# Longterm operation of a microbiological mercury removing pilot plant at two chloralkali factories in Europe

J. Leonhaeuser1, H. von Canstein1, I. Wagner-Doebler1, W.-D. Deckwer2

1Dept. Microbiology, National Research Institute for Biotechnology (GBF), Braunschweig, Germany

## 2Technical University, Braunschweig, Germany

A pilot plant for the demonstration of microbial mercury removal from wastewater in technical scale was constructed in a cooperation between GBF and Preussag Wassertechnik. In a packed bed bioreactor mercury was accumulated as elemental mercury following enzymatic reduction by a diverse community of naturally immobilised mercury resistant bacteria. The plant included automated pH adjustment of the incoming wastewater from pH 2.5 to pH 7.0, a polishing activated carbon filter in the outflow, automated continuous feeding of the bacteria, continuous measurement of temperature, pH, redox potential and oxygen before and after the bioreactor, continuous mercury measurements in the inflow and outflow, remote control of pumps and valves, and remote access to process data. It was installed in a mobile container and operated on site a German chloralkali electrolysis factories for 8 months and at a Czech chloralkali factory for 3 years continuously.

Complete oxidation of the incoming wastewater to convert all mercury into the ionic form (Hg2+) which is bioavailable to mercury resistant microbes was crucial for optimum bioreactor performance. This oxidation pretreatment was operating at the German electrolysis factory, since the ion exchange columns used there for mercury clean-up also react only with Hg2+. During the 8 months of operation, 7500 m3 of wastewater were treated and effluent mercury concentrations of <50 ppb were routinely reached at an average inflow concentration of 4.5 mg Hg/l. The upper temperature limit for the process was determined to be 45°C. Except for maintenance problems, there was no operation problem.

The plant was subsequently operated for 3 years at a Czech chloralkali factory. Numerous technical problems had to be solved, including the construction of a wastewater pre-treatment unit, process modifications to maintain a stable inflow volume, removal of excess suspended material from the inflow by a sand filter, and installation of heat exchangers to prevent the inflow temperature to drop below 20°C in winter. Due to frequent problems with the stability of the electrolysis process, hazardous situations repeatedly occured resulting in highly toxic wastewater inflow loads (mercury concentrations above 50 mg/l, chlorine concentrations up to 100 mg/l, high salt loads) which were not bypassed due to mechanical problems (clogging of valves and tubes, corrosion of electronic elements). In spite of all this, good performance was obtained in the third year of operation. From May 2002 to August 2003, 22 000 m3 of wastewater were treated;  inflow concentrations were between 0.6 mg Hg/l and 3.87 mg Hg/l (monthly average) and outflow concentrations between 60 and 180 ppb (monthly average) were obtained. These values were higher than at the German factory because of the presence of suspended matter transported out of the bioreactor.

The microbiological process costs less than 40 % of ion exchange columns both regarding investment and operating costs. However, the company Spolchemie decided to install the more expensive ion exchange treatment in order to meet Western European standards as recommended by Eurochlor. Effluent concentrations below 10 ppb can be reached with ion exchange columns, and the retained mercury can be recycled into the electrolysis cells. However, the longterm experience gained with the microbiological process in a difficult industrial setting is an important basis for future applications.