## Prva stran
variable | 145 | 1.KORAK | variable_1 | 2.KORAK | KORAKI!
Device name | Tip | število spremenljivk | Tip (izbrani) | Zamenjaj z | 1.V Sheet "variable" skopiraj vsebino iz variable.dbf - iz Citect SCAD-a projekta, ki ga želiš pretvoriti.
IOD_ST3 | BCD | 0 | BCD | INT | 2.V polje A3 vpiši Device ime spremenljivk ki se bodo prenašale preko Modnet protokola
| BYTE | 8 | BYTE | BYTE | 3.V polje A6 vpiši ime krmilnika (npr.:PLC1, če je adresa v spremenljivkah PLC1:.NapakaKoncnega_stikala, drugače pusti polje prazno)
OPC name | DIGITAL | 52 | DIGITAL | DIGITAL | 4. Pritisni gumb 1.KORAK (V poljih C3:C10 se izpiše število spremenljivk, ki imajo Device enak tistemu v polju A3)
ST3 | INT | 25 | INT | INT | 5. Pritisni gumb 2.KORAK (V Sheet-u variable_1 se naredi seznam spremenljivk, ki se bodo prenačale preko Modnet protokola)
| LONG | 0 | LONG | LONG | 6. Pritisni gumb 3.KORAK (V poljih C15:C24 se izpiše število spremnljiv po tipih, v poljih F15:F24 se izpiše število potrebni wordow/coilov za prenos spremnljivk)
| REAL | 5 | REAL | REAL | 7. 4.KORAK: V polja C29:C38 je potrebno ročno vpisati začetne naslove spremnljivk. Potrebno je paziti na:
| STRING | 5 | UINT | UINT | *naslov se morajo začeti z lihim številom npr.:1, 101, 551
| UINT | 1 | STRING | STRING | *naslove je potrebno nastaviti tako, da se naslovi sremenljivk ne more prekrivati (naslovi spremenjivk gredo od (začetnega naslova) do (začetnega naslova+število potrebnih wordow))
8. Pritisni gumb 5.KORAK (V Sheet-u variable_2 se naredi seznam spremenljivk, ki so tokrat sortirana po tipih)
9. Pritisni gumb 6.KORAK (V Sheet-u variable_3 se naredi seznam spremenljivk, katerih Device se zamenja z devicom v polju C41)
Trajanje makroja | variable_1 |  |  | 3.KORAK | 10. Pritisni gumb 7.KORAK (V Sheet-u variable_new se generira seznam spremenljivk. To vsebino je potrebno skopirati v variable.dbf)
0 | Tip | število spremenljivk | TIP | št.potrebnih coilov/wordov | *ta korak traja nekoliko dalj časa (odvisno od števila spremenljivk)
| BCD | 0 | BCD | 0 | *če se pojavi težava z adresami ki se začnejo z 0000 (npr.: "00001" se spremeni na "1") je potrebno uporabiti priloženo (prazno) variable.dbf ali v
| BYTE | 0 | BYTE | 0 | ProjectEditoju/VariableTags na poljubni spremenljki nastaviti adreso" 00001"
| DIGITAL | 52 | DIGITAL | 52 (Coil) | 11. Pritisni gumb 8.KORAK in 9.KORAK (V Sheet-u Xsoft se generira koda)
| INT | 33 | INT | 33 (word) | 12. S pritiskom na gumb 10.KORAK se zgenerira EXP koda za Xsoft (Xsoft_EXP)
| LONG | 0 | LONG | 0 (word) | 13. S pritiskom na gumb Save*.EXP se avtomatsko generira datoka *.EXP
| REAL | 5 | REAL | 10 (word)
| STRING | 5 | STRING | 75 (word)
| UINT | 1 | UINT | 1 (word)
POZOR!
*V Sheet-u variable mora biti vsebina skopirana od polja A1 naprej (če je katera vrstica prazna makroji ne bodo delovali pravilno)
*Ena "STRING" spremenljivka zasede 15wordow (to pomeni 29 znakov, 1BYTE=1STRING)
|  | 4.KORAK(vpiši ročno) | variable_2 | 5.KORAK | *Dolžina "STRING" spremenljivk je 29 znakov (lahko tudi več vendar ne z uporabno tega dokumenta in XSoft programa,potrebna je modifikacija makrojev in Xsoft programa)
| Tip | Začetni naslov |  | Sortiraj | *Vsi stringi so enake dolžine (29)
| BCD |  |  | BCD | *"BYTE" spremenljivke se v variable.dbf spremenijo v "INT" (prenašanje posameznih bytov ni mogoče, niti naslavaljanje v citectscadi)
| BYTE |  |  | DIGITAL | *Naslovi spremenljivk se morajo obvezno začeti z lihim naslovom (preizkušeno je z začetnimi naslovi, ki se izpišejo po pritisku na gumb Ponastavi)
| DIGITAL | 1 |  | BYTE | *Z pritiskom na gumb RESET se pobriše vsebina vseh Sheet-ov razen Sheet-a variable (makor reset se izvaja precej časa)
| INT | 1 |  | INT | *makroji ne delujejo pravilno,če je v Sheet-u variable več kot 9999 vrstic oz. spremenljivk (število vseh spremnljivk je prikazano v polju B1)
| LONG | 3001 |  | LONG | *če se vsebine iz variable_new ne gre skpirat v variable.dbf datotek, vsebino skopirajte najprej v *.txt datoteko in nato v variable.dbf
| REAL | 4001 |  | REAL | *v polju A14 na Sheet-u Prva stran se prikazuje število ciklop do konca izvedbe makroja (samo za gumb 7.KORAK)
| STRING | 5001 |  | STRING
| UINT | 6001 |  | UINT
| variable_3 | 6.KORAK | variable_new | 7.KORAK
| New Device name | IOD_ST3_TCP |  | Nova variable dbf
|  |  | xSoft | 8.KORAK in 9.KORAK
xSoft koda
xSoft_EXP
Izvoz*.EXP
1.KORAK
2.KORAK
3.KORAK
5.KORAK
6.KORAK
7.KORAK
8.KORAK
9.KORAK
RESET
Ponastavi
10.KORAK
Save*.EXP

## variable
ST3ComError | DIGITAL | IOD_ST3 | ST3:.ComError | [6 empty] | 6157 | 0x07400010
ST3ComSCADA | DIGITAL | IOD_ST3 | ST3:.ComSCADA | [6 empty] | 6157 | 0x07400020
ST3ComSCADA1 | DIGITAL | IOD_ST3 | ST3:.ComSCADA1 | [6 empty] | 6157 | 0x07400030
ST3ComSCADA2 | DIGITAL | IOD_ST3 | ST3:.ComSCADA2 | [6 empty] | 6157 | 0x07400040
ST3ComSCADA3 | DIGITAL | IOD_ST3 | ST3:.ComSCADA3 | [6 empty] | 6157 | 0x07400050
ST3Date_Time0 | STRING | IOD_ST3 | ST3:.Date_Time[0] | [6 empty] | 6157 | 0x07400069
ST3Date_Time1 | STRING | IOD_ST3 | ST3:.Date_Time[1] | [6 empty] | 6157 | 0x0740006a
ST3Date_Time2 | STRING | IOD_ST3 | ST3:.Date_Time[2] | [6 empty] | 6157 | 0x0740006b
ST3Date_Time3 | STRING | IOD_ST3 | ST3:.Date_Time[3] | [6 empty] | 6157 | 0x0740006c
ST3DateTimeDan | BYTE | IOD_ST3 | ST3:.DateTime.Dan | [6 empty] | 6157 | 0x0740006d
ST3DateTimeLeto | BYTE | IOD_ST3 | ST3:.DateTime.Leto | [6 empty] | 6157 | 0x0740006e
ST3DateTimeLeto2 | INT | IOD_ST3 | ST3:.DateTime.Leto2 | [6 empty] | 6157 | 0x0740006f
ST3DateTimeMesec | BYTE | IOD_ST3 | ST3:.DateTime.Mesec | [6 empty] | 6157 | 0x07400070
ST3DateTimeMinuta | BYTE | IOD_ST3 | ST3:.DateTime.Minuta | [6 empty] | 6157 | 0x07400071
ST3DateTimeSekunda | BYTE | IOD_ST3 | ST3:.DateTime.Sekunda | [6 empty] | 6157 | 0x07400072
ST3DateTimeUra | BYTE | IOD_ST3 | ST3:.DateTime.Ura | [6 empty] | 6157 | 0x07400073
ST3HIA1_vlaga_s | INT | IOD_ST3 | ST3:.HIA1_vlaga_s | 0 | 1000 | 0 | 100.0 | % | ###.# | 6157 | 0x07400075
ST3HIA2_vlaga_s | INT | IOD_ST3 | ST3:.HIA2_vlaga_s | 0 | 1000 | 0 | 100.0 | % | ###.# | 6157 | 0x07400077
ST3HIA3_vlaga_s | INT | IOD_ST3 | ST3:.HIA3_vlaga_s | 0 | 1000 | 0 | 100.0 | % | ###.# | 6157 | 0x07400079
ST3HIA4_vlaga_s | INT | IOD_ST3 | ST3:.HIA4_vlaga_s | 0 | 1000 | 0 | 100.0 | % | ###.# | 6157 | 0x0740007b
ST3HIA5_vlaga_s | INT | IOD_ST3 | ST3:.HIA5_vlaga_s | 0 | 1000 | 0 | 100.0 | % | ###.# | 6157 | 0x0740007d
ST3HIA6_vlaga_s | INT | IOD_ST3 | ST3:.HIA6_vlaga_s | 0 | 1000 | 0 | 100.0 | % | ###.# | 6157 | 0x0740007f
ST3HIA7_vlaga_s | INT | IOD_ST3 | ST3:.HIA7_vlaga_s | 0 | 1000 | 0 | 100.0 | % | ###.# | 6157 | 0x07400081
ST3HIA8_vlaga_s | INT | IOD_ST3 | ST3:.HIA8_vlaga_s | 0 | 1000 | 0 | 100.0 | % | ###.# | 6157 | 0x07400083
ST3kom_nast_cas_izpada | UINT | IOD_ST3 | ST3:.kom_nast_cas_izpada | [6 empty] | 6157 | 0x07400084
ST3napaka_kom_panel | DIGITAL | IOD_ST3 | ST3:.napaka_kom_panel | [6 empty] | 6157 | 0x07400090
ST3napaka_kom_scada | DIGITAL | IOD_ST3 | ST3:.napaka_kom_scada | [6 empty] | 6157 | 0x074000a0
ST3napaka_kom_scada2 | DIGITAL | IOD_ST3 | ST3:.napaka_kom_scada2 | [6 empty] | 6157 | 0x074000b0
ST3NapakaSenzorSkupno | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorSkupno | [6 empty] | 6157 | 0x074000c0
ST3NapakaSenzorVlagaHIA1 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA1 | [6 empty] | 6157 | 0x074000d0
ST3NapakaSenzorVlagaHIA2 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA2 | [6 empty] | 6157 | 0x074000e0
ST3NapakaSenzorVlagaHIA3 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA3 | [6 empty] | 6157 | 0x074000f0
ST3NapakaSenzorVlagaHIA4 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA4 | [6 empty] | 6157 | 0x07400100
ST3NapakaSenzorVlagaHIA5 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA5 | [6 empty] | 6157 | 0x07400110
ST3NapakaSenzorVlagaHIA6 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA6 | [6 empty] | 6157 | 0x07400120
ST3NapakaSenzorVlagaHIA7 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA7 | [6 empty] | 6157 | 0x07400130
ST3NapakaSenzorVlagaHIA8 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA8 | [6 empty] | 6157 | 0x07400140
ST3NapakaTSTempTIA1 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA1 | [6 empty] | 6157 | 0x07400150
ST3NapakaTSTempTIA2 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA2 | [6 empty] | 6157 | 0x07400160
ST3NapakaTSTempTIA3 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA3 | [6 empty] | 6157 | 0x07400170
ST3NapakaTSTempTIA4 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA4 | [6 empty] | 6157 | 0x07400180
ST3NapakaTSTempTIA5 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA5 | [6 empty] | 6157 | 0x07400190
ST3NapakaTSTempTIA6 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA6 | [6 empty] | 6157 | 0x074001a0
ST3NapakaTSTempTIA7 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA7 | [6 empty] | 6157 | 0x074001b0
ST3NapakaTSTempTIA8 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA8 | [6 empty] | 6157 | 0x074001c0
ST3PrevisokaTemp | DIGITAL | IOD_ST3 | ST3:.PrevisokaTemp | [6 empty] | 6157 | 0x074001d0
ST3razlitjeLAH1 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH1 | [6 empty] | 6157 | 0x074001e0
ST3razlitjeLAH2 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH2 | [6 empty] | 6157 | 0x074001f0
ST3razlitjeLAH3 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH3 | [6 empty] | 6157 | 0x07400200
ST3razlitjeLAH4 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH4 | [6 empty] | 6157 | 0x07400210
ST3razlitjeLAH5 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH5 | [6 empty] | 6157 | 0x07400220
ST3razlitjeLAH6 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH6 | [6 empty] | 6157 | 0x07400230
ST3razlitjeLAH7 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH7 | [6 empty] | 6157 | 0x07400240
ST3razlitjeLAH8 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH8 | [6 empty] | 6157 | 0x07400250
ST3rVersion | REAL | IOD_ST3 | ST3:.rVersion | [6 empty] | 6157 | 0x07400260
ST3SetDateTime | DIGITAL | IOD_ST3 | ST3:.SetDateTime | [6 empty] | 6157 | 0x07400270
ST3SetDateTimeDemand | DIGITAL | IOD_ST3 | ST3:.SetDateTimeDemand | [6 empty] | 6157 | 0x07400280
ST3SetDateTimeError | DIGITAL | IOD_ST3 | ST3:.SetDateTimeError | [6 empty] | 6157 | 0x07400290
ST3SetDateTimeFinished | DIGITAL | IOD_ST3 | ST3:.SetDateTimeFinished | [6 empty] | 6157 | 0x074002a0
ST3SlabaBaterijaPLC | DIGITAL | IOD_ST3 | ST3:.SlabaBaterijaPLC | [6 empty] | 6157 | 0x074002b0
ST3TIA1_alarm | INT | IOD_ST3 | ST3:.TIA1_alarm | 0 | 60 | 0 | 60 | °C | ## | 6157 | 0x074002c9
ST3TIA1_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA1_previs_temp | [6 empty] | 6157 | 0x074002d0
ST3TIA1_temp_s | INT | IOD_ST3 | ST3:.TIA1_temp_s | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 0x074002e1
ST3TIA2_alarm | INT | IOD_ST3 | ST3:.TIA2_alarm | 0 | 60 | 0 | 60 | °C | ## | 6157 | 0x074002e2
ST3TIA2_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA2_previs_temp | [6 empty] | 6157 | 0x074002f0
ST3TIA2_temp_s | INT | IOD_ST3 | ST3:.TIA2_temp_s | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 0x07400301
ST3TIA3_alarm | INT | IOD_ST3 | ST3:.TIA3_alarm | 0 | 60 | 0 | 60 | °C | ## | 6157 | 0x07400302
ST3TIA3_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA3_previs_temp | [6 empty] | 6157 | 0x07400310
ST3TIA3_temp_s | INT | IOD_ST3 | ST3:.TIA3_temp_s | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 0x07400321
ST3TIA4_alarm | INT | IOD_ST3 | ST3:.TIA4_alarm | 0 | 60 | 0 | 60 | °C | ## | 6157 | 0x07400322
ST3TIA4_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA4_previs_temp | [6 empty] | 6157 | 0x07400330
ST3TIA4_temp_s | INT | IOD_ST3 | ST3:.TIA4_temp_s | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 0x07400341
ST3TIA5_alarm | INT | IOD_ST3 | ST3:.TIA5_alarm | 0 | 60 | 0 | 60 | °C | ## | 6157 | 0x07400342
ST3TIA5_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA5_previs_temp | [6 empty] | 6157 | 0x07400350
ST3TIA5_temp_s | INT | IOD_ST3 | ST3:.TIA5_temp_s | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 0x07400361
ST3TIA6_alarm | INT | IOD_ST3 | ST3:.TIA6_alarm | 0 | 60 | 0 | 60 | °C | ## | 6157 | 0x07400362
ST3TIA6_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA6_previs_temp | [6 empty] | 6157 | 0x07400370
ST3TIA6_temp_s | INT | IOD_ST3 | ST3:.TIA6_temp_s | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 0x07400381
ST3TIA7_alarm | INT | IOD_ST3 | ST3:.TIA7_alarm | 0 | 60 | 0 | 60 | °C | ## | 6157 | 0x07400382
ST3TIA7_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA7_previs_temp | [6 empty] | 6157 | 0x07400390
ST3TIA7_temp_s | INT | IOD_ST3 | ST3:.TIA7_temp_s | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 0x074003a1
ST3TIA8_alarm | INT | IOD_ST3 | ST3:.TIA8_alarm | 0 | 60 | 0 | 60 | °C | ## | 6157 | 0x074003a2
ST3TIA8_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA8_previs_temp | [6 empty] | 6157 | 0x074003b0
ST3TIA8_temp_s | INT | IOD_ST3 | ST3:.TIA8_temp_s | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 0x074003c1
ST3ups_alarm | DIGITAL | IOD_ST3 | ST3:.ups_alarm | [6 empty] | 6157 | 0x074003d0
ST3ups_baterijski_nac | DIGITAL | IOD_ST3 | ST3:.ups_baterijski_nac | [6 empty] | 6157 | 0x074003e0
ST3ups_polnjenje | DIGITAL | IOD_ST3 | ST3:.ups_polnjenje | [6 empty] | 6157 | 0x074003f0
ST3UserCurrentLevel | BYTE | IOD_ST3 | ST3:.UserCurrentLevel | [6 empty] | 6157 | 0x07400400
ST3UserCurrentName | STRING | IOD_ST3 | ST3:.UserCurrentName | [6 empty] | 6157 | 0x07400401
ST3UserLoggedIn | DIGITAL | IOD_ST3 | ST3:.UserLoggedIn | [6 empty] | 6157 | 0x07400410
ST3XVH_AlarmOn | DIGITAL | IOD_ST3 | ST3:.XVH_AlarmOn | [6 empty] | 6157 | 0x07400420
ST3XVH_UPSstatus | BYTE | IOD_ST3 | ST3:.XVH_UPSstatus | [6 empty] | 6157 | 0x07400430
ST3XVHdepltedBatery1 | REAL | IOD_ST3 | ST3:.XVHdepltedBatery1 | [6 empty] | 6157 | 0x07400431
ST3XVHdepltedBatery2 | REAL | IOD_ST3 | ST3:.XVHdepltedBatery2 | [6 empty] | 6157 | 0x07400432
ST3XVHlowBatery1 | REAL | IOD_ST3 | ST3:.XVHlowBatery1 | [6 empty] | 6157 | 0x07400433
ST3XVHlowBatery2 | REAL | IOD_ST3 | ST3:.XVHlowBatery2 | [6 empty] | 6157 | 0x07400434
ST3Server_B_Izpad | DIGITAL | IOD_ST3_mem | D200 | [7 empty] | 0x07400440
ST3Server_A_Izpad | DIGITAL | IOD_ST3_mem | D201 | [7 empty] | 0x07400450
AST3_omogoci_sms | DIGITAL | IOD_ST3_disk | D1[100] | [7 empty] | 0x07400460
ST3NapakaSenzorVlagaHIA1_om | DIGITAL | IOD_ST3_disk | D102 | [7 empty] | 0x07400470
ST3NapakaSenzorVlagaHIA2_om | DIGITAL | IOD_ST3_disk | D103 | [7 empty] | 0x07400480
ST3NapakaSenzorVlagaHIA3_om | DIGITAL | IOD_ST3_disk | D104 | [7 empty] | 0x07400490
ST3NapakaSenzorVlagaHIA4_om | DIGITAL | IOD_ST3_disk | D105 | [7 empty] | 0x074004a0
ST3NapakaSenzorVlagaHIA5_om | DIGITAL | IOD_ST3_disk | D106 | [7 empty] | 0x074004b0
ST3NapakaSenzorVlagaHIA6_om | DIGITAL | IOD_ST3_disk | D107 | [7 empty] | 0x074004c0
ST3NapakaSenzorVlagaHIA7_om | DIGITAL | IOD_ST3_disk | D108 | [7 empty] | 0x074004d0
ST3NapakaSenzorVlagaHIA8_om | DIGITAL | IOD_ST3_disk | D109 | [7 empty] | 0x074004e0
ST3NapakaTSTempTIA1_om | DIGITAL | IOD_ST3_disk | D110 | [7 empty] | 0x074004f0
ST3NapakaTSTempTIA2_om | DIGITAL | IOD_ST3_disk | D111 | [7 empty] | 0x07400500
ST3NapakaTSTempTIA3_om | DIGITAL | IOD_ST3_disk | D112 | [7 empty] | 0x07400510
ST3NapakaTSTempTIA4_om | DIGITAL | IOD_ST3_disk | D113 | [7 empty] | 0x07400520
ST3NapakaTSTempTIA5_om | DIGITAL | IOD_ST3_disk | D114 | [7 empty] | 0x07400530
ST3NapakaTSTempTIA6_om | DIGITAL | IOD_ST3_disk | D115 | [7 empty] | 0x07400540
ST3NapakaTSTempTIA7_om | DIGITAL | IOD_ST3_disk | D116 | [7 empty] | 0x07400550
ST3NapakaTSTempTIA8_om | DIGITAL | IOD_ST3_disk | D117 | [7 empty] | 0x07400560
ST3TIA1_previs_temp_om | DIGITAL | IOD_ST3_disk | D118 | [7 empty] | 0x07400570
ST3TIA2_previs_temp_om | DIGITAL | IOD_ST3_disk | D119 | [7 empty] | 0x07400580
ST3TIA3_previs_temp_om | DIGITAL | IOD_ST3_disk | D120 | [7 empty] | 0x07400590
ST3TIA4_previs_temp_om | DIGITAL | IOD_ST3_disk | D121 | [7 empty] | 0x074005a0
ST3TIA5_previs_temp_om | DIGITAL | IOD_ST3_disk | D122 | [7 empty] | 0x074005b0
ST3TIA6_previs_temp_om | DIGITAL | IOD_ST3_disk | D123 | [7 empty] | 0x074005c0
ST3TIA7_previs_temp_om | DIGITAL | IOD_ST3_disk | D124 | [7 empty] | 0x074005d0
ST3TIA8_previs_temp_om | DIGITAL | IOD_ST3_disk | D125 | [7 empty] | 0x074005e0
ST3razlitjeLAH1_om | DIGITAL | IOD_ST3_disk | D126 | [7 empty] | 0x074005f0
ST3razlitjeLAH2_om | DIGITAL | IOD_ST3_disk | D127 | [7 empty] | 0x07400600
ST3razlitjeLAH3_om | DIGITAL | IOD_ST3_disk | D128 | [7 empty] | 0x07400610
ST3razlitjeLAH4_om | DIGITAL | IOD_ST3_disk | D129 | [7 empty] | 0x07400620
ST3razlitjeLAH5_om | DIGITAL | IOD_ST3_disk | D130 | [7 empty] | 0x07400630
ST3razlitjeLAH6_om | DIGITAL | IOD_ST3_disk | D131 | [7 empty] | 0x07400640
ST3razlitjeLAH7_om | DIGITAL | IOD_ST3_disk | D132 | [7 empty] | 0x07400650
ST3razlitjeLAH8_om | DIGITAL | IOD_ST3_disk | D133 | [7 empty] | 0x07400660
ST3Server_A_Izpad_om | DIGITAL | IOD_ST3_disk | D134 | [7 empty] | 0x07400670
ST3Server_B_Izpad_om | DIGITAL | IOD_ST3_disk | D135 | [7 empty] | 0x07400680
ST3napaka_kom_panel_om | DIGITAL | IOD_ST3_disk | D136 | [7 empty] | 0x07400690
ST3SetDateTimeError_om | DIGITAL | IOD_ST3_disk | D137 | [7 empty] | 0x074006a0
ST3SlabaBaterijaPLC_om | DIGITAL | IOD_ST3_disk | D138 | [7 empty] | 0x074006b0
ST3ups_baterijski_nac_om | DIGITAL | IOD_ST3_disk | D139 | [7 empty] | 0x074006c0
ST3ups_alarm_om | DIGITAL | IOD_ST3_disk | D140 | [7 empty] | 0x074006d0
ST3ups_polnjenje_om | DIGITAL | IOD_ST3_disk | D141 | [7 empty] | 0x074006e0
ST3UserloggedIn_mem | INT | IOD_ST3_mem | I1 | [7 empty] | 0x074006f0
ST3_ComSCADA_stevec1 | INT | IOD_ST3_mem | I2 | [7 empty] | 0x074006f1
ST3_ComSCADA_stevec2 | INT | IOD_ST3_mem | I3 | [7 empty] | 0x074006f2
ST3_ComSCADA_stevec3 | INT | IOD_ST3_mem | I4 | [7 empty] | 0x074006f3
ST3_ComSCADA_stevec4 | INT | IOD_ST3_mem | I5 | [7 empty] | 0x074006f4
BST3_omogoci_sms | DIGITAL | IOD_ST3_disk | D200[100] | [7 empty] | 0x07400700

## variable_1
ST3ComError | DIGITAL | IOD_ST3 | ST3:.ComError
ST3ComSCADA | DIGITAL | IOD_ST3 | ST3:.ComSCADA
ST3ComSCADA1 | DIGITAL | IOD_ST3 | ST3:.ComSCADA1
ST3ComSCADA2 | DIGITAL | IOD_ST3 | ST3:.ComSCADA2
ST3ComSCADA3 | DIGITAL | IOD_ST3 | ST3:.ComSCADA3
ST3Date_Time0 | STRING | IOD_ST3 | ST3:.Date_Time[0]
ST3Date_Time1 | STRING | IOD_ST3 | ST3:.Date_Time[1]
ST3Date_Time2 | STRING | IOD_ST3 | ST3:.Date_Time[2]
ST3Date_Time3 | STRING | IOD_ST3 | ST3:.Date_Time[3]
ST3DateTimeDan | INT | IOD_ST3 | ST3:.DateTime.Dan | BYTE
ST3DateTimeLeto | INT | IOD_ST3 | ST3:.DateTime.Leto | BYTE
ST3DateTimeLeto2 | INT | IOD_ST3 | ST3:.DateTime.Leto2
ST3DateTimeMesec | INT | IOD_ST3 | ST3:.DateTime.Mesec | BYTE
ST3DateTimeMinuta | INT | IOD_ST3 | ST3:.DateTime.Minuta | BYTE
ST3DateTimeSekunda | INT | IOD_ST3 | ST3:.DateTime.Sekunda | BYTE
ST3DateTimeUra | INT | IOD_ST3 | ST3:.DateTime.Ura | BYTE
ST3HIA1_vlaga_s | INT | IOD_ST3 | ST3:.HIA1_vlaga_s
ST3HIA2_vlaga_s | INT | IOD_ST3 | ST3:.HIA2_vlaga_s
ST3HIA3_vlaga_s | INT | IOD_ST3 | ST3:.HIA3_vlaga_s
ST3HIA4_vlaga_s | INT | IOD_ST3 | ST3:.HIA4_vlaga_s
ST3HIA5_vlaga_s | INT | IOD_ST3 | ST3:.HIA5_vlaga_s
ST3HIA6_vlaga_s | INT | IOD_ST3 | ST3:.HIA6_vlaga_s
ST3HIA7_vlaga_s | INT | IOD_ST3 | ST3:.HIA7_vlaga_s
ST3HIA8_vlaga_s | INT | IOD_ST3 | ST3:.HIA8_vlaga_s
ST3kom_nast_cas_izpada | UINT | IOD_ST3 | ST3:.kom_nast_cas_izpada
ST3napaka_kom_panel | DIGITAL | IOD_ST3 | ST3:.napaka_kom_panel
ST3napaka_kom_scada | DIGITAL | IOD_ST3 | ST3:.napaka_kom_scada
ST3napaka_kom_scada2 | DIGITAL | IOD_ST3 | ST3:.napaka_kom_scada2
ST3NapakaSenzorSkupno | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorSkupno
ST3NapakaSenzorVlagaHIA1 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA1
ST3NapakaSenzorVlagaHIA2 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA2
ST3NapakaSenzorVlagaHIA3 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA3
ST3NapakaSenzorVlagaHIA4 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA4
ST3NapakaSenzorVlagaHIA5 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA5
ST3NapakaSenzorVlagaHIA6 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA6
ST3NapakaSenzorVlagaHIA7 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA7
ST3NapakaSenzorVlagaHIA8 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA8
ST3NapakaTSTempTIA1 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA1
ST3NapakaTSTempTIA2 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA2
ST3NapakaTSTempTIA3 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA3
ST3NapakaTSTempTIA4 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA4
ST3NapakaTSTempTIA5 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA5
ST3NapakaTSTempTIA6 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA6
ST3NapakaTSTempTIA7 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA7
ST3NapakaTSTempTIA8 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA8
ST3PrevisokaTemp | DIGITAL | IOD_ST3 | ST3:.PrevisokaTemp
ST3razlitjeLAH1 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH1
ST3razlitjeLAH2 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH2
ST3razlitjeLAH3 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH3
ST3razlitjeLAH4 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH4
ST3razlitjeLAH5 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH5
ST3razlitjeLAH6 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH6
ST3razlitjeLAH7 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH7
ST3razlitjeLAH8 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH8
ST3rVersion | REAL | IOD_ST3 | ST3:.rVersion
ST3SetDateTime | DIGITAL | IOD_ST3 | ST3:.SetDateTime
ST3SetDateTimeDemand | DIGITAL | IOD_ST3 | ST3:.SetDateTimeDemand
ST3SetDateTimeError | DIGITAL | IOD_ST3 | ST3:.SetDateTimeError
ST3SetDateTimeFinished | DIGITAL | IOD_ST3 | ST3:.SetDateTimeFinished
ST3SlabaBaterijaPLC | DIGITAL | IOD_ST3 | ST3:.SlabaBaterijaPLC
ST3TIA1_alarm | INT | IOD_ST3 | ST3:.TIA1_alarm
ST3TIA1_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA1_previs_temp
ST3TIA1_temp_s | INT | IOD_ST3 | ST3:.TIA1_temp_s
ST3TIA2_alarm | INT | IOD_ST3 | ST3:.TIA2_alarm
ST3TIA2_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA2_previs_temp
ST3TIA2_temp_s | INT | IOD_ST3 | ST3:.TIA2_temp_s
ST3TIA3_alarm | INT | IOD_ST3 | ST3:.TIA3_alarm
ST3TIA3_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA3_previs_temp
ST3TIA3_temp_s | INT | IOD_ST3 | ST3:.TIA3_temp_s
ST3TIA4_alarm | INT | IOD_ST3 | ST3:.TIA4_alarm
ST3TIA4_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA4_previs_temp
ST3TIA4_temp_s | INT | IOD_ST3 | ST3:.TIA4_temp_s
ST3TIA5_alarm | INT | IOD_ST3 | ST3:.TIA5_alarm
ST3TIA5_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA5_previs_temp
ST3TIA5_temp_s | INT | IOD_ST3 | ST3:.TIA5_temp_s
ST3TIA6_alarm | INT | IOD_ST3 | ST3:.TIA6_alarm
ST3TIA6_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA6_previs_temp
ST3TIA6_temp_s | INT | IOD_ST3 | ST3:.TIA6_temp_s
ST3TIA7_alarm | INT | IOD_ST3 | ST3:.TIA7_alarm
ST3TIA7_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA7_previs_temp
ST3TIA7_temp_s | INT | IOD_ST3 | ST3:.TIA7_temp_s
ST3TIA8_alarm | INT | IOD_ST3 | ST3:.TIA8_alarm
ST3TIA8_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA8_previs_temp
ST3TIA8_temp_s | INT | IOD_ST3 | ST3:.TIA8_temp_s
ST3ups_alarm | DIGITAL | IOD_ST3 | ST3:.ups_alarm
ST3ups_baterijski_nac | DIGITAL | IOD_ST3 | ST3:.ups_baterijski_nac
ST3ups_polnjenje | DIGITAL | IOD_ST3 | ST3:.ups_polnjenje
ST3UserCurrentLevel | INT | IOD_ST3 | ST3:.UserCurrentLevel | BYTE
ST3UserCurrentName | STRING | IOD_ST3 | ST3:.UserCurrentName
ST3UserLoggedIn | DIGITAL | IOD_ST3 | ST3:.UserLoggedIn
ST3XVH_AlarmOn | DIGITAL | IOD_ST3 | ST3:.XVH_AlarmOn
ST3XVH_UPSstatus | INT | IOD_ST3 | ST3:.XVH_UPSstatus | BYTE
ST3XVHdepltedBatery1 | REAL | IOD_ST3 | ST3:.XVHdepltedBatery1
ST3XVHdepltedBatery2 | REAL | IOD_ST3 | ST3:.XVHdepltedBatery2
ST3XVHlowBatery1 | REAL | IOD_ST3 | ST3:.XVHlowBatery1
ST3XVHlowBatery2 | REAL | IOD_ST3 | ST3:.XVHlowBatery2

## variable_2
ST3ComError | DIGITAL | IOD_ST3 | ST3:.ComError
ST3ComSCADA | DIGITAL | IOD_ST3 | ST3:.ComSCADA
ST3ComSCADA1 | DIGITAL | IOD_ST3 | ST3:.ComSCADA1
ST3ComSCADA2 | DIGITAL | IOD_ST3 | ST3:.ComSCADA2
ST3ComSCADA3 | DIGITAL | IOD_ST3 | ST3:.ComSCADA3
ST3napaka_kom_panel | DIGITAL | IOD_ST3 | ST3:.napaka_kom_panel
ST3napaka_kom_scada | DIGITAL | IOD_ST3 | ST3:.napaka_kom_scada
ST3napaka_kom_scada2 | DIGITAL | IOD_ST3 | ST3:.napaka_kom_scada2
ST3NapakaSenzorSkupno | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorSkupno
ST3NapakaSenzorVlagaHIA1 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA1
ST3NapakaSenzorVlagaHIA2 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA2
ST3NapakaSenzorVlagaHIA3 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA3
ST3NapakaSenzorVlagaHIA4 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA4
ST3NapakaSenzorVlagaHIA5 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA5
ST3NapakaSenzorVlagaHIA6 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA6
ST3NapakaSenzorVlagaHIA7 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA7
ST3NapakaSenzorVlagaHIA8 | DIGITAL | IOD_ST3 | ST3:.NapakaSenzorVlagaHIA8
ST3NapakaTSTempTIA1 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA1
ST3NapakaTSTempTIA2 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA2
ST3NapakaTSTempTIA3 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA3
ST3NapakaTSTempTIA4 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA4
ST3NapakaTSTempTIA5 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA5
ST3NapakaTSTempTIA6 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA6
ST3NapakaTSTempTIA7 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA7
ST3NapakaTSTempTIA8 | DIGITAL | IOD_ST3 | ST3:.NapakaTSTempTIA8
ST3PrevisokaTemp | DIGITAL | IOD_ST3 | ST3:.PrevisokaTemp
ST3razlitjeLAH1 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH1
ST3razlitjeLAH2 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH2
ST3razlitjeLAH3 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH3
ST3razlitjeLAH4 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH4
ST3razlitjeLAH5 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH5
ST3razlitjeLAH6 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH6
ST3razlitjeLAH7 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH7
ST3razlitjeLAH8 | DIGITAL | IOD_ST3 | ST3:.razlitjeLAH8
ST3SetDateTime | DIGITAL | IOD_ST3 | ST3:.SetDateTime
ST3SetDateTimeDemand | DIGITAL | IOD_ST3 | ST3:.SetDateTimeDemand
ST3SetDateTimeError | DIGITAL | IOD_ST3 | ST3:.SetDateTimeError
ST3SetDateTimeFinished | DIGITAL | IOD_ST3 | ST3:.SetDateTimeFinished
ST3SlabaBaterijaPLC | DIGITAL | IOD_ST3 | ST3:.SlabaBaterijaPLC
ST3TIA1_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA1_previs_temp
ST3TIA2_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA2_previs_temp
ST3TIA3_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA3_previs_temp
ST3TIA4_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA4_previs_temp
ST3TIA5_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA5_previs_temp
ST3TIA6_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA6_previs_temp
ST3TIA7_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA7_previs_temp
ST3TIA8_previs_temp | DIGITAL | IOD_ST3 | ST3:.TIA8_previs_temp
ST3ups_alarm | DIGITAL | IOD_ST3 | ST3:.ups_alarm
ST3ups_baterijski_nac | DIGITAL | IOD_ST3 | ST3:.ups_baterijski_nac
ST3ups_polnjenje | DIGITAL | IOD_ST3 | ST3:.ups_polnjenje
ST3UserLoggedIn | DIGITAL | IOD_ST3 | ST3:.UserLoggedIn
ST3XVH_AlarmOn | DIGITAL | IOD_ST3 | ST3:.XVH_AlarmOn
ST3DateTimeDan | INT | IOD_ST3 | ST3:.DateTime.Dan | BYTE
ST3DateTimeLeto | INT | IOD_ST3 | ST3:.DateTime.Leto | BYTE
ST3DateTimeLeto2 | INT | IOD_ST3 | ST3:.DateTime.Leto2
ST3DateTimeMesec | INT | IOD_ST3 | ST3:.DateTime.Mesec | BYTE
ST3DateTimeMinuta | INT | IOD_ST3 | ST3:.DateTime.Minuta | BYTE
ST3DateTimeSekunda | INT | IOD_ST3 | ST3:.DateTime.Sekunda | BYTE
ST3DateTimeUra | INT | IOD_ST3 | ST3:.DateTime.Ura | BYTE
ST3HIA1_vlaga_s | INT | IOD_ST3 | ST3:.HIA1_vlaga_s
ST3HIA2_vlaga_s | INT | IOD_ST3 | ST3:.HIA2_vlaga_s
ST3HIA3_vlaga_s | INT | IOD_ST3 | ST3:.HIA3_vlaga_s
ST3HIA4_vlaga_s | INT | IOD_ST3 | ST3:.HIA4_vlaga_s
ST3HIA5_vlaga_s | INT | IOD_ST3 | ST3:.HIA5_vlaga_s
ST3HIA6_vlaga_s | INT | IOD_ST3 | ST3:.HIA6_vlaga_s
ST3HIA7_vlaga_s | INT | IOD_ST3 | ST3:.HIA7_vlaga_s
ST3HIA8_vlaga_s | INT | IOD_ST3 | ST3:.HIA8_vlaga_s
ST3TIA1_alarm | INT | IOD_ST3 | ST3:.TIA1_alarm
ST3TIA1_temp_s | INT | IOD_ST3 | ST3:.TIA1_temp_s
ST3TIA2_alarm | INT | IOD_ST3 | ST3:.TIA2_alarm
ST3TIA2_temp_s | INT | IOD_ST3 | ST3:.TIA2_temp_s
ST3TIA3_alarm | INT | IOD_ST3 | ST3:.TIA3_alarm
ST3TIA3_temp_s | INT | IOD_ST3 | ST3:.TIA3_temp_s
ST3TIA4_alarm | INT | IOD_ST3 | ST3:.TIA4_alarm
ST3TIA4_temp_s | INT | IOD_ST3 | ST3:.TIA4_temp_s
ST3TIA5_alarm | INT | IOD_ST3 | ST3:.TIA5_alarm
ST3TIA5_temp_s | INT | IOD_ST3 | ST3:.TIA5_temp_s
ST3TIA6_alarm | INT | IOD_ST3 | ST3:.TIA6_alarm
ST3TIA6_temp_s | INT | IOD_ST3 | ST3:.TIA6_temp_s
ST3TIA7_alarm | INT | IOD_ST3 | ST3:.TIA7_alarm
ST3TIA7_temp_s | INT | IOD_ST3 | ST3:.TIA7_temp_s
ST3TIA8_alarm | INT | IOD_ST3 | ST3:.TIA8_alarm
ST3TIA8_temp_s | INT | IOD_ST3 | ST3:.TIA8_temp_s
ST3UserCurrentLevel | INT | IOD_ST3 | ST3:.UserCurrentLevel | BYTE
ST3XVH_UPSstatus | INT | IOD_ST3 | ST3:.XVH_UPSstatus | BYTE
ST3rVersion | REAL | IOD_ST3 | ST3:.rVersion
ST3XVHdepltedBatery1 | REAL | IOD_ST3 | ST3:.XVHdepltedBatery1
ST3XVHdepltedBatery2 | REAL | IOD_ST3 | ST3:.XVHdepltedBatery2
ST3XVHlowBatery1 | REAL | IOD_ST3 | ST3:.XVHlowBatery1
ST3XVHlowBatery2 | REAL | IOD_ST3 | ST3:.XVHlowBatery2
ST3Date_Time0 | STRING | IOD_ST3 | ST3:.Date_Time[0]
ST3Date_Time1 | STRING | IOD_ST3 | ST3:.Date_Time[1]
ST3Date_Time2 | STRING | IOD_ST3 | ST3:.Date_Time[2]
ST3Date_Time3 | STRING | IOD_ST3 | ST3:.Date_Time[3]
ST3UserCurrentName | STRING | IOD_ST3 | ST3:.UserCurrentName
ST3kom_nast_cas_izpada | UINT | IOD_ST3 | ST3:.kom_nast_cas_izpada

## variable_3
ST3ComError | DIGITAL | IOD_ST3_TCP | 1 | 00001 | ComError
ST3ComSCADA | DIGITAL | IOD_ST3_TCP | 2 | 00002 | ComSCADA
ST3ComSCADA1 | DIGITAL | IOD_ST3_TCP | 3 | 00003 | ComSCADA1
ST3ComSCADA2 | DIGITAL | IOD_ST3_TCP | 4 | 00004 | ComSCADA2
ST3ComSCADA3 | DIGITAL | IOD_ST3_TCP | 5 | 00005 | ComSCADA3
ST3napaka_kom_panel | DIGITAL | IOD_ST3_TCP | 6 | 00006 | napaka_kom_panel
ST3napaka_kom_scada | DIGITAL | IOD_ST3_TCP | 7 | 00007 | napaka_kom_scada
ST3napaka_kom_scada2 | DIGITAL | IOD_ST3_TCP | 8 | 00008 | napaka_kom_scada2
ST3NapakaSenzorSkupno | DIGITAL | IOD_ST3_TCP | 9 | 00009 | NapakaSenzorSkupno
ST3NapakaSenzorVlagaHIA1 | DIGITAL | IOD_ST3_TCP | 10 | 00010 | NapakaSenzorVlagaHIA1
ST3NapakaSenzorVlagaHIA2 | DIGITAL | IOD_ST3_TCP | 11 | 00011 | NapakaSenzorVlagaHIA2
ST3NapakaSenzorVlagaHIA3 | DIGITAL | IOD_ST3_TCP | 12 | 00012 | NapakaSenzorVlagaHIA3
ST3NapakaSenzorVlagaHIA4 | DIGITAL | IOD_ST3_TCP | 13 | 00013 | NapakaSenzorVlagaHIA4
ST3NapakaSenzorVlagaHIA5 | DIGITAL | IOD_ST3_TCP | 14 | 00014 | NapakaSenzorVlagaHIA5
ST3NapakaSenzorVlagaHIA6 | DIGITAL | IOD_ST3_TCP | 15 | 00015 | NapakaSenzorVlagaHIA6
ST3NapakaSenzorVlagaHIA7 | DIGITAL | IOD_ST3_TCP | 16 | 00016 | NapakaSenzorVlagaHIA7
ST3NapakaSenzorVlagaHIA8 | DIGITAL | IOD_ST3_TCP | 17 | 00017 | NapakaSenzorVlagaHIA8
ST3NapakaTSTempTIA1 | DIGITAL | IOD_ST3_TCP | 18 | 00018 | NapakaTSTempTIA1
ST3NapakaTSTempTIA2 | DIGITAL | IOD_ST3_TCP | 19 | 00019 | NapakaTSTempTIA2
ST3NapakaTSTempTIA3 | DIGITAL | IOD_ST3_TCP | 20 | 00020 | NapakaTSTempTIA3
ST3NapakaTSTempTIA4 | DIGITAL | IOD_ST3_TCP | 21 | 00021 | NapakaTSTempTIA4
ST3NapakaTSTempTIA5 | DIGITAL | IOD_ST3_TCP | 22 | 00022 | NapakaTSTempTIA5
ST3NapakaTSTempTIA6 | DIGITAL | IOD_ST3_TCP | 23 | 00023 | NapakaTSTempTIA6
ST3NapakaTSTempTIA7 | DIGITAL | IOD_ST3_TCP | 24 | 00024 | NapakaTSTempTIA7
ST3NapakaTSTempTIA8 | DIGITAL | IOD_ST3_TCP | 25 | 00025 | NapakaTSTempTIA8
ST3PrevisokaTemp | DIGITAL | IOD_ST3_TCP | 26 | 00026 | PrevisokaTemp
ST3razlitjeLAH1 | DIGITAL | IOD_ST3_TCP | 27 | 00027 | razlitjeLAH1
ST3razlitjeLAH2 | DIGITAL | IOD_ST3_TCP | 28 | 00028 | razlitjeLAH2
ST3razlitjeLAH3 | DIGITAL | IOD_ST3_TCP | 29 | 00029 | razlitjeLAH3
ST3razlitjeLAH4 | DIGITAL | IOD_ST3_TCP | 30 | 00030 | razlitjeLAH4
ST3razlitjeLAH5 | DIGITAL | IOD_ST3_TCP | 31 | 00031 | razlitjeLAH5
ST3razlitjeLAH6 | DIGITAL | IOD_ST3_TCP | 32 | 00032 | razlitjeLAH6
ST3razlitjeLAH7 | DIGITAL | IOD_ST3_TCP | 33 | 00033 | razlitjeLAH7
ST3razlitjeLAH8 | DIGITAL | IOD_ST3_TCP | 34 | 00034 | razlitjeLAH8
ST3SetDateTime | DIGITAL | IOD_ST3_TCP | 35 | 00035 | SetDateTime
ST3SetDateTimeDemand | DIGITAL | IOD_ST3_TCP | 36 | 00036 | SetDateTimeDemand
ST3SetDateTimeError | DIGITAL | IOD_ST3_TCP | 37 | 00037 | SetDateTimeError
ST3SetDateTimeFinished | DIGITAL | IOD_ST3_TCP | 38 | 00038 | SetDateTimeFinished
ST3SlabaBaterijaPLC | DIGITAL | IOD_ST3_TCP | 39 | 00039 | SlabaBaterijaPLC
ST3TIA1_previs_temp | DIGITAL | IOD_ST3_TCP | 40 | 00040 | TIA1_previs_temp
ST3TIA2_previs_temp | DIGITAL | IOD_ST3_TCP | 41 | 00041 | TIA2_previs_temp
ST3TIA3_previs_temp | DIGITAL | IOD_ST3_TCP | 42 | 00042 | TIA3_previs_temp
ST3TIA4_previs_temp | DIGITAL | IOD_ST3_TCP | 43 | 00043 | TIA4_previs_temp
ST3TIA5_previs_temp | DIGITAL | IOD_ST3_TCP | 44 | 00044 | TIA5_previs_temp
ST3TIA6_previs_temp | DIGITAL | IOD_ST3_TCP | 45 | 00045 | TIA6_previs_temp
ST3TIA7_previs_temp | DIGITAL | IOD_ST3_TCP | 46 | 00046 | TIA7_previs_temp
ST3TIA8_previs_temp | DIGITAL | IOD_ST3_TCP | 47 | 00047 | TIA8_previs_temp
ST3ups_alarm | DIGITAL | IOD_ST3_TCP | 48 | 00048 | ups_alarm
ST3ups_baterijski_nac | DIGITAL | IOD_ST3_TCP | 49 | 00049 | ups_baterijski_nac
ST3ups_polnjenje | DIGITAL | IOD_ST3_TCP | 50 | 00050 | ups_polnjenje
ST3UserLoggedIn | DIGITAL | IOD_ST3_TCP | 51 | 00051 | UserLoggedIn
ST3XVH_AlarmOn | DIGITAL | IOD_ST3_TCP | 52 | 00052 | XVH_AlarmOn
ST3DateTimeDan | INT | IOD_ST3_TCP | 1 | 40001 | DateTime.Dan | BYTE
ST3DateTimeLeto | INT | IOD_ST3_TCP | 2 | 40002 | DateTime.Leto | BYTE
ST3DateTimeLeto2 | INT | IOD_ST3_TCP | 3 | 40003 | DateTime.Leto2
ST3DateTimeMesec | INT | IOD_ST3_TCP | 4 | 40004 | DateTime.Mesec | BYTE
ST3DateTimeMinuta | INT | IOD_ST3_TCP | 5 | 40005 | DateTime.Minuta | BYTE
ST3DateTimeSekunda | INT | IOD_ST3_TCP | 6 | 40006 | DateTime.Sekunda | BYTE
ST3DateTimeUra | INT | IOD_ST3_TCP | 7 | 40007 | DateTime.Ura | BYTE
ST3HIA1_vlaga_s | INT | IOD_ST3_TCP | 8 | 40008 | HIA1_vlaga_s
ST3HIA2_vlaga_s | INT | IOD_ST3_TCP | 9 | 40009 | HIA2_vlaga_s
ST3HIA3_vlaga_s | INT | IOD_ST3_TCP | 10 | 40010 | HIA3_vlaga_s
ST3HIA4_vlaga_s | INT | IOD_ST3_TCP | 11 | 40011 | HIA4_vlaga_s
ST3HIA5_vlaga_s | INT | IOD_ST3_TCP | 12 | 40012 | HIA5_vlaga_s
ST3HIA6_vlaga_s | INT | IOD_ST3_TCP | 13 | 40013 | HIA6_vlaga_s
ST3HIA7_vlaga_s | INT | IOD_ST3_TCP | 14 | 40014 | HIA7_vlaga_s
ST3HIA8_vlaga_s | INT | IOD_ST3_TCP | 15 | 40015 | HIA8_vlaga_s
ST3TIA1_alarm | INT | IOD_ST3_TCP | 16 | 40016 | TIA1_alarm
ST3TIA1_temp_s | INT | IOD_ST3_TCP | 17 | 40017 | TIA1_temp_s
ST3TIA2_alarm | INT | IOD_ST3_TCP | 18 | 40018 | TIA2_alarm
ST3TIA2_temp_s | INT | IOD_ST3_TCP | 19 | 40019 | TIA2_temp_s
ST3TIA3_alarm | INT | IOD_ST3_TCP | 20 | 40020 | TIA3_alarm
ST3TIA3_temp_s | INT | IOD_ST3_TCP | 21 | 40021 | TIA3_temp_s
ST3TIA4_alarm | INT | IOD_ST3_TCP | 22 | 40022 | TIA4_alarm
ST3TIA4_temp_s | INT | IOD_ST3_TCP | 23 | 40023 | TIA4_temp_s
ST3TIA5_alarm | INT | IOD_ST3_TCP | 24 | 40024 | TIA5_alarm
ST3TIA5_temp_s | INT | IOD_ST3_TCP | 25 | 40025 | TIA5_temp_s
ST3TIA6_alarm | INT | IOD_ST3_TCP | 26 | 40026 | TIA6_alarm
ST3TIA6_temp_s | INT | IOD_ST3_TCP | 27 | 40027 | TIA6_temp_s
ST3TIA7_alarm | INT | IOD_ST3_TCP | 28 | 40028 | TIA7_alarm
ST3TIA7_temp_s | INT | IOD_ST3_TCP | 29 | 40029 | TIA7_temp_s
ST3TIA8_alarm | INT | IOD_ST3_TCP | 30 | 40030 | TIA8_alarm
ST3TIA8_temp_s | INT | IOD_ST3_TCP | 31 | 40031 | TIA8_temp_s
ST3UserCurrentLevel | INT | IOD_ST3_TCP | 32 | 40032 | UserCurrentLevel | BYTE
ST3XVH_UPSstatus | INT | IOD_ST3_TCP | 33 | 40033 | XVH_UPSstatus | BYTE
ST3rVersion | REAL | IOD_ST3_TCP | 4001 | 44001 | rVersion
ST3XVHdepltedBatery1 | REAL | IOD_ST3_TCP | 4003 | 44003 | XVHdepltedBatery1
ST3XVHdepltedBatery2 | REAL | IOD_ST3_TCP | 4005 | 44005 | XVHdepltedBatery2
ST3XVHlowBatery1 | REAL | IOD_ST3_TCP | 4007 | 44007 | XVHlowBatery1
ST3XVHlowBatery2 | REAL | IOD_ST3_TCP | 4009 | 44009 | XVHlowBatery2
ST3Date_Time0 | STRING | IOD_ST3_TCP | 5001 | 45001[15] | Date_Time[0]
ST3Date_Time1 | STRING | IOD_ST3_TCP | 5016 | 45016[15] | Date_Time[1]
ST3Date_Time2 | STRING | IOD_ST3_TCP | 5031 | 45031[15] | Date_Time[2]
ST3Date_Time3 | STRING | IOD_ST3_TCP | 5046 | 45046[15] | Date_Time[3]
ST3UserCurrentName | STRING | IOD_ST3_TCP | 5061 | 45061[15] | UserCurrentName
ST3kom_nast_cas_izpada | UINT | IOD_ST3_TCP | 6001 | 46001 | kom_nast_cas_izpada

## variable_new
ST3ComError | DIGITAL | IOD_ST3_TCP | 00001
ST3ComSCADA | DIGITAL | IOD_ST3_TCP | 00002
ST3ComSCADA1 | DIGITAL | IOD_ST3_TCP | 00003
ST3ComSCADA2 | DIGITAL | IOD_ST3_TCP | 00004
ST3ComSCADA3 | DIGITAL | IOD_ST3_TCP | 00005
ST3Date_Time0 | STRING | IOD_ST3_TCP | 45001[15]
ST3Date_Time1 | STRING | IOD_ST3_TCP | 45016[15]
ST3Date_Time2 | STRING | IOD_ST3_TCP | 45031[15]
ST3Date_Time3 | STRING | IOD_ST3_TCP | 45046[15]
ST3DateTimeDan | INT | IOD_ST3_TCP | 40001
ST3DateTimeLeto | INT | IOD_ST3_TCP | 40002
ST3DateTimeLeto2 | INT | IOD_ST3_TCP | 40003
ST3DateTimeMesec | INT | IOD_ST3_TCP | 40004
ST3DateTimeMinuta | INT | IOD_ST3_TCP | 40005
ST3DateTimeSekunda | INT | IOD_ST3_TCP | 40006
ST3DateTimeUra | INT | IOD_ST3_TCP | 40007
ST3HIA1_vlaga_s | INT | IOD_ST3_TCP | 40008 | 0 | 1000 | 0 | 100 | % | ###.#
ST3HIA2_vlaga_s | INT | IOD_ST3_TCP | 40009 | 0 | 1000 | 0 | 100 | % | ###.#
ST3HIA3_vlaga_s | INT | IOD_ST3_TCP | 40010 | 0 | 1000 | 0 | 100 | % | ###.#
ST3HIA4_vlaga_s | INT | IOD_ST3_TCP | 40011 | 0 | 1000 | 0 | 100 | % | ###.#
ST3HIA5_vlaga_s | INT | IOD_ST3_TCP | 40012 | 0 | 1000 | 0 | 100 | % | ###.#
ST3HIA6_vlaga_s | INT | IOD_ST3_TCP | 40013 | 0 | 1000 | 0 | 100 | % | ###.#
ST3HIA7_vlaga_s | INT | IOD_ST3_TCP | 40014 | 0 | 1000 | 0 | 100 | % | ###.#
ST3HIA8_vlaga_s | INT | IOD_ST3_TCP | 40015 | 0 | 1000 | 0 | 100 | % | ###.#
ST3kom_nast_cas_izpada | UINT | IOD_ST3_TCP | 46001
ST3napaka_kom_panel | DIGITAL | IOD_ST3_TCP | 00006
ST3napaka_kom_scada | DIGITAL | IOD_ST3_TCP | 00007
ST3napaka_kom_scada2 | DIGITAL | IOD_ST3_TCP | 00008
ST3NapakaSenzorSkupno | DIGITAL | IOD_ST3_TCP | 00009
ST3NapakaSenzorVlagaHIA1 | DIGITAL | IOD_ST3_TCP | 00010
ST3NapakaSenzorVlagaHIA2 | DIGITAL | IOD_ST3_TCP | 00011
ST3NapakaSenzorVlagaHIA3 | DIGITAL | IOD_ST3_TCP | 00012
ST3NapakaSenzorVlagaHIA4 | DIGITAL | IOD_ST3_TCP | 00013
ST3NapakaSenzorVlagaHIA5 | DIGITAL | IOD_ST3_TCP | 00014
ST3NapakaSenzorVlagaHIA6 | DIGITAL | IOD_ST3_TCP | 00015
ST3NapakaSenzorVlagaHIA7 | DIGITAL | IOD_ST3_TCP | 00016
ST3NapakaSenzorVlagaHIA8 | DIGITAL | IOD_ST3_TCP | 00017
ST3NapakaTSTempTIA1 | DIGITAL | IOD_ST3_TCP | 00018
ST3NapakaTSTempTIA2 | DIGITAL | IOD_ST3_TCP | 00019
ST3NapakaTSTempTIA3 | DIGITAL | IOD_ST3_TCP | 00020
ST3NapakaTSTempTIA4 | DIGITAL | IOD_ST3_TCP | 00021
ST3NapakaTSTempTIA5 | DIGITAL | IOD_ST3_TCP | 00022
ST3NapakaTSTempTIA6 | DIGITAL | IOD_ST3_TCP | 00023
ST3NapakaTSTempTIA7 | DIGITAL | IOD_ST3_TCP | 00024
ST3NapakaTSTempTIA8 | DIGITAL | IOD_ST3_TCP | 00025
ST3PrevisokaTemp | DIGITAL | IOD_ST3_TCP | 00026
ST3razlitjeLAH1 | DIGITAL | IOD_ST3_TCP | 00027
ST3razlitjeLAH2 | DIGITAL | IOD_ST3_TCP | 00028
ST3razlitjeLAH3 | DIGITAL | IOD_ST3_TCP | 00029
ST3razlitjeLAH4 | DIGITAL | IOD_ST3_TCP | 00030
ST3razlitjeLAH5 | DIGITAL | IOD_ST3_TCP | 00031
ST3razlitjeLAH6 | DIGITAL | IOD_ST3_TCP | 00032
ST3razlitjeLAH7 | DIGITAL | IOD_ST3_TCP | 00033
ST3razlitjeLAH8 | DIGITAL | IOD_ST3_TCP | 00034
ST3rVersion | REAL | IOD_ST3_TCP | 44001
ST3SetDateTime | DIGITAL | IOD_ST3_TCP | 00035
ST3SetDateTimeDemand | DIGITAL | IOD_ST3_TCP | 00036
ST3SetDateTimeError | DIGITAL | IOD_ST3_TCP | 00037
ST3SetDateTimeFinished | DIGITAL | IOD_ST3_TCP | 00038
ST3SlabaBaterijaPLC | DIGITAL | IOD_ST3_TCP | 00039
ST3TIA1_alarm | INT | IOD_ST3_TCP | 40016 | 0 | 60 | 0 | 60 | °C | ##
ST3TIA1_previs_temp | DIGITAL | IOD_ST3_TCP | 00040
ST3TIA1_temp_s | INT | IOD_ST3_TCP | 40017 | 0 | 600 | 0 | 60 | °C | ##.#
ST3TIA2_alarm | INT | IOD_ST3_TCP | 40018 | 0 | 60 | 0 | 60 | °C | ##
ST3TIA2_previs_temp | DIGITAL | IOD_ST3_TCP | 00041
ST3TIA2_temp_s | INT | IOD_ST3_TCP | 40019 | 0 | 600 | 0 | 60 | °C | ##.#
ST3TIA3_alarm | INT | IOD_ST3_TCP | 40020 | 0 | 60 | 0 | 60 | °C | ##
ST3TIA3_previs_temp | DIGITAL | IOD_ST3_TCP | 00042
ST3TIA3_temp_s | INT | IOD_ST3_TCP | 40021 | 0 | 600 | 0 | 60 | °C | ##.#
ST3TIA4_alarm | INT | IOD_ST3_TCP | 40022 | 0 | 60 | 0 | 60 | °C | ##
ST3TIA4_previs_temp | DIGITAL | IOD_ST3_TCP | 00043
ST3TIA4_temp_s | INT | IOD_ST3_TCP | 40023 | 0 | 600 | 0 | 60 | °C | ##.#
ST3TIA5_alarm | INT | IOD_ST3_TCP | 40024 | 0 | 60 | 0 | 60 | °C | ##
ST3TIA5_previs_temp | DIGITAL | IOD_ST3_TCP | 00044
ST3TIA5_temp_s | INT | IOD_ST3_TCP | 40025 | 0 | 600 | 0 | 60 | °C | ##.#
ST3TIA6_alarm | INT | IOD_ST3_TCP | 40026 | 0 | 60 | 0 | 60 | °C | ##
ST3TIA6_previs_temp | DIGITAL | IOD_ST3_TCP | 00045
ST3TIA6_temp_s | INT | IOD_ST3_TCP | 40027 | 0 | 600 | 0 | 60 | °C | ##.#
ST3TIA7_alarm | INT | IOD_ST3_TCP | 40028 | 0 | 60 | 0 | 60 | °C | ##
ST3TIA7_previs_temp | DIGITAL | IOD_ST3_TCP | 00046
ST3TIA7_temp_s | INT | IOD_ST3_TCP | 40029 | 0 | 600 | 0 | 60 | °C | ##.#
ST3TIA8_alarm | INT | IOD_ST3_TCP | 40030 | 0 | 60 | 0 | 60 | °C | ##
ST3TIA8_previs_temp | DIGITAL | IOD_ST3_TCP | 00047
ST3TIA8_temp_s | INT | IOD_ST3_TCP | 40031 | 0 | 600 | 0 | 60 | °C | ##.#
ST3ups_alarm | DIGITAL | IOD_ST3_TCP | 00048
ST3ups_baterijski_nac | DIGITAL | IOD_ST3_TCP | 00049
ST3ups_polnjenje | DIGITAL | IOD_ST3_TCP | 00050
ST3UserCurrentLevel | INT | IOD_ST3_TCP | 40032
ST3UserCurrentName | STRING | IOD_ST3_TCP | 45061[15]
ST3UserLoggedIn | DIGITAL | IOD_ST3_TCP | 00051
ST3XVH_AlarmOn | DIGITAL | IOD_ST3_TCP | 00052
ST3XVH_UPSstatus | INT | IOD_ST3_TCP | 40033
ST3XVHdepltedBatery1 | REAL | IOD_ST3_TCP | 44003
ST3XVHdepltedBatery2 | REAL | IOD_ST3_TCP | 44005
ST3XVHlowBatery1 | REAL | IOD_ST3_TCP | 44007
ST3XVHlowBatery2 | REAL | IOD_ST3_TCP | 44009
ST3Server_B_Izpad | DIGITAL | IOD_ST3_mem | D200
ST3Server_A_Izpad | DIGITAL | IOD_ST3_mem | D201
AST3_omogoci_sms | DIGITAL | IOD_ST3_disk | D1[100]
ST3NapakaSenzorVlagaHIA1_om | DIGITAL | IOD_ST3_disk | D102
ST3NapakaSenzorVlagaHIA2_om | DIGITAL | IOD_ST3_disk | D103
ST3NapakaSenzorVlagaHIA3_om | DIGITAL | IOD_ST3_disk | D104
ST3NapakaSenzorVlagaHIA4_om | DIGITAL | IOD_ST3_disk | D105
ST3NapakaSenzorVlagaHIA5_om | DIGITAL | IOD_ST3_disk | D106
ST3NapakaSenzorVlagaHIA6_om | DIGITAL | IOD_ST3_disk | D107
ST3NapakaSenzorVlagaHIA7_om | DIGITAL | IOD_ST3_disk | D108
ST3NapakaSenzorVlagaHIA8_om | DIGITAL | IOD_ST3_disk | D109
ST3NapakaTSTempTIA1_om | DIGITAL | IOD_ST3_disk | D110
ST3NapakaTSTempTIA2_om | DIGITAL | IOD_ST3_disk | D111
ST3NapakaTSTempTIA3_om | DIGITAL | IOD_ST3_disk | D112
ST3NapakaTSTempTIA4_om | DIGITAL | IOD_ST3_disk | D113
ST3NapakaTSTempTIA5_om | DIGITAL | IOD_ST3_disk | D114
ST3NapakaTSTempTIA6_om | DIGITAL | IOD_ST3_disk | D115
ST3NapakaTSTempTIA7_om | DIGITAL | IOD_ST3_disk | D116
ST3NapakaTSTempTIA8_om | DIGITAL | IOD_ST3_disk | D117
ST3TIA1_previs_temp_om | DIGITAL | IOD_ST3_disk | D118
ST3TIA2_previs_temp_om | DIGITAL | IOD_ST3_disk | D119
ST3TIA3_previs_temp_om | DIGITAL | IOD_ST3_disk | D120
ST3TIA4_previs_temp_om | DIGITAL | IOD_ST3_disk | D121
ST3TIA5_previs_temp_om | DIGITAL | IOD_ST3_disk | D122
ST3TIA6_previs_temp_om | DIGITAL | IOD_ST3_disk | D123
ST3TIA7_previs_temp_om | DIGITAL | IOD_ST3_disk | D124
ST3TIA8_previs_temp_om | DIGITAL | IOD_ST3_disk | D125
ST3razlitjeLAH1_om | DIGITAL | IOD_ST3_disk | D126
ST3razlitjeLAH2_om | DIGITAL | IOD_ST3_disk | D127
ST3razlitjeLAH3_om | DIGITAL | IOD_ST3_disk | D128
ST3razlitjeLAH4_om | DIGITAL | IOD_ST3_disk | D129
ST3razlitjeLAH5_om | DIGITAL | IOD_ST3_disk | D130
ST3razlitjeLAH6_om | DIGITAL | IOD_ST3_disk | D131
ST3razlitjeLAH7_om | DIGITAL | IOD_ST3_disk | D132
ST3razlitjeLAH8_om | DIGITAL | IOD_ST3_disk | D133
ST3Server_A_Izpad_om | DIGITAL | IOD_ST3_disk | D134
ST3Server_B_Izpad_om | DIGITAL | IOD_ST3_disk | D135
ST3napaka_kom_panel_om | DIGITAL | IOD_ST3_disk | D136
ST3SetDateTimeError_om | DIGITAL | IOD_ST3_disk | D137
ST3SlabaBaterijaPLC_om | DIGITAL | IOD_ST3_disk | D138
ST3ups_baterijski_nac_om | DIGITAL | IOD_ST3_disk | D139
ST3ups_alarm_om | DIGITAL | IOD_ST3_disk | D140
ST3ups_polnjenje_om | DIGITAL | IOD_ST3_disk | D141
ST3UserloggedIn_mem | INT | IOD_ST3_mem | I1
ST3_ComSCADA_stevec1 | INT | IOD_ST3_mem | I2
ST3_ComSCADA_stevec2 | INT | IOD_ST3_mem | I3
ST3_ComSCADA_stevec3 | INT | IOD_ST3_mem | I4
ST3_ComSCADA_stevec4 | INT | IOD_ST3_mem | I5
BST3_omogoci_sms | DIGITAL | IOD_ST3_disk | D200[100]

## XSoft
mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Write_BOOL(FC) | mod_Write_Word(FC) | mod_Write_Word(FC) | mod_Write_dWord(FC) | mod_Write_dWord(FC) | mod_Write_String(FC)
(*Branje BOOL*) | (*Branje INT*) | (*Branje UINT*) | (*Branje LONG*) | (*Branje REAL*) | (*Branje STRING*) | (*Pisanje BOOL*) | (*Pisanje INT*) | (*Pisanje UINT*) | (*Pisanje LONG*) | (*Pisanje REAL*) | (*Pisanje STRING*)
(**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**)
mind_bool[0]:=ComError; | mind[0]:=DateTime.Dan; | mind[6000]:=kom_nast_cas_izpada; |  | Read_Real(rVar:=rVersion,lo:=4000,hi:=4001); | Read_String(sVar:=Date_Time[0],start:=5000); | 0:ComError:=Bit_0; | 0:DateTime.Dan:=Byte_0; | 6000:kom_nast_cas_izpada:=Word_01; |  | 4001:rVersion:=Real_0; | 5000:Date_Time[0]:=String_0;
mind_bool[1]:=ComSCADA; | mind[1]:=DateTime.Leto; |  |  | Read_Real(rVar:=XVHdepltedBatery1,lo:=4002,hi:=4003); | Read_String(sVar:=Date_Time[1],start:=5015); | 1:ComSCADA:=Bit_0; | 1:DateTime.Leto:=Byte_0; |  |  | 4003:XVHdepltedBatery1:=Real_0; | 5015:Date_Time[1]:=String_0;
mind_bool[2]:=ComSCADA1; | mind[2]:=DateTime.Leto2; |  |  | Read_Real(rVar:=XVHdepltedBatery2,lo:=4004,hi:=4005); | Read_String(sVar:=Date_Time[2],start:=5030); | 2:ComSCADA1:=Bit_0; | 2:DateTime.Leto2:=Word_01; |  |  | 4005:XVHdepltedBatery2:=Real_0; | 5030:Date_Time[2]:=String_0;
mind_bool[3]:=ComSCADA2; | mind[3]:=DateTime.Mesec; |  |  | Read_Real(rVar:=XVHlowBatery1,lo:=4006,hi:=4007); | Read_String(sVar:=Date_Time[3],start:=5045); | 3:ComSCADA2:=Bit_0; | 3:DateTime.Mesec:=Byte_0; |  |  | 4007:XVHlowBatery1:=Real_0; | 5045:Date_Time[3]:=String_0;
mind_bool[4]:=ComSCADA3; | mind[4]:=DateTime.Minuta; |  |  | Read_Real(rVar:=XVHlowBatery2,lo:=4008,hi:=4009); | Read_String(sVar:=UserCurrentName,start:=5060); | 4:ComSCADA3:=Bit_0; | 4:DateTime.Minuta:=Byte_0; |  |  | 4009:XVHlowBatery2:=Real_0; | 5060:UserCurrentName:=String_0;
mind_bool[5]:=napaka_kom_panel; | mind[5]:=DateTime.Sekunda; |  |  |  |  | 5:napaka_kom_panel:=Bit_0; | 5:DateTime.Sekunda:=Byte_0;
mind_bool[6]:=napaka_kom_scada; | mind[6]:=DateTime.Ura; |  |  |  |  | 6:napaka_kom_scada:=Bit_0; | 6:DateTime.Ura:=Byte_0;
mind_bool[7]:=napaka_kom_scada2; | mind[7]:=HIA1_vlaga_s; |  |  |  |  | 7:napaka_kom_scada2:=Bit_0; | 7:HIA1_vlaga_s:=Word_01;
mind_bool[8]:=NapakaSenzorSkupno; | mind[8]:=HIA2_vlaga_s; |  |  |  |  | 8:NapakaSenzorSkupno:=Bit_0; | 8:HIA2_vlaga_s:=Word_01;
mind_bool[9]:=NapakaSenzorVlagaHIA1; | mind[9]:=HIA3_vlaga_s; |  |  |  |  | 9:NapakaSenzorVlagaHIA1:=Bit_0; | 9:HIA3_vlaga_s:=Word_01;
mind_bool[10]:=NapakaSenzorVlagaHIA2; | mind[10]:=HIA4_vlaga_s; |  |  |  |  | 10:NapakaSenzorVlagaHIA2:=Bit_0; | 10:HIA4_vlaga_s:=Word_01;
mind_bool[11]:=NapakaSenzorVlagaHIA3; | mind[11]:=HIA5_vlaga_s; |  |  |  |  | 11:NapakaSenzorVlagaHIA3:=Bit_0; | 11:HIA5_vlaga_s:=Word_01;
mind_bool[12]:=NapakaSenzorVlagaHIA4; | mind[12]:=HIA6_vlaga_s; |  |  |  |  | 12:NapakaSenzorVlagaHIA4:=Bit_0; | 12:HIA6_vlaga_s:=Word_01;
mind_bool[13]:=NapakaSenzorVlagaHIA5; | mind[13]:=HIA7_vlaga_s; |  |  |  |  | 13:NapakaSenzorVlagaHIA5:=Bit_0; | 13:HIA7_vlaga_s:=Word_01;
mind_bool[14]:=NapakaSenzorVlagaHIA6; | mind[14]:=HIA8_vlaga_s; |  |  |  |  | 14:NapakaSenzorVlagaHIA6:=Bit_0; | 14:HIA8_vlaga_s:=Word_01;
mind_bool[15]:=NapakaSenzorVlagaHIA7; | mind[15]:=TIA1_alarm; |  |  |  |  | 15:NapakaSenzorVlagaHIA7:=Bit_0; | 15:TIA1_alarm:=Word_01;
mind_bool[16]:=NapakaSenzorVlagaHIA8; | mind[16]:=TIA1_temp_s; |  |  |  |  | 16:NapakaSenzorVlagaHIA8:=Bit_0; | 16:TIA1_temp_s:=Word_01;
mind_bool[17]:=NapakaTSTempTIA1; | mind[17]:=TIA2_alarm; |  |  |  |  | 17:NapakaTSTempTIA1:=Bit_0; | 17:TIA2_alarm:=Word_01;
mind_bool[18]:=NapakaTSTempTIA2; | mind[18]:=TIA2_temp_s; |  |  |  |  | 18:NapakaTSTempTIA2:=Bit_0; | 18:TIA2_temp_s:=Word_01;
mind_bool[19]:=NapakaTSTempTIA3; | mind[19]:=TIA3_alarm; |  |  |  |  | 19:NapakaTSTempTIA3:=Bit_0; | 19:TIA3_alarm:=Word_01;
mind_bool[20]:=NapakaTSTempTIA4; | mind[20]:=TIA3_temp_s; |  |  |  |  | 20:NapakaTSTempTIA4:=Bit_0; | 20:TIA3_temp_s:=Word_01;
mind_bool[21]:=NapakaTSTempTIA5; | mind[21]:=TIA4_alarm; |  |  |  |  | 21:NapakaTSTempTIA5:=Bit_0; | 21:TIA4_alarm:=Word_01;
mind_bool[22]:=NapakaTSTempTIA6; | mind[22]:=TIA4_temp_s; |  |  |  |  | 22:NapakaTSTempTIA6:=Bit_0; | 22:TIA4_temp_s:=Word_01;
mind_bool[23]:=NapakaTSTempTIA7; | mind[23]:=TIA5_alarm; |  |  |  |  | 23:NapakaTSTempTIA7:=Bit_0; | 23:TIA5_alarm:=Word_01;
mind_bool[24]:=NapakaTSTempTIA8; | mind[24]:=TIA5_temp_s; |  |  |  |  | 24:NapakaTSTempTIA8:=Bit_0; | 24:TIA5_temp_s:=Word_01;
mind_bool[25]:=PrevisokaTemp; | mind[25]:=TIA6_alarm; |  |  |  |  | 25:PrevisokaTemp:=Bit_0; | 25:TIA6_alarm:=Word_01;
mind_bool[26]:=razlitjeLAH1; | mind[26]:=TIA6_temp_s; |  |  |  |  | 26:razlitjeLAH1:=Bit_0; | 26:TIA6_temp_s:=Word_01;
mind_bool[27]:=razlitjeLAH2; | mind[27]:=TIA7_alarm; |  |  |  |  | 27:razlitjeLAH2:=Bit_0; | 27:TIA7_alarm:=Word_01;
mind_bool[28]:=razlitjeLAH3; | mind[28]:=TIA7_temp_s; |  |  |  |  | 28:razlitjeLAH3:=Bit_0; | 28:TIA7_temp_s:=Word_01;
mind_bool[29]:=razlitjeLAH4; | mind[29]:=TIA8_alarm; |  |  |  |  | 29:razlitjeLAH4:=Bit_0; | 29:TIA8_alarm:=Word_01;
mind_bool[30]:=razlitjeLAH5; | mind[30]:=TIA8_temp_s; |  |  |  |  | 30:razlitjeLAH5:=Bit_0; | 30:TIA8_temp_s:=Word_01;
mind_bool[31]:=razlitjeLAH6; | mind[31]:=UserCurrentLevel; |  |  |  |  | 31:razlitjeLAH6:=Bit_0; | 31:UserCurrentLevel:=Byte_0;
mind_bool[32]:=razlitjeLAH7; | mind[32]:=XVH_UPSstatus; |  |  |  |  | 32:razlitjeLAH7:=Bit_0; | 32:XVH_UPSstatus:=Byte_0;
mind_bool[33]:=razlitjeLAH8; | [5 empty] | 33:razlitjeLAH8:=Bit_0;
mind_bool[34]:=SetDateTime; | [5 empty] | 34:SetDateTime:=Bit_0;
mind_bool[35]:=SetDateTimeDemand; | [5 empty] | 35:SetDateTimeDemand:=Bit_0;
mind_bool[36]:=SetDateTimeError; | [5 empty] | 36:SetDateTimeError:=Bit_0;
mind_bool[37]:=SetDateTimeFinished; | [5 empty] | 37:SetDateTimeFinished:=Bit_0;
mind_bool[38]:=SlabaBaterijaPLC; | [5 empty] | 38:SlabaBaterijaPLC:=Bit_0;
mind_bool[39]:=TIA1_previs_temp; | [5 empty] | 39:TIA1_previs_temp:=Bit_0;
mind_bool[40]:=TIA2_previs_temp; | [5 empty] | 40:TIA2_previs_temp:=Bit_0;
mind_bool[41]:=TIA3_previs_temp; | [5 empty] | 41:TIA3_previs_temp:=Bit_0;
mind_bool[42]:=TIA4_previs_temp; | [5 empty] | 42:TIA4_previs_temp:=Bit_0;
mind_bool[43]:=TIA5_previs_temp; | [5 empty] | 43:TIA5_previs_temp:=Bit_0;
mind_bool[44]:=TIA6_previs_temp; | [5 empty] | 44:TIA6_previs_temp:=Bit_0;
mind_bool[45]:=TIA7_previs_temp; | [5 empty] | 45:TIA7_previs_temp:=Bit_0;
mind_bool[46]:=TIA8_previs_temp; | [5 empty] | 46:TIA8_previs_temp:=Bit_0;
mind_bool[47]:=ups_alarm; | [5 empty] | 47:ups_alarm:=Bit_0;
mind_bool[48]:=ups_baterijski_nac; | [5 empty] | 48:ups_baterijski_nac:=Bit_0;
mind_bool[49]:=ups_polnjenje; | [5 empty] | 49:ups_polnjenje:=Bit_0;
mind_bool[50]:=UserLoggedIn; | [5 empty] | 50:UserLoggedIn:=Bit_0;
mind_bool[51]:=XVH_AlarmOn; | [5 empty] | 51:XVH_AlarmOn:=Bit_0;

## XSoft_EXP
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
PROGRAM mod_Read
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*Branje BOOL*)
(**)
mind_bool[0]:=ComError;
mind_bool[1]:=ComSCADA;
mind_bool[2]:=ComSCADA1;
mind_bool[3]:=ComSCADA2;
mind_bool[4]:=ComSCADA3;
mind_bool[5]:=napaka_kom_panel;
mind_bool[6]:=napaka_kom_scada;
mind_bool[7]:=napaka_kom_scada2;
mind_bool[8]:=NapakaSenzorSkupno;
mind_bool[9]:=NapakaSenzorVlagaHIA1;
mind_bool[10]:=NapakaSenzorVlagaHIA2;
mind_bool[11]:=NapakaSenzorVlagaHIA3;
mind_bool[12]:=NapakaSenzorVlagaHIA4;
mind_bool[13]:=NapakaSenzorVlagaHIA5;
mind_bool[14]:=NapakaSenzorVlagaHIA6;
mind_bool[15]:=NapakaSenzorVlagaHIA7;
mind_bool[16]:=NapakaSenzorVlagaHIA8;
mind_bool[17]:=NapakaTSTempTIA1;
mind_bool[18]:=NapakaTSTempTIA2;
mind_bool[19]:=NapakaTSTempTIA3;
mind_bool[20]:=NapakaTSTempTIA4;
mind_bool[21]:=NapakaTSTempTIA5;
mind_bool[22]:=NapakaTSTempTIA6;
mind_bool[23]:=NapakaTSTempTIA7;
mind_bool[24]:=NapakaTSTempTIA8;
mind_bool[25]:=PrevisokaTemp;
mind_bool[26]:=razlitjeLAH1;
mind_bool[27]:=razlitjeLAH2;
mind_bool[28]:=razlitjeLAH3;
mind_bool[29]:=razlitjeLAH4;
mind_bool[30]:=razlitjeLAH5;
mind_bool[31]:=razlitjeLAH6;
mind_bool[32]:=razlitjeLAH7;
mind_bool[33]:=razlitjeLAH8;
mind_bool[34]:=SetDateTime;
mind_bool[35]:=SetDateTimeDemand;
mind_bool[36]:=SetDateTimeError;
mind_bool[37]:=SetDateTimeFinished;
mind_bool[38]:=SlabaBaterijaPLC;
mind_bool[39]:=TIA1_previs_temp;
mind_bool[40]:=TIA2_previs_temp;
mind_bool[41]:=TIA3_previs_temp;
mind_bool[42]:=TIA4_previs_temp;
mind_bool[43]:=TIA5_previs_temp;
mind_bool[44]:=TIA6_previs_temp;
mind_bool[45]:=TIA7_previs_temp;
mind_bool[46]:=TIA8_previs_temp;
mind_bool[47]:=ups_alarm;
mind_bool[48]:=ups_baterijski_nac;
mind_bool[49]:=ups_polnjenje;
mind_bool[50]:=UserLoggedIn;
mind_bool[51]:=XVH_AlarmOn;
(*Branje INT*)
(**)
mind[0]:=DateTime.Dan;
mind[1]:=DateTime.Leto;
mind[2]:=DateTime.Leto2;
mind[3]:=DateTime.Mesec;
mind[4]:=DateTime.Minuta;
mind[5]:=DateTime.Sekunda;
mind[6]:=DateTime.Ura;
mind[7]:=HIA1_vlaga_s;
mind[8]:=HIA2_vlaga_s;
mind[9]:=HIA3_vlaga_s;
mind[10]:=HIA4_vlaga_s;
mind[11]:=HIA5_vlaga_s;
mind[12]:=HIA6_vlaga_s;
mind[13]:=HIA7_vlaga_s;
mind[14]:=HIA8_vlaga_s;
mind[15]:=TIA1_alarm;
mind[16]:=TIA1_temp_s;
mind[17]:=TIA2_alarm;
mind[18]:=TIA2_temp_s;
mind[19]:=TIA3_alarm;
mind[20]:=TIA3_temp_s;
mind[21]:=TIA4_alarm;
mind[22]:=TIA4_temp_s;
mind[23]:=TIA5_alarm;
mind[24]:=TIA5_temp_s;
mind[25]:=TIA6_alarm;
mind[26]:=TIA6_temp_s;
mind[27]:=TIA7_alarm;
mind[28]:=TIA7_temp_s;
mind[29]:=TIA8_alarm;
mind[30]:=TIA8_temp_s;
mind[31]:=UserCurrentLevel;
mind[32]:=XVH_UPSstatus;
(*Branje UINT*)
(**)
mind[6000]:=kom_nast_cas_izpada;
(*Branje LONG*)
(**)
(*Branje REAL*)
(**)
Read_Real(rVar:=rVersion,lo:=4000,hi:=4001);
Read_Real(rVar:=XVHdepltedBatery1,lo:=4002,hi:=4003);
Read_Real(rVar:=XVHdepltedBatery2,lo:=4004,hi:=4005);
Read_Real(rVar:=XVHlowBatery1,lo:=4006,hi:=4007);
Read_Real(rVar:=XVHlowBatery2,lo:=4008,hi:=4009);
(*Branje STRING*)
(**)
Read_String(sVar:=Date_Time[0],start:=5000);
Read_String(sVar:=Date_Time[1],start:=5015);
Read_String(sVar:=Date_Time[2],start:=5030);
Read_String(sVar:=Date_Time[3],start:=5045);
Read_String(sVar:=UserCurrentName,start:=5060);
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Bool : BOOL
VAR_INPUT
index: INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje BOOL*)
(**)
0:ComError:=Bit_0;
1:ComSCADA:=Bit_0;
2:ComSCADA1:=Bit_0;
3:ComSCADA2:=Bit_0;
4:ComSCADA3:=Bit_0;
5:napaka_kom_panel:=Bit_0;
6:napaka_kom_scada:=Bit_0;
7:napaka_kom_scada2:=Bit_0;
8:NapakaSenzorSkupno:=Bit_0;
9:NapakaSenzorVlagaHIA1:=Bit_0;
10:NapakaSenzorVlagaHIA2:=Bit_0;
11:NapakaSenzorVlagaHIA3:=Bit_0;
12:NapakaSenzorVlagaHIA4:=Bit_0;
13:NapakaSenzorVlagaHIA5:=Bit_0;
14:NapakaSenzorVlagaHIA6:=Bit_0;
15:NapakaSenzorVlagaHIA7:=Bit_0;
16:NapakaSenzorVlagaHIA8:=Bit_0;
17:NapakaTSTempTIA1:=Bit_0;
18:NapakaTSTempTIA2:=Bit_0;
19:NapakaTSTempTIA3:=Bit_0;
20:NapakaTSTempTIA4:=Bit_0;
21:NapakaTSTempTIA5:=Bit_0;
22:NapakaTSTempTIA6:=Bit_0;
23:NapakaTSTempTIA7:=Bit_0;
24:NapakaTSTempTIA8:=Bit_0;
25:PrevisokaTemp:=Bit_0;
26:razlitjeLAH1:=Bit_0;
27:razlitjeLAH2:=Bit_0;
28:razlitjeLAH3:=Bit_0;
29:razlitjeLAH4:=Bit_0;
30:razlitjeLAH5:=Bit_0;
31:razlitjeLAH6:=Bit_0;
32:razlitjeLAH7:=Bit_0;
33:razlitjeLAH8:=Bit_0;
34:SetDateTime:=Bit_0;
35:SetDateTimeDemand:=Bit_0;
36:SetDateTimeError:=Bit_0;
37:SetDateTimeFinished:=Bit_0;
38:SlabaBaterijaPLC:=Bit_0;
39:TIA1_previs_temp:=Bit_0;
40:TIA2_previs_temp:=Bit_0;
41:TIA3_previs_temp:=Bit_0;
42:TIA4_previs_temp:=Bit_0;
43:TIA5_previs_temp:=Bit_0;
44:TIA6_previs_temp:=Bit_0;
45:TIA7_previs_temp:=Bit_0;
46:TIA8_previs_temp:=Bit_0;
47:ups_alarm:=Bit_0;
48:ups_baterijski_nac:=Bit_0;
49:ups_polnjenje:=Bit_0;
50:UserLoggedIn:=Bit_0;
51:XVH_AlarmOn:=Bit_0;
(*BOOL*)
END_CASE
END_FUNCTION
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_dWord : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje LONG*)
(**)
(*Pisanje REAL*)
(**)
4001:rVersion:=Real_0;
4003:XVHdepltedBatery1:=Real_0;
4005:XVHdepltedBatery2:=Real_0;
4007:XVHlowBatery1:=Real_0;
4009:XVHlowBatery2:=Real_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_String : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje STRING*)
(**)
5000:Date_Time[0]:=String_0;
5015:Date_Time[1]:=String_0;
5030:Date_Time[2]:=String_0;
5045:Date_Time[3]:=String_0;
5060:UserCurrentName:=String_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Word : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje INT*)
(**)
0:DateTime.Dan:=Byte_0;
1:DateTime.Leto:=Byte_0;
2:DateTime.Leto2:=Word_01;
3:DateTime.Mesec:=Byte_0;
4:DateTime.Minuta:=Byte_0;
5:DateTime.Sekunda:=Byte_0;
6:DateTime.Ura:=Byte_0;
7:HIA1_vlaga_s:=Word_01;
8:HIA2_vlaga_s:=Word_01;
9:HIA3_vlaga_s:=Word_01;
10:HIA4_vlaga_s:=Word_01;
11:HIA5_vlaga_s:=Word_01;
12:HIA6_vlaga_s:=Word_01;
13:HIA7_vlaga_s:=Word_01;
14:HIA8_vlaga_s:=Word_01;
15:TIA1_alarm:=Word_01;
16:TIA1_temp_s:=Word_01;
17:TIA2_alarm:=Word_01;
18:TIA2_temp_s:=Word_01;
19:TIA3_alarm:=Word_01;
20:TIA3_temp_s:=Word_01;
21:TIA4_alarm:=Word_01;
22:TIA4_temp_s:=Word_01;
23:TIA5_alarm:=Word_01;
24:TIA5_temp_s:=Word_01;
25:TIA6_alarm:=Word_01;
26:TIA6_temp_s:=Word_01;
27:TIA7_alarm:=Word_01;
28:TIA7_temp_s:=Word_01;
29:TIA8_alarm:=Word_01;
30:TIA8_temp_s:=Word_01;
31:UserCurrentLevel:=Byte_0;
32:XVH_UPSstatus:=Byte_0;
(*Pisanje UINT*)
(**)
6000:kom_nast_cas_izpada:=Word_01;
;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
(*Modbus Slave Example*)
PROGRAM PLC_PRG_modnet
VAR
Slave_Adresa:BYTE:=2;
Slave_Port:INT:=502;
SlaveSetup:MBS_Setup;
SlavePoll:MBS_Poll;
SlaveAnswer:MBS_Answer;
step: USINT;
end :BOOL;
i: INT;
cycle :BOOL := FALSE; (* First cycle *)
OpenDefaultPort: BOOL;
Write_16: BOOL;
Write_15: BOOL;
Write_5: BOOL;
j: INT;
slavepollwOffset_temp: INT;
slaveanswerwCount_temp: INT;
slaveanswerwoffset_temp: INT;
END_VAR
(* @END_DECLARATION := '0' *)
(*Modbus Slave Example*)
IF Write_16=TRUE THEN (**)
FOR j := 0 TO (slaveanswerwCount_temp-1)/15 BY 1 DO (*vpiše se dword, real*)
wStr_0:=mind[slaveanswerwoffset_temp+j];
wStr_1:=mind[slaveanswerwoffset_temp+j+1];
wStr_2 :=mind[slaveanswerwoffset_temp+j+2];
wStr_3:=mind[slaveanswerwoffset_temp+j+3];
wStr_4:=mind[slaveanswerwoffset_temp+j+4];
wStr_5 :=mind[slaveanswerwoffset_temp+j+5];
wStr_6:=mind[slaveanswerwoffset_temp+j+6];
wStr_7:=mind[slaveanswerwoffset_temp+j+7];
wStr_8:=mind[slaveanswerwoffset_temp+j+8];
wStr_9:=mind[slaveanswerwoffset_temp+j+9];
wStr_10:=mind[slaveanswerwoffset_temp+j+10];
wStr_11:=mind[slaveanswerwoffset_temp+j+11];
wStr_12:=mind[slaveanswerwoffset_temp+j+12];
wStr_13:=mind[slaveanswerwoffset_temp+j+13];
wStr_14:=mind[slaveanswerwoffset_temp+j+14];
bStr_29:=0;
mod_Write_String(index:=slaveanswerwoffset_temp+j); (*vpis real in string*)
END_FOR;
FOR j := 1 TO slaveanswerwCount_temp-1 BY 2 DO (*vpiše se dword, real*)
Word_01:=mind[slaveanswerwoffset_temp+j-1];
Word_23:=mind[slaveanswerwoffset_temp+j];
mod_Write_dWord(index:=slaveanswerwoffset_temp+j); (*vpis real in dword*)
END_FOR;
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO (*vpiše se word*)
Word_01:=mind[slaveanswerwoffset_temp+j];
mod_Write_Word(index:=slaveanswerwoffset_temp+j); (*vpis word*)
END_FOR;
Write_16:=FALSE;
END_IF;
IF Write_5=TRUE OR Write_15=TRUE THEN (**)
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO
Bit_0:=mind_bool[slaveanswerwoffset_temp+j];
mod_Write_Bool(index:=slaveanswerwoffset_temp+j); (*vpis spremembe v spremenljivko*)
END_FOR;
Write_5:=FALSE;
Write_15:=FALSE;
END_IF;
(*iz scade ni komande za branje*)
IF Write_16=FALSE AND Write_5=FALSE AND Write_15=FALSE THEN
mod_Read();(*branje spremenljivk za scado*)
END_IF
(*Close all sockets on corresponding event*)
IF cycle = FALSE THEN
SysCallbackRegister(INDEXOF(Callback_Stop),event_stop);
SysCallbackRegister(INDEXOF(Callback_Reset),event_before_reset);
SysCallbackRegister(INDEXOF(Callback_Reset),event_shutdown);
cycle := TRUE;
END_IF
(*Close all connections via application *)
IF end = TRUE THEN
MBS_CloseAllConnections();
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=FALSE); (*Close port*)
step := 0;
END_IF
IF OpenDefaultPort=TRUE THEN
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=TRUE); (*Close port*)
step := 0;
OpenDefaultPort:=FALSE;
END_IF
(* State machine for setup, poll and answer *)
CASE step OF
0:(**)
SlaveSetup.bUnitIdentifier:=Slave_Adresa;(*Subunitnumber*)
slavesetup.wDefaultPort:=Slave_Port;(*Standartport *)
SlaveSetup.xAdditionalPortActive:=FALSE;(*Port opened or closed*)
SlaveSetup.xSecureMode:=FALSE;(*If TRUE only preset IPs are accepted*)
SlaveSetup.tTimeout:=T#3m;(*Timeout if no communication with slave established*)
SlaveSetup(xStrobe:=TRUE);(*Strobe starts function*)
IF slavesetup.xBusy = FALSE THEN
slavesetup(xstrobe := FALSE);
step := 1 ;
END_IF;
1:(**)
SlavePoll(xStrobe:=TRUE);(*Searching for master commands*)
IF NOT SlavePoll.xBusy THEN
step:=2;
SlavePoll(xStrobe:=FALSE);
END_IF;
2:(**)
step:= 1;
CASE SlavePoll.bFunctionCode OF (*Connect accepted pollparameters with answerparameters*)
8:(**)(*Poll answers*)
;
15:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind_bool[slaveanswer.woffset+i] := slavepoll.xarData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.xarData:=slavepoll.xarData;
Write_15:=TRUE;
16:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind[slaveanswer.woffset+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.wardata := slavepoll.warData;
Write_16:=TRUE;
1,2:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slavepoll.wcount-1 BY 1 DO
slaveanswer.xarData[i]:=mind_bool[slavepoll.woffset+i]; (*Read from Data-array*)
END_FOR
3,4:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slaveanswer.wCount-1 BY 1 DO
slaveanswer.warData[i]:=mind[slavepoll.woffset+i];(*Read from Data-array*)
END_FOR
5:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
mind_bool[slavepoll.woffset]:=slavepoll.xarData[0];(*Write to Data-array*)
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.xarData := slavepoll.xardata;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
Write_5:=TRUE;
6:
slaveanswer.bFunctionCode:= slavepoll.bFunctionCode;
mind[slavepoll.woffset]:= slavepoll.warData[0];(*Write to Data-array*)
slaveanswer.wOffset:= slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wardata := slavepoll.wardata;
23:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
FOR i:= 0 TO slavepoll.wCountAdd-1 BY 1 DO
mind[slavepoll.woffsetadd+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
FOR i := 0 TO slavepoll.wCount BY 1 DO
slaveanswer.warData[i] := mind[1+slavepoll.woffset+i];(*Read from Data-array*)
END_FOR;
END_CASE;
IF slavepoll.xAvailable = TRUE THEN
slaveanswer();(*When Data ready, send answer*)
END_IF
END_CASE;
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_dWord : BOOL
VAR_INPUT
dVAR: DWORD;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
DWord_0:=dVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_Real : BOOL
VAR_INPUT
rVAR: REAL;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
Real_0:=rVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_String : BOOL
VAR_INPUT
sVar: STRING;
start:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
String_0:=LEFT (sVar,29);
mind[start]:=wStr_0;
mind[start+1]:=wStr_1;
mind[start+2]:=wStr_2;
mind[start+3]:=wStr_3;
mind[start+4]:=wStr_4;
mind[start+5]:=wStr_5;
mind[start+6]:=wStr_6;
mind[start+7]:=wStr_7;
mind[start+8]:=wStr_8;
mind[start+9]:=wStr_9;
mind[start+10]:=wStr_10;
mind[start+11]:=wStr_11;
mind[start+12]:=wStr_12;
mind[start+13]:=wStr_13;
bStr_29:=0;
mind[start+14]:=wStr_14;
END_FUNCTION
(* @GLOBAL_VARIABLE_LIST := 'Global_Variables_Modnet' *)
(* @PATH := '' *)
(* @SYMFILEFLAGS := '2048' *)
VAR_GLOBAL
(*delovno polje za modnet komunikacijo*)
mind :ARRAY [0..9999] OF WORD;
mind_bool :ARRAY [0..9999] OF BOOL; (*Buffer-Array*)
(*Delovni markerji //*)
Bit_0 AT %MX0.0 : BOOL;
Byte_0 AT %MB0 : BYTE;
Byte_1 AT %MB1 : BYTE;
Byte_2 AT %MB2 : BYTE;
Byte_3 AT %MB3 : BYTE;
Real_0 AT %MR0:REAL;
DWord_0 AT %MD0:DWORD;
Word_01 AT %MW0:WORD;
Word_23 AT %MW2:WORD;
String_0 AT %MW10:STRING;
wStr_0 AT %MW10:WORD;
wStr_1 AT %MW12:WORD;
wStr_2 AT %MW14:WORD;
wStr_3 AT %MW16:WORD;
wStr_4 AT %MW18:WORD;
wStr_5 AT %MW20:WORD;
wStr_6 AT %MW22:WORD;
wStr_7 AT %MW24:WORD;
wStr_8 AT %MW26:WORD;
wStr_9 AT %MW28:WORD;
wStr_10 AT %MW30:WORD;
wStr_11 AT %MW32:WORD;
wStr_12 AT %MW34:WORD;
wStr_13 AT %MW36:WORD;
wStr_14 AT %MW38:WORD;
bStr_00 AT %MB10:BYTE;
bStr_01 AT %MB11:BYTE;
bStr_02 AT %MB12:BYTE;
bStr_03 AT %MB13:BYTE;
bStr_04 AT %MB14:BYTE;
bStr_05 AT %MB15:BYTE;
bStr_06 AT %MB16:BYTE;
bStr_07 AT %MB17:BYTE;
bStr_08 AT %MB18:BYTE;
bStr_09 AT %MB19:BYTE;
bStr_10 AT %MB20:BYTE;
bStr_11 AT %MB21:BYTE;
bStr_12 AT %MB22:BYTE;
bStr_13 AT %MB23:BYTE;
bStr_14 AT %MB24:BYTE;
bStr_15 AT %MB25:BYTE;
bStr_16 AT %MB26:BYTE;
bStr_17 AT %MB27:BYTE;
bStr_18 AT %MB28:BYTE;
bStr_19 AT %MB29:BYTE;
bStr_20 AT %MB30:BYTE;
bStr_21 AT %MB31:BYTE;
bStr_22 AT %MB32:BYTE;
bStr_23 AT %MB33:BYTE;
bStr_24 AT %MB34:BYTE;
bStr_25 AT %MB35:BYTE;
bStr_26 AT %MB36:BYTE;
bStr_27 AT %MB37:BYTE;
bStr_28 AT %MB38:BYTE;
bStr_29 AT %MB39:BYTE;
(********************************************)
END_VAR
(* @OBJECT_END := 'Global_Variables_Modnet' *)
(* @CONNECTIONS := Global_Variables_Modnet
FILENAME : ''
FILETIME : 0
EXPORT : 0
NUMOFCONNECTIONS : 0
*)
(*KONEC_KODA*)