## Prva stran
variable | 1394 | 1.KORAK | variable_1 | 2.KORAK | KORAKI!
Device name | Tip | število spremenljivk | Tip (izbrani) | Zamenjaj z | 1.V Sheet "variable" skopiraj vsebino iz variable.dbf - iz Citect SCAD-a projekta, ki ga želiš pretvoriti.
IOD_GSM | BCD | 0 | BCD | INT | 2.V polje A3 vpiši Device ime spremenljivk ki se bodo prenašale preko Modnet protokola
| BYTE | 115 | BYTE | BYTE | 3.V polje A6 vpiši ime krmilnika (npr.:PLC1, če je adresa v spremenljivkah PLC1:.NapakaKoncnega_stikala, drugače pusti polje prazno)
OPC name | DIGITAL | 458 | DIGITAL | DIGITAL | 4. Pritisni gumb 1.KORAK (V poljih C3:C10 se izpiše število spremenljivk, ki imajo Device enak tistemu v polju A3)
GSM | INT | 143 | INT | INT | 5. Pritisni gumb 2.KORAK (V Sheet-u variable_1 se naredi seznam spremenljivk, ki se bodo prenačale preko Modnet protokola)
| LONG | 0 | LONG | LONG | 6. Pritisni gumb 3.KORAK (V poljih C15:C24 se izpiše število spremnljiv po tipih, v poljih F15:F24 se izpiše število potrebni wordow/coilov za prenos spremnljivk)
| REAL | 327 | REAL | REAL | 7. 4.KORAK: V polja C29:C38 je potrebno ročno vpisati začetne naslove spremnljivk. Potrebno je paziti na:
| STRING | 5 | UINT | UINT | *naslov se morajo začeti z lihim številom npr.:1, 101, 551
| UINT | 24 | STRING | STRING | *naslove je potrebno nastaviti tako, da se naslovi sremenljivk ne more prekrivati (naslovi spremenjivk gredo od (začetnega naslova) do (začetnega naslova+število potrebnih wordow))
8. Pritisni gumb 5.KORAK (V Sheet-u variable_2 se naredi seznam spremenljivk, ki so tokrat sortirana po tipih)
9. Pritisni gumb 6.KORAK (V Sheet-u variable_3 se naredi seznam spremenljivk, katerih Device se zamenja z devicom v polju C41)
Trajanje makroja | variable_1 |  |  | 3.KORAK | 10. Pritisni gumb 7.KORAK (V Sheet-u variable_new se generira seznam spremenljivk. To vsebino je potrebno skopirati v variable.dbf)
0 | Tip | število spremenljivk | TIP | št.potrebnih coilov/wordov | *ta korak traja nekoliko dalj časa (odvisno od števila spremenljivk)
| BCD | 0 | BCD | 0 | *če se pojavi težava z adresami ki se začnejo z 0000 (npr.: "00001" se spremeni na "1") je potrebno uporabiti priloženo (prazno) variable.dbf ali v
| BYTE | 0 | BYTE | 0 | ProjectEditoju/VariableTags na poljubni spremenljki nastaviti adreso" 00001"
| DIGITAL | 458 | DIGITAL | 458 (Coil) | 11. Pritisni gumb 8.KORAK in 9.KORAK (V Sheet-u Xsoft se generira koda)
| INT | 258 | INT | 258 (word) | 12. S pritiskom na gumb 10.KORAK se zgenerira EXP koda za Xsoft (Xsoft_EXP)
| LONG | 0 | LONG | 0 (word) | 13. S pritiskom na gumb Save*.EXP se avtomatsko generira datoka *.EXP
| REAL | 327 | REAL | 654 (word)
| STRING | 5 | STRING | 75 (word)
| UINT | 24 | UINT | 24 (word)
POZOR!
*V Sheet-u variable mora biti vsebina skopirana od polja A1 naprej (če je katera vrstica prazna makroji ne bodo delovali pravilno)
*Ena "STRING" spremenljivka zasede 15wordow (to pomeni 29 znakov, 1BYTE=1STRING)
|  | 4.KORAK(vpiši ročno) | variable_2 | 5.KORAK | *Dolžina "STRING" spremenljivk je 29 znakov (lahko tudi več vendar ne z uporabno tega dokumenta in XSoft programa,potrebna je modifikacija makrojev in Xsoft programa)
| Tip | Začetni naslov |  | Sortiraj | *Vsi stringi so enake dolžine (29)
| BCD |  |  | BCD | *"BYTE" spremenljivke se v variable.dbf spremenijo v "INT" (prenašanje posameznih bytov ni mogoče, niti naslavaljanje v citectscadi)
| BYTE |  |  | DIGITAL | *Naslovi spremenljivk se morajo obvezno začeti z lihim naslovom (preizkušeno je z začetnimi naslovi, ki se izpišejo po pritisku na gumb Ponastavi)
| DIGITAL | 1 |  | BYTE | *Z pritiskom na gumb RESET se pobriše vsebina vseh Sheet-ov razen Sheet-a variable (makor reset se izvaja precej časa)
| INT | 1 |  | INT | *makroji ne delujejo pravilno,če je v Sheet-u variable več kot 9999 vrstic oz. spremenljivk (število vseh spremnljivk je prikazano v polju B1)
| LONG | 3001 |  | LONG | *če se vsebine iz variable_new ne gre skpirat v variable.dbf datotek, vsebino skopirajte najprej v *.txt datoteko in nato v variable.dbf
| REAL | 4001 |  | REAL | *v polju A14 na Sheet-u Prva stran se prikazuje število ciklop do konca izvedbe makroja (samo za gumb 7.KORAK)
| STRING | 5001 |  | STRING
| UINT | 6001 |  | UINT
| variable_3 | 6.KORAK | variable_new | 7.KORAK
| New Device name | IOD_GSM_TCP |  | Nova variable dbf
|  |  | xSoft | 8.KORAK in 9.KORAK
xSoft koda
xSoft_EXP
Izvoz*.EXP
1.KORAK
2.KORAK
3.KORAK
5.KORAK
6.KORAK
7.KORAK
8.KORAK
9.KORAK
RESET
Ponastavi
10.KORAK
Save*.EXP

## variable
GSM_DanEnergCirc1 | LONG | IOD_GSM_disk | L0[30] | [7 empty] | 6157 | 0 | 0x02800001
GSM_CasDDanEnergCirc1 | INT | IOD_GSM_disk | I0[30] | [7 empty] | 6157 | 0 | 0x02800002
GSM_CasMDanEnergCirc1 | INT | IOD_GSM_disk | I30[30] | [7 empty] | 6157 | 0 | 0x02800003
GSM_TedenEnergCirc1 | LONG | IOD_GSM_disk | L30[30] | [7 empty] | 6157 | 0 | 0x02800004
GSM_CasDTedenEnergCirc1 | INT | IOD_GSM_disk | I60[30] | [7 empty] | 6157 | 0 | 0x02800005
GSM_CasMTedenEnergCirc1 | INT | IOD_GSM_disk | I90[30] | [7 empty] | 6157 | 0 | 0x02800006
GSM_MesecEnergCirc1 | LONG | IOD_GSM_disk | L90[30] | [7 empty] | 6157 | 0 | 0x02800007
GSM_CasDMesecEnergCirc1 | INT | IOD_GSM_disk | I120[30] | [7 empty] | 6157 | 0 | 0x02800008
GSM_CasMMesecEnergCirc1 | INT | IOD_GSM_disk | I150[30] | [7 empty] | 6157 | 0 | 0x02800009
GSM_StSt_DanEnergCirc1 | LONG | IOD_GSM_disk | L270 | [7 empty] | 6157 | 0 | 0x0280000a
GSM_StSt_TedenEnergCirc1 | LONG | IOD_GSM_disk | L272 | [7 empty] | 6157 | 0 | 0x0280000b
GSM_StSt_MesecEnergCirc1 | LONG | IOD_GSM_disk | L274 | [7 empty] | 6157 | 0 | 0x0280000c
GSM_StStCasDDanEnergCirc1 | INT | IOD_GSM_disk | I276 | [7 empty] | 6157 | 0 | 0x0280000d
GSM_StStCasMDanEnergCirc1 | INT | IOD_GSM_disk | I277 | [7 empty] | 6157 | 0 | 0x0280000e
GSM_StStCasDTedenEnergCirc1 | INT | IOD_GSM_disk | I278 | [7 empty] | 6157 | 0 | 0x0280000f
GSM_StStCasMTedenEnergCirc1 | INT | IOD_GSM_disk | I279 | [7 empty] | 6157 | 0 | 0x02800010
GSM_StStCasDMesecEnergCirc1 | INT | IOD_GSM_disk | I280 | [7 empty] | 6157 | 0 | 0x02800011
GSM_StStCasMMesecEnergCirc1 | INT | IOD_GSM_disk | I281 | [7 empty] | 6157 | 0 | 0x02800012
GSM_MaxDnevnaEnergija | LONG | IOD_GSM_disk | L282 | 0 | 9999999 | 0 | 9999999 |  | ####### |  | 6157 | 0 | 0x02800013
GSM_MaxMesecnaEnergija | LONG | IOD_GSM_disk | L284 | 0 | 9999999 | 0 | 9999999 |  | ####### |  | 6157 | 0 | 0x02800014
GSM_MaxTedenskaEnergija | LONG | IOD_GSM_disk | L286 | 0 | 9999999 | 0 | 9999999 |  | ####### |  | 6157 | 0 | 0x02800015
GSM_Prikaz_analizatorja_ce_je_1 | DIGITAL | IOD_GSM_mem | D287 | [7 empty] | 6157 | 0 | 0x02800020
GSMAlarmGenUPS_A_V23 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_A_V23 | [7 empty] | 6157 | 1 | 0x02800030
GSMAlarmGenUPS_V23 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_V23 | [7 empty] | 6157 | 1 | 0x02800040
GSMAlarmGenUPS_V25 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_V25 | [7 empty] | 6157 | 1 | 0x02800050
GSMAlarmPMM1VirATokPrevisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirATokPrevisok | [7 empty] | 6157 | 1 | 0x02800060
GSMAlarmPMM1VirATokVisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirATokVisok | [7 empty] | 6157 | 1 | 0x02800070
GSMAlarmPMM1VirBTokPrevisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirBTokPrevisok | [7 empty] | 6157 | 1 | 0x02800080
GSMAlarmPMM1VirBTokVisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirBTokVisok | [7 empty] | 6157 | 1 | 0x02800090
GSMAlarmPMM2x17nad8010 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[10] | [7 empty] | 6157 | 1 | 0x028000a0
GSMAlarmPMM2x17nad8011 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[11] | [7 empty] | 6157 | 1 | 0x028000b0
GSMAlarmPMM2x17nad8012 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[12] | [7 empty] | 6157 | 1 | 0x028000c0
GSMAlarmPMM2x17nad8013 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[13] | [7 empty] | 6157 | 1 | 0x028000d0
GSMAlarmPMM2x17nad8014 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[14] | [7 empty] | 6157 | 1 | 0x028000e0
GSMAlarmPMM2x17nad8015 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[15] | [7 empty] | 6157 | 1 | 0x028000f0
GSMAlarmPMM2x17nad8016 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[16] | [7 empty] | 6157 | 1 | 0x02800100
GSMAlarmPMM2x17nad8017 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[17] | [7 empty] | 6157 | 1 | 0x02800110
GSMAlarmPMM2x17nad8018 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[18] | [7 empty] | 6157 | 1 | 0x02800120
GSMAlarmPMM2x17nad8019 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[19] | [7 empty] | 6157 | 1 | 0x02800130
GSMAlarmPMM2x17nad801 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[1] | [7 empty] | 6157 | 1 | 0x02800140
GSMAlarmPMM2x17nad8020 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[20] | [7 empty] | 6157 | 1 | 0x02800150
GSMAlarmPMM2x17nad8021 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[21] | [7 empty] | 6157 | 1 | 0x02800160
GSMAlarmPMM2x17nad8022 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[22] | [7 empty] | 6157 | 1 | 0x02800170
GSMAlarmPMM2x17nad8023 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[23] | [7 empty] | 6157 | 1 | 0x02800180
GSMAlarmPMM2x17nad8024 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[24] | [7 empty] | 6157 | 1 | 0x02800190
GSMAlarmPMM2x17nad8025 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[25] | [7 empty] | 6157 | 1 | 0x028001a0
GSMAlarmPMM2x17nad8026 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[26] | [7 empty] | 6157 | 1 | 0x028001b0
GSMAlarmPMM2x17nad8027 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[27] | [7 empty] | 6157 | 1 | 0x028001c0
GSMAlarmPMM2x17nad8028 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[28] | [7 empty] | 6157 | 1 | 0x028001d0
GSMAlarmPMM2x17nad8029 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[29] | [7 empty] | 6157 | 1 | 0x028001e0
GSMAlarmPMM2x17nad802 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[2] | [7 empty] | 6157 | 1 | 0x028001f0
GSMAlarmPMM2x17nad8030 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[30] | [7 empty] | 6157 | 1 | 0x02800200
GSMAlarmPMM2x17nad8031 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[31] | [7 empty] | 6157 | 1 | 0x02800210
GSMAlarmPMM2x17nad8032 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[32] | [7 empty] | 6157 | 1 | 0x02800220
GSMAlarmPMM2x17nad8033 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[33] | [7 empty] | 6157 | 1 | 0x02800230
GSMAlarmPMM2x17nad8034 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[34] | [7 empty] | 6157 | 1 | 0x02800240
GSMAlarmPMM2x17nad8035 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[35] | [7 empty] | 6157 | 1 | 0x02800250
GSMAlarmPMM2x17nad8036 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[36] | [7 empty] | 6157 | 1 | 0x02800260
GSMAlarmPMM2x17nad8037 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[37] | [7 empty] | 6157 | 1 | 0x02800270
GSMAlarmPMM2x17nad8038 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[38] | [7 empty] | 6157 | 1 | 0x02800280
GSMAlarmPMM2x17nad8039 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[39] | [7 empty] | 6157 | 1 | 0x02800290
GSMAlarmPMM2x17nad803 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[3] | [7 empty] | 6157 | 1 | 0x028002a0
GSMAlarmPMM2x17nad8040 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[40] | [7 empty] | 6157 | 1 | 0x028002b0
GSMAlarmPMM2x17nad8041 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[41] | [7 empty] | 6157 | 1 | 0x028002c0
GSMAlarmPMM2x17nad8042 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[42] | [7 empty] | 6157 | 1 | 0x028002d0
GSMAlarmPMM2x17nad804 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[4] | [7 empty] | 6157 | 1 | 0x028002e0
GSMAlarmPMM2x17nad805 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[5] | [7 empty] | 6157 | 1 | 0x028002f0
GSMAlarmPMM2x17nad806 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[6] | [7 empty] | 6157 | 1 | 0x02800300
GSMAlarmPMM2x17nad807 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[7] | [7 empty] | 6157 | 1 | 0x02800310
GSMAlarmPMM2x17nad808 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[8] | [7 empty] | 6157 | 1 | 0x02800320
GSMAlarmPMM2x17nad809 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[9] | [7 empty] | 6157 | 1 | 0x02800330
GSMCirc1CosFi_III | REAL | IOD_GSM | GSM:.Circ[1].CosFi_III | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x02800340
GSMCirc1DelovnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].DelovnaEnergija | [7 empty] | 6157 | 1 | 0x02800341
GSMCirc1DelovnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_III | 0 | 50.0 | 0 | 50.0 | kW | ###.# |  | 6157 | 1 | 0x02800342
GSMCirc1DelovnaMoc_L1 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L1 | 0 | 50.0 | 0 | 50.0 | kW | ###.# |  | 6157 | 1 | 0x02800343
GSMCirc1DelovnaMoc_L2 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L2 | 0 | 50.0 | 0 | 50.0 | kW | ###.# |  | 6157 | 1 | 0x02800344
GSMCirc1DelovnaMoc_L3 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L3 | 0 | 50.0 | 0 | 50.0 | kW | ###.# |  | 6157 | 1 | 0x02800345
GSMCirc1Frekvenca_L1 | REAL | IOD_GSM | GSM:.Circ[1].Frekvenca_L1 | 0 | 60.0 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x02800346
GSMCirc1InduktivnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].InduktivnaEnergija | [7 empty] | 6157 | 1 | 0x02800347
GSMCirc1InduktivnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].InduktivnaMoc_III | 0 | 50.0 | 0 | 50.0 | kVAR | ###.# |  | 6157 | 1 | 0x02800348
GSMCirc1JalovaMoc_L1 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L1 | 0 | 50.0 | 0 | 50.0 | kVAR | ###.# |  | 6157 | 1 | 0x02800349
GSMCirc1JalovaMoc_L2 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L2 | 0 | 50.0 | 0 | 50.0 | kVAR | ###.# |  | 6157 | 1 | 0x0280034a
GSMCirc1JalovaMoc_L3 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L3 | 0 | 50.0 | 0 | 50.0 | kVAR | ###.# |  | 6157 | 1 | 0x0280034b
GSMCirc1KapacitivnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].KapacitivnaEnergija | [7 empty] | 6157 | 1 | 0x0280034c
GSMCirc1KapacitivnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].KapacitivnaMoc_III | 0 | 50.0 | 0 | 50.0 | kVAR | ###.# |  | 6157 | 1 | 0x0280034d
GSMCirc1MaximumDemand | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemand | 0 | 1200.0 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x0280034e
GSMCirc1Napetost_L1_L2 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L1_L2 | 0 | 450.0 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x0280034f
GSMCirc1Napetost_L1_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L1_N | 0 | 270.0 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x02800350
GSMCirc1Napetost_L2_L3 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L2_L3 | 0 | 450.0 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x02800351
GSMCirc1Napetost_L2_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L2_N | 0 | 270.0 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x02800352
GSMCirc1Napetost_L3_L1 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L3_L1 | 0 | 450.0 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x02800353
GSMCirc1Napetost_L3_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L3_N | 0 | 270.0 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x02800354
GSMCirc1NavideznaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].NavideznaMoc_III | 0 | 50.0 | 0 | 50.0 | kVA | ###.# |  | 6157 | 1 | 0x02800355
GSMCirc1NicelniTok | REAL | IOD_GSM | GSM:.Circ[1].NicelniTok | 0 | 200.0 | 0 | 200.0 | A | ###.# |  | 6157 | 1 | 0x02800356
GSMCirc1PowerFactor_III | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_III | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x02800357
GSMCirc1PowerFactor_L1 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L1 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x02800358
GSMCirc1PowerFactor_L2 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L2 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x02800359
GSMCirc1PowerFactor_L3 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L3 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x0280035a
GSMCirc1THDI_L1 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L1 | 0 | 10 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x0280035b
GSMCirc1THDI_L2 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L2 | 0 | 10 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x0280035c
GSMCirc1THDI_L3 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L3 | 0 | 10 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x0280035d
GSMCirc1THDV_L1 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L1 | 0 | 10 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x0280035e
GSMCirc1THDV_L2 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L2 | 0 | 10 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x0280035f
GSMCirc1THDV_L3 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L3 | 0 | 10 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x02800360
GSMCirc1Tok_L1 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L1 | 0 | 200.0 | 0 | 200.0 | A | ###.# |  | 6157 | 1 | 0x02800361
GSMCirc1Tok_L2 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L2 | 0 | 200.0 | 0 | 200.0 | A | ###.# |  | 6157 | 1 | 0x02800362
GSMCirc1Tok_L3 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L3 | 0 | 200.0 | 0 | 200.0 | A | ###.# |  | 6157 | 1 | 0x02800363
GSMCirc1TokPovprecje_III | REAL | IOD_GSM | GSM:.Circ[1].TokPovprecje_III | 0 | 200.0 | 0 | 200.0 | A | ###.# |  | 6157 | 1 | 0x02800364
GSMComError | DIGITAL | IOD_GSM | GSM:.ComError | [7 empty] | 6157 | 1 | 0x02800370
GSMComSCADA | DIGITAL | IOD_GSM | GSM:.ComSCADA | [7 empty] | 6157 | 1 | 0x02800380
GSMComSCADA1 | DIGITAL | IOD_GSM | GSM:.ComSCADA1 | [7 empty] | 6157 | 1 | 0x02800390
GSMComSCADA2 | DIGITAL | IOD_GSM | GSM:.ComSCADA2 | [7 empty] | 6157 | 1 | 0x028003a0
GSMComSCADA3 | DIGITAL | IOD_GSM | GSM:.ComSCADA3 | [7 empty] | 6157 | 1 | 0x028003b0
GSMDate_Time0 | STRING | IOD_GSM | GSM:.Date_Time[0] | [7 empty] | 6157 | 1 | 0x028003c8
GSMDate_Time1 | STRING | IOD_GSM | GSM:.Date_Time[1] | [7 empty] | 6157 | 1 | 0x028003c9
GSMDate_Time2 | STRING | IOD_GSM | GSM:.Date_Time[2] | [7 empty] | 6157 | 1 | 0x028003ca
GSMDate_Time3 | STRING | IOD_GSM | GSM:.Date_Time[3] | [7 empty] | 6157 | 1 | 0x028003cb
GSMDateTimeDan | BYTE | IOD_GSM | GSM:.DateTime.Dan | [7 empty] | 6157 | 1 | 0x028003cc
GSMDateTimeLeto | BYTE | IOD_GSM | GSM:.DateTime.Leto | [7 empty] | 6157 | 1 | 0x028003cd
GSMDateTimeLeto2 | INT | IOD_GSM | GSM:.DateTime.Leto2 | [7 empty] | 6157 | 1 | 0x028003ce
GSMDateTimeMesec | BYTE | IOD_GSM | GSM:.DateTime.Mesec | [7 empty] | 6157 | 1 | 0x028003cf
GSMDateTimeMinuta | BYTE | IOD_GSM | GSM:.DateTime.Minuta | [7 empty] | 6157 | 1 | 0x028003d0
GSMDateTimeSekunda | BYTE | IOD_GSM | GSM:.DateTime.Sekunda | [7 empty] | 6157 | 1 | 0x028003d1
GSMDateTimeUra | BYTE | IOD_GSM | GSM:.DateTime.Ura | [7 empty] | 6157 | 1 | 0x028003d2
GSMErrComCirc1 | DIGITAL | IOD_GSM | GSM:.ErrComCirc[1] | [7 empty] | 6157 | 1 | 0x028003e0
GSMErrComKlima1 | DIGITAL | IOD_GSM | GSM:.ErrComKlima[1] | [7 empty] | 6157 | 1 | 0x028003f0
GSMErrComKlima2 | DIGITAL | IOD_GSM | GSM:.ErrComKlima[2] | [7 empty] | 6157 | 1 | 0x02800400
GSMErrComPMM1 | DIGITAL | IOD_GSM | GSM:.ErrComPMM[1] | [7 empty] | 6157 | 1 | 0x02800410
GSMErrComPort2 | DIGITAL | IOD_GSM | GSM:.ErrComPort2 | [7 empty] | 6157 | 1 | 0x02800420
GSMErrComPort3 | DIGITAL | IOD_GSM | GSM:.ErrComPort3 | [7 empty] | 6157 | 1 | 0x02800430
GSMErrComPort4 | DIGITAL | IOD_GSM | GSM:.ErrComPort4 | [7 empty] | 6157 | 1 | 0x02800440
GSMErrComUPS1 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[1] | [7 empty] | 6157 | 1 | 0x02800450
GSMErrComUPS2 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[2] | [7 empty] | 6157 | 1 | 0x02800460
GSMErrComUPSMGE1 | DIGITAL | IOD_GSM | GSM:.ErrComUPSMGE[1] | [7 empty] | 6157 | 1 | 0x02800470
GSMErrorComCirc1Code10 | BYTE | IOD_GSM | GSM:.ErrorComCirc[1].Code[10] | [7 empty] | 6157 | 1 | 0x02800480
GSMErrorComCirc1Code11 | BYTE | IOD_GSM | GSM:.ErrorComCirc[1].Code[11] | [7 empty] | 6157 | 1 | 0x02800481
GSMErrorComCirc1Code12 | BYTE | IOD_GSM | GSM:.ErrorComCirc[1].Code[12] | [7 empty] | 6157 | 1 | 0x02800482
GSMErrorComCirc1Code13 | BYTE | IOD_GSM | GSM:.ErrorComCirc[1].Code[13] | [7 empty] | 6157 | 1 | 0x02800483
GSMErrorComCirc1Code14 | BYTE | IOD_GSM | GSM:.ErrorComCirc[1].Code[14] | [7 empty] | 6157 | 1 | 0x02800484
GSMErrorComCirc1Code15 | BYTE | IOD_GSM | GSM:.ErrorComCirc[1].Code[15] | [7 empty] | 6157 | 1 | 0x02800485
GSMErrorComCirc1Code1 | BYTE | IOD_GSM | GSM:.ErrorComCirc[1].Code[1] | [7 empty] | 6157 | 1 | 0x02800486
GSMErrorComCirc1Code2 | BYTE | IOD_GSM | GSM:.ErrorComCirc[1].Code[2] | [7 empty] | 6157 | 1 | 0x02800487
GSMErrorComCirc1Code3 | BYTE | IOD_GSM | GSM:.ErrorComCirc[1].Code[3] | [7 empty] | 6157 | 1 | 0x02800488
GSMErrorComCirc1Code4 | BYTE | IOD_GSM | GSM:.ErrorComCirc[1].Code[4] | [7 empty] | 6157 | 1 | 0x02800489
GSMErrorComCirc1Code5 | BYTE | IOD_GSM | GSM:.ErrorComCirc[1].Code[5] | [7 empty] | 6157 | 1 | 0x0280048a
GSMErrorComCirc1Code6 | BYTE | IOD_GSM | GSM:.ErrorComCirc[1].Code[6] | [7 empty] | 6157 | 1 | 0x0280048b
GSMErrorComCirc1Code7 | BYTE | IOD_GSM | GSM:.ErrorComCirc[1].Code[7] | [7 empty] | 6157 | 1 | 0x0280048c
GSMErrorComCirc1Code8 | BYTE | IOD_GSM | GSM:.ErrorComCirc[1].Code[8] | [7 empty] | 6157 | 1 | 0x0280048d
GSMErrorComCirc1Code9 | BYTE | IOD_GSM | GSM:.ErrorComCirc[1].Code[9] | [7 empty] | 6157 | 1 | 0x0280048e
GSMErrorComCirc1Error | DIGITAL | IOD_GSM | GSM:.ErrorComCirc[1].Error | [7 empty] | 6157 | 1 | 0x02800490
GSMErrorComCirc1Status | INT | IOD_GSM | GSM:.ErrorComCirc[1].Status | [7 empty] | 6157 | 1 | 0x028004a0
GSMErrorComKlima1Code10 | BYTE | IOD_GSM | GSM:.ErrorComKlima[1].Code[10] | [7 empty] | 6157 | 1 | 0x028004a1
GSMErrorComKlima1Code11 | BYTE | IOD_GSM | GSM:.ErrorComKlima[1].Code[11] | [7 empty] | 6157 | 1 | 0x028004a2
GSMErrorComKlima1Code12 | BYTE | IOD_GSM | GSM:.ErrorComKlima[1].Code[12] | [7 empty] | 6157 | 1 | 0x028004a3
GSMErrorComKlima1Code13 | BYTE | IOD_GSM | GSM:.ErrorComKlima[1].Code[13] | [7 empty] | 6157 | 1 | 0x028004a4
GSMErrorComKlima1Code14 | BYTE | IOD_GSM | GSM:.ErrorComKlima[1].Code[14] | [7 empty] | 6157 | 1 | 0x028004a5
GSMErrorComKlima1Code15 | BYTE | IOD_GSM | GSM:.ErrorComKlima[1].Code[15] | [7 empty] | 6157 | 1 | 0x028004a6
GSMErrorComKlima1Code1 | BYTE | IOD_GSM | GSM:.ErrorComKlima[1].Code[1] | [7 empty] | 6157 | 1 | 0x028004a7
GSMErrorComKlima1Code2 | BYTE | IOD_GSM | GSM:.ErrorComKlima[1].Code[2] | [7 empty] | 6157 | 1 | 0x028004a8
GSMErrorComKlima1Code3 | BYTE | IOD_GSM | GSM:.ErrorComKlima[1].Code[3] | [7 empty] | 6157 | 1 | 0x028004a9
GSMErrorComKlima1Code4 | BYTE | IOD_GSM | GSM:.ErrorComKlima[1].Code[4] | [7 empty] | 6157 | 1 | 0x028004aa
GSMErrorComKlima1Code5 | BYTE | IOD_GSM | GSM:.ErrorComKlima[1].Code[5] | [7 empty] | 6157 | 1 | 0x028004ab
GSMErrorComKlima1Code6 | BYTE | IOD_GSM | GSM:.ErrorComKlima[1].Code[6] | [7 empty] | 6157 | 1 | 0x028004ac
GSMErrorComKlima1Code7 | BYTE | IOD_GSM | GSM:.ErrorComKlima[1].Code[7] | [7 empty] | 6157 | 1 | 0x028004ad
GSMErrorComKlima1Code8 | BYTE | IOD_GSM | GSM:.ErrorComKlima[1].Code[8] | [7 empty] | 6157 | 1 | 0x028004ae
GSMErrorComKlima1Code9 | BYTE | IOD_GSM | GSM:.ErrorComKlima[1].Code[9] | [7 empty] | 6157 | 1 | 0x028004af
GSMErrorComKlima1Error | DIGITAL | IOD_GSM | GSM:.ErrorComKlima[1].Error | [7 empty] | 6157 | 1 | 0x028004b0
GSMErrorComKlima1Status | INT | IOD_GSM | GSM:.ErrorComKlima[1].Status | [7 empty] | 6157 | 1 | 0x028004c0
GSMErrorComKlima2Code10 | BYTE | IOD_GSM | GSM:.ErrorComKlima[2].Code[10] | [7 empty] | 6157 | 1 | 0x028004c1
GSMErrorComKlima2Code11 | BYTE | IOD_GSM | GSM:.ErrorComKlima[2].Code[11] | [7 empty] | 6157 | 1 | 0x028004c2
GSMErrorComKlima2Code12 | BYTE | IOD_GSM | GSM:.ErrorComKlima[2].Code[12] | [7 empty] | 6157 | 1 | 0x028004c3
GSMErrorComKlima2Code13 | BYTE | IOD_GSM | GSM:.ErrorComKlima[2].Code[13] | [7 empty] | 6157 | 1 | 0x028004c4
GSMErrorComKlima2Code14 | BYTE | IOD_GSM | GSM:.ErrorComKlima[2].Code[14] | [7 empty] | 6157 | 1 | 0x028004c5
GSMErrorComKlima2Code15 | BYTE | IOD_GSM | GSM:.ErrorComKlima[2].Code[15] | [7 empty] | 6157 | 1 | 0x028004c6
GSMErrorComKlima2Code1 | BYTE | IOD_GSM | GSM:.ErrorComKlima[2].Code[1] | [7 empty] | 6157 | 1 | 0x028004c7
GSMErrorComKlima2Code2 | BYTE | IOD_GSM | GSM:.ErrorComKlima[2].Code[2] | [7 empty] | 6157 | 1 | 0x028004c8
GSMErrorComKlima2Code3 | BYTE | IOD_GSM | GSM:.ErrorComKlima[2].Code[3] | [7 empty] | 6157 | 1 | 0x028004c9
GSMErrorComKlima2Code4 | BYTE | IOD_GSM | GSM:.ErrorComKlima[2].Code[4] | [7 empty] | 6157 | 1 | 0x028004ca
GSMErrorComKlima2Code5 | BYTE | IOD_GSM | GSM:.ErrorComKlima[2].Code[5] | [7 empty] | 6157 | 1 | 0x028004cb
GSMErrorComKlima2Code6 | BYTE | IOD_GSM | GSM:.ErrorComKlima[2].Code[6] | [7 empty] | 6157 | 1 | 0x028004cc
GSMErrorComKlima2Code7 | BYTE | IOD_GSM | GSM:.ErrorComKlima[2].Code[7] | [7 empty] | 6157 | 1 | 0x028004cd
GSMErrorComKlima2Code8 | BYTE | IOD_GSM | GSM:.ErrorComKlima[2].Code[8] | [7 empty] | 6157 | 1 | 0x028004ce
GSMErrorComKlima2Code9 | BYTE | IOD_GSM | GSM:.ErrorComKlima[2].Code[9] | [7 empty] | 6157 | 1 | 0x028004cf
GSMErrorComKlima2Error | DIGITAL | IOD_GSM | GSM:.ErrorComKlima[2].Error | [7 empty] | 6157 | 1 | 0x028004d0
GSMErrorComKlima2Status | INT | IOD_GSM | GSM:.ErrorComKlima[2].Status | [7 empty] | 6157 | 1 | 0x028004e0
GSMErrorComPMM1Code10 | BYTE | IOD_GSM | GSM:.ErrorComPMM[1].Code[10] | [7 empty] | 6157 | 1 | 0x028004e1
GSMErrorComPMM1Code11 | BYTE | IOD_GSM | GSM:.ErrorComPMM[1].Code[11] | [7 empty] | 6157 | 1 | 0x028004e2
GSMErrorComPMM1Code12 | BYTE | IOD_GSM | GSM:.ErrorComPMM[1].Code[12] | [7 empty] | 6157 | 1 | 0x028004e3
GSMErrorComPMM1Code13 | BYTE | IOD_GSM | GSM:.ErrorComPMM[1].Code[13] | [7 empty] | 6157 | 1 | 0x028004e4
GSMErrorComPMM1Code14 | BYTE | IOD_GSM | GSM:.ErrorComPMM[1].Code[14] | [7 empty] | 6157 | 1 | 0x028004e5
GSMErrorComPMM1Code15 | BYTE | IOD_GSM | GSM:.ErrorComPMM[1].Code[15] | [7 empty] | 6157 | 1 | 0x028004e6
GSMErrorComPMM1Code1 | BYTE | IOD_GSM | GSM:.ErrorComPMM[1].Code[1] | [7 empty] | 6157 | 1 | 0x028004e7
GSMErrorComPMM1Code2 | BYTE | IOD_GSM | GSM:.ErrorComPMM[1].Code[2] | [7 empty] | 6157 | 1 | 0x028004e8
GSMErrorComPMM1Code3 | BYTE | IOD_GSM | GSM:.ErrorComPMM[1].Code[3] | [7 empty] | 6157 | 1 | 0x028004e9
GSMErrorComPMM1Code4 | BYTE | IOD_GSM | GSM:.ErrorComPMM[1].Code[4] | [7 empty] | 6157 | 1 | 0x028004ea
GSMErrorComPMM1Code5 | BYTE | IOD_GSM | GSM:.ErrorComPMM[1].Code[5] | [7 empty] | 6157 | 1 | 0x028004eb
GSMErrorComPMM1Code6 | BYTE | IOD_GSM | GSM:.ErrorComPMM[1].Code[6] | [7 empty] | 6157 | 1 | 0x028004ec
GSMErrorComPMM1Code7 | BYTE | IOD_GSM | GSM:.ErrorComPMM[1].Code[7] | [7 empty] | 6157 | 1 | 0x028004ed
GSMErrorComPMM1Code8 | BYTE | IOD_GSM | GSM:.ErrorComPMM[1].Code[8] | [7 empty] | 6157 | 1 | 0x028004ee
GSMErrorComPMM1Code9 | BYTE | IOD_GSM | GSM:.ErrorComPMM[1].Code[9] | [7 empty] | 6157 | 1 | 0x028004ef
GSMErrorComPMM1Error | DIGITAL | IOD_GSM | GSM:.ErrorComPMM[1].Error | [7 empty] | 6157 | 1 | 0x028004f0
GSMErrorComPMM1Status | INT | IOD_GSM | GSM:.ErrorComPMM[1].Status | [7 empty] | 6157 | 1 | 0x02800500
GSMErrorComUPS1Code10 | BYTE | IOD_GSM | GSM:.ErrorComUPS[1].Code[10] | [7 empty] | 6157 | 1 | 0x02800501
GSMErrorComUPS1Code11 | BYTE | IOD_GSM | GSM:.ErrorComUPS[1].Code[11] | [7 empty] | 6157 | 1 | 0x02800502
GSMErrorComUPS1Code12 | BYTE | IOD_GSM | GSM:.ErrorComUPS[1].Code[12] | [7 empty] | 6157 | 1 | 0x02800503
GSMErrorComUPS1Code13 | BYTE | IOD_GSM | GSM:.ErrorComUPS[1].Code[13] | [7 empty] | 6157 | 1 | 0x02800504
GSMErrorComUPS1Code14 | BYTE | IOD_GSM | GSM:.ErrorComUPS[1].Code[14] | [7 empty] | 6157 | 1 | 0x02800505
GSMErrorComUPS1Code15 | BYTE | IOD_GSM | GSM:.ErrorComUPS[1].Code[15] | [7 empty] | 6157 | 1 | 0x02800506
GSMErrorComUPS1Code1 | BYTE | IOD_GSM | GSM:.ErrorComUPS[1].Code[1] | [7 empty] | 6157 | 1 | 0x02800507
GSMErrorComUPS1Code2 | BYTE | IOD_GSM | GSM:.ErrorComUPS[1].Code[2] | [7 empty] | 6157 | 1 | 0x02800508
GSMErrorComUPS1Code3 | BYTE | IOD_GSM | GSM:.ErrorComUPS[1].Code[3] | [7 empty] | 6157 | 1 | 0x02800509
GSMErrorComUPS1Code4 | BYTE | IOD_GSM | GSM:.ErrorComUPS[1].Code[4] | [7 empty] | 6157 | 1 | 0x0280050a
GSMErrorComUPS1Code5 | BYTE | IOD_GSM | GSM:.ErrorComUPS[1].Code[5] | [7 empty] | 6157 | 1 | 0x0280050b
GSMErrorComUPS1Code6 | BYTE | IOD_GSM | GSM:.ErrorComUPS[1].Code[6] | [7 empty] | 6157 | 1 | 0x0280050c
GSMErrorComUPS1Code7 | BYTE | IOD_GSM | GSM:.ErrorComUPS[1].Code[7] | [7 empty] | 6157 | 1 | 0x0280050d
GSMErrorComUPS1Code8 | BYTE | IOD_GSM | GSM:.ErrorComUPS[1].Code[8] | [7 empty] | 6157 | 1 | 0x0280050e
GSMErrorComUPS1Code9 | BYTE | IOD_GSM | GSM:.ErrorComUPS[1].Code[9] | [7 empty] | 6157 | 1 | 0x0280050f
GSMErrorComUPS1Error | DIGITAL | IOD_GSM | GSM:.ErrorComUPS[1].Error | [7 empty] | 6157 | 1 | 0x02800510
GSMErrorComUPS1Status | INT | IOD_GSM | GSM:.ErrorComUPS[1].Status | [7 empty] | 6157 | 1 | 0x02800520
GSMErrorComUPS2Code10 | BYTE | IOD_GSM | GSM:.ErrorComUPS[2].Code[10] | [7 empty] | 6157 | 1 | 0x02800521
GSMErrorComUPS2Code11 | BYTE | IOD_GSM | GSM:.ErrorComUPS[2].Code[11] | [7 empty] | 6157 | 1 | 0x02800522
GSMErrorComUPS2Code12 | BYTE | IOD_GSM | GSM:.ErrorComUPS[2].Code[12] | [7 empty] | 6157 | 1 | 0x02800523
GSMErrorComUPS2Code13 | BYTE | IOD_GSM | GSM:.ErrorComUPS[2].Code[13] | [7 empty] | 6157 | 1 | 0x02800524
GSMErrorComUPS2Code14 | BYTE | IOD_GSM | GSM:.ErrorComUPS[2].Code[14] | [7 empty] | 6157 | 1 | 0x02800525
GSMErrorComUPS2Code15 | BYTE | IOD_GSM | GSM:.ErrorComUPS[2].Code[15] | [7 empty] | 6157 | 1 | 0x02800526
GSMErrorComUPS2Code1 | BYTE | IOD_GSM | GSM:.ErrorComUPS[2].Code[1] | [7 empty] | 6157 | 1 | 0x02800527
GSMErrorComUPS2Code2 | BYTE | IOD_GSM | GSM:.ErrorComUPS[2].Code[2] | [7 empty] | 6157 | 1 | 0x02800528
GSMErrorComUPS2Code3 | BYTE | IOD_GSM | GSM:.ErrorComUPS[2].Code[3] | [7 empty] | 6157 | 1 | 0x02800529
GSMErrorComUPS2Code4 | BYTE | IOD_GSM | GSM:.ErrorComUPS[2].Code[4] | [7 empty] | 6157 | 1 | 0x0280052a
GSMErrorComUPS2Code5 | BYTE | IOD_GSM | GSM:.ErrorComUPS[2].Code[5] | [7 empty] | 6157 | 1 | 0x0280052b
GSMErrorComUPS2Code6 | BYTE | IOD_GSM | GSM:.ErrorComUPS[2].Code[6] | [7 empty] | 6157 | 1 | 0x0280052c
GSMErrorComUPS2Code7 | BYTE | IOD_GSM | GSM:.ErrorComUPS[2].Code[7] | [7 empty] | 6157 | 1 | 0x0280052d
GSMErrorComUPS2Code8 | BYTE | IOD_GSM | GSM:.ErrorComUPS[2].Code[8] | [7 empty] | 6157 | 1 | 0x0280052e
GSMErrorComUPS2Code9 | BYTE | IOD_GSM | GSM:.ErrorComUPS[2].Code[9] | [7 empty] | 6157 | 1 | 0x0280052f
GSMErrorComUPS2Error | DIGITAL | IOD_GSM | GSM:.ErrorComUPS[2].Error | [7 empty] | 6157 | 1 | 0x02800530
GSMErrorComUPS2Status | INT | IOD_GSM | GSM:.ErrorComUPS[2].Status | [7 empty] | 6157 | 1 | 0x02800540
GSMErrorComUPSMGE1Code10 | BYTE | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[10] | [7 empty] | 6157 | 1 | 0x02800541
GSMErrorComUPSMGE1Code11 | BYTE | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[11] | [7 empty] | 6157 | 1 | 0x02800542
GSMErrorComUPSMGE1Code12 | BYTE | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[12] | [7 empty] | 6157 | 1 | 0x02800543
GSMErrorComUPSMGE1Code13 | BYTE | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[13] | [7 empty] | 6157 | 1 | 0x02800544
GSMErrorComUPSMGE1Code14 | BYTE | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[14] | [7 empty] | 6157 | 1 | 0x02800545
GSMErrorComUPSMGE1Code15 | BYTE | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[15] | [7 empty] | 6157 | 1 | 0x02800546
GSMErrorComUPSMGE1Code1 | BYTE | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[1] | [7 empty] | 6157 | 1 | 0x02800547
GSMErrorComUPSMGE1Code2 | BYTE | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[2] | [7 empty] | 6157 | 1 | 0x02800548
GSMErrorComUPSMGE1Code3 | BYTE | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[3] | [7 empty] | 6157 | 1 | 0x02800549
GSMErrorComUPSMGE1Code4 | BYTE | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[4] | [7 empty] | 6157 | 1 | 0x0280054a
GSMErrorComUPSMGE1Code5 | BYTE | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[5] | [7 empty] | 6157 | 1 | 0x0280054b
GSMErrorComUPSMGE1Code6 | BYTE | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[6] | [7 empty] | 6157 | 1 | 0x0280054c
GSMErrorComUPSMGE1Code7 | BYTE | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[7] | [7 empty] | 6157 | 1 | 0x0280054d
GSMErrorComUPSMGE1Code8 | BYTE | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[8] | [7 empty] | 6157 | 1 | 0x0280054e
GSMErrorComUPSMGE1Code9 | BYTE | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[9] | [7 empty] | 6157 | 1 | 0x0280054f
GSMErrorComUPSMGE1Error | DIGITAL | IOD_GSM | GSM:.ErrorComUPSMGE[1].Error | [7 empty] | 6157 | 1 | 0x02800550
GSMErrorComUPSMGE1Status | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Status | [7 empty] | 6157 | 1 | 0x02800560
GSMF1_1_zascita_ok | DIGITAL | IOD_GSM | GSM:.F1_1_zascita_ok | [7 empty] | 6157 | 1 | 0x02800570
GSMHIA1_vlaga_s | INT | IOD_GSM | GSM:.HIA1_vlaga_s | 0 | 1000 | 0 | 100.0 | % | ###.# |  | 6157 | 1 | 0x02800581
GSMHIA2_vlaga_s | INT | IOD_GSM | GSM:.HIA2_vlaga_s | 0 | 1000 | 0 | 100.0 | % | ###.# |  | 6157 | 1 | 0x02800583
GSMHIA3_vlaga_s | INT | IOD_GSM | GSM:.HIA3_vlaga_s | 0 | 1000 | 0 | 100.0 | % | ###.# |  | 6157 | 1 | 0x02800585
GSMHIA4_vlaga_s | INT | IOD_GSM | GSM:.HIA4_vlaga_s | 0 | 1000 | 0 | 100.0 | % | ###.# |  | 6157 | 1 | 0x02800587
GSMHIA5_vlaga_s | INT | IOD_GSM | GSM:.HIA5_vlaga_s | 0 | 1000 | 0 | 100.0 | % | ###.# |  | 6157 | 1 | 0x02800589
GSMHIA6_vlaga_s | INT | IOD_GSM | GSM:.HIA6_vlaga_s | 0 | 1000 | 0 | 100.0 | % | ###.# |  | 6157 | 1 | 0x0280058b
GSMHIA7_vlaga_s | INT | IOD_GSM | GSM:.HIA7_vlaga_s | 0 | 1000 | 0 | 100.0 | % | ###.# |  | 6157 | 1 | 0x0280058d
GSMK1_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K1_SkupnaNapaka | [7 empty] | 6157 | 1 | 0x02800590
GSMK1AlarmPozara | DIGITAL | IOD_GSM | GSM:.K1AlarmPozara | [7 empty] | 6157 | 1 | 0x028005a0
GSMK1KlimaZdruzenAlarm | DIGITAL | IOD_GSM | GSM:.K1KlimaZdruzenAlarm | [7 empty] | 6157 | 1 | 0x028005b0
GSMK1NiPretoka | DIGITAL | IOD_GSM | GSM:.K1NiPretoka | [7 empty] | 6157 | 1 | 0x028005c0
GSMK1OkvaraRototerma | DIGITAL | IOD_GSM | GSM:.K1OkvaraRototerma | [7 empty] | 6157 | 1 | 0x028005d0
GSMK1OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.K1OkvaraVlazNap | [7 empty] | 6157 | 1 | 0x028005e0
GSMK1PreobMotCrpGr | DIGITAL | IOD_GSM | GSM:.K1PreobMotCrpGr | [7 empty] | 6157 | 1 | 0x028005f0
GSMK1PreobMotVent | DIGITAL | IOD_GSM | GSM:.K1PreobMotVent | [7 empty] | 6157 | 1 | 0x02800600
GSMK1ProtizamrzZascAkt | DIGITAL | IOD_GSM | GSM:.K1ProtizamrzZascAkt | [7 empty] | 6157 | 1 | 0x02800610
GSMK1ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.K1ZamasenostFiltra | [7 empty] | 6157 | 1 | 0x02800620
GSMK2_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K2_SkupnaNapaka | [7 empty] | 6157 | 1 | 0x02800630
GSMK2AlarmPozara | DIGITAL | IOD_GSM | GSM:.K2AlarmPozara | [7 empty] | 6157 | 1 | 0x02800640
GSMK2KlimaZdruzenAlarm | DIGITAL | IOD_GSM | GSM:.K2KlimaZdruzenAlarm | [7 empty] | 6157 | 1 | 0x02800650
GSMK2NiPretoka | DIGITAL | IOD_GSM | GSM:.K2NiPretoka | [7 empty] | 6157 | 1 | 0x02800660
GSMK2OkvaraRototerma | DIGITAL | IOD_GSM | GSM:.K2OkvaraRototerma | [7 empty] | 6157 | 1 | 0x02800670
GSMK2OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.K2OkvaraVlazNap | [7 empty] | 6157 | 1 | 0x02800680
GSMK2PreobMotCrpGr | DIGITAL | IOD_GSM | GSM:.K2PreobMotCrpGr | [7 empty] | 6157 | 1 | 0x02800690
GSMK2PreobMotVent | DIGITAL | IOD_GSM | GSM:.K2PreobMotVent | [7 empty] | 6157 | 1 | 0x028006a0
GSMK2ProtizamrzZascAkt | DIGITAL | IOD_GSM | GSM:.K2ProtizamrzZascAkt | [7 empty] | 6157 | 1 | 0x028006b0
GSMK2ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.K2ZamasenostFiltra | [7 empty] | 6157 | 1 | 0x028006c0
GSMK3_deluje | DIGITAL | IOD_GSM | GSM:.K3_deluje | [7 empty] | 6157 | 1 | 0x028006d0
GSMK3_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K3_SkupnaNapaka | [7 empty] | 6157 | 1 | 0x028006e0
GSMKlima1_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima1_izkljucena | [7 empty] | 6157 | 1 | 0x028006f0
GSMKLIMA1_kke_pogon | DIGITAL | IOD_GSM | GSM:.KLIMA1_kke_pogon | [7 empty] | 6157 | 1 | 0x02800700
GSMKLIMA1_krm_nap_ok | DIGITAL | IOD_GSM | GSM:.KLIMA1_krm_nap_ok | [7 empty] | 6157 | 1 | 0x02800710
GSMKlima2_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima2_izkljucena | [7 empty] | 6157 | 1 | 0x02800720
GSMKlima3_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima3_izkljucena | [7 empty] | 6157 | 1 | 0x02800730
GSMKlima1Alarm_pozar | DIGITAL | IOD_GSM | GSM:.Klima[1].Alarm_pozar | [7 empty] | 6157 | 1 | 0x02800740
GSMKlima1Analog_izh_mesanje | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_mesanje | [7 empty] | 6157 | 1 | 0x02800750
GSMKlima1Analog_izh_rekuperator | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_rekuperator | [7 empty] | 6157 | 1 | 0x02800751
GSMKlima1Analog_izh_VentGrelnika | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_VentGrelnika | [7 empty] | 6157 | 1 | 0x02800752
GSMKlima1Analog_izh_VentHlajenja | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_VentHlajenja | [7 empty] | 6157 | 1 | 0x02800753
GSMKlima1Dejanska_zel_temp | INT | IOD_GSM | GSM:.Klima[1].Dejanska_zel_temp | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800754
GSMKlima1DelVentHit1 | DIGITAL | IOD_GSM | GSM:.Klima[1].DelVentHit1 | 0 | 1000 | 0 | 1000 | % | ###.# |  | 6157 | 1 | 0x02800760
GSMKlima1DelVentHit2 | DIGITAL | IOD_GSM | GSM:.Klima[1].DelVentHit2 | 0 | 1000 | 0 | 1000 | % | ###.# |  | 6157 | 1 | 0x02800770
GSMKlima1Hitrost_del_vent_disp | INT | IOD_GSM | GSM:.Klima[1].Hitrost_del_vent_disp | 0 | 1000 | 0 | 1000 | % | ### |  | 6157 | 1 | 0x02800780
GSMKlima1Max_vpih | INT | IOD_GSM | GSM:.Klima[1].Max_vpih | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800781
GSMKlima1Min_vpih | INT | IOD_GSM | GSM:.Klima[1].Min_vpih | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800782
GSMKlima1Ni_pretoka | DIGITAL | IOD_GSM | GSM:.Klima[1].Ni_pretoka | [7 empty] | 6157 | 1 | 0x02800790
GSMKlima1Obrat_ure_Vent_h1 | INT | IOD_GSM | GSM:.Klima[1].Obrat_ure_Vent_h1 | [7 empty] | 6157 | 1 | 0x028007a0
GSMKlima1Obrat_ure_Vent_h2 | INT | IOD_GSM | GSM:.Klima[1].Obrat_ure_Vent_h2 | [7 empty] | 6157 | 1 | 0x028007a1
GSMKlima1OkvaraRototerm | DIGITAL | IOD_GSM | GSM:.Klima[1].OkvaraRototerm | [7 empty] | 6157 | 1 | 0x028007b0
GSMKlima1OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.Klima[1].OkvaraVlazNap | [7 empty] | 6157 | 1 | 0x028007c0
GSMKlima1Pol_komp_konec | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_konec | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028007d0
GSMKlima1Pol_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_sprem_zel_vr | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028007d1
GSMKlima1Pol_komp_zacetek | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_zacetek | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028007d2
GSMKlima1PreklopHitDelVent | INT | IOD_GSM | GSM:.Klima[1].PreklopHitDelVent | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028007d3
GSMKlima1PreobMotCrpGrel | DIGITAL | IOD_GSM | GSM:.Klima[1].PreobMotCrpGrel | [7 empty] | 6157 | 1 | 0x028007e0
GSMKlima1PreobMotVent | DIGITAL | IOD_GSM | GSM:.Klima[1].PreobMotVent | [7 empty] | 6157 | 1 | 0x028007f0
GSMKlima1Protizamrz_zascita | INT | IOD_GSM | GSM:.Klima[1].Protizamrz_zascita | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800800
GSMKlima1ProtizamrzZascAktivna | DIGITAL | IOD_GSM | GSM:.Klima[1].ProtizamrzZascAktivna | [7 empty] | 6157 | 1 | 0x02800810
GSMKlima1Rezim_delovanja | INT | IOD_GSM | GSM:.Klima[1].Rezim_delovanja | [7 empty] | 6157 | 1 | 0x02800820
GSMKlima1Temperatura_dovoda | INT | IOD_GSM | GSM:.Klima[1].Temperatura_dovoda | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800821
GSMKlima1Temperatura_prostora | INT | IOD_GSM | GSM:.Klima[1].Temperatura_prostora | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800822
GSMKlima1TempPredPloscnimRekup | INT | IOD_GSM | GSM:.Klima[1].TempPredPloscnimRekup | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800823
GSMKlima1TempZaPloscnimRekup | INT | IOD_GSM | GSM:.Klima[1].TempZaPloscnimRekup | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800824
GSMKlima1VklopRegKlimata | DIGITAL | IOD_GSM | GSM:.Klima[1].VklopRegKlimata | [7 empty] | 6157 | 1 | 0x02800830
GSMKlima1Vlaga_v_prostoru | INT | IOD_GSM | GSM:.Klima[1].Vlaga_v_prostoru | 0 | 1000 | 0 | 100 | % | ##.# |  | 6157 | 1 | 0x02800840
GSMKlima1VlagaVstopZrakaProstor | INT | IOD_GSM | GSM:.Klima[1].VlagaVstopZrakaProstor | 0 | 1000 | 0 | 100 | % | ##.# |  | 6157 | 1 | 0x02800841
GSMKlima1ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.Klima[1].ZamasenostFiltra | [7 empty] | 6157 | 1 | 0x02800850
GSMKlima1ZdruzAlarmA | DIGITAL | IOD_GSM | GSM:.Klima[1].ZdruzAlarmA | [7 empty] | 6157 | 1 | 0x02800860
GSMKlima1ZdruzAlarmB | DIGITAL | IOD_GSM | GSM:.Klima[1].ZdruzAlarmB | [7 empty] | 6157 | 1 | 0x02800870
GSMKlima1Zel_temp_eko_gretja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_eko_gretja | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800880
GSMKlima1Zel_temp_eko_hlajenja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_eko_hlajenja | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800881
GSMKlima1Zel_temp_komf_gretja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_komf_gretja | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800882
GSMKlima1Zel_temp_komf_hlajenja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_komf_hlajenja | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800883
GSMKlima1Zim_komp_konec | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_konec | -400 | 600 | -40 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800884
GSMKlima1Zim_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_sprem_zel_vr | -400 | 600 | -40 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800885
GSMKlima1Zim_komp_zacetek | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_zacetek | -400 | 600 | -40 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800886
GSMKlima1ZimKompMinVpihKonec | INT | IOD_GSM | GSM:.Klima[1].ZimKompMinVpihKonec | -400 | 600 | -40 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800887
GSMKlima1ZimKompMinVpihZac | INT | IOD_GSM | GSM:.Klima[1].ZimKompMinVpihZac | -400 | 600 | -40 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800888
GSMKlima1ZkompMinVpihSpremZelVr | INT | IOD_GSM | GSM:.Klima[1].ZkompMinVpihSpremZelVr | -400 | 600 | -40 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800889
GSMKlima1Zunanja_temp | INT | IOD_GSM | GSM:.Klima[1].Zunanja_temp | -400 | 600 | -40 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x0280088a
GSMKlima2Alarm_pozar | DIGITAL | IOD_GSM | GSM:.Klima[2].Alarm_pozar | [7 empty] | 6157 | 1 | 0x02800890
GSMKlima2Analog_izh_mesanje | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_mesanje | [7 empty] | 6157 | 1 | 0x028008a0
GSMKlima2Analog_izh_rekuperator | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_rekuperator | [7 empty] | 6157 | 1 | 0x028008a1
GSMKlima2Analog_izh_VentGrelnika | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_VentGrelnika | [7 empty] | 6157 | 1 | 0x028008a2
GSMKlima2Analog_izh_VentHlajenja | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_VentHlajenja | [7 empty] | 6157 | 1 | 0x028008a3
GSMKlima2Dejanska_zel_temp | INT | IOD_GSM | GSM:.Klima[2].Dejanska_zel_temp | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028008a4
GSMKlima2DelVentHit1 | DIGITAL | IOD_GSM | GSM:.Klima[2].DelVentHit1 | 0 | 1000 | 0 | 1000 | % | ###.# |  | 6157 | 1 | 0x028008b0
GSMKlima2DelVentHit2 | DIGITAL | IOD_GSM | GSM:.Klima[2].DelVentHit2 | 0 | 1000 | 0 | 1000 | % | ###.# |  | 6157 | 1 | 0x028008c0
GSMKlima2Hitrost_del_vent_disp | INT | IOD_GSM | GSM:.Klima[2].Hitrost_del_vent_disp | 0 | 1000 | 0 | 1000 | % | ### |  | 6157 | 1 | 0x028008d0
GSMKlima2Max_vpih | INT | IOD_GSM | GSM:.Klima[2].Max_vpih | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028008d1
GSMKlima2Min_vpih | INT | IOD_GSM | GSM:.Klima[2].Min_vpih | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028008d2
GSMKlima2Ni_pretoka | DIGITAL | IOD_GSM | GSM:.Klima[2].Ni_pretoka | [7 empty] | 6157 | 1 | 0x028008e0
GSMKlima2Obrat_ure_Vent_h1 | INT | IOD_GSM | GSM:.Klima[2].Obrat_ure_Vent_h1 | [7 empty] | 6157 | 1 | 0x028008f0
GSMKlima2Obrat_ure_Vent_h2 | INT | IOD_GSM | GSM:.Klima[2].Obrat_ure_Vent_h2 | [7 empty] | 6157 | 1 | 0x028008f1
GSMKlima2OkvaraRototerm | DIGITAL | IOD_GSM | GSM:.Klima[2].OkvaraRototerm | [7 empty] | 6157 | 1 | 0x02800900
GSMKlima2OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.Klima[2].OkvaraVlazNap | [7 empty] | 6157 | 1 | 0x02800910
GSMKlima2Pol_komp_konec | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_konec | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800920
GSMKlima2Pol_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_sprem_zel_vr | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800921
GSMKlima2Pol_komp_zacetek | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_zacetek | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800922
GSMKlima2PreklopHitDelVent | INT | IOD_GSM | GSM:.Klima[2].PreklopHitDelVent | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800923
GSMKlima2PreobMotCrpGrel | DIGITAL | IOD_GSM | GSM:.Klima[2].PreobMotCrpGrel | [7 empty] | 6157 | 1 | 0x02800930
GSMKlima2PreobMotVent | DIGITAL | IOD_GSM | GSM:.Klima[2].PreobMotVent | [7 empty] | 6157 | 1 | 0x02800940
GSMKlima2Protizamrz_zascita | INT | IOD_GSM | GSM:.Klima[2].Protizamrz_zascita | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800950
GSMKlima2ProtizamrzZascAktivna | DIGITAL | IOD_GSM | GSM:.Klima[2].ProtizamrzZascAktivna | [7 empty] | 6157 | 1 | 0x02800960
GSMKlima2Rezim_delovanja | INT | IOD_GSM | GSM:.Klima[2].Rezim_delovanja | [7 empty] | 6157 | 1 | 0x02800970
GSMKlima2Temperatura_dovoda | INT | IOD_GSM | GSM:.Klima[2].Temperatura_dovoda | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800971
GSMKlima2Temperatura_prostora | INT | IOD_GSM | GSM:.Klima[2].Temperatura_prostora | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800972
GSMKlima2TempPredPloscnimRekup | INT | IOD_GSM | GSM:.Klima[2].TempPredPloscnimRekup | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800973
GSMKlima2TempZaPloscnimRekup | INT | IOD_GSM | GSM:.Klima[2].TempZaPloscnimRekup | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02800974
GSMKlima2VklopRegKlimata | DIGITAL | IOD_GSM | GSM:.Klima[2].VklopRegKlimata | [7 empty] | 6157 | 1 | 0x02800980
GSMKlima2Vlaga_v_prostoru | INT | IOD_GSM | GSM:.Klima[2].Vlaga_v_prostoru | 0 | 1000 | 0 | 100 | % | ##.# |  | 6157 | 1 | 0x02800990
GSMKlima2VlagaVstopZrakaProstor | INT | IOD_GSM | GSM:.Klima[2].VlagaVstopZrakaProstor | 0 | 1000 | 0 | 100 | % | ##.# |  | 6157 | 1 | 0x02800991
GSMKlima2ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.Klima[2].ZamasenostFiltra | [7 empty] | 6157 | 1 | 0x028009a0
GSMKlima2ZdruzAlarmA | DIGITAL | IOD_GSM | GSM:.Klima[2].ZdruzAlarmA | [7 empty] | 6157 | 1 | 0x028009b0
GSMKlima2ZdruzAlarmB | DIGITAL | IOD_GSM | GSM:.Klima[2].ZdruzAlarmB | [7 empty] | 6157 | 1 | 0x028009c0
GSMKlima2Zel_temp_eko_gretja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_eko_gretja | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028009d0
GSMKlima2Zel_temp_eko_hlajenja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_eko_hlajenja | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028009d1
GSMKlima2Zel_temp_komf_gretja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_komf_gretja | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028009d2
GSMKlima2Zel_temp_komf_hlajenja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_komf_hlajenja | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028009d3
GSMKlima2Zim_komp_konec | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_konec | -400 | 600 | -40 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028009d4
GSMKlima2Zim_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_sprem_zel_vr | -400 | 600 | -40 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028009d5
GSMKlima2Zim_komp_zacetek | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_zacetek | -400 | 600 | -40 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028009d6
GSMKlima2ZimKompMinVpihKonec | INT | IOD_GSM | GSM:.Klima[2].ZimKompMinVpihKonec | -400 | 600 | -40 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028009d7
GSMKlima2ZimKompMinVpihZac | INT | IOD_GSM | GSM:.Klima[2].ZimKompMinVpihZac | -400 | 600 | -40 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028009d8
GSMKlima2ZkompMinVpihSpremZelVr | INT | IOD_GSM | GSM:.Klima[2].ZkompMinVpihSpremZelVr | -400 | 600 | -40 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028009d9
GSMKlima2Zunanja_temp | INT | IOD_GSM | GSM:.Klima[2].Zunanja_temp | -400 | 600 | -40 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028009da
GSMKLIMA_m1_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMA_m1_delovanje | [7 empty] | 6157 | 1 | 0x028009e0
GSMKLIMA_m1_napaka | DIGITAL | IOD_GSM | GSM:.KLIMA_m1_napaka | [7 empty] | 6157 | 1 | 0x028009f0
GSMKLIMA_m2_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMA_m2_delovanje | [7 empty] | 6157 | 1 | 0x02800a00
GSMKLIMA_m2_napaka | DIGITAL | IOD_GSM | GSM:.KLIMA_m2_napaka | [7 empty] | 6157 | 1 | 0x02800a10
GSMKlimaIzklopObrUre | INT | IOD_GSM | GSM:.KlimaIzklopObrUre | [7 empty] | 6157 | 1 | 0x02800a20
GSMKLIMAT1_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMAT1_delovanje | [7 empty] | 6157 | 1 | 0x02800a30
GSMKLIMAT1_napaka | DIGITAL | IOD_GSM | GSM:.KLIMAT1_napaka | [7 empty] | 6157 | 1 | 0x02800a40
GSMKLIMAT1_vklop_delovanja | DIGITAL | IOD_GSM | GSM:.KLIMAT1_vklop_delovanja | [7 empty] | 6157 | 1 | 0x02800a50
GSMKLIMAT2_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMAT2_delovanje | [7 empty] | 6157 | 1 | 0x02800a60
GSMKLIMAT2_napaka | DIGITAL | IOD_GSM | GSM:.KLIMAT2_napaka | [7 empty] | 6157 | 1 | 0x02800a70
GSMKLIMAT2_vklop_delovanja | DIGITAL | IOD_GSM | GSM:.KLIMAT2_vklop_delovanja | [7 empty] | 6157 | 1 | 0x02800a80
GSMKlimeAVTO | DIGITAL | IOD_GSM | GSM:.KlimeAVTO | [7 empty] | 6157 | 1 | 0x02800a90
GSMkom_nast_cas_izpada | UINT | IOD_GSM | GSM:.kom_nast_cas_izpada | [7 empty] | 6157 | 1 | 0x02800aa0
GSMN_F1_1_zascita_ok | DIGITAL | IOD_GSM | GSM:.N_F1_1_zascita_ok | [7 empty] | 6157 | 1 | 0x02800ab0
GSMN_KLIMA1_krm_nap_ok | DIGITAL | IOD_GSM | GSM:.N_KLIMA1_krm_nap_ok | [7 empty] | 6157 | 1 | 0x02800ac0
GSMN_KLIMAT1_napaka | DIGITAL | IOD_GSM | GSM:.N_KLIMAT1_napaka | [7 empty] | 6157 | 1 | 0x02800ad0
GSMN_KLIMAT2_napaka | DIGITAL | IOD_GSM | GSM:.N_KLIMAT2_napaka | [7 empty] | 6157 | 1 | 0x02800ae0
GSMN_Q12_izpad | DIGITAL | IOD_GSM | GSM:.N_Q12_izpad | [7 empty] | 6157 | 1 | 0x02800af0
GSMN_UPS_A_V23_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_A_V23_delovanje | [7 empty] | 6157 | 1 | 0x02800b00
GSMN_UPS_A_V23_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_A_V23_napaka | [7 empty] | 6157 | 1 | 0x02800b10
GSMN_UPS_V23_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_V23_delovanje | [7 empty] | 6157 | 1 | 0x02800b20
GSMN_UPS_V23_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_V23_napaka | [7 empty] | 6157 | 1 | 0x02800b30
GSMN_UPS_V25_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_V25_delovanje | [7 empty] | 6157 | 1 | 0x02800b40
GSMN_UPS_V25_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_V25_napaka | [7 empty] | 6157 | 1 | 0x02800b50
GSMN_VLAZILEC1_napaka | DIGITAL | IOD_GSM | GSM:.N_VLAZILEC1_napaka | [7 empty] | 6157 | 1 | 0x02800b60
GSMN_VLAZILEC2_napaka | DIGITAL | IOD_GSM | GSM:.N_VLAZILEC2_napaka | [7 empty] | 6157 | 1 | 0x02800b70
GSMnapaka_kom_panel | DIGITAL | IOD_GSM | GSM:.napaka_kom_panel | [7 empty] | 6157 | 1 | 0x02800b80
GSMnapaka_kom_scada | DIGITAL | IOD_GSM | GSM:.napaka_kom_scada | [7 empty] | 6157 | 1 | 0x02800b90
GSMnapaka_kom_scada2 | DIGITAL | IOD_GSM | GSM:.napaka_kom_scada2 | [7 empty] | 6157 | 1 | 0x02800ba0
GSMNapakaSenzorSkupno | DIGITAL | IOD_GSM | GSM:.NapakaSenzorSkupno | [7 empty] | 6157 | 1 | 0x02800bb0
GSMNapakaSenzorVlagaHIA1 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA1 | [7 empty] | 6157 | 1 | 0x02800bc0
GSMNapakaSenzorVlagaHIA2 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA2 | [7 empty] | 6157 | 1 | 0x02800bd0
GSMNapakaSenzorVlagaHIA3 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA3 | [7 empty] | 6157 | 1 | 0x02800be0
GSMNapakaSenzorVlagaHIA4 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA4 | [7 empty] | 6157 | 1 | 0x02800bf0
GSMNapakaSenzorVlagaHIA5 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA5 | [7 empty] | 6157 | 1 | 0x02800c00
GSMNapakaSenzorVlagaHIA6 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA6 | [7 empty] | 6157 | 1 | 0x02800c10
GSMNapakaSenzorVlagaHIA7 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA7 | [7 empty] | 6157 | 1 | 0x02800c20
GSMNapakaTSTempTIA1 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA1 | [7 empty] | 6157 | 1 | 0x02800c30
GSMNapakaTSTempTIA2 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA2 | [7 empty] | 6157 | 1 | 0x02800c40
GSMNapakaTSTempTIA3 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA3 | [7 empty] | 6157 | 1 | 0x02800c50
GSMNapakaTSTempTIA4 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA4 | [7 empty] | 6157 | 1 | 0x02800c60
GSMNapakaTSTempTIA5 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA5 | [7 empty] | 6157 | 1 | 0x02800c70
GSMNapakaTSTempTIA6 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA6 | [7 empty] | 6157 | 1 | 0x02800c80
GSMNapakaTSTempTIA7 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA7 | [7 empty] | 6157 | 1 | 0x02800c90
GSMOpozoriloPMM2x17med60in8010 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[10] | [7 empty] | 6157 | 1 | 0x02800ca0
GSMOpozoriloPMM2x17med60in8011 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[11] | [7 empty] | 6157 | 1 | 0x02800cb0
GSMOpozoriloPMM2x17med60in8012 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[12] | [7 empty] | 6157 | 1 | 0x02800cc0
GSMOpozoriloPMM2x17med60in8013 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[13] | [7 empty] | 6157 | 1 | 0x02800cd0
GSMOpozoriloPMM2x17med60in8014 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[14] | [7 empty] | 6157 | 1 | 0x02800ce0
GSMOpozoriloPMM2x17med60in8015 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[15] | [7 empty] | 6157 | 1 | 0x02800cf0
GSMOpozoriloPMM2x17med60in8016 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[16] | [7 empty] | 6157 | 1 | 0x02800d00
GSMOpozoriloPMM2x17med60in8017 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[17] | [7 empty] | 6157 | 1 | 0x02800d10
GSMOpozoriloPMM2x17med60in8018 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[18] | [7 empty] | 6157 | 1 | 0x02800d20
GSMOpozoriloPMM2x17med60in8019 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[19] | [7 empty] | 6157 | 1 | 0x02800d30
GSMOpozoriloPMM2x17med60in801 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[1] | [7 empty] | 6157 | 1 | 0x02800d40
GSMOpozoriloPMM2x17med60in8020 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[20] | [7 empty] | 6157 | 1 | 0x02800d50
GSMOpozoriloPMM2x17med60in8021 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[21] | [7 empty] | 6157 | 1 | 0x02800d60
GSMOpozoriloPMM2x17med60in8022 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[22] | [7 empty] | 6157 | 1 | 0x02800d70
GSMOpozoriloPMM2x17med60in8023 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[23] | [7 empty] | 6157 | 1 | 0x02800d80
GSMOpozoriloPMM2x17med60in8024 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[24] | [7 empty] | 6157 | 1 | 0x02800d90
GSMOpozoriloPMM2x17med60in8025 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[25] | [7 empty] | 6157 | 1 | 0x02800da0
GSMOpozoriloPMM2x17med60in8026 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[26] | [7 empty] | 6157 | 1 | 0x02800db0
GSMOpozoriloPMM2x17med60in8027 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[27] | [7 empty] | 6157 | 1 | 0x02800dc0
GSMOpozoriloPMM2x17med60in8028 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[28] | [7 empty] | 6157 | 1 | 0x02800dd0
GSMOpozoriloPMM2x17med60in8029 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[29] | [7 empty] | 6157 | 1 | 0x02800de0
GSMOpozoriloPMM2x17med60in802 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[2] | [7 empty] | 6157 | 1 | 0x02800df0
GSMOpozoriloPMM2x17med60in8030 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[30] | [7 empty] | 6157 | 1 | 0x02800e00
GSMOpozoriloPMM2x17med60in8031 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[31] | [7 empty] | 6157 | 1 | 0x02800e10
GSMOpozoriloPMM2x17med60in8032 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[32] | [7 empty] | 6157 | 1 | 0x02800e20
GSMOpozoriloPMM2x17med60in8033 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[33] | [7 empty] | 6157 | 1 | 0x02800e30
GSMOpozoriloPMM2x17med60in8034 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[34] | [7 empty] | 6157 | 1 | 0x02800e40
GSMOpozoriloPMM2x17med60in8035 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[35] | [7 empty] | 6157 | 1 | 0x02800e50
GSMOpozoriloPMM2x17med60in8036 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[36] | [7 empty] | 6157 | 1 | 0x02800e60
GSMOpozoriloPMM2x17med60in8037 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[37] | [7 empty] | 6157 | 1 | 0x02800e70
GSMOpozoriloPMM2x17med60in8038 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[38] | [7 empty] | 6157 | 1 | 0x02800e80
GSMOpozoriloPMM2x17med60in8039 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[39] | [7 empty] | 6157 | 1 | 0x02800e90
GSMOpozoriloPMM2x17med60in803 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[3] | [7 empty] | 6157 | 1 | 0x02800ea0
GSMOpozoriloPMM2x17med60in8040 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[40] | [7 empty] | 6157 | 1 | 0x02800eb0
GSMOpozoriloPMM2x17med60in8041 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[41] | [7 empty] | 6157 | 1 | 0x02800ec0
GSMOpozoriloPMM2x17med60in8042 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[42] | [7 empty] | 6157 | 1 | 0x02800ed0
GSMOpozoriloPMM2x17med60in804 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[4] | [7 empty] | 6157 | 1 | 0x02800ee0
GSMOpozoriloPMM2x17med60in805 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[5] | [7 empty] | 6157 | 1 | 0x02800ef0
GSMOpozoriloPMM2x17med60in806 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[6] | [7 empty] | 6157 | 1 | 0x02800f00
GSMOpozoriloPMM2x17med60in807 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[7] | [7 empty] | 6157 | 1 | 0x02800f10
GSMOpozoriloPMM2x17med60in808 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[8] | [7 empty] | 6157 | 1 | 0x02800f20
GSMOpozoriloPMM2x17med60in809 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[9] | [7 empty] | 6157 | 1 | 0x02800f30
GSMPMM1OverCurrentBetw1 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[1] | [7 empty] | 6157 | 1 | 0x02800f40
GSMPMM1OverCurrentBetw2 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[2] | [7 empty] | 6157 | 1 | 0x02800f50
GSMPMM1OverCurrentBetw3 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[3] | [7 empty] | 6157 | 1 | 0x02800f60
GSMPMM1OverCurrentOver1 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[1] | [7 empty] | 6157 | 1 | 0x02800f70
GSMPMM1OverCurrentOver2 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[2] | [7 empty] | 6157 | 1 | 0x02800f80
GSMPMM1OverCurrentOver3 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[3] | [7 empty] | 6157 | 1 | 0x02800f90
GSMPMM1ActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM[1].ActiveEnergyConsumed_kWh | 0 | 1000 | 0 | 1000 | kVARh | #### |  | 6157 | 1 | 0x02800fa0
GSMPMM1ActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseA_kW | 0 | 100 | 0 | 100 | kW | ####.# |  | 6157 | 1 | 0x02800fa1
GSMPMM1ActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseB_kW | 0 | 100 | 0 | 100 | kW | ####.# |  | 6157 | 1 | 0x02800fa2
GSMPMM1ActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseC_kW | 0 | 100 | 0 | 100 | kW | ####.# |  | 6157 | 1 | 0x02800fa3
GSMPMM1AlarmPhase1C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C01_16_60to80 | [7 empty] | 6157 | 1 | 0x02800fa4
GSMPMM1AlarmPhase1C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C01_16_over80 | [7 empty] | 6157 | 1 | 0x02800fa5
GSMPMM1AlarmPhase1C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C17_32_60to80 | [7 empty] | 6157 | 1 | 0x02800fa6
GSMPMM1AlarmPhase1C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C17_32_over80 | [7 empty] | 6157 | 1 | 0x02800fa7
GSMPMM1AlarmPhase1C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C33_42_60to80 | [7 empty] | 6157 | 1 | 0x02800fa8
GSMPMM1AlarmPhase1C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C33_42_over80 | [7 empty] | 6157 | 1 | 0x02800fa9
GSMPMM1AlarmPhase1GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].GlobalAlarmReg | [7 empty] | 6157 | 1 | 0x02800faa
GSMPMM1AlarmPhase2C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C01_16_60to80 | [7 empty] | 6157 | 1 | 0x02800fab
GSMPMM1AlarmPhase2C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C01_16_over80 | [7 empty] | 6157 | 1 | 0x02800fac
GSMPMM1AlarmPhase2C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C17_32_60to80 | [7 empty] | 6157 | 1 | 0x02800fad
GSMPMM1AlarmPhase2C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C17_32_over80 | [7 empty] | 6157 | 1 | 0x02800fae
GSMPMM1AlarmPhase2C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C33_42_60to80 | [7 empty] | 6157 | 1 | 0x02800faf
GSMPMM1AlarmPhase2C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C33_42_over80 | [7 empty] | 6157 | 1 | 0x02800fb0
GSMPMM1AlarmPhase2GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].GlobalAlarmReg | [7 empty] | 6157 | 1 | 0x02800fb1
GSMPMM1AlarmPhase3C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C01_16_60to80 | [7 empty] | 6157 | 1 | 0x02800fb2
GSMPMM1AlarmPhase3C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C01_16_over80 | [7 empty] | 6157 | 1 | 0x02800fb3
GSMPMM1AlarmPhase3C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C17_32_60to80 | [7 empty] | 6157 | 1 | 0x02800fb4
GSMPMM1AlarmPhase3C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C17_32_over80 | [7 empty] | 6157 | 1 | 0x02800fb5
GSMPMM1AlarmPhase3C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C33_42_60to80 | [7 empty] | 6157 | 1 | 0x02800fb6
GSMPMM1AlarmPhase3C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C33_42_over80 | [7 empty] | 6157 | 1 | 0x02800fb7
GSMPMM1AlarmPhase3GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].GlobalAlarmReg | [7 empty] | 6157 | 1 | 0x02800fb8
GSMPMM1AparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseA | 0 | 100 | 0 | 100 | kVAR | ####.# |  | 6157 | 1 | 0x02800fb9
GSMPMM1AparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseB | 0 | 100 | 0 | 100 | kVAR | ####.# |  | 6157 | 1 | 0x02800fba
GSMPMM1AparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseC | 0 | 100 | 0 | 100 | kVAR | ####.# |  | 6157 | 1 | 0x02800fbb
GSMPMM1AverageCurrent_A | REAL | IOD_GSM | GSM:.PMM[1].AverageCurrent_A | 0 | 16 | 0 | 16 | A | ####.# |  | 6157 | 1 | 0x02800fbc
GSMPMM1AveragePhaseToNeutral_V | REAL | IOD_GSM | GSM:.PMM[1].AveragePhaseToNeutral_V | 0 | 270 | 0 | 270 | V | ####.# |  | 6157 | 1 | 0x02800fbd
GSMPMM1AveragePhaseToPhase_V | REAL | IOD_GSM | GSM:.PMM[1].AveragePhaseToPhase_V | 0 | 450 | 0 | 450 | V | ####.# |  | 6157 | 1 | 0x02800fbe
GSMPMM1CurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseA_A | 0 | 500 | 0 | 500 | A | ####.# |  | 6157 | 1 | 0x02800fbf
GSMPMM1CurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseB_A | 0 | 500 | 0 | 500 | A | ####.# |  | 6157 | 1 | 0x02800fc0
GSMPMM1CurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseC_A | 0 | 500 | 0 | 500 | A | ####.# |  | 6157 | 1 | 0x02800fc1
GSMPMM1Frequency_Hz | REAL | IOD_GSM | GSM:.PMM[1].Frequency_Hz | 0 | 70 | 0 | 70 | Hz | ####.# |  | 6157 | 1 | 0x02800fc2
GSMPMM1Phase1Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[10] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fc3
GSMPMM1Phase1Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[11] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fc4
GSMPMM1Phase1Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[12] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fc5
GSMPMM1Phase1Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[13] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fc6
GSMPMM1Phase1Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[14] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fc7
GSMPMM1Phase1Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[15] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fc8
GSMPMM1Phase1Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[16] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fc9
GSMPMM1Phase1Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[17] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fca
GSMPMM1Phase1Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[18] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fcb
GSMPMM1Phase1Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[19] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fcc
GSMPMM1Phase1Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[1] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fcd
GSMPMM1Phase1Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[20] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fce
GSMPMM1Phase1Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[21] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fcf
GSMPMM1Phase1Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[22] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fd0
GSMPMM1Phase1Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[23] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fd1
GSMPMM1Phase1Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[24] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fd2
GSMPMM1Phase1Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[25] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fd3
GSMPMM1Phase1Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[26] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fd4
GSMPMM1Phase1Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[27] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fd5
GSMPMM1Phase1Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[28] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fd6
GSMPMM1Phase1Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[29] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fd7
GSMPMM1Phase1Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[2] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fd8
GSMPMM1Phase1Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[30] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fd9
GSMPMM1Phase1Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[31] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fda
GSMPMM1Phase1Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[32] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fdb
GSMPMM1Phase1Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[33] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fdc
GSMPMM1Phase1Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[34] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fdd
GSMPMM1Phase1Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[35] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fde
GSMPMM1Phase1Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[36] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fdf
GSMPMM1Phase1Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[37] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fe0
GSMPMM1Phase1Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[38] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fe1
GSMPMM1Phase1Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[39] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fe2
GSMPMM1Phase1Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[3] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fe3
GSMPMM1Phase1Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[40] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fe4
GSMPMM1Phase1Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[41] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fe5
GSMPMM1Phase1Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[42] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fe6
GSMPMM1Phase1Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[4] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fe7
GSMPMM1Phase1Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[5] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fe8
GSMPMM1Phase1Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[6] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fe9
GSMPMM1Phase1Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[7] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fea
GSMPMM1Phase1Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[8] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800feb
GSMPMM1Phase1Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[9] | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02800fec
GSMPMM1Phase2Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[10] | [7 empty] | 6157 | 1 | 0x02800fed
GSMPMM1Phase2Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[11] | [7 empty] | 6157 | 1 | 0x02800fee
GSMPMM1Phase2Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[12] | [7 empty] | 6157 | 1 | 0x02800fef
GSMPMM1Phase2Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[13] | [7 empty] | 6157 | 1 | 0x02800ff0
GSMPMM1Phase2Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[14] | [7 empty] | 6157 | 1 | 0x02800ff1
GSMPMM1Phase2Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[15] | [7 empty] | 6157 | 1 | 0x02800ff2
GSMPMM1Phase2Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[16] | [7 empty] | 6157 | 1 | 0x02800ff3
GSMPMM1Phase2Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[17] | [7 empty] | 6157 | 1 | 0x02800ff4
GSMPMM1Phase2Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[18] | [7 empty] | 6157 | 1 | 0x02800ff5
GSMPMM1Phase2Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[19] | [7 empty] | 6157 | 1 | 0x02800ff6
GSMPMM1Phase2Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[1] | [7 empty] | 6157 | 1 | 0x02800ff7
GSMPMM1Phase2Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[20] | [7 empty] | 6157 | 1 | 0x02800ff8
GSMPMM1Phase2Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[21] | [7 empty] | 6157 | 1 | 0x02800ff9
GSMPMM1Phase2Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[22] | [7 empty] | 6157 | 1 | 0x02800ffa
GSMPMM1Phase2Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[23] | [7 empty] | 6157 | 1 | 0x02800ffb
GSMPMM1Phase2Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[24] | [7 empty] | 6157 | 1 | 0x02800ffc
GSMPMM1Phase2Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[25] | [7 empty] | 6157 | 1 | 0x02800ffd
GSMPMM1Phase2Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[26] | [7 empty] | 6157 | 1 | 0x02800ffe
GSMPMM1Phase2Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[27] | [7 empty] | 6157 | 1 | 0x02800fff
GSMPMM1Phase2Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[28] | [7 empty] | 6157 | 1 | 0x02801000
GSMPMM1Phase2Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[29] | [7 empty] | 6157 | 1 | 0x02801001
GSMPMM1Phase2Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[2] | [7 empty] | 6157 | 1 | 0x02801002
GSMPMM1Phase2Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[30] | [7 empty] | 6157 | 1 | 0x02801003
GSMPMM1Phase2Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[31] | [7 empty] | 6157 | 1 | 0x02801004
GSMPMM1Phase2Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[32] | [7 empty] | 6157 | 1 | 0x02801005
GSMPMM1Phase2Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[33] | [7 empty] | 6157 | 1 | 0x02801006
GSMPMM1Phase2Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[34] | [7 empty] | 6157 | 1 | 0x02801007
GSMPMM1Phase2Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[35] | [7 empty] | 6157 | 1 | 0x02801008
GSMPMM1Phase2Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[36] | [7 empty] | 6157 | 1 | 0x02801009
GSMPMM1Phase2Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[37] | [7 empty] | 6157 | 1 | 0x0280100a
GSMPMM1Phase2Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[38] | [7 empty] | 6157 | 1 | 0x0280100b
GSMPMM1Phase2Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[39] | [7 empty] | 6157 | 1 | 0x0280100c
GSMPMM1Phase2Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[3] | [7 empty] | 6157 | 1 | 0x0280100d
GSMPMM1Phase2Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[40] | [7 empty] | 6157 | 1 | 0x0280100e
GSMPMM1Phase2Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[41] | [7 empty] | 6157 | 1 | 0x0280100f
GSMPMM1Phase2Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[42] | [7 empty] | 6157 | 1 | 0x02801010
GSMPMM1Phase2Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[4] | [7 empty] | 6157 | 1 | 0x02801011
GSMPMM1Phase2Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[5] | [7 empty] | 6157 | 1 | 0x02801012
GSMPMM1Phase2Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[6] | [7 empty] | 6157 | 1 | 0x02801013
GSMPMM1Phase2Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[7] | [7 empty] | 6157 | 1 | 0x02801014
GSMPMM1Phase2Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[8] | [7 empty] | 6157 | 1 | 0x02801015
GSMPMM1Phase2Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[9] | [7 empty] | 6157 | 1 | 0x02801016
GSMPMM1Phase3Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[10] | [7 empty] | 6157 | 1 | 0x02801017
GSMPMM1Phase3Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[11] | [7 empty] | 6157 | 1 | 0x02801018
GSMPMM1Phase3Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[12] | [7 empty] | 6157 | 1 | 0x02801019
GSMPMM1Phase3Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[13] | [7 empty] | 6157 | 1 | 0x0280101a
GSMPMM1Phase3Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[14] | [7 empty] | 6157 | 1 | 0x0280101b
GSMPMM1Phase3Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[15] | [7 empty] | 6157 | 1 | 0x0280101c
GSMPMM1Phase3Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[16] | [7 empty] | 6157 | 1 | 0x0280101d
GSMPMM1Phase3Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[17] | [7 empty] | 6157 | 1 | 0x0280101e
GSMPMM1Phase3Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[18] | [7 empty] | 6157 | 1 | 0x0280101f
GSMPMM1Phase3Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[19] | [7 empty] | 6157 | 1 | 0x02801020
GSMPMM1Phase3Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[1] | [7 empty] | 6157 | 1 | 0x02801021
GSMPMM1Phase3Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[20] | [7 empty] | 6157 | 1 | 0x02801022
GSMPMM1Phase3Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[21] | [7 empty] | 6157 | 1 | 0x02801023
GSMPMM1Phase3Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[22] | [7 empty] | 6157 | 1 | 0x02801024
GSMPMM1Phase3Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[23] | [7 empty] | 6157 | 1 | 0x02801025
GSMPMM1Phase3Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[24] | [7 empty] | 6157 | 1 | 0x02801026
GSMPMM1Phase3Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[25] | [7 empty] | 6157 | 1 | 0x02801027
GSMPMM1Phase3Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[26] | [7 empty] | 6157 | 1 | 0x02801028
GSMPMM1Phase3Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[27] | [7 empty] | 6157 | 1 | 0x02801029
GSMPMM1Phase3Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[28] | [7 empty] | 6157 | 1 | 0x0280102a
GSMPMM1Phase3Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[29] | [7 empty] | 6157 | 1 | 0x0280102b
GSMPMM1Phase3Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[2] | [7 empty] | 6157 | 1 | 0x0280102c
GSMPMM1Phase3Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[30] | [7 empty] | 6157 | 1 | 0x0280102d
GSMPMM1Phase3Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[31] | [7 empty] | 6157 | 1 | 0x0280102e
GSMPMM1Phase3Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[32] | [7 empty] | 6157 | 1 | 0x0280102f
GSMPMM1Phase3Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[33] | [7 empty] | 6157 | 1 | 0x02801030
GSMPMM1Phase3Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[34] | [7 empty] | 6157 | 1 | 0x02801031
GSMPMM1Phase3Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[35] | [7 empty] | 6157 | 1 | 0x02801032
GSMPMM1Phase3Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[36] | [7 empty] | 6157 | 1 | 0x02801033
GSMPMM1Phase3Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[37] | [7 empty] | 6157 | 1 | 0x02801034
GSMPMM1Phase3Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[38] | [7 empty] | 6157 | 1 | 0x02801035
GSMPMM1Phase3Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[39] | [7 empty] | 6157 | 1 | 0x02801036
GSMPMM1Phase3Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[3] | [7 empty] | 6157 | 1 | 0x02801037
GSMPMM1Phase3Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[40] | [7 empty] | 6157 | 1 | 0x02801038
GSMPMM1Phase3Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[41] | [7 empty] | 6157 | 1 | 0x02801039
GSMPMM1Phase3Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[42] | [7 empty] | 6157 | 1 | 0x0280103a
GSMPMM1Phase3Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[4] | [7 empty] | 6157 | 1 | 0x0280103b
GSMPMM1Phase3Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[5] | [7 empty] | 6157 | 1 | 0x0280103c
GSMPMM1Phase3Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[6] | [7 empty] | 6157 | 1 | 0x0280103d
GSMPMM1Phase3Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[7] | [7 empty] | 6157 | 1 | 0x0280103e
GSMPMM1Phase3Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[8] | [7 empty] | 6157 | 1 | 0x0280103f
GSMPMM1Phase3Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[9] | [7 empty] | 6157 | 1 | 0x02801040
GSMPMM1PowerFactorSys | REAL | IOD_GSM | GSM:.PMM[1].PowerFactorSys | 0 | 1 | 0 | 1 |  | ####.# |  | 6157 | 1 | 0x02801041
GSMPMM1ReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM[1].ReactiveEnergyConsumed_kVARh | 0 | 1000 | 0 | 1000 | kVARh | #### |  | 6157 | 1 | 0x02801042
GSMPMM1ReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseA | 0 | 100 | 0 | 100 | kVAR | ####.# |  | 6157 | 1 | 0x02801043
GSMPMM1ReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseB | 0 | 100 | 0 | 100 | kVAR | ####.# |  | 6157 | 1 | 0x02801044
GSMPMM1ReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseC | 0 | 100 | 0 | 100 | kVAR | ####.# |  | 6157 | 1 | 0x02801045
GSMPMM1TotalActivePower_kW | REAL | IOD_GSM | GSM:.PMM[1].TotalActivePower_kW | 0 | 300 | 0 | 300 | kW | ####.# |  | 6157 | 1 | 0x02801046
GSMPMM1TotalAparentPower_kVA | REAL | IOD_GSM | GSM:.PMM[1].TotalAparentPower_kVA | 0 | 300 | 0 | 300 | kVA | ####.# |  | 6157 | 1 | 0x02801047
GSMPMM1TotalPowerFactor | REAL | IOD_GSM | GSM:.PMM[1].TotalPowerFactor | 0 | 1 | 0 | 1 |  | ####.# |  | 6157 | 1 | 0x02801048
GSMPMM1TotalReactivePower_kVAR | REAL | IOD_GSM | GSM:.PMM[1].TotalReactivePower_kVAR | 0 | 300 | 0 | 300 | kVAR | ####.# |  | 6157 | 1 | 0x02801049
GSMPMM1VirA_fsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_fsys | 0 | 70 | 0 | 70 | Hz | ####.# |  | 6157 | 1 | 0x0280104a
GSMPMM1VirA_Isys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Isys | 0 | 1000 | 0 | 1000 | A | ####.# |  | 6157 | 1 | 0x0280104b
GSMPMM1VirA_PFsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_PFsys | 0 | 1 | 0 | 1 |  | ####.# |  | 6157 | 1 | 0x0280104c
GSMPMM1VirA_Psys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Psys | 0 | 300 | 0 | 300 | kW | ####.# |  | 6157 | 1 | 0x0280104d
GSMPMM1VirA_Qsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Qsys | 0 | 300 | 0 | 300 | kVAR | ####.# |  | 6157 | 1 | 0x0280104e
GSMPMM1VirA_Ssys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Ssys | 0 | 300 | 0 | 300 | kVA | ####.# |  | 6157 | 1 | 0x0280104f
GSMPMM1VirA_Usys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Usys | 0 | 450 | 0 | 450 | V | ####.# |  | 6157 | 1 | 0x02801050
GSMPMM1VirB_fsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_fsys | 0 | 70 | 0 | 70 | Hz | ####.# |  | 6157 | 1 | 0x02801051
GSMPMM1VirB_Isys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Isys | 0 | 1000 | 0 | 1000 | A | ####.# |  | 6157 | 1 | 0x02801052
GSMPMM1VirB_PFsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_PFsys | 0 | 1 | 0 | 1 |  | ####.# |  | 6157 | 1 | 0x02801053
GSMPMM1VirB_Psys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Psys | 0 | 300 | 0 | 300 | kW | ####.# |  | 6157 | 1 | 0x02801054
GSMPMM1VirB_Qsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Qsys | 0 | 300 | 0 | 300 | kVAR | ####.# |  | 6157 | 1 | 0x02801055
GSMPMM1VirB_Ssys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Ssys | 0 | 300 | 0 | 300 | kVA | ####.# |  | 6157 | 1 | 0x02801056
GSMPMM1VirB_Usys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Usys | 0 | 450 | 0 | 450 | V | ####.# |  | 6157 | 1 | 0x02801057
GSMPMM1VirBActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM[1].VirBActiveEnergyConsumed_kWh | 0 | 1000 | 0 | 1000 | kVARh | ####.# |  | 6157 | 1 | 0x02801058
GSMPMM1VirBActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseA_kW | 0 | 100 | 0 | 100 | kW | ####.# |  | 6157 | 1 | 0x02801059
GSMPMM1VirBActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseB_kW | 0 | 100 | 0 | 100 | kW | ####.# |  | 6157 | 1 | 0x0280105a
GSMPMM1VirBActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseC_kW | 0 | 100 | 0 | 100 | kW | ####.# |  | 6157 | 1 | 0x0280105b
GSMPMM1VirBAparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseA | 0 | 100 | 0 | 100 | kVAR | ####.# |  | 6157 | 1 | 0x0280105c
GSMPMM1VirBAparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseB | 0 | 100 | 0 | 100 | kVAR | ####.# |  | 6157 | 1 | 0x0280105d
GSMPMM1VirBAparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseC | 0 | 100 | 0 | 100 | kVAR | ####.# |  | 6157 | 1 | 0x0280105e
GSMPMM1VirBAverageCurrent_A | REAL | IOD_GSM | GSM:.PMM[1].VirBAverageCurrent_A | 0 | 100 | 0 | 100 | A | ####.# |  | 6157 | 1 | 0x0280105f
GSMPMM1VirBAveragePhaseToNeutral_V | REAL | IOD_GSM | GSM:.PMM[1].VirBAveragePhaseToNeutral_V | 0 | 270 | 0 | 270 | V | ####.# |  | 6157 | 1 | 0x02801060
GSMPMM1VirBAveragePhaseToPhase_V | REAL | IOD_GSM | GSM:.PMM[1].VirBAveragePhaseToPhase_V | 0 | 270 | 0 | 270 | V | ####.# |  | 6157 | 1 | 0x02801061
GSMPMM1VirBCurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseA_A | 0 | 100 | 0 | 100 | A | ####.# |  | 6157 | 1 | 0x02801062
GSMPMM1VirBCurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseB_A | 0 | 100 | 0 | 100 | A | ####.# |  | 6157 | 1 | 0x02801063
GSMPMM1VirBCurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseC_A | 0 | 100 | 0 | 100 | A | ####.# |  | 6157 | 1 | 0x02801064
GSMPMM1VirBFrequency_Hz | REAL | IOD_GSM | GSM:.PMM[1].VirBFrequency_Hz | 0 | 70 | 0 | 70 | Hz | ####.# |  | 6157 | 1 | 0x02801065
GSMPMM1VirBPowerFactorSys | REAL | IOD_GSM | GSM:.PMM[1].VirBPowerFactorSys | 0 | 1 | 0 | 1 |  | ####.# |  | 6157 | 1 | 0x02801066
GSMPMM1VirBReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM[1].VirBReactiveEnergyConsumed_kVARh | 0 | 1000 | 0 | 1000 | kVARh | ####.# |  | 6157 | 1 | 0x02801067
GSMPMM1VirBReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseA | 0 | 100 | 0 | 100 | kVAR | ####.# |  | 6157 | 1 | 0x02801068
GSMPMM1VirBReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseB | 0 | 100 | 0 | 100 | kVAR | ####.# |  | 6157 | 1 | 0x02801069
GSMPMM1VirBReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseC | 0 | 100 | 0 | 100 | kVAR | ####.# |  | 6157 | 1 | 0x0280106a
GSMPMM1VirBTotalActivePower_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalActivePower_kW | 0 | 300 | 0 | 300 | kW | ####.# |  | 6157 | 1 | 0x0280106b
GSMPMM1VirBTotalAparentPower_kVA | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalAparentPower_kVA | 0 | 300 | 0 | 300 | kVA | ####.# |  | 6157 | 1 | 0x0280106c
GSMPMM1VirBTotalPowerFactor | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalPowerFactor | 0 | 1 | 0 | 1 |  | ####.# |  | 6157 | 1 | 0x0280106d
GSMPMM1VirBTotalReactivePower_kVAR | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalReactivePower_kVAR | 0 | 100 | 0 | 100 | kVAR | ####.# |  | 6157 | 1 | 0x0280106e
GSMPMM1VirBVoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseAB_V | 0 | 450 | 0 | 450 | V | ####.# |  | 6157 | 1 | 0x0280106f
GSMPMM1VirBVoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseAN_V | 0 | 270 | 0 | 270 | V | ####.# |  | 6157 | 1 | 0x02801070
GSMPMM1VirBVoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseBC_V | 0 | 450 | 0 | 450 | V | ####.# |  | 6157 | 1 | 0x02801071
GSMPMM1VirBVoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseBN_V | 0 | 270 | 0 | 270 | V | ####.# |  | 6157 | 1 | 0x02801072
GSMPMM1VirBVoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseCA_V | 0 | 450 | 0 | 450 | V | ####.# |  | 6157 | 1 | 0x02801073
GSMPMM1VirBVoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseCN_V | 0 | 270 | 0 | 270 | V | ####.# |  | 6157 | 1 | 0x02801074
GSMPMM1VoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseAB_V | 0 | 450 | 0 | 450 | V | ####.# |  | 6157 | 1 | 0x02801075
GSMPMM1VoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseAN_V | 0 | 270 | 0 | 270 | V | ####.# |  | 6157 | 1 | 0x02801076
GSMPMM1VoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseBC_V | 0 | 450 | 0 | 450 | V | ####.# |  | 6157 | 1 | 0x02801077
GSMPMM1VoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseBN_V | 0 | 270 | 0 | 270 | V | ####.# |  | 6157 | 1 | 0x02801078
GSMPMM1VoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseCA_V | 0 | 450 | 0 | 450 | V | ####.# |  | 6157 | 1 | 0x02801079
GSMPMM1VoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseCN_V | 0 | 270 | 0 | 270 | V | ####.# |  | 6157 | 1 | 0x0280107a
GSMPMMfaza01 | REAL | IOD_GSM | GSM:.PMMfaza01 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x0280107b
GSMPMMfaza02 | REAL | IOD_GSM | GSM:.PMMfaza02 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x0280107c
GSMPMMfaza03 | REAL | IOD_GSM | GSM:.PMMfaza03 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x0280107d
GSMPMMfaza04 | REAL | IOD_GSM | GSM:.PMMfaza04 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x0280107e
GSMPMMfaza05 | REAL | IOD_GSM | GSM:.PMMfaza05 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x0280107f
GSMPMMfaza06 | REAL | IOD_GSM | GSM:.PMMfaza06 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02801080
GSMPMMfaza07 | REAL | IOD_GSM | GSM:.PMMfaza07 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02801081
GSMPMMfaza08 | REAL | IOD_GSM | GSM:.PMMfaza08 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02801082
GSMPMMfaza09 | REAL | IOD_GSM | GSM:.PMMfaza09 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02801083
GSMPMMfaza10 | REAL | IOD_GSM | GSM:.PMMfaza10 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02801084
GSMPMMfaza11 | REAL | IOD_GSM | GSM:.PMMfaza11 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02801085
GSMPMMfaza12 | REAL | IOD_GSM | GSM:.PMMfaza12 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02801086
GSMPMMfaza13 | REAL | IOD_GSM | GSM:.PMMfaza13 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02801087
GSMPMMfaza14 | REAL | IOD_GSM | GSM:.PMMfaza14 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02801088
GSMPMMfaza15 | REAL | IOD_GSM | GSM:.PMMfaza15 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02801089
GSMPMMfaza16 | REAL | IOD_GSM | GSM:.PMMfaza16 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x0280108a
GSMPMMfaza17 | REAL | IOD_GSM | GSM:.PMMfaza17 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x0280108b
GSMPMMfaza18 | REAL | IOD_GSM | GSM:.PMMfaza18 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x0280108c
GSMPMMfaza19 | REAL | IOD_GSM | GSM:.PMMfaza19 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x0280108d
GSMPMMfaza20 | REAL | IOD_GSM | GSM:.PMMfaza20 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x0280108e
GSMPMMfaza21 | REAL | IOD_GSM | GSM:.PMMfaza21 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x0280108f
GSMPMMfaza22 | REAL | IOD_GSM | GSM:.PMMfaza22 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02801090
GSMPMMfaza23 | REAL | IOD_GSM | GSM:.PMMfaza23 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02801091
GSMPMMfaza24 | REAL | IOD_GSM | GSM:.PMMfaza24 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02801092
GSMPMMfaza25 | REAL | IOD_GSM | GSM:.PMMfaza25 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02801093
GSMPMMfaza26 | REAL | IOD_GSM | GSM:.PMMfaza26 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02801094
GSMPMMfaza27 | REAL | IOD_GSM | GSM:.PMMfaza27 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02801095
GSMPMMfaza28 | REAL | IOD_GSM | GSM:.PMMfaza28 | 0 | 20 | 0 | 20 | A | ####.# |  | 6157 | 1 | 0x02801096
GSMPMMfaza29 | REAL | IOD_GSM | GSM:.PMMfaza29 | [7 empty] | 6157 | 1 | 0x02801097
GSMPMMfaza30 | REAL | IOD_GSM | GSM:.PMMfaza30 | [7 empty] | 6157 | 1 | 0x02801098
GSMPMMfaza31 | REAL | IOD_GSM | GSM:.PMMfaza31 | [7 empty] | 6157 | 1 | 0x02801099
GSMPMMfaza32 | REAL | IOD_GSM | GSM:.PMMfaza32 | [7 empty] | 6157 | 1 | 0x0280109a
GSMPMMfaza33 | REAL | IOD_GSM | GSM:.PMMfaza33 | [7 empty] | 6157 | 1 | 0x0280109b
GSMPMMfaza34 | REAL | IOD_GSM | GSM:.PMMfaza34 | [7 empty] | 6157 | 1 | 0x0280109c
GSMPMMfaza35 | REAL | IOD_GSM | GSM:.PMMfaza35 | [7 empty] | 6157 | 1 | 0x0280109d
GSMPMMfaza36 | REAL | IOD_GSM | GSM:.PMMfaza36 | [7 empty] | 6157 | 1 | 0x0280109e
GSMPMMfaza37 | REAL | IOD_GSM | GSM:.PMMfaza37 | [7 empty] | 6157 | 1 | 0x0280109f
GSMPMMfaza38 | REAL | IOD_GSM | GSM:.PMMfaza38 | [7 empty] | 6157 | 1 | 0x028010a0
GSMPMMfaza39 | REAL | IOD_GSM | GSM:.PMMfaza39 | [7 empty] | 6157 | 1 | 0x028010a1
GSMPMMfaza40 | REAL | IOD_GSM | GSM:.PMMfaza40 | [7 empty] | 6157 | 1 | 0x028010a2
GSMPMMfaza41 | REAL | IOD_GSM | GSM:.PMMfaza41 | [7 empty] | 6157 | 1 | 0x028010a3
GSMPMMfaza42 | REAL | IOD_GSM | GSM:.PMMfaza42 | [7 empty] | 6157 | 1 | 0x028010a4
GSMPrevisokaTemp | DIGITAL | IOD_GSM | GSM:.PrevisokaTemp | [7 empty] | 6157 | 1 | 0x028010b0
GSMQ0_izkljuceno | DIGITAL | IOD_GSM | GSM:.Q0_izkljuceno | [7 empty] | 6157 | 1 | 0x028010c0
GSMQ0_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q0_vkljuceno | [7 empty] | 6157 | 1 | 0x028010d0
GSMQ12_izkljuceno | DIGITAL | IOD_GSM | GSM:.Q12_izkljuceno | [7 empty] | 6157 | 1 | 0x028010e0
GSMQ12_izpad | DIGITAL | IOD_GSM | GSM:.Q12_izpad | [7 empty] | 6157 | 1 | 0x028010f0
GSMQ12_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q12_vkljuceno | [7 empty] | 6157 | 1 | 0x02801100
GSMQ12stanje | BYTE | IOD_GSM | GSM:.Q12stanje | [7 empty] | 6157 | 1 | 0x02801110
GSMrazlitjeLAH1 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH1 | [7 empty] | 6157 | 1 | 0x02801120
GSMrazlitjeLAH2 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH2 | [7 empty] | 6157 | 1 | 0x02801130
GSMrazlitjeLAH3 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH3 | [7 empty] | 6157 | 1 | 0x02801140
GSMrazlitjeLAH4 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH4 | [7 empty] | 6157 | 1 | 0x02801150
GSMSetDateTime | DIGITAL | IOD_GSM | GSM:.SetDateTime | [7 empty] | 6157 | 1 | 0x02801160
GSMSetDateTimeDemand | DIGITAL | IOD_GSM | GSM:.SetDateTimeDemand | [7 empty] | 6157 | 1 | 0x02801170
GSMSetDateTimeError | DIGITAL | IOD_GSM | GSM:.SetDateTimeError | [7 empty] | 6157 | 1 | 0x02801180
GSMSetDateTimeFinished | DIGITAL | IOD_GSM | GSM:.SetDateTimeFinished | [7 empty] | 6157 | 1 | 0x02801190
GSMSkupneNapakeNaprav_PMM17VirBVirA | DIGITAL | IOD_GSM | GSM:.SkupneNapakeNaprav_PMM17VirBVirA | [7 empty] | 6157 | 1 | 0x028011a0
GSMSlabaBaterijaPLC | DIGITAL | IOD_GSM | GSM:.SlabaBaterijaPLC | [7 empty] | 6157 | 1 | 0x028011b0
GSMTempHistereza | INT | IOD_GSM | GSM:.TempHistereza | 0 | 60 | 0 | 60 | °C | ## |  | 6157 | 1 | 0x028011c8
GSMTempPovp234 | INT | IOD_GSM | GSM:.TempPovp234 | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028011c9
GSMTempPovp234Alarm | INT | IOD_GSM | GSM:.TempPovp234Alarm | 0 | 60 | 0 | 60 | °C | ## |  | 6157 | 1 | 0x028011ca
GSMTempPovp234Previs | DIGITAL | IOD_GSM | GSM:.TempPovp234Previs | [7 empty] | 6157 | 1 | 0x028011d0
GSMTempPovp56 | INT | IOD_GSM | GSM:.TempPovp56 | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028011e0
GSMTempPovp56Alarm | INT | IOD_GSM | GSM:.TempPovp56Alarm | 0 | 60 | 0 | 60 | °C | ## |  | 6157 | 1 | 0x028011e1
GSMTempPovp56Previs | DIGITAL | IOD_GSM | GSM:.TempPovp56Previs | [7 empty] | 6157 | 1 | 0x028011f0
GSMTempZaVklopKlim1 | INT | IOD_GSM | GSM:.TempZaVklopKlim1 | 0 | 60 | 0 | 60 | °C | ## |  | 6157 | 1 | 0x02801200
GSMTempZaVklopKlim2 | INT | IOD_GSM | GSM:.TempZaVklopKlim2 | 0 | 60 | 0 | 60 | °C | ## |  | 6157 | 1 | 0x02801201
GSMTIA1_alarm | INT | IOD_GSM | GSM:.TIA1_alarm | 0 | 60 | 0 | 60 | °C | ## |  | 6157 | 1 | 0x02801202
GSMTIA1_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA1_previs_temp | [7 empty] | 6157 | 1 | 0x02801210
GSMTIA1_temp_s | INT | IOD_GSM | GSM:.TIA1_temp_s | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02801221
GSMTIA2_alarm | INT | IOD_GSM | GSM:.TIA2_alarm | 0 | 60 | 0 | 60 | °C | ## |  | 6157 | 1 | 0x02801222
GSMTIA2_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA2_previs_temp | [7 empty] | 6157 | 1 | 0x02801230
GSMTIA2_temp_s | INT | IOD_GSM | GSM:.TIA2_temp_s | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02801241
GSMTIA3_alarm | INT | IOD_GSM | GSM:.TIA3_alarm | 0 | 60 | 0 | 60 | °C | ## |  | 6157 | 1 | 0x02801242
GSMTIA3_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA3_previs_temp | [7 empty] | 6157 | 1 | 0x02801250
GSMTIA3_temp_s | INT | IOD_GSM | GSM:.TIA3_temp_s | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02801261
GSMTIA4_alarm | INT | IOD_GSM | GSM:.TIA4_alarm | 0 | 60 | 0 | 60 | °C | ## |  | 6157 | 1 | 0x02801262
GSMTIA4_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA4_previs_temp | [7 empty] | 6157 | 1 | 0x02801270
GSMTIA4_temp_s | INT | IOD_GSM | GSM:.TIA4_temp_s | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x02801281
GSMTIA5_alarm | INT | IOD_GSM | GSM:.TIA5_alarm | 0 | 60 | 0 | 60 | °C | ## |  | 6157 | 1 | 0x02801282
GSMTIA5_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA5_previs_temp | [7 empty] | 6157 | 1 | 0x02801290
GSMTIA5_temp_s | INT | IOD_GSM | GSM:.TIA5_temp_s | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028012a1
GSMTIA6_alarm | INT | IOD_GSM | GSM:.TIA6_alarm | 0 | 60 | 0 | 60 | °C | ## |  | 6157 | 1 | 0x028012a2
GSMTIA6_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA6_previs_temp | [7 empty] | 6157 | 1 | 0x028012b0
GSMTIA6_temp_s | INT | IOD_GSM | GSM:.TIA6_temp_s | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028012c1
GSMTIA7_alarm | INT | IOD_GSM | GSM:.TIA7_alarm | 0 | 60 | 0 | 60 | °C | ## |  | 6157 | 1 | 0x028012c2
GSMTIA7_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA7_previs_temp | [7 empty] | 6157 | 1 | 0x028012d0
GSMTIA7_temp_s | INT | IOD_GSM | GSM:.TIA7_temp_s | 0 | 600 | 0 | 60.0 | °C | ##.# |  | 6157 | 1 | 0x028012e1
GSMUPS1Errors10 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[10] | [7 empty] | 6157 | 1 | 0x028012f0
GSMUPS1Errors11 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[11] | [7 empty] | 6157 | 1 | 0x02801300
GSMUPS1Errors12 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[12] | [7 empty] | 6157 | 1 | 0x02801310
GSMUPS1Errors13 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[13] | [7 empty] | 6157 | 1 | 0x02801320
GSMUPS1Errors14 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[14] | [7 empty] | 6157 | 1 | 0x02801330
GSMUPS1Errors15 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[15] | [7 empty] | 6157 | 1 | 0x02801340
GSMUPS1Errors16 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[16] | [7 empty] | 6157 | 1 | 0x02801350
GSMUPS1Errors17 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[17] | [7 empty] | 6157 | 1 | 0x02801360
GSMUPS1Errors18 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[18] | [7 empty] | 6157 | 1 | 0x02801370
GSMUPS1Errors19 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[19] | [7 empty] | 6157 | 1 | 0x02801380
GSMUPS1Errors1 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[1] | [7 empty] | 6157 | 1 | 0x02801390
GSMUPS1Errors20 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[20] | [7 empty] | 6157 | 1 | 0x028013a0
GSMUPS1Errors21 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[21] | [7 empty] | 6157 | 1 | 0x028013b0
GSMUPS1Errors22 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[22] | [7 empty] | 6157 | 1 | 0x028013c0
GSMUPS1Errors23 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[23] | [7 empty] | 6157 | 1 | 0x028013d0
GSMUPS1Errors24 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[24] | [7 empty] | 6157 | 1 | 0x028013e0
GSMUPS1Errors25 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[25] | [7 empty] | 6157 | 1 | 0x028013f0
GSMUPS1Errors2 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[2] | [7 empty] | 6157 | 1 | 0x02801400
GSMUPS1Errors3 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[3] | [7 empty] | 6157 | 1 | 0x02801410
GSMUPS1Errors4 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[4] | [7 empty] | 6157 | 1 | 0x02801420
GSMUPS1Errors5 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[5] | [7 empty] | 6157 | 1 | 0x02801430
GSMUPS1Errors6 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[6] | [7 empty] | 6157 | 1 | 0x02801440
GSMUPS1Errors7 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[7] | [7 empty] | 6157 | 1 | 0x02801450
GSMUPS1Errors8 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[8] | [7 empty] | 6157 | 1 | 0x02801460
GSMUPS1Errors9 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[9] | [7 empty] | 6157 | 1 | 0x02801470
GSMUPS2Errors10 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[10] | [7 empty] | 6157 | 1 | 0x02801480
GSMUPS2Errors11 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[11] | [7 empty] | 6157 | 1 | 0x02801490
GSMUPS2Errors12 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[12] | [7 empty] | 6157 | 1 | 0x028014a0
GSMUPS2Errors13 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[13] | [7 empty] | 6157 | 1 | 0x028014b0
GSMUPS2Errors14 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[14] | [7 empty] | 6157 | 1 | 0x028014c0
GSMUPS2Errors15 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[15] | [7 empty] | 6157 | 1 | 0x028014d0
GSMUPS2Errors16 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[16] | [7 empty] | 6157 | 1 | 0x028014e0
GSMUPS2Errors17 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[17] | [7 empty] | 6157 | 1 | 0x028014f0
GSMUPS2Errors18 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[18] | [7 empty] | 6157 | 1 | 0x02801500
GSMUPS2Errors19 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[19] | [7 empty] | 6157 | 1 | 0x02801510
GSMUPS2Errors1 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[1] | [7 empty] | 6157 | 1 | 0x02801520
GSMUPS2Errors20 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[20] | [7 empty] | 6157 | 1 | 0x02801530
GSMUPS2Errors21 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[21] | [7 empty] | 6157 | 1 | 0x02801540
GSMUPS2Errors22 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[22] | [7 empty] | 6157 | 1 | 0x02801550
GSMUPS2Errors23 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[23] | [7 empty] | 6157 | 1 | 0x02801560
GSMUPS2Errors24 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[24] | [7 empty] | 6157 | 1 | 0x02801570
GSMUPS2Errors25 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[25] | [7 empty] | 6157 | 1 | 0x02801580
GSMUPS2Errors2 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[2] | [7 empty] | 6157 | 1 | 0x02801590
GSMUPS2Errors3 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[3] | [7 empty] | 6157 | 1 | 0x028015a0
GSMUPS2Errors4 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[4] | [7 empty] | 6157 | 1 | 0x028015b0
GSMUPS2Errors5 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[5] | [7 empty] | 6157 | 1 | 0x028015c0
GSMUPS2Errors6 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[6] | [7 empty] | 6157 | 1 | 0x028015d0
GSMUPS2Errors7 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[7] | [7 empty] | 6157 | 1 | 0x028015e0
GSMUPS2Errors8 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[8] | [7 empty] | 6157 | 1 | 0x028015f0
GSMUPS2Errors9 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[9] | [7 empty] | 6157 | 1 | 0x02801600
GSMUPS1AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmAwaitingPower | [7 empty] | 6157 | 1 | 0x02801610
GSMUPS1AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmBypassBad | [7 empty] | 6157 | 1 | 0x02801620
GSMUPS1AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmChargerFailed | [7 empty] | 6157 | 1 | 0x02801630
GSMUPS1AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmCommunicationsLost | [7 empty] | 6157 | 1 | 0x02801640
GSMUPS1AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmDepletedBattery | [7 empty] | 6157 | 1 | 0x02801650
GSMUPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmDiagnosticTestFailed | [7 empty] | 6157 | 1 | 0x02801660
GSMUPS1AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmInverterError | [7 empty] | 6157 | 1 | 0x02801670
GSMUPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmIzhodOffKotZahtevano | [7 empty] | 6157 | 1 | 0x02801680
GSMUPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmIzhodPreobremenjen | [7 empty] | 6157 | 1 | 0x02801690
GSMUPS1AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmLowBattery | [7 empty] | 6157 | 1 | 0x028016a0
GSMUPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmNapakaNaVarovalki | [7 empty] | 6157 | 1 | 0x028016b0
GSMUPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmNapakaNaVentilatorju | [7 empty] | 6157 | 1 | 0x028016c0
GSMUPS1AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmOnBattery | [7 empty] | 6157 | 1 | 0x028016d0
GSMUPS1AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmOnBypass | [7 empty] | 6157 | 1 | 0x028016e0
GSMUPS1AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmShutdownImminent | [7 empty] | 6157 | 1 | 0x028016f0
GSMUPS1AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmShutdownPending | [7 empty] | 6157 | 1 | 0x02801700
GSMUPS1AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmSlabaBaterija | [7 empty] | 6157 | 1 | 0x02801710
GSMUPS1AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmSplosnaNapaka | [7 empty] | 6157 | 1 | 0x02801720
GSMUPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmStanjeIzhodaIzvenToleranc | [7 empty] | 6157 | 1 | 0x02801730
GSMUPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmStanjeVhodaIzvenToleranc | [7 empty] | 6157 | 1 | 0x02801740
GSMUPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmTemperaturaIzvenToleranc | [7 empty] | 6157 | 1 | 0x02801750
GSMUPS1AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmTestInProgres | [7 empty] | 6157 | 1 | 0x02801760
GSMUPS1AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSIzhodOff | [7 empty] | 6157 | 1 | 0x02801770
GSMUPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSOffKotZahtevano | [7 empty] | 6157 | 1 | 0x02801780
GSMUPS1AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSSystemOff | [7 empty] | 6157 | 1 | 0x02801790
GSMUPS1EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[1].EstimatedChargeRemaining | 0 | 100 | 0 | 100 | % | ### |  | 6157 | 1 | 0x028017a0
GSMUPS1EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[1].EstimatedMinutesRemaining | 0 | 500 | 0 | 500 | min | ### |  | 6157 | 1 | 0x028017a1
GSMUPS1InverterStatus | INT | IOD_GSM | GSM:.UPS[1].InverterStatus | [7 empty] | 6157 | 1 | 0x028017a2
GSMUPS1IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL1 | 0 | 100 | 0 | 100 | % | ##.# |  | 6157 | 1 | 0x028017a3
GSMUPS1IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL2 | 0 | 100 | 0 | 100 | % | ##.# |  | 6157 | 1 | 0x028017a4
GSMUPS1IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL3 | 0 | 100 | 0 | 100 | % | ##.# |  | 6157 | 1 | 0x028017a5
GSMUPS1Napaka | DIGITAL | IOD_GSM | GSM:.UPS[1].Napaka | [7 empty] | 6157 | 1 | 0x028017b0
GSMUPS1NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[1].NapetostBaterije | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x028017c0
GSMUPS1OutputStatus | INT | IOD_GSM | GSM:.UPS[1].OutputStatus | [7 empty] | 6157 | 1 | 0x028017c1
GSMUPS1StatusBaterije | UINT | IOD_GSM | GSM:.UPS[1].StatusBaterije | [5 empty] | ## |  | 6157 | 1 | 0x028017c2
GSMUPS1StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusEcomodeAktiven | [7 empty] | 6157 | 1 | 0x028017d0
GSMUPS1StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusInverterIsOn | [7 empty] | 6157 | 1 | 0x028017e0
GSMUPS1StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusStopOperation | [7 empty] | 6157 | 1 | 0x028017f0
GSMUPS1SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[1].SteviloIzpadovVhodneLinije | [5 empty] | ##### |  | 6157 | 1 | 0x02801800
GSMUPS1TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[1].TemperaturaBaterije | 0 | 100 | 0 | 100 | °C | ### |  | 6157 | 1 | 0x02801801
GSMUPS1UnitStatus | INT | IOD_GSM | GSM:.UPS[1].UnitStatus | [7 empty] | 6157 | 1 | 0x02801802
GSMUPS1VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL1 | 0 | 60.0 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x02801803
GSMUPS1VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL2 | 0 | 60.0 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x02801804
GSMUPS1VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL3 | 0 | 60.0 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x02801805
GSMUPS1VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL1 | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x02801806
GSMUPS1VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL2 | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x02801807
GSMUPS1VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL3 | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x02801808
GSMUPS2AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmAwaitingPower | [7 empty] | 6157 | 1 | 0x02801810
GSMUPS2AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmBypassBad | [7 empty] | 6157 | 1 | 0x02801820
GSMUPS2AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmChargerFailed | [7 empty] | 6157 | 1 | 0x02801830
GSMUPS2AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmCommunicationsLost | [7 empty] | 6157 | 1 | 0x02801840
GSMUPS2AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmDepletedBattery | [7 empty] | 6157 | 1 | 0x02801850
GSMUPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmDiagnosticTestFailed | [7 empty] | 6157 | 1 | 0x02801860
GSMUPS2AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmInverterError | [7 empty] | 6157 | 1 | 0x02801870
GSMUPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmIzhodOffKotZahtevano | [7 empty] | 6157 | 1 | 0x02801880
GSMUPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmIzhodPreobremenjen | [7 empty] | 6157 | 1 | 0x02801890
GSMUPS2AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmLowBattery | [7 empty] | 6157 | 1 | 0x028018a0
GSMUPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmNapakaNaVarovalki | [7 empty] | 6157 | 1 | 0x028018b0
GSMUPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmNapakaNaVentilatorju | [7 empty] | 6157 | 1 | 0x028018c0
GSMUPS2AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmOnBattery | [7 empty] | 6157 | 1 | 0x028018d0
GSMUPS2AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmOnBypass | [7 empty] | 6157 | 1 | 0x028018e0
GSMUPS2AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmShutdownImminent | [7 empty] | 6157 | 1 | 0x028018f0
GSMUPS2AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmShutdownPending | [7 empty] | 6157 | 1 | 0x02801900
GSMUPS2AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmSlabaBaterija | [7 empty] | 6157 | 1 | 0x02801910
GSMUPS2AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmSplosnaNapaka | [7 empty] | 6157 | 1 | 0x02801920
GSMUPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmStanjeIzhodaIzvenToleranc | [7 empty] | 6157 | 1 | 0x02801930
GSMUPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmStanjeVhodaIzvenToleranc | [7 empty] | 6157 | 1 | 0x02801940
GSMUPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmTemperaturaIzvenToleranc | [7 empty] | 6157 | 1 | 0x02801950
GSMUPS2AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmTestInProgres | [7 empty] | 6157 | 1 | 0x02801960
GSMUPS2AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSIzhodOff | [7 empty] | 6157 | 1 | 0x02801970
GSMUPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSOffKotZahtevano | [7 empty] | 6157 | 1 | 0x02801980
GSMUPS2AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSSystemOff | [7 empty] | 6157 | 1 | 0x02801990
GSMUPS2EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[2].EstimatedChargeRemaining | 0 | 100 | 0 | 100 | % | ### |  | 6157 | 1 | 0x028019a0
GSMUPS2EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[2].EstimatedMinutesRemaining | 0 | 500 | 0 | 500 | min | ### |  | 6157 | 1 | 0x028019a1
GSMUPS2InverterStatus | INT | IOD_GSM | GSM:.UPS[2].InverterStatus | [7 empty] | 6157 | 1 | 0x028019a2
GSMUPS2IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL1 | 0 | 100 | 0 | 100 | % | ##.# |  | 6157 | 1 | 0x028019a3
GSMUPS2IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL2 | 0 | 100 | 0 | 100 | % | ##.# |  | 6157 | 1 | 0x028019a4
GSMUPS2IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL3 | 0 | 100 | 0 | 100 | % | ##.# |  | 6157 | 1 | 0x028019a5
GSMUPS2Napaka | DIGITAL | IOD_GSM | GSM:.UPS[2].Napaka | [7 empty] | 6157 | 1 | 0x028019b0
GSMUPS2NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[2].NapetostBaterije | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x028019c0
GSMUPS2OutputStatus | INT | IOD_GSM | GSM:.UPS[2].OutputStatus | [7 empty] | 6157 | 1 | 0x028019c1
GSMUPS2StatusBaterije | UINT | IOD_GSM | GSM:.UPS[2].StatusBaterije | [5 empty] | ## |  | 6157 | 1 | 0x028019c2
GSMUPS2StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusEcomodeAktiven | [7 empty] | 6157 | 1 | 0x028019d0
GSMUPS2StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusInverterIsOn | [7 empty] | 6157 | 1 | 0x028019e0
GSMUPS2StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusStopOperation | [7 empty] | 6157 | 1 | 0x028019f0
GSMUPS2SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[2].SteviloIzpadovVhodneLinije | [5 empty] | ##### |  | 6157 | 1 | 0x02801a00
GSMUPS2TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[2].TemperaturaBaterije | 0 | 100 | 0 | 100 | °C | ### |  | 6157 | 1 | 0x02801a01
GSMUPS2UnitStatus | INT | IOD_GSM | GSM:.UPS[2].UnitStatus | [7 empty] | 6157 | 1 | 0x02801a02
GSMUPS2VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL1 | 0 | 60.0 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x02801a03
GSMUPS2VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL2 | 0 | 60.0 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x02801a04
GSMUPS2VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL3 | 0 | 60.0 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x02801a05
GSMUPS2VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL1 | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x02801a06
GSMUPS2VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL2 | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x02801a07
GSMUPS2VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL3 | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x02801a08
GSMUPS_A_V23_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_A_V23_delovanje | [7 empty] | 6157 | 1 | 0x02801a10
GSMUPS_A_V23_napaka | DIGITAL | IOD_GSM | GSM:.UPS_A_V23_napaka | [7 empty] | 6157 | 1 | 0x02801a20
GSMups_alarm | DIGITAL | IOD_GSM | GSM:.ups_alarm | [7 empty] | 6157 | 1 | 0x02801a30
GSMups_baterijski_nac | DIGITAL | IOD_GSM | GSM:.ups_baterijski_nac | [7 empty] | 6157 | 1 | 0x02801a40
GSMUPS_MGE1BatteryBackupTime | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryBackupTime | 0 | 500 | 0 | 500 | min | ### |  | 6157 | 1 | 0x02801a50
GSMUPS_MGE1BatteryChargedState | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryChargedState | [7 empty] | 6157 | 1 | 0x02801a60
GSMUPS_MGE1BatteryChargingLevel | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryChargingLevel | 0 | 100 | 0 | 100 | % | ##.# |  | 6157 | 1 | 0x02801a70
GSMUPS_MGE1BatteryCircuitBreaker | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryCircuitBreaker | [7 empty] | 6157 | 1 | 0x02801a80
GSMUPS_MGE1BatteryCompInProgress | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryCompInProgress | [7 empty] | 6157 | 1 | 0x02801a90
GSMUPS_MGE1BatteryFuseFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryFuseFault | [7 empty] | 6157 | 1 | 0x02801aa0
GSMUPS_MGE1BatteryLowWarning | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryLowWarning | [7 empty] | 6157 | 1 | 0x02801ab0
GSMUPS_MGE1BatteryRechargeDuration | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryRechargeDuration | [7 empty] | 6157 | 1 | 0x02801ac0
GSMUPS_MGE1BatteryTempOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryTempOutOfToler | [7 empty] | 6157 | 1 | 0x02801ad0
GSMUPS_MGE1BypassInFreeFrequency | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BypassInFreeFrequency | [7 empty] | 6157 | 1 | 0x02801ae0
GSMUPS_MGE1ChargerGeneralFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].ChargerGeneralFault | [7 empty] | 6157 | 1 | 0x02801af0
GSMUPS_MGE1DeviceVentilationFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].DeviceVentilationFault | [7 empty] | 6157 | 1 | 0x02801b00
GSMUPS_MGE1I1output | INT | IOD_GSM | GSM:.UPS_MGE[1].I1output | 0 | 100 | 0 | 100 | A | ####.# |  | 6157 | 1 | 0x02801b10
GSMUPS_MGE1I2output | INT | IOD_GSM | GSM:.UPS_MGE[1].I2output | 0 | 100 | 0 | 100 | A | ####.# |  | 6157 | 1 | 0x02801b11
GSMUPS_MGE1I3output | INT | IOD_GSM | GSM:.UPS_MGE[1].I3output | 0 | 100 | 0 | 100 | A | ####.# |  | 6157 | 1 | 0x02801b12
GSMUPS_MGE1InverterFrequency | INT | IOD_GSM | GSM:.UPS_MGE[1].InverterFrequency | [7 empty] | 6157 | 1 | 0x02801b13
GSMUPS_MGE1InverterFuseFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterFuseFault | [7 empty] | 6157 | 1 | 0x02801b20
GSMUPS_MGE1InverterOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterOverload | [7 empty] | 6157 | 1 | 0x02801b30
GSMUPS_MGE1InverterThermalOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterThermalOverload | [7 empty] | 6157 | 1 | 0x02801b40
GSMUPS_MGE1Mains1VoltOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains1VoltOutOfToler | [7 empty] | 6157 | 1 | 0x02801b50
GSMUPS_MGE1Mains2Overload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains2Overload | [7 empty] | 6157 | 1 | 0x02801b60
GSMUPS_MGE1Mains2VoltOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains2VoltOutOfToler | [7 empty] | 6157 | 1 | 0x02801b70
GSMUPS_MGE1MaintenancePosition | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].MaintenancePosition | [7 empty] | 6157 | 1 | 0x02801b80
GSMUPS_MGE1ManualBypassSwitch | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].ManualBypassSwitch | [7 empty] | 6157 | 1 | 0x02801b90
GSMUPS_MGE1NapakaNaVarovalkah | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].NapakaNaVarovalkah | [7 empty] | 6157 | 1 | 0x02801ba0
GSMUPS_MGE1OutputActivePower1 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower1 | 0 | 100 | 0 | 100 | % | ##.# |  | 6157 | 1 | 0x02801bb0
GSMUPS_MGE1OutputActivePower2 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower2 | 0 | 100 | 0 | 100 | % | ##.# |  | 6157 | 1 | 0x02801bb1
GSMUPS_MGE1OutputActivePower3 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower3 | 0 | 100 | 0 | 100 | % | ##.# |  | 6157 | 1 | 0x02801bb2
GSMUPS_MGE1OutputFrequency | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputFrequency | 0 | 60.0 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x02801bb3
GSMUPS_MGE1OutputInShortCircuit | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputInShortCircuit | [7 empty] | 6157 | 1 | 0x02801bc0
GSMUPS_MGE1OutputLoadLevel | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputLoadLevel | [7 empty] | 6157 | 1 | 0x02801bd0
GSMUPS_MGE1OutputOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputOverload | [7 empty] | 6157 | 1 | 0x02801be0
GSMUPS_MGE1OutputThermalOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputThermalOverload | [7 empty] | 6157 | 1 | 0x02801bf0
GSMUPS_MGE1RectifierOn | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].RectifierOn | [7 empty] | 6157 | 1 | 0x02801c00
GSMUPS_MGE1RectifierThermOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].RectifierThermOverload | [7 empty] | 6157 | 1 | 0x02801c10
GSMUPS_MGE1Skupna_napaka | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Skupna_napaka | [7 empty] | 6157 | 1 | 0x02801c20
GSMUPS_MGE1StatusBaterije | BYTE | IOD_GSM | GSM:.UPS_MGE[1].StatusBaterije | [7 empty] | 6157 | 1 | 0x02801c30
GSMUPS_MGE1U12mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U12mains1 | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x02801c31
GSMUPS_MGE1U12mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U12mains2 | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x02801c32
GSMUPS_MGE1U1N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U1N_inverter | [7 empty] | 6157 | 1 | 0x02801c33
GSMUPS_MGE1U1N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U1N_output | 0 | 270 | 0 | 270 | V | ####.# |  | 6157 | 1 | 0x02801c34
GSMUPS_MGE1U23mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U23mains1 | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x02801c35
GSMUPS_MGE1U23mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U23mains2 | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x02801c36
GSMUPS_MGE1U2N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U2N_inverter | [7 empty] | 6157 | 1 | 0x02801c37
GSMUPS_MGE1U2N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U2N_output | 0 | 270 | 0 | 270 | V | ####.# |  | 6157 | 1 | 0x02801c38
GSMUPS_MGE1U31mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U31mains1 | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x02801c39
GSMUPS_MGE1U31mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U31mains2 | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x02801c3a
GSMUPS_MGE1U3N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U3N_inverter | [7 empty] | 6157 | 1 | 0x02801c3b
GSMUPS_MGE1U3N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U3N_output | 0 | 270 | 0 | 270 | V | ####.# |  | 6157 | 1 | 0x02801c3c
GSMUPS_MGE1U_battery | INT | IOD_GSM | GSM:.UPS_MGE[1].U_battery | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x02801c3d
GSMUPS_MGE1UPS_coupled | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_coupled | [7 empty] | 6157 | 1 | 0x02801c40
GSMUPS_MGE1UPS_error | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_error | [7 empty] | 6157 | 1 | 0x02801c50
GSMUPS_MGE1UPS_in_backup | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_in_backup | [7 empty] | 6157 | 1 | 0x02801c60
GSMups_polnjenje | DIGITAL | IOD_GSM | GSM:.ups_polnjenje | [7 empty] | 6157 | 1 | 0x02801c70
GSMUPS_V23_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_V23_delovanje | [7 empty] | 6157 | 1 | 0x02801c80
GSMUPS_V23_napaka | DIGITAL | IOD_GSM | GSM:.UPS_V23_napaka | [7 empty] | 6157 | 1 | 0x02801c90
GSMUPS_V25_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_V25_delovanje | [7 empty] | 6157 | 1 | 0x02801ca0
GSMUPS_V25_napaka | DIGITAL | IOD_GSM | GSM:.UPS_V25_napaka | [7 empty] | 6157 | 1 | 0x02801cb0
GSMUPSMGEErrors10 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[10] | [7 empty] | 6157 | 1 | 0x02801cc0
GSMUPSMGEErrors11 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[11] | [7 empty] | 6157 | 1 | 0x02801cd0
GSMUPSMGEErrors12 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[12] | [7 empty] | 6157 | 1 | 0x02801ce0
GSMUPSMGEErrors13 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[13] | [7 empty] | 6157 | 1 | 0x02801cf0
GSMUPSMGEErrors14 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[14] | [7 empty] | 6157 | 1 | 0x02801d00
GSMUPSMGEErrors15 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[15] | [7 empty] | 6157 | 1 | 0x02801d10
GSMUPSMGEErrors16 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[16] | [7 empty] | 6157 | 1 | 0x02801d20
GSMUPSMGEErrors17 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[17] | [7 empty] | 6157 | 1 | 0x02801d30
GSMUPSMGEErrors1 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[1] | [7 empty] | 6157 | 1 | 0x02801d40
GSMUPSMGEErrors2 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[2] | [7 empty] | 6157 | 1 | 0x02801d50
GSMUPSMGEErrors3 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[3] | [7 empty] | 6157 | 1 | 0x02801d60
GSMUPSMGEErrors4 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[4] | [7 empty] | 6157 | 1 | 0x02801d70
GSMUPSMGEErrors5 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[5] | [7 empty] | 6157 | 1 | 0x02801d80
GSMUPSMGEErrors6 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[6] | [7 empty] | 6157 | 1 | 0x02801d90
GSMUPSMGEErrors7 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[7] | [7 empty] | 6157 | 1 | 0x02801da0
GSMUPSMGEErrors8 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[8] | [7 empty] | 6157 | 1 | 0x02801db0
GSMUPSMGEErrors9 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[9] | [7 empty] | 6157 | 1 | 0x02801dc0
GSMUserCurrentLevel | BYTE | IOD_GSM | GSM:.UserCurrentLevel | [7 empty] | 6157 | 1 | 0x02801dd0
GSMUserCurrentName | STRING | IOD_GSM | GSM:.UserCurrentName | [7 empty] | 6157 | 1 | 0x02801dd1
GSMUserLoggedIn | DIGITAL | IOD_GSM | GSM:.UserLoggedIn | [7 empty] | 6157 | 1 | 0x02801de0
GSMVLAZILEC1_delovanje | DIGITAL | IOD_GSM | GSM:.VLAZILEC1_delovanje | [7 empty] | 6157 | 1 | 0x02801df0
GSMVLAZILEC1_napaka | DIGITAL | IOD_GSM | GSM:.VLAZILEC1_napaka | [7 empty] | 6157 | 1 | 0x02801e00
GSMVLAZILEC2_delovanje | DIGITAL | IOD_GSM | GSM:.VLAZILEC2_delovanje | [7 empty] | 6157 | 1 | 0x02801e10
GSMVLAZILEC2_napaka | DIGITAL | IOD_GSM | GSM:.VLAZILEC2_napaka | [7 empty] | 6157 | 1 | 0x02801e20
GSMXVH_AlarmOn | DIGITAL | IOD_GSM | GSM:.XVH_AlarmOn | [7 empty] | 6157 | 1 | 0x02801e30
GSMXVH_enopolna_napaka | DIGITAL | IOD_GSM | GSM:.XVH_enopolna_napaka | [7 empty] | 6157 | 1 | 0x02801e40
GSMXVH_UPSstatus | BYTE | IOD_GSM | GSM:.XVH_UPSstatus | [7 empty] | 6157 | 1 | 0x02801e50
GSMXVHdepltedBatery1 | REAL | IOD_GSM | GSM:.XVHdepltedBatery1 | [7 empty] | 6157 | 1 | 0x02801e51
GSMXVHdepltedBatery2 | REAL | IOD_GSM | GSM:.XVHdepltedBatery2 | [7 empty] | 6157 | 1 | 0x02801e52
GSMXVHlowBatery1 | REAL | IOD_GSM | GSM:.XVHlowBatery1 | [7 empty] | 6157 | 1 | 0x02801e53
GSMXVHlowBatery2 | REAL | IOD_GSM | GSM:.XVHlowBatery2 | [7 empty] | 6157 | 1 | 0x02801e54
GSMPMM_2x17_VirA_zavihek | DIGITAL | IOD_GSM_disk | D288 | [7 empty] | 6157 | 0 | 0x02801e60
GSMPMM_2x17_VirB_zavihek | DIGITAL | IOD_GSM_disk | D289 | [7 empty] | 6157 | 0 | 0x02801e70
GSMServer_B_Izpad | DIGITAL | IOD_GSM_mem | D566 | [9 empty] | 0x02801e80
GSMServer_A_Izpad | DIGITAL | IOD_GSM_mem | D567 | [9 empty] | 0x02801e90
GSM_meja_tok_opozoriloL1 | INT | IOD_GSM_disk | I300 | [9 empty] | 0x02801ea0
GSM_meja_tok_opozoriloL2 | INT | IOD_GSM_disk | I302 | [9 empty] | 0x02801ea1
GSM_meja_tok_opozoriloL3 | INT | IOD_GSM_disk | I304 | [9 empty] | 0x02801ea2
GSM_meja_tok_alarmL1 | INT | IOD_GSM_disk | I306 | [9 empty] | 0x02801ea3
GSM_meja_tok_alarmL2 | INT | IOD_GSM_disk | I308 | [9 empty] | 0x02801ea4
GSM_meja_tok_alarmL3 | INT | IOD_GSM_disk | I310 | [9 empty] | 0x02801ea5
GSM_omogocanje_tok_opozorilaL1 | DIGITAL | IOD_GSM_disk | D312 | [9 empty] | 0x02801eb0
GSM_omogocanje_tok_opozorilaL2 | DIGITAL | IOD_GSM_disk | D313 | [9 empty] | 0x02801ec0
GSM_omogocanje_tok_opozorilaL3 | DIGITAL | IOD_GSM_disk | D314 | [9 empty] | 0x02801ed0
GSM_omogocanje_tok_alarmL1 | DIGITAL | IOD_GSM_disk | D315 | [9 empty] | 0x02801ee0
GSM_omogocanje_tok_alarmL2 | DIGITAL | IOD_GSM_disk | D316 | [9 empty] | 0x02801ef0
GSM_omogocanje_tok_alarmL3 | DIGITAL | IOD_GSM_disk | D317 | [9 empty] | 0x02801f00
GSMErrComCirc1_om | DIGITAL | IOD_GSM_disk | D318 | [9 empty] | 0x02801f10
GSMErrComKlima1_om | DIGITAL | IOD_GSM_disk | D319 | [9 empty] | 0x02801f20
GSMErrComKlima2_om | DIGITAL | IOD_GSM_disk | D320 | [9 empty] | 0x02801f30
GSMErrComPMM1_om | DIGITAL | IOD_GSM_disk | D321 | [9 empty] | 0x02801f40
GSMErrComPort2_om | DIGITAL | IOD_GSM_disk | D322 | [9 empty] | 0x02801f50
GSMErrComPort3_om | DIGITAL | IOD_GSM_disk | D323 | [9 empty] | 0x02801f60
GSMErrComPort4_om | DIGITAL | IOD_GSM_disk | D324 | [9 empty] | 0x02801f70
GSMErrComUPS1_om | DIGITAL | IOD_GSM_disk | D325 | [9 empty] | 0x02801f80
GSMErrComUPS2_om | DIGITAL | IOD_GSM_disk | D326 | [9 empty] | 0x02801f90
GSMErrComUPSMGE1_om | DIGITAL | IOD_GSM_disk | D327 | [9 empty] | 0x02801fa0
GSMrazlitjeLAH1_om | DIGITAL | IOD_GSM_disk | D328 | [9 empty] | 0x02801fb0
GSMrazlitjeLAH2_om | DIGITAL | IOD_GSM_disk | D329 | [9 empty] | 0x02801fc0
GSMrazlitjeLAH3_om | DIGITAL | IOD_GSM_disk | D330 | [9 empty] | 0x02801fd0
GSMrazlitjeLAH4_om | DIGITAL | IOD_GSM_disk | D331 | [9 empty] | 0x02801fe0
GSMServer_A_Izpad_om | DIGITAL | IOD_GSM_disk | D332 | [9 empty] | 0x02801ff0
GSMServer_B_Izpad_om | DIGITAL | IOD_GSM_disk | D333 | [9 empty] | 0x02802000
GSMnapaka_kom_panel_om | DIGITAL | IOD_GSM_disk | D334 | [9 empty] | 0x02802010
GSMSetDateTimeError_om | DIGITAL | IOD_GSM_disk | D335 | [9 empty] | 0x02802020
GSMSlabaBaterijaPLC_om | DIGITAL | IOD_GSM_disk | D336 | [9 empty] | 0x02802030
GSMups_baterijski_nac_om | DIGITAL | IOD_GSM_disk | D337 | [9 empty] | 0x02802040
GSMups_alarm_om | DIGITAL | IOD_GSM_disk | D338 | [9 empty] | 0x02802050
GSMups_polnjenje_om | DIGITAL | IOD_GSM_disk | D339 | [9 empty] | 0x02802060
GSMQ0_izkljuceno_om | DIGITAL | IOD_GSM_disk | D340 | [9 empty] | 0x02802070
GSMQ0_vkljuceno_om | DIGITAL | IOD_GSM_disk | D341 | [9 empty] | 0x02802080
GSMQ12_izkljuceno_om | DIGITAL | IOD_GSM_disk | D342 | [9 empty] | 0x02802090
GSMQ12_izpad_om | DIGITAL | IOD_GSM_disk | D343 | [9 empty] | 0x028020a0
GSMQ12_vkljuceno_om | DIGITAL | IOD_GSM_disk | D344 | [9 empty] | 0x028020b0
GSMN_F1_1_zascita_ok_om | DIGITAL | IOD_GSM_disk | D345 | [9 empty] | 0x028020c0
GSMK1_SkupnaNapaka_om | DIGITAL | IOD_GSM_disk | D346 | [9 empty] | 0x028020d0
GSMK1AlarmPozara_om | DIGITAL | IOD_GSM_disk | D347 | [9 empty] | 0x028020e0
GSMK1KlimaZdruzenAlarm_om | DIGITAL | IOD_GSM_disk | D348 | [9 empty] | 0x028020f0
GSMK1NiPretoka_om | DIGITAL | IOD_GSM_disk | D349 | [9 empty] | 0x02802100
GSMK1OkvaraRototerma_om | DIGITAL | IOD_GSM_disk | D350 | [9 empty] | 0x02802110
GSMK1OkvaraVlazNap_om | DIGITAL | IOD_GSM_disk | D351 | [9 empty] | 0x02802120
GSMK1PreobMotCrpGr_om | DIGITAL | IOD_GSM_disk | D352 | [9 empty] | 0x02802130
GSMK1PreobMotVent_om | DIGITAL | IOD_GSM_disk | D353 | [9 empty] | 0x02802140
GSMK1ProtizamrzZascAkt_om | DIGITAL | IOD_GSM_disk | D354 | [9 empty] | 0x02802150
GSMK1ZamasenostFiltra_om | DIGITAL | IOD_GSM_disk | D355 | [9 empty] | 0x02802160
GSMKLIMAT1_delovanje_om | DIGITAL | IOD_GSM_disk | D356 | [9 empty] | 0x02802170
GSMKLIMAT1_vklop_delovanja_om | DIGITAL | IOD_GSM_disk | D357 | [9 empty] | 0x02802180
GSMN_KLIMAT1_napaka_om | DIGITAL | IOD_GSM_disk | D358 | [9 empty] | 0x02802190
GSMKlimeAVTO_om | DIGITAL | IOD_GSM_disk | D359 | [9 empty] | 0x028021a0
GSMKlima1_izkljucena_om | DIGITAL | IOD_GSM_disk | D360 | [9 empty] | 0x028021b0
GSMN_VLAZILEC1_napaka_om | DIGITAL | IOD_GSM_disk | D361 | [9 empty] | 0x028021c0
GSMK2_SkupnaNapaka_om | DIGITAL | IOD_GSM_disk | D362 | [9 empty] | 0x028021d0
GSMK2AlarmPozara_om | DIGITAL | IOD_GSM_disk | D363 | [9 empty] | 0x028021e0
GSMK2KlimaZdruzenAlarm_om | DIGITAL | IOD_GSM_disk | D364 | [9 empty] | 0x028021f0
GSMK2NiPretoka_om | DIGITAL | IOD_GSM_disk | D365 | [9 empty] | 0x02802200
GSMK2OkvaraRototerma_om | DIGITAL | IOD_GSM_disk | D366 | [9 empty] | 0x02802210
GSMK2OkvaraVlazNap_om | DIGITAL | IOD_GSM_disk | D367 | [9 empty] | 0x02802220
GSMK2PreobMotCrpGr_om | DIGITAL | IOD_GSM_disk | D368 | [9 empty] | 0x02802230
GSMK2PreobMotVent_om | DIGITAL | IOD_GSM_disk | D369 | [9 empty] | 0x02802240
GSMK2ProtizamrzZascAkt_om | DIGITAL | IOD_GSM_disk | D370 | [9 empty] | 0x02802250
GSMK2ZamasenostFiltra_om | DIGITAL | IOD_GSM_disk | D371 | [9 empty] | 0x02802260
GSMKLIMAT2_delovanje_om | DIGITAL | IOD_GSM_disk | D372 | [9 empty] | 0x02802270
GSMKLIMAT2_vklop_delovanja_om | DIGITAL | IOD_GSM_disk | D373 | [9 empty] | 0x02802280
GSMN_KLIMAT2_napaka_om | DIGITAL | IOD_GSM_disk | D374 | [9 empty] | 0x02802290
GSMKlima2_izkljucena_om | DIGITAL | IOD_GSM_disk | D375 | [9 empty] | 0x028022a0
GSMN_VLAZILEC2_napaka_om | DIGITAL | IOD_GSM_disk | D376 | [9 empty] | 0x028022b0
GSMKLIMA_m1_napaka_om | DIGITAL | IOD_GSM_disk | D377 | [9 empty] | 0x028022c0
GSMKLIMA_m2_napaka_om | DIGITAL | IOD_GSM_disk | D378 | [9 empty] | 0x028022d0
GSMKlima3_izkljucena_om | DIGITAL | IOD_GSM_disk | D379 | [9 empty] | 0x028022e0
GSMN_KLIMA1_krm_nap_ok_om | DIGITAL | IOD_GSM_disk | D380 | [9 empty] | 0x028022f0
GSMKLIMA1_kke_pogon_om | DIGITAL | IOD_GSM_disk | D381 | [9 empty] | 0x02802300
GSMKLIMA_m1_delovanje_om | DIGITAL | IOD_GSM_disk | D382 | [9 empty] | 0x02802310
GSMKLIMA_m2_delovanje_om | DIGITAL | IOD_GSM_disk | D383 | [9 empty] | 0x02802320
GSMK3_deluje_om | DIGITAL | IOD_GSM_disk | D384 | [9 empty] | 0x02802330
GSMK3_SkupnaNapaka_om | DIGITAL | IOD_GSM_disk | D385 | [9 empty] | 0x02802340
GSMN_UPS_V23_delovanje_om | DIGITAL | IOD_GSM_disk | D386 | [9 empty] | 0x02802350
GSMN_UPS_V23_napaka_om | DIGITAL | IOD_GSM_disk | D387 | [9 empty] | 0x02802360
GSMUPS1AlarmSlabaBaterija_om | DIGITAL | IOD_GSM_disk | D388 | [9 empty] | 0x02802370
GSMUPS1AlarmOnBattery_om | DIGITAL | IOD_GSM_disk | D389 | [9 empty] | 0x02802380
GSMUPS1AlarmLowBattery_om | DIGITAL | IOD_GSM_disk | D390 | [9 empty] | 0x02802390
GSMUPS1AlarmDepletedBattery_om | DIGITAL | IOD_GSM_disk | D391 | [9 empty] | 0x028023a0
GSMUPS1AlarmTemperaturaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D392 | [9 empty] | 0x028023b0
GSMUPS1AlarmStanjeVhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D393 | [9 empty] | 0x028023c0
GSMUPS1AlarmStanjeIzhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D394 | [9 empty] | 0x028023d0
GSMUPS1AlarmIzhodPreobremenjen_om | DIGITAL | IOD_GSM_disk | D395 | [9 empty] | 0x028023e0
GSMUPS1AlarmOnBypass_om | DIGITAL | IOD_GSM_disk | D396 | [9 empty] | 0x028023f0
GSMUPS1AlarmBypassBad_om | DIGITAL | IOD_GSM_disk | D397 | [9 empty] | 0x02802400
GSMUPS1AlarmIzhodOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D398 | [9 empty] | 0x02802410
GSMUPS1AlarmUPSOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D399 | [9 empty] | 0x02802420
GSMUPS1AlarmChargerFailed_om | DIGITAL | IOD_GSM_disk | D400 | [9 empty] | 0x02802430
GSMUPS1AlarmUPSIzhodOff_om | DIGITAL | IOD_GSM_disk | D401 | [9 empty] | 0x02802440
GSMUPS1AlarmUPSSystemOff_om | DIGITAL | IOD_GSM_disk | D402 | [9 empty] | 0x02802450
GSMUPS1AlarmNapakaNaVentilatorju_om | DIGITAL | IOD_GSM_disk | D403 | [9 empty] | 0x02802460
GSMUPS1AlarmNapakaNaVarovalki_om | DIGITAL | IOD_GSM_disk | D404 | [9 empty] | 0x02802470
GSMUPS1AlarmSplosnaNapaka_om | DIGITAL | IOD_GSM_disk | D405 | [9 empty] | 0x02802480
GSMUPS1AlarmDiagnosticTestFailed_om | DIGITAL | IOD_GSM_disk | D406 | [9 empty] | 0x02802490
GSMUPS1AlarmCommunicationsLost_om | DIGITAL | IOD_GSM_disk | D407 | [9 empty] | 0x028024a0
GSMUPS1AlarmAwaitingPower_om | DIGITAL | IOD_GSM_disk | D408 | [9 empty] | 0x028024b0
GSMUPS1AlarmShutdownPending_om | DIGITAL | IOD_GSM_disk | D409 | [9 empty] | 0x028024c0
GSMUPS1AlarmShutdownImminent_om | DIGITAL | IOD_GSM_disk | D410 | [9 empty] | 0x028024d0
GSMUPS1AlarmTestInProgres_om | DIGITAL | IOD_GSM_disk | D411 | [9 empty] | 0x028024e0
GSMUPS1AlarmInverterError_om | DIGITAL | IOD_GSM_disk | D412 | [9 empty] | 0x028024f0
GSMN_UPS_V25_delovanje_om | DIGITAL | IOD_GSM_disk | D413 | [9 empty] | 0x02802500
GSMN_UPS_V25_napaka_om | DIGITAL | IOD_GSM_disk | D414 | [9 empty] | 0x02802510
GSMUPS2AlarmSlabaBaterija_om | DIGITAL | IOD_GSM_disk | D415 | [9 empty] | 0x02802520
GSMUPS2AlarmOnBattery_om | DIGITAL | IOD_GSM_disk | D416 | [9 empty] | 0x02802530
GSMUPS2AlarmLowBattery_om | DIGITAL | IOD_GSM_disk | D417 | [9 empty] | 0x02802540
GSMUPS2AlarmDepletedBattery_om | DIGITAL | IOD_GSM_disk | D418 | [9 empty] | 0x02802550
GSMUPS2AlarmTemperaturaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D419 | [9 empty] | 0x02802560
GSMUPS2AlarmStanjeVhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D420 | [9 empty] | 0x02802570
GSMUPS2AlarmStanjeIzhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D421 | [9 empty] | 0x02802580
GSMUPS2AlarmIzhodPreobremenjen_om | DIGITAL | IOD_GSM_disk | D422 | [9 empty] | 0x02802590
GSMUPS2AlarmOnBypass_om | DIGITAL | IOD_GSM_disk | D423 | [9 empty] | 0x028025a0
GSMUPS2AlarmBypassBad_om | DIGITAL | IOD_GSM_disk | D424 | [9 empty] | 0x028025b0
GSMUPS2AlarmIzhodOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D425 | [9 empty] | 0x028025c0
GSMUPS2AlarmUPSOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D426 | [9 empty] | 0x028025d0
GSMUPS2AlarmChargerFailed_om | DIGITAL | IOD_GSM_disk | D427 | [9 empty] | 0x028025e0
GSMUPS2AlarmUPSIzhodOff_om | DIGITAL | IOD_GSM_disk | D428 | [9 empty] | 0x028025f0
GSMUPS2AlarmUPSSystemOff_om | DIGITAL | IOD_GSM_disk | D429 | [9 empty] | 0x02802600
GSMUPS2AlarmNapakaNaVentilatorju_om | DIGITAL | IOD_GSM_disk | D430 | [9 empty] | 0x02802610
GSMUPS2AlarmNapakaNaVarovalki_om | DIGITAL | IOD_GSM_disk | D431 | [9 empty] | 0x02802620
GSMUPS2AlarmSplosnaNapaka_om | DIGITAL | IOD_GSM_disk | D432 | [9 empty] | 0x02802630
GSMUPS2AlarmDiagnosticTestFailed_om | DIGITAL | IOD_GSM_disk | D433 | [9 empty] | 0x02802640
GSMUPS2AlarmCommunicationsLost_om | DIGITAL | IOD_GSM_disk | D434 | [9 empty] | 0x02802650
GSMUPS2AlarmAwaitingPower_om | DIGITAL | IOD_GSM_disk | D435 | [9 empty] | 0x02802660
GSMUPS2AlarmShutdownPending_om | DIGITAL | IOD_GSM_disk | D436 | [9 empty] | 0x02802670
GSMUPS2AlarmShutdownImminent_om | DIGITAL | IOD_GSM_disk | D437 | [9 empty] | 0x02802680
GSMUPS2AlarmTestInProgres_om | DIGITAL | IOD_GSM_disk | D438 | [9 empty] | 0x02802690
GSMUPS2AlarmInverterError_om | DIGITAL | IOD_GSM_disk | D439 | [9 empty] | 0x028026a0
GSMUPS_MGE1UPS_error_om | DIGITAL | IOD_GSM_disk | D440 | [9 empty] | 0x028026b0
GSMUPS_MGE1BatteryLowWarning_om | DIGITAL | IOD_GSM_disk | D441 | [9 empty] | 0x028026c0
GSMUPS_MGE1DeviceVentilationFault_om | DIGITAL | IOD_GSM_disk | D442 | [9 empty] | 0x028026d0
GSMUPS_MGE1BatteryCompInProgress_om | DIGITAL | IOD_GSM_disk | D443 | [9 empty] | 0x028026e0
GSMUPS_MGE1BatteryTempOutOfToler_om | DIGITAL | IOD_GSM_disk | D444 | [9 empty] | 0x028026f0
GSMUPS_MGE1BatteryFuseFault_om | DIGITAL | IOD_GSM_disk | D445 | [9 empty] | 0x02802700
GSMUPS_MGE1Mains1VoltOutOfToler_om | DIGITAL | IOD_GSM_disk | D446 | [9 empty] | 0x02802710
GSMUPS_MGE1RectifierThermOverload_om | DIGITAL | IOD_GSM_disk | D447 | [9 empty] | 0x02802720
GSMUPS_MGE1MaintenancePosition_om | DIGITAL | IOD_GSM_disk | D448 | [9 empty] | 0x02802730
GSMUPS_MGE1ChargerGeneralFault_om | DIGITAL | IOD_GSM_disk | D449 | [9 empty] | 0x02802740
GSMUPS_MGE1BatteryChargedState_om | DIGITAL | IOD_GSM_disk | D450 | [9 empty] | 0x02802750
GSMUPS_MGE1InverterOverload_om | DIGITAL | IOD_GSM_disk | D451 | [9 empty] | 0x02802760
GSMUPS_MGE1InverterThermalOverload_om | DIGITAL | IOD_GSM_disk | D452 | [9 empty] | 0x02802770
GSMUPS_MGE1OutputThermalOverload_om | DIGITAL | IOD_GSM_disk | D453 | [9 empty] | 0x02802780
GSMUPS_MGE1OutputOverload_om | DIGITAL | IOD_GSM_disk | D454 | [9 empty] | 0x02802790
GSMUPS_MGE1InverterFuseFault_om | DIGITAL | IOD_GSM_disk | D455 | [9 empty] | 0x028027a0
GSMUPS_MGE1OutputInShortCircuit_om | DIGITAL | IOD_GSM_disk | D456 | [9 empty] | 0x028027b0
GSMNapakaSenzorVlagaHIA1_om | DIGITAL | IOD_GSM_disk | D457 | [9 empty] | 0x028027c0
GSMNapakaSenzorVlagaHIA2_om | DIGITAL | IOD_GSM_disk | D458 | [9 empty] | 0x028027d0
GSMNapakaSenzorVlagaHIA3_om | DIGITAL | IOD_GSM_disk | D459 | [9 empty] | 0x028027e0
GSMNapakaSenzorVlagaHIA4_om | DIGITAL | IOD_GSM_disk | D460 | [9 empty] | 0x028027f0
GSMNapakaSenzorVlagaHIA5_om | DIGITAL | IOD_GSM_disk | D461 | [9 empty] | 0x02802800
GSMNapakaSenzorVlagaHIA6_om | DIGITAL | IOD_GSM_disk | D462 | [9 empty] | 0x02802810
GSMNapakaSenzorVlagaHIA7_om | DIGITAL | IOD_GSM_disk | D463 | [9 empty] | 0x02802820
GSMNapakaTSTempTIA1_om | DIGITAL | IOD_GSM_disk | D464 | [9 empty] | 0x02802830
GSMNapakaTSTempTIA2_om | DIGITAL | IOD_GSM_disk | D465 | [9 empty] | 0x02802840
GSMNapakaTSTempTIA3_om | DIGITAL | IOD_GSM_disk | D466 | [9 empty] | 0x02802850
GSMNapakaTSTempTIA4_om | DIGITAL | IOD_GSM_disk | D467 | [9 empty] | 0x02802860
GSMNapakaTSTempTIA5_om | DIGITAL | IOD_GSM_disk | D468 | [9 empty] | 0x02802870
GSMNapakaTSTempTIA6_om | DIGITAL | IOD_GSM_disk | D469 | [9 empty] | 0x02802880
GSMNapakaTSTempTIA7_om | DIGITAL | IOD_GSM_disk | D470 | [9 empty] | 0x02802890
GSMTIA1_previs_temp_om | DIGITAL | IOD_GSM_disk | D471 | [9 empty] | 0x028028a0
GSMTIA2_previs_temp_om | DIGITAL | IOD_GSM_disk | D472 | [9 empty] | 0x028028b0
GSMTIA3_previs_temp_om | DIGITAL | IOD_GSM_disk | D473 | [9 empty] | 0x028028c0
GSMTIA4_previs_temp_om | DIGITAL | IOD_GSM_disk | D474 | [9 empty] | 0x028028d0
GSMTIA5_previs_temp_om | DIGITAL | IOD_GSM_disk | D475 | [9 empty] | 0x028028e0
GSMTIA6_previs_temp_om | DIGITAL | IOD_GSM_disk | D476 | [9 empty] | 0x028028f0
GSMTIA7_previs_temp_om | DIGITAL | IOD_GSM_disk | D477 | [9 empty] | 0x02802900
GSMPMM2OverCurrentBetw_VirA_om | DIGITAL | IOD_GSM_disk | D478 | [9 empty] | 0x02802910
GSMPMM2OverCurrentBetw_VirB_om | DIGITAL | IOD_GSM_disk | D479 | [9 empty] | 0x02802920
GSMPMM2OverCurrentOver_VirA_om | DIGITAL | IOD_GSM_disk | D480 | [9 empty] | 0x02802930
GSMPMM2OverCurrentOver_VirB_om | DIGITAL | IOD_GSM_disk | D481 | [9 empty] | 0x02802940
GSMPMM2OverCurrentBetw_VirA | DIGITAL | IOD_GSM_disk | D482 | [9 empty] | 0x02802950
GSMPMM2OverCurrentBetw_VirB | DIGITAL | IOD_GSM_disk | D483 | [9 empty] | 0x02802960
GSMPMM2OverCurrentOver_VirA | DIGITAL | IOD_GSM_disk | D484 | [9 empty] | 0x02802970
GSMPMM2OverCurrentOver_VirB | DIGITAL | IOD_GSM_disk | D485 | [9 empty] | 0x02802980
GSMAlarmPMM1VirATokPrevisok_om | DIGITAL | IOD_GSM_disk | D486 | [9 empty] | 0x02802990
GSMAlarmPMM1VirATokVisok_om | DIGITAL | IOD_GSM_disk | D487 | [9 empty] | 0x028029a0
GSMAlarmPMM1VirBTokPrevisok_om | DIGITAL | IOD_GSM_disk | D488 | [9 empty] | 0x028029b0
GSMAlarmPMM1VirBTokVisok_om | DIGITAL | IOD_GSM_disk | D489 | [9 empty] | 0x028029c0
GSMAlarmPMM2x17nad801_om | DIGITAL | IOD_GSM_disk | D490 | [9 empty] | 0x028029d0
GSMAlarmPMM2x17nad802_om | DIGITAL | IOD_GSM_disk | D491 | [9 empty] | 0x028029e0
GSMAlarmPMM2x17nad803_om | DIGITAL | IOD_GSM_disk | D492 | [9 empty] | 0x028029f0
GSMAlarmPMM2x17nad804_om | DIGITAL | IOD_GSM_disk | D493 | [9 empty] | 0x02802a00
GSMAlarmPMM2x17nad805_om | DIGITAL | IOD_GSM_disk | D494 | [9 empty] | 0x02802a10
GSMAlarmPMM2x17nad806_om | DIGITAL | IOD_GSM_disk | D495 | [9 empty] | 0x02802a20
GSMAlarmPMM2x17nad807_om | DIGITAL | IOD_GSM_disk | D496 | [9 empty] | 0x02802a30
GSMAlarmPMM2x17nad808_om | DIGITAL | IOD_GSM_disk | D497 | [9 empty] | 0x02802a40
GSMAlarmPMM2x17nad809_om | DIGITAL | IOD_GSM_disk | D498 | [9 empty] | 0x02802a50
GSMAlarmPMM2x17nad8010_om | DIGITAL | IOD_GSM_disk | D499 | [9 empty] | 0x02802a60
GSMAlarmPMM2x17nad8011_om | DIGITAL | IOD_GSM_disk | D500 | [9 empty] | 0x02802a70
GSMAlarmPMM2x17nad8012_om | DIGITAL | IOD_GSM_disk | D501 | [9 empty] | 0x02802a80
GSMAlarmPMM2x17nad8013_om | DIGITAL | IOD_GSM_disk | D502 | [9 empty] | 0x02802a90
GSMAlarmPMM2x17nad8014_om | DIGITAL | IOD_GSM_disk | D503 | [9 empty] | 0x02802aa0
GSMAlarmPMM2x17nad8015_om | DIGITAL | IOD_GSM_disk | D504 | [9 empty] | 0x02802ab0
GSMAlarmPMM2x17nad8016_om | DIGITAL | IOD_GSM_disk | D505 | [9 empty] | 0x02802ac0
GSMAlarmPMM2x17nad8017_om | DIGITAL | IOD_GSM_disk | D506 | [9 empty] | 0x02802ad0
GSMAlarmPMM2x17nad8018_om | DIGITAL | IOD_GSM_disk | D507 | [9 empty] | 0x02802ae0
GSMAlarmPMM2x17nad8019_om | DIGITAL | IOD_GSM_disk | D508 | [9 empty] | 0x02802af0
GSMAlarmPMM2x17nad8020_om | DIGITAL | IOD_GSM_disk | D509 | [9 empty] | 0x02802b00
GSMAlarmPMM2x17nad8021_om | DIGITAL | IOD_GSM_disk | D510 | [9 empty] | 0x02802b10
GSMAlarmPMM2x17nad8022_om | DIGITAL | IOD_GSM_disk | D511 | [9 empty] | 0x02802b20
GSMAlarmPMM2x17nad8023_om | DIGITAL | IOD_GSM_disk | D512 | [9 empty] | 0x02802b30
GSMAlarmPMM2x17nad8024_om | DIGITAL | IOD_GSM_disk | D513 | [9 empty] | 0x02802b40
GSMAlarmPMM2x17nad8025_om | DIGITAL | IOD_GSM_disk | D514 | [9 empty] | 0x02802b50
GSMAlarmPMM2x17nad8026_om | DIGITAL | IOD_GSM_disk | D515 | [9 empty] | 0x02802b60
GSMAlarmPMM2x17nad8027_om | DIGITAL | IOD_GSM_disk | D516 | [9 empty] | 0x02802b70
GSMAlarmPMM2x17nad8028_om | DIGITAL | IOD_GSM_disk | D517 | [9 empty] | 0x02802b80
GSMOpozoriloPMM2x17med60in801_om | DIGITAL | IOD_GSM_disk | D518 | [9 empty] | 0x02802b90
GSMOpozoriloPMM2x17med60in802_om | DIGITAL | IOD_GSM_disk | D519 | [9 empty] | 0x02802ba0
GSMOpozoriloPMM2x17med60in803_om | DIGITAL | IOD_GSM_disk | D520 | [9 empty] | 0x02802bb0
GSMOpozoriloPMM2x17med60in804_om | DIGITAL | IOD_GSM_disk | D521 | [9 empty] | 0x02802bc0
GSMOpozoriloPMM2x17med60in805_om | DIGITAL | IOD_GSM_disk | D522 | [9 empty] | 0x02802bd0
GSMOpozoriloPMM2x17med60in806_om | DIGITAL | IOD_GSM_disk | D523 | [9 empty] | 0x02802be0
GSMOpozoriloPMM2x17med60in807_om | DIGITAL | IOD_GSM_disk | D524 | [9 empty] | 0x02802bf0
GSMOpozoriloPMM2x17med60in808_om | DIGITAL | IOD_GSM_disk | D525 | [9 empty] | 0x02802c00
GSMOpozoriloPMM2x17med60in809_om | DIGITAL | IOD_GSM_disk | D526 | [9 empty] | 0x02802c10
GSMOpozoriloPMM2x17med60in8010_om | DIGITAL | IOD_GSM_disk | D527 | [9 empty] | 0x02802c20
GSMOpozoriloPMM2x17med60in8011_om | DIGITAL | IOD_GSM_disk | D528 | [9 empty] | 0x02802c30
GSMOpozoriloPMM2x17med60in8012_om | DIGITAL | IOD_GSM_disk | D529 | [9 empty] | 0x02802c40
GSMOpozoriloPMM2x17med60in8013_om | DIGITAL | IOD_GSM_disk | D530 | [9 empty] | 0x02802c50
GSMOpozoriloPMM2x17med60in8014_om | DIGITAL | IOD_GSM_disk | D531 | [9 empty] | 0x02802c60
GSMOpozoriloPMM2x17med60in8015_om | DIGITAL | IOD_GSM_disk | D532 | [9 empty] | 0x02802c70
GSMOpozoriloPMM2x17med60in8016_om | DIGITAL | IOD_GSM_disk | D533 | [9 empty] | 0x02802c80
GSMOpozoriloPMM2x17med60in8017_om | DIGITAL | IOD_GSM_disk | D534 | [9 empty] | 0x02802c90
GSMOpozoriloPMM2x17med60in8018_om | DIGITAL | IOD_GSM_disk | D535 | [9 empty] | 0x02802ca0
GSMOpozoriloPMM2x17med60in8019_om | DIGITAL | IOD_GSM_disk | D536 | [9 empty] | 0x02802cb0
GSMOpozoriloPMM2x17med60in8020_om | DIGITAL | IOD_GSM_disk | D537 | [9 empty] | 0x02802cc0
GSMOpozoriloPMM2x17med60in8021_om | DIGITAL | IOD_GSM_disk | D538 | [9 empty] | 0x02802cd0
GSMOpozoriloPMM2x17med60in8022_om | DIGITAL | IOD_GSM_disk | D539 | [9 empty] | 0x02802ce0
GSMOpozoriloPMM2x17med60in8023_om | DIGITAL | IOD_GSM_disk | D540 | [9 empty] | 0x02802cf0
GSMOpozoriloPMM2x17med60in8024_om | DIGITAL | IOD_GSM_disk | D541 | [9 empty] | 0x02802d00
GSMOpozoriloPMM2x17med60in8025_om | DIGITAL | IOD_GSM_disk | D542 | [9 empty] | 0x02802d10
GSMOpozoriloPMM2x17med60in8026_om | DIGITAL | IOD_GSM_disk | D543 | [9 empty] | 0x02802d20
GSMOpozoriloPMM2x17med60in8027_om | DIGITAL | IOD_GSM_disk | D544 | [9 empty] | 0x02802d30
GSMOpozoriloPMM2x17med60in8028_om | DIGITAL | IOD_GSM_disk | D545 | [9 empty] | 0x02802d40
GSMN_UPS_A_V23_delovanje_om | DIGITAL | IOD_GSM_disk | D546 | [9 empty] | 0x02802d50
GSMN_UPS_A_V23_napaka_om | DIGITAL | IOD_GSM_disk | D547 | [9 empty] | 0x02802d60
GSMUPS1Napaka_om | DIGITAL | IOD_GSM_disk | D548 | [9 empty] | 0x02802d70
AGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D600[300] | [9 empty] | 0x02802d80
BGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D900[300] | [9 empty] | 0x02802d90
CGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D1200[300] | [9 empty] | 0x02802da0
DGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D1500[300] | [9 empty] | 0x02802db0
EGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D1800[300] | [9 empty] | 0x02802dc0
FGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D2100[300] | [9 empty] | 0x02802dd0
GSM_Anali_razlika_dnevnaCirc1 | LONG | IOD_GSM_disk | L290 | [9 empty] | 0x02802de0
GSM_Anali_razlika_tedenCirc1 | LONG | IOD_GSM_disk | L292 | [9 empty] | 0x02802de1
GSM_Anali_razlika_mesCirc1 | LONG | IOD_GSM_disk | L294 | [9 empty] | 0x02802de2
GSMUserloggedIn_mem | DIGITAL | IOD_GSM_mem | D572 | [9 empty] | 0x02802df0
GSM_ComSCADA_stevec1 | INT | IOD_GSM_mem | I600 | [9 empty] | 0x02802e00
GSM_ComSCADA_stevec2 | INT | IOD_GSM_mem | I601 | [9 empty] | 0x02802e01
GSM_ComSCADA_stevec3 | INT | IOD_GSM_mem | I602 | [9 empty] | 0x02802e02
GSM_ComSCADA_stevec4 | INT | IOD_GSM_mem | I603 | [9 empty] | 0x02802e03
GSMKLIMAT1_vklop_delovanjaR | DIGITAL | IOD_GSM | GSM:.KLIMAT1_vklop_delovanjaR | [6 empty] | Zahteva za vklop klime1 iz panela v ročn. režim | 6157 | 1 | 0x02802e10
GSMKLIMAT2_vklop_delovanjaR | DIGITAL | IOD_GSM | GSM:.KLIMAT2_vklop_delovanjaR | [6 empty] | Zahteva za vklop klime2 iz panela v ročn. režim | 6157 | 1 | 0x02802e20
GSMKLIMAT1_R_zakleni | DIGITAL | IOD_GSM | GSM:.KLIMAT1_R_zakleni | [6 empty] | Preprečitev ročn. vklopa klime1 v AVTO režimu | 6157 | 1 | 0x02802e30
GSMKLIMAT2_R_zakleni | DIGITAL | IOD_GSM | GSM:.KLIMAT2_R_zakleni | [6 empty] | Preprečitev ročn. vklopa klime2 v AVTO režimu | 6157 | 1 | 0x02802e40
GSMK1_vklop_izklop_poteka | DIGITAL | IOD_GSM | GSM:.K1_vklop_izklop_poteka | [6 empty] | Izpis med čakanj. na vkl./izkl. Klime1 po zaht. | 6157 | 1 | 0x02802e50
GSMK2_vklop_izklop_poteka | DIGITAL | IOD_GSM | GSM:.K2_vklop_izklop_poteka | [6 empty] | Izpis med čakanj. na vkl./izkl. Klime2 po zaht. | 6157 | 1 | 0x02802e60
GSMPMMskupniTokA | REAL | IOD_GSM | GSM:.PMMskupniTokA | 0 | 230 | 0 | 230 | A | ####.# | PMM Skupni tok Vir A | 6157 | 1 | 0x02802e70
GSMPMMskupniTokB | REAL | IOD_GSM | GSM:.PMMskupniTokB | 0 | 230 | 0 | 230 | A | ####.# | PMM Skupni tok Vir B | 6157 | 1 | 0x02802e71
GSMUPS2Napaka_om | DIGITAL | IOD_GSM_disk | D549 | [9 empty] | 0x02802e80
GSMN_KlimeAVTO | DIGITAL | IOD_GSM | GSM:.N_KlimeAVTO | [7 empty] | 6157 | 1 | 0x02802e90
GSMK1_obr_u_skupno | UINT | IOD_GSM | GSM:.K1_obr_u_skupno | [9 empty] | 0x02802ea0
GSMK2_obr_u_skupno | UINT | IOD_GSM | GSM:.K2_obr_u_skupno | [9 empty] | 0x02802ea1
GSMUPS3AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmAwaitingPower | [7 empty] | 6157 | 1 | 0x02802eb0
GSMUPS3AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmBypassBad | [7 empty] | 6157 | 1 | 0x02802ec0
GSMUPS3AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmChargerFailed | [7 empty] | 6157 | 1 | 0x02802ed0
GSMUPS3AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmCommunicationsLost | [7 empty] | 6157 | 1 | 0x02802ee0
GSMUPS3AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmDepletedBattery | [7 empty] | 6157 | 1 | 0x02802ef0
GSMUPS3AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmDiagnosticTestFailed | [7 empty] | 6157 | 1 | 0x02802f00
GSMUPS3AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmInverterError | [7 empty] | 6157 | 1 | 0x02802f10
GSMUPS3AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmIzhodOffKotZahtevano | [7 empty] | 6157 | 1 | 0x02802f20
GSMUPS3AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmIzhodPreobremenjen | [7 empty] | 6157 | 1 | 0x02802f30
GSMUPS3AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmLowBattery | [7 empty] | 6157 | 1 | 0x02802f40
GSMUPS3AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmNapakaNaVarovalki | [7 empty] | 6157 | 1 | 0x02802f50
GSMUPS3AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmNapakaNaVentilatorju | [7 empty] | 6157 | 1 | 0x02802f60
GSMUPS3AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmOnBattery | [7 empty] | 6157 | 1 | 0x02802f70
GSMUPS3AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmOnBypass | [7 empty] | 6157 | 1 | 0x02802f80
GSMUPS3AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmShutdownImminent | [7 empty] | 6157 | 1 | 0x02802f90
GSMUPS3AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmShutdownPending | [7 empty] | 6157 | 1 | 0x02802fa0
GSMUPS3AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmSlabaBaterija | [7 empty] | 6157 | 1 | 0x02802fb0
GSMUPS3AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmSplosnaNapaka | [7 empty] | 6157 | 1 | 0x02802fc0
GSMUPS3AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmStanjeIzhodaIzvenToleranc | [7 empty] | 6157 | 1 | 0x02802fd0
GSMUPS3AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmStanjeVhodaIzvenToleranc | [7 empty] | 6157 | 1 | 0x02802fe0
GSMUPS3AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmTemperaturaIzvenToleranc | [7 empty] | 6157 | 1 | 0x02802ff0
GSMUPS3AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmTestInProgres | [7 empty] | 6157 | 1 | 0x02803000
GSMUPS3AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSIzhodOff | [7 empty] | 6157 | 1 | 0x02803010
GSMUPS3AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSOffKotZahtevano | [7 empty] | 6157 | 1 | 0x02803020
GSMUPS3AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSSystemOff | [7 empty] | 6157 | 1 | 0x02803030
GSMUPS3EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[3].EstimatedChargeRemaining | 0 | 100 | 0 | 100 | % | ### |  | 6157 | 1 | 0x02803040
GSMUPS3EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[3].EstimatedMinutesRemaining | 0 | 500 | 0 | 500 | min | ### |  | 6157 | 1 | 0x02803041
GSMUPS3InverterStatus | INT | IOD_GSM | GSM:.UPS[3].InverterStatus | [7 empty] | 6157 | 1 | 0x02803042
GSMUPS3IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL1 | 0 | 100 | 0 | 100 | % | ##.# |  | 6157 | 1 | 0x02803043
GSMUPS3IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL2 | 0 | 100 | 0 | 100 | % | ##.# |  | 6157 | 1 | 0x02803044
GSMUPS3IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL3 | 0 | 100 | 0 | 100 | % | ##.# |  | 6157 | 1 | 0x02803045
GSMUPS3Napaka | DIGITAL | IOD_GSM | GSM:.UPS[3].Napaka | [7 empty] | 6157 | 1 | 0x02803050
GSMUPS3NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[3].NapetostBaterije | 0 | 600.0 | 0 | 600.0 | V | ###.# |  | 6157 | 1 | 0x02803060
GSMUPS3OutputStatus | INT | IOD_GSM | GSM:.UPS[3].OutputStatus | [7 empty] | 6157 | 1 | 0x02803061
GSMUPS3StatusBaterije | UINT | IOD_GSM | GSM:.UPS[3].StatusBaterije | [5 empty] | ## |  | 6157 | 1 | 0x02803062
GSMUPS3StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusEcomodeAktiven | [7 empty] | 6157 | 1 | 0x02803070
GSMUPS3StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusInverterIsOn | [7 empty] | 6157 | 1 | 0x02803080
GSMUPS3StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusStopOperation | [7 empty] | 6157 | 1 | 0x02803090
GSMUPS3SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[3].SteviloIzpadovVhodneLinije | [5 empty] | ##### |  | 6157 | 1 | 0x028030a0
GSMUPS3TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[3].TemperaturaBaterije | 0 | 100 | 0 | 100 | °C | ### |  | 6157 | 1 | 0x028030a1
GSMUPS3UnitStatus | INT | IOD_GSM | GSM:.UPS[3].UnitStatus | [7 empty] | 6157 | 1 | 0x028030a2
GSMUPS3VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL1 | 0 | 60.0 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x028030a3
GSMUPS3VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL2 | 0 | 60.0 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x028030a4
GSMUPS3VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL3 | 0 | 60.0 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x028030a5
GSMUPS3VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL1 | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x028030a6
GSMUPS3VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL2 | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x028030a7
GSMUPS3VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL3 | 0 | 500.0 | 0 | 500.0 | V | ###.# |  | 6157 | 1 | 0x028030a8
GSMErrComUPS3 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[3] | [7 empty] | 6157 | 1 | 0x028030b0
GSMUPS3AlarmSlabaBaterija_om | DIGITAL | IOD_GSM_disk | D2400 | [9 empty] | 0x028030c0
GSMUPS3AlarmOnBattery_om | DIGITAL | IOD_GSM_disk | D2401 | [9 empty] | 0x028030d0
GSMUPS3AlarmLowBattery_om | DIGITAL | IOD_GSM_disk | D2402 | [9 empty] | 0x028030e0
GSMUPS3AlarmDepletedBattery_om | DIGITAL | IOD_GSM_disk | D2403 | [9 empty] | 0x028030f0
GSMUPS3AlarmTemperaturaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D2404 | [9 empty] | 0x02803100
GSMUPS3AlarmStanjeVhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D2405 | [9 empty] | 0x02803110
GSMUPS3AlarmStanjeIzhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D2406 | [9 empty] | 0x02803120
GSMUPS3AlarmIzhodPreobremenjen_om | DIGITAL | IOD_GSM_disk | D2407 | [9 empty] | 0x02803130
GSMUPS3AlarmOnBypass_om | DIGITAL | IOD_GSM_disk | D2408 | [9 empty] | 0x02803140
GSMUPS3AlarmBypassBad_om | DIGITAL | IOD_GSM_disk | D2409 | [9 empty] | 0x02803150
GSMUPS3AlarmIzhodOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D2410 | [9 empty] | 0x02803160
GSMUPS3AlarmUPSOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D2411 | [9 empty] | 0x02803170
GSMUPS3AlarmChargerFailed_om | DIGITAL | IOD_GSM_disk | D2412 | [9 empty] | 0x02803180
GSMUPS3AlarmUPSIzhodOff_om | DIGITAL | IOD_GSM_disk | D2413 | [9 empty] | 0x02803190
GSMUPS3AlarmUPSSystemOff_om | DIGITAL | IOD_GSM_disk | D2414 | [9 empty] | 0x028031a0
GSMUPS3AlarmNapakaNaVentilatorju_om | DIGITAL | IOD_GSM_disk | D2415 | [9 empty] | 0x028031b0
GSMUPS3AlarmNapakaNaVarovalki_om | DIGITAL | IOD_GSM_disk | D2416 | [9 empty] | 0x028031c0
GSMUPS3AlarmSplosnaNapaka_om | DIGITAL | IOD_GSM_disk | D2417 | [9 empty] | 0x028031d0
GSMUPS3AlarmDiagnosticTestFailed_om | DIGITAL | IOD_GSM_disk | D2418 | [9 empty] | 0x028031e0
GSMUPS3AlarmCommunicationsLost_om | DIGITAL | IOD_GSM_disk | D2419 | [9 empty] | 0x028031f0
GSMUPS3AlarmAwaitingPower_om | DIGITAL | IOD_GSM_disk | D2420 | [9 empty] | 0x02803200
GSMUPS3AlarmShutdownPending_om | DIGITAL | IOD_GSM_disk | D2421 | [9 empty] | 0x02803210
GSMUPS3AlarmShutdownImminent_om | DIGITAL | IOD_GSM_disk | D2422 | [9 empty] | 0x02803220
GSMUPS3AlarmTestInProgres_om | DIGITAL | IOD_GSM_disk | D2423 | [9 empty] | 0x02803230
GSMUPS3AlarmInverterError_om | DIGITAL | IOD_GSM_disk | D2424 | [9 empty] | 0x02803240
GSMUPS3Napaka_om | DIGITAL | IOD_GSM_disk | D2425 | [9 empty] | 0x02803250
GSMGSM_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.GSM_PozCent_napaka | [7 empty] | 6157 | 1 | 0x02803260
GSMGSM_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.GSM_PozSenzor_okvara | [7 empty] | 6157 | 1 | 0x02803270
GSMGSM_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.GSM_Gasenje_alarm | [7 empty] | 6157 | 1 | 0x02803280
GSMAGR_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.AGR_PozCent_napaka | [7 empty] | 6157 | 1 | 0x02803290
GSMAGR_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.AGR_PozSenzor_okvara | [7 empty] | 6157 | 1 | 0x028032a0
GSMAGR_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.AGR_Gasenje_alarm | [7 empty] | 6157 | 1 | 0x028032b0
GSMGSM_PozCent_napaka_om | DIGITAL | IOD_GSM_disk | D2426 | [9 empty] | 0x028032c0
GSMGSM_PozSenzor_okvara_om | DIGITAL | IOD_GSM_disk | D2427 | [9 empty] | 0x028032d0
GSMGSM_Gasenje_alarm_om | DIGITAL | IOD_GSM_disk | D2428 | [9 empty] | 0x028032e0
GSMAGR_PozCent_napaka_om | DIGITAL | IOD_GSM_disk | D2429 | [9 empty] | 0x028032f0
GSMAGR_PozSenzor_okvara_om | DIGITAL | IOD_GSM_disk | D2430 | [9 empty] | 0x02803300
GSMAGR_Gasenje_alarm_om | DIGITAL | IOD_GSM_disk | D2431 | [9 empty] | 0x02803310
GSMCirc1MaximumDemandA2 | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemandA2 | 0 | 1200.0 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x02803320
GSMCirc1MaximumDemandA3 | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemandA3 | 0 | 1200.0 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x02803321
GSMCirc1RazEner_D_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x02803322
GSMCirc1RazEner_T_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x02803323
GSMCirc1RazEner_M_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x02803324
GSMCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Dnevne_energija_scada1 | [7 empty] | 6157 | 1 | 0x02803330
GSMCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Dnevne_energija_scada2 | [7 empty] | 6157 | 1 | 0x02803340
GSMCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Tedenska_energija_scada1 | [7 empty] | 6157 | 1 | 0x02803350
GSMCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Tedenska_energija_scada2 | [7 empty] | 6157 | 1 | 0x02803360
GSMCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Mesecna_energija_scada1 | [7 empty] | 6157 | 1 | 0x02803370
GSMCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Mesecna_energija_scada2 | [7 empty] | 6157 | 1 | 0x02803380
GSMCirc_Vpis_Dnevne_energija_scada1_mem | DIGITAL | IOD_GSM_disk | D3000 | [9 empty] | 0x02803390
GSMCirc_Vpis_Dnevne_energija_scada2_mem | DIGITAL | IOD_GSM_disk | D3001 | [9 empty] | 0x028033a0
GSMCirc_Vpis_Tedenska_energija_scada1_mem | DIGITAL | IOD_GSM_disk | D3002 | [9 empty] | 0x028033b0
GSMCirc_Vpis_Tedenska_energija_scada2_mem | DIGITAL | IOD_GSM_disk | D3003 | [9 empty] | 0x028033c0
GSMCirc_Vpis_Mesecna_energija_scada1_mem | DIGITAL | IOD_GSM_disk | D3004 | [9 empty] | 0x028033d0
GSMCirc_Vpis_Mesecna_energija_scada2_mem | DIGITAL | IOD_GSM_disk | D3005 | [9 empty] | 0x028033e0
GSMPozarnaCentrala_skupno | DIGITAL | IOD_GSM | GSM:.PozarnaCentrala_skupno | [7 empty] | 6157 | 1 | 0x028033f0

## variable_1
GSMAlarmGenUPS_A_V23 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_A_V23
GSMAlarmGenUPS_V23 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_V23
GSMAlarmGenUPS_V25 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_V25
GSMAlarmPMM1VirATokPrevisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirATokPrevisok
GSMAlarmPMM1VirATokVisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirATokVisok
GSMAlarmPMM1VirBTokPrevisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirBTokPrevisok
GSMAlarmPMM1VirBTokVisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirBTokVisok
GSMAlarmPMM2x17nad8010 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[10]
GSMAlarmPMM2x17nad8011 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[11]
GSMAlarmPMM2x17nad8012 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[12]
GSMAlarmPMM2x17nad8013 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[13]
GSMAlarmPMM2x17nad8014 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[14]
GSMAlarmPMM2x17nad8015 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[15]
GSMAlarmPMM2x17nad8016 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[16]
GSMAlarmPMM2x17nad8017 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[17]
GSMAlarmPMM2x17nad8018 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[18]
GSMAlarmPMM2x17nad8019 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[19]
GSMAlarmPMM2x17nad801 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[1]
GSMAlarmPMM2x17nad8020 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[20]
GSMAlarmPMM2x17nad8021 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[21]
GSMAlarmPMM2x17nad8022 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[22]
GSMAlarmPMM2x17nad8023 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[23]
GSMAlarmPMM2x17nad8024 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[24]
GSMAlarmPMM2x17nad8025 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[25]
GSMAlarmPMM2x17nad8026 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[26]
GSMAlarmPMM2x17nad8027 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[27]
GSMAlarmPMM2x17nad8028 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[28]
GSMAlarmPMM2x17nad8029 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[29]
GSMAlarmPMM2x17nad802 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[2]
GSMAlarmPMM2x17nad8030 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[30]
GSMAlarmPMM2x17nad8031 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[31]
GSMAlarmPMM2x17nad8032 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[32]
GSMAlarmPMM2x17nad8033 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[33]
GSMAlarmPMM2x17nad8034 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[34]
GSMAlarmPMM2x17nad8035 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[35]
GSMAlarmPMM2x17nad8036 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[36]
GSMAlarmPMM2x17nad8037 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[37]
GSMAlarmPMM2x17nad8038 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[38]
GSMAlarmPMM2x17nad8039 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[39]
GSMAlarmPMM2x17nad803 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[3]
GSMAlarmPMM2x17nad8040 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[40]
GSMAlarmPMM2x17nad8041 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[41]
GSMAlarmPMM2x17nad8042 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[42]
GSMAlarmPMM2x17nad804 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[4]
GSMAlarmPMM2x17nad805 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[5]
GSMAlarmPMM2x17nad806 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[6]
GSMAlarmPMM2x17nad807 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[7]
GSMAlarmPMM2x17nad808 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[8]
GSMAlarmPMM2x17nad809 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[9]
GSMCirc1CosFi_III | REAL | IOD_GSM | GSM:.Circ[1].CosFi_III
GSMCirc1DelovnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].DelovnaEnergija
GSMCirc1DelovnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_III
GSMCirc1DelovnaMoc_L1 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L1
GSMCirc1DelovnaMoc_L2 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L2
GSMCirc1DelovnaMoc_L3 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L3
GSMCirc1Frekvenca_L1 | REAL | IOD_GSM | GSM:.Circ[1].Frekvenca_L1
GSMCirc1InduktivnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].InduktivnaEnergija
GSMCirc1InduktivnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].InduktivnaMoc_III
GSMCirc1JalovaMoc_L1 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L1
GSMCirc1JalovaMoc_L2 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L2
GSMCirc1JalovaMoc_L3 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L3
GSMCirc1KapacitivnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].KapacitivnaEnergija
GSMCirc1KapacitivnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].KapacitivnaMoc_III
GSMCirc1MaximumDemand | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemand
GSMCirc1Napetost_L1_L2 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L1_L2
GSMCirc1Napetost_L1_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L1_N
GSMCirc1Napetost_L2_L3 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L2_L3
GSMCirc1Napetost_L2_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L2_N
GSMCirc1Napetost_L3_L1 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L3_L1
GSMCirc1Napetost_L3_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L3_N
GSMCirc1NavideznaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].NavideznaMoc_III
GSMCirc1NicelniTok | REAL | IOD_GSM | GSM:.Circ[1].NicelniTok
GSMCirc1PowerFactor_III | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_III
GSMCirc1PowerFactor_L1 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L1
GSMCirc1PowerFactor_L2 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L2
GSMCirc1PowerFactor_L3 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L3
GSMCirc1THDI_L1 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L1
GSMCirc1THDI_L2 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L2
GSMCirc1THDI_L3 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L3
GSMCirc1THDV_L1 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L1
GSMCirc1THDV_L2 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L2
GSMCirc1THDV_L3 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L3
GSMCirc1Tok_L1 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L1
GSMCirc1Tok_L2 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L2
GSMCirc1Tok_L3 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L3
GSMCirc1TokPovprecje_III | REAL | IOD_GSM | GSM:.Circ[1].TokPovprecje_III
GSMComError | DIGITAL | IOD_GSM | GSM:.ComError
GSMComSCADA | DIGITAL | IOD_GSM | GSM:.ComSCADA
GSMComSCADA1 | DIGITAL | IOD_GSM | GSM:.ComSCADA1
GSMComSCADA2 | DIGITAL | IOD_GSM | GSM:.ComSCADA2
GSMComSCADA3 | DIGITAL | IOD_GSM | GSM:.ComSCADA3
GSMDate_Time0 | STRING | IOD_GSM | GSM:.Date_Time[0]
GSMDate_Time1 | STRING | IOD_GSM | GSM:.Date_Time[1]
GSMDate_Time2 | STRING | IOD_GSM | GSM:.Date_Time[2]
GSMDate_Time3 | STRING | IOD_GSM | GSM:.Date_Time[3]
GSMDateTimeDan | INT | IOD_GSM | GSM:.DateTime.Dan | BYTE
GSMDateTimeLeto | INT | IOD_GSM | GSM:.DateTime.Leto | BYTE
GSMDateTimeLeto2 | INT | IOD_GSM | GSM:.DateTime.Leto2
GSMDateTimeMesec | INT | IOD_GSM | GSM:.DateTime.Mesec | BYTE
GSMDateTimeMinuta | INT | IOD_GSM | GSM:.DateTime.Minuta | BYTE
GSMDateTimeSekunda | INT | IOD_GSM | GSM:.DateTime.Sekunda | BYTE
GSMDateTimeUra | INT | IOD_GSM | GSM:.DateTime.Ura | BYTE
GSMErrComCirc1 | DIGITAL | IOD_GSM | GSM:.ErrComCirc[1]
GSMErrComKlima1 | DIGITAL | IOD_GSM | GSM:.ErrComKlima[1]
GSMErrComKlima2 | DIGITAL | IOD_GSM | GSM:.ErrComKlima[2]
GSMErrComPMM1 | DIGITAL | IOD_GSM | GSM:.ErrComPMM[1]
GSMErrComPort2 | DIGITAL | IOD_GSM | GSM:.ErrComPort2
GSMErrComPort3 | DIGITAL | IOD_GSM | GSM:.ErrComPort3
GSMErrComPort4 | DIGITAL | IOD_GSM | GSM:.ErrComPort4
GSMErrComUPS1 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[1]
GSMErrComUPS2 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[2]
GSMErrComUPSMGE1 | DIGITAL | IOD_GSM | GSM:.ErrComUPSMGE[1]
GSMErrorComCirc1Code10 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[10] | BYTE
GSMErrorComCirc1Code11 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[11] | BYTE
GSMErrorComCirc1Code12 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[12] | BYTE
GSMErrorComCirc1Code13 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[13] | BYTE
GSMErrorComCirc1Code14 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[14] | BYTE
GSMErrorComCirc1Code15 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[15] | BYTE
GSMErrorComCirc1Code1 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[1] | BYTE
GSMErrorComCirc1Code2 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[2] | BYTE
GSMErrorComCirc1Code3 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[3] | BYTE
GSMErrorComCirc1Code4 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[4] | BYTE
GSMErrorComCirc1Code5 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[5] | BYTE
GSMErrorComCirc1Code6 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[6] | BYTE
GSMErrorComCirc1Code7 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[7] | BYTE
GSMErrorComCirc1Code8 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[8] | BYTE
GSMErrorComCirc1Code9 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[9] | BYTE
GSMErrorComCirc1Error | DIGITAL | IOD_GSM | GSM:.ErrorComCirc[1].Error
GSMErrorComCirc1Status | INT | IOD_GSM | GSM:.ErrorComCirc[1].Status
GSMErrorComKlima1Code10 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[10] | BYTE
GSMErrorComKlima1Code11 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[11] | BYTE
GSMErrorComKlima1Code12 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[12] | BYTE
GSMErrorComKlima1Code13 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[13] | BYTE
GSMErrorComKlima1Code14 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[14] | BYTE
GSMErrorComKlima1Code15 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[15] | BYTE
GSMErrorComKlima1Code1 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[1] | BYTE
GSMErrorComKlima1Code2 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[2] | BYTE
GSMErrorComKlima1Code3 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[3] | BYTE
GSMErrorComKlima1Code4 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[4] | BYTE
GSMErrorComKlima1Code5 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[5] | BYTE
GSMErrorComKlima1Code6 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[6] | BYTE
GSMErrorComKlima1Code7 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[7] | BYTE
GSMErrorComKlima1Code8 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[8] | BYTE
GSMErrorComKlima1Code9 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[9] | BYTE
GSMErrorComKlima1Error | DIGITAL | IOD_GSM | GSM:.ErrorComKlima[1].Error
GSMErrorComKlima1Status | INT | IOD_GSM | GSM:.ErrorComKlima[1].Status
GSMErrorComKlima2Code10 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[10] | BYTE
GSMErrorComKlima2Code11 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[11] | BYTE
GSMErrorComKlima2Code12 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[12] | BYTE
GSMErrorComKlima2Code13 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[13] | BYTE
GSMErrorComKlima2Code14 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[14] | BYTE
GSMErrorComKlima2Code15 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[15] | BYTE
GSMErrorComKlima2Code1 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[1] | BYTE
GSMErrorComKlima2Code2 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[2] | BYTE
GSMErrorComKlima2Code3 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[3] | BYTE
GSMErrorComKlima2Code4 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[4] | BYTE
GSMErrorComKlima2Code5 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[5] | BYTE
GSMErrorComKlima2Code6 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[6] | BYTE
GSMErrorComKlima2Code7 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[7] | BYTE
GSMErrorComKlima2Code8 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[8] | BYTE
GSMErrorComKlima2Code9 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[9] | BYTE
GSMErrorComKlima2Error | DIGITAL | IOD_GSM | GSM:.ErrorComKlima[2].Error
GSMErrorComKlima2Status | INT | IOD_GSM | GSM:.ErrorComKlima[2].Status
GSMErrorComPMM1Code10 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[10] | BYTE
GSMErrorComPMM1Code11 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[11] | BYTE
GSMErrorComPMM1Code12 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[12] | BYTE
GSMErrorComPMM1Code13 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[13] | BYTE
GSMErrorComPMM1Code14 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[14] | BYTE
GSMErrorComPMM1Code15 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[15] | BYTE
GSMErrorComPMM1Code1 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[1] | BYTE
GSMErrorComPMM1Code2 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[2] | BYTE
GSMErrorComPMM1Code3 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[3] | BYTE
GSMErrorComPMM1Code4 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[4] | BYTE
GSMErrorComPMM1Code5 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[5] | BYTE
GSMErrorComPMM1Code6 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[6] | BYTE
GSMErrorComPMM1Code7 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[7] | BYTE
GSMErrorComPMM1Code8 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[8] | BYTE
GSMErrorComPMM1Code9 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[9] | BYTE
GSMErrorComPMM1Error | DIGITAL | IOD_GSM | GSM:.ErrorComPMM[1].Error
GSMErrorComPMM1Status | INT | IOD_GSM | GSM:.ErrorComPMM[1].Status
GSMErrorComUPS1Code10 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[10] | BYTE
GSMErrorComUPS1Code11 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[11] | BYTE
GSMErrorComUPS1Code12 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[12] | BYTE
GSMErrorComUPS1Code13 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[13] | BYTE
GSMErrorComUPS1Code14 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[14] | BYTE
GSMErrorComUPS1Code15 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[15] | BYTE
GSMErrorComUPS1Code1 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[1] | BYTE
GSMErrorComUPS1Code2 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[2] | BYTE
GSMErrorComUPS1Code3 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[3] | BYTE
GSMErrorComUPS1Code4 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[4] | BYTE
GSMErrorComUPS1Code5 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[5] | BYTE
GSMErrorComUPS1Code6 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[6] | BYTE
GSMErrorComUPS1Code7 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[7] | BYTE
GSMErrorComUPS1Code8 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[8] | BYTE
GSMErrorComUPS1Code9 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[9] | BYTE
GSMErrorComUPS1Error | DIGITAL | IOD_GSM | GSM:.ErrorComUPS[1].Error
GSMErrorComUPS1Status | INT | IOD_GSM | GSM:.ErrorComUPS[1].Status
GSMErrorComUPS2Code10 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[10] | BYTE
GSMErrorComUPS2Code11 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[11] | BYTE
GSMErrorComUPS2Code12 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[12] | BYTE
GSMErrorComUPS2Code13 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[13] | BYTE
GSMErrorComUPS2Code14 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[14] | BYTE
GSMErrorComUPS2Code15 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[15] | BYTE
GSMErrorComUPS2Code1 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[1] | BYTE
GSMErrorComUPS2Code2 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[2] | BYTE
GSMErrorComUPS2Code3 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[3] | BYTE
GSMErrorComUPS2Code4 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[4] | BYTE
GSMErrorComUPS2Code5 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[5] | BYTE
GSMErrorComUPS2Code6 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[6] | BYTE
GSMErrorComUPS2Code7 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[7] | BYTE
GSMErrorComUPS2Code8 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[8] | BYTE
GSMErrorComUPS2Code9 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[9] | BYTE
GSMErrorComUPS2Error | DIGITAL | IOD_GSM | GSM:.ErrorComUPS[2].Error
GSMErrorComUPS2Status | INT | IOD_GSM | GSM:.ErrorComUPS[2].Status
GSMErrorComUPSMGE1Code10 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[10] | BYTE
GSMErrorComUPSMGE1Code11 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[11] | BYTE
GSMErrorComUPSMGE1Code12 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[12] | BYTE
GSMErrorComUPSMGE1Code13 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[13] | BYTE
GSMErrorComUPSMGE1Code14 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[14] | BYTE
GSMErrorComUPSMGE1Code15 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[15] | BYTE
GSMErrorComUPSMGE1Code1 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[1] | BYTE
GSMErrorComUPSMGE1Code2 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[2] | BYTE
GSMErrorComUPSMGE1Code3 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[3] | BYTE
GSMErrorComUPSMGE1Code4 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[4] | BYTE
GSMErrorComUPSMGE1Code5 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[5] | BYTE
GSMErrorComUPSMGE1Code6 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[6] | BYTE
GSMErrorComUPSMGE1Code7 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[7] | BYTE
GSMErrorComUPSMGE1Code8 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[8] | BYTE
GSMErrorComUPSMGE1Code9 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[9] | BYTE
GSMErrorComUPSMGE1Error | DIGITAL | IOD_GSM | GSM:.ErrorComUPSMGE[1].Error
GSMErrorComUPSMGE1Status | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Status
GSMF1_1_zascita_ok | DIGITAL | IOD_GSM | GSM:.F1_1_zascita_ok
GSMHIA1_vlaga_s | INT | IOD_GSM | GSM:.HIA1_vlaga_s
GSMHIA2_vlaga_s | INT | IOD_GSM | GSM:.HIA2_vlaga_s
GSMHIA3_vlaga_s | INT | IOD_GSM | GSM:.HIA3_vlaga_s
GSMHIA4_vlaga_s | INT | IOD_GSM | GSM:.HIA4_vlaga_s
GSMHIA5_vlaga_s | INT | IOD_GSM | GSM:.HIA5_vlaga_s
GSMHIA6_vlaga_s | INT | IOD_GSM | GSM:.HIA6_vlaga_s
GSMHIA7_vlaga_s | INT | IOD_GSM | GSM:.HIA7_vlaga_s
GSMK1_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K1_SkupnaNapaka
GSMK1AlarmPozara | DIGITAL | IOD_GSM | GSM:.K1AlarmPozara
GSMK1KlimaZdruzenAlarm | DIGITAL | IOD_GSM | GSM:.K1KlimaZdruzenAlarm
GSMK1NiPretoka | DIGITAL | IOD_GSM | GSM:.K1NiPretoka
GSMK1OkvaraRototerma | DIGITAL | IOD_GSM | GSM:.K1OkvaraRototerma
GSMK1OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.K1OkvaraVlazNap
GSMK1PreobMotCrpGr | DIGITAL | IOD_GSM | GSM:.K1PreobMotCrpGr
GSMK1PreobMotVent | DIGITAL | IOD_GSM | GSM:.K1PreobMotVent
GSMK1ProtizamrzZascAkt | DIGITAL | IOD_GSM | GSM:.K1ProtizamrzZascAkt
GSMK1ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.K1ZamasenostFiltra
GSMK2_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K2_SkupnaNapaka
GSMK2AlarmPozara | DIGITAL | IOD_GSM | GSM:.K2AlarmPozara
GSMK2KlimaZdruzenAlarm | DIGITAL | IOD_GSM | GSM:.K2KlimaZdruzenAlarm
GSMK2NiPretoka | DIGITAL | IOD_GSM | GSM:.K2NiPretoka
GSMK2OkvaraRototerma | DIGITAL | IOD_GSM | GSM:.K2OkvaraRototerma
GSMK2OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.K2OkvaraVlazNap
GSMK2PreobMotCrpGr | DIGITAL | IOD_GSM | GSM:.K2PreobMotCrpGr
GSMK2PreobMotVent | DIGITAL | IOD_GSM | GSM:.K2PreobMotVent
GSMK2ProtizamrzZascAkt | DIGITAL | IOD_GSM | GSM:.K2ProtizamrzZascAkt
GSMK2ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.K2ZamasenostFiltra
GSMK3_deluje | DIGITAL | IOD_GSM | GSM:.K3_deluje
GSMK3_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K3_SkupnaNapaka
GSMKlima1_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima1_izkljucena
GSMKLIMA1_kke_pogon | DIGITAL | IOD_GSM | GSM:.KLIMA1_kke_pogon
GSMKLIMA1_krm_nap_ok | DIGITAL | IOD_GSM | GSM:.KLIMA1_krm_nap_ok
GSMKlima2_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima2_izkljucena
GSMKlima3_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima3_izkljucena
GSMKlima1Alarm_pozar | DIGITAL | IOD_GSM | GSM:.Klima[1].Alarm_pozar
GSMKlima1Analog_izh_mesanje | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_mesanje
GSMKlima1Analog_izh_rekuperator | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_rekuperator
GSMKlima1Analog_izh_VentGrelnika | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_VentGrelnika
GSMKlima1Analog_izh_VentHlajenja | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_VentHlajenja
GSMKlima1Dejanska_zel_temp | INT | IOD_GSM | GSM:.Klima[1].Dejanska_zel_temp
GSMKlima1DelVentHit1 | DIGITAL | IOD_GSM | GSM:.Klima[1].DelVentHit1
GSMKlima1DelVentHit2 | DIGITAL | IOD_GSM | GSM:.Klima[1].DelVentHit2
GSMKlima1Hitrost_del_vent_disp | INT | IOD_GSM | GSM:.Klima[1].Hitrost_del_vent_disp
GSMKlima1Max_vpih | INT | IOD_GSM | GSM:.Klima[1].Max_vpih
GSMKlima1Min_vpih | INT | IOD_GSM | GSM:.Klima[1].Min_vpih
GSMKlima1Ni_pretoka | DIGITAL | IOD_GSM | GSM:.Klima[1].Ni_pretoka
GSMKlima1Obrat_ure_Vent_h1 | INT | IOD_GSM | GSM:.Klima[1].Obrat_ure_Vent_h1
GSMKlima1Obrat_ure_Vent_h2 | INT | IOD_GSM | GSM:.Klima[1].Obrat_ure_Vent_h2
GSMKlima1OkvaraRototerm | DIGITAL | IOD_GSM | GSM:.Klima[1].OkvaraRototerm
GSMKlima1OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.Klima[1].OkvaraVlazNap
GSMKlima1Pol_komp_konec | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_konec
GSMKlima1Pol_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_sprem_zel_vr
GSMKlima1Pol_komp_zacetek | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_zacetek
GSMKlima1PreklopHitDelVent | INT | IOD_GSM | GSM:.Klima[1].PreklopHitDelVent
GSMKlima1PreobMotCrpGrel | DIGITAL | IOD_GSM | GSM:.Klima[1].PreobMotCrpGrel
GSMKlima1PreobMotVent | DIGITAL | IOD_GSM | GSM:.Klima[1].PreobMotVent
GSMKlima1Protizamrz_zascita | INT | IOD_GSM | GSM:.Klima[1].Protizamrz_zascita
GSMKlima1ProtizamrzZascAktivna | DIGITAL | IOD_GSM | GSM:.Klima[1].ProtizamrzZascAktivna
GSMKlima1Rezim_delovanja | INT | IOD_GSM | GSM:.Klima[1].Rezim_delovanja
GSMKlima1Temperatura_dovoda | INT | IOD_GSM | GSM:.Klima[1].Temperatura_dovoda
GSMKlima1Temperatura_prostora | INT | IOD_GSM | GSM:.Klima[1].Temperatura_prostora
GSMKlima1TempPredPloscnimRekup | INT | IOD_GSM | GSM:.Klima[1].TempPredPloscnimRekup
GSMKlima1TempZaPloscnimRekup | INT | IOD_GSM | GSM:.Klima[1].TempZaPloscnimRekup
GSMKlima1VklopRegKlimata | DIGITAL | IOD_GSM | GSM:.Klima[1].VklopRegKlimata
GSMKlima1Vlaga_v_prostoru | INT | IOD_GSM | GSM:.Klima[1].Vlaga_v_prostoru
GSMKlima1VlagaVstopZrakaProstor | INT | IOD_GSM | GSM:.Klima[1].VlagaVstopZrakaProstor
GSMKlima1ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.Klima[1].ZamasenostFiltra
GSMKlima1ZdruzAlarmA | DIGITAL | IOD_GSM | GSM:.Klima[1].ZdruzAlarmA
GSMKlima1ZdruzAlarmB | DIGITAL | IOD_GSM | GSM:.Klima[1].ZdruzAlarmB
GSMKlima1Zel_temp_eko_gretja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_eko_gretja
GSMKlima1Zel_temp_eko_hlajenja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_eko_hlajenja
GSMKlima1Zel_temp_komf_gretja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_komf_gretja
GSMKlima1Zel_temp_komf_hlajenja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_komf_hlajenja
GSMKlima1Zim_komp_konec | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_konec
GSMKlima1Zim_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_sprem_zel_vr
GSMKlima1Zim_komp_zacetek | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_zacetek
GSMKlima1ZimKompMinVpihKonec | INT | IOD_GSM | GSM:.Klima[1].ZimKompMinVpihKonec
GSMKlima1ZimKompMinVpihZac | INT | IOD_GSM | GSM:.Klima[1].ZimKompMinVpihZac
GSMKlima1ZkompMinVpihSpremZelVr | INT | IOD_GSM | GSM:.Klima[1].ZkompMinVpihSpremZelVr
GSMKlima1Zunanja_temp | INT | IOD_GSM | GSM:.Klima[1].Zunanja_temp
GSMKlima2Alarm_pozar | DIGITAL | IOD_GSM | GSM:.Klima[2].Alarm_pozar
GSMKlima2Analog_izh_mesanje | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_mesanje
GSMKlima2Analog_izh_rekuperator | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_rekuperator
GSMKlima2Analog_izh_VentGrelnika | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_VentGrelnika
GSMKlima2Analog_izh_VentHlajenja | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_VentHlajenja
GSMKlima2Dejanska_zel_temp | INT | IOD_GSM | GSM:.Klima[2].Dejanska_zel_temp
GSMKlima2DelVentHit1 | DIGITAL | IOD_GSM | GSM:.Klima[2].DelVentHit1
GSMKlima2DelVentHit2 | DIGITAL | IOD_GSM | GSM:.Klima[2].DelVentHit2
GSMKlima2Hitrost_del_vent_disp | INT | IOD_GSM | GSM:.Klima[2].Hitrost_del_vent_disp
GSMKlima2Max_vpih | INT | IOD_GSM | GSM:.Klima[2].Max_vpih
GSMKlima2Min_vpih | INT | IOD_GSM | GSM:.Klima[2].Min_vpih
GSMKlima2Ni_pretoka | DIGITAL | IOD_GSM | GSM:.Klima[2].Ni_pretoka
GSMKlima2Obrat_ure_Vent_h1 | INT | IOD_GSM | GSM:.Klima[2].Obrat_ure_Vent_h1
GSMKlima2Obrat_ure_Vent_h2 | INT | IOD_GSM | GSM:.Klima[2].Obrat_ure_Vent_h2
GSMKlima2OkvaraRototerm | DIGITAL | IOD_GSM | GSM:.Klima[2].OkvaraRototerm
GSMKlima2OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.Klima[2].OkvaraVlazNap
GSMKlima2Pol_komp_konec | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_konec
GSMKlima2Pol_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_sprem_zel_vr
GSMKlima2Pol_komp_zacetek | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_zacetek
GSMKlima2PreklopHitDelVent | INT | IOD_GSM | GSM:.Klima[2].PreklopHitDelVent
GSMKlima2PreobMotCrpGrel | DIGITAL | IOD_GSM | GSM:.Klima[2].PreobMotCrpGrel
GSMKlima2PreobMotVent | DIGITAL | IOD_GSM | GSM:.Klima[2].PreobMotVent
GSMKlima2Protizamrz_zascita | INT | IOD_GSM | GSM:.Klima[2].Protizamrz_zascita
GSMKlima2ProtizamrzZascAktivna | DIGITAL | IOD_GSM | GSM:.Klima[2].ProtizamrzZascAktivna
GSMKlima2Rezim_delovanja | INT | IOD_GSM | GSM:.Klima[2].Rezim_delovanja
GSMKlima2Temperatura_dovoda | INT | IOD_GSM | GSM:.Klima[2].Temperatura_dovoda
GSMKlima2Temperatura_prostora | INT | IOD_GSM | GSM:.Klima[2].Temperatura_prostora
GSMKlima2TempPredPloscnimRekup | INT | IOD_GSM | GSM:.Klima[2].TempPredPloscnimRekup
GSMKlima2TempZaPloscnimRekup | INT | IOD_GSM | GSM:.Klima[2].TempZaPloscnimRekup
GSMKlima2VklopRegKlimata | DIGITAL | IOD_GSM | GSM:.Klima[2].VklopRegKlimata
GSMKlima2Vlaga_v_prostoru | INT | IOD_GSM | GSM:.Klima[2].Vlaga_v_prostoru
GSMKlima2VlagaVstopZrakaProstor | INT | IOD_GSM | GSM:.Klima[2].VlagaVstopZrakaProstor
GSMKlima2ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.Klima[2].ZamasenostFiltra
GSMKlima2ZdruzAlarmA | DIGITAL | IOD_GSM | GSM:.Klima[2].ZdruzAlarmA
GSMKlima2ZdruzAlarmB | DIGITAL | IOD_GSM | GSM:.Klima[2].ZdruzAlarmB
GSMKlima2Zel_temp_eko_gretja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_eko_gretja
GSMKlima2Zel_temp_eko_hlajenja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_eko_hlajenja
GSMKlima2Zel_temp_komf_gretja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_komf_gretja
GSMKlima2Zel_temp_komf_hlajenja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_komf_hlajenja
GSMKlima2Zim_komp_konec | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_konec
GSMKlima2Zim_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_sprem_zel_vr
GSMKlima2Zim_komp_zacetek | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_zacetek
GSMKlima2ZimKompMinVpihKonec | INT | IOD_GSM | GSM:.Klima[2].ZimKompMinVpihKonec
GSMKlima2ZimKompMinVpihZac | INT | IOD_GSM | GSM:.Klima[2].ZimKompMinVpihZac
GSMKlima2ZkompMinVpihSpremZelVr | INT | IOD_GSM | GSM:.Klima[2].ZkompMinVpihSpremZelVr
GSMKlima2Zunanja_temp | INT | IOD_GSM | GSM:.Klima[2].Zunanja_temp
GSMKLIMA_m1_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMA_m1_delovanje
GSMKLIMA_m1_napaka | DIGITAL | IOD_GSM | GSM:.KLIMA_m1_napaka
GSMKLIMA_m2_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMA_m2_delovanje
GSMKLIMA_m2_napaka | DIGITAL | IOD_GSM | GSM:.KLIMA_m2_napaka
GSMKlimaIzklopObrUre | INT | IOD_GSM | GSM:.KlimaIzklopObrUre
GSMKLIMAT1_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMAT1_delovanje
GSMKLIMAT1_napaka | DIGITAL | IOD_GSM | GSM:.KLIMAT1_napaka
GSMKLIMAT1_vklop_delovanja | DIGITAL | IOD_GSM | GSM:.KLIMAT1_vklop_delovanja
GSMKLIMAT2_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMAT2_delovanje
GSMKLIMAT2_napaka | DIGITAL | IOD_GSM | GSM:.KLIMAT2_napaka
GSMKLIMAT2_vklop_delovanja | DIGITAL | IOD_GSM | GSM:.KLIMAT2_vklop_delovanja
GSMKlimeAVTO | DIGITAL | IOD_GSM | GSM:.KlimeAVTO
GSMkom_nast_cas_izpada | UINT | IOD_GSM | GSM:.kom_nast_cas_izpada
GSMN_F1_1_zascita_ok | DIGITAL | IOD_GSM | GSM:.N_F1_1_zascita_ok
GSMN_KLIMA1_krm_nap_ok | DIGITAL | IOD_GSM | GSM:.N_KLIMA1_krm_nap_ok
GSMN_KLIMAT1_napaka | DIGITAL | IOD_GSM | GSM:.N_KLIMAT1_napaka
GSMN_KLIMAT2_napaka | DIGITAL | IOD_GSM | GSM:.N_KLIMAT2_napaka
GSMN_Q12_izpad | DIGITAL | IOD_GSM | GSM:.N_Q12_izpad
GSMN_UPS_A_V23_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_A_V23_delovanje
GSMN_UPS_A_V23_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_A_V23_napaka
GSMN_UPS_V23_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_V23_delovanje
GSMN_UPS_V23_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_V23_napaka
GSMN_UPS_V25_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_V25_delovanje
GSMN_UPS_V25_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_V25_napaka
GSMN_VLAZILEC1_napaka | DIGITAL | IOD_GSM | GSM:.N_VLAZILEC1_napaka
GSMN_VLAZILEC2_napaka | DIGITAL | IOD_GSM | GSM:.N_VLAZILEC2_napaka
GSMnapaka_kom_panel | DIGITAL | IOD_GSM | GSM:.napaka_kom_panel
GSMnapaka_kom_scada | DIGITAL | IOD_GSM | GSM:.napaka_kom_scada
GSMnapaka_kom_scada2 | DIGITAL | IOD_GSM | GSM:.napaka_kom_scada2
GSMNapakaSenzorSkupno | DIGITAL | IOD_GSM | GSM:.NapakaSenzorSkupno
GSMNapakaSenzorVlagaHIA1 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA1
GSMNapakaSenzorVlagaHIA2 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA2
GSMNapakaSenzorVlagaHIA3 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA3
GSMNapakaSenzorVlagaHIA4 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA4
GSMNapakaSenzorVlagaHIA5 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA5
GSMNapakaSenzorVlagaHIA6 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA6
GSMNapakaSenzorVlagaHIA7 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA7
GSMNapakaTSTempTIA1 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA1
GSMNapakaTSTempTIA2 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA2
GSMNapakaTSTempTIA3 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA3
GSMNapakaTSTempTIA4 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA4
GSMNapakaTSTempTIA5 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA5
GSMNapakaTSTempTIA6 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA6
GSMNapakaTSTempTIA7 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA7
GSMOpozoriloPMM2x17med60in8010 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[10]
GSMOpozoriloPMM2x17med60in8011 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[11]
GSMOpozoriloPMM2x17med60in8012 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[12]
GSMOpozoriloPMM2x17med60in8013 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[13]
GSMOpozoriloPMM2x17med60in8014 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[14]
GSMOpozoriloPMM2x17med60in8015 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[15]
GSMOpozoriloPMM2x17med60in8016 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[16]
GSMOpozoriloPMM2x17med60in8017 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[17]
GSMOpozoriloPMM2x17med60in8018 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[18]
GSMOpozoriloPMM2x17med60in8019 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[19]
GSMOpozoriloPMM2x17med60in801 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[1]
GSMOpozoriloPMM2x17med60in8020 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[20]
GSMOpozoriloPMM2x17med60in8021 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[21]
GSMOpozoriloPMM2x17med60in8022 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[22]
GSMOpozoriloPMM2x17med60in8023 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[23]
GSMOpozoriloPMM2x17med60in8024 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[24]
GSMOpozoriloPMM2x17med60in8025 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[25]
GSMOpozoriloPMM2x17med60in8026 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[26]
GSMOpozoriloPMM2x17med60in8027 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[27]
GSMOpozoriloPMM2x17med60in8028 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[28]
GSMOpozoriloPMM2x17med60in8029 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[29]
GSMOpozoriloPMM2x17med60in802 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[2]
GSMOpozoriloPMM2x17med60in8030 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[30]
GSMOpozoriloPMM2x17med60in8031 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[31]
GSMOpozoriloPMM2x17med60in8032 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[32]
GSMOpozoriloPMM2x17med60in8033 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[33]
GSMOpozoriloPMM2x17med60in8034 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[34]
GSMOpozoriloPMM2x17med60in8035 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[35]
GSMOpozoriloPMM2x17med60in8036 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[36]
GSMOpozoriloPMM2x17med60in8037 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[37]
GSMOpozoriloPMM2x17med60in8038 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[38]
GSMOpozoriloPMM2x17med60in8039 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[39]
GSMOpozoriloPMM2x17med60in803 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[3]
GSMOpozoriloPMM2x17med60in8040 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[40]
GSMOpozoriloPMM2x17med60in8041 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[41]
GSMOpozoriloPMM2x17med60in8042 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[42]
GSMOpozoriloPMM2x17med60in804 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[4]
GSMOpozoriloPMM2x17med60in805 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[5]
GSMOpozoriloPMM2x17med60in806 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[6]
GSMOpozoriloPMM2x17med60in807 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[7]
GSMOpozoriloPMM2x17med60in808 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[8]
GSMOpozoriloPMM2x17med60in809 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[9]
GSMPMM1OverCurrentBetw1 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[1]
GSMPMM1OverCurrentBetw2 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[2]
GSMPMM1OverCurrentBetw3 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[3]
GSMPMM1OverCurrentOver1 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[1]
GSMPMM1OverCurrentOver2 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[2]
GSMPMM1OverCurrentOver3 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[3]
GSMPMM1ActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM[1].ActiveEnergyConsumed_kWh
GSMPMM1ActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseA_kW
GSMPMM1ActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseB_kW
GSMPMM1ActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseC_kW
GSMPMM1AlarmPhase1C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C01_16_60to80
GSMPMM1AlarmPhase1C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C01_16_over80
GSMPMM1AlarmPhase1C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C17_32_60to80
GSMPMM1AlarmPhase1C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C17_32_over80
GSMPMM1AlarmPhase1C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C33_42_60to80
GSMPMM1AlarmPhase1C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C33_42_over80
GSMPMM1AlarmPhase1GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].GlobalAlarmReg
GSMPMM1AlarmPhase2C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C01_16_60to80
GSMPMM1AlarmPhase2C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C01_16_over80
GSMPMM1AlarmPhase2C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C17_32_60to80
GSMPMM1AlarmPhase2C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C17_32_over80
GSMPMM1AlarmPhase2C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C33_42_60to80
GSMPMM1AlarmPhase2C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C33_42_over80
GSMPMM1AlarmPhase2GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].GlobalAlarmReg
GSMPMM1AlarmPhase3C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C01_16_60to80
GSMPMM1AlarmPhase3C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C01_16_over80
GSMPMM1AlarmPhase3C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C17_32_60to80
GSMPMM1AlarmPhase3C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C17_32_over80
GSMPMM1AlarmPhase3C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C33_42_60to80
GSMPMM1AlarmPhase3C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C33_42_over80
GSMPMM1AlarmPhase3GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].GlobalAlarmReg
GSMPMM1AparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseA
GSMPMM1AparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseB
GSMPMM1AparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseC
GSMPMM1AverageCurrent_A | REAL | IOD_GSM | GSM:.PMM[1].AverageCurrent_A
GSMPMM1AveragePhaseToNeutral_V | REAL | IOD_GSM | GSM:.PMM[1].AveragePhaseToNeutral_V
GSMPMM1AveragePhaseToPhase_V | REAL | IOD_GSM | GSM:.PMM[1].AveragePhaseToPhase_V
GSMPMM1CurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseA_A
GSMPMM1CurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseB_A
GSMPMM1CurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseC_A
GSMPMM1Frequency_Hz | REAL | IOD_GSM | GSM:.PMM[1].Frequency_Hz
GSMPMM1Phase1Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[10]
GSMPMM1Phase1Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[11]
GSMPMM1Phase1Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[12]
GSMPMM1Phase1Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[13]
GSMPMM1Phase1Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[14]
GSMPMM1Phase1Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[15]
GSMPMM1Phase1Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[16]
GSMPMM1Phase1Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[17]
GSMPMM1Phase1Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[18]
GSMPMM1Phase1Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[19]
GSMPMM1Phase1Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[1]
GSMPMM1Phase1Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[20]
GSMPMM1Phase1Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[21]
GSMPMM1Phase1Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[22]
GSMPMM1Phase1Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[23]
GSMPMM1Phase1Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[24]
GSMPMM1Phase1Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[25]
GSMPMM1Phase1Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[26]
GSMPMM1Phase1Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[27]
GSMPMM1Phase1Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[28]
GSMPMM1Phase1Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[29]
GSMPMM1Phase1Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[2]
GSMPMM1Phase1Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[30]
GSMPMM1Phase1Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[31]
GSMPMM1Phase1Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[32]
GSMPMM1Phase1Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[33]
GSMPMM1Phase1Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[34]
GSMPMM1Phase1Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[35]
GSMPMM1Phase1Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[36]
GSMPMM1Phase1Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[37]
GSMPMM1Phase1Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[38]
GSMPMM1Phase1Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[39]
GSMPMM1Phase1Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[3]
GSMPMM1Phase1Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[40]
GSMPMM1Phase1Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[41]
GSMPMM1Phase1Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[42]
GSMPMM1Phase1Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[4]
GSMPMM1Phase1Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[5]
GSMPMM1Phase1Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[6]
GSMPMM1Phase1Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[7]
GSMPMM1Phase1Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[8]
GSMPMM1Phase1Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[9]
GSMPMM1Phase2Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[10]
GSMPMM1Phase2Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[11]
GSMPMM1Phase2Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[12]
GSMPMM1Phase2Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[13]
GSMPMM1Phase2Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[14]
GSMPMM1Phase2Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[15]
GSMPMM1Phase2Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[16]
GSMPMM1Phase2Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[17]
GSMPMM1Phase2Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[18]
GSMPMM1Phase2Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[19]
GSMPMM1Phase2Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[1]
GSMPMM1Phase2Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[20]
GSMPMM1Phase2Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[21]
GSMPMM1Phase2Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[22]
GSMPMM1Phase2Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[23]
GSMPMM1Phase2Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[24]
GSMPMM1Phase2Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[25]
GSMPMM1Phase2Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[26]
GSMPMM1Phase2Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[27]
GSMPMM1Phase2Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[28]
GSMPMM1Phase2Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[29]
GSMPMM1Phase2Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[2]
GSMPMM1Phase2Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[30]
GSMPMM1Phase2Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[31]
GSMPMM1Phase2Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[32]
GSMPMM1Phase2Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[33]
GSMPMM1Phase2Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[34]
GSMPMM1Phase2Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[35]
GSMPMM1Phase2Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[36]
GSMPMM1Phase2Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[37]
GSMPMM1Phase2Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[38]
GSMPMM1Phase2Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[39]
GSMPMM1Phase2Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[3]
GSMPMM1Phase2Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[40]
GSMPMM1Phase2Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[41]
GSMPMM1Phase2Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[42]
GSMPMM1Phase2Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[4]
GSMPMM1Phase2Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[5]
GSMPMM1Phase2Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[6]
GSMPMM1Phase2Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[7]
GSMPMM1Phase2Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[8]
GSMPMM1Phase2Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[9]
GSMPMM1Phase3Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[10]
GSMPMM1Phase3Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[11]
GSMPMM1Phase3Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[12]
GSMPMM1Phase3Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[13]
GSMPMM1Phase3Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[14]
GSMPMM1Phase3Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[15]
GSMPMM1Phase3Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[16]
GSMPMM1Phase3Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[17]
GSMPMM1Phase3Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[18]
GSMPMM1Phase3Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[19]
GSMPMM1Phase3Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[1]
GSMPMM1Phase3Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[20]
GSMPMM1Phase3Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[21]
GSMPMM1Phase3Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[22]
GSMPMM1Phase3Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[23]
GSMPMM1Phase3Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[24]
GSMPMM1Phase3Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[25]
GSMPMM1Phase3Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[26]
GSMPMM1Phase3Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[27]
GSMPMM1Phase3Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[28]
GSMPMM1Phase3Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[29]
GSMPMM1Phase3Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[2]
GSMPMM1Phase3Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[30]
GSMPMM1Phase3Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[31]
GSMPMM1Phase3Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[32]
GSMPMM1Phase3Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[33]
GSMPMM1Phase3Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[34]
GSMPMM1Phase3Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[35]
GSMPMM1Phase3Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[36]
GSMPMM1Phase3Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[37]
GSMPMM1Phase3Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[38]
GSMPMM1Phase3Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[39]
GSMPMM1Phase3Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[3]
GSMPMM1Phase3Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[40]
GSMPMM1Phase3Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[41]
GSMPMM1Phase3Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[42]
GSMPMM1Phase3Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[4]
GSMPMM1Phase3Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[5]
GSMPMM1Phase3Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[6]
GSMPMM1Phase3Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[7]
GSMPMM1Phase3Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[8]
GSMPMM1Phase3Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[9]
GSMPMM1PowerFactorSys | REAL | IOD_GSM | GSM:.PMM[1].PowerFactorSys
GSMPMM1ReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM[1].ReactiveEnergyConsumed_kVARh
GSMPMM1ReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseA
GSMPMM1ReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseB
GSMPMM1ReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseC
GSMPMM1TotalActivePower_kW | REAL | IOD_GSM | GSM:.PMM[1].TotalActivePower_kW
GSMPMM1TotalAparentPower_kVA | REAL | IOD_GSM | GSM:.PMM[1].TotalAparentPower_kVA
GSMPMM1TotalPowerFactor | REAL | IOD_GSM | GSM:.PMM[1].TotalPowerFactor
GSMPMM1TotalReactivePower_kVAR | REAL | IOD_GSM | GSM:.PMM[1].TotalReactivePower_kVAR
GSMPMM1VirA_fsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_fsys
GSMPMM1VirA_Isys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Isys
GSMPMM1VirA_PFsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_PFsys
GSMPMM1VirA_Psys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Psys
GSMPMM1VirA_Qsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Qsys
GSMPMM1VirA_Ssys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Ssys
GSMPMM1VirA_Usys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Usys
GSMPMM1VirB_fsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_fsys
GSMPMM1VirB_Isys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Isys
GSMPMM1VirB_PFsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_PFsys
GSMPMM1VirB_Psys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Psys
GSMPMM1VirB_Qsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Qsys
GSMPMM1VirB_Ssys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Ssys
GSMPMM1VirB_Usys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Usys
GSMPMM1VirBActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM[1].VirBActiveEnergyConsumed_kWh
GSMPMM1VirBActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseA_kW
GSMPMM1VirBActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseB_kW
GSMPMM1VirBActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseC_kW
GSMPMM1VirBAparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseA
GSMPMM1VirBAparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseB
GSMPMM1VirBAparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseC
GSMPMM1VirBAverageCurrent_A | REAL | IOD_GSM | GSM:.PMM[1].VirBAverageCurrent_A
GSMPMM1VirBAveragePhaseToNeutral_V | REAL | IOD_GSM | GSM:.PMM[1].VirBAveragePhaseToNeutral_V
GSMPMM1VirBAveragePhaseToPhase_V | REAL | IOD_GSM | GSM:.PMM[1].VirBAveragePhaseToPhase_V
GSMPMM1VirBCurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseA_A
GSMPMM1VirBCurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseB_A
GSMPMM1VirBCurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseC_A
GSMPMM1VirBFrequency_Hz | REAL | IOD_GSM | GSM:.PMM[1].VirBFrequency_Hz
GSMPMM1VirBPowerFactorSys | REAL | IOD_GSM | GSM:.PMM[1].VirBPowerFactorSys
GSMPMM1VirBReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM[1].VirBReactiveEnergyConsumed_kVARh
GSMPMM1VirBReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseA
GSMPMM1VirBReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseB
GSMPMM1VirBReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseC
GSMPMM1VirBTotalActivePower_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalActivePower_kW
GSMPMM1VirBTotalAparentPower_kVA | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalAparentPower_kVA
GSMPMM1VirBTotalPowerFactor | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalPowerFactor
GSMPMM1VirBTotalReactivePower_kVAR | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalReactivePower_kVAR
GSMPMM1VirBVoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseAB_V
GSMPMM1VirBVoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseAN_V
GSMPMM1VirBVoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseBC_V
GSMPMM1VirBVoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseBN_V
GSMPMM1VirBVoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseCA_V
GSMPMM1VirBVoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseCN_V
GSMPMM1VoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseAB_V
GSMPMM1VoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseAN_V
GSMPMM1VoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseBC_V
GSMPMM1VoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseBN_V
GSMPMM1VoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseCA_V
GSMPMM1VoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseCN_V
GSMPMMfaza01 | REAL | IOD_GSM | GSM:.PMMfaza01
GSMPMMfaza02 | REAL | IOD_GSM | GSM:.PMMfaza02
GSMPMMfaza03 | REAL | IOD_GSM | GSM:.PMMfaza03
GSMPMMfaza04 | REAL | IOD_GSM | GSM:.PMMfaza04
GSMPMMfaza05 | REAL | IOD_GSM | GSM:.PMMfaza05
GSMPMMfaza06 | REAL | IOD_GSM | GSM:.PMMfaza06
GSMPMMfaza07 | REAL | IOD_GSM | GSM:.PMMfaza07
GSMPMMfaza08 | REAL | IOD_GSM | GSM:.PMMfaza08
GSMPMMfaza09 | REAL | IOD_GSM | GSM:.PMMfaza09
GSMPMMfaza10 | REAL | IOD_GSM | GSM:.PMMfaza10
GSMPMMfaza11 | REAL | IOD_GSM | GSM:.PMMfaza11
GSMPMMfaza12 | REAL | IOD_GSM | GSM:.PMMfaza12
GSMPMMfaza13 | REAL | IOD_GSM | GSM:.PMMfaza13
GSMPMMfaza14 | REAL | IOD_GSM | GSM:.PMMfaza14
GSMPMMfaza15 | REAL | IOD_GSM | GSM:.PMMfaza15
GSMPMMfaza16 | REAL | IOD_GSM | GSM:.PMMfaza16
GSMPMMfaza17 | REAL | IOD_GSM | GSM:.PMMfaza17
GSMPMMfaza18 | REAL | IOD_GSM | GSM:.PMMfaza18
GSMPMMfaza19 | REAL | IOD_GSM | GSM:.PMMfaza19
GSMPMMfaza20 | REAL | IOD_GSM | GSM:.PMMfaza20
GSMPMMfaza21 | REAL | IOD_GSM | GSM:.PMMfaza21
GSMPMMfaza22 | REAL | IOD_GSM | GSM:.PMMfaza22
GSMPMMfaza23 | REAL | IOD_GSM | GSM:.PMMfaza23
GSMPMMfaza24 | REAL | IOD_GSM | GSM:.PMMfaza24
GSMPMMfaza25 | REAL | IOD_GSM | GSM:.PMMfaza25
GSMPMMfaza26 | REAL | IOD_GSM | GSM:.PMMfaza26
GSMPMMfaza27 | REAL | IOD_GSM | GSM:.PMMfaza27
GSMPMMfaza28 | REAL | IOD_GSM | GSM:.PMMfaza28
GSMPMMfaza29 | REAL | IOD_GSM | GSM:.PMMfaza29
GSMPMMfaza30 | REAL | IOD_GSM | GSM:.PMMfaza30
GSMPMMfaza31 | REAL | IOD_GSM | GSM:.PMMfaza31
GSMPMMfaza32 | REAL | IOD_GSM | GSM:.PMMfaza32
GSMPMMfaza33 | REAL | IOD_GSM | GSM:.PMMfaza33
GSMPMMfaza34 | REAL | IOD_GSM | GSM:.PMMfaza34
GSMPMMfaza35 | REAL | IOD_GSM | GSM:.PMMfaza35
GSMPMMfaza36 | REAL | IOD_GSM | GSM:.PMMfaza36
GSMPMMfaza37 | REAL | IOD_GSM | GSM:.PMMfaza37
GSMPMMfaza38 | REAL | IOD_GSM | GSM:.PMMfaza38
GSMPMMfaza39 | REAL | IOD_GSM | GSM:.PMMfaza39
GSMPMMfaza40 | REAL | IOD_GSM | GSM:.PMMfaza40
GSMPMMfaza41 | REAL | IOD_GSM | GSM:.PMMfaza41
GSMPMMfaza42 | REAL | IOD_GSM | GSM:.PMMfaza42
GSMPrevisokaTemp | DIGITAL | IOD_GSM | GSM:.PrevisokaTemp
GSMQ0_izkljuceno | DIGITAL | IOD_GSM | GSM:.Q0_izkljuceno
GSMQ0_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q0_vkljuceno
GSMQ12_izkljuceno | DIGITAL | IOD_GSM | GSM:.Q12_izkljuceno
GSMQ12_izpad | DIGITAL | IOD_GSM | GSM:.Q12_izpad
GSMQ12_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q12_vkljuceno
GSMQ12stanje | INT | IOD_GSM | GSM:.Q12stanje | BYTE
GSMrazlitjeLAH1 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH1
GSMrazlitjeLAH2 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH2
GSMrazlitjeLAH3 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH3
GSMrazlitjeLAH4 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH4
GSMSetDateTime | DIGITAL | IOD_GSM | GSM:.SetDateTime
GSMSetDateTimeDemand | DIGITAL | IOD_GSM | GSM:.SetDateTimeDemand
GSMSetDateTimeError | DIGITAL | IOD_GSM | GSM:.SetDateTimeError
GSMSetDateTimeFinished | DIGITAL | IOD_GSM | GSM:.SetDateTimeFinished
GSMSkupneNapakeNaprav_PMM17VirBVirA | DIGITAL | IOD_GSM | GSM:.SkupneNapakeNaprav_PMM17VirBVirA
GSMSlabaBaterijaPLC | DIGITAL | IOD_GSM | GSM:.SlabaBaterijaPLC
GSMTempHistereza | INT | IOD_GSM | GSM:.TempHistereza
GSMTempPovp234 | INT | IOD_GSM | GSM:.TempPovp234
GSMTempPovp234Alarm | INT | IOD_GSM | GSM:.TempPovp234Alarm
GSMTempPovp234Previs | DIGITAL | IOD_GSM | GSM:.TempPovp234Previs
GSMTempPovp56 | INT | IOD_GSM | GSM:.TempPovp56
GSMTempPovp56Alarm | INT | IOD_GSM | GSM:.TempPovp56Alarm
GSMTempPovp56Previs | DIGITAL | IOD_GSM | GSM:.TempPovp56Previs
GSMTempZaVklopKlim1 | INT | IOD_GSM | GSM:.TempZaVklopKlim1
GSMTempZaVklopKlim2 | INT | IOD_GSM | GSM:.TempZaVklopKlim2
GSMTIA1_alarm | INT | IOD_GSM | GSM:.TIA1_alarm
GSMTIA1_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA1_previs_temp
GSMTIA1_temp_s | INT | IOD_GSM | GSM:.TIA1_temp_s
GSMTIA2_alarm | INT | IOD_GSM | GSM:.TIA2_alarm
GSMTIA2_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA2_previs_temp
GSMTIA2_temp_s | INT | IOD_GSM | GSM:.TIA2_temp_s
GSMTIA3_alarm | INT | IOD_GSM | GSM:.TIA3_alarm
GSMTIA3_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA3_previs_temp
GSMTIA3_temp_s | INT | IOD_GSM | GSM:.TIA3_temp_s
GSMTIA4_alarm | INT | IOD_GSM | GSM:.TIA4_alarm
GSMTIA4_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA4_previs_temp
GSMTIA4_temp_s | INT | IOD_GSM | GSM:.TIA4_temp_s
GSMTIA5_alarm | INT | IOD_GSM | GSM:.TIA5_alarm
GSMTIA5_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA5_previs_temp
GSMTIA5_temp_s | INT | IOD_GSM | GSM:.TIA5_temp_s
GSMTIA6_alarm | INT | IOD_GSM | GSM:.TIA6_alarm
GSMTIA6_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA6_previs_temp
GSMTIA6_temp_s | INT | IOD_GSM | GSM:.TIA6_temp_s
GSMTIA7_alarm | INT | IOD_GSM | GSM:.TIA7_alarm
GSMTIA7_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA7_previs_temp
GSMTIA7_temp_s | INT | IOD_GSM | GSM:.TIA7_temp_s
GSMUPS1Errors10 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[10]
GSMUPS1Errors11 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[11]
GSMUPS1Errors12 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[12]
GSMUPS1Errors13 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[13]
GSMUPS1Errors14 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[14]
GSMUPS1Errors15 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[15]
GSMUPS1Errors16 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[16]
GSMUPS1Errors17 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[17]
GSMUPS1Errors18 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[18]
GSMUPS1Errors19 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[19]
GSMUPS1Errors1 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[1]
GSMUPS1Errors20 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[20]
GSMUPS1Errors21 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[21]
GSMUPS1Errors22 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[22]
GSMUPS1Errors23 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[23]
GSMUPS1Errors24 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[24]
GSMUPS1Errors25 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[25]
GSMUPS1Errors2 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[2]
GSMUPS1Errors3 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[3]
GSMUPS1Errors4 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[4]
GSMUPS1Errors5 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[5]
GSMUPS1Errors6 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[6]
GSMUPS1Errors7 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[7]
GSMUPS1Errors8 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[8]
GSMUPS1Errors9 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[9]
GSMUPS2Errors10 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[10]
GSMUPS2Errors11 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[11]
GSMUPS2Errors12 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[12]
GSMUPS2Errors13 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[13]
GSMUPS2Errors14 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[14]
GSMUPS2Errors15 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[15]
GSMUPS2Errors16 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[16]
GSMUPS2Errors17 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[17]
GSMUPS2Errors18 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[18]
GSMUPS2Errors19 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[19]
GSMUPS2Errors1 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[1]
GSMUPS2Errors20 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[20]
GSMUPS2Errors21 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[21]
GSMUPS2Errors22 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[22]
GSMUPS2Errors23 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[23]
GSMUPS2Errors24 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[24]
GSMUPS2Errors25 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[25]
GSMUPS2Errors2 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[2]
GSMUPS2Errors3 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[3]
GSMUPS2Errors4 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[4]
GSMUPS2Errors5 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[5]
GSMUPS2Errors6 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[6]
GSMUPS2Errors7 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[7]
GSMUPS2Errors8 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[8]
GSMUPS2Errors9 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[9]
GSMUPS1AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmAwaitingPower
GSMUPS1AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmBypassBad
GSMUPS1AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmChargerFailed
GSMUPS1AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmCommunicationsLost
GSMUPS1AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmDepletedBattery
GSMUPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmDiagnosticTestFailed
GSMUPS1AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmInverterError
GSMUPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmIzhodOffKotZahtevano
GSMUPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmIzhodPreobremenjen
GSMUPS1AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmLowBattery
GSMUPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmNapakaNaVarovalki
GSMUPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmNapakaNaVentilatorju
GSMUPS1AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmOnBattery
GSMUPS1AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmOnBypass
GSMUPS1AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmShutdownImminent
GSMUPS1AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmShutdownPending
GSMUPS1AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmSlabaBaterija
GSMUPS1AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmSplosnaNapaka
GSMUPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmStanjeIzhodaIzvenToleranc
GSMUPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmStanjeVhodaIzvenToleranc
GSMUPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmTemperaturaIzvenToleranc
GSMUPS1AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmTestInProgres
GSMUPS1AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSIzhodOff
GSMUPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSOffKotZahtevano
GSMUPS1AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSSystemOff
GSMUPS1EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[1].EstimatedChargeRemaining
GSMUPS1EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[1].EstimatedMinutesRemaining
GSMUPS1InverterStatus | INT | IOD_GSM | GSM:.UPS[1].InverterStatus
GSMUPS1IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL1
GSMUPS1IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL2
GSMUPS1IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL3
GSMUPS1Napaka | DIGITAL | IOD_GSM | GSM:.UPS[1].Napaka
GSMUPS1NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[1].NapetostBaterije
GSMUPS1OutputStatus | INT | IOD_GSM | GSM:.UPS[1].OutputStatus
GSMUPS1StatusBaterije | UINT | IOD_GSM | GSM:.UPS[1].StatusBaterije
GSMUPS1StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusEcomodeAktiven
GSMUPS1StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusInverterIsOn
GSMUPS1StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusStopOperation
GSMUPS1SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[1].SteviloIzpadovVhodneLinije
GSMUPS1TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[1].TemperaturaBaterije
GSMUPS1UnitStatus | INT | IOD_GSM | GSM:.UPS[1].UnitStatus
GSMUPS1VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL1
GSMUPS1VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL2
GSMUPS1VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL3
GSMUPS1VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL1
GSMUPS1VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL2
GSMUPS1VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL3
GSMUPS2AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmAwaitingPower
GSMUPS2AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmBypassBad
GSMUPS2AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmChargerFailed
GSMUPS2AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmCommunicationsLost
GSMUPS2AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmDepletedBattery
GSMUPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmDiagnosticTestFailed
GSMUPS2AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmInverterError
GSMUPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmIzhodOffKotZahtevano
GSMUPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmIzhodPreobremenjen
GSMUPS2AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmLowBattery
GSMUPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmNapakaNaVarovalki
GSMUPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmNapakaNaVentilatorju
GSMUPS2AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmOnBattery
GSMUPS2AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmOnBypass
GSMUPS2AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmShutdownImminent
GSMUPS2AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmShutdownPending
GSMUPS2AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmSlabaBaterija
GSMUPS2AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmSplosnaNapaka
GSMUPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmStanjeIzhodaIzvenToleranc
GSMUPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmStanjeVhodaIzvenToleranc
GSMUPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmTemperaturaIzvenToleranc
GSMUPS2AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmTestInProgres
GSMUPS2AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSIzhodOff
GSMUPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSOffKotZahtevano
GSMUPS2AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSSystemOff
GSMUPS2EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[2].EstimatedChargeRemaining
GSMUPS2EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[2].EstimatedMinutesRemaining
GSMUPS2InverterStatus | INT | IOD_GSM | GSM:.UPS[2].InverterStatus
GSMUPS2IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL1
GSMUPS2IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL2
GSMUPS2IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL3
GSMUPS2Napaka | DIGITAL | IOD_GSM | GSM:.UPS[2].Napaka
GSMUPS2NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[2].NapetostBaterije
GSMUPS2OutputStatus | INT | IOD_GSM | GSM:.UPS[2].OutputStatus
GSMUPS2StatusBaterije | UINT | IOD_GSM | GSM:.UPS[2].StatusBaterije
GSMUPS2StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusEcomodeAktiven
GSMUPS2StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusInverterIsOn
GSMUPS2StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusStopOperation
GSMUPS2SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[2].SteviloIzpadovVhodneLinije
GSMUPS2TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[2].TemperaturaBaterije
GSMUPS2UnitStatus | INT | IOD_GSM | GSM:.UPS[2].UnitStatus
GSMUPS2VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL1
GSMUPS2VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL2
GSMUPS2VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL3
GSMUPS2VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL1
GSMUPS2VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL2
GSMUPS2VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL3
GSMUPS_A_V23_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_A_V23_delovanje
GSMUPS_A_V23_napaka | DIGITAL | IOD_GSM | GSM:.UPS_A_V23_napaka
GSMups_alarm | DIGITAL | IOD_GSM | GSM:.ups_alarm
GSMups_baterijski_nac | DIGITAL | IOD_GSM | GSM:.ups_baterijski_nac
GSMUPS_MGE1BatteryBackupTime | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryBackupTime
GSMUPS_MGE1BatteryChargedState | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryChargedState
GSMUPS_MGE1BatteryChargingLevel | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryChargingLevel
GSMUPS_MGE1BatteryCircuitBreaker | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryCircuitBreaker
GSMUPS_MGE1BatteryCompInProgress | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryCompInProgress
GSMUPS_MGE1BatteryFuseFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryFuseFault
GSMUPS_MGE1BatteryLowWarning | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryLowWarning
GSMUPS_MGE1BatteryRechargeDuration | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryRechargeDuration
GSMUPS_MGE1BatteryTempOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryTempOutOfToler
GSMUPS_MGE1BypassInFreeFrequency | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BypassInFreeFrequency
GSMUPS_MGE1ChargerGeneralFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].ChargerGeneralFault
GSMUPS_MGE1DeviceVentilationFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].DeviceVentilationFault
GSMUPS_MGE1I1output | INT | IOD_GSM | GSM:.UPS_MGE[1].I1output
GSMUPS_MGE1I2output | INT | IOD_GSM | GSM:.UPS_MGE[1].I2output
GSMUPS_MGE1I3output | INT | IOD_GSM | GSM:.UPS_MGE[1].I3output
GSMUPS_MGE1InverterFrequency | INT | IOD_GSM | GSM:.UPS_MGE[1].InverterFrequency
GSMUPS_MGE1InverterFuseFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterFuseFault
GSMUPS_MGE1InverterOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterOverload
GSMUPS_MGE1InverterThermalOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterThermalOverload
GSMUPS_MGE1Mains1VoltOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains1VoltOutOfToler
GSMUPS_MGE1Mains2Overload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains2Overload
GSMUPS_MGE1Mains2VoltOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains2VoltOutOfToler
GSMUPS_MGE1MaintenancePosition | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].MaintenancePosition
GSMUPS_MGE1ManualBypassSwitch | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].ManualBypassSwitch
GSMUPS_MGE1NapakaNaVarovalkah | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].NapakaNaVarovalkah
GSMUPS_MGE1OutputActivePower1 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower1
GSMUPS_MGE1OutputActivePower2 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower2
GSMUPS_MGE1OutputActivePower3 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower3
GSMUPS_MGE1OutputFrequency | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputFrequency
GSMUPS_MGE1OutputInShortCircuit | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputInShortCircuit
GSMUPS_MGE1OutputLoadLevel | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputLoadLevel
GSMUPS_MGE1OutputOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputOverload
GSMUPS_MGE1OutputThermalOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputThermalOverload
GSMUPS_MGE1RectifierOn | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].RectifierOn
GSMUPS_MGE1RectifierThermOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].RectifierThermOverload
GSMUPS_MGE1Skupna_napaka | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Skupna_napaka
GSMUPS_MGE1StatusBaterije | INT | IOD_GSM | GSM:.UPS_MGE[1].StatusBaterije | BYTE
GSMUPS_MGE1U12mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U12mains1
GSMUPS_MGE1U12mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U12mains2
GSMUPS_MGE1U1N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U1N_inverter
GSMUPS_MGE1U1N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U1N_output
GSMUPS_MGE1U23mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U23mains1
GSMUPS_MGE1U23mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U23mains2
GSMUPS_MGE1U2N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U2N_inverter
GSMUPS_MGE1U2N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U2N_output
GSMUPS_MGE1U31mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U31mains1
GSMUPS_MGE1U31mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U31mains2
GSMUPS_MGE1U3N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U3N_inverter
GSMUPS_MGE1U3N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U3N_output
GSMUPS_MGE1U_battery | INT | IOD_GSM | GSM:.UPS_MGE[1].U_battery
GSMUPS_MGE1UPS_coupled | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_coupled
GSMUPS_MGE1UPS_error | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_error
GSMUPS_MGE1UPS_in_backup | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_in_backup
GSMups_polnjenje | DIGITAL | IOD_GSM | GSM:.ups_polnjenje
GSMUPS_V23_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_V23_delovanje
GSMUPS_V23_napaka | DIGITAL | IOD_GSM | GSM:.UPS_V23_napaka
GSMUPS_V25_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_V25_delovanje
GSMUPS_V25_napaka | DIGITAL | IOD_GSM | GSM:.UPS_V25_napaka
GSMUPSMGEErrors10 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[10]
GSMUPSMGEErrors11 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[11]
GSMUPSMGEErrors12 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[12]
GSMUPSMGEErrors13 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[13]
GSMUPSMGEErrors14 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[14]
GSMUPSMGEErrors15 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[15]
GSMUPSMGEErrors16 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[16]
GSMUPSMGEErrors17 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[17]
GSMUPSMGEErrors1 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[1]
GSMUPSMGEErrors2 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[2]
GSMUPSMGEErrors3 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[3]
GSMUPSMGEErrors4 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[4]
GSMUPSMGEErrors5 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[5]
GSMUPSMGEErrors6 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[6]
GSMUPSMGEErrors7 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[7]
GSMUPSMGEErrors8 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[8]
GSMUPSMGEErrors9 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[9]
GSMUserCurrentLevel | INT | IOD_GSM | GSM:.UserCurrentLevel | BYTE
GSMUserCurrentName | STRING | IOD_GSM | GSM:.UserCurrentName
GSMUserLoggedIn | DIGITAL | IOD_GSM | GSM:.UserLoggedIn
GSMVLAZILEC1_delovanje | DIGITAL | IOD_GSM | GSM:.VLAZILEC1_delovanje
GSMVLAZILEC1_napaka | DIGITAL | IOD_GSM | GSM:.VLAZILEC1_napaka
GSMVLAZILEC2_delovanje | DIGITAL | IOD_GSM | GSM:.VLAZILEC2_delovanje
GSMVLAZILEC2_napaka | DIGITAL | IOD_GSM | GSM:.VLAZILEC2_napaka
GSMXVH_AlarmOn | DIGITAL | IOD_GSM | GSM:.XVH_AlarmOn
GSMXVH_enopolna_napaka | DIGITAL | IOD_GSM | GSM:.XVH_enopolna_napaka
GSMXVH_UPSstatus | INT | IOD_GSM | GSM:.XVH_UPSstatus | BYTE
GSMXVHdepltedBatery1 | REAL | IOD_GSM | GSM:.XVHdepltedBatery1
GSMXVHdepltedBatery2 | REAL | IOD_GSM | GSM:.XVHdepltedBatery2
GSMXVHlowBatery1 | REAL | IOD_GSM | GSM:.XVHlowBatery1
GSMXVHlowBatery2 | REAL | IOD_GSM | GSM:.XVHlowBatery2
GSMKLIMAT1_vklop_delovanjaR | DIGITAL | IOD_GSM | GSM:.KLIMAT1_vklop_delovanjaR
GSMKLIMAT2_vklop_delovanjaR | DIGITAL | IOD_GSM | GSM:.KLIMAT2_vklop_delovanjaR
GSMKLIMAT1_R_zakleni | DIGITAL | IOD_GSM | GSM:.KLIMAT1_R_zakleni
GSMKLIMAT2_R_zakleni | DIGITAL | IOD_GSM | GSM:.KLIMAT2_R_zakleni
GSMK1_vklop_izklop_poteka | DIGITAL | IOD_GSM | GSM:.K1_vklop_izklop_poteka
GSMK2_vklop_izklop_poteka | DIGITAL | IOD_GSM | GSM:.K2_vklop_izklop_poteka
GSMPMMskupniTokA | REAL | IOD_GSM | GSM:.PMMskupniTokA
GSMPMMskupniTokB | REAL | IOD_GSM | GSM:.PMMskupniTokB
GSMN_KlimeAVTO | DIGITAL | IOD_GSM | GSM:.N_KlimeAVTO
GSMK1_obr_u_skupno | UINT | IOD_GSM | GSM:.K1_obr_u_skupno
GSMK2_obr_u_skupno | UINT | IOD_GSM | GSM:.K2_obr_u_skupno
GSMUPS3AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmAwaitingPower
GSMUPS3AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmBypassBad
GSMUPS3AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmChargerFailed
GSMUPS3AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmCommunicationsLost
GSMUPS3AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmDepletedBattery
GSMUPS3AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmDiagnosticTestFailed
GSMUPS3AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmInverterError
GSMUPS3AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmIzhodOffKotZahtevano
GSMUPS3AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmIzhodPreobremenjen
GSMUPS3AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmLowBattery
GSMUPS3AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmNapakaNaVarovalki
GSMUPS3AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmNapakaNaVentilatorju
GSMUPS3AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmOnBattery
GSMUPS3AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmOnBypass
GSMUPS3AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmShutdownImminent
GSMUPS3AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmShutdownPending
GSMUPS3AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmSlabaBaterija
GSMUPS3AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmSplosnaNapaka
GSMUPS3AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmStanjeIzhodaIzvenToleranc
GSMUPS3AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmStanjeVhodaIzvenToleranc
GSMUPS3AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmTemperaturaIzvenToleranc
GSMUPS3AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmTestInProgres
GSMUPS3AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSIzhodOff
GSMUPS3AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSOffKotZahtevano
GSMUPS3AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSSystemOff
GSMUPS3EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[3].EstimatedChargeRemaining
GSMUPS3EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[3].EstimatedMinutesRemaining
GSMUPS3InverterStatus | INT | IOD_GSM | GSM:.UPS[3].InverterStatus
GSMUPS3IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL1
GSMUPS3IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL2
GSMUPS3IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL3
GSMUPS3Napaka | DIGITAL | IOD_GSM | GSM:.UPS[3].Napaka
GSMUPS3NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[3].NapetostBaterije
GSMUPS3OutputStatus | INT | IOD_GSM | GSM:.UPS[3].OutputStatus
GSMUPS3StatusBaterije | UINT | IOD_GSM | GSM:.UPS[3].StatusBaterije
GSMUPS3StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusEcomodeAktiven
GSMUPS3StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusInverterIsOn
GSMUPS3StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusStopOperation
GSMUPS3SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[3].SteviloIzpadovVhodneLinije
GSMUPS3TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[3].TemperaturaBaterije
GSMUPS3UnitStatus | INT | IOD_GSM | GSM:.UPS[3].UnitStatus
GSMUPS3VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL1
GSMUPS3VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL2
GSMUPS3VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL3
GSMUPS3VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL1
GSMUPS3VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL2
GSMUPS3VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL3
GSMErrComUPS3 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[3]
GSMGSM_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.GSM_PozCent_napaka
GSMGSM_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.GSM_PozSenzor_okvara
GSMGSM_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.GSM_Gasenje_alarm
GSMAGR_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.AGR_PozCent_napaka
GSMAGR_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.AGR_PozSenzor_okvara
GSMAGR_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.AGR_Gasenje_alarm
GSMCirc1MaximumDemandA2 | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemandA2
GSMCirc1MaximumDemandA3 | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemandA3
GSMCirc1RazEner_D_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_D_SCADA
GSMCirc1RazEner_T_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_T_SCADA
GSMCirc1RazEner_M_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_M_SCADA
GSMCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Dnevne_energija_scada1
GSMCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Dnevne_energija_scada2
GSMCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Tedenska_energija_scada1
GSMCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Tedenska_energija_scada2
GSMCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Mesecna_energija_scada1
GSMCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Mesecna_energija_scada2
GSMPozarnaCentrala_skupno | DIGITAL | IOD_GSM | GSM:.PozarnaCentrala_skupno

## variable_2
GSMAlarmGenUPS_A_V23 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_A_V23
GSMAlarmGenUPS_V23 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_V23
GSMAlarmGenUPS_V25 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_V25
GSMAlarmPMM1VirATokPrevisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirATokPrevisok
GSMAlarmPMM1VirATokVisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirATokVisok
GSMAlarmPMM1VirBTokPrevisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirBTokPrevisok
GSMAlarmPMM1VirBTokVisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirBTokVisok
GSMAlarmPMM2x17nad8010 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[10]
GSMAlarmPMM2x17nad8011 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[11]
GSMAlarmPMM2x17nad8012 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[12]
GSMAlarmPMM2x17nad8013 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[13]
GSMAlarmPMM2x17nad8014 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[14]
GSMAlarmPMM2x17nad8015 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[15]
GSMAlarmPMM2x17nad8016 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[16]
GSMAlarmPMM2x17nad8017 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[17]
GSMAlarmPMM2x17nad8018 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[18]
GSMAlarmPMM2x17nad8019 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[19]
GSMAlarmPMM2x17nad801 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[1]
GSMAlarmPMM2x17nad8020 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[20]
GSMAlarmPMM2x17nad8021 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[21]
GSMAlarmPMM2x17nad8022 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[22]
GSMAlarmPMM2x17nad8023 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[23]
GSMAlarmPMM2x17nad8024 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[24]
GSMAlarmPMM2x17nad8025 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[25]
GSMAlarmPMM2x17nad8026 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[26]
GSMAlarmPMM2x17nad8027 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[27]
GSMAlarmPMM2x17nad8028 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[28]
GSMAlarmPMM2x17nad8029 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[29]
GSMAlarmPMM2x17nad802 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[2]
GSMAlarmPMM2x17nad8030 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[30]
GSMAlarmPMM2x17nad8031 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[31]
GSMAlarmPMM2x17nad8032 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[32]
GSMAlarmPMM2x17nad8033 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[33]
GSMAlarmPMM2x17nad8034 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[34]
GSMAlarmPMM2x17nad8035 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[35]
GSMAlarmPMM2x17nad8036 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[36]
GSMAlarmPMM2x17nad8037 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[37]
GSMAlarmPMM2x17nad8038 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[38]
GSMAlarmPMM2x17nad8039 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[39]
GSMAlarmPMM2x17nad803 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[3]
GSMAlarmPMM2x17nad8040 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[40]
GSMAlarmPMM2x17nad8041 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[41]
GSMAlarmPMM2x17nad8042 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[42]
GSMAlarmPMM2x17nad804 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[4]
GSMAlarmPMM2x17nad805 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[5]
GSMAlarmPMM2x17nad806 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[6]
GSMAlarmPMM2x17nad807 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[7]
GSMAlarmPMM2x17nad808 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[8]
GSMAlarmPMM2x17nad809 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[9]
GSMComError | DIGITAL | IOD_GSM | GSM:.ComError
GSMComSCADA | DIGITAL | IOD_GSM | GSM:.ComSCADA
GSMComSCADA1 | DIGITAL | IOD_GSM | GSM:.ComSCADA1
GSMComSCADA2 | DIGITAL | IOD_GSM | GSM:.ComSCADA2
GSMComSCADA3 | DIGITAL | IOD_GSM | GSM:.ComSCADA3
GSMErrComCirc1 | DIGITAL | IOD_GSM | GSM:.ErrComCirc[1]
GSMErrComKlima1 | DIGITAL | IOD_GSM | GSM:.ErrComKlima[1]
GSMErrComKlima2 | DIGITAL | IOD_GSM | GSM:.ErrComKlima[2]
GSMErrComPMM1 | DIGITAL | IOD_GSM | GSM:.ErrComPMM[1]
GSMErrComPort2 | DIGITAL | IOD_GSM | GSM:.ErrComPort2
GSMErrComPort3 | DIGITAL | IOD_GSM | GSM:.ErrComPort3
GSMErrComPort4 | DIGITAL | IOD_GSM | GSM:.ErrComPort4
GSMErrComUPS1 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[1]
GSMErrComUPS2 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[2]
GSMErrComUPSMGE1 | DIGITAL | IOD_GSM | GSM:.ErrComUPSMGE[1]
GSMErrorComCirc1Error | DIGITAL | IOD_GSM | GSM:.ErrorComCirc[1].Error
GSMErrorComKlima1Error | DIGITAL | IOD_GSM | GSM:.ErrorComKlima[1].Error
GSMErrorComKlima2Error | DIGITAL | IOD_GSM | GSM:.ErrorComKlima[2].Error
GSMErrorComPMM1Error | DIGITAL | IOD_GSM | GSM:.ErrorComPMM[1].Error
GSMErrorComUPS1Error | DIGITAL | IOD_GSM | GSM:.ErrorComUPS[1].Error
GSMErrorComUPS2Error | DIGITAL | IOD_GSM | GSM:.ErrorComUPS[2].Error
GSMErrorComUPSMGE1Error | DIGITAL | IOD_GSM | GSM:.ErrorComUPSMGE[1].Error
GSMF1_1_zascita_ok | DIGITAL | IOD_GSM | GSM:.F1_1_zascita_ok
GSMK1_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K1_SkupnaNapaka
GSMK1AlarmPozara | DIGITAL | IOD_GSM | GSM:.K1AlarmPozara
GSMK1KlimaZdruzenAlarm | DIGITAL | IOD_GSM | GSM:.K1KlimaZdruzenAlarm
GSMK1NiPretoka | DIGITAL | IOD_GSM | GSM:.K1NiPretoka
GSMK1OkvaraRototerma | DIGITAL | IOD_GSM | GSM:.K1OkvaraRototerma
GSMK1OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.K1OkvaraVlazNap
GSMK1PreobMotCrpGr | DIGITAL | IOD_GSM | GSM:.K1PreobMotCrpGr
GSMK1PreobMotVent | DIGITAL | IOD_GSM | GSM:.K1PreobMotVent
GSMK1ProtizamrzZascAkt | DIGITAL | IOD_GSM | GSM:.K1ProtizamrzZascAkt
GSMK1ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.K1ZamasenostFiltra
GSMK2_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K2_SkupnaNapaka
GSMK2AlarmPozara | DIGITAL | IOD_GSM | GSM:.K2AlarmPozara
GSMK2KlimaZdruzenAlarm | DIGITAL | IOD_GSM | GSM:.K2KlimaZdruzenAlarm
GSMK2NiPretoka | DIGITAL | IOD_GSM | GSM:.K2NiPretoka
GSMK2OkvaraRototerma | DIGITAL | IOD_GSM | GSM:.K2OkvaraRototerma
GSMK2OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.K2OkvaraVlazNap
GSMK2PreobMotCrpGr | DIGITAL | IOD_GSM | GSM:.K2PreobMotCrpGr
GSMK2PreobMotVent | DIGITAL | IOD_GSM | GSM:.K2PreobMotVent
GSMK2ProtizamrzZascAkt | DIGITAL | IOD_GSM | GSM:.K2ProtizamrzZascAkt
GSMK2ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.K2ZamasenostFiltra
GSMK3_deluje | DIGITAL | IOD_GSM | GSM:.K3_deluje
GSMK3_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K3_SkupnaNapaka
GSMKlima1_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima1_izkljucena
GSMKLIMA1_kke_pogon | DIGITAL | IOD_GSM | GSM:.KLIMA1_kke_pogon
GSMKLIMA1_krm_nap_ok | DIGITAL | IOD_GSM | GSM:.KLIMA1_krm_nap_ok
GSMKlima2_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima2_izkljucena
GSMKlima3_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima3_izkljucena
GSMKlima1Alarm_pozar | DIGITAL | IOD_GSM | GSM:.Klima[1].Alarm_pozar
GSMKlima1DelVentHit1 | DIGITAL | IOD_GSM | GSM:.Klima[1].DelVentHit1
GSMKlima1DelVentHit2 | DIGITAL | IOD_GSM | GSM:.Klima[1].DelVentHit2
GSMKlima1Ni_pretoka | DIGITAL | IOD_GSM | GSM:.Klima[1].Ni_pretoka
GSMKlima1OkvaraRototerm | DIGITAL | IOD_GSM | GSM:.Klima[1].OkvaraRototerm
GSMKlima1OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.Klima[1].OkvaraVlazNap
GSMKlima1PreobMotCrpGrel | DIGITAL | IOD_GSM | GSM:.Klima[1].PreobMotCrpGrel
GSMKlima1PreobMotVent | DIGITAL | IOD_GSM | GSM:.Klima[1].PreobMotVent
GSMKlima1ProtizamrzZascAktivna | DIGITAL | IOD_GSM | GSM:.Klima[1].ProtizamrzZascAktivna
GSMKlima1VklopRegKlimata | DIGITAL | IOD_GSM | GSM:.Klima[1].VklopRegKlimata
GSMKlima1ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.Klima[1].ZamasenostFiltra
GSMKlima1ZdruzAlarmA | DIGITAL | IOD_GSM | GSM:.Klima[1].ZdruzAlarmA
GSMKlima1ZdruzAlarmB | DIGITAL | IOD_GSM | GSM:.Klima[1].ZdruzAlarmB
GSMKlima2Alarm_pozar | DIGITAL | IOD_GSM | GSM:.Klima[2].Alarm_pozar
GSMKlima2DelVentHit1 | DIGITAL | IOD_GSM | GSM:.Klima[2].DelVentHit1
GSMKlima2DelVentHit2 | DIGITAL | IOD_GSM | GSM:.Klima[2].DelVentHit2
GSMKlima2Ni_pretoka | DIGITAL | IOD_GSM | GSM:.Klima[2].Ni_pretoka
GSMKlima2OkvaraRototerm | DIGITAL | IOD_GSM | GSM:.Klima[2].OkvaraRototerm
GSMKlima2OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.Klima[2].OkvaraVlazNap
GSMKlima2PreobMotCrpGrel | DIGITAL | IOD_GSM | GSM:.Klima[2].PreobMotCrpGrel
GSMKlima2PreobMotVent | DIGITAL | IOD_GSM | GSM:.Klima[2].PreobMotVent
GSMKlima2ProtizamrzZascAktivna | DIGITAL | IOD_GSM | GSM:.Klima[2].ProtizamrzZascAktivna
GSMKlima2VklopRegKlimata | DIGITAL | IOD_GSM | GSM:.Klima[2].VklopRegKlimata
GSMKlima2ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.Klima[2].ZamasenostFiltra
GSMKlima2ZdruzAlarmA | DIGITAL | IOD_GSM | GSM:.Klima[2].ZdruzAlarmA
GSMKlima2ZdruzAlarmB | DIGITAL | IOD_GSM | GSM:.Klima[2].ZdruzAlarmB
GSMKLIMA_m1_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMA_m1_delovanje
GSMKLIMA_m1_napaka | DIGITAL | IOD_GSM | GSM:.KLIMA_m1_napaka
GSMKLIMA_m2_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMA_m2_delovanje
GSMKLIMA_m2_napaka | DIGITAL | IOD_GSM | GSM:.KLIMA_m2_napaka
GSMKLIMAT1_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMAT1_delovanje
GSMKLIMAT1_napaka | DIGITAL | IOD_GSM | GSM:.KLIMAT1_napaka
GSMKLIMAT1_vklop_delovanja | DIGITAL | IOD_GSM | GSM:.KLIMAT1_vklop_delovanja
GSMKLIMAT2_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMAT2_delovanje
GSMKLIMAT2_napaka | DIGITAL | IOD_GSM | GSM:.KLIMAT2_napaka
GSMKLIMAT2_vklop_delovanja | DIGITAL | IOD_GSM | GSM:.KLIMAT2_vklop_delovanja
GSMKlimeAVTO | DIGITAL | IOD_GSM | GSM:.KlimeAVTO
GSMN_F1_1_zascita_ok | DIGITAL | IOD_GSM | GSM:.N_F1_1_zascita_ok
GSMN_KLIMA1_krm_nap_ok | DIGITAL | IOD_GSM | GSM:.N_KLIMA1_krm_nap_ok
GSMN_KLIMAT1_napaka | DIGITAL | IOD_GSM | GSM:.N_KLIMAT1_napaka
GSMN_KLIMAT2_napaka | DIGITAL | IOD_GSM | GSM:.N_KLIMAT2_napaka
GSMN_Q12_izpad | DIGITAL | IOD_GSM | GSM:.N_Q12_izpad
GSMN_UPS_A_V23_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_A_V23_delovanje
GSMN_UPS_A_V23_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_A_V23_napaka
GSMN_UPS_V23_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_V23_delovanje
GSMN_UPS_V23_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_V23_napaka
GSMN_UPS_V25_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_V25_delovanje
GSMN_UPS_V25_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_V25_napaka
GSMN_VLAZILEC1_napaka | DIGITAL | IOD_GSM | GSM:.N_VLAZILEC1_napaka
GSMN_VLAZILEC2_napaka | DIGITAL | IOD_GSM | GSM:.N_VLAZILEC2_napaka
GSMnapaka_kom_panel | DIGITAL | IOD_GSM | GSM:.napaka_kom_panel
GSMnapaka_kom_scada | DIGITAL | IOD_GSM | GSM:.napaka_kom_scada
GSMnapaka_kom_scada2 | DIGITAL | IOD_GSM | GSM:.napaka_kom_scada2
GSMNapakaSenzorSkupno | DIGITAL | IOD_GSM | GSM:.NapakaSenzorSkupno
GSMNapakaSenzorVlagaHIA1 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA1
GSMNapakaSenzorVlagaHIA2 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA2
GSMNapakaSenzorVlagaHIA3 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA3
GSMNapakaSenzorVlagaHIA4 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA4
GSMNapakaSenzorVlagaHIA5 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA5
GSMNapakaSenzorVlagaHIA6 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA6
GSMNapakaSenzorVlagaHIA7 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA7
GSMNapakaTSTempTIA1 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA1
GSMNapakaTSTempTIA2 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA2
GSMNapakaTSTempTIA3 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA3
GSMNapakaTSTempTIA4 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA4
GSMNapakaTSTempTIA5 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA5
GSMNapakaTSTempTIA6 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA6
GSMNapakaTSTempTIA7 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA7
GSMOpozoriloPMM2x17med60in8010 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[10]
GSMOpozoriloPMM2x17med60in8011 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[11]
GSMOpozoriloPMM2x17med60in8012 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[12]
GSMOpozoriloPMM2x17med60in8013 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[13]
GSMOpozoriloPMM2x17med60in8014 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[14]
GSMOpozoriloPMM2x17med60in8015 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[15]
GSMOpozoriloPMM2x17med60in8016 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[16]
GSMOpozoriloPMM2x17med60in8017 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[17]
GSMOpozoriloPMM2x17med60in8018 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[18]
GSMOpozoriloPMM2x17med60in8019 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[19]
GSMOpozoriloPMM2x17med60in801 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[1]
GSMOpozoriloPMM2x17med60in8020 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[20]
GSMOpozoriloPMM2x17med60in8021 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[21]
GSMOpozoriloPMM2x17med60in8022 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[22]
GSMOpozoriloPMM2x17med60in8023 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[23]
GSMOpozoriloPMM2x17med60in8024 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[24]
GSMOpozoriloPMM2x17med60in8025 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[25]
GSMOpozoriloPMM2x17med60in8026 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[26]
GSMOpozoriloPMM2x17med60in8027 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[27]
GSMOpozoriloPMM2x17med60in8028 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[28]
GSMOpozoriloPMM2x17med60in8029 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[29]
GSMOpozoriloPMM2x17med60in802 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[2]
GSMOpozoriloPMM2x17med60in8030 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[30]
GSMOpozoriloPMM2x17med60in8031 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[31]
GSMOpozoriloPMM2x17med60in8032 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[32]
GSMOpozoriloPMM2x17med60in8033 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[33]
GSMOpozoriloPMM2x17med60in8034 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[34]
GSMOpozoriloPMM2x17med60in8035 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[35]
GSMOpozoriloPMM2x17med60in8036 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[36]
GSMOpozoriloPMM2x17med60in8037 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[37]
GSMOpozoriloPMM2x17med60in8038 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[38]
GSMOpozoriloPMM2x17med60in8039 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[39]
GSMOpozoriloPMM2x17med60in803 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[3]
GSMOpozoriloPMM2x17med60in8040 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[40]
GSMOpozoriloPMM2x17med60in8041 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[41]
GSMOpozoriloPMM2x17med60in8042 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[42]
GSMOpozoriloPMM2x17med60in804 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[4]
GSMOpozoriloPMM2x17med60in805 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[5]
GSMOpozoriloPMM2x17med60in806 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[6]
GSMOpozoriloPMM2x17med60in807 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[7]
GSMOpozoriloPMM2x17med60in808 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[8]
GSMOpozoriloPMM2x17med60in809 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[9]
GSMPMM1OverCurrentBetw1 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[1]
GSMPMM1OverCurrentBetw2 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[2]
GSMPMM1OverCurrentBetw3 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[3]
GSMPMM1OverCurrentOver1 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[1]
GSMPMM1OverCurrentOver2 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[2]
GSMPMM1OverCurrentOver3 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[3]
GSMPrevisokaTemp | DIGITAL | IOD_GSM | GSM:.PrevisokaTemp
GSMQ0_izkljuceno | DIGITAL | IOD_GSM | GSM:.Q0_izkljuceno
GSMQ0_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q0_vkljuceno
GSMQ12_izkljuceno | DIGITAL | IOD_GSM | GSM:.Q12_izkljuceno
GSMQ12_izpad | DIGITAL | IOD_GSM | GSM:.Q12_izpad
GSMQ12_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q12_vkljuceno
GSMrazlitjeLAH1 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH1
GSMrazlitjeLAH2 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH2
GSMrazlitjeLAH3 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH3
GSMrazlitjeLAH4 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH4
GSMSetDateTime | DIGITAL | IOD_GSM | GSM:.SetDateTime
GSMSetDateTimeDemand | DIGITAL | IOD_GSM | GSM:.SetDateTimeDemand
GSMSetDateTimeError | DIGITAL | IOD_GSM | GSM:.SetDateTimeError
GSMSetDateTimeFinished | DIGITAL | IOD_GSM | GSM:.SetDateTimeFinished
GSMSkupneNapakeNaprav_PMM17VirBVirA | DIGITAL | IOD_GSM | GSM:.SkupneNapakeNaprav_PMM17VirBVirA
GSMSlabaBaterijaPLC | DIGITAL | IOD_GSM | GSM:.SlabaBaterijaPLC
GSMTempPovp234Previs | DIGITAL | IOD_GSM | GSM:.TempPovp234Previs
GSMTempPovp56Previs | DIGITAL | IOD_GSM | GSM:.TempPovp56Previs
GSMTIA1_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA1_previs_temp
GSMTIA2_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA2_previs_temp
GSMTIA3_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA3_previs_temp
GSMTIA4_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA4_previs_temp
GSMTIA5_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA5_previs_temp
GSMTIA6_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA6_previs_temp
GSMTIA7_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA7_previs_temp
GSMUPS1Errors10 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[10]
GSMUPS1Errors11 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[11]
GSMUPS1Errors12 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[12]
GSMUPS1Errors13 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[13]
GSMUPS1Errors14 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[14]
GSMUPS1Errors15 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[15]
GSMUPS1Errors16 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[16]
GSMUPS1Errors17 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[17]
GSMUPS1Errors18 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[18]
GSMUPS1Errors19 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[19]
GSMUPS1Errors1 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[1]
GSMUPS1Errors20 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[20]
GSMUPS1Errors21 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[21]
GSMUPS1Errors22 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[22]
GSMUPS1Errors23 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[23]
GSMUPS1Errors24 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[24]
GSMUPS1Errors25 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[25]
GSMUPS1Errors2 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[2]
GSMUPS1Errors3 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[3]
GSMUPS1Errors4 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[4]
GSMUPS1Errors5 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[5]
GSMUPS1Errors6 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[6]
GSMUPS1Errors7 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[7]
GSMUPS1Errors8 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[8]
GSMUPS1Errors9 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[9]
GSMUPS2Errors10 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[10]
GSMUPS2Errors11 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[11]
GSMUPS2Errors12 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[12]
GSMUPS2Errors13 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[13]
GSMUPS2Errors14 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[14]
GSMUPS2Errors15 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[15]
GSMUPS2Errors16 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[16]
GSMUPS2Errors17 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[17]
GSMUPS2Errors18 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[18]
GSMUPS2Errors19 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[19]
GSMUPS2Errors1 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[1]
GSMUPS2Errors20 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[20]
GSMUPS2Errors21 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[21]
GSMUPS2Errors22 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[22]
GSMUPS2Errors23 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[23]
GSMUPS2Errors24 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[24]
GSMUPS2Errors25 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[25]
GSMUPS2Errors2 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[2]
GSMUPS2Errors3 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[3]
GSMUPS2Errors4 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[4]
GSMUPS2Errors5 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[5]
GSMUPS2Errors6 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[6]
GSMUPS2Errors7 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[7]
GSMUPS2Errors8 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[8]
GSMUPS2Errors9 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[9]
GSMUPS1AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmAwaitingPower
GSMUPS1AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmBypassBad
GSMUPS1AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmChargerFailed
GSMUPS1AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmCommunicationsLost
GSMUPS1AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmDepletedBattery
GSMUPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmDiagnosticTestFailed
GSMUPS1AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmInverterError
GSMUPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmIzhodOffKotZahtevano
GSMUPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmIzhodPreobremenjen
GSMUPS1AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmLowBattery
GSMUPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmNapakaNaVarovalki
GSMUPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmNapakaNaVentilatorju
GSMUPS1AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmOnBattery
GSMUPS1AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmOnBypass
GSMUPS1AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmShutdownImminent
GSMUPS1AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmShutdownPending
GSMUPS1AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmSlabaBaterija
GSMUPS1AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmSplosnaNapaka
GSMUPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmStanjeIzhodaIzvenToleranc
GSMUPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmStanjeVhodaIzvenToleranc
GSMUPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmTemperaturaIzvenToleranc
GSMUPS1AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmTestInProgres
GSMUPS1AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSIzhodOff
GSMUPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSOffKotZahtevano
GSMUPS1AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSSystemOff
GSMUPS1Napaka | DIGITAL | IOD_GSM | GSM:.UPS[1].Napaka
GSMUPS1StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusEcomodeAktiven
GSMUPS1StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusInverterIsOn
GSMUPS1StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusStopOperation
GSMUPS2AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmAwaitingPower
GSMUPS2AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmBypassBad
GSMUPS2AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmChargerFailed
GSMUPS2AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmCommunicationsLost
GSMUPS2AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmDepletedBattery
GSMUPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmDiagnosticTestFailed
GSMUPS2AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmInverterError
GSMUPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmIzhodOffKotZahtevano
GSMUPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmIzhodPreobremenjen
GSMUPS2AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmLowBattery
GSMUPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmNapakaNaVarovalki
GSMUPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmNapakaNaVentilatorju
GSMUPS2AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmOnBattery
GSMUPS2AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmOnBypass
GSMUPS2AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmShutdownImminent
GSMUPS2AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmShutdownPending
GSMUPS2AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmSlabaBaterija
GSMUPS2AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmSplosnaNapaka
GSMUPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmStanjeIzhodaIzvenToleranc
GSMUPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmStanjeVhodaIzvenToleranc
GSMUPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmTemperaturaIzvenToleranc
GSMUPS2AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmTestInProgres
GSMUPS2AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSIzhodOff
GSMUPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSOffKotZahtevano
GSMUPS2AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSSystemOff
GSMUPS2Napaka | DIGITAL | IOD_GSM | GSM:.UPS[2].Napaka
GSMUPS2StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusEcomodeAktiven
GSMUPS2StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusInverterIsOn
GSMUPS2StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusStopOperation
GSMUPS_A_V23_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_A_V23_delovanje
GSMUPS_A_V23_napaka | DIGITAL | IOD_GSM | GSM:.UPS_A_V23_napaka
GSMups_alarm | DIGITAL | IOD_GSM | GSM:.ups_alarm
GSMups_baterijski_nac | DIGITAL | IOD_GSM | GSM:.ups_baterijski_nac
GSMUPS_MGE1BatteryChargedState | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryChargedState
GSMUPS_MGE1BatteryCircuitBreaker | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryCircuitBreaker
GSMUPS_MGE1BatteryCompInProgress | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryCompInProgress
GSMUPS_MGE1BatteryFuseFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryFuseFault
GSMUPS_MGE1BatteryLowWarning | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryLowWarning
GSMUPS_MGE1BatteryTempOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryTempOutOfToler
GSMUPS_MGE1BypassInFreeFrequency | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BypassInFreeFrequency
GSMUPS_MGE1ChargerGeneralFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].ChargerGeneralFault
GSMUPS_MGE1DeviceVentilationFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].DeviceVentilationFault
GSMUPS_MGE1InverterFuseFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterFuseFault
GSMUPS_MGE1InverterOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterOverload
GSMUPS_MGE1InverterThermalOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterThermalOverload
GSMUPS_MGE1Mains1VoltOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains1VoltOutOfToler
GSMUPS_MGE1Mains2Overload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains2Overload
GSMUPS_MGE1Mains2VoltOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains2VoltOutOfToler
GSMUPS_MGE1MaintenancePosition | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].MaintenancePosition
GSMUPS_MGE1ManualBypassSwitch | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].ManualBypassSwitch
GSMUPS_MGE1NapakaNaVarovalkah | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].NapakaNaVarovalkah
GSMUPS_MGE1OutputInShortCircuit | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputInShortCircuit
GSMUPS_MGE1OutputOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputOverload
GSMUPS_MGE1OutputThermalOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputThermalOverload
GSMUPS_MGE1RectifierOn | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].RectifierOn
GSMUPS_MGE1RectifierThermOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].RectifierThermOverload
GSMUPS_MGE1Skupna_napaka | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Skupna_napaka
GSMUPS_MGE1UPS_coupled | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_coupled
GSMUPS_MGE1UPS_error | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_error
GSMUPS_MGE1UPS_in_backup | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_in_backup
GSMups_polnjenje | DIGITAL | IOD_GSM | GSM:.ups_polnjenje
GSMUPS_V23_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_V23_delovanje
GSMUPS_V23_napaka | DIGITAL | IOD_GSM | GSM:.UPS_V23_napaka
GSMUPS_V25_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_V25_delovanje
GSMUPS_V25_napaka | DIGITAL | IOD_GSM | GSM:.UPS_V25_napaka
GSMUPSMGEErrors10 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[10]
GSMUPSMGEErrors11 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[11]
GSMUPSMGEErrors12 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[12]
GSMUPSMGEErrors13 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[13]
GSMUPSMGEErrors14 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[14]
GSMUPSMGEErrors15 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[15]
GSMUPSMGEErrors16 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[16]
GSMUPSMGEErrors17 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[17]
GSMUPSMGEErrors1 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[1]
GSMUPSMGEErrors2 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[2]
GSMUPSMGEErrors3 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[3]
GSMUPSMGEErrors4 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[4]
GSMUPSMGEErrors5 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[5]
GSMUPSMGEErrors6 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[6]
GSMUPSMGEErrors7 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[7]
GSMUPSMGEErrors8 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[8]
GSMUPSMGEErrors9 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[9]
GSMUserLoggedIn | DIGITAL | IOD_GSM | GSM:.UserLoggedIn
GSMVLAZILEC1_delovanje | DIGITAL | IOD_GSM | GSM:.VLAZILEC1_delovanje
GSMVLAZILEC1_napaka | DIGITAL | IOD_GSM | GSM:.VLAZILEC1_napaka
GSMVLAZILEC2_delovanje | DIGITAL | IOD_GSM | GSM:.VLAZILEC2_delovanje
GSMVLAZILEC2_napaka | DIGITAL | IOD_GSM | GSM:.VLAZILEC2_napaka
GSMXVH_AlarmOn | DIGITAL | IOD_GSM | GSM:.XVH_AlarmOn
GSMXVH_enopolna_napaka | DIGITAL | IOD_GSM | GSM:.XVH_enopolna_napaka
GSMKLIMAT1_vklop_delovanjaR | DIGITAL | IOD_GSM | GSM:.KLIMAT1_vklop_delovanjaR
GSMKLIMAT2_vklop_delovanjaR | DIGITAL | IOD_GSM | GSM:.KLIMAT2_vklop_delovanjaR
GSMKLIMAT1_R_zakleni | DIGITAL | IOD_GSM | GSM:.KLIMAT1_R_zakleni
GSMKLIMAT2_R_zakleni | DIGITAL | IOD_GSM | GSM:.KLIMAT2_R_zakleni
GSMK1_vklop_izklop_poteka | DIGITAL | IOD_GSM | GSM:.K1_vklop_izklop_poteka
GSMK2_vklop_izklop_poteka | DIGITAL | IOD_GSM | GSM:.K2_vklop_izklop_poteka
GSMN_KlimeAVTO | DIGITAL | IOD_GSM | GSM:.N_KlimeAVTO
GSMUPS3AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmAwaitingPower
GSMUPS3AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmBypassBad
GSMUPS3AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmChargerFailed
GSMUPS3AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmCommunicationsLost
GSMUPS3AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmDepletedBattery
GSMUPS3AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmDiagnosticTestFailed
GSMUPS3AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmInverterError
GSMUPS3AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmIzhodOffKotZahtevano
GSMUPS3AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmIzhodPreobremenjen
GSMUPS3AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmLowBattery
GSMUPS3AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmNapakaNaVarovalki
GSMUPS3AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmNapakaNaVentilatorju
GSMUPS3AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmOnBattery
GSMUPS3AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmOnBypass
GSMUPS3AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmShutdownImminent
GSMUPS3AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmShutdownPending
GSMUPS3AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmSlabaBaterija
GSMUPS3AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmSplosnaNapaka
GSMUPS3AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmStanjeIzhodaIzvenToleranc
GSMUPS3AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmStanjeVhodaIzvenToleranc
GSMUPS3AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmTemperaturaIzvenToleranc
GSMUPS3AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmTestInProgres
GSMUPS3AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSIzhodOff
GSMUPS3AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSOffKotZahtevano
GSMUPS3AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSSystemOff
GSMUPS3Napaka | DIGITAL | IOD_GSM | GSM:.UPS[3].Napaka
GSMUPS3StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusEcomodeAktiven
GSMUPS3StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusInverterIsOn
GSMUPS3StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusStopOperation
GSMErrComUPS3 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[3]
GSMGSM_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.GSM_PozCent_napaka
GSMGSM_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.GSM_PozSenzor_okvara
GSMGSM_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.GSM_Gasenje_alarm
GSMAGR_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.AGR_PozCent_napaka
GSMAGR_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.AGR_PozSenzor_okvara
GSMAGR_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.AGR_Gasenje_alarm
GSMCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Dnevne_energija_scada1
GSMCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Dnevne_energija_scada2
GSMCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Tedenska_energija_scada1
GSMCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Tedenska_energija_scada2
GSMCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Mesecna_energija_scada1
GSMCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Mesecna_energija_scada2
GSMPozarnaCentrala_skupno | DIGITAL | IOD_GSM | GSM:.PozarnaCentrala_skupno
GSMDateTimeDan | INT | IOD_GSM | GSM:.DateTime.Dan | BYTE
GSMDateTimeLeto | INT | IOD_GSM | GSM:.DateTime.Leto | BYTE
GSMDateTimeLeto2 | INT | IOD_GSM | GSM:.DateTime.Leto2
GSMDateTimeMesec | INT | IOD_GSM | GSM:.DateTime.Mesec | BYTE
GSMDateTimeMinuta | INT | IOD_GSM | GSM:.DateTime.Minuta | BYTE
GSMDateTimeSekunda | INT | IOD_GSM | GSM:.DateTime.Sekunda | BYTE
GSMDateTimeUra | INT | IOD_GSM | GSM:.DateTime.Ura | BYTE
GSMErrorComCirc1Code10 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[10] | BYTE
GSMErrorComCirc1Code11 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[11] | BYTE
GSMErrorComCirc1Code12 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[12] | BYTE
GSMErrorComCirc1Code13 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[13] | BYTE
GSMErrorComCirc1Code14 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[14] | BYTE
GSMErrorComCirc1Code15 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[15] | BYTE
GSMErrorComCirc1Code1 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[1] | BYTE
GSMErrorComCirc1Code2 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[2] | BYTE
GSMErrorComCirc1Code3 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[3] | BYTE
GSMErrorComCirc1Code4 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[4] | BYTE
GSMErrorComCirc1Code5 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[5] | BYTE
GSMErrorComCirc1Code6 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[6] | BYTE
GSMErrorComCirc1Code7 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[7] | BYTE
GSMErrorComCirc1Code8 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[8] | BYTE
GSMErrorComCirc1Code9 | INT | IOD_GSM | GSM:.ErrorComCirc[1].Code[9] | BYTE
GSMErrorComCirc1Status | INT | IOD_GSM | GSM:.ErrorComCirc[1].Status
GSMErrorComKlima1Code10 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[10] | BYTE
GSMErrorComKlima1Code11 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[11] | BYTE
GSMErrorComKlima1Code12 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[12] | BYTE
GSMErrorComKlima1Code13 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[13] | BYTE
GSMErrorComKlima1Code14 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[14] | BYTE
GSMErrorComKlima1Code15 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[15] | BYTE
GSMErrorComKlima1Code1 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[1] | BYTE
GSMErrorComKlima1Code2 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[2] | BYTE
GSMErrorComKlima1Code3 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[3] | BYTE
GSMErrorComKlima1Code4 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[4] | BYTE
GSMErrorComKlima1Code5 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[5] | BYTE
GSMErrorComKlima1Code6 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[6] | BYTE
GSMErrorComKlima1Code7 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[7] | BYTE
GSMErrorComKlima1Code8 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[8] | BYTE
GSMErrorComKlima1Code9 | INT | IOD_GSM | GSM:.ErrorComKlima[1].Code[9] | BYTE
GSMErrorComKlima1Status | INT | IOD_GSM | GSM:.ErrorComKlima[1].Status
GSMErrorComKlima2Code10 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[10] | BYTE
GSMErrorComKlima2Code11 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[11] | BYTE
GSMErrorComKlima2Code12 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[12] | BYTE
GSMErrorComKlima2Code13 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[13] | BYTE
GSMErrorComKlima2Code14 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[14] | BYTE
GSMErrorComKlima2Code15 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[15] | BYTE
GSMErrorComKlima2Code1 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[1] | BYTE
GSMErrorComKlima2Code2 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[2] | BYTE
GSMErrorComKlima2Code3 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[3] | BYTE
GSMErrorComKlima2Code4 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[4] | BYTE
GSMErrorComKlima2Code5 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[5] | BYTE
GSMErrorComKlima2Code6 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[6] | BYTE
GSMErrorComKlima2Code7 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[7] | BYTE
GSMErrorComKlima2Code8 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[8] | BYTE
GSMErrorComKlima2Code9 | INT | IOD_GSM | GSM:.ErrorComKlima[2].Code[9] | BYTE
GSMErrorComKlima2Status | INT | IOD_GSM | GSM:.ErrorComKlima[2].Status
GSMErrorComPMM1Code10 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[10] | BYTE
GSMErrorComPMM1Code11 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[11] | BYTE
GSMErrorComPMM1Code12 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[12] | BYTE
GSMErrorComPMM1Code13 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[13] | BYTE
GSMErrorComPMM1Code14 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[14] | BYTE
GSMErrorComPMM1Code15 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[15] | BYTE
GSMErrorComPMM1Code1 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[1] | BYTE
GSMErrorComPMM1Code2 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[2] | BYTE
GSMErrorComPMM1Code3 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[3] | BYTE
GSMErrorComPMM1Code4 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[4] | BYTE
GSMErrorComPMM1Code5 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[5] | BYTE
GSMErrorComPMM1Code6 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[6] | BYTE
GSMErrorComPMM1Code7 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[7] | BYTE
GSMErrorComPMM1Code8 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[8] | BYTE
GSMErrorComPMM1Code9 | INT | IOD_GSM | GSM:.ErrorComPMM[1].Code[9] | BYTE
GSMErrorComPMM1Status | INT | IOD_GSM | GSM:.ErrorComPMM[1].Status
GSMErrorComUPS1Code10 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[10] | BYTE
GSMErrorComUPS1Code11 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[11] | BYTE
GSMErrorComUPS1Code12 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[12] | BYTE
GSMErrorComUPS1Code13 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[13] | BYTE
GSMErrorComUPS1Code14 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[14] | BYTE
GSMErrorComUPS1Code15 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[15] | BYTE
GSMErrorComUPS1Code1 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[1] | BYTE
GSMErrorComUPS1Code2 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[2] | BYTE
GSMErrorComUPS1Code3 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[3] | BYTE
GSMErrorComUPS1Code4 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[4] | BYTE
GSMErrorComUPS1Code5 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[5] | BYTE
GSMErrorComUPS1Code6 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[6] | BYTE
GSMErrorComUPS1Code7 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[7] | BYTE
GSMErrorComUPS1Code8 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[8] | BYTE
GSMErrorComUPS1Code9 | INT | IOD_GSM | GSM:.ErrorComUPS[1].Code[9] | BYTE
GSMErrorComUPS1Status | INT | IOD_GSM | GSM:.ErrorComUPS[1].Status
GSMErrorComUPS2Code10 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[10] | BYTE
GSMErrorComUPS2Code11 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[11] | BYTE
GSMErrorComUPS2Code12 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[12] | BYTE
GSMErrorComUPS2Code13 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[13] | BYTE
GSMErrorComUPS2Code14 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[14] | BYTE
GSMErrorComUPS2Code15 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[15] | BYTE
GSMErrorComUPS2Code1 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[1] | BYTE
GSMErrorComUPS2Code2 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[2] | BYTE
GSMErrorComUPS2Code3 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[3] | BYTE
GSMErrorComUPS2Code4 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[4] | BYTE
GSMErrorComUPS2Code5 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[5] | BYTE
GSMErrorComUPS2Code6 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[6] | BYTE
GSMErrorComUPS2Code7 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[7] | BYTE
GSMErrorComUPS2Code8 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[8] | BYTE
GSMErrorComUPS2Code9 | INT | IOD_GSM | GSM:.ErrorComUPS[2].Code[9] | BYTE
GSMErrorComUPS2Status | INT | IOD_GSM | GSM:.ErrorComUPS[2].Status
GSMErrorComUPSMGE1Code10 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[10] | BYTE
GSMErrorComUPSMGE1Code11 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[11] | BYTE
GSMErrorComUPSMGE1Code12 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[12] | BYTE
GSMErrorComUPSMGE1Code13 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[13] | BYTE
GSMErrorComUPSMGE1Code14 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[14] | BYTE
GSMErrorComUPSMGE1Code15 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[15] | BYTE
GSMErrorComUPSMGE1Code1 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[1] | BYTE
GSMErrorComUPSMGE1Code2 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[2] | BYTE
GSMErrorComUPSMGE1Code3 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[3] | BYTE
GSMErrorComUPSMGE1Code4 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[4] | BYTE
GSMErrorComUPSMGE1Code5 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[5] | BYTE
GSMErrorComUPSMGE1Code6 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[6] | BYTE
GSMErrorComUPSMGE1Code7 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[7] | BYTE
GSMErrorComUPSMGE1Code8 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[8] | BYTE
GSMErrorComUPSMGE1Code9 | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Code[9] | BYTE
GSMErrorComUPSMGE1Status | INT | IOD_GSM | GSM:.ErrorComUPSMGE[1].Status
GSMHIA1_vlaga_s | INT | IOD_GSM | GSM:.HIA1_vlaga_s
GSMHIA2_vlaga_s | INT | IOD_GSM | GSM:.HIA2_vlaga_s
GSMHIA3_vlaga_s | INT | IOD_GSM | GSM:.HIA3_vlaga_s
GSMHIA4_vlaga_s | INT | IOD_GSM | GSM:.HIA4_vlaga_s
GSMHIA5_vlaga_s | INT | IOD_GSM | GSM:.HIA5_vlaga_s
GSMHIA6_vlaga_s | INT | IOD_GSM | GSM:.HIA6_vlaga_s
GSMHIA7_vlaga_s | INT | IOD_GSM | GSM:.HIA7_vlaga_s
GSMKlima1Analog_izh_mesanje | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_mesanje
GSMKlima1Analog_izh_rekuperator | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_rekuperator
GSMKlima1Analog_izh_VentGrelnika | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_VentGrelnika
GSMKlima1Analog_izh_VentHlajenja | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_VentHlajenja
GSMKlima1Dejanska_zel_temp | INT | IOD_GSM | GSM:.Klima[1].Dejanska_zel_temp
GSMKlima1Hitrost_del_vent_disp | INT | IOD_GSM | GSM:.Klima[1].Hitrost_del_vent_disp
GSMKlima1Max_vpih | INT | IOD_GSM | GSM:.Klima[1].Max_vpih
GSMKlima1Min_vpih | INT | IOD_GSM | GSM:.Klima[1].Min_vpih
GSMKlima1Obrat_ure_Vent_h1 | INT | IOD_GSM | GSM:.Klima[1].Obrat_ure_Vent_h1
GSMKlima1Obrat_ure_Vent_h2 | INT | IOD_GSM | GSM:.Klima[1].Obrat_ure_Vent_h2
GSMKlima1Pol_komp_konec | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_konec
GSMKlima1Pol_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_sprem_zel_vr
GSMKlima1Pol_komp_zacetek | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_zacetek
GSMKlima1PreklopHitDelVent | INT | IOD_GSM | GSM:.Klima[1].PreklopHitDelVent
GSMKlima1Protizamrz_zascita | INT | IOD_GSM | GSM:.Klima[1].Protizamrz_zascita
GSMKlima1Rezim_delovanja | INT | IOD_GSM | GSM:.Klima[1].Rezim_delovanja
GSMKlima1Temperatura_dovoda | INT | IOD_GSM | GSM:.Klima[1].Temperatura_dovoda
GSMKlima1Temperatura_prostora | INT | IOD_GSM | GSM:.Klima[1].Temperatura_prostora
GSMKlima1TempPredPloscnimRekup | INT | IOD_GSM | GSM:.Klima[1].TempPredPloscnimRekup
GSMKlima1TempZaPloscnimRekup | INT | IOD_GSM | GSM:.Klima[1].TempZaPloscnimRekup
GSMKlima1Vlaga_v_prostoru | INT | IOD_GSM | GSM:.Klima[1].Vlaga_v_prostoru
GSMKlima1VlagaVstopZrakaProstor | INT | IOD_GSM | GSM:.Klima[1].VlagaVstopZrakaProstor
GSMKlima1Zel_temp_eko_gretja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_eko_gretja
GSMKlima1Zel_temp_eko_hlajenja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_eko_hlajenja
GSMKlima1Zel_temp_komf_gretja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_komf_gretja
GSMKlima1Zel_temp_komf_hlajenja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_komf_hlajenja
GSMKlima1Zim_komp_konec | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_konec
GSMKlima1Zim_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_sprem_zel_vr
GSMKlima1Zim_komp_zacetek | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_zacetek
GSMKlima1ZimKompMinVpihKonec | INT | IOD_GSM | GSM:.Klima[1].ZimKompMinVpihKonec
GSMKlima1ZimKompMinVpihZac | INT | IOD_GSM | GSM:.Klima[1].ZimKompMinVpihZac
GSMKlima1ZkompMinVpihSpremZelVr | INT | IOD_GSM | GSM:.Klima[1].ZkompMinVpihSpremZelVr
GSMKlima1Zunanja_temp | INT | IOD_GSM | GSM:.Klima[1].Zunanja_temp
GSMKlima2Analog_izh_mesanje | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_mesanje
GSMKlima2Analog_izh_rekuperator | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_rekuperator
GSMKlima2Analog_izh_VentGrelnika | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_VentGrelnika
GSMKlima2Analog_izh_VentHlajenja | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_VentHlajenja
GSMKlima2Dejanska_zel_temp | INT | IOD_GSM | GSM:.Klima[2].Dejanska_zel_temp
GSMKlima2Hitrost_del_vent_disp | INT | IOD_GSM | GSM:.Klima[2].Hitrost_del_vent_disp
GSMKlima2Max_vpih | INT | IOD_GSM | GSM:.Klima[2].Max_vpih
GSMKlima2Min_vpih | INT | IOD_GSM | GSM:.Klima[2].Min_vpih
GSMKlima2Obrat_ure_Vent_h1 | INT | IOD_GSM | GSM:.Klima[2].Obrat_ure_Vent_h1
GSMKlima2Obrat_ure_Vent_h2 | INT | IOD_GSM | GSM:.Klima[2].Obrat_ure_Vent_h2
GSMKlima2Pol_komp_konec | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_konec
GSMKlima2Pol_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_sprem_zel_vr
GSMKlima2Pol_komp_zacetek | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_zacetek
GSMKlima2PreklopHitDelVent | INT | IOD_GSM | GSM:.Klima[2].PreklopHitDelVent
GSMKlima2Protizamrz_zascita | INT | IOD_GSM | GSM:.Klima[2].Protizamrz_zascita
GSMKlima2Rezim_delovanja | INT | IOD_GSM | GSM:.Klima[2].Rezim_delovanja
GSMKlima2Temperatura_dovoda | INT | IOD_GSM | GSM:.Klima[2].Temperatura_dovoda
GSMKlima2Temperatura_prostora | INT | IOD_GSM | GSM:.Klima[2].Temperatura_prostora
GSMKlima2TempPredPloscnimRekup | INT | IOD_GSM | GSM:.Klima[2].TempPredPloscnimRekup
GSMKlima2TempZaPloscnimRekup | INT | IOD_GSM | GSM:.Klima[2].TempZaPloscnimRekup
GSMKlima2Vlaga_v_prostoru | INT | IOD_GSM | GSM:.Klima[2].Vlaga_v_prostoru
GSMKlima2VlagaVstopZrakaProstor | INT | IOD_GSM | GSM:.Klima[2].VlagaVstopZrakaProstor
GSMKlima2Zel_temp_eko_gretja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_eko_gretja
GSMKlima2Zel_temp_eko_hlajenja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_eko_hlajenja
GSMKlima2Zel_temp_komf_gretja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_komf_gretja
GSMKlima2Zel_temp_komf_hlajenja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_komf_hlajenja
GSMKlima2Zim_komp_konec | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_konec
GSMKlima2Zim_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_sprem_zel_vr
GSMKlima2Zim_komp_zacetek | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_zacetek
GSMKlima2ZimKompMinVpihKonec | INT | IOD_GSM | GSM:.Klima[2].ZimKompMinVpihKonec
GSMKlima2ZimKompMinVpihZac | INT | IOD_GSM | GSM:.Klima[2].ZimKompMinVpihZac
GSMKlima2ZkompMinVpihSpremZelVr | INT | IOD_GSM | GSM:.Klima[2].ZkompMinVpihSpremZelVr
GSMKlima2Zunanja_temp | INT | IOD_GSM | GSM:.Klima[2].Zunanja_temp
GSMKlimaIzklopObrUre | INT | IOD_GSM | GSM:.KlimaIzklopObrUre
GSMPMM1AlarmPhase1GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].GlobalAlarmReg
GSMPMM1AlarmPhase2GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].GlobalAlarmReg
GSMPMM1AlarmPhase3GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].GlobalAlarmReg
GSMQ12stanje | INT | IOD_GSM | GSM:.Q12stanje | BYTE
GSMTempHistereza | INT | IOD_GSM | GSM:.TempHistereza
GSMTempPovp234 | INT | IOD_GSM | GSM:.TempPovp234
GSMTempPovp234Alarm | INT | IOD_GSM | GSM:.TempPovp234Alarm
GSMTempPovp56 | INT | IOD_GSM | GSM:.TempPovp56
GSMTempPovp56Alarm | INT | IOD_GSM | GSM:.TempPovp56Alarm
GSMTempZaVklopKlim1 | INT | IOD_GSM | GSM:.TempZaVklopKlim1
GSMTempZaVklopKlim2 | INT | IOD_GSM | GSM:.TempZaVklopKlim2
GSMTIA1_alarm | INT | IOD_GSM | GSM:.TIA1_alarm
GSMTIA1_temp_s | INT | IOD_GSM | GSM:.TIA1_temp_s
GSMTIA2_alarm | INT | IOD_GSM | GSM:.TIA2_alarm
GSMTIA2_temp_s | INT | IOD_GSM | GSM:.TIA2_temp_s
GSMTIA3_alarm | INT | IOD_GSM | GSM:.TIA3_alarm
GSMTIA3_temp_s | INT | IOD_GSM | GSM:.TIA3_temp_s
GSMTIA4_alarm | INT | IOD_GSM | GSM:.TIA4_alarm
GSMTIA4_temp_s | INT | IOD_GSM | GSM:.TIA4_temp_s
GSMTIA5_alarm | INT | IOD_GSM | GSM:.TIA5_alarm
GSMTIA5_temp_s | INT | IOD_GSM | GSM:.TIA5_temp_s
GSMTIA6_alarm | INT | IOD_GSM | GSM:.TIA6_alarm
GSMTIA6_temp_s | INT | IOD_GSM | GSM:.TIA6_temp_s
GSMTIA7_alarm | INT | IOD_GSM | GSM:.TIA7_alarm
GSMTIA7_temp_s | INT | IOD_GSM | GSM:.TIA7_temp_s
GSMUPS1InverterStatus | INT | IOD_GSM | GSM:.UPS[1].InverterStatus
GSMUPS1OutputStatus | INT | IOD_GSM | GSM:.UPS[1].OutputStatus
GSMUPS1SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[1].SteviloIzpadovVhodneLinije
GSMUPS1UnitStatus | INT | IOD_GSM | GSM:.UPS[1].UnitStatus
GSMUPS2InverterStatus | INT | IOD_GSM | GSM:.UPS[2].InverterStatus
GSMUPS2OutputStatus | INT | IOD_GSM | GSM:.UPS[2].OutputStatus
GSMUPS2SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[2].SteviloIzpadovVhodneLinije
GSMUPS2UnitStatus | INT | IOD_GSM | GSM:.UPS[2].UnitStatus
GSMUPS_MGE1BatteryBackupTime | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryBackupTime
GSMUPS_MGE1BatteryChargingLevel | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryChargingLevel
GSMUPS_MGE1BatteryRechargeDuration | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryRechargeDuration
GSMUPS_MGE1I1output | INT | IOD_GSM | GSM:.UPS_MGE[1].I1output
GSMUPS_MGE1I2output | INT | IOD_GSM | GSM:.UPS_MGE[1].I2output
GSMUPS_MGE1I3output | INT | IOD_GSM | GSM:.UPS_MGE[1].I3output
GSMUPS_MGE1InverterFrequency | INT | IOD_GSM | GSM:.UPS_MGE[1].InverterFrequency
GSMUPS_MGE1OutputActivePower1 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower1
GSMUPS_MGE1OutputActivePower2 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower2
GSMUPS_MGE1OutputActivePower3 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower3
GSMUPS_MGE1OutputFrequency | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputFrequency
GSMUPS_MGE1OutputLoadLevel | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputLoadLevel
GSMUPS_MGE1StatusBaterije | INT | IOD_GSM | GSM:.UPS_MGE[1].StatusBaterije | BYTE
GSMUPS_MGE1U12mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U12mains1
GSMUPS_MGE1U12mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U12mains2
GSMUPS_MGE1U1N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U1N_inverter
GSMUPS_MGE1U1N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U1N_output
GSMUPS_MGE1U23mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U23mains1
GSMUPS_MGE1U23mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U23mains2
GSMUPS_MGE1U2N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U2N_inverter
GSMUPS_MGE1U2N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U2N_output
GSMUPS_MGE1U31mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U31mains1
GSMUPS_MGE1U31mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U31mains2
GSMUPS_MGE1U3N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U3N_inverter
GSMUPS_MGE1U3N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U3N_output
GSMUPS_MGE1U_battery | INT | IOD_GSM | GSM:.UPS_MGE[1].U_battery
GSMUserCurrentLevel | INT | IOD_GSM | GSM:.UserCurrentLevel | BYTE
GSMXVH_UPSstatus | INT | IOD_GSM | GSM:.XVH_UPSstatus | BYTE
GSMUPS3InverterStatus | INT | IOD_GSM | GSM:.UPS[3].InverterStatus
GSMUPS3OutputStatus | INT | IOD_GSM | GSM:.UPS[3].OutputStatus
GSMUPS3SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[3].SteviloIzpadovVhodneLinije
GSMUPS3UnitStatus | INT | IOD_GSM | GSM:.UPS[3].UnitStatus
GSMCirc1CosFi_III | REAL | IOD_GSM | GSM:.Circ[1].CosFi_III
GSMCirc1DelovnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].DelovnaEnergija
GSMCirc1DelovnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_III
GSMCirc1DelovnaMoc_L1 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L1
GSMCirc1DelovnaMoc_L2 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L2
GSMCirc1DelovnaMoc_L3 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L3
GSMCirc1Frekvenca_L1 | REAL | IOD_GSM | GSM:.Circ[1].Frekvenca_L1
GSMCirc1InduktivnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].InduktivnaEnergija
GSMCirc1InduktivnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].InduktivnaMoc_III
GSMCirc1JalovaMoc_L1 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L1
GSMCirc1JalovaMoc_L2 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L2
GSMCirc1JalovaMoc_L3 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L3
GSMCirc1KapacitivnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].KapacitivnaEnergija
GSMCirc1KapacitivnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].KapacitivnaMoc_III
GSMCirc1MaximumDemand | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemand
GSMCirc1Napetost_L1_L2 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L1_L2
GSMCirc1Napetost_L1_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L1_N
GSMCirc1Napetost_L2_L3 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L2_L3
GSMCirc1Napetost_L2_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L2_N
GSMCirc1Napetost_L3_L1 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L3_L1
GSMCirc1Napetost_L3_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L3_N
GSMCirc1NavideznaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].NavideznaMoc_III
GSMCirc1NicelniTok | REAL | IOD_GSM | GSM:.Circ[1].NicelniTok
GSMCirc1PowerFactor_III | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_III
GSMCirc1PowerFactor_L1 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L1
GSMCirc1PowerFactor_L2 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L2
GSMCirc1PowerFactor_L3 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L3
GSMCirc1THDI_L1 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L1
GSMCirc1THDI_L2 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L2
GSMCirc1THDI_L3 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L3
GSMCirc1THDV_L1 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L1
GSMCirc1THDV_L2 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L2
GSMCirc1THDV_L3 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L3
GSMCirc1Tok_L1 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L1
GSMCirc1Tok_L2 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L2
GSMCirc1Tok_L3 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L3
GSMCirc1TokPovprecje_III | REAL | IOD_GSM | GSM:.Circ[1].TokPovprecje_III
GSMPMM1ActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM[1].ActiveEnergyConsumed_kWh
GSMPMM1ActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseA_kW
GSMPMM1ActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseB_kW
GSMPMM1ActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseC_kW
GSMPMM1AparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseA
GSMPMM1AparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseB
GSMPMM1AparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseC
GSMPMM1AverageCurrent_A | REAL | IOD_GSM | GSM:.PMM[1].AverageCurrent_A
GSMPMM1AveragePhaseToNeutral_V | REAL | IOD_GSM | GSM:.PMM[1].AveragePhaseToNeutral_V
GSMPMM1AveragePhaseToPhase_V | REAL | IOD_GSM | GSM:.PMM[1].AveragePhaseToPhase_V
GSMPMM1CurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseA_A
GSMPMM1CurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseB_A
GSMPMM1CurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseC_A
GSMPMM1Frequency_Hz | REAL | IOD_GSM | GSM:.PMM[1].Frequency_Hz
GSMPMM1Phase1Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[10]
GSMPMM1Phase1Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[11]
GSMPMM1Phase1Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[12]
GSMPMM1Phase1Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[13]
GSMPMM1Phase1Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[14]
GSMPMM1Phase1Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[15]
GSMPMM1Phase1Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[16]
GSMPMM1Phase1Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[17]
GSMPMM1Phase1Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[18]
GSMPMM1Phase1Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[19]
GSMPMM1Phase1Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[1]
GSMPMM1Phase1Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[20]
GSMPMM1Phase1Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[21]
GSMPMM1Phase1Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[22]
GSMPMM1Phase1Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[23]
GSMPMM1Phase1Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[24]
GSMPMM1Phase1Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[25]
GSMPMM1Phase1Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[26]
GSMPMM1Phase1Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[27]
GSMPMM1Phase1Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[28]
GSMPMM1Phase1Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[29]
GSMPMM1Phase1Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[2]
GSMPMM1Phase1Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[30]
GSMPMM1Phase1Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[31]
GSMPMM1Phase1Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[32]
GSMPMM1Phase1Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[33]
GSMPMM1Phase1Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[34]
GSMPMM1Phase1Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[35]
GSMPMM1Phase1Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[36]
GSMPMM1Phase1Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[37]
GSMPMM1Phase1Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[38]
GSMPMM1Phase1Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[39]
GSMPMM1Phase1Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[3]
GSMPMM1Phase1Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[40]
GSMPMM1Phase1Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[41]
GSMPMM1Phase1Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[42]
GSMPMM1Phase1Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[4]
GSMPMM1Phase1Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[5]
GSMPMM1Phase1Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[6]
GSMPMM1Phase1Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[7]
GSMPMM1Phase1Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[8]
GSMPMM1Phase1Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[9]
GSMPMM1Phase2Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[10]
GSMPMM1Phase2Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[11]
GSMPMM1Phase2Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[12]
GSMPMM1Phase2Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[13]
GSMPMM1Phase2Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[14]
GSMPMM1Phase2Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[15]
GSMPMM1Phase2Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[16]
GSMPMM1Phase2Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[17]
GSMPMM1Phase2Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[18]
GSMPMM1Phase2Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[19]
GSMPMM1Phase2Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[1]
GSMPMM1Phase2Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[20]
GSMPMM1Phase2Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[21]
GSMPMM1Phase2Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[22]
GSMPMM1Phase2Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[23]
GSMPMM1Phase2Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[24]
GSMPMM1Phase2Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[25]
GSMPMM1Phase2Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[26]
GSMPMM1Phase2Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[27]
GSMPMM1Phase2Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[28]
GSMPMM1Phase2Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[29]
GSMPMM1Phase2Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[2]
GSMPMM1Phase2Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[30]
GSMPMM1Phase2Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[31]
GSMPMM1Phase2Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[32]
GSMPMM1Phase2Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[33]
GSMPMM1Phase2Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[34]
GSMPMM1Phase2Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[35]
GSMPMM1Phase2Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[36]
GSMPMM1Phase2Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[37]
GSMPMM1Phase2Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[38]
GSMPMM1Phase2Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[39]
GSMPMM1Phase2Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[3]
GSMPMM1Phase2Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[40]
GSMPMM1Phase2Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[41]
GSMPMM1Phase2Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[42]
GSMPMM1Phase2Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[4]
GSMPMM1Phase2Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[5]
GSMPMM1Phase2Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[6]
GSMPMM1Phase2Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[7]
GSMPMM1Phase2Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[8]
GSMPMM1Phase2Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[9]
GSMPMM1Phase3Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[10]
GSMPMM1Phase3Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[11]
GSMPMM1Phase3Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[12]
GSMPMM1Phase3Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[13]
GSMPMM1Phase3Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[14]
GSMPMM1Phase3Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[15]
GSMPMM1Phase3Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[16]
GSMPMM1Phase3Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[17]
GSMPMM1Phase3Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[18]
GSMPMM1Phase3Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[19]
GSMPMM1Phase3Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[1]
GSMPMM1Phase3Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[20]
GSMPMM1Phase3Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[21]
GSMPMM1Phase3Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[22]
GSMPMM1Phase3Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[23]
GSMPMM1Phase3Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[24]
GSMPMM1Phase3Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[25]
GSMPMM1Phase3Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[26]
GSMPMM1Phase3Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[27]
GSMPMM1Phase3Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[28]
GSMPMM1Phase3Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[29]
GSMPMM1Phase3Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[2]
GSMPMM1Phase3Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[30]
GSMPMM1Phase3Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[31]
GSMPMM1Phase3Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[32]
GSMPMM1Phase3Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[33]
GSMPMM1Phase3Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[34]
GSMPMM1Phase3Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[35]
GSMPMM1Phase3Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[36]
GSMPMM1Phase3Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[37]
GSMPMM1Phase3Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[38]
GSMPMM1Phase3Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[39]
GSMPMM1Phase3Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[3]
GSMPMM1Phase3Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[40]
GSMPMM1Phase3Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[41]
GSMPMM1Phase3Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[42]
GSMPMM1Phase3Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[4]
GSMPMM1Phase3Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[5]
GSMPMM1Phase3Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[6]
GSMPMM1Phase3Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[7]
GSMPMM1Phase3Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[8]
GSMPMM1Phase3Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[9]
GSMPMM1PowerFactorSys | REAL | IOD_GSM | GSM:.PMM[1].PowerFactorSys
GSMPMM1ReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM[1].ReactiveEnergyConsumed_kVARh
GSMPMM1ReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseA
GSMPMM1ReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseB
GSMPMM1ReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseC
GSMPMM1TotalActivePower_kW | REAL | IOD_GSM | GSM:.PMM[1].TotalActivePower_kW
GSMPMM1TotalAparentPower_kVA | REAL | IOD_GSM | GSM:.PMM[1].TotalAparentPower_kVA
GSMPMM1TotalPowerFactor | REAL | IOD_GSM | GSM:.PMM[1].TotalPowerFactor
GSMPMM1TotalReactivePower_kVAR | REAL | IOD_GSM | GSM:.PMM[1].TotalReactivePower_kVAR
GSMPMM1VirA_fsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_fsys
GSMPMM1VirA_Isys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Isys
GSMPMM1VirA_PFsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_PFsys
GSMPMM1VirA_Psys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Psys
GSMPMM1VirA_Qsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Qsys
GSMPMM1VirA_Ssys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Ssys
GSMPMM1VirA_Usys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Usys
GSMPMM1VirB_fsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_fsys
GSMPMM1VirB_Isys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Isys
GSMPMM1VirB_PFsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_PFsys
GSMPMM1VirB_Psys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Psys
GSMPMM1VirB_Qsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Qsys
GSMPMM1VirB_Ssys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Ssys
GSMPMM1VirB_Usys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Usys
GSMPMM1VirBActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM[1].VirBActiveEnergyConsumed_kWh
GSMPMM1VirBActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseA_kW
GSMPMM1VirBActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseB_kW
GSMPMM1VirBActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseC_kW
GSMPMM1VirBAparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseA
GSMPMM1VirBAparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseB
GSMPMM1VirBAparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseC
GSMPMM1VirBAverageCurrent_A | REAL | IOD_GSM | GSM:.PMM[1].VirBAverageCurrent_A
GSMPMM1VirBAveragePhaseToNeutral_V | REAL | IOD_GSM | GSM:.PMM[1].VirBAveragePhaseToNeutral_V
GSMPMM1VirBAveragePhaseToPhase_V | REAL | IOD_GSM | GSM:.PMM[1].VirBAveragePhaseToPhase_V
GSMPMM1VirBCurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseA_A
GSMPMM1VirBCurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseB_A
GSMPMM1VirBCurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseC_A
GSMPMM1VirBFrequency_Hz | REAL | IOD_GSM | GSM:.PMM[1].VirBFrequency_Hz
GSMPMM1VirBPowerFactorSys | REAL | IOD_GSM | GSM:.PMM[1].VirBPowerFactorSys
GSMPMM1VirBReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM[1].VirBReactiveEnergyConsumed_kVARh
GSMPMM1VirBReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseA
GSMPMM1VirBReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseB
GSMPMM1VirBReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseC
GSMPMM1VirBTotalActivePower_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalActivePower_kW
GSMPMM1VirBTotalAparentPower_kVA | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalAparentPower_kVA
GSMPMM1VirBTotalPowerFactor | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalPowerFactor
GSMPMM1VirBTotalReactivePower_kVAR | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalReactivePower_kVAR
GSMPMM1VirBVoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseAB_V
GSMPMM1VirBVoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseAN_V
GSMPMM1VirBVoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseBC_V
GSMPMM1VirBVoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseBN_V
GSMPMM1VirBVoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseCA_V
GSMPMM1VirBVoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseCN_V
GSMPMM1VoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseAB_V
GSMPMM1VoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseAN_V
GSMPMM1VoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseBC_V
GSMPMM1VoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseBN_V
GSMPMM1VoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseCA_V
GSMPMM1VoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseCN_V
GSMPMMfaza01 | REAL | IOD_GSM | GSM:.PMMfaza01
GSMPMMfaza02 | REAL | IOD_GSM | GSM:.PMMfaza02
GSMPMMfaza03 | REAL | IOD_GSM | GSM:.PMMfaza03
GSMPMMfaza04 | REAL | IOD_GSM | GSM:.PMMfaza04
GSMPMMfaza05 | REAL | IOD_GSM | GSM:.PMMfaza05
GSMPMMfaza06 | REAL | IOD_GSM | GSM:.PMMfaza06
GSMPMMfaza07 | REAL | IOD_GSM | GSM:.PMMfaza07
GSMPMMfaza08 | REAL | IOD_GSM | GSM:.PMMfaza08
GSMPMMfaza09 | REAL | IOD_GSM | GSM:.PMMfaza09
GSMPMMfaza10 | REAL | IOD_GSM | GSM:.PMMfaza10
GSMPMMfaza11 | REAL | IOD_GSM | GSM:.PMMfaza11
GSMPMMfaza12 | REAL | IOD_GSM | GSM:.PMMfaza12
GSMPMMfaza13 | REAL | IOD_GSM | GSM:.PMMfaza13
GSMPMMfaza14 | REAL | IOD_GSM | GSM:.PMMfaza14
GSMPMMfaza15 | REAL | IOD_GSM | GSM:.PMMfaza15
GSMPMMfaza16 | REAL | IOD_GSM | GSM:.PMMfaza16
GSMPMMfaza17 | REAL | IOD_GSM | GSM:.PMMfaza17
GSMPMMfaza18 | REAL | IOD_GSM | GSM:.PMMfaza18
GSMPMMfaza19 | REAL | IOD_GSM | GSM:.PMMfaza19
GSMPMMfaza20 | REAL | IOD_GSM | GSM:.PMMfaza20
GSMPMMfaza21 | REAL | IOD_GSM | GSM:.PMMfaza21
GSMPMMfaza22 | REAL | IOD_GSM | GSM:.PMMfaza22
GSMPMMfaza23 | REAL | IOD_GSM | GSM:.PMMfaza23
GSMPMMfaza24 | REAL | IOD_GSM | GSM:.PMMfaza24
GSMPMMfaza25 | REAL | IOD_GSM | GSM:.PMMfaza25
GSMPMMfaza26 | REAL | IOD_GSM | GSM:.PMMfaza26
GSMPMMfaza27 | REAL | IOD_GSM | GSM:.PMMfaza27
GSMPMMfaza28 | REAL | IOD_GSM | GSM:.PMMfaza28
GSMPMMfaza29 | REAL | IOD_GSM | GSM:.PMMfaza29
GSMPMMfaza30 | REAL | IOD_GSM | GSM:.PMMfaza30
GSMPMMfaza31 | REAL | IOD_GSM | GSM:.PMMfaza31
GSMPMMfaza32 | REAL | IOD_GSM | GSM:.PMMfaza32
GSMPMMfaza33 | REAL | IOD_GSM | GSM:.PMMfaza33
GSMPMMfaza34 | REAL | IOD_GSM | GSM:.PMMfaza34
GSMPMMfaza35 | REAL | IOD_GSM | GSM:.PMMfaza35
GSMPMMfaza36 | REAL | IOD_GSM | GSM:.PMMfaza36
GSMPMMfaza37 | REAL | IOD_GSM | GSM:.PMMfaza37
GSMPMMfaza38 | REAL | IOD_GSM | GSM:.PMMfaza38
GSMPMMfaza39 | REAL | IOD_GSM | GSM:.PMMfaza39
GSMPMMfaza40 | REAL | IOD_GSM | GSM:.PMMfaza40
GSMPMMfaza41 | REAL | IOD_GSM | GSM:.PMMfaza41
GSMPMMfaza42 | REAL | IOD_GSM | GSM:.PMMfaza42
GSMUPS1EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[1].EstimatedChargeRemaining
GSMUPS1EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[1].EstimatedMinutesRemaining
GSMUPS1IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL1
GSMUPS1IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL2
GSMUPS1IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL3
GSMUPS1NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[1].NapetostBaterije
GSMUPS1TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[1].TemperaturaBaterije
GSMUPS1VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL1
GSMUPS1VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL2
GSMUPS1VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL3
GSMUPS1VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL1
GSMUPS1VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL2
GSMUPS1VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL3
GSMUPS2EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[2].EstimatedChargeRemaining
GSMUPS2EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[2].EstimatedMinutesRemaining
GSMUPS2IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL1
GSMUPS2IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL2
GSMUPS2IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL3
GSMUPS2NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[2].NapetostBaterije
GSMUPS2TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[2].TemperaturaBaterije
GSMUPS2VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL1
GSMUPS2VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL2
GSMUPS2VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL3
GSMUPS2VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL1
GSMUPS2VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL2
GSMUPS2VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL3
GSMXVHdepltedBatery1 | REAL | IOD_GSM | GSM:.XVHdepltedBatery1
GSMXVHdepltedBatery2 | REAL | IOD_GSM | GSM:.XVHdepltedBatery2
GSMXVHlowBatery1 | REAL | IOD_GSM | GSM:.XVHlowBatery1
GSMXVHlowBatery2 | REAL | IOD_GSM | GSM:.XVHlowBatery2
GSMPMMskupniTokA | REAL | IOD_GSM | GSM:.PMMskupniTokA
GSMPMMskupniTokB | REAL | IOD_GSM | GSM:.PMMskupniTokB
GSMUPS3EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[3].EstimatedChargeRemaining
GSMUPS3EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[3].EstimatedMinutesRemaining
GSMUPS3IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL1
GSMUPS3IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL2
GSMUPS3IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL3
GSMUPS3NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[3].NapetostBaterije
GSMUPS3TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[3].TemperaturaBaterije
GSMUPS3VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL1
GSMUPS3VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL2
GSMUPS3VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL3
GSMUPS3VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL1
GSMUPS3VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL2
GSMUPS3VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL3
GSMCirc1MaximumDemandA2 | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemandA2
GSMCirc1MaximumDemandA3 | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemandA3
GSMCirc1RazEner_D_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_D_SCADA
GSMCirc1RazEner_T_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_T_SCADA
GSMCirc1RazEner_M_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_M_SCADA
GSMDate_Time0 | STRING | IOD_GSM | GSM:.Date_Time[0]
GSMDate_Time1 | STRING | IOD_GSM | GSM:.Date_Time[1]
GSMDate_Time2 | STRING | IOD_GSM | GSM:.Date_Time[2]
GSMDate_Time3 | STRING | IOD_GSM | GSM:.Date_Time[3]
GSMUserCurrentName | STRING | IOD_GSM | GSM:.UserCurrentName
GSMkom_nast_cas_izpada | UINT | IOD_GSM | GSM:.kom_nast_cas_izpada
GSMPMM1AlarmPhase1C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C01_16_60to80
GSMPMM1AlarmPhase1C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C01_16_over80
GSMPMM1AlarmPhase1C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C17_32_60to80
GSMPMM1AlarmPhase1C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C17_32_over80
GSMPMM1AlarmPhase1C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C33_42_60to80
GSMPMM1AlarmPhase1C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C33_42_over80
GSMPMM1AlarmPhase2C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C01_16_60to80
GSMPMM1AlarmPhase2C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C01_16_over80
GSMPMM1AlarmPhase2C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C17_32_60to80
GSMPMM1AlarmPhase2C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C17_32_over80
GSMPMM1AlarmPhase2C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C33_42_60to80
GSMPMM1AlarmPhase2C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C33_42_over80
GSMPMM1AlarmPhase3C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C01_16_60to80
GSMPMM1AlarmPhase3C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C01_16_over80
GSMPMM1AlarmPhase3C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C17_32_60to80
GSMPMM1AlarmPhase3C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C17_32_over80
GSMPMM1AlarmPhase3C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C33_42_60to80
GSMPMM1AlarmPhase3C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C33_42_over80
GSMUPS1StatusBaterije | UINT | IOD_GSM | GSM:.UPS[1].StatusBaterije
GSMUPS2StatusBaterije | UINT | IOD_GSM | GSM:.UPS[2].StatusBaterije
GSMK1_obr_u_skupno | UINT | IOD_GSM | GSM:.K1_obr_u_skupno
GSMK2_obr_u_skupno | UINT | IOD_GSM | GSM:.K2_obr_u_skupno
GSMUPS3StatusBaterije | UINT | IOD_GSM | GSM:.UPS[3].StatusBaterije

## variable_3
GSMAlarmGenUPS_A_V23 | DIGITAL | IOD_GSM_TCP | 1 | 00001 | AlarmGenUPS_A_V23
GSMAlarmGenUPS_V23 | DIGITAL | IOD_GSM_TCP | 2 | 00002 | AlarmGenUPS_V23
GSMAlarmGenUPS_V25 | DIGITAL | IOD_GSM_TCP | 3 | 00003 | AlarmGenUPS_V25
GSMAlarmPMM1VirATokPrevisok | DIGITAL | IOD_GSM_TCP | 4 | 00004 | AlarmPMM1VirATokPrevisok
GSMAlarmPMM1VirATokVisok | DIGITAL | IOD_GSM_TCP | 5 | 00005 | AlarmPMM1VirATokVisok
GSMAlarmPMM1VirBTokPrevisok | DIGITAL | IOD_GSM_TCP | 6 | 00006 | AlarmPMM1VirBTokPrevisok
GSMAlarmPMM1VirBTokVisok | DIGITAL | IOD_GSM_TCP | 7 | 00007 | AlarmPMM1VirBTokVisok
GSMAlarmPMM2x17nad8010 | DIGITAL | IOD_GSM_TCP | 8 | 00008 | AlarmPMM2x17nad80[10]
GSMAlarmPMM2x17nad8011 | DIGITAL | IOD_GSM_TCP | 9 | 00009 | AlarmPMM2x17nad80[11]
GSMAlarmPMM2x17nad8012 | DIGITAL | IOD_GSM_TCP | 10 | 00010 | AlarmPMM2x17nad80[12]
GSMAlarmPMM2x17nad8013 | DIGITAL | IOD_GSM_TCP | 11 | 00011 | AlarmPMM2x17nad80[13]
GSMAlarmPMM2x17nad8014 | DIGITAL | IOD_GSM_TCP | 12 | 00012 | AlarmPMM2x17nad80[14]
GSMAlarmPMM2x17nad8015 | DIGITAL | IOD_GSM_TCP | 13 | 00013 | AlarmPMM2x17nad80[15]
GSMAlarmPMM2x17nad8016 | DIGITAL | IOD_GSM_TCP | 14 | 00014 | AlarmPMM2x17nad80[16]
GSMAlarmPMM2x17nad8017 | DIGITAL | IOD_GSM_TCP | 15 | 00015 | AlarmPMM2x17nad80[17]
GSMAlarmPMM2x17nad8018 | DIGITAL | IOD_GSM_TCP | 16 | 00016 | AlarmPMM2x17nad80[18]
GSMAlarmPMM2x17nad8019 | DIGITAL | IOD_GSM_TCP | 17 | 00017 | AlarmPMM2x17nad80[19]
GSMAlarmPMM2x17nad801 | DIGITAL | IOD_GSM_TCP | 18 | 00018 | AlarmPMM2x17nad80[1]
GSMAlarmPMM2x17nad8020 | DIGITAL | IOD_GSM_TCP | 19 | 00019 | AlarmPMM2x17nad80[20]
GSMAlarmPMM2x17nad8021 | DIGITAL | IOD_GSM_TCP | 20 | 00020 | AlarmPMM2x17nad80[21]
GSMAlarmPMM2x17nad8022 | DIGITAL | IOD_GSM_TCP | 21 | 00021 | AlarmPMM2x17nad80[22]
GSMAlarmPMM2x17nad8023 | DIGITAL | IOD_GSM_TCP | 22 | 00022 | AlarmPMM2x17nad80[23]
GSMAlarmPMM2x17nad8024 | DIGITAL | IOD_GSM_TCP | 23 | 00023 | AlarmPMM2x17nad80[24]
GSMAlarmPMM2x17nad8025 | DIGITAL | IOD_GSM_TCP | 24 | 00024 | AlarmPMM2x17nad80[25]
GSMAlarmPMM2x17nad8026 | DIGITAL | IOD_GSM_TCP | 25 | 00025 | AlarmPMM2x17nad80[26]
GSMAlarmPMM2x17nad8027 | DIGITAL | IOD_GSM_TCP | 26 | 00026 | AlarmPMM2x17nad80[27]
GSMAlarmPMM2x17nad8028 | DIGITAL | IOD_GSM_TCP | 27 | 00027 | AlarmPMM2x17nad80[28]
GSMAlarmPMM2x17nad8029 | DIGITAL | IOD_GSM_TCP | 28 | 00028 | AlarmPMM2x17nad80[29]
GSMAlarmPMM2x17nad802 | DIGITAL | IOD_GSM_TCP | 29 | 00029 | AlarmPMM2x17nad80[2]
GSMAlarmPMM2x17nad8030 | DIGITAL | IOD_GSM_TCP | 30 | 00030 | AlarmPMM2x17nad80[30]
GSMAlarmPMM2x17nad8031 | DIGITAL | IOD_GSM_TCP | 31 | 00031 | AlarmPMM2x17nad80[31]
GSMAlarmPMM2x17nad8032 | DIGITAL | IOD_GSM_TCP | 32 | 00032 | AlarmPMM2x17nad80[32]
GSMAlarmPMM2x17nad8033 | DIGITAL | IOD_GSM_TCP | 33 | 00033 | AlarmPMM2x17nad80[33]
GSMAlarmPMM2x17nad8034 | DIGITAL | IOD_GSM_TCP | 34 | 00034 | AlarmPMM2x17nad80[34]
GSMAlarmPMM2x17nad8035 | DIGITAL | IOD_GSM_TCP | 35 | 00035 | AlarmPMM2x17nad80[35]
GSMAlarmPMM2x17nad8036 | DIGITAL | IOD_GSM_TCP | 36 | 00036 | AlarmPMM2x17nad80[36]
GSMAlarmPMM2x17nad8037 | DIGITAL | IOD_GSM_TCP | 37 | 00037 | AlarmPMM2x17nad80[37]
GSMAlarmPMM2x17nad8038 | DIGITAL | IOD_GSM_TCP | 38 | 00038 | AlarmPMM2x17nad80[38]
GSMAlarmPMM2x17nad8039 | DIGITAL | IOD_GSM_TCP | 39 | 00039 | AlarmPMM2x17nad80[39]
GSMAlarmPMM2x17nad803 | DIGITAL | IOD_GSM_TCP | 40 | 00040 | AlarmPMM2x17nad80[3]
GSMAlarmPMM2x17nad8040 | DIGITAL | IOD_GSM_TCP | 41 | 00041 | AlarmPMM2x17nad80[40]
GSMAlarmPMM2x17nad8041 | DIGITAL | IOD_GSM_TCP | 42 | 00042 | AlarmPMM2x17nad80[41]
GSMAlarmPMM2x17nad8042 | DIGITAL | IOD_GSM_TCP | 43 | 00043 | AlarmPMM2x17nad80[42]
GSMAlarmPMM2x17nad804 | DIGITAL | IOD_GSM_TCP | 44 | 00044 | AlarmPMM2x17nad80[4]
GSMAlarmPMM2x17nad805 | DIGITAL | IOD_GSM_TCP | 45 | 00045 | AlarmPMM2x17nad80[5]
GSMAlarmPMM2x17nad806 | DIGITAL | IOD_GSM_TCP | 46 | 00046 | AlarmPMM2x17nad80[6]
GSMAlarmPMM2x17nad807 | DIGITAL | IOD_GSM_TCP | 47 | 00047 | AlarmPMM2x17nad80[7]
GSMAlarmPMM2x17nad808 | DIGITAL | IOD_GSM_TCP | 48 | 00048 | AlarmPMM2x17nad80[8]
GSMAlarmPMM2x17nad809 | DIGITAL | IOD_GSM_TCP | 49 | 00049 | AlarmPMM2x17nad80[9]
GSMComError | DIGITAL | IOD_GSM_TCP | 50 | 00050 | ComError
GSMComSCADA | DIGITAL | IOD_GSM_TCP | 51 | 00051 | ComSCADA
GSMComSCADA1 | DIGITAL | IOD_GSM_TCP | 52 | 00052 | ComSCADA1
GSMComSCADA2 | DIGITAL | IOD_GSM_TCP | 53 | 00053 | ComSCADA2
GSMComSCADA3 | DIGITAL | IOD_GSM_TCP | 54 | 00054 | ComSCADA3
GSMErrComCirc1 | DIGITAL | IOD_GSM_TCP | 55 | 00055 | ErrComCirc[1]
GSMErrComKlima1 | DIGITAL | IOD_GSM_TCP | 56 | 00056 | ErrComKlima[1]
GSMErrComKlima2 | DIGITAL | IOD_GSM_TCP | 57 | 00057 | ErrComKlima[2]
GSMErrComPMM1 | DIGITAL | IOD_GSM_TCP | 58 | 00058 | ErrComPMM[1]
GSMErrComPort2 | DIGITAL | IOD_GSM_TCP | 59 | 00059 | ErrComPort2
GSMErrComPort3 | DIGITAL | IOD_GSM_TCP | 60 | 00060 | ErrComPort3
GSMErrComPort4 | DIGITAL | IOD_GSM_TCP | 61 | 00061 | ErrComPort4
GSMErrComUPS1 | DIGITAL | IOD_GSM_TCP | 62 | 00062 | ErrComUPS[1]
GSMErrComUPS2 | DIGITAL | IOD_GSM_TCP | 63 | 00063 | ErrComUPS[2]
GSMErrComUPSMGE1 | DIGITAL | IOD_GSM_TCP | 64 | 00064 | ErrComUPSMGE[1]
GSMErrorComCirc1Error | DIGITAL | IOD_GSM_TCP | 65 | 00065 | ErrorComCirc[1].Error
GSMErrorComKlima1Error | DIGITAL | IOD_GSM_TCP | 66 | 00066 | ErrorComKlima[1].Error
GSMErrorComKlima2Error | DIGITAL | IOD_GSM_TCP | 67 | 00067 | ErrorComKlima[2].Error
GSMErrorComPMM1Error | DIGITAL | IOD_GSM_TCP | 68 | 00068 | ErrorComPMM[1].Error
GSMErrorComUPS1Error | DIGITAL | IOD_GSM_TCP | 69 | 00069 | ErrorComUPS[1].Error
GSMErrorComUPS2Error | DIGITAL | IOD_GSM_TCP | 70 | 00070 | ErrorComUPS[2].Error
GSMErrorComUPSMGE1Error | DIGITAL | IOD_GSM_TCP | 71 | 00071 | ErrorComUPSMGE[1].Error
GSMF1_1_zascita_ok | DIGITAL | IOD_GSM_TCP | 72 | 00072 | F1_1_zascita_ok
GSMK1_SkupnaNapaka | DIGITAL | IOD_GSM_TCP | 73 | 00073 | K1_SkupnaNapaka
GSMK1AlarmPozara | DIGITAL | IOD_GSM_TCP | 74 | 00074 | K1AlarmPozara
GSMK1KlimaZdruzenAlarm | DIGITAL | IOD_GSM_TCP | 75 | 00075 | K1KlimaZdruzenAlarm
GSMK1NiPretoka | DIGITAL | IOD_GSM_TCP | 76 | 00076 | K1NiPretoka
GSMK1OkvaraRototerma | DIGITAL | IOD_GSM_TCP | 77 | 00077 | K1OkvaraRototerma
GSMK1OkvaraVlazNap | DIGITAL | IOD_GSM_TCP | 78 | 00078 | K1OkvaraVlazNap
GSMK1PreobMotCrpGr | DIGITAL | IOD_GSM_TCP | 79 | 00079 | K1PreobMotCrpGr
GSMK1PreobMotVent | DIGITAL | IOD_GSM_TCP | 80 | 00080 | K1PreobMotVent
GSMK1ProtizamrzZascAkt | DIGITAL | IOD_GSM_TCP | 81 | 00081 | K1ProtizamrzZascAkt
GSMK1ZamasenostFiltra | DIGITAL | IOD_GSM_TCP | 82 | 00082 | K1ZamasenostFiltra
GSMK2_SkupnaNapaka | DIGITAL | IOD_GSM_TCP | 83 | 00083 | K2_SkupnaNapaka
GSMK2AlarmPozara | DIGITAL | IOD_GSM_TCP | 84 | 00084 | K2AlarmPozara
GSMK2KlimaZdruzenAlarm | DIGITAL | IOD_GSM_TCP | 85 | 00085 | K2KlimaZdruzenAlarm
GSMK2NiPretoka | DIGITAL | IOD_GSM_TCP | 86 | 00086 | K2NiPretoka
GSMK2OkvaraRototerma | DIGITAL | IOD_GSM_TCP | 87 | 00087 | K2OkvaraRototerma
GSMK2OkvaraVlazNap | DIGITAL | IOD_GSM_TCP | 88 | 00088 | K2OkvaraVlazNap
GSMK2PreobMotCrpGr | DIGITAL | IOD_GSM_TCP | 89 | 00089 | K2PreobMotCrpGr
GSMK2PreobMotVent | DIGITAL | IOD_GSM_TCP | 90 | 00090 | K2PreobMotVent
GSMK2ProtizamrzZascAkt | DIGITAL | IOD_GSM_TCP | 91 | 00091 | K2ProtizamrzZascAkt
GSMK2ZamasenostFiltra | DIGITAL | IOD_GSM_TCP | 92 | 00092 | K2ZamasenostFiltra
GSMK3_deluje | DIGITAL | IOD_GSM_TCP | 93 | 00093 | K3_deluje
GSMK3_SkupnaNapaka | DIGITAL | IOD_GSM_TCP | 94 | 00094 | K3_SkupnaNapaka
GSMKlima1_izkljucena | DIGITAL | IOD_GSM_TCP | 95 | 00095 | Klima1_izkljucena
GSMKLIMA1_kke_pogon | DIGITAL | IOD_GSM_TCP | 96 | 00096 | KLIMA1_kke_pogon
GSMKLIMA1_krm_nap_ok | DIGITAL | IOD_GSM_TCP | 97 | 00097 | KLIMA1_krm_nap_ok
GSMKlima2_izkljucena | DIGITAL | IOD_GSM_TCP | 98 | 00098 | Klima2_izkljucena
GSMKlima3_izkljucena | DIGITAL | IOD_GSM_TCP | 99 | 00099 | Klima3_izkljucena
GSMKlima1Alarm_pozar | DIGITAL | IOD_GSM_TCP | 100 | 00100 | Klima[1].Alarm_pozar
GSMKlima1DelVentHit1 | DIGITAL | IOD_GSM_TCP | 101 | 00101 | Klima[1].DelVentHit1
GSMKlima1DelVentHit2 | DIGITAL | IOD_GSM_TCP | 102 | 00102 | Klima[1].DelVentHit2
GSMKlima1Ni_pretoka | DIGITAL | IOD_GSM_TCP | 103 | 00103 | Klima[1].Ni_pretoka
GSMKlima1OkvaraRototerm | DIGITAL | IOD_GSM_TCP | 104 | 00104 | Klima[1].OkvaraRototerm
GSMKlima1OkvaraVlazNap | DIGITAL | IOD_GSM_TCP | 105 | 00105 | Klima[1].OkvaraVlazNap
GSMKlima1PreobMotCrpGrel | DIGITAL | IOD_GSM_TCP | 106 | 00106 | Klima[1].PreobMotCrpGrel
GSMKlima1PreobMotVent | DIGITAL | IOD_GSM_TCP | 107 | 00107 | Klima[1].PreobMotVent
GSMKlima1ProtizamrzZascAktivna | DIGITAL | IOD_GSM_TCP | 108 | 00108 | Klima[1].ProtizamrzZascAktivna
GSMKlima1VklopRegKlimata | DIGITAL | IOD_GSM_TCP | 109 | 00109 | Klima[1].VklopRegKlimata
GSMKlima1ZamasenostFiltra | DIGITAL | IOD_GSM_TCP | 110 | 00110 | Klima[1].ZamasenostFiltra
GSMKlima1ZdruzAlarmA | DIGITAL | IOD_GSM_TCP | 111 | 00111 | Klima[1].ZdruzAlarmA
GSMKlima1ZdruzAlarmB | DIGITAL | IOD_GSM_TCP | 112 | 00112 | Klima[1].ZdruzAlarmB
GSMKlima2Alarm_pozar | DIGITAL | IOD_GSM_TCP | 113 | 00113 | Klima[2].Alarm_pozar
GSMKlima2DelVentHit1 | DIGITAL | IOD_GSM_TCP | 114 | 00114 | Klima[2].DelVentHit1
GSMKlima2DelVentHit2 | DIGITAL | IOD_GSM_TCP | 115 | 00115 | Klima[2].DelVentHit2
GSMKlima2Ni_pretoka | DIGITAL | IOD_GSM_TCP | 116 | 00116 | Klima[2].Ni_pretoka
GSMKlima2OkvaraRototerm | DIGITAL | IOD_GSM_TCP | 117 | 00117 | Klima[2].OkvaraRototerm
GSMKlima2OkvaraVlazNap | DIGITAL | IOD_GSM_TCP | 118 | 00118 | Klima[2].OkvaraVlazNap
GSMKlima2PreobMotCrpGrel | DIGITAL | IOD_GSM_TCP | 119 | 00119 | Klima[2].PreobMotCrpGrel
GSMKlima2PreobMotVent | DIGITAL | IOD_GSM_TCP | 120 | 00120 | Klima[2].PreobMotVent
GSMKlima2ProtizamrzZascAktivna | DIGITAL | IOD_GSM_TCP | 121 | 00121 | Klima[2].ProtizamrzZascAktivna
GSMKlima2VklopRegKlimata | DIGITAL | IOD_GSM_TCP | 122 | 00122 | Klima[2].VklopRegKlimata
GSMKlima2ZamasenostFiltra | DIGITAL | IOD_GSM_TCP | 123 | 00123 | Klima[2].ZamasenostFiltra
GSMKlima2ZdruzAlarmA | DIGITAL | IOD_GSM_TCP | 124 | 00124 | Klima[2].ZdruzAlarmA
GSMKlima2ZdruzAlarmB | DIGITAL | IOD_GSM_TCP | 125 | 00125 | Klima[2].ZdruzAlarmB
GSMKLIMA_m1_delovanje | DIGITAL | IOD_GSM_TCP | 126 | 00126 | KLIMA_m1_delovanje
GSMKLIMA_m1_napaka | DIGITAL | IOD_GSM_TCP | 127 | 00127 | KLIMA_m1_napaka
GSMKLIMA_m2_delovanje | DIGITAL | IOD_GSM_TCP | 128 | 00128 | KLIMA_m2_delovanje
GSMKLIMA_m2_napaka | DIGITAL | IOD_GSM_TCP | 129 | 00129 | KLIMA_m2_napaka
GSMKLIMAT1_delovanje | DIGITAL | IOD_GSM_TCP | 130 | 00130 | KLIMAT1_delovanje
GSMKLIMAT1_napaka | DIGITAL | IOD_GSM_TCP | 131 | 00131 | KLIMAT1_napaka
GSMKLIMAT1_vklop_delovanja | DIGITAL | IOD_GSM_TCP | 132 | 00132 | KLIMAT1_vklop_delovanja
GSMKLIMAT2_delovanje | DIGITAL | IOD_GSM_TCP | 133 | 00133 | KLIMAT2_delovanje
GSMKLIMAT2_napaka | DIGITAL | IOD_GSM_TCP | 134 | 00134 | KLIMAT2_napaka
GSMKLIMAT2_vklop_delovanja | DIGITAL | IOD_GSM_TCP | 135 | 00135 | KLIMAT2_vklop_delovanja
GSMKlimeAVTO | DIGITAL | IOD_GSM_TCP | 136 | 00136 | KlimeAVTO
GSMN_F1_1_zascita_ok | DIGITAL | IOD_GSM_TCP | 137 | 00137 | N_F1_1_zascita_ok
GSMN_KLIMA1_krm_nap_ok | DIGITAL | IOD_GSM_TCP | 138 | 00138 | N_KLIMA1_krm_nap_ok
GSMN_KLIMAT1_napaka | DIGITAL | IOD_GSM_TCP | 139 | 00139 | N_KLIMAT1_napaka
GSMN_KLIMAT2_napaka | DIGITAL | IOD_GSM_TCP | 140 | 00140 | N_KLIMAT2_napaka
GSMN_Q12_izpad | DIGITAL | IOD_GSM_TCP | 141 | 00141 | N_Q12_izpad
GSMN_UPS_A_V23_delovanje | DIGITAL | IOD_GSM_TCP | 142 | 00142 | N_UPS_A_V23_delovanje
GSMN_UPS_A_V23_napaka | DIGITAL | IOD_GSM_TCP | 143 | 00143 | N_UPS_A_V23_napaka
GSMN_UPS_V23_delovanje | DIGITAL | IOD_GSM_TCP | 144 | 00144 | N_UPS_V23_delovanje
GSMN_UPS_V23_napaka | DIGITAL | IOD_GSM_TCP | 145 | 00145 | N_UPS_V23_napaka
GSMN_UPS_V25_delovanje | DIGITAL | IOD_GSM_TCP | 146 | 00146 | N_UPS_V25_delovanje
GSMN_UPS_V25_napaka | DIGITAL | IOD_GSM_TCP | 147 | 00147 | N_UPS_V25_napaka
GSMN_VLAZILEC1_napaka | DIGITAL | IOD_GSM_TCP | 148 | 00148 | N_VLAZILEC1_napaka
GSMN_VLAZILEC2_napaka | DIGITAL | IOD_GSM_TCP | 149 | 00149 | N_VLAZILEC2_napaka
GSMnapaka_kom_panel | DIGITAL | IOD_GSM_TCP | 150 | 00150 | napaka_kom_panel
GSMnapaka_kom_scada | DIGITAL | IOD_GSM_TCP | 151 | 00151 | napaka_kom_scada
GSMnapaka_kom_scada2 | DIGITAL | IOD_GSM_TCP | 152 | 00152 | napaka_kom_scada2
GSMNapakaSenzorSkupno | DIGITAL | IOD_GSM_TCP | 153 | 00153 | NapakaSenzorSkupno
GSMNapakaSenzorVlagaHIA1 | DIGITAL | IOD_GSM_TCP | 154 | 00154 | NapakaSenzorVlagaHIA1
GSMNapakaSenzorVlagaHIA2 | DIGITAL | IOD_GSM_TCP | 155 | 00155 | NapakaSenzorVlagaHIA2
GSMNapakaSenzorVlagaHIA3 | DIGITAL | IOD_GSM_TCP | 156 | 00156 | NapakaSenzorVlagaHIA3
GSMNapakaSenzorVlagaHIA4 | DIGITAL | IOD_GSM_TCP | 157 | 00157 | NapakaSenzorVlagaHIA4
GSMNapakaSenzorVlagaHIA5 | DIGITAL | IOD_GSM_TCP | 158 | 00158 | NapakaSenzorVlagaHIA5
GSMNapakaSenzorVlagaHIA6 | DIGITAL | IOD_GSM_TCP | 159 | 00159 | NapakaSenzorVlagaHIA6
GSMNapakaSenzorVlagaHIA7 | DIGITAL | IOD_GSM_TCP | 160 | 00160 | NapakaSenzorVlagaHIA7
GSMNapakaTSTempTIA1 | DIGITAL | IOD_GSM_TCP | 161 | 00161 | NapakaTSTempTIA1
GSMNapakaTSTempTIA2 | DIGITAL | IOD_GSM_TCP | 162 | 00162 | NapakaTSTempTIA2
GSMNapakaTSTempTIA3 | DIGITAL | IOD_GSM_TCP | 163 | 00163 | NapakaTSTempTIA3
GSMNapakaTSTempTIA4 | DIGITAL | IOD_GSM_TCP | 164 | 00164 | NapakaTSTempTIA4
GSMNapakaTSTempTIA5 | DIGITAL | IOD_GSM_TCP | 165 | 00165 | NapakaTSTempTIA5
GSMNapakaTSTempTIA6 | DIGITAL | IOD_GSM_TCP | 166 | 00166 | NapakaTSTempTIA6
GSMNapakaTSTempTIA7 | DIGITAL | IOD_GSM_TCP | 167 | 00167 | NapakaTSTempTIA7
GSMOpozoriloPMM2x17med60in8010 | DIGITAL | IOD_GSM_TCP | 168 | 00168 | OpozoriloPMM2x17med60in80[10]
GSMOpozoriloPMM2x17med60in8011 | DIGITAL | IOD_GSM_TCP | 169 | 00169 | OpozoriloPMM2x17med60in80[11]
GSMOpozoriloPMM2x17med60in8012 | DIGITAL | IOD_GSM_TCP | 170 | 00170 | OpozoriloPMM2x17med60in80[12]
GSMOpozoriloPMM2x17med60in8013 | DIGITAL | IOD_GSM_TCP | 171 | 00171 | OpozoriloPMM2x17med60in80[13]
GSMOpozoriloPMM2x17med60in8014 | DIGITAL | IOD_GSM_TCP | 172 | 00172 | OpozoriloPMM2x17med60in80[14]
GSMOpozoriloPMM2x17med60in8015 | DIGITAL | IOD_GSM_TCP | 173 | 00173 | OpozoriloPMM2x17med60in80[15]
GSMOpozoriloPMM2x17med60in8016 | DIGITAL | IOD_GSM_TCP | 174 | 00174 | OpozoriloPMM2x17med60in80[16]
GSMOpozoriloPMM2x17med60in8017 | DIGITAL | IOD_GSM_TCP | 175 | 00175 | OpozoriloPMM2x17med60in80[17]
GSMOpozoriloPMM2x17med60in8018 | DIGITAL | IOD_GSM_TCP | 176 | 00176 | OpozoriloPMM2x17med60in80[18]
GSMOpozoriloPMM2x17med60in8019 | DIGITAL | IOD_GSM_TCP | 177 | 00177 | OpozoriloPMM2x17med60in80[19]
GSMOpozoriloPMM2x17med60in801 | DIGITAL | IOD_GSM_TCP | 178 | 00178 | OpozoriloPMM2x17med60in80[1]
GSMOpozoriloPMM2x17med60in8020 | DIGITAL | IOD_GSM_TCP | 179 | 00179 | OpozoriloPMM2x17med60in80[20]
GSMOpozoriloPMM2x17med60in8021 | DIGITAL | IOD_GSM_TCP | 180 | 00180 | OpozoriloPMM2x17med60in80[21]
GSMOpozoriloPMM2x17med60in8022 | DIGITAL | IOD_GSM_TCP | 181 | 00181 | OpozoriloPMM2x17med60in80[22]
GSMOpozoriloPMM2x17med60in8023 | DIGITAL | IOD_GSM_TCP | 182 | 00182 | OpozoriloPMM2x17med60in80[23]
GSMOpozoriloPMM2x17med60in8024 | DIGITAL | IOD_GSM_TCP | 183 | 00183 | OpozoriloPMM2x17med60in80[24]
GSMOpozoriloPMM2x17med60in8025 | DIGITAL | IOD_GSM_TCP | 184 | 00184 | OpozoriloPMM2x17med60in80[25]
GSMOpozoriloPMM2x17med60in8026 | DIGITAL | IOD_GSM_TCP | 185 | 00185 | OpozoriloPMM2x17med60in80[26]
GSMOpozoriloPMM2x17med60in8027 | DIGITAL | IOD_GSM_TCP | 186 | 00186 | OpozoriloPMM2x17med60in80[27]
GSMOpozoriloPMM2x17med60in8028 | DIGITAL | IOD_GSM_TCP | 187 | 00187 | OpozoriloPMM2x17med60in80[28]
GSMOpozoriloPMM2x17med60in8029 | DIGITAL | IOD_GSM_TCP | 188 | 00188 | OpozoriloPMM2x17med60in80[29]
GSMOpozoriloPMM2x17med60in802 | DIGITAL | IOD_GSM_TCP | 189 | 00189 | OpozoriloPMM2x17med60in80[2]
GSMOpozoriloPMM2x17med60in8030 | DIGITAL | IOD_GSM_TCP | 190 | 00190 | OpozoriloPMM2x17med60in80[30]
GSMOpozoriloPMM2x17med60in8031 | DIGITAL | IOD_GSM_TCP | 191 | 00191 | OpozoriloPMM2x17med60in80[31]
GSMOpozoriloPMM2x17med60in8032 | DIGITAL | IOD_GSM_TCP | 192 | 00192 | OpozoriloPMM2x17med60in80[32]
GSMOpozoriloPMM2x17med60in8033 | DIGITAL | IOD_GSM_TCP | 193 | 00193 | OpozoriloPMM2x17med60in80[33]
GSMOpozoriloPMM2x17med60in8034 | DIGITAL | IOD_GSM_TCP | 194 | 00194 | OpozoriloPMM2x17med60in80[34]
GSMOpozoriloPMM2x17med60in8035 | DIGITAL | IOD_GSM_TCP | 195 | 00195 | OpozoriloPMM2x17med60in80[35]
GSMOpozoriloPMM2x17med60in8036 | DIGITAL | IOD_GSM_TCP | 196 | 00196 | OpozoriloPMM2x17med60in80[36]
GSMOpozoriloPMM2x17med60in8037 | DIGITAL | IOD_GSM_TCP | 197 | 00197 | OpozoriloPMM2x17med60in80[37]
GSMOpozoriloPMM2x17med60in8038 | DIGITAL | IOD_GSM_TCP | 198 | 00198 | OpozoriloPMM2x17med60in80[38]
GSMOpozoriloPMM2x17med60in8039 | DIGITAL | IOD_GSM_TCP | 199 | 00199 | OpozoriloPMM2x17med60in80[39]
GSMOpozoriloPMM2x17med60in803 | DIGITAL | IOD_GSM_TCP | 200 | 00200 | OpozoriloPMM2x17med60in80[3]
GSMOpozoriloPMM2x17med60in8040 | DIGITAL | IOD_GSM_TCP | 201 | 00201 | OpozoriloPMM2x17med60in80[40]
GSMOpozoriloPMM2x17med60in8041 | DIGITAL | IOD_GSM_TCP | 202 | 00202 | OpozoriloPMM2x17med60in80[41]
GSMOpozoriloPMM2x17med60in8042 | DIGITAL | IOD_GSM_TCP | 203 | 00203 | OpozoriloPMM2x17med60in80[42]
GSMOpozoriloPMM2x17med60in804 | DIGITAL | IOD_GSM_TCP | 204 | 00204 | OpozoriloPMM2x17med60in80[4]
GSMOpozoriloPMM2x17med60in805 | DIGITAL | IOD_GSM_TCP | 205 | 00205 | OpozoriloPMM2x17med60in80[5]
GSMOpozoriloPMM2x17med60in806 | DIGITAL | IOD_GSM_TCP | 206 | 00206 | OpozoriloPMM2x17med60in80[6]
GSMOpozoriloPMM2x17med60in807 | DIGITAL | IOD_GSM_TCP | 207 | 00207 | OpozoriloPMM2x17med60in80[7]
GSMOpozoriloPMM2x17med60in808 | DIGITAL | IOD_GSM_TCP | 208 | 00208 | OpozoriloPMM2x17med60in80[8]
GSMOpozoriloPMM2x17med60in809 | DIGITAL | IOD_GSM_TCP | 209 | 00209 | OpozoriloPMM2x17med60in80[9]
GSMPMM1OverCurrentBetw1 | DIGITAL | IOD_GSM_TCP | 210 | 00210 | PMM1OverCurrentBetw[1]
GSMPMM1OverCurrentBetw2 | DIGITAL | IOD_GSM_TCP | 211 | 00211 | PMM1OverCurrentBetw[2]
GSMPMM1OverCurrentBetw3 | DIGITAL | IOD_GSM_TCP | 212 | 00212 | PMM1OverCurrentBetw[3]
GSMPMM1OverCurrentOver1 | DIGITAL | IOD_GSM_TCP | 213 | 00213 | PMM1OverCurrentOver[1]
GSMPMM1OverCurrentOver2 | DIGITAL | IOD_GSM_TCP | 214 | 00214 | PMM1OverCurrentOver[2]
GSMPMM1OverCurrentOver3 | DIGITAL | IOD_GSM_TCP | 215 | 00215 | PMM1OverCurrentOver[3]
GSMPrevisokaTemp | DIGITAL | IOD_GSM_TCP | 216 | 00216 | PrevisokaTemp
GSMQ0_izkljuceno | DIGITAL | IOD_GSM_TCP | 217 | 00217 | Q0_izkljuceno
GSMQ0_vkljuceno | DIGITAL | IOD_GSM_TCP | 218 | 00218 | Q0_vkljuceno
GSMQ12_izkljuceno | DIGITAL | IOD_GSM_TCP | 219 | 00219 | Q12_izkljuceno
GSMQ12_izpad | DIGITAL | IOD_GSM_TCP | 220 | 00220 | Q12_izpad
GSMQ12_vkljuceno | DIGITAL | IOD_GSM_TCP | 221 | 00221 | Q12_vkljuceno
GSMrazlitjeLAH1 | DIGITAL | IOD_GSM_TCP | 222 | 00222 | razlitjeLAH1
GSMrazlitjeLAH2 | DIGITAL | IOD_GSM_TCP | 223 | 00223 | razlitjeLAH2
GSMrazlitjeLAH3 | DIGITAL | IOD_GSM_TCP | 224 | 00224 | razlitjeLAH3
GSMrazlitjeLAH4 | DIGITAL | IOD_GSM_TCP | 225 | 00225 | razlitjeLAH4
GSMSetDateTime | DIGITAL | IOD_GSM_TCP | 226 | 00226 | SetDateTime
GSMSetDateTimeDemand | DIGITAL | IOD_GSM_TCP | 227 | 00227 | SetDateTimeDemand
GSMSetDateTimeError | DIGITAL | IOD_GSM_TCP | 228 | 00228 | SetDateTimeError
GSMSetDateTimeFinished | DIGITAL | IOD_GSM_TCP | 229 | 00229 | SetDateTimeFinished
GSMSkupneNapakeNaprav_PMM17VirBVirA | DIGITAL | IOD_GSM_TCP | 230 | 00230 | SkupneNapakeNaprav_PMM17VirBVirA
GSMSlabaBaterijaPLC | DIGITAL | IOD_GSM_TCP | 231 | 00231 | SlabaBaterijaPLC
GSMTempPovp234Previs | DIGITAL | IOD_GSM_TCP | 232 | 00232 | TempPovp234Previs
GSMTempPovp56Previs | DIGITAL | IOD_GSM_TCP | 233 | 00233 | TempPovp56Previs
GSMTIA1_previs_temp | DIGITAL | IOD_GSM_TCP | 234 | 00234 | TIA1_previs_temp
GSMTIA2_previs_temp | DIGITAL | IOD_GSM_TCP | 235 | 00235 | TIA2_previs_temp
GSMTIA3_previs_temp | DIGITAL | IOD_GSM_TCP | 236 | 00236 | TIA3_previs_temp
GSMTIA4_previs_temp | DIGITAL | IOD_GSM_TCP | 237 | 00237 | TIA4_previs_temp
GSMTIA5_previs_temp | DIGITAL | IOD_GSM_TCP | 238 | 00238 | TIA5_previs_temp
GSMTIA6_previs_temp | DIGITAL | IOD_GSM_TCP | 239 | 00239 | TIA6_previs_temp
GSMTIA7_previs_temp | DIGITAL | IOD_GSM_TCP | 240 | 00240 | TIA7_previs_temp
GSMUPS1Errors10 | DIGITAL | IOD_GSM_TCP | 241 | 00241 | UPS1Errors[10]
GSMUPS1Errors11 | DIGITAL | IOD_GSM_TCP | 242 | 00242 | UPS1Errors[11]
GSMUPS1Errors12 | DIGITAL | IOD_GSM_TCP | 243 | 00243 | UPS1Errors[12]
GSMUPS1Errors13 | DIGITAL | IOD_GSM_TCP | 244 | 00244 | UPS1Errors[13]
GSMUPS1Errors14 | DIGITAL | IOD_GSM_TCP | 245 | 00245 | UPS1Errors[14]
GSMUPS1Errors15 | DIGITAL | IOD_GSM_TCP | 246 | 00246 | UPS1Errors[15]
GSMUPS1Errors16 | DIGITAL | IOD_GSM_TCP | 247 | 00247 | UPS1Errors[16]
GSMUPS1Errors17 | DIGITAL | IOD_GSM_TCP | 248 | 00248 | UPS1Errors[17]
GSMUPS1Errors18 | DIGITAL | IOD_GSM_TCP | 249 | 00249 | UPS1Errors[18]
GSMUPS1Errors19 | DIGITAL | IOD_GSM_TCP | 250 | 00250 | UPS1Errors[19]
GSMUPS1Errors1 | DIGITAL | IOD_GSM_TCP | 251 | 00251 | UPS1Errors[1]
GSMUPS1Errors20 | DIGITAL | IOD_GSM_TCP | 252 | 00252 | UPS1Errors[20]
GSMUPS1Errors21 | DIGITAL | IOD_GSM_TCP | 253 | 00253 | UPS1Errors[21]
GSMUPS1Errors22 | DIGITAL | IOD_GSM_TCP | 254 | 00254 | UPS1Errors[22]
GSMUPS1Errors23 | DIGITAL | IOD_GSM_TCP | 255 | 00255 | UPS1Errors[23]
GSMUPS1Errors24 | DIGITAL | IOD_GSM_TCP | 256 | 00256 | UPS1Errors[24]
GSMUPS1Errors25 | DIGITAL | IOD_GSM_TCP | 257 | 00257 | UPS1Errors[25]
GSMUPS1Errors2 | DIGITAL | IOD_GSM_TCP | 258 | 00258 | UPS1Errors[2]
GSMUPS1Errors3 | DIGITAL | IOD_GSM_TCP | 259 | 00259 | UPS1Errors[3]
GSMUPS1Errors4 | DIGITAL | IOD_GSM_TCP | 260 | 00260 | UPS1Errors[4]
GSMUPS1Errors5 | DIGITAL | IOD_GSM_TCP | 261 | 00261 | UPS1Errors[5]
GSMUPS1Errors6 | DIGITAL | IOD_GSM_TCP | 262 | 00262 | UPS1Errors[6]
GSMUPS1Errors7 | DIGITAL | IOD_GSM_TCP | 263 | 00263 | UPS1Errors[7]
GSMUPS1Errors8 | DIGITAL | IOD_GSM_TCP | 264 | 00264 | UPS1Errors[8]
GSMUPS1Errors9 | DIGITAL | IOD_GSM_TCP | 265 | 00265 | UPS1Errors[9]
GSMUPS2Errors10 | DIGITAL | IOD_GSM_TCP | 266 | 00266 | UPS2Errors[10]
GSMUPS2Errors11 | DIGITAL | IOD_GSM_TCP | 267 | 00267 | UPS2Errors[11]
GSMUPS2Errors12 | DIGITAL | IOD_GSM_TCP | 268 | 00268 | UPS2Errors[12]
GSMUPS2Errors13 | DIGITAL | IOD_GSM_TCP | 269 | 00269 | UPS2Errors[13]
GSMUPS2Errors14 | DIGITAL | IOD_GSM_TCP | 270 | 00270 | UPS2Errors[14]
GSMUPS2Errors15 | DIGITAL | IOD_GSM_TCP | 271 | 00271 | UPS2Errors[15]
GSMUPS2Errors16 | DIGITAL | IOD_GSM_TCP | 272 | 00272 | UPS2Errors[16]
GSMUPS2Errors17 | DIGITAL | IOD_GSM_TCP | 273 | 00273 | UPS2Errors[17]
GSMUPS2Errors18 | DIGITAL | IOD_GSM_TCP | 274 | 00274 | UPS2Errors[18]
GSMUPS2Errors19 | DIGITAL | IOD_GSM_TCP | 275 | 00275 | UPS2Errors[19]
GSMUPS2Errors1 | DIGITAL | IOD_GSM_TCP | 276 | 00276 | UPS2Errors[1]
GSMUPS2Errors20 | DIGITAL | IOD_GSM_TCP | 277 | 00277 | UPS2Errors[20]
GSMUPS2Errors21 | DIGITAL | IOD_GSM_TCP | 278 | 00278 | UPS2Errors[21]
GSMUPS2Errors22 | DIGITAL | IOD_GSM_TCP | 279 | 00279 | UPS2Errors[22]
GSMUPS2Errors23 | DIGITAL | IOD_GSM_TCP | 280 | 00280 | UPS2Errors[23]
GSMUPS2Errors24 | DIGITAL | IOD_GSM_TCP | 281 | 00281 | UPS2Errors[24]
GSMUPS2Errors25 | DIGITAL | IOD_GSM_TCP | 282 | 00282 | UPS2Errors[25]
GSMUPS2Errors2 | DIGITAL | IOD_GSM_TCP | 283 | 00283 | UPS2Errors[2]
GSMUPS2Errors3 | DIGITAL | IOD_GSM_TCP | 284 | 00284 | UPS2Errors[3]
GSMUPS2Errors4 | DIGITAL | IOD_GSM_TCP | 285 | 00285 | UPS2Errors[4]
GSMUPS2Errors5 | DIGITAL | IOD_GSM_TCP | 286 | 00286 | UPS2Errors[5]
GSMUPS2Errors6 | DIGITAL | IOD_GSM_TCP | 287 | 00287 | UPS2Errors[6]
GSMUPS2Errors7 | DIGITAL | IOD_GSM_TCP | 288 | 00288 | UPS2Errors[7]
GSMUPS2Errors8 | DIGITAL | IOD_GSM_TCP | 289 | 00289 | UPS2Errors[8]
GSMUPS2Errors9 | DIGITAL | IOD_GSM_TCP | 290 | 00290 | UPS2Errors[9]
GSMUPS1AlarmAwaitingPower | DIGITAL | IOD_GSM_TCP | 291 | 00291 | UPS[1].AlarmAwaitingPower
GSMUPS1AlarmBypassBad | DIGITAL | IOD_GSM_TCP | 292 | 00292 | UPS[1].AlarmBypassBad
GSMUPS1AlarmChargerFailed | DIGITAL | IOD_GSM_TCP | 293 | 00293 | UPS[1].AlarmChargerFailed
GSMUPS1AlarmCommunicationsLost | DIGITAL | IOD_GSM_TCP | 294 | 00294 | UPS[1].AlarmCommunicationsLost
GSMUPS1AlarmDepletedBattery | DIGITAL | IOD_GSM_TCP | 295 | 00295 | UPS[1].AlarmDepletedBattery
GSMUPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM_TCP | 296 | 00296 | UPS[1].AlarmDiagnosticTestFailed
GSMUPS1AlarmInverterError | DIGITAL | IOD_GSM_TCP | 297 | 00297 | UPS[1].AlarmInverterError
GSMUPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 298 | 00298 | UPS[1].AlarmIzhodOffKotZahtevano
GSMUPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM_TCP | 299 | 00299 | UPS[1].AlarmIzhodPreobremenjen
GSMUPS1AlarmLowBattery | DIGITAL | IOD_GSM_TCP | 300 | 00300 | UPS[1].AlarmLowBattery
GSMUPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM_TCP | 301 | 00301 | UPS[1].AlarmNapakaNaVarovalki
GSMUPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM_TCP | 302 | 00302 | UPS[1].AlarmNapakaNaVentilatorju
GSMUPS1AlarmOnBattery | DIGITAL | IOD_GSM_TCP | 303 | 00303 | UPS[1].AlarmOnBattery
GSMUPS1AlarmOnBypass | DIGITAL | IOD_GSM_TCP | 304 | 00304 | UPS[1].AlarmOnBypass
GSMUPS1AlarmShutdownImminent | DIGITAL | IOD_GSM_TCP | 305 | 00305 | UPS[1].AlarmShutdownImminent
GSMUPS1AlarmShutdownPending | DIGITAL | IOD_GSM_TCP | 306 | 00306 | UPS[1].AlarmShutdownPending
GSMUPS1AlarmSlabaBaterija | DIGITAL | IOD_GSM_TCP | 307 | 00307 | UPS[1].AlarmSlabaBaterija
GSMUPS1AlarmSplosnaNapaka | DIGITAL | IOD_GSM_TCP | 308 | 00308 | UPS[1].AlarmSplosnaNapaka
GSMUPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 309 | 00309 | UPS[1].AlarmStanjeIzhodaIzvenToleranc
GSMUPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 310 | 00310 | UPS[1].AlarmStanjeVhodaIzvenToleranc
GSMUPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 311 | 00311 | UPS[1].AlarmTemperaturaIzvenToleranc
GSMUPS1AlarmTestInProgres | DIGITAL | IOD_GSM_TCP | 312 | 00312 | UPS[1].AlarmTestInProgres
GSMUPS1AlarmUPSIzhodOff | DIGITAL | IOD_GSM_TCP | 313 | 00313 | UPS[1].AlarmUPSIzhodOff
GSMUPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 314 | 00314 | UPS[1].AlarmUPSOffKotZahtevano
GSMUPS1AlarmUPSSystemOff | DIGITAL | IOD_GSM_TCP | 315 | 00315 | UPS[1].AlarmUPSSystemOff
GSMUPS1Napaka | DIGITAL | IOD_GSM_TCP | 316 | 00316 | UPS[1].Napaka
GSMUPS1StatusEcomodeAktiven | DIGITAL | IOD_GSM_TCP | 317 | 00317 | UPS[1].StatusEcomodeAktiven
GSMUPS1StatusInverterIsOn | DIGITAL | IOD_GSM_TCP | 318 | 00318 | UPS[1].StatusInverterIsOn
GSMUPS1StatusStopOperation | DIGITAL | IOD_GSM_TCP | 319 | 00319 | UPS[1].StatusStopOperation
GSMUPS2AlarmAwaitingPower | DIGITAL | IOD_GSM_TCP | 320 | 00320 | UPS[2].AlarmAwaitingPower
GSMUPS2AlarmBypassBad | DIGITAL | IOD_GSM_TCP | 321 | 00321 | UPS[2].AlarmBypassBad
GSMUPS2AlarmChargerFailed | DIGITAL | IOD_GSM_TCP | 322 | 00322 | UPS[2].AlarmChargerFailed
GSMUPS2AlarmCommunicationsLost | DIGITAL | IOD_GSM_TCP | 323 | 00323 | UPS[2].AlarmCommunicationsLost
GSMUPS2AlarmDepletedBattery | DIGITAL | IOD_GSM_TCP | 324 | 00324 | UPS[2].AlarmDepletedBattery
GSMUPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM_TCP | 325 | 00325 | UPS[2].AlarmDiagnosticTestFailed
GSMUPS2AlarmInverterError | DIGITAL | IOD_GSM_TCP | 326 | 00326 | UPS[2].AlarmInverterError
GSMUPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 327 | 00327 | UPS[2].AlarmIzhodOffKotZahtevano
GSMUPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM_TCP | 328 | 00328 | UPS[2].AlarmIzhodPreobremenjen
GSMUPS2AlarmLowBattery | DIGITAL | IOD_GSM_TCP | 329 | 00329 | UPS[2].AlarmLowBattery
GSMUPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM_TCP | 330 | 00330 | UPS[2].AlarmNapakaNaVarovalki
GSMUPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM_TCP | 331 | 00331 | UPS[2].AlarmNapakaNaVentilatorju
GSMUPS2AlarmOnBattery | DIGITAL | IOD_GSM_TCP | 332 | 00332 | UPS[2].AlarmOnBattery
GSMUPS2AlarmOnBypass | DIGITAL | IOD_GSM_TCP | 333 | 00333 | UPS[2].AlarmOnBypass
GSMUPS2AlarmShutdownImminent | DIGITAL | IOD_GSM_TCP | 334 | 00334 | UPS[2].AlarmShutdownImminent
GSMUPS2AlarmShutdownPending | DIGITAL | IOD_GSM_TCP | 335 | 00335 | UPS[2].AlarmShutdownPending
GSMUPS2AlarmSlabaBaterija | DIGITAL | IOD_GSM_TCP | 336 | 00336 | UPS[2].AlarmSlabaBaterija
GSMUPS2AlarmSplosnaNapaka | DIGITAL | IOD_GSM_TCP | 337 | 00337 | UPS[2].AlarmSplosnaNapaka
GSMUPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 338 | 00338 | UPS[2].AlarmStanjeIzhodaIzvenToleranc
GSMUPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 339 | 00339 | UPS[2].AlarmStanjeVhodaIzvenToleranc
GSMUPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 340 | 00340 | UPS[2].AlarmTemperaturaIzvenToleranc
GSMUPS2AlarmTestInProgres | DIGITAL | IOD_GSM_TCP | 341 | 00341 | UPS[2].AlarmTestInProgres
GSMUPS2AlarmUPSIzhodOff | DIGITAL | IOD_GSM_TCP | 342 | 00342 | UPS[2].AlarmUPSIzhodOff
GSMUPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 343 | 00343 | UPS[2].AlarmUPSOffKotZahtevano
GSMUPS2AlarmUPSSystemOff | DIGITAL | IOD_GSM_TCP | 344 | 00344 | UPS[2].AlarmUPSSystemOff
GSMUPS2Napaka | DIGITAL | IOD_GSM_TCP | 345 | 00345 | UPS[2].Napaka
GSMUPS2StatusEcomodeAktiven | DIGITAL | IOD_GSM_TCP | 346 | 00346 | UPS[2].StatusEcomodeAktiven
GSMUPS2StatusInverterIsOn | DIGITAL | IOD_GSM_TCP | 347 | 00347 | UPS[2].StatusInverterIsOn
GSMUPS2StatusStopOperation | DIGITAL | IOD_GSM_TCP | 348 | 00348 | UPS[2].StatusStopOperation
GSMUPS_A_V23_delovanje | DIGITAL | IOD_GSM_TCP | 349 | 00349 | UPS_A_V23_delovanje
GSMUPS_A_V23_napaka | DIGITAL | IOD_GSM_TCP | 350 | 00350 | UPS_A_V23_napaka
GSMups_alarm | DIGITAL | IOD_GSM_TCP | 351 | 00351 | ups_alarm
GSMups_baterijski_nac | DIGITAL | IOD_GSM_TCP | 352 | 00352 | ups_baterijski_nac
GSMUPS_MGE1BatteryChargedState | DIGITAL | IOD_GSM_TCP | 353 | 00353 | UPS_MGE[1].BatteryChargedState
GSMUPS_MGE1BatteryCircuitBreaker | DIGITAL | IOD_GSM_TCP | 354 | 00354 | UPS_MGE[1].BatteryCircuitBreaker
GSMUPS_MGE1BatteryCompInProgress | DIGITAL | IOD_GSM_TCP | 355 | 00355 | UPS_MGE[1].BatteryCompInProgress
GSMUPS_MGE1BatteryFuseFault | DIGITAL | IOD_GSM_TCP | 356 | 00356 | UPS_MGE[1].BatteryFuseFault
GSMUPS_MGE1BatteryLowWarning | DIGITAL | IOD_GSM_TCP | 357 | 00357 | UPS_MGE[1].BatteryLowWarning
GSMUPS_MGE1BatteryTempOutOfToler | DIGITAL | IOD_GSM_TCP | 358 | 00358 | UPS_MGE[1].BatteryTempOutOfToler
GSMUPS_MGE1BypassInFreeFrequency | DIGITAL | IOD_GSM_TCP | 359 | 00359 | UPS_MGE[1].BypassInFreeFrequency
GSMUPS_MGE1ChargerGeneralFault | DIGITAL | IOD_GSM_TCP | 360 | 00360 | UPS_MGE[1].ChargerGeneralFault
GSMUPS_MGE1DeviceVentilationFault | DIGITAL | IOD_GSM_TCP | 361 | 00361 | UPS_MGE[1].DeviceVentilationFault
GSMUPS_MGE1InverterFuseFault | DIGITAL | IOD_GSM_TCP | 362 | 00362 | UPS_MGE[1].InverterFuseFault
GSMUPS_MGE1InverterOverload | DIGITAL | IOD_GSM_TCP | 363 | 00363 | UPS_MGE[1].InverterOverload
GSMUPS_MGE1InverterThermalOverload | DIGITAL | IOD_GSM_TCP | 364 | 00364 | UPS_MGE[1].InverterThermalOverload
GSMUPS_MGE1Mains1VoltOutOfToler | DIGITAL | IOD_GSM_TCP | 365 | 00365 | UPS_MGE[1].Mains1VoltOutOfToler
GSMUPS_MGE1Mains2Overload | DIGITAL | IOD_GSM_TCP | 366 | 00366 | UPS_MGE[1].Mains2Overload
GSMUPS_MGE1Mains2VoltOutOfToler | DIGITAL | IOD_GSM_TCP | 367 | 00367 | UPS_MGE[1].Mains2VoltOutOfToler
GSMUPS_MGE1MaintenancePosition | DIGITAL | IOD_GSM_TCP | 368 | 00368 | UPS_MGE[1].MaintenancePosition
GSMUPS_MGE1ManualBypassSwitch | DIGITAL | IOD_GSM_TCP | 369 | 00369 | UPS_MGE[1].ManualBypassSwitch
GSMUPS_MGE1NapakaNaVarovalkah | DIGITAL | IOD_GSM_TCP | 370 | 00370 | UPS_MGE[1].NapakaNaVarovalkah
GSMUPS_MGE1OutputInShortCircuit | DIGITAL | IOD_GSM_TCP | 371 | 00371 | UPS_MGE[1].OutputInShortCircuit
GSMUPS_MGE1OutputOverload | DIGITAL | IOD_GSM_TCP | 372 | 00372 | UPS_MGE[1].OutputOverload
GSMUPS_MGE1OutputThermalOverload | DIGITAL | IOD_GSM_TCP | 373 | 00373 | UPS_MGE[1].OutputThermalOverload
GSMUPS_MGE1RectifierOn | DIGITAL | IOD_GSM_TCP | 374 | 00374 | UPS_MGE[1].RectifierOn
GSMUPS_MGE1RectifierThermOverload | DIGITAL | IOD_GSM_TCP | 375 | 00375 | UPS_MGE[1].RectifierThermOverload
GSMUPS_MGE1Skupna_napaka | DIGITAL | IOD_GSM_TCP | 376 | 00376 | UPS_MGE[1].Skupna_napaka
GSMUPS_MGE1UPS_coupled | DIGITAL | IOD_GSM_TCP | 377 | 00377 | UPS_MGE[1].UPS_coupled
GSMUPS_MGE1UPS_error | DIGITAL | IOD_GSM_TCP | 378 | 00378 | UPS_MGE[1].UPS_error
GSMUPS_MGE1UPS_in_backup | DIGITAL | IOD_GSM_TCP | 379 | 00379 | UPS_MGE[1].UPS_in_backup
GSMups_polnjenje | DIGITAL | IOD_GSM_TCP | 380 | 00380 | ups_polnjenje
GSMUPS_V23_delovanje | DIGITAL | IOD_GSM_TCP | 381 | 00381 | UPS_V23_delovanje
GSMUPS_V23_napaka | DIGITAL | IOD_GSM_TCP | 382 | 00382 | UPS_V23_napaka
GSMUPS_V25_delovanje | DIGITAL | IOD_GSM_TCP | 383 | 00383 | UPS_V25_delovanje
GSMUPS_V25_napaka | DIGITAL | IOD_GSM_TCP | 384 | 00384 | UPS_V25_napaka
GSMUPSMGEErrors10 | DIGITAL | IOD_GSM_TCP | 385 | 00385 | UPSMGEErrors[10]
GSMUPSMGEErrors11 | DIGITAL | IOD_GSM_TCP | 386 | 00386 | UPSMGEErrors[11]
GSMUPSMGEErrors12 | DIGITAL | IOD_GSM_TCP | 387 | 00387 | UPSMGEErrors[12]
GSMUPSMGEErrors13 | DIGITAL | IOD_GSM_TCP | 388 | 00388 | UPSMGEErrors[13]
GSMUPSMGEErrors14 | DIGITAL | IOD_GSM_TCP | 389 | 00389 | UPSMGEErrors[14]
GSMUPSMGEErrors15 | DIGITAL | IOD_GSM_TCP | 390 | 00390 | UPSMGEErrors[15]
GSMUPSMGEErrors16 | DIGITAL | IOD_GSM_TCP | 391 | 00391 | UPSMGEErrors[16]
GSMUPSMGEErrors17 | DIGITAL | IOD_GSM_TCP | 392 | 00392 | UPSMGEErrors[17]
GSMUPSMGEErrors1 | DIGITAL | IOD_GSM_TCP | 393 | 00393 | UPSMGEErrors[1]
GSMUPSMGEErrors2 | DIGITAL | IOD_GSM_TCP | 394 | 00394 | UPSMGEErrors[2]
GSMUPSMGEErrors3 | DIGITAL | IOD_GSM_TCP | 395 | 00395 | UPSMGEErrors[3]
GSMUPSMGEErrors4 | DIGITAL | IOD_GSM_TCP | 396 | 00396 | UPSMGEErrors[4]
GSMUPSMGEErrors5 | DIGITAL | IOD_GSM_TCP | 397 | 00397 | UPSMGEErrors[5]
GSMUPSMGEErrors6 | DIGITAL | IOD_GSM_TCP | 398 | 00398 | UPSMGEErrors[6]
GSMUPSMGEErrors7 | DIGITAL | IOD_GSM_TCP | 399 | 00399 | UPSMGEErrors[7]
GSMUPSMGEErrors8 | DIGITAL | IOD_GSM_TCP | 400 | 00400 | UPSMGEErrors[8]
GSMUPSMGEErrors9 | DIGITAL | IOD_GSM_TCP | 401 | 00401 | UPSMGEErrors[9]
GSMUserLoggedIn | DIGITAL | IOD_GSM_TCP | 402 | 00402 | UserLoggedIn
GSMVLAZILEC1_delovanje | DIGITAL | IOD_GSM_TCP | 403 | 00403 | VLAZILEC1_delovanje
GSMVLAZILEC1_napaka | DIGITAL | IOD_GSM_TCP | 404 | 00404 | VLAZILEC1_napaka
GSMVLAZILEC2_delovanje | DIGITAL | IOD_GSM_TCP | 405 | 00405 | VLAZILEC2_delovanje
GSMVLAZILEC2_napaka | DIGITAL | IOD_GSM_TCP | 406 | 00406 | VLAZILEC2_napaka
GSMXVH_AlarmOn | DIGITAL | IOD_GSM_TCP | 407 | 00407 | XVH_AlarmOn
GSMXVH_enopolna_napaka | DIGITAL | IOD_GSM_TCP | 408 | 00408 | XVH_enopolna_napaka
GSMKLIMAT1_vklop_delovanjaR | DIGITAL | IOD_GSM_TCP | 409 | 00409 | KLIMAT1_vklop_delovanjaR
GSMKLIMAT2_vklop_delovanjaR | DIGITAL | IOD_GSM_TCP | 410 | 00410 | KLIMAT2_vklop_delovanjaR
GSMKLIMAT1_R_zakleni | DIGITAL | IOD_GSM_TCP | 411 | 00411 | KLIMAT1_R_zakleni
GSMKLIMAT2_R_zakleni | DIGITAL | IOD_GSM_TCP | 412 | 00412 | KLIMAT2_R_zakleni
GSMK1_vklop_izklop_poteka | DIGITAL | IOD_GSM_TCP | 413 | 00413 | K1_vklop_izklop_poteka
GSMK2_vklop_izklop_poteka | DIGITAL | IOD_GSM_TCP | 414 | 00414 | K2_vklop_izklop_poteka
GSMN_KlimeAVTO | DIGITAL | IOD_GSM_TCP | 415 | 00415 | N_KlimeAVTO
GSMUPS3AlarmAwaitingPower | DIGITAL | IOD_GSM_TCP | 416 | 00416 | UPS[3].AlarmAwaitingPower
GSMUPS3AlarmBypassBad | DIGITAL | IOD_GSM_TCP | 417 | 00417 | UPS[3].AlarmBypassBad
GSMUPS3AlarmChargerFailed | DIGITAL | IOD_GSM_TCP | 418 | 00418 | UPS[3].AlarmChargerFailed
GSMUPS3AlarmCommunicationsLost | DIGITAL | IOD_GSM_TCP | 419 | 00419 | UPS[3].AlarmCommunicationsLost
GSMUPS3AlarmDepletedBattery | DIGITAL | IOD_GSM_TCP | 420 | 00420 | UPS[3].AlarmDepletedBattery
GSMUPS3AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM_TCP | 421 | 00421 | UPS[3].AlarmDiagnosticTestFailed
GSMUPS3AlarmInverterError | DIGITAL | IOD_GSM_TCP | 422 | 00422 | UPS[3].AlarmInverterError
GSMUPS3AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 423 | 00423 | UPS[3].AlarmIzhodOffKotZahtevano
GSMUPS3AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM_TCP | 424 | 00424 | UPS[3].AlarmIzhodPreobremenjen
GSMUPS3AlarmLowBattery | DIGITAL | IOD_GSM_TCP | 425 | 00425 | UPS[3].AlarmLowBattery
GSMUPS3AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM_TCP | 426 | 00426 | UPS[3].AlarmNapakaNaVarovalki
GSMUPS3AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM_TCP | 427 | 00427 | UPS[3].AlarmNapakaNaVentilatorju
GSMUPS3AlarmOnBattery | DIGITAL | IOD_GSM_TCP | 428 | 00428 | UPS[3].AlarmOnBattery
GSMUPS3AlarmOnBypass | DIGITAL | IOD_GSM_TCP | 429 | 00429 | UPS[3].AlarmOnBypass
GSMUPS3AlarmShutdownImminent | DIGITAL | IOD_GSM_TCP | 430 | 00430 | UPS[3].AlarmShutdownImminent
GSMUPS3AlarmShutdownPending | DIGITAL | IOD_GSM_TCP | 431 | 00431 | UPS[3].AlarmShutdownPending
GSMUPS3AlarmSlabaBaterija | DIGITAL | IOD_GSM_TCP | 432 | 00432 | UPS[3].AlarmSlabaBaterija
GSMUPS3AlarmSplosnaNapaka | DIGITAL | IOD_GSM_TCP | 433 | 00433 | UPS[3].AlarmSplosnaNapaka
GSMUPS3AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 434 | 00434 | UPS[3].AlarmStanjeIzhodaIzvenToleranc
GSMUPS3AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 435 | 00435 | UPS[3].AlarmStanjeVhodaIzvenToleranc
GSMUPS3AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 436 | 00436 | UPS[3].AlarmTemperaturaIzvenToleranc
GSMUPS3AlarmTestInProgres | DIGITAL | IOD_GSM_TCP | 437 | 00437 | UPS[3].AlarmTestInProgres
GSMUPS3AlarmUPSIzhodOff | DIGITAL | IOD_GSM_TCP | 438 | 00438 | UPS[3].AlarmUPSIzhodOff
GSMUPS3AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 439 | 00439 | UPS[3].AlarmUPSOffKotZahtevano
GSMUPS3AlarmUPSSystemOff | DIGITAL | IOD_GSM_TCP | 440 | 00440 | UPS[3].AlarmUPSSystemOff
GSMUPS3Napaka | DIGITAL | IOD_GSM_TCP | 441 | 00441 | UPS[3].Napaka
GSMUPS3StatusEcomodeAktiven | DIGITAL | IOD_GSM_TCP | 442 | 00442 | UPS[3].StatusEcomodeAktiven
GSMUPS3StatusInverterIsOn | DIGITAL | IOD_GSM_TCP | 443 | 00443 | UPS[3].StatusInverterIsOn
GSMUPS3StatusStopOperation | DIGITAL | IOD_GSM_TCP | 444 | 00444 | UPS[3].StatusStopOperation
GSMErrComUPS3 | DIGITAL | IOD_GSM_TCP | 445 | 00445 | ErrComUPS[3]
GSMGSM_PozCent_napaka | DIGITAL | IOD_GSM_TCP | 446 | 00446 | GSM_PozCent_napaka
GSMGSM_PozSenzor_okvara | DIGITAL | IOD_GSM_TCP | 447 | 00447 | GSM_PozSenzor_okvara
GSMGSM_Gasenje_alarm | DIGITAL | IOD_GSM_TCP | 448 | 00448 | GSM_Gasenje_alarm
GSMAGR_PozCent_napaka | DIGITAL | IOD_GSM_TCP | 449 | 00449 | AGR_PozCent_napaka
GSMAGR_PozSenzor_okvara | DIGITAL | IOD_GSM_TCP | 450 | 00450 | AGR_PozSenzor_okvara
GSMAGR_Gasenje_alarm | DIGITAL | IOD_GSM_TCP | 451 | 00451 | AGR_Gasenje_alarm
GSMCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_GSM_TCP | 452 | 00452 | Circ_Vpis_Dnevne_energija_scada1
GSMCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_GSM_TCP | 453 | 00453 | Circ_Vpis_Dnevne_energija_scada2
GSMCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_GSM_TCP | 454 | 00454 | Circ_Vpis_Tedenska_energija_scada1
GSMCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_GSM_TCP | 455 | 00455 | Circ_Vpis_Tedenska_energija_scada2
GSMCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_GSM_TCP | 456 | 00456 | Circ_Vpis_Mesecna_energija_scada1
GSMCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_GSM_TCP | 457 | 00457 | Circ_Vpis_Mesecna_energija_scada2
GSMPozarnaCentrala_skupno | DIGITAL | IOD_GSM_TCP | 458 | 00458 | PozarnaCentrala_skupno
GSMDateTimeDan | INT | IOD_GSM_TCP | 1 | 40001 | DateTime.Dan | BYTE
GSMDateTimeLeto | INT | IOD_GSM_TCP | 2 | 40002 | DateTime.Leto | BYTE
GSMDateTimeLeto2 | INT | IOD_GSM_TCP | 3 | 40003 | DateTime.Leto2
GSMDateTimeMesec | INT | IOD_GSM_TCP | 4 | 40004 | DateTime.Mesec | BYTE
GSMDateTimeMinuta | INT | IOD_GSM_TCP | 5 | 40005 | DateTime.Minuta | BYTE
GSMDateTimeSekunda | INT | IOD_GSM_TCP | 6 | 40006 | DateTime.Sekunda | BYTE
GSMDateTimeUra | INT | IOD_GSM_TCP | 7 | 40007 | DateTime.Ura | BYTE
GSMErrorComCirc1Code10 | INT | IOD_GSM_TCP | 8 | 40008 | ErrorComCirc[1].Code[10] | BYTE
GSMErrorComCirc1Code11 | INT | IOD_GSM_TCP | 9 | 40009 | ErrorComCirc[1].Code[11] | BYTE
GSMErrorComCirc1Code12 | INT | IOD_GSM_TCP | 10 | 40010 | ErrorComCirc[1].Code[12] | BYTE
GSMErrorComCirc1Code13 | INT | IOD_GSM_TCP | 11 | 40011 | ErrorComCirc[1].Code[13] | BYTE
GSMErrorComCirc1Code14 | INT | IOD_GSM_TCP | 12 | 40012 | ErrorComCirc[1].Code[14] | BYTE
GSMErrorComCirc1Code15 | INT | IOD_GSM_TCP | 13 | 40013 | ErrorComCirc[1].Code[15] | BYTE
GSMErrorComCirc1Code1 | INT | IOD_GSM_TCP | 14 | 40014 | ErrorComCirc[1].Code[1] | BYTE
GSMErrorComCirc1Code2 | INT | IOD_GSM_TCP | 15 | 40015 | ErrorComCirc[1].Code[2] | BYTE
GSMErrorComCirc1Code3 | INT | IOD_GSM_TCP | 16 | 40016 | ErrorComCirc[1].Code[3] | BYTE
GSMErrorComCirc1Code4 | INT | IOD_GSM_TCP | 17 | 40017 | ErrorComCirc[1].Code[4] | BYTE
GSMErrorComCirc1Code5 | INT | IOD_GSM_TCP | 18 | 40018 | ErrorComCirc[1].Code[5] | BYTE
GSMErrorComCirc1Code6 | INT | IOD_GSM_TCP | 19 | 40019 | ErrorComCirc[1].Code[6] | BYTE
GSMErrorComCirc1Code7 | INT | IOD_GSM_TCP | 20 | 40020 | ErrorComCirc[1].Code[7] | BYTE
GSMErrorComCirc1Code8 | INT | IOD_GSM_TCP | 21 | 40021 | ErrorComCirc[1].Code[8] | BYTE
GSMErrorComCirc1Code9 | INT | IOD_GSM_TCP | 22 | 40022 | ErrorComCirc[1].Code[9] | BYTE
GSMErrorComCirc1Status | INT | IOD_GSM_TCP | 23 | 40023 | ErrorComCirc[1].Status
GSMErrorComKlima1Code10 | INT | IOD_GSM_TCP | 24 | 40024 | ErrorComKlima[1].Code[10] | BYTE
GSMErrorComKlima1Code11 | INT | IOD_GSM_TCP | 25 | 40025 | ErrorComKlima[1].Code[11] | BYTE
GSMErrorComKlima1Code12 | INT | IOD_GSM_TCP | 26 | 40026 | ErrorComKlima[1].Code[12] | BYTE
GSMErrorComKlima1Code13 | INT | IOD_GSM_TCP | 27 | 40027 | ErrorComKlima[1].Code[13] | BYTE
GSMErrorComKlima1Code14 | INT | IOD_GSM_TCP | 28 | 40028 | ErrorComKlima[1].Code[14] | BYTE
GSMErrorComKlima1Code15 | INT | IOD_GSM_TCP | 29 | 40029 | ErrorComKlima[1].Code[15] | BYTE
GSMErrorComKlima1Code1 | INT | IOD_GSM_TCP | 30 | 40030 | ErrorComKlima[1].Code[1] | BYTE
GSMErrorComKlima1Code2 | INT | IOD_GSM_TCP | 31 | 40031 | ErrorComKlima[1].Code[2] | BYTE
GSMErrorComKlima1Code3 | INT | IOD_GSM_TCP | 32 | 40032 | ErrorComKlima[1].Code[3] | BYTE
GSMErrorComKlima1Code4 | INT | IOD_GSM_TCP | 33 | 40033 | ErrorComKlima[1].Code[4] | BYTE
GSMErrorComKlima1Code5 | INT | IOD_GSM_TCP | 34 | 40034 | ErrorComKlima[1].Code[5] | BYTE
GSMErrorComKlima1Code6 | INT | IOD_GSM_TCP | 35 | 40035 | ErrorComKlima[1].Code[6] | BYTE
GSMErrorComKlima1Code7 | INT | IOD_GSM_TCP | 36 | 40036 | ErrorComKlima[1].Code[7] | BYTE
GSMErrorComKlima1Code8 | INT | IOD_GSM_TCP | 37 | 40037 | ErrorComKlima[1].Code[8] | BYTE
GSMErrorComKlima1Code9 | INT | IOD_GSM_TCP | 38 | 40038 | ErrorComKlima[1].Code[9] | BYTE
GSMErrorComKlima1Status | INT | IOD_GSM_TCP | 39 | 40039 | ErrorComKlima[1].Status
GSMErrorComKlima2Code10 | INT | IOD_GSM_TCP | 40 | 40040 | ErrorComKlima[2].Code[10] | BYTE
GSMErrorComKlima2Code11 | INT | IOD_GSM_TCP | 41 | 40041 | ErrorComKlima[2].Code[11] | BYTE
GSMErrorComKlima2Code12 | INT | IOD_GSM_TCP | 42 | 40042 | ErrorComKlima[2].Code[12] | BYTE
GSMErrorComKlima2Code13 | INT | IOD_GSM_TCP | 43 | 40043 | ErrorComKlima[2].Code[13] | BYTE
GSMErrorComKlima2Code14 | INT | IOD_GSM_TCP | 44 | 40044 | ErrorComKlima[2].Code[14] | BYTE
GSMErrorComKlima2Code15 | INT | IOD_GSM_TCP | 45 | 40045 | ErrorComKlima[2].Code[15] | BYTE
GSMErrorComKlima2Code1 | INT | IOD_GSM_TCP | 46 | 40046 | ErrorComKlima[2].Code[1] | BYTE
GSMErrorComKlima2Code2 | INT | IOD_GSM_TCP | 47 | 40047 | ErrorComKlima[2].Code[2] | BYTE
GSMErrorComKlima2Code3 | INT | IOD_GSM_TCP | 48 | 40048 | ErrorComKlima[2].Code[3] | BYTE
GSMErrorComKlima2Code4 | INT | IOD_GSM_TCP | 49 | 40049 | ErrorComKlima[2].Code[4] | BYTE
GSMErrorComKlima2Code5 | INT | IOD_GSM_TCP | 50 | 40050 | ErrorComKlima[2].Code[5] | BYTE
GSMErrorComKlima2Code6 | INT | IOD_GSM_TCP | 51 | 40051 | ErrorComKlima[2].Code[6] | BYTE
GSMErrorComKlima2Code7 | INT | IOD_GSM_TCP | 52 | 40052 | ErrorComKlima[2].Code[7] | BYTE
GSMErrorComKlima2Code8 | INT | IOD_GSM_TCP | 53 | 40053 | ErrorComKlima[2].Code[8] | BYTE
GSMErrorComKlima2Code9 | INT | IOD_GSM_TCP | 54 | 40054 | ErrorComKlima[2].Code[9] | BYTE
GSMErrorComKlima2Status | INT | IOD_GSM_TCP | 55 | 40055 | ErrorComKlima[2].Status
GSMErrorComPMM1Code10 | INT | IOD_GSM_TCP | 56 | 40056 | ErrorComPMM[1].Code[10] | BYTE
GSMErrorComPMM1Code11 | INT | IOD_GSM_TCP | 57 | 40057 | ErrorComPMM[1].Code[11] | BYTE
GSMErrorComPMM1Code12 | INT | IOD_GSM_TCP | 58 | 40058 | ErrorComPMM[1].Code[12] | BYTE
GSMErrorComPMM1Code13 | INT | IOD_GSM_TCP | 59 | 40059 | ErrorComPMM[1].Code[13] | BYTE
GSMErrorComPMM1Code14 | INT | IOD_GSM_TCP | 60 | 40060 | ErrorComPMM[1].Code[14] | BYTE
GSMErrorComPMM1Code15 | INT | IOD_GSM_TCP | 61 | 40061 | ErrorComPMM[1].Code[15] | BYTE
GSMErrorComPMM1Code1 | INT | IOD_GSM_TCP | 62 | 40062 | ErrorComPMM[1].Code[1] | BYTE
GSMErrorComPMM1Code2 | INT | IOD_GSM_TCP | 63 | 40063 | ErrorComPMM[1].Code[2] | BYTE
GSMErrorComPMM1Code3 | INT | IOD_GSM_TCP | 64 | 40064 | ErrorComPMM[1].Code[3] | BYTE
GSMErrorComPMM1Code4 | INT | IOD_GSM_TCP | 65 | 40065 | ErrorComPMM[1].Code[4] | BYTE
GSMErrorComPMM1Code5 | INT | IOD_GSM_TCP | 66 | 40066 | ErrorComPMM[1].Code[5] | BYTE
GSMErrorComPMM1Code6 | INT | IOD_GSM_TCP | 67 | 40067 | ErrorComPMM[1].Code[6] | BYTE
GSMErrorComPMM1Code7 | INT | IOD_GSM_TCP | 68 | 40068 | ErrorComPMM[1].Code[7] | BYTE
GSMErrorComPMM1Code8 | INT | IOD_GSM_TCP | 69 | 40069 | ErrorComPMM[1].Code[8] | BYTE
GSMErrorComPMM1Code9 | INT | IOD_GSM_TCP | 70 | 40070 | ErrorComPMM[1].Code[9] | BYTE
GSMErrorComPMM1Status | INT | IOD_GSM_TCP | 71 | 40071 | ErrorComPMM[1].Status
GSMErrorComUPS1Code10 | INT | IOD_GSM_TCP | 72 | 40072 | ErrorComUPS[1].Code[10] | BYTE
GSMErrorComUPS1Code11 | INT | IOD_GSM_TCP | 73 | 40073 | ErrorComUPS[1].Code[11] | BYTE
GSMErrorComUPS1Code12 | INT | IOD_GSM_TCP | 74 | 40074 | ErrorComUPS[1].Code[12] | BYTE
GSMErrorComUPS1Code13 | INT | IOD_GSM_TCP | 75 | 40075 | ErrorComUPS[1].Code[13] | BYTE
GSMErrorComUPS1Code14 | INT | IOD_GSM_TCP | 76 | 40076 | ErrorComUPS[1].Code[14] | BYTE
GSMErrorComUPS1Code15 | INT | IOD_GSM_TCP | 77 | 40077 | ErrorComUPS[1].Code[15] | BYTE
GSMErrorComUPS1Code1 | INT | IOD_GSM_TCP | 78 | 40078 | ErrorComUPS[1].Code[1] | BYTE
GSMErrorComUPS1Code2 | INT | IOD_GSM_TCP | 79 | 40079 | ErrorComUPS[1].Code[2] | BYTE
GSMErrorComUPS1Code3 | INT | IOD_GSM_TCP | 80 | 40080 | ErrorComUPS[1].Code[3] | BYTE
GSMErrorComUPS1Code4 | INT | IOD_GSM_TCP | 81 | 40081 | ErrorComUPS[1].Code[4] | BYTE
GSMErrorComUPS1Code5 | INT | IOD_GSM_TCP | 82 | 40082 | ErrorComUPS[1].Code[5] | BYTE
GSMErrorComUPS1Code6 | INT | IOD_GSM_TCP | 83 | 40083 | ErrorComUPS[1].Code[6] | BYTE
GSMErrorComUPS1Code7 | INT | IOD_GSM_TCP | 84 | 40084 | ErrorComUPS[1].Code[7] | BYTE
GSMErrorComUPS1Code8 | INT | IOD_GSM_TCP | 85 | 40085 | ErrorComUPS[1].Code[8] | BYTE
GSMErrorComUPS1Code9 | INT | IOD_GSM_TCP | 86 | 40086 | ErrorComUPS[1].Code[9] | BYTE
GSMErrorComUPS1Status | INT | IOD_GSM_TCP | 87 | 40087 | ErrorComUPS[1].Status
GSMErrorComUPS2Code10 | INT | IOD_GSM_TCP | 88 | 40088 | ErrorComUPS[2].Code[10] | BYTE
GSMErrorComUPS2Code11 | INT | IOD_GSM_TCP | 89 | 40089 | ErrorComUPS[2].Code[11] | BYTE
GSMErrorComUPS2Code12 | INT | IOD_GSM_TCP | 90 | 40090 | ErrorComUPS[2].Code[12] | BYTE
GSMErrorComUPS2Code13 | INT | IOD_GSM_TCP | 91 | 40091 | ErrorComUPS[2].Code[13] | BYTE
GSMErrorComUPS2Code14 | INT | IOD_GSM_TCP | 92 | 40092 | ErrorComUPS[2].Code[14] | BYTE
GSMErrorComUPS2Code15 | INT | IOD_GSM_TCP | 93 | 40093 | ErrorComUPS[2].Code[15] | BYTE
GSMErrorComUPS2Code1 | INT | IOD_GSM_TCP | 94 | 40094 | ErrorComUPS[2].Code[1] | BYTE
GSMErrorComUPS2Code2 | INT | IOD_GSM_TCP | 95 | 40095 | ErrorComUPS[2].Code[2] | BYTE
GSMErrorComUPS2Code3 | INT | IOD_GSM_TCP | 96 | 40096 | ErrorComUPS[2].Code[3] | BYTE
GSMErrorComUPS2Code4 | INT | IOD_GSM_TCP | 97 | 40097 | ErrorComUPS[2].Code[4] | BYTE
GSMErrorComUPS2Code5 | INT | IOD_GSM_TCP | 98 | 40098 | ErrorComUPS[2].Code[5] | BYTE
GSMErrorComUPS2Code6 | INT | IOD_GSM_TCP | 99 | 40099 | ErrorComUPS[2].Code[6] | BYTE
GSMErrorComUPS2Code7 | INT | IOD_GSM_TCP | 100 | 40100 | ErrorComUPS[2].Code[7] | BYTE
GSMErrorComUPS2Code8 | INT | IOD_GSM_TCP | 101 | 40101 | ErrorComUPS[2].Code[8] | BYTE
GSMErrorComUPS2Code9 | INT | IOD_GSM_TCP | 102 | 40102 | ErrorComUPS[2].Code[9] | BYTE
GSMErrorComUPS2Status | INT | IOD_GSM_TCP | 103 | 40103 | ErrorComUPS[2].Status
GSMErrorComUPSMGE1Code10 | INT | IOD_GSM_TCP | 104 | 40104 | ErrorComUPSMGE[1].Code[10] | BYTE
GSMErrorComUPSMGE1Code11 | INT | IOD_GSM_TCP | 105 | 40105 | ErrorComUPSMGE[1].Code[11] | BYTE
GSMErrorComUPSMGE1Code12 | INT | IOD_GSM_TCP | 106 | 40106 | ErrorComUPSMGE[1].Code[12] | BYTE
GSMErrorComUPSMGE1Code13 | INT | IOD_GSM_TCP | 107 | 40107 | ErrorComUPSMGE[1].Code[13] | BYTE
GSMErrorComUPSMGE1Code14 | INT | IOD_GSM_TCP | 108 | 40108 | ErrorComUPSMGE[1].Code[14] | BYTE
GSMErrorComUPSMGE1Code15 | INT | IOD_GSM_TCP | 109 | 40109 | ErrorComUPSMGE[1].Code[15] | BYTE
GSMErrorComUPSMGE1Code1 | INT | IOD_GSM_TCP | 110 | 40110 | ErrorComUPSMGE[1].Code[1] | BYTE
GSMErrorComUPSMGE1Code2 | INT | IOD_GSM_TCP | 111 | 40111 | ErrorComUPSMGE[1].Code[2] | BYTE
GSMErrorComUPSMGE1Code3 | INT | IOD_GSM_TCP | 112 | 40112 | ErrorComUPSMGE[1].Code[3] | BYTE
GSMErrorComUPSMGE1Code4 | INT | IOD_GSM_TCP | 113 | 40113 | ErrorComUPSMGE[1].Code[4] | BYTE
GSMErrorComUPSMGE1Code5 | INT | IOD_GSM_TCP | 114 | 40114 | ErrorComUPSMGE[1].Code[5] | BYTE
GSMErrorComUPSMGE1Code6 | INT | IOD_GSM_TCP | 115 | 40115 | ErrorComUPSMGE[1].Code[6] | BYTE
GSMErrorComUPSMGE1Code7 | INT | IOD_GSM_TCP | 116 | 40116 | ErrorComUPSMGE[1].Code[7] | BYTE
GSMErrorComUPSMGE1Code8 | INT | IOD_GSM_TCP | 117 | 40117 | ErrorComUPSMGE[1].Code[8] | BYTE
GSMErrorComUPSMGE1Code9 | INT | IOD_GSM_TCP | 118 | 40118 | ErrorComUPSMGE[1].Code[9] | BYTE
GSMErrorComUPSMGE1Status | INT | IOD_GSM_TCP | 119 | 40119 | ErrorComUPSMGE[1].Status
GSMHIA1_vlaga_s | INT | IOD_GSM_TCP | 120 | 40120 | HIA1_vlaga_s
GSMHIA2_vlaga_s | INT | IOD_GSM_TCP | 121 | 40121 | HIA2_vlaga_s
GSMHIA3_vlaga_s | INT | IOD_GSM_TCP | 122 | 40122 | HIA3_vlaga_s
GSMHIA4_vlaga_s | INT | IOD_GSM_TCP | 123 | 40123 | HIA4_vlaga_s
GSMHIA5_vlaga_s | INT | IOD_GSM_TCP | 124 | 40124 | HIA5_vlaga_s
GSMHIA6_vlaga_s | INT | IOD_GSM_TCP | 125 | 40125 | HIA6_vlaga_s
GSMHIA7_vlaga_s | INT | IOD_GSM_TCP | 126 | 40126 | HIA7_vlaga_s
GSMKlima1Analog_izh_mesanje | INT | IOD_GSM_TCP | 127 | 40127 | Klima[1].Analog_izh_mesanje
GSMKlima1Analog_izh_rekuperator | INT | IOD_GSM_TCP | 128 | 40128 | Klima[1].Analog_izh_rekuperator
GSMKlima1Analog_izh_VentGrelnika | INT | IOD_GSM_TCP | 129 | 40129 | Klima[1].Analog_izh_VentGrelnika
GSMKlima1Analog_izh_VentHlajenja | INT | IOD_GSM_TCP | 130 | 40130 | Klima[1].Analog_izh_VentHlajenja
GSMKlima1Dejanska_zel_temp | INT | IOD_GSM_TCP | 131 | 40131 | Klima[1].Dejanska_zel_temp
GSMKlima1Hitrost_del_vent_disp | INT | IOD_GSM_TCP | 132 | 40132 | Klima[1].Hitrost_del_vent_disp
GSMKlima1Max_vpih | INT | IOD_GSM_TCP | 133 | 40133 | Klima[1].Max_vpih
GSMKlima1Min_vpih | INT | IOD_GSM_TCP | 134 | 40134 | Klima[1].Min_vpih
GSMKlima1Obrat_ure_Vent_h1 | INT | IOD_GSM_TCP | 135 | 40135 | Klima[1].Obrat_ure_Vent_h1
GSMKlima1Obrat_ure_Vent_h2 | INT | IOD_GSM_TCP | 136 | 40136 | Klima[1].Obrat_ure_Vent_h2
GSMKlima1Pol_komp_konec | INT | IOD_GSM_TCP | 137 | 40137 | Klima[1].Pol_komp_konec
GSMKlima1Pol_komp_sprem_zel_vr | INT | IOD_GSM_TCP | 138 | 40138 | Klima[1].Pol_komp_sprem_zel_vr
GSMKlima1Pol_komp_zacetek | INT | IOD_GSM_TCP | 139 | 40139 | Klima[1].Pol_komp_zacetek
GSMKlima1PreklopHitDelVent | INT | IOD_GSM_TCP | 140 | 40140 | Klima[1].PreklopHitDelVent
GSMKlima1Protizamrz_zascita | INT | IOD_GSM_TCP | 141 | 40141 | Klima[1].Protizamrz_zascita
GSMKlima1Rezim_delovanja | INT | IOD_GSM_TCP | 142 | 40142 | Klima[1].Rezim_delovanja
GSMKlima1Temperatura_dovoda | INT | IOD_GSM_TCP | 143 | 40143 | Klima[1].Temperatura_dovoda
GSMKlima1Temperatura_prostora | INT | IOD_GSM_TCP | 144 | 40144 | Klima[1].Temperatura_prostora
GSMKlima1TempPredPloscnimRekup | INT | IOD_GSM_TCP | 145 | 40145 | Klima[1].TempPredPloscnimRekup
GSMKlima1TempZaPloscnimRekup | INT | IOD_GSM_TCP | 146 | 40146 | Klima[1].TempZaPloscnimRekup
GSMKlima1Vlaga_v_prostoru | INT | IOD_GSM_TCP | 147 | 40147 | Klima[1].Vlaga_v_prostoru
GSMKlima1VlagaVstopZrakaProstor | INT | IOD_GSM_TCP | 148 | 40148 | Klima[1].VlagaVstopZrakaProstor
GSMKlima1Zel_temp_eko_gretja | INT | IOD_GSM_TCP | 149 | 40149 | Klima[1].Zel_temp_eko_gretja
GSMKlima1Zel_temp_eko_hlajenja | INT | IOD_GSM_TCP | 150 | 40150 | Klima[1].Zel_temp_eko_hlajenja
GSMKlima1Zel_temp_komf_gretja | INT | IOD_GSM_TCP | 151 | 40151 | Klima[1].Zel_temp_komf_gretja
GSMKlima1Zel_temp_komf_hlajenja | INT | IOD_GSM_TCP | 152 | 40152 | Klima[1].Zel_temp_komf_hlajenja
GSMKlima1Zim_komp_konec | INT | IOD_GSM_TCP | 153 | 40153 | Klima[1].Zim_komp_konec
GSMKlima1Zim_komp_sprem_zel_vr | INT | IOD_GSM_TCP | 154 | 40154 | Klima[1].Zim_komp_sprem_zel_vr
GSMKlima1Zim_komp_zacetek | INT | IOD_GSM_TCP | 155 | 40155 | Klima[1].Zim_komp_zacetek
GSMKlima1ZimKompMinVpihKonec | INT | IOD_GSM_TCP | 156 | 40156 | Klima[1].ZimKompMinVpihKonec
GSMKlima1ZimKompMinVpihZac | INT | IOD_GSM_TCP | 157 | 40157 | Klima[1].ZimKompMinVpihZac
GSMKlima1ZkompMinVpihSpremZelVr | INT | IOD_GSM_TCP | 158 | 40158 | Klima[1].ZkompMinVpihSpremZelVr
GSMKlima1Zunanja_temp | INT | IOD_GSM_TCP | 159 | 40159 | Klima[1].Zunanja_temp
GSMKlima2Analog_izh_mesanje | INT | IOD_GSM_TCP | 160 | 40160 | Klima[2].Analog_izh_mesanje
GSMKlima2Analog_izh_rekuperator | INT | IOD_GSM_TCP | 161 | 40161 | Klima[2].Analog_izh_rekuperator
GSMKlima2Analog_izh_VentGrelnika | INT | IOD_GSM_TCP | 162 | 40162 | Klima[2].Analog_izh_VentGrelnika
GSMKlima2Analog_izh_VentHlajenja | INT | IOD_GSM_TCP | 163 | 40163 | Klima[2].Analog_izh_VentHlajenja
GSMKlima2Dejanska_zel_temp | INT | IOD_GSM_TCP | 164 | 40164 | Klima[2].Dejanska_zel_temp
GSMKlima2Hitrost_del_vent_disp | INT | IOD_GSM_TCP | 165 | 40165 | Klima[2].Hitrost_del_vent_disp
GSMKlima2Max_vpih | INT | IOD_GSM_TCP | 166 | 40166 | Klima[2].Max_vpih
GSMKlima2Min_vpih | INT | IOD_GSM_TCP | 167 | 40167 | Klima[2].Min_vpih
GSMKlima2Obrat_ure_Vent_h1 | INT | IOD_GSM_TCP | 168 | 40168 | Klima[2].Obrat_ure_Vent_h1
GSMKlima2Obrat_ure_Vent_h2 | INT | IOD_GSM_TCP | 169 | 40169 | Klima[2].Obrat_ure_Vent_h2
GSMKlima2Pol_komp_konec | INT | IOD_GSM_TCP | 170 | 40170 | Klima[2].Pol_komp_konec
GSMKlima2Pol_komp_sprem_zel_vr | INT | IOD_GSM_TCP | 171 | 40171 | Klima[2].Pol_komp_sprem_zel_vr
GSMKlima2Pol_komp_zacetek | INT | IOD_GSM_TCP | 172 | 40172 | Klima[2].Pol_komp_zacetek
GSMKlima2PreklopHitDelVent | INT | IOD_GSM_TCP | 173 | 40173 | Klima[2].PreklopHitDelVent
GSMKlima2Protizamrz_zascita | INT | IOD_GSM_TCP | 174 | 40174 | Klima[2].Protizamrz_zascita
GSMKlima2Rezim_delovanja | INT | IOD_GSM_TCP | 175 | 40175 | Klima[2].Rezim_delovanja
GSMKlima2Temperatura_dovoda | INT | IOD_GSM_TCP | 176 | 40176 | Klima[2].Temperatura_dovoda
GSMKlima2Temperatura_prostora | INT | IOD_GSM_TCP | 177 | 40177 | Klima[2].Temperatura_prostora
GSMKlima2TempPredPloscnimRekup | INT | IOD_GSM_TCP | 178 | 40178 | Klima[2].TempPredPloscnimRekup
GSMKlima2TempZaPloscnimRekup | INT | IOD_GSM_TCP | 179 | 40179 | Klima[2].TempZaPloscnimRekup
GSMKlima2Vlaga_v_prostoru | INT | IOD_GSM_TCP | 180 | 40180 | Klima[2].Vlaga_v_prostoru
GSMKlima2VlagaVstopZrakaProstor | INT | IOD_GSM_TCP | 181 | 40181 | Klima[2].VlagaVstopZrakaProstor
GSMKlima2Zel_temp_eko_gretja | INT | IOD_GSM_TCP | 182 | 40182 | Klima[2].Zel_temp_eko_gretja
GSMKlima2Zel_temp_eko_hlajenja | INT | IOD_GSM_TCP | 183 | 40183 | Klima[2].Zel_temp_eko_hlajenja
GSMKlima2Zel_temp_komf_gretja | INT | IOD_GSM_TCP | 184 | 40184 | Klima[2].Zel_temp_komf_gretja
GSMKlima2Zel_temp_komf_hlajenja | INT | IOD_GSM_TCP | 185 | 40185 | Klima[2].Zel_temp_komf_hlajenja
GSMKlima2Zim_komp_konec | INT | IOD_GSM_TCP | 186 | 40186 | Klima[2].Zim_komp_konec
GSMKlima2Zim_komp_sprem_zel_vr | INT | IOD_GSM_TCP | 187 | 40187 | Klima[2].Zim_komp_sprem_zel_vr
GSMKlima2Zim_komp_zacetek | INT | IOD_GSM_TCP | 188 | 40188 | Klima[2].Zim_komp_zacetek
GSMKlima2ZimKompMinVpihKonec | INT | IOD_GSM_TCP | 189 | 40189 | Klima[2].ZimKompMinVpihKonec
GSMKlima2ZimKompMinVpihZac | INT | IOD_GSM_TCP | 190 | 40190 | Klima[2].ZimKompMinVpihZac
GSMKlima2ZkompMinVpihSpremZelVr | INT | IOD_GSM_TCP | 191 | 40191 | Klima[2].ZkompMinVpihSpremZelVr
GSMKlima2Zunanja_temp | INT | IOD_GSM_TCP | 192 | 40192 | Klima[2].Zunanja_temp
GSMKlimaIzklopObrUre | INT | IOD_GSM_TCP | 193 | 40193 | KlimaIzklopObrUre
GSMPMM1AlarmPhase1GlobalAlarmReg | INT | IOD_GSM_TCP | 194 | 40194 | PMM[1].AlarmPhase[1].GlobalAlarmReg
GSMPMM1AlarmPhase2GlobalAlarmReg | INT | IOD_GSM_TCP | 195 | 40195 | PMM[1].AlarmPhase[2].GlobalAlarmReg
GSMPMM1AlarmPhase3GlobalAlarmReg | INT | IOD_GSM_TCP | 196 | 40196 | PMM[1].AlarmPhase[3].GlobalAlarmReg
GSMQ12stanje | INT | IOD_GSM_TCP | 197 | 40197 | Q12stanje | BYTE
GSMTempHistereza | INT | IOD_GSM_TCP | 198 | 40198 | TempHistereza
GSMTempPovp234 | INT | IOD_GSM_TCP | 199 | 40199 | TempPovp234
GSMTempPovp234Alarm | INT | IOD_GSM_TCP | 200 | 40200 | TempPovp234Alarm
GSMTempPovp56 | INT | IOD_GSM_TCP | 201 | 40201 | TempPovp56
GSMTempPovp56Alarm | INT | IOD_GSM_TCP | 202 | 40202 | TempPovp56Alarm
GSMTempZaVklopKlim1 | INT | IOD_GSM_TCP | 203 | 40203 | TempZaVklopKlim1
GSMTempZaVklopKlim2 | INT | IOD_GSM_TCP | 204 | 40204 | TempZaVklopKlim2
GSMTIA1_alarm | INT | IOD_GSM_TCP | 205 | 40205 | TIA1_alarm
GSMTIA1_temp_s | INT | IOD_GSM_TCP | 206 | 40206 | TIA1_temp_s
GSMTIA2_alarm | INT | IOD_GSM_TCP | 207 | 40207 | TIA2_alarm
GSMTIA2_temp_s | INT | IOD_GSM_TCP | 208 | 40208 | TIA2_temp_s
GSMTIA3_alarm | INT | IOD_GSM_TCP | 209 | 40209 | TIA3_alarm
GSMTIA3_temp_s | INT | IOD_GSM_TCP | 210 | 40210 | TIA3_temp_s
GSMTIA4_alarm | INT | IOD_GSM_TCP | 211 | 40211 | TIA4_alarm
GSMTIA4_temp_s | INT | IOD_GSM_TCP | 212 | 40212 | TIA4_temp_s
GSMTIA5_alarm | INT | IOD_GSM_TCP | 213 | 40213 | TIA5_alarm
GSMTIA5_temp_s | INT | IOD_GSM_TCP | 214 | 40214 | TIA5_temp_s
GSMTIA6_alarm | INT | IOD_GSM_TCP | 215 | 40215 | TIA6_alarm
GSMTIA6_temp_s | INT | IOD_GSM_TCP | 216 | 40216 | TIA6_temp_s
GSMTIA7_alarm | INT | IOD_GSM_TCP | 217 | 40217 | TIA7_alarm
GSMTIA7_temp_s | INT | IOD_GSM_TCP | 218 | 40218 | TIA7_temp_s
GSMUPS1InverterStatus | INT | IOD_GSM_TCP | 219 | 40219 | UPS[1].InverterStatus
GSMUPS1OutputStatus | INT | IOD_GSM_TCP | 220 | 40220 | UPS[1].OutputStatus
GSMUPS1SteviloIzpadovVhodneLinije | INT | IOD_GSM_TCP | 221 | 40221 | UPS[1].SteviloIzpadovVhodneLinije
GSMUPS1UnitStatus | INT | IOD_GSM_TCP | 222 | 40222 | UPS[1].UnitStatus
GSMUPS2InverterStatus | INT | IOD_GSM_TCP | 223 | 40223 | UPS[2].InverterStatus
GSMUPS2OutputStatus | INT | IOD_GSM_TCP | 224 | 40224 | UPS[2].OutputStatus
GSMUPS2SteviloIzpadovVhodneLinije | INT | IOD_GSM_TCP | 225 | 40225 | UPS[2].SteviloIzpadovVhodneLinije
GSMUPS2UnitStatus | INT | IOD_GSM_TCP | 226 | 40226 | UPS[2].UnitStatus
GSMUPS_MGE1BatteryBackupTime | INT | IOD_GSM_TCP | 227 | 40227 | UPS_MGE[1].BatteryBackupTime
GSMUPS_MGE1BatteryChargingLevel | INT | IOD_GSM_TCP | 228 | 40228 | UPS_MGE[1].BatteryChargingLevel
GSMUPS_MGE1BatteryRechargeDuration | INT | IOD_GSM_TCP | 229 | 40229 | UPS_MGE[1].BatteryRechargeDuration
GSMUPS_MGE1I1output | INT | IOD_GSM_TCP | 230 | 40230 | UPS_MGE[1].I1output
GSMUPS_MGE1I2output | INT | IOD_GSM_TCP | 231 | 40231 | UPS_MGE[1].I2output
GSMUPS_MGE1I3output | INT | IOD_GSM_TCP | 232 | 40232 | UPS_MGE[1].I3output
GSMUPS_MGE1InverterFrequency | INT | IOD_GSM_TCP | 233 | 40233 | UPS_MGE[1].InverterFrequency
GSMUPS_MGE1OutputActivePower1 | INT | IOD_GSM_TCP | 234 | 40234 | UPS_MGE[1].OutputActivePower1
GSMUPS_MGE1OutputActivePower2 | INT | IOD_GSM_TCP | 235 | 40235 | UPS_MGE[1].OutputActivePower2
GSMUPS_MGE1OutputActivePower3 | INT | IOD_GSM_TCP | 236 | 40236 | UPS_MGE[1].OutputActivePower3
GSMUPS_MGE1OutputFrequency | INT | IOD_GSM_TCP | 237 | 40237 | UPS_MGE[1].OutputFrequency
GSMUPS_MGE1OutputLoadLevel | INT | IOD_GSM_TCP | 238 | 40238 | UPS_MGE[1].OutputLoadLevel
GSMUPS_MGE1StatusBaterije | INT | IOD_GSM_TCP | 239 | 40239 | UPS_MGE[1].StatusBaterije | BYTE
GSMUPS_MGE1U12mains1 | INT | IOD_GSM_TCP | 240 | 40240 | UPS_MGE[1].U12mains1
GSMUPS_MGE1U12mains2 | INT | IOD_GSM_TCP | 241 | 40241 | UPS_MGE[1].U12mains2
GSMUPS_MGE1U1N_inverter | INT | IOD_GSM_TCP | 242 | 40242 | UPS_MGE[1].U1N_inverter
GSMUPS_MGE1U1N_output | INT | IOD_GSM_TCP | 243 | 40243 | UPS_MGE[1].U1N_output
GSMUPS_MGE1U23mains1 | INT | IOD_GSM_TCP | 244 | 40244 | UPS_MGE[1].U23mains1
GSMUPS_MGE1U23mains2 | INT | IOD_GSM_TCP | 245 | 40245 | UPS_MGE[1].U23mains2
GSMUPS_MGE1U2N_inverter | INT | IOD_GSM_TCP | 246 | 40246 | UPS_MGE[1].U2N_inverter
GSMUPS_MGE1U2N_output | INT | IOD_GSM_TCP | 247 | 40247 | UPS_MGE[1].U2N_output
GSMUPS_MGE1U31mains1 | INT | IOD_GSM_TCP | 248 | 40248 | UPS_MGE[1].U31mains1
GSMUPS_MGE1U31mains2 | INT | IOD_GSM_TCP | 249 | 40249 | UPS_MGE[1].U31mains2
GSMUPS_MGE1U3N_inverter | INT | IOD_GSM_TCP | 250 | 40250 | UPS_MGE[1].U3N_inverter
GSMUPS_MGE1U3N_output | INT | IOD_GSM_TCP | 251 | 40251 | UPS_MGE[1].U3N_output
GSMUPS_MGE1U_battery | INT | IOD_GSM_TCP | 252 | 40252 | UPS_MGE[1].U_battery
GSMUserCurrentLevel | INT | IOD_GSM_TCP | 253 | 40253 | UserCurrentLevel | BYTE
GSMXVH_UPSstatus | INT | IOD_GSM_TCP | 254 | 40254 | XVH_UPSstatus | BYTE
GSMUPS3InverterStatus | INT | IOD_GSM_TCP | 255 | 40255 | UPS[3].InverterStatus
GSMUPS3OutputStatus | INT | IOD_GSM_TCP | 256 | 40256 | UPS[3].OutputStatus
GSMUPS3SteviloIzpadovVhodneLinije | INT | IOD_GSM_TCP | 257 | 40257 | UPS[3].SteviloIzpadovVhodneLinije
GSMUPS3UnitStatus | INT | IOD_GSM_TCP | 258 | 40258 | UPS[3].UnitStatus
GSMCirc1CosFi_III | REAL | IOD_GSM_TCP | 4001 | 44001 | Circ[1].CosFi_III
GSMCirc1DelovnaEnergija | REAL | IOD_GSM_TCP | 4003 | 44003 | Circ[1].DelovnaEnergija
GSMCirc1DelovnaMoc_III | REAL | IOD_GSM_TCP | 4005 | 44005 | Circ[1].DelovnaMoc_III
GSMCirc1DelovnaMoc_L1 | REAL | IOD_GSM_TCP | 4007 | 44007 | Circ[1].DelovnaMoc_L1
GSMCirc1DelovnaMoc_L2 | REAL | IOD_GSM_TCP | 4009 | 44009 | Circ[1].DelovnaMoc_L2
GSMCirc1DelovnaMoc_L3 | REAL | IOD_GSM_TCP | 4011 | 44011 | Circ[1].DelovnaMoc_L3
GSMCirc1Frekvenca_L1 | REAL | IOD_GSM_TCP | 4013 | 44013 | Circ[1].Frekvenca_L1
GSMCirc1InduktivnaEnergija | REAL | IOD_GSM_TCP | 4015 | 44015 | Circ[1].InduktivnaEnergija
GSMCirc1InduktivnaMoc_III | REAL | IOD_GSM_TCP | 4017 | 44017 | Circ[1].InduktivnaMoc_III
GSMCirc1JalovaMoc_L1 | REAL | IOD_GSM_TCP | 4019 | 44019 | Circ[1].JalovaMoc_L1
GSMCirc1JalovaMoc_L2 | REAL | IOD_GSM_TCP | 4021 | 44021 | Circ[1].JalovaMoc_L2
GSMCirc1JalovaMoc_L3 | REAL | IOD_GSM_TCP | 4023 | 44023 | Circ[1].JalovaMoc_L3
GSMCirc1KapacitivnaEnergija | REAL | IOD_GSM_TCP | 4025 | 44025 | Circ[1].KapacitivnaEnergija
GSMCirc1KapacitivnaMoc_III | REAL | IOD_GSM_TCP | 4027 | 44027 | Circ[1].KapacitivnaMoc_III
GSMCirc1MaximumDemand | REAL | IOD_GSM_TCP | 4029 | 44029 | Circ[1].MaximumDemand
GSMCirc1Napetost_L1_L2 | REAL | IOD_GSM_TCP | 4031 | 44031 | Circ[1].Napetost_L1_L2
GSMCirc1Napetost_L1_N | REAL | IOD_GSM_TCP | 4033 | 44033 | Circ[1].Napetost_L1_N
GSMCirc1Napetost_L2_L3 | REAL | IOD_GSM_TCP | 4035 | 44035 | Circ[1].Napetost_L2_L3
GSMCirc1Napetost_L2_N | REAL | IOD_GSM_TCP | 4037 | 44037 | Circ[1].Napetost_L2_N
GSMCirc1Napetost_L3_L1 | REAL | IOD_GSM_TCP | 4039 | 44039 | Circ[1].Napetost_L3_L1
GSMCirc1Napetost_L3_N | REAL | IOD_GSM_TCP | 4041 | 44041 | Circ[1].Napetost_L3_N
GSMCirc1NavideznaMoc_III | REAL | IOD_GSM_TCP | 4043 | 44043 | Circ[1].NavideznaMoc_III
GSMCirc1NicelniTok | REAL | IOD_GSM_TCP | 4045 | 44045 | Circ[1].NicelniTok
GSMCirc1PowerFactor_III | REAL | IOD_GSM_TCP | 4047 | 44047 | Circ[1].PowerFactor_III
GSMCirc1PowerFactor_L1 | REAL | IOD_GSM_TCP | 4049 | 44049 | Circ[1].PowerFactor_L1
GSMCirc1PowerFactor_L2 | REAL | IOD_GSM_TCP | 4051 | 44051 | Circ[1].PowerFactor_L2
GSMCirc1PowerFactor_L3 | REAL | IOD_GSM_TCP | 4053 | 44053 | Circ[1].PowerFactor_L3
GSMCirc1THDI_L1 | REAL | IOD_GSM_TCP | 4055 | 44055 | Circ[1].THDI_L1
GSMCirc1THDI_L2 | REAL | IOD_GSM_TCP | 4057 | 44057 | Circ[1].THDI_L2
GSMCirc1THDI_L3 | REAL | IOD_GSM_TCP | 4059 | 44059 | Circ[1].THDI_L3
GSMCirc1THDV_L1 | REAL | IOD_GSM_TCP | 4061 | 44061 | Circ[1].THDV_L1
GSMCirc1THDV_L2 | REAL | IOD_GSM_TCP | 4063 | 44063 | Circ[1].THDV_L2
GSMCirc1THDV_L3 | REAL | IOD_GSM_TCP | 4065 | 44065 | Circ[1].THDV_L3
GSMCirc1Tok_L1 | REAL | IOD_GSM_TCP | 4067 | 44067 | Circ[1].Tok_L1
GSMCirc1Tok_L2 | REAL | IOD_GSM_TCP | 4069 | 44069 | Circ[1].Tok_L2
GSMCirc1Tok_L3 | REAL | IOD_GSM_TCP | 4071 | 44071 | Circ[1].Tok_L3
GSMCirc1TokPovprecje_III | REAL | IOD_GSM_TCP | 4073 | 44073 | Circ[1].TokPovprecje_III
GSMPMM1ActiveEnergyConsumed_kWh | REAL | IOD_GSM_TCP | 4075 | 44075 | PMM[1].ActiveEnergyConsumed_kWh
GSMPMM1ActivePowerPhaseA_kW | REAL | IOD_GSM_TCP | 4077 | 44077 | PMM[1].ActivePowerPhaseA_kW
GSMPMM1ActivePowerPhaseB_kW | REAL | IOD_GSM_TCP | 4079 | 44079 | PMM[1].ActivePowerPhaseB_kW
GSMPMM1ActivePowerPhaseC_kW | REAL | IOD_GSM_TCP | 4081 | 44081 | PMM[1].ActivePowerPhaseC_kW
GSMPMM1AparentPowerPhaseA | REAL | IOD_GSM_TCP | 4083 | 44083 | PMM[1].AparentPowerPhaseA
GSMPMM1AparentPowerPhaseB | REAL | IOD_GSM_TCP | 4085 | 44085 | PMM[1].AparentPowerPhaseB
GSMPMM1AparentPowerPhaseC | REAL | IOD_GSM_TCP | 4087 | 44087 | PMM[1].AparentPowerPhaseC
GSMPMM1AverageCurrent_A | REAL | IOD_GSM_TCP | 4089 | 44089 | PMM[1].AverageCurrent_A
GSMPMM1AveragePhaseToNeutral_V | REAL | IOD_GSM_TCP | 4091 | 44091 | PMM[1].AveragePhaseToNeutral_V
GSMPMM1AveragePhaseToPhase_V | REAL | IOD_GSM_TCP | 4093 | 44093 | PMM[1].AveragePhaseToPhase_V
GSMPMM1CurrentInPhaseA_A | REAL | IOD_GSM_TCP | 4095 | 44095 | PMM[1].CurrentInPhaseA_A
GSMPMM1CurrentInPhaseB_A | REAL | IOD_GSM_TCP | 4097 | 44097 | PMM[1].CurrentInPhaseB_A
GSMPMM1CurrentInPhaseC_A | REAL | IOD_GSM_TCP | 4099 | 44099 | PMM[1].CurrentInPhaseC_A
GSMPMM1Frequency_Hz | REAL | IOD_GSM_TCP | 4101 | 44101 | PMM[1].Frequency_Hz
GSMPMM1Phase1Current10 | REAL | IOD_GSM_TCP | 4103 | 44103 | PMM[1].Phase[1].Current[10]
GSMPMM1Phase1Current11 | REAL | IOD_GSM_TCP | 4105 | 44105 | PMM[1].Phase[1].Current[11]
GSMPMM1Phase1Current12 | REAL | IOD_GSM_TCP | 4107 | 44107 | PMM[1].Phase[1].Current[12]
GSMPMM1Phase1Current13 | REAL | IOD_GSM_TCP | 4109 | 44109 | PMM[1].Phase[1].Current[13]
GSMPMM1Phase1Current14 | REAL | IOD_GSM_TCP | 4111 | 44111 | PMM[1].Phase[1].Current[14]
GSMPMM1Phase1Current15 | REAL | IOD_GSM_TCP | 4113 | 44113 | PMM[1].Phase[1].Current[15]
GSMPMM1Phase1Current16 | REAL | IOD_GSM_TCP | 4115 | 44115 | PMM[1].Phase[1].Current[16]
GSMPMM1Phase1Current17 | REAL | IOD_GSM_TCP | 4117 | 44117 | PMM[1].Phase[1].Current[17]
GSMPMM1Phase1Current18 | REAL | IOD_GSM_TCP | 4119 | 44119 | PMM[1].Phase[1].Current[18]
GSMPMM1Phase1Current19 | REAL | IOD_GSM_TCP | 4121 | 44121 | PMM[1].Phase[1].Current[19]
GSMPMM1Phase1Current1 | REAL | IOD_GSM_TCP | 4123 | 44123 | PMM[1].Phase[1].Current[1]
GSMPMM1Phase1Current20 | REAL | IOD_GSM_TCP | 4125 | 44125 | PMM[1].Phase[1].Current[20]
GSMPMM1Phase1Current21 | REAL | IOD_GSM_TCP | 4127 | 44127 | PMM[1].Phase[1].Current[21]
GSMPMM1Phase1Current22 | REAL | IOD_GSM_TCP | 4129 | 44129 | PMM[1].Phase[1].Current[22]
GSMPMM1Phase1Current23 | REAL | IOD_GSM_TCP | 4131 | 44131 | PMM[1].Phase[1].Current[23]
GSMPMM1Phase1Current24 | REAL | IOD_GSM_TCP | 4133 | 44133 | PMM[1].Phase[1].Current[24]
GSMPMM1Phase1Current25 | REAL | IOD_GSM_TCP | 4135 | 44135 | PMM[1].Phase[1].Current[25]
GSMPMM1Phase1Current26 | REAL | IOD_GSM_TCP | 4137 | 44137 | PMM[1].Phase[1].Current[26]
GSMPMM1Phase1Current27 | REAL | IOD_GSM_TCP | 4139 | 44139 | PMM[1].Phase[1].Current[27]
GSMPMM1Phase1Current28 | REAL | IOD_GSM_TCP | 4141 | 44141 | PMM[1].Phase[1].Current[28]
GSMPMM1Phase1Current29 | REAL | IOD_GSM_TCP | 4143 | 44143 | PMM[1].Phase[1].Current[29]
GSMPMM1Phase1Current2 | REAL | IOD_GSM_TCP | 4145 | 44145 | PMM[1].Phase[1].Current[2]
GSMPMM1Phase1Current30 | REAL | IOD_GSM_TCP | 4147 | 44147 | PMM[1].Phase[1].Current[30]
GSMPMM1Phase1Current31 | REAL | IOD_GSM_TCP | 4149 | 44149 | PMM[1].Phase[1].Current[31]
GSMPMM1Phase1Current32 | REAL | IOD_GSM_TCP | 4151 | 44151 | PMM[1].Phase[1].Current[32]
GSMPMM1Phase1Current33 | REAL | IOD_GSM_TCP | 4153 | 44153 | PMM[1].Phase[1].Current[33]
GSMPMM1Phase1Current34 | REAL | IOD_GSM_TCP | 4155 | 44155 | PMM[1].Phase[1].Current[34]
GSMPMM1Phase1Current35 | REAL | IOD_GSM_TCP | 4157 | 44157 | PMM[1].Phase[1].Current[35]
GSMPMM1Phase1Current36 | REAL | IOD_GSM_TCP | 4159 | 44159 | PMM[1].Phase[1].Current[36]
GSMPMM1Phase1Current37 | REAL | IOD_GSM_TCP | 4161 | 44161 | PMM[1].Phase[1].Current[37]
GSMPMM1Phase1Current38 | REAL | IOD_GSM_TCP | 4163 | 44163 | PMM[1].Phase[1].Current[38]
GSMPMM1Phase1Current39 | REAL | IOD_GSM_TCP | 4165 | 44165 | PMM[1].Phase[1].Current[39]
GSMPMM1Phase1Current3 | REAL | IOD_GSM_TCP | 4167 | 44167 | PMM[1].Phase[1].Current[3]
GSMPMM1Phase1Current40 | REAL | IOD_GSM_TCP | 4169 | 44169 | PMM[1].Phase[1].Current[40]
GSMPMM1Phase1Current41 | REAL | IOD_GSM_TCP | 4171 | 44171 | PMM[1].Phase[1].Current[41]
GSMPMM1Phase1Current42 | REAL | IOD_GSM_TCP | 4173 | 44173 | PMM[1].Phase[1].Current[42]
GSMPMM1Phase1Current4 | REAL | IOD_GSM_TCP | 4175 | 44175 | PMM[1].Phase[1].Current[4]
GSMPMM1Phase1Current5 | REAL | IOD_GSM_TCP | 4177 | 44177 | PMM[1].Phase[1].Current[5]
GSMPMM1Phase1Current6 | REAL | IOD_GSM_TCP | 4179 | 44179 | PMM[1].Phase[1].Current[6]
GSMPMM1Phase1Current7 | REAL | IOD_GSM_TCP | 4181 | 44181 | PMM[1].Phase[1].Current[7]
GSMPMM1Phase1Current8 | REAL | IOD_GSM_TCP | 4183 | 44183 | PMM[1].Phase[1].Current[8]
GSMPMM1Phase1Current9 | REAL | IOD_GSM_TCP | 4185 | 44185 | PMM[1].Phase[1].Current[9]
GSMPMM1Phase2Current10 | REAL | IOD_GSM_TCP | 4187 | 44187 | PMM[1].Phase[2].Current[10]
GSMPMM1Phase2Current11 | REAL | IOD_GSM_TCP | 4189 | 44189 | PMM[1].Phase[2].Current[11]
GSMPMM1Phase2Current12 | REAL | IOD_GSM_TCP | 4191 | 44191 | PMM[1].Phase[2].Current[12]
GSMPMM1Phase2Current13 | REAL | IOD_GSM_TCP | 4193 | 44193 | PMM[1].Phase[2].Current[13]
GSMPMM1Phase2Current14 | REAL | IOD_GSM_TCP | 4195 | 44195 | PMM[1].Phase[2].Current[14]
GSMPMM1Phase2Current15 | REAL | IOD_GSM_TCP | 4197 | 44197 | PMM[1].Phase[2].Current[15]
GSMPMM1Phase2Current16 | REAL | IOD_GSM_TCP | 4199 | 44199 | PMM[1].Phase[2].Current[16]
GSMPMM1Phase2Current17 | REAL | IOD_GSM_TCP | 4201 | 44201 | PMM[1].Phase[2].Current[17]
GSMPMM1Phase2Current18 | REAL | IOD_GSM_TCP | 4203 | 44203 | PMM[1].Phase[2].Current[18]
GSMPMM1Phase2Current19 | REAL | IOD_GSM_TCP | 4205 | 44205 | PMM[1].Phase[2].Current[19]
GSMPMM1Phase2Current1 | REAL | IOD_GSM_TCP | 4207 | 44207 | PMM[1].Phase[2].Current[1]
GSMPMM1Phase2Current20 | REAL | IOD_GSM_TCP | 4209 | 44209 | PMM[1].Phase[2].Current[20]
GSMPMM1Phase2Current21 | REAL | IOD_GSM_TCP | 4211 | 44211 | PMM[1].Phase[2].Current[21]
GSMPMM1Phase2Current22 | REAL | IOD_GSM_TCP | 4213 | 44213 | PMM[1].Phase[2].Current[22]
GSMPMM1Phase2Current23 | REAL | IOD_GSM_TCP | 4215 | 44215 | PMM[1].Phase[2].Current[23]
GSMPMM1Phase2Current24 | REAL | IOD_GSM_TCP | 4217 | 44217 | PMM[1].Phase[2].Current[24]
GSMPMM1Phase2Current25 | REAL | IOD_GSM_TCP | 4219 | 44219 | PMM[1].Phase[2].Current[25]
GSMPMM1Phase2Current26 | REAL | IOD_GSM_TCP | 4221 | 44221 | PMM[1].Phase[2].Current[26]
GSMPMM1Phase2Current27 | REAL | IOD_GSM_TCP | 4223 | 44223 | PMM[1].Phase[2].Current[27]
GSMPMM1Phase2Current28 | REAL | IOD_GSM_TCP | 4225 | 44225 | PMM[1].Phase[2].Current[28]
GSMPMM1Phase2Current29 | REAL | IOD_GSM_TCP | 4227 | 44227 | PMM[1].Phase[2].Current[29]
GSMPMM1Phase2Current2 | REAL | IOD_GSM_TCP | 4229 | 44229 | PMM[1].Phase[2].Current[2]
GSMPMM1Phase2Current30 | REAL | IOD_GSM_TCP | 4231 | 44231 | PMM[1].Phase[2].Current[30]
GSMPMM1Phase2Current31 | REAL | IOD_GSM_TCP | 4233 | 44233 | PMM[1].Phase[2].Current[31]
GSMPMM1Phase2Current32 | REAL | IOD_GSM_TCP | 4235 | 44235 | PMM[1].Phase[2].Current[32]
GSMPMM1Phase2Current33 | REAL | IOD_GSM_TCP | 4237 | 44237 | PMM[1].Phase[2].Current[33]
GSMPMM1Phase2Current34 | REAL | IOD_GSM_TCP | 4239 | 44239 | PMM[1].Phase[2].Current[34]
GSMPMM1Phase2Current35 | REAL | IOD_GSM_TCP | 4241 | 44241 | PMM[1].Phase[2].Current[35]
GSMPMM1Phase2Current36 | REAL | IOD_GSM_TCP | 4243 | 44243 | PMM[1].Phase[2].Current[36]
GSMPMM1Phase2Current37 | REAL | IOD_GSM_TCP | 4245 | 44245 | PMM[1].Phase[2].Current[37]
GSMPMM1Phase2Current38 | REAL | IOD_GSM_TCP | 4247 | 44247 | PMM[1].Phase[2].Current[38]
GSMPMM1Phase2Current39 | REAL | IOD_GSM_TCP | 4249 | 44249 | PMM[1].Phase[2].Current[39]
GSMPMM1Phase2Current3 | REAL | IOD_GSM_TCP | 4251 | 44251 | PMM[1].Phase[2].Current[3]
GSMPMM1Phase2Current40 | REAL | IOD_GSM_TCP | 4253 | 44253 | PMM[1].Phase[2].Current[40]
GSMPMM1Phase2Current41 | REAL | IOD_GSM_TCP | 4255 | 44255 | PMM[1].Phase[2].Current[41]
GSMPMM1Phase2Current42 | REAL | IOD_GSM_TCP | 4257 | 44257 | PMM[1].Phase[2].Current[42]
GSMPMM1Phase2Current4 | REAL | IOD_GSM_TCP | 4259 | 44259 | PMM[1].Phase[2].Current[4]
GSMPMM1Phase2Current5 | REAL | IOD_GSM_TCP | 4261 | 44261 | PMM[1].Phase[2].Current[5]
GSMPMM1Phase2Current6 | REAL | IOD_GSM_TCP | 4263 | 44263 | PMM[1].Phase[2].Current[6]
GSMPMM1Phase2Current7 | REAL | IOD_GSM_TCP | 4265 | 44265 | PMM[1].Phase[2].Current[7]
GSMPMM1Phase2Current8 | REAL | IOD_GSM_TCP | 4267 | 44267 | PMM[1].Phase[2].Current[8]
GSMPMM1Phase2Current9 | REAL | IOD_GSM_TCP | 4269 | 44269 | PMM[1].Phase[2].Current[9]
GSMPMM1Phase3Current10 | REAL | IOD_GSM_TCP | 4271 | 44271 | PMM[1].Phase[3].Current[10]
GSMPMM1Phase3Current11 | REAL | IOD_GSM_TCP | 4273 | 44273 | PMM[1].Phase[3].Current[11]
GSMPMM1Phase3Current12 | REAL | IOD_GSM_TCP | 4275 | 44275 | PMM[1].Phase[3].Current[12]
GSMPMM1Phase3Current13 | REAL | IOD_GSM_TCP | 4277 | 44277 | PMM[1].Phase[3].Current[13]
GSMPMM1Phase3Current14 | REAL | IOD_GSM_TCP | 4279 | 44279 | PMM[1].Phase[3].Current[14]
GSMPMM1Phase3Current15 | REAL | IOD_GSM_TCP | 4281 | 44281 | PMM[1].Phase[3].Current[15]
GSMPMM1Phase3Current16 | REAL | IOD_GSM_TCP | 4283 | 44283 | PMM[1].Phase[3].Current[16]
GSMPMM1Phase3Current17 | REAL | IOD_GSM_TCP | 4285 | 44285 | PMM[1].Phase[3].Current[17]
GSMPMM1Phase3Current18 | REAL | IOD_GSM_TCP | 4287 | 44287 | PMM[1].Phase[3].Current[18]
GSMPMM1Phase3Current19 | REAL | IOD_GSM_TCP | 4289 | 44289 | PMM[1].Phase[3].Current[19]
GSMPMM1Phase3Current1 | REAL | IOD_GSM_TCP | 4291 | 44291 | PMM[1].Phase[3].Current[1]
GSMPMM1Phase3Current20 | REAL | IOD_GSM_TCP | 4293 | 44293 | PMM[1].Phase[3].Current[20]
GSMPMM1Phase3Current21 | REAL | IOD_GSM_TCP | 4295 | 44295 | PMM[1].Phase[3].Current[21]
GSMPMM1Phase3Current22 | REAL | IOD_GSM_TCP | 4297 | 44297 | PMM[1].Phase[3].Current[22]
GSMPMM1Phase3Current23 | REAL | IOD_GSM_TCP | 4299 | 44299 | PMM[1].Phase[3].Current[23]
GSMPMM1Phase3Current24 | REAL | IOD_GSM_TCP | 4301 | 44301 | PMM[1].Phase[3].Current[24]
GSMPMM1Phase3Current25 | REAL | IOD_GSM_TCP | 4303 | 44303 | PMM[1].Phase[3].Current[25]
GSMPMM1Phase3Current26 | REAL | IOD_GSM_TCP | 4305 | 44305 | PMM[1].Phase[3].Current[26]
GSMPMM1Phase3Current27 | REAL | IOD_GSM_TCP | 4307 | 44307 | PMM[1].Phase[3].Current[27]
GSMPMM1Phase3Current28 | REAL | IOD_GSM_TCP | 4309 | 44309 | PMM[1].Phase[3].Current[28]
GSMPMM1Phase3Current29 | REAL | IOD_GSM_TCP | 4311 | 44311 | PMM[1].Phase[3].Current[29]
GSMPMM1Phase3Current2 | REAL | IOD_GSM_TCP | 4313 | 44313 | PMM[1].Phase[3].Current[2]
GSMPMM1Phase3Current30 | REAL | IOD_GSM_TCP | 4315 | 44315 | PMM[1].Phase[3].Current[30]
GSMPMM1Phase3Current31 | REAL | IOD_GSM_TCP | 4317 | 44317 | PMM[1].Phase[3].Current[31]
GSMPMM1Phase3Current32 | REAL | IOD_GSM_TCP | 4319 | 44319 | PMM[1].Phase[3].Current[32]
GSMPMM1Phase3Current33 | REAL | IOD_GSM_TCP | 4321 | 44321 | PMM[1].Phase[3].Current[33]
GSMPMM1Phase3Current34 | REAL | IOD_GSM_TCP | 4323 | 44323 | PMM[1].Phase[3].Current[34]
GSMPMM1Phase3Current35 | REAL | IOD_GSM_TCP | 4325 | 44325 | PMM[1].Phase[3].Current[35]
GSMPMM1Phase3Current36 | REAL | IOD_GSM_TCP | 4327 | 44327 | PMM[1].Phase[3].Current[36]
GSMPMM1Phase3Current37 | REAL | IOD_GSM_TCP | 4329 | 44329 | PMM[1].Phase[3].Current[37]
GSMPMM1Phase3Current38 | REAL | IOD_GSM_TCP | 4331 | 44331 | PMM[1].Phase[3].Current[38]
GSMPMM1Phase3Current39 | REAL | IOD_GSM_TCP | 4333 | 44333 | PMM[1].Phase[3].Current[39]
GSMPMM1Phase3Current3 | REAL | IOD_GSM_TCP | 4335 | 44335 | PMM[1].Phase[3].Current[3]
GSMPMM1Phase3Current40 | REAL | IOD_GSM_TCP | 4337 | 44337 | PMM[1].Phase[3].Current[40]
GSMPMM1Phase3Current41 | REAL | IOD_GSM_TCP | 4339 | 44339 | PMM[1].Phase[3].Current[41]
GSMPMM1Phase3Current42 | REAL | IOD_GSM_TCP | 4341 | 44341 | PMM[1].Phase[3].Current[42]
GSMPMM1Phase3Current4 | REAL | IOD_GSM_TCP | 4343 | 44343 | PMM[1].Phase[3].Current[4]
GSMPMM1Phase3Current5 | REAL | IOD_GSM_TCP | 4345 | 44345 | PMM[1].Phase[3].Current[5]
GSMPMM1Phase3Current6 | REAL | IOD_GSM_TCP | 4347 | 44347 | PMM[1].Phase[3].Current[6]
GSMPMM1Phase3Current7 | REAL | IOD_GSM_TCP | 4349 | 44349 | PMM[1].Phase[3].Current[7]
GSMPMM1Phase3Current8 | REAL | IOD_GSM_TCP | 4351 | 44351 | PMM[1].Phase[3].Current[8]
GSMPMM1Phase3Current9 | REAL | IOD_GSM_TCP | 4353 | 44353 | PMM[1].Phase[3].Current[9]
GSMPMM1PowerFactorSys | REAL | IOD_GSM_TCP | 4355 | 44355 | PMM[1].PowerFactorSys
GSMPMM1ReactiveEnergyConsumed_kVARh | REAL | IOD_GSM_TCP | 4357 | 44357 | PMM[1].ReactiveEnergyConsumed_kVARh
GSMPMM1ReactivePowerPhaseA | REAL | IOD_GSM_TCP | 4359 | 44359 | PMM[1].ReactivePowerPhaseA
GSMPMM1ReactivePowerPhaseB | REAL | IOD_GSM_TCP | 4361 | 44361 | PMM[1].ReactivePowerPhaseB
GSMPMM1ReactivePowerPhaseC | REAL | IOD_GSM_TCP | 4363 | 44363 | PMM[1].ReactivePowerPhaseC
GSMPMM1TotalActivePower_kW | REAL | IOD_GSM_TCP | 4365 | 44365 | PMM[1].TotalActivePower_kW
GSMPMM1TotalAparentPower_kVA | REAL | IOD_GSM_TCP | 4367 | 44367 | PMM[1].TotalAparentPower_kVA
GSMPMM1TotalPowerFactor | REAL | IOD_GSM_TCP | 4369 | 44369 | PMM[1].TotalPowerFactor
GSMPMM1TotalReactivePower_kVAR | REAL | IOD_GSM_TCP | 4371 | 44371 | PMM[1].TotalReactivePower_kVAR
GSMPMM1VirA_fsys | REAL | IOD_GSM_TCP | 4373 | 44373 | PMM[1].VirA_fsys
GSMPMM1VirA_Isys | REAL | IOD_GSM_TCP | 4375 | 44375 | PMM[1].VirA_Isys
GSMPMM1VirA_PFsys | REAL | IOD_GSM_TCP | 4377 | 44377 | PMM[1].VirA_PFsys
GSMPMM1VirA_Psys | REAL | IOD_GSM_TCP | 4379 | 44379 | PMM[1].VirA_Psys
GSMPMM1VirA_Qsys | REAL | IOD_GSM_TCP | 4381 | 44381 | PMM[1].VirA_Qsys
GSMPMM1VirA_Ssys | REAL | IOD_GSM_TCP | 4383 | 44383 | PMM[1].VirA_Ssys
GSMPMM1VirA_Usys | REAL | IOD_GSM_TCP | 4385 | 44385 | PMM[1].VirA_Usys
GSMPMM1VirB_fsys | REAL | IOD_GSM_TCP | 4387 | 44387 | PMM[1].VirB_fsys
GSMPMM1VirB_Isys | REAL | IOD_GSM_TCP | 4389 | 44389 | PMM[1].VirB_Isys
GSMPMM1VirB_PFsys | REAL | IOD_GSM_TCP | 4391 | 44391 | PMM[1].VirB_PFsys
GSMPMM1VirB_Psys | REAL | IOD_GSM_TCP | 4393 | 44393 | PMM[1].VirB_Psys
GSMPMM1VirB_Qsys | REAL | IOD_GSM_TCP | 4395 | 44395 | PMM[1].VirB_Qsys
GSMPMM1VirB_Ssys | REAL | IOD_GSM_TCP | 4397 | 44397 | PMM[1].VirB_Ssys
GSMPMM1VirB_Usys | REAL | IOD_GSM_TCP | 4399 | 44399 | PMM[1].VirB_Usys
GSMPMM1VirBActiveEnergyConsumed_kWh | REAL | IOD_GSM_TCP | 4401 | 44401 | PMM[1].VirBActiveEnergyConsumed_kWh
GSMPMM1VirBActivePowerPhaseA_kW | REAL | IOD_GSM_TCP | 4403 | 44403 | PMM[1].VirBActivePowerPhaseA_kW
GSMPMM1VirBActivePowerPhaseB_kW | REAL | IOD_GSM_TCP | 4405 | 44405 | PMM[1].VirBActivePowerPhaseB_kW
GSMPMM1VirBActivePowerPhaseC_kW | REAL | IOD_GSM_TCP | 4407 | 44407 | PMM[1].VirBActivePowerPhaseC_kW
GSMPMM1VirBAparentPowerPhaseA | REAL | IOD_GSM_TCP | 4409 | 44409 | PMM[1].VirBAparentPowerPhaseA
GSMPMM1VirBAparentPowerPhaseB | REAL | IOD_GSM_TCP | 4411 | 44411 | PMM[1].VirBAparentPowerPhaseB
GSMPMM1VirBAparentPowerPhaseC | REAL | IOD_GSM_TCP | 4413 | 44413 | PMM[1].VirBAparentPowerPhaseC
GSMPMM1VirBAverageCurrent_A | REAL | IOD_GSM_TCP | 4415 | 44415 | PMM[1].VirBAverageCurrent_A
GSMPMM1VirBAveragePhaseToNeutral_V | REAL | IOD_GSM_TCP | 4417 | 44417 | PMM[1].VirBAveragePhaseToNeutral_V
GSMPMM1VirBAveragePhaseToPhase_V | REAL | IOD_GSM_TCP | 4419 | 44419 | PMM[1].VirBAveragePhaseToPhase_V
GSMPMM1VirBCurrentInPhaseA_A | REAL | IOD_GSM_TCP | 4421 | 44421 | PMM[1].VirBCurrentInPhaseA_A
GSMPMM1VirBCurrentInPhaseB_A | REAL | IOD_GSM_TCP | 4423 | 44423 | PMM[1].VirBCurrentInPhaseB_A
GSMPMM1VirBCurrentInPhaseC_A | REAL | IOD_GSM_TCP | 4425 | 44425 | PMM[1].VirBCurrentInPhaseC_A
GSMPMM1VirBFrequency_Hz | REAL | IOD_GSM_TCP | 4427 | 44427 | PMM[1].VirBFrequency_Hz
GSMPMM1VirBPowerFactorSys | REAL | IOD_GSM_TCP | 4429 | 44429 | PMM[1].VirBPowerFactorSys
GSMPMM1VirBReactiveEnergyConsumed_kVARh | REAL | IOD_GSM_TCP | 4431 | 44431 | PMM[1].VirBReactiveEnergyConsumed_kVARh
GSMPMM1VirBReactivePowerPhaseA | REAL | IOD_GSM_TCP | 4433 | 44433 | PMM[1].VirBReactivePowerPhaseA
GSMPMM1VirBReactivePowerPhaseB | REAL | IOD_GSM_TCP | 4435 | 44435 | PMM[1].VirBReactivePowerPhaseB
GSMPMM1VirBReactivePowerPhaseC | REAL | IOD_GSM_TCP | 4437 | 44437 | PMM[1].VirBReactivePowerPhaseC
GSMPMM1VirBTotalActivePower_kW | REAL | IOD_GSM_TCP | 4439 | 44439 | PMM[1].VirBTotalActivePower_kW
GSMPMM1VirBTotalAparentPower_kVA | REAL | IOD_GSM_TCP | 4441 | 44441 | PMM[1].VirBTotalAparentPower_kVA
GSMPMM1VirBTotalPowerFactor | REAL | IOD_GSM_TCP | 4443 | 44443 | PMM[1].VirBTotalPowerFactor
GSMPMM1VirBTotalReactivePower_kVAR | REAL | IOD_GSM_TCP | 4445 | 44445 | PMM[1].VirBTotalReactivePower_kVAR
GSMPMM1VirBVoltageBetweenPhaseAB_V | REAL | IOD_GSM_TCP | 4447 | 44447 | PMM[1].VirBVoltageBetweenPhaseAB_V
GSMPMM1VirBVoltageBetweenPhaseAN_V | REAL | IOD_GSM_TCP | 4449 | 44449 | PMM[1].VirBVoltageBetweenPhaseAN_V
GSMPMM1VirBVoltageBetweenPhaseBC_V | REAL | IOD_GSM_TCP | 4451 | 44451 | PMM[1].VirBVoltageBetweenPhaseBC_V
GSMPMM1VirBVoltageBetweenPhaseBN_V | REAL | IOD_GSM_TCP | 4453 | 44453 | PMM[1].VirBVoltageBetweenPhaseBN_V
GSMPMM1VirBVoltageBetweenPhaseCA_V | REAL | IOD_GSM_TCP | 4455 | 44455 | PMM[1].VirBVoltageBetweenPhaseCA_V
GSMPMM1VirBVoltageBetweenPhaseCN_V | REAL | IOD_GSM_TCP | 4457 | 44457 | PMM[1].VirBVoltageBetweenPhaseCN_V
GSMPMM1VoltageBetweenPhaseAB_V | REAL | IOD_GSM_TCP | 4459 | 44459 | PMM[1].VoltageBetweenPhaseAB_V
GSMPMM1VoltageBetweenPhaseAN_V | REAL | IOD_GSM_TCP | 4461 | 44461 | PMM[1].VoltageBetweenPhaseAN_V
GSMPMM1VoltageBetweenPhaseBC_V | REAL | IOD_GSM_TCP | 4463 | 44463 | PMM[1].VoltageBetweenPhaseBC_V
GSMPMM1VoltageBetweenPhaseBN_V | REAL | IOD_GSM_TCP | 4465 | 44465 | PMM[1].VoltageBetweenPhaseBN_V
GSMPMM1VoltageBetweenPhaseCA_V | REAL | IOD_GSM_TCP | 4467 | 44467 | PMM[1].VoltageBetweenPhaseCA_V
GSMPMM1VoltageBetweenPhaseCN_V | REAL | IOD_GSM_TCP | 4469 | 44469 | PMM[1].VoltageBetweenPhaseCN_V
GSMPMMfaza01 | REAL | IOD_GSM_TCP | 4471 | 44471 | PMMfaza01
GSMPMMfaza02 | REAL | IOD_GSM_TCP | 4473 | 44473 | PMMfaza02
GSMPMMfaza03 | REAL | IOD_GSM_TCP | 4475 | 44475 | PMMfaza03
GSMPMMfaza04 | REAL | IOD_GSM_TCP | 4477 | 44477 | PMMfaza04
GSMPMMfaza05 | REAL | IOD_GSM_TCP | 4479 | 44479 | PMMfaza05
GSMPMMfaza06 | REAL | IOD_GSM_TCP | 4481 | 44481 | PMMfaza06
GSMPMMfaza07 | REAL | IOD_GSM_TCP | 4483 | 44483 | PMMfaza07
GSMPMMfaza08 | REAL | IOD_GSM_TCP | 4485 | 44485 | PMMfaza08
GSMPMMfaza09 | REAL | IOD_GSM_TCP | 4487 | 44487 | PMMfaza09
GSMPMMfaza10 | REAL | IOD_GSM_TCP | 4489 | 44489 | PMMfaza10
GSMPMMfaza11 | REAL | IOD_GSM_TCP | 4491 | 44491 | PMMfaza11
GSMPMMfaza12 | REAL | IOD_GSM_TCP | 4493 | 44493 | PMMfaza12
GSMPMMfaza13 | REAL | IOD_GSM_TCP | 4495 | 44495 | PMMfaza13
GSMPMMfaza14 | REAL | IOD_GSM_TCP | 4497 | 44497 | PMMfaza14
GSMPMMfaza15 | REAL | IOD_GSM_TCP | 4499 | 44499 | PMMfaza15
GSMPMMfaza16 | REAL | IOD_GSM_TCP | 4501 | 44501 | PMMfaza16
GSMPMMfaza17 | REAL | IOD_GSM_TCP | 4503 | 44503 | PMMfaza17
GSMPMMfaza18 | REAL | IOD_GSM_TCP | 4505 | 44505 | PMMfaza18
GSMPMMfaza19 | REAL | IOD_GSM_TCP | 4507 | 44507 | PMMfaza19
GSMPMMfaza20 | REAL | IOD_GSM_TCP | 4509 | 44509 | PMMfaza20
GSMPMMfaza21 | REAL | IOD_GSM_TCP | 4511 | 44511 | PMMfaza21
GSMPMMfaza22 | REAL | IOD_GSM_TCP | 4513 | 44513 | PMMfaza22
GSMPMMfaza23 | REAL | IOD_GSM_TCP | 4515 | 44515 | PMMfaza23
GSMPMMfaza24 | REAL | IOD_GSM_TCP | 4517 | 44517 | PMMfaza24
GSMPMMfaza25 | REAL | IOD_GSM_TCP | 4519 | 44519 | PMMfaza25
GSMPMMfaza26 | REAL | IOD_GSM_TCP | 4521 | 44521 | PMMfaza26
GSMPMMfaza27 | REAL | IOD_GSM_TCP | 4523 | 44523 | PMMfaza27
GSMPMMfaza28 | REAL | IOD_GSM_TCP | 4525 | 44525 | PMMfaza28
GSMPMMfaza29 | REAL | IOD_GSM_TCP | 4527 | 44527 | PMMfaza29
GSMPMMfaza30 | REAL | IOD_GSM_TCP | 4529 | 44529 | PMMfaza30
GSMPMMfaza31 | REAL | IOD_GSM_TCP | 4531 | 44531 | PMMfaza31
GSMPMMfaza32 | REAL | IOD_GSM_TCP | 4533 | 44533 | PMMfaza32
GSMPMMfaza33 | REAL | IOD_GSM_TCP | 4535 | 44535 | PMMfaza33
GSMPMMfaza34 | REAL | IOD_GSM_TCP | 4537 | 44537 | PMMfaza34
GSMPMMfaza35 | REAL | IOD_GSM_TCP | 4539 | 44539 | PMMfaza35
GSMPMMfaza36 | REAL | IOD_GSM_TCP | 4541 | 44541 | PMMfaza36
GSMPMMfaza37 | REAL | IOD_GSM_TCP | 4543 | 44543 | PMMfaza37
GSMPMMfaza38 | REAL | IOD_GSM_TCP | 4545 | 44545 | PMMfaza38
GSMPMMfaza39 | REAL | IOD_GSM_TCP | 4547 | 44547 | PMMfaza39
GSMPMMfaza40 | REAL | IOD_GSM_TCP | 4549 | 44549 | PMMfaza40
GSMPMMfaza41 | REAL | IOD_GSM_TCP | 4551 | 44551 | PMMfaza41
GSMPMMfaza42 | REAL | IOD_GSM_TCP | 4553 | 44553 | PMMfaza42
GSMUPS1EstimatedChargeRemaining | REAL | IOD_GSM_TCP | 4555 | 44555 | UPS[1].EstimatedChargeRemaining
GSMUPS1EstimatedMinutesRemaining | REAL | IOD_GSM_TCP | 4557 | 44557 | UPS[1].EstimatedMinutesRemaining
GSMUPS1IzhodMocL1 | REAL | IOD_GSM_TCP | 4559 | 44559 | UPS[1].IzhodMocL1
GSMUPS1IzhodMocL2 | REAL | IOD_GSM_TCP | 4561 | 44561 | UPS[1].IzhodMocL2
GSMUPS1IzhodMocL3 | REAL | IOD_GSM_TCP | 4563 | 44563 | UPS[1].IzhodMocL3
GSMUPS1NapetostBaterije | REAL | IOD_GSM_TCP | 4565 | 44565 | UPS[1].NapetostBaterije
GSMUPS1TemperaturaBaterije | REAL | IOD_GSM_TCP | 4567 | 44567 | UPS[1].TemperaturaBaterije
GSMUPS1VhodFrekvencaL1 | REAL | IOD_GSM_TCP | 4569 | 44569 | UPS[1].VhodFrekvencaL1
GSMUPS1VhodFrekvencaL2 | REAL | IOD_GSM_TCP | 4571 | 44571 | UPS[1].VhodFrekvencaL2
GSMUPS1VhodFrekvencaL3 | REAL | IOD_GSM_TCP | 4573 | 44573 | UPS[1].VhodFrekvencaL3
GSMUPS1VhodNapetostL1 | REAL | IOD_GSM_TCP | 4575 | 44575 | UPS[1].VhodNapetostL1
GSMUPS1VhodNapetostL2 | REAL | IOD_GSM_TCP | 4577 | 44577 | UPS[1].VhodNapetostL2
GSMUPS1VhodNapetostL3 | REAL | IOD_GSM_TCP | 4579 | 44579 | UPS[1].VhodNapetostL3
GSMUPS2EstimatedChargeRemaining | REAL | IOD_GSM_TCP | 4581 | 44581 | UPS[2].EstimatedChargeRemaining
GSMUPS2EstimatedMinutesRemaining | REAL | IOD_GSM_TCP | 4583 | 44583 | UPS[2].EstimatedMinutesRemaining
GSMUPS2IzhodMocL1 | REAL | IOD_GSM_TCP | 4585 | 44585 | UPS[2].IzhodMocL1
GSMUPS2IzhodMocL2 | REAL | IOD_GSM_TCP | 4587 | 44587 | UPS[2].IzhodMocL2
GSMUPS2IzhodMocL3 | REAL | IOD_GSM_TCP | 4589 | 44589 | UPS[2].IzhodMocL3
GSMUPS2NapetostBaterije | REAL | IOD_GSM_TCP | 4591 | 44591 | UPS[2].NapetostBaterije
GSMUPS2TemperaturaBaterije | REAL | IOD_GSM_TCP | 4593 | 44593 | UPS[2].TemperaturaBaterije
GSMUPS2VhodFrekvencaL1 | REAL | IOD_GSM_TCP | 4595 | 44595 | UPS[2].VhodFrekvencaL1
GSMUPS2VhodFrekvencaL2 | REAL | IOD_GSM_TCP | 4597 | 44597 | UPS[2].VhodFrekvencaL2
GSMUPS2VhodFrekvencaL3 | REAL | IOD_GSM_TCP | 4599 | 44599 | UPS[2].VhodFrekvencaL3
GSMUPS2VhodNapetostL1 | REAL | IOD_GSM_TCP | 4601 | 44601 | UPS[2].VhodNapetostL1
GSMUPS2VhodNapetostL2 | REAL | IOD_GSM_TCP | 4603 | 44603 | UPS[2].VhodNapetostL2
GSMUPS2VhodNapetostL3 | REAL | IOD_GSM_TCP | 4605 | 44605 | UPS[2].VhodNapetostL3
GSMXVHdepltedBatery1 | REAL | IOD_GSM_TCP | 4607 | 44607 | XVHdepltedBatery1
GSMXVHdepltedBatery2 | REAL | IOD_GSM_TCP | 4609 | 44609 | XVHdepltedBatery2
GSMXVHlowBatery1 | REAL | IOD_GSM_TCP | 4611 | 44611 | XVHlowBatery1
GSMXVHlowBatery2 | REAL | IOD_GSM_TCP | 4613 | 44613 | XVHlowBatery2
GSMPMMskupniTokA | REAL | IOD_GSM_TCP | 4615 | 44615 | PMMskupniTokA
GSMPMMskupniTokB | REAL | IOD_GSM_TCP | 4617 | 44617 | PMMskupniTokB
GSMUPS3EstimatedChargeRemaining | REAL | IOD_GSM_TCP | 4619 | 44619 | UPS[3].EstimatedChargeRemaining
GSMUPS3EstimatedMinutesRemaining | REAL | IOD_GSM_TCP | 4621 | 44621 | UPS[3].EstimatedMinutesRemaining
GSMUPS3IzhodMocL1 | REAL | IOD_GSM_TCP | 4623 | 44623 | UPS[3].IzhodMocL1
GSMUPS3IzhodMocL2 | REAL | IOD_GSM_TCP | 4625 | 44625 | UPS[3].IzhodMocL2
GSMUPS3IzhodMocL3 | REAL | IOD_GSM_TCP | 4627 | 44627 | UPS[3].IzhodMocL3
GSMUPS3NapetostBaterije | REAL | IOD_GSM_TCP | 4629 | 44629 | UPS[3].NapetostBaterije
GSMUPS3TemperaturaBaterije | REAL | IOD_GSM_TCP | 4631 | 44631 | UPS[3].TemperaturaBaterije
GSMUPS3VhodFrekvencaL1 | REAL | IOD_GSM_TCP | 4633 | 44633 | UPS[3].VhodFrekvencaL1
GSMUPS3VhodFrekvencaL2 | REAL | IOD_GSM_TCP | 4635 | 44635 | UPS[3].VhodFrekvencaL2
GSMUPS3VhodFrekvencaL3 | REAL | IOD_GSM_TCP | 4637 | 44637 | UPS[3].VhodFrekvencaL3
GSMUPS3VhodNapetostL1 | REAL | IOD_GSM_TCP | 4639 | 44639 | UPS[3].VhodNapetostL1
GSMUPS3VhodNapetostL2 | REAL | IOD_GSM_TCP | 4641 | 44641 | UPS[3].VhodNapetostL2
GSMUPS3VhodNapetostL3 | REAL | IOD_GSM_TCP | 4643 | 44643 | UPS[3].VhodNapetostL3
GSMCirc1MaximumDemandA2 | REAL | IOD_GSM_TCP | 4645 | 44645 | Circ[1].MaximumDemandA2
GSMCirc1MaximumDemandA3 | REAL | IOD_GSM_TCP | 4647 | 44647 | Circ[1].MaximumDemandA3
GSMCirc1RazEner_D_SCADA | REAL | IOD_GSM_TCP | 4649 | 44649 | Circ[1].RazEner_D_SCADA
GSMCirc1RazEner_T_SCADA | REAL | IOD_GSM_TCP | 4651 | 44651 | Circ[1].RazEner_T_SCADA
GSMCirc1RazEner_M_SCADA | REAL | IOD_GSM_TCP | 4653 | 44653 | Circ[1].RazEner_M_SCADA
GSMDate_Time0 | STRING | IOD_GSM_TCP | 5001 | 45001[15] | Date_Time[0]
GSMDate_Time1 | STRING | IOD_GSM_TCP | 5016 | 45016[15] | Date_Time[1]
GSMDate_Time2 | STRING | IOD_GSM_TCP | 5031 | 45031[15] | Date_Time[2]
GSMDate_Time3 | STRING | IOD_GSM_TCP | 5046 | 45046[15] | Date_Time[3]
GSMUserCurrentName | STRING | IOD_GSM_TCP | 5061 | 45061[15] | UserCurrentName
GSMkom_nast_cas_izpada | UINT | IOD_GSM_TCP | 6001 | 46001 | kom_nast_cas_izpada
GSMPMM1AlarmPhase1C01_16_60to80 | UINT | IOD_GSM_TCP | 6002 | 46002 | PMM[1].AlarmPhase[1].C01_16_60to80
GSMPMM1AlarmPhase1C01_16_over80 | UINT | IOD_GSM_TCP | 6003 | 46003 | PMM[1].AlarmPhase[1].C01_16_over80
GSMPMM1AlarmPhase1C17_32_60to80 | UINT | IOD_GSM_TCP | 6004 | 46004 | PMM[1].AlarmPhase[1].C17_32_60to80
GSMPMM1AlarmPhase1C17_32_over80 | UINT | IOD_GSM_TCP | 6005 | 46005 | PMM[1].AlarmPhase[1].C17_32_over80
GSMPMM1AlarmPhase1C33_42_60to80 | UINT | IOD_GSM_TCP | 6006 | 46006 | PMM[1].AlarmPhase[1].C33_42_60to80
GSMPMM1AlarmPhase1C33_42_over80 | UINT | IOD_GSM_TCP | 6007 | 46007 | PMM[1].AlarmPhase[1].C33_42_over80
GSMPMM1AlarmPhase2C01_16_60to80 | UINT | IOD_GSM_TCP | 6008 | 46008 | PMM[1].AlarmPhase[2].C01_16_60to80
GSMPMM1AlarmPhase2C01_16_over80 | UINT | IOD_GSM_TCP | 6009 | 46009 | PMM[1].AlarmPhase[2].C01_16_over80
GSMPMM1AlarmPhase2C17_32_60to80 | UINT | IOD_GSM_TCP | 6010 | 46010 | PMM[1].AlarmPhase[2].C17_32_60to80
GSMPMM1AlarmPhase2C17_32_over80 | UINT | IOD_GSM_TCP | 6011 | 46011 | PMM[1].AlarmPhase[2].C17_32_over80
GSMPMM1AlarmPhase2C33_42_60to80 | UINT | IOD_GSM_TCP | 6012 | 46012 | PMM[1].AlarmPhase[2].C33_42_60to80
GSMPMM1AlarmPhase2C33_42_over80 | UINT | IOD_GSM_TCP | 6013 | 46013 | PMM[1].AlarmPhase[2].C33_42_over80
GSMPMM1AlarmPhase3C01_16_60to80 | UINT | IOD_GSM_TCP | 6014 | 46014 | PMM[1].AlarmPhase[3].C01_16_60to80
GSMPMM1AlarmPhase3C01_16_over80 | UINT | IOD_GSM_TCP | 6015 | 46015 | PMM[1].AlarmPhase[3].C01_16_over80
GSMPMM1AlarmPhase3C17_32_60to80 | UINT | IOD_GSM_TCP | 6016 | 46016 | PMM[1].AlarmPhase[3].C17_32_60to80
GSMPMM1AlarmPhase3C17_32_over80 | UINT | IOD_GSM_TCP | 6017 | 46017 | PMM[1].AlarmPhase[3].C17_32_over80
GSMPMM1AlarmPhase3C33_42_60to80 | UINT | IOD_GSM_TCP | 6018 | 46018 | PMM[1].AlarmPhase[3].C33_42_60to80
GSMPMM1AlarmPhase3C33_42_over80 | UINT | IOD_GSM_TCP | 6019 | 46019 | PMM[1].AlarmPhase[3].C33_42_over80
GSMUPS1StatusBaterije | UINT | IOD_GSM_TCP | 6020 | 46020 | UPS[1].StatusBaterije
GSMUPS2StatusBaterije | UINT | IOD_GSM_TCP | 6021 | 46021 | UPS[2].StatusBaterije
GSMK1_obr_u_skupno | UINT | IOD_GSM_TCP | 6022 | 46022 | K1_obr_u_skupno
GSMK2_obr_u_skupno | UINT | IOD_GSM_TCP | 6023 | 46023 | K2_obr_u_skupno
GSMUPS3StatusBaterije | UINT | IOD_GSM_TCP | 6024 | 46024 | UPS[3].StatusBaterije

## variable_new
GSM_DanEnergCirc1 | LONG | IOD_GSM_disk | L0[30] | [6 empty] | 6157 | 0
GSM_CasDDanEnergCirc1 | INT | IOD_GSM_disk | I0[30] | [6 empty] | 6157 | 0
GSM_CasMDanEnergCirc1 | INT | IOD_GSM_disk | I30[30] | [6 empty] | 6157 | 0
GSM_TedenEnergCirc1 | LONG | IOD_GSM_disk | L30[30] | [6 empty] | 6157 | 0
GSM_CasDTedenEnergCirc1 | INT | IOD_GSM_disk | I60[30] | [6 empty] | 6157 | 0
GSM_CasMTedenEnergCirc1 | INT | IOD_GSM_disk | I90[30] | [6 empty] | 6157 | 0
GSM_MesecEnergCirc1 | LONG | IOD_GSM_disk | L90[30] | [6 empty] | 6157 | 0
GSM_CasDMesecEnergCirc1 | INT | IOD_GSM_disk | I120[30] | [6 empty] | 6157 | 0
GSM_CasMMesecEnergCirc1 | INT | IOD_GSM_disk | I150[30] | [6 empty] | 6157 | 0
GSM_StSt_DanEnergCirc1 | LONG | IOD_GSM_disk | L270 | [6 empty] | 6157 | 0
GSM_StSt_TedenEnergCirc1 | LONG | IOD_GSM_disk | L272 | [6 empty] | 6157 | 0
GSM_StSt_MesecEnergCirc1 | LONG | IOD_GSM_disk | L274 | [6 empty] | 6157 | 0
GSM_StStCasDDanEnergCirc1 | INT | IOD_GSM_disk | I276 | [6 empty] | 6157 | 0
GSM_StStCasMDanEnergCirc1 | INT | IOD_GSM_disk | I277 | [6 empty] | 6157 | 0
GSM_StStCasDTedenEnergCirc1 | INT | IOD_GSM_disk | I278 | [6 empty] | 6157 | 0
GSM_StStCasMTedenEnergCirc1 | INT | IOD_GSM_disk | I279 | [6 empty] | 6157 | 0
GSM_StStCasDMesecEnergCirc1 | INT | IOD_GSM_disk | I280 | [6 empty] | 6157 | 0
GSM_StStCasMMesecEnergCirc1 | INT | IOD_GSM_disk | I281 | [6 empty] | 6157 | 0
GSM_MaxDnevnaEnergija | LONG | IOD_GSM_disk | L282 | 0 | 9999999 | 0 | 9999999 |  | ####### | 6157 | 0
GSM_MaxMesecnaEnergija | LONG | IOD_GSM_disk | L284 | 0 | 9999999 | 0 | 9999999 |  | ####### | 6157 | 0
GSM_MaxTedenskaEnergija | LONG | IOD_GSM_disk | L286 | 0 | 9999999 | 0 | 9999999 |  | ####### | 6157 | 0
GSM_Prikaz_analizatorja_ce_je_1 | DIGITAL | IOD_GSM_mem | D287 | [6 empty] | 6157 | 0
GSMAlarmGenUPS_A_V23 | DIGITAL | IOD_GSM_TCP | 00001
GSMAlarmGenUPS_V23 | DIGITAL | IOD_GSM_TCP | 00002
GSMAlarmGenUPS_V25 | DIGITAL | IOD_GSM_TCP | 00003
GSMAlarmPMM1VirATokPrevisok | DIGITAL | IOD_GSM_TCP | 00004
GSMAlarmPMM1VirATokVisok | DIGITAL | IOD_GSM_TCP | 00005
GSMAlarmPMM1VirBTokPrevisok | DIGITAL | IOD_GSM_TCP | 00006
GSMAlarmPMM1VirBTokVisok | DIGITAL | IOD_GSM_TCP | 00007
GSMAlarmPMM2x17nad8010 | DIGITAL | IOD_GSM_TCP | 00008
GSMAlarmPMM2x17nad8011 | DIGITAL | IOD_GSM_TCP | 00009
GSMAlarmPMM2x17nad8012 | DIGITAL | IOD_GSM_TCP | 00010
GSMAlarmPMM2x17nad8013 | DIGITAL | IOD_GSM_TCP | 00011
GSMAlarmPMM2x17nad8014 | DIGITAL | IOD_GSM_TCP | 00012
GSMAlarmPMM2x17nad8015 | DIGITAL | IOD_GSM_TCP | 00013
GSMAlarmPMM2x17nad8016 | DIGITAL | IOD_GSM_TCP | 00014
GSMAlarmPMM2x17nad8017 | DIGITAL | IOD_GSM_TCP | 00015
GSMAlarmPMM2x17nad8018 | DIGITAL | IOD_GSM_TCP | 00016
GSMAlarmPMM2x17nad8019 | DIGITAL | IOD_GSM_TCP | 00017
GSMAlarmPMM2x17nad801 | DIGITAL | IOD_GSM_TCP | 00018
GSMAlarmPMM2x17nad8020 | DIGITAL | IOD_GSM_TCP | 00019
GSMAlarmPMM2x17nad8021 | DIGITAL | IOD_GSM_TCP | 00020
GSMAlarmPMM2x17nad8022 | DIGITAL | IOD_GSM_TCP | 00021
GSMAlarmPMM2x17nad8023 | DIGITAL | IOD_GSM_TCP | 00022
GSMAlarmPMM2x17nad8024 | DIGITAL | IOD_GSM_TCP | 00023
GSMAlarmPMM2x17nad8025 | DIGITAL | IOD_GSM_TCP | 00024
GSMAlarmPMM2x17nad8026 | DIGITAL | IOD_GSM_TCP | 00025
GSMAlarmPMM2x17nad8027 | DIGITAL | IOD_GSM_TCP | 00026
GSMAlarmPMM2x17nad8028 | DIGITAL | IOD_GSM_TCP | 00027
GSMAlarmPMM2x17nad8029 | DIGITAL | IOD_GSM_TCP | 00028
GSMAlarmPMM2x17nad802 | DIGITAL | IOD_GSM_TCP | 00029
GSMAlarmPMM2x17nad8030 | DIGITAL | IOD_GSM_TCP | 00030
GSMAlarmPMM2x17nad8031 | DIGITAL | IOD_GSM_TCP | 00031
GSMAlarmPMM2x17nad8032 | DIGITAL | IOD_GSM_TCP | 00032
GSMAlarmPMM2x17nad8033 | DIGITAL | IOD_GSM_TCP | 00033
GSMAlarmPMM2x17nad8034 | DIGITAL | IOD_GSM_TCP | 00034
GSMAlarmPMM2x17nad8035 | DIGITAL | IOD_GSM_TCP | 00035
GSMAlarmPMM2x17nad8036 | DIGITAL | IOD_GSM_TCP | 00036
GSMAlarmPMM2x17nad8037 | DIGITAL | IOD_GSM_TCP | 00037
GSMAlarmPMM2x17nad8038 | DIGITAL | IOD_GSM_TCP | 00038
GSMAlarmPMM2x17nad8039 | DIGITAL | IOD_GSM_TCP | 00039
GSMAlarmPMM2x17nad803 | DIGITAL | IOD_GSM_TCP | 00040
GSMAlarmPMM2x17nad8040 | DIGITAL | IOD_GSM_TCP | 00041
GSMAlarmPMM2x17nad8041 | DIGITAL | IOD_GSM_TCP | 00042
GSMAlarmPMM2x17nad8042 | DIGITAL | IOD_GSM_TCP | 00043
GSMAlarmPMM2x17nad804 | DIGITAL | IOD_GSM_TCP | 00044
GSMAlarmPMM2x17nad805 | DIGITAL | IOD_GSM_TCP | 00045
GSMAlarmPMM2x17nad806 | DIGITAL | IOD_GSM_TCP | 00046
GSMAlarmPMM2x17nad807 | DIGITAL | IOD_GSM_TCP | 00047
GSMAlarmPMM2x17nad808 | DIGITAL | IOD_GSM_TCP | 00048
GSMAlarmPMM2x17nad809 | DIGITAL | IOD_GSM_TCP | 00049
GSMCirc1CosFi_III | REAL | IOD_GSM_TCP | 44001 | -1 | 1 | -1 | 1 |  | ##.##
GSMCirc1DelovnaEnergija | REAL | IOD_GSM_TCP | 44003
GSMCirc1DelovnaMoc_III | REAL | IOD_GSM_TCP | 44005 | 0 | 50 | 0 | 50 | kW | ###.#
GSMCirc1DelovnaMoc_L1 | REAL | IOD_GSM_TCP | 44007 | 0 | 50 | 0 | 50 | kW | ###.#
GSMCirc1DelovnaMoc_L2 | REAL | IOD_GSM_TCP | 44009 | 0 | 50 | 0 | 50 | kW | ###.#
GSMCirc1DelovnaMoc_L3 | REAL | IOD_GSM_TCP | 44011 | 0 | 50 | 0 | 50 | kW | ###.#
GSMCirc1Frekvenca_L1 | REAL | IOD_GSM_TCP | 44013 | 0 | 60 | 0 | 60 | Hz | ##.#
GSMCirc1InduktivnaEnergija | REAL | IOD_GSM_TCP | 44015
GSMCirc1InduktivnaMoc_III | REAL | IOD_GSM_TCP | 44017 | 0 | 50 | 0 | 50 | kVAR | ###.#
GSMCirc1JalovaMoc_L1 | REAL | IOD_GSM_TCP | 44019 | 0 | 50 | 0 | 50 | kVAR | ###.#
GSMCirc1JalovaMoc_L2 | REAL | IOD_GSM_TCP | 44021 | 0 | 50 | 0 | 50 | kVAR | ###.#
GSMCirc1JalovaMoc_L3 | REAL | IOD_GSM_TCP | 44023 | 0 | 50 | 0 | 50 | kVAR | ###.#
GSMCirc1KapacitivnaEnergija | REAL | IOD_GSM_TCP | 44025
GSMCirc1KapacitivnaMoc_III | REAL | IOD_GSM_TCP | 44027 | 0 | 50 | 0 | 50 | kVAR | ###.#
GSMCirc1MaximumDemand | REAL | IOD_GSM_TCP | 44029 | 0 | 1200 | 0 | 1200 | A | ###.#
GSMCirc1Napetost_L1_L2 | REAL | IOD_GSM_TCP | 44031 | 0 | 450 | 0 | 450 | V | ###.#
GSMCirc1Napetost_L1_N | REAL | IOD_GSM_TCP | 44033 | 0 | 270 | 0 | 270 | V | ###.#
GSMCirc1Napetost_L2_L3 | REAL | IOD_GSM_TCP | 44035 | 0 | 450 | 0 | 450 | V | ###.#
GSMCirc1Napetost_L2_N | REAL | IOD_GSM_TCP | 44037 | 0 | 270 | 0 | 270 | V | ###.#
GSMCirc1Napetost_L3_L1 | REAL | IOD_GSM_TCP | 44039 | 0 | 450 | 0 | 450 | V | ###.#
GSMCirc1Napetost_L3_N | REAL | IOD_GSM_TCP | 44041 | 0 | 270 | 0 | 270 | V | ###.#
GSMCirc1NavideznaMoc_III | REAL | IOD_GSM_TCP | 44043 | 0 | 50 | 0 | 50 | kVA | ###.#
GSMCirc1NicelniTok | REAL | IOD_GSM_TCP | 44045 | 0 | 200 | 0 | 200 | A | ###.#
GSMCirc1PowerFactor_III | REAL | IOD_GSM_TCP | 44047 | -1 | 1 | -1 | 1 |  | ##.##
GSMCirc1PowerFactor_L1 | REAL | IOD_GSM_TCP | 44049 | -1 | 1 | -1 | 1 |  | ##.##
GSMCirc1PowerFactor_L2 | REAL | IOD_GSM_TCP | 44051 | -1 | 1 | -1 | 1 |  | ##.##
GSMCirc1PowerFactor_L3 | REAL | IOD_GSM_TCP | 44053 | -1 | 1 | -1 | 1 |  | ##.##
GSMCirc1THDI_L1 | REAL | IOD_GSM_TCP | 44055 | 0 | 10 | 0 | 10 | % | ###.#
GSMCirc1THDI_L2 | REAL | IOD_GSM_TCP | 44057 | 0 | 10 | 0 | 10 | % | ###.#
GSMCirc1THDI_L3 | REAL | IOD_GSM_TCP | 44059 | 0 | 10 | 0 | 10 | % | ###.#
GSMCirc1THDV_L1 | REAL | IOD_GSM_TCP | 44061 | 0 | 10 | 0 | 10 | % | ###.#
GSMCirc1THDV_L2 | REAL | IOD_GSM_TCP | 44063 | 0 | 10 | 0 | 10 | % | ###.#
GSMCirc1THDV_L3 | REAL | IOD_GSM_TCP | 44065 | 0 | 10 | 0 | 10 | % | ###.#
GSMCirc1Tok_L1 | REAL | IOD_GSM_TCP | 44067 | 0 | 200 | 0 | 200 | A | ###.#
GSMCirc1Tok_L2 | REAL | IOD_GSM_TCP | 44069 | 0 | 200 | 0 | 200 | A | ###.#
GSMCirc1Tok_L3 | REAL | IOD_GSM_TCP | 44071 | 0 | 200 | 0 | 200 | A | ###.#
GSMCirc1TokPovprecje_III | REAL | IOD_GSM_TCP | 44073 | 0 | 200 | 0 | 200 | A | ###.#
GSMComError | DIGITAL | IOD_GSM_TCP | 00050
GSMComSCADA | DIGITAL | IOD_GSM_TCP | 00051
GSMComSCADA1 | DIGITAL | IOD_GSM_TCP | 00052
GSMComSCADA2 | DIGITAL | IOD_GSM_TCP | 00053
GSMComSCADA3 | DIGITAL | IOD_GSM_TCP | 00054
GSMDate_Time0 | STRING | IOD_GSM_TCP | 45001[15]
GSMDate_Time1 | STRING | IOD_GSM_TCP | 45016[15]
GSMDate_Time2 | STRING | IOD_GSM_TCP | 45031[15]
GSMDate_Time3 | STRING | IOD_GSM_TCP | 45046[15]
GSMDateTimeDan | INT | IOD_GSM_TCP | 40001
GSMDateTimeLeto | INT | IOD_GSM_TCP | 40002
GSMDateTimeLeto2 | INT | IOD_GSM_TCP | 40003
GSMDateTimeMesec | INT | IOD_GSM_TCP | 40004
GSMDateTimeMinuta | INT | IOD_GSM_TCP | 40005
GSMDateTimeSekunda | INT | IOD_GSM_TCP | 40006
GSMDateTimeUra | INT | IOD_GSM_TCP | 40007
GSMErrComCirc1 | DIGITAL | IOD_GSM_TCP | 00055
GSMErrComKlima1 | DIGITAL | IOD_GSM_TCP | 00056
GSMErrComKlima2 | DIGITAL | IOD_GSM_TCP | 00057
GSMErrComPMM1 | DIGITAL | IOD_GSM_TCP | 00058
GSMErrComPort2 | DIGITAL | IOD_GSM_TCP | 00059
GSMErrComPort3 | DIGITAL | IOD_GSM_TCP | 00060
GSMErrComPort4 | DIGITAL | IOD_GSM_TCP | 00061
GSMErrComUPS1 | DIGITAL | IOD_GSM_TCP | 00062
GSMErrComUPS2 | DIGITAL | IOD_GSM_TCP | 00063
GSMErrComUPSMGE1 | DIGITAL | IOD_GSM_TCP | 00064
GSMErrorComCirc1Code10 | INT | IOD_GSM_TCP | 40008
GSMErrorComCirc1Code11 | INT | IOD_GSM_TCP | 40009
GSMErrorComCirc1Code12 | INT | IOD_GSM_TCP | 40010
GSMErrorComCirc1Code13 | INT | IOD_GSM_TCP | 40011
GSMErrorComCirc1Code14 | INT | IOD_GSM_TCP | 40012
GSMErrorComCirc1Code15 | INT | IOD_GSM_TCP | 40013
GSMErrorComCirc1Code1 | INT | IOD_GSM_TCP | 40014
GSMErrorComCirc1Code2 | INT | IOD_GSM_TCP | 40015
GSMErrorComCirc1Code3 | INT | IOD_GSM_TCP | 40016
GSMErrorComCirc1Code4 | INT | IOD_GSM_TCP | 40017
GSMErrorComCirc1Code5 | INT | IOD_GSM_TCP | 40018
GSMErrorComCirc1Code6 | INT | IOD_GSM_TCP | 40019
GSMErrorComCirc1Code7 | INT | IOD_GSM_TCP | 40020
GSMErrorComCirc1Code8 | INT | IOD_GSM_TCP | 40021
GSMErrorComCirc1Code9 | INT | IOD_GSM_TCP | 40022
GSMErrorComCirc1Error | DIGITAL | IOD_GSM_TCP | 00065
GSMErrorComCirc1Status | INT | IOD_GSM_TCP | 40023
GSMErrorComKlima1Code10 | INT | IOD_GSM_TCP | 40024
GSMErrorComKlima1Code11 | INT | IOD_GSM_TCP | 40025
GSMErrorComKlima1Code12 | INT | IOD_GSM_TCP | 40026
GSMErrorComKlima1Code13 | INT | IOD_GSM_TCP | 40027
GSMErrorComKlima1Code14 | INT | IOD_GSM_TCP | 40028
GSMErrorComKlima1Code15 | INT | IOD_GSM_TCP | 40029
GSMErrorComKlima1Code1 | INT | IOD_GSM_TCP | 40030
GSMErrorComKlima1Code2 | INT | IOD_GSM_TCP | 40031
GSMErrorComKlima1Code3 | INT | IOD_GSM_TCP | 40032
GSMErrorComKlima1Code4 | INT | IOD_GSM_TCP | 40033
GSMErrorComKlima1Code5 | INT | IOD_GSM_TCP | 40034
GSMErrorComKlima1Code6 | INT | IOD_GSM_TCP | 40035
GSMErrorComKlima1Code7 | INT | IOD_GSM_TCP | 40036
GSMErrorComKlima1Code8 | INT | IOD_GSM_TCP | 40037
GSMErrorComKlima1Code9 | INT | IOD_GSM_TCP | 40038
GSMErrorComKlima1Error | DIGITAL | IOD_GSM_TCP | 00066
GSMErrorComKlima1Status | INT | IOD_GSM_TCP | 40039
GSMErrorComKlima2Code10 | INT | IOD_GSM_TCP | 40040
GSMErrorComKlima2Code11 | INT | IOD_GSM_TCP | 40041
GSMErrorComKlima2Code12 | INT | IOD_GSM_TCP | 40042
GSMErrorComKlima2Code13 | INT | IOD_GSM_TCP | 40043
GSMErrorComKlima2Code14 | INT | IOD_GSM_TCP | 40044
GSMErrorComKlima2Code15 | INT | IOD_GSM_TCP | 40045
GSMErrorComKlima2Code1 | INT | IOD_GSM_TCP | 40046
GSMErrorComKlima2Code2 | INT | IOD_GSM_TCP | 40047
GSMErrorComKlima2Code3 | INT | IOD_GSM_TCP | 40048
GSMErrorComKlima2Code4 | INT | IOD_GSM_TCP | 40049
GSMErrorComKlima2Code5 | INT | IOD_GSM_TCP | 40050
GSMErrorComKlima2Code6 | INT | IOD_GSM_TCP | 40051
GSMErrorComKlima2Code7 | INT | IOD_GSM_TCP | 40052
GSMErrorComKlima2Code8 | INT | IOD_GSM_TCP | 40053
GSMErrorComKlima2Code9 | INT | IOD_GSM_TCP | 40054
GSMErrorComKlima2Error | DIGITAL | IOD_GSM_TCP | 00067
GSMErrorComKlima2Status | INT | IOD_GSM_TCP | 40055
GSMErrorComPMM1Code10 | INT | IOD_GSM_TCP | 40056
GSMErrorComPMM1Code11 | INT | IOD_GSM_TCP | 40057
GSMErrorComPMM1Code12 | INT | IOD_GSM_TCP | 40058
GSMErrorComPMM1Code13 | INT | IOD_GSM_TCP | 40059
GSMErrorComPMM1Code14 | INT | IOD_GSM_TCP | 40060
GSMErrorComPMM1Code15 | INT | IOD_GSM_TCP | 40061
GSMErrorComPMM1Code1 | INT | IOD_GSM_TCP | 40062
GSMErrorComPMM1Code2 | INT | IOD_GSM_TCP | 40063
GSMErrorComPMM1Code3 | INT | IOD_GSM_TCP | 40064
GSMErrorComPMM1Code4 | INT | IOD_GSM_TCP | 40065
GSMErrorComPMM1Code5 | INT | IOD_GSM_TCP | 40066
GSMErrorComPMM1Code6 | INT | IOD_GSM_TCP | 40067
GSMErrorComPMM1Code7 | INT | IOD_GSM_TCP | 40068
GSMErrorComPMM1Code8 | INT | IOD_GSM_TCP | 40069
GSMErrorComPMM1Code9 | INT | IOD_GSM_TCP | 40070
GSMErrorComPMM1Error | DIGITAL | IOD_GSM_TCP | 00068
GSMErrorComPMM1Status | INT | IOD_GSM_TCP | 40071
GSMErrorComUPS1Code10 | INT | IOD_GSM_TCP | 40072
GSMErrorComUPS1Code11 | INT | IOD_GSM_TCP | 40073
GSMErrorComUPS1Code12 | INT | IOD_GSM_TCP | 40074
GSMErrorComUPS1Code13 | INT | IOD_GSM_TCP | 40075
GSMErrorComUPS1Code14 | INT | IOD_GSM_TCP | 40076
GSMErrorComUPS1Code15 | INT | IOD_GSM_TCP | 40077
GSMErrorComUPS1Code1 | INT | IOD_GSM_TCP | 40078
GSMErrorComUPS1Code2 | INT | IOD_GSM_TCP | 40079
GSMErrorComUPS1Code3 | INT | IOD_GSM_TCP | 40080
GSMErrorComUPS1Code4 | INT | IOD_GSM_TCP | 40081
GSMErrorComUPS1Code5 | INT | IOD_GSM_TCP | 40082
GSMErrorComUPS1Code6 | INT | IOD_GSM_TCP | 40083
GSMErrorComUPS1Code7 | INT | IOD_GSM_TCP | 40084
GSMErrorComUPS1Code8 | INT | IOD_GSM_TCP | 40085
GSMErrorComUPS1Code9 | INT | IOD_GSM_TCP | 40086
GSMErrorComUPS1Error | DIGITAL | IOD_GSM_TCP | 00069
GSMErrorComUPS1Status | INT | IOD_GSM_TCP | 40087
GSMErrorComUPS2Code10 | INT | IOD_GSM_TCP | 40088
GSMErrorComUPS2Code11 | INT | IOD_GSM_TCP | 40089
GSMErrorComUPS2Code12 | INT | IOD_GSM_TCP | 40090
GSMErrorComUPS2Code13 | INT | IOD_GSM_TCP | 40091
GSMErrorComUPS2Code14 | INT | IOD_GSM_TCP | 40092
GSMErrorComUPS2Code15 | INT | IOD_GSM_TCP | 40093
GSMErrorComUPS2Code1 | INT | IOD_GSM_TCP | 40094
GSMErrorComUPS2Code2 | INT | IOD_GSM_TCP | 40095
GSMErrorComUPS2Code3 | INT | IOD_GSM_TCP | 40096
GSMErrorComUPS2Code4 | INT | IOD_GSM_TCP | 40097
GSMErrorComUPS2Code5 | INT | IOD_GSM_TCP | 40098
GSMErrorComUPS2Code6 | INT | IOD_GSM_TCP | 40099
GSMErrorComUPS2Code7 | INT | IOD_GSM_TCP | 40100
GSMErrorComUPS2Code8 | INT | IOD_GSM_TCP | 40101
GSMErrorComUPS2Code9 | INT | IOD_GSM_TCP | 40102
GSMErrorComUPS2Error | DIGITAL | IOD_GSM_TCP | 00070
GSMErrorComUPS2Status | INT | IOD_GSM_TCP | 40103
GSMErrorComUPSMGE1Code10 | INT | IOD_GSM_TCP | 40104
GSMErrorComUPSMGE1Code11 | INT | IOD_GSM_TCP | 40105
GSMErrorComUPSMGE1Code12 | INT | IOD_GSM_TCP | 40106
GSMErrorComUPSMGE1Code13 | INT | IOD_GSM_TCP | 40107
GSMErrorComUPSMGE1Code14 | INT | IOD_GSM_TCP | 40108
GSMErrorComUPSMGE1Code15 | INT | IOD_GSM_TCP | 40109
GSMErrorComUPSMGE1Code1 | INT | IOD_GSM_TCP | 40110
GSMErrorComUPSMGE1Code2 | INT | IOD_GSM_TCP | 40111
GSMErrorComUPSMGE1Code3 | INT | IOD_GSM_TCP | 40112
GSMErrorComUPSMGE1Code4 | INT | IOD_GSM_TCP | 40113
GSMErrorComUPSMGE1Code5 | INT | IOD_GSM_TCP | 40114
GSMErrorComUPSMGE1Code6 | INT | IOD_GSM_TCP | 40115
GSMErrorComUPSMGE1Code7 | INT | IOD_GSM_TCP | 40116
GSMErrorComUPSMGE1Code8 | INT | IOD_GSM_TCP | 40117
GSMErrorComUPSMGE1Code9 | INT | IOD_GSM_TCP | 40118
GSMErrorComUPSMGE1Error | DIGITAL | IOD_GSM_TCP | 00071
GSMErrorComUPSMGE1Status | INT | IOD_GSM_TCP | 40119
GSMF1_1_zascita_ok | DIGITAL | IOD_GSM_TCP | 00072
GSMHIA1_vlaga_s | INT | IOD_GSM_TCP | 40120 | 0 | 1000 | 0 | 100 | % | ###.#
GSMHIA2_vlaga_s | INT | IOD_GSM_TCP | 40121 | 0 | 1000 | 0 | 100 | % | ###.#
GSMHIA3_vlaga_s | INT | IOD_GSM_TCP | 40122 | 0 | 1000 | 0 | 100 | % | ###.#
GSMHIA4_vlaga_s | INT | IOD_GSM_TCP | 40123 | 0 | 1000 | 0 | 100 | % | ###.#
GSMHIA5_vlaga_s | INT | IOD_GSM_TCP | 40124 | 0 | 1000 | 0 | 100 | % | ###.#
GSMHIA6_vlaga_s | INT | IOD_GSM_TCP | 40125 | 0 | 1000 | 0 | 100 | % | ###.#
GSMHIA7_vlaga_s | INT | IOD_GSM_TCP | 40126 | 0 | 1000 | 0 | 100 | % | ###.#
GSMK1_SkupnaNapaka | DIGITAL | IOD_GSM_TCP | 00073
GSMK1AlarmPozara | DIGITAL | IOD_GSM_TCP | 00074
GSMK1KlimaZdruzenAlarm | DIGITAL | IOD_GSM_TCP | 00075
GSMK1NiPretoka | DIGITAL | IOD_GSM_TCP | 00076
GSMK1OkvaraRototerma | DIGITAL | IOD_GSM_TCP | 00077
GSMK1OkvaraVlazNap | DIGITAL | IOD_GSM_TCP | 00078
GSMK1PreobMotCrpGr | DIGITAL | IOD_GSM_TCP | 00079
GSMK1PreobMotVent | DIGITAL | IOD_GSM_TCP | 00080
GSMK1ProtizamrzZascAkt | DIGITAL | IOD_GSM_TCP | 00081
GSMK1ZamasenostFiltra | DIGITAL | IOD_GSM_TCP | 00082
GSMK2_SkupnaNapaka | DIGITAL | IOD_GSM_TCP | 00083
GSMK2AlarmPozara | DIGITAL | IOD_GSM_TCP | 00084
GSMK2KlimaZdruzenAlarm | DIGITAL | IOD_GSM_TCP | 00085
GSMK2NiPretoka | DIGITAL | IOD_GSM_TCP | 00086
GSMK2OkvaraRototerma | DIGITAL | IOD_GSM_TCP | 00087
GSMK2OkvaraVlazNap | DIGITAL | IOD_GSM_TCP | 00088
GSMK2PreobMotCrpGr | DIGITAL | IOD_GSM_TCP | 00089
GSMK2PreobMotVent | DIGITAL | IOD_GSM_TCP | 00090
GSMK2ProtizamrzZascAkt | DIGITAL | IOD_GSM_TCP | 00091
GSMK2ZamasenostFiltra | DIGITAL | IOD_GSM_TCP | 00092
GSMK3_deluje | DIGITAL | IOD_GSM_TCP | 00093
GSMK3_SkupnaNapaka | DIGITAL | IOD_GSM_TCP | 00094
GSMKlima1_izkljucena | DIGITAL | IOD_GSM_TCP | 00095
GSMKLIMA1_kke_pogon | DIGITAL | IOD_GSM_TCP | 00096
GSMKLIMA1_krm_nap_ok | DIGITAL | IOD_GSM_TCP | 00097
GSMKlima2_izkljucena | DIGITAL | IOD_GSM_TCP | 00098
GSMKlima3_izkljucena | DIGITAL | IOD_GSM_TCP | 00099
GSMKlima1Alarm_pozar | DIGITAL | IOD_GSM_TCP | 00100
GSMKlima1Analog_izh_mesanje | INT | IOD_GSM_TCP | 40127
GSMKlima1Analog_izh_rekuperator | INT | IOD_GSM_TCP | 40128
GSMKlima1Analog_izh_VentGrelnika | INT | IOD_GSM_TCP | 40129
GSMKlima1Analog_izh_VentHlajenja | INT | IOD_GSM_TCP | 40130
GSMKlima1Dejanska_zel_temp | INT | IOD_GSM_TCP | 40131 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima1DelVentHit1 | DIGITAL | IOD_GSM_TCP | 00101 | 0 | 1000 | 0 | 1000 | % | ###.#
GSMKlima1DelVentHit2 | DIGITAL | IOD_GSM_TCP | 00102 | 0 | 1000 | 0 | 1000 | % | ###.#
GSMKlima1Hitrost_del_vent_disp | INT | IOD_GSM_TCP | 40132 | 0 | 1000 | 0 | 1000 | % | ###
GSMKlima1Max_vpih | INT | IOD_GSM_TCP | 40133 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima1Min_vpih | INT | IOD_GSM_TCP | 40134 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima1Ni_pretoka | DIGITAL | IOD_GSM_TCP | 00103
GSMKlima1Obrat_ure_Vent_h1 | INT | IOD_GSM_TCP | 40135
GSMKlima1Obrat_ure_Vent_h2 | INT | IOD_GSM_TCP | 40136
GSMKlima1OkvaraRototerm | DIGITAL | IOD_GSM_TCP | 00104
GSMKlima1OkvaraVlazNap | DIGITAL | IOD_GSM_TCP | 00105
GSMKlima1Pol_komp_konec | INT | IOD_GSM_TCP | 40137 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima1Pol_komp_sprem_zel_vr | INT | IOD_GSM_TCP | 40138 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima1Pol_komp_zacetek | INT | IOD_GSM_TCP | 40139 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima1PreklopHitDelVent | INT | IOD_GSM_TCP | 40140 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima1PreobMotCrpGrel | DIGITAL | IOD_GSM_TCP | 00106
GSMKlima1PreobMotVent | DIGITAL | IOD_GSM_TCP | 00107
GSMKlima1Protizamrz_zascita | INT | IOD_GSM_TCP | 40141 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima1ProtizamrzZascAktivna | DIGITAL | IOD_GSM_TCP | 00108
GSMKlima1Rezim_delovanja | INT | IOD_GSM_TCP | 40142
GSMKlima1Temperatura_dovoda | INT | IOD_GSM_TCP | 40143 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima1Temperatura_prostora | INT | IOD_GSM_TCP | 40144 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima1TempPredPloscnimRekup | INT | IOD_GSM_TCP | 40145 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima1TempZaPloscnimRekup | INT | IOD_GSM_TCP | 40146 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima1VklopRegKlimata | DIGITAL | IOD_GSM_TCP | 00109
GSMKlima1Vlaga_v_prostoru | INT | IOD_GSM_TCP | 40147 | 0 | 1000 | 0 | 100 | % | ##.#
GSMKlima1VlagaVstopZrakaProstor | INT | IOD_GSM_TCP | 40148 | 0 | 1000 | 0 | 100 | % | ##.#
GSMKlima1ZamasenostFiltra | DIGITAL | IOD_GSM_TCP | 00110
GSMKlima1ZdruzAlarmA | DIGITAL | IOD_GSM_TCP | 00111
GSMKlima1ZdruzAlarmB | DIGITAL | IOD_GSM_TCP | 00112
GSMKlima1Zel_temp_eko_gretja | INT | IOD_GSM_TCP | 40149 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima1Zel_temp_eko_hlajenja | INT | IOD_GSM_TCP | 40150 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima1Zel_temp_komf_gretja | INT | IOD_GSM_TCP | 40151 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima1Zel_temp_komf_hlajenja | INT | IOD_GSM_TCP | 40152 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima1Zim_komp_konec | INT | IOD_GSM_TCP | 40153 | -400 | 600 | -40 | 60 | °C | ##.#
GSMKlima1Zim_komp_sprem_zel_vr | INT | IOD_GSM_TCP | 40154 | -400 | 600 | -40 | 60 | °C | ##.#
GSMKlima1Zim_komp_zacetek | INT | IOD_GSM_TCP | 40155 | -400 | 600 | -40 | 60 | °C | ##.#
GSMKlima1ZimKompMinVpihKonec | INT | IOD_GSM_TCP | 40156 | -400 | 600 | -40 | 60 | °C | ##.#
GSMKlima1ZimKompMinVpihZac | INT | IOD_GSM_TCP | 40157 | -400 | 600 | -40 | 60 | °C | ##.#
GSMKlima1ZkompMinVpihSpremZelVr | INT | IOD_GSM_TCP | 40158 | -400 | 600 | -40 | 60 | °C | ##.#
GSMKlima1Zunanja_temp | INT | IOD_GSM_TCP | 40159 | -400 | 600 | -40 | 60 | °C | ##.#
GSMKlima2Alarm_pozar | DIGITAL | IOD_GSM_TCP | 00113
GSMKlima2Analog_izh_mesanje | INT | IOD_GSM_TCP | 40160
GSMKlima2Analog_izh_rekuperator | INT | IOD_GSM_TCP | 40161
GSMKlima2Analog_izh_VentGrelnika | INT | IOD_GSM_TCP | 40162
GSMKlima2Analog_izh_VentHlajenja | INT | IOD_GSM_TCP | 40163
GSMKlima2Dejanska_zel_temp | INT | IOD_GSM_TCP | 40164 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima2DelVentHit1 | DIGITAL | IOD_GSM_TCP | 00114 | 0 | 1000 | 0 | 1000 | % | ###.#
GSMKlima2DelVentHit2 | DIGITAL | IOD_GSM_TCP | 00115 | 0 | 1000 | 0 | 1000 | % | ###.#
GSMKlima2Hitrost_del_vent_disp | INT | IOD_GSM_TCP | 40165 | 0 | 1000 | 0 | 1000 | % | ###
GSMKlima2Max_vpih | INT | IOD_GSM_TCP | 40166 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima2Min_vpih | INT | IOD_GSM_TCP | 40167 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima2Ni_pretoka | DIGITAL | IOD_GSM_TCP | 00116
GSMKlima2Obrat_ure_Vent_h1 | INT | IOD_GSM_TCP | 40168
GSMKlima2Obrat_ure_Vent_h2 | INT | IOD_GSM_TCP | 40169
GSMKlima2OkvaraRototerm | DIGITAL | IOD_GSM_TCP | 00117
GSMKlima2OkvaraVlazNap | DIGITAL | IOD_GSM_TCP | 00118
GSMKlima2Pol_komp_konec | INT | IOD_GSM_TCP | 40170 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima2Pol_komp_sprem_zel_vr | INT | IOD_GSM_TCP | 40171 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima2Pol_komp_zacetek | INT | IOD_GSM_TCP | 40172 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima2PreklopHitDelVent | INT | IOD_GSM_TCP | 40173 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima2PreobMotCrpGrel | DIGITAL | IOD_GSM_TCP | 00119
GSMKlima2PreobMotVent | DIGITAL | IOD_GSM_TCP | 00120
GSMKlima2Protizamrz_zascita | INT | IOD_GSM_TCP | 40174 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima2ProtizamrzZascAktivna | DIGITAL | IOD_GSM_TCP | 00121
GSMKlima2Rezim_delovanja | INT | IOD_GSM_TCP | 40175
GSMKlima2Temperatura_dovoda | INT | IOD_GSM_TCP | 40176 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima2Temperatura_prostora | INT | IOD_GSM_TCP | 40177 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima2TempPredPloscnimRekup | INT | IOD_GSM_TCP | 40178 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima2TempZaPloscnimRekup | INT | IOD_GSM_TCP | 40179 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima2VklopRegKlimata | DIGITAL | IOD_GSM_TCP | 00122
GSMKlima2Vlaga_v_prostoru | INT | IOD_GSM_TCP | 40180 | 0 | 1000 | 0 | 100 | % | ##.#
GSMKlima2VlagaVstopZrakaProstor | INT | IOD_GSM_TCP | 40181 | 0 | 1000 | 0 | 100 | % | ##.#
GSMKlima2ZamasenostFiltra | DIGITAL | IOD_GSM_TCP | 00123
GSMKlima2ZdruzAlarmA | DIGITAL | IOD_GSM_TCP | 00124
GSMKlima2ZdruzAlarmB | DIGITAL | IOD_GSM_TCP | 00125
GSMKlima2Zel_temp_eko_gretja | INT | IOD_GSM_TCP | 40182 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima2Zel_temp_eko_hlajenja | INT | IOD_GSM_TCP | 40183 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima2Zel_temp_komf_gretja | INT | IOD_GSM_TCP | 40184 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima2Zel_temp_komf_hlajenja | INT | IOD_GSM_TCP | 40185 | 0 | 600 | 0 | 60 | °C | ##.#
GSMKlima2Zim_komp_konec | INT | IOD_GSM_TCP | 40186 | -400 | 600 | -40 | 60 | °C | ##.#
GSMKlima2Zim_komp_sprem_zel_vr | INT | IOD_GSM_TCP | 40187 | -400 | 600 | -40 | 60 | °C | ##.#
GSMKlima2Zim_komp_zacetek | INT | IOD_GSM_TCP | 40188 | -400 | 600 | -40 | 60 | °C | ##.#
GSMKlima2ZimKompMinVpihKonec | INT | IOD_GSM_TCP | 40189 | -400 | 600 | -40 | 60 | °C | ##.#
GSMKlima2ZimKompMinVpihZac | INT | IOD_GSM_TCP | 40190 | -400 | 600 | -40 | 60 | °C | ##.#
GSMKlima2ZkompMinVpihSpremZelVr | INT | IOD_GSM_TCP | 40191 | -400 | 600 | -40 | 60 | °C | ##.#
GSMKlima2Zunanja_temp | INT | IOD_GSM_TCP | 40192 | -400 | 600 | -40 | 60 | °C | ##.#
GSMKLIMA_m1_delovanje | DIGITAL | IOD_GSM_TCP | 00126
GSMKLIMA_m1_napaka | DIGITAL | IOD_GSM_TCP | 00127
GSMKLIMA_m2_delovanje | DIGITAL | IOD_GSM_TCP | 00128
GSMKLIMA_m2_napaka | DIGITAL | IOD_GSM_TCP | 00129
GSMKlimaIzklopObrUre | INT | IOD_GSM_TCP | 40193
GSMKLIMAT1_delovanje | DIGITAL | IOD_GSM_TCP | 00130
GSMKLIMAT1_napaka | DIGITAL | IOD_GSM_TCP | 00131
GSMKLIMAT1_vklop_delovanja | DIGITAL | IOD_GSM_TCP | 00132
GSMKLIMAT2_delovanje | DIGITAL | IOD_GSM_TCP | 00133
GSMKLIMAT2_napaka | DIGITAL | IOD_GSM_TCP | 00134
GSMKLIMAT2_vklop_delovanja | DIGITAL | IOD_GSM_TCP | 00135
GSMKlimeAVTO | DIGITAL | IOD_GSM_TCP | 00136
GSMkom_nast_cas_izpada | UINT | IOD_GSM_TCP | 46001
GSMN_F1_1_zascita_ok | DIGITAL | IOD_GSM_TCP | 00137
GSMN_KLIMA1_krm_nap_ok | DIGITAL | IOD_GSM_TCP | 00138
GSMN_KLIMAT1_napaka | DIGITAL | IOD_GSM_TCP | 00139
GSMN_KLIMAT2_napaka | DIGITAL | IOD_GSM_TCP | 00140
GSMN_Q12_izpad | DIGITAL | IOD_GSM_TCP | 00141
GSMN_UPS_A_V23_delovanje | DIGITAL | IOD_GSM_TCP | 00142
GSMN_UPS_A_V23_napaka | DIGITAL | IOD_GSM_TCP | 00143
GSMN_UPS_V23_delovanje | DIGITAL | IOD_GSM_TCP | 00144
GSMN_UPS_V23_napaka | DIGITAL | IOD_GSM_TCP | 00145
GSMN_UPS_V25_delovanje | DIGITAL | IOD_GSM_TCP | 00146
GSMN_UPS_V25_napaka | DIGITAL | IOD_GSM_TCP | 00147
GSMN_VLAZILEC1_napaka | DIGITAL | IOD_GSM_TCP | 00148
GSMN_VLAZILEC2_napaka | DIGITAL | IOD_GSM_TCP | 00149
GSMnapaka_kom_panel | DIGITAL | IOD_GSM_TCP | 00150
GSMnapaka_kom_scada | DIGITAL | IOD_GSM_TCP | 00151
GSMnapaka_kom_scada2 | DIGITAL | IOD_GSM_TCP | 00152
GSMNapakaSenzorSkupno | DIGITAL | IOD_GSM_TCP | 00153
GSMNapakaSenzorVlagaHIA1 | DIGITAL | IOD_GSM_TCP | 00154
GSMNapakaSenzorVlagaHIA2 | DIGITAL | IOD_GSM_TCP | 00155
GSMNapakaSenzorVlagaHIA3 | DIGITAL | IOD_GSM_TCP | 00156
GSMNapakaSenzorVlagaHIA4 | DIGITAL | IOD_GSM_TCP | 00157
GSMNapakaSenzorVlagaHIA5 | DIGITAL | IOD_GSM_TCP | 00158
GSMNapakaSenzorVlagaHIA6 | DIGITAL | IOD_GSM_TCP | 00159
GSMNapakaSenzorVlagaHIA7 | DIGITAL | IOD_GSM_TCP | 00160
GSMNapakaTSTempTIA1 | DIGITAL | IOD_GSM_TCP | 00161
GSMNapakaTSTempTIA2 | DIGITAL | IOD_GSM_TCP | 00162
GSMNapakaTSTempTIA3 | DIGITAL | IOD_GSM_TCP | 00163
GSMNapakaTSTempTIA4 | DIGITAL | IOD_GSM_TCP | 00164
GSMNapakaTSTempTIA5 | DIGITAL | IOD_GSM_TCP | 00165
GSMNapakaTSTempTIA6 | DIGITAL | IOD_GSM_TCP | 00166
GSMNapakaTSTempTIA7 | DIGITAL | IOD_GSM_TCP | 00167
GSMOpozoriloPMM2x17med60in8010 | DIGITAL | IOD_GSM_TCP | 00168
GSMOpozoriloPMM2x17med60in8011 | DIGITAL | IOD_GSM_TCP | 00169
GSMOpozoriloPMM2x17med60in8012 | DIGITAL | IOD_GSM_TCP | 00170
GSMOpozoriloPMM2x17med60in8013 | DIGITAL | IOD_GSM_TCP | 00171
GSMOpozoriloPMM2x17med60in8014 | DIGITAL | IOD_GSM_TCP | 00172
GSMOpozoriloPMM2x17med60in8015 | DIGITAL | IOD_GSM_TCP | 00173
GSMOpozoriloPMM2x17med60in8016 | DIGITAL | IOD_GSM_TCP | 00174
GSMOpozoriloPMM2x17med60in8017 | DIGITAL | IOD_GSM_TCP | 00175
GSMOpozoriloPMM2x17med60in8018 | DIGITAL | IOD_GSM_TCP | 00176
GSMOpozoriloPMM2x17med60in8019 | DIGITAL | IOD_GSM_TCP | 00177
GSMOpozoriloPMM2x17med60in801 | DIGITAL | IOD_GSM_TCP | 00178
GSMOpozoriloPMM2x17med60in8020 | DIGITAL | IOD_GSM_TCP | 00179
GSMOpozoriloPMM2x17med60in8021 | DIGITAL | IOD_GSM_TCP | 00180
GSMOpozoriloPMM2x17med60in8022 | DIGITAL | IOD_GSM_TCP | 00181
GSMOpozoriloPMM2x17med60in8023 | DIGITAL | IOD_GSM_TCP | 00182
GSMOpozoriloPMM2x17med60in8024 | DIGITAL | IOD_GSM_TCP | 00183
GSMOpozoriloPMM2x17med60in8025 | DIGITAL | IOD_GSM_TCP | 00184
GSMOpozoriloPMM2x17med60in8026 | DIGITAL | IOD_GSM_TCP | 00185
GSMOpozoriloPMM2x17med60in8027 | DIGITAL | IOD_GSM_TCP | 00186
GSMOpozoriloPMM2x17med60in8028 | DIGITAL | IOD_GSM_TCP | 00187
GSMOpozoriloPMM2x17med60in8029 | DIGITAL | IOD_GSM_TCP | 00188
GSMOpozoriloPMM2x17med60in802 | DIGITAL | IOD_GSM_TCP | 00189
GSMOpozoriloPMM2x17med60in8030 | DIGITAL | IOD_GSM_TCP | 00190
GSMOpozoriloPMM2x17med60in8031 | DIGITAL | IOD_GSM_TCP | 00191
GSMOpozoriloPMM2x17med60in8032 | DIGITAL | IOD_GSM_TCP | 00192
GSMOpozoriloPMM2x17med60in8033 | DIGITAL | IOD_GSM_TCP | 00193
GSMOpozoriloPMM2x17med60in8034 | DIGITAL | IOD_GSM_TCP | 00194
GSMOpozoriloPMM2x17med60in8035 | DIGITAL | IOD_GSM_TCP | 00195
GSMOpozoriloPMM2x17med60in8036 | DIGITAL | IOD_GSM_TCP | 00196
GSMOpozoriloPMM2x17med60in8037 | DIGITAL | IOD_GSM_TCP | 00197
GSMOpozoriloPMM2x17med60in8038 | DIGITAL | IOD_GSM_TCP | 00198
GSMOpozoriloPMM2x17med60in8039 | DIGITAL | IOD_GSM_TCP | 00199
GSMOpozoriloPMM2x17med60in803 | DIGITAL | IOD_GSM_TCP | 00200
GSMOpozoriloPMM2x17med60in8040 | DIGITAL | IOD_GSM_TCP | 00201
GSMOpozoriloPMM2x17med60in8041 | DIGITAL | IOD_GSM_TCP | 00202
GSMOpozoriloPMM2x17med60in8042 | DIGITAL | IOD_GSM_TCP | 00203
GSMOpozoriloPMM2x17med60in804 | DIGITAL | IOD_GSM_TCP | 00204
GSMOpozoriloPMM2x17med60in805 | DIGITAL | IOD_GSM_TCP | 00205
GSMOpozoriloPMM2x17med60in806 | DIGITAL | IOD_GSM_TCP | 00206
GSMOpozoriloPMM2x17med60in807 | DIGITAL | IOD_GSM_TCP | 00207
GSMOpozoriloPMM2x17med60in808 | DIGITAL | IOD_GSM_TCP | 00208
GSMOpozoriloPMM2x17med60in809 | DIGITAL | IOD_GSM_TCP | 00209
GSMPMM1OverCurrentBetw1 | DIGITAL | IOD_GSM_TCP | 00210
GSMPMM1OverCurrentBetw2 | DIGITAL | IOD_GSM_TCP | 00211
GSMPMM1OverCurrentBetw3 | DIGITAL | IOD_GSM_TCP | 00212
GSMPMM1OverCurrentOver1 | DIGITAL | IOD_GSM_TCP | 00213
GSMPMM1OverCurrentOver2 | DIGITAL | IOD_GSM_TCP | 00214
GSMPMM1OverCurrentOver3 | DIGITAL | IOD_GSM_TCP | 00215
GSMPMM1ActiveEnergyConsumed_kWh | REAL | IOD_GSM_TCP | 44075 | 0 | 1000 | 0 | 1000 | kVARh | ####
GSMPMM1ActivePowerPhaseA_kW | REAL | IOD_GSM_TCP | 44077 | 0 | 100 | 0 | 100 | kW | ####.#
GSMPMM1ActivePowerPhaseB_kW | REAL | IOD_GSM_TCP | 44079 | 0 | 100 | 0 | 100 | kW | ####.#
GSMPMM1ActivePowerPhaseC_kW | REAL | IOD_GSM_TCP | 44081 | 0 | 100 | 0 | 100 | kW | ####.#
GSMPMM1AlarmPhase1C01_16_60to80 | UINT | IOD_GSM_TCP | 46002
GSMPMM1AlarmPhase1C01_16_over80 | UINT | IOD_GSM_TCP | 46003
GSMPMM1AlarmPhase1C17_32_60to80 | UINT | IOD_GSM_TCP | 46004
GSMPMM1AlarmPhase1C17_32_over80 | UINT | IOD_GSM_TCP | 46005
GSMPMM1AlarmPhase1C33_42_60to80 | UINT | IOD_GSM_TCP | 46006
GSMPMM1AlarmPhase1C33_42_over80 | UINT | IOD_GSM_TCP | 46007
GSMPMM1AlarmPhase1GlobalAlarmReg | INT | IOD_GSM_TCP | 40194
GSMPMM1AlarmPhase2C01_16_60to80 | UINT | IOD_GSM_TCP | 46008
GSMPMM1AlarmPhase2C01_16_over80 | UINT | IOD_GSM_TCP | 46009
GSMPMM1AlarmPhase2C17_32_60to80 | UINT | IOD_GSM_TCP | 46010
GSMPMM1AlarmPhase2C17_32_over80 | UINT | IOD_GSM_TCP | 46011
GSMPMM1AlarmPhase2C33_42_60to80 | UINT | IOD_GSM_TCP | 46012
GSMPMM1AlarmPhase2C33_42_over80 | UINT | IOD_GSM_TCP | 46013
GSMPMM1AlarmPhase2GlobalAlarmReg | INT | IOD_GSM_TCP | 40195
GSMPMM1AlarmPhase3C01_16_60to80 | UINT | IOD_GSM_TCP | 46014
GSMPMM1AlarmPhase3C01_16_over80 | UINT | IOD_GSM_TCP | 46015
GSMPMM1AlarmPhase3C17_32_60to80 | UINT | IOD_GSM_TCP | 46016
GSMPMM1AlarmPhase3C17_32_over80 | UINT | IOD_GSM_TCP | 46017
GSMPMM1AlarmPhase3C33_42_60to80 | UINT | IOD_GSM_TCP | 46018
GSMPMM1AlarmPhase3C33_42_over80 | UINT | IOD_GSM_TCP | 46019
GSMPMM1AlarmPhase3GlobalAlarmReg | INT | IOD_GSM_TCP | 40196
GSMPMM1AparentPowerPhaseA | REAL | IOD_GSM_TCP | 44083 | 0 | 100 | 0 | 100 | kVAR | ####.#
GSMPMM1AparentPowerPhaseB | REAL | IOD_GSM_TCP | 44085 | 0 | 100 | 0 | 100 | kVAR | ####.#
GSMPMM1AparentPowerPhaseC | REAL | IOD_GSM_TCP | 44087 | 0 | 100 | 0 | 100 | kVAR | ####.#
GSMPMM1AverageCurrent_A | REAL | IOD_GSM_TCP | 44089 | 0 | 16 | 0 | 16 | A | ####.#
GSMPMM1AveragePhaseToNeutral_V | REAL | IOD_GSM_TCP | 44091 | 0 | 270 | 0 | 270 | V | ####.#
GSMPMM1AveragePhaseToPhase_V | REAL | IOD_GSM_TCP | 44093 | 0 | 450 | 0 | 450 | V | ####.#
GSMPMM1CurrentInPhaseA_A | REAL | IOD_GSM_TCP | 44095 | 0 | 500 | 0 | 500 | A | ####.#
GSMPMM1CurrentInPhaseB_A | REAL | IOD_GSM_TCP | 44097 | 0 | 500 | 0 | 500 | A | ####.#
GSMPMM1CurrentInPhaseC_A | REAL | IOD_GSM_TCP | 44099 | 0 | 500 | 0 | 500 | A | ####.#
GSMPMM1Frequency_Hz | REAL | IOD_GSM_TCP | 44101 | 0 | 70 | 0 | 70 | Hz | ####.#
GSMPMM1Phase1Current10 | REAL | IOD_GSM_TCP | 44103 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current11 | REAL | IOD_GSM_TCP | 44105 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current12 | REAL | IOD_GSM_TCP | 44107 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current13 | REAL | IOD_GSM_TCP | 44109 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current14 | REAL | IOD_GSM_TCP | 44111 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current15 | REAL | IOD_GSM_TCP | 44113 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current16 | REAL | IOD_GSM_TCP | 44115 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current17 | REAL | IOD_GSM_TCP | 44117 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current18 | REAL | IOD_GSM_TCP | 44119 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current19 | REAL | IOD_GSM_TCP | 44121 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current1 | REAL | IOD_GSM_TCP | 44123 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current20 | REAL | IOD_GSM_TCP | 44125 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current21 | REAL | IOD_GSM_TCP | 44127 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current22 | REAL | IOD_GSM_TCP | 44129 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current23 | REAL | IOD_GSM_TCP | 44131 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current24 | REAL | IOD_GSM_TCP | 44133 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current25 | REAL | IOD_GSM_TCP | 44135 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current26 | REAL | IOD_GSM_TCP | 44137 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current27 | REAL | IOD_GSM_TCP | 44139 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current28 | REAL | IOD_GSM_TCP | 44141 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current29 | REAL | IOD_GSM_TCP | 44143 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current2 | REAL | IOD_GSM_TCP | 44145 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current30 | REAL | IOD_GSM_TCP | 44147 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current31 | REAL | IOD_GSM_TCP | 44149 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current32 | REAL | IOD_GSM_TCP | 44151 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current33 | REAL | IOD_GSM_TCP | 44153 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current34 | REAL | IOD_GSM_TCP | 44155 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current35 | REAL | IOD_GSM_TCP | 44157 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current36 | REAL | IOD_GSM_TCP | 44159 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current37 | REAL | IOD_GSM_TCP | 44161 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current38 | REAL | IOD_GSM_TCP | 44163 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current39 | REAL | IOD_GSM_TCP | 44165 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current3 | REAL | IOD_GSM_TCP | 44167 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current40 | REAL | IOD_GSM_TCP | 44169 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current41 | REAL | IOD_GSM_TCP | 44171 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current42 | REAL | IOD_GSM_TCP | 44173 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current4 | REAL | IOD_GSM_TCP | 44175 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current5 | REAL | IOD_GSM_TCP | 44177 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current6 | REAL | IOD_GSM_TCP | 44179 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current7 | REAL | IOD_GSM_TCP | 44181 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current8 | REAL | IOD_GSM_TCP | 44183 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase1Current9 | REAL | IOD_GSM_TCP | 44185 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMM1Phase2Current10 | REAL | IOD_GSM_TCP | 44187
GSMPMM1Phase2Current11 | REAL | IOD_GSM_TCP | 44189
GSMPMM1Phase2Current12 | REAL | IOD_GSM_TCP | 44191
GSMPMM1Phase2Current13 | REAL | IOD_GSM_TCP | 44193
GSMPMM1Phase2Current14 | REAL | IOD_GSM_TCP | 44195
GSMPMM1Phase2Current15 | REAL | IOD_GSM_TCP | 44197
GSMPMM1Phase2Current16 | REAL | IOD_GSM_TCP | 44199
GSMPMM1Phase2Current17 | REAL | IOD_GSM_TCP | 44201
GSMPMM1Phase2Current18 | REAL | IOD_GSM_TCP | 44203
GSMPMM1Phase2Current19 | REAL | IOD_GSM_TCP | 44205
GSMPMM1Phase2Current1 | REAL | IOD_GSM_TCP | 44207
GSMPMM1Phase2Current20 | REAL | IOD_GSM_TCP | 44209
GSMPMM1Phase2Current21 | REAL | IOD_GSM_TCP | 44211
GSMPMM1Phase2Current22 | REAL | IOD_GSM_TCP | 44213
GSMPMM1Phase2Current23 | REAL | IOD_GSM_TCP | 44215
GSMPMM1Phase2Current24 | REAL | IOD_GSM_TCP | 44217
GSMPMM1Phase2Current25 | REAL | IOD_GSM_TCP | 44219
GSMPMM1Phase2Current26 | REAL | IOD_GSM_TCP | 44221
GSMPMM1Phase2Current27 | REAL | IOD_GSM_TCP | 44223
GSMPMM1Phase2Current28 | REAL | IOD_GSM_TCP | 44225
GSMPMM1Phase2Current29 | REAL | IOD_GSM_TCP | 44227
GSMPMM1Phase2Current2 | REAL | IOD_GSM_TCP | 44229
GSMPMM1Phase2Current30 | REAL | IOD_GSM_TCP | 44231
GSMPMM1Phase2Current31 | REAL | IOD_GSM_TCP | 44233
GSMPMM1Phase2Current32 | REAL | IOD_GSM_TCP | 44235
GSMPMM1Phase2Current33 | REAL | IOD_GSM_TCP | 44237
GSMPMM1Phase2Current34 | REAL | IOD_GSM_TCP | 44239
GSMPMM1Phase2Current35 | REAL | IOD_GSM_TCP | 44241
GSMPMM1Phase2Current36 | REAL | IOD_GSM_TCP | 44243
GSMPMM1Phase2Current37 | REAL | IOD_GSM_TCP | 44245
GSMPMM1Phase2Current38 | REAL | IOD_GSM_TCP | 44247
GSMPMM1Phase2Current39 | REAL | IOD_GSM_TCP | 44249
GSMPMM1Phase2Current3 | REAL | IOD_GSM_TCP | 44251
GSMPMM1Phase2Current40 | REAL | IOD_GSM_TCP | 44253
GSMPMM1Phase2Current41 | REAL | IOD_GSM_TCP | 44255
GSMPMM1Phase2Current42 | REAL | IOD_GSM_TCP | 44257
GSMPMM1Phase2Current4 | REAL | IOD_GSM_TCP | 44259
GSMPMM1Phase2Current5 | REAL | IOD_GSM_TCP | 44261
GSMPMM1Phase2Current6 | REAL | IOD_GSM_TCP | 44263
GSMPMM1Phase2Current7 | REAL | IOD_GSM_TCP | 44265
GSMPMM1Phase2Current8 | REAL | IOD_GSM_TCP | 44267
GSMPMM1Phase2Current9 | REAL | IOD_GSM_TCP | 44269
GSMPMM1Phase3Current10 | REAL | IOD_GSM_TCP | 44271
GSMPMM1Phase3Current11 | REAL | IOD_GSM_TCP | 44273
GSMPMM1Phase3Current12 | REAL | IOD_GSM_TCP | 44275
GSMPMM1Phase3Current13 | REAL | IOD_GSM_TCP | 44277
GSMPMM1Phase3Current14 | REAL | IOD_GSM_TCP | 44279
GSMPMM1Phase3Current15 | REAL | IOD_GSM_TCP | 44281
GSMPMM1Phase3Current16 | REAL | IOD_GSM_TCP | 44283
GSMPMM1Phase3Current17 | REAL | IOD_GSM_TCP | 44285
GSMPMM1Phase3Current18 | REAL | IOD_GSM_TCP | 44287
GSMPMM1Phase3Current19 | REAL | IOD_GSM_TCP | 44289
GSMPMM1Phase3Current1 | REAL | IOD_GSM_TCP | 44291
GSMPMM1Phase3Current20 | REAL | IOD_GSM_TCP | 44293
GSMPMM1Phase3Current21 | REAL | IOD_GSM_TCP | 44295
GSMPMM1Phase3Current22 | REAL | IOD_GSM_TCP | 44297
GSMPMM1Phase3Current23 | REAL | IOD_GSM_TCP | 44299
GSMPMM1Phase3Current24 | REAL | IOD_GSM_TCP | 44301
GSMPMM1Phase3Current25 | REAL | IOD_GSM_TCP | 44303
GSMPMM1Phase3Current26 | REAL | IOD_GSM_TCP | 44305
GSMPMM1Phase3Current27 | REAL | IOD_GSM_TCP | 44307
GSMPMM1Phase3Current28 | REAL | IOD_GSM_TCP | 44309
GSMPMM1Phase3Current29 | REAL | IOD_GSM_TCP | 44311
GSMPMM1Phase3Current2 | REAL | IOD_GSM_TCP | 44313
GSMPMM1Phase3Current30 | REAL | IOD_GSM_TCP | 44315
GSMPMM1Phase3Current31 | REAL | IOD_GSM_TCP | 44317
GSMPMM1Phase3Current32 | REAL | IOD_GSM_TCP | 44319
GSMPMM1Phase3Current33 | REAL | IOD_GSM_TCP | 44321
GSMPMM1Phase3Current34 | REAL | IOD_GSM_TCP | 44323
GSMPMM1Phase3Current35 | REAL | IOD_GSM_TCP | 44325
GSMPMM1Phase3Current36 | REAL | IOD_GSM_TCP | 44327
GSMPMM1Phase3Current37 | REAL | IOD_GSM_TCP | 44329
GSMPMM1Phase3Current38 | REAL | IOD_GSM_TCP | 44331
GSMPMM1Phase3Current39 | REAL | IOD_GSM_TCP | 44333
GSMPMM1Phase3Current3 | REAL | IOD_GSM_TCP | 44335
GSMPMM1Phase3Current40 | REAL | IOD_GSM_TCP | 44337
GSMPMM1Phase3Current41 | REAL | IOD_GSM_TCP | 44339
GSMPMM1Phase3Current42 | REAL | IOD_GSM_TCP | 44341
GSMPMM1Phase3Current4 | REAL | IOD_GSM_TCP | 44343
GSMPMM1Phase3Current5 | REAL | IOD_GSM_TCP | 44345
GSMPMM1Phase3Current6 | REAL | IOD_GSM_TCP | 44347
GSMPMM1Phase3Current7 | REAL | IOD_GSM_TCP | 44349
GSMPMM1Phase3Current8 | REAL | IOD_GSM_TCP | 44351
GSMPMM1Phase3Current9 | REAL | IOD_GSM_TCP | 44353
GSMPMM1PowerFactorSys | REAL | IOD_GSM_TCP | 44355 | 0 | 1 | 0 | 1 |  | ####.#
GSMPMM1ReactiveEnergyConsumed_kVARh | REAL | IOD_GSM_TCP | 44357 | 0 | 1000 | 0 | 1000 | kVARh | ####
GSMPMM1ReactivePowerPhaseA | REAL | IOD_GSM_TCP | 44359 | 0 | 100 | 0 | 100 | kVAR | ####.#
GSMPMM1ReactivePowerPhaseB | REAL | IOD_GSM_TCP | 44361 | 0 | 100 | 0 | 100 | kVAR | ####.#
GSMPMM1ReactivePowerPhaseC | REAL | IOD_GSM_TCP | 44363 | 0 | 100 | 0 | 100 | kVAR | ####.#
GSMPMM1TotalActivePower_kW | REAL | IOD_GSM_TCP | 44365 | 0 | 300 | 0 | 300 | kW | ####.#
GSMPMM1TotalAparentPower_kVA | REAL | IOD_GSM_TCP | 44367 | 0 | 300 | 0 | 300 | kVA | ####.#
GSMPMM1TotalPowerFactor | REAL | IOD_GSM_TCP | 44369 | 0 | 1 | 0 | 1 |  | ####.#
GSMPMM1TotalReactivePower_kVAR | REAL | IOD_GSM_TCP | 44371 | 0 | 300 | 0 | 300 | kVAR | ####.#
GSMPMM1VirA_fsys | REAL | IOD_GSM_TCP | 44373 | 0 | 70 | 0 | 70 | Hz | ####.#
GSMPMM1VirA_Isys | REAL | IOD_GSM_TCP | 44375 | 0 | 1000 | 0 | 1000 | A | ####.#
GSMPMM1VirA_PFsys | REAL | IOD_GSM_TCP | 44377 | 0 | 1 | 0 | 1 |  | ####.#
GSMPMM1VirA_Psys | REAL | IOD_GSM_TCP | 44379 | 0 | 300 | 0 | 300 | kW | ####.#
GSMPMM1VirA_Qsys | REAL | IOD_GSM_TCP | 44381 | 0 | 300 | 0 | 300 | kVAR | ####.#
GSMPMM1VirA_Ssys | REAL | IOD_GSM_TCP | 44383 | 0 | 300 | 0 | 300 | kVA | ####.#
GSMPMM1VirA_Usys | REAL | IOD_GSM_TCP | 44385 | 0 | 450 | 0 | 450 | V | ####.#
GSMPMM1VirB_fsys | REAL | IOD_GSM_TCP | 44387 | 0 | 70 | 0 | 70 | Hz | ####.#
GSMPMM1VirB_Isys | REAL | IOD_GSM_TCP | 44389 | 0 | 1000 | 0 | 1000 | A | ####.#
GSMPMM1VirB_PFsys | REAL | IOD_GSM_TCP | 44391 | 0 | 1 | 0 | 1 |  | ####.#
GSMPMM1VirB_Psys | REAL | IOD_GSM_TCP | 44393 | 0 | 300 | 0 | 300 | kW | ####.#
GSMPMM1VirB_Qsys | REAL | IOD_GSM_TCP | 44395 | 0 | 300 | 0 | 300 | kVAR | ####.#
GSMPMM1VirB_Ssys | REAL | IOD_GSM_TCP | 44397 | 0 | 300 | 0 | 300 | kVA | ####.#
GSMPMM1VirB_Usys | REAL | IOD_GSM_TCP | 44399 | 0 | 450 | 0 | 450 | V | ####.#
GSMPMM1VirBActiveEnergyConsumed_kWh | REAL | IOD_GSM_TCP | 44401 | 0 | 1000 | 0 | 1000 | kVARh | ####.#
GSMPMM1VirBActivePowerPhaseA_kW | REAL | IOD_GSM_TCP | 44403 | 0 | 100 | 0 | 100 | kW | ####.#
GSMPMM1VirBActivePowerPhaseB_kW | REAL | IOD_GSM_TCP | 44405 | 0 | 100 | 0 | 100 | kW | ####.#
GSMPMM1VirBActivePowerPhaseC_kW | REAL | IOD_GSM_TCP | 44407 | 0 | 100 | 0 | 100 | kW | ####.#
GSMPMM1VirBAparentPowerPhaseA | REAL | IOD_GSM_TCP | 44409 | 0 | 100 | 0 | 100 | kVAR | ####.#
GSMPMM1VirBAparentPowerPhaseB | REAL | IOD_GSM_TCP | 44411 | 0 | 100 | 0 | 100 | kVAR | ####.#
GSMPMM1VirBAparentPowerPhaseC | REAL | IOD_GSM_TCP | 44413 | 0 | 100 | 0 | 100 | kVAR | ####.#
GSMPMM1VirBAverageCurrent_A | REAL | IOD_GSM_TCP | 44415 | 0 | 100 | 0 | 100 | A | ####.#
GSMPMM1VirBAveragePhaseToNeutral_V | REAL | IOD_GSM_TCP | 44417 | 0 | 270 | 0 | 270 | V | ####.#
GSMPMM1VirBAveragePhaseToPhase_V | REAL | IOD_GSM_TCP | 44419 | 0 | 270 | 0 | 270 | V | ####.#
GSMPMM1VirBCurrentInPhaseA_A | REAL | IOD_GSM_TCP | 44421 | 0 | 100 | 0 | 100 | A | ####.#
GSMPMM1VirBCurrentInPhaseB_A | REAL | IOD_GSM_TCP | 44423 | 0 | 100 | 0 | 100 | A | ####.#
GSMPMM1VirBCurrentInPhaseC_A | REAL | IOD_GSM_TCP | 44425 | 0 | 100 | 0 | 100 | A | ####.#
GSMPMM1VirBFrequency_Hz | REAL | IOD_GSM_TCP | 44427 | 0 | 70 | 0 | 70 | Hz | ####.#
GSMPMM1VirBPowerFactorSys | REAL | IOD_GSM_TCP | 44429 | 0 | 1 | 0 | 1 |  | ####.#
GSMPMM1VirBReactiveEnergyConsumed_kVARh | REAL | IOD_GSM_TCP | 44431 | 0 | 1000 | 0 | 1000 | kVARh | ####.#
GSMPMM1VirBReactivePowerPhaseA | REAL | IOD_GSM_TCP | 44433 | 0 | 100 | 0 | 100 | kVAR | ####.#
GSMPMM1VirBReactivePowerPhaseB | REAL | IOD_GSM_TCP | 44435 | 0 | 100 | 0 | 100 | kVAR | ####.#
GSMPMM1VirBReactivePowerPhaseC | REAL | IOD_GSM_TCP | 44437 | 0 | 100 | 0 | 100 | kVAR | ####.#
GSMPMM1VirBTotalActivePower_kW | REAL | IOD_GSM_TCP | 44439 | 0 | 300 | 0 | 300 | kW | ####.#
GSMPMM1VirBTotalAparentPower_kVA | REAL | IOD_GSM_TCP | 44441 | 0 | 300 | 0 | 300 | kVA | ####.#
GSMPMM1VirBTotalPowerFactor | REAL | IOD_GSM_TCP | 44443 | 0 | 1 | 0 | 1 |  | ####.#
GSMPMM1VirBTotalReactivePower_kVAR | REAL | IOD_GSM_TCP | 44445 | 0 | 100 | 0 | 100 | kVAR | ####.#
GSMPMM1VirBVoltageBetweenPhaseAB_V | REAL | IOD_GSM_TCP | 44447 | 0 | 450 | 0 | 450 | V | ####.#
GSMPMM1VirBVoltageBetweenPhaseAN_V | REAL | IOD_GSM_TCP | 44449 | 0 | 270 | 0 | 270 | V | ####.#
GSMPMM1VirBVoltageBetweenPhaseBC_V | REAL | IOD_GSM_TCP | 44451 | 0 | 450 | 0 | 450 | V | ####.#
GSMPMM1VirBVoltageBetweenPhaseBN_V | REAL | IOD_GSM_TCP | 44453 | 0 | 270 | 0 | 270 | V | ####.#
GSMPMM1VirBVoltageBetweenPhaseCA_V | REAL | IOD_GSM_TCP | 44455 | 0 | 450 | 0 | 450 | V | ####.#
GSMPMM1VirBVoltageBetweenPhaseCN_V | REAL | IOD_GSM_TCP | 44457 | 0 | 270 | 0 | 270 | V | ####.#
GSMPMM1VoltageBetweenPhaseAB_V | REAL | IOD_GSM_TCP | 44459 | 0 | 450 | 0 | 450 | V | ####.#
GSMPMM1VoltageBetweenPhaseAN_V | REAL | IOD_GSM_TCP | 44461 | 0 | 270 | 0 | 270 | V | ####.#
GSMPMM1VoltageBetweenPhaseBC_V | REAL | IOD_GSM_TCP | 44463 | 0 | 450 | 0 | 450 | V | ####.#
GSMPMM1VoltageBetweenPhaseBN_V | REAL | IOD_GSM_TCP | 44465 | 0 | 270 | 0 | 270 | V | ####.#
GSMPMM1VoltageBetweenPhaseCA_V | REAL | IOD_GSM_TCP | 44467 | 0 | 450 | 0 | 450 | V | ####.#
GSMPMM1VoltageBetweenPhaseCN_V | REAL | IOD_GSM_TCP | 44469 | 0 | 270 | 0 | 270 | V | ####.#
GSMPMMfaza01 | REAL | IOD_GSM_TCP | 44471 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza02 | REAL | IOD_GSM_TCP | 44473 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza03 | REAL | IOD_GSM_TCP | 44475 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza04 | REAL | IOD_GSM_TCP | 44477 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza05 | REAL | IOD_GSM_TCP | 44479 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza06 | REAL | IOD_GSM_TCP | 44481 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza07 | REAL | IOD_GSM_TCP | 44483 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza08 | REAL | IOD_GSM_TCP | 44485 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza09 | REAL | IOD_GSM_TCP | 44487 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza10 | REAL | IOD_GSM_TCP | 44489 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza11 | REAL | IOD_GSM_TCP | 44491 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza12 | REAL | IOD_GSM_TCP | 44493 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza13 | REAL | IOD_GSM_TCP | 44495 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza14 | REAL | IOD_GSM_TCP | 44497 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza15 | REAL | IOD_GSM_TCP | 44499 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza16 | REAL | IOD_GSM_TCP | 44501 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza17 | REAL | IOD_GSM_TCP | 44503 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza18 | REAL | IOD_GSM_TCP | 44505 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza19 | REAL | IOD_GSM_TCP | 44507 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza20 | REAL | IOD_GSM_TCP | 44509 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza21 | REAL | IOD_GSM_TCP | 44511 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza22 | REAL | IOD_GSM_TCP | 44513 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza23 | REAL | IOD_GSM_TCP | 44515 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza24 | REAL | IOD_GSM_TCP | 44517 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza25 | REAL | IOD_GSM_TCP | 44519 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza26 | REAL | IOD_GSM_TCP | 44521 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza27 | REAL | IOD_GSM_TCP | 44523 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza28 | REAL | IOD_GSM_TCP | 44525 | 0 | 20 | 0 | 20 | A | ####.#
GSMPMMfaza29 | REAL | IOD_GSM_TCP | 44527
GSMPMMfaza30 | REAL | IOD_GSM_TCP | 44529
GSMPMMfaza31 | REAL | IOD_GSM_TCP | 44531
GSMPMMfaza32 | REAL | IOD_GSM_TCP | 44533
GSMPMMfaza33 | REAL | IOD_GSM_TCP | 44535
GSMPMMfaza34 | REAL | IOD_GSM_TCP | 44537
GSMPMMfaza35 | REAL | IOD_GSM_TCP | 44539
GSMPMMfaza36 | REAL | IOD_GSM_TCP | 44541
GSMPMMfaza37 | REAL | IOD_GSM_TCP | 44543
GSMPMMfaza38 | REAL | IOD_GSM_TCP | 44545
GSMPMMfaza39 | REAL | IOD_GSM_TCP | 44547
GSMPMMfaza40 | REAL | IOD_GSM_TCP | 44549
GSMPMMfaza41 | REAL | IOD_GSM_TCP | 44551
GSMPMMfaza42 | REAL | IOD_GSM_TCP | 44553
GSMPrevisokaTemp | DIGITAL | IOD_GSM_TCP | 00216
GSMQ0_izkljuceno | DIGITAL | IOD_GSM_TCP | 00217
GSMQ0_vkljuceno | DIGITAL | IOD_GSM_TCP | 00218
GSMQ12_izkljuceno | DIGITAL | IOD_GSM_TCP | 00219
GSMQ12_izpad | DIGITAL | IOD_GSM_TCP | 00220
GSMQ12_vkljuceno | DIGITAL | IOD_GSM_TCP | 00221
GSMQ12stanje | INT | IOD_GSM_TCP | 40197
GSMrazlitjeLAH1 | DIGITAL | IOD_GSM_TCP | 00222
GSMrazlitjeLAH2 | DIGITAL | IOD_GSM_TCP | 00223
GSMrazlitjeLAH3 | DIGITAL | IOD_GSM_TCP | 00224
GSMrazlitjeLAH4 | DIGITAL | IOD_GSM_TCP | 00225
GSMSetDateTime | DIGITAL | IOD_GSM_TCP | 00226
GSMSetDateTimeDemand | DIGITAL | IOD_GSM_TCP | 00227
GSMSetDateTimeError | DIGITAL | IOD_GSM_TCP | 00228
GSMSetDateTimeFinished | DIGITAL | IOD_GSM_TCP | 00229
GSMSkupneNapakeNaprav_PMM17VirBVirA | DIGITAL | IOD_GSM_TCP | 00230
GSMSlabaBaterijaPLC | DIGITAL | IOD_GSM_TCP | 00231
GSMTempHistereza | INT | IOD_GSM_TCP | 40198 | 0 | 60 | 0 | 60 | °C | ##
GSMTempPovp234 | INT | IOD_GSM_TCP | 40199 | 0 | 600 | 0 | 60 | °C | ##.#
GSMTempPovp234Alarm | INT | IOD_GSM_TCP | 40200 | 0 | 60 | 0 | 60 | °C | ##
GSMTempPovp234Previs | DIGITAL | IOD_GSM_TCP | 00232
GSMTempPovp56 | INT | IOD_GSM_TCP | 40201 | 0 | 600 | 0 | 60 | °C | ##.#
GSMTempPovp56Alarm | INT | IOD_GSM_TCP | 40202 | 0 | 60 | 0 | 60 | °C | ##
GSMTempPovp56Previs | DIGITAL | IOD_GSM_TCP | 00233
GSMTempZaVklopKlim1 | INT | IOD_GSM_TCP | 40203 | 0 | 60 | 0 | 60 | °C | ##
GSMTempZaVklopKlim2 | INT | IOD_GSM_TCP | 40204 | 0 | 60 | 0 | 60 | °C | ##
GSMTIA1_alarm | INT | IOD_GSM_TCP | 40205 | 0 | 60 | 0 | 60 | °C | ##
GSMTIA1_previs_temp | DIGITAL | IOD_GSM_TCP | 00234
GSMTIA1_temp_s | INT | IOD_GSM_TCP | 40206 | 0 | 600 | 0 | 60 | °C | ##.#
GSMTIA2_alarm | INT | IOD_GSM_TCP | 40207 | 0 | 60 | 0 | 60 | °C | ##
GSMTIA2_previs_temp | DIGITAL | IOD_GSM_TCP | 00235
GSMTIA2_temp_s | INT | IOD_GSM_TCP | 40208 | 0 | 600 | 0 | 60 | °C | ##.#
GSMTIA3_alarm | INT | IOD_GSM_TCP | 40209 | 0 | 60 | 0 | 60 | °C | ##
GSMTIA3_previs_temp | DIGITAL | IOD_GSM_TCP | 00236
GSMTIA3_temp_s | INT | IOD_GSM_TCP | 40210 | 0 | 600 | 0 | 60 | °C | ##.#
GSMTIA4_alarm | INT | IOD_GSM_TCP | 40211 | 0 | 60 | 0 | 60 | °C | ##
GSMTIA4_previs_temp | DIGITAL | IOD_GSM_TCP | 00237
GSMTIA4_temp_s | INT | IOD_GSM_TCP | 40212 | 0 | 600 | 0 | 60 | °C | ##.#
GSMTIA5_alarm | INT | IOD_GSM_TCP | 40213 | 0 | 60 | 0 | 60 | °C | ##
GSMTIA5_previs_temp | DIGITAL | IOD_GSM_TCP | 00238
GSMTIA5_temp_s | INT | IOD_GSM_TCP | 40214 | 0 | 600 | 0 | 60 | °C | ##.#
GSMTIA6_alarm | INT | IOD_GSM_TCP | 40215 | 0 | 60 | 0 | 60 | °C | ##
GSMTIA6_previs_temp | DIGITAL | IOD_GSM_TCP | 00239
GSMTIA6_temp_s | INT | IOD_GSM_TCP | 40216 | 0 | 600 | 0 | 60 | °C | ##.#
GSMTIA7_alarm | INT | IOD_GSM_TCP | 40217 | 0 | 60 | 0 | 60 | °C | ##
GSMTIA7_previs_temp | DIGITAL | IOD_GSM_TCP | 00240
GSMTIA7_temp_s | INT | IOD_GSM_TCP | 40218 | 0 | 600 | 0 | 60 | °C | ##.#
GSMUPS1Errors10 | DIGITAL | IOD_GSM_TCP | 00241
GSMUPS1Errors11 | DIGITAL | IOD_GSM_TCP | 00242
GSMUPS1Errors12 | DIGITAL | IOD_GSM_TCP | 00243
GSMUPS1Errors13 | DIGITAL | IOD_GSM_TCP | 00244
GSMUPS1Errors14 | DIGITAL | IOD_GSM_TCP | 00245
GSMUPS1Errors15 | DIGITAL | IOD_GSM_TCP | 00246
GSMUPS1Errors16 | DIGITAL | IOD_GSM_TCP | 00247
GSMUPS1Errors17 | DIGITAL | IOD_GSM_TCP | 00248
GSMUPS1Errors18 | DIGITAL | IOD_GSM_TCP | 00249
GSMUPS1Errors19 | DIGITAL | IOD_GSM_TCP | 00250
GSMUPS1Errors1 | DIGITAL | IOD_GSM_TCP | 00251
GSMUPS1Errors20 | DIGITAL | IOD_GSM_TCP | 00252
GSMUPS1Errors21 | DIGITAL | IOD_GSM_TCP | 00253
GSMUPS1Errors22 | DIGITAL | IOD_GSM_TCP | 00254
GSMUPS1Errors23 | DIGITAL | IOD_GSM_TCP | 00255
GSMUPS1Errors24 | DIGITAL | IOD_GSM_TCP | 00256
GSMUPS1Errors25 | DIGITAL | IOD_GSM_TCP | 00257
GSMUPS1Errors2 | DIGITAL | IOD_GSM_TCP | 00258
GSMUPS1Errors3 | DIGITAL | IOD_GSM_TCP | 00259
GSMUPS1Errors4 | DIGITAL | IOD_GSM_TCP | 00260
GSMUPS1Errors5 | DIGITAL | IOD_GSM_TCP | 00261
GSMUPS1Errors6 | DIGITAL | IOD_GSM_TCP | 00262
GSMUPS1Errors7 | DIGITAL | IOD_GSM_TCP | 00263
GSMUPS1Errors8 | DIGITAL | IOD_GSM_TCP | 00264
GSMUPS1Errors9 | DIGITAL | IOD_GSM_TCP | 00265
GSMUPS2Errors10 | DIGITAL | IOD_GSM_TCP | 00266
GSMUPS2Errors11 | DIGITAL | IOD_GSM_TCP | 00267
GSMUPS2Errors12 | DIGITAL | IOD_GSM_TCP | 00268
GSMUPS2Errors13 | DIGITAL | IOD_GSM_TCP | 00269
GSMUPS2Errors14 | DIGITAL | IOD_GSM_TCP | 00270
GSMUPS2Errors15 | DIGITAL | IOD_GSM_TCP | 00271
GSMUPS2Errors16 | DIGITAL | IOD_GSM_TCP | 00272
GSMUPS2Errors17 | DIGITAL | IOD_GSM_TCP | 00273
GSMUPS2Errors18 | DIGITAL | IOD_GSM_TCP | 00274
GSMUPS2Errors19 | DIGITAL | IOD_GSM_TCP | 00275
GSMUPS2Errors1 | DIGITAL | IOD_GSM_TCP | 00276
GSMUPS2Errors20 | DIGITAL | IOD_GSM_TCP | 00277
GSMUPS2Errors21 | DIGITAL | IOD_GSM_TCP | 00278
GSMUPS2Errors22 | DIGITAL | IOD_GSM_TCP | 00279
GSMUPS2Errors23 | DIGITAL | IOD_GSM_TCP | 00280
GSMUPS2Errors24 | DIGITAL | IOD_GSM_TCP | 00281
GSMUPS2Errors25 | DIGITAL | IOD_GSM_TCP | 00282
GSMUPS2Errors2 | DIGITAL | IOD_GSM_TCP | 00283
GSMUPS2Errors3 | DIGITAL | IOD_GSM_TCP | 00284
GSMUPS2Errors4 | DIGITAL | IOD_GSM_TCP | 00285
GSMUPS2Errors5 | DIGITAL | IOD_GSM_TCP | 00286
GSMUPS2Errors6 | DIGITAL | IOD_GSM_TCP | 00287
GSMUPS2Errors7 | DIGITAL | IOD_GSM_TCP | 00288
GSMUPS2Errors8 | DIGITAL | IOD_GSM_TCP | 00289
GSMUPS2Errors9 | DIGITAL | IOD_GSM_TCP | 00290
GSMUPS1AlarmAwaitingPower | DIGITAL | IOD_GSM_TCP | 00291
GSMUPS1AlarmBypassBad | DIGITAL | IOD_GSM_TCP | 00292
GSMUPS1AlarmChargerFailed | DIGITAL | IOD_GSM_TCP | 00293
GSMUPS1AlarmCommunicationsLost | DIGITAL | IOD_GSM_TCP | 00294
GSMUPS1AlarmDepletedBattery | DIGITAL | IOD_GSM_TCP | 00295
GSMUPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM_TCP | 00296
GSMUPS1AlarmInverterError | DIGITAL | IOD_GSM_TCP | 00297
GSMUPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 00298
GSMUPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM_TCP | 00299
GSMUPS1AlarmLowBattery | DIGITAL | IOD_GSM_TCP | 00300
GSMUPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM_TCP | 00301
GSMUPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM_TCP | 00302
GSMUPS1AlarmOnBattery | DIGITAL | IOD_GSM_TCP | 00303
GSMUPS1AlarmOnBypass | DIGITAL | IOD_GSM_TCP | 00304
GSMUPS1AlarmShutdownImminent | DIGITAL | IOD_GSM_TCP | 00305
GSMUPS1AlarmShutdownPending | DIGITAL | IOD_GSM_TCP | 00306
GSMUPS1AlarmSlabaBaterija | DIGITAL | IOD_GSM_TCP | 00307
GSMUPS1AlarmSplosnaNapaka | DIGITAL | IOD_GSM_TCP | 00308
GSMUPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00309
GSMUPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00310
GSMUPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00311
GSMUPS1AlarmTestInProgres | DIGITAL | IOD_GSM_TCP | 00312
GSMUPS1AlarmUPSIzhodOff | DIGITAL | IOD_GSM_TCP | 00313
GSMUPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 00314
GSMUPS1AlarmUPSSystemOff | DIGITAL | IOD_GSM_TCP | 00315
GSMUPS1EstimatedChargeRemaining | REAL | IOD_GSM_TCP | 44555 | 0 | 100 | 0 | 100 | % | ###
GSMUPS1EstimatedMinutesRemaining | REAL | IOD_GSM_TCP | 44557 | 0 | 500 | 0 | 500 | min | ###
GSMUPS1InverterStatus | INT | IOD_GSM_TCP | 40219
GSMUPS1IzhodMocL1 | REAL | IOD_GSM_TCP | 44559 | 0 | 100 | 0 | 100 | % | ##.#
GSMUPS1IzhodMocL2 | REAL | IOD_GSM_TCP | 44561 | 0 | 100 | 0 | 100 | % | ##.#
GSMUPS1IzhodMocL3 | REAL | IOD_GSM_TCP | 44563 | 0 | 100 | 0 | 100 | % | ##.#
GSMUPS1Napaka | DIGITAL | IOD_GSM_TCP | 00316
GSMUPS1NapetostBaterije | REAL | IOD_GSM_TCP | 44565 | 0 | 500 | 0 | 500 | V | ###.#
GSMUPS1OutputStatus | INT | IOD_GSM_TCP | 40220
GSMUPS1StatusBaterije | UINT | IOD_GSM_TCP | 46020 | [5 empty] | ##
GSMUPS1StatusEcomodeAktiven | DIGITAL | IOD_GSM_TCP | 00317
GSMUPS1StatusInverterIsOn | DIGITAL | IOD_GSM_TCP | 00318
GSMUPS1StatusStopOperation | DIGITAL | IOD_GSM_TCP | 00319
GSMUPS1SteviloIzpadovVhodneLinije | INT | IOD_GSM_TCP | 40221 | [5 empty] | #####
GSMUPS1TemperaturaBaterije | REAL | IOD_GSM_TCP | 44567 | 0 | 100 | 0 | 100 | °C | ###
GSMUPS1UnitStatus | INT | IOD_GSM_TCP | 40222
GSMUPS1VhodFrekvencaL1 | REAL | IOD_GSM_TCP | 44569 | 0 | 60 | 0 | 60 | Hz | ##.#
GSMUPS1VhodFrekvencaL2 | REAL | IOD_GSM_TCP | 44571 | 0 | 60 | 0 | 60 | Hz | ##.#
GSMUPS1VhodFrekvencaL3 | REAL | IOD_GSM_TCP | 44573 | 0 | 60 | 0 | 60 | Hz | ##.#
GSMUPS1VhodNapetostL1 | REAL | IOD_GSM_TCP | 44575 | 0 | 500 | 0 | 500 | V | ###.#
GSMUPS1VhodNapetostL2 | REAL | IOD_GSM_TCP | 44577 | 0 | 500 | 0 | 500 | V | ###.#
GSMUPS1VhodNapetostL3 | REAL | IOD_GSM_TCP | 44579 | 0 | 500 | 0 | 500 | V | ###.#
GSMUPS2AlarmAwaitingPower | DIGITAL | IOD_GSM_TCP | 00320
GSMUPS2AlarmBypassBad | DIGITAL | IOD_GSM_TCP | 00321
GSMUPS2AlarmChargerFailed | DIGITAL | IOD_GSM_TCP | 00322
GSMUPS2AlarmCommunicationsLost | DIGITAL | IOD_GSM_TCP | 00323
GSMUPS2AlarmDepletedBattery | DIGITAL | IOD_GSM_TCP | 00324
GSMUPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM_TCP | 00325
GSMUPS2AlarmInverterError | DIGITAL | IOD_GSM_TCP | 00326
GSMUPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 00327
GSMUPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM_TCP | 00328
GSMUPS2AlarmLowBattery | DIGITAL | IOD_GSM_TCP | 00329
GSMUPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM_TCP | 00330
GSMUPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM_TCP | 00331
GSMUPS2AlarmOnBattery | DIGITAL | IOD_GSM_TCP | 00332
GSMUPS2AlarmOnBypass | DIGITAL | IOD_GSM_TCP | 00333
GSMUPS2AlarmShutdownImminent | DIGITAL | IOD_GSM_TCP | 00334
GSMUPS2AlarmShutdownPending | DIGITAL | IOD_GSM_TCP | 00335
GSMUPS2AlarmSlabaBaterija | DIGITAL | IOD_GSM_TCP | 00336
GSMUPS2AlarmSplosnaNapaka | DIGITAL | IOD_GSM_TCP | 00337
GSMUPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00338
GSMUPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00339
GSMUPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00340
GSMUPS2AlarmTestInProgres | DIGITAL | IOD_GSM_TCP | 00341
GSMUPS2AlarmUPSIzhodOff | DIGITAL | IOD_GSM_TCP | 00342
GSMUPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 00343
GSMUPS2AlarmUPSSystemOff | DIGITAL | IOD_GSM_TCP | 00344
GSMUPS2EstimatedChargeRemaining | REAL | IOD_GSM_TCP | 44581 | 0 | 100 | 0 | 100 | % | ###
GSMUPS2EstimatedMinutesRemaining | REAL | IOD_GSM_TCP | 44583 | 0 | 500 | 0 | 500 | min | ###
GSMUPS2InverterStatus | INT | IOD_GSM_TCP | 40223
GSMUPS2IzhodMocL1 | REAL | IOD_GSM_TCP | 44585 | 0 | 100 | 0 | 100 | % | ##.#
GSMUPS2IzhodMocL2 | REAL | IOD_GSM_TCP | 44587 | 0 | 100 | 0 | 100 | % | ##.#
GSMUPS2IzhodMocL3 | REAL | IOD_GSM_TCP | 44589 | 0 | 100 | 0 | 100 | % | ##.#
GSMUPS2Napaka | DIGITAL | IOD_GSM_TCP | 00345
GSMUPS2NapetostBaterije | REAL | IOD_GSM_TCP | 44591 | 0 | 500 | 0 | 500 | V | ###.#
GSMUPS2OutputStatus | INT | IOD_GSM_TCP | 40224
GSMUPS2StatusBaterije | UINT | IOD_GSM_TCP | 46021 | [5 empty] | ##
GSMUPS2StatusEcomodeAktiven | DIGITAL | IOD_GSM_TCP | 00346
GSMUPS2StatusInverterIsOn | DIGITAL | IOD_GSM_TCP | 00347
GSMUPS2StatusStopOperation | DIGITAL | IOD_GSM_TCP | 00348
GSMUPS2SteviloIzpadovVhodneLinije | INT | IOD_GSM_TCP | 40225 | [5 empty] | #####
GSMUPS2TemperaturaBaterije | REAL | IOD_GSM_TCP | 44593 | 0 | 100 | 0 | 100 | °C | ###
GSMUPS2UnitStatus | INT | IOD_GSM_TCP | 40226
GSMUPS2VhodFrekvencaL1 | REAL | IOD_GSM_TCP | 44595 | 0 | 60 | 0 | 60 | Hz | ##.#
GSMUPS2VhodFrekvencaL2 | REAL | IOD_GSM_TCP | 44597 | 0 | 60 | 0 | 60 | Hz | ##.#
GSMUPS2VhodFrekvencaL3 | REAL | IOD_GSM_TCP | 44599 | 0 | 60 | 0 | 60 | Hz | ##.#
GSMUPS2VhodNapetostL1 | REAL | IOD_GSM_TCP | 44601 | 0 | 500 | 0 | 500 | V | ###.#
GSMUPS2VhodNapetostL2 | REAL | IOD_GSM_TCP | 44603 | 0 | 500 | 0 | 500 | V | ###.#
GSMUPS2VhodNapetostL3 | REAL | IOD_GSM_TCP | 44605 | 0 | 500 | 0 | 500 | V | ###.#
GSMUPS_A_V23_delovanje | DIGITAL | IOD_GSM_TCP | 00349
GSMUPS_A_V23_napaka | DIGITAL | IOD_GSM_TCP | 00350
GSMups_alarm | DIGITAL | IOD_GSM_TCP | 00351
GSMups_baterijski_nac | DIGITAL | IOD_GSM_TCP | 00352
GSMUPS_MGE1BatteryBackupTime | INT | IOD_GSM_TCP | 40227 | 0 | 500 | 0 | 500 | min | ###
GSMUPS_MGE1BatteryChargedState | DIGITAL | IOD_GSM_TCP | 00353
GSMUPS_MGE1BatteryChargingLevel | INT | IOD_GSM_TCP | 40228 | 0 | 100 | 0 | 100 | % | ##.#
GSMUPS_MGE1BatteryCircuitBreaker | DIGITAL | IOD_GSM_TCP | 00354
GSMUPS_MGE1BatteryCompInProgress | DIGITAL | IOD_GSM_TCP | 00355
GSMUPS_MGE1BatteryFuseFault | DIGITAL | IOD_GSM_TCP | 00356
GSMUPS_MGE1BatteryLowWarning | DIGITAL | IOD_GSM_TCP | 00357
GSMUPS_MGE1BatteryRechargeDuration | INT | IOD_GSM_TCP | 40229
GSMUPS_MGE1BatteryTempOutOfToler | DIGITAL | IOD_GSM_TCP | 00358
GSMUPS_MGE1BypassInFreeFrequency | DIGITAL | IOD_GSM_TCP | 00359
GSMUPS_MGE1ChargerGeneralFault | DIGITAL | IOD_GSM_TCP | 00360
GSMUPS_MGE1DeviceVentilationFault | DIGITAL | IOD_GSM_TCP | 00361
GSMUPS_MGE1I1output | INT | IOD_GSM_TCP | 40230 | 0 | 100 | 0 | 100 | A | ####.#
GSMUPS_MGE1I2output | INT | IOD_GSM_TCP | 40231 | 0 | 100 | 0 | 100 | A | ####.#
GSMUPS_MGE1I3output | INT | IOD_GSM_TCP | 40232 | 0 | 100 | 0 | 100 | A | ####.#
GSMUPS_MGE1InverterFrequency | INT | IOD_GSM_TCP | 40233
GSMUPS_MGE1InverterFuseFault | DIGITAL | IOD_GSM_TCP | 00362
GSMUPS_MGE1InverterOverload | DIGITAL | IOD_GSM_TCP | 00363
GSMUPS_MGE1InverterThermalOverload | DIGITAL | IOD_GSM_TCP | 00364
GSMUPS_MGE1Mains1VoltOutOfToler | DIGITAL | IOD_GSM_TCP | 00365
GSMUPS_MGE1Mains2Overload | DIGITAL | IOD_GSM_TCP | 00366
GSMUPS_MGE1Mains2VoltOutOfToler | DIGITAL | IOD_GSM_TCP | 00367
GSMUPS_MGE1MaintenancePosition | DIGITAL | IOD_GSM_TCP | 00368
GSMUPS_MGE1ManualBypassSwitch | DIGITAL | IOD_GSM_TCP | 00369
GSMUPS_MGE1NapakaNaVarovalkah | DIGITAL | IOD_GSM_TCP | 00370
GSMUPS_MGE1OutputActivePower1 | INT | IOD_GSM_TCP | 40234 | 0 | 100 | 0 | 100 | % | ##.#
GSMUPS_MGE1OutputActivePower2 | INT | IOD_GSM_TCP | 40235 | 0 | 100 | 0 | 100 | % | ##.#
GSMUPS_MGE1OutputActivePower3 | INT | IOD_GSM_TCP | 40236 | 0 | 100 | 0 | 100 | % | ##.#
GSMUPS_MGE1OutputFrequency | INT | IOD_GSM_TCP | 40237 | 0 | 60 | 0 | 60 | Hz | ##.#
GSMUPS_MGE1OutputInShortCircuit | DIGITAL | IOD_GSM_TCP | 00371
GSMUPS_MGE1OutputLoadLevel | INT | IOD_GSM_TCP | 40238
GSMUPS_MGE1OutputOverload | DIGITAL | IOD_GSM_TCP | 00372
GSMUPS_MGE1OutputThermalOverload | DIGITAL | IOD_GSM_TCP | 00373
GSMUPS_MGE1RectifierOn | DIGITAL | IOD_GSM_TCP | 00374
GSMUPS_MGE1RectifierThermOverload | DIGITAL | IOD_GSM_TCP | 00375
GSMUPS_MGE1Skupna_napaka | DIGITAL | IOD_GSM_TCP | 00376
GSMUPS_MGE1StatusBaterije | INT | IOD_GSM_TCP | 40239
GSMUPS_MGE1U12mains1 | INT | IOD_GSM_TCP | 40240 | 0 | 500 | 0 | 500 | V | ###.#
GSMUPS_MGE1U12mains2 | INT | IOD_GSM_TCP | 40241 | 0 | 500 | 0 | 500 | V | ###.#
GSMUPS_MGE1U1N_inverter | INT | IOD_GSM_TCP | 40242
GSMUPS_MGE1U1N_output | INT | IOD_GSM_TCP | 40243 | 0 | 270 | 0 | 270 | V | ####.#
GSMUPS_MGE1U23mains1 | INT | IOD_GSM_TCP | 40244 | 0 | 500 | 0 | 500 | V | ###.#
GSMUPS_MGE1U23mains2 | INT | IOD_GSM_TCP | 40245 | 0 | 500 | 0 | 500 | V | ###.#
GSMUPS_MGE1U2N_inverter | INT | IOD_GSM_TCP | 40246
GSMUPS_MGE1U2N_output | INT | IOD_GSM_TCP | 40247 | 0 | 270 | 0 | 270 | V | ####.#
GSMUPS_MGE1U31mains1 | INT | IOD_GSM_TCP | 40248 | 0 | 500 | 0 | 500 | V | ###.#
GSMUPS_MGE1U31mains2 | INT | IOD_GSM_TCP | 40249 | 0 | 500 | 0 | 500 | V | ###.#
GSMUPS_MGE1U3N_inverter | INT | IOD_GSM_TCP | 40250
GSMUPS_MGE1U3N_output | INT | IOD_GSM_TCP | 40251 | 0 | 270 | 0 | 270 | V | ####.#
GSMUPS_MGE1U_battery | INT | IOD_GSM_TCP | 40252 | 0 | 500 | 0 | 500 | V | ###.#
GSMUPS_MGE1UPS_coupled | DIGITAL | IOD_GSM_TCP | 00377
GSMUPS_MGE1UPS_error | DIGITAL | IOD_GSM_TCP | 00378
GSMUPS_MGE1UPS_in_backup | DIGITAL | IOD_GSM_TCP | 00379
GSMups_polnjenje | DIGITAL | IOD_GSM_TCP | 00380
GSMUPS_V23_delovanje | DIGITAL | IOD_GSM_TCP | 00381
GSMUPS_V23_napaka | DIGITAL | IOD_GSM_TCP | 00382
GSMUPS_V25_delovanje | DIGITAL | IOD_GSM_TCP | 00383
GSMUPS_V25_napaka | DIGITAL | IOD_GSM_TCP | 00384
GSMUPSMGEErrors10 | DIGITAL | IOD_GSM_TCP | 00385
GSMUPSMGEErrors11 | DIGITAL | IOD_GSM_TCP | 00386
GSMUPSMGEErrors12 | DIGITAL | IOD_GSM_TCP | 00387
GSMUPSMGEErrors13 | DIGITAL | IOD_GSM_TCP | 00388
GSMUPSMGEErrors14 | DIGITAL | IOD_GSM_TCP | 00389
GSMUPSMGEErrors15 | DIGITAL | IOD_GSM_TCP | 00390
GSMUPSMGEErrors16 | DIGITAL | IOD_GSM_TCP | 00391
GSMUPSMGEErrors17 | DIGITAL | IOD_GSM_TCP | 00392
GSMUPSMGEErrors1 | DIGITAL | IOD_GSM_TCP | 00393
GSMUPSMGEErrors2 | DIGITAL | IOD_GSM_TCP | 00394
GSMUPSMGEErrors3 | DIGITAL | IOD_GSM_TCP | 00395
GSMUPSMGEErrors4 | DIGITAL | IOD_GSM_TCP | 00396
GSMUPSMGEErrors5 | DIGITAL | IOD_GSM_TCP | 00397
GSMUPSMGEErrors6 | DIGITAL | IOD_GSM_TCP | 00398
GSMUPSMGEErrors7 | DIGITAL | IOD_GSM_TCP | 00399
GSMUPSMGEErrors8 | DIGITAL | IOD_GSM_TCP | 00400
GSMUPSMGEErrors9 | DIGITAL | IOD_GSM_TCP | 00401
GSMUserCurrentLevel | INT | IOD_GSM_TCP | 40253
GSMUserCurrentName | STRING | IOD_GSM_TCP | 45061[15]
GSMUserLoggedIn | DIGITAL | IOD_GSM_TCP | 00402
GSMVLAZILEC1_delovanje | DIGITAL | IOD_GSM_TCP | 00403
GSMVLAZILEC1_napaka | DIGITAL | IOD_GSM_TCP | 00404
GSMVLAZILEC2_delovanje | DIGITAL | IOD_GSM_TCP | 00405
GSMVLAZILEC2_napaka | DIGITAL | IOD_GSM_TCP | 00406
GSMXVH_AlarmOn | DIGITAL | IOD_GSM_TCP | 00407
GSMXVH_enopolna_napaka | DIGITAL | IOD_GSM_TCP | 00408
GSMXVH_UPSstatus | INT | IOD_GSM_TCP | 40254
GSMXVHdepltedBatery1 | REAL | IOD_GSM_TCP | 44607
GSMXVHdepltedBatery2 | REAL | IOD_GSM_TCP | 44609
GSMXVHlowBatery1 | REAL | IOD_GSM_TCP | 44611
GSMXVHlowBatery2 | REAL | IOD_GSM_TCP | 44613
GSMPMM_2x17_VirA_zavihek | DIGITAL | IOD_GSM_disk | D288 | [6 empty] | 6157 | 0
GSMPMM_2x17_VirB_zavihek | DIGITAL | IOD_GSM_disk | D289 | [6 empty] | 6157 | 0
GSMServer_B_Izpad | DIGITAL | IOD_GSM_mem | D566
GSMServer_A_Izpad | DIGITAL | IOD_GSM_mem | D567
GSM_meja_tok_opozoriloL1 | INT | IOD_GSM_disk | I300
GSM_meja_tok_opozoriloL2 | INT | IOD_GSM_disk | I302
GSM_meja_tok_opozoriloL3 | INT | IOD_GSM_disk | I304
GSM_meja_tok_alarmL1 | INT | IOD_GSM_disk | I306
GSM_meja_tok_alarmL2 | INT | IOD_GSM_disk | I308
GSM_meja_tok_alarmL3 | INT | IOD_GSM_disk | I310
GSM_omogocanje_tok_opozorilaL1 | DIGITAL | IOD_GSM_disk | D312
GSM_omogocanje_tok_opozorilaL2 | DIGITAL | IOD_GSM_disk | D313
GSM_omogocanje_tok_opozorilaL3 | DIGITAL | IOD_GSM_disk | D314
GSM_omogocanje_tok_alarmL1 | DIGITAL | IOD_GSM_disk | D315
GSM_omogocanje_tok_alarmL2 | DIGITAL | IOD_GSM_disk | D316
GSM_omogocanje_tok_alarmL3 | DIGITAL | IOD_GSM_disk | D317
GSMErrComCirc1_om | DIGITAL | IOD_GSM_disk | D318
GSMErrComKlima1_om | DIGITAL | IOD_GSM_disk | D319
GSMErrComKlima2_om | DIGITAL | IOD_GSM_disk | D320
GSMErrComPMM1_om | DIGITAL | IOD_GSM_disk | D321
GSMErrComPort2_om | DIGITAL | IOD_GSM_disk | D322
GSMErrComPort3_om | DIGITAL | IOD_GSM_disk | D323
GSMErrComPort4_om | DIGITAL | IOD_GSM_disk | D324
GSMErrComUPS1_om | DIGITAL | IOD_GSM_disk | D325
GSMErrComUPS2_om | DIGITAL | IOD_GSM_disk | D326
GSMErrComUPSMGE1_om | DIGITAL | IOD_GSM_disk | D327
GSMrazlitjeLAH1_om | DIGITAL | IOD_GSM_disk | D328
GSMrazlitjeLAH2_om | DIGITAL | IOD_GSM_disk | D329
GSMrazlitjeLAH3_om | DIGITAL | IOD_GSM_disk | D330
GSMrazlitjeLAH4_om | DIGITAL | IOD_GSM_disk | D331
GSMServer_A_Izpad_om | DIGITAL | IOD_GSM_disk | D332
GSMServer_B_Izpad_om | DIGITAL | IOD_GSM_disk | D333
GSMnapaka_kom_panel_om | DIGITAL | IOD_GSM_disk | D334
GSMSetDateTimeError_om | DIGITAL | IOD_GSM_disk | D335
GSMSlabaBaterijaPLC_om | DIGITAL | IOD_GSM_disk | D336
GSMups_baterijski_nac_om | DIGITAL | IOD_GSM_disk | D337
GSMups_alarm_om | DIGITAL | IOD_GSM_disk | D338
GSMups_polnjenje_om | DIGITAL | IOD_GSM_disk | D339
GSMQ0_izkljuceno_om | DIGITAL | IOD_GSM_disk | D340
GSMQ0_vkljuceno_om | DIGITAL | IOD_GSM_disk | D341
GSMQ12_izkljuceno_om | DIGITAL | IOD_GSM_disk | D342
GSMQ12_izpad_om | DIGITAL | IOD_GSM_disk | D343
GSMQ12_vkljuceno_om | DIGITAL | IOD_GSM_disk | D344
GSMN_F1_1_zascita_ok_om | DIGITAL | IOD_GSM_disk | D345
GSMK1_SkupnaNapaka_om | DIGITAL | IOD_GSM_disk | D346
GSMK1AlarmPozara_om | DIGITAL | IOD_GSM_disk | D347
GSMK1KlimaZdruzenAlarm_om | DIGITAL | IOD_GSM_disk | D348
GSMK1NiPretoka_om | DIGITAL | IOD_GSM_disk | D349
GSMK1OkvaraRototerma_om | DIGITAL | IOD_GSM_disk | D350
GSMK1OkvaraVlazNap_om | DIGITAL | IOD_GSM_disk | D351
GSMK1PreobMotCrpGr_om | DIGITAL | IOD_GSM_disk | D352
GSMK1PreobMotVent_om | DIGITAL | IOD_GSM_disk | D353
GSMK1ProtizamrzZascAkt_om | DIGITAL | IOD_GSM_disk | D354
GSMK1ZamasenostFiltra_om | DIGITAL | IOD_GSM_disk | D355
GSMKLIMAT1_delovanje_om | DIGITAL | IOD_GSM_disk | D356
GSMKLIMAT1_vklop_delovanja_om | DIGITAL | IOD_GSM_disk | D357
GSMN_KLIMAT1_napaka_om | DIGITAL | IOD_GSM_disk | D358
GSMKlimeAVTO_om | DIGITAL | IOD_GSM_disk | D359
GSMKlima1_izkljucena_om | DIGITAL | IOD_GSM_disk | D360
GSMN_VLAZILEC1_napaka_om | DIGITAL | IOD_GSM_disk | D361
GSMK2_SkupnaNapaka_om | DIGITAL | IOD_GSM_disk | D362
GSMK2AlarmPozara_om | DIGITAL | IOD_GSM_disk | D363
GSMK2KlimaZdruzenAlarm_om | DIGITAL | IOD_GSM_disk | D364
GSMK2NiPretoka_om | DIGITAL | IOD_GSM_disk | D365
GSMK2OkvaraRototerma_om | DIGITAL | IOD_GSM_disk | D366
GSMK2OkvaraVlazNap_om | DIGITAL | IOD_GSM_disk | D367
GSMK2PreobMotCrpGr_om | DIGITAL | IOD_GSM_disk | D368
GSMK2PreobMotVent_om | DIGITAL | IOD_GSM_disk | D369
GSMK2ProtizamrzZascAkt_om | DIGITAL | IOD_GSM_disk | D370
GSMK2ZamasenostFiltra_om | DIGITAL | IOD_GSM_disk | D371
GSMKLIMAT2_delovanje_om | DIGITAL | IOD_GSM_disk | D372
GSMKLIMAT2_vklop_delovanja_om | DIGITAL | IOD_GSM_disk | D373
GSMN_KLIMAT2_napaka_om | DIGITAL | IOD_GSM_disk | D374
GSMKlima2_izkljucena_om | DIGITAL | IOD_GSM_disk | D375
GSMN_VLAZILEC2_napaka_om | DIGITAL | IOD_GSM_disk | D376
GSMKLIMA_m1_napaka_om | DIGITAL | IOD_GSM_disk | D377
GSMKLIMA_m2_napaka_om | DIGITAL | IOD_GSM_disk | D378
GSMKlima3_izkljucena_om | DIGITAL | IOD_GSM_disk | D379
GSMN_KLIMA1_krm_nap_ok_om | DIGITAL | IOD_GSM_disk | D380
GSMKLIMA1_kke_pogon_om | DIGITAL | IOD_GSM_disk | D381
GSMKLIMA_m1_delovanje_om | DIGITAL | IOD_GSM_disk | D382
GSMKLIMA_m2_delovanje_om | DIGITAL | IOD_GSM_disk | D383
GSMK3_deluje_om | DIGITAL | IOD_GSM_disk | D384
GSMK3_SkupnaNapaka_om | DIGITAL | IOD_GSM_disk | D385
GSMN_UPS_V23_delovanje_om | DIGITAL | IOD_GSM_disk | D386
GSMN_UPS_V23_napaka_om | DIGITAL | IOD_GSM_disk | D387
GSMUPS1AlarmSlabaBaterija_om | DIGITAL | IOD_GSM_disk | D388
GSMUPS1AlarmOnBattery_om | DIGITAL | IOD_GSM_disk | D389
GSMUPS1AlarmLowBattery_om | DIGITAL | IOD_GSM_disk | D390
GSMUPS1AlarmDepletedBattery_om | DIGITAL | IOD_GSM_disk | D391
GSMUPS1AlarmTemperaturaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D392
GSMUPS1AlarmStanjeVhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D393
GSMUPS1AlarmStanjeIzhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D394
GSMUPS1AlarmIzhodPreobremenjen_om | DIGITAL | IOD_GSM_disk | D395
GSMUPS1AlarmOnBypass_om | DIGITAL | IOD_GSM_disk | D396
GSMUPS1AlarmBypassBad_om | DIGITAL | IOD_GSM_disk | D397
GSMUPS1AlarmIzhodOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D398
GSMUPS1AlarmUPSOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D399
GSMUPS1AlarmChargerFailed_om | DIGITAL | IOD_GSM_disk | D400
GSMUPS1AlarmUPSIzhodOff_om | DIGITAL | IOD_GSM_disk | D401
GSMUPS1AlarmUPSSystemOff_om | DIGITAL | IOD_GSM_disk | D402
GSMUPS1AlarmNapakaNaVentilatorju_om | DIGITAL | IOD_GSM_disk | D403
GSMUPS1AlarmNapakaNaVarovalki_om | DIGITAL | IOD_GSM_disk | D404
GSMUPS1AlarmSplosnaNapaka_om | DIGITAL | IOD_GSM_disk | D405
GSMUPS1AlarmDiagnosticTestFailed_om | DIGITAL | IOD_GSM_disk | D406
GSMUPS1AlarmCommunicationsLost_om | DIGITAL | IOD_GSM_disk | D407
GSMUPS1AlarmAwaitingPower_om | DIGITAL | IOD_GSM_disk | D408
GSMUPS1AlarmShutdownPending_om | DIGITAL | IOD_GSM_disk | D409
GSMUPS1AlarmShutdownImminent_om | DIGITAL | IOD_GSM_disk | D410
GSMUPS1AlarmTestInProgres_om | DIGITAL | IOD_GSM_disk | D411
GSMUPS1AlarmInverterError_om | DIGITAL | IOD_GSM_disk | D412
GSMN_UPS_V25_delovanje_om | DIGITAL | IOD_GSM_disk | D413
GSMN_UPS_V25_napaka_om | DIGITAL | IOD_GSM_disk | D414
GSMUPS2AlarmSlabaBaterija_om | DIGITAL | IOD_GSM_disk | D415
GSMUPS2AlarmOnBattery_om | DIGITAL | IOD_GSM_disk | D416
GSMUPS2AlarmLowBattery_om | DIGITAL | IOD_GSM_disk | D417
GSMUPS2AlarmDepletedBattery_om | DIGITAL | IOD_GSM_disk | D418
GSMUPS2AlarmTemperaturaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D419
GSMUPS2AlarmStanjeVhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D420
GSMUPS2AlarmStanjeIzhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D421
GSMUPS2AlarmIzhodPreobremenjen_om | DIGITAL | IOD_GSM_disk | D422
GSMUPS2AlarmOnBypass_om | DIGITAL | IOD_GSM_disk | D423
GSMUPS2AlarmBypassBad_om | DIGITAL | IOD_GSM_disk | D424
GSMUPS2AlarmIzhodOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D425
GSMUPS2AlarmUPSOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D426
GSMUPS2AlarmChargerFailed_om | DIGITAL | IOD_GSM_disk | D427
GSMUPS2AlarmUPSIzhodOff_om | DIGITAL | IOD_GSM_disk | D428
GSMUPS2AlarmUPSSystemOff_om | DIGITAL | IOD_GSM_disk | D429
GSMUPS2AlarmNapakaNaVentilatorju_om | DIGITAL | IOD_GSM_disk | D430
GSMUPS2AlarmNapakaNaVarovalki_om | DIGITAL | IOD_GSM_disk | D431
GSMUPS2AlarmSplosnaNapaka_om | DIGITAL | IOD_GSM_disk | D432
GSMUPS2AlarmDiagnosticTestFailed_om | DIGITAL | IOD_GSM_disk | D433
GSMUPS2AlarmCommunicationsLost_om | DIGITAL | IOD_GSM_disk | D434
GSMUPS2AlarmAwaitingPower_om | DIGITAL | IOD_GSM_disk | D435
GSMUPS2AlarmShutdownPending_om | DIGITAL | IOD_GSM_disk | D436
GSMUPS2AlarmShutdownImminent_om | DIGITAL | IOD_GSM_disk | D437
GSMUPS2AlarmTestInProgres_om | DIGITAL | IOD_GSM_disk | D438
GSMUPS2AlarmInverterError_om | DIGITAL | IOD_GSM_disk | D439
GSMUPS_MGE1UPS_error_om | DIGITAL | IOD_GSM_disk | D440
GSMUPS_MGE1BatteryLowWarning_om | DIGITAL | IOD_GSM_disk | D441
GSMUPS_MGE1DeviceVentilationFault_om | DIGITAL | IOD_GSM_disk | D442
GSMUPS_MGE1BatteryCompInProgress_om | DIGITAL | IOD_GSM_disk | D443
GSMUPS_MGE1BatteryTempOutOfToler_om | DIGITAL | IOD_GSM_disk | D444
GSMUPS_MGE1BatteryFuseFault_om | DIGITAL | IOD_GSM_disk | D445
GSMUPS_MGE1Mains1VoltOutOfToler_om | DIGITAL | IOD_GSM_disk | D446
GSMUPS_MGE1RectifierThermOverload_om | DIGITAL | IOD_GSM_disk | D447
GSMUPS_MGE1MaintenancePosition_om | DIGITAL | IOD_GSM_disk | D448
GSMUPS_MGE1ChargerGeneralFault_om | DIGITAL | IOD_GSM_disk | D449
GSMUPS_MGE1BatteryChargedState_om | DIGITAL | IOD_GSM_disk | D450
GSMUPS_MGE1InverterOverload_om | DIGITAL | IOD_GSM_disk | D451
GSMUPS_MGE1InverterThermalOverload_om | DIGITAL | IOD_GSM_disk | D452
GSMUPS_MGE1OutputThermalOverload_om | DIGITAL | IOD_GSM_disk | D453
GSMUPS_MGE1OutputOverload_om | DIGITAL | IOD_GSM_disk | D454
GSMUPS_MGE1InverterFuseFault_om | DIGITAL | IOD_GSM_disk | D455
GSMUPS_MGE1OutputInShortCircuit_om | DIGITAL | IOD_GSM_disk | D456
GSMNapakaSenzorVlagaHIA1_om | DIGITAL | IOD_GSM_disk | D457
GSMNapakaSenzorVlagaHIA2_om | DIGITAL | IOD_GSM_disk | D458
GSMNapakaSenzorVlagaHIA3_om | DIGITAL | IOD_GSM_disk | D459
GSMNapakaSenzorVlagaHIA4_om | DIGITAL | IOD_GSM_disk | D460
GSMNapakaSenzorVlagaHIA5_om | DIGITAL | IOD_GSM_disk | D461
GSMNapakaSenzorVlagaHIA6_om | DIGITAL | IOD_GSM_disk | D462
GSMNapakaSenzorVlagaHIA7_om | DIGITAL | IOD_GSM_disk | D463
GSMNapakaTSTempTIA1_om | DIGITAL | IOD_GSM_disk | D464
GSMNapakaTSTempTIA2_om | DIGITAL | IOD_GSM_disk | D465
GSMNapakaTSTempTIA3_om | DIGITAL | IOD_GSM_disk | D466
GSMNapakaTSTempTIA4_om | DIGITAL | IOD_GSM_disk | D467
GSMNapakaTSTempTIA5_om | DIGITAL | IOD_GSM_disk | D468
GSMNapakaTSTempTIA6_om | DIGITAL | IOD_GSM_disk | D469
GSMNapakaTSTempTIA7_om | DIGITAL | IOD_GSM_disk | D470
GSMTIA1_previs_temp_om | DIGITAL | IOD_GSM_disk | D471
GSMTIA2_previs_temp_om | DIGITAL | IOD_GSM_disk | D472
GSMTIA3_previs_temp_om | DIGITAL | IOD_GSM_disk | D473
GSMTIA4_previs_temp_om | DIGITAL | IOD_GSM_disk | D474
GSMTIA5_previs_temp_om | DIGITAL | IOD_GSM_disk | D475
GSMTIA6_previs_temp_om | DIGITAL | IOD_GSM_disk | D476
GSMTIA7_previs_temp_om | DIGITAL | IOD_GSM_disk | D477
GSMPMM2OverCurrentBetw_VirA_om | DIGITAL | IOD_GSM_disk | D478
GSMPMM2OverCurrentBetw_VirB_om | DIGITAL | IOD_GSM_disk | D479
GSMPMM2OverCurrentOver_VirA_om | DIGITAL | IOD_GSM_disk | D480
GSMPMM2OverCurrentOver_VirB_om | DIGITAL | IOD_GSM_disk | D481
GSMPMM2OverCurrentBetw_VirA | DIGITAL | IOD_GSM_disk | D482
GSMPMM2OverCurrentBetw_VirB | DIGITAL | IOD_GSM_disk | D483
GSMPMM2OverCurrentOver_VirA | DIGITAL | IOD_GSM_disk | D484
GSMPMM2OverCurrentOver_VirB | DIGITAL | IOD_GSM_disk | D485
GSMAlarmPMM1VirATokPrevisok_om | DIGITAL | IOD_GSM_disk | D486
GSMAlarmPMM1VirATokVisok_om | DIGITAL | IOD_GSM_disk | D487
GSMAlarmPMM1VirBTokPrevisok_om | DIGITAL | IOD_GSM_disk | D488
GSMAlarmPMM1VirBTokVisok_om | DIGITAL | IOD_GSM_disk | D489
GSMAlarmPMM2x17nad801_om | DIGITAL | IOD_GSM_disk | D490
GSMAlarmPMM2x17nad802_om | DIGITAL | IOD_GSM_disk | D491
GSMAlarmPMM2x17nad803_om | DIGITAL | IOD_GSM_disk | D492
GSMAlarmPMM2x17nad804_om | DIGITAL | IOD_GSM_disk | D493
GSMAlarmPMM2x17nad805_om | DIGITAL | IOD_GSM_disk | D494
GSMAlarmPMM2x17nad806_om | DIGITAL | IOD_GSM_disk | D495
GSMAlarmPMM2x17nad807_om | DIGITAL | IOD_GSM_disk | D496
GSMAlarmPMM2x17nad808_om | DIGITAL | IOD_GSM_disk | D497
GSMAlarmPMM2x17nad809_om | DIGITAL | IOD_GSM_disk | D498
GSMAlarmPMM2x17nad8010_om | DIGITAL | IOD_GSM_disk | D499
GSMAlarmPMM2x17nad8011_om | DIGITAL | IOD_GSM_disk | D500
GSMAlarmPMM2x17nad8012_om | DIGITAL | IOD_GSM_disk | D501
GSMAlarmPMM2x17nad8013_om | DIGITAL | IOD_GSM_disk | D502
GSMAlarmPMM2x17nad8014_om | DIGITAL | IOD_GSM_disk | D503
GSMAlarmPMM2x17nad8015_om | DIGITAL | IOD_GSM_disk | D504
GSMAlarmPMM2x17nad8016_om | DIGITAL | IOD_GSM_disk | D505
GSMAlarmPMM2x17nad8017_om | DIGITAL | IOD_GSM_disk | D506
GSMAlarmPMM2x17nad8018_om | DIGITAL | IOD_GSM_disk | D507
GSMAlarmPMM2x17nad8019_om | DIGITAL | IOD_GSM_disk | D508
GSMAlarmPMM2x17nad8020_om | DIGITAL | IOD_GSM_disk | D509
GSMAlarmPMM2x17nad8021_om | DIGITAL | IOD_GSM_disk | D510
GSMAlarmPMM2x17nad8022_om | DIGITAL | IOD_GSM_disk | D511
GSMAlarmPMM2x17nad8023_om | DIGITAL | IOD_GSM_disk | D512
GSMAlarmPMM2x17nad8024_om | DIGITAL | IOD_GSM_disk | D513
GSMAlarmPMM2x17nad8025_om | DIGITAL | IOD_GSM_disk | D514
GSMAlarmPMM2x17nad8026_om | DIGITAL | IOD_GSM_disk | D515
GSMAlarmPMM2x17nad8027_om | DIGITAL | IOD_GSM_disk | D516
GSMAlarmPMM2x17nad8028_om | DIGITAL | IOD_GSM_disk | D517
GSMOpozoriloPMM2x17med60in801_om | DIGITAL | IOD_GSM_disk | D518
GSMOpozoriloPMM2x17med60in802_om | DIGITAL | IOD_GSM_disk | D519
GSMOpozoriloPMM2x17med60in803_om | DIGITAL | IOD_GSM_disk | D520
GSMOpozoriloPMM2x17med60in804_om | DIGITAL | IOD_GSM_disk | D521
GSMOpozoriloPMM2x17med60in805_om | DIGITAL | IOD_GSM_disk | D522
GSMOpozoriloPMM2x17med60in806_om | DIGITAL | IOD_GSM_disk | D523
GSMOpozoriloPMM2x17med60in807_om | DIGITAL | IOD_GSM_disk | D524
GSMOpozoriloPMM2x17med60in808_om | DIGITAL | IOD_GSM_disk | D525
GSMOpozoriloPMM2x17med60in809_om | DIGITAL | IOD_GSM_disk | D526
GSMOpozoriloPMM2x17med60in8010_om | DIGITAL | IOD_GSM_disk | D527
GSMOpozoriloPMM2x17med60in8011_om | DIGITAL | IOD_GSM_disk | D528
GSMOpozoriloPMM2x17med60in8012_om | DIGITAL | IOD_GSM_disk | D529
GSMOpozoriloPMM2x17med60in8013_om | DIGITAL | IOD_GSM_disk | D530
GSMOpozoriloPMM2x17med60in8014_om | DIGITAL | IOD_GSM_disk | D531
GSMOpozoriloPMM2x17med60in8015_om | DIGITAL | IOD_GSM_disk | D532
GSMOpozoriloPMM2x17med60in8016_om | DIGITAL | IOD_GSM_disk | D533
GSMOpozoriloPMM2x17med60in8017_om | DIGITAL | IOD_GSM_disk | D534
GSMOpozoriloPMM2x17med60in8018_om | DIGITAL | IOD_GSM_disk | D535
GSMOpozoriloPMM2x17med60in8019_om | DIGITAL | IOD_GSM_disk | D536
GSMOpozoriloPMM2x17med60in8020_om | DIGITAL | IOD_GSM_disk | D537
GSMOpozoriloPMM2x17med60in8021_om | DIGITAL | IOD_GSM_disk | D538
GSMOpozoriloPMM2x17med60in8022_om | DIGITAL | IOD_GSM_disk | D539
GSMOpozoriloPMM2x17med60in8023_om | DIGITAL | IOD_GSM_disk | D540
GSMOpozoriloPMM2x17med60in8024_om | DIGITAL | IOD_GSM_disk | D541
GSMOpozoriloPMM2x17med60in8025_om | DIGITAL | IOD_GSM_disk | D542
GSMOpozoriloPMM2x17med60in8026_om | DIGITAL | IOD_GSM_disk | D543
GSMOpozoriloPMM2x17med60in8027_om | DIGITAL | IOD_GSM_disk | D544
GSMOpozoriloPMM2x17med60in8028_om | DIGITAL | IOD_GSM_disk | D545
GSMN_UPS_A_V23_delovanje_om | DIGITAL | IOD_GSM_disk | D546
GSMN_UPS_A_V23_napaka_om | DIGITAL | IOD_GSM_disk | D547
GSMUPS1Napaka_om | DIGITAL | IOD_GSM_disk | D548
AGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D600[300]
BGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D900[300]
CGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D1200[300]
DGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D1500[300]
EGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D1800[300]
FGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D2100[300]
GSM_Anali_razlika_dnevnaCirc1 | LONG | IOD_GSM_disk | L290
GSM_Anali_razlika_tedenCirc1 | LONG | IOD_GSM_disk | L292
GSM_Anali_razlika_mesCirc1 | LONG | IOD_GSM_disk | L294
GSMUserloggedIn_mem | DIGITAL | IOD_GSM_mem | D572
GSM_ComSCADA_stevec1 | INT | IOD_GSM_mem | I600
GSM_ComSCADA_stevec2 | INT | IOD_GSM_mem | I601
GSM_ComSCADA_stevec3 | INT | IOD_GSM_mem | I602
GSM_ComSCADA_stevec4 | INT | IOD_GSM_mem | I603
GSMKLIMAT1_vklop_delovanjaR | DIGITAL | IOD_GSM_TCP | 00409
GSMKLIMAT2_vklop_delovanjaR | DIGITAL | IOD_GSM_TCP | 00410
GSMKLIMAT1_R_zakleni | DIGITAL | IOD_GSM_TCP | 00411
GSMKLIMAT2_R_zakleni | DIGITAL | IOD_GSM_TCP | 00412
GSMK1_vklop_izklop_poteka | DIGITAL | IOD_GSM_TCP | 00413
GSMK2_vklop_izklop_poteka | DIGITAL | IOD_GSM_TCP | 00414
GSMPMMskupniTokA | REAL | IOD_GSM_TCP | 44615 | 0 | 230 | 0 | 230 | A | ####.#
GSMPMMskupniTokB | REAL | IOD_GSM_TCP | 44617 | 0 | 230 | 0 | 230 | A | ####.#
GSMUPS2Napaka_om | DIGITAL | IOD_GSM_disk | D549
GSMN_KlimeAVTO | DIGITAL | IOD_GSM_TCP | 00415
GSMK1_obr_u_skupno | UINT | IOD_GSM_TCP | 46022
GSMK2_obr_u_skupno | UINT | IOD_GSM_TCP | 46023
GSMUPS3AlarmAwaitingPower | DIGITAL | IOD_GSM_TCP | 00416
GSMUPS3AlarmBypassBad | DIGITAL | IOD_GSM_TCP | 00417
GSMUPS3AlarmChargerFailed | DIGITAL | IOD_GSM_TCP | 00418
GSMUPS3AlarmCommunicationsLost | DIGITAL | IOD_GSM_TCP | 00419
GSMUPS3AlarmDepletedBattery | DIGITAL | IOD_GSM_TCP | 00420
GSMUPS3AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM_TCP | 00421
GSMUPS3AlarmInverterError | DIGITAL | IOD_GSM_TCP | 00422
GSMUPS3AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 00423
GSMUPS3AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM_TCP | 00424
GSMUPS3AlarmLowBattery | DIGITAL | IOD_GSM_TCP | 00425
GSMUPS3AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM_TCP | 00426
GSMUPS3AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM_TCP | 00427
GSMUPS3AlarmOnBattery | DIGITAL | IOD_GSM_TCP | 00428
GSMUPS3AlarmOnBypass | DIGITAL | IOD_GSM_TCP | 00429
GSMUPS3AlarmShutdownImminent | DIGITAL | IOD_GSM_TCP | 00430
GSMUPS3AlarmShutdownPending | DIGITAL | IOD_GSM_TCP | 00431
GSMUPS3AlarmSlabaBaterija | DIGITAL | IOD_GSM_TCP | 00432
GSMUPS3AlarmSplosnaNapaka | DIGITAL | IOD_GSM_TCP | 00433
GSMUPS3AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00434
GSMUPS3AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00435
GSMUPS3AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00436
GSMUPS3AlarmTestInProgres | DIGITAL | IOD_GSM_TCP | 00437
GSMUPS3AlarmUPSIzhodOff | DIGITAL | IOD_GSM_TCP | 00438
GSMUPS3AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 00439
GSMUPS3AlarmUPSSystemOff | DIGITAL | IOD_GSM_TCP | 00440
GSMUPS3EstimatedChargeRemaining | REAL | IOD_GSM_TCP | 44619 | 0 | 100 | 0 | 100 | % | ###
GSMUPS3EstimatedMinutesRemaining | REAL | IOD_GSM_TCP | 44621 | 0 | 500 | 0 | 500 | min | ###
GSMUPS3InverterStatus | INT | IOD_GSM_TCP | 40255
GSMUPS3IzhodMocL1 | REAL | IOD_GSM_TCP | 44623 | 0 | 100 | 0 | 100 | % | ##.#
GSMUPS3IzhodMocL2 | REAL | IOD_GSM_TCP | 44625 | 0 | 100 | 0 | 100 | % | ##.#
GSMUPS3IzhodMocL3 | REAL | IOD_GSM_TCP | 44627 | 0 | 100 | 0 | 100 | % | ##.#
GSMUPS3Napaka | DIGITAL | IOD_GSM_TCP | 00441
GSMUPS3NapetostBaterije | REAL | IOD_GSM_TCP | 44629 | 0 | 600 | 0 | 600 | V | ###.#
GSMUPS3OutputStatus | INT | IOD_GSM_TCP | 40256
GSMUPS3StatusBaterije | UINT | IOD_GSM_TCP | 46024 | [5 empty] | ##
GSMUPS3StatusEcomodeAktiven | DIGITAL | IOD_GSM_TCP | 00442
GSMUPS3StatusInverterIsOn | DIGITAL | IOD_GSM_TCP | 00443
GSMUPS3StatusStopOperation | DIGITAL | IOD_GSM_TCP | 00444
GSMUPS3SteviloIzpadovVhodneLinije | INT | IOD_GSM_TCP | 40257 | [5 empty] | #####
GSMUPS3TemperaturaBaterije | REAL | IOD_GSM_TCP | 44631 | 0 | 100 | 0 | 100 | °C | ###
GSMUPS3UnitStatus | INT | IOD_GSM_TCP | 40258
GSMUPS3VhodFrekvencaL1 | REAL | IOD_GSM_TCP | 44633 | 0 | 60 | 0 | 60 | Hz | ##.#
GSMUPS3VhodFrekvencaL2 | REAL | IOD_GSM_TCP | 44635 | 0 | 60 | 0 | 60 | Hz | ##.#
GSMUPS3VhodFrekvencaL3 | REAL | IOD_GSM_TCP | 44637 | 0 | 60 | 0 | 60 | Hz | ##.#
GSMUPS3VhodNapetostL1 | REAL | IOD_GSM_TCP | 44639 | 0 | 500 | 0 | 500 | V | ###.#
GSMUPS3VhodNapetostL2 | REAL | IOD_GSM_TCP | 44641 | 0 | 500 | 0 | 500 | V | ###.#
GSMUPS3VhodNapetostL3 | REAL | IOD_GSM_TCP | 44643 | 0 | 500 | 0 | 500 | V | ###.#
GSMErrComUPS3 | DIGITAL | IOD_GSM_TCP | 00445
GSMUPS3AlarmSlabaBaterija_om | DIGITAL | IOD_GSM_disk | D2400
GSMUPS3AlarmOnBattery_om | DIGITAL | IOD_GSM_disk | D2401
GSMUPS3AlarmLowBattery_om | DIGITAL | IOD_GSM_disk | D2402
GSMUPS3AlarmDepletedBattery_om | DIGITAL | IOD_GSM_disk | D2403
GSMUPS3AlarmTemperaturaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D2404
GSMUPS3AlarmStanjeVhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D2405
GSMUPS3AlarmStanjeIzhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D2406
GSMUPS3AlarmIzhodPreobremenjen_om | DIGITAL | IOD_GSM_disk | D2407
GSMUPS3AlarmOnBypass_om | DIGITAL | IOD_GSM_disk | D2408
GSMUPS3AlarmBypassBad_om | DIGITAL | IOD_GSM_disk | D2409
GSMUPS3AlarmIzhodOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D2410
GSMUPS3AlarmUPSOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D2411
GSMUPS3AlarmChargerFailed_om | DIGITAL | IOD_GSM_disk | D2412
GSMUPS3AlarmUPSIzhodOff_om | DIGITAL | IOD_GSM_disk | D2413
GSMUPS3AlarmUPSSystemOff_om | DIGITAL | IOD_GSM_disk | D2414
GSMUPS3AlarmNapakaNaVentilatorju_om | DIGITAL | IOD_GSM_disk | D2415
GSMUPS3AlarmNapakaNaVarovalki_om | DIGITAL | IOD_GSM_disk | D2416
GSMUPS3AlarmSplosnaNapaka_om | DIGITAL | IOD_GSM_disk | D2417
GSMUPS3AlarmDiagnosticTestFailed_om | DIGITAL | IOD_GSM_disk | D2418
GSMUPS3AlarmCommunicationsLost_om | DIGITAL | IOD_GSM_disk | D2419
GSMUPS3AlarmAwaitingPower_om | DIGITAL | IOD_GSM_disk | D2420
GSMUPS3AlarmShutdownPending_om | DIGITAL | IOD_GSM_disk | D2421
GSMUPS3AlarmShutdownImminent_om | DIGITAL | IOD_GSM_disk | D2422
GSMUPS3AlarmTestInProgres_om | DIGITAL | IOD_GSM_disk | D2423
GSMUPS3AlarmInverterError_om | DIGITAL | IOD_GSM_disk | D2424
GSMUPS3Napaka_om | DIGITAL | IOD_GSM_disk | D2425
GSMGSM_PozCent_napaka | DIGITAL | IOD_GSM_TCP | 00446
GSMGSM_PozSenzor_okvara | DIGITAL | IOD_GSM_TCP | 00447
GSMGSM_Gasenje_alarm | DIGITAL | IOD_GSM_TCP | 00448
GSMAGR_PozCent_napaka | DIGITAL | IOD_GSM_TCP | 00449
GSMAGR_PozSenzor_okvara | DIGITAL | IOD_GSM_TCP | 00450
GSMAGR_Gasenje_alarm | DIGITAL | IOD_GSM_TCP | 00451
GSMGSM_PozCent_napaka_om | DIGITAL | IOD_GSM_disk | D2426
GSMGSM_PozSenzor_okvara_om | DIGITAL | IOD_GSM_disk | D2427
GSMGSM_Gasenje_alarm_om | DIGITAL | IOD_GSM_disk | D2428
GSMAGR_PozCent_napaka_om | DIGITAL | IOD_GSM_disk | D2429
GSMAGR_PozSenzor_okvara_om | DIGITAL | IOD_GSM_disk | D2430
GSMAGR_Gasenje_alarm_om | DIGITAL | IOD_GSM_disk | D2431
GSMCirc1MaximumDemandA2 | REAL | IOD_GSM_TCP | 44645 | 0 | 1200 | 0 | 1200 | A | ###.#
GSMCirc1MaximumDemandA3 | REAL | IOD_GSM_TCP | 44647 | 0 | 1200 | 0 | 1200 | A | ###.#
GSMCirc1RazEner_D_SCADA | REAL | IOD_GSM_TCP | 44649
GSMCirc1RazEner_T_SCADA | REAL | IOD_GSM_TCP | 44651
GSMCirc1RazEner_M_SCADA | REAL | IOD_GSM_TCP | 44653
GSMCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_GSM_TCP | 00452
GSMCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_GSM_TCP | 00453
GSMCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_GSM_TCP | 00454
GSMCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_GSM_TCP | 00455
GSMCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_GSM_TCP | 00456
GSMCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_GSM_TCP | 00457
GSMCirc_Vpis_Dnevne_energija_scada1_mem | DIGITAL | IOD_GSM_disk | D3000
GSMCirc_Vpis_Dnevne_energija_scada2_mem | DIGITAL | IOD_GSM_disk | D3001
GSMCirc_Vpis_Tedenska_energija_scada1_mem | DIGITAL | IOD_GSM_disk | D3002
GSMCirc_Vpis_Tedenska_energija_scada2_mem | DIGITAL | IOD_GSM_disk | D3003
GSMCirc_Vpis_Mesecna_energija_scada1_mem | DIGITAL | IOD_GSM_disk | D3004
GSMCirc_Vpis_Mesecna_energija_scada2_mem | DIGITAL | IOD_GSM_disk | D3005
GSMPozarnaCentrala_skupno | DIGITAL | IOD_GSM_TCP | 00458

## XSoft
mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Write_BOOL(FC) | mod_Write_Word(FC) | mod_Write_Word(FC) | mod_Write_dWord(FC) | mod_Write_dWord(FC) | mod_Write_String(FC)
(*Branje BOOL*) | (*Branje INT*) | (*Branje UINT*) | (*Branje LONG*) | (*Branje REAL*) | (*Branje STRING*) | (*Pisanje BOOL*) | (*Pisanje INT*) | (*Pisanje UINT*) | (*Pisanje LONG*) | (*Pisanje REAL*) | (*Pisanje STRING*)
(**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**)
mind_bool[0]:=AlarmGenUPS_A_V23; | mind[0]:=DateTime.Dan; | mind[6000]:=kom_nast_cas_izpada; |  | Read_Real(rVar:=Circ[1].CosFi_III,lo:=4000,hi:=4001); | Read_String(sVar:=Date_Time[0],start:=5000); | 0:AlarmGenUPS_A_V23:=Bit_0; | 0:DateTime.Dan:=Byte_0; | 6000:kom_nast_cas_izpada:=Word_01; |  | 4001:Circ[1].CosFi_III:=Real_0; | 5000:Date_Time[0]:=String_0;
mind_bool[1]:=AlarmGenUPS_V23; | mind[1]:=DateTime.Leto; | mind[6001]:=PMM[1].AlarmPhase[1].C01_16_60to80; |  | Read_Real(rVar:=Circ[1].DelovnaEnergija,lo:=4002,hi:=4003); | Read_String(sVar:=Date_Time[1],start:=5015); | 1:AlarmGenUPS_V23:=Bit_0; | 1:DateTime.Leto:=Byte_0; | 6001:PMM[1].AlarmPhase[1].C01_16_60to80:=Word_01; |  | 4003:Circ[1].DelovnaEnergija:=Real_0; | 5015:Date_Time[1]:=String_0;
mind_bool[2]:=AlarmGenUPS_V25; | mind[2]:=DateTime.Leto2; | mind[6002]:=PMM[1].AlarmPhase[1].C01_16_over80; |  | Read_Real(rVar:=Circ[1].DelovnaMoc_III,lo:=4004,hi:=4005); | Read_String(sVar:=Date_Time[2],start:=5030); | 2:AlarmGenUPS_V25:=Bit_0; | 2:DateTime.Leto2:=Word_01; | 6002:PMM[1].AlarmPhase[1].C01_16_over80:=Word_01; |  | 4005:Circ[1].DelovnaMoc_III:=Real_0; | 5030:Date_Time[2]:=String_0;
mind_bool[3]:=AlarmPMM1VirATokPrevisok; | mind[3]:=DateTime.Mesec; | mind[6003]:=PMM[1].AlarmPhase[1].C17_32_60to80; |  | Read_Real(rVar:=Circ[1].DelovnaMoc_L1,lo:=4006,hi:=4007); | Read_String(sVar:=Date_Time[3],start:=5045); | 3:AlarmPMM1VirATokPrevisok:=Bit_0; | 3:DateTime.Mesec:=Byte_0; | 6003:PMM[1].AlarmPhase[1].C17_32_60to80:=Word_01; |  | 4007:Circ[1].DelovnaMoc_L1:=Real_0; | 5045:Date_Time[3]:=String_0;
mind_bool[4]:=AlarmPMM1VirATokVisok; | mind[4]:=DateTime.Minuta; | mind[6004]:=PMM[1].AlarmPhase[1].C17_32_over80; |  | Read_Real(rVar:=Circ[1].DelovnaMoc_L2,lo:=4008,hi:=4009); | Read_String(sVar:=UserCurrentName,start:=5060); | 4:AlarmPMM1VirATokVisok:=Bit_0; | 4:DateTime.Minuta:=Byte_0; | 6004:PMM[1].AlarmPhase[1].C17_32_over80:=Word_01; |  | 4009:Circ[1].DelovnaMoc_L2:=Real_0; | 5060:UserCurrentName:=String_0;
mind_bool[5]:=AlarmPMM1VirBTokPrevisok; | mind[5]:=DateTime.Sekunda; | mind[6005]:=PMM[1].AlarmPhase[1].C33_42_60to80; |  | Read_Real(rVar:=Circ[1].DelovnaMoc_L3,lo:=4010,hi:=4011); |  | 5:AlarmPMM1VirBTokPrevisok:=Bit_0; | 5:DateTime.Sekunda:=Byte_0; | 6005:PMM[1].AlarmPhase[1].C33_42_60to80:=Word_01; |  | 4011:Circ[1].DelovnaMoc_L3:=Real_0;
mind_bool[6]:=AlarmPMM1VirBTokVisok; | mind[6]:=DateTime.Ura; | mind[6006]:=PMM[1].AlarmPhase[1].C33_42_over80; |  | Read_Real(rVar:=Circ[1].Frekvenca_L1,lo:=4012,hi:=4013); |  | 6:AlarmPMM1VirBTokVisok:=Bit_0; | 6:DateTime.Ura:=Byte_0; | 6006:PMM[1].AlarmPhase[1].C33_42_over80:=Word_01; |  | 4013:Circ[1].Frekvenca_L1:=Real_0;
mind_bool[7]:=AlarmPMM2x17nad80[10]; | mind[7]:=ErrorComCirc[1].Code[10]; | mind[6007]:=PMM[1].AlarmPhase[2].C01_16_60to80; |  | Read_Real(rVar:=Circ[1].InduktivnaEnergija,lo:=4014,hi:=4015); |  | 7:AlarmPMM2x17nad80[10]:=Bit_0; | 7:ErrorComCirc[1].Code[10]:=Byte_0; | 6007:PMM[1].AlarmPhase[2].C01_16_60to80:=Word_01; |  | 4015:Circ[1].InduktivnaEnergija:=Real_0;
mind_bool[8]:=AlarmPMM2x17nad80[11]; | mind[8]:=ErrorComCirc[1].Code[11]; | mind[6008]:=PMM[1].AlarmPhase[2].C01_16_over80; |  | Read_Real(rVar:=Circ[1].InduktivnaMoc_III,lo:=4016,hi:=4017); |  | 8:AlarmPMM2x17nad80[11]:=Bit_0; | 8:ErrorComCirc[1].Code[11]:=Byte_0; | 6008:PMM[1].AlarmPhase[2].C01_16_over80:=Word_01; |  | 4017:Circ[1].InduktivnaMoc_III:=Real_0;
mind_bool[9]:=AlarmPMM2x17nad80[12]; | mind[9]:=ErrorComCirc[1].Code[12]; | mind[6009]:=PMM[1].AlarmPhase[2].C17_32_60to80; |  | Read_Real(rVar:=Circ[1].JalovaMoc_L1,lo:=4018,hi:=4019); |  | 9:AlarmPMM2x17nad80[12]:=Bit_0; | 9:ErrorComCirc[1].Code[12]:=Byte_0; | 6009:PMM[1].AlarmPhase[2].C17_32_60to80:=Word_01; |  | 4019:Circ[1].JalovaMoc_L1:=Real_0;
mind_bool[10]:=AlarmPMM2x17nad80[13]; | mind[10]:=ErrorComCirc[1].Code[13]; | mind[6010]:=PMM[1].AlarmPhase[2].C17_32_over80; |  | Read_Real(rVar:=Circ[1].JalovaMoc_L2,lo:=4020,hi:=4021); |  | 10:AlarmPMM2x17nad80[13]:=Bit_0; | 10:ErrorComCirc[1].Code[13]:=Byte_0; | 6010:PMM[1].AlarmPhase[2].C17_32_over80:=Word_01; |  | 4021:Circ[1].JalovaMoc_L2:=Real_0;
mind_bool[11]:=AlarmPMM2x17nad80[14]; | mind[11]:=ErrorComCirc[1].Code[14]; | mind[6011]:=PMM[1].AlarmPhase[2].C33_42_60to80; |  | Read_Real(rVar:=Circ[1].JalovaMoc_L3,lo:=4022,hi:=4023); |  | 11:AlarmPMM2x17nad80[14]:=Bit_0; | 11:ErrorComCirc[1].Code[14]:=Byte_0; | 6011:PMM[1].AlarmPhase[2].C33_42_60to80:=Word_01; |  | 4023:Circ[1].JalovaMoc_L3:=Real_0;
mind_bool[12]:=AlarmPMM2x17nad80[15]; | mind[12]:=ErrorComCirc[1].Code[15]; | mind[6012]:=PMM[1].AlarmPhase[2].C33_42_over80; |  | Read_Real(rVar:=Circ[1].KapacitivnaEnergija,lo:=4024,hi:=4025); |  | 12:AlarmPMM2x17nad80[15]:=Bit_0; | 12:ErrorComCirc[1].Code[15]:=Byte_0; | 6012:PMM[1].AlarmPhase[2].C33_42_over80:=Word_01; |  | 4025:Circ[1].KapacitivnaEnergija:=Real_0;
mind_bool[13]:=AlarmPMM2x17nad80[16]; | mind[13]:=ErrorComCirc[1].Code[1]; | mind[6013]:=PMM[1].AlarmPhase[3].C01_16_60to80; |  | Read_Real(rVar:=Circ[1].KapacitivnaMoc_III,lo:=4026,hi:=4027); |  | 13:AlarmPMM2x17nad80[16]:=Bit_0; | 13:ErrorComCirc[1].Code[1]:=Byte_0; | 6013:PMM[1].AlarmPhase[3].C01_16_60to80:=Word_01; |  | 4027:Circ[1].KapacitivnaMoc_III:=Real_0;
mind_bool[14]:=AlarmPMM2x17nad80[17]; | mind[14]:=ErrorComCirc[1].Code[2]; | mind[6014]:=PMM[1].AlarmPhase[3].C01_16_over80; |  | Read_Real(rVar:=Circ[1].MaximumDemand,lo:=4028,hi:=4029); |  | 14:AlarmPMM2x17nad80[17]:=Bit_0; | 14:ErrorComCirc[1].Code[2]:=Byte_0; | 6014:PMM[1].AlarmPhase[3].C01_16_over80:=Word_01; |  | 4029:Circ[1].MaximumDemand:=Real_0;
mind_bool[15]:=AlarmPMM2x17nad80[18]; | mind[15]:=ErrorComCirc[1].Code[3]; | mind[6015]:=PMM[1].AlarmPhase[3].C17_32_60to80; |  | Read_Real(rVar:=Circ[1].Napetost_L1_L2,lo:=4030,hi:=4031); |  | 15:AlarmPMM2x17nad80[18]:=Bit_0; | 15:ErrorComCirc[1].Code[3]:=Byte_0; | 6015:PMM[1].AlarmPhase[3].C17_32_60to80:=Word_01; |  | 4031:Circ[1].Napetost_L1_L2:=Real_0;
mind_bool[16]:=AlarmPMM2x17nad80[19]; | mind[16]:=ErrorComCirc[1].Code[4]; | mind[6016]:=PMM[1].AlarmPhase[3].C17_32_over80; |  | Read_Real(rVar:=Circ[1].Napetost_L1_N,lo:=4032,hi:=4033); |  | 16:AlarmPMM2x17nad80[19]:=Bit_0; | 16:ErrorComCirc[1].Code[4]:=Byte_0; | 6016:PMM[1].AlarmPhase[3].C17_32_over80:=Word_01; |  | 4033:Circ[1].Napetost_L1_N:=Real_0;
mind_bool[17]:=AlarmPMM2x17nad80[1]; | mind[17]:=ErrorComCirc[1].Code[5]; | mind[6017]:=PMM[1].AlarmPhase[3].C33_42_60to80; |  | Read_Real(rVar:=Circ[1].Napetost_L2_L3,lo:=4034,hi:=4035); |  | 17:AlarmPMM2x17nad80[1]:=Bit_0; | 17:ErrorComCirc[1].Code[5]:=Byte_0; | 6017:PMM[1].AlarmPhase[3].C33_42_60to80:=Word_01; |  | 4035:Circ[1].Napetost_L2_L3:=Real_0;
mind_bool[18]:=AlarmPMM2x17nad80[20]; | mind[18]:=ErrorComCirc[1].Code[6]; | mind[6018]:=PMM[1].AlarmPhase[3].C33_42_over80; |  | Read_Real(rVar:=Circ[1].Napetost_L2_N,lo:=4036,hi:=4037); |  | 18:AlarmPMM2x17nad80[20]:=Bit_0; | 18:ErrorComCirc[1].Code[6]:=Byte_0; | 6018:PMM[1].AlarmPhase[3].C33_42_over80:=Word_01; |  | 4037:Circ[1].Napetost_L2_N:=Real_0;
mind_bool[19]:=AlarmPMM2x17nad80[21]; | mind[19]:=ErrorComCirc[1].Code[7]; | mind[6019]:=UPS[1].StatusBaterije; |  | Read_Real(rVar:=Circ[1].Napetost_L3_L1,lo:=4038,hi:=4039); |  | 19:AlarmPMM2x17nad80[21]:=Bit_0; | 19:ErrorComCirc[1].Code[7]:=Byte_0; | 6019:UPS[1].StatusBaterije:=Word_01; |  | 4039:Circ[1].Napetost_L3_L1:=Real_0;
mind_bool[20]:=AlarmPMM2x17nad80[22]; | mind[20]:=ErrorComCirc[1].Code[8]; | mind[6020]:=UPS[2].StatusBaterije; |  | Read_Real(rVar:=Circ[1].Napetost_L3_N,lo:=4040,hi:=4041); |  | 20:AlarmPMM2x17nad80[22]:=Bit_0; | 20:ErrorComCirc[1].Code[8]:=Byte_0; | 6020:UPS[2].StatusBaterije:=Word_01; |  | 4041:Circ[1].Napetost_L3_N:=Real_0;
mind_bool[21]:=AlarmPMM2x17nad80[23]; | mind[21]:=ErrorComCirc[1].Code[9]; | mind[6021]:=K1_obr_u_skupno; |  | Read_Real(rVar:=Circ[1].NavideznaMoc_III,lo:=4042,hi:=4043); |  | 21:AlarmPMM2x17nad80[23]:=Bit_0; | 21:ErrorComCirc[1].Code[9]:=Byte_0; | 6021:K1_obr_u_skupno:=Word_01; |  | 4043:Circ[1].NavideznaMoc_III:=Real_0;
mind_bool[22]:=AlarmPMM2x17nad80[24]; | mind[22]:=ErrorComCirc[1].Status; | mind[6022]:=K2_obr_u_skupno; |  | Read_Real(rVar:=Circ[1].NicelniTok,lo:=4044,hi:=4045); |  | 22:AlarmPMM2x17nad80[24]:=Bit_0; | 22:ErrorComCirc[1].Status:=Word_01; | 6022:K2_obr_u_skupno:=Word_01; |  | 4045:Circ[1].NicelniTok:=Real_0;
mind_bool[23]:=AlarmPMM2x17nad80[25]; | mind[23]:=ErrorComKlima[1].Code[10]; | mind[6023]:=UPS[3].StatusBaterije; |  | Read_Real(rVar:=Circ[1].PowerFactor_III,lo:=4046,hi:=4047); |  | 23:AlarmPMM2x17nad80[25]:=Bit_0; | 23:ErrorComKlima[1].Code[10]:=Byte_0; | 6023:UPS[3].StatusBaterije:=Word_01; |  | 4047:Circ[1].PowerFactor_III:=Real_0;
mind_bool[24]:=AlarmPMM2x17nad80[26]; | mind[24]:=ErrorComKlima[1].Code[11]; |  |  | Read_Real(rVar:=Circ[1].PowerFactor_L1,lo:=4048,hi:=4049); |  | 24:AlarmPMM2x17nad80[26]:=Bit_0; | 24:ErrorComKlima[1].Code[11]:=Byte_0; |  |  | 4049:Circ[1].PowerFactor_L1:=Real_0;
mind_bool[25]:=AlarmPMM2x17nad80[27]; | mind[25]:=ErrorComKlima[1].Code[12]; |  |  | Read_Real(rVar:=Circ[1].PowerFactor_L2,lo:=4050,hi:=4051); |  | 25:AlarmPMM2x17nad80[27]:=Bit_0; | 25:ErrorComKlima[1].Code[12]:=Byte_0; |  |  | 4051:Circ[1].PowerFactor_L2:=Real_0;
mind_bool[26]:=AlarmPMM2x17nad80[28]; | mind[26]:=ErrorComKlima[1].Code[13]; |  |  | Read_Real(rVar:=Circ[1].PowerFactor_L3,lo:=4052,hi:=4053); |  | 26:AlarmPMM2x17nad80[28]:=Bit_0; | 26:ErrorComKlima[1].Code[13]:=Byte_0; |  |  | 4053:Circ[1].PowerFactor_L3:=Real_0;
mind_bool[27]:=AlarmPMM2x17nad80[29]; | mind[27]:=ErrorComKlima[1].Code[14]; |  |  | Read_Real(rVar:=Circ[1].THDI_L1,lo:=4054,hi:=4055); |  | 27:AlarmPMM2x17nad80[29]:=Bit_0; | 27:ErrorComKlima[1].Code[14]:=Byte_0; |  |  | 4055:Circ[1].THDI_L1:=Real_0;
mind_bool[28]:=AlarmPMM2x17nad80[2]; | mind[28]:=ErrorComKlima[1].Code[15]; |  |  | Read_Real(rVar:=Circ[1].THDI_L2,lo:=4056,hi:=4057); |  | 28:AlarmPMM2x17nad80[2]:=Bit_0; | 28:ErrorComKlima[1].Code[15]:=Byte_0; |  |  | 4057:Circ[1].THDI_L2:=Real_0;
mind_bool[29]:=AlarmPMM2x17nad80[30]; | mind[29]:=ErrorComKlima[1].Code[1]; |  |  | Read_Real(rVar:=Circ[1].THDI_L3,lo:=4058,hi:=4059); |  | 29:AlarmPMM2x17nad80[30]:=Bit_0; | 29:ErrorComKlima[1].Code[1]:=Byte_0; |  |  | 4059:Circ[1].THDI_L3:=Real_0;
mind_bool[30]:=AlarmPMM2x17nad80[31]; | mind[30]:=ErrorComKlima[1].Code[2]; |  |  | Read_Real(rVar:=Circ[1].THDV_L1,lo:=4060,hi:=4061); |  | 30:AlarmPMM2x17nad80[31]:=Bit_0; | 30:ErrorComKlima[1].Code[2]:=Byte_0; |  |  | 4061:Circ[1].THDV_L1:=Real_0;
mind_bool[31]:=AlarmPMM2x17nad80[32]; | mind[31]:=ErrorComKlima[1].Code[3]; |  |  | Read_Real(rVar:=Circ[1].THDV_L2,lo:=4062,hi:=4063); |  | 31:AlarmPMM2x17nad80[32]:=Bit_0; | 31:ErrorComKlima[1].Code[3]:=Byte_0; |  |  | 4063:Circ[1].THDV_L2:=Real_0;
mind_bool[32]:=AlarmPMM2x17nad80[33]; | mind[32]:=ErrorComKlima[1].Code[4]; |  |  | Read_Real(rVar:=Circ[1].THDV_L3,lo:=4064,hi:=4065); |  | 32:AlarmPMM2x17nad80[33]:=Bit_0; | 32:ErrorComKlima[1].Code[4]:=Byte_0; |  |  | 4065:Circ[1].THDV_L3:=Real_0;
mind_bool[33]:=AlarmPMM2x17nad80[34]; | mind[33]:=ErrorComKlima[1].Code[5]; |  |  | Read_Real(rVar:=Circ[1].Tok_L1,lo:=4066,hi:=4067); |  | 33:AlarmPMM2x17nad80[34]:=Bit_0; | 33:ErrorComKlima[1].Code[5]:=Byte_0; |  |  | 4067:Circ[1].Tok_L1:=Real_0;
mind_bool[34]:=AlarmPMM2x17nad80[35]; | mind[34]:=ErrorComKlima[1].Code[6]; |  |  | Read_Real(rVar:=Circ[1].Tok_L2,lo:=4068,hi:=4069); |  | 34:AlarmPMM2x17nad80[35]:=Bit_0; | 34:ErrorComKlima[1].Code[6]:=Byte_0; |  |  | 4069:Circ[1].Tok_L2:=Real_0;
mind_bool[35]:=AlarmPMM2x17nad80[36]; | mind[35]:=ErrorComKlima[1].Code[7]; |  |  | Read_Real(rVar:=Circ[1].Tok_L3,lo:=4070,hi:=4071); |  | 35:AlarmPMM2x17nad80[36]:=Bit_0; | 35:ErrorComKlima[1].Code[7]:=Byte_0; |  |  | 4071:Circ[1].Tok_L3:=Real_0;
mind_bool[36]:=AlarmPMM2x17nad80[37]; | mind[36]:=ErrorComKlima[1].Code[8]; |  |  | Read_Real(rVar:=Circ[1].TokPovprecje_III,lo:=4072,hi:=4073); |  | 36:AlarmPMM2x17nad80[37]:=Bit_0; | 36:ErrorComKlima[1].Code[8]:=Byte_0; |  |  | 4073:Circ[1].TokPovprecje_III:=Real_0;
mind_bool[37]:=AlarmPMM2x17nad80[38]; | mind[37]:=ErrorComKlima[1].Code[9]; |  |  | Read_Real(rVar:=PMM[1].ActiveEnergyConsumed_kWh,lo:=4074,hi:=4075); |  | 37:AlarmPMM2x17nad80[38]:=Bit_0; | 37:ErrorComKlima[1].Code[9]:=Byte_0; |  |  | 4075:PMM[1].ActiveEnergyConsumed_kWh:=Real_0;
mind_bool[38]:=AlarmPMM2x17nad80[39]; | mind[38]:=ErrorComKlima[1].Status; |  |  | Read_Real(rVar:=PMM[1].ActivePowerPhaseA_kW,lo:=4076,hi:=4077); |  | 38:AlarmPMM2x17nad80[39]:=Bit_0; | 38:ErrorComKlima[1].Status:=Word_01; |  |  | 4077:PMM[1].ActivePowerPhaseA_kW:=Real_0;
mind_bool[39]:=AlarmPMM2x17nad80[3]; | mind[39]:=ErrorComKlima[2].Code[10]; |  |  | Read_Real(rVar:=PMM[1].ActivePowerPhaseB_kW,lo:=4078,hi:=4079); |  | 39:AlarmPMM2x17nad80[3]:=Bit_0; | 39:ErrorComKlima[2].Code[10]:=Byte_0; |  |  | 4079:PMM[1].ActivePowerPhaseB_kW:=Real_0;
mind_bool[40]:=AlarmPMM2x17nad80[40]; | mind[40]:=ErrorComKlima[2].Code[11]; |  |  | Read_Real(rVar:=PMM[1].ActivePowerPhaseC_kW,lo:=4080,hi:=4081); |  | 40:AlarmPMM2x17nad80[40]:=Bit_0; | 40:ErrorComKlima[2].Code[11]:=Byte_0; |  |  | 4081:PMM[1].ActivePowerPhaseC_kW:=Real_0;
mind_bool[41]:=AlarmPMM2x17nad80[41]; | mind[41]:=ErrorComKlima[2].Code[12]; |  |  | Read_Real(rVar:=PMM[1].AparentPowerPhaseA,lo:=4082,hi:=4083); |  | 41:AlarmPMM2x17nad80[41]:=Bit_0; | 41:ErrorComKlima[2].Code[12]:=Byte_0; |  |  | 4083:PMM[1].AparentPowerPhaseA:=Real_0;
mind_bool[42]:=AlarmPMM2x17nad80[42]; | mind[42]:=ErrorComKlima[2].Code[13]; |  |  | Read_Real(rVar:=PMM[1].AparentPowerPhaseB,lo:=4084,hi:=4085); |  | 42:AlarmPMM2x17nad80[42]:=Bit_0; | 42:ErrorComKlima[2].Code[13]:=Byte_0; |  |  | 4085:PMM[1].AparentPowerPhaseB:=Real_0;
mind_bool[43]:=AlarmPMM2x17nad80[4]; | mind[43]:=ErrorComKlima[2].Code[14]; |  |  | Read_Real(rVar:=PMM[1].AparentPowerPhaseC,lo:=4086,hi:=4087); |  | 43:AlarmPMM2x17nad80[4]:=Bit_0; | 43:ErrorComKlima[2].Code[14]:=Byte_0; |  |  | 4087:PMM[1].AparentPowerPhaseC:=Real_0;
mind_bool[44]:=AlarmPMM2x17nad80[5]; | mind[44]:=ErrorComKlima[2].Code[15]; |  |  | Read_Real(rVar:=PMM[1].AverageCurrent_A,lo:=4088,hi:=4089); |  | 44:AlarmPMM2x17nad80[5]:=Bit_0; | 44:ErrorComKlima[2].Code[15]:=Byte_0; |  |  | 4089:PMM[1].AverageCurrent_A:=Real_0;
mind_bool[45]:=AlarmPMM2x17nad80[6]; | mind[45]:=ErrorComKlima[2].Code[1]; |  |  | Read_Real(rVar:=PMM[1].AveragePhaseToNeutral_V,lo:=4090,hi:=4091); |  | 45:AlarmPMM2x17nad80[6]:=Bit_0; | 45:ErrorComKlima[2].Code[1]:=Byte_0; |  |  | 4091:PMM[1].AveragePhaseToNeutral_V:=Real_0;
mind_bool[46]:=AlarmPMM2x17nad80[7]; | mind[46]:=ErrorComKlima[2].Code[2]; |  |  | Read_Real(rVar:=PMM[1].AveragePhaseToPhase_V,lo:=4092,hi:=4093); |  | 46:AlarmPMM2x17nad80[7]:=Bit_0; | 46:ErrorComKlima[2].Code[2]:=Byte_0; |  |  | 4093:PMM[1].AveragePhaseToPhase_V:=Real_0;
mind_bool[47]:=AlarmPMM2x17nad80[8]; | mind[47]:=ErrorComKlima[2].Code[3]; |  |  | Read_Real(rVar:=PMM[1].CurrentInPhaseA_A,lo:=4094,hi:=4095); |  | 47:AlarmPMM2x17nad80[8]:=Bit_0; | 47:ErrorComKlima[2].Code[3]:=Byte_0; |  |  | 4095:PMM[1].CurrentInPhaseA_A:=Real_0;
mind_bool[48]:=AlarmPMM2x17nad80[9]; | mind[48]:=ErrorComKlima[2].Code[4]; |  |  | Read_Real(rVar:=PMM[1].CurrentInPhaseB_A,lo:=4096,hi:=4097); |  | 48:AlarmPMM2x17nad80[9]:=Bit_0; | 48:ErrorComKlima[2].Code[4]:=Byte_0; |  |  | 4097:PMM[1].CurrentInPhaseB_A:=Real_0;
mind_bool[49]:=ComError; | mind[49]:=ErrorComKlima[2].Code[5]; |  |  | Read_Real(rVar:=PMM[1].CurrentInPhaseC_A,lo:=4098,hi:=4099); |  | 49:ComError:=Bit_0; | 49:ErrorComKlima[2].Code[5]:=Byte_0; |  |  | 4099:PMM[1].CurrentInPhaseC_A:=Real_0;
mind_bool[50]:=ComSCADA; | mind[50]:=ErrorComKlima[2].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Frequency_Hz,lo:=4100,hi:=4101); |  | 50:ComSCADA:=Bit_0; | 50:ErrorComKlima[2].Code[6]:=Byte_0; |  |  | 4101:PMM[1].Frequency_Hz:=Real_0;
mind_bool[51]:=ComSCADA1; | mind[51]:=ErrorComKlima[2].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[10],lo:=4102,hi:=4103); |  | 51:ComSCADA1:=Bit_0; | 51:ErrorComKlima[2].Code[7]:=Byte_0; |  |  | 4103:PMM[1].Phase[1].Current[10]:=Real_0;
mind_bool[52]:=ComSCADA2; | mind[52]:=ErrorComKlima[2].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[11],lo:=4104,hi:=4105); |  | 52:ComSCADA2:=Bit_0; | 52:ErrorComKlima[2].Code[8]:=Byte_0; |  |  | 4105:PMM[1].Phase[1].Current[11]:=Real_0;
mind_bool[53]:=ComSCADA3; | mind[53]:=ErrorComKlima[2].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[12],lo:=4106,hi:=4107); |  | 53:ComSCADA3:=Bit_0; | 53:ErrorComKlima[2].Code[9]:=Byte_0; |  |  | 4107:PMM[1].Phase[1].Current[12]:=Real_0;
mind_bool[54]:=ErrComCirc[1]; | mind[54]:=ErrorComKlima[2].Status; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[13],lo:=4108,hi:=4109); |  | 54:ErrComCirc[1]:=Bit_0; | 54:ErrorComKlima[2].Status:=Word_01; |  |  | 4109:PMM[1].Phase[1].Current[13]:=Real_0;
mind_bool[55]:=ErrComKlima[1]; | mind[55]:=ErrorComPMM[1].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[14],lo:=4110,hi:=4111); |  | 55:ErrComKlima[1]:=Bit_0; | 55:ErrorComPMM[1].Code[10]:=Byte_0; |  |  | 4111:PMM[1].Phase[1].Current[14]:=Real_0;
mind_bool[56]:=ErrComKlima[2]; | mind[56]:=ErrorComPMM[1].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[15],lo:=4112,hi:=4113); |  | 56:ErrComKlima[2]:=Bit_0; | 56:ErrorComPMM[1].Code[11]:=Byte_0; |  |  | 4113:PMM[1].Phase[1].Current[15]:=Real_0;
mind_bool[57]:=ErrComPMM[1]; | mind[57]:=ErrorComPMM[1].Code[12]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[16],lo:=4114,hi:=4115); |  | 57:ErrComPMM[1]:=Bit_0; | 57:ErrorComPMM[1].Code[12]:=Byte_0; |  |  | 4115:PMM[1].Phase[1].Current[16]:=Real_0;
mind_bool[58]:=ErrComPort2; | mind[58]:=ErrorComPMM[1].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[17],lo:=4116,hi:=4117); |  | 58:ErrComPort2:=Bit_0; | 58:ErrorComPMM[1].Code[13]:=Byte_0; |  |  | 4117:PMM[1].Phase[1].Current[17]:=Real_0;
mind_bool[59]:=ErrComPort3; | mind[59]:=ErrorComPMM[1].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[18],lo:=4118,hi:=4119); |  | 59:ErrComPort3:=Bit_0; | 59:ErrorComPMM[1].Code[14]:=Byte_0; |  |  | 4119:PMM[1].Phase[1].Current[18]:=Real_0;
mind_bool[60]:=ErrComPort4; | mind[60]:=ErrorComPMM[1].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[19],lo:=4120,hi:=4121); |  | 60:ErrComPort4:=Bit_0; | 60:ErrorComPMM[1].Code[15]:=Byte_0; |  |  | 4121:PMM[1].Phase[1].Current[19]:=Real_0;
mind_bool[61]:=ErrComUPS[1]; | mind[61]:=ErrorComPMM[1].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[1],lo:=4122,hi:=4123); |  | 61:ErrComUPS[1]:=Bit_0; | 61:ErrorComPMM[1].Code[1]:=Byte_0; |  |  | 4123:PMM[1].Phase[1].Current[1]:=Real_0;
mind_bool[62]:=ErrComUPS[2]; | mind[62]:=ErrorComPMM[1].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[20],lo:=4124,hi:=4125); |  | 62:ErrComUPS[2]:=Bit_0; | 62:ErrorComPMM[1].Code[2]:=Byte_0; |  |  | 4125:PMM[1].Phase[1].Current[20]:=Real_0;
mind_bool[63]:=ErrComUPSMGE[1]; | mind[63]:=ErrorComPMM[1].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[21],lo:=4126,hi:=4127); |  | 63:ErrComUPSMGE[1]:=Bit_0; | 63:ErrorComPMM[1].Code[3]:=Byte_0; |  |  | 4127:PMM[1].Phase[1].Current[21]:=Real_0;
mind_bool[64]:=ErrorComCirc[1].Error; | mind[64]:=ErrorComPMM[1].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[22],lo:=4128,hi:=4129); |  | 64:ErrorComCirc[1].Error:=Bit_0; | 64:ErrorComPMM[1].Code[4]:=Byte_0; |  |  | 4129:PMM[1].Phase[1].Current[22]:=Real_0;
mind_bool[65]:=ErrorComKlima[1].Error; | mind[65]:=ErrorComPMM[1].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[23],lo:=4130,hi:=4131); |  | 65:ErrorComKlima[1].Error:=Bit_0; | 65:ErrorComPMM[1].Code[5]:=Byte_0; |  |  | 4131:PMM[1].Phase[1].Current[23]:=Real_0;
mind_bool[66]:=ErrorComKlima[2].Error; | mind[66]:=ErrorComPMM[1].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[24],lo:=4132,hi:=4133); |  | 66:ErrorComKlima[2].Error:=Bit_0; | 66:ErrorComPMM[1].Code[6]:=Byte_0; |  |  | 4133:PMM[1].Phase[1].Current[24]:=Real_0;
mind_bool[67]:=ErrorComPMM[1].Error; | mind[67]:=ErrorComPMM[1].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[25],lo:=4134,hi:=4135); |  | 67:ErrorComPMM[1].Error:=Bit_0; | 67:ErrorComPMM[1].Code[7]:=Byte_0; |  |  | 4135:PMM[1].Phase[1].Current[25]:=Real_0;
mind_bool[68]:=ErrorComUPS[1].Error; | mind[68]:=ErrorComPMM[1].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[26],lo:=4136,hi:=4137); |  | 68:ErrorComUPS[1].Error:=Bit_0; | 68:ErrorComPMM[1].Code[8]:=Byte_0; |  |  | 4137:PMM[1].Phase[1].Current[26]:=Real_0;
mind_bool[69]:=ErrorComUPS[2].Error; | mind[69]:=ErrorComPMM[1].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[27],lo:=4138,hi:=4139); |  | 69:ErrorComUPS[2].Error:=Bit_0; | 69:ErrorComPMM[1].Code[9]:=Byte_0; |  |  | 4139:PMM[1].Phase[1].Current[27]:=Real_0;
mind_bool[70]:=ErrorComUPSMGE[1].Error; | mind[70]:=ErrorComPMM[1].Status; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[28],lo:=4140,hi:=4141); |  | 70:ErrorComUPSMGE[1].Error:=Bit_0; | 70:ErrorComPMM[1].Status:=Word_01; |  |  | 4141:PMM[1].Phase[1].Current[28]:=Real_0;
mind_bool[71]:=F1_1_zascita_ok; | mind[71]:=ErrorComUPS[1].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[29],lo:=4142,hi:=4143); |  | 71:F1_1_zascita_ok:=Bit_0; | 71:ErrorComUPS[1].Code[10]:=Byte_0; |  |  | 4143:PMM[1].Phase[1].Current[29]:=Real_0;
mind_bool[72]:=K1_SkupnaNapaka; | mind[72]:=ErrorComUPS[1].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[2],lo:=4144,hi:=4145); |  | 72:K1_SkupnaNapaka:=Bit_0; | 72:ErrorComUPS[1].Code[11]:=Byte_0; |  |  | 4145:PMM[1].Phase[1].Current[2]:=Real_0;
mind_bool[73]:=K1AlarmPozara; | mind[73]:=ErrorComUPS[1].Code[12]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[30],lo:=4146,hi:=4147); |  | 73:K1AlarmPozara:=Bit_0; | 73:ErrorComUPS[1].Code[12]:=Byte_0; |  |  | 4147:PMM[1].Phase[1].Current[30]:=Real_0;
mind_bool[74]:=K1KlimaZdruzenAlarm; | mind[74]:=ErrorComUPS[1].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[31],lo:=4148,hi:=4149); |  | 74:K1KlimaZdruzenAlarm:=Bit_0; | 74:ErrorComUPS[1].Code[13]:=Byte_0; |  |  | 4149:PMM[1].Phase[1].Current[31]:=Real_0;
mind_bool[75]:=K1NiPretoka; | mind[75]:=ErrorComUPS[1].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[32],lo:=4150,hi:=4151); |  | 75:K1NiPretoka:=Bit_0; | 75:ErrorComUPS[1].Code[14]:=Byte_0; |  |  | 4151:PMM[1].Phase[1].Current[32]:=Real_0;
mind_bool[76]:=K1OkvaraRototerma; | mind[76]:=ErrorComUPS[1].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[33],lo:=4152,hi:=4153); |  | 76:K1OkvaraRototerma:=Bit_0; | 76:ErrorComUPS[1].Code[15]:=Byte_0; |  |  | 4153:PMM[1].Phase[1].Current[33]:=Real_0;
mind_bool[77]:=K1OkvaraVlazNap; | mind[77]:=ErrorComUPS[1].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[34],lo:=4154,hi:=4155); |  | 77:K1OkvaraVlazNap:=Bit_0; | 77:ErrorComUPS[1].Code[1]:=Byte_0; |  |  | 4155:PMM[1].Phase[1].Current[34]:=Real_0;
mind_bool[78]:=K1PreobMotCrpGr; | mind[78]:=ErrorComUPS[1].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[35],lo:=4156,hi:=4157); |  | 78:K1PreobMotCrpGr:=Bit_0; | 78:ErrorComUPS[1].Code[2]:=Byte_0; |  |  | 4157:PMM[1].Phase[1].Current[35]:=Real_0;
mind_bool[79]:=K1PreobMotVent; | mind[79]:=ErrorComUPS[1].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[36],lo:=4158,hi:=4159); |  | 79:K1PreobMotVent:=Bit_0; | 79:ErrorComUPS[1].Code[3]:=Byte_0; |  |  | 4159:PMM[1].Phase[1].Current[36]:=Real_0;
mind_bool[80]:=K1ProtizamrzZascAkt; | mind[80]:=ErrorComUPS[1].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[37],lo:=4160,hi:=4161); |  | 80:K1ProtizamrzZascAkt:=Bit_0; | 80:ErrorComUPS[1].Code[4]:=Byte_0; |  |  | 4161:PMM[1].Phase[1].Current[37]:=Real_0;
mind_bool[81]:=K1ZamasenostFiltra; | mind[81]:=ErrorComUPS[1].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[38],lo:=4162,hi:=4163); |  | 81:K1ZamasenostFiltra:=Bit_0; | 81:ErrorComUPS[1].Code[5]:=Byte_0; |  |  | 4163:PMM[1].Phase[1].Current[38]:=Real_0;
mind_bool[82]:=K2_SkupnaNapaka; | mind[82]:=ErrorComUPS[1].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[39],lo:=4164,hi:=4165); |  | 82:K2_SkupnaNapaka:=Bit_0; | 82:ErrorComUPS[1].Code[6]:=Byte_0; |  |  | 4165:PMM[1].Phase[1].Current[39]:=Real_0;
mind_bool[83]:=K2AlarmPozara; | mind[83]:=ErrorComUPS[1].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[3],lo:=4166,hi:=4167); |  | 83:K2AlarmPozara:=Bit_0; | 83:ErrorComUPS[1].Code[7]:=Byte_0; |  |  | 4167:PMM[1].Phase[1].Current[3]:=Real_0;
mind_bool[84]:=K2KlimaZdruzenAlarm; | mind[84]:=ErrorComUPS[1].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[40],lo:=4168,hi:=4169); |  | 84:K2KlimaZdruzenAlarm:=Bit_0; | 84:ErrorComUPS[1].Code[8]:=Byte_0; |  |  | 4169:PMM[1].Phase[1].Current[40]:=Real_0;
mind_bool[85]:=K2NiPretoka; | mind[85]:=ErrorComUPS[1].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[41],lo:=4170,hi:=4171); |  | 85:K2NiPretoka:=Bit_0; | 85:ErrorComUPS[1].Code[9]:=Byte_0; |  |  | 4171:PMM[1].Phase[1].Current[41]:=Real_0;
mind_bool[86]:=K2OkvaraRototerma; | mind[86]:=ErrorComUPS[1].Status; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[42],lo:=4172,hi:=4173); |  | 86:K2OkvaraRototerma:=Bit_0; | 86:ErrorComUPS[1].Status:=Word_01; |  |  | 4173:PMM[1].Phase[1].Current[42]:=Real_0;
mind_bool[87]:=K2OkvaraVlazNap; | mind[87]:=ErrorComUPS[2].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[4],lo:=4174,hi:=4175); |  | 87:K2OkvaraVlazNap:=Bit_0; | 87:ErrorComUPS[2].Code[10]:=Byte_0; |  |  | 4175:PMM[1].Phase[1].Current[4]:=Real_0;
mind_bool[88]:=K2PreobMotCrpGr; | mind[88]:=ErrorComUPS[2].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[5],lo:=4176,hi:=4177); |  | 88:K2PreobMotCrpGr:=Bit_0; | 88:ErrorComUPS[2].Code[11]:=Byte_0; |  |  | 4177:PMM[1].Phase[1].Current[5]:=Real_0;
mind_bool[89]:=K2PreobMotVent; | mind[89]:=ErrorComUPS[2].Code[12]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[6],lo:=4178,hi:=4179); |  | 89:K2PreobMotVent:=Bit_0; | 89:ErrorComUPS[2].Code[12]:=Byte_0; |  |  | 4179:PMM[1].Phase[1].Current[6]:=Real_0;
mind_bool[90]:=K2ProtizamrzZascAkt; | mind[90]:=ErrorComUPS[2].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[7],lo:=4180,hi:=4181); |  | 90:K2ProtizamrzZascAkt:=Bit_0; | 90:ErrorComUPS[2].Code[13]:=Byte_0; |  |  | 4181:PMM[1].Phase[1].Current[7]:=Real_0;
mind_bool[91]:=K2ZamasenostFiltra; | mind[91]:=ErrorComUPS[2].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[8],lo:=4182,hi:=4183); |  | 91:K2ZamasenostFiltra:=Bit_0; | 91:ErrorComUPS[2].Code[14]:=Byte_0; |  |  | 4183:PMM[1].Phase[1].Current[8]:=Real_0;
mind_bool[92]:=K3_deluje; | mind[92]:=ErrorComUPS[2].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[9],lo:=4184,hi:=4185); |  | 92:K3_deluje:=Bit_0; | 92:ErrorComUPS[2].Code[15]:=Byte_0; |  |  | 4185:PMM[1].Phase[1].Current[9]:=Real_0;
mind_bool[93]:=K3_SkupnaNapaka; | mind[93]:=ErrorComUPS[2].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[10],lo:=4186,hi:=4187); |  | 93:K3_SkupnaNapaka:=Bit_0; | 93:ErrorComUPS[2].Code[1]:=Byte_0; |  |  | 4187:PMM[1].Phase[2].Current[10]:=Real_0;
mind_bool[94]:=Klima1_izkljucena; | mind[94]:=ErrorComUPS[2].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[11],lo:=4188,hi:=4189); |  | 94:Klima1_izkljucena:=Bit_0; | 94:ErrorComUPS[2].Code[2]:=Byte_0; |  |  | 4189:PMM[1].Phase[2].Current[11]:=Real_0;
mind_bool[95]:=KLIMA1_kke_pogon; | mind[95]:=ErrorComUPS[2].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[12],lo:=4190,hi:=4191); |  | 95:KLIMA1_kke_pogon:=Bit_0; | 95:ErrorComUPS[2].Code[3]:=Byte_0; |  |  | 4191:PMM[1].Phase[2].Current[12]:=Real_0;
mind_bool[96]:=KLIMA1_krm_nap_ok; | mind[96]:=ErrorComUPS[2].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[13],lo:=4192,hi:=4193); |  | 96:KLIMA1_krm_nap_ok:=Bit_0; | 96:ErrorComUPS[2].Code[4]:=Byte_0; |  |  | 4193:PMM[1].Phase[2].Current[13]:=Real_0;
mind_bool[97]:=Klima2_izkljucena; | mind[97]:=ErrorComUPS[2].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[14],lo:=4194,hi:=4195); |  | 97:Klima2_izkljucena:=Bit_0; | 97:ErrorComUPS[2].Code[5]:=Byte_0; |  |  | 4195:PMM[1].Phase[2].Current[14]:=Real_0;
mind_bool[98]:=Klima3_izkljucena; | mind[98]:=ErrorComUPS[2].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[15],lo:=4196,hi:=4197); |  | 98:Klima3_izkljucena:=Bit_0; | 98:ErrorComUPS[2].Code[6]:=Byte_0; |  |  | 4197:PMM[1].Phase[2].Current[15]:=Real_0;
mind_bool[99]:=Klima[1].Alarm_pozar; | mind[99]:=ErrorComUPS[2].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[16],lo:=4198,hi:=4199); |  | 99:Klima[1].Alarm_pozar:=Bit_0; | 99:ErrorComUPS[2].Code[7]:=Byte_0; |  |  | 4199:PMM[1].Phase[2].Current[16]:=Real_0;
mind_bool[100]:=Klima[1].DelVentHit1; | mind[100]:=ErrorComUPS[2].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[17],lo:=4200,hi:=4201); |  | 100:Klima[1].DelVentHit1:=Bit_0; | 100:ErrorComUPS[2].Code[8]:=Byte_0; |  |  | 4201:PMM[1].Phase[2].Current[17]:=Real_0;
mind_bool[101]:=Klima[1].DelVentHit2; | mind[101]:=ErrorComUPS[2].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[18],lo:=4202,hi:=4203); |  | 101:Klima[1].DelVentHit2:=Bit_0; | 101:ErrorComUPS[2].Code[9]:=Byte_0; |  |  | 4203:PMM[1].Phase[2].Current[18]:=Real_0;
mind_bool[102]:=Klima[1].Ni_pretoka; | mind[102]:=ErrorComUPS[2].Status; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[19],lo:=4204,hi:=4205); |  | 102:Klima[1].Ni_pretoka:=Bit_0; | 102:ErrorComUPS[2].Status:=Word_01; |  |  | 4205:PMM[1].Phase[2].Current[19]:=Real_0;
mind_bool[103]:=Klima[1].OkvaraRototerm; | mind[103]:=ErrorComUPSMGE[1].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[1],lo:=4206,hi:=4207); |  | 103:Klima[1].OkvaraRototerm:=Bit_0; | 103:ErrorComUPSMGE[1].Code[10]:=Byte_0; |  |  | 4207:PMM[1].Phase[2].Current[1]:=Real_0;
mind_bool[104]:=Klima[1].OkvaraVlazNap; | mind[104]:=ErrorComUPSMGE[1].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[20],lo:=4208,hi:=4209); |  | 104:Klima[1].OkvaraVlazNap:=Bit_0; | 104:ErrorComUPSMGE[1].Code[11]:=Byte_0; |  |  | 4209:PMM[1].Phase[2].Current[20]:=Real_0;
mind_bool[105]:=Klima[1].PreobMotCrpGrel; | mind[105]:=ErrorComUPSMGE[1].Code[12]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[21],lo:=4210,hi:=4211); |  | 105:Klima[1].PreobMotCrpGrel:=Bit_0; | 105:ErrorComUPSMGE[1].Code[12]:=Byte_0; |  |  | 4211:PMM[1].Phase[2].Current[21]:=Real_0;
mind_bool[106]:=Klima[1].PreobMotVent; | mind[106]:=ErrorComUPSMGE[1].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[22],lo:=4212,hi:=4213); |  | 106:Klima[1].PreobMotVent:=Bit_0; | 106:ErrorComUPSMGE[1].Code[13]:=Byte_0; |  |  | 4213:PMM[1].Phase[2].Current[22]:=Real_0;
mind_bool[107]:=Klima[1].ProtizamrzZascAktivna; | mind[107]:=ErrorComUPSMGE[1].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[23],lo:=4214,hi:=4215); |  | 107:Klima[1].ProtizamrzZascAktivna:=Bit_0; | 107:ErrorComUPSMGE[1].Code[14]:=Byte_0; |  |  | 4215:PMM[1].Phase[2].Current[23]:=Real_0;
mind_bool[108]:=Klima[1].VklopRegKlimata; | mind[108]:=ErrorComUPSMGE[1].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[24],lo:=4216,hi:=4217); |  | 108:Klima[1].VklopRegKlimata:=Bit_0; | 108:ErrorComUPSMGE[1].Code[15]:=Byte_0; |  |  | 4217:PMM[1].Phase[2].Current[24]:=Real_0;
mind_bool[109]:=Klima[1].ZamasenostFiltra; | mind[109]:=ErrorComUPSMGE[1].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[25],lo:=4218,hi:=4219); |  | 109:Klima[1].ZamasenostFiltra:=Bit_0; | 109:ErrorComUPSMGE[1].Code[1]:=Byte_0; |  |  | 4219:PMM[1].Phase[2].Current[25]:=Real_0;
mind_bool[110]:=Klima[1].ZdruzAlarmA; | mind[110]:=ErrorComUPSMGE[1].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[26],lo:=4220,hi:=4221); |  | 110:Klima[1].ZdruzAlarmA:=Bit_0; | 110:ErrorComUPSMGE[1].Code[2]:=Byte_0; |  |  | 4221:PMM[1].Phase[2].Current[26]:=Real_0;
mind_bool[111]:=Klima[1].ZdruzAlarmB; | mind[111]:=ErrorComUPSMGE[1].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[27],lo:=4222,hi:=4223); |  | 111:Klima[1].ZdruzAlarmB:=Bit_0; | 111:ErrorComUPSMGE[1].Code[3]:=Byte_0; |  |  | 4223:PMM[1].Phase[2].Current[27]:=Real_0;
mind_bool[112]:=Klima[2].Alarm_pozar; | mind[112]:=ErrorComUPSMGE[1].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[28],lo:=4224,hi:=4225); |  | 112:Klima[2].Alarm_pozar:=Bit_0; | 112:ErrorComUPSMGE[1].Code[4]:=Byte_0; |  |  | 4225:PMM[1].Phase[2].Current[28]:=Real_0;
mind_bool[113]:=Klima[2].DelVentHit1; | mind[113]:=ErrorComUPSMGE[1].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[29],lo:=4226,hi:=4227); |  | 113:Klima[2].DelVentHit1:=Bit_0; | 113:ErrorComUPSMGE[1].Code[5]:=Byte_0; |  |  | 4227:PMM[1].Phase[2].Current[29]:=Real_0;
mind_bool[114]:=Klima[2].DelVentHit2; | mind[114]:=ErrorComUPSMGE[1].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[2],lo:=4228,hi:=4229); |  | 114:Klima[2].DelVentHit2:=Bit_0; | 114:ErrorComUPSMGE[1].Code[6]:=Byte_0; |  |  | 4229:PMM[1].Phase[2].Current[2]:=Real_0;
mind_bool[115]:=Klima[2].Ni_pretoka; | mind[115]:=ErrorComUPSMGE[1].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[30],lo:=4230,hi:=4231); |  | 115:Klima[2].Ni_pretoka:=Bit_0; | 115:ErrorComUPSMGE[1].Code[7]:=Byte_0; |  |  | 4231:PMM[1].Phase[2].Current[30]:=Real_0;
mind_bool[116]:=Klima[2].OkvaraRototerm; | mind[116]:=ErrorComUPSMGE[1].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[31],lo:=4232,hi:=4233); |  | 116:Klima[2].OkvaraRototerm:=Bit_0; | 116:ErrorComUPSMGE[1].Code[8]:=Byte_0; |  |  | 4233:PMM[1].Phase[2].Current[31]:=Real_0;
mind_bool[117]:=Klima[2].OkvaraVlazNap; | mind[117]:=ErrorComUPSMGE[1].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[32],lo:=4234,hi:=4235); |  | 117:Klima[2].OkvaraVlazNap:=Bit_0; | 117:ErrorComUPSMGE[1].Code[9]:=Byte_0; |  |  | 4235:PMM[1].Phase[2].Current[32]:=Real_0;
mind_bool[118]:=Klima[2].PreobMotCrpGrel; | mind[118]:=ErrorComUPSMGE[1].Status; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[33],lo:=4236,hi:=4237); |  | 118:Klima[2].PreobMotCrpGrel:=Bit_0; | 118:ErrorComUPSMGE[1].Status:=Word_01; |  |  | 4237:PMM[1].Phase[2].Current[33]:=Real_0;
mind_bool[119]:=Klima[2].PreobMotVent; | mind[119]:=HIA1_vlaga_s; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[34],lo:=4238,hi:=4239); |  | 119:Klima[2].PreobMotVent:=Bit_0; | 119:HIA1_vlaga_s:=Word_01; |  |  | 4239:PMM[1].Phase[2].Current[34]:=Real_0;
mind_bool[120]:=Klima[2].ProtizamrzZascAktivna; | mind[120]:=HIA2_vlaga_s; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[35],lo:=4240,hi:=4241); |  | 120:Klima[2].ProtizamrzZascAktivna:=Bit_0; | 120:HIA2_vlaga_s:=Word_01; |  |  | 4241:PMM[1].Phase[2].Current[35]:=Real_0;
mind_bool[121]:=Klima[2].VklopRegKlimata; | mind[121]:=HIA3_vlaga_s; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[36],lo:=4242,hi:=4243); |  | 121:Klima[2].VklopRegKlimata:=Bit_0; | 121:HIA3_vlaga_s:=Word_01; |  |  | 4243:PMM[1].Phase[2].Current[36]:=Real_0;
mind_bool[122]:=Klima[2].ZamasenostFiltra; | mind[122]:=HIA4_vlaga_s; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[37],lo:=4244,hi:=4245); |  | 122:Klima[2].ZamasenostFiltra:=Bit_0; | 122:HIA4_vlaga_s:=Word_01; |  |  | 4245:PMM[1].Phase[2].Current[37]:=Real_0;
mind_bool[123]:=Klima[2].ZdruzAlarmA; | mind[123]:=HIA5_vlaga_s; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[38],lo:=4246,hi:=4247); |  | 123:Klima[2].ZdruzAlarmA:=Bit_0; | 123:HIA5_vlaga_s:=Word_01; |  |  | 4247:PMM[1].Phase[2].Current[38]:=Real_0;
mind_bool[124]:=Klima[2].ZdruzAlarmB; | mind[124]:=HIA6_vlaga_s; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[39],lo:=4248,hi:=4249); |  | 124:Klima[2].ZdruzAlarmB:=Bit_0; | 124:HIA6_vlaga_s:=Word_01; |  |  | 4249:PMM[1].Phase[2].Current[39]:=Real_0;
mind_bool[125]:=KLIMA_m1_delovanje; | mind[125]:=HIA7_vlaga_s; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[3],lo:=4250,hi:=4251); |  | 125:KLIMA_m1_delovanje:=Bit_0; | 125:HIA7_vlaga_s:=Word_01; |  |  | 4251:PMM[1].Phase[2].Current[3]:=Real_0;
mind_bool[126]:=KLIMA_m1_napaka; | mind[126]:=Klima[1].Analog_izh_mesanje; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[40],lo:=4252,hi:=4253); |  | 126:KLIMA_m1_napaka:=Bit_0; | 126:Klima[1].Analog_izh_mesanje:=Word_01; |  |  | 4253:PMM[1].Phase[2].Current[40]:=Real_0;
mind_bool[127]:=KLIMA_m2_delovanje; | mind[127]:=Klima[1].Analog_izh_rekuperator; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[41],lo:=4254,hi:=4255); |  | 127:KLIMA_m2_delovanje:=Bit_0; | 127:Klima[1].Analog_izh_rekuperator:=Word_01; |  |  | 4255:PMM[1].Phase[2].Current[41]:=Real_0;
mind_bool[128]:=KLIMA_m2_napaka; | mind[128]:=Klima[1].Analog_izh_VentGrelnika; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[42],lo:=4256,hi:=4257); |  | 128:KLIMA_m2_napaka:=Bit_0; | 128:Klima[1].Analog_izh_VentGrelnika:=Word_01; |  |  | 4257:PMM[1].Phase[2].Current[42]:=Real_0;
mind_bool[129]:=KLIMAT1_delovanje; | mind[129]:=Klima[1].Analog_izh_VentHlajenja; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[4],lo:=4258,hi:=4259); |  | 129:KLIMAT1_delovanje:=Bit_0; | 129:Klima[1].Analog_izh_VentHlajenja:=Word_01; |  |  | 4259:PMM[1].Phase[2].Current[4]:=Real_0;
mind_bool[130]:=KLIMAT1_napaka; | mind[130]:=Klima[1].Dejanska_zel_temp; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[5],lo:=4260,hi:=4261); |  | 130:KLIMAT1_napaka:=Bit_0; | 130:Klima[1].Dejanska_zel_temp:=Word_01; |  |  | 4261:PMM[1].Phase[2].Current[5]:=Real_0;
mind_bool[131]:=KLIMAT1_vklop_delovanja; | mind[131]:=Klima[1].Hitrost_del_vent_disp; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[6],lo:=4262,hi:=4263); |  | 131:KLIMAT1_vklop_delovanja:=Bit_0; | 131:Klima[1].Hitrost_del_vent_disp:=Word_01; |  |  | 4263:PMM[1].Phase[2].Current[6]:=Real_0;
mind_bool[132]:=KLIMAT2_delovanje; | mind[132]:=Klima[1].Max_vpih; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[7],lo:=4264,hi:=4265); |  | 132:KLIMAT2_delovanje:=Bit_0; | 132:Klima[1].Max_vpih:=Word_01; |  |  | 4265:PMM[1].Phase[2].Current[7]:=Real_0;
mind_bool[133]:=KLIMAT2_napaka; | mind[133]:=Klima[1].Min_vpih; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[8],lo:=4266,hi:=4267); |  | 133:KLIMAT2_napaka:=Bit_0; | 133:Klima[1].Min_vpih:=Word_01; |  |  | 4267:PMM[1].Phase[2].Current[8]:=Real_0;
mind_bool[134]:=KLIMAT2_vklop_delovanja; | mind[134]:=Klima[1].Obrat_ure_Vent_h1; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[9],lo:=4268,hi:=4269); |  | 134:KLIMAT2_vklop_delovanja:=Bit_0; | 134:Klima[1].Obrat_ure_Vent_h1:=Word_01; |  |  | 4269:PMM[1].Phase[2].Current[9]:=Real_0;
mind_bool[135]:=KlimeAVTO; | mind[135]:=Klima[1].Obrat_ure_Vent_h2; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[10],lo:=4270,hi:=4271); |  | 135:KlimeAVTO:=Bit_0; | 135:Klima[1].Obrat_ure_Vent_h2:=Word_01; |  |  | 4271:PMM[1].Phase[3].Current[10]:=Real_0;
mind_bool[136]:=N_F1_1_zascita_ok; | mind[136]:=Klima[1].Pol_komp_konec; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[11],lo:=4272,hi:=4273); |  | 136:N_F1_1_zascita_ok:=Bit_0; | 136:Klima[1].Pol_komp_konec:=Word_01; |  |  | 4273:PMM[1].Phase[3].Current[11]:=Real_0;
mind_bool[137]:=N_KLIMA1_krm_nap_ok; | mind[137]:=Klima[1].Pol_komp_sprem_zel_vr; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[12],lo:=4274,hi:=4275); |  | 137:N_KLIMA1_krm_nap_ok:=Bit_0; | 137:Klima[1].Pol_komp_sprem_zel_vr:=Word_01; |  |  | 4275:PMM[1].Phase[3].Current[12]:=Real_0;
mind_bool[138]:=N_KLIMAT1_napaka; | mind[138]:=Klima[1].Pol_komp_zacetek; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[13],lo:=4276,hi:=4277); |  | 138:N_KLIMAT1_napaka:=Bit_0; | 138:Klima[1].Pol_komp_zacetek:=Word_01; |  |  | 4277:PMM[1].Phase[3].Current[13]:=Real_0;
mind_bool[139]:=N_KLIMAT2_napaka; | mind[139]:=Klima[1].PreklopHitDelVent; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[14],lo:=4278,hi:=4279); |  | 139:N_KLIMAT2_napaka:=Bit_0; | 139:Klima[1].PreklopHitDelVent:=Word_01; |  |  | 4279:PMM[1].Phase[3].Current[14]:=Real_0;
mind_bool[140]:=N_Q12_izpad; | mind[140]:=Klima[1].Protizamrz_zascita; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[15],lo:=4280,hi:=4281); |  | 140:N_Q12_izpad:=Bit_0; | 140:Klima[1].Protizamrz_zascita:=Word_01; |  |  | 4281:PMM[1].Phase[3].Current[15]:=Real_0;
mind_bool[141]:=N_UPS_A_V23_delovanje; | mind[141]:=Klima[1].Rezim_delovanja; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[16],lo:=4282,hi:=4283); |  | 141:N_UPS_A_V23_delovanje:=Bit_0; | 141:Klima[1].Rezim_delovanja:=Word_01; |  |  | 4283:PMM[1].Phase[3].Current[16]:=Real_0;
mind_bool[142]:=N_UPS_A_V23_napaka; | mind[142]:=Klima[1].Temperatura_dovoda; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[17],lo:=4284,hi:=4285); |  | 142:N_UPS_A_V23_napaka:=Bit_0; | 142:Klima[1].Temperatura_dovoda:=Word_01; |  |  | 4285:PMM[1].Phase[3].Current[17]:=Real_0;
mind_bool[143]:=N_UPS_V23_delovanje; | mind[143]:=Klima[1].Temperatura_prostora; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[18],lo:=4286,hi:=4287); |  | 143:N_UPS_V23_delovanje:=Bit_0; | 143:Klima[1].Temperatura_prostora:=Word_01; |  |  | 4287:PMM[1].Phase[3].Current[18]:=Real_0;
mind_bool[144]:=N_UPS_V23_napaka; | mind[144]:=Klima[1].TempPredPloscnimRekup; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[19],lo:=4288,hi:=4289); |  | 144:N_UPS_V23_napaka:=Bit_0; | 144:Klima[1].TempPredPloscnimRekup:=Word_01; |  |  | 4289:PMM[1].Phase[3].Current[19]:=Real_0;
mind_bool[145]:=N_UPS_V25_delovanje; | mind[145]:=Klima[1].TempZaPloscnimRekup; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[1],lo:=4290,hi:=4291); |  | 145:N_UPS_V25_delovanje:=Bit_0; | 145:Klima[1].TempZaPloscnimRekup:=Word_01; |  |  | 4291:PMM[1].Phase[3].Current[1]:=Real_0;
mind_bool[146]:=N_UPS_V25_napaka; | mind[146]:=Klima[1].Vlaga_v_prostoru; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[20],lo:=4292,hi:=4293); |  | 146:N_UPS_V25_napaka:=Bit_0; | 146:Klima[1].Vlaga_v_prostoru:=Word_01; |  |  | 4293:PMM[1].Phase[3].Current[20]:=Real_0;
mind_bool[147]:=N_VLAZILEC1_napaka; | mind[147]:=Klima[1].VlagaVstopZrakaProstor; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[21],lo:=4294,hi:=4295); |  | 147:N_VLAZILEC1_napaka:=Bit_0; | 147:Klima[1].VlagaVstopZrakaProstor:=Word_01; |  |  | 4295:PMM[1].Phase[3].Current[21]:=Real_0;
mind_bool[148]:=N_VLAZILEC2_napaka; | mind[148]:=Klima[1].Zel_temp_eko_gretja; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[22],lo:=4296,hi:=4297); |  | 148:N_VLAZILEC2_napaka:=Bit_0; | 148:Klima[1].Zel_temp_eko_gretja:=Word_01; |  |  | 4297:PMM[1].Phase[3].Current[22]:=Real_0;
mind_bool[149]:=napaka_kom_panel; | mind[149]:=Klima[1].Zel_temp_eko_hlajenja; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[23],lo:=4298,hi:=4299); |  | 149:napaka_kom_panel:=Bit_0; | 149:Klima[1].Zel_temp_eko_hlajenja:=Word_01; |  |  | 4299:PMM[1].Phase[3].Current[23]:=Real_0;
mind_bool[150]:=napaka_kom_scada; | mind[150]:=Klima[1].Zel_temp_komf_gretja; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[24],lo:=4300,hi:=4301); |  | 150:napaka_kom_scada:=Bit_0; | 150:Klima[1].Zel_temp_komf_gretja:=Word_01; |  |  | 4301:PMM[1].Phase[3].Current[24]:=Real_0;
mind_bool[151]:=napaka_kom_scada2; | mind[151]:=Klima[1].Zel_temp_komf_hlajenja; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[25],lo:=4302,hi:=4303); |  | 151:napaka_kom_scada2:=Bit_0; | 151:Klima[1].Zel_temp_komf_hlajenja:=Word_01; |  |  | 4303:PMM[1].Phase[3].Current[25]:=Real_0;
mind_bool[152]:=NapakaSenzorSkupno; | mind[152]:=Klima[1].Zim_komp_konec; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[26],lo:=4304,hi:=4305); |  | 152:NapakaSenzorSkupno:=Bit_0; | 152:Klima[1].Zim_komp_konec:=Word_01; |  |  | 4305:PMM[1].Phase[3].Current[26]:=Real_0;
mind_bool[153]:=NapakaSenzorVlagaHIA1; | mind[153]:=Klima[1].Zim_komp_sprem_zel_vr; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[27],lo:=4306,hi:=4307); |  | 153:NapakaSenzorVlagaHIA1:=Bit_0; | 153:Klima[1].Zim_komp_sprem_zel_vr:=Word_01; |  |  | 4307:PMM[1].Phase[3].Current[27]:=Real_0;
mind_bool[154]:=NapakaSenzorVlagaHIA2; | mind[154]:=Klima[1].Zim_komp_zacetek; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[28],lo:=4308,hi:=4309); |  | 154:NapakaSenzorVlagaHIA2:=Bit_0; | 154:Klima[1].Zim_komp_zacetek:=Word_01; |  |  | 4309:PMM[1].Phase[3].Current[28]:=Real_0;
mind_bool[155]:=NapakaSenzorVlagaHIA3; | mind[155]:=Klima[1].ZimKompMinVpihKonec; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[29],lo:=4310,hi:=4311); |  | 155:NapakaSenzorVlagaHIA3:=Bit_0; | 155:Klima[1].ZimKompMinVpihKonec:=Word_01; |  |  | 4311:PMM[1].Phase[3].Current[29]:=Real_0;
mind_bool[156]:=NapakaSenzorVlagaHIA4; | mind[156]:=Klima[1].ZimKompMinVpihZac; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[2],lo:=4312,hi:=4313); |  | 156:NapakaSenzorVlagaHIA4:=Bit_0; | 156:Klima[1].ZimKompMinVpihZac:=Word_01; |  |  | 4313:PMM[1].Phase[3].Current[2]:=Real_0;
mind_bool[157]:=NapakaSenzorVlagaHIA5; | mind[157]:=Klima[1].ZkompMinVpihSpremZelVr; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[30],lo:=4314,hi:=4315); |  | 157:NapakaSenzorVlagaHIA5:=Bit_0; | 157:Klima[1].ZkompMinVpihSpremZelVr:=Word_01; |  |  | 4315:PMM[1].Phase[3].Current[30]:=Real_0;
mind_bool[158]:=NapakaSenzorVlagaHIA6; | mind[158]:=Klima[1].Zunanja_temp; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[31],lo:=4316,hi:=4317); |  | 158:NapakaSenzorVlagaHIA6:=Bit_0; | 158:Klima[1].Zunanja_temp:=Word_01; |  |  | 4317:PMM[1].Phase[3].Current[31]:=Real_0;
mind_bool[159]:=NapakaSenzorVlagaHIA7; | mind[159]:=Klima[2].Analog_izh_mesanje; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[32],lo:=4318,hi:=4319); |  | 159:NapakaSenzorVlagaHIA7:=Bit_0; | 159:Klima[2].Analog_izh_mesanje:=Word_01; |  |  | 4319:PMM[1].Phase[3].Current[32]:=Real_0;
mind_bool[160]:=NapakaTSTempTIA1; | mind[160]:=Klima[2].Analog_izh_rekuperator; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[33],lo:=4320,hi:=4321); |  | 160:NapakaTSTempTIA1:=Bit_0; | 160:Klima[2].Analog_izh_rekuperator:=Word_01; |  |  | 4321:PMM[1].Phase[3].Current[33]:=Real_0;
mind_bool[161]:=NapakaTSTempTIA2; | mind[161]:=Klima[2].Analog_izh_VentGrelnika; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[34],lo:=4322,hi:=4323); |  | 161:NapakaTSTempTIA2:=Bit_0; | 161:Klima[2].Analog_izh_VentGrelnika:=Word_01; |  |  | 4323:PMM[1].Phase[3].Current[34]:=Real_0;
mind_bool[162]:=NapakaTSTempTIA3; | mind[162]:=Klima[2].Analog_izh_VentHlajenja; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[35],lo:=4324,hi:=4325); |  | 162:NapakaTSTempTIA3:=Bit_0; | 162:Klima[2].Analog_izh_VentHlajenja:=Word_01; |  |  | 4325:PMM[1].Phase[3].Current[35]:=Real_0;
mind_bool[163]:=NapakaTSTempTIA4; | mind[163]:=Klima[2].Dejanska_zel_temp; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[36],lo:=4326,hi:=4327); |  | 163:NapakaTSTempTIA4:=Bit_0; | 163:Klima[2].Dejanska_zel_temp:=Word_01; |  |  | 4327:PMM[1].Phase[3].Current[36]:=Real_0;
mind_bool[164]:=NapakaTSTempTIA5; | mind[164]:=Klima[2].Hitrost_del_vent_disp; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[37],lo:=4328,hi:=4329); |  | 164:NapakaTSTempTIA5:=Bit_0; | 164:Klima[2].Hitrost_del_vent_disp:=Word_01; |  |  | 4329:PMM[1].Phase[3].Current[37]:=Real_0;
mind_bool[165]:=NapakaTSTempTIA6; | mind[165]:=Klima[2].Max_vpih; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[38],lo:=4330,hi:=4331); |  | 165:NapakaTSTempTIA6:=Bit_0; | 165:Klima[2].Max_vpih:=Word_01; |  |  | 4331:PMM[1].Phase[3].Current[38]:=Real_0;
mind_bool[166]:=NapakaTSTempTIA7; | mind[166]:=Klima[2].Min_vpih; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[39],lo:=4332,hi:=4333); |  | 166:NapakaTSTempTIA7:=Bit_0; | 166:Klima[2].Min_vpih:=Word_01; |  |  | 4333:PMM[1].Phase[3].Current[39]:=Real_0;
mind_bool[167]:=OpozoriloPMM2x17med60in80[10]; | mind[167]:=Klima[2].Obrat_ure_Vent_h1; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[3],lo:=4334,hi:=4335); |  | 167:OpozoriloPMM2x17med60in80[10]:=Bit_0; | 167:Klima[2].Obrat_ure_Vent_h1:=Word_01; |  |  | 4335:PMM[1].Phase[3].Current[3]:=Real_0;
mind_bool[168]:=OpozoriloPMM2x17med60in80[11]; | mind[168]:=Klima[2].Obrat_ure_Vent_h2; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[40],lo:=4336,hi:=4337); |  | 168:OpozoriloPMM2x17med60in80[11]:=Bit_0; | 168:Klima[2].Obrat_ure_Vent_h2:=Word_01; |  |  | 4337:PMM[1].Phase[3].Current[40]:=Real_0;
mind_bool[169]:=OpozoriloPMM2x17med60in80[12]; | mind[169]:=Klima[2].Pol_komp_konec; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[41],lo:=4338,hi:=4339); |  | 169:OpozoriloPMM2x17med60in80[12]:=Bit_0; | 169:Klima[2].Pol_komp_konec:=Word_01; |  |  | 4339:PMM[1].Phase[3].Current[41]:=Real_0;
mind_bool[170]:=OpozoriloPMM2x17med60in80[13]; | mind[170]:=Klima[2].Pol_komp_sprem_zel_vr; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[42],lo:=4340,hi:=4341); |  | 170:OpozoriloPMM2x17med60in80[13]:=Bit_0; | 170:Klima[2].Pol_komp_sprem_zel_vr:=Word_01; |  |  | 4341:PMM[1].Phase[3].Current[42]:=Real_0;
mind_bool[171]:=OpozoriloPMM2x17med60in80[14]; | mind[171]:=Klima[2].Pol_komp_zacetek; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[4],lo:=4342,hi:=4343); |  | 171:OpozoriloPMM2x17med60in80[14]:=Bit_0; | 171:Klima[2].Pol_komp_zacetek:=Word_01; |  |  | 4343:PMM[1].Phase[3].Current[4]:=Real_0;
mind_bool[172]:=OpozoriloPMM2x17med60in80[15]; | mind[172]:=Klima[2].PreklopHitDelVent; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[5],lo:=4344,hi:=4345); |  | 172:OpozoriloPMM2x17med60in80[15]:=Bit_0; | 172:Klima[2].PreklopHitDelVent:=Word_01; |  |  | 4345:PMM[1].Phase[3].Current[5]:=Real_0;
mind_bool[173]:=OpozoriloPMM2x17med60in80[16]; | mind[173]:=Klima[2].Protizamrz_zascita; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[6],lo:=4346,hi:=4347); |  | 173:OpozoriloPMM2x17med60in80[16]:=Bit_0; | 173:Klima[2].Protizamrz_zascita:=Word_01; |  |  | 4347:PMM[1].Phase[3].Current[6]:=Real_0;
mind_bool[174]:=OpozoriloPMM2x17med60in80[17]; | mind[174]:=Klima[2].Rezim_delovanja; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[7],lo:=4348,hi:=4349); |  | 174:OpozoriloPMM2x17med60in80[17]:=Bit_0; | 174:Klima[2].Rezim_delovanja:=Word_01; |  |  | 4349:PMM[1].Phase[3].Current[7]:=Real_0;
mind_bool[175]:=OpozoriloPMM2x17med60in80[18]; | mind[175]:=Klima[2].Temperatura_dovoda; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[8],lo:=4350,hi:=4351); |  | 175:OpozoriloPMM2x17med60in80[18]:=Bit_0; | 175:Klima[2].Temperatura_dovoda:=Word_01; |  |  | 4351:PMM[1].Phase[3].Current[8]:=Real_0;
mind_bool[176]:=OpozoriloPMM2x17med60in80[19]; | mind[176]:=Klima[2].Temperatura_prostora; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[9],lo:=4352,hi:=4353); |  | 176:OpozoriloPMM2x17med60in80[19]:=Bit_0; | 176:Klima[2].Temperatura_prostora:=Word_01; |  |  | 4353:PMM[1].Phase[3].Current[9]:=Real_0;
mind_bool[177]:=OpozoriloPMM2x17med60in80[1]; | mind[177]:=Klima[2].TempPredPloscnimRekup; |  |  | Read_Real(rVar:=PMM[1].PowerFactorSys,lo:=4354,hi:=4355); |  | 177:OpozoriloPMM2x17med60in80[1]:=Bit_0; | 177:Klima[2].TempPredPloscnimRekup:=Word_01; |  |  | 4355:PMM[1].PowerFactorSys:=Real_0;
mind_bool[178]:=OpozoriloPMM2x17med60in80[20]; | mind[178]:=Klima[2].TempZaPloscnimRekup; |  |  | Read_Real(rVar:=PMM[1].ReactiveEnergyConsumed_kVARh,lo:=4356,hi:=4357); |  | 178:OpozoriloPMM2x17med60in80[20]:=Bit_0; | 178:Klima[2].TempZaPloscnimRekup:=Word_01; |  |  | 4357:PMM[1].ReactiveEnergyConsumed_kVARh:=Real_0;
mind_bool[179]:=OpozoriloPMM2x17med60in80[21]; | mind[179]:=Klima[2].Vlaga_v_prostoru; |  |  | Read_Real(rVar:=PMM[1].ReactivePowerPhaseA,lo:=4358,hi:=4359); |  | 179:OpozoriloPMM2x17med60in80[21]:=Bit_0; | 179:Klima[2].Vlaga_v_prostoru:=Word_01; |  |  | 4359:PMM[1].ReactivePowerPhaseA:=Real_0;
mind_bool[180]:=OpozoriloPMM2x17med60in80[22]; | mind[180]:=Klima[2].VlagaVstopZrakaProstor; |  |  | Read_Real(rVar:=PMM[1].ReactivePowerPhaseB,lo:=4360,hi:=4361); |  | 180:OpozoriloPMM2x17med60in80[22]:=Bit_0; | 180:Klima[2].VlagaVstopZrakaProstor:=Word_01; |  |  | 4361:PMM[1].ReactivePowerPhaseB:=Real_0;
mind_bool[181]:=OpozoriloPMM2x17med60in80[23]; | mind[181]:=Klima[2].Zel_temp_eko_gretja; |  |  | Read_Real(rVar:=PMM[1].ReactivePowerPhaseC,lo:=4362,hi:=4363); |  | 181:OpozoriloPMM2x17med60in80[23]:=Bit_0; | 181:Klima[2].Zel_temp_eko_gretja:=Word_01; |  |  | 4363:PMM[1].ReactivePowerPhaseC:=Real_0;
mind_bool[182]:=OpozoriloPMM2x17med60in80[24]; | mind[182]:=Klima[2].Zel_temp_eko_hlajenja; |  |  | Read_Real(rVar:=PMM[1].TotalActivePower_kW,lo:=4364,hi:=4365); |  | 182:OpozoriloPMM2x17med60in80[24]:=Bit_0; | 182:Klima[2].Zel_temp_eko_hlajenja:=Word_01; |  |  | 4365:PMM[1].TotalActivePower_kW:=Real_0;
mind_bool[183]:=OpozoriloPMM2x17med60in80[25]; | mind[183]:=Klima[2].Zel_temp_komf_gretja; |  |  | Read_Real(rVar:=PMM[1].TotalAparentPower_kVA,lo:=4366,hi:=4367); |  | 183:OpozoriloPMM2x17med60in80[25]:=Bit_0; | 183:Klima[2].Zel_temp_komf_gretja:=Word_01; |  |  | 4367:PMM[1].TotalAparentPower_kVA:=Real_0;
mind_bool[184]:=OpozoriloPMM2x17med60in80[26]; | mind[184]:=Klima[2].Zel_temp_komf_hlajenja; |  |  | Read_Real(rVar:=PMM[1].TotalPowerFactor,lo:=4368,hi:=4369); |  | 184:OpozoriloPMM2x17med60in80[26]:=Bit_0; | 184:Klima[2].Zel_temp_komf_hlajenja:=Word_01; |  |  | 4369:PMM[1].TotalPowerFactor:=Real_0;
mind_bool[185]:=OpozoriloPMM2x17med60in80[27]; | mind[185]:=Klima[2].Zim_komp_konec; |  |  | Read_Real(rVar:=PMM[1].TotalReactivePower_kVAR,lo:=4370,hi:=4371); |  | 185:OpozoriloPMM2x17med60in80[27]:=Bit_0; | 185:Klima[2].Zim_komp_konec:=Word_01; |  |  | 4371:PMM[1].TotalReactivePower_kVAR:=Real_0;
mind_bool[186]:=OpozoriloPMM2x17med60in80[28]; | mind[186]:=Klima[2].Zim_komp_sprem_zel_vr; |  |  | Read_Real(rVar:=PMM[1].VirA_fsys,lo:=4372,hi:=4373); |  | 186:OpozoriloPMM2x17med60in80[28]:=Bit_0; | 186:Klima[2].Zim_komp_sprem_zel_vr:=Word_01; |  |  | 4373:PMM[1].VirA_fsys:=Real_0;
mind_bool[187]:=OpozoriloPMM2x17med60in80[29]; | mind[187]:=Klima[2].Zim_komp_zacetek; |  |  | Read_Real(rVar:=PMM[1].VirA_Isys,lo:=4374,hi:=4375); |  | 187:OpozoriloPMM2x17med60in80[29]:=Bit_0; | 187:Klima[2].Zim_komp_zacetek:=Word_01; |  |  | 4375:PMM[1].VirA_Isys:=Real_0;
mind_bool[188]:=OpozoriloPMM2x17med60in80[2]; | mind[188]:=Klima[2].ZimKompMinVpihKonec; |  |  | Read_Real(rVar:=PMM[1].VirA_PFsys,lo:=4376,hi:=4377); |  | 188:OpozoriloPMM2x17med60in80[2]:=Bit_0; | 188:Klima[2].ZimKompMinVpihKonec:=Word_01; |  |  | 4377:PMM[1].VirA_PFsys:=Real_0;
mind_bool[189]:=OpozoriloPMM2x17med60in80[30]; | mind[189]:=Klima[2].ZimKompMinVpihZac; |  |  | Read_Real(rVar:=PMM[1].VirA_Psys,lo:=4378,hi:=4379); |  | 189:OpozoriloPMM2x17med60in80[30]:=Bit_0; | 189:Klima[2].ZimKompMinVpihZac:=Word_01; |  |  | 4379:PMM[1].VirA_Psys:=Real_0;
mind_bool[190]:=OpozoriloPMM2x17med60in80[31]; | mind[190]:=Klima[2].ZkompMinVpihSpremZelVr; |  |  | Read_Real(rVar:=PMM[1].VirA_Qsys,lo:=4380,hi:=4381); |  | 190:OpozoriloPMM2x17med60in80[31]:=Bit_0; | 190:Klima[2].ZkompMinVpihSpremZelVr:=Word_01; |  |  | 4381:PMM[1].VirA_Qsys:=Real_0;
mind_bool[191]:=OpozoriloPMM2x17med60in80[32]; | mind[191]:=Klima[2].Zunanja_temp; |  |  | Read_Real(rVar:=PMM[1].VirA_Ssys,lo:=4382,hi:=4383); |  | 191:OpozoriloPMM2x17med60in80[32]:=Bit_0; | 191:Klima[2].Zunanja_temp:=Word_01; |  |  | 4383:PMM[1].VirA_Ssys:=Real_0;
mind_bool[192]:=OpozoriloPMM2x17med60in80[33]; | mind[192]:=KlimaIzklopObrUre; |  |  | Read_Real(rVar:=PMM[1].VirA_Usys,lo:=4384,hi:=4385); |  | 192:OpozoriloPMM2x17med60in80[33]:=Bit_0; | 192:KlimaIzklopObrUre:=Word_01; |  |  | 4385:PMM[1].VirA_Usys:=Real_0;
mind_bool[193]:=OpozoriloPMM2x17med60in80[34]; | mind[193]:=PMM[1].AlarmPhase[1].GlobalAlarmReg; |  |  | Read_Real(rVar:=PMM[1].VirB_fsys,lo:=4386,hi:=4387); |  | 193:OpozoriloPMM2x17med60in80[34]:=Bit_0; | 193:PMM[1].AlarmPhase[1].GlobalAlarmReg:=Word_01; |  |  | 4387:PMM[1].VirB_fsys:=Real_0;
mind_bool[194]:=OpozoriloPMM2x17med60in80[35]; | mind[194]:=PMM[1].AlarmPhase[2].GlobalAlarmReg; |  |  | Read_Real(rVar:=PMM[1].VirB_Isys,lo:=4388,hi:=4389); |  | 194:OpozoriloPMM2x17med60in80[35]:=Bit_0; | 194:PMM[1].AlarmPhase[2].GlobalAlarmReg:=Word_01; |  |  | 4389:PMM[1].VirB_Isys:=Real_0;
mind_bool[195]:=OpozoriloPMM2x17med60in80[36]; | mind[195]:=PMM[1].AlarmPhase[3].GlobalAlarmReg; |  |  | Read_Real(rVar:=PMM[1].VirB_PFsys,lo:=4390,hi:=4391); |  | 195:OpozoriloPMM2x17med60in80[36]:=Bit_0; | 195:PMM[1].AlarmPhase[3].GlobalAlarmReg:=Word_01; |  |  | 4391:PMM[1].VirB_PFsys:=Real_0;
mind_bool[196]:=OpozoriloPMM2x17med60in80[37]; | mind[196]:=Q12stanje; |  |  | Read_Real(rVar:=PMM[1].VirB_Psys,lo:=4392,hi:=4393); |  | 196:OpozoriloPMM2x17med60in80[37]:=Bit_0; | 196:Q12stanje:=Byte_0; |  |  | 4393:PMM[1].VirB_Psys:=Real_0;
mind_bool[197]:=OpozoriloPMM2x17med60in80[38]; | mind[197]:=TempHistereza; |  |  | Read_Real(rVar:=PMM[1].VirB_Qsys,lo:=4394,hi:=4395); |  | 197:OpozoriloPMM2x17med60in80[38]:=Bit_0; | 197:TempHistereza:=Word_01; |  |  | 4395:PMM[1].VirB_Qsys:=Real_0;
mind_bool[198]:=OpozoriloPMM2x17med60in80[39]; | mind[198]:=TempPovp234; |  |  | Read_Real(rVar:=PMM[1].VirB_Ssys,lo:=4396,hi:=4397); |  | 198:OpozoriloPMM2x17med60in80[39]:=Bit_0; | 198:TempPovp234:=Word_01; |  |  | 4397:PMM[1].VirB_Ssys:=Real_0;
mind_bool[199]:=OpozoriloPMM2x17med60in80[3]; | mind[199]:=TempPovp234Alarm; |  |  | Read_Real(rVar:=PMM[1].VirB_Usys,lo:=4398,hi:=4399); |  | 199:OpozoriloPMM2x17med60in80[3]:=Bit_0; | 199:TempPovp234Alarm:=Word_01; |  |  | 4399:PMM[1].VirB_Usys:=Real_0;
mind_bool[200]:=OpozoriloPMM2x17med60in80[40]; | mind[200]:=TempPovp56; |  |  | Read_Real(rVar:=PMM[1].VirBActiveEnergyConsumed_kWh,lo:=4400,hi:=4401); |  | 200:OpozoriloPMM2x17med60in80[40]:=Bit_0; | 200:TempPovp56:=Word_01; |  |  | 4401:PMM[1].VirBActiveEnergyConsumed_kWh:=Real_0;
mind_bool[201]:=OpozoriloPMM2x17med60in80[41]; | mind[201]:=TempPovp56Alarm; |  |  | Read_Real(rVar:=PMM[1].VirBActivePowerPhaseA_kW,lo:=4402,hi:=4403); |  | 201:OpozoriloPMM2x17med60in80[41]:=Bit_0; | 201:TempPovp56Alarm:=Word_01; |  |  | 4403:PMM[1].VirBActivePowerPhaseA_kW:=Real_0;
mind_bool[202]:=OpozoriloPMM2x17med60in80[42]; | mind[202]:=TempZaVklopKlim1; |  |  | Read_Real(rVar:=PMM[1].VirBActivePowerPhaseB_kW,lo:=4404,hi:=4405); |  | 202:OpozoriloPMM2x17med60in80[42]:=Bit_0; | 202:TempZaVklopKlim1:=Word_01; |  |  | 4405:PMM[1].VirBActivePowerPhaseB_kW:=Real_0;
mind_bool[203]:=OpozoriloPMM2x17med60in80[4]; | mind[203]:=TempZaVklopKlim2; |  |  | Read_Real(rVar:=PMM[1].VirBActivePowerPhaseC_kW,lo:=4406,hi:=4407); |  | 203:OpozoriloPMM2x17med60in80[4]:=Bit_0; | 203:TempZaVklopKlim2:=Word_01; |  |  | 4407:PMM[1].VirBActivePowerPhaseC_kW:=Real_0;
mind_bool[204]:=OpozoriloPMM2x17med60in80[5]; | mind[204]:=TIA1_alarm; |  |  | Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseA,lo:=4408,hi:=4409); |  | 204:OpozoriloPMM2x17med60in80[5]:=Bit_0; | 204:TIA1_alarm:=Word_01; |  |  | 4409:PMM[1].VirBAparentPowerPhaseA:=Real_0;
mind_bool[205]:=OpozoriloPMM2x17med60in80[6]; | mind[205]:=TIA1_temp_s; |  |  | Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseB,lo:=4410,hi:=4411); |  | 205:OpozoriloPMM2x17med60in80[6]:=Bit_0; | 205:TIA1_temp_s:=Word_01; |  |  | 4411:PMM[1].VirBAparentPowerPhaseB:=Real_0;
mind_bool[206]:=OpozoriloPMM2x17med60in80[7]; | mind[206]:=TIA2_alarm; |  |  | Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseC,lo:=4412,hi:=4413); |  | 206:OpozoriloPMM2x17med60in80[7]:=Bit_0; | 206:TIA2_alarm:=Word_01; |  |  | 4413:PMM[1].VirBAparentPowerPhaseC:=Real_0;
mind_bool[207]:=OpozoriloPMM2x17med60in80[8]; | mind[207]:=TIA2_temp_s; |  |  | Read_Real(rVar:=PMM[1].VirBAverageCurrent_A,lo:=4414,hi:=4415); |  | 207:OpozoriloPMM2x17med60in80[8]:=Bit_0; | 207:TIA2_temp_s:=Word_01; |  |  | 4415:PMM[1].VirBAverageCurrent_A:=Real_0;
mind_bool[208]:=OpozoriloPMM2x17med60in80[9]; | mind[208]:=TIA3_alarm; |  |  | Read_Real(rVar:=PMM[1].VirBAveragePhaseToNeutral_V,lo:=4416,hi:=4417); |  | 208:OpozoriloPMM2x17med60in80[9]:=Bit_0; | 208:TIA3_alarm:=Word_01; |  |  | 4417:PMM[1].VirBAveragePhaseToNeutral_V:=Real_0;
mind_bool[209]:=PMM1OverCurrentBetw[1]; | mind[209]:=TIA3_temp_s; |  |  | Read_Real(rVar:=PMM[1].VirBAveragePhaseToPhase_V,lo:=4418,hi:=4419); |  | 209:PMM1OverCurrentBetw[1]:=Bit_0; | 209:TIA3_temp_s:=Word_01; |  |  | 4419:PMM[1].VirBAveragePhaseToPhase_V:=Real_0;
mind_bool[210]:=PMM1OverCurrentBetw[2]; | mind[210]:=TIA4_alarm; |  |  | Read_Real(rVar:=PMM[1].VirBCurrentInPhaseA_A,lo:=4420,hi:=4421); |  | 210:PMM1OverCurrentBetw[2]:=Bit_0; | 210:TIA4_alarm:=Word_01; |  |  | 4421:PMM[1].VirBCurrentInPhaseA_A:=Real_0;
mind_bool[211]:=PMM1OverCurrentBetw[3]; | mind[211]:=TIA4_temp_s; |  |  | Read_Real(rVar:=PMM[1].VirBCurrentInPhaseB_A,lo:=4422,hi:=4423); |  | 211:PMM1OverCurrentBetw[3]:=Bit_0; | 211:TIA4_temp_s:=Word_01; |  |  | 4423:PMM[1].VirBCurrentInPhaseB_A:=Real_0;
mind_bool[212]:=PMM1OverCurrentOver[1]; | mind[212]:=TIA5_alarm; |  |  | Read_Real(rVar:=PMM[1].VirBCurrentInPhaseC_A,lo:=4424,hi:=4425); |  | 212:PMM1OverCurrentOver[1]:=Bit_0; | 212:TIA5_alarm:=Word_01; |  |  | 4425:PMM[1].VirBCurrentInPhaseC_A:=Real_0;
mind_bool[213]:=PMM1OverCurrentOver[2]; | mind[213]:=TIA5_temp_s; |  |  | Read_Real(rVar:=PMM[1].VirBFrequency_Hz,lo:=4426,hi:=4427); |  | 213:PMM1OverCurrentOver[2]:=Bit_0; | 213:TIA5_temp_s:=Word_01; |  |  | 4427:PMM[1].VirBFrequency_Hz:=Real_0;
mind_bool[214]:=PMM1OverCurrentOver[3]; | mind[214]:=TIA6_alarm; |  |  | Read_Real(rVar:=PMM[1].VirBPowerFactorSys,lo:=4428,hi:=4429); |  | 214:PMM1OverCurrentOver[3]:=Bit_0; | 214:TIA6_alarm:=Word_01; |  |  | 4429:PMM[1].VirBPowerFactorSys:=Real_0;
mind_bool[215]:=PrevisokaTemp; | mind[215]:=TIA6_temp_s; |  |  | Read_Real(rVar:=PMM[1].VirBReactiveEnergyConsumed_kVARh,lo:=4430,hi:=4431); |  | 215:PrevisokaTemp:=Bit_0; | 215:TIA6_temp_s:=Word_01; |  |  | 4431:PMM[1].VirBReactiveEnergyConsumed_kVARh:=Real_0;
mind_bool[216]:=Q0_izkljuceno; | mind[216]:=TIA7_alarm; |  |  | Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseA,lo:=4432,hi:=4433); |  | 216:Q0_izkljuceno:=Bit_0; | 216:TIA7_alarm:=Word_01; |  |  | 4433:PMM[1].VirBReactivePowerPhaseA:=Real_0;
mind_bool[217]:=Q0_vkljuceno; | mind[217]:=TIA7_temp_s; |  |  | Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseB,lo:=4434,hi:=4435); |  | 217:Q0_vkljuceno:=Bit_0; | 217:TIA7_temp_s:=Word_01; |  |  | 4435:PMM[1].VirBReactivePowerPhaseB:=Real_0;
mind_bool[218]:=Q12_izkljuceno; | mind[218]:=UPS[1].InverterStatus; |  |  | Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseC,lo:=4436,hi:=4437); |  | 218:Q12_izkljuceno:=Bit_0; | 218:UPS[1].InverterStatus:=Word_01; |  |  | 4437:PMM[1].VirBReactivePowerPhaseC:=Real_0;
mind_bool[219]:=Q12_izpad; | mind[219]:=UPS[1].OutputStatus; |  |  | Read_Real(rVar:=PMM[1].VirBTotalActivePower_kW,lo:=4438,hi:=4439); |  | 219:Q12_izpad:=Bit_0; | 219:UPS[1].OutputStatus:=Word_01; |  |  | 4439:PMM[1].VirBTotalActivePower_kW:=Real_0;
mind_bool[220]:=Q12_vkljuceno; | mind[220]:=UPS[1].SteviloIzpadovVhodneLinije; |  |  | Read_Real(rVar:=PMM[1].VirBTotalAparentPower_kVA,lo:=4440,hi:=4441); |  | 220:Q12_vkljuceno:=Bit_0; | 220:UPS[1].SteviloIzpadovVhodneLinije:=Word_01; |  |  | 4441:PMM[1].VirBTotalAparentPower_kVA:=Real_0;
mind_bool[221]:=razlitjeLAH1; | mind[221]:=UPS[1].UnitStatus; |  |  | Read_Real(rVar:=PMM[1].VirBTotalPowerFactor,lo:=4442,hi:=4443); |  | 221:razlitjeLAH1:=Bit_0; | 221:UPS[1].UnitStatus:=Word_01; |  |  | 4443:PMM[1].VirBTotalPowerFactor:=Real_0;
mind_bool[222]:=razlitjeLAH2; | mind[222]:=UPS[2].InverterStatus; |  |  | Read_Real(rVar:=PMM[1].VirBTotalReactivePower_kVAR,lo:=4444,hi:=4445); |  | 222:razlitjeLAH2:=Bit_0; | 222:UPS[2].InverterStatus:=Word_01; |  |  | 4445:PMM[1].VirBTotalReactivePower_kVAR:=Real_0;
mind_bool[223]:=razlitjeLAH3; | mind[223]:=UPS[2].OutputStatus; |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseAB_V,lo:=4446,hi:=4447); |  | 223:razlitjeLAH3:=Bit_0; | 223:UPS[2].OutputStatus:=Word_01; |  |  | 4447:PMM[1].VirBVoltageBetweenPhaseAB_V:=Real_0;
mind_bool[224]:=razlitjeLAH4; | mind[224]:=UPS[2].SteviloIzpadovVhodneLinije; |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseAN_V,lo:=4448,hi:=4449); |  | 224:razlitjeLAH4:=Bit_0; | 224:UPS[2].SteviloIzpadovVhodneLinije:=Word_01; |  |  | 4449:PMM[1].VirBVoltageBetweenPhaseAN_V:=Real_0;
mind_bool[225]:=SetDateTime; | mind[225]:=UPS[2].UnitStatus; |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseBC_V,lo:=4450,hi:=4451); |  | 225:SetDateTime:=Bit_0; | 225:UPS[2].UnitStatus:=Word_01; |  |  | 4451:PMM[1].VirBVoltageBetweenPhaseBC_V:=Real_0;
mind_bool[226]:=SetDateTimeDemand; | mind[226]:=UPS_MGE[1].BatteryBackupTime; |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseBN_V,lo:=4452,hi:=4453); |  | 226:SetDateTimeDemand:=Bit_0; | 226:UPS_MGE[1].BatteryBackupTime:=Word_01; |  |  | 4453:PMM[1].VirBVoltageBetweenPhaseBN_V:=Real_0;
mind_bool[227]:=SetDateTimeError; | mind[227]:=UPS_MGE[1].BatteryChargingLevel; |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseCA_V,lo:=4454,hi:=4455); |  | 227:SetDateTimeError:=Bit_0; | 227:UPS_MGE[1].BatteryChargingLevel:=Word_01; |  |  | 4455:PMM[1].VirBVoltageBetweenPhaseCA_V:=Real_0;
mind_bool[228]:=SetDateTimeFinished; | mind[228]:=UPS_MGE[1].BatteryRechargeDuration; |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseCN_V,lo:=4456,hi:=4457); |  | 228:SetDateTimeFinished:=Bit_0; | 228:UPS_MGE[1].BatteryRechargeDuration:=Word_01; |  |  | 4457:PMM[1].VirBVoltageBetweenPhaseCN_V:=Real_0;
mind_bool[229]:=SkupneNapakeNaprav_PMM17VirBVirA; | mind[229]:=UPS_MGE[1].I1output; |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseAB_V,lo:=4458,hi:=4459); |  | 229:SkupneNapakeNaprav_PMM17VirBVirA:=Bit_0; | 229:UPS_MGE[1].I1output:=Word_01; |  |  | 4459:PMM[1].VoltageBetweenPhaseAB_V:=Real_0;
mind_bool[230]:=SlabaBaterijaPLC; | mind[230]:=UPS_MGE[1].I2output; |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseAN_V,lo:=4460,hi:=4461); |  | 230:SlabaBaterijaPLC:=Bit_0; | 230:UPS_MGE[1].I2output:=Word_01; |  |  | 4461:PMM[1].VoltageBetweenPhaseAN_V:=Real_0;
mind_bool[231]:=TempPovp234Previs; | mind[231]:=UPS_MGE[1].I3output; |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseBC_V,lo:=4462,hi:=4463); |  | 231:TempPovp234Previs:=Bit_0; | 231:UPS_MGE[1].I3output:=Word_01; |  |  | 4463:PMM[1].VoltageBetweenPhaseBC_V:=Real_0;
mind_bool[232]:=TempPovp56Previs; | mind[232]:=UPS_MGE[1].InverterFrequency; |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseBN_V,lo:=4464,hi:=4465); |  | 232:TempPovp56Previs:=Bit_0; | 232:UPS_MGE[1].InverterFrequency:=Word_01; |  |  | 4465:PMM[1].VoltageBetweenPhaseBN_V:=Real_0;
mind_bool[233]:=TIA1_previs_temp; | mind[233]:=UPS_MGE[1].OutputActivePower1; |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseCA_V,lo:=4466,hi:=4467); |  | 233:TIA1_previs_temp:=Bit_0; | 233:UPS_MGE[1].OutputActivePower1:=Word_01; |  |  | 4467:PMM[1].VoltageBetweenPhaseCA_V:=Real_0;
mind_bool[234]:=TIA2_previs_temp; | mind[234]:=UPS_MGE[1].OutputActivePower2; |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseCN_V,lo:=4468,hi:=4469); |  | 234:TIA2_previs_temp:=Bit_0; | 234:UPS_MGE[1].OutputActivePower2:=Word_01; |  |  | 4469:PMM[1].VoltageBetweenPhaseCN_V:=Real_0;
mind_bool[235]:=TIA3_previs_temp; | mind[235]:=UPS_MGE[1].OutputActivePower3; |  |  | Read_Real(rVar:=PMMfaza01,lo:=4470,hi:=4471); |  | 235:TIA3_previs_temp:=Bit_0; | 235:UPS_MGE[1].OutputActivePower3:=Word_01; |  |  | 4471:PMMfaza01:=Real_0;
mind_bool[236]:=TIA4_previs_temp; | mind[236]:=UPS_MGE[1].OutputFrequency; |  |  | Read_Real(rVar:=PMMfaza02,lo:=4472,hi:=4473); |  | 236:TIA4_previs_temp:=Bit_0; | 236:UPS_MGE[1].OutputFrequency:=Word_01; |  |  | 4473:PMMfaza02:=Real_0;
mind_bool[237]:=TIA5_previs_temp; | mind[237]:=UPS_MGE[1].OutputLoadLevel; |  |  | Read_Real(rVar:=PMMfaza03,lo:=4474,hi:=4475); |  | 237:TIA5_previs_temp:=Bit_0; | 237:UPS_MGE[1].OutputLoadLevel:=Word_01; |  |  | 4475:PMMfaza03:=Real_0;
mind_bool[238]:=TIA6_previs_temp; | mind[238]:=UPS_MGE[1].StatusBaterije; |  |  | Read_Real(rVar:=PMMfaza04,lo:=4476,hi:=4477); |  | 238:TIA6_previs_temp:=Bit_0; | 238:UPS_MGE[1].StatusBaterije:=Byte_0; |  |  | 4477:PMMfaza04:=Real_0;
mind_bool[239]:=TIA7_previs_temp; | mind[239]:=UPS_MGE[1].U12mains1; |  |  | Read_Real(rVar:=PMMfaza05,lo:=4478,hi:=4479); |  | 239:TIA7_previs_temp:=Bit_0; | 239:UPS_MGE[1].U12mains1:=Word_01; |  |  | 4479:PMMfaza05:=Real_0;
mind_bool[240]:=UPS1Errors[10]; | mind[240]:=UPS_MGE[1].U12mains2; |  |  | Read_Real(rVar:=PMMfaza06,lo:=4480,hi:=4481); |  | 240:UPS1Errors[10]:=Bit_0; | 240:UPS_MGE[1].U12mains2:=Word_01; |  |  | 4481:PMMfaza06:=Real_0;
mind_bool[241]:=UPS1Errors[11]; | mind[241]:=UPS_MGE[1].U1N_inverter; |  |  | Read_Real(rVar:=PMMfaza07,lo:=4482,hi:=4483); |  | 241:UPS1Errors[11]:=Bit_0; | 241:UPS_MGE[1].U1N_inverter:=Word_01; |  |  | 4483:PMMfaza07:=Real_0;
mind_bool[242]:=UPS1Errors[12]; | mind[242]:=UPS_MGE[1].U1N_output; |  |  | Read_Real(rVar:=PMMfaza08,lo:=4484,hi:=4485); |  | 242:UPS1Errors[12]:=Bit_0; | 242:UPS_MGE[1].U1N_output:=Word_01; |  |  | 4485:PMMfaza08:=Real_0;
mind_bool[243]:=UPS1Errors[13]; | mind[243]:=UPS_MGE[1].U23mains1; |  |  | Read_Real(rVar:=PMMfaza09,lo:=4486,hi:=4487); |  | 243:UPS1Errors[13]:=Bit_0; | 243:UPS_MGE[1].U23mains1:=Word_01; |  |  | 4487:PMMfaza09:=Real_0;
mind_bool[244]:=UPS1Errors[14]; | mind[244]:=UPS_MGE[1].U23mains2; |  |  | Read_Real(rVar:=PMMfaza10,lo:=4488,hi:=4489); |  | 244:UPS1Errors[14]:=Bit_0; | 244:UPS_MGE[1].U23mains2:=Word_01; |  |  | 4489:PMMfaza10:=Real_0;
mind_bool[245]:=UPS1Errors[15]; | mind[245]:=UPS_MGE[1].U2N_inverter; |  |  | Read_Real(rVar:=PMMfaza11,lo:=4490,hi:=4491); |  | 245:UPS1Errors[15]:=Bit_0; | 245:UPS_MGE[1].U2N_inverter:=Word_01; |  |  | 4491:PMMfaza11:=Real_0;
mind_bool[246]:=UPS1Errors[16]; | mind[246]:=UPS_MGE[1].U2N_output; |  |  | Read_Real(rVar:=PMMfaza12,lo:=4492,hi:=4493); |  | 246:UPS1Errors[16]:=Bit_0; | 246:UPS_MGE[1].U2N_output:=Word_01; |  |  | 4493:PMMfaza12:=Real_0;
mind_bool[247]:=UPS1Errors[17]; | mind[247]:=UPS_MGE[1].U31mains1; |  |  | Read_Real(rVar:=PMMfaza13,lo:=4494,hi:=4495); |  | 247:UPS1Errors[17]:=Bit_0; | 247:UPS_MGE[1].U31mains1:=Word_01; |  |  | 4495:PMMfaza13:=Real_0;
mind_bool[248]:=UPS1Errors[18]; | mind[248]:=UPS_MGE[1].U31mains2; |  |  | Read_Real(rVar:=PMMfaza14,lo:=4496,hi:=4497); |  | 248:UPS1Errors[18]:=Bit_0; | 248:UPS_MGE[1].U31mains2:=Word_01; |  |  | 4497:PMMfaza14:=Real_0;
mind_bool[249]:=UPS1Errors[19]; | mind[249]:=UPS_MGE[1].U3N_inverter; |  |  | Read_Real(rVar:=PMMfaza15,lo:=4498,hi:=4499); |  | 249:UPS1Errors[19]:=Bit_0; | 249:UPS_MGE[1].U3N_inverter:=Word_01; |  |  | 4499:PMMfaza15:=Real_0;
mind_bool[250]:=UPS1Errors[1]; | mind[250]:=UPS_MGE[1].U3N_output; |  |  | Read_Real(rVar:=PMMfaza16,lo:=4500,hi:=4501); |  | 250:UPS1Errors[1]:=Bit_0; | 250:UPS_MGE[1].U3N_output:=Word_01; |  |  | 4501:PMMfaza16:=Real_0;
mind_bool[251]:=UPS1Errors[20]; | mind[251]:=UPS_MGE[1].U_battery; |  |  | Read_Real(rVar:=PMMfaza17,lo:=4502,hi:=4503); |  | 251:UPS1Errors[20]:=Bit_0; | 251:UPS_MGE[1].U_battery:=Word_01; |  |  | 4503:PMMfaza17:=Real_0;
mind_bool[252]:=UPS1Errors[21]; | mind[252]:=UserCurrentLevel; |  |  | Read_Real(rVar:=PMMfaza18,lo:=4504,hi:=4505); |  | 252:UPS1Errors[21]:=Bit_0; | 252:UserCurrentLevel:=Byte_0; |  |  | 4505:PMMfaza18:=Real_0;
mind_bool[253]:=UPS1Errors[22]; | mind[253]:=XVH_UPSstatus; |  |  | Read_Real(rVar:=PMMfaza19,lo:=4506,hi:=4507); |  | 253:UPS1Errors[22]:=Bit_0; | 253:XVH_UPSstatus:=Byte_0; |  |  | 4507:PMMfaza19:=Real_0;
mind_bool[254]:=UPS1Errors[23]; | mind[254]:=UPS[3].InverterStatus; |  |  | Read_Real(rVar:=PMMfaza20,lo:=4508,hi:=4509); |  | 254:UPS1Errors[23]:=Bit_0; | 254:UPS[3].InverterStatus:=Word_01; |  |  | 4509:PMMfaza20:=Real_0;
mind_bool[255]:=UPS1Errors[24]; | mind[255]:=UPS[3].OutputStatus; |  |  | Read_Real(rVar:=PMMfaza21,lo:=4510,hi:=4511); |  | 255:UPS1Errors[24]:=Bit_0; | 255:UPS[3].OutputStatus:=Word_01; |  |  | 4511:PMMfaza21:=Real_0;
mind_bool[256]:=UPS1Errors[25]; | mind[256]:=UPS[3].SteviloIzpadovVhodneLinije; |  |  | Read_Real(rVar:=PMMfaza22,lo:=4512,hi:=4513); |  | 256:UPS1Errors[25]:=Bit_0; | 256:UPS[3].SteviloIzpadovVhodneLinije:=Word_01; |  |  | 4513:PMMfaza22:=Real_0;
mind_bool[257]:=UPS1Errors[2]; | mind[257]:=UPS[3].UnitStatus; |  |  | Read_Real(rVar:=PMMfaza23,lo:=4514,hi:=4515); |  | 257:UPS1Errors[2]:=Bit_0; | 257:UPS[3].UnitStatus:=Word_01; |  |  | 4515:PMMfaza23:=Real_0;
mind_bool[258]:=UPS1Errors[3]; |  |  |  | Read_Real(rVar:=PMMfaza24,lo:=4516,hi:=4517); |  | 258:UPS1Errors[3]:=Bit_0; |  |  |  | 4517:PMMfaza24:=Real_0;
mind_bool[259]:=UPS1Errors[4]; |  |  |  | Read_Real(rVar:=PMMfaza25,lo:=4518,hi:=4519); |  | 259:UPS1Errors[4]:=Bit_0; |  |  |  | 4519:PMMfaza25:=Real_0;
mind_bool[260]:=UPS1Errors[5]; |  |  |  | Read_Real(rVar:=PMMfaza26,lo:=4520,hi:=4521); |  | 260:UPS1Errors[5]:=Bit_0; |  |  |  | 4521:PMMfaza26:=Real_0;
mind_bool[261]:=UPS1Errors[6]; |  |  |  | Read_Real(rVar:=PMMfaza27,lo:=4522,hi:=4523); |  | 261:UPS1Errors[6]:=Bit_0; |  |  |  | 4523:PMMfaza27:=Real_0;
mind_bool[262]:=UPS1Errors[7]; |  |  |  | Read_Real(rVar:=PMMfaza28,lo:=4524,hi:=4525); |  | 262:UPS1Errors[7]:=Bit_0; |  |  |  | 4525:PMMfaza28:=Real_0;
mind_bool[263]:=UPS1Errors[8]; |  |  |  | Read_Real(rVar:=PMMfaza29,lo:=4526,hi:=4527); |  | 263:UPS1Errors[8]:=Bit_0; |  |  |  | 4527:PMMfaza29:=Real_0;
mind_bool[264]:=UPS1Errors[9]; |  |  |  | Read_Real(rVar:=PMMfaza30,lo:=4528,hi:=4529); |  | 264:UPS1Errors[9]:=Bit_0; |  |  |  | 4529:PMMfaza30:=Real_0;
mind_bool[265]:=UPS2Errors[10]; |  |  |  | Read_Real(rVar:=PMMfaza31,lo:=4530,hi:=4531); |  | 265:UPS2Errors[10]:=Bit_0; |  |  |  | 4531:PMMfaza31:=Real_0;
mind_bool[266]:=UPS2Errors[11]; |  |  |  | Read_Real(rVar:=PMMfaza32,lo:=4532,hi:=4533); |  | 266:UPS2Errors[11]:=Bit_0; |  |  |  | 4533:PMMfaza32:=Real_0;
mind_bool[267]:=UPS2Errors[12]; |  |  |  | Read_Real(rVar:=PMMfaza33,lo:=4534,hi:=4535); |  | 267:UPS2Errors[12]:=Bit_0; |  |  |  | 4535:PMMfaza33:=Real_0;
mind_bool[268]:=UPS2Errors[13]; |  |  |  | Read_Real(rVar:=PMMfaza34,lo:=4536,hi:=4537); |  | 268:UPS2Errors[13]:=Bit_0; |  |  |  | 4537:PMMfaza34:=Real_0;
mind_bool[269]:=UPS2Errors[14]; |  |  |  | Read_Real(rVar:=PMMfaza35,lo:=4538,hi:=4539); |  | 269:UPS2Errors[14]:=Bit_0; |  |  |  | 4539:PMMfaza35:=Real_0;
mind_bool[270]:=UPS2Errors[15]; |  |  |  | Read_Real(rVar:=PMMfaza36,lo:=4540,hi:=4541); |  | 270:UPS2Errors[15]:=Bit_0; |  |  |  | 4541:PMMfaza36:=Real_0;
mind_bool[271]:=UPS2Errors[16]; |  |  |  | Read_Real(rVar:=PMMfaza37,lo:=4542,hi:=4543); |  | 271:UPS2Errors[16]:=Bit_0; |  |  |  | 4543:PMMfaza37:=Real_0;
mind_bool[272]:=UPS2Errors[17]; |  |  |  | Read_Real(rVar:=PMMfaza38,lo:=4544,hi:=4545); |  | 272:UPS2Errors[17]:=Bit_0; |  |  |  | 4545:PMMfaza38:=Real_0;
mind_bool[273]:=UPS2Errors[18]; |  |  |  | Read_Real(rVar:=PMMfaza39,lo:=4546,hi:=4547); |  | 273:UPS2Errors[18]:=Bit_0; |  |  |  | 4547:PMMfaza39:=Real_0;
mind_bool[274]:=UPS2Errors[19]; |  |  |  | Read_Real(rVar:=PMMfaza40,lo:=4548,hi:=4549); |  | 274:UPS2Errors[19]:=Bit_0; |  |  |  | 4549:PMMfaza40:=Real_0;
mind_bool[275]:=UPS2Errors[1]; |  |  |  | Read_Real(rVar:=PMMfaza41,lo:=4550,hi:=4551); |  | 275:UPS2Errors[1]:=Bit_0; |  |  |  | 4551:PMMfaza41:=Real_0;
mind_bool[276]:=UPS2Errors[20]; |  |  |  | Read_Real(rVar:=PMMfaza42,lo:=4552,hi:=4553); |  | 276:UPS2Errors[20]:=Bit_0; |  |  |  | 4553:PMMfaza42:=Real_0;
mind_bool[277]:=UPS2Errors[21]; |  |  |  | Read_Real(rVar:=UPS[1].EstimatedChargeRemaining,lo:=4554,hi:=4555); |  | 277:UPS2Errors[21]:=Bit_0; |  |  |  | 4555:UPS[1].EstimatedChargeRemaining:=Real_0;
mind_bool[278]:=UPS2Errors[22]; |  |  |  | Read_Real(rVar:=UPS[1].EstimatedMinutesRemaining,lo:=4556,hi:=4557); |  | 278:UPS2Errors[22]:=Bit_0; |  |  |  | 4557:UPS[1].EstimatedMinutesRemaining:=Real_0;
mind_bool[279]:=UPS2Errors[23]; |  |  |  | Read_Real(rVar:=UPS[1].IzhodMocL1,lo:=4558,hi:=4559); |  | 279:UPS2Errors[23]:=Bit_0; |  |  |  | 4559:UPS[1].IzhodMocL1:=Real_0;
mind_bool[280]:=UPS2Errors[24]; |  |  |  | Read_Real(rVar:=UPS[1].IzhodMocL2,lo:=4560,hi:=4561); |  | 280:UPS2Errors[24]:=Bit_0; |  |  |  | 4561:UPS[1].IzhodMocL2:=Real_0;
mind_bool[281]:=UPS2Errors[25]; |  |  |  | Read_Real(rVar:=UPS[1].IzhodMocL3,lo:=4562,hi:=4563); |  | 281:UPS2Errors[25]:=Bit_0; |  |  |  | 4563:UPS[1].IzhodMocL3:=Real_0;
mind_bool[282]:=UPS2Errors[2]; |  |  |  | Read_Real(rVar:=UPS[1].NapetostBaterije,lo:=4564,hi:=4565); |  | 282:UPS2Errors[2]:=Bit_0; |  |  |  | 4565:UPS[1].NapetostBaterije:=Real_0;
mind_bool[283]:=UPS2Errors[3]; |  |  |  | Read_Real(rVar:=UPS[1].TemperaturaBaterije,lo:=4566,hi:=4567); |  | 283:UPS2Errors[3]:=Bit_0; |  |  |  | 4567:UPS[1].TemperaturaBaterije:=Real_0;
mind_bool[284]:=UPS2Errors[4]; |  |  |  | Read_Real(rVar:=UPS[1].VhodFrekvencaL1,lo:=4568,hi:=4569); |  | 284:UPS2Errors[4]:=Bit_0; |  |  |  | 4569:UPS[1].VhodFrekvencaL1:=Real_0;
mind_bool[285]:=UPS2Errors[5]; |  |  |  | Read_Real(rVar:=UPS[1].VhodFrekvencaL2,lo:=4570,hi:=4571); |  | 285:UPS2Errors[5]:=Bit_0; |  |  |  | 4571:UPS[1].VhodFrekvencaL2:=Real_0;
mind_bool[286]:=UPS2Errors[6]; |  |  |  | Read_Real(rVar:=UPS[1].VhodFrekvencaL3,lo:=4572,hi:=4573); |  | 286:UPS2Errors[6]:=Bit_0; |  |  |  | 4573:UPS[1].VhodFrekvencaL3:=Real_0;
mind_bool[287]:=UPS2Errors[7]; |  |  |  | Read_Real(rVar:=UPS[1].VhodNapetostL1,lo:=4574,hi:=4575); |  | 287:UPS2Errors[7]:=Bit_0; |  |  |  | 4575:UPS[1].VhodNapetostL1:=Real_0;
mind_bool[288]:=UPS2Errors[8]; |  |  |  | Read_Real(rVar:=UPS[1].VhodNapetostL2,lo:=4576,hi:=4577); |  | 288:UPS2Errors[8]:=Bit_0; |  |  |  | 4577:UPS[1].VhodNapetostL2:=Real_0;
mind_bool[289]:=UPS2Errors[9]; |  |  |  | Read_Real(rVar:=UPS[1].VhodNapetostL3,lo:=4578,hi:=4579); |  | 289:UPS2Errors[9]:=Bit_0; |  |  |  | 4579:UPS[1].VhodNapetostL3:=Real_0;
mind_bool[290]:=UPS[1].AlarmAwaitingPower; |  |  |  | Read_Real(rVar:=UPS[2].EstimatedChargeRemaining,lo:=4580,hi:=4581); |  | 290:UPS[1].AlarmAwaitingPower:=Bit_0; |  |  |  | 4581:UPS[2].EstimatedChargeRemaining:=Real_0;
mind_bool[291]:=UPS[1].AlarmBypassBad; |  |  |  | Read_Real(rVar:=UPS[2].EstimatedMinutesRemaining,lo:=4582,hi:=4583); |  | 291:UPS[1].AlarmBypassBad:=Bit_0; |  |  |  | 4583:UPS[2].EstimatedMinutesRemaining:=Real_0;
mind_bool[292]:=UPS[1].AlarmChargerFailed; |  |  |  | Read_Real(rVar:=UPS[2].IzhodMocL1,lo:=4584,hi:=4585); |  | 292:UPS[1].AlarmChargerFailed:=Bit_0; |  |  |  | 4585:UPS[2].IzhodMocL1:=Real_0;
mind_bool[293]:=UPS[1].AlarmCommunicationsLost; |  |  |  | Read_Real(rVar:=UPS[2].IzhodMocL2,lo:=4586,hi:=4587); |  | 293:UPS[1].AlarmCommunicationsLost:=Bit_0; |  |  |  | 4587:UPS[2].IzhodMocL2:=Real_0;
mind_bool[294]:=UPS[1].AlarmDepletedBattery; |  |  |  | Read_Real(rVar:=UPS[2].IzhodMocL3,lo:=4588,hi:=4589); |  | 294:UPS[1].AlarmDepletedBattery:=Bit_0; |  |  |  | 4589:UPS[2].IzhodMocL3:=Real_0;
mind_bool[295]:=UPS[1].AlarmDiagnosticTestFailed; |  |  |  | Read_Real(rVar:=UPS[2].NapetostBaterije,lo:=4590,hi:=4591); |  | 295:UPS[1].AlarmDiagnosticTestFailed:=Bit_0; |  |  |  | 4591:UPS[2].NapetostBaterije:=Real_0;
mind_bool[296]:=UPS[1].AlarmInverterError; |  |  |  | Read_Real(rVar:=UPS[2].TemperaturaBaterije,lo:=4592,hi:=4593); |  | 296:UPS[1].AlarmInverterError:=Bit_0; |  |  |  | 4593:UPS[2].TemperaturaBaterije:=Real_0;
mind_bool[297]:=UPS[1].AlarmIzhodOffKotZahtevano; |  |  |  | Read_Real(rVar:=UPS[2].VhodFrekvencaL1,lo:=4594,hi:=4595); |  | 297:UPS[1].AlarmIzhodOffKotZahtevano:=Bit_0; |  |  |  | 4595:UPS[2].VhodFrekvencaL1:=Real_0;
mind_bool[298]:=UPS[1].AlarmIzhodPreobremenjen; |  |  |  | Read_Real(rVar:=UPS[2].VhodFrekvencaL2,lo:=4596,hi:=4597); |  | 298:UPS[1].AlarmIzhodPreobremenjen:=Bit_0; |  |  |  | 4597:UPS[2].VhodFrekvencaL2:=Real_0;
mind_bool[299]:=UPS[1].AlarmLowBattery; |  |  |  | Read_Real(rVar:=UPS[2].VhodFrekvencaL3,lo:=4598,hi:=4599); |  | 299:UPS[1].AlarmLowBattery:=Bit_0; |  |  |  | 4599:UPS[2].VhodFrekvencaL3:=Real_0;
mind_bool[300]:=UPS[1].AlarmNapakaNaVarovalki; |  |  |  | Read_Real(rVar:=UPS[2].VhodNapetostL1,lo:=4600,hi:=4601); |  | 300:UPS[1].AlarmNapakaNaVarovalki:=Bit_0; |  |  |  | 4601:UPS[2].VhodNapetostL1:=Real_0;
mind_bool[301]:=UPS[1].AlarmNapakaNaVentilatorju; |  |  |  | Read_Real(rVar:=UPS[2].VhodNapetostL2,lo:=4602,hi:=4603); |  | 301:UPS[1].AlarmNapakaNaVentilatorju:=Bit_0; |  |  |  | 4603:UPS[2].VhodNapetostL2:=Real_0;
mind_bool[302]:=UPS[1].AlarmOnBattery; |  |  |  | Read_Real(rVar:=UPS[2].VhodNapetostL3,lo:=4604,hi:=4605); |  | 302:UPS[1].AlarmOnBattery:=Bit_0; |  |  |  | 4605:UPS[2].VhodNapetostL3:=Real_0;
mind_bool[303]:=UPS[1].AlarmOnBypass; |  |  |  | Read_Real(rVar:=XVHdepltedBatery1,lo:=4606,hi:=4607); |  | 303:UPS[1].AlarmOnBypass:=Bit_0; |  |  |  | 4607:XVHdepltedBatery1:=Real_0;
mind_bool[304]:=UPS[1].AlarmShutdownImminent; |  |  |  | Read_Real(rVar:=XVHdepltedBatery2,lo:=4608,hi:=4609); |  | 304:UPS[1].AlarmShutdownImminent:=Bit_0; |  |  |  | 4609:XVHdepltedBatery2:=Real_0;
mind_bool[305]:=UPS[1].AlarmShutdownPending; |  |  |  | Read_Real(rVar:=XVHlowBatery1,lo:=4610,hi:=4611); |  | 305:UPS[1].AlarmShutdownPending:=Bit_0; |  |  |  | 4611:XVHlowBatery1:=Real_0;
mind_bool[306]:=UPS[1].AlarmSlabaBaterija; |  |  |  | Read_Real(rVar:=XVHlowBatery2,lo:=4612,hi:=4613); |  | 306:UPS[1].AlarmSlabaBaterija:=Bit_0; |  |  |  | 4613:XVHlowBatery2:=Real_0;
mind_bool[307]:=UPS[1].AlarmSplosnaNapaka; |  |  |  | Read_Real(rVar:=PMMskupniTokA,lo:=4614,hi:=4615); |  | 307:UPS[1].AlarmSplosnaNapaka:=Bit_0; |  |  |  | 4615:PMMskupniTokA:=Real_0;
mind_bool[308]:=UPS[1].AlarmStanjeIzhodaIzvenToleranc; |  |  |  | Read_Real(rVar:=PMMskupniTokB,lo:=4616,hi:=4617); |  | 308:UPS[1].AlarmStanjeIzhodaIzvenToleranc:=Bit_0; |  |  |  | 4617:PMMskupniTokB:=Real_0;
mind_bool[309]:=UPS[1].AlarmStanjeVhodaIzvenToleranc; |  |  |  | Read_Real(rVar:=UPS[3].EstimatedChargeRemaining,lo:=4618,hi:=4619); |  | 309:UPS[1].AlarmStanjeVhodaIzvenToleranc:=Bit_0; |  |  |  | 4619:UPS[3].EstimatedChargeRemaining:=Real_0;
mind_bool[310]:=UPS[1].AlarmTemperaturaIzvenToleranc; |  |  |  | Read_Real(rVar:=UPS[3].EstimatedMinutesRemaining,lo:=4620,hi:=4621); |  | 310:UPS[1].AlarmTemperaturaIzvenToleranc:=Bit_0; |  |  |  | 4621:UPS[3].EstimatedMinutesRemaining:=Real_0;
mind_bool[311]:=UPS[1].AlarmTestInProgres; |  |  |  | Read_Real(rVar:=UPS[3].IzhodMocL1,lo:=4622,hi:=4623); |  | 311:UPS[1].AlarmTestInProgres:=Bit_0; |  |  |  | 4623:UPS[3].IzhodMocL1:=Real_0;
mind_bool[312]:=UPS[1].AlarmUPSIzhodOff; |  |  |  | Read_Real(rVar:=UPS[3].IzhodMocL2,lo:=4624,hi:=4625); |  | 312:UPS[1].AlarmUPSIzhodOff:=Bit_0; |  |  |  | 4625:UPS[3].IzhodMocL2:=Real_0;
mind_bool[313]:=UPS[1].AlarmUPSOffKotZahtevano; |  |  |  | Read_Real(rVar:=UPS[3].IzhodMocL3,lo:=4626,hi:=4627); |  | 313:UPS[1].AlarmUPSOffKotZahtevano:=Bit_0; |  |  |  | 4627:UPS[3].IzhodMocL3:=Real_0;
mind_bool[314]:=UPS[1].AlarmUPSSystemOff; |  |  |  | Read_Real(rVar:=UPS[3].NapetostBaterije,lo:=4628,hi:=4629); |  | 314:UPS[1].AlarmUPSSystemOff:=Bit_0; |  |  |  | 4629:UPS[3].NapetostBaterije:=Real_0;
mind_bool[315]:=UPS[1].Napaka; |  |  |  | Read_Real(rVar:=UPS[3].TemperaturaBaterije,lo:=4630,hi:=4631); |  | 315:UPS[1].Napaka:=Bit_0; |  |  |  | 4631:UPS[3].TemperaturaBaterije:=Real_0;
mind_bool[316]:=UPS[1].StatusEcomodeAktiven; |  |  |  | Read_Real(rVar:=UPS[3].VhodFrekvencaL1,lo:=4632,hi:=4633); |  | 316:UPS[1].StatusEcomodeAktiven:=Bit_0; |  |  |  | 4633:UPS[3].VhodFrekvencaL1:=Real_0;
mind_bool[317]:=UPS[1].StatusInverterIsOn; |  |  |  | Read_Real(rVar:=UPS[3].VhodFrekvencaL2,lo:=4634,hi:=4635); |  | 317:UPS[1].StatusInverterIsOn:=Bit_0; |  |  |  | 4635:UPS[3].VhodFrekvencaL2:=Real_0;
mind_bool[318]:=UPS[1].StatusStopOperation; |  |  |  | Read_Real(rVar:=UPS[3].VhodFrekvencaL3,lo:=4636,hi:=4637); |  | 318:UPS[1].StatusStopOperation:=Bit_0; |  |  |  | 4637:UPS[3].VhodFrekvencaL3:=Real_0;
mind_bool[319]:=UPS[2].AlarmAwaitingPower; |  |  |  | Read_Real(rVar:=UPS[3].VhodNapetostL1,lo:=4638,hi:=4639); |  | 319:UPS[2].AlarmAwaitingPower:=Bit_0; |  |  |  | 4639:UPS[3].VhodNapetostL1:=Real_0;
mind_bool[320]:=UPS[2].AlarmBypassBad; |  |  |  | Read_Real(rVar:=UPS[3].VhodNapetostL2,lo:=4640,hi:=4641); |  | 320:UPS[2].AlarmBypassBad:=Bit_0; |  |  |  | 4641:UPS[3].VhodNapetostL2:=Real_0;
mind_bool[321]:=UPS[2].AlarmChargerFailed; |  |  |  | Read_Real(rVar:=UPS[3].VhodNapetostL3,lo:=4642,hi:=4643); |  | 321:UPS[2].AlarmChargerFailed:=Bit_0; |  |  |  | 4643:UPS[3].VhodNapetostL3:=Real_0;
mind_bool[322]:=UPS[2].AlarmCommunicationsLost; |  |  |  | Read_Real(rVar:=Circ[1].MaximumDemandA2,lo:=4644,hi:=4645); |  | 322:UPS[2].AlarmCommunicationsLost:=Bit_0; |  |  |  | 4645:Circ[1].MaximumDemandA2:=Real_0;
mind_bool[323]:=UPS[2].AlarmDepletedBattery; |  |  |  | Read_Real(rVar:=Circ[1].MaximumDemandA3,lo:=4646,hi:=4647); |  | 323:UPS[2].AlarmDepletedBattery:=Bit_0; |  |  |  | 4647:Circ[1].MaximumDemandA3:=Real_0;
mind_bool[324]:=UPS[2].AlarmDiagnosticTestFailed; |  |  |  | Read_Real(rVar:=Circ[1].RazEner_D_SCADA,lo:=4648,hi:=4649); |  | 324:UPS[2].AlarmDiagnosticTestFailed:=Bit_0; |  |  |  | 4649:Circ[1].RazEner_D_SCADA:=Real_0;
mind_bool[325]:=UPS[2].AlarmInverterError; |  |  |  | Read_Real(rVar:=Circ[1].RazEner_T_SCADA,lo:=4650,hi:=4651); |  | 325:UPS[2].AlarmInverterError:=Bit_0; |  |  |  | 4651:Circ[1].RazEner_T_SCADA:=Real_0;
mind_bool[326]:=UPS[2].AlarmIzhodOffKotZahtevano; |  |  |  | Read_Real(rVar:=Circ[1].RazEner_M_SCADA,lo:=4652,hi:=4653); |  | 326:UPS[2].AlarmIzhodOffKotZahtevano:=Bit_0; |  |  |  | 4653:Circ[1].RazEner_M_SCADA:=Real_0;
mind_bool[327]:=UPS[2].AlarmIzhodPreobremenjen; | [5 empty] | 327:UPS[2].AlarmIzhodPreobremenjen:=Bit_0;
mind_bool[328]:=UPS[2].AlarmLowBattery; | [5 empty] | 328:UPS[2].AlarmLowBattery:=Bit_0;
mind_bool[329]:=UPS[2].AlarmNapakaNaVarovalki; | [5 empty] | 329:UPS[2].AlarmNapakaNaVarovalki:=Bit_0;
mind_bool[330]:=UPS[2].AlarmNapakaNaVentilatorju; | [5 empty] | 330:UPS[2].AlarmNapakaNaVentilatorju:=Bit_0;
mind_bool[331]:=UPS[2].AlarmOnBattery; | [5 empty] | 331:UPS[2].AlarmOnBattery:=Bit_0;
mind_bool[332]:=UPS[2].AlarmOnBypass; | [5 empty] | 332:UPS[2].AlarmOnBypass:=Bit_0;
mind_bool[333]:=UPS[2].AlarmShutdownImminent; | [5 empty] | 333:UPS[2].AlarmShutdownImminent:=Bit_0;
mind_bool[334]:=UPS[2].AlarmShutdownPending; | [5 empty] | 334:UPS[2].AlarmShutdownPending:=Bit_0;
mind_bool[335]:=UPS[2].AlarmSlabaBaterija; | [5 empty] | 335:UPS[2].AlarmSlabaBaterija:=Bit_0;
mind_bool[336]:=UPS[2].AlarmSplosnaNapaka; | [5 empty] | 336:UPS[2].AlarmSplosnaNapaka:=Bit_0;
mind_bool[337]:=UPS[2].AlarmStanjeIzhodaIzvenToleranc; | [5 empty] | 337:UPS[2].AlarmStanjeIzhodaIzvenToleranc:=Bit_0;
mind_bool[338]:=UPS[2].AlarmStanjeVhodaIzvenToleranc; | [5 empty] | 338:UPS[2].AlarmStanjeVhodaIzvenToleranc:=Bit_0;
mind_bool[339]:=UPS[2].AlarmTemperaturaIzvenToleranc; | [5 empty] | 339:UPS[2].AlarmTemperaturaIzvenToleranc:=Bit_0;
mind_bool[340]:=UPS[2].AlarmTestInProgres; | [5 empty] | 340:UPS[2].AlarmTestInProgres:=Bit_0;
mind_bool[341]:=UPS[2].AlarmUPSIzhodOff; | [5 empty] | 341:UPS[2].AlarmUPSIzhodOff:=Bit_0;
mind_bool[342]:=UPS[2].AlarmUPSOffKotZahtevano; | [5 empty] | 342:UPS[2].AlarmUPSOffKotZahtevano:=Bit_0;
mind_bool[343]:=UPS[2].AlarmUPSSystemOff; | [5 empty] | 343:UPS[2].AlarmUPSSystemOff:=Bit_0;
mind_bool[344]:=UPS[2].Napaka; | [5 empty] | 344:UPS[2].Napaka:=Bit_0;
mind_bool[345]:=UPS[2].StatusEcomodeAktiven; | [5 empty] | 345:UPS[2].StatusEcomodeAktiven:=Bit_0;
mind_bool[346]:=UPS[2].StatusInverterIsOn; | [5 empty] | 346:UPS[2].StatusInverterIsOn:=Bit_0;
mind_bool[347]:=UPS[2].StatusStopOperation; | [5 empty] | 347:UPS[2].StatusStopOperation:=Bit_0;
mind_bool[348]:=UPS_A_V23_delovanje; | [5 empty] | 348:UPS_A_V23_delovanje:=Bit_0;
mind_bool[349]:=UPS_A_V23_napaka; | [5 empty] | 349:UPS_A_V23_napaka:=Bit_0;
mind_bool[350]:=ups_alarm; | [5 empty] | 350:ups_alarm:=Bit_0;
mind_bool[351]:=ups_baterijski_nac; | [5 empty] | 351:ups_baterijski_nac:=Bit_0;
mind_bool[352]:=UPS_MGE[1].BatteryChargedState; | [5 empty] | 352:UPS_MGE[1].BatteryChargedState:=Bit_0;
mind_bool[353]:=UPS_MGE[1].BatteryCircuitBreaker; | [5 empty] | 353:UPS_MGE[1].BatteryCircuitBreaker:=Bit_0;
mind_bool[354]:=UPS_MGE[1].BatteryCompInProgress; | [5 empty] | 354:UPS_MGE[1].BatteryCompInProgress:=Bit_0;
mind_bool[355]:=UPS_MGE[1].BatteryFuseFault; | [5 empty] | 355:UPS_MGE[1].BatteryFuseFault:=Bit_0;
mind_bool[356]:=UPS_MGE[1].BatteryLowWarning; | [5 empty] | 356:UPS_MGE[1].BatteryLowWarning:=Bit_0;
mind_bool[357]:=UPS_MGE[1].BatteryTempOutOfToler; | [5 empty] | 357:UPS_MGE[1].BatteryTempOutOfToler:=Bit_0;
mind_bool[358]:=UPS_MGE[1].BypassInFreeFrequency; | [5 empty] | 358:UPS_MGE[1].BypassInFreeFrequency:=Bit_0;
mind_bool[359]:=UPS_MGE[1].ChargerGeneralFault; | [5 empty] | 359:UPS_MGE[1].ChargerGeneralFault:=Bit_0;
mind_bool[360]:=UPS_MGE[1].DeviceVentilationFault; | [5 empty] | 360:UPS_MGE[1].DeviceVentilationFault:=Bit_0;
mind_bool[361]:=UPS_MGE[1].InverterFuseFault; | [5 empty] | 361:UPS_MGE[1].InverterFuseFault:=Bit_0;
mind_bool[362]:=UPS_MGE[1].InverterOverload; | [5 empty] | 362:UPS_MGE[1].InverterOverload:=Bit_0;
mind_bool[363]:=UPS_MGE[1].InverterThermalOverload; | [5 empty] | 363:UPS_MGE[1].InverterThermalOverload:=Bit_0;
mind_bool[364]:=UPS_MGE[1].Mains1VoltOutOfToler; | [5 empty] | 364:UPS_MGE[1].Mains1VoltOutOfToler:=Bit_0;
mind_bool[365]:=UPS_MGE[1].Mains2Overload; | [5 empty] | 365:UPS_MGE[1].Mains2Overload:=Bit_0;
mind_bool[366]:=UPS_MGE[1].Mains2VoltOutOfToler; | [5 empty] | 366:UPS_MGE[1].Mains2VoltOutOfToler:=Bit_0;
mind_bool[367]:=UPS_MGE[1].MaintenancePosition; | [5 empty] | 367:UPS_MGE[1].MaintenancePosition:=Bit_0;
mind_bool[368]:=UPS_MGE[1].ManualBypassSwitch; | [5 empty] | 368:UPS_MGE[1].ManualBypassSwitch:=Bit_0;
mind_bool[369]:=UPS_MGE[1].NapakaNaVarovalkah; | [5 empty] | 369:UPS_MGE[1].NapakaNaVarovalkah:=Bit_0;
mind_bool[370]:=UPS_MGE[1].OutputInShortCircuit; | [5 empty] | 370:UPS_MGE[1].OutputInShortCircuit:=Bit_0;
mind_bool[371]:=UPS_MGE[1].OutputOverload; | [5 empty] | 371:UPS_MGE[1].OutputOverload:=Bit_0;
mind_bool[372]:=UPS_MGE[1].OutputThermalOverload; | [5 empty] | 372:UPS_MGE[1].OutputThermalOverload:=Bit_0;
mind_bool[373]:=UPS_MGE[1].RectifierOn; | [5 empty] | 373:UPS_MGE[1].RectifierOn:=Bit_0;
mind_bool[374]:=UPS_MGE[1].RectifierThermOverload; | [5 empty] | 374:UPS_MGE[1].RectifierThermOverload:=Bit_0;
mind_bool[375]:=UPS_MGE[1].Skupna_napaka; | [5 empty] | 375:UPS_MGE[1].Skupna_napaka:=Bit_0;
mind_bool[376]:=UPS_MGE[1].UPS_coupled; | [5 empty] | 376:UPS_MGE[1].UPS_coupled:=Bit_0;
mind_bool[377]:=UPS_MGE[1].UPS_error; | [5 empty] | 377:UPS_MGE[1].UPS_error:=Bit_0;
mind_bool[378]:=UPS_MGE[1].UPS_in_backup; | [5 empty] | 378:UPS_MGE[1].UPS_in_backup:=Bit_0;
mind_bool[379]:=ups_polnjenje; | [5 empty] | 379:ups_polnjenje:=Bit_0;
mind_bool[380]:=UPS_V23_delovanje; | [5 empty] | 380:UPS_V23_delovanje:=Bit_0;
mind_bool[381]:=UPS_V23_napaka; | [5 empty] | 381:UPS_V23_napaka:=Bit_0;
mind_bool[382]:=UPS_V25_delovanje; | [5 empty] | 382:UPS_V25_delovanje:=Bit_0;
mind_bool[383]:=UPS_V25_napaka; | [5 empty] | 383:UPS_V25_napaka:=Bit_0;
mind_bool[384]:=UPSMGEErrors[10]; | [5 empty] | 384:UPSMGEErrors[10]:=Bit_0;
mind_bool[385]:=UPSMGEErrors[11]; | [5 empty] | 385:UPSMGEErrors[11]:=Bit_0;
mind_bool[386]:=UPSMGEErrors[12]; | [5 empty] | 386:UPSMGEErrors[12]:=Bit_0;
mind_bool[387]:=UPSMGEErrors[13]; | [5 empty] | 387:UPSMGEErrors[13]:=Bit_0;
mind_bool[388]:=UPSMGEErrors[14]; | [5 empty] | 388:UPSMGEErrors[14]:=Bit_0;
mind_bool[389]:=UPSMGEErrors[15]; | [5 empty] | 389:UPSMGEErrors[15]:=Bit_0;
mind_bool[390]:=UPSMGEErrors[16]; | [5 empty] | 390:UPSMGEErrors[16]:=Bit_0;
mind_bool[391]:=UPSMGEErrors[17]; | [5 empty] | 391:UPSMGEErrors[17]:=Bit_0;
mind_bool[392]:=UPSMGEErrors[1]; | [5 empty] | 392:UPSMGEErrors[1]:=Bit_0;
mind_bool[393]:=UPSMGEErrors[2]; | [5 empty] | 393:UPSMGEErrors[2]:=Bit_0;
mind_bool[394]:=UPSMGEErrors[3]; | [5 empty] | 394:UPSMGEErrors[3]:=Bit_0;
mind_bool[395]:=UPSMGEErrors[4]; | [5 empty] | 395:UPSMGEErrors[4]:=Bit_0;
mind_bool[396]:=UPSMGEErrors[5]; | [5 empty] | 396:UPSMGEErrors[5]:=Bit_0;
mind_bool[397]:=UPSMGEErrors[6]; | [5 empty] | 397:UPSMGEErrors[6]:=Bit_0;
mind_bool[398]:=UPSMGEErrors[7]; | [5 empty] | 398:UPSMGEErrors[7]:=Bit_0;
mind_bool[399]:=UPSMGEErrors[8]; | [5 empty] | 399:UPSMGEErrors[8]:=Bit_0;
mind_bool[400]:=UPSMGEErrors[9]; | [5 empty] | 400:UPSMGEErrors[9]:=Bit_0;
mind_bool[401]:=UserLoggedIn; | [5 empty] | 401:UserLoggedIn:=Bit_0;
mind_bool[402]:=VLAZILEC1_delovanje; | [5 empty] | 402:VLAZILEC1_delovanje:=Bit_0;
mind_bool[403]:=VLAZILEC1_napaka; | [5 empty] | 403:VLAZILEC1_napaka:=Bit_0;
mind_bool[404]:=VLAZILEC2_delovanje; | [5 empty] | 404:VLAZILEC2_delovanje:=Bit_0;
mind_bool[405]:=VLAZILEC2_napaka; | [5 empty] | 405:VLAZILEC2_napaka:=Bit_0;
mind_bool[406]:=XVH_AlarmOn; | [5 empty] | 406:XVH_AlarmOn:=Bit_0;
mind_bool[407]:=XVH_enopolna_napaka; | [5 empty] | 407:XVH_enopolna_napaka:=Bit_0;
mind_bool[408]:=KLIMAT1_vklop_delovanjaR; | [5 empty] | 408:KLIMAT1_vklop_delovanjaR:=Bit_0;
mind_bool[409]:=KLIMAT2_vklop_delovanjaR; | [5 empty] | 409:KLIMAT2_vklop_delovanjaR:=Bit_0;
mind_bool[410]:=KLIMAT1_R_zakleni; | [5 empty] | 410:KLIMAT1_R_zakleni:=Bit_0;
mind_bool[411]:=KLIMAT2_R_zakleni; | [5 empty] | 411:KLIMAT2_R_zakleni:=Bit_0;
mind_bool[412]:=K1_vklop_izklop_poteka; | [5 empty] | 412:K1_vklop_izklop_poteka:=Bit_0;
mind_bool[413]:=K2_vklop_izklop_poteka; | [5 empty] | 413:K2_vklop_izklop_poteka:=Bit_0;
mind_bool[414]:=N_KlimeAVTO; | [5 empty] | 414:N_KlimeAVTO:=Bit_0;
mind_bool[415]:=UPS[3].AlarmAwaitingPower; | [5 empty] | 415:UPS[3].AlarmAwaitingPower:=Bit_0;
mind_bool[416]:=UPS[3].AlarmBypassBad; | [5 empty] | 416:UPS[3].AlarmBypassBad:=Bit_0;
mind_bool[417]:=UPS[3].AlarmChargerFailed; | [5 empty] | 417:UPS[3].AlarmChargerFailed:=Bit_0;
mind_bool[418]:=UPS[3].AlarmCommunicationsLost; | [5 empty] | 418:UPS[3].AlarmCommunicationsLost:=Bit_0;
mind_bool[419]:=UPS[3].AlarmDepletedBattery; | [5 empty] | 419:UPS[3].AlarmDepletedBattery:=Bit_0;
mind_bool[420]:=UPS[3].AlarmDiagnosticTestFailed; | [5 empty] | 420:UPS[3].AlarmDiagnosticTestFailed:=Bit_0;
mind_bool[421]:=UPS[3].AlarmInverterError; | [5 empty] | 421:UPS[3].AlarmInverterError:=Bit_0;
mind_bool[422]:=UPS[3].AlarmIzhodOffKotZahtevano; | [5 empty] | 422:UPS[3].AlarmIzhodOffKotZahtevano:=Bit_0;
mind_bool[423]:=UPS[3].AlarmIzhodPreobremenjen; | [5 empty] | 423:UPS[3].AlarmIzhodPreobremenjen:=Bit_0;
mind_bool[424]:=UPS[3].AlarmLowBattery; | [5 empty] | 424:UPS[3].AlarmLowBattery:=Bit_0;
mind_bool[425]:=UPS[3].AlarmNapakaNaVarovalki; | [5 empty] | 425:UPS[3].AlarmNapakaNaVarovalki:=Bit_0;
mind_bool[426]:=UPS[3].AlarmNapakaNaVentilatorju; | [5 empty] | 426:UPS[3].AlarmNapakaNaVentilatorju:=Bit_0;
mind_bool[427]:=UPS[3].AlarmOnBattery; | [5 empty] | 427:UPS[3].AlarmOnBattery:=Bit_0;
mind_bool[428]:=UPS[3].AlarmOnBypass; | [5 empty] | 428:UPS[3].AlarmOnBypass:=Bit_0;
mind_bool[429]:=UPS[3].AlarmShutdownImminent; | [5 empty] | 429:UPS[3].AlarmShutdownImminent:=Bit_0;
mind_bool[430]:=UPS[3].AlarmShutdownPending; | [5 empty] | 430:UPS[3].AlarmShutdownPending:=Bit_0;
mind_bool[431]:=UPS[3].AlarmSlabaBaterija; | [5 empty] | 431:UPS[3].AlarmSlabaBaterija:=Bit_0;
mind_bool[432]:=UPS[3].AlarmSplosnaNapaka; | [5 empty] | 432:UPS[3].AlarmSplosnaNapaka:=Bit_0;
mind_bool[433]:=UPS[3].AlarmStanjeIzhodaIzvenToleranc; | [5 empty] | 433:UPS[3].AlarmStanjeIzhodaIzvenToleranc:=Bit_0;
mind_bool[434]:=UPS[3].AlarmStanjeVhodaIzvenToleranc; | [5 empty] | 434:UPS[3].AlarmStanjeVhodaIzvenToleranc:=Bit_0;
mind_bool[435]:=UPS[3].AlarmTemperaturaIzvenToleranc; | [5 empty] | 435:UPS[3].AlarmTemperaturaIzvenToleranc:=Bit_0;
mind_bool[436]:=UPS[3].AlarmTestInProgres; | [5 empty] | 436:UPS[3].AlarmTestInProgres:=Bit_0;
mind_bool[437]:=UPS[3].AlarmUPSIzhodOff; | [5 empty] | 437:UPS[3].AlarmUPSIzhodOff:=Bit_0;
mind_bool[438]:=UPS[3].AlarmUPSOffKotZahtevano; | [5 empty] | 438:UPS[3].AlarmUPSOffKotZahtevano:=Bit_0;
mind_bool[439]:=UPS[3].AlarmUPSSystemOff; | [5 empty] | 439:UPS[3].AlarmUPSSystemOff:=Bit_0;
mind_bool[440]:=UPS[3].Napaka; | [5 empty] | 440:UPS[3].Napaka:=Bit_0;
mind_bool[441]:=UPS[3].StatusEcomodeAktiven; | [5 empty] | 441:UPS[3].StatusEcomodeAktiven:=Bit_0;
mind_bool[442]:=UPS[3].StatusInverterIsOn; | [5 empty] | 442:UPS[3].StatusInverterIsOn:=Bit_0;
mind_bool[443]:=UPS[3].StatusStopOperation; | [5 empty] | 443:UPS[3].StatusStopOperation:=Bit_0;
mind_bool[444]:=ErrComUPS[3]; | [5 empty] | 444:ErrComUPS[3]:=Bit_0;
mind_bool[445]:=GSM_PozCent_napaka; | [5 empty] | 445:GSM_PozCent_napaka:=Bit_0;
mind_bool[446]:=GSM_PozSenzor_okvara; | [5 empty] | 446:GSM_PozSenzor_okvara:=Bit_0;
mind_bool[447]:=GSM_Gasenje_alarm; | [5 empty] | 447:GSM_Gasenje_alarm:=Bit_0;
mind_bool[448]:=AGR_PozCent_napaka; | [5 empty] | 448:AGR_PozCent_napaka:=Bit_0;
mind_bool[449]:=AGR_PozSenzor_okvara; | [5 empty] | 449:AGR_PozSenzor_okvara:=Bit_0;
mind_bool[450]:=AGR_Gasenje_alarm; | [5 empty] | 450:AGR_Gasenje_alarm:=Bit_0;
mind_bool[451]:=Circ_Vpis_Dnevne_energija_scada1; | [5 empty] | 451:Circ_Vpis_Dnevne_energija_scada1:=Bit_0;
mind_bool[452]:=Circ_Vpis_Dnevne_energija_scada2; | [5 empty] | 452:Circ_Vpis_Dnevne_energija_scada2:=Bit_0;
mind_bool[453]:=Circ_Vpis_Tedenska_energija_scada1; | [5 empty] | 453:Circ_Vpis_Tedenska_energija_scada1:=Bit_0;
mind_bool[454]:=Circ_Vpis_Tedenska_energija_scada2; | [5 empty] | 454:Circ_Vpis_Tedenska_energija_scada2:=Bit_0;
mind_bool[455]:=Circ_Vpis_Mesecna_energija_scada1; | [5 empty] | 455:Circ_Vpis_Mesecna_energija_scada1:=Bit_0;
mind_bool[456]:=Circ_Vpis_Mesecna_energija_scada2; | [5 empty] | 456:Circ_Vpis_Mesecna_energija_scada2:=Bit_0;
mind_bool[457]:=PozarnaCentrala_skupno; | [5 empty] | 457:PozarnaCentrala_skupno:=Bit_0;

## XSoft_EXP
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
PROGRAM mod_Read
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*Branje BOOL*)
(**)
mind_bool[0]:=AlarmGenUPS_A_V23;
mind_bool[1]:=AlarmGenUPS_V23;
mind_bool[2]:=AlarmGenUPS_V25;
mind_bool[3]:=AlarmPMM1VirATokPrevisok;
mind_bool[4]:=AlarmPMM1VirATokVisok;
mind_bool[5]:=AlarmPMM1VirBTokPrevisok;
mind_bool[6]:=AlarmPMM1VirBTokVisok;
mind_bool[7]:=AlarmPMM2x17nad80[10];
mind_bool[8]:=AlarmPMM2x17nad80[11];
mind_bool[9]:=AlarmPMM2x17nad80[12];
mind_bool[10]:=AlarmPMM2x17nad80[13];
mind_bool[11]:=AlarmPMM2x17nad80[14];
mind_bool[12]:=AlarmPMM2x17nad80[15];
mind_bool[13]:=AlarmPMM2x17nad80[16];
mind_bool[14]:=AlarmPMM2x17nad80[17];
mind_bool[15]:=AlarmPMM2x17nad80[18];
mind_bool[16]:=AlarmPMM2x17nad80[19];
mind_bool[17]:=AlarmPMM2x17nad80[1];
mind_bool[18]:=AlarmPMM2x17nad80[20];
mind_bool[19]:=AlarmPMM2x17nad80[21];
mind_bool[20]:=AlarmPMM2x17nad80[22];
mind_bool[21]:=AlarmPMM2x17nad80[23];
mind_bool[22]:=AlarmPMM2x17nad80[24];
mind_bool[23]:=AlarmPMM2x17nad80[25];
mind_bool[24]:=AlarmPMM2x17nad80[26];
mind_bool[25]:=AlarmPMM2x17nad80[27];
mind_bool[26]:=AlarmPMM2x17nad80[28];
mind_bool[27]:=AlarmPMM2x17nad80[29];
mind_bool[28]:=AlarmPMM2x17nad80[2];
mind_bool[29]:=AlarmPMM2x17nad80[30];
mind_bool[30]:=AlarmPMM2x17nad80[31];
mind_bool[31]:=AlarmPMM2x17nad80[32];
mind_bool[32]:=AlarmPMM2x17nad80[33];
mind_bool[33]:=AlarmPMM2x17nad80[34];
mind_bool[34]:=AlarmPMM2x17nad80[35];
mind_bool[35]:=AlarmPMM2x17nad80[36];
mind_bool[36]:=AlarmPMM2x17nad80[37];
mind_bool[37]:=AlarmPMM2x17nad80[38];
mind_bool[38]:=AlarmPMM2x17nad80[39];
mind_bool[39]:=AlarmPMM2x17nad80[3];
mind_bool[40]:=AlarmPMM2x17nad80[40];
mind_bool[41]:=AlarmPMM2x17nad80[41];
mind_bool[42]:=AlarmPMM2x17nad80[42];
mind_bool[43]:=AlarmPMM2x17nad80[4];
mind_bool[44]:=AlarmPMM2x17nad80[5];
mind_bool[45]:=AlarmPMM2x17nad80[6];
mind_bool[46]:=AlarmPMM2x17nad80[7];
mind_bool[47]:=AlarmPMM2x17nad80[8];
mind_bool[48]:=AlarmPMM2x17nad80[9];
mind_bool[49]:=ComError;
mind_bool[50]:=ComSCADA;
mind_bool[51]:=ComSCADA1;
mind_bool[52]:=ComSCADA2;
mind_bool[53]:=ComSCADA3;
mind_bool[54]:=ErrComCirc[1];
mind_bool[55]:=ErrComKlima[1];
mind_bool[56]:=ErrComKlima[2];
mind_bool[57]:=ErrComPMM[1];
mind_bool[58]:=ErrComPort2;
mind_bool[59]:=ErrComPort3;
mind_bool[60]:=ErrComPort4;
mind_bool[61]:=ErrComUPS[1];
mind_bool[62]:=ErrComUPS[2];
mind_bool[63]:=ErrComUPSMGE[1];
mind_bool[64]:=ErrorComCirc[1].Error;
mind_bool[65]:=ErrorComKlima[1].Error;
mind_bool[66]:=ErrorComKlima[2].Error;
mind_bool[67]:=ErrorComPMM[1].Error;
mind_bool[68]:=ErrorComUPS[1].Error;
mind_bool[69]:=ErrorComUPS[2].Error;
mind_bool[70]:=ErrorComUPSMGE[1].Error;
mind_bool[71]:=F1_1_zascita_ok;
mind_bool[72]:=K1_SkupnaNapaka;
mind_bool[73]:=K1AlarmPozara;
mind_bool[74]:=K1KlimaZdruzenAlarm;
mind_bool[75]:=K1NiPretoka;
mind_bool[76]:=K1OkvaraRototerma;
mind_bool[77]:=K1OkvaraVlazNap;
mind_bool[78]:=K1PreobMotCrpGr;
mind_bool[79]:=K1PreobMotVent;
mind_bool[80]:=K1ProtizamrzZascAkt;
mind_bool[81]:=K1ZamasenostFiltra;
mind_bool[82]:=K2_SkupnaNapaka;
mind_bool[83]:=K2AlarmPozara;
mind_bool[84]:=K2KlimaZdruzenAlarm;
mind_bool[85]:=K2NiPretoka;
mind_bool[86]:=K2OkvaraRototerma;
mind_bool[87]:=K2OkvaraVlazNap;
mind_bool[88]:=K2PreobMotCrpGr;
mind_bool[89]:=K2PreobMotVent;
mind_bool[90]:=K2ProtizamrzZascAkt;
mind_bool[91]:=K2ZamasenostFiltra;
mind_bool[92]:=K3_deluje;
mind_bool[93]:=K3_SkupnaNapaka;
mind_bool[94]:=Klima1_izkljucena;
mind_bool[95]:=KLIMA1_kke_pogon;
mind_bool[96]:=KLIMA1_krm_nap_ok;
mind_bool[97]:=Klima2_izkljucena;
mind_bool[98]:=Klima3_izkljucena;
mind_bool[99]:=Klima[1].Alarm_pozar;
mind_bool[100]:=Klima[1].DelVentHit1;
mind_bool[101]:=Klima[1].DelVentHit2;
mind_bool[102]:=Klima[1].Ni_pretoka;
mind_bool[103]:=Klima[1].OkvaraRototerm;
mind_bool[104]:=Klima[1].OkvaraVlazNap;
mind_bool[105]:=Klima[1].PreobMotCrpGrel;
mind_bool[106]:=Klima[1].PreobMotVent;
mind_bool[107]:=Klima[1].ProtizamrzZascAktivna;
mind_bool[108]:=Klima[1].VklopRegKlimata;
mind_bool[109]:=Klima[1].ZamasenostFiltra;
mind_bool[110]:=Klima[1].ZdruzAlarmA;
mind_bool[111]:=Klima[1].ZdruzAlarmB;
mind_bool[112]:=Klima[2].Alarm_pozar;
mind_bool[113]:=Klima[2].DelVentHit1;
mind_bool[114]:=Klima[2].DelVentHit2;
mind_bool[115]:=Klima[2].Ni_pretoka;
mind_bool[116]:=Klima[2].OkvaraRototerm;
mind_bool[117]:=Klima[2].OkvaraVlazNap;
mind_bool[118]:=Klima[2].PreobMotCrpGrel;
mind_bool[119]:=Klima[2].PreobMotVent;
mind_bool[120]:=Klima[2].ProtizamrzZascAktivna;
mind_bool[121]:=Klima[2].VklopRegKlimata;
mind_bool[122]:=Klima[2].ZamasenostFiltra;
mind_bool[123]:=Klima[2].ZdruzAlarmA;
mind_bool[124]:=Klima[2].ZdruzAlarmB;
mind_bool[125]:=KLIMA_m1_delovanje;
mind_bool[126]:=KLIMA_m1_napaka;
mind_bool[127]:=KLIMA_m2_delovanje;
mind_bool[128]:=KLIMA_m2_napaka;
mind_bool[129]:=KLIMAT1_delovanje;
mind_bool[130]:=KLIMAT1_napaka;
mind_bool[131]:=KLIMAT1_vklop_delovanja;
mind_bool[132]:=KLIMAT2_delovanje;
mind_bool[133]:=KLIMAT2_napaka;
mind_bool[134]:=KLIMAT2_vklop_delovanja;
mind_bool[135]:=KlimeAVTO;
mind_bool[136]:=N_F1_1_zascita_ok;
mind_bool[137]:=N_KLIMA1_krm_nap_ok;
mind_bool[138]:=N_KLIMAT1_napaka;
mind_bool[139]:=N_KLIMAT2_napaka;
mind_bool[140]:=N_Q12_izpad;
mind_bool[141]:=N_UPS_A_V23_delovanje;
mind_bool[142]:=N_UPS_A_V23_napaka;
mind_bool[143]:=N_UPS_V23_delovanje;
mind_bool[144]:=N_UPS_V23_napaka;
mind_bool[145]:=N_UPS_V25_delovanje;
mind_bool[146]:=N_UPS_V25_napaka;
mind_bool[147]:=N_VLAZILEC1_napaka;
mind_bool[148]:=N_VLAZILEC2_napaka;
mind_bool[149]:=napaka_kom_panel;
mind_bool[150]:=napaka_kom_scada;
mind_bool[151]:=napaka_kom_scada2;
mind_bool[152]:=NapakaSenzorSkupno;
mind_bool[153]:=NapakaSenzorVlagaHIA1;
mind_bool[154]:=NapakaSenzorVlagaHIA2;
mind_bool[155]:=NapakaSenzorVlagaHIA3;
mind_bool[156]:=NapakaSenzorVlagaHIA4;
mind_bool[157]:=NapakaSenzorVlagaHIA5;
mind_bool[158]:=NapakaSenzorVlagaHIA6;
mind_bool[159]:=NapakaSenzorVlagaHIA7;
mind_bool[160]:=NapakaTSTempTIA1;
mind_bool[161]:=NapakaTSTempTIA2;
mind_bool[162]:=NapakaTSTempTIA3;
mind_bool[163]:=NapakaTSTempTIA4;
mind_bool[164]:=NapakaTSTempTIA5;
mind_bool[165]:=NapakaTSTempTIA6;
mind_bool[166]:=NapakaTSTempTIA7;
mind_bool[167]:=OpozoriloPMM2x17med60in80[10];
mind_bool[168]:=OpozoriloPMM2x17med60in80[11];
mind_bool[169]:=OpozoriloPMM2x17med60in80[12];
mind_bool[170]:=OpozoriloPMM2x17med60in80[13];
mind_bool[171]:=OpozoriloPMM2x17med60in80[14];
mind_bool[172]:=OpozoriloPMM2x17med60in80[15];
mind_bool[173]:=OpozoriloPMM2x17med60in80[16];
mind_bool[174]:=OpozoriloPMM2x17med60in80[17];
mind_bool[175]:=OpozoriloPMM2x17med60in80[18];
mind_bool[176]:=OpozoriloPMM2x17med60in80[19];
mind_bool[177]:=OpozoriloPMM2x17med60in80[1];
mind_bool[178]:=OpozoriloPMM2x17med60in80[20];
mind_bool[179]:=OpozoriloPMM2x17med60in80[21];
mind_bool[180]:=OpozoriloPMM2x17med60in80[22];
mind_bool[181]:=OpozoriloPMM2x17med60in80[23];
mind_bool[182]:=OpozoriloPMM2x17med60in80[24];
mind_bool[183]:=OpozoriloPMM2x17med60in80[25];
mind_bool[184]:=OpozoriloPMM2x17med60in80[26];
mind_bool[185]:=OpozoriloPMM2x17med60in80[27];
mind_bool[186]:=OpozoriloPMM2x17med60in80[28];
mind_bool[187]:=OpozoriloPMM2x17med60in80[29];
mind_bool[188]:=OpozoriloPMM2x17med60in80[2];
mind_bool[189]:=OpozoriloPMM2x17med60in80[30];
mind_bool[190]:=OpozoriloPMM2x17med60in80[31];
mind_bool[191]:=OpozoriloPMM2x17med60in80[32];
mind_bool[192]:=OpozoriloPMM2x17med60in80[33];
mind_bool[193]:=OpozoriloPMM2x17med60in80[34];
mind_bool[194]:=OpozoriloPMM2x17med60in80[35];
mind_bool[195]:=OpozoriloPMM2x17med60in80[36];
mind_bool[196]:=OpozoriloPMM2x17med60in80[37];
mind_bool[197]:=OpozoriloPMM2x17med60in80[38];
mind_bool[198]:=OpozoriloPMM2x17med60in80[39];
mind_bool[199]:=OpozoriloPMM2x17med60in80[3];
mind_bool[200]:=OpozoriloPMM2x17med60in80[40];
mind_bool[201]:=OpozoriloPMM2x17med60in80[41];
mind_bool[202]:=OpozoriloPMM2x17med60in80[42];
mind_bool[203]:=OpozoriloPMM2x17med60in80[4];
mind_bool[204]:=OpozoriloPMM2x17med60in80[5];
mind_bool[205]:=OpozoriloPMM2x17med60in80[6];
mind_bool[206]:=OpozoriloPMM2x17med60in80[7];
mind_bool[207]:=OpozoriloPMM2x17med60in80[8];
mind_bool[208]:=OpozoriloPMM2x17med60in80[9];
mind_bool[209]:=PMM1OverCurrentBetw[1];
mind_bool[210]:=PMM1OverCurrentBetw[2];
mind_bool[211]:=PMM1OverCurrentBetw[3];
mind_bool[212]:=PMM1OverCurrentOver[1];
mind_bool[213]:=PMM1OverCurrentOver[2];
mind_bool[214]:=PMM1OverCurrentOver[3];
mind_bool[215]:=PrevisokaTemp;
mind_bool[216]:=Q0_izkljuceno;
mind_bool[217]:=Q0_vkljuceno;
mind_bool[218]:=Q12_izkljuceno;
mind_bool[219]:=Q12_izpad;
mind_bool[220]:=Q12_vkljuceno;
mind_bool[221]:=razlitjeLAH1;
mind_bool[222]:=razlitjeLAH2;
mind_bool[223]:=razlitjeLAH3;
mind_bool[224]:=razlitjeLAH4;
mind_bool[225]:=SetDateTime;
mind_bool[226]:=SetDateTimeDemand;
mind_bool[227]:=SetDateTimeError;
mind_bool[228]:=SetDateTimeFinished;
mind_bool[229]:=SkupneNapakeNaprav_PMM17VirBVirA;
mind_bool[230]:=SlabaBaterijaPLC;
mind_bool[231]:=TempPovp234Previs;
mind_bool[232]:=TempPovp56Previs;
mind_bool[233]:=TIA1_previs_temp;
mind_bool[234]:=TIA2_previs_temp;
mind_bool[235]:=TIA3_previs_temp;
mind_bool[236]:=TIA4_previs_temp;
mind_bool[237]:=TIA5_previs_temp;
mind_bool[238]:=TIA6_previs_temp;
mind_bool[239]:=TIA7_previs_temp;
mind_bool[240]:=UPS1Errors[10];
mind_bool[241]:=UPS1Errors[11];
mind_bool[242]:=UPS1Errors[12];
mind_bool[243]:=UPS1Errors[13];
mind_bool[244]:=UPS1Errors[14];
mind_bool[245]:=UPS1Errors[15];
mind_bool[246]:=UPS1Errors[16];
mind_bool[247]:=UPS1Errors[17];
mind_bool[248]:=UPS1Errors[18];
mind_bool[249]:=UPS1Errors[19];
mind_bool[250]:=UPS1Errors[1];
mind_bool[251]:=UPS1Errors[20];
mind_bool[252]:=UPS1Errors[21];
mind_bool[253]:=UPS1Errors[22];
mind_bool[254]:=UPS1Errors[23];
mind_bool[255]:=UPS1Errors[24];
mind_bool[256]:=UPS1Errors[25];
mind_bool[257]:=UPS1Errors[2];
mind_bool[258]:=UPS1Errors[3];
mind_bool[259]:=UPS1Errors[4];
mind_bool[260]:=UPS1Errors[5];
mind_bool[261]:=UPS1Errors[6];
mind_bool[262]:=UPS1Errors[7];
mind_bool[263]:=UPS1Errors[8];
mind_bool[264]:=UPS1Errors[9];
mind_bool[265]:=UPS2Errors[10];
mind_bool[266]:=UPS2Errors[11];
mind_bool[267]:=UPS2Errors[12];
mind_bool[268]:=UPS2Errors[13];
mind_bool[269]:=UPS2Errors[14];
mind_bool[270]:=UPS2Errors[15];
mind_bool[271]:=UPS2Errors[16];
mind_bool[272]:=UPS2Errors[17];
mind_bool[273]:=UPS2Errors[18];
mind_bool[274]:=UPS2Errors[19];
mind_bool[275]:=UPS2Errors[1];
mind_bool[276]:=UPS2Errors[20];
mind_bool[277]:=UPS2Errors[21];
mind_bool[278]:=UPS2Errors[22];
mind_bool[279]:=UPS2Errors[23];
mind_bool[280]:=UPS2Errors[24];
mind_bool[281]:=UPS2Errors[25];
mind_bool[282]:=UPS2Errors[2];
mind_bool[283]:=UPS2Errors[3];
mind_bool[284]:=UPS2Errors[4];
mind_bool[285]:=UPS2Errors[5];
mind_bool[286]:=UPS2Errors[6];
mind_bool[287]:=UPS2Errors[7];
mind_bool[288]:=UPS2Errors[8];
mind_bool[289]:=UPS2Errors[9];
mind_bool[290]:=UPS[1].AlarmAwaitingPower;
mind_bool[291]:=UPS[1].AlarmBypassBad;
mind_bool[292]:=UPS[1].AlarmChargerFailed;
mind_bool[293]:=UPS[1].AlarmCommunicationsLost;
mind_bool[294]:=UPS[1].AlarmDepletedBattery;
mind_bool[295]:=UPS[1].AlarmDiagnosticTestFailed;
mind_bool[296]:=UPS[1].AlarmInverterError;
mind_bool[297]:=UPS[1].AlarmIzhodOffKotZahtevano;
mind_bool[298]:=UPS[1].AlarmIzhodPreobremenjen;
mind_bool[299]:=UPS[1].AlarmLowBattery;
mind_bool[300]:=UPS[1].AlarmNapakaNaVarovalki;
mind_bool[301]:=UPS[1].AlarmNapakaNaVentilatorju;
mind_bool[302]:=UPS[1].AlarmOnBattery;
mind_bool[303]:=UPS[1].AlarmOnBypass;
mind_bool[304]:=UPS[1].AlarmShutdownImminent;
mind_bool[305]:=UPS[1].AlarmShutdownPending;
mind_bool[306]:=UPS[1].AlarmSlabaBaterija;
mind_bool[307]:=UPS[1].AlarmSplosnaNapaka;
mind_bool[308]:=UPS[1].AlarmStanjeIzhodaIzvenToleranc;
mind_bool[309]:=UPS[1].AlarmStanjeVhodaIzvenToleranc;
mind_bool[310]:=UPS[1].AlarmTemperaturaIzvenToleranc;
mind_bool[311]:=UPS[1].AlarmTestInProgres;
mind_bool[312]:=UPS[1].AlarmUPSIzhodOff;
mind_bool[313]:=UPS[1].AlarmUPSOffKotZahtevano;
mind_bool[314]:=UPS[1].AlarmUPSSystemOff;
mind_bool[315]:=UPS[1].Napaka;
mind_bool[316]:=UPS[1].StatusEcomodeAktiven;
mind_bool[317]:=UPS[1].StatusInverterIsOn;
mind_bool[318]:=UPS[1].StatusStopOperation;
mind_bool[319]:=UPS[2].AlarmAwaitingPower;
mind_bool[320]:=UPS[2].AlarmBypassBad;
mind_bool[321]:=UPS[2].AlarmChargerFailed;
mind_bool[322]:=UPS[2].AlarmCommunicationsLost;
mind_bool[323]:=UPS[2].AlarmDepletedBattery;
mind_bool[324]:=UPS[2].AlarmDiagnosticTestFailed;
mind_bool[325]:=UPS[2].AlarmInverterError;
mind_bool[326]:=UPS[2].AlarmIzhodOffKotZahtevano;
mind_bool[327]:=UPS[2].AlarmIzhodPreobremenjen;
mind_bool[328]:=UPS[2].AlarmLowBattery;
mind_bool[329]:=UPS[2].AlarmNapakaNaVarovalki;
mind_bool[330]:=UPS[2].AlarmNapakaNaVentilatorju;
mind_bool[331]:=UPS[2].AlarmOnBattery;
mind_bool[332]:=UPS[2].AlarmOnBypass;
mind_bool[333]:=UPS[2].AlarmShutdownImminent;
mind_bool[334]:=UPS[2].AlarmShutdownPending;
mind_bool[335]:=UPS[2].AlarmSlabaBaterija;
mind_bool[336]:=UPS[2].AlarmSplosnaNapaka;
mind_bool[337]:=UPS[2].AlarmStanjeIzhodaIzvenToleranc;
mind_bool[338]:=UPS[2].AlarmStanjeVhodaIzvenToleranc;
mind_bool[339]:=UPS[2].AlarmTemperaturaIzvenToleranc;
mind_bool[340]:=UPS[2].AlarmTestInProgres;
mind_bool[341]:=UPS[2].AlarmUPSIzhodOff;
mind_bool[342]:=UPS[2].AlarmUPSOffKotZahtevano;
mind_bool[343]:=UPS[2].AlarmUPSSystemOff;
mind_bool[344]:=UPS[2].Napaka;
mind_bool[345]:=UPS[2].StatusEcomodeAktiven;
mind_bool[346]:=UPS[2].StatusInverterIsOn;
mind_bool[347]:=UPS[2].StatusStopOperation;
mind_bool[348]:=UPS_A_V23_delovanje;
mind_bool[349]:=UPS_A_V23_napaka;
mind_bool[350]:=ups_alarm;
mind_bool[351]:=ups_baterijski_nac;
mind_bool[352]:=UPS_MGE[1].BatteryChargedState;
mind_bool[353]:=UPS_MGE[1].BatteryCircuitBreaker;
mind_bool[354]:=UPS_MGE[1].BatteryCompInProgress;
mind_bool[355]:=UPS_MGE[1].BatteryFuseFault;
mind_bool[356]:=UPS_MGE[1].BatteryLowWarning;
mind_bool[357]:=UPS_MGE[1].BatteryTempOutOfToler;
mind_bool[358]:=UPS_MGE[1].BypassInFreeFrequency;
mind_bool[359]:=UPS_MGE[1].ChargerGeneralFault;
mind_bool[360]:=UPS_MGE[1].DeviceVentilationFault;
mind_bool[361]:=UPS_MGE[1].InverterFuseFault;
mind_bool[362]:=UPS_MGE[1].InverterOverload;
mind_bool[363]:=UPS_MGE[1].InverterThermalOverload;
mind_bool[364]:=UPS_MGE[1].Mains1VoltOutOfToler;
mind_bool[365]:=UPS_MGE[1].Mains2Overload;
mind_bool[366]:=UPS_MGE[1].Mains2VoltOutOfToler;
mind_bool[367]:=UPS_MGE[1].MaintenancePosition;
mind_bool[368]:=UPS_MGE[1].ManualBypassSwitch;
mind_bool[369]:=UPS_MGE[1].NapakaNaVarovalkah;
mind_bool[370]:=UPS_MGE[1].OutputInShortCircuit;
mind_bool[371]:=UPS_MGE[1].OutputOverload;
mind_bool[372]:=UPS_MGE[1].OutputThermalOverload;
mind_bool[373]:=UPS_MGE[1].RectifierOn;
mind_bool[374]:=UPS_MGE[1].RectifierThermOverload;
mind_bool[375]:=UPS_MGE[1].Skupna_napaka;
mind_bool[376]:=UPS_MGE[1].UPS_coupled;
mind_bool[377]:=UPS_MGE[1].UPS_error;
mind_bool[378]:=UPS_MGE[1].UPS_in_backup;
mind_bool[379]:=ups_polnjenje;
mind_bool[380]:=UPS_V23_delovanje;
mind_bool[381]:=UPS_V23_napaka;
mind_bool[382]:=UPS_V25_delovanje;
mind_bool[383]:=UPS_V25_napaka;
mind_bool[384]:=UPSMGEErrors[10];
mind_bool[385]:=UPSMGEErrors[11];
mind_bool[386]:=UPSMGEErrors[12];
mind_bool[387]:=UPSMGEErrors[13];
mind_bool[388]:=UPSMGEErrors[14];
mind_bool[389]:=UPSMGEErrors[15];
mind_bool[390]:=UPSMGEErrors[16];
mind_bool[391]:=UPSMGEErrors[17];
mind_bool[392]:=UPSMGEErrors[1];
mind_bool[393]:=UPSMGEErrors[2];
mind_bool[394]:=UPSMGEErrors[3];
mind_bool[395]:=UPSMGEErrors[4];
mind_bool[396]:=UPSMGEErrors[5];
mind_bool[397]:=UPSMGEErrors[6];
mind_bool[398]:=UPSMGEErrors[7];
mind_bool[399]:=UPSMGEErrors[8];
mind_bool[400]:=UPSMGEErrors[9];
mind_bool[401]:=UserLoggedIn;
mind_bool[402]:=VLAZILEC1_delovanje;
mind_bool[403]:=VLAZILEC1_napaka;
mind_bool[404]:=VLAZILEC2_delovanje;
mind_bool[405]:=VLAZILEC2_napaka;
mind_bool[406]:=XVH_AlarmOn;
mind_bool[407]:=XVH_enopolna_napaka;
mind_bool[408]:=KLIMAT1_vklop_delovanjaR;
mind_bool[409]:=KLIMAT2_vklop_delovanjaR;
mind_bool[410]:=KLIMAT1_R_zakleni;
mind_bool[411]:=KLIMAT2_R_zakleni;
mind_bool[412]:=K1_vklop_izklop_poteka;
mind_bool[413]:=K2_vklop_izklop_poteka;
mind_bool[414]:=N_KlimeAVTO;
mind_bool[415]:=UPS[3].AlarmAwaitingPower;
mind_bool[416]:=UPS[3].AlarmBypassBad;
mind_bool[417]:=UPS[3].AlarmChargerFailed;
mind_bool[418]:=UPS[3].AlarmCommunicationsLost;
mind_bool[419]:=UPS[3].AlarmDepletedBattery;
mind_bool[420]:=UPS[3].AlarmDiagnosticTestFailed;
mind_bool[421]:=UPS[3].AlarmInverterError;
mind_bool[422]:=UPS[3].AlarmIzhodOffKotZahtevano;
mind_bool[423]:=UPS[3].AlarmIzhodPreobremenjen;
mind_bool[424]:=UPS[3].AlarmLowBattery;
mind_bool[425]:=UPS[3].AlarmNapakaNaVarovalki;
mind_bool[426]:=UPS[3].AlarmNapakaNaVentilatorju;
mind_bool[427]:=UPS[3].AlarmOnBattery;
mind_bool[428]:=UPS[3].AlarmOnBypass;
mind_bool[429]:=UPS[3].AlarmShutdownImminent;
mind_bool[430]:=UPS[3].AlarmShutdownPending;
mind_bool[431]:=UPS[3].AlarmSlabaBaterija;
mind_bool[432]:=UPS[3].AlarmSplosnaNapaka;
mind_bool[433]:=UPS[3].AlarmStanjeIzhodaIzvenToleranc;
mind_bool[434]:=UPS[3].AlarmStanjeVhodaIzvenToleranc;
mind_bool[435]:=UPS[3].AlarmTemperaturaIzvenToleranc;
mind_bool[436]:=UPS[3].AlarmTestInProgres;
mind_bool[437]:=UPS[3].AlarmUPSIzhodOff;
mind_bool[438]:=UPS[3].AlarmUPSOffKotZahtevano;
mind_bool[439]:=UPS[3].AlarmUPSSystemOff;
mind_bool[440]:=UPS[3].Napaka;
mind_bool[441]:=UPS[3].StatusEcomodeAktiven;
mind_bool[442]:=UPS[3].StatusInverterIsOn;
mind_bool[443]:=UPS[3].StatusStopOperation;
mind_bool[444]:=ErrComUPS[3];
mind_bool[445]:=GSM_PozCent_napaka;
mind_bool[446]:=GSM_PozSenzor_okvara;
mind_bool[447]:=GSM_Gasenje_alarm;
mind_bool[448]:=AGR_PozCent_napaka;
mind_bool[449]:=AGR_PozSenzor_okvara;
mind_bool[450]:=AGR_Gasenje_alarm;
mind_bool[451]:=Circ_Vpis_Dnevne_energija_scada1;
mind_bool[452]:=Circ_Vpis_Dnevne_energija_scada2;
mind_bool[453]:=Circ_Vpis_Tedenska_energija_scada1;
mind_bool[454]:=Circ_Vpis_Tedenska_energija_scada2;
mind_bool[455]:=Circ_Vpis_Mesecna_energija_scada1;
mind_bool[456]:=Circ_Vpis_Mesecna_energija_scada2;
mind_bool[457]:=PozarnaCentrala_skupno;
(*Branje INT*)
(**)
mind[0]:=DateTime.Dan;
mind[1]:=DateTime.Leto;
mind[2]:=DateTime.Leto2;
mind[3]:=DateTime.Mesec;
mind[4]:=DateTime.Minuta;
mind[5]:=DateTime.Sekunda;
mind[6]:=DateTime.Ura;
mind[7]:=ErrorComCirc[1].Code[10];
mind[8]:=ErrorComCirc[1].Code[11];
mind[9]:=ErrorComCirc[1].Code[12];
mind[10]:=ErrorComCirc[1].Code[13];
mind[11]:=ErrorComCirc[1].Code[14];
mind[12]:=ErrorComCirc[1].Code[15];
mind[13]:=ErrorComCirc[1].Code[1];
mind[14]:=ErrorComCirc[1].Code[2];
mind[15]:=ErrorComCirc[1].Code[3];
mind[16]:=ErrorComCirc[1].Code[4];
mind[17]:=ErrorComCirc[1].Code[5];
mind[18]:=ErrorComCirc[1].Code[6];
mind[19]:=ErrorComCirc[1].Code[7];
mind[20]:=ErrorComCirc[1].Code[8];
mind[21]:=ErrorComCirc[1].Code[9];
mind[22]:=ErrorComCirc[1].Status;
mind[23]:=ErrorComKlima[1].Code[10];
mind[24]:=ErrorComKlima[1].Code[11];
mind[25]:=ErrorComKlima[1].Code[12];
mind[26]:=ErrorComKlima[1].Code[13];
mind[27]:=ErrorComKlima[1].Code[14];
mind[28]:=ErrorComKlima[1].Code[15];
mind[29]:=ErrorComKlima[1].Code[1];
mind[30]:=ErrorComKlima[1].Code[2];
mind[31]:=ErrorComKlima[1].Code[3];
mind[32]:=ErrorComKlima[1].Code[4];
mind[33]:=ErrorComKlima[1].Code[5];
mind[34]:=ErrorComKlima[1].Code[6];
mind[35]:=ErrorComKlima[1].Code[7];
mind[36]:=ErrorComKlima[1].Code[8];
mind[37]:=ErrorComKlima[1].Code[9];
mind[38]:=ErrorComKlima[1].Status;
mind[39]:=ErrorComKlima[2].Code[10];
mind[40]:=ErrorComKlima[2].Code[11];
mind[41]:=ErrorComKlima[2].Code[12];
mind[42]:=ErrorComKlima[2].Code[13];
mind[43]:=ErrorComKlima[2].Code[14];
mind[44]:=ErrorComKlima[2].Code[15];
mind[45]:=ErrorComKlima[2].Code[1];
mind[46]:=ErrorComKlima[2].Code[2];
mind[47]:=ErrorComKlima[2].Code[3];
mind[48]:=ErrorComKlima[2].Code[4];
mind[49]:=ErrorComKlima[2].Code[5];
mind[50]:=ErrorComKlima[2].Code[6];
mind[51]:=ErrorComKlima[2].Code[7];
mind[52]:=ErrorComKlima[2].Code[8];
mind[53]:=ErrorComKlima[2].Code[9];
mind[54]:=ErrorComKlima[2].Status;
mind[55]:=ErrorComPMM[1].Code[10];
mind[56]:=ErrorComPMM[1].Code[11];
mind[57]:=ErrorComPMM[1].Code[12];
mind[58]:=ErrorComPMM[1].Code[13];
mind[59]:=ErrorComPMM[1].Code[14];
mind[60]:=ErrorComPMM[1].Code[15];
mind[61]:=ErrorComPMM[1].Code[1];
mind[62]:=ErrorComPMM[1].Code[2];
mind[63]:=ErrorComPMM[1].Code[3];
mind[64]:=ErrorComPMM[1].Code[4];
mind[65]:=ErrorComPMM[1].Code[5];
mind[66]:=ErrorComPMM[1].Code[6];
mind[67]:=ErrorComPMM[1].Code[7];
mind[68]:=ErrorComPMM[1].Code[8];
mind[69]:=ErrorComPMM[1].Code[9];
mind[70]:=ErrorComPMM[1].Status;
mind[71]:=ErrorComUPS[1].Code[10];
mind[72]:=ErrorComUPS[1].Code[11];
mind[73]:=ErrorComUPS[1].Code[12];
mind[74]:=ErrorComUPS[1].Code[13];
mind[75]:=ErrorComUPS[1].Code[14];
mind[76]:=ErrorComUPS[1].Code[15];
mind[77]:=ErrorComUPS[1].Code[1];
mind[78]:=ErrorComUPS[1].Code[2];
mind[79]:=ErrorComUPS[1].Code[3];
mind[80]:=ErrorComUPS[1].Code[4];
mind[81]:=ErrorComUPS[1].Code[5];
mind[82]:=ErrorComUPS[1].Code[6];
mind[83]:=ErrorComUPS[1].Code[7];
mind[84]:=ErrorComUPS[1].Code[8];
mind[85]:=ErrorComUPS[1].Code[9];
mind[86]:=ErrorComUPS[1].Status;
mind[87]:=ErrorComUPS[2].Code[10];
mind[88]:=ErrorComUPS[2].Code[11];
mind[89]:=ErrorComUPS[2].Code[12];
mind[90]:=ErrorComUPS[2].Code[13];
mind[91]:=ErrorComUPS[2].Code[14];
mind[92]:=ErrorComUPS[2].Code[15];
mind[93]:=ErrorComUPS[2].Code[1];
mind[94]:=ErrorComUPS[2].Code[2];
mind[95]:=ErrorComUPS[2].Code[3];
mind[96]:=ErrorComUPS[2].Code[4];
mind[97]:=ErrorComUPS[2].Code[5];
mind[98]:=ErrorComUPS[2].Code[6];
mind[99]:=ErrorComUPS[2].Code[7];
mind[100]:=ErrorComUPS[2].Code[8];
mind[101]:=ErrorComUPS[2].Code[9];
mind[102]:=ErrorComUPS[2].Status;
mind[103]:=ErrorComUPSMGE[1].Code[10];
mind[104]:=ErrorComUPSMGE[1].Code[11];
mind[105]:=ErrorComUPSMGE[1].Code[12];
mind[106]:=ErrorComUPSMGE[1].Code[13];
mind[107]:=ErrorComUPSMGE[1].Code[14];
mind[108]:=ErrorComUPSMGE[1].Code[15];
mind[109]:=ErrorComUPSMGE[1].Code[1];
mind[110]:=ErrorComUPSMGE[1].Code[2];
mind[111]:=ErrorComUPSMGE[1].Code[3];
mind[112]:=ErrorComUPSMGE[1].Code[4];
mind[113]:=ErrorComUPSMGE[1].Code[5];
mind[114]:=ErrorComUPSMGE[1].Code[6];
mind[115]:=ErrorComUPSMGE[1].Code[7];
mind[116]:=ErrorComUPSMGE[1].Code[8];
mind[117]:=ErrorComUPSMGE[1].Code[9];
mind[118]:=ErrorComUPSMGE[1].Status;
mind[119]:=HIA1_vlaga_s;
mind[120]:=HIA2_vlaga_s;
mind[121]:=HIA3_vlaga_s;
mind[122]:=HIA4_vlaga_s;
mind[123]:=HIA5_vlaga_s;
mind[124]:=HIA6_vlaga_s;
mind[125]:=HIA7_vlaga_s;
mind[126]:=Klima[1].Analog_izh_mesanje;
mind[127]:=Klima[1].Analog_izh_rekuperator;
mind[128]:=Klima[1].Analog_izh_VentGrelnika;
mind[129]:=Klima[1].Analog_izh_VentHlajenja;
mind[130]:=Klima[1].Dejanska_zel_temp;
mind[131]:=Klima[1].Hitrost_del_vent_disp;
mind[132]:=Klima[1].Max_vpih;
mind[133]:=Klima[1].Min_vpih;
mind[134]:=Klima[1].Obrat_ure_Vent_h1;
mind[135]:=Klima[1].Obrat_ure_Vent_h2;
mind[136]:=Klima[1].Pol_komp_konec;
mind[137]:=Klima[1].Pol_komp_sprem_zel_vr;
mind[138]:=Klima[1].Pol_komp_zacetek;
mind[139]:=Klima[1].PreklopHitDelVent;
mind[140]:=Klima[1].Protizamrz_zascita;
mind[141]:=Klima[1].Rezim_delovanja;
mind[142]:=Klima[1].Temperatura_dovoda;
mind[143]:=Klima[1].Temperatura_prostora;
mind[144]:=Klima[1].TempPredPloscnimRekup;
mind[145]:=Klima[1].TempZaPloscnimRekup;
mind[146]:=Klima[1].Vlaga_v_prostoru;
mind[147]:=Klima[1].VlagaVstopZrakaProstor;
mind[148]:=Klima[1].Zel_temp_eko_gretja;
mind[149]:=Klima[1].Zel_temp_eko_hlajenja;
mind[150]:=Klima[1].Zel_temp_komf_gretja;
mind[151]:=Klima[1].Zel_temp_komf_hlajenja;
mind[152]:=Klima[1].Zim_komp_konec;
mind[153]:=Klima[1].Zim_komp_sprem_zel_vr;
mind[154]:=Klima[1].Zim_komp_zacetek;
mind[155]:=Klima[1].ZimKompMinVpihKonec;
mind[156]:=Klima[1].ZimKompMinVpihZac;
mind[157]:=Klima[1].ZkompMinVpihSpremZelVr;
mind[158]:=Klima[1].Zunanja_temp;
mind[159]:=Klima[2].Analog_izh_mesanje;
mind[160]:=Klima[2].Analog_izh_rekuperator;
mind[161]:=Klima[2].Analog_izh_VentGrelnika;
mind[162]:=Klima[2].Analog_izh_VentHlajenja;
mind[163]:=Klima[2].Dejanska_zel_temp;
mind[164]:=Klima[2].Hitrost_del_vent_disp;
mind[165]:=Klima[2].Max_vpih;
mind[166]:=Klima[2].Min_vpih;
mind[167]:=Klima[2].Obrat_ure_Vent_h1;
mind[168]:=Klima[2].Obrat_ure_Vent_h2;
mind[169]:=Klima[2].Pol_komp_konec;
mind[170]:=Klima[2].Pol_komp_sprem_zel_vr;
mind[171]:=Klima[2].Pol_komp_zacetek;
mind[172]:=Klima[2].PreklopHitDelVent;
mind[173]:=Klima[2].Protizamrz_zascita;
mind[174]:=Klima[2].Rezim_delovanja;
mind[175]:=Klima[2].Temperatura_dovoda;
mind[176]:=Klima[2].Temperatura_prostora;
mind[177]:=Klima[2].TempPredPloscnimRekup;
mind[178]:=Klima[2].TempZaPloscnimRekup;
mind[179]:=Klima[2].Vlaga_v_prostoru;
mind[180]:=Klima[2].VlagaVstopZrakaProstor;
mind[181]:=Klima[2].Zel_temp_eko_gretja;
mind[182]:=Klima[2].Zel_temp_eko_hlajenja;
mind[183]:=Klima[2].Zel_temp_komf_gretja;
mind[184]:=Klima[2].Zel_temp_komf_hlajenja;
mind[185]:=Klima[2].Zim_komp_konec;
mind[186]:=Klima[2].Zim_komp_sprem_zel_vr;
mind[187]:=Klima[2].Zim_komp_zacetek;
mind[188]:=Klima[2].ZimKompMinVpihKonec;
mind[189]:=Klima[2].ZimKompMinVpihZac;
mind[190]:=Klima[2].ZkompMinVpihSpremZelVr;
mind[191]:=Klima[2].Zunanja_temp;
mind[192]:=KlimaIzklopObrUre;
mind[193]:=PMM[1].AlarmPhase[1].GlobalAlarmReg;
mind[194]:=PMM[1].AlarmPhase[2].GlobalAlarmReg;
mind[195]:=PMM[1].AlarmPhase[3].GlobalAlarmReg;
mind[196]:=Q12stanje;
mind[197]:=TempHistereza;
mind[198]:=TempPovp234;
mind[199]:=TempPovp234Alarm;
mind[200]:=TempPovp56;
mind[201]:=TempPovp56Alarm;
mind[202]:=TempZaVklopKlim1;
mind[203]:=TempZaVklopKlim2;
mind[204]:=TIA1_alarm;
mind[205]:=TIA1_temp_s;
mind[206]:=TIA2_alarm;
mind[207]:=TIA2_temp_s;
mind[208]:=TIA3_alarm;
mind[209]:=TIA3_temp_s;
mind[210]:=TIA4_alarm;
mind[211]:=TIA4_temp_s;
mind[212]:=TIA5_alarm;
mind[213]:=TIA5_temp_s;
mind[214]:=TIA6_alarm;
mind[215]:=TIA6_temp_s;
mind[216]:=TIA7_alarm;
mind[217]:=TIA7_temp_s;
mind[218]:=UPS[1].InverterStatus;
mind[219]:=UPS[1].OutputStatus;
mind[220]:=UPS[1].SteviloIzpadovVhodneLinije;
mind[221]:=UPS[1].UnitStatus;
mind[222]:=UPS[2].InverterStatus;
mind[223]:=UPS[2].OutputStatus;
mind[224]:=UPS[2].SteviloIzpadovVhodneLinije;
mind[225]:=UPS[2].UnitStatus;
mind[226]:=UPS_MGE[1].BatteryBackupTime;
mind[227]:=UPS_MGE[1].BatteryChargingLevel;
mind[228]:=UPS_MGE[1].BatteryRechargeDuration;
mind[229]:=UPS_MGE[1].I1output;
mind[230]:=UPS_MGE[1].I2output;
mind[231]:=UPS_MGE[1].I3output;
mind[232]:=UPS_MGE[1].InverterFrequency;
mind[233]:=UPS_MGE[1].OutputActivePower1;
mind[234]:=UPS_MGE[1].OutputActivePower2;
mind[235]:=UPS_MGE[1].OutputActivePower3;
mind[236]:=UPS_MGE[1].OutputFrequency;
mind[237]:=UPS_MGE[1].OutputLoadLevel;
mind[238]:=UPS_MGE[1].StatusBaterije;
mind[239]:=UPS_MGE[1].U12mains1;
mind[240]:=UPS_MGE[1].U12mains2;
mind[241]:=UPS_MGE[1].U1N_inverter;
mind[242]:=UPS_MGE[1].U1N_output;
mind[243]:=UPS_MGE[1].U23mains1;
mind[244]:=UPS_MGE[1].U23mains2;
mind[245]:=UPS_MGE[1].U2N_inverter;
mind[246]:=UPS_MGE[1].U2N_output;
mind[247]:=UPS_MGE[1].U31mains1;
mind[248]:=UPS_MGE[1].U31mains2;
mind[249]:=UPS_MGE[1].U3N_inverter;
mind[250]:=UPS_MGE[1].U3N_output;
mind[251]:=UPS_MGE[1].U_battery;
mind[252]:=UserCurrentLevel;
mind[253]:=XVH_UPSstatus;
mind[254]:=UPS[3].InverterStatus;
mind[255]:=UPS[3].OutputStatus;
mind[256]:=UPS[3].SteviloIzpadovVhodneLinije;
mind[257]:=UPS[3].UnitStatus;
(*Branje UINT*)
(**)
mind[6000]:=kom_nast_cas_izpada;
mind[6001]:=PMM[1].AlarmPhase[1].C01_16_60to80;
mind[6002]:=PMM[1].AlarmPhase[1].C01_16_over80;
mind[6003]:=PMM[1].AlarmPhase[1].C17_32_60to80;
mind[6004]:=PMM[1].AlarmPhase[1].C17_32_over80;
mind[6005]:=PMM[1].AlarmPhase[1].C33_42_60to80;
mind[6006]:=PMM[1].AlarmPhase[1].C33_42_over80;
mind[6007]:=PMM[1].AlarmPhase[2].C01_16_60to80;
mind[6008]:=PMM[1].AlarmPhase[2].C01_16_over80;
mind[6009]:=PMM[1].AlarmPhase[2].C17_32_60to80;
mind[6010]:=PMM[1].AlarmPhase[2].C17_32_over80;
mind[6011]:=PMM[1].AlarmPhase[2].C33_42_60to80;
mind[6012]:=PMM[1].AlarmPhase[2].C33_42_over80;
mind[6013]:=PMM[1].AlarmPhase[3].C01_16_60to80;
mind[6014]:=PMM[1].AlarmPhase[3].C01_16_over80;
mind[6015]:=PMM[1].AlarmPhase[3].C17_32_60to80;
mind[6016]:=PMM[1].AlarmPhase[3].C17_32_over80;
mind[6017]:=PMM[1].AlarmPhase[3].C33_42_60to80;
mind[6018]:=PMM[1].AlarmPhase[3].C33_42_over80;
mind[6019]:=UPS[1].StatusBaterije;
mind[6020]:=UPS[2].StatusBaterije;
mind[6021]:=K1_obr_u_skupno;
mind[6022]:=K2_obr_u_skupno;
mind[6023]:=UPS[3].StatusBaterije;
(*Branje LONG*)
(**)
(*Branje REAL*)
(**)
Read_Real(rVar:=Circ[1].CosFi_III,lo:=4000,hi:=4001);
Read_Real(rVar:=Circ[1].DelovnaEnergija,lo:=4002,hi:=4003);
Read_Real(rVar:=Circ[1].DelovnaMoc_III,lo:=4004,hi:=4005);
Read_Real(rVar:=Circ[1].DelovnaMoc_L1,lo:=4006,hi:=4007);
Read_Real(rVar:=Circ[1].DelovnaMoc_L2,lo:=4008,hi:=4009);
Read_Real(rVar:=Circ[1].DelovnaMoc_L3,lo:=4010,hi:=4011);
Read_Real(rVar:=Circ[1].Frekvenca_L1,lo:=4012,hi:=4013);
Read_Real(rVar:=Circ[1].InduktivnaEnergija,lo:=4014,hi:=4015);
Read_Real(rVar:=Circ[1].InduktivnaMoc_III,lo:=4016,hi:=4017);
Read_Real(rVar:=Circ[1].JalovaMoc_L1,lo:=4018,hi:=4019);
Read_Real(rVar:=Circ[1].JalovaMoc_L2,lo:=4020,hi:=4021);
Read_Real(rVar:=Circ[1].JalovaMoc_L3,lo:=4022,hi:=4023);
Read_Real(rVar:=Circ[1].KapacitivnaEnergija,lo:=4024,hi:=4025);
Read_Real(rVar:=Circ[1].KapacitivnaMoc_III,lo:=4026,hi:=4027);
Read_Real(rVar:=Circ[1].MaximumDemand,lo:=4028,hi:=4029);
Read_Real(rVar:=Circ[1].Napetost_L1_L2,lo:=4030,hi:=4031);
Read_Real(rVar:=Circ[1].Napetost_L1_N,lo:=4032,hi:=4033);
Read_Real(rVar:=Circ[1].Napetost_L2_L3,lo:=4034,hi:=4035);
Read_Real(rVar:=Circ[1].Napetost_L2_N,lo:=4036,hi:=4037);
Read_Real(rVar:=Circ[1].Napetost_L3_L1,lo:=4038,hi:=4039);
Read_Real(rVar:=Circ[1].Napetost_L3_N,lo:=4040,hi:=4041);
Read_Real(rVar:=Circ[1].NavideznaMoc_III,lo:=4042,hi:=4043);
Read_Real(rVar:=Circ[1].NicelniTok,lo:=4044,hi:=4045);
Read_Real(rVar:=Circ[1].PowerFactor_III,lo:=4046,hi:=4047);
Read_Real(rVar:=Circ[1].PowerFactor_L1,lo:=4048,hi:=4049);
Read_Real(rVar:=Circ[1].PowerFactor_L2,lo:=4050,hi:=4051);
Read_Real(rVar:=Circ[1].PowerFactor_L3,lo:=4052,hi:=4053);
Read_Real(rVar:=Circ[1].THDI_L1,lo:=4054,hi:=4055);
Read_Real(rVar:=Circ[1].THDI_L2,lo:=4056,hi:=4057);
Read_Real(rVar:=Circ[1].THDI_L3,lo:=4058,hi:=4059);
Read_Real(rVar:=Circ[1].THDV_L1,lo:=4060,hi:=4061);
Read_Real(rVar:=Circ[1].THDV_L2,lo:=4062,hi:=4063);
Read_Real(rVar:=Circ[1].THDV_L3,lo:=4064,hi:=4065);
Read_Real(rVar:=Circ[1].Tok_L1,lo:=4066,hi:=4067);
Read_Real(rVar:=Circ[1].Tok_L2,lo:=4068,hi:=4069);
Read_Real(rVar:=Circ[1].Tok_L3,lo:=4070,hi:=4071);
Read_Real(rVar:=Circ[1].TokPovprecje_III,lo:=4072,hi:=4073);
Read_Real(rVar:=PMM[1].ActiveEnergyConsumed_kWh,lo:=4074,hi:=4075);
Read_Real(rVar:=PMM[1].ActivePowerPhaseA_kW,lo:=4076,hi:=4077);
Read_Real(rVar:=PMM[1].ActivePowerPhaseB_kW,lo:=4078,hi:=4079);
Read_Real(rVar:=PMM[1].ActivePowerPhaseC_kW,lo:=4080,hi:=4081);
Read_Real(rVar:=PMM[1].AparentPowerPhaseA,lo:=4082,hi:=4083);
Read_Real(rVar:=PMM[1].AparentPowerPhaseB,lo:=4084,hi:=4085);
Read_Real(rVar:=PMM[1].AparentPowerPhaseC,lo:=4086,hi:=4087);
Read_Real(rVar:=PMM[1].AverageCurrent_A,lo:=4088,hi:=4089);
Read_Real(rVar:=PMM[1].AveragePhaseToNeutral_V,lo:=4090,hi:=4091);
Read_Real(rVar:=PMM[1].AveragePhaseToPhase_V,lo:=4092,hi:=4093);
Read_Real(rVar:=PMM[1].CurrentInPhaseA_A,lo:=4094,hi:=4095);
Read_Real(rVar:=PMM[1].CurrentInPhaseB_A,lo:=4096,hi:=4097);
Read_Real(rVar:=PMM[1].CurrentInPhaseC_A,lo:=4098,hi:=4099);
Read_Real(rVar:=PMM[1].Frequency_Hz,lo:=4100,hi:=4101);
Read_Real(rVar:=PMM[1].Phase[1].Current[10],lo:=4102,hi:=4103);
Read_Real(rVar:=PMM[1].Phase[1].Current[11],lo:=4104,hi:=4105);
Read_Real(rVar:=PMM[1].Phase[1].Current[12],lo:=4106,hi:=4107);
Read_Real(rVar:=PMM[1].Phase[1].Current[13],lo:=4108,hi:=4109);
Read_Real(rVar:=PMM[1].Phase[1].Current[14],lo:=4110,hi:=4111);
Read_Real(rVar:=PMM[1].Phase[1].Current[15],lo:=4112,hi:=4113);
Read_Real(rVar:=PMM[1].Phase[1].Current[16],lo:=4114,hi:=4115);
Read_Real(rVar:=PMM[1].Phase[1].Current[17],lo:=4116,hi:=4117);
Read_Real(rVar:=PMM[1].Phase[1].Current[18],lo:=4118,hi:=4119);
Read_Real(rVar:=PMM[1].Phase[1].Current[19],lo:=4120,hi:=4121);
Read_Real(rVar:=PMM[1].Phase[1].Current[1],lo:=4122,hi:=4123);
Read_Real(rVar:=PMM[1].Phase[1].Current[20],lo:=4124,hi:=4125);
Read_Real(rVar:=PMM[1].Phase[1].Current[21],lo:=4126,hi:=4127);
Read_Real(rVar:=PMM[1].Phase[1].Current[22],lo:=4128,hi:=4129);
Read_Real(rVar:=PMM[1].Phase[1].Current[23],lo:=4130,hi:=4131);
Read_Real(rVar:=PMM[1].Phase[1].Current[24],lo:=4132,hi:=4133);
Read_Real(rVar:=PMM[1].Phase[1].Current[25],lo:=4134,hi:=4135);
Read_Real(rVar:=PMM[1].Phase[1].Current[26],lo:=4136,hi:=4137);
Read_Real(rVar:=PMM[1].Phase[1].Current[27],lo:=4138,hi:=4139);
Read_Real(rVar:=PMM[1].Phase[1].Current[28],lo:=4140,hi:=4141);
Read_Real(rVar:=PMM[1].Phase[1].Current[29],lo:=4142,hi:=4143);
Read_Real(rVar:=PMM[1].Phase[1].Current[2],lo:=4144,hi:=4145);
Read_Real(rVar:=PMM[1].Phase[1].Current[30],lo:=4146,hi:=4147);
Read_Real(rVar:=PMM[1].Phase[1].Current[31],lo:=4148,hi:=4149);
Read_Real(rVar:=PMM[1].Phase[1].Current[32],lo:=4150,hi:=4151);
Read_Real(rVar:=PMM[1].Phase[1].Current[33],lo:=4152,hi:=4153);
Read_Real(rVar:=PMM[1].Phase[1].Current[34],lo:=4154,hi:=4155);
Read_Real(rVar:=PMM[1].Phase[1].Current[35],lo:=4156,hi:=4157);
Read_Real(rVar:=PMM[1].Phase[1].Current[36],lo:=4158,hi:=4159);
Read_Real(rVar:=PMM[1].Phase[1].Current[37],lo:=4160,hi:=4161);
Read_Real(rVar:=PMM[1].Phase[1].Current[38],lo:=4162,hi:=4163);
Read_Real(rVar:=PMM[1].Phase[1].Current[39],lo:=4164,hi:=4165);
Read_Real(rVar:=PMM[1].Phase[1].Current[3],lo:=4166,hi:=4167);
Read_Real(rVar:=PMM[1].Phase[1].Current[40],lo:=4168,hi:=4169);
Read_Real(rVar:=PMM[1].Phase[1].Current[41],lo:=4170,hi:=4171);
Read_Real(rVar:=PMM[1].Phase[1].Current[42],lo:=4172,hi:=4173);
Read_Real(rVar:=PMM[1].Phase[1].Current[4],lo:=4174,hi:=4175);
Read_Real(rVar:=PMM[1].Phase[1].Current[5],lo:=4176,hi:=4177);
Read_Real(rVar:=PMM[1].Phase[1].Current[6],lo:=4178,hi:=4179);
Read_Real(rVar:=PMM[1].Phase[1].Current[7],lo:=4180,hi:=4181);
Read_Real(rVar:=PMM[1].Phase[1].Current[8],lo:=4182,hi:=4183);
Read_Real(rVar:=PMM[1].Phase[1].Current[9],lo:=4184,hi:=4185);
Read_Real(rVar:=PMM[1].Phase[2].Current[10],lo:=4186,hi:=4187);
Read_Real(rVar:=PMM[1].Phase[2].Current[11],lo:=4188,hi:=4189);
Read_Real(rVar:=PMM[1].Phase[2].Current[12],lo:=4190,hi:=4191);
Read_Real(rVar:=PMM[1].Phase[2].Current[13],lo:=4192,hi:=4193);
Read_Real(rVar:=PMM[1].Phase[2].Current[14],lo:=4194,hi:=4195);
Read_Real(rVar:=PMM[1].Phase[2].Current[15],lo:=4196,hi:=4197);
Read_Real(rVar:=PMM[1].Phase[2].Current[16],lo:=4198,hi:=4199);
Read_Real(rVar:=PMM[1].Phase[2].Current[17],lo:=4200,hi:=4201);
Read_Real(rVar:=PMM[1].Phase[2].Current[18],lo:=4202,hi:=4203);
Read_Real(rVar:=PMM[1].Phase[2].Current[19],lo:=4204,hi:=4205);
Read_Real(rVar:=PMM[1].Phase[2].Current[1],lo:=4206,hi:=4207);
Read_Real(rVar:=PMM[1].Phase[2].Current[20],lo:=4208,hi:=4209);
Read_Real(rVar:=PMM[1].Phase[2].Current[21],lo:=4210,hi:=4211);
Read_Real(rVar:=PMM[1].Phase[2].Current[22],lo:=4212,hi:=4213);
Read_Real(rVar:=PMM[1].Phase[2].Current[23],lo:=4214,hi:=4215);
Read_Real(rVar:=PMM[1].Phase[2].Current[24],lo:=4216,hi:=4217);
Read_Real(rVar:=PMM[1].Phase[2].Current[25],lo:=4218,hi:=4219);
Read_Real(rVar:=PMM[1].Phase[2].Current[26],lo:=4220,hi:=4221);
Read_Real(rVar:=PMM[1].Phase[2].Current[27],lo:=4222,hi:=4223);
Read_Real(rVar:=PMM[1].Phase[2].Current[28],lo:=4224,hi:=4225);
Read_Real(rVar:=PMM[1].Phase[2].Current[29],lo:=4226,hi:=4227);
Read_Real(rVar:=PMM[1].Phase[2].Current[2],lo:=4228,hi:=4229);
Read_Real(rVar:=PMM[1].Phase[2].Current[30],lo:=4230,hi:=4231);
Read_Real(rVar:=PMM[1].Phase[2].Current[31],lo:=4232,hi:=4233);
Read_Real(rVar:=PMM[1].Phase[2].Current[32],lo:=4234,hi:=4235);
Read_Real(rVar:=PMM[1].Phase[2].Current[33],lo:=4236,hi:=4237);
Read_Real(rVar:=PMM[1].Phase[2].Current[34],lo:=4238,hi:=4239);
Read_Real(rVar:=PMM[1].Phase[2].Current[35],lo:=4240,hi:=4241);
Read_Real(rVar:=PMM[1].Phase[2].Current[36],lo:=4242,hi:=4243);
Read_Real(rVar:=PMM[1].Phase[2].Current[37],lo:=4244,hi:=4245);
Read_Real(rVar:=PMM[1].Phase[2].Current[38],lo:=4246,hi:=4247);
Read_Real(rVar:=PMM[1].Phase[2].Current[39],lo:=4248,hi:=4249);
Read_Real(rVar:=PMM[1].Phase[2].Current[3],lo:=4250,hi:=4251);
Read_Real(rVar:=PMM[1].Phase[2].Current[40],lo:=4252,hi:=4253);
Read_Real(rVar:=PMM[1].Phase[2].Current[41],lo:=4254,hi:=4255);
Read_Real(rVar:=PMM[1].Phase[2].Current[42],lo:=4256,hi:=4257);
Read_Real(rVar:=PMM[1].Phase[2].Current[4],lo:=4258,hi:=4259);
Read_Real(rVar:=PMM[1].Phase[2].Current[5],lo:=4260,hi:=4261);
Read_Real(rVar:=PMM[1].Phase[2].Current[6],lo:=4262,hi:=4263);
Read_Real(rVar:=PMM[1].Phase[2].Current[7],lo:=4264,hi:=4265);
Read_Real(rVar:=PMM[1].Phase[2].Current[8],lo:=4266,hi:=4267);
Read_Real(rVar:=PMM[1].Phase[2].Current[9],lo:=4268,hi:=4269);
Read_Real(rVar:=PMM[1].Phase[3].Current[10],lo:=4270,hi:=4271);
Read_Real(rVar:=PMM[1].Phase[3].Current[11],lo:=4272,hi:=4273);
Read_Real(rVar:=PMM[1].Phase[3].Current[12],lo:=4274,hi:=4275);
Read_Real(rVar:=PMM[1].Phase[3].Current[13],lo:=4276,hi:=4277);
Read_Real(rVar:=PMM[1].Phase[3].Current[14],lo:=4278,hi:=4279);
Read_Real(rVar:=PMM[1].Phase[3].Current[15],lo:=4280,hi:=4281);
Read_Real(rVar:=PMM[1].Phase[3].Current[16],lo:=4282,hi:=4283);
Read_Real(rVar:=PMM[1].Phase[3].Current[17],lo:=4284,hi:=4285);
Read_Real(rVar:=PMM[1].Phase[3].Current[18],lo:=4286,hi:=4287);
Read_Real(rVar:=PMM[1].Phase[3].Current[19],lo:=4288,hi:=4289);
Read_Real(rVar:=PMM[1].Phase[3].Current[1],lo:=4290,hi:=4291);
Read_Real(rVar:=PMM[1].Phase[3].Current[20],lo:=4292,hi:=4293);
Read_Real(rVar:=PMM[1].Phase[3].Current[21],lo:=4294,hi:=4295);
Read_Real(rVar:=PMM[1].Phase[3].Current[22],lo:=4296,hi:=4297);
Read_Real(rVar:=PMM[1].Phase[3].Current[23],lo:=4298,hi:=4299);
Read_Real(rVar:=PMM[1].Phase[3].Current[24],lo:=4300,hi:=4301);
Read_Real(rVar:=PMM[1].Phase[3].Current[25],lo:=4302,hi:=4303);
Read_Real(rVar:=PMM[1].Phase[3].Current[26],lo:=4304,hi:=4305);
Read_Real(rVar:=PMM[1].Phase[3].Current[27],lo:=4306,hi:=4307);
Read_Real(rVar:=PMM[1].Phase[3].Current[28],lo:=4308,hi:=4309);
Read_Real(rVar:=PMM[1].Phase[3].Current[29],lo:=4310,hi:=4311);
Read_Real(rVar:=PMM[1].Phase[3].Current[2],lo:=4312,hi:=4313);
Read_Real(rVar:=PMM[1].Phase[3].Current[30],lo:=4314,hi:=4315);
Read_Real(rVar:=PMM[1].Phase[3].Current[31],lo:=4316,hi:=4317);
Read_Real(rVar:=PMM[1].Phase[3].Current[32],lo:=4318,hi:=4319);
Read_Real(rVar:=PMM[1].Phase[3].Current[33],lo:=4320,hi:=4321);
Read_Real(rVar:=PMM[1].Phase[3].Current[34],lo:=4322,hi:=4323);
Read_Real(rVar:=PMM[1].Phase[3].Current[35],lo:=4324,hi:=4325);
Read_Real(rVar:=PMM[1].Phase[3].Current[36],lo:=4326,hi:=4327);
Read_Real(rVar:=PMM[1].Phase[3].Current[37],lo:=4328,hi:=4329);
Read_Real(rVar:=PMM[1].Phase[3].Current[38],lo:=4330,hi:=4331);
Read_Real(rVar:=PMM[1].Phase[3].Current[39],lo:=4332,hi:=4333);
Read_Real(rVar:=PMM[1].Phase[3].Current[3],lo:=4334,hi:=4335);
Read_Real(rVar:=PMM[1].Phase[3].Current[40],lo:=4336,hi:=4337);
Read_Real(rVar:=PMM[1].Phase[3].Current[41],lo:=4338,hi:=4339);
Read_Real(rVar:=PMM[1].Phase[3].Current[42],lo:=4340,hi:=4341);
Read_Real(rVar:=PMM[1].Phase[3].Current[4],lo:=4342,hi:=4343);
Read_Real(rVar:=PMM[1].Phase[3].Current[5],lo:=4344,hi:=4345);
Read_Real(rVar:=PMM[1].Phase[3].Current[6],lo:=4346,hi:=4347);
Read_Real(rVar:=PMM[1].Phase[3].Current[7],lo:=4348,hi:=4349);
Read_Real(rVar:=PMM[1].Phase[3].Current[8],lo:=4350,hi:=4351);
Read_Real(rVar:=PMM[1].Phase[3].Current[9],lo:=4352,hi:=4353);
Read_Real(rVar:=PMM[1].PowerFactorSys,lo:=4354,hi:=4355);
Read_Real(rVar:=PMM[1].ReactiveEnergyConsumed_kVARh,lo:=4356,hi:=4357);
Read_Real(rVar:=PMM[1].ReactivePowerPhaseA,lo:=4358,hi:=4359);
Read_Real(rVar:=PMM[1].ReactivePowerPhaseB,lo:=4360,hi:=4361);
Read_Real(rVar:=PMM[1].ReactivePowerPhaseC,lo:=4362,hi:=4363);
Read_Real(rVar:=PMM[1].TotalActivePower_kW,lo:=4364,hi:=4365);
Read_Real(rVar:=PMM[1].TotalAparentPower_kVA,lo:=4366,hi:=4367);
Read_Real(rVar:=PMM[1].TotalPowerFactor,lo:=4368,hi:=4369);
Read_Real(rVar:=PMM[1].TotalReactivePower_kVAR,lo:=4370,hi:=4371);
Read_Real(rVar:=PMM[1].VirA_fsys,lo:=4372,hi:=4373);
Read_Real(rVar:=PMM[1].VirA_Isys,lo:=4374,hi:=4375);
Read_Real(rVar:=PMM[1].VirA_PFsys,lo:=4376,hi:=4377);
Read_Real(rVar:=PMM[1].VirA_Psys,lo:=4378,hi:=4379);
Read_Real(rVar:=PMM[1].VirA_Qsys,lo:=4380,hi:=4381);
Read_Real(rVar:=PMM[1].VirA_Ssys,lo:=4382,hi:=4383);
Read_Real(rVar:=PMM[1].VirA_Usys,lo:=4384,hi:=4385);
Read_Real(rVar:=PMM[1].VirB_fsys,lo:=4386,hi:=4387);
Read_Real(rVar:=PMM[1].VirB_Isys,lo:=4388,hi:=4389);
Read_Real(rVar:=PMM[1].VirB_PFsys,lo:=4390,hi:=4391);
Read_Real(rVar:=PMM[1].VirB_Psys,lo:=4392,hi:=4393);
Read_Real(rVar:=PMM[1].VirB_Qsys,lo:=4394,hi:=4395);
Read_Real(rVar:=PMM[1].VirB_Ssys,lo:=4396,hi:=4397);
Read_Real(rVar:=PMM[1].VirB_Usys,lo:=4398,hi:=4399);
Read_Real(rVar:=PMM[1].VirBActiveEnergyConsumed_kWh,lo:=4400,hi:=4401);
Read_Real(rVar:=PMM[1].VirBActivePowerPhaseA_kW,lo:=4402,hi:=4403);
Read_Real(rVar:=PMM[1].VirBActivePowerPhaseB_kW,lo:=4404,hi:=4405);
Read_Real(rVar:=PMM[1].VirBActivePowerPhaseC_kW,lo:=4406,hi:=4407);
Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseA,lo:=4408,hi:=4409);
Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseB,lo:=4410,hi:=4411);
Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseC,lo:=4412,hi:=4413);
Read_Real(rVar:=PMM[1].VirBAverageCurrent_A,lo:=4414,hi:=4415);
Read_Real(rVar:=PMM[1].VirBAveragePhaseToNeutral_V,lo:=4416,hi:=4417);
Read_Real(rVar:=PMM[1].VirBAveragePhaseToPhase_V,lo:=4418,hi:=4419);
Read_Real(rVar:=PMM[1].VirBCurrentInPhaseA_A,lo:=4420,hi:=4421);
Read_Real(rVar:=PMM[1].VirBCurrentInPhaseB_A,lo:=4422,hi:=4423);
Read_Real(rVar:=PMM[1].VirBCurrentInPhaseC_A,lo:=4424,hi:=4425);
Read_Real(rVar:=PMM[1].VirBFrequency_Hz,lo:=4426,hi:=4427);
Read_Real(rVar:=PMM[1].VirBPowerFactorSys,lo:=4428,hi:=4429);
Read_Real(rVar:=PMM[1].VirBReactiveEnergyConsumed_kVARh,lo:=4430,hi:=4431);
Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseA,lo:=4432,hi:=4433);
Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseB,lo:=4434,hi:=4435);
Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseC,lo:=4436,hi:=4437);
Read_Real(rVar:=PMM[1].VirBTotalActivePower_kW,lo:=4438,hi:=4439);
Read_Real(rVar:=PMM[1].VirBTotalAparentPower_kVA,lo:=4440,hi:=4441);
Read_Real(rVar:=PMM[1].VirBTotalPowerFactor,lo:=4442,hi:=4443);
Read_Real(rVar:=PMM[1].VirBTotalReactivePower_kVAR,lo:=4444,hi:=4445);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseAB_V,lo:=4446,hi:=4447);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseAN_V,lo:=4448,hi:=4449);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseBC_V,lo:=4450,hi:=4451);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseBN_V,lo:=4452,hi:=4453);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseCA_V,lo:=4454,hi:=4455);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseCN_V,lo:=4456,hi:=4457);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseAB_V,lo:=4458,hi:=4459);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseAN_V,lo:=4460,hi:=4461);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseBC_V,lo:=4462,hi:=4463);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseBN_V,lo:=4464,hi:=4465);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseCA_V,lo:=4466,hi:=4467);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseCN_V,lo:=4468,hi:=4469);
Read_Real(rVar:=PMMfaza01,lo:=4470,hi:=4471);
Read_Real(rVar:=PMMfaza02,lo:=4472,hi:=4473);
Read_Real(rVar:=PMMfaza03,lo:=4474,hi:=4475);
Read_Real(rVar:=PMMfaza04,lo:=4476,hi:=4477);
Read_Real(rVar:=PMMfaza05,lo:=4478,hi:=4479);
Read_Real(rVar:=PMMfaza06,lo:=4480,hi:=4481);
Read_Real(rVar:=PMMfaza07,lo:=4482,hi:=4483);
Read_Real(rVar:=PMMfaza08,lo:=4484,hi:=4485);
Read_Real(rVar:=PMMfaza09,lo:=4486,hi:=4487);
Read_Real(rVar:=PMMfaza10,lo:=4488,hi:=4489);
Read_Real(rVar:=PMMfaza11,lo:=4490,hi:=4491);
Read_Real(rVar:=PMMfaza12,lo:=4492,hi:=4493);
Read_Real(rVar:=PMMfaza13,lo:=4494,hi:=4495);
Read_Real(rVar:=PMMfaza14,lo:=4496,hi:=4497);
Read_Real(rVar:=PMMfaza15,lo:=4498,hi:=4499);
Read_Real(rVar:=PMMfaza16,lo:=4500,hi:=4501);
Read_Real(rVar:=PMMfaza17,lo:=4502,hi:=4503);
Read_Real(rVar:=PMMfaza18,lo:=4504,hi:=4505);
Read_Real(rVar:=PMMfaza19,lo:=4506,hi:=4507);
Read_Real(rVar:=PMMfaza20,lo:=4508,hi:=4509);
Read_Real(rVar:=PMMfaza21,lo:=4510,hi:=4511);
Read_Real(rVar:=PMMfaza22,lo:=4512,hi:=4513);
Read_Real(rVar:=PMMfaza23,lo:=4514,hi:=4515);
Read_Real(rVar:=PMMfaza24,lo:=4516,hi:=4517);
Read_Real(rVar:=PMMfaza25,lo:=4518,hi:=4519);
Read_Real(rVar:=PMMfaza26,lo:=4520,hi:=4521);
Read_Real(rVar:=PMMfaza27,lo:=4522,hi:=4523);
Read_Real(rVar:=PMMfaza28,lo:=4524,hi:=4525);
Read_Real(rVar:=PMMfaza29,lo:=4526,hi:=4527);
Read_Real(rVar:=PMMfaza30,lo:=4528,hi:=4529);
Read_Real(rVar:=PMMfaza31,lo:=4530,hi:=4531);
Read_Real(rVar:=PMMfaza32,lo:=4532,hi:=4533);
Read_Real(rVar:=PMMfaza33,lo:=4534,hi:=4535);
Read_Real(rVar:=PMMfaza34,lo:=4536,hi:=4537);
Read_Real(rVar:=PMMfaza35,lo:=4538,hi:=4539);
Read_Real(rVar:=PMMfaza36,lo:=4540,hi:=4541);
Read_Real(rVar:=PMMfaza37,lo:=4542,hi:=4543);
Read_Real(rVar:=PMMfaza38,lo:=4544,hi:=4545);
Read_Real(rVar:=PMMfaza39,lo:=4546,hi:=4547);
Read_Real(rVar:=PMMfaza40,lo:=4548,hi:=4549);
Read_Real(rVar:=PMMfaza41,lo:=4550,hi:=4551);
Read_Real(rVar:=PMMfaza42,lo:=4552,hi:=4553);
Read_Real(rVar:=UPS[1].EstimatedChargeRemaining,lo:=4554,hi:=4555);
Read_Real(rVar:=UPS[1].EstimatedMinutesRemaining,lo:=4556,hi:=4557);
Read_Real(rVar:=UPS[1].IzhodMocL1,lo:=4558,hi:=4559);
Read_Real(rVar:=UPS[1].IzhodMocL2,lo:=4560,hi:=4561);
Read_Real(rVar:=UPS[1].IzhodMocL3,lo:=4562,hi:=4563);
Read_Real(rVar:=UPS[1].NapetostBaterije,lo:=4564,hi:=4565);
Read_Real(rVar:=UPS[1].TemperaturaBaterije,lo:=4566,hi:=4567);
Read_Real(rVar:=UPS[1].VhodFrekvencaL1,lo:=4568,hi:=4569);
Read_Real(rVar:=UPS[1].VhodFrekvencaL2,lo:=4570,hi:=4571);
Read_Real(rVar:=UPS[1].VhodFrekvencaL3,lo:=4572,hi:=4573);
Read_Real(rVar:=UPS[1].VhodNapetostL1,lo:=4574,hi:=4575);
Read_Real(rVar:=UPS[1].VhodNapetostL2,lo:=4576,hi:=4577);
Read_Real(rVar:=UPS[1].VhodNapetostL3,lo:=4578,hi:=4579);
Read_Real(rVar:=UPS[2].EstimatedChargeRemaining,lo:=4580,hi:=4581);
Read_Real(rVar:=UPS[2].EstimatedMinutesRemaining,lo:=4582,hi:=4583);
Read_Real(rVar:=UPS[2].IzhodMocL1,lo:=4584,hi:=4585);
Read_Real(rVar:=UPS[2].IzhodMocL2,lo:=4586,hi:=4587);
Read_Real(rVar:=UPS[2].IzhodMocL3,lo:=4588,hi:=4589);
Read_Real(rVar:=UPS[2].NapetostBaterije,lo:=4590,hi:=4591);
Read_Real(rVar:=UPS[2].TemperaturaBaterije,lo:=4592,hi:=4593);
Read_Real(rVar:=UPS[2].VhodFrekvencaL1,lo:=4594,hi:=4595);
Read_Real(rVar:=UPS[2].VhodFrekvencaL2,lo:=4596,hi:=4597);
Read_Real(rVar:=UPS[2].VhodFrekvencaL3,lo:=4598,hi:=4599);
Read_Real(rVar:=UPS[2].VhodNapetostL1,lo:=4600,hi:=4601);
Read_Real(rVar:=UPS[2].VhodNapetostL2,lo:=4602,hi:=4603);
Read_Real(rVar:=UPS[2].VhodNapetostL3,lo:=4604,hi:=4605);
Read_Real(rVar:=XVHdepltedBatery1,lo:=4606,hi:=4607);
Read_Real(rVar:=XVHdepltedBatery2,lo:=4608,hi:=4609);
Read_Real(rVar:=XVHlowBatery1,lo:=4610,hi:=4611);
Read_Real(rVar:=XVHlowBatery2,lo:=4612,hi:=4613);
Read_Real(rVar:=PMMskupniTokA,lo:=4614,hi:=4615);
Read_Real(rVar:=PMMskupniTokB,lo:=4616,hi:=4617);
Read_Real(rVar:=UPS[3].EstimatedChargeRemaining,lo:=4618,hi:=4619);
Read_Real(rVar:=UPS[3].EstimatedMinutesRemaining,lo:=4620,hi:=4621);
Read_Real(rVar:=UPS[3].IzhodMocL1,lo:=4622,hi:=4623);
Read_Real(rVar:=UPS[3].IzhodMocL2,lo:=4624,hi:=4625);
Read_Real(rVar:=UPS[3].IzhodMocL3,lo:=4626,hi:=4627);
Read_Real(rVar:=UPS[3].NapetostBaterije,lo:=4628,hi:=4629);
Read_Real(rVar:=UPS[3].TemperaturaBaterije,lo:=4630,hi:=4631);
Read_Real(rVar:=UPS[3].VhodFrekvencaL1,lo:=4632,hi:=4633);
Read_Real(rVar:=UPS[3].VhodFrekvencaL2,lo:=4634,hi:=4635);
Read_Real(rVar:=UPS[3].VhodFrekvencaL3,lo:=4636,hi:=4637);
Read_Real(rVar:=UPS[3].VhodNapetostL1,lo:=4638,hi:=4639);
Read_Real(rVar:=UPS[3].VhodNapetostL2,lo:=4640,hi:=4641);
Read_Real(rVar:=UPS[3].VhodNapetostL3,lo:=4642,hi:=4643);
Read_Real(rVar:=Circ[1].MaximumDemandA2,lo:=4644,hi:=4645);
Read_Real(rVar:=Circ[1].MaximumDemandA3,lo:=4646,hi:=4647);
Read_Real(rVar:=Circ[1].RazEner_D_SCADA,lo:=4648,hi:=4649);
Read_Real(rVar:=Circ[1].RazEner_T_SCADA,lo:=4650,hi:=4651);
Read_Real(rVar:=Circ[1].RazEner_M_SCADA,lo:=4652,hi:=4653);
(*Branje STRING*)
(**)
Read_String(sVar:=Date_Time[0],start:=5000);
Read_String(sVar:=Date_Time[1],start:=5015);
Read_String(sVar:=Date_Time[2],start:=5030);
Read_String(sVar:=Date_Time[3],start:=5045);
Read_String(sVar:=UserCurrentName,start:=5060);
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Bool : BOOL
VAR_INPUT
index: INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje BOOL*)
(**)
0:AlarmGenUPS_A_V23:=Bit_0;
1:AlarmGenUPS_V23:=Bit_0;
2:AlarmGenUPS_V25:=Bit_0;
3:AlarmPMM1VirATokPrevisok:=Bit_0;
4:AlarmPMM1VirATokVisok:=Bit_0;
5:AlarmPMM1VirBTokPrevisok:=Bit_0;
6:AlarmPMM1VirBTokVisok:=Bit_0;
7:AlarmPMM2x17nad80[10]:=Bit_0;
8:AlarmPMM2x17nad80[11]:=Bit_0;
9:AlarmPMM2x17nad80[12]:=Bit_0;
10:AlarmPMM2x17nad80[13]:=Bit_0;
11:AlarmPMM2x17nad80[14]:=Bit_0;
12:AlarmPMM2x17nad80[15]:=Bit_0;
13:AlarmPMM2x17nad80[16]:=Bit_0;
14:AlarmPMM2x17nad80[17]:=Bit_0;
15:AlarmPMM2x17nad80[18]:=Bit_0;
16:AlarmPMM2x17nad80[19]:=Bit_0;
17:AlarmPMM2x17nad80[1]:=Bit_0;
18:AlarmPMM2x17nad80[20]:=Bit_0;
19:AlarmPMM2x17nad80[21]:=Bit_0;
20:AlarmPMM2x17nad80[22]:=Bit_0;
21:AlarmPMM2x17nad80[23]:=Bit_0;
22:AlarmPMM2x17nad80[24]:=Bit_0;
23:AlarmPMM2x17nad80[25]:=Bit_0;
24:AlarmPMM2x17nad80[26]:=Bit_0;
25:AlarmPMM2x17nad80[27]:=Bit_0;
26:AlarmPMM2x17nad80[28]:=Bit_0;
27:AlarmPMM2x17nad80[29]:=Bit_0;
28:AlarmPMM2x17nad80[2]:=Bit_0;
29:AlarmPMM2x17nad80[30]:=Bit_0;
30:AlarmPMM2x17nad80[31]:=Bit_0;
31:AlarmPMM2x17nad80[32]:=Bit_0;
32:AlarmPMM2x17nad80[33]:=Bit_0;
33:AlarmPMM2x17nad80[34]:=Bit_0;
34:AlarmPMM2x17nad80[35]:=Bit_0;
35:AlarmPMM2x17nad80[36]:=Bit_0;
36:AlarmPMM2x17nad80[37]:=Bit_0;
37:AlarmPMM2x17nad80[38]:=Bit_0;
38:AlarmPMM2x17nad80[39]:=Bit_0;
39:AlarmPMM2x17nad80[3]:=Bit_0;
40:AlarmPMM2x17nad80[40]:=Bit_0;
41:AlarmPMM2x17nad80[41]:=Bit_0;
42:AlarmPMM2x17nad80[42]:=Bit_0;
43:AlarmPMM2x17nad80[4]:=Bit_0;
44:AlarmPMM2x17nad80[5]:=Bit_0;
45:AlarmPMM2x17nad80[6]:=Bit_0;
46:AlarmPMM2x17nad80[7]:=Bit_0;
47:AlarmPMM2x17nad80[8]:=Bit_0;
48:AlarmPMM2x17nad80[9]:=Bit_0;
49:ComError:=Bit_0;
50:ComSCADA:=Bit_0;
51:ComSCADA1:=Bit_0;
52:ComSCADA2:=Bit_0;
53:ComSCADA3:=Bit_0;
54:ErrComCirc[1]:=Bit_0;
55:ErrComKlima[1]:=Bit_0;
56:ErrComKlima[2]:=Bit_0;
57:ErrComPMM[1]:=Bit_0;
58:ErrComPort2:=Bit_0;
59:ErrComPort3:=Bit_0;
60:ErrComPort4:=Bit_0;
61:ErrComUPS[1]:=Bit_0;
62:ErrComUPS[2]:=Bit_0;
63:ErrComUPSMGE[1]:=Bit_0;
64:ErrorComCirc[1].Error:=Bit_0;
65:ErrorComKlima[1].Error:=Bit_0;
66:ErrorComKlima[2].Error:=Bit_0;
67:ErrorComPMM[1].Error:=Bit_0;
68:ErrorComUPS[1].Error:=Bit_0;
69:ErrorComUPS[2].Error:=Bit_0;
70:ErrorComUPSMGE[1].Error:=Bit_0;
71:F1_1_zascita_ok:=Bit_0;
72:K1_SkupnaNapaka:=Bit_0;
73:K1AlarmPozara:=Bit_0;
74:K1KlimaZdruzenAlarm:=Bit_0;
75:K1NiPretoka:=Bit_0;
76:K1OkvaraRototerma:=Bit_0;
77:K1OkvaraVlazNap:=Bit_0;
78:K1PreobMotCrpGr:=Bit_0;
79:K1PreobMotVent:=Bit_0;
80:K1ProtizamrzZascAkt:=Bit_0;
81:K1ZamasenostFiltra:=Bit_0;
82:K2_SkupnaNapaka:=Bit_0;
83:K2AlarmPozara:=Bit_0;
84:K2KlimaZdruzenAlarm:=Bit_0;
85:K2NiPretoka:=Bit_0;
86:K2OkvaraRototerma:=Bit_0;
87:K2OkvaraVlazNap:=Bit_0;
88:K2PreobMotCrpGr:=Bit_0;
89:K2PreobMotVent:=Bit_0;
90:K2ProtizamrzZascAkt:=Bit_0;
91:K2ZamasenostFiltra:=Bit_0;
92:K3_deluje:=Bit_0;
93:K3_SkupnaNapaka:=Bit_0;
94:Klima1_izkljucena:=Bit_0;
95:KLIMA1_kke_pogon:=Bit_0;
96:KLIMA1_krm_nap_ok:=Bit_0;
97:Klima2_izkljucena:=Bit_0;
98:Klima3_izkljucena:=Bit_0;
99:Klima[1].Alarm_pozar:=Bit_0;
100:Klima[1].DelVentHit1:=Bit_0;
101:Klima[1].DelVentHit2:=Bit_0;
102:Klima[1].Ni_pretoka:=Bit_0;
103:Klima[1].OkvaraRototerm:=Bit_0;
104:Klima[1].OkvaraVlazNap:=Bit_0;
105:Klima[1].PreobMotCrpGrel:=Bit_0;
106:Klima[1].PreobMotVent:=Bit_0;
107:Klima[1].ProtizamrzZascAktivna:=Bit_0;
108:Klima[1].VklopRegKlimata:=Bit_0;
109:Klima[1].ZamasenostFiltra:=Bit_0;
110:Klima[1].ZdruzAlarmA:=Bit_0;
111:Klima[1].ZdruzAlarmB:=Bit_0;
112:Klima[2].Alarm_pozar:=Bit_0;
113:Klima[2].DelVentHit1:=Bit_0;
114:Klima[2].DelVentHit2:=Bit_0;
115:Klima[2].Ni_pretoka:=Bit_0;
116:Klima[2].OkvaraRototerm:=Bit_0;
117:Klima[2].OkvaraVlazNap:=Bit_0;
118:Klima[2].PreobMotCrpGrel:=Bit_0;
119:Klima[2].PreobMotVent:=Bit_0;
120:Klima[2].ProtizamrzZascAktivna:=Bit_0;
121:Klima[2].VklopRegKlimata:=Bit_0;
122:Klima[2].ZamasenostFiltra:=Bit_0;
123:Klima[2].ZdruzAlarmA:=Bit_0;
124:Klima[2].ZdruzAlarmB:=Bit_0;
125:KLIMA_m1_delovanje:=Bit_0;
126:KLIMA_m1_napaka:=Bit_0;
127:KLIMA_m2_delovanje:=Bit_0;
128:KLIMA_m2_napaka:=Bit_0;
129:KLIMAT1_delovanje:=Bit_0;
130:KLIMAT1_napaka:=Bit_0;
131:KLIMAT1_vklop_delovanja:=Bit_0;
132:KLIMAT2_delovanje:=Bit_0;
133:KLIMAT2_napaka:=Bit_0;
134:KLIMAT2_vklop_delovanja:=Bit_0;
135:KlimeAVTO:=Bit_0;
136:N_F1_1_zascita_ok:=Bit_0;
137:N_KLIMA1_krm_nap_ok:=Bit_0;
138:N_KLIMAT1_napaka:=Bit_0;
139:N_KLIMAT2_napaka:=Bit_0;
140:N_Q12_izpad:=Bit_0;
141:N_UPS_A_V23_delovanje:=Bit_0;
142:N_UPS_A_V23_napaka:=Bit_0;
143:N_UPS_V23_delovanje:=Bit_0;
144:N_UPS_V23_napaka:=Bit_0;
145:N_UPS_V25_delovanje:=Bit_0;
146:N_UPS_V25_napaka:=Bit_0;
147:N_VLAZILEC1_napaka:=Bit_0;
148:N_VLAZILEC2_napaka:=Bit_0;
149:napaka_kom_panel:=Bit_0;
150:napaka_kom_scada:=Bit_0;
151:napaka_kom_scada2:=Bit_0;
152:NapakaSenzorSkupno:=Bit_0;
153:NapakaSenzorVlagaHIA1:=Bit_0;
154:NapakaSenzorVlagaHIA2:=Bit_0;
155:NapakaSenzorVlagaHIA3:=Bit_0;
156:NapakaSenzorVlagaHIA4:=Bit_0;
157:NapakaSenzorVlagaHIA5:=Bit_0;
158:NapakaSenzorVlagaHIA6:=Bit_0;
159:NapakaSenzorVlagaHIA7:=Bit_0;
160:NapakaTSTempTIA1:=Bit_0;
161:NapakaTSTempTIA2:=Bit_0;
162:NapakaTSTempTIA3:=Bit_0;
163:NapakaTSTempTIA4:=Bit_0;
164:NapakaTSTempTIA5:=Bit_0;
165:NapakaTSTempTIA6:=Bit_0;
166:NapakaTSTempTIA7:=Bit_0;
167:OpozoriloPMM2x17med60in80[10]:=Bit_0;
168:OpozoriloPMM2x17med60in80[11]:=Bit_0;
169:OpozoriloPMM2x17med60in80[12]:=Bit_0;
170:OpozoriloPMM2x17med60in80[13]:=Bit_0;
171:OpozoriloPMM2x17med60in80[14]:=Bit_0;
172:OpozoriloPMM2x17med60in80[15]:=Bit_0;
173:OpozoriloPMM2x17med60in80[16]:=Bit_0;
174:OpozoriloPMM2x17med60in80[17]:=Bit_0;
175:OpozoriloPMM2x17med60in80[18]:=Bit_0;
176:OpozoriloPMM2x17med60in80[19]:=Bit_0;
177:OpozoriloPMM2x17med60in80[1]:=Bit_0;
178:OpozoriloPMM2x17med60in80[20]:=Bit_0;
179:OpozoriloPMM2x17med60in80[21]:=Bit_0;
180:OpozoriloPMM2x17med60in80[22]:=Bit_0;
181:OpozoriloPMM2x17med60in80[23]:=Bit_0;
182:OpozoriloPMM2x17med60in80[24]:=Bit_0;
183:OpozoriloPMM2x17med60in80[25]:=Bit_0;
184:OpozoriloPMM2x17med60in80[26]:=Bit_0;
185:OpozoriloPMM2x17med60in80[27]:=Bit_0;
186:OpozoriloPMM2x17med60in80[28]:=Bit_0;
187:OpozoriloPMM2x17med60in80[29]:=Bit_0;
188:OpozoriloPMM2x17med60in80[2]:=Bit_0;
189:OpozoriloPMM2x17med60in80[30]:=Bit_0;
190:OpozoriloPMM2x17med60in80[31]:=Bit_0;
191:OpozoriloPMM2x17med60in80[32]:=Bit_0;
192:OpozoriloPMM2x17med60in80[33]:=Bit_0;
193:OpozoriloPMM2x17med60in80[34]:=Bit_0;
194:OpozoriloPMM2x17med60in80[35]:=Bit_0;
195:OpozoriloPMM2x17med60in80[36]:=Bit_0;
196:OpozoriloPMM2x17med60in80[37]:=Bit_0;
197:OpozoriloPMM2x17med60in80[38]:=Bit_0;
198:OpozoriloPMM2x17med60in80[39]:=Bit_0;
199:OpozoriloPMM2x17med60in80[3]:=Bit_0;
200:OpozoriloPMM2x17med60in80[40]:=Bit_0;
201:OpozoriloPMM2x17med60in80[41]:=Bit_0;
202:OpozoriloPMM2x17med60in80[42]:=Bit_0;
203:OpozoriloPMM2x17med60in80[4]:=Bit_0;
204:OpozoriloPMM2x17med60in80[5]:=Bit_0;
205:OpozoriloPMM2x17med60in80[6]:=Bit_0;
206:OpozoriloPMM2x17med60in80[7]:=Bit_0;
207:OpozoriloPMM2x17med60in80[8]:=Bit_0;
208:OpozoriloPMM2x17med60in80[9]:=Bit_0;
209:PMM1OverCurrentBetw[1]:=Bit_0;
210:PMM1OverCurrentBetw[2]:=Bit_0;
211:PMM1OverCurrentBetw[3]:=Bit_0;
212:PMM1OverCurrentOver[1]:=Bit_0;
213:PMM1OverCurrentOver[2]:=Bit_0;
214:PMM1OverCurrentOver[3]:=Bit_0;
215:PrevisokaTemp:=Bit_0;
216:Q0_izkljuceno:=Bit_0;
217:Q0_vkljuceno:=Bit_0;
218:Q12_izkljuceno:=Bit_0;
219:Q12_izpad:=Bit_0;
220:Q12_vkljuceno:=Bit_0;
221:razlitjeLAH1:=Bit_0;
222:razlitjeLAH2:=Bit_0;
223:razlitjeLAH3:=Bit_0;
224:razlitjeLAH4:=Bit_0;
225:SetDateTime:=Bit_0;
226:SetDateTimeDemand:=Bit_0;
227:SetDateTimeError:=Bit_0;
228:SetDateTimeFinished:=Bit_0;
229:SkupneNapakeNaprav_PMM17VirBVirA:=Bit_0;
230:SlabaBaterijaPLC:=Bit_0;
231:TempPovp234Previs:=Bit_0;
232:TempPovp56Previs:=Bit_0;
233:TIA1_previs_temp:=Bit_0;
234:TIA2_previs_temp:=Bit_0;
235:TIA3_previs_temp:=Bit_0;
236:TIA4_previs_temp:=Bit_0;
237:TIA5_previs_temp:=Bit_0;
238:TIA6_previs_temp:=Bit_0;
239:TIA7_previs_temp:=Bit_0;
240:UPS1Errors[10]:=Bit_0;
241:UPS1Errors[11]:=Bit_0;
242:UPS1Errors[12]:=Bit_0;
243:UPS1Errors[13]:=Bit_0;
244:UPS1Errors[14]:=Bit_0;
245:UPS1Errors[15]:=Bit_0;
246:UPS1Errors[16]:=Bit_0;
247:UPS1Errors[17]:=Bit_0;
248:UPS1Errors[18]:=Bit_0;
249:UPS1Errors[19]:=Bit_0;
250:UPS1Errors[1]:=Bit_0;
251:UPS1Errors[20]:=Bit_0;
252:UPS1Errors[21]:=Bit_0;
253:UPS1Errors[22]:=Bit_0;
254:UPS1Errors[23]:=Bit_0;
255:UPS1Errors[24]:=Bit_0;
256:UPS1Errors[25]:=Bit_0;
257:UPS1Errors[2]:=Bit_0;
258:UPS1Errors[3]:=Bit_0;
259:UPS1Errors[4]:=Bit_0;
260:UPS1Errors[5]:=Bit_0;
261:UPS1Errors[6]:=Bit_0;
262:UPS1Errors[7]:=Bit_0;
263:UPS1Errors[8]:=Bit_0;
264:UPS1Errors[9]:=Bit_0;
265:UPS2Errors[10]:=Bit_0;
266:UPS2Errors[11]:=Bit_0;
267:UPS2Errors[12]:=Bit_0;
268:UPS2Errors[13]:=Bit_0;
269:UPS2Errors[14]:=Bit_0;
270:UPS2Errors[15]:=Bit_0;
271:UPS2Errors[16]:=Bit_0;
272:UPS2Errors[17]:=Bit_0;
273:UPS2Errors[18]:=Bit_0;
274:UPS2Errors[19]:=Bit_0;
275:UPS2Errors[1]:=Bit_0;
276:UPS2Errors[20]:=Bit_0;
277:UPS2Errors[21]:=Bit_0;
278:UPS2Errors[22]:=Bit_0;
279:UPS2Errors[23]:=Bit_0;
280:UPS2Errors[24]:=Bit_0;
281:UPS2Errors[25]:=Bit_0;
282:UPS2Errors[2]:=Bit_0;
283:UPS2Errors[3]:=Bit_0;
284:UPS2Errors[4]:=Bit_0;
285:UPS2Errors[5]:=Bit_0;
286:UPS2Errors[6]:=Bit_0;
287:UPS2Errors[7]:=Bit_0;
288:UPS2Errors[8]:=Bit_0;
289:UPS2Errors[9]:=Bit_0;
290:UPS[1].AlarmAwaitingPower:=Bit_0;
291:UPS[1].AlarmBypassBad:=Bit_0;
292:UPS[1].AlarmChargerFailed:=Bit_0;
293:UPS[1].AlarmCommunicationsLost:=Bit_0;
294:UPS[1].AlarmDepletedBattery:=Bit_0;
295:UPS[1].AlarmDiagnosticTestFailed:=Bit_0;
296:UPS[1].AlarmInverterError:=Bit_0;
297:UPS[1].AlarmIzhodOffKotZahtevano:=Bit_0;
298:UPS[1].AlarmIzhodPreobremenjen:=Bit_0;
299:UPS[1].AlarmLowBattery:=Bit_0;
300:UPS[1].AlarmNapakaNaVarovalki:=Bit_0;
301:UPS[1].AlarmNapakaNaVentilatorju:=Bit_0;
302:UPS[1].AlarmOnBattery:=Bit_0;
303:UPS[1].AlarmOnBypass:=Bit_0;
304:UPS[1].AlarmShutdownImminent:=Bit_0;
305:UPS[1].AlarmShutdownPending:=Bit_0;
306:UPS[1].AlarmSlabaBaterija:=Bit_0;
307:UPS[1].AlarmSplosnaNapaka:=Bit_0;
308:UPS[1].AlarmStanjeIzhodaIzvenToleranc:=Bit_0;
309:UPS[1].AlarmStanjeVhodaIzvenToleranc:=Bit_0;
310:UPS[1].AlarmTemperaturaIzvenToleranc:=Bit_0;
311:UPS[1].AlarmTestInProgres:=Bit_0;
312:UPS[1].AlarmUPSIzhodOff:=Bit_0;
313:UPS[1].AlarmUPSOffKotZahtevano:=Bit_0;
314:UPS[1].AlarmUPSSystemOff:=Bit_0;
315:UPS[1].Napaka:=Bit_0;
316:UPS[1].StatusEcomodeAktiven:=Bit_0;
317:UPS[1].StatusInverterIsOn:=Bit_0;
318:UPS[1].StatusStopOperation:=Bit_0;
319:UPS[2].AlarmAwaitingPower:=Bit_0;
320:UPS[2].AlarmBypassBad:=Bit_0;
321:UPS[2].AlarmChargerFailed:=Bit_0;
322:UPS[2].AlarmCommunicationsLost:=Bit_0;
323:UPS[2].AlarmDepletedBattery:=Bit_0;
324:UPS[2].AlarmDiagnosticTestFailed:=Bit_0;
325:UPS[2].AlarmInverterError:=Bit_0;
326:UPS[2].AlarmIzhodOffKotZahtevano:=Bit_0;
327:UPS[2].AlarmIzhodPreobremenjen:=Bit_0;
328:UPS[2].AlarmLowBattery:=Bit_0;
329:UPS[2].AlarmNapakaNaVarovalki:=Bit_0;
330:UPS[2].AlarmNapakaNaVentilatorju:=Bit_0;
331:UPS[2].AlarmOnBattery:=Bit_0;
332:UPS[2].AlarmOnBypass:=Bit_0;
333:UPS[2].AlarmShutdownImminent:=Bit_0;
334:UPS[2].AlarmShutdownPending:=Bit_0;
335:UPS[2].AlarmSlabaBaterija:=Bit_0;
336:UPS[2].AlarmSplosnaNapaka:=Bit_0;
337:UPS[2].AlarmStanjeIzhodaIzvenToleranc:=Bit_0;
338:UPS[2].AlarmStanjeVhodaIzvenToleranc:=Bit_0;
339:UPS[2].AlarmTemperaturaIzvenToleranc:=Bit_0;
340:UPS[2].AlarmTestInProgres:=Bit_0;
341:UPS[2].AlarmUPSIzhodOff:=Bit_0;
342:UPS[2].AlarmUPSOffKotZahtevano:=Bit_0;
343:UPS[2].AlarmUPSSystemOff:=Bit_0;
344:UPS[2].Napaka:=Bit_0;
345:UPS[2].StatusEcomodeAktiven:=Bit_0;
346:UPS[2].StatusInverterIsOn:=Bit_0;
347:UPS[2].StatusStopOperation:=Bit_0;
348:UPS_A_V23_delovanje:=Bit_0;
349:UPS_A_V23_napaka:=Bit_0;
350:ups_alarm:=Bit_0;
351:ups_baterijski_nac:=Bit_0;
352:UPS_MGE[1].BatteryChargedState:=Bit_0;
353:UPS_MGE[1].BatteryCircuitBreaker:=Bit_0;
354:UPS_MGE[1].BatteryCompInProgress:=Bit_0;
355:UPS_MGE[1].BatteryFuseFault:=Bit_0;
356:UPS_MGE[1].BatteryLowWarning:=Bit_0;
357:UPS_MGE[1].BatteryTempOutOfToler:=Bit_0;
358:UPS_MGE[1].BypassInFreeFrequency:=Bit_0;
359:UPS_MGE[1].ChargerGeneralFault:=Bit_0;
360:UPS_MGE[1].DeviceVentilationFault:=Bit_0;
361:UPS_MGE[1].InverterFuseFault:=Bit_0;
362:UPS_MGE[1].InverterOverload:=Bit_0;
363:UPS_MGE[1].InverterThermalOverload:=Bit_0;
364:UPS_MGE[1].Mains1VoltOutOfToler:=Bit_0;
365:UPS_MGE[1].Mains2Overload:=Bit_0;
366:UPS_MGE[1].Mains2VoltOutOfToler:=Bit_0;
367:UPS_MGE[1].MaintenancePosition:=Bit_0;
368:UPS_MGE[1].ManualBypassSwitch:=Bit_0;
369:UPS_MGE[1].NapakaNaVarovalkah:=Bit_0;
370:UPS_MGE[1].OutputInShortCircuit:=Bit_0;
371:UPS_MGE[1].OutputOverload:=Bit_0;
372:UPS_MGE[1].OutputThermalOverload:=Bit_0;
373:UPS_MGE[1].RectifierOn:=Bit_0;
374:UPS_MGE[1].RectifierThermOverload:=Bit_0;
375:UPS_MGE[1].Skupna_napaka:=Bit_0;
376:UPS_MGE[1].UPS_coupled:=Bit_0;
377:UPS_MGE[1].UPS_error:=Bit_0;
378:UPS_MGE[1].UPS_in_backup:=Bit_0;
379:ups_polnjenje:=Bit_0;
380:UPS_V23_delovanje:=Bit_0;
381:UPS_V23_napaka:=Bit_0;
382:UPS_V25_delovanje:=Bit_0;
383:UPS_V25_napaka:=Bit_0;
384:UPSMGEErrors[10]:=Bit_0;
385:UPSMGEErrors[11]:=Bit_0;
386:UPSMGEErrors[12]:=Bit_0;
387:UPSMGEErrors[13]:=Bit_0;
388:UPSMGEErrors[14]:=Bit_0;
389:UPSMGEErrors[15]:=Bit_0;
390:UPSMGEErrors[16]:=Bit_0;
391:UPSMGEErrors[17]:=Bit_0;
392:UPSMGEErrors[1]:=Bit_0;
393:UPSMGEErrors[2]:=Bit_0;
394:UPSMGEErrors[3]:=Bit_0;
395:UPSMGEErrors[4]:=Bit_0;
396:UPSMGEErrors[5]:=Bit_0;
397:UPSMGEErrors[6]:=Bit_0;
398:UPSMGEErrors[7]:=Bit_0;
399:UPSMGEErrors[8]:=Bit_0;
400:UPSMGEErrors[9]:=Bit_0;
401:UserLoggedIn:=Bit_0;
402:VLAZILEC1_delovanje:=Bit_0;
403:VLAZILEC1_napaka:=Bit_0;
404:VLAZILEC2_delovanje:=Bit_0;
405:VLAZILEC2_napaka:=Bit_0;
406:XVH_AlarmOn:=Bit_0;
407:XVH_enopolna_napaka:=Bit_0;
408:KLIMAT1_vklop_delovanjaR:=Bit_0;
409:KLIMAT2_vklop_delovanjaR:=Bit_0;
410:KLIMAT1_R_zakleni:=Bit_0;
411:KLIMAT2_R_zakleni:=Bit_0;
412:K1_vklop_izklop_poteka:=Bit_0;
413:K2_vklop_izklop_poteka:=Bit_0;
414:N_KlimeAVTO:=Bit_0;
415:UPS[3].AlarmAwaitingPower:=Bit_0;
416:UPS[3].AlarmBypassBad:=Bit_0;
417:UPS[3].AlarmChargerFailed:=Bit_0;
418:UPS[3].AlarmCommunicationsLost:=Bit_0;
419:UPS[3].AlarmDepletedBattery:=Bit_0;
420:UPS[3].AlarmDiagnosticTestFailed:=Bit_0;
421:UPS[3].AlarmInverterError:=Bit_0;
422:UPS[3].AlarmIzhodOffKotZahtevano:=Bit_0;
423:UPS[3].AlarmIzhodPreobremenjen:=Bit_0;
424:UPS[3].AlarmLowBattery:=Bit_0;
425:UPS[3].AlarmNapakaNaVarovalki:=Bit_0;
426:UPS[3].AlarmNapakaNaVentilatorju:=Bit_0;
427:UPS[3].AlarmOnBattery:=Bit_0;
428:UPS[3].AlarmOnBypass:=Bit_0;
429:UPS[3].AlarmShutdownImminent:=Bit_0;
430:UPS[3].AlarmShutdownPending:=Bit_0;
431:UPS[3].AlarmSlabaBaterija:=Bit_0;
432:UPS[3].AlarmSplosnaNapaka:=Bit_0;
433:UPS[3].AlarmStanjeIzhodaIzvenToleranc:=Bit_0;
434:UPS[3].AlarmStanjeVhodaIzvenToleranc:=Bit_0;
435:UPS[3].AlarmTemperaturaIzvenToleranc:=Bit_0;
436:UPS[3].AlarmTestInProgres:=Bit_0;
437:UPS[3].AlarmUPSIzhodOff:=Bit_0;
438:UPS[3].AlarmUPSOffKotZahtevano:=Bit_0;
439:UPS[3].AlarmUPSSystemOff:=Bit_0;
440:UPS[3].Napaka:=Bit_0;
441:UPS[3].StatusEcomodeAktiven:=Bit_0;
442:UPS[3].StatusInverterIsOn:=Bit_0;
443:UPS[3].StatusStopOperation:=Bit_0;
444:ErrComUPS[3]:=Bit_0;
445:GSM_PozCent_napaka:=Bit_0;
446:GSM_PozSenzor_okvara:=Bit_0;
447:GSM_Gasenje_alarm:=Bit_0;
448:AGR_PozCent_napaka:=Bit_0;
449:AGR_PozSenzor_okvara:=Bit_0;
450:AGR_Gasenje_alarm:=Bit_0;
451:Circ_Vpis_Dnevne_energija_scada1:=Bit_0;
452:Circ_Vpis_Dnevne_energija_scada2:=Bit_0;
453:Circ_Vpis_Tedenska_energija_scada1:=Bit_0;
454:Circ_Vpis_Tedenska_energija_scada2:=Bit_0;
455:Circ_Vpis_Mesecna_energija_scada1:=Bit_0;
456:Circ_Vpis_Mesecna_energija_scada2:=Bit_0;
457:PozarnaCentrala_skupno:=Bit_0;
(*BOOL*)
END_CASE
END_FUNCTION
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_dWord : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje LONG*)
(**)
(*Pisanje REAL*)
(**)
4001:Circ[1].CosFi_III:=Real_0;
4003:Circ[1].DelovnaEnergija:=Real_0;
4005:Circ[1].DelovnaMoc_III:=Real_0;
4007:Circ[1].DelovnaMoc_L1:=Real_0;
4009:Circ[1].DelovnaMoc_L2:=Real_0;
4011:Circ[1].DelovnaMoc_L3:=Real_0;
4013:Circ[1].Frekvenca_L1:=Real_0;
4015:Circ[1].InduktivnaEnergija:=Real_0;
4017:Circ[1].InduktivnaMoc_III:=Real_0;
4019:Circ[1].JalovaMoc_L1:=Real_0;
4021:Circ[1].JalovaMoc_L2:=Real_0;
4023:Circ[1].JalovaMoc_L3:=Real_0;
4025:Circ[1].KapacitivnaEnergija:=Real_0;
4027:Circ[1].KapacitivnaMoc_III:=Real_0;
4029:Circ[1].MaximumDemand:=Real_0;
4031:Circ[1].Napetost_L1_L2:=Real_0;
4033:Circ[1].Napetost_L1_N:=Real_0;
4035:Circ[1].Napetost_L2_L3:=Real_0;
4037:Circ[1].Napetost_L2_N:=Real_0;
4039:Circ[1].Napetost_L3_L1:=Real_0;
4041:Circ[1].Napetost_L3_N:=Real_0;
4043:Circ[1].NavideznaMoc_III:=Real_0;
4045:Circ[1].NicelniTok:=Real_0;
4047:Circ[1].PowerFactor_III:=Real_0;
4049:Circ[1].PowerFactor_L1:=Real_0;
4051:Circ[1].PowerFactor_L2:=Real_0;
4053:Circ[1].PowerFactor_L3:=Real_0;
4055:Circ[1].THDI_L1:=Real_0;
4057:Circ[1].THDI_L2:=Real_0;
4059:Circ[1].THDI_L3:=Real_0;
4061:Circ[1].THDV_L1:=Real_0;
4063:Circ[1].THDV_L2:=Real_0;
4065:Circ[1].THDV_L3:=Real_0;
4067:Circ[1].Tok_L1:=Real_0;
4069:Circ[1].Tok_L2:=Real_0;
4071:Circ[1].Tok_L3:=Real_0;
4073:Circ[1].TokPovprecje_III:=Real_0;
4075:PMM[1].ActiveEnergyConsumed_kWh:=Real_0;
4077:PMM[1].ActivePowerPhaseA_kW:=Real_0;
4079:PMM[1].ActivePowerPhaseB_kW:=Real_0;
4081:PMM[1].ActivePowerPhaseC_kW:=Real_0;
4083:PMM[1].AparentPowerPhaseA:=Real_0;
4085:PMM[1].AparentPowerPhaseB:=Real_0;
4087:PMM[1].AparentPowerPhaseC:=Real_0;
4089:PMM[1].AverageCurrent_A:=Real_0;
4091:PMM[1].AveragePhaseToNeutral_V:=Real_0;
4093:PMM[1].AveragePhaseToPhase_V:=Real_0;
4095:PMM[1].CurrentInPhaseA_A:=Real_0;
4097:PMM[1].CurrentInPhaseB_A:=Real_0;
4099:PMM[1].CurrentInPhaseC_A:=Real_0;
4101:PMM[1].Frequency_Hz:=Real_0;
4103:PMM[1].Phase[1].Current[10]:=Real_0;
4105:PMM[1].Phase[1].Current[11]:=Real_0;
4107:PMM[1].Phase[1].Current[12]:=Real_0;
4109:PMM[1].Phase[1].Current[13]:=Real_0;
4111:PMM[1].Phase[1].Current[14]:=Real_0;
4113:PMM[1].Phase[1].Current[15]:=Real_0;
4115:PMM[1].Phase[1].Current[16]:=Real_0;
4117:PMM[1].Phase[1].Current[17]:=Real_0;
4119:PMM[1].Phase[1].Current[18]:=Real_0;
4121:PMM[1].Phase[1].Current[19]:=Real_0;
4123:PMM[1].Phase[1].Current[1]:=Real_0;
4125:PMM[1].Phase[1].Current[20]:=Real_0;
4127:PMM[1].Phase[1].Current[21]:=Real_0;
4129:PMM[1].Phase[1].Current[22]:=Real_0;
4131:PMM[1].Phase[1].Current[23]:=Real_0;
4133:PMM[1].Phase[1].Current[24]:=Real_0;
4135:PMM[1].Phase[1].Current[25]:=Real_0;
4137:PMM[1].Phase[1].Current[26]:=Real_0;
4139:PMM[1].Phase[1].Current[27]:=Real_0;
4141:PMM[1].Phase[1].Current[28]:=Real_0;
4143:PMM[1].Phase[1].Current[29]:=Real_0;
4145:PMM[1].Phase[1].Current[2]:=Real_0;
4147:PMM[1].Phase[1].Current[30]:=Real_0;
4149:PMM[1].Phase[1].Current[31]:=Real_0;
4151:PMM[1].Phase[1].Current[32]:=Real_0;
4153:PMM[1].Phase[1].Current[33]:=Real_0;
4155:PMM[1].Phase[1].Current[34]:=Real_0;
4157:PMM[1].Phase[1].Current[35]:=Real_0;
4159:PMM[1].Phase[1].Current[36]:=Real_0;
4161:PMM[1].Phase[1].Current[37]:=Real_0;
4163:PMM[1].Phase[1].Current[38]:=Real_0;
4165:PMM[1].Phase[1].Current[39]:=Real_0;
4167:PMM[1].Phase[1].Current[3]:=Real_0;
4169:PMM[1].Phase[1].Current[40]:=Real_0;
4171:PMM[1].Phase[1].Current[41]:=Real_0;
4173:PMM[1].Phase[1].Current[42]:=Real_0;
4175:PMM[1].Phase[1].Current[4]:=Real_0;
4177:PMM[1].Phase[1].Current[5]:=Real_0;
4179:PMM[1].Phase[1].Current[6]:=Real_0;
4181:PMM[1].Phase[1].Current[7]:=Real_0;
4183:PMM[1].Phase[1].Current[8]:=Real_0;
4185:PMM[1].Phase[1].Current[9]:=Real_0;
4187:PMM[1].Phase[2].Current[10]:=Real_0;
4189:PMM[1].Phase[2].Current[11]:=Real_0;
4191:PMM[1].Phase[2].Current[12]:=Real_0;
4193:PMM[1].Phase[2].Current[13]:=Real_0;
4195:PMM[1].Phase[2].Current[14]:=Real_0;
4197:PMM[1].Phase[2].Current[15]:=Real_0;
4199:PMM[1].Phase[2].Current[16]:=Real_0;
4201:PMM[1].Phase[2].Current[17]:=Real_0;
4203:PMM[1].Phase[2].Current[18]:=Real_0;
4205:PMM[1].Phase[2].Current[19]:=Real_0;
4207:PMM[1].Phase[2].Current[1]:=Real_0;
4209:PMM[1].Phase[2].Current[20]:=Real_0;
4211:PMM[1].Phase[2].Current[21]:=Real_0;
4213:PMM[1].Phase[2].Current[22]:=Real_0;
4215:PMM[1].Phase[2].Current[23]:=Real_0;
4217:PMM[1].Phase[2].Current[24]:=Real_0;
4219:PMM[1].Phase[2].Current[25]:=Real_0;
4221:PMM[1].Phase[2].Current[26]:=Real_0;
4223:PMM[1].Phase[2].Current[27]:=Real_0;
4225:PMM[1].Phase[2].Current[28]:=Real_0;
4227:PMM[1].Phase[2].Current[29]:=Real_0;
4229:PMM[1].Phase[2].Current[2]:=Real_0;
4231:PMM[1].Phase[2].Current[30]:=Real_0;
4233:PMM[1].Phase[2].Current[31]:=Real_0;
4235:PMM[1].Phase[2].Current[32]:=Real_0;
4237:PMM[1].Phase[2].Current[33]:=Real_0;
4239:PMM[1].Phase[2].Current[34]:=Real_0;
4241:PMM[1].Phase[2].Current[35]:=Real_0;
4243:PMM[1].Phase[2].Current[36]:=Real_0;
4245:PMM[1].Phase[2].Current[37]:=Real_0;
4247:PMM[1].Phase[2].Current[38]:=Real_0;
4249:PMM[1].Phase[2].Current[39]:=Real_0;
4251:PMM[1].Phase[2].Current[3]:=Real_0;
4253:PMM[1].Phase[2].Current[40]:=Real_0;
4255:PMM[1].Phase[2].Current[41]:=Real_0;
4257:PMM[1].Phase[2].Current[42]:=Real_0;
4259:PMM[1].Phase[2].Current[4]:=Real_0;
4261:PMM[1].Phase[2].Current[5]:=Real_0;
4263:PMM[1].Phase[2].Current[6]:=Real_0;
4265:PMM[1].Phase[2].Current[7]:=Real_0;
4267:PMM[1].Phase[2].Current[8]:=Real_0;
4269:PMM[1].Phase[2].Current[9]:=Real_0;
4271:PMM[1].Phase[3].Current[10]:=Real_0;
4273:PMM[1].Phase[3].Current[11]:=Real_0;
4275:PMM[1].Phase[3].Current[12]:=Real_0;
4277:PMM[1].Phase[3].Current[13]:=Real_0;
4279:PMM[1].Phase[3].Current[14]:=Real_0;
4281:PMM[1].Phase[3].Current[15]:=Real_0;
4283:PMM[1].Phase[3].Current[16]:=Real_0;
4285:PMM[1].Phase[3].Current[17]:=Real_0;
4287:PMM[1].Phase[3].Current[18]:=Real_0;
4289:PMM[1].Phase[3].Current[19]:=Real_0;
4291:PMM[1].Phase[3].Current[1]:=Real_0;
4293:PMM[1].Phase[3].Current[20]:=Real_0;
4295:PMM[1].Phase[3].Current[21]:=Real_0;
4297:PMM[1].Phase[3].Current[22]:=Real_0;
4299:PMM[1].Phase[3].Current[23]:=Real_0;
4301:PMM[1].Phase[3].Current[24]:=Real_0;
4303:PMM[1].Phase[3].Current[25]:=Real_0;
4305:PMM[1].Phase[3].Current[26]:=Real_0;
4307:PMM[1].Phase[3].Current[27]:=Real_0;
4309:PMM[1].Phase[3].Current[28]:=Real_0;
4311:PMM[1].Phase[3].Current[29]:=Real_0;
4313:PMM[1].Phase[3].Current[2]:=Real_0;
4315:PMM[1].Phase[3].Current[30]:=Real_0;
4317:PMM[1].Phase[3].Current[31]:=Real_0;
4319:PMM[1].Phase[3].Current[32]:=Real_0;
4321:PMM[1].Phase[3].Current[33]:=Real_0;
4323:PMM[1].Phase[3].Current[34]:=Real_0;
4325:PMM[1].Phase[3].Current[35]:=Real_0;
4327:PMM[1].Phase[3].Current[36]:=Real_0;
4329:PMM[1].Phase[3].Current[37]:=Real_0;
4331:PMM[1].Phase[3].Current[38]:=Real_0;
4333:PMM[1].Phase[3].Current[39]:=Real_0;
4335:PMM[1].Phase[3].Current[3]:=Real_0;
4337:PMM[1].Phase[3].Current[40]:=Real_0;
4339:PMM[1].Phase[3].Current[41]:=Real_0;
4341:PMM[1].Phase[3].Current[42]:=Real_0;
4343:PMM[1].Phase[3].Current[4]:=Real_0;
4345:PMM[1].Phase[3].Current[5]:=Real_0;
4347:PMM[1].Phase[3].Current[6]:=Real_0;
4349:PMM[1].Phase[3].Current[7]:=Real_0;
4351:PMM[1].Phase[3].Current[8]:=Real_0;
4353:PMM[1].Phase[3].Current[9]:=Real_0;
4355:PMM[1].PowerFactorSys:=Real_0;
4357:PMM[1].ReactiveEnergyConsumed_kVARh:=Real_0;
4359:PMM[1].ReactivePowerPhaseA:=Real_0;
4361:PMM[1].ReactivePowerPhaseB:=Real_0;
4363:PMM[1].ReactivePowerPhaseC:=Real_0;
4365:PMM[1].TotalActivePower_kW:=Real_0;
4367:PMM[1].TotalAparentPower_kVA:=Real_0;
4369:PMM[1].TotalPowerFactor:=Real_0;
4371:PMM[1].TotalReactivePower_kVAR:=Real_0;
4373:PMM[1].VirA_fsys:=Real_0;
4375:PMM[1].VirA_Isys:=Real_0;
4377:PMM[1].VirA_PFsys:=Real_0;
4379:PMM[1].VirA_Psys:=Real_0;
4381:PMM[1].VirA_Qsys:=Real_0;
4383:PMM[1].VirA_Ssys:=Real_0;
4385:PMM[1].VirA_Usys:=Real_0;
4387:PMM[1].VirB_fsys:=Real_0;
4389:PMM[1].VirB_Isys:=Real_0;
4391:PMM[1].VirB_PFsys:=Real_0;
4393:PMM[1].VirB_Psys:=Real_0;
4395:PMM[1].VirB_Qsys:=Real_0;
4397:PMM[1].VirB_Ssys:=Real_0;
4399:PMM[1].VirB_Usys:=Real_0;
4401:PMM[1].VirBActiveEnergyConsumed_kWh:=Real_0;
4403:PMM[1].VirBActivePowerPhaseA_kW:=Real_0;
4405:PMM[1].VirBActivePowerPhaseB_kW:=Real_0;
4407:PMM[1].VirBActivePowerPhaseC_kW:=Real_0;
4409:PMM[1].VirBAparentPowerPhaseA:=Real_0;
4411:PMM[1].VirBAparentPowerPhaseB:=Real_0;
4413:PMM[1].VirBAparentPowerPhaseC:=Real_0;
4415:PMM[1].VirBAverageCurrent_A:=Real_0;
4417:PMM[1].VirBAveragePhaseToNeutral_V:=Real_0;
4419:PMM[1].VirBAveragePhaseToPhase_V:=Real_0;
4421:PMM[1].VirBCurrentInPhaseA_A:=Real_0;
4423:PMM[1].VirBCurrentInPhaseB_A:=Real_0;
4425:PMM[1].VirBCurrentInPhaseC_A:=Real_0;
4427:PMM[1].VirBFrequency_Hz:=Real_0;
4429:PMM[1].VirBPowerFactorSys:=Real_0;
4431:PMM[1].VirBReactiveEnergyConsumed_kVARh:=Real_0;
4433:PMM[1].VirBReactivePowerPhaseA:=Real_0;
4435:PMM[1].VirBReactivePowerPhaseB:=Real_0;
4437:PMM[1].VirBReactivePowerPhaseC:=Real_0;
4439:PMM[1].VirBTotalActivePower_kW:=Real_0;
4441:PMM[1].VirBTotalAparentPower_kVA:=Real_0;
4443:PMM[1].VirBTotalPowerFactor:=Real_0;
4445:PMM[1].VirBTotalReactivePower_kVAR:=Real_0;
4447:PMM[1].VirBVoltageBetweenPhaseAB_V:=Real_0;
4449:PMM[1].VirBVoltageBetweenPhaseAN_V:=Real_0;
4451:PMM[1].VirBVoltageBetweenPhaseBC_V:=Real_0;
4453:PMM[1].VirBVoltageBetweenPhaseBN_V:=Real_0;
4455:PMM[1].VirBVoltageBetweenPhaseCA_V:=Real_0;
4457:PMM[1].VirBVoltageBetweenPhaseCN_V:=Real_0;
4459:PMM[1].VoltageBetweenPhaseAB_V:=Real_0;
4461:PMM[1].VoltageBetweenPhaseAN_V:=Real_0;
4463:PMM[1].VoltageBetweenPhaseBC_V:=Real_0;
4465:PMM[1].VoltageBetweenPhaseBN_V:=Real_0;
4467:PMM[1].VoltageBetweenPhaseCA_V:=Real_0;
4469:PMM[1].VoltageBetweenPhaseCN_V:=Real_0;
4471:PMMfaza01:=Real_0;
4473:PMMfaza02:=Real_0;
4475:PMMfaza03:=Real_0;
4477:PMMfaza04:=Real_0;
4479:PMMfaza05:=Real_0;
4481:PMMfaza06:=Real_0;
4483:PMMfaza07:=Real_0;
4485:PMMfaza08:=Real_0;
4487:PMMfaza09:=Real_0;
4489:PMMfaza10:=Real_0;
4491:PMMfaza11:=Real_0;
4493:PMMfaza12:=Real_0;
4495:PMMfaza13:=Real_0;
4497:PMMfaza14:=Real_0;
4499:PMMfaza15:=Real_0;
4501:PMMfaza16:=Real_0;
4503:PMMfaza17:=Real_0;
4505:PMMfaza18:=Real_0;
4507:PMMfaza19:=Real_0;
4509:PMMfaza20:=Real_0;
4511:PMMfaza21:=Real_0;
4513:PMMfaza22:=Real_0;
4515:PMMfaza23:=Real_0;
4517:PMMfaza24:=Real_0;
4519:PMMfaza25:=Real_0;
4521:PMMfaza26:=Real_0;
4523:PMMfaza27:=Real_0;
4525:PMMfaza28:=Real_0;
4527:PMMfaza29:=Real_0;
4529:PMMfaza30:=Real_0;
4531:PMMfaza31:=Real_0;
4533:PMMfaza32:=Real_0;
4535:PMMfaza33:=Real_0;
4537:PMMfaza34:=Real_0;
4539:PMMfaza35:=Real_0;
4541:PMMfaza36:=Real_0;
4543:PMMfaza37:=Real_0;
4545:PMMfaza38:=Real_0;
4547:PMMfaza39:=Real_0;
4549:PMMfaza40:=Real_0;
4551:PMMfaza41:=Real_0;
4553:PMMfaza42:=Real_0;
4555:UPS[1].EstimatedChargeRemaining:=Real_0;
4557:UPS[1].EstimatedMinutesRemaining:=Real_0;
4559:UPS[1].IzhodMocL1:=Real_0;
4561:UPS[1].IzhodMocL2:=Real_0;
4563:UPS[1].IzhodMocL3:=Real_0;
4565:UPS[1].NapetostBaterije:=Real_0;
4567:UPS[1].TemperaturaBaterije:=Real_0;
4569:UPS[1].VhodFrekvencaL1:=Real_0;
4571:UPS[1].VhodFrekvencaL2:=Real_0;
4573:UPS[1].VhodFrekvencaL3:=Real_0;
4575:UPS[1].VhodNapetostL1:=Real_0;
4577:UPS[1].VhodNapetostL2:=Real_0;
4579:UPS[1].VhodNapetostL3:=Real_0;
4581:UPS[2].EstimatedChargeRemaining:=Real_0;
4583:UPS[2].EstimatedMinutesRemaining:=Real_0;
4585:UPS[2].IzhodMocL1:=Real_0;
4587:UPS[2].IzhodMocL2:=Real_0;
4589:UPS[2].IzhodMocL3:=Real_0;
4591:UPS[2].NapetostBaterije:=Real_0;
4593:UPS[2].TemperaturaBaterije:=Real_0;
4595:UPS[2].VhodFrekvencaL1:=Real_0;
4597:UPS[2].VhodFrekvencaL2:=Real_0;
4599:UPS[2].VhodFrekvencaL3:=Real_0;
4601:UPS[2].VhodNapetostL1:=Real_0;
4603:UPS[2].VhodNapetostL2:=Real_0;
4605:UPS[2].VhodNapetostL3:=Real_0;
4607:XVHdepltedBatery1:=Real_0;
4609:XVHdepltedBatery2:=Real_0;
4611:XVHlowBatery1:=Real_0;
4613:XVHlowBatery2:=Real_0;
4615:PMMskupniTokA:=Real_0;
4617:PMMskupniTokB:=Real_0;
4619:UPS[3].EstimatedChargeRemaining:=Real_0;
4621:UPS[3].EstimatedMinutesRemaining:=Real_0;
4623:UPS[3].IzhodMocL1:=Real_0;
4625:UPS[3].IzhodMocL2:=Real_0;
4627:UPS[3].IzhodMocL3:=Real_0;
4629:UPS[3].NapetostBaterije:=Real_0;
4631:UPS[3].TemperaturaBaterije:=Real_0;
4633:UPS[3].VhodFrekvencaL1:=Real_0;
4635:UPS[3].VhodFrekvencaL2:=Real_0;
4637:UPS[3].VhodFrekvencaL3:=Real_0;
4639:UPS[3].VhodNapetostL1:=Real_0;
4641:UPS[3].VhodNapetostL2:=Real_0;
4643:UPS[3].VhodNapetostL3:=Real_0;
4645:Circ[1].MaximumDemandA2:=Real_0;
4647:Circ[1].MaximumDemandA3:=Real_0;
4649:Circ[1].RazEner_D_SCADA:=Real_0;
4651:Circ[1].RazEner_T_SCADA:=Real_0;
4653:Circ[1].RazEner_M_SCADA:=Real_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_String : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje STRING*)
(**)
5000:Date_Time[0]:=String_0;
5015:Date_Time[1]:=String_0;
5030:Date_Time[2]:=String_0;
5045:Date_Time[3]:=String_0;
5060:UserCurrentName:=String_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Word : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje INT*)
(**)
0:DateTime.Dan:=Byte_0;
1:DateTime.Leto:=Byte_0;
2:DateTime.Leto2:=Word_01;
3:DateTime.Mesec:=Byte_0;
4:DateTime.Minuta:=Byte_0;
5:DateTime.Sekunda:=Byte_0;
6:DateTime.Ura:=Byte_0;
7:ErrorComCirc[1].Code[10]:=Byte_0;
8:ErrorComCirc[1].Code[11]:=Byte_0;
9:ErrorComCirc[1].Code[12]:=Byte_0;
10:ErrorComCirc[1].Code[13]:=Byte_0;
11:ErrorComCirc[1].Code[14]:=Byte_0;
12:ErrorComCirc[1].Code[15]:=Byte_0;
13:ErrorComCirc[1].Code[1]:=Byte_0;
14:ErrorComCirc[1].Code[2]:=Byte_0;
15:ErrorComCirc[1].Code[3]:=Byte_0;
16:ErrorComCirc[1].Code[4]:=Byte_0;
17:ErrorComCirc[1].Code[5]:=Byte_0;
18:ErrorComCirc[1].Code[6]:=Byte_0;
19:ErrorComCirc[1].Code[7]:=Byte_0;
20:ErrorComCirc[1].Code[8]:=Byte_0;
21:ErrorComCirc[1].Code[9]:=Byte_0;
22:ErrorComCirc[1].Status:=Word_01;
23:ErrorComKlima[1].Code[10]:=Byte_0;
24:ErrorComKlima[1].Code[11]:=Byte_0;
25:ErrorComKlima[1].Code[12]:=Byte_0;
26:ErrorComKlima[1].Code[13]:=Byte_0;
27:ErrorComKlima[1].Code[14]:=Byte_0;
28:ErrorComKlima[1].Code[15]:=Byte_0;
29:ErrorComKlima[1].Code[1]:=Byte_0;
30:ErrorComKlima[1].Code[2]:=Byte_0;
31:ErrorComKlima[1].Code[3]:=Byte_0;
32:ErrorComKlima[1].Code[4]:=Byte_0;
33:ErrorComKlima[1].Code[5]:=Byte_0;
34:ErrorComKlima[1].Code[6]:=Byte_0;
35:ErrorComKlima[1].Code[7]:=Byte_0;
36:ErrorComKlima[1].Code[8]:=Byte_0;
37:ErrorComKlima[1].Code[9]:=Byte_0;
38:ErrorComKlima[1].Status:=Word_01;
39:ErrorComKlima[2].Code[10]:=Byte_0;
40:ErrorComKlima[2].Code[11]:=Byte_0;
41:ErrorComKlima[2].Code[12]:=Byte_0;
42:ErrorComKlima[2].Code[13]:=Byte_0;
43:ErrorComKlima[2].Code[14]:=Byte_0;
44:ErrorComKlima[2].Code[15]:=Byte_0;
45:ErrorComKlima[2].Code[1]:=Byte_0;
46:ErrorComKlima[2].Code[2]:=Byte_0;
47:ErrorComKlima[2].Code[3]:=Byte_0;
48:ErrorComKlima[2].Code[4]:=Byte_0;
49:ErrorComKlima[2].Code[5]:=Byte_0;
50:ErrorComKlima[2].Code[6]:=Byte_0;
51:ErrorComKlima[2].Code[7]:=Byte_0;
52:ErrorComKlima[2].Code[8]:=Byte_0;
53:ErrorComKlima[2].Code[9]:=Byte_0;
54:ErrorComKlima[2].Status:=Word_01;
55:ErrorComPMM[1].Code[10]:=Byte_0;
56:ErrorComPMM[1].Code[11]:=Byte_0;
57:ErrorComPMM[1].Code[12]:=Byte_0;
58:ErrorComPMM[1].Code[13]:=Byte_0;
59:ErrorComPMM[1].Code[14]:=Byte_0;
60:ErrorComPMM[1].Code[15]:=Byte_0;
61:ErrorComPMM[1].Code[1]:=Byte_0;
62:ErrorComPMM[1].Code[2]:=Byte_0;
63:ErrorComPMM[1].Code[3]:=Byte_0;
64:ErrorComPMM[1].Code[4]:=Byte_0;
65:ErrorComPMM[1].Code[5]:=Byte_0;
66:ErrorComPMM[1].Code[6]:=Byte_0;
67:ErrorComPMM[1].Code[7]:=Byte_0;
68:ErrorComPMM[1].Code[8]:=Byte_0;
69:ErrorComPMM[1].Code[9]:=Byte_0;
70:ErrorComPMM[1].Status:=Word_01;
71:ErrorComUPS[1].Code[10]:=Byte_0;
72:ErrorComUPS[1].Code[11]:=Byte_0;
73:ErrorComUPS[1].Code[12]:=Byte_0;
74:ErrorComUPS[1].Code[13]:=Byte_0;
75:ErrorComUPS[1].Code[14]:=Byte_0;
76:ErrorComUPS[1].Code[15]:=Byte_0;
77:ErrorComUPS[1].Code[1]:=Byte_0;
78:ErrorComUPS[1].Code[2]:=Byte_0;
79:ErrorComUPS[1].Code[3]:=Byte_0;
80:ErrorComUPS[1].Code[4]:=Byte_0;
81:ErrorComUPS[1].Code[5]:=Byte_0;
82:ErrorComUPS[1].Code[6]:=Byte_0;
83:ErrorComUPS[1].Code[7]:=Byte_0;
84:ErrorComUPS[1].Code[8]:=Byte_0;
85:ErrorComUPS[1].Code[9]:=Byte_0;
86:ErrorComUPS[1].Status:=Word_01;
87:ErrorComUPS[2].Code[10]:=Byte_0;
88:ErrorComUPS[2].Code[11]:=Byte_0;
89:ErrorComUPS[2].Code[12]:=Byte_0;
90:ErrorComUPS[2].Code[13]:=Byte_0;
91:ErrorComUPS[2].Code[14]:=Byte_0;
92:ErrorComUPS[2].Code[15]:=Byte_0;
93:ErrorComUPS[2].Code[1]:=Byte_0;
94:ErrorComUPS[2].Code[2]:=Byte_0;
95:ErrorComUPS[2].Code[3]:=Byte_0;
96:ErrorComUPS[2].Code[4]:=Byte_0;
97:ErrorComUPS[2].Code[5]:=Byte_0;
98:ErrorComUPS[2].Code[6]:=Byte_0;
99:ErrorComUPS[2].Code[7]:=Byte_0;
100:ErrorComUPS[2].Code[8]:=Byte_0;
101:ErrorComUPS[2].Code[9]:=Byte_0;
102:ErrorComUPS[2].Status:=Word_01;
103:ErrorComUPSMGE[1].Code[10]:=Byte_0;
104:ErrorComUPSMGE[1].Code[11]:=Byte_0;
105:ErrorComUPSMGE[1].Code[12]:=Byte_0;
106:ErrorComUPSMGE[1].Code[13]:=Byte_0;
107:ErrorComUPSMGE[1].Code[14]:=Byte_0;
108:ErrorComUPSMGE[1].Code[15]:=Byte_0;
109:ErrorComUPSMGE[1].Code[1]:=Byte_0;
110:ErrorComUPSMGE[1].Code[2]:=Byte_0;
111:ErrorComUPSMGE[1].Code[3]:=Byte_0;
112:ErrorComUPSMGE[1].Code[4]:=Byte_0;
113:ErrorComUPSMGE[1].Code[5]:=Byte_0;
114:ErrorComUPSMGE[1].Code[6]:=Byte_0;
115:ErrorComUPSMGE[1].Code[7]:=Byte_0;
116:ErrorComUPSMGE[1].Code[8]:=Byte_0;
117:ErrorComUPSMGE[1].Code[9]:=Byte_0;
118:ErrorComUPSMGE[1].Status:=Word_01;
119:HIA1_vlaga_s:=Word_01;
120:HIA2_vlaga_s:=Word_01;
121:HIA3_vlaga_s:=Word_01;
122:HIA4_vlaga_s:=Word_01;
123:HIA5_vlaga_s:=Word_01;
124:HIA6_vlaga_s:=Word_01;
125:HIA7_vlaga_s:=Word_01;
126:Klima[1].Analog_izh_mesanje:=Word_01;
127:Klima[1].Analog_izh_rekuperator:=Word_01;
128:Klima[1].Analog_izh_VentGrelnika:=Word_01;
129:Klima[1].Analog_izh_VentHlajenja:=Word_01;
130:Klima[1].Dejanska_zel_temp:=Word_01;
131:Klima[1].Hitrost_del_vent_disp:=Word_01;
132:Klima[1].Max_vpih:=Word_01;
133:Klima[1].Min_vpih:=Word_01;
134:Klima[1].Obrat_ure_Vent_h1:=Word_01;
135:Klima[1].Obrat_ure_Vent_h2:=Word_01;
136:Klima[1].Pol_komp_konec:=Word_01;
137:Klima[1].Pol_komp_sprem_zel_vr:=Word_01;
138:Klima[1].Pol_komp_zacetek:=Word_01;
139:Klima[1].PreklopHitDelVent:=Word_01;
140:Klima[1].Protizamrz_zascita:=Word_01;
141:Klima[1].Rezim_delovanja:=Word_01;
142:Klima[1].Temperatura_dovoda:=Word_01;
143:Klima[1].Temperatura_prostora:=Word_01;
144:Klima[1].TempPredPloscnimRekup:=Word_01;
145:Klima[1].TempZaPloscnimRekup:=Word_01;
146:Klima[1].Vlaga_v_prostoru:=Word_01;
147:Klima[1].VlagaVstopZrakaProstor:=Word_01;
148:Klima[1].Zel_temp_eko_gretja:=Word_01;
149:Klima[1].Zel_temp_eko_hlajenja:=Word_01;
150:Klima[1].Zel_temp_komf_gretja:=Word_01;
151:Klima[1].Zel_temp_komf_hlajenja:=Word_01;
152:Klima[1].Zim_komp_konec:=Word_01;
153:Klima[1].Zim_komp_sprem_zel_vr:=Word_01;
154:Klima[1].Zim_komp_zacetek:=Word_01;
155:Klima[1].ZimKompMinVpihKonec:=Word_01;
156:Klima[1].ZimKompMinVpihZac:=Word_01;
157:Klima[1].ZkompMinVpihSpremZelVr:=Word_01;
158:Klima[1].Zunanja_temp:=Word_01;
159:Klima[2].Analog_izh_mesanje:=Word_01;
160:Klima[2].Analog_izh_rekuperator:=Word_01;
161:Klima[2].Analog_izh_VentGrelnika:=Word_01;
162:Klima[2].Analog_izh_VentHlajenja:=Word_01;
163:Klima[2].Dejanska_zel_temp:=Word_01;
164:Klima[2].Hitrost_del_vent_disp:=Word_01;
165:Klima[2].Max_vpih:=Word_01;
166:Klima[2].Min_vpih:=Word_01;
167:Klima[2].Obrat_ure_Vent_h1:=Word_01;
168:Klima[2].Obrat_ure_Vent_h2:=Word_01;
169:Klima[2].Pol_komp_konec:=Word_01;
170:Klima[2].Pol_komp_sprem_zel_vr:=Word_01;
171:Klima[2].Pol_komp_zacetek:=Word_01;
172:Klima[2].PreklopHitDelVent:=Word_01;
173:Klima[2].Protizamrz_zascita:=Word_01;
174:Klima[2].Rezim_delovanja:=Word_01;
175:Klima[2].Temperatura_dovoda:=Word_01;
176:Klima[2].Temperatura_prostora:=Word_01;
177:Klima[2].TempPredPloscnimRekup:=Word_01;
178:Klima[2].TempZaPloscnimRekup:=Word_01;
179:Klima[2].Vlaga_v_prostoru:=Word_01;
180:Klima[2].VlagaVstopZrakaProstor:=Word_01;
181:Klima[2].Zel_temp_eko_gretja:=Word_01;
182:Klima[2].Zel_temp_eko_hlajenja:=Word_01;
183:Klima[2].Zel_temp_komf_gretja:=Word_01;
184:Klima[2].Zel_temp_komf_hlajenja:=Word_01;
185:Klima[2].Zim_komp_konec:=Word_01;
186:Klima[2].Zim_komp_sprem_zel_vr:=Word_01;
187:Klima[2].Zim_komp_zacetek:=Word_01;
188:Klima[2].ZimKompMinVpihKonec:=Word_01;
189:Klima[2].ZimKompMinVpihZac:=Word_01;
190:Klima[2].ZkompMinVpihSpremZelVr:=Word_01;
191:Klima[2].Zunanja_temp:=Word_01;
192:KlimaIzklopObrUre:=Word_01;
193:PMM[1].AlarmPhase[1].GlobalAlarmReg:=Word_01;
194:PMM[1].AlarmPhase[2].GlobalAlarmReg:=Word_01;
195:PMM[1].AlarmPhase[3].GlobalAlarmReg:=Word_01;
196:Q12stanje:=Byte_0;
197:TempHistereza:=Word_01;
198:TempPovp234:=Word_01;
199:TempPovp234Alarm:=Word_01;
200:TempPovp56:=Word_01;
201:TempPovp56Alarm:=Word_01;
202:TempZaVklopKlim1:=Word_01;
203:TempZaVklopKlim2:=Word_01;
204:TIA1_alarm:=Word_01;
205:TIA1_temp_s:=Word_01;
206:TIA2_alarm:=Word_01;
207:TIA2_temp_s:=Word_01;
208:TIA3_alarm:=Word_01;
209:TIA3_temp_s:=Word_01;
210:TIA4_alarm:=Word_01;
211:TIA4_temp_s:=Word_01;
212:TIA5_alarm:=Word_01;
213:TIA5_temp_s:=Word_01;
214:TIA6_alarm:=Word_01;
215:TIA6_temp_s:=Word_01;
216:TIA7_alarm:=Word_01;
217:TIA7_temp_s:=Word_01;
218:UPS[1].InverterStatus:=Word_01;
219:UPS[1].OutputStatus:=Word_01;
220:UPS[1].SteviloIzpadovVhodneLinije:=Word_01;
221:UPS[1].UnitStatus:=Word_01;
222:UPS[2].InverterStatus:=Word_01;
223:UPS[2].OutputStatus:=Word_01;
224:UPS[2].SteviloIzpadovVhodneLinije:=Word_01;
225:UPS[2].UnitStatus:=Word_01;
226:UPS_MGE[1].BatteryBackupTime:=Word_01;
227:UPS_MGE[1].BatteryChargingLevel:=Word_01;
228:UPS_MGE[1].BatteryRechargeDuration:=Word_01;
229:UPS_MGE[1].I1output:=Word_01;
230:UPS_MGE[1].I2output:=Word_01;
231:UPS_MGE[1].I3output:=Word_01;
232:UPS_MGE[1].InverterFrequency:=Word_01;
233:UPS_MGE[1].OutputActivePower1:=Word_01;
234:UPS_MGE[1].OutputActivePower2:=Word_01;
235:UPS_MGE[1].OutputActivePower3:=Word_01;
236:UPS_MGE[1].OutputFrequency:=Word_01;
237:UPS_MGE[1].OutputLoadLevel:=Word_01;
238:UPS_MGE[1].StatusBaterije:=Byte_0;
239:UPS_MGE[1].U12mains1:=Word_01;
240:UPS_MGE[1].U12mains2:=Word_01;
241:UPS_MGE[1].U1N_inverter:=Word_01;
242:UPS_MGE[1].U1N_output:=Word_01;
243:UPS_MGE[1].U23mains1:=Word_01;
244:UPS_MGE[1].U23mains2:=Word_01;
245:UPS_MGE[1].U2N_inverter:=Word_01;
246:UPS_MGE[1].U2N_output:=Word_01;
247:UPS_MGE[1].U31mains1:=Word_01;
248:UPS_MGE[1].U31mains2:=Word_01;
249:UPS_MGE[1].U3N_inverter:=Word_01;
250:UPS_MGE[1].U3N_output:=Word_01;
251:UPS_MGE[1].U_battery:=Word_01;
252:UserCurrentLevel:=Byte_0;
253:XVH_UPSstatus:=Byte_0;
254:UPS[3].InverterStatus:=Word_01;
255:UPS[3].OutputStatus:=Word_01;
256:UPS[3].SteviloIzpadovVhodneLinije:=Word_01;
257:UPS[3].UnitStatus:=Word_01;
(*Pisanje UINT*)
(**)
6000:kom_nast_cas_izpada:=Word_01;
6001:PMM[1].AlarmPhase[1].C01_16_60to80:=Word_01;
6002:PMM[1].AlarmPhase[1].C01_16_over80:=Word_01;
6003:PMM[1].AlarmPhase[1].C17_32_60to80:=Word_01;
6004:PMM[1].AlarmPhase[1].C17_32_over80:=Word_01;
6005:PMM[1].AlarmPhase[1].C33_42_60to80:=Word_01;
6006:PMM[1].AlarmPhase[1].C33_42_over80:=Word_01;
6007:PMM[1].AlarmPhase[2].C01_16_60to80:=Word_01;
6008:PMM[1].AlarmPhase[2].C01_16_over80:=Word_01;
6009:PMM[1].AlarmPhase[2].C17_32_60to80:=Word_01;
6010:PMM[1].AlarmPhase[2].C17_32_over80:=Word_01;
6011:PMM[1].AlarmPhase[2].C33_42_60to80:=Word_01;
6012:PMM[1].AlarmPhase[2].C33_42_over80:=Word_01;
6013:PMM[1].AlarmPhase[3].C01_16_60to80:=Word_01;
6014:PMM[1].AlarmPhase[3].C01_16_over80:=Word_01;
6015:PMM[1].AlarmPhase[3].C17_32_60to80:=Word_01;
6016:PMM[1].AlarmPhase[3].C17_32_over80:=Word_01;
6017:PMM[1].AlarmPhase[3].C33_42_60to80:=Word_01;
6018:PMM[1].AlarmPhase[3].C33_42_over80:=Word_01;
6019:UPS[1].StatusBaterije:=Word_01;
6020:UPS[2].StatusBaterije:=Word_01;
6021:K1_obr_u_skupno:=Word_01;
6022:K2_obr_u_skupno:=Word_01;
6023:UPS[3].StatusBaterije:=Word_01;
;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
(*Modbus Slave Example*)
PROGRAM PLC_PRG_modnet
VAR
Slave_Adresa:BYTE:=2;
Slave_Port:INT:=502;
SlaveSetup:MBS_Setup;
SlavePoll:MBS_Poll;
SlaveAnswer:MBS_Answer;
step: USINT;
end :BOOL;
i: INT;
cycle :BOOL := FALSE; (* First cycle *)
OpenDefaultPort: BOOL;
Write_16: BOOL;
Write_15: BOOL;
Write_5: BOOL;
j: INT;
slavepollwOffset_temp: INT;
slaveanswerwCount_temp: INT;
slaveanswerwoffset_temp: INT;
END_VAR
(* @END_DECLARATION := '0' *)
(*Modbus Slave Example*)
IF Write_16=TRUE THEN (**)
FOR j := 0 TO (slaveanswerwCount_temp-1)/15 BY 1 DO (*vpiše se dword, real*)
wStr_0:=mind[slaveanswerwoffset_temp+j];
wStr_1:=mind[slaveanswerwoffset_temp+j+1];
wStr_2 :=mind[slaveanswerwoffset_temp+j+2];
wStr_3:=mind[slaveanswerwoffset_temp+j+3];
wStr_4:=mind[slaveanswerwoffset_temp+j+4];
wStr_5 :=mind[slaveanswerwoffset_temp+j+5];
wStr_6:=mind[slaveanswerwoffset_temp+j+6];
wStr_7:=mind[slaveanswerwoffset_temp+j+7];
wStr_8:=mind[slaveanswerwoffset_temp+j+8];
wStr_9:=mind[slaveanswerwoffset_temp+j+9];
wStr_10:=mind[slaveanswerwoffset_temp+j+10];
wStr_11:=mind[slaveanswerwoffset_temp+j+11];
wStr_12:=mind[slaveanswerwoffset_temp+j+12];
wStr_13:=mind[slaveanswerwoffset_temp+j+13];
wStr_14:=mind[slaveanswerwoffset_temp+j+14];
bStr_29:=0;
mod_Write_String(index:=slaveanswerwoffset_temp+j); (*vpis real in string*)
END_FOR;
FOR j := 1 TO slaveanswerwCount_temp-1 BY 2 DO (*vpiše se dword, real*)
Word_01:=mind[slaveanswerwoffset_temp+j-1];
Word_23:=mind[slaveanswerwoffset_temp+j];
mod_Write_dWord(index:=slaveanswerwoffset_temp+j); (*vpis real in dword*)
END_FOR;
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO (*vpiše se word*)
Word_01:=mind[slaveanswerwoffset_temp+j];
mod_Write_Word(index:=slaveanswerwoffset_temp+j); (*vpis word*)
END_FOR;
Write_16:=FALSE;
END_IF;
IF Write_5=TRUE OR Write_15=TRUE THEN (**)
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO
Bit_0:=mind_bool[slaveanswerwoffset_temp+j];
mod_Write_Bool(index:=slaveanswerwoffset_temp+j); (*vpis spremembe v spremenljivko*)
END_FOR;
Write_5:=FALSE;
Write_15:=FALSE;
END_IF;
(*iz scade ni komande za branje*)
IF Write_16=FALSE AND Write_5=FALSE AND Write_15=FALSE THEN
mod_Read();(*branje spremenljivk za scado*)
END_IF
(*Close all sockets on corresponding event*)
IF cycle = FALSE THEN
SysCallbackRegister(INDEXOF(Callback_Stop),event_stop);
SysCallbackRegister(INDEXOF(Callback_Reset),event_before_reset);
SysCallbackRegister(INDEXOF(Callback_Reset),event_shutdown);
cycle := TRUE;
END_IF
(*Close all connections via application *)
IF end = TRUE THEN
MBS_CloseAllConnections();
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=FALSE); (*Close port*)
step := 0;
END_IF
IF OpenDefaultPort=TRUE THEN
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=TRUE); (*Close port*)
step := 0;
OpenDefaultPort:=FALSE;
END_IF
(* State machine for setup, poll and answer *)
CASE step OF
0:(**)
SlaveSetup.bUnitIdentifier:=Slave_Adresa;(*Subunitnumber*)
slavesetup.wDefaultPort:=Slave_Port;(*Standartport *)
SlaveSetup.xAdditionalPortActive:=FALSE;(*Port opened or closed*)
SlaveSetup.xSecureMode:=FALSE;(*If TRUE only preset IPs are accepted*)
SlaveSetup.tTimeout:=T#3m;(*Timeout if no communication with slave established*)
SlaveSetup(xStrobe:=TRUE);(*Strobe starts function*)
IF slavesetup.xBusy = FALSE THEN
slavesetup(xstrobe := FALSE);
step := 1 ;
END_IF;
1:(**)
SlavePoll(xStrobe:=TRUE);(*Searching for master commands*)
IF NOT SlavePoll.xBusy THEN
step:=2;
SlavePoll(xStrobe:=FALSE);
END_IF;
2:(**)
step:= 1;
CASE SlavePoll.bFunctionCode OF (*Connect accepted pollparameters with answerparameters*)
8:(**)(*Poll answers*)
;
15:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind_bool[slaveanswer.woffset+i] := slavepoll.xarData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.xarData:=slavepoll.xarData;
Write_15:=TRUE;
16:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind[slaveanswer.woffset+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.wardata := slavepoll.warData;
Write_16:=TRUE;
1,2:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slavepoll.wcount-1 BY 1 DO
slaveanswer.xarData[i]:=mind_bool[slavepoll.woffset+i]; (*Read from Data-array*)
END_FOR
3,4:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slaveanswer.wCount-1 BY 1 DO
slaveanswer.warData[i]:=mind[slavepoll.woffset+i];(*Read from Data-array*)
END_FOR
5:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
mind_bool[slavepoll.woffset]:=slavepoll.xarData[0];(*Write to Data-array*)
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.xarData := slavepoll.xardata;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
Write_5:=TRUE;
6:
slaveanswer.bFunctionCode:= slavepoll.bFunctionCode;
mind[slavepoll.woffset]:= slavepoll.warData[0];(*Write to Data-array*)
slaveanswer.wOffset:= slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wardata := slavepoll.wardata;
23:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
FOR i:= 0 TO slavepoll.wCountAdd-1 BY 1 DO
mind[slavepoll.woffsetadd+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
FOR i := 0 TO slavepoll.wCount BY 1 DO
slaveanswer.warData[i] := mind[1+slavepoll.woffset+i];(*Read from Data-array*)
END_FOR;
END_CASE;
IF slavepoll.xAvailable = TRUE THEN
slaveanswer();(*When Data ready, send answer*)
END_IF
END_CASE;
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_dWord : BOOL
VAR_INPUT
dVAR: DWORD;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
DWord_0:=dVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_Real : BOOL
VAR_INPUT
rVAR: REAL;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
Real_0:=rVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_String : BOOL
VAR_INPUT
sVar: STRING;
start:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
String_0:=LEFT (sVar,29);
mind[start]:=wStr_0;
mind[start+1]:=wStr_1;
mind[start+2]:=wStr_2;
mind[start+3]:=wStr_3;
mind[start+4]:=wStr_4;
mind[start+5]:=wStr_5;
mind[start+6]:=wStr_6;
mind[start+7]:=wStr_7;
mind[start+8]:=wStr_8;
mind[start+9]:=wStr_9;
mind[start+10]:=wStr_10;
mind[start+11]:=wStr_11;
mind[start+12]:=wStr_12;
mind[start+13]:=wStr_13;
bStr_29:=0;
mind[start+14]:=wStr_14;
END_FUNCTION
(* @GLOBAL_VARIABLE_LIST := 'Global_Variables_Modnet' *)
(* @PATH := '' *)
(* @SYMFILEFLAGS := '2048' *)
VAR_GLOBAL
(*delovno polje za modnet komunikacijo*)
mind :ARRAY [0..9999] OF WORD;
mind_bool :ARRAY [0..9999] OF BOOL; (*Buffer-Array*)
(*Delovni markerji //*)
Bit_0 AT %MX0.0 : BOOL;
Byte_0 AT %MB0 : BYTE;
Byte_1 AT %MB1 : BYTE;
Byte_2 AT %MB2 : BYTE;
Byte_3 AT %MB3 : BYTE;
Real_0 AT %MR0:REAL;
DWord_0 AT %MD0:DWORD;
Word_01 AT %MW0:WORD;
Word_23 AT %MW2:WORD;
String_0 AT %MW10:STRING;
wStr_0 AT %MW10:WORD;
wStr_1 AT %MW12:WORD;
wStr_2 AT %MW14:WORD;
wStr_3 AT %MW16:WORD;
wStr_4 AT %MW18:WORD;
wStr_5 AT %MW20:WORD;
wStr_6 AT %MW22:WORD;
wStr_7 AT %MW24:WORD;
wStr_8 AT %MW26:WORD;
wStr_9 AT %MW28:WORD;
wStr_10 AT %MW30:WORD;
wStr_11 AT %MW32:WORD;
wStr_12 AT %MW34:WORD;
wStr_13 AT %MW36:WORD;
wStr_14 AT %MW38:WORD;
bStr_00 AT %MB10:BYTE;
bStr_01 AT %MB11:BYTE;
bStr_02 AT %MB12:BYTE;
bStr_03 AT %MB13:BYTE;
bStr_04 AT %MB14:BYTE;
bStr_05 AT %MB15:BYTE;
bStr_06 AT %MB16:BYTE;
bStr_07 AT %MB17:BYTE;
bStr_08 AT %MB18:BYTE;
bStr_09 AT %MB19:BYTE;
bStr_10 AT %MB20:BYTE;
bStr_11 AT %MB21:BYTE;
bStr_12 AT %MB22:BYTE;
bStr_13 AT %MB23:BYTE;
bStr_14 AT %MB24:BYTE;
bStr_15 AT %MB25:BYTE;
bStr_16 AT %MB26:BYTE;
bStr_17 AT %MB27:BYTE;
bStr_18 AT %MB28:BYTE;
bStr_19 AT %MB29:BYTE;
bStr_20 AT %MB30:BYTE;
bStr_21 AT %MB31:BYTE;
bStr_22 AT %MB32:BYTE;
bStr_23 AT %MB33:BYTE;
bStr_24 AT %MB34:BYTE;
bStr_25 AT %MB35:BYTE;
bStr_26 AT %MB36:BYTE;
bStr_27 AT %MB37:BYTE;
bStr_28 AT %MB38:BYTE;
bStr_29 AT %MB39:BYTE;
(********************************************)
END_VAR
(* @OBJECT_END := 'Global_Variables_Modnet' *)
(* @CONNECTIONS := Global_Variables_Modnet
FILENAME : ''
FILETIME : 0
EXPORT : 0
NUMOFCONNECTIONS : 0
*)
(*KONEC_KODA*)