## Prva stran
variable | 2972 | 1.KORAK | variable_1 | 2.KORAK | KORAKI!
Device name | Tip | število spremenljivk | Tip (izbrani) | Zamenjaj z | 1.V Sheet "variable" skopiraj vsebino iz variable.dbf - iz Citect SCAD-a projekta, ki ga želiš pretvoriti.
IOD_PTO | BCD | 0 | BCD | INT | 2.V polje A3 vpiši Device ime spremenljivk ki se bodo prenašale preko Modnet protokola
| BYTE | 201 | BYTE | BYTE | 3.V polje A6 vpiši ime krmilnika (npr.:PLC1, če je adresa v spremenljivkah PLC1:.NapakaKoncnega_stikala, drugače pusti polje prazno)
OPC name | DIGITAL | 957 | DIGITAL | DIGITAL | 4. Pritisni gumb 1.KORAK (V poljih C3:C10 se izpiše število spremenljivk, ki imajo Device enak tistemu v polju A3)
PTO | INT | 43 | INT | INT | 5. Pritisni gumb 2.KORAK (V Sheet-u variable_1 se naredi seznam spremenljivk, ki se bodo prenačale preko Modnet protokola)
| LONG | 0 | LONG | LONG | 6. Pritisni gumb 3.KORAK (V poljih C15:C24 se izpiše število spremnljiv po tipih, v poljih F15:F24 se izpiše število potrebni wordow/coilov za prenos spremnljivk)
| REAL | 437 | REAL | REAL | 7. 4.KORAK: V polja C29:C38 je potrebno ročno vpisati začetne naslove spremnljivk. Potrebno je paziti na:
| STRING | 5 | UINT | UINT | *naslov se morajo začeti z lihim številom npr.:1, 101, 551
| UINT | 1 | STRING | STRING | *naslove je potrebno nastaviti tako, da se naslovi sremenljivk ne more prekrivati (naslovi spremenjivk gredo od (začetnega naslova) do (začetnega naslova+število potrebnih wordow))
8. Pritisni gumb 5.KORAK (V Sheet-u variable_2 se naredi seznam spremenljivk, ki so tokrat sortirana po tipih)
9. Pritisni gumb 6.KORAK (V Sheet-u variable_3 se naredi seznam spremenljivk, katerih Device se zamenja z devicom v polju C41)
Trajanje makroja | variable_1 |  |  | 3.KORAK | 10. Pritisni gumb 7.KORAK (V Sheet-u variable_new se generira seznam spremenljivk. To vsebino je potrebno skopirati v variable.dbf)
0 | Tip | število spremenljivk | TIP | št.potrebnih coilov/wordov | *ta korak traja nekoliko dalj časa (odvisno od števila spremenljivk)
| BCD | 0 | BCD | 0 | *če se pojavi težava z adresami ki se začnejo z 0000 (npr.: "00001" se spremeni na "1") je potrebno uporabiti priloženo (prazno) variable.dbf ali v
| BYTE | 0 | BYTE | 0 | ProjectEditoju/VariableTags na poljubni spremenljki nastaviti adreso" 00001"
| DIGITAL | 957 | DIGITAL | 957 (Coil) | 11. Pritisni gumb 8.KORAK in 9.KORAK (V Sheet-u Xsoft se generira koda)
| INT | 244 | INT | 244 (word) | 12. S pritiskom na gumb 10.KORAK se zgenerira EXP koda za Xsoft (Xsoft_EXP)
| LONG | 0 | LONG | 0 (word) | 13. S pritiskom na gumb Save*.EXP se avtomatsko generira datoka *.EXP
| REAL | 437 | REAL | 874 (word)
| STRING | 5 | STRING | 75 (word)
| UINT | 1 | UINT | 1 (word)
POZOR!
*V Sheet-u variable mora biti vsebina skopirana od polja A1 naprej (če je katera vrstica prazna makroji ne bodo delovali pravilno)
*Ena "STRING" spremenljivka zasede 15wordow (to pomeni 29 znakov, 1BYTE=1STRING)
|  | 4.KORAK(vpiši ročno) | variable_2 | 5.KORAK | *Dolžina "STRING" spremenljivk je 29 znakov (lahko tudi več vendar ne z uporabno tega dokumenta in XSoft programa,potrebna je modifikacija makrojev in Xsoft programa)
| Tip | Začetni naslov |  | Sortiraj | *Vsi stringi so enake dolžine (29)
| BCD |  |  | BCD | *"BYTE" spremenljivke se v variable.dbf spremenijo v "INT" (prenašanje posameznih bytov ni mogoče, niti naslavaljanje v citectscadi)
| BYTE |  |  | DIGITAL | *Naslovi spremenljivk se morajo obvezno začeti z lihim naslovom (preizkušeno je z začetnimi naslovi, ki se izpišejo po pritisku na gumb Ponastavi)
| DIGITAL | 1 |  | BYTE | *Z pritiskom na gumb RESET se pobriše vsebina vseh Sheet-ov razen Sheet-a variable (makor reset se izvaja precej časa)
| INT | 1 |  | INT | *makroji ne delujejo pravilno,če je v Sheet-u variable več kot 9999 vrstic oz. spremenljivk (število vseh spremnljivk je prikazano v polju B1)
| LONG | 3001 |  | LONG | *če se vsebine iz variable_new ne gre skpirat v variable.dbf datotek, vsebino skopirajte najprej v *.txt datoteko in nato v variable.dbf
| REAL | 4001 |  | REAL | *v polju A14 na Sheet-u Prva stran se prikazuje število ciklop do konca izvedbe makroja (samo za gumb 7.KORAK)
| STRING | 5001 |  | STRING
| UINT | 6001 |  | UINT
| variable_3 | 6.KORAK | variable_new | 7.KORAK
| New Device name | IOD_PTO_TCP |  | Nova variable dbf
|  |  | xSoft | 8.KORAK in 9.KORAK
xSoft koda
xSoft_EXP
Izvoz*.EXP
1.KORAK
2.KORAK
3.KORAK
5.KORAK
6.KORAK
7.KORAK
8.KORAK
9.KORAK
RESET
Ponastavi
10.KORAK
Save*.EXP

## variable
PTOVsotaF1_1_16B | INT | IOD_PTO_disk | I35 | [8 empty] | 0x53409090
PTOVsotaF1_17_32B | INT | IOD_PTO_disk | I36 | [8 empty] | 0x53409091
PTOVsotaF1_33_42B | INT | IOD_PTO_disk | I37 | [8 empty] | 0x53409092
PTOVsotaF2_1_16B | INT | IOD_PTO_disk | I38 | [8 empty] | 0x53409093
PTOVsotaF2_17_32B | INT | IOD_PTO_disk | I39 | [8 empty] | 0x53409094
PTOVsotaF2_33_42B | INT | IOD_PTO_disk | I40 | [8 empty] | 0x53409095
PTOVsotaF3_1_16B | INT | IOD_PTO_disk | I41 | [8 empty] | 0x53409096
PTOVsotaF3_17_32B | INT | IOD_PTO_disk | I42 | [8 empty] | 0x53409097
PTOVsotaF3_33_42B | INT | IOD_PTO_disk | I43 | [8 empty] | 0x53409098
PTOVsotaF1_1_16A | INT | IOD_PTO_disk | I44 | [8 empty] | 0x53409099
PTOVsotaF1_17_32A | INT | IOD_PTO_disk | I45 | [8 empty] | 0x5340909a
PTOVsotaF1_33_42A | INT | IOD_PTO_disk | I46 | [8 empty] | 0x5340909b
PTOVsotaF2_1_16A | INT | IOD_PTO_disk | I47 | [8 empty] | 0x5340909c
PTOVsotaF2_17_32A | INT | IOD_PTO_disk | I48 | [8 empty] | 0x5340909d
PTOVsotaF2_33_42A | INT | IOD_PTO_disk | I49 | [8 empty] | 0x5340909e
PTOVsotaF3_1_16A | INT | IOD_PTO_disk | I50 | [8 empty] | 0x5340909f
PTOVsotaF3_17_32A | INT | IOD_PTO_disk | I51 | [8 empty] | 0x534090a0
PTOVsotaF3_33_42A | INT | IOD_PTO_disk | I52 | [8 empty] | 0x534090a1
PTOAlarmGenComm | DIGITAL | IOD_PTO | PTO:.AlarmGenComm | [6 empty] | 6157 | 1 | 0x534090b0
PTOAlarmGenKlima1 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[1] | [6 empty] | 6157 | 1 | 0x534090c0
PTOAlarmGenKlima2 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[2] | [6 empty] | 6157 | 1 | 0x534090d0
PTOAlarmGenKlima3 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[3] | [6 empty] | 6157 | 1 | 0x534090e0
PTOAlarmGenKlima4 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[4] | [6 empty] | 6157 | 1 | 0x534090f0
PTOAlarmGenKlima5 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[5] | [6 empty] | 6157 | 1 | 0x53409100
PTOAlarmGenKlima6 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[6] | [6 empty] | 6157 | 1 | 0x53409110
PTOAlarmGenPMM | DIGITAL | IOD_PTO | PTO:.AlarmGenPMM | [6 empty] | 6157 | 1 | 0x53409120
PTOAlarmGenRest | DIGITAL | IOD_PTO | PTO:.AlarmGenRest | [6 empty] | 6157 | 1 | 0x53409130
PTOAlarmGenSenzor | DIGITAL | IOD_PTO | PTO:.AlarmGenSenzor | [6 empty] | 6157 | 1 | 0x53409140
PTOAlarmGenStikala | DIGITAL | IOD_PTO | PTO:.AlarmGenStikala | [6 empty] | 6157 | 1 | 0x53409150
PTOAlarmGenTemp | DIGITAL | IOD_PTO | PTO:.AlarmGenTemp | [6 empty] | 6157 | 1 | 0x53409160
PTOAlarmGenUPS1 | DIGITAL | IOD_PTO | PTO:.AlarmGenUPS1 | [6 empty] | 6157 | 1 | 0x53409170
PTOAlarmGenUPS2 | DIGITAL | IOD_PTO | PTO:.AlarmGenUPS2 | [6 empty] | 6157 | 1 | 0x53409180
PTOComSCADA | DIGITAL | IOD_PTO | PTO:.ComSCADA | [6 empty] | 6157 | 1 | 0x53409190
PTOComSCADA1 | DIGITAL | IOD_PTO | PTO:.ComSCADA1 | [6 empty] | 6157 | 1 | 0x534091a0
PTODate_Time0 | STRING | IOD_PTO | PTO:.Date_Time[0] | [6 empty] | 6157 | 1 | 0x534091b8
PTODate_Time1 | STRING | IOD_PTO | PTO:.Date_Time[1] | [6 empty] | 6157 | 1 | 0x534091b9
PTODate_Time2 | STRING | IOD_PTO | PTO:.Date_Time[2] | [6 empty] | 6157 | 1 | 0x534091ba
PTODate_Time3 | STRING | IOD_PTO | PTO:.Date_Time[3] | [6 empty] | 6157 | 1 | 0x534091bb
PTODateTimeDan | BYTE | IOD_PTO | PTO:.DateTime.Dan | [6 empty] | 6157 | 1 | 0x534091bc
PTODateTimeLeto | BYTE | IOD_PTO | PTO:.DateTime.Leto | [6 empty] | 6157 | 1 | 0x534091bd
PTODateTimeMesec | BYTE | IOD_PTO | PTO:.DateTime.Mesec | [6 empty] | 6157 | 1 | 0x534091be
PTODateTimeMinuta | BYTE | IOD_PTO | PTO:.DateTime.Minuta | [6 empty] | 6157 | 1 | 0x534091bf
PTODateTimeSekunda | BYTE | IOD_PTO | PTO:.DateTime.Sekunda | [6 empty] | 6157 | 1 | 0x534091c0
PTODateTimeUra | BYTE | IOD_PTO | PTO:.DateTime.Ura | [6 empty] | 6157 | 1 | 0x534091c1
PTODI_A1Q01_DovUpsA_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q01_DovUpsA_ON | [6 empty] | 6157 | 1 | 0x534091d0
PTODI_A1Q02_DovByA_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q02_DovByA_ON | [6 empty] | 6157 | 1 | 0x534091e0
PTODI_A1Q0_GlavnoSti_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q0_GlavnoSti_ON | [6 empty] | 6157 | 1 | 0x534091f0
PTODI_A1Q11_OdcUpsA_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q11_OdcUpsA_IZP | [6 empty] | 6157 | 1 | 0x53409200
PTODI_A1Q11_OdcUpsA_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q11_OdcUpsA_ON | [6 empty] | 6157 | 1 | 0x53409210
PTODI_A1Q12_OdcByUpsA_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q12_OdcByUpsA_IZP | [6 empty] | 6157 | 1 | 0x53409220
PTODI_A1Q12_OdcByUpsA_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q12_OdcByUpsA_ON | [6 empty] | 6157 | 1 | 0x53409230
PTODI_A1Q13_OdcByA_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q13_OdcByA_IZP | [6 empty] | 6157 | 1 | 0x53409240
PTODI_A1Q13_OdcByA_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q13_OdcByA_ON | [6 empty] | 6157 | 1 | 0x53409250
PTODI_A2Q0_GlavnoSti_ON | DIGITAL | IOD_PTO | PTO:.DI_A2Q0_GlavnoSti_ON | [6 empty] | 6157 | 1 | 0x53409260
PTODI_F201_OdcKl1ZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F201_OdcKl1ZE_IZP | [6 empty] | 6157 | 1 | 0x53409270
PTODI_F201_OdcKl1ZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F201_OdcKl1ZE_ON | [6 empty] | 6157 | 1 | 0x53409280
PTODI_F202_OdcKl2ZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F202_OdcKl2ZE_IZP | [6 empty] | 6157 | 1 | 0x53409290
PTODI_F202_OdcKl2ZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F202_OdcKl2ZE_ON | [6 empty] | 6157 | 1 | 0x534092a0
PTODI_F203_OdcKl3ZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F203_OdcKl3ZE_IZP | [6 empty] | 6157 | 1 | 0x534092b0
PTODI_F203_OdcKl3ZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F203_OdcKl3ZE_ON | [6 empty] | 6157 | 1 | 0x534092c0
PTODI_F204_OdcKl4ZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F204_OdcKl4ZE_IZP | [6 empty] | 6157 | 1 | 0x534092d0
PTODI_F204_OdcKl4ZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F204_OdcKl4ZE_ON | [6 empty] | 6157 | 1 | 0x534092e0
PTODI_F205_OdcKl5aZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F205_OdcKl5aZE_IZP | [6 empty] | 6157 | 1 | 0x534092f0
PTODI_F205_OdcKl5aZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F205_OdcKl5aZE_ON | [6 empty] | 6157 | 1 | 0x53409300
PTODI_F206_OdcKl5bZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F206_OdcKl5bZE_IZP | [6 empty] | 6157 | 1 | 0x53409310
PTODI_F206_OdcKl5bZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F206_OdcKl5bZE_ON | [6 empty] | 6157 | 1 | 0x53409320
PTODI_F207_OdcKl6aZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F207_OdcKl6aZE_IZP | [6 empty] | 6157 | 1 | 0x53409330
PTODI_F207_OdcKl6aZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F207_OdcKl6aZE_ON | [6 empty] | 6157 | 1 | 0x53409340
PTODI_F208_OdcKl6bZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F208_OdcKl6bZE_IZP | [6 empty] | 6157 | 1 | 0x53409350
PTODI_F208_OdcKl6bZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F208_OdcKl6bZE_ON | [6 empty] | 6157 | 1 | 0x53409360
PTODI_IzpadMreze | DIGITAL | IOD_PTO | PTO:.DI_IzpadMreze | [6 empty] | 6157 | 1 | 0x53409370
PTODI_Klima1_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima1_ERR | [6 empty] | 6157 | 1 | 0x53409380
PTODI_Klima1_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima1_ON | [6 empty] | 6157 | 1 | 0x53409390
PTODI_Klima2_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima2_ERR | [6 empty] | 6157 | 1 | 0x534093a0
PTODI_Klima2_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima2_ON | [6 empty] | 6157 | 1 | 0x534093b0
PTODI_Klima3_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima3_ERR | [6 empty] | 6157 | 1 | 0x534093c0
PTODI_Klima3_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima3_ON | [6 empty] | 6157 | 1 | 0x534093d0
PTODI_Klima4_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima4_ERR | [6 empty] | 6157 | 1 | 0x534093e0
PTODI_Klima4_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima4_ON | [6 empty] | 6157 | 1 | 0x534093f0
PTODI_Klima5_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima5_ERR | [6 empty] | 6157 | 1 | 0x53409400
PTODI_Klima5_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima5_ON | [6 empty] | 6157 | 1 | 0x53409410
PTODI_Klima6_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima6_ERR | [6 empty] | 6157 | 1 | 0x53409420
PTODI_Klima6_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima6_ON | [6 empty] | 6157 | 1 | 0x53409430
PTODI_KlimaSplitPP_ERR | DIGITAL | IOD_PTO | PTO:.DI_KlimaSplitPP_ERR | [6 empty] | 6157 | 1 | 0x53409440
PTODI_KlimaSplitPP_ON | DIGITAL | IOD_PTO | PTO:.DI_KlimaSplitPP_ON | [6 empty] | 6157 | 1 | 0x53409450
PTODI_PrenapA1_OK | DIGITAL | IOD_PTO | PTO:.DI_PrenapA1_OK | [6 empty] | 6157 | 1 | 0x53409460
PTODI_PrenapA2_OK | DIGITAL | IOD_PTO | PTO:.DI_PrenapA2_OK | [6 empty] | 6157 | 1 | 0x53409470
PTODI_Q101_OdcKlima1_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q101_OdcKlima1_IZP | [6 empty] | 6157 | 1 | 0x53409480
PTODI_Q101_OdcKlima1_ON | DIGITAL | IOD_PTO | PTO:.DI_Q101_OdcKlima1_ON | [6 empty] | 6157 | 1 | 0x53409490
PTODI_Q102_OdcKlima2_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q102_OdcKlima2_IZP | [6 empty] | 6157 | 1 | 0x534094a0
PTODI_Q102_OdcKlima2_ON | DIGITAL | IOD_PTO | PTO:.DI_Q102_OdcKlima2_ON | [6 empty] | 6157 | 1 | 0x534094b0
PTODI_Q103_OdcKlima3_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q103_OdcKlima3_IZP | [6 empty] | 6157 | 1 | 0x534094c0
PTODI_Q103_OdcKlima3_ON | DIGITAL | IOD_PTO | PTO:.DI_Q103_OdcKlima3_ON | [6 empty] | 6157 | 1 | 0x534094d0
PTODI_Q104_OdcKlima4_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q104_OdcKlima4_IZP | [6 empty] | 6157 | 1 | 0x534094e0
PTODI_Q104_OdcKlima4_ON | DIGITAL | IOD_PTO | PTO:.DI_Q104_OdcKlima4_ON | [6 empty] | 6157 | 1 | 0x534094f0
PTODI_Q105_OdcKlima5_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q105_OdcKlima5_IZP | [6 empty] | 6157 | 1 | 0x53409500
PTODI_Q105_OdcKlima5_ON | DIGITAL | IOD_PTO | PTO:.DI_Q105_OdcKlima5_ON | [6 empty] | 6157 | 1 | 0x53409510
PTODI_Q106_OdcKlima6_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q106_OdcKlima6_IZP | [6 empty] | 6157 | 1 | 0x53409520
PTODI_Q106_OdcKlima6_ON | DIGITAL | IOD_PTO | PTO:.DI_Q106_OdcKlima6_ON | [6 empty] | 6157 | 1 | 0x53409530
PTODI_Q107_OdcUsmSS2_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q107_OdcUsmSS2_IZP | [6 empty] | 6157 | 1 | 0x53409540
PTODI_Q107_OdcUsmSS2_ON | DIGITAL | IOD_PTO | PTO:.DI_Q107_OdcUsmSS2_ON | [6 empty] | 6157 | 1 | 0x53409550
PTODI_Q108_OdcUsmSS3_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q108_OdcUsmSS3_IZP | [6 empty] | 6157 | 1 | 0x53409560
PTODI_Q108_OdcUsmSS3_ON | DIGITAL | IOD_PTO | PTO:.DI_Q108_OdcUsmSS3_ON | [6 empty] | 6157 | 1 | 0x53409570
PTODI_RazlitjeVodeK1K2 | DIGITAL | IOD_PTO | PTO:.DI_RazlitjeVodeK1K2 | [6 empty] | 6157 | 1 | 0x53409580
PTODI_RazlitjeVodeK3K4 | DIGITAL | IOD_PTO | PTO:.DI_RazlitjeVodeK3K4 | [6 empty] | 6157 | 1 | 0x53409590
PTODI_RazlitjeVodeK5 | DIGITAL | IOD_PTO | PTO:.DI_RazlitjeVodeK5 | [6 empty] | 6157 | 1 | 0x534095a0
PTODI_RazlitjeVodeK6 | DIGITAL | IOD_PTO | PTO:.DI_RazlitjeVodeK6 | [6 empty] | 6157 | 1 | 0x534095b0
PTODI_UPS_Alarm | DIGITAL | IOD_PTO | PTO:.DI_UPS_Alarm | [6 empty] | 6157 | 1 | 0x534095c0
PTODI_UPS_BatNacin | DIGITAL | IOD_PTO | PTO:.DI_UPS_BatNacin | [6 empty] | 6157 | 1 | 0x534095d0
PTODI_UPS_Polnjenje | DIGITAL | IOD_PTO | PTO:.DI_UPS_Polnjenje | [6 empty] | 6157 | 1 | 0x534095e0
PTODI_UpsA_BypassON | DIGITAL | IOD_PTO | PTO:.DI_UpsA_BypassON | [6 empty] | 6157 | 1 | 0x534095f0
PTODI_UpsA_ERR | DIGITAL | IOD_PTO | PTO:.DI_UpsA_ERR | [6 empty] | 6157 | 1 | 0x53409600
PTODI_UpsB_BypassON | DIGITAL | IOD_PTO | PTO:.DI_UpsB_BypassON | [6 empty] | 6157 | 1 | 0x53409610
PTODI_UpsB_ERR | DIGITAL | IOD_PTO | PTO:.DI_UpsB_ERR | [6 empty] | 6157 | 1 | 0x53409620
PTODI_UQ11_OdcPMM_IZP | DIGITAL | IOD_PTO | PTO:.DI_UQ11_OdcPMM_IZP | [6 empty] | 6157 | 1 | 0x53409630
PTODI_UQ11_OdcPMM_ON | DIGITAL | IOD_PTO | PTO:.DI_UQ11_OdcPMM_ON | [6 empty] | 6157 | 1 | 0x53409640
PTODI_UQ12_OdcPMM_IZP | DIGITAL | IOD_PTO | PTO:.DI_UQ12_OdcPMM_IZP | [6 empty] | 6157 | 1 | 0x53409650
PTODI_UQ12_OdcPMM_ON | DIGITAL | IOD_PTO | PTO:.DI_UQ12_OdcPMM_ON | [6 empty] | 6157 | 1 | 0x53409660
PTODIN_A1Q11_OdcUpsA_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q11_OdcUpsA_IZP | [6 empty] | 6157 | 1 | 0x53409670
PTODIN_A1Q12_OdcByUpsA_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q12_OdcByUpsA_IZP | [6 empty] | 6157 | 1 | 0x53409680
PTODIN_A1Q13_OdcByA_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q13_OdcByA_IZP | [6 empty] | 6157 | 1 | 0x53409690
PTODIN_F201_OdcKl1ZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F201_OdcKl1ZE_IZP | [6 empty] | 6157 | 1 | 0x534096a0
PTODIN_F202_OdcKl2ZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F202_OdcKl2ZE_IZP | [6 empty] | 6157 | 1 | 0x534096b0
PTODIN_F203_OdcKl3ZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F203_OdcKl3ZE_IZP | [6 empty] | 6157 | 1 | 0x534096c0
PTODIN_F204_OdcKl4ZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F204_OdcKl4ZE_IZP | [6 empty] | 6157 | 1 | 0x534096d0
PTODIN_F205_OdcKl5aZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F205_OdcKl5aZE_IZP | [6 empty] | 6157 | 1 | 0x534096e0
PTODIN_F206_OdcKl5bZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F206_OdcKl5bZE_IZP | [6 empty] | 6157 | 1 | 0x534096f0
PTODIN_F207_OdcKl6aZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F207_OdcKl6aZE_IZP | [6 empty] | 6157 | 1 | 0x53409700
PTODIN_F208_OdcKl6bZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F208_OdcKl6bZE_IZP | [6 empty] | 6157 | 1 | 0x53409710
PTODIN_Klima1_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima1_ERR | [6 empty] | 6157 | 1 | 0x53409720
PTODIN_Klima2_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima2_ERR | [6 empty] | 6157 | 1 | 0x53409730
PTODIN_Klima3_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima3_ERR | [6 empty] | 6157 | 1 | 0x53409740
PTODIN_Klima4_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima4_ERR | [6 empty] | 6157 | 1 | 0x53409750
PTODIN_Klima5_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima5_ERR | [6 empty] | 6157 | 1 | 0x53409760
PTODIN_Klima6_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima6_ERR | [6 empty] | 6157 | 1 | 0x53409770
PTODIN_KlimaSplitPP_ERR | DIGITAL | IOD_PTO | PTO:.DIN_KlimaSplitPP_ERR | [6 empty] | 6157 | 1 | 0x53409780
PTODIN_PrenapA1_OK | DIGITAL | IOD_PTO | PTO:.DIN_PrenapA1_OK | [6 empty] | 6157 | 1 | 0x53409790
PTODIN_PrenapA2_OK | DIGITAL | IOD_PTO | PTO:.DIN_PrenapA2_OK | [6 empty] | 6157 | 1 | 0x534097a0
PTODIN_Q101_OdcKlima1_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q101_OdcKlima1_IZP | [6 empty] | 6157 | 1 | 0x534097b0
PTODIN_Q102_OdcKlima2_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q102_OdcKlima2_IZP | [6 empty] | 6157 | 1 | 0x534097c0
PTODIN_Q103_OdcKlima3_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q103_OdcKlima3_IZP | [6 empty] | 6157 | 1 | 0x534097d0
PTODIN_Q104_OdcKlima4_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q104_OdcKlima4_IZP | [6 empty] | 6157 | 1 | 0x534097e0
PTODIN_Q105_OdcKlima5_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q105_OdcKlima5_IZP | [6 empty] | 6157 | 1 | 0x534097f0
PTODIN_Q106_OdcKlima6_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q106_OdcKlima6_IZP | [6 empty] | 6157 | 1 | 0x53409800
PTODIN_Q107_OdcUsmSS2_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q107_OdcUsmSS2_IZP | [6 empty] | 6157 | 1 | 0x53409810
PTODIN_Q108_OdcUsmSS3_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q108_OdcUsmSS3_IZP | [6 empty] | 6157 | 1 | 0x53409820
PTODIN_UpsA_BypassON | DIGITAL | IOD_PTO | PTO:.DIN_UpsA_BypassON | [6 empty] | 6157 | 1 | 0x53409830
PTODIN_UpsA_ERR | DIGITAL | IOD_PTO | PTO:.DIN_UpsA_ERR | [6 empty] | 6157 | 1 | 0x53409840
PTODIN_UpsB_BypassON | DIGITAL | IOD_PTO | PTO:.DIN_UpsB_BypassON | [6 empty] | 6157 | 1 | 0x53409850
PTODIN_UpsB_ERR | DIGITAL | IOD_PTO | PTO:.DIN_UpsB_ERR | [6 empty] | 6157 | 1 | 0x53409860
PTODIN_UQ11_OdcPMM_IZP | DIGITAL | IOD_PTO | PTO:.DIN_UQ11_OdcPMM_IZP | [6 empty] | 6157 | 1 | 0x53409870
PTODIN_UQ12_OdcPMM_IZP | DIGITAL | IOD_PTO | PTO:.DIN_UQ12_OdcPMM_IZP | [6 empty] | 6157 | 1 | 0x53409880
PTODO_Klima1_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima1_Izklop | [6 empty] | 6157 | 1 | 0x53409890
PTODO_Klima2_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima2_Izklop | [6 empty] | 6157 | 1 | 0x534098a0
PTODO_Klima3_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima3_Izklop | [6 empty] | 6157 | 1 | 0x534098b0
PTODO_Klima4_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima4_Izklop | [6 empty] | 6157 | 1 | 0x534098c0
PTODO_Klima5_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima5_Izklop | [6 empty] | 6157 | 1 | 0x534098d0
PTODO_Klima6_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima6_Izklop | [6 empty] | 6157 | 1 | 0x534098e0
PTOErrComKlima1 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[1] | [6 empty] | 6157 | 1 | 0x534098f0
PTOErrComKlima2 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[2] | [6 empty] | 6157 | 1 | 0x53409900
PTOErrComKlima3 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[3] | [6 empty] | 6157 | 1 | 0x53409910
PTOErrComKlima4 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[4] | [6 empty] | 6157 | 1 | 0x53409920
PTOErrComKlima5 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[5] | [6 empty] | 6157 | 1 | 0x53409930
PTOErrComKlima6 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[6] | [6 empty] | 6157 | 1 | 0x53409940
PTOErrCommScada | DIGITAL | IOD_PTO | PTO:.ErrCommScada | [6 empty] | 6157 | 1 | 0x53409950
PTOErrComPanelPLC | DIGITAL | IOD_PTO | PTO:.ErrComPanelPLC | [6 empty] | 6157 | 1 | 0x53409960
PTOErrComPMM | DIGITAL | IOD_PTO | PTO:.ErrComPMM | [6 empty] | 6157 | 1 | 0x53409970
PTOErrComPort2 | DIGITAL | IOD_PTO | PTO:.ErrComPort2 | [6 empty] | 6157 | 1 | 0x53409980
PTOErrComPort3 | DIGITAL | IOD_PTO | PTO:.ErrComPort3 | [6 empty] | 6157 | 1 | 0x53409990
PTOErrComPort4 | DIGITAL | IOD_PTO | PTO:.ErrComPort4 | [6 empty] | 6157 | 1 | 0x534099a0
PTOErrComUPS1 | DIGITAL | IOD_PTO | PTO:.ErrComUPS[1] | [6 empty] | 6157 | 1 | 0x534099b0
PTOErrComUPS2 | DIGITAL | IOD_PTO | PTO:.ErrComUPS[2] | [6 empty] | 6157 | 1 | 0x534099c0
PTOErrorComKlima1Code10 | BYTE | IOD_PTO | PTO:.ErrorComKlima[1].Code[10] | [6 empty] | 6157 | 1 | 0x534099d0
PTOErrorComKlima1Code11 | BYTE | IOD_PTO | PTO:.ErrorComKlima[1].Code[11] | [6 empty] | 6157 | 1 | 0x534099d1
PTOErrorComKlima1Code12 | BYTE | IOD_PTO | PTO:.ErrorComKlima[1].Code[12] | [6 empty] | 6157 | 1 | 0x534099d2
PTOErrorComKlima1Code13 | BYTE | IOD_PTO | PTO:.ErrorComKlima[1].Code[13] | [6 empty] | 6157 | 1 | 0x534099d3
PTOErrorComKlima1Code14 | BYTE | IOD_PTO | PTO:.ErrorComKlima[1].Code[14] | [6 empty] | 6157 | 1 | 0x534099d4
PTOErrorComKlima1Code15 | BYTE | IOD_PTO | PTO:.ErrorComKlima[1].Code[15] | [6 empty] | 6157 | 1 | 0x534099d5
PTOErrorComKlima1Code1 | BYTE | IOD_PTO | PTO:.ErrorComKlima[1].Code[1] | [6 empty] | 6157 | 1 | 0x534099d6
PTOErrorComKlima1Code2 | BYTE | IOD_PTO | PTO:.ErrorComKlima[1].Code[2] | [6 empty] | 6157 | 1 | 0x534099d7
PTOErrorComKlima1Code3 | BYTE | IOD_PTO | PTO:.ErrorComKlima[1].Code[3] | [6 empty] | 6157 | 1 | 0x534099d8
PTOErrorComKlima1Code4 | BYTE | IOD_PTO | PTO:.ErrorComKlima[1].Code[4] | [6 empty] | 6157 | 1 | 0x534099d9
PTOErrorComKlima1Code5 | BYTE | IOD_PTO | PTO:.ErrorComKlima[1].Code[5] | [6 empty] | 6157 | 1 | 0x534099da
PTOErrorComKlima1Code6 | BYTE | IOD_PTO | PTO:.ErrorComKlima[1].Code[6] | [6 empty] | 6157 | 1 | 0x534099db
PTOErrorComKlima1Code7 | BYTE | IOD_PTO | PTO:.ErrorComKlima[1].Code[7] | [6 empty] | 6157 | 1 | 0x534099dc
PTOErrorComKlima1Code8 | BYTE | IOD_PTO | PTO:.ErrorComKlima[1].Code[8] | [6 empty] | 6157 | 1 | 0x534099dd
PTOErrorComKlima1Code9 | BYTE | IOD_PTO | PTO:.ErrorComKlima[1].Code[9] | [6 empty] | 6157 | 1 | 0x534099de
PTOErrorComKlima1Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[1].Error | [6 empty] | 6157 | 1 | 0x534099e0
PTOErrorComKlima1Status | INT | IOD_PTO | PTO:.ErrorComKlima[1].Status | [6 empty] | 6157 | 1 | 0x534099f0
PTOErrorComKlima2Code10 | BYTE | IOD_PTO | PTO:.ErrorComKlima[2].Code[10] | [6 empty] | 6157 | 1 | 0x534099f1
PTOErrorComKlima2Code11 | BYTE | IOD_PTO | PTO:.ErrorComKlima[2].Code[11] | [6 empty] | 6157 | 1 | 0x534099f2
PTOErrorComKlima2Code12 | BYTE | IOD_PTO | PTO:.ErrorComKlima[2].Code[12] | [6 empty] | 6157 | 1 | 0x534099f3
PTOErrorComKlima2Code13 | BYTE | IOD_PTO | PTO:.ErrorComKlima[2].Code[13] | [6 empty] | 6157 | 1 | 0x534099f4
PTOErrorComKlima2Code14 | BYTE | IOD_PTO | PTO:.ErrorComKlima[2].Code[14] | [6 empty] | 6157 | 1 | 0x534099f5
PTOErrorComKlima2Code15 | BYTE | IOD_PTO | PTO:.ErrorComKlima[2].Code[15] | [6 empty] | 6157 | 1 | 0x534099f6
PTOErrorComKlima2Code1 | BYTE | IOD_PTO | PTO:.ErrorComKlima[2].Code[1] | [6 empty] | 6157 | 1 | 0x534099f7
PTOErrorComKlima2Code2 | BYTE | IOD_PTO | PTO:.ErrorComKlima[2].Code[2] | [6 empty] | 6157 | 1 | 0x534099f8
PTOErrorComKlima2Code3 | BYTE | IOD_PTO | PTO:.ErrorComKlima[2].Code[3] | [6 empty] | 6157 | 1 | 0x534099f9
PTOErrorComKlima2Code4 | BYTE | IOD_PTO | PTO:.ErrorComKlima[2].Code[4] | [6 empty] | 6157 | 1 | 0x534099fa
PTOErrorComKlima2Code5 | BYTE | IOD_PTO | PTO:.ErrorComKlima[2].Code[5] | [6 empty] | 6157 | 1 | 0x534099fb
PTOErrorComKlima2Code6 | BYTE | IOD_PTO | PTO:.ErrorComKlima[2].Code[6] | [6 empty] | 6157 | 1 | 0x534099fc
PTOErrorComKlima2Code7 | BYTE | IOD_PTO | PTO:.ErrorComKlima[2].Code[7] | [6 empty] | 6157 | 1 | 0x534099fd
PTOErrorComKlima2Code8 | BYTE | IOD_PTO | PTO:.ErrorComKlima[2].Code[8] | [6 empty] | 6157 | 1 | 0x534099fe
PTOErrorComKlima2Code9 | BYTE | IOD_PTO | PTO:.ErrorComKlima[2].Code[9] | [6 empty] | 6157 | 1 | 0x534099ff
PTOErrorComKlima2Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[2].Error | [6 empty] | 6157 | 1 | 0x53409a00
PTOErrorComKlima2Status | INT | IOD_PTO | PTO:.ErrorComKlima[2].Status | [6 empty] | 6157 | 1 | 0x53409a10
PTOErrorComKlima3Code10 | BYTE | IOD_PTO | PTO:.ErrorComKlima[3].Code[10] | [6 empty] | 6157 | 1 | 0x53409a11
PTOErrorComKlima3Code11 | BYTE | IOD_PTO | PTO:.ErrorComKlima[3].Code[11] | [6 empty] | 6157 | 1 | 0x53409a12
PTOErrorComKlima3Code12 | BYTE | IOD_PTO | PTO:.ErrorComKlima[3].Code[12] | [6 empty] | 6157 | 1 | 0x53409a13
PTOErrorComKlima3Code13 | BYTE | IOD_PTO | PTO:.ErrorComKlima[3].Code[13] | [6 empty] | 6157 | 1 | 0x53409a14
PTOErrorComKlima3Code14 | BYTE | IOD_PTO | PTO:.ErrorComKlima[3].Code[14] | [6 empty] | 6157 | 1 | 0x53409a15
PTOErrorComKlima3Code15 | BYTE | IOD_PTO | PTO:.ErrorComKlima[3].Code[15] | [6 empty] | 6157 | 1 | 0x53409a16
PTOErrorComKlima3Code1 | BYTE | IOD_PTO | PTO:.ErrorComKlima[3].Code[1] | [6 empty] | 6157 | 1 | 0x53409a17
PTOErrorComKlima3Code2 | BYTE | IOD_PTO | PTO:.ErrorComKlima[3].Code[2] | [6 empty] | 6157 | 1 | 0x53409a18
PTOErrorComKlima3Code3 | BYTE | IOD_PTO | PTO:.ErrorComKlima[3].Code[3] | [6 empty] | 6157 | 1 | 0x53409a19
PTOErrorComKlima3Code4 | BYTE | IOD_PTO | PTO:.ErrorComKlima[3].Code[4] | [6 empty] | 6157 | 1 | 0x53409a1a
PTOErrorComKlima3Code5 | BYTE | IOD_PTO | PTO:.ErrorComKlima[3].Code[5] | [6 empty] | 6157 | 1 | 0x53409a1b
PTOErrorComKlima3Code6 | BYTE | IOD_PTO | PTO:.ErrorComKlima[3].Code[6] | [6 empty] | 6157 | 1 | 0x53409a1c
PTOErrorComKlima3Code7 | BYTE | IOD_PTO | PTO:.ErrorComKlima[3].Code[7] | [6 empty] | 6157 | 1 | 0x53409a1d
PTOErrorComKlima3Code8 | BYTE | IOD_PTO | PTO:.ErrorComKlima[3].Code[8] | [6 empty] | 6157 | 1 | 0x53409a1e
PTOErrorComKlima3Code9 | BYTE | IOD_PTO | PTO:.ErrorComKlima[3].Code[9] | [6 empty] | 6157 | 1 | 0x53409a1f
PTOErrorComKlima3Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[3].Error | [6 empty] | 6157 | 1 | 0x53409a20
PTOErrorComKlima3Status | INT | IOD_PTO | PTO:.ErrorComKlima[3].Status | [6 empty] | 6157 | 1 | 0x53409a30
PTOErrorComKlima4Code10 | BYTE | IOD_PTO | PTO:.ErrorComKlima[4].Code[10] | [6 empty] | 6157 | 1 | 0x53409a31
PTOErrorComKlima4Code11 | BYTE | IOD_PTO | PTO:.ErrorComKlima[4].Code[11] | [6 empty] | 6157 | 1 | 0x53409a32
PTOErrorComKlima4Code12 | BYTE | IOD_PTO | PTO:.ErrorComKlima[4].Code[12] | [6 empty] | 6157 | 1 | 0x53409a33
PTOErrorComKlima4Code13 | BYTE | IOD_PTO | PTO:.ErrorComKlima[4].Code[13] | [6 empty] | 6157 | 1 | 0x53409a34
PTOErrorComKlima4Code14 | BYTE | IOD_PTO | PTO:.ErrorComKlima[4].Code[14] | [6 empty] | 6157 | 1 | 0x53409a35
PTOErrorComKlima4Code15 | BYTE | IOD_PTO | PTO:.ErrorComKlima[4].Code[15] | [6 empty] | 6157 | 1 | 0x53409a36
PTOErrorComKlima4Code1 | BYTE | IOD_PTO | PTO:.ErrorComKlima[4].Code[1] | [6 empty] | 6157 | 1 | 0x53409a37
PTOErrorComKlima4Code2 | BYTE | IOD_PTO | PTO:.ErrorComKlima[4].Code[2] | [6 empty] | 6157 | 1 | 0x53409a38
PTOErrorComKlima4Code3 | BYTE | IOD_PTO | PTO:.ErrorComKlima[4].Code[3] | [6 empty] | 6157 | 1 | 0x53409a39
PTOErrorComKlima4Code4 | BYTE | IOD_PTO | PTO:.ErrorComKlima[4].Code[4] | [6 empty] | 6157 | 1 | 0x53409a3a
PTOErrorComKlima4Code5 | BYTE | IOD_PTO | PTO:.ErrorComKlima[4].Code[5] | [6 empty] | 6157 | 1 | 0x53409a3b
PTOErrorComKlima4Code6 | BYTE | IOD_PTO | PTO:.ErrorComKlima[4].Code[6] | [6 empty] | 6157 | 1 | 0x53409a3c
PTOErrorComKlima4Code7 | BYTE | IOD_PTO | PTO:.ErrorComKlima[4].Code[7] | [6 empty] | 6157 | 1 | 0x53409a3d
PTOErrorComKlima4Code8 | BYTE | IOD_PTO | PTO:.ErrorComKlima[4].Code[8] | [6 empty] | 6157 | 1 | 0x53409a3e
PTOErrorComKlima4Code9 | BYTE | IOD_PTO | PTO:.ErrorComKlima[4].Code[9] | [6 empty] | 6157 | 1 | 0x53409a3f
PTOErrorComKlima4Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[4].Error | [6 empty] | 6157 | 1 | 0x53409a40
PTOErrorComKlima4Status | INT | IOD_PTO | PTO:.ErrorComKlima[4].Status | [6 empty] | 6157 | 1 | 0x53409a50
PTOErrorComKlima5Code10 | BYTE | IOD_PTO | PTO:.ErrorComKlima[5].Code[10] | [6 empty] | 6157 | 1 | 0x53409a51
PTOErrorComKlima5Code11 | BYTE | IOD_PTO | PTO:.ErrorComKlima[5].Code[11] | [6 empty] | 6157 | 1 | 0x53409a52
PTOErrorComKlima5Code12 | BYTE | IOD_PTO | PTO:.ErrorComKlima[5].Code[12] | [6 empty] | 6157 | 1 | 0x53409a53
PTOErrorComKlima5Code13 | BYTE | IOD_PTO | PTO:.ErrorComKlima[5].Code[13] | [6 empty] | 6157 | 1 | 0x53409a54
PTOErrorComKlima5Code14 | BYTE | IOD_PTO | PTO:.ErrorComKlima[5].Code[14] | [6 empty] | 6157 | 1 | 0x53409a55
PTOErrorComKlima5Code15 | BYTE | IOD_PTO | PTO:.ErrorComKlima[5].Code[15] | [6 empty] | 6157 | 1 | 0x53409a56
PTOErrorComKlima5Code1 | BYTE | IOD_PTO | PTO:.ErrorComKlima[5].Code[1] | [6 empty] | 6157 | 1 | 0x53409a57
PTOErrorComKlima5Code2 | BYTE | IOD_PTO | PTO:.ErrorComKlima[5].Code[2] | [6 empty] | 6157 | 1 | 0x53409a58
PTOErrorComKlima5Code3 | BYTE | IOD_PTO | PTO:.ErrorComKlima[5].Code[3] | [6 empty] | 6157 | 1 | 0x53409a59
PTOErrorComKlima5Code4 | BYTE | IOD_PTO | PTO:.ErrorComKlima[5].Code[4] | [6 empty] | 6157 | 1 | 0x53409a5a
PTOErrorComKlima5Code5 | BYTE | IOD_PTO | PTO:.ErrorComKlima[5].Code[5] | [6 empty] | 6157 | 1 | 0x53409a5b
PTOErrorComKlima5Code6 | BYTE | IOD_PTO | PTO:.ErrorComKlima[5].Code[6] | [6 empty] | 6157 | 1 | 0x53409a5c
PTOErrorComKlima5Code7 | BYTE | IOD_PTO | PTO:.ErrorComKlima[5].Code[7] | [6 empty] | 6157 | 1 | 0x53409a5d
PTOErrorComKlima5Code8 | BYTE | IOD_PTO | PTO:.ErrorComKlima[5].Code[8] | [6 empty] | 6157 | 1 | 0x53409a5e
PTOErrorComKlima5Code9 | BYTE | IOD_PTO | PTO:.ErrorComKlima[5].Code[9] | [6 empty] | 6157 | 1 | 0x53409a5f
PTOErrorComKlima5Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[5].Error | [6 empty] | 6157 | 1 | 0x53409a60
PTOErrorComKlima5Status | INT | IOD_PTO | PTO:.ErrorComKlima[5].Status | [6 empty] | 6157 | 1 | 0x53409a70
PTOErrorComKlima6Code10 | BYTE | IOD_PTO | PTO:.ErrorComKlima[6].Code[10] | [6 empty] | 6157 | 1 | 0x53409a71
PTOErrorComKlima6Code11 | BYTE | IOD_PTO | PTO:.ErrorComKlima[6].Code[11] | [6 empty] | 6157 | 1 | 0x53409a72
PTOErrorComKlima6Code12 | BYTE | IOD_PTO | PTO:.ErrorComKlima[6].Code[12] | [6 empty] | 6157 | 1 | 0x53409a73
PTOErrorComKlima6Code13 | BYTE | IOD_PTO | PTO:.ErrorComKlima[6].Code[13] | [6 empty] | 6157 | 1 | 0x53409a74
PTOErrorComKlima6Code14 | BYTE | IOD_PTO | PTO:.ErrorComKlima[6].Code[14] | [6 empty] | 6157 | 1 | 0x53409a75
PTOErrorComKlima6Code15 | BYTE | IOD_PTO | PTO:.ErrorComKlima[6].Code[15] | [6 empty] | 6157 | 1 | 0x53409a76
PTOErrorComKlima6Code1 | BYTE | IOD_PTO | PTO:.ErrorComKlima[6].Code[1] | [6 empty] | 6157 | 1 | 0x53409a77
PTOErrorComKlima6Code2 | BYTE | IOD_PTO | PTO:.ErrorComKlima[6].Code[2] | [6 empty] | 6157 | 1 | 0x53409a78
PTOErrorComKlima6Code3 | BYTE | IOD_PTO | PTO:.ErrorComKlima[6].Code[3] | [6 empty] | 6157 | 1 | 0x53409a79
PTOErrorComKlima6Code4 | BYTE | IOD_PTO | PTO:.ErrorComKlima[6].Code[4] | [6 empty] | 6157 | 1 | 0x53409a7a
PTOErrorComKlima6Code5 | BYTE | IOD_PTO | PTO:.ErrorComKlima[6].Code[5] | [6 empty] | 6157 | 1 | 0x53409a7b
PTOErrorComKlima6Code6 | BYTE | IOD_PTO | PTO:.ErrorComKlima[6].Code[6] | [6 empty] | 6157 | 1 | 0x53409a7c
PTOErrorComKlima6Code7 | BYTE | IOD_PTO | PTO:.ErrorComKlima[6].Code[7] | [6 empty] | 6157 | 1 | 0x53409a7d
PTOErrorComKlima6Code8 | BYTE | IOD_PTO | PTO:.ErrorComKlima[6].Code[8] | [6 empty] | 6157 | 1 | 0x53409a7e
PTOErrorComKlima6Code9 | BYTE | IOD_PTO | PTO:.ErrorComKlima[6].Code[9] | [6 empty] | 6157 | 1 | 0x53409a7f
PTOErrorComKlima6Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[6].Error | [6 empty] | 6157 | 1 | 0x53409a80
PTOErrorComKlima6Status | INT | IOD_PTO | PTO:.ErrorComKlima[6].Status | [6 empty] | 6157 | 1 | 0x53409a90
PTOErrorComPMMCode10 | BYTE | IOD_PTO | PTO:.ErrorComPMM.Code[10] | [6 empty] | 6157 | 1 | 0x53409a91
PTOErrorComPMMCode11 | BYTE | IOD_PTO | PTO:.ErrorComPMM.Code[11] | [6 empty] | 6157 | 1 | 0x53409a92
PTOErrorComPMMCode12 | BYTE | IOD_PTO | PTO:.ErrorComPMM.Code[12] | [6 empty] | 6157 | 1 | 0x53409a93
PTOErrorComPMMCode13 | BYTE | IOD_PTO | PTO:.ErrorComPMM.Code[13] | [6 empty] | 6157 | 1 | 0x53409a94
PTOErrorComPMMCode14 | BYTE | IOD_PTO | PTO:.ErrorComPMM.Code[14] | [6 empty] | 6157 | 1 | 0x53409a95
PTOErrorComPMMCode15 | BYTE | IOD_PTO | PTO:.ErrorComPMM.Code[15] | [6 empty] | 6157 | 1 | 0x53409a96
PTOErrorComPMMCode1 | BYTE | IOD_PTO | PTO:.ErrorComPMM.Code[1] | [6 empty] | 6157 | 1 | 0x53409a97
PTOErrorComPMMCode2 | BYTE | IOD_PTO | PTO:.ErrorComPMM.Code[2] | [6 empty] | 6157 | 1 | 0x53409a98
PTOErrorComPMMCode3 | BYTE | IOD_PTO | PTO:.ErrorComPMM.Code[3] | [6 empty] | 6157 | 1 | 0x53409a99
PTOErrorComPMMCode4 | BYTE | IOD_PTO | PTO:.ErrorComPMM.Code[4] | [6 empty] | 6157 | 1 | 0x53409a9a
PTOErrorComPMMCode5 | BYTE | IOD_PTO | PTO:.ErrorComPMM.Code[5] | [6 empty] | 6157 | 1 | 0x53409a9b
PTOErrorComPMMCode6 | BYTE | IOD_PTO | PTO:.ErrorComPMM.Code[6] | [6 empty] | 6157 | 1 | 0x53409a9c
PTOErrorComPMMCode7 | BYTE | IOD_PTO | PTO:.ErrorComPMM.Code[7] | [6 empty] | 6157 | 1 | 0x53409a9d
PTOErrorComPMMCode8 | BYTE | IOD_PTO | PTO:.ErrorComPMM.Code[8] | [6 empty] | 6157 | 1 | 0x53409a9e
PTOErrorComPMMCode9 | BYTE | IOD_PTO | PTO:.ErrorComPMM.Code[9] | [6 empty] | 6157 | 1 | 0x53409a9f
PTOErrorComPMMError | DIGITAL | IOD_PTO | PTO:.ErrorComPMM.Error | [6 empty] | 6157 | 1 | 0x53409aa0
PTOErrorComPMMStatus | INT | IOD_PTO | PTO:.ErrorComPMM.Status | [6 empty] | 6157 | 1 | 0x53409ab0
PTOErrorComUPS1Code10 | BYTE | IOD_PTO | PTO:.ErrorComUPS[1].Code[10] | [6 empty] | 6157 | 1 | 0x53409ab1
PTOErrorComUPS1Code11 | BYTE | IOD_PTO | PTO:.ErrorComUPS[1].Code[11] | [6 empty] | 6157 | 1 | 0x53409ab2
PTOErrorComUPS1Code12 | BYTE | IOD_PTO | PTO:.ErrorComUPS[1].Code[12] | [6 empty] | 6157 | 1 | 0x53409ab3
PTOErrorComUPS1Code13 | BYTE | IOD_PTO | PTO:.ErrorComUPS[1].Code[13] | [6 empty] | 6157 | 1 | 0x53409ab4
PTOErrorComUPS1Code14 | BYTE | IOD_PTO | PTO:.ErrorComUPS[1].Code[14] | [6 empty] | 6157 | 1 | 0x53409ab5
PTOErrorComUPS1Code15 | BYTE | IOD_PTO | PTO:.ErrorComUPS[1].Code[15] | [6 empty] | 6157 | 1 | 0x53409ab6
PTOErrorComUPS1Code1 | BYTE | IOD_PTO | PTO:.ErrorComUPS[1].Code[1] | [6 empty] | 6157 | 1 | 0x53409ab7
PTOErrorComUPS1Code2 | BYTE | IOD_PTO | PTO:.ErrorComUPS[1].Code[2] | [6 empty] | 6157 | 1 | 0x53409ab8
PTOErrorComUPS1Code3 | BYTE | IOD_PTO | PTO:.ErrorComUPS[1].Code[3] | [6 empty] | 6157 | 1 | 0x53409ab9
PTOErrorComUPS1Code4 | BYTE | IOD_PTO | PTO:.ErrorComUPS[1].Code[4] | [6 empty] | 6157 | 1 | 0x53409aba
PTOErrorComUPS1Code5 | BYTE | IOD_PTO | PTO:.ErrorComUPS[1].Code[5] | [6 empty] | 6157 | 1 | 0x53409abb
PTOErrorComUPS1Code6 | BYTE | IOD_PTO | PTO:.ErrorComUPS[1].Code[6] | [6 empty] | 6157 | 1 | 0x53409abc
PTOErrorComUPS1Code7 | BYTE | IOD_PTO | PTO:.ErrorComUPS[1].Code[7] | [6 empty] | 6157 | 1 | 0x53409abd
PTOErrorComUPS1Code8 | BYTE | IOD_PTO | PTO:.ErrorComUPS[1].Code[8] | [6 empty] | 6157 | 1 | 0x53409abe
PTOErrorComUPS1Code9 | BYTE | IOD_PTO | PTO:.ErrorComUPS[1].Code[9] | [6 empty] | 6157 | 1 | 0x53409abf
PTOErrorComUPS1Error | DIGITAL | IOD_PTO | PTO:.ErrorComUPS[1].Error | [6 empty] | 6157 | 1 | 0x53409ac0
PTOErrorComUPS1Status | INT | IOD_PTO | PTO:.ErrorComUPS[1].Status | [6 empty] | 6157 | 1 | 0x53409ad0
PTOErrorComUPS2Code10 | BYTE | IOD_PTO | PTO:.ErrorComUPS[2].Code[10] | [6 empty] | 6157 | 1 | 0x53409ad1
PTOErrorComUPS2Code11 | BYTE | IOD_PTO | PTO:.ErrorComUPS[2].Code[11] | [6 empty] | 6157 | 1 | 0x53409ad2
PTOErrorComUPS2Code12 | BYTE | IOD_PTO | PTO:.ErrorComUPS[2].Code[12] | [6 empty] | 6157 | 1 | 0x53409ad3
PTOErrorComUPS2Code13 | BYTE | IOD_PTO | PTO:.ErrorComUPS[2].Code[13] | [6 empty] | 6157 | 1 | 0x53409ad4
PTOErrorComUPS2Code14 | BYTE | IOD_PTO | PTO:.ErrorComUPS[2].Code[14] | [6 empty] | 6157 | 1 | 0x53409ad5
PTOErrorComUPS2Code15 | BYTE | IOD_PTO | PTO:.ErrorComUPS[2].Code[15] | [6 empty] | 6157 | 1 | 0x53409ad6
PTOErrorComUPS2Code1 | BYTE | IOD_PTO | PTO:.ErrorComUPS[2].Code[1] | [6 empty] | 6157 | 1 | 0x53409ad7
PTOErrorComUPS2Code2 | BYTE | IOD_PTO | PTO:.ErrorComUPS[2].Code[2] | [6 empty] | 6157 | 1 | 0x53409ad8
PTOErrorComUPS2Code3 | BYTE | IOD_PTO | PTO:.ErrorComUPS[2].Code[3] | [6 empty] | 6157 | 1 | 0x53409ad9
PTOErrorComUPS2Code4 | BYTE | IOD_PTO | PTO:.ErrorComUPS[2].Code[4] | [6 empty] | 6157 | 1 | 0x53409ada
PTOErrorComUPS2Code5 | BYTE | IOD_PTO | PTO:.ErrorComUPS[2].Code[5] | [6 empty] | 6157 | 1 | 0x53409adb
PTOErrorComUPS2Code6 | BYTE | IOD_PTO | PTO:.ErrorComUPS[2].Code[6] | [6 empty] | 6157 | 1 | 0x53409adc
PTOErrorComUPS2Code7 | BYTE | IOD_PTO | PTO:.ErrorComUPS[2].Code[7] | [6 empty] | 6157 | 1 | 0x53409add
PTOErrorComUPS2Code8 | BYTE | IOD_PTO | PTO:.ErrorComUPS[2].Code[8] | [6 empty] | 6157 | 1 | 0x53409ade
PTOErrorComUPS2Code9 | BYTE | IOD_PTO | PTO:.ErrorComUPS[2].Code[9] | [6 empty] | 6157 | 1 | 0x53409adf
PTOErrorComUPS2Error | DIGITAL | IOD_PTO | PTO:.ErrorComUPS[2].Error | [6 empty] | 6157 | 1 | 0x53409ae0
PTOErrorComUPS2Status | INT | IOD_PTO | PTO:.ErrorComUPS[2].Status | [6 empty] | 6157 | 1 | 0x53409af0
PTOKlima1Errors10 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[10] | [6 empty] | 6157 | 1 | 0x53409b00
PTOKlima1Errors11 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[11] | [6 empty] | 6157 | 1 | 0x53409b10
PTOKlima1Errors12 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[12] | [6 empty] | 6157 | 1 | 0x53409b20
PTOKlima1Errors13 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[13] | [6 empty] | 6157 | 1 | 0x53409b30
PTOKlima1Errors14 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[14] | [6 empty] | 6157 | 1 | 0x53409b40
PTOKlima1Errors15 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[15] | [6 empty] | 6157 | 1 | 0x53409b50
PTOKlima1Errors16 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[16] | [6 empty] | 6157 | 1 | 0x53409b60
PTOKlima1Errors17 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[17] | [6 empty] | 6157 | 1 | 0x53409b70
PTOKlima1Errors18 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[18] | [6 empty] | 6157 | 1 | 0x53409b80
PTOKlima1Errors19 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[19] | [6 empty] | 6157 | 1 | 0x53409b90
PTOKlima1Errors1 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[1] | [6 empty] | 6157 | 1 | 0x53409ba0
PTOKlima1Errors20 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[20] | [6 empty] | 6157 | 1 | 0x53409bb0
PTOKlima1Errors21 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[21] | [6 empty] | 6157 | 1 | 0x53409bc0
PTOKlima1Errors22 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[22] | [6 empty] | 6157 | 1 | 0x53409bd0
PTOKlima1Errors23 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[23] | [6 empty] | 6157 | 1 | 0x53409be0
PTOKlima1Errors24 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[24] | [6 empty] | 6157 | 1 | 0x53409bf0
PTOKlima1Errors25 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[25] | [6 empty] | 6157 | 1 | 0x53409c00
PTOKlima1Errors26 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[26] | [6 empty] | 6157 | 1 | 0x53409c10
PTOKlima1Errors27 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[27] | [6 empty] | 6157 | 1 | 0x53409c20
PTOKlima1Errors28 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[28] | [6 empty] | 6157 | 1 | 0x53409c30
PTOKlima1Errors29 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[29] | [6 empty] | 6157 | 1 | 0x53409c40
PTOKlima1Errors2 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[2] | [6 empty] | 6157 | 1 | 0x53409c50
PTOKlima1Errors30 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[30] | [6 empty] | 6157 | 1 | 0x53409c60
PTOKlima1Errors31 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[31] | [6 empty] | 6157 | 1 | 0x53409c70
PTOKlima1Errors32 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[32] | [6 empty] | 6157 | 1 | 0x53409c80
PTOKlima1Errors33 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[33] | [6 empty] | 6157 | 1 | 0x53409c90
PTOKlima1Errors34 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[34] | [6 empty] | 6157 | 1 | 0x53409ca0
PTOKlima1Errors35 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[35] | [6 empty] | 6157 | 1 | 0x53409cb0
PTOKlima1Errors3 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[3] | [6 empty] | 6157 | 1 | 0x53409cc0
PTOKlima1Errors4 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[4] | [6 empty] | 6157 | 1 | 0x53409cd0
PTOKlima1Errors5 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[5] | [6 empty] | 6157 | 1 | 0x53409ce0
PTOKlima1Errors6 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[6] | [6 empty] | 6157 | 1 | 0x53409cf0
PTOKlima1Errors7 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[7] | [6 empty] | 6157 | 1 | 0x53409d00
PTOKlima1Errors8 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[8] | [6 empty] | 6157 | 1 | 0x53409d10
PTOKlima1Errors9 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[9] | [6 empty] | 6157 | 1 | 0x53409d20
PTOKlima2Errors10 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[10] | [6 empty] | 6157 | 1 | 0x53409d30
PTOKlima2Errors11 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[11] | [6 empty] | 6157 | 1 | 0x53409d40
PTOKlima2Errors12 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[12] | [6 empty] | 6157 | 1 | 0x53409d50
PTOKlima2Errors13 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[13] | [6 empty] | 6157 | 1 | 0x53409d60
PTOKlima2Errors14 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[14] | [6 empty] | 6157 | 1 | 0x53409d70
PTOKlima2Errors15 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[15] | [6 empty] | 6157 | 1 | 0x53409d80
PTOKlima2Errors16 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[16] | [6 empty] | 6157 | 1 | 0x53409d90
PTOKlima2Errors17 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[17] | [6 empty] | 6157 | 1 | 0x53409da0
PTOKlima2Errors18 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[18] | [6 empty] | 6157 | 1 | 0x53409db0
PTOKlima2Errors19 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[19] | [6 empty] | 6157 | 1 | 0x53409dc0
PTOKlima2Errors1 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[1] | [6 empty] | 6157 | 1 | 0x53409dd0
PTOKlima2Errors20 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[20] | [6 empty] | 6157 | 1 | 0x53409de0
PTOKlima2Errors21 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[21] | [6 empty] | 6157 | 1 | 0x53409df0
PTOKlima2Errors22 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[22] | [6 empty] | 6157 | 1 | 0x53409e00
PTOKlima2Errors23 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[23] | [6 empty] | 6157 | 1 | 0x53409e10
PTOKlima2Errors24 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[24] | [6 empty] | 6157 | 1 | 0x53409e20
PTOKlima2Errors25 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[25] | [6 empty] | 6157 | 1 | 0x53409e30
PTOKlima2Errors26 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[26] | [6 empty] | 6157 | 1 | 0x53409e40
PTOKlima2Errors27 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[27] | [6 empty] | 6157 | 1 | 0x53409e50
PTOKlima2Errors28 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[28] | [6 empty] | 6157 | 1 | 0x53409e60
PTOKlima2Errors29 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[29] | [6 empty] | 6157 | 1 | 0x53409e70
PTOKlima2Errors2 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[2] | [6 empty] | 6157 | 1 | 0x53409e80
PTOKlima2Errors30 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[30] | [6 empty] | 6157 | 1 | 0x53409e90
PTOKlima2Errors31 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[31] | [6 empty] | 6157 | 1 | 0x53409ea0
PTOKlima2Errors32 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[32] | [6 empty] | 6157 | 1 | 0x53409eb0
PTOKlima2Errors33 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[33] | [6 empty] | 6157 | 1 | 0x53409ec0
PTOKlima2Errors34 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[34] | [6 empty] | 6157 | 1 | 0x53409ed0
PTOKlima2Errors35 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[35] | [6 empty] | 6157 | 1 | 0x53409ee0
PTOKlima2Errors3 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[3] | [6 empty] | 6157 | 1 | 0x53409ef0
PTOKlima2Errors4 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[4] | [6 empty] | 6157 | 1 | 0x53409f00
PTOKlima2Errors5 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[5] | [6 empty] | 6157 | 1 | 0x53409f10
PTOKlima2Errors6 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[6] | [6 empty] | 6157 | 1 | 0x53409f20
PTOKlima2Errors7 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[7] | [6 empty] | 6157 | 1 | 0x53409f30
PTOKlima2Errors8 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[8] | [6 empty] | 6157 | 1 | 0x53409f40
PTOKlima2Errors9 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[9] | [6 empty] | 6157 | 1 | 0x53409f50
PTOKlima3Errors10 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[10] | [6 empty] | 6157 | 1 | 0x53409f60
PTOKlima3Errors11 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[11] | [6 empty] | 6157 | 1 | 0x53409f70
PTOKlima3Errors12 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[12] | [6 empty] | 6157 | 1 | 0x53409f80
PTOKlima3Errors13 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[13] | [6 empty] | 6157 | 1 | 0x53409f90
PTOKlima3Errors14 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[14] | [6 empty] | 6157 | 1 | 0x53409fa0
PTOKlima3Errors15 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[15] | [6 empty] | 6157 | 1 | 0x53409fb0
PTOKlima3Errors16 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[16] | [6 empty] | 6157 | 1 | 0x53409fc0
PTOKlima3Errors17 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[17] | [6 empty] | 6157 | 1 | 0x53409fd0
PTOKlima3Errors18 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[18] | [6 empty] | 6157 | 1 | 0x53409fe0
PTOKlima3Errors19 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[19] | [6 empty] | 6157 | 1 | 0x53409ff0
PTOKlima3Errors1 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[1] | [6 empty] | 6157 | 1 | 0x5340a000
PTOKlima3Errors20 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[20] | [6 empty] | 6157 | 1 | 0x5340a010
PTOKlima3Errors21 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[21] | [6 empty] | 6157 | 1 | 0x5340a020
PTOKlima3Errors22 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[22] | [6 empty] | 6157 | 1 | 0x5340a030
PTOKlima3Errors23 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[23] | [6 empty] | 6157 | 1 | 0x5340a040
PTOKlima3Errors24 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[24] | [6 empty] | 6157 | 1 | 0x5340a050
PTOKlima3Errors25 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[25] | [6 empty] | 6157 | 1 | 0x5340a060
PTOKlima3Errors26 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[26] | [6 empty] | 6157 | 1 | 0x5340a070
PTOKlima3Errors27 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[27] | [6 empty] | 6157 | 1 | 0x5340a080
PTOKlima3Errors28 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[28] | [6 empty] | 6157 | 1 | 0x5340a090
PTOKlima3Errors29 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[29] | [6 empty] | 6157 | 1 | 0x5340a0a0
PTOKlima3Errors2 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[2] | [6 empty] | 6157 | 1 | 0x5340a0b0
PTOKlima3Errors30 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[30] | [6 empty] | 6157 | 1 | 0x5340a0c0
PTOKlima3Errors31 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[31] | [6 empty] | 6157 | 1 | 0x5340a0d0
PTOKlima3Errors32 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[32] | [6 empty] | 6157 | 1 | 0x5340a0e0
PTOKlima3Errors33 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[33] | [6 empty] | 6157 | 1 | 0x5340a0f0
PTOKlima3Errors34 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[34] | [6 empty] | 6157 | 1 | 0x5340a100
PTOKlima3Errors35 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[35] | [6 empty] | 6157 | 1 | 0x5340a110
PTOKlima3Errors3 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[3] | [6 empty] | 6157 | 1 | 0x5340a120
PTOKlima3Errors4 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[4] | [6 empty] | 6157 | 1 | 0x5340a130
PTOKlima3Errors5 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[5] | [6 empty] | 6157 | 1 | 0x5340a140
PTOKlima3Errors6 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[6] | [6 empty] | 6157 | 1 | 0x5340a150
PTOKlima3Errors7 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[7] | [6 empty] | 6157 | 1 | 0x5340a160
PTOKlima3Errors8 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[8] | [6 empty] | 6157 | 1 | 0x5340a170
PTOKlima3Errors9 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[9] | [6 empty] | 6157 | 1 | 0x5340a180
PTOKlima4Errors10 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[10] | [6 empty] | 6157 | 1 | 0x5340a190
PTOKlima4Errors11 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[11] | [6 empty] | 6157 | 1 | 0x5340a1a0
PTOKlima4Errors12 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[12] | [6 empty] | 6157 | 1 | 0x5340a1b0
PTOKlima4Errors13 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[13] | [6 empty] | 6157 | 1 | 0x5340a1c0
PTOKlima4Errors14 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[14] | [6 empty] | 6157 | 1 | 0x5340a1d0
PTOKlima4Errors15 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[15] | [6 empty] | 6157 | 1 | 0x5340a1e0
PTOKlima4Errors16 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[16] | [6 empty] | 6157 | 1 | 0x5340a1f0
PTOKlima4Errors17 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[17] | [6 empty] | 6157 | 1 | 0x5340a200
PTOKlima4Errors18 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[18] | [6 empty] | 6157 | 1 | 0x5340a210
PTOKlima4Errors19 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[19] | [6 empty] | 6157 | 1 | 0x5340a220
PTOKlima4Errors1 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[1] | [6 empty] | 6157 | 1 | 0x5340a230
PTOKlima4Errors20 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[20] | [6 empty] | 6157 | 1 | 0x5340a240
PTOKlima4Errors21 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[21] | [6 empty] | 6157 | 1 | 0x5340a250
PTOKlima4Errors22 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[22] | [6 empty] | 6157 | 1 | 0x5340a260
PTOKlima4Errors23 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[23] | [6 empty] | 6157 | 1 | 0x5340a270
PTOKlima4Errors24 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[24] | [6 empty] | 6157 | 1 | 0x5340a280
PTOKlima4Errors25 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[25] | [6 empty] | 6157 | 1 | 0x5340a290
PTOKlima4Errors26 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[26] | [6 empty] | 6157 | 1 | 0x5340a2a0
PTOKlima4Errors27 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[27] | [6 empty] | 6157 | 1 | 0x5340a2b0
PTOKlima4Errors28 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[28] | [6 empty] | 6157 | 1 | 0x5340a2c0
PTOKlima4Errors29 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[29] | [6 empty] | 6157 | 1 | 0x5340a2d0
PTOKlima4Errors2 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[2] | [6 empty] | 6157 | 1 | 0x5340a2e0
PTOKlima4Errors30 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[30] | [6 empty] | 6157 | 1 | 0x5340a2f0
PTOKlima4Errors31 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[31] | [6 empty] | 6157 | 1 | 0x5340a300
PTOKlima4Errors32 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[32] | [6 empty] | 6157 | 1 | 0x5340a310
PTOKlima4Errors33 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[33] | [6 empty] | 6157 | 1 | 0x5340a320
PTOKlima4Errors34 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[34] | [6 empty] | 6157 | 1 | 0x5340a330
PTOKlima4Errors35 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[35] | [6 empty] | 6157 | 1 | 0x5340a340
PTOKlima4Errors3 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[3] | [6 empty] | 6157 | 1 | 0x5340a350
PTOKlima4Errors4 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[4] | [6 empty] | 6157 | 1 | 0x5340a360
PTOKlima4Errors5 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[5] | [6 empty] | 6157 | 1 | 0x5340a370
PTOKlima4Errors6 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[6] | [6 empty] | 6157 | 1 | 0x5340a380
PTOKlima4Errors7 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[7] | [6 empty] | 6157 | 1 | 0x5340a390
PTOKlima4Errors8 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[8] | [6 empty] | 6157 | 1 | 0x5340a3a0
PTOKlima4Errors9 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[9] | [6 empty] | 6157 | 1 | 0x5340a3b0
PTOKlima5Errors10 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[10] | [6 empty] | 6157 | 1 | 0x5340a3c0
PTOKlima5Errors11 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[11] | [6 empty] | 6157 | 1 | 0x5340a3d0
PTOKlima5Errors12 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[12] | [6 empty] | 6157 | 1 | 0x5340a3e0
PTOKlima5Errors13 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[13] | [6 empty] | 6157 | 1 | 0x5340a3f0
PTOKlima5Errors14 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[14] | [6 empty] | 6157 | 1 | 0x5340a400
PTOKlima5Errors15 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[15] | [6 empty] | 6157 | 1 | 0x5340a410
PTOKlima5Errors16 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[16] | [6 empty] | 6157 | 1 | 0x5340a420
PTOKlima5Errors17 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[17] | [6 empty] | 6157 | 1 | 0x5340a430
PTOKlima5Errors18 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[18] | [6 empty] | 6157 | 1 | 0x5340a440
PTOKlima5Errors19 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[19] | [6 empty] | 6157 | 1 | 0x5340a450
PTOKlima5Errors1 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[1] | [6 empty] | 6157 | 1 | 0x5340a460
PTOKlima5Errors20 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[20] | [6 empty] | 6157 | 1 | 0x5340a470
PTOKlima5Errors21 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[21] | [6 empty] | 6157 | 1 | 0x5340a480
PTOKlima5Errors22 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[22] | [6 empty] | 6157 | 1 | 0x5340a490
PTOKlima5Errors23 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[23] | [6 empty] | 6157 | 1 | 0x5340a4a0
PTOKlima5Errors24 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[24] | [6 empty] | 6157 | 1 | 0x5340a4b0
PTOKlima5Errors25 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[25] | [6 empty] | 6157 | 1 | 0x5340a4c0
PTOKlima5Errors26 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[26] | [6 empty] | 6157 | 1 | 0x5340a4d0
PTOKlima5Errors27 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[27] | [6 empty] | 6157 | 1 | 0x5340a4e0
PTOKlima5Errors28 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[28] | [6 empty] | 6157 | 1 | 0x5340a4f0
PTOKlima5Errors29 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[29] | [6 empty] | 6157 | 1 | 0x5340a500
PTOKlima5Errors2 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[2] | [6 empty] | 6157 | 1 | 0x5340a510
PTOKlima5Errors30 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[30] | [6 empty] | 6157 | 1 | 0x5340a520
PTOKlima5Errors31 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[31] | [6 empty] | 6157 | 1 | 0x5340a530
PTOKlima5Errors32 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[32] | [6 empty] | 6157 | 1 | 0x5340a540
PTOKlima5Errors33 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[33] | [6 empty] | 6157 | 1 | 0x5340a550
PTOKlima5Errors34 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[34] | [6 empty] | 6157 | 1 | 0x5340a560
PTOKlima5Errors35 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[35] | [6 empty] | 6157 | 1 | 0x5340a570
PTOKlima5Errors3 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[3] | [6 empty] | 6157 | 1 | 0x5340a580
PTOKlima5Errors4 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[4] | [6 empty] | 6157 | 1 | 0x5340a590
PTOKlima5Errors5 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[5] | [6 empty] | 6157 | 1 | 0x5340a5a0
PTOKlima5Errors6 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[6] | [6 empty] | 6157 | 1 | 0x5340a5b0
PTOKlima5Errors7 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[7] | [6 empty] | 6157 | 1 | 0x5340a5c0
PTOKlima5Errors8 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[8] | [6 empty] | 6157 | 1 | 0x5340a5d0
PTOKlima5Errors9 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[9] | [6 empty] | 6157 | 1 | 0x5340a5e0
PTOKlima6Errors10 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[10] | [6 empty] | 6157 | 1 | 0x5340a5f0
PTOKlima6Errors11 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[11] | [6 empty] | 6157 | 1 | 0x5340a600
PTOKlima6Errors12 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[12] | [6 empty] | 6157 | 1 | 0x5340a610
PTOKlima6Errors13 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[13] | [6 empty] | 6157 | 1 | 0x5340a620
PTOKlima6Errors14 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[14] | [6 empty] | 6157 | 1 | 0x5340a630
PTOKlima6Errors15 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[15] | [6 empty] | 6157 | 1 | 0x5340a640
PTOKlima6Errors16 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[16] | [6 empty] | 6157 | 1 | 0x5340a650
PTOKlima6Errors17 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[17] | [6 empty] | 6157 | 1 | 0x5340a660
PTOKlima6Errors18 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[18] | [6 empty] | 6157 | 1 | 0x5340a670
PTOKlima6Errors19 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[19] | [6 empty] | 6157 | 1 | 0x5340a680
PTOKlima6Errors1 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[1] | [6 empty] | 6157 | 1 | 0x5340a690
PTOKlima6Errors20 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[20] | [6 empty] | 6157 | 1 | 0x5340a6a0
PTOKlima6Errors21 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[21] | [6 empty] | 6157 | 1 | 0x5340a6b0
PTOKlima6Errors22 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[22] | [6 empty] | 6157 | 1 | 0x5340a6c0
PTOKlima6Errors23 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[23] | [6 empty] | 6157 | 1 | 0x5340a6d0
PTOKlima6Errors24 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[24] | [6 empty] | 6157 | 1 | 0x5340a6e0
PTOKlima6Errors25 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[25] | [6 empty] | 6157 | 1 | 0x5340a6f0
PTOKlima6Errors26 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[26] | [6 empty] | 6157 | 1 | 0x5340a700
PTOKlima6Errors27 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[27] | [6 empty] | 6157 | 1 | 0x5340a710
PTOKlima6Errors28 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[28] | [6 empty] | 6157 | 1 | 0x5340a720
PTOKlima6Errors29 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[29] | [6 empty] | 6157 | 1 | 0x5340a730
PTOKlima6Errors2 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[2] | [6 empty] | 6157 | 1 | 0x5340a740
PTOKlima6Errors30 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[30] | [6 empty] | 6157 | 1 | 0x5340a750
PTOKlima6Errors31 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[31] | [6 empty] | 6157 | 1 | 0x5340a760
PTOKlima6Errors32 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[32] | [6 empty] | 6157 | 1 | 0x5340a770
PTOKlima6Errors33 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[33] | [6 empty] | 6157 | 1 | 0x5340a780
PTOKlima6Errors34 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[34] | [6 empty] | 6157 | 1 | 0x5340a790
PTOKlima6Errors35 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[35] | [6 empty] | 6157 | 1 | 0x5340a7a0
PTOKlima6Errors3 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[3] | [6 empty] | 6157 | 1 | 0x5340a7b0
PTOKlima6Errors4 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[4] | [6 empty] | 6157 | 1 | 0x5340a7c0
PTOKlima6Errors5 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[5] | [6 empty] | 6157 | 1 | 0x5340a7d0
PTOKlima6Errors6 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[6] | [6 empty] | 6157 | 1 | 0x5340a7e0
PTOKlima6Errors7 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[7] | [6 empty] | 6157 | 1 | 0x5340a7f0
PTOKlima6Errors8 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[8] | [6 empty] | 6157 | 1 | 0x5340a800
PTOKlima6Errors9 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[9] | [6 empty] | 6157 | 1 | 0x5340a810
PTOKlima1Deluje | DIGITAL | IOD_PTO | PTO:.Klima[1].Deluje | [6 empty] | 6157 | 1 | 0x5340a820
PTOKlima1FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[1].FenThermalCutout | [6 empty] | 6157 | 1 | 0x5340a830
PTOKlima1GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].GeneralAlarm | [6 empty] | 6157 | 1 | 0x5340a840
PTOKlima1GrelecStatus | BYTE | IOD_PTO | PTO:.Klima[1].GrelecStatus | [6 empty] | 6157 | 1 | 0x5340a850
PTOKlima1IzhodniVentStatus | BYTE | IOD_PTO | PTO:.Klima[1].IzhodniVentStatus | [6 empty] | 6157 | 1 | 0x5340a851
PTOKlima1Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Kompresor1naMejiObrUr | [6 empty] | 6157 | 1 | 0x5340a860
PTOKlima1Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Kompresor2naMejiObrUr | [6 empty] | 6157 | 1 | 0x5340a870
PTOKlima1KompresorStatus | BYTE | IOD_PTO | PTO:.Klima[1].KompresorStatus | [6 empty] | 6157 | 1 | 0x5340a880
PTOKlima1Napaka | DIGITAL | IOD_PTO | PTO:.Klima[1].Napaka | [6 empty] | 6157 | 1 | 0x5340a890
PTOKlima1NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaPriPretokuZraka | [6 empty] | 6157 | 1 | 0x5340a8a0
PTOKlima1NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorTempIzpiha | [6 empty] | 6157 | 1 | 0x5340a8b0
PTOKlima1NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorTempProstora | [6 empty] | 6157 | 1 | 0x5340a8c0
PTOKlima1NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorVlaznosti | [6 empty] | 6157 | 1 | 0x5340a8d0
PTOKlima1NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorZunanjeTemp | [6 empty] | 6157 | 1 | 0x5340a8e0
PTOKlima1NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[1].NiTokaVVlazilcu | [6 empty] | 6157 | 1 | 0x5340a8f0
PTOKlima1NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[1].NiVodeVVlazilcu | [6 empty] | 6157 | 1 | 0x5340a900
PTOKlima1NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[1].NizekPritiskKompresor1 | [6 empty] | 6157 | 1 | 0x5340a910
PTOKlima1NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[1].NizekPritiskKompresor2 | [6 empty] | 6157 | 1 | 0x5340a920
PTOKlima1NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[1].NizkaTempVProstoru | [6 empty] | 6157 | 1 | 0x5340a930
PTOKlima1NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[1].NizkaVlaznost | [6 empty] | 6157 | 1 | 0x5340a940
PTOKlima1ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[1].ObratovalneUre |  |  |  |  | h | #### | 6157 | 1 | 0x5340a950
PTOKlima1OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[1].OnOffEnablingBySupervisor | [6 empty] | 6157 | 1 | 0x5340a960
PTOKlima1PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].PozarniAlarm | [6 empty] | 6157 | 1 | 0x5340a970
PTOKlima1Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[1].Razvlazevanje | [6 empty] | 6157 | 1 | 0x5340a980
PTOKlima1RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[1].RemoteOFFtoOutput | [6 empty] | 6157 | 1 | 0x5340a990
PTOKlima1RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[1].RocniIzklop | [6 empty] | 6157 | 1 | 0x5340a9a0
PTOKlima1SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[1].SenzorjiStatus | [6 empty] | 6157 | 1 | 0x5340a9b0
PTOKlima1TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[1].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5340a9c0
PTOKlima1TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[1].TempIzpihanegaZraka | [6 empty] | 6157 | 1 | 0x5340a9c1
PTOKlima1UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[1].UnitOnOff | [6 empty] | 6157 | 1 | 0x5340a9d0
PTOKlima1VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[1].VisokaTempVProstoru | [6 empty] | 6157 | 1 | 0x5340a9e0
PTOKlima1VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[1].VisokaVlaznost | [6 empty] | 6157 | 1 | 0x5340a9f0
PTOKlima1VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[1].VisokTokVVlazilcu | [6 empty] | 6157 | 1 | 0x5340aa00
PTOKlima1Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[1].Vlazenje | [6 empty] | 6157 | 1 | 0x5340aa10
PTOKlima1VlazilecStatus | BYTE | IOD_PTO | PTO:.Klima[1].VlazilecStatus | [6 empty] | 6157 | 1 | 0x5340aa20
PTOKlima1VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[1].VlaznostProstora | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x5340aa21
PTOKlima1ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[1].ZamasenFilter | [6 empty] | 6157 | 1 | 0x5340aa30
PTOKlima1ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[1].ZunanjaTemp | [6 empty] | 6157 | 1 | 0x5340aa40
PTOKlima2Deluje | DIGITAL | IOD_PTO | PTO:.Klima[2].Deluje | [6 empty] | 6157 | 1 | 0x5340aa50
PTOKlima2FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[2].FenThermalCutout | [6 empty] | 6157 | 1 | 0x5340aa60
PTOKlima2GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].GeneralAlarm | [6 empty] | 6157 | 1 | 0x5340aa70
PTOKlima2GrelecStatus | BYTE | IOD_PTO | PTO:.Klima[2].GrelecStatus | [6 empty] | 6157 | 1 | 0x5340aa80
PTOKlima2IzhodniVentStatus | BYTE | IOD_PTO | PTO:.Klima[2].IzhodniVentStatus | [6 empty] | 6157 | 1 | 0x5340aa81
PTOKlima2Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Kompresor1naMejiObrUr | [6 empty] | 6157 | 1 | 0x5340aa90
PTOKlima2Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Kompresor2naMejiObrUr | [6 empty] | 6157 | 1 | 0x5340aaa0
PTOKlima2KompresorStatus | BYTE | IOD_PTO | PTO:.Klima[2].KompresorStatus | [6 empty] | 6157 | 1 | 0x5340aab0
PTOKlima2Napaka | DIGITAL | IOD_PTO | PTO:.Klima[2].Napaka | [6 empty] | 6157 | 1 | 0x5340aac0
PTOKlima2NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaPriPretokuZraka | [6 empty] | 6157 | 1 | 0x5340aad0
PTOKlima2NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorTempIzpiha | [6 empty] | 6157 | 1 | 0x5340aae0
PTOKlima2NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorTempProstora | [6 empty] | 6157 | 1 | 0x5340aaf0
PTOKlima2NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorVlaznosti | [6 empty] | 6157 | 1 | 0x5340ab00
PTOKlima2NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorZunanjeTemp | [6 empty] | 6157 | 1 | 0x5340ab10
PTOKlima2NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[2].NiTokaVVlazilcu | [6 empty] | 6157 | 1 | 0x5340ab20
PTOKlima2NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[2].NiVodeVVlazilcu | [6 empty] | 6157 | 1 | 0x5340ab30
PTOKlima2NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[2].NizekPritiskKompresor1 | [6 empty] | 6157 | 1 | 0x5340ab40
PTOKlima2NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[2].NizekPritiskKompresor2 | [6 empty] | 6157 | 1 | 0x5340ab50
PTOKlima2NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[2].NizkaTempVProstoru | [6 empty] | 6157 | 1 | 0x5340ab60
PTOKlima2NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[2].NizkaVlaznost | [6 empty] | 6157 | 1 | 0x5340ab70
PTOKlima2ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[2].ObratovalneUre |  |  |  |  | h | #### | 6157 | 1 | 0x5340ab80
PTOKlima2OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[2].OnOffEnablingBySupervisor | [6 empty] | 6157 | 1 | 0x5340ab90
PTOKlima2PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].PozarniAlarm | [6 empty] | 6157 | 1 | 0x5340aba0
PTOKlima2Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[2].Razvlazevanje | [6 empty] | 6157 | 1 | 0x5340abb0
PTOKlima2RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[2].RemoteOFFtoOutput | [6 empty] | 6157 | 1 | 0x5340abc0
PTOKlima2RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[2].RocniIzklop | [6 empty] | 6157 | 1 | 0x5340abd0
PTOKlima2SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[2].SenzorjiStatus | [6 empty] | 6157 | 1 | 0x5340abe0
PTOKlima2TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[2].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5340abf0
PTOKlima2TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[2].TempIzpihanegaZraka | [6 empty] | 6157 | 1 | 0x5340abf1
PTOKlima2UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[2].UnitOnOff | [6 empty] | 6157 | 1 | 0x5340ac00
PTOKlima2VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[2].VisokaTempVProstoru | [6 empty] | 6157 | 1 | 0x5340ac10
PTOKlima2VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[2].VisokaVlaznost | [6 empty] | 6157 | 1 | 0x5340ac20
PTOKlima2VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[2].VisokTokVVlazilcu | [6 empty] | 6157 | 1 | 0x5340ac30
PTOKlima2Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[2].Vlazenje | [6 empty] | 6157 | 1 | 0x5340ac40
PTOKlima2VlazilecStatus | BYTE | IOD_PTO | PTO:.Klima[2].VlazilecStatus | [6 empty] | 6157 | 1 | 0x5340ac50
PTOKlima2VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[2].VlaznostProstora | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x5340ac51
PTOKlima2ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[2].ZamasenFilter | [6 empty] | 6157 | 1 | 0x5340ac60
PTOKlima2ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[2].ZunanjaTemp | [6 empty] | 6157 | 1 | 0x5340ac70
PTOKlima3Deluje | DIGITAL | IOD_PTO | PTO:.Klima[3].Deluje | [6 empty] | 6157 | 1 | 0x5340ac80
PTOKlima3FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[3].FenThermalCutout | [6 empty] | 6157 | 1 | 0x5340ac90
PTOKlima3GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].GeneralAlarm | [6 empty] | 6157 | 1 | 0x5340aca0
PTOKlima3GrelecStatus | BYTE | IOD_PTO | PTO:.Klima[3].GrelecStatus | [6 empty] | 6157 | 1 | 0x5340acb0
PTOKlima3IzhodniVentStatus | BYTE | IOD_PTO | PTO:.Klima[3].IzhodniVentStatus | [6 empty] | 6157 | 1 | 0x5340acb1
PTOKlima3Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Kompresor1naMejiObrUr | [6 empty] | 6157 | 1 | 0x5340acc0
PTOKlima3Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Kompresor2naMejiObrUr | [6 empty] | 6157 | 1 | 0x5340acd0
PTOKlima3KompresorStatus | BYTE | IOD_PTO | PTO:.Klima[3].KompresorStatus | [6 empty] | 6157 | 1 | 0x5340ace0
PTOKlima3Napaka | DIGITAL | IOD_PTO | PTO:.Klima[3].Napaka | [6 empty] | 6157 | 1 | 0x5340acf0
PTOKlima3NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaPriPretokuZraka | [6 empty] | 6157 | 1 | 0x5340ad00
PTOKlima3NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorTempIzpiha | [6 empty] | 6157 | 1 | 0x5340ad10
PTOKlima3NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorTempProstora | [6 empty] | 6157 | 1 | 0x5340ad20
PTOKlima3NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorVlaznosti | [6 empty] | 6157 | 1 | 0x5340ad30
PTOKlima3NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorZunanjeTemp | [6 empty] | 6157 | 1 | 0x5340ad40
PTOKlima3NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[3].NiTokaVVlazilcu | [6 empty] | 6157 | 1 | 0x5340ad50
PTOKlima3NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[3].NiVodeVVlazilcu | [6 empty] | 6157 | 1 | 0x5340ad60
PTOKlima3NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[3].NizekPritiskKompresor1 | [6 empty] | 6157 | 1 | 0x5340ad70
PTOKlima3NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[3].NizekPritiskKompresor2 | [6 empty] | 6157 | 1 | 0x5340ad80
PTOKlima3NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[3].NizkaTempVProstoru | [6 empty] | 6157 | 1 | 0x5340ad90
PTOKlima3NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[3].NizkaVlaznost | [6 empty] | 6157 | 1 | 0x5340ada0
PTOKlima3ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[3].ObratovalneUre |  |  |  |  | h | #### | 6157 | 1 | 0x5340adb0
PTOKlima3OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[3].OnOffEnablingBySupervisor | [6 empty] | 6157 | 1 | 0x5340adc0
PTOKlima3PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].PozarniAlarm | [6 empty] | 6157 | 1 | 0x5340add0
PTOKlima3Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[3].Razvlazevanje | [6 empty] | 6157 | 1 | 0x5340ade0
PTOKlima3RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[3].RemoteOFFtoOutput | [6 empty] | 6157 | 1 | 0x5340adf0
PTOKlima3RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[3].RocniIzklop | [6 empty] | 6157 | 1 | 0x5340ae00
PTOKlima3SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[3].SenzorjiStatus | [6 empty] | 6157 | 1 | 0x5340ae10
PTOKlima3TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[3].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5340ae20
PTOKlima3TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[3].TempIzpihanegaZraka | [6 empty] | 6157 | 1 | 0x5340ae21
PTOKlima3UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[3].UnitOnOff | [6 empty] | 6157 | 1 | 0x5340ae30
PTOKlima3VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[3].VisokaTempVProstoru | [6 empty] | 6157 | 1 | 0x5340ae40
PTOKlima3VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[3].VisokaVlaznost | [6 empty] | 6157 | 1 | 0x5340ae50
PTOKlima3VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[3].VisokTokVVlazilcu | [6 empty] | 6157 | 1 | 0x5340ae60
PTOKlima3Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[3].Vlazenje | [6 empty] | 6157 | 1 | 0x5340ae70
PTOKlima3VlazilecStatus | BYTE | IOD_PTO | PTO:.Klima[3].VlazilecStatus | [6 empty] | 6157 | 1 | 0x5340ae80
PTOKlima3VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[3].VlaznostProstora | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x5340ae81
PTOKlima3ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[3].ZamasenFilter | [6 empty] | 6157 | 1 | 0x5340ae90
PTOKlima3ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[3].ZunanjaTemp | [6 empty] | 6157 | 1 | 0x5340aea0
PTOKlima4Deluje | DIGITAL | IOD_PTO | PTO:.Klima[4].Deluje | [6 empty] | 6157 | 1 | 0x5340aeb0
PTOKlima4FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[4].FenThermalCutout | [6 empty] | 6157 | 1 | 0x5340aec0
PTOKlima4GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].GeneralAlarm | [6 empty] | 6157 | 1 | 0x5340aed0
PTOKlima4GrelecStatus | BYTE | IOD_PTO | PTO:.Klima[4].GrelecStatus | [6 empty] | 6157 | 1 | 0x5340aee0
PTOKlima4IzhodniVentStatus | BYTE | IOD_PTO | PTO:.Klima[4].IzhodniVentStatus | [6 empty] | 6157 | 1 | 0x5340aee1
PTOKlima4Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Kompresor1naMejiObrUr | [6 empty] | 6157 | 1 | 0x5340aef0
PTOKlima4Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Kompresor2naMejiObrUr | [6 empty] | 6157 | 1 | 0x5340af00
PTOKlima4KompresorStatus | BYTE | IOD_PTO | PTO:.Klima[4].KompresorStatus | [6 empty] | 6157 | 1 | 0x5340af10
PTOKlima4Napaka | DIGITAL | IOD_PTO | PTO:.Klima[4].Napaka | [6 empty] | 6157 | 1 | 0x5340af20
PTOKlima4NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaPriPretokuZraka | [6 empty] | 6157 | 1 | 0x5340af30
PTOKlima4NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorTempIzpiha | [6 empty] | 6157 | 1 | 0x5340af40
PTOKlima4NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorTempProstora | [6 empty] | 6157 | 1 | 0x5340af50
PTOKlima4NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorVlaznosti | [6 empty] | 6157 | 1 | 0x5340af60
PTOKlima4NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorZunanjeTemp | [6 empty] | 6157 | 1 | 0x5340af70
PTOKlima4NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[4].NiTokaVVlazilcu | [6 empty] | 6157 | 1 | 0x5340af80
PTOKlima4NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[4].NiVodeVVlazilcu | [6 empty] | 6157 | 1 | 0x5340af90
PTOKlima4NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[4].NizekPritiskKompresor1 | [6 empty] | 6157 | 1 | 0x5340afa0
PTOKlima4NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[4].NizekPritiskKompresor2 | [6 empty] | 6157 | 1 | 0x5340afb0
PTOKlima4NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[4].NizkaTempVProstoru | [6 empty] | 6157 | 1 | 0x5340afc0
PTOKlima4NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[4].NizkaVlaznost | [6 empty] | 6157 | 1 | 0x5340afd0
PTOKlima4ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[4].ObratovalneUre |  |  |  |  | h | #### | 6157 | 1 | 0x5340afe0
PTOKlima4OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[4].OnOffEnablingBySupervisor | [6 empty] | 6157 | 1 | 0x5340aff0
PTOKlima4PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].PozarniAlarm | [6 empty] | 6157 | 1 | 0x5340b000
PTOKlima4Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[4].Razvlazevanje | [6 empty] | 6157 | 1 | 0x5340b010
PTOKlima4RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[4].RemoteOFFtoOutput | [6 empty] | 6157 | 1 | 0x5340b020
PTOKlima4RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[4].RocniIzklop | [6 empty] | 6157 | 1 | 0x5340b030
PTOKlima4SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[4].SenzorjiStatus | [6 empty] | 6157 | 1 | 0x5340b040
PTOKlima4TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[4].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5340b050
PTOKlima4TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[4].TempIzpihanegaZraka | [6 empty] | 6157 | 1 | 0x5340b051
PTOKlima4UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[4].UnitOnOff | [6 empty] | 6157 | 1 | 0x5340b060
PTOKlima4VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[4].VisokaTempVProstoru | [6 empty] | 6157 | 1 | 0x5340b070
PTOKlima4VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[4].VisokaVlaznost | [6 empty] | 6157 | 1 | 0x5340b080
PTOKlima4VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[4].VisokTokVVlazilcu | [6 empty] | 6157 | 1 | 0x5340b090
PTOKlima4Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[4].Vlazenje | [6 empty] | 6157 | 1 | 0x5340b0a0
PTOKlima4VlazilecStatus | BYTE | IOD_PTO | PTO:.Klima[4].VlazilecStatus | [6 empty] | 6157 | 1 | 0x5340b0b0
PTOKlima4VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[4].VlaznostProstora | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x5340b0b1
PTOKlima4ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[4].ZamasenFilter | [6 empty] | 6157 | 1 | 0x5340b0c0
PTOKlima4ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[4].ZunanjaTemp | [6 empty] | 6157 | 1 | 0x5340b0d0
PTOKlima5Deluje | DIGITAL | IOD_PTO | PTO:.Klima[5].Deluje | [6 empty] | 6157 | 1 | 0x5340b0e0
PTOKlima5FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[5].FenThermalCutout | [6 empty] | 6157 | 1 | 0x5340b0f0
PTOKlima5GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].GeneralAlarm | [6 empty] | 6157 | 1 | 0x5340b100
PTOKlima5GrelecStatus | BYTE | IOD_PTO | PTO:.Klima[5].GrelecStatus | [6 empty] | 6157 | 1 | 0x5340b110
PTOKlima5IzhodniVentStatus | BYTE | IOD_PTO | PTO:.Klima[5].IzhodniVentStatus | [6 empty] | 6157 | 1 | 0x5340b111
PTOKlima5Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Kompresor1naMejiObrUr | [6 empty] | 6157 | 1 | 0x5340b120
PTOKlima5Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Kompresor2naMejiObrUr | [6 empty] | 6157 | 1 | 0x5340b130
PTOKlima5KompresorStatus | BYTE | IOD_PTO | PTO:.Klima[5].KompresorStatus | [6 empty] | 6157 | 1 | 0x5340b140
PTOKlima5Napaka | DIGITAL | IOD_PTO | PTO:.Klima[5].Napaka | [6 empty] | 6157 | 1 | 0x5340b150
PTOKlima5NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaPriPretokuZraka | [6 empty] | 6157 | 1 | 0x5340b160
PTOKlima5NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorTempIzpiha | [6 empty] | 6157 | 1 | 0x5340b170
PTOKlima5NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorTempProstora | [6 empty] | 6157 | 1 | 0x5340b180
PTOKlima5NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorVlaznosti | [6 empty] | 6157 | 1 | 0x5340b190
PTOKlima5NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorZunanjeTemp | [6 empty] | 6157 | 1 | 0x5340b1a0
PTOKlima5NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[5].NiTokaVVlazilcu | [6 empty] | 6157 | 1 | 0x5340b1b0
PTOKlima5NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[5].NiVodeVVlazilcu | [6 empty] | 6157 | 1 | 0x5340b1c0
PTOKlima5NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[5].NizekPritiskKompresor1 | [6 empty] | 6157 | 1 | 0x5340b1d0
PTOKlima5NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[5].NizekPritiskKompresor2 | [6 empty] | 6157 | 1 | 0x5340b1e0
PTOKlima5NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[5].NizkaTempVProstoru | [6 empty] | 6157 | 1 | 0x5340b1f0
PTOKlima5NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[5].NizkaVlaznost | [6 empty] | 6157 | 1 | 0x5340b200
PTOKlima5ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[5].ObratovalneUre |  |  |  |  | h | #### | 6157 | 1 | 0x5340b210
PTOKlima5OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[5].OnOffEnablingBySupervisor | [6 empty] | 6157 | 1 | 0x5340b220
PTOKlima5PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].PozarniAlarm | [6 empty] | 6157 | 1 | 0x5340b230
PTOKlima5Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[5].Razvlazevanje | [6 empty] | 6157 | 1 | 0x5340b240
PTOKlima5RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[5].RemoteOFFtoOutput | [6 empty] | 6157 | 1 | 0x5340b250
PTOKlima5RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[5].RocniIzklop | [6 empty] | 6157 | 1 | 0x5340b260
PTOKlima5SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[5].SenzorjiStatus | [6 empty] | 6157 | 1 | 0x5340b270
PTOKlima5TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[5].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5340b280
PTOKlima5TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[5].TempIzpihanegaZraka | [6 empty] | 6157 | 1 | 0x5340b281
PTOKlima5UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[5].UnitOnOff | [6 empty] | 6157 | 1 | 0x5340b290
PTOKlima5VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[5].VisokaTempVProstoru | [6 empty] | 6157 | 1 | 0x5340b2a0
PTOKlima5VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[5].VisokaVlaznost | [6 empty] | 6157 | 1 | 0x5340b2b0
PTOKlima5VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[5].VisokTokVVlazilcu | [6 empty] | 6157 | 1 | 0x5340b2c0
PTOKlima5Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[5].Vlazenje | [6 empty] | 6157 | 1 | 0x5340b2d0
PTOKlima5VlazilecStatus | BYTE | IOD_PTO | PTO:.Klima[5].VlazilecStatus | [6 empty] | 6157 | 1 | 0x5340b2e0
PTOKlima5VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[5].VlaznostProstora | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x5340b2e1
PTOKlima5ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[5].ZamasenFilter | [6 empty] | 6157 | 1 | 0x5340b2f0
PTOKlima5ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[5].ZunanjaTemp | [6 empty] | 6157 | 1 | 0x5340b300
PTOKlima6Deluje | DIGITAL | IOD_PTO | PTO:.Klima[6].Deluje | [6 empty] | 6157 | 1 | 0x5340b310
PTOKlima6FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[6].FenThermalCutout | [6 empty] | 6157 | 1 | 0x5340b320
PTOKlima6GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].GeneralAlarm | [6 empty] | 6157 | 1 | 0x5340b330
PTOKlima6GrelecStatus | BYTE | IOD_PTO | PTO:.Klima[6].GrelecStatus | [6 empty] | 6157 | 1 | 0x5340b340
PTOKlima6IzhodniVentStatus | BYTE | IOD_PTO | PTO:.Klima[6].IzhodniVentStatus | [6 empty] | 6157 | 1 | 0x5340b341
PTOKlima6Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Kompresor1naMejiObrUr | [6 empty] | 6157 | 1 | 0x5340b350
PTOKlima6Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Kompresor2naMejiObrUr | [6 empty] | 6157 | 1 | 0x5340b360
PTOKlima6KompresorStatus | BYTE | IOD_PTO | PTO:.Klima[6].KompresorStatus | [6 empty] | 6157 | 1 | 0x5340b370
PTOKlima6Napaka | DIGITAL | IOD_PTO | PTO:.Klima[6].Napaka | [6 empty] | 6157 | 1 | 0x5340b380
PTOKlima6NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaPriPretokuZraka | [6 empty] | 6157 | 1 | 0x5340b390
PTOKlima6NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorTempIzpiha | [6 empty] | 6157 | 1 | 0x5340b3a0
PTOKlima6NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorTempProstora | [6 empty] | 6157 | 1 | 0x5340b3b0
PTOKlima6NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorVlaznosti | [6 empty] | 6157 | 1 | 0x5340b3c0
PTOKlima6NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorZunanjeTemp | [6 empty] | 6157 | 1 | 0x5340b3d0
PTOKlima6NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[6].NiTokaVVlazilcu | [6 empty] | 6157 | 1 | 0x5340b3e0
PTOKlima6NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[6].NiVodeVVlazilcu | [6 empty] | 6157 | 1 | 0x5340b3f0
PTOKlima6NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[6].NizekPritiskKompresor1 | [6 empty] | 6157 | 1 | 0x5340b400
PTOKlima6NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[6].NizekPritiskKompresor2 | [6 empty] | 6157 | 1 | 0x5340b410
PTOKlima6NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[6].NizkaTempVProstoru | [6 empty] | 6157 | 1 | 0x5340b420
PTOKlima6NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[6].NizkaVlaznost | [6 empty] | 6157 | 1 | 0x5340b430
PTOKlima6ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[6].ObratovalneUre |  |  |  |  | h | #### | 6157 | 1 | 0x5340b440
PTOKlima6OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[6].OnOffEnablingBySupervisor | [6 empty] | 6157 | 1 | 0x5340b450
PTOKlima6PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].PozarniAlarm | [6 empty] | 6157 | 1 | 0x5340b460
PTOKlima6Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[6].Razvlazevanje | [6 empty] | 6157 | 1 | 0x5340b470
PTOKlima6RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[6].RemoteOFFtoOutput | [6 empty] | 6157 | 1 | 0x5340b480
PTOKlima6RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[6].RocniIzklop | [6 empty] | 6157 | 1 | 0x5340b490
PTOKlima6SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[6].SenzorjiStatus | [6 empty] | 6157 | 1 | 0x5340b4a0
PTOKlima6TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[6].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5340b4b0
PTOKlima6TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[6].TempIzpihanegaZraka | [6 empty] | 6157 | 1 | 0x5340b4b1
PTOKlima6UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[6].UnitOnOff | [6 empty] | 6157 | 1 | 0x5340b4c0
PTOKlima6VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[6].VisokaTempVProstoru | [6 empty] | 6157 | 1 | 0x5340b4d0
PTOKlima6VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[6].VisokaVlaznost | [6 empty] | 6157 | 1 | 0x5340b4e0
PTOKlima6VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[6].VisokTokVVlazilcu | [6 empty] | 6157 | 1 | 0x5340b4f0
PTOKlima6Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[6].Vlazenje | [6 empty] | 6157 | 1 | 0x5340b500
PTOKlima6VlazilecStatus | BYTE | IOD_PTO | PTO:.Klima[6].VlazilecStatus | [6 empty] | 6157 | 1 | 0x5340b510
PTOKlima6VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[6].VlaznostProstora | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x5340b511
PTOKlima6ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[6].ZamasenFilter | [6 empty] | 6157 | 1 | 0x5340b520
PTOKlima6ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[6].ZunanjaTemp | [6 empty] | 6157 | 1 | 0x5340b530
PTOKlimeNaCas0 | DIGITAL | IOD_PTO | PTO:.KlimeNaCas[0] | [6 empty] | 6157 | 1 | 0x5340b540
PTOKlimeNaCas1 | DIGITAL | IOD_PTO | PTO:.KlimeNaCas[1] | [6 empty] | 6157 | 1 | 0x5340b550
PTOKlimeNaCas2 | DIGITAL | IOD_PTO | PTO:.KlimeNaCas[2] | [6 empty] | 6157 | 1 | 0x5340b560
PTOKlimeNaCas3 | DIGITAL | IOD_PTO | PTO:.KlimeNaCas[3] | [6 empty] | 6157 | 1 | 0x5340b570
PTOMrezaIzpad | DIGITAL | IOD_PTO | PTO:.MrezaIzpad | [6 empty] | 6157 | 1 | 0x5340b580
PTOMrezaIzpadKlimaOff1 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[1] | [6 empty] | 6157 | 1 | 0x5340b590
PTOMrezaIzpadKlimaOff2 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[2] | [6 empty] | 6157 | 1 | 0x5340b5a0
PTOMrezaIzpadKlimaOff3 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[3] | [6 empty] | 6157 | 1 | 0x5340b5b0
PTOMrezaIzpadKlimaOff4 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[4] | [6 empty] | 6157 | 1 | 0x5340b5c0
PTOMrezaIzpadKlimaOff5 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[5] | [6 empty] | 6157 | 1 | 0x5340b5d0
PTOMrezaIzpadKlimaOff6 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[6] | [6 empty] | 6157 | 1 | 0x5340b5e0
PTOMrezaIzpadVklopDelay1 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[1] | [6 empty] | 6157 | 1 | 0x5340b5f0
PTOMrezaIzpadVklopDelay2 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[2] | [6 empty] | 6157 | 1 | 0x5340b5f1
PTOMrezaIzpadVklopDelay3 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[3] | [6 empty] | 6157 | 1 | 0x5340b5f2
PTOMrezaIzpadVklopDelay4 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[4] | [6 empty] | 6157 | 1 | 0x5340b5f3
PTOMrezaIzpadVklopDelay5 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[5] | [6 empty] | 6157 | 1 | 0x5340b5f4
PTOMrezaIzpadVklopDelay6 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[6] | [6 empty] | 6157 | 1 | 0x5340b5f5
PTONapakaSenzorTemp1 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[1] | [6 empty] | 6157 | 1 | 0x5340b600
PTONapakaSenzorTemp2 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[2] | [6 empty] | 6157 | 1 | 0x5340b610
PTONapakaSenzorTemp3 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[3] | [6 empty] | 6157 | 1 | 0x5340b620
PTONapakaSenzorTemp4 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[4] | [6 empty] | 6157 | 1 | 0x5340b630
PTONapakaSenzorTemp5 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[5] | [6 empty] | 6157 | 1 | 0x5340b640
PTONapakaSenzorTemp6 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[6] | [6 empty] | 6157 | 1 | 0x5340b650
PTONapakaSenzorVlaga1 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[1] | [6 empty] | 6157 | 1 | 0x5340b660
PTONapakaSenzorVlaga2 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[2] | [6 empty] | 6157 | 1 | 0x5340b670
PTONapakaSenzorVlaga3 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[3] | [6 empty] | 6157 | 1 | 0x5340b680
PTONapakaSenzorVlaga4 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[4] | [6 empty] | 6157 | 1 | 0x5340b690
PTONapakaSenzorVlaga5 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[5] | [6 empty] | 6157 | 1 | 0x5340b6a0
PTONapakaSenzorVlaga6 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[6] | [6 empty] | 6157 | 1 | 0x5340b6b0
PTOPMMActiveEnergyConsumed_kWh | REAL | IOD_PTO | PTO:.PMM.ActiveEnergyConsumed_kWh |  |  |  |  | kVAr | #### | 6157 | 1 | 0x5340b6c0
PTOPMMActivePowerPhaseA_kW | REAL | IOD_PTO | PTO:.PMM.ActivePowerPhaseA_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 1 | 0x5340b6c1
PTOPMMActivePowerPhaseB_kW | REAL | IOD_PTO | PTO:.PMM.ActivePowerPhaseB_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 1 | 0x5340b6c2
PTOPMMActivePowerPhaseC_kW | REAL | IOD_PTO | PTO:.PMM.ActivePowerPhaseC_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 1 | 0x5340b6c3
PTOPMMAlarmPhase1C01_16_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C01_16_60to80 | [6 empty] | 6157 | 1 | 0x5340b6c4
PTOPMMAlarmPhase1C01_16_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C01_16_over80 | [6 empty] | 6157 | 1 | 0x5340b6c5
PTOPMMAlarmPhase1C17_32_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C17_32_60to80 | [6 empty] | 6157 | 1 | 0x5340b6c6
PTOPMMAlarmPhase1C17_32_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C17_32_over80 | [6 empty] | 6157 | 1 | 0x5340b6c7
PTOPMMAlarmPhase1C33_42_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C33_42_60to80 | [6 empty] | 6157 | 1 | 0x5340b6c8
PTOPMMAlarmPhase1C33_42_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C33_42_over80 | [6 empty] | 6157 | 1 | 0x5340b6c9
PTOPMMAlarmPhase2C01_16_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C01_16_60to80 | [6 empty] | 6157 | 1 | 0x5340b6ca
PTOPMMAlarmPhase2C01_16_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C01_16_over80 | [6 empty] | 6157 | 1 | 0x5340b6cb
PTOPMMAlarmPhase2C17_32_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C17_32_60to80 | [6 empty] | 6157 | 1 | 0x5340b6cc
PTOPMMAlarmPhase2C17_32_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C17_32_over80 | [6 empty] | 6157 | 1 | 0x5340b6cd
PTOPMMAlarmPhase2C33_42_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C33_42_60to80 | [6 empty] | 6157 | 1 | 0x5340b6ce
PTOPMMAlarmPhase2C33_42_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C33_42_over80 | [6 empty] | 6157 | 1 | 0x5340b6cf
PTOPMMAlarmPhase3C01_16_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C01_16_60to80 | [6 empty] | 6157 | 1 | 0x5340b6d0
PTOPMMAlarmPhase3C01_16_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C01_16_over80 | [6 empty] | 6157 | 1 | 0x5340b6d1
PTOPMMAlarmPhase3C17_32_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C17_32_60to80 | [6 empty] | 6157 | 1 | 0x5340b6d2
PTOPMMAlarmPhase3C17_32_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C17_32_over80 | [6 empty] | 6157 | 1 | 0x5340b6d3
PTOPMMAlarmPhase3C33_42_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C33_42_60to80 | [6 empty] | 6157 | 1 | 0x5340b6d4
PTOPMMAlarmPhase3C33_42_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C33_42_over80 | [6 empty] | 6157 | 1 | 0x5340b6d5
PTOPMMAparentPowerPhaseA | REAL | IOD_PTO | PTO:.PMM.AparentPowerPhaseA | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 1 | 0x5340b6d6
PTOPMMAparentPowerPhaseB | REAL | IOD_PTO | PTO:.PMM.AparentPowerPhaseB | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 1 | 0x5340b6d7
PTOPMMAparentPowerPhaseC | REAL | IOD_PTO | PTO:.PMM.AparentPowerPhaseC | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 1 | 0x5340b6d8
PTOPMMAverageCurrent_A | REAL | IOD_PTO | PTO:.PMM.AverageCurrent_A | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b6d9
PTOPMMAveragePhaseToNeutral_V | REAL | IOD_PTO | PTO:.PMM.AveragePhaseToNeutral_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 1 | 0x5340b6da
PTOPMMAveragePhaseToPhase_V | REAL | IOD_PTO | PTO:.PMM.AveragePhaseToPhase_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 1 | 0x5340b6db
PTOPMMCurrentInPhaseA_A | REAL | IOD_PTO | PTO:.PMM.CurrentInPhaseA_A | 0 | 500 | 0 | 500 | A | ####.# | 6157 | 1 | 0x5340b6dc
PTOPMMCurrentInPhaseB_A | REAL | IOD_PTO | PTO:.PMM.CurrentInPhaseB_A | 0 | 500 | 0 | 500 | A | ####.# | 6157 | 1 | 0x5340b6dd
PTOPMMCurrentInPhaseC_A | REAL | IOD_PTO | PTO:.PMM.CurrentInPhaseC_A | 0 | 500 | 0 | 500 | A | ####.# | 6157 | 1 | 0x5340b6de
PTOPMMFrequency_Hz | REAL | IOD_PTO | PTO:.PMM.Frequency_Hz | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x5340b6df
PTOPMMNapaka | DIGITAL | IOD_PTO | PTO:.PMM.Napaka | [6 empty] | 6157 | 1 | 0x5340b6e0
PTOPMMPhase1Current10 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[10] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b6f0
PTOPMMPhase1Current11 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[11] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b6f1
PTOPMMPhase1Current12 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[12] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b6f2
PTOPMMPhase1Current13 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[13] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b6f3
PTOPMMPhase1Current14 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[14] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b6f4
PTOPMMPhase1Current15 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[15] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b6f5
PTOPMMPhase1Current16 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[16] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b6f6
PTOPMMPhase1Current17 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[17] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b6f7
PTOPMMPhase1Current18 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[18] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b6f8
PTOPMMPhase1Current19 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[19] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b6f9
PTOPMMPhase1Current1 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[1] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b6fa
PTOPMMPhase1Current20 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[20] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b6fb
PTOPMMPhase1Current21 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[21] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b6fc
PTOPMMPhase1Current22 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[22] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b6fd
PTOPMMPhase1Current23 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[23] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b6fe
PTOPMMPhase1Current24 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[24] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b6ff
PTOPMMPhase1Current25 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[25] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b700
PTOPMMPhase1Current26 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[26] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b701
PTOPMMPhase1Current27 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[27] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b702
PTOPMMPhase1Current28 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[28] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b703
PTOPMMPhase1Current29 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[29] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b704
PTOPMMPhase1Current2 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[2] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b705
PTOPMMPhase1Current30 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[30] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b706
PTOPMMPhase1Current31 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[31] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b707
PTOPMMPhase1Current32 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[32] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b708
PTOPMMPhase1Current33 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[33] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b709
PTOPMMPhase1Current34 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[34] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b70a
PTOPMMPhase1Current35 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[35] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b70b
PTOPMMPhase1Current36 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[36] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b70c
PTOPMMPhase1Current37 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[37] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b70d
PTOPMMPhase1Current38 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[38] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b70e
PTOPMMPhase1Current39 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[39] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b70f
PTOPMMPhase1Current3 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[3] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b710
PTOPMMPhase1Current40 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[40] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b711
PTOPMMPhase1Current41 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[41] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b712
PTOPMMPhase1Current42 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[42] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b713
PTOPMMPhase1Current4 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[4] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b714
PTOPMMPhase1Current5 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[5] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b715
PTOPMMPhase1Current6 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[6] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b716
PTOPMMPhase1Current7 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[7] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b717
PTOPMMPhase1Current8 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[8] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b718
PTOPMMPhase1Current9 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[9] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b719
PTOPMMPhase2Current10 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[10] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b71a
PTOPMMPhase2Current11 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[11] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b71b
PTOPMMPhase2Current12 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[12] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b71c
PTOPMMPhase2Current13 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[13] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b71d
PTOPMMPhase2Current14 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[14] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b71e
PTOPMMPhase2Current15 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[15] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b71f
PTOPMMPhase2Current16 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[16] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b720
PTOPMMPhase2Current17 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[17] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b721
PTOPMMPhase2Current18 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[18] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b722
PTOPMMPhase2Current19 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[19] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b723
PTOPMMPhase2Current1 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[1] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b724
PTOPMMPhase2Current20 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[20] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b725
PTOPMMPhase2Current21 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[21] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b726
PTOPMMPhase2Current22 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[22] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b727
PTOPMMPhase2Current23 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[23] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b728
PTOPMMPhase2Current24 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[24] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b729
PTOPMMPhase2Current25 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[25] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b72a
PTOPMMPhase2Current26 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[26] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b72b
PTOPMMPhase2Current27 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[27] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b72c
PTOPMMPhase2Current28 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[28] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b72d
PTOPMMPhase2Current29 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[29] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b72e
PTOPMMPhase2Current2 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[2] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b72f
PTOPMMPhase2Current30 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[30] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b730
PTOPMMPhase2Current31 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[31] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b731
PTOPMMPhase2Current32 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[32] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b732
PTOPMMPhase2Current33 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[33] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b733
PTOPMMPhase2Current34 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[34] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b734
PTOPMMPhase2Current35 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[35] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b735
PTOPMMPhase2Current36 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[36] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b736
PTOPMMPhase2Current37 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[37] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b737
PTOPMMPhase2Current38 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[38] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b738
PTOPMMPhase2Current39 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[39] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b739
PTOPMMPhase2Current3 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[3] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b73a
PTOPMMPhase2Current40 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[40] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b73b
PTOPMMPhase2Current41 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[41] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b73c
PTOPMMPhase2Current42 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[42] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b73d
PTOPMMPhase2Current4 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[4] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b73e
PTOPMMPhase2Current5 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[5] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b73f
PTOPMMPhase2Current6 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[6] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b740
PTOPMMPhase2Current7 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[7] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b741
PTOPMMPhase2Current8 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[8] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b742
PTOPMMPhase2Current9 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[9] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b743
PTOPMMPhase3Current10 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[10] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b744
PTOPMMPhase3Current11 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[11] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b745
PTOPMMPhase3Current12 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[12] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b746
PTOPMMPhase3Current13 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[13] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b747
PTOPMMPhase3Current14 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[14] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b748
PTOPMMPhase3Current15 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[15] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b749
PTOPMMPhase3Current16 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[16] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b74a
PTOPMMPhase3Current17 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[17] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b74b
PTOPMMPhase3Current18 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[18] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b74c
PTOPMMPhase3Current19 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[19] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b74d
PTOPMMPhase3Current1 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[1] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b74e
PTOPMMPhase3Current20 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[20] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b74f
PTOPMMPhase3Current21 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[21] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b750
PTOPMMPhase3Current22 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[22] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b751
PTOPMMPhase3Current23 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[23] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b752
PTOPMMPhase3Current24 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[24] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b753
PTOPMMPhase3Current25 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[25] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b754
PTOPMMPhase3Current26 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[26] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b755
PTOPMMPhase3Current27 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[27] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b756
PTOPMMPhase3Current28 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[28] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b757
PTOPMMPhase3Current29 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[29] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b758
PTOPMMPhase3Current2 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[2] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b759
PTOPMMPhase3Current30 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[30] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b75a
PTOPMMPhase3Current31 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[31] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b75b
PTOPMMPhase3Current32 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[32] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b75c
PTOPMMPhase3Current33 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[33] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b75d
PTOPMMPhase3Current34 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[34] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b75e
PTOPMMPhase3Current35 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[35] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b75f
PTOPMMPhase3Current36 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[36] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b760
PTOPMMPhase3Current37 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[37] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b761
PTOPMMPhase3Current38 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[38] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b762
PTOPMMPhase3Current39 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[39] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b763
PTOPMMPhase3Current3 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[3] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b764
PTOPMMPhase3Current40 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[40] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b765
PTOPMMPhase3Current41 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[41] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b766
PTOPMMPhase3Current42 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[42] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b767
PTOPMMPhase3Current4 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[4] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b768
PTOPMMPhase3Current5 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[5] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b769
PTOPMMPhase3Current6 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[6] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b76a
PTOPMMPhase3Current7 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[7] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b76b
PTOPMMPhase3Current8 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[8] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b76c
PTOPMMPhase3Current9 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[9] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 1 | 0x5340b76d
PTOPMMPowerFactorSys | REAL | IOD_PTO | PTO:.PMM.PowerFactorSys | 0 | 1 | 0 | 1 |  | ####.# | 6157 | 1 | 0x5340b76e
PTOPMMReactiveEnergyConsumed_kVARh | REAL | IOD_PTO | PTO:.PMM.ReactiveEnergyConsumed_kVARh |  |  |  |  | kVArh | ####.# | 6157 | 1 | 0x5340b76f
PTOPMMReactivePowerPhaseA | REAL | IOD_PTO | PTO:.PMM.ReactivePowerPhaseA | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 1 | 0x5340b770
PTOPMMReactivePowerPhaseB | REAL | IOD_PTO | PTO:.PMM.ReactivePowerPhaseB | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 1 | 0x5340b771
PTOPMMReactivePowerPhaseC | REAL | IOD_PTO | PTO:.PMM.ReactivePowerPhaseC | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 1 | 0x5340b772
PTOPMMTotalActivePower_kW | REAL | IOD_PTO | PTO:.PMM.TotalActivePower_kW | 0 | 300 | 0 | 300 | kW | ####.# | 6157 | 1 | 0x5340b773
PTOPMMTotalAparentPower_kVA | REAL | IOD_PTO | PTO:.PMM.TotalAparentPower_kVA | 0 | 300 | 0 | 300 | kVA | ####.# | 6157 | 1 | 0x5340b774
PTOPMMTotalPowerFactor | REAL | IOD_PTO | PTO:.PMM.TotalPowerFactor | 0 | 1 | 0 | 1 |  | ####.# | 6157 | 1 | 0x5340b775
PTOPMMTotalReactivePower_kVAR | REAL | IOD_PTO | PTO:.PMM.TotalReactivePower_kVAR | 0 | 300 | 0 | 300 | kVAr | ####.# | 6157 | 1 | 0x5340b776
PTOPMMVirA_fsys | REAL | IOD_PTO | PTO:.PMM.VirA_fsys | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x5340b777
PTOPMMVirA_Isys | REAL | IOD_PTO | PTO:.PMM.VirA_Isys | 0 | 1000 | 0 | 1000 | A | ####.# | 6157 | 1 | 0x5340b778
PTOPMMVirA_PFsys | REAL | IOD_PTO | PTO:.PMM.VirA_PFsys | 0 | 1 | 0 | 0 | 1 | ####.# | 6157 | 1 | 0x5340b779
PTOPMMVirA_Psys | REAL | IOD_PTO | PTO:.PMM.VirA_Psys | 0 | 300 | 0 | 300 | kW | ####.# | 6157 | 1 | 0x5340b77a
PTOPMMVirA_Qsys | REAL | IOD_PTO | PTO:.PMM.VirA_Qsys | 0 | 300 | 0 | 300 | kVAr | ####.# | 6157 | 1 | 0x5340b77b
PTOPMMVirA_Ssys | REAL | IOD_PTO | PTO:.PMM.VirA_Ssys | 0 | 300 | 0 | 300 | kVA | ####.# | 6157 | 1 | 0x5340b77c
PTOPMMVirA_Usys | REAL | IOD_PTO | PTO:.PMM.VirA_Usys | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 1 | 0x5340b77d
PTOPMMVirB_fsys | REAL | IOD_PTO | PTO:.PMM.VirB_fsys | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x5340b77e
PTOPMMVirB_Isys | REAL | IOD_PTO | PTO:.PMM.VirB_Isys | 0 | 1000 | 0 | 1000 | A | ####.# | 6157 | 1 | 0x5340b77f
PTOPMMVirB_PFsys | REAL | IOD_PTO | PTO:.PMM.VirB_PFsys | 0 | 1 | 0 | 0 | 1 | ####.# | 6157 | 1 | 0x5340b780
PTOPMMVirB_Psys | REAL | IOD_PTO | PTO:.PMM.VirB_Psys | 0 | 300 | 0 | 300 | kW | ####.# | 6157 | 1 | 0x5340b781
PTOPMMVirB_Qsys | REAL | IOD_PTO | PTO:.PMM.VirB_Qsys | 0 | 300 | 0 | 300 | kVAr | ####.# | 6157 | 1 | 0x5340b782
PTOPMMVirB_Ssys | REAL | IOD_PTO | PTO:.PMM.VirB_Ssys | 0 | 300 | 0 | 300 | kVA | ####.# | 6157 | 1 | 0x5340b783
PTOPMMVirB_Usys | REAL | IOD_PTO | PTO:.PMM.VirB_Usys | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 1 | 0x5340b784
PTOPMMVirBActiveEnergyConsumed_kWh | REAL | IOD_PTO | PTO:.PMM.VirBActiveEnergyConsumed_kWh |  |  |  |  | kVArh | ####.# | 6157 | 1 | 0x5340b785
PTOPMMVirBActivePowerPhaseA_kW | REAL | IOD_PTO | PTO:.PMM.VirBActivePowerPhaseA_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 1 | 0x5340b786
PTOPMMVirBActivePowerPhaseB_kW | REAL | IOD_PTO | PTO:.PMM.VirBActivePowerPhaseB_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 1 | 0x5340b787
PTOPMMVirBActivePowerPhaseC_kW | REAL | IOD_PTO | PTO:.PMM.VirBActivePowerPhaseC_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 1 | 0x5340b788
PTOPMMVirBAparentPowerPhaseA | REAL | IOD_PTO | PTO:.PMM.VirBAparentPowerPhaseA | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 1 | 0x5340b789
PTOPMMVirBAparentPowerPhaseB | REAL | IOD_PTO | PTO:.PMM.VirBAparentPowerPhaseB | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 1 | 0x5340b78a
PTOPMMVirBAparentPowerPhaseC | REAL | IOD_PTO | PTO:.PMM.VirBAparentPowerPhaseC | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 1 | 0x5340b78b
PTOPMMVirBAverageCurrent_A | REAL | IOD_PTO | PTO:.PMM.VirBAverageCurrent_A | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x5340b78c
PTOPMMVirBAveragePhaseToNeutral_V | REAL | IOD_PTO | PTO:.PMM.VirBAveragePhaseToNeutral_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 1 | 0x5340b78d
PTOPMMVirBAveragePhaseToPhase_V | REAL | IOD_PTO | PTO:.PMM.VirBAveragePhaseToPhase_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 1 | 0x5340b78e
PTOPMMVirBCurrentInPhaseA_A | REAL | IOD_PTO | PTO:.PMM.VirBCurrentInPhaseA_A | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x5340b78f
PTOPMMVirBCurrentInPhaseB_A | REAL | IOD_PTO | PTO:.PMM.VirBCurrentInPhaseB_A | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x5340b790
PTOPMMVirBCurrentInPhaseC_A | REAL | IOD_PTO | PTO:.PMM.VirBCurrentInPhaseC_A | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x5340b791
PTOPMMVirBFrequency_Hz | REAL | IOD_PTO | PTO:.PMM.VirBFrequency_Hz | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x5340b792
PTOPMMVirBPowerFactorSys | REAL | IOD_PTO | PTO:.PMM.VirBPowerFactorSys | 0 | 1 | 0 | 1 |  | ####.# | 6157 | 1 | 0x5340b793
PTOPMMVirBReactiveEnergyConsumed_kVARh | REAL | IOD_PTO | PTO:.PMM.VirBReactiveEnergyConsumed_kVARh |  |  |  |  | kVArh | ####.# | 6157 | 1 | 0x5340b794
PTOPMMVirBReactivePowerPhaseA | REAL | IOD_PTO | PTO:.PMM.VirBReactivePowerPhaseA | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 1 | 0x5340b795
PTOPMMVirBReactivePowerPhaseB | REAL | IOD_PTO | PTO:.PMM.VirBReactivePowerPhaseB | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 1 | 0x5340b796
PTOPMMVirBReactivePowerPhaseC | REAL | IOD_PTO | PTO:.PMM.VirBReactivePowerPhaseC | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 1 | 0x5340b797
PTOPMMVirBTotalActivePower_kW | REAL | IOD_PTO | PTO:.PMM.VirBTotalActivePower_kW | 0 | 300 | 0 | 300 | kW | ####.# | 6157 | 1 | 0x5340b798
PTOPMMVirBTotalAparentPower_kVA | REAL | IOD_PTO | PTO:.PMM.VirBTotalAparentPower_kVA | 0 | 300 | 0 | 300 | kVA | ####.# | 6157 | 1 | 0x5340b799
PTOPMMVirBTotalPowerFactor | REAL | IOD_PTO | PTO:.PMM.VirBTotalPowerFactor | 0 | 1 | 0 | 1 |  | ####.# | 6157 | 1 | 0x5340b79a
PTOPMMVirBTotalReactivePower_kVAR | REAL | IOD_PTO | PTO:.PMM.VirBTotalReactivePower_kVAR | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 1 | 0x5340b79b
PTOPMMVirBVoltageBetweenPhaseAB_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseAB_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 1 | 0x5340b79c
PTOPMMVirBVoltageBetweenPhaseAN_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseAN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 1 | 0x5340b79d
PTOPMMVirBVoltageBetweenPhaseBC_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseBC_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 1 | 0x5340b79e
PTOPMMVirBVoltageBetweenPhaseBN_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseBN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 1 | 0x5340b79f
PTOPMMVirBVoltageBetweenPhaseCA_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseCA_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 1 | 0x5340b7a0
PTOPMMVirBVoltageBetweenPhaseCN_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseCN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 1 | 0x5340b7a1
PTOPMMVoltageBetweenPhaseAB_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseAB_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 1 | 0x5340b7a2
PTOPMMVoltageBetweenPhaseAN_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseAN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 1 | 0x5340b7a3
PTOPMMVoltageBetweenPhaseBC_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseBC_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 1 | 0x5340b7a4
PTOPMMVoltageBetweenPhaseBN_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseBN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 1 | 0x5340b7a5
PTOPMMVoltageBetweenPhaseCA_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseCA_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 1 | 0x5340b7a6
PTOPMMVoltageBetweenPhaseCN_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseCN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 1 | 0x5340b7a7
PTOPMMfaza01 | REAL | IOD_PTO | PTO:.PMMfaza01 | [6 empty] | 6157 | 1 | 0x5340b7a8
PTOPMMfaza02 | REAL | IOD_PTO | PTO:.PMMfaza02 | [6 empty] | 6157 | 1 | 0x5340b7a9
PTOPMMfaza03 | REAL | IOD_PTO | PTO:.PMMfaza03 | [6 empty] | 6157 | 1 | 0x5340b7aa
PTOPMMfaza04 | REAL | IOD_PTO | PTO:.PMMfaza04 | [6 empty] | 6157 | 1 | 0x5340b7ab
PTOPMMfaza05 | REAL | IOD_PTO | PTO:.PMMfaza05 | [6 empty] | 6157 | 1 | 0x5340b7ac
PTOPMMfaza06 | REAL | IOD_PTO | PTO:.PMMfaza06 | [6 empty] | 6157 | 1 | 0x5340b7ad
PTOPMMfaza07 | REAL | IOD_PTO | PTO:.PMMfaza07 | [6 empty] | 6157 | 1 | 0x5340b7ae
PTOPMMfaza08 | REAL | IOD_PTO | PTO:.PMMfaza08 | [6 empty] | 6157 | 1 | 0x5340b7af
PTOPMMfaza09 | REAL | IOD_PTO | PTO:.PMMfaza09 | [6 empty] | 6157 | 1 | 0x5340b7b0
PTOPMMfaza10 | REAL | IOD_PTO | PTO:.PMMfaza10 | [6 empty] | 6157 | 1 | 0x5340b7b1
PTOPMMfaza11 | REAL | IOD_PTO | PTO:.PMMfaza11 | [6 empty] | 6157 | 1 | 0x5340b7b2
PTOPMMfaza12 | REAL | IOD_PTO | PTO:.PMMfaza12 | [6 empty] | 6157 | 1 | 0x5340b7b3
PTOPMMfaza13 | REAL | IOD_PTO | PTO:.PMMfaza13 | [6 empty] | 6157 | 1 | 0x5340b7b4
PTOPMMfaza14 | REAL | IOD_PTO | PTO:.PMMfaza14 | [6 empty] | 6157 | 1 | 0x5340b7b5
PTOPMMfaza15 | REAL | IOD_PTO | PTO:.PMMfaza15 | [6 empty] | 6157 | 1 | 0x5340b7b6
PTOPMMfaza16 | REAL | IOD_PTO | PTO:.PMMfaza16 | [6 empty] | 6157 | 1 | 0x5340b7b7
PTOPMMfaza17 | REAL | IOD_PTO | PTO:.PMMfaza17 | [6 empty] | 6157 | 1 | 0x5340b7b8
PTOPMMfaza18 | REAL | IOD_PTO | PTO:.PMMfaza18 | [6 empty] | 6157 | 1 | 0x5340b7b9
PTOPMMfaza19 | REAL | IOD_PTO | PTO:.PMMfaza19 | [6 empty] | 6157 | 1 | 0x5340b7ba
PTOPMMfaza20 | REAL | IOD_PTO | PTO:.PMMfaza20 | [6 empty] | 6157 | 1 | 0x5340b7bb
PTOPMMfaza21 | REAL | IOD_PTO | PTO:.PMMfaza21 | [6 empty] | 6157 | 1 | 0x5340b7bc
PTOPMMfaza22 | REAL | IOD_PTO | PTO:.PMMfaza22 | [6 empty] | 6157 | 1 | 0x5340b7bd
PTOPMMfaza23 | REAL | IOD_PTO | PTO:.PMMfaza23 | [6 empty] | 6157 | 1 | 0x5340b7be
PTOPMMfaza24 | REAL | IOD_PTO | PTO:.PMMfaza24 | [6 empty] | 6157 | 1 | 0x5340b7bf
PTOPMMfaza25 | REAL | IOD_PTO | PTO:.PMMfaza25 | [6 empty] | 6157 | 1 | 0x5340b7c0
PTOPMMfaza26 | REAL | IOD_PTO | PTO:.PMMfaza26 | [6 empty] | 6157 | 1 | 0x5340b7c1
PTOPMMfaza27 | REAL | IOD_PTO | PTO:.PMMfaza27 | [6 empty] | 6157 | 1 | 0x5340b7c2
PTOPMMfaza28 | REAL | IOD_PTO | PTO:.PMMfaza28 | [6 empty] | 6157 | 1 | 0x5340b7c3
PTOPMMfaza29 | REAL | IOD_PTO | PTO:.PMMfaza29 | [6 empty] | 6157 | 1 | 0x5340b7c4
PTOPMMfaza30 | REAL | IOD_PTO | PTO:.PMMfaza30 | [6 empty] | 6157 | 1 | 0x5340b7c5
PTOPMMfaza31 | REAL | IOD_PTO | PTO:.PMMfaza31 | [6 empty] | 6157 | 1 | 0x5340b7c6
PTOPMMfaza32 | REAL | IOD_PTO | PTO:.PMMfaza32 | [6 empty] | 6157 | 1 | 0x5340b7c7
PTOPMMfaza33 | REAL | IOD_PTO | PTO:.PMMfaza33 | [6 empty] | 6157 | 1 | 0x5340b7c8
PTOPMMfaza34 | REAL | IOD_PTO | PTO:.PMMfaza34 | [6 empty] | 6157 | 1 | 0x5340b7c9
PTOPMMfaza35 | REAL | IOD_PTO | PTO:.PMMfaza35 | [6 empty] | 6157 | 1 | 0x5340b7ca
PTOPMMfaza36 | REAL | IOD_PTO | PTO:.PMMfaza36 | [6 empty] | 6157 | 1 | 0x5340b7cb
PTOPMMfaza37 | REAL | IOD_PTO | PTO:.PMMfaza37 | [6 empty] | 6157 | 1 | 0x5340b7cc
PTOPMMfaza38 | REAL | IOD_PTO | PTO:.PMMfaza38 | [6 empty] | 6157 | 1 | 0x5340b7cd
PTOPMMfaza39 | REAL | IOD_PTO | PTO:.PMMfaza39 | [6 empty] | 6157 | 1 | 0x5340b7ce
PTOPMMfaza40 | REAL | IOD_PTO | PTO:.PMMfaza40 | [6 empty] | 6157 | 1 | 0x5340b7cf
PTOPMMfaza41 | REAL | IOD_PTO | PTO:.PMMfaza41 | [6 empty] | 6157 | 1 | 0x5340b7d0
PTOPMMfaza42 | REAL | IOD_PTO | PTO:.PMMfaza42 | [6 empty] | 6157 | 1 | 0x5340b7d1
PTOPMMfaza6010 | REAL | IOD_PTO | PTO:.PMMfaza60[10] | [6 empty] | 6157 | 1 | 0x5340b7d2
PTOPMMfaza6011 | REAL | IOD_PTO | PTO:.PMMfaza60[11] | [6 empty] | 6157 | 1 | 0x5340b7d3
PTOPMMfaza6012 | REAL | IOD_PTO | PTO:.PMMfaza60[12] | [6 empty] | 6157 | 1 | 0x5340b7d4
PTOPMMfaza6013 | REAL | IOD_PTO | PTO:.PMMfaza60[13] | [6 empty] | 6157 | 1 | 0x5340b7d5
PTOPMMfaza6014 | REAL | IOD_PTO | PTO:.PMMfaza60[14] | [6 empty] | 6157 | 1 | 0x5340b7d6
PTOPMMfaza6015 | REAL | IOD_PTO | PTO:.PMMfaza60[15] | [6 empty] | 6157 | 1 | 0x5340b7d7
PTOPMMfaza6016 | REAL | IOD_PTO | PTO:.PMMfaza60[16] | [6 empty] | 6157 | 1 | 0x5340b7d8
PTOPMMfaza6017 | REAL | IOD_PTO | PTO:.PMMfaza60[17] | [6 empty] | 6157 | 1 | 0x5340b7d9
PTOPMMfaza6018 | REAL | IOD_PTO | PTO:.PMMfaza60[18] | [6 empty] | 6157 | 1 | 0x5340b7da
PTOPMMfaza6019 | REAL | IOD_PTO | PTO:.PMMfaza60[19] | [6 empty] | 6157 | 1 | 0x5340b7db
PTOPMMfaza601 | REAL | IOD_PTO | PTO:.PMMfaza60[1] | [6 empty] | 6157 | 1 | 0x5340b7dc
PTOPMMfaza6020 | REAL | IOD_PTO | PTO:.PMMfaza60[20] | [6 empty] | 6157 | 1 | 0x5340b7dd
PTOPMMfaza6021 | REAL | IOD_PTO | PTO:.PMMfaza60[21] | [6 empty] | 6157 | 1 | 0x5340b7de
PTOPMMfaza6022 | REAL | IOD_PTO | PTO:.PMMfaza60[22] | [6 empty] | 6157 | 1 | 0x5340b7df
PTOPMMfaza6023 | REAL | IOD_PTO | PTO:.PMMfaza60[23] | [6 empty] | 6157 | 1 | 0x5340b7e0
PTOPMMfaza6024 | REAL | IOD_PTO | PTO:.PMMfaza60[24] | [6 empty] | 6157 | 1 | 0x5340b7e1
PTOPMMfaza6025 | REAL | IOD_PTO | PTO:.PMMfaza60[25] | [6 empty] | 6157 | 1 | 0x5340b7e2
PTOPMMfaza6026 | REAL | IOD_PTO | PTO:.PMMfaza60[26] | [6 empty] | 6157 | 1 | 0x5340b7e3
PTOPMMfaza6027 | REAL | IOD_PTO | PTO:.PMMfaza60[27] | [6 empty] | 6157 | 1 | 0x5340b7e4
PTOPMMfaza6028 | REAL | IOD_PTO | PTO:.PMMfaza60[28] | [6 empty] | 6157 | 1 | 0x5340b7e5
PTOPMMfaza6029 | REAL | IOD_PTO | PTO:.PMMfaza60[29] | [6 empty] | 6157 | 1 | 0x5340b7e6
PTOPMMfaza602 | REAL | IOD_PTO | PTO:.PMMfaza60[2] | [6 empty] | 6157 | 1 | 0x5340b7e7
PTOPMMfaza6030 | REAL | IOD_PTO | PTO:.PMMfaza60[30] | [6 empty] | 6157 | 1 | 0x5340b7e8
PTOPMMfaza6031 | REAL | IOD_PTO | PTO:.PMMfaza60[31] | [6 empty] | 6157 | 1 | 0x5340b7e9
PTOPMMfaza6032 | REAL | IOD_PTO | PTO:.PMMfaza60[32] | [6 empty] | 6157 | 1 | 0x5340b7ea
PTOPMMfaza6033 | REAL | IOD_PTO | PTO:.PMMfaza60[33] | [6 empty] | 6157 | 1 | 0x5340b7eb
PTOPMMfaza6034 | REAL | IOD_PTO | PTO:.PMMfaza60[34] | [6 empty] | 6157 | 1 | 0x5340b7ec
PTOPMMfaza6035 | REAL | IOD_PTO | PTO:.PMMfaza60[35] | [6 empty] | 6157 | 1 | 0x5340b7ed
PTOPMMfaza6036 | REAL | IOD_PTO | PTO:.PMMfaza60[36] | [6 empty] | 6157 | 1 | 0x5340b7ee
PTOPMMfaza6037 | REAL | IOD_PTO | PTO:.PMMfaza60[37] | [6 empty] | 6157 | 1 | 0x5340b7ef
PTOPMMfaza6038 | REAL | IOD_PTO | PTO:.PMMfaza60[38] | [6 empty] | 6157 | 1 | 0x5340b7f0
PTOPMMfaza6039 | REAL | IOD_PTO | PTO:.PMMfaza60[39] | [6 empty] | 6157 | 1 | 0x5340b7f1
PTOPMMfaza603 | REAL | IOD_PTO | PTO:.PMMfaza60[3] | [6 empty] | 6157 | 1 | 0x5340b7f2
PTOPMMfaza6040 | REAL | IOD_PTO | PTO:.PMMfaza60[40] | [6 empty] | 6157 | 1 | 0x5340b7f3
PTOPMMfaza6041 | REAL | IOD_PTO | PTO:.PMMfaza60[41] | [6 empty] | 6157 | 1 | 0x5340b7f4
PTOPMMfaza6042 | REAL | IOD_PTO | PTO:.PMMfaza60[42] | [6 empty] | 6157 | 1 | 0x5340b7f5
PTOPMMfaza604 | REAL | IOD_PTO | PTO:.PMMfaza60[4] | [6 empty] | 6157 | 1 | 0x5340b7f6
PTOPMMfaza605 | REAL | IOD_PTO | PTO:.PMMfaza60[5] | [6 empty] | 6157 | 1 | 0x5340b7f7
PTOPMMfaza606 | REAL | IOD_PTO | PTO:.PMMfaza60[6] | [6 empty] | 6157 | 1 | 0x5340b7f8
PTOPMMfaza607 | REAL | IOD_PTO | PTO:.PMMfaza60[7] | [6 empty] | 6157 | 1 | 0x5340b7f9
PTOPMMfaza608 | REAL | IOD_PTO | PTO:.PMMfaza60[8] | [6 empty] | 6157 | 1 | 0x5340b7fa
PTOPMMfaza609 | REAL | IOD_PTO | PTO:.PMMfaza60[9] | [6 empty] | 6157 | 1 | 0x5340b7fb
PTOPMMfaza8010 | REAL | IOD_PTO | PTO:.PMMfaza80[10] | [6 empty] | 6157 | 1 | 0x5340b7fc
PTOPMMfaza8011 | REAL | IOD_PTO | PTO:.PMMfaza80[11] | [6 empty] | 6157 | 1 | 0x5340b7fd
PTOPMMfaza8012 | REAL | IOD_PTO | PTO:.PMMfaza80[12] | [6 empty] | 6157 | 1 | 0x5340b7fe
PTOPMMfaza8013 | REAL | IOD_PTO | PTO:.PMMfaza80[13] | [6 empty] | 6157 | 1 | 0x5340b7ff
PTOPMMfaza8014 | REAL | IOD_PTO | PTO:.PMMfaza80[14] | [6 empty] | 6157 | 1 | 0x5340b800
PTOPMMfaza8015 | REAL | IOD_PTO | PTO:.PMMfaza80[15] | [6 empty] | 6157 | 1 | 0x5340b801
PTOPMMfaza8016 | REAL | IOD_PTO | PTO:.PMMfaza80[16] | [6 empty] | 6157 | 1 | 0x5340b802
PTOPMMfaza8017 | REAL | IOD_PTO | PTO:.PMMfaza80[17] | [6 empty] | 6157 | 1 | 0x5340b803
PTOPMMfaza8018 | REAL | IOD_PTO | PTO:.PMMfaza80[18] | [6 empty] | 6157 | 1 | 0x5340b804
PTOPMMfaza8019 | REAL | IOD_PTO | PTO:.PMMfaza80[19] | [6 empty] | 6157 | 1 | 0x5340b805
PTOPMMfaza801 | REAL | IOD_PTO | PTO:.PMMfaza80[1] | [6 empty] | 6157 | 1 | 0x5340b806
PTOPMMfaza8020 | REAL | IOD_PTO | PTO:.PMMfaza80[20] | [6 empty] | 6157 | 1 | 0x5340b807
PTOPMMfaza8021 | REAL | IOD_PTO | PTO:.PMMfaza80[21] | [6 empty] | 6157 | 1 | 0x5340b808
PTOPMMfaza8022 | REAL | IOD_PTO | PTO:.PMMfaza80[22] | [6 empty] | 6157 | 1 | 0x5340b809
PTOPMMfaza8023 | REAL | IOD_PTO | PTO:.PMMfaza80[23] | [6 empty] | 6157 | 1 | 0x5340b80a
PTOPMMfaza8024 | REAL | IOD_PTO | PTO:.PMMfaza80[24] | [6 empty] | 6157 | 1 | 0x5340b80b
PTOPMMfaza8025 | REAL | IOD_PTO | PTO:.PMMfaza80[25] | [6 empty] | 6157 | 1 | 0x5340b80c
PTOPMMfaza8026 | REAL | IOD_PTO | PTO:.PMMfaza80[26] | [6 empty] | 6157 | 1 | 0x5340b80d
PTOPMMfaza8027 | REAL | IOD_PTO | PTO:.PMMfaza80[27] | [6 empty] | 6157 | 1 | 0x5340b80e
PTOPMMfaza8028 | REAL | IOD_PTO | PTO:.PMMfaza80[28] | [6 empty] | 6157 | 1 | 0x5340b80f
PTOPMMfaza8029 | REAL | IOD_PTO | PTO:.PMMfaza80[29] | [6 empty] | 6157 | 1 | 0x5340b810
PTOPMMfaza802 | REAL | IOD_PTO | PTO:.PMMfaza80[2] | [6 empty] | 6157 | 1 | 0x5340b811
PTOPMMfaza8030 | REAL | IOD_PTO | PTO:.PMMfaza80[30] | [6 empty] | 6157 | 1 | 0x5340b812
PTOPMMfaza8031 | REAL | IOD_PTO | PTO:.PMMfaza80[31] | [6 empty] | 6157 | 1 | 0x5340b813
PTOPMMfaza8032 | REAL | IOD_PTO | PTO:.PMMfaza80[32] | [6 empty] | 6157 | 1 | 0x5340b814
PTOPMMfaza8033 | REAL | IOD_PTO | PTO:.PMMfaza80[33] | [6 empty] | 6157 | 1 | 0x5340b815
PTOPMMfaza8034 | REAL | IOD_PTO | PTO:.PMMfaza80[34] | [6 empty] | 6157 | 1 | 0x5340b816
PTOPMMfaza8035 | REAL | IOD_PTO | PTO:.PMMfaza80[35] | [6 empty] | 6157 | 1 | 0x5340b817
PTOPMMfaza8036 | REAL | IOD_PTO | PTO:.PMMfaza80[36] | [6 empty] | 6157 | 1 | 0x5340b818
PTOPMMfaza8037 | REAL | IOD_PTO | PTO:.PMMfaza80[37] | [6 empty] | 6157 | 1 | 0x5340b819
PTOPMMfaza8038 | REAL | IOD_PTO | PTO:.PMMfaza80[38] | [6 empty] | 6157 | 1 | 0x5340b81a
PTOPMMfaza8039 | REAL | IOD_PTO | PTO:.PMMfaza80[39] | [6 empty] | 6157 | 1 | 0x5340b81b
PTOPMMfaza803 | REAL | IOD_PTO | PTO:.PMMfaza80[3] | [6 empty] | 6157 | 1 | 0x5340b81c
PTOPMMfaza8040 | REAL | IOD_PTO | PTO:.PMMfaza80[40] | [6 empty] | 6157 | 1 | 0x5340b81d
PTOPMMfaza8041 | REAL | IOD_PTO | PTO:.PMMfaza80[41] | [6 empty] | 6157 | 1 | 0x5340b81e
PTOPMMfaza8042 | REAL | IOD_PTO | PTO:.PMMfaza80[42] | [6 empty] | 6157 | 1 | 0x5340b81f
PTOPMMfaza804 | REAL | IOD_PTO | PTO:.PMMfaza80[4] | [6 empty] | 6157 | 1 | 0x5340b820
PTOPMMfaza805 | REAL | IOD_PTO | PTO:.PMMfaza80[5] | [6 empty] | 6157 | 1 | 0x5340b821
PTOPMMfaza806 | REAL | IOD_PTO | PTO:.PMMfaza80[6] | [6 empty] | 6157 | 1 | 0x5340b822
PTOPMMfaza807 | REAL | IOD_PTO | PTO:.PMMfaza80[7] | [6 empty] | 6157 | 1 | 0x5340b823
PTOPMMfaza808 | REAL | IOD_PTO | PTO:.PMMfaza80[8] | [6 empty] | 6157 | 1 | 0x5340b824
PTOPMMfaza809 | REAL | IOD_PTO | PTO:.PMMfaza80[9] | [6 empty] | 6157 | 1 | 0x5340b825
PTOPMMOverCurrentBetw1 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentBetw[1] | [6 empty] | 6157 | 1 | 0x5340b830
PTOPMMOverCurrentBetw2 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentBetw[2] | [6 empty] | 6157 | 1 | 0x5340b840
PTOPMMOverCurrentBetw3 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentBetw[3] | [6 empty] | 6157 | 1 | 0x5340b850
PTOPMMOverCurrentOver1 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentOver[1] | [6 empty] | 6157 | 1 | 0x5340b860
PTOPMMOverCurrentOver2 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentOver[2] | [6 empty] | 6157 | 1 | 0x5340b870
PTOPMMOverCurrentOver3 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentOver[3] | [6 empty] | 6157 | 1 | 0x5340b880
PTOQstanje10 | BYTE | IOD_PTO | PTO:.Qstanje[10] | [6 empty] | 6157 | 1 | 0x5340b890
PTOQstanje11 | BYTE | IOD_PTO | PTO:.Qstanje[11] | [6 empty] | 6157 | 1 | 0x5340b891
PTOQstanje12 | BYTE | IOD_PTO | PTO:.Qstanje[12] | [6 empty] | 6157 | 1 | 0x5340b892
PTOQstanje13 | BYTE | IOD_PTO | PTO:.Qstanje[13] | [6 empty] | 6157 | 1 | 0x5340b893
PTOQstanje14 | BYTE | IOD_PTO | PTO:.Qstanje[14] | [6 empty] | 6157 | 1 | 0x5340b894
PTOQstanje15 | BYTE | IOD_PTO | PTO:.Qstanje[15] | [6 empty] | 6157 | 1 | 0x5340b895
PTOQstanje16 | BYTE | IOD_PTO | PTO:.Qstanje[16] | [6 empty] | 6157 | 1 | 0x5340b896
PTOQstanje17 | BYTE | IOD_PTO | PTO:.Qstanje[17] | [6 empty] | 6157 | 1 | 0x5340b897
PTOQstanje18 | BYTE | IOD_PTO | PTO:.Qstanje[18] | [6 empty] | 6157 | 1 | 0x5340b898
PTOQstanje19 | BYTE | IOD_PTO | PTO:.Qstanje[19] | [6 empty] | 6157 | 1 | 0x5340b899
PTOQstanje1 | BYTE | IOD_PTO | PTO:.Qstanje[1] | [6 empty] | 6157 | 1 | 0x5340b89a
PTOQstanje20 | BYTE | IOD_PTO | PTO:.Qstanje[20] | [6 empty] | 6157 | 1 | 0x5340b89b
PTOQstanje21 | BYTE | IOD_PTO | PTO:.Qstanje[21] | [6 empty] | 6157 | 1 | 0x5340b89c
PTOQstanje22 | BYTE | IOD_PTO | PTO:.Qstanje[22] | [6 empty] | 6157 | 1 | 0x5340b89d
PTOQstanje23 | BYTE | IOD_PTO | PTO:.Qstanje[23] | [6 empty] | 6157 | 1 | 0x5340b89e
PTOQstanje24 | BYTE | IOD_PTO | PTO:.Qstanje[24] | [6 empty] | 6157 | 1 | 0x5340b89f
PTOQstanje25 | BYTE | IOD_PTO | PTO:.Qstanje[25] | [6 empty] | 6157 | 1 | 0x5340b8a0
PTOQstanje26 | BYTE | IOD_PTO | PTO:.Qstanje[26] | [6 empty] | 6157 | 1 | 0x5340b8a1
PTOQstanje27 | BYTE | IOD_PTO | PTO:.Qstanje[27] | [6 empty] | 6157 | 1 | 0x5340b8a2
PTOQstanje28 | BYTE | IOD_PTO | PTO:.Qstanje[28] | [6 empty] | 6157 | 1 | 0x5340b8a3
PTOQstanje29 | BYTE | IOD_PTO | PTO:.Qstanje[29] | [6 empty] | 6157 | 1 | 0x5340b8a4
PTOQstanje2 | BYTE | IOD_PTO | PTO:.Qstanje[2] | [6 empty] | 6157 | 1 | 0x5340b8a5
PTOQstanje30 | BYTE | IOD_PTO | PTO:.Qstanje[30] | [6 empty] | 6157 | 1 | 0x5340b8a6
PTOQstanje31 | BYTE | IOD_PTO | PTO:.Qstanje[31] | [6 empty] | 6157 | 1 | 0x5340b8a7
PTOQstanje32 | BYTE | IOD_PTO | PTO:.Qstanje[32] | [6 empty] | 6157 | 1 | 0x5340b8a8
PTOQstanje33 | BYTE | IOD_PTO | PTO:.Qstanje[33] | [6 empty] | 6157 | 1 | 0x5340b8a9
PTOQstanje34 | BYTE | IOD_PTO | PTO:.Qstanje[34] | [6 empty] | 6157 | 1 | 0x5340b8aa
PTOQstanje35 | BYTE | IOD_PTO | PTO:.Qstanje[35] | [6 empty] | 6157 | 1 | 0x5340b8ab
PTOQstanje3 | BYTE | IOD_PTO | PTO:.Qstanje[3] | [6 empty] | 6157 | 1 | 0x5340b8ac
PTOQstanje4 | BYTE | IOD_PTO | PTO:.Qstanje[4] | [6 empty] | 6157 | 1 | 0x5340b8ad
PTOQstanje5 | BYTE | IOD_PTO | PTO:.Qstanje[5] | [6 empty] | 6157 | 1 | 0x5340b8ae
PTOQstanje6 | BYTE | IOD_PTO | PTO:.Qstanje[6] | [6 empty] | 6157 | 1 | 0x5340b8af
PTOQstanje7 | BYTE | IOD_PTO | PTO:.Qstanje[7] | [6 empty] | 6157 | 1 | 0x5340b8b0
PTOQstanje8 | BYTE | IOD_PTO | PTO:.Qstanje[8] | [6 empty] | 6157 | 1 | 0x5340b8b1
PTOQstanje9 | BYTE | IOD_PTO | PTO:.Qstanje[9] | [6 empty] | 6157 | 1 | 0x5340b8b2
PTOSenzorTemp1 | REAL | IOD_PTO | PTO:.SenzorTemp[1] | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5340b8b3
PTOSenzorTemp2 | REAL | IOD_PTO | PTO:.SenzorTemp[2] | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5340b8b4
PTOSenzorTemp3 | REAL | IOD_PTO | PTO:.SenzorTemp[3] | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5340b8b5
PTOSenzorTemp4 | REAL | IOD_PTO | PTO:.SenzorTemp[4] | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5340b8b6
PTOSenzorTemp5 | REAL | IOD_PTO | PTO:.SenzorTemp[5] | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5340b8b7
PTOSenzorTemp6 | REAL | IOD_PTO | PTO:.SenzorTemp[6] | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5340b8b8
PTOSenzorVlaga1 | REAL | IOD_PTO | PTO:.SenzorVlaga[1] | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x5340b8b9
PTOSenzorVlaga2 | REAL | IOD_PTO | PTO:.SenzorVlaga[2] | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x5340b8ba
PTOSenzorVlaga3 | REAL | IOD_PTO | PTO:.SenzorVlaga[3] | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x5340b8bb
PTOSenzorVlaga4 | REAL | IOD_PTO | PTO:.SenzorVlaga[4] | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x5340b8bc
PTOSenzorVlaga5 | REAL | IOD_PTO | PTO:.SenzorVlaga[5] | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x5340b8bd
PTOSenzorVlaga6 | REAL | IOD_PTO | PTO:.SenzorVlaga[6] | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x5340b8be
PTOSetDateTime | DIGITAL | IOD_PTO | PTO:.SetDateTime | [6 empty] | 6157 | 1 | 0x5340b8c0
PTOSetDateTimeDemand | DIGITAL | IOD_PTO | PTO:.SetDateTimeDemand | [6 empty] | 6157 | 1 | 0x5340b8d0
PTOSetDateTimeError | DIGITAL | IOD_PTO | PTO:.SetDateTimeError | [6 empty] | 6157 | 1 | 0x5340b8e0
PTOSetDateTimeFinished | DIGITAL | IOD_PTO | PTO:.SetDateTimeFinished | [6 empty] | 6157 | 1 | 0x5340b8f0
PTOSetRemoteOnOff1 | DIGITAL | IOD_PTO | PTO:.SetRemoteOnOff[1] | [6 empty] | 6157 | 1 | 0x5340b900
PTOSetRemoteOnOff2 | DIGITAL | IOD_PTO | PTO:.SetRemoteOnOff[2] | [6 empty] | 6157 | 1 | 0x5340b910
PTOSlabaBaterijaPLC_A1 | DIGITAL | IOD_PTO | PTO:.SlabaBaterijaPLC_A1 | [6 empty] | 6157 | 1 | 0x5340b920
PTOTempAlarmPoint0 | REAL | IOD_PTO | PTO:.TempAlarmPoint[0] | [6 empty] | 6157 | 1 | 0x5340b938
PTOTempAlarmPoint1 | REAL | IOD_PTO | PTO:.TempAlarmPoint[1] | [6 empty] | 6157 | 1 | 0x5340b939
PTOTempAlarmPoint2 | REAL | IOD_PTO | PTO:.TempAlarmPoint[2] | [6 empty] | 6157 | 1 | 0x5340b93a
PTOTempAlarmPoint3 | REAL | IOD_PTO | PTO:.TempAlarmPoint[3] | [6 empty] | 6157 | 1 | 0x5340b93b
PTOTempMaxPoint0 | REAL | IOD_PTO | PTO:.TempMaxPoint[0] | [6 empty] | 6157 | 1 | 0x5340b93c
PTOTempMaxPoint1 | REAL | IOD_PTO | PTO:.TempMaxPoint[1] | [6 empty] | 6157 | 1 | 0x5340b93d
PTOTempMaxPoint2 | REAL | IOD_PTO | PTO:.TempMaxPoint[2] | [6 empty] | 6157 | 1 | 0x5340b93e
PTOTempMaxPoint3 | REAL | IOD_PTO | PTO:.TempMaxPoint[3] | [6 empty] | 6157 | 1 | 0x5340b93f
PTOTempPovp0 | REAL | IOD_PTO | PTO:.TempPovp[0] | [6 empty] | 6157 | 1 | 0x5340b940
PTOTempPovp1 | REAL | IOD_PTO | PTO:.TempPovp[1] | [6 empty] | 6157 | 1 | 0x5340b941
PTOTempPovp2 | REAL | IOD_PTO | PTO:.TempPovp[2] | [6 empty] | 6157 | 1 | 0x5340b942
PTOTempPovp3 | REAL | IOD_PTO | PTO:.TempPovp[3] | [6 empty] | 6157 | 1 | 0x5340b943
PTOTempSetPoint0 | REAL | IOD_PTO | PTO:.TempSetPoint[0] | [6 empty] | 6157 | 1 | 0x5340b944
PTOTempSetPoint1 | REAL | IOD_PTO | PTO:.TempSetPoint[1] | [6 empty] | 6157 | 1 | 0x5340b945
PTOTempSetPoint2 | REAL | IOD_PTO | PTO:.TempSetPoint[2] | [6 empty] | 6157 | 1 | 0x5340b946
PTOTempSetPoint3 | REAL | IOD_PTO | PTO:.TempSetPoint[3] | [6 empty] | 6157 | 1 | 0x5340b947
PTOTempTSprevisoka1 | DIGITAL | IOD_PTO | PTO:.TempTSprevisoka[1] | [6 empty] | 6157 | 1 | 0x5340b950
PTOTempTSprevisoka2 | DIGITAL | IOD_PTO | PTO:.TempTSprevisoka[2] | [6 empty] | 6157 | 1 | 0x5340b960
PTOTempTSprevisoka3 | DIGITAL | IOD_PTO | PTO:.TempTSprevisoka[3] | [6 empty] | 6157 | 1 | 0x5340b970
PTOTempTSprevisokaSum | DIGITAL | IOD_PTO | PTO:.TempTSprevisokaSum | [6 empty] | 6157 | 1 | 0x5340b980
PTOUPS1Errors10 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[10] | [6 empty] | 6157 | 1 | 0x5340b990
PTOUPS1Errors11 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[11] | [6 empty] | 6157 | 1 | 0x5340b9a0
PTOUPS1Errors12 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[12] | [6 empty] | 6157 | 1 | 0x5340b9b0
PTOUPS1Errors13 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[13] | [6 empty] | 6157 | 1 | 0x5340b9c0
PTOUPS1Errors14 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[14] | [6 empty] | 6157 | 1 | 0x5340b9d0
PTOUPS1Errors15 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[15] | [6 empty] | 6157 | 1 | 0x5340b9e0
PTOUPS1Errors16 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[16] | [6 empty] | 6157 | 1 | 0x5340b9f0
PTOUPS1Errors17 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[17] | [6 empty] | 6157 | 1 | 0x5340ba00
PTOUPS1Errors18 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[18] | [6 empty] | 6157 | 1 | 0x5340ba10
PTOUPS1Errors19 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[19] | [6 empty] | 6157 | 1 | 0x5340ba20
PTOUPS1Errors1 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[1] | [6 empty] | 6157 | 1 | 0x5340ba30
PTOUPS1Errors20 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[20] | [6 empty] | 6157 | 1 | 0x5340ba40
PTOUPS1Errors21 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[21] | [6 empty] | 6157 | 1 | 0x5340ba50
PTOUPS1Errors22 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[22] | [6 empty] | 6157 | 1 | 0x5340ba60
PTOUPS1Errors23 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[23] | [6 empty] | 6157 | 1 | 0x5340ba70
PTOUPS1Errors24 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[24] | [6 empty] | 6157 | 1 | 0x5340ba80
PTOUPS1Errors25 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[25] | [6 empty] | 6157 | 1 | 0x5340ba90
PTOUPS1Errors2 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[2] | [6 empty] | 6157 | 1 | 0x5340baa0
PTOUPS1Errors3 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[3] | [6 empty] | 6157 | 1 | 0x5340bab0
PTOUPS1Errors4 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[4] | [6 empty] | 6157 | 1 | 0x5340bac0
PTOUPS1Errors5 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[5] | [6 empty] | 6157 | 1 | 0x5340bad0
PTOUPS1Errors6 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[6] | [6 empty] | 6157 | 1 | 0x5340bae0
PTOUPS1Errors7 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[7] | [6 empty] | 6157 | 1 | 0x5340baf0
PTOUPS1Errors8 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[8] | [6 empty] | 6157 | 1 | 0x5340bb00
PTOUPS1Errors9 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[9] | [6 empty] | 6157 | 1 | 0x5340bb10
PTOUPS2Errors10 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[10] | [6 empty] | 6157 | 1 | 0x5340bb20
PTOUPS2Errors11 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[11] | [6 empty] | 6157 | 1 | 0x5340bb30
PTOUPS2Errors12 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[12] | [6 empty] | 6157 | 1 | 0x5340bb40
PTOUPS2Errors13 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[13] | [6 empty] | 6157 | 1 | 0x5340bb50
PTOUPS2Errors14 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[14] | [6 empty] | 6157 | 1 | 0x5340bb60
PTOUPS2Errors15 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[15] | [6 empty] | 6157 | 1 | 0x5340bb70
PTOUPS2Errors16 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[16] | [6 empty] | 6157 | 1 | 0x5340bb80
PTOUPS2Errors17 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[17] | [6 empty] | 6157 | 1 | 0x5340bb90
PTOUPS2Errors18 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[18] | [6 empty] | 6157 | 1 | 0x5340bba0
PTOUPS2Errors19 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[19] | [6 empty] | 6157 | 1 | 0x5340bbb0
PTOUPS2Errors1 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[1] | [6 empty] | 6157 | 1 | 0x5340bbc0
PTOUPS2Errors20 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[20] | [6 empty] | 6157 | 1 | 0x5340bbd0
PTOUPS2Errors21 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[21] | [6 empty] | 6157 | 1 | 0x5340bbe0
PTOUPS2Errors22 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[22] | [6 empty] | 6157 | 1 | 0x5340bbf0
PTOUPS2Errors23 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[23] | [6 empty] | 6157 | 1 | 0x5340bc00
PTOUPS2Errors24 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[24] | [6 empty] | 6157 | 1 | 0x5340bc10
PTOUPS2Errors25 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[25] | [6 empty] | 6157 | 1 | 0x5340bc20
PTOUPS2Errors2 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[2] | [6 empty] | 6157 | 1 | 0x5340bc30
PTOUPS2Errors3 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[3] | [6 empty] | 6157 | 1 | 0x5340bc40
PTOUPS2Errors4 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[4] | [6 empty] | 6157 | 1 | 0x5340bc50
PTOUPS2Errors5 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[5] | [6 empty] | 6157 | 1 | 0x5340bc60
PTOUPS2Errors6 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[6] | [6 empty] | 6157 | 1 | 0x5340bc70
PTOUPS2Errors7 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[7] | [6 empty] | 6157 | 1 | 0x5340bc80
PTOUPS2Errors8 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[8] | [6 empty] | 6157 | 1 | 0x5340bc90
PTOUPS2Errors9 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[9] | [6 empty] | 6157 | 1 | 0x5340bca0
PTOUPS1AlarmAwaitingPower | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmAwaitingPower | [6 empty] | 6157 | 1 | 0x5340bcb0
PTOUPS1AlarmBypassBad | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmBypassBad | [6 empty] | 6157 | 1 | 0x5340bcc0
PTOUPS1AlarmChargerFailed | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmChargerFailed | [6 empty] | 6157 | 1 | 0x5340bcd0
PTOUPS1AlarmCommunicationsLost | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmCommunicationsLost | [6 empty] | 6157 | 1 | 0x5340bce0
PTOUPS1AlarmDepletedBattery | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmDepletedBattery | [6 empty] | 6157 | 1 | 0x5340bcf0
PTOUPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmDiagnosticTestFailed | [6 empty] | 6157 | 1 | 0x5340bd00
PTOUPS1AlarmInverterError | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmInverterError | [6 empty] | 6157 | 1 | 0x5340bd10
PTOUPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmIzhodOffKotZahtevano | [6 empty] | 6157 | 1 | 0x5340bd20
PTOUPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmIzhodPreobremenjen | [6 empty] | 6157 | 1 | 0x5340bd30
PTOUPS1AlarmLowBattery | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmLowBattery | [6 empty] | 6157 | 1 | 0x5340bd40
PTOUPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmNapakaNaVarovalki | [6 empty] | 6157 | 1 | 0x5340bd50
PTOUPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmNapakaNaVentilatorju | [6 empty] | 6157 | 1 | 0x5340bd60
PTOUPS1AlarmOnBattery | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmOnBattery | [6 empty] | 6157 | 1 | 0x5340bd70
PTOUPS1AlarmOnBypass | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmOnBypass | [6 empty] | 6157 | 1 | 0x5340bd80
PTOUPS1AlarmShutdownImminent | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmShutdownImminent | [6 empty] | 6157 | 1 | 0x5340bd90
PTOUPS1AlarmShutdownPending | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmShutdownPending | [6 empty] | 6157 | 1 | 0x5340bda0
PTOUPS1AlarmSlabaBaterija | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmSlabaBaterija | [6 empty] | 6157 | 1 | 0x5340bdb0
PTOUPS1AlarmSplosnaNapaka | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmSplosnaNapaka | [6 empty] | 6157 | 1 | 0x5340bdc0
PTOUPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmStanjeIzhodaIzvenToleranc | [6 empty] | 6157 | 1 | 0x5340bdd0
PTOUPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmStanjeVhodaIzvenToleranc | [6 empty] | 6157 | 1 | 0x5340bde0
PTOUPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmTemperaturaIzvenToleranc | [6 empty] | 6157 | 1 | 0x5340bdf0
PTOUPS1AlarmTestInProgres | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmTestInProgres | [6 empty] | 6157 | 1 | 0x5340be00
PTOUPS1AlarmUPSIzhodOff | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmUPSIzhodOff | [6 empty] | 6157 | 1 | 0x5340be10
PTOUPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmUPSOffKotZahtevano | [6 empty] | 6157 | 1 | 0x5340be20
PTOUPS1AlarmUPSSystemOff | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmUPSSystemOff | [6 empty] | 6157 | 1 | 0x5340be30
PTOUPS1EstimatedChargeRemaining | REAL | IOD_PTO | PTO:.UPS[1].EstimatedChargeRemaining | 0 | 100 | 0 | 100 | % | #### | 6157 | 1 | 0x5340be40
PTOUPS1EstimatedMinutesRemaining | REAL | IOD_PTO | PTO:.UPS[1].EstimatedMinutesRemaining | 0 | 1000 | 0 | 100 | min | #### | 6157 | 1 | 0x5340be41
PTOUPS1InverterStatus | INT | IOD_PTO | PTO:.UPS[1].InverterStatus | [6 empty] | 6157 | 1 | 0x5340be42
PTOUPS1IzhodMocL1 | REAL | IOD_PTO | PTO:.UPS[1].IzhodMocL1 | 0 | 100 | 0 | 100 | % | #### | 6157 | 1 | 0x5340be43
PTOUPS1IzhodMocL2 | REAL | IOD_PTO | PTO:.UPS[1].IzhodMocL2 | 0 | 100 | 0 | 100 | % | #### | 6157 | 1 | 0x5340be44
PTOUPS1IzhodMocL3 | REAL | IOD_PTO | PTO:.UPS[1].IzhodMocL3 | 0 | 100 | 0 | 100 | % | #### | 6157 | 1 | 0x5340be45
PTOUPS1Napaka | DIGITAL | IOD_PTO | PTO:.UPS[1].Napaka | [6 empty] | 6157 | 1 | 0x5340be50
PTOUPS1NapetostBaterije | REAL | IOD_PTO | PTO:.UPS[1].NapetostBaterije | 0 | 500 | 0 | 500 | V | #### | 6157 | 1 | 0x5340be60
PTOUPS1OutputStatus | INT | IOD_PTO | PTO:.UPS[1].OutputStatus | [6 empty] | 6157 | 1 | 0x5340be61
PTOUPS1StatusBaterije | INT | IOD_PTO | PTO:.UPS[1].StatusBaterije | [6 empty] | 6157 | 1 | 0x5340be62
PTOUPS1StatusEcomodeAktiven | DIGITAL | IOD_PTO | PTO:.UPS[1].StatusEcomodeAktiven | [6 empty] | 6157 | 1 | 0x5340be70
PTOUPS1StatusInverterIsOn | DIGITAL | IOD_PTO | PTO:.UPS[1].StatusInverterIsOn | [6 empty] | 6157 | 1 | 0x5340be80
PTOUPS1StatusStopOperation | DIGITAL | IOD_PTO | PTO:.UPS[1].StatusStopOperation | [6 empty] | 6157 | 1 | 0x5340be90
PTOUPS1SteviloIzpadovVhodneLinije | INT | IOD_PTO | PTO:.UPS[1].SteviloIzpadovVhodneLinije | 0 | 1000 | 0 | 1000 |  | #### | 6157 | 1 | 0x5340bea0
PTOUPS1TemperaturaBaterije | REAL | IOD_PTO | PTO:.UPS[1].TemperaturaBaterije | 0 | 200 | 0 | 200 | °C | #### | 6157 | 1 | 0x5340bea1
PTOUPS1UnitStatus | INT | IOD_PTO | PTO:.UPS[1].UnitStatus | [6 empty] | 6157 | 1 | 0x5340bea2
PTOUPS1VhodFrekvencaL1 | REAL | IOD_PTO | PTO:.UPS[1].VhodFrekvencaL1 | 0 | 100 | 0 | 100 | Hz | #### | 6157 | 1 | 0x5340bea3
PTOUPS1VhodFrekvencaL2 | REAL | IOD_PTO | PTO:.UPS[1].VhodFrekvencaL2 | 0 | 100 | 0 | 100 | Hz | #### | 6157 | 1 | 0x5340bea4
PTOUPS1VhodFrekvencaL3 | REAL | IOD_PTO | PTO:.UPS[1].VhodFrekvencaL3 | 0 | 100 | 0 | 100 | Hz | #### | 6157 | 1 | 0x5340bea5
PTOUPS1VhodNapetostL1 | REAL | IOD_PTO | PTO:.UPS[1].VhodNapetostL1 | 0 | 500 | 0 | 500 | V | #### | 6157 | 1 | 0x5340bea6
PTOUPS1VhodNapetostL2 | REAL | IOD_PTO | PTO:.UPS[1].VhodNapetostL2 | 0 | 500 | 0 | 500 | V | #### | 6157 | 1 | 0x5340bea7
PTOUPS1VhodNapetostL3 | REAL | IOD_PTO | PTO:.UPS[1].VhodNapetostL3 | 0 | 500 | 0 | 500 | V | #### | 6157 | 1 | 0x5340bea8
PTOUPS2AlarmAwaitingPower | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmAwaitingPower | [6 empty] | 6157 | 1 | 0x5340beb0
PTOUPS2AlarmBypassBad | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmBypassBad | [6 empty] | 6157 | 1 | 0x5340bec0
PTOUPS2AlarmChargerFailed | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmChargerFailed | [6 empty] | 6157 | 1 | 0x5340bed0
PTOUPS2AlarmCommunicationsLost | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmCommunicationsLost | [6 empty] | 6157 | 1 | 0x5340bee0
PTOUPS2AlarmDepletedBattery | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmDepletedBattery | [6 empty] | 6157 | 1 | 0x5340bef0
PTOUPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmDiagnosticTestFailed | [6 empty] | 6157 | 1 | 0x5340bf00
PTOUPS2AlarmInverterError | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmInverterError | [6 empty] | 6157 | 1 | 0x5340bf10
PTOUPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmIzhodOffKotZahtevano | [6 empty] | 6157 | 1 | 0x5340bf20
PTOUPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmIzhodPreobremenjen | [6 empty] | 6157 | 1 | 0x5340bf30
PTOUPS2AlarmLowBattery | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmLowBattery | [6 empty] | 6157 | 1 | 0x5340bf40
PTOUPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmNapakaNaVarovalki | [6 empty] | 6157 | 1 | 0x5340bf50
PTOUPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmNapakaNaVentilatorju | [6 empty] | 6157 | 1 | 0x5340bf60
PTOUPS2AlarmOnBattery | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmOnBattery | [6 empty] | 6157 | 1 | 0x5340bf70
PTOUPS2AlarmOnBypass | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmOnBypass | [6 empty] | 6157 | 1 | 0x5340bf80
PTOUPS2AlarmShutdownImminent | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmShutdownImminent | [6 empty] | 6157 | 1 | 0x5340bf90
PTOUPS2AlarmShutdownPending | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmShutdownPending | [6 empty] | 6157 | 1 | 0x5340bfa0
PTOUPS2AlarmSlabaBaterija | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmSlabaBaterija | [6 empty] | 6157 | 1 | 0x5340bfb0
PTOUPS2AlarmSplosnaNapaka | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmSplosnaNapaka | [6 empty] | 6157 | 1 | 0x5340bfc0
PTOUPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmStanjeIzhodaIzvenToleranc | [6 empty] | 6157 | 1 | 0x5340bfd0
PTOUPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmStanjeVhodaIzvenToleranc | [6 empty] | 6157 | 1 | 0x5340bfe0
PTOUPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmTemperaturaIzvenToleranc | [6 empty] | 6157 | 1 | 0x5340bff0
PTOUPS2AlarmTestInProgres | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmTestInProgres | [6 empty] | 6157 | 1 | 0x5340c000
PTOUPS2AlarmUPSIzhodOff | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmUPSIzhodOff | [6 empty] | 6157 | 1 | 0x5340c010
PTOUPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmUPSOffKotZahtevano | [6 empty] | 6157 | 1 | 0x5340c020
PTOUPS2AlarmUPSSystemOff | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmUPSSystemOff | [6 empty] | 6157 | 1 | 0x5340c030
PTOUPS2EstimatedChargeRemaining | REAL | IOD_PTO | PTO:.UPS[2].EstimatedChargeRemaining | 0 | 100 | 0 | 100 | % | #### | 6157 | 1 | 0x5340c040
PTOUPS2EstimatedMinutesRemaining | REAL | IOD_PTO | PTO:.UPS[2].EstimatedMinutesRemaining | 0 | 1000 | 0 | 100 | min | #### | 6157 | 1 | 0x5340c041
PTOUPS2InverterStatus | INT | IOD_PTO | PTO:.UPS[2].InverterStatus | [6 empty] | 6157 | 1 | 0x5340c042
PTOUPS2IzhodMocL1 | REAL | IOD_PTO | PTO:.UPS[2].IzhodMocL1 | 0 | 100 | 0 | 100 | % | #### | 6157 | 1 | 0x5340c043
PTOUPS2IzhodMocL2 | REAL | IOD_PTO | PTO:.UPS[2].IzhodMocL2 | 0 | 100 | 0 | 100 | % | #### | 6157 | 1 | 0x5340c044
PTOUPS2IzhodMocL3 | REAL | IOD_PTO | PTO:.UPS[2].IzhodMocL3 | 0 | 100 | 0 | 100 | % | #### | 6157 | 1 | 0x5340c045
PTOUPS2Napaka | DIGITAL | IOD_PTO | PTO:.UPS[2].Napaka | [6 empty] | 6157 | 1 | 0x5340c050
PTOUPS2NapetostBaterije | REAL | IOD_PTO | PTO:.UPS[2].NapetostBaterije | 0 | 500 | 0 | 500 | V | #### | 6157 | 1 | 0x5340c060
PTOUPS2OutputStatus | INT | IOD_PTO | PTO:.UPS[2].OutputStatus | [6 empty] | 6157 | 1 | 0x5340c061
PTOUPS2StatusBaterije | INT | IOD_PTO | PTO:.UPS[2].StatusBaterije | [6 empty] | 6157 | 1 | 0x5340c062
PTOUPS2StatusEcomodeAktiven | DIGITAL | IOD_PTO | PTO:.UPS[2].StatusEcomodeAktiven | [6 empty] | 6157 | 1 | 0x5340c070
PTOUPS2StatusInverterIsOn | DIGITAL | IOD_PTO | PTO:.UPS[2].StatusInverterIsOn | [6 empty] | 6157 | 1 | 0x5340c080
PTOUPS2StatusStopOperation | DIGITAL | IOD_PTO | PTO:.UPS[2].StatusStopOperation | [6 empty] | 6157 | 1 | 0x5340c090
PTOUPS2SteviloIzpadovVhodneLinije | INT | IOD_PTO | PTO:.UPS[2].SteviloIzpadovVhodneLinije | 0 | 1000 | 0 | 1000 |  | #### | 6157 | 1 | 0x5340c0a0
PTOUPS2TemperaturaBaterije | REAL | IOD_PTO | PTO:.UPS[2].TemperaturaBaterije | 0 | 200 | 0 | 200 | °C | #### | 6157 | 1 | 0x5340c0a1
PTOUPS2UnitStatus | INT | IOD_PTO | PTO:.UPS[2].UnitStatus | [6 empty] | 6157 | 1 | 0x5340c0a2
PTOUPS2VhodFrekvencaL1 | REAL | IOD_PTO | PTO:.UPS[2].VhodFrekvencaL1 | 0 | 100 | 0 | 100 | Hz | #### | 6157 | 1 | 0x5340c0a3
PTOUPS2VhodFrekvencaL2 | REAL | IOD_PTO | PTO:.UPS[2].VhodFrekvencaL2 | 0 | 100 | 0 | 100 | Hz | #### | 6157 | 1 | 0x5340c0a4
PTOUPS2VhodFrekvencaL3 | REAL | IOD_PTO | PTO:.UPS[2].VhodFrekvencaL3 | 0 | 100 | 0 | 100 | Hz | #### | 6157 | 1 | 0x5340c0a5
PTOUPS2VhodNapetostL1 | REAL | IOD_PTO | PTO:.UPS[2].VhodNapetostL1 | 0 | 500 | 0 | 500 | V | #### | 6157 | 1 | 0x5340c0a6
PTOUPS2VhodNapetostL2 | REAL | IOD_PTO | PTO:.UPS[2].VhodNapetostL2 | 0 | 500 | 0 | 500 | V | #### | 6157 | 1 | 0x5340c0a7
PTOUPS2VhodNapetostL3 | REAL | IOD_PTO | PTO:.UPS[2].VhodNapetostL3 | 0 | 500 | 0 | 500 | V | #### | 6157 | 1 | 0x5340c0a8
PTOUserCurrentLevel | BYTE | IOD_PTO | PTO:.UserCurrentLevel | [6 empty] | 6157 | 1 | 0x5340c0a9
PTOUserCurrentName | STRING | IOD_PTO | PTO:.UserCurrentName | [6 empty] | 6157 | 1 | 0x5340c0aa
PTOUserLoggedIn | DIGITAL | IOD_PTO | PTO:.UserLoggedIn | [6 empty] | 6157 | 1 | 0x5340c0b0
PTOVlagaPovp1 | REAL | IOD_PTO | PTO:.VlagaPovp[1] | [6 empty] | 6157 | 1 | 0x5340c0c0
PTOVlagaPovp2 | REAL | IOD_PTO | PTO:.VlagaPovp[2] | [6 empty] | 6157 | 1 | 0x5340c0c1
PTOVlagaPovp3 | REAL | IOD_PTO | PTO:.VlagaPovp[3] | [6 empty] | 6157 | 1 | 0x5340c0c2
APTO_omogoci_sms | DIGITAL | IOD_PTO_disk2 | D1[600] | [8 empty] | 0x5340c0d0
BPTO_omogoci_sms | DIGITAL | IOD_PTO_disk2 | D601[600] | [8 empty] | 0x5340c0e0
CPTO_omogoci_sms | DIGITAL | IOD_PTO_disk2 | D1202[600] | [8 empty] | 0x5340c0f0
DPTO_omogoci_sms | DIGITAL | IOD_PTO_disk2 | D1804[600] | [8 empty] | 0x5340c100
EPTO_omogoci_sms | DIGITAL | IOD_PTO_disk2 | D2406[600] | [8 empty] | 0x5340c110
FPTO_omogoci_sms | DIGITAL | IOD_PTO_disk2 | D3008[600] | [8 empty] | 0x5340c120
PTO_PMM_1_Faza1_Tok01_nad80 | DIGITAL | IOD_PTO_disk | D1 | [8 empty] | 0x5340c130
PTO_PMM_1_Faza1_Tok02_nad80 | DIGITAL | IOD_PTO_disk | D2 | [8 empty] | 0x5340c140
PTO_PMM_1_Faza1_Tok03_nad80 | DIGITAL | IOD_PTO_disk | D3 | [8 empty] | 0x5340c150
PTO_PMM_1_Faza1_Tok04_nad80 | DIGITAL | IOD_PTO_disk | D4 | [8 empty] | 0x5340c160
PTO_PMM_1_Faza1_Tok05_nad80 | DIGITAL | IOD_PTO_disk | D5 | [8 empty] | 0x5340c170
PTO_PMM_1_Faza1_Tok06_nad80 | DIGITAL | IOD_PTO_disk | D6 | [8 empty] | 0x5340c180
PTO_PMM_1_Faza1_Tok07_nad80 | DIGITAL | IOD_PTO_disk | D7 | [8 empty] | 0x5340c190
PTO_PMM_1_Faza1_Tok08_nad80 | DIGITAL | IOD_PTO_disk | D8 | [8 empty] | 0x5340c1a0
PTO_PMM_1_Faza1_Tok09_nad80 | DIGITAL | IOD_PTO_disk | D9 | [8 empty] | 0x5340c1b0
PTO_PMM_1_Faza1_Tok10_nad80 | DIGITAL | IOD_PTO_disk | D10 | [8 empty] | 0x5340c1c0
PTO_PMM_1_Faza1_Tok11_nad80 | DIGITAL | IOD_PTO_disk | D11 | [8 empty] | 0x5340c1d0
PTO_PMM_1_Faza1_Tok12_nad80 | DIGITAL | IOD_PTO_disk | D12 | [8 empty] | 0x5340c1e0
PTO_PMM_1_Faza1_Tok13_nad80 | DIGITAL | IOD_PTO_disk | D13 | [8 empty] | 0x5340c1f0
PTO_PMM_1_Faza1_Tok14_nad80 | DIGITAL | IOD_PTO_disk | D14 | [8 empty] | 0x5340c200
PTO_PMM_1_Faza1_Tok15_nad80 | DIGITAL | IOD_PTO_disk | D15 | [8 empty] | 0x5340c210
PTO_PMM_1_Faza1_Tok16_nad80 | DIGITAL | IOD_PTO_disk | D16 | [8 empty] | 0x5340c220
PTO_PMM_1_Faza1_Tok17_nad80 | DIGITAL | IOD_PTO_disk | D17 | [8 empty] | 0x5340c230
PTO_PMM_1_Faza1_Tok18_nad80 | DIGITAL | IOD_PTO_disk | D18 | [8 empty] | 0x5340c240
PTO_PMM_1_Faza1_Tok19_nad80 | DIGITAL | IOD_PTO_disk | D19 | [8 empty] | 0x5340c250
PTO_PMM_1_Faza1_Tok20_nad80 | DIGITAL | IOD_PTO_disk | D20 | [8 empty] | 0x5340c260
PTO_PMM_1_Faza1_Tok21_nad80 | DIGITAL | IOD_PTO_disk | D21 | [8 empty] | 0x5340c270
PTO_PMM_1_Faza1_Tok22_nad80 | DIGITAL | IOD_PTO_disk | D22 | [8 empty] | 0x5340c280
PTO_PMM_1_Faza1_Tok23_nad80 | DIGITAL | IOD_PTO_disk | D23 | [8 empty] | 0x5340c290
PTO_PMM_1_Faza1_Tok24_nad80 | DIGITAL | IOD_PTO_disk | D24 | [8 empty] | 0x5340c2a0
PTO_PMM_1_Faza1_Tok25_nad80 | DIGITAL | IOD_PTO_disk | D25 | [8 empty] | 0x5340c2b0
PTO_PMM_1_Faza1_Tok26_nad80 | DIGITAL | IOD_PTO_disk | D26 | [8 empty] | 0x5340c2c0
PTO_PMM_1_Faza1_Tok27_nad80 | DIGITAL | IOD_PTO_disk | D27 | [8 empty] | 0x5340c2d0
PTO_PMM_1_Faza1_Tok28_nad80 | DIGITAL | IOD_PTO_disk | D28 | [8 empty] | 0x5340c2e0
PTO_PMM_1_Faza1_Tok29_nad80 | DIGITAL | IOD_PTO_disk | D29 | [8 empty] | 0x5340c2f0
PTO_PMM_1_Faza1_Tok30_nad80 | DIGITAL | IOD_PTO_disk | D30 | [8 empty] | 0x5340c300
PTO_PMM_1_Faza1_Tok31_nad80 | DIGITAL | IOD_PTO_disk | D31 | [8 empty] | 0x5340c310
PTO_PMM_1_Faza1_Tok32_nad80 | DIGITAL | IOD_PTO_disk | D32 | [8 empty] | 0x5340c320
PTO_PMM_1_Faza1_Tok33_nad80 | DIGITAL | IOD_PTO_disk | D33 | [8 empty] | 0x5340c330
PTO_PMM_1_Faza1_Tok34_nad80 | DIGITAL | IOD_PTO_disk | D34 | [8 empty] | 0x5340c340
PTO_PMM_1_Faza1_Tok35_nad80 | DIGITAL | IOD_PTO_disk | D35 | [8 empty] | 0x5340c350
PTO_PMM_1_Faza1_Tok36_nad80 | DIGITAL | IOD_PTO_disk | D36 | [8 empty] | 0x5340c360
PTO_PMM_1_Faza1_Tok37_nad80 | DIGITAL | IOD_PTO_disk | D37 | [8 empty] | 0x5340c370
PTO_PMM_1_Faza1_Tok38_nad80 | DIGITAL | IOD_PTO_disk | D38 | [8 empty] | 0x5340c380
PTO_PMM_1_Faza1_Tok39_nad80 | DIGITAL | IOD_PTO_disk | D39 | [8 empty] | 0x5340c390
PTO_PMM_1_Faza1_Tok40_nad80 | DIGITAL | IOD_PTO_disk | D40 | [8 empty] | 0x5340c3a0
PTO_PMM_1_Faza1_Tok41_nad80 | DIGITAL | IOD_PTO_disk | D41 | [8 empty] | 0x5340c3b0
PTO_PMM_1_Faza1_Tok42_nad80 | DIGITAL | IOD_PTO_disk | D42 | [8 empty] | 0x5340c3c0
PTO_PMM_1_Faza2_Tok01_nad80 | DIGITAL | IOD_PTO_disk | D43 | [8 empty] | 0x5340c3d0
PTO_PMM_1_Faza2_Tok02_nad80 | DIGITAL | IOD_PTO_disk | D44 | [8 empty] | 0x5340c3e0
PTO_PMM_1_Faza2_Tok03_nad80 | DIGITAL | IOD_PTO_disk | D45 | [8 empty] | 0x5340c3f0
PTO_PMM_1_Faza2_Tok04_nad80 | DIGITAL | IOD_PTO_disk | D46 | [8 empty] | 0x5340c400
PTO_PMM_1_Faza2_Tok05_nad80 | DIGITAL | IOD_PTO_disk | D47 | [8 empty] | 0x5340c410
PTO_PMM_1_Faza2_Tok06_nad80 | DIGITAL | IOD_PTO_disk | D48 | [8 empty] | 0x5340c420
PTO_PMM_1_Faza2_Tok07_nad80 | DIGITAL | IOD_PTO_disk | D49 | [8 empty] | 0x5340c430
PTO_PMM_1_Faza2_Tok08_nad80 | DIGITAL | IOD_PTO_disk | D50 | [8 empty] | 0x5340c440
PTO_PMM_1_Faza2_Tok09_nad80 | DIGITAL | IOD_PTO_disk | D51 | [8 empty] | 0x5340c450
PTO_PMM_1_Faza2_Tok10_nad80 | DIGITAL | IOD_PTO_disk | D52 | [8 empty] | 0x5340c460
PTO_PMM_1_Faza2_Tok11_nad80 | DIGITAL | IOD_PTO_disk | D53 | [8 empty] | 0x5340c470
PTO_PMM_1_Faza2_Tok12_nad80 | DIGITAL | IOD_PTO_disk | D54 | [8 empty] | 0x5340c480
PTO_PMM_1_Faza2_Tok13_nad80 | DIGITAL | IOD_PTO_disk | D55 | [8 empty] | 0x5340c490
PTO_PMM_1_Faza2_Tok14_nad80 | DIGITAL | IOD_PTO_disk | D56 | [8 empty] | 0x5340c4a0
PTO_PMM_1_Faza2_Tok15_nad80 | DIGITAL | IOD_PTO_disk | D57 | [8 empty] | 0x5340c4b0
PTO_PMM_1_Faza2_Tok16_nad80 | DIGITAL | IOD_PTO_disk | D58 | [8 empty] | 0x5340c4c0
PTO_PMM_1_Faza2_Tok17_nad80 | DIGITAL | IOD_PTO_disk | D59 | [8 empty] | 0x5340c4d0
PTO_PMM_1_Faza2_Tok18_nad80 | DIGITAL | IOD_PTO_disk | D60 | [8 empty] | 0x5340c4e0
PTO_PMM_1_Faza2_Tok19_nad80 | DIGITAL | IOD_PTO_disk | D61 | [8 empty] | 0x5340c4f0
PTO_PMM_1_Faza2_Tok20_nad80 | DIGITAL | IOD_PTO_disk | D62 | [8 empty] | 0x5340c500
PTO_PMM_1_Faza2_Tok21_nad80 | DIGITAL | IOD_PTO_disk | D63 | [8 empty] | 0x5340c510
PTO_PMM_1_Faza2_Tok22_nad80 | DIGITAL | IOD_PTO_disk | D64 | [8 empty] | 0x5340c520
PTO_PMM_1_Faza2_Tok23_nad80 | DIGITAL | IOD_PTO_disk | D65 | [8 empty] | 0x5340c530
PTO_PMM_1_Faza2_Tok24_nad80 | DIGITAL | IOD_PTO_disk | D66 | [8 empty] | 0x5340c540
PTO_PMM_1_Faza2_Tok25_nad80 | DIGITAL | IOD_PTO_disk | D67 | [8 empty] | 0x5340c550
PTO_PMM_1_Faza2_Tok26_nad80 | DIGITAL | IOD_PTO_disk | D68 | [8 empty] | 0x5340c560
PTO_PMM_1_Faza2_Tok27_nad80 | DIGITAL | IOD_PTO_disk | D69 | [8 empty] | 0x5340c570
PTO_PMM_1_Faza2_Tok28_nad80 | DIGITAL | IOD_PTO_disk | D70 | [8 empty] | 0x5340c580
PTO_PMM_1_Faza2_Tok29_nad80 | DIGITAL | IOD_PTO_disk | D71 | [8 empty] | 0x5340c590
PTO_PMM_1_Faza2_Tok30_nad80 | DIGITAL | IOD_PTO_disk | D72 | [8 empty] | 0x5340c5a0
PTO_PMM_1_Faza2_Tok31_nad80 | DIGITAL | IOD_PTO_disk | D73 | [8 empty] | 0x5340c5b0
PTO_PMM_1_Faza2_Tok32_nad80 | DIGITAL | IOD_PTO_disk | D74 | [8 empty] | 0x5340c5c0
PTO_PMM_1_Faza2_Tok33_nad80 | DIGITAL | IOD_PTO_disk | D75 | [8 empty] | 0x5340c5d0
PTO_PMM_1_Faza2_Tok34_nad80 | DIGITAL | IOD_PTO_disk | D76 | [8 empty] | 0x5340c5e0
PTO_PMM_1_Faza2_Tok35_nad80 | DIGITAL | IOD_PTO_disk | D77 | [8 empty] | 0x5340c5f0
PTO_PMM_1_Faza2_Tok36_nad80 | DIGITAL | IOD_PTO_disk | D78 | [8 empty] | 0x5340c600
PTO_PMM_1_Faza2_Tok37_nad80 | DIGITAL | IOD_PTO_disk | D79 | [8 empty] | 0x5340c610
PTO_PMM_1_Faza2_Tok38_nad80 | DIGITAL | IOD_PTO_disk | D80 | [8 empty] | 0x5340c620
PTO_PMM_1_Faza2_Tok39_nad80 | DIGITAL | IOD_PTO_disk | D81 | [8 empty] | 0x5340c630
PTO_PMM_1_Faza2_Tok40_nad80 | DIGITAL | IOD_PTO_disk | D82 | [8 empty] | 0x5340c640
PTO_PMM_1_Faza2_Tok41_nad80 | DIGITAL | IOD_PTO_disk | D83 | [8 empty] | 0x5340c650
PTO_PMM_1_Faza2_Tok42_nad80 | DIGITAL | IOD_PTO_disk | D84 | [8 empty] | 0x5340c660
PTO_PMM_1_Faza3_Tok01_nad80 | DIGITAL | IOD_PTO_disk | D85 | [8 empty] | 0x5340c670
PTO_PMM_1_Faza3_Tok02_nad80 | DIGITAL | IOD_PTO_disk | D86 | [8 empty] | 0x5340c680
PTO_PMM_1_Faza3_Tok03_nad80 | DIGITAL | IOD_PTO_disk | D87 | [8 empty] | 0x5340c690
PTO_PMM_1_Faza3_Tok04_nad80 | DIGITAL | IOD_PTO_disk | D88 | [8 empty] | 0x5340c6a0
PTO_PMM_1_Faza3_Tok05_nad80 | DIGITAL | IOD_PTO_disk | D89 | [8 empty] | 0x5340c6b0
PTO_PMM_1_Faza3_Tok06_nad80 | DIGITAL | IOD_PTO_disk | D90 | [8 empty] | 0x5340c6c0
PTO_PMM_1_Faza3_Tok07_nad80 | DIGITAL | IOD_PTO_disk | D91 | [8 empty] | 0x5340c6d0
PTO_PMM_1_Faza3_Tok08_nad80 | DIGITAL | IOD_PTO_disk | D92 | [8 empty] | 0x5340c6e0
PTO_PMM_1_Faza3_Tok09_nad80 | DIGITAL | IOD_PTO_disk | D93 | [8 empty] | 0x5340c6f0
PTO_PMM_1_Faza3_Tok10_nad80 | DIGITAL | IOD_PTO_disk | D94 | [8 empty] | 0x5340c700
PTO_PMM_1_Faza3_Tok11_nad80 | DIGITAL | IOD_PTO_disk | D95 | [8 empty] | 0x5340c710
PTO_PMM_1_Faza3_Tok12_nad80 | DIGITAL | IOD_PTO_disk | D96 | [8 empty] | 0x5340c720
PTO_PMM_1_Faza3_Tok13_nad80 | DIGITAL | IOD_PTO_disk | D97 | [8 empty] | 0x5340c730
PTO_PMM_1_Faza3_Tok14_nad80 | DIGITAL | IOD_PTO_disk | D98 | [8 empty] | 0x5340c740
PTO_PMM_1_Faza3_Tok15_nad80 | DIGITAL | IOD_PTO_disk | D99 | [8 empty] | 0x5340c750
PTO_PMM_1_Faza3_Tok16_nad80 | DIGITAL | IOD_PTO_disk | D100 | [8 empty] | 0x5340c760
PTO_PMM_1_Faza3_Tok17_nad80 | DIGITAL | IOD_PTO_disk | D101 | [8 empty] | 0x5340c770
PTO_PMM_1_Faza3_Tok18_nad80 | DIGITAL | IOD_PTO_disk | D102 | [8 empty] | 0x5340c780
PTO_PMM_1_Faza3_Tok19_nad80 | DIGITAL | IOD_PTO_disk | D103 | [8 empty] | 0x5340c790
PTO_PMM_1_Faza3_Tok20_nad80 | DIGITAL | IOD_PTO_disk | D104 | [8 empty] | 0x5340c7a0
PTO_PMM_1_Faza3_Tok21_nad80 | DIGITAL | IOD_PTO_disk | D105 | [8 empty] | 0x5340c7b0
PTO_PMM_1_Faza3_Tok22_nad80 | DIGITAL | IOD_PTO_disk | D106 | [8 empty] | 0x5340c7c0
PTO_PMM_1_Faza3_Tok23_nad80 | DIGITAL | IOD_PTO_disk | D107 | [8 empty] | 0x5340c7d0
PTO_PMM_1_Faza3_Tok24_nad80 | DIGITAL | IOD_PTO_disk | D108 | [8 empty] | 0x5340c7e0
PTO_PMM_1_Faza3_Tok25_nad80 | DIGITAL | IOD_PTO_disk | D109 | [8 empty] | 0x5340c7f0
PTO_PMM_1_Faza3_Tok26_nad80 | DIGITAL | IOD_PTO_disk | D110 | [8 empty] | 0x5340c800
PTO_PMM_1_Faza3_Tok27_nad80 | DIGITAL | IOD_PTO_disk | D111 | [8 empty] | 0x5340c810
PTO_PMM_1_Faza3_Tok28_nad80 | DIGITAL | IOD_PTO_disk | D112 | [8 empty] | 0x5340c820
PTO_PMM_1_Faza3_Tok29_nad80 | DIGITAL | IOD_PTO_disk | D113 | [8 empty] | 0x5340c830
PTO_PMM_1_Faza3_Tok30_nad80 | DIGITAL | IOD_PTO_disk | D114 | [8 empty] | 0x5340c840
PTO_PMM_1_Faza3_Tok31_nad80 | DIGITAL | IOD_PTO_disk | D115 | [8 empty] | 0x5340c850
PTO_PMM_1_Faza3_Tok32_nad80 | DIGITAL | IOD_PTO_disk | D116 | [8 empty] | 0x5340c860
PTO_PMM_1_Faza3_Tok33_nad80 | DIGITAL | IOD_PTO_disk | D117 | [8 empty] | 0x5340c870
PTO_PMM_1_Faza3_Tok34_nad80 | DIGITAL | IOD_PTO_disk | D118 | [8 empty] | 0x5340c880
PTO_PMM_1_Faza3_Tok35_nad80 | DIGITAL | IOD_PTO_disk | D119 | [8 empty] | 0x5340c890
PTO_PMM_1_Faza3_Tok36_nad80 | DIGITAL | IOD_PTO_disk | D120 | [8 empty] | 0x5340c8a0
PTO_PMM_1_Faza3_Tok37_nad80 | DIGITAL | IOD_PTO_disk | D121 | [8 empty] | 0x5340c8b0
PTO_PMM_1_Faza3_Tok38_nad80 | DIGITAL | IOD_PTO_disk | D122 | [8 empty] | 0x5340c8c0
PTO_PMM_1_Faza3_Tok39_nad80 | DIGITAL | IOD_PTO_disk | D123 | [8 empty] | 0x5340c8d0
PTO_PMM_1_Faza3_Tok40_nad80 | DIGITAL | IOD_PTO_disk | D124 | [8 empty] | 0x5340c8e0
PTO_PMM_1_Faza3_Tok41_nad80 | DIGITAL | IOD_PTO_disk | D125 | [8 empty] | 0x5340c8f0
PTO_PMM_1_Faza3_Tok42_nad80 | DIGITAL | IOD_PTO_disk | D126 | [8 empty] | 0x5340c900
PTO_PMM_1_Faza1_Tok01_med60in80 | DIGITAL | IOD_PTO_disk | D127 | [8 empty] | 0x5340c910
PTO_PMM_1_Faza1_Tok02_med60in80 | DIGITAL | IOD_PTO_disk | D128 | [8 empty] | 0x5340c920
PTO_PMM_1_Faza1_Tok03_med60in80 | DIGITAL | IOD_PTO_disk | D129 | [8 empty] | 0x5340c930
PTO_PMM_1_Faza1_Tok04_med60in80 | DIGITAL | IOD_PTO_disk | D130 | [8 empty] | 0x5340c940
PTO_PMM_1_Faza1_Tok05_med60in80 | DIGITAL | IOD_PTO_disk | D131 | [8 empty] | 0x5340c950
PTO_PMM_1_Faza1_Tok06_med60in80 | DIGITAL | IOD_PTO_disk | D132 | [8 empty] | 0x5340c960
PTO_PMM_1_Faza1_Tok07_med60in80 | DIGITAL | IOD_PTO_disk | D133 | [8 empty] | 0x5340c970
PTO_PMM_1_Faza1_Tok08_med60in80 | DIGITAL | IOD_PTO_disk | D134 | [8 empty] | 0x5340c980
PTO_PMM_1_Faza1_Tok09_med60in80 | DIGITAL | IOD_PTO_disk | D135 | [8 empty] | 0x5340c990
PTO_PMM_1_Faza1_Tok10_med60in80 | DIGITAL | IOD_PTO_disk | D136 | [8 empty] | 0x5340c9a0
PTO_PMM_1_Faza1_Tok11_med60in80 | DIGITAL | IOD_PTO_disk | D137 | [8 empty] | 0x5340c9b0
PTO_PMM_1_Faza1_Tok12_med60in80 | DIGITAL | IOD_PTO_disk | D138 | [8 empty] | 0x5340c9c0
PTO_PMM_1_Faza1_Tok13_med60in80 | DIGITAL | IOD_PTO_disk | D139 | [8 empty] | 0x5340c9d0
PTO_PMM_1_Faza1_Tok14_med60in80 | DIGITAL | IOD_PTO_disk | D140 | [8 empty] | 0x5340c9e0
PTO_PMM_1_Faza1_Tok15_med60in80 | DIGITAL | IOD_PTO_disk | D141 | [8 empty] | 0x5340c9f0
PTO_PMM_1_Faza1_Tok16_med60in80 | DIGITAL | IOD_PTO_disk | D142 | [8 empty] | 0x5340ca00
PTO_PMM_1_Faza1_Tok17_med60in80 | DIGITAL | IOD_PTO_disk | D143 | [8 empty] | 0x5340ca10
PTO_PMM_1_Faza1_Tok18_med60in80 | DIGITAL | IOD_PTO_disk | D144 | [8 empty] | 0x5340ca20
PTO_PMM_1_Faza1_Tok19_med60in80 | DIGITAL | IOD_PTO_disk | D145 | [8 empty] | 0x5340ca30
PTO_PMM_1_Faza1_Tok20_med60in80 | DIGITAL | IOD_PTO_disk | D146 | [8 empty] | 0x5340ca40
PTO_PMM_1_Faza1_Tok21_med60in80 | DIGITAL | IOD_PTO_disk | D147 | [8 empty] | 0x5340ca50
PTO_PMM_1_Faza1_Tok22_med60in80 | DIGITAL | IOD_PTO_disk | D148 | [8 empty] | 0x5340ca60
PTO_PMM_1_Faza1_Tok23_med60in80 | DIGITAL | IOD_PTO_disk | D149 | [8 empty] | 0x5340ca70
PTO_PMM_1_Faza1_Tok24_med60in80 | DIGITAL | IOD_PTO_disk | D150 | [8 empty] | 0x5340ca80
PTO_PMM_1_Faza1_Tok25_med60in80 | DIGITAL | IOD_PTO_disk | D151 | [8 empty] | 0x5340ca90
PTO_PMM_1_Faza1_Tok26_med60in80 | DIGITAL | IOD_PTO_disk | D152 | [8 empty] | 0x5340caa0
PTO_PMM_1_Faza1_Tok27_med60in80 | DIGITAL | IOD_PTO_disk | D153 | [8 empty] | 0x5340cab0
PTO_PMM_1_Faza1_Tok28_med60in80 | DIGITAL | IOD_PTO_disk | D154 | [8 empty] | 0x5340cac0
PTO_PMM_1_Faza1_Tok29_med60in80 | DIGITAL | IOD_PTO_disk | D155 | [8 empty] | 0x5340cad0
PTO_PMM_1_Faza1_Tok30_med60in80 | DIGITAL | IOD_PTO_disk | D156 | [8 empty] | 0x5340cae0
PTO_PMM_1_Faza1_Tok31_med60in80 | DIGITAL | IOD_PTO_disk | D157 | [8 empty] | 0x5340caf0
PTO_PMM_1_Faza1_Tok32_med60in80 | DIGITAL | IOD_PTO_disk | D158 | [8 empty] | 0x5340cb00
PTO_PMM_1_Faza1_Tok33_med60in80 | DIGITAL | IOD_PTO_disk | D159 | [8 empty] | 0x5340cb10
PTO_PMM_1_Faza1_Tok34_med60in80 | DIGITAL | IOD_PTO_disk | D160 | [8 empty] | 0x5340cb20
PTO_PMM_1_Faza1_Tok35_med60in80 | DIGITAL | IOD_PTO_disk | D161 | [8 empty] | 0x5340cb30
PTO_PMM_1_Faza1_Tok36_med60in80 | DIGITAL | IOD_PTO_disk | D162 | [8 empty] | 0x5340cb40
PTO_PMM_1_Faza1_Tok37_med60in80 | DIGITAL | IOD_PTO_disk | D163 | [8 empty] | 0x5340cb50
PTO_PMM_1_Faza1_Tok38_med60in80 | DIGITAL | IOD_PTO_disk | D164 | [8 empty] | 0x5340cb60
PTO_PMM_1_Faza1_Tok39_med60in80 | DIGITAL | IOD_PTO_disk | D165 | [8 empty] | 0x5340cb70
PTO_PMM_1_Faza1_Tok40_med60in80 | DIGITAL | IOD_PTO_disk | D166 | [8 empty] | 0x5340cb80
PTO_PMM_1_Faza1_Tok41_med60in80 | DIGITAL | IOD_PTO_disk | D167 | [8 empty] | 0x5340cb90
PTO_PMM_1_Faza1_Tok42_med60in80 | DIGITAL | IOD_PTO_disk | D168 | [8 empty] | 0x5340cba0
PTO_PMM_1_Faza2_Tok01_med60in80 | DIGITAL | IOD_PTO_disk | D169 | [8 empty] | 0x5340cbb0
PTO_PMM_1_Faza2_Tok02_med60in80 | DIGITAL | IOD_PTO_disk | D170 | [8 empty] | 0x5340cbc0
PTO_PMM_1_Faza2_Tok03_med60in80 | DIGITAL | IOD_PTO_disk | D171 | [8 empty] | 0x5340cbd0
PTO_PMM_1_Faza2_Tok04_med60in80 | DIGITAL | IOD_PTO_disk | D172 | [8 empty] | 0x5340cbe0
PTO_PMM_1_Faza2_Tok05_med60in80 | DIGITAL | IOD_PTO_disk | D173 | [8 empty] | 0x5340cbf0
PTO_PMM_1_Faza2_Tok06_med60in80 | DIGITAL | IOD_PTO_disk | D174 | [8 empty] | 0x5340cc00
PTO_PMM_1_Faza2_Tok07_med60in80 | DIGITAL | IOD_PTO_disk | D175 | [8 empty] | 0x5340cc10
PTO_PMM_1_Faza2_Tok08_med60in80 | DIGITAL | IOD_PTO_disk | D176 | [8 empty] | 0x5340cc20
PTO_PMM_1_Faza2_Tok09_med60in80 | DIGITAL | IOD_PTO_disk | D177 | [8 empty] | 0x5340cc30
PTO_PMM_1_Faza2_Tok10_med60in80 | DIGITAL | IOD_PTO_disk | D178 | [8 empty] | 0x5340cc40
PTO_PMM_1_Faza2_Tok11_med60in80 | DIGITAL | IOD_PTO_disk | D179 | [8 empty] | 0x5340cc50
PTO_PMM_1_Faza2_Tok12_med60in80 | DIGITAL | IOD_PTO_disk | D180 | [8 empty] | 0x5340cc60
PTO_PMM_1_Faza2_Tok13_med60in80 | DIGITAL | IOD_PTO_disk | D181 | [8 empty] | 0x5340cc70
PTO_PMM_1_Faza2_Tok14_med60in80 | DIGITAL | IOD_PTO_disk | D182 | [8 empty] | 0x5340cc80
PTO_PMM_1_Faza2_Tok15_med60in80 | DIGITAL | IOD_PTO_disk | D183 | [8 empty] | 0x5340cc90
PTO_PMM_1_Faza2_Tok16_med60in80 | DIGITAL | IOD_PTO_disk | D184 | [8 empty] | 0x5340cca0
PTO_PMM_1_Faza2_Tok17_med60in80 | DIGITAL | IOD_PTO_disk | D185 | [8 empty] | 0x5340ccb0
PTO_PMM_1_Faza2_Tok18_med60in80 | DIGITAL | IOD_PTO_disk | D186 | [8 empty] | 0x5340ccc0
PTO_PMM_1_Faza2_Tok19_med60in80 | DIGITAL | IOD_PTO_disk | D187 | [8 empty] | 0x5340ccd0
PTO_PMM_1_Faza2_Tok20_med60in80 | DIGITAL | IOD_PTO_disk | D188 | [8 empty] | 0x5340cce0
PTO_PMM_1_Faza2_Tok21_med60in80 | DIGITAL | IOD_PTO_disk | D189 | [8 empty] | 0x5340ccf0
PTO_PMM_1_Faza2_Tok22_med60in80 | DIGITAL | IOD_PTO_disk | D190 | [8 empty] | 0x5340cd00
PTO_PMM_1_Faza2_Tok23_med60in80 | DIGITAL | IOD_PTO_disk | D191 | [8 empty] | 0x5340cd10
PTO_PMM_1_Faza2_Tok24_med60in80 | DIGITAL | IOD_PTO_disk | D192 | [8 empty] | 0x5340cd20
PTO_PMM_1_Faza2_Tok25_med60in80 | DIGITAL | IOD_PTO_disk | D193 | [8 empty] | 0x5340cd30
PTO_PMM_1_Faza2_Tok26_med60in80 | DIGITAL | IOD_PTO_disk | D194 | [8 empty] | 0x5340cd40
PTO_PMM_1_Faza2_Tok27_med60in80 | DIGITAL | IOD_PTO_disk | D195 | [8 empty] | 0x5340cd50
PTO_PMM_1_Faza2_Tok28_med60in80 | DIGITAL | IOD_PTO_disk | D196 | [8 empty] | 0x5340cd60
PTO_PMM_1_Faza2_Tok29_med60in80 | DIGITAL | IOD_PTO_disk | D197 | [8 empty] | 0x5340cd70
PTO_PMM_1_Faza2_Tok30_med60in80 | DIGITAL | IOD_PTO_disk | D198 | [8 empty] | 0x5340cd80
PTO_PMM_1_Faza2_Tok31_med60in80 | DIGITAL | IOD_PTO_disk | D199 | [8 empty] | 0x5340cd90
PTO_PMM_1_Faza2_Tok32_med60in80 | DIGITAL | IOD_PTO_disk | D200 | [8 empty] | 0x5340cda0
PTO_PMM_1_Faza2_Tok33_med60in80 | DIGITAL | IOD_PTO_disk | D201 | [8 empty] | 0x5340cdb0
PTO_PMM_1_Faza2_Tok34_med60in80 | DIGITAL | IOD_PTO_disk | D202 | [8 empty] | 0x5340cdc0
PTO_PMM_1_Faza2_Tok35_med60in80 | DIGITAL | IOD_PTO_disk | D203 | [8 empty] | 0x5340cdd0
PTO_PMM_1_Faza2_Tok36_med60in80 | DIGITAL | IOD_PTO_disk | D204 | [8 empty] | 0x5340cde0
PTO_PMM_1_Faza2_Tok37_med60in80 | DIGITAL | IOD_PTO_disk | D205 | [8 empty] | 0x5340cdf0
PTO_PMM_1_Faza2_Tok38_med60in80 | DIGITAL | IOD_PTO_disk | D206 | [8 empty] | 0x5340ce00
PTO_PMM_1_Faza2_Tok39_med60in80 | DIGITAL | IOD_PTO_disk | D207 | [8 empty] | 0x5340ce10
PTO_PMM_1_Faza2_Tok40_med60in80 | DIGITAL | IOD_PTO_disk | D208 | [8 empty] | 0x5340ce20
PTO_PMM_1_Faza2_Tok41_med60in80 | DIGITAL | IOD_PTO_disk | D209 | [8 empty] | 0x5340ce30
PTO_PMM_1_Faza2_Tok42_med60in80 | DIGITAL | IOD_PTO_disk | D210 | [8 empty] | 0x5340ce40
PTO_PMM_1_Faza3_Tok01_med60in80 | DIGITAL | IOD_PTO_disk | D211 | [8 empty] | 0x5340ce50
PTO_PMM_1_Faza3_Tok02_med60in80 | DIGITAL | IOD_PTO_disk | D212 | [8 empty] | 0x5340ce60
PTO_PMM_1_Faza3_Tok03_med60in80 | DIGITAL | IOD_PTO_disk | D213 | [8 empty] | 0x5340ce70
PTO_PMM_1_Faza3_Tok04_med60in80 | DIGITAL | IOD_PTO_disk | D214 | [8 empty] | 0x5340ce80
PTO_PMM_1_Faza3_Tok05_med60in80 | DIGITAL | IOD_PTO_disk | D215 | [8 empty] | 0x5340ce90
PTO_PMM_1_Faza3_Tok06_med60in80 | DIGITAL | IOD_PTO_disk | D216 | [8 empty] | 0x5340cea0
PTO_PMM_1_Faza3_Tok07_med60in80 | DIGITAL | IOD_PTO_disk | D217 | [8 empty] | 0x5340ceb0
PTO_PMM_1_Faza3_Tok08_med60in80 | DIGITAL | IOD_PTO_disk | D218 | [8 empty] | 0x5340cec0
PTO_PMM_1_Faza3_Tok09_med60in80 | DIGITAL | IOD_PTO_disk | D219 | [8 empty] | 0x5340ced0
PTO_PMM_1_Faza3_Tok10_med60in80 | DIGITAL | IOD_PTO_disk | D220 | [8 empty] | 0x5340cee0
PTO_PMM_1_Faza3_Tok11_med60in80 | DIGITAL | IOD_PTO_disk | D221 | [8 empty] | 0x5340cef0
PTO_PMM_1_Faza3_Tok12_med60in80 | DIGITAL | IOD_PTO_disk | D222 | [8 empty] | 0x5340cf00
PTO_PMM_1_Faza3_Tok13_med60in80 | DIGITAL | IOD_PTO_disk | D223 | [8 empty] | 0x5340cf10
PTO_PMM_1_Faza3_Tok14_med60in80 | DIGITAL | IOD_PTO_disk | D224 | [8 empty] | 0x5340cf20
PTO_PMM_1_Faza3_Tok15_med60in80 | DIGITAL | IOD_PTO_disk | D225 | [8 empty] | 0x5340cf30
PTO_PMM_1_Faza3_Tok16_med60in80 | DIGITAL | IOD_PTO_disk | D226 | [8 empty] | 0x5340cf40
PTO_PMM_1_Faza3_Tok17_med60in80 | DIGITAL | IOD_PTO_disk | D227 | [8 empty] | 0x5340cf50
PTO_PMM_1_Faza3_Tok18_med60in80 | DIGITAL | IOD_PTO_disk | D228 | [8 empty] | 0x5340cf60
PTO_PMM_1_Faza3_Tok19_med60in80 | DIGITAL | IOD_PTO_disk | D229 | [8 empty] | 0x5340cf70
PTO_PMM_1_Faza3_Tok20_med60in80 | DIGITAL | IOD_PTO_disk | D230 | [8 empty] | 0x5340cf80
PTO_PMM_1_Faza3_Tok21_med60in80 | DIGITAL | IOD_PTO_disk | D231 | [8 empty] | 0x5340cf90
PTO_PMM_1_Faza3_Tok22_med60in80 | DIGITAL | IOD_PTO_disk | D232 | [8 empty] | 0x5340cfa0
PTO_PMM_1_Faza3_Tok23_med60in80 | DIGITAL | IOD_PTO_disk | D233 | [8 empty] | 0x5340cfb0
PTO_PMM_1_Faza3_Tok24_med60in80 | DIGITAL | IOD_PTO_disk | D234 | [8 empty] | 0x5340cfc0
PTO_PMM_1_Faza3_Tok25_med60in80 | DIGITAL | IOD_PTO_disk | D235 | [8 empty] | 0x5340cfd0
PTO_PMM_1_Faza3_Tok26_med60in80 | DIGITAL | IOD_PTO_disk | D236 | [8 empty] | 0x5340cfe0
PTO_PMM_1_Faza3_Tok27_med60in80 | DIGITAL | IOD_PTO_disk | D237 | [8 empty] | 0x5340cff0
PTO_PMM_1_Faza3_Tok28_med60in80 | DIGITAL | IOD_PTO_disk | D238 | [8 empty] | 0x5340d000
PTO_PMM_1_Faza3_Tok29_med60in80 | DIGITAL | IOD_PTO_disk | D239 | [8 empty] | 0x5340d010
PTO_PMM_1_Faza3_Tok30_med60in80 | DIGITAL | IOD_PTO_disk | D240 | [8 empty] | 0x5340d020
PTO_PMM_1_Faza3_Tok31_med60in80 | DIGITAL | IOD_PTO_disk | D241 | [8 empty] | 0x5340d030
PTO_PMM_1_Faza3_Tok32_med60in80 | DIGITAL | IOD_PTO_disk | D242 | [8 empty] | 0x5340d040
PTO_PMM_1_Faza3_Tok33_med60in80 | DIGITAL | IOD_PTO_disk | D243 | [8 empty] | 0x5340d050
PTO_PMM_1_Faza3_Tok34_med60in80 | DIGITAL | IOD_PTO_disk | D244 | [8 empty] | 0x5340d060
PTO_PMM_1_Faza3_Tok35_med60in80 | DIGITAL | IOD_PTO_disk | D245 | [8 empty] | 0x5340d070
PTO_PMM_1_Faza3_Tok36_med60in80 | DIGITAL | IOD_PTO_disk | D246 | [8 empty] | 0x5340d080
PTO_PMM_1_Faza3_Tok37_med60in80 | DIGITAL | IOD_PTO_disk | D247 | [8 empty] | 0x5340d090
PTO_PMM_1_Faza3_Tok38_med60in80 | DIGITAL | IOD_PTO_disk | D248 | [8 empty] | 0x5340d0a0
PTO_PMM_1_Faza3_Tok39_med60in80 | DIGITAL | IOD_PTO_disk | D249 | [8 empty] | 0x5340d0b0
PTO_PMM_1_Faza3_Tok40_med60in80 | DIGITAL | IOD_PTO_disk | D250 | [8 empty] | 0x5340d0c0
PTO_PMM_1_Faza3_Tok41_med60in80 | DIGITAL | IOD_PTO_disk | D251 | [8 empty] | 0x5340d0d0
PTO_PMM_1_Faza3_Tok42_med60in80 | DIGITAL | IOD_PTO_disk | D252 | [8 empty] | 0x5340d0e0
PTO_Polje_1Faza1_Tok01_16_nad80 | DIGITAL | IOD_PTO_disk | D2000[16] | [8 empty] | 0x5340d0f0
PTO_Polje_1Faza1_Tok17_32_nad80 | DIGITAL | IOD_PTO_disk | D2016[16] | [8 empty] | 0x5340d100
PTO_Polje_1Faza1_Tok33_42_nad80 | DIGITAL | IOD_PTO_disk | D2032[16] | [8 empty] | 0x5340d110
PTO_Polje_1Faza2_Tok01_16_nad80 | DIGITAL | IOD_PTO_disk | D2048[16] | [8 empty] | 0x5340d120
PTO_Polje_1Faza2_Tok17_32_nad80 | DIGITAL | IOD_PTO_disk | D2064[16] | [8 empty] | 0x5340d130
PTO_Polje_1Faza2_Tok33_42_nad80 | DIGITAL | IOD_PTO_disk | D2080[16] | [8 empty] | 0x5340d140
PTO_Polje_1Faza3_Tok01_16_nad80 | DIGITAL | IOD_PTO_disk | D2096[16] | [8 empty] | 0x5340d150
PTO_Polje_1Faza3_Tok17_32_nad80 | DIGITAL | IOD_PTO_disk | D2112[16] | [8 empty] | 0x5340d160
PTO_Polje_1Faza3_Tok33_42_nad80 | DIGITAL | IOD_PTO_disk | D2128[16] | [8 empty] | 0x5340d170
PTO_Polje_1Faza1_Tok01_16_med60_80 | DIGITAL | IOD_PTO_disk | D2320[16] | [8 empty] | 0x5340d180
PTO_Polje_1Faza1_Tok17_32_med60_80 | DIGITAL | IOD_PTO_disk | D2336[16] | [8 empty] | 0x5340d190
PTO_Polje_1Faza1_Tok33_42_med60_80 | DIGITAL | IOD_PTO_disk | D2352[16] | [8 empty] | 0x5340d1a0
PTO_Polje_1Faza2_Tok01_16_med60_80 | DIGITAL | IOD_PTO_disk | D2368[16] | [8 empty] | 0x5340d1b0
PTO_Polje_1Faza2_Tok17_32_med60_80 | DIGITAL | IOD_PTO_disk | D2384[16] | [8 empty] | 0x5340d1c0
PTO_Polje_1Faza2_Tok33_42_med60_80 | DIGITAL | IOD_PTO_disk | D2400[16] | [8 empty] | 0x5340d1d0
PTO_Polje_1Faza3_Tok01_16_med60_80 | DIGITAL | IOD_PTO_disk | D2416[16] | [8 empty] | 0x5340d1e0
PTO_Polje_1Faza3_Tok17_32_med60_80 | DIGITAL | IOD_PTO_disk | D2432[16] | [8 empty] | 0x5340d1f0
PTO_Polje_1Faza3_Tok33_42_med60_80 | DIGITAL | IOD_PTO_disk | D2448[16] | [8 empty] | 0x5340d200
PTO_PrviZagon | DIGITAL | IOD_PTO_disk | D3001 | [8 empty] | 0x5340d210
PTO_ComSCADA_stevec1 | INT | IOD_PTO_disk | I1 | [8 empty] | 0x5340d220
PTO_ComSCADA_stevec2 | INT | IOD_PTO_disk | I2 | [8 empty] | 0x5340d221
PTOErrCommScada_omogoci | DIGITAL | IOD_PTO_disk | D3010 | [8 empty] | 0x5340d230
PTOErrComPanelPLC_omogoci | DIGITAL | IOD_PTO_disk | D3011 | [8 empty] | 0x5340d240
PTOErrComPort2_omogoci | DIGITAL | IOD_PTO_disk | D3012 | [8 empty] | 0x5340d250
PTOErrComPort3_omogoci | DIGITAL | IOD_PTO_disk | D3013 | [8 empty] | 0x5340d260
PTOErrComPort4_omogoci | DIGITAL | IOD_PTO_disk | D3014 | [8 empty] | 0x5340d270
PTOErrComUPS1_omogoci | DIGITAL | IOD_PTO_disk | D3015 | [8 empty] | 0x5340d280
PTOErrComUPS2_omogoci | DIGITAL | IOD_PTO_disk | D3016 | [8 empty] | 0x5340d290
PTOErrComPMM1_omogoci | DIGITAL | IOD_PTO_disk | D3017 | [8 empty] | 0x5340d2a0
PTOErrComCirc1_omogoci | DIGITAL | IOD_PTO_disk | D3018 | [8 empty] | 0x5340d2b0
PTOErrComKlima1_omogoci | DIGITAL | IOD_PTO_disk | D3019 | [8 empty] | 0x5340d2c0
PTOErrComKlima2_omogoci | DIGITAL | IOD_PTO_disk | D3020 | [8 empty] | 0x5340d2d0
PTOErrComKlima3_omogoci | DIGITAL | IOD_PTO_disk | D3021 | [8 empty] | 0x5340d2e0
PTOErrComKlima4_omogoci | DIGITAL | IOD_PTO_disk | D3022 | [8 empty] | 0x5340d2f0
PTOErrComKlima5_omogoci | DIGITAL | IOD_PTO_disk | D3023 | [8 empty] | 0x5340d300
PTOErrComKlima6_omogoci | DIGITAL | IOD_PTO_disk | D3024 | [8 empty] | 0x5340d310
PTOPMMOverCurrentBetw1_omogoci | DIGITAL | IOD_PTO_disk | D3025 | [8 empty] | 0x5340d320
PTOPMMOverCurrentBetw2_omogoci | DIGITAL | IOD_PTO_disk | D3026 | [8 empty] | 0x5340d330
PTOPMMOverCurrentBetw3_omogoci | DIGITAL | IOD_PTO_disk | D3027 | [8 empty] | 0x5340d340
PTOPMMOverCurrentOver1_omogoci | DIGITAL | IOD_PTO_disk | D3028 | [8 empty] | 0x5340d350
PTOPMMOverCurrentOver2_omogoci | DIGITAL | IOD_PTO_disk | D3029 | [8 empty] | 0x5340d360
PTOPMMOverCurrentOver3_omogoci | DIGITAL | IOD_PTO_disk | D3030 | [8 empty] | 0x5340d370
PTOUPS2AlarmSlabaBaterija_omogoci | DIGITAL | IOD_PTO_disk | D3031 | [8 empty] | 0x5340d380
PTOUPS2AlarmOnBattery_omogoci | DIGITAL | IOD_PTO_disk | D3032 | [8 empty] | 0x5340d390
PTOUPS2AlarmLowBattery_omogoci | DIGITAL | IOD_PTO_disk | D3033 | [8 empty] | 0x5340d3a0
PTOUPS2AlarmDepletedBattery_omogoci | DIGITAL | IOD_PTO_disk | D3034 | [8 empty] | 0x5340d3b0
PTOUPS2AlarmTemperaturaIzvenTo_omogoci | DIGITAL | IOD_PTO_disk | D3035 | [8 empty] | 0x5340d3c0
PTOUPS2AlarmStanjeVhodaIzvenTo_omogoci | DIGITAL | IOD_PTO_disk | D3036 | [8 empty] | 0x5340d3d0
PTOUPS2AlarmStanjeIzhodaIzvenTo_omogoci | DIGITAL | IOD_PTO_disk | D3037 | [8 empty] | 0x5340d3e0
PTOUPS2AlarmIzhodPreobremenjen_omogoci | DIGITAL | IOD_PTO_disk | D3038 | [8 empty] | 0x5340d3f0
PTOUPS2AlarmOnBypass_omogoci | DIGITAL | IOD_PTO_disk | D3039 | [8 empty] | 0x5340d400
PTOUPS2AlarmBypassBad_omogoci | DIGITAL | IOD_PTO_disk | D3040 | [8 empty] | 0x5340d410
PTOUPS2AlarmIzhodOffKotZahteva_omogoci | DIGITAL | IOD_PTO_disk | D3041 | [8 empty] | 0x5340d420
PTOUPS2AlarmUPSOffKotZahtevano_omogoci | DIGITAL | IOD_PTO_disk | D3042 | [8 empty] | 0x5340d430
PTOUPS2AlarmChargerFailed_omogoci | DIGITAL | IOD_PTO_disk | D3043 | [8 empty] | 0x5340d440
PTOUPS2AlarmUPSIzhodOff_omogoci | DIGITAL | IOD_PTO_disk | D3044 | [8 empty] | 0x5340d450
PTOUPS2AlarmUPSSystemOff_omogoci | DIGITAL | IOD_PTO_disk | D3045 | [8 empty] | 0x5340d460
PTOUPS2AlarmNapakaNaVentilator_omogoci | DIGITAL | IOD_PTO_disk | D3046 | [8 empty] | 0x5340d470
PTOUPS2AlarmNapakaNaVarovalki_omogoci | DIGITAL | IOD_PTO_disk | D3047 | [8 empty] | 0x5340d480
PTOUPS2AlarmSplosnaNapaka_omogoci | DIGITAL | IOD_PTO_disk | D3048 | [8 empty] | 0x5340d490
PTOUPS2AlarmDiagnosticTestFail_omogoci | DIGITAL | IOD_PTO_disk | D3049 | [8 empty] | 0x5340d4a0
PTOUPS2AlarmCommunicationsLost_omogoci | DIGITAL | IOD_PTO_disk | D3050 | [8 empty] | 0x5340d4b0
PTOUPS2AlarmAwaitingPower_omogoci | DIGITAL | IOD_PTO_disk | D3051 | [8 empty] | 0x5340d4c0
PTOUPS2AlarmShutdownPending_omogoci | DIGITAL | IOD_PTO_disk | D3052 | [8 empty] | 0x5340d4d0
PTOUPS2AlarmShutdownImminent_omogoci | DIGITAL | IOD_PTO_disk | D3053 | [8 empty] | 0x5340d4e0
PTOUPS2AlarmTestInProgres_omogoci | DIGITAL | IOD_PTO_disk | D3054 | [8 empty] | 0x5340d4f0
PTOUPS2AlarmReceptacleOff_omogoci | DIGITAL | IOD_PTO_disk | D3055 | [8 empty] | 0x5340d500
PTOUPS1AlarmSlabaBaterija_omogoci | DIGITAL | IOD_PTO_disk | D3056 | [8 empty] | 0x5340d510
PTOUPS1AlarmOnBattery_omogoci | DIGITAL | IOD_PTO_disk | D3057 | [8 empty] | 0x5340d520
PTOUPS1AlarmLowBattery_omogoci | DIGITAL | IOD_PTO_disk | D3058 | [8 empty] | 0x5340d530
PTOUPS1AlarmDepletedBattery_omogoci | DIGITAL | IOD_PTO_disk | D3059 | [8 empty] | 0x5340d540
PTOUPS1AlarmTemperaturaIzvenTo_omogoci | DIGITAL | IOD_PTO_disk | D3060 | [8 empty] | 0x5340d550
PTOUPS1AlarmStanjeVhodaIzvenTo_omogoci | DIGITAL | IOD_PTO_disk | D3061 | [8 empty] | 0x5340d560
PTOUPS1AlarmStanjeIzhodaIizvenTo_omogoci | DIGITAL | IOD_PTO_disk | D3062 | [8 empty] | 0x5340d570
PTOUPS1AlarmIzhodPreobremenjen_omogoci | DIGITAL | IOD_PTO_disk | D3063 | [8 empty] | 0x5340d580
PTOUPS1AlarmOnBypass_omogoci | DIGITAL | IOD_PTO_disk | D3064 | [8 empty] | 0x5340d590
PTOUPS1AlarmBypassBad_omogoci | DIGITAL | IOD_PTO_disk | D3065 | [8 empty] | 0x5340d5a0
PTOUPS1AlarmIzhodOffKotZahteva_omogoci | DIGITAL | IOD_PTO_disk | D3066 | [8 empty] | 0x5340d5b0
PTOUPS1AlarmUPSOffKotZahtevano_omogoci | DIGITAL | IOD_PTO_disk | D3067 | [8 empty] | 0x5340d5c0
PTOUPS1AlarmChargerFailed_omogoci | DIGITAL | IOD_PTO_disk | D3068 | [8 empty] | 0x5340d5d0
PTOUPS1AlarmUPSIzhodOff_omogoci | DIGITAL | IOD_PTO_disk | D3069 | [8 empty] | 0x5340d5e0
PTOUPS1AlarmUPSSystemOff_omogoci | DIGITAL | IOD_PTO_disk | D3070 | [8 empty] | 0x5340d5f0
PTOUPS1AlarmNapakaNaVentilator_omogoci | DIGITAL | IOD_PTO_disk | D3071 | [8 empty] | 0x5340d600
PTOUPS1AlarmNapakaNaVarovalki_omogoci | DIGITAL | IOD_PTO_disk | D3072 | [8 empty] | 0x5340d610
PTOUPS1AlarmSplosnaNapaka_omogoci | DIGITAL | IOD_PTO_disk | D3073 | [8 empty] | 0x5340d620
PTOUPS1AlarmDiagnosticTestFail_omogoci | DIGITAL | IOD_PTO_disk | D3074 | [8 empty] | 0x5340d630
PTOUPS1AlarmCommunicationsLost_omogoci | DIGITAL | IOD_PTO_disk | D3075 | [8 empty] | 0x5340d640
PTOUPS1AlarmAwaitingPower_omogoci | DIGITAL | IOD_PTO_disk | D3076 | [8 empty] | 0x5340d650
PTOUPS1AlarmShutdownPending_omogoci | DIGITAL | IOD_PTO_disk | D3077 | [8 empty] | 0x5340d660
PTOUPS1AlarmShutdownImminent_omogoci | DIGITAL | IOD_PTO_disk | D3078 | [8 empty] | 0x5340d670
PTOUPS1AlarmTestInProgres_omogoci | DIGITAL | IOD_PTO_disk | D3079 | [8 empty] | 0x5340d680
PTOUPS1AlarmReceptacleOff_omogoci | DIGITAL | IOD_PTO_disk | D3080 | [8 empty] | 0x5340d690
PTODI_Q2_Rezerva_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3081 | [8 empty] | 0x5340d6a0
PTODI_Q5_OdcKlima1_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3082 | [8 empty] | 0x5340d6b0
PTODI_Q6_OdcKlima2_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3083 | [8 empty] | 0x5340d6c0
PTODI_Q7_OdcKlima3_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3084 | [8 empty] | 0x5340d6d0
PTODI_Q8_OdcKlima4_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3085 | [8 empty] | 0x5340d6e0
PTODI_Q9_OdcKlima5_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3086 | [8 empty] | 0x5340d6f0
PTODI_Q10_OdcKlima6_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3087 | [8 empty] | 0x5340d700
PTODI_Q25_OdcUpsA_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3088 | [8 empty] | 0x5340d710
PTODI_Q26_OdcByA_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3089 | [8 empty] | 0x5340d720
PTODI_Q27_OdcByUpsA_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3090 | [8 empty] | 0x5340d730
PTODI_Q28_OdcUpsB_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3091 | [8 empty] | 0x5340d740
PTODI_Q29_OdcByB_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3092 | [8 empty] | 0x5340d750
PTODI_Q30_OdcByUpsB_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3093 | [8 empty] | 0x5340d760
PTODI_Klima5_ERR_omogoci | DIGITAL | IOD_PTO_disk | D3094 | [8 empty] | 0x5340d770
PTODI_Klima6_ERR_omogoci | DIGITAL | IOD_PTO_disk | D3095 | [8 empty] | 0x5340d780
PTODI_KlimaSplit1_ERR_omogoci | DIGITAL | IOD_PTO_disk | D3096 | [8 empty] | 0x5340d790
PTODI_UpsA_ON_omogoci | DIGITAL | IOD_PTO_disk | D3097 | [8 empty] | 0x5340d7a0
PTODI_UpsA_ERR_omogoci | DIGITAL | IOD_PTO_disk | D3098 | [8 empty] | 0x5340d7b0
PTODI_UpsB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3099 | [8 empty] | 0x5340d7c0
PTODI_UpsB_ERR_omogoci | DIGITAL | IOD_PTO_disk | D3100 | [8 empty] | 0x5340d7d0
PTODI_UPS_Alarm_omogoci | DIGITAL | IOD_PTO_disk | D3101 | [8 empty] | 0x5340d7e0
PTODI_UPS_BatNacin_omogoci | DIGITAL | IOD_PTO_disk | D3102 | [8 empty] | 0x5340d7f0
PTODI_UPS_Polnjenje_omogoci | DIGITAL | IOD_PTO_disk | D3103 | [8 empty] | 0x5340d800
PTODI_RazlitjeVodeK5K6_omogoci | DIGITAL | IOD_PTO_disk | D3104 | [8 empty] | 0x5340d810
PTOSetDateTimeError_omogoci | DIGITAL | IOD_PTO_disk | D3105 | [8 empty] | 0x5340d820
PTOTempTSprevisoka1_omogoci | DIGITAL | IOD_PTO_disk | D3106 | [8 empty] | 0x5340d830
PTONapakaSenzorTemp1_omogoci | DIGITAL | IOD_PTO_disk | D3107 | [8 empty] | 0x5340d840
PTONapakaSenzorVlaga1_omogoci | DIGITAL | IOD_PTO_disk | D3108 | [8 empty] | 0x5340d850
PTOSlabaBaterijaPLC_A1_omogoci | DIGITAL | IOD_PTO_disk | D3109 | [8 empty] | 0x5340d860
PTOKlima1GeneralAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3110 | [8 empty] | 0x5340d870
PTOKlima1AlarmKompresor1omogoci | DIGITAL | IOD_PTO_disk | D3111 | [8 empty] | 0x5340d880
PTOKlima1AlarmKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3112 | [8 empty] | 0x5340d890
PTOKlima1NizekPritiskKompresor1omogoci | DIGITAL | IOD_PTO_disk | D3113 | [8 empty] | 0x5340d8a0
PTOKlima1NizekPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3114 | [8 empty] | 0x5340d8b0
PTOKlima1NapakaPriPretoku_omogoci | DIGITAL | IOD_PTO_disk | D3115 | [8 empty] | 0x5340d8c0
PTOKlima1FenThermalCutout_omogoci | DIGITAL | IOD_PTO_disk | D3116 | [8 empty] | 0x5340d8d0
PTOKlima1ThermalCutoutHeater1omogoci | DIGITAL | IOD_PTO_disk | D3117 | [8 empty] | 0x5340d8e0
PTOKlima1ThermalCutoutHeater2_omogoci | DIGITAL | IOD_PTO_disk | D3118 | [8 empty] | 0x5340d8f0
PTOKlima1PozarniAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3119 | [8 empty] | 0x5340d900
PTOKlima1ZamasenFilter_omogoci | DIGITAL | IOD_PTO_disk | D3120 | [8 empty] | 0x5340d910
PTOKlima1VisokaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3121 | [8 empty] | 0x5340d920
PTOKlima1NizkaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3122 | [8 empty] | 0x5340d930
PTOKlima1VisokaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3123 | [8 empty] | 0x5340d940
PTOKlima1NizkaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3124 | [8 empty] | 0x5340d950
PTOKlima1Kompresor1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3125 | [8 empty] | 0x5340d960
PTOKlima1Kompresor2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3126 | [8 empty] | 0x5340d970
PTOKlima1VentilatorNaMejiObrU_omogoci | DIGITAL | IOD_PTO_disk | D3127 | [8 empty] | 0x5340d980
PTOKlima1VisokaTempPovratneVod_omogoci | DIGITAL | IOD_PTO_disk | D3128 | [8 empty] | 0x5340d990
PTOKlima1NizkaTempPovratneVode_omogoci | DIGITAL | IOD_PTO_disk | D3129 | [8 empty] | 0x5340d9a0
PTOKlima1NapakaSenzorTempPros_omogoci | DIGITAL | IOD_PTO_disk | D3130 | [8 empty] | 0x5340d9b0
PTOKlima1NapakaSenzorTempIzih_omogoci | DIGITAL | IOD_PTO_disk | D3131 | [8 empty] | 0x5340d9c0
PTOKlima1NapakaSenzorPovratVod_omogoci | DIGITAL | IOD_PTO_disk | D3132 | [8 empty] | 0x5340d9d0
PTOKlima1NapakaSenzorZunanjeTe_omogoci | DIGITAL | IOD_PTO_disk | D3133 | [8 empty] | 0x5340d9e0
PTOKlima1NapakaSenzorVlaznosti_omogoci | DIGITAL | IOD_PTO_disk | D3134 | [8 empty] | 0x5340d9f0
PTOKlima1FaultyEPROM_omogoci | DIGITAL | IOD_PTO_disk | D3135 | [8 empty] | 0x5340da00
PTOKlima1StoppedByAlarms_omogoci | DIGITAL | IOD_PTO_disk | D3136 | [8 empty] | 0x5340da10
PTOKlima1VisokTokVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3137 | [8 empty] | 0x5340da20
PTOKlima1NiVodeVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3138 | [8 empty] | 0x5340da30
PTOKlima1NiTokaVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3139 | [8 empty] | 0x5340da40
PTOKlima1RocniIzklop_omogoci | DIGITAL | IOD_PTO_disk | D3140 | [8 empty] | 0x5340da50
PTOKlima2GeneralAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3141 | [8 empty] | 0x5340da60
PTOKlima2AlarmKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3142 | [8 empty] | 0x5340da70
PTOKlima2AlarmKompresor2omogoci | DIGITAL | IOD_PTO_disk | D3143 | [8 empty] | 0x5340da80
PTOKlima2NizekPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3144 | [8 empty] | 0x5340da90
PTOKlima2NizekPritiskKompresor2omogoci | DIGITAL | IOD_PTO_disk | D3145 | [8 empty] | 0x5340daa0
PTOKlima2NapakaPriPretokuZraka_omogoci | DIGITAL | IOD_PTO_disk | D3146 | [8 empty] | 0x5340dab0
PTOKlima2FenThermalCutout_omogoci | DIGITAL | IOD_PTO_disk | D3147 | [8 empty] | 0x5340dac0
PTOKlima2ThermalCutoutHeater1_omogoci | DIGITAL | IOD_PTO_disk | D3148 | [8 empty] | 0x5340dad0
PTOKlima2ThermalCutoutHeater2_omogoci | DIGITAL | IOD_PTO_disk | D3149 | [8 empty] | 0x5340dae0
PTOKlima2PozarniAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3150 | [8 empty] | 0x5340daf0
PTOKlima2ZamasenFilter_omogoci | DIGITAL | IOD_PTO_disk | D3151 | [8 empty] | 0x5340db00
PTOKlima2VisokaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3152 | [8 empty] | 0x5340db10
PTOKlima2NizkaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3153 | [8 empty] | 0x5340db20
PTOKlima2VisokaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3154 | [8 empty] | 0x5340db30
PTOKlima2NizkaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3155 | [8 empty] | 0x5340db40
PTOKlima2Kompresor1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3156 | [8 empty] | 0x5340db50
PTOKlima2Kompresor2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3157 | [8 empty] | 0x5340db60
PTOKlima2VentilatorNaMejiObrU_omogoci | DIGITAL | IOD_PTO_disk | D3158 | [8 empty] | 0x5340db70
PTOKlima2VisokaTempPovratneVod_omogoci | DIGITAL | IOD_PTO_disk | D3159 | [8 empty] | 0x5340db80
PTOKlima2NizkaTempPovratneVode_omogoci | DIGITAL | IOD_PTO_disk | D3160 | [8 empty] | 0x5340db90
PTOKlima2NapakaSenzorTempPros_omogoci | DIGITAL | IOD_PTO_disk | D3161 | [8 empty] | 0x5340dba0
PTOKlima2NapakaSenzorPovratVod_omogoci | DIGITAL | IOD_PTO_disk | D3162 | [8 empty] | 0x5340dbb0
PTOKlima2NapakaSenzorZunanjeTe_omogoci | DIGITAL | IOD_PTO_disk | D3163 | [8 empty] | 0x5340dbc0
PTOKlima2NapakaSenzorTempIzpih_omogoci | DIGITAL | IOD_PTO_disk | D3164 | [8 empty] | 0x5340dbd0
PTOKlima2NapakaSenzorVlaznosti_omogoci | DIGITAL | IOD_PTO_disk | D3165 | [8 empty] | 0x5340dbe0
PTOKlima2FaultyEPROM_omogoci | DIGITAL | IOD_PTO_disk | D3166 | [8 empty] | 0x5340dbf0
PTOKlima2StoppedByAlarms_omogoci | DIGITAL | IOD_PTO_disk | D3167 | [8 empty] | 0x5340dc00
PTOKlima2VisokTokVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3168 | [8 empty] | 0x5340dc10
PTOKlima2NiVodeVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3169 | [8 empty] | 0x5340dc20
PTOKlima2NiTokaVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3170 | [8 empty] | 0x5340dc30
PTOKlima2RocniIzklop_omogoci | DIGITAL | IOD_PTO_disk | D3171 | [8 empty] | 0x5340dc40
PTOKlima3GeneralAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3172 | [8 empty] | 0x5340dc50
PTOKlima3AlarmKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3173 | [8 empty] | 0x5340dc60
PTOKlima3AlarmKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3174 | [8 empty] | 0x5340dc70
PTOKlima3NizekPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3175 | [8 empty] | 0x5340dc80
PTOKlima3NizekPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3176 | [8 empty] | 0x5340dc90
PTOKlima3NapakaPriPretoku_omogoci | DIGITAL | IOD_PTO_disk | D3177 | [8 empty] | 0x5340dca0
PTOKlima3FenThermalCutout_omogoci | DIGITAL | IOD_PTO_disk | D3178 | [8 empty] | 0x5340dcb0
PTOKlima3ThermalCutoutHeater1_omogoci | DIGITAL | IOD_PTO_disk | D3179 | [8 empty] | 0x5340dcc0
PTOKlima3ThermalCutoutHeater2_omogoci | DIGITAL | IOD_PTO_disk | D3180 | [8 empty] | 0x5340dcd0
PTOKlima3PozarniAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3181 | [8 empty] | 0x5340dce0
PTOKlima3ZamasenFilter_omogoci | DIGITAL | IOD_PTO_disk | D3182 | [8 empty] | 0x5340dcf0
PTOKlima3VisokaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3183 | [8 empty] | 0x5340dd00
PTOKlima3NizkaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3184 | [8 empty] | 0x5340dd10
PTOKlima3VisokaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3185 | [8 empty] | 0x5340dd20
PTOKlima3NizkaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3186 | [8 empty] | 0x5340dd30
PTOKlima3Kompresor1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3187 | [8 empty] | 0x5340dd40
PTOKlima3Kompresor2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3188 | [8 empty] | 0x5340dd50
PTOKlima3VentilatorNaMejiObrU_omogoci | DIGITAL | IOD_PTO_disk | D3189 | [8 empty] | 0x5340dd60
PTOKlima3VisokaTempPovratneVod_omogoci | DIGITAL | IOD_PTO_disk | D3190 | [8 empty] | 0x5340dd70
PTOKlima3NizkaTempPovratneVode_omogoci | DIGITAL | IOD_PTO_disk | D3191 | [8 empty] | 0x5340dd80
PTOKlima3NapakaSenzorTempPros_omogoci | DIGITAL | IOD_PTO_disk | D3192 | [8 empty] | 0x5340dd90
PTOKlima3NapakaSenzorTempIzih_omogoci | DIGITAL | IOD_PTO_disk | D3193 | [8 empty] | 0x5340dda0
PTOKlima3NapakaSenzorPovratVod_omogoci | DIGITAL | IOD_PTO_disk | D3194 | [8 empty] | 0x5340ddb0
PTOKlima3NapakaSenzorZunanjeTe_omogoci | DIGITAL | IOD_PTO_disk | D3195 | [8 empty] | 0x5340ddc0
PTOKlima3NapakaSenzorVlaznosti_omogoci | DIGITAL | IOD_PTO_disk | D3196 | [8 empty] | 0x5340ddd0
PTOKlima3FaultyEPROM_omogoci | DIGITAL | IOD_PTO_disk | D3197 | [8 empty] | 0x5340dde0
PTOKlima3StoppedByAlarms_omogoci | DIGITAL | IOD_PTO_disk | D3198 | [8 empty] | 0x5340ddf0
PTOKlima3VisokTokVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3199 | [8 empty] | 0x5340de00
PTOKlima3NiVodeVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3200 | [8 empty] | 0x5340de10
PTOKlima3NiTokaVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3201 | [8 empty] | 0x5340de20
PTOKlima3RocniIzklop_omogoci | DIGITAL | IOD_PTO_disk | D3202 | [8 empty] | 0x5340de30
PTOKlima4GeneralAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3203 | [8 empty] | 0x5340de40
PTOKlima4AlarmKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3204 | [8 empty] | 0x5340de50
PTOKlima4AlarmKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3205 | [8 empty] | 0x5340de60
PTOKlima4NizekPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3206 | [8 empty] | 0x5340de70
PTOKlima4NizekPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3207 | [8 empty] | 0x5340de80
PTOKlima4NapakaPriPretoku_omogoci | DIGITAL | IOD_PTO_disk | D3208 | [8 empty] | 0x5340de90
PTOKlima4FenThermalCutout_omogoci | DIGITAL | IOD_PTO_disk | D3209 | [8 empty] | 0x5340dea0
PTOKlima4ThermalCutoutHeater1_omogoci | DIGITAL | IOD_PTO_disk | D3210 | [8 empty] | 0x5340deb0
PTOKlima4ThermalCutoutHeater2_omogoci | DIGITAL | IOD_PTO_disk | D3211 | [8 empty] | 0x5340dec0
PTOKlima4PozarniAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3212 | [8 empty] | 0x5340ded0
PTOKlima4ZamasenFilter_omogoci | DIGITAL | IOD_PTO_disk | D3213 | [8 empty] | 0x5340dee0
PTOKlima4VisokaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3214 | [8 empty] | 0x5340def0
PTOKlima4NizkaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3215 | [8 empty] | 0x5340df00
PTOKlima4VisokaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3216 | [8 empty] | 0x5340df10
PTOKlima4NizkaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3217 | [8 empty] | 0x5340df20
PTOKlima4Kompresor1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3218 | [8 empty] | 0x5340df30
PTOKlima4Kompresor2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3219 | [8 empty] | 0x5340df40
PTOKlima4VentilatorNaMejiObrU_omogoci | DIGITAL | IOD_PTO_disk | D3220 | [8 empty] | 0x5340df50
PTOKlima4VisokaTempPovratneVod_omogoci | DIGITAL | IOD_PTO_disk | D3221 | [8 empty] | 0x5340df60
PTOKlima4NizkaTempPovratneVode_omogoci | DIGITAL | IOD_PTO_disk | D3222 | [8 empty] | 0x5340df70
PTOKlima4NapakaSenzorTempPros_omogoci | DIGITAL | IOD_PTO_disk | D3223 | [8 empty] | 0x5340df80
PTOKlima4NapakaSenzorTempIzih_omogoci | DIGITAL | IOD_PTO_disk | D3224 | [8 empty] | 0x5340df90
PTOKlima4NapakaSenzorPovratVod_omogoci | DIGITAL | IOD_PTO_disk | D3225 | [8 empty] | 0x5340dfa0
PTOKlima4NapakaSenzorZunanjeTe_omogoci | DIGITAL | IOD_PTO_disk | D3226 | [8 empty] | 0x5340dfb0
PTOKlima4NapakaSenzorVlaznosti_omogoci | DIGITAL | IOD_PTO_disk | D3227 | [8 empty] | 0x5340dfc0
PTOKlima4FaultyEPROM_omogoci | DIGITAL | IOD_PTO_disk | D3228 | [8 empty] | 0x5340dfd0
PTOKlima4StoppedByAlarms_omogoci | DIGITAL | IOD_PTO_disk | D3229 | [8 empty] | 0x5340dfe0
PTOKlima4VisokTokVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3230 | [8 empty] | 0x5340dff0
PTOKlima4NiVodeVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3231 | [8 empty] | 0x5340e000
PTOKlima4NiTokaVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3232 | [8 empty] | 0x5340e010
PTOKlima4RocniIzklop_omogoci | DIGITAL | IOD_PTO_disk | D3233 | [8 empty] | 0x5340e020
PTOKlima5GeneralAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3234 | [8 empty] | 0x5340e030
PTOKlima5AlarmKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3235 | [8 empty] | 0x5340e040
PTOKlima5AlarmKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3236 | [8 empty] | 0x5340e050
PTOKlima5NizekPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3237 | [8 empty] | 0x5340e060
PTOKlima5NizekPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3238 | [8 empty] | 0x5340e070
PTOKlima5NapakaPriPretoku_omogoci | DIGITAL | IOD_PTO_disk | D3239 | [8 empty] | 0x5340e080
PTOKlima5FenThermalCutout_omogoci | DIGITAL | IOD_PTO_disk | D3240 | [8 empty] | 0x5340e090
PTOKlima5ThermalCutoutHeater1_omogoci | DIGITAL | IOD_PTO_disk | D3241 | [8 empty] | 0x5340e0a0
PTOKlima5ThermalCutoutHeater2_omogoci | DIGITAL | IOD_PTO_disk | D3242 | [8 empty] | 0x5340e0b0
PTOKlima5PozarniAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3243 | [8 empty] | 0x5340e0c0
PTOKlima5ZamasenFilter_omogoci | DIGITAL | IOD_PTO_disk | D3244 | [8 empty] | 0x5340e0d0
PTOKlima5VisokaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3245 | [8 empty] | 0x5340e0e0
PTOKlima5NizkaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3246 | [8 empty] | 0x5340e0f0
PTOKlima5VisokaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3247 | [8 empty] | 0x5340e100
PTOKlima5NizkaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3248 | [8 empty] | 0x5340e110
PTOKlima5Kompresor1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3249 | [8 empty] | 0x5340e120
PTOKlima5Kompresor2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3250 | [8 empty] | 0x5340e130
PTOKlima5VentilatorNaMejiObrU_omogoci | DIGITAL | IOD_PTO_disk | D3251 | [8 empty] | 0x5340e140
PTOKlima5VisokaTempPovratneVod_omogoci | DIGITAL | IOD_PTO_disk | D3252 | [8 empty] | 0x5340e150
PTOKlima5NizkaTempPovratneVode_omogoci | DIGITAL | IOD_PTO_disk | D3253 | [8 empty] | 0x5340e160
PTOKlima5NapakaSenzorTempPros_omogoci | DIGITAL | IOD_PTO_disk | D3254 | [8 empty] | 0x5340e170
PTOKlima5NapakaSenzorTempIzih_omogoci | DIGITAL | IOD_PTO_disk | D3255 | [8 empty] | 0x5340e180
PTOKlima5NapakaSenzorPovratVod_omogoci | DIGITAL | IOD_PTO_disk | D3256 | [8 empty] | 0x5340e190
PTOKlima5NapakaSenzorZunanjeTe_omogoci | DIGITAL | IOD_PTO_disk | D3257 | [8 empty] | 0x5340e1a0
PTOKlima5NapakaSenzorVlaznosti_omogoci | DIGITAL | IOD_PTO_disk | D3258 | [8 empty] | 0x5340e1b0
PTOKlima5FaultyEPROM_omogoci | DIGITAL | IOD_PTO_disk | D3259 | [8 empty] | 0x5340e1c0
PTOKlima5StoppedByAlarms_omogoci | DIGITAL | IOD_PTO_disk | D3260 | [8 empty] | 0x5340e1d0
PTOKlima5VisokTokVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3261 | [8 empty] | 0x5340e1e0
PTOKlima5NiVodeVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3262 | [8 empty] | 0x5340e1f0
PTOKlima5NiTokaVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3263 | [8 empty] | 0x5340e200
PTOKlima5RocniIzklop_omogoci | DIGITAL | IOD_PTO_disk | D3264 | [8 empty] | 0x5340e210
PTOKlima6GeneralAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3265 | [8 empty] | 0x5340e220
PTOKlima6AlarmKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3266 | [8 empty] | 0x5340e230
PTOKlima6AlarmKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3267 | [8 empty] | 0x5340e240
PTOKlima6NizekPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3268 | [8 empty] | 0x5340e250
PTOKlima6NizekPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3269 | [8 empty] | 0x5340e260
PTOKlima6NapakaPriPretoku_omogoci | DIGITAL | IOD_PTO_disk | D3270 | [8 empty] | 0x5340e270
PTOKlima6FenThermalCutout_omogoci | DIGITAL | IOD_PTO_disk | D3271 | [8 empty] | 0x5340e280
PTOKlima6ThermalCutoutHeater1_omogoci | DIGITAL | IOD_PTO_disk | D3272 | [8 empty] | 0x5340e290
PTOKlima6ThermalCutoutHeater2_omogoci | DIGITAL | IOD_PTO_disk | D3273 | [8 empty] | 0x5340e2a0
PTOKlima6PozarniAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3274 | [8 empty] | 0x5340e2b0
PTOKlima6ZamasenFilter_omogoci | DIGITAL | IOD_PTO_disk | D3275 | [8 empty] | 0x5340e2c0
PTOKlima6VisokaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3276 | [8 empty] | 0x5340e2d0
PTOKlima6NizkaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3277 | [8 empty] | 0x5340e2e0
PTOKlima6VisokaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3278 | [8 empty] | 0x5340e2f0
PTOKlima6NizkaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3279 | [8 empty] | 0x5340e300
PTOKlima6Kompresor1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3280 | [8 empty] | 0x5340e310
PTOKlima6Kompresor2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3281 | [8 empty] | 0x5340e320
PTOKlima6VentilatorNaMejiObrU_omogoci | DIGITAL | IOD_PTO_disk | D3282 | [8 empty] | 0x5340e330
PTOKlima6VisokaTempPovratneVod_omogoci | DIGITAL | IOD_PTO_disk | D3283 | [8 empty] | 0x5340e340
PTOKlima6NizkaTempPovratneVode_omogoci | DIGITAL | IOD_PTO_disk | D3284 | [8 empty] | 0x5340e350
PTOKlima6NapakaSenzorTempPros_omogoci | DIGITAL | IOD_PTO_disk | D3285 | [8 empty] | 0x5340e360
PTOKlima6NapakaSenzorTempIzih_omogoci | DIGITAL | IOD_PTO_disk | D3286 | [8 empty] | 0x5340e370
PTOKlima6NapakaSenzorPovratVod_omogoci | DIGITAL | IOD_PTO_disk | D3287 | [8 empty] | 0x5340e380
PTOKlima6NapakaSenzorZunanjeTe_omogoci | DIGITAL | IOD_PTO_disk | D3288 | [8 empty] | 0x5340e390
PTOKlima6NapakaSenzorVlaznosti_omogoci | DIGITAL | IOD_PTO_disk | D3289 | [8 empty] | 0x5340e3a0
PTOKlima6FaultyEPROM_omogoci | DIGITAL | IOD_PTO_disk | D3290 | [8 empty] | 0x5340e3b0
PTOKlima6StoppedByAlarms_omogoci | DIGITAL | IOD_PTO_disk | D3291 | [8 empty] | 0x5340e3c0
PTOKlima6VisokTokVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3292 | [8 empty] | 0x5340e3d0
PTOKlima6NiVodeVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3293 | [8 empty] | 0x5340e3e0
PTOKlima6NiTokaVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3294 | [8 empty] | 0x5340e3f0
PTOKlima6RocniIzklop_omogoci | DIGITAL | IOD_PTO_disk | D3295 | [8 empty] | 0x5340e400
PTOPMM_Faza1_Tok01_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3100 | [8 empty] | 0x5340e410
PTOPMM_Faza1_Tok02_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3101 | [8 empty] | 0x5340e420
PTOPMM_Faza1_Tok03_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3102 | [8 empty] | 0x5340e430
PTOPMM_Faza1_Tok04_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3103 | [8 empty] | 0x5340e440
PTOPMM_Faza1_Tok05_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3104 | [8 empty] | 0x5340e450
PTOPMM_Faza1_Tok06_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3105 | [8 empty] | 0x5340e460
PTOPMM_Faza1_Tok07_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3106 | [8 empty] | 0x5340e470
PTOPMM_Faza1_Tok08_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3107 | [8 empty] | 0x5340e480
PTOPMM_Faza1_Tok09_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3108 | [8 empty] | 0x5340e490
PTOPMM_Faza1_Tok10_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3109 | [8 empty] | 0x5340e4a0
PTOPMM_Faza1_Tok11_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3110 | [8 empty] | 0x5340e4b0
PTOPMM_Faza1_Tok12_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3111 | [8 empty] | 0x5340e4c0
PTOPMM_Faza1_Tok13_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3112 | [8 empty] | 0x5340e4d0
PTOPMM_Faza1_Tok14_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3113 | [8 empty] | 0x5340e4e0
PTOPMM_Faza1_Tok15_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3114 | [8 empty] | 0x5340e4f0
PTOPMM_Faza1_Tok16_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3115 | [8 empty] | 0x5340e500
PTOPMM_Faza1_Tok17_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3116 | [8 empty] | 0x5340e510
PTOPMM_Faza1_Tok18_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3117 | [8 empty] | 0x5340e520
PTOPMM_Faza1_Tok19_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3118 | [8 empty] | 0x5340e530
PTOPMM_Faza1_Tok20_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3119 | [8 empty] | 0x5340e540
PTOPMM_Faza1_Tok21_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3120 | [8 empty] | 0x5340e550
PTOPMM_Faza1_Tok22_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3121 | [8 empty] | 0x5340e560
PTOPMM_Faza1_Tok23_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3122 | [8 empty] | 0x5340e570
PTOPMM_Faza1_Tok24_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3123 | [8 empty] | 0x5340e580
PTOPMM_Faza1_Tok25_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3124 | [8 empty] | 0x5340e590
PTOPMM_Faza1_Tok26_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3125 | [8 empty] | 0x5340e5a0
PTOPMM_Faza1_Tok27_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3126 | [8 empty] | 0x5340e5b0
PTOPMM_Faza1_Tok28_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3127 | [8 empty] | 0x5340e5c0
PTOPMM_Faza1_Tok29_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3128 | [8 empty] | 0x5340e5d0
PTOPMM_Faza1_Tok30_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3129 | [8 empty] | 0x5340e5e0
PTOPMM_Faza1_Tok31_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3130 | [8 empty] | 0x5340e5f0
PTOPMM_Faza1_Tok32_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3131 | [8 empty] | 0x5340e600
PTOPMM_Faza1_Tok33_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3132 | [8 empty] | 0x5340e610
PTOPMM_Faza1_Tok34_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3133 | [8 empty] | 0x5340e620
PTOPMM_Faza1_Tok35_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3134 | [8 empty] | 0x5340e630
PTOPMM_Faza1_Tok36_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3135 | [8 empty] | 0x5340e640
PTOPMM_Faza1_Tok37_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3136 | [8 empty] | 0x5340e650
PTOPMM_Faza1_Tok38_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3137 | [8 empty] | 0x5340e660
PTOPMM_Faza1_Tok39_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3138 | [8 empty] | 0x5340e670
PTOPMM_Faza1_Tok40_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3139 | [8 empty] | 0x5340e680
PTOPMM_Faza1_Tok41_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3140 | [8 empty] | 0x5340e690
PTOPMM_Faza1_Tok42_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3141 | [8 empty] | 0x5340e6a0
PTOPMM_Faza2_Tok01_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3142 | [8 empty] | 0x5340e6b0
PTOPMM_Faza2_Tok02_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3143 | [8 empty] | 0x5340e6c0
PTOPMM_Faza2_Tok03_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3144 | [8 empty] | 0x5340e6d0
PTOPMM_Faza2_Tok04_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3145 | [8 empty] | 0x5340e6e0
PTOPMM_Faza2_Tok05_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3146 | [8 empty] | 0x5340e6f0
PTOPMM_Faza2_Tok06_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3147 | [8 empty] | 0x5340e700
PTOPMM_Faza2_Tok07_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3148 | [8 empty] | 0x5340e710
PTOPMM_Faza2_Tok08_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3149 | [8 empty] | 0x5340e720
PTOPMM_Faza2_Tok09_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3150 | [8 empty] | 0x5340e730
PTOPMM_Faza2_Tok10_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3151 | [8 empty] | 0x5340e740
PTOPMM_Faza2_Tok11_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3152 | [8 empty] | 0x5340e750
PTOPMM_Faza2_Tok12_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3153 | [8 empty] | 0x5340e760
PTOPMM_Faza2_Tok13_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3154 | [8 empty] | 0x5340e770
PTOPMM_Faza2_Tok14_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3155 | [8 empty] | 0x5340e780
PTOPMM_Faza2_Tok15_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3156 | [8 empty] | 0x5340e790
PTOPMM_Faza2_Tok16_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3157 | [8 empty] | 0x5340e7a0
PTOPMM_Faza2_Tok17_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3158 | [8 empty] | 0x5340e7b0
PTOPMM_Faza2_Tok18_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3159 | [8 empty] | 0x5340e7c0
PTOPMM_Faza2_Tok19_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3160 | [8 empty] | 0x5340e7d0
PTOPMM_Faza2_Tok20_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3161 | [8 empty] | 0x5340e7e0
PTOPMM_Faza2_Tok21_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3162 | [8 empty] | 0x5340e7f0
PTOPMM_Faza2_Tok22_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3163 | [8 empty] | 0x5340e800
PTOPMM_Faza2_Tok23_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3164 | [8 empty] | 0x5340e810
PTOPMM_Faza2_Tok24_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3165 | [8 empty] | 0x5340e820
PTOPMM_Faza2_Tok25_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3166 | [8 empty] | 0x5340e830
PTOPMM_Faza2_Tok26_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3167 | [8 empty] | 0x5340e840
PTOPMM_Faza2_Tok27_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3168 | [8 empty] | 0x5340e850
PTOPMM_Faza2_Tok28_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3169 | [8 empty] | 0x5340e860
PTOPMM_Faza2_Tok29_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3170 | [8 empty] | 0x5340e870
PTOPMM_Faza2_Tok30_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3171 | [8 empty] | 0x5340e880
PTOPMM_Faza2_Tok31_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3172 | [8 empty] | 0x5340e890
PTOPMM_Faza2_Tok32_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3173 | [8 empty] | 0x5340e8a0
PTOPMM_Faza2_Tok33_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3174 | [8 empty] | 0x5340e8b0
PTOPMM_Faza2_Tok34_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3175 | [8 empty] | 0x5340e8c0
PTOPMM_Faza2_Tok35_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3176 | [8 empty] | 0x5340e8d0
PTOPMM_Faza2_Tok36_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3177 | [8 empty] | 0x5340e8e0
PTOPMM_Faza2_Tok37_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3178 | [8 empty] | 0x5340e8f0
PTOPMM_Faza2_Tok38_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3179 | [8 empty] | 0x5340e900
PTOPMM_Faza2_Tok39_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3180 | [8 empty] | 0x5340e910
PTOPMM_Faza2_Tok40_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3181 | [8 empty] | 0x5340e920
PTOPMM_Faza2_Tok41_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3182 | [8 empty] | 0x5340e930
PTOPMM_Faza2_Tok42_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3183 | [8 empty] | 0x5340e940
PTOPMM_Faza3_Tok01_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3184 | [8 empty] | 0x5340e950
PTOPMM_Faza3_Tok02_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3185 | [8 empty] | 0x5340e960
PTOPMM_Faza3_Tok03_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3186 | [8 empty] | 0x5340e970
PTOPMM_Faza3_Tok04_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3187 | [8 empty] | 0x5340e980
PTOPMM_Faza3_Tok05_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3188 | [8 empty] | 0x5340e990
PTOPMM_Faza3_Tok06_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3189 | [8 empty] | 0x5340e9a0
PTOPMM_Faza3_Tok07_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3190 | [8 empty] | 0x5340e9b0
PTOPMM_Faza3_Tok08_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3191 | [8 empty] | 0x5340e9c0
PTOPMM_Faza3_Tok09_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3192 | [8 empty] | 0x5340e9d0
PTOPMM_Faza3_Tok10_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3193 | [8 empty] | 0x5340e9e0
PTOPMM_Faza3_Tok11_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3194 | [8 empty] | 0x5340e9f0
PTOPMM_Faza3_Tok12_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3195 | [8 empty] | 0x5340ea00
PTOPMM_Faza3_Tok13_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3196 | [8 empty] | 0x5340ea10
PTOPMM_Faza3_Tok14_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3197 | [8 empty] | 0x5340ea20
PTOPMM_Faza3_Tok15_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3198 | [8 empty] | 0x5340ea30
PTOPMM_Faza3_Tok16_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3199 | [8 empty] | 0x5340ea40
PTOPMM_Faza3_Tok17_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3200 | [8 empty] | 0x5340ea50
PTOPMM_Faza3_Tok18_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3201 | [8 empty] | 0x5340ea60
PTOPMM_Faza3_Tok19_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3202 | [8 empty] | 0x5340ea70
PTOPMM_Faza3_Tok20_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3203 | [8 empty] | 0x5340ea80
PTOPMM_Faza3_Tok21_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3204 | [8 empty] | 0x5340ea90
PTOPMM_Faza3_Tok22_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3205 | [8 empty] | 0x5340eaa0
PTOPMM_Faza3_Tok23_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3206 | [8 empty] | 0x5340eab0
PTOPMM_Faza3_Tok24_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3207 | [8 empty] | 0x5340eac0
PTOPMM_Faza3_Tok25_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3208 | [8 empty] | 0x5340ead0
PTOPMM_Faza3_Tok26_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3209 | [8 empty] | 0x5340eae0
PTOPMM_Faza3_Tok27_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3210 | [8 empty] | 0x5340eaf0
PTOPMM_Faza3_Tok28_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3211 | [8 empty] | 0x5340eb00
PTOPMM_Faza3_Tok29_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3212 | [8 empty] | 0x5340eb10
PTOPMM_Faza3_Tok30_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3213 | [8 empty] | 0x5340eb20
PTOPMM_Faza3_Tok31_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3214 | [8 empty] | 0x5340eb30
PTOPMM_Faza3_Tok32_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3215 | [8 empty] | 0x5340eb40
PTOPMM_Faza3_Tok33_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3216 | [8 empty] | 0x5340eb50
PTOPMM_Faza3_Tok34_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3217 | [8 empty] | 0x5340eb60
PTOPMM_Faza3_Tok35_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3218 | [8 empty] | 0x5340eb70
PTOPMM_Faza3_Tok36_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3219 | [8 empty] | 0x5340eb80
PTOPMM_Faza3_Tok37_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3220 | [8 empty] | 0x5340eb90
PTOPMM_Faza3_Tok38_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3221 | [8 empty] | 0x5340eba0
PTOPMM_Faza3_Tok39_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3222 | [8 empty] | 0x5340ebb0
PTOPMM_Faza3_Tok40_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3223 | [8 empty] | 0x5340ebc0
PTOPMM_Faza3_Tok41_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3224 | [8 empty] | 0x5340ebd0
PTOPMM_Faza3_Tok42_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3225 | [8 empty] | 0x5340ebe0
PTOPMM_Faza1_Tok01_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3226 | [8 empty] | 0x5340ebf0
PTOPMM_Faza1_Tok02_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3227 | [8 empty] | 0x5340ec00
PTOPMM_Faza1_Tok03_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3228 | [8 empty] | 0x5340ec10
PTOPMM_Faza1_Tok04_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3229 | [8 empty] | 0x5340ec20
PTOPMM_Faza1_Tok05_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3230 | [8 empty] | 0x5340ec30
PTOPMM_Faza1_Tok06_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3231 | [8 empty] | 0x5340ec40
PTOPMM_Faza1_Tok07_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3232 | [8 empty] | 0x5340ec50
PTOPMM_Faza1_Tok08_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3233 | [8 empty] | 0x5340ec60
PTOPMM_Faza1_Tok09_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3234 | [8 empty] | 0x5340ec70
PTOPMM_Faza1_Tok10_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3235 | [8 empty] | 0x5340ec80
PTOPMM_Faza1_Tok11_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3236 | [8 empty] | 0x5340ec90
PTOPMM_Faza1_Tok12_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3237 | [8 empty] | 0x5340eca0
PTOPMM_Faza1_Tok13_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3238 | [8 empty] | 0x5340ecb0
PTOPMM_Faza1_Tok14_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3239 | [8 empty] | 0x5340ecc0
PTOPMM_Faza1_Tok15_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3240 | [8 empty] | 0x5340ecd0
PTOPMM_Faza1_Tok16_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3241 | [8 empty] | 0x5340ece0
PTOPMM_Faza1_Tok17_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3242 | [8 empty] | 0x5340ecf0
PTOPMM_Faza1_Tok18_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3243 | [8 empty] | 0x5340ed00
PTOPMM_Faza1_Tok19_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3244 | [8 empty] | 0x5340ed10
PTOPMM_Faza1_Tok20_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3245 | [8 empty] | 0x5340ed20
PTOPMM_Faza1_Tok21_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3246 | [8 empty] | 0x5340ed30
PTOPMM_Faza1_Tok22_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3247 | [8 empty] | 0x5340ed40
PTOPMM_Faza1_Tok23_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3248 | [8 empty] | 0x5340ed50
PTOPMM_Faza1_Tok24_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3249 | [8 empty] | 0x5340ed60
PTOPMM_Faza1_Tok25_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3250 | [8 empty] | 0x5340ed70
PTOPMM_Faza1_Tok26_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3251 | [8 empty] | 0x5340ed80
PTOPMM_Faza1_Tok27_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3252 | [8 empty] | 0x5340ed90
PTOPMM_Faza1_Tok28_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3253 | [8 empty] | 0x5340eda0
PTOPMM_Faza1_Tok29_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3254 | [8 empty] | 0x5340edb0
PTOPMM_Faza1_Tok30_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3255 | [8 empty] | 0x5340edc0
PTOPMM_Faza1_Tok31_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3256 | [8 empty] | 0x5340edd0
PTOPMM_Faza1_Tok32_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3257 | [8 empty] | 0x5340ede0
PTOPMM_Faza1_Tok33_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3258 | [8 empty] | 0x5340edf0
PTOPMM_Faza1_Tok34_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3259 | [8 empty] | 0x5340ee00
PTOPMM_Faza1_Tok35_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3260 | [8 empty] | 0x5340ee10
PTOPMM_Faza1_Tok36_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3261 | [8 empty] | 0x5340ee20
PTOPMM_Faza1_Tok37_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3262 | [8 empty] | 0x5340ee30
PTOPMM_Faza1_Tok38_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3263 | [8 empty] | 0x5340ee40
PTOPMM_Faza1_Tok39_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3264 | [8 empty] | 0x5340ee50
PTOPMM_Faza1_Tok40_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3265 | [8 empty] | 0x5340ee60
PTOPMM_Faza1_Tok41_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3266 | [8 empty] | 0x5340ee70
PTOPMM_Faza1_Tok42_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3267 | [8 empty] | 0x5340ee80
PTOPMM_Faza2_Tok01_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3268 | [8 empty] | 0x5340ee90
PTOPMM_Faza2_Tok02_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3269 | [8 empty] | 0x5340eea0
PTOPMM_Faza2_Tok03_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3270 | [8 empty] | 0x5340eeb0
PTOPMM_Faza2_Tok04_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3271 | [8 empty] | 0x5340eec0
PTOPMM_Faza2_Tok05_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3272 | [8 empty] | 0x5340eed0
PTOPMM_Faza2_Tok06_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3273 | [8 empty] | 0x5340eee0
PTOPMM_Faza2_Tok07_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3274 | [8 empty] | 0x5340eef0
PTOPMM_Faza2_Tok08_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3275 | [8 empty] | 0x5340ef00
PTOPMM_Faza2_Tok09_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3276 | [8 empty] | 0x5340ef10
PTOPMM_Faza2_Tok10_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3277 | [8 empty] | 0x5340ef20
PTOPMM_Faza2_Tok11_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3278 | [8 empty] | 0x5340ef30
PTOPMM_Faza2_Tok12_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3279 | [8 empty] | 0x5340ef40
PTOPMM_Faza2_Tok13_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3280 | [8 empty] | 0x5340ef50
PTOPMM_Faza2_Tok14_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3281 | [8 empty] | 0x5340ef60
PTOPMM_Faza2_Tok15_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3282 | [8 empty] | 0x5340ef70
PTOPMM_Faza2_Tok16_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3283 | [8 empty] | 0x5340ef80
PTOPMM_Faza2_Tok17_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3284 | [8 empty] | 0x5340ef90
PTOPMM_Faza2_Tok18_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3285 | [8 empty] | 0x5340efa0
PTOPMM_Faza2_Tok19_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3286 | [8 empty] | 0x5340efb0
PTOPMM_Faza2_Tok20_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3287 | [8 empty] | 0x5340efc0
PTOPMM_Faza2_Tok21_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3288 | [8 empty] | 0x5340efd0
PTOPMM_Faza2_Tok22_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3289 | [8 empty] | 0x5340efe0
PTOPMM_Faza2_Tok23_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3290 | [8 empty] | 0x5340eff0
PTOPMM_Faza2_Tok24_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3291 | [8 empty] | 0x5340f000
PTOPMM_Faza2_Tok25_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3292 | [8 empty] | 0x5340f010
PTOPMM_Faza2_Tok26_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3293 | [8 empty] | 0x5340f020
PTOPMM_Faza2_Tok27_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3294 | [8 empty] | 0x5340f030
PTOPMM_Faza2_Tok28_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3295 | [8 empty] | 0x5340f040
PTOPMM_Faza2_Tok29_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3296 | [8 empty] | 0x5340f050
PTOPMM_Faza2_Tok30_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3297 | [8 empty] | 0x5340f060
PTOPMM_Faza2_Tok31_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3298 | [8 empty] | 0x5340f070
PTOPMM_Faza2_Tok32_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3299 | [8 empty] | 0x5340f080
PTOPMM_Faza2_Tok33_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3300 | [8 empty] | 0x5340f090
PTOPMM_Faza2_Tok34_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3301 | [8 empty] | 0x5340f0a0
PTOPMM_Faza2_Tok35_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3302 | [8 empty] | 0x5340f0b0
PTOPMM_Faza2_Tok36_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3303 | [8 empty] | 0x5340f0c0
PTOPMM_Faza2_Tok37_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3304 | [8 empty] | 0x5340f0d0
PTOPMM_Faza2_Tok38_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3305 | [8 empty] | 0x5340f0e0
PTOPMM_Faza2_Tok39_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3306 | [8 empty] | 0x5340f0f0
PTOPMM_Faza2_Tok40_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3307 | [8 empty] | 0x5340f100
PTOPMM_Faza2_Tok41_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3308 | [8 empty] | 0x5340f110
PTOPMM_Faza2_Tok42_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3309 | [8 empty] | 0x5340f120
PTOPMM_Faza3_Tok01_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3310 | [8 empty] | 0x5340f130
PTOPMM_Faza3_Tok02_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3311 | [8 empty] | 0x5340f140
PTOPMM_Faza3_Tok03_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3312 | [8 empty] | 0x5340f150
PTOPMM_Faza3_Tok04_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3313 | [8 empty] | 0x5340f160
PTOPMM_Faza3_Tok05_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3314 | [8 empty] | 0x5340f170
PTOPMM_Faza3_Tok06_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3315 | [8 empty] | 0x5340f180
PTOPMM_Faza3_Tok07_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3316 | [8 empty] | 0x5340f190
PTOPMM_Faza3_Tok08_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3317 | [8 empty] | 0x5340f1a0
PTOPMM_Faza3_Tok09_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3318 | [8 empty] | 0x5340f1b0
PTOPMM_Faza3_Tok10_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3319 | [8 empty] | 0x5340f1c0
PTOPMM_Faza3_Tok11_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3320 | [8 empty] | 0x5340f1d0
PTOPMM_Faza3_Tok12_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3321 | [8 empty] | 0x5340f1e0
PTOPMM_Faza3_Tok13_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3322 | [8 empty] | 0x5340f1f0
PTOPMM_Faza3_Tok14_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3323 | [8 empty] | 0x5340f200
PTOPMM_Faza3_Tok15_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3324 | [8 empty] | 0x5340f210
PTOPMM_Faza3_Tok16_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3325 | [8 empty] | 0x5340f220
PTOPMM_Faza3_Tok17_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3326 | [8 empty] | 0x5340f230
PTOPMM_Faza3_Tok18_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3327 | [8 empty] | 0x5340f240
PTOPMM_Faza3_Tok19_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3328 | [8 empty] | 0x5340f250
PTOPMM_Faza3_Tok20_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3329 | [8 empty] | 0x5340f260
PTOPMM_Faza3_Tok21_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3330 | [8 empty] | 0x5340f270
PTOPMM_Faza3_Tok22_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3331 | [8 empty] | 0x5340f280
PTOPMM_Faza3_Tok23_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3332 | [8 empty] | 0x5340f290
PTOPMM_Faza3_Tok24_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3333 | [8 empty] | 0x5340f2a0
PTOPMM_Faza3_Tok25_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3334 | [8 empty] | 0x5340f2b0
PTOPMM_Faza3_Tok26_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3335 | [8 empty] | 0x5340f2c0
PTOPMM_Faza3_Tok27_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3336 | [8 empty] | 0x5340f2d0
PTOPMM_Faza3_Tok28_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3337 | [8 empty] | 0x5340f2e0
PTOPMM_Faza3_Tok29_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3338 | [8 empty] | 0x5340f2f0
PTOPMM_Faza3_Tok30_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3339 | [8 empty] | 0x5340f300
PTOPMM_Faza3_Tok31_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3340 | [8 empty] | 0x5340f310
PTOPMM_Faza3_Tok32_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3341 | [8 empty] | 0x5340f320
PTOPMM_Faza3_Tok33_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3342 | [8 empty] | 0x5340f330
PTOPMM_Faza3_Tok34_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3343 | [8 empty] | 0x5340f340
PTOPMM_Faza3_Tok35_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3344 | [8 empty] | 0x5340f350
PTOPMM_Faza3_Tok36_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3345 | [8 empty] | 0x5340f360
PTOPMM_Faza3_Tok37_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3346 | [8 empty] | 0x5340f370
PTOPMM_Faza3_Tok38_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3347 | [8 empty] | 0x5340f380
PTOPMM_Faza3_Tok39_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3348 | [8 empty] | 0x5340f390
PTOPMM_Faza3_Tok40_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3349 | [8 empty] | 0x5340f3a0
PTOPMM_Faza3_Tok41_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3350 | [8 empty] | 0x5340f3b0
PTOPMM_Faza3_Tok42_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3351 | [8 empty] | 0x5340f3c0
PTOR1K5A2Q101odcepKS011izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3352 | [8 empty] | 0x5340f3d0
PTOR1K5A2Q102odcepKS021izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3353 | [8 empty] | 0x5340f3e0
PTOR1K5A2Q103odcepKS031izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3354 | [8 empty] | 0x5340f3f0
PTOR1K5A2Q104odcepKS041izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3355 | [8 empty] | 0x5340f400
PTOR1K5A2Q105odcepKS051izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3356 | [8 empty] | 0x5340f410
PTOR1K5A2Q106odcepKS061izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3357 | [8 empty] | 0x5340f420
PTOR1K5A2Q107odcusmSS2izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3358 | [8 empty] | 0x5340f430
PTOR1K5A2Q108odcusmSS3izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3359 | [8 empty] | 0x5340f440
PTOR1K5A2F201odcepKS012izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3360 | [8 empty] | 0x5340f450
PTOR1K5A2F202odcepKS022izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3361 | [8 empty] | 0x5340f460
PTOR1K5A2F203odcepKS032izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3362 | [8 empty] | 0x5340f470
PTOR1K5A2F204odcepKS042izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3363 | [8 empty] | 0x5340f480
PTOR1K5A2F205odcepKS052izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3364 | [8 empty] | 0x5340f490
PTOR1K5A2F206odcepKS053izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3365 | [8 empty] | 0x5340f4a0
PTOR1K5A2F207odcepKS062izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3366 | [8 empty] | 0x5340f4b0
PTOR1K5A1F208odcepKS063izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3367 | [8 empty] | 0x5340f4c0
PTOR1K5A1Q11odcepUPSAizpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3368 | [8 empty] | 0x5340f4d0
PTOR1K5A1Q12odcbyUPSAizpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3369 | [8 empty] | 0x5340f4e0
PTOR1K5A1Q13odcmehbyAizpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3370 | [8 empty] | 0x5340f4f0
PTOR1K5UAQ11odcepPMMizpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3371 | [8 empty] | 0x5340f500
PTOR1K5UAQ12odcepPMMizpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3372 | [8 empty] | 0x5340f510
PTOR1K5A2prenapetostna_omogoci | DIGITAL | IOD_PTO_disk2 | D3373 | [8 empty] | 0x5340f520
PTOR1K5A1prenapetostna_omogoci | DIGITAL | IOD_PTO_disk2 | D3374 | [8 empty] | 0x5340f530
PTOKlima1skupnanapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3375 | [8 empty] | 0x5340f540
PTOKlima2skupnanapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3376 | [8 empty] | 0x5340f550
PTOKlima3skupnanapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3377 | [8 empty] | 0x5340f560
PTOKlima4skupnanapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3378 | [8 empty] | 0x5340f570
PTOKlima5skupnanapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3379 | [8 empty] | 0x5340f580
PTOKlima6skupnanapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3380 | [8 empty] | 0x5340f590
PTOKlimasplitnapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3381 | [8 empty] | 0x5340f5a0
PTOUPSAvklopljenbypassDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3382 | [8 empty] | 0x5340f5b0
PTOUPSAsplosnanapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3383 | [8 empty] | 0x5340f5c0
PTOUPSBvklopljenbypassDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3384 | [8 empty] | 0x5340f5d0
PTOUPSBsplosnanapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3385 | [8 empty] | 0x5340f5e0
PTOR1K5CNSUPSzakrmnapaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3386 | [8 empty] | 0x5340f5f0
PTOR1K5CNSUPSzakrmtokizbaterije_omogoci | DIGITAL | IOD_PTO_disk2 | D3387 | [8 empty] | 0x5340f600
PTOR1K5CNSUPSzakrmpolnjenjebat_omogoci | DIGITAL | IOD_PTO_disk2 | D3388 | [8 empty] | 0x5340f610
PTOPLCnapakaprinastavljanjucasa_omogoci | DIGITAL | IOD_PTO_disk2 | D3389 | [8 empty] | 0x5340f620
PTOPLCslababaterijakrmilnikaXC200_omogoci | DIGITAL | IOD_PTO_disk2 | D3390 | [8 empty] | 0x5340f630
PTOTempvsersobi1previsoka_omogoci | DIGITAL | IOD_PTO_disk2 | D3391 | [8 empty] | 0x5340f640
PTOTempvsersobi2previsoka_omogoci | DIGITAL | IOD_PTO_disk2 | D3392 | [8 empty] | 0x5340f650
PTOTempvsersobi3previsoka_omogoci | DIGITAL | IOD_PTO_disk2 | D3393 | [8 empty] | 0x5340f660
PTOSenzortemperatureTH1napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3394 | [8 empty] | 0x5340f670
PTOSenzortemperatureTH2napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3395 | [8 empty] | 0x5340f680
PTOSenzortemperatureTH3napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3396 | [8 empty] | 0x5340f690
PTOSenzortemperatureTH4napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3397 | [8 empty] | 0x5340f6a0
PTOSenzortemperatureTH5napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3398 | [8 empty] | 0x5340f6b0
PTOSenzortemperatureTH6napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3399 | [8 empty] | 0x5340f6c0
PTOSenzorvlageTH1napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3400 | [8 empty] | 0x5340f6d0
PTOSenzorvlageTH2napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3401 | [8 empty] | 0x5340f6e0
PTOSenzorvlageTH3napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3402 | [8 empty] | 0x5340f6f0
PTOSenzorvlageTH4napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3403 | [8 empty] | 0x5340f700
PTOSenzorvlageTH5napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3404 | [8 empty] | 0x5340f710
PTOSenzorvlageTH6napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3405 | [8 empty] | 0x5340f720
PTORazlitjevodeLAH1klimaKS0102_omogoci | DIGITAL | IOD_PTO_disk2 | D3406 | [8 empty] | 0x5340f730
PTORazlitjevodeLAH2klimaKS0304_omogoci | DIGITAL | IOD_PTO_disk2 | D3407 | [8 empty] | 0x5340f740
PTORazlitjevodeLAH3klimaKS05_omogoci | DIGITAL | IOD_PTO_disk2 | D3408 | [8 empty] | 0x5340f750
PTORazlitjevodeLAH4klimaKS06_omogoci | DIGITAL | IOD_PTO_disk2 | D3409 | [8 empty] | 0x5340f760
PTO_UPS_A_napaka_razsmernika_omogoci | DIGITAL | IOD_PTO_disk2 | D3410 | [8 empty] | 0x5340f770
PTO_UPS_B_napaka_razsmernika_omogoci | DIGITAL | IOD_PTO_disk2 | D3411 | [8 empty] | 0x5340f780
PTOPMM_2x63_VirA_zavihek | DIGITAL | IOD_PTO_disk2 | D3412 | [8 empty] | 0x5340f790
PTOPMM_2x63_VirB_zavihek | DIGITAL | IOD_PTO_disk2 | D3413 | [8 empty] | 0x5340f7a0
PTOPMM_2x17_VirA_zavihek | DIGITAL | IOD_PTO_disk2 | D3414 | [8 empty] | 0x5340f7b0
PTOPMM_2x17_VirB_zavihek | DIGITAL | IOD_PTO_disk2 | D3415 | [8 empty] | 0x5340f7c0
PTOPMM1OverCurrentBetw1_Omogoci | DIGITAL | IOD_PTO_disk2 | D3416 | [8 empty] | 0x5340f7d0
PTOPMM1OverCurrentBetw2_Omogoci | DIGITAL | IOD_PTO_disk2 | D3417 | [8 empty] | 0x5340f7e0
PTOPMM1OverCurrentBetw3_Omogoci | DIGITAL | IOD_PTO_disk2 | D3418 | [8 empty] | 0x5340f7f0
PTOPMM1OverCurrentOver1_Omogoci | DIGITAL | IOD_PTO_disk2 | D3419 | [8 empty] | 0x5340f800
PTOPMM1OverCurrentOver2_Omogoci | DIGITAL | IOD_PTO_disk2 | D3420 | [8 empty] | 0x5340f810
PTOPMM1OverCurrentOver3_Omogoci | DIGITAL | IOD_PTO_disk2 | D3421 | [8 empty] | 0x5340f820
PTOPMM2OverCurrentBetw1_Omogoci | DIGITAL | IOD_PTO_disk2 | D3422 | [8 empty] | 0x5340f830
PTOPMM2OverCurrentBetw2_Omogoci | DIGITAL | IOD_PTO_disk2 | D3423 | [8 empty] | 0x5340f840
PTOPMM2OverCurrentBetw3_Omogoci | DIGITAL | IOD_PTO_disk2 | D3424 | [8 empty] | 0x5340f850
PTOPMM2OverCurrentOver1_Omogoci | DIGITAL | IOD_PTO_disk2 | D3425 | [8 empty] | 0x5340f860
PTOPMM2OverCurrentOver2_Omogoci | DIGITAL | IOD_PTO_disk2 | D3426 | [8 empty] | 0x5340f870
PTOPMM2OverCurrentOver3_Omogoci | DIGITAL | IOD_PTO_disk2 | D3427 | [8 empty] | 0x5340f880
PTOSKTemp1_Opozorilo_Zgornja_Meja | REAL | IOD_PTO_disk | R1 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x5340f890
PTOSKTemp1_Alarm_Zgornja_Meja | REAL | IOD_PTO_disk | R2 | 0 | 60 | 0 | 60 | °C | ####.# |  |  | 0x5340f891
PTOSKTemp1_Opozorilo_Omogoci | DIGITAL | IOD_PTO_disk | D3819 | [8 empty] | 0x5340f8a0
PTOSKTemp1_Alarm_Omogoci | DIGITAL | IOD_PTO_disk | D3820 | [8 empty] | 0x5340f8b0
PTOSKVlaga1_Opozorilo_Zgornja_Meja | REAL | IOD_PTO_disk | R3 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x5340f8c0
PTOSKVlaga1_Alarm_Zgornja_Meja | REAL | IOD_PTO_disk | R4 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x5340f8c1
PTOSKVlaga1_Opozorilo_Omogoci | DIGITAL | IOD_PTO_disk | D3821 | [8 empty] | 0x5340f8d0
PTOSKVlaga1_Alarm_Omogoci | DIGITAL | IOD_PTO_disk | D3822 | [8 empty] | 0x5340f8e0
PTOSKTemp2_Opozorilo_Zgornja_Meja | REAL | IOD_PTO_disk | R5 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x5340f8f0
PTOSKTemp2_Alarm_Zgornja_Meja | REAL | IOD_PTO_disk | R6 | 0 | 60 | 0 | 60 | °C | ####.# |  |  | 0x5340f8f1
PTOSKTemp2_Opozorilo_Omogoci | DIGITAL | IOD_PTO_disk | D3823 | [8 empty] | 0x5340f900
PTOSKTemp2_Alarm_Omogoci | DIGITAL | IOD_PTO_disk | D3824 | [8 empty] | 0x5340f910
PTOSKVlaga2_Opozorilo_Zgornja_Meja | REAL | IOD_PTO_disk | R7 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x5340f920
PTOSKVlaga2_Alarm_Zgornja_Meja | REAL | IOD_PTO_disk | R8 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x5340f921
PTOSKVlaga2_Opozorilo_Omogoci | DIGITAL | IOD_PTO_disk | D3825 | [8 empty] | 0x5340f930
PTOSKVlaga2_Alarm_Omogoci | DIGITAL | IOD_PTO_disk | D3826 | [8 empty] | 0x5340f940
PTOSKTemp3_Opozorilo_Zgornja_Meja | REAL | IOD_PTO_disk | R9 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x5340f950
PTOSKTemp3_Alarm_Zgornja_Meja | REAL | IOD_PTO_disk | R10 | 0 | 60 | 0 | 60 | °C | ####.# |  |  | 0x5340f951
PTOSKTemp3_Opozorilo_Omogoci | DIGITAL | IOD_PTO_disk | D3827 | [8 empty] | 0x5340f960
PTOSKTemp3_Alarm_Omogoci | DIGITAL | IOD_PTO_disk | D3828 | [8 empty] | 0x5340f970
PTOSKVlaga3_Opozorilo_Zgornja_Meja | REAL | IOD_PTO_disk | R11 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x5340f980
PTOSKVlaga3_Alarm_Zgornja_Meja | REAL | IOD_PTO_disk | R12 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x5340f981
PTOSKVlaga3_Opozorilo_Omogoci | DIGITAL | IOD_PTO_disk | D3829 | [8 empty] | 0x5340f990
PTOSKVlaga3_Alarm_Omogoci | DIGITAL | IOD_PTO_disk | D3830 | [8 empty] | 0x5340f9a0
PTOSKTemp4_Opozorilo_Zgornja_Meja | REAL | IOD_PTO_disk | R13 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x5340f9b0
PTOSKTemp4_Alarm_Zgornja_Meja | REAL | IOD_PTO_disk | R14 | 0 | 60 | 0 | 60 | °C | ####.# |  |  | 0x5340f9b1
PTOSKTemp4_Opozorilo_Omogoci | DIGITAL | IOD_PTO_disk | D3831 | [8 empty] | 0x5340f9c0
PTOSKTemp4_Alarm_Omogoci | DIGITAL | IOD_PTO_disk | D3832 | [8 empty] | 0x5340f9d0
PTOSKVlaga4_Opozorilo_Zgornja_Meja | REAL | IOD_PTO_disk | R15 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x5340f9e0
PTOSKVlaga4_Alarm_Zgornja_Meja | REAL | IOD_PTO_disk | R16 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x5340f9e1
PTOSKVlaga4_Opozorilo_Omogoci | DIGITAL | IOD_PTO_disk | D3833 | [8 empty] | 0x5340f9f0
PTOSKVlaga4_Alarm_Omogoci | DIGITAL | IOD_PTO_disk | D3834 | [8 empty] | 0x5340fa00
PTOComSCADA_stevec | INT | IOD_PTO_disk | I3 | [8 empty] | 0x5340fa10
PTOComSCADA_stevec1 | INT | IOD_PTO_disk | I4 | [8 empty] | 0x5340fa11
Prikaz | DIGITAL | IOD_PTO_disk | D3836 | [8 empty] | 0x5340fa20
PTOPMM2x63_VirA_Faza1_Med60in80 | REAL | IOD_PTO_disk | R30[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x5340fa30
PTOPMM2x63_VirB_Faza1_Med60in80 | REAL | IOD_PTO_disk | R60[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x5340fa31
PTOPMM2x63_VirA_Faza1_Nad80 | REAL | IOD_PTO_disk | R90[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x5340fa32
PTOPMM2x63_VirB_Faza1_Mad80 | REAL | IOD_PTO_disk | R120[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x5340fa33
PTOPMM2x63_VirA_Faza2_Med60in80 | REAL | IOD_PTO_disk | R150[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x5340fa34
PTOPMM2x63_VirB_Faza2_Med60in80 | REAL | IOD_PTO_disk | R180[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x5340fa35
PTOPMM2x63_VirA_Faza2_Nad80 | REAL | IOD_PTO_disk | R210[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x5340fa36
PTOPMM2x63_VirB_Faza2_Mad80 | REAL | IOD_PTO_disk | R240[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x5340fa37
PTOPMM2x63_VirA_Faza3_Med60in80 | REAL | IOD_PTO_disk | R270[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x5340fa38
PTOPMM2x63_VirB_Faza3_Med60in80 | REAL | IOD_PTO_disk | R300[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x5340fa39
PTOPMM2x63_VirA_Faza3_Nad80 | REAL | IOD_PTO_disk | R330[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x5340fa3a
PTOPMM2x63_VirB_Faza3_Mad80 | REAL | IOD_PTO_disk | R360[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x5340fa3b
PTOPMM1PoljeFazaATok1_16_nad80 | DIGITAL | IOD_PTO_disk2 | D3500[16] | [8 empty] | 0x5340fa40
PTOPMM1PoljeFazaATok17_32_nad80 | DIGITAL | IOD_PTO_disk2 | D3517[16] | [8 empty] | 0x5340fa50
PTOPMM1PoljeFazaATok33_42_nad80 | DIGITAL | IOD_PTO_disk2 | D3534[16] | [8 empty] | 0x5340fa60
PTOPMM1PoljeFazaBTok1_16_nad80 | DIGITAL | IOD_PTO_disk2 | D3551[16] | [8 empty] | 0x5340fa70
PTOPMM1PoljeFazaBTok17_32_nad80 | DIGITAL | IOD_PTO_disk2 | D3568[16] | [8 empty] | 0x5340fa80
PTOPMM1PoljeFazaBTok33_42_nad80 | DIGITAL | IOD_PTO_disk2 | D3585[16] | [8 empty] | 0x5340fa90
PTOPMM1PoljeFazaCTok1_16_nad80 | DIGITAL | IOD_PTO_disk2 | D3602[16] | [8 empty] | 0x5340faa0
PTOPMM1PoljeFazaCTok17_32_nad80 | DIGITAL | IOD_PTO_disk2 | D3619[16] | [8 empty] | 0x5340fab0
PTOPMM1PoljeFazaCTok33_42_nad80 | DIGITAL | IOD_PTO_disk2 | D3636[16] | [8 empty] | 0x5340fac0
PTOPMM1PoljeFazaATok1_16_med60_80 | DIGITAL | IOD_PTO_disk2 | D3653[16] | [8 empty] | 0x5340fad0
PTOPMM1PoljeFazaATok17_32_med60_80 | DIGITAL | IOD_PTO_disk2 | D3670[16] | [8 empty] | 0x5340fae0
PTOPMM1PoljeFazaATok33_42_med60_80 | DIGITAL | IOD_PTO_disk2 | D3687[16] | [8 empty] | 0x5340faf0
PTOPMM1PoljeFazaBTok1_16_med60_80 | DIGITAL | IOD_PTO_disk2 | D3704[16] | [8 empty] | 0x5340fb00
PTOPMM1PoljeFazaBTok17_32_med60_80 | DIGITAL | IOD_PTO_disk2 | D3721[16] | [8 empty] | 0x5340fb10
PTOPMM1PoljeFazaBTok33_42_med60_80 | DIGITAL | IOD_PTO_disk2 | D3738[16] | [8 empty] | 0x5340fb20
PTOPMM1PoljeFazaCTok1_16_med60_80 | DIGITAL | IOD_PTO_disk2 | D3755[16] | [8 empty] | 0x5340fb30
PTOPMM1PoljeFazaCTok17_32_med60_80 | DIGITAL | IOD_PTO_disk2 | D3772[16] | [8 empty] | 0x5340fb40
PTOPMM1PoljeFazaCTok33_42_med60_80 | DIGITAL | IOD_PTO_disk2 | D3789[16] | [8 empty] | 0x5340fb50
PTOPMM1OverCurrentBetw1_VirB_Omogoci | DIGITAL | IOD_PTO_disk2 | D3837 | [8 empty] | 0x5340fb60
PTOPMM1OverCurrentBetw1_VirA_Omogoci | DIGITAL | IOD_PTO_disk2 | D3838 | [8 empty] | 0x5340fb70
PTOPMM1OverCurrentBetw2_VirB_Omogoci | DIGITAL | IOD_PTO_disk2 | D3839 | [8 empty] | 0x5340fb80
PTOPMM1OverCurrentBetw2_VirA_Omogoci | DIGITAL | IOD_PTO_disk2 | D3840 | [8 empty] | 0x5340fb90
PTOPMM1OverCurrentBetw3_VirB_Omogoci | DIGITAL | IOD_PTO_disk2 | D3841 | [8 empty] | 0x5340fba0
PTOPMM1OverCurrentBetw3_VirA_Omogoci | DIGITAL | IOD_PTO_disk2 | D3842 | [8 empty] | 0x5340fbb0
PTOPMM1OverCurrentBetw1_VirB | DIGITAL | IOD_PTO_disk2 | D3843 | [8 empty] | 0x5340fbc0
PTOPMM1OverCurrentBetw1_VirA | DIGITAL | IOD_PTO_disk2 | D3844 | [8 empty] | 0x5340fbd0
PTOPMM1OverCurrentBetw2_VirB | DIGITAL | IOD_PTO_disk2 | D3845 | [8 empty] | 0x5340fbe0
PTOPMM1OverCurrentBetw2_VirA | DIGITAL | IOD_PTO_disk2 | D3846 | [8 empty] | 0x5340fbf0
PTOPMM1OverCurrentBetw3_VirB | DIGITAL | IOD_PTO_disk2 | D3847 | [8 empty] | 0x5340fc00
PTOPMM1OverCurrentBetw3_VirA | DIGITAL | IOD_PTO_disk2 | D3848 | [8 empty] | 0x5340fc10
PTOPrikaz | DIGITAL | IOD_PTO_disk2 | D3849 | [8 empty] | 0x5340fc20
PTOPMM1OverCurrentBetw1_VirB_1_2 | INT | IOD_PTO_disk | I5 | [8 empty] | 0x5340fc30
PTOPMM1OverCurrentBetw1_VirA_1_2 | INT | IOD_PTO_disk | I6 | [8 empty] | 0x5340fc31
PTOPMM1OverCurrentBetw1_VirB_2_2 | INT | IOD_PTO_disk | I7 | [8 empty] | 0x5340fc32
PTOPMM1OverCurrentBetw1_VirA_2_2 | INT | IOD_PTO_disk | I8 | [8 empty] | 0x5340fc33
PTOPMM1OverCurrentBetw2_VirB_1_2 | INT | IOD_PTO_disk | I9 | [8 empty] | 0x5340fc34
PTOPMM1OverCurrentBetw2_VirA_1_2 | INT | IOD_PTO_disk | I10 | [8 empty] | 0x5340fc35
PTOPMM1OverCurrentBetw2_VirB_2_2 | INT | IOD_PTO_disk | I11 | [8 empty] | 0x5340fc36
PTOPMM1OverCurrentBetw2_VirA_2_2 | INT | IOD_PTO_disk | I12 | [8 empty] | 0x5340fc37
PTOPMM1OverCurrentBetw3_VirB_1_2 | INT | IOD_PTO_disk | I13 | [8 empty] | 0x5340fc38
PTOPMM1OverCurrentBetw3_VirA_1_2 | INT | IOD_PTO_disk | I14 | [8 empty] | 0x5340fc39
PTOPMM1OverCurrentBetw3_VirB_2_2 | INT | IOD_PTO_disk | I15 | [8 empty] | 0x5340fc3a
PTOPMM1OverCurrentBetw3_VirA_2_2 | INT | IOD_PTO_disk | I16 | [8 empty] | 0x5340fc3b
PTOPMM1OverCurrentOver1_VirB_Omogoci | DIGITAL | IOD_PTO_disk | D3850 | [8 empty] | 0x5340fc40
PTOPMM1OverCurrentOver1_VirA_Omogoci | DIGITAL | IOD_PTO_disk | D3851 | [8 empty] | 0x5340fc50
PTOPMM1OverCurrentOver2_VirB_Omogoci | DIGITAL | IOD_PTO_disk | D3852 | [8 empty] | 0x5340fc60
PTOPMM1OverCurrentOver2_VirA_Omogoci | DIGITAL | IOD_PTO_disk | D3853 | [8 empty] | 0x5340fc70
PTOPMM1OverCurrentOver3_VirB_Omogoci | DIGITAL | IOD_PTO_disk | D3854 | [8 empty] | 0x5340fc80
PTOPMM1OverCurrentOver3_VirA_Omogoci | DIGITAL | IOD_PTO_disk | D3855 | [8 empty] | 0x5340fc90
PTOPMM1OverCurrentOver1_VirB | DIGITAL | IOD_PTO_disk | D3856 | [8 empty] | 0x5340fca0
PTOPMM1OverCurrentOver1_VirA | DIGITAL | IOD_PTO_disk | D3857 | [8 empty] | 0x5340fcb0
PTOPMM1OverCurrentOver2_VirB | DIGITAL | IOD_PTO_disk | D3858 | [8 empty] | 0x5340fcc0
PTOPMM1OverCurrentOver2_VirA | DIGITAL | IOD_PTO_disk | D3859 | [8 empty] | 0x5340fcd0
PTOPMM1OverCurrentOver3_VirB | DIGITAL | IOD_PTO_disk | D3860 | [8 empty] | 0x5340fce0
PTOPMM1OverCurrentOver3_VirA | DIGITAL | IOD_PTO_disk | D3861 | [8 empty] | 0x5340fcf0
PTOPMM1OverCurrentOver1_VirB_1_2 | INT | IOD_PTO_disk | I17 | [8 empty] | 0x5340fd00
PTOPMM1OverCurrentOver1_VirA_1_2 | INT | IOD_PTO_disk | I18 | [8 empty] | 0x5340fd01
PTOPMM1OverCurrentOver1_VirB_2_2 | INT | IOD_PTO_disk | I19 | [8 empty] | 0x5340fd02
PTOPMM1OverCurrentOver1_VirA_2_2 | INT | IOD_PTO_disk | I20 | [8 empty] | 0x5340fd03
PTOPMM1OverCurrentOver2_VirB_1_2 | INT | IOD_PTO_disk | I21 | [8 empty] | 0x5340fd04
PTOPMM1OverCurrentOver2_VirA_1_2 | INT | IOD_PTO_disk | I22 | [8 empty] | 0x5340fd05
PTOPMM1OverCurrentOver2_VirB_2_2 | INT | IOD_PTO_disk | I23 | [8 empty] | 0x5340fd06
PTOPMM1OverCurrentOver2_VirA_2_2 | INT | IOD_PTO_disk | I24 | [8 empty] | 0x5340fd07
PTOPMM1OverCurrentOver3_VirB_1_2 | INT | IOD_PTO_disk | I25 | [8 empty] | 0x5340fd08
PTOPMM1OverCurrentOver3_VirA_1_2 | INT | IOD_PTO_disk | I26 | [8 empty] | 0x5340fd09
PTOPMM1OverCurrentOver3_VirB_2_2 | INT | IOD_PTO_disk | I27 | [8 empty] | 0x5340fd0a
PTOPMM1OverCurrentOver3_VirA_2_2 | INT | IOD_PTO_disk | I28 | [8 empty] | 0x5340fd0b
PTOOmogociVseAlarme | DIGITAL | IOD_PTO_disk | D3862 | [8 empty] | 0x5340fd10
PTOOmogociVseSMSAlarme | DIGITAL | IOD_PTO_disk | D3863 | [8 empty] | 0x5340fd20
PTOOmogociVseDogodke_DO | DIGITAL | IOD_PTO_disk | D3864 | [8 empty] | 0x5340fd30
PTOOmogociVseDogodke_DI | DIGITAL | IOD_PTO_disk | D3865 | [8 empty] | 0x5340fd40
PTOOmogociVseDogodke_COM | DIGITAL | IOD_PTO_disk | D3866 | [8 empty] | 0x5340fd50
PTORazlikaUr | REAL | IOD_PTO | PTO:.RazlikaUr | [6 empty] | 6157 | 1 | 0x5340fd60
PTOPMMOverCurrentOver1A_omogoci | DIGITAL | IOD_PTO_disk | D3867 | [8 empty] | 0x5340fd70
PTOPMMOverCurrentOver2A_omogoci | DIGITAL | IOD_PTO_disk | D3868 | [8 empty] | 0x5340fd80
PTOPMMOverCurrentOver3A_omogoci | DIGITAL | IOD_PTO_disk | D3869 | [8 empty] | 0x5340fd90
PTO_DI_A1Q02_IZKLJUCENO_omogoci | DIGITAL | IOD_PTO_disk | D3870 | [8 empty] | 0x5340fda0
PTO_DI_A1Q12_IZKLJUCENO_omogoci | DIGITAL | IOD_PTO_disk | D3873 | [8 empty] | 0x5340fdb0
PTO_DI_A1Q02_VKLJUCENO_omogoci | DIGITAL | IOD_PTO_disk | D3874 | [8 empty] | 0x5340fdc0
PTO_DI_A1Q12_VKLJUCENO_omogoci | DIGITAL | IOD_PTO_disk | D3875 | [8 empty] | 0x5340fdd0
NOT_PTODI_A2Q0_GlavnoSti_ON_omogoci | DIGITAL | IOD_PTO_disk | D3876 | [8 empty] | 0x5340fde0
NOT_PTODI_Q101_OdcKlima1_ON_omogoci | DIGITAL | IOD_PTO_disk | D3877 | [8 empty] | 0x5340fdf0
NOT_PTODI_Q102_OdcKlima2_ON_omogoci | DIGITAL | IOD_PTO_disk | D3878 | [8 empty] | 0x5340fe00
NOT_PTODI_Q103_OdcKlima3_ON_omogoci | DIGITAL | IOD_PTO_disk | D3879 | [8 empty] | 0x5340fe10
NOT_PTODI_Q104_OdcKlima4_ON_omogoci | DIGITAL | IOD_PTO_disk | D3880 | [8 empty] | 0x5340fe20
NOT_PTODI_Q105_OdcKlima5_ON_omogoci | DIGITAL | IOD_PTO_disk | D3881 | [8 empty] | 0x5340fe30
NOT_PTODI_Q106_OdcKlima6_ON_omogoci | DIGITAL | IOD_PTO_disk | D3882 | [8 empty] | 0x5340fe40
NOT_PTODI_Q107_OdcUsmSS2_ON_omogoci | DIGITAL | IOD_PTO_disk | D3883 | [8 empty] | 0x5340fe50
NOT_PTODI_Q108_OdcUsmSS3_ON_omogoci | DIGITAL | IOD_PTO_disk | D3884 | [8 empty] | 0x5340fe60
NOT_PTODI_F201_OdcKl1ZE_ON_omogoci | DIGITAL | IOD_PTO_disk | D3885 | [8 empty] | 0x5340fe70
NOT_PTODI_F202_OdcKl2ZE_ON_omogoci | DIGITAL | IOD_PTO_disk | D3886 | [8 empty] | 0x5340fe80
NOT_PTODI_F203_OdcKl3ZE_ON_omogoci | DIGITAL | IOD_PTO_disk | D3887 | [8 empty] | 0x5340fe90
NOT_PTODI_F204_OdcKl4ZE_ON_omogoci | DIGITAL | IOD_PTO_disk | D3888 | [8 empty] | 0x5340fea0
NOT_PTODI_F205_OdcKl5aZE_ON_omogoci | DIGITAL | IOD_PTO_disk | D3889 | [8 empty] | 0x5340feb0
NOT_PTODI_F206_OdcKl5bZE_ON_omogoci | DIGITAL | IOD_PTO_disk | D3890 | [8 empty] | 0x5340fec0
NOT_PTODI_F207_OdcKl6aZE_ON_omogoci | DIGITAL | IOD_PTO_disk | D3891 | [8 empty] | 0x5340fed0
NOT_PTODI_F208_OdcKl6bZE_ON_omogoci | DIGITAL | IOD_PTO_disk | D3892 | [8 empty] | 0x5340fee0
NOT_PTODI_A1Q0_GlavnoSti_ON_omogoci | DIGITAL | IOD_PTO_disk | D3893 | [8 empty] | 0x5340fef0
NOT_PTODI_A1Q11_OdcUpsA_ON_omogoci | DIGITAL | IOD_PTO_disk | D3894 | [8 empty] | 0x5340ff00
NOT_PTODI_A1Q12_OdcByUpsA_ON_omogoci | DIGITAL | IOD_PTO_disk | D3895 | [8 empty] | 0x5340ff10
NOT_PTODI_A1Q13_OdcByA_ON_omogoci | DIGITAL | IOD_PTO_disk | D3896 | [8 empty] | 0x5340ff20
NOT_PTODI_A1Q01_DovUpsA_ON_omogoci | DIGITAL | IOD_PTO_disk | D3897 | [8 empty] | 0x5340ff30
PTODI_A1Q02_DovByA_ON_omogoci | DIGITAL | IOD_PTO_disk | D3898 | [8 empty] | 0x5340ff40
NOT_PTODI_UQ11_OdcPMM_ON_omogoci | DIGITAL | IOD_PTO_disk | D3899 | [8 empty] | 0x5340ff50
NOT_PTODI_UQ12_OdcPMM_ON_omogoci | DIGITAL | IOD_PTO_disk | D3900 | [8 empty] | 0x5340ff60
PTODI_Klima1_ON_omogoci | DIGITAL | IOD_PTO_disk | D3901 | [8 empty] | 0x5340ff70
PTODI_Klima2_ON_omogoci | DIGITAL | IOD_PTO_disk | D3902 | [8 empty] | 0x5340ff80
PTODI_Klima3_ON_omogoci | DIGITAL | IOD_PTO_disk | D3903 | [8 empty] | 0x5340ff90
PTODI_Klima4_ON_omogoci | DIGITAL | IOD_PTO_disk | D3904 | [8 empty] | 0x5340ffa0
PTODI_Klima5_ON_omogoci | DIGITAL | IOD_PTO_disk | D3905 | [8 empty] | 0x5340ffb0
PTODI_Klima6_ON_omogoci | DIGITAL | IOD_PTO_disk | D3906 | [6 empty] | 6157 | 1 | 0x5340ffc0
PTODIN_A1Q11_OdcUpsB_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q11_OdcUpsB_IZP | [6 empty] | 6157 | 1 | 0x5340ffd0
PTODIN_A1Q12_OdcByUpsB_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q12_OdcByUpsB_IZP | [6 empty] | 6157 | 1 | 0x5340ffe0
PTODIN_A1Q13_OdcByB_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q13_OdcByB_IZP | [6 empty] | 6157 | 1 | 0x5340fff0
PTODIN_UQ11_OdcPMMB_IZP | DIGITAL | IOD_PTO | PTO:.DIN_UQ11_OdcPMMB_IZP | [6 empty] | 6157 | 1 | 0x53410000
PTODIN_UQ12_OdcPMMB_IZP | DIGITAL | IOD_PTO | PTO:.DIN_UQ12_OdcPMMB_IZP | [6 empty] | 6157 | 1 | 0x53410010
PTODIN_PrenapA3_OK | DIGITAL | IOD_PTO | PTO:.DIN_PrenapA3_OK | [6 empty] | 6157 | 1 | 0x53410020
A1Q11_OdcUpsB_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3907 | [8 empty] | 0x53410030
A1Q12_OdcByUpsB_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3908 | [8 empty] | 0x53410040
A1Q13_OdcByB_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3909 | [8 empty] | 0x53410050
UQ11_OdcPMMB_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3910 | [8 empty] | 0x53410060
UQ12_OdcPMMB_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3911 | [8 empty] | 0x53410070
PrenapA3_OK_omogoci | DIGITAL | IOD_PTO_disk | D3912 | [8 empty] | 0x53410080
PTODIN_A1Q0_GlavnoStiB_ON | DIGITAL | IOD_PTO | PTO:.DIN_A1Q0_GlavnoStiB_ON | [6 empty] | 6157 | 1 | 0x53410090
PTODIN_A1Q11_OdcUpsB_ON | DIGITAL | IOD_PTO | PTO:.DIN_A1Q11_OdcUpsB_ON | [6 empty] | 6157 | 1 | 0x534100a0
PTODIN_A1Q12_OdcByUpsB_ON | DIGITAL | IOD_PTO | PTO:.DIN_A1Q12_OdcByUpsB_ON | [6 empty] | 6157 | 1 | 0x534100b0
PTODI_A1Q13_OdcByB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q13_OdcByB_ON | [6 empty] | 6157 | 1 | 0x534100c0
PTODIN_A1Q01_DovUpsB_ON | DIGITAL | IOD_PTO | PTO:.DIN_A1Q01_DovUpsB_ON | [6 empty] | 6157 | 1 | 0x534100d0
PTODI_A1Q02_DovByB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q02_DovByB_ON | [6 empty] | 6157 | 1 | 0x534100e0
PTODIN_UQ11_OdcPMMB_ON | DIGITAL | IOD_PTO | PTO:.DIN_UQ11_OdcPMMB_ON | [6 empty] | 6157 | 1 | 0x534100f0
PTODI_UQ12_OdcPMMB_ON | DIGITAL | IOD_PTO | PTO:.DI_UQ12_OdcPMMB_ON | [6 empty] | 6157 | 1 | 0x53410100
PTODIN_A1Q0_GlavnoStiB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3913 | [8 empty] | 0x53410110
PTODIN_A1Q11_OdcUpsB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3914 | [8 empty] | 0x53410120
PTODIN_A1Q12_OdcByUpsB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3915 | [8 empty] | 0x53410130
PTODI_A1Q13_OdcByB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3916 | [8 empty] | 0x53410140
PTODIN_A1Q01_DovUpsB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3917 | [8 empty] | 0x53410150
PTODI_A1Q02_DovByB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3918 | [8 empty] | 0x53410160
PTODIN_UQ11_OdcPMMB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3919 | [8 empty] | 0x53410170
PTODI_UQ12_OdcPMMB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3920 | [8 empty] | 0x53410180
PTOKlima1NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].NapacnoGesloAlarm | [6 empty] | 6157 | 1 | 0x53410190
PTOKlima1ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].ExtTempHumAlarm | [6 empty] | 6157 | 1 | 0x534101a0
PTOKlima1PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].PoplavniAlarm | [6 empty] | 6157 | 1 | 0x534101b0
PTOKlima1VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[1].VisokPritiskKompresor1 | [6 empty] | 6157 | 1 | 0x534101c0
PTOKlima1VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[1].VisokPritiskKompresor2 | [6 empty] | 6157 | 1 | 0x534101d0
PTOKlima1ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[1].ElVentilKompresor1ERR | [6 empty] | 6157 | 1 | 0x534101e0
PTOKlima1ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[1].ElVentilKompresor2ERR | [6 empty] | 6157 | 1 | 0x534101f0
PTOKlima1WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].WrongPhaseSeqAlarm | [6 empty] | 6157 | 1 | 0x53410200
PTOKlima1PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[1].PrekinjenLANalarm | [6 empty] | 6157 | 1 | 0x53410210
PTOKlima1CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[1].CWTempHighForDehum | [6 empty] | 6157 | 1 | 0x53410220
PTOKlima1CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[1].CWVentilErrOrLowFlow | [6 empty] | 6157 | 1 | 0x53410230
PTOKlima1NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaPriPretokuVode | [6 empty] | 6157 | 1 | 0x53410240
PTOKlima1CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[1].CWhighTemp | [6 empty] | 6157 | 1 | 0x53410250
PTOKlima1NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorHotWTemp | [6 empty] | 6157 | 1 | 0x53410260
PTOKlima1NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorCondWTemp | [6 empty] | 6157 | 1 | 0x53410270
PTOKlima1NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorCW | [6 empty] | 6157 | 1 | 0x53410280
PTOKlima1Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Kompresor3naMejiObrUr | [6 empty] | 6157 | 1 | 0x53410290
PTOKlima1Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Kompresor4naMejiObrUr | [6 empty] | 6157 | 1 | 0x534102a0
PTOKlima1ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].ZracniFilterNaMejiObrUr | [6 empty] | 6157 | 1 | 0x534102b0
PTOKlima1Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Grelec1naMejiObrUr | [6 empty] | 6157 | 1 | 0x534102c0
PTOKlima1Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Grelec2naMejiObrUr | [6 empty] | 6157 | 1 | 0x534102d0
PTOKlima1VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].VlazilecNaMejiObrUr | [6 empty] | 6157 | 1 | 0x534102e0
PTOKlima1AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].AirCondUnitNaMejiObrUr | [6 empty] | 6157 | 1 | 0x534102f0
PTOKlima1DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[1].DigIn2Alarm | [6 empty] | 6157 | 1 | 0x53410300
PTOKlima1DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[1].DigIn4Alarm | [6 empty] | 6157 | 1 | 0x53410310
PTOKlima1DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[1].DigIn6Alarm | [6 empty] | 6157 | 1 | 0x53410320
PTOKlima1VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].VlazilecGenAlarm | [6 empty] | 6157 | 1 | 0x53410330
PTOKlima1General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].General2ndLevAlarm | [6 empty] | 6157 | 1 | 0x53410340
PTOKlima1UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].UnitOnRotAlarm | [6 empty] | 6157 | 1 | 0x53410350
PTOKlima1UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[1].UnitOnAlarmA | [6 empty] | 6157 | 1 | 0x53410360
PTOKlima1UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[1].UnitOnAlarmB | [6 empty] | 6157 | 1 | 0x53410370
PTOKlima1UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[1].UnitOnAlarmC | [6 empty] | 6157 | 1 | 0x53410380
PTOKlima2NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].NapacnoGesloAlarm | [6 empty] | 6157 | 1 | 0x53410390
PTOKlima2ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].ExtTempHumAlarm | [6 empty] | 6157 | 1 | 0x534103a0
PTOKlima2PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].PoplavniAlarm | [6 empty] | 6157 | 1 | 0x534103b0
PTOKlima2VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[2].VisokPritiskKompresor1 | [6 empty] | 6157 | 1 | 0x534103c0
PTOKlima2VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[2].VisokPritiskKompresor2 | [6 empty] | 6157 | 1 | 0x534103d0
PTOKlima2ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[2].ElVentilKompresor1ERR | [6 empty] | 6157 | 1 | 0x534103e0
PTOKlima2ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[2].ElVentilKompresor2ERR | [6 empty] | 6157 | 1 | 0x534103f0
PTOKlima2WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].WrongPhaseSeqAlarm | [6 empty] | 6157 | 1 | 0x53410400
PTOKlima2PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[2].PrekinjenLANalarm | [6 empty] | 6157 | 1 | 0x53410410
PTOKlima2CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[2].CWTempHighForDehum | [6 empty] | 6157 | 1 | 0x53410420
PTOKlima2CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[2].CWVentilErrOrLowFlow | [6 empty] | 6157 | 1 | 0x53410430
PTOKlima2NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaPriPretokuVode | [6 empty] | 6157 | 1 | 0x53410440
PTOKlima2CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[2].CWhighTemp | [6 empty] | 6157 | 1 | 0x53410450
PTOKlima2NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorHotWTemp | [6 empty] | 6157 | 1 | 0x53410460
PTOKlima2NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorCondWTemp | [6 empty] | 6157 | 1 | 0x53410470
PTOKlima2NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorCW | [6 empty] | 6157 | 1 | 0x53410480
PTOKlima2Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Kompresor3naMejiObrUr | [6 empty] | 6157 | 1 | 0x53410490
PTOKlima2Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Kompresor4naMejiObrUr | [6 empty] | 6157 | 1 | 0x534104a0
PTOKlima2ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].ZracniFilterNaMejiObrUr | [6 empty] | 6157 | 1 | 0x534104b0
PTOKlima2Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Grelec1naMejiObrUr | [6 empty] | 6157 | 1 | 0x534104c0
PTOKlima2Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Grelec2naMejiObrUr | [6 empty] | 6157 | 1 | 0x534104d0
PTOKlima2VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].VlazilecNaMejiObrUr | [6 empty] | 6157 | 1 | 0x534104e0
PTOKlima2AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].AirCondUnitNaMejiObrUr | [6 empty] | 6157 | 1 | 0x534104f0
PTOKlima2DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[2].DigIn2Alarm | [6 empty] | 6157 | 1 | 0x53410500
PTOKlima2DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[2].DigIn4Alarm | [6 empty] | 6157 | 1 | 0x53410510
PTOKlima2DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[2].DigIn6Alarm | [6 empty] | 6157 | 1 | 0x53410520
PTOKlima2VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].VlazilecGenAlarm | [6 empty] | 6157 | 1 | 0x53410530
PTOKlima2General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].General2ndLevAlarm | [6 empty] | 6157 | 1 | 0x53410540
PTOKlima2UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].UnitOnRotAlarm | [6 empty] | 6157 | 1 | 0x53410550
PTOKlima2UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[2].UnitOnAlarmA | [6 empty] | 6157 | 1 | 0x53410560
PTOKlima2UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[2].UnitOnAlarmB | [6 empty] | 6157 | 1 | 0x53410570
PTOKlima2UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[2].UnitOnAlarmC | [6 empty] | 6157 | 1 | 0x53410580
PTOKlima3NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].NapacnoGesloAlarm | [6 empty] | 6157 | 1 | 0x53410590
PTOKlima3ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].ExtTempHumAlarm | [6 empty] | 6157 | 1 | 0x534105a0
PTOKlima3PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].PoplavniAlarm | [6 empty] | 6157 | 1 | 0x534105b0
PTOKlima3VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[3].VisokPritiskKompresor1 | [6 empty] | 6157 | 1 | 0x534105c0
PTOKlima3VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[3].VisokPritiskKompresor2 | [6 empty] | 6157 | 1 | 0x534105d0
PTOKlima3ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[3].ElVentilKompresor1ERR | [6 empty] | 6157 | 1 | 0x534105e0
PTOKlima3ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[3].ElVentilKompresor2ERR | [6 empty] | 6157 | 1 | 0x534105f0
PTOKlima3WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].WrongPhaseSeqAlarm | [6 empty] | 6157 | 1 | 0x53410600
PTOKlima3PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[3].PrekinjenLANalarm | [6 empty] | 6157 | 1 | 0x53410610
PTOKlima3CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[3].CWTempHighForDehum | [6 empty] | 6157 | 1 | 0x53410620
PTOKlima3CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[3].CWVentilErrOrLowFlow | [6 empty] | 6157 | 1 | 0x53410630
PTOKlima3NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaPriPretokuVode | [6 empty] | 6157 | 1 | 0x53410640
PTOKlima3CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[3].CWhighTemp | [6 empty] | 6157 | 1 | 0x53410650
PTOKlima3NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorHotWTemp | [6 empty] | 6157 | 1 | 0x53410660
PTOKlima3NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorCondWTemp | [6 empty] | 6157 | 1 | 0x53410670
PTOKlima3NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorCW | [6 empty] | 6157 | 1 | 0x53410680
PTOKlima3Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Kompresor3naMejiObrUr | [6 empty] | 6157 | 1 | 0x53410690
PTOKlima3Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Kompresor4naMejiObrUr | [6 empty] | 6157 | 1 | 0x534106a0
PTOKlima3ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].ZracniFilterNaMejiObrUr | [6 empty] | 6157 | 1 | 0x534106b0
PTOKlima3Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Grelec1naMejiObrUr | [6 empty] | 6157 | 1 | 0x534106c0
PTOKlima3Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Grelec2naMejiObrUr | [6 empty] | 6157 | 1 | 0x534106d0
PTOKlima3VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].VlazilecNaMejiObrUr | [6 empty] | 6157 | 1 | 0x534106e0
PTOKlima3AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].AirCondUnitNaMejiObrUr | [6 empty] | 6157 | 1 | 0x534106f0
PTOKlima3DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[3].DigIn2Alarm | [6 empty] | 6157 | 1 | 0x53410700
PTOKlima3DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[3].DigIn4Alarm | [6 empty] | 6157 | 1 | 0x53410710
PTOKlima3DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[3].DigIn6Alarm | [6 empty] | 6157 | 1 | 0x53410720
PTOKlima3VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].VlazilecGenAlarm | [6 empty] | 6157 | 1 | 0x53410730
PTOKlima3General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].General2ndLevAlarm | [6 empty] | 6157 | 1 | 0x53410740
PTOKlima3UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].UnitOnRotAlarm | [6 empty] | 6157 | 1 | 0x53410750
PTOKlima3UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[3].UnitOnAlarmA | [6 empty] | 6157 | 1 | 0x53410760
PTOKlima3UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[3].UnitOnAlarmB | [6 empty] | 6157 | 1 | 0x53410770
PTOKlima3UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[3].UnitOnAlarmC | [6 empty] | 6157 | 1 | 0x53410780
PTOKlima4NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].NapacnoGesloAlarm | [6 empty] | 6157 | 1 | 0x53410790
PTOKlima4ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].ExtTempHumAlarm | [6 empty] | 6157 | 1 | 0x534107a0
PTOKlima4PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].PoplavniAlarm | [6 empty] | 6157 | 1 | 0x534107b0
PTOKlima4VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[4].VisokPritiskKompresor1 | [6 empty] | 6157 | 1 | 0x534107c0
PTOKlima4VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[4].VisokPritiskKompresor2 | [6 empty] | 6157 | 1 | 0x534107d0
PTOKlima4ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[4].ElVentilKompresor1ERR | [6 empty] | 6157 | 1 | 0x534107e0
PTOKlima4ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[4].ElVentilKompresor2ERR | [6 empty] | 6157 | 1 | 0x534107f0
PTOKlima4WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].WrongPhaseSeqAlarm | [6 empty] | 6157 | 1 | 0x53410800
PTOKlima4PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[4].PrekinjenLANalarm | [6 empty] | 6157 | 1 | 0x53410810
PTOKlima4CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[4].CWTempHighForDehum | [6 empty] | 6157 | 1 | 0x53410820
PTOKlima4CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[4].CWVentilErrOrLowFlow | [6 empty] | 6157 | 1 | 0x53410830
PTOKlima4NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaPriPretokuVode | [6 empty] | 6157 | 1 | 0x53410840
PTOKlima4CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[4].CWhighTemp | [6 empty] | 6157 | 1 | 0x53410850
PTOKlima4NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorHotWTemp | [6 empty] | 6157 | 1 | 0x53410860
PTOKlima4NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorCondWTemp | [6 empty] | 6157 | 1 | 0x53410870
PTOKlima4NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorCW | [6 empty] | 6157 | 1 | 0x53410880
PTOKlima4Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Kompresor3naMejiObrUr | [6 empty] | 6157 | 1 | 0x53410890
PTOKlima4Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Kompresor4naMejiObrUr | [6 empty] | 6157 | 1 | 0x534108a0
PTOKlima4ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].ZracniFilterNaMejiObrUr | [6 empty] | 6157 | 1 | 0x534108b0
PTOKlima4Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Grelec1naMejiObrUr | [6 empty] | 6157 | 1 | 0x534108c0
PTOKlima4Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Grelec2naMejiObrUr | [6 empty] | 6157 | 1 | 0x534108d0
PTOKlima4VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].VlazilecNaMejiObrUr | [6 empty] | 6157 | 1 | 0x534108e0
PTOKlima4AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].AirCondUnitNaMejiObrUr | [6 empty] | 6157 | 1 | 0x534108f0
PTOKlima4DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[4].DigIn2Alarm | [6 empty] | 6157 | 1 | 0x53410900
PTOKlima4DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[4].DigIn4Alarm | [6 empty] | 6157 | 1 | 0x53410910
PTOKlima4DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[4].DigIn6Alarm | [6 empty] | 6157 | 1 | 0x53410920
PTOKlima4VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].VlazilecGenAlarm | [6 empty] | 6157 | 1 | 0x53410930
PTOKlima4General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].General2ndLevAlarm | [6 empty] | 6157 | 1 | 0x53410940
PTOKlima4UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].UnitOnRotAlarm | [6 empty] | 6157 | 1 | 0x53410950
PTOKlima4UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[4].UnitOnAlarmA | [6 empty] | 6157 | 1 | 0x53410960
PTOKlima4UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[4].UnitOnAlarmB | [6 empty] | 6157 | 1 | 0x53410970
PTOKlima4UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[4].UnitOnAlarmC | [6 empty] | 6157 | 1 | 0x53410980
PTOKlima5NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].NapacnoGesloAlarm | [6 empty] | 6157 | 1 | 0x53410990
PTOKlima5ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].ExtTempHumAlarm | [6 empty] | 6157 | 1 | 0x534109a0
PTOKlima5PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].PoplavniAlarm | [6 empty] | 6157 | 1 | 0x534109b0
PTOKlima5VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[5].VisokPritiskKompresor1 | [6 empty] | 6157 | 1 | 0x534109c0
PTOKlima5VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[5].VisokPritiskKompresor2 | [6 empty] | 6157 | 1 | 0x534109d0
PTOKlima5ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[5].ElVentilKompresor1ERR | [6 empty] | 6157 | 1 | 0x534109e0
PTOKlima5ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[5].ElVentilKompresor2ERR | [6 empty] | 6157 | 1 | 0x534109f0
PTOKlima5WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].WrongPhaseSeqAlarm | [6 empty] | 6157 | 1 | 0x53410a00
PTOKlima5PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[5].PrekinjenLANalarm | [6 empty] | 6157 | 1 | 0x53410a10
PTOKlima5CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[5].CWTempHighForDehum | [6 empty] | 6157 | 1 | 0x53410a20
PTOKlima5CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[5].CWVentilErrOrLowFlow | [6 empty] | 6157 | 1 | 0x53410a30
PTOKlima5NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaPriPretokuVode | [6 empty] | 6157 | 1 | 0x53410a40
PTOKlima5CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[5].CWhighTemp | [6 empty] | 6157 | 1 | 0x53410a50
PTOKlima5NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorHotWTemp | [6 empty] | 6157 | 1 | 0x53410a60
PTOKlima5NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorCondWTemp | [6 empty] | 6157 | 1 | 0x53410a70
PTOKlima5NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorCW | [6 empty] | 6157 | 1 | 0x53410a80
PTOKlima5Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Kompresor3naMejiObrUr | [6 empty] | 6157 | 1 | 0x53410a90
PTOKlima5Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Kompresor4naMejiObrUr | [6 empty] | 6157 | 1 | 0x53410aa0
PTOKlima5ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].ZracniFilterNaMejiObrUr | [6 empty] | 6157 | 1 | 0x53410ab0
PTOKlima5Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Grelec1naMejiObrUr | [6 empty] | 6157 | 1 | 0x53410ac0
PTOKlima5Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Grelec2naMejiObrUr | [6 empty] | 6157 | 1 | 0x53410ad0
PTOKlima5VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].VlazilecNaMejiObrUr | [6 empty] | 6157 | 1 | 0x53410ae0
PTOKlima5AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].AirCondUnitNaMejiObrUr | [6 empty] | 6157 | 1 | 0x53410af0
PTOKlima5DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[5].DigIn2Alarm | [6 empty] | 6157 | 1 | 0x53410b00
PTOKlima5DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[5].DigIn4Alarm | [6 empty] | 6157 | 1 | 0x53410b10
PTOKlima5DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[5].DigIn6Alarm | [6 empty] | 6157 | 1 | 0x53410b20
PTOKlima5VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].VlazilecGenAlarm | [6 empty] | 6157 | 1 | 0x53410b30
PTOKlima5General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].General2ndLevAlarm | [6 empty] | 6157 | 1 | 0x53410b40
PTOKlima5UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].UnitOnRotAlarm | [6 empty] | 6157 | 1 | 0x53410b50
PTOKlima5UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[5].UnitOnAlarmA | [6 empty] | 6157 | 1 | 0x53410b60
PTOKlima5UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[5].UnitOnAlarmB | [6 empty] | 6157 | 1 | 0x53410b70
PTOKlima5UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[5].UnitOnAlarmC | [6 empty] | 6157 | 1 | 0x53410b80
PTOKlima6NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].NapacnoGesloAlarm | [6 empty] | 6157 | 1 | 0x53410b90
PTOKlima6ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].ExtTempHumAlarm | [6 empty] | 6157 | 1 | 0x53410ba0
PTOKlima6PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].PoplavniAlarm | [6 empty] | 6157 | 1 | 0x53410bb0
PTOKlima6VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[6].VisokPritiskKompresor1 | [6 empty] | 6157 | 1 | 0x53410bc0
PTOKlima6VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[6].VisokPritiskKompresor2 | [6 empty] | 6157 | 1 | 0x53410bd0
PTOKlima6ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[6].ElVentilKompresor1ERR | [6 empty] | 6157 | 1 | 0x53410be0
PTOKlima6ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[6].ElVentilKompresor2ERR | [6 empty] | 6157 | 1 | 0x53410bf0
PTOKlima6WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].WrongPhaseSeqAlarm | [6 empty] | 6157 | 1 | 0x53410c00
PTOKlima6PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[6].PrekinjenLANalarm | [6 empty] | 6157 | 1 | 0x53410c10
PTOKlima6CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[6].CWTempHighForDehum | [6 empty] | 6157 | 1 | 0x53410c20
PTOKlima6CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[6].CWVentilErrOrLowFlow | [6 empty] | 6157 | 1 | 0x53410c30
PTOKlima6NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaPriPretokuVode | [6 empty] | 6157 | 1 | 0x53410c40
PTOKlima6CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[6].CWhighTemp | [6 empty] | 6157 | 1 | 0x53410c50
PTOKlima6NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorHotWTemp | [6 empty] | 6157 | 1 | 0x53410c60
PTOKlima6NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorCondWTemp | [6 empty] | 6157 | 1 | 0x53410c70
PTOKlima6NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorCW | [6 empty] | 6157 | 1 | 0x53410c80
PTOKlima6Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Kompresor3naMejiObrUr | [6 empty] | 6157 | 1 | 0x53410c90
PTOKlima6Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Kompresor4naMejiObrUr | [6 empty] | 6157 | 1 | 0x53410ca0
PTOKlima6ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].ZracniFilterNaMejiObrUr | [6 empty] | 6157 | 1 | 0x53410cb0
PTOKlima6Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Grelec1naMejiObrUr | [6 empty] | 6157 | 1 | 0x53410cc0
PTOKlima6Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Grelec2naMejiObrUr | [6 empty] | 6157 | 1 | 0x53410cd0
PTOKlima6VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].VlazilecNaMejiObrUr | [6 empty] | 6157 | 1 | 0x53410ce0
PTOKlima6AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].AirCondUnitNaMejiObrUr | [6 empty] | 6157 | 1 | 0x53410cf0
PTOKlima6DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[6].DigIn2Alarm | [6 empty] | 6157 | 1 | 0x53410d00
PTOKlima6DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[6].DigIn4Alarm | [6 empty] | 6157 | 1 | 0x53410d10
PTOKlima6DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[6].DigIn6Alarm | [6 empty] | 6157 | 1 | 0x53410d20
PTOKlima6VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].VlazilecGenAlarm | [6 empty] | 6157 | 1 | 0x53410d30
PTOKlima6General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].General2ndLevAlarm | [6 empty] | 6157 | 1 | 0x53410d40
PTOKlima6UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].UnitOnRotAlarm | [6 empty] | 6157 | 1 | 0x53410d50
PTOKlima6UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[6].UnitOnAlarmA | [6 empty] | 6157 | 1 | 0x53410d60
PTOKlima6UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[6].UnitOnAlarmB | [6 empty] | 6157 | 1 | 0x53410d70
PTOKlima6UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[6].UnitOnAlarmC | [6 empty] | 6157 | 1 | 0x53410d80
PTOKlima1NapacnoGesloAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3850 | [8 empty] | 0x53410d90
PTOKlima1ExtTempHumAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3851 | [8 empty] | 0x53410da0
PTOKlima1PoplavniAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3852 | [8 empty] | 0x53410db0
PTOKlima1VisokPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk2 | D3853 | [8 empty] | 0x53410dc0
PTOKlima1VisokPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk2 | D3854 | [8 empty] | 0x53410dd0
PTOKlima1ElVentilKompresor1ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3855 | [8 empty] | 0x53410de0
PTOKlima1ElVentilKompresor2ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3856 | [8 empty] | 0x53410df0
PTOKlima1WrongPhaseSeqAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3857 | [8 empty] | 0x53410e00
PTOKlima1PrekinjenLANalarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3858 | [8 empty] | 0x53410e10
PTOKlima1CWTempHighForDehum_omogoci | DIGITAL | IOD_PTO_disk2 | D3859 | [8 empty] | 0x53410e20
PTOKlima1CWVentilErrOrLowFlow_omogoci | DIGITAL | IOD_PTO_disk2 | D3860 | [8 empty] | 0x53410e30
PTOKlima1NapakaPriPretokuVode_omogoci | DIGITAL | IOD_PTO_disk2 | D3861 | [8 empty] | 0x53410e40
PTOKlima1CWhighTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3862 | [8 empty] | 0x53410e50
PTOKlima1NapakaSenzorHotWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3863 | [8 empty] | 0x53410e60
PTOKlima1NapakaSenzorCondWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3864 | [8 empty] | 0x53410e70
PTOKlima1NapakaSenzorCW_omogoci | DIGITAL | IOD_PTO_disk2 | D3865 | [8 empty] | 0x53410e80
PTOKlima1Kompresor3naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3866 | [8 empty] | 0x53410e90
PTOKlima1Kompresor4naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3867 | [8 empty] | 0x53410ea0
PTOKlima1ZracniFilterNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3868 | [8 empty] | 0x53410eb0
PTOKlima1Grelec1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3869 | [8 empty] | 0x53410ec0
PTOKlima1Grelec2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3870 | [8 empty] | 0x53410ed0
PTOKlima1VlazilecNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3871 | [8 empty] | 0x53410ee0
PTOKlima1AirCondUnitNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3872 | [8 empty] | 0x53410ef0
PTOKlima1DigIn2Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3873 | [8 empty] | 0x53410f00
PTOKlima1DigIn4Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3874 | [8 empty] | 0x53410f10
PTOKlima1DigIn6Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3875 | [8 empty] | 0x53410f20
PTOKlima1VlazilecGenAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3876 | [8 empty] | 0x53410f30
PTOKlima1General2ndLevAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3877 | [8 empty] | 0x53410f40
PTOKlima1UnitOnRotAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3878 | [8 empty] | 0x53410f50
PTOKlima1UnitOnAlarmA_omogoci | DIGITAL | IOD_PTO_disk2 | D3879 | [8 empty] | 0x53410f60
PTOKlima1UnitOnAlarmB_omogoci | DIGITAL | IOD_PTO_disk2 | D3880 | [8 empty] | 0x53410f70
PTOKlima1UnitOnAlarmC_omogoci | DIGITAL | IOD_PTO_disk2 | D3881 | [8 empty] | 0x53410f80
PTOKlima2NapacnoGesloAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3882 | [8 empty] | 0x53410f90
PTOKlima2ExtTempHumAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3883 | [8 empty] | 0x53410fa0
PTOKlima2PoplavniAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3884 | [8 empty] | 0x53410fb0
PTOKlima2VisokPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk2 | D3885 | [8 empty] | 0x53410fc0
PTOKlima2VisokPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk2 | D3886 | [8 empty] | 0x53410fd0
PTOKlima2ElVentilKompresor1ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3887 | [8 empty] | 0x53410fe0
PTOKlima2ElVentilKompresor2ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3888 | [8 empty] | 0x53410ff0
PTOKlima2WrongPhaseSeqAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3889 | [8 empty] | 0x53411000
PTOKlima2PrekinjenLANalarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3890 | [8 empty] | 0x53411010
PTOKlima2CWTempHighForDehum_omogoci | DIGITAL | IOD_PTO_disk2 | D3891 | [8 empty] | 0x53411020
PTOKlima2CWVentilErrOrLowFlow_omogoci | DIGITAL | IOD_PTO_disk2 | D3892 | [8 empty] | 0x53411030
PTOKlima2NapakaPriPretokuVode_omogoci | DIGITAL | IOD_PTO_disk2 | D3893 | [8 empty] | 0x53411040
PTOKlima2CWhighTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3894 | [8 empty] | 0x53411050
PTOKlima2NapakaSenzorHotWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3895 | [8 empty] | 0x53411060
PTOKlima2NapakaSenzorCondWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3896 | [8 empty] | 0x53411070
PTOKlima2NapakaSenzorCW_omogoci | DIGITAL | IOD_PTO_disk2 | D3897 | [8 empty] | 0x53411080
PTOKlima2Kompresor3naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3898 | [8 empty] | 0x53411090
PTOKlima2Kompresor4naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3899 | [8 empty] | 0x534110a0
PTOKlima2ZracniFilterNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3900 | [8 empty] | 0x534110b0
PTOKlima2Grelec1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3901 | [8 empty] | 0x534110c0
PTOKlima2Grelec2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3902 | [8 empty] | 0x534110d0
PTOKlima2VlazilecNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3903 | [8 empty] | 0x534110e0
PTOKlima2AirCondUnitNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3904 | [8 empty] | 0x534110f0
PTOKlima2DigIn2Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3905 | [8 empty] | 0x53411100
PTOKlima2DigIn4Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3906 | [8 empty] | 0x53411110
PTOKlima2DigIn6Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3907 | [8 empty] | 0x53411120
PTOKlima2VlazilecGenAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3908 | [8 empty] | 0x53411130
PTOKlima2General2ndLevAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3909 | [8 empty] | 0x53411140
PTOKlima2UnitOnRotAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3910 | [8 empty] | 0x53411150
PTOKlima2UnitOnAlarmA_omogoci | DIGITAL | IOD_PTO_disk2 | D3911 | [8 empty] | 0x53411160
PTOKlima2UnitOnAlarmB_omogoci | DIGITAL | IOD_PTO_disk2 | D3912 | [8 empty] | 0x53411170
PTOKlima2UnitOnAlarmC_omogoci | DIGITAL | IOD_PTO_disk2 | D3913 | [8 empty] | 0x53411180
PTOKlima3NapacnoGesloAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3914 | [8 empty] | 0x53411190
PTOKlima3ExtTempHumAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3915 | [8 empty] | 0x534111a0
PTOKlima3PoplavniAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3916 | [8 empty] | 0x534111b0
PTOKlima3VisokPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk2 | D3917 | [8 empty] | 0x534111c0
PTOKlima3VisokPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk2 | D3918 | [8 empty] | 0x534111d0
PTOKlima3ElVentilKompresor1ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3919 | [8 empty] | 0x534111e0
PTOKlima3ElVentilKompresor2ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3920 | [8 empty] | 0x534111f0
PTOKlima3WrongPhaseSeqAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3921 | [8 empty] | 0x53411200
PTOKlima3PrekinjenLANalarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3922 | [8 empty] | 0x53411210
PTOKlima3CWTempHighForDehum_omogoci | DIGITAL | IOD_PTO_disk2 | D3923 | [8 empty] | 0x53411220
PTOKlima3CWVentilErrOrLowFlow_omogoci | DIGITAL | IOD_PTO_disk2 | D3924 | [8 empty] | 0x53411230
PTOKlima3NapakaPriPretokuVode_omogoci | DIGITAL | IOD_PTO_disk2 | D3925 | [8 empty] | 0x53411240
PTOKlima3CWhighTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3926 | [8 empty] | 0x53411250
PTOKlima3NapakaSenzorHotWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3927 | [8 empty] | 0x53411260
PTOKlima3NapakaSenzorCondWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3928 | [8 empty] | 0x53411270
PTOKlima3NapakaSenzorCW_omogoci | DIGITAL | IOD_PTO_disk2 | D3929 | [8 empty] | 0x53411280
PTOKlima3Kompresor3naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3930 | [8 empty] | 0x53411290
PTOKlima3Kompresor4naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3931 | [8 empty] | 0x534112a0
PTOKlima3ZracniFilterNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3932 | [8 empty] | 0x534112b0
PTOKlima3Grelec1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3933 | [8 empty] | 0x534112c0
PTOKlima3Grelec2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3934 | [8 empty] | 0x534112d0
PTOKlima3VlazilecNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3935 | [8 empty] | 0x534112e0
PTOKlima3AirCondUnitNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3936 | [8 empty] | 0x534112f0
PTOKlima3DigIn2Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3937 | [8 empty] | 0x53411300
PTOKlima3DigIn4Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3938 | [8 empty] | 0x53411310
PTOKlima3DigIn6Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3939 | [8 empty] | 0x53411320
PTOKlima3VlazilecGenAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3940 | [8 empty] | 0x53411330
PTOKlima3General2ndLevAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3941 | [8 empty] | 0x53411340
PTOKlima3UnitOnRotAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3942 | [8 empty] | 0x53411350
PTOKlima3UnitOnAlarmA_omogoci | DIGITAL | IOD_PTO_disk2 | D3943 | [8 empty] | 0x53411360
PTOKlima3UnitOnAlarmB_omogoci | DIGITAL | IOD_PTO_disk2 | D3944 | [8 empty] | 0x53411370
PTOKlima3UnitOnAlarmC_omogoci | DIGITAL | IOD_PTO_disk2 | D3945 | [8 empty] | 0x53411380
PTOKlima4NapacnoGesloAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3946 | [8 empty] | 0x53411390
PTOKlima4ExtTempHumAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3947 | [8 empty] | 0x534113a0
PTOKlima4PoplavniAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3948 | [8 empty] | 0x534113b0
PTOKlima4VisokPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk2 | D3949 | [8 empty] | 0x534113c0
PTOKlima4VisokPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk2 | D3950 | [8 empty] | 0x534113d0
PTOKlima4ElVentilKompresor1ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3951 | [8 empty] | 0x534113e0
PTOKlima4ElVentilKompresor2ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3952 | [8 empty] | 0x534113f0
PTOKlima4WrongPhaseSeqAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3953 | [8 empty] | 0x53411400
PTOKlima4PrekinjenLANalarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3954 | [8 empty] | 0x53411410
PTOKlima4CWTempHighForDehum_omogoci | DIGITAL | IOD_PTO_disk2 | D3955 | [8 empty] | 0x53411420
PTOKlima4CWVentilErrOrLowFlow_omogoci | DIGITAL | IOD_PTO_disk2 | D3956 | [8 empty] | 0x53411430
PTOKlima4NapakaPriPretokuVode_omogoci | DIGITAL | IOD_PTO_disk2 | D3957 | [8 empty] | 0x53411440
PTOKlima4CWhighTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3958 | [8 empty] | 0x53411450
PTOKlima4NapakaSenzorHotWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3959 | [8 empty] | 0x53411460
PTOKlima4NapakaSenzorCondWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3960 | [8 empty] | 0x53411470
PTOKlima4NapakaSenzorCW_omogoci | DIGITAL | IOD_PTO_disk2 | D3961 | [8 empty] | 0x53411480
PTOKlima4Kompresor3naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3962 | [8 empty] | 0x53411490
PTOKlima4Kompresor4naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3963 | [8 empty] | 0x534114a0
PTOKlima4ZracniFilterNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3964 | [8 empty] | 0x534114b0
PTOKlima4Grelec1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3965 | [8 empty] | 0x534114c0
PTOKlima4Grelec2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3966 | [8 empty] | 0x534114d0
PTOKlima4VlazilecNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3967 | [8 empty] | 0x534114e0
PTOKlima4AirCondUnitNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3968 | [8 empty] | 0x534114f0
PTOKlima4DigIn2Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3969 | [8 empty] | 0x53411500
PTOKlima4DigIn4Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3970 | [8 empty] | 0x53411510
PTOKlima4DigIn6Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3971 | [8 empty] | 0x53411520
PTOKlima4VlazilecGenAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3972 | [8 empty] | 0x53411530
PTOKlima4General2ndLevAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3973 | [8 empty] | 0x53411540
PTOKlima4UnitOnRotAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3974 | [8 empty] | 0x53411550
PTOKlima4UnitOnAlarmA_omogoci | DIGITAL | IOD_PTO_disk2 | D3975 | [8 empty] | 0x53411560
PTOKlima4UnitOnAlarmB_omogoci | DIGITAL | IOD_PTO_disk2 | D3976 | [8 empty] | 0x53411570
PTOKlima4UnitOnAlarmC_omogoci | DIGITAL | IOD_PTO_disk2 | D3977 | [8 empty] | 0x53411580
PTOKlima5NapacnoGesloAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3978 | [8 empty] | 0x53411590
PTOKlima5ExtTempHumAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3979 | [8 empty] | 0x534115a0
PTOKlima5PoplavniAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3980 | [8 empty] | 0x534115b0
PTOKlima5VisokPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk2 | D3981 | [8 empty] | 0x534115c0
PTOKlima5VisokPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk2 | D3982 | [8 empty] | 0x534115d0
PTOKlima5ElVentilKompresor1ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3983 | [8 empty] | 0x534115e0
PTOKlima5ElVentilKompresor2ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3984 | [8 empty] | 0x534115f0
PTOKlima5WrongPhaseSeqAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3985 | [8 empty] | 0x53411600
PTOKlima5PrekinjenLANalarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3986 | [8 empty] | 0x53411610
PTOKlima5CWTempHighForDehum_omogoci | DIGITAL | IOD_PTO_disk2 | D3987 | [8 empty] | 0x53411620
PTOKlima5CWVentilErrOrLowFlow_omogoci | DIGITAL | IOD_PTO_disk2 | D3988 | [8 empty] | 0x53411630
PTOKlima5NapakaPriPretokuVode_omogoci | DIGITAL | IOD_PTO_disk2 | D3989 | [8 empty] | 0x53411640
PTOKlima5CWhighTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3990 | [8 empty] | 0x53411650
PTOKlima5NapakaSenzorHotWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3991 | [8 empty] | 0x53411660
PTOKlima5NapakaSenzorCondWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3992 | [8 empty] | 0x53411670
PTOKlima5NapakaSenzorCW_omogoci | DIGITAL | IOD_PTO_disk2 | D3993 | [8 empty] | 0x53411680
PTOKlima5Kompresor3naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3994 | [8 empty] | 0x53411690
PTOKlima5Kompresor4naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3995 | [8 empty] | 0x534116a0
PTOKlima5ZracniFilterNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3996 | [8 empty] | 0x534116b0
PTOKlima5Grelec1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3997 | [8 empty] | 0x534116c0
PTOKlima5Grelec2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3998 | [8 empty] | 0x534116d0
PTOKlima5VlazilecNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3999 | [8 empty] | 0x534116e0
PTOKlima5AirCondUnitNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D4000 | [8 empty] | 0x534116f0
PTOKlima5DigIn2Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4001 | [8 empty] | 0x53411700
PTOKlima5DigIn4Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4002 | [8 empty] | 0x53411710
PTOKlima5DigIn6Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4003 | [8 empty] | 0x53411720
PTOKlima5VlazilecGenAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4004 | [8 empty] | 0x53411730
PTOKlima5General2ndLevAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4005 | [8 empty] | 0x53411740
PTOKlima5UnitOnRotAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4006 | [8 empty] | 0x53411750
PTOKlima5UnitOnAlarmA_omogoci | DIGITAL | IOD_PTO_disk2 | D4007 | [8 empty] | 0x53411760
PTOKlima5UnitOnAlarmB_omogoci | DIGITAL | IOD_PTO_disk2 | D4008 | [8 empty] | 0x53411770
PTOKlima5UnitOnAlarmC_omogoci | DIGITAL | IOD_PTO_disk2 | D4009 | [8 empty] | 0x53411780
PTOKlima6NapacnoGesloAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4010 | [8 empty] | 0x53411790
PTOKlima6ExtTempHumAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4011 | [8 empty] | 0x534117a0
PTOKlima6PoplavniAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4012 | [8 empty] | 0x534117b0
PTOKlima6VisokPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk2 | D4013 | [8 empty] | 0x534117c0
PTOKlima6VisokPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk2 | D4014 | [8 empty] | 0x534117d0
PTOKlima6ElVentilKompresor1ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D4015 | [8 empty] | 0x534117e0
PTOKlima6ElVentilKompresor2ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D4016 | [8 empty] | 0x534117f0
PTOKlima6WrongPhaseSeqAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4017 | [8 empty] | 0x53411800
PTOKlima6PrekinjenLANalarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4018 | [8 empty] | 0x53411810
PTOKlima6CWTempHighForDehum_omogoci | DIGITAL | IOD_PTO_disk2 | D4019 | [8 empty] | 0x53411820
PTOKlima6CWVentilErrOrLowFlow_omogoci | DIGITAL | IOD_PTO_disk2 | D4020 | [8 empty] | 0x53411830
PTOKlima6NapakaPriPretokuVode_omogoci | DIGITAL | IOD_PTO_disk2 | D4021 | [8 empty] | 0x53411840
PTOKlima6CWhighTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D4022 | [8 empty] | 0x53411850
PTOKlima6NapakaSenzorHotWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D4023 | [8 empty] | 0x53411860
PTOKlima6NapakaSenzorCondWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D4024 | [8 empty] | 0x53411870
PTOKlima6NapakaSenzorCW_omogoci | DIGITAL | IOD_PTO_disk2 | D4025 | [8 empty] | 0x53411880
PTOKlima6Kompresor3naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D4026 | [8 empty] | 0x53411890
PTOKlima6Kompresor4naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D4027 | [8 empty] | 0x534118a0
PTOKlima6ZracniFilterNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D4028 | [8 empty] | 0x534118b0
PTOKlima6Grelec1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D4029 | [8 empty] | 0x534118c0
PTOKlima6Grelec2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D4030 | [8 empty] | 0x534118d0
PTOKlima6VlazilecNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D4031 | [8 empty] | 0x534118e0
PTOKlima6AirCondUnitNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D4032 | [8 empty] | 0x534118f0
PTOKlima6DigIn2Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4033 | [8 empty] | 0x53411900
PTOKlima6DigIn4Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4034 | [8 empty] | 0x53411910
PTOKlima6DigIn6Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4035 | [8 empty] | 0x53411920
PTOKlima6VlazilecGenAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4036 | [8 empty] | 0x53411930
PTOKlima6General2ndLevAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4037 | [8 empty] | 0x53411940
PTOKlima6UnitOnRotAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4038 | [8 empty] | 0x53411950
PTOKlima6UnitOnAlarmA_omogoci | DIGITAL | IOD_PTO_disk2 | D4039 | [8 empty] | 0x53411960
PTOKlima6UnitOnAlarmB_omogoci | DIGITAL | IOD_PTO_disk2 | D4040 | [8 empty] | 0x53411970
PTOKlima6UnitOnAlarmC_omogoci | DIGITAL | IOD_PTO_disk2 | D4041 | [8 empty] | 0x53411980
PTOKlima1NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[1].NastTempHlajenje | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x53411990
PTOKlima2NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[2].NastTempHlajenje | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x53411991
PTOKlima3NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[3].NastTempHlajenje | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x53411992
PTOKlima4NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[4].NastTempHlajenje | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x53411993
PTOKlima5NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[5].NastTempHlajenje | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x53411994
PTOKlima6NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[6].NastTempHlajenje | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x53411995
PTOKlima1NastTempGretje | REAL | IOD_PTO | PTO:.Klima[1].NastTempGretje | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x53411996
PTOKlima2NastTempGretje | REAL | IOD_PTO | PTO:.Klima[2].NastTempGretje | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x53411997
PTOKlima3NastTempGretje | REAL | IOD_PTO | PTO:.Klima[3].NastTempGretje | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x53411998
PTOKlima4NastTempGretje | REAL | IOD_PTO | PTO:.Klima[4].NastTempGretje | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x53411999
PTOKlima5NastTempGretje | REAL | IOD_PTO | PTO:.Klima[5].NastTempGretje | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5341199a
PTOKlima6NastTempGretje | REAL | IOD_PTO | PTO:.Klima[6].NastTempGretje | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5341199b
PTOKlima1TempHladneVode | REAL | IOD_PTO | PTO:.Klima[1].TempHladneVode | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5341199c
PTOKlima2TempHladneVode | REAL | IOD_PTO | PTO:.Klima[2].TempHladneVode | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5341199d
PTOKlima3TempHladneVode | REAL | IOD_PTO | PTO:.Klima[3].TempHladneVode | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5341199e
PTOKlima4TempHladneVode | REAL | IOD_PTO | PTO:.Klima[4].TempHladneVode | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x5341199f
PTOKlima5TempHladneVode | REAL | IOD_PTO | PTO:.Klima[5].TempHladneVode | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x534119a0
PTOKlima6TempHladneVode | REAL | IOD_PTO | PTO:.Klima[6].TempHladneVode | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x534119a1
PTOKlima1TempTopleVode | REAL | IOD_PTO | PTO:.Klima[1].TempTopleVode | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x534119a2
PTOKlima2TempTopleVode | REAL | IOD_PTO | PTO:.Klima[2].TempTopleVode | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x534119a3
PTOKlima3TempTopleVode | REAL | IOD_PTO | PTO:.Klima[3].TempTopleVode | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x534119a4
PTOKlima4TempTopleVode | REAL | IOD_PTO | PTO:.Klima[4].TempTopleVode | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x534119a5
PTOKlima5TempTopleVode | REAL | IOD_PTO | PTO:.Klima[5].TempTopleVode | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x534119a6
PTOKlima6TempTopleVode | REAL | IOD_PTO | PTO:.Klima[6].TempTopleVode | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x534119a7
PTOKlima1Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[1].Komp1On | [6 empty] | 6157 | 1 | 0x534119b0
PTOKlima1Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[1].Komp2On | [6 empty] | 6157 | 1 | 0x534119c0
PTOKlima1Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[1].Komp3On | [6 empty] | 6157 | 1 | 0x534119d0
PTOKlima1Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[1].Komp4On | [6 empty] | 6157 | 1 | 0x534119e0
PTOKlima2Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[2].Komp1On | [6 empty] | 6157 | 1 | 0x534119f0
PTOKlima2Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[2].Komp2On | [6 empty] | 6157 | 1 | 0x53411a00
PTOKlima2Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[2].Komp3On | [6 empty] | 6157 | 1 | 0x53411a10
PTOKlima2Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[2].Komp4On | [6 empty] | 6157 | 1 | 0x53411a20
PTOKlima3Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[3].Komp1On | [6 empty] | 6157 | 1 | 0x53411a30
PTOKlima3Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[3].Komp2On | [6 empty] | 6157 | 1 | 0x53411a40
PTOKlima3Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[3].Komp3On | [6 empty] | 6157 | 1 | 0x53411a50
PTOKlima3Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[3].Komp4On | [6 empty] | 6157 | 1 | 0x53411a60
PTOKlima4Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[4].Komp1On | [6 empty] | 6157 | 1 | 0x53411a70
PTOKlima4Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[4].Komp2On | [6 empty] | 6157 | 1 | 0x53411a80
PTOKlima4Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[4].Komp3On | [6 empty] | 6157 | 1 | 0x53411a90
PTOKlima4Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[4].Komp4On | [6 empty] | 6157 | 1 | 0x53411aa0
PTOKlima5Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[5].Komp1On | [6 empty] | 6157 | 1 | 0x53411ab0
PTOKlima5Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[5].Komp2On | [6 empty] | 6157 | 1 | 0x53411ac0
PTOKlima5Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[5].Komp3On | [6 empty] | 6157 | 1 | 0x53411ad0
PTOKlima5Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[5].Komp4On | [6 empty] | 6157 | 1 | 0x53411ae0
PTOKlima6Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[6].Komp1On | [6 empty] | 6157 | 1 | 0x53411af0
PTOKlima6Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[6].Komp2On | [6 empty] | 6157 | 1 | 0x53411b00
PTOKlima6Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[6].Komp3On | [6 empty] | 6157 | 1 | 0x53411b10
PTOKlima6Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[6].Komp4On | [6 empty] | 6157 | 1 | 0x53411b20
PTOKlima1GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[1].GretjeStopnja1 | [6 empty] | 6157 | 1 | 0x53411b30
PTOKlima1GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[1].GretjeStopnja2 | [6 empty] | 6157 | 1 | 0x53411b40
PTOKlima1GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[1].GretjeStopnja3 | [6 empty] | 6157 | 1 | 0x53411b50
PTOKlima2GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[2].GretjeStopnja1 | [6 empty] | 6157 | 1 | 0x53411b60
PTOKlima2GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[2].GretjeStopnja2 | [6 empty] | 6157 | 1 | 0x53411b70
PTOKlima2GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[2].GretjeStopnja3 | [6 empty] | 6157 | 1 | 0x53411b80
PTOKlima3GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[3].GretjeStopnja1 | [6 empty] | 6157 | 1 | 0x53411b90
PTOKlima3GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[3].GretjeStopnja2 | [6 empty] | 6157 | 1 | 0x53411ba0
PTOKlima3GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[3].GretjeStopnja3 | [6 empty] | 6157 | 1 | 0x53411bb0
PTOKlima4GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[4].GretjeStopnja1 | [6 empty] | 6157 | 1 | 0x53411bc0
PTOKlima4GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[4].GretjeStopnja2 | [6 empty] | 6157 | 1 | 0x53411bd0
PTOKlima4GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[4].GretjeStopnja3 | [6 empty] | 6157 | 1 | 0x53411be0
PTOKlima5GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[5].GretjeStopnja1 | [6 empty] | 6157 | 1 | 0x53411bf0
PTOKlima5GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[5].GretjeStopnja2 | [6 empty] | 6157 | 1 | 0x53411c00
PTOKlima5GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[5].GretjeStopnja3 | [6 empty] | 6157 | 1 | 0x53411c10
PTOKlima6GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[6].GretjeStopnja1 | [6 empty] | 6157 | 1 | 0x53411c20
PTOKlima6GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[6].GretjeStopnja2 | [6 empty] | 6157 | 1 | 0x53411c30
PTOKlima6GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[6].GretjeStopnja3 | [6 empty] | 6157 | 1 | 0x53411c40
PTOKlima1HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[1].HotGasOn | [6 empty] | 6157 | 1 | 0x53411c50
PTOKlima2HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[2].HotGasOn | [6 empty] | 6157 | 1 | 0x53411c60
PTOKlima3HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[3].HotGasOn | [6 empty] | 6157 | 1 | 0x53411c70
PTOKlima4HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[4].HotGasOn | [6 empty] | 6157 | 1 | 0x53411c80
PTOKlima5HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[5].HotGasOn | [6 empty] | 6157 | 1 | 0x53411c90
PTOKlima6HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[6].HotGasOn | [6 empty] | 6157 | 1 | 0x53411ca0
PTOKlima1EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[1].EmergencyWorking | [6 empty] | 6157 | 1 | 0x53411cb0
PTOKlima2EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[2].EmergencyWorking | [6 empty] | 6157 | 1 | 0x53411cc0
PTOKlima3EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[3].EmergencyWorking | [6 empty] | 6157 | 1 | 0x53411cd0
PTOKlima4EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[4].EmergencyWorking | [6 empty] | 6157 | 1 | 0x53411ce0
PTOKlima5EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[5].EmergencyWorking | [6 empty] | 6157 | 1 | 0x53411cf0
PTOKlima6EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[6].EmergencyWorking | [6 empty] | 6157 | 1 | 0x53411d00
PTODI_A1Q01_DovUpsB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q01_DovUpsB_ON | [6 empty] | 6157 | 1 | 0x53411d10
PTODI_A1Q0_GlavnoStiB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q0_GlavnoStiB_ON | [6 empty] | 6157 | 1 | 0x53411d20
PTODI_A1Q11_OdcUpsB_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q11_OdcUpsB_IZP | [6 empty] | 6157 | 1 | 0x53411d30
PTODI_A1Q11_OdcUpsB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q11_OdcUpsB_ON | [6 empty] | 6157 | 1 | 0x53411d40
PTODI_A1Q12_OdcByUpsB_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q12_OdcByUpsB_IZP | [6 empty] | 6157 | 1 | 0x53411d50
PTODI_A1Q12_OdcByUpsB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q12_OdcByUpsB_ON | [6 empty] | 6157 | 1 | 0x53411d60
PTODI_A1Q13_OdcByB_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q13_OdcByB_IZP | [6 empty] | 6157 | 1 | 0x53411d70
PTOZamikVklopa | REAL | IOD_PTO | PTO:.ZamikVklopa | [6 empty] | 6157 | 1 | 0x53411d80
PTOServer_B_Izpad | DIGITAL | IOD_PTO_disk2 | D4042 | [8 empty] | 0x53411d90
PTOServer_A_Izpad | DIGITAL | IOD_PTO_disk2 | D4043 | [8 empty] | 0x53411da0
PTO_ComSCADA_stevec3 | INT | IOD_PTO_disk | I4002 | [8 empty] | 0x53411db0
PTO_ComSCADA_stevec4 | INT | IOD_PTO_disk | I4004 | [8 empty] | 0x53411db1
PTOErrCommScada_omogoci2 | DIGITAL | IOD_PTO_disk2 | D4044 | [8 empty] | 0x53411dc0
PTOErrCommScada2 | DIGITAL | IOD_PTO | PTO:.ErrCommScada2 | [6 empty] | 6157 | 1 | 0x53411dd0
PTOComSCADA2 | DIGITAL | IOD_PTO | PTO:.ComSCADA2 | [6 empty] | 6157 | 1 | 0x53411de0
PTOComSCADA3 | DIGITAL | IOD_PTO | PTO:.ComSCADA3 | [6 empty] | 6157 | 1 | 0x53411df0
PTOUserLoggedIn_mem | DIGITAL | IOD_PTO_disk2 | D4045 | [8 empty] | 0x53411e00
PTOkom_nast_cas_izpada | UINT | IOD_PTO | PTO:.kom_nast_cas_izpada | [6 empty] | 6157 | 1 | 0x53411e10
PTOKlima1Komp1On_omogoci | DIGITAL | IOD_PTO_disk2 | D4046 | [8 empty] | 0x53411e20
PTOKlima1Komp2On_omogoci | DIGITAL | IOD_PTO_disk2 | D4047 | [8 empty] | 0x53411e30
PTOKlima2Komp1On_omogoci | DIGITAL | IOD_PTO_disk2 | D4048 | [8 empty] | 0x53411e40
PTOKlima2Komp2On_omogoci | DIGITAL | IOD_PTO_disk2 | D4049 | [8 empty] | 0x53411e50
PTOKlima3Komp1On_omogoci | DIGITAL | IOD_PTO_disk2 | D4050 | [8 empty] | 0x53411e60
PTOKlima3Komp2On_omogoci | DIGITAL | IOD_PTO_disk2 | D4051 | [8 empty] | 0x53411e70
PTOKlima4Komp1On_omogoci | DIGITAL | IOD_PTO_disk2 | D4052 | [8 empty] | 0x53411e80
PTOKlima4Komp2On_omogoci | DIGITAL | IOD_PTO_disk2 | D4053 | [8 empty] | 0x53411e90
PTOKlima5Komp1On_omogoci | DIGITAL | IOD_PTO_disk2 | D4054 | [8 empty] | 0x53411ea0
PTOKlima5Komp2On_omogoci | DIGITAL | IOD_PTO_disk2 | D4055 | [8 empty] | 0x53411eb0
PTOKlima6Komp1On_omogoci | DIGITAL | IOD_PTO_disk2 | D4056 | [8 empty] | 0x53411ec0
PTOKlima6Komp2On_omogoci | DIGITAL | IOD_PTO_disk2 | D4057 | [8 empty] | 0x53411ed0
PTOKlima1GretjeStopnja1_omogoci | DIGITAL | IOD_PTO_disk2 | D4058 | [8 empty] | 0x53411ee0
PTOKlima1GretjeStopnja2_omogoci | DIGITAL | IOD_PTO_disk2 | D4059 | [8 empty] | 0x53411ef0
PTOKlima1GretjeStopnja3_omogoci | DIGITAL | IOD_PTO_disk2 | D4060 | [8 empty] | 0x53411f00
PTOKlima2GretjeStopnja1_omogoci | DIGITAL | IOD_PTO_disk2 | D4061 | [8 empty] | 0x53411f10
PTOKlima2GretjeStopnja2_omogoci | DIGITAL | IOD_PTO_disk2 | D4062 | [8 empty] | 0x53411f20
PTOKlima2GretjeStopnja3_omogoci | DIGITAL | IOD_PTO_disk2 | D4063 | [8 empty] | 0x53411f30
PTOKlima3GretjeStopnja1_omogoci | DIGITAL | IOD_PTO_disk2 | D4064 | [8 empty] | 0x53411f40
PTOKlima3GretjeStopnja2_omogoci | DIGITAL | IOD_PTO_disk2 | D4065 | [8 empty] | 0x53411f50
PTOKlima3GretjeStopnja3_omogoci | DIGITAL | IOD_PTO_disk2 | D4066 | [8 empty] | 0x53411f60
PTOKlima4GretjeStopnja1_omogoci | DIGITAL | IOD_PTO_disk2 | D4067 | [8 empty] | 0x53411f70
PTOKlima4GretjeStopnja2_omogoci | DIGITAL | IOD_PTO_disk2 | D4068 | [8 empty] | 0x53411f80
PTOKlima4GretjeStopnja3_omogoci | DIGITAL | IOD_PTO_disk2 | D4069 | [8 empty] | 0x53411f90
PTOKlima5GretjeStopnja1_omogoci | DIGITAL | IOD_PTO_disk2 | D4070 | [8 empty] | 0x53411fa0
PTOKlima5GretjeStopnja2_omogoci | DIGITAL | IOD_PTO_disk2 | D4071 | [8 empty] | 0x53411fb0
PTOKlima5GretjeStopnja3_omogoci | DIGITAL | IOD_PTO_disk2 | D4072 | [8 empty] | 0x53411fc0
PTOKlima6GretjeStopnja1_omogoci | DIGITAL | IOD_PTO_disk2 | D4073 | [8 empty] | 0x53411fd0
PTOKlima6GretjeStopnja2_omogoci | DIGITAL | IOD_PTO_disk2 | D4074 | [8 empty] | 0x53411fe0
PTOKlima6GretjeStopnja3_omogoci | DIGITAL | IOD_PTO_disk2 | D4075 | [8 empty] | 0x53411ff0
PTOKlima1Razvlazevanje_omogoci | DIGITAL | IOD_PTO_disk2 | D4076 | [8 empty] | 0x53412000
PTOKlima2Razvlazevanje_omogoci | DIGITAL | IOD_PTO_disk2 | D4077 | [8 empty] | 0x53412010
PTOKlima3Razvlazevanje_omogoci | DIGITAL | IOD_PTO_disk2 | D4078 | [8 empty] | 0x53412020
PTOKlima4Razvlazevanje_omogoci | DIGITAL | IOD_PTO_disk2 | D4079 | [8 empty] | 0x53412030
PTOKlima5Razvlazevanje_omogoci | DIGITAL | IOD_PTO_disk2 | D4080 | [8 empty] | 0x53412040
PTOKlima6Razvlazevanje_omogoci | DIGITAL | IOD_PTO_disk2 | D4081 | [8 empty] | 0x53412050
PTOKlima1Vlazenje_omogoci | DIGITAL | IOD_PTO_disk2 | D4082 | [8 empty] | 0x53412060
PTOKlima2Vlazenje_omogoci | DIGITAL | IOD_PTO_disk2 | D4083 | [8 empty] | 0x53412070
PTOKlima3Vlazenje_omogoci | DIGITAL | IOD_PTO_disk2 | D4084 | [8 empty] | 0x53412080
PTOKlima4Vlazenje_omogoci | DIGITAL | IOD_PTO_disk2 | D4085 | [8 empty] | 0x53412090
PTOKlima5Vlazenje_omogoci | DIGITAL | IOD_PTO_disk2 | D4086 | [8 empty] | 0x534120a0
PTOKlima6Vlazenje_omogoci | DIGITAL | IOD_PTO_disk2 | D4087 | [8 empty] | 0x534120b0
PTOKlima1UnitOnOff_omogoci | DIGITAL | IOD_PTO_disk2 | D4088 | [8 empty] | 0x534120c0
PTOKlima2UnitOnOff_omogoci | DIGITAL | IOD_PTO_disk2 | D4089 | [8 empty] | 0x534120d0
PTOKlima3UnitOnOff_omogoci | DIGITAL | IOD_PTO_disk2 | D4090 | [8 empty] | 0x534120e0
PTOKlima4UnitOnOff_omogoci | DIGITAL | IOD_PTO_disk2 | D4091 | [8 empty] | 0x534120f0
PTOKlima5UnitOnOff_omogoci | DIGITAL | IOD_PTO_disk2 | D4092 | [8 empty] | 0x53412100
PTOKlima6UnitOnOff_omogoci | DIGITAL | IOD_PTO_disk2 | D4093 | [8 empty] | 0x53412110

## variable_1
PTOAlarmGenComm | DIGITAL | IOD_PTO | PTO:.AlarmGenComm
PTOAlarmGenKlima1 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[1]
PTOAlarmGenKlima2 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[2]
PTOAlarmGenKlima3 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[3]
PTOAlarmGenKlima4 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[4]
PTOAlarmGenKlima5 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[5]
PTOAlarmGenKlima6 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[6]
PTOAlarmGenPMM | DIGITAL | IOD_PTO | PTO:.AlarmGenPMM
PTOAlarmGenRest | DIGITAL | IOD_PTO | PTO:.AlarmGenRest
PTOAlarmGenSenzor | DIGITAL | IOD_PTO | PTO:.AlarmGenSenzor
PTOAlarmGenStikala | DIGITAL | IOD_PTO | PTO:.AlarmGenStikala
PTOAlarmGenTemp | DIGITAL | IOD_PTO | PTO:.AlarmGenTemp
PTOAlarmGenUPS1 | DIGITAL | IOD_PTO | PTO:.AlarmGenUPS1
PTOAlarmGenUPS2 | DIGITAL | IOD_PTO | PTO:.AlarmGenUPS2
PTOComSCADA | DIGITAL | IOD_PTO | PTO:.ComSCADA
PTOComSCADA1 | DIGITAL | IOD_PTO | PTO:.ComSCADA1
PTODate_Time0 | STRING | IOD_PTO | PTO:.Date_Time[0]
PTODate_Time1 | STRING | IOD_PTO | PTO:.Date_Time[1]
PTODate_Time2 | STRING | IOD_PTO | PTO:.Date_Time[2]
PTODate_Time3 | STRING | IOD_PTO | PTO:.Date_Time[3]
PTODateTimeDan | INT | IOD_PTO | PTO:.DateTime.Dan | BYTE
PTODateTimeLeto | INT | IOD_PTO | PTO:.DateTime.Leto | BYTE
PTODateTimeMesec | INT | IOD_PTO | PTO:.DateTime.Mesec | BYTE
PTODateTimeMinuta | INT | IOD_PTO | PTO:.DateTime.Minuta | BYTE
PTODateTimeSekunda | INT | IOD_PTO | PTO:.DateTime.Sekunda | BYTE
PTODateTimeUra | INT | IOD_PTO | PTO:.DateTime.Ura | BYTE
PTODI_A1Q01_DovUpsA_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q01_DovUpsA_ON
PTODI_A1Q02_DovByA_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q02_DovByA_ON
PTODI_A1Q0_GlavnoSti_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q0_GlavnoSti_ON
PTODI_A1Q11_OdcUpsA_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q11_OdcUpsA_IZP
PTODI_A1Q11_OdcUpsA_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q11_OdcUpsA_ON
PTODI_A1Q12_OdcByUpsA_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q12_OdcByUpsA_IZP
PTODI_A1Q12_OdcByUpsA_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q12_OdcByUpsA_ON
PTODI_A1Q13_OdcByA_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q13_OdcByA_IZP
PTODI_A1Q13_OdcByA_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q13_OdcByA_ON
PTODI_A2Q0_GlavnoSti_ON | DIGITAL | IOD_PTO | PTO:.DI_A2Q0_GlavnoSti_ON
PTODI_F201_OdcKl1ZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F201_OdcKl1ZE_IZP
PTODI_F201_OdcKl1ZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F201_OdcKl1ZE_ON
PTODI_F202_OdcKl2ZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F202_OdcKl2ZE_IZP
PTODI_F202_OdcKl2ZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F202_OdcKl2ZE_ON
PTODI_F203_OdcKl3ZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F203_OdcKl3ZE_IZP
PTODI_F203_OdcKl3ZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F203_OdcKl3ZE_ON
PTODI_F204_OdcKl4ZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F204_OdcKl4ZE_IZP
PTODI_F204_OdcKl4ZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F204_OdcKl4ZE_ON
PTODI_F205_OdcKl5aZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F205_OdcKl5aZE_IZP
PTODI_F205_OdcKl5aZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F205_OdcKl5aZE_ON
PTODI_F206_OdcKl5bZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F206_OdcKl5bZE_IZP
PTODI_F206_OdcKl5bZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F206_OdcKl5bZE_ON
PTODI_F207_OdcKl6aZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F207_OdcKl6aZE_IZP
PTODI_F207_OdcKl6aZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F207_OdcKl6aZE_ON
PTODI_F208_OdcKl6bZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F208_OdcKl6bZE_IZP
PTODI_F208_OdcKl6bZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F208_OdcKl6bZE_ON
PTODI_IzpadMreze | DIGITAL | IOD_PTO | PTO:.DI_IzpadMreze
PTODI_Klima1_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima1_ERR
PTODI_Klima1_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima1_ON
PTODI_Klima2_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima2_ERR
PTODI_Klima2_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima2_ON
PTODI_Klima3_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima3_ERR
PTODI_Klima3_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima3_ON
PTODI_Klima4_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima4_ERR
PTODI_Klima4_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima4_ON
PTODI_Klima5_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima5_ERR
PTODI_Klima5_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima5_ON
PTODI_Klima6_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima6_ERR
PTODI_Klima6_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima6_ON
PTODI_KlimaSplitPP_ERR | DIGITAL | IOD_PTO | PTO:.DI_KlimaSplitPP_ERR
PTODI_KlimaSplitPP_ON | DIGITAL | IOD_PTO | PTO:.DI_KlimaSplitPP_ON
PTODI_PrenapA1_OK | DIGITAL | IOD_PTO | PTO:.DI_PrenapA1_OK
PTODI_PrenapA2_OK | DIGITAL | IOD_PTO | PTO:.DI_PrenapA2_OK
PTODI_Q101_OdcKlima1_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q101_OdcKlima1_IZP
PTODI_Q101_OdcKlima1_ON | DIGITAL | IOD_PTO | PTO:.DI_Q101_OdcKlima1_ON
PTODI_Q102_OdcKlima2_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q102_OdcKlima2_IZP
PTODI_Q102_OdcKlima2_ON | DIGITAL | IOD_PTO | PTO:.DI_Q102_OdcKlima2_ON
PTODI_Q103_OdcKlima3_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q103_OdcKlima3_IZP
PTODI_Q103_OdcKlima3_ON | DIGITAL | IOD_PTO | PTO:.DI_Q103_OdcKlima3_ON
PTODI_Q104_OdcKlima4_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q104_OdcKlima4_IZP
PTODI_Q104_OdcKlima4_ON | DIGITAL | IOD_PTO | PTO:.DI_Q104_OdcKlima4_ON
PTODI_Q105_OdcKlima5_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q105_OdcKlima5_IZP
PTODI_Q105_OdcKlima5_ON | DIGITAL | IOD_PTO | PTO:.DI_Q105_OdcKlima5_ON
PTODI_Q106_OdcKlima6_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q106_OdcKlima6_IZP
PTODI_Q106_OdcKlima6_ON | DIGITAL | IOD_PTO | PTO:.DI_Q106_OdcKlima6_ON
PTODI_Q107_OdcUsmSS2_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q107_OdcUsmSS2_IZP
PTODI_Q107_OdcUsmSS2_ON | DIGITAL | IOD_PTO | PTO:.DI_Q107_OdcUsmSS2_ON
PTODI_Q108_OdcUsmSS3_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q108_OdcUsmSS3_IZP
PTODI_Q108_OdcUsmSS3_ON | DIGITAL | IOD_PTO | PTO:.DI_Q108_OdcUsmSS3_ON
PTODI_RazlitjeVodeK1K2 | DIGITAL | IOD_PTO | PTO:.DI_RazlitjeVodeK1K2
PTODI_RazlitjeVodeK3K4 | DIGITAL | IOD_PTO | PTO:.DI_RazlitjeVodeK3K4
PTODI_RazlitjeVodeK5 | DIGITAL | IOD_PTO | PTO:.DI_RazlitjeVodeK5
PTODI_RazlitjeVodeK6 | DIGITAL | IOD_PTO | PTO:.DI_RazlitjeVodeK6
PTODI_UPS_Alarm | DIGITAL | IOD_PTO | PTO:.DI_UPS_Alarm
PTODI_UPS_BatNacin | DIGITAL | IOD_PTO | PTO:.DI_UPS_BatNacin
PTODI_UPS_Polnjenje | DIGITAL | IOD_PTO | PTO:.DI_UPS_Polnjenje
PTODI_UpsA_BypassON | DIGITAL | IOD_PTO | PTO:.DI_UpsA_BypassON
PTODI_UpsA_ERR | DIGITAL | IOD_PTO | PTO:.DI_UpsA_ERR
PTODI_UpsB_BypassON | DIGITAL | IOD_PTO | PTO:.DI_UpsB_BypassON
PTODI_UpsB_ERR | DIGITAL | IOD_PTO | PTO:.DI_UpsB_ERR
PTODI_UQ11_OdcPMM_IZP | DIGITAL | IOD_PTO | PTO:.DI_UQ11_OdcPMM_IZP
PTODI_UQ11_OdcPMM_ON | DIGITAL | IOD_PTO | PTO:.DI_UQ11_OdcPMM_ON
PTODI_UQ12_OdcPMM_IZP | DIGITAL | IOD_PTO | PTO:.DI_UQ12_OdcPMM_IZP
PTODI_UQ12_OdcPMM_ON | DIGITAL | IOD_PTO | PTO:.DI_UQ12_OdcPMM_ON
PTODIN_A1Q11_OdcUpsA_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q11_OdcUpsA_IZP
PTODIN_A1Q12_OdcByUpsA_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q12_OdcByUpsA_IZP
PTODIN_A1Q13_OdcByA_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q13_OdcByA_IZP
PTODIN_F201_OdcKl1ZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F201_OdcKl1ZE_IZP
PTODIN_F202_OdcKl2ZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F202_OdcKl2ZE_IZP
PTODIN_F203_OdcKl3ZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F203_OdcKl3ZE_IZP
PTODIN_F204_OdcKl4ZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F204_OdcKl4ZE_IZP
PTODIN_F205_OdcKl5aZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F205_OdcKl5aZE_IZP
PTODIN_F206_OdcKl5bZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F206_OdcKl5bZE_IZP
PTODIN_F207_OdcKl6aZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F207_OdcKl6aZE_IZP
PTODIN_F208_OdcKl6bZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F208_OdcKl6bZE_IZP
PTODIN_Klima1_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima1_ERR
PTODIN_Klima2_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima2_ERR
PTODIN_Klima3_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima3_ERR
PTODIN_Klima4_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima4_ERR
PTODIN_Klima5_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima5_ERR
PTODIN_Klima6_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima6_ERR
PTODIN_KlimaSplitPP_ERR | DIGITAL | IOD_PTO | PTO:.DIN_KlimaSplitPP_ERR
PTODIN_PrenapA1_OK | DIGITAL | IOD_PTO | PTO:.DIN_PrenapA1_OK
PTODIN_PrenapA2_OK | DIGITAL | IOD_PTO | PTO:.DIN_PrenapA2_OK
PTODIN_Q101_OdcKlima1_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q101_OdcKlima1_IZP
PTODIN_Q102_OdcKlima2_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q102_OdcKlima2_IZP
PTODIN_Q103_OdcKlima3_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q103_OdcKlima3_IZP
PTODIN_Q104_OdcKlima4_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q104_OdcKlima4_IZP
PTODIN_Q105_OdcKlima5_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q105_OdcKlima5_IZP
PTODIN_Q106_OdcKlima6_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q106_OdcKlima6_IZP
PTODIN_Q107_OdcUsmSS2_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q107_OdcUsmSS2_IZP
PTODIN_Q108_OdcUsmSS3_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q108_OdcUsmSS3_IZP
PTODIN_UpsA_BypassON | DIGITAL | IOD_PTO | PTO:.DIN_UpsA_BypassON
PTODIN_UpsA_ERR | DIGITAL | IOD_PTO | PTO:.DIN_UpsA_ERR
PTODIN_UpsB_BypassON | DIGITAL | IOD_PTO | PTO:.DIN_UpsB_BypassON
PTODIN_UpsB_ERR | DIGITAL | IOD_PTO | PTO:.DIN_UpsB_ERR
PTODIN_UQ11_OdcPMM_IZP | DIGITAL | IOD_PTO | PTO:.DIN_UQ11_OdcPMM_IZP
PTODIN_UQ12_OdcPMM_IZP | DIGITAL | IOD_PTO | PTO:.DIN_UQ12_OdcPMM_IZP
PTODO_Klima1_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima1_Izklop
PTODO_Klima2_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima2_Izklop
PTODO_Klima3_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima3_Izklop
PTODO_Klima4_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima4_Izklop
PTODO_Klima5_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima5_Izklop
PTODO_Klima6_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima6_Izklop
PTOErrComKlima1 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[1]
PTOErrComKlima2 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[2]
PTOErrComKlima3 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[3]
PTOErrComKlima4 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[4]
PTOErrComKlima5 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[5]
PTOErrComKlima6 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[6]
PTOErrCommScada | DIGITAL | IOD_PTO | PTO:.ErrCommScada
PTOErrComPanelPLC | DIGITAL | IOD_PTO | PTO:.ErrComPanelPLC
PTOErrComPMM | DIGITAL | IOD_PTO | PTO:.ErrComPMM
PTOErrComPort2 | DIGITAL | IOD_PTO | PTO:.ErrComPort2
PTOErrComPort3 | DIGITAL | IOD_PTO | PTO:.ErrComPort3
PTOErrComPort4 | DIGITAL | IOD_PTO | PTO:.ErrComPort4
PTOErrComUPS1 | DIGITAL | IOD_PTO | PTO:.ErrComUPS[1]
PTOErrComUPS2 | DIGITAL | IOD_PTO | PTO:.ErrComUPS[2]
PTOErrorComKlima1Code10 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[10] | BYTE
PTOErrorComKlima1Code11 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[11] | BYTE
PTOErrorComKlima1Code12 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[12] | BYTE
PTOErrorComKlima1Code13 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[13] | BYTE
PTOErrorComKlima1Code14 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[14] | BYTE
PTOErrorComKlima1Code15 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[15] | BYTE
PTOErrorComKlima1Code1 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[1] | BYTE
PTOErrorComKlima1Code2 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[2] | BYTE
PTOErrorComKlima1Code3 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[3] | BYTE
PTOErrorComKlima1Code4 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[4] | BYTE
PTOErrorComKlima1Code5 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[5] | BYTE
PTOErrorComKlima1Code6 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[6] | BYTE
PTOErrorComKlima1Code7 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[7] | BYTE
PTOErrorComKlima1Code8 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[8] | BYTE
PTOErrorComKlima1Code9 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[9] | BYTE
PTOErrorComKlima1Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[1].Error
PTOErrorComKlima1Status | INT | IOD_PTO | PTO:.ErrorComKlima[1].Status
PTOErrorComKlima2Code10 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[10] | BYTE
PTOErrorComKlima2Code11 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[11] | BYTE
PTOErrorComKlima2Code12 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[12] | BYTE
PTOErrorComKlima2Code13 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[13] | BYTE
PTOErrorComKlima2Code14 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[14] | BYTE
PTOErrorComKlima2Code15 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[15] | BYTE
PTOErrorComKlima2Code1 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[1] | BYTE
PTOErrorComKlima2Code2 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[2] | BYTE
PTOErrorComKlima2Code3 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[3] | BYTE
PTOErrorComKlima2Code4 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[4] | BYTE
PTOErrorComKlima2Code5 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[5] | BYTE
PTOErrorComKlima2Code6 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[6] | BYTE
PTOErrorComKlima2Code7 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[7] | BYTE
PTOErrorComKlima2Code8 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[8] | BYTE
PTOErrorComKlima2Code9 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[9] | BYTE
PTOErrorComKlima2Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[2].Error
PTOErrorComKlima2Status | INT | IOD_PTO | PTO:.ErrorComKlima[2].Status
PTOErrorComKlima3Code10 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[10] | BYTE
PTOErrorComKlima3Code11 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[11] | BYTE
PTOErrorComKlima3Code12 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[12] | BYTE
PTOErrorComKlima3Code13 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[13] | BYTE
PTOErrorComKlima3Code14 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[14] | BYTE
PTOErrorComKlima3Code15 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[15] | BYTE
PTOErrorComKlima3Code1 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[1] | BYTE
PTOErrorComKlima3Code2 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[2] | BYTE
PTOErrorComKlima3Code3 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[3] | BYTE
PTOErrorComKlima3Code4 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[4] | BYTE
PTOErrorComKlima3Code5 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[5] | BYTE
PTOErrorComKlima3Code6 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[6] | BYTE
PTOErrorComKlima3Code7 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[7] | BYTE
PTOErrorComKlima3Code8 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[8] | BYTE
PTOErrorComKlima3Code9 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[9] | BYTE
PTOErrorComKlima3Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[3].Error
PTOErrorComKlima3Status | INT | IOD_PTO | PTO:.ErrorComKlima[3].Status
PTOErrorComKlima4Code10 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[10] | BYTE
PTOErrorComKlima4Code11 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[11] | BYTE
PTOErrorComKlima4Code12 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[12] | BYTE
PTOErrorComKlima4Code13 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[13] | BYTE
PTOErrorComKlima4Code14 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[14] | BYTE
PTOErrorComKlima4Code15 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[15] | BYTE
PTOErrorComKlima4Code1 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[1] | BYTE
PTOErrorComKlima4Code2 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[2] | BYTE
PTOErrorComKlima4Code3 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[3] | BYTE
PTOErrorComKlima4Code4 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[4] | BYTE
PTOErrorComKlima4Code5 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[5] | BYTE
PTOErrorComKlima4Code6 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[6] | BYTE
PTOErrorComKlima4Code7 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[7] | BYTE
PTOErrorComKlima4Code8 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[8] | BYTE
PTOErrorComKlima4Code9 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[9] | BYTE
PTOErrorComKlima4Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[4].Error
PTOErrorComKlima4Status | INT | IOD_PTO | PTO:.ErrorComKlima[4].Status
PTOErrorComKlima5Code10 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[10] | BYTE
PTOErrorComKlima5Code11 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[11] | BYTE
PTOErrorComKlima5Code12 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[12] | BYTE
PTOErrorComKlima5Code13 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[13] | BYTE
PTOErrorComKlima5Code14 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[14] | BYTE
PTOErrorComKlima5Code15 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[15] | BYTE
PTOErrorComKlima5Code1 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[1] | BYTE
PTOErrorComKlima5Code2 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[2] | BYTE
PTOErrorComKlima5Code3 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[3] | BYTE
PTOErrorComKlima5Code4 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[4] | BYTE
PTOErrorComKlima5Code5 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[5] | BYTE
PTOErrorComKlima5Code6 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[6] | BYTE
PTOErrorComKlima5Code7 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[7] | BYTE
PTOErrorComKlima5Code8 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[8] | BYTE
PTOErrorComKlima5Code9 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[9] | BYTE
PTOErrorComKlima5Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[5].Error
PTOErrorComKlima5Status | INT | IOD_PTO | PTO:.ErrorComKlima[5].Status
PTOErrorComKlima6Code10 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[10] | BYTE
PTOErrorComKlima6Code11 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[11] | BYTE
PTOErrorComKlima6Code12 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[12] | BYTE
PTOErrorComKlima6Code13 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[13] | BYTE
PTOErrorComKlima6Code14 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[14] | BYTE
PTOErrorComKlima6Code15 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[15] | BYTE
PTOErrorComKlima6Code1 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[1] | BYTE
PTOErrorComKlima6Code2 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[2] | BYTE
PTOErrorComKlima6Code3 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[3] | BYTE
PTOErrorComKlima6Code4 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[4] | BYTE
PTOErrorComKlima6Code5 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[5] | BYTE
PTOErrorComKlima6Code6 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[6] | BYTE
PTOErrorComKlima6Code7 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[7] | BYTE
PTOErrorComKlima6Code8 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[8] | BYTE
PTOErrorComKlima6Code9 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[9] | BYTE
PTOErrorComKlima6Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[6].Error
PTOErrorComKlima6Status | INT | IOD_PTO | PTO:.ErrorComKlima[6].Status
PTOErrorComPMMCode10 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[10] | BYTE
PTOErrorComPMMCode11 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[11] | BYTE
PTOErrorComPMMCode12 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[12] | BYTE
PTOErrorComPMMCode13 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[13] | BYTE
PTOErrorComPMMCode14 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[14] | BYTE
PTOErrorComPMMCode15 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[15] | BYTE
PTOErrorComPMMCode1 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[1] | BYTE
PTOErrorComPMMCode2 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[2] | BYTE
PTOErrorComPMMCode3 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[3] | BYTE
PTOErrorComPMMCode4 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[4] | BYTE
PTOErrorComPMMCode5 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[5] | BYTE
PTOErrorComPMMCode6 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[6] | BYTE
PTOErrorComPMMCode7 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[7] | BYTE
PTOErrorComPMMCode8 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[8] | BYTE
PTOErrorComPMMCode9 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[9] | BYTE
PTOErrorComPMMError | DIGITAL | IOD_PTO | PTO:.ErrorComPMM.Error
PTOErrorComPMMStatus | INT | IOD_PTO | PTO:.ErrorComPMM.Status
PTOErrorComUPS1Code10 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[10] | BYTE
PTOErrorComUPS1Code11 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[11] | BYTE
PTOErrorComUPS1Code12 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[12] | BYTE
PTOErrorComUPS1Code13 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[13] | BYTE
PTOErrorComUPS1Code14 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[14] | BYTE
PTOErrorComUPS1Code15 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[15] | BYTE
PTOErrorComUPS1Code1 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[1] | BYTE
PTOErrorComUPS1Code2 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[2] | BYTE
PTOErrorComUPS1Code3 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[3] | BYTE
PTOErrorComUPS1Code4 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[4] | BYTE
PTOErrorComUPS1Code5 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[5] | BYTE
PTOErrorComUPS1Code6 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[6] | BYTE
PTOErrorComUPS1Code7 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[7] | BYTE
PTOErrorComUPS1Code8 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[8] | BYTE
PTOErrorComUPS1Code9 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[9] | BYTE
PTOErrorComUPS1Error | DIGITAL | IOD_PTO | PTO:.ErrorComUPS[1].Error
PTOErrorComUPS1Status | INT | IOD_PTO | PTO:.ErrorComUPS[1].Status
PTOErrorComUPS2Code10 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[10] | BYTE
PTOErrorComUPS2Code11 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[11] | BYTE
PTOErrorComUPS2Code12 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[12] | BYTE
PTOErrorComUPS2Code13 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[13] | BYTE
PTOErrorComUPS2Code14 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[14] | BYTE
PTOErrorComUPS2Code15 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[15] | BYTE
PTOErrorComUPS2Code1 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[1] | BYTE
PTOErrorComUPS2Code2 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[2] | BYTE
PTOErrorComUPS2Code3 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[3] | BYTE
PTOErrorComUPS2Code4 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[4] | BYTE
PTOErrorComUPS2Code5 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[5] | BYTE
PTOErrorComUPS2Code6 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[6] | BYTE
PTOErrorComUPS2Code7 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[7] | BYTE
PTOErrorComUPS2Code8 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[8] | BYTE
PTOErrorComUPS2Code9 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[9] | BYTE
PTOErrorComUPS2Error | DIGITAL | IOD_PTO | PTO:.ErrorComUPS[2].Error
PTOErrorComUPS2Status | INT | IOD_PTO | PTO:.ErrorComUPS[2].Status
PTOKlima1Errors10 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[10]
PTOKlima1Errors11 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[11]
PTOKlima1Errors12 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[12]
PTOKlima1Errors13 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[13]
PTOKlima1Errors14 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[14]
PTOKlima1Errors15 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[15]
PTOKlima1Errors16 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[16]
PTOKlima1Errors17 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[17]
PTOKlima1Errors18 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[18]
PTOKlima1Errors19 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[19]
PTOKlima1Errors1 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[1]
PTOKlima1Errors20 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[20]
PTOKlima1Errors21 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[21]
PTOKlima1Errors22 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[22]
PTOKlima1Errors23 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[23]
PTOKlima1Errors24 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[24]
PTOKlima1Errors25 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[25]
PTOKlima1Errors26 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[26]
PTOKlima1Errors27 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[27]
PTOKlima1Errors28 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[28]
PTOKlima1Errors29 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[29]
PTOKlima1Errors2 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[2]
PTOKlima1Errors30 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[30]
PTOKlima1Errors31 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[31]
PTOKlima1Errors32 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[32]
PTOKlima1Errors33 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[33]
PTOKlima1Errors34 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[34]
PTOKlima1Errors35 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[35]
PTOKlima1Errors3 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[3]
PTOKlima1Errors4 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[4]
PTOKlima1Errors5 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[5]
PTOKlima1Errors6 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[6]
PTOKlima1Errors7 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[7]
PTOKlima1Errors8 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[8]
PTOKlima1Errors9 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[9]
PTOKlima2Errors10 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[10]
PTOKlima2Errors11 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[11]
PTOKlima2Errors12 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[12]
PTOKlima2Errors13 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[13]
PTOKlima2Errors14 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[14]
PTOKlima2Errors15 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[15]
PTOKlima2Errors16 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[16]
PTOKlima2Errors17 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[17]
PTOKlima2Errors18 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[18]
PTOKlima2Errors19 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[19]
PTOKlima2Errors1 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[1]
PTOKlima2Errors20 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[20]
PTOKlima2Errors21 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[21]
PTOKlima2Errors22 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[22]
PTOKlima2Errors23 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[23]
PTOKlima2Errors24 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[24]
PTOKlima2Errors25 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[25]
PTOKlima2Errors26 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[26]
PTOKlima2Errors27 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[27]
PTOKlima2Errors28 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[28]
PTOKlima2Errors29 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[29]
PTOKlima2Errors2 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[2]
PTOKlima2Errors30 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[30]
PTOKlima2Errors31 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[31]
PTOKlima2Errors32 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[32]
PTOKlima2Errors33 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[33]
PTOKlima2Errors34 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[34]
PTOKlima2Errors35 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[35]
PTOKlima2Errors3 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[3]
PTOKlima2Errors4 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[4]
PTOKlima2Errors5 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[5]
PTOKlima2Errors6 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[6]
PTOKlima2Errors7 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[7]
PTOKlima2Errors8 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[8]
PTOKlima2Errors9 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[9]
PTOKlima3Errors10 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[10]
PTOKlima3Errors11 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[11]
PTOKlima3Errors12 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[12]
PTOKlima3Errors13 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[13]
PTOKlima3Errors14 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[14]
PTOKlima3Errors15 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[15]
PTOKlima3Errors16 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[16]
PTOKlima3Errors17 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[17]
PTOKlima3Errors18 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[18]
PTOKlima3Errors19 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[19]
PTOKlima3Errors1 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[1]
PTOKlima3Errors20 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[20]
PTOKlima3Errors21 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[21]
PTOKlima3Errors22 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[22]
PTOKlima3Errors23 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[23]
PTOKlima3Errors24 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[24]
PTOKlima3Errors25 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[25]
PTOKlima3Errors26 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[26]
PTOKlima3Errors27 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[27]
PTOKlima3Errors28 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[28]
PTOKlima3Errors29 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[29]
PTOKlima3Errors2 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[2]
PTOKlima3Errors30 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[30]
PTOKlima3Errors31 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[31]
PTOKlima3Errors32 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[32]
PTOKlima3Errors33 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[33]
PTOKlima3Errors34 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[34]
PTOKlima3Errors35 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[35]
PTOKlima3Errors3 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[3]
PTOKlima3Errors4 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[4]
PTOKlima3Errors5 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[5]
PTOKlima3Errors6 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[6]
PTOKlima3Errors7 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[7]
PTOKlima3Errors8 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[8]
PTOKlima3Errors9 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[9]
PTOKlima4Errors10 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[10]
PTOKlima4Errors11 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[11]
PTOKlima4Errors12 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[12]
PTOKlima4Errors13 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[13]
PTOKlima4Errors14 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[14]
PTOKlima4Errors15 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[15]
PTOKlima4Errors16 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[16]
PTOKlima4Errors17 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[17]
PTOKlima4Errors18 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[18]
PTOKlima4Errors19 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[19]
PTOKlima4Errors1 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[1]
PTOKlima4Errors20 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[20]
PTOKlima4Errors21 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[21]
PTOKlima4Errors22 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[22]
PTOKlima4Errors23 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[23]
PTOKlima4Errors24 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[24]
PTOKlima4Errors25 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[25]
PTOKlima4Errors26 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[26]
PTOKlima4Errors27 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[27]
PTOKlima4Errors28 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[28]
PTOKlima4Errors29 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[29]
PTOKlima4Errors2 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[2]
PTOKlima4Errors30 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[30]
PTOKlima4Errors31 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[31]
PTOKlima4Errors32 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[32]
PTOKlima4Errors33 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[33]
PTOKlima4Errors34 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[34]
PTOKlima4Errors35 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[35]
PTOKlima4Errors3 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[3]
PTOKlima4Errors4 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[4]
PTOKlima4Errors5 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[5]
PTOKlima4Errors6 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[6]
PTOKlima4Errors7 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[7]
PTOKlima4Errors8 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[8]
PTOKlima4Errors9 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[9]
PTOKlima5Errors10 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[10]
PTOKlima5Errors11 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[11]
PTOKlima5Errors12 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[12]
PTOKlima5Errors13 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[13]
PTOKlima5Errors14 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[14]
PTOKlima5Errors15 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[15]
PTOKlima5Errors16 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[16]
PTOKlima5Errors17 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[17]
PTOKlima5Errors18 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[18]
PTOKlima5Errors19 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[19]
PTOKlima5Errors1 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[1]
PTOKlima5Errors20 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[20]
PTOKlima5Errors21 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[21]
PTOKlima5Errors22 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[22]
PTOKlima5Errors23 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[23]
PTOKlima5Errors24 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[24]
PTOKlima5Errors25 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[25]
PTOKlima5Errors26 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[26]
PTOKlima5Errors27 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[27]
PTOKlima5Errors28 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[28]
PTOKlima5Errors29 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[29]
PTOKlima5Errors2 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[2]
PTOKlima5Errors30 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[30]
PTOKlima5Errors31 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[31]
PTOKlima5Errors32 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[32]
PTOKlima5Errors33 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[33]
PTOKlima5Errors34 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[34]
PTOKlima5Errors35 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[35]
PTOKlima5Errors3 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[3]
PTOKlima5Errors4 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[4]
PTOKlima5Errors5 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[5]
PTOKlima5Errors6 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[6]
PTOKlima5Errors7 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[7]
PTOKlima5Errors8 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[8]
PTOKlima5Errors9 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[9]
PTOKlima6Errors10 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[10]
PTOKlima6Errors11 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[11]
PTOKlima6Errors12 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[12]
PTOKlima6Errors13 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[13]
PTOKlima6Errors14 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[14]
PTOKlima6Errors15 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[15]
PTOKlima6Errors16 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[16]
PTOKlima6Errors17 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[17]
PTOKlima6Errors18 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[18]
PTOKlima6Errors19 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[19]
PTOKlima6Errors1 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[1]
PTOKlima6Errors20 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[20]
PTOKlima6Errors21 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[21]
PTOKlima6Errors22 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[22]
PTOKlima6Errors23 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[23]
PTOKlima6Errors24 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[24]
PTOKlima6Errors25 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[25]
PTOKlima6Errors26 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[26]
PTOKlima6Errors27 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[27]
PTOKlima6Errors28 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[28]
PTOKlima6Errors29 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[29]
PTOKlima6Errors2 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[2]
PTOKlima6Errors30 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[30]
PTOKlima6Errors31 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[31]
PTOKlima6Errors32 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[32]
PTOKlima6Errors33 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[33]
PTOKlima6Errors34 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[34]
PTOKlima6Errors35 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[35]
PTOKlima6Errors3 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[3]
PTOKlima6Errors4 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[4]
PTOKlima6Errors5 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[5]
PTOKlima6Errors6 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[6]
PTOKlima6Errors7 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[7]
PTOKlima6Errors8 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[8]
PTOKlima6Errors9 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[9]
PTOKlima1Deluje | DIGITAL | IOD_PTO | PTO:.Klima[1].Deluje
PTOKlima1FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[1].FenThermalCutout
PTOKlima1GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].GeneralAlarm
PTOKlima1GrelecStatus | INT | IOD_PTO | PTO:.Klima[1].GrelecStatus | BYTE
PTOKlima1IzhodniVentStatus | INT | IOD_PTO | PTO:.Klima[1].IzhodniVentStatus | BYTE
PTOKlima1Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Kompresor1naMejiObrUr
PTOKlima1Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Kompresor2naMejiObrUr
PTOKlima1KompresorStatus | INT | IOD_PTO | PTO:.Klima[1].KompresorStatus | BYTE
PTOKlima1Napaka | DIGITAL | IOD_PTO | PTO:.Klima[1].Napaka
PTOKlima1NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaPriPretokuZraka
PTOKlima1NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorTempIzpiha
PTOKlima1NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorTempProstora
PTOKlima1NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorVlaznosti
PTOKlima1NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorZunanjeTemp
PTOKlima1NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[1].NiTokaVVlazilcu
PTOKlima1NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[1].NiVodeVVlazilcu
PTOKlima1NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[1].NizekPritiskKompresor1
PTOKlima1NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[1].NizekPritiskKompresor2
PTOKlima1NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[1].NizkaTempVProstoru
PTOKlima1NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[1].NizkaVlaznost
PTOKlima1ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[1].ObratovalneUre
PTOKlima1OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[1].OnOffEnablingBySupervisor
PTOKlima1PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].PozarniAlarm
PTOKlima1Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[1].Razvlazevanje
PTOKlima1RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[1].RemoteOFFtoOutput
PTOKlima1RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[1].RocniIzklop
PTOKlima1SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[1].SenzorjiStatus
PTOKlima1TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[1].TemperaturaProstora
PTOKlima1TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[1].TempIzpihanegaZraka
PTOKlima1UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[1].UnitOnOff
PTOKlima1VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[1].VisokaTempVProstoru
PTOKlima1VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[1].VisokaVlaznost
PTOKlima1VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[1].VisokTokVVlazilcu
PTOKlima1Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[1].Vlazenje
PTOKlima1VlazilecStatus | INT | IOD_PTO | PTO:.Klima[1].VlazilecStatus | BYTE
PTOKlima1VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[1].VlaznostProstora
PTOKlima1ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[1].ZamasenFilter
PTOKlima1ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[1].ZunanjaTemp
PTOKlima2Deluje | DIGITAL | IOD_PTO | PTO:.Klima[2].Deluje
PTOKlima2FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[2].FenThermalCutout
PTOKlima2GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].GeneralAlarm
PTOKlima2GrelecStatus | INT | IOD_PTO | PTO:.Klima[2].GrelecStatus | BYTE
PTOKlima2IzhodniVentStatus | INT | IOD_PTO | PTO:.Klima[2].IzhodniVentStatus | BYTE
PTOKlima2Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Kompresor1naMejiObrUr
PTOKlima2Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Kompresor2naMejiObrUr
PTOKlima2KompresorStatus | INT | IOD_PTO | PTO:.Klima[2].KompresorStatus | BYTE
PTOKlima2Napaka | DIGITAL | IOD_PTO | PTO:.Klima[2].Napaka
PTOKlima2NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaPriPretokuZraka
PTOKlima2NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorTempIzpiha
PTOKlima2NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorTempProstora
PTOKlima2NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorVlaznosti
PTOKlima2NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorZunanjeTemp
PTOKlima2NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[2].NiTokaVVlazilcu
PTOKlima2NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[2].NiVodeVVlazilcu
PTOKlima2NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[2].NizekPritiskKompresor1
PTOKlima2NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[2].NizekPritiskKompresor2
PTOKlima2NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[2].NizkaTempVProstoru
PTOKlima2NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[2].NizkaVlaznost
PTOKlima2ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[2].ObratovalneUre
PTOKlima2OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[2].OnOffEnablingBySupervisor
PTOKlima2PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].PozarniAlarm
PTOKlima2Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[2].Razvlazevanje
PTOKlima2RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[2].RemoteOFFtoOutput
PTOKlima2RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[2].RocniIzklop
PTOKlima2SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[2].SenzorjiStatus
PTOKlima2TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[2].TemperaturaProstora
PTOKlima2TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[2].TempIzpihanegaZraka
PTOKlima2UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[2].UnitOnOff
PTOKlima2VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[2].VisokaTempVProstoru
PTOKlima2VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[2].VisokaVlaznost
PTOKlima2VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[2].VisokTokVVlazilcu
PTOKlima2Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[2].Vlazenje
PTOKlima2VlazilecStatus | INT | IOD_PTO | PTO:.Klima[2].VlazilecStatus | BYTE
PTOKlima2VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[2].VlaznostProstora
PTOKlima2ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[2].ZamasenFilter
PTOKlima2ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[2].ZunanjaTemp
PTOKlima3Deluje | DIGITAL | IOD_PTO | PTO:.Klima[3].Deluje
PTOKlima3FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[3].FenThermalCutout
PTOKlima3GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].GeneralAlarm
PTOKlima3GrelecStatus | INT | IOD_PTO | PTO:.Klima[3].GrelecStatus | BYTE
PTOKlima3IzhodniVentStatus | INT | IOD_PTO | PTO:.Klima[3].IzhodniVentStatus | BYTE
PTOKlima3Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Kompresor1naMejiObrUr
PTOKlima3Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Kompresor2naMejiObrUr
PTOKlima3KompresorStatus | INT | IOD_PTO | PTO:.Klima[3].KompresorStatus | BYTE
PTOKlima3Napaka | DIGITAL | IOD_PTO | PTO:.Klima[3].Napaka
PTOKlima3NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaPriPretokuZraka
PTOKlima3NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorTempIzpiha
PTOKlima3NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorTempProstora
PTOKlima3NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorVlaznosti
PTOKlima3NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorZunanjeTemp
PTOKlima3NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[3].NiTokaVVlazilcu
PTOKlima3NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[3].NiVodeVVlazilcu
PTOKlima3NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[3].NizekPritiskKompresor1
PTOKlima3NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[3].NizekPritiskKompresor2
PTOKlima3NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[3].NizkaTempVProstoru
PTOKlima3NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[3].NizkaVlaznost
PTOKlima3ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[3].ObratovalneUre
PTOKlima3OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[3].OnOffEnablingBySupervisor
PTOKlima3PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].PozarniAlarm
PTOKlima3Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[3].Razvlazevanje
PTOKlima3RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[3].RemoteOFFtoOutput
PTOKlima3RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[3].RocniIzklop
PTOKlima3SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[3].SenzorjiStatus
PTOKlima3TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[3].TemperaturaProstora
PTOKlima3TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[3].TempIzpihanegaZraka
PTOKlima3UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[3].UnitOnOff
PTOKlima3VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[3].VisokaTempVProstoru
PTOKlima3VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[3].VisokaVlaznost
PTOKlima3VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[3].VisokTokVVlazilcu
PTOKlima3Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[3].Vlazenje
PTOKlima3VlazilecStatus | INT | IOD_PTO | PTO:.Klima[3].VlazilecStatus | BYTE
PTOKlima3VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[3].VlaznostProstora
PTOKlima3ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[3].ZamasenFilter
PTOKlima3ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[3].ZunanjaTemp
PTOKlima4Deluje | DIGITAL | IOD_PTO | PTO:.Klima[4].Deluje
PTOKlima4FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[4].FenThermalCutout
PTOKlima4GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].GeneralAlarm
PTOKlima4GrelecStatus | INT | IOD_PTO | PTO:.Klima[4].GrelecStatus | BYTE
PTOKlima4IzhodniVentStatus | INT | IOD_PTO | PTO:.Klima[4].IzhodniVentStatus | BYTE
PTOKlima4Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Kompresor1naMejiObrUr
PTOKlima4Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Kompresor2naMejiObrUr
PTOKlima4KompresorStatus | INT | IOD_PTO | PTO:.Klima[4].KompresorStatus | BYTE
PTOKlima4Napaka | DIGITAL | IOD_PTO | PTO:.Klima[4].Napaka
PTOKlima4NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaPriPretokuZraka
PTOKlima4NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorTempIzpiha
PTOKlima4NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorTempProstora
PTOKlima4NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorVlaznosti
PTOKlima4NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorZunanjeTemp
PTOKlima4NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[4].NiTokaVVlazilcu
PTOKlima4NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[4].NiVodeVVlazilcu
PTOKlima4NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[4].NizekPritiskKompresor1
PTOKlima4NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[4].NizekPritiskKompresor2
PTOKlima4NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[4].NizkaTempVProstoru
PTOKlima4NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[4].NizkaVlaznost
PTOKlima4ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[4].ObratovalneUre
PTOKlima4OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[4].OnOffEnablingBySupervisor
PTOKlima4PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].PozarniAlarm
PTOKlima4Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[4].Razvlazevanje
PTOKlima4RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[4].RemoteOFFtoOutput
PTOKlima4RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[4].RocniIzklop
PTOKlima4SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[4].SenzorjiStatus
PTOKlima4TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[4].TemperaturaProstora
PTOKlima4TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[4].TempIzpihanegaZraka
PTOKlima4UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[4].UnitOnOff
PTOKlima4VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[4].VisokaTempVProstoru
PTOKlima4VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[4].VisokaVlaznost
PTOKlima4VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[4].VisokTokVVlazilcu
PTOKlima4Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[4].Vlazenje
PTOKlima4VlazilecStatus | INT | IOD_PTO | PTO:.Klima[4].VlazilecStatus | BYTE
PTOKlima4VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[4].VlaznostProstora
PTOKlima4ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[4].ZamasenFilter
PTOKlima4ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[4].ZunanjaTemp
PTOKlima5Deluje | DIGITAL | IOD_PTO | PTO:.Klima[5].Deluje
PTOKlima5FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[5].FenThermalCutout
PTOKlima5GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].GeneralAlarm
PTOKlima5GrelecStatus | INT | IOD_PTO | PTO:.Klima[5].GrelecStatus | BYTE
PTOKlima5IzhodniVentStatus | INT | IOD_PTO | PTO:.Klima[5].IzhodniVentStatus | BYTE
PTOKlima5Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Kompresor1naMejiObrUr
PTOKlima5Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Kompresor2naMejiObrUr
PTOKlima5KompresorStatus | INT | IOD_PTO | PTO:.Klima[5].KompresorStatus | BYTE
PTOKlima5Napaka | DIGITAL | IOD_PTO | PTO:.Klima[5].Napaka
PTOKlima5NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaPriPretokuZraka
PTOKlima5NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorTempIzpiha
PTOKlima5NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorTempProstora
PTOKlima5NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorVlaznosti
PTOKlima5NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorZunanjeTemp
PTOKlima5NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[5].NiTokaVVlazilcu
PTOKlima5NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[5].NiVodeVVlazilcu
PTOKlima5NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[5].NizekPritiskKompresor1
PTOKlima5NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[5].NizekPritiskKompresor2
PTOKlima5NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[5].NizkaTempVProstoru
PTOKlima5NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[5].NizkaVlaznost
PTOKlima5ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[5].ObratovalneUre
PTOKlima5OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[5].OnOffEnablingBySupervisor
PTOKlima5PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].PozarniAlarm
PTOKlima5Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[5].Razvlazevanje
PTOKlima5RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[5].RemoteOFFtoOutput
PTOKlima5RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[5].RocniIzklop
PTOKlima5SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[5].SenzorjiStatus
PTOKlima5TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[5].TemperaturaProstora
PTOKlima5TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[5].TempIzpihanegaZraka
PTOKlima5UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[5].UnitOnOff
PTOKlima5VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[5].VisokaTempVProstoru
PTOKlima5VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[5].VisokaVlaznost
PTOKlima5VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[5].VisokTokVVlazilcu
PTOKlima5Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[5].Vlazenje
PTOKlima5VlazilecStatus | INT | IOD_PTO | PTO:.Klima[5].VlazilecStatus | BYTE
PTOKlima5VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[5].VlaznostProstora
PTOKlima5ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[5].ZamasenFilter
PTOKlima5ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[5].ZunanjaTemp
PTOKlima6Deluje | DIGITAL | IOD_PTO | PTO:.Klima[6].Deluje
PTOKlima6FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[6].FenThermalCutout
PTOKlima6GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].GeneralAlarm
PTOKlima6GrelecStatus | INT | IOD_PTO | PTO:.Klima[6].GrelecStatus | BYTE
PTOKlima6IzhodniVentStatus | INT | IOD_PTO | PTO:.Klima[6].IzhodniVentStatus | BYTE
PTOKlima6Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Kompresor1naMejiObrUr
PTOKlima6Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Kompresor2naMejiObrUr
PTOKlima6KompresorStatus | INT | IOD_PTO | PTO:.Klima[6].KompresorStatus | BYTE
PTOKlima6Napaka | DIGITAL | IOD_PTO | PTO:.Klima[6].Napaka
PTOKlima6NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaPriPretokuZraka
PTOKlima6NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorTempIzpiha
PTOKlima6NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorTempProstora
PTOKlima6NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorVlaznosti
PTOKlima6NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorZunanjeTemp
PTOKlima6NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[6].NiTokaVVlazilcu
PTOKlima6NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[6].NiVodeVVlazilcu
PTOKlima6NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[6].NizekPritiskKompresor1
PTOKlima6NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[6].NizekPritiskKompresor2
PTOKlima6NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[6].NizkaTempVProstoru
PTOKlima6NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[6].NizkaVlaznost
PTOKlima6ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[6].ObratovalneUre
PTOKlima6OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[6].OnOffEnablingBySupervisor
PTOKlima6PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].PozarniAlarm
PTOKlima6Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[6].Razvlazevanje
PTOKlima6RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[6].RemoteOFFtoOutput
PTOKlima6RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[6].RocniIzklop
PTOKlima6SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[6].SenzorjiStatus
PTOKlima6TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[6].TemperaturaProstora
PTOKlima6TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[6].TempIzpihanegaZraka
PTOKlima6UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[6].UnitOnOff
PTOKlima6VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[6].VisokaTempVProstoru
PTOKlima6VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[6].VisokaVlaznost
PTOKlima6VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[6].VisokTokVVlazilcu
PTOKlima6Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[6].Vlazenje
PTOKlima6VlazilecStatus | INT | IOD_PTO | PTO:.Klima[6].VlazilecStatus | BYTE
PTOKlima6VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[6].VlaznostProstora
PTOKlima6ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[6].ZamasenFilter
PTOKlima6ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[6].ZunanjaTemp
PTOKlimeNaCas0 | DIGITAL | IOD_PTO | PTO:.KlimeNaCas[0]
PTOKlimeNaCas1 | DIGITAL | IOD_PTO | PTO:.KlimeNaCas[1]
PTOKlimeNaCas2 | DIGITAL | IOD_PTO | PTO:.KlimeNaCas[2]
PTOKlimeNaCas3 | DIGITAL | IOD_PTO | PTO:.KlimeNaCas[3]
PTOMrezaIzpad | DIGITAL | IOD_PTO | PTO:.MrezaIzpad
PTOMrezaIzpadKlimaOff1 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[1]
PTOMrezaIzpadKlimaOff2 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[2]
PTOMrezaIzpadKlimaOff3 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[3]
PTOMrezaIzpadKlimaOff4 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[4]
PTOMrezaIzpadKlimaOff5 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[5]
PTOMrezaIzpadKlimaOff6 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[6]
PTOMrezaIzpadVklopDelay1 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[1]
PTOMrezaIzpadVklopDelay2 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[2]
PTOMrezaIzpadVklopDelay3 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[3]
PTOMrezaIzpadVklopDelay4 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[4]
PTOMrezaIzpadVklopDelay5 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[5]
PTOMrezaIzpadVklopDelay6 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[6]
PTONapakaSenzorTemp1 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[1]
PTONapakaSenzorTemp2 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[2]
PTONapakaSenzorTemp3 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[3]
PTONapakaSenzorTemp4 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[4]
PTONapakaSenzorTemp5 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[5]
PTONapakaSenzorTemp6 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[6]
PTONapakaSenzorVlaga1 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[1]
PTONapakaSenzorVlaga2 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[2]
PTONapakaSenzorVlaga3 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[3]
PTONapakaSenzorVlaga4 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[4]
PTONapakaSenzorVlaga5 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[5]
PTONapakaSenzorVlaga6 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[6]
PTOPMMActiveEnergyConsumed_kWh | REAL | IOD_PTO | PTO:.PMM.ActiveEnergyConsumed_kWh
PTOPMMActivePowerPhaseA_kW | REAL | IOD_PTO | PTO:.PMM.ActivePowerPhaseA_kW
PTOPMMActivePowerPhaseB_kW | REAL | IOD_PTO | PTO:.PMM.ActivePowerPhaseB_kW
PTOPMMActivePowerPhaseC_kW | REAL | IOD_PTO | PTO:.PMM.ActivePowerPhaseC_kW
PTOPMMAlarmPhase1C01_16_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C01_16_60to80
PTOPMMAlarmPhase1C01_16_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C01_16_over80
PTOPMMAlarmPhase1C17_32_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C17_32_60to80
PTOPMMAlarmPhase1C17_32_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C17_32_over80
PTOPMMAlarmPhase1C33_42_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C33_42_60to80
PTOPMMAlarmPhase1C33_42_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C33_42_over80
PTOPMMAlarmPhase2C01_16_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C01_16_60to80
PTOPMMAlarmPhase2C01_16_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C01_16_over80
PTOPMMAlarmPhase2C17_32_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C17_32_60to80
PTOPMMAlarmPhase2C17_32_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C17_32_over80
PTOPMMAlarmPhase2C33_42_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C33_42_60to80
PTOPMMAlarmPhase2C33_42_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C33_42_over80
PTOPMMAlarmPhase3C01_16_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C01_16_60to80
PTOPMMAlarmPhase3C01_16_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C01_16_over80
PTOPMMAlarmPhase3C17_32_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C17_32_60to80
PTOPMMAlarmPhase3C17_32_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C17_32_over80
PTOPMMAlarmPhase3C33_42_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C33_42_60to80
PTOPMMAlarmPhase3C33_42_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C33_42_over80
PTOPMMAparentPowerPhaseA | REAL | IOD_PTO | PTO:.PMM.AparentPowerPhaseA
PTOPMMAparentPowerPhaseB | REAL | IOD_PTO | PTO:.PMM.AparentPowerPhaseB
PTOPMMAparentPowerPhaseC | REAL | IOD_PTO | PTO:.PMM.AparentPowerPhaseC
PTOPMMAverageCurrent_A | REAL | IOD_PTO | PTO:.PMM.AverageCurrent_A
PTOPMMAveragePhaseToNeutral_V | REAL | IOD_PTO | PTO:.PMM.AveragePhaseToNeutral_V
PTOPMMAveragePhaseToPhase_V | REAL | IOD_PTO | PTO:.PMM.AveragePhaseToPhase_V
PTOPMMCurrentInPhaseA_A | REAL | IOD_PTO | PTO:.PMM.CurrentInPhaseA_A
PTOPMMCurrentInPhaseB_A | REAL | IOD_PTO | PTO:.PMM.CurrentInPhaseB_A
PTOPMMCurrentInPhaseC_A | REAL | IOD_PTO | PTO:.PMM.CurrentInPhaseC_A
PTOPMMFrequency_Hz | REAL | IOD_PTO | PTO:.PMM.Frequency_Hz
PTOPMMNapaka | DIGITAL | IOD_PTO | PTO:.PMM.Napaka
PTOPMMPhase1Current10 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[10]
PTOPMMPhase1Current11 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[11]
PTOPMMPhase1Current12 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[12]
PTOPMMPhase1Current13 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[13]
PTOPMMPhase1Current14 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[14]
PTOPMMPhase1Current15 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[15]
PTOPMMPhase1Current16 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[16]
PTOPMMPhase1Current17 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[17]
PTOPMMPhase1Current18 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[18]
PTOPMMPhase1Current19 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[19]
PTOPMMPhase1Current1 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[1]
PTOPMMPhase1Current20 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[20]
PTOPMMPhase1Current21 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[21]
PTOPMMPhase1Current22 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[22]
PTOPMMPhase1Current23 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[23]
PTOPMMPhase1Current24 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[24]
PTOPMMPhase1Current25 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[25]
PTOPMMPhase1Current26 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[26]
PTOPMMPhase1Current27 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[27]
PTOPMMPhase1Current28 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[28]
PTOPMMPhase1Current29 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[29]
PTOPMMPhase1Current2 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[2]
PTOPMMPhase1Current30 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[30]
PTOPMMPhase1Current31 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[31]
PTOPMMPhase1Current32 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[32]
PTOPMMPhase1Current33 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[33]
PTOPMMPhase1Current34 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[34]
PTOPMMPhase1Current35 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[35]
PTOPMMPhase1Current36 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[36]
PTOPMMPhase1Current37 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[37]
PTOPMMPhase1Current38 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[38]
PTOPMMPhase1Current39 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[39]
PTOPMMPhase1Current3 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[3]
PTOPMMPhase1Current40 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[40]
PTOPMMPhase1Current41 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[41]
PTOPMMPhase1Current42 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[42]
PTOPMMPhase1Current4 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[4]
PTOPMMPhase1Current5 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[5]
PTOPMMPhase1Current6 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[6]
PTOPMMPhase1Current7 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[7]
PTOPMMPhase1Current8 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[8]
PTOPMMPhase1Current9 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[9]
PTOPMMPhase2Current10 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[10]
PTOPMMPhase2Current11 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[11]
PTOPMMPhase2Current12 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[12]
PTOPMMPhase2Current13 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[13]
PTOPMMPhase2Current14 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[14]
PTOPMMPhase2Current15 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[15]
PTOPMMPhase2Current16 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[16]
PTOPMMPhase2Current17 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[17]
PTOPMMPhase2Current18 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[18]
PTOPMMPhase2Current19 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[19]
PTOPMMPhase2Current1 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[1]
PTOPMMPhase2Current20 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[20]
PTOPMMPhase2Current21 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[21]
PTOPMMPhase2Current22 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[22]
PTOPMMPhase2Current23 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[23]
PTOPMMPhase2Current24 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[24]
PTOPMMPhase2Current25 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[25]
PTOPMMPhase2Current26 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[26]
PTOPMMPhase2Current27 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[27]
PTOPMMPhase2Current28 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[28]
PTOPMMPhase2Current29 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[29]
PTOPMMPhase2Current2 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[2]
PTOPMMPhase2Current30 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[30]
PTOPMMPhase2Current31 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[31]
PTOPMMPhase2Current32 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[32]
PTOPMMPhase2Current33 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[33]
PTOPMMPhase2Current34 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[34]
PTOPMMPhase2Current35 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[35]
PTOPMMPhase2Current36 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[36]
PTOPMMPhase2Current37 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[37]
PTOPMMPhase2Current38 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[38]
PTOPMMPhase2Current39 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[39]
PTOPMMPhase2Current3 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[3]
PTOPMMPhase2Current40 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[40]
PTOPMMPhase2Current41 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[41]
PTOPMMPhase2Current42 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[42]
PTOPMMPhase2Current4 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[4]
PTOPMMPhase2Current5 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[5]
PTOPMMPhase2Current6 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[6]
PTOPMMPhase2Current7 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[7]
PTOPMMPhase2Current8 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[8]
PTOPMMPhase2Current9 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[9]
PTOPMMPhase3Current10 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[10]
PTOPMMPhase3Current11 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[11]
PTOPMMPhase3Current12 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[12]
PTOPMMPhase3Current13 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[13]
PTOPMMPhase3Current14 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[14]
PTOPMMPhase3Current15 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[15]
PTOPMMPhase3Current16 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[16]
PTOPMMPhase3Current17 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[17]
PTOPMMPhase3Current18 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[18]
PTOPMMPhase3Current19 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[19]
PTOPMMPhase3Current1 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[1]
PTOPMMPhase3Current20 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[20]
PTOPMMPhase3Current21 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[21]
PTOPMMPhase3Current22 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[22]
PTOPMMPhase3Current23 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[23]
PTOPMMPhase3Current24 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[24]
PTOPMMPhase3Current25 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[25]
PTOPMMPhase3Current26 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[26]
PTOPMMPhase3Current27 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[27]
PTOPMMPhase3Current28 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[28]
PTOPMMPhase3Current29 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[29]
PTOPMMPhase3Current2 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[2]
PTOPMMPhase3Current30 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[30]
PTOPMMPhase3Current31 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[31]
PTOPMMPhase3Current32 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[32]
PTOPMMPhase3Current33 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[33]
PTOPMMPhase3Current34 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[34]
PTOPMMPhase3Current35 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[35]
PTOPMMPhase3Current36 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[36]
PTOPMMPhase3Current37 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[37]
PTOPMMPhase3Current38 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[38]
PTOPMMPhase3Current39 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[39]
PTOPMMPhase3Current3 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[3]
PTOPMMPhase3Current40 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[40]
PTOPMMPhase3Current41 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[41]
PTOPMMPhase3Current42 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[42]
PTOPMMPhase3Current4 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[4]
PTOPMMPhase3Current5 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[5]
PTOPMMPhase3Current6 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[6]
PTOPMMPhase3Current7 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[7]
PTOPMMPhase3Current8 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[8]
PTOPMMPhase3Current9 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[9]
PTOPMMPowerFactorSys | REAL | IOD_PTO | PTO:.PMM.PowerFactorSys
PTOPMMReactiveEnergyConsumed_kVARh | REAL | IOD_PTO | PTO:.PMM.ReactiveEnergyConsumed_kVARh
PTOPMMReactivePowerPhaseA | REAL | IOD_PTO | PTO:.PMM.ReactivePowerPhaseA
PTOPMMReactivePowerPhaseB | REAL | IOD_PTO | PTO:.PMM.ReactivePowerPhaseB
PTOPMMReactivePowerPhaseC | REAL | IOD_PTO | PTO:.PMM.ReactivePowerPhaseC
PTOPMMTotalActivePower_kW | REAL | IOD_PTO | PTO:.PMM.TotalActivePower_kW
PTOPMMTotalAparentPower_kVA | REAL | IOD_PTO | PTO:.PMM.TotalAparentPower_kVA
PTOPMMTotalPowerFactor | REAL | IOD_PTO | PTO:.PMM.TotalPowerFactor
PTOPMMTotalReactivePower_kVAR | REAL | IOD_PTO | PTO:.PMM.TotalReactivePower_kVAR
PTOPMMVirA_fsys | REAL | IOD_PTO | PTO:.PMM.VirA_fsys
PTOPMMVirA_Isys | REAL | IOD_PTO | PTO:.PMM.VirA_Isys
PTOPMMVirA_PFsys | REAL | IOD_PTO | PTO:.PMM.VirA_PFsys
PTOPMMVirA_Psys | REAL | IOD_PTO | PTO:.PMM.VirA_Psys
PTOPMMVirA_Qsys | REAL | IOD_PTO | PTO:.PMM.VirA_Qsys
PTOPMMVirA_Ssys | REAL | IOD_PTO | PTO:.PMM.VirA_Ssys
PTOPMMVirA_Usys | REAL | IOD_PTO | PTO:.PMM.VirA_Usys
PTOPMMVirB_fsys | REAL | IOD_PTO | PTO:.PMM.VirB_fsys
PTOPMMVirB_Isys | REAL | IOD_PTO | PTO:.PMM.VirB_Isys
PTOPMMVirB_PFsys | REAL | IOD_PTO | PTO:.PMM.VirB_PFsys
PTOPMMVirB_Psys | REAL | IOD_PTO | PTO:.PMM.VirB_Psys
PTOPMMVirB_Qsys | REAL | IOD_PTO | PTO:.PMM.VirB_Qsys
PTOPMMVirB_Ssys | REAL | IOD_PTO | PTO:.PMM.VirB_Ssys
PTOPMMVirB_Usys | REAL | IOD_PTO | PTO:.PMM.VirB_Usys
PTOPMMVirBActiveEnergyConsumed_kWh | REAL | IOD_PTO | PTO:.PMM.VirBActiveEnergyConsumed_kWh
PTOPMMVirBActivePowerPhaseA_kW | REAL | IOD_PTO | PTO:.PMM.VirBActivePowerPhaseA_kW
PTOPMMVirBActivePowerPhaseB_kW | REAL | IOD_PTO | PTO:.PMM.VirBActivePowerPhaseB_kW
PTOPMMVirBActivePowerPhaseC_kW | REAL | IOD_PTO | PTO:.PMM.VirBActivePowerPhaseC_kW
PTOPMMVirBAparentPowerPhaseA | REAL | IOD_PTO | PTO:.PMM.VirBAparentPowerPhaseA
PTOPMMVirBAparentPowerPhaseB | REAL | IOD_PTO | PTO:.PMM.VirBAparentPowerPhaseB
PTOPMMVirBAparentPowerPhaseC | REAL | IOD_PTO | PTO:.PMM.VirBAparentPowerPhaseC
PTOPMMVirBAverageCurrent_A | REAL | IOD_PTO | PTO:.PMM.VirBAverageCurrent_A
PTOPMMVirBAveragePhaseToNeutral_V | REAL | IOD_PTO | PTO:.PMM.VirBAveragePhaseToNeutral_V
PTOPMMVirBAveragePhaseToPhase_V | REAL | IOD_PTO | PTO:.PMM.VirBAveragePhaseToPhase_V
PTOPMMVirBCurrentInPhaseA_A | REAL | IOD_PTO | PTO:.PMM.VirBCurrentInPhaseA_A
PTOPMMVirBCurrentInPhaseB_A | REAL | IOD_PTO | PTO:.PMM.VirBCurrentInPhaseB_A
PTOPMMVirBCurrentInPhaseC_A | REAL | IOD_PTO | PTO:.PMM.VirBCurrentInPhaseC_A
PTOPMMVirBFrequency_Hz | REAL | IOD_PTO | PTO:.PMM.VirBFrequency_Hz
PTOPMMVirBPowerFactorSys | REAL | IOD_PTO | PTO:.PMM.VirBPowerFactorSys
PTOPMMVirBReactiveEnergyConsumed_kVARh | REAL | IOD_PTO | PTO:.PMM.VirBReactiveEnergyConsumed_kVARh
PTOPMMVirBReactivePowerPhaseA | REAL | IOD_PTO | PTO:.PMM.VirBReactivePowerPhaseA
PTOPMMVirBReactivePowerPhaseB | REAL | IOD_PTO | PTO:.PMM.VirBReactivePowerPhaseB
PTOPMMVirBReactivePowerPhaseC | REAL | IOD_PTO | PTO:.PMM.VirBReactivePowerPhaseC
PTOPMMVirBTotalActivePower_kW | REAL | IOD_PTO | PTO:.PMM.VirBTotalActivePower_kW
PTOPMMVirBTotalAparentPower_kVA | REAL | IOD_PTO | PTO:.PMM.VirBTotalAparentPower_kVA
PTOPMMVirBTotalPowerFactor | REAL | IOD_PTO | PTO:.PMM.VirBTotalPowerFactor
PTOPMMVirBTotalReactivePower_kVAR | REAL | IOD_PTO | PTO:.PMM.VirBTotalReactivePower_kVAR
PTOPMMVirBVoltageBetweenPhaseAB_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseAB_V
PTOPMMVirBVoltageBetweenPhaseAN_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseAN_V
PTOPMMVirBVoltageBetweenPhaseBC_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseBC_V
PTOPMMVirBVoltageBetweenPhaseBN_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseBN_V
PTOPMMVirBVoltageBetweenPhaseCA_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseCA_V
PTOPMMVirBVoltageBetweenPhaseCN_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseCN_V
PTOPMMVoltageBetweenPhaseAB_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseAB_V
PTOPMMVoltageBetweenPhaseAN_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseAN_V
PTOPMMVoltageBetweenPhaseBC_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseBC_V
PTOPMMVoltageBetweenPhaseBN_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseBN_V
PTOPMMVoltageBetweenPhaseCA_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseCA_V
PTOPMMVoltageBetweenPhaseCN_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseCN_V
PTOPMMfaza01 | REAL | IOD_PTO | PTO:.PMMfaza01
PTOPMMfaza02 | REAL | IOD_PTO | PTO:.PMMfaza02
PTOPMMfaza03 | REAL | IOD_PTO | PTO:.PMMfaza03
PTOPMMfaza04 | REAL | IOD_PTO | PTO:.PMMfaza04
PTOPMMfaza05 | REAL | IOD_PTO | PTO:.PMMfaza05
PTOPMMfaza06 | REAL | IOD_PTO | PTO:.PMMfaza06
PTOPMMfaza07 | REAL | IOD_PTO | PTO:.PMMfaza07
PTOPMMfaza08 | REAL | IOD_PTO | PTO:.PMMfaza08
PTOPMMfaza09 | REAL | IOD_PTO | PTO:.PMMfaza09
PTOPMMfaza10 | REAL | IOD_PTO | PTO:.PMMfaza10
PTOPMMfaza11 | REAL | IOD_PTO | PTO:.PMMfaza11
PTOPMMfaza12 | REAL | IOD_PTO | PTO:.PMMfaza12
PTOPMMfaza13 | REAL | IOD_PTO | PTO:.PMMfaza13
PTOPMMfaza14 | REAL | IOD_PTO | PTO:.PMMfaza14
PTOPMMfaza15 | REAL | IOD_PTO | PTO:.PMMfaza15
PTOPMMfaza16 | REAL | IOD_PTO | PTO:.PMMfaza16
PTOPMMfaza17 | REAL | IOD_PTO | PTO:.PMMfaza17
PTOPMMfaza18 | REAL | IOD_PTO | PTO:.PMMfaza18
PTOPMMfaza19 | REAL | IOD_PTO | PTO:.PMMfaza19
PTOPMMfaza20 | REAL | IOD_PTO | PTO:.PMMfaza20
PTOPMMfaza21 | REAL | IOD_PTO | PTO:.PMMfaza21
PTOPMMfaza22 | REAL | IOD_PTO | PTO:.PMMfaza22
PTOPMMfaza23 | REAL | IOD_PTO | PTO:.PMMfaza23
PTOPMMfaza24 | REAL | IOD_PTO | PTO:.PMMfaza24
PTOPMMfaza25 | REAL | IOD_PTO | PTO:.PMMfaza25
PTOPMMfaza26 | REAL | IOD_PTO | PTO:.PMMfaza26
PTOPMMfaza27 | REAL | IOD_PTO | PTO:.PMMfaza27
PTOPMMfaza28 | REAL | IOD_PTO | PTO:.PMMfaza28
PTOPMMfaza29 | REAL | IOD_PTO | PTO:.PMMfaza29
PTOPMMfaza30 | REAL | IOD_PTO | PTO:.PMMfaza30
PTOPMMfaza31 | REAL | IOD_PTO | PTO:.PMMfaza31
PTOPMMfaza32 | REAL | IOD_PTO | PTO:.PMMfaza32
PTOPMMfaza33 | REAL | IOD_PTO | PTO:.PMMfaza33
PTOPMMfaza34 | REAL | IOD_PTO | PTO:.PMMfaza34
PTOPMMfaza35 | REAL | IOD_PTO | PTO:.PMMfaza35
PTOPMMfaza36 | REAL | IOD_PTO | PTO:.PMMfaza36
PTOPMMfaza37 | REAL | IOD_PTO | PTO:.PMMfaza37
PTOPMMfaza38 | REAL | IOD_PTO | PTO:.PMMfaza38
PTOPMMfaza39 | REAL | IOD_PTO | PTO:.PMMfaza39
PTOPMMfaza40 | REAL | IOD_PTO | PTO:.PMMfaza40
PTOPMMfaza41 | REAL | IOD_PTO | PTO:.PMMfaza41
PTOPMMfaza42 | REAL | IOD_PTO | PTO:.PMMfaza42
PTOPMMfaza6010 | REAL | IOD_PTO | PTO:.PMMfaza60[10]
PTOPMMfaza6011 | REAL | IOD_PTO | PTO:.PMMfaza60[11]
PTOPMMfaza6012 | REAL | IOD_PTO | PTO:.PMMfaza60[12]
PTOPMMfaza6013 | REAL | IOD_PTO | PTO:.PMMfaza60[13]
PTOPMMfaza6014 | REAL | IOD_PTO | PTO:.PMMfaza60[14]
PTOPMMfaza6015 | REAL | IOD_PTO | PTO:.PMMfaza60[15]
PTOPMMfaza6016 | REAL | IOD_PTO | PTO:.PMMfaza60[16]
PTOPMMfaza6017 | REAL | IOD_PTO | PTO:.PMMfaza60[17]
PTOPMMfaza6018 | REAL | IOD_PTO | PTO:.PMMfaza60[18]
PTOPMMfaza6019 | REAL | IOD_PTO | PTO:.PMMfaza60[19]
PTOPMMfaza601 | REAL | IOD_PTO | PTO:.PMMfaza60[1]
PTOPMMfaza6020 | REAL | IOD_PTO | PTO:.PMMfaza60[20]
PTOPMMfaza6021 | REAL | IOD_PTO | PTO:.PMMfaza60[21]
PTOPMMfaza6022 | REAL | IOD_PTO | PTO:.PMMfaza60[22]
PTOPMMfaza6023 | REAL | IOD_PTO | PTO:.PMMfaza60[23]
PTOPMMfaza6024 | REAL | IOD_PTO | PTO:.PMMfaza60[24]
PTOPMMfaza6025 | REAL | IOD_PTO | PTO:.PMMfaza60[25]
PTOPMMfaza6026 | REAL | IOD_PTO | PTO:.PMMfaza60[26]
PTOPMMfaza6027 | REAL | IOD_PTO | PTO:.PMMfaza60[27]
PTOPMMfaza6028 | REAL | IOD_PTO | PTO:.PMMfaza60[28]
PTOPMMfaza6029 | REAL | IOD_PTO | PTO:.PMMfaza60[29]
PTOPMMfaza602 | REAL | IOD_PTO | PTO:.PMMfaza60[2]
PTOPMMfaza6030 | REAL | IOD_PTO | PTO:.PMMfaza60[30]
PTOPMMfaza6031 | REAL | IOD_PTO | PTO:.PMMfaza60[31]
PTOPMMfaza6032 | REAL | IOD_PTO | PTO:.PMMfaza60[32]
PTOPMMfaza6033 | REAL | IOD_PTO | PTO:.PMMfaza60[33]
PTOPMMfaza6034 | REAL | IOD_PTO | PTO:.PMMfaza60[34]
PTOPMMfaza6035 | REAL | IOD_PTO | PTO:.PMMfaza60[35]
PTOPMMfaza6036 | REAL | IOD_PTO | PTO:.PMMfaza60[36]
PTOPMMfaza6037 | REAL | IOD_PTO | PTO:.PMMfaza60[37]
PTOPMMfaza6038 | REAL | IOD_PTO | PTO:.PMMfaza60[38]
PTOPMMfaza6039 | REAL | IOD_PTO | PTO:.PMMfaza60[39]
PTOPMMfaza603 | REAL | IOD_PTO | PTO:.PMMfaza60[3]
PTOPMMfaza6040 | REAL | IOD_PTO | PTO:.PMMfaza60[40]
PTOPMMfaza6041 | REAL | IOD_PTO | PTO:.PMMfaza60[41]
PTOPMMfaza6042 | REAL | IOD_PTO | PTO:.PMMfaza60[42]
PTOPMMfaza604 | REAL | IOD_PTO | PTO:.PMMfaza60[4]
PTOPMMfaza605 | REAL | IOD_PTO | PTO:.PMMfaza60[5]
PTOPMMfaza606 | REAL | IOD_PTO | PTO:.PMMfaza60[6]
PTOPMMfaza607 | REAL | IOD_PTO | PTO:.PMMfaza60[7]
PTOPMMfaza608 | REAL | IOD_PTO | PTO:.PMMfaza60[8]
PTOPMMfaza609 | REAL | IOD_PTO | PTO:.PMMfaza60[9]
PTOPMMfaza8010 | REAL | IOD_PTO | PTO:.PMMfaza80[10]
PTOPMMfaza8011 | REAL | IOD_PTO | PTO:.PMMfaza80[11]
PTOPMMfaza8012 | REAL | IOD_PTO | PTO:.PMMfaza80[12]
PTOPMMfaza8013 | REAL | IOD_PTO | PTO:.PMMfaza80[13]
PTOPMMfaza8014 | REAL | IOD_PTO | PTO:.PMMfaza80[14]
PTOPMMfaza8015 | REAL | IOD_PTO | PTO:.PMMfaza80[15]
PTOPMMfaza8016 | REAL | IOD_PTO | PTO:.PMMfaza80[16]
PTOPMMfaza8017 | REAL | IOD_PTO | PTO:.PMMfaza80[17]
PTOPMMfaza8018 | REAL | IOD_PTO | PTO:.PMMfaza80[18]
PTOPMMfaza8019 | REAL | IOD_PTO | PTO:.PMMfaza80[19]
PTOPMMfaza801 | REAL | IOD_PTO | PTO:.PMMfaza80[1]
PTOPMMfaza8020 | REAL | IOD_PTO | PTO:.PMMfaza80[20]
PTOPMMfaza8021 | REAL | IOD_PTO | PTO:.PMMfaza80[21]
PTOPMMfaza8022 | REAL | IOD_PTO | PTO:.PMMfaza80[22]
PTOPMMfaza8023 | REAL | IOD_PTO | PTO:.PMMfaza80[23]
PTOPMMfaza8024 | REAL | IOD_PTO | PTO:.PMMfaza80[24]
PTOPMMfaza8025 | REAL | IOD_PTO | PTO:.PMMfaza80[25]
PTOPMMfaza8026 | REAL | IOD_PTO | PTO:.PMMfaza80[26]
PTOPMMfaza8027 | REAL | IOD_PTO | PTO:.PMMfaza80[27]
PTOPMMfaza8028 | REAL | IOD_PTO | PTO:.PMMfaza80[28]
PTOPMMfaza8029 | REAL | IOD_PTO | PTO:.PMMfaza80[29]
PTOPMMfaza802 | REAL | IOD_PTO | PTO:.PMMfaza80[2]
PTOPMMfaza8030 | REAL | IOD_PTO | PTO:.PMMfaza80[30]
PTOPMMfaza8031 | REAL | IOD_PTO | PTO:.PMMfaza80[31]
PTOPMMfaza8032 | REAL | IOD_PTO | PTO:.PMMfaza80[32]
PTOPMMfaza8033 | REAL | IOD_PTO | PTO:.PMMfaza80[33]
PTOPMMfaza8034 | REAL | IOD_PTO | PTO:.PMMfaza80[34]
PTOPMMfaza8035 | REAL | IOD_PTO | PTO:.PMMfaza80[35]
PTOPMMfaza8036 | REAL | IOD_PTO | PTO:.PMMfaza80[36]
PTOPMMfaza8037 | REAL | IOD_PTO | PTO:.PMMfaza80[37]
PTOPMMfaza8038 | REAL | IOD_PTO | PTO:.PMMfaza80[38]
PTOPMMfaza8039 | REAL | IOD_PTO | PTO:.PMMfaza80[39]
PTOPMMfaza803 | REAL | IOD_PTO | PTO:.PMMfaza80[3]
PTOPMMfaza8040 | REAL | IOD_PTO | PTO:.PMMfaza80[40]
PTOPMMfaza8041 | REAL | IOD_PTO | PTO:.PMMfaza80[41]
PTOPMMfaza8042 | REAL | IOD_PTO | PTO:.PMMfaza80[42]
PTOPMMfaza804 | REAL | IOD_PTO | PTO:.PMMfaza80[4]
PTOPMMfaza805 | REAL | IOD_PTO | PTO:.PMMfaza80[5]
PTOPMMfaza806 | REAL | IOD_PTO | PTO:.PMMfaza80[6]
PTOPMMfaza807 | REAL | IOD_PTO | PTO:.PMMfaza80[7]
PTOPMMfaza808 | REAL | IOD_PTO | PTO:.PMMfaza80[8]
PTOPMMfaza809 | REAL | IOD_PTO | PTO:.PMMfaza80[9]
PTOPMMOverCurrentBetw1 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentBetw[1]
PTOPMMOverCurrentBetw2 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentBetw[2]
PTOPMMOverCurrentBetw3 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentBetw[3]
PTOPMMOverCurrentOver1 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentOver[1]
PTOPMMOverCurrentOver2 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentOver[2]
PTOPMMOverCurrentOver3 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentOver[3]
PTOQstanje10 | INT | IOD_PTO | PTO:.Qstanje[10] | BYTE
PTOQstanje11 | INT | IOD_PTO | PTO:.Qstanje[11] | BYTE
PTOQstanje12 | INT | IOD_PTO | PTO:.Qstanje[12] | BYTE
PTOQstanje13 | INT | IOD_PTO | PTO:.Qstanje[13] | BYTE
PTOQstanje14 | INT | IOD_PTO | PTO:.Qstanje[14] | BYTE
PTOQstanje15 | INT | IOD_PTO | PTO:.Qstanje[15] | BYTE
PTOQstanje16 | INT | IOD_PTO | PTO:.Qstanje[16] | BYTE
PTOQstanje17 | INT | IOD_PTO | PTO:.Qstanje[17] | BYTE
PTOQstanje18 | INT | IOD_PTO | PTO:.Qstanje[18] | BYTE
PTOQstanje19 | INT | IOD_PTO | PTO:.Qstanje[19] | BYTE
PTOQstanje1 | INT | IOD_PTO | PTO:.Qstanje[1] | BYTE
PTOQstanje20 | INT | IOD_PTO | PTO:.Qstanje[20] | BYTE
PTOQstanje21 | INT | IOD_PTO | PTO:.Qstanje[21] | BYTE
PTOQstanje22 | INT | IOD_PTO | PTO:.Qstanje[22] | BYTE
PTOQstanje23 | INT | IOD_PTO | PTO:.Qstanje[23] | BYTE
PTOQstanje24 | INT | IOD_PTO | PTO:.Qstanje[24] | BYTE
PTOQstanje25 | INT | IOD_PTO | PTO:.Qstanje[25] | BYTE
PTOQstanje26 | INT | IOD_PTO | PTO:.Qstanje[26] | BYTE
PTOQstanje27 | INT | IOD_PTO | PTO:.Qstanje[27] | BYTE
PTOQstanje28 | INT | IOD_PTO | PTO:.Qstanje[28] | BYTE
PTOQstanje29 | INT | IOD_PTO | PTO:.Qstanje[29] | BYTE
PTOQstanje2 | INT | IOD_PTO | PTO:.Qstanje[2] | BYTE
PTOQstanje30 | INT | IOD_PTO | PTO:.Qstanje[30] | BYTE
PTOQstanje31 | INT | IOD_PTO | PTO:.Qstanje[31] | BYTE
PTOQstanje32 | INT | IOD_PTO | PTO:.Qstanje[32] | BYTE
PTOQstanje33 | INT | IOD_PTO | PTO:.Qstanje[33] | BYTE
PTOQstanje34 | INT | IOD_PTO | PTO:.Qstanje[34] | BYTE
PTOQstanje35 | INT | IOD_PTO | PTO:.Qstanje[35] | BYTE
PTOQstanje3 | INT | IOD_PTO | PTO:.Qstanje[3] | BYTE
PTOQstanje4 | INT | IOD_PTO | PTO:.Qstanje[4] | BYTE
PTOQstanje5 | INT | IOD_PTO | PTO:.Qstanje[5] | BYTE
PTOQstanje6 | INT | IOD_PTO | PTO:.Qstanje[6] | BYTE
PTOQstanje7 | INT | IOD_PTO | PTO:.Qstanje[7] | BYTE
PTOQstanje8 | INT | IOD_PTO | PTO:.Qstanje[8] | BYTE
PTOQstanje9 | INT | IOD_PTO | PTO:.Qstanje[9] | BYTE
PTOSenzorTemp1 | REAL | IOD_PTO | PTO:.SenzorTemp[1]
PTOSenzorTemp2 | REAL | IOD_PTO | PTO:.SenzorTemp[2]
PTOSenzorTemp3 | REAL | IOD_PTO | PTO:.SenzorTemp[3]
PTOSenzorTemp4 | REAL | IOD_PTO | PTO:.SenzorTemp[4]
PTOSenzorTemp5 | REAL | IOD_PTO | PTO:.SenzorTemp[5]
PTOSenzorTemp6 | REAL | IOD_PTO | PTO:.SenzorTemp[6]
PTOSenzorVlaga1 | REAL | IOD_PTO | PTO:.SenzorVlaga[1]
PTOSenzorVlaga2 | REAL | IOD_PTO | PTO:.SenzorVlaga[2]
PTOSenzorVlaga3 | REAL | IOD_PTO | PTO:.SenzorVlaga[3]
PTOSenzorVlaga4 | REAL | IOD_PTO | PTO:.SenzorVlaga[4]
PTOSenzorVlaga5 | REAL | IOD_PTO | PTO:.SenzorVlaga[5]
PTOSenzorVlaga6 | REAL | IOD_PTO | PTO:.SenzorVlaga[6]
PTOSetDateTime | DIGITAL | IOD_PTO | PTO:.SetDateTime
PTOSetDateTimeDemand | DIGITAL | IOD_PTO | PTO:.SetDateTimeDemand
PTOSetDateTimeError | DIGITAL | IOD_PTO | PTO:.SetDateTimeError
PTOSetDateTimeFinished | DIGITAL | IOD_PTO | PTO:.SetDateTimeFinished
PTOSetRemoteOnOff1 | DIGITAL | IOD_PTO | PTO:.SetRemoteOnOff[1]
PTOSetRemoteOnOff2 | DIGITAL | IOD_PTO | PTO:.SetRemoteOnOff[2]
PTOSlabaBaterijaPLC_A1 | DIGITAL | IOD_PTO | PTO:.SlabaBaterijaPLC_A1
PTOTempAlarmPoint0 | REAL | IOD_PTO | PTO:.TempAlarmPoint[0]
PTOTempAlarmPoint1 | REAL | IOD_PTO | PTO:.TempAlarmPoint[1]
PTOTempAlarmPoint2 | REAL | IOD_PTO | PTO:.TempAlarmPoint[2]
PTOTempAlarmPoint3 | REAL | IOD_PTO | PTO:.TempAlarmPoint[3]
PTOTempMaxPoint0 | REAL | IOD_PTO | PTO:.TempMaxPoint[0]
PTOTempMaxPoint1 | REAL | IOD_PTO | PTO:.TempMaxPoint[1]
PTOTempMaxPoint2 | REAL | IOD_PTO | PTO:.TempMaxPoint[2]
PTOTempMaxPoint3 | REAL | IOD_PTO | PTO:.TempMaxPoint[3]
PTOTempPovp0 | REAL | IOD_PTO | PTO:.TempPovp[0]
PTOTempPovp1 | REAL | IOD_PTO | PTO:.TempPovp[1]
PTOTempPovp2 | REAL | IOD_PTO | PTO:.TempPovp[2]
PTOTempPovp3 | REAL | IOD_PTO | PTO:.TempPovp[3]
PTOTempSetPoint0 | REAL | IOD_PTO | PTO:.TempSetPoint[0]
PTOTempSetPoint1 | REAL | IOD_PTO | PTO:.TempSetPoint[1]
PTOTempSetPoint2 | REAL | IOD_PTO | PTO:.TempSetPoint[2]
PTOTempSetPoint3 | REAL | IOD_PTO | PTO:.TempSetPoint[3]
PTOTempTSprevisoka1 | DIGITAL | IOD_PTO | PTO:.TempTSprevisoka[1]
PTOTempTSprevisoka2 | DIGITAL | IOD_PTO | PTO:.TempTSprevisoka[2]
PTOTempTSprevisoka3 | DIGITAL | IOD_PTO | PTO:.TempTSprevisoka[3]
PTOTempTSprevisokaSum | DIGITAL | IOD_PTO | PTO:.TempTSprevisokaSum
PTOUPS1Errors10 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[10]
PTOUPS1Errors11 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[11]
PTOUPS1Errors12 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[12]
PTOUPS1Errors13 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[13]
PTOUPS1Errors14 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[14]
PTOUPS1Errors15 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[15]
PTOUPS1Errors16 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[16]
PTOUPS1Errors17 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[17]
PTOUPS1Errors18 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[18]
PTOUPS1Errors19 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[19]
PTOUPS1Errors1 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[1]
PTOUPS1Errors20 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[20]
PTOUPS1Errors21 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[21]
PTOUPS1Errors22 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[22]
PTOUPS1Errors23 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[23]
PTOUPS1Errors24 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[24]
PTOUPS1Errors25 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[25]
PTOUPS1Errors2 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[2]
PTOUPS1Errors3 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[3]
PTOUPS1Errors4 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[4]
PTOUPS1Errors5 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[5]
PTOUPS1Errors6 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[6]
PTOUPS1Errors7 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[7]
PTOUPS1Errors8 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[8]
PTOUPS1Errors9 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[9]
PTOUPS2Errors10 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[10]
PTOUPS2Errors11 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[11]
PTOUPS2Errors12 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[12]
PTOUPS2Errors13 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[13]
PTOUPS2Errors14 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[14]
PTOUPS2Errors15 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[15]
PTOUPS2Errors16 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[16]
PTOUPS2Errors17 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[17]
PTOUPS2Errors18 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[18]
PTOUPS2Errors19 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[19]
PTOUPS2Errors1 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[1]
PTOUPS2Errors20 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[20]
PTOUPS2Errors21 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[21]
PTOUPS2Errors22 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[22]
PTOUPS2Errors23 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[23]
PTOUPS2Errors24 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[24]
PTOUPS2Errors25 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[25]
PTOUPS2Errors2 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[2]
PTOUPS2Errors3 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[3]
PTOUPS2Errors4 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[4]
PTOUPS2Errors5 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[5]
PTOUPS2Errors6 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[6]
PTOUPS2Errors7 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[7]
PTOUPS2Errors8 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[8]
PTOUPS2Errors9 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[9]
PTOUPS1AlarmAwaitingPower | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmAwaitingPower
PTOUPS1AlarmBypassBad | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmBypassBad
PTOUPS1AlarmChargerFailed | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmChargerFailed
PTOUPS1AlarmCommunicationsLost | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmCommunicationsLost
PTOUPS1AlarmDepletedBattery | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmDepletedBattery
PTOUPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmDiagnosticTestFailed
PTOUPS1AlarmInverterError | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmInverterError
PTOUPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmIzhodOffKotZahtevano
PTOUPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmIzhodPreobremenjen
PTOUPS1AlarmLowBattery | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmLowBattery
PTOUPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmNapakaNaVarovalki
PTOUPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmNapakaNaVentilatorju
PTOUPS1AlarmOnBattery | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmOnBattery
PTOUPS1AlarmOnBypass | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmOnBypass
PTOUPS1AlarmShutdownImminent | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmShutdownImminent
PTOUPS1AlarmShutdownPending | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmShutdownPending
PTOUPS1AlarmSlabaBaterija | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmSlabaBaterija
PTOUPS1AlarmSplosnaNapaka | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmSplosnaNapaka
PTOUPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmStanjeIzhodaIzvenToleranc
PTOUPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmStanjeVhodaIzvenToleranc
PTOUPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmTemperaturaIzvenToleranc
PTOUPS1AlarmTestInProgres | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmTestInProgres
PTOUPS1AlarmUPSIzhodOff | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmUPSIzhodOff
PTOUPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmUPSOffKotZahtevano
PTOUPS1AlarmUPSSystemOff | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmUPSSystemOff
PTOUPS1EstimatedChargeRemaining | REAL | IOD_PTO | PTO:.UPS[1].EstimatedChargeRemaining
PTOUPS1EstimatedMinutesRemaining | REAL | IOD_PTO | PTO:.UPS[1].EstimatedMinutesRemaining
PTOUPS1InverterStatus | INT | IOD_PTO | PTO:.UPS[1].InverterStatus
PTOUPS1IzhodMocL1 | REAL | IOD_PTO | PTO:.UPS[1].IzhodMocL1
PTOUPS1IzhodMocL2 | REAL | IOD_PTO | PTO:.UPS[1].IzhodMocL2
PTOUPS1IzhodMocL3 | REAL | IOD_PTO | PTO:.UPS[1].IzhodMocL3
PTOUPS1Napaka | DIGITAL | IOD_PTO | PTO:.UPS[1].Napaka
PTOUPS1NapetostBaterije | REAL | IOD_PTO | PTO:.UPS[1].NapetostBaterije
PTOUPS1OutputStatus | INT | IOD_PTO | PTO:.UPS[1].OutputStatus
PTOUPS1StatusBaterije | INT | IOD_PTO | PTO:.UPS[1].StatusBaterije
PTOUPS1StatusEcomodeAktiven | DIGITAL | IOD_PTO | PTO:.UPS[1].StatusEcomodeAktiven
PTOUPS1StatusInverterIsOn | DIGITAL | IOD_PTO | PTO:.UPS[1].StatusInverterIsOn
PTOUPS1StatusStopOperation | DIGITAL | IOD_PTO | PTO:.UPS[1].StatusStopOperation
PTOUPS1SteviloIzpadovVhodneLinije | INT | IOD_PTO | PTO:.UPS[1].SteviloIzpadovVhodneLinije
PTOUPS1TemperaturaBaterije | REAL | IOD_PTO | PTO:.UPS[1].TemperaturaBaterije
PTOUPS1UnitStatus | INT | IOD_PTO | PTO:.UPS[1].UnitStatus
PTOUPS1VhodFrekvencaL1 | REAL | IOD_PTO | PTO:.UPS[1].VhodFrekvencaL1
PTOUPS1VhodFrekvencaL2 | REAL | IOD_PTO | PTO:.UPS[1].VhodFrekvencaL2
PTOUPS1VhodFrekvencaL3 | REAL | IOD_PTO | PTO:.UPS[1].VhodFrekvencaL3
PTOUPS1VhodNapetostL1 | REAL | IOD_PTO | PTO:.UPS[1].VhodNapetostL1
PTOUPS1VhodNapetostL2 | REAL | IOD_PTO | PTO:.UPS[1].VhodNapetostL2
PTOUPS1VhodNapetostL3 | REAL | IOD_PTO | PTO:.UPS[1].VhodNapetostL3
PTOUPS2AlarmAwaitingPower | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmAwaitingPower
PTOUPS2AlarmBypassBad | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmBypassBad
PTOUPS2AlarmChargerFailed | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmChargerFailed
PTOUPS2AlarmCommunicationsLost | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmCommunicationsLost
PTOUPS2AlarmDepletedBattery | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmDepletedBattery
PTOUPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmDiagnosticTestFailed
PTOUPS2AlarmInverterError | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmInverterError
PTOUPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmIzhodOffKotZahtevano
PTOUPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmIzhodPreobremenjen
PTOUPS2AlarmLowBattery | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmLowBattery
PTOUPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmNapakaNaVarovalki
PTOUPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmNapakaNaVentilatorju
PTOUPS2AlarmOnBattery | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmOnBattery
PTOUPS2AlarmOnBypass | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmOnBypass
PTOUPS2AlarmShutdownImminent | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmShutdownImminent
PTOUPS2AlarmShutdownPending | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmShutdownPending
PTOUPS2AlarmSlabaBaterija | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmSlabaBaterija
PTOUPS2AlarmSplosnaNapaka | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmSplosnaNapaka
PTOUPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmStanjeIzhodaIzvenToleranc
PTOUPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmStanjeVhodaIzvenToleranc
PTOUPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmTemperaturaIzvenToleranc
PTOUPS2AlarmTestInProgres | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmTestInProgres
PTOUPS2AlarmUPSIzhodOff | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmUPSIzhodOff
PTOUPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmUPSOffKotZahtevano
PTOUPS2AlarmUPSSystemOff | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmUPSSystemOff
PTOUPS2EstimatedChargeRemaining | REAL | IOD_PTO | PTO:.UPS[2].EstimatedChargeRemaining
PTOUPS2EstimatedMinutesRemaining | REAL | IOD_PTO | PTO:.UPS[2].EstimatedMinutesRemaining
PTOUPS2InverterStatus | INT | IOD_PTO | PTO:.UPS[2].InverterStatus
PTOUPS2IzhodMocL1 | REAL | IOD_PTO | PTO:.UPS[2].IzhodMocL1
PTOUPS2IzhodMocL2 | REAL | IOD_PTO | PTO:.UPS[2].IzhodMocL2
PTOUPS2IzhodMocL3 | REAL | IOD_PTO | PTO:.UPS[2].IzhodMocL3
PTOUPS2Napaka | DIGITAL | IOD_PTO | PTO:.UPS[2].Napaka
PTOUPS2NapetostBaterije | REAL | IOD_PTO | PTO:.UPS[2].NapetostBaterije
PTOUPS2OutputStatus | INT | IOD_PTO | PTO:.UPS[2].OutputStatus
PTOUPS2StatusBaterije | INT | IOD_PTO | PTO:.UPS[2].StatusBaterije
PTOUPS2StatusEcomodeAktiven | DIGITAL | IOD_PTO | PTO:.UPS[2].StatusEcomodeAktiven
PTOUPS2StatusInverterIsOn | DIGITAL | IOD_PTO | PTO:.UPS[2].StatusInverterIsOn
PTOUPS2StatusStopOperation | DIGITAL | IOD_PTO | PTO:.UPS[2].StatusStopOperation
PTOUPS2SteviloIzpadovVhodneLinije | INT | IOD_PTO | PTO:.UPS[2].SteviloIzpadovVhodneLinije
PTOUPS2TemperaturaBaterije | REAL | IOD_PTO | PTO:.UPS[2].TemperaturaBaterije
PTOUPS2UnitStatus | INT | IOD_PTO | PTO:.UPS[2].UnitStatus
PTOUPS2VhodFrekvencaL1 | REAL | IOD_PTO | PTO:.UPS[2].VhodFrekvencaL1
PTOUPS2VhodFrekvencaL2 | REAL | IOD_PTO | PTO:.UPS[2].VhodFrekvencaL2
PTOUPS2VhodFrekvencaL3 | REAL | IOD_PTO | PTO:.UPS[2].VhodFrekvencaL3
PTOUPS2VhodNapetostL1 | REAL | IOD_PTO | PTO:.UPS[2].VhodNapetostL1
PTOUPS2VhodNapetostL2 | REAL | IOD_PTO | PTO:.UPS[2].VhodNapetostL2
PTOUPS2VhodNapetostL3 | REAL | IOD_PTO | PTO:.UPS[2].VhodNapetostL3
PTOUserCurrentLevel | INT | IOD_PTO | PTO:.UserCurrentLevel | BYTE
PTOUserCurrentName | STRING | IOD_PTO | PTO:.UserCurrentName
PTOUserLoggedIn | DIGITAL | IOD_PTO | PTO:.UserLoggedIn
PTOVlagaPovp1 | REAL | IOD_PTO | PTO:.VlagaPovp[1]
PTOVlagaPovp2 | REAL | IOD_PTO | PTO:.VlagaPovp[2]
PTOVlagaPovp3 | REAL | IOD_PTO | PTO:.VlagaPovp[3]
PTORazlikaUr | REAL | IOD_PTO | PTO:.RazlikaUr
PTODIN_A1Q11_OdcUpsB_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q11_OdcUpsB_IZP
PTODIN_A1Q12_OdcByUpsB_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q12_OdcByUpsB_IZP
PTODIN_A1Q13_OdcByB_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q13_OdcByB_IZP
PTODIN_UQ11_OdcPMMB_IZP | DIGITAL | IOD_PTO | PTO:.DIN_UQ11_OdcPMMB_IZP
PTODIN_UQ12_OdcPMMB_IZP | DIGITAL | IOD_PTO | PTO:.DIN_UQ12_OdcPMMB_IZP
PTODIN_PrenapA3_OK | DIGITAL | IOD_PTO | PTO:.DIN_PrenapA3_OK
PTODIN_A1Q0_GlavnoStiB_ON | DIGITAL | IOD_PTO | PTO:.DIN_A1Q0_GlavnoStiB_ON
PTODIN_A1Q11_OdcUpsB_ON | DIGITAL | IOD_PTO | PTO:.DIN_A1Q11_OdcUpsB_ON
PTODIN_A1Q12_OdcByUpsB_ON | DIGITAL | IOD_PTO | PTO:.DIN_A1Q12_OdcByUpsB_ON
PTODI_A1Q13_OdcByB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q13_OdcByB_ON
PTODIN_A1Q01_DovUpsB_ON | DIGITAL | IOD_PTO | PTO:.DIN_A1Q01_DovUpsB_ON
PTODI_A1Q02_DovByB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q02_DovByB_ON
PTODIN_UQ11_OdcPMMB_ON | DIGITAL | IOD_PTO | PTO:.DIN_UQ11_OdcPMMB_ON
PTODI_UQ12_OdcPMMB_ON | DIGITAL | IOD_PTO | PTO:.DI_UQ12_OdcPMMB_ON
PTOKlima1NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].NapacnoGesloAlarm
PTOKlima1ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].ExtTempHumAlarm
PTOKlima1PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].PoplavniAlarm
PTOKlima1VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[1].VisokPritiskKompresor1
PTOKlima1VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[1].VisokPritiskKompresor2
PTOKlima1ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[1].ElVentilKompresor1ERR
PTOKlima1ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[1].ElVentilKompresor2ERR
PTOKlima1WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].WrongPhaseSeqAlarm
PTOKlima1PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[1].PrekinjenLANalarm
PTOKlima1CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[1].CWTempHighForDehum
PTOKlima1CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[1].CWVentilErrOrLowFlow
PTOKlima1NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaPriPretokuVode
PTOKlima1CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[1].CWhighTemp
PTOKlima1NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorHotWTemp
PTOKlima1NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorCondWTemp
PTOKlima1NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorCW
PTOKlima1Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Kompresor3naMejiObrUr
PTOKlima1Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Kompresor4naMejiObrUr
PTOKlima1ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].ZracniFilterNaMejiObrUr
PTOKlima1Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Grelec1naMejiObrUr
PTOKlima1Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Grelec2naMejiObrUr
PTOKlima1VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].VlazilecNaMejiObrUr
PTOKlima1AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].AirCondUnitNaMejiObrUr
PTOKlima1DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[1].DigIn2Alarm
PTOKlima1DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[1].DigIn4Alarm
PTOKlima1DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[1].DigIn6Alarm
PTOKlima1VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].VlazilecGenAlarm
PTOKlima1General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].General2ndLevAlarm
PTOKlima1UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].UnitOnRotAlarm
PTOKlima1UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[1].UnitOnAlarmA
PTOKlima1UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[1].UnitOnAlarmB
PTOKlima1UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[1].UnitOnAlarmC
PTOKlima2NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].NapacnoGesloAlarm
PTOKlima2ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].ExtTempHumAlarm
PTOKlima2PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].PoplavniAlarm
PTOKlima2VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[2].VisokPritiskKompresor1
PTOKlima2VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[2].VisokPritiskKompresor2
PTOKlima2ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[2].ElVentilKompresor1ERR
PTOKlima2ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[2].ElVentilKompresor2ERR
PTOKlima2WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].WrongPhaseSeqAlarm
PTOKlima2PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[2].PrekinjenLANalarm
PTOKlima2CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[2].CWTempHighForDehum
PTOKlima2CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[2].CWVentilErrOrLowFlow
PTOKlima2NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaPriPretokuVode
PTOKlima2CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[2].CWhighTemp
PTOKlima2NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorHotWTemp
PTOKlima2NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorCondWTemp
PTOKlima2NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorCW
PTOKlima2Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Kompresor3naMejiObrUr
PTOKlima2Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Kompresor4naMejiObrUr
PTOKlima2ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].ZracniFilterNaMejiObrUr
PTOKlima2Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Grelec1naMejiObrUr
PTOKlima2Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Grelec2naMejiObrUr
PTOKlima2VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].VlazilecNaMejiObrUr
PTOKlima2AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].AirCondUnitNaMejiObrUr
PTOKlima2DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[2].DigIn2Alarm
PTOKlima2DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[2].DigIn4Alarm
PTOKlima2DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[2].DigIn6Alarm
PTOKlima2VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].VlazilecGenAlarm
PTOKlima2General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].General2ndLevAlarm
PTOKlima2UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].UnitOnRotAlarm
PTOKlima2UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[2].UnitOnAlarmA
PTOKlima2UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[2].UnitOnAlarmB
PTOKlima2UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[2].UnitOnAlarmC
PTOKlima3NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].NapacnoGesloAlarm
PTOKlima3ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].ExtTempHumAlarm
PTOKlima3PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].PoplavniAlarm
PTOKlima3VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[3].VisokPritiskKompresor1
PTOKlima3VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[3].VisokPritiskKompresor2
PTOKlima3ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[3].ElVentilKompresor1ERR
PTOKlima3ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[3].ElVentilKompresor2ERR
PTOKlima3WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].WrongPhaseSeqAlarm
PTOKlima3PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[3].PrekinjenLANalarm
PTOKlima3CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[3].CWTempHighForDehum
PTOKlima3CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[3].CWVentilErrOrLowFlow
PTOKlima3NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaPriPretokuVode
PTOKlima3CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[3].CWhighTemp
PTOKlima3NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorHotWTemp
PTOKlima3NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorCondWTemp
PTOKlima3NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorCW
PTOKlima3Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Kompresor3naMejiObrUr
PTOKlima3Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Kompresor4naMejiObrUr
PTOKlima3ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].ZracniFilterNaMejiObrUr
PTOKlima3Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Grelec1naMejiObrUr
PTOKlima3Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Grelec2naMejiObrUr
PTOKlima3VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].VlazilecNaMejiObrUr
PTOKlima3AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].AirCondUnitNaMejiObrUr
PTOKlima3DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[3].DigIn2Alarm
PTOKlima3DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[3].DigIn4Alarm
PTOKlima3DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[3].DigIn6Alarm
PTOKlima3VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].VlazilecGenAlarm
PTOKlima3General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].General2ndLevAlarm
PTOKlima3UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].UnitOnRotAlarm
PTOKlima3UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[3].UnitOnAlarmA
PTOKlima3UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[3].UnitOnAlarmB
PTOKlima3UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[3].UnitOnAlarmC
PTOKlima4NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].NapacnoGesloAlarm
PTOKlima4ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].ExtTempHumAlarm
PTOKlima4PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].PoplavniAlarm
PTOKlima4VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[4].VisokPritiskKompresor1
PTOKlima4VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[4].VisokPritiskKompresor2
PTOKlima4ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[4].ElVentilKompresor1ERR
PTOKlima4ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[4].ElVentilKompresor2ERR
PTOKlima4WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].WrongPhaseSeqAlarm
PTOKlima4PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[4].PrekinjenLANalarm
PTOKlima4CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[4].CWTempHighForDehum
PTOKlima4CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[4].CWVentilErrOrLowFlow
PTOKlima4NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaPriPretokuVode
PTOKlima4CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[4].CWhighTemp
PTOKlima4NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorHotWTemp
PTOKlima4NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorCondWTemp
PTOKlima4NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorCW
PTOKlima4Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Kompresor3naMejiObrUr
PTOKlima4Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Kompresor4naMejiObrUr
PTOKlima4ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].ZracniFilterNaMejiObrUr
PTOKlima4Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Grelec1naMejiObrUr
PTOKlima4Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Grelec2naMejiObrUr
PTOKlima4VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].VlazilecNaMejiObrUr
PTOKlima4AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].AirCondUnitNaMejiObrUr
PTOKlima4DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[4].DigIn2Alarm
PTOKlima4DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[4].DigIn4Alarm
PTOKlima4DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[4].DigIn6Alarm
PTOKlima4VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].VlazilecGenAlarm
PTOKlima4General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].General2ndLevAlarm
PTOKlima4UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].UnitOnRotAlarm
PTOKlima4UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[4].UnitOnAlarmA
PTOKlima4UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[4].UnitOnAlarmB
PTOKlima4UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[4].UnitOnAlarmC
PTOKlima5NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].NapacnoGesloAlarm
PTOKlima5ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].ExtTempHumAlarm
PTOKlima5PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].PoplavniAlarm
PTOKlima5VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[5].VisokPritiskKompresor1
PTOKlima5VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[5].VisokPritiskKompresor2
PTOKlima5ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[5].ElVentilKompresor1ERR
PTOKlima5ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[5].ElVentilKompresor2ERR
PTOKlima5WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].WrongPhaseSeqAlarm
PTOKlima5PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[5].PrekinjenLANalarm
PTOKlima5CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[5].CWTempHighForDehum
PTOKlima5CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[5].CWVentilErrOrLowFlow
PTOKlima5NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaPriPretokuVode
PTOKlima5CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[5].CWhighTemp
PTOKlima5NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorHotWTemp
PTOKlima5NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorCondWTemp
PTOKlima5NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorCW
PTOKlima5Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Kompresor3naMejiObrUr
PTOKlima5Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Kompresor4naMejiObrUr
PTOKlima5ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].ZracniFilterNaMejiObrUr
PTOKlima5Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Grelec1naMejiObrUr
PTOKlima5Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Grelec2naMejiObrUr
PTOKlima5VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].VlazilecNaMejiObrUr
PTOKlima5AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].AirCondUnitNaMejiObrUr
PTOKlima5DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[5].DigIn2Alarm
PTOKlima5DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[5].DigIn4Alarm
PTOKlima5DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[5].DigIn6Alarm
PTOKlima5VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].VlazilecGenAlarm
PTOKlima5General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].General2ndLevAlarm
PTOKlima5UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].UnitOnRotAlarm
PTOKlima5UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[5].UnitOnAlarmA
PTOKlima5UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[5].UnitOnAlarmB
PTOKlima5UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[5].UnitOnAlarmC
PTOKlima6NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].NapacnoGesloAlarm
PTOKlima6ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].ExtTempHumAlarm
PTOKlima6PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].PoplavniAlarm
PTOKlima6VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[6].VisokPritiskKompresor1
PTOKlima6VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[6].VisokPritiskKompresor2
PTOKlima6ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[6].ElVentilKompresor1ERR
PTOKlima6ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[6].ElVentilKompresor2ERR
PTOKlima6WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].WrongPhaseSeqAlarm
PTOKlima6PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[6].PrekinjenLANalarm
PTOKlima6CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[6].CWTempHighForDehum
PTOKlima6CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[6].CWVentilErrOrLowFlow
PTOKlima6NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaPriPretokuVode
PTOKlima6CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[6].CWhighTemp
PTOKlima6NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorHotWTemp
PTOKlima6NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorCondWTemp
PTOKlima6NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorCW
PTOKlima6Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Kompresor3naMejiObrUr
PTOKlima6Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Kompresor4naMejiObrUr
PTOKlima6ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].ZracniFilterNaMejiObrUr
PTOKlima6Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Grelec1naMejiObrUr
PTOKlima6Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Grelec2naMejiObrUr
PTOKlima6VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].VlazilecNaMejiObrUr
PTOKlima6AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].AirCondUnitNaMejiObrUr
PTOKlima6DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[6].DigIn2Alarm
PTOKlima6DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[6].DigIn4Alarm
PTOKlima6DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[6].DigIn6Alarm
PTOKlima6VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].VlazilecGenAlarm
PTOKlima6General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].General2ndLevAlarm
PTOKlima6UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].UnitOnRotAlarm
PTOKlima6UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[6].UnitOnAlarmA
PTOKlima6UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[6].UnitOnAlarmB
PTOKlima6UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[6].UnitOnAlarmC
PTOKlima1NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[1].NastTempHlajenje
PTOKlima2NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[2].NastTempHlajenje
PTOKlima3NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[3].NastTempHlajenje
PTOKlima4NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[4].NastTempHlajenje
PTOKlima5NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[5].NastTempHlajenje
PTOKlima6NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[6].NastTempHlajenje
PTOKlima1NastTempGretje | REAL | IOD_PTO | PTO:.Klima[1].NastTempGretje
PTOKlima2NastTempGretje | REAL | IOD_PTO | PTO:.Klima[2].NastTempGretje
PTOKlima3NastTempGretje | REAL | IOD_PTO | PTO:.Klima[3].NastTempGretje
PTOKlima4NastTempGretje | REAL | IOD_PTO | PTO:.Klima[4].NastTempGretje
PTOKlima5NastTempGretje | REAL | IOD_PTO | PTO:.Klima[5].NastTempGretje
PTOKlima6NastTempGretje | REAL | IOD_PTO | PTO:.Klima[6].NastTempGretje
PTOKlima1TempHladneVode | REAL | IOD_PTO | PTO:.Klima[1].TempHladneVode
PTOKlima2TempHladneVode | REAL | IOD_PTO | PTO:.Klima[2].TempHladneVode
PTOKlima3TempHladneVode | REAL | IOD_PTO | PTO:.Klima[3].TempHladneVode
PTOKlima4TempHladneVode | REAL | IOD_PTO | PTO:.Klima[4].TempHladneVode
PTOKlima5TempHladneVode | REAL | IOD_PTO | PTO:.Klima[5].TempHladneVode
PTOKlima6TempHladneVode | REAL | IOD_PTO | PTO:.Klima[6].TempHladneVode
PTOKlima1TempTopleVode | REAL | IOD_PTO | PTO:.Klima[1].TempTopleVode
PTOKlima2TempTopleVode | REAL | IOD_PTO | PTO:.Klima[2].TempTopleVode
PTOKlima3TempTopleVode | REAL | IOD_PTO | PTO:.Klima[3].TempTopleVode
PTOKlima4TempTopleVode | REAL | IOD_PTO | PTO:.Klima[4].TempTopleVode
PTOKlima5TempTopleVode | REAL | IOD_PTO | PTO:.Klima[5].TempTopleVode
PTOKlima6TempTopleVode | REAL | IOD_PTO | PTO:.Klima[6].TempTopleVode
PTOKlima1Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[1].Komp1On
PTOKlima1Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[1].Komp2On
PTOKlima1Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[1].Komp3On
PTOKlima1Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[1].Komp4On
PTOKlima2Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[2].Komp1On
PTOKlima2Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[2].Komp2On
PTOKlima2Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[2].Komp3On
PTOKlima2Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[2].Komp4On
PTOKlima3Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[3].Komp1On
PTOKlima3Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[3].Komp2On
PTOKlima3Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[3].Komp3On
PTOKlima3Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[3].Komp4On
PTOKlima4Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[4].Komp1On
PTOKlima4Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[4].Komp2On
PTOKlima4Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[4].Komp3On
PTOKlima4Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[4].Komp4On
PTOKlima5Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[5].Komp1On
PTOKlima5Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[5].Komp2On
PTOKlima5Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[5].Komp3On
PTOKlima5Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[5].Komp4On
PTOKlima6Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[6].Komp1On
PTOKlima6Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[6].Komp2On
PTOKlima6Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[6].Komp3On
PTOKlima6Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[6].Komp4On
PTOKlima1GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[1].GretjeStopnja1
PTOKlima1GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[1].GretjeStopnja2
PTOKlima1GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[1].GretjeStopnja3
PTOKlima2GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[2].GretjeStopnja1
PTOKlima2GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[2].GretjeStopnja2
PTOKlima2GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[2].GretjeStopnja3
PTOKlima3GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[3].GretjeStopnja1
PTOKlima3GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[3].GretjeStopnja2
PTOKlima3GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[3].GretjeStopnja3
PTOKlima4GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[4].GretjeStopnja1
PTOKlima4GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[4].GretjeStopnja2
PTOKlima4GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[4].GretjeStopnja3
PTOKlima5GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[5].GretjeStopnja1
PTOKlima5GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[5].GretjeStopnja2
PTOKlima5GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[5].GretjeStopnja3
PTOKlima6GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[6].GretjeStopnja1
PTOKlima6GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[6].GretjeStopnja2
PTOKlima6GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[6].GretjeStopnja3
PTOKlima1HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[1].HotGasOn
PTOKlima2HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[2].HotGasOn
PTOKlima3HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[3].HotGasOn
PTOKlima4HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[4].HotGasOn
PTOKlima5HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[5].HotGasOn
PTOKlima6HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[6].HotGasOn
PTOKlima1EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[1].EmergencyWorking
PTOKlima2EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[2].EmergencyWorking
PTOKlima3EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[3].EmergencyWorking
PTOKlima4EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[4].EmergencyWorking
PTOKlima5EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[5].EmergencyWorking
PTOKlima6EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[6].EmergencyWorking
PTODI_A1Q01_DovUpsB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q01_DovUpsB_ON
PTODI_A1Q0_GlavnoStiB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q0_GlavnoStiB_ON
PTODI_A1Q11_OdcUpsB_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q11_OdcUpsB_IZP
PTODI_A1Q11_OdcUpsB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q11_OdcUpsB_ON
PTODI_A1Q12_OdcByUpsB_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q12_OdcByUpsB_IZP
PTODI_A1Q12_OdcByUpsB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q12_OdcByUpsB_ON
PTODI_A1Q13_OdcByB_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q13_OdcByB_IZP
PTOZamikVklopa | REAL | IOD_PTO | PTO:.ZamikVklopa
PTOErrCommScada2 | DIGITAL | IOD_PTO | PTO:.ErrCommScada2
PTOComSCADA2 | DIGITAL | IOD_PTO | PTO:.ComSCADA2
PTOComSCADA3 | DIGITAL | IOD_PTO | PTO:.ComSCADA3
PTOkom_nast_cas_izpada | UINT | IOD_PTO | PTO:.kom_nast_cas_izpada

## variable_2
PTOAlarmGenComm | DIGITAL | IOD_PTO | PTO:.AlarmGenComm
PTOAlarmGenKlima1 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[1]
PTOAlarmGenKlima2 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[2]
PTOAlarmGenKlima3 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[3]
PTOAlarmGenKlima4 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[4]
PTOAlarmGenKlima5 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[5]
PTOAlarmGenKlima6 | DIGITAL | IOD_PTO | PTO:.AlarmGenKlima[6]
PTOAlarmGenPMM | DIGITAL | IOD_PTO | PTO:.AlarmGenPMM
PTOAlarmGenRest | DIGITAL | IOD_PTO | PTO:.AlarmGenRest
PTOAlarmGenSenzor | DIGITAL | IOD_PTO | PTO:.AlarmGenSenzor
PTOAlarmGenStikala | DIGITAL | IOD_PTO | PTO:.AlarmGenStikala
PTOAlarmGenTemp | DIGITAL | IOD_PTO | PTO:.AlarmGenTemp
PTOAlarmGenUPS1 | DIGITAL | IOD_PTO | PTO:.AlarmGenUPS1
PTOAlarmGenUPS2 | DIGITAL | IOD_PTO | PTO:.AlarmGenUPS2
PTOComSCADA | DIGITAL | IOD_PTO | PTO:.ComSCADA
PTOComSCADA1 | DIGITAL | IOD_PTO | PTO:.ComSCADA1
PTODI_A1Q01_DovUpsA_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q01_DovUpsA_ON
PTODI_A1Q02_DovByA_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q02_DovByA_ON
PTODI_A1Q0_GlavnoSti_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q0_GlavnoSti_ON
PTODI_A1Q11_OdcUpsA_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q11_OdcUpsA_IZP
PTODI_A1Q11_OdcUpsA_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q11_OdcUpsA_ON
PTODI_A1Q12_OdcByUpsA_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q12_OdcByUpsA_IZP
PTODI_A1Q12_OdcByUpsA_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q12_OdcByUpsA_ON
PTODI_A1Q13_OdcByA_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q13_OdcByA_IZP
PTODI_A1Q13_OdcByA_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q13_OdcByA_ON
PTODI_A2Q0_GlavnoSti_ON | DIGITAL | IOD_PTO | PTO:.DI_A2Q0_GlavnoSti_ON
PTODI_F201_OdcKl1ZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F201_OdcKl1ZE_IZP
PTODI_F201_OdcKl1ZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F201_OdcKl1ZE_ON
PTODI_F202_OdcKl2ZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F202_OdcKl2ZE_IZP
PTODI_F202_OdcKl2ZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F202_OdcKl2ZE_ON
PTODI_F203_OdcKl3ZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F203_OdcKl3ZE_IZP
PTODI_F203_OdcKl3ZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F203_OdcKl3ZE_ON
PTODI_F204_OdcKl4ZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F204_OdcKl4ZE_IZP
PTODI_F204_OdcKl4ZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F204_OdcKl4ZE_ON
PTODI_F205_OdcKl5aZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F205_OdcKl5aZE_IZP
PTODI_F205_OdcKl5aZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F205_OdcKl5aZE_ON
PTODI_F206_OdcKl5bZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F206_OdcKl5bZE_IZP
PTODI_F206_OdcKl5bZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F206_OdcKl5bZE_ON
PTODI_F207_OdcKl6aZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F207_OdcKl6aZE_IZP
PTODI_F207_OdcKl6aZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F207_OdcKl6aZE_ON
PTODI_F208_OdcKl6bZE_IZP | DIGITAL | IOD_PTO | PTO:.DI_F208_OdcKl6bZE_IZP
PTODI_F208_OdcKl6bZE_ON | DIGITAL | IOD_PTO | PTO:.DI_F208_OdcKl6bZE_ON
PTODI_IzpadMreze | DIGITAL | IOD_PTO | PTO:.DI_IzpadMreze
PTODI_Klima1_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima1_ERR
PTODI_Klima1_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima1_ON
PTODI_Klima2_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima2_ERR
PTODI_Klima2_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima2_ON
PTODI_Klima3_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima3_ERR
PTODI_Klima3_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima3_ON
PTODI_Klima4_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima4_ERR
PTODI_Klima4_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima4_ON
PTODI_Klima5_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima5_ERR
PTODI_Klima5_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima5_ON
PTODI_Klima6_ERR | DIGITAL | IOD_PTO | PTO:.DI_Klima6_ERR
PTODI_Klima6_ON | DIGITAL | IOD_PTO | PTO:.DI_Klima6_ON
PTODI_KlimaSplitPP_ERR | DIGITAL | IOD_PTO | PTO:.DI_KlimaSplitPP_ERR
PTODI_KlimaSplitPP_ON | DIGITAL | IOD_PTO | PTO:.DI_KlimaSplitPP_ON
PTODI_PrenapA1_OK | DIGITAL | IOD_PTO | PTO:.DI_PrenapA1_OK
PTODI_PrenapA2_OK | DIGITAL | IOD_PTO | PTO:.DI_PrenapA2_OK
PTODI_Q101_OdcKlima1_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q101_OdcKlima1_IZP
PTODI_Q101_OdcKlima1_ON | DIGITAL | IOD_PTO | PTO:.DI_Q101_OdcKlima1_ON
PTODI_Q102_OdcKlima2_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q102_OdcKlima2_IZP
PTODI_Q102_OdcKlima2_ON | DIGITAL | IOD_PTO | PTO:.DI_Q102_OdcKlima2_ON
PTODI_Q103_OdcKlima3_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q103_OdcKlima3_IZP
PTODI_Q103_OdcKlima3_ON | DIGITAL | IOD_PTO | PTO:.DI_Q103_OdcKlima3_ON
PTODI_Q104_OdcKlima4_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q104_OdcKlima4_IZP
PTODI_Q104_OdcKlima4_ON | DIGITAL | IOD_PTO | PTO:.DI_Q104_OdcKlima4_ON
PTODI_Q105_OdcKlima5_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q105_OdcKlima5_IZP
PTODI_Q105_OdcKlima5_ON | DIGITAL | IOD_PTO | PTO:.DI_Q105_OdcKlima5_ON
PTODI_Q106_OdcKlima6_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q106_OdcKlima6_IZP
PTODI_Q106_OdcKlima6_ON | DIGITAL | IOD_PTO | PTO:.DI_Q106_OdcKlima6_ON
PTODI_Q107_OdcUsmSS2_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q107_OdcUsmSS2_IZP
PTODI_Q107_OdcUsmSS2_ON | DIGITAL | IOD_PTO | PTO:.DI_Q107_OdcUsmSS2_ON
PTODI_Q108_OdcUsmSS3_IZP | DIGITAL | IOD_PTO | PTO:.DI_Q108_OdcUsmSS3_IZP
PTODI_Q108_OdcUsmSS3_ON | DIGITAL | IOD_PTO | PTO:.DI_Q108_OdcUsmSS3_ON
PTODI_RazlitjeVodeK1K2 | DIGITAL | IOD_PTO | PTO:.DI_RazlitjeVodeK1K2
PTODI_RazlitjeVodeK3K4 | DIGITAL | IOD_PTO | PTO:.DI_RazlitjeVodeK3K4
PTODI_RazlitjeVodeK5 | DIGITAL | IOD_PTO | PTO:.DI_RazlitjeVodeK5
PTODI_RazlitjeVodeK6 | DIGITAL | IOD_PTO | PTO:.DI_RazlitjeVodeK6
PTODI_UPS_Alarm | DIGITAL | IOD_PTO | PTO:.DI_UPS_Alarm
PTODI_UPS_BatNacin | DIGITAL | IOD_PTO | PTO:.DI_UPS_BatNacin
PTODI_UPS_Polnjenje | DIGITAL | IOD_PTO | PTO:.DI_UPS_Polnjenje
PTODI_UpsA_BypassON | DIGITAL | IOD_PTO | PTO:.DI_UpsA_BypassON
PTODI_UpsA_ERR | DIGITAL | IOD_PTO | PTO:.DI_UpsA_ERR
PTODI_UpsB_BypassON | DIGITAL | IOD_PTO | PTO:.DI_UpsB_BypassON
PTODI_UpsB_ERR | DIGITAL | IOD_PTO | PTO:.DI_UpsB_ERR
PTODI_UQ11_OdcPMM_IZP | DIGITAL | IOD_PTO | PTO:.DI_UQ11_OdcPMM_IZP
PTODI_UQ11_OdcPMM_ON | DIGITAL | IOD_PTO | PTO:.DI_UQ11_OdcPMM_ON
PTODI_UQ12_OdcPMM_IZP | DIGITAL | IOD_PTO | PTO:.DI_UQ12_OdcPMM_IZP
PTODI_UQ12_OdcPMM_ON | DIGITAL | IOD_PTO | PTO:.DI_UQ12_OdcPMM_ON
PTODIN_A1Q11_OdcUpsA_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q11_OdcUpsA_IZP
PTODIN_A1Q12_OdcByUpsA_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q12_OdcByUpsA_IZP
PTODIN_A1Q13_OdcByA_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q13_OdcByA_IZP
PTODIN_F201_OdcKl1ZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F201_OdcKl1ZE_IZP
PTODIN_F202_OdcKl2ZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F202_OdcKl2ZE_IZP
PTODIN_F203_OdcKl3ZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F203_OdcKl3ZE_IZP
PTODIN_F204_OdcKl4ZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F204_OdcKl4ZE_IZP
PTODIN_F205_OdcKl5aZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F205_OdcKl5aZE_IZP
PTODIN_F206_OdcKl5bZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F206_OdcKl5bZE_IZP
PTODIN_F207_OdcKl6aZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F207_OdcKl6aZE_IZP
PTODIN_F208_OdcKl6bZE_IZP | DIGITAL | IOD_PTO | PTO:.DIN_F208_OdcKl6bZE_IZP
PTODIN_Klima1_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima1_ERR
PTODIN_Klima2_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima2_ERR
PTODIN_Klima3_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima3_ERR
PTODIN_Klima4_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima4_ERR
PTODIN_Klima5_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima5_ERR
PTODIN_Klima6_ERR | DIGITAL | IOD_PTO | PTO:.DIN_Klima6_ERR
PTODIN_KlimaSplitPP_ERR | DIGITAL | IOD_PTO | PTO:.DIN_KlimaSplitPP_ERR
PTODIN_PrenapA1_OK | DIGITAL | IOD_PTO | PTO:.DIN_PrenapA1_OK
PTODIN_PrenapA2_OK | DIGITAL | IOD_PTO | PTO:.DIN_PrenapA2_OK
PTODIN_Q101_OdcKlima1_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q101_OdcKlima1_IZP
PTODIN_Q102_OdcKlima2_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q102_OdcKlima2_IZP
PTODIN_Q103_OdcKlima3_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q103_OdcKlima3_IZP
PTODIN_Q104_OdcKlima4_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q104_OdcKlima4_IZP
PTODIN_Q105_OdcKlima5_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q105_OdcKlima5_IZP
PTODIN_Q106_OdcKlima6_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q106_OdcKlima6_IZP
PTODIN_Q107_OdcUsmSS2_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q107_OdcUsmSS2_IZP
PTODIN_Q108_OdcUsmSS3_IZP | DIGITAL | IOD_PTO | PTO:.DIN_Q108_OdcUsmSS3_IZP
PTODIN_UpsA_BypassON | DIGITAL | IOD_PTO | PTO:.DIN_UpsA_BypassON
PTODIN_UpsA_ERR | DIGITAL | IOD_PTO | PTO:.DIN_UpsA_ERR
PTODIN_UpsB_BypassON | DIGITAL | IOD_PTO | PTO:.DIN_UpsB_BypassON
PTODIN_UpsB_ERR | DIGITAL | IOD_PTO | PTO:.DIN_UpsB_ERR
PTODIN_UQ11_OdcPMM_IZP | DIGITAL | IOD_PTO | PTO:.DIN_UQ11_OdcPMM_IZP
PTODIN_UQ12_OdcPMM_IZP | DIGITAL | IOD_PTO | PTO:.DIN_UQ12_OdcPMM_IZP
PTODO_Klima1_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima1_Izklop
PTODO_Klima2_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima2_Izklop
PTODO_Klima3_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima3_Izklop
PTODO_Klima4_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima4_Izklop
PTODO_Klima5_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima5_Izklop
PTODO_Klima6_Izklop | DIGITAL | IOD_PTO | PTO:.DO_Klima6_Izklop
PTOErrComKlima1 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[1]
PTOErrComKlima2 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[2]
PTOErrComKlima3 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[3]
PTOErrComKlima4 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[4]
PTOErrComKlima5 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[5]
PTOErrComKlima6 | DIGITAL | IOD_PTO | PTO:.ErrComKlima[6]
PTOErrCommScada | DIGITAL | IOD_PTO | PTO:.ErrCommScada
PTOErrComPanelPLC | DIGITAL | IOD_PTO | PTO:.ErrComPanelPLC
PTOErrComPMM | DIGITAL | IOD_PTO | PTO:.ErrComPMM
PTOErrComPort2 | DIGITAL | IOD_PTO | PTO:.ErrComPort2
PTOErrComPort3 | DIGITAL | IOD_PTO | PTO:.ErrComPort3
PTOErrComPort4 | DIGITAL | IOD_PTO | PTO:.ErrComPort4
PTOErrComUPS1 | DIGITAL | IOD_PTO | PTO:.ErrComUPS[1]
PTOErrComUPS2 | DIGITAL | IOD_PTO | PTO:.ErrComUPS[2]
PTOErrorComKlima1Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[1].Error
PTOErrorComKlima2Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[2].Error
PTOErrorComKlima3Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[3].Error
PTOErrorComKlima4Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[4].Error
PTOErrorComKlima5Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[5].Error
PTOErrorComKlima6Error | DIGITAL | IOD_PTO | PTO:.ErrorComKlima[6].Error
PTOErrorComPMMError | DIGITAL | IOD_PTO | PTO:.ErrorComPMM.Error
PTOErrorComUPS1Error | DIGITAL | IOD_PTO | PTO:.ErrorComUPS[1].Error
PTOErrorComUPS2Error | DIGITAL | IOD_PTO | PTO:.ErrorComUPS[2].Error
PTOKlima1Errors10 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[10]
PTOKlima1Errors11 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[11]
PTOKlima1Errors12 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[12]
PTOKlima1Errors13 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[13]
PTOKlima1Errors14 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[14]
PTOKlima1Errors15 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[15]
PTOKlima1Errors16 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[16]
PTOKlima1Errors17 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[17]
PTOKlima1Errors18 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[18]
PTOKlima1Errors19 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[19]
PTOKlima1Errors1 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[1]
PTOKlima1Errors20 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[20]
PTOKlima1Errors21 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[21]
PTOKlima1Errors22 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[22]
PTOKlima1Errors23 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[23]
PTOKlima1Errors24 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[24]
PTOKlima1Errors25 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[25]
PTOKlima1Errors26 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[26]
PTOKlima1Errors27 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[27]
PTOKlima1Errors28 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[28]
PTOKlima1Errors29 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[29]
PTOKlima1Errors2 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[2]
PTOKlima1Errors30 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[30]
PTOKlima1Errors31 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[31]
PTOKlima1Errors32 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[32]
PTOKlima1Errors33 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[33]
PTOKlima1Errors34 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[34]
PTOKlima1Errors35 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[35]
PTOKlima1Errors3 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[3]
PTOKlima1Errors4 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[4]
PTOKlima1Errors5 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[5]
PTOKlima1Errors6 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[6]
PTOKlima1Errors7 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[7]
PTOKlima1Errors8 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[8]
PTOKlima1Errors9 | DIGITAL | IOD_PTO | PTO:.Klima1Errors[9]
PTOKlima2Errors10 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[10]
PTOKlima2Errors11 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[11]
PTOKlima2Errors12 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[12]
PTOKlima2Errors13 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[13]
PTOKlima2Errors14 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[14]
PTOKlima2Errors15 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[15]
PTOKlima2Errors16 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[16]
PTOKlima2Errors17 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[17]
PTOKlima2Errors18 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[18]
PTOKlima2Errors19 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[19]
PTOKlima2Errors1 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[1]
PTOKlima2Errors20 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[20]
PTOKlima2Errors21 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[21]
PTOKlima2Errors22 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[22]
PTOKlima2Errors23 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[23]
PTOKlima2Errors24 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[24]
PTOKlima2Errors25 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[25]
PTOKlima2Errors26 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[26]
PTOKlima2Errors27 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[27]
PTOKlima2Errors28 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[28]
PTOKlima2Errors29 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[29]
PTOKlima2Errors2 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[2]
PTOKlima2Errors30 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[30]
PTOKlima2Errors31 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[31]
PTOKlima2Errors32 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[32]
PTOKlima2Errors33 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[33]
PTOKlima2Errors34 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[34]
PTOKlima2Errors35 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[35]
PTOKlima2Errors3 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[3]
PTOKlima2Errors4 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[4]
PTOKlima2Errors5 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[5]
PTOKlima2Errors6 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[6]
PTOKlima2Errors7 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[7]
PTOKlima2Errors8 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[8]
PTOKlima2Errors9 | DIGITAL | IOD_PTO | PTO:.Klima2Errors[9]
PTOKlima3Errors10 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[10]
PTOKlima3Errors11 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[11]
PTOKlima3Errors12 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[12]
PTOKlima3Errors13 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[13]
PTOKlima3Errors14 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[14]
PTOKlima3Errors15 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[15]
PTOKlima3Errors16 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[16]
PTOKlima3Errors17 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[17]
PTOKlima3Errors18 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[18]
PTOKlima3Errors19 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[19]
PTOKlima3Errors1 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[1]
PTOKlima3Errors20 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[20]
PTOKlima3Errors21 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[21]
PTOKlima3Errors22 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[22]
PTOKlima3Errors23 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[23]
PTOKlima3Errors24 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[24]
PTOKlima3Errors25 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[25]
PTOKlima3Errors26 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[26]
PTOKlima3Errors27 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[27]
PTOKlima3Errors28 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[28]
PTOKlima3Errors29 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[29]
PTOKlima3Errors2 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[2]
PTOKlima3Errors30 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[30]
PTOKlima3Errors31 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[31]
PTOKlima3Errors32 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[32]
PTOKlima3Errors33 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[33]
PTOKlima3Errors34 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[34]
PTOKlima3Errors35 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[35]
PTOKlima3Errors3 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[3]
PTOKlima3Errors4 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[4]
PTOKlima3Errors5 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[5]
PTOKlima3Errors6 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[6]
PTOKlima3Errors7 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[7]
PTOKlima3Errors8 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[8]
PTOKlima3Errors9 | DIGITAL | IOD_PTO | PTO:.Klima3Errors[9]
PTOKlima4Errors10 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[10]
PTOKlima4Errors11 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[11]
PTOKlima4Errors12 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[12]
PTOKlima4Errors13 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[13]
PTOKlima4Errors14 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[14]
PTOKlima4Errors15 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[15]
PTOKlima4Errors16 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[16]
PTOKlima4Errors17 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[17]
PTOKlima4Errors18 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[18]
PTOKlima4Errors19 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[19]
PTOKlima4Errors1 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[1]
PTOKlima4Errors20 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[20]
PTOKlima4Errors21 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[21]
PTOKlima4Errors22 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[22]
PTOKlima4Errors23 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[23]
PTOKlima4Errors24 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[24]
PTOKlima4Errors25 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[25]
PTOKlima4Errors26 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[26]
PTOKlima4Errors27 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[27]
PTOKlima4Errors28 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[28]
PTOKlima4Errors29 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[29]
PTOKlima4Errors2 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[2]
PTOKlima4Errors30 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[30]
PTOKlima4Errors31 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[31]
PTOKlima4Errors32 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[32]
PTOKlima4Errors33 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[33]
PTOKlima4Errors34 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[34]
PTOKlima4Errors35 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[35]
PTOKlima4Errors3 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[3]
PTOKlima4Errors4 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[4]
PTOKlima4Errors5 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[5]
PTOKlima4Errors6 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[6]
PTOKlima4Errors7 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[7]
PTOKlima4Errors8 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[8]
PTOKlima4Errors9 | DIGITAL | IOD_PTO | PTO:.Klima4Errors[9]
PTOKlima5Errors10 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[10]
PTOKlima5Errors11 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[11]
PTOKlima5Errors12 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[12]
PTOKlima5Errors13 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[13]
PTOKlima5Errors14 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[14]
PTOKlima5Errors15 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[15]
PTOKlima5Errors16 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[16]
PTOKlima5Errors17 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[17]
PTOKlima5Errors18 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[18]
PTOKlima5Errors19 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[19]
PTOKlima5Errors1 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[1]
PTOKlima5Errors20 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[20]
PTOKlima5Errors21 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[21]
PTOKlima5Errors22 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[22]
PTOKlima5Errors23 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[23]
PTOKlima5Errors24 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[24]
PTOKlima5Errors25 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[25]
PTOKlima5Errors26 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[26]
PTOKlima5Errors27 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[27]
PTOKlima5Errors28 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[28]
PTOKlima5Errors29 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[29]
PTOKlima5Errors2 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[2]
PTOKlima5Errors30 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[30]
PTOKlima5Errors31 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[31]
PTOKlima5Errors32 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[32]
PTOKlima5Errors33 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[33]
PTOKlima5Errors34 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[34]
PTOKlima5Errors35 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[35]
PTOKlima5Errors3 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[3]
PTOKlima5Errors4 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[4]
PTOKlima5Errors5 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[5]
PTOKlima5Errors6 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[6]
PTOKlima5Errors7 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[7]
PTOKlima5Errors8 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[8]
PTOKlima5Errors9 | DIGITAL | IOD_PTO | PTO:.Klima5Errors[9]
PTOKlima6Errors10 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[10]
PTOKlima6Errors11 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[11]
PTOKlima6Errors12 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[12]
PTOKlima6Errors13 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[13]
PTOKlima6Errors14 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[14]
PTOKlima6Errors15 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[15]
PTOKlima6Errors16 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[16]
PTOKlima6Errors17 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[17]
PTOKlima6Errors18 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[18]
PTOKlima6Errors19 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[19]
PTOKlima6Errors1 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[1]
PTOKlima6Errors20 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[20]
PTOKlima6Errors21 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[21]
PTOKlima6Errors22 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[22]
PTOKlima6Errors23 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[23]
PTOKlima6Errors24 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[24]
PTOKlima6Errors25 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[25]
PTOKlima6Errors26 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[26]
PTOKlima6Errors27 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[27]
PTOKlima6Errors28 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[28]
PTOKlima6Errors29 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[29]
PTOKlima6Errors2 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[2]
PTOKlima6Errors30 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[30]
PTOKlima6Errors31 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[31]
PTOKlima6Errors32 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[32]
PTOKlima6Errors33 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[33]
PTOKlima6Errors34 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[34]
PTOKlima6Errors35 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[35]
PTOKlima6Errors3 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[3]
PTOKlima6Errors4 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[4]
PTOKlima6Errors5 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[5]
PTOKlima6Errors6 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[6]
PTOKlima6Errors7 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[7]
PTOKlima6Errors8 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[8]
PTOKlima6Errors9 | DIGITAL | IOD_PTO | PTO:.Klima6Errors[9]
PTOKlima1Deluje | DIGITAL | IOD_PTO | PTO:.Klima[1].Deluje
PTOKlima1FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[1].FenThermalCutout
PTOKlima1GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].GeneralAlarm
PTOKlima1Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Kompresor1naMejiObrUr
PTOKlima1Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Kompresor2naMejiObrUr
PTOKlima1Napaka | DIGITAL | IOD_PTO | PTO:.Klima[1].Napaka
PTOKlima1NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaPriPretokuZraka
PTOKlima1NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorTempIzpiha
PTOKlima1NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorTempProstora
PTOKlima1NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorVlaznosti
PTOKlima1NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorZunanjeTemp
PTOKlima1NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[1].NiTokaVVlazilcu
PTOKlima1NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[1].NiVodeVVlazilcu
PTOKlima1NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[1].NizekPritiskKompresor1
PTOKlima1NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[1].NizekPritiskKompresor2
PTOKlima1NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[1].NizkaTempVProstoru
PTOKlima1NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[1].NizkaVlaznost
PTOKlima1OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[1].OnOffEnablingBySupervisor
PTOKlima1PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].PozarniAlarm
PTOKlima1Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[1].Razvlazevanje
PTOKlima1RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[1].RemoteOFFtoOutput
PTOKlima1RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[1].RocniIzklop
PTOKlima1SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[1].SenzorjiStatus
PTOKlima1UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[1].UnitOnOff
PTOKlima1VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[1].VisokaTempVProstoru
PTOKlima1VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[1].VisokaVlaznost
PTOKlima1VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[1].VisokTokVVlazilcu
PTOKlima1Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[1].Vlazenje
PTOKlima1ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[1].ZamasenFilter
PTOKlima2Deluje | DIGITAL | IOD_PTO | PTO:.Klima[2].Deluje
PTOKlima2FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[2].FenThermalCutout
PTOKlima2GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].GeneralAlarm
PTOKlima2Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Kompresor1naMejiObrUr
PTOKlima2Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Kompresor2naMejiObrUr
PTOKlima2Napaka | DIGITAL | IOD_PTO | PTO:.Klima[2].Napaka
PTOKlima2NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaPriPretokuZraka
PTOKlima2NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorTempIzpiha
PTOKlima2NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorTempProstora
PTOKlima2NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorVlaznosti
PTOKlima2NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorZunanjeTemp
PTOKlima2NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[2].NiTokaVVlazilcu
PTOKlima2NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[2].NiVodeVVlazilcu
PTOKlima2NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[2].NizekPritiskKompresor1
PTOKlima2NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[2].NizekPritiskKompresor2
PTOKlima2NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[2].NizkaTempVProstoru
PTOKlima2NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[2].NizkaVlaznost
PTOKlima2OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[2].OnOffEnablingBySupervisor
PTOKlima2PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].PozarniAlarm
PTOKlima2Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[2].Razvlazevanje
PTOKlima2RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[2].RemoteOFFtoOutput
PTOKlima2RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[2].RocniIzklop
PTOKlima2SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[2].SenzorjiStatus
PTOKlima2UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[2].UnitOnOff
PTOKlima2VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[2].VisokaTempVProstoru
PTOKlima2VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[2].VisokaVlaznost
PTOKlima2VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[2].VisokTokVVlazilcu
PTOKlima2Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[2].Vlazenje
PTOKlima2ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[2].ZamasenFilter
PTOKlima3Deluje | DIGITAL | IOD_PTO | PTO:.Klima[3].Deluje
PTOKlima3FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[3].FenThermalCutout
PTOKlima3GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].GeneralAlarm
PTOKlima3Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Kompresor1naMejiObrUr
PTOKlima3Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Kompresor2naMejiObrUr
PTOKlima3Napaka | DIGITAL | IOD_PTO | PTO:.Klima[3].Napaka
PTOKlima3NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaPriPretokuZraka
PTOKlima3NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorTempIzpiha
PTOKlima3NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorTempProstora
PTOKlima3NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorVlaznosti
PTOKlima3NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorZunanjeTemp
PTOKlima3NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[3].NiTokaVVlazilcu
PTOKlima3NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[3].NiVodeVVlazilcu
PTOKlima3NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[3].NizekPritiskKompresor1
PTOKlima3NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[3].NizekPritiskKompresor2
PTOKlima3NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[3].NizkaTempVProstoru
PTOKlima3NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[3].NizkaVlaznost
PTOKlima3OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[3].OnOffEnablingBySupervisor
PTOKlima3PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].PozarniAlarm
PTOKlima3Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[3].Razvlazevanje
PTOKlima3RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[3].RemoteOFFtoOutput
PTOKlima3RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[3].RocniIzklop
PTOKlima3SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[3].SenzorjiStatus
PTOKlima3UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[3].UnitOnOff
PTOKlima3VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[3].VisokaTempVProstoru
PTOKlima3VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[3].VisokaVlaznost
PTOKlima3VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[3].VisokTokVVlazilcu
PTOKlima3Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[3].Vlazenje
PTOKlima3ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[3].ZamasenFilter
PTOKlima4Deluje | DIGITAL | IOD_PTO | PTO:.Klima[4].Deluje
PTOKlima4FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[4].FenThermalCutout
PTOKlima4GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].GeneralAlarm
PTOKlima4Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Kompresor1naMejiObrUr
PTOKlima4Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Kompresor2naMejiObrUr
PTOKlima4Napaka | DIGITAL | IOD_PTO | PTO:.Klima[4].Napaka
PTOKlima4NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaPriPretokuZraka
PTOKlima4NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorTempIzpiha
PTOKlima4NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorTempProstora
PTOKlima4NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorVlaznosti
PTOKlima4NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorZunanjeTemp
PTOKlima4NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[4].NiTokaVVlazilcu
PTOKlima4NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[4].NiVodeVVlazilcu
PTOKlima4NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[4].NizekPritiskKompresor1
PTOKlima4NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[4].NizekPritiskKompresor2
PTOKlima4NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[4].NizkaTempVProstoru
PTOKlima4NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[4].NizkaVlaznost
PTOKlima4OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[4].OnOffEnablingBySupervisor
PTOKlima4PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].PozarniAlarm
PTOKlima4Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[4].Razvlazevanje
PTOKlima4RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[4].RemoteOFFtoOutput
PTOKlima4RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[4].RocniIzklop
PTOKlima4SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[4].SenzorjiStatus
PTOKlima4UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[4].UnitOnOff
PTOKlima4VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[4].VisokaTempVProstoru
PTOKlima4VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[4].VisokaVlaznost
PTOKlima4VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[4].VisokTokVVlazilcu
PTOKlima4Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[4].Vlazenje
PTOKlima4ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[4].ZamasenFilter
PTOKlima5Deluje | DIGITAL | IOD_PTO | PTO:.Klima[5].Deluje
PTOKlima5FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[5].FenThermalCutout
PTOKlima5GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].GeneralAlarm
PTOKlima5Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Kompresor1naMejiObrUr
PTOKlima5Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Kompresor2naMejiObrUr
PTOKlima5Napaka | DIGITAL | IOD_PTO | PTO:.Klima[5].Napaka
PTOKlima5NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaPriPretokuZraka
PTOKlima5NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorTempIzpiha
PTOKlima5NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorTempProstora
PTOKlima5NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorVlaznosti
PTOKlima5NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorZunanjeTemp
PTOKlima5NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[5].NiTokaVVlazilcu
PTOKlima5NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[5].NiVodeVVlazilcu
PTOKlima5NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[5].NizekPritiskKompresor1
PTOKlima5NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[5].NizekPritiskKompresor2
PTOKlima5NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[5].NizkaTempVProstoru
PTOKlima5NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[5].NizkaVlaznost
PTOKlima5OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[5].OnOffEnablingBySupervisor
PTOKlima5PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].PozarniAlarm
PTOKlima5Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[5].Razvlazevanje
PTOKlima5RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[5].RemoteOFFtoOutput
PTOKlima5RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[5].RocniIzklop
PTOKlima5SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[5].SenzorjiStatus
PTOKlima5UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[5].UnitOnOff
PTOKlima5VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[5].VisokaTempVProstoru
PTOKlima5VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[5].VisokaVlaznost
PTOKlima5VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[5].VisokTokVVlazilcu
PTOKlima5Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[5].Vlazenje
PTOKlima5ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[5].ZamasenFilter
PTOKlima6Deluje | DIGITAL | IOD_PTO | PTO:.Klima[6].Deluje
PTOKlima6FenThermalCutout | DIGITAL | IOD_PTO | PTO:.Klima[6].FenThermalCutout
PTOKlima6GeneralAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].GeneralAlarm
PTOKlima6Kompresor1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Kompresor1naMejiObrUr
PTOKlima6Kompresor2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Kompresor2naMejiObrUr
PTOKlima6Napaka | DIGITAL | IOD_PTO | PTO:.Klima[6].Napaka
PTOKlima6NapakaPriPretokuZraka | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaPriPretokuZraka
PTOKlima6NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorTempIzpiha
PTOKlima6NapakaSenzorTempProstora | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorTempProstora
PTOKlima6NapakaSenzorVlaznosti | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorVlaznosti
PTOKlima6NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorZunanjeTemp
PTOKlima6NiTokaVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[6].NiTokaVVlazilcu
PTOKlima6NiVodeVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[6].NiVodeVVlazilcu
PTOKlima6NizekPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[6].NizekPritiskKompresor1
PTOKlima6NizekPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[6].NizekPritiskKompresor2
PTOKlima6NizkaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[6].NizkaTempVProstoru
PTOKlima6NizkaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[6].NizkaVlaznost
PTOKlima6OnOffEnablingBySupervisor | DIGITAL | IOD_PTO | PTO:.Klima[6].OnOffEnablingBySupervisor
PTOKlima6PozarniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].PozarniAlarm
PTOKlima6Razvlazevanje | DIGITAL | IOD_PTO | PTO:.Klima[6].Razvlazevanje
PTOKlima6RemoteOFFtoOutput | DIGITAL | IOD_PTO | PTO:.Klima[6].RemoteOFFtoOutput
PTOKlima6RocniIzklop | DIGITAL | IOD_PTO | PTO:.Klima[6].RocniIzklop
PTOKlima6SenzorjiStatus | DIGITAL | IOD_PTO | PTO:.Klima[6].SenzorjiStatus
PTOKlima6UnitOnOff | DIGITAL | IOD_PTO | PTO:.Klima[6].UnitOnOff
PTOKlima6VisokaTempVProstoru | DIGITAL | IOD_PTO | PTO:.Klima[6].VisokaTempVProstoru
PTOKlima6VisokaVlaznost | DIGITAL | IOD_PTO | PTO:.Klima[6].VisokaVlaznost
PTOKlima6VisokTokVVlazilcu | DIGITAL | IOD_PTO | PTO:.Klima[6].VisokTokVVlazilcu
PTOKlima6Vlazenje | DIGITAL | IOD_PTO | PTO:.Klima[6].Vlazenje
PTOKlima6ZamasenFilter | DIGITAL | IOD_PTO | PTO:.Klima[6].ZamasenFilter
PTOKlimeNaCas0 | DIGITAL | IOD_PTO | PTO:.KlimeNaCas[0]
PTOKlimeNaCas1 | DIGITAL | IOD_PTO | PTO:.KlimeNaCas[1]
PTOKlimeNaCas2 | DIGITAL | IOD_PTO | PTO:.KlimeNaCas[2]
PTOKlimeNaCas3 | DIGITAL | IOD_PTO | PTO:.KlimeNaCas[3]
PTOMrezaIzpad | DIGITAL | IOD_PTO | PTO:.MrezaIzpad
PTOMrezaIzpadKlimaOff1 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[1]
PTOMrezaIzpadKlimaOff2 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[2]
PTOMrezaIzpadKlimaOff3 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[3]
PTOMrezaIzpadKlimaOff4 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[4]
PTOMrezaIzpadKlimaOff5 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[5]
PTOMrezaIzpadKlimaOff6 | DIGITAL | IOD_PTO | PTO:.MrezaIzpadKlimaOff[6]
PTONapakaSenzorTemp1 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[1]
PTONapakaSenzorTemp2 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[2]
PTONapakaSenzorTemp3 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[3]
PTONapakaSenzorTemp4 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[4]
PTONapakaSenzorTemp5 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[5]
PTONapakaSenzorTemp6 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorTemp[6]
PTONapakaSenzorVlaga1 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[1]
PTONapakaSenzorVlaga2 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[2]
PTONapakaSenzorVlaga3 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[3]
PTONapakaSenzorVlaga4 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[4]
PTONapakaSenzorVlaga5 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[5]
PTONapakaSenzorVlaga6 | DIGITAL | IOD_PTO | PTO:.NapakaSenzorVlaga[6]
PTOPMMNapaka | DIGITAL | IOD_PTO | PTO:.PMM.Napaka
PTOPMMOverCurrentBetw1 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentBetw[1]
PTOPMMOverCurrentBetw2 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentBetw[2]
PTOPMMOverCurrentBetw3 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentBetw[3]
PTOPMMOverCurrentOver1 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentOver[1]
PTOPMMOverCurrentOver2 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentOver[2]
PTOPMMOverCurrentOver3 | DIGITAL | IOD_PTO | PTO:.PMMOverCurrentOver[3]
PTOSetDateTime | DIGITAL | IOD_PTO | PTO:.SetDateTime
PTOSetDateTimeDemand | DIGITAL | IOD_PTO | PTO:.SetDateTimeDemand
PTOSetDateTimeError | DIGITAL | IOD_PTO | PTO:.SetDateTimeError
PTOSetDateTimeFinished | DIGITAL | IOD_PTO | PTO:.SetDateTimeFinished
PTOSetRemoteOnOff1 | DIGITAL | IOD_PTO | PTO:.SetRemoteOnOff[1]
PTOSetRemoteOnOff2 | DIGITAL | IOD_PTO | PTO:.SetRemoteOnOff[2]
PTOSlabaBaterijaPLC_A1 | DIGITAL | IOD_PTO | PTO:.SlabaBaterijaPLC_A1
PTOTempTSprevisoka1 | DIGITAL | IOD_PTO | PTO:.TempTSprevisoka[1]
PTOTempTSprevisoka2 | DIGITAL | IOD_PTO | PTO:.TempTSprevisoka[2]
PTOTempTSprevisoka3 | DIGITAL | IOD_PTO | PTO:.TempTSprevisoka[3]
PTOTempTSprevisokaSum | DIGITAL | IOD_PTO | PTO:.TempTSprevisokaSum
PTOUPS1Errors10 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[10]
PTOUPS1Errors11 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[11]
PTOUPS1Errors12 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[12]
PTOUPS1Errors13 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[13]
PTOUPS1Errors14 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[14]
PTOUPS1Errors15 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[15]
PTOUPS1Errors16 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[16]
PTOUPS1Errors17 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[17]
PTOUPS1Errors18 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[18]
PTOUPS1Errors19 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[19]
PTOUPS1Errors1 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[1]
PTOUPS1Errors20 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[20]
PTOUPS1Errors21 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[21]
PTOUPS1Errors22 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[22]
PTOUPS1Errors23 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[23]
PTOUPS1Errors24 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[24]
PTOUPS1Errors25 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[25]
PTOUPS1Errors2 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[2]
PTOUPS1Errors3 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[3]
PTOUPS1Errors4 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[4]
PTOUPS1Errors5 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[5]
PTOUPS1Errors6 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[6]
PTOUPS1Errors7 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[7]
PTOUPS1Errors8 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[8]
PTOUPS1Errors9 | DIGITAL | IOD_PTO | PTO:.UPS1Errors[9]
PTOUPS2Errors10 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[10]
PTOUPS2Errors11 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[11]
PTOUPS2Errors12 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[12]
PTOUPS2Errors13 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[13]
PTOUPS2Errors14 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[14]
PTOUPS2Errors15 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[15]
PTOUPS2Errors16 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[16]
PTOUPS2Errors17 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[17]
PTOUPS2Errors18 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[18]
PTOUPS2Errors19 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[19]
PTOUPS2Errors1 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[1]
PTOUPS2Errors20 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[20]
PTOUPS2Errors21 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[21]
PTOUPS2Errors22 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[22]
PTOUPS2Errors23 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[23]
PTOUPS2Errors24 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[24]
PTOUPS2Errors25 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[25]
PTOUPS2Errors2 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[2]
PTOUPS2Errors3 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[3]
PTOUPS2Errors4 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[4]
PTOUPS2Errors5 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[5]
PTOUPS2Errors6 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[6]
PTOUPS2Errors7 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[7]
PTOUPS2Errors8 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[8]
PTOUPS2Errors9 | DIGITAL | IOD_PTO | PTO:.UPS2Errors[9]
PTOUPS1AlarmAwaitingPower | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmAwaitingPower
PTOUPS1AlarmBypassBad | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmBypassBad
PTOUPS1AlarmChargerFailed | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmChargerFailed
PTOUPS1AlarmCommunicationsLost | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmCommunicationsLost
PTOUPS1AlarmDepletedBattery | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmDepletedBattery
PTOUPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmDiagnosticTestFailed
PTOUPS1AlarmInverterError | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmInverterError
PTOUPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmIzhodOffKotZahtevano
PTOUPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmIzhodPreobremenjen
PTOUPS1AlarmLowBattery | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmLowBattery
PTOUPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmNapakaNaVarovalki
PTOUPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmNapakaNaVentilatorju
PTOUPS1AlarmOnBattery | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmOnBattery
PTOUPS1AlarmOnBypass | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmOnBypass
PTOUPS1AlarmShutdownImminent | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmShutdownImminent
PTOUPS1AlarmShutdownPending | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmShutdownPending
PTOUPS1AlarmSlabaBaterija | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmSlabaBaterija
PTOUPS1AlarmSplosnaNapaka | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmSplosnaNapaka
PTOUPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmStanjeIzhodaIzvenToleranc
PTOUPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmStanjeVhodaIzvenToleranc
PTOUPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmTemperaturaIzvenToleranc
PTOUPS1AlarmTestInProgres | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmTestInProgres
PTOUPS1AlarmUPSIzhodOff | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmUPSIzhodOff
PTOUPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmUPSOffKotZahtevano
PTOUPS1AlarmUPSSystemOff | DIGITAL | IOD_PTO | PTO:.UPS[1].AlarmUPSSystemOff
PTOUPS1Napaka | DIGITAL | IOD_PTO | PTO:.UPS[1].Napaka
PTOUPS1StatusEcomodeAktiven | DIGITAL | IOD_PTO | PTO:.UPS[1].StatusEcomodeAktiven
PTOUPS1StatusInverterIsOn | DIGITAL | IOD_PTO | PTO:.UPS[1].StatusInverterIsOn
PTOUPS1StatusStopOperation | DIGITAL | IOD_PTO | PTO:.UPS[1].StatusStopOperation
PTOUPS2AlarmAwaitingPower | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmAwaitingPower
PTOUPS2AlarmBypassBad | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmBypassBad
PTOUPS2AlarmChargerFailed | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmChargerFailed
PTOUPS2AlarmCommunicationsLost | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmCommunicationsLost
PTOUPS2AlarmDepletedBattery | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmDepletedBattery
PTOUPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmDiagnosticTestFailed
PTOUPS2AlarmInverterError | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmInverterError
PTOUPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmIzhodOffKotZahtevano
PTOUPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmIzhodPreobremenjen
PTOUPS2AlarmLowBattery | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmLowBattery
PTOUPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmNapakaNaVarovalki
PTOUPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmNapakaNaVentilatorju
PTOUPS2AlarmOnBattery | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmOnBattery
PTOUPS2AlarmOnBypass | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmOnBypass
PTOUPS2AlarmShutdownImminent | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmShutdownImminent
PTOUPS2AlarmShutdownPending | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmShutdownPending
PTOUPS2AlarmSlabaBaterija | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmSlabaBaterija
PTOUPS2AlarmSplosnaNapaka | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmSplosnaNapaka
PTOUPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmStanjeIzhodaIzvenToleranc
PTOUPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmStanjeVhodaIzvenToleranc
PTOUPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmTemperaturaIzvenToleranc
PTOUPS2AlarmTestInProgres | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmTestInProgres
PTOUPS2AlarmUPSIzhodOff | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmUPSIzhodOff
PTOUPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmUPSOffKotZahtevano
PTOUPS2AlarmUPSSystemOff | DIGITAL | IOD_PTO | PTO:.UPS[2].AlarmUPSSystemOff
PTOUPS2Napaka | DIGITAL | IOD_PTO | PTO:.UPS[2].Napaka
PTOUPS2StatusEcomodeAktiven | DIGITAL | IOD_PTO | PTO:.UPS[2].StatusEcomodeAktiven
PTOUPS2StatusInverterIsOn | DIGITAL | IOD_PTO | PTO:.UPS[2].StatusInverterIsOn
PTOUPS2StatusStopOperation | DIGITAL | IOD_PTO | PTO:.UPS[2].StatusStopOperation
PTOUserLoggedIn | DIGITAL | IOD_PTO | PTO:.UserLoggedIn
PTODIN_A1Q11_OdcUpsB_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q11_OdcUpsB_IZP
PTODIN_A1Q12_OdcByUpsB_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q12_OdcByUpsB_IZP
PTODIN_A1Q13_OdcByB_IZP | DIGITAL | IOD_PTO | PTO:.DIN_A1Q13_OdcByB_IZP
PTODIN_UQ11_OdcPMMB_IZP | DIGITAL | IOD_PTO | PTO:.DIN_UQ11_OdcPMMB_IZP
PTODIN_UQ12_OdcPMMB_IZP | DIGITAL | IOD_PTO | PTO:.DIN_UQ12_OdcPMMB_IZP
PTODIN_PrenapA3_OK | DIGITAL | IOD_PTO | PTO:.DIN_PrenapA3_OK
PTODIN_A1Q0_GlavnoStiB_ON | DIGITAL | IOD_PTO | PTO:.DIN_A1Q0_GlavnoStiB_ON
PTODIN_A1Q11_OdcUpsB_ON | DIGITAL | IOD_PTO | PTO:.DIN_A1Q11_OdcUpsB_ON
PTODIN_A1Q12_OdcByUpsB_ON | DIGITAL | IOD_PTO | PTO:.DIN_A1Q12_OdcByUpsB_ON
PTODI_A1Q13_OdcByB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q13_OdcByB_ON
PTODIN_A1Q01_DovUpsB_ON | DIGITAL | IOD_PTO | PTO:.DIN_A1Q01_DovUpsB_ON
PTODI_A1Q02_DovByB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q02_DovByB_ON
PTODIN_UQ11_OdcPMMB_ON | DIGITAL | IOD_PTO | PTO:.DIN_UQ11_OdcPMMB_ON
PTODI_UQ12_OdcPMMB_ON | DIGITAL | IOD_PTO | PTO:.DI_UQ12_OdcPMMB_ON
PTOKlima1NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].NapacnoGesloAlarm
PTOKlima1ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].ExtTempHumAlarm
PTOKlima1PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].PoplavniAlarm
PTOKlima1VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[1].VisokPritiskKompresor1
PTOKlima1VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[1].VisokPritiskKompresor2
PTOKlima1ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[1].ElVentilKompresor1ERR
PTOKlima1ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[1].ElVentilKompresor2ERR
PTOKlima1WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].WrongPhaseSeqAlarm
PTOKlima1PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[1].PrekinjenLANalarm
PTOKlima1CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[1].CWTempHighForDehum
PTOKlima1CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[1].CWVentilErrOrLowFlow
PTOKlima1NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaPriPretokuVode
PTOKlima1CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[1].CWhighTemp
PTOKlima1NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorHotWTemp
PTOKlima1NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorCondWTemp
PTOKlima1NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[1].NapakaSenzorCW
PTOKlima1Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Kompresor3naMejiObrUr
PTOKlima1Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Kompresor4naMejiObrUr
PTOKlima1ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].ZracniFilterNaMejiObrUr
PTOKlima1Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Grelec1naMejiObrUr
PTOKlima1Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].Grelec2naMejiObrUr
PTOKlima1VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].VlazilecNaMejiObrUr
PTOKlima1AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[1].AirCondUnitNaMejiObrUr
PTOKlima1DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[1].DigIn2Alarm
PTOKlima1DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[1].DigIn4Alarm
PTOKlima1DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[1].DigIn6Alarm
PTOKlima1VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].VlazilecGenAlarm
PTOKlima1General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].General2ndLevAlarm
PTOKlima1UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[1].UnitOnRotAlarm
PTOKlima1UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[1].UnitOnAlarmA
PTOKlima1UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[1].UnitOnAlarmB
PTOKlima1UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[1].UnitOnAlarmC
PTOKlima2NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].NapacnoGesloAlarm
PTOKlima2ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].ExtTempHumAlarm
PTOKlima2PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].PoplavniAlarm
PTOKlima2VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[2].VisokPritiskKompresor1
PTOKlima2VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[2].VisokPritiskKompresor2
PTOKlima2ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[2].ElVentilKompresor1ERR
PTOKlima2ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[2].ElVentilKompresor2ERR
PTOKlima2WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].WrongPhaseSeqAlarm
PTOKlima2PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[2].PrekinjenLANalarm
PTOKlima2CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[2].CWTempHighForDehum
PTOKlima2CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[2].CWVentilErrOrLowFlow
PTOKlima2NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaPriPretokuVode
PTOKlima2CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[2].CWhighTemp
PTOKlima2NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorHotWTemp
PTOKlima2NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorCondWTemp
PTOKlima2NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[2].NapakaSenzorCW
PTOKlima2Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Kompresor3naMejiObrUr
PTOKlima2Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Kompresor4naMejiObrUr
PTOKlima2ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].ZracniFilterNaMejiObrUr
PTOKlima2Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Grelec1naMejiObrUr
PTOKlima2Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].Grelec2naMejiObrUr
PTOKlima2VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].VlazilecNaMejiObrUr
PTOKlima2AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[2].AirCondUnitNaMejiObrUr
PTOKlima2DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[2].DigIn2Alarm
PTOKlima2DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[2].DigIn4Alarm
PTOKlima2DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[2].DigIn6Alarm
PTOKlima2VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].VlazilecGenAlarm
PTOKlima2General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].General2ndLevAlarm
PTOKlima2UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[2].UnitOnRotAlarm
PTOKlima2UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[2].UnitOnAlarmA
PTOKlima2UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[2].UnitOnAlarmB
PTOKlima2UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[2].UnitOnAlarmC
PTOKlima3NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].NapacnoGesloAlarm
PTOKlima3ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].ExtTempHumAlarm
PTOKlima3PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].PoplavniAlarm
PTOKlima3VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[3].VisokPritiskKompresor1
PTOKlima3VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[3].VisokPritiskKompresor2
PTOKlima3ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[3].ElVentilKompresor1ERR
PTOKlima3ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[3].ElVentilKompresor2ERR
PTOKlima3WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].WrongPhaseSeqAlarm
PTOKlima3PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[3].PrekinjenLANalarm
PTOKlima3CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[3].CWTempHighForDehum
PTOKlima3CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[3].CWVentilErrOrLowFlow
PTOKlima3NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaPriPretokuVode
PTOKlima3CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[3].CWhighTemp
PTOKlima3NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorHotWTemp
PTOKlima3NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorCondWTemp
PTOKlima3NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[3].NapakaSenzorCW
PTOKlima3Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Kompresor3naMejiObrUr
PTOKlima3Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Kompresor4naMejiObrUr
PTOKlima3ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].ZracniFilterNaMejiObrUr
PTOKlima3Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Grelec1naMejiObrUr
PTOKlima3Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].Grelec2naMejiObrUr
PTOKlima3VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].VlazilecNaMejiObrUr
PTOKlima3AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[3].AirCondUnitNaMejiObrUr
PTOKlima3DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[3].DigIn2Alarm
PTOKlima3DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[3].DigIn4Alarm
PTOKlima3DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[3].DigIn6Alarm
PTOKlima3VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].VlazilecGenAlarm
PTOKlima3General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].General2ndLevAlarm
PTOKlima3UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[3].UnitOnRotAlarm
PTOKlima3UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[3].UnitOnAlarmA
PTOKlima3UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[3].UnitOnAlarmB
PTOKlima3UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[3].UnitOnAlarmC
PTOKlima4NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].NapacnoGesloAlarm
PTOKlima4ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].ExtTempHumAlarm
PTOKlima4PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].PoplavniAlarm
PTOKlima4VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[4].VisokPritiskKompresor1
PTOKlima4VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[4].VisokPritiskKompresor2
PTOKlima4ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[4].ElVentilKompresor1ERR
PTOKlima4ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[4].ElVentilKompresor2ERR
PTOKlima4WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].WrongPhaseSeqAlarm
PTOKlima4PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[4].PrekinjenLANalarm
PTOKlima4CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[4].CWTempHighForDehum
PTOKlima4CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[4].CWVentilErrOrLowFlow
PTOKlima4NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaPriPretokuVode
PTOKlima4CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[4].CWhighTemp
PTOKlima4NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorHotWTemp
PTOKlima4NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorCondWTemp
PTOKlima4NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[4].NapakaSenzorCW
PTOKlima4Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Kompresor3naMejiObrUr
PTOKlima4Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Kompresor4naMejiObrUr
PTOKlima4ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].ZracniFilterNaMejiObrUr
PTOKlima4Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Grelec1naMejiObrUr
PTOKlima4Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].Grelec2naMejiObrUr
PTOKlima4VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].VlazilecNaMejiObrUr
PTOKlima4AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[4].AirCondUnitNaMejiObrUr
PTOKlima4DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[4].DigIn2Alarm
PTOKlima4DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[4].DigIn4Alarm
PTOKlima4DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[4].DigIn6Alarm
PTOKlima4VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].VlazilecGenAlarm
PTOKlima4General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].General2ndLevAlarm
PTOKlima4UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[4].UnitOnRotAlarm
PTOKlima4UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[4].UnitOnAlarmA
PTOKlima4UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[4].UnitOnAlarmB
PTOKlima4UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[4].UnitOnAlarmC
PTOKlima5NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].NapacnoGesloAlarm
PTOKlima5ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].ExtTempHumAlarm
PTOKlima5PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].PoplavniAlarm
PTOKlima5VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[5].VisokPritiskKompresor1
PTOKlima5VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[5].VisokPritiskKompresor2
PTOKlima5ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[5].ElVentilKompresor1ERR
PTOKlima5ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[5].ElVentilKompresor2ERR
PTOKlima5WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].WrongPhaseSeqAlarm
PTOKlima5PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[5].PrekinjenLANalarm
PTOKlima5CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[5].CWTempHighForDehum
PTOKlima5CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[5].CWVentilErrOrLowFlow
PTOKlima5NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaPriPretokuVode
PTOKlima5CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[5].CWhighTemp
PTOKlima5NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorHotWTemp
PTOKlima5NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorCondWTemp
PTOKlima5NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[5].NapakaSenzorCW
PTOKlima5Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Kompresor3naMejiObrUr
PTOKlima5Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Kompresor4naMejiObrUr
PTOKlima5ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].ZracniFilterNaMejiObrUr
PTOKlima5Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Grelec1naMejiObrUr
PTOKlima5Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].Grelec2naMejiObrUr
PTOKlima5VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].VlazilecNaMejiObrUr
PTOKlima5AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[5].AirCondUnitNaMejiObrUr
PTOKlima5DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[5].DigIn2Alarm
PTOKlima5DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[5].DigIn4Alarm
PTOKlima5DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[5].DigIn6Alarm
PTOKlima5VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].VlazilecGenAlarm
PTOKlima5General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].General2ndLevAlarm
PTOKlima5UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[5].UnitOnRotAlarm
PTOKlima5UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[5].UnitOnAlarmA
PTOKlima5UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[5].UnitOnAlarmB
PTOKlima5UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[5].UnitOnAlarmC
PTOKlima6NapacnoGesloAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].NapacnoGesloAlarm
PTOKlima6ExtTempHumAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].ExtTempHumAlarm
PTOKlima6PoplavniAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].PoplavniAlarm
PTOKlima6VisokPritiskKompresor1 | DIGITAL | IOD_PTO | PTO:.Klima[6].VisokPritiskKompresor1
PTOKlima6VisokPritiskKompresor2 | DIGITAL | IOD_PTO | PTO:.Klima[6].VisokPritiskKompresor2
PTOKlima6ElVentilKompresor1ERR | DIGITAL | IOD_PTO | PTO:.Klima[6].ElVentilKompresor1ERR
PTOKlima6ElVentilKompresor2ERR | DIGITAL | IOD_PTO | PTO:.Klima[6].ElVentilKompresor2ERR
PTOKlima6WrongPhaseSeqAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].WrongPhaseSeqAlarm
PTOKlima6PrekinjenLANalarm | DIGITAL | IOD_PTO | PTO:.Klima[6].PrekinjenLANalarm
PTOKlima6CWTempHighForDehum | DIGITAL | IOD_PTO | PTO:.Klima[6].CWTempHighForDehum
PTOKlima6CWVentilErrOrLowFlow | DIGITAL | IOD_PTO | PTO:.Klima[6].CWVentilErrOrLowFlow
PTOKlima6NapakaPriPretokuVode | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaPriPretokuVode
PTOKlima6CWhighTemp | DIGITAL | IOD_PTO | PTO:.Klima[6].CWhighTemp
PTOKlima6NapakaSenzorHotWTemp | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorHotWTemp
PTOKlima6NapakaSenzorCondWTemp | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorCondWTemp
PTOKlima6NapakaSenzorCW | DIGITAL | IOD_PTO | PTO:.Klima[6].NapakaSenzorCW
PTOKlima6Kompresor3naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Kompresor3naMejiObrUr
PTOKlima6Kompresor4naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Kompresor4naMejiObrUr
PTOKlima6ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].ZracniFilterNaMejiObrUr
PTOKlima6Grelec1naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Grelec1naMejiObrUr
PTOKlima6Grelec2naMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].Grelec2naMejiObrUr
PTOKlima6VlazilecNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].VlazilecNaMejiObrUr
PTOKlima6AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO | PTO:.Klima[6].AirCondUnitNaMejiObrUr
PTOKlima6DigIn2Alarm | DIGITAL | IOD_PTO | PTO:.Klima[6].DigIn2Alarm
PTOKlima6DigIn4Alarm | DIGITAL | IOD_PTO | PTO:.Klima[6].DigIn4Alarm
PTOKlima6DigIn6Alarm | DIGITAL | IOD_PTO | PTO:.Klima[6].DigIn6Alarm
PTOKlima6VlazilecGenAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].VlazilecGenAlarm
PTOKlima6General2ndLevAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].General2ndLevAlarm
PTOKlima6UnitOnRotAlarm | DIGITAL | IOD_PTO | PTO:.Klima[6].UnitOnRotAlarm
PTOKlima6UnitOnAlarmA | DIGITAL | IOD_PTO | PTO:.Klima[6].UnitOnAlarmA
PTOKlima6UnitOnAlarmB | DIGITAL | IOD_PTO | PTO:.Klima[6].UnitOnAlarmB
PTOKlima6UnitOnAlarmC | DIGITAL | IOD_PTO | PTO:.Klima[6].UnitOnAlarmC
PTOKlima1Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[1].Komp1On
PTOKlima1Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[1].Komp2On
PTOKlima1Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[1].Komp3On
PTOKlima1Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[1].Komp4On
PTOKlima2Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[2].Komp1On
PTOKlima2Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[2].Komp2On
PTOKlima2Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[2].Komp3On
PTOKlima2Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[2].Komp4On
PTOKlima3Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[3].Komp1On
PTOKlima3Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[3].Komp2On
PTOKlima3Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[3].Komp3On
PTOKlima3Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[3].Komp4On
PTOKlima4Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[4].Komp1On
PTOKlima4Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[4].Komp2On
PTOKlima4Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[4].Komp3On
PTOKlima4Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[4].Komp4On
PTOKlima5Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[5].Komp1On
PTOKlima5Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[5].Komp2On
PTOKlima5Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[5].Komp3On
PTOKlima5Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[5].Komp4On
PTOKlima6Komp1On | DIGITAL | IOD_PTO | PTO:.Klima[6].Komp1On
PTOKlima6Komp2On | DIGITAL | IOD_PTO | PTO:.Klima[6].Komp2On
PTOKlima6Komp3On | DIGITAL | IOD_PTO | PTO:.Klima[6].Komp3On
PTOKlima6Komp4On | DIGITAL | IOD_PTO | PTO:.Klima[6].Komp4On
PTOKlima1GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[1].GretjeStopnja1
PTOKlima1GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[1].GretjeStopnja2
PTOKlima1GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[1].GretjeStopnja3
PTOKlima2GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[2].GretjeStopnja1
PTOKlima2GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[2].GretjeStopnja2
PTOKlima2GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[2].GretjeStopnja3
PTOKlima3GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[3].GretjeStopnja1
PTOKlima3GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[3].GretjeStopnja2
PTOKlima3GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[3].GretjeStopnja3
PTOKlima4GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[4].GretjeStopnja1
PTOKlima4GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[4].GretjeStopnja2
PTOKlima4GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[4].GretjeStopnja3
PTOKlima5GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[5].GretjeStopnja1
PTOKlima5GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[5].GretjeStopnja2
PTOKlima5GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[5].GretjeStopnja3
PTOKlima6GretjeStopnja1 | DIGITAL | IOD_PTO | PTO:.Klima[6].GretjeStopnja1
PTOKlima6GretjeStopnja2 | DIGITAL | IOD_PTO | PTO:.Klima[6].GretjeStopnja2
PTOKlima6GretjeStopnja3 | DIGITAL | IOD_PTO | PTO:.Klima[6].GretjeStopnja3
PTOKlima1HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[1].HotGasOn
PTOKlima2HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[2].HotGasOn
PTOKlima3HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[3].HotGasOn
PTOKlima4HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[4].HotGasOn
PTOKlima5HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[5].HotGasOn
PTOKlima6HotGasOn | DIGITAL | IOD_PTO | PTO:.Klima[6].HotGasOn
PTOKlima1EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[1].EmergencyWorking
PTOKlima2EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[2].EmergencyWorking
PTOKlima3EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[3].EmergencyWorking
PTOKlima4EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[4].EmergencyWorking
PTOKlima5EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[5].EmergencyWorking
PTOKlima6EmergencyWorking | DIGITAL | IOD_PTO | PTO:.Klima[6].EmergencyWorking
PTODI_A1Q01_DovUpsB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q01_DovUpsB_ON
PTODI_A1Q0_GlavnoStiB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q0_GlavnoStiB_ON
PTODI_A1Q11_OdcUpsB_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q11_OdcUpsB_IZP
PTODI_A1Q11_OdcUpsB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q11_OdcUpsB_ON
PTODI_A1Q12_OdcByUpsB_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q12_OdcByUpsB_IZP
PTODI_A1Q12_OdcByUpsB_ON | DIGITAL | IOD_PTO | PTO:.DI_A1Q12_OdcByUpsB_ON
PTODI_A1Q13_OdcByB_IZP | DIGITAL | IOD_PTO | PTO:.DI_A1Q13_OdcByB_IZP
PTOErrCommScada2 | DIGITAL | IOD_PTO | PTO:.ErrCommScada2
PTOComSCADA2 | DIGITAL | IOD_PTO | PTO:.ComSCADA2
PTOComSCADA3 | DIGITAL | IOD_PTO | PTO:.ComSCADA3
PTODateTimeDan | INT | IOD_PTO | PTO:.DateTime.Dan | BYTE
PTODateTimeLeto | INT | IOD_PTO | PTO:.DateTime.Leto | BYTE
PTODateTimeMesec | INT | IOD_PTO | PTO:.DateTime.Mesec | BYTE
PTODateTimeMinuta | INT | IOD_PTO | PTO:.DateTime.Minuta | BYTE
PTODateTimeSekunda | INT | IOD_PTO | PTO:.DateTime.Sekunda | BYTE
PTODateTimeUra | INT | IOD_PTO | PTO:.DateTime.Ura | BYTE
PTOErrorComKlima1Code10 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[10] | BYTE
PTOErrorComKlima1Code11 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[11] | BYTE
PTOErrorComKlima1Code12 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[12] | BYTE
PTOErrorComKlima1Code13 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[13] | BYTE
PTOErrorComKlima1Code14 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[14] | BYTE
PTOErrorComKlima1Code15 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[15] | BYTE
PTOErrorComKlima1Code1 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[1] | BYTE
PTOErrorComKlima1Code2 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[2] | BYTE
PTOErrorComKlima1Code3 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[3] | BYTE
PTOErrorComKlima1Code4 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[4] | BYTE
PTOErrorComKlima1Code5 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[5] | BYTE
PTOErrorComKlima1Code6 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[6] | BYTE
PTOErrorComKlima1Code7 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[7] | BYTE
PTOErrorComKlima1Code8 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[8] | BYTE
PTOErrorComKlima1Code9 | INT | IOD_PTO | PTO:.ErrorComKlima[1].Code[9] | BYTE
PTOErrorComKlima1Status | INT | IOD_PTO | PTO:.ErrorComKlima[1].Status
PTOErrorComKlima2Code10 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[10] | BYTE
PTOErrorComKlima2Code11 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[11] | BYTE
PTOErrorComKlima2Code12 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[12] | BYTE
PTOErrorComKlima2Code13 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[13] | BYTE
PTOErrorComKlima2Code14 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[14] | BYTE
PTOErrorComKlima2Code15 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[15] | BYTE
PTOErrorComKlima2Code1 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[1] | BYTE
PTOErrorComKlima2Code2 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[2] | BYTE
PTOErrorComKlima2Code3 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[3] | BYTE
PTOErrorComKlima2Code4 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[4] | BYTE
PTOErrorComKlima2Code5 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[5] | BYTE
PTOErrorComKlima2Code6 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[6] | BYTE
PTOErrorComKlima2Code7 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[7] | BYTE
PTOErrorComKlima2Code8 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[8] | BYTE
PTOErrorComKlima2Code9 | INT | IOD_PTO | PTO:.ErrorComKlima[2].Code[9] | BYTE
PTOErrorComKlima2Status | INT | IOD_PTO | PTO:.ErrorComKlima[2].Status
PTOErrorComKlima3Code10 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[10] | BYTE
PTOErrorComKlima3Code11 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[11] | BYTE
PTOErrorComKlima3Code12 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[12] | BYTE
PTOErrorComKlima3Code13 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[13] | BYTE
PTOErrorComKlima3Code14 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[14] | BYTE
PTOErrorComKlima3Code15 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[15] | BYTE
PTOErrorComKlima3Code1 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[1] | BYTE
PTOErrorComKlima3Code2 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[2] | BYTE
PTOErrorComKlima3Code3 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[3] | BYTE
PTOErrorComKlima3Code4 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[4] | BYTE
PTOErrorComKlima3Code5 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[5] | BYTE
PTOErrorComKlima3Code6 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[6] | BYTE
PTOErrorComKlima3Code7 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[7] | BYTE
PTOErrorComKlima3Code8 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[8] | BYTE
PTOErrorComKlima3Code9 | INT | IOD_PTO | PTO:.ErrorComKlima[3].Code[9] | BYTE
PTOErrorComKlima3Status | INT | IOD_PTO | PTO:.ErrorComKlima[3].Status
PTOErrorComKlima4Code10 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[10] | BYTE
PTOErrorComKlima4Code11 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[11] | BYTE
PTOErrorComKlima4Code12 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[12] | BYTE
PTOErrorComKlima4Code13 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[13] | BYTE
PTOErrorComKlima4Code14 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[14] | BYTE
PTOErrorComKlima4Code15 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[15] | BYTE
PTOErrorComKlima4Code1 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[1] | BYTE
PTOErrorComKlima4Code2 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[2] | BYTE
PTOErrorComKlima4Code3 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[3] | BYTE
PTOErrorComKlima4Code4 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[4] | BYTE
PTOErrorComKlima4Code5 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[5] | BYTE
PTOErrorComKlima4Code6 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[6] | BYTE
PTOErrorComKlima4Code7 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[7] | BYTE
PTOErrorComKlima4Code8 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[8] | BYTE
PTOErrorComKlima4Code9 | INT | IOD_PTO | PTO:.ErrorComKlima[4].Code[9] | BYTE
PTOErrorComKlima4Status | INT | IOD_PTO | PTO:.ErrorComKlima[4].Status
PTOErrorComKlima5Code10 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[10] | BYTE
PTOErrorComKlima5Code11 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[11] | BYTE
PTOErrorComKlima5Code12 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[12] | BYTE
PTOErrorComKlima5Code13 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[13] | BYTE
PTOErrorComKlima5Code14 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[14] | BYTE
PTOErrorComKlima5Code15 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[15] | BYTE
PTOErrorComKlima5Code1 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[1] | BYTE
PTOErrorComKlima5Code2 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[2] | BYTE
PTOErrorComKlima5Code3 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[3] | BYTE
PTOErrorComKlima5Code4 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[4] | BYTE
PTOErrorComKlima5Code5 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[5] | BYTE
PTOErrorComKlima5Code6 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[6] | BYTE
PTOErrorComKlima5Code7 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[7] | BYTE
PTOErrorComKlima5Code8 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[8] | BYTE
PTOErrorComKlima5Code9 | INT | IOD_PTO | PTO:.ErrorComKlima[5].Code[9] | BYTE
PTOErrorComKlima5Status | INT | IOD_PTO | PTO:.ErrorComKlima[5].Status
PTOErrorComKlima6Code10 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[10] | BYTE
PTOErrorComKlima6Code11 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[11] | BYTE
PTOErrorComKlima6Code12 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[12] | BYTE
PTOErrorComKlima6Code13 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[13] | BYTE
PTOErrorComKlima6Code14 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[14] | BYTE
PTOErrorComKlima6Code15 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[15] | BYTE
PTOErrorComKlima6Code1 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[1] | BYTE
PTOErrorComKlima6Code2 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[2] | BYTE
PTOErrorComKlima6Code3 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[3] | BYTE
PTOErrorComKlima6Code4 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[4] | BYTE
PTOErrorComKlima6Code5 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[5] | BYTE
PTOErrorComKlima6Code6 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[6] | BYTE
PTOErrorComKlima6Code7 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[7] | BYTE
PTOErrorComKlima6Code8 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[8] | BYTE
PTOErrorComKlima6Code9 | INT | IOD_PTO | PTO:.ErrorComKlima[6].Code[9] | BYTE
PTOErrorComKlima6Status | INT | IOD_PTO | PTO:.ErrorComKlima[6].Status
PTOErrorComPMMCode10 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[10] | BYTE
PTOErrorComPMMCode11 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[11] | BYTE
PTOErrorComPMMCode12 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[12] | BYTE
PTOErrorComPMMCode13 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[13] | BYTE
PTOErrorComPMMCode14 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[14] | BYTE
PTOErrorComPMMCode15 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[15] | BYTE
PTOErrorComPMMCode1 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[1] | BYTE
PTOErrorComPMMCode2 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[2] | BYTE
PTOErrorComPMMCode3 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[3] | BYTE
PTOErrorComPMMCode4 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[4] | BYTE
PTOErrorComPMMCode5 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[5] | BYTE
PTOErrorComPMMCode6 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[6] | BYTE
PTOErrorComPMMCode7 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[7] | BYTE
PTOErrorComPMMCode8 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[8] | BYTE
PTOErrorComPMMCode9 | INT | IOD_PTO | PTO:.ErrorComPMM.Code[9] | BYTE
PTOErrorComPMMStatus | INT | IOD_PTO | PTO:.ErrorComPMM.Status
PTOErrorComUPS1Code10 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[10] | BYTE
PTOErrorComUPS1Code11 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[11] | BYTE
PTOErrorComUPS1Code12 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[12] | BYTE
PTOErrorComUPS1Code13 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[13] | BYTE
PTOErrorComUPS1Code14 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[14] | BYTE
PTOErrorComUPS1Code15 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[15] | BYTE
PTOErrorComUPS1Code1 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[1] | BYTE
PTOErrorComUPS1Code2 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[2] | BYTE
PTOErrorComUPS1Code3 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[3] | BYTE
PTOErrorComUPS1Code4 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[4] | BYTE
PTOErrorComUPS1Code5 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[5] | BYTE
PTOErrorComUPS1Code6 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[6] | BYTE
PTOErrorComUPS1Code7 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[7] | BYTE
PTOErrorComUPS1Code8 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[8] | BYTE
PTOErrorComUPS1Code9 | INT | IOD_PTO | PTO:.ErrorComUPS[1].Code[9] | BYTE
PTOErrorComUPS1Status | INT | IOD_PTO | PTO:.ErrorComUPS[1].Status
PTOErrorComUPS2Code10 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[10] | BYTE
PTOErrorComUPS2Code11 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[11] | BYTE
PTOErrorComUPS2Code12 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[12] | BYTE
PTOErrorComUPS2Code13 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[13] | BYTE
PTOErrorComUPS2Code14 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[14] | BYTE
PTOErrorComUPS2Code15 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[15] | BYTE
PTOErrorComUPS2Code1 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[1] | BYTE
PTOErrorComUPS2Code2 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[2] | BYTE
PTOErrorComUPS2Code3 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[3] | BYTE
PTOErrorComUPS2Code4 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[4] | BYTE
PTOErrorComUPS2Code5 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[5] | BYTE
PTOErrorComUPS2Code6 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[6] | BYTE
PTOErrorComUPS2Code7 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[7] | BYTE
PTOErrorComUPS2Code8 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[8] | BYTE
PTOErrorComUPS2Code9 | INT | IOD_PTO | PTO:.ErrorComUPS[2].Code[9] | BYTE
PTOErrorComUPS2Status | INT | IOD_PTO | PTO:.ErrorComUPS[2].Status
PTOKlima1GrelecStatus | INT | IOD_PTO | PTO:.Klima[1].GrelecStatus | BYTE
PTOKlima1IzhodniVentStatus | INT | IOD_PTO | PTO:.Klima[1].IzhodniVentStatus | BYTE
PTOKlima1KompresorStatus | INT | IOD_PTO | PTO:.Klima[1].KompresorStatus | BYTE
PTOKlima1VlazilecStatus | INT | IOD_PTO | PTO:.Klima[1].VlazilecStatus | BYTE
PTOKlima2GrelecStatus | INT | IOD_PTO | PTO:.Klima[2].GrelecStatus | BYTE
PTOKlima2IzhodniVentStatus | INT | IOD_PTO | PTO:.Klima[2].IzhodniVentStatus | BYTE
PTOKlima2KompresorStatus | INT | IOD_PTO | PTO:.Klima[2].KompresorStatus | BYTE
PTOKlima2VlazilecStatus | INT | IOD_PTO | PTO:.Klima[2].VlazilecStatus | BYTE
PTOKlima3GrelecStatus | INT | IOD_PTO | PTO:.Klima[3].GrelecStatus | BYTE
PTOKlima3IzhodniVentStatus | INT | IOD_PTO | PTO:.Klima[3].IzhodniVentStatus | BYTE
PTOKlima3KompresorStatus | INT | IOD_PTO | PTO:.Klima[3].KompresorStatus | BYTE
PTOKlima3VlazilecStatus | INT | IOD_PTO | PTO:.Klima[3].VlazilecStatus | BYTE
PTOKlima4GrelecStatus | INT | IOD_PTO | PTO:.Klima[4].GrelecStatus | BYTE
PTOKlima4IzhodniVentStatus | INT | IOD_PTO | PTO:.Klima[4].IzhodniVentStatus | BYTE
PTOKlima4KompresorStatus | INT | IOD_PTO | PTO:.Klima[4].KompresorStatus | BYTE
PTOKlima4VlazilecStatus | INT | IOD_PTO | PTO:.Klima[4].VlazilecStatus | BYTE
PTOKlima5GrelecStatus | INT | IOD_PTO | PTO:.Klima[5].GrelecStatus | BYTE
PTOKlima5IzhodniVentStatus | INT | IOD_PTO | PTO:.Klima[5].IzhodniVentStatus | BYTE
PTOKlima5KompresorStatus | INT | IOD_PTO | PTO:.Klima[5].KompresorStatus | BYTE
PTOKlima5VlazilecStatus | INT | IOD_PTO | PTO:.Klima[5].VlazilecStatus | BYTE
PTOKlima6GrelecStatus | INT | IOD_PTO | PTO:.Klima[6].GrelecStatus | BYTE
PTOKlima6IzhodniVentStatus | INT | IOD_PTO | PTO:.Klima[6].IzhodniVentStatus | BYTE
PTOKlima6KompresorStatus | INT | IOD_PTO | PTO:.Klima[6].KompresorStatus | BYTE
PTOKlima6VlazilecStatus | INT | IOD_PTO | PTO:.Klima[6].VlazilecStatus | BYTE
PTOMrezaIzpadVklopDelay1 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[1]
PTOMrezaIzpadVklopDelay2 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[2]
PTOMrezaIzpadVklopDelay3 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[3]
PTOMrezaIzpadVklopDelay4 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[4]
PTOMrezaIzpadVklopDelay5 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[5]
PTOMrezaIzpadVklopDelay6 | INT | IOD_PTO | PTO:.MrezaIzpadVklopDelay[6]
PTOPMMAlarmPhase1C01_16_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C01_16_60to80
PTOPMMAlarmPhase1C01_16_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C01_16_over80
PTOPMMAlarmPhase1C17_32_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C17_32_60to80
PTOPMMAlarmPhase1C17_32_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C17_32_over80
PTOPMMAlarmPhase1C33_42_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C33_42_60to80
PTOPMMAlarmPhase1C33_42_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[1].C33_42_over80
PTOPMMAlarmPhase2C01_16_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C01_16_60to80
PTOPMMAlarmPhase2C01_16_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C01_16_over80
PTOPMMAlarmPhase2C17_32_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C17_32_60to80
PTOPMMAlarmPhase2C17_32_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C17_32_over80
PTOPMMAlarmPhase2C33_42_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C33_42_60to80
PTOPMMAlarmPhase2C33_42_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[2].C33_42_over80
PTOPMMAlarmPhase3C01_16_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C01_16_60to80
PTOPMMAlarmPhase3C01_16_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C01_16_over80
PTOPMMAlarmPhase3C17_32_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C17_32_60to80
PTOPMMAlarmPhase3C17_32_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C17_32_over80
PTOPMMAlarmPhase3C33_42_60to80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C33_42_60to80
PTOPMMAlarmPhase3C33_42_over80 | INT | IOD_PTO | PTO:.PMM.AlarmPhase[3].C33_42_over80
PTOQstanje10 | INT | IOD_PTO | PTO:.Qstanje[10] | BYTE
PTOQstanje11 | INT | IOD_PTO | PTO:.Qstanje[11] | BYTE
PTOQstanje12 | INT | IOD_PTO | PTO:.Qstanje[12] | BYTE
PTOQstanje13 | INT | IOD_PTO | PTO:.Qstanje[13] | BYTE
PTOQstanje14 | INT | IOD_PTO | PTO:.Qstanje[14] | BYTE
PTOQstanje15 | INT | IOD_PTO | PTO:.Qstanje[15] | BYTE
PTOQstanje16 | INT | IOD_PTO | PTO:.Qstanje[16] | BYTE
PTOQstanje17 | INT | IOD_PTO | PTO:.Qstanje[17] | BYTE
PTOQstanje18 | INT | IOD_PTO | PTO:.Qstanje[18] | BYTE
PTOQstanje19 | INT | IOD_PTO | PTO:.Qstanje[19] | BYTE
PTOQstanje1 | INT | IOD_PTO | PTO:.Qstanje[1] | BYTE
PTOQstanje20 | INT | IOD_PTO | PTO:.Qstanje[20] | BYTE
PTOQstanje21 | INT | IOD_PTO | PTO:.Qstanje[21] | BYTE
PTOQstanje22 | INT | IOD_PTO | PTO:.Qstanje[22] | BYTE
PTOQstanje23 | INT | IOD_PTO | PTO:.Qstanje[23] | BYTE
PTOQstanje24 | INT | IOD_PTO | PTO:.Qstanje[24] | BYTE
PTOQstanje25 | INT | IOD_PTO | PTO:.Qstanje[25] | BYTE
PTOQstanje26 | INT | IOD_PTO | PTO:.Qstanje[26] | BYTE
PTOQstanje27 | INT | IOD_PTO | PTO:.Qstanje[27] | BYTE
PTOQstanje28 | INT | IOD_PTO | PTO:.Qstanje[28] | BYTE
PTOQstanje29 | INT | IOD_PTO | PTO:.Qstanje[29] | BYTE
PTOQstanje2 | INT | IOD_PTO | PTO:.Qstanje[2] | BYTE
PTOQstanje30 | INT | IOD_PTO | PTO:.Qstanje[30] | BYTE
PTOQstanje31 | INT | IOD_PTO | PTO:.Qstanje[31] | BYTE
PTOQstanje32 | INT | IOD_PTO | PTO:.Qstanje[32] | BYTE
PTOQstanje33 | INT | IOD_PTO | PTO:.Qstanje[33] | BYTE
PTOQstanje34 | INT | IOD_PTO | PTO:.Qstanje[34] | BYTE
PTOQstanje35 | INT | IOD_PTO | PTO:.Qstanje[35] | BYTE
PTOQstanje3 | INT | IOD_PTO | PTO:.Qstanje[3] | BYTE
PTOQstanje4 | INT | IOD_PTO | PTO:.Qstanje[4] | BYTE
PTOQstanje5 | INT | IOD_PTO | PTO:.Qstanje[5] | BYTE
PTOQstanje6 | INT | IOD_PTO | PTO:.Qstanje[6] | BYTE
PTOQstanje7 | INT | IOD_PTO | PTO:.Qstanje[7] | BYTE
PTOQstanje8 | INT | IOD_PTO | PTO:.Qstanje[8] | BYTE
PTOQstanje9 | INT | IOD_PTO | PTO:.Qstanje[9] | BYTE
PTOUPS1InverterStatus | INT | IOD_PTO | PTO:.UPS[1].InverterStatus
PTOUPS1OutputStatus | INT | IOD_PTO | PTO:.UPS[1].OutputStatus
PTOUPS1StatusBaterije | INT | IOD_PTO | PTO:.UPS[1].StatusBaterije
PTOUPS1SteviloIzpadovVhodneLinije | INT | IOD_PTO | PTO:.UPS[1].SteviloIzpadovVhodneLinije
PTOUPS1UnitStatus | INT | IOD_PTO | PTO:.UPS[1].UnitStatus
PTOUPS2InverterStatus | INT | IOD_PTO | PTO:.UPS[2].InverterStatus
PTOUPS2OutputStatus | INT | IOD_PTO | PTO:.UPS[2].OutputStatus
PTOUPS2StatusBaterije | INT | IOD_PTO | PTO:.UPS[2].StatusBaterije
PTOUPS2SteviloIzpadovVhodneLinije | INT | IOD_PTO | PTO:.UPS[2].SteviloIzpadovVhodneLinije
PTOUPS2UnitStatus | INT | IOD_PTO | PTO:.UPS[2].UnitStatus
PTOUserCurrentLevel | INT | IOD_PTO | PTO:.UserCurrentLevel | BYTE
PTOKlima1ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[1].ObratovalneUre
PTOKlima1TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[1].TemperaturaProstora
PTOKlima1TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[1].TempIzpihanegaZraka
PTOKlima1VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[1].VlaznostProstora
PTOKlima1ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[1].ZunanjaTemp
PTOKlima2ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[2].ObratovalneUre
PTOKlima2TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[2].TemperaturaProstora
PTOKlima2TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[2].TempIzpihanegaZraka
PTOKlima2VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[2].VlaznostProstora
PTOKlima2ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[2].ZunanjaTemp
PTOKlima3ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[3].ObratovalneUre
PTOKlima3TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[3].TemperaturaProstora
PTOKlima3TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[3].TempIzpihanegaZraka
PTOKlima3VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[3].VlaznostProstora
PTOKlima3ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[3].ZunanjaTemp
PTOKlima4ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[4].ObratovalneUre
PTOKlima4TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[4].TemperaturaProstora
PTOKlima4TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[4].TempIzpihanegaZraka
PTOKlima4VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[4].VlaznostProstora
PTOKlima4ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[4].ZunanjaTemp
PTOKlima5ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[5].ObratovalneUre
PTOKlima5TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[5].TemperaturaProstora
PTOKlima5TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[5].TempIzpihanegaZraka
PTOKlima5VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[5].VlaznostProstora
PTOKlima5ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[5].ZunanjaTemp
PTOKlima6ObratovalneUre | REAL | IOD_PTO | PTO:.Klima[6].ObratovalneUre
PTOKlima6TemperaturaProstora | REAL | IOD_PTO | PTO:.Klima[6].TemperaturaProstora
PTOKlima6TempIzpihanegaZraka | REAL | IOD_PTO | PTO:.Klima[6].TempIzpihanegaZraka
PTOKlima6VlaznostProstora | REAL | IOD_PTO | PTO:.Klima[6].VlaznostProstora
PTOKlima6ZunanjaTemp | REAL | IOD_PTO | PTO:.Klima[6].ZunanjaTemp
PTOPMMActiveEnergyConsumed_kWh | REAL | IOD_PTO | PTO:.PMM.ActiveEnergyConsumed_kWh
PTOPMMActivePowerPhaseA_kW | REAL | IOD_PTO | PTO:.PMM.ActivePowerPhaseA_kW
PTOPMMActivePowerPhaseB_kW | REAL | IOD_PTO | PTO:.PMM.ActivePowerPhaseB_kW
PTOPMMActivePowerPhaseC_kW | REAL | IOD_PTO | PTO:.PMM.ActivePowerPhaseC_kW
PTOPMMAparentPowerPhaseA | REAL | IOD_PTO | PTO:.PMM.AparentPowerPhaseA
PTOPMMAparentPowerPhaseB | REAL | IOD_PTO | PTO:.PMM.AparentPowerPhaseB
PTOPMMAparentPowerPhaseC | REAL | IOD_PTO | PTO:.PMM.AparentPowerPhaseC
PTOPMMAverageCurrent_A | REAL | IOD_PTO | PTO:.PMM.AverageCurrent_A
PTOPMMAveragePhaseToNeutral_V | REAL | IOD_PTO | PTO:.PMM.AveragePhaseToNeutral_V
PTOPMMAveragePhaseToPhase_V | REAL | IOD_PTO | PTO:.PMM.AveragePhaseToPhase_V
PTOPMMCurrentInPhaseA_A | REAL | IOD_PTO | PTO:.PMM.CurrentInPhaseA_A
PTOPMMCurrentInPhaseB_A | REAL | IOD_PTO | PTO:.PMM.CurrentInPhaseB_A
PTOPMMCurrentInPhaseC_A | REAL | IOD_PTO | PTO:.PMM.CurrentInPhaseC_A
PTOPMMFrequency_Hz | REAL | IOD_PTO | PTO:.PMM.Frequency_Hz
PTOPMMPhase1Current10 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[10]
PTOPMMPhase1Current11 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[11]
PTOPMMPhase1Current12 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[12]
PTOPMMPhase1Current13 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[13]
PTOPMMPhase1Current14 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[14]
PTOPMMPhase1Current15 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[15]
PTOPMMPhase1Current16 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[16]
PTOPMMPhase1Current17 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[17]
PTOPMMPhase1Current18 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[18]
PTOPMMPhase1Current19 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[19]
PTOPMMPhase1Current1 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[1]
PTOPMMPhase1Current20 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[20]
PTOPMMPhase1Current21 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[21]
PTOPMMPhase1Current22 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[22]
PTOPMMPhase1Current23 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[23]
PTOPMMPhase1Current24 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[24]
PTOPMMPhase1Current25 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[25]
PTOPMMPhase1Current26 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[26]
PTOPMMPhase1Current27 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[27]
PTOPMMPhase1Current28 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[28]
PTOPMMPhase1Current29 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[29]
PTOPMMPhase1Current2 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[2]
PTOPMMPhase1Current30 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[30]
PTOPMMPhase1Current31 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[31]
PTOPMMPhase1Current32 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[32]
PTOPMMPhase1Current33 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[33]
PTOPMMPhase1Current34 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[34]
PTOPMMPhase1Current35 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[35]
PTOPMMPhase1Current36 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[36]
PTOPMMPhase1Current37 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[37]
PTOPMMPhase1Current38 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[38]
PTOPMMPhase1Current39 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[39]
PTOPMMPhase1Current3 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[3]
PTOPMMPhase1Current40 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[40]
PTOPMMPhase1Current41 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[41]
PTOPMMPhase1Current42 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[42]
PTOPMMPhase1Current4 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[4]
PTOPMMPhase1Current5 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[5]
PTOPMMPhase1Current6 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[6]
PTOPMMPhase1Current7 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[7]
PTOPMMPhase1Current8 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[8]
PTOPMMPhase1Current9 | REAL | IOD_PTO | PTO:.PMM.Phase[1].Current[9]
PTOPMMPhase2Current10 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[10]
PTOPMMPhase2Current11 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[11]
PTOPMMPhase2Current12 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[12]
PTOPMMPhase2Current13 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[13]
PTOPMMPhase2Current14 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[14]
PTOPMMPhase2Current15 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[15]
PTOPMMPhase2Current16 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[16]
PTOPMMPhase2Current17 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[17]
PTOPMMPhase2Current18 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[18]
PTOPMMPhase2Current19 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[19]
PTOPMMPhase2Current1 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[1]
PTOPMMPhase2Current20 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[20]
PTOPMMPhase2Current21 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[21]
PTOPMMPhase2Current22 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[22]
PTOPMMPhase2Current23 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[23]
PTOPMMPhase2Current24 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[24]
PTOPMMPhase2Current25 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[25]
PTOPMMPhase2Current26 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[26]
PTOPMMPhase2Current27 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[27]
PTOPMMPhase2Current28 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[28]
PTOPMMPhase2Current29 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[29]
PTOPMMPhase2Current2 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[2]
PTOPMMPhase2Current30 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[30]
PTOPMMPhase2Current31 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[31]
PTOPMMPhase2Current32 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[32]
PTOPMMPhase2Current33 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[33]
PTOPMMPhase2Current34 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[34]
PTOPMMPhase2Current35 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[35]
PTOPMMPhase2Current36 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[36]
PTOPMMPhase2Current37 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[37]
PTOPMMPhase2Current38 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[38]
PTOPMMPhase2Current39 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[39]
PTOPMMPhase2Current3 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[3]
PTOPMMPhase2Current40 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[40]
PTOPMMPhase2Current41 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[41]
PTOPMMPhase2Current42 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[42]
PTOPMMPhase2Current4 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[4]
PTOPMMPhase2Current5 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[5]
PTOPMMPhase2Current6 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[6]
PTOPMMPhase2Current7 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[7]
PTOPMMPhase2Current8 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[8]
PTOPMMPhase2Current9 | REAL | IOD_PTO | PTO:.PMM.Phase[2].Current[9]
PTOPMMPhase3Current10 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[10]
PTOPMMPhase3Current11 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[11]
PTOPMMPhase3Current12 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[12]
PTOPMMPhase3Current13 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[13]
PTOPMMPhase3Current14 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[14]
PTOPMMPhase3Current15 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[15]
PTOPMMPhase3Current16 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[16]
PTOPMMPhase3Current17 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[17]
PTOPMMPhase3Current18 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[18]
PTOPMMPhase3Current19 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[19]
PTOPMMPhase3Current1 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[1]
PTOPMMPhase3Current20 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[20]
PTOPMMPhase3Current21 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[21]
PTOPMMPhase3Current22 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[22]
PTOPMMPhase3Current23 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[23]
PTOPMMPhase3Current24 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[24]
PTOPMMPhase3Current25 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[25]
PTOPMMPhase3Current26 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[26]
PTOPMMPhase3Current27 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[27]
PTOPMMPhase3Current28 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[28]
PTOPMMPhase3Current29 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[29]
PTOPMMPhase3Current2 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[2]
PTOPMMPhase3Current30 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[30]
PTOPMMPhase3Current31 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[31]
PTOPMMPhase3Current32 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[32]
PTOPMMPhase3Current33 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[33]
PTOPMMPhase3Current34 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[34]
PTOPMMPhase3Current35 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[35]
PTOPMMPhase3Current36 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[36]
PTOPMMPhase3Current37 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[37]
PTOPMMPhase3Current38 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[38]
PTOPMMPhase3Current39 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[39]
PTOPMMPhase3Current3 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[3]
PTOPMMPhase3Current40 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[40]
PTOPMMPhase3Current41 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[41]
PTOPMMPhase3Current42 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[42]
PTOPMMPhase3Current4 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[4]
PTOPMMPhase3Current5 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[5]
PTOPMMPhase3Current6 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[6]
PTOPMMPhase3Current7 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[7]
PTOPMMPhase3Current8 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[8]
PTOPMMPhase3Current9 | REAL | IOD_PTO | PTO:.PMM.Phase[3].Current[9]
PTOPMMPowerFactorSys | REAL | IOD_PTO | PTO:.PMM.PowerFactorSys
PTOPMMReactiveEnergyConsumed_kVARh | REAL | IOD_PTO | PTO:.PMM.ReactiveEnergyConsumed_kVARh
PTOPMMReactivePowerPhaseA | REAL | IOD_PTO | PTO:.PMM.ReactivePowerPhaseA
PTOPMMReactivePowerPhaseB | REAL | IOD_PTO | PTO:.PMM.ReactivePowerPhaseB
PTOPMMReactivePowerPhaseC | REAL | IOD_PTO | PTO:.PMM.ReactivePowerPhaseC
PTOPMMTotalActivePower_kW | REAL | IOD_PTO | PTO:.PMM.TotalActivePower_kW
PTOPMMTotalAparentPower_kVA | REAL | IOD_PTO | PTO:.PMM.TotalAparentPower_kVA
PTOPMMTotalPowerFactor | REAL | IOD_PTO | PTO:.PMM.TotalPowerFactor
PTOPMMTotalReactivePower_kVAR | REAL | IOD_PTO | PTO:.PMM.TotalReactivePower_kVAR
PTOPMMVirA_fsys | REAL | IOD_PTO | PTO:.PMM.VirA_fsys
PTOPMMVirA_Isys | REAL | IOD_PTO | PTO:.PMM.VirA_Isys
PTOPMMVirA_PFsys | REAL | IOD_PTO | PTO:.PMM.VirA_PFsys
PTOPMMVirA_Psys | REAL | IOD_PTO | PTO:.PMM.VirA_Psys
PTOPMMVirA_Qsys | REAL | IOD_PTO | PTO:.PMM.VirA_Qsys
PTOPMMVirA_Ssys | REAL | IOD_PTO | PTO:.PMM.VirA_Ssys
PTOPMMVirA_Usys | REAL | IOD_PTO | PTO:.PMM.VirA_Usys
PTOPMMVirB_fsys | REAL | IOD_PTO | PTO:.PMM.VirB_fsys
PTOPMMVirB_Isys | REAL | IOD_PTO | PTO:.PMM.VirB_Isys
PTOPMMVirB_PFsys | REAL | IOD_PTO | PTO:.PMM.VirB_PFsys
PTOPMMVirB_Psys | REAL | IOD_PTO | PTO:.PMM.VirB_Psys
PTOPMMVirB_Qsys | REAL | IOD_PTO | PTO:.PMM.VirB_Qsys
PTOPMMVirB_Ssys | REAL | IOD_PTO | PTO:.PMM.VirB_Ssys
PTOPMMVirB_Usys | REAL | IOD_PTO | PTO:.PMM.VirB_Usys
PTOPMMVirBActiveEnergyConsumed_kWh | REAL | IOD_PTO | PTO:.PMM.VirBActiveEnergyConsumed_kWh
PTOPMMVirBActivePowerPhaseA_kW | REAL | IOD_PTO | PTO:.PMM.VirBActivePowerPhaseA_kW
PTOPMMVirBActivePowerPhaseB_kW | REAL | IOD_PTO | PTO:.PMM.VirBActivePowerPhaseB_kW
PTOPMMVirBActivePowerPhaseC_kW | REAL | IOD_PTO | PTO:.PMM.VirBActivePowerPhaseC_kW
PTOPMMVirBAparentPowerPhaseA | REAL | IOD_PTO | PTO:.PMM.VirBAparentPowerPhaseA
PTOPMMVirBAparentPowerPhaseB | REAL | IOD_PTO | PTO:.PMM.VirBAparentPowerPhaseB
PTOPMMVirBAparentPowerPhaseC | REAL | IOD_PTO | PTO:.PMM.VirBAparentPowerPhaseC
PTOPMMVirBAverageCurrent_A | REAL | IOD_PTO | PTO:.PMM.VirBAverageCurrent_A
PTOPMMVirBAveragePhaseToNeutral_V | REAL | IOD_PTO | PTO:.PMM.VirBAveragePhaseToNeutral_V
PTOPMMVirBAveragePhaseToPhase_V | REAL | IOD_PTO | PTO:.PMM.VirBAveragePhaseToPhase_V
PTOPMMVirBCurrentInPhaseA_A | REAL | IOD_PTO | PTO:.PMM.VirBCurrentInPhaseA_A
PTOPMMVirBCurrentInPhaseB_A | REAL | IOD_PTO | PTO:.PMM.VirBCurrentInPhaseB_A
PTOPMMVirBCurrentInPhaseC_A | REAL | IOD_PTO | PTO:.PMM.VirBCurrentInPhaseC_A
PTOPMMVirBFrequency_Hz | REAL | IOD_PTO | PTO:.PMM.VirBFrequency_Hz
PTOPMMVirBPowerFactorSys | REAL | IOD_PTO | PTO:.PMM.VirBPowerFactorSys
PTOPMMVirBReactiveEnergyConsumed_kVARh | REAL | IOD_PTO | PTO:.PMM.VirBReactiveEnergyConsumed_kVARh
PTOPMMVirBReactivePowerPhaseA | REAL | IOD_PTO | PTO:.PMM.VirBReactivePowerPhaseA
PTOPMMVirBReactivePowerPhaseB | REAL | IOD_PTO | PTO:.PMM.VirBReactivePowerPhaseB
PTOPMMVirBReactivePowerPhaseC | REAL | IOD_PTO | PTO:.PMM.VirBReactivePowerPhaseC
PTOPMMVirBTotalActivePower_kW | REAL | IOD_PTO | PTO:.PMM.VirBTotalActivePower_kW
PTOPMMVirBTotalAparentPower_kVA | REAL | IOD_PTO | PTO:.PMM.VirBTotalAparentPower_kVA
PTOPMMVirBTotalPowerFactor | REAL | IOD_PTO | PTO:.PMM.VirBTotalPowerFactor
PTOPMMVirBTotalReactivePower_kVAR | REAL | IOD_PTO | PTO:.PMM.VirBTotalReactivePower_kVAR
PTOPMMVirBVoltageBetweenPhaseAB_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseAB_V
PTOPMMVirBVoltageBetweenPhaseAN_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseAN_V
PTOPMMVirBVoltageBetweenPhaseBC_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseBC_V
PTOPMMVirBVoltageBetweenPhaseBN_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseBN_V
PTOPMMVirBVoltageBetweenPhaseCA_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseCA_V
PTOPMMVirBVoltageBetweenPhaseCN_V | REAL | IOD_PTO | PTO:.PMM.VirBVoltageBetweenPhaseCN_V
PTOPMMVoltageBetweenPhaseAB_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseAB_V
PTOPMMVoltageBetweenPhaseAN_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseAN_V
PTOPMMVoltageBetweenPhaseBC_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseBC_V
PTOPMMVoltageBetweenPhaseBN_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseBN_V
PTOPMMVoltageBetweenPhaseCA_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseCA_V
PTOPMMVoltageBetweenPhaseCN_V | REAL | IOD_PTO | PTO:.PMM.VoltageBetweenPhaseCN_V
PTOPMMfaza01 | REAL | IOD_PTO | PTO:.PMMfaza01
PTOPMMfaza02 | REAL | IOD_PTO | PTO:.PMMfaza02
PTOPMMfaza03 | REAL | IOD_PTO | PTO:.PMMfaza03
PTOPMMfaza04 | REAL | IOD_PTO | PTO:.PMMfaza04
PTOPMMfaza05 | REAL | IOD_PTO | PTO:.PMMfaza05
PTOPMMfaza06 | REAL | IOD_PTO | PTO:.PMMfaza06
PTOPMMfaza07 | REAL | IOD_PTO | PTO:.PMMfaza07
PTOPMMfaza08 | REAL | IOD_PTO | PTO:.PMMfaza08
PTOPMMfaza09 | REAL | IOD_PTO | PTO:.PMMfaza09
PTOPMMfaza10 | REAL | IOD_PTO | PTO:.PMMfaza10
PTOPMMfaza11 | REAL | IOD_PTO | PTO:.PMMfaza11
PTOPMMfaza12 | REAL | IOD_PTO | PTO:.PMMfaza12
PTOPMMfaza13 | REAL | IOD_PTO | PTO:.PMMfaza13
PTOPMMfaza14 | REAL | IOD_PTO | PTO:.PMMfaza14
PTOPMMfaza15 | REAL | IOD_PTO | PTO:.PMMfaza15
PTOPMMfaza16 | REAL | IOD_PTO | PTO:.PMMfaza16
PTOPMMfaza17 | REAL | IOD_PTO | PTO:.PMMfaza17
PTOPMMfaza18 | REAL | IOD_PTO | PTO:.PMMfaza18
PTOPMMfaza19 | REAL | IOD_PTO | PTO:.PMMfaza19
PTOPMMfaza20 | REAL | IOD_PTO | PTO:.PMMfaza20
PTOPMMfaza21 | REAL | IOD_PTO | PTO:.PMMfaza21
PTOPMMfaza22 | REAL | IOD_PTO | PTO:.PMMfaza22
PTOPMMfaza23 | REAL | IOD_PTO | PTO:.PMMfaza23
PTOPMMfaza24 | REAL | IOD_PTO | PTO:.PMMfaza24
PTOPMMfaza25 | REAL | IOD_PTO | PTO:.PMMfaza25
PTOPMMfaza26 | REAL | IOD_PTO | PTO:.PMMfaza26
PTOPMMfaza27 | REAL | IOD_PTO | PTO:.PMMfaza27
PTOPMMfaza28 | REAL | IOD_PTO | PTO:.PMMfaza28
PTOPMMfaza29 | REAL | IOD_PTO | PTO:.PMMfaza29
PTOPMMfaza30 | REAL | IOD_PTO | PTO:.PMMfaza30
PTOPMMfaza31 | REAL | IOD_PTO | PTO:.PMMfaza31
PTOPMMfaza32 | REAL | IOD_PTO | PTO:.PMMfaza32
PTOPMMfaza33 | REAL | IOD_PTO | PTO:.PMMfaza33
PTOPMMfaza34 | REAL | IOD_PTO | PTO:.PMMfaza34
PTOPMMfaza35 | REAL | IOD_PTO | PTO:.PMMfaza35
PTOPMMfaza36 | REAL | IOD_PTO | PTO:.PMMfaza36
PTOPMMfaza37 | REAL | IOD_PTO | PTO:.PMMfaza37
PTOPMMfaza38 | REAL | IOD_PTO | PTO:.PMMfaza38
PTOPMMfaza39 | REAL | IOD_PTO | PTO:.PMMfaza39
PTOPMMfaza40 | REAL | IOD_PTO | PTO:.PMMfaza40
PTOPMMfaza41 | REAL | IOD_PTO | PTO:.PMMfaza41
PTOPMMfaza42 | REAL | IOD_PTO | PTO:.PMMfaza42
PTOPMMfaza6010 | REAL | IOD_PTO | PTO:.PMMfaza60[10]
PTOPMMfaza6011 | REAL | IOD_PTO | PTO:.PMMfaza60[11]
PTOPMMfaza6012 | REAL | IOD_PTO | PTO:.PMMfaza60[12]
PTOPMMfaza6013 | REAL | IOD_PTO | PTO:.PMMfaza60[13]
PTOPMMfaza6014 | REAL | IOD_PTO | PTO:.PMMfaza60[14]
PTOPMMfaza6015 | REAL | IOD_PTO | PTO:.PMMfaza60[15]
PTOPMMfaza6016 | REAL | IOD_PTO | PTO:.PMMfaza60[16]
PTOPMMfaza6017 | REAL | IOD_PTO | PTO:.PMMfaza60[17]
PTOPMMfaza6018 | REAL | IOD_PTO | PTO:.PMMfaza60[18]
PTOPMMfaza6019 | REAL | IOD_PTO | PTO:.PMMfaza60[19]
PTOPMMfaza601 | REAL | IOD_PTO | PTO:.PMMfaza60[1]
PTOPMMfaza6020 | REAL | IOD_PTO | PTO:.PMMfaza60[20]
PTOPMMfaza6021 | REAL | IOD_PTO | PTO:.PMMfaza60[21]
PTOPMMfaza6022 | REAL | IOD_PTO | PTO:.PMMfaza60[22]
PTOPMMfaza6023 | REAL | IOD_PTO | PTO:.PMMfaza60[23]
PTOPMMfaza6024 | REAL | IOD_PTO | PTO:.PMMfaza60[24]
PTOPMMfaza6025 | REAL | IOD_PTO | PTO:.PMMfaza60[25]
PTOPMMfaza6026 | REAL | IOD_PTO | PTO:.PMMfaza60[26]
PTOPMMfaza6027 | REAL | IOD_PTO | PTO:.PMMfaza60[27]
PTOPMMfaza6028 | REAL | IOD_PTO | PTO:.PMMfaza60[28]
PTOPMMfaza6029 | REAL | IOD_PTO | PTO:.PMMfaza60[29]
PTOPMMfaza602 | REAL | IOD_PTO | PTO:.PMMfaza60[2]
PTOPMMfaza6030 | REAL | IOD_PTO | PTO:.PMMfaza60[30]
PTOPMMfaza6031 | REAL | IOD_PTO | PTO:.PMMfaza60[31]
PTOPMMfaza6032 | REAL | IOD_PTO | PTO:.PMMfaza60[32]
PTOPMMfaza6033 | REAL | IOD_PTO | PTO:.PMMfaza60[33]
PTOPMMfaza6034 | REAL | IOD_PTO | PTO:.PMMfaza60[34]
PTOPMMfaza6035 | REAL | IOD_PTO | PTO:.PMMfaza60[35]
PTOPMMfaza6036 | REAL | IOD_PTO | PTO:.PMMfaza60[36]
PTOPMMfaza6037 | REAL | IOD_PTO | PTO:.PMMfaza60[37]
PTOPMMfaza6038 | REAL | IOD_PTO | PTO:.PMMfaza60[38]
PTOPMMfaza6039 | REAL | IOD_PTO | PTO:.PMMfaza60[39]
PTOPMMfaza603 | REAL | IOD_PTO | PTO:.PMMfaza60[3]
PTOPMMfaza6040 | REAL | IOD_PTO | PTO:.PMMfaza60[40]
PTOPMMfaza6041 | REAL | IOD_PTO | PTO:.PMMfaza60[41]
PTOPMMfaza6042 | REAL | IOD_PTO | PTO:.PMMfaza60[42]
PTOPMMfaza604 | REAL | IOD_PTO | PTO:.PMMfaza60[4]
PTOPMMfaza605 | REAL | IOD_PTO | PTO:.PMMfaza60[5]
PTOPMMfaza606 | REAL | IOD_PTO | PTO:.PMMfaza60[6]
PTOPMMfaza607 | REAL | IOD_PTO | PTO:.PMMfaza60[7]
PTOPMMfaza608 | REAL | IOD_PTO | PTO:.PMMfaza60[8]
PTOPMMfaza609 | REAL | IOD_PTO | PTO:.PMMfaza60[9]
PTOPMMfaza8010 | REAL | IOD_PTO | PTO:.PMMfaza80[10]
PTOPMMfaza8011 | REAL | IOD_PTO | PTO:.PMMfaza80[11]
PTOPMMfaza8012 | REAL | IOD_PTO | PTO:.PMMfaza80[12]
PTOPMMfaza8013 | REAL | IOD_PTO | PTO:.PMMfaza80[13]
PTOPMMfaza8014 | REAL | IOD_PTO | PTO:.PMMfaza80[14]
PTOPMMfaza8015 | REAL | IOD_PTO | PTO:.PMMfaza80[15]
PTOPMMfaza8016 | REAL | IOD_PTO | PTO:.PMMfaza80[16]
PTOPMMfaza8017 | REAL | IOD_PTO | PTO:.PMMfaza80[17]
PTOPMMfaza8018 | REAL | IOD_PTO | PTO:.PMMfaza80[18]
PTOPMMfaza8019 | REAL | IOD_PTO | PTO:.PMMfaza80[19]
PTOPMMfaza801 | REAL | IOD_PTO | PTO:.PMMfaza80[1]
PTOPMMfaza8020 | REAL | IOD_PTO | PTO:.PMMfaza80[20]
PTOPMMfaza8021 | REAL | IOD_PTO | PTO:.PMMfaza80[21]
PTOPMMfaza8022 | REAL | IOD_PTO | PTO:.PMMfaza80[22]
PTOPMMfaza8023 | REAL | IOD_PTO | PTO:.PMMfaza80[23]
PTOPMMfaza8024 | REAL | IOD_PTO | PTO:.PMMfaza80[24]
PTOPMMfaza8025 | REAL | IOD_PTO | PTO:.PMMfaza80[25]
PTOPMMfaza8026 | REAL | IOD_PTO | PTO:.PMMfaza80[26]
PTOPMMfaza8027 | REAL | IOD_PTO | PTO:.PMMfaza80[27]
PTOPMMfaza8028 | REAL | IOD_PTO | PTO:.PMMfaza80[28]
PTOPMMfaza8029 | REAL | IOD_PTO | PTO:.PMMfaza80[29]
PTOPMMfaza802 | REAL | IOD_PTO | PTO:.PMMfaza80[2]
PTOPMMfaza8030 | REAL | IOD_PTO | PTO:.PMMfaza80[30]
PTOPMMfaza8031 | REAL | IOD_PTO | PTO:.PMMfaza80[31]
PTOPMMfaza8032 | REAL | IOD_PTO | PTO:.PMMfaza80[32]
PTOPMMfaza8033 | REAL | IOD_PTO | PTO:.PMMfaza80[33]
PTOPMMfaza8034 | REAL | IOD_PTO | PTO:.PMMfaza80[34]
PTOPMMfaza8035 | REAL | IOD_PTO | PTO:.PMMfaza80[35]
PTOPMMfaza8036 | REAL | IOD_PTO | PTO:.PMMfaza80[36]
PTOPMMfaza8037 | REAL | IOD_PTO | PTO:.PMMfaza80[37]
PTOPMMfaza8038 | REAL | IOD_PTO | PTO:.PMMfaza80[38]
PTOPMMfaza8039 | REAL | IOD_PTO | PTO:.PMMfaza80[39]
PTOPMMfaza803 | REAL | IOD_PTO | PTO:.PMMfaza80[3]
PTOPMMfaza8040 | REAL | IOD_PTO | PTO:.PMMfaza80[40]
PTOPMMfaza8041 | REAL | IOD_PTO | PTO:.PMMfaza80[41]
PTOPMMfaza8042 | REAL | IOD_PTO | PTO:.PMMfaza80[42]
PTOPMMfaza804 | REAL | IOD_PTO | PTO:.PMMfaza80[4]
PTOPMMfaza805 | REAL | IOD_PTO | PTO:.PMMfaza80[5]
PTOPMMfaza806 | REAL | IOD_PTO | PTO:.PMMfaza80[6]
PTOPMMfaza807 | REAL | IOD_PTO | PTO:.PMMfaza80[7]
PTOPMMfaza808 | REAL | IOD_PTO | PTO:.PMMfaza80[8]
PTOPMMfaza809 | REAL | IOD_PTO | PTO:.PMMfaza80[9]
PTOSenzorTemp1 | REAL | IOD_PTO | PTO:.SenzorTemp[1]
PTOSenzorTemp2 | REAL | IOD_PTO | PTO:.SenzorTemp[2]
PTOSenzorTemp3 | REAL | IOD_PTO | PTO:.SenzorTemp[3]
PTOSenzorTemp4 | REAL | IOD_PTO | PTO:.SenzorTemp[4]
PTOSenzorTemp5 | REAL | IOD_PTO | PTO:.SenzorTemp[5]
PTOSenzorTemp6 | REAL | IOD_PTO | PTO:.SenzorTemp[6]
PTOSenzorVlaga1 | REAL | IOD_PTO | PTO:.SenzorVlaga[1]
PTOSenzorVlaga2 | REAL | IOD_PTO | PTO:.SenzorVlaga[2]
PTOSenzorVlaga3 | REAL | IOD_PTO | PTO:.SenzorVlaga[3]
PTOSenzorVlaga4 | REAL | IOD_PTO | PTO:.SenzorVlaga[4]
PTOSenzorVlaga5 | REAL | IOD_PTO | PTO:.SenzorVlaga[5]
PTOSenzorVlaga6 | REAL | IOD_PTO | PTO:.SenzorVlaga[6]
PTOTempAlarmPoint0 | REAL | IOD_PTO | PTO:.TempAlarmPoint[0]
PTOTempAlarmPoint1 | REAL | IOD_PTO | PTO:.TempAlarmPoint[1]
PTOTempAlarmPoint2 | REAL | IOD_PTO | PTO:.TempAlarmPoint[2]
PTOTempAlarmPoint3 | REAL | IOD_PTO | PTO:.TempAlarmPoint[3]
PTOTempMaxPoint0 | REAL | IOD_PTO | PTO:.TempMaxPoint[0]
PTOTempMaxPoint1 | REAL | IOD_PTO | PTO:.TempMaxPoint[1]
PTOTempMaxPoint2 | REAL | IOD_PTO | PTO:.TempMaxPoint[2]
PTOTempMaxPoint3 | REAL | IOD_PTO | PTO:.TempMaxPoint[3]
PTOTempPovp0 | REAL | IOD_PTO | PTO:.TempPovp[0]
PTOTempPovp1 | REAL | IOD_PTO | PTO:.TempPovp[1]
PTOTempPovp2 | REAL | IOD_PTO | PTO:.TempPovp[2]
PTOTempPovp3 | REAL | IOD_PTO | PTO:.TempPovp[3]
PTOTempSetPoint0 | REAL | IOD_PTO | PTO:.TempSetPoint[0]
PTOTempSetPoint1 | REAL | IOD_PTO | PTO:.TempSetPoint[1]
PTOTempSetPoint2 | REAL | IOD_PTO | PTO:.TempSetPoint[2]
PTOTempSetPoint3 | REAL | IOD_PTO | PTO:.TempSetPoint[3]
PTOUPS1EstimatedChargeRemaining | REAL | IOD_PTO | PTO:.UPS[1].EstimatedChargeRemaining
PTOUPS1EstimatedMinutesRemaining | REAL | IOD_PTO | PTO:.UPS[1].EstimatedMinutesRemaining
PTOUPS1IzhodMocL1 | REAL | IOD_PTO | PTO:.UPS[1].IzhodMocL1
PTOUPS1IzhodMocL2 | REAL | IOD_PTO | PTO:.UPS[1].IzhodMocL2
PTOUPS1IzhodMocL3 | REAL | IOD_PTO | PTO:.UPS[1].IzhodMocL3
PTOUPS1NapetostBaterije | REAL | IOD_PTO | PTO:.UPS[1].NapetostBaterije
PTOUPS1TemperaturaBaterije | REAL | IOD_PTO | PTO:.UPS[1].TemperaturaBaterije
PTOUPS1VhodFrekvencaL1 | REAL | IOD_PTO | PTO:.UPS[1].VhodFrekvencaL1
PTOUPS1VhodFrekvencaL2 | REAL | IOD_PTO | PTO:.UPS[1].VhodFrekvencaL2
PTOUPS1VhodFrekvencaL3 | REAL | IOD_PTO | PTO:.UPS[1].VhodFrekvencaL3
PTOUPS1VhodNapetostL1 | REAL | IOD_PTO | PTO:.UPS[1].VhodNapetostL1
PTOUPS1VhodNapetostL2 | REAL | IOD_PTO | PTO:.UPS[1].VhodNapetostL2
PTOUPS1VhodNapetostL3 | REAL | IOD_PTO | PTO:.UPS[1].VhodNapetostL3
PTOUPS2EstimatedChargeRemaining | REAL | IOD_PTO | PTO:.UPS[2].EstimatedChargeRemaining
PTOUPS2EstimatedMinutesRemaining | REAL | IOD_PTO | PTO:.UPS[2].EstimatedMinutesRemaining
PTOUPS2IzhodMocL1 | REAL | IOD_PTO | PTO:.UPS[2].IzhodMocL1
PTOUPS2IzhodMocL2 | REAL | IOD_PTO | PTO:.UPS[2].IzhodMocL2
PTOUPS2IzhodMocL3 | REAL | IOD_PTO | PTO:.UPS[2].IzhodMocL3
PTOUPS2NapetostBaterije | REAL | IOD_PTO | PTO:.UPS[2].NapetostBaterije
PTOUPS2TemperaturaBaterije | REAL | IOD_PTO | PTO:.UPS[2].TemperaturaBaterije
PTOUPS2VhodFrekvencaL1 | REAL | IOD_PTO | PTO:.UPS[2].VhodFrekvencaL1
PTOUPS2VhodFrekvencaL2 | REAL | IOD_PTO | PTO:.UPS[2].VhodFrekvencaL2
PTOUPS2VhodFrekvencaL3 | REAL | IOD_PTO | PTO:.UPS[2].VhodFrekvencaL3
PTOUPS2VhodNapetostL1 | REAL | IOD_PTO | PTO:.UPS[2].VhodNapetostL1
PTOUPS2VhodNapetostL2 | REAL | IOD_PTO | PTO:.UPS[2].VhodNapetostL2
PTOUPS2VhodNapetostL3 | REAL | IOD_PTO | PTO:.UPS[2].VhodNapetostL3
PTOVlagaPovp1 | REAL | IOD_PTO | PTO:.VlagaPovp[1]
PTOVlagaPovp2 | REAL | IOD_PTO | PTO:.VlagaPovp[2]
PTOVlagaPovp3 | REAL | IOD_PTO | PTO:.VlagaPovp[3]
PTORazlikaUr | REAL | IOD_PTO | PTO:.RazlikaUr
PTOKlima1NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[1].NastTempHlajenje
PTOKlima2NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[2].NastTempHlajenje
PTOKlima3NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[3].NastTempHlajenje
PTOKlima4NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[4].NastTempHlajenje
PTOKlima5NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[5].NastTempHlajenje
PTOKlima6NastTempHlajenje | REAL | IOD_PTO | PTO:.Klima[6].NastTempHlajenje
PTOKlima1NastTempGretje | REAL | IOD_PTO | PTO:.Klima[1].NastTempGretje
PTOKlima2NastTempGretje | REAL | IOD_PTO | PTO:.Klima[2].NastTempGretje
PTOKlima3NastTempGretje | REAL | IOD_PTO | PTO:.Klima[3].NastTempGretje
PTOKlima4NastTempGretje | REAL | IOD_PTO | PTO:.Klima[4].NastTempGretje
PTOKlima5NastTempGretje | REAL | IOD_PTO | PTO:.Klima[5].NastTempGretje
PTOKlima6NastTempGretje | REAL | IOD_PTO | PTO:.Klima[6].NastTempGretje
PTOKlima1TempHladneVode | REAL | IOD_PTO | PTO:.Klima[1].TempHladneVode
PTOKlima2TempHladneVode | REAL | IOD_PTO | PTO:.Klima[2].TempHladneVode
PTOKlima3TempHladneVode | REAL | IOD_PTO | PTO:.Klima[3].TempHladneVode
PTOKlima4TempHladneVode | REAL | IOD_PTO | PTO:.Klima[4].TempHladneVode
PTOKlima5TempHladneVode | REAL | IOD_PTO | PTO:.Klima[5].TempHladneVode
PTOKlima6TempHladneVode | REAL | IOD_PTO | PTO:.Klima[6].TempHladneVode
PTOKlima1TempTopleVode | REAL | IOD_PTO | PTO:.Klima[1].TempTopleVode
PTOKlima2TempTopleVode | REAL | IOD_PTO | PTO:.Klima[2].TempTopleVode
PTOKlima3TempTopleVode | REAL | IOD_PTO | PTO:.Klima[3].TempTopleVode
PTOKlima4TempTopleVode | REAL | IOD_PTO | PTO:.Klima[4].TempTopleVode
PTOKlima5TempTopleVode | REAL | IOD_PTO | PTO:.Klima[5].TempTopleVode
PTOKlima6TempTopleVode | REAL | IOD_PTO | PTO:.Klima[6].TempTopleVode
PTOZamikVklopa | REAL | IOD_PTO | PTO:.ZamikVklopa
PTODate_Time0 | STRING | IOD_PTO | PTO:.Date_Time[0]
PTODate_Time1 | STRING | IOD_PTO | PTO:.Date_Time[1]
PTODate_Time2 | STRING | IOD_PTO | PTO:.Date_Time[2]
PTODate_Time3 | STRING | IOD_PTO | PTO:.Date_Time[3]
PTOUserCurrentName | STRING | IOD_PTO | PTO:.UserCurrentName
PTOkom_nast_cas_izpada | UINT | IOD_PTO | PTO:.kom_nast_cas_izpada

## variable_3
PTOAlarmGenComm | DIGITAL | IOD_PTO_TCP | 1 | 00001 | AlarmGenComm
PTOAlarmGenKlima1 | DIGITAL | IOD_PTO_TCP | 2 | 00002 | AlarmGenKlima[1]
PTOAlarmGenKlima2 | DIGITAL | IOD_PTO_TCP | 3 | 00003 | AlarmGenKlima[2]
PTOAlarmGenKlima3 | DIGITAL | IOD_PTO_TCP | 4 | 00004 | AlarmGenKlima[3]
PTOAlarmGenKlima4 | DIGITAL | IOD_PTO_TCP | 5 | 00005 | AlarmGenKlima[4]
PTOAlarmGenKlima5 | DIGITAL | IOD_PTO_TCP | 6 | 00006 | AlarmGenKlima[5]
PTOAlarmGenKlima6 | DIGITAL | IOD_PTO_TCP | 7 | 00007 | AlarmGenKlima[6]
PTOAlarmGenPMM | DIGITAL | IOD_PTO_TCP | 8 | 00008 | AlarmGenPMM
PTOAlarmGenRest | DIGITAL | IOD_PTO_TCP | 9 | 00009 | AlarmGenRest
PTOAlarmGenSenzor | DIGITAL | IOD_PTO_TCP | 10 | 00010 | AlarmGenSenzor
PTOAlarmGenStikala | DIGITAL | IOD_PTO_TCP | 11 | 00011 | AlarmGenStikala
PTOAlarmGenTemp | DIGITAL | IOD_PTO_TCP | 12 | 00012 | AlarmGenTemp
PTOAlarmGenUPS1 | DIGITAL | IOD_PTO_TCP | 13 | 00013 | AlarmGenUPS1
PTOAlarmGenUPS2 | DIGITAL | IOD_PTO_TCP | 14 | 00014 | AlarmGenUPS2
PTOComSCADA | DIGITAL | IOD_PTO_TCP | 15 | 00015 | ComSCADA
PTOComSCADA1 | DIGITAL | IOD_PTO_TCP | 16 | 00016 | ComSCADA1
PTODI_A1Q01_DovUpsA_ON | DIGITAL | IOD_PTO_TCP | 17 | 00017 | DI_A1Q01_DovUpsA_ON
PTODI_A1Q02_DovByA_ON | DIGITAL | IOD_PTO_TCP | 18 | 00018 | DI_A1Q02_DovByA_ON
PTODI_A1Q0_GlavnoSti_ON | DIGITAL | IOD_PTO_TCP | 19 | 00019 | DI_A1Q0_GlavnoSti_ON
PTODI_A1Q11_OdcUpsA_IZP | DIGITAL | IOD_PTO_TCP | 20 | 00020 | DI_A1Q11_OdcUpsA_IZP
PTODI_A1Q11_OdcUpsA_ON | DIGITAL | IOD_PTO_TCP | 21 | 00021 | DI_A1Q11_OdcUpsA_ON
PTODI_A1Q12_OdcByUpsA_IZP | DIGITAL | IOD_PTO_TCP | 22 | 00022 | DI_A1Q12_OdcByUpsA_IZP
PTODI_A1Q12_OdcByUpsA_ON | DIGITAL | IOD_PTO_TCP | 23 | 00023 | DI_A1Q12_OdcByUpsA_ON
PTODI_A1Q13_OdcByA_IZP | DIGITAL | IOD_PTO_TCP | 24 | 00024 | DI_A1Q13_OdcByA_IZP
PTODI_A1Q13_OdcByA_ON | DIGITAL | IOD_PTO_TCP | 25 | 00025 | DI_A1Q13_OdcByA_ON
PTODI_A2Q0_GlavnoSti_ON | DIGITAL | IOD_PTO_TCP | 26 | 00026 | DI_A2Q0_GlavnoSti_ON
PTODI_F201_OdcKl1ZE_IZP | DIGITAL | IOD_PTO_TCP | 27 | 00027 | DI_F201_OdcKl1ZE_IZP
PTODI_F201_OdcKl1ZE_ON | DIGITAL | IOD_PTO_TCP | 28 | 00028 | DI_F201_OdcKl1ZE_ON
PTODI_F202_OdcKl2ZE_IZP | DIGITAL | IOD_PTO_TCP | 29 | 00029 | DI_F202_OdcKl2ZE_IZP
PTODI_F202_OdcKl2ZE_ON | DIGITAL | IOD_PTO_TCP | 30 | 00030 | DI_F202_OdcKl2ZE_ON
PTODI_F203_OdcKl3ZE_IZP | DIGITAL | IOD_PTO_TCP | 31 | 00031 | DI_F203_OdcKl3ZE_IZP
PTODI_F203_OdcKl3ZE_ON | DIGITAL | IOD_PTO_TCP | 32 | 00032 | DI_F203_OdcKl3ZE_ON
PTODI_F204_OdcKl4ZE_IZP | DIGITAL | IOD_PTO_TCP | 33 | 00033 | DI_F204_OdcKl4ZE_IZP
PTODI_F204_OdcKl4ZE_ON | DIGITAL | IOD_PTO_TCP | 34 | 00034 | DI_F204_OdcKl4ZE_ON
PTODI_F205_OdcKl5aZE_IZP | DIGITAL | IOD_PTO_TCP | 35 | 00035 | DI_F205_OdcKl5aZE_IZP
PTODI_F205_OdcKl5aZE_ON | DIGITAL | IOD_PTO_TCP | 36 | 00036 | DI_F205_OdcKl5aZE_ON
PTODI_F206_OdcKl5bZE_IZP | DIGITAL | IOD_PTO_TCP | 37 | 00037 | DI_F206_OdcKl5bZE_IZP
PTODI_F206_OdcKl5bZE_ON | DIGITAL | IOD_PTO_TCP | 38 | 00038 | DI_F206_OdcKl5bZE_ON
PTODI_F207_OdcKl6aZE_IZP | DIGITAL | IOD_PTO_TCP | 39 | 00039 | DI_F207_OdcKl6aZE_IZP
PTODI_F207_OdcKl6aZE_ON | DIGITAL | IOD_PTO_TCP | 40 | 00040 | DI_F207_OdcKl6aZE_ON
PTODI_F208_OdcKl6bZE_IZP | DIGITAL | IOD_PTO_TCP | 41 | 00041 | DI_F208_OdcKl6bZE_IZP
PTODI_F208_OdcKl6bZE_ON | DIGITAL | IOD_PTO_TCP | 42 | 00042 | DI_F208_OdcKl6bZE_ON
PTODI_IzpadMreze | DIGITAL | IOD_PTO_TCP | 43 | 00043 | DI_IzpadMreze
PTODI_Klima1_ERR | DIGITAL | IOD_PTO_TCP | 44 | 00044 | DI_Klima1_ERR
PTODI_Klima1_ON | DIGITAL | IOD_PTO_TCP | 45 | 00045 | DI_Klima1_ON
PTODI_Klima2_ERR | DIGITAL | IOD_PTO_TCP | 46 | 00046 | DI_Klima2_ERR
PTODI_Klima2_ON | DIGITAL | IOD_PTO_TCP | 47 | 00047 | DI_Klima2_ON
PTODI_Klima3_ERR | DIGITAL | IOD_PTO_TCP | 48 | 00048 | DI_Klima3_ERR
PTODI_Klima3_ON | DIGITAL | IOD_PTO_TCP | 49 | 00049 | DI_Klima3_ON
PTODI_Klima4_ERR | DIGITAL | IOD_PTO_TCP | 50 | 00050 | DI_Klima4_ERR
PTODI_Klima4_ON | DIGITAL | IOD_PTO_TCP | 51 | 00051 | DI_Klima4_ON
PTODI_Klima5_ERR | DIGITAL | IOD_PTO_TCP | 52 | 00052 | DI_Klima5_ERR
PTODI_Klima5_ON | DIGITAL | IOD_PTO_TCP | 53 | 00053 | DI_Klima5_ON
PTODI_Klima6_ERR | DIGITAL | IOD_PTO_TCP | 54 | 00054 | DI_Klima6_ERR
PTODI_Klima6_ON | DIGITAL | IOD_PTO_TCP | 55 | 00055 | DI_Klima6_ON
PTODI_KlimaSplitPP_ERR | DIGITAL | IOD_PTO_TCP | 56 | 00056 | DI_KlimaSplitPP_ERR
PTODI_KlimaSplitPP_ON | DIGITAL | IOD_PTO_TCP | 57 | 00057 | DI_KlimaSplitPP_ON
PTODI_PrenapA1_OK | DIGITAL | IOD_PTO_TCP | 58 | 00058 | DI_PrenapA1_OK
PTODI_PrenapA2_OK | DIGITAL | IOD_PTO_TCP | 59 | 00059 | DI_PrenapA2_OK
PTODI_Q101_OdcKlima1_IZP | DIGITAL | IOD_PTO_TCP | 60 | 00060 | DI_Q101_OdcKlima1_IZP
PTODI_Q101_OdcKlima1_ON | DIGITAL | IOD_PTO_TCP | 61 | 00061 | DI_Q101_OdcKlima1_ON
PTODI_Q102_OdcKlima2_IZP | DIGITAL | IOD_PTO_TCP | 62 | 00062 | DI_Q102_OdcKlima2_IZP
PTODI_Q102_OdcKlima2_ON | DIGITAL | IOD_PTO_TCP | 63 | 00063 | DI_Q102_OdcKlima2_ON
PTODI_Q103_OdcKlima3_IZP | DIGITAL | IOD_PTO_TCP | 64 | 00064 | DI_Q103_OdcKlima3_IZP
PTODI_Q103_OdcKlima3_ON | DIGITAL | IOD_PTO_TCP | 65 | 00065 | DI_Q103_OdcKlima3_ON
PTODI_Q104_OdcKlima4_IZP | DIGITAL | IOD_PTO_TCP | 66 | 00066 | DI_Q104_OdcKlima4_IZP
PTODI_Q104_OdcKlima4_ON | DIGITAL | IOD_PTO_TCP | 67 | 00067 | DI_Q104_OdcKlima4_ON
PTODI_Q105_OdcKlima5_IZP | DIGITAL | IOD_PTO_TCP | 68 | 00068 | DI_Q105_OdcKlima5_IZP
PTODI_Q105_OdcKlima5_ON | DIGITAL | IOD_PTO_TCP | 69 | 00069 | DI_Q105_OdcKlima5_ON
PTODI_Q106_OdcKlima6_IZP | DIGITAL | IOD_PTO_TCP | 70 | 00070 | DI_Q106_OdcKlima6_IZP
PTODI_Q106_OdcKlima6_ON | DIGITAL | IOD_PTO_TCP | 71 | 00071 | DI_Q106_OdcKlima6_ON
PTODI_Q107_OdcUsmSS2_IZP | DIGITAL | IOD_PTO_TCP | 72 | 00072 | DI_Q107_OdcUsmSS2_IZP
PTODI_Q107_OdcUsmSS2_ON | DIGITAL | IOD_PTO_TCP | 73 | 00073 | DI_Q107_OdcUsmSS2_ON
PTODI_Q108_OdcUsmSS3_IZP | DIGITAL | IOD_PTO_TCP | 74 | 00074 | DI_Q108_OdcUsmSS3_IZP
PTODI_Q108_OdcUsmSS3_ON | DIGITAL | IOD_PTO_TCP | 75 | 00075 | DI_Q108_OdcUsmSS3_ON
PTODI_RazlitjeVodeK1K2 | DIGITAL | IOD_PTO_TCP | 76 | 00076 | DI_RazlitjeVodeK1K2
PTODI_RazlitjeVodeK3K4 | DIGITAL | IOD_PTO_TCP | 77 | 00077 | DI_RazlitjeVodeK3K4
PTODI_RazlitjeVodeK5 | DIGITAL | IOD_PTO_TCP | 78 | 00078 | DI_RazlitjeVodeK5
PTODI_RazlitjeVodeK6 | DIGITAL | IOD_PTO_TCP | 79 | 00079 | DI_RazlitjeVodeK6
PTODI_UPS_Alarm | DIGITAL | IOD_PTO_TCP | 80 | 00080 | DI_UPS_Alarm
PTODI_UPS_BatNacin | DIGITAL | IOD_PTO_TCP | 81 | 00081 | DI_UPS_BatNacin
PTODI_UPS_Polnjenje | DIGITAL | IOD_PTO_TCP | 82 | 00082 | DI_UPS_Polnjenje
PTODI_UpsA_BypassON | DIGITAL | IOD_PTO_TCP | 83 | 00083 | DI_UpsA_BypassON
PTODI_UpsA_ERR | DIGITAL | IOD_PTO_TCP | 84 | 00084 | DI_UpsA_ERR
PTODI_UpsB_BypassON | DIGITAL | IOD_PTO_TCP | 85 | 00085 | DI_UpsB_BypassON
PTODI_UpsB_ERR | DIGITAL | IOD_PTO_TCP | 86 | 00086 | DI_UpsB_ERR
PTODI_UQ11_OdcPMM_IZP | DIGITAL | IOD_PTO_TCP | 87 | 00087 | DI_UQ11_OdcPMM_IZP
PTODI_UQ11_OdcPMM_ON | DIGITAL | IOD_PTO_TCP | 88 | 00088 | DI_UQ11_OdcPMM_ON
PTODI_UQ12_OdcPMM_IZP | DIGITAL | IOD_PTO_TCP | 89 | 00089 | DI_UQ12_OdcPMM_IZP
PTODI_UQ12_OdcPMM_ON | DIGITAL | IOD_PTO_TCP | 90 | 00090 | DI_UQ12_OdcPMM_ON
PTODIN_A1Q11_OdcUpsA_IZP | DIGITAL | IOD_PTO_TCP | 91 | 00091 | DIN_A1Q11_OdcUpsA_IZP
PTODIN_A1Q12_OdcByUpsA_IZP | DIGITAL | IOD_PTO_TCP | 92 | 00092 | DIN_A1Q12_OdcByUpsA_IZP
PTODIN_A1Q13_OdcByA_IZP | DIGITAL | IOD_PTO_TCP | 93 | 00093 | DIN_A1Q13_OdcByA_IZP
PTODIN_F201_OdcKl1ZE_IZP | DIGITAL | IOD_PTO_TCP | 94 | 00094 | DIN_F201_OdcKl1ZE_IZP
PTODIN_F202_OdcKl2ZE_IZP | DIGITAL | IOD_PTO_TCP | 95 | 00095 | DIN_F202_OdcKl2ZE_IZP
PTODIN_F203_OdcKl3ZE_IZP | DIGITAL | IOD_PTO_TCP | 96 | 00096 | DIN_F203_OdcKl3ZE_IZP
PTODIN_F204_OdcKl4ZE_IZP | DIGITAL | IOD_PTO_TCP | 97 | 00097 | DIN_F204_OdcKl4ZE_IZP
PTODIN_F205_OdcKl5aZE_IZP | DIGITAL | IOD_PTO_TCP | 98 | 00098 | DIN_F205_OdcKl5aZE_IZP
PTODIN_F206_OdcKl5bZE_IZP | DIGITAL | IOD_PTO_TCP | 99 | 00099 | DIN_F206_OdcKl5bZE_IZP
PTODIN_F207_OdcKl6aZE_IZP | DIGITAL | IOD_PTO_TCP | 100 | 00100 | DIN_F207_OdcKl6aZE_IZP
PTODIN_F208_OdcKl6bZE_IZP | DIGITAL | IOD_PTO_TCP | 101 | 00101 | DIN_F208_OdcKl6bZE_IZP
PTODIN_Klima1_ERR | DIGITAL | IOD_PTO_TCP | 102 | 00102 | DIN_Klima1_ERR
PTODIN_Klima2_ERR | DIGITAL | IOD_PTO_TCP | 103 | 00103 | DIN_Klima2_ERR
PTODIN_Klima3_ERR | DIGITAL | IOD_PTO_TCP | 104 | 00104 | DIN_Klima3_ERR
PTODIN_Klima4_ERR | DIGITAL | IOD_PTO_TCP | 105 | 00105 | DIN_Klima4_ERR
PTODIN_Klima5_ERR | DIGITAL | IOD_PTO_TCP | 106 | 00106 | DIN_Klima5_ERR
PTODIN_Klima6_ERR | DIGITAL | IOD_PTO_TCP | 107 | 00107 | DIN_Klima6_ERR
PTODIN_KlimaSplitPP_ERR | DIGITAL | IOD_PTO_TCP | 108 | 00108 | DIN_KlimaSplitPP_ERR
PTODIN_PrenapA1_OK | DIGITAL | IOD_PTO_TCP | 109 | 00109 | DIN_PrenapA1_OK
PTODIN_PrenapA2_OK | DIGITAL | IOD_PTO_TCP | 110 | 00110 | DIN_PrenapA2_OK
PTODIN_Q101_OdcKlima1_IZP | DIGITAL | IOD_PTO_TCP | 111 | 00111 | DIN_Q101_OdcKlima1_IZP
PTODIN_Q102_OdcKlima2_IZP | DIGITAL | IOD_PTO_TCP | 112 | 00112 | DIN_Q102_OdcKlima2_IZP
PTODIN_Q103_OdcKlima3_IZP | DIGITAL | IOD_PTO_TCP | 113 | 00113 | DIN_Q103_OdcKlima3_IZP
PTODIN_Q104_OdcKlima4_IZP | DIGITAL | IOD_PTO_TCP | 114 | 00114 | DIN_Q104_OdcKlima4_IZP
PTODIN_Q105_OdcKlima5_IZP | DIGITAL | IOD_PTO_TCP | 115 | 00115 | DIN_Q105_OdcKlima5_IZP
PTODIN_Q106_OdcKlima6_IZP | DIGITAL | IOD_PTO_TCP | 116 | 00116 | DIN_Q106_OdcKlima6_IZP
PTODIN_Q107_OdcUsmSS2_IZP | DIGITAL | IOD_PTO_TCP | 117 | 00117 | DIN_Q107_OdcUsmSS2_IZP
PTODIN_Q108_OdcUsmSS3_IZP | DIGITAL | IOD_PTO_TCP | 118 | 00118 | DIN_Q108_OdcUsmSS3_IZP
PTODIN_UpsA_BypassON | DIGITAL | IOD_PTO_TCP | 119 | 00119 | DIN_UpsA_BypassON
PTODIN_UpsA_ERR | DIGITAL | IOD_PTO_TCP | 120 | 00120 | DIN_UpsA_ERR
PTODIN_UpsB_BypassON | DIGITAL | IOD_PTO_TCP | 121 | 00121 | DIN_UpsB_BypassON
PTODIN_UpsB_ERR | DIGITAL | IOD_PTO_TCP | 122 | 00122 | DIN_UpsB_ERR
PTODIN_UQ11_OdcPMM_IZP | DIGITAL | IOD_PTO_TCP | 123 | 00123 | DIN_UQ11_OdcPMM_IZP
PTODIN_UQ12_OdcPMM_IZP | DIGITAL | IOD_PTO_TCP | 124 | 00124 | DIN_UQ12_OdcPMM_IZP
PTODO_Klima1_Izklop | DIGITAL | IOD_PTO_TCP | 125 | 00125 | DO_Klima1_Izklop
PTODO_Klima2_Izklop | DIGITAL | IOD_PTO_TCP | 126 | 00126 | DO_Klima2_Izklop
PTODO_Klima3_Izklop | DIGITAL | IOD_PTO_TCP | 127 | 00127 | DO_Klima3_Izklop
PTODO_Klima4_Izklop | DIGITAL | IOD_PTO_TCP | 128 | 00128 | DO_Klima4_Izklop
PTODO_Klima5_Izklop | DIGITAL | IOD_PTO_TCP | 129 | 00129 | DO_Klima5_Izklop
PTODO_Klima6_Izklop | DIGITAL | IOD_PTO_TCP | 130 | 00130 | DO_Klima6_Izklop
PTOErrComKlima1 | DIGITAL | IOD_PTO_TCP | 131 | 00131 | ErrComKlima[1]
PTOErrComKlima2 | DIGITAL | IOD_PTO_TCP | 132 | 00132 | ErrComKlima[2]
PTOErrComKlima3 | DIGITAL | IOD_PTO_TCP | 133 | 00133 | ErrComKlima[3]
PTOErrComKlima4 | DIGITAL | IOD_PTO_TCP | 134 | 00134 | ErrComKlima[4]
PTOErrComKlima5 | DIGITAL | IOD_PTO_TCP | 135 | 00135 | ErrComKlima[5]
PTOErrComKlima6 | DIGITAL | IOD_PTO_TCP | 136 | 00136 | ErrComKlima[6]
PTOErrCommScada | DIGITAL | IOD_PTO_TCP | 137 | 00137 | ErrCommScada
PTOErrComPanelPLC | DIGITAL | IOD_PTO_TCP | 138 | 00138 | ErrComPanelPLC
PTOErrComPMM | DIGITAL | IOD_PTO_TCP | 139 | 00139 | ErrComPMM
PTOErrComPort2 | DIGITAL | IOD_PTO_TCP | 140 | 00140 | ErrComPort2
PTOErrComPort3 | DIGITAL | IOD_PTO_TCP | 141 | 00141 | ErrComPort3
PTOErrComPort4 | DIGITAL | IOD_PTO_TCP | 142 | 00142 | ErrComPort4
PTOErrComUPS1 | DIGITAL | IOD_PTO_TCP | 143 | 00143 | ErrComUPS[1]
PTOErrComUPS2 | DIGITAL | IOD_PTO_TCP | 144 | 00144 | ErrComUPS[2]
PTOErrorComKlima1Error | DIGITAL | IOD_PTO_TCP | 145 | 00145 | ErrorComKlima[1].Error
PTOErrorComKlima2Error | DIGITAL | IOD_PTO_TCP | 146 | 00146 | ErrorComKlima[2].Error
PTOErrorComKlima3Error | DIGITAL | IOD_PTO_TCP | 147 | 00147 | ErrorComKlima[3].Error
PTOErrorComKlima4Error | DIGITAL | IOD_PTO_TCP | 148 | 00148 | ErrorComKlima[4].Error
PTOErrorComKlima5Error | DIGITAL | IOD_PTO_TCP | 149 | 00149 | ErrorComKlima[5].Error
PTOErrorComKlima6Error | DIGITAL | IOD_PTO_TCP | 150 | 00150 | ErrorComKlima[6].Error
PTOErrorComPMMError | DIGITAL | IOD_PTO_TCP | 151 | 00151 | ErrorComPMM.Error
PTOErrorComUPS1Error | DIGITAL | IOD_PTO_TCP | 152 | 00152 | ErrorComUPS[1].Error
PTOErrorComUPS2Error | DIGITAL | IOD_PTO_TCP | 153 | 00153 | ErrorComUPS[2].Error
PTOKlima1Errors10 | DIGITAL | IOD_PTO_TCP | 154 | 00154 | Klima1Errors[10]
PTOKlima1Errors11 | DIGITAL | IOD_PTO_TCP | 155 | 00155 | Klima1Errors[11]
PTOKlima1Errors12 | DIGITAL | IOD_PTO_TCP | 156 | 00156 | Klima1Errors[12]
PTOKlima1Errors13 | DIGITAL | IOD_PTO_TCP | 157 | 00157 | Klima1Errors[13]
PTOKlima1Errors14 | DIGITAL | IOD_PTO_TCP | 158 | 00158 | Klima1Errors[14]
PTOKlima1Errors15 | DIGITAL | IOD_PTO_TCP | 159 | 00159 | Klima1Errors[15]
PTOKlima1Errors16 | DIGITAL | IOD_PTO_TCP | 160 | 00160 | Klima1Errors[16]
PTOKlima1Errors17 | DIGITAL | IOD_PTO_TCP | 161 | 00161 | Klima1Errors[17]
PTOKlima1Errors18 | DIGITAL | IOD_PTO_TCP | 162 | 00162 | Klima1Errors[18]
PTOKlima1Errors19 | DIGITAL | IOD_PTO_TCP | 163 | 00163 | Klima1Errors[19]
PTOKlima1Errors1 | DIGITAL | IOD_PTO_TCP | 164 | 00164 | Klima1Errors[1]
PTOKlima1Errors20 | DIGITAL | IOD_PTO_TCP | 165 | 00165 | Klima1Errors[20]
PTOKlima1Errors21 | DIGITAL | IOD_PTO_TCP | 166 | 00166 | Klima1Errors[21]
PTOKlima1Errors22 | DIGITAL | IOD_PTO_TCP | 167 | 00167 | Klima1Errors[22]
PTOKlima1Errors23 | DIGITAL | IOD_PTO_TCP | 168 | 00168 | Klima1Errors[23]
PTOKlima1Errors24 | DIGITAL | IOD_PTO_TCP | 169 | 00169 | Klima1Errors[24]
PTOKlima1Errors25 | DIGITAL | IOD_PTO_TCP | 170 | 00170 | Klima1Errors[25]
PTOKlima1Errors26 | DIGITAL | IOD_PTO_TCP | 171 | 00171 | Klima1Errors[26]
PTOKlima1Errors27 | DIGITAL | IOD_PTO_TCP | 172 | 00172 | Klima1Errors[27]
PTOKlima1Errors28 | DIGITAL | IOD_PTO_TCP | 173 | 00173 | Klima1Errors[28]
PTOKlima1Errors29 | DIGITAL | IOD_PTO_TCP | 174 | 00174 | Klima1Errors[29]
PTOKlima1Errors2 | DIGITAL | IOD_PTO_TCP | 175 | 00175 | Klima1Errors[2]
PTOKlima1Errors30 | DIGITAL | IOD_PTO_TCP | 176 | 00176 | Klima1Errors[30]
PTOKlima1Errors31 | DIGITAL | IOD_PTO_TCP | 177 | 00177 | Klima1Errors[31]
PTOKlima1Errors32 | DIGITAL | IOD_PTO_TCP | 178 | 00178 | Klima1Errors[32]
PTOKlima1Errors33 | DIGITAL | IOD_PTO_TCP | 179 | 00179 | Klima1Errors[33]
PTOKlima1Errors34 | DIGITAL | IOD_PTO_TCP | 180 | 00180 | Klima1Errors[34]
PTOKlima1Errors35 | DIGITAL | IOD_PTO_TCP | 181 | 00181 | Klima1Errors[35]
PTOKlima1Errors3 | DIGITAL | IOD_PTO_TCP | 182 | 00182 | Klima1Errors[3]
PTOKlima1Errors4 | DIGITAL | IOD_PTO_TCP | 183 | 00183 | Klima1Errors[4]
PTOKlima1Errors5 | DIGITAL | IOD_PTO_TCP | 184 | 00184 | Klima1Errors[5]
PTOKlima1Errors6 | DIGITAL | IOD_PTO_TCP | 185 | 00185 | Klima1Errors[6]
PTOKlima1Errors7 | DIGITAL | IOD_PTO_TCP | 186 | 00186 | Klima1Errors[7]
PTOKlima1Errors8 | DIGITAL | IOD_PTO_TCP | 187 | 00187 | Klima1Errors[8]
PTOKlima1Errors9 | DIGITAL | IOD_PTO_TCP | 188 | 00188 | Klima1Errors[9]
PTOKlima2Errors10 | DIGITAL | IOD_PTO_TCP | 189 | 00189 | Klima2Errors[10]
PTOKlima2Errors11 | DIGITAL | IOD_PTO_TCP | 190 | 00190 | Klima2Errors[11]
PTOKlima2Errors12 | DIGITAL | IOD_PTO_TCP | 191 | 00191 | Klima2Errors[12]
PTOKlima2Errors13 | DIGITAL | IOD_PTO_TCP | 192 | 00192 | Klima2Errors[13]
PTOKlima2Errors14 | DIGITAL | IOD_PTO_TCP | 193 | 00193 | Klima2Errors[14]
PTOKlima2Errors15 | DIGITAL | IOD_PTO_TCP | 194 | 00194 | Klima2Errors[15]
PTOKlima2Errors16 | DIGITAL | IOD_PTO_TCP | 195 | 00195 | Klima2Errors[16]
PTOKlima2Errors17 | DIGITAL | IOD_PTO_TCP | 196 | 00196 | Klima2Errors[17]
PTOKlima2Errors18 | DIGITAL | IOD_PTO_TCP | 197 | 00197 | Klima2Errors[18]
PTOKlima2Errors19 | DIGITAL | IOD_PTO_TCP | 198 | 00198 | Klima2Errors[19]
PTOKlima2Errors1 | DIGITAL | IOD_PTO_TCP | 199 | 00199 | Klima2Errors[1]
PTOKlima2Errors20 | DIGITAL | IOD_PTO_TCP | 200 | 00200 | Klima2Errors[20]
PTOKlima2Errors21 | DIGITAL | IOD_PTO_TCP | 201 | 00201 | Klima2Errors[21]
PTOKlima2Errors22 | DIGITAL | IOD_PTO_TCP | 202 | 00202 | Klima2Errors[22]
PTOKlima2Errors23 | DIGITAL | IOD_PTO_TCP | 203 | 00203 | Klima2Errors[23]
PTOKlima2Errors24 | DIGITAL | IOD_PTO_TCP | 204 | 00204 | Klima2Errors[24]
PTOKlima2Errors25 | DIGITAL | IOD_PTO_TCP | 205 | 00205 | Klima2Errors[25]
PTOKlima2Errors26 | DIGITAL | IOD_PTO_TCP | 206 | 00206 | Klima2Errors[26]
PTOKlima2Errors27 | DIGITAL | IOD_PTO_TCP | 207 | 00207 | Klima2Errors[27]
PTOKlima2Errors28 | DIGITAL | IOD_PTO_TCP | 208 | 00208 | Klima2Errors[28]
PTOKlima2Errors29 | DIGITAL | IOD_PTO_TCP | 209 | 00209 | Klima2Errors[29]
PTOKlima2Errors2 | DIGITAL | IOD_PTO_TCP | 210 | 00210 | Klima2Errors[2]
PTOKlima2Errors30 | DIGITAL | IOD_PTO_TCP | 211 | 00211 | Klima2Errors[30]
PTOKlima2Errors31 | DIGITAL | IOD_PTO_TCP | 212 | 00212 | Klima2Errors[31]
PTOKlima2Errors32 | DIGITAL | IOD_PTO_TCP | 213 | 00213 | Klima2Errors[32]
PTOKlima2Errors33 | DIGITAL | IOD_PTO_TCP | 214 | 00214 | Klima2Errors[33]
PTOKlima2Errors34 | DIGITAL | IOD_PTO_TCP | 215 | 00215 | Klima2Errors[34]
PTOKlima2Errors35 | DIGITAL | IOD_PTO_TCP | 216 | 00216 | Klima2Errors[35]
PTOKlima2Errors3 | DIGITAL | IOD_PTO_TCP | 217 | 00217 | Klima2Errors[3]
PTOKlima2Errors4 | DIGITAL | IOD_PTO_TCP | 218 | 00218 | Klima2Errors[4]
PTOKlima2Errors5 | DIGITAL | IOD_PTO_TCP | 219 | 00219 | Klima2Errors[5]
PTOKlima2Errors6 | DIGITAL | IOD_PTO_TCP | 220 | 00220 | Klima2Errors[6]
PTOKlima2Errors7 | DIGITAL | IOD_PTO_TCP | 221 | 00221 | Klima2Errors[7]
PTOKlima2Errors8 | DIGITAL | IOD_PTO_TCP | 222 | 00222 | Klima2Errors[8]
PTOKlima2Errors9 | DIGITAL | IOD_PTO_TCP | 223 | 00223 | Klima2Errors[9]
PTOKlima3Errors10 | DIGITAL | IOD_PTO_TCP | 224 | 00224 | Klima3Errors[10]
PTOKlima3Errors11 | DIGITAL | IOD_PTO_TCP | 225 | 00225 | Klima3Errors[11]
PTOKlima3Errors12 | DIGITAL | IOD_PTO_TCP | 226 | 00226 | Klima3Errors[12]
PTOKlima3Errors13 | DIGITAL | IOD_PTO_TCP | 227 | 00227 | Klima3Errors[13]
PTOKlima3Errors14 | DIGITAL | IOD_PTO_TCP | 228 | 00228 | Klima3Errors[14]
PTOKlima3Errors15 | DIGITAL | IOD_PTO_TCP | 229 | 00229 | Klima3Errors[15]
PTOKlima3Errors16 | DIGITAL | IOD_PTO_TCP | 230 | 00230 | Klima3Errors[16]
PTOKlima3Errors17 | DIGITAL | IOD_PTO_TCP | 231 | 00231 | Klima3Errors[17]
PTOKlima3Errors18 | DIGITAL | IOD_PTO_TCP | 232 | 00232 | Klima3Errors[18]
PTOKlima3Errors19 | DIGITAL | IOD_PTO_TCP | 233 | 00233 | Klima3Errors[19]
PTOKlima3Errors1 | DIGITAL | IOD_PTO_TCP | 234 | 00234 | Klima3Errors[1]
PTOKlima3Errors20 | DIGITAL | IOD_PTO_TCP | 235 | 00235 | Klima3Errors[20]
PTOKlima3Errors21 | DIGITAL | IOD_PTO_TCP | 236 | 00236 | Klima3Errors[21]
PTOKlima3Errors22 | DIGITAL | IOD_PTO_TCP | 237 | 00237 | Klima3Errors[22]
PTOKlima3Errors23 | DIGITAL | IOD_PTO_TCP | 238 | 00238 | Klima3Errors[23]
PTOKlima3Errors24 | DIGITAL | IOD_PTO_TCP | 239 | 00239 | Klima3Errors[24]
PTOKlima3Errors25 | DIGITAL | IOD_PTO_TCP | 240 | 00240 | Klima3Errors[25]
PTOKlima3Errors26 | DIGITAL | IOD_PTO_TCP | 241 | 00241 | Klima3Errors[26]
PTOKlima3Errors27 | DIGITAL | IOD_PTO_TCP | 242 | 00242 | Klima3Errors[27]
PTOKlima3Errors28 | DIGITAL | IOD_PTO_TCP | 243 | 00243 | Klima3Errors[28]
PTOKlima3Errors29 | DIGITAL | IOD_PTO_TCP | 244 | 00244 | Klima3Errors[29]
PTOKlima3Errors2 | DIGITAL | IOD_PTO_TCP | 245 | 00245 | Klima3Errors[2]
PTOKlima3Errors30 | DIGITAL | IOD_PTO_TCP | 246 | 00246 | Klima3Errors[30]
PTOKlima3Errors31 | DIGITAL | IOD_PTO_TCP | 247 | 00247 | Klima3Errors[31]
PTOKlima3Errors32 | DIGITAL | IOD_PTO_TCP | 248 | 00248 | Klima3Errors[32]
PTOKlima3Errors33 | DIGITAL | IOD_PTO_TCP | 249 | 00249 | Klima3Errors[33]
PTOKlima3Errors34 | DIGITAL | IOD_PTO_TCP | 250 | 00250 | Klima3Errors[34]
PTOKlima3Errors35 | DIGITAL | IOD_PTO_TCP | 251 | 00251 | Klima3Errors[35]
PTOKlima3Errors3 | DIGITAL | IOD_PTO_TCP | 252 | 00252 | Klima3Errors[3]
PTOKlima3Errors4 | DIGITAL | IOD_PTO_TCP | 253 | 00253 | Klima3Errors[4]
PTOKlima3Errors5 | DIGITAL | IOD_PTO_TCP | 254 | 00254 | Klima3Errors[5]
PTOKlima3Errors6 | DIGITAL | IOD_PTO_TCP | 255 | 00255 | Klima3Errors[6]
PTOKlima3Errors7 | DIGITAL | IOD_PTO_TCP | 256 | 00256 | Klima3Errors[7]
PTOKlima3Errors8 | DIGITAL | IOD_PTO_TCP | 257 | 00257 | Klima3Errors[8]
PTOKlima3Errors9 | DIGITAL | IOD_PTO_TCP | 258 | 00258 | Klima3Errors[9]
PTOKlima4Errors10 | DIGITAL | IOD_PTO_TCP | 259 | 00259 | Klima4Errors[10]
PTOKlima4Errors11 | DIGITAL | IOD_PTO_TCP | 260 | 00260 | Klima4Errors[11]
PTOKlima4Errors12 | DIGITAL | IOD_PTO_TCP | 261 | 00261 | Klima4Errors[12]
PTOKlima4Errors13 | DIGITAL | IOD_PTO_TCP | 262 | 00262 | Klima4Errors[13]
PTOKlima4Errors14 | DIGITAL | IOD_PTO_TCP | 263 | 00263 | Klima4Errors[14]
PTOKlima4Errors15 | DIGITAL | IOD_PTO_TCP | 264 | 00264 | Klima4Errors[15]
PTOKlima4Errors16 | DIGITAL | IOD_PTO_TCP | 265 | 00265 | Klima4Errors[16]
PTOKlima4Errors17 | DIGITAL | IOD_PTO_TCP | 266 | 00266 | Klima4Errors[17]
PTOKlima4Errors18 | DIGITAL | IOD_PTO_TCP | 267 | 00267 | Klima4Errors[18]
PTOKlima4Errors19 | DIGITAL | IOD_PTO_TCP | 268 | 00268 | Klima4Errors[19]
PTOKlima4Errors1 | DIGITAL | IOD_PTO_TCP | 269 | 00269 | Klima4Errors[1]
PTOKlima4Errors20 | DIGITAL | IOD_PTO_TCP | 270 | 00270 | Klima4Errors[20]
PTOKlima4Errors21 | DIGITAL | IOD_PTO_TCP | 271 | 00271 | Klima4Errors[21]
PTOKlima4Errors22 | DIGITAL | IOD_PTO_TCP | 272 | 00272 | Klima4Errors[22]
PTOKlima4Errors23 | DIGITAL | IOD_PTO_TCP | 273 | 00273 | Klima4Errors[23]
PTOKlima4Errors24 | DIGITAL | IOD_PTO_TCP | 274 | 00274 | Klima4Errors[24]
PTOKlima4Errors25 | DIGITAL | IOD_PTO_TCP | 275 | 00275 | Klima4Errors[25]
PTOKlima4Errors26 | DIGITAL | IOD_PTO_TCP | 276 | 00276 | Klima4Errors[26]
PTOKlima4Errors27 | DIGITAL | IOD_PTO_TCP | 277 | 00277 | Klima4Errors[27]
PTOKlima4Errors28 | DIGITAL | IOD_PTO_TCP | 278 | 00278 | Klima4Errors[28]
PTOKlima4Errors29 | DIGITAL | IOD_PTO_TCP | 279 | 00279 | Klima4Errors[29]
PTOKlima4Errors2 | DIGITAL | IOD_PTO_TCP | 280 | 00280 | Klima4Errors[2]
PTOKlima4Errors30 | DIGITAL | IOD_PTO_TCP | 281 | 00281 | Klima4Errors[30]
PTOKlima4Errors31 | DIGITAL | IOD_PTO_TCP | 282 | 00282 | Klima4Errors[31]
PTOKlima4Errors32 | DIGITAL | IOD_PTO_TCP | 283 | 00283 | Klima4Errors[32]
PTOKlima4Errors33 | DIGITAL | IOD_PTO_TCP | 284 | 00284 | Klima4Errors[33]
PTOKlima4Errors34 | DIGITAL | IOD_PTO_TCP | 285 | 00285 | Klima4Errors[34]
PTOKlima4Errors35 | DIGITAL | IOD_PTO_TCP | 286 | 00286 | Klima4Errors[35]
PTOKlima4Errors3 | DIGITAL | IOD_PTO_TCP | 287 | 00287 | Klima4Errors[3]
PTOKlima4Errors4 | DIGITAL | IOD_PTO_TCP | 288 | 00288 | Klima4Errors[4]
PTOKlima4Errors5 | DIGITAL | IOD_PTO_TCP | 289 | 00289 | Klima4Errors[5]
PTOKlima4Errors6 | DIGITAL | IOD_PTO_TCP | 290 | 00290 | Klima4Errors[6]
PTOKlima4Errors7 | DIGITAL | IOD_PTO_TCP | 291 | 00291 | Klima4Errors[7]
PTOKlima4Errors8 | DIGITAL | IOD_PTO_TCP | 292 | 00292 | Klima4Errors[8]
PTOKlima4Errors9 | DIGITAL | IOD_PTO_TCP | 293 | 00293 | Klima4Errors[9]
PTOKlima5Errors10 | DIGITAL | IOD_PTO_TCP | 294 | 00294 | Klima5Errors[10]
PTOKlima5Errors11 | DIGITAL | IOD_PTO_TCP | 295 | 00295 | Klima5Errors[11]
PTOKlima5Errors12 | DIGITAL | IOD_PTO_TCP | 296 | 00296 | Klima5Errors[12]
PTOKlima5Errors13 | DIGITAL | IOD_PTO_TCP | 297 | 00297 | Klima5Errors[13]
PTOKlima5Errors14 | DIGITAL | IOD_PTO_TCP | 298 | 00298 | Klima5Errors[14]
PTOKlima5Errors15 | DIGITAL | IOD_PTO_TCP | 299 | 00299 | Klima5Errors[15]
PTOKlima5Errors16 | DIGITAL | IOD_PTO_TCP | 300 | 00300 | Klima5Errors[16]
PTOKlima5Errors17 | DIGITAL | IOD_PTO_TCP | 301 | 00301 | Klima5Errors[17]
PTOKlima5Errors18 | DIGITAL | IOD_PTO_TCP | 302 | 00302 | Klima5Errors[18]
PTOKlima5Errors19 | DIGITAL | IOD_PTO_TCP | 303 | 00303 | Klima5Errors[19]
PTOKlima5Errors1 | DIGITAL | IOD_PTO_TCP | 304 | 00304 | Klima5Errors[1]
PTOKlima5Errors20 | DIGITAL | IOD_PTO_TCP | 305 | 00305 | Klima5Errors[20]
PTOKlima5Errors21 | DIGITAL | IOD_PTO_TCP | 306 | 00306 | Klima5Errors[21]
PTOKlima5Errors22 | DIGITAL | IOD_PTO_TCP | 307 | 00307 | Klima5Errors[22]
PTOKlima5Errors23 | DIGITAL | IOD_PTO_TCP | 308 | 00308 | Klima5Errors[23]
PTOKlima5Errors24 | DIGITAL | IOD_PTO_TCP | 309 | 00309 | Klima5Errors[24]
PTOKlima5Errors25 | DIGITAL | IOD_PTO_TCP | 310 | 00310 | Klima5Errors[25]
PTOKlima5Errors26 | DIGITAL | IOD_PTO_TCP | 311 | 00311 | Klima5Errors[26]
PTOKlima5Errors27 | DIGITAL | IOD_PTO_TCP | 312 | 00312 | Klima5Errors[27]
PTOKlima5Errors28 | DIGITAL | IOD_PTO_TCP | 313 | 00313 | Klima5Errors[28]
PTOKlima5Errors29 | DIGITAL | IOD_PTO_TCP | 314 | 00314 | Klima5Errors[29]
PTOKlima5Errors2 | DIGITAL | IOD_PTO_TCP | 315 | 00315 | Klima5Errors[2]
PTOKlima5Errors30 | DIGITAL | IOD_PTO_TCP | 316 | 00316 | Klima5Errors[30]
PTOKlima5Errors31 | DIGITAL | IOD_PTO_TCP | 317 | 00317 | Klima5Errors[31]
PTOKlima5Errors32 | DIGITAL | IOD_PTO_TCP | 318 | 00318 | Klima5Errors[32]
PTOKlima5Errors33 | DIGITAL | IOD_PTO_TCP | 319 | 00319 | Klima5Errors[33]
PTOKlima5Errors34 | DIGITAL | IOD_PTO_TCP | 320 | 00320 | Klima5Errors[34]
PTOKlima5Errors35 | DIGITAL | IOD_PTO_TCP | 321 | 00321 | Klima5Errors[35]
PTOKlima5Errors3 | DIGITAL | IOD_PTO_TCP | 322 | 00322 | Klima5Errors[3]
PTOKlima5Errors4 | DIGITAL | IOD_PTO_TCP | 323 | 00323 | Klima5Errors[4]
PTOKlima5Errors5 | DIGITAL | IOD_PTO_TCP | 324 | 00324 | Klima5Errors[5]
PTOKlima5Errors6 | DIGITAL | IOD_PTO_TCP | 325 | 00325 | Klima5Errors[6]
PTOKlima5Errors7 | DIGITAL | IOD_PTO_TCP | 326 | 00326 | Klima5Errors[7]
PTOKlima5Errors8 | DIGITAL | IOD_PTO_TCP | 327 | 00327 | Klima5Errors[8]
PTOKlima5Errors9 | DIGITAL | IOD_PTO_TCP | 328 | 00328 | Klima5Errors[9]
PTOKlima6Errors10 | DIGITAL | IOD_PTO_TCP | 329 | 00329 | Klima6Errors[10]
PTOKlima6Errors11 | DIGITAL | IOD_PTO_TCP | 330 | 00330 | Klima6Errors[11]
PTOKlima6Errors12 | DIGITAL | IOD_PTO_TCP | 331 | 00331 | Klima6Errors[12]
PTOKlima6Errors13 | DIGITAL | IOD_PTO_TCP | 332 | 00332 | Klima6Errors[13]
PTOKlima6Errors14 | DIGITAL | IOD_PTO_TCP | 333 | 00333 | Klima6Errors[14]
PTOKlima6Errors15 | DIGITAL | IOD_PTO_TCP | 334 | 00334 | Klima6Errors[15]
PTOKlima6Errors16 | DIGITAL | IOD_PTO_TCP | 335 | 00335 | Klima6Errors[16]
PTOKlima6Errors17 | DIGITAL | IOD_PTO_TCP | 336 | 00336 | Klima6Errors[17]
PTOKlima6Errors18 | DIGITAL | IOD_PTO_TCP | 337 | 00337 | Klima6Errors[18]
PTOKlima6Errors19 | DIGITAL | IOD_PTO_TCP | 338 | 00338 | Klima6Errors[19]
PTOKlima6Errors1 | DIGITAL | IOD_PTO_TCP | 339 | 00339 | Klima6Errors[1]
PTOKlima6Errors20 | DIGITAL | IOD_PTO_TCP | 340 | 00340 | Klima6Errors[20]
PTOKlima6Errors21 | DIGITAL | IOD_PTO_TCP | 341 | 00341 | Klima6Errors[21]
PTOKlima6Errors22 | DIGITAL | IOD_PTO_TCP | 342 | 00342 | Klima6Errors[22]
PTOKlima6Errors23 | DIGITAL | IOD_PTO_TCP | 343 | 00343 | Klima6Errors[23]
PTOKlima6Errors24 | DIGITAL | IOD_PTO_TCP | 344 | 00344 | Klima6Errors[24]
PTOKlima6Errors25 | DIGITAL | IOD_PTO_TCP | 345 | 00345 | Klima6Errors[25]
PTOKlima6Errors26 | DIGITAL | IOD_PTO_TCP | 346 | 00346 | Klima6Errors[26]
PTOKlima6Errors27 | DIGITAL | IOD_PTO_TCP | 347 | 00347 | Klima6Errors[27]
PTOKlima6Errors28 | DIGITAL | IOD_PTO_TCP | 348 | 00348 | Klima6Errors[28]
PTOKlima6Errors29 | DIGITAL | IOD_PTO_TCP | 349 | 00349 | Klima6Errors[29]
PTOKlima6Errors2 | DIGITAL | IOD_PTO_TCP | 350 | 00350 | Klima6Errors[2]
PTOKlima6Errors30 | DIGITAL | IOD_PTO_TCP | 351 | 00351 | Klima6Errors[30]
PTOKlima6Errors31 | DIGITAL | IOD_PTO_TCP | 352 | 00352 | Klima6Errors[31]
PTOKlima6Errors32 | DIGITAL | IOD_PTO_TCP | 353 | 00353 | Klima6Errors[32]
PTOKlima6Errors33 | DIGITAL | IOD_PTO_TCP | 354 | 00354 | Klima6Errors[33]
PTOKlima6Errors34 | DIGITAL | IOD_PTO_TCP | 355 | 00355 | Klima6Errors[34]
PTOKlima6Errors35 | DIGITAL | IOD_PTO_TCP | 356 | 00356 | Klima6Errors[35]
PTOKlima6Errors3 | DIGITAL | IOD_PTO_TCP | 357 | 00357 | Klima6Errors[3]
PTOKlima6Errors4 | DIGITAL | IOD_PTO_TCP | 358 | 00358 | Klima6Errors[4]
PTOKlima6Errors5 | DIGITAL | IOD_PTO_TCP | 359 | 00359 | Klima6Errors[5]
PTOKlima6Errors6 | DIGITAL | IOD_PTO_TCP | 360 | 00360 | Klima6Errors[6]
PTOKlima6Errors7 | DIGITAL | IOD_PTO_TCP | 361 | 00361 | Klima6Errors[7]
PTOKlima6Errors8 | DIGITAL | IOD_PTO_TCP | 362 | 00362 | Klima6Errors[8]
PTOKlima6Errors9 | DIGITAL | IOD_PTO_TCP | 363 | 00363 | Klima6Errors[9]
PTOKlima1Deluje | DIGITAL | IOD_PTO_TCP | 364 | 00364 | Klima[1].Deluje
PTOKlima1FenThermalCutout | DIGITAL | IOD_PTO_TCP | 365 | 00365 | Klima[1].FenThermalCutout
PTOKlima1GeneralAlarm | DIGITAL | IOD_PTO_TCP | 366 | 00366 | Klima[1].GeneralAlarm
PTOKlima1Kompresor1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 367 | 00367 | Klima[1].Kompresor1naMejiObrUr
PTOKlima1Kompresor2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 368 | 00368 | Klima[1].Kompresor2naMejiObrUr
PTOKlima1Napaka | DIGITAL | IOD_PTO_TCP | 369 | 00369 | Klima[1].Napaka
PTOKlima1NapakaPriPretokuZraka | DIGITAL | IOD_PTO_TCP | 370 | 00370 | Klima[1].NapakaPriPretokuZraka
PTOKlima1NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO_TCP | 371 | 00371 | Klima[1].NapakaSenzorTempIzpiha
PTOKlima1NapakaSenzorTempProstora | DIGITAL | IOD_PTO_TCP | 372 | 00372 | Klima[1].NapakaSenzorTempProstora
PTOKlima1NapakaSenzorVlaznosti | DIGITAL | IOD_PTO_TCP | 373 | 00373 | Klima[1].NapakaSenzorVlaznosti
PTOKlima1NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO_TCP | 374 | 00374 | Klima[1].NapakaSenzorZunanjeTemp
PTOKlima1NiTokaVVlazilcu | DIGITAL | IOD_PTO_TCP | 375 | 00375 | Klima[1].NiTokaVVlazilcu
PTOKlima1NiVodeVVlazilcu | DIGITAL | IOD_PTO_TCP | 376 | 00376 | Klima[1].NiVodeVVlazilcu
PTOKlima1NizekPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 377 | 00377 | Klima[1].NizekPritiskKompresor1
PTOKlima1NizekPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 378 | 00378 | Klima[1].NizekPritiskKompresor2
PTOKlima1NizkaTempVProstoru | DIGITAL | IOD_PTO_TCP | 379 | 00379 | Klima[1].NizkaTempVProstoru
PTOKlima1NizkaVlaznost | DIGITAL | IOD_PTO_TCP | 380 | 00380 | Klima[1].NizkaVlaznost
PTOKlima1OnOffEnablingBySupervisor | DIGITAL | IOD_PTO_TCP | 381 | 00381 | Klima[1].OnOffEnablingBySupervisor
PTOKlima1PozarniAlarm | DIGITAL | IOD_PTO_TCP | 382 | 00382 | Klima[1].PozarniAlarm
PTOKlima1Razvlazevanje | DIGITAL | IOD_PTO_TCP | 383 | 00383 | Klima[1].Razvlazevanje
PTOKlima1RemoteOFFtoOutput | DIGITAL | IOD_PTO_TCP | 384 | 00384 | Klima[1].RemoteOFFtoOutput
PTOKlima1RocniIzklop | DIGITAL | IOD_PTO_TCP | 385 | 00385 | Klima[1].RocniIzklop
PTOKlima1SenzorjiStatus | DIGITAL | IOD_PTO_TCP | 386 | 00386 | Klima[1].SenzorjiStatus
PTOKlima1UnitOnOff | DIGITAL | IOD_PTO_TCP | 387 | 00387 | Klima[1].UnitOnOff
PTOKlima1VisokaTempVProstoru | DIGITAL | IOD_PTO_TCP | 388 | 00388 | Klima[1].VisokaTempVProstoru
PTOKlima1VisokaVlaznost | DIGITAL | IOD_PTO_TCP | 389 | 00389 | Klima[1].VisokaVlaznost
PTOKlima1VisokTokVVlazilcu | DIGITAL | IOD_PTO_TCP | 390 | 00390 | Klima[1].VisokTokVVlazilcu
PTOKlima1Vlazenje | DIGITAL | IOD_PTO_TCP | 391 | 00391 | Klima[1].Vlazenje
PTOKlima1ZamasenFilter | DIGITAL | IOD_PTO_TCP | 392 | 00392 | Klima[1].ZamasenFilter
PTOKlima2Deluje | DIGITAL | IOD_PTO_TCP | 393 | 00393 | Klima[2].Deluje
PTOKlima2FenThermalCutout | DIGITAL | IOD_PTO_TCP | 394 | 00394 | Klima[2].FenThermalCutout
PTOKlima2GeneralAlarm | DIGITAL | IOD_PTO_TCP | 395 | 00395 | Klima[2].GeneralAlarm
PTOKlima2Kompresor1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 396 | 00396 | Klima[2].Kompresor1naMejiObrUr
PTOKlima2Kompresor2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 397 | 00397 | Klima[2].Kompresor2naMejiObrUr
PTOKlima2Napaka | DIGITAL | IOD_PTO_TCP | 398 | 00398 | Klima[2].Napaka
PTOKlima2NapakaPriPretokuZraka | DIGITAL | IOD_PTO_TCP | 399 | 00399 | Klima[2].NapakaPriPretokuZraka
PTOKlima2NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO_TCP | 400 | 00400 | Klima[2].NapakaSenzorTempIzpiha
PTOKlima2NapakaSenzorTempProstora | DIGITAL | IOD_PTO_TCP | 401 | 00401 | Klima[2].NapakaSenzorTempProstora
PTOKlima2NapakaSenzorVlaznosti | DIGITAL | IOD_PTO_TCP | 402 | 00402 | Klima[2].NapakaSenzorVlaznosti
PTOKlima2NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO_TCP | 403 | 00403 | Klima[2].NapakaSenzorZunanjeTemp
PTOKlima2NiTokaVVlazilcu | DIGITAL | IOD_PTO_TCP | 404 | 00404 | Klima[2].NiTokaVVlazilcu
PTOKlima2NiVodeVVlazilcu | DIGITAL | IOD_PTO_TCP | 405 | 00405 | Klima[2].NiVodeVVlazilcu
PTOKlima2NizekPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 406 | 00406 | Klima[2].NizekPritiskKompresor1
PTOKlima2NizekPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 407 | 00407 | Klima[2].NizekPritiskKompresor2
PTOKlima2NizkaTempVProstoru | DIGITAL | IOD_PTO_TCP | 408 | 00408 | Klima[2].NizkaTempVProstoru
PTOKlima2NizkaVlaznost | DIGITAL | IOD_PTO_TCP | 409 | 00409 | Klima[2].NizkaVlaznost
PTOKlima2OnOffEnablingBySupervisor | DIGITAL | IOD_PTO_TCP | 410 | 00410 | Klima[2].OnOffEnablingBySupervisor
PTOKlima2PozarniAlarm | DIGITAL | IOD_PTO_TCP | 411 | 00411 | Klima[2].PozarniAlarm
PTOKlima2Razvlazevanje | DIGITAL | IOD_PTO_TCP | 412 | 00412 | Klima[2].Razvlazevanje
PTOKlima2RemoteOFFtoOutput | DIGITAL | IOD_PTO_TCP | 413 | 00413 | Klima[2].RemoteOFFtoOutput
PTOKlima2RocniIzklop | DIGITAL | IOD_PTO_TCP | 414 | 00414 | Klima[2].RocniIzklop
PTOKlima2SenzorjiStatus | DIGITAL | IOD_PTO_TCP | 415 | 00415 | Klima[2].SenzorjiStatus
PTOKlima2UnitOnOff | DIGITAL | IOD_PTO_TCP | 416 | 00416 | Klima[2].UnitOnOff
PTOKlima2VisokaTempVProstoru | DIGITAL | IOD_PTO_TCP | 417 | 00417 | Klima[2].VisokaTempVProstoru
PTOKlima2VisokaVlaznost | DIGITAL | IOD_PTO_TCP | 418 | 00418 | Klima[2].VisokaVlaznost
PTOKlima2VisokTokVVlazilcu | DIGITAL | IOD_PTO_TCP | 419 | 00419 | Klima[2].VisokTokVVlazilcu
PTOKlima2Vlazenje | DIGITAL | IOD_PTO_TCP | 420 | 00420 | Klima[2].Vlazenje
PTOKlima2ZamasenFilter | DIGITAL | IOD_PTO_TCP | 421 | 00421 | Klima[2].ZamasenFilter
PTOKlima3Deluje | DIGITAL | IOD_PTO_TCP | 422 | 00422 | Klima[3].Deluje
PTOKlima3FenThermalCutout | DIGITAL | IOD_PTO_TCP | 423 | 00423 | Klima[3].FenThermalCutout
PTOKlima3GeneralAlarm | DIGITAL | IOD_PTO_TCP | 424 | 00424 | Klima[3].GeneralAlarm
PTOKlima3Kompresor1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 425 | 00425 | Klima[3].Kompresor1naMejiObrUr
PTOKlima3Kompresor2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 426 | 00426 | Klima[3].Kompresor2naMejiObrUr
PTOKlima3Napaka | DIGITAL | IOD_PTO_TCP | 427 | 00427 | Klima[3].Napaka
PTOKlima3NapakaPriPretokuZraka | DIGITAL | IOD_PTO_TCP | 428 | 00428 | Klima[3].NapakaPriPretokuZraka
PTOKlima3NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO_TCP | 429 | 00429 | Klima[3].NapakaSenzorTempIzpiha
PTOKlima3NapakaSenzorTempProstora | DIGITAL | IOD_PTO_TCP | 430 | 00430 | Klima[3].NapakaSenzorTempProstora
PTOKlima3NapakaSenzorVlaznosti | DIGITAL | IOD_PTO_TCP | 431 | 00431 | Klima[3].NapakaSenzorVlaznosti
PTOKlima3NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO_TCP | 432 | 00432 | Klima[3].NapakaSenzorZunanjeTemp
PTOKlima3NiTokaVVlazilcu | DIGITAL | IOD_PTO_TCP | 433 | 00433 | Klima[3].NiTokaVVlazilcu
PTOKlima3NiVodeVVlazilcu | DIGITAL | IOD_PTO_TCP | 434 | 00434 | Klima[3].NiVodeVVlazilcu
PTOKlima3NizekPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 435 | 00435 | Klima[3].NizekPritiskKompresor1
PTOKlima3NizekPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 436 | 00436 | Klima[3].NizekPritiskKompresor2
PTOKlima3NizkaTempVProstoru | DIGITAL | IOD_PTO_TCP | 437 | 00437 | Klima[3].NizkaTempVProstoru
PTOKlima3NizkaVlaznost | DIGITAL | IOD_PTO_TCP | 438 | 00438 | Klima[3].NizkaVlaznost
PTOKlima3OnOffEnablingBySupervisor | DIGITAL | IOD_PTO_TCP | 439 | 00439 | Klima[3].OnOffEnablingBySupervisor
PTOKlima3PozarniAlarm | DIGITAL | IOD_PTO_TCP | 440 | 00440 | Klima[3].PozarniAlarm
PTOKlima3Razvlazevanje | DIGITAL | IOD_PTO_TCP | 441 | 00441 | Klima[3].Razvlazevanje
PTOKlima3RemoteOFFtoOutput | DIGITAL | IOD_PTO_TCP | 442 | 00442 | Klima[3].RemoteOFFtoOutput
PTOKlima3RocniIzklop | DIGITAL | IOD_PTO_TCP | 443 | 00443 | Klima[3].RocniIzklop
PTOKlima3SenzorjiStatus | DIGITAL | IOD_PTO_TCP | 444 | 00444 | Klima[3].SenzorjiStatus
PTOKlima3UnitOnOff | DIGITAL | IOD_PTO_TCP | 445 | 00445 | Klima[3].UnitOnOff
PTOKlima3VisokaTempVProstoru | DIGITAL | IOD_PTO_TCP | 446 | 00446 | Klima[3].VisokaTempVProstoru
PTOKlima3VisokaVlaznost | DIGITAL | IOD_PTO_TCP | 447 | 00447 | Klima[3].VisokaVlaznost
PTOKlima3VisokTokVVlazilcu | DIGITAL | IOD_PTO_TCP | 448 | 00448 | Klima[3].VisokTokVVlazilcu
PTOKlima3Vlazenje | DIGITAL | IOD_PTO_TCP | 449 | 00449 | Klima[3].Vlazenje
PTOKlima3ZamasenFilter | DIGITAL | IOD_PTO_TCP | 450 | 00450 | Klima[3].ZamasenFilter
PTOKlima4Deluje | DIGITAL | IOD_PTO_TCP | 451 | 00451 | Klima[4].Deluje
PTOKlima4FenThermalCutout | DIGITAL | IOD_PTO_TCP | 452 | 00452 | Klima[4].FenThermalCutout
PTOKlima4GeneralAlarm | DIGITAL | IOD_PTO_TCP | 453 | 00453 | Klima[4].GeneralAlarm
PTOKlima4Kompresor1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 454 | 00454 | Klima[4].Kompresor1naMejiObrUr
PTOKlima4Kompresor2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 455 | 00455 | Klima[4].Kompresor2naMejiObrUr
PTOKlima4Napaka | DIGITAL | IOD_PTO_TCP | 456 | 00456 | Klima[4].Napaka
PTOKlima4NapakaPriPretokuZraka | DIGITAL | IOD_PTO_TCP | 457 | 00457 | Klima[4].NapakaPriPretokuZraka
PTOKlima4NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO_TCP | 458 | 00458 | Klima[4].NapakaSenzorTempIzpiha
PTOKlima4NapakaSenzorTempProstora | DIGITAL | IOD_PTO_TCP | 459 | 00459 | Klima[4].NapakaSenzorTempProstora
PTOKlima4NapakaSenzorVlaznosti | DIGITAL | IOD_PTO_TCP | 460 | 00460 | Klima[4].NapakaSenzorVlaznosti
PTOKlima4NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO_TCP | 461 | 00461 | Klima[4].NapakaSenzorZunanjeTemp
PTOKlima4NiTokaVVlazilcu | DIGITAL | IOD_PTO_TCP | 462 | 00462 | Klima[4].NiTokaVVlazilcu
PTOKlima4NiVodeVVlazilcu | DIGITAL | IOD_PTO_TCP | 463 | 00463 | Klima[4].NiVodeVVlazilcu
PTOKlima4NizekPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 464 | 00464 | Klima[4].NizekPritiskKompresor1
PTOKlima4NizekPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 465 | 00465 | Klima[4].NizekPritiskKompresor2
PTOKlima4NizkaTempVProstoru | DIGITAL | IOD_PTO_TCP | 466 | 00466 | Klima[4].NizkaTempVProstoru
PTOKlima4NizkaVlaznost | DIGITAL | IOD_PTO_TCP | 467 | 00467 | Klima[4].NizkaVlaznost
PTOKlima4OnOffEnablingBySupervisor | DIGITAL | IOD_PTO_TCP | 468 | 00468 | Klima[4].OnOffEnablingBySupervisor
PTOKlima4PozarniAlarm | DIGITAL | IOD_PTO_TCP | 469 | 00469 | Klima[4].PozarniAlarm
PTOKlima4Razvlazevanje | DIGITAL | IOD_PTO_TCP | 470 | 00470 | Klima[4].Razvlazevanje
PTOKlima4RemoteOFFtoOutput | DIGITAL | IOD_PTO_TCP | 471 | 00471 | Klima[4].RemoteOFFtoOutput
PTOKlima4RocniIzklop | DIGITAL | IOD_PTO_TCP | 472 | 00472 | Klima[4].RocniIzklop
PTOKlima4SenzorjiStatus | DIGITAL | IOD_PTO_TCP | 473 | 00473 | Klima[4].SenzorjiStatus
PTOKlima4UnitOnOff | DIGITAL | IOD_PTO_TCP | 474 | 00474 | Klima[4].UnitOnOff
PTOKlima4VisokaTempVProstoru | DIGITAL | IOD_PTO_TCP | 475 | 00475 | Klima[4].VisokaTempVProstoru
PTOKlima4VisokaVlaznost | DIGITAL | IOD_PTO_TCP | 476 | 00476 | Klima[4].VisokaVlaznost
PTOKlima4VisokTokVVlazilcu | DIGITAL | IOD_PTO_TCP | 477 | 00477 | Klima[4].VisokTokVVlazilcu
PTOKlima4Vlazenje | DIGITAL | IOD_PTO_TCP | 478 | 00478 | Klima[4].Vlazenje
PTOKlima4ZamasenFilter | DIGITAL | IOD_PTO_TCP | 479 | 00479 | Klima[4].ZamasenFilter
PTOKlima5Deluje | DIGITAL | IOD_PTO_TCP | 480 | 00480 | Klima[5].Deluje
PTOKlima5FenThermalCutout | DIGITAL | IOD_PTO_TCP | 481 | 00481 | Klima[5].FenThermalCutout
PTOKlima5GeneralAlarm | DIGITAL | IOD_PTO_TCP | 482 | 00482 | Klima[5].GeneralAlarm
PTOKlima5Kompresor1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 483 | 00483 | Klima[5].Kompresor1naMejiObrUr
PTOKlima5Kompresor2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 484 | 00484 | Klima[5].Kompresor2naMejiObrUr
PTOKlima5Napaka | DIGITAL | IOD_PTO_TCP | 485 | 00485 | Klima[5].Napaka
PTOKlima5NapakaPriPretokuZraka | DIGITAL | IOD_PTO_TCP | 486 | 00486 | Klima[5].NapakaPriPretokuZraka
PTOKlima5NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO_TCP | 487 | 00487 | Klima[5].NapakaSenzorTempIzpiha
PTOKlima5NapakaSenzorTempProstora | DIGITAL | IOD_PTO_TCP | 488 | 00488 | Klima[5].NapakaSenzorTempProstora
PTOKlima5NapakaSenzorVlaznosti | DIGITAL | IOD_PTO_TCP | 489 | 00489 | Klima[5].NapakaSenzorVlaznosti
PTOKlima5NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO_TCP | 490 | 00490 | Klima[5].NapakaSenzorZunanjeTemp
PTOKlima5NiTokaVVlazilcu | DIGITAL | IOD_PTO_TCP | 491 | 00491 | Klima[5].NiTokaVVlazilcu
PTOKlima5NiVodeVVlazilcu | DIGITAL | IOD_PTO_TCP | 492 | 00492 | Klima[5].NiVodeVVlazilcu
PTOKlima5NizekPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 493 | 00493 | Klima[5].NizekPritiskKompresor1
PTOKlima5NizekPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 494 | 00494 | Klima[5].NizekPritiskKompresor2
PTOKlima5NizkaTempVProstoru | DIGITAL | IOD_PTO_TCP | 495 | 00495 | Klima[5].NizkaTempVProstoru
PTOKlima5NizkaVlaznost | DIGITAL | IOD_PTO_TCP | 496 | 00496 | Klima[5].NizkaVlaznost
PTOKlima5OnOffEnablingBySupervisor | DIGITAL | IOD_PTO_TCP | 497 | 00497 | Klima[5].OnOffEnablingBySupervisor
PTOKlima5PozarniAlarm | DIGITAL | IOD_PTO_TCP | 498 | 00498 | Klima[5].PozarniAlarm
PTOKlima5Razvlazevanje | DIGITAL | IOD_PTO_TCP | 499 | 00499 | Klima[5].Razvlazevanje
PTOKlima5RemoteOFFtoOutput | DIGITAL | IOD_PTO_TCP | 500 | 00500 | Klima[5].RemoteOFFtoOutput
PTOKlima5RocniIzklop | DIGITAL | IOD_PTO_TCP | 501 | 00501 | Klima[5].RocniIzklop
PTOKlima5SenzorjiStatus | DIGITAL | IOD_PTO_TCP | 502 | 00502 | Klima[5].SenzorjiStatus
PTOKlima5UnitOnOff | DIGITAL | IOD_PTO_TCP | 503 | 00503 | Klima[5].UnitOnOff
PTOKlima5VisokaTempVProstoru | DIGITAL | IOD_PTO_TCP | 504 | 00504 | Klima[5].VisokaTempVProstoru
PTOKlima5VisokaVlaznost | DIGITAL | IOD_PTO_TCP | 505 | 00505 | Klima[5].VisokaVlaznost
PTOKlima5VisokTokVVlazilcu | DIGITAL | IOD_PTO_TCP | 506 | 00506 | Klima[5].VisokTokVVlazilcu
PTOKlima5Vlazenje | DIGITAL | IOD_PTO_TCP | 507 | 00507 | Klima[5].Vlazenje
PTOKlima5ZamasenFilter | DIGITAL | IOD_PTO_TCP | 508 | 00508 | Klima[5].ZamasenFilter
PTOKlima6Deluje | DIGITAL | IOD_PTO_TCP | 509 | 00509 | Klima[6].Deluje
PTOKlima6FenThermalCutout | DIGITAL | IOD_PTO_TCP | 510 | 00510 | Klima[6].FenThermalCutout
PTOKlima6GeneralAlarm | DIGITAL | IOD_PTO_TCP | 511 | 00511 | Klima[6].GeneralAlarm
PTOKlima6Kompresor1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 512 | 00512 | Klima[6].Kompresor1naMejiObrUr
PTOKlima6Kompresor2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 513 | 00513 | Klima[6].Kompresor2naMejiObrUr
PTOKlima6Napaka | DIGITAL | IOD_PTO_TCP | 514 | 00514 | Klima[6].Napaka
PTOKlima6NapakaPriPretokuZraka | DIGITAL | IOD_PTO_TCP | 515 | 00515 | Klima[6].NapakaPriPretokuZraka
PTOKlima6NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO_TCP | 516 | 00516 | Klima[6].NapakaSenzorTempIzpiha
PTOKlima6NapakaSenzorTempProstora | DIGITAL | IOD_PTO_TCP | 517 | 00517 | Klima[6].NapakaSenzorTempProstora
PTOKlima6NapakaSenzorVlaznosti | DIGITAL | IOD_PTO_TCP | 518 | 00518 | Klima[6].NapakaSenzorVlaznosti
PTOKlima6NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO_TCP | 519 | 00519 | Klima[6].NapakaSenzorZunanjeTemp
PTOKlima6NiTokaVVlazilcu | DIGITAL | IOD_PTO_TCP | 520 | 00520 | Klima[6].NiTokaVVlazilcu
PTOKlima6NiVodeVVlazilcu | DIGITAL | IOD_PTO_TCP | 521 | 00521 | Klima[6].NiVodeVVlazilcu
PTOKlima6NizekPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 522 | 00522 | Klima[6].NizekPritiskKompresor1
PTOKlima6NizekPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 523 | 00523 | Klima[6].NizekPritiskKompresor2
PTOKlima6NizkaTempVProstoru | DIGITAL | IOD_PTO_TCP | 524 | 00524 | Klima[6].NizkaTempVProstoru
PTOKlima6NizkaVlaznost | DIGITAL | IOD_PTO_TCP | 525 | 00525 | Klima[6].NizkaVlaznost
PTOKlima6OnOffEnablingBySupervisor | DIGITAL | IOD_PTO_TCP | 526 | 00526 | Klima[6].OnOffEnablingBySupervisor
PTOKlima6PozarniAlarm | DIGITAL | IOD_PTO_TCP | 527 | 00527 | Klima[6].PozarniAlarm
PTOKlima6Razvlazevanje | DIGITAL | IOD_PTO_TCP | 528 | 00528 | Klima[6].Razvlazevanje
PTOKlima6RemoteOFFtoOutput | DIGITAL | IOD_PTO_TCP | 529 | 00529 | Klima[6].RemoteOFFtoOutput
PTOKlima6RocniIzklop | DIGITAL | IOD_PTO_TCP | 530 | 00530 | Klima[6].RocniIzklop
PTOKlima6SenzorjiStatus | DIGITAL | IOD_PTO_TCP | 531 | 00531 | Klima[6].SenzorjiStatus
PTOKlima6UnitOnOff | DIGITAL | IOD_PTO_TCP | 532 | 00532 | Klima[6].UnitOnOff
PTOKlima6VisokaTempVProstoru | DIGITAL | IOD_PTO_TCP | 533 | 00533 | Klima[6].VisokaTempVProstoru
PTOKlima6VisokaVlaznost | DIGITAL | IOD_PTO_TCP | 534 | 00534 | Klima[6].VisokaVlaznost
PTOKlima6VisokTokVVlazilcu | DIGITAL | IOD_PTO_TCP | 535 | 00535 | Klima[6].VisokTokVVlazilcu
PTOKlima6Vlazenje | DIGITAL | IOD_PTO_TCP | 536 | 00536 | Klima[6].Vlazenje
PTOKlima6ZamasenFilter | DIGITAL | IOD_PTO_TCP | 537 | 00537 | Klima[6].ZamasenFilter
PTOKlimeNaCas0 | DIGITAL | IOD_PTO_TCP | 538 | 00538 | KlimeNaCas[0]
PTOKlimeNaCas1 | DIGITAL | IOD_PTO_TCP | 539 | 00539 | KlimeNaCas[1]
PTOKlimeNaCas2 | DIGITAL | IOD_PTO_TCP | 540 | 00540 | KlimeNaCas[2]
PTOKlimeNaCas3 | DIGITAL | IOD_PTO_TCP | 541 | 00541 | KlimeNaCas[3]
PTOMrezaIzpad | DIGITAL | IOD_PTO_TCP | 542 | 00542 | MrezaIzpad
PTOMrezaIzpadKlimaOff1 | DIGITAL | IOD_PTO_TCP | 543 | 00543 | MrezaIzpadKlimaOff[1]
PTOMrezaIzpadKlimaOff2 | DIGITAL | IOD_PTO_TCP | 544 | 00544 | MrezaIzpadKlimaOff[2]
PTOMrezaIzpadKlimaOff3 | DIGITAL | IOD_PTO_TCP | 545 | 00545 | MrezaIzpadKlimaOff[3]
PTOMrezaIzpadKlimaOff4 | DIGITAL | IOD_PTO_TCP | 546 | 00546 | MrezaIzpadKlimaOff[4]
PTOMrezaIzpadKlimaOff5 | DIGITAL | IOD_PTO_TCP | 547 | 00547 | MrezaIzpadKlimaOff[5]
PTOMrezaIzpadKlimaOff6 | DIGITAL | IOD_PTO_TCP | 548 | 00548 | MrezaIzpadKlimaOff[6]
PTONapakaSenzorTemp1 | DIGITAL | IOD_PTO_TCP | 549 | 00549 | NapakaSenzorTemp[1]
PTONapakaSenzorTemp2 | DIGITAL | IOD_PTO_TCP | 550 | 00550 | NapakaSenzorTemp[2]
PTONapakaSenzorTemp3 | DIGITAL | IOD_PTO_TCP | 551 | 00551 | NapakaSenzorTemp[3]
PTONapakaSenzorTemp4 | DIGITAL | IOD_PTO_TCP | 552 | 00552 | NapakaSenzorTemp[4]
PTONapakaSenzorTemp5 | DIGITAL | IOD_PTO_TCP | 553 | 00553 | NapakaSenzorTemp[5]
PTONapakaSenzorTemp6 | DIGITAL | IOD_PTO_TCP | 554 | 00554 | NapakaSenzorTemp[6]
PTONapakaSenzorVlaga1 | DIGITAL | IOD_PTO_TCP | 555 | 00555 | NapakaSenzorVlaga[1]
PTONapakaSenzorVlaga2 | DIGITAL | IOD_PTO_TCP | 556 | 00556 | NapakaSenzorVlaga[2]
PTONapakaSenzorVlaga3 | DIGITAL | IOD_PTO_TCP | 557 | 00557 | NapakaSenzorVlaga[3]
PTONapakaSenzorVlaga4 | DIGITAL | IOD_PTO_TCP | 558 | 00558 | NapakaSenzorVlaga[4]
PTONapakaSenzorVlaga5 | DIGITAL | IOD_PTO_TCP | 559 | 00559 | NapakaSenzorVlaga[5]
PTONapakaSenzorVlaga6 | DIGITAL | IOD_PTO_TCP | 560 | 00560 | NapakaSenzorVlaga[6]
PTOPMMNapaka | DIGITAL | IOD_PTO_TCP | 561 | 00561 | PMM.Napaka
PTOPMMOverCurrentBetw1 | DIGITAL | IOD_PTO_TCP | 562 | 00562 | PMMOverCurrentBetw[1]
PTOPMMOverCurrentBetw2 | DIGITAL | IOD_PTO_TCP | 563 | 00563 | PMMOverCurrentBetw[2]
PTOPMMOverCurrentBetw3 | DIGITAL | IOD_PTO_TCP | 564 | 00564 | PMMOverCurrentBetw[3]
PTOPMMOverCurrentOver1 | DIGITAL | IOD_PTO_TCP | 565 | 00565 | PMMOverCurrentOver[1]
PTOPMMOverCurrentOver2 | DIGITAL | IOD_PTO_TCP | 566 | 00566 | PMMOverCurrentOver[2]
PTOPMMOverCurrentOver3 | DIGITAL | IOD_PTO_TCP | 567 | 00567 | PMMOverCurrentOver[3]
PTOSetDateTime | DIGITAL | IOD_PTO_TCP | 568 | 00568 | SetDateTime
PTOSetDateTimeDemand | DIGITAL | IOD_PTO_TCP | 569 | 00569 | SetDateTimeDemand
PTOSetDateTimeError | DIGITAL | IOD_PTO_TCP | 570 | 00570 | SetDateTimeError
PTOSetDateTimeFinished | DIGITAL | IOD_PTO_TCP | 571 | 00571 | SetDateTimeFinished
PTOSetRemoteOnOff1 | DIGITAL | IOD_PTO_TCP | 572 | 00572 | SetRemoteOnOff[1]
PTOSetRemoteOnOff2 | DIGITAL | IOD_PTO_TCP | 573 | 00573 | SetRemoteOnOff[2]
PTOSlabaBaterijaPLC_A1 | DIGITAL | IOD_PTO_TCP | 574 | 00574 | SlabaBaterijaPLC_A1
PTOTempTSprevisoka1 | DIGITAL | IOD_PTO_TCP | 575 | 00575 | TempTSprevisoka[1]
PTOTempTSprevisoka2 | DIGITAL | IOD_PTO_TCP | 576 | 00576 | TempTSprevisoka[2]
PTOTempTSprevisoka3 | DIGITAL | IOD_PTO_TCP | 577 | 00577 | TempTSprevisoka[3]
PTOTempTSprevisokaSum | DIGITAL | IOD_PTO_TCP | 578 | 00578 | TempTSprevisokaSum
PTOUPS1Errors10 | DIGITAL | IOD_PTO_TCP | 579 | 00579 | UPS1Errors[10]
PTOUPS1Errors11 | DIGITAL | IOD_PTO_TCP | 580 | 00580 | UPS1Errors[11]
PTOUPS1Errors12 | DIGITAL | IOD_PTO_TCP | 581 | 00581 | UPS1Errors[12]
PTOUPS1Errors13 | DIGITAL | IOD_PTO_TCP | 582 | 00582 | UPS1Errors[13]
PTOUPS1Errors14 | DIGITAL | IOD_PTO_TCP | 583 | 00583 | UPS1Errors[14]
PTOUPS1Errors15 | DIGITAL | IOD_PTO_TCP | 584 | 00584 | UPS1Errors[15]
PTOUPS1Errors16 | DIGITAL | IOD_PTO_TCP | 585 | 00585 | UPS1Errors[16]
PTOUPS1Errors17 | DIGITAL | IOD_PTO_TCP | 586 | 00586 | UPS1Errors[17]
PTOUPS1Errors18 | DIGITAL | IOD_PTO_TCP | 587 | 00587 | UPS1Errors[18]
PTOUPS1Errors19 | DIGITAL | IOD_PTO_TCP | 588 | 00588 | UPS1Errors[19]
PTOUPS1Errors1 | DIGITAL | IOD_PTO_TCP | 589 | 00589 | UPS1Errors[1]
PTOUPS1Errors20 | DIGITAL | IOD_PTO_TCP | 590 | 00590 | UPS1Errors[20]
PTOUPS1Errors21 | DIGITAL | IOD_PTO_TCP | 591 | 00591 | UPS1Errors[21]
PTOUPS1Errors22 | DIGITAL | IOD_PTO_TCP | 592 | 00592 | UPS1Errors[22]
PTOUPS1Errors23 | DIGITAL | IOD_PTO_TCP | 593 | 00593 | UPS1Errors[23]
PTOUPS1Errors24 | DIGITAL | IOD_PTO_TCP | 594 | 00594 | UPS1Errors[24]
PTOUPS1Errors25 | DIGITAL | IOD_PTO_TCP | 595 | 00595 | UPS1Errors[25]
PTOUPS1Errors2 | DIGITAL | IOD_PTO_TCP | 596 | 00596 | UPS1Errors[2]
PTOUPS1Errors3 | DIGITAL | IOD_PTO_TCP | 597 | 00597 | UPS1Errors[3]
PTOUPS1Errors4 | DIGITAL | IOD_PTO_TCP | 598 | 00598 | UPS1Errors[4]
PTOUPS1Errors5 | DIGITAL | IOD_PTO_TCP | 599 | 00599 | UPS1Errors[5]
PTOUPS1Errors6 | DIGITAL | IOD_PTO_TCP | 600 | 00600 | UPS1Errors[6]
PTOUPS1Errors7 | DIGITAL | IOD_PTO_TCP | 601 | 00601 | UPS1Errors[7]
PTOUPS1Errors8 | DIGITAL | IOD_PTO_TCP | 602 | 00602 | UPS1Errors[8]
PTOUPS1Errors9 | DIGITAL | IOD_PTO_TCP | 603 | 00603 | UPS1Errors[9]
PTOUPS2Errors10 | DIGITAL | IOD_PTO_TCP | 604 | 00604 | UPS2Errors[10]
PTOUPS2Errors11 | DIGITAL | IOD_PTO_TCP | 605 | 00605 | UPS2Errors[11]
PTOUPS2Errors12 | DIGITAL | IOD_PTO_TCP | 606 | 00606 | UPS2Errors[12]
PTOUPS2Errors13 | DIGITAL | IOD_PTO_TCP | 607 | 00607 | UPS2Errors[13]
PTOUPS2Errors14 | DIGITAL | IOD_PTO_TCP | 608 | 00608 | UPS2Errors[14]
PTOUPS2Errors15 | DIGITAL | IOD_PTO_TCP | 609 | 00609 | UPS2Errors[15]
PTOUPS2Errors16 | DIGITAL | IOD_PTO_TCP | 610 | 00610 | UPS2Errors[16]
PTOUPS2Errors17 | DIGITAL | IOD_PTO_TCP | 611 | 00611 | UPS2Errors[17]
PTOUPS2Errors18 | DIGITAL | IOD_PTO_TCP | 612 | 00612 | UPS2Errors[18]
PTOUPS2Errors19 | DIGITAL | IOD_PTO_TCP | 613 | 00613 | UPS2Errors[19]
PTOUPS2Errors1 | DIGITAL | IOD_PTO_TCP | 614 | 00614 | UPS2Errors[1]
PTOUPS2Errors20 | DIGITAL | IOD_PTO_TCP | 615 | 00615 | UPS2Errors[20]
PTOUPS2Errors21 | DIGITAL | IOD_PTO_TCP | 616 | 00616 | UPS2Errors[21]
PTOUPS2Errors22 | DIGITAL | IOD_PTO_TCP | 617 | 00617 | UPS2Errors[22]
PTOUPS2Errors23 | DIGITAL | IOD_PTO_TCP | 618 | 00618 | UPS2Errors[23]
PTOUPS2Errors24 | DIGITAL | IOD_PTO_TCP | 619 | 00619 | UPS2Errors[24]
PTOUPS2Errors25 | DIGITAL | IOD_PTO_TCP | 620 | 00620 | UPS2Errors[25]
PTOUPS2Errors2 | DIGITAL | IOD_PTO_TCP | 621 | 00621 | UPS2Errors[2]
PTOUPS2Errors3 | DIGITAL | IOD_PTO_TCP | 622 | 00622 | UPS2Errors[3]
PTOUPS2Errors4 | DIGITAL | IOD_PTO_TCP | 623 | 00623 | UPS2Errors[4]
PTOUPS2Errors5 | DIGITAL | IOD_PTO_TCP | 624 | 00624 | UPS2Errors[5]
PTOUPS2Errors6 | DIGITAL | IOD_PTO_TCP | 625 | 00625 | UPS2Errors[6]
PTOUPS2Errors7 | DIGITAL | IOD_PTO_TCP | 626 | 00626 | UPS2Errors[7]
PTOUPS2Errors8 | DIGITAL | IOD_PTO_TCP | 627 | 00627 | UPS2Errors[8]
PTOUPS2Errors9 | DIGITAL | IOD_PTO_TCP | 628 | 00628 | UPS2Errors[9]
PTOUPS1AlarmAwaitingPower | DIGITAL | IOD_PTO_TCP | 629 | 00629 | UPS[1].AlarmAwaitingPower
PTOUPS1AlarmBypassBad | DIGITAL | IOD_PTO_TCP | 630 | 00630 | UPS[1].AlarmBypassBad
PTOUPS1AlarmChargerFailed | DIGITAL | IOD_PTO_TCP | 631 | 00631 | UPS[1].AlarmChargerFailed
PTOUPS1AlarmCommunicationsLost | DIGITAL | IOD_PTO_TCP | 632 | 00632 | UPS[1].AlarmCommunicationsLost
PTOUPS1AlarmDepletedBattery | DIGITAL | IOD_PTO_TCP | 633 | 00633 | UPS[1].AlarmDepletedBattery
PTOUPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_PTO_TCP | 634 | 00634 | UPS[1].AlarmDiagnosticTestFailed
PTOUPS1AlarmInverterError | DIGITAL | IOD_PTO_TCP | 635 | 00635 | UPS[1].AlarmInverterError
PTOUPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_PTO_TCP | 636 | 00636 | UPS[1].AlarmIzhodOffKotZahtevano
PTOUPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_PTO_TCP | 637 | 00637 | UPS[1].AlarmIzhodPreobremenjen
PTOUPS1AlarmLowBattery | DIGITAL | IOD_PTO_TCP | 638 | 00638 | UPS[1].AlarmLowBattery
PTOUPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_PTO_TCP | 639 | 00639 | UPS[1].AlarmNapakaNaVarovalki
PTOUPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_PTO_TCP | 640 | 00640 | UPS[1].AlarmNapakaNaVentilatorju
PTOUPS1AlarmOnBattery | DIGITAL | IOD_PTO_TCP | 641 | 00641 | UPS[1].AlarmOnBattery
PTOUPS1AlarmOnBypass | DIGITAL | IOD_PTO_TCP | 642 | 00642 | UPS[1].AlarmOnBypass
PTOUPS1AlarmShutdownImminent | DIGITAL | IOD_PTO_TCP | 643 | 00643 | UPS[1].AlarmShutdownImminent
PTOUPS1AlarmShutdownPending | DIGITAL | IOD_PTO_TCP | 644 | 00644 | UPS[1].AlarmShutdownPending
PTOUPS1AlarmSlabaBaterija | DIGITAL | IOD_PTO_TCP | 645 | 00645 | UPS[1].AlarmSlabaBaterija
PTOUPS1AlarmSplosnaNapaka | DIGITAL | IOD_PTO_TCP | 646 | 00646 | UPS[1].AlarmSplosnaNapaka
PTOUPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_PTO_TCP | 647 | 00647 | UPS[1].AlarmStanjeIzhodaIzvenToleranc
PTOUPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_PTO_TCP | 648 | 00648 | UPS[1].AlarmStanjeVhodaIzvenToleranc
PTOUPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_PTO_TCP | 649 | 00649 | UPS[1].AlarmTemperaturaIzvenToleranc
PTOUPS1AlarmTestInProgres | DIGITAL | IOD_PTO_TCP | 650 | 00650 | UPS[1].AlarmTestInProgres
PTOUPS1AlarmUPSIzhodOff | DIGITAL | IOD_PTO_TCP | 651 | 00651 | UPS[1].AlarmUPSIzhodOff
PTOUPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_PTO_TCP | 652 | 00652 | UPS[1].AlarmUPSOffKotZahtevano
PTOUPS1AlarmUPSSystemOff | DIGITAL | IOD_PTO_TCP | 653 | 00653 | UPS[1].AlarmUPSSystemOff
PTOUPS1Napaka | DIGITAL | IOD_PTO_TCP | 654 | 00654 | UPS[1].Napaka
PTOUPS1StatusEcomodeAktiven | DIGITAL | IOD_PTO_TCP | 655 | 00655 | UPS[1].StatusEcomodeAktiven
PTOUPS1StatusInverterIsOn | DIGITAL | IOD_PTO_TCP | 656 | 00656 | UPS[1].StatusInverterIsOn
PTOUPS1StatusStopOperation | DIGITAL | IOD_PTO_TCP | 657 | 00657 | UPS[1].StatusStopOperation
PTOUPS2AlarmAwaitingPower | DIGITAL | IOD_PTO_TCP | 658 | 00658 | UPS[2].AlarmAwaitingPower
PTOUPS2AlarmBypassBad | DIGITAL | IOD_PTO_TCP | 659 | 00659 | UPS[2].AlarmBypassBad
PTOUPS2AlarmChargerFailed | DIGITAL | IOD_PTO_TCP | 660 | 00660 | UPS[2].AlarmChargerFailed
PTOUPS2AlarmCommunicationsLost | DIGITAL | IOD_PTO_TCP | 661 | 00661 | UPS[2].AlarmCommunicationsLost
PTOUPS2AlarmDepletedBattery | DIGITAL | IOD_PTO_TCP | 662 | 00662 | UPS[2].AlarmDepletedBattery
PTOUPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_PTO_TCP | 663 | 00663 | UPS[2].AlarmDiagnosticTestFailed
PTOUPS2AlarmInverterError | DIGITAL | IOD_PTO_TCP | 664 | 00664 | UPS[2].AlarmInverterError
PTOUPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_PTO_TCP | 665 | 00665 | UPS[2].AlarmIzhodOffKotZahtevano
PTOUPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_PTO_TCP | 666 | 00666 | UPS[2].AlarmIzhodPreobremenjen
PTOUPS2AlarmLowBattery | DIGITAL | IOD_PTO_TCP | 667 | 00667 | UPS[2].AlarmLowBattery
PTOUPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_PTO_TCP | 668 | 00668 | UPS[2].AlarmNapakaNaVarovalki
PTOUPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_PTO_TCP | 669 | 00669 | UPS[2].AlarmNapakaNaVentilatorju
PTOUPS2AlarmOnBattery | DIGITAL | IOD_PTO_TCP | 670 | 00670 | UPS[2].AlarmOnBattery
PTOUPS2AlarmOnBypass | DIGITAL | IOD_PTO_TCP | 671 | 00671 | UPS[2].AlarmOnBypass
PTOUPS2AlarmShutdownImminent | DIGITAL | IOD_PTO_TCP | 672 | 00672 | UPS[2].AlarmShutdownImminent
PTOUPS2AlarmShutdownPending | DIGITAL | IOD_PTO_TCP | 673 | 00673 | UPS[2].AlarmShutdownPending
PTOUPS2AlarmSlabaBaterija | DIGITAL | IOD_PTO_TCP | 674 | 00674 | UPS[2].AlarmSlabaBaterija
PTOUPS2AlarmSplosnaNapaka | DIGITAL | IOD_PTO_TCP | 675 | 00675 | UPS[2].AlarmSplosnaNapaka
PTOUPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_PTO_TCP | 676 | 00676 | UPS[2].AlarmStanjeIzhodaIzvenToleranc
PTOUPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_PTO_TCP | 677 | 00677 | UPS[2].AlarmStanjeVhodaIzvenToleranc
PTOUPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_PTO_TCP | 678 | 00678 | UPS[2].AlarmTemperaturaIzvenToleranc
PTOUPS2AlarmTestInProgres | DIGITAL | IOD_PTO_TCP | 679 | 00679 | UPS[2].AlarmTestInProgres
PTOUPS2AlarmUPSIzhodOff | DIGITAL | IOD_PTO_TCP | 680 | 00680 | UPS[2].AlarmUPSIzhodOff
PTOUPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_PTO_TCP | 681 | 00681 | UPS[2].AlarmUPSOffKotZahtevano
PTOUPS2AlarmUPSSystemOff | DIGITAL | IOD_PTO_TCP | 682 | 00682 | UPS[2].AlarmUPSSystemOff
PTOUPS2Napaka | DIGITAL | IOD_PTO_TCP | 683 | 00683 | UPS[2].Napaka
PTOUPS2StatusEcomodeAktiven | DIGITAL | IOD_PTO_TCP | 684 | 00684 | UPS[2].StatusEcomodeAktiven
PTOUPS2StatusInverterIsOn | DIGITAL | IOD_PTO_TCP | 685 | 00685 | UPS[2].StatusInverterIsOn
PTOUPS2StatusStopOperation | DIGITAL | IOD_PTO_TCP | 686 | 00686 | UPS[2].StatusStopOperation
PTOUserLoggedIn | DIGITAL | IOD_PTO_TCP | 687 | 00687 | UserLoggedIn
PTODIN_A1Q11_OdcUpsB_IZP | DIGITAL | IOD_PTO_TCP | 688 | 00688 | DIN_A1Q11_OdcUpsB_IZP
PTODIN_A1Q12_OdcByUpsB_IZP | DIGITAL | IOD_PTO_TCP | 689 | 00689 | DIN_A1Q12_OdcByUpsB_IZP
PTODIN_A1Q13_OdcByB_IZP | DIGITAL | IOD_PTO_TCP | 690 | 00690 | DIN_A1Q13_OdcByB_IZP
PTODIN_UQ11_OdcPMMB_IZP | DIGITAL | IOD_PTO_TCP | 691 | 00691 | DIN_UQ11_OdcPMMB_IZP
PTODIN_UQ12_OdcPMMB_IZP | DIGITAL | IOD_PTO_TCP | 692 | 00692 | DIN_UQ12_OdcPMMB_IZP
PTODIN_PrenapA3_OK | DIGITAL | IOD_PTO_TCP | 693 | 00693 | DIN_PrenapA3_OK
PTODIN_A1Q0_GlavnoStiB_ON | DIGITAL | IOD_PTO_TCP | 694 | 00694 | DIN_A1Q0_GlavnoStiB_ON
PTODIN_A1Q11_OdcUpsB_ON | DIGITAL | IOD_PTO_TCP | 695 | 00695 | DIN_A1Q11_OdcUpsB_ON
PTODIN_A1Q12_OdcByUpsB_ON | DIGITAL | IOD_PTO_TCP | 696 | 00696 | DIN_A1Q12_OdcByUpsB_ON
PTODI_A1Q13_OdcByB_ON | DIGITAL | IOD_PTO_TCP | 697 | 00697 | DI_A1Q13_OdcByB_ON
PTODIN_A1Q01_DovUpsB_ON | DIGITAL | IOD_PTO_TCP | 698 | 00698 | DIN_A1Q01_DovUpsB_ON
PTODI_A1Q02_DovByB_ON | DIGITAL | IOD_PTO_TCP | 699 | 00699 | DI_A1Q02_DovByB_ON
PTODIN_UQ11_OdcPMMB_ON | DIGITAL | IOD_PTO_TCP | 700 | 00700 | DIN_UQ11_OdcPMMB_ON
PTODI_UQ12_OdcPMMB_ON | DIGITAL | IOD_PTO_TCP | 701 | 00701 | DI_UQ12_OdcPMMB_ON
PTOKlima1NapacnoGesloAlarm | DIGITAL | IOD_PTO_TCP | 702 | 00702 | Klima[1].NapacnoGesloAlarm
PTOKlima1ExtTempHumAlarm | DIGITAL | IOD_PTO_TCP | 703 | 00703 | Klima[1].ExtTempHumAlarm
PTOKlima1PoplavniAlarm | DIGITAL | IOD_PTO_TCP | 704 | 00704 | Klima[1].PoplavniAlarm
PTOKlima1VisokPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 705 | 00705 | Klima[1].VisokPritiskKompresor1
PTOKlima1VisokPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 706 | 00706 | Klima[1].VisokPritiskKompresor2
PTOKlima1ElVentilKompresor1ERR | DIGITAL | IOD_PTO_TCP | 707 | 00707 | Klima[1].ElVentilKompresor1ERR
PTOKlima1ElVentilKompresor2ERR | DIGITAL | IOD_PTO_TCP | 708 | 00708 | Klima[1].ElVentilKompresor2ERR
PTOKlima1WrongPhaseSeqAlarm | DIGITAL | IOD_PTO_TCP | 709 | 00709 | Klima[1].WrongPhaseSeqAlarm
PTOKlima1PrekinjenLANalarm | DIGITAL | IOD_PTO_TCP | 710 | 00710 | Klima[1].PrekinjenLANalarm
PTOKlima1CWTempHighForDehum | DIGITAL | IOD_PTO_TCP | 711 | 00711 | Klima[1].CWTempHighForDehum
PTOKlima1CWVentilErrOrLowFlow | DIGITAL | IOD_PTO_TCP | 712 | 00712 | Klima[1].CWVentilErrOrLowFlow
PTOKlima1NapakaPriPretokuVode | DIGITAL | IOD_PTO_TCP | 713 | 00713 | Klima[1].NapakaPriPretokuVode
PTOKlima1CWhighTemp | DIGITAL | IOD_PTO_TCP | 714 | 00714 | Klima[1].CWhighTemp
PTOKlima1NapakaSenzorHotWTemp | DIGITAL | IOD_PTO_TCP | 715 | 00715 | Klima[1].NapakaSenzorHotWTemp
PTOKlima1NapakaSenzorCondWTemp | DIGITAL | IOD_PTO_TCP | 716 | 00716 | Klima[1].NapakaSenzorCondWTemp
PTOKlima1NapakaSenzorCW | DIGITAL | IOD_PTO_TCP | 717 | 00717 | Klima[1].NapakaSenzorCW
PTOKlima1Kompresor3naMejiObrUr | DIGITAL | IOD_PTO_TCP | 718 | 00718 | Klima[1].Kompresor3naMejiObrUr
PTOKlima1Kompresor4naMejiObrUr | DIGITAL | IOD_PTO_TCP | 719 | 00719 | Klima[1].Kompresor4naMejiObrUr
PTOKlima1ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 720 | 00720 | Klima[1].ZracniFilterNaMejiObrUr
PTOKlima1Grelec1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 721 | 00721 | Klima[1].Grelec1naMejiObrUr
PTOKlima1Grelec2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 722 | 00722 | Klima[1].Grelec2naMejiObrUr
PTOKlima1VlazilecNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 723 | 00723 | Klima[1].VlazilecNaMejiObrUr
PTOKlima1AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 724 | 00724 | Klima[1].AirCondUnitNaMejiObrUr
PTOKlima1DigIn2Alarm | DIGITAL | IOD_PTO_TCP | 725 | 00725 | Klima[1].DigIn2Alarm
PTOKlima1DigIn4Alarm | DIGITAL | IOD_PTO_TCP | 726 | 00726 | Klima[1].DigIn4Alarm
PTOKlima1DigIn6Alarm | DIGITAL | IOD_PTO_TCP | 727 | 00727 | Klima[1].DigIn6Alarm
PTOKlima1VlazilecGenAlarm | DIGITAL | IOD_PTO_TCP | 728 | 00728 | Klima[1].VlazilecGenAlarm
PTOKlima1General2ndLevAlarm | DIGITAL | IOD_PTO_TCP | 729 | 00729 | Klima[1].General2ndLevAlarm
PTOKlima1UnitOnRotAlarm | DIGITAL | IOD_PTO_TCP | 730 | 00730 | Klima[1].UnitOnRotAlarm
PTOKlima1UnitOnAlarmA | DIGITAL | IOD_PTO_TCP | 731 | 00731 | Klima[1].UnitOnAlarmA
PTOKlima1UnitOnAlarmB | DIGITAL | IOD_PTO_TCP | 732 | 00732 | Klima[1].UnitOnAlarmB
PTOKlima1UnitOnAlarmC | DIGITAL | IOD_PTO_TCP | 733 | 00733 | Klima[1].UnitOnAlarmC
PTOKlima2NapacnoGesloAlarm | DIGITAL | IOD_PTO_TCP | 734 | 00734 | Klima[2].NapacnoGesloAlarm
PTOKlima2ExtTempHumAlarm | DIGITAL | IOD_PTO_TCP | 735 | 00735 | Klima[2].ExtTempHumAlarm
PTOKlima2PoplavniAlarm | DIGITAL | IOD_PTO_TCP | 736 | 00736 | Klima[2].PoplavniAlarm
PTOKlima2VisokPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 737 | 00737 | Klima[2].VisokPritiskKompresor1
PTOKlima2VisokPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 738 | 00738 | Klima[2].VisokPritiskKompresor2
PTOKlima2ElVentilKompresor1ERR | DIGITAL | IOD_PTO_TCP | 739 | 00739 | Klima[2].ElVentilKompresor1ERR
PTOKlima2ElVentilKompresor2ERR | DIGITAL | IOD_PTO_TCP | 740 | 00740 | Klima[2].ElVentilKompresor2ERR
PTOKlima2WrongPhaseSeqAlarm | DIGITAL | IOD_PTO_TCP | 741 | 00741 | Klima[2].WrongPhaseSeqAlarm
PTOKlima2PrekinjenLANalarm | DIGITAL | IOD_PTO_TCP | 742 | 00742 | Klima[2].PrekinjenLANalarm
PTOKlima2CWTempHighForDehum | DIGITAL | IOD_PTO_TCP | 743 | 00743 | Klima[2].CWTempHighForDehum
PTOKlima2CWVentilErrOrLowFlow | DIGITAL | IOD_PTO_TCP | 744 | 00744 | Klima[2].CWVentilErrOrLowFlow
PTOKlima2NapakaPriPretokuVode | DIGITAL | IOD_PTO_TCP | 745 | 00745 | Klima[2].NapakaPriPretokuVode
PTOKlima2CWhighTemp | DIGITAL | IOD_PTO_TCP | 746 | 00746 | Klima[2].CWhighTemp
PTOKlima2NapakaSenzorHotWTemp | DIGITAL | IOD_PTO_TCP | 747 | 00747 | Klima[2].NapakaSenzorHotWTemp
PTOKlima2NapakaSenzorCondWTemp | DIGITAL | IOD_PTO_TCP | 748 | 00748 | Klima[2].NapakaSenzorCondWTemp
PTOKlima2NapakaSenzorCW | DIGITAL | IOD_PTO_TCP | 749 | 00749 | Klima[2].NapakaSenzorCW
PTOKlima2Kompresor3naMejiObrUr | DIGITAL | IOD_PTO_TCP | 750 | 00750 | Klima[2].Kompresor3naMejiObrUr
PTOKlima2Kompresor4naMejiObrUr | DIGITAL | IOD_PTO_TCP | 751 | 00751 | Klima[2].Kompresor4naMejiObrUr
PTOKlima2ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 752 | 00752 | Klima[2].ZracniFilterNaMejiObrUr
PTOKlima2Grelec1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 753 | 00753 | Klima[2].Grelec1naMejiObrUr
PTOKlima2Grelec2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 754 | 00754 | Klima[2].Grelec2naMejiObrUr
PTOKlima2VlazilecNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 755 | 00755 | Klima[2].VlazilecNaMejiObrUr
PTOKlima2AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 756 | 00756 | Klima[2].AirCondUnitNaMejiObrUr
PTOKlima2DigIn2Alarm | DIGITAL | IOD_PTO_TCP | 757 | 00757 | Klima[2].DigIn2Alarm
PTOKlima2DigIn4Alarm | DIGITAL | IOD_PTO_TCP | 758 | 00758 | Klima[2].DigIn4Alarm
PTOKlima2DigIn6Alarm | DIGITAL | IOD_PTO_TCP | 759 | 00759 | Klima[2].DigIn6Alarm
PTOKlima2VlazilecGenAlarm | DIGITAL | IOD_PTO_TCP | 760 | 00760 | Klima[2].VlazilecGenAlarm
PTOKlima2General2ndLevAlarm | DIGITAL | IOD_PTO_TCP | 761 | 00761 | Klima[2].General2ndLevAlarm
PTOKlima2UnitOnRotAlarm | DIGITAL | IOD_PTO_TCP | 762 | 00762 | Klima[2].UnitOnRotAlarm
PTOKlima2UnitOnAlarmA | DIGITAL | IOD_PTO_TCP | 763 | 00763 | Klima[2].UnitOnAlarmA
PTOKlima2UnitOnAlarmB | DIGITAL | IOD_PTO_TCP | 764 | 00764 | Klima[2].UnitOnAlarmB
PTOKlima2UnitOnAlarmC | DIGITAL | IOD_PTO_TCP | 765 | 00765 | Klima[2].UnitOnAlarmC
PTOKlima3NapacnoGesloAlarm | DIGITAL | IOD_PTO_TCP | 766 | 00766 | Klima[3].NapacnoGesloAlarm
PTOKlima3ExtTempHumAlarm | DIGITAL | IOD_PTO_TCP | 767 | 00767 | Klima[3].ExtTempHumAlarm
PTOKlima3PoplavniAlarm | DIGITAL | IOD_PTO_TCP | 768 | 00768 | Klima[3].PoplavniAlarm
PTOKlima3VisokPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 769 | 00769 | Klima[3].VisokPritiskKompresor1
PTOKlima3VisokPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 770 | 00770 | Klima[3].VisokPritiskKompresor2
PTOKlima3ElVentilKompresor1ERR | DIGITAL | IOD_PTO_TCP | 771 | 00771 | Klima[3].ElVentilKompresor1ERR
PTOKlima3ElVentilKompresor2ERR | DIGITAL | IOD_PTO_TCP | 772 | 00772 | Klima[3].ElVentilKompresor2ERR
PTOKlima3WrongPhaseSeqAlarm | DIGITAL | IOD_PTO_TCP | 773 | 00773 | Klima[3].WrongPhaseSeqAlarm
PTOKlima3PrekinjenLANalarm | DIGITAL | IOD_PTO_TCP | 774 | 00774 | Klima[3].PrekinjenLANalarm
PTOKlima3CWTempHighForDehum | DIGITAL | IOD_PTO_TCP | 775 | 00775 | Klima[3].CWTempHighForDehum
PTOKlima3CWVentilErrOrLowFlow | DIGITAL | IOD_PTO_TCP | 776 | 00776 | Klima[3].CWVentilErrOrLowFlow
PTOKlima3NapakaPriPretokuVode | DIGITAL | IOD_PTO_TCP | 777 | 00777 | Klima[3].NapakaPriPretokuVode
PTOKlima3CWhighTemp | DIGITAL | IOD_PTO_TCP | 778 | 00778 | Klima[3].CWhighTemp
PTOKlima3NapakaSenzorHotWTemp | DIGITAL | IOD_PTO_TCP | 779 | 00779 | Klima[3].NapakaSenzorHotWTemp
PTOKlima3NapakaSenzorCondWTemp | DIGITAL | IOD_PTO_TCP | 780 | 00780 | Klima[3].NapakaSenzorCondWTemp
PTOKlima3NapakaSenzorCW | DIGITAL | IOD_PTO_TCP | 781 | 00781 | Klima[3].NapakaSenzorCW
PTOKlima3Kompresor3naMejiObrUr | DIGITAL | IOD_PTO_TCP | 782 | 00782 | Klima[3].Kompresor3naMejiObrUr
PTOKlima3Kompresor4naMejiObrUr | DIGITAL | IOD_PTO_TCP | 783 | 00783 | Klima[3].Kompresor4naMejiObrUr
PTOKlima3ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 784 | 00784 | Klima[3].ZracniFilterNaMejiObrUr
PTOKlima3Grelec1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 785 | 00785 | Klima[3].Grelec1naMejiObrUr
PTOKlima3Grelec2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 786 | 00786 | Klima[3].Grelec2naMejiObrUr
PTOKlima3VlazilecNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 787 | 00787 | Klima[3].VlazilecNaMejiObrUr
PTOKlima3AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 788 | 00788 | Klima[3].AirCondUnitNaMejiObrUr
PTOKlima3DigIn2Alarm | DIGITAL | IOD_PTO_TCP | 789 | 00789 | Klima[3].DigIn2Alarm
PTOKlima3DigIn4Alarm | DIGITAL | IOD_PTO_TCP | 790 | 00790 | Klima[3].DigIn4Alarm
PTOKlima3DigIn6Alarm | DIGITAL | IOD_PTO_TCP | 791 | 00791 | Klima[3].DigIn6Alarm
PTOKlima3VlazilecGenAlarm | DIGITAL | IOD_PTO_TCP | 792 | 00792 | Klima[3].VlazilecGenAlarm
PTOKlima3General2ndLevAlarm | DIGITAL | IOD_PTO_TCP | 793 | 00793 | Klima[3].General2ndLevAlarm
PTOKlima3UnitOnRotAlarm | DIGITAL | IOD_PTO_TCP | 794 | 00794 | Klima[3].UnitOnRotAlarm
PTOKlima3UnitOnAlarmA | DIGITAL | IOD_PTO_TCP | 795 | 00795 | Klima[3].UnitOnAlarmA
PTOKlima3UnitOnAlarmB | DIGITAL | IOD_PTO_TCP | 796 | 00796 | Klima[3].UnitOnAlarmB
PTOKlima3UnitOnAlarmC | DIGITAL | IOD_PTO_TCP | 797 | 00797 | Klima[3].UnitOnAlarmC
PTOKlima4NapacnoGesloAlarm | DIGITAL | IOD_PTO_TCP | 798 | 00798 | Klima[4].NapacnoGesloAlarm
PTOKlima4ExtTempHumAlarm | DIGITAL | IOD_PTO_TCP | 799 | 00799 | Klima[4].ExtTempHumAlarm
PTOKlima4PoplavniAlarm | DIGITAL | IOD_PTO_TCP | 800 | 00800 | Klima[4].PoplavniAlarm
PTOKlima4VisokPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 801 | 00801 | Klima[4].VisokPritiskKompresor1
PTOKlima4VisokPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 802 | 00802 | Klima[4].VisokPritiskKompresor2
PTOKlima4ElVentilKompresor1ERR | DIGITAL | IOD_PTO_TCP | 803 | 00803 | Klima[4].ElVentilKompresor1ERR
PTOKlima4ElVentilKompresor2ERR | DIGITAL | IOD_PTO_TCP | 804 | 00804 | Klima[4].ElVentilKompresor2ERR
PTOKlima4WrongPhaseSeqAlarm | DIGITAL | IOD_PTO_TCP | 805 | 00805 | Klima[4].WrongPhaseSeqAlarm
PTOKlima4PrekinjenLANalarm | DIGITAL | IOD_PTO_TCP | 806 | 00806 | Klima[4].PrekinjenLANalarm
PTOKlima4CWTempHighForDehum | DIGITAL | IOD_PTO_TCP | 807 | 00807 | Klima[4].CWTempHighForDehum
PTOKlima4CWVentilErrOrLowFlow | DIGITAL | IOD_PTO_TCP | 808 | 00808 | Klima[4].CWVentilErrOrLowFlow
PTOKlima4NapakaPriPretokuVode | DIGITAL | IOD_PTO_TCP | 809 | 00809 | Klima[4].NapakaPriPretokuVode
PTOKlima4CWhighTemp | DIGITAL | IOD_PTO_TCP | 810 | 00810 | Klima[4].CWhighTemp
PTOKlima4NapakaSenzorHotWTemp | DIGITAL | IOD_PTO_TCP | 811 | 00811 | Klima[4].NapakaSenzorHotWTemp
PTOKlima4NapakaSenzorCondWTemp | DIGITAL | IOD_PTO_TCP | 812 | 00812 | Klima[4].NapakaSenzorCondWTemp
PTOKlima4NapakaSenzorCW | DIGITAL | IOD_PTO_TCP | 813 | 00813 | Klima[4].NapakaSenzorCW
PTOKlima4Kompresor3naMejiObrUr | DIGITAL | IOD_PTO_TCP | 814 | 00814 | Klima[4].Kompresor3naMejiObrUr
PTOKlima4Kompresor4naMejiObrUr | DIGITAL | IOD_PTO_TCP | 815 | 00815 | Klima[4].Kompresor4naMejiObrUr
PTOKlima4ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 816 | 00816 | Klima[4].ZracniFilterNaMejiObrUr
PTOKlima4Grelec1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 817 | 00817 | Klima[4].Grelec1naMejiObrUr
PTOKlima4Grelec2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 818 | 00818 | Klima[4].Grelec2naMejiObrUr
PTOKlima4VlazilecNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 819 | 00819 | Klima[4].VlazilecNaMejiObrUr
PTOKlima4AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 820 | 00820 | Klima[4].AirCondUnitNaMejiObrUr
PTOKlima4DigIn2Alarm | DIGITAL | IOD_PTO_TCP | 821 | 00821 | Klima[4].DigIn2Alarm
PTOKlima4DigIn4Alarm | DIGITAL | IOD_PTO_TCP | 822 | 00822 | Klima[4].DigIn4Alarm
PTOKlima4DigIn6Alarm | DIGITAL | IOD_PTO_TCP | 823 | 00823 | Klima[4].DigIn6Alarm
PTOKlima4VlazilecGenAlarm | DIGITAL | IOD_PTO_TCP | 824 | 00824 | Klima[4].VlazilecGenAlarm
PTOKlima4General2ndLevAlarm | DIGITAL | IOD_PTO_TCP | 825 | 00825 | Klima[4].General2ndLevAlarm
PTOKlima4UnitOnRotAlarm | DIGITAL | IOD_PTO_TCP | 826 | 00826 | Klima[4].UnitOnRotAlarm
PTOKlima4UnitOnAlarmA | DIGITAL | IOD_PTO_TCP | 827 | 00827 | Klima[4].UnitOnAlarmA
PTOKlima4UnitOnAlarmB | DIGITAL | IOD_PTO_TCP | 828 | 00828 | Klima[4].UnitOnAlarmB
PTOKlima4UnitOnAlarmC | DIGITAL | IOD_PTO_TCP | 829 | 00829 | Klima[4].UnitOnAlarmC
PTOKlima5NapacnoGesloAlarm | DIGITAL | IOD_PTO_TCP | 830 | 00830 | Klima[5].NapacnoGesloAlarm
PTOKlima5ExtTempHumAlarm | DIGITAL | IOD_PTO_TCP | 831 | 00831 | Klima[5].ExtTempHumAlarm
PTOKlima5PoplavniAlarm | DIGITAL | IOD_PTO_TCP | 832 | 00832 | Klima[5].PoplavniAlarm
PTOKlima5VisokPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 833 | 00833 | Klima[5].VisokPritiskKompresor1
PTOKlima5VisokPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 834 | 00834 | Klima[5].VisokPritiskKompresor2
PTOKlima5ElVentilKompresor1ERR | DIGITAL | IOD_PTO_TCP | 835 | 00835 | Klima[5].ElVentilKompresor1ERR
PTOKlima5ElVentilKompresor2ERR | DIGITAL | IOD_PTO_TCP | 836 | 00836 | Klima[5].ElVentilKompresor2ERR
PTOKlima5WrongPhaseSeqAlarm | DIGITAL | IOD_PTO_TCP | 837 | 00837 | Klima[5].WrongPhaseSeqAlarm
PTOKlima5PrekinjenLANalarm | DIGITAL | IOD_PTO_TCP | 838 | 00838 | Klima[5].PrekinjenLANalarm
PTOKlima5CWTempHighForDehum | DIGITAL | IOD_PTO_TCP | 839 | 00839 | Klima[5].CWTempHighForDehum
PTOKlima5CWVentilErrOrLowFlow | DIGITAL | IOD_PTO_TCP | 840 | 00840 | Klima[5].CWVentilErrOrLowFlow
PTOKlima5NapakaPriPretokuVode | DIGITAL | IOD_PTO_TCP | 841 | 00841 | Klima[5].NapakaPriPretokuVode
PTOKlima5CWhighTemp | DIGITAL | IOD_PTO_TCP | 842 | 00842 | Klima[5].CWhighTemp
PTOKlima5NapakaSenzorHotWTemp | DIGITAL | IOD_PTO_TCP | 843 | 00843 | Klima[5].NapakaSenzorHotWTemp
PTOKlima5NapakaSenzorCondWTemp | DIGITAL | IOD_PTO_TCP | 844 | 00844 | Klima[5].NapakaSenzorCondWTemp
PTOKlima5NapakaSenzorCW | DIGITAL | IOD_PTO_TCP | 845 | 00845 | Klima[5].NapakaSenzorCW
PTOKlima5Kompresor3naMejiObrUr | DIGITAL | IOD_PTO_TCP | 846 | 00846 | Klima[5].Kompresor3naMejiObrUr
PTOKlima5Kompresor4naMejiObrUr | DIGITAL | IOD_PTO_TCP | 847 | 00847 | Klima[5].Kompresor4naMejiObrUr
PTOKlima5ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 848 | 00848 | Klima[5].ZracniFilterNaMejiObrUr
PTOKlima5Grelec1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 849 | 00849 | Klima[5].Grelec1naMejiObrUr
PTOKlima5Grelec2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 850 | 00850 | Klima[5].Grelec2naMejiObrUr
PTOKlima5VlazilecNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 851 | 00851 | Klima[5].VlazilecNaMejiObrUr
PTOKlima5AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 852 | 00852 | Klima[5].AirCondUnitNaMejiObrUr
PTOKlima5DigIn2Alarm | DIGITAL | IOD_PTO_TCP | 853 | 00853 | Klima[5].DigIn2Alarm
PTOKlima5DigIn4Alarm | DIGITAL | IOD_PTO_TCP | 854 | 00854 | Klima[5].DigIn4Alarm
PTOKlima5DigIn6Alarm | DIGITAL | IOD_PTO_TCP | 855 | 00855 | Klima[5].DigIn6Alarm
PTOKlima5VlazilecGenAlarm | DIGITAL | IOD_PTO_TCP | 856 | 00856 | Klima[5].VlazilecGenAlarm
PTOKlima5General2ndLevAlarm | DIGITAL | IOD_PTO_TCP | 857 | 00857 | Klima[5].General2ndLevAlarm
PTOKlima5UnitOnRotAlarm | DIGITAL | IOD_PTO_TCP | 858 | 00858 | Klima[5].UnitOnRotAlarm
PTOKlima5UnitOnAlarmA | DIGITAL | IOD_PTO_TCP | 859 | 00859 | Klima[5].UnitOnAlarmA
PTOKlima5UnitOnAlarmB | DIGITAL | IOD_PTO_TCP | 860 | 00860 | Klima[5].UnitOnAlarmB
PTOKlima5UnitOnAlarmC | DIGITAL | IOD_PTO_TCP | 861 | 00861 | Klima[5].UnitOnAlarmC
PTOKlima6NapacnoGesloAlarm | DIGITAL | IOD_PTO_TCP | 862 | 00862 | Klima[6].NapacnoGesloAlarm
PTOKlima6ExtTempHumAlarm | DIGITAL | IOD_PTO_TCP | 863 | 00863 | Klima[6].ExtTempHumAlarm
PTOKlima6PoplavniAlarm | DIGITAL | IOD_PTO_TCP | 864 | 00864 | Klima[6].PoplavniAlarm
PTOKlima6VisokPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 865 | 00865 | Klima[6].VisokPritiskKompresor1
PTOKlima6VisokPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 866 | 00866 | Klima[6].VisokPritiskKompresor2
PTOKlima6ElVentilKompresor1ERR | DIGITAL | IOD_PTO_TCP | 867 | 00867 | Klima[6].ElVentilKompresor1ERR
PTOKlima6ElVentilKompresor2ERR | DIGITAL | IOD_PTO_TCP | 868 | 00868 | Klima[6].ElVentilKompresor2ERR
PTOKlima6WrongPhaseSeqAlarm | DIGITAL | IOD_PTO_TCP | 869 | 00869 | Klima[6].WrongPhaseSeqAlarm
PTOKlima6PrekinjenLANalarm | DIGITAL | IOD_PTO_TCP | 870 | 00870 | Klima[6].PrekinjenLANalarm
PTOKlima6CWTempHighForDehum | DIGITAL | IOD_PTO_TCP | 871 | 00871 | Klima[6].CWTempHighForDehum
PTOKlima6CWVentilErrOrLowFlow | DIGITAL | IOD_PTO_TCP | 872 | 00872 | Klima[6].CWVentilErrOrLowFlow
PTOKlima6NapakaPriPretokuVode | DIGITAL | IOD_PTO_TCP | 873 | 00873 | Klima[6].NapakaPriPretokuVode
PTOKlima6CWhighTemp | DIGITAL | IOD_PTO_TCP | 874 | 00874 | Klima[6].CWhighTemp
PTOKlima6NapakaSenzorHotWTemp | DIGITAL | IOD_PTO_TCP | 875 | 00875 | Klima[6].NapakaSenzorHotWTemp
PTOKlima6NapakaSenzorCondWTemp | DIGITAL | IOD_PTO_TCP | 876 | 00876 | Klima[6].NapakaSenzorCondWTemp
PTOKlima6NapakaSenzorCW | DIGITAL | IOD_PTO_TCP | 877 | 00877 | Klima[6].NapakaSenzorCW
PTOKlima6Kompresor3naMejiObrUr | DIGITAL | IOD_PTO_TCP | 878 | 00878 | Klima[6].Kompresor3naMejiObrUr
PTOKlima6Kompresor4naMejiObrUr | DIGITAL | IOD_PTO_TCP | 879 | 00879 | Klima[6].Kompresor4naMejiObrUr
PTOKlima6ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 880 | 00880 | Klima[6].ZracniFilterNaMejiObrUr
PTOKlima6Grelec1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 881 | 00881 | Klima[6].Grelec1naMejiObrUr
PTOKlima6Grelec2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 882 | 00882 | Klima[6].Grelec2naMejiObrUr
PTOKlima6VlazilecNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 883 | 00883 | Klima[6].VlazilecNaMejiObrUr
PTOKlima6AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 884 | 00884 | Klima[6].AirCondUnitNaMejiObrUr
PTOKlima6DigIn2Alarm | DIGITAL | IOD_PTO_TCP | 885 | 00885 | Klima[6].DigIn2Alarm
PTOKlima6DigIn4Alarm | DIGITAL | IOD_PTO_TCP | 886 | 00886 | Klima[6].DigIn4Alarm
PTOKlima6DigIn6Alarm | DIGITAL | IOD_PTO_TCP | 887 | 00887 | Klima[6].DigIn6Alarm
PTOKlima6VlazilecGenAlarm | DIGITAL | IOD_PTO_TCP | 888 | 00888 | Klima[6].VlazilecGenAlarm
PTOKlima6General2ndLevAlarm | DIGITAL | IOD_PTO_TCP | 889 | 00889 | Klima[6].General2ndLevAlarm
PTOKlima6UnitOnRotAlarm | DIGITAL | IOD_PTO_TCP | 890 | 00890 | Klima[6].UnitOnRotAlarm
PTOKlima6UnitOnAlarmA | DIGITAL | IOD_PTO_TCP | 891 | 00891 | Klima[6].UnitOnAlarmA
PTOKlima6UnitOnAlarmB | DIGITAL | IOD_PTO_TCP | 892 | 00892 | Klima[6].UnitOnAlarmB
PTOKlima6UnitOnAlarmC | DIGITAL | IOD_PTO_TCP | 893 | 00893 | Klima[6].UnitOnAlarmC
PTOKlima1Komp1On | DIGITAL | IOD_PTO_TCP | 894 | 00894 | Klima[1].Komp1On
PTOKlima1Komp2On | DIGITAL | IOD_PTO_TCP | 895 | 00895 | Klima[1].Komp2On
PTOKlima1Komp3On | DIGITAL | IOD_PTO_TCP | 896 | 00896 | Klima[1].Komp3On
PTOKlima1Komp4On | DIGITAL | IOD_PTO_TCP | 897 | 00897 | Klima[1].Komp4On
PTOKlima2Komp1On | DIGITAL | IOD_PTO_TCP | 898 | 00898 | Klima[2].Komp1On
PTOKlima2Komp2On | DIGITAL | IOD_PTO_TCP | 899 | 00899 | Klima[2].Komp2On
PTOKlima2Komp3On | DIGITAL | IOD_PTO_TCP | 900 | 00900 | Klima[2].Komp3On
PTOKlima2Komp4On | DIGITAL | IOD_PTO_TCP | 901 | 00901 | Klima[2].Komp4On
PTOKlima3Komp1On | DIGITAL | IOD_PTO_TCP | 902 | 00902 | Klima[3].Komp1On
PTOKlima3Komp2On | DIGITAL | IOD_PTO_TCP | 903 | 00903 | Klima[3].Komp2On
PTOKlima3Komp3On | DIGITAL | IOD_PTO_TCP | 904 | 00904 | Klima[3].Komp3On
PTOKlima3Komp4On | DIGITAL | IOD_PTO_TCP | 905 | 00905 | Klima[3].Komp4On
PTOKlima4Komp1On | DIGITAL | IOD_PTO_TCP | 906 | 00906 | Klima[4].Komp1On
PTOKlima4Komp2On | DIGITAL | IOD_PTO_TCP | 907 | 00907 | Klima[4].Komp2On
PTOKlima4Komp3On | DIGITAL | IOD_PTO_TCP | 908 | 00908 | Klima[4].Komp3On
PTOKlima4Komp4On | DIGITAL | IOD_PTO_TCP | 909 | 00909 | Klima[4].Komp4On
PTOKlima5Komp1On | DIGITAL | IOD_PTO_TCP | 910 | 00910 | Klima[5].Komp1On
PTOKlima5Komp2On | DIGITAL | IOD_PTO_TCP | 911 | 00911 | Klima[5].Komp2On
PTOKlima5Komp3On | DIGITAL | IOD_PTO_TCP | 912 | 00912 | Klima[5].Komp3On
PTOKlima5Komp4On | DIGITAL | IOD_PTO_TCP | 913 | 00913 | Klima[5].Komp4On
PTOKlima6Komp1On | DIGITAL | IOD_PTO_TCP | 914 | 00914 | Klima[6].Komp1On
PTOKlima6Komp2On | DIGITAL | IOD_PTO_TCP | 915 | 00915 | Klima[6].Komp2On
PTOKlima6Komp3On | DIGITAL | IOD_PTO_TCP | 916 | 00916 | Klima[6].Komp3On
PTOKlima6Komp4On | DIGITAL | IOD_PTO_TCP | 917 | 00917 | Klima[6].Komp4On
PTOKlima1GretjeStopnja1 | DIGITAL | IOD_PTO_TCP | 918 | 00918 | Klima[1].GretjeStopnja1
PTOKlima1GretjeStopnja2 | DIGITAL | IOD_PTO_TCP | 919 | 00919 | Klima[1].GretjeStopnja2
PTOKlima1GretjeStopnja3 | DIGITAL | IOD_PTO_TCP | 920 | 00920 | Klima[1].GretjeStopnja3
PTOKlima2GretjeStopnja1 | DIGITAL | IOD_PTO_TCP | 921 | 00921 | Klima[2].GretjeStopnja1
PTOKlima2GretjeStopnja2 | DIGITAL | IOD_PTO_TCP | 922 | 00922 | Klima[2].GretjeStopnja2
PTOKlima2GretjeStopnja3 | DIGITAL | IOD_PTO_TCP | 923 | 00923 | Klima[2].GretjeStopnja3
PTOKlima3GretjeStopnja1 | DIGITAL | IOD_PTO_TCP | 924 | 00924 | Klima[3].GretjeStopnja1
PTOKlima3GretjeStopnja2 | DIGITAL | IOD_PTO_TCP | 925 | 00925 | Klima[3].GretjeStopnja2
PTOKlima3GretjeStopnja3 | DIGITAL | IOD_PTO_TCP | 926 | 00926 | Klima[3].GretjeStopnja3
PTOKlima4GretjeStopnja1 | DIGITAL | IOD_PTO_TCP | 927 | 00927 | Klima[4].GretjeStopnja1
PTOKlima4GretjeStopnja2 | DIGITAL | IOD_PTO_TCP | 928 | 00928 | Klima[4].GretjeStopnja2
PTOKlima4GretjeStopnja3 | DIGITAL | IOD_PTO_TCP | 929 | 00929 | Klima[4].GretjeStopnja3
PTOKlima5GretjeStopnja1 | DIGITAL | IOD_PTO_TCP | 930 | 00930 | Klima[5].GretjeStopnja1
PTOKlima5GretjeStopnja2 | DIGITAL | IOD_PTO_TCP | 931 | 00931 | Klima[5].GretjeStopnja2
PTOKlima5GretjeStopnja3 | DIGITAL | IOD_PTO_TCP | 932 | 00932 | Klima[5].GretjeStopnja3
PTOKlima6GretjeStopnja1 | DIGITAL | IOD_PTO_TCP | 933 | 00933 | Klima[6].GretjeStopnja1
PTOKlima6GretjeStopnja2 | DIGITAL | IOD_PTO_TCP | 934 | 00934 | Klima[6].GretjeStopnja2
PTOKlima6GretjeStopnja3 | DIGITAL | IOD_PTO_TCP | 935 | 00935 | Klima[6].GretjeStopnja3
PTOKlima1HotGasOn | DIGITAL | IOD_PTO_TCP | 936 | 00936 | Klima[1].HotGasOn
PTOKlima2HotGasOn | DIGITAL | IOD_PTO_TCP | 937 | 00937 | Klima[2].HotGasOn
PTOKlima3HotGasOn | DIGITAL | IOD_PTO_TCP | 938 | 00938 | Klima[3].HotGasOn
PTOKlima4HotGasOn | DIGITAL | IOD_PTO_TCP | 939 | 00939 | Klima[4].HotGasOn
PTOKlima5HotGasOn | DIGITAL | IOD_PTO_TCP | 940 | 00940 | Klima[5].HotGasOn
PTOKlima6HotGasOn | DIGITAL | IOD_PTO_TCP | 941 | 00941 | Klima[6].HotGasOn
PTOKlima1EmergencyWorking | DIGITAL | IOD_PTO_TCP | 942 | 00942 | Klima[1].EmergencyWorking
PTOKlima2EmergencyWorking | DIGITAL | IOD_PTO_TCP | 943 | 00943 | Klima[2].EmergencyWorking
PTOKlima3EmergencyWorking | DIGITAL | IOD_PTO_TCP | 944 | 00944 | Klima[3].EmergencyWorking
PTOKlima4EmergencyWorking | DIGITAL | IOD_PTO_TCP | 945 | 00945 | Klima[4].EmergencyWorking
PTOKlima5EmergencyWorking | DIGITAL | IOD_PTO_TCP | 946 | 00946 | Klima[5].EmergencyWorking
PTOKlima6EmergencyWorking | DIGITAL | IOD_PTO_TCP | 947 | 00947 | Klima[6].EmergencyWorking
PTODI_A1Q01_DovUpsB_ON | DIGITAL | IOD_PTO_TCP | 948 | 00948 | DI_A1Q01_DovUpsB_ON
PTODI_A1Q0_GlavnoStiB_ON | DIGITAL | IOD_PTO_TCP | 949 | 00949 | DI_A1Q0_GlavnoStiB_ON
PTODI_A1Q11_OdcUpsB_IZP | DIGITAL | IOD_PTO_TCP | 950 | 00950 | DI_A1Q11_OdcUpsB_IZP
PTODI_A1Q11_OdcUpsB_ON | DIGITAL | IOD_PTO_TCP | 951 | 00951 | DI_A1Q11_OdcUpsB_ON
PTODI_A1Q12_OdcByUpsB_IZP | DIGITAL | IOD_PTO_TCP | 952 | 00952 | DI_A1Q12_OdcByUpsB_IZP
PTODI_A1Q12_OdcByUpsB_ON | DIGITAL | IOD_PTO_TCP | 953 | 00953 | DI_A1Q12_OdcByUpsB_ON
PTODI_A1Q13_OdcByB_IZP | DIGITAL | IOD_PTO_TCP | 954 | 00954 | DI_A1Q13_OdcByB_IZP
PTOErrCommScada2 | DIGITAL | IOD_PTO_TCP | 955 | 00955 | ErrCommScada2
PTOComSCADA2 | DIGITAL | IOD_PTO_TCP | 956 | 00956 | ComSCADA2
PTOComSCADA3 | DIGITAL | IOD_PTO_TCP | 957 | 00957 | ComSCADA3
PTODateTimeDan | INT | IOD_PTO_TCP | 1 | 40001 | DateTime.Dan | BYTE
PTODateTimeLeto | INT | IOD_PTO_TCP | 2 | 40002 | DateTime.Leto | BYTE
PTODateTimeMesec | INT | IOD_PTO_TCP | 3 | 40003 | DateTime.Mesec | BYTE
PTODateTimeMinuta | INT | IOD_PTO_TCP | 4 | 40004 | DateTime.Minuta | BYTE
PTODateTimeSekunda | INT | IOD_PTO_TCP | 5 | 40005 | DateTime.Sekunda | BYTE
PTODateTimeUra | INT | IOD_PTO_TCP | 6 | 40006 | DateTime.Ura | BYTE
PTOErrorComKlima1Code10 | INT | IOD_PTO_TCP | 7 | 40007 | ErrorComKlima[1].Code[10] | BYTE
PTOErrorComKlima1Code11 | INT | IOD_PTO_TCP | 8 | 40008 | ErrorComKlima[1].Code[11] | BYTE
PTOErrorComKlima1Code12 | INT | IOD_PTO_TCP | 9 | 40009 | ErrorComKlima[1].Code[12] | BYTE
PTOErrorComKlima1Code13 | INT | IOD_PTO_TCP | 10 | 40010 | ErrorComKlima[1].Code[13] | BYTE
PTOErrorComKlima1Code14 | INT | IOD_PTO_TCP | 11 | 40011 | ErrorComKlima[1].Code[14] | BYTE
PTOErrorComKlima1Code15 | INT | IOD_PTO_TCP | 12 | 40012 | ErrorComKlima[1].Code[15] | BYTE
PTOErrorComKlima1Code1 | INT | IOD_PTO_TCP | 13 | 40013 | ErrorComKlima[1].Code[1] | BYTE
PTOErrorComKlima1Code2 | INT | IOD_PTO_TCP | 14 | 40014 | ErrorComKlima[1].Code[2] | BYTE
PTOErrorComKlima1Code3 | INT | IOD_PTO_TCP | 15 | 40015 | ErrorComKlima[1].Code[3] | BYTE
PTOErrorComKlima1Code4 | INT | IOD_PTO_TCP | 16 | 40016 | ErrorComKlima[1].Code[4] | BYTE
PTOErrorComKlima1Code5 | INT | IOD_PTO_TCP | 17 | 40017 | ErrorComKlima[1].Code[5] | BYTE
PTOErrorComKlima1Code6 | INT | IOD_PTO_TCP | 18 | 40018 | ErrorComKlima[1].Code[6] | BYTE
PTOErrorComKlima1Code7 | INT | IOD_PTO_TCP | 19 | 40019 | ErrorComKlima[1].Code[7] | BYTE
PTOErrorComKlima1Code8 | INT | IOD_PTO_TCP | 20 | 40020 | ErrorComKlima[1].Code[8] | BYTE
PTOErrorComKlima1Code9 | INT | IOD_PTO_TCP | 21 | 40021 | ErrorComKlima[1].Code[9] | BYTE
PTOErrorComKlima1Status | INT | IOD_PTO_TCP | 22 | 40022 | ErrorComKlima[1].Status
PTOErrorComKlima2Code10 | INT | IOD_PTO_TCP | 23 | 40023 | ErrorComKlima[2].Code[10] | BYTE
PTOErrorComKlima2Code11 | INT | IOD_PTO_TCP | 24 | 40024 | ErrorComKlima[2].Code[11] | BYTE
PTOErrorComKlima2Code12 | INT | IOD_PTO_TCP | 25 | 40025 | ErrorComKlima[2].Code[12] | BYTE
PTOErrorComKlima2Code13 | INT | IOD_PTO_TCP | 26 | 40026 | ErrorComKlima[2].Code[13] | BYTE
PTOErrorComKlima2Code14 | INT | IOD_PTO_TCP | 27 | 40027 | ErrorComKlima[2].Code[14] | BYTE
PTOErrorComKlima2Code15 | INT | IOD_PTO_TCP | 28 | 40028 | ErrorComKlima[2].Code[15] | BYTE
PTOErrorComKlima2Code1 | INT | IOD_PTO_TCP | 29 | 40029 | ErrorComKlima[2].Code[1] | BYTE
PTOErrorComKlima2Code2 | INT | IOD_PTO_TCP | 30 | 40030 | ErrorComKlima[2].Code[2] | BYTE
PTOErrorComKlima2Code3 | INT | IOD_PTO_TCP | 31 | 40031 | ErrorComKlima[2].Code[3] | BYTE
PTOErrorComKlima2Code4 | INT | IOD_PTO_TCP | 32 | 40032 | ErrorComKlima[2].Code[4] | BYTE
PTOErrorComKlima2Code5 | INT | IOD_PTO_TCP | 33 | 40033 | ErrorComKlima[2].Code[5] | BYTE
PTOErrorComKlima2Code6 | INT | IOD_PTO_TCP | 34 | 40034 | ErrorComKlima[2].Code[6] | BYTE
PTOErrorComKlima2Code7 | INT | IOD_PTO_TCP | 35 | 40035 | ErrorComKlima[2].Code[7] | BYTE
PTOErrorComKlima2Code8 | INT | IOD_PTO_TCP | 36 | 40036 | ErrorComKlima[2].Code[8] | BYTE
PTOErrorComKlima2Code9 | INT | IOD_PTO_TCP | 37 | 40037 | ErrorComKlima[2].Code[9] | BYTE
PTOErrorComKlima2Status | INT | IOD_PTO_TCP | 38 | 40038 | ErrorComKlima[2].Status
PTOErrorComKlima3Code10 | INT | IOD_PTO_TCP | 39 | 40039 | ErrorComKlima[3].Code[10] | BYTE
PTOErrorComKlima3Code11 | INT | IOD_PTO_TCP | 40 | 40040 | ErrorComKlima[3].Code[11] | BYTE
PTOErrorComKlima3Code12 | INT | IOD_PTO_TCP | 41 | 40041 | ErrorComKlima[3].Code[12] | BYTE
PTOErrorComKlima3Code13 | INT | IOD_PTO_TCP | 42 | 40042 | ErrorComKlima[3].Code[13] | BYTE
PTOErrorComKlima3Code14 | INT | IOD_PTO_TCP | 43 | 40043 | ErrorComKlima[3].Code[14] | BYTE
PTOErrorComKlima3Code15 | INT | IOD_PTO_TCP | 44 | 40044 | ErrorComKlima[3].Code[15] | BYTE
PTOErrorComKlima3Code1 | INT | IOD_PTO_TCP | 45 | 40045 | ErrorComKlima[3].Code[1] | BYTE
PTOErrorComKlima3Code2 | INT | IOD_PTO_TCP | 46 | 40046 | ErrorComKlima[3].Code[2] | BYTE
PTOErrorComKlima3Code3 | INT | IOD_PTO_TCP | 47 | 40047 | ErrorComKlima[3].Code[3] | BYTE
PTOErrorComKlima3Code4 | INT | IOD_PTO_TCP | 48 | 40048 | ErrorComKlima[3].Code[4] | BYTE
PTOErrorComKlima3Code5 | INT | IOD_PTO_TCP | 49 | 40049 | ErrorComKlima[3].Code[5] | BYTE
PTOErrorComKlima3Code6 | INT | IOD_PTO_TCP | 50 | 40050 | ErrorComKlima[3].Code[6] | BYTE
PTOErrorComKlima3Code7 | INT | IOD_PTO_TCP | 51 | 40051 | ErrorComKlima[3].Code[7] | BYTE
PTOErrorComKlima3Code8 | INT | IOD_PTO_TCP | 52 | 40052 | ErrorComKlima[3].Code[8] | BYTE
PTOErrorComKlima3Code9 | INT | IOD_PTO_TCP | 53 | 40053 | ErrorComKlima[3].Code[9] | BYTE
PTOErrorComKlima3Status | INT | IOD_PTO_TCP | 54 | 40054 | ErrorComKlima[3].Status
PTOErrorComKlima4Code10 | INT | IOD_PTO_TCP | 55 | 40055 | ErrorComKlima[4].Code[10] | BYTE
PTOErrorComKlima4Code11 | INT | IOD_PTO_TCP | 56 | 40056 | ErrorComKlima[4].Code[11] | BYTE
PTOErrorComKlima4Code12 | INT | IOD_PTO_TCP | 57 | 40057 | ErrorComKlima[4].Code[12] | BYTE
PTOErrorComKlima4Code13 | INT | IOD_PTO_TCP | 58 | 40058 | ErrorComKlima[4].Code[13] | BYTE
PTOErrorComKlima4Code14 | INT | IOD_PTO_TCP | 59 | 40059 | ErrorComKlima[4].Code[14] | BYTE
PTOErrorComKlima4Code15 | INT | IOD_PTO_TCP | 60 | 40060 | ErrorComKlima[4].Code[15] | BYTE
PTOErrorComKlima4Code1 | INT | IOD_PTO_TCP | 61 | 40061 | ErrorComKlima[4].Code[1] | BYTE
PTOErrorComKlima4Code2 | INT | IOD_PTO_TCP | 62 | 40062 | ErrorComKlima[4].Code[2] | BYTE
PTOErrorComKlima4Code3 | INT | IOD_PTO_TCP | 63 | 40063 | ErrorComKlima[4].Code[3] | BYTE
PTOErrorComKlima4Code4 | INT | IOD_PTO_TCP | 64 | 40064 | ErrorComKlima[4].Code[4] | BYTE
PTOErrorComKlima4Code5 | INT | IOD_PTO_TCP | 65 | 40065 | ErrorComKlima[4].Code[5] | BYTE
PTOErrorComKlima4Code6 | INT | IOD_PTO_TCP | 66 | 40066 | ErrorComKlima[4].Code[6] | BYTE
PTOErrorComKlima4Code7 | INT | IOD_PTO_TCP | 67 | 40067 | ErrorComKlima[4].Code[7] | BYTE
PTOErrorComKlima4Code8 | INT | IOD_PTO_TCP | 68 | 40068 | ErrorComKlima[4].Code[8] | BYTE
PTOErrorComKlima4Code9 | INT | IOD_PTO_TCP | 69 | 40069 | ErrorComKlima[4].Code[9] | BYTE
PTOErrorComKlima4Status | INT | IOD_PTO_TCP | 70 | 40070 | ErrorComKlima[4].Status
PTOErrorComKlima5Code10 | INT | IOD_PTO_TCP | 71 | 40071 | ErrorComKlima[5].Code[10] | BYTE
PTOErrorComKlima5Code11 | INT | IOD_PTO_TCP | 72 | 40072 | ErrorComKlima[5].Code[11] | BYTE
PTOErrorComKlima5Code12 | INT | IOD_PTO_TCP | 73 | 40073 | ErrorComKlima[5].Code[12] | BYTE
PTOErrorComKlima5Code13 | INT | IOD_PTO_TCP | 74 | 40074 | ErrorComKlima[5].Code[13] | BYTE
PTOErrorComKlima5Code14 | INT | IOD_PTO_TCP | 75 | 40075 | ErrorComKlima[5].Code[14] | BYTE
PTOErrorComKlima5Code15 | INT | IOD_PTO_TCP | 76 | 40076 | ErrorComKlima[5].Code[15] | BYTE
PTOErrorComKlima5Code1 | INT | IOD_PTO_TCP | 77 | 40077 | ErrorComKlima[5].Code[1] | BYTE
PTOErrorComKlima5Code2 | INT | IOD_PTO_TCP | 78 | 40078 | ErrorComKlima[5].Code[2] | BYTE
PTOErrorComKlima5Code3 | INT | IOD_PTO_TCP | 79 | 40079 | ErrorComKlima[5].Code[3] | BYTE
PTOErrorComKlima5Code4 | INT | IOD_PTO_TCP | 80 | 40080 | ErrorComKlima[5].Code[4] | BYTE
PTOErrorComKlima5Code5 | INT | IOD_PTO_TCP | 81 | 40081 | ErrorComKlima[5].Code[5] | BYTE
PTOErrorComKlima5Code6 | INT | IOD_PTO_TCP | 82 | 40082 | ErrorComKlima[5].Code[6] | BYTE
PTOErrorComKlima5Code7 | INT | IOD_PTO_TCP | 83 | 40083 | ErrorComKlima[5].Code[7] | BYTE
PTOErrorComKlima5Code8 | INT | IOD_PTO_TCP | 84 | 40084 | ErrorComKlima[5].Code[8] | BYTE
PTOErrorComKlima5Code9 | INT | IOD_PTO_TCP | 85 | 40085 | ErrorComKlima[5].Code[9] | BYTE
PTOErrorComKlima5Status | INT | IOD_PTO_TCP | 86 | 40086 | ErrorComKlima[5].Status
PTOErrorComKlima6Code10 | INT | IOD_PTO_TCP | 87 | 40087 | ErrorComKlima[6].Code[10] | BYTE
PTOErrorComKlima6Code11 | INT | IOD_PTO_TCP | 88 | 40088 | ErrorComKlima[6].Code[11] | BYTE
PTOErrorComKlima6Code12 | INT | IOD_PTO_TCP | 89 | 40089 | ErrorComKlima[6].Code[12] | BYTE
PTOErrorComKlima6Code13 | INT | IOD_PTO_TCP | 90 | 40090 | ErrorComKlima[6].Code[13] | BYTE
PTOErrorComKlima6Code14 | INT | IOD_PTO_TCP | 91 | 40091 | ErrorComKlima[6].Code[14] | BYTE
PTOErrorComKlima6Code15 | INT | IOD_PTO_TCP | 92 | 40092 | ErrorComKlima[6].Code[15] | BYTE
PTOErrorComKlima6Code1 | INT | IOD_PTO_TCP | 93 | 40093 | ErrorComKlima[6].Code[1] | BYTE
PTOErrorComKlima6Code2 | INT | IOD_PTO_TCP | 94 | 40094 | ErrorComKlima[6].Code[2] | BYTE
PTOErrorComKlima6Code3 | INT | IOD_PTO_TCP | 95 | 40095 | ErrorComKlima[6].Code[3] | BYTE
PTOErrorComKlima6Code4 | INT | IOD_PTO_TCP | 96 | 40096 | ErrorComKlima[6].Code[4] | BYTE
PTOErrorComKlima6Code5 | INT | IOD_PTO_TCP | 97 | 40097 | ErrorComKlima[6].Code[5] | BYTE
PTOErrorComKlima6Code6 | INT | IOD_PTO_TCP | 98 | 40098 | ErrorComKlima[6].Code[6] | BYTE
PTOErrorComKlima6Code7 | INT | IOD_PTO_TCP | 99 | 40099 | ErrorComKlima[6].Code[7] | BYTE
PTOErrorComKlima6Code8 | INT | IOD_PTO_TCP | 100 | 40100 | ErrorComKlima[6].Code[8] | BYTE
PTOErrorComKlima6Code9 | INT | IOD_PTO_TCP | 101 | 40101 | ErrorComKlima[6].Code[9] | BYTE
PTOErrorComKlima6Status | INT | IOD_PTO_TCP | 102 | 40102 | ErrorComKlima[6].Status
PTOErrorComPMMCode10 | INT | IOD_PTO_TCP | 103 | 40103 | ErrorComPMM.Code[10] | BYTE
PTOErrorComPMMCode11 | INT | IOD_PTO_TCP | 104 | 40104 | ErrorComPMM.Code[11] | BYTE
PTOErrorComPMMCode12 | INT | IOD_PTO_TCP | 105 | 40105 | ErrorComPMM.Code[12] | BYTE
PTOErrorComPMMCode13 | INT | IOD_PTO_TCP | 106 | 40106 | ErrorComPMM.Code[13] | BYTE
PTOErrorComPMMCode14 | INT | IOD_PTO_TCP | 107 | 40107 | ErrorComPMM.Code[14] | BYTE
PTOErrorComPMMCode15 | INT | IOD_PTO_TCP | 108 | 40108 | ErrorComPMM.Code[15] | BYTE
PTOErrorComPMMCode1 | INT | IOD_PTO_TCP | 109 | 40109 | ErrorComPMM.Code[1] | BYTE
PTOErrorComPMMCode2 | INT | IOD_PTO_TCP | 110 | 40110 | ErrorComPMM.Code[2] | BYTE
PTOErrorComPMMCode3 | INT | IOD_PTO_TCP | 111 | 40111 | ErrorComPMM.Code[3] | BYTE
PTOErrorComPMMCode4 | INT | IOD_PTO_TCP | 112 | 40112 | ErrorComPMM.Code[4] | BYTE
PTOErrorComPMMCode5 | INT | IOD_PTO_TCP | 113 | 40113 | ErrorComPMM.Code[5] | BYTE
PTOErrorComPMMCode6 | INT | IOD_PTO_TCP | 114 | 40114 | ErrorComPMM.Code[6] | BYTE
PTOErrorComPMMCode7 | INT | IOD_PTO_TCP | 115 | 40115 | ErrorComPMM.Code[7] | BYTE
PTOErrorComPMMCode8 | INT | IOD_PTO_TCP | 116 | 40116 | ErrorComPMM.Code[8] | BYTE
PTOErrorComPMMCode9 | INT | IOD_PTO_TCP | 117 | 40117 | ErrorComPMM.Code[9] | BYTE
PTOErrorComPMMStatus | INT | IOD_PTO_TCP | 118 | 40118 | ErrorComPMM.Status
PTOErrorComUPS1Code10 | INT | IOD_PTO_TCP | 119 | 40119 | ErrorComUPS[1].Code[10] | BYTE
PTOErrorComUPS1Code11 | INT | IOD_PTO_TCP | 120 | 40120 | ErrorComUPS[1].Code[11] | BYTE
PTOErrorComUPS1Code12 | INT | IOD_PTO_TCP | 121 | 40121 | ErrorComUPS[1].Code[12] | BYTE
PTOErrorComUPS1Code13 | INT | IOD_PTO_TCP | 122 | 40122 | ErrorComUPS[1].Code[13] | BYTE
PTOErrorComUPS1Code14 | INT | IOD_PTO_TCP | 123 | 40123 | ErrorComUPS[1].Code[14] | BYTE
PTOErrorComUPS1Code15 | INT | IOD_PTO_TCP | 124 | 40124 | ErrorComUPS[1].Code[15] | BYTE
PTOErrorComUPS1Code1 | INT | IOD_PTO_TCP | 125 | 40125 | ErrorComUPS[1].Code[1] | BYTE
PTOErrorComUPS1Code2 | INT | IOD_PTO_TCP | 126 | 40126 | ErrorComUPS[1].Code[2] | BYTE
PTOErrorComUPS1Code3 | INT | IOD_PTO_TCP | 127 | 40127 | ErrorComUPS[1].Code[3] | BYTE
PTOErrorComUPS1Code4 | INT | IOD_PTO_TCP | 128 | 40128 | ErrorComUPS[1].Code[4] | BYTE
PTOErrorComUPS1Code5 | INT | IOD_PTO_TCP | 129 | 40129 | ErrorComUPS[1].Code[5] | BYTE
PTOErrorComUPS1Code6 | INT | IOD_PTO_TCP | 130 | 40130 | ErrorComUPS[1].Code[6] | BYTE
PTOErrorComUPS1Code7 | INT | IOD_PTO_TCP | 131 | 40131 | ErrorComUPS[1].Code[7] | BYTE
PTOErrorComUPS1Code8 | INT | IOD_PTO_TCP | 132 | 40132 | ErrorComUPS[1].Code[8] | BYTE
PTOErrorComUPS1Code9 | INT | IOD_PTO_TCP | 133 | 40133 | ErrorComUPS[1].Code[9] | BYTE
PTOErrorComUPS1Status | INT | IOD_PTO_TCP | 134 | 40134 | ErrorComUPS[1].Status
PTOErrorComUPS2Code10 | INT | IOD_PTO_TCP | 135 | 40135 | ErrorComUPS[2].Code[10] | BYTE
PTOErrorComUPS2Code11 | INT | IOD_PTO_TCP | 136 | 40136 | ErrorComUPS[2].Code[11] | BYTE
PTOErrorComUPS2Code12 | INT | IOD_PTO_TCP | 137 | 40137 | ErrorComUPS[2].Code[12] | BYTE
PTOErrorComUPS2Code13 | INT | IOD_PTO_TCP | 138 | 40138 | ErrorComUPS[2].Code[13] | BYTE
PTOErrorComUPS2Code14 | INT | IOD_PTO_TCP | 139 | 40139 | ErrorComUPS[2].Code[14] | BYTE
PTOErrorComUPS2Code15 | INT | IOD_PTO_TCP | 140 | 40140 | ErrorComUPS[2].Code[15] | BYTE
PTOErrorComUPS2Code1 | INT | IOD_PTO_TCP | 141 | 40141 | ErrorComUPS[2].Code[1] | BYTE
PTOErrorComUPS2Code2 | INT | IOD_PTO_TCP | 142 | 40142 | ErrorComUPS[2].Code[2] | BYTE
PTOErrorComUPS2Code3 | INT | IOD_PTO_TCP | 143 | 40143 | ErrorComUPS[2].Code[3] | BYTE
PTOErrorComUPS2Code4 | INT | IOD_PTO_TCP | 144 | 40144 | ErrorComUPS[2].Code[4] | BYTE
PTOErrorComUPS2Code5 | INT | IOD_PTO_TCP | 145 | 40145 | ErrorComUPS[2].Code[5] | BYTE
PTOErrorComUPS2Code6 | INT | IOD_PTO_TCP | 146 | 40146 | ErrorComUPS[2].Code[6] | BYTE
PTOErrorComUPS2Code7 | INT | IOD_PTO_TCP | 147 | 40147 | ErrorComUPS[2].Code[7] | BYTE
PTOErrorComUPS2Code8 | INT | IOD_PTO_TCP | 148 | 40148 | ErrorComUPS[2].Code[8] | BYTE
PTOErrorComUPS2Code9 | INT | IOD_PTO_TCP | 149 | 40149 | ErrorComUPS[2].Code[9] | BYTE
PTOErrorComUPS2Status | INT | IOD_PTO_TCP | 150 | 40150 | ErrorComUPS[2].Status
PTOKlima1GrelecStatus | INT | IOD_PTO_TCP | 151 | 40151 | Klima[1].GrelecStatus | BYTE
PTOKlima1IzhodniVentStatus | INT | IOD_PTO_TCP | 152 | 40152 | Klima[1].IzhodniVentStatus | BYTE
PTOKlima1KompresorStatus | INT | IOD_PTO_TCP | 153 | 40153 | Klima[1].KompresorStatus | BYTE
PTOKlima1VlazilecStatus | INT | IOD_PTO_TCP | 154 | 40154 | Klima[1].VlazilecStatus | BYTE
PTOKlima2GrelecStatus | INT | IOD_PTO_TCP | 155 | 40155 | Klima[2].GrelecStatus | BYTE
PTOKlima2IzhodniVentStatus | INT | IOD_PTO_TCP | 156 | 40156 | Klima[2].IzhodniVentStatus | BYTE
PTOKlima2KompresorStatus | INT | IOD_PTO_TCP | 157 | 40157 | Klima[2].KompresorStatus | BYTE
PTOKlima2VlazilecStatus | INT | IOD_PTO_TCP | 158 | 40158 | Klima[2].VlazilecStatus | BYTE
PTOKlima3GrelecStatus | INT | IOD_PTO_TCP | 159 | 40159 | Klima[3].GrelecStatus | BYTE
PTOKlima3IzhodniVentStatus | INT | IOD_PTO_TCP | 160 | 40160 | Klima[3].IzhodniVentStatus | BYTE
PTOKlima3KompresorStatus | INT | IOD_PTO_TCP | 161 | 40161 | Klima[3].KompresorStatus | BYTE
PTOKlima3VlazilecStatus | INT | IOD_PTO_TCP | 162 | 40162 | Klima[3].VlazilecStatus | BYTE
PTOKlima4GrelecStatus | INT | IOD_PTO_TCP | 163 | 40163 | Klima[4].GrelecStatus | BYTE
PTOKlima4IzhodniVentStatus | INT | IOD_PTO_TCP | 164 | 40164 | Klima[4].IzhodniVentStatus | BYTE
PTOKlima4KompresorStatus | INT | IOD_PTO_TCP | 165 | 40165 | Klima[4].KompresorStatus | BYTE
PTOKlima4VlazilecStatus | INT | IOD_PTO_TCP | 166 | 40166 | Klima[4].VlazilecStatus | BYTE
PTOKlima5GrelecStatus | INT | IOD_PTO_TCP | 167 | 40167 | Klima[5].GrelecStatus | BYTE
PTOKlima5IzhodniVentStatus | INT | IOD_PTO_TCP | 168 | 40168 | Klima[5].IzhodniVentStatus | BYTE
PTOKlima5KompresorStatus | INT | IOD_PTO_TCP | 169 | 40169 | Klima[5].KompresorStatus | BYTE
PTOKlima5VlazilecStatus | INT | IOD_PTO_TCP | 170 | 40170 | Klima[5].VlazilecStatus | BYTE
PTOKlima6GrelecStatus | INT | IOD_PTO_TCP | 171 | 40171 | Klima[6].GrelecStatus | BYTE
PTOKlima6IzhodniVentStatus | INT | IOD_PTO_TCP | 172 | 40172 | Klima[6].IzhodniVentStatus | BYTE
PTOKlima6KompresorStatus | INT | IOD_PTO_TCP | 173 | 40173 | Klima[6].KompresorStatus | BYTE
PTOKlima6VlazilecStatus | INT | IOD_PTO_TCP | 174 | 40174 | Klima[6].VlazilecStatus | BYTE
PTOMrezaIzpadVklopDelay1 | INT | IOD_PTO_TCP | 175 | 40175 | MrezaIzpadVklopDelay[1]
PTOMrezaIzpadVklopDelay2 | INT | IOD_PTO_TCP | 176 | 40176 | MrezaIzpadVklopDelay[2]
PTOMrezaIzpadVklopDelay3 | INT | IOD_PTO_TCP | 177 | 40177 | MrezaIzpadVklopDelay[3]
PTOMrezaIzpadVklopDelay4 | INT | IOD_PTO_TCP | 178 | 40178 | MrezaIzpadVklopDelay[4]
PTOMrezaIzpadVklopDelay5 | INT | IOD_PTO_TCP | 179 | 40179 | MrezaIzpadVklopDelay[5]
PTOMrezaIzpadVklopDelay6 | INT | IOD_PTO_TCP | 180 | 40180 | MrezaIzpadVklopDelay[6]
PTOPMMAlarmPhase1C01_16_60to80 | INT | IOD_PTO_TCP | 181 | 40181 | PMM.AlarmPhase[1].C01_16_60to80
PTOPMMAlarmPhase1C01_16_over80 | INT | IOD_PTO_TCP | 182 | 40182 | PMM.AlarmPhase[1].C01_16_over80
PTOPMMAlarmPhase1C17_32_60to80 | INT | IOD_PTO_TCP | 183 | 40183 | PMM.AlarmPhase[1].C17_32_60to80
PTOPMMAlarmPhase1C17_32_over80 | INT | IOD_PTO_TCP | 184 | 40184 | PMM.AlarmPhase[1].C17_32_over80
PTOPMMAlarmPhase1C33_42_60to80 | INT | IOD_PTO_TCP | 185 | 40185 | PMM.AlarmPhase[1].C33_42_60to80
PTOPMMAlarmPhase1C33_42_over80 | INT | IOD_PTO_TCP | 186 | 40186 | PMM.AlarmPhase[1].C33_42_over80
PTOPMMAlarmPhase2C01_16_60to80 | INT | IOD_PTO_TCP | 187 | 40187 | PMM.AlarmPhase[2].C01_16_60to80
PTOPMMAlarmPhase2C01_16_over80 | INT | IOD_PTO_TCP | 188 | 40188 | PMM.AlarmPhase[2].C01_16_over80
PTOPMMAlarmPhase2C17_32_60to80 | INT | IOD_PTO_TCP | 189 | 40189 | PMM.AlarmPhase[2].C17_32_60to80
PTOPMMAlarmPhase2C17_32_over80 | INT | IOD_PTO_TCP | 190 | 40190 | PMM.AlarmPhase[2].C17_32_over80
PTOPMMAlarmPhase2C33_42_60to80 | INT | IOD_PTO_TCP | 191 | 40191 | PMM.AlarmPhase[2].C33_42_60to80
PTOPMMAlarmPhase2C33_42_over80 | INT | IOD_PTO_TCP | 192 | 40192 | PMM.AlarmPhase[2].C33_42_over80
PTOPMMAlarmPhase3C01_16_60to80 | INT | IOD_PTO_TCP | 193 | 40193 | PMM.AlarmPhase[3].C01_16_60to80
PTOPMMAlarmPhase3C01_16_over80 | INT | IOD_PTO_TCP | 194 | 40194 | PMM.AlarmPhase[3].C01_16_over80
PTOPMMAlarmPhase3C17_32_60to80 | INT | IOD_PTO_TCP | 195 | 40195 | PMM.AlarmPhase[3].C17_32_60to80
PTOPMMAlarmPhase3C17_32_over80 | INT | IOD_PTO_TCP | 196 | 40196 | PMM.AlarmPhase[3].C17_32_over80
PTOPMMAlarmPhase3C33_42_60to80 | INT | IOD_PTO_TCP | 197 | 40197 | PMM.AlarmPhase[3].C33_42_60to80
PTOPMMAlarmPhase3C33_42_over80 | INT | IOD_PTO_TCP | 198 | 40198 | PMM.AlarmPhase[3].C33_42_over80
PTOQstanje10 | INT | IOD_PTO_TCP | 199 | 40199 | Qstanje[10] | BYTE
PTOQstanje11 | INT | IOD_PTO_TCP | 200 | 40200 | Qstanje[11] | BYTE
PTOQstanje12 | INT | IOD_PTO_TCP | 201 | 40201 | Qstanje[12] | BYTE
PTOQstanje13 | INT | IOD_PTO_TCP | 202 | 40202 | Qstanje[13] | BYTE
PTOQstanje14 | INT | IOD_PTO_TCP | 203 | 40203 | Qstanje[14] | BYTE
PTOQstanje15 | INT | IOD_PTO_TCP | 204 | 40204 | Qstanje[15] | BYTE
PTOQstanje16 | INT | IOD_PTO_TCP | 205 | 40205 | Qstanje[16] | BYTE
PTOQstanje17 | INT | IOD_PTO_TCP | 206 | 40206 | Qstanje[17] | BYTE
PTOQstanje18 | INT | IOD_PTO_TCP | 207 | 40207 | Qstanje[18] | BYTE
PTOQstanje19 | INT | IOD_PTO_TCP | 208 | 40208 | Qstanje[19] | BYTE
PTOQstanje1 | INT | IOD_PTO_TCP | 209 | 40209 | Qstanje[1] | BYTE
PTOQstanje20 | INT | IOD_PTO_TCP | 210 | 40210 | Qstanje[20] | BYTE
PTOQstanje21 | INT | IOD_PTO_TCP | 211 | 40211 | Qstanje[21] | BYTE
PTOQstanje22 | INT | IOD_PTO_TCP | 212 | 40212 | Qstanje[22] | BYTE
PTOQstanje23 | INT | IOD_PTO_TCP | 213 | 40213 | Qstanje[23] | BYTE
PTOQstanje24 | INT | IOD_PTO_TCP | 214 | 40214 | Qstanje[24] | BYTE
PTOQstanje25 | INT | IOD_PTO_TCP | 215 | 40215 | Qstanje[25] | BYTE
PTOQstanje26 | INT | IOD_PTO_TCP | 216 | 40216 | Qstanje[26] | BYTE
PTOQstanje27 | INT | IOD_PTO_TCP | 217 | 40217 | Qstanje[27] | BYTE
PTOQstanje28 | INT | IOD_PTO_TCP | 218 | 40218 | Qstanje[28] | BYTE
PTOQstanje29 | INT | IOD_PTO_TCP | 219 | 40219 | Qstanje[29] | BYTE
PTOQstanje2 | INT | IOD_PTO_TCP | 220 | 40220 | Qstanje[2] | BYTE
PTOQstanje30 | INT | IOD_PTO_TCP | 221 | 40221 | Qstanje[30] | BYTE
PTOQstanje31 | INT | IOD_PTO_TCP | 222 | 40222 | Qstanje[31] | BYTE
PTOQstanje32 | INT | IOD_PTO_TCP | 223 | 40223 | Qstanje[32] | BYTE
PTOQstanje33 | INT | IOD_PTO_TCP | 224 | 40224 | Qstanje[33] | BYTE
PTOQstanje34 | INT | IOD_PTO_TCP | 225 | 40225 | Qstanje[34] | BYTE
PTOQstanje35 | INT | IOD_PTO_TCP | 226 | 40226 | Qstanje[35] | BYTE
PTOQstanje3 | INT | IOD_PTO_TCP | 227 | 40227 | Qstanje[3] | BYTE
PTOQstanje4 | INT | IOD_PTO_TCP | 228 | 40228 | Qstanje[4] | BYTE
PTOQstanje5 | INT | IOD_PTO_TCP | 229 | 40229 | Qstanje[5] | BYTE
PTOQstanje6 | INT | IOD_PTO_TCP | 230 | 40230 | Qstanje[6] | BYTE
PTOQstanje7 | INT | IOD_PTO_TCP | 231 | 40231 | Qstanje[7] | BYTE
PTOQstanje8 | INT | IOD_PTO_TCP | 232 | 40232 | Qstanje[8] | BYTE
PTOQstanje9 | INT | IOD_PTO_TCP | 233 | 40233 | Qstanje[9] | BYTE
PTOUPS1InverterStatus | INT | IOD_PTO_TCP | 234 | 40234 | UPS[1].InverterStatus
PTOUPS1OutputStatus | INT | IOD_PTO_TCP | 235 | 40235 | UPS[1].OutputStatus
PTOUPS1StatusBaterije | INT | IOD_PTO_TCP | 236 | 40236 | UPS[1].StatusBaterije
PTOUPS1SteviloIzpadovVhodneLinije | INT | IOD_PTO_TCP | 237 | 40237 | UPS[1].SteviloIzpadovVhodneLinije
PTOUPS1UnitStatus | INT | IOD_PTO_TCP | 238 | 40238 | UPS[1].UnitStatus
PTOUPS2InverterStatus | INT | IOD_PTO_TCP | 239 | 40239 | UPS[2].InverterStatus
PTOUPS2OutputStatus | INT | IOD_PTO_TCP | 240 | 40240 | UPS[2].OutputStatus
PTOUPS2StatusBaterije | INT | IOD_PTO_TCP | 241 | 40241 | UPS[2].StatusBaterije
PTOUPS2SteviloIzpadovVhodneLinije | INT | IOD_PTO_TCP | 242 | 40242 | UPS[2].SteviloIzpadovVhodneLinije
PTOUPS2UnitStatus | INT | IOD_PTO_TCP | 243 | 40243 | UPS[2].UnitStatus
PTOUserCurrentLevel | INT | IOD_PTO_TCP | 244 | 40244 | UserCurrentLevel | BYTE
PTOKlima1ObratovalneUre | REAL | IOD_PTO_TCP | 4001 | 44001 | Klima[1].ObratovalneUre
PTOKlima1TemperaturaProstora | REAL | IOD_PTO_TCP | 4003 | 44003 | Klima[1].TemperaturaProstora
PTOKlima1TempIzpihanegaZraka | REAL | IOD_PTO_TCP | 4005 | 44005 | Klima[1].TempIzpihanegaZraka
PTOKlima1VlaznostProstora | REAL | IOD_PTO_TCP | 4007 | 44007 | Klima[1].VlaznostProstora
PTOKlima1ZunanjaTemp | REAL | IOD_PTO_TCP | 4009 | 44009 | Klima[1].ZunanjaTemp
PTOKlima2ObratovalneUre | REAL | IOD_PTO_TCP | 4011 | 44011 | Klima[2].ObratovalneUre
PTOKlima2TemperaturaProstora | REAL | IOD_PTO_TCP | 4013 | 44013 | Klima[2].TemperaturaProstora
PTOKlima2TempIzpihanegaZraka | REAL | IOD_PTO_TCP | 4015 | 44015 | Klima[2].TempIzpihanegaZraka
PTOKlima2VlaznostProstora | REAL | IOD_PTO_TCP | 4017 | 44017 | Klima[2].VlaznostProstora
PTOKlima2ZunanjaTemp | REAL | IOD_PTO_TCP | 4019 | 44019 | Klima[2].ZunanjaTemp
PTOKlima3ObratovalneUre | REAL | IOD_PTO_TCP | 4021 | 44021 | Klima[3].ObratovalneUre
PTOKlima3TemperaturaProstora | REAL | IOD_PTO_TCP | 4023 | 44023 | Klima[3].TemperaturaProstora
PTOKlima3TempIzpihanegaZraka | REAL | IOD_PTO_TCP | 4025 | 44025 | Klima[3].TempIzpihanegaZraka
PTOKlima3VlaznostProstora | REAL | IOD_PTO_TCP | 4027 | 44027 | Klima[3].VlaznostProstora
PTOKlima3ZunanjaTemp | REAL | IOD_PTO_TCP | 4029 | 44029 | Klima[3].ZunanjaTemp
PTOKlima4ObratovalneUre | REAL | IOD_PTO_TCP | 4031 | 44031 | Klima[4].ObratovalneUre
PTOKlima4TemperaturaProstora | REAL | IOD_PTO_TCP | 4033 | 44033 | Klima[4].TemperaturaProstora
PTOKlima4TempIzpihanegaZraka | REAL | IOD_PTO_TCP | 4035 | 44035 | Klima[4].TempIzpihanegaZraka
PTOKlima4VlaznostProstora | REAL | IOD_PTO_TCP | 4037 | 44037 | Klima[4].VlaznostProstora
PTOKlima4ZunanjaTemp | REAL | IOD_PTO_TCP | 4039 | 44039 | Klima[4].ZunanjaTemp
PTOKlima5ObratovalneUre | REAL | IOD_PTO_TCP | 4041 | 44041 | Klima[5].ObratovalneUre
PTOKlima5TemperaturaProstora | REAL | IOD_PTO_TCP | 4043 | 44043 | Klima[5].TemperaturaProstora
PTOKlima5TempIzpihanegaZraka | REAL | IOD_PTO_TCP | 4045 | 44045 | Klima[5].TempIzpihanegaZraka
PTOKlima5VlaznostProstora | REAL | IOD_PTO_TCP | 4047 | 44047 | Klima[5].VlaznostProstora
PTOKlima5ZunanjaTemp | REAL | IOD_PTO_TCP | 4049 | 44049 | Klima[5].ZunanjaTemp
PTOKlima6ObratovalneUre | REAL | IOD_PTO_TCP | 4051 | 44051 | Klima[6].ObratovalneUre
PTOKlima6TemperaturaProstora | REAL | IOD_PTO_TCP | 4053 | 44053 | Klima[6].TemperaturaProstora
PTOKlima6TempIzpihanegaZraka | REAL | IOD_PTO_TCP | 4055 | 44055 | Klima[6].TempIzpihanegaZraka
PTOKlima6VlaznostProstora | REAL | IOD_PTO_TCP | 4057 | 44057 | Klima[6].VlaznostProstora
PTOKlima6ZunanjaTemp | REAL | IOD_PTO_TCP | 4059 | 44059 | Klima[6].ZunanjaTemp
PTOPMMActiveEnergyConsumed_kWh | REAL | IOD_PTO_TCP | 4061 | 44061 | PMM.ActiveEnergyConsumed_kWh
PTOPMMActivePowerPhaseA_kW | REAL | IOD_PTO_TCP | 4063 | 44063 | PMM.ActivePowerPhaseA_kW
PTOPMMActivePowerPhaseB_kW | REAL | IOD_PTO_TCP | 4065 | 44065 | PMM.ActivePowerPhaseB_kW
PTOPMMActivePowerPhaseC_kW | REAL | IOD_PTO_TCP | 4067 | 44067 | PMM.ActivePowerPhaseC_kW
PTOPMMAparentPowerPhaseA | REAL | IOD_PTO_TCP | 4069 | 44069 | PMM.AparentPowerPhaseA
PTOPMMAparentPowerPhaseB | REAL | IOD_PTO_TCP | 4071 | 44071 | PMM.AparentPowerPhaseB
PTOPMMAparentPowerPhaseC | REAL | IOD_PTO_TCP | 4073 | 44073 | PMM.AparentPowerPhaseC
PTOPMMAverageCurrent_A | REAL | IOD_PTO_TCP | 4075 | 44075 | PMM.AverageCurrent_A
PTOPMMAveragePhaseToNeutral_V | REAL | IOD_PTO_TCP | 4077 | 44077 | PMM.AveragePhaseToNeutral_V
PTOPMMAveragePhaseToPhase_V | REAL | IOD_PTO_TCP | 4079 | 44079 | PMM.AveragePhaseToPhase_V
PTOPMMCurrentInPhaseA_A | REAL | IOD_PTO_TCP | 4081 | 44081 | PMM.CurrentInPhaseA_A
PTOPMMCurrentInPhaseB_A | REAL | IOD_PTO_TCP | 4083 | 44083 | PMM.CurrentInPhaseB_A
PTOPMMCurrentInPhaseC_A | REAL | IOD_PTO_TCP | 4085 | 44085 | PMM.CurrentInPhaseC_A
PTOPMMFrequency_Hz | REAL | IOD_PTO_TCP | 4087 | 44087 | PMM.Frequency_Hz
PTOPMMPhase1Current10 | REAL | IOD_PTO_TCP | 4089 | 44089 | PMM.Phase[1].Current[10]
PTOPMMPhase1Current11 | REAL | IOD_PTO_TCP | 4091 | 44091 | PMM.Phase[1].Current[11]
PTOPMMPhase1Current12 | REAL | IOD_PTO_TCP | 4093 | 44093 | PMM.Phase[1].Current[12]
PTOPMMPhase1Current13 | REAL | IOD_PTO_TCP | 4095 | 44095 | PMM.Phase[1].Current[13]
PTOPMMPhase1Current14 | REAL | IOD_PTO_TCP | 4097 | 44097 | PMM.Phase[1].Current[14]
PTOPMMPhase1Current15 | REAL | IOD_PTO_TCP | 4099 | 44099 | PMM.Phase[1].Current[15]
PTOPMMPhase1Current16 | REAL | IOD_PTO_TCP | 4101 | 44101 | PMM.Phase[1].Current[16]
PTOPMMPhase1Current17 | REAL | IOD_PTO_TCP | 4103 | 44103 | PMM.Phase[1].Current[17]
PTOPMMPhase1Current18 | REAL | IOD_PTO_TCP | 4105 | 44105 | PMM.Phase[1].Current[18]
PTOPMMPhase1Current19 | REAL | IOD_PTO_TCP | 4107 | 44107 | PMM.Phase[1].Current[19]
PTOPMMPhase1Current1 | REAL | IOD_PTO_TCP | 4109 | 44109 | PMM.Phase[1].Current[1]
PTOPMMPhase1Current20 | REAL | IOD_PTO_TCP | 4111 | 44111 | PMM.Phase[1].Current[20]
PTOPMMPhase1Current21 | REAL | IOD_PTO_TCP | 4113 | 44113 | PMM.Phase[1].Current[21]
PTOPMMPhase1Current22 | REAL | IOD_PTO_TCP | 4115 | 44115 | PMM.Phase[1].Current[22]
PTOPMMPhase1Current23 | REAL | IOD_PTO_TCP | 4117 | 44117 | PMM.Phase[1].Current[23]
PTOPMMPhase1Current24 | REAL | IOD_PTO_TCP | 4119 | 44119 | PMM.Phase[1].Current[24]
PTOPMMPhase1Current25 | REAL | IOD_PTO_TCP | 4121 | 44121 | PMM.Phase[1].Current[25]
PTOPMMPhase1Current26 | REAL | IOD_PTO_TCP | 4123 | 44123 | PMM.Phase[1].Current[26]
PTOPMMPhase1Current27 | REAL | IOD_PTO_TCP | 4125 | 44125 | PMM.Phase[1].Current[27]
PTOPMMPhase1Current28 | REAL | IOD_PTO_TCP | 4127 | 44127 | PMM.Phase[1].Current[28]
PTOPMMPhase1Current29 | REAL | IOD_PTO_TCP | 4129 | 44129 | PMM.Phase[1].Current[29]
PTOPMMPhase1Current2 | REAL | IOD_PTO_TCP | 4131 | 44131 | PMM.Phase[1].Current[2]
PTOPMMPhase1Current30 | REAL | IOD_PTO_TCP | 4133 | 44133 | PMM.Phase[1].Current[30]
PTOPMMPhase1Current31 | REAL | IOD_PTO_TCP | 4135 | 44135 | PMM.Phase[1].Current[31]
PTOPMMPhase1Current32 | REAL | IOD_PTO_TCP | 4137 | 44137 | PMM.Phase[1].Current[32]
PTOPMMPhase1Current33 | REAL | IOD_PTO_TCP | 4139 | 44139 | PMM.Phase[1].Current[33]
PTOPMMPhase1Current34 | REAL | IOD_PTO_TCP | 4141 | 44141 | PMM.Phase[1].Current[34]
PTOPMMPhase1Current35 | REAL | IOD_PTO_TCP | 4143 | 44143 | PMM.Phase[1].Current[35]
PTOPMMPhase1Current36 | REAL | IOD_PTO_TCP | 4145 | 44145 | PMM.Phase[1].Current[36]
PTOPMMPhase1Current37 | REAL | IOD_PTO_TCP | 4147 | 44147 | PMM.Phase[1].Current[37]
PTOPMMPhase1Current38 | REAL | IOD_PTO_TCP | 4149 | 44149 | PMM.Phase[1].Current[38]
PTOPMMPhase1Current39 | REAL | IOD_PTO_TCP | 4151 | 44151 | PMM.Phase[1].Current[39]
PTOPMMPhase1Current3 | REAL | IOD_PTO_TCP | 4153 | 44153 | PMM.Phase[1].Current[3]
PTOPMMPhase1Current40 | REAL | IOD_PTO_TCP | 4155 | 44155 | PMM.Phase[1].Current[40]
PTOPMMPhase1Current41 | REAL | IOD_PTO_TCP | 4157 | 44157 | PMM.Phase[1].Current[41]
PTOPMMPhase1Current42 | REAL | IOD_PTO_TCP | 4159 | 44159 | PMM.Phase[1].Current[42]
PTOPMMPhase1Current4 | REAL | IOD_PTO_TCP | 4161 | 44161 | PMM.Phase[1].Current[4]
PTOPMMPhase1Current5 | REAL | IOD_PTO_TCP | 4163 | 44163 | PMM.Phase[1].Current[5]
PTOPMMPhase1Current6 | REAL | IOD_PTO_TCP | 4165 | 44165 | PMM.Phase[1].Current[6]
PTOPMMPhase1Current7 | REAL | IOD_PTO_TCP | 4167 | 44167 | PMM.Phase[1].Current[7]
PTOPMMPhase1Current8 | REAL | IOD_PTO_TCP | 4169 | 44169 | PMM.Phase[1].Current[8]
PTOPMMPhase1Current9 | REAL | IOD_PTO_TCP | 4171 | 44171 | PMM.Phase[1].Current[9]
PTOPMMPhase2Current10 | REAL | IOD_PTO_TCP | 4173 | 44173 | PMM.Phase[2].Current[10]
PTOPMMPhase2Current11 | REAL | IOD_PTO_TCP | 4175 | 44175 | PMM.Phase[2].Current[11]
PTOPMMPhase2Current12 | REAL | IOD_PTO_TCP | 4177 | 44177 | PMM.Phase[2].Current[12]
PTOPMMPhase2Current13 | REAL | IOD_PTO_TCP | 4179 | 44179 | PMM.Phase[2].Current[13]
PTOPMMPhase2Current14 | REAL | IOD_PTO_TCP | 4181 | 44181 | PMM.Phase[2].Current[14]
PTOPMMPhase2Current15 | REAL | IOD_PTO_TCP | 4183 | 44183 | PMM.Phase[2].Current[15]
PTOPMMPhase2Current16 | REAL | IOD_PTO_TCP | 4185 | 44185 | PMM.Phase[2].Current[16]
PTOPMMPhase2Current17 | REAL | IOD_PTO_TCP | 4187 | 44187 | PMM.Phase[2].Current[17]
PTOPMMPhase2Current18 | REAL | IOD_PTO_TCP | 4189 | 44189 | PMM.Phase[2].Current[18]
PTOPMMPhase2Current19 | REAL | IOD_PTO_TCP | 4191 | 44191 | PMM.Phase[2].Current[19]
PTOPMMPhase2Current1 | REAL | IOD_PTO_TCP | 4193 | 44193 | PMM.Phase[2].Current[1]
PTOPMMPhase2Current20 | REAL | IOD_PTO_TCP | 4195 | 44195 | PMM.Phase[2].Current[20]
PTOPMMPhase2Current21 | REAL | IOD_PTO_TCP | 4197 | 44197 | PMM.Phase[2].Current[21]
PTOPMMPhase2Current22 | REAL | IOD_PTO_TCP | 4199 | 44199 | PMM.Phase[2].Current[22]
PTOPMMPhase2Current23 | REAL | IOD_PTO_TCP | 4201 | 44201 | PMM.Phase[2].Current[23]
PTOPMMPhase2Current24 | REAL | IOD_PTO_TCP | 4203 | 44203 | PMM.Phase[2].Current[24]
PTOPMMPhase2Current25 | REAL | IOD_PTO_TCP | 4205 | 44205 | PMM.Phase[2].Current[25]
PTOPMMPhase2Current26 | REAL | IOD_PTO_TCP | 4207 | 44207 | PMM.Phase[2].Current[26]
PTOPMMPhase2Current27 | REAL | IOD_PTO_TCP | 4209 | 44209 | PMM.Phase[2].Current[27]
PTOPMMPhase2Current28 | REAL | IOD_PTO_TCP | 4211 | 44211 | PMM.Phase[2].Current[28]
PTOPMMPhase2Current29 | REAL | IOD_PTO_TCP | 4213 | 44213 | PMM.Phase[2].Current[29]
PTOPMMPhase2Current2 | REAL | IOD_PTO_TCP | 4215 | 44215 | PMM.Phase[2].Current[2]
PTOPMMPhase2Current30 | REAL | IOD_PTO_TCP | 4217 | 44217 | PMM.Phase[2].Current[30]
PTOPMMPhase2Current31 | REAL | IOD_PTO_TCP | 4219 | 44219 | PMM.Phase[2].Current[31]
PTOPMMPhase2Current32 | REAL | IOD_PTO_TCP | 4221 | 44221 | PMM.Phase[2].Current[32]
PTOPMMPhase2Current33 | REAL | IOD_PTO_TCP | 4223 | 44223 | PMM.Phase[2].Current[33]
PTOPMMPhase2Current34 | REAL | IOD_PTO_TCP | 4225 | 44225 | PMM.Phase[2].Current[34]
PTOPMMPhase2Current35 | REAL | IOD_PTO_TCP | 4227 | 44227 | PMM.Phase[2].Current[35]
PTOPMMPhase2Current36 | REAL | IOD_PTO_TCP | 4229 | 44229 | PMM.Phase[2].Current[36]
PTOPMMPhase2Current37 | REAL | IOD_PTO_TCP | 4231 | 44231 | PMM.Phase[2].Current[37]
PTOPMMPhase2Current38 | REAL | IOD_PTO_TCP | 4233 | 44233 | PMM.Phase[2].Current[38]
PTOPMMPhase2Current39 | REAL | IOD_PTO_TCP | 4235 | 44235 | PMM.Phase[2].Current[39]
PTOPMMPhase2Current3 | REAL | IOD_PTO_TCP | 4237 | 44237 | PMM.Phase[2].Current[3]
PTOPMMPhase2Current40 | REAL | IOD_PTO_TCP | 4239 | 44239 | PMM.Phase[2].Current[40]
PTOPMMPhase2Current41 | REAL | IOD_PTO_TCP | 4241 | 44241 | PMM.Phase[2].Current[41]
PTOPMMPhase2Current42 | REAL | IOD_PTO_TCP | 4243 | 44243 | PMM.Phase[2].Current[42]
PTOPMMPhase2Current4 | REAL | IOD_PTO_TCP | 4245 | 44245 | PMM.Phase[2].Current[4]
PTOPMMPhase2Current5 | REAL | IOD_PTO_TCP | 4247 | 44247 | PMM.Phase[2].Current[5]
PTOPMMPhase2Current6 | REAL | IOD_PTO_TCP | 4249 | 44249 | PMM.Phase[2].Current[6]
PTOPMMPhase2Current7 | REAL | IOD_PTO_TCP | 4251 | 44251 | PMM.Phase[2].Current[7]
PTOPMMPhase2Current8 | REAL | IOD_PTO_TCP | 4253 | 44253 | PMM.Phase[2].Current[8]
PTOPMMPhase2Current9 | REAL | IOD_PTO_TCP | 4255 | 44255 | PMM.Phase[2].Current[9]
PTOPMMPhase3Current10 | REAL | IOD_PTO_TCP | 4257 | 44257 | PMM.Phase[3].Current[10]
PTOPMMPhase3Current11 | REAL | IOD_PTO_TCP | 4259 | 44259 | PMM.Phase[3].Current[11]
PTOPMMPhase3Current12 | REAL | IOD_PTO_TCP | 4261 | 44261 | PMM.Phase[3].Current[12]
PTOPMMPhase3Current13 | REAL | IOD_PTO_TCP | 4263 | 44263 | PMM.Phase[3].Current[13]
PTOPMMPhase3Current14 | REAL | IOD_PTO_TCP | 4265 | 44265 | PMM.Phase[3].Current[14]
PTOPMMPhase3Current15 | REAL | IOD_PTO_TCP | 4267 | 44267 | PMM.Phase[3].Current[15]
PTOPMMPhase3Current16 | REAL | IOD_PTO_TCP | 4269 | 44269 | PMM.Phase[3].Current[16]
PTOPMMPhase3Current17 | REAL | IOD_PTO_TCP | 4271 | 44271 | PMM.Phase[3].Current[17]
PTOPMMPhase3Current18 | REAL | IOD_PTO_TCP | 4273 | 44273 | PMM.Phase[3].Current[18]
PTOPMMPhase3Current19 | REAL | IOD_PTO_TCP | 4275 | 44275 | PMM.Phase[3].Current[19]
PTOPMMPhase3Current1 | REAL | IOD_PTO_TCP | 4277 | 44277 | PMM.Phase[3].Current[1]
PTOPMMPhase3Current20 | REAL | IOD_PTO_TCP | 4279 | 44279 | PMM.Phase[3].Current[20]
PTOPMMPhase3Current21 | REAL | IOD_PTO_TCP | 4281 | 44281 | PMM.Phase[3].Current[21]
PTOPMMPhase3Current22 | REAL | IOD_PTO_TCP | 4283 | 44283 | PMM.Phase[3].Current[22]
PTOPMMPhase3Current23 | REAL | IOD_PTO_TCP | 4285 | 44285 | PMM.Phase[3].Current[23]
PTOPMMPhase3Current24 | REAL | IOD_PTO_TCP | 4287 | 44287 | PMM.Phase[3].Current[24]
PTOPMMPhase3Current25 | REAL | IOD_PTO_TCP | 4289 | 44289 | PMM.Phase[3].Current[25]
PTOPMMPhase3Current26 | REAL | IOD_PTO_TCP | 4291 | 44291 | PMM.Phase[3].Current[26]
PTOPMMPhase3Current27 | REAL | IOD_PTO_TCP | 4293 | 44293 | PMM.Phase[3].Current[27]
PTOPMMPhase3Current28 | REAL | IOD_PTO_TCP | 4295 | 44295 | PMM.Phase[3].Current[28]
PTOPMMPhase3Current29 | REAL | IOD_PTO_TCP | 4297 | 44297 | PMM.Phase[3].Current[29]
PTOPMMPhase3Current2 | REAL | IOD_PTO_TCP | 4299 | 44299 | PMM.Phase[3].Current[2]
PTOPMMPhase3Current30 | REAL | IOD_PTO_TCP | 4301 | 44301 | PMM.Phase[3].Current[30]
PTOPMMPhase3Current31 | REAL | IOD_PTO_TCP | 4303 | 44303 | PMM.Phase[3].Current[31]
PTOPMMPhase3Current32 | REAL | IOD_PTO_TCP | 4305 | 44305 | PMM.Phase[3].Current[32]
PTOPMMPhase3Current33 | REAL | IOD_PTO_TCP | 4307 | 44307 | PMM.Phase[3].Current[33]
PTOPMMPhase3Current34 | REAL | IOD_PTO_TCP | 4309 | 44309 | PMM.Phase[3].Current[34]
PTOPMMPhase3Current35 | REAL | IOD_PTO_TCP | 4311 | 44311 | PMM.Phase[3].Current[35]
PTOPMMPhase3Current36 | REAL | IOD_PTO_TCP | 4313 | 44313 | PMM.Phase[3].Current[36]
PTOPMMPhase3Current37 | REAL | IOD_PTO_TCP | 4315 | 44315 | PMM.Phase[3].Current[37]
PTOPMMPhase3Current38 | REAL | IOD_PTO_TCP | 4317 | 44317 | PMM.Phase[3].Current[38]
PTOPMMPhase3Current39 | REAL | IOD_PTO_TCP | 4319 | 44319 | PMM.Phase[3].Current[39]
PTOPMMPhase3Current3 | REAL | IOD_PTO_TCP | 4321 | 44321 | PMM.Phase[3].Current[3]
PTOPMMPhase3Current40 | REAL | IOD_PTO_TCP | 4323 | 44323 | PMM.Phase[3].Current[40]
PTOPMMPhase3Current41 | REAL | IOD_PTO_TCP | 4325 | 44325 | PMM.Phase[3].Current[41]
PTOPMMPhase3Current42 | REAL | IOD_PTO_TCP | 4327 | 44327 | PMM.Phase[3].Current[42]
PTOPMMPhase3Current4 | REAL | IOD_PTO_TCP | 4329 | 44329 | PMM.Phase[3].Current[4]
PTOPMMPhase3Current5 | REAL | IOD_PTO_TCP | 4331 | 44331 | PMM.Phase[3].Current[5]
PTOPMMPhase3Current6 | REAL | IOD_PTO_TCP | 4333 | 44333 | PMM.Phase[3].Current[6]
PTOPMMPhase3Current7 | REAL | IOD_PTO_TCP | 4335 | 44335 | PMM.Phase[3].Current[7]
PTOPMMPhase3Current8 | REAL | IOD_PTO_TCP | 4337 | 44337 | PMM.Phase[3].Current[8]
PTOPMMPhase3Current9 | REAL | IOD_PTO_TCP | 4339 | 44339 | PMM.Phase[3].Current[9]
PTOPMMPowerFactorSys | REAL | IOD_PTO_TCP | 4341 | 44341 | PMM.PowerFactorSys
PTOPMMReactiveEnergyConsumed_kVARh | REAL | IOD_PTO_TCP | 4343 | 44343 | PMM.ReactiveEnergyConsumed_kVARh
PTOPMMReactivePowerPhaseA | REAL | IOD_PTO_TCP | 4345 | 44345 | PMM.ReactivePowerPhaseA
PTOPMMReactivePowerPhaseB | REAL | IOD_PTO_TCP | 4347 | 44347 | PMM.ReactivePowerPhaseB
PTOPMMReactivePowerPhaseC | REAL | IOD_PTO_TCP | 4349 | 44349 | PMM.ReactivePowerPhaseC
PTOPMMTotalActivePower_kW | REAL | IOD_PTO_TCP | 4351 | 44351 | PMM.TotalActivePower_kW
PTOPMMTotalAparentPower_kVA | REAL | IOD_PTO_TCP | 4353 | 44353 | PMM.TotalAparentPower_kVA
PTOPMMTotalPowerFactor | REAL | IOD_PTO_TCP | 4355 | 44355 | PMM.TotalPowerFactor
PTOPMMTotalReactivePower_kVAR | REAL | IOD_PTO_TCP | 4357 | 44357 | PMM.TotalReactivePower_kVAR
PTOPMMVirA_fsys | REAL | IOD_PTO_TCP | 4359 | 44359 | PMM.VirA_fsys
PTOPMMVirA_Isys | REAL | IOD_PTO_TCP | 4361 | 44361 | PMM.VirA_Isys
PTOPMMVirA_PFsys | REAL | IOD_PTO_TCP | 4363 | 44363 | PMM.VirA_PFsys
PTOPMMVirA_Psys | REAL | IOD_PTO_TCP | 4365 | 44365 | PMM.VirA_Psys
PTOPMMVirA_Qsys | REAL | IOD_PTO_TCP | 4367 | 44367 | PMM.VirA_Qsys
PTOPMMVirA_Ssys | REAL | IOD_PTO_TCP | 4369 | 44369 | PMM.VirA_Ssys
PTOPMMVirA_Usys | REAL | IOD_PTO_TCP | 4371 | 44371 | PMM.VirA_Usys
PTOPMMVirB_fsys | REAL | IOD_PTO_TCP | 4373 | 44373 | PMM.VirB_fsys
PTOPMMVirB_Isys | REAL | IOD_PTO_TCP | 4375 | 44375 | PMM.VirB_Isys
PTOPMMVirB_PFsys | REAL | IOD_PTO_TCP | 4377 | 44377 | PMM.VirB_PFsys
PTOPMMVirB_Psys | REAL | IOD_PTO_TCP | 4379 | 44379 | PMM.VirB_Psys
PTOPMMVirB_Qsys | REAL | IOD_PTO_TCP | 4381 | 44381 | PMM.VirB_Qsys
PTOPMMVirB_Ssys | REAL | IOD_PTO_TCP | 4383 | 44383 | PMM.VirB_Ssys
PTOPMMVirB_Usys | REAL | IOD_PTO_TCP | 4385 | 44385 | PMM.VirB_Usys
PTOPMMVirBActiveEnergyConsumed_kWh | REAL | IOD_PTO_TCP | 4387 | 44387 | PMM.VirBActiveEnergyConsumed_kWh
PTOPMMVirBActivePowerPhaseA_kW | REAL | IOD_PTO_TCP | 4389 | 44389 | PMM.VirBActivePowerPhaseA_kW
PTOPMMVirBActivePowerPhaseB_kW | REAL | IOD_PTO_TCP | 4391 | 44391 | PMM.VirBActivePowerPhaseB_kW
PTOPMMVirBActivePowerPhaseC_kW | REAL | IOD_PTO_TCP | 4393 | 44393 | PMM.VirBActivePowerPhaseC_kW
PTOPMMVirBAparentPowerPhaseA | REAL | IOD_PTO_TCP | 4395 | 44395 | PMM.VirBAparentPowerPhaseA
PTOPMMVirBAparentPowerPhaseB | REAL | IOD_PTO_TCP | 4397 | 44397 | PMM.VirBAparentPowerPhaseB
PTOPMMVirBAparentPowerPhaseC | REAL | IOD_PTO_TCP | 4399 | 44399 | PMM.VirBAparentPowerPhaseC
PTOPMMVirBAverageCurrent_A | REAL | IOD_PTO_TCP | 4401 | 44401 | PMM.VirBAverageCurrent_A
PTOPMMVirBAveragePhaseToNeutral_V | REAL | IOD_PTO_TCP | 4403 | 44403 | PMM.VirBAveragePhaseToNeutral_V
PTOPMMVirBAveragePhaseToPhase_V | REAL | IOD_PTO_TCP | 4405 | 44405 | PMM.VirBAveragePhaseToPhase_V
PTOPMMVirBCurrentInPhaseA_A | REAL | IOD_PTO_TCP | 4407 | 44407 | PMM.VirBCurrentInPhaseA_A
PTOPMMVirBCurrentInPhaseB_A | REAL | IOD_PTO_TCP | 4409 | 44409 | PMM.VirBCurrentInPhaseB_A
PTOPMMVirBCurrentInPhaseC_A | REAL | IOD_PTO_TCP | 4411 | 44411 | PMM.VirBCurrentInPhaseC_A
PTOPMMVirBFrequency_Hz | REAL | IOD_PTO_TCP | 4413 | 44413 | PMM.VirBFrequency_Hz
PTOPMMVirBPowerFactorSys | REAL | IOD_PTO_TCP | 4415 | 44415 | PMM.VirBPowerFactorSys
PTOPMMVirBReactiveEnergyConsumed_kVARh | REAL | IOD_PTO_TCP | 4417 | 44417 | PMM.VirBReactiveEnergyConsumed_kVARh
PTOPMMVirBReactivePowerPhaseA | REAL | IOD_PTO_TCP | 4419 | 44419 | PMM.VirBReactivePowerPhaseA
PTOPMMVirBReactivePowerPhaseB | REAL | IOD_PTO_TCP | 4421 | 44421 | PMM.VirBReactivePowerPhaseB
PTOPMMVirBReactivePowerPhaseC | REAL | IOD_PTO_TCP | 4423 | 44423 | PMM.VirBReactivePowerPhaseC
PTOPMMVirBTotalActivePower_kW | REAL | IOD_PTO_TCP | 4425 | 44425 | PMM.VirBTotalActivePower_kW
PTOPMMVirBTotalAparentPower_kVA | REAL | IOD_PTO_TCP | 4427 | 44427 | PMM.VirBTotalAparentPower_kVA
PTOPMMVirBTotalPowerFactor | REAL | IOD_PTO_TCP | 4429 | 44429 | PMM.VirBTotalPowerFactor
PTOPMMVirBTotalReactivePower_kVAR | REAL | IOD_PTO_TCP | 4431 | 44431 | PMM.VirBTotalReactivePower_kVAR
PTOPMMVirBVoltageBetweenPhaseAB_V | REAL | IOD_PTO_TCP | 4433 | 44433 | PMM.VirBVoltageBetweenPhaseAB_V
PTOPMMVirBVoltageBetweenPhaseAN_V | REAL | IOD_PTO_TCP | 4435 | 44435 | PMM.VirBVoltageBetweenPhaseAN_V
PTOPMMVirBVoltageBetweenPhaseBC_V | REAL | IOD_PTO_TCP | 4437 | 44437 | PMM.VirBVoltageBetweenPhaseBC_V
PTOPMMVirBVoltageBetweenPhaseBN_V | REAL | IOD_PTO_TCP | 4439 | 44439 | PMM.VirBVoltageBetweenPhaseBN_V
PTOPMMVirBVoltageBetweenPhaseCA_V | REAL | IOD_PTO_TCP | 4441 | 44441 | PMM.VirBVoltageBetweenPhaseCA_V
PTOPMMVirBVoltageBetweenPhaseCN_V | REAL | IOD_PTO_TCP | 4443 | 44443 | PMM.VirBVoltageBetweenPhaseCN_V
PTOPMMVoltageBetweenPhaseAB_V | REAL | IOD_PTO_TCP | 4445 | 44445 | PMM.VoltageBetweenPhaseAB_V
PTOPMMVoltageBetweenPhaseAN_V | REAL | IOD_PTO_TCP | 4447 | 44447 | PMM.VoltageBetweenPhaseAN_V
PTOPMMVoltageBetweenPhaseBC_V | REAL | IOD_PTO_TCP | 4449 | 44449 | PMM.VoltageBetweenPhaseBC_V
PTOPMMVoltageBetweenPhaseBN_V | REAL | IOD_PTO_TCP | 4451 | 44451 | PMM.VoltageBetweenPhaseBN_V
PTOPMMVoltageBetweenPhaseCA_V | REAL | IOD_PTO_TCP | 4453 | 44453 | PMM.VoltageBetweenPhaseCA_V
PTOPMMVoltageBetweenPhaseCN_V | REAL | IOD_PTO_TCP | 4455 | 44455 | PMM.VoltageBetweenPhaseCN_V
PTOPMMfaza01 | REAL | IOD_PTO_TCP | 4457 | 44457 | PMMfaza01
PTOPMMfaza02 | REAL | IOD_PTO_TCP | 4459 | 44459 | PMMfaza02
PTOPMMfaza03 | REAL | IOD_PTO_TCP | 4461 | 44461 | PMMfaza03
PTOPMMfaza04 | REAL | IOD_PTO_TCP | 4463 | 44463 | PMMfaza04
PTOPMMfaza05 | REAL | IOD_PTO_TCP | 4465 | 44465 | PMMfaza05
PTOPMMfaza06 | REAL | IOD_PTO_TCP | 4467 | 44467 | PMMfaza06
PTOPMMfaza07 | REAL | IOD_PTO_TCP | 4469 | 44469 | PMMfaza07
PTOPMMfaza08 | REAL | IOD_PTO_TCP | 4471 | 44471 | PMMfaza08
PTOPMMfaza09 | REAL | IOD_PTO_TCP | 4473 | 44473 | PMMfaza09
PTOPMMfaza10 | REAL | IOD_PTO_TCP | 4475 | 44475 | PMMfaza10
PTOPMMfaza11 | REAL | IOD_PTO_TCP | 4477 | 44477 | PMMfaza11
PTOPMMfaza12 | REAL | IOD_PTO_TCP | 4479 | 44479 | PMMfaza12
PTOPMMfaza13 | REAL | IOD_PTO_TCP | 4481 | 44481 | PMMfaza13
PTOPMMfaza14 | REAL | IOD_PTO_TCP | 4483 | 44483 | PMMfaza14
PTOPMMfaza15 | REAL | IOD_PTO_TCP | 4485 | 44485 | PMMfaza15
PTOPMMfaza16 | REAL | IOD_PTO_TCP | 4487 | 44487 | PMMfaza16
PTOPMMfaza17 | REAL | IOD_PTO_TCP | 4489 | 44489 | PMMfaza17
PTOPMMfaza18 | REAL | IOD_PTO_TCP | 4491 | 44491 | PMMfaza18
PTOPMMfaza19 | REAL | IOD_PTO_TCP | 4493 | 44493 | PMMfaza19
PTOPMMfaza20 | REAL | IOD_PTO_TCP | 4495 | 44495 | PMMfaza20
PTOPMMfaza21 | REAL | IOD_PTO_TCP | 4497 | 44497 | PMMfaza21
PTOPMMfaza22 | REAL | IOD_PTO_TCP | 4499 | 44499 | PMMfaza22
PTOPMMfaza23 | REAL | IOD_PTO_TCP | 4501 | 44501 | PMMfaza23
PTOPMMfaza24 | REAL | IOD_PTO_TCP | 4503 | 44503 | PMMfaza24
PTOPMMfaza25 | REAL | IOD_PTO_TCP | 4505 | 44505 | PMMfaza25
PTOPMMfaza26 | REAL | IOD_PTO_TCP | 4507 | 44507 | PMMfaza26
PTOPMMfaza27 | REAL | IOD_PTO_TCP | 4509 | 44509 | PMMfaza27
PTOPMMfaza28 | REAL | IOD_PTO_TCP | 4511 | 44511 | PMMfaza28
PTOPMMfaza29 | REAL | IOD_PTO_TCP | 4513 | 44513 | PMMfaza29
PTOPMMfaza30 | REAL | IOD_PTO_TCP | 4515 | 44515 | PMMfaza30
PTOPMMfaza31 | REAL | IOD_PTO_TCP | 4517 | 44517 | PMMfaza31
PTOPMMfaza32 | REAL | IOD_PTO_TCP | 4519 | 44519 | PMMfaza32
PTOPMMfaza33 | REAL | IOD_PTO_TCP | 4521 | 44521 | PMMfaza33
PTOPMMfaza34 | REAL | IOD_PTO_TCP | 4523 | 44523 | PMMfaza34
PTOPMMfaza35 | REAL | IOD_PTO_TCP | 4525 | 44525 | PMMfaza35
PTOPMMfaza36 | REAL | IOD_PTO_TCP | 4527 | 44527 | PMMfaza36
PTOPMMfaza37 | REAL | IOD_PTO_TCP | 4529 | 44529 | PMMfaza37
PTOPMMfaza38 | REAL | IOD_PTO_TCP | 4531 | 44531 | PMMfaza38
PTOPMMfaza39 | REAL | IOD_PTO_TCP | 4533 | 44533 | PMMfaza39
PTOPMMfaza40 | REAL | IOD_PTO_TCP | 4535 | 44535 | PMMfaza40
PTOPMMfaza41 | REAL | IOD_PTO_TCP | 4537 | 44537 | PMMfaza41
PTOPMMfaza42 | REAL | IOD_PTO_TCP | 4539 | 44539 | PMMfaza42
PTOPMMfaza6010 | REAL | IOD_PTO_TCP | 4541 | 44541 | PMMfaza60[10]
PTOPMMfaza6011 | REAL | IOD_PTO_TCP | 4543 | 44543 | PMMfaza60[11]
PTOPMMfaza6012 | REAL | IOD_PTO_TCP | 4545 | 44545 | PMMfaza60[12]
PTOPMMfaza6013 | REAL | IOD_PTO_TCP | 4547 | 44547 | PMMfaza60[13]
PTOPMMfaza6014 | REAL | IOD_PTO_TCP | 4549 | 44549 | PMMfaza60[14]
PTOPMMfaza6015 | REAL | IOD_PTO_TCP | 4551 | 44551 | PMMfaza60[15]
PTOPMMfaza6016 | REAL | IOD_PTO_TCP | 4553 | 44553 | PMMfaza60[16]
PTOPMMfaza6017 | REAL | IOD_PTO_TCP | 4555 | 44555 | PMMfaza60[17]
PTOPMMfaza6018 | REAL | IOD_PTO_TCP | 4557 | 44557 | PMMfaza60[18]
PTOPMMfaza6019 | REAL | IOD_PTO_TCP | 4559 | 44559 | PMMfaza60[19]
PTOPMMfaza601 | REAL | IOD_PTO_TCP | 4561 | 44561 | PMMfaza60[1]
PTOPMMfaza6020 | REAL | IOD_PTO_TCP | 4563 | 44563 | PMMfaza60[20]
PTOPMMfaza6021 | REAL | IOD_PTO_TCP | 4565 | 44565 | PMMfaza60[21]
PTOPMMfaza6022 | REAL | IOD_PTO_TCP | 4567 | 44567 | PMMfaza60[22]
PTOPMMfaza6023 | REAL | IOD_PTO_TCP | 4569 | 44569 | PMMfaza60[23]
PTOPMMfaza6024 | REAL | IOD_PTO_TCP | 4571 | 44571 | PMMfaza60[24]
PTOPMMfaza6025 | REAL | IOD_PTO_TCP | 4573 | 44573 | PMMfaza60[25]
PTOPMMfaza6026 | REAL | IOD_PTO_TCP | 4575 | 44575 | PMMfaza60[26]
PTOPMMfaza6027 | REAL | IOD_PTO_TCP | 4577 | 44577 | PMMfaza60[27]
PTOPMMfaza6028 | REAL | IOD_PTO_TCP | 4579 | 44579 | PMMfaza60[28]
PTOPMMfaza6029 | REAL | IOD_PTO_TCP | 4581 | 44581 | PMMfaza60[29]
PTOPMMfaza602 | REAL | IOD_PTO_TCP | 4583 | 44583 | PMMfaza60[2]
PTOPMMfaza6030 | REAL | IOD_PTO_TCP | 4585 | 44585 | PMMfaza60[30]
PTOPMMfaza6031 | REAL | IOD_PTO_TCP | 4587 | 44587 | PMMfaza60[31]
PTOPMMfaza6032 | REAL | IOD_PTO_TCP | 4589 | 44589 | PMMfaza60[32]
PTOPMMfaza6033 | REAL | IOD_PTO_TCP | 4591 | 44591 | PMMfaza60[33]
PTOPMMfaza6034 | REAL | IOD_PTO_TCP | 4593 | 44593 | PMMfaza60[34]
PTOPMMfaza6035 | REAL | IOD_PTO_TCP | 4595 | 44595 | PMMfaza60[35]
PTOPMMfaza6036 | REAL | IOD_PTO_TCP | 4597 | 44597 | PMMfaza60[36]
PTOPMMfaza6037 | REAL | IOD_PTO_TCP | 4599 | 44599 | PMMfaza60[37]
PTOPMMfaza6038 | REAL | IOD_PTO_TCP | 4601 | 44601 | PMMfaza60[38]
PTOPMMfaza6039 | REAL | IOD_PTO_TCP | 4603 | 44603 | PMMfaza60[39]
PTOPMMfaza603 | REAL | IOD_PTO_TCP | 4605 | 44605 | PMMfaza60[3]
PTOPMMfaza6040 | REAL | IOD_PTO_TCP | 4607 | 44607 | PMMfaza60[40]
PTOPMMfaza6041 | REAL | IOD_PTO_TCP | 4609 | 44609 | PMMfaza60[41]
PTOPMMfaza6042 | REAL | IOD_PTO_TCP | 4611 | 44611 | PMMfaza60[42]
PTOPMMfaza604 | REAL | IOD_PTO_TCP | 4613 | 44613 | PMMfaza60[4]
PTOPMMfaza605 | REAL | IOD_PTO_TCP | 4615 | 44615 | PMMfaza60[5]
PTOPMMfaza606 | REAL | IOD_PTO_TCP | 4617 | 44617 | PMMfaza60[6]
PTOPMMfaza607 | REAL | IOD_PTO_TCP | 4619 | 44619 | PMMfaza60[7]
PTOPMMfaza608 | REAL | IOD_PTO_TCP | 4621 | 44621 | PMMfaza60[8]
PTOPMMfaza609 | REAL | IOD_PTO_TCP | 4623 | 44623 | PMMfaza60[9]
PTOPMMfaza8010 | REAL | IOD_PTO_TCP | 4625 | 44625 | PMMfaza80[10]
PTOPMMfaza8011 | REAL | IOD_PTO_TCP | 4627 | 44627 | PMMfaza80[11]
PTOPMMfaza8012 | REAL | IOD_PTO_TCP | 4629 | 44629 | PMMfaza80[12]
PTOPMMfaza8013 | REAL | IOD_PTO_TCP | 4631 | 44631 | PMMfaza80[13]
PTOPMMfaza8014 | REAL | IOD_PTO_TCP | 4633 | 44633 | PMMfaza80[14]
PTOPMMfaza8015 | REAL | IOD_PTO_TCP | 4635 | 44635 | PMMfaza80[15]
PTOPMMfaza8016 | REAL | IOD_PTO_TCP | 4637 | 44637 | PMMfaza80[16]
PTOPMMfaza8017 | REAL | IOD_PTO_TCP | 4639 | 44639 | PMMfaza80[17]
PTOPMMfaza8018 | REAL | IOD_PTO_TCP | 4641 | 44641 | PMMfaza80[18]
PTOPMMfaza8019 | REAL | IOD_PTO_TCP | 4643 | 44643 | PMMfaza80[19]
PTOPMMfaza801 | REAL | IOD_PTO_TCP | 4645 | 44645 | PMMfaza80[1]
PTOPMMfaza8020 | REAL | IOD_PTO_TCP | 4647 | 44647 | PMMfaza80[20]
PTOPMMfaza8021 | REAL | IOD_PTO_TCP | 4649 | 44649 | PMMfaza80[21]
PTOPMMfaza8022 | REAL | IOD_PTO_TCP | 4651 | 44651 | PMMfaza80[22]
PTOPMMfaza8023 | REAL | IOD_PTO_TCP | 4653 | 44653 | PMMfaza80[23]
PTOPMMfaza8024 | REAL | IOD_PTO_TCP | 4655 | 44655 | PMMfaza80[24]
PTOPMMfaza8025 | REAL | IOD_PTO_TCP | 4657 | 44657 | PMMfaza80[25]
PTOPMMfaza8026 | REAL | IOD_PTO_TCP | 4659 | 44659 | PMMfaza80[26]
PTOPMMfaza8027 | REAL | IOD_PTO_TCP | 4661 | 44661 | PMMfaza80[27]
PTOPMMfaza8028 | REAL | IOD_PTO_TCP | 4663 | 44663 | PMMfaza80[28]
PTOPMMfaza8029 | REAL | IOD_PTO_TCP | 4665 | 44665 | PMMfaza80[29]
PTOPMMfaza802 | REAL | IOD_PTO_TCP | 4667 | 44667 | PMMfaza80[2]
PTOPMMfaza8030 | REAL | IOD_PTO_TCP | 4669 | 44669 | PMMfaza80[30]
PTOPMMfaza8031 | REAL | IOD_PTO_TCP | 4671 | 44671 | PMMfaza80[31]
PTOPMMfaza8032 | REAL | IOD_PTO_TCP | 4673 | 44673 | PMMfaza80[32]
PTOPMMfaza8033 | REAL | IOD_PTO_TCP | 4675 | 44675 | PMMfaza80[33]
PTOPMMfaza8034 | REAL | IOD_PTO_TCP | 4677 | 44677 | PMMfaza80[34]
PTOPMMfaza8035 | REAL | IOD_PTO_TCP | 4679 | 44679 | PMMfaza80[35]
PTOPMMfaza8036 | REAL | IOD_PTO_TCP | 4681 | 44681 | PMMfaza80[36]
PTOPMMfaza8037 | REAL | IOD_PTO_TCP | 4683 | 44683 | PMMfaza80[37]
PTOPMMfaza8038 | REAL | IOD_PTO_TCP | 4685 | 44685 | PMMfaza80[38]
PTOPMMfaza8039 | REAL | IOD_PTO_TCP | 4687 | 44687 | PMMfaza80[39]
PTOPMMfaza803 | REAL | IOD_PTO_TCP | 4689 | 44689 | PMMfaza80[3]
PTOPMMfaza8040 | REAL | IOD_PTO_TCP | 4691 | 44691 | PMMfaza80[40]
PTOPMMfaza8041 | REAL | IOD_PTO_TCP | 4693 | 44693 | PMMfaza80[41]
PTOPMMfaza8042 | REAL | IOD_PTO_TCP | 4695 | 44695 | PMMfaza80[42]
PTOPMMfaza804 | REAL | IOD_PTO_TCP | 4697 | 44697 | PMMfaza80[4]
PTOPMMfaza805 | REAL | IOD_PTO_TCP | 4699 | 44699 | PMMfaza80[5]
PTOPMMfaza806 | REAL | IOD_PTO_TCP | 4701 | 44701 | PMMfaza80[6]
PTOPMMfaza807 | REAL | IOD_PTO_TCP | 4703 | 44703 | PMMfaza80[7]
PTOPMMfaza808 | REAL | IOD_PTO_TCP | 4705 | 44705 | PMMfaza80[8]
PTOPMMfaza809 | REAL | IOD_PTO_TCP | 4707 | 44707 | PMMfaza80[9]
PTOSenzorTemp1 | REAL | IOD_PTO_TCP | 4709 | 44709 | SenzorTemp[1]
PTOSenzorTemp2 | REAL | IOD_PTO_TCP | 4711 | 44711 | SenzorTemp[2]
PTOSenzorTemp3 | REAL | IOD_PTO_TCP | 4713 | 44713 | SenzorTemp[3]
PTOSenzorTemp4 | REAL | IOD_PTO_TCP | 4715 | 44715 | SenzorTemp[4]
PTOSenzorTemp5 | REAL | IOD_PTO_TCP | 4717 | 44717 | SenzorTemp[5]
PTOSenzorTemp6 | REAL | IOD_PTO_TCP | 4719 | 44719 | SenzorTemp[6]
PTOSenzorVlaga1 | REAL | IOD_PTO_TCP | 4721 | 44721 | SenzorVlaga[1]
PTOSenzorVlaga2 | REAL | IOD_PTO_TCP | 4723 | 44723 | SenzorVlaga[2]
PTOSenzorVlaga3 | REAL | IOD_PTO_TCP | 4725 | 44725 | SenzorVlaga[3]
PTOSenzorVlaga4 | REAL | IOD_PTO_TCP | 4727 | 44727 | SenzorVlaga[4]
PTOSenzorVlaga5 | REAL | IOD_PTO_TCP | 4729 | 44729 | SenzorVlaga[5]
PTOSenzorVlaga6 | REAL | IOD_PTO_TCP | 4731 | 44731 | SenzorVlaga[6]
PTOTempAlarmPoint0 | REAL | IOD_PTO_TCP | 4733 | 44733 | TempAlarmPoint[0]
PTOTempAlarmPoint1 | REAL | IOD_PTO_TCP | 4735 | 44735 | TempAlarmPoint[1]
PTOTempAlarmPoint2 | REAL | IOD_PTO_TCP | 4737 | 44737 | TempAlarmPoint[2]
PTOTempAlarmPoint3 | REAL | IOD_PTO_TCP | 4739 | 44739 | TempAlarmPoint[3]
PTOTempMaxPoint0 | REAL | IOD_PTO_TCP | 4741 | 44741 | TempMaxPoint[0]
PTOTempMaxPoint1 | REAL | IOD_PTO_TCP | 4743 | 44743 | TempMaxPoint[1]
PTOTempMaxPoint2 | REAL | IOD_PTO_TCP | 4745 | 44745 | TempMaxPoint[2]
PTOTempMaxPoint3 | REAL | IOD_PTO_TCP | 4747 | 44747 | TempMaxPoint[3]
PTOTempPovp0 | REAL | IOD_PTO_TCP | 4749 | 44749 | TempPovp[0]
PTOTempPovp1 | REAL | IOD_PTO_TCP | 4751 | 44751 | TempPovp[1]
PTOTempPovp2 | REAL | IOD_PTO_TCP | 4753 | 44753 | TempPovp[2]
PTOTempPovp3 | REAL | IOD_PTO_TCP | 4755 | 44755 | TempPovp[3]
PTOTempSetPoint0 | REAL | IOD_PTO_TCP | 4757 | 44757 | TempSetPoint[0]
PTOTempSetPoint1 | REAL | IOD_PTO_TCP | 4759 | 44759 | TempSetPoint[1]
PTOTempSetPoint2 | REAL | IOD_PTO_TCP | 4761 | 44761 | TempSetPoint[2]
PTOTempSetPoint3 | REAL | IOD_PTO_TCP | 4763 | 44763 | TempSetPoint[3]
PTOUPS1EstimatedChargeRemaining | REAL | IOD_PTO_TCP | 4765 | 44765 | UPS[1].EstimatedChargeRemaining
PTOUPS1EstimatedMinutesRemaining | REAL | IOD_PTO_TCP | 4767 | 44767 | UPS[1].EstimatedMinutesRemaining
PTOUPS1IzhodMocL1 | REAL | IOD_PTO_TCP | 4769 | 44769 | UPS[1].IzhodMocL1
PTOUPS1IzhodMocL2 | REAL | IOD_PTO_TCP | 4771 | 44771 | UPS[1].IzhodMocL2
PTOUPS1IzhodMocL3 | REAL | IOD_PTO_TCP | 4773 | 44773 | UPS[1].IzhodMocL3
PTOUPS1NapetostBaterije | REAL | IOD_PTO_TCP | 4775 | 44775 | UPS[1].NapetostBaterije
PTOUPS1TemperaturaBaterije | REAL | IOD_PTO_TCP | 4777 | 44777 | UPS[1].TemperaturaBaterije
PTOUPS1VhodFrekvencaL1 | REAL | IOD_PTO_TCP | 4779 | 44779 | UPS[1].VhodFrekvencaL1
PTOUPS1VhodFrekvencaL2 | REAL | IOD_PTO_TCP | 4781 | 44781 | UPS[1].VhodFrekvencaL2
PTOUPS1VhodFrekvencaL3 | REAL | IOD_PTO_TCP | 4783 | 44783 | UPS[1].VhodFrekvencaL3
PTOUPS1VhodNapetostL1 | REAL | IOD_PTO_TCP | 4785 | 44785 | UPS[1].VhodNapetostL1
PTOUPS1VhodNapetostL2 | REAL | IOD_PTO_TCP | 4787 | 44787 | UPS[1].VhodNapetostL2
PTOUPS1VhodNapetostL3 | REAL | IOD_PTO_TCP | 4789 | 44789 | UPS[1].VhodNapetostL3
PTOUPS2EstimatedChargeRemaining | REAL | IOD_PTO_TCP | 4791 | 44791 | UPS[2].EstimatedChargeRemaining
PTOUPS2EstimatedMinutesRemaining | REAL | IOD_PTO_TCP | 4793 | 44793 | UPS[2].EstimatedMinutesRemaining
PTOUPS2IzhodMocL1 | REAL | IOD_PTO_TCP | 4795 | 44795 | UPS[2].IzhodMocL1
PTOUPS2IzhodMocL2 | REAL | IOD_PTO_TCP | 4797 | 44797 | UPS[2].IzhodMocL2
PTOUPS2IzhodMocL3 | REAL | IOD_PTO_TCP | 4799 | 44799 | UPS[2].IzhodMocL3
PTOUPS2NapetostBaterije | REAL | IOD_PTO_TCP | 4801 | 44801 | UPS[2].NapetostBaterije
PTOUPS2TemperaturaBaterije | REAL | IOD_PTO_TCP | 4803 | 44803 | UPS[2].TemperaturaBaterije
PTOUPS2VhodFrekvencaL1 | REAL | IOD_PTO_TCP | 4805 | 44805 | UPS[2].VhodFrekvencaL1
PTOUPS2VhodFrekvencaL2 | REAL | IOD_PTO_TCP | 4807 | 44807 | UPS[2].VhodFrekvencaL2
PTOUPS2VhodFrekvencaL3 | REAL | IOD_PTO_TCP | 4809 | 44809 | UPS[2].VhodFrekvencaL3
PTOUPS2VhodNapetostL1 | REAL | IOD_PTO_TCP | 4811 | 44811 | UPS[2].VhodNapetostL1
PTOUPS2VhodNapetostL2 | REAL | IOD_PTO_TCP | 4813 | 44813 | UPS[2].VhodNapetostL2
PTOUPS2VhodNapetostL3 | REAL | IOD_PTO_TCP | 4815 | 44815 | UPS[2].VhodNapetostL3
PTOVlagaPovp1 | REAL | IOD_PTO_TCP | 4817 | 44817 | VlagaPovp[1]
PTOVlagaPovp2 | REAL | IOD_PTO_TCP | 4819 | 44819 | VlagaPovp[2]
PTOVlagaPovp3 | REAL | IOD_PTO_TCP | 4821 | 44821 | VlagaPovp[3]
PTORazlikaUr | REAL | IOD_PTO_TCP | 4823 | 44823 | RazlikaUr
PTOKlima1NastTempHlajenje | REAL | IOD_PTO_TCP | 4825 | 44825 | Klima[1].NastTempHlajenje
PTOKlima2NastTempHlajenje | REAL | IOD_PTO_TCP | 4827 | 44827 | Klima[2].NastTempHlajenje
PTOKlima3NastTempHlajenje | REAL | IOD_PTO_TCP | 4829 | 44829 | Klima[3].NastTempHlajenje
PTOKlima4NastTempHlajenje | REAL | IOD_PTO_TCP | 4831 | 44831 | Klima[4].NastTempHlajenje
PTOKlima5NastTempHlajenje | REAL | IOD_PTO_TCP | 4833 | 44833 | Klima[5].NastTempHlajenje
PTOKlima6NastTempHlajenje | REAL | IOD_PTO_TCP | 4835 | 44835 | Klima[6].NastTempHlajenje
PTOKlima1NastTempGretje | REAL | IOD_PTO_TCP | 4837 | 44837 | Klima[1].NastTempGretje
PTOKlima2NastTempGretje | REAL | IOD_PTO_TCP | 4839 | 44839 | Klima[2].NastTempGretje
PTOKlima3NastTempGretje | REAL | IOD_PTO_TCP | 4841 | 44841 | Klima[3].NastTempGretje
PTOKlima4NastTempGretje | REAL | IOD_PTO_TCP | 4843 | 44843 | Klima[4].NastTempGretje
PTOKlima5NastTempGretje | REAL | IOD_PTO_TCP | 4845 | 44845 | Klima[5].NastTempGretje
PTOKlima6NastTempGretje | REAL | IOD_PTO_TCP | 4847 | 44847 | Klima[6].NastTempGretje
PTOKlima1TempHladneVode | REAL | IOD_PTO_TCP | 4849 | 44849 | Klima[1].TempHladneVode
PTOKlima2TempHladneVode | REAL | IOD_PTO_TCP | 4851 | 44851 | Klima[2].TempHladneVode
PTOKlima3TempHladneVode | REAL | IOD_PTO_TCP | 4853 | 44853 | Klima[3].TempHladneVode
PTOKlima4TempHladneVode | REAL | IOD_PTO_TCP | 4855 | 44855 | Klima[4].TempHladneVode
PTOKlima5TempHladneVode | REAL | IOD_PTO_TCP | 4857 | 44857 | Klima[5].TempHladneVode
PTOKlima6TempHladneVode | REAL | IOD_PTO_TCP | 4859 | 44859 | Klima[6].TempHladneVode
PTOKlima1TempTopleVode | REAL | IOD_PTO_TCP | 4861 | 44861 | Klima[1].TempTopleVode
PTOKlima2TempTopleVode | REAL | IOD_PTO_TCP | 4863 | 44863 | Klima[2].TempTopleVode
PTOKlima3TempTopleVode | REAL | IOD_PTO_TCP | 4865 | 44865 | Klima[3].TempTopleVode
PTOKlima4TempTopleVode | REAL | IOD_PTO_TCP | 4867 | 44867 | Klima[4].TempTopleVode
PTOKlima5TempTopleVode | REAL | IOD_PTO_TCP | 4869 | 44869 | Klima[5].TempTopleVode
PTOKlima6TempTopleVode | REAL | IOD_PTO_TCP | 4871 | 44871 | Klima[6].TempTopleVode
PTOZamikVklopa | REAL | IOD_PTO_TCP | 4873 | 44873 | ZamikVklopa
PTODate_Time0 | STRING | IOD_PTO_TCP | 5001 | 45001[15] | Date_Time[0]
PTODate_Time1 | STRING | IOD_PTO_TCP | 5016 | 45016[15] | Date_Time[1]
PTODate_Time2 | STRING | IOD_PTO_TCP | 5031 | 45031[15] | Date_Time[2]
PTODate_Time3 | STRING | IOD_PTO_TCP | 5046 | 45046[15] | Date_Time[3]
PTOUserCurrentName | STRING | IOD_PTO_TCP | 5061 | 45061[15] | UserCurrentName
PTOkom_nast_cas_izpada | UINT | IOD_PTO_TCP | 6001 | 46001 | kom_nast_cas_izpada

## variable_new
PTOVsotaF1_1_16B | INT | IOD_PTO_disk | I35
PTOVsotaF1_17_32B | INT | IOD_PTO_disk | I36
PTOVsotaF1_33_42B | INT | IOD_PTO_disk | I37
PTOVsotaF2_1_16B | INT | IOD_PTO_disk | I38
PTOVsotaF2_17_32B | INT | IOD_PTO_disk | I39
PTOVsotaF2_33_42B | INT | IOD_PTO_disk | I40
PTOVsotaF3_1_16B | INT | IOD_PTO_disk | I41
PTOVsotaF3_17_32B | INT | IOD_PTO_disk | I42
PTOVsotaF3_33_42B | INT | IOD_PTO_disk | I43
PTOVsotaF1_1_16A | INT | IOD_PTO_disk | I44
PTOVsotaF1_17_32A | INT | IOD_PTO_disk | I45
PTOVsotaF1_33_42A | INT | IOD_PTO_disk | I46
PTOVsotaF2_1_16A | INT | IOD_PTO_disk | I47
PTOVsotaF2_17_32A | INT | IOD_PTO_disk | I48
PTOVsotaF2_33_42A | INT | IOD_PTO_disk | I49
PTOVsotaF3_1_16A | INT | IOD_PTO_disk | I50
PTOVsotaF3_17_32A | INT | IOD_PTO_disk | I51
PTOVsotaF3_33_42A | INT | IOD_PTO_disk | I52
PTOAlarmGenComm | DIGITAL | IOD_PTO_TCP | 00001
PTOAlarmGenKlima1 | DIGITAL | IOD_PTO_TCP | 00002
PTOAlarmGenKlima2 | DIGITAL | IOD_PTO_TCP | 00003
PTOAlarmGenKlima3 | DIGITAL | IOD_PTO_TCP | 00004
PTOAlarmGenKlima4 | DIGITAL | IOD_PTO_TCP | 00005
PTOAlarmGenKlima5 | DIGITAL | IOD_PTO_TCP | 00006
PTOAlarmGenKlima6 | DIGITAL | IOD_PTO_TCP | 00007
PTOAlarmGenPMM | DIGITAL | IOD_PTO_TCP | 00008
PTOAlarmGenRest | DIGITAL | IOD_PTO_TCP | 00009
PTOAlarmGenSenzor | DIGITAL | IOD_PTO_TCP | 00010
PTOAlarmGenStikala | DIGITAL | IOD_PTO_TCP | 00011
PTOAlarmGenTemp | DIGITAL | IOD_PTO_TCP | 00012
PTOAlarmGenUPS1 | DIGITAL | IOD_PTO_TCP | 00013
PTOAlarmGenUPS2 | DIGITAL | IOD_PTO_TCP | 00014
PTOComSCADA | DIGITAL | IOD_PTO_TCP | 00015
PTOComSCADA1 | DIGITAL | IOD_PTO_TCP | 00016
PTODate_Time0 | STRING | IOD_PTO_TCP | 45001[15]
PTODate_Time1 | STRING | IOD_PTO_TCP | 45016[15]
PTODate_Time2 | STRING | IOD_PTO_TCP | 45031[15]
PTODate_Time3 | STRING | IOD_PTO_TCP | 45046[15]
PTODateTimeDan | INT | IOD_PTO_TCP | 40001
PTODateTimeLeto | INT | IOD_PTO_TCP | 40002
PTODateTimeMesec | INT | IOD_PTO_TCP | 40003
PTODateTimeMinuta | INT | IOD_PTO_TCP | 40004
PTODateTimeSekunda | INT | IOD_PTO_TCP | 40005
PTODateTimeUra | INT | IOD_PTO_TCP | 40006
PTODI_A1Q01_DovUpsA_ON | DIGITAL | IOD_PTO_TCP | 00017
PTODI_A1Q02_DovByA_ON | DIGITAL | IOD_PTO_TCP | 00018
PTODI_A1Q0_GlavnoSti_ON | DIGITAL | IOD_PTO_TCP | 00019
PTODI_A1Q11_OdcUpsA_IZP | DIGITAL | IOD_PTO_TCP | 00020
PTODI_A1Q11_OdcUpsA_ON | DIGITAL | IOD_PTO_TCP | 00021
PTODI_A1Q12_OdcByUpsA_IZP | DIGITAL | IOD_PTO_TCP | 00022
PTODI_A1Q12_OdcByUpsA_ON | DIGITAL | IOD_PTO_TCP | 00023
PTODI_A1Q13_OdcByA_IZP | DIGITAL | IOD_PTO_TCP | 00024
PTODI_A1Q13_OdcByA_ON | DIGITAL | IOD_PTO_TCP | 00025
PTODI_A2Q0_GlavnoSti_ON | DIGITAL | IOD_PTO_TCP | 00026
PTODI_F201_OdcKl1ZE_IZP | DIGITAL | IOD_PTO_TCP | 00027
PTODI_F201_OdcKl1ZE_ON | DIGITAL | IOD_PTO_TCP | 00028
PTODI_F202_OdcKl2ZE_IZP | DIGITAL | IOD_PTO_TCP | 00029
PTODI_F202_OdcKl2ZE_ON | DIGITAL | IOD_PTO_TCP | 00030
PTODI_F203_OdcKl3ZE_IZP | DIGITAL | IOD_PTO_TCP | 00031
PTODI_F203_OdcKl3ZE_ON | DIGITAL | IOD_PTO_TCP | 00032
PTODI_F204_OdcKl4ZE_IZP | DIGITAL | IOD_PTO_TCP | 00033
PTODI_F204_OdcKl4ZE_ON | DIGITAL | IOD_PTO_TCP | 00034
PTODI_F205_OdcKl5aZE_IZP | DIGITAL | IOD_PTO_TCP | 00035
PTODI_F205_OdcKl5aZE_ON | DIGITAL | IOD_PTO_TCP | 00036
PTODI_F206_OdcKl5bZE_IZP | DIGITAL | IOD_PTO_TCP | 00037
PTODI_F206_OdcKl5bZE_ON | DIGITAL | IOD_PTO_TCP | 00038
PTODI_F207_OdcKl6aZE_IZP | DIGITAL | IOD_PTO_TCP | 00039
PTODI_F207_OdcKl6aZE_ON | DIGITAL | IOD_PTO_TCP | 00040
PTODI_F208_OdcKl6bZE_IZP | DIGITAL | IOD_PTO_TCP | 00041
PTODI_F208_OdcKl6bZE_ON | DIGITAL | IOD_PTO_TCP | 00042
PTODI_IzpadMreze | DIGITAL | IOD_PTO_TCP | 00043
PTODI_Klima1_ERR | DIGITAL | IOD_PTO_TCP | 00044
PTODI_Klima1_ON | DIGITAL | IOD_PTO_TCP | 00045
PTODI_Klima2_ERR | DIGITAL | IOD_PTO_TCP | 00046
PTODI_Klima2_ON | DIGITAL | IOD_PTO_TCP | 00047
PTODI_Klima3_ERR | DIGITAL | IOD_PTO_TCP | 00048
PTODI_Klima3_ON | DIGITAL | IOD_PTO_TCP | 00049
PTODI_Klima4_ERR | DIGITAL | IOD_PTO_TCP | 00050
PTODI_Klima4_ON | DIGITAL | IOD_PTO_TCP | 00051
PTODI_Klima5_ERR | DIGITAL | IOD_PTO_TCP | 00052
PTODI_Klima5_ON | DIGITAL | IOD_PTO_TCP | 00053
PTODI_Klima6_ERR | DIGITAL | IOD_PTO_TCP | 00054
PTODI_Klima6_ON | DIGITAL | IOD_PTO_TCP | 00055
PTODI_KlimaSplitPP_ERR | DIGITAL | IOD_PTO_TCP | 00056
PTODI_KlimaSplitPP_ON | DIGITAL | IOD_PTO_TCP | 00057
PTODI_PrenapA1_OK | DIGITAL | IOD_PTO_TCP | 00058
PTODI_PrenapA2_OK | DIGITAL | IOD_PTO_TCP | 00059
PTODI_Q101_OdcKlima1_IZP | DIGITAL | IOD_PTO_TCP | 00060
PTODI_Q101_OdcKlima1_ON | DIGITAL | IOD_PTO_TCP | 00061
PTODI_Q102_OdcKlima2_IZP | DIGITAL | IOD_PTO_TCP | 00062
PTODI_Q102_OdcKlima2_ON | DIGITAL | IOD_PTO_TCP | 00063
PTODI_Q103_OdcKlima3_IZP | DIGITAL | IOD_PTO_TCP | 00064
PTODI_Q103_OdcKlima3_ON | DIGITAL | IOD_PTO_TCP | 00065
PTODI_Q104_OdcKlima4_IZP | DIGITAL | IOD_PTO_TCP | 00066
PTODI_Q104_OdcKlima4_ON | DIGITAL | IOD_PTO_TCP | 00067
PTODI_Q105_OdcKlima5_IZP | DIGITAL | IOD_PTO_TCP | 00068
PTODI_Q105_OdcKlima5_ON | DIGITAL | IOD_PTO_TCP | 00069
PTODI_Q106_OdcKlima6_IZP | DIGITAL | IOD_PTO_TCP | 00070
PTODI_Q106_OdcKlima6_ON | DIGITAL | IOD_PTO_TCP | 00071
PTODI_Q107_OdcUsmSS2_IZP | DIGITAL | IOD_PTO_TCP | 00072
PTODI_Q107_OdcUsmSS2_ON | DIGITAL | IOD_PTO_TCP | 00073
PTODI_Q108_OdcUsmSS3_IZP | DIGITAL | IOD_PTO_TCP | 00074
PTODI_Q108_OdcUsmSS3_ON | DIGITAL | IOD_PTO_TCP | 00075
PTODI_RazlitjeVodeK1K2 | DIGITAL | IOD_PTO_TCP | 00076
PTODI_RazlitjeVodeK3K4 | DIGITAL | IOD_PTO_TCP | 00077
PTODI_RazlitjeVodeK5 | DIGITAL | IOD_PTO_TCP | 00078
PTODI_RazlitjeVodeK6 | DIGITAL | IOD_PTO_TCP | 00079
PTODI_UPS_Alarm | DIGITAL | IOD_PTO_TCP | 00080
PTODI_UPS_BatNacin | DIGITAL | IOD_PTO_TCP | 00081
PTODI_UPS_Polnjenje | DIGITAL | IOD_PTO_TCP | 00082
PTODI_UpsA_BypassON | DIGITAL | IOD_PTO_TCP | 00083
PTODI_UpsA_ERR | DIGITAL | IOD_PTO_TCP | 00084
PTODI_UpsB_BypassON | DIGITAL | IOD_PTO_TCP | 00085
PTODI_UpsB_ERR | DIGITAL | IOD_PTO_TCP | 00086
PTODI_UQ11_OdcPMM_IZP | DIGITAL | IOD_PTO_TCP | 00087
PTODI_UQ11_OdcPMM_ON | DIGITAL | IOD_PTO_TCP | 00088
PTODI_UQ12_OdcPMM_IZP | DIGITAL | IOD_PTO_TCP | 00089
PTODI_UQ12_OdcPMM_ON | DIGITAL | IOD_PTO_TCP | 00090
PTODIN_A1Q11_OdcUpsA_IZP | DIGITAL | IOD_PTO_TCP | 00091
PTODIN_A1Q12_OdcByUpsA_IZP | DIGITAL | IOD_PTO_TCP | 00092
PTODIN_A1Q13_OdcByA_IZP | DIGITAL | IOD_PTO_TCP | 00093
PTODIN_F201_OdcKl1ZE_IZP | DIGITAL | IOD_PTO_TCP | 00094
PTODIN_F202_OdcKl2ZE_IZP | DIGITAL | IOD_PTO_TCP | 00095
PTODIN_F203_OdcKl3ZE_IZP | DIGITAL | IOD_PTO_TCP | 00096
PTODIN_F204_OdcKl4ZE_IZP | DIGITAL | IOD_PTO_TCP | 00097
PTODIN_F205_OdcKl5aZE_IZP | DIGITAL | IOD_PTO_TCP | 00098
PTODIN_F206_OdcKl5bZE_IZP | DIGITAL | IOD_PTO_TCP | 00099
PTODIN_F207_OdcKl6aZE_IZP | DIGITAL | IOD_PTO_TCP | 00100
PTODIN_F208_OdcKl6bZE_IZP | DIGITAL | IOD_PTO_TCP | 00101
PTODIN_Klima1_ERR | DIGITAL | IOD_PTO_TCP | 00102
PTODIN_Klima2_ERR | DIGITAL | IOD_PTO_TCP | 00103
PTODIN_Klima3_ERR | DIGITAL | IOD_PTO_TCP | 00104
PTODIN_Klima4_ERR | DIGITAL | IOD_PTO_TCP | 00105
PTODIN_Klima5_ERR | DIGITAL | IOD_PTO_TCP | 00106
PTODIN_Klima6_ERR | DIGITAL | IOD_PTO_TCP | 00107
PTODIN_KlimaSplitPP_ERR | DIGITAL | IOD_PTO_TCP | 00108
PTODIN_PrenapA1_OK | DIGITAL | IOD_PTO_TCP | 00109
PTODIN_PrenapA2_OK | DIGITAL | IOD_PTO_TCP | 00110
PTODIN_Q101_OdcKlima1_IZP | DIGITAL | IOD_PTO_TCP | 00111
PTODIN_Q102_OdcKlima2_IZP | DIGITAL | IOD_PTO_TCP | 00112
PTODIN_Q103_OdcKlima3_IZP | DIGITAL | IOD_PTO_TCP | 00113
PTODIN_Q104_OdcKlima4_IZP | DIGITAL | IOD_PTO_TCP | 00114
PTODIN_Q105_OdcKlima5_IZP | DIGITAL | IOD_PTO_TCP | 00115
PTODIN_Q106_OdcKlima6_IZP | DIGITAL | IOD_PTO_TCP | 00116
PTODIN_Q107_OdcUsmSS2_IZP | DIGITAL | IOD_PTO_TCP | 00117
PTODIN_Q108_OdcUsmSS3_IZP | DIGITAL | IOD_PTO_TCP | 00118
PTODIN_UpsA_BypassON | DIGITAL | IOD_PTO_TCP | 00119
PTODIN_UpsA_ERR | DIGITAL | IOD_PTO_TCP | 00120
PTODIN_UpsB_BypassON | DIGITAL | IOD_PTO_TCP | 00121
PTODIN_UpsB_ERR | DIGITAL | IOD_PTO_TCP | 00122
PTODIN_UQ11_OdcPMM_IZP | DIGITAL | IOD_PTO_TCP | 00123
PTODIN_UQ12_OdcPMM_IZP | DIGITAL | IOD_PTO_TCP | 00124
PTODO_Klima1_Izklop | DIGITAL | IOD_PTO_TCP | 00125
PTODO_Klima2_Izklop | DIGITAL | IOD_PTO_TCP | 00126
PTODO_Klima3_Izklop | DIGITAL | IOD_PTO_TCP | 00127
PTODO_Klima4_Izklop | DIGITAL | IOD_PTO_TCP | 00128
PTODO_Klima5_Izklop | DIGITAL | IOD_PTO_TCP | 00129
PTODO_Klima6_Izklop | DIGITAL | IOD_PTO_TCP | 00130
PTOErrComKlima1 | DIGITAL | IOD_PTO_TCP | 00131
PTOErrComKlima2 | DIGITAL | IOD_PTO_TCP | 00132
PTOErrComKlima3 | DIGITAL | IOD_PTO_TCP | 00133
PTOErrComKlima4 | DIGITAL | IOD_PTO_TCP | 00134
PTOErrComKlima5 | DIGITAL | IOD_PTO_TCP | 00135
PTOErrComKlima6 | DIGITAL | IOD_PTO_TCP | 00136
PTOErrCommScada | DIGITAL | IOD_PTO_TCP | 00137
PTOErrComPanelPLC | DIGITAL | IOD_PTO_TCP | 00138
PTOErrComPMM | DIGITAL | IOD_PTO_TCP | 00139
PTOErrComPort2 | DIGITAL | IOD_PTO_TCP | 00140
PTOErrComPort3 | DIGITAL | IOD_PTO_TCP | 00141
PTOErrComPort4 | DIGITAL | IOD_PTO_TCP | 00142
PTOErrComUPS1 | DIGITAL | IOD_PTO_TCP | 00143
PTOErrComUPS2 | DIGITAL | IOD_PTO_TCP | 00144
PTOErrorComKlima1Code10 | INT | IOD_PTO_TCP | 40007
PTOErrorComKlima1Code11 | INT | IOD_PTO_TCP | 40008
PTOErrorComKlima1Code12 | INT | IOD_PTO_TCP | 40009
PTOErrorComKlima1Code13 | INT | IOD_PTO_TCP | 40010
PTOErrorComKlima1Code14 | INT | IOD_PTO_TCP | 40011
PTOErrorComKlima1Code15 | INT | IOD_PTO_TCP | 40012
PTOErrorComKlima1Code1 | INT | IOD_PTO_TCP | 40013
PTOErrorComKlima1Code2 | INT | IOD_PTO_TCP | 40014
PTOErrorComKlima1Code3 | INT | IOD_PTO_TCP | 40015
PTOErrorComKlima1Code4 | INT | IOD_PTO_TCP | 40016
PTOErrorComKlima1Code5 | INT | IOD_PTO_TCP | 40017
PTOErrorComKlima1Code6 | INT | IOD_PTO_TCP | 40018
PTOErrorComKlima1Code7 | INT | IOD_PTO_TCP | 40019
PTOErrorComKlima1Code8 | INT | IOD_PTO_TCP | 40020
PTOErrorComKlima1Code9 | INT | IOD_PTO_TCP | 40021
PTOErrorComKlima1Error | DIGITAL | IOD_PTO_TCP | 00145
PTOErrorComKlima1Status | INT | IOD_PTO_TCP | 40022
PTOErrorComKlima2Code10 | INT | IOD_PTO_TCP | 40023
PTOErrorComKlima2Code11 | INT | IOD_PTO_TCP | 40024
PTOErrorComKlima2Code12 | INT | IOD_PTO_TCP | 40025
PTOErrorComKlima2Code13 | INT | IOD_PTO_TCP | 40026
PTOErrorComKlima2Code14 | INT | IOD_PTO_TCP | 40027
PTOErrorComKlima2Code15 | INT | IOD_PTO_TCP | 40028
PTOErrorComKlima2Code1 | INT | IOD_PTO_TCP | 40029
PTOErrorComKlima2Code2 | INT | IOD_PTO_TCP | 40030
PTOErrorComKlima2Code3 | INT | IOD_PTO_TCP | 40031
PTOErrorComKlima2Code4 | INT | IOD_PTO_TCP | 40032
PTOErrorComKlima2Code5 | INT | IOD_PTO_TCP | 40033
PTOErrorComKlima2Code6 | INT | IOD_PTO_TCP | 40034
PTOErrorComKlima2Code7 | INT | IOD_PTO_TCP | 40035
PTOErrorComKlima2Code8 | INT | IOD_PTO_TCP | 40036
PTOErrorComKlima2Code9 | INT | IOD_PTO_TCP | 40037
PTOErrorComKlima2Error | DIGITAL | IOD_PTO_TCP | 00146
PTOErrorComKlima2Status | INT | IOD_PTO_TCP | 40038
PTOErrorComKlima3Code10 | INT | IOD_PTO_TCP | 40039
PTOErrorComKlima3Code11 | INT | IOD_PTO_TCP | 40040
PTOErrorComKlima3Code12 | INT | IOD_PTO_TCP | 40041
PTOErrorComKlima3Code13 | INT | IOD_PTO_TCP | 40042
PTOErrorComKlima3Code14 | INT | IOD_PTO_TCP | 40043
PTOErrorComKlima3Code15 | INT | IOD_PTO_TCP | 40044
PTOErrorComKlima3Code1 | INT | IOD_PTO_TCP | 40045
PTOErrorComKlima3Code2 | INT | IOD_PTO_TCP | 40046
PTOErrorComKlima3Code3 | INT | IOD_PTO_TCP | 40047
PTOErrorComKlima3Code4 | INT | IOD_PTO_TCP | 40048
PTOErrorComKlima3Code5 | INT | IOD_PTO_TCP | 40049
PTOErrorComKlima3Code6 | INT | IOD_PTO_TCP | 40050
PTOErrorComKlima3Code7 | INT | IOD_PTO_TCP | 40051
PTOErrorComKlima3Code8 | INT | IOD_PTO_TCP | 40052
PTOErrorComKlima3Code9 | INT | IOD_PTO_TCP | 40053
PTOErrorComKlima3Error | DIGITAL | IOD_PTO_TCP | 00147
PTOErrorComKlima3Status | INT | IOD_PTO_TCP | 40054
PTOErrorComKlima4Code10 | INT | IOD_PTO_TCP | 40055
PTOErrorComKlima4Code11 | INT | IOD_PTO_TCP | 40056
PTOErrorComKlima4Code12 | INT | IOD_PTO_TCP | 40057
PTOErrorComKlima4Code13 | INT | IOD_PTO_TCP | 40058
PTOErrorComKlima4Code14 | INT | IOD_PTO_TCP | 40059
PTOErrorComKlima4Code15 | INT | IOD_PTO_TCP | 40060
PTOErrorComKlima4Code1 | INT | IOD_PTO_TCP | 40061
PTOErrorComKlima4Code2 | INT | IOD_PTO_TCP | 40062
PTOErrorComKlima4Code3 | INT | IOD_PTO_TCP | 40063
PTOErrorComKlima4Code4 | INT | IOD_PTO_TCP | 40064
PTOErrorComKlima4Code5 | INT | IOD_PTO_TCP | 40065
PTOErrorComKlima4Code6 | INT | IOD_PTO_TCP | 40066
PTOErrorComKlima4Code7 | INT | IOD_PTO_TCP | 40067
PTOErrorComKlima4Code8 | INT | IOD_PTO_TCP | 40068
PTOErrorComKlima4Code9 | INT | IOD_PTO_TCP | 40069
PTOErrorComKlima4Error | DIGITAL | IOD_PTO_TCP | 00148
PTOErrorComKlima4Status | INT | IOD_PTO_TCP | 40070
PTOErrorComKlima5Code10 | INT | IOD_PTO_TCP | 40071
PTOErrorComKlima5Code11 | INT | IOD_PTO_TCP | 40072
PTOErrorComKlima5Code12 | INT | IOD_PTO_TCP | 40073
PTOErrorComKlima5Code13 | INT | IOD_PTO_TCP | 40074
PTOErrorComKlima5Code14 | INT | IOD_PTO_TCP | 40075
PTOErrorComKlima5Code15 | INT | IOD_PTO_TCP | 40076
PTOErrorComKlima5Code1 | INT | IOD_PTO_TCP | 40077
PTOErrorComKlima5Code2 | INT | IOD_PTO_TCP | 40078
PTOErrorComKlima5Code3 | INT | IOD_PTO_TCP | 40079
PTOErrorComKlima5Code4 | INT | IOD_PTO_TCP | 40080
PTOErrorComKlima5Code5 | INT | IOD_PTO_TCP | 40081
PTOErrorComKlima5Code6 | INT | IOD_PTO_TCP | 40082
PTOErrorComKlima5Code7 | INT | IOD_PTO_TCP | 40083
PTOErrorComKlima5Code8 | INT | IOD_PTO_TCP | 40084
PTOErrorComKlima5Code9 | INT | IOD_PTO_TCP | 40085
PTOErrorComKlima5Error | DIGITAL | IOD_PTO_TCP | 00149
PTOErrorComKlima5Status | INT | IOD_PTO_TCP | 40086
PTOErrorComKlima6Code10 | INT | IOD_PTO_TCP | 40087
PTOErrorComKlima6Code11 | INT | IOD_PTO_TCP | 40088
PTOErrorComKlima6Code12 | INT | IOD_PTO_TCP | 40089
PTOErrorComKlima6Code13 | INT | IOD_PTO_TCP | 40090
PTOErrorComKlima6Code14 | INT | IOD_PTO_TCP | 40091
PTOErrorComKlima6Code15 | INT | IOD_PTO_TCP | 40092
PTOErrorComKlima6Code1 | INT | IOD_PTO_TCP | 40093
PTOErrorComKlima6Code2 | INT | IOD_PTO_TCP | 40094
PTOErrorComKlima6Code3 | INT | IOD_PTO_TCP | 40095
PTOErrorComKlima6Code4 | INT | IOD_PTO_TCP | 40096
PTOErrorComKlima6Code5 | INT | IOD_PTO_TCP | 40097
PTOErrorComKlima6Code6 | INT | IOD_PTO_TCP | 40098
PTOErrorComKlima6Code7 | INT | IOD_PTO_TCP | 40099
PTOErrorComKlima6Code8 | INT | IOD_PTO_TCP | 40100
PTOErrorComKlima6Code9 | INT | IOD_PTO_TCP | 40101
PTOErrorComKlima6Error | DIGITAL | IOD_PTO_TCP | 00150
PTOErrorComKlima6Status | INT | IOD_PTO_TCP | 40102
PTOErrorComPMMCode10 | INT | IOD_PTO_TCP | 40103
PTOErrorComPMMCode11 | INT | IOD_PTO_TCP | 40104
PTOErrorComPMMCode12 | INT | IOD_PTO_TCP | 40105
PTOErrorComPMMCode13 | INT | IOD_PTO_TCP | 40106
PTOErrorComPMMCode14 | INT | IOD_PTO_TCP | 40107
PTOErrorComPMMCode15 | INT | IOD_PTO_TCP | 40108
PTOErrorComPMMCode1 | INT | IOD_PTO_TCP | 40109
PTOErrorComPMMCode2 | INT | IOD_PTO_TCP | 40110
PTOErrorComPMMCode3 | INT | IOD_PTO_TCP | 40111
PTOErrorComPMMCode4 | INT | IOD_PTO_TCP | 40112
PTOErrorComPMMCode5 | INT | IOD_PTO_TCP | 40113
PTOErrorComPMMCode6 | INT | IOD_PTO_TCP | 40114
PTOErrorComPMMCode7 | INT | IOD_PTO_TCP | 40115
PTOErrorComPMMCode8 | INT | IOD_PTO_TCP | 40116
PTOErrorComPMMCode9 | INT | IOD_PTO_TCP | 40117
PTOErrorComPMMError | DIGITAL | IOD_PTO_TCP | 00151
PTOErrorComPMMStatus | INT | IOD_PTO_TCP | 40118
PTOErrorComUPS1Code10 | INT | IOD_PTO_TCP | 40119
PTOErrorComUPS1Code11 | INT | IOD_PTO_TCP | 40120
PTOErrorComUPS1Code12 | INT | IOD_PTO_TCP | 40121
PTOErrorComUPS1Code13 | INT | IOD_PTO_TCP | 40122
PTOErrorComUPS1Code14 | INT | IOD_PTO_TCP | 40123
PTOErrorComUPS1Code15 | INT | IOD_PTO_TCP | 40124
PTOErrorComUPS1Code1 | INT | IOD_PTO_TCP | 40125
PTOErrorComUPS1Code2 | INT | IOD_PTO_TCP | 40126
PTOErrorComUPS1Code3 | INT | IOD_PTO_TCP | 40127
PTOErrorComUPS1Code4 | INT | IOD_PTO_TCP | 40128
PTOErrorComUPS1Code5 | INT | IOD_PTO_TCP | 40129
PTOErrorComUPS1Code6 | INT | IOD_PTO_TCP | 40130
PTOErrorComUPS1Code7 | INT | IOD_PTO_TCP | 40131
PTOErrorComUPS1Code8 | INT | IOD_PTO_TCP | 40132
PTOErrorComUPS1Code9 | INT | IOD_PTO_TCP | 40133
PTOErrorComUPS1Error | DIGITAL | IOD_PTO_TCP | 00152
PTOErrorComUPS1Status | INT | IOD_PTO_TCP | 40134
PTOErrorComUPS2Code10 | INT | IOD_PTO_TCP | 40135
PTOErrorComUPS2Code11 | INT | IOD_PTO_TCP | 40136
PTOErrorComUPS2Code12 | INT | IOD_PTO_TCP | 40137
PTOErrorComUPS2Code13 | INT | IOD_PTO_TCP | 40138
PTOErrorComUPS2Code14 | INT | IOD_PTO_TCP | 40139
PTOErrorComUPS2Code15 | INT | IOD_PTO_TCP | 40140
PTOErrorComUPS2Code1 | INT | IOD_PTO_TCP | 40141
PTOErrorComUPS2Code2 | INT | IOD_PTO_TCP | 40142
PTOErrorComUPS2Code3 | INT | IOD_PTO_TCP | 40143
PTOErrorComUPS2Code4 | INT | IOD_PTO_TCP | 40144
PTOErrorComUPS2Code5 | INT | IOD_PTO_TCP | 40145
PTOErrorComUPS2Code6 | INT | IOD_PTO_TCP | 40146
PTOErrorComUPS2Code7 | INT | IOD_PTO_TCP | 40147
PTOErrorComUPS2Code8 | INT | IOD_PTO_TCP | 40148
PTOErrorComUPS2Code9 | INT | IOD_PTO_TCP | 40149
PTOErrorComUPS2Error | DIGITAL | IOD_PTO_TCP | 00153
PTOErrorComUPS2Status | INT | IOD_PTO_TCP | 40150
PTOKlima1Errors10 | DIGITAL | IOD_PTO_TCP | 00154
PTOKlima1Errors11 | DIGITAL | IOD_PTO_TCP | 00155
PTOKlima1Errors12 | DIGITAL | IOD_PTO_TCP | 00156
PTOKlima1Errors13 | DIGITAL | IOD_PTO_TCP | 00157
PTOKlima1Errors14 | DIGITAL | IOD_PTO_TCP | 00158
PTOKlima1Errors15 | DIGITAL | IOD_PTO_TCP | 00159
PTOKlima1Errors16 | DIGITAL | IOD_PTO_TCP | 00160
PTOKlima1Errors17 | DIGITAL | IOD_PTO_TCP | 00161
PTOKlima1Errors18 | DIGITAL | IOD_PTO_TCP | 00162
PTOKlima1Errors19 | DIGITAL | IOD_PTO_TCP | 00163
PTOKlima1Errors1 | DIGITAL | IOD_PTO_TCP | 00164
PTOKlima1Errors20 | DIGITAL | IOD_PTO_TCP | 00165
PTOKlima1Errors21 | DIGITAL | IOD_PTO_TCP | 00166
PTOKlima1Errors22 | DIGITAL | IOD_PTO_TCP | 00167
PTOKlima1Errors23 | DIGITAL | IOD_PTO_TCP | 00168
PTOKlima1Errors24 | DIGITAL | IOD_PTO_TCP | 00169
PTOKlima1Errors25 | DIGITAL | IOD_PTO_TCP | 00170
PTOKlima1Errors26 | DIGITAL | IOD_PTO_TCP | 00171
PTOKlima1Errors27 | DIGITAL | IOD_PTO_TCP | 00172
PTOKlima1Errors28 | DIGITAL | IOD_PTO_TCP | 00173
PTOKlima1Errors29 | DIGITAL | IOD_PTO_TCP | 00174
PTOKlima1Errors2 | DIGITAL | IOD_PTO_TCP | 00175
PTOKlima1Errors30 | DIGITAL | IOD_PTO_TCP | 00176
PTOKlima1Errors31 | DIGITAL | IOD_PTO_TCP | 00177
PTOKlima1Errors32 | DIGITAL | IOD_PTO_TCP | 00178
PTOKlima1Errors33 | DIGITAL | IOD_PTO_TCP | 00179
PTOKlima1Errors34 | DIGITAL | IOD_PTO_TCP | 00180
PTOKlima1Errors35 | DIGITAL | IOD_PTO_TCP | 00181
PTOKlima1Errors3 | DIGITAL | IOD_PTO_TCP | 00182
PTOKlima1Errors4 | DIGITAL | IOD_PTO_TCP | 00183
PTOKlima1Errors5 | DIGITAL | IOD_PTO_TCP | 00184
PTOKlima1Errors6 | DIGITAL | IOD_PTO_TCP | 00185
PTOKlima1Errors7 | DIGITAL | IOD_PTO_TCP | 00186
PTOKlima1Errors8 | DIGITAL | IOD_PTO_TCP | 00187
PTOKlima1Errors9 | DIGITAL | IOD_PTO_TCP | 00188
PTOKlima2Errors10 | DIGITAL | IOD_PTO_TCP | 00189
PTOKlima2Errors11 | DIGITAL | IOD_PTO_TCP | 00190
PTOKlima2Errors12 | DIGITAL | IOD_PTO_TCP | 00191
PTOKlima2Errors13 | DIGITAL | IOD_PTO_TCP | 00192
PTOKlima2Errors14 | DIGITAL | IOD_PTO_TCP | 00193
PTOKlima2Errors15 | DIGITAL | IOD_PTO_TCP | 00194
PTOKlima2Errors16 | DIGITAL | IOD_PTO_TCP | 00195
PTOKlima2Errors17 | DIGITAL | IOD_PTO_TCP | 00196
PTOKlima2Errors18 | DIGITAL | IOD_PTO_TCP | 00197
PTOKlima2Errors19 | DIGITAL | IOD_PTO_TCP | 00198
PTOKlima2Errors1 | DIGITAL | IOD_PTO_TCP | 00199
PTOKlima2Errors20 | DIGITAL | IOD_PTO_TCP | 00200
PTOKlima2Errors21 | DIGITAL | IOD_PTO_TCP | 00201
PTOKlima2Errors22 | DIGITAL | IOD_PTO_TCP | 00202
PTOKlima2Errors23 | DIGITAL | IOD_PTO_TCP | 00203
PTOKlima2Errors24 | DIGITAL | IOD_PTO_TCP | 00204
PTOKlima2Errors25 | DIGITAL | IOD_PTO_TCP | 00205
PTOKlima2Errors26 | DIGITAL | IOD_PTO_TCP | 00206
PTOKlima2Errors27 | DIGITAL | IOD_PTO_TCP | 00207
PTOKlima2Errors28 | DIGITAL | IOD_PTO_TCP | 00208
PTOKlima2Errors29 | DIGITAL | IOD_PTO_TCP | 00209
PTOKlima2Errors2 | DIGITAL | IOD_PTO_TCP | 00210
PTOKlima2Errors30 | DIGITAL | IOD_PTO_TCP | 00211
PTOKlima2Errors31 | DIGITAL | IOD_PTO_TCP | 00212
PTOKlima2Errors32 | DIGITAL | IOD_PTO_TCP | 00213
PTOKlima2Errors33 | DIGITAL | IOD_PTO_TCP | 00214
PTOKlima2Errors34 | DIGITAL | IOD_PTO_TCP | 00215
PTOKlima2Errors35 | DIGITAL | IOD_PTO_TCP | 00216
PTOKlima2Errors3 | DIGITAL | IOD_PTO_TCP | 00217
PTOKlima2Errors4 | DIGITAL | IOD_PTO_TCP | 00218
PTOKlima2Errors5 | DIGITAL | IOD_PTO_TCP | 00219
PTOKlima2Errors6 | DIGITAL | IOD_PTO_TCP | 00220
PTOKlima2Errors7 | DIGITAL | IOD_PTO_TCP | 00221
PTOKlima2Errors8 | DIGITAL | IOD_PTO_TCP | 00222
PTOKlima2Errors9 | DIGITAL | IOD_PTO_TCP | 00223
PTOKlima3Errors10 | DIGITAL | IOD_PTO_TCP | 00224
PTOKlima3Errors11 | DIGITAL | IOD_PTO_TCP | 00225
PTOKlima3Errors12 | DIGITAL | IOD_PTO_TCP | 00226
PTOKlima3Errors13 | DIGITAL | IOD_PTO_TCP | 00227
PTOKlima3Errors14 | DIGITAL | IOD_PTO_TCP | 00228
PTOKlima3Errors15 | DIGITAL | IOD_PTO_TCP | 00229
PTOKlima3Errors16 | DIGITAL | IOD_PTO_TCP | 00230
PTOKlima3Errors17 | DIGITAL | IOD_PTO_TCP | 00231
PTOKlima3Errors18 | DIGITAL | IOD_PTO_TCP | 00232
PTOKlima3Errors19 | DIGITAL | IOD_PTO_TCP | 00233
PTOKlima3Errors1 | DIGITAL | IOD_PTO_TCP | 00234
PTOKlima3Errors20 | DIGITAL | IOD_PTO_TCP | 00235
PTOKlima3Errors21 | DIGITAL | IOD_PTO_TCP | 00236
PTOKlima3Errors22 | DIGITAL | IOD_PTO_TCP | 00237
PTOKlima3Errors23 | DIGITAL | IOD_PTO_TCP | 00238
PTOKlima3Errors24 | DIGITAL | IOD_PTO_TCP | 00239
PTOKlima3Errors25 | DIGITAL | IOD_PTO_TCP | 00240
PTOKlima3Errors26 | DIGITAL | IOD_PTO_TCP | 00241
PTOKlima3Errors27 | DIGITAL | IOD_PTO_TCP | 00242
PTOKlima3Errors28 | DIGITAL | IOD_PTO_TCP | 00243
PTOKlima3Errors29 | DIGITAL | IOD_PTO_TCP | 00244
PTOKlima3Errors2 | DIGITAL | IOD_PTO_TCP | 00245
PTOKlima3Errors30 | DIGITAL | IOD_PTO_TCP | 00246
PTOKlima3Errors31 | DIGITAL | IOD_PTO_TCP | 00247
PTOKlima3Errors32 | DIGITAL | IOD_PTO_TCP | 00248
PTOKlima3Errors33 | DIGITAL | IOD_PTO_TCP | 00249
PTOKlima3Errors34 | DIGITAL | IOD_PTO_TCP | 00250
PTOKlima3Errors35 | DIGITAL | IOD_PTO_TCP | 00251
PTOKlima3Errors3 | DIGITAL | IOD_PTO_TCP | 00252
PTOKlima3Errors4 | DIGITAL | IOD_PTO_TCP | 00253
PTOKlima3Errors5 | DIGITAL | IOD_PTO_TCP | 00254
PTOKlima3Errors6 | DIGITAL | IOD_PTO_TCP | 00255
PTOKlima3Errors7 | DIGITAL | IOD_PTO_TCP | 00256
PTOKlima3Errors8 | DIGITAL | IOD_PTO_TCP | 00257
PTOKlima3Errors9 | DIGITAL | IOD_PTO_TCP | 00258
PTOKlima4Errors10 | DIGITAL | IOD_PTO_TCP | 00259
PTOKlima4Errors11 | DIGITAL | IOD_PTO_TCP | 00260
PTOKlima4Errors12 | DIGITAL | IOD_PTO_TCP | 00261
PTOKlima4Errors13 | DIGITAL | IOD_PTO_TCP | 00262
PTOKlima4Errors14 | DIGITAL | IOD_PTO_TCP | 00263
PTOKlima4Errors15 | DIGITAL | IOD_PTO_TCP | 00264
PTOKlima4Errors16 | DIGITAL | IOD_PTO_TCP | 00265
PTOKlima4Errors17 | DIGITAL | IOD_PTO_TCP | 00266
PTOKlima4Errors18 | DIGITAL | IOD_PTO_TCP | 00267
PTOKlima4Errors19 | DIGITAL | IOD_PTO_TCP | 00268
PTOKlima4Errors1 | DIGITAL | IOD_PTO_TCP | 00269
PTOKlima4Errors20 | DIGITAL | IOD_PTO_TCP | 00270
PTOKlima4Errors21 | DIGITAL | IOD_PTO_TCP | 00271
PTOKlima4Errors22 | DIGITAL | IOD_PTO_TCP | 00272
PTOKlima4Errors23 | DIGITAL | IOD_PTO_TCP | 00273
PTOKlima4Errors24 | DIGITAL | IOD_PTO_TCP | 00274
PTOKlima4Errors25 | DIGITAL | IOD_PTO_TCP | 00275
PTOKlima4Errors26 | DIGITAL | IOD_PTO_TCP | 00276
PTOKlima4Errors27 | DIGITAL | IOD_PTO_TCP | 00277
PTOKlima4Errors28 | DIGITAL | IOD_PTO_TCP | 00278
PTOKlima4Errors29 | DIGITAL | IOD_PTO_TCP | 00279
PTOKlima4Errors2 | DIGITAL | IOD_PTO_TCP | 00280
PTOKlima4Errors30 | DIGITAL | IOD_PTO_TCP | 00281
PTOKlima4Errors31 | DIGITAL | IOD_PTO_TCP | 00282
PTOKlima4Errors32 | DIGITAL | IOD_PTO_TCP | 00283
PTOKlima4Errors33 | DIGITAL | IOD_PTO_TCP | 00284
PTOKlima4Errors34 | DIGITAL | IOD_PTO_TCP | 00285
PTOKlima4Errors35 | DIGITAL | IOD_PTO_TCP | 00286
PTOKlima4Errors3 | DIGITAL | IOD_PTO_TCP | 00287
PTOKlima4Errors4 | DIGITAL | IOD_PTO_TCP | 00288
PTOKlima4Errors5 | DIGITAL | IOD_PTO_TCP | 00289
PTOKlima4Errors6 | DIGITAL | IOD_PTO_TCP | 00290
PTOKlima4Errors7 | DIGITAL | IOD_PTO_TCP | 00291
PTOKlima4Errors8 | DIGITAL | IOD_PTO_TCP | 00292
PTOKlima4Errors9 | DIGITAL | IOD_PTO_TCP | 00293
PTOKlima5Errors10 | DIGITAL | IOD_PTO_TCP | 00294
PTOKlima5Errors11 | DIGITAL | IOD_PTO_TCP | 00295
PTOKlima5Errors12 | DIGITAL | IOD_PTO_TCP | 00296
PTOKlima5Errors13 | DIGITAL | IOD_PTO_TCP | 00297
PTOKlima5Errors14 | DIGITAL | IOD_PTO_TCP | 00298
PTOKlima5Errors15 | DIGITAL | IOD_PTO_TCP | 00299
PTOKlima5Errors16 | DIGITAL | IOD_PTO_TCP | 00300
PTOKlima5Errors17 | DIGITAL | IOD_PTO_TCP | 00301
PTOKlima5Errors18 | DIGITAL | IOD_PTO_TCP | 00302
PTOKlima5Errors19 | DIGITAL | IOD_PTO_TCP | 00303
PTOKlima5Errors1 | DIGITAL | IOD_PTO_TCP | 00304
PTOKlima5Errors20 | DIGITAL | IOD_PTO_TCP | 00305
PTOKlima5Errors21 | DIGITAL | IOD_PTO_TCP | 00306
PTOKlima5Errors22 | DIGITAL | IOD_PTO_TCP | 00307
PTOKlima5Errors23 | DIGITAL | IOD_PTO_TCP | 00308
PTOKlima5Errors24 | DIGITAL | IOD_PTO_TCP | 00309
PTOKlima5Errors25 | DIGITAL | IOD_PTO_TCP | 00310
PTOKlima5Errors26 | DIGITAL | IOD_PTO_TCP | 00311
PTOKlima5Errors27 | DIGITAL | IOD_PTO_TCP | 00312
PTOKlima5Errors28 | DIGITAL | IOD_PTO_TCP | 00313
PTOKlima5Errors29 | DIGITAL | IOD_PTO_TCP | 00314
PTOKlima5Errors2 | DIGITAL | IOD_PTO_TCP | 00315
PTOKlima5Errors30 | DIGITAL | IOD_PTO_TCP | 00316
PTOKlima5Errors31 | DIGITAL | IOD_PTO_TCP | 00317
PTOKlima5Errors32 | DIGITAL | IOD_PTO_TCP | 00318
PTOKlima5Errors33 | DIGITAL | IOD_PTO_TCP | 00319
PTOKlima5Errors34 | DIGITAL | IOD_PTO_TCP | 00320
PTOKlima5Errors35 | DIGITAL | IOD_PTO_TCP | 00321
PTOKlima5Errors3 | DIGITAL | IOD_PTO_TCP | 00322
PTOKlima5Errors4 | DIGITAL | IOD_PTO_TCP | 00323
PTOKlima5Errors5 | DIGITAL | IOD_PTO_TCP | 00324
PTOKlima5Errors6 | DIGITAL | IOD_PTO_TCP | 00325
PTOKlima5Errors7 | DIGITAL | IOD_PTO_TCP | 00326
PTOKlima5Errors8 | DIGITAL | IOD_PTO_TCP | 00327
PTOKlima5Errors9 | DIGITAL | IOD_PTO_TCP | 00328
PTOKlima6Errors10 | DIGITAL | IOD_PTO_TCP | 00329
PTOKlima6Errors11 | DIGITAL | IOD_PTO_TCP | 00330
PTOKlima6Errors12 | DIGITAL | IOD_PTO_TCP | 00331
PTOKlima6Errors13 | DIGITAL | IOD_PTO_TCP | 00332
PTOKlima6Errors14 | DIGITAL | IOD_PTO_TCP | 00333
PTOKlima6Errors15 | DIGITAL | IOD_PTO_TCP | 00334
PTOKlima6Errors16 | DIGITAL | IOD_PTO_TCP | 00335
PTOKlima6Errors17 | DIGITAL | IOD_PTO_TCP | 00336
PTOKlima6Errors18 | DIGITAL | IOD_PTO_TCP | 00337
PTOKlima6Errors19 | DIGITAL | IOD_PTO_TCP | 00338
PTOKlima6Errors1 | DIGITAL | IOD_PTO_TCP | 00339
PTOKlima6Errors20 | DIGITAL | IOD_PTO_TCP | 00340
PTOKlima6Errors21 | DIGITAL | IOD_PTO_TCP | 00341
PTOKlima6Errors22 | DIGITAL | IOD_PTO_TCP | 00342
PTOKlima6Errors23 | DIGITAL | IOD_PTO_TCP | 00343
PTOKlima6Errors24 | DIGITAL | IOD_PTO_TCP | 00344
PTOKlima6Errors25 | DIGITAL | IOD_PTO_TCP | 00345
PTOKlima6Errors26 | DIGITAL | IOD_PTO_TCP | 00346
PTOKlima6Errors27 | DIGITAL | IOD_PTO_TCP | 00347
PTOKlima6Errors28 | DIGITAL | IOD_PTO_TCP | 00348
PTOKlima6Errors29 | DIGITAL | IOD_PTO_TCP | 00349
PTOKlima6Errors2 | DIGITAL | IOD_PTO_TCP | 00350
PTOKlima6Errors30 | DIGITAL | IOD_PTO_TCP | 00351
PTOKlima6Errors31 | DIGITAL | IOD_PTO_TCP | 00352
PTOKlima6Errors32 | DIGITAL | IOD_PTO_TCP | 00353
PTOKlima6Errors33 | DIGITAL | IOD_PTO_TCP | 00354
PTOKlima6Errors34 | DIGITAL | IOD_PTO_TCP | 00355
PTOKlima6Errors35 | DIGITAL | IOD_PTO_TCP | 00356
PTOKlima6Errors3 | DIGITAL | IOD_PTO_TCP | 00357
PTOKlima6Errors4 | DIGITAL | IOD_PTO_TCP | 00358
PTOKlima6Errors5 | DIGITAL | IOD_PTO_TCP | 00359
PTOKlima6Errors6 | DIGITAL | IOD_PTO_TCP | 00360
PTOKlima6Errors7 | DIGITAL | IOD_PTO_TCP | 00361
PTOKlima6Errors8 | DIGITAL | IOD_PTO_TCP | 00362
PTOKlima6Errors9 | DIGITAL | IOD_PTO_TCP | 00363
PTOKlima1Deluje | DIGITAL | IOD_PTO_TCP | 00364
PTOKlima1FenThermalCutout | DIGITAL | IOD_PTO_TCP | 00365
PTOKlima1GeneralAlarm | DIGITAL | IOD_PTO_TCP | 00366
PTOKlima1GrelecStatus | INT | IOD_PTO_TCP | 40151
PTOKlima1IzhodniVentStatus | INT | IOD_PTO_TCP | 40152
PTOKlima1Kompresor1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00367
PTOKlima1Kompresor2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00368
PTOKlima1KompresorStatus | INT | IOD_PTO_TCP | 40153
PTOKlima1Napaka | DIGITAL | IOD_PTO_TCP | 00369
PTOKlima1NapakaPriPretokuZraka | DIGITAL | IOD_PTO_TCP | 00370
PTOKlima1NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO_TCP | 00371
PTOKlima1NapakaSenzorTempProstora | DIGITAL | IOD_PTO_TCP | 00372
PTOKlima1NapakaSenzorVlaznosti | DIGITAL | IOD_PTO_TCP | 00373
PTOKlima1NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO_TCP | 00374
PTOKlima1NiTokaVVlazilcu | DIGITAL | IOD_PTO_TCP | 00375
PTOKlima1NiVodeVVlazilcu | DIGITAL | IOD_PTO_TCP | 00376
PTOKlima1NizekPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 00377
PTOKlima1NizekPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 00378
PTOKlima1NizkaTempVProstoru | DIGITAL | IOD_PTO_TCP | 00379
PTOKlima1NizkaVlaznost | DIGITAL | IOD_PTO_TCP | 00380
PTOKlima1ObratovalneUre | REAL | IOD_PTO_TCP | 44001 |  |  |  |  | h | ####
PTOKlima1OnOffEnablingBySupervisor | DIGITAL | IOD_PTO_TCP | 00381
PTOKlima1PozarniAlarm | DIGITAL | IOD_PTO_TCP | 00382
PTOKlima1Razvlazevanje | DIGITAL | IOD_PTO_TCP | 00383
PTOKlima1RemoteOFFtoOutput | DIGITAL | IOD_PTO_TCP | 00384
PTOKlima1RocniIzklop | DIGITAL | IOD_PTO_TCP | 00385
PTOKlima1SenzorjiStatus | DIGITAL | IOD_PTO_TCP | 00386
PTOKlima1TemperaturaProstora | REAL | IOD_PTO_TCP | 44003 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima1TempIzpihanegaZraka | REAL | IOD_PTO_TCP | 44005
PTOKlima1UnitOnOff | DIGITAL | IOD_PTO_TCP | 00387
PTOKlima1VisokaTempVProstoru | DIGITAL | IOD_PTO_TCP | 00388
PTOKlima1VisokaVlaznost | DIGITAL | IOD_PTO_TCP | 00389
PTOKlima1VisokTokVVlazilcu | DIGITAL | IOD_PTO_TCP | 00390
PTOKlima1Vlazenje | DIGITAL | IOD_PTO_TCP | 00391
PTOKlima1VlazilecStatus | INT | IOD_PTO_TCP | 40154
PTOKlima1VlaznostProstora | REAL | IOD_PTO_TCP | 44007 | 0 | 100 | 0 | 100 | % | ####.#
PTOKlima1ZamasenFilter | DIGITAL | IOD_PTO_TCP | 00392
PTOKlima1ZunanjaTemp | REAL | IOD_PTO_TCP | 44009
PTOKlima2Deluje | DIGITAL | IOD_PTO_TCP | 00393
PTOKlima2FenThermalCutout | DIGITAL | IOD_PTO_TCP | 00394
PTOKlima2GeneralAlarm | DIGITAL | IOD_PTO_TCP | 00395
PTOKlima2GrelecStatus | INT | IOD_PTO_TCP | 40155
PTOKlima2IzhodniVentStatus | INT | IOD_PTO_TCP | 40156
PTOKlima2Kompresor1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00396
PTOKlima2Kompresor2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00397
PTOKlima2KompresorStatus | INT | IOD_PTO_TCP | 40157
PTOKlima2Napaka | DIGITAL | IOD_PTO_TCP | 00398
PTOKlima2NapakaPriPretokuZraka | DIGITAL | IOD_PTO_TCP | 00399
PTOKlima2NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO_TCP | 00400
PTOKlima2NapakaSenzorTempProstora | DIGITAL | IOD_PTO_TCP | 00401
PTOKlima2NapakaSenzorVlaznosti | DIGITAL | IOD_PTO_TCP | 00402
PTOKlima2NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO_TCP | 00403
PTOKlima2NiTokaVVlazilcu | DIGITAL | IOD_PTO_TCP | 00404
PTOKlima2NiVodeVVlazilcu | DIGITAL | IOD_PTO_TCP | 00405
PTOKlima2NizekPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 00406
PTOKlima2NizekPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 00407
PTOKlima2NizkaTempVProstoru | DIGITAL | IOD_PTO_TCP | 00408
PTOKlima2NizkaVlaznost | DIGITAL | IOD_PTO_TCP | 00409
PTOKlima2ObratovalneUre | REAL | IOD_PTO_TCP | 44011 |  |  |  |  | h | ####
PTOKlima2OnOffEnablingBySupervisor | DIGITAL | IOD_PTO_TCP | 00410
PTOKlima2PozarniAlarm | DIGITAL | IOD_PTO_TCP | 00411
PTOKlima2Razvlazevanje | DIGITAL | IOD_PTO_TCP | 00412
PTOKlima2RemoteOFFtoOutput | DIGITAL | IOD_PTO_TCP | 00413
PTOKlima2RocniIzklop | DIGITAL | IOD_PTO_TCP | 00414
PTOKlima2SenzorjiStatus | DIGITAL | IOD_PTO_TCP | 00415
PTOKlima2TemperaturaProstora | REAL | IOD_PTO_TCP | 44013 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima2TempIzpihanegaZraka | REAL | IOD_PTO_TCP | 44015
PTOKlima2UnitOnOff | DIGITAL | IOD_PTO_TCP | 00416
PTOKlima2VisokaTempVProstoru | DIGITAL | IOD_PTO_TCP | 00417
PTOKlima2VisokaVlaznost | DIGITAL | IOD_PTO_TCP | 00418
PTOKlima2VisokTokVVlazilcu | DIGITAL | IOD_PTO_TCP | 00419
PTOKlima2Vlazenje | DIGITAL | IOD_PTO_TCP | 00420
PTOKlima2VlazilecStatus | INT | IOD_PTO_TCP | 40158
PTOKlima2VlaznostProstora | REAL | IOD_PTO_TCP | 44017 | 0 | 100 | 0 | 100 | % | ####.#
PTOKlima2ZamasenFilter | DIGITAL | IOD_PTO_TCP | 00421
PTOKlima2ZunanjaTemp | REAL | IOD_PTO_TCP | 44019
PTOKlima3Deluje | DIGITAL | IOD_PTO_TCP | 00422
PTOKlima3FenThermalCutout | DIGITAL | IOD_PTO_TCP | 00423
PTOKlima3GeneralAlarm | DIGITAL | IOD_PTO_TCP | 00424
PTOKlima3GrelecStatus | INT | IOD_PTO_TCP | 40159
PTOKlima3IzhodniVentStatus | INT | IOD_PTO_TCP | 40160
PTOKlima3Kompresor1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00425
PTOKlima3Kompresor2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00426
PTOKlima3KompresorStatus | INT | IOD_PTO_TCP | 40161
PTOKlima3Napaka | DIGITAL | IOD_PTO_TCP | 00427
PTOKlima3NapakaPriPretokuZraka | DIGITAL | IOD_PTO_TCP | 00428
PTOKlima3NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO_TCP | 00429
PTOKlima3NapakaSenzorTempProstora | DIGITAL | IOD_PTO_TCP | 00430
PTOKlima3NapakaSenzorVlaznosti | DIGITAL | IOD_PTO_TCP | 00431
PTOKlima3NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO_TCP | 00432
PTOKlima3NiTokaVVlazilcu | DIGITAL | IOD_PTO_TCP | 00433
PTOKlima3NiVodeVVlazilcu | DIGITAL | IOD_PTO_TCP | 00434
PTOKlima3NizekPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 00435
PTOKlima3NizekPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 00436
PTOKlima3NizkaTempVProstoru | DIGITAL | IOD_PTO_TCP | 00437
PTOKlima3NizkaVlaznost | DIGITAL | IOD_PTO_TCP | 00438
PTOKlima3ObratovalneUre | REAL | IOD_PTO_TCP | 44021 |  |  |  |  | h | ####
PTOKlima3OnOffEnablingBySupervisor | DIGITAL | IOD_PTO_TCP | 00439
PTOKlima3PozarniAlarm | DIGITAL | IOD_PTO_TCP | 00440
PTOKlima3Razvlazevanje | DIGITAL | IOD_PTO_TCP | 00441
PTOKlima3RemoteOFFtoOutput | DIGITAL | IOD_PTO_TCP | 00442
PTOKlima3RocniIzklop | DIGITAL | IOD_PTO_TCP | 00443
PTOKlima3SenzorjiStatus | DIGITAL | IOD_PTO_TCP | 00444
PTOKlima3TemperaturaProstora | REAL | IOD_PTO_TCP | 44023 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima3TempIzpihanegaZraka | REAL | IOD_PTO_TCP | 44025
PTOKlima3UnitOnOff | DIGITAL | IOD_PTO_TCP | 00445
PTOKlima3VisokaTempVProstoru | DIGITAL | IOD_PTO_TCP | 00446
PTOKlima3VisokaVlaznost | DIGITAL | IOD_PTO_TCP | 00447
PTOKlima3VisokTokVVlazilcu | DIGITAL | IOD_PTO_TCP | 00448
PTOKlima3Vlazenje | DIGITAL | IOD_PTO_TCP | 00449
PTOKlima3VlazilecStatus | INT | IOD_PTO_TCP | 40162
PTOKlima3VlaznostProstora | REAL | IOD_PTO_TCP | 44027 | 0 | 100 | 0 | 100 | % | ####.#
PTOKlima3ZamasenFilter | DIGITAL | IOD_PTO_TCP | 00450
PTOKlima3ZunanjaTemp | REAL | IOD_PTO_TCP | 44029
PTOKlima4Deluje | DIGITAL | IOD_PTO_TCP | 00451
PTOKlima4FenThermalCutout | DIGITAL | IOD_PTO_TCP | 00452
PTOKlima4GeneralAlarm | DIGITAL | IOD_PTO_TCP | 00453
PTOKlima4GrelecStatus | INT | IOD_PTO_TCP | 40163
PTOKlima4IzhodniVentStatus | INT | IOD_PTO_TCP | 40164
PTOKlima4Kompresor1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00454
PTOKlima4Kompresor2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00455
PTOKlima4KompresorStatus | INT | IOD_PTO_TCP | 40165
PTOKlima4Napaka | DIGITAL | IOD_PTO_TCP | 00456
PTOKlima4NapakaPriPretokuZraka | DIGITAL | IOD_PTO_TCP | 00457
PTOKlima4NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO_TCP | 00458
PTOKlima4NapakaSenzorTempProstora | DIGITAL | IOD_PTO_TCP | 00459
PTOKlima4NapakaSenzorVlaznosti | DIGITAL | IOD_PTO_TCP | 00460
PTOKlima4NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO_TCP | 00461
PTOKlima4NiTokaVVlazilcu | DIGITAL | IOD_PTO_TCP | 00462
PTOKlima4NiVodeVVlazilcu | DIGITAL | IOD_PTO_TCP | 00463
PTOKlima4NizekPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 00464
PTOKlima4NizekPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 00465
PTOKlima4NizkaTempVProstoru | DIGITAL | IOD_PTO_TCP | 00466
PTOKlima4NizkaVlaznost | DIGITAL | IOD_PTO_TCP | 00467
PTOKlima4ObratovalneUre | REAL | IOD_PTO_TCP | 44031 |  |  |  |  | h | ####
PTOKlima4OnOffEnablingBySupervisor | DIGITAL | IOD_PTO_TCP | 00468
PTOKlima4PozarniAlarm | DIGITAL | IOD_PTO_TCP | 00469
PTOKlima4Razvlazevanje | DIGITAL | IOD_PTO_TCP | 00470
PTOKlima4RemoteOFFtoOutput | DIGITAL | IOD_PTO_TCP | 00471
PTOKlima4RocniIzklop | DIGITAL | IOD_PTO_TCP | 00472
PTOKlima4SenzorjiStatus | DIGITAL | IOD_PTO_TCP | 00473
PTOKlima4TemperaturaProstora | REAL | IOD_PTO_TCP | 44033 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima4TempIzpihanegaZraka | REAL | IOD_PTO_TCP | 44035
PTOKlima4UnitOnOff | DIGITAL | IOD_PTO_TCP | 00474
PTOKlima4VisokaTempVProstoru | DIGITAL | IOD_PTO_TCP | 00475
PTOKlima4VisokaVlaznost | DIGITAL | IOD_PTO_TCP | 00476
PTOKlima4VisokTokVVlazilcu | DIGITAL | IOD_PTO_TCP | 00477
PTOKlima4Vlazenje | DIGITAL | IOD_PTO_TCP | 00478
PTOKlima4VlazilecStatus | INT | IOD_PTO_TCP | 40166
PTOKlima4VlaznostProstora | REAL | IOD_PTO_TCP | 44037 | 0 | 100 | 0 | 100 | % | ####.#
PTOKlima4ZamasenFilter | DIGITAL | IOD_PTO_TCP | 00479
PTOKlima4ZunanjaTemp | REAL | IOD_PTO_TCP | 44039
PTOKlima5Deluje | DIGITAL | IOD_PTO_TCP | 00480
PTOKlima5FenThermalCutout | DIGITAL | IOD_PTO_TCP | 00481
PTOKlima5GeneralAlarm | DIGITAL | IOD_PTO_TCP | 00482
PTOKlima5GrelecStatus | INT | IOD_PTO_TCP | 40167
PTOKlima5IzhodniVentStatus | INT | IOD_PTO_TCP | 40168
PTOKlima5Kompresor1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00483
PTOKlima5Kompresor2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00484
PTOKlima5KompresorStatus | INT | IOD_PTO_TCP | 40169
PTOKlima5Napaka | DIGITAL | IOD_PTO_TCP | 00485
PTOKlima5NapakaPriPretokuZraka | DIGITAL | IOD_PTO_TCP | 00486
PTOKlima5NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO_TCP | 00487
PTOKlima5NapakaSenzorTempProstora | DIGITAL | IOD_PTO_TCP | 00488
PTOKlima5NapakaSenzorVlaznosti | DIGITAL | IOD_PTO_TCP | 00489
PTOKlima5NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO_TCP | 00490
PTOKlima5NiTokaVVlazilcu | DIGITAL | IOD_PTO_TCP | 00491
PTOKlima5NiVodeVVlazilcu | DIGITAL | IOD_PTO_TCP | 00492
PTOKlima5NizekPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 00493
PTOKlima5NizekPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 00494
PTOKlima5NizkaTempVProstoru | DIGITAL | IOD_PTO_TCP | 00495
PTOKlima5NizkaVlaznost | DIGITAL | IOD_PTO_TCP | 00496
PTOKlima5ObratovalneUre | REAL | IOD_PTO_TCP | 44041 |  |  |  |  | h | ####
PTOKlima5OnOffEnablingBySupervisor | DIGITAL | IOD_PTO_TCP | 00497
PTOKlima5PozarniAlarm | DIGITAL | IOD_PTO_TCP | 00498
PTOKlima5Razvlazevanje | DIGITAL | IOD_PTO_TCP | 00499
PTOKlima5RemoteOFFtoOutput | DIGITAL | IOD_PTO_TCP | 00500
PTOKlima5RocniIzklop | DIGITAL | IOD_PTO_TCP | 00501
PTOKlima5SenzorjiStatus | DIGITAL | IOD_PTO_TCP | 00502
PTOKlima5TemperaturaProstora | REAL | IOD_PTO_TCP | 44043 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima5TempIzpihanegaZraka | REAL | IOD_PTO_TCP | 44045
PTOKlima5UnitOnOff | DIGITAL | IOD_PTO_TCP | 00503
PTOKlima5VisokaTempVProstoru | DIGITAL | IOD_PTO_TCP | 00504
PTOKlima5VisokaVlaznost | DIGITAL | IOD_PTO_TCP | 00505
PTOKlima5VisokTokVVlazilcu | DIGITAL | IOD_PTO_TCP | 00506
PTOKlima5Vlazenje | DIGITAL | IOD_PTO_TCP | 00507
PTOKlima5VlazilecStatus | INT | IOD_PTO_TCP | 40170
PTOKlima5VlaznostProstora | REAL | IOD_PTO_TCP | 44047 | 0 | 100 | 0 | 100 | % | ####.#
PTOKlima5ZamasenFilter | DIGITAL | IOD_PTO_TCP | 00508
PTOKlima5ZunanjaTemp | REAL | IOD_PTO_TCP | 44049
PTOKlima6Deluje | DIGITAL | IOD_PTO_TCP | 00509
PTOKlima6FenThermalCutout | DIGITAL | IOD_PTO_TCP | 00510
PTOKlima6GeneralAlarm | DIGITAL | IOD_PTO_TCP | 00511
PTOKlima6GrelecStatus | INT | IOD_PTO_TCP | 40171
PTOKlima6IzhodniVentStatus | INT | IOD_PTO_TCP | 40172
PTOKlima6Kompresor1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00512
PTOKlima6Kompresor2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00513
PTOKlima6KompresorStatus | INT | IOD_PTO_TCP | 40173
PTOKlima6Napaka | DIGITAL | IOD_PTO_TCP | 00514
PTOKlima6NapakaPriPretokuZraka | DIGITAL | IOD_PTO_TCP | 00515
PTOKlima6NapakaSenzorTempIzpiha | DIGITAL | IOD_PTO_TCP | 00516
PTOKlima6NapakaSenzorTempProstora | DIGITAL | IOD_PTO_TCP | 00517
PTOKlima6NapakaSenzorVlaznosti | DIGITAL | IOD_PTO_TCP | 00518
PTOKlima6NapakaSenzorZunanjeTemp | DIGITAL | IOD_PTO_TCP | 00519
PTOKlima6NiTokaVVlazilcu | DIGITAL | IOD_PTO_TCP | 00520
PTOKlima6NiVodeVVlazilcu | DIGITAL | IOD_PTO_TCP | 00521
PTOKlima6NizekPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 00522
PTOKlima6NizekPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 00523
PTOKlima6NizkaTempVProstoru | DIGITAL | IOD_PTO_TCP | 00524
PTOKlima6NizkaVlaznost | DIGITAL | IOD_PTO_TCP | 00525
PTOKlima6ObratovalneUre | REAL | IOD_PTO_TCP | 44051 |  |  |  |  | h | ####
PTOKlima6OnOffEnablingBySupervisor | DIGITAL | IOD_PTO_TCP | 00526
PTOKlima6PozarniAlarm | DIGITAL | IOD_PTO_TCP | 00527
PTOKlima6Razvlazevanje | DIGITAL | IOD_PTO_TCP | 00528
PTOKlima6RemoteOFFtoOutput | DIGITAL | IOD_PTO_TCP | 00529
PTOKlima6RocniIzklop | DIGITAL | IOD_PTO_TCP | 00530
PTOKlima6SenzorjiStatus | DIGITAL | IOD_PTO_TCP | 00531
PTOKlima6TemperaturaProstora | REAL | IOD_PTO_TCP | 44053 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima6TempIzpihanegaZraka | REAL | IOD_PTO_TCP | 44055
PTOKlima6UnitOnOff | DIGITAL | IOD_PTO_TCP | 00532
PTOKlima6VisokaTempVProstoru | DIGITAL | IOD_PTO_TCP | 00533
PTOKlima6VisokaVlaznost | DIGITAL | IOD_PTO_TCP | 00534
PTOKlima6VisokTokVVlazilcu | DIGITAL | IOD_PTO_TCP | 00535
PTOKlima6Vlazenje | DIGITAL | IOD_PTO_TCP | 00536
PTOKlima6VlazilecStatus | INT | IOD_PTO_TCP | 40174
PTOKlima6VlaznostProstora | REAL | IOD_PTO_TCP | 44057 | 0 | 100 | 0 | 100 | % | ####.#
PTOKlima6ZamasenFilter | DIGITAL | IOD_PTO_TCP | 00537
PTOKlima6ZunanjaTemp | REAL | IOD_PTO_TCP | 44059
PTOKlimeNaCas0 | DIGITAL | IOD_PTO_TCP | 00538
PTOKlimeNaCas1 | DIGITAL | IOD_PTO_TCP | 00539
PTOKlimeNaCas2 | DIGITAL | IOD_PTO_TCP | 00540
PTOKlimeNaCas3 | DIGITAL | IOD_PTO_TCP | 00541
PTOMrezaIzpad | DIGITAL | IOD_PTO_TCP | 00542
PTOMrezaIzpadKlimaOff1 | DIGITAL | IOD_PTO_TCP | 00543
PTOMrezaIzpadKlimaOff2 | DIGITAL | IOD_PTO_TCP | 00544
PTOMrezaIzpadKlimaOff3 | DIGITAL | IOD_PTO_TCP | 00545
PTOMrezaIzpadKlimaOff4 | DIGITAL | IOD_PTO_TCP | 00546
PTOMrezaIzpadKlimaOff5 | DIGITAL | IOD_PTO_TCP | 00547
PTOMrezaIzpadKlimaOff6 | DIGITAL | IOD_PTO_TCP | 00548
PTOMrezaIzpadVklopDelay1 | INT | IOD_PTO_TCP | 40175
PTOMrezaIzpadVklopDelay2 | INT | IOD_PTO_TCP | 40176
PTOMrezaIzpadVklopDelay3 | INT | IOD_PTO_TCP | 40177
PTOMrezaIzpadVklopDelay4 | INT | IOD_PTO_TCP | 40178
PTOMrezaIzpadVklopDelay5 | INT | IOD_PTO_TCP | 40179
PTOMrezaIzpadVklopDelay6 | INT | IOD_PTO_TCP | 40180
PTONapakaSenzorTemp1 | DIGITAL | IOD_PTO_TCP | 00549
PTONapakaSenzorTemp2 | DIGITAL | IOD_PTO_TCP | 00550
PTONapakaSenzorTemp3 | DIGITAL | IOD_PTO_TCP | 00551
PTONapakaSenzorTemp4 | DIGITAL | IOD_PTO_TCP | 00552
PTONapakaSenzorTemp5 | DIGITAL | IOD_PTO_TCP | 00553
PTONapakaSenzorTemp6 | DIGITAL | IOD_PTO_TCP | 00554
PTONapakaSenzorVlaga1 | DIGITAL | IOD_PTO_TCP | 00555
PTONapakaSenzorVlaga2 | DIGITAL | IOD_PTO_TCP | 00556
PTONapakaSenzorVlaga3 | DIGITAL | IOD_PTO_TCP | 00557
PTONapakaSenzorVlaga4 | DIGITAL | IOD_PTO_TCP | 00558
PTONapakaSenzorVlaga5 | DIGITAL | IOD_PTO_TCP | 00559
PTONapakaSenzorVlaga6 | DIGITAL | IOD_PTO_TCP | 00560
PTOPMMActiveEnergyConsumed_kWh | REAL | IOD_PTO_TCP | 44061 |  |  |  |  | kVAr | ####
PTOPMMActivePowerPhaseA_kW | REAL | IOD_PTO_TCP | 44063 | 0 | 100 | 0 | 100 | kW | ####.#
PTOPMMActivePowerPhaseB_kW | REAL | IOD_PTO_TCP | 44065 | 0 | 100 | 0 | 100 | kW | ####.#
PTOPMMActivePowerPhaseC_kW | REAL | IOD_PTO_TCP | 44067 | 0 | 100 | 0 | 100 | kW | ####.#
PTOPMMAlarmPhase1C01_16_60to80 | INT | IOD_PTO_TCP | 40181
PTOPMMAlarmPhase1C01_16_over80 | INT | IOD_PTO_TCP | 40182
PTOPMMAlarmPhase1C17_32_60to80 | INT | IOD_PTO_TCP | 40183
PTOPMMAlarmPhase1C17_32_over80 | INT | IOD_PTO_TCP | 40184
PTOPMMAlarmPhase1C33_42_60to80 | INT | IOD_PTO_TCP | 40185
PTOPMMAlarmPhase1C33_42_over80 | INT | IOD_PTO_TCP | 40186
PTOPMMAlarmPhase2C01_16_60to80 | INT | IOD_PTO_TCP | 40187
PTOPMMAlarmPhase2C01_16_over80 | INT | IOD_PTO_TCP | 40188
PTOPMMAlarmPhase2C17_32_60to80 | INT | IOD_PTO_TCP | 40189
PTOPMMAlarmPhase2C17_32_over80 | INT | IOD_PTO_TCP | 40190
PTOPMMAlarmPhase2C33_42_60to80 | INT | IOD_PTO_TCP | 40191
PTOPMMAlarmPhase2C33_42_over80 | INT | IOD_PTO_TCP | 40192
PTOPMMAlarmPhase3C01_16_60to80 | INT | IOD_PTO_TCP | 40193
PTOPMMAlarmPhase3C01_16_over80 | INT | IOD_PTO_TCP | 40194
PTOPMMAlarmPhase3C17_32_60to80 | INT | IOD_PTO_TCP | 40195
PTOPMMAlarmPhase3C17_32_over80 | INT | IOD_PTO_TCP | 40196
PTOPMMAlarmPhase3C33_42_60to80 | INT | IOD_PTO_TCP | 40197
PTOPMMAlarmPhase3C33_42_over80 | INT | IOD_PTO_TCP | 40198
PTOPMMAparentPowerPhaseA | REAL | IOD_PTO_TCP | 44069 | 0 | 100 | 0 | 100 | kVAr | ####.#
PTOPMMAparentPowerPhaseB | REAL | IOD_PTO_TCP | 44071 | 0 | 100 | 0 | 100 | kVAr | ####.#
PTOPMMAparentPowerPhaseC | REAL | IOD_PTO_TCP | 44073 | 0 | 100 | 0 | 100 | kVAr | ####.#
PTOPMMAverageCurrent_A | REAL | IOD_PTO_TCP | 44075 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMAveragePhaseToNeutral_V | REAL | IOD_PTO_TCP | 44077 | 0 | 270 | 0 | 270 | V | ####.#
PTOPMMAveragePhaseToPhase_V | REAL | IOD_PTO_TCP | 44079 | 0 | 450 | 0 | 450 | V | ####.#
PTOPMMCurrentInPhaseA_A | REAL | IOD_PTO_TCP | 44081 | 0 | 500 | 0 | 500 | A | ####.#
PTOPMMCurrentInPhaseB_A | REAL | IOD_PTO_TCP | 44083 | 0 | 500 | 0 | 500 | A | ####.#
PTOPMMCurrentInPhaseC_A | REAL | IOD_PTO_TCP | 44085 | 0 | 500 | 0 | 500 | A | ####.#
PTOPMMFrequency_Hz | REAL | IOD_PTO_TCP | 44087 | 0 | 70 | 0 | 70 | Hz | ####.#
PTOPMMNapaka | DIGITAL | IOD_PTO_TCP | 00561
PTOPMMPhase1Current10 | REAL | IOD_PTO_TCP | 44089 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current11 | REAL | IOD_PTO_TCP | 44091 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current12 | REAL | IOD_PTO_TCP | 44093 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current13 | REAL | IOD_PTO_TCP | 44095 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current14 | REAL | IOD_PTO_TCP | 44097 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current15 | REAL | IOD_PTO_TCP | 44099 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current16 | REAL | IOD_PTO_TCP | 44101 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current17 | REAL | IOD_PTO_TCP | 44103 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current18 | REAL | IOD_PTO_TCP | 44105 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current19 | REAL | IOD_PTO_TCP | 44107 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current1 | REAL | IOD_PTO_TCP | 44109 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current20 | REAL | IOD_PTO_TCP | 44111 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current21 | REAL | IOD_PTO_TCP | 44113 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current22 | REAL | IOD_PTO_TCP | 44115 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current23 | REAL | IOD_PTO_TCP | 44117 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current24 | REAL | IOD_PTO_TCP | 44119 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current25 | REAL | IOD_PTO_TCP | 44121 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current26 | REAL | IOD_PTO_TCP | 44123 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current27 | REAL | IOD_PTO_TCP | 44125 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current28 | REAL | IOD_PTO_TCP | 44127 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current29 | REAL | IOD_PTO_TCP | 44129 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current2 | REAL | IOD_PTO_TCP | 44131 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current30 | REAL | IOD_PTO_TCP | 44133 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current31 | REAL | IOD_PTO_TCP | 44135 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current32 | REAL | IOD_PTO_TCP | 44137 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current33 | REAL | IOD_PTO_TCP | 44139 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current34 | REAL | IOD_PTO_TCP | 44141 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current35 | REAL | IOD_PTO_TCP | 44143 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current36 | REAL | IOD_PTO_TCP | 44145 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current37 | REAL | IOD_PTO_TCP | 44147 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current38 | REAL | IOD_PTO_TCP | 44149 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current39 | REAL | IOD_PTO_TCP | 44151 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current3 | REAL | IOD_PTO_TCP | 44153 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current40 | REAL | IOD_PTO_TCP | 44155 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current41 | REAL | IOD_PTO_TCP | 44157 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current42 | REAL | IOD_PTO_TCP | 44159 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current4 | REAL | IOD_PTO_TCP | 44161 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current5 | REAL | IOD_PTO_TCP | 44163 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current6 | REAL | IOD_PTO_TCP | 44165 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current7 | REAL | IOD_PTO_TCP | 44167 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current8 | REAL | IOD_PTO_TCP | 44169 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase1Current9 | REAL | IOD_PTO_TCP | 44171 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current10 | REAL | IOD_PTO_TCP | 44173 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current11 | REAL | IOD_PTO_TCP | 44175 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current12 | REAL | IOD_PTO_TCP | 44177 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current13 | REAL | IOD_PTO_TCP | 44179 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current14 | REAL | IOD_PTO_TCP | 44181 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current15 | REAL | IOD_PTO_TCP | 44183 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current16 | REAL | IOD_PTO_TCP | 44185 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current17 | REAL | IOD_PTO_TCP | 44187 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current18 | REAL | IOD_PTO_TCP | 44189 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current19 | REAL | IOD_PTO_TCP | 44191 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current1 | REAL | IOD_PTO_TCP | 44193 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current20 | REAL | IOD_PTO_TCP | 44195 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current21 | REAL | IOD_PTO_TCP | 44197 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current22 | REAL | IOD_PTO_TCP | 44199 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current23 | REAL | IOD_PTO_TCP | 44201 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current24 | REAL | IOD_PTO_TCP | 44203 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current25 | REAL | IOD_PTO_TCP | 44205 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current26 | REAL | IOD_PTO_TCP | 44207 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current27 | REAL | IOD_PTO_TCP | 44209 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current28 | REAL | IOD_PTO_TCP | 44211 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current29 | REAL | IOD_PTO_TCP | 44213 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current2 | REAL | IOD_PTO_TCP | 44215 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current30 | REAL | IOD_PTO_TCP | 44217 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current31 | REAL | IOD_PTO_TCP | 44219 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current32 | REAL | IOD_PTO_TCP | 44221 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current33 | REAL | IOD_PTO_TCP | 44223 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current34 | REAL | IOD_PTO_TCP | 44225 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current35 | REAL | IOD_PTO_TCP | 44227 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current36 | REAL | IOD_PTO_TCP | 44229 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current37 | REAL | IOD_PTO_TCP | 44231 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current38 | REAL | IOD_PTO_TCP | 44233 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current39 | REAL | IOD_PTO_TCP | 44235 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current3 | REAL | IOD_PTO_TCP | 44237 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current40 | REAL | IOD_PTO_TCP | 44239 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current41 | REAL | IOD_PTO_TCP | 44241 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current42 | REAL | IOD_PTO_TCP | 44243 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current4 | REAL | IOD_PTO_TCP | 44245 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current5 | REAL | IOD_PTO_TCP | 44247 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current6 | REAL | IOD_PTO_TCP | 44249 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current7 | REAL | IOD_PTO_TCP | 44251 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current8 | REAL | IOD_PTO_TCP | 44253 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase2Current9 | REAL | IOD_PTO_TCP | 44255 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current10 | REAL | IOD_PTO_TCP | 44257 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current11 | REAL | IOD_PTO_TCP | 44259 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current12 | REAL | IOD_PTO_TCP | 44261 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current13 | REAL | IOD_PTO_TCP | 44263 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current14 | REAL | IOD_PTO_TCP | 44265 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current15 | REAL | IOD_PTO_TCP | 44267 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current16 | REAL | IOD_PTO_TCP | 44269 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current17 | REAL | IOD_PTO_TCP | 44271 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current18 | REAL | IOD_PTO_TCP | 44273 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current19 | REAL | IOD_PTO_TCP | 44275 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current1 | REAL | IOD_PTO_TCP | 44277 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current20 | REAL | IOD_PTO_TCP | 44279 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current21 | REAL | IOD_PTO_TCP | 44281 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current22 | REAL | IOD_PTO_TCP | 44283 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current23 | REAL | IOD_PTO_TCP | 44285 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current24 | REAL | IOD_PTO_TCP | 44287 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current25 | REAL | IOD_PTO_TCP | 44289 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current26 | REAL | IOD_PTO_TCP | 44291 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current27 | REAL | IOD_PTO_TCP | 44293 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current28 | REAL | IOD_PTO_TCP | 44295 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current29 | REAL | IOD_PTO_TCP | 44297 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current2 | REAL | IOD_PTO_TCP | 44299 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current30 | REAL | IOD_PTO_TCP | 44301 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current31 | REAL | IOD_PTO_TCP | 44303 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current32 | REAL | IOD_PTO_TCP | 44305 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current33 | REAL | IOD_PTO_TCP | 44307 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current34 | REAL | IOD_PTO_TCP | 44309 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current35 | REAL | IOD_PTO_TCP | 44311 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current36 | REAL | IOD_PTO_TCP | 44313 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current37 | REAL | IOD_PTO_TCP | 44315 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current38 | REAL | IOD_PTO_TCP | 44317 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current39 | REAL | IOD_PTO_TCP | 44319 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current3 | REAL | IOD_PTO_TCP | 44321 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current40 | REAL | IOD_PTO_TCP | 44323 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current41 | REAL | IOD_PTO_TCP | 44325 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current42 | REAL | IOD_PTO_TCP | 44327 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current4 | REAL | IOD_PTO_TCP | 44329 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current5 | REAL | IOD_PTO_TCP | 44331 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current6 | REAL | IOD_PTO_TCP | 44333 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current7 | REAL | IOD_PTO_TCP | 44335 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current8 | REAL | IOD_PTO_TCP | 44337 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPhase3Current9 | REAL | IOD_PTO_TCP | 44339 | 0 | 16 | 0 | 16 | A | ####.#
PTOPMMPowerFactorSys | REAL | IOD_PTO_TCP | 44341 | 0 | 1 | 0 | 1 |  | ####.#
PTOPMMReactiveEnergyConsumed_kVARh | REAL | IOD_PTO_TCP | 44343 |  |  |  |  | kVArh | ####.#
PTOPMMReactivePowerPhaseA | REAL | IOD_PTO_TCP | 44345 | 0 | 100 | 0 | 100 | kVAr | ####.#
PTOPMMReactivePowerPhaseB | REAL | IOD_PTO_TCP | 44347 | 0 | 100 | 0 | 100 | kVAr | ####.#
PTOPMMReactivePowerPhaseC | REAL | IOD_PTO_TCP | 44349 | 0 | 100 | 0 | 100 | kVAr | ####.#
PTOPMMTotalActivePower_kW | REAL | IOD_PTO_TCP | 44351 | 0 | 300 | 0 | 300 | kW | ####.#
PTOPMMTotalAparentPower_kVA | REAL | IOD_PTO_TCP | 44353 | 0 | 300 | 0 | 300 | kVA | ####.#
PTOPMMTotalPowerFactor | REAL | IOD_PTO_TCP | 44355 | 0 | 1 | 0 | 1 |  | ####.#
PTOPMMTotalReactivePower_kVAR | REAL | IOD_PTO_TCP | 44357 | 0 | 300 | 0 | 300 | kVAr | ####.#
PTOPMMVirA_fsys | REAL | IOD_PTO_TCP | 44359 | 0 | 70 | 0 | 70 | Hz | ####.#
PTOPMMVirA_Isys | REAL | IOD_PTO_TCP | 44361 | 0 | 1000 | 0 | 1000 | A | ####.#
PTOPMMVirA_PFsys | REAL | IOD_PTO_TCP | 44363 | 0 | 1 | 0 | 0 | 1 | ####.#
PTOPMMVirA_Psys | REAL | IOD_PTO_TCP | 44365 | 0 | 300 | 0 | 300 | kW | ####.#
PTOPMMVirA_Qsys | REAL | IOD_PTO_TCP | 44367 | 0 | 300 | 0 | 300 | kVAr | ####.#
PTOPMMVirA_Ssys | REAL | IOD_PTO_TCP | 44369 | 0 | 300 | 0 | 300 | kVA | ####.#
PTOPMMVirA_Usys | REAL | IOD_PTO_TCP | 44371 | 0 | 450 | 0 | 450 | V | ####.#
PTOPMMVirB_fsys | REAL | IOD_PTO_TCP | 44373 | 0 | 70 | 0 | 70 | Hz | ####.#
PTOPMMVirB_Isys | REAL | IOD_PTO_TCP | 44375 | 0 | 1000 | 0 | 1000 | A | ####.#
PTOPMMVirB_PFsys | REAL | IOD_PTO_TCP | 44377 | 0 | 1 | 0 | 0 | 1 | ####.#
PTOPMMVirB_Psys | REAL | IOD_PTO_TCP | 44379 | 0 | 300 | 0 | 300 | kW | ####.#
PTOPMMVirB_Qsys | REAL | IOD_PTO_TCP | 44381 | 0 | 300 | 0 | 300 | kVAr | ####.#
PTOPMMVirB_Ssys | REAL | IOD_PTO_TCP | 44383 | 0 | 300 | 0 | 300 | kVA | ####.#
PTOPMMVirB_Usys | REAL | IOD_PTO_TCP | 44385 | 0 | 450 | 0 | 450 | V | ####.#
PTOPMMVirBActiveEnergyConsumed_kWh | REAL | IOD_PTO_TCP | 44387 |  |  |  |  | kVArh | ####.#
PTOPMMVirBActivePowerPhaseA_kW | REAL | IOD_PTO_TCP | 44389 | 0 | 100 | 0 | 100 | kW | ####.#
PTOPMMVirBActivePowerPhaseB_kW | REAL | IOD_PTO_TCP | 44391 | 0 | 100 | 0 | 100 | kW | ####.#
PTOPMMVirBActivePowerPhaseC_kW | REAL | IOD_PTO_TCP | 44393 | 0 | 100 | 0 | 100 | kW | ####.#
PTOPMMVirBAparentPowerPhaseA | REAL | IOD_PTO_TCP | 44395 | 0 | 100 | 0 | 100 | kVAr | ####.#
PTOPMMVirBAparentPowerPhaseB | REAL | IOD_PTO_TCP | 44397 | 0 | 100 | 0 | 100 | kVAr | ####.#
PTOPMMVirBAparentPowerPhaseC | REAL | IOD_PTO_TCP | 44399 | 0 | 100 | 0 | 100 | kVAr | ####.#
PTOPMMVirBAverageCurrent_A | REAL | IOD_PTO_TCP | 44401 | 0 | 100 | 0 | 100 | A | ####.#
PTOPMMVirBAveragePhaseToNeutral_V | REAL | IOD_PTO_TCP | 44403 | 0 | 270 | 0 | 270 | V | ####.#
PTOPMMVirBAveragePhaseToPhase_V | REAL | IOD_PTO_TCP | 44405 | 0 | 270 | 0 | 270 | V | ####.#
PTOPMMVirBCurrentInPhaseA_A | REAL | IOD_PTO_TCP | 44407 | 0 | 100 | 0 | 100 | A | ####.#
PTOPMMVirBCurrentInPhaseB_A | REAL | IOD_PTO_TCP | 44409 | 0 | 100 | 0 | 100 | A | ####.#
PTOPMMVirBCurrentInPhaseC_A | REAL | IOD_PTO_TCP | 44411 | 0 | 100 | 0 | 100 | A | ####.#
PTOPMMVirBFrequency_Hz | REAL | IOD_PTO_TCP | 44413 | 0 | 70 | 0 | 70 | Hz | ####.#
PTOPMMVirBPowerFactorSys | REAL | IOD_PTO_TCP | 44415 | 0 | 1 | 0 | 1 |  | ####.#
PTOPMMVirBReactiveEnergyConsumed_kVARh | REAL | IOD_PTO_TCP | 44417 |  |  |  |  | kVArh | ####.#
PTOPMMVirBReactivePowerPhaseA | REAL | IOD_PTO_TCP | 44419 | 0 | 100 | 0 | 100 | kVAr | ####.#
PTOPMMVirBReactivePowerPhaseB | REAL | IOD_PTO_TCP | 44421 | 0 | 100 | 0 | 100 | kVAr | ####.#
PTOPMMVirBReactivePowerPhaseC | REAL | IOD_PTO_TCP | 44423 | 0 | 100 | 0 | 100 | kVAr | ####.#
PTOPMMVirBTotalActivePower_kW | REAL | IOD_PTO_TCP | 44425 | 0 | 300 | 0 | 300 | kW | ####.#
PTOPMMVirBTotalAparentPower_kVA | REAL | IOD_PTO_TCP | 44427 | 0 | 300 | 0 | 300 | kVA | ####.#
PTOPMMVirBTotalPowerFactor | REAL | IOD_PTO_TCP | 44429 | 0 | 1 | 0 | 1 |  | ####.#
PTOPMMVirBTotalReactivePower_kVAR | REAL | IOD_PTO_TCP | 44431 | 0 | 100 | 0 | 100 | kVAr | ####.#
PTOPMMVirBVoltageBetweenPhaseAB_V | REAL | IOD_PTO_TCP | 44433 | 0 | 450 | 0 | 450 | V | ####.#
PTOPMMVirBVoltageBetweenPhaseAN_V | REAL | IOD_PTO_TCP | 44435 | 0 | 270 | 0 | 270 | V | ####.#
PTOPMMVirBVoltageBetweenPhaseBC_V | REAL | IOD_PTO_TCP | 44437 | 0 | 450 | 0 | 450 | V | ####.#
PTOPMMVirBVoltageBetweenPhaseBN_V | REAL | IOD_PTO_TCP | 44439 | 0 | 270 | 0 | 270 | V | ####.#
PTOPMMVirBVoltageBetweenPhaseCA_V | REAL | IOD_PTO_TCP | 44441 | 0 | 450 | 0 | 450 | V | ####.#
PTOPMMVirBVoltageBetweenPhaseCN_V | REAL | IOD_PTO_TCP | 44443 | 0 | 270 | 0 | 270 | V | ####.#
PTOPMMVoltageBetweenPhaseAB_V | REAL | IOD_PTO_TCP | 44445 | 0 | 450 | 0 | 450 | V | ####.#
PTOPMMVoltageBetweenPhaseAN_V | REAL | IOD_PTO_TCP | 44447 | 0 | 270 | 0 | 270 | V | ####.#
PTOPMMVoltageBetweenPhaseBC_V | REAL | IOD_PTO_TCP | 44449 | 0 | 450 | 0 | 450 | V | ####.#
PTOPMMVoltageBetweenPhaseBN_V | REAL | IOD_PTO_TCP | 44451 | 0 | 270 | 0 | 270 | V | ####.#
PTOPMMVoltageBetweenPhaseCA_V | REAL | IOD_PTO_TCP | 44453 | 0 | 450 | 0 | 450 | V | ####.#
PTOPMMVoltageBetweenPhaseCN_V | REAL | IOD_PTO_TCP | 44455 | 0 | 270 | 0 | 270 | V | ####.#
PTOPMMfaza01 | REAL | IOD_PTO_TCP | 44457
PTOPMMfaza02 | REAL | IOD_PTO_TCP | 44459
PTOPMMfaza03 | REAL | IOD_PTO_TCP | 44461
PTOPMMfaza04 | REAL | IOD_PTO_TCP | 44463
PTOPMMfaza05 | REAL | IOD_PTO_TCP | 44465
PTOPMMfaza06 | REAL | IOD_PTO_TCP | 44467
PTOPMMfaza07 | REAL | IOD_PTO_TCP | 44469
PTOPMMfaza08 | REAL | IOD_PTO_TCP | 44471
PTOPMMfaza09 | REAL | IOD_PTO_TCP | 44473
PTOPMMfaza10 | REAL | IOD_PTO_TCP | 44475
PTOPMMfaza11 | REAL | IOD_PTO_TCP | 44477
PTOPMMfaza12 | REAL | IOD_PTO_TCP | 44479
PTOPMMfaza13 | REAL | IOD_PTO_TCP | 44481
PTOPMMfaza14 | REAL | IOD_PTO_TCP | 44483
PTOPMMfaza15 | REAL | IOD_PTO_TCP | 44485
PTOPMMfaza16 | REAL | IOD_PTO_TCP | 44487
PTOPMMfaza17 | REAL | IOD_PTO_TCP | 44489
PTOPMMfaza18 | REAL | IOD_PTO_TCP | 44491
PTOPMMfaza19 | REAL | IOD_PTO_TCP | 44493
PTOPMMfaza20 | REAL | IOD_PTO_TCP | 44495
PTOPMMfaza21 | REAL | IOD_PTO_TCP | 44497
PTOPMMfaza22 | REAL | IOD_PTO_TCP | 44499
PTOPMMfaza23 | REAL | IOD_PTO_TCP | 44501
PTOPMMfaza24 | REAL | IOD_PTO_TCP | 44503
PTOPMMfaza25 | REAL | IOD_PTO_TCP | 44505
PTOPMMfaza26 | REAL | IOD_PTO_TCP | 44507
PTOPMMfaza27 | REAL | IOD_PTO_TCP | 44509
PTOPMMfaza28 | REAL | IOD_PTO_TCP | 44511
PTOPMMfaza29 | REAL | IOD_PTO_TCP | 44513
PTOPMMfaza30 | REAL | IOD_PTO_TCP | 44515
PTOPMMfaza31 | REAL | IOD_PTO_TCP | 44517
PTOPMMfaza32 | REAL | IOD_PTO_TCP | 44519
PTOPMMfaza33 | REAL | IOD_PTO_TCP | 44521
PTOPMMfaza34 | REAL | IOD_PTO_TCP | 44523
PTOPMMfaza35 | REAL | IOD_PTO_TCP | 44525
PTOPMMfaza36 | REAL | IOD_PTO_TCP | 44527
PTOPMMfaza37 | REAL | IOD_PTO_TCP | 44529
PTOPMMfaza38 | REAL | IOD_PTO_TCP | 44531
PTOPMMfaza39 | REAL | IOD_PTO_TCP | 44533
PTOPMMfaza40 | REAL | IOD_PTO_TCP | 44535
PTOPMMfaza41 | REAL | IOD_PTO_TCP | 44537
PTOPMMfaza42 | REAL | IOD_PTO_TCP | 44539
PTOPMMfaza6010 | REAL | IOD_PTO_TCP | 44541
PTOPMMfaza6011 | REAL | IOD_PTO_TCP | 44543
PTOPMMfaza6012 | REAL | IOD_PTO_TCP | 44545
PTOPMMfaza6013 | REAL | IOD_PTO_TCP | 44547
PTOPMMfaza6014 | REAL | IOD_PTO_TCP | 44549
PTOPMMfaza6015 | REAL | IOD_PTO_TCP | 44551
PTOPMMfaza6016 | REAL | IOD_PTO_TCP | 44553
PTOPMMfaza6017 | REAL | IOD_PTO_TCP | 44555
PTOPMMfaza6018 | REAL | IOD_PTO_TCP | 44557
PTOPMMfaza6019 | REAL | IOD_PTO_TCP | 44559
PTOPMMfaza601 | REAL | IOD_PTO_TCP | 44561
PTOPMMfaza6020 | REAL | IOD_PTO_TCP | 44563
PTOPMMfaza6021 | REAL | IOD_PTO_TCP | 44565
PTOPMMfaza6022 | REAL | IOD_PTO_TCP | 44567
PTOPMMfaza6023 | REAL | IOD_PTO_TCP | 44569
PTOPMMfaza6024 | REAL | IOD_PTO_TCP | 44571
PTOPMMfaza6025 | REAL | IOD_PTO_TCP | 44573
PTOPMMfaza6026 | REAL | IOD_PTO_TCP | 44575
PTOPMMfaza6027 | REAL | IOD_PTO_TCP | 44577
PTOPMMfaza6028 | REAL | IOD_PTO_TCP | 44579
PTOPMMfaza6029 | REAL | IOD_PTO_TCP | 44581
PTOPMMfaza602 | REAL | IOD_PTO_TCP | 44583
PTOPMMfaza6030 | REAL | IOD_PTO_TCP | 44585
PTOPMMfaza6031 | REAL | IOD_PTO_TCP | 44587
PTOPMMfaza6032 | REAL | IOD_PTO_TCP | 44589
PTOPMMfaza6033 | REAL | IOD_PTO_TCP | 44591
PTOPMMfaza6034 | REAL | IOD_PTO_TCP | 44593
PTOPMMfaza6035 | REAL | IOD_PTO_TCP | 44595
PTOPMMfaza6036 | REAL | IOD_PTO_TCP | 44597
PTOPMMfaza6037 | REAL | IOD_PTO_TCP | 44599
PTOPMMfaza6038 | REAL | IOD_PTO_TCP | 44601
PTOPMMfaza6039 | REAL | IOD_PTO_TCP | 44603
PTOPMMfaza603 | REAL | IOD_PTO_TCP | 44605
PTOPMMfaza6040 | REAL | IOD_PTO_TCP | 44607
PTOPMMfaza6041 | REAL | IOD_PTO_TCP | 44609
PTOPMMfaza6042 | REAL | IOD_PTO_TCP | 44611
PTOPMMfaza604 | REAL | IOD_PTO_TCP | 44613
PTOPMMfaza605 | REAL | IOD_PTO_TCP | 44615
PTOPMMfaza606 | REAL | IOD_PTO_TCP | 44617
PTOPMMfaza607 | REAL | IOD_PTO_TCP | 44619
PTOPMMfaza608 | REAL | IOD_PTO_TCP | 44621
PTOPMMfaza609 | REAL | IOD_PTO_TCP | 44623
PTOPMMfaza8010 | REAL | IOD_PTO_TCP | 44625
PTOPMMfaza8011 | REAL | IOD_PTO_TCP | 44627
PTOPMMfaza8012 | REAL | IOD_PTO_TCP | 44629
PTOPMMfaza8013 | REAL | IOD_PTO_TCP | 44631
PTOPMMfaza8014 | REAL | IOD_PTO_TCP | 44633
PTOPMMfaza8015 | REAL | IOD_PTO_TCP | 44635
PTOPMMfaza8016 | REAL | IOD_PTO_TCP | 44637
PTOPMMfaza8017 | REAL | IOD_PTO_TCP | 44639
PTOPMMfaza8018 | REAL | IOD_PTO_TCP | 44641
PTOPMMfaza8019 | REAL | IOD_PTO_TCP | 44643
PTOPMMfaza801 | REAL | IOD_PTO_TCP | 44645
PTOPMMfaza8020 | REAL | IOD_PTO_TCP | 44647
PTOPMMfaza8021 | REAL | IOD_PTO_TCP | 44649
PTOPMMfaza8022 | REAL | IOD_PTO_TCP | 44651
PTOPMMfaza8023 | REAL | IOD_PTO_TCP | 44653
PTOPMMfaza8024 | REAL | IOD_PTO_TCP | 44655
PTOPMMfaza8025 | REAL | IOD_PTO_TCP | 44657
PTOPMMfaza8026 | REAL | IOD_PTO_TCP | 44659
PTOPMMfaza8027 | REAL | IOD_PTO_TCP | 44661
PTOPMMfaza8028 | REAL | IOD_PTO_TCP | 44663
PTOPMMfaza8029 | REAL | IOD_PTO_TCP | 44665
PTOPMMfaza802 | REAL | IOD_PTO_TCP | 44667
PTOPMMfaza8030 | REAL | IOD_PTO_TCP | 44669
PTOPMMfaza8031 | REAL | IOD_PTO_TCP | 44671
PTOPMMfaza8032 | REAL | IOD_PTO_TCP | 44673
PTOPMMfaza8033 | REAL | IOD_PTO_TCP | 44675
PTOPMMfaza8034 | REAL | IOD_PTO_TCP | 44677
PTOPMMfaza8035 | REAL | IOD_PTO_TCP | 44679
PTOPMMfaza8036 | REAL | IOD_PTO_TCP | 44681
PTOPMMfaza8037 | REAL | IOD_PTO_TCP | 44683
PTOPMMfaza8038 | REAL | IOD_PTO_TCP | 44685
PTOPMMfaza8039 | REAL | IOD_PTO_TCP | 44687
PTOPMMfaza803 | REAL | IOD_PTO_TCP | 44689
PTOPMMfaza8040 | REAL | IOD_PTO_TCP | 44691
PTOPMMfaza8041 | REAL | IOD_PTO_TCP | 44693
PTOPMMfaza8042 | REAL | IOD_PTO_TCP | 44695
PTOPMMfaza804 | REAL | IOD_PTO_TCP | 44697
PTOPMMfaza805 | REAL | IOD_PTO_TCP | 44699
PTOPMMfaza806 | REAL | IOD_PTO_TCP | 44701
PTOPMMfaza807 | REAL | IOD_PTO_TCP | 44703
PTOPMMfaza808 | REAL | IOD_PTO_TCP | 44705
PTOPMMfaza809 | REAL | IOD_PTO_TCP | 44707
PTOPMMOverCurrentBetw1 | DIGITAL | IOD_PTO_TCP | 00562
PTOPMMOverCurrentBetw2 | DIGITAL | IOD_PTO_TCP | 00563
PTOPMMOverCurrentBetw3 | DIGITAL | IOD_PTO_TCP | 00564
PTOPMMOverCurrentOver1 | DIGITAL | IOD_PTO_TCP | 00565
PTOPMMOverCurrentOver2 | DIGITAL | IOD_PTO_TCP | 00566
PTOPMMOverCurrentOver3 | DIGITAL | IOD_PTO_TCP | 00567
PTOQstanje10 | INT | IOD_PTO_TCP | 40199
PTOQstanje11 | INT | IOD_PTO_TCP | 40200
PTOQstanje12 | INT | IOD_PTO_TCP | 40201
PTOQstanje13 | INT | IOD_PTO_TCP | 40202
PTOQstanje14 | INT | IOD_PTO_TCP | 40203
PTOQstanje15 | INT | IOD_PTO_TCP | 40204
PTOQstanje16 | INT | IOD_PTO_TCP | 40205
PTOQstanje17 | INT | IOD_PTO_TCP | 40206
PTOQstanje18 | INT | IOD_PTO_TCP | 40207
PTOQstanje19 | INT | IOD_PTO_TCP | 40208
PTOQstanje1 | INT | IOD_PTO_TCP | 40209
PTOQstanje20 | INT | IOD_PTO_TCP | 40210
PTOQstanje21 | INT | IOD_PTO_TCP | 40211
PTOQstanje22 | INT | IOD_PTO_TCP | 40212
PTOQstanje23 | INT | IOD_PTO_TCP | 40213
PTOQstanje24 | INT | IOD_PTO_TCP | 40214
PTOQstanje25 | INT | IOD_PTO_TCP | 40215
PTOQstanje26 | INT | IOD_PTO_TCP | 40216
PTOQstanje27 | INT | IOD_PTO_TCP | 40217
PTOQstanje28 | INT | IOD_PTO_TCP | 40218
PTOQstanje29 | INT | IOD_PTO_TCP | 40219
PTOQstanje2 | INT | IOD_PTO_TCP | 40220
PTOQstanje30 | INT | IOD_PTO_TCP | 40221
PTOQstanje31 | INT | IOD_PTO_TCP | 40222
PTOQstanje32 | INT | IOD_PTO_TCP | 40223
PTOQstanje33 | INT | IOD_PTO_TCP | 40224
PTOQstanje34 | INT | IOD_PTO_TCP | 40225
PTOQstanje35 | INT | IOD_PTO_TCP | 40226
PTOQstanje3 | INT | IOD_PTO_TCP | 40227
PTOQstanje4 | INT | IOD_PTO_TCP | 40228
PTOQstanje5 | INT | IOD_PTO_TCP | 40229
PTOQstanje6 | INT | IOD_PTO_TCP | 40230
PTOQstanje7 | INT | IOD_PTO_TCP | 40231
PTOQstanje8 | INT | IOD_PTO_TCP | 40232
PTOQstanje9 | INT | IOD_PTO_TCP | 40233
PTOSenzorTemp1 | REAL | IOD_PTO_TCP | 44709 | 0 | 60 | 0 | 60 | °C | ####.#
PTOSenzorTemp2 | REAL | IOD_PTO_TCP | 44711 | 0 | 60 | 0 | 60 | °C | ####.#
PTOSenzorTemp3 | REAL | IOD_PTO_TCP | 44713 | 0 | 60 | 0 | 60 | °C | ####.#
PTOSenzorTemp4 | REAL | IOD_PTO_TCP | 44715 | 0 | 60 | 0 | 60 | °C | ####.#
PTOSenzorTemp5 | REAL | IOD_PTO_TCP | 44717 | 0 | 60 | 0 | 60 | °C | ####.#
PTOSenzorTemp6 | REAL | IOD_PTO_TCP | 44719 | 0 | 60 | 0 | 60 | °C | ####.#
PTOSenzorVlaga1 | REAL | IOD_PTO_TCP | 44721 | 0 | 100 | 0 | 100 | % | ####.#
PTOSenzorVlaga2 | REAL | IOD_PTO_TCP | 44723 | 0 | 100 | 0 | 100 | % | ####.#
PTOSenzorVlaga3 | REAL | IOD_PTO_TCP | 44725 | 0 | 100 | 0 | 100 | % | ####.#
PTOSenzorVlaga4 | REAL | IOD_PTO_TCP | 44727 | 0 | 100 | 0 | 100 | % | ####.#
PTOSenzorVlaga5 | REAL | IOD_PTO_TCP | 44729 | 0 | 100 | 0 | 100 | % | ####.#
PTOSenzorVlaga6 | REAL | IOD_PTO_TCP | 44731 | 0 | 100 | 0 | 100 | % | ####.#
PTOSetDateTime | DIGITAL | IOD_PTO_TCP | 00568
PTOSetDateTimeDemand | DIGITAL | IOD_PTO_TCP | 00569
PTOSetDateTimeError | DIGITAL | IOD_PTO_TCP | 00570
PTOSetDateTimeFinished | DIGITAL | IOD_PTO_TCP | 00571
PTOSetRemoteOnOff1 | DIGITAL | IOD_PTO_TCP | 00572
PTOSetRemoteOnOff2 | DIGITAL | IOD_PTO_TCP | 00573
PTOSlabaBaterijaPLC_A1 | DIGITAL | IOD_PTO_TCP | 00574
PTOTempAlarmPoint0 | REAL | IOD_PTO_TCP | 44733
PTOTempAlarmPoint1 | REAL | IOD_PTO_TCP | 44735
PTOTempAlarmPoint2 | REAL | IOD_PTO_TCP | 44737
PTOTempAlarmPoint3 | REAL | IOD_PTO_TCP | 44739
PTOTempMaxPoint0 | REAL | IOD_PTO_TCP | 44741
PTOTempMaxPoint1 | REAL | IOD_PTO_TCP | 44743
PTOTempMaxPoint2 | REAL | IOD_PTO_TCP | 44745
PTOTempMaxPoint3 | REAL | IOD_PTO_TCP | 44747
PTOTempPovp0 | REAL | IOD_PTO_TCP | 44749
PTOTempPovp1 | REAL | IOD_PTO_TCP | 44751
PTOTempPovp2 | REAL | IOD_PTO_TCP | 44753
PTOTempPovp3 | REAL | IOD_PTO_TCP | 44755
PTOTempSetPoint0 | REAL | IOD_PTO_TCP | 44757
PTOTempSetPoint1 | REAL | IOD_PTO_TCP | 44759
PTOTempSetPoint2 | REAL | IOD_PTO_TCP | 44761
PTOTempSetPoint3 | REAL | IOD_PTO_TCP | 44763
PTOTempTSprevisoka1 | DIGITAL | IOD_PTO_TCP | 00575
PTOTempTSprevisoka2 | DIGITAL | IOD_PTO_TCP | 00576
PTOTempTSprevisoka3 | DIGITAL | IOD_PTO_TCP | 00577
PTOTempTSprevisokaSum | DIGITAL | IOD_PTO_TCP | 00578
PTOUPS1Errors10 | DIGITAL | IOD_PTO_TCP | 00579
PTOUPS1Errors11 | DIGITAL | IOD_PTO_TCP | 00580
PTOUPS1Errors12 | DIGITAL | IOD_PTO_TCP | 00581
PTOUPS1Errors13 | DIGITAL | IOD_PTO_TCP | 00582
PTOUPS1Errors14 | DIGITAL | IOD_PTO_TCP | 00583
PTOUPS1Errors15 | DIGITAL | IOD_PTO_TCP | 00584
PTOUPS1Errors16 | DIGITAL | IOD_PTO_TCP | 00585
PTOUPS1Errors17 | DIGITAL | IOD_PTO_TCP | 00586
PTOUPS1Errors18 | DIGITAL | IOD_PTO_TCP | 00587
PTOUPS1Errors19 | DIGITAL | IOD_PTO_TCP | 00588
PTOUPS1Errors1 | DIGITAL | IOD_PTO_TCP | 00589
PTOUPS1Errors20 | DIGITAL | IOD_PTO_TCP | 00590
PTOUPS1Errors21 | DIGITAL | IOD_PTO_TCP | 00591
PTOUPS1Errors22 | DIGITAL | IOD_PTO_TCP | 00592
PTOUPS1Errors23 | DIGITAL | IOD_PTO_TCP | 00593
PTOUPS1Errors24 | DIGITAL | IOD_PTO_TCP | 00594
PTOUPS1Errors25 | DIGITAL | IOD_PTO_TCP | 00595
PTOUPS1Errors2 | DIGITAL | IOD_PTO_TCP | 00596
PTOUPS1Errors3 | DIGITAL | IOD_PTO_TCP | 00597
PTOUPS1Errors4 | DIGITAL | IOD_PTO_TCP | 00598
PTOUPS1Errors5 | DIGITAL | IOD_PTO_TCP | 00599
PTOUPS1Errors6 | DIGITAL | IOD_PTO_TCP | 00600
PTOUPS1Errors7 | DIGITAL | IOD_PTO_TCP | 00601
PTOUPS1Errors8 | DIGITAL | IOD_PTO_TCP | 00602
PTOUPS1Errors9 | DIGITAL | IOD_PTO_TCP | 00603
PTOUPS2Errors10 | DIGITAL | IOD_PTO_TCP | 00604
PTOUPS2Errors11 | DIGITAL | IOD_PTO_TCP | 00605
PTOUPS2Errors12 | DIGITAL | IOD_PTO_TCP | 00606
PTOUPS2Errors13 | DIGITAL | IOD_PTO_TCP | 00607
PTOUPS2Errors14 | DIGITAL | IOD_PTO_TCP | 00608
PTOUPS2Errors15 | DIGITAL | IOD_PTO_TCP | 00609
PTOUPS2Errors16 | DIGITAL | IOD_PTO_TCP | 00610
PTOUPS2Errors17 | DIGITAL | IOD_PTO_TCP | 00611
PTOUPS2Errors18 | DIGITAL | IOD_PTO_TCP | 00612
PTOUPS2Errors19 | DIGITAL | IOD_PTO_TCP | 00613
PTOUPS2Errors1 | DIGITAL | IOD_PTO_TCP | 00614
PTOUPS2Errors20 | DIGITAL | IOD_PTO_TCP | 00615
PTOUPS2Errors21 | DIGITAL | IOD_PTO_TCP | 00616
PTOUPS2Errors22 | DIGITAL | IOD_PTO_TCP | 00617
PTOUPS2Errors23 | DIGITAL | IOD_PTO_TCP | 00618
PTOUPS2Errors24 | DIGITAL | IOD_PTO_TCP | 00619
PTOUPS2Errors25 | DIGITAL | IOD_PTO_TCP | 00620
PTOUPS2Errors2 | DIGITAL | IOD_PTO_TCP | 00621
PTOUPS2Errors3 | DIGITAL | IOD_PTO_TCP | 00622
PTOUPS2Errors4 | DIGITAL | IOD_PTO_TCP | 00623
PTOUPS2Errors5 | DIGITAL | IOD_PTO_TCP | 00624
PTOUPS2Errors6 | DIGITAL | IOD_PTO_TCP | 00625
PTOUPS2Errors7 | DIGITAL | IOD_PTO_TCP | 00626
PTOUPS2Errors8 | DIGITAL | IOD_PTO_TCP | 00627
PTOUPS2Errors9 | DIGITAL | IOD_PTO_TCP | 00628
PTOUPS1AlarmAwaitingPower | DIGITAL | IOD_PTO_TCP | 00629
PTOUPS1AlarmBypassBad | DIGITAL | IOD_PTO_TCP | 00630
PTOUPS1AlarmChargerFailed | DIGITAL | IOD_PTO_TCP | 00631
PTOUPS1AlarmCommunicationsLost | DIGITAL | IOD_PTO_TCP | 00632
PTOUPS1AlarmDepletedBattery | DIGITAL | IOD_PTO_TCP | 00633
PTOUPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_PTO_TCP | 00634
PTOUPS1AlarmInverterError | DIGITAL | IOD_PTO_TCP | 00635
PTOUPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_PTO_TCP | 00636
PTOUPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_PTO_TCP | 00637
PTOUPS1AlarmLowBattery | DIGITAL | IOD_PTO_TCP | 00638
PTOUPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_PTO_TCP | 00639
PTOUPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_PTO_TCP | 00640
PTOUPS1AlarmOnBattery | DIGITAL | IOD_PTO_TCP | 00641
PTOUPS1AlarmOnBypass | DIGITAL | IOD_PTO_TCP | 00642
PTOUPS1AlarmShutdownImminent | DIGITAL | IOD_PTO_TCP | 00643
PTOUPS1AlarmShutdownPending | DIGITAL | IOD_PTO_TCP | 00644
PTOUPS1AlarmSlabaBaterija | DIGITAL | IOD_PTO_TCP | 00645
PTOUPS1AlarmSplosnaNapaka | DIGITAL | IOD_PTO_TCP | 00646
PTOUPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_PTO_TCP | 00647
PTOUPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_PTO_TCP | 00648
PTOUPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_PTO_TCP | 00649
PTOUPS1AlarmTestInProgres | DIGITAL | IOD_PTO_TCP | 00650
PTOUPS1AlarmUPSIzhodOff | DIGITAL | IOD_PTO_TCP | 00651
PTOUPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_PTO_TCP | 00652
PTOUPS1AlarmUPSSystemOff | DIGITAL | IOD_PTO_TCP | 00653
PTOUPS1EstimatedChargeRemaining | REAL | IOD_PTO_TCP | 44765 | 0 | 100 | 0 | 100 | % | ####
PTOUPS1EstimatedMinutesRemaining | REAL | IOD_PTO_TCP | 44767 | 0 | 1000 | 0 | 100 | min | ####
PTOUPS1InverterStatus | INT | IOD_PTO_TCP | 40234
PTOUPS1IzhodMocL1 | REAL | IOD_PTO_TCP | 44769 | 0 | 100 | 0 | 100 | % | ####
PTOUPS1IzhodMocL2 | REAL | IOD_PTO_TCP | 44771 | 0 | 100 | 0 | 100 | % | ####
PTOUPS1IzhodMocL3 | REAL | IOD_PTO_TCP | 44773 | 0 | 100 | 0 | 100 | % | ####
PTOUPS1Napaka | DIGITAL | IOD_PTO_TCP | 00654
PTOUPS1NapetostBaterije | REAL | IOD_PTO_TCP | 44775 | 0 | 500 | 0 | 500 | V | ####
PTOUPS1OutputStatus | INT | IOD_PTO_TCP | 40235
PTOUPS1StatusBaterije | INT | IOD_PTO_TCP | 40236
PTOUPS1StatusEcomodeAktiven | DIGITAL | IOD_PTO_TCP | 00655
PTOUPS1StatusInverterIsOn | DIGITAL | IOD_PTO_TCP | 00656
PTOUPS1StatusStopOperation | DIGITAL | IOD_PTO_TCP | 00657
PTOUPS1SteviloIzpadovVhodneLinije | INT | IOD_PTO_TCP | 40237 | 0 | 1000 | 0 | 1000 |  | ####
PTOUPS1TemperaturaBaterije | REAL | IOD_PTO_TCP | 44777 | 0 | 200 | 0 | 200 | °C | ####
PTOUPS1UnitStatus | INT | IOD_PTO_TCP | 40238
PTOUPS1VhodFrekvencaL1 | REAL | IOD_PTO_TCP | 44779 | 0 | 100 | 0 | 100 | Hz | ####
PTOUPS1VhodFrekvencaL2 | REAL | IOD_PTO_TCP | 44781 | 0 | 100 | 0 | 100 | Hz | ####
PTOUPS1VhodFrekvencaL3 | REAL | IOD_PTO_TCP | 44783 | 0 | 100 | 0 | 100 | Hz | ####
PTOUPS1VhodNapetostL1 | REAL | IOD_PTO_TCP | 44785 | 0 | 500 | 0 | 500 | V | ####
PTOUPS1VhodNapetostL2 | REAL | IOD_PTO_TCP | 44787 | 0 | 500 | 0 | 500 | V | ####
PTOUPS1VhodNapetostL3 | REAL | IOD_PTO_TCP | 44789 | 0 | 500 | 0 | 500 | V | ####
PTOUPS2AlarmAwaitingPower | DIGITAL | IOD_PTO_TCP | 00658
PTOUPS2AlarmBypassBad | DIGITAL | IOD_PTO_TCP | 00659
PTOUPS2AlarmChargerFailed | DIGITAL | IOD_PTO_TCP | 00660
PTOUPS2AlarmCommunicationsLost | DIGITAL | IOD_PTO_TCP | 00661
PTOUPS2AlarmDepletedBattery | DIGITAL | IOD_PTO_TCP | 00662
PTOUPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_PTO_TCP | 00663
PTOUPS2AlarmInverterError | DIGITAL | IOD_PTO_TCP | 00664
PTOUPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_PTO_TCP | 00665
PTOUPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_PTO_TCP | 00666
PTOUPS2AlarmLowBattery | DIGITAL | IOD_PTO_TCP | 00667
PTOUPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_PTO_TCP | 00668
PTOUPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_PTO_TCP | 00669
PTOUPS2AlarmOnBattery | DIGITAL | IOD_PTO_TCP | 00670
PTOUPS2AlarmOnBypass | DIGITAL | IOD_PTO_TCP | 00671
PTOUPS2AlarmShutdownImminent | DIGITAL | IOD_PTO_TCP | 00672
PTOUPS2AlarmShutdownPending | DIGITAL | IOD_PTO_TCP | 00673
PTOUPS2AlarmSlabaBaterija | DIGITAL | IOD_PTO_TCP | 00674
PTOUPS2AlarmSplosnaNapaka | DIGITAL | IOD_PTO_TCP | 00675
PTOUPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_PTO_TCP | 00676
PTOUPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_PTO_TCP | 00677
PTOUPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_PTO_TCP | 00678
PTOUPS2AlarmTestInProgres | DIGITAL | IOD_PTO_TCP | 00679
PTOUPS2AlarmUPSIzhodOff | DIGITAL | IOD_PTO_TCP | 00680
PTOUPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_PTO_TCP | 00681
PTOUPS2AlarmUPSSystemOff | DIGITAL | IOD_PTO_TCP | 00682
PTOUPS2EstimatedChargeRemaining | REAL | IOD_PTO_TCP | 44791 | 0 | 100 | 0 | 100 | % | ####
PTOUPS2EstimatedMinutesRemaining | REAL | IOD_PTO_TCP | 44793 | 0 | 1000 | 0 | 100 | min | ####
PTOUPS2InverterStatus | INT | IOD_PTO_TCP | 40239
PTOUPS2IzhodMocL1 | REAL | IOD_PTO_TCP | 44795 | 0 | 100 | 0 | 100 | % | ####
PTOUPS2IzhodMocL2 | REAL | IOD_PTO_TCP | 44797 | 0 | 100 | 0 | 100 | % | ####
PTOUPS2IzhodMocL3 | REAL | IOD_PTO_TCP | 44799 | 0 | 100 | 0 | 100 | % | ####
PTOUPS2Napaka | DIGITAL | IOD_PTO_TCP | 00683
PTOUPS2NapetostBaterije | REAL | IOD_PTO_TCP | 44801 | 0 | 500 | 0 | 500 | V | ####
PTOUPS2OutputStatus | INT | IOD_PTO_TCP | 40240
PTOUPS2StatusBaterije | INT | IOD_PTO_TCP | 40241
PTOUPS2StatusEcomodeAktiven | DIGITAL | IOD_PTO_TCP | 00684
PTOUPS2StatusInverterIsOn | DIGITAL | IOD_PTO_TCP | 00685
PTOUPS2StatusStopOperation | DIGITAL | IOD_PTO_TCP | 00686
PTOUPS2SteviloIzpadovVhodneLinije | INT | IOD_PTO_TCP | 40242 | 0 | 1000 | 0 | 1000 |  | ####
PTOUPS2TemperaturaBaterije | REAL | IOD_PTO_TCP | 44803 | 0 | 200 | 0 | 200 | °C | ####
PTOUPS2UnitStatus | INT | IOD_PTO_TCP | 40243
PTOUPS2VhodFrekvencaL1 | REAL | IOD_PTO_TCP | 44805 | 0 | 100 | 0 | 100 | Hz | ####
PTOUPS2VhodFrekvencaL2 | REAL | IOD_PTO_TCP | 44807 | 0 | 100 | 0 | 100 | Hz | ####
PTOUPS2VhodFrekvencaL3 | REAL | IOD_PTO_TCP | 44809 | 0 | 100 | 0 | 100 | Hz | ####
PTOUPS2VhodNapetostL1 | REAL | IOD_PTO_TCP | 44811 | 0 | 500 | 0 | 500 | V | ####
PTOUPS2VhodNapetostL2 | REAL | IOD_PTO_TCP | 44813 | 0 | 500 | 0 | 500 | V | ####
PTOUPS2VhodNapetostL3 | REAL | IOD_PTO_TCP | 44815 | 0 | 500 | 0 | 500 | V | ####
PTOUserCurrentLevel | INT | IOD_PTO_TCP | 40244
PTOUserCurrentName | STRING | IOD_PTO_TCP | 45061[15]
PTOUserLoggedIn | DIGITAL | IOD_PTO_TCP | 00687
PTOVlagaPovp1 | REAL | IOD_PTO_TCP | 44817
PTOVlagaPovp2 | REAL | IOD_PTO_TCP | 44819
PTOVlagaPovp3 | REAL | IOD_PTO_TCP | 44821
APTO_omogoci_sms | DIGITAL | IOD_PTO_disk2 | D1[600]
BPTO_omogoci_sms | DIGITAL | IOD_PTO_disk2 | D601[600]
CPTO_omogoci_sms | DIGITAL | IOD_PTO_disk2 | D1202[600]
DPTO_omogoci_sms | DIGITAL | IOD_PTO_disk2 | D1804[600]
EPTO_omogoci_sms | DIGITAL | IOD_PTO_disk2 | D2406[600]
FPTO_omogoci_sms | DIGITAL | IOD_PTO_disk2 | D3008[600]
PTO_PMM_1_Faza1_Tok01_nad80 | DIGITAL | IOD_PTO_disk | D1
PTO_PMM_1_Faza1_Tok02_nad80 | DIGITAL | IOD_PTO_disk | D2
PTO_PMM_1_Faza1_Tok03_nad80 | DIGITAL | IOD_PTO_disk | D3
PTO_PMM_1_Faza1_Tok04_nad80 | DIGITAL | IOD_PTO_disk | D4
PTO_PMM_1_Faza1_Tok05_nad80 | DIGITAL | IOD_PTO_disk | D5
PTO_PMM_1_Faza1_Tok06_nad80 | DIGITAL | IOD_PTO_disk | D6
PTO_PMM_1_Faza1_Tok07_nad80 | DIGITAL | IOD_PTO_disk | D7
PTO_PMM_1_Faza1_Tok08_nad80 | DIGITAL | IOD_PTO_disk | D8
PTO_PMM_1_Faza1_Tok09_nad80 | DIGITAL | IOD_PTO_disk | D9
PTO_PMM_1_Faza1_Tok10_nad80 | DIGITAL | IOD_PTO_disk | D10
PTO_PMM_1_Faza1_Tok11_nad80 | DIGITAL | IOD_PTO_disk | D11
PTO_PMM_1_Faza1_Tok12_nad80 | DIGITAL | IOD_PTO_disk | D12
PTO_PMM_1_Faza1_Tok13_nad80 | DIGITAL | IOD_PTO_disk | D13
PTO_PMM_1_Faza1_Tok14_nad80 | DIGITAL | IOD_PTO_disk | D14
PTO_PMM_1_Faza1_Tok15_nad80 | DIGITAL | IOD_PTO_disk | D15
PTO_PMM_1_Faza1_Tok16_nad80 | DIGITAL | IOD_PTO_disk | D16
PTO_PMM_1_Faza1_Tok17_nad80 | DIGITAL | IOD_PTO_disk | D17
PTO_PMM_1_Faza1_Tok18_nad80 | DIGITAL | IOD_PTO_disk | D18
PTO_PMM_1_Faza1_Tok19_nad80 | DIGITAL | IOD_PTO_disk | D19
PTO_PMM_1_Faza1_Tok20_nad80 | DIGITAL | IOD_PTO_disk | D20
PTO_PMM_1_Faza1_Tok21_nad80 | DIGITAL | IOD_PTO_disk | D21
PTO_PMM_1_Faza1_Tok22_nad80 | DIGITAL | IOD_PTO_disk | D22
PTO_PMM_1_Faza1_Tok23_nad80 | DIGITAL | IOD_PTO_disk | D23
PTO_PMM_1_Faza1_Tok24_nad80 | DIGITAL | IOD_PTO_disk | D24
PTO_PMM_1_Faza1_Tok25_nad80 | DIGITAL | IOD_PTO_disk | D25
PTO_PMM_1_Faza1_Tok26_nad80 | DIGITAL | IOD_PTO_disk | D26
PTO_PMM_1_Faza1_Tok27_nad80 | DIGITAL | IOD_PTO_disk | D27
PTO_PMM_1_Faza1_Tok28_nad80 | DIGITAL | IOD_PTO_disk | D28
PTO_PMM_1_Faza1_Tok29_nad80 | DIGITAL | IOD_PTO_disk | D29
PTO_PMM_1_Faza1_Tok30_nad80 | DIGITAL | IOD_PTO_disk | D30
PTO_PMM_1_Faza1_Tok31_nad80 | DIGITAL | IOD_PTO_disk | D31
PTO_PMM_1_Faza1_Tok32_nad80 | DIGITAL | IOD_PTO_disk | D32
PTO_PMM_1_Faza1_Tok33_nad80 | DIGITAL | IOD_PTO_disk | D33
PTO_PMM_1_Faza1_Tok34_nad80 | DIGITAL | IOD_PTO_disk | D34
PTO_PMM_1_Faza1_Tok35_nad80 | DIGITAL | IOD_PTO_disk | D35
PTO_PMM_1_Faza1_Tok36_nad80 | DIGITAL | IOD_PTO_disk | D36
PTO_PMM_1_Faza1_Tok37_nad80 | DIGITAL | IOD_PTO_disk | D37
PTO_PMM_1_Faza1_Tok38_nad80 | DIGITAL | IOD_PTO_disk | D38
PTO_PMM_1_Faza1_Tok39_nad80 | DIGITAL | IOD_PTO_disk | D39
PTO_PMM_1_Faza1_Tok40_nad80 | DIGITAL | IOD_PTO_disk | D40
PTO_PMM_1_Faza1_Tok41_nad80 | DIGITAL | IOD_PTO_disk | D41
PTO_PMM_1_Faza1_Tok42_nad80 | DIGITAL | IOD_PTO_disk | D42
PTO_PMM_1_Faza2_Tok01_nad80 | DIGITAL | IOD_PTO_disk | D43
PTO_PMM_1_Faza2_Tok02_nad80 | DIGITAL | IOD_PTO_disk | D44
PTO_PMM_1_Faza2_Tok03_nad80 | DIGITAL | IOD_PTO_disk | D45
PTO_PMM_1_Faza2_Tok04_nad80 | DIGITAL | IOD_PTO_disk | D46
PTO_PMM_1_Faza2_Tok05_nad80 | DIGITAL | IOD_PTO_disk | D47
PTO_PMM_1_Faza2_Tok06_nad80 | DIGITAL | IOD_PTO_disk | D48
PTO_PMM_1_Faza2_Tok07_nad80 | DIGITAL | IOD_PTO_disk | D49
PTO_PMM_1_Faza2_Tok08_nad80 | DIGITAL | IOD_PTO_disk | D50
PTO_PMM_1_Faza2_Tok09_nad80 | DIGITAL | IOD_PTO_disk | D51
PTO_PMM_1_Faza2_Tok10_nad80 | DIGITAL | IOD_PTO_disk | D52
PTO_PMM_1_Faza2_Tok11_nad80 | DIGITAL | IOD_PTO_disk | D53
PTO_PMM_1_Faza2_Tok12_nad80 | DIGITAL | IOD_PTO_disk | D54
PTO_PMM_1_Faza2_Tok13_nad80 | DIGITAL | IOD_PTO_disk | D55
PTO_PMM_1_Faza2_Tok14_nad80 | DIGITAL | IOD_PTO_disk | D56
PTO_PMM_1_Faza2_Tok15_nad80 | DIGITAL | IOD_PTO_disk | D57
PTO_PMM_1_Faza2_Tok16_nad80 | DIGITAL | IOD_PTO_disk | D58
PTO_PMM_1_Faza2_Tok17_nad80 | DIGITAL | IOD_PTO_disk | D59
PTO_PMM_1_Faza2_Tok18_nad80 | DIGITAL | IOD_PTO_disk | D60
PTO_PMM_1_Faza2_Tok19_nad80 | DIGITAL | IOD_PTO_disk | D61
PTO_PMM_1_Faza2_Tok20_nad80 | DIGITAL | IOD_PTO_disk | D62
PTO_PMM_1_Faza2_Tok21_nad80 | DIGITAL | IOD_PTO_disk | D63
PTO_PMM_1_Faza2_Tok22_nad80 | DIGITAL | IOD_PTO_disk | D64
PTO_PMM_1_Faza2_Tok23_nad80 | DIGITAL | IOD_PTO_disk | D65
PTO_PMM_1_Faza2_Tok24_nad80 | DIGITAL | IOD_PTO_disk | D66
PTO_PMM_1_Faza2_Tok25_nad80 | DIGITAL | IOD_PTO_disk | D67
PTO_PMM_1_Faza2_Tok26_nad80 | DIGITAL | IOD_PTO_disk | D68
PTO_PMM_1_Faza2_Tok27_nad80 | DIGITAL | IOD_PTO_disk | D69
PTO_PMM_1_Faza2_Tok28_nad80 | DIGITAL | IOD_PTO_disk | D70
PTO_PMM_1_Faza2_Tok29_nad80 | DIGITAL | IOD_PTO_disk | D71
PTO_PMM_1_Faza2_Tok30_nad80 | DIGITAL | IOD_PTO_disk | D72
PTO_PMM_1_Faza2_Tok31_nad80 | DIGITAL | IOD_PTO_disk | D73
PTO_PMM_1_Faza2_Tok32_nad80 | DIGITAL | IOD_PTO_disk | D74
PTO_PMM_1_Faza2_Tok33_nad80 | DIGITAL | IOD_PTO_disk | D75
PTO_PMM_1_Faza2_Tok34_nad80 | DIGITAL | IOD_PTO_disk | D76
PTO_PMM_1_Faza2_Tok35_nad80 | DIGITAL | IOD_PTO_disk | D77
PTO_PMM_1_Faza2_Tok36_nad80 | DIGITAL | IOD_PTO_disk | D78
PTO_PMM_1_Faza2_Tok37_nad80 | DIGITAL | IOD_PTO_disk | D79
PTO_PMM_1_Faza2_Tok38_nad80 | DIGITAL | IOD_PTO_disk | D80
PTO_PMM_1_Faza2_Tok39_nad80 | DIGITAL | IOD_PTO_disk | D81
PTO_PMM_1_Faza2_Tok40_nad80 | DIGITAL | IOD_PTO_disk | D82
PTO_PMM_1_Faza2_Tok41_nad80 | DIGITAL | IOD_PTO_disk | D83
PTO_PMM_1_Faza2_Tok42_nad80 | DIGITAL | IOD_PTO_disk | D84
PTO_PMM_1_Faza3_Tok01_nad80 | DIGITAL | IOD_PTO_disk | D85
PTO_PMM_1_Faza3_Tok02_nad80 | DIGITAL | IOD_PTO_disk | D86
PTO_PMM_1_Faza3_Tok03_nad80 | DIGITAL | IOD_PTO_disk | D87
PTO_PMM_1_Faza3_Tok04_nad80 | DIGITAL | IOD_PTO_disk | D88
PTO_PMM_1_Faza3_Tok05_nad80 | DIGITAL | IOD_PTO_disk | D89
PTO_PMM_1_Faza3_Tok06_nad80 | DIGITAL | IOD_PTO_disk | D90
PTO_PMM_1_Faza3_Tok07_nad80 | DIGITAL | IOD_PTO_disk | D91
PTO_PMM_1_Faza3_Tok08_nad80 | DIGITAL | IOD_PTO_disk | D92
PTO_PMM_1_Faza3_Tok09_nad80 | DIGITAL | IOD_PTO_disk | D93
PTO_PMM_1_Faza3_Tok10_nad80 | DIGITAL | IOD_PTO_disk | D94
PTO_PMM_1_Faza3_Tok11_nad80 | DIGITAL | IOD_PTO_disk | D95
PTO_PMM_1_Faza3_Tok12_nad80 | DIGITAL | IOD_PTO_disk | D96
PTO_PMM_1_Faza3_Tok13_nad80 | DIGITAL | IOD_PTO_disk | D97
PTO_PMM_1_Faza3_Tok14_nad80 | DIGITAL | IOD_PTO_disk | D98
PTO_PMM_1_Faza3_Tok15_nad80 | DIGITAL | IOD_PTO_disk | D99
PTO_PMM_1_Faza3_Tok16_nad80 | DIGITAL | IOD_PTO_disk | D100
PTO_PMM_1_Faza3_Tok17_nad80 | DIGITAL | IOD_PTO_disk | D101
PTO_PMM_1_Faza3_Tok18_nad80 | DIGITAL | IOD_PTO_disk | D102
PTO_PMM_1_Faza3_Tok19_nad80 | DIGITAL | IOD_PTO_disk | D103
PTO_PMM_1_Faza3_Tok20_nad80 | DIGITAL | IOD_PTO_disk | D104
PTO_PMM_1_Faza3_Tok21_nad80 | DIGITAL | IOD_PTO_disk | D105
PTO_PMM_1_Faza3_Tok22_nad80 | DIGITAL | IOD_PTO_disk | D106
PTO_PMM_1_Faza3_Tok23_nad80 | DIGITAL | IOD_PTO_disk | D107
PTO_PMM_1_Faza3_Tok24_nad80 | DIGITAL | IOD_PTO_disk | D108
PTO_PMM_1_Faza3_Tok25_nad80 | DIGITAL | IOD_PTO_disk | D109
PTO_PMM_1_Faza3_Tok26_nad80 | DIGITAL | IOD_PTO_disk | D110
PTO_PMM_1_Faza3_Tok27_nad80 | DIGITAL | IOD_PTO_disk | D111
PTO_PMM_1_Faza3_Tok28_nad80 | DIGITAL | IOD_PTO_disk | D112
PTO_PMM_1_Faza3_Tok29_nad80 | DIGITAL | IOD_PTO_disk | D113
PTO_PMM_1_Faza3_Tok30_nad80 | DIGITAL | IOD_PTO_disk | D114
PTO_PMM_1_Faza3_Tok31_nad80 | DIGITAL | IOD_PTO_disk | D115
PTO_PMM_1_Faza3_Tok32_nad80 | DIGITAL | IOD_PTO_disk | D116
PTO_PMM_1_Faza3_Tok33_nad80 | DIGITAL | IOD_PTO_disk | D117
PTO_PMM_1_Faza3_Tok34_nad80 | DIGITAL | IOD_PTO_disk | D118
PTO_PMM_1_Faza3_Tok35_nad80 | DIGITAL | IOD_PTO_disk | D119
PTO_PMM_1_Faza3_Tok36_nad80 | DIGITAL | IOD_PTO_disk | D120
PTO_PMM_1_Faza3_Tok37_nad80 | DIGITAL | IOD_PTO_disk | D121
PTO_PMM_1_Faza3_Tok38_nad80 | DIGITAL | IOD_PTO_disk | D122
PTO_PMM_1_Faza3_Tok39_nad80 | DIGITAL | IOD_PTO_disk | D123
PTO_PMM_1_Faza3_Tok40_nad80 | DIGITAL | IOD_PTO_disk | D124
PTO_PMM_1_Faza3_Tok41_nad80 | DIGITAL | IOD_PTO_disk | D125
PTO_PMM_1_Faza3_Tok42_nad80 | DIGITAL | IOD_PTO_disk | D126
PTO_PMM_1_Faza1_Tok01_med60in80 | DIGITAL | IOD_PTO_disk | D127
PTO_PMM_1_Faza1_Tok02_med60in80 | DIGITAL | IOD_PTO_disk | D128
PTO_PMM_1_Faza1_Tok03_med60in80 | DIGITAL | IOD_PTO_disk | D129
PTO_PMM_1_Faza1_Tok04_med60in80 | DIGITAL | IOD_PTO_disk | D130
PTO_PMM_1_Faza1_Tok05_med60in80 | DIGITAL | IOD_PTO_disk | D131
PTO_PMM_1_Faza1_Tok06_med60in80 | DIGITAL | IOD_PTO_disk | D132
PTO_PMM_1_Faza1_Tok07_med60in80 | DIGITAL | IOD_PTO_disk | D133
PTO_PMM_1_Faza1_Tok08_med60in80 | DIGITAL | IOD_PTO_disk | D134
PTO_PMM_1_Faza1_Tok09_med60in80 | DIGITAL | IOD_PTO_disk | D135
PTO_PMM_1_Faza1_Tok10_med60in80 | DIGITAL | IOD_PTO_disk | D136
PTO_PMM_1_Faza1_Tok11_med60in80 | DIGITAL | IOD_PTO_disk | D137
PTO_PMM_1_Faza1_Tok12_med60in80 | DIGITAL | IOD_PTO_disk | D138
PTO_PMM_1_Faza1_Tok13_med60in80 | DIGITAL | IOD_PTO_disk | D139
PTO_PMM_1_Faza1_Tok14_med60in80 | DIGITAL | IOD_PTO_disk | D140
PTO_PMM_1_Faza1_Tok15_med60in80 | DIGITAL | IOD_PTO_disk | D141
PTO_PMM_1_Faza1_Tok16_med60in80 | DIGITAL | IOD_PTO_disk | D142
PTO_PMM_1_Faza1_Tok17_med60in80 | DIGITAL | IOD_PTO_disk | D143
PTO_PMM_1_Faza1_Tok18_med60in80 | DIGITAL | IOD_PTO_disk | D144
PTO_PMM_1_Faza1_Tok19_med60in80 | DIGITAL | IOD_PTO_disk | D145
PTO_PMM_1_Faza1_Tok20_med60in80 | DIGITAL | IOD_PTO_disk | D146
PTO_PMM_1_Faza1_Tok21_med60in80 | DIGITAL | IOD_PTO_disk | D147
PTO_PMM_1_Faza1_Tok22_med60in80 | DIGITAL | IOD_PTO_disk | D148
PTO_PMM_1_Faza1_Tok23_med60in80 | DIGITAL | IOD_PTO_disk | D149
PTO_PMM_1_Faza1_Tok24_med60in80 | DIGITAL | IOD_PTO_disk | D150
PTO_PMM_1_Faza1_Tok25_med60in80 | DIGITAL | IOD_PTO_disk | D151
PTO_PMM_1_Faza1_Tok26_med60in80 | DIGITAL | IOD_PTO_disk | D152
PTO_PMM_1_Faza1_Tok27_med60in80 | DIGITAL | IOD_PTO_disk | D153
PTO_PMM_1_Faza1_Tok28_med60in80 | DIGITAL | IOD_PTO_disk | D154
PTO_PMM_1_Faza1_Tok29_med60in80 | DIGITAL | IOD_PTO_disk | D155
PTO_PMM_1_Faza1_Tok30_med60in80 | DIGITAL | IOD_PTO_disk | D156
PTO_PMM_1_Faza1_Tok31_med60in80 | DIGITAL | IOD_PTO_disk | D157
PTO_PMM_1_Faza1_Tok32_med60in80 | DIGITAL | IOD_PTO_disk | D158
PTO_PMM_1_Faza1_Tok33_med60in80 | DIGITAL | IOD_PTO_disk | D159
PTO_PMM_1_Faza1_Tok34_med60in80 | DIGITAL | IOD_PTO_disk | D160
PTO_PMM_1_Faza1_Tok35_med60in80 | DIGITAL | IOD_PTO_disk | D161
PTO_PMM_1_Faza1_Tok36_med60in80 | DIGITAL | IOD_PTO_disk | D162
PTO_PMM_1_Faza1_Tok37_med60in80 | DIGITAL | IOD_PTO_disk | D163
PTO_PMM_1_Faza1_Tok38_med60in80 | DIGITAL | IOD_PTO_disk | D164
PTO_PMM_1_Faza1_Tok39_med60in80 | DIGITAL | IOD_PTO_disk | D165
PTO_PMM_1_Faza1_Tok40_med60in80 | DIGITAL | IOD_PTO_disk | D166
PTO_PMM_1_Faza1_Tok41_med60in80 | DIGITAL | IOD_PTO_disk | D167
PTO_PMM_1_Faza1_Tok42_med60in80 | DIGITAL | IOD_PTO_disk | D168
PTO_PMM_1_Faza2_Tok01_med60in80 | DIGITAL | IOD_PTO_disk | D169
PTO_PMM_1_Faza2_Tok02_med60in80 | DIGITAL | IOD_PTO_disk | D170
PTO_PMM_1_Faza2_Tok03_med60in80 | DIGITAL | IOD_PTO_disk | D171
PTO_PMM_1_Faza2_Tok04_med60in80 | DIGITAL | IOD_PTO_disk | D172
PTO_PMM_1_Faza2_Tok05_med60in80 | DIGITAL | IOD_PTO_disk | D173
PTO_PMM_1_Faza2_Tok06_med60in80 | DIGITAL | IOD_PTO_disk | D174
PTO_PMM_1_Faza2_Tok07_med60in80 | DIGITAL | IOD_PTO_disk | D175
PTO_PMM_1_Faza2_Tok08_med60in80 | DIGITAL | IOD_PTO_disk | D176
PTO_PMM_1_Faza2_Tok09_med60in80 | DIGITAL | IOD_PTO_disk | D177
PTO_PMM_1_Faza2_Tok10_med60in80 | DIGITAL | IOD_PTO_disk | D178
PTO_PMM_1_Faza2_Tok11_med60in80 | DIGITAL | IOD_PTO_disk | D179
PTO_PMM_1_Faza2_Tok12_med60in80 | DIGITAL | IOD_PTO_disk | D180
PTO_PMM_1_Faza2_Tok13_med60in80 | DIGITAL | IOD_PTO_disk | D181
PTO_PMM_1_Faza2_Tok14_med60in80 | DIGITAL | IOD_PTO_disk | D182
PTO_PMM_1_Faza2_Tok15_med60in80 | DIGITAL | IOD_PTO_disk | D183
PTO_PMM_1_Faza2_Tok16_med60in80 | DIGITAL | IOD_PTO_disk | D184
PTO_PMM_1_Faza2_Tok17_med60in80 | DIGITAL | IOD_PTO_disk | D185
PTO_PMM_1_Faza2_Tok18_med60in80 | DIGITAL | IOD_PTO_disk | D186
PTO_PMM_1_Faza2_Tok19_med60in80 | DIGITAL | IOD_PTO_disk | D187
PTO_PMM_1_Faza2_Tok20_med60in80 | DIGITAL | IOD_PTO_disk | D188
PTO_PMM_1_Faza2_Tok21_med60in80 | DIGITAL | IOD_PTO_disk | D189
PTO_PMM_1_Faza2_Tok22_med60in80 | DIGITAL | IOD_PTO_disk | D190
PTO_PMM_1_Faza2_Tok23_med60in80 | DIGITAL | IOD_PTO_disk | D191
PTO_PMM_1_Faza2_Tok24_med60in80 | DIGITAL | IOD_PTO_disk | D192
PTO_PMM_1_Faza2_Tok25_med60in80 | DIGITAL | IOD_PTO_disk | D193
PTO_PMM_1_Faza2_Tok26_med60in80 | DIGITAL | IOD_PTO_disk | D194
PTO_PMM_1_Faza2_Tok27_med60in80 | DIGITAL | IOD_PTO_disk | D195
PTO_PMM_1_Faza2_Tok28_med60in80 | DIGITAL | IOD_PTO_disk | D196
PTO_PMM_1_Faza2_Tok29_med60in80 | DIGITAL | IOD_PTO_disk | D197
PTO_PMM_1_Faza2_Tok30_med60in80 | DIGITAL | IOD_PTO_disk | D198
PTO_PMM_1_Faza2_Tok31_med60in80 | DIGITAL | IOD_PTO_disk | D199
PTO_PMM_1_Faza2_Tok32_med60in80 | DIGITAL | IOD_PTO_disk | D200
PTO_PMM_1_Faza2_Tok33_med60in80 | DIGITAL | IOD_PTO_disk | D201
PTO_PMM_1_Faza2_Tok34_med60in80 | DIGITAL | IOD_PTO_disk | D202
PTO_PMM_1_Faza2_Tok35_med60in80 | DIGITAL | IOD_PTO_disk | D203
PTO_PMM_1_Faza2_Tok36_med60in80 | DIGITAL | IOD_PTO_disk | D204
PTO_PMM_1_Faza2_Tok37_med60in80 | DIGITAL | IOD_PTO_disk | D205
PTO_PMM_1_Faza2_Tok38_med60in80 | DIGITAL | IOD_PTO_disk | D206
PTO_PMM_1_Faza2_Tok39_med60in80 | DIGITAL | IOD_PTO_disk | D207
PTO_PMM_1_Faza2_Tok40_med60in80 | DIGITAL | IOD_PTO_disk | D208
PTO_PMM_1_Faza2_Tok41_med60in80 | DIGITAL | IOD_PTO_disk | D209
PTO_PMM_1_Faza2_Tok42_med60in80 | DIGITAL | IOD_PTO_disk | D210
PTO_PMM_1_Faza3_Tok01_med60in80 | DIGITAL | IOD_PTO_disk | D211
PTO_PMM_1_Faza3_Tok02_med60in80 | DIGITAL | IOD_PTO_disk | D212
PTO_PMM_1_Faza3_Tok03_med60in80 | DIGITAL | IOD_PTO_disk | D213
PTO_PMM_1_Faza3_Tok04_med60in80 | DIGITAL | IOD_PTO_disk | D214
PTO_PMM_1_Faza3_Tok05_med60in80 | DIGITAL | IOD_PTO_disk | D215
PTO_PMM_1_Faza3_Tok06_med60in80 | DIGITAL | IOD_PTO_disk | D216
PTO_PMM_1_Faza3_Tok07_med60in80 | DIGITAL | IOD_PTO_disk | D217
PTO_PMM_1_Faza3_Tok08_med60in80 | DIGITAL | IOD_PTO_disk | D218
PTO_PMM_1_Faza3_Tok09_med60in80 | DIGITAL | IOD_PTO_disk | D219
PTO_PMM_1_Faza3_Tok10_med60in80 | DIGITAL | IOD_PTO_disk | D220
PTO_PMM_1_Faza3_Tok11_med60in80 | DIGITAL | IOD_PTO_disk | D221
PTO_PMM_1_Faza3_Tok12_med60in80 | DIGITAL | IOD_PTO_disk | D222
PTO_PMM_1_Faza3_Tok13_med60in80 | DIGITAL | IOD_PTO_disk | D223
PTO_PMM_1_Faza3_Tok14_med60in80 | DIGITAL | IOD_PTO_disk | D224
PTO_PMM_1_Faza3_Tok15_med60in80 | DIGITAL | IOD_PTO_disk | D225
PTO_PMM_1_Faza3_Tok16_med60in80 | DIGITAL | IOD_PTO_disk | D226
PTO_PMM_1_Faza3_Tok17_med60in80 | DIGITAL | IOD_PTO_disk | D227
PTO_PMM_1_Faza3_Tok18_med60in80 | DIGITAL | IOD_PTO_disk | D228
PTO_PMM_1_Faza3_Tok19_med60in80 | DIGITAL | IOD_PTO_disk | D229
PTO_PMM_1_Faza3_Tok20_med60in80 | DIGITAL | IOD_PTO_disk | D230
PTO_PMM_1_Faza3_Tok21_med60in80 | DIGITAL | IOD_PTO_disk | D231
PTO_PMM_1_Faza3_Tok22_med60in80 | DIGITAL | IOD_PTO_disk | D232
PTO_PMM_1_Faza3_Tok23_med60in80 | DIGITAL | IOD_PTO_disk | D233
PTO_PMM_1_Faza3_Tok24_med60in80 | DIGITAL | IOD_PTO_disk | D234
PTO_PMM_1_Faza3_Tok25_med60in80 | DIGITAL | IOD_PTO_disk | D235
PTO_PMM_1_Faza3_Tok26_med60in80 | DIGITAL | IOD_PTO_disk | D236
PTO_PMM_1_Faza3_Tok27_med60in80 | DIGITAL | IOD_PTO_disk | D237
PTO_PMM_1_Faza3_Tok28_med60in80 | DIGITAL | IOD_PTO_disk | D238
PTO_PMM_1_Faza3_Tok29_med60in80 | DIGITAL | IOD_PTO_disk | D239
PTO_PMM_1_Faza3_Tok30_med60in80 | DIGITAL | IOD_PTO_disk | D240
PTO_PMM_1_Faza3_Tok31_med60in80 | DIGITAL | IOD_PTO_disk | D241
PTO_PMM_1_Faza3_Tok32_med60in80 | DIGITAL | IOD_PTO_disk | D242
PTO_PMM_1_Faza3_Tok33_med60in80 | DIGITAL | IOD_PTO_disk | D243
PTO_PMM_1_Faza3_Tok34_med60in80 | DIGITAL | IOD_PTO_disk | D244
PTO_PMM_1_Faza3_Tok35_med60in80 | DIGITAL | IOD_PTO_disk | D245
PTO_PMM_1_Faza3_Tok36_med60in80 | DIGITAL | IOD_PTO_disk | D246
PTO_PMM_1_Faza3_Tok37_med60in80 | DIGITAL | IOD_PTO_disk | D247
PTO_PMM_1_Faza3_Tok38_med60in80 | DIGITAL | IOD_PTO_disk | D248
PTO_PMM_1_Faza3_Tok39_med60in80 | DIGITAL | IOD_PTO_disk | D249
PTO_PMM_1_Faza3_Tok40_med60in80 | DIGITAL | IOD_PTO_disk | D250
PTO_PMM_1_Faza3_Tok41_med60in80 | DIGITAL | IOD_PTO_disk | D251
PTO_PMM_1_Faza3_Tok42_med60in80 | DIGITAL | IOD_PTO_disk | D252
PTO_Polje_1Faza1_Tok01_16_nad80 | DIGITAL | IOD_PTO_disk | D2000[16]
PTO_Polje_1Faza1_Tok17_32_nad80 | DIGITAL | IOD_PTO_disk | D2016[16]
PTO_Polje_1Faza1_Tok33_42_nad80 | DIGITAL | IOD_PTO_disk | D2032[16]
PTO_Polje_1Faza2_Tok01_16_nad80 | DIGITAL | IOD_PTO_disk | D2048[16]
PTO_Polje_1Faza2_Tok17_32_nad80 | DIGITAL | IOD_PTO_disk | D2064[16]
PTO_Polje_1Faza2_Tok33_42_nad80 | DIGITAL | IOD_PTO_disk | D2080[16]
PTO_Polje_1Faza3_Tok01_16_nad80 | DIGITAL | IOD_PTO_disk | D2096[16]
PTO_Polje_1Faza3_Tok17_32_nad80 | DIGITAL | IOD_PTO_disk | D2112[16]
PTO_Polje_1Faza3_Tok33_42_nad80 | DIGITAL | IOD_PTO_disk | D2128[16]
PTO_Polje_1Faza1_Tok01_16_med60_80 | DIGITAL | IOD_PTO_disk | D2320[16]
PTO_Polje_1Faza1_Tok17_32_med60_80 | DIGITAL | IOD_PTO_disk | D2336[16]
PTO_Polje_1Faza1_Tok33_42_med60_80 | DIGITAL | IOD_PTO_disk | D2352[16]
PTO_Polje_1Faza2_Tok01_16_med60_80 | DIGITAL | IOD_PTO_disk | D2368[16]
PTO_Polje_1Faza2_Tok17_32_med60_80 | DIGITAL | IOD_PTO_disk | D2384[16]
PTO_Polje_1Faza2_Tok33_42_med60_80 | DIGITAL | IOD_PTO_disk | D2400[16]
PTO_Polje_1Faza3_Tok01_16_med60_80 | DIGITAL | IOD_PTO_disk | D2416[16]
PTO_Polje_1Faza3_Tok17_32_med60_80 | DIGITAL | IOD_PTO_disk | D2432[16]
PTO_Polje_1Faza3_Tok33_42_med60_80 | DIGITAL | IOD_PTO_disk | D2448[16]
PTO_PrviZagon | DIGITAL | IOD_PTO_disk | D3001
PTO_ComSCADA_stevec1 | INT | IOD_PTO_disk | I1
PTO_ComSCADA_stevec2 | INT | IOD_PTO_disk | I2
PTOErrCommScada_omogoci | DIGITAL | IOD_PTO_disk | D3010
PTOErrComPanelPLC_omogoci | DIGITAL | IOD_PTO_disk | D3011
PTOErrComPort2_omogoci | DIGITAL | IOD_PTO_disk | D3012
PTOErrComPort3_omogoci | DIGITAL | IOD_PTO_disk | D3013
PTOErrComPort4_omogoci | DIGITAL | IOD_PTO_disk | D3014
PTOErrComUPS1_omogoci | DIGITAL | IOD_PTO_disk | D3015
PTOErrComUPS2_omogoci | DIGITAL | IOD_PTO_disk | D3016
PTOErrComPMM1_omogoci | DIGITAL | IOD_PTO_disk | D3017
PTOErrComCirc1_omogoci | DIGITAL | IOD_PTO_disk | D3018
PTOErrComKlima1_omogoci | DIGITAL | IOD_PTO_disk | D3019
PTOErrComKlima2_omogoci | DIGITAL | IOD_PTO_disk | D3020
PTOErrComKlima3_omogoci | DIGITAL | IOD_PTO_disk | D3021
PTOErrComKlima4_omogoci | DIGITAL | IOD_PTO_disk | D3022
PTOErrComKlima5_omogoci | DIGITAL | IOD_PTO_disk | D3023
PTOErrComKlima6_omogoci | DIGITAL | IOD_PTO_disk | D3024
PTOPMMOverCurrentBetw1_omogoci | DIGITAL | IOD_PTO_disk | D3025
PTOPMMOverCurrentBetw2_omogoci | DIGITAL | IOD_PTO_disk | D3026
PTOPMMOverCurrentBetw3_omogoci | DIGITAL | IOD_PTO_disk | D3027
PTOPMMOverCurrentOver1_omogoci | DIGITAL | IOD_PTO_disk | D3028
PTOPMMOverCurrentOver2_omogoci | DIGITAL | IOD_PTO_disk | D3029
PTOPMMOverCurrentOver3_omogoci | DIGITAL | IOD_PTO_disk | D3030
PTOUPS2AlarmSlabaBaterija_omogoci | DIGITAL | IOD_PTO_disk | D3031
PTOUPS2AlarmOnBattery_omogoci | DIGITAL | IOD_PTO_disk | D3032
PTOUPS2AlarmLowBattery_omogoci | DIGITAL | IOD_PTO_disk | D3033
PTOUPS2AlarmDepletedBattery_omogoci | DIGITAL | IOD_PTO_disk | D3034
PTOUPS2AlarmTemperaturaIzvenTo_omogoci | DIGITAL | IOD_PTO_disk | D3035
PTOUPS2AlarmStanjeVhodaIzvenTo_omogoci | DIGITAL | IOD_PTO_disk | D3036
PTOUPS2AlarmStanjeIzhodaIzvenTo_omogoci | DIGITAL | IOD_PTO_disk | D3037
PTOUPS2AlarmIzhodPreobremenjen_omogoci | DIGITAL | IOD_PTO_disk | D3038
PTOUPS2AlarmOnBypass_omogoci | DIGITAL | IOD_PTO_disk | D3039
PTOUPS2AlarmBypassBad_omogoci | DIGITAL | IOD_PTO_disk | D3040
PTOUPS2AlarmIzhodOffKotZahteva_omogoci | DIGITAL | IOD_PTO_disk | D3041
PTOUPS2AlarmUPSOffKotZahtevano_omogoci | DIGITAL | IOD_PTO_disk | D3042
PTOUPS2AlarmChargerFailed_omogoci | DIGITAL | IOD_PTO_disk | D3043
PTOUPS2AlarmUPSIzhodOff_omogoci | DIGITAL | IOD_PTO_disk | D3044
PTOUPS2AlarmUPSSystemOff_omogoci | DIGITAL | IOD_PTO_disk | D3045
PTOUPS2AlarmNapakaNaVentilator_omogoci | DIGITAL | IOD_PTO_disk | D3046
PTOUPS2AlarmNapakaNaVarovalki_omogoci | DIGITAL | IOD_PTO_disk | D3047
PTOUPS2AlarmSplosnaNapaka_omogoci | DIGITAL | IOD_PTO_disk | D3048
PTOUPS2AlarmDiagnosticTestFail_omogoci | DIGITAL | IOD_PTO_disk | D3049
PTOUPS2AlarmCommunicationsLost_omogoci | DIGITAL | IOD_PTO_disk | D3050
PTOUPS2AlarmAwaitingPower_omogoci | DIGITAL | IOD_PTO_disk | D3051
PTOUPS2AlarmShutdownPending_omogoci | DIGITAL | IOD_PTO_disk | D3052
PTOUPS2AlarmShutdownImminent_omogoci | DIGITAL | IOD_PTO_disk | D3053
PTOUPS2AlarmTestInProgres_omogoci | DIGITAL | IOD_PTO_disk | D3054
PTOUPS2AlarmReceptacleOff_omogoci | DIGITAL | IOD_PTO_disk | D3055
PTOUPS1AlarmSlabaBaterija_omogoci | DIGITAL | IOD_PTO_disk | D3056
PTOUPS1AlarmOnBattery_omogoci | DIGITAL | IOD_PTO_disk | D3057
PTOUPS1AlarmLowBattery_omogoci | DIGITAL | IOD_PTO_disk | D3058
PTOUPS1AlarmDepletedBattery_omogoci | DIGITAL | IOD_PTO_disk | D3059
PTOUPS1AlarmTemperaturaIzvenTo_omogoci | DIGITAL | IOD_PTO_disk | D3060
PTOUPS1AlarmStanjeVhodaIzvenTo_omogoci | DIGITAL | IOD_PTO_disk | D3061
PTOUPS1AlarmStanjeIzhodaIizvenTo_omogoci | DIGITAL | IOD_PTO_disk | D3062
PTOUPS1AlarmIzhodPreobremenjen_omogoci | DIGITAL | IOD_PTO_disk | D3063
PTOUPS1AlarmOnBypass_omogoci | DIGITAL | IOD_PTO_disk | D3064
PTOUPS1AlarmBypassBad_omogoci | DIGITAL | IOD_PTO_disk | D3065
PTOUPS1AlarmIzhodOffKotZahteva_omogoci | DIGITAL | IOD_PTO_disk | D3066
PTOUPS1AlarmUPSOffKotZahtevano_omogoci | DIGITAL | IOD_PTO_disk | D3067
PTOUPS1AlarmChargerFailed_omogoci | DIGITAL | IOD_PTO_disk | D3068
PTOUPS1AlarmUPSIzhodOff_omogoci | DIGITAL | IOD_PTO_disk | D3069
PTOUPS1AlarmUPSSystemOff_omogoci | DIGITAL | IOD_PTO_disk | D3070
PTOUPS1AlarmNapakaNaVentilator_omogoci | DIGITAL | IOD_PTO_disk | D3071
PTOUPS1AlarmNapakaNaVarovalki_omogoci | DIGITAL | IOD_PTO_disk | D3072
PTOUPS1AlarmSplosnaNapaka_omogoci | DIGITAL | IOD_PTO_disk | D3073
PTOUPS1AlarmDiagnosticTestFail_omogoci | DIGITAL | IOD_PTO_disk | D3074
PTOUPS1AlarmCommunicationsLost_omogoci | DIGITAL | IOD_PTO_disk | D3075
PTOUPS1AlarmAwaitingPower_omogoci | DIGITAL | IOD_PTO_disk | D3076
PTOUPS1AlarmShutdownPending_omogoci | DIGITAL | IOD_PTO_disk | D3077
PTOUPS1AlarmShutdownImminent_omogoci | DIGITAL | IOD_PTO_disk | D3078
PTOUPS1AlarmTestInProgres_omogoci | DIGITAL | IOD_PTO_disk | D3079
PTOUPS1AlarmReceptacleOff_omogoci | DIGITAL | IOD_PTO_disk | D3080
PTODI_Q2_Rezerva_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3081
PTODI_Q5_OdcKlima1_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3082
PTODI_Q6_OdcKlima2_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3083
PTODI_Q7_OdcKlima3_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3084
PTODI_Q8_OdcKlima4_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3085
PTODI_Q9_OdcKlima5_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3086
PTODI_Q10_OdcKlima6_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3087
PTODI_Q25_OdcUpsA_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3088
PTODI_Q26_OdcByA_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3089
PTODI_Q27_OdcByUpsA_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3090
PTODI_Q28_OdcUpsB_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3091
PTODI_Q29_OdcByB_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3092
PTODI_Q30_OdcByUpsB_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3093
PTODI_Klima5_ERR_omogoci | DIGITAL | IOD_PTO_disk | D3094
PTODI_Klima6_ERR_omogoci | DIGITAL | IOD_PTO_disk | D3095
PTODI_KlimaSplit1_ERR_omogoci | DIGITAL | IOD_PTO_disk | D3096
PTODI_UpsA_ON_omogoci | DIGITAL | IOD_PTO_disk | D3097
PTODI_UpsA_ERR_omogoci | DIGITAL | IOD_PTO_disk | D3098
PTODI_UpsB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3099
PTODI_UpsB_ERR_omogoci | DIGITAL | IOD_PTO_disk | D3100
PTODI_UPS_Alarm_omogoci | DIGITAL | IOD_PTO_disk | D3101
PTODI_UPS_BatNacin_omogoci | DIGITAL | IOD_PTO_disk | D3102
PTODI_UPS_Polnjenje_omogoci | DIGITAL | IOD_PTO_disk | D3103
PTODI_RazlitjeVodeK5K6_omogoci | DIGITAL | IOD_PTO_disk | D3104
PTOSetDateTimeError_omogoci | DIGITAL | IOD_PTO_disk | D3105
PTOTempTSprevisoka1_omogoci | DIGITAL | IOD_PTO_disk | D3106
PTONapakaSenzorTemp1_omogoci | DIGITAL | IOD_PTO_disk | D3107
PTONapakaSenzorVlaga1_omogoci | DIGITAL | IOD_PTO_disk | D3108
PTOSlabaBaterijaPLC_A1_omogoci | DIGITAL | IOD_PTO_disk | D3109
PTOKlima1GeneralAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3110
PTOKlima1AlarmKompresor1omogoci | DIGITAL | IOD_PTO_disk | D3111
PTOKlima1AlarmKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3112
PTOKlima1NizekPritiskKompresor1omogoci | DIGITAL | IOD_PTO_disk | D3113
PTOKlima1NizekPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3114
PTOKlima1NapakaPriPretoku_omogoci | DIGITAL | IOD_PTO_disk | D3115
PTOKlima1FenThermalCutout_omogoci | DIGITAL | IOD_PTO_disk | D3116
PTOKlima1ThermalCutoutHeater1omogoci | DIGITAL | IOD_PTO_disk | D3117
PTOKlima1ThermalCutoutHeater2_omogoci | DIGITAL | IOD_PTO_disk | D3118
PTOKlima1PozarniAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3119
PTOKlima1ZamasenFilter_omogoci | DIGITAL | IOD_PTO_disk | D3120
PTOKlima1VisokaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3121
PTOKlima1NizkaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3122
PTOKlima1VisokaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3123
PTOKlima1NizkaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3124
PTOKlima1Kompresor1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3125
PTOKlima1Kompresor2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3126
PTOKlima1VentilatorNaMejiObrU_omogoci | DIGITAL | IOD_PTO_disk | D3127
PTOKlima1VisokaTempPovratneVod_omogoci | DIGITAL | IOD_PTO_disk | D3128
PTOKlima1NizkaTempPovratneVode_omogoci | DIGITAL | IOD_PTO_disk | D3129
PTOKlima1NapakaSenzorTempPros_omogoci | DIGITAL | IOD_PTO_disk | D3130
PTOKlima1NapakaSenzorTempIzih_omogoci | DIGITAL | IOD_PTO_disk | D3131
PTOKlima1NapakaSenzorPovratVod_omogoci | DIGITAL | IOD_PTO_disk | D3132
PTOKlima1NapakaSenzorZunanjeTe_omogoci | DIGITAL | IOD_PTO_disk | D3133
PTOKlima1NapakaSenzorVlaznosti_omogoci | DIGITAL | IOD_PTO_disk | D3134
PTOKlima1FaultyEPROM_omogoci | DIGITAL | IOD_PTO_disk | D3135
PTOKlima1StoppedByAlarms_omogoci | DIGITAL | IOD_PTO_disk | D3136
PTOKlima1VisokTokVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3137
PTOKlima1NiVodeVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3138
PTOKlima1NiTokaVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3139
PTOKlima1RocniIzklop_omogoci | DIGITAL | IOD_PTO_disk | D3140
PTOKlima2GeneralAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3141
PTOKlima2AlarmKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3142
PTOKlima2AlarmKompresor2omogoci | DIGITAL | IOD_PTO_disk | D3143
PTOKlima2NizekPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3144
PTOKlima2NizekPritiskKompresor2omogoci | DIGITAL | IOD_PTO_disk | D3145
PTOKlima2NapakaPriPretokuZraka_omogoci | DIGITAL | IOD_PTO_disk | D3146
PTOKlima2FenThermalCutout_omogoci | DIGITAL | IOD_PTO_disk | D3147
PTOKlima2ThermalCutoutHeater1_omogoci | DIGITAL | IOD_PTO_disk | D3148
PTOKlima2ThermalCutoutHeater2_omogoci | DIGITAL | IOD_PTO_disk | D3149
PTOKlima2PozarniAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3150
PTOKlima2ZamasenFilter_omogoci | DIGITAL | IOD_PTO_disk | D3151
PTOKlima2VisokaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3152
PTOKlima2NizkaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3153
PTOKlima2VisokaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3154
PTOKlima2NizkaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3155
PTOKlima2Kompresor1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3156
PTOKlima2Kompresor2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3157
PTOKlima2VentilatorNaMejiObrU_omogoci | DIGITAL | IOD_PTO_disk | D3158
PTOKlima2VisokaTempPovratneVod_omogoci | DIGITAL | IOD_PTO_disk | D3159
PTOKlima2NizkaTempPovratneVode_omogoci | DIGITAL | IOD_PTO_disk | D3160
PTOKlima2NapakaSenzorTempPros_omogoci | DIGITAL | IOD_PTO_disk | D3161
PTOKlima2NapakaSenzorPovratVod_omogoci | DIGITAL | IOD_PTO_disk | D3162
PTOKlima2NapakaSenzorZunanjeTe_omogoci | DIGITAL | IOD_PTO_disk | D3163
PTOKlima2NapakaSenzorTempIzpih_omogoci | DIGITAL | IOD_PTO_disk | D3164
PTOKlima2NapakaSenzorVlaznosti_omogoci | DIGITAL | IOD_PTO_disk | D3165
PTOKlima2FaultyEPROM_omogoci | DIGITAL | IOD_PTO_disk | D3166
PTOKlima2StoppedByAlarms_omogoci | DIGITAL | IOD_PTO_disk | D3167
PTOKlima2VisokTokVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3168
PTOKlima2NiVodeVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3169
PTOKlima2NiTokaVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3170
PTOKlima2RocniIzklop_omogoci | DIGITAL | IOD_PTO_disk | D3171
PTOKlima3GeneralAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3172
PTOKlima3AlarmKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3173
PTOKlima3AlarmKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3174
PTOKlima3NizekPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3175
PTOKlima3NizekPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3176
PTOKlima3NapakaPriPretoku_omogoci | DIGITAL | IOD_PTO_disk | D3177
PTOKlima3FenThermalCutout_omogoci | DIGITAL | IOD_PTO_disk | D3178
PTOKlima3ThermalCutoutHeater1_omogoci | DIGITAL | IOD_PTO_disk | D3179
PTOKlima3ThermalCutoutHeater2_omogoci | DIGITAL | IOD_PTO_disk | D3180
PTOKlima3PozarniAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3181
PTOKlima3ZamasenFilter_omogoci | DIGITAL | IOD_PTO_disk | D3182
PTOKlima3VisokaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3183
PTOKlima3NizkaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3184
PTOKlima3VisokaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3185
PTOKlima3NizkaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3186
PTOKlima3Kompresor1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3187
PTOKlima3Kompresor2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3188
PTOKlima3VentilatorNaMejiObrU_omogoci | DIGITAL | IOD_PTO_disk | D3189
PTOKlima3VisokaTempPovratneVod_omogoci | DIGITAL | IOD_PTO_disk | D3190
PTOKlima3NizkaTempPovratneVode_omogoci | DIGITAL | IOD_PTO_disk | D3191
PTOKlima3NapakaSenzorTempPros_omogoci | DIGITAL | IOD_PTO_disk | D3192
PTOKlima3NapakaSenzorTempIzih_omogoci | DIGITAL | IOD_PTO_disk | D3193
PTOKlima3NapakaSenzorPovratVod_omogoci | DIGITAL | IOD_PTO_disk | D3194
PTOKlima3NapakaSenzorZunanjeTe_omogoci | DIGITAL | IOD_PTO_disk | D3195
PTOKlima3NapakaSenzorVlaznosti_omogoci | DIGITAL | IOD_PTO_disk | D3196
PTOKlima3FaultyEPROM_omogoci | DIGITAL | IOD_PTO_disk | D3197
PTOKlima3StoppedByAlarms_omogoci | DIGITAL | IOD_PTO_disk | D3198
PTOKlima3VisokTokVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3199
PTOKlima3NiVodeVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3200
PTOKlima3NiTokaVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3201
PTOKlima3RocniIzklop_omogoci | DIGITAL | IOD_PTO_disk | D3202
PTOKlima4GeneralAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3203
PTOKlima4AlarmKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3204
PTOKlima4AlarmKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3205
PTOKlima4NizekPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3206
PTOKlima4NizekPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3207
PTOKlima4NapakaPriPretoku_omogoci | DIGITAL | IOD_PTO_disk | D3208
PTOKlima4FenThermalCutout_omogoci | DIGITAL | IOD_PTO_disk | D3209
PTOKlima4ThermalCutoutHeater1_omogoci | DIGITAL | IOD_PTO_disk | D3210
PTOKlima4ThermalCutoutHeater2_omogoci | DIGITAL | IOD_PTO_disk | D3211
PTOKlima4PozarniAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3212
PTOKlima4ZamasenFilter_omogoci | DIGITAL | IOD_PTO_disk | D3213
PTOKlima4VisokaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3214
PTOKlima4NizkaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3215
PTOKlima4VisokaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3216
PTOKlima4NizkaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3217
PTOKlima4Kompresor1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3218
PTOKlima4Kompresor2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3219
PTOKlima4VentilatorNaMejiObrU_omogoci | DIGITAL | IOD_PTO_disk | D3220
PTOKlima4VisokaTempPovratneVod_omogoci | DIGITAL | IOD_PTO_disk | D3221
PTOKlima4NizkaTempPovratneVode_omogoci | DIGITAL | IOD_PTO_disk | D3222
PTOKlima4NapakaSenzorTempPros_omogoci | DIGITAL | IOD_PTO_disk | D3223
PTOKlima4NapakaSenzorTempIzih_omogoci | DIGITAL | IOD_PTO_disk | D3224
PTOKlima4NapakaSenzorPovratVod_omogoci | DIGITAL | IOD_PTO_disk | D3225
PTOKlima4NapakaSenzorZunanjeTe_omogoci | DIGITAL | IOD_PTO_disk | D3226
PTOKlima4NapakaSenzorVlaznosti_omogoci | DIGITAL | IOD_PTO_disk | D3227
PTOKlima4FaultyEPROM_omogoci | DIGITAL | IOD_PTO_disk | D3228
PTOKlima4StoppedByAlarms_omogoci | DIGITAL | IOD_PTO_disk | D3229
PTOKlima4VisokTokVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3230
PTOKlima4NiVodeVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3231
PTOKlima4NiTokaVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3232
PTOKlima4RocniIzklop_omogoci | DIGITAL | IOD_PTO_disk | D3233
PTOKlima5GeneralAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3234
PTOKlima5AlarmKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3235
PTOKlima5AlarmKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3236
PTOKlima5NizekPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3237
PTOKlima5NizekPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3238
PTOKlima5NapakaPriPretoku_omogoci | DIGITAL | IOD_PTO_disk | D3239
PTOKlima5FenThermalCutout_omogoci | DIGITAL | IOD_PTO_disk | D3240
PTOKlima5ThermalCutoutHeater1_omogoci | DIGITAL | IOD_PTO_disk | D3241
PTOKlima5ThermalCutoutHeater2_omogoci | DIGITAL | IOD_PTO_disk | D3242
PTOKlima5PozarniAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3243
PTOKlima5ZamasenFilter_omogoci | DIGITAL | IOD_PTO_disk | D3244
PTOKlima5VisokaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3245
PTOKlima5NizkaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3246
PTOKlima5VisokaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3247
PTOKlima5NizkaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3248
PTOKlima5Kompresor1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3249
PTOKlima5Kompresor2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3250
PTOKlima5VentilatorNaMejiObrU_omogoci | DIGITAL | IOD_PTO_disk | D3251
PTOKlima5VisokaTempPovratneVod_omogoci | DIGITAL | IOD_PTO_disk | D3252
PTOKlima5NizkaTempPovratneVode_omogoci | DIGITAL | IOD_PTO_disk | D3253
PTOKlima5NapakaSenzorTempPros_omogoci | DIGITAL | IOD_PTO_disk | D3254
PTOKlima5NapakaSenzorTempIzih_omogoci | DIGITAL | IOD_PTO_disk | D3255
PTOKlima5NapakaSenzorPovratVod_omogoci | DIGITAL | IOD_PTO_disk | D3256
PTOKlima5NapakaSenzorZunanjeTe_omogoci | DIGITAL | IOD_PTO_disk | D3257
PTOKlima5NapakaSenzorVlaznosti_omogoci | DIGITAL | IOD_PTO_disk | D3258
PTOKlima5FaultyEPROM_omogoci | DIGITAL | IOD_PTO_disk | D3259
PTOKlima5StoppedByAlarms_omogoci | DIGITAL | IOD_PTO_disk | D3260
PTOKlima5VisokTokVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3261
PTOKlima5NiVodeVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3262
PTOKlima5NiTokaVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3263
PTOKlima5RocniIzklop_omogoci | DIGITAL | IOD_PTO_disk | D3264
PTOKlima6GeneralAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3265
PTOKlima6AlarmKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3266
PTOKlima6AlarmKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3267
PTOKlima6NizekPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk | D3268
PTOKlima6NizekPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk | D3269
PTOKlima6NapakaPriPretoku_omogoci | DIGITAL | IOD_PTO_disk | D3270
PTOKlima6FenThermalCutout_omogoci | DIGITAL | IOD_PTO_disk | D3271
PTOKlima6ThermalCutoutHeater1_omogoci | DIGITAL | IOD_PTO_disk | D3272
PTOKlima6ThermalCutoutHeater2_omogoci | DIGITAL | IOD_PTO_disk | D3273
PTOKlima6PozarniAlarm_omogoci | DIGITAL | IOD_PTO_disk | D3274
PTOKlima6ZamasenFilter_omogoci | DIGITAL | IOD_PTO_disk | D3275
PTOKlima6VisokaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3276
PTOKlima6NizkaTempVProstoru_omogoci | DIGITAL | IOD_PTO_disk | D3277
PTOKlima6VisokaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3278
PTOKlima6NizkaVlaznost_omogoci | DIGITAL | IOD_PTO_disk | D3279
PTOKlima6Kompresor1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3280
PTOKlima6Kompresor2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk | D3281
PTOKlima6VentilatorNaMejiObrU_omogoci | DIGITAL | IOD_PTO_disk | D3282
PTOKlima6VisokaTempPovratneVod_omogoci | DIGITAL | IOD_PTO_disk | D3283
PTOKlima6NizkaTempPovratneVode_omogoci | DIGITAL | IOD_PTO_disk | D3284
PTOKlima6NapakaSenzorTempPros_omogoci | DIGITAL | IOD_PTO_disk | D3285
PTOKlima6NapakaSenzorTempIzih_omogoci | DIGITAL | IOD_PTO_disk | D3286
PTOKlima6NapakaSenzorPovratVod_omogoci | DIGITAL | IOD_PTO_disk | D3287
PTOKlima6NapakaSenzorZunanjeTe_omogoci | DIGITAL | IOD_PTO_disk | D3288
PTOKlima6NapakaSenzorVlaznosti_omogoci | DIGITAL | IOD_PTO_disk | D3289
PTOKlima6FaultyEPROM_omogoci | DIGITAL | IOD_PTO_disk | D3290
PTOKlima6StoppedByAlarms_omogoci | DIGITAL | IOD_PTO_disk | D3291
PTOKlima6VisokTokVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3292
PTOKlima6NiVodeVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3293
PTOKlima6NiTokaVVlazilcu_omogoci | DIGITAL | IOD_PTO_disk | D3294
PTOKlima6RocniIzklop_omogoci | DIGITAL | IOD_PTO_disk | D3295
PTOPMM_Faza1_Tok01_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3100
PTOPMM_Faza1_Tok02_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3101
PTOPMM_Faza1_Tok03_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3102
PTOPMM_Faza1_Tok04_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3103
PTOPMM_Faza1_Tok05_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3104
PTOPMM_Faza1_Tok06_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3105
PTOPMM_Faza1_Tok07_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3106
PTOPMM_Faza1_Tok08_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3107
PTOPMM_Faza1_Tok09_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3108
PTOPMM_Faza1_Tok10_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3109
PTOPMM_Faza1_Tok11_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3110
PTOPMM_Faza1_Tok12_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3111
PTOPMM_Faza1_Tok13_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3112
PTOPMM_Faza1_Tok14_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3113
PTOPMM_Faza1_Tok15_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3114
PTOPMM_Faza1_Tok16_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3115
PTOPMM_Faza1_Tok17_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3116
PTOPMM_Faza1_Tok18_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3117
PTOPMM_Faza1_Tok19_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3118
PTOPMM_Faza1_Tok20_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3119
PTOPMM_Faza1_Tok21_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3120
PTOPMM_Faza1_Tok22_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3121
PTOPMM_Faza1_Tok23_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3122
PTOPMM_Faza1_Tok24_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3123
PTOPMM_Faza1_Tok25_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3124
PTOPMM_Faza1_Tok26_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3125
PTOPMM_Faza1_Tok27_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3126
PTOPMM_Faza1_Tok28_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3127
PTOPMM_Faza1_Tok29_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3128
PTOPMM_Faza1_Tok30_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3129
PTOPMM_Faza1_Tok31_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3130
PTOPMM_Faza1_Tok32_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3131
PTOPMM_Faza1_Tok33_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3132
PTOPMM_Faza1_Tok34_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3133
PTOPMM_Faza1_Tok35_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3134
PTOPMM_Faza1_Tok36_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3135
PTOPMM_Faza1_Tok37_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3136
PTOPMM_Faza1_Tok38_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3137
PTOPMM_Faza1_Tok39_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3138
PTOPMM_Faza1_Tok40_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3139
PTOPMM_Faza1_Tok41_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3140
PTOPMM_Faza1_Tok42_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3141
PTOPMM_Faza2_Tok01_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3142
PTOPMM_Faza2_Tok02_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3143
PTOPMM_Faza2_Tok03_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3144
PTOPMM_Faza2_Tok04_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3145
PTOPMM_Faza2_Tok05_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3146
PTOPMM_Faza2_Tok06_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3147
PTOPMM_Faza2_Tok07_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3148
PTOPMM_Faza2_Tok08_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3149
PTOPMM_Faza2_Tok09_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3150
PTOPMM_Faza2_Tok10_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3151
PTOPMM_Faza2_Tok11_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3152
PTOPMM_Faza2_Tok12_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3153
PTOPMM_Faza2_Tok13_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3154
PTOPMM_Faza2_Tok14_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3155
PTOPMM_Faza2_Tok15_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3156
PTOPMM_Faza2_Tok16_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3157
PTOPMM_Faza2_Tok17_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3158
PTOPMM_Faza2_Tok18_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3159
PTOPMM_Faza2_Tok19_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3160
PTOPMM_Faza2_Tok20_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3161
PTOPMM_Faza2_Tok21_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3162
PTOPMM_Faza2_Tok22_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3163
PTOPMM_Faza2_Tok23_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3164
PTOPMM_Faza2_Tok24_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3165
PTOPMM_Faza2_Tok25_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3166
PTOPMM_Faza2_Tok26_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3167
PTOPMM_Faza2_Tok27_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3168
PTOPMM_Faza2_Tok28_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3169
PTOPMM_Faza2_Tok29_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3170
PTOPMM_Faza2_Tok30_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3171
PTOPMM_Faza2_Tok31_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3172
PTOPMM_Faza2_Tok32_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3173
PTOPMM_Faza2_Tok33_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3174
PTOPMM_Faza2_Tok34_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3175
PTOPMM_Faza2_Tok35_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3176
PTOPMM_Faza2_Tok36_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3177
PTOPMM_Faza2_Tok37_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3178
PTOPMM_Faza2_Tok38_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3179
PTOPMM_Faza2_Tok39_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3180
PTOPMM_Faza2_Tok40_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3181
PTOPMM_Faza2_Tok41_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3182
PTOPMM_Faza2_Tok42_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3183
PTOPMM_Faza3_Tok01_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3184
PTOPMM_Faza3_Tok02_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3185
PTOPMM_Faza3_Tok03_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3186
PTOPMM_Faza3_Tok04_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3187
PTOPMM_Faza3_Tok05_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3188
PTOPMM_Faza3_Tok06_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3189
PTOPMM_Faza3_Tok07_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3190
PTOPMM_Faza3_Tok08_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3191
PTOPMM_Faza3_Tok09_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3192
PTOPMM_Faza3_Tok10_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3193
PTOPMM_Faza3_Tok11_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3194
PTOPMM_Faza3_Tok12_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3195
PTOPMM_Faza3_Tok13_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3196
PTOPMM_Faza3_Tok14_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3197
PTOPMM_Faza3_Tok15_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3198
PTOPMM_Faza3_Tok16_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3199
PTOPMM_Faza3_Tok17_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3200
PTOPMM_Faza3_Tok18_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3201
PTOPMM_Faza3_Tok19_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3202
PTOPMM_Faza3_Tok20_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3203
PTOPMM_Faza3_Tok21_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3204
PTOPMM_Faza3_Tok22_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3205
PTOPMM_Faza3_Tok23_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3206
PTOPMM_Faza3_Tok24_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3207
PTOPMM_Faza3_Tok25_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3208
PTOPMM_Faza3_Tok26_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3209
PTOPMM_Faza3_Tok27_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3210
PTOPMM_Faza3_Tok28_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3211
PTOPMM_Faza3_Tok29_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3212
PTOPMM_Faza3_Tok30_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3213
PTOPMM_Faza3_Tok31_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3214
PTOPMM_Faza3_Tok32_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3215
PTOPMM_Faza3_Tok33_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3216
PTOPMM_Faza3_Tok34_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3217
PTOPMM_Faza3_Tok35_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3218
PTOPMM_Faza3_Tok36_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3219
PTOPMM_Faza3_Tok37_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3220
PTOPMM_Faza3_Tok38_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3221
PTOPMM_Faza3_Tok39_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3222
PTOPMM_Faza3_Tok40_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3223
PTOPMM_Faza3_Tok41_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3224
PTOPMM_Faza3_Tok42_nad80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3225
PTOPMM_Faza1_Tok01_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3226
PTOPMM_Faza1_Tok02_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3227
PTOPMM_Faza1_Tok03_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3228
PTOPMM_Faza1_Tok04_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3229
PTOPMM_Faza1_Tok05_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3230
PTOPMM_Faza1_Tok06_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3231
PTOPMM_Faza1_Tok07_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3232
PTOPMM_Faza1_Tok08_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3233
PTOPMM_Faza1_Tok09_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3234
PTOPMM_Faza1_Tok10_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3235
PTOPMM_Faza1_Tok11_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3236
PTOPMM_Faza1_Tok12_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3237
PTOPMM_Faza1_Tok13_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3238
PTOPMM_Faza1_Tok14_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3239
PTOPMM_Faza1_Tok15_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3240
PTOPMM_Faza1_Tok16_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3241
PTOPMM_Faza1_Tok17_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3242
PTOPMM_Faza1_Tok18_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3243
PTOPMM_Faza1_Tok19_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3244
PTOPMM_Faza1_Tok20_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3245
PTOPMM_Faza1_Tok21_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3246
PTOPMM_Faza1_Tok22_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3247
PTOPMM_Faza1_Tok23_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3248
PTOPMM_Faza1_Tok24_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3249
PTOPMM_Faza1_Tok25_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3250
PTOPMM_Faza1_Tok26_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3251
PTOPMM_Faza1_Tok27_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3252
PTOPMM_Faza1_Tok28_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3253
PTOPMM_Faza1_Tok29_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3254
PTOPMM_Faza1_Tok30_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3255
PTOPMM_Faza1_Tok31_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3256
PTOPMM_Faza1_Tok32_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3257
PTOPMM_Faza1_Tok33_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3258
PTOPMM_Faza1_Tok34_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3259
PTOPMM_Faza1_Tok35_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3260
PTOPMM_Faza1_Tok36_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3261
PTOPMM_Faza1_Tok37_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3262
PTOPMM_Faza1_Tok38_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3263
PTOPMM_Faza1_Tok39_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3264
PTOPMM_Faza1_Tok40_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3265
PTOPMM_Faza1_Tok41_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3266
PTOPMM_Faza1_Tok42_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3267
PTOPMM_Faza2_Tok01_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3268
PTOPMM_Faza2_Tok02_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3269
PTOPMM_Faza2_Tok03_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3270
PTOPMM_Faza2_Tok04_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3271
PTOPMM_Faza2_Tok05_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3272
PTOPMM_Faza2_Tok06_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3273
PTOPMM_Faza2_Tok07_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3274
PTOPMM_Faza2_Tok08_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3275
PTOPMM_Faza2_Tok09_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3276
PTOPMM_Faza2_Tok10_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3277
PTOPMM_Faza2_Tok11_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3278
PTOPMM_Faza2_Tok12_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3279
PTOPMM_Faza2_Tok13_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3280
PTOPMM_Faza2_Tok14_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3281
PTOPMM_Faza2_Tok15_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3282
PTOPMM_Faza2_Tok16_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3283
PTOPMM_Faza2_Tok17_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3284
PTOPMM_Faza2_Tok18_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3285
PTOPMM_Faza2_Tok19_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3286
PTOPMM_Faza2_Tok20_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3287
PTOPMM_Faza2_Tok21_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3288
PTOPMM_Faza2_Tok22_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3289
PTOPMM_Faza2_Tok23_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3290
PTOPMM_Faza2_Tok24_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3291
PTOPMM_Faza2_Tok25_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3292
PTOPMM_Faza2_Tok26_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3293
PTOPMM_Faza2_Tok27_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3294
PTOPMM_Faza2_Tok28_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3295
PTOPMM_Faza2_Tok29_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3296
PTOPMM_Faza2_Tok30_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3297
PTOPMM_Faza2_Tok31_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3298
PTOPMM_Faza2_Tok32_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3299
PTOPMM_Faza2_Tok33_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3300
PTOPMM_Faza2_Tok34_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3301
PTOPMM_Faza2_Tok35_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3302
PTOPMM_Faza2_Tok36_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3303
PTOPMM_Faza2_Tok37_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3304
PTOPMM_Faza2_Tok38_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3305
PTOPMM_Faza2_Tok39_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3306
PTOPMM_Faza2_Tok40_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3307
PTOPMM_Faza2_Tok41_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3308
PTOPMM_Faza2_Tok42_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3309
PTOPMM_Faza3_Tok01_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3310
PTOPMM_Faza3_Tok02_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3311
PTOPMM_Faza3_Tok03_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3312
PTOPMM_Faza3_Tok04_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3313
PTOPMM_Faza3_Tok05_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3314
PTOPMM_Faza3_Tok06_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3315
PTOPMM_Faza3_Tok07_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3316
PTOPMM_Faza3_Tok08_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3317
PTOPMM_Faza3_Tok09_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3318
PTOPMM_Faza3_Tok10_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3319
PTOPMM_Faza3_Tok11_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3320
PTOPMM_Faza3_Tok12_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3321
PTOPMM_Faza3_Tok13_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3322
PTOPMM_Faza3_Tok14_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3323
PTOPMM_Faza3_Tok15_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3324
PTOPMM_Faza3_Tok16_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3325
PTOPMM_Faza3_Tok17_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3326
PTOPMM_Faza3_Tok18_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3327
PTOPMM_Faza3_Tok19_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3328
PTOPMM_Faza3_Tok20_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3329
PTOPMM_Faza3_Tok21_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3330
PTOPMM_Faza3_Tok22_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3331
PTOPMM_Faza3_Tok23_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3332
PTOPMM_Faza3_Tok24_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3333
PTOPMM_Faza3_Tok25_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3334
PTOPMM_Faza3_Tok26_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3335
PTOPMM_Faza3_Tok27_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3336
PTOPMM_Faza3_Tok28_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3337
PTOPMM_Faza3_Tok29_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3338
PTOPMM_Faza3_Tok30_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3339
PTOPMM_Faza3_Tok31_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3340
PTOPMM_Faza3_Tok32_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3341
PTOPMM_Faza3_Tok33_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3342
PTOPMM_Faza3_Tok34_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3343
PTOPMM_Faza3_Tok35_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3344
PTOPMM_Faza3_Tok36_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3345
PTOPMM_Faza3_Tok37_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3346
PTOPMM_Faza3_Tok38_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3347
PTOPMM_Faza3_Tok39_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3348
PTOPMM_Faza3_Tok40_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3349
PTOPMM_Faza3_Tok41_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3350
PTOPMM_Faza3_Tok42_med60in80_Omogoci | DIGITAL | IOD_PTO_disk2 | D3351
PTOR1K5A2Q101odcepKS011izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3352
PTOR1K5A2Q102odcepKS021izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3353
PTOR1K5A2Q103odcepKS031izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3354
PTOR1K5A2Q104odcepKS041izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3355
PTOR1K5A2Q105odcepKS051izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3356
PTOR1K5A2Q106odcepKS061izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3357
PTOR1K5A2Q107odcusmSS2izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3358
PTOR1K5A2Q108odcusmSS3izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3359
PTOR1K5A2F201odcepKS012izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3360
PTOR1K5A2F202odcepKS022izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3361
PTOR1K5A2F203odcepKS032izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3362
PTOR1K5A2F204odcepKS042izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3363
PTOR1K5A2F205odcepKS052izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3364
PTOR1K5A2F206odcepKS053izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3365
PTOR1K5A2F207odcepKS062izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3366
PTOR1K5A1F208odcepKS063izpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3367
PTOR1K5A1Q11odcepUPSAizpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3368
PTOR1K5A1Q12odcbyUPSAizpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3369
PTOR1K5A1Q13odcmehbyAizpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3370
PTOR1K5UAQ11odcepPMMizpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3371
PTOR1K5UAQ12odcepPMMizpad_omogoci | DIGITAL | IOD_PTO_disk2 | D3372
PTOR1K5A2prenapetostna_omogoci | DIGITAL | IOD_PTO_disk2 | D3373
PTOR1K5A1prenapetostna_omogoci | DIGITAL | IOD_PTO_disk2 | D3374
PTOKlima1skupnanapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3375
PTOKlima2skupnanapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3376
PTOKlima3skupnanapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3377
PTOKlima4skupnanapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3378
PTOKlima5skupnanapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3379
PTOKlima6skupnanapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3380
PTOKlimasplitnapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3381
PTOUPSAvklopljenbypassDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3382
PTOUPSAsplosnanapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3383
PTOUPSBvklopljenbypassDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3384
PTOUPSBsplosnanapakaDI_omogoci | DIGITAL | IOD_PTO_disk2 | D3385
PTOR1K5CNSUPSzakrmnapaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3386
PTOR1K5CNSUPSzakrmtokizbaterije_omogoci | DIGITAL | IOD_PTO_disk2 | D3387
PTOR1K5CNSUPSzakrmpolnjenjebat_omogoci | DIGITAL | IOD_PTO_disk2 | D3388
PTOPLCnapakaprinastavljanjucasa_omogoci | DIGITAL | IOD_PTO_disk2 | D3389
PTOPLCslababaterijakrmilnikaXC200_omogoci | DIGITAL | IOD_PTO_disk2 | D3390
PTOTempvsersobi1previsoka_omogoci | DIGITAL | IOD_PTO_disk2 | D3391
PTOTempvsersobi2previsoka_omogoci | DIGITAL | IOD_PTO_disk2 | D3392
PTOTempvsersobi3previsoka_omogoci | DIGITAL | IOD_PTO_disk2 | D3393
PTOSenzortemperatureTH1napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3394
PTOSenzortemperatureTH2napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3395
PTOSenzortemperatureTH3napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3396
PTOSenzortemperatureTH4napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3397
PTOSenzortemperatureTH5napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3398
PTOSenzortemperatureTH6napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3399
PTOSenzorvlageTH1napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3400
PTOSenzorvlageTH2napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3401
PTOSenzorvlageTH3napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3402
PTOSenzorvlageTH4napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3403
PTOSenzorvlageTH5napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3404
PTOSenzorvlageTH6napaka_omogoci | DIGITAL | IOD_PTO_disk2 | D3405
PTORazlitjevodeLAH1klimaKS0102_omogoci | DIGITAL | IOD_PTO_disk2 | D3406
PTORazlitjevodeLAH2klimaKS0304_omogoci | DIGITAL | IOD_PTO_disk2 | D3407
PTORazlitjevodeLAH3klimaKS05_omogoci | DIGITAL | IOD_PTO_disk2 | D3408
PTORazlitjevodeLAH4klimaKS06_omogoci | DIGITAL | IOD_PTO_disk2 | D3409
PTO_UPS_A_napaka_razsmernika_omogoci | DIGITAL | IOD_PTO_disk2 | D3410
PTO_UPS_B_napaka_razsmernika_omogoci | DIGITAL | IOD_PTO_disk2 | D3411
PTOPMM_2x63_VirA_zavihek | DIGITAL | IOD_PTO_disk2 | D3412
PTOPMM_2x63_VirB_zavihek | DIGITAL | IOD_PTO_disk2 | D3413
PTOPMM_2x17_VirA_zavihek | DIGITAL | IOD_PTO_disk2 | D3414
PTOPMM_2x17_VirB_zavihek | DIGITAL | IOD_PTO_disk2 | D3415
PTOPMM1OverCurrentBetw1_Omogoci | DIGITAL | IOD_PTO_disk2 | D3416
PTOPMM1OverCurrentBetw2_Omogoci | DIGITAL | IOD_PTO_disk2 | D3417
PTOPMM1OverCurrentBetw3_Omogoci | DIGITAL | IOD_PTO_disk2 | D3418
PTOPMM1OverCurrentOver1_Omogoci | DIGITAL | IOD_PTO_disk2 | D3419
PTOPMM1OverCurrentOver2_Omogoci | DIGITAL | IOD_PTO_disk2 | D3420
PTOPMM1OverCurrentOver3_Omogoci | DIGITAL | IOD_PTO_disk2 | D3421
PTOPMM2OverCurrentBetw1_Omogoci | DIGITAL | IOD_PTO_disk2 | D3422
PTOPMM2OverCurrentBetw2_Omogoci | DIGITAL | IOD_PTO_disk2 | D3423
PTOPMM2OverCurrentBetw3_Omogoci | DIGITAL | IOD_PTO_disk2 | D3424
PTOPMM2OverCurrentOver1_Omogoci | DIGITAL | IOD_PTO_disk2 | D3425
PTOPMM2OverCurrentOver2_Omogoci | DIGITAL | IOD_PTO_disk2 | D3426
PTOPMM2OverCurrentOver3_Omogoci | DIGITAL | IOD_PTO_disk2 | D3427
PTOSKTemp1_Opozorilo_Zgornja_Meja | REAL | IOD_PTO_disk | R1 | 0 | 100 | 0 | 100 | % | ####.#
PTOSKTemp1_Alarm_Zgornja_Meja | REAL | IOD_PTO_disk | R2 | 0 | 60 | 0 | 60 | °C | ####.#
PTOSKTemp1_Opozorilo_Omogoci | DIGITAL | IOD_PTO_disk | D3819
PTOSKTemp1_Alarm_Omogoci | DIGITAL | IOD_PTO_disk | D3820
PTOSKVlaga1_Opozorilo_Zgornja_Meja | REAL | IOD_PTO_disk | R3 | 0 | 100 | 0 | 100 | % | ####.#
PTOSKVlaga1_Alarm_Zgornja_Meja | REAL | IOD_PTO_disk | R4 | 0 | 100 | 0 | 100 | % | ####.#
PTOSKVlaga1_Opozorilo_Omogoci | DIGITAL | IOD_PTO_disk | D3821
PTOSKVlaga1_Alarm_Omogoci | DIGITAL | IOD_PTO_disk | D3822
PTOSKTemp2_Opozorilo_Zgornja_Meja | REAL | IOD_PTO_disk | R5 | 0 | 100 | 0 | 100 | % | ####.#
PTOSKTemp2_Alarm_Zgornja_Meja | REAL | IOD_PTO_disk | R6 | 0 | 60 | 0 | 60 | °C | ####.#
PTOSKTemp2_Opozorilo_Omogoci | DIGITAL | IOD_PTO_disk | D3823
PTOSKTemp2_Alarm_Omogoci | DIGITAL | IOD_PTO_disk | D3824
PTOSKVlaga2_Opozorilo_Zgornja_Meja | REAL | IOD_PTO_disk | R7 | 0 | 100 | 0 | 100 | % | ####.#
PTOSKVlaga2_Alarm_Zgornja_Meja | REAL | IOD_PTO_disk | R8 | 0 | 100 | 0 | 100 | % | ####.#
PTOSKVlaga2_Opozorilo_Omogoci | DIGITAL | IOD_PTO_disk | D3825
PTOSKVlaga2_Alarm_Omogoci | DIGITAL | IOD_PTO_disk | D3826
PTOSKTemp3_Opozorilo_Zgornja_Meja | REAL | IOD_PTO_disk | R9 | 0 | 100 | 0 | 100 | % | ####.#
PTOSKTemp3_Alarm_Zgornja_Meja | REAL | IOD_PTO_disk | R10 | 0 | 60 | 0 | 60 | °C | ####.#
PTOSKTemp3_Opozorilo_Omogoci | DIGITAL | IOD_PTO_disk | D3827
PTOSKTemp3_Alarm_Omogoci | DIGITAL | IOD_PTO_disk | D3828
PTOSKVlaga3_Opozorilo_Zgornja_Meja | REAL | IOD_PTO_disk | R11 | 0 | 100 | 0 | 100 | % | ####.#
PTOSKVlaga3_Alarm_Zgornja_Meja | REAL | IOD_PTO_disk | R12 | 0 | 100 | 0 | 100 | % | ####.#
PTOSKVlaga3_Opozorilo_Omogoci | DIGITAL | IOD_PTO_disk | D3829
PTOSKVlaga3_Alarm_Omogoci | DIGITAL | IOD_PTO_disk | D3830
PTOSKTemp4_Opozorilo_Zgornja_Meja | REAL | IOD_PTO_disk | R13 | 0 | 100 | 0 | 100 | % | ####.#
PTOSKTemp4_Alarm_Zgornja_Meja | REAL | IOD_PTO_disk | R14 | 0 | 60 | 0 | 60 | °C | ####.#
PTOSKTemp4_Opozorilo_Omogoci | DIGITAL | IOD_PTO_disk | D3831
PTOSKTemp4_Alarm_Omogoci | DIGITAL | IOD_PTO_disk | D3832
PTOSKVlaga4_Opozorilo_Zgornja_Meja | REAL | IOD_PTO_disk | R15 | 0 | 100 | 0 | 100 | % | ####.#
PTOSKVlaga4_Alarm_Zgornja_Meja | REAL | IOD_PTO_disk | R16 | 0 | 100 | 0 | 100 | % | ####.#
PTOSKVlaga4_Opozorilo_Omogoci | DIGITAL | IOD_PTO_disk | D3833
PTOSKVlaga4_Alarm_Omogoci | DIGITAL | IOD_PTO_disk | D3834
PTOComSCADA_stevec | INT | IOD_PTO_disk | I3
PTOComSCADA_stevec1 | INT | IOD_PTO_disk | I4
Prikaz | DIGITAL | IOD_PTO_disk | D3836
PTOPMM2x63_VirA_Faza1_Med60in80 | REAL | IOD_PTO_disk | R30[21] | 0 | 16 | 0 | 16 | A | ####.#
PTOPMM2x63_VirB_Faza1_Med60in80 | REAL | IOD_PTO_disk | R60[21] | 0 | 16 | 0 | 16 | A | ####.#
PTOPMM2x63_VirA_Faza1_Nad80 | REAL | IOD_PTO_disk | R90[21] | 0 | 16 | 0 | 16 | A | ####.#
PTOPMM2x63_VirB_Faza1_Mad80 | REAL | IOD_PTO_disk | R120[21] | 0 | 16 | 0 | 16 | A | ####.#
PTOPMM2x63_VirA_Faza2_Med60in80 | REAL | IOD_PTO_disk | R150[21] | 0 | 16 | 0 | 16 | A | ####.#
PTOPMM2x63_VirB_Faza2_Med60in80 | REAL | IOD_PTO_disk | R180[21] | 0 | 16 | 0 | 16 | A | ####.#
PTOPMM2x63_VirA_Faza2_Nad80 | REAL | IOD_PTO_disk | R210[21] | 0 | 16 | 0 | 16 | A | ####.#
PTOPMM2x63_VirB_Faza2_Mad80 | REAL | IOD_PTO_disk | R240[21] | 0 | 16 | 0 | 16 | A | ####.#
PTOPMM2x63_VirA_Faza3_Med60in80 | REAL | IOD_PTO_disk | R270[21] | 0 | 16 | 0 | 16 | A | ####.#
PTOPMM2x63_VirB_Faza3_Med60in80 | REAL | IOD_PTO_disk | R300[21] | 0 | 16 | 0 | 16 | A | ####.#
PTOPMM2x63_VirA_Faza3_Nad80 | REAL | IOD_PTO_disk | R330[21] | 0 | 16 | 0 | 16 | A | ####.#
PTOPMM2x63_VirB_Faza3_Mad80 | REAL | IOD_PTO_disk | R360[21] | 0 | 16 | 0 | 16 | A | ####.#
PTOPMM1PoljeFazaATok1_16_nad80 | DIGITAL | IOD_PTO_disk2 | D3500[16]
PTOPMM1PoljeFazaATok17_32_nad80 | DIGITAL | IOD_PTO_disk2 | D3517[16]
PTOPMM1PoljeFazaATok33_42_nad80 | DIGITAL | IOD_PTO_disk2 | D3534[16]
PTOPMM1PoljeFazaBTok1_16_nad80 | DIGITAL | IOD_PTO_disk2 | D3551[16]
PTOPMM1PoljeFazaBTok17_32_nad80 | DIGITAL | IOD_PTO_disk2 | D3568[16]
PTOPMM1PoljeFazaBTok33_42_nad80 | DIGITAL | IOD_PTO_disk2 | D3585[16]
PTOPMM1PoljeFazaCTok1_16_nad80 | DIGITAL | IOD_PTO_disk2 | D3602[16]
PTOPMM1PoljeFazaCTok17_32_nad80 | DIGITAL | IOD_PTO_disk2 | D3619[16]
PTOPMM1PoljeFazaCTok33_42_nad80 | DIGITAL | IOD_PTO_disk2 | D3636[16]
PTOPMM1PoljeFazaATok1_16_med60_80 | DIGITAL | IOD_PTO_disk2 | D3653[16]
PTOPMM1PoljeFazaATok17_32_med60_80 | DIGITAL | IOD_PTO_disk2 | D3670[16]
PTOPMM1PoljeFazaATok33_42_med60_80 | DIGITAL | IOD_PTO_disk2 | D3687[16]
PTOPMM1PoljeFazaBTok1_16_med60_80 | DIGITAL | IOD_PTO_disk2 | D3704[16]
PTOPMM1PoljeFazaBTok17_32_med60_80 | DIGITAL | IOD_PTO_disk2 | D3721[16]
PTOPMM1PoljeFazaBTok33_42_med60_80 | DIGITAL | IOD_PTO_disk2 | D3738[16]
PTOPMM1PoljeFazaCTok1_16_med60_80 | DIGITAL | IOD_PTO_disk2 | D3755[16]
PTOPMM1PoljeFazaCTok17_32_med60_80 | DIGITAL | IOD_PTO_disk2 | D3772[16]
PTOPMM1PoljeFazaCTok33_42_med60_80 | DIGITAL | IOD_PTO_disk2 | D3789[16]
PTOPMM1OverCurrentBetw1_VirB_Omogoci | DIGITAL | IOD_PTO_disk2 | D3837
PTOPMM1OverCurrentBetw1_VirA_Omogoci | DIGITAL | IOD_PTO_disk2 | D3838
PTOPMM1OverCurrentBetw2_VirB_Omogoci | DIGITAL | IOD_PTO_disk2 | D3839
PTOPMM1OverCurrentBetw2_VirA_Omogoci | DIGITAL | IOD_PTO_disk2 | D3840
PTOPMM1OverCurrentBetw3_VirB_Omogoci | DIGITAL | IOD_PTO_disk2 | D3841
PTOPMM1OverCurrentBetw3_VirA_Omogoci | DIGITAL | IOD_PTO_disk2 | D3842
PTOPMM1OverCurrentBetw1_VirB | DIGITAL | IOD_PTO_disk2 | D3843
PTOPMM1OverCurrentBetw1_VirA | DIGITAL | IOD_PTO_disk2 | D3844
PTOPMM1OverCurrentBetw2_VirB | DIGITAL | IOD_PTO_disk2 | D3845
PTOPMM1OverCurrentBetw2_VirA | DIGITAL | IOD_PTO_disk2 | D3846
PTOPMM1OverCurrentBetw3_VirB | DIGITAL | IOD_PTO_disk2 | D3847
PTOPMM1OverCurrentBetw3_VirA | DIGITAL | IOD_PTO_disk2 | D3848
PTOPrikaz | DIGITAL | IOD_PTO_disk2 | D3849
PTOPMM1OverCurrentBetw1_VirB_1_2 | INT | IOD_PTO_disk | I5
PTOPMM1OverCurrentBetw1_VirA_1_2 | INT | IOD_PTO_disk | I6
PTOPMM1OverCurrentBetw1_VirB_2_2 | INT | IOD_PTO_disk | I7
PTOPMM1OverCurrentBetw1_VirA_2_2 | INT | IOD_PTO_disk | I8
PTOPMM1OverCurrentBetw2_VirB_1_2 | INT | IOD_PTO_disk | I9
PTOPMM1OverCurrentBetw2_VirA_1_2 | INT | IOD_PTO_disk | I10
PTOPMM1OverCurrentBetw2_VirB_2_2 | INT | IOD_PTO_disk | I11
PTOPMM1OverCurrentBetw2_VirA_2_2 | INT | IOD_PTO_disk | I12
PTOPMM1OverCurrentBetw3_VirB_1_2 | INT | IOD_PTO_disk | I13
PTOPMM1OverCurrentBetw3_VirA_1_2 | INT | IOD_PTO_disk | I14
PTOPMM1OverCurrentBetw3_VirB_2_2 | INT | IOD_PTO_disk | I15
PTOPMM1OverCurrentBetw3_VirA_2_2 | INT | IOD_PTO_disk | I16
PTOPMM1OverCurrentOver1_VirB_Omogoci | DIGITAL | IOD_PTO_disk | D3850
PTOPMM1OverCurrentOver1_VirA_Omogoci | DIGITAL | IOD_PTO_disk | D3851
PTOPMM1OverCurrentOver2_VirB_Omogoci | DIGITAL | IOD_PTO_disk | D3852
PTOPMM1OverCurrentOver2_VirA_Omogoci | DIGITAL | IOD_PTO_disk | D3853
PTOPMM1OverCurrentOver3_VirB_Omogoci | DIGITAL | IOD_PTO_disk | D3854
PTOPMM1OverCurrentOver3_VirA_Omogoci | DIGITAL | IOD_PTO_disk | D3855
PTOPMM1OverCurrentOver1_VirB | DIGITAL | IOD_PTO_disk | D3856
PTOPMM1OverCurrentOver1_VirA | DIGITAL | IOD_PTO_disk | D3857
PTOPMM1OverCurrentOver2_VirB | DIGITAL | IOD_PTO_disk | D3858
PTOPMM1OverCurrentOver2_VirA | DIGITAL | IOD_PTO_disk | D3859
PTOPMM1OverCurrentOver3_VirB | DIGITAL | IOD_PTO_disk | D3860
PTOPMM1OverCurrentOver3_VirA | DIGITAL | IOD_PTO_disk | D3861
PTOPMM1OverCurrentOver1_VirB_1_2 | INT | IOD_PTO_disk | I17
PTOPMM1OverCurrentOver1_VirA_1_2 | INT | IOD_PTO_disk | I18
PTOPMM1OverCurrentOver1_VirB_2_2 | INT | IOD_PTO_disk | I19
PTOPMM1OverCurrentOver1_VirA_2_2 | INT | IOD_PTO_disk | I20
PTOPMM1OverCurrentOver2_VirB_1_2 | INT | IOD_PTO_disk | I21
PTOPMM1OverCurrentOver2_VirA_1_2 | INT | IOD_PTO_disk | I22
PTOPMM1OverCurrentOver2_VirB_2_2 | INT | IOD_PTO_disk | I23
PTOPMM1OverCurrentOver2_VirA_2_2 | INT | IOD_PTO_disk | I24
PTOPMM1OverCurrentOver3_VirB_1_2 | INT | IOD_PTO_disk | I25
PTOPMM1OverCurrentOver3_VirA_1_2 | INT | IOD_PTO_disk | I26
PTOPMM1OverCurrentOver3_VirB_2_2 | INT | IOD_PTO_disk | I27
PTOPMM1OverCurrentOver3_VirA_2_2 | INT | IOD_PTO_disk | I28
PTOOmogociVseAlarme | DIGITAL | IOD_PTO_disk | D3862
PTOOmogociVseSMSAlarme | DIGITAL | IOD_PTO_disk | D3863
PTOOmogociVseDogodke_DO | DIGITAL | IOD_PTO_disk | D3864
PTOOmogociVseDogodke_DI | DIGITAL | IOD_PTO_disk | D3865
PTOOmogociVseDogodke_COM | DIGITAL | IOD_PTO_disk | D3866
PTORazlikaUr | REAL | IOD_PTO_TCP | 44823
PTOPMMOverCurrentOver1A_omogoci | DIGITAL | IOD_PTO_disk | D3867
PTOPMMOverCurrentOver2A_omogoci | DIGITAL | IOD_PTO_disk | D3868
PTOPMMOverCurrentOver3A_omogoci | DIGITAL | IOD_PTO_disk | D3869
PTO_DI_A1Q02_IZKLJUCENO_omogoci | DIGITAL | IOD_PTO_disk | D3870
PTO_DI_A1Q12_IZKLJUCENO_omogoci | DIGITAL | IOD_PTO_disk | D3873
PTO_DI_A1Q02_VKLJUCENO_omogoci | DIGITAL | IOD_PTO_disk | D3874
PTO_DI_A1Q12_VKLJUCENO_omogoci | DIGITAL | IOD_PTO_disk | D3875
NOT_PTODI_A2Q0_GlavnoSti_ON_omogoci | DIGITAL | IOD_PTO_disk | D3876
NOT_PTODI_Q101_OdcKlima1_ON_omogoci | DIGITAL | IOD_PTO_disk | D3877
NOT_PTODI_Q102_OdcKlima2_ON_omogoci | DIGITAL | IOD_PTO_disk | D3878
NOT_PTODI_Q103_OdcKlima3_ON_omogoci | DIGITAL | IOD_PTO_disk | D3879
NOT_PTODI_Q104_OdcKlima4_ON_omogoci | DIGITAL | IOD_PTO_disk | D3880
NOT_PTODI_Q105_OdcKlima5_ON_omogoci | DIGITAL | IOD_PTO_disk | D3881
NOT_PTODI_Q106_OdcKlima6_ON_omogoci | DIGITAL | IOD_PTO_disk | D3882
NOT_PTODI_Q107_OdcUsmSS2_ON_omogoci | DIGITAL | IOD_PTO_disk | D3883
NOT_PTODI_Q108_OdcUsmSS3_ON_omogoci | DIGITAL | IOD_PTO_disk | D3884
NOT_PTODI_F201_OdcKl1ZE_ON_omogoci | DIGITAL | IOD_PTO_disk | D3885
NOT_PTODI_F202_OdcKl2ZE_ON_omogoci | DIGITAL | IOD_PTO_disk | D3886
NOT_PTODI_F203_OdcKl3ZE_ON_omogoci | DIGITAL | IOD_PTO_disk | D3887
NOT_PTODI_F204_OdcKl4ZE_ON_omogoci | DIGITAL | IOD_PTO_disk | D3888
NOT_PTODI_F205_OdcKl5aZE_ON_omogoci | DIGITAL | IOD_PTO_disk | D3889
NOT_PTODI_F206_OdcKl5bZE_ON_omogoci | DIGITAL | IOD_PTO_disk | D3890
NOT_PTODI_F207_OdcKl6aZE_ON_omogoci | DIGITAL | IOD_PTO_disk | D3891
NOT_PTODI_F208_OdcKl6bZE_ON_omogoci | DIGITAL | IOD_PTO_disk | D3892
NOT_PTODI_A1Q0_GlavnoSti_ON_omogoci | DIGITAL | IOD_PTO_disk | D3893
NOT_PTODI_A1Q11_OdcUpsA_ON_omogoci | DIGITAL | IOD_PTO_disk | D3894
NOT_PTODI_A1Q12_OdcByUpsA_ON_omogoci | DIGITAL | IOD_PTO_disk | D3895
NOT_PTODI_A1Q13_OdcByA_ON_omogoci | DIGITAL | IOD_PTO_disk | D3896
NOT_PTODI_A1Q01_DovUpsA_ON_omogoci | DIGITAL | IOD_PTO_disk | D3897
PTODI_A1Q02_DovByA_ON_omogoci | DIGITAL | IOD_PTO_disk | D3898
NOT_PTODI_UQ11_OdcPMM_ON_omogoci | DIGITAL | IOD_PTO_disk | D3899
NOT_PTODI_UQ12_OdcPMM_ON_omogoci | DIGITAL | IOD_PTO_disk | D3900
PTODI_Klima1_ON_omogoci | DIGITAL | IOD_PTO_disk | D3901
PTODI_Klima2_ON_omogoci | DIGITAL | IOD_PTO_disk | D3902
PTODI_Klima3_ON_omogoci | DIGITAL | IOD_PTO_disk | D3903
PTODI_Klima4_ON_omogoci | DIGITAL | IOD_PTO_disk | D3904
PTODI_Klima5_ON_omogoci | DIGITAL | IOD_PTO_disk | D3905
PTODI_Klima6_ON_omogoci | DIGITAL | IOD_PTO_disk | D3906 | [6 empty] | 6157 | 1
PTODIN_A1Q11_OdcUpsB_IZP | DIGITAL | IOD_PTO_TCP | 00688
PTODIN_A1Q12_OdcByUpsB_IZP | DIGITAL | IOD_PTO_TCP | 00689
PTODIN_A1Q13_OdcByB_IZP | DIGITAL | IOD_PTO_TCP | 00690
PTODIN_UQ11_OdcPMMB_IZP | DIGITAL | IOD_PTO_TCP | 00691
PTODIN_UQ12_OdcPMMB_IZP | DIGITAL | IOD_PTO_TCP | 00692
PTODIN_PrenapA3_OK | DIGITAL | IOD_PTO_TCP | 00693
A1Q11_OdcUpsB_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3907
A1Q12_OdcByUpsB_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3908
A1Q13_OdcByB_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3909
UQ11_OdcPMMB_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3910
UQ12_OdcPMMB_IZP_omogoci | DIGITAL | IOD_PTO_disk | D3911
PrenapA3_OK_omogoci | DIGITAL | IOD_PTO_disk | D3912
PTODIN_A1Q0_GlavnoStiB_ON | DIGITAL | IOD_PTO_TCP | 00694
PTODIN_A1Q11_OdcUpsB_ON | DIGITAL | IOD_PTO_TCP | 00695
PTODIN_A1Q12_OdcByUpsB_ON | DIGITAL | IOD_PTO_TCP | 00696
PTODI_A1Q13_OdcByB_ON | DIGITAL | IOD_PTO_TCP | 00697
PTODIN_A1Q01_DovUpsB_ON | DIGITAL | IOD_PTO_TCP | 00698
PTODI_A1Q02_DovByB_ON | DIGITAL | IOD_PTO_TCP | 00699
PTODIN_UQ11_OdcPMMB_ON | DIGITAL | IOD_PTO_TCP | 00700
PTODI_UQ12_OdcPMMB_ON | DIGITAL | IOD_PTO_TCP | 00701
PTODIN_A1Q0_GlavnoStiB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3913
PTODIN_A1Q11_OdcUpsB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3914
PTODIN_A1Q12_OdcByUpsB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3915
PTODI_A1Q13_OdcByB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3916
PTODIN_A1Q01_DovUpsB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3917
PTODI_A1Q02_DovByB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3918
PTODIN_UQ11_OdcPMMB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3919
PTODI_UQ12_OdcPMMB_ON_omogoci | DIGITAL | IOD_PTO_disk | D3920
PTOKlima1NapacnoGesloAlarm | DIGITAL | IOD_PTO_TCP | 00702
PTOKlima1ExtTempHumAlarm | DIGITAL | IOD_PTO_TCP | 00703
PTOKlima1PoplavniAlarm | DIGITAL | IOD_PTO_TCP | 00704
PTOKlima1VisokPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 00705
PTOKlima1VisokPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 00706
PTOKlima1ElVentilKompresor1ERR | DIGITAL | IOD_PTO_TCP | 00707
PTOKlima1ElVentilKompresor2ERR | DIGITAL | IOD_PTO_TCP | 00708
PTOKlima1WrongPhaseSeqAlarm | DIGITAL | IOD_PTO_TCP | 00709
PTOKlima1PrekinjenLANalarm | DIGITAL | IOD_PTO_TCP | 00710
PTOKlima1CWTempHighForDehum | DIGITAL | IOD_PTO_TCP | 00711
PTOKlima1CWVentilErrOrLowFlow | DIGITAL | IOD_PTO_TCP | 00712
PTOKlima1NapakaPriPretokuVode | DIGITAL | IOD_PTO_TCP | 00713
PTOKlima1CWhighTemp | DIGITAL | IOD_PTO_TCP | 00714
PTOKlima1NapakaSenzorHotWTemp | DIGITAL | IOD_PTO_TCP | 00715
PTOKlima1NapakaSenzorCondWTemp | DIGITAL | IOD_PTO_TCP | 00716
PTOKlima1NapakaSenzorCW | DIGITAL | IOD_PTO_TCP | 00717
PTOKlima1Kompresor3naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00718
PTOKlima1Kompresor4naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00719
PTOKlima1ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00720
PTOKlima1Grelec1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00721
PTOKlima1Grelec2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00722
PTOKlima1VlazilecNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00723
PTOKlima1AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00724
PTOKlima1DigIn2Alarm | DIGITAL | IOD_PTO_TCP | 00725
PTOKlima1DigIn4Alarm | DIGITAL | IOD_PTO_TCP | 00726
PTOKlima1DigIn6Alarm | DIGITAL | IOD_PTO_TCP | 00727
PTOKlima1VlazilecGenAlarm | DIGITAL | IOD_PTO_TCP | 00728
PTOKlima1General2ndLevAlarm | DIGITAL | IOD_PTO_TCP | 00729
PTOKlima1UnitOnRotAlarm | DIGITAL | IOD_PTO_TCP | 00730
PTOKlima1UnitOnAlarmA | DIGITAL | IOD_PTO_TCP | 00731
PTOKlima1UnitOnAlarmB | DIGITAL | IOD_PTO_TCP | 00732
PTOKlima1UnitOnAlarmC | DIGITAL | IOD_PTO_TCP | 00733
PTOKlima2NapacnoGesloAlarm | DIGITAL | IOD_PTO_TCP | 00734
PTOKlima2ExtTempHumAlarm | DIGITAL | IOD_PTO_TCP | 00735
PTOKlima2PoplavniAlarm | DIGITAL | IOD_PTO_TCP | 00736
PTOKlima2VisokPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 00737
PTOKlima2VisokPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 00738
PTOKlima2ElVentilKompresor1ERR | DIGITAL | IOD_PTO_TCP | 00739
PTOKlima2ElVentilKompresor2ERR | DIGITAL | IOD_PTO_TCP | 00740
PTOKlima2WrongPhaseSeqAlarm | DIGITAL | IOD_PTO_TCP | 00741
PTOKlima2PrekinjenLANalarm | DIGITAL | IOD_PTO_TCP | 00742
PTOKlima2CWTempHighForDehum | DIGITAL | IOD_PTO_TCP | 00743
PTOKlima2CWVentilErrOrLowFlow | DIGITAL | IOD_PTO_TCP | 00744
PTOKlima2NapakaPriPretokuVode | DIGITAL | IOD_PTO_TCP | 00745
PTOKlima2CWhighTemp | DIGITAL | IOD_PTO_TCP | 00746
PTOKlima2NapakaSenzorHotWTemp | DIGITAL | IOD_PTO_TCP | 00747
PTOKlima2NapakaSenzorCondWTemp | DIGITAL | IOD_PTO_TCP | 00748
PTOKlima2NapakaSenzorCW | DIGITAL | IOD_PTO_TCP | 00749
PTOKlima2Kompresor3naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00750
PTOKlima2Kompresor4naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00751
PTOKlima2ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00752
PTOKlima2Grelec1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00753
PTOKlima2Grelec2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00754
PTOKlima2VlazilecNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00755
PTOKlima2AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00756
PTOKlima2DigIn2Alarm | DIGITAL | IOD_PTO_TCP | 00757
PTOKlima2DigIn4Alarm | DIGITAL | IOD_PTO_TCP | 00758
PTOKlima2DigIn6Alarm | DIGITAL | IOD_PTO_TCP | 00759
PTOKlima2VlazilecGenAlarm | DIGITAL | IOD_PTO_TCP | 00760
PTOKlima2General2ndLevAlarm | DIGITAL | IOD_PTO_TCP | 00761
PTOKlima2UnitOnRotAlarm | DIGITAL | IOD_PTO_TCP | 00762
PTOKlima2UnitOnAlarmA | DIGITAL | IOD_PTO_TCP | 00763
PTOKlima2UnitOnAlarmB | DIGITAL | IOD_PTO_TCP | 00764
PTOKlima2UnitOnAlarmC | DIGITAL | IOD_PTO_TCP | 00765
PTOKlima3NapacnoGesloAlarm | DIGITAL | IOD_PTO_TCP | 00766
PTOKlima3ExtTempHumAlarm | DIGITAL | IOD_PTO_TCP | 00767
PTOKlima3PoplavniAlarm | DIGITAL | IOD_PTO_TCP | 00768
PTOKlima3VisokPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 00769
PTOKlima3VisokPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 00770
PTOKlima3ElVentilKompresor1ERR | DIGITAL | IOD_PTO_TCP | 00771
PTOKlima3ElVentilKompresor2ERR | DIGITAL | IOD_PTO_TCP | 00772
PTOKlima3WrongPhaseSeqAlarm | DIGITAL | IOD_PTO_TCP | 00773
PTOKlima3PrekinjenLANalarm | DIGITAL | IOD_PTO_TCP | 00774
PTOKlima3CWTempHighForDehum | DIGITAL | IOD_PTO_TCP | 00775
PTOKlima3CWVentilErrOrLowFlow | DIGITAL | IOD_PTO_TCP | 00776
PTOKlima3NapakaPriPretokuVode | DIGITAL | IOD_PTO_TCP | 00777
PTOKlima3CWhighTemp | DIGITAL | IOD_PTO_TCP | 00778
PTOKlima3NapakaSenzorHotWTemp | DIGITAL | IOD_PTO_TCP | 00779
PTOKlima3NapakaSenzorCondWTemp | DIGITAL | IOD_PTO_TCP | 00780
PTOKlima3NapakaSenzorCW | DIGITAL | IOD_PTO_TCP | 00781
PTOKlima3Kompresor3naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00782
PTOKlima3Kompresor4naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00783
PTOKlima3ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00784
PTOKlima3Grelec1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00785
PTOKlima3Grelec2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00786
PTOKlima3VlazilecNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00787
PTOKlima3AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00788
PTOKlima3DigIn2Alarm | DIGITAL | IOD_PTO_TCP | 00789
PTOKlima3DigIn4Alarm | DIGITAL | IOD_PTO_TCP | 00790
PTOKlima3DigIn6Alarm | DIGITAL | IOD_PTO_TCP | 00791
PTOKlima3VlazilecGenAlarm | DIGITAL | IOD_PTO_TCP | 00792
PTOKlima3General2ndLevAlarm | DIGITAL | IOD_PTO_TCP | 00793
PTOKlima3UnitOnRotAlarm | DIGITAL | IOD_PTO_TCP | 00794
PTOKlima3UnitOnAlarmA | DIGITAL | IOD_PTO_TCP | 00795
PTOKlima3UnitOnAlarmB | DIGITAL | IOD_PTO_TCP | 00796
PTOKlima3UnitOnAlarmC | DIGITAL | IOD_PTO_TCP | 00797
PTOKlima4NapacnoGesloAlarm | DIGITAL | IOD_PTO_TCP | 00798
PTOKlima4ExtTempHumAlarm | DIGITAL | IOD_PTO_TCP | 00799
PTOKlima4PoplavniAlarm | DIGITAL | IOD_PTO_TCP | 00800
PTOKlima4VisokPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 00801
PTOKlima4VisokPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 00802
PTOKlima4ElVentilKompresor1ERR | DIGITAL | IOD_PTO_TCP | 00803
PTOKlima4ElVentilKompresor2ERR | DIGITAL | IOD_PTO_TCP | 00804
PTOKlima4WrongPhaseSeqAlarm | DIGITAL | IOD_PTO_TCP | 00805
PTOKlima4PrekinjenLANalarm | DIGITAL | IOD_PTO_TCP | 00806
PTOKlima4CWTempHighForDehum | DIGITAL | IOD_PTO_TCP | 00807
PTOKlima4CWVentilErrOrLowFlow | DIGITAL | IOD_PTO_TCP | 00808
PTOKlima4NapakaPriPretokuVode | DIGITAL | IOD_PTO_TCP | 00809
PTOKlima4CWhighTemp | DIGITAL | IOD_PTO_TCP | 00810
PTOKlima4NapakaSenzorHotWTemp | DIGITAL | IOD_PTO_TCP | 00811
PTOKlima4NapakaSenzorCondWTemp | DIGITAL | IOD_PTO_TCP | 00812
PTOKlima4NapakaSenzorCW | DIGITAL | IOD_PTO_TCP | 00813
PTOKlima4Kompresor3naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00814
PTOKlima4Kompresor4naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00815
PTOKlima4ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00816
PTOKlima4Grelec1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00817
PTOKlima4Grelec2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00818
PTOKlima4VlazilecNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00819
PTOKlima4AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00820
PTOKlima4DigIn2Alarm | DIGITAL | IOD_PTO_TCP | 00821
PTOKlima4DigIn4Alarm | DIGITAL | IOD_PTO_TCP | 00822
PTOKlima4DigIn6Alarm | DIGITAL | IOD_PTO_TCP | 00823
PTOKlima4VlazilecGenAlarm | DIGITAL | IOD_PTO_TCP | 00824
PTOKlima4General2ndLevAlarm | DIGITAL | IOD_PTO_TCP | 00825
PTOKlima4UnitOnRotAlarm | DIGITAL | IOD_PTO_TCP | 00826
PTOKlima4UnitOnAlarmA | DIGITAL | IOD_PTO_TCP | 00827
PTOKlima4UnitOnAlarmB | DIGITAL | IOD_PTO_TCP | 00828
PTOKlima4UnitOnAlarmC | DIGITAL | IOD_PTO_TCP | 00829
PTOKlima5NapacnoGesloAlarm | DIGITAL | IOD_PTO_TCP | 00830
PTOKlima5ExtTempHumAlarm | DIGITAL | IOD_PTO_TCP | 00831
PTOKlima5PoplavniAlarm | DIGITAL | IOD_PTO_TCP | 00832
PTOKlima5VisokPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 00833
PTOKlima5VisokPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 00834
PTOKlima5ElVentilKompresor1ERR | DIGITAL | IOD_PTO_TCP | 00835
PTOKlima5ElVentilKompresor2ERR | DIGITAL | IOD_PTO_TCP | 00836
PTOKlima5WrongPhaseSeqAlarm | DIGITAL | IOD_PTO_TCP | 00837
PTOKlima5PrekinjenLANalarm | DIGITAL | IOD_PTO_TCP | 00838
PTOKlima5CWTempHighForDehum | DIGITAL | IOD_PTO_TCP | 00839
PTOKlima5CWVentilErrOrLowFlow | DIGITAL | IOD_PTO_TCP | 00840
PTOKlima5NapakaPriPretokuVode | DIGITAL | IOD_PTO_TCP | 00841
PTOKlima5CWhighTemp | DIGITAL | IOD_PTO_TCP | 00842
PTOKlima5NapakaSenzorHotWTemp | DIGITAL | IOD_PTO_TCP | 00843
PTOKlima5NapakaSenzorCondWTemp | DIGITAL | IOD_PTO_TCP | 00844
PTOKlima5NapakaSenzorCW | DIGITAL | IOD_PTO_TCP | 00845
PTOKlima5Kompresor3naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00846
PTOKlima5Kompresor4naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00847
PTOKlima5ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00848
PTOKlima5Grelec1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00849
PTOKlima5Grelec2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00850
PTOKlima5VlazilecNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00851
PTOKlima5AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00852
PTOKlima5DigIn2Alarm | DIGITAL | IOD_PTO_TCP | 00853
PTOKlima5DigIn4Alarm | DIGITAL | IOD_PTO_TCP | 00854
PTOKlima5DigIn6Alarm | DIGITAL | IOD_PTO_TCP | 00855
PTOKlima5VlazilecGenAlarm | DIGITAL | IOD_PTO_TCP | 00856
PTOKlima5General2ndLevAlarm | DIGITAL | IOD_PTO_TCP | 00857
PTOKlima5UnitOnRotAlarm | DIGITAL | IOD_PTO_TCP | 00858
PTOKlima5UnitOnAlarmA | DIGITAL | IOD_PTO_TCP | 00859
PTOKlima5UnitOnAlarmB | DIGITAL | IOD_PTO_TCP | 00860
PTOKlima5UnitOnAlarmC | DIGITAL | IOD_PTO_TCP | 00861
PTOKlima6NapacnoGesloAlarm | DIGITAL | IOD_PTO_TCP | 00862
PTOKlima6ExtTempHumAlarm | DIGITAL | IOD_PTO_TCP | 00863
PTOKlima6PoplavniAlarm | DIGITAL | IOD_PTO_TCP | 00864
PTOKlima6VisokPritiskKompresor1 | DIGITAL | IOD_PTO_TCP | 00865
PTOKlima6VisokPritiskKompresor2 | DIGITAL | IOD_PTO_TCP | 00866
PTOKlima6ElVentilKompresor1ERR | DIGITAL | IOD_PTO_TCP | 00867
PTOKlima6ElVentilKompresor2ERR | DIGITAL | IOD_PTO_TCP | 00868
PTOKlima6WrongPhaseSeqAlarm | DIGITAL | IOD_PTO_TCP | 00869
PTOKlima6PrekinjenLANalarm | DIGITAL | IOD_PTO_TCP | 00870
PTOKlima6CWTempHighForDehum | DIGITAL | IOD_PTO_TCP | 00871
PTOKlima6CWVentilErrOrLowFlow | DIGITAL | IOD_PTO_TCP | 00872
PTOKlima6NapakaPriPretokuVode | DIGITAL | IOD_PTO_TCP | 00873
PTOKlima6CWhighTemp | DIGITAL | IOD_PTO_TCP | 00874
PTOKlima6NapakaSenzorHotWTemp | DIGITAL | IOD_PTO_TCP | 00875
PTOKlima6NapakaSenzorCondWTemp | DIGITAL | IOD_PTO_TCP | 00876
PTOKlima6NapakaSenzorCW | DIGITAL | IOD_PTO_TCP | 00877
PTOKlima6Kompresor3naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00878
PTOKlima6Kompresor4naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00879
PTOKlima6ZracniFilterNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00880
PTOKlima6Grelec1naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00881
PTOKlima6Grelec2naMejiObrUr | DIGITAL | IOD_PTO_TCP | 00882
PTOKlima6VlazilecNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00883
PTOKlima6AirCondUnitNaMejiObrUr | DIGITAL | IOD_PTO_TCP | 00884
PTOKlima6DigIn2Alarm | DIGITAL | IOD_PTO_TCP | 00885
PTOKlima6DigIn4Alarm | DIGITAL | IOD_PTO_TCP | 00886
PTOKlima6DigIn6Alarm | DIGITAL | IOD_PTO_TCP | 00887
PTOKlima6VlazilecGenAlarm | DIGITAL | IOD_PTO_TCP | 00888
PTOKlima6General2ndLevAlarm | DIGITAL | IOD_PTO_TCP | 00889
PTOKlima6UnitOnRotAlarm | DIGITAL | IOD_PTO_TCP | 00890
PTOKlima6UnitOnAlarmA | DIGITAL | IOD_PTO_TCP | 00891
PTOKlima6UnitOnAlarmB | DIGITAL | IOD_PTO_TCP | 00892
PTOKlima6UnitOnAlarmC | DIGITAL | IOD_PTO_TCP | 00893
PTOKlima1NapacnoGesloAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3850
PTOKlima1ExtTempHumAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3851
PTOKlima1PoplavniAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3852
PTOKlima1VisokPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk2 | D3853
PTOKlima1VisokPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk2 | D3854
PTOKlima1ElVentilKompresor1ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3855
PTOKlima1ElVentilKompresor2ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3856
PTOKlima1WrongPhaseSeqAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3857
PTOKlima1PrekinjenLANalarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3858
PTOKlima1CWTempHighForDehum_omogoci | DIGITAL | IOD_PTO_disk2 | D3859
PTOKlima1CWVentilErrOrLowFlow_omogoci | DIGITAL | IOD_PTO_disk2 | D3860
PTOKlima1NapakaPriPretokuVode_omogoci | DIGITAL | IOD_PTO_disk2 | D3861
PTOKlima1CWhighTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3862
PTOKlima1NapakaSenzorHotWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3863
PTOKlima1NapakaSenzorCondWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3864
PTOKlima1NapakaSenzorCW_omogoci | DIGITAL | IOD_PTO_disk2 | D3865
PTOKlima1Kompresor3naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3866
PTOKlima1Kompresor4naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3867
PTOKlima1ZracniFilterNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3868
PTOKlima1Grelec1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3869
PTOKlima1Grelec2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3870
PTOKlima1VlazilecNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3871
PTOKlima1AirCondUnitNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3872
PTOKlima1DigIn2Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3873
PTOKlima1DigIn4Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3874
PTOKlima1DigIn6Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3875
PTOKlima1VlazilecGenAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3876
PTOKlima1General2ndLevAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3877
PTOKlima1UnitOnRotAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3878
PTOKlima1UnitOnAlarmA_omogoci | DIGITAL | IOD_PTO_disk2 | D3879
PTOKlima1UnitOnAlarmB_omogoci | DIGITAL | IOD_PTO_disk2 | D3880
PTOKlima1UnitOnAlarmC_omogoci | DIGITAL | IOD_PTO_disk2 | D3881
PTOKlima2NapacnoGesloAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3882
PTOKlima2ExtTempHumAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3883
PTOKlima2PoplavniAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3884
PTOKlima2VisokPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk2 | D3885
PTOKlima2VisokPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk2 | D3886
PTOKlima2ElVentilKompresor1ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3887
PTOKlima2ElVentilKompresor2ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3888
PTOKlima2WrongPhaseSeqAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3889
PTOKlima2PrekinjenLANalarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3890
PTOKlima2CWTempHighForDehum_omogoci | DIGITAL | IOD_PTO_disk2 | D3891
PTOKlima2CWVentilErrOrLowFlow_omogoci | DIGITAL | IOD_PTO_disk2 | D3892
PTOKlima2NapakaPriPretokuVode_omogoci | DIGITAL | IOD_PTO_disk2 | D3893
PTOKlima2CWhighTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3894
PTOKlima2NapakaSenzorHotWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3895
PTOKlima2NapakaSenzorCondWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3896
PTOKlima2NapakaSenzorCW_omogoci | DIGITAL | IOD_PTO_disk2 | D3897
PTOKlima2Kompresor3naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3898
PTOKlima2Kompresor4naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3899
PTOKlima2ZracniFilterNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3900
PTOKlima2Grelec1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3901
PTOKlima2Grelec2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3902
PTOKlima2VlazilecNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3903
PTOKlima2AirCondUnitNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3904
PTOKlima2DigIn2Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3905
PTOKlima2DigIn4Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3906
PTOKlima2DigIn6Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3907
PTOKlima2VlazilecGenAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3908
PTOKlima2General2ndLevAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3909
PTOKlima2UnitOnRotAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3910
PTOKlima2UnitOnAlarmA_omogoci | DIGITAL | IOD_PTO_disk2 | D3911
PTOKlima2UnitOnAlarmB_omogoci | DIGITAL | IOD_PTO_disk2 | D3912
PTOKlima2UnitOnAlarmC_omogoci | DIGITAL | IOD_PTO_disk2 | D3913
PTOKlima3NapacnoGesloAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3914
PTOKlima3ExtTempHumAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3915
PTOKlima3PoplavniAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3916
PTOKlima3VisokPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk2 | D3917
PTOKlima3VisokPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk2 | D3918
PTOKlima3ElVentilKompresor1ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3919
PTOKlima3ElVentilKompresor2ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3920
PTOKlima3WrongPhaseSeqAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3921
PTOKlima3PrekinjenLANalarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3922
PTOKlima3CWTempHighForDehum_omogoci | DIGITAL | IOD_PTO_disk2 | D3923
PTOKlima3CWVentilErrOrLowFlow_omogoci | DIGITAL | IOD_PTO_disk2 | D3924
PTOKlima3NapakaPriPretokuVode_omogoci | DIGITAL | IOD_PTO_disk2 | D3925
PTOKlima3CWhighTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3926
PTOKlima3NapakaSenzorHotWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3927
PTOKlima3NapakaSenzorCondWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3928
PTOKlima3NapakaSenzorCW_omogoci | DIGITAL | IOD_PTO_disk2 | D3929
PTOKlima3Kompresor3naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3930
PTOKlima3Kompresor4naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3931
PTOKlima3ZracniFilterNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3932
PTOKlima3Grelec1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3933
PTOKlima3Grelec2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3934
PTOKlima3VlazilecNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3935
PTOKlima3AirCondUnitNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3936
PTOKlima3DigIn2Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3937
PTOKlima3DigIn4Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3938
PTOKlima3DigIn6Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3939
PTOKlima3VlazilecGenAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3940
PTOKlima3General2ndLevAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3941
PTOKlima3UnitOnRotAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3942
PTOKlima3UnitOnAlarmA_omogoci | DIGITAL | IOD_PTO_disk2 | D3943
PTOKlima3UnitOnAlarmB_omogoci | DIGITAL | IOD_PTO_disk2 | D3944
PTOKlima3UnitOnAlarmC_omogoci | DIGITAL | IOD_PTO_disk2 | D3945
PTOKlima4NapacnoGesloAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3946
PTOKlima4ExtTempHumAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3947
PTOKlima4PoplavniAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3948
PTOKlima4VisokPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk2 | D3949
PTOKlima4VisokPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk2 | D3950
PTOKlima4ElVentilKompresor1ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3951
PTOKlima4ElVentilKompresor2ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3952
PTOKlima4WrongPhaseSeqAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3953
PTOKlima4PrekinjenLANalarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3954
PTOKlima4CWTempHighForDehum_omogoci | DIGITAL | IOD_PTO_disk2 | D3955
PTOKlima4CWVentilErrOrLowFlow_omogoci | DIGITAL | IOD_PTO_disk2 | D3956
PTOKlima4NapakaPriPretokuVode_omogoci | DIGITAL | IOD_PTO_disk2 | D3957
PTOKlima4CWhighTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3958
PTOKlima4NapakaSenzorHotWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3959
PTOKlima4NapakaSenzorCondWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3960
PTOKlima4NapakaSenzorCW_omogoci | DIGITAL | IOD_PTO_disk2 | D3961
PTOKlima4Kompresor3naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3962
PTOKlima4Kompresor4naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3963
PTOKlima4ZracniFilterNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3964
PTOKlima4Grelec1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3965
PTOKlima4Grelec2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3966
PTOKlima4VlazilecNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3967
PTOKlima4AirCondUnitNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3968
PTOKlima4DigIn2Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3969
PTOKlima4DigIn4Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3970
PTOKlima4DigIn6Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3971
PTOKlima4VlazilecGenAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3972
PTOKlima4General2ndLevAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3973
PTOKlima4UnitOnRotAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3974
PTOKlima4UnitOnAlarmA_omogoci | DIGITAL | IOD_PTO_disk2 | D3975
PTOKlima4UnitOnAlarmB_omogoci | DIGITAL | IOD_PTO_disk2 | D3976
PTOKlima4UnitOnAlarmC_omogoci | DIGITAL | IOD_PTO_disk2 | D3977
PTOKlima5NapacnoGesloAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3978
PTOKlima5ExtTempHumAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3979
PTOKlima5PoplavniAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3980
PTOKlima5VisokPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk2 | D3981
PTOKlima5VisokPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk2 | D3982
PTOKlima5ElVentilKompresor1ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3983
PTOKlima5ElVentilKompresor2ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D3984
PTOKlima5WrongPhaseSeqAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3985
PTOKlima5PrekinjenLANalarm_omogoci | DIGITAL | IOD_PTO_disk2 | D3986
PTOKlima5CWTempHighForDehum_omogoci | DIGITAL | IOD_PTO_disk2 | D3987
PTOKlima5CWVentilErrOrLowFlow_omogoci | DIGITAL | IOD_PTO_disk2 | D3988
PTOKlima5NapakaPriPretokuVode_omogoci | DIGITAL | IOD_PTO_disk2 | D3989
PTOKlima5CWhighTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3990
PTOKlima5NapakaSenzorHotWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3991
PTOKlima5NapakaSenzorCondWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D3992
PTOKlima5NapakaSenzorCW_omogoci | DIGITAL | IOD_PTO_disk2 | D3993
PTOKlima5Kompresor3naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3994
PTOKlima5Kompresor4naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3995
PTOKlima5ZracniFilterNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3996
PTOKlima5Grelec1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3997
PTOKlima5Grelec2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3998
PTOKlima5VlazilecNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D3999
PTOKlima5AirCondUnitNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D4000
PTOKlima5DigIn2Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4001
PTOKlima5DigIn4Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4002
PTOKlima5DigIn6Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4003
PTOKlima5VlazilecGenAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4004
PTOKlima5General2ndLevAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4005
PTOKlima5UnitOnRotAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4006
PTOKlima5UnitOnAlarmA_omogoci | DIGITAL | IOD_PTO_disk2 | D4007
PTOKlima5UnitOnAlarmB_omogoci | DIGITAL | IOD_PTO_disk2 | D4008
PTOKlima5UnitOnAlarmC_omogoci | DIGITAL | IOD_PTO_disk2 | D4009
PTOKlima6NapacnoGesloAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4010
PTOKlima6ExtTempHumAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4011
PTOKlima6PoplavniAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4012
PTOKlima6VisokPritiskKompresor1_omogoci | DIGITAL | IOD_PTO_disk2 | D4013
PTOKlima6VisokPritiskKompresor2_omogoci | DIGITAL | IOD_PTO_disk2 | D4014
PTOKlima6ElVentilKompresor1ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D4015
PTOKlima6ElVentilKompresor2ERR_omogoci | DIGITAL | IOD_PTO_disk2 | D4016
PTOKlima6WrongPhaseSeqAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4017
PTOKlima6PrekinjenLANalarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4018
PTOKlima6CWTempHighForDehum_omogoci | DIGITAL | IOD_PTO_disk2 | D4019
PTOKlima6CWVentilErrOrLowFlow_omogoci | DIGITAL | IOD_PTO_disk2 | D4020
PTOKlima6NapakaPriPretokuVode_omogoci | DIGITAL | IOD_PTO_disk2 | D4021
PTOKlima6CWhighTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D4022
PTOKlima6NapakaSenzorHotWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D4023
PTOKlima6NapakaSenzorCondWTemp_omogoci | DIGITAL | IOD_PTO_disk2 | D4024
PTOKlima6NapakaSenzorCW_omogoci | DIGITAL | IOD_PTO_disk2 | D4025
PTOKlima6Kompresor3naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D4026
PTOKlima6Kompresor4naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D4027
PTOKlima6ZracniFilterNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D4028
PTOKlima6Grelec1naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D4029
PTOKlima6Grelec2naMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D4030
PTOKlima6VlazilecNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D4031
PTOKlima6AirCondUnitNaMejiObrUr_omogoci | DIGITAL | IOD_PTO_disk2 | D4032
PTOKlima6DigIn2Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4033
PTOKlima6DigIn4Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4034
PTOKlima6DigIn6Alarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4035
PTOKlima6VlazilecGenAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4036
PTOKlima6General2ndLevAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4037
PTOKlima6UnitOnRotAlarm_omogoci | DIGITAL | IOD_PTO_disk2 | D4038
PTOKlima6UnitOnAlarmA_omogoci | DIGITAL | IOD_PTO_disk2 | D4039
PTOKlima6UnitOnAlarmB_omogoci | DIGITAL | IOD_PTO_disk2 | D4040
PTOKlima6UnitOnAlarmC_omogoci | DIGITAL | IOD_PTO_disk2 | D4041
PTOKlima1NastTempHlajenje | REAL | IOD_PTO_TCP | 44825 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima2NastTempHlajenje | REAL | IOD_PTO_TCP | 44827 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima3NastTempHlajenje | REAL | IOD_PTO_TCP | 44829 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima4NastTempHlajenje | REAL | IOD_PTO_TCP | 44831 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima5NastTempHlajenje | REAL | IOD_PTO_TCP | 44833 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima6NastTempHlajenje | REAL | IOD_PTO_TCP | 44835 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima1NastTempGretje | REAL | IOD_PTO_TCP | 44837 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima2NastTempGretje | REAL | IOD_PTO_TCP | 44839 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima3NastTempGretje | REAL | IOD_PTO_TCP | 44841 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima4NastTempGretje | REAL | IOD_PTO_TCP | 44843 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima5NastTempGretje | REAL | IOD_PTO_TCP | 44845 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima6NastTempGretje | REAL | IOD_PTO_TCP | 44847 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima1TempHladneVode | REAL | IOD_PTO_TCP | 44849 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima2TempHladneVode | REAL | IOD_PTO_TCP | 44851 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima3TempHladneVode | REAL | IOD_PTO_TCP | 44853 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima4TempHladneVode | REAL | IOD_PTO_TCP | 44855 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima5TempHladneVode | REAL | IOD_PTO_TCP | 44857 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima6TempHladneVode | REAL | IOD_PTO_TCP | 44859 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima1TempTopleVode | REAL | IOD_PTO_TCP | 44861 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima2TempTopleVode | REAL | IOD_PTO_TCP | 44863 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima3TempTopleVode | REAL | IOD_PTO_TCP | 44865 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima4TempTopleVode | REAL | IOD_PTO_TCP | 44867 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima5TempTopleVode | REAL | IOD_PTO_TCP | 44869 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima6TempTopleVode | REAL | IOD_PTO_TCP | 44871 | 0 | 60 | 0 | 60 | °C | ####.#
PTOKlima1Komp1On | DIGITAL | IOD_PTO_TCP | 00894
PTOKlima1Komp2On | DIGITAL | IOD_PTO_TCP | 00895
PTOKlima1Komp3On | DIGITAL | IOD_PTO_TCP | 00896
PTOKlima1Komp4On | DIGITAL | IOD_PTO_TCP | 00897
PTOKlima2Komp1On | DIGITAL | IOD_PTO_TCP | 00898
PTOKlima2Komp2On | DIGITAL | IOD_PTO_TCP | 00899
PTOKlima2Komp3On | DIGITAL | IOD_PTO_TCP | 00900
PTOKlima2Komp4On | DIGITAL | IOD_PTO_TCP | 00901
PTOKlima3Komp1On | DIGITAL | IOD_PTO_TCP | 00902
PTOKlima3Komp2On | DIGITAL | IOD_PTO_TCP | 00903
PTOKlima3Komp3On | DIGITAL | IOD_PTO_TCP | 00904
PTOKlima3Komp4On | DIGITAL | IOD_PTO_TCP | 00905
PTOKlima4Komp1On | DIGITAL | IOD_PTO_TCP | 00906
PTOKlima4Komp2On | DIGITAL | IOD_PTO_TCP | 00907
PTOKlima4Komp3On | DIGITAL | IOD_PTO_TCP | 00908
PTOKlima4Komp4On | DIGITAL | IOD_PTO_TCP | 00909
PTOKlima5Komp1On | DIGITAL | IOD_PTO_TCP | 00910
PTOKlima5Komp2On | DIGITAL | IOD_PTO_TCP | 00911
PTOKlima5Komp3On | DIGITAL | IOD_PTO_TCP | 00912
PTOKlima5Komp4On | DIGITAL | IOD_PTO_TCP | 00913
PTOKlima6Komp1On | DIGITAL | IOD_PTO_TCP | 00914
PTOKlima6Komp2On | DIGITAL | IOD_PTO_TCP | 00915
PTOKlima6Komp3On | DIGITAL | IOD_PTO_TCP | 00916
PTOKlima6Komp4On | DIGITAL | IOD_PTO_TCP | 00917
PTOKlima1GretjeStopnja1 | DIGITAL | IOD_PTO_TCP | 00918
PTOKlima1GretjeStopnja2 | DIGITAL | IOD_PTO_TCP | 00919
PTOKlima1GretjeStopnja3 | DIGITAL | IOD_PTO_TCP | 00920
PTOKlima2GretjeStopnja1 | DIGITAL | IOD_PTO_TCP | 00921
PTOKlima2GretjeStopnja2 | DIGITAL | IOD_PTO_TCP | 00922
PTOKlima2GretjeStopnja3 | DIGITAL | IOD_PTO_TCP | 00923
PTOKlima3GretjeStopnja1 | DIGITAL | IOD_PTO_TCP | 00924
PTOKlima3GretjeStopnja2 | DIGITAL | IOD_PTO_TCP | 00925
PTOKlima3GretjeStopnja3 | DIGITAL | IOD_PTO_TCP | 00926
PTOKlima4GretjeStopnja1 | DIGITAL | IOD_PTO_TCP | 00927
PTOKlima4GretjeStopnja2 | DIGITAL | IOD_PTO_TCP | 00928
PTOKlima4GretjeStopnja3 | DIGITAL | IOD_PTO_TCP | 00929
PTOKlima5GretjeStopnja1 | DIGITAL | IOD_PTO_TCP | 00930
PTOKlima5GretjeStopnja2 | DIGITAL | IOD_PTO_TCP | 00931
PTOKlima5GretjeStopnja3 | DIGITAL | IOD_PTO_TCP | 00932
PTOKlima6GretjeStopnja1 | DIGITAL | IOD_PTO_TCP | 00933
PTOKlima6GretjeStopnja2 | DIGITAL | IOD_PTO_TCP | 00934
PTOKlima6GretjeStopnja3 | DIGITAL | IOD_PTO_TCP | 00935
PTOKlima1HotGasOn | DIGITAL | IOD_PTO_TCP | 00936
PTOKlima2HotGasOn | DIGITAL | IOD_PTO_TCP | 00937
PTOKlima3HotGasOn | DIGITAL | IOD_PTO_TCP | 00938
PTOKlima4HotGasOn | DIGITAL | IOD_PTO_TCP | 00939
PTOKlima5HotGasOn | DIGITAL | IOD_PTO_TCP | 00940
PTOKlima6HotGasOn | DIGITAL | IOD_PTO_TCP | 00941
PTOKlima1EmergencyWorking | DIGITAL | IOD_PTO_TCP | 00942
PTOKlima2EmergencyWorking | DIGITAL | IOD_PTO_TCP | 00943
PTOKlima3EmergencyWorking | DIGITAL | IOD_PTO_TCP | 00944
PTOKlima4EmergencyWorking | DIGITAL | IOD_PTO_TCP | 00945
PTOKlima5EmergencyWorking | DIGITAL | IOD_PTO_TCP | 00946
PTOKlima6EmergencyWorking | DIGITAL | IOD_PTO_TCP | 00947
PTODI_A1Q01_DovUpsB_ON | DIGITAL | IOD_PTO_TCP | 00948
PTODI_A1Q0_GlavnoStiB_ON | DIGITAL | IOD_PTO_TCP | 00949
PTODI_A1Q11_OdcUpsB_IZP | DIGITAL | IOD_PTO_TCP | 00950
PTODI_A1Q11_OdcUpsB_ON | DIGITAL | IOD_PTO_TCP | 00951
PTODI_A1Q12_OdcByUpsB_IZP | DIGITAL | IOD_PTO_TCP | 00952
PTODI_A1Q12_OdcByUpsB_ON | DIGITAL | IOD_PTO_TCP | 00953
PTODI_A1Q13_OdcByB_IZP | DIGITAL | IOD_PTO_TCP | 00954
PTOZamikVklopa | REAL | IOD_PTO_TCP | 44873
PTOServer_B_Izpad | DIGITAL | IOD_PTO_disk2 | D4042
PTOServer_A_Izpad | DIGITAL | IOD_PTO_disk2 | D4043
PTO_ComSCADA_stevec3 | INT | IOD_PTO_disk | I4002
PTO_ComSCADA_stevec4 | INT | IOD_PTO_disk | I4004
PTOErrCommScada_omogoci2 | DIGITAL | IOD_PTO_disk2 | D4044
PTOErrCommScada2 | DIGITAL | IOD_PTO_TCP | 00955
PTOComSCADA2 | DIGITAL | IOD_PTO_TCP | 00956
PTOComSCADA3 | DIGITAL | IOD_PTO_TCP | 00957
PTOUserLoggedIn_mem | DIGITAL | IOD_PTO_disk2 | D4045
PTOkom_nast_cas_izpada | UINT | IOD_PTO_TCP | 46001
PTOKlima1Komp1On_omogoci | DIGITAL | IOD_PTO_disk2 | D4046
PTOKlima1Komp2On_omogoci | DIGITAL | IOD_PTO_disk2 | D4047
PTOKlima2Komp1On_omogoci | DIGITAL | IOD_PTO_disk2 | D4048
PTOKlima2Komp2On_omogoci | DIGITAL | IOD_PTO_disk2 | D4049
PTOKlima3Komp1On_omogoci | DIGITAL | IOD_PTO_disk2 | D4050
PTOKlima3Komp2On_omogoci | DIGITAL | IOD_PTO_disk2 | D4051
PTOKlima4Komp1On_omogoci | DIGITAL | IOD_PTO_disk2 | D4052
PTOKlima4Komp2On_omogoci | DIGITAL | IOD_PTO_disk2 | D4053
PTOKlima5Komp1On_omogoci | DIGITAL | IOD_PTO_disk2 | D4054
PTOKlima5Komp2On_omogoci | DIGITAL | IOD_PTO_disk2 | D4055
PTOKlima6Komp1On_omogoci | DIGITAL | IOD_PTO_disk2 | D4056
PTOKlima6Komp2On_omogoci | DIGITAL | IOD_PTO_disk2 | D4057
PTOKlima1GretjeStopnja1_omogoci | DIGITAL | IOD_PTO_disk2 | D4058
PTOKlima1GretjeStopnja2_omogoci | DIGITAL | IOD_PTO_disk2 | D4059
PTOKlima1GretjeStopnja3_omogoci | DIGITAL | IOD_PTO_disk2 | D4060
PTOKlima2GretjeStopnja1_omogoci | DIGITAL | IOD_PTO_disk2 | D4061
PTOKlima2GretjeStopnja2_omogoci | DIGITAL | IOD_PTO_disk2 | D4062
PTOKlima2GretjeStopnja3_omogoci | DIGITAL | IOD_PTO_disk2 | D4063
PTOKlima3GretjeStopnja1_omogoci | DIGITAL | IOD_PTO_disk2 | D4064
PTOKlima3GretjeStopnja2_omogoci | DIGITAL | IOD_PTO_disk2 | D4065
PTOKlima3GretjeStopnja3_omogoci | DIGITAL | IOD_PTO_disk2 | D4066
PTOKlima4GretjeStopnja1_omogoci | DIGITAL | IOD_PTO_disk2 | D4067
PTOKlima4GretjeStopnja2_omogoci | DIGITAL | IOD_PTO_disk2 | D4068
PTOKlima4GretjeStopnja3_omogoci | DIGITAL | IOD_PTO_disk2 | D4069
PTOKlima5GretjeStopnja1_omogoci | DIGITAL | IOD_PTO_disk2 | D4070
PTOKlima5GretjeStopnja2_omogoci | DIGITAL | IOD_PTO_disk2 | D4071
PTOKlima5GretjeStopnja3_omogoci | DIGITAL | IOD_PTO_disk2 | D4072
PTOKlima6GretjeStopnja1_omogoci | DIGITAL | IOD_PTO_disk2 | D4073
PTOKlima6GretjeStopnja2_omogoci | DIGITAL | IOD_PTO_disk2 | D4074
PTOKlima6GretjeStopnja3_omogoci | DIGITAL | IOD_PTO_disk2 | D4075
PTOKlima1Razvlazevanje_omogoci | DIGITAL | IOD_PTO_disk2 | D4076
PTOKlima2Razvlazevanje_omogoci | DIGITAL | IOD_PTO_disk2 | D4077
PTOKlima3Razvlazevanje_omogoci | DIGITAL | IOD_PTO_disk2 | D4078
PTOKlima4Razvlazevanje_omogoci | DIGITAL | IOD_PTO_disk2 | D4079
PTOKlima5Razvlazevanje_omogoci | DIGITAL | IOD_PTO_disk2 | D4080
PTOKlima6Razvlazevanje_omogoci | DIGITAL | IOD_PTO_disk2 | D4081
PTOKlima1Vlazenje_omogoci | DIGITAL | IOD_PTO_disk2 | D4082
PTOKlima2Vlazenje_omogoci | DIGITAL | IOD_PTO_disk2 | D4083
PTOKlima3Vlazenje_omogoci | DIGITAL | IOD_PTO_disk2 | D4084
PTOKlima4Vlazenje_omogoci | DIGITAL | IOD_PTO_disk2 | D4085
PTOKlima5Vlazenje_omogoci | DIGITAL | IOD_PTO_disk2 | D4086
PTOKlima6Vlazenje_omogoci | DIGITAL | IOD_PTO_disk2 | D4087
PTOKlima1UnitOnOff_omogoci | DIGITAL | IOD_PTO_disk2 | D4088
PTOKlima2UnitOnOff_omogoci | DIGITAL | IOD_PTO_disk2 | D4089
PTOKlima3UnitOnOff_omogoci | DIGITAL | IOD_PTO_disk2 | D4090
PTOKlima4UnitOnOff_omogoci | DIGITAL | IOD_PTO_disk2 | D4091
PTOKlima5UnitOnOff_omogoci | DIGITAL | IOD_PTO_disk2 | D4092
PTOKlima6UnitOnOff_omogoci | DIGITAL | IOD_PTO_disk2 | D4093

## XSoft
mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Write_BOOL(FC) | mod_Write_Word(FC) | mod_Write_Word(FC) | mod_Write_dWord(FC) | mod_Write_dWord(FC) | mod_Write_String(FC)
(*Branje BOOL*) | (*Branje INT*) | (*Branje UINT*) | (*Branje LONG*) | (*Branje REAL*) | (*Branje STRING*) | (*Pisanje BOOL*) | (*Pisanje INT*) | (*Pisanje UINT*) | (*Pisanje LONG*) | (*Pisanje REAL*) | (*Pisanje STRING*)
(**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**)
mind_bool[0]:=AlarmGenComm; | mind[0]:=DateTime.Dan; | mind[6000]:=kom_nast_cas_izpada; |  | Read_Real(rVar:=Klima[1].ObratovalneUre,lo:=4000,hi:=4001); | Read_String(sVar:=Date_Time[0],start:=5000); | 0:AlarmGenComm:=Bit_0; | 0:DateTime.Dan:=Byte_0; | 6000:kom_nast_cas_izpada:=Word_01; |  | 4001:Klima[1].ObratovalneUre:=Real_0; | 5000:Date_Time[0]:=String_0;
mind_bool[1]:=AlarmGenKlima[1]; | mind[1]:=DateTime.Leto; |  |  | Read_Real(rVar:=Klima[1].TemperaturaProstora,lo:=4002,hi:=4003); | Read_String(sVar:=Date_Time[1],start:=5015); | 1:AlarmGenKlima[1]:=Bit_0; | 1:DateTime.Leto:=Byte_0; |  |  | 4003:Klima[1].TemperaturaProstora:=Real_0; | 5015:Date_Time[1]:=String_0;
mind_bool[2]:=AlarmGenKlima[2]; | mind[2]:=DateTime.Mesec; |  |  | Read_Real(rVar:=Klima[1].TempIzpihanegaZraka,lo:=4004,hi:=4005); | Read_String(sVar:=Date_Time[2],start:=5030); | 2:AlarmGenKlima[2]:=Bit_0; | 2:DateTime.Mesec:=Byte_0; |  |  | 4005:Klima[1].TempIzpihanegaZraka:=Real_0; | 5030:Date_Time[2]:=String_0;
mind_bool[3]:=AlarmGenKlima[3]; | mind[3]:=DateTime.Minuta; |  |  | Read_Real(rVar:=Klima[1].VlaznostProstora,lo:=4006,hi:=4007); | Read_String(sVar:=Date_Time[3],start:=5045); | 3:AlarmGenKlima[3]:=Bit_0; | 3:DateTime.Minuta:=Byte_0; |  |  | 4007:Klima[1].VlaznostProstora:=Real_0; | 5045:Date_Time[3]:=String_0;
mind_bool[4]:=AlarmGenKlima[4]; | mind[4]:=DateTime.Sekunda; |  |  | Read_Real(rVar:=Klima[1].ZunanjaTemp,lo:=4008,hi:=4009); | Read_String(sVar:=UserCurrentName,start:=5060); | 4:AlarmGenKlima[4]:=Bit_0; | 4:DateTime.Sekunda:=Byte_0; |  |  | 4009:Klima[1].ZunanjaTemp:=Real_0; | 5060:UserCurrentName:=String_0;
mind_bool[5]:=AlarmGenKlima[5]; | mind[5]:=DateTime.Ura; |  |  | Read_Real(rVar:=Klima[2].ObratovalneUre,lo:=4010,hi:=4011); |  | 5:AlarmGenKlima[5]:=Bit_0; | 5:DateTime.Ura:=Byte_0; |  |  | 4011:Klima[2].ObratovalneUre:=Real_0;
mind_bool[6]:=AlarmGenKlima[6]; | mind[6]:=ErrorComKlima[1].Code[10]; |  |  | Read_Real(rVar:=Klima[2].TemperaturaProstora,lo:=4012,hi:=4013); |  | 6:AlarmGenKlima[6]:=Bit_0; | 6:ErrorComKlima[1].Code[10]:=Byte_0; |  |  | 4013:Klima[2].TemperaturaProstora:=Real_0;
mind_bool[7]:=AlarmGenPMM; | mind[7]:=ErrorComKlima[1].Code[11]; |  |  | Read_Real(rVar:=Klima[2].TempIzpihanegaZraka,lo:=4014,hi:=4015); |  | 7:AlarmGenPMM:=Bit_0; | 7:ErrorComKlima[1].Code[11]:=Byte_0; |  |  | 4015:Klima[2].TempIzpihanegaZraka:=Real_0;
mind_bool[8]:=AlarmGenRest; | mind[8]:=ErrorComKlima[1].Code[12]; |  |  | Read_Real(rVar:=Klima[2].VlaznostProstora,lo:=4016,hi:=4017); |  | 8:AlarmGenRest:=Bit_0; | 8:ErrorComKlima[1].Code[12]:=Byte_0; |  |  | 4017:Klima[2].VlaznostProstora:=Real_0;
mind_bool[9]:=AlarmGenSenzor; | mind[9]:=ErrorComKlima[1].Code[13]; |  |  | Read_Real(rVar:=Klima[2].ZunanjaTemp,lo:=4018,hi:=4019); |  | 9:AlarmGenSenzor:=Bit_0; | 9:ErrorComKlima[1].Code[13]:=Byte_0; |  |  | 4019:Klima[2].ZunanjaTemp:=Real_0;
mind_bool[10]:=AlarmGenStikala; | mind[10]:=ErrorComKlima[1].Code[14]; |  |  | Read_Real(rVar:=Klima[3].ObratovalneUre,lo:=4020,hi:=4021); |  | 10:AlarmGenStikala:=Bit_0; | 10:ErrorComKlima[1].Code[14]:=Byte_0; |  |  | 4021:Klima[3].ObratovalneUre:=Real_0;
mind_bool[11]:=AlarmGenTemp; | mind[11]:=ErrorComKlima[1].Code[15]; |  |  | Read_Real(rVar:=Klima[3].TemperaturaProstora,lo:=4022,hi:=4023); |  | 11:AlarmGenTemp:=Bit_0; | 11:ErrorComKlima[1].Code[15]:=Byte_0; |  |  | 4023:Klima[3].TemperaturaProstora:=Real_0;
mind_bool[12]:=AlarmGenUPS1; | mind[12]:=ErrorComKlima[1].Code[1]; |  |  | Read_Real(rVar:=Klima[3].TempIzpihanegaZraka,lo:=4024,hi:=4025); |  | 12:AlarmGenUPS1:=Bit_0; | 12:ErrorComKlima[1].Code[1]:=Byte_0; |  |  | 4025:Klima[3].TempIzpihanegaZraka:=Real_0;
mind_bool[13]:=AlarmGenUPS2; | mind[13]:=ErrorComKlima[1].Code[2]; |  |  | Read_Real(rVar:=Klima[3].VlaznostProstora,lo:=4026,hi:=4027); |  | 13:AlarmGenUPS2:=Bit_0; | 13:ErrorComKlima[1].Code[2]:=Byte_0; |  |  | 4027:Klima[3].VlaznostProstora:=Real_0;
mind_bool[14]:=ComSCADA; | mind[14]:=ErrorComKlima[1].Code[3]; |  |  | Read_Real(rVar:=Klima[3].ZunanjaTemp,lo:=4028,hi:=4029); |  | 14:ComSCADA:=Bit_0; | 14:ErrorComKlima[1].Code[3]:=Byte_0; |  |  | 4029:Klima[3].ZunanjaTemp:=Real_0;
mind_bool[15]:=ComSCADA1; | mind[15]:=ErrorComKlima[1].Code[4]; |  |  | Read_Real(rVar:=Klima[4].ObratovalneUre,lo:=4030,hi:=4031); |  | 15:ComSCADA1:=Bit_0; | 15:ErrorComKlima[1].Code[4]:=Byte_0; |  |  | 4031:Klima[4].ObratovalneUre:=Real_0;
mind_bool[16]:=DI_A1Q01_DovUpsA_ON; | mind[16]:=ErrorComKlima[1].Code[5]; |  |  | Read_Real(rVar:=Klima[4].TemperaturaProstora,lo:=4032,hi:=4033); |  | 16:DI_A1Q01_DovUpsA_ON:=Bit_0; | 16:ErrorComKlima[1].Code[5]:=Byte_0; |  |  | 4033:Klima[4].TemperaturaProstora:=Real_0;
mind_bool[17]:=DI_A1Q02_DovByA_ON; | mind[17]:=ErrorComKlima[1].Code[6]; |  |  | Read_Real(rVar:=Klima[4].TempIzpihanegaZraka,lo:=4034,hi:=4035); |  | 17:DI_A1Q02_DovByA_ON:=Bit_0; | 17:ErrorComKlima[1].Code[6]:=Byte_0; |  |  | 4035:Klima[4].TempIzpihanegaZraka:=Real_0;
mind_bool[18]:=DI_A1Q0_GlavnoSti_ON; | mind[18]:=ErrorComKlima[1].Code[7]; |  |  | Read_Real(rVar:=Klima[4].VlaznostProstora,lo:=4036,hi:=4037); |  | 18:DI_A1Q0_GlavnoSti_ON:=Bit_0; | 18:ErrorComKlima[1].Code[7]:=Byte_0; |  |  | 4037:Klima[4].VlaznostProstora:=Real_0;
mind_bool[19]:=DI_A1Q11_OdcUpsA_IZP; | mind[19]:=ErrorComKlima[1].Code[8]; |  |  | Read_Real(rVar:=Klima[4].ZunanjaTemp,lo:=4038,hi:=4039); |  | 19:DI_A1Q11_OdcUpsA_IZP:=Bit_0; | 19:ErrorComKlima[1].Code[8]:=Byte_0; |  |  | 4039:Klima[4].ZunanjaTemp:=Real_0;
mind_bool[20]:=DI_A1Q11_OdcUpsA_ON; | mind[20]:=ErrorComKlima[1].Code[9]; |  |  | Read_Real(rVar:=Klima[5].ObratovalneUre,lo:=4040,hi:=4041); |  | 20:DI_A1Q11_OdcUpsA_ON:=Bit_0; | 20:ErrorComKlima[1].Code[9]:=Byte_0; |  |  | 4041:Klima[5].ObratovalneUre:=Real_0;
mind_bool[21]:=DI_A1Q12_OdcByUpsA_IZP; | mind[21]:=ErrorComKlima[1].Status; |  |  | Read_Real(rVar:=Klima[5].TemperaturaProstora,lo:=4042,hi:=4043); |  | 21:DI_A1Q12_OdcByUpsA_IZP:=Bit_0; | 21:ErrorComKlima[1].Status:=Word_01; |  |  | 4043:Klima[5].TemperaturaProstora:=Real_0;
mind_bool[22]:=DI_A1Q12_OdcByUpsA_ON; | mind[22]:=ErrorComKlima[2].Code[10]; |  |  | Read_Real(rVar:=Klima[5].TempIzpihanegaZraka,lo:=4044,hi:=4045); |  | 22:DI_A1Q12_OdcByUpsA_ON:=Bit_0; | 22:ErrorComKlima[2].Code[10]:=Byte_0; |  |  | 4045:Klima[5].TempIzpihanegaZraka:=Real_0;
mind_bool[23]:=DI_A1Q13_OdcByA_IZP; | mind[23]:=ErrorComKlima[2].Code[11]; |  |  | Read_Real(rVar:=Klima[5].VlaznostProstora,lo:=4046,hi:=4047); |  | 23:DI_A1Q13_OdcByA_IZP:=Bit_0; | 23:ErrorComKlima[2].Code[11]:=Byte_0; |  |  | 4047:Klima[5].VlaznostProstora:=Real_0;
mind_bool[24]:=DI_A1Q13_OdcByA_ON; | mind[24]:=ErrorComKlima[2].Code[12]; |  |  | Read_Real(rVar:=Klima[5].ZunanjaTemp,lo:=4048,hi:=4049); |  | 24:DI_A1Q13_OdcByA_ON:=Bit_0; | 24:ErrorComKlima[2].Code[12]:=Byte_0; |  |  | 4049:Klima[5].ZunanjaTemp:=Real_0;
mind_bool[25]:=DI_A2Q0_GlavnoSti_ON; | mind[25]:=ErrorComKlima[2].Code[13]; |  |  | Read_Real(rVar:=Klima[6].ObratovalneUre,lo:=4050,hi:=4051); |  | 25:DI_A2Q0_GlavnoSti_ON:=Bit_0; | 25:ErrorComKlima[2].Code[13]:=Byte_0; |  |  | 4051:Klima[6].ObratovalneUre:=Real_0;
mind_bool[26]:=DI_F201_OdcKl1ZE_IZP; | mind[26]:=ErrorComKlima[2].Code[14]; |  |  | Read_Real(rVar:=Klima[6].TemperaturaProstora,lo:=4052,hi:=4053); |  | 26:DI_F201_OdcKl1ZE_IZP:=Bit_0; | 26:ErrorComKlima[2].Code[14]:=Byte_0; |  |  | 4053:Klima[6].TemperaturaProstora:=Real_0;
mind_bool[27]:=DI_F201_OdcKl1ZE_ON; | mind[27]:=ErrorComKlima[2].Code[15]; |  |  | Read_Real(rVar:=Klima[6].TempIzpihanegaZraka,lo:=4054,hi:=4055); |  | 27:DI_F201_OdcKl1ZE_ON:=Bit_0; | 27:ErrorComKlima[2].Code[15]:=Byte_0; |  |  | 4055:Klima[6].TempIzpihanegaZraka:=Real_0;
mind_bool[28]:=DI_F202_OdcKl2ZE_IZP; | mind[28]:=ErrorComKlima[2].Code[1]; |  |  | Read_Real(rVar:=Klima[6].VlaznostProstora,lo:=4056,hi:=4057); |  | 28:DI_F202_OdcKl2ZE_IZP:=Bit_0; | 28:ErrorComKlima[2].Code[1]:=Byte_0; |  |  | 4057:Klima[6].VlaznostProstora:=Real_0;
mind_bool[29]:=DI_F202_OdcKl2ZE_ON; | mind[29]:=ErrorComKlima[2].Code[2]; |  |  | Read_Real(rVar:=Klima[6].ZunanjaTemp,lo:=4058,hi:=4059); |  | 29:DI_F202_OdcKl2ZE_ON:=Bit_0; | 29:ErrorComKlima[2].Code[2]:=Byte_0; |  |  | 4059:Klima[6].ZunanjaTemp:=Real_0;
mind_bool[30]:=DI_F203_OdcKl3ZE_IZP; | mind[30]:=ErrorComKlima[2].Code[3]; |  |  | Read_Real(rVar:=PMM.ActiveEnergyConsumed_kWh,lo:=4060,hi:=4061); |  | 30:DI_F203_OdcKl3ZE_IZP:=Bit_0; | 30:ErrorComKlima[2].Code[3]:=Byte_0; |  |  | 4061:PMM.ActiveEnergyConsumed_kWh:=Real_0;
mind_bool[31]:=DI_F203_OdcKl3ZE_ON; | mind[31]:=ErrorComKlima[2].Code[4]; |  |  | Read_Real(rVar:=PMM.ActivePowerPhaseA_kW,lo:=4062,hi:=4063); |  | 31:DI_F203_OdcKl3ZE_ON:=Bit_0; | 31:ErrorComKlima[2].Code[4]:=Byte_0; |  |  | 4063:PMM.ActivePowerPhaseA_kW:=Real_0;
mind_bool[32]:=DI_F204_OdcKl4ZE_IZP; | mind[32]:=ErrorComKlima[2].Code[5]; |  |  | Read_Real(rVar:=PMM.ActivePowerPhaseB_kW,lo:=4064,hi:=4065); |  | 32:DI_F204_OdcKl4ZE_IZP:=Bit_0; | 32:ErrorComKlima[2].Code[5]:=Byte_0; |  |  | 4065:PMM.ActivePowerPhaseB_kW:=Real_0;
mind_bool[33]:=DI_F204_OdcKl4ZE_ON; | mind[33]:=ErrorComKlima[2].Code[6]; |  |  | Read_Real(rVar:=PMM.ActivePowerPhaseC_kW,lo:=4066,hi:=4067); |  | 33:DI_F204_OdcKl4ZE_ON:=Bit_0; | 33:ErrorComKlima[2].Code[6]:=Byte_0; |  |  | 4067:PMM.ActivePowerPhaseC_kW:=Real_0;
mind_bool[34]:=DI_F205_OdcKl5aZE_IZP; | mind[34]:=ErrorComKlima[2].Code[7]; |  |  | Read_Real(rVar:=PMM.AparentPowerPhaseA,lo:=4068,hi:=4069); |  | 34:DI_F205_OdcKl5aZE_IZP:=Bit_0; | 34:ErrorComKlima[2].Code[7]:=Byte_0; |  |  | 4069:PMM.AparentPowerPhaseA:=Real_0;
mind_bool[35]:=DI_F205_OdcKl5aZE_ON; | mind[35]:=ErrorComKlima[2].Code[8]; |  |  | Read_Real(rVar:=PMM.AparentPowerPhaseB,lo:=4070,hi:=4071); |  | 35:DI_F205_OdcKl5aZE_ON:=Bit_0; | 35:ErrorComKlima[2].Code[8]:=Byte_0; |  |  | 4071:PMM.AparentPowerPhaseB:=Real_0;
mind_bool[36]:=DI_F206_OdcKl5bZE_IZP; | mind[36]:=ErrorComKlima[2].Code[9]; |  |  | Read_Real(rVar:=PMM.AparentPowerPhaseC,lo:=4072,hi:=4073); |  | 36:DI_F206_OdcKl5bZE_IZP:=Bit_0; | 36:ErrorComKlima[2].Code[9]:=Byte_0; |  |  | 4073:PMM.AparentPowerPhaseC:=Real_0;
mind_bool[37]:=DI_F206_OdcKl5bZE_ON; | mind[37]:=ErrorComKlima[2].Status; |  |  | Read_Real(rVar:=PMM.AverageCurrent_A,lo:=4074,hi:=4075); |  | 37:DI_F206_OdcKl5bZE_ON:=Bit_0; | 37:ErrorComKlima[2].Status:=Word_01; |  |  | 4075:PMM.AverageCurrent_A:=Real_0;
mind_bool[38]:=DI_F207_OdcKl6aZE_IZP; | mind[38]:=ErrorComKlima[3].Code[10]; |  |  | Read_Real(rVar:=PMM.AveragePhaseToNeutral_V,lo:=4076,hi:=4077); |  | 38:DI_F207_OdcKl6aZE_IZP:=Bit_0; | 38:ErrorComKlima[3].Code[10]:=Byte_0; |  |  | 4077:PMM.AveragePhaseToNeutral_V:=Real_0;
mind_bool[39]:=DI_F207_OdcKl6aZE_ON; | mind[39]:=ErrorComKlima[3].Code[11]; |  |  | Read_Real(rVar:=PMM.AveragePhaseToPhase_V,lo:=4078,hi:=4079); |  | 39:DI_F207_OdcKl6aZE_ON:=Bit_0; | 39:ErrorComKlima[3].Code[11]:=Byte_0; |  |  | 4079:PMM.AveragePhaseToPhase_V:=Real_0;
mind_bool[40]:=DI_F208_OdcKl6bZE_IZP; | mind[40]:=ErrorComKlima[3].Code[12]; |  |  | Read_Real(rVar:=PMM.CurrentInPhaseA_A,lo:=4080,hi:=4081); |  | 40:DI_F208_OdcKl6bZE_IZP:=Bit_0; | 40:ErrorComKlima[3].Code[12]:=Byte_0; |  |  | 4081:PMM.CurrentInPhaseA_A:=Real_0;
mind_bool[41]:=DI_F208_OdcKl6bZE_ON; | mind[41]:=ErrorComKlima[3].Code[13]; |  |  | Read_Real(rVar:=PMM.CurrentInPhaseB_A,lo:=4082,hi:=4083); |  | 41:DI_F208_OdcKl6bZE_ON:=Bit_0; | 41:ErrorComKlima[3].Code[13]:=Byte_0; |  |  | 4083:PMM.CurrentInPhaseB_A:=Real_0;
mind_bool[42]:=DI_IzpadMreze; | mind[42]:=ErrorComKlima[3].Code[14]; |  |  | Read_Real(rVar:=PMM.CurrentInPhaseC_A,lo:=4084,hi:=4085); |  | 42:DI_IzpadMreze:=Bit_0; | 42:ErrorComKlima[3].Code[14]:=Byte_0; |  |  | 4085:PMM.CurrentInPhaseC_A:=Real_0;
mind_bool[43]:=DI_Klima1_ERR; | mind[43]:=ErrorComKlima[3].Code[15]; |  |  | Read_Real(rVar:=PMM.Frequency_Hz,lo:=4086,hi:=4087); |  | 43:DI_Klima1_ERR:=Bit_0; | 43:ErrorComKlima[3].Code[15]:=Byte_0; |  |  | 4087:PMM.Frequency_Hz:=Real_0;
mind_bool[44]:=DI_Klima1_ON; | mind[44]:=ErrorComKlima[3].Code[1]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[10],lo:=4088,hi:=4089); |  | 44:DI_Klima1_ON:=Bit_0; | 44:ErrorComKlima[3].Code[1]:=Byte_0; |  |  | 4089:PMM.Phase[1].Current[10]:=Real_0;
mind_bool[45]:=DI_Klima2_ERR; | mind[45]:=ErrorComKlima[3].Code[2]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[11],lo:=4090,hi:=4091); |  | 45:DI_Klima2_ERR:=Bit_0; | 45:ErrorComKlima[3].Code[2]:=Byte_0; |  |  | 4091:PMM.Phase[1].Current[11]:=Real_0;
mind_bool[46]:=DI_Klima2_ON; | mind[46]:=ErrorComKlima[3].Code[3]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[12],lo:=4092,hi:=4093); |  | 46:DI_Klima2_ON:=Bit_0; | 46:ErrorComKlima[3].Code[3]:=Byte_0; |  |  | 4093:PMM.Phase[1].Current[12]:=Real_0;
mind_bool[47]:=DI_Klima3_ERR; | mind[47]:=ErrorComKlima[3].Code[4]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[13],lo:=4094,hi:=4095); |  | 47:DI_Klima3_ERR:=Bit_0; | 47:ErrorComKlima[3].Code[4]:=Byte_0; |  |  | 4095:PMM.Phase[1].Current[13]:=Real_0;
mind_bool[48]:=DI_Klima3_ON; | mind[48]:=ErrorComKlima[3].Code[5]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[14],lo:=4096,hi:=4097); |  | 48:DI_Klima3_ON:=Bit_0; | 48:ErrorComKlima[3].Code[5]:=Byte_0; |  |  | 4097:PMM.Phase[1].Current[14]:=Real_0;
mind_bool[49]:=DI_Klima4_ERR; | mind[49]:=ErrorComKlima[3].Code[6]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[15],lo:=4098,hi:=4099); |  | 49:DI_Klima4_ERR:=Bit_0; | 49:ErrorComKlima[3].Code[6]:=Byte_0; |  |  | 4099:PMM.Phase[1].Current[15]:=Real_0;
mind_bool[50]:=DI_Klima4_ON; | mind[50]:=ErrorComKlima[3].Code[7]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[16],lo:=4100,hi:=4101); |  | 50:DI_Klima4_ON:=Bit_0; | 50:ErrorComKlima[3].Code[7]:=Byte_0; |  |  | 4101:PMM.Phase[1].Current[16]:=Real_0;
mind_bool[51]:=DI_Klima5_ERR; | mind[51]:=ErrorComKlima[3].Code[8]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[17],lo:=4102,hi:=4103); |  | 51:DI_Klima5_ERR:=Bit_0; | 51:ErrorComKlima[3].Code[8]:=Byte_0; |  |  | 4103:PMM.Phase[1].Current[17]:=Real_0;
mind_bool[52]:=DI_Klima5_ON; | mind[52]:=ErrorComKlima[3].Code[9]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[18],lo:=4104,hi:=4105); |  | 52:DI_Klima5_ON:=Bit_0; | 52:ErrorComKlima[3].Code[9]:=Byte_0; |  |  | 4105:PMM.Phase[1].Current[18]:=Real_0;
mind_bool[53]:=DI_Klima6_ERR; | mind[53]:=ErrorComKlima[3].Status; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[19],lo:=4106,hi:=4107); |  | 53:DI_Klima6_ERR:=Bit_0; | 53:ErrorComKlima[3].Status:=Word_01; |  |  | 4107:PMM.Phase[1].Current[19]:=Real_0;
mind_bool[54]:=DI_Klima6_ON; | mind[54]:=ErrorComKlima[4].Code[10]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[1],lo:=4108,hi:=4109); |  | 54:DI_Klima6_ON:=Bit_0; | 54:ErrorComKlima[4].Code[10]:=Byte_0; |  |  | 4109:PMM.Phase[1].Current[1]:=Real_0;
mind_bool[55]:=DI_KlimaSplitPP_ERR; | mind[55]:=ErrorComKlima[4].Code[11]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[20],lo:=4110,hi:=4111); |  | 55:DI_KlimaSplitPP_ERR:=Bit_0; | 55:ErrorComKlima[4].Code[11]:=Byte_0; |  |  | 4111:PMM.Phase[1].Current[20]:=Real_0;
mind_bool[56]:=DI_KlimaSplitPP_ON; | mind[56]:=ErrorComKlima[4].Code[12]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[21],lo:=4112,hi:=4113); |  | 56:DI_KlimaSplitPP_ON:=Bit_0; | 56:ErrorComKlima[4].Code[12]:=Byte_0; |  |  | 4113:PMM.Phase[1].Current[21]:=Real_0;
mind_bool[57]:=DI_PrenapA1_OK; | mind[57]:=ErrorComKlima[4].Code[13]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[22],lo:=4114,hi:=4115); |  | 57:DI_PrenapA1_OK:=Bit_0; | 57:ErrorComKlima[4].Code[13]:=Byte_0; |  |  | 4115:PMM.Phase[1].Current[22]:=Real_0;
mind_bool[58]:=DI_PrenapA2_OK; | mind[58]:=ErrorComKlima[4].Code[14]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[23],lo:=4116,hi:=4117); |  | 58:DI_PrenapA2_OK:=Bit_0; | 58:ErrorComKlima[4].Code[14]:=Byte_0; |  |  | 4117:PMM.Phase[1].Current[23]:=Real_0;
mind_bool[59]:=DI_Q101_OdcKlima1_IZP; | mind[59]:=ErrorComKlima[4].Code[15]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[24],lo:=4118,hi:=4119); |  | 59:DI_Q101_OdcKlima1_IZP:=Bit_0; | 59:ErrorComKlima[4].Code[15]:=Byte_0; |  |  | 4119:PMM.Phase[1].Current[24]:=Real_0;
mind_bool[60]:=DI_Q101_OdcKlima1_ON; | mind[60]:=ErrorComKlima[4].Code[1]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[25],lo:=4120,hi:=4121); |  | 60:DI_Q101_OdcKlima1_ON:=Bit_0; | 60:ErrorComKlima[4].Code[1]:=Byte_0; |  |  | 4121:PMM.Phase[1].Current[25]:=Real_0;
mind_bool[61]:=DI_Q102_OdcKlima2_IZP; | mind[61]:=ErrorComKlima[4].Code[2]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[26],lo:=4122,hi:=4123); |  | 61:DI_Q102_OdcKlima2_IZP:=Bit_0; | 61:ErrorComKlima[4].Code[2]:=Byte_0; |  |  | 4123:PMM.Phase[1].Current[26]:=Real_0;
mind_bool[62]:=DI_Q102_OdcKlima2_ON; | mind[62]:=ErrorComKlima[4].Code[3]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[27],lo:=4124,hi:=4125); |  | 62:DI_Q102_OdcKlima2_ON:=Bit_0; | 62:ErrorComKlima[4].Code[3]:=Byte_0; |  |  | 4125:PMM.Phase[1].Current[27]:=Real_0;
mind_bool[63]:=DI_Q103_OdcKlima3_IZP; | mind[63]:=ErrorComKlima[4].Code[4]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[28],lo:=4126,hi:=4127); |  | 63:DI_Q103_OdcKlima3_IZP:=Bit_0; | 63:ErrorComKlima[4].Code[4]:=Byte_0; |  |  | 4127:PMM.Phase[1].Current[28]:=Real_0;
mind_bool[64]:=DI_Q103_OdcKlima3_ON; | mind[64]:=ErrorComKlima[4].Code[5]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[29],lo:=4128,hi:=4129); |  | 64:DI_Q103_OdcKlima3_ON:=Bit_0; | 64:ErrorComKlima[4].Code[5]:=Byte_0; |  |  | 4129:PMM.Phase[1].Current[29]:=Real_0;
mind_bool[65]:=DI_Q104_OdcKlima4_IZP; | mind[65]:=ErrorComKlima[4].Code[6]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[2],lo:=4130,hi:=4131); |  | 65:DI_Q104_OdcKlima4_IZP:=Bit_0; | 65:ErrorComKlima[4].Code[6]:=Byte_0; |  |  | 4131:PMM.Phase[1].Current[2]:=Real_0;
mind_bool[66]:=DI_Q104_OdcKlima4_ON; | mind[66]:=ErrorComKlima[4].Code[7]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[30],lo:=4132,hi:=4133); |  | 66:DI_Q104_OdcKlima4_ON:=Bit_0; | 66:ErrorComKlima[4].Code[7]:=Byte_0; |  |  | 4133:PMM.Phase[1].Current[30]:=Real_0;
mind_bool[67]:=DI_Q105_OdcKlima5_IZP; | mind[67]:=ErrorComKlima[4].Code[8]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[31],lo:=4134,hi:=4135); |  | 67:DI_Q105_OdcKlima5_IZP:=Bit_0; | 67:ErrorComKlima[4].Code[8]:=Byte_0; |  |  | 4135:PMM.Phase[1].Current[31]:=Real_0;
mind_bool[68]:=DI_Q105_OdcKlima5_ON; | mind[68]:=ErrorComKlima[4].Code[9]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[32],lo:=4136,hi:=4137); |  | 68:DI_Q105_OdcKlima5_ON:=Bit_0; | 68:ErrorComKlima[4].Code[9]:=Byte_0; |  |  | 4137:PMM.Phase[1].Current[32]:=Real_0;
mind_bool[69]:=DI_Q106_OdcKlima6_IZP; | mind[69]:=ErrorComKlima[4].Status; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[33],lo:=4138,hi:=4139); |  | 69:DI_Q106_OdcKlima6_IZP:=Bit_0; | 69:ErrorComKlima[4].Status:=Word_01; |  |  | 4139:PMM.Phase[1].Current[33]:=Real_0;
mind_bool[70]:=DI_Q106_OdcKlima6_ON; | mind[70]:=ErrorComKlima[5].Code[10]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[34],lo:=4140,hi:=4141); |  | 70:DI_Q106_OdcKlima6_ON:=Bit_0; | 70:ErrorComKlima[5].Code[10]:=Byte_0; |  |  | 4141:PMM.Phase[1].Current[34]:=Real_0;
mind_bool[71]:=DI_Q107_OdcUsmSS2_IZP; | mind[71]:=ErrorComKlima[5].Code[11]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[35],lo:=4142,hi:=4143); |  | 71:DI_Q107_OdcUsmSS2_IZP:=Bit_0; | 71:ErrorComKlima[5].Code[11]:=Byte_0; |  |  | 4143:PMM.Phase[1].Current[35]:=Real_0;
mind_bool[72]:=DI_Q107_OdcUsmSS2_ON; | mind[72]:=ErrorComKlima[5].Code[12]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[36],lo:=4144,hi:=4145); |  | 72:DI_Q107_OdcUsmSS2_ON:=Bit_0; | 72:ErrorComKlima[5].Code[12]:=Byte_0; |  |  | 4145:PMM.Phase[1].Current[36]:=Real_0;
mind_bool[73]:=DI_Q108_OdcUsmSS3_IZP; | mind[73]:=ErrorComKlima[5].Code[13]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[37],lo:=4146,hi:=4147); |  | 73:DI_Q108_OdcUsmSS3_IZP:=Bit_0; | 73:ErrorComKlima[5].Code[13]:=Byte_0; |  |  | 4147:PMM.Phase[1].Current[37]:=Real_0;
mind_bool[74]:=DI_Q108_OdcUsmSS3_ON; | mind[74]:=ErrorComKlima[5].Code[14]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[38],lo:=4148,hi:=4149); |  | 74:DI_Q108_OdcUsmSS3_ON:=Bit_0; | 74:ErrorComKlima[5].Code[14]:=Byte_0; |  |  | 4149:PMM.Phase[1].Current[38]:=Real_0;
mind_bool[75]:=DI_RazlitjeVodeK1K2; | mind[75]:=ErrorComKlima[5].Code[15]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[39],lo:=4150,hi:=4151); |  | 75:DI_RazlitjeVodeK1K2:=Bit_0; | 75:ErrorComKlima[5].Code[15]:=Byte_0; |  |  | 4151:PMM.Phase[1].Current[39]:=Real_0;
mind_bool[76]:=DI_RazlitjeVodeK3K4; | mind[76]:=ErrorComKlima[5].Code[1]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[3],lo:=4152,hi:=4153); |  | 76:DI_RazlitjeVodeK3K4:=Bit_0; | 76:ErrorComKlima[5].Code[1]:=Byte_0; |  |  | 4153:PMM.Phase[1].Current[3]:=Real_0;
mind_bool[77]:=DI_RazlitjeVodeK5; | mind[77]:=ErrorComKlima[5].Code[2]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[40],lo:=4154,hi:=4155); |  | 77:DI_RazlitjeVodeK5:=Bit_0; | 77:ErrorComKlima[5].Code[2]:=Byte_0; |  |  | 4155:PMM.Phase[1].Current[40]:=Real_0;
mind_bool[78]:=DI_RazlitjeVodeK6; | mind[78]:=ErrorComKlima[5].Code[3]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[41],lo:=4156,hi:=4157); |  | 78:DI_RazlitjeVodeK6:=Bit_0; | 78:ErrorComKlima[5].Code[3]:=Byte_0; |  |  | 4157:PMM.Phase[1].Current[41]:=Real_0;
mind_bool[79]:=DI_UPS_Alarm; | mind[79]:=ErrorComKlima[5].Code[4]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[42],lo:=4158,hi:=4159); |  | 79:DI_UPS_Alarm:=Bit_0; | 79:ErrorComKlima[5].Code[4]:=Byte_0; |  |  | 4159:PMM.Phase[1].Current[42]:=Real_0;
mind_bool[80]:=DI_UPS_BatNacin; | mind[80]:=ErrorComKlima[5].Code[5]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[4],lo:=4160,hi:=4161); |  | 80:DI_UPS_BatNacin:=Bit_0; | 80:ErrorComKlima[5].Code[5]:=Byte_0; |  |  | 4161:PMM.Phase[1].Current[4]:=Real_0;
mind_bool[81]:=DI_UPS_Polnjenje; | mind[81]:=ErrorComKlima[5].Code[6]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[5],lo:=4162,hi:=4163); |  | 81:DI_UPS_Polnjenje:=Bit_0; | 81:ErrorComKlima[5].Code[6]:=Byte_0; |  |  | 4163:PMM.Phase[1].Current[5]:=Real_0;
mind_bool[82]:=DI_UpsA_BypassON; | mind[82]:=ErrorComKlima[5].Code[7]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[6],lo:=4164,hi:=4165); |  | 82:DI_UpsA_BypassON:=Bit_0; | 82:ErrorComKlima[5].Code[7]:=Byte_0; |  |  | 4165:PMM.Phase[1].Current[6]:=Real_0;
mind_bool[83]:=DI_UpsA_ERR; | mind[83]:=ErrorComKlima[5].Code[8]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[7],lo:=4166,hi:=4167); |  | 83:DI_UpsA_ERR:=Bit_0; | 83:ErrorComKlima[5].Code[8]:=Byte_0; |  |  | 4167:PMM.Phase[1].Current[7]:=Real_0;
mind_bool[84]:=DI_UpsB_BypassON; | mind[84]:=ErrorComKlima[5].Code[9]; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[8],lo:=4168,hi:=4169); |  | 84:DI_UpsB_BypassON:=Bit_0; | 84:ErrorComKlima[5].Code[9]:=Byte_0; |  |  | 4169:PMM.Phase[1].Current[8]:=Real_0;
mind_bool[85]:=DI_UpsB_ERR; | mind[85]:=ErrorComKlima[5].Status; |  |  | Read_Real(rVar:=PMM.Phase[1].Current[9],lo:=4170,hi:=4171); |  | 85:DI_UpsB_ERR:=Bit_0; | 85:ErrorComKlima[5].Status:=Word_01; |  |  | 4171:PMM.Phase[1].Current[9]:=Real_0;
mind_bool[86]:=DI_UQ11_OdcPMM_IZP; | mind[86]:=ErrorComKlima[6].Code[10]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[10],lo:=4172,hi:=4173); |  | 86:DI_UQ11_OdcPMM_IZP:=Bit_0; | 86:ErrorComKlima[6].Code[10]:=Byte_0; |  |  | 4173:PMM.Phase[2].Current[10]:=Real_0;
mind_bool[87]:=DI_UQ11_OdcPMM_ON; | mind[87]:=ErrorComKlima[6].Code[11]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[11],lo:=4174,hi:=4175); |  | 87:DI_UQ11_OdcPMM_ON:=Bit_0; | 87:ErrorComKlima[6].Code[11]:=Byte_0; |  |  | 4175:PMM.Phase[2].Current[11]:=Real_0;
mind_bool[88]:=DI_UQ12_OdcPMM_IZP; | mind[88]:=ErrorComKlima[6].Code[12]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[12],lo:=4176,hi:=4177); |  | 88:DI_UQ12_OdcPMM_IZP:=Bit_0; | 88:ErrorComKlima[6].Code[12]:=Byte_0; |  |  | 4177:PMM.Phase[2].Current[12]:=Real_0;
mind_bool[89]:=DI_UQ12_OdcPMM_ON; | mind[89]:=ErrorComKlima[6].Code[13]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[13],lo:=4178,hi:=4179); |  | 89:DI_UQ12_OdcPMM_ON:=Bit_0; | 89:ErrorComKlima[6].Code[13]:=Byte_0; |  |  | 4179:PMM.Phase[2].Current[13]:=Real_0;
mind_bool[90]:=DIN_A1Q11_OdcUpsA_IZP; | mind[90]:=ErrorComKlima[6].Code[14]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[14],lo:=4180,hi:=4181); |  | 90:DIN_A1Q11_OdcUpsA_IZP:=Bit_0; | 90:ErrorComKlima[6].Code[14]:=Byte_0; |  |  | 4181:PMM.Phase[2].Current[14]:=Real_0;
mind_bool[91]:=DIN_A1Q12_OdcByUpsA_IZP; | mind[91]:=ErrorComKlima[6].Code[15]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[15],lo:=4182,hi:=4183); |  | 91:DIN_A1Q12_OdcByUpsA_IZP:=Bit_0; | 91:ErrorComKlima[6].Code[15]:=Byte_0; |  |  | 4183:PMM.Phase[2].Current[15]:=Real_0;
mind_bool[92]:=DIN_A1Q13_OdcByA_IZP; | mind[92]:=ErrorComKlima[6].Code[1]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[16],lo:=4184,hi:=4185); |  | 92:DIN_A1Q13_OdcByA_IZP:=Bit_0; | 92:ErrorComKlima[6].Code[1]:=Byte_0; |  |  | 4185:PMM.Phase[2].Current[16]:=Real_0;
mind_bool[93]:=DIN_F201_OdcKl1ZE_IZP; | mind[93]:=ErrorComKlima[6].Code[2]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[17],lo:=4186,hi:=4187); |  | 93:DIN_F201_OdcKl1ZE_IZP:=Bit_0; | 93:ErrorComKlima[6].Code[2]:=Byte_0; |  |  | 4187:PMM.Phase[2].Current[17]:=Real_0;
mind_bool[94]:=DIN_F202_OdcKl2ZE_IZP; | mind[94]:=ErrorComKlima[6].Code[3]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[18],lo:=4188,hi:=4189); |  | 94:DIN_F202_OdcKl2ZE_IZP:=Bit_0; | 94:ErrorComKlima[6].Code[3]:=Byte_0; |  |  | 4189:PMM.Phase[2].Current[18]:=Real_0;
mind_bool[95]:=DIN_F203_OdcKl3ZE_IZP; | mind[95]:=ErrorComKlima[6].Code[4]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[19],lo:=4190,hi:=4191); |  | 95:DIN_F203_OdcKl3ZE_IZP:=Bit_0; | 95:ErrorComKlima[6].Code[4]:=Byte_0; |  |  | 4191:PMM.Phase[2].Current[19]:=Real_0;
mind_bool[96]:=DIN_F204_OdcKl4ZE_IZP; | mind[96]:=ErrorComKlima[6].Code[5]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[1],lo:=4192,hi:=4193); |  | 96:DIN_F204_OdcKl4ZE_IZP:=Bit_0; | 96:ErrorComKlima[6].Code[5]:=Byte_0; |  |  | 4193:PMM.Phase[2].Current[1]:=Real_0;
mind_bool[97]:=DIN_F205_OdcKl5aZE_IZP; | mind[97]:=ErrorComKlima[6].Code[6]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[20],lo:=4194,hi:=4195); |  | 97:DIN_F205_OdcKl5aZE_IZP:=Bit_0; | 97:ErrorComKlima[6].Code[6]:=Byte_0; |  |  | 4195:PMM.Phase[2].Current[20]:=Real_0;
mind_bool[98]:=DIN_F206_OdcKl5bZE_IZP; | mind[98]:=ErrorComKlima[6].Code[7]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[21],lo:=4196,hi:=4197); |  | 98:DIN_F206_OdcKl5bZE_IZP:=Bit_0; | 98:ErrorComKlima[6].Code[7]:=Byte_0; |  |  | 4197:PMM.Phase[2].Current[21]:=Real_0;
mind_bool[99]:=DIN_F207_OdcKl6aZE_IZP; | mind[99]:=ErrorComKlima[6].Code[8]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[22],lo:=4198,hi:=4199); |  | 99:DIN_F207_OdcKl6aZE_IZP:=Bit_0; | 99:ErrorComKlima[6].Code[8]:=Byte_0; |  |  | 4199:PMM.Phase[2].Current[22]:=Real_0;
mind_bool[100]:=DIN_F208_OdcKl6bZE_IZP; | mind[100]:=ErrorComKlima[6].Code[9]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[23],lo:=4200,hi:=4201); |  | 100:DIN_F208_OdcKl6bZE_IZP:=Bit_0; | 100:ErrorComKlima[6].Code[9]:=Byte_0; |  |  | 4201:PMM.Phase[2].Current[23]:=Real_0;
mind_bool[101]:=DIN_Klima1_ERR; | mind[101]:=ErrorComKlima[6].Status; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[24],lo:=4202,hi:=4203); |  | 101:DIN_Klima1_ERR:=Bit_0; | 101:ErrorComKlima[6].Status:=Word_01; |  |  | 4203:PMM.Phase[2].Current[24]:=Real_0;
mind_bool[102]:=DIN_Klima2_ERR; | mind[102]:=ErrorComPMM.Code[10]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[25],lo:=4204,hi:=4205); |  | 102:DIN_Klima2_ERR:=Bit_0; | 102:ErrorComPMM.Code[10]:=Byte_0; |  |  | 4205:PMM.Phase[2].Current[25]:=Real_0;
mind_bool[103]:=DIN_Klima3_ERR; | mind[103]:=ErrorComPMM.Code[11]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[26],lo:=4206,hi:=4207); |  | 103:DIN_Klima3_ERR:=Bit_0; | 103:ErrorComPMM.Code[11]:=Byte_0; |  |  | 4207:PMM.Phase[2].Current[26]:=Real_0;
mind_bool[104]:=DIN_Klima4_ERR; | mind[104]:=ErrorComPMM.Code[12]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[27],lo:=4208,hi:=4209); |  | 104:DIN_Klima4_ERR:=Bit_0; | 104:ErrorComPMM.Code[12]:=Byte_0; |  |  | 4209:PMM.Phase[2].Current[27]:=Real_0;
mind_bool[105]:=DIN_Klima5_ERR; | mind[105]:=ErrorComPMM.Code[13]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[28],lo:=4210,hi:=4211); |  | 105:DIN_Klima5_ERR:=Bit_0; | 105:ErrorComPMM.Code[13]:=Byte_0; |  |  | 4211:PMM.Phase[2].Current[28]:=Real_0;
mind_bool[106]:=DIN_Klima6_ERR; | mind[106]:=ErrorComPMM.Code[14]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[29],lo:=4212,hi:=4213); |  | 106:DIN_Klima6_ERR:=Bit_0; | 106:ErrorComPMM.Code[14]:=Byte_0; |  |  | 4213:PMM.Phase[2].Current[29]:=Real_0;
mind_bool[107]:=DIN_KlimaSplitPP_ERR; | mind[107]:=ErrorComPMM.Code[15]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[2],lo:=4214,hi:=4215); |  | 107:DIN_KlimaSplitPP_ERR:=Bit_0; | 107:ErrorComPMM.Code[15]:=Byte_0; |  |  | 4215:PMM.Phase[2].Current[2]:=Real_0;
mind_bool[108]:=DIN_PrenapA1_OK; | mind[108]:=ErrorComPMM.Code[1]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[30],lo:=4216,hi:=4217); |  | 108:DIN_PrenapA1_OK:=Bit_0; | 108:ErrorComPMM.Code[1]:=Byte_0; |  |  | 4217:PMM.Phase[2].Current[30]:=Real_0;
mind_bool[109]:=DIN_PrenapA2_OK; | mind[109]:=ErrorComPMM.Code[2]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[31],lo:=4218,hi:=4219); |  | 109:DIN_PrenapA2_OK:=Bit_0; | 109:ErrorComPMM.Code[2]:=Byte_0; |  |  | 4219:PMM.Phase[2].Current[31]:=Real_0;
mind_bool[110]:=DIN_Q101_OdcKlima1_IZP; | mind[110]:=ErrorComPMM.Code[3]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[32],lo:=4220,hi:=4221); |  | 110:DIN_Q101_OdcKlima1_IZP:=Bit_0; | 110:ErrorComPMM.Code[3]:=Byte_0; |  |  | 4221:PMM.Phase[2].Current[32]:=Real_0;
mind_bool[111]:=DIN_Q102_OdcKlima2_IZP; | mind[111]:=ErrorComPMM.Code[4]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[33],lo:=4222,hi:=4223); |  | 111:DIN_Q102_OdcKlima2_IZP:=Bit_0; | 111:ErrorComPMM.Code[4]:=Byte_0; |  |  | 4223:PMM.Phase[2].Current[33]:=Real_0;
mind_bool[112]:=DIN_Q103_OdcKlima3_IZP; | mind[112]:=ErrorComPMM.Code[5]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[34],lo:=4224,hi:=4225); |  | 112:DIN_Q103_OdcKlima3_IZP:=Bit_0; | 112:ErrorComPMM.Code[5]:=Byte_0; |  |  | 4225:PMM.Phase[2].Current[34]:=Real_0;
mind_bool[113]:=DIN_Q104_OdcKlima4_IZP; | mind[113]:=ErrorComPMM.Code[6]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[35],lo:=4226,hi:=4227); |  | 113:DIN_Q104_OdcKlima4_IZP:=Bit_0; | 113:ErrorComPMM.Code[6]:=Byte_0; |  |  | 4227:PMM.Phase[2].Current[35]:=Real_0;
mind_bool[114]:=DIN_Q105_OdcKlima5_IZP; | mind[114]:=ErrorComPMM.Code[7]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[36],lo:=4228,hi:=4229); |  | 114:DIN_Q105_OdcKlima5_IZP:=Bit_0; | 114:ErrorComPMM.Code[7]:=Byte_0; |  |  | 4229:PMM.Phase[2].Current[36]:=Real_0;
mind_bool[115]:=DIN_Q106_OdcKlima6_IZP; | mind[115]:=ErrorComPMM.Code[8]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[37],lo:=4230,hi:=4231); |  | 115:DIN_Q106_OdcKlima6_IZP:=Bit_0; | 115:ErrorComPMM.Code[8]:=Byte_0; |  |  | 4231:PMM.Phase[2].Current[37]:=Real_0;
mind_bool[116]:=DIN_Q107_OdcUsmSS2_IZP; | mind[116]:=ErrorComPMM.Code[9]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[38],lo:=4232,hi:=4233); |  | 116:DIN_Q107_OdcUsmSS2_IZP:=Bit_0; | 116:ErrorComPMM.Code[9]:=Byte_0; |  |  | 4233:PMM.Phase[2].Current[38]:=Real_0;
mind_bool[117]:=DIN_Q108_OdcUsmSS3_IZP; | mind[117]:=ErrorComPMM.Status; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[39],lo:=4234,hi:=4235); |  | 117:DIN_Q108_OdcUsmSS3_IZP:=Bit_0; | 117:ErrorComPMM.Status:=Word_01; |  |  | 4235:PMM.Phase[2].Current[39]:=Real_0;
mind_bool[118]:=DIN_UpsA_BypassON; | mind[118]:=ErrorComUPS[1].Code[10]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[3],lo:=4236,hi:=4237); |  | 118:DIN_UpsA_BypassON:=Bit_0; | 118:ErrorComUPS[1].Code[10]:=Byte_0; |  |  | 4237:PMM.Phase[2].Current[3]:=Real_0;
mind_bool[119]:=DIN_UpsA_ERR; | mind[119]:=ErrorComUPS[1].Code[11]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[40],lo:=4238,hi:=4239); |  | 119:DIN_UpsA_ERR:=Bit_0; | 119:ErrorComUPS[1].Code[11]:=Byte_0; |  |  | 4239:PMM.Phase[2].Current[40]:=Real_0;
mind_bool[120]:=DIN_UpsB_BypassON; | mind[120]:=ErrorComUPS[1].Code[12]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[41],lo:=4240,hi:=4241); |  | 120:DIN_UpsB_BypassON:=Bit_0; | 120:ErrorComUPS[1].Code[12]:=Byte_0; |  |  | 4241:PMM.Phase[2].Current[41]:=Real_0;
mind_bool[121]:=DIN_UpsB_ERR; | mind[121]:=ErrorComUPS[1].Code[13]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[42],lo:=4242,hi:=4243); |  | 121:DIN_UpsB_ERR:=Bit_0; | 121:ErrorComUPS[1].Code[13]:=Byte_0; |  |  | 4243:PMM.Phase[2].Current[42]:=Real_0;
mind_bool[122]:=DIN_UQ11_OdcPMM_IZP; | mind[122]:=ErrorComUPS[1].Code[14]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[4],lo:=4244,hi:=4245); |  | 122:DIN_UQ11_OdcPMM_IZP:=Bit_0; | 122:ErrorComUPS[1].Code[14]:=Byte_0; |  |  | 4245:PMM.Phase[2].Current[4]:=Real_0;
mind_bool[123]:=DIN_UQ12_OdcPMM_IZP; | mind[123]:=ErrorComUPS[1].Code[15]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[5],lo:=4246,hi:=4247); |  | 123:DIN_UQ12_OdcPMM_IZP:=Bit_0; | 123:ErrorComUPS[1].Code[15]:=Byte_0; |  |  | 4247:PMM.Phase[2].Current[5]:=Real_0;
mind_bool[124]:=DO_Klima1_Izklop; | mind[124]:=ErrorComUPS[1].Code[1]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[6],lo:=4248,hi:=4249); |  | 124:DO_Klima1_Izklop:=Bit_0; | 124:ErrorComUPS[1].Code[1]:=Byte_0; |  |  | 4249:PMM.Phase[2].Current[6]:=Real_0;
mind_bool[125]:=DO_Klima2_Izklop; | mind[125]:=ErrorComUPS[1].Code[2]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[7],lo:=4250,hi:=4251); |  | 125:DO_Klima2_Izklop:=Bit_0; | 125:ErrorComUPS[1].Code[2]:=Byte_0; |  |  | 4251:PMM.Phase[2].Current[7]:=Real_0;
mind_bool[126]:=DO_Klima3_Izklop; | mind[126]:=ErrorComUPS[1].Code[3]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[8],lo:=4252,hi:=4253); |  | 126:DO_Klima3_Izklop:=Bit_0; | 126:ErrorComUPS[1].Code[3]:=Byte_0; |  |  | 4253:PMM.Phase[2].Current[8]:=Real_0;
mind_bool[127]:=DO_Klima4_Izklop; | mind[127]:=ErrorComUPS[1].Code[4]; |  |  | Read_Real(rVar:=PMM.Phase[2].Current[9],lo:=4254,hi:=4255); |  | 127:DO_Klima4_Izklop:=Bit_0; | 127:ErrorComUPS[1].Code[4]:=Byte_0; |  |  | 4255:PMM.Phase[2].Current[9]:=Real_0;
mind_bool[128]:=DO_Klima5_Izklop; | mind[128]:=ErrorComUPS[1].Code[5]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[10],lo:=4256,hi:=4257); |  | 128:DO_Klima5_Izklop:=Bit_0; | 128:ErrorComUPS[1].Code[5]:=Byte_0; |  |  | 4257:PMM.Phase[3].Current[10]:=Real_0;
mind_bool[129]:=DO_Klima6_Izklop; | mind[129]:=ErrorComUPS[1].Code[6]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[11],lo:=4258,hi:=4259); |  | 129:DO_Klima6_Izklop:=Bit_0; | 129:ErrorComUPS[1].Code[6]:=Byte_0; |  |  | 4259:PMM.Phase[3].Current[11]:=Real_0;
mind_bool[130]:=ErrComKlima[1]; | mind[130]:=ErrorComUPS[1].Code[7]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[12],lo:=4260,hi:=4261); |  | 130:ErrComKlima[1]:=Bit_0; | 130:ErrorComUPS[1].Code[7]:=Byte_0; |  |  | 4261:PMM.Phase[3].Current[12]:=Real_0;
mind_bool[131]:=ErrComKlima[2]; | mind[131]:=ErrorComUPS[1].Code[8]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[13],lo:=4262,hi:=4263); |  | 131:ErrComKlima[2]:=Bit_0; | 131:ErrorComUPS[1].Code[8]:=Byte_0; |  |  | 4263:PMM.Phase[3].Current[13]:=Real_0;
mind_bool[132]:=ErrComKlima[3]; | mind[132]:=ErrorComUPS[1].Code[9]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[14],lo:=4264,hi:=4265); |  | 132:ErrComKlima[3]:=Bit_0; | 132:ErrorComUPS[1].Code[9]:=Byte_0; |  |  | 4265:PMM.Phase[3].Current[14]:=Real_0;
mind_bool[133]:=ErrComKlima[4]; | mind[133]:=ErrorComUPS[1].Status; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[15],lo:=4266,hi:=4267); |  | 133:ErrComKlima[4]:=Bit_0; | 133:ErrorComUPS[1].Status:=Word_01; |  |  | 4267:PMM.Phase[3].Current[15]:=Real_0;
mind_bool[134]:=ErrComKlima[5]; | mind[134]:=ErrorComUPS[2].Code[10]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[16],lo:=4268,hi:=4269); |  | 134:ErrComKlima[5]:=Bit_0; | 134:ErrorComUPS[2].Code[10]:=Byte_0; |  |  | 4269:PMM.Phase[3].Current[16]:=Real_0;
mind_bool[135]:=ErrComKlima[6]; | mind[135]:=ErrorComUPS[2].Code[11]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[17],lo:=4270,hi:=4271); |  | 135:ErrComKlima[6]:=Bit_0; | 135:ErrorComUPS[2].Code[11]:=Byte_0; |  |  | 4271:PMM.Phase[3].Current[17]:=Real_0;
mind_bool[136]:=ErrCommScada; | mind[136]:=ErrorComUPS[2].Code[12]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[18],lo:=4272,hi:=4273); |  | 136:ErrCommScada:=Bit_0; | 136:ErrorComUPS[2].Code[12]:=Byte_0; |  |  | 4273:PMM.Phase[3].Current[18]:=Real_0;
mind_bool[137]:=ErrComPanelPLC; | mind[137]:=ErrorComUPS[2].Code[13]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[19],lo:=4274,hi:=4275); |  | 137:ErrComPanelPLC:=Bit_0; | 137:ErrorComUPS[2].Code[13]:=Byte_0; |  |  | 4275:PMM.Phase[3].Current[19]:=Real_0;
mind_bool[138]:=ErrComPMM; | mind[138]:=ErrorComUPS[2].Code[14]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[1],lo:=4276,hi:=4277); |  | 138:ErrComPMM:=Bit_0; | 138:ErrorComUPS[2].Code[14]:=Byte_0; |  |  | 4277:PMM.Phase[3].Current[1]:=Real_0;
mind_bool[139]:=ErrComPort2; | mind[139]:=ErrorComUPS[2].Code[15]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[20],lo:=4278,hi:=4279); |  | 139:ErrComPort2:=Bit_0; | 139:ErrorComUPS[2].Code[15]:=Byte_0; |  |  | 4279:PMM.Phase[3].Current[20]:=Real_0;
mind_bool[140]:=ErrComPort3; | mind[140]:=ErrorComUPS[2].Code[1]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[21],lo:=4280,hi:=4281); |  | 140:ErrComPort3:=Bit_0; | 140:ErrorComUPS[2].Code[1]:=Byte_0; |  |  | 4281:PMM.Phase[3].Current[21]:=Real_0;
mind_bool[141]:=ErrComPort4; | mind[141]:=ErrorComUPS[2].Code[2]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[22],lo:=4282,hi:=4283); |  | 141:ErrComPort4:=Bit_0; | 141:ErrorComUPS[2].Code[2]:=Byte_0; |  |  | 4283:PMM.Phase[3].Current[22]:=Real_0;
mind_bool[142]:=ErrComUPS[1]; | mind[142]:=ErrorComUPS[2].Code[3]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[23],lo:=4284,hi:=4285); |  | 142:ErrComUPS[1]:=Bit_0; | 142:ErrorComUPS[2].Code[3]:=Byte_0; |  |  | 4285:PMM.Phase[3].Current[23]:=Real_0;
mind_bool[143]:=ErrComUPS[2]; | mind[143]:=ErrorComUPS[2].Code[4]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[24],lo:=4286,hi:=4287); |  | 143:ErrComUPS[2]:=Bit_0; | 143:ErrorComUPS[2].Code[4]:=Byte_0; |  |  | 4287:PMM.Phase[3].Current[24]:=Real_0;
mind_bool[144]:=ErrorComKlima[1].Error; | mind[144]:=ErrorComUPS[2].Code[5]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[25],lo:=4288,hi:=4289); |  | 144:ErrorComKlima[1].Error:=Bit_0; | 144:ErrorComUPS[2].Code[5]:=Byte_0; |  |  | 4289:PMM.Phase[3].Current[25]:=Real_0;
mind_bool[145]:=ErrorComKlima[2].Error; | mind[145]:=ErrorComUPS[2].Code[6]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[26],lo:=4290,hi:=4291); |  | 145:ErrorComKlima[2].Error:=Bit_0; | 145:ErrorComUPS[2].Code[6]:=Byte_0; |  |  | 4291:PMM.Phase[3].Current[26]:=Real_0;
mind_bool[146]:=ErrorComKlima[3].Error; | mind[146]:=ErrorComUPS[2].Code[7]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[27],lo:=4292,hi:=4293); |  | 146:ErrorComKlima[3].Error:=Bit_0; | 146:ErrorComUPS[2].Code[7]:=Byte_0; |  |  | 4293:PMM.Phase[3].Current[27]:=Real_0;
mind_bool[147]:=ErrorComKlima[4].Error; | mind[147]:=ErrorComUPS[2].Code[8]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[28],lo:=4294,hi:=4295); |  | 147:ErrorComKlima[4].Error:=Bit_0; | 147:ErrorComUPS[2].Code[8]:=Byte_0; |  |  | 4295:PMM.Phase[3].Current[28]:=Real_0;
mind_bool[148]:=ErrorComKlima[5].Error; | mind[148]:=ErrorComUPS[2].Code[9]; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[29],lo:=4296,hi:=4297); |  | 148:ErrorComKlima[5].Error:=Bit_0; | 148:ErrorComUPS[2].Code[9]:=Byte_0; |  |  | 4297:PMM.Phase[3].Current[29]:=Real_0;
mind_bool[149]:=ErrorComKlima[6].Error; | mind[149]:=ErrorComUPS[2].Status; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[2],lo:=4298,hi:=4299); |  | 149:ErrorComKlima[6].Error:=Bit_0; | 149:ErrorComUPS[2].Status:=Word_01; |  |  | 4299:PMM.Phase[3].Current[2]:=Real_0;
mind_bool[150]:=ErrorComPMM.Error; | mind[150]:=Klima[1].GrelecStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[30],lo:=4300,hi:=4301); |  | 150:ErrorComPMM.Error:=Bit_0; | 150:Klima[1].GrelecStatus:=Byte_0; |  |  | 4301:PMM.Phase[3].Current[30]:=Real_0;
mind_bool[151]:=ErrorComUPS[1].Error; | mind[151]:=Klima[1].IzhodniVentStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[31],lo:=4302,hi:=4303); |  | 151:ErrorComUPS[1].Error:=Bit_0; | 151:Klima[1].IzhodniVentStatus:=Byte_0; |  |  | 4303:PMM.Phase[3].Current[31]:=Real_0;
mind_bool[152]:=ErrorComUPS[2].Error; | mind[152]:=Klima[1].KompresorStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[32],lo:=4304,hi:=4305); |  | 152:ErrorComUPS[2].Error:=Bit_0; | 152:Klima[1].KompresorStatus:=Byte_0; |  |  | 4305:PMM.Phase[3].Current[32]:=Real_0;
mind_bool[153]:=Klima1Errors[10]; | mind[153]:=Klima[1].VlazilecStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[33],lo:=4306,hi:=4307); |  | 153:Klima1Errors[10]:=Bit_0; | 153:Klima[1].VlazilecStatus:=Byte_0; |  |  | 4307:PMM.Phase[3].Current[33]:=Real_0;
mind_bool[154]:=Klima1Errors[11]; | mind[154]:=Klima[2].GrelecStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[34],lo:=4308,hi:=4309); |  | 154:Klima1Errors[11]:=Bit_0; | 154:Klima[2].GrelecStatus:=Byte_0; |  |  | 4309:PMM.Phase[3].Current[34]:=Real_0;
mind_bool[155]:=Klima1Errors[12]; | mind[155]:=Klima[2].IzhodniVentStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[35],lo:=4310,hi:=4311); |  | 155:Klima1Errors[12]:=Bit_0; | 155:Klima[2].IzhodniVentStatus:=Byte_0; |  |  | 4311:PMM.Phase[3].Current[35]:=Real_0;
mind_bool[156]:=Klima1Errors[13]; | mind[156]:=Klima[2].KompresorStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[36],lo:=4312,hi:=4313); |  | 156:Klima1Errors[13]:=Bit_0; | 156:Klima[2].KompresorStatus:=Byte_0; |  |  | 4313:PMM.Phase[3].Current[36]:=Real_0;
mind_bool[157]:=Klima1Errors[14]; | mind[157]:=Klima[2].VlazilecStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[37],lo:=4314,hi:=4315); |  | 157:Klima1Errors[14]:=Bit_0; | 157:Klima[2].VlazilecStatus:=Byte_0; |  |  | 4315:PMM.Phase[3].Current[37]:=Real_0;
mind_bool[158]:=Klima1Errors[15]; | mind[158]:=Klima[3].GrelecStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[38],lo:=4316,hi:=4317); |  | 158:Klima1Errors[15]:=Bit_0; | 158:Klima[3].GrelecStatus:=Byte_0; |  |  | 4317:PMM.Phase[3].Current[38]:=Real_0;
mind_bool[159]:=Klima1Errors[16]; | mind[159]:=Klima[3].IzhodniVentStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[39],lo:=4318,hi:=4319); |  | 159:Klima1Errors[16]:=Bit_0; | 159:Klima[3].IzhodniVentStatus:=Byte_0; |  |  | 4319:PMM.Phase[3].Current[39]:=Real_0;
mind_bool[160]:=Klima1Errors[17]; | mind[160]:=Klima[3].KompresorStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[3],lo:=4320,hi:=4321); |  | 160:Klima1Errors[17]:=Bit_0; | 160:Klima[3].KompresorStatus:=Byte_0; |  |  | 4321:PMM.Phase[3].Current[3]:=Real_0;
mind_bool[161]:=Klima1Errors[18]; | mind[161]:=Klima[3].VlazilecStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[40],lo:=4322,hi:=4323); |  | 161:Klima1Errors[18]:=Bit_0; | 161:Klima[3].VlazilecStatus:=Byte_0; |  |  | 4323:PMM.Phase[3].Current[40]:=Real_0;
mind_bool[162]:=Klima1Errors[19]; | mind[162]:=Klima[4].GrelecStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[41],lo:=4324,hi:=4325); |  | 162:Klima1Errors[19]:=Bit_0; | 162:Klima[4].GrelecStatus:=Byte_0; |  |  | 4325:PMM.Phase[3].Current[41]:=Real_0;
mind_bool[163]:=Klima1Errors[1]; | mind[163]:=Klima[4].IzhodniVentStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[42],lo:=4326,hi:=4327); |  | 163:Klima1Errors[1]:=Bit_0; | 163:Klima[4].IzhodniVentStatus:=Byte_0; |  |  | 4327:PMM.Phase[3].Current[42]:=Real_0;
mind_bool[164]:=Klima1Errors[20]; | mind[164]:=Klima[4].KompresorStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[4],lo:=4328,hi:=4329); |  | 164:Klima1Errors[20]:=Bit_0; | 164:Klima[4].KompresorStatus:=Byte_0; |  |  | 4329:PMM.Phase[3].Current[4]:=Real_0;
mind_bool[165]:=Klima1Errors[21]; | mind[165]:=Klima[4].VlazilecStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[5],lo:=4330,hi:=4331); |  | 165:Klima1Errors[21]:=Bit_0; | 165:Klima[4].VlazilecStatus:=Byte_0; |  |  | 4331:PMM.Phase[3].Current[5]:=Real_0;
mind_bool[166]:=Klima1Errors[22]; | mind[166]:=Klima[5].GrelecStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[6],lo:=4332,hi:=4333); |  | 166:Klima1Errors[22]:=Bit_0; | 166:Klima[5].GrelecStatus:=Byte_0; |  |  | 4333:PMM.Phase[3].Current[6]:=Real_0;
mind_bool[167]:=Klima1Errors[23]; | mind[167]:=Klima[5].IzhodniVentStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[7],lo:=4334,hi:=4335); |  | 167:Klima1Errors[23]:=Bit_0; | 167:Klima[5].IzhodniVentStatus:=Byte_0; |  |  | 4335:PMM.Phase[3].Current[7]:=Real_0;
mind_bool[168]:=Klima1Errors[24]; | mind[168]:=Klima[5].KompresorStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[8],lo:=4336,hi:=4337); |  | 168:Klima1Errors[24]:=Bit_0; | 168:Klima[5].KompresorStatus:=Byte_0; |  |  | 4337:PMM.Phase[3].Current[8]:=Real_0;
mind_bool[169]:=Klima1Errors[25]; | mind[169]:=Klima[5].VlazilecStatus; |  |  | Read_Real(rVar:=PMM.Phase[3].Current[9],lo:=4338,hi:=4339); |  | 169:Klima1Errors[25]:=Bit_0; | 169:Klima[5].VlazilecStatus:=Byte_0; |  |  | 4339:PMM.Phase[3].Current[9]:=Real_0;
mind_bool[170]:=Klima1Errors[26]; | mind[170]:=Klima[6].GrelecStatus; |  |  | Read_Real(rVar:=PMM.PowerFactorSys,lo:=4340,hi:=4341); |  | 170:Klima1Errors[26]:=Bit_0; | 170:Klima[6].GrelecStatus:=Byte_0; |  |  | 4341:PMM.PowerFactorSys:=Real_0;
mind_bool[171]:=Klima1Errors[27]; | mind[171]:=Klima[6].IzhodniVentStatus; |  |  | Read_Real(rVar:=PMM.ReactiveEnergyConsumed_kVARh,lo:=4342,hi:=4343); |  | 171:Klima1Errors[27]:=Bit_0; | 171:Klima[6].IzhodniVentStatus:=Byte_0; |  |  | 4343:PMM.ReactiveEnergyConsumed_kVARh:=Real_0;
mind_bool[172]:=Klima1Errors[28]; | mind[172]:=Klima[6].KompresorStatus; |  |  | Read_Real(rVar:=PMM.ReactivePowerPhaseA,lo:=4344,hi:=4345); |  | 172:Klima1Errors[28]:=Bit_0; | 172:Klima[6].KompresorStatus:=Byte_0; |  |  | 4345:PMM.ReactivePowerPhaseA:=Real_0;
mind_bool[173]:=Klima1Errors[29]; | mind[173]:=Klima[6].VlazilecStatus; |  |  | Read_Real(rVar:=PMM.ReactivePowerPhaseB,lo:=4346,hi:=4347); |  | 173:Klima1Errors[29]:=Bit_0; | 173:Klima[6].VlazilecStatus:=Byte_0; |  |  | 4347:PMM.ReactivePowerPhaseB:=Real_0;
mind_bool[174]:=Klima1Errors[2]; | mind[174]:=MrezaIzpadVklopDelay[1]; |  |  | Read_Real(rVar:=PMM.ReactivePowerPhaseC,lo:=4348,hi:=4349); |  | 174:Klima1Errors[2]:=Bit_0; | 174:MrezaIzpadVklopDelay[1]:=Word_01; |  |  | 4349:PMM.ReactivePowerPhaseC:=Real_0;
mind_bool[175]:=Klima1Errors[30]; | mind[175]:=MrezaIzpadVklopDelay[2]; |  |  | Read_Real(rVar:=PMM.TotalActivePower_kW,lo:=4350,hi:=4351); |  | 175:Klima1Errors[30]:=Bit_0; | 175:MrezaIzpadVklopDelay[2]:=Word_01; |  |  | 4351:PMM.TotalActivePower_kW:=Real_0;
mind_bool[176]:=Klima1Errors[31]; | mind[176]:=MrezaIzpadVklopDelay[3]; |  |  | Read_Real(rVar:=PMM.TotalAparentPower_kVA,lo:=4352,hi:=4353); |  | 176:Klima1Errors[31]:=Bit_0; | 176:MrezaIzpadVklopDelay[3]:=Word_01; |  |  | 4353:PMM.TotalAparentPower_kVA:=Real_0;
mind_bool[177]:=Klima1Errors[32]; | mind[177]:=MrezaIzpadVklopDelay[4]; |  |  | Read_Real(rVar:=PMM.TotalPowerFactor,lo:=4354,hi:=4355); |  | 177:Klima1Errors[32]:=Bit_0; | 177:MrezaIzpadVklopDelay[4]:=Word_01; |  |  | 4355:PMM.TotalPowerFactor:=Real_0;
mind_bool[178]:=Klima1Errors[33]; | mind[178]:=MrezaIzpadVklopDelay[5]; |  |  | Read_Real(rVar:=PMM.TotalReactivePower_kVAR,lo:=4356,hi:=4357); |  | 178:Klima1Errors[33]:=Bit_0; | 178:MrezaIzpadVklopDelay[5]:=Word_01; |  |  | 4357:PMM.TotalReactivePower_kVAR:=Real_0;
mind_bool[179]:=Klima1Errors[34]; | mind[179]:=MrezaIzpadVklopDelay[6]; |  |  | Read_Real(rVar:=PMM.VirA_fsys,lo:=4358,hi:=4359); |  | 179:Klima1Errors[34]:=Bit_0; | 179:MrezaIzpadVklopDelay[6]:=Word_01; |  |  | 4359:PMM.VirA_fsys:=Real_0;
mind_bool[180]:=Klima1Errors[35]; | mind[180]:=PMM.AlarmPhase[1].C01_16_60to80; |  |  | Read_Real(rVar:=PMM.VirA_Isys,lo:=4360,hi:=4361); |  | 180:Klima1Errors[35]:=Bit_0; | 180:PMM.AlarmPhase[1].C01_16_60to80:=Word_01; |  |  | 4361:PMM.VirA_Isys:=Real_0;
mind_bool[181]:=Klima1Errors[3]; | mind[181]:=PMM.AlarmPhase[1].C01_16_over80; |  |  | Read_Real(rVar:=PMM.VirA_PFsys,lo:=4362,hi:=4363); |  | 181:Klima1Errors[3]:=Bit_0; | 181:PMM.AlarmPhase[1].C01_16_over80:=Word_01; |  |  | 4363:PMM.VirA_PFsys:=Real_0;
mind_bool[182]:=Klima1Errors[4]; | mind[182]:=PMM.AlarmPhase[1].C17_32_60to80; |  |  | Read_Real(rVar:=PMM.VirA_Psys,lo:=4364,hi:=4365); |  | 182:Klima1Errors[4]:=Bit_0; | 182:PMM.AlarmPhase[1].C17_32_60to80:=Word_01; |  |  | 4365:PMM.VirA_Psys:=Real_0;
mind_bool[183]:=Klima1Errors[5]; | mind[183]:=PMM.AlarmPhase[1].C17_32_over80; |  |  | Read_Real(rVar:=PMM.VirA_Qsys,lo:=4366,hi:=4367); |  | 183:Klima1Errors[5]:=Bit_0; | 183:PMM.AlarmPhase[1].C17_32_over80:=Word_01; |  |  | 4367:PMM.VirA_Qsys:=Real_0;
mind_bool[184]:=Klima1Errors[6]; | mind[184]:=PMM.AlarmPhase[1].C33_42_60to80; |  |  | Read_Real(rVar:=PMM.VirA_Ssys,lo:=4368,hi:=4369); |  | 184:Klima1Errors[6]:=Bit_0; | 184:PMM.AlarmPhase[1].C33_42_60to80:=Word_01; |  |  | 4369:PMM.VirA_Ssys:=Real_0;
mind_bool[185]:=Klima1Errors[7]; | mind[185]:=PMM.AlarmPhase[1].C33_42_over80; |  |  | Read_Real(rVar:=PMM.VirA_Usys,lo:=4370,hi:=4371); |  | 185:Klima1Errors[7]:=Bit_0; | 185:PMM.AlarmPhase[1].C33_42_over80:=Word_01; |  |  | 4371:PMM.VirA_Usys:=Real_0;
mind_bool[186]:=Klima1Errors[8]; | mind[186]:=PMM.AlarmPhase[2].C01_16_60to80; |  |  | Read_Real(rVar:=PMM.VirB_fsys,lo:=4372,hi:=4373); |  | 186:Klima1Errors[8]:=Bit_0; | 186:PMM.AlarmPhase[2].C01_16_60to80:=Word_01; |  |  | 4373:PMM.VirB_fsys:=Real_0;
mind_bool[187]:=Klima1Errors[9]; | mind[187]:=PMM.AlarmPhase[2].C01_16_over80; |  |  | Read_Real(rVar:=PMM.VirB_Isys,lo:=4374,hi:=4375); |  | 187:Klima1Errors[9]:=Bit_0; | 187:PMM.AlarmPhase[2].C01_16_over80:=Word_01; |  |  | 4375:PMM.VirB_Isys:=Real_0;
mind_bool[188]:=Klima2Errors[10]; | mind[188]:=PMM.AlarmPhase[2].C17_32_60to80; |  |  | Read_Real(rVar:=PMM.VirB_PFsys,lo:=4376,hi:=4377); |  | 188:Klima2Errors[10]:=Bit_0; | 188:PMM.AlarmPhase[2].C17_32_60to80:=Word_01; |  |  | 4377:PMM.VirB_PFsys:=Real_0;
mind_bool[189]:=Klima2Errors[11]; | mind[189]:=PMM.AlarmPhase[2].C17_32_over80; |  |  | Read_Real(rVar:=PMM.VirB_Psys,lo:=4378,hi:=4379); |  | 189:Klima2Errors[11]:=Bit_0; | 189:PMM.AlarmPhase[2].C17_32_over80:=Word_01; |  |  | 4379:PMM.VirB_Psys:=Real_0;
mind_bool[190]:=Klima2Errors[12]; | mind[190]:=PMM.AlarmPhase[2].C33_42_60to80; |  |  | Read_Real(rVar:=PMM.VirB_Qsys,lo:=4380,hi:=4381); |  | 190:Klima2Errors[12]:=Bit_0; | 190:PMM.AlarmPhase[2].C33_42_60to80:=Word_01; |  |  | 4381:PMM.VirB_Qsys:=Real_0;
mind_bool[191]:=Klima2Errors[13]; | mind[191]:=PMM.AlarmPhase[2].C33_42_over80; |  |  | Read_Real(rVar:=PMM.VirB_Ssys,lo:=4382,hi:=4383); |  | 191:Klima2Errors[13]:=Bit_0; | 191:PMM.AlarmPhase[2].C33_42_over80:=Word_01; |  |  | 4383:PMM.VirB_Ssys:=Real_0;
mind_bool[192]:=Klima2Errors[14]; | mind[192]:=PMM.AlarmPhase[3].C01_16_60to80; |  |  | Read_Real(rVar:=PMM.VirB_Usys,lo:=4384,hi:=4385); |  | 192:Klima2Errors[14]:=Bit_0; | 192:PMM.AlarmPhase[3].C01_16_60to80:=Word_01; |  |  | 4385:PMM.VirB_Usys:=Real_0;
mind_bool[193]:=Klima2Errors[15]; | mind[193]:=PMM.AlarmPhase[3].C01_16_over80; |  |  | Read_Real(rVar:=PMM.VirBActiveEnergyConsumed_kWh,lo:=4386,hi:=4387); |  | 193:Klima2Errors[15]:=Bit_0; | 193:PMM.AlarmPhase[3].C01_16_over80:=Word_01; |  |  | 4387:PMM.VirBActiveEnergyConsumed_kWh:=Real_0;
mind_bool[194]:=Klima2Errors[16]; | mind[194]:=PMM.AlarmPhase[3].C17_32_60to80; |  |  | Read_Real(rVar:=PMM.VirBActivePowerPhaseA_kW,lo:=4388,hi:=4389); |  | 194:Klima2Errors[16]:=Bit_0; | 194:PMM.AlarmPhase[3].C17_32_60to80:=Word_01; |  |  | 4389:PMM.VirBActivePowerPhaseA_kW:=Real_0;
mind_bool[195]:=Klima2Errors[17]; | mind[195]:=PMM.AlarmPhase[3].C17_32_over80; |  |  | Read_Real(rVar:=PMM.VirBActivePowerPhaseB_kW,lo:=4390,hi:=4391); |  | 195:Klima2Errors[17]:=Bit_0; | 195:PMM.AlarmPhase[3].C17_32_over80:=Word_01; |  |  | 4391:PMM.VirBActivePowerPhaseB_kW:=Real_0;
mind_bool[196]:=Klima2Errors[18]; | mind[196]:=PMM.AlarmPhase[3].C33_42_60to80; |  |  | Read_Real(rVar:=PMM.VirBActivePowerPhaseC_kW,lo:=4392,hi:=4393); |  | 196:Klima2Errors[18]:=Bit_0; | 196:PMM.AlarmPhase[3].C33_42_60to80:=Word_01; |  |  | 4393:PMM.VirBActivePowerPhaseC_kW:=Real_0;
mind_bool[197]:=Klima2Errors[19]; | mind[197]:=PMM.AlarmPhase[3].C33_42_over80; |  |  | Read_Real(rVar:=PMM.VirBAparentPowerPhaseA,lo:=4394,hi:=4395); |  | 197:Klima2Errors[19]:=Bit_0; | 197:PMM.AlarmPhase[3].C33_42_over80:=Word_01; |  |  | 4395:PMM.VirBAparentPowerPhaseA:=Real_0;
mind_bool[198]:=Klima2Errors[1]; | mind[198]:=Qstanje[10]; |  |  | Read_Real(rVar:=PMM.VirBAparentPowerPhaseB,lo:=4396,hi:=4397); |  | 198:Klima2Errors[1]:=Bit_0; | 198:Qstanje[10]:=Byte_0; |  |  | 4397:PMM.VirBAparentPowerPhaseB:=Real_0;
mind_bool[199]:=Klima2Errors[20]; | mind[199]:=Qstanje[11]; |  |  | Read_Real(rVar:=PMM.VirBAparentPowerPhaseC,lo:=4398,hi:=4399); |  | 199:Klima2Errors[20]:=Bit_0; | 199:Qstanje[11]:=Byte_0; |  |  | 4399:PMM.VirBAparentPowerPhaseC:=Real_0;
mind_bool[200]:=Klima2Errors[21]; | mind[200]:=Qstanje[12]; |  |  | Read_Real(rVar:=PMM.VirBAverageCurrent_A,lo:=4400,hi:=4401); |  | 200:Klima2Errors[21]:=Bit_0; | 200:Qstanje[12]:=Byte_0; |  |  | 4401:PMM.VirBAverageCurrent_A:=Real_0;
mind_bool[201]:=Klima2Errors[22]; | mind[201]:=Qstanje[13]; |  |  | Read_Real(rVar:=PMM.VirBAveragePhaseToNeutral_V,lo:=4402,hi:=4403); |  | 201:Klima2Errors[22]:=Bit_0; | 201:Qstanje[13]:=Byte_0; |  |  | 4403:PMM.VirBAveragePhaseToNeutral_V:=Real_0;
mind_bool[202]:=Klima2Errors[23]; | mind[202]:=Qstanje[14]; |  |  | Read_Real(rVar:=PMM.VirBAveragePhaseToPhase_V,lo:=4404,hi:=4405); |  | 202:Klima2Errors[23]:=Bit_0; | 202:Qstanje[14]:=Byte_0; |  |  | 4405:PMM.VirBAveragePhaseToPhase_V:=Real_0;
mind_bool[203]:=Klima2Errors[24]; | mind[203]:=Qstanje[15]; |  |  | Read_Real(rVar:=PMM.VirBCurrentInPhaseA_A,lo:=4406,hi:=4407); |  | 203:Klima2Errors[24]:=Bit_0; | 203:Qstanje[15]:=Byte_0; |  |  | 4407:PMM.VirBCurrentInPhaseA_A:=Real_0;
mind_bool[204]:=Klima2Errors[25]; | mind[204]:=Qstanje[16]; |  |  | Read_Real(rVar:=PMM.VirBCurrentInPhaseB_A,lo:=4408,hi:=4409); |  | 204:Klima2Errors[25]:=Bit_0; | 204:Qstanje[16]:=Byte_0; |  |  | 4409:PMM.VirBCurrentInPhaseB_A:=Real_0;
mind_bool[205]:=Klima2Errors[26]; | mind[205]:=Qstanje[17]; |  |  | Read_Real(rVar:=PMM.VirBCurrentInPhaseC_A,lo:=4410,hi:=4411); |  | 205:Klima2Errors[26]:=Bit_0; | 205:Qstanje[17]:=Byte_0; |  |  | 4411:PMM.VirBCurrentInPhaseC_A:=Real_0;
mind_bool[206]:=Klima2Errors[27]; | mind[206]:=Qstanje[18]; |  |  | Read_Real(rVar:=PMM.VirBFrequency_Hz,lo:=4412,hi:=4413); |  | 206:Klima2Errors[27]:=Bit_0; | 206:Qstanje[18]:=Byte_0; |  |  | 4413:PMM.VirBFrequency_Hz:=Real_0;
mind_bool[207]:=Klima2Errors[28]; | mind[207]:=Qstanje[19]; |  |  | Read_Real(rVar:=PMM.VirBPowerFactorSys,lo:=4414,hi:=4415); |  | 207:Klima2Errors[28]:=Bit_0; | 207:Qstanje[19]:=Byte_0; |  |  | 4415:PMM.VirBPowerFactorSys:=Real_0;
mind_bool[208]:=Klima2Errors[29]; | mind[208]:=Qstanje[1]; |  |  | Read_Real(rVar:=PMM.VirBReactiveEnergyConsumed_kVARh,lo:=4416,hi:=4417); |  | 208:Klima2Errors[29]:=Bit_0; | 208:Qstanje[1]:=Byte_0; |  |  | 4417:PMM.VirBReactiveEnergyConsumed_kVARh:=Real_0;
mind_bool[209]:=Klima2Errors[2]; | mind[209]:=Qstanje[20]; |  |  | Read_Real(rVar:=PMM.VirBReactivePowerPhaseA,lo:=4418,hi:=4419); |  | 209:Klima2Errors[2]:=Bit_0; | 209:Qstanje[20]:=Byte_0; |  |  | 4419:PMM.VirBReactivePowerPhaseA:=Real_0;
mind_bool[210]:=Klima2Errors[30]; | mind[210]:=Qstanje[21]; |  |  | Read_Real(rVar:=PMM.VirBReactivePowerPhaseB,lo:=4420,hi:=4421); |  | 210:Klima2Errors[30]:=Bit_0; | 210:Qstanje[21]:=Byte_0; |  |  | 4421:PMM.VirBReactivePowerPhaseB:=Real_0;
mind_bool[211]:=Klima2Errors[31]; | mind[211]:=Qstanje[22]; |  |  | Read_Real(rVar:=PMM.VirBReactivePowerPhaseC,lo:=4422,hi:=4423); |  | 211:Klima2Errors[31]:=Bit_0; | 211:Qstanje[22]:=Byte_0; |  |  | 4423:PMM.VirBReactivePowerPhaseC:=Real_0;
mind_bool[212]:=Klima2Errors[32]; | mind[212]:=Qstanje[23]; |  |  | Read_Real(rVar:=PMM.VirBTotalActivePower_kW,lo:=4424,hi:=4425); |  | 212:Klima2Errors[32]:=Bit_0; | 212:Qstanje[23]:=Byte_0; |  |  | 4425:PMM.VirBTotalActivePower_kW:=Real_0;
mind_bool[213]:=Klima2Errors[33]; | mind[213]:=Qstanje[24]; |  |  | Read_Real(rVar:=PMM.VirBTotalAparentPower_kVA,lo:=4426,hi:=4427); |  | 213:Klima2Errors[33]:=Bit_0; | 213:Qstanje[24]:=Byte_0; |  |  | 4427:PMM.VirBTotalAparentPower_kVA:=Real_0;
mind_bool[214]:=Klima2Errors[34]; | mind[214]:=Qstanje[25]; |  |  | Read_Real(rVar:=PMM.VirBTotalPowerFactor,lo:=4428,hi:=4429); |  | 214:Klima2Errors[34]:=Bit_0; | 214:Qstanje[25]:=Byte_0; |  |  | 4429:PMM.VirBTotalPowerFactor:=Real_0;
mind_bool[215]:=Klima2Errors[35]; | mind[215]:=Qstanje[26]; |  |  | Read_Real(rVar:=PMM.VirBTotalReactivePower_kVAR,lo:=4430,hi:=4431); |  | 215:Klima2Errors[35]:=Bit_0; | 215:Qstanje[26]:=Byte_0; |  |  | 4431:PMM.VirBTotalReactivePower_kVAR:=Real_0;
mind_bool[216]:=Klima2Errors[3]; | mind[216]:=Qstanje[27]; |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseAB_V,lo:=4432,hi:=4433); |  | 216:Klima2Errors[3]:=Bit_0; | 216:Qstanje[27]:=Byte_0; |  |  | 4433:PMM.VirBVoltageBetweenPhaseAB_V:=Real_0;
mind_bool[217]:=Klima2Errors[4]; | mind[217]:=Qstanje[28]; |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseAN_V,lo:=4434,hi:=4435); |  | 217:Klima2Errors[4]:=Bit_0; | 217:Qstanje[28]:=Byte_0; |  |  | 4435:PMM.VirBVoltageBetweenPhaseAN_V:=Real_0;
mind_bool[218]:=Klima2Errors[5]; | mind[218]:=Qstanje[29]; |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseBC_V,lo:=4436,hi:=4437); |  | 218:Klima2Errors[5]:=Bit_0; | 218:Qstanje[29]:=Byte_0; |  |  | 4437:PMM.VirBVoltageBetweenPhaseBC_V:=Real_0;
mind_bool[219]:=Klima2Errors[6]; | mind[219]:=Qstanje[2]; |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseBN_V,lo:=4438,hi:=4439); |  | 219:Klima2Errors[6]:=Bit_0; | 219:Qstanje[2]:=Byte_0; |  |  | 4439:PMM.VirBVoltageBetweenPhaseBN_V:=Real_0;
mind_bool[220]:=Klima2Errors[7]; | mind[220]:=Qstanje[30]; |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseCA_V,lo:=4440,hi:=4441); |  | 220:Klima2Errors[7]:=Bit_0; | 220:Qstanje[30]:=Byte_0; |  |  | 4441:PMM.VirBVoltageBetweenPhaseCA_V:=Real_0;
mind_bool[221]:=Klima2Errors[8]; | mind[221]:=Qstanje[31]; |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseCN_V,lo:=4442,hi:=4443); |  | 221:Klima2Errors[8]:=Bit_0; | 221:Qstanje[31]:=Byte_0; |  |  | 4443:PMM.VirBVoltageBetweenPhaseCN_V:=Real_0;
mind_bool[222]:=Klima2Errors[9]; | mind[222]:=Qstanje[32]; |  |  | Read_Real(rVar:=PMM.VoltageBetweenPhaseAB_V,lo:=4444,hi:=4445); |  | 222:Klima2Errors[9]:=Bit_0; | 222:Qstanje[32]:=Byte_0; |  |  | 4445:PMM.VoltageBetweenPhaseAB_V:=Real_0;
mind_bool[223]:=Klima3Errors[10]; | mind[223]:=Qstanje[33]; |  |  | Read_Real(rVar:=PMM.VoltageBetweenPhaseAN_V,lo:=4446,hi:=4447); |  | 223:Klima3Errors[10]:=Bit_0; | 223:Qstanje[33]:=Byte_0; |  |  | 4447:PMM.VoltageBetweenPhaseAN_V:=Real_0;
mind_bool[224]:=Klima3Errors[11]; | mind[224]:=Qstanje[34]; |  |  | Read_Real(rVar:=PMM.VoltageBetweenPhaseBC_V,lo:=4448,hi:=4449); |  | 224:Klima3Errors[11]:=Bit_0; | 224:Qstanje[34]:=Byte_0; |  |  | 4449:PMM.VoltageBetweenPhaseBC_V:=Real_0;
mind_bool[225]:=Klima3Errors[12]; | mind[225]:=Qstanje[35]; |  |  | Read_Real(rVar:=PMM.VoltageBetweenPhaseBN_V,lo:=4450,hi:=4451); |  | 225:Klima3Errors[12]:=Bit_0; | 225:Qstanje[35]:=Byte_0; |  |  | 4451:PMM.VoltageBetweenPhaseBN_V:=Real_0;
mind_bool[226]:=Klima3Errors[13]; | mind[226]:=Qstanje[3]; |  |  | Read_Real(rVar:=PMM.VoltageBetweenPhaseCA_V,lo:=4452,hi:=4453); |  | 226:Klima3Errors[13]:=Bit_0; | 226:Qstanje[3]:=Byte_0; |  |  | 4453:PMM.VoltageBetweenPhaseCA_V:=Real_0;
mind_bool[227]:=Klima3Errors[14]; | mind[227]:=Qstanje[4]; |  |  | Read_Real(rVar:=PMM.VoltageBetweenPhaseCN_V,lo:=4454,hi:=4455); |  | 227:Klima3Errors[14]:=Bit_0; | 227:Qstanje[4]:=Byte_0; |  |  | 4455:PMM.VoltageBetweenPhaseCN_V:=Real_0;
mind_bool[228]:=Klima3Errors[15]; | mind[228]:=Qstanje[5]; |  |  | Read_Real(rVar:=PMMfaza01,lo:=4456,hi:=4457); |  | 228:Klima3Errors[15]:=Bit_0; | 228:Qstanje[5]:=Byte_0; |  |  | 4457:PMMfaza01:=Real_0;
mind_bool[229]:=Klima3Errors[16]; | mind[229]:=Qstanje[6]; |  |  | Read_Real(rVar:=PMMfaza02,lo:=4458,hi:=4459); |  | 229:Klima3Errors[16]:=Bit_0; | 229:Qstanje[6]:=Byte_0; |  |  | 4459:PMMfaza02:=Real_0;
mind_bool[230]:=Klima3Errors[17]; | mind[230]:=Qstanje[7]; |  |  | Read_Real(rVar:=PMMfaza03,lo:=4460,hi:=4461); |  | 230:Klima3Errors[17]:=Bit_0; | 230:Qstanje[7]:=Byte_0; |  |  | 4461:PMMfaza03:=Real_0;
mind_bool[231]:=Klima3Errors[18]; | mind[231]:=Qstanje[8]; |  |  | Read_Real(rVar:=PMMfaza04,lo:=4462,hi:=4463); |  | 231:Klima3Errors[18]:=Bit_0; | 231:Qstanje[8]:=Byte_0; |  |  | 4463:PMMfaza04:=Real_0;
mind_bool[232]:=Klima3Errors[19]; | mind[232]:=Qstanje[9]; |  |  | Read_Real(rVar:=PMMfaza05,lo:=4464,hi:=4465); |  | 232:Klima3Errors[19]:=Bit_0; | 232:Qstanje[9]:=Byte_0; |  |  | 4465:PMMfaza05:=Real_0;
mind_bool[233]:=Klima3Errors[1]; | mind[233]:=UPS[1].InverterStatus; |  |  | Read_Real(rVar:=PMMfaza06,lo:=4466,hi:=4467); |  | 233:Klima3Errors[1]:=Bit_0; | 233:UPS[1].InverterStatus:=Word_01; |  |  | 4467:PMMfaza06:=Real_0;
mind_bool[234]:=Klima3Errors[20]; | mind[234]:=UPS[1].OutputStatus; |  |  | Read_Real(rVar:=PMMfaza07,lo:=4468,hi:=4469); |  | 234:Klima3Errors[20]:=Bit_0; | 234:UPS[1].OutputStatus:=Word_01; |  |  | 4469:PMMfaza07:=Real_0;
mind_bool[235]:=Klima3Errors[21]; | mind[235]:=UPS[1].StatusBaterije; |  |  | Read_Real(rVar:=PMMfaza08,lo:=4470,hi:=4471); |  | 235:Klima3Errors[21]:=Bit_0; | 235:UPS[1].StatusBaterije:=Word_01; |  |  | 4471:PMMfaza08:=Real_0;
mind_bool[236]:=Klima3Errors[22]; | mind[236]:=UPS[1].SteviloIzpadovVhodneLinije; |  |  | Read_Real(rVar:=PMMfaza09,lo:=4472,hi:=4473); |  | 236:Klima3Errors[22]:=Bit_0; | 236:UPS[1].SteviloIzpadovVhodneLinije:=Word_01; |  |  | 4473:PMMfaza09:=Real_0;
mind_bool[237]:=Klima3Errors[23]; | mind[237]:=UPS[1].UnitStatus; |  |  | Read_Real(rVar:=PMMfaza10,lo:=4474,hi:=4475); |  | 237:Klima3Errors[23]:=Bit_0; | 237:UPS[1].UnitStatus:=Word_01; |  |  | 4475:PMMfaza10:=Real_0;
mind_bool[238]:=Klima3Errors[24]; | mind[238]:=UPS[2].InverterStatus; |  |  | Read_Real(rVar:=PMMfaza11,lo:=4476,hi:=4477); |  | 238:Klima3Errors[24]:=Bit_0; | 238:UPS[2].InverterStatus:=Word_01; |  |  | 4477:PMMfaza11:=Real_0;
mind_bool[239]:=Klima3Errors[25]; | mind[239]:=UPS[2].OutputStatus; |  |  | Read_Real(rVar:=PMMfaza12,lo:=4478,hi:=4479); |  | 239:Klima3Errors[25]:=Bit_0; | 239:UPS[2].OutputStatus:=Word_01; |  |  | 4479:PMMfaza12:=Real_0;
mind_bool[240]:=Klima3Errors[26]; | mind[240]:=UPS[2].StatusBaterije; |  |  | Read_Real(rVar:=PMMfaza13,lo:=4480,hi:=4481); |  | 240:Klima3Errors[26]:=Bit_0; | 240:UPS[2].StatusBaterije:=Word_01; |  |  | 4481:PMMfaza13:=Real_0;
mind_bool[241]:=Klima3Errors[27]; | mind[241]:=UPS[2].SteviloIzpadovVhodneLinije; |  |  | Read_Real(rVar:=PMMfaza14,lo:=4482,hi:=4483); |  | 241:Klima3Errors[27]:=Bit_0; | 241:UPS[2].SteviloIzpadovVhodneLinije:=Word_01; |  |  | 4483:PMMfaza14:=Real_0;
mind_bool[242]:=Klima3Errors[28]; | mind[242]:=UPS[2].UnitStatus; |  |  | Read_Real(rVar:=PMMfaza15,lo:=4484,hi:=4485); |  | 242:Klima3Errors[28]:=Bit_0; | 242:UPS[2].UnitStatus:=Word_01; |  |  | 4485:PMMfaza15:=Real_0;
mind_bool[243]:=Klima3Errors[29]; | mind[243]:=UserCurrentLevel; |  |  | Read_Real(rVar:=PMMfaza16,lo:=4486,hi:=4487); |  | 243:Klima3Errors[29]:=Bit_0; | 243:UserCurrentLevel:=Byte_0; |  |  | 4487:PMMfaza16:=Real_0;
mind_bool[244]:=Klima3Errors[2]; |  |  |  | Read_Real(rVar:=PMMfaza17,lo:=4488,hi:=4489); |  | 244:Klima3Errors[2]:=Bit_0; |  |  |  | 4489:PMMfaza17:=Real_0;
mind_bool[245]:=Klima3Errors[30]; |  |  |  | Read_Real(rVar:=PMMfaza18,lo:=4490,hi:=4491); |  | 245:Klima3Errors[30]:=Bit_0; |  |  |  | 4491:PMMfaza18:=Real_0;
mind_bool[246]:=Klima3Errors[31]; |  |  |  | Read_Real(rVar:=PMMfaza19,lo:=4492,hi:=4493); |  | 246:Klima3Errors[31]:=Bit_0; |  |  |  | 4493:PMMfaza19:=Real_0;
mind_bool[247]:=Klima3Errors[32]; |  |  |  | Read_Real(rVar:=PMMfaza20,lo:=4494,hi:=4495); |  | 247:Klima3Errors[32]:=Bit_0; |  |  |  | 4495:PMMfaza20:=Real_0;
mind_bool[248]:=Klima3Errors[33]; |  |  |  | Read_Real(rVar:=PMMfaza21,lo:=4496,hi:=4497); |  | 248:Klima3Errors[33]:=Bit_0; |  |  |  | 4497:PMMfaza21:=Real_0;
mind_bool[249]:=Klima3Errors[34]; |  |  |  | Read_Real(rVar:=PMMfaza22,lo:=4498,hi:=4499); |  | 249:Klima3Errors[34]:=Bit_0; |  |  |  | 4499:PMMfaza22:=Real_0;
mind_bool[250]:=Klima3Errors[35]; |  |  |  | Read_Real(rVar:=PMMfaza23,lo:=4500,hi:=4501); |  | 250:Klima3Errors[35]:=Bit_0; |  |  |  | 4501:PMMfaza23:=Real_0;
mind_bool[251]:=Klima3Errors[3]; |  |  |  | Read_Real(rVar:=PMMfaza24,lo:=4502,hi:=4503); |  | 251:Klima3Errors[3]:=Bit_0; |  |  |  | 4503:PMMfaza24:=Real_0;
mind_bool[252]:=Klima3Errors[4]; |  |  |  | Read_Real(rVar:=PMMfaza25,lo:=4504,hi:=4505); |  | 252:Klima3Errors[4]:=Bit_0; |  |  |  | 4505:PMMfaza25:=Real_0;
mind_bool[253]:=Klima3Errors[5]; |  |  |  | Read_Real(rVar:=PMMfaza26,lo:=4506,hi:=4507); |  | 253:Klima3Errors[5]:=Bit_0; |  |  |  | 4507:PMMfaza26:=Real_0;
mind_bool[254]:=Klima3Errors[6]; |  |  |  | Read_Real(rVar:=PMMfaza27,lo:=4508,hi:=4509); |  | 254:Klima3Errors[6]:=Bit_0; |  |  |  | 4509:PMMfaza27:=Real_0;
mind_bool[255]:=Klima3Errors[7]; |  |  |  | Read_Real(rVar:=PMMfaza28,lo:=4510,hi:=4511); |  | 255:Klima3Errors[7]:=Bit_0; |  |  |  | 4511:PMMfaza28:=Real_0;
mind_bool[256]:=Klima3Errors[8]; |  |  |  | Read_Real(rVar:=PMMfaza29,lo:=4512,hi:=4513); |  | 256:Klima3Errors[8]:=Bit_0; |  |  |  | 4513:PMMfaza29:=Real_0;
mind_bool[257]:=Klima3Errors[9]; |  |  |  | Read_Real(rVar:=PMMfaza30,lo:=4514,hi:=4515); |  | 257:Klima3Errors[9]:=Bit_0; |  |  |  | 4515:PMMfaza30:=Real_0;
mind_bool[258]:=Klima4Errors[10]; |  |  |  | Read_Real(rVar:=PMMfaza31,lo:=4516,hi:=4517); |  | 258:Klima4Errors[10]:=Bit_0; |  |  |  | 4517:PMMfaza31:=Real_0;
mind_bool[259]:=Klima4Errors[11]; |  |  |  | Read_Real(rVar:=PMMfaza32,lo:=4518,hi:=4519); |  | 259:Klima4Errors[11]:=Bit_0; |  |  |  | 4519:PMMfaza32:=Real_0;
mind_bool[260]:=Klima4Errors[12]; |  |  |  | Read_Real(rVar:=PMMfaza33,lo:=4520,hi:=4521); |  | 260:Klima4Errors[12]:=Bit_0; |  |  |  | 4521:PMMfaza33:=Real_0;
mind_bool[261]:=Klima4Errors[13]; |  |  |  | Read_Real(rVar:=PMMfaza34,lo:=4522,hi:=4523); |  | 261:Klima4Errors[13]:=Bit_0; |  |  |  | 4523:PMMfaza34:=Real_0;
mind_bool[262]:=Klima4Errors[14]; |  |  |  | Read_Real(rVar:=PMMfaza35,lo:=4524,hi:=4525); |  | 262:Klima4Errors[14]:=Bit_0; |  |  |  | 4525:PMMfaza35:=Real_0;
mind_bool[263]:=Klima4Errors[15]; |  |  |  | Read_Real(rVar:=PMMfaza36,lo:=4526,hi:=4527); |  | 263:Klima4Errors[15]:=Bit_0; |  |  |  | 4527:PMMfaza36:=Real_0;
mind_bool[264]:=Klima4Errors[16]; |  |  |  | Read_Real(rVar:=PMMfaza37,lo:=4528,hi:=4529); |  | 264:Klima4Errors[16]:=Bit_0; |  |  |  | 4529:PMMfaza37:=Real_0;
mind_bool[265]:=Klima4Errors[17]; |  |  |  | Read_Real(rVar:=PMMfaza38,lo:=4530,hi:=4531); |  | 265:Klima4Errors[17]:=Bit_0; |  |  |  | 4531:PMMfaza38:=Real_0;
mind_bool[266]:=Klima4Errors[18]; |  |  |  | Read_Real(rVar:=PMMfaza39,lo:=4532,hi:=4533); |  | 266:Klima4Errors[18]:=Bit_0; |  |  |  | 4533:PMMfaza39:=Real_0;
mind_bool[267]:=Klima4Errors[19]; |  |  |  | Read_Real(rVar:=PMMfaza40,lo:=4534,hi:=4535); |  | 267:Klima4Errors[19]:=Bit_0; |  |  |  | 4535:PMMfaza40:=Real_0;
mind_bool[268]:=Klima4Errors[1]; |  |  |  | Read_Real(rVar:=PMMfaza41,lo:=4536,hi:=4537); |  | 268:Klima4Errors[1]:=Bit_0; |  |  |  | 4537:PMMfaza41:=Real_0;
mind_bool[269]:=Klima4Errors[20]; |  |  |  | Read_Real(rVar:=PMMfaza42,lo:=4538,hi:=4539); |  | 269:Klima4Errors[20]:=Bit_0; |  |  |  | 4539:PMMfaza42:=Real_0;
mind_bool[270]:=Klima4Errors[21]; |  |  |  | Read_Real(rVar:=PMMfaza60[10],lo:=4540,hi:=4541); |  | 270:Klima4Errors[21]:=Bit_0; |  |  |  | 4541:PMMfaza60[10]:=Real_0;
mind_bool[271]:=Klima4Errors[22]; |  |  |  | Read_Real(rVar:=PMMfaza60[11],lo:=4542,hi:=4543); |  | 271:Klima4Errors[22]:=Bit_0; |  |  |  | 4543:PMMfaza60[11]:=Real_0;
mind_bool[272]:=Klima4Errors[23]; |  |  |  | Read_Real(rVar:=PMMfaza60[12],lo:=4544,hi:=4545); |  | 272:Klima4Errors[23]:=Bit_0; |  |  |  | 4545:PMMfaza60[12]:=Real_0;
mind_bool[273]:=Klima4Errors[24]; |  |  |  | Read_Real(rVar:=PMMfaza60[13],lo:=4546,hi:=4547); |  | 273:Klima4Errors[24]:=Bit_0; |  |  |  | 4547:PMMfaza60[13]:=Real_0;
mind_bool[274]:=Klima4Errors[25]; |  |  |  | Read_Real(rVar:=PMMfaza60[14],lo:=4548,hi:=4549); |  | 274:Klima4Errors[25]:=Bit_0; |  |  |  | 4549:PMMfaza60[14]:=Real_0;
mind_bool[275]:=Klima4Errors[26]; |  |  |  | Read_Real(rVar:=PMMfaza60[15],lo:=4550,hi:=4551); |  | 275:Klima4Errors[26]:=Bit_0; |  |  |  | 4551:PMMfaza60[15]:=Real_0;
mind_bool[276]:=Klima4Errors[27]; |  |  |  | Read_Real(rVar:=PMMfaza60[16],lo:=4552,hi:=4553); |  | 276:Klima4Errors[27]:=Bit_0; |  |  |  | 4553:PMMfaza60[16]:=Real_0;
mind_bool[277]:=Klima4Errors[28]; |  |  |  | Read_Real(rVar:=PMMfaza60[17],lo:=4554,hi:=4555); |  | 277:Klima4Errors[28]:=Bit_0; |  |  |  | 4555:PMMfaza60[17]:=Real_0;
mind_bool[278]:=Klima4Errors[29]; |  |  |  | Read_Real(rVar:=PMMfaza60[18],lo:=4556,hi:=4557); |  | 278:Klima4Errors[29]:=Bit_0; |  |  |  | 4557:PMMfaza60[18]:=Real_0;
mind_bool[279]:=Klima4Errors[2]; |  |  |  | Read_Real(rVar:=PMMfaza60[19],lo:=4558,hi:=4559); |  | 279:Klima4Errors[2]:=Bit_0; |  |  |  | 4559:PMMfaza60[19]:=Real_0;
mind_bool[280]:=Klima4Errors[30]; |  |  |  | Read_Real(rVar:=PMMfaza60[1],lo:=4560,hi:=4561); |  | 280:Klima4Errors[30]:=Bit_0; |  |  |  | 4561:PMMfaza60[1]:=Real_0;
mind_bool[281]:=Klima4Errors[31]; |  |  |  | Read_Real(rVar:=PMMfaza60[20],lo:=4562,hi:=4563); |  | 281:Klima4Errors[31]:=Bit_0; |  |  |  | 4563:PMMfaza60[20]:=Real_0;
mind_bool[282]:=Klima4Errors[32]; |  |  |  | Read_Real(rVar:=PMMfaza60[21],lo:=4564,hi:=4565); |  | 282:Klima4Errors[32]:=Bit_0; |  |  |  | 4565:PMMfaza60[21]:=Real_0;
mind_bool[283]:=Klima4Errors[33]; |  |  |  | Read_Real(rVar:=PMMfaza60[22],lo:=4566,hi:=4567); |  | 283:Klima4Errors[33]:=Bit_0; |  |  |  | 4567:PMMfaza60[22]:=Real_0;
mind_bool[284]:=Klima4Errors[34]; |  |  |  | Read_Real(rVar:=PMMfaza60[23],lo:=4568,hi:=4569); |  | 284:Klima4Errors[34]:=Bit_0; |  |  |  | 4569:PMMfaza60[23]:=Real_0;
mind_bool[285]:=Klima4Errors[35]; |  |  |  | Read_Real(rVar:=PMMfaza60[24],lo:=4570,hi:=4571); |  | 285:Klima4Errors[35]:=Bit_0; |  |  |  | 4571:PMMfaza60[24]:=Real_0;
mind_bool[286]:=Klima4Errors[3]; |  |  |  | Read_Real(rVar:=PMMfaza60[25],lo:=4572,hi:=4573); |  | 286:Klima4Errors[3]:=Bit_0; |  |  |  | 4573:PMMfaza60[25]:=Real_0;
mind_bool[287]:=Klima4Errors[4]; |  |  |  | Read_Real(rVar:=PMMfaza60[26],lo:=4574,hi:=4575); |  | 287:Klima4Errors[4]:=Bit_0; |  |  |  | 4575:PMMfaza60[26]:=Real_0;
mind_bool[288]:=Klima4Errors[5]; |  |  |  | Read_Real(rVar:=PMMfaza60[27],lo:=4576,hi:=4577); |  | 288:Klima4Errors[5]:=Bit_0; |  |  |  | 4577:PMMfaza60[27]:=Real_0;
mind_bool[289]:=Klima4Errors[6]; |  |  |  | Read_Real(rVar:=PMMfaza60[28],lo:=4578,hi:=4579); |  | 289:Klima4Errors[6]:=Bit_0; |  |  |  | 4579:PMMfaza60[28]:=Real_0;
mind_bool[290]:=Klima4Errors[7]; |  |  |  | Read_Real(rVar:=PMMfaza60[29],lo:=4580,hi:=4581); |  | 290:Klima4Errors[7]:=Bit_0; |  |  |  | 4581:PMMfaza60[29]:=Real_0;
mind_bool[291]:=Klima4Errors[8]; |  |  |  | Read_Real(rVar:=PMMfaza60[2],lo:=4582,hi:=4583); |  | 291:Klima4Errors[8]:=Bit_0; |  |  |  | 4583:PMMfaza60[2]:=Real_0;
mind_bool[292]:=Klima4Errors[9]; |  |  |  | Read_Real(rVar:=PMMfaza60[30],lo:=4584,hi:=4585); |  | 292:Klima4Errors[9]:=Bit_0; |  |  |  | 4585:PMMfaza60[30]:=Real_0;
mind_bool[293]:=Klima5Errors[10]; |  |  |  | Read_Real(rVar:=PMMfaza60[31],lo:=4586,hi:=4587); |  | 293:Klima5Errors[10]:=Bit_0; |  |  |  | 4587:PMMfaza60[31]:=Real_0;
mind_bool[294]:=Klima5Errors[11]; |  |  |  | Read_Real(rVar:=PMMfaza60[32],lo:=4588,hi:=4589); |  | 294:Klima5Errors[11]:=Bit_0; |  |  |  | 4589:PMMfaza60[32]:=Real_0;
mind_bool[295]:=Klima5Errors[12]; |  |  |  | Read_Real(rVar:=PMMfaza60[33],lo:=4590,hi:=4591); |  | 295:Klima5Errors[12]:=Bit_0; |  |  |  | 4591:PMMfaza60[33]:=Real_0;
mind_bool[296]:=Klima5Errors[13]; |  |  |  | Read_Real(rVar:=PMMfaza60[34],lo:=4592,hi:=4593); |  | 296:Klima5Errors[13]:=Bit_0; |  |  |  | 4593:PMMfaza60[34]:=Real_0;
mind_bool[297]:=Klima5Errors[14]; |  |  |  | Read_Real(rVar:=PMMfaza60[35],lo:=4594,hi:=4595); |  | 297:Klima5Errors[14]:=Bit_0; |  |  |  | 4595:PMMfaza60[35]:=Real_0;
mind_bool[298]:=Klima5Errors[15]; |  |  |  | Read_Real(rVar:=PMMfaza60[36],lo:=4596,hi:=4597); |  | 298:Klima5Errors[15]:=Bit_0; |  |  |  | 4597:PMMfaza60[36]:=Real_0;
mind_bool[299]:=Klima5Errors[16]; |  |  |  | Read_Real(rVar:=PMMfaza60[37],lo:=4598,hi:=4599); |  | 299:Klima5Errors[16]:=Bit_0; |  |  |  | 4599:PMMfaza60[37]:=Real_0;
mind_bool[300]:=Klima5Errors[17]; |  |  |  | Read_Real(rVar:=PMMfaza60[38],lo:=4600,hi:=4601); |  | 300:Klima5Errors[17]:=Bit_0; |  |  |  | 4601:PMMfaza60[38]:=Real_0;
mind_bool[301]:=Klima5Errors[18]; |  |  |  | Read_Real(rVar:=PMMfaza60[39],lo:=4602,hi:=4603); |  | 301:Klima5Errors[18]:=Bit_0; |  |  |  | 4603:PMMfaza60[39]:=Real_0;
mind_bool[302]:=Klima5Errors[19]; |  |  |  | Read_Real(rVar:=PMMfaza60[3],lo:=4604,hi:=4605); |  | 302:Klima5Errors[19]:=Bit_0; |  |  |  | 4605:PMMfaza60[3]:=Real_0;
mind_bool[303]:=Klima5Errors[1]; |  |  |  | Read_Real(rVar:=PMMfaza60[40],lo:=4606,hi:=4607); |  | 303:Klima5Errors[1]:=Bit_0; |  |  |  | 4607:PMMfaza60[40]:=Real_0;
mind_bool[304]:=Klima5Errors[20]; |  |  |  | Read_Real(rVar:=PMMfaza60[41],lo:=4608,hi:=4609); |  | 304:Klima5Errors[20]:=Bit_0; |  |  |  | 4609:PMMfaza60[41]:=Real_0;
mind_bool[305]:=Klima5Errors[21]; |  |  |  | Read_Real(rVar:=PMMfaza60[42],lo:=4610,hi:=4611); |  | 305:Klima5Errors[21]:=Bit_0; |  |  |  | 4611:PMMfaza60[42]:=Real_0;
mind_bool[306]:=Klima5Errors[22]; |  |  |  | Read_Real(rVar:=PMMfaza60[4],lo:=4612,hi:=4613); |  | 306:Klima5Errors[22]:=Bit_0; |  |  |  | 4613:PMMfaza60[4]:=Real_0;
mind_bool[307]:=Klima5Errors[23]; |  |  |  | Read_Real(rVar:=PMMfaza60[5],lo:=4614,hi:=4615); |  | 307:Klima5Errors[23]:=Bit_0; |  |  |  | 4615:PMMfaza60[5]:=Real_0;
mind_bool[308]:=Klima5Errors[24]; |  |  |  | Read_Real(rVar:=PMMfaza60[6],lo:=4616,hi:=4617); |  | 308:Klima5Errors[24]:=Bit_0; |  |  |  | 4617:PMMfaza60[6]:=Real_0;
mind_bool[309]:=Klima5Errors[25]; |  |  |  | Read_Real(rVar:=PMMfaza60[7],lo:=4618,hi:=4619); |  | 309:Klima5Errors[25]:=Bit_0; |  |  |  | 4619:PMMfaza60[7]:=Real_0;
mind_bool[310]:=Klima5Errors[26]; |  |  |  | Read_Real(rVar:=PMMfaza60[8],lo:=4620,hi:=4621); |  | 310:Klima5Errors[26]:=Bit_0; |  |  |  | 4621:PMMfaza60[8]:=Real_0;
mind_bool[311]:=Klima5Errors[27]; |  |  |  | Read_Real(rVar:=PMMfaza60[9],lo:=4622,hi:=4623); |  | 311:Klima5Errors[27]:=Bit_0; |  |  |  | 4623:PMMfaza60[9]:=Real_0;
mind_bool[312]:=Klima5Errors[28]; |  |  |  | Read_Real(rVar:=PMMfaza80[10],lo:=4624,hi:=4625); |  | 312:Klima5Errors[28]:=Bit_0; |  |  |  | 4625:PMMfaza80[10]:=Real_0;
mind_bool[313]:=Klima5Errors[29]; |  |  |  | Read_Real(rVar:=PMMfaza80[11],lo:=4626,hi:=4627); |  | 313:Klima5Errors[29]:=Bit_0; |  |  |  | 4627:PMMfaza80[11]:=Real_0;
mind_bool[314]:=Klima5Errors[2]; |  |  |  | Read_Real(rVar:=PMMfaza80[12],lo:=4628,hi:=4629); |  | 314:Klima5Errors[2]:=Bit_0; |  |  |  | 4629:PMMfaza80[12]:=Real_0;
mind_bool[315]:=Klima5Errors[30]; |  |  |  | Read_Real(rVar:=PMMfaza80[13],lo:=4630,hi:=4631); |  | 315:Klima5Errors[30]:=Bit_0; |  |  |  | 4631:PMMfaza80[13]:=Real_0;
mind_bool[316]:=Klima5Errors[31]; |  |  |  | Read_Real(rVar:=PMMfaza80[14],lo:=4632,hi:=4633); |  | 316:Klima5Errors[31]:=Bit_0; |  |  |  | 4633:PMMfaza80[14]:=Real_0;
mind_bool[317]:=Klima5Errors[32]; |  |  |  | Read_Real(rVar:=PMMfaza80[15],lo:=4634,hi:=4635); |  | 317:Klima5Errors[32]:=Bit_0; |  |  |  | 4635:PMMfaza80[15]:=Real_0;
mind_bool[318]:=Klima5Errors[33]; |  |  |  | Read_Real(rVar:=PMMfaza80[16],lo:=4636,hi:=4637); |  | 318:Klima5Errors[33]:=Bit_0; |  |  |  | 4637:PMMfaza80[16]:=Real_0;
mind_bool[319]:=Klima5Errors[34]; |  |  |  | Read_Real(rVar:=PMMfaza80[17],lo:=4638,hi:=4639); |  | 319:Klima5Errors[34]:=Bit_0; |  |  |  | 4639:PMMfaza80[17]:=Real_0;
mind_bool[320]:=Klima5Errors[35]; |  |  |  | Read_Real(rVar:=PMMfaza80[18],lo:=4640,hi:=4641); |  | 320:Klima5Errors[35]:=Bit_0; |  |  |  | 4641:PMMfaza80[18]:=Real_0;
mind_bool[321]:=Klima5Errors[3]; |  |  |  | Read_Real(rVar:=PMMfaza80[19],lo:=4642,hi:=4643); |  | 321:Klima5Errors[3]:=Bit_0; |  |  |  | 4643:PMMfaza80[19]:=Real_0;
mind_bool[322]:=Klima5Errors[4]; |  |  |  | Read_Real(rVar:=PMMfaza80[1],lo:=4644,hi:=4645); |  | 322:Klima5Errors[4]:=Bit_0; |  |  |  | 4645:PMMfaza80[1]:=Real_0;
mind_bool[323]:=Klima5Errors[5]; |  |  |  | Read_Real(rVar:=PMMfaza80[20],lo:=4646,hi:=4647); |  | 323:Klima5Errors[5]:=Bit_0; |  |  |  | 4647:PMMfaza80[20]:=Real_0;
mind_bool[324]:=Klima5Errors[6]; |  |  |  | Read_Real(rVar:=PMMfaza80[21],lo:=4648,hi:=4649); |  | 324:Klima5Errors[6]:=Bit_0; |  |  |  | 4649:PMMfaza80[21]:=Real_0;
mind_bool[325]:=Klima5Errors[7]; |  |  |  | Read_Real(rVar:=PMMfaza80[22],lo:=4650,hi:=4651); |  | 325:Klima5Errors[7]:=Bit_0; |  |  |  | 4651:PMMfaza80[22]:=Real_0;
mind_bool[326]:=Klima5Errors[8]; |  |  |  | Read_Real(rVar:=PMMfaza80[23],lo:=4652,hi:=4653); |  | 326:Klima5Errors[8]:=Bit_0; |  |  |  | 4653:PMMfaza80[23]:=Real_0;
mind_bool[327]:=Klima5Errors[9]; |  |  |  | Read_Real(rVar:=PMMfaza80[24],lo:=4654,hi:=4655); |  | 327:Klima5Errors[9]:=Bit_0; |  |  |  | 4655:PMMfaza80[24]:=Real_0;
mind_bool[328]:=Klima6Errors[10]; |  |  |  | Read_Real(rVar:=PMMfaza80[25],lo:=4656,hi:=4657); |  | 328:Klima6Errors[10]:=Bit_0; |  |  |  | 4657:PMMfaza80[25]:=Real_0;
mind_bool[329]:=Klima6Errors[11]; |  |  |  | Read_Real(rVar:=PMMfaza80[26],lo:=4658,hi:=4659); |  | 329:Klima6Errors[11]:=Bit_0; |  |  |  | 4659:PMMfaza80[26]:=Real_0;
mind_bool[330]:=Klima6Errors[12]; |  |  |  | Read_Real(rVar:=PMMfaza80[27],lo:=4660,hi:=4661); |  | 330:Klima6Errors[12]:=Bit_0; |  |  |  | 4661:PMMfaza80[27]:=Real_0;
mind_bool[331]:=Klima6Errors[13]; |  |  |  | Read_Real(rVar:=PMMfaza80[28],lo:=4662,hi:=4663); |  | 331:Klima6Errors[13]:=Bit_0; |  |  |  | 4663:PMMfaza80[28]:=Real_0;
mind_bool[332]:=Klima6Errors[14]; |  |  |  | Read_Real(rVar:=PMMfaza80[29],lo:=4664,hi:=4665); |  | 332:Klima6Errors[14]:=Bit_0; |  |  |  | 4665:PMMfaza80[29]:=Real_0;
mind_bool[333]:=Klima6Errors[15]; |  |  |  | Read_Real(rVar:=PMMfaza80[2],lo:=4666,hi:=4667); |  | 333:Klima6Errors[15]:=Bit_0; |  |  |  | 4667:PMMfaza80[2]:=Real_0;
mind_bool[334]:=Klima6Errors[16]; |  |  |  | Read_Real(rVar:=PMMfaza80[30],lo:=4668,hi:=4669); |  | 334:Klima6Errors[16]:=Bit_0; |  |  |  | 4669:PMMfaza80[30]:=Real_0;
mind_bool[335]:=Klima6Errors[17]; |  |  |  | Read_Real(rVar:=PMMfaza80[31],lo:=4670,hi:=4671); |  | 335:Klima6Errors[17]:=Bit_0; |  |  |  | 4671:PMMfaza80[31]:=Real_0;
mind_bool[336]:=Klima6Errors[18]; |  |  |  | Read_Real(rVar:=PMMfaza80[32],lo:=4672,hi:=4673); |  | 336:Klima6Errors[18]:=Bit_0; |  |  |  | 4673:PMMfaza80[32]:=Real_0;
mind_bool[337]:=Klima6Errors[19]; |  |  |  | Read_Real(rVar:=PMMfaza80[33],lo:=4674,hi:=4675); |  | 337:Klima6Errors[19]:=Bit_0; |  |  |  | 4675:PMMfaza80[33]:=Real_0;
mind_bool[338]:=Klima6Errors[1]; |  |  |  | Read_Real(rVar:=PMMfaza80[34],lo:=4676,hi:=4677); |  | 338:Klima6Errors[1]:=Bit_0; |  |  |  | 4677:PMMfaza80[34]:=Real_0;
mind_bool[339]:=Klima6Errors[20]; |  |  |  | Read_Real(rVar:=PMMfaza80[35],lo:=4678,hi:=4679); |  | 339:Klima6Errors[20]:=Bit_0; |  |  |  | 4679:PMMfaza80[35]:=Real_0;
mind_bool[340]:=Klima6Errors[21]; |  |  |  | Read_Real(rVar:=PMMfaza80[36],lo:=4680,hi:=4681); |  | 340:Klima6Errors[21]:=Bit_0; |  |  |  | 4681:PMMfaza80[36]:=Real_0;
mind_bool[341]:=Klima6Errors[22]; |  |  |  | Read_Real(rVar:=PMMfaza80[37],lo:=4682,hi:=4683); |  | 341:Klima6Errors[22]:=Bit_0; |  |  |  | 4683:PMMfaza80[37]:=Real_0;
mind_bool[342]:=Klima6Errors[23]; |  |  |  | Read_Real(rVar:=PMMfaza80[38],lo:=4684,hi:=4685); |  | 342:Klima6Errors[23]:=Bit_0; |  |  |  | 4685:PMMfaza80[38]:=Real_0;
mind_bool[343]:=Klima6Errors[24]; |  |  |  | Read_Real(rVar:=PMMfaza80[39],lo:=4686,hi:=4687); |  | 343:Klima6Errors[24]:=Bit_0; |  |  |  | 4687:PMMfaza80[39]:=Real_0;
mind_bool[344]:=Klima6Errors[25]; |  |  |  | Read_Real(rVar:=PMMfaza80[3],lo:=4688,hi:=4689); |  | 344:Klima6Errors[25]:=Bit_0; |  |  |  | 4689:PMMfaza80[3]:=Real_0;
mind_bool[345]:=Klima6Errors[26]; |  |  |  | Read_Real(rVar:=PMMfaza80[40],lo:=4690,hi:=4691); |  | 345:Klima6Errors[26]:=Bit_0; |  |  |  | 4691:PMMfaza80[40]:=Real_0;
mind_bool[346]:=Klima6Errors[27]; |  |  |  | Read_Real(rVar:=PMMfaza80[41],lo:=4692,hi:=4693); |  | 346:Klima6Errors[27]:=Bit_0; |  |  |  | 4693:PMMfaza80[41]:=Real_0;
mind_bool[347]:=Klima6Errors[28]; |  |  |  | Read_Real(rVar:=PMMfaza80[42],lo:=4694,hi:=4695); |  | 347:Klima6Errors[28]:=Bit_0; |  |  |  | 4695:PMMfaza80[42]:=Real_0;
mind_bool[348]:=Klima6Errors[29]; |  |  |  | Read_Real(rVar:=PMMfaza80[4],lo:=4696,hi:=4697); |  | 348:Klima6Errors[29]:=Bit_0; |  |  |  | 4697:PMMfaza80[4]:=Real_0;
mind_bool[349]:=Klima6Errors[2]; |  |  |  | Read_Real(rVar:=PMMfaza80[5],lo:=4698,hi:=4699); |  | 349:Klima6Errors[2]:=Bit_0; |  |  |  | 4699:PMMfaza80[5]:=Real_0;
mind_bool[350]:=Klima6Errors[30]; |  |  |  | Read_Real(rVar:=PMMfaza80[6],lo:=4700,hi:=4701); |  | 350:Klima6Errors[30]:=Bit_0; |  |  |  | 4701:PMMfaza80[6]:=Real_0;
mind_bool[351]:=Klima6Errors[31]; |  |  |  | Read_Real(rVar:=PMMfaza80[7],lo:=4702,hi:=4703); |  | 351:Klima6Errors[31]:=Bit_0; |  |  |  | 4703:PMMfaza80[7]:=Real_0;
mind_bool[352]:=Klima6Errors[32]; |  |  |  | Read_Real(rVar:=PMMfaza80[8],lo:=4704,hi:=4705); |  | 352:Klima6Errors[32]:=Bit_0; |  |  |  | 4705:PMMfaza80[8]:=Real_0;
mind_bool[353]:=Klima6Errors[33]; |  |  |  | Read_Real(rVar:=PMMfaza80[9],lo:=4706,hi:=4707); |  | 353:Klima6Errors[33]:=Bit_0; |  |  |  | 4707:PMMfaza80[9]:=Real_0;
mind_bool[354]:=Klima6Errors[34]; |  |  |  | Read_Real(rVar:=SenzorTemp[1],lo:=4708,hi:=4709); |  | 354:Klima6Errors[34]:=Bit_0; |  |  |  | 4709:SenzorTemp[1]:=Real_0;
mind_bool[355]:=Klima6Errors[35]; |  |  |  | Read_Real(rVar:=SenzorTemp[2],lo:=4710,hi:=4711); |  | 355:Klima6Errors[35]:=Bit_0; |  |  |  | 4711:SenzorTemp[2]:=Real_0;
mind_bool[356]:=Klima6Errors[3]; |  |  |  | Read_Real(rVar:=SenzorTemp[3],lo:=4712,hi:=4713); |  | 356:Klima6Errors[3]:=Bit_0; |  |  |  | 4713:SenzorTemp[3]:=Real_0;
mind_bool[357]:=Klima6Errors[4]; |  |  |  | Read_Real(rVar:=SenzorTemp[4],lo:=4714,hi:=4715); |  | 357:Klima6Errors[4]:=Bit_0; |  |  |  | 4715:SenzorTemp[4]:=Real_0;
mind_bool[358]:=Klima6Errors[5]; |  |  |  | Read_Real(rVar:=SenzorTemp[5],lo:=4716,hi:=4717); |  | 358:Klima6Errors[5]:=Bit_0; |  |  |  | 4717:SenzorTemp[5]:=Real_0;
mind_bool[359]:=Klima6Errors[6]; |  |  |  | Read_Real(rVar:=SenzorTemp[6],lo:=4718,hi:=4719); |  | 359:Klima6Errors[6]:=Bit_0; |  |  |  | 4719:SenzorTemp[6]:=Real_0;
mind_bool[360]:=Klima6Errors[7]; |  |  |  | Read_Real(rVar:=SenzorVlaga[1],lo:=4720,hi:=4721); |  | 360:Klima6Errors[7]:=Bit_0; |  |  |  | 4721:SenzorVlaga[1]:=Real_0;
mind_bool[361]:=Klima6Errors[8]; |  |  |  | Read_Real(rVar:=SenzorVlaga[2],lo:=4722,hi:=4723); |  | 361:Klima6Errors[8]:=Bit_0; |  |  |  | 4723:SenzorVlaga[2]:=Real_0;
mind_bool[362]:=Klima6Errors[9]; |  |  |  | Read_Real(rVar:=SenzorVlaga[3],lo:=4724,hi:=4725); |  | 362:Klima6Errors[9]:=Bit_0; |  |  |  | 4725:SenzorVlaga[3]:=Real_0;
mind_bool[363]:=Klima[1].Deluje; |  |  |  | Read_Real(rVar:=SenzorVlaga[4],lo:=4726,hi:=4727); |  | 363:Klima[1].Deluje:=Bit_0; |  |  |  | 4727:SenzorVlaga[4]:=Real_0;
mind_bool[364]:=Klima[1].FenThermalCutout; |  |  |  | Read_Real(rVar:=SenzorVlaga[5],lo:=4728,hi:=4729); |  | 364:Klima[1].FenThermalCutout:=Bit_0; |  |  |  | 4729:SenzorVlaga[5]:=Real_0;
mind_bool[365]:=Klima[1].GeneralAlarm; |  |  |  | Read_Real(rVar:=SenzorVlaga[6],lo:=4730,hi:=4731); |  | 365:Klima[1].GeneralAlarm:=Bit_0; |  |  |  | 4731:SenzorVlaga[6]:=Real_0;
mind_bool[366]:=Klima[1].Kompresor1naMejiObrUr; |  |  |  | Read_Real(rVar:=TempAlarmPoint[0],lo:=4732,hi:=4733); |  | 366:Klima[1].Kompresor1naMejiObrUr:=Bit_0; |  |  |  | 4733:TempAlarmPoint[0]:=Real_0;
mind_bool[367]:=Klima[1].Kompresor2naMejiObrUr; |  |  |  | Read_Real(rVar:=TempAlarmPoint[1],lo:=4734,hi:=4735); |  | 367:Klima[1].Kompresor2naMejiObrUr:=Bit_0; |  |  |  | 4735:TempAlarmPoint[1]:=Real_0;
mind_bool[368]:=Klima[1].Napaka; |  |  |  | Read_Real(rVar:=TempAlarmPoint[2],lo:=4736,hi:=4737); |  | 368:Klima[1].Napaka:=Bit_0; |  |  |  | 4737:TempAlarmPoint[2]:=Real_0;
mind_bool[369]:=Klima[1].NapakaPriPretokuZraka; |  |  |  | Read_Real(rVar:=TempAlarmPoint[3],lo:=4738,hi:=4739); |  | 369:Klima[1].NapakaPriPretokuZraka:=Bit_0; |  |  |  | 4739:TempAlarmPoint[3]:=Real_0;
mind_bool[370]:=Klima[1].NapakaSenzorTempIzpiha; |  |  |  | Read_Real(rVar:=TempMaxPoint[0],lo:=4740,hi:=4741); |  | 370:Klima[1].NapakaSenzorTempIzpiha:=Bit_0; |  |  |  | 4741:TempMaxPoint[0]:=Real_0;
mind_bool[371]:=Klima[1].NapakaSenzorTempProstora; |  |  |  | Read_Real(rVar:=TempMaxPoint[1],lo:=4742,hi:=4743); |  | 371:Klima[1].NapakaSenzorTempProstora:=Bit_0; |  |  |  | 4743:TempMaxPoint[1]:=Real_0;
mind_bool[372]:=Klima[1].NapakaSenzorVlaznosti; |  |  |  | Read_Real(rVar:=TempMaxPoint[2],lo:=4744,hi:=4745); |  | 372:Klima[1].NapakaSenzorVlaznosti:=Bit_0; |  |  |  | 4745:TempMaxPoint[2]:=Real_0;
mind_bool[373]:=Klima[1].NapakaSenzorZunanjeTemp; |  |  |  | Read_Real(rVar:=TempMaxPoint[3],lo:=4746,hi:=4747); |  | 373:Klima[1].NapakaSenzorZunanjeTemp:=Bit_0; |  |  |  | 4747:TempMaxPoint[3]:=Real_0;
mind_bool[374]:=Klima[1].NiTokaVVlazilcu; |  |  |  | Read_Real(rVar:=TempPovp[0],lo:=4748,hi:=4749); |  | 374:Klima[1].NiTokaVVlazilcu:=Bit_0; |  |  |  | 4749:TempPovp[0]:=Real_0;
mind_bool[375]:=Klima[1].NiVodeVVlazilcu; |  |  |  | Read_Real(rVar:=TempPovp[1],lo:=4750,hi:=4751); |  | 375:Klima[1].NiVodeVVlazilcu:=Bit_0; |  |  |  | 4751:TempPovp[1]:=Real_0;
mind_bool[376]:=Klima[1].NizekPritiskKompresor1; |  |  |  | Read_Real(rVar:=TempPovp[2],lo:=4752,hi:=4753); |  | 376:Klima[1].NizekPritiskKompresor1:=Bit_0; |  |  |  | 4753:TempPovp[2]:=Real_0;
mind_bool[377]:=Klima[1].NizekPritiskKompresor2; |  |  |  | Read_Real(rVar:=TempPovp[3],lo:=4754,hi:=4755); |  | 377:Klima[1].NizekPritiskKompresor2:=Bit_0; |  |  |  | 4755:TempPovp[3]:=Real_0;
mind_bool[378]:=Klima[1].NizkaTempVProstoru; |  |  |  | Read_Real(rVar:=TempSetPoint[0],lo:=4756,hi:=4757); |  | 378:Klima[1].NizkaTempVProstoru:=Bit_0; |  |  |  | 4757:TempSetPoint[0]:=Real_0;
mind_bool[379]:=Klima[1].NizkaVlaznost; |  |  |  | Read_Real(rVar:=TempSetPoint[1],lo:=4758,hi:=4759); |  | 379:Klima[1].NizkaVlaznost:=Bit_0; |  |  |  | 4759:TempSetPoint[1]:=Real_0;
mind_bool[380]:=Klima[1].OnOffEnablingBySupervisor; |  |  |  | Read_Real(rVar:=TempSetPoint[2],lo:=4760,hi:=4761); |  | 380:Klima[1].OnOffEnablingBySupervisor:=Bit_0; |  |  |  | 4761:TempSetPoint[2]:=Real_0;
mind_bool[381]:=Klima[1].PozarniAlarm; |  |  |  | Read_Real(rVar:=TempSetPoint[3],lo:=4762,hi:=4763); |  | 381:Klima[1].PozarniAlarm:=Bit_0; |  |  |  | 4763:TempSetPoint[3]:=Real_0;
mind_bool[382]:=Klima[1].Razvlazevanje; |  |  |  | Read_Real(rVar:=UPS[1].EstimatedChargeRemaining,lo:=4764,hi:=4765); |  | 382:Klima[1].Razvlazevanje:=Bit_0; |  |  |  | 4765:UPS[1].EstimatedChargeRemaining:=Real_0;
mind_bool[383]:=Klima[1].RemoteOFFtoOutput; |  |  |  | Read_Real(rVar:=UPS[1].EstimatedMinutesRemaining,lo:=4766,hi:=4767); |  | 383:Klima[1].RemoteOFFtoOutput:=Bit_0; |  |  |  | 4767:UPS[1].EstimatedMinutesRemaining:=Real_0;
mind_bool[384]:=Klima[1].RocniIzklop; |  |  |  | Read_Real(rVar:=UPS[1].IzhodMocL1,lo:=4768,hi:=4769); |  | 384:Klima[1].RocniIzklop:=Bit_0; |  |  |  | 4769:UPS[1].IzhodMocL1:=Real_0;
mind_bool[385]:=Klima[1].SenzorjiStatus; |  |  |  | Read_Real(rVar:=UPS[1].IzhodMocL2,lo:=4770,hi:=4771); |  | 385:Klima[1].SenzorjiStatus:=Bit_0; |  |  |  | 4771:UPS[1].IzhodMocL2:=Real_0;
mind_bool[386]:=Klima[1].UnitOnOff; |  |  |  | Read_Real(rVar:=UPS[1].IzhodMocL3,lo:=4772,hi:=4773); |  | 386:Klima[1].UnitOnOff:=Bit_0; |  |  |  | 4773:UPS[1].IzhodMocL3:=Real_0;
mind_bool[387]:=Klima[1].VisokaTempVProstoru; |  |  |  | Read_Real(rVar:=UPS[1].NapetostBaterije,lo:=4774,hi:=4775); |  | 387:Klima[1].VisokaTempVProstoru:=Bit_0; |  |  |  | 4775:UPS[1].NapetostBaterije:=Real_0;
mind_bool[388]:=Klima[1].VisokaVlaznost; |  |  |  | Read_Real(rVar:=UPS[1].TemperaturaBaterije,lo:=4776,hi:=4777); |  | 388:Klima[1].VisokaVlaznost:=Bit_0; |  |  |  | 4777:UPS[1].TemperaturaBaterije:=Real_0;
mind_bool[389]:=Klima[1].VisokTokVVlazilcu; |  |  |  | Read_Real(rVar:=UPS[1].VhodFrekvencaL1,lo:=4778,hi:=4779); |  | 389:Klima[1].VisokTokVVlazilcu:=Bit_0; |  |  |  | 4779:UPS[1].VhodFrekvencaL1:=Real_0;
mind_bool[390]:=Klima[1].Vlazenje; |  |  |  | Read_Real(rVar:=UPS[1].VhodFrekvencaL2,lo:=4780,hi:=4781); |  | 390:Klima[1].Vlazenje:=Bit_0; |  |  |  | 4781:UPS[1].VhodFrekvencaL2:=Real_0;
mind_bool[391]:=Klima[1].ZamasenFilter; |  |  |  | Read_Real(rVar:=UPS[1].VhodFrekvencaL3,lo:=4782,hi:=4783); |  | 391:Klima[1].ZamasenFilter:=Bit_0; |  |  |  | 4783:UPS[1].VhodFrekvencaL3:=Real_0;
mind_bool[392]:=Klima[2].Deluje; |  |  |  | Read_Real(rVar:=UPS[1].VhodNapetostL1,lo:=4784,hi:=4785); |  | 392:Klima[2].Deluje:=Bit_0; |  |  |  | 4785:UPS[1].VhodNapetostL1:=Real_0;
mind_bool[393]:=Klima[2].FenThermalCutout; |  |  |  | Read_Real(rVar:=UPS[1].VhodNapetostL2,lo:=4786,hi:=4787); |  | 393:Klima[2].FenThermalCutout:=Bit_0; |  |  |  | 4787:UPS[1].VhodNapetostL2:=Real_0;
mind_bool[394]:=Klima[2].GeneralAlarm; |  |  |  | Read_Real(rVar:=UPS[1].VhodNapetostL3,lo:=4788,hi:=4789); |  | 394:Klima[2].GeneralAlarm:=Bit_0; |  |  |  | 4789:UPS[1].VhodNapetostL3:=Real_0;
mind_bool[395]:=Klima[2].Kompresor1naMejiObrUr; |  |  |  | Read_Real(rVar:=UPS[2].EstimatedChargeRemaining,lo:=4790,hi:=4791); |  | 395:Klima[2].Kompresor1naMejiObrUr:=Bit_0; |  |  |  | 4791:UPS[2].EstimatedChargeRemaining:=Real_0;
mind_bool[396]:=Klima[2].Kompresor2naMejiObrUr; |  |  |  | Read_Real(rVar:=UPS[2].EstimatedMinutesRemaining,lo:=4792,hi:=4793); |  | 396:Klima[2].Kompresor2naMejiObrUr:=Bit_0; |  |  |  | 4793:UPS[2].EstimatedMinutesRemaining:=Real_0;
mind_bool[397]:=Klima[2].Napaka; |  |  |  | Read_Real(rVar:=UPS[2].IzhodMocL1,lo:=4794,hi:=4795); |  | 397:Klima[2].Napaka:=Bit_0; |  |  |  | 4795:UPS[2].IzhodMocL1:=Real_0;
mind_bool[398]:=Klima[2].NapakaPriPretokuZraka; |  |  |  | Read_Real(rVar:=UPS[2].IzhodMocL2,lo:=4796,hi:=4797); |  | 398:Klima[2].NapakaPriPretokuZraka:=Bit_0; |  |  |  | 4797:UPS[2].IzhodMocL2:=Real_0;
mind_bool[399]:=Klima[2].NapakaSenzorTempIzpiha; |  |  |  | Read_Real(rVar:=UPS[2].IzhodMocL3,lo:=4798,hi:=4799); |  | 399:Klima[2].NapakaSenzorTempIzpiha:=Bit_0; |  |  |  | 4799:UPS[2].IzhodMocL3:=Real_0;
mind_bool[400]:=Klima[2].NapakaSenzorTempProstora; |  |  |  | Read_Real(rVar:=UPS[2].NapetostBaterije,lo:=4800,hi:=4801); |  | 400:Klima[2].NapakaSenzorTempProstora:=Bit_0; |  |  |  | 4801:UPS[2].NapetostBaterije:=Real_0;
mind_bool[401]:=Klima[2].NapakaSenzorVlaznosti; |  |  |  | Read_Real(rVar:=UPS[2].TemperaturaBaterije,lo:=4802,hi:=4803); |  | 401:Klima[2].NapakaSenzorVlaznosti:=Bit_0; |  |  |  | 4803:UPS[2].TemperaturaBaterije:=Real_0;
mind_bool[402]:=Klima[2].NapakaSenzorZunanjeTemp; |  |  |  | Read_Real(rVar:=UPS[2].VhodFrekvencaL1,lo:=4804,hi:=4805); |  | 402:Klima[2].NapakaSenzorZunanjeTemp:=Bit_0; |  |  |  | 4805:UPS[2].VhodFrekvencaL1:=Real_0;
mind_bool[403]:=Klima[2].NiTokaVVlazilcu; |  |  |  | Read_Real(rVar:=UPS[2].VhodFrekvencaL2,lo:=4806,hi:=4807); |  | 403:Klima[2].NiTokaVVlazilcu:=Bit_0; |  |  |  | 4807:UPS[2].VhodFrekvencaL2:=Real_0;
mind_bool[404]:=Klima[2].NiVodeVVlazilcu; |  |  |  | Read_Real(rVar:=UPS[2].VhodFrekvencaL3,lo:=4808,hi:=4809); |  | 404:Klima[2].NiVodeVVlazilcu:=Bit_0; |  |  |  | 4809:UPS[2].VhodFrekvencaL3:=Real_0;
mind_bool[405]:=Klima[2].NizekPritiskKompresor1; |  |  |  | Read_Real(rVar:=UPS[2].VhodNapetostL1,lo:=4810,hi:=4811); |  | 405:Klima[2].NizekPritiskKompresor1:=Bit_0; |  |  |  | 4811:UPS[2].VhodNapetostL1:=Real_0;
mind_bool[406]:=Klima[2].NizekPritiskKompresor2; |  |  |  | Read_Real(rVar:=UPS[2].VhodNapetostL2,lo:=4812,hi:=4813); |  | 406:Klima[2].NizekPritiskKompresor2:=Bit_0; |  |  |  | 4813:UPS[2].VhodNapetostL2:=Real_0;
mind_bool[407]:=Klima[2].NizkaTempVProstoru; |  |  |  | Read_Real(rVar:=UPS[2].VhodNapetostL3,lo:=4814,hi:=4815); |  | 407:Klima[2].NizkaTempVProstoru:=Bit_0; |  |  |  | 4815:UPS[2].VhodNapetostL3:=Real_0;
mind_bool[408]:=Klima[2].NizkaVlaznost; |  |  |  | Read_Real(rVar:=VlagaPovp[1],lo:=4816,hi:=4817); |  | 408:Klima[2].NizkaVlaznost:=Bit_0; |  |  |  | 4817:VlagaPovp[1]:=Real_0;
mind_bool[409]:=Klima[2].OnOffEnablingBySupervisor; |  |  |  | Read_Real(rVar:=VlagaPovp[2],lo:=4818,hi:=4819); |  | 409:Klima[2].OnOffEnablingBySupervisor:=Bit_0; |  |  |  | 4819:VlagaPovp[2]:=Real_0;
mind_bool[410]:=Klima[2].PozarniAlarm; |  |  |  | Read_Real(rVar:=VlagaPovp[3],lo:=4820,hi:=4821); |  | 410:Klima[2].PozarniAlarm:=Bit_0; |  |  |  | 4821:VlagaPovp[3]:=Real_0;
mind_bool[411]:=Klima[2].Razvlazevanje; |  |  |  | Read_Real(rVar:=RazlikaUr,lo:=4822,hi:=4823); |  | 411:Klima[2].Razvlazevanje:=Bit_0; |  |  |  | 4823:RazlikaUr:=Real_0;
mind_bool[412]:=Klima[2].RemoteOFFtoOutput; |  |  |  | Read_Real(rVar:=Klima[1].NastTempHlajenje,lo:=4824,hi:=4825); |  | 412:Klima[2].RemoteOFFtoOutput:=Bit_0; |  |  |  | 4825:Klima[1].NastTempHlajenje:=Real_0;
mind_bool[413]:=Klima[2].RocniIzklop; |  |  |  | Read_Real(rVar:=Klima[2].NastTempHlajenje,lo:=4826,hi:=4827); |  | 413:Klima[2].RocniIzklop:=Bit_0; |  |  |  | 4827:Klima[2].NastTempHlajenje:=Real_0;
mind_bool[414]:=Klima[2].SenzorjiStatus; |  |  |  | Read_Real(rVar:=Klima[3].NastTempHlajenje,lo:=4828,hi:=4829); |  | 414:Klima[2].SenzorjiStatus:=Bit_0; |  |  |  | 4829:Klima[3].NastTempHlajenje:=Real_0;
mind_bool[415]:=Klima[2].UnitOnOff; |  |  |  | Read_Real(rVar:=Klima[4].NastTempHlajenje,lo:=4830,hi:=4831); |  | 415:Klima[2].UnitOnOff:=Bit_0; |  |  |  | 4831:Klima[4].NastTempHlajenje:=Real_0;
mind_bool[416]:=Klima[2].VisokaTempVProstoru; |  |  |  | Read_Real(rVar:=Klima[5].NastTempHlajenje,lo:=4832,hi:=4833); |  | 416:Klima[2].VisokaTempVProstoru:=Bit_0; |  |  |  | 4833:Klima[5].NastTempHlajenje:=Real_0;
mind_bool[417]:=Klima[2].VisokaVlaznost; |  |  |  | Read_Real(rVar:=Klima[6].NastTempHlajenje,lo:=4834,hi:=4835); |  | 417:Klima[2].VisokaVlaznost:=Bit_0; |  |  |  | 4835:Klima[6].NastTempHlajenje:=Real_0;
mind_bool[418]:=Klima[2].VisokTokVVlazilcu; |  |  |  | Read_Real(rVar:=Klima[1].NastTempGretje,lo:=4836,hi:=4837); |  | 418:Klima[2].VisokTokVVlazilcu:=Bit_0; |  |  |  | 4837:Klima[1].NastTempGretje:=Real_0;
mind_bool[419]:=Klima[2].Vlazenje; |  |  |  | Read_Real(rVar:=Klima[2].NastTempGretje,lo:=4838,hi:=4839); |  | 419:Klima[2].Vlazenje:=Bit_0; |  |  |  | 4839:Klima[2].NastTempGretje:=Real_0;
mind_bool[420]:=Klima[2].ZamasenFilter; |  |  |  | Read_Real(rVar:=Klima[3].NastTempGretje,lo:=4840,hi:=4841); |  | 420:Klima[2].ZamasenFilter:=Bit_0; |  |  |  | 4841:Klima[3].NastTempGretje:=Real_0;
mind_bool[421]:=Klima[3].Deluje; |  |  |  | Read_Real(rVar:=Klima[4].NastTempGretje,lo:=4842,hi:=4843); |  | 421:Klima[3].Deluje:=Bit_0; |  |  |  | 4843:Klima[4].NastTempGretje:=Real_0;
mind_bool[422]:=Klima[3].FenThermalCutout; |  |  |  | Read_Real(rVar:=Klima[5].NastTempGretje,lo:=4844,hi:=4845); |  | 422:Klima[3].FenThermalCutout:=Bit_0; |  |  |  | 4845:Klima[5].NastTempGretje:=Real_0;
mind_bool[423]:=Klima[3].GeneralAlarm; |  |  |  | Read_Real(rVar:=Klima[6].NastTempGretje,lo:=4846,hi:=4847); |  | 423:Klima[3].GeneralAlarm:=Bit_0; |  |  |  | 4847:Klima[6].NastTempGretje:=Real_0;
mind_bool[424]:=Klima[3].Kompresor1naMejiObrUr; |  |  |  | Read_Real(rVar:=Klima[1].TempHladneVode,lo:=4848,hi:=4849); |  | 424:Klima[3].Kompresor1naMejiObrUr:=Bit_0; |  |  |  | 4849:Klima[1].TempHladneVode:=Real_0;
mind_bool[425]:=Klima[3].Kompresor2naMejiObrUr; |  |  |  | Read_Real(rVar:=Klima[2].TempHladneVode,lo:=4850,hi:=4851); |  | 425:Klima[3].Kompresor2naMejiObrUr:=Bit_0; |  |  |  | 4851:Klima[2].TempHladneVode:=Real_0;
mind_bool[426]:=Klima[3].Napaka; |  |  |  | Read_Real(rVar:=Klima[3].TempHladneVode,lo:=4852,hi:=4853); |  | 426:Klima[3].Napaka:=Bit_0; |  |  |  | 4853:Klima[3].TempHladneVode:=Real_0;
mind_bool[427]:=Klima[3].NapakaPriPretokuZraka; |  |  |  | Read_Real(rVar:=Klima[4].TempHladneVode,lo:=4854,hi:=4855); |  | 427:Klima[3].NapakaPriPretokuZraka:=Bit_0; |  |  |  | 4855:Klima[4].TempHladneVode:=Real_0;
mind_bool[428]:=Klima[3].NapakaSenzorTempIzpiha; |  |  |  | Read_Real(rVar:=Klima[5].TempHladneVode,lo:=4856,hi:=4857); |  | 428:Klima[3].NapakaSenzorTempIzpiha:=Bit_0; |  |  |  | 4857:Klima[5].TempHladneVode:=Real_0;
mind_bool[429]:=Klima[3].NapakaSenzorTempProstora; |  |  |  | Read_Real(rVar:=Klima[6].TempHladneVode,lo:=4858,hi:=4859); |  | 429:Klima[3].NapakaSenzorTempProstora:=Bit_0; |  |  |  | 4859:Klima[6].TempHladneVode:=Real_0;
mind_bool[430]:=Klima[3].NapakaSenzorVlaznosti; |  |  |  | Read_Real(rVar:=Klima[1].TempTopleVode,lo:=4860,hi:=4861); |  | 430:Klima[3].NapakaSenzorVlaznosti:=Bit_0; |  |  |  | 4861:Klima[1].TempTopleVode:=Real_0;
mind_bool[431]:=Klima[3].NapakaSenzorZunanjeTemp; |  |  |  | Read_Real(rVar:=Klima[2].TempTopleVode,lo:=4862,hi:=4863); |  | 431:Klima[3].NapakaSenzorZunanjeTemp:=Bit_0; |  |  |  | 4863:Klima[2].TempTopleVode:=Real_0;
mind_bool[432]:=Klima[3].NiTokaVVlazilcu; |  |  |  | Read_Real(rVar:=Klima[3].TempTopleVode,lo:=4864,hi:=4865); |  | 432:Klima[3].NiTokaVVlazilcu:=Bit_0; |  |  |  | 4865:Klima[3].TempTopleVode:=Real_0;
mind_bool[433]:=Klima[3].NiVodeVVlazilcu; |  |  |  | Read_Real(rVar:=Klima[4].TempTopleVode,lo:=4866,hi:=4867); |  | 433:Klima[3].NiVodeVVlazilcu:=Bit_0; |  |  |  | 4867:Klima[4].TempTopleVode:=Real_0;
mind_bool[434]:=Klima[3].NizekPritiskKompresor1; |  |  |  | Read_Real(rVar:=Klima[5].TempTopleVode,lo:=4868,hi:=4869); |  | 434:Klima[3].NizekPritiskKompresor1:=Bit_0; |  |  |  | 4869:Klima[5].TempTopleVode:=Real_0;
mind_bool[435]:=Klima[3].NizekPritiskKompresor2; |  |  |  | Read_Real(rVar:=Klima[6].TempTopleVode,lo:=4870,hi:=4871); |  | 435:Klima[3].NizekPritiskKompresor2:=Bit_0; |  |  |  | 4871:Klima[6].TempTopleVode:=Real_0;
mind_bool[436]:=Klima[3].NizkaTempVProstoru; |  |  |  | Read_Real(rVar:=ZamikVklopa,lo:=4872,hi:=4873); |  | 436:Klima[3].NizkaTempVProstoru:=Bit_0; |  |  |  | 4873:ZamikVklopa:=Real_0;
mind_bool[437]:=Klima[3].NizkaVlaznost; | [5 empty] | 437:Klima[3].NizkaVlaznost:=Bit_0;
mind_bool[438]:=Klima[3].OnOffEnablingBySupervisor; | [5 empty] | 438:Klima[3].OnOffEnablingBySupervisor:=Bit_0;
mind_bool[439]:=Klima[3].PozarniAlarm; | [5 empty] | 439:Klima[3].PozarniAlarm:=Bit_0;
mind_bool[440]:=Klima[3].Razvlazevanje; | [5 empty] | 440:Klima[3].Razvlazevanje:=Bit_0;
mind_bool[441]:=Klima[3].RemoteOFFtoOutput; | [5 empty] | 441:Klima[3].RemoteOFFtoOutput:=Bit_0;
mind_bool[442]:=Klima[3].RocniIzklop; | [5 empty] | 442:Klima[3].RocniIzklop:=Bit_0;
mind_bool[443]:=Klima[3].SenzorjiStatus; | [5 empty] | 443:Klima[3].SenzorjiStatus:=Bit_0;
mind_bool[444]:=Klima[3].UnitOnOff; | [5 empty] | 444:Klima[3].UnitOnOff:=Bit_0;
mind_bool[445]:=Klima[3].VisokaTempVProstoru; | [5 empty] | 445:Klima[3].VisokaTempVProstoru:=Bit_0;
mind_bool[446]:=Klima[3].VisokaVlaznost; | [5 empty] | 446:Klima[3].VisokaVlaznost:=Bit_0;
mind_bool[447]:=Klima[3].VisokTokVVlazilcu; | [5 empty] | 447:Klima[3].VisokTokVVlazilcu:=Bit_0;
mind_bool[448]:=Klima[3].Vlazenje; | [5 empty] | 448:Klima[3].Vlazenje:=Bit_0;
mind_bool[449]:=Klima[3].ZamasenFilter; | [5 empty] | 449:Klima[3].ZamasenFilter:=Bit_0;
mind_bool[450]:=Klima[4].Deluje; | [5 empty] | 450:Klima[4].Deluje:=Bit_0;
mind_bool[451]:=Klima[4].FenThermalCutout; | [5 empty] | 451:Klima[4].FenThermalCutout:=Bit_0;
mind_bool[452]:=Klima[4].GeneralAlarm; | [5 empty] | 452:Klima[4].GeneralAlarm:=Bit_0;
mind_bool[453]:=Klima[4].Kompresor1naMejiObrUr; | [5 empty] | 453:Klima[4].Kompresor1naMejiObrUr:=Bit_0;
mind_bool[454]:=Klima[4].Kompresor2naMejiObrUr; | [5 empty] | 454:Klima[4].Kompresor2naMejiObrUr:=Bit_0;
mind_bool[455]:=Klima[4].Napaka; | [5 empty] | 455:Klima[4].Napaka:=Bit_0;
mind_bool[456]:=Klima[4].NapakaPriPretokuZraka; | [5 empty] | 456:Klima[4].NapakaPriPretokuZraka:=Bit_0;
mind_bool[457]:=Klima[4].NapakaSenzorTempIzpiha; | [5 empty] | 457:Klima[4].NapakaSenzorTempIzpiha:=Bit_0;
mind_bool[458]:=Klima[4].NapakaSenzorTempProstora; | [5 empty] | 458:Klima[4].NapakaSenzorTempProstora:=Bit_0;
mind_bool[459]:=Klima[4].NapakaSenzorVlaznosti; | [5 empty] | 459:Klima[4].NapakaSenzorVlaznosti:=Bit_0;
mind_bool[460]:=Klima[4].NapakaSenzorZunanjeTemp; | [5 empty] | 460:Klima[4].NapakaSenzorZunanjeTemp:=Bit_0;
mind_bool[461]:=Klima[4].NiTokaVVlazilcu; | [5 empty] | 461:Klima[4].NiTokaVVlazilcu:=Bit_0;
mind_bool[462]:=Klima[4].NiVodeVVlazilcu; | [5 empty] | 462:Klima[4].NiVodeVVlazilcu:=Bit_0;
mind_bool[463]:=Klima[4].NizekPritiskKompresor1; | [5 empty] | 463:Klima[4].NizekPritiskKompresor1:=Bit_0;
mind_bool[464]:=Klima[4].NizekPritiskKompresor2; | [5 empty] | 464:Klima[4].NizekPritiskKompresor2:=Bit_0;
mind_bool[465]:=Klima[4].NizkaTempVProstoru; | [5 empty] | 465:Klima[4].NizkaTempVProstoru:=Bit_0;
mind_bool[466]:=Klima[4].NizkaVlaznost; | [5 empty] | 466:Klima[4].NizkaVlaznost:=Bit_0;
mind_bool[467]:=Klima[4].OnOffEnablingBySupervisor; | [5 empty] | 467:Klima[4].OnOffEnablingBySupervisor:=Bit_0;
mind_bool[468]:=Klima[4].PozarniAlarm; | [5 empty] | 468:Klima[4].PozarniAlarm:=Bit_0;
mind_bool[469]:=Klima[4].Razvlazevanje; | [5 empty] | 469:Klima[4].Razvlazevanje:=Bit_0;
mind_bool[470]:=Klima[4].RemoteOFFtoOutput; | [5 empty] | 470:Klima[4].RemoteOFFtoOutput:=Bit_0;
mind_bool[471]:=Klima[4].RocniIzklop; | [5 empty] | 471:Klima[4].RocniIzklop:=Bit_0;
mind_bool[472]:=Klima[4].SenzorjiStatus; | [5 empty] | 472:Klima[4].SenzorjiStatus:=Bit_0;
mind_bool[473]:=Klima[4].UnitOnOff; | [5 empty] | 473:Klima[4].UnitOnOff:=Bit_0;
mind_bool[474]:=Klima[4].VisokaTempVProstoru; | [5 empty] | 474:Klima[4].VisokaTempVProstoru:=Bit_0;
mind_bool[475]:=Klima[4].VisokaVlaznost; | [5 empty] | 475:Klima[4].VisokaVlaznost:=Bit_0;
mind_bool[476]:=Klima[4].VisokTokVVlazilcu; | [5 empty] | 476:Klima[4].VisokTokVVlazilcu:=Bit_0;
mind_bool[477]:=Klima[4].Vlazenje; | [5 empty] | 477:Klima[4].Vlazenje:=Bit_0;
mind_bool[478]:=Klima[4].ZamasenFilter; | [5 empty] | 478:Klima[4].ZamasenFilter:=Bit_0;
mind_bool[479]:=Klima[5].Deluje; | [5 empty] | 479:Klima[5].Deluje:=Bit_0;
mind_bool[480]:=Klima[5].FenThermalCutout; | [5 empty] | 480:Klima[5].FenThermalCutout:=Bit_0;
mind_bool[481]:=Klima[5].GeneralAlarm; | [5 empty] | 481:Klima[5].GeneralAlarm:=Bit_0;
mind_bool[482]:=Klima[5].Kompresor1naMejiObrUr; | [5 empty] | 482:Klima[5].Kompresor1naMejiObrUr:=Bit_0;
mind_bool[483]:=Klima[5].Kompresor2naMejiObrUr; | [5 empty] | 483:Klima[5].Kompresor2naMejiObrUr:=Bit_0;
mind_bool[484]:=Klima[5].Napaka; | [5 empty] | 484:Klima[5].Napaka:=Bit_0;
mind_bool[485]:=Klima[5].NapakaPriPretokuZraka; | [5 empty] | 485:Klima[5].NapakaPriPretokuZraka:=Bit_0;
mind_bool[486]:=Klima[5].NapakaSenzorTempIzpiha; | [5 empty] | 486:Klima[5].NapakaSenzorTempIzpiha:=Bit_0;
mind_bool[487]:=Klima[5].NapakaSenzorTempProstora; | [5 empty] | 487:Klima[5].NapakaSenzorTempProstora:=Bit_0;
mind_bool[488]:=Klima[5].NapakaSenzorVlaznosti; | [5 empty] | 488:Klima[5].NapakaSenzorVlaznosti:=Bit_0;
mind_bool[489]:=Klima[5].NapakaSenzorZunanjeTemp; | [5 empty] | 489:Klima[5].NapakaSenzorZunanjeTemp:=Bit_0;
mind_bool[490]:=Klima[5].NiTokaVVlazilcu; | [5 empty] | 490:Klima[5].NiTokaVVlazilcu:=Bit_0;
mind_bool[491]:=Klima[5].NiVodeVVlazilcu; | [5 empty] | 491:Klima[5].NiVodeVVlazilcu:=Bit_0;
mind_bool[492]:=Klima[5].NizekPritiskKompresor1; | [5 empty] | 492:Klima[5].NizekPritiskKompresor1:=Bit_0;
mind_bool[493]:=Klima[5].NizekPritiskKompresor2; | [5 empty] | 493:Klima[5].NizekPritiskKompresor2:=Bit_0;
mind_bool[494]:=Klima[5].NizkaTempVProstoru; | [5 empty] | 494:Klima[5].NizkaTempVProstoru:=Bit_0;
mind_bool[495]:=Klima[5].NizkaVlaznost; | [5 empty] | 495:Klima[5].NizkaVlaznost:=Bit_0;
mind_bool[496]:=Klima[5].OnOffEnablingBySupervisor; | [5 empty] | 496:Klima[5].OnOffEnablingBySupervisor:=Bit_0;
mind_bool[497]:=Klima[5].PozarniAlarm; | [5 empty] | 497:Klima[5].PozarniAlarm:=Bit_0;
mind_bool[498]:=Klima[5].Razvlazevanje; | [5 empty] | 498:Klima[5].Razvlazevanje:=Bit_0;
mind_bool[499]:=Klima[5].RemoteOFFtoOutput; | [5 empty] | 499:Klima[5].RemoteOFFtoOutput:=Bit_0;
mind_bool[500]:=Klima[5].RocniIzklop; | [5 empty] | 500:Klima[5].RocniIzklop:=Bit_0;
mind_bool[501]:=Klima[5].SenzorjiStatus; | [5 empty] | 501:Klima[5].SenzorjiStatus:=Bit_0;
mind_bool[502]:=Klima[5].UnitOnOff; | [5 empty] | 502:Klima[5].UnitOnOff:=Bit_0;
mind_bool[503]:=Klima[5].VisokaTempVProstoru; | [5 empty] | 503:Klima[5].VisokaTempVProstoru:=Bit_0;
mind_bool[504]:=Klima[5].VisokaVlaznost; | [5 empty] | 504:Klima[5].VisokaVlaznost:=Bit_0;
mind_bool[505]:=Klima[5].VisokTokVVlazilcu; | [5 empty] | 505:Klima[5].VisokTokVVlazilcu:=Bit_0;
mind_bool[506]:=Klima[5].Vlazenje; | [5 empty] | 506:Klima[5].Vlazenje:=Bit_0;
mind_bool[507]:=Klima[5].ZamasenFilter; | [5 empty] | 507:Klima[5].ZamasenFilter:=Bit_0;
mind_bool[508]:=Klima[6].Deluje; | [5 empty] | 508:Klima[6].Deluje:=Bit_0;
mind_bool[509]:=Klima[6].FenThermalCutout; | [5 empty] | 509:Klima[6].FenThermalCutout:=Bit_0;
mind_bool[510]:=Klima[6].GeneralAlarm; | [5 empty] | 510:Klima[6].GeneralAlarm:=Bit_0;
mind_bool[511]:=Klima[6].Kompresor1naMejiObrUr; | [5 empty] | 511:Klima[6].Kompresor1naMejiObrUr:=Bit_0;
mind_bool[512]:=Klima[6].Kompresor2naMejiObrUr; | [5 empty] | 512:Klima[6].Kompresor2naMejiObrUr:=Bit_0;
mind_bool[513]:=Klima[6].Napaka; | [5 empty] | 513:Klima[6].Napaka:=Bit_0;
mind_bool[514]:=Klima[6].NapakaPriPretokuZraka; | [5 empty] | 514:Klima[6].NapakaPriPretokuZraka:=Bit_0;
mind_bool[515]:=Klima[6].NapakaSenzorTempIzpiha; | [5 empty] | 515:Klima[6].NapakaSenzorTempIzpiha:=Bit_0;
mind_bool[516]:=Klima[6].NapakaSenzorTempProstora; | [5 empty] | 516:Klima[6].NapakaSenzorTempProstora:=Bit_0;
mind_bool[517]:=Klima[6].NapakaSenzorVlaznosti; | [5 empty] | 517:Klima[6].NapakaSenzorVlaznosti:=Bit_0;
mind_bool[518]:=Klima[6].NapakaSenzorZunanjeTemp; | [5 empty] | 518:Klima[6].NapakaSenzorZunanjeTemp:=Bit_0;
mind_bool[519]:=Klima[6].NiTokaVVlazilcu; | [5 empty] | 519:Klima[6].NiTokaVVlazilcu:=Bit_0;
mind_bool[520]:=Klima[6].NiVodeVVlazilcu; | [5 empty] | 520:Klima[6].NiVodeVVlazilcu:=Bit_0;
mind_bool[521]:=Klima[6].NizekPritiskKompresor1; | [5 empty] | 521:Klima[6].NizekPritiskKompresor1:=Bit_0;
mind_bool[522]:=Klima[6].NizekPritiskKompresor2; | [5 empty] | 522:Klima[6].NizekPritiskKompresor2:=Bit_0;
mind_bool[523]:=Klima[6].NizkaTempVProstoru; | [5 empty] | 523:Klima[6].NizkaTempVProstoru:=Bit_0;
mind_bool[524]:=Klima[6].NizkaVlaznost; | [5 empty] | 524:Klima[6].NizkaVlaznost:=Bit_0;
mind_bool[525]:=Klima[6].OnOffEnablingBySupervisor; | [5 empty] | 525:Klima[6].OnOffEnablingBySupervisor:=Bit_0;
mind_bool[526]:=Klima[6].PozarniAlarm; | [5 empty] | 526:Klima[6].PozarniAlarm:=Bit_0;
mind_bool[527]:=Klima[6].Razvlazevanje; | [5 empty] | 527:Klima[6].Razvlazevanje:=Bit_0;
mind_bool[528]:=Klima[6].RemoteOFFtoOutput; | [5 empty] | 528:Klima[6].RemoteOFFtoOutput:=Bit_0;
mind_bool[529]:=Klima[6].RocniIzklop; | [5 empty] | 529:Klima[6].RocniIzklop:=Bit_0;
mind_bool[530]:=Klima[6].SenzorjiStatus; | [5 empty] | 530:Klima[6].SenzorjiStatus:=Bit_0;
mind_bool[531]:=Klima[6].UnitOnOff; | [5 empty] | 531:Klima[6].UnitOnOff:=Bit_0;
mind_bool[532]:=Klima[6].VisokaTempVProstoru; | [5 empty] | 532:Klima[6].VisokaTempVProstoru:=Bit_0;
mind_bool[533]:=Klima[6].VisokaVlaznost; | [5 empty] | 533:Klima[6].VisokaVlaznost:=Bit_0;
mind_bool[534]:=Klima[6].VisokTokVVlazilcu; | [5 empty] | 534:Klima[6].VisokTokVVlazilcu:=Bit_0;
mind_bool[535]:=Klima[6].Vlazenje; | [5 empty] | 535:Klima[6].Vlazenje:=Bit_0;
mind_bool[536]:=Klima[6].ZamasenFilter; | [5 empty] | 536:Klima[6].ZamasenFilter:=Bit_0;
mind_bool[537]:=KlimeNaCas[0]; | [5 empty] | 537:KlimeNaCas[0]:=Bit_0;
mind_bool[538]:=KlimeNaCas[1]; | [5 empty] | 538:KlimeNaCas[1]:=Bit_0;
mind_bool[539]:=KlimeNaCas[2]; | [5 empty] | 539:KlimeNaCas[2]:=Bit_0;
mind_bool[540]:=KlimeNaCas[3]; | [5 empty] | 540:KlimeNaCas[3]:=Bit_0;
mind_bool[541]:=MrezaIzpad; | [5 empty] | 541:MrezaIzpad:=Bit_0;
mind_bool[542]:=MrezaIzpadKlimaOff[1]; | [5 empty] | 542:MrezaIzpadKlimaOff[1]:=Bit_0;
mind_bool[543]:=MrezaIzpadKlimaOff[2]; | [5 empty] | 543:MrezaIzpadKlimaOff[2]:=Bit_0;
mind_bool[544]:=MrezaIzpadKlimaOff[3]; | [5 empty] | 544:MrezaIzpadKlimaOff[3]:=Bit_0;
mind_bool[545]:=MrezaIzpadKlimaOff[4]; | [5 empty] | 545:MrezaIzpadKlimaOff[4]:=Bit_0;
mind_bool[546]:=MrezaIzpadKlimaOff[5]; | [5 empty] | 546:MrezaIzpadKlimaOff[5]:=Bit_0;
mind_bool[547]:=MrezaIzpadKlimaOff[6]; | [5 empty] | 547:MrezaIzpadKlimaOff[6]:=Bit_0;
mind_bool[548]:=NapakaSenzorTemp[1]; | [5 empty] | 548:NapakaSenzorTemp[1]:=Bit_0;
mind_bool[549]:=NapakaSenzorTemp[2]; | [5 empty] | 549:NapakaSenzorTemp[2]:=Bit_0;
mind_bool[550]:=NapakaSenzorTemp[3]; | [5 empty] | 550:NapakaSenzorTemp[3]:=Bit_0;
mind_bool[551]:=NapakaSenzorTemp[4]; | [5 empty] | 551:NapakaSenzorTemp[4]:=Bit_0;
mind_bool[552]:=NapakaSenzorTemp[5]; | [5 empty] | 552:NapakaSenzorTemp[5]:=Bit_0;
mind_bool[553]:=NapakaSenzorTemp[6]; | [5 empty] | 553:NapakaSenzorTemp[6]:=Bit_0;
mind_bool[554]:=NapakaSenzorVlaga[1]; | [5 empty] | 554:NapakaSenzorVlaga[1]:=Bit_0;
mind_bool[555]:=NapakaSenzorVlaga[2]; | [5 empty] | 555:NapakaSenzorVlaga[2]:=Bit_0;
mind_bool[556]:=NapakaSenzorVlaga[3]; | [5 empty] | 556:NapakaSenzorVlaga[3]:=Bit_0;
mind_bool[557]:=NapakaSenzorVlaga[4]; | [5 empty] | 557:NapakaSenzorVlaga[4]:=Bit_0;
mind_bool[558]:=NapakaSenzorVlaga[5]; | [5 empty] | 558:NapakaSenzorVlaga[5]:=Bit_0;
mind_bool[559]:=NapakaSenzorVlaga[6]; | [5 empty] | 559:NapakaSenzorVlaga[6]:=Bit_0;
mind_bool[560]:=PMM.Napaka; | [5 empty] | 560:PMM.Napaka:=Bit_0;
mind_bool[561]:=PMMOverCurrentBetw[1]; | [5 empty] | 561:PMMOverCurrentBetw[1]:=Bit_0;
mind_bool[562]:=PMMOverCurrentBetw[2]; | [5 empty] | 562:PMMOverCurrentBetw[2]:=Bit_0;
mind_bool[563]:=PMMOverCurrentBetw[3]; | [5 empty] | 563:PMMOverCurrentBetw[3]:=Bit_0;
mind_bool[564]:=PMMOverCurrentOver[1]; | [5 empty] | 564:PMMOverCurrentOver[1]:=Bit_0;
mind_bool[565]:=PMMOverCurrentOver[2]; | [5 empty] | 565:PMMOverCurrentOver[2]:=Bit_0;
mind_bool[566]:=PMMOverCurrentOver[3]; | [5 empty] | 566:PMMOverCurrentOver[3]:=Bit_0;
mind_bool[567]:=SetDateTime; | [5 empty] | 567:SetDateTime:=Bit_0;
mind_bool[568]:=SetDateTimeDemand; | [5 empty] | 568:SetDateTimeDemand:=Bit_0;
mind_bool[569]:=SetDateTimeError; | [5 empty] | 569:SetDateTimeError:=Bit_0;
mind_bool[570]:=SetDateTimeFinished; | [5 empty] | 570:SetDateTimeFinished:=Bit_0;
mind_bool[571]:=SetRemoteOnOff[1]; | [5 empty] | 571:SetRemoteOnOff[1]:=Bit_0;
mind_bool[572]:=SetRemoteOnOff[2]; | [5 empty] | 572:SetRemoteOnOff[2]:=Bit_0;
mind_bool[573]:=SlabaBaterijaPLC_A1; | [5 empty] | 573:SlabaBaterijaPLC_A1:=Bit_0;
mind_bool[574]:=TempTSprevisoka[1]; | [5 empty] | 574:TempTSprevisoka[1]:=Bit_0;
mind_bool[575]:=TempTSprevisoka[2]; | [5 empty] | 575:TempTSprevisoka[2]:=Bit_0;
mind_bool[576]:=TempTSprevisoka[3]; | [5 empty] | 576:TempTSprevisoka[3]:=Bit_0;
mind_bool[577]:=TempTSprevisokaSum; | [5 empty] | 577:TempTSprevisokaSum:=Bit_0;
mind_bool[578]:=UPS1Errors[10]; | [5 empty] | 578:UPS1Errors[10]:=Bit_0;
mind_bool[579]:=UPS1Errors[11]; | [5 empty] | 579:UPS1Errors[11]:=Bit_0;
mind_bool[580]:=UPS1Errors[12]; | [5 empty] | 580:UPS1Errors[12]:=Bit_0;
mind_bool[581]:=UPS1Errors[13]; | [5 empty] | 581:UPS1Errors[13]:=Bit_0;
mind_bool[582]:=UPS1Errors[14]; | [5 empty] | 582:UPS1Errors[14]:=Bit_0;
mind_bool[583]:=UPS1Errors[15]; | [5 empty] | 583:UPS1Errors[15]:=Bit_0;
mind_bool[584]:=UPS1Errors[16]; | [5 empty] | 584:UPS1Errors[16]:=Bit_0;
mind_bool[585]:=UPS1Errors[17]; | [5 empty] | 585:UPS1Errors[17]:=Bit_0;
mind_bool[586]:=UPS1Errors[18]; | [5 empty] | 586:UPS1Errors[18]:=Bit_0;
mind_bool[587]:=UPS1Errors[19]; | [5 empty] | 587:UPS1Errors[19]:=Bit_0;
mind_bool[588]:=UPS1Errors[1]; | [5 empty] | 588:UPS1Errors[1]:=Bit_0;
mind_bool[589]:=UPS1Errors[20]; | [5 empty] | 589:UPS1Errors[20]:=Bit_0;
mind_bool[590]:=UPS1Errors[21]; | [5 empty] | 590:UPS1Errors[21]:=Bit_0;
mind_bool[591]:=UPS1Errors[22]; | [5 empty] | 591:UPS1Errors[22]:=Bit_0;
mind_bool[592]:=UPS1Errors[23]; | [5 empty] | 592:UPS1Errors[23]:=Bit_0;
mind_bool[593]:=UPS1Errors[24]; | [5 empty] | 593:UPS1Errors[24]:=Bit_0;
mind_bool[594]:=UPS1Errors[25]; | [5 empty] | 594:UPS1Errors[25]:=Bit_0;
mind_bool[595]:=UPS1Errors[2]; | [5 empty] | 595:UPS1Errors[2]:=Bit_0;
mind_bool[596]:=UPS1Errors[3]; | [5 empty] | 596:UPS1Errors[3]:=Bit_0;
mind_bool[597]:=UPS1Errors[4]; | [5 empty] | 597:UPS1Errors[4]:=Bit_0;
mind_bool[598]:=UPS1Errors[5]; | [5 empty] | 598:UPS1Errors[5]:=Bit_0;
mind_bool[599]:=UPS1Errors[6]; | [5 empty] | 599:UPS1Errors[6]:=Bit_0;
mind_bool[600]:=UPS1Errors[7]; | [5 empty] | 600:UPS1Errors[7]:=Bit_0;
mind_bool[601]:=UPS1Errors[8]; | [5 empty] | 601:UPS1Errors[8]:=Bit_0;
mind_bool[602]:=UPS1Errors[9]; | [5 empty] | 602:UPS1Errors[9]:=Bit_0;
mind_bool[603]:=UPS2Errors[10]; | [5 empty] | 603:UPS2Errors[10]:=Bit_0;
mind_bool[604]:=UPS2Errors[11]; | [5 empty] | 604:UPS2Errors[11]:=Bit_0;
mind_bool[605]:=UPS2Errors[12]; | [5 empty] | 605:UPS2Errors[12]:=Bit_0;
mind_bool[606]:=UPS2Errors[13]; | [5 empty] | 606:UPS2Errors[13]:=Bit_0;
mind_bool[607]:=UPS2Errors[14]; | [5 empty] | 607:UPS2Errors[14]:=Bit_0;
mind_bool[608]:=UPS2Errors[15]; | [5 empty] | 608:UPS2Errors[15]:=Bit_0;
mind_bool[609]:=UPS2Errors[16]; | [5 empty] | 609:UPS2Errors[16]:=Bit_0;
mind_bool[610]:=UPS2Errors[17]; | [5 empty] | 610:UPS2Errors[17]:=Bit_0;
mind_bool[611]:=UPS2Errors[18]; | [5 empty] | 611:UPS2Errors[18]:=Bit_0;
mind_bool[612]:=UPS2Errors[19]; | [5 empty] | 612:UPS2Errors[19]:=Bit_0;
mind_bool[613]:=UPS2Errors[1]; | [5 empty] | 613:UPS2Errors[1]:=Bit_0;
mind_bool[614]:=UPS2Errors[20]; | [5 empty] | 614:UPS2Errors[20]:=Bit_0;
mind_bool[615]:=UPS2Errors[21]; | [5 empty] | 615:UPS2Errors[21]:=Bit_0;
mind_bool[616]:=UPS2Errors[22]; | [5 empty] | 616:UPS2Errors[22]:=Bit_0;
mind_bool[617]:=UPS2Errors[23]; | [5 empty] | 617:UPS2Errors[23]:=Bit_0;
mind_bool[618]:=UPS2Errors[24]; | [5 empty] | 618:UPS2Errors[24]:=Bit_0;
mind_bool[619]:=UPS2Errors[25]; | [5 empty] | 619:UPS2Errors[25]:=Bit_0;
mind_bool[620]:=UPS2Errors[2]; | [5 empty] | 620:UPS2Errors[2]:=Bit_0;
mind_bool[621]:=UPS2Errors[3]; | [5 empty] | 621:UPS2Errors[3]:=Bit_0;
mind_bool[622]:=UPS2Errors[4]; | [5 empty] | 622:UPS2Errors[4]:=Bit_0;
mind_bool[623]:=UPS2Errors[5]; | [5 empty] | 623:UPS2Errors[5]:=Bit_0;
mind_bool[624]:=UPS2Errors[6]; | [5 empty] | 624:UPS2Errors[6]:=Bit_0;
mind_bool[625]:=UPS2Errors[7]; | [5 empty] | 625:UPS2Errors[7]:=Bit_0;
mind_bool[626]:=UPS2Errors[8]; | [5 empty] | 626:UPS2Errors[8]:=Bit_0;
mind_bool[627]:=UPS2Errors[9]; | [5 empty] | 627:UPS2Errors[9]:=Bit_0;
mind_bool[628]:=UPS[1].AlarmAwaitingPower; | [5 empty] | 628:UPS[1].AlarmAwaitingPower:=Bit_0;
mind_bool[629]:=UPS[1].AlarmBypassBad; | [5 empty] | 629:UPS[1].AlarmBypassBad:=Bit_0;
mind_bool[630]:=UPS[1].AlarmChargerFailed; | [5 empty] | 630:UPS[1].AlarmChargerFailed:=Bit_0;
mind_bool[631]:=UPS[1].AlarmCommunicationsLost; | [5 empty] | 631:UPS[1].AlarmCommunicationsLost:=Bit_0;
mind_bool[632]:=UPS[1].AlarmDepletedBattery; | [5 empty] | 632:UPS[1].AlarmDepletedBattery:=Bit_0;
mind_bool[633]:=UPS[1].AlarmDiagnosticTestFailed; | [5 empty] | 633:UPS[1].AlarmDiagnosticTestFailed:=Bit_0;
mind_bool[634]:=UPS[1].AlarmInverterError; | [5 empty] | 634:UPS[1].AlarmInverterError:=Bit_0;
mind_bool[635]:=UPS[1].AlarmIzhodOffKotZahtevano; | [5 empty] | 635:UPS[1].AlarmIzhodOffKotZahtevano:=Bit_0;
mind_bool[636]:=UPS[1].AlarmIzhodPreobremenjen; | [5 empty] | 636:UPS[1].AlarmIzhodPreobremenjen:=Bit_0;
mind_bool[637]:=UPS[1].AlarmLowBattery; | [5 empty] | 637:UPS[1].AlarmLowBattery:=Bit_0;
mind_bool[638]:=UPS[1].AlarmNapakaNaVarovalki; | [5 empty] | 638:UPS[1].AlarmNapakaNaVarovalki:=Bit_0;
mind_bool[639]:=UPS[1].AlarmNapakaNaVentilatorju; | [5 empty] | 639:UPS[1].AlarmNapakaNaVentilatorju:=Bit_0;
mind_bool[640]:=UPS[1].AlarmOnBattery; | [5 empty] | 640:UPS[1].AlarmOnBattery:=Bit_0;
mind_bool[641]:=UPS[1].AlarmOnBypass; | [5 empty] | 641:UPS[1].AlarmOnBypass:=Bit_0;
mind_bool[642]:=UPS[1].AlarmShutdownImminent; | [5 empty] | 642:UPS[1].AlarmShutdownImminent:=Bit_0;
mind_bool[643]:=UPS[1].AlarmShutdownPending; | [5 empty] | 643:UPS[1].AlarmShutdownPending:=Bit_0;
mind_bool[644]:=UPS[1].AlarmSlabaBaterija; | [5 empty] | 644:UPS[1].AlarmSlabaBaterija:=Bit_0;
mind_bool[645]:=UPS[1].AlarmSplosnaNapaka; | [5 empty] | 645:UPS[1].AlarmSplosnaNapaka:=Bit_0;
mind_bool[646]:=UPS[1].AlarmStanjeIzhodaIzvenToleranc; | [5 empty] | 646:UPS[1].AlarmStanjeIzhodaIzvenToleranc:=Bit_0;
mind_bool[647]:=UPS[1].AlarmStanjeVhodaIzvenToleranc; | [5 empty] | 647:UPS[1].AlarmStanjeVhodaIzvenToleranc:=Bit_0;
mind_bool[648]:=UPS[1].AlarmTemperaturaIzvenToleranc; | [5 empty] | 648:UPS[1].AlarmTemperaturaIzvenToleranc:=Bit_0;
mind_bool[649]:=UPS[1].AlarmTestInProgres; | [5 empty] | 649:UPS[1].AlarmTestInProgres:=Bit_0;
mind_bool[650]:=UPS[1].AlarmUPSIzhodOff; | [5 empty] | 650:UPS[1].AlarmUPSIzhodOff:=Bit_0;
mind_bool[651]:=UPS[1].AlarmUPSOffKotZahtevano; | [5 empty] | 651:UPS[1].AlarmUPSOffKotZahtevano:=Bit_0;
mind_bool[652]:=UPS[1].AlarmUPSSystemOff; | [5 empty] | 652:UPS[1].AlarmUPSSystemOff:=Bit_0;
mind_bool[653]:=UPS[1].Napaka; | [5 empty] | 653:UPS[1].Napaka:=Bit_0;
mind_bool[654]:=UPS[1].StatusEcomodeAktiven; | [5 empty] | 654:UPS[1].StatusEcomodeAktiven:=Bit_0;
mind_bool[655]:=UPS[1].StatusInverterIsOn; | [5 empty] | 655:UPS[1].StatusInverterIsOn:=Bit_0;
mind_bool[656]:=UPS[1].StatusStopOperation; | [5 empty] | 656:UPS[1].StatusStopOperation:=Bit_0;
mind_bool[657]:=UPS[2].AlarmAwaitingPower; | [5 empty] | 657:UPS[2].AlarmAwaitingPower:=Bit_0;
mind_bool[658]:=UPS[2].AlarmBypassBad; | [5 empty] | 658:UPS[2].AlarmBypassBad:=Bit_0;
mind_bool[659]:=UPS[2].AlarmChargerFailed; | [5 empty] | 659:UPS[2].AlarmChargerFailed:=Bit_0;
mind_bool[660]:=UPS[2].AlarmCommunicationsLost; | [5 empty] | 660:UPS[2].AlarmCommunicationsLost:=Bit_0;
mind_bool[661]:=UPS[2].AlarmDepletedBattery; | [5 empty] | 661:UPS[2].AlarmDepletedBattery:=Bit_0;
mind_bool[662]:=UPS[2].AlarmDiagnosticTestFailed; | [5 empty] | 662:UPS[2].AlarmDiagnosticTestFailed:=Bit_0;
mind_bool[663]:=UPS[2].AlarmInverterError; | [5 empty] | 663:UPS[2].AlarmInverterError:=Bit_0;
mind_bool[664]:=UPS[2].AlarmIzhodOffKotZahtevano; | [5 empty] | 664:UPS[2].AlarmIzhodOffKotZahtevano:=Bit_0;
mind_bool[665]:=UPS[2].AlarmIzhodPreobremenjen; | [5 empty] | 665:UPS[2].AlarmIzhodPreobremenjen:=Bit_0;
mind_bool[666]:=UPS[2].AlarmLowBattery; | [5 empty] | 666:UPS[2].AlarmLowBattery:=Bit_0;
mind_bool[667]:=UPS[2].AlarmNapakaNaVarovalki; | [5 empty] | 667:UPS[2].AlarmNapakaNaVarovalki:=Bit_0;
mind_bool[668]:=UPS[2].AlarmNapakaNaVentilatorju; | [5 empty] | 668:UPS[2].AlarmNapakaNaVentilatorju:=Bit_0;
mind_bool[669]:=UPS[2].AlarmOnBattery; | [5 empty] | 669:UPS[2].AlarmOnBattery:=Bit_0;
mind_bool[670]:=UPS[2].AlarmOnBypass; | [5 empty] | 670:UPS[2].AlarmOnBypass:=Bit_0;
mind_bool[671]:=UPS[2].AlarmShutdownImminent; | [5 empty] | 671:UPS[2].AlarmShutdownImminent:=Bit_0;
mind_bool[672]:=UPS[2].AlarmShutdownPending; | [5 empty] | 672:UPS[2].AlarmShutdownPending:=Bit_0;
mind_bool[673]:=UPS[2].AlarmSlabaBaterija; | [5 empty] | 673:UPS[2].AlarmSlabaBaterija:=Bit_0;
mind_bool[674]:=UPS[2].AlarmSplosnaNapaka; | [5 empty] | 674:UPS[2].AlarmSplosnaNapaka:=Bit_0;
mind_bool[675]:=UPS[2].AlarmStanjeIzhodaIzvenToleranc; | [5 empty] | 675:UPS[2].AlarmStanjeIzhodaIzvenToleranc:=Bit_0;
mind_bool[676]:=UPS[2].AlarmStanjeVhodaIzvenToleranc; | [5 empty] | 676:UPS[2].AlarmStanjeVhodaIzvenToleranc:=Bit_0;
mind_bool[677]:=UPS[2].AlarmTemperaturaIzvenToleranc; | [5 empty] | 677:UPS[2].AlarmTemperaturaIzvenToleranc:=Bit_0;
mind_bool[678]:=UPS[2].AlarmTestInProgres; | [5 empty] | 678:UPS[2].AlarmTestInProgres:=Bit_0;
mind_bool[679]:=UPS[2].AlarmUPSIzhodOff; | [5 empty] | 679:UPS[2].AlarmUPSIzhodOff:=Bit_0;
mind_bool[680]:=UPS[2].AlarmUPSOffKotZahtevano; | [5 empty] | 680:UPS[2].AlarmUPSOffKotZahtevano:=Bit_0;
mind_bool[681]:=UPS[2].AlarmUPSSystemOff; | [5 empty] | 681:UPS[2].AlarmUPSSystemOff:=Bit_0;
mind_bool[682]:=UPS[2].Napaka; | [5 empty] | 682:UPS[2].Napaka:=Bit_0;
mind_bool[683]:=UPS[2].StatusEcomodeAktiven; | [5 empty] | 683:UPS[2].StatusEcomodeAktiven:=Bit_0;
mind_bool[684]:=UPS[2].StatusInverterIsOn; | [5 empty] | 684:UPS[2].StatusInverterIsOn:=Bit_0;
mind_bool[685]:=UPS[2].StatusStopOperation; | [5 empty] | 685:UPS[2].StatusStopOperation:=Bit_0;
mind_bool[686]:=UserLoggedIn; | [5 empty] | 686:UserLoggedIn:=Bit_0;
mind_bool[687]:=DIN_A1Q11_OdcUpsB_IZP; | [5 empty] | 687:DIN_A1Q11_OdcUpsB_IZP:=Bit_0;
mind_bool[688]:=DIN_A1Q12_OdcByUpsB_IZP; | [5 empty] | 688:DIN_A1Q12_OdcByUpsB_IZP:=Bit_0;
mind_bool[689]:=DIN_A1Q13_OdcByB_IZP; | [5 empty] | 689:DIN_A1Q13_OdcByB_IZP:=Bit_0;
mind_bool[690]:=DIN_UQ11_OdcPMMB_IZP; | [5 empty] | 690:DIN_UQ11_OdcPMMB_IZP:=Bit_0;
mind_bool[691]:=DIN_UQ12_OdcPMMB_IZP; | [5 empty] | 691:DIN_UQ12_OdcPMMB_IZP:=Bit_0;
mind_bool[692]:=DIN_PrenapA3_OK; | [5 empty] | 692:DIN_PrenapA3_OK:=Bit_0;
mind_bool[693]:=DIN_A1Q0_GlavnoStiB_ON; | [5 empty] | 693:DIN_A1Q0_GlavnoStiB_ON:=Bit_0;
mind_bool[694]:=DIN_A1Q11_OdcUpsB_ON; | [5 empty] | 694:DIN_A1Q11_OdcUpsB_ON:=Bit_0;
mind_bool[695]:=DIN_A1Q12_OdcByUpsB_ON; | [5 empty] | 695:DIN_A1Q12_OdcByUpsB_ON:=Bit_0;
mind_bool[696]:=DI_A1Q13_OdcByB_ON; | [5 empty] | 696:DI_A1Q13_OdcByB_ON:=Bit_0;
mind_bool[697]:=DIN_A1Q01_DovUpsB_ON; | [5 empty] | 697:DIN_A1Q01_DovUpsB_ON:=Bit_0;
mind_bool[698]:=DI_A1Q02_DovByB_ON; | [5 empty] | 698:DI_A1Q02_DovByB_ON:=Bit_0;
mind_bool[699]:=DIN_UQ11_OdcPMMB_ON; | [5 empty] | 699:DIN_UQ11_OdcPMMB_ON:=Bit_0;
mind_bool[700]:=DI_UQ12_OdcPMMB_ON; | [5 empty] | 700:DI_UQ12_OdcPMMB_ON:=Bit_0;
mind_bool[701]:=Klima[1].NapacnoGesloAlarm; | [5 empty] | 701:Klima[1].NapacnoGesloAlarm:=Bit_0;
mind_bool[702]:=Klima[1].ExtTempHumAlarm; | [5 empty] | 702:Klima[1].ExtTempHumAlarm:=Bit_0;
mind_bool[703]:=Klima[1].PoplavniAlarm; | [5 empty] | 703:Klima[1].PoplavniAlarm:=Bit_0;
mind_bool[704]:=Klima[1].VisokPritiskKompresor1; | [5 empty] | 704:Klima[1].VisokPritiskKompresor1:=Bit_0;
mind_bool[705]:=Klima[1].VisokPritiskKompresor2; | [5 empty] | 705:Klima[1].VisokPritiskKompresor2:=Bit_0;
mind_bool[706]:=Klima[1].ElVentilKompresor1ERR; | [5 empty] | 706:Klima[1].ElVentilKompresor1ERR:=Bit_0;
mind_bool[707]:=Klima[1].ElVentilKompresor2ERR; | [5 empty] | 707:Klima[1].ElVentilKompresor2ERR:=Bit_0;
mind_bool[708]:=Klima[1].WrongPhaseSeqAlarm; | [5 empty] | 708:Klima[1].WrongPhaseSeqAlarm:=Bit_0;
mind_bool[709]:=Klima[1].PrekinjenLANalarm; | [5 empty] | 709:Klima[1].PrekinjenLANalarm:=Bit_0;
mind_bool[710]:=Klima[1].CWTempHighForDehum; | [5 empty] | 710:Klima[1].CWTempHighForDehum:=Bit_0;
mind_bool[711]:=Klima[1].CWVentilErrOrLowFlow; | [5 empty] | 711:Klima[1].CWVentilErrOrLowFlow:=Bit_0;
mind_bool[712]:=Klima[1].NapakaPriPretokuVode; | [5 empty] | 712:Klima[1].NapakaPriPretokuVode:=Bit_0;
mind_bool[713]:=Klima[1].CWhighTemp; | [5 empty] | 713:Klima[1].CWhighTemp:=Bit_0;
mind_bool[714]:=Klima[1].NapakaSenzorHotWTemp; | [5 empty] | 714:Klima[1].NapakaSenzorHotWTemp:=Bit_0;
mind_bool[715]:=Klima[1].NapakaSenzorCondWTemp; | [5 empty] | 715:Klima[1].NapakaSenzorCondWTemp:=Bit_0;
mind_bool[716]:=Klima[1].NapakaSenzorCW; | [5 empty] | 716:Klima[1].NapakaSenzorCW:=Bit_0;
mind_bool[717]:=Klima[1].Kompresor3naMejiObrUr; | [5 empty] | 717:Klima[1].Kompresor3naMejiObrUr:=Bit_0;
mind_bool[718]:=Klima[1].Kompresor4naMejiObrUr; | [5 empty] | 718:Klima[1].Kompresor4naMejiObrUr:=Bit_0;
mind_bool[719]:=Klima[1].ZracniFilterNaMejiObrUr; | [5 empty] | 719:Klima[1].ZracniFilterNaMejiObrUr:=Bit_0;
mind_bool[720]:=Klima[1].Grelec1naMejiObrUr; | [5 empty] | 720:Klima[1].Grelec1naMejiObrUr:=Bit_0;
mind_bool[721]:=Klima[1].Grelec2naMejiObrUr; | [5 empty] | 721:Klima[1].Grelec2naMejiObrUr:=Bit_0;
mind_bool[722]:=Klima[1].VlazilecNaMejiObrUr; | [5 empty] | 722:Klima[1].VlazilecNaMejiObrUr:=Bit_0;
mind_bool[723]:=Klima[1].AirCondUnitNaMejiObrUr; | [5 empty] | 723:Klima[1].AirCondUnitNaMejiObrUr:=Bit_0;
mind_bool[724]:=Klima[1].DigIn2Alarm; | [5 empty] | 724:Klima[1].DigIn2Alarm:=Bit_0;
mind_bool[725]:=Klima[1].DigIn4Alarm; | [5 empty] | 725:Klima[1].DigIn4Alarm:=Bit_0;
mind_bool[726]:=Klima[1].DigIn6Alarm; | [5 empty] | 726:Klima[1].DigIn6Alarm:=Bit_0;
mind_bool[727]:=Klima[1].VlazilecGenAlarm; | [5 empty] | 727:Klima[1].VlazilecGenAlarm:=Bit_0;
mind_bool[728]:=Klima[1].General2ndLevAlarm; | [5 empty] | 728:Klima[1].General2ndLevAlarm:=Bit_0;
mind_bool[729]:=Klima[1].UnitOnRotAlarm; | [5 empty] | 729:Klima[1].UnitOnRotAlarm:=Bit_0;
mind_bool[730]:=Klima[1].UnitOnAlarmA; | [5 empty] | 730:Klima[1].UnitOnAlarmA:=Bit_0;
mind_bool[731]:=Klima[1].UnitOnAlarmB; | [5 empty] | 731:Klima[1].UnitOnAlarmB:=Bit_0;
mind_bool[732]:=Klima[1].UnitOnAlarmC; | [5 empty] | 732:Klima[1].UnitOnAlarmC:=Bit_0;
mind_bool[733]:=Klima[2].NapacnoGesloAlarm; | [5 empty] | 733:Klima[2].NapacnoGesloAlarm:=Bit_0;
mind_bool[734]:=Klima[2].ExtTempHumAlarm; | [5 empty] | 734:Klima[2].ExtTempHumAlarm:=Bit_0;
mind_bool[735]:=Klima[2].PoplavniAlarm; | [5 empty] | 735:Klima[2].PoplavniAlarm:=Bit_0;
mind_bool[736]:=Klima[2].VisokPritiskKompresor1; | [5 empty] | 736:Klima[2].VisokPritiskKompresor1:=Bit_0;
mind_bool[737]:=Klima[2].VisokPritiskKompresor2; | [5 empty] | 737:Klima[2].VisokPritiskKompresor2:=Bit_0;
mind_bool[738]:=Klima[2].ElVentilKompresor1ERR; | [5 empty] | 738:Klima[2].ElVentilKompresor1ERR:=Bit_0;
mind_bool[739]:=Klima[2].ElVentilKompresor2ERR; | [5 empty] | 739:Klima[2].ElVentilKompresor2ERR:=Bit_0;
mind_bool[740]:=Klima[2].WrongPhaseSeqAlarm; | [5 empty] | 740:Klima[2].WrongPhaseSeqAlarm:=Bit_0;
mind_bool[741]:=Klima[2].PrekinjenLANalarm; | [5 empty] | 741:Klima[2].PrekinjenLANalarm:=Bit_0;
mind_bool[742]:=Klima[2].CWTempHighForDehum; | [5 empty] | 742:Klima[2].CWTempHighForDehum:=Bit_0;
mind_bool[743]:=Klima[2].CWVentilErrOrLowFlow; | [5 empty] | 743:Klima[2].CWVentilErrOrLowFlow:=Bit_0;
mind_bool[744]:=Klima[2].NapakaPriPretokuVode; | [5 empty] | 744:Klima[2].NapakaPriPretokuVode:=Bit_0;
mind_bool[745]:=Klima[2].CWhighTemp; | [5 empty] | 745:Klima[2].CWhighTemp:=Bit_0;
mind_bool[746]:=Klima[2].NapakaSenzorHotWTemp; | [5 empty] | 746:Klima[2].NapakaSenzorHotWTemp:=Bit_0;
mind_bool[747]:=Klima[2].NapakaSenzorCondWTemp; | [5 empty] | 747:Klima[2].NapakaSenzorCondWTemp:=Bit_0;
mind_bool[748]:=Klima[2].NapakaSenzorCW; | [5 empty] | 748:Klima[2].NapakaSenzorCW:=Bit_0;
mind_bool[749]:=Klima[2].Kompresor3naMejiObrUr; | [5 empty] | 749:Klima[2].Kompresor3naMejiObrUr:=Bit_0;
mind_bool[750]:=Klima[2].Kompresor4naMejiObrUr; | [5 empty] | 750:Klima[2].Kompresor4naMejiObrUr:=Bit_0;
mind_bool[751]:=Klima[2].ZracniFilterNaMejiObrUr; | [5 empty] | 751:Klima[2].ZracniFilterNaMejiObrUr:=Bit_0;
mind_bool[752]:=Klima[2].Grelec1naMejiObrUr; | [5 empty] | 752:Klima[2].Grelec1naMejiObrUr:=Bit_0;
mind_bool[753]:=Klima[2].Grelec2naMejiObrUr; | [5 empty] | 753:Klima[2].Grelec2naMejiObrUr:=Bit_0;
mind_bool[754]:=Klima[2].VlazilecNaMejiObrUr; | [5 empty] | 754:Klima[2].VlazilecNaMejiObrUr:=Bit_0;
mind_bool[755]:=Klima[2].AirCondUnitNaMejiObrUr; | [5 empty] | 755:Klima[2].AirCondUnitNaMejiObrUr:=Bit_0;
mind_bool[756]:=Klima[2].DigIn2Alarm; | [5 empty] | 756:Klima[2].DigIn2Alarm:=Bit_0;
mind_bool[757]:=Klima[2].DigIn4Alarm; | [5 empty] | 757:Klima[2].DigIn4Alarm:=Bit_0;
mind_bool[758]:=Klima[2].DigIn6Alarm; | [5 empty] | 758:Klima[2].DigIn6Alarm:=Bit_0;
mind_bool[759]:=Klima[2].VlazilecGenAlarm; | [5 empty] | 759:Klima[2].VlazilecGenAlarm:=Bit_0;
mind_bool[760]:=Klima[2].General2ndLevAlarm; | [5 empty] | 760:Klima[2].General2ndLevAlarm:=Bit_0;
mind_bool[761]:=Klima[2].UnitOnRotAlarm; | [5 empty] | 761:Klima[2].UnitOnRotAlarm:=Bit_0;
mind_bool[762]:=Klima[2].UnitOnAlarmA; | [5 empty] | 762:Klima[2].UnitOnAlarmA:=Bit_0;
mind_bool[763]:=Klima[2].UnitOnAlarmB; | [5 empty] | 763:Klima[2].UnitOnAlarmB:=Bit_0;
mind_bool[764]:=Klima[2].UnitOnAlarmC; | [5 empty] | 764:Klima[2].UnitOnAlarmC:=Bit_0;
mind_bool[765]:=Klima[3].NapacnoGesloAlarm; | [5 empty] | 765:Klima[3].NapacnoGesloAlarm:=Bit_0;
mind_bool[766]:=Klima[3].ExtTempHumAlarm; | [5 empty] | 766:Klima[3].ExtTempHumAlarm:=Bit_0;
mind_bool[767]:=Klima[3].PoplavniAlarm; | [5 empty] | 767:Klima[3].PoplavniAlarm:=Bit_0;
mind_bool[768]:=Klima[3].VisokPritiskKompresor1; | [5 empty] | 768:Klima[3].VisokPritiskKompresor1:=Bit_0;
mind_bool[769]:=Klima[3].VisokPritiskKompresor2; | [5 empty] | 769:Klima[3].VisokPritiskKompresor2:=Bit_0;
mind_bool[770]:=Klima[3].ElVentilKompresor1ERR; | [5 empty] | 770:Klima[3].ElVentilKompresor1ERR:=Bit_0;
mind_bool[771]:=Klima[3].ElVentilKompresor2ERR; | [5 empty] | 771:Klima[3].ElVentilKompresor2ERR:=Bit_0;
mind_bool[772]:=Klima[3].WrongPhaseSeqAlarm; | [5 empty] | 772:Klima[3].WrongPhaseSeqAlarm:=Bit_0;
mind_bool[773]:=Klima[3].PrekinjenLANalarm; | [5 empty] | 773:Klima[3].PrekinjenLANalarm:=Bit_0;
mind_bool[774]:=Klima[3].CWTempHighForDehum; | [5 empty] | 774:Klima[3].CWTempHighForDehum:=Bit_0;
mind_bool[775]:=Klima[3].CWVentilErrOrLowFlow; | [5 empty] | 775:Klima[3].CWVentilErrOrLowFlow:=Bit_0;
mind_bool[776]:=Klima[3].NapakaPriPretokuVode; | [5 empty] | 776:Klima[3].NapakaPriPretokuVode:=Bit_0;
mind_bool[777]:=Klima[3].CWhighTemp; | [5 empty] | 777:Klima[3].CWhighTemp:=Bit_0;
mind_bool[778]:=Klima[3].NapakaSenzorHotWTemp; | [5 empty] | 778:Klima[3].NapakaSenzorHotWTemp:=Bit_0;
mind_bool[779]:=Klima[3].NapakaSenzorCondWTemp; | [5 empty] | 779:Klima[3].NapakaSenzorCondWTemp:=Bit_0;
mind_bool[780]:=Klima[3].NapakaSenzorCW; | [5 empty] | 780:Klima[3].NapakaSenzorCW:=Bit_0;
mind_bool[781]:=Klima[3].Kompresor3naMejiObrUr; | [5 empty] | 781:Klima[3].Kompresor3naMejiObrUr:=Bit_0;
mind_bool[782]:=Klima[3].Kompresor4naMejiObrUr; | [5 empty] | 782:Klima[3].Kompresor4naMejiObrUr:=Bit_0;
mind_bool[783]:=Klima[3].ZracniFilterNaMejiObrUr; | [5 empty] | 783:Klima[3].ZracniFilterNaMejiObrUr:=Bit_0;
mind_bool[784]:=Klima[3].Grelec1naMejiObrUr; | [5 empty] | 784:Klima[3].Grelec1naMejiObrUr:=Bit_0;
mind_bool[785]:=Klima[3].Grelec2naMejiObrUr; | [5 empty] | 785:Klima[3].Grelec2naMejiObrUr:=Bit_0;
mind_bool[786]:=Klima[3].VlazilecNaMejiObrUr; | [5 empty] | 786:Klima[3].VlazilecNaMejiObrUr:=Bit_0;
mind_bool[787]:=Klima[3].AirCondUnitNaMejiObrUr; | [5 empty] | 787:Klima[3].AirCondUnitNaMejiObrUr:=Bit_0;
mind_bool[788]:=Klima[3].DigIn2Alarm; | [5 empty] | 788:Klima[3].DigIn2Alarm:=Bit_0;
mind_bool[789]:=Klima[3].DigIn4Alarm; | [5 empty] | 789:Klima[3].DigIn4Alarm:=Bit_0;
mind_bool[790]:=Klima[3].DigIn6Alarm; | [5 empty] | 790:Klima[3].DigIn6Alarm:=Bit_0;
mind_bool[791]:=Klima[3].VlazilecGenAlarm; | [5 empty] | 791:Klima[3].VlazilecGenAlarm:=Bit_0;
mind_bool[792]:=Klima[3].General2ndLevAlarm; | [5 empty] | 792:Klima[3].General2ndLevAlarm:=Bit_0;
mind_bool[793]:=Klima[3].UnitOnRotAlarm; | [5 empty] | 793:Klima[3].UnitOnRotAlarm:=Bit_0;
mind_bool[794]:=Klima[3].UnitOnAlarmA; | [5 empty] | 794:Klima[3].UnitOnAlarmA:=Bit_0;
mind_bool[795]:=Klima[3].UnitOnAlarmB; | [5 empty] | 795:Klima[3].UnitOnAlarmB:=Bit_0;
mind_bool[796]:=Klima[3].UnitOnAlarmC; | [5 empty] | 796:Klima[3].UnitOnAlarmC:=Bit_0;
mind_bool[797]:=Klima[4].NapacnoGesloAlarm; | [5 empty] | 797:Klima[4].NapacnoGesloAlarm:=Bit_0;
mind_bool[798]:=Klima[4].ExtTempHumAlarm; | [5 empty] | 798:Klima[4].ExtTempHumAlarm:=Bit_0;
mind_bool[799]:=Klima[4].PoplavniAlarm; | [5 empty] | 799:Klima[4].PoplavniAlarm:=Bit_0;
mind_bool[800]:=Klima[4].VisokPritiskKompresor1; | [5 empty] | 800:Klima[4].VisokPritiskKompresor1:=Bit_0;
mind_bool[801]:=Klima[4].VisokPritiskKompresor2; | [5 empty] | 801:Klima[4].VisokPritiskKompresor2:=Bit_0;
mind_bool[802]:=Klima[4].ElVentilKompresor1ERR; | [5 empty] | 802:Klima[4].ElVentilKompresor1ERR:=Bit_0;
mind_bool[803]:=Klima[4].ElVentilKompresor2ERR; | [5 empty] | 803:Klima[4].ElVentilKompresor2ERR:=Bit_0;
mind_bool[804]:=Klima[4].WrongPhaseSeqAlarm; | [5 empty] | 804:Klima[4].WrongPhaseSeqAlarm:=Bit_0;
mind_bool[805]:=Klima[4].PrekinjenLANalarm; | [5 empty] | 805:Klima[4].PrekinjenLANalarm:=Bit_0;
mind_bool[806]:=Klima[4].CWTempHighForDehum; | [5 empty] | 806:Klima[4].CWTempHighForDehum:=Bit_0;
mind_bool[807]:=Klima[4].CWVentilErrOrLowFlow; | [5 empty] | 807:Klima[4].CWVentilErrOrLowFlow:=Bit_0;
mind_bool[808]:=Klima[4].NapakaPriPretokuVode; | [5 empty] | 808:Klima[4].NapakaPriPretokuVode:=Bit_0;
mind_bool[809]:=Klima[4].CWhighTemp; | [5 empty] | 809:Klima[4].CWhighTemp:=Bit_0;
mind_bool[810]:=Klima[4].NapakaSenzorHotWTemp; | [5 empty] | 810:Klima[4].NapakaSenzorHotWTemp:=Bit_0;
mind_bool[811]:=Klima[4].NapakaSenzorCondWTemp; | [5 empty] | 811:Klima[4].NapakaSenzorCondWTemp:=Bit_0;
mind_bool[812]:=Klima[4].NapakaSenzorCW; | [5 empty] | 812:Klima[4].NapakaSenzorCW:=Bit_0;
mind_bool[813]:=Klima[4].Kompresor3naMejiObrUr; | [5 empty] | 813:Klima[4].Kompresor3naMejiObrUr:=Bit_0;
mind_bool[814]:=Klima[4].Kompresor4naMejiObrUr; | [5 empty] | 814:Klima[4].Kompresor4naMejiObrUr:=Bit_0;
mind_bool[815]:=Klima[4].ZracniFilterNaMejiObrUr; | [5 empty] | 815:Klima[4].ZracniFilterNaMejiObrUr:=Bit_0;
mind_bool[816]:=Klima[4].Grelec1naMejiObrUr; | [5 empty] | 816:Klima[4].Grelec1naMejiObrUr:=Bit_0;
mind_bool[817]:=Klima[4].Grelec2naMejiObrUr; | [5 empty] | 817:Klima[4].Grelec2naMejiObrUr:=Bit_0;
mind_bool[818]:=Klima[4].VlazilecNaMejiObrUr; | [5 empty] | 818:Klima[4].VlazilecNaMejiObrUr:=Bit_0;
mind_bool[819]:=Klima[4].AirCondUnitNaMejiObrUr; | [5 empty] | 819:Klima[4].AirCondUnitNaMejiObrUr:=Bit_0;
mind_bool[820]:=Klima[4].DigIn2Alarm; | [5 empty] | 820:Klima[4].DigIn2Alarm:=Bit_0;
mind_bool[821]:=Klima[4].DigIn4Alarm; | [5 empty] | 821:Klima[4].DigIn4Alarm:=Bit_0;
mind_bool[822]:=Klima[4].DigIn6Alarm; | [5 empty] | 822:Klima[4].DigIn6Alarm:=Bit_0;
mind_bool[823]:=Klima[4].VlazilecGenAlarm; | [5 empty] | 823:Klima[4].VlazilecGenAlarm:=Bit_0;
mind_bool[824]:=Klima[4].General2ndLevAlarm; | [5 empty] | 824:Klima[4].General2ndLevAlarm:=Bit_0;
mind_bool[825]:=Klima[4].UnitOnRotAlarm; | [5 empty] | 825:Klima[4].UnitOnRotAlarm:=Bit_0;
mind_bool[826]:=Klima[4].UnitOnAlarmA; | [5 empty] | 826:Klima[4].UnitOnAlarmA:=Bit_0;
mind_bool[827]:=Klima[4].UnitOnAlarmB; | [5 empty] | 827:Klima[4].UnitOnAlarmB:=Bit_0;
mind_bool[828]:=Klima[4].UnitOnAlarmC; | [5 empty] | 828:Klima[4].UnitOnAlarmC:=Bit_0;
mind_bool[829]:=Klima[5].NapacnoGesloAlarm; | [5 empty] | 829:Klima[5].NapacnoGesloAlarm:=Bit_0;
mind_bool[830]:=Klima[5].ExtTempHumAlarm; | [5 empty] | 830:Klima[5].ExtTempHumAlarm:=Bit_0;
mind_bool[831]:=Klima[5].PoplavniAlarm; | [5 empty] | 831:Klima[5].PoplavniAlarm:=Bit_0;
mind_bool[832]:=Klima[5].VisokPritiskKompresor1; | [5 empty] | 832:Klima[5].VisokPritiskKompresor1:=Bit_0;
mind_bool[833]:=Klima[5].VisokPritiskKompresor2; | [5 empty] | 833:Klima[5].VisokPritiskKompresor2:=Bit_0;
mind_bool[834]:=Klima[5].ElVentilKompresor1ERR; | [5 empty] | 834:Klima[5].ElVentilKompresor1ERR:=Bit_0;
mind_bool[835]:=Klima[5].ElVentilKompresor2ERR; | [5 empty] | 835:Klima[5].ElVentilKompresor2ERR:=Bit_0;
mind_bool[836]:=Klima[5].WrongPhaseSeqAlarm; | [5 empty] | 836:Klima[5].WrongPhaseSeqAlarm:=Bit_0;
mind_bool[837]:=Klima[5].PrekinjenLANalarm; | [5 empty] | 837:Klima[5].PrekinjenLANalarm:=Bit_0;
mind_bool[838]:=Klima[5].CWTempHighForDehum; | [5 empty] | 838:Klima[5].CWTempHighForDehum:=Bit_0;
mind_bool[839]:=Klima[5].CWVentilErrOrLowFlow; | [5 empty] | 839:Klima[5].CWVentilErrOrLowFlow:=Bit_0;
mind_bool[840]:=Klima[5].NapakaPriPretokuVode; | [5 empty] | 840:Klima[5].NapakaPriPretokuVode:=Bit_0;
mind_bool[841]:=Klima[5].CWhighTemp; | [5 empty] | 841:Klima[5].CWhighTemp:=Bit_0;
mind_bool[842]:=Klima[5].NapakaSenzorHotWTemp; | [5 empty] | 842:Klima[5].NapakaSenzorHotWTemp:=Bit_0;
mind_bool[843]:=Klima[5].NapakaSenzorCondWTemp; | [5 empty] | 843:Klima[5].NapakaSenzorCondWTemp:=Bit_0;
mind_bool[844]:=Klima[5].NapakaSenzorCW; | [5 empty] | 844:Klima[5].NapakaSenzorCW:=Bit_0;
mind_bool[845]:=Klima[5].Kompresor3naMejiObrUr; | [5 empty] | 845:Klima[5].Kompresor3naMejiObrUr:=Bit_0;
mind_bool[846]:=Klima[5].Kompresor4naMejiObrUr; | [5 empty] | 846:Klima[5].Kompresor4naMejiObrUr:=Bit_0;
mind_bool[847]:=Klima[5].ZracniFilterNaMejiObrUr; | [5 empty] | 847:Klima[5].ZracniFilterNaMejiObrUr:=Bit_0;
mind_bool[848]:=Klima[5].Grelec1naMejiObrUr; | [5 empty] | 848:Klima[5].Grelec1naMejiObrUr:=Bit_0;
mind_bool[849]:=Klima[5].Grelec2naMejiObrUr; | [5 empty] | 849:Klima[5].Grelec2naMejiObrUr:=Bit_0;
mind_bool[850]:=Klima[5].VlazilecNaMejiObrUr; | [5 empty] | 850:Klima[5].VlazilecNaMejiObrUr:=Bit_0;
mind_bool[851]:=Klima[5].AirCondUnitNaMejiObrUr; | [5 empty] | 851:Klima[5].AirCondUnitNaMejiObrUr:=Bit_0;
mind_bool[852]:=Klima[5].DigIn2Alarm; | [5 empty] | 852:Klima[5].DigIn2Alarm:=Bit_0;
mind_bool[853]:=Klima[5].DigIn4Alarm; | [5 empty] | 853:Klima[5].DigIn4Alarm:=Bit_0;
mind_bool[854]:=Klima[5].DigIn6Alarm; | [5 empty] | 854:Klima[5].DigIn6Alarm:=Bit_0;
mind_bool[855]:=Klima[5].VlazilecGenAlarm; | [5 empty] | 855:Klima[5].VlazilecGenAlarm:=Bit_0;
mind_bool[856]:=Klima[5].General2ndLevAlarm; | [5 empty] | 856:Klima[5].General2ndLevAlarm:=Bit_0;
mind_bool[857]:=Klima[5].UnitOnRotAlarm; | [5 empty] | 857:Klima[5].UnitOnRotAlarm:=Bit_0;
mind_bool[858]:=Klima[5].UnitOnAlarmA; | [5 empty] | 858:Klima[5].UnitOnAlarmA:=Bit_0;
mind_bool[859]:=Klima[5].UnitOnAlarmB; | [5 empty] | 859:Klima[5].UnitOnAlarmB:=Bit_0;
mind_bool[860]:=Klima[5].UnitOnAlarmC; | [5 empty] | 860:Klima[5].UnitOnAlarmC:=Bit_0;
mind_bool[861]:=Klima[6].NapacnoGesloAlarm; | [5 empty] | 861:Klima[6].NapacnoGesloAlarm:=Bit_0;
mind_bool[862]:=Klima[6].ExtTempHumAlarm; | [5 empty] | 862:Klima[6].ExtTempHumAlarm:=Bit_0;
mind_bool[863]:=Klima[6].PoplavniAlarm; | [5 empty] | 863:Klima[6].PoplavniAlarm:=Bit_0;
mind_bool[864]:=Klima[6].VisokPritiskKompresor1; | [5 empty] | 864:Klima[6].VisokPritiskKompresor1:=Bit_0;
mind_bool[865]:=Klima[6].VisokPritiskKompresor2; | [5 empty] | 865:Klima[6].VisokPritiskKompresor2:=Bit_0;
mind_bool[866]:=Klima[6].ElVentilKompresor1ERR; | [5 empty] | 866:Klima[6].ElVentilKompresor1ERR:=Bit_0;
mind_bool[867]:=Klima[6].ElVentilKompresor2ERR; | [5 empty] | 867:Klima[6].ElVentilKompresor2ERR:=Bit_0;
mind_bool[868]:=Klima[6].WrongPhaseSeqAlarm; | [5 empty] | 868:Klima[6].WrongPhaseSeqAlarm:=Bit_0;
mind_bool[869]:=Klima[6].PrekinjenLANalarm; | [5 empty] | 869:Klima[6].PrekinjenLANalarm:=Bit_0;
mind_bool[870]:=Klima[6].CWTempHighForDehum; | [5 empty] | 870:Klima[6].CWTempHighForDehum:=Bit_0;
mind_bool[871]:=Klima[6].CWVentilErrOrLowFlow; | [5 empty] | 871:Klima[6].CWVentilErrOrLowFlow:=Bit_0;
mind_bool[872]:=Klima[6].NapakaPriPretokuVode; | [5 empty] | 872:Klima[6].NapakaPriPretokuVode:=Bit_0;
mind_bool[873]:=Klima[6].CWhighTemp; | [5 empty] | 873:Klima[6].CWhighTemp:=Bit_0;
mind_bool[874]:=Klima[6].NapakaSenzorHotWTemp; | [5 empty] | 874:Klima[6].NapakaSenzorHotWTemp:=Bit_0;
mind_bool[875]:=Klima[6].NapakaSenzorCondWTemp; | [5 empty] | 875:Klima[6].NapakaSenzorCondWTemp:=Bit_0;
mind_bool[876]:=Klima[6].NapakaSenzorCW; | [5 empty] | 876:Klima[6].NapakaSenzorCW:=Bit_0;
mind_bool[877]:=Klima[6].Kompresor3naMejiObrUr; | [5 empty] | 877:Klima[6].Kompresor3naMejiObrUr:=Bit_0;
mind_bool[878]:=Klima[6].Kompresor4naMejiObrUr; | [5 empty] | 878:Klima[6].Kompresor4naMejiObrUr:=Bit_0;
mind_bool[879]:=Klima[6].ZracniFilterNaMejiObrUr; | [5 empty] | 879:Klima[6].ZracniFilterNaMejiObrUr:=Bit_0;
mind_bool[880]:=Klima[6].Grelec1naMejiObrUr; | [5 empty] | 880:Klima[6].Grelec1naMejiObrUr:=Bit_0;
mind_bool[881]:=Klima[6].Grelec2naMejiObrUr; | [5 empty] | 881:Klima[6].Grelec2naMejiObrUr:=Bit_0;
mind_bool[882]:=Klima[6].VlazilecNaMejiObrUr; | [5 empty] | 882:Klima[6].VlazilecNaMejiObrUr:=Bit_0;
mind_bool[883]:=Klima[6].AirCondUnitNaMejiObrUr; | [5 empty] | 883:Klima[6].AirCondUnitNaMejiObrUr:=Bit_0;
mind_bool[884]:=Klima[6].DigIn2Alarm; | [5 empty] | 884:Klima[6].DigIn2Alarm:=Bit_0;
mind_bool[885]:=Klima[6].DigIn4Alarm; | [5 empty] | 885:Klima[6].DigIn4Alarm:=Bit_0;
mind_bool[886]:=Klima[6].DigIn6Alarm; | [5 empty] | 886:Klima[6].DigIn6Alarm:=Bit_0;
mind_bool[887]:=Klima[6].VlazilecGenAlarm; | [5 empty] | 887:Klima[6].VlazilecGenAlarm:=Bit_0;
mind_bool[888]:=Klima[6].General2ndLevAlarm; | [5 empty] | 888:Klima[6].General2ndLevAlarm:=Bit_0;
mind_bool[889]:=Klima[6].UnitOnRotAlarm; | [5 empty] | 889:Klima[6].UnitOnRotAlarm:=Bit_0;
mind_bool[890]:=Klima[6].UnitOnAlarmA; | [5 empty] | 890:Klima[6].UnitOnAlarmA:=Bit_0;
mind_bool[891]:=Klima[6].UnitOnAlarmB; | [5 empty] | 891:Klima[6].UnitOnAlarmB:=Bit_0;
mind_bool[892]:=Klima[6].UnitOnAlarmC; | [5 empty] | 892:Klima[6].UnitOnAlarmC:=Bit_0;
mind_bool[893]:=Klima[1].Komp1On; | [5 empty] | 893:Klima[1].Komp1On:=Bit_0;
mind_bool[894]:=Klima[1].Komp2On; | [5 empty] | 894:Klima[1].Komp2On:=Bit_0;
mind_bool[895]:=Klima[1].Komp3On; | [5 empty] | 895:Klima[1].Komp3On:=Bit_0;
mind_bool[896]:=Klima[1].Komp4On; | [5 empty] | 896:Klima[1].Komp4On:=Bit_0;
mind_bool[897]:=Klima[2].Komp1On; | [5 empty] | 897:Klima[2].Komp1On:=Bit_0;
mind_bool[898]:=Klima[2].Komp2On; | [5 empty] | 898:Klima[2].Komp2On:=Bit_0;
mind_bool[899]:=Klima[2].Komp3On; | [5 empty] | 899:Klima[2].Komp3On:=Bit_0;
mind_bool[900]:=Klima[2].Komp4On; | [5 empty] | 900:Klima[2].Komp4On:=Bit_0;
mind_bool[901]:=Klima[3].Komp1On; | [5 empty] | 901:Klima[3].Komp1On:=Bit_0;
mind_bool[902]:=Klima[3].Komp2On; | [5 empty] | 902:Klima[3].Komp2On:=Bit_0;
mind_bool[903]:=Klima[3].Komp3On; | [5 empty] | 903:Klima[3].Komp3On:=Bit_0;
mind_bool[904]:=Klima[3].Komp4On; | [5 empty] | 904:Klima[3].Komp4On:=Bit_0;
mind_bool[905]:=Klima[4].Komp1On; | [5 empty] | 905:Klima[4].Komp1On:=Bit_0;
mind_bool[906]:=Klima[4].Komp2On; | [5 empty] | 906:Klima[4].Komp2On:=Bit_0;
mind_bool[907]:=Klima[4].Komp3On; | [5 empty] | 907:Klima[4].Komp3On:=Bit_0;
mind_bool[908]:=Klima[4].Komp4On; | [5 empty] | 908:Klima[4].Komp4On:=Bit_0;
mind_bool[909]:=Klima[5].Komp1On; | [5 empty] | 909:Klima[5].Komp1On:=Bit_0;
mind_bool[910]:=Klima[5].Komp2On; | [5 empty] | 910:Klima[5].Komp2On:=Bit_0;
mind_bool[911]:=Klima[5].Komp3On; | [5 empty] | 911:Klima[5].Komp3On:=Bit_0;
mind_bool[912]:=Klima[5].Komp4On; | [5 empty] | 912:Klima[5].Komp4On:=Bit_0;
mind_bool[913]:=Klima[6].Komp1On; | [5 empty] | 913:Klima[6].Komp1On:=Bit_0;
mind_bool[914]:=Klima[6].Komp2On; | [5 empty] | 914:Klima[6].Komp2On:=Bit_0;
mind_bool[915]:=Klima[6].Komp3On; | [5 empty] | 915:Klima[6].Komp3On:=Bit_0;
mind_bool[916]:=Klima[6].Komp4On; | [5 empty] | 916:Klima[6].Komp4On:=Bit_0;
mind_bool[917]:=Klima[1].GretjeStopnja1; | [5 empty] | 917:Klima[1].GretjeStopnja1:=Bit_0;
mind_bool[918]:=Klima[1].GretjeStopnja2; | [5 empty] | 918:Klima[1].GretjeStopnja2:=Bit_0;
mind_bool[919]:=Klima[1].GretjeStopnja3; | [5 empty] | 919:Klima[1].GretjeStopnja3:=Bit_0;
mind_bool[920]:=Klima[2].GretjeStopnja1; | [5 empty] | 920:Klima[2].GretjeStopnja1:=Bit_0;
mind_bool[921]:=Klima[2].GretjeStopnja2; | [5 empty] | 921:Klima[2].GretjeStopnja2:=Bit_0;
mind_bool[922]:=Klima[2].GretjeStopnja3; | [5 empty] | 922:Klima[2].GretjeStopnja3:=Bit_0;
mind_bool[923]:=Klima[3].GretjeStopnja1; | [5 empty] | 923:Klima[3].GretjeStopnja1:=Bit_0;
mind_bool[924]:=Klima[3].GretjeStopnja2; | [5 empty] | 924:Klima[3].GretjeStopnja2:=Bit_0;
mind_bool[925]:=Klima[3].GretjeStopnja3; | [5 empty] | 925:Klima[3].GretjeStopnja3:=Bit_0;
mind_bool[926]:=Klima[4].GretjeStopnja1; | [5 empty] | 926:Klima[4].GretjeStopnja1:=Bit_0;
mind_bool[927]:=Klima[4].GretjeStopnja2; | [5 empty] | 927:Klima[4].GretjeStopnja2:=Bit_0;
mind_bool[928]:=Klima[4].GretjeStopnja3; | [5 empty] | 928:Klima[4].GretjeStopnja3:=Bit_0;
mind_bool[929]:=Klima[5].GretjeStopnja1; | [5 empty] | 929:Klima[5].GretjeStopnja1:=Bit_0;
mind_bool[930]:=Klima[5].GretjeStopnja2; | [5 empty] | 930:Klima[5].GretjeStopnja2:=Bit_0;
mind_bool[931]:=Klima[5].GretjeStopnja3; | [5 empty] | 931:Klima[5].GretjeStopnja3:=Bit_0;
mind_bool[932]:=Klima[6].GretjeStopnja1; | [5 empty] | 932:Klima[6].GretjeStopnja1:=Bit_0;
mind_bool[933]:=Klima[6].GretjeStopnja2; | [5 empty] | 933:Klima[6].GretjeStopnja2:=Bit_0;
mind_bool[934]:=Klima[6].GretjeStopnja3; | [5 empty] | 934:Klima[6].GretjeStopnja3:=Bit_0;
mind_bool[935]:=Klima[1].HotGasOn; | [5 empty] | 935:Klima[1].HotGasOn:=Bit_0;
mind_bool[936]:=Klima[2].HotGasOn; | [5 empty] | 936:Klima[2].HotGasOn:=Bit_0;
mind_bool[937]:=Klima[3].HotGasOn; | [5 empty] | 937:Klima[3].HotGasOn:=Bit_0;
mind_bool[938]:=Klima[4].HotGasOn; | [5 empty] | 938:Klima[4].HotGasOn:=Bit_0;
mind_bool[939]:=Klima[5].HotGasOn; | [5 empty] | 939:Klima[5].HotGasOn:=Bit_0;
mind_bool[940]:=Klima[6].HotGasOn; | [5 empty] | 940:Klima[6].HotGasOn:=Bit_0;
mind_bool[941]:=Klima[1].EmergencyWorking; | [5 empty] | 941:Klima[1].EmergencyWorking:=Bit_0;
mind_bool[942]:=Klima[2].EmergencyWorking; | [5 empty] | 942:Klima[2].EmergencyWorking:=Bit_0;
mind_bool[943]:=Klima[3].EmergencyWorking; | [5 empty] | 943:Klima[3].EmergencyWorking:=Bit_0;
mind_bool[944]:=Klima[4].EmergencyWorking; | [5 empty] | 944:Klima[4].EmergencyWorking:=Bit_0;
mind_bool[945]:=Klima[5].EmergencyWorking; | [5 empty] | 945:Klima[5].EmergencyWorking:=Bit_0;
mind_bool[946]:=Klima[6].EmergencyWorking; | [5 empty] | 946:Klima[6].EmergencyWorking:=Bit_0;
mind_bool[947]:=DI_A1Q01_DovUpsB_ON; | [5 empty] | 947:DI_A1Q01_DovUpsB_ON:=Bit_0;
mind_bool[948]:=DI_A1Q0_GlavnoStiB_ON; | [5 empty] | 948:DI_A1Q0_GlavnoStiB_ON:=Bit_0;
mind_bool[949]:=DI_A1Q11_OdcUpsB_IZP; | [5 empty] | 949:DI_A1Q11_OdcUpsB_IZP:=Bit_0;
mind_bool[950]:=DI_A1Q11_OdcUpsB_ON; | [5 empty] | 950:DI_A1Q11_OdcUpsB_ON:=Bit_0;
mind_bool[951]:=DI_A1Q12_OdcByUpsB_IZP; | [5 empty] | 951:DI_A1Q12_OdcByUpsB_IZP:=Bit_0;
mind_bool[952]:=DI_A1Q12_OdcByUpsB_ON; | [5 empty] | 952:DI_A1Q12_OdcByUpsB_ON:=Bit_0;
mind_bool[953]:=DI_A1Q13_OdcByB_IZP; | [5 empty] | 953:DI_A1Q13_OdcByB_IZP:=Bit_0;
mind_bool[954]:=ErrCommScada2; | [5 empty] | 954:ErrCommScada2:=Bit_0;
mind_bool[955]:=ComSCADA2; | [5 empty] | 955:ComSCADA2:=Bit_0;
mind_bool[956]:=ComSCADA3; | [5 empty] | 956:ComSCADA3:=Bit_0;

## XSoft_EXP
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
PROGRAM mod_Read
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*Branje BOOL*)
(**)
mind_bool[0]:=AlarmGenComm;
mind_bool[1]:=AlarmGenKlima[1];
mind_bool[2]:=AlarmGenKlima[2];
mind_bool[3]:=AlarmGenKlima[3];
mind_bool[4]:=AlarmGenKlima[4];
mind_bool[5]:=AlarmGenKlima[5];
mind_bool[6]:=AlarmGenKlima[6];
mind_bool[7]:=AlarmGenPMM;
mind_bool[8]:=AlarmGenRest;
mind_bool[9]:=AlarmGenSenzor;
mind_bool[10]:=AlarmGenStikala;
mind_bool[11]:=AlarmGenTemp;
mind_bool[12]:=AlarmGenUPS1;
mind_bool[13]:=AlarmGenUPS2;
mind_bool[14]:=ComSCADA;
mind_bool[15]:=ComSCADA1;
mind_bool[16]:=DI_A1Q01_DovUpsA_ON;
mind_bool[17]:=DI_A1Q02_DovByA_ON;
mind_bool[18]:=DI_A1Q0_GlavnoSti_ON;
mind_bool[19]:=DI_A1Q11_OdcUpsA_IZP;
mind_bool[20]:=DI_A1Q11_OdcUpsA_ON;
mind_bool[21]:=DI_A1Q12_OdcByUpsA_IZP;
mind_bool[22]:=DI_A1Q12_OdcByUpsA_ON;
mind_bool[23]:=DI_A1Q13_OdcByA_IZP;
mind_bool[24]:=DI_A1Q13_OdcByA_ON;
mind_bool[25]:=DI_A2Q0_GlavnoSti_ON;
mind_bool[26]:=DI_F201_OdcKl1ZE_IZP;
mind_bool[27]:=DI_F201_OdcKl1ZE_ON;
mind_bool[28]:=DI_F202_OdcKl2ZE_IZP;
mind_bool[29]:=DI_F202_OdcKl2ZE_ON;
mind_bool[30]:=DI_F203_OdcKl3ZE_IZP;
mind_bool[31]:=DI_F203_OdcKl3ZE_ON;
mind_bool[32]:=DI_F204_OdcKl4ZE_IZP;
mind_bool[33]:=DI_F204_OdcKl4ZE_ON;
mind_bool[34]:=DI_F205_OdcKl5aZE_IZP;
mind_bool[35]:=DI_F205_OdcKl5aZE_ON;
mind_bool[36]:=DI_F206_OdcKl5bZE_IZP;
mind_bool[37]:=DI_F206_OdcKl5bZE_ON;
mind_bool[38]:=DI_F207_OdcKl6aZE_IZP;
mind_bool[39]:=DI_F207_OdcKl6aZE_ON;
mind_bool[40]:=DI_F208_OdcKl6bZE_IZP;
mind_bool[41]:=DI_F208_OdcKl6bZE_ON;
mind_bool[42]:=DI_IzpadMreze;
mind_bool[43]:=DI_Klima1_ERR;
mind_bool[44]:=DI_Klima1_ON;
mind_bool[45]:=DI_Klima2_ERR;
mind_bool[46]:=DI_Klima2_ON;
mind_bool[47]:=DI_Klima3_ERR;
mind_bool[48]:=DI_Klima3_ON;
mind_bool[49]:=DI_Klima4_ERR;
mind_bool[50]:=DI_Klima4_ON;
mind_bool[51]:=DI_Klima5_ERR;
mind_bool[52]:=DI_Klima5_ON;
mind_bool[53]:=DI_Klima6_ERR;
mind_bool[54]:=DI_Klima6_ON;
mind_bool[55]:=DI_KlimaSplitPP_ERR;
mind_bool[56]:=DI_KlimaSplitPP_ON;
mind_bool[57]:=DI_PrenapA1_OK;
mind_bool[58]:=DI_PrenapA2_OK;
mind_bool[59]:=DI_Q101_OdcKlima1_IZP;
mind_bool[60]:=DI_Q101_OdcKlima1_ON;
mind_bool[61]:=DI_Q102_OdcKlima2_IZP;
mind_bool[62]:=DI_Q102_OdcKlima2_ON;
mind_bool[63]:=DI_Q103_OdcKlima3_IZP;
mind_bool[64]:=DI_Q103_OdcKlima3_ON;
mind_bool[65]:=DI_Q104_OdcKlima4_IZP;
mind_bool[66]:=DI_Q104_OdcKlima4_ON;
mind_bool[67]:=DI_Q105_OdcKlima5_IZP;
mind_bool[68]:=DI_Q105_OdcKlima5_ON;
mind_bool[69]:=DI_Q106_OdcKlima6_IZP;
mind_bool[70]:=DI_Q106_OdcKlima6_ON;
mind_bool[71]:=DI_Q107_OdcUsmSS2_IZP;
mind_bool[72]:=DI_Q107_OdcUsmSS2_ON;
mind_bool[73]:=DI_Q108_OdcUsmSS3_IZP;
mind_bool[74]:=DI_Q108_OdcUsmSS3_ON;
mind_bool[75]:=DI_RazlitjeVodeK1K2;
mind_bool[76]:=DI_RazlitjeVodeK3K4;
mind_bool[77]:=DI_RazlitjeVodeK5;
mind_bool[78]:=DI_RazlitjeVodeK6;
mind_bool[79]:=DI_UPS_Alarm;
mind_bool[80]:=DI_UPS_BatNacin;
mind_bool[81]:=DI_UPS_Polnjenje;
mind_bool[82]:=DI_UpsA_BypassON;
mind_bool[83]:=DI_UpsA_ERR;
mind_bool[84]:=DI_UpsB_BypassON;
mind_bool[85]:=DI_UpsB_ERR;
mind_bool[86]:=DI_UQ11_OdcPMM_IZP;
mind_bool[87]:=DI_UQ11_OdcPMM_ON;
mind_bool[88]:=DI_UQ12_OdcPMM_IZP;
mind_bool[89]:=DI_UQ12_OdcPMM_ON;
mind_bool[90]:=DIN_A1Q11_OdcUpsA_IZP;
mind_bool[91]:=DIN_A1Q12_OdcByUpsA_IZP;
mind_bool[92]:=DIN_A1Q13_OdcByA_IZP;
mind_bool[93]:=DIN_F201_OdcKl1ZE_IZP;
mind_bool[94]:=DIN_F202_OdcKl2ZE_IZP;
mind_bool[95]:=DIN_F203_OdcKl3ZE_IZP;
mind_bool[96]:=DIN_F204_OdcKl4ZE_IZP;
mind_bool[97]:=DIN_F205_OdcKl5aZE_IZP;
mind_bool[98]:=DIN_F206_OdcKl5bZE_IZP;
mind_bool[99]:=DIN_F207_OdcKl6aZE_IZP;
mind_bool[100]:=DIN_F208_OdcKl6bZE_IZP;
mind_bool[101]:=DIN_Klima1_ERR;
mind_bool[102]:=DIN_Klima2_ERR;
mind_bool[103]:=DIN_Klima3_ERR;
mind_bool[104]:=DIN_Klima4_ERR;
mind_bool[105]:=DIN_Klima5_ERR;
mind_bool[106]:=DIN_Klima6_ERR;
mind_bool[107]:=DIN_KlimaSplitPP_ERR;
mind_bool[108]:=DIN_PrenapA1_OK;
mind_bool[109]:=DIN_PrenapA2_OK;
mind_bool[110]:=DIN_Q101_OdcKlima1_IZP;
mind_bool[111]:=DIN_Q102_OdcKlima2_IZP;
mind_bool[112]:=DIN_Q103_OdcKlima3_IZP;
mind_bool[113]:=DIN_Q104_OdcKlima4_IZP;
mind_bool[114]:=DIN_Q105_OdcKlima5_IZP;
mind_bool[115]:=DIN_Q106_OdcKlima6_IZP;
mind_bool[116]:=DIN_Q107_OdcUsmSS2_IZP;
mind_bool[117]:=DIN_Q108_OdcUsmSS3_IZP;
mind_bool[118]:=DIN_UpsA_BypassON;
mind_bool[119]:=DIN_UpsA_ERR;
mind_bool[120]:=DIN_UpsB_BypassON;
mind_bool[121]:=DIN_UpsB_ERR;
mind_bool[122]:=DIN_UQ11_OdcPMM_IZP;
mind_bool[123]:=DIN_UQ12_OdcPMM_IZP;
mind_bool[124]:=DO_Klima1_Izklop;
mind_bool[125]:=DO_Klima2_Izklop;
mind_bool[126]:=DO_Klima3_Izklop;
mind_bool[127]:=DO_Klima4_Izklop;
mind_bool[128]:=DO_Klima5_Izklop;
mind_bool[129]:=DO_Klima6_Izklop;
mind_bool[130]:=ErrComKlima[1];
mind_bool[131]:=ErrComKlima[2];
mind_bool[132]:=ErrComKlima[3];
mind_bool[133]:=ErrComKlima[4];
mind_bool[134]:=ErrComKlima[5];
mind_bool[135]:=ErrComKlima[6];
mind_bool[136]:=ErrCommScada;
mind_bool[137]:=ErrComPanelPLC;
mind_bool[138]:=ErrComPMM;
mind_bool[139]:=ErrComPort2;
mind_bool[140]:=ErrComPort3;
mind_bool[141]:=ErrComPort4;
mind_bool[142]:=ErrComUPS[1];
mind_bool[143]:=ErrComUPS[2];
mind_bool[144]:=ErrorComKlima[1].Error;
mind_bool[145]:=ErrorComKlima[2].Error;
mind_bool[146]:=ErrorComKlima[3].Error;
mind_bool[147]:=ErrorComKlima[4].Error;
mind_bool[148]:=ErrorComKlima[5].Error;
mind_bool[149]:=ErrorComKlima[6].Error;
mind_bool[150]:=ErrorComPMM.Error;
mind_bool[151]:=ErrorComUPS[1].Error;
mind_bool[152]:=ErrorComUPS[2].Error;
mind_bool[153]:=Klima1Errors[10];
mind_bool[154]:=Klima1Errors[11];
mind_bool[155]:=Klima1Errors[12];
mind_bool[156]:=Klima1Errors[13];
mind_bool[157]:=Klima1Errors[14];
mind_bool[158]:=Klima1Errors[15];
mind_bool[159]:=Klima1Errors[16];
mind_bool[160]:=Klima1Errors[17];
mind_bool[161]:=Klima1Errors[18];
mind_bool[162]:=Klima1Errors[19];
mind_bool[163]:=Klima1Errors[1];
mind_bool[164]:=Klima1Errors[20];
mind_bool[165]:=Klima1Errors[21];
mind_bool[166]:=Klima1Errors[22];
mind_bool[167]:=Klima1Errors[23];
mind_bool[168]:=Klima1Errors[24];
mind_bool[169]:=Klima1Errors[25];
mind_bool[170]:=Klima1Errors[26];
mind_bool[171]:=Klima1Errors[27];
mind_bool[172]:=Klima1Errors[28];
mind_bool[173]:=Klima1Errors[29];
mind_bool[174]:=Klima1Errors[2];
mind_bool[175]:=Klima1Errors[30];
mind_bool[176]:=Klima1Errors[31];
mind_bool[177]:=Klima1Errors[32];
mind_bool[178]:=Klima1Errors[33];
mind_bool[179]:=Klima1Errors[34];
mind_bool[180]:=Klima1Errors[35];
mind_bool[181]:=Klima1Errors[3];
mind_bool[182]:=Klima1Errors[4];
mind_bool[183]:=Klima1Errors[5];
mind_bool[184]:=Klima1Errors[6];
mind_bool[185]:=Klima1Errors[7];
mind_bool[186]:=Klima1Errors[8];
mind_bool[187]:=Klima1Errors[9];
mind_bool[188]:=Klima2Errors[10];
mind_bool[189]:=Klima2Errors[11];
mind_bool[190]:=Klima2Errors[12];
mind_bool[191]:=Klima2Errors[13];
mind_bool[192]:=Klima2Errors[14];
mind_bool[193]:=Klima2Errors[15];
mind_bool[194]:=Klima2Errors[16];
mind_bool[195]:=Klima2Errors[17];
mind_bool[196]:=Klima2Errors[18];
mind_bool[197]:=Klima2Errors[19];
mind_bool[198]:=Klima2Errors[1];
mind_bool[199]:=Klima2Errors[20];
mind_bool[200]:=Klima2Errors[21];
mind_bool[201]:=Klima2Errors[22];
mind_bool[202]:=Klima2Errors[23];
mind_bool[203]:=Klima2Errors[24];
mind_bool[204]:=Klima2Errors[25];
mind_bool[205]:=Klima2Errors[26];
mind_bool[206]:=Klima2Errors[27];
mind_bool[207]:=Klima2Errors[28];
mind_bool[208]:=Klima2Errors[29];
mind_bool[209]:=Klima2Errors[2];
mind_bool[210]:=Klima2Errors[30];
mind_bool[211]:=Klima2Errors[31];
mind_bool[212]:=Klima2Errors[32];
mind_bool[213]:=Klima2Errors[33];
mind_bool[214]:=Klima2Errors[34];
mind_bool[215]:=Klima2Errors[35];
mind_bool[216]:=Klima2Errors[3];
mind_bool[217]:=Klima2Errors[4];
mind_bool[218]:=Klima2Errors[5];
mind_bool[219]:=Klima2Errors[6];
mind_bool[220]:=Klima2Errors[7];
mind_bool[221]:=Klima2Errors[8];
mind_bool[222]:=Klima2Errors[9];
mind_bool[223]:=Klima3Errors[10];
mind_bool[224]:=Klima3Errors[11];
mind_bool[225]:=Klima3Errors[12];
mind_bool[226]:=Klima3Errors[13];
mind_bool[227]:=Klima3Errors[14];
mind_bool[228]:=Klima3Errors[15];
mind_bool[229]:=Klima3Errors[16];
mind_bool[230]:=Klima3Errors[17];
mind_bool[231]:=Klima3Errors[18];
mind_bool[232]:=Klima3Errors[19];
mind_bool[233]:=Klima3Errors[1];
mind_bool[234]:=Klima3Errors[20];
mind_bool[235]:=Klima3Errors[21];
mind_bool[236]:=Klima3Errors[22];
mind_bool[237]:=Klima3Errors[23];
mind_bool[238]:=Klima3Errors[24];
mind_bool[239]:=Klima3Errors[25];
mind_bool[240]:=Klima3Errors[26];
mind_bool[241]:=Klima3Errors[27];
mind_bool[242]:=Klima3Errors[28];
mind_bool[243]:=Klima3Errors[29];
mind_bool[244]:=Klima3Errors[2];
mind_bool[245]:=Klima3Errors[30];
mind_bool[246]:=Klima3Errors[31];
mind_bool[247]:=Klima3Errors[32];
mind_bool[248]:=Klima3Errors[33];
mind_bool[249]:=Klima3Errors[34];
mind_bool[250]:=Klima3Errors[35];
mind_bool[251]:=Klima3Errors[3];
mind_bool[252]:=Klima3Errors[4];
mind_bool[253]:=Klima3Errors[5];
mind_bool[254]:=Klima3Errors[6];
mind_bool[255]:=Klima3Errors[7];
mind_bool[256]:=Klima3Errors[8];
mind_bool[257]:=Klima3Errors[9];
mind_bool[258]:=Klima4Errors[10];
mind_bool[259]:=Klima4Errors[11];
mind_bool[260]:=Klima4Errors[12];
mind_bool[261]:=Klima4Errors[13];
mind_bool[262]:=Klima4Errors[14];
mind_bool[263]:=Klima4Errors[15];
mind_bool[264]:=Klima4Errors[16];
mind_bool[265]:=Klima4Errors[17];
mind_bool[266]:=Klima4Errors[18];
mind_bool[267]:=Klima4Errors[19];
mind_bool[268]:=Klima4Errors[1];
mind_bool[269]:=Klima4Errors[20];
mind_bool[270]:=Klima4Errors[21];
mind_bool[271]:=Klima4Errors[22];
mind_bool[272]:=Klima4Errors[23];
mind_bool[273]:=Klima4Errors[24];
mind_bool[274]:=Klima4Errors[25];
mind_bool[275]:=Klima4Errors[26];
mind_bool[276]:=Klima4Errors[27];
mind_bool[277]:=Klima4Errors[28];
mind_bool[278]:=Klima4Errors[29];
mind_bool[279]:=Klima4Errors[2];
mind_bool[280]:=Klima4Errors[30];
mind_bool[281]:=Klima4Errors[31];
mind_bool[282]:=Klima4Errors[32];
mind_bool[283]:=Klima4Errors[33];
mind_bool[284]:=Klima4Errors[34];
mind_bool[285]:=Klima4Errors[35];
mind_bool[286]:=Klima4Errors[3];
mind_bool[287]:=Klima4Errors[4];
mind_bool[288]:=Klima4Errors[5];
mind_bool[289]:=Klima4Errors[6];
mind_bool[290]:=Klima4Errors[7];
mind_bool[291]:=Klima4Errors[8];
mind_bool[292]:=Klima4Errors[9];
mind_bool[293]:=Klima5Errors[10];
mind_bool[294]:=Klima5Errors[11];
mind_bool[295]:=Klima5Errors[12];
mind_bool[296]:=Klima5Errors[13];
mind_bool[297]:=Klima5Errors[14];
mind_bool[298]:=Klima5Errors[15];
mind_bool[299]:=Klima5Errors[16];
mind_bool[300]:=Klima5Errors[17];
mind_bool[301]:=Klima5Errors[18];
mind_bool[302]:=Klima5Errors[19];
mind_bool[303]:=Klima5Errors[1];
mind_bool[304]:=Klima5Errors[20];
mind_bool[305]:=Klima5Errors[21];
mind_bool[306]:=Klima5Errors[22];
mind_bool[307]:=Klima5Errors[23];
mind_bool[308]:=Klima5Errors[24];
mind_bool[309]:=Klima5Errors[25];
mind_bool[310]:=Klima5Errors[26];
mind_bool[311]:=Klima5Errors[27];
mind_bool[312]:=Klima5Errors[28];
mind_bool[313]:=Klima5Errors[29];
mind_bool[314]:=Klima5Errors[2];
mind_bool[315]:=Klima5Errors[30];
mind_bool[316]:=Klima5Errors[31];
mind_bool[317]:=Klima5Errors[32];
mind_bool[318]:=Klima5Errors[33];
mind_bool[319]:=Klima5Errors[34];
mind_bool[320]:=Klima5Errors[35];
mind_bool[321]:=Klima5Errors[3];
mind_bool[322]:=Klima5Errors[4];
mind_bool[323]:=Klima5Errors[5];
mind_bool[324]:=Klima5Errors[6];
mind_bool[325]:=Klima5Errors[7];
mind_bool[326]:=Klima5Errors[8];
mind_bool[327]:=Klima5Errors[9];
mind_bool[328]:=Klima6Errors[10];
mind_bool[329]:=Klima6Errors[11];
mind_bool[330]:=Klima6Errors[12];
mind_bool[331]:=Klima6Errors[13];
mind_bool[332]:=Klima6Errors[14];
mind_bool[333]:=Klima6Errors[15];
mind_bool[334]:=Klima6Errors[16];
mind_bool[335]:=Klima6Errors[17];
mind_bool[336]:=Klima6Errors[18];
mind_bool[337]:=Klima6Errors[19];
mind_bool[338]:=Klima6Errors[1];
mind_bool[339]:=Klima6Errors[20];
mind_bool[340]:=Klima6Errors[21];
mind_bool[341]:=Klima6Errors[22];
mind_bool[342]:=Klima6Errors[23];
mind_bool[343]:=Klima6Errors[24];
mind_bool[344]:=Klima6Errors[25];
mind_bool[345]:=Klima6Errors[26];
mind_bool[346]:=Klima6Errors[27];
mind_bool[347]:=Klima6Errors[28];
mind_bool[348]:=Klima6Errors[29];
mind_bool[349]:=Klima6Errors[2];
mind_bool[350]:=Klima6Errors[30];
mind_bool[351]:=Klima6Errors[31];
mind_bool[352]:=Klima6Errors[32];
mind_bool[353]:=Klima6Errors[33];
mind_bool[354]:=Klima6Errors[34];
mind_bool[355]:=Klima6Errors[35];
mind_bool[356]:=Klima6Errors[3];
mind_bool[357]:=Klima6Errors[4];
mind_bool[358]:=Klima6Errors[5];
mind_bool[359]:=Klima6Errors[6];
mind_bool[360]:=Klima6Errors[7];
mind_bool[361]:=Klima6Errors[8];
mind_bool[362]:=Klima6Errors[9];
mind_bool[363]:=Klima[1].Deluje;
mind_bool[364]:=Klima[1].FenThermalCutout;
mind_bool[365]:=Klima[1].GeneralAlarm;
mind_bool[366]:=Klima[1].Kompresor1naMejiObrUr;
mind_bool[367]:=Klima[1].Kompresor2naMejiObrUr;
mind_bool[368]:=Klima[1].Napaka;
mind_bool[369]:=Klima[1].NapakaPriPretokuZraka;
mind_bool[370]:=Klima[1].NapakaSenzorTempIzpiha;
mind_bool[371]:=Klima[1].NapakaSenzorTempProstora;
mind_bool[372]:=Klima[1].NapakaSenzorVlaznosti;
mind_bool[373]:=Klima[1].NapakaSenzorZunanjeTemp;
mind_bool[374]:=Klima[1].NiTokaVVlazilcu;
mind_bool[375]:=Klima[1].NiVodeVVlazilcu;
mind_bool[376]:=Klima[1].NizekPritiskKompresor1;
mind_bool[377]:=Klima[1].NizekPritiskKompresor2;
mind_bool[378]:=Klima[1].NizkaTempVProstoru;
mind_bool[379]:=Klima[1].NizkaVlaznost;
mind_bool[380]:=Klima[1].OnOffEnablingBySupervisor;
mind_bool[381]:=Klima[1].PozarniAlarm;
mind_bool[382]:=Klima[1].Razvlazevanje;
mind_bool[383]:=Klima[1].RemoteOFFtoOutput;
mind_bool[384]:=Klima[1].RocniIzklop;
mind_bool[385]:=Klima[1].SenzorjiStatus;
mind_bool[386]:=Klima[1].UnitOnOff;
mind_bool[387]:=Klima[1].VisokaTempVProstoru;
mind_bool[388]:=Klima[1].VisokaVlaznost;
mind_bool[389]:=Klima[1].VisokTokVVlazilcu;
mind_bool[390]:=Klima[1].Vlazenje;
mind_bool[391]:=Klima[1].ZamasenFilter;
mind_bool[392]:=Klima[2].Deluje;
mind_bool[393]:=Klima[2].FenThermalCutout;
mind_bool[394]:=Klima[2].GeneralAlarm;
mind_bool[395]:=Klima[2].Kompresor1naMejiObrUr;
mind_bool[396]:=Klima[2].Kompresor2naMejiObrUr;
mind_bool[397]:=Klima[2].Napaka;
mind_bool[398]:=Klima[2].NapakaPriPretokuZraka;
mind_bool[399]:=Klima[2].NapakaSenzorTempIzpiha;
mind_bool[400]:=Klima[2].NapakaSenzorTempProstora;
mind_bool[401]:=Klima[2].NapakaSenzorVlaznosti;
mind_bool[402]:=Klima[2].NapakaSenzorZunanjeTemp;
mind_bool[403]:=Klima[2].NiTokaVVlazilcu;
mind_bool[404]:=Klima[2].NiVodeVVlazilcu;
mind_bool[405]:=Klima[2].NizekPritiskKompresor1;
mind_bool[406]:=Klima[2].NizekPritiskKompresor2;
mind_bool[407]:=Klima[2].NizkaTempVProstoru;
mind_bool[408]:=Klima[2].NizkaVlaznost;
mind_bool[409]:=Klima[2].OnOffEnablingBySupervisor;
mind_bool[410]:=Klima[2].PozarniAlarm;
mind_bool[411]:=Klima[2].Razvlazevanje;
mind_bool[412]:=Klima[2].RemoteOFFtoOutput;
mind_bool[413]:=Klima[2].RocniIzklop;
mind_bool[414]:=Klima[2].SenzorjiStatus;
mind_bool[415]:=Klima[2].UnitOnOff;
mind_bool[416]:=Klima[2].VisokaTempVProstoru;
mind_bool[417]:=Klima[2].VisokaVlaznost;
mind_bool[418]:=Klima[2].VisokTokVVlazilcu;
mind_bool[419]:=Klima[2].Vlazenje;
mind_bool[420]:=Klima[2].ZamasenFilter;
mind_bool[421]:=Klima[3].Deluje;
mind_bool[422]:=Klima[3].FenThermalCutout;
mind_bool[423]:=Klima[3].GeneralAlarm;
mind_bool[424]:=Klima[3].Kompresor1naMejiObrUr;
mind_bool[425]:=Klima[3].Kompresor2naMejiObrUr;
mind_bool[426]:=Klima[3].Napaka;
mind_bool[427]:=Klima[3].NapakaPriPretokuZraka;
mind_bool[428]:=Klima[3].NapakaSenzorTempIzpiha;
mind_bool[429]:=Klima[3].NapakaSenzorTempProstora;
mind_bool[430]:=Klima[3].NapakaSenzorVlaznosti;
mind_bool[431]:=Klima[3].NapakaSenzorZunanjeTemp;
mind_bool[432]:=Klima[3].NiTokaVVlazilcu;
mind_bool[433]:=Klima[3].NiVodeVVlazilcu;
mind_bool[434]:=Klima[3].NizekPritiskKompresor1;
mind_bool[435]:=Klima[3].NizekPritiskKompresor2;
mind_bool[436]:=Klima[3].NizkaTempVProstoru;
mind_bool[437]:=Klima[3].NizkaVlaznost;
mind_bool[438]:=Klima[3].OnOffEnablingBySupervisor;
mind_bool[439]:=Klima[3].PozarniAlarm;
mind_bool[440]:=Klima[3].Razvlazevanje;
mind_bool[441]:=Klima[3].RemoteOFFtoOutput;
mind_bool[442]:=Klima[3].RocniIzklop;
mind_bool[443]:=Klima[3].SenzorjiStatus;
mind_bool[444]:=Klima[3].UnitOnOff;
mind_bool[445]:=Klima[3].VisokaTempVProstoru;
mind_bool[446]:=Klima[3].VisokaVlaznost;
mind_bool[447]:=Klima[3].VisokTokVVlazilcu;
mind_bool[448]:=Klima[3].Vlazenje;
mind_bool[449]:=Klima[3].ZamasenFilter;
mind_bool[450]:=Klima[4].Deluje;
mind_bool[451]:=Klima[4].FenThermalCutout;
mind_bool[452]:=Klima[4].GeneralAlarm;
mind_bool[453]:=Klima[4].Kompresor1naMejiObrUr;
mind_bool[454]:=Klima[4].Kompresor2naMejiObrUr;
mind_bool[455]:=Klima[4].Napaka;
mind_bool[456]:=Klima[4].NapakaPriPretokuZraka;
mind_bool[457]:=Klima[4].NapakaSenzorTempIzpiha;
mind_bool[458]:=Klima[4].NapakaSenzorTempProstora;
mind_bool[459]:=Klima[4].NapakaSenzorVlaznosti;
mind_bool[460]:=Klima[4].NapakaSenzorZunanjeTemp;
mind_bool[461]:=Klima[4].NiTokaVVlazilcu;
mind_bool[462]:=Klima[4].NiVodeVVlazilcu;
mind_bool[463]:=Klima[4].NizekPritiskKompresor1;
mind_bool[464]:=Klima[4].NizekPritiskKompresor2;
mind_bool[465]:=Klima[4].NizkaTempVProstoru;
mind_bool[466]:=Klima[4].NizkaVlaznost;
mind_bool[467]:=Klima[4].OnOffEnablingBySupervisor;
mind_bool[468]:=Klima[4].PozarniAlarm;
mind_bool[469]:=Klima[4].Razvlazevanje;
mind_bool[470]:=Klima[4].RemoteOFFtoOutput;
mind_bool[471]:=Klima[4].RocniIzklop;
mind_bool[472]:=Klima[4].SenzorjiStatus;
mind_bool[473]:=Klima[4].UnitOnOff;
mind_bool[474]:=Klima[4].VisokaTempVProstoru;
mind_bool[475]:=Klima[4].VisokaVlaznost;
mind_bool[476]:=Klima[4].VisokTokVVlazilcu;
mind_bool[477]:=Klima[4].Vlazenje;
mind_bool[478]:=Klima[4].ZamasenFilter;
mind_bool[479]:=Klima[5].Deluje;
mind_bool[480]:=Klima[5].FenThermalCutout;
mind_bool[481]:=Klima[5].GeneralAlarm;
mind_bool[482]:=Klima[5].Kompresor1naMejiObrUr;
mind_bool[483]:=Klima[5].Kompresor2naMejiObrUr;
mind_bool[484]:=Klima[5].Napaka;
mind_bool[485]:=Klima[5].NapakaPriPretokuZraka;
mind_bool[486]:=Klima[5].NapakaSenzorTempIzpiha;
mind_bool[487]:=Klima[5].NapakaSenzorTempProstora;
mind_bool[488]:=Klima[5].NapakaSenzorVlaznosti;
mind_bool[489]:=Klima[5].NapakaSenzorZunanjeTemp;
mind_bool[490]:=Klima[5].NiTokaVVlazilcu;
mind_bool[491]:=Klima[5].NiVodeVVlazilcu;
mind_bool[492]:=Klima[5].NizekPritiskKompresor1;
mind_bool[493]:=Klima[5].NizekPritiskKompresor2;
mind_bool[494]:=Klima[5].NizkaTempVProstoru;
mind_bool[495]:=Klima[5].NizkaVlaznost;
mind_bool[496]:=Klima[5].OnOffEnablingBySupervisor;
mind_bool[497]:=Klima[5].PozarniAlarm;
mind_bool[498]:=Klima[5].Razvlazevanje;
mind_bool[499]:=Klima[5].RemoteOFFtoOutput;
mind_bool[500]:=Klima[5].RocniIzklop;
mind_bool[501]:=Klima[5].SenzorjiStatus;
mind_bool[502]:=Klima[5].UnitOnOff;
mind_bool[503]:=Klima[5].VisokaTempVProstoru;
mind_bool[504]:=Klima[5].VisokaVlaznost;
mind_bool[505]:=Klima[5].VisokTokVVlazilcu;
mind_bool[506]:=Klima[5].Vlazenje;
mind_bool[507]:=Klima[5].ZamasenFilter;
mind_bool[508]:=Klima[6].Deluje;
mind_bool[509]:=Klima[6].FenThermalCutout;
mind_bool[510]:=Klima[6].GeneralAlarm;
mind_bool[511]:=Klima[6].Kompresor1naMejiObrUr;
mind_bool[512]:=Klima[6].Kompresor2naMejiObrUr;
mind_bool[513]:=Klima[6].Napaka;
mind_bool[514]:=Klima[6].NapakaPriPretokuZraka;
mind_bool[515]:=Klima[6].NapakaSenzorTempIzpiha;
mind_bool[516]:=Klima[6].NapakaSenzorTempProstora;
mind_bool[517]:=Klima[6].NapakaSenzorVlaznosti;
mind_bool[518]:=Klima[6].NapakaSenzorZunanjeTemp;
mind_bool[519]:=Klima[6].NiTokaVVlazilcu;
mind_bool[520]:=Klima[6].NiVodeVVlazilcu;
mind_bool[521]:=Klima[6].NizekPritiskKompresor1;
mind_bool[522]:=Klima[6].NizekPritiskKompresor2;
mind_bool[523]:=Klima[6].NizkaTempVProstoru;
mind_bool[524]:=Klima[6].NizkaVlaznost;
mind_bool[525]:=Klima[6].OnOffEnablingBySupervisor;
mind_bool[526]:=Klima[6].PozarniAlarm;
mind_bool[527]:=Klima[6].Razvlazevanje;
mind_bool[528]:=Klima[6].RemoteOFFtoOutput;
mind_bool[529]:=Klima[6].RocniIzklop;
mind_bool[530]:=Klima[6].SenzorjiStatus;
mind_bool[531]:=Klima[6].UnitOnOff;
mind_bool[532]:=Klima[6].VisokaTempVProstoru;
mind_bool[533]:=Klima[6].VisokaVlaznost;
mind_bool[534]:=Klima[6].VisokTokVVlazilcu;
mind_bool[535]:=Klima[6].Vlazenje;
mind_bool[536]:=Klima[6].ZamasenFilter;
mind_bool[537]:=KlimeNaCas[0];
mind_bool[538]:=KlimeNaCas[1];
mind_bool[539]:=KlimeNaCas[2];
mind_bool[540]:=KlimeNaCas[3];
mind_bool[541]:=MrezaIzpad;
mind_bool[542]:=MrezaIzpadKlimaOff[1];
mind_bool[543]:=MrezaIzpadKlimaOff[2];
mind_bool[544]:=MrezaIzpadKlimaOff[3];
mind_bool[545]:=MrezaIzpadKlimaOff[4];
mind_bool[546]:=MrezaIzpadKlimaOff[5];
mind_bool[547]:=MrezaIzpadKlimaOff[6];
mind_bool[548]:=NapakaSenzorTemp[1];
mind_bool[549]:=NapakaSenzorTemp[2];
mind_bool[550]:=NapakaSenzorTemp[3];
mind_bool[551]:=NapakaSenzorTemp[4];
mind_bool[552]:=NapakaSenzorTemp[5];
mind_bool[553]:=NapakaSenzorTemp[6];
mind_bool[554]:=NapakaSenzorVlaga[1];
mind_bool[555]:=NapakaSenzorVlaga[2];
mind_bool[556]:=NapakaSenzorVlaga[3];
mind_bool[557]:=NapakaSenzorVlaga[4];
mind_bool[558]:=NapakaSenzorVlaga[5];
mind_bool[559]:=NapakaSenzorVlaga[6];
mind_bool[560]:=PMM.Napaka;
mind_bool[561]:=PMMOverCurrentBetw[1];
mind_bool[562]:=PMMOverCurrentBetw[2];
mind_bool[563]:=PMMOverCurrentBetw[3];
mind_bool[564]:=PMMOverCurrentOver[1];
mind_bool[565]:=PMMOverCurrentOver[2];
mind_bool[566]:=PMMOverCurrentOver[3];
mind_bool[567]:=SetDateTime;
mind_bool[568]:=SetDateTimeDemand;
mind_bool[569]:=SetDateTimeError;
mind_bool[570]:=SetDateTimeFinished;
mind_bool[571]:=SetRemoteOnOff[1];
mind_bool[572]:=SetRemoteOnOff[2];
mind_bool[573]:=SlabaBaterijaPLC_A1;
mind_bool[574]:=TempTSprevisoka[1];
mind_bool[575]:=TempTSprevisoka[2];
mind_bool[576]:=TempTSprevisoka[3];
mind_bool[577]:=TempTSprevisokaSum;
mind_bool[578]:=UPS1Errors[10];
mind_bool[579]:=UPS1Errors[11];
mind_bool[580]:=UPS1Errors[12];
mind_bool[581]:=UPS1Errors[13];
mind_bool[582]:=UPS1Errors[14];
mind_bool[583]:=UPS1Errors[15];
mind_bool[584]:=UPS1Errors[16];
mind_bool[585]:=UPS1Errors[17];
mind_bool[586]:=UPS1Errors[18];
mind_bool[587]:=UPS1Errors[19];
mind_bool[588]:=UPS1Errors[1];
mind_bool[589]:=UPS1Errors[20];
mind_bool[590]:=UPS1Errors[21];
mind_bool[591]:=UPS1Errors[22];
mind_bool[592]:=UPS1Errors[23];
mind_bool[593]:=UPS1Errors[24];
mind_bool[594]:=UPS1Errors[25];
mind_bool[595]:=UPS1Errors[2];
mind_bool[596]:=UPS1Errors[3];
mind_bool[597]:=UPS1Errors[4];
mind_bool[598]:=UPS1Errors[5];
mind_bool[599]:=UPS1Errors[6];
mind_bool[600]:=UPS1Errors[7];
mind_bool[601]:=UPS1Errors[8];
mind_bool[602]:=UPS1Errors[9];
mind_bool[603]:=UPS2Errors[10];
mind_bool[604]:=UPS2Errors[11];
mind_bool[605]:=UPS2Errors[12];
mind_bool[606]:=UPS2Errors[13];
mind_bool[607]:=UPS2Errors[14];
mind_bool[608]:=UPS2Errors[15];
mind_bool[609]:=UPS2Errors[16];
mind_bool[610]:=UPS2Errors[17];
mind_bool[611]:=UPS2Errors[18];
mind_bool[612]:=UPS2Errors[19];
mind_bool[613]:=UPS2Errors[1];
mind_bool[614]:=UPS2Errors[20];
mind_bool[615]:=UPS2Errors[21];
mind_bool[616]:=UPS2Errors[22];
mind_bool[617]:=UPS2Errors[23];
mind_bool[618]:=UPS2Errors[24];
mind_bool[619]:=UPS2Errors[25];
mind_bool[620]:=UPS2Errors[2];
mind_bool[621]:=UPS2Errors[3];
mind_bool[622]:=UPS2Errors[4];
mind_bool[623]:=UPS2Errors[5];
mind_bool[624]:=UPS2Errors[6];
mind_bool[625]:=UPS2Errors[7];
mind_bool[626]:=UPS2Errors[8];
mind_bool[627]:=UPS2Errors[9];
mind_bool[628]:=UPS[1].AlarmAwaitingPower;
mind_bool[629]:=UPS[1].AlarmBypassBad;
mind_bool[630]:=UPS[1].AlarmChargerFailed;
mind_bool[631]:=UPS[1].AlarmCommunicationsLost;
mind_bool[632]:=UPS[1].AlarmDepletedBattery;
mind_bool[633]:=UPS[1].AlarmDiagnosticTestFailed;
mind_bool[634]:=UPS[1].AlarmInverterError;
mind_bool[635]:=UPS[1].AlarmIzhodOffKotZahtevano;
mind_bool[636]:=UPS[1].AlarmIzhodPreobremenjen;
mind_bool[637]:=UPS[1].AlarmLowBattery;
mind_bool[638]:=UPS[1].AlarmNapakaNaVarovalki;
mind_bool[639]:=UPS[1].AlarmNapakaNaVentilatorju;
mind_bool[640]:=UPS[1].AlarmOnBattery;
mind_bool[641]:=UPS[1].AlarmOnBypass;
mind_bool[642]:=UPS[1].AlarmShutdownImminent;
mind_bool[643]:=UPS[1].AlarmShutdownPending;
mind_bool[644]:=UPS[1].AlarmSlabaBaterija;
mind_bool[645]:=UPS[1].AlarmSplosnaNapaka;
mind_bool[646]:=UPS[1].AlarmStanjeIzhodaIzvenToleranc;
mind_bool[647]:=UPS[1].AlarmStanjeVhodaIzvenToleranc;
mind_bool[648]:=UPS[1].AlarmTemperaturaIzvenToleranc;
mind_bool[649]:=UPS[1].AlarmTestInProgres;
mind_bool[650]:=UPS[1].AlarmUPSIzhodOff;
mind_bool[651]:=UPS[1].AlarmUPSOffKotZahtevano;
mind_bool[652]:=UPS[1].AlarmUPSSystemOff;
mind_bool[653]:=UPS[1].Napaka;
mind_bool[654]:=UPS[1].StatusEcomodeAktiven;
mind_bool[655]:=UPS[1].StatusInverterIsOn;
mind_bool[656]:=UPS[1].StatusStopOperation;
mind_bool[657]:=UPS[2].AlarmAwaitingPower;
mind_bool[658]:=UPS[2].AlarmBypassBad;
mind_bool[659]:=UPS[2].AlarmChargerFailed;
mind_bool[660]:=UPS[2].AlarmCommunicationsLost;
mind_bool[661]:=UPS[2].AlarmDepletedBattery;
mind_bool[662]:=UPS[2].AlarmDiagnosticTestFailed;
mind_bool[663]:=UPS[2].AlarmInverterError;
mind_bool[664]:=UPS[2].AlarmIzhodOffKotZahtevano;
mind_bool[665]:=UPS[2].AlarmIzhodPreobremenjen;
mind_bool[666]:=UPS[2].AlarmLowBattery;
mind_bool[667]:=UPS[2].AlarmNapakaNaVarovalki;
mind_bool[668]:=UPS[2].AlarmNapakaNaVentilatorju;
mind_bool[669]:=UPS[2].AlarmOnBattery;
mind_bool[670]:=UPS[2].AlarmOnBypass;
mind_bool[671]:=UPS[2].AlarmShutdownImminent;
mind_bool[672]:=UPS[2].AlarmShutdownPending;
mind_bool[673]:=UPS[2].AlarmSlabaBaterija;
mind_bool[674]:=UPS[2].AlarmSplosnaNapaka;
mind_bool[675]:=UPS[2].AlarmStanjeIzhodaIzvenToleranc;
mind_bool[676]:=UPS[2].AlarmStanjeVhodaIzvenToleranc;
mind_bool[677]:=UPS[2].AlarmTemperaturaIzvenToleranc;
mind_bool[678]:=UPS[2].AlarmTestInProgres;
mind_bool[679]:=UPS[2].AlarmUPSIzhodOff;
mind_bool[680]:=UPS[2].AlarmUPSOffKotZahtevano;
mind_bool[681]:=UPS[2].AlarmUPSSystemOff;
mind_bool[682]:=UPS[2].Napaka;
mind_bool[683]:=UPS[2].StatusEcomodeAktiven;
mind_bool[684]:=UPS[2].StatusInverterIsOn;
mind_bool[685]:=UPS[2].StatusStopOperation;
mind_bool[686]:=UserLoggedIn;
mind_bool[687]:=DIN_A1Q11_OdcUpsB_IZP;
mind_bool[688]:=DIN_A1Q12_OdcByUpsB_IZP;
mind_bool[689]:=DIN_A1Q13_OdcByB_IZP;
mind_bool[690]:=DIN_UQ11_OdcPMMB_IZP;
mind_bool[691]:=DIN_UQ12_OdcPMMB_IZP;
mind_bool[692]:=DIN_PrenapA3_OK;
mind_bool[693]:=DIN_A1Q0_GlavnoStiB_ON;
mind_bool[694]:=DIN_A1Q11_OdcUpsB_ON;
mind_bool[695]:=DIN_A1Q12_OdcByUpsB_ON;
mind_bool[696]:=DI_A1Q13_OdcByB_ON;
mind_bool[697]:=DIN_A1Q01_DovUpsB_ON;
mind_bool[698]:=DI_A1Q02_DovByB_ON;
mind_bool[699]:=DIN_UQ11_OdcPMMB_ON;
mind_bool[700]:=DI_UQ12_OdcPMMB_ON;
mind_bool[701]:=Klima[1].NapacnoGesloAlarm;
mind_bool[702]:=Klima[1].ExtTempHumAlarm;
mind_bool[703]:=Klima[1].PoplavniAlarm;
mind_bool[704]:=Klima[1].VisokPritiskKompresor1;
mind_bool[705]:=Klima[1].VisokPritiskKompresor2;
mind_bool[706]:=Klima[1].ElVentilKompresor1ERR;
mind_bool[707]:=Klima[1].ElVentilKompresor2ERR;
mind_bool[708]:=Klima[1].WrongPhaseSeqAlarm;
mind_bool[709]:=Klima[1].PrekinjenLANalarm;
mind_bool[710]:=Klima[1].CWTempHighForDehum;
mind_bool[711]:=Klima[1].CWVentilErrOrLowFlow;
mind_bool[712]:=Klima[1].NapakaPriPretokuVode;
mind_bool[713]:=Klima[1].CWhighTemp;
mind_bool[714]:=Klima[1].NapakaSenzorHotWTemp;
mind_bool[715]:=Klima[1].NapakaSenzorCondWTemp;
mind_bool[716]:=Klima[1].NapakaSenzorCW;
mind_bool[717]:=Klima[1].Kompresor3naMejiObrUr;
mind_bool[718]:=Klima[1].Kompresor4naMejiObrUr;
mind_bool[719]:=Klima[1].ZracniFilterNaMejiObrUr;
mind_bool[720]:=Klima[1].Grelec1naMejiObrUr;
mind_bool[721]:=Klima[1].Grelec2naMejiObrUr;
mind_bool[722]:=Klima[1].VlazilecNaMejiObrUr;
mind_bool[723]:=Klima[1].AirCondUnitNaMejiObrUr;
mind_bool[724]:=Klima[1].DigIn2Alarm;
mind_bool[725]:=Klima[1].DigIn4Alarm;
mind_bool[726]:=Klima[1].DigIn6Alarm;
mind_bool[727]:=Klima[1].VlazilecGenAlarm;
mind_bool[728]:=Klima[1].General2ndLevAlarm;
mind_bool[729]:=Klima[1].UnitOnRotAlarm;
mind_bool[730]:=Klima[1].UnitOnAlarmA;
mind_bool[731]:=Klima[1].UnitOnAlarmB;
mind_bool[732]:=Klima[1].UnitOnAlarmC;
mind_bool[733]:=Klima[2].NapacnoGesloAlarm;
mind_bool[734]:=Klima[2].ExtTempHumAlarm;
mind_bool[735]:=Klima[2].PoplavniAlarm;
mind_bool[736]:=Klima[2].VisokPritiskKompresor1;
mind_bool[737]:=Klima[2].VisokPritiskKompresor2;
mind_bool[738]:=Klima[2].ElVentilKompresor1ERR;
mind_bool[739]:=Klima[2].ElVentilKompresor2ERR;
mind_bool[740]:=Klima[2].WrongPhaseSeqAlarm;
mind_bool[741]:=Klima[2].PrekinjenLANalarm;
mind_bool[742]:=Klima[2].CWTempHighForDehum;
mind_bool[743]:=Klima[2].CWVentilErrOrLowFlow;
mind_bool[744]:=Klima[2].NapakaPriPretokuVode;
mind_bool[745]:=Klima[2].CWhighTemp;
mind_bool[746]:=Klima[2].NapakaSenzorHotWTemp;
mind_bool[747]:=Klima[2].NapakaSenzorCondWTemp;
mind_bool[748]:=Klima[2].NapakaSenzorCW;
mind_bool[749]:=Klima[2].Kompresor3naMejiObrUr;
mind_bool[750]:=Klima[2].Kompresor4naMejiObrUr;
mind_bool[751]:=Klima[2].ZracniFilterNaMejiObrUr;
mind_bool[752]:=Klima[2].Grelec1naMejiObrUr;
mind_bool[753]:=Klima[2].Grelec2naMejiObrUr;
mind_bool[754]:=Klima[2].VlazilecNaMejiObrUr;
mind_bool[755]:=Klima[2].AirCondUnitNaMejiObrUr;
mind_bool[756]:=Klima[2].DigIn2Alarm;
mind_bool[757]:=Klima[2].DigIn4Alarm;
mind_bool[758]:=Klima[2].DigIn6Alarm;
mind_bool[759]:=Klima[2].VlazilecGenAlarm;
mind_bool[760]:=Klima[2].General2ndLevAlarm;
mind_bool[761]:=Klima[2].UnitOnRotAlarm;
mind_bool[762]:=Klima[2].UnitOnAlarmA;
mind_bool[763]:=Klima[2].UnitOnAlarmB;
mind_bool[764]:=Klima[2].UnitOnAlarmC;
mind_bool[765]:=Klima[3].NapacnoGesloAlarm;
mind_bool[766]:=Klima[3].ExtTempHumAlarm;
mind_bool[767]:=Klima[3].PoplavniAlarm;
mind_bool[768]:=Klima[3].VisokPritiskKompresor1;
mind_bool[769]:=Klima[3].VisokPritiskKompresor2;
mind_bool[770]:=Klima[3].ElVentilKompresor1ERR;
mind_bool[771]:=Klima[3].ElVentilKompresor2ERR;
mind_bool[772]:=Klima[3].WrongPhaseSeqAlarm;
mind_bool[773]:=Klima[3].PrekinjenLANalarm;
mind_bool[774]:=Klima[3].CWTempHighForDehum;
mind_bool[775]:=Klima[3].CWVentilErrOrLowFlow;
mind_bool[776]:=Klima[3].NapakaPriPretokuVode;
mind_bool[777]:=Klima[3].CWhighTemp;
mind_bool[778]:=Klima[3].NapakaSenzorHotWTemp;
mind_bool[779]:=Klima[3].NapakaSenzorCondWTemp;
mind_bool[780]:=Klima[3].NapakaSenzorCW;
mind_bool[781]:=Klima[3].Kompresor3naMejiObrUr;
mind_bool[782]:=Klima[3].Kompresor4naMejiObrUr;
mind_bool[783]:=Klima[3].ZracniFilterNaMejiObrUr;
mind_bool[784]:=Klima[3].Grelec1naMejiObrUr;
mind_bool[785]:=Klima[3].Grelec2naMejiObrUr;
mind_bool[786]:=Klima[3].VlazilecNaMejiObrUr;
mind_bool[787]:=Klima[3].AirCondUnitNaMejiObrUr;
mind_bool[788]:=Klima[3].DigIn2Alarm;
mind_bool[789]:=Klima[3].DigIn4Alarm;
mind_bool[790]:=Klima[3].DigIn6Alarm;
mind_bool[791]:=Klima[3].VlazilecGenAlarm;
mind_bool[792]:=Klima[3].General2ndLevAlarm;
mind_bool[793]:=Klima[3].UnitOnRotAlarm;
mind_bool[794]:=Klima[3].UnitOnAlarmA;
mind_bool[795]:=Klima[3].UnitOnAlarmB;
mind_bool[796]:=Klima[3].UnitOnAlarmC;
mind_bool[797]:=Klima[4].NapacnoGesloAlarm;
mind_bool[798]:=Klima[4].ExtTempHumAlarm;
mind_bool[799]:=Klima[4].PoplavniAlarm;
mind_bool[800]:=Klima[4].VisokPritiskKompresor1;
mind_bool[801]:=Klima[4].VisokPritiskKompresor2;
mind_bool[802]:=Klima[4].ElVentilKompresor1ERR;
mind_bool[803]:=Klima[4].ElVentilKompresor2ERR;
mind_bool[804]:=Klima[4].WrongPhaseSeqAlarm;
mind_bool[805]:=Klima[4].PrekinjenLANalarm;
mind_bool[806]:=Klima[4].CWTempHighForDehum;
mind_bool[807]:=Klima[4].CWVentilErrOrLowFlow;
mind_bool[808]:=Klima[4].NapakaPriPretokuVode;
mind_bool[809]:=Klima[4].CWhighTemp;
mind_bool[810]:=Klima[4].NapakaSenzorHotWTemp;
mind_bool[811]:=Klima[4].NapakaSenzorCondWTemp;
mind_bool[812]:=Klima[4].NapakaSenzorCW;
mind_bool[813]:=Klima[4].Kompresor3naMejiObrUr;
mind_bool[814]:=Klima[4].Kompresor4naMejiObrUr;
mind_bool[815]:=Klima[4].ZracniFilterNaMejiObrUr;
mind_bool[816]:=Klima[4].Grelec1naMejiObrUr;
mind_bool[817]:=Klima[4].Grelec2naMejiObrUr;
mind_bool[818]:=Klima[4].VlazilecNaMejiObrUr;
mind_bool[819]:=Klima[4].AirCondUnitNaMejiObrUr;
mind_bool[820]:=Klima[4].DigIn2Alarm;
mind_bool[821]:=Klima[4].DigIn4Alarm;
mind_bool[822]:=Klima[4].DigIn6Alarm;
mind_bool[823]:=Klima[4].VlazilecGenAlarm;
mind_bool[824]:=Klima[4].General2ndLevAlarm;
mind_bool[825]:=Klima[4].UnitOnRotAlarm;
mind_bool[826]:=Klima[4].UnitOnAlarmA;
mind_bool[827]:=Klima[4].UnitOnAlarmB;
mind_bool[828]:=Klima[4].UnitOnAlarmC;
mind_bool[829]:=Klima[5].NapacnoGesloAlarm;
mind_bool[830]:=Klima[5].ExtTempHumAlarm;
mind_bool[831]:=Klima[5].PoplavniAlarm;
mind_bool[832]:=Klima[5].VisokPritiskKompresor1;
mind_bool[833]:=Klima[5].VisokPritiskKompresor2;
mind_bool[834]:=Klima[5].ElVentilKompresor1ERR;
mind_bool[835]:=Klima[5].ElVentilKompresor2ERR;
mind_bool[836]:=Klima[5].WrongPhaseSeqAlarm;
mind_bool[837]:=Klima[5].PrekinjenLANalarm;
mind_bool[838]:=Klima[5].CWTempHighForDehum;
mind_bool[839]:=Klima[5].CWVentilErrOrLowFlow;
mind_bool[840]:=Klima[5].NapakaPriPretokuVode;
mind_bool[841]:=Klima[5].CWhighTemp;
mind_bool[842]:=Klima[5].NapakaSenzorHotWTemp;
mind_bool[843]:=Klima[5].NapakaSenzorCondWTemp;
mind_bool[844]:=Klima[5].NapakaSenzorCW;
mind_bool[845]:=Klima[5].Kompresor3naMejiObrUr;
mind_bool[846]:=Klima[5].Kompresor4naMejiObrUr;
mind_bool[847]:=Klima[5].ZracniFilterNaMejiObrUr;
mind_bool[848]:=Klima[5].Grelec1naMejiObrUr;
mind_bool[849]:=Klima[5].Grelec2naMejiObrUr;
mind_bool[850]:=Klima[5].VlazilecNaMejiObrUr;
mind_bool[851]:=Klima[5].AirCondUnitNaMejiObrUr;
mind_bool[852]:=Klima[5].DigIn2Alarm;
mind_bool[853]:=Klima[5].DigIn4Alarm;
mind_bool[854]:=Klima[5].DigIn6Alarm;
mind_bool[855]:=Klima[5].VlazilecGenAlarm;
mind_bool[856]:=Klima[5].General2ndLevAlarm;
mind_bool[857]:=Klima[5].UnitOnRotAlarm;
mind_bool[858]:=Klima[5].UnitOnAlarmA;
mind_bool[859]:=Klima[5].UnitOnAlarmB;
mind_bool[860]:=Klima[5].UnitOnAlarmC;
mind_bool[861]:=Klima[6].NapacnoGesloAlarm;
mind_bool[862]:=Klima[6].ExtTempHumAlarm;
mind_bool[863]:=Klima[6].PoplavniAlarm;
mind_bool[864]:=Klima[6].VisokPritiskKompresor1;
mind_bool[865]:=Klima[6].VisokPritiskKompresor2;
mind_bool[866]:=Klima[6].ElVentilKompresor1ERR;
mind_bool[867]:=Klima[6].ElVentilKompresor2ERR;
mind_bool[868]:=Klima[6].WrongPhaseSeqAlarm;
mind_bool[869]:=Klima[6].PrekinjenLANalarm;
mind_bool[870]:=Klima[6].CWTempHighForDehum;
mind_bool[871]:=Klima[6].CWVentilErrOrLowFlow;
mind_bool[872]:=Klima[6].NapakaPriPretokuVode;
mind_bool[873]:=Klima[6].CWhighTemp;
mind_bool[874]:=Klima[6].NapakaSenzorHotWTemp;
mind_bool[875]:=Klima[6].NapakaSenzorCondWTemp;
mind_bool[876]:=Klima[6].NapakaSenzorCW;
mind_bool[877]:=Klima[6].Kompresor3naMejiObrUr;
mind_bool[878]:=Klima[6].Kompresor4naMejiObrUr;
mind_bool[879]:=Klima[6].ZracniFilterNaMejiObrUr;
mind_bool[880]:=Klima[6].Grelec1naMejiObrUr;
mind_bool[881]:=Klima[6].Grelec2naMejiObrUr;
mind_bool[882]:=Klima[6].VlazilecNaMejiObrUr;
mind_bool[883]:=Klima[6].AirCondUnitNaMejiObrUr;
mind_bool[884]:=Klima[6].DigIn2Alarm;
mind_bool[885]:=Klima[6].DigIn4Alarm;
mind_bool[886]:=Klima[6].DigIn6Alarm;
mind_bool[887]:=Klima[6].VlazilecGenAlarm;
mind_bool[888]:=Klima[6].General2ndLevAlarm;
mind_bool[889]:=Klima[6].UnitOnRotAlarm;
mind_bool[890]:=Klima[6].UnitOnAlarmA;
mind_bool[891]:=Klima[6].UnitOnAlarmB;
mind_bool[892]:=Klima[6].UnitOnAlarmC;
mind_bool[893]:=Klima[1].Komp1On;
mind_bool[894]:=Klima[1].Komp2On;
mind_bool[895]:=Klima[1].Komp3On;
mind_bool[896]:=Klima[1].Komp4On;
mind_bool[897]:=Klima[2].Komp1On;
mind_bool[898]:=Klima[2].Komp2On;
mind_bool[899]:=Klima[2].Komp3On;
mind_bool[900]:=Klima[2].Komp4On;
mind_bool[901]:=Klima[3].Komp1On;
mind_bool[902]:=Klima[3].Komp2On;
mind_bool[903]:=Klima[3].Komp3On;
mind_bool[904]:=Klima[3].Komp4On;
mind_bool[905]:=Klima[4].Komp1On;
mind_bool[906]:=Klima[4].Komp2On;
mind_bool[907]:=Klima[4].Komp3On;
mind_bool[908]:=Klima[4].Komp4On;
mind_bool[909]:=Klima[5].Komp1On;
mind_bool[910]:=Klima[5].Komp2On;
mind_bool[911]:=Klima[5].Komp3On;
mind_bool[912]:=Klima[5].Komp4On;
mind_bool[913]:=Klima[6].Komp1On;
mind_bool[914]:=Klima[6].Komp2On;
mind_bool[915]:=Klima[6].Komp3On;
mind_bool[916]:=Klima[6].Komp4On;
mind_bool[917]:=Klima[1].GretjeStopnja1;
mind_bool[918]:=Klima[1].GretjeStopnja2;
mind_bool[919]:=Klima[1].GretjeStopnja3;
mind_bool[920]:=Klima[2].GretjeStopnja1;
mind_bool[921]:=Klima[2].GretjeStopnja2;
mind_bool[922]:=Klima[2].GretjeStopnja3;
mind_bool[923]:=Klima[3].GretjeStopnja1;
mind_bool[924]:=Klima[3].GretjeStopnja2;
mind_bool[925]:=Klima[3].GretjeStopnja3;
mind_bool[926]:=Klima[4].GretjeStopnja1;
mind_bool[927]:=Klima[4].GretjeStopnja2;
mind_bool[928]:=Klima[4].GretjeStopnja3;
mind_bool[929]:=Klima[5].GretjeStopnja1;
mind_bool[930]:=Klima[5].GretjeStopnja2;
mind_bool[931]:=Klima[5].GretjeStopnja3;
mind_bool[932]:=Klima[6].GretjeStopnja1;
mind_bool[933]:=Klima[6].GretjeStopnja2;
mind_bool[934]:=Klima[6].GretjeStopnja3;
mind_bool[935]:=Klima[1].HotGasOn;
mind_bool[936]:=Klima[2].HotGasOn;
mind_bool[937]:=Klima[3].HotGasOn;
mind_bool[938]:=Klima[4].HotGasOn;
mind_bool[939]:=Klima[5].HotGasOn;
mind_bool[940]:=Klima[6].HotGasOn;
mind_bool[941]:=Klima[1].EmergencyWorking;
mind_bool[942]:=Klima[2].EmergencyWorking;
mind_bool[943]:=Klima[3].EmergencyWorking;
mind_bool[944]:=Klima[4].EmergencyWorking;
mind_bool[945]:=Klima[5].EmergencyWorking;
mind_bool[946]:=Klima[6].EmergencyWorking;
mind_bool[947]:=DI_A1Q01_DovUpsB_ON;
mind_bool[948]:=DI_A1Q0_GlavnoStiB_ON;
mind_bool[949]:=DI_A1Q11_OdcUpsB_IZP;
mind_bool[950]:=DI_A1Q11_OdcUpsB_ON;
mind_bool[951]:=DI_A1Q12_OdcByUpsB_IZP;
mind_bool[952]:=DI_A1Q12_OdcByUpsB_ON;
mind_bool[953]:=DI_A1Q13_OdcByB_IZP;
mind_bool[954]:=ErrCommScada2;
mind_bool[955]:=ComSCADA2;
mind_bool[956]:=ComSCADA3;
(*Branje INT*)
(**)
mind[0]:=DateTime.Dan;
mind[1]:=DateTime.Leto;
mind[2]:=DateTime.Mesec;
mind[3]:=DateTime.Minuta;
mind[4]:=DateTime.Sekunda;
mind[5]:=DateTime.Ura;
mind[6]:=ErrorComKlima[1].Code[10];
mind[7]:=ErrorComKlima[1].Code[11];
mind[8]:=ErrorComKlima[1].Code[12];
mind[9]:=ErrorComKlima[1].Code[13];
mind[10]:=ErrorComKlima[1].Code[14];
mind[11]:=ErrorComKlima[1].Code[15];
mind[12]:=ErrorComKlima[1].Code[1];
mind[13]:=ErrorComKlima[1].Code[2];
mind[14]:=ErrorComKlima[1].Code[3];
mind[15]:=ErrorComKlima[1].Code[4];
mind[16]:=ErrorComKlima[1].Code[5];
mind[17]:=ErrorComKlima[1].Code[6];
mind[18]:=ErrorComKlima[1].Code[7];
mind[19]:=ErrorComKlima[1].Code[8];
mind[20]:=ErrorComKlima[1].Code[9];
mind[21]:=ErrorComKlima[1].Status;
mind[22]:=ErrorComKlima[2].Code[10];
mind[23]:=ErrorComKlima[2].Code[11];
mind[24]:=ErrorComKlima[2].Code[12];
mind[25]:=ErrorComKlima[2].Code[13];
mind[26]:=ErrorComKlima[2].Code[14];
mind[27]:=ErrorComKlima[2].Code[15];
mind[28]:=ErrorComKlima[2].Code[1];
mind[29]:=ErrorComKlima[2].Code[2];
mind[30]:=ErrorComKlima[2].Code[3];
mind[31]:=ErrorComKlima[2].Code[4];
mind[32]:=ErrorComKlima[2].Code[5];
mind[33]:=ErrorComKlima[2].Code[6];
mind[34]:=ErrorComKlima[2].Code[7];
mind[35]:=ErrorComKlima[2].Code[8];
mind[36]:=ErrorComKlima[2].Code[9];
mind[37]:=ErrorComKlima[2].Status;
mind[38]:=ErrorComKlima[3].Code[10];
mind[39]:=ErrorComKlima[3].Code[11];
mind[40]:=ErrorComKlima[3].Code[12];
mind[41]:=ErrorComKlima[3].Code[13];
mind[42]:=ErrorComKlima[3].Code[14];
mind[43]:=ErrorComKlima[3].Code[15];
mind[44]:=ErrorComKlima[3].Code[1];
mind[45]:=ErrorComKlima[3].Code[2];
mind[46]:=ErrorComKlima[3].Code[3];
mind[47]:=ErrorComKlima[3].Code[4];
mind[48]:=ErrorComKlima[3].Code[5];
mind[49]:=ErrorComKlima[3].Code[6];
mind[50]:=ErrorComKlima[3].Code[7];
mind[51]:=ErrorComKlima[3].Code[8];
mind[52]:=ErrorComKlima[3].Code[9];
mind[53]:=ErrorComKlima[3].Status;
mind[54]:=ErrorComKlima[4].Code[10];
mind[55]:=ErrorComKlima[4].Code[11];
mind[56]:=ErrorComKlima[4].Code[12];
mind[57]:=ErrorComKlima[4].Code[13];
mind[58]:=ErrorComKlima[4].Code[14];
mind[59]:=ErrorComKlima[4].Code[15];
mind[60]:=ErrorComKlima[4].Code[1];
mind[61]:=ErrorComKlima[4].Code[2];
mind[62]:=ErrorComKlima[4].Code[3];
mind[63]:=ErrorComKlima[4].Code[4];
mind[64]:=ErrorComKlima[4].Code[5];
mind[65]:=ErrorComKlima[4].Code[6];
mind[66]:=ErrorComKlima[4].Code[7];
mind[67]:=ErrorComKlima[4].Code[8];
mind[68]:=ErrorComKlima[4].Code[9];
mind[69]:=ErrorComKlima[4].Status;
mind[70]:=ErrorComKlima[5].Code[10];
mind[71]:=ErrorComKlima[5].Code[11];
mind[72]:=ErrorComKlima[5].Code[12];
mind[73]:=ErrorComKlima[5].Code[13];
mind[74]:=ErrorComKlima[5].Code[14];
mind[75]:=ErrorComKlima[5].Code[15];
mind[76]:=ErrorComKlima[5].Code[1];
mind[77]:=ErrorComKlima[5].Code[2];
mind[78]:=ErrorComKlima[5].Code[3];
mind[79]:=ErrorComKlima[5].Code[4];
mind[80]:=ErrorComKlima[5].Code[5];
mind[81]:=ErrorComKlima[5].Code[6];
mind[82]:=ErrorComKlima[5].Code[7];
mind[83]:=ErrorComKlima[5].Code[8];
mind[84]:=ErrorComKlima[5].Code[9];
mind[85]:=ErrorComKlima[5].Status;
mind[86]:=ErrorComKlima[6].Code[10];
mind[87]:=ErrorComKlima[6].Code[11];
mind[88]:=ErrorComKlima[6].Code[12];
mind[89]:=ErrorComKlima[6].Code[13];
mind[90]:=ErrorComKlima[6].Code[14];
mind[91]:=ErrorComKlima[6].Code[15];
mind[92]:=ErrorComKlima[6].Code[1];
mind[93]:=ErrorComKlima[6].Code[2];
mind[94]:=ErrorComKlima[6].Code[3];
mind[95]:=ErrorComKlima[6].Code[4];
mind[96]:=ErrorComKlima[6].Code[5];
mind[97]:=ErrorComKlima[6].Code[6];
mind[98]:=ErrorComKlima[6].Code[7];
mind[99]:=ErrorComKlima[6].Code[8];
mind[100]:=ErrorComKlima[6].Code[9];
mind[101]:=ErrorComKlima[6].Status;
mind[102]:=ErrorComPMM.Code[10];
mind[103]:=ErrorComPMM.Code[11];
mind[104]:=ErrorComPMM.Code[12];
mind[105]:=ErrorComPMM.Code[13];
mind[106]:=ErrorComPMM.Code[14];
mind[107]:=ErrorComPMM.Code[15];
mind[108]:=ErrorComPMM.Code[1];
mind[109]:=ErrorComPMM.Code[2];
mind[110]:=ErrorComPMM.Code[3];
mind[111]:=ErrorComPMM.Code[4];
mind[112]:=ErrorComPMM.Code[5];
mind[113]:=ErrorComPMM.Code[6];
mind[114]:=ErrorComPMM.Code[7];
mind[115]:=ErrorComPMM.Code[8];
mind[116]:=ErrorComPMM.Code[9];
mind[117]:=ErrorComPMM.Status;
mind[118]:=ErrorComUPS[1].Code[10];
mind[119]:=ErrorComUPS[1].Code[11];
mind[120]:=ErrorComUPS[1].Code[12];
mind[121]:=ErrorComUPS[1].Code[13];
mind[122]:=ErrorComUPS[1].Code[14];
mind[123]:=ErrorComUPS[1].Code[15];
mind[124]:=ErrorComUPS[1].Code[1];
mind[125]:=ErrorComUPS[1].Code[2];
mind[126]:=ErrorComUPS[1].Code[3];
mind[127]:=ErrorComUPS[1].Code[4];
mind[128]:=ErrorComUPS[1].Code[5];
mind[129]:=ErrorComUPS[1].Code[6];
mind[130]:=ErrorComUPS[1].Code[7];
mind[131]:=ErrorComUPS[1].Code[8];
mind[132]:=ErrorComUPS[1].Code[9];
mind[133]:=ErrorComUPS[1].Status;
mind[134]:=ErrorComUPS[2].Code[10];
mind[135]:=ErrorComUPS[2].Code[11];
mind[136]:=ErrorComUPS[2].Code[12];
mind[137]:=ErrorComUPS[2].Code[13];
mind[138]:=ErrorComUPS[2].Code[14];
mind[139]:=ErrorComUPS[2].Code[15];
mind[140]:=ErrorComUPS[2].Code[1];
mind[141]:=ErrorComUPS[2].Code[2];
mind[142]:=ErrorComUPS[2].Code[3];
mind[143]:=ErrorComUPS[2].Code[4];
mind[144]:=ErrorComUPS[2].Code[5];
mind[145]:=ErrorComUPS[2].Code[6];
mind[146]:=ErrorComUPS[2].Code[7];
mind[147]:=ErrorComUPS[2].Code[8];
mind[148]:=ErrorComUPS[2].Code[9];
mind[149]:=ErrorComUPS[2].Status;
mind[150]:=Klima[1].GrelecStatus;
mind[151]:=Klima[1].IzhodniVentStatus;
mind[152]:=Klima[1].KompresorStatus;
mind[153]:=Klima[1].VlazilecStatus;
mind[154]:=Klima[2].GrelecStatus;
mind[155]:=Klima[2].IzhodniVentStatus;
mind[156]:=Klima[2].KompresorStatus;
mind[157]:=Klima[2].VlazilecStatus;
mind[158]:=Klima[3].GrelecStatus;
mind[159]:=Klima[3].IzhodniVentStatus;
mind[160]:=Klima[3].KompresorStatus;
mind[161]:=Klima[3].VlazilecStatus;
mind[162]:=Klima[4].GrelecStatus;
mind[163]:=Klima[4].IzhodniVentStatus;
mind[164]:=Klima[4].KompresorStatus;
mind[165]:=Klima[4].VlazilecStatus;
mind[166]:=Klima[5].GrelecStatus;
mind[167]:=Klima[5].IzhodniVentStatus;
mind[168]:=Klima[5].KompresorStatus;
mind[169]:=Klima[5].VlazilecStatus;
mind[170]:=Klima[6].GrelecStatus;
mind[171]:=Klima[6].IzhodniVentStatus;
mind[172]:=Klima[6].KompresorStatus;
mind[173]:=Klima[6].VlazilecStatus;
mind[174]:=MrezaIzpadVklopDelay[1];
mind[175]:=MrezaIzpadVklopDelay[2];
mind[176]:=MrezaIzpadVklopDelay[3];
mind[177]:=MrezaIzpadVklopDelay[4];
mind[178]:=MrezaIzpadVklopDelay[5];
mind[179]:=MrezaIzpadVklopDelay[6];
mind[180]:=PMM.AlarmPhase[1].C01_16_60to80;
mind[181]:=PMM.AlarmPhase[1].C01_16_over80;
mind[182]:=PMM.AlarmPhase[1].C17_32_60to80;
mind[183]:=PMM.AlarmPhase[1].C17_32_over80;
mind[184]:=PMM.AlarmPhase[1].C33_42_60to80;
mind[185]:=PMM.AlarmPhase[1].C33_42_over80;
mind[186]:=PMM.AlarmPhase[2].C01_16_60to80;
mind[187]:=PMM.AlarmPhase[2].C01_16_over80;
mind[188]:=PMM.AlarmPhase[2].C17_32_60to80;
mind[189]:=PMM.AlarmPhase[2].C17_32_over80;
mind[190]:=PMM.AlarmPhase[2].C33_42_60to80;
mind[191]:=PMM.AlarmPhase[2].C33_42_over80;
mind[192]:=PMM.AlarmPhase[3].C01_16_60to80;
mind[193]:=PMM.AlarmPhase[3].C01_16_over80;
mind[194]:=PMM.AlarmPhase[3].C17_32_60to80;
mind[195]:=PMM.AlarmPhase[3].C17_32_over80;
mind[196]:=PMM.AlarmPhase[3].C33_42_60to80;
mind[197]:=PMM.AlarmPhase[3].C33_42_over80;
mind[198]:=Qstanje[10];
mind[199]:=Qstanje[11];
mind[200]:=Qstanje[12];
mind[201]:=Qstanje[13];
mind[202]:=Qstanje[14];
mind[203]:=Qstanje[15];
mind[204]:=Qstanje[16];
mind[205]:=Qstanje[17];
mind[206]:=Qstanje[18];
mind[207]:=Qstanje[19];
mind[208]:=Qstanje[1];
mind[209]:=Qstanje[20];
mind[210]:=Qstanje[21];
mind[211]:=Qstanje[22];
mind[212]:=Qstanje[23];
mind[213]:=Qstanje[24];
mind[214]:=Qstanje[25];
mind[215]:=Qstanje[26];
mind[216]:=Qstanje[27];
mind[217]:=Qstanje[28];
mind[218]:=Qstanje[29];
mind[219]:=Qstanje[2];
mind[220]:=Qstanje[30];
mind[221]:=Qstanje[31];
mind[222]:=Qstanje[32];
mind[223]:=Qstanje[33];
mind[224]:=Qstanje[34];
mind[225]:=Qstanje[35];
mind[226]:=Qstanje[3];
mind[227]:=Qstanje[4];
mind[228]:=Qstanje[5];
mind[229]:=Qstanje[6];
mind[230]:=Qstanje[7];
mind[231]:=Qstanje[8];
mind[232]:=Qstanje[9];
mind[233]:=UPS[1].InverterStatus;
mind[234]:=UPS[1].OutputStatus;
mind[235]:=UPS[1].StatusBaterije;
mind[236]:=UPS[1].SteviloIzpadovVhodneLinije;
mind[237]:=UPS[1].UnitStatus;
mind[238]:=UPS[2].InverterStatus;
mind[239]:=UPS[2].OutputStatus;
mind[240]:=UPS[2].StatusBaterije;
mind[241]:=UPS[2].SteviloIzpadovVhodneLinije;
mind[242]:=UPS[2].UnitStatus;
mind[243]:=UserCurrentLevel;
(*Branje UINT*)
(**)
mind[6000]:=kom_nast_cas_izpada;
(*Branje LONG*)
(**)
(*Branje REAL*)
(**)
Read_Real(rVar:=Klima[1].ObratovalneUre,lo:=4000,hi:=4001);
Read_Real(rVar:=Klima[1].TemperaturaProstora,lo:=4002,hi:=4003);
Read_Real(rVar:=Klima[1].TempIzpihanegaZraka,lo:=4004,hi:=4005);
Read_Real(rVar:=Klima[1].VlaznostProstora,lo:=4006,hi:=4007);
Read_Real(rVar:=Klima[1].ZunanjaTemp,lo:=4008,hi:=4009);
Read_Real(rVar:=Klima[2].ObratovalneUre,lo:=4010,hi:=4011);
Read_Real(rVar:=Klima[2].TemperaturaProstora,lo:=4012,hi:=4013);
Read_Real(rVar:=Klima[2].TempIzpihanegaZraka,lo:=4014,hi:=4015);
Read_Real(rVar:=Klima[2].VlaznostProstora,lo:=4016,hi:=4017);
Read_Real(rVar:=Klima[2].ZunanjaTemp,lo:=4018,hi:=4019);
Read_Real(rVar:=Klima[3].ObratovalneUre,lo:=4020,hi:=4021);
Read_Real(rVar:=Klima[3].TemperaturaProstora,lo:=4022,hi:=4023);
Read_Real(rVar:=Klima[3].TempIzpihanegaZraka,lo:=4024,hi:=4025);
Read_Real(rVar:=Klima[3].VlaznostProstora,lo:=4026,hi:=4027);
Read_Real(rVar:=Klima[3].ZunanjaTemp,lo:=4028,hi:=4029);
Read_Real(rVar:=Klima[4].ObratovalneUre,lo:=4030,hi:=4031);
Read_Real(rVar:=Klima[4].TemperaturaProstora,lo:=4032,hi:=4033);
Read_Real(rVar:=Klima[4].TempIzpihanegaZraka,lo:=4034,hi:=4035);
Read_Real(rVar:=Klima[4].VlaznostProstora,lo:=4036,hi:=4037);
Read_Real(rVar:=Klima[4].ZunanjaTemp,lo:=4038,hi:=4039);
Read_Real(rVar:=Klima[5].ObratovalneUre,lo:=4040,hi:=4041);
Read_Real(rVar:=Klima[5].TemperaturaProstora,lo:=4042,hi:=4043);
Read_Real(rVar:=Klima[5].TempIzpihanegaZraka,lo:=4044,hi:=4045);
Read_Real(rVar:=Klima[5].VlaznostProstora,lo:=4046,hi:=4047);
Read_Real(rVar:=Klima[5].ZunanjaTemp,lo:=4048,hi:=4049);
Read_Real(rVar:=Klima[6].ObratovalneUre,lo:=4050,hi:=4051);
Read_Real(rVar:=Klima[6].TemperaturaProstora,lo:=4052,hi:=4053);
Read_Real(rVar:=Klima[6].TempIzpihanegaZraka,lo:=4054,hi:=4055);
Read_Real(rVar:=Klima[6].VlaznostProstora,lo:=4056,hi:=4057);
Read_Real(rVar:=Klima[6].ZunanjaTemp,lo:=4058,hi:=4059);
Read_Real(rVar:=PMM.ActiveEnergyConsumed_kWh,lo:=4060,hi:=4061);
Read_Real(rVar:=PMM.ActivePowerPhaseA_kW,lo:=4062,hi:=4063);
Read_Real(rVar:=PMM.ActivePowerPhaseB_kW,lo:=4064,hi:=4065);
Read_Real(rVar:=PMM.ActivePowerPhaseC_kW,lo:=4066,hi:=4067);
Read_Real(rVar:=PMM.AparentPowerPhaseA,lo:=4068,hi:=4069);
Read_Real(rVar:=PMM.AparentPowerPhaseB,lo:=4070,hi:=4071);
Read_Real(rVar:=PMM.AparentPowerPhaseC,lo:=4072,hi:=4073);
Read_Real(rVar:=PMM.AverageCurrent_A,lo:=4074,hi:=4075);
Read_Real(rVar:=PMM.AveragePhaseToNeutral_V,lo:=4076,hi:=4077);
Read_Real(rVar:=PMM.AveragePhaseToPhase_V,lo:=4078,hi:=4079);
Read_Real(rVar:=PMM.CurrentInPhaseA_A,lo:=4080,hi:=4081);
Read_Real(rVar:=PMM.CurrentInPhaseB_A,lo:=4082,hi:=4083);
Read_Real(rVar:=PMM.CurrentInPhaseC_A,lo:=4084,hi:=4085);
Read_Real(rVar:=PMM.Frequency_Hz,lo:=4086,hi:=4087);
Read_Real(rVar:=PMM.Phase[1].Current[10],lo:=4088,hi:=4089);
Read_Real(rVar:=PMM.Phase[1].Current[11],lo:=4090,hi:=4091);
Read_Real(rVar:=PMM.Phase[1].Current[12],lo:=4092,hi:=4093);
Read_Real(rVar:=PMM.Phase[1].Current[13],lo:=4094,hi:=4095);
Read_Real(rVar:=PMM.Phase[1].Current[14],lo:=4096,hi:=4097);
Read_Real(rVar:=PMM.Phase[1].Current[15],lo:=4098,hi:=4099);
Read_Real(rVar:=PMM.Phase[1].Current[16],lo:=4100,hi:=4101);
Read_Real(rVar:=PMM.Phase[1].Current[17],lo:=4102,hi:=4103);
Read_Real(rVar:=PMM.Phase[1].Current[18],lo:=4104,hi:=4105);
Read_Real(rVar:=PMM.Phase[1].Current[19],lo:=4106,hi:=4107);
Read_Real(rVar:=PMM.Phase[1].Current[1],lo:=4108,hi:=4109);
Read_Real(rVar:=PMM.Phase[1].Current[20],lo:=4110,hi:=4111);
Read_Real(rVar:=PMM.Phase[1].Current[21],lo:=4112,hi:=4113);
Read_Real(rVar:=PMM.Phase[1].Current[22],lo:=4114,hi:=4115);
Read_Real(rVar:=PMM.Phase[1].Current[23],lo:=4116,hi:=4117);
Read_Real(rVar:=PMM.Phase[1].Current[24],lo:=4118,hi:=4119);
Read_Real(rVar:=PMM.Phase[1].Current[25],lo:=4120,hi:=4121);
Read_Real(rVar:=PMM.Phase[1].Current[26],lo:=4122,hi:=4123);
Read_Real(rVar:=PMM.Phase[1].Current[27],lo:=4124,hi:=4125);
Read_Real(rVar:=PMM.Phase[1].Current[28],lo:=4126,hi:=4127);
Read_Real(rVar:=PMM.Phase[1].Current[29],lo:=4128,hi:=4129);
Read_Real(rVar:=PMM.Phase[1].Current[2],lo:=4130,hi:=4131);
Read_Real(rVar:=PMM.Phase[1].Current[30],lo:=4132,hi:=4133);
Read_Real(rVar:=PMM.Phase[1].Current[31],lo:=4134,hi:=4135);
Read_Real(rVar:=PMM.Phase[1].Current[32],lo:=4136,hi:=4137);
Read_Real(rVar:=PMM.Phase[1].Current[33],lo:=4138,hi:=4139);
Read_Real(rVar:=PMM.Phase[1].Current[34],lo:=4140,hi:=4141);
Read_Real(rVar:=PMM.Phase[1].Current[35],lo:=4142,hi:=4143);
Read_Real(rVar:=PMM.Phase[1].Current[36],lo:=4144,hi:=4145);
Read_Real(rVar:=PMM.Phase[1].Current[37],lo:=4146,hi:=4147);
Read_Real(rVar:=PMM.Phase[1].Current[38],lo:=4148,hi:=4149);
Read_Real(rVar:=PMM.Phase[1].Current[39],lo:=4150,hi:=4151);
Read_Real(rVar:=PMM.Phase[1].Current[3],lo:=4152,hi:=4153);
Read_Real(rVar:=PMM.Phase[1].Current[40],lo:=4154,hi:=4155);
Read_Real(rVar:=PMM.Phase[1].Current[41],lo:=4156,hi:=4157);
Read_Real(rVar:=PMM.Phase[1].Current[42],lo:=4158,hi:=4159);
Read_Real(rVar:=PMM.Phase[1].Current[4],lo:=4160,hi:=4161);
Read_Real(rVar:=PMM.Phase[1].Current[5],lo:=4162,hi:=4163);
Read_Real(rVar:=PMM.Phase[1].Current[6],lo:=4164,hi:=4165);
Read_Real(rVar:=PMM.Phase[1].Current[7],lo:=4166,hi:=4167);
Read_Real(rVar:=PMM.Phase[1].Current[8],lo:=4168,hi:=4169);
Read_Real(rVar:=PMM.Phase[1].Current[9],lo:=4170,hi:=4171);
Read_Real(rVar:=PMM.Phase[2].Current[10],lo:=4172,hi:=4173);
Read_Real(rVar:=PMM.Phase[2].Current[11],lo:=4174,hi:=4175);
Read_Real(rVar:=PMM.Phase[2].Current[12],lo:=4176,hi:=4177);
Read_Real(rVar:=PMM.Phase[2].Current[13],lo:=4178,hi:=4179);
Read_Real(rVar:=PMM.Phase[2].Current[14],lo:=4180,hi:=4181);
Read_Real(rVar:=PMM.Phase[2].Current[15],lo:=4182,hi:=4183);
Read_Real(rVar:=PMM.Phase[2].Current[16],lo:=4184,hi:=4185);
Read_Real(rVar:=PMM.Phase[2].Current[17],lo:=4186,hi:=4187);
Read_Real(rVar:=PMM.Phase[2].Current[18],lo:=4188,hi:=4189);
Read_Real(rVar:=PMM.Phase[2].Current[19],lo:=4190,hi:=4191);
Read_Real(rVar:=PMM.Phase[2].Current[1],lo:=4192,hi:=4193);
Read_Real(rVar:=PMM.Phase[2].Current[20],lo:=4194,hi:=4195);
Read_Real(rVar:=PMM.Phase[2].Current[21],lo:=4196,hi:=4197);
Read_Real(rVar:=PMM.Phase[2].Current[22],lo:=4198,hi:=4199);
Read_Real(rVar:=PMM.Phase[2].Current[23],lo:=4200,hi:=4201);
Read_Real(rVar:=PMM.Phase[2].Current[24],lo:=4202,hi:=4203);
Read_Real(rVar:=PMM.Phase[2].Current[25],lo:=4204,hi:=4205);
Read_Real(rVar:=PMM.Phase[2].Current[26],lo:=4206,hi:=4207);
Read_Real(rVar:=PMM.Phase[2].Current[27],lo:=4208,hi:=4209);
Read_Real(rVar:=PMM.Phase[2].Current[28],lo:=4210,hi:=4211);
Read_Real(rVar:=PMM.Phase[2].Current[29],lo:=4212,hi:=4213);
Read_Real(rVar:=PMM.Phase[2].Current[2],lo:=4214,hi:=4215);
Read_Real(rVar:=PMM.Phase[2].Current[30],lo:=4216,hi:=4217);
Read_Real(rVar:=PMM.Phase[2].Current[31],lo:=4218,hi:=4219);
Read_Real(rVar:=PMM.Phase[2].Current[32],lo:=4220,hi:=4221);
Read_Real(rVar:=PMM.Phase[2].Current[33],lo:=4222,hi:=4223);
Read_Real(rVar:=PMM.Phase[2].Current[34],lo:=4224,hi:=4225);
Read_Real(rVar:=PMM.Phase[2].Current[35],lo:=4226,hi:=4227);
Read_Real(rVar:=PMM.Phase[2].Current[36],lo:=4228,hi:=4229);
Read_Real(rVar:=PMM.Phase[2].Current[37],lo:=4230,hi:=4231);
Read_Real(rVar:=PMM.Phase[2].Current[38],lo:=4232,hi:=4233);
Read_Real(rVar:=PMM.Phase[2].Current[39],lo:=4234,hi:=4235);
Read_Real(rVar:=PMM.Phase[2].Current[3],lo:=4236,hi:=4237);
Read_Real(rVar:=PMM.Phase[2].Current[40],lo:=4238,hi:=4239);
Read_Real(rVar:=PMM.Phase[2].Current[41],lo:=4240,hi:=4241);
Read_Real(rVar:=PMM.Phase[2].Current[42],lo:=4242,hi:=4243);
Read_Real(rVar:=PMM.Phase[2].Current[4],lo:=4244,hi:=4245);
Read_Real(rVar:=PMM.Phase[2].Current[5],lo:=4246,hi:=4247);
Read_Real(rVar:=PMM.Phase[2].Current[6],lo:=4248,hi:=4249);
Read_Real(rVar:=PMM.Phase[2].Current[7],lo:=4250,hi:=4251);
Read_Real(rVar:=PMM.Phase[2].Current[8],lo:=4252,hi:=4253);
Read_Real(rVar:=PMM.Phase[2].Current[9],lo:=4254,hi:=4255);
Read_Real(rVar:=PMM.Phase[3].Current[10],lo:=4256,hi:=4257);
Read_Real(rVar:=PMM.Phase[3].Current[11],lo:=4258,hi:=4259);
Read_Real(rVar:=PMM.Phase[3].Current[12],lo:=4260,hi:=4261);
Read_Real(rVar:=PMM.Phase[3].Current[13],lo:=4262,hi:=4263);
Read_Real(rVar:=PMM.Phase[3].Current[14],lo:=4264,hi:=4265);
Read_Real(rVar:=PMM.Phase[3].Current[15],lo:=4266,hi:=4267);
Read_Real(rVar:=PMM.Phase[3].Current[16],lo:=4268,hi:=4269);
Read_Real(rVar:=PMM.Phase[3].Current[17],lo:=4270,hi:=4271);
Read_Real(rVar:=PMM.Phase[3].Current[18],lo:=4272,hi:=4273);
Read_Real(rVar:=PMM.Phase[3].Current[19],lo:=4274,hi:=4275);
Read_Real(rVar:=PMM.Phase[3].Current[1],lo:=4276,hi:=4277);
Read_Real(rVar:=PMM.Phase[3].Current[20],lo:=4278,hi:=4279);
Read_Real(rVar:=PMM.Phase[3].Current[21],lo:=4280,hi:=4281);
Read_Real(rVar:=PMM.Phase[3].Current[22],lo:=4282,hi:=4283);
Read_Real(rVar:=PMM.Phase[3].Current[23],lo:=4284,hi:=4285);
Read_Real(rVar:=PMM.Phase[3].Current[24],lo:=4286,hi:=4287);
Read_Real(rVar:=PMM.Phase[3].Current[25],lo:=4288,hi:=4289);
Read_Real(rVar:=PMM.Phase[3].Current[26],lo:=4290,hi:=4291);
Read_Real(rVar:=PMM.Phase[3].Current[27],lo:=4292,hi:=4293);
Read_Real(rVar:=PMM.Phase[3].Current[28],lo:=4294,hi:=4295);
Read_Real(rVar:=PMM.Phase[3].Current[29],lo:=4296,hi:=4297);
Read_Real(rVar:=PMM.Phase[3].Current[2],lo:=4298,hi:=4299);
Read_Real(rVar:=PMM.Phase[3].Current[30],lo:=4300,hi:=4301);
Read_Real(rVar:=PMM.Phase[3].Current[31],lo:=4302,hi:=4303);
Read_Real(rVar:=PMM.Phase[3].Current[32],lo:=4304,hi:=4305);
Read_Real(rVar:=PMM.Phase[3].Current[33],lo:=4306,hi:=4307);
Read_Real(rVar:=PMM.Phase[3].Current[34],lo:=4308,hi:=4309);
Read_Real(rVar:=PMM.Phase[3].Current[35],lo:=4310,hi:=4311);
Read_Real(rVar:=PMM.Phase[3].Current[36],lo:=4312,hi:=4313);
Read_Real(rVar:=PMM.Phase[3].Current[37],lo:=4314,hi:=4315);
Read_Real(rVar:=PMM.Phase[3].Current[38],lo:=4316,hi:=4317);
Read_Real(rVar:=PMM.Phase[3].Current[39],lo:=4318,hi:=4319);
Read_Real(rVar:=PMM.Phase[3].Current[3],lo:=4320,hi:=4321);
Read_Real(rVar:=PMM.Phase[3].Current[40],lo:=4322,hi:=4323);
Read_Real(rVar:=PMM.Phase[3].Current[41],lo:=4324,hi:=4325);
Read_Real(rVar:=PMM.Phase[3].Current[42],lo:=4326,hi:=4327);
Read_Real(rVar:=PMM.Phase[3].Current[4],lo:=4328,hi:=4329);
Read_Real(rVar:=PMM.Phase[3].Current[5],lo:=4330,hi:=4331);
Read_Real(rVar:=PMM.Phase[3].Current[6],lo:=4332,hi:=4333);
Read_Real(rVar:=PMM.Phase[3].Current[7],lo:=4334,hi:=4335);
Read_Real(rVar:=PMM.Phase[3].Current[8],lo:=4336,hi:=4337);
Read_Real(rVar:=PMM.Phase[3].Current[9],lo:=4338,hi:=4339);
Read_Real(rVar:=PMM.PowerFactorSys,lo:=4340,hi:=4341);
Read_Real(rVar:=PMM.ReactiveEnergyConsumed_kVARh,lo:=4342,hi:=4343);
Read_Real(rVar:=PMM.ReactivePowerPhaseA,lo:=4344,hi:=4345);
Read_Real(rVar:=PMM.ReactivePowerPhaseB,lo:=4346,hi:=4347);
Read_Real(rVar:=PMM.ReactivePowerPhaseC,lo:=4348,hi:=4349);
Read_Real(rVar:=PMM.TotalActivePower_kW,lo:=4350,hi:=4351);
Read_Real(rVar:=PMM.TotalAparentPower_kVA,lo:=4352,hi:=4353);
Read_Real(rVar:=PMM.TotalPowerFactor,lo:=4354,hi:=4355);
Read_Real(rVar:=PMM.TotalReactivePower_kVAR,lo:=4356,hi:=4357);
Read_Real(rVar:=PMM.VirA_fsys,lo:=4358,hi:=4359);
Read_Real(rVar:=PMM.VirA_Isys,lo:=4360,hi:=4361);
Read_Real(rVar:=PMM.VirA_PFsys,lo:=4362,hi:=4363);
Read_Real(rVar:=PMM.VirA_Psys,lo:=4364,hi:=4365);
Read_Real(rVar:=PMM.VirA_Qsys,lo:=4366,hi:=4367);
Read_Real(rVar:=PMM.VirA_Ssys,lo:=4368,hi:=4369);
Read_Real(rVar:=PMM.VirA_Usys,lo:=4370,hi:=4371);
Read_Real(rVar:=PMM.VirB_fsys,lo:=4372,hi:=4373);
Read_Real(rVar:=PMM.VirB_Isys,lo:=4374,hi:=4375);
Read_Real(rVar:=PMM.VirB_PFsys,lo:=4376,hi:=4377);
Read_Real(rVar:=PMM.VirB_Psys,lo:=4378,hi:=4379);
Read_Real(rVar:=PMM.VirB_Qsys,lo:=4380,hi:=4381);
Read_Real(rVar:=PMM.VirB_Ssys,lo:=4382,hi:=4383);
Read_Real(rVar:=PMM.VirB_Usys,lo:=4384,hi:=4385);
Read_Real(rVar:=PMM.VirBActiveEnergyConsumed_kWh,lo:=4386,hi:=4387);
Read_Real(rVar:=PMM.VirBActivePowerPhaseA_kW,lo:=4388,hi:=4389);
Read_Real(rVar:=PMM.VirBActivePowerPhaseB_kW,lo:=4390,hi:=4391);
Read_Real(rVar:=PMM.VirBActivePowerPhaseC_kW,lo:=4392,hi:=4393);
Read_Real(rVar:=PMM.VirBAparentPowerPhaseA,lo:=4394,hi:=4395);
Read_Real(rVar:=PMM.VirBAparentPowerPhaseB,lo:=4396,hi:=4397);
Read_Real(rVar:=PMM.VirBAparentPowerPhaseC,lo:=4398,hi:=4399);
Read_Real(rVar:=PMM.VirBAverageCurrent_A,lo:=4400,hi:=4401);
Read_Real(rVar:=PMM.VirBAveragePhaseToNeutral_V,lo:=4402,hi:=4403);
Read_Real(rVar:=PMM.VirBAveragePhaseToPhase_V,lo:=4404,hi:=4405);
Read_Real(rVar:=PMM.VirBCurrentInPhaseA_A,lo:=4406,hi:=4407);
Read_Real(rVar:=PMM.VirBCurrentInPhaseB_A,lo:=4408,hi:=4409);
Read_Real(rVar:=PMM.VirBCurrentInPhaseC_A,lo:=4410,hi:=4411);
Read_Real(rVar:=PMM.VirBFrequency_Hz,lo:=4412,hi:=4413);
Read_Real(rVar:=PMM.VirBPowerFactorSys,lo:=4414,hi:=4415);
Read_Real(rVar:=PMM.VirBReactiveEnergyConsumed_kVARh,lo:=4416,hi:=4417);
Read_Real(rVar:=PMM.VirBReactivePowerPhaseA,lo:=4418,hi:=4419);
Read_Real(rVar:=PMM.VirBReactivePowerPhaseB,lo:=4420,hi:=4421);
Read_Real(rVar:=PMM.VirBReactivePowerPhaseC,lo:=4422,hi:=4423);
Read_Real(rVar:=PMM.VirBTotalActivePower_kW,lo:=4424,hi:=4425);
Read_Real(rVar:=PMM.VirBTotalAparentPower_kVA,lo:=4426,hi:=4427);
Read_Real(rVar:=PMM.VirBTotalPowerFactor,lo:=4428,hi:=4429);
Read_Real(rVar:=PMM.VirBTotalReactivePower_kVAR,lo:=4430,hi:=4431);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseAB_V,lo:=4432,hi:=4433);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseAN_V,lo:=4434,hi:=4435);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseBC_V,lo:=4436,hi:=4437);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseBN_V,lo:=4438,hi:=4439);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseCA_V,lo:=4440,hi:=4441);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseCN_V,lo:=4442,hi:=4443);
Read_Real(rVar:=PMM.VoltageBetweenPhaseAB_V,lo:=4444,hi:=4445);
Read_Real(rVar:=PMM.VoltageBetweenPhaseAN_V,lo:=4446,hi:=4447);
Read_Real(rVar:=PMM.VoltageBetweenPhaseBC_V,lo:=4448,hi:=4449);
Read_Real(rVar:=PMM.VoltageBetweenPhaseBN_V,lo:=4450,hi:=4451);
Read_Real(rVar:=PMM.VoltageBetweenPhaseCA_V,lo:=4452,hi:=4453);
Read_Real(rVar:=PMM.VoltageBetweenPhaseCN_V,lo:=4454,hi:=4455);
Read_Real(rVar:=PMMfaza01,lo:=4456,hi:=4457);
Read_Real(rVar:=PMMfaza02,lo:=4458,hi:=4459);
Read_Real(rVar:=PMMfaza03,lo:=4460,hi:=4461);
Read_Real(rVar:=PMMfaza04,lo:=4462,hi:=4463);
Read_Real(rVar:=PMMfaza05,lo:=4464,hi:=4465);
Read_Real(rVar:=PMMfaza06,lo:=4466,hi:=4467);
Read_Real(rVar:=PMMfaza07,lo:=4468,hi:=4469);
Read_Real(rVar:=PMMfaza08,lo:=4470,hi:=4471);
Read_Real(rVar:=PMMfaza09,lo:=4472,hi:=4473);
Read_Real(rVar:=PMMfaza10,lo:=4474,hi:=4475);
Read_Real(rVar:=PMMfaza11,lo:=4476,hi:=4477);
Read_Real(rVar:=PMMfaza12,lo:=4478,hi:=4479);
Read_Real(rVar:=PMMfaza13,lo:=4480,hi:=4481);
Read_Real(rVar:=PMMfaza14,lo:=4482,hi:=4483);
Read_Real(rVar:=PMMfaza15,lo:=4484,hi:=4485);
Read_Real(rVar:=PMMfaza16,lo:=4486,hi:=4487);
Read_Real(rVar:=PMMfaza17,lo:=4488,hi:=4489);
Read_Real(rVar:=PMMfaza18,lo:=4490,hi:=4491);
Read_Real(rVar:=PMMfaza19,lo:=4492,hi:=4493);
Read_Real(rVar:=PMMfaza20,lo:=4494,hi:=4495);
Read_Real(rVar:=PMMfaza21,lo:=4496,hi:=4497);
Read_Real(rVar:=PMMfaza22,lo:=4498,hi:=4499);
Read_Real(rVar:=PMMfaza23,lo:=4500,hi:=4501);
Read_Real(rVar:=PMMfaza24,lo:=4502,hi:=4503);
Read_Real(rVar:=PMMfaza25,lo:=4504,hi:=4505);
Read_Real(rVar:=PMMfaza26,lo:=4506,hi:=4507);
Read_Real(rVar:=PMMfaza27,lo:=4508,hi:=4509);
Read_Real(rVar:=PMMfaza28,lo:=4510,hi:=4511);
Read_Real(rVar:=PMMfaza29,lo:=4512,hi:=4513);
Read_Real(rVar:=PMMfaza30,lo:=4514,hi:=4515);
Read_Real(rVar:=PMMfaza31,lo:=4516,hi:=4517);
Read_Real(rVar:=PMMfaza32,lo:=4518,hi:=4519);
Read_Real(rVar:=PMMfaza33,lo:=4520,hi:=4521);
Read_Real(rVar:=PMMfaza34,lo:=4522,hi:=4523);
Read_Real(rVar:=PMMfaza35,lo:=4524,hi:=4525);
Read_Real(rVar:=PMMfaza36,lo:=4526,hi:=4527);
Read_Real(rVar:=PMMfaza37,lo:=4528,hi:=4529);
Read_Real(rVar:=PMMfaza38,lo:=4530,hi:=4531);
Read_Real(rVar:=PMMfaza39,lo:=4532,hi:=4533);
Read_Real(rVar:=PMMfaza40,lo:=4534,hi:=4535);
Read_Real(rVar:=PMMfaza41,lo:=4536,hi:=4537);
Read_Real(rVar:=PMMfaza42,lo:=4538,hi:=4539);
Read_Real(rVar:=PMMfaza60[10],lo:=4540,hi:=4541);
Read_Real(rVar:=PMMfaza60[11],lo:=4542,hi:=4543);
Read_Real(rVar:=PMMfaza60[12],lo:=4544,hi:=4545);
Read_Real(rVar:=PMMfaza60[13],lo:=4546,hi:=4547);
Read_Real(rVar:=PMMfaza60[14],lo:=4548,hi:=4549);
Read_Real(rVar:=PMMfaza60[15],lo:=4550,hi:=4551);
Read_Real(rVar:=PMMfaza60[16],lo:=4552,hi:=4553);
Read_Real(rVar:=PMMfaza60[17],lo:=4554,hi:=4555);
Read_Real(rVar:=PMMfaza60[18],lo:=4556,hi:=4557);
Read_Real(rVar:=PMMfaza60[19],lo:=4558,hi:=4559);
Read_Real(rVar:=PMMfaza60[1],lo:=4560,hi:=4561);
Read_Real(rVar:=PMMfaza60[20],lo:=4562,hi:=4563);
Read_Real(rVar:=PMMfaza60[21],lo:=4564,hi:=4565);
Read_Real(rVar:=PMMfaza60[22],lo:=4566,hi:=4567);
Read_Real(rVar:=PMMfaza60[23],lo:=4568,hi:=4569);
Read_Real(rVar:=PMMfaza60[24],lo:=4570,hi:=4571);
Read_Real(rVar:=PMMfaza60[25],lo:=4572,hi:=4573);
Read_Real(rVar:=PMMfaza60[26],lo:=4574,hi:=4575);
Read_Real(rVar:=PMMfaza60[27],lo:=4576,hi:=4577);
Read_Real(rVar:=PMMfaza60[28],lo:=4578,hi:=4579);
Read_Real(rVar:=PMMfaza60[29],lo:=4580,hi:=4581);
Read_Real(rVar:=PMMfaza60[2],lo:=4582,hi:=4583);
Read_Real(rVar:=PMMfaza60[30],lo:=4584,hi:=4585);
Read_Real(rVar:=PMMfaza60[31],lo:=4586,hi:=4587);
Read_Real(rVar:=PMMfaza60[32],lo:=4588,hi:=4589);
Read_Real(rVar:=PMMfaza60[33],lo:=4590,hi:=4591);
Read_Real(rVar:=PMMfaza60[34],lo:=4592,hi:=4593);
Read_Real(rVar:=PMMfaza60[35],lo:=4594,hi:=4595);
Read_Real(rVar:=PMMfaza60[36],lo:=4596,hi:=4597);
Read_Real(rVar:=PMMfaza60[37],lo:=4598,hi:=4599);
Read_Real(rVar:=PMMfaza60[38],lo:=4600,hi:=4601);
Read_Real(rVar:=PMMfaza60[39],lo:=4602,hi:=4603);
Read_Real(rVar:=PMMfaza60[3],lo:=4604,hi:=4605);
Read_Real(rVar:=PMMfaza60[40],lo:=4606,hi:=4607);
Read_Real(rVar:=PMMfaza60[41],lo:=4608,hi:=4609);
Read_Real(rVar:=PMMfaza60[42],lo:=4610,hi:=4611);
Read_Real(rVar:=PMMfaza60[4],lo:=4612,hi:=4613);
Read_Real(rVar:=PMMfaza60[5],lo:=4614,hi:=4615);
Read_Real(rVar:=PMMfaza60[6],lo:=4616,hi:=4617);
Read_Real(rVar:=PMMfaza60[7],lo:=4618,hi:=4619);
Read_Real(rVar:=PMMfaza60[8],lo:=4620,hi:=4621);
Read_Real(rVar:=PMMfaza60[9],lo:=4622,hi:=4623);
Read_Real(rVar:=PMMfaza80[10],lo:=4624,hi:=4625);
Read_Real(rVar:=PMMfaza80[11],lo:=4626,hi:=4627);
Read_Real(rVar:=PMMfaza80[12],lo:=4628,hi:=4629);
Read_Real(rVar:=PMMfaza80[13],lo:=4630,hi:=4631);
Read_Real(rVar:=PMMfaza80[14],lo:=4632,hi:=4633);
Read_Real(rVar:=PMMfaza80[15],lo:=4634,hi:=4635);
Read_Real(rVar:=PMMfaza80[16],lo:=4636,hi:=4637);
Read_Real(rVar:=PMMfaza80[17],lo:=4638,hi:=4639);
Read_Real(rVar:=PMMfaza80[18],lo:=4640,hi:=4641);
Read_Real(rVar:=PMMfaza80[19],lo:=4642,hi:=4643);
Read_Real(rVar:=PMMfaza80[1],lo:=4644,hi:=4645);
Read_Real(rVar:=PMMfaza80[20],lo:=4646,hi:=4647);
Read_Real(rVar:=PMMfaza80[21],lo:=4648,hi:=4649);
Read_Real(rVar:=PMMfaza80[22],lo:=4650,hi:=4651);
Read_Real(rVar:=PMMfaza80[23],lo:=4652,hi:=4653);
Read_Real(rVar:=PMMfaza80[24],lo:=4654,hi:=4655);
Read_Real(rVar:=PMMfaza80[25],lo:=4656,hi:=4657);
Read_Real(rVar:=PMMfaza80[26],lo:=4658,hi:=4659);
Read_Real(rVar:=PMMfaza80[27],lo:=4660,hi:=4661);
Read_Real(rVar:=PMMfaza80[28],lo:=4662,hi:=4663);
Read_Real(rVar:=PMMfaza80[29],lo:=4664,hi:=4665);
Read_Real(rVar:=PMMfaza80[2],lo:=4666,hi:=4667);
Read_Real(rVar:=PMMfaza80[30],lo:=4668,hi:=4669);
Read_Real(rVar:=PMMfaza80[31],lo:=4670,hi:=4671);
Read_Real(rVar:=PMMfaza80[32],lo:=4672,hi:=4673);
Read_Real(rVar:=PMMfaza80[33],lo:=4674,hi:=4675);
Read_Real(rVar:=PMMfaza80[34],lo:=4676,hi:=4677);
Read_Real(rVar:=PMMfaza80[35],lo:=4678,hi:=4679);
Read_Real(rVar:=PMMfaza80[36],lo:=4680,hi:=4681);
Read_Real(rVar:=PMMfaza80[37],lo:=4682,hi:=4683);
Read_Real(rVar:=PMMfaza80[38],lo:=4684,hi:=4685);
Read_Real(rVar:=PMMfaza80[39],lo:=4686,hi:=4687);
Read_Real(rVar:=PMMfaza80[3],lo:=4688,hi:=4689);
Read_Real(rVar:=PMMfaza80[40],lo:=4690,hi:=4691);
Read_Real(rVar:=PMMfaza80[41],lo:=4692,hi:=4693);
Read_Real(rVar:=PMMfaza80[42],lo:=4694,hi:=4695);
Read_Real(rVar:=PMMfaza80[4],lo:=4696,hi:=4697);
Read_Real(rVar:=PMMfaza80[5],lo:=4698,hi:=4699);
Read_Real(rVar:=PMMfaza80[6],lo:=4700,hi:=4701);
Read_Real(rVar:=PMMfaza80[7],lo:=4702,hi:=4703);
Read_Real(rVar:=PMMfaza80[8],lo:=4704,hi:=4705);
Read_Real(rVar:=PMMfaza80[9],lo:=4706,hi:=4707);
Read_Real(rVar:=SenzorTemp[1],lo:=4708,hi:=4709);
Read_Real(rVar:=SenzorTemp[2],lo:=4710,hi:=4711);
Read_Real(rVar:=SenzorTemp[3],lo:=4712,hi:=4713);
Read_Real(rVar:=SenzorTemp[4],lo:=4714,hi:=4715);
Read_Real(rVar:=SenzorTemp[5],lo:=4716,hi:=4717);
Read_Real(rVar:=SenzorTemp[6],lo:=4718,hi:=4719);
Read_Real(rVar:=SenzorVlaga[1],lo:=4720,hi:=4721);
Read_Real(rVar:=SenzorVlaga[2],lo:=4722,hi:=4723);
Read_Real(rVar:=SenzorVlaga[3],lo:=4724,hi:=4725);
Read_Real(rVar:=SenzorVlaga[4],lo:=4726,hi:=4727);
Read_Real(rVar:=SenzorVlaga[5],lo:=4728,hi:=4729);
Read_Real(rVar:=SenzorVlaga[6],lo:=4730,hi:=4731);
Read_Real(rVar:=TempAlarmPoint[0],lo:=4732,hi:=4733);
Read_Real(rVar:=TempAlarmPoint[1],lo:=4734,hi:=4735);
Read_Real(rVar:=TempAlarmPoint[2],lo:=4736,hi:=4737);
Read_Real(rVar:=TempAlarmPoint[3],lo:=4738,hi:=4739);
Read_Real(rVar:=TempMaxPoint[0],lo:=4740,hi:=4741);
Read_Real(rVar:=TempMaxPoint[1],lo:=4742,hi:=4743);
Read_Real(rVar:=TempMaxPoint[2],lo:=4744,hi:=4745);
Read_Real(rVar:=TempMaxPoint[3],lo:=4746,hi:=4747);
Read_Real(rVar:=TempPovp[0],lo:=4748,hi:=4749);
Read_Real(rVar:=TempPovp[1],lo:=4750,hi:=4751);
Read_Real(rVar:=TempPovp[2],lo:=4752,hi:=4753);
Read_Real(rVar:=TempPovp[3],lo:=4754,hi:=4755);
Read_Real(rVar:=TempSetPoint[0],lo:=4756,hi:=4757);
Read_Real(rVar:=TempSetPoint[1],lo:=4758,hi:=4759);
Read_Real(rVar:=TempSetPoint[2],lo:=4760,hi:=4761);
Read_Real(rVar:=TempSetPoint[3],lo:=4762,hi:=4763);
Read_Real(rVar:=UPS[1].EstimatedChargeRemaining,lo:=4764,hi:=4765);
Read_Real(rVar:=UPS[1].EstimatedMinutesRemaining,lo:=4766,hi:=4767);
Read_Real(rVar:=UPS[1].IzhodMocL1,lo:=4768,hi:=4769);
Read_Real(rVar:=UPS[1].IzhodMocL2,lo:=4770,hi:=4771);
Read_Real(rVar:=UPS[1].IzhodMocL3,lo:=4772,hi:=4773);
Read_Real(rVar:=UPS[1].NapetostBaterije,lo:=4774,hi:=4775);
Read_Real(rVar:=UPS[1].TemperaturaBaterije,lo:=4776,hi:=4777);
Read_Real(rVar:=UPS[1].VhodFrekvencaL1,lo:=4778,hi:=4779);
Read_Real(rVar:=UPS[1].VhodFrekvencaL2,lo:=4780,hi:=4781);
Read_Real(rVar:=UPS[1].VhodFrekvencaL3,lo:=4782,hi:=4783);
Read_Real(rVar:=UPS[1].VhodNapetostL1,lo:=4784,hi:=4785);
Read_Real(rVar:=UPS[1].VhodNapetostL2,lo:=4786,hi:=4787);
Read_Real(rVar:=UPS[1].VhodNapetostL3,lo:=4788,hi:=4789);
Read_Real(rVar:=UPS[2].EstimatedChargeRemaining,lo:=4790,hi:=4791);
Read_Real(rVar:=UPS[2].EstimatedMinutesRemaining,lo:=4792,hi:=4793);
Read_Real(rVar:=UPS[2].IzhodMocL1,lo:=4794,hi:=4795);
Read_Real(rVar:=UPS[2].IzhodMocL2,lo:=4796,hi:=4797);
Read_Real(rVar:=UPS[2].IzhodMocL3,lo:=4798,hi:=4799);
Read_Real(rVar:=UPS[2].NapetostBaterije,lo:=4800,hi:=4801);
Read_Real(rVar:=UPS[2].TemperaturaBaterije,lo:=4802,hi:=4803);
Read_Real(rVar:=UPS[2].VhodFrekvencaL1,lo:=4804,hi:=4805);
Read_Real(rVar:=UPS[2].VhodFrekvencaL2,lo:=4806,hi:=4807);
Read_Real(rVar:=UPS[2].VhodFrekvencaL3,lo:=4808,hi:=4809);
Read_Real(rVar:=UPS[2].VhodNapetostL1,lo:=4810,hi:=4811);
Read_Real(rVar:=UPS[2].VhodNapetostL2,lo:=4812,hi:=4813);
Read_Real(rVar:=UPS[2].VhodNapetostL3,lo:=4814,hi:=4815);
Read_Real(rVar:=VlagaPovp[1],lo:=4816,hi:=4817);
Read_Real(rVar:=VlagaPovp[2],lo:=4818,hi:=4819);
Read_Real(rVar:=VlagaPovp[3],lo:=4820,hi:=4821);
Read_Real(rVar:=RazlikaUr,lo:=4822,hi:=4823);
Read_Real(rVar:=Klima[1].NastTempHlajenje,lo:=4824,hi:=4825);
Read_Real(rVar:=Klima[2].NastTempHlajenje,lo:=4826,hi:=4827);
Read_Real(rVar:=Klima[3].NastTempHlajenje,lo:=4828,hi:=4829);
Read_Real(rVar:=Klima[4].NastTempHlajenje,lo:=4830,hi:=4831);
Read_Real(rVar:=Klima[5].NastTempHlajenje,lo:=4832,hi:=4833);
Read_Real(rVar:=Klima[6].NastTempHlajenje,lo:=4834,hi:=4835);
Read_Real(rVar:=Klima[1].NastTempGretje,lo:=4836,hi:=4837);
Read_Real(rVar:=Klima[2].NastTempGretje,lo:=4838,hi:=4839);
Read_Real(rVar:=Klima[3].NastTempGretje,lo:=4840,hi:=4841);
Read_Real(rVar:=Klima[4].NastTempGretje,lo:=4842,hi:=4843);
Read_Real(rVar:=Klima[5].NastTempGretje,lo:=4844,hi:=4845);
Read_Real(rVar:=Klima[6].NastTempGretje,lo:=4846,hi:=4847);
Read_Real(rVar:=Klima[1].TempHladneVode,lo:=4848,hi:=4849);
Read_Real(rVar:=Klima[2].TempHladneVode,lo:=4850,hi:=4851);
Read_Real(rVar:=Klima[3].TempHladneVode,lo:=4852,hi:=4853);
Read_Real(rVar:=Klima[4].TempHladneVode,lo:=4854,hi:=4855);
Read_Real(rVar:=Klima[5].TempHladneVode,lo:=4856,hi:=4857);
Read_Real(rVar:=Klima[6].TempHladneVode,lo:=4858,hi:=4859);
Read_Real(rVar:=Klima[1].TempTopleVode,lo:=4860,hi:=4861);
Read_Real(rVar:=Klima[2].TempTopleVode,lo:=4862,hi:=4863);
Read_Real(rVar:=Klima[3].TempTopleVode,lo:=4864,hi:=4865);
Read_Real(rVar:=Klima[4].TempTopleVode,lo:=4866,hi:=4867);
Read_Real(rVar:=Klima[5].TempTopleVode,lo:=4868,hi:=4869);
Read_Real(rVar:=Klima[6].TempTopleVode,lo:=4870,hi:=4871);
Read_Real(rVar:=ZamikVklopa,lo:=4872,hi:=4873);
(*Branje STRING*)
(**)
Read_String(sVar:=Date_Time[0],start:=5000);
Read_String(sVar:=Date_Time[1],start:=5015);
Read_String(sVar:=Date_Time[2],start:=5030);
Read_String(sVar:=Date_Time[3],start:=5045);
Read_String(sVar:=UserCurrentName,start:=5060);
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Bool : BOOL
VAR_INPUT
index: INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje BOOL*)
(**)
0:AlarmGenComm:=Bit_0;
1:AlarmGenKlima[1]:=Bit_0;
2:AlarmGenKlima[2]:=Bit_0;
3:AlarmGenKlima[3]:=Bit_0;
4:AlarmGenKlima[4]:=Bit_0;
5:AlarmGenKlima[5]:=Bit_0;
6:AlarmGenKlima[6]:=Bit_0;
7:AlarmGenPMM:=Bit_0;
8:AlarmGenRest:=Bit_0;
9:AlarmGenSenzor:=Bit_0;
10:AlarmGenStikala:=Bit_0;
11:AlarmGenTemp:=Bit_0;
12:AlarmGenUPS1:=Bit_0;
13:AlarmGenUPS2:=Bit_0;
14:ComSCADA:=Bit_0;
15:ComSCADA1:=Bit_0;
16:DI_A1Q01_DovUpsA_ON:=Bit_0;
17:DI_A1Q02_DovByA_ON:=Bit_0;
18:DI_A1Q0_GlavnoSti_ON:=Bit_0;
19:DI_A1Q11_OdcUpsA_IZP:=Bit_0;
20:DI_A1Q11_OdcUpsA_ON:=Bit_0;
21:DI_A1Q12_OdcByUpsA_IZP:=Bit_0;
22:DI_A1Q12_OdcByUpsA_ON:=Bit_0;
23:DI_A1Q13_OdcByA_IZP:=Bit_0;
24:DI_A1Q13_OdcByA_ON:=Bit_0;
25:DI_A2Q0_GlavnoSti_ON:=Bit_0;
26:DI_F201_OdcKl1ZE_IZP:=Bit_0;
27:DI_F201_OdcKl1ZE_ON:=Bit_0;
28:DI_F202_OdcKl2ZE_IZP:=Bit_0;
29:DI_F202_OdcKl2ZE_ON:=Bit_0;
30:DI_F203_OdcKl3ZE_IZP:=Bit_0;
31:DI_F203_OdcKl3ZE_ON:=Bit_0;
32:DI_F204_OdcKl4ZE_IZP:=Bit_0;
33:DI_F204_OdcKl4ZE_ON:=Bit_0;
34:DI_F205_OdcKl5aZE_IZP:=Bit_0;
35:DI_F205_OdcKl5aZE_ON:=Bit_0;
36:DI_F206_OdcKl5bZE_IZP:=Bit_0;
37:DI_F206_OdcKl5bZE_ON:=Bit_0;
38:DI_F207_OdcKl6aZE_IZP:=Bit_0;
39:DI_F207_OdcKl6aZE_ON:=Bit_0;
40:DI_F208_OdcKl6bZE_IZP:=Bit_0;
41:DI_F208_OdcKl6bZE_ON:=Bit_0;
42:DI_IzpadMreze:=Bit_0;
43:DI_Klima1_ERR:=Bit_0;
44:DI_Klima1_ON:=Bit_0;
45:DI_Klima2_ERR:=Bit_0;
46:DI_Klima2_ON:=Bit_0;
47:DI_Klima3_ERR:=Bit_0;
48:DI_Klima3_ON:=Bit_0;
49:DI_Klima4_ERR:=Bit_0;
50:DI_Klima4_ON:=Bit_0;
51:DI_Klima5_ERR:=Bit_0;
52:DI_Klima5_ON:=Bit_0;
53:DI_Klima6_ERR:=Bit_0;
54:DI_Klima6_ON:=Bit_0;
55:DI_KlimaSplitPP_ERR:=Bit_0;
56:DI_KlimaSplitPP_ON:=Bit_0;
57:DI_PrenapA1_OK:=Bit_0;
58:DI_PrenapA2_OK:=Bit_0;
59:DI_Q101_OdcKlima1_IZP:=Bit_0;
60:DI_Q101_OdcKlima1_ON:=Bit_0;
61:DI_Q102_OdcKlima2_IZP:=Bit_0;
62:DI_Q102_OdcKlima2_ON:=Bit_0;
63:DI_Q103_OdcKlima3_IZP:=Bit_0;
64:DI_Q103_OdcKlima3_ON:=Bit_0;
65:DI_Q104_OdcKlima4_IZP:=Bit_0;
66:DI_Q104_OdcKlima4_ON:=Bit_0;
67:DI_Q105_OdcKlima5_IZP:=Bit_0;
68:DI_Q105_OdcKlima5_ON:=Bit_0;
69:DI_Q106_OdcKlima6_IZP:=Bit_0;
70:DI_Q106_OdcKlima6_ON:=Bit_0;
71:DI_Q107_OdcUsmSS2_IZP:=Bit_0;
72:DI_Q107_OdcUsmSS2_ON:=Bit_0;
73:DI_Q108_OdcUsmSS3_IZP:=Bit_0;
74:DI_Q108_OdcUsmSS3_ON:=Bit_0;
75:DI_RazlitjeVodeK1K2:=Bit_0;
76:DI_RazlitjeVodeK3K4:=Bit_0;
77:DI_RazlitjeVodeK5:=Bit_0;
78:DI_RazlitjeVodeK6:=Bit_0;
79:DI_UPS_Alarm:=Bit_0;
80:DI_UPS_BatNacin:=Bit_0;
81:DI_UPS_Polnjenje:=Bit_0;
82:DI_UpsA_BypassON:=Bit_0;
83:DI_UpsA_ERR:=Bit_0;
84:DI_UpsB_BypassON:=Bit_0;
85:DI_UpsB_ERR:=Bit_0;
86:DI_UQ11_OdcPMM_IZP:=Bit_0;
87:DI_UQ11_OdcPMM_ON:=Bit_0;
88:DI_UQ12_OdcPMM_IZP:=Bit_0;
89:DI_UQ12_OdcPMM_ON:=Bit_0;
90:DIN_A1Q11_OdcUpsA_IZP:=Bit_0;
91:DIN_A1Q12_OdcByUpsA_IZP:=Bit_0;
92:DIN_A1Q13_OdcByA_IZP:=Bit_0;
93:DIN_F201_OdcKl1ZE_IZP:=Bit_0;
94:DIN_F202_OdcKl2ZE_IZP:=Bit_0;
95:DIN_F203_OdcKl3ZE_IZP:=Bit_0;
96:DIN_F204_OdcKl4ZE_IZP:=Bit_0;
97:DIN_F205_OdcKl5aZE_IZP:=Bit_0;
98:DIN_F206_OdcKl5bZE_IZP:=Bit_0;
99:DIN_F207_OdcKl6aZE_IZP:=Bit_0;
100:DIN_F208_OdcKl6bZE_IZP:=Bit_0;
101:DIN_Klima1_ERR:=Bit_0;
102:DIN_Klima2_ERR:=Bit_0;
103:DIN_Klima3_ERR:=Bit_0;
104:DIN_Klima4_ERR:=Bit_0;
105:DIN_Klima5_ERR:=Bit_0;
106:DIN_Klima6_ERR:=Bit_0;
107:DIN_KlimaSplitPP_ERR:=Bit_0;
108:DIN_PrenapA1_OK:=Bit_0;
109:DIN_PrenapA2_OK:=Bit_0;
110:DIN_Q101_OdcKlima1_IZP:=Bit_0;
111:DIN_Q102_OdcKlima2_IZP:=Bit_0;
112:DIN_Q103_OdcKlima3_IZP:=Bit_0;
113:DIN_Q104_OdcKlima4_IZP:=Bit_0;
114:DIN_Q105_OdcKlima5_IZP:=Bit_0;
115:DIN_Q106_OdcKlima6_IZP:=Bit_0;
116:DIN_Q107_OdcUsmSS2_IZP:=Bit_0;
117:DIN_Q108_OdcUsmSS3_IZP:=Bit_0;
118:DIN_UpsA_BypassON:=Bit_0;
119:DIN_UpsA_ERR:=Bit_0;
120:DIN_UpsB_BypassON:=Bit_0;
121:DIN_UpsB_ERR:=Bit_0;
122:DIN_UQ11_OdcPMM_IZP:=Bit_0;
123:DIN_UQ12_OdcPMM_IZP:=Bit_0;
124:DO_Klima1_Izklop:=Bit_0;
125:DO_Klima2_Izklop:=Bit_0;
126:DO_Klima3_Izklop:=Bit_0;
127:DO_Klima4_Izklop:=Bit_0;
128:DO_Klima5_Izklop:=Bit_0;
129:DO_Klima6_Izklop:=Bit_0;
130:ErrComKlima[1]:=Bit_0;
131:ErrComKlima[2]:=Bit_0;
132:ErrComKlima[3]:=Bit_0;
133:ErrComKlima[4]:=Bit_0;
134:ErrComKlima[5]:=Bit_0;
135:ErrComKlima[6]:=Bit_0;
136:ErrCommScada:=Bit_0;
137:ErrComPanelPLC:=Bit_0;
138:ErrComPMM:=Bit_0;
139:ErrComPort2:=Bit_0;
140:ErrComPort3:=Bit_0;
141:ErrComPort4:=Bit_0;
142:ErrComUPS[1]:=Bit_0;
143:ErrComUPS[2]:=Bit_0;
144:ErrorComKlima[1].Error:=Bit_0;
145:ErrorComKlima[2].Error:=Bit_0;
146:ErrorComKlima[3].Error:=Bit_0;
147:ErrorComKlima[4].Error:=Bit_0;
148:ErrorComKlima[5].Error:=Bit_0;
149:ErrorComKlima[6].Error:=Bit_0;
150:ErrorComPMM.Error:=Bit_0;
151:ErrorComUPS[1].Error:=Bit_0;
152:ErrorComUPS[2].Error:=Bit_0;
153:Klima1Errors[10]:=Bit_0;
154:Klima1Errors[11]:=Bit_0;
155:Klima1Errors[12]:=Bit_0;
156:Klima1Errors[13]:=Bit_0;
157:Klima1Errors[14]:=Bit_0;
158:Klima1Errors[15]:=Bit_0;
159:Klima1Errors[16]:=Bit_0;
160:Klima1Errors[17]:=Bit_0;
161:Klima1Errors[18]:=Bit_0;
162:Klima1Errors[19]:=Bit_0;
163:Klima1Errors[1]:=Bit_0;
164:Klima1Errors[20]:=Bit_0;
165:Klima1Errors[21]:=Bit_0;
166:Klima1Errors[22]:=Bit_0;
167:Klima1Errors[23]:=Bit_0;
168:Klima1Errors[24]:=Bit_0;
169:Klima1Errors[25]:=Bit_0;
170:Klima1Errors[26]:=Bit_0;
171:Klima1Errors[27]:=Bit_0;
172:Klima1Errors[28]:=Bit_0;
173:Klima1Errors[29]:=Bit_0;
174:Klima1Errors[2]:=Bit_0;
175:Klima1Errors[30]:=Bit_0;
176:Klima1Errors[31]:=Bit_0;
177:Klima1Errors[32]:=Bit_0;
178:Klima1Errors[33]:=Bit_0;
179:Klima1Errors[34]:=Bit_0;
180:Klima1Errors[35]:=Bit_0;
181:Klima1Errors[3]:=Bit_0;
182:Klima1Errors[4]:=Bit_0;
183:Klima1Errors[5]:=Bit_0;
184:Klima1Errors[6]:=Bit_0;
185:Klima1Errors[7]:=Bit_0;
186:Klima1Errors[8]:=Bit_0;
187:Klima1Errors[9]:=Bit_0;
188:Klima2Errors[10]:=Bit_0;
189:Klima2Errors[11]:=Bit_0;
190:Klima2Errors[12]:=Bit_0;
191:Klima2Errors[13]:=Bit_0;
192:Klima2Errors[14]:=Bit_0;
193:Klima2Errors[15]:=Bit_0;
194:Klima2Errors[16]:=Bit_0;
195:Klima2Errors[17]:=Bit_0;
196:Klima2Errors[18]:=Bit_0;
197:Klima2Errors[19]:=Bit_0;
198:Klima2Errors[1]:=Bit_0;
199:Klima2Errors[20]:=Bit_0;
200:Klima2Errors[21]:=Bit_0;
201:Klima2Errors[22]:=Bit_0;
202:Klima2Errors[23]:=Bit_0;
203:Klima2Errors[24]:=Bit_0;
204:Klima2Errors[25]:=Bit_0;
205:Klima2Errors[26]:=Bit_0;
206:Klima2Errors[27]:=Bit_0;
207:Klima2Errors[28]:=Bit_0;
208:Klima2Errors[29]:=Bit_0;
209:Klima2Errors[2]:=Bit_0;
210:Klima2Errors[30]:=Bit_0;
211:Klima2Errors[31]:=Bit_0;
212:Klima2Errors[32]:=Bit_0;
213:Klima2Errors[33]:=Bit_0;
214:Klima2Errors[34]:=Bit_0;
215:Klima2Errors[35]:=Bit_0;
216:Klima2Errors[3]:=Bit_0;
217:Klima2Errors[4]:=Bit_0;
218:Klima2Errors[5]:=Bit_0;
219:Klima2Errors[6]:=Bit_0;
220:Klima2Errors[7]:=Bit_0;
221:Klima2Errors[8]:=Bit_0;
222:Klima2Errors[9]:=Bit_0;
223:Klima3Errors[10]:=Bit_0;
224:Klima3Errors[11]:=Bit_0;
225:Klima3Errors[12]:=Bit_0;
226:Klima3Errors[13]:=Bit_0;
227:Klima3Errors[14]:=Bit_0;
228:Klima3Errors[15]:=Bit_0;
229:Klima3Errors[16]:=Bit_0;
230:Klima3Errors[17]:=Bit_0;
231:Klima3Errors[18]:=Bit_0;
232:Klima3Errors[19]:=Bit_0;
233:Klima3Errors[1]:=Bit_0;
234:Klima3Errors[20]:=Bit_0;
235:Klima3Errors[21]:=Bit_0;
236:Klima3Errors[22]:=Bit_0;
237:Klima3Errors[23]:=Bit_0;
238:Klima3Errors[24]:=Bit_0;
239:Klima3Errors[25]:=Bit_0;
240:Klima3Errors[26]:=Bit_0;
241:Klima3Errors[27]:=Bit_0;
242:Klima3Errors[28]:=Bit_0;
243:Klima3Errors[29]:=Bit_0;
244:Klima3Errors[2]:=Bit_0;
245:Klima3Errors[30]:=Bit_0;
246:Klima3Errors[31]:=Bit_0;
247:Klima3Errors[32]:=Bit_0;
248:Klima3Errors[33]:=Bit_0;
249:Klima3Errors[34]:=Bit_0;
250:Klima3Errors[35]:=Bit_0;
251:Klima3Errors[3]:=Bit_0;
252:Klima3Errors[4]:=Bit_0;
253:Klima3Errors[5]:=Bit_0;
254:Klima3Errors[6]:=Bit_0;
255:Klima3Errors[7]:=Bit_0;
256:Klima3Errors[8]:=Bit_0;
257:Klima3Errors[9]:=Bit_0;
258:Klima4Errors[10]:=Bit_0;
259:Klima4Errors[11]:=Bit_0;
260:Klima4Errors[12]:=Bit_0;
261:Klima4Errors[13]:=Bit_0;
262:Klima4Errors[14]:=Bit_0;
263:Klima4Errors[15]:=Bit_0;
264:Klima4Errors[16]:=Bit_0;
265:Klima4Errors[17]:=Bit_0;
266:Klima4Errors[18]:=Bit_0;
267:Klima4Errors[19]:=Bit_0;
268:Klima4Errors[1]:=Bit_0;
269:Klima4Errors[20]:=Bit_0;
270:Klima4Errors[21]:=Bit_0;
271:Klima4Errors[22]:=Bit_0;
272:Klima4Errors[23]:=Bit_0;
273:Klima4Errors[24]:=Bit_0;
274:Klima4Errors[25]:=Bit_0;
275:Klima4Errors[26]:=Bit_0;
276:Klima4Errors[27]:=Bit_0;
277:Klima4Errors[28]:=Bit_0;
278:Klima4Errors[29]:=Bit_0;
279:Klima4Errors[2]:=Bit_0;
280:Klima4Errors[30]:=Bit_0;
281:Klima4Errors[31]:=Bit_0;
282:Klima4Errors[32]:=Bit_0;
283:Klima4Errors[33]:=Bit_0;
284:Klima4Errors[34]:=Bit_0;
285:Klima4Errors[35]:=Bit_0;
286:Klima4Errors[3]:=Bit_0;
287:Klima4Errors[4]:=Bit_0;
288:Klima4Errors[5]:=Bit_0;
289:Klima4Errors[6]:=Bit_0;
290:Klima4Errors[7]:=Bit_0;
291:Klima4Errors[8]:=Bit_0;
292:Klima4Errors[9]:=Bit_0;
293:Klima5Errors[10]:=Bit_0;
294:Klima5Errors[11]:=Bit_0;
295:Klima5Errors[12]:=Bit_0;
296:Klima5Errors[13]:=Bit_0;
297:Klima5Errors[14]:=Bit_0;
298:Klima5Errors[15]:=Bit_0;
299:Klima5Errors[16]:=Bit_0;
300:Klima5Errors[17]:=Bit_0;
301:Klima5Errors[18]:=Bit_0;
302:Klima5Errors[19]:=Bit_0;
303:Klima5Errors[1]:=Bit_0;
304:Klima5Errors[20]:=Bit_0;
305:Klima5Errors[21]:=Bit_0;
306:Klima5Errors[22]:=Bit_0;
307:Klima5Errors[23]:=Bit_0;
308:Klima5Errors[24]:=Bit_0;
309:Klima5Errors[25]:=Bit_0;
310:Klima5Errors[26]:=Bit_0;
311:Klima5Errors[27]:=Bit_0;
312:Klima5Errors[28]:=Bit_0;
313:Klima5Errors[29]:=Bit_0;
314:Klima5Errors[2]:=Bit_0;
315:Klima5Errors[30]:=Bit_0;
316:Klima5Errors[31]:=Bit_0;
317:Klima5Errors[32]:=Bit_0;
318:Klima5Errors[33]:=Bit_0;
319:Klima5Errors[34]:=Bit_0;
320:Klima5Errors[35]:=Bit_0;
321:Klima5Errors[3]:=Bit_0;
322:Klima5Errors[4]:=Bit_0;
323:Klima5Errors[5]:=Bit_0;
324:Klima5Errors[6]:=Bit_0;
325:Klima5Errors[7]:=Bit_0;
326:Klima5Errors[8]:=Bit_0;
327:Klima5Errors[9]:=Bit_0;
328:Klima6Errors[10]:=Bit_0;
329:Klima6Errors[11]:=Bit_0;
330:Klima6Errors[12]:=Bit_0;
331:Klima6Errors[13]:=Bit_0;
332:Klima6Errors[14]:=Bit_0;
333:Klima6Errors[15]:=Bit_0;
334:Klima6Errors[16]:=Bit_0;
335:Klima6Errors[17]:=Bit_0;
336:Klima6Errors[18]:=Bit_0;
337:Klima6Errors[19]:=Bit_0;
338:Klima6Errors[1]:=Bit_0;
339:Klima6Errors[20]:=Bit_0;
340:Klima6Errors[21]:=Bit_0;
341:Klima6Errors[22]:=Bit_0;
342:Klima6Errors[23]:=Bit_0;
343:Klima6Errors[24]:=Bit_0;
344:Klima6Errors[25]:=Bit_0;
345:Klima6Errors[26]:=Bit_0;
346:Klima6Errors[27]:=Bit_0;
347:Klima6Errors[28]:=Bit_0;
348:Klima6Errors[29]:=Bit_0;
349:Klima6Errors[2]:=Bit_0;
350:Klima6Errors[30]:=Bit_0;
351:Klima6Errors[31]:=Bit_0;
352:Klima6Errors[32]:=Bit_0;
353:Klima6Errors[33]:=Bit_0;
354:Klima6Errors[34]:=Bit_0;
355:Klima6Errors[35]:=Bit_0;
356:Klima6Errors[3]:=Bit_0;
357:Klima6Errors[4]:=Bit_0;
358:Klima6Errors[5]:=Bit_0;
359:Klima6Errors[6]:=Bit_0;
360:Klima6Errors[7]:=Bit_0;
361:Klima6Errors[8]:=Bit_0;
362:Klima6Errors[9]:=Bit_0;
363:Klima[1].Deluje:=Bit_0;
364:Klima[1].FenThermalCutout:=Bit_0;
365:Klima[1].GeneralAlarm:=Bit_0;
366:Klima[1].Kompresor1naMejiObrUr:=Bit_0;
367:Klima[1].Kompresor2naMejiObrUr:=Bit_0;
368:Klima[1].Napaka:=Bit_0;
369:Klima[1].NapakaPriPretokuZraka:=Bit_0;
370:Klima[1].NapakaSenzorTempIzpiha:=Bit_0;
371:Klima[1].NapakaSenzorTempProstora:=Bit_0;
372:Klima[1].NapakaSenzorVlaznosti:=Bit_0;
373:Klima[1].NapakaSenzorZunanjeTemp:=Bit_0;
374:Klima[1].NiTokaVVlazilcu:=Bit_0;
375:Klima[1].NiVodeVVlazilcu:=Bit_0;
376:Klima[1].NizekPritiskKompresor1:=Bit_0;
377:Klima[1].NizekPritiskKompresor2:=Bit_0;
378:Klima[1].NizkaTempVProstoru:=Bit_0;
379:Klima[1].NizkaVlaznost:=Bit_0;
380:Klima[1].OnOffEnablingBySupervisor:=Bit_0;
381:Klima[1].PozarniAlarm:=Bit_0;
382:Klima[1].Razvlazevanje:=Bit_0;
383:Klima[1].RemoteOFFtoOutput:=Bit_0;
384:Klima[1].RocniIzklop:=Bit_0;
385:Klima[1].SenzorjiStatus:=Bit_0;
386:Klima[1].UnitOnOff:=Bit_0;
387:Klima[1].VisokaTempVProstoru:=Bit_0;
388:Klima[1].VisokaVlaznost:=Bit_0;
389:Klima[1].VisokTokVVlazilcu:=Bit_0;
390:Klima[1].Vlazenje:=Bit_0;
391:Klima[1].ZamasenFilter:=Bit_0;
392:Klima[2].Deluje:=Bit_0;
393:Klima[2].FenThermalCutout:=Bit_0;
394:Klima[2].GeneralAlarm:=Bit_0;
395:Klima[2].Kompresor1naMejiObrUr:=Bit_0;
396:Klima[2].Kompresor2naMejiObrUr:=Bit_0;
397:Klima[2].Napaka:=Bit_0;
398:Klima[2].NapakaPriPretokuZraka:=Bit_0;
399:Klima[2].NapakaSenzorTempIzpiha:=Bit_0;
400:Klima[2].NapakaSenzorTempProstora:=Bit_0;
401:Klima[2].NapakaSenzorVlaznosti:=Bit_0;
402:Klima[2].NapakaSenzorZunanjeTemp:=Bit_0;
403:Klima[2].NiTokaVVlazilcu:=Bit_0;
404:Klima[2].NiVodeVVlazilcu:=Bit_0;
405:Klima[2].NizekPritiskKompresor1:=Bit_0;
406:Klima[2].NizekPritiskKompresor2:=Bit_0;
407:Klima[2].NizkaTempVProstoru:=Bit_0;
408:Klima[2].NizkaVlaznost:=Bit_0;
409:Klima[2].OnOffEnablingBySupervisor:=Bit_0;
410:Klima[2].PozarniAlarm:=Bit_0;
411:Klima[2].Razvlazevanje:=Bit_0;
412:Klima[2].RemoteOFFtoOutput:=Bit_0;
413:Klima[2].RocniIzklop:=Bit_0;
414:Klima[2].SenzorjiStatus:=Bit_0;
415:Klima[2].UnitOnOff:=Bit_0;
416:Klima[2].VisokaTempVProstoru:=Bit_0;
417:Klima[2].VisokaVlaznost:=Bit_0;
418:Klima[2].VisokTokVVlazilcu:=Bit_0;
419:Klima[2].Vlazenje:=Bit_0;
420:Klima[2].ZamasenFilter:=Bit_0;
421:Klima[3].Deluje:=Bit_0;
422:Klima[3].FenThermalCutout:=Bit_0;
423:Klima[3].GeneralAlarm:=Bit_0;
424:Klima[3].Kompresor1naMejiObrUr:=Bit_0;
425:Klima[3].Kompresor2naMejiObrUr:=Bit_0;
426:Klima[3].Napaka:=Bit_0;
427:Klima[3].NapakaPriPretokuZraka:=Bit_0;
428:Klima[3].NapakaSenzorTempIzpiha:=Bit_0;
429:Klima[3].NapakaSenzorTempProstora:=Bit_0;
430:Klima[3].NapakaSenzorVlaznosti:=Bit_0;
431:Klima[3].NapakaSenzorZunanjeTemp:=Bit_0;
432:Klima[3].NiTokaVVlazilcu:=Bit_0;
433:Klima[3].NiVodeVVlazilcu:=Bit_0;
434:Klima[3].NizekPritiskKompresor1:=Bit_0;
435:Klima[3].NizekPritiskKompresor2:=Bit_0;
436:Klima[3].NizkaTempVProstoru:=Bit_0;
437:Klima[3].NizkaVlaznost:=Bit_0;
438:Klima[3].OnOffEnablingBySupervisor:=Bit_0;
439:Klima[3].PozarniAlarm:=Bit_0;
440:Klima[3].Razvlazevanje:=Bit_0;
441:Klima[3].RemoteOFFtoOutput:=Bit_0;
442:Klima[3].RocniIzklop:=Bit_0;
443:Klima[3].SenzorjiStatus:=Bit_0;
444:Klima[3].UnitOnOff:=Bit_0;
445:Klima[3].VisokaTempVProstoru:=Bit_0;
446:Klima[3].VisokaVlaznost:=Bit_0;
447:Klima[3].VisokTokVVlazilcu:=Bit_0;
448:Klima[3].Vlazenje:=Bit_0;
449:Klima[3].ZamasenFilter:=Bit_0;
450:Klima[4].Deluje:=Bit_0;
451:Klima[4].FenThermalCutout:=Bit_0;
452:Klima[4].GeneralAlarm:=Bit_0;
453:Klima[4].Kompresor1naMejiObrUr:=Bit_0;
454:Klima[4].Kompresor2naMejiObrUr:=Bit_0;
455:Klima[4].Napaka:=Bit_0;
456:Klima[4].NapakaPriPretokuZraka:=Bit_0;
457:Klima[4].NapakaSenzorTempIzpiha:=Bit_0;
458:Klima[4].NapakaSenzorTempProstora:=Bit_0;
459:Klima[4].NapakaSenzorVlaznosti:=Bit_0;
460:Klima[4].NapakaSenzorZunanjeTemp:=Bit_0;
461:Klima[4].NiTokaVVlazilcu:=Bit_0;
462:Klima[4].NiVodeVVlazilcu:=Bit_0;
463:Klima[4].NizekPritiskKompresor1:=Bit_0;
464:Klima[4].NizekPritiskKompresor2:=Bit_0;
465:Klima[4].NizkaTempVProstoru:=Bit_0;
466:Klima[4].NizkaVlaznost:=Bit_0;
467:Klima[4].OnOffEnablingBySupervisor:=Bit_0;
468:Klima[4].PozarniAlarm:=Bit_0;
469:Klima[4].Razvlazevanje:=Bit_0;
470:Klima[4].RemoteOFFtoOutput:=Bit_0;
471:Klima[4].RocniIzklop:=Bit_0;
472:Klima[4].SenzorjiStatus:=Bit_0;
473:Klima[4].UnitOnOff:=Bit_0;
474:Klima[4].VisokaTempVProstoru:=Bit_0;
475:Klima[4].VisokaVlaznost:=Bit_0;
476:Klima[4].VisokTokVVlazilcu:=Bit_0;
477:Klima[4].Vlazenje:=Bit_0;
478:Klima[4].ZamasenFilter:=Bit_0;
479:Klima[5].Deluje:=Bit_0;
480:Klima[5].FenThermalCutout:=Bit_0;
481:Klima[5].GeneralAlarm:=Bit_0;
482:Klima[5].Kompresor1naMejiObrUr:=Bit_0;
483:Klima[5].Kompresor2naMejiObrUr:=Bit_0;
484:Klima[5].Napaka:=Bit_0;
485:Klima[5].NapakaPriPretokuZraka:=Bit_0;
486:Klima[5].NapakaSenzorTempIzpiha:=Bit_0;
487:Klima[5].NapakaSenzorTempProstora:=Bit_0;
488:Klima[5].NapakaSenzorVlaznosti:=Bit_0;
489:Klima[5].NapakaSenzorZunanjeTemp:=Bit_0;
490:Klima[5].NiTokaVVlazilcu:=Bit_0;
491:Klima[5].NiVodeVVlazilcu:=Bit_0;
492:Klima[5].NizekPritiskKompresor1:=Bit_0;
493:Klima[5].NizekPritiskKompresor2:=Bit_0;
494:Klima[5].NizkaTempVProstoru:=Bit_0;
495:Klima[5].NizkaVlaznost:=Bit_0;
496:Klima[5].OnOffEnablingBySupervisor:=Bit_0;
497:Klima[5].PozarniAlarm:=Bit_0;
498:Klima[5].Razvlazevanje:=Bit_0;
499:Klima[5].RemoteOFFtoOutput:=Bit_0;
500:Klima[5].RocniIzklop:=Bit_0;
501:Klima[5].SenzorjiStatus:=Bit_0;
502:Klima[5].UnitOnOff:=Bit_0;
503:Klima[5].VisokaTempVProstoru:=Bit_0;
504:Klima[5].VisokaVlaznost:=Bit_0;
505:Klima[5].VisokTokVVlazilcu:=Bit_0;
506:Klima[5].Vlazenje:=Bit_0;
507:Klima[5].ZamasenFilter:=Bit_0;
508:Klima[6].Deluje:=Bit_0;
509:Klima[6].FenThermalCutout:=Bit_0;
510:Klima[6].GeneralAlarm:=Bit_0;
511:Klima[6].Kompresor1naMejiObrUr:=Bit_0;
512:Klima[6].Kompresor2naMejiObrUr:=Bit_0;
513:Klima[6].Napaka:=Bit_0;
514:Klima[6].NapakaPriPretokuZraka:=Bit_0;
515:Klima[6].NapakaSenzorTempIzpiha:=Bit_0;
516:Klima[6].NapakaSenzorTempProstora:=Bit_0;
517:Klima[6].NapakaSenzorVlaznosti:=Bit_0;
518:Klima[6].NapakaSenzorZunanjeTemp:=Bit_0;
519:Klima[6].NiTokaVVlazilcu:=Bit_0;
520:Klima[6].NiVodeVVlazilcu:=Bit_0;
521:Klima[6].NizekPritiskKompresor1:=Bit_0;
522:Klima[6].NizekPritiskKompresor2:=Bit_0;
523:Klima[6].NizkaTempVProstoru:=Bit_0;
524:Klima[6].NizkaVlaznost:=Bit_0;
525:Klima[6].OnOffEnablingBySupervisor:=Bit_0;
526:Klima[6].PozarniAlarm:=Bit_0;
527:Klima[6].Razvlazevanje:=Bit_0;
528:Klima[6].RemoteOFFtoOutput:=Bit_0;
529:Klima[6].RocniIzklop:=Bit_0;
530:Klima[6].SenzorjiStatus:=Bit_0;
531:Klima[6].UnitOnOff:=Bit_0;
532:Klima[6].VisokaTempVProstoru:=Bit_0;
533:Klima[6].VisokaVlaznost:=Bit_0;
534:Klima[6].VisokTokVVlazilcu:=Bit_0;
535:Klima[6].Vlazenje:=Bit_0;
536:Klima[6].ZamasenFilter:=Bit_0;
537:KlimeNaCas[0]:=Bit_0;
538:KlimeNaCas[1]:=Bit_0;
539:KlimeNaCas[2]:=Bit_0;
540:KlimeNaCas[3]:=Bit_0;
541:MrezaIzpad:=Bit_0;
542:MrezaIzpadKlimaOff[1]:=Bit_0;
543:MrezaIzpadKlimaOff[2]:=Bit_0;
544:MrezaIzpadKlimaOff[3]:=Bit_0;
545:MrezaIzpadKlimaOff[4]:=Bit_0;
546:MrezaIzpadKlimaOff[5]:=Bit_0;
547:MrezaIzpadKlimaOff[6]:=Bit_0;
548:NapakaSenzorTemp[1]:=Bit_0;
549:NapakaSenzorTemp[2]:=Bit_0;
550:NapakaSenzorTemp[3]:=Bit_0;
551:NapakaSenzorTemp[4]:=Bit_0;
552:NapakaSenzorTemp[5]:=Bit_0;
553:NapakaSenzorTemp[6]:=Bit_0;
554:NapakaSenzorVlaga[1]:=Bit_0;
555:NapakaSenzorVlaga[2]:=Bit_0;
556:NapakaSenzorVlaga[3]:=Bit_0;
557:NapakaSenzorVlaga[4]:=Bit_0;
558:NapakaSenzorVlaga[5]:=Bit_0;
559:NapakaSenzorVlaga[6]:=Bit_0;
560:PMM.Napaka:=Bit_0;
561:PMMOverCurrentBetw[1]:=Bit_0;
562:PMMOverCurrentBetw[2]:=Bit_0;
563:PMMOverCurrentBetw[3]:=Bit_0;
564:PMMOverCurrentOver[1]:=Bit_0;
565:PMMOverCurrentOver[2]:=Bit_0;
566:PMMOverCurrentOver[3]:=Bit_0;
567:SetDateTime:=Bit_0;
568:SetDateTimeDemand:=Bit_0;
569:SetDateTimeError:=Bit_0;
570:SetDateTimeFinished:=Bit_0;
571:SetRemoteOnOff[1]:=Bit_0;
572:SetRemoteOnOff[2]:=Bit_0;
573:SlabaBaterijaPLC_A1:=Bit_0;
574:TempTSprevisoka[1]:=Bit_0;
575:TempTSprevisoka[2]:=Bit_0;
576:TempTSprevisoka[3]:=Bit_0;
577:TempTSprevisokaSum:=Bit_0;
578:UPS1Errors[10]:=Bit_0;
579:UPS1Errors[11]:=Bit_0;
580:UPS1Errors[12]:=Bit_0;
581:UPS1Errors[13]:=Bit_0;
582:UPS1Errors[14]:=Bit_0;
583:UPS1Errors[15]:=Bit_0;
584:UPS1Errors[16]:=Bit_0;
585:UPS1Errors[17]:=Bit_0;
586:UPS1Errors[18]:=Bit_0;
587:UPS1Errors[19]:=Bit_0;
588:UPS1Errors[1]:=Bit_0;
589:UPS1Errors[20]:=Bit_0;
590:UPS1Errors[21]:=Bit_0;
591:UPS1Errors[22]:=Bit_0;
592:UPS1Errors[23]:=Bit_0;
593:UPS1Errors[24]:=Bit_0;
594:UPS1Errors[25]:=Bit_0;
595:UPS1Errors[2]:=Bit_0;
596:UPS1Errors[3]:=Bit_0;
597:UPS1Errors[4]:=Bit_0;
598:UPS1Errors[5]:=Bit_0;
599:UPS1Errors[6]:=Bit_0;
600:UPS1Errors[7]:=Bit_0;
601:UPS1Errors[8]:=Bit_0;
602:UPS1Errors[9]:=Bit_0;
603:UPS2Errors[10]:=Bit_0;
604:UPS2Errors[11]:=Bit_0;
605:UPS2Errors[12]:=Bit_0;
606:UPS2Errors[13]:=Bit_0;
607:UPS2Errors[14]:=Bit_0;
608:UPS2Errors[15]:=Bit_0;
609:UPS2Errors[16]:=Bit_0;
610:UPS2Errors[17]:=Bit_0;
611:UPS2Errors[18]:=Bit_0;
612:UPS2Errors[19]:=Bit_0;
613:UPS2Errors[1]:=Bit_0;
614:UPS2Errors[20]:=Bit_0;
615:UPS2Errors[21]:=Bit_0;
616:UPS2Errors[22]:=Bit_0;
617:UPS2Errors[23]:=Bit_0;
618:UPS2Errors[24]:=Bit_0;
619:UPS2Errors[25]:=Bit_0;
620:UPS2Errors[2]:=Bit_0;
621:UPS2Errors[3]:=Bit_0;
622:UPS2Errors[4]:=Bit_0;
623:UPS2Errors[5]:=Bit_0;
624:UPS2Errors[6]:=Bit_0;
625:UPS2Errors[7]:=Bit_0;
626:UPS2Errors[8]:=Bit_0;
627:UPS2Errors[9]:=Bit_0;
628:UPS[1].AlarmAwaitingPower:=Bit_0;
629:UPS[1].AlarmBypassBad:=Bit_0;
630:UPS[1].AlarmChargerFailed:=Bit_0;
631:UPS[1].AlarmCommunicationsLost:=Bit_0;
632:UPS[1].AlarmDepletedBattery:=Bit_0;
633:UPS[1].AlarmDiagnosticTestFailed:=Bit_0;
634:UPS[1].AlarmInverterError:=Bit_0;
635:UPS[1].AlarmIzhodOffKotZahtevano:=Bit_0;
636:UPS[1].AlarmIzhodPreobremenjen:=Bit_0;
637:UPS[1].AlarmLowBattery:=Bit_0;
638:UPS[1].AlarmNapakaNaVarovalki:=Bit_0;
639:UPS[1].AlarmNapakaNaVentilatorju:=Bit_0;
640:UPS[1].AlarmOnBattery:=Bit_0;
641:UPS[1].AlarmOnBypass:=Bit_0;
642:UPS[1].AlarmShutdownImminent:=Bit_0;
643:UPS[1].AlarmShutdownPending:=Bit_0;
644:UPS[1].AlarmSlabaBaterija:=Bit_0;
645:UPS[1].AlarmSplosnaNapaka:=Bit_0;
646:UPS[1].AlarmStanjeIzhodaIzvenToleranc:=Bit_0;
647:UPS[1].AlarmStanjeVhodaIzvenToleranc:=Bit_0;
648:UPS[1].AlarmTemperaturaIzvenToleranc:=Bit_0;
649:UPS[1].AlarmTestInProgres:=Bit_0;
650:UPS[1].AlarmUPSIzhodOff:=Bit_0;
651:UPS[1].AlarmUPSOffKotZahtevano:=Bit_0;
652:UPS[1].AlarmUPSSystemOff:=Bit_0;
653:UPS[1].Napaka:=Bit_0;
654:UPS[1].StatusEcomodeAktiven:=Bit_0;
655:UPS[1].StatusInverterIsOn:=Bit_0;
656:UPS[1].StatusStopOperation:=Bit_0;
657:UPS[2].AlarmAwaitingPower:=Bit_0;
658:UPS[2].AlarmBypassBad:=Bit_0;
659:UPS[2].AlarmChargerFailed:=Bit_0;
660:UPS[2].AlarmCommunicationsLost:=Bit_0;
661:UPS[2].AlarmDepletedBattery:=Bit_0;
662:UPS[2].AlarmDiagnosticTestFailed:=Bit_0;
663:UPS[2].AlarmInverterError:=Bit_0;
664:UPS[2].AlarmIzhodOffKotZahtevano:=Bit_0;
665:UPS[2].AlarmIzhodPreobremenjen:=Bit_0;
666:UPS[2].AlarmLowBattery:=Bit_0;
667:UPS[2].AlarmNapakaNaVarovalki:=Bit_0;
668:UPS[2].AlarmNapakaNaVentilatorju:=Bit_0;
669:UPS[2].AlarmOnBattery:=Bit_0;
670:UPS[2].AlarmOnBypass:=Bit_0;
671:UPS[2].AlarmShutdownImminent:=Bit_0;
672:UPS[2].AlarmShutdownPending:=Bit_0;
673:UPS[2].AlarmSlabaBaterija:=Bit_0;
674:UPS[2].AlarmSplosnaNapaka:=Bit_0;
675:UPS[2].AlarmStanjeIzhodaIzvenToleranc:=Bit_0;
676:UPS[2].AlarmStanjeVhodaIzvenToleranc:=Bit_0;
677:UPS[2].AlarmTemperaturaIzvenToleranc:=Bit_0;
678:UPS[2].AlarmTestInProgres:=Bit_0;
679:UPS[2].AlarmUPSIzhodOff:=Bit_0;
680:UPS[2].AlarmUPSOffKotZahtevano:=Bit_0;
681:UPS[2].AlarmUPSSystemOff:=Bit_0;
682:UPS[2].Napaka:=Bit_0;
683:UPS[2].StatusEcomodeAktiven:=Bit_0;
684:UPS[2].StatusInverterIsOn:=Bit_0;
685:UPS[2].StatusStopOperation:=Bit_0;
686:UserLoggedIn:=Bit_0;
687:DIN_A1Q11_OdcUpsB_IZP:=Bit_0;
688:DIN_A1Q12_OdcByUpsB_IZP:=Bit_0;
689:DIN_A1Q13_OdcByB_IZP:=Bit_0;
690:DIN_UQ11_OdcPMMB_IZP:=Bit_0;
691:DIN_UQ12_OdcPMMB_IZP:=Bit_0;
692:DIN_PrenapA3_OK:=Bit_0;
693:DIN_A1Q0_GlavnoStiB_ON:=Bit_0;
694:DIN_A1Q11_OdcUpsB_ON:=Bit_0;
695:DIN_A1Q12_OdcByUpsB_ON:=Bit_0;
696:DI_A1Q13_OdcByB_ON:=Bit_0;
697:DIN_A1Q01_DovUpsB_ON:=Bit_0;
698:DI_A1Q02_DovByB_ON:=Bit_0;
699:DIN_UQ11_OdcPMMB_ON:=Bit_0;
700:DI_UQ12_OdcPMMB_ON:=Bit_0;
701:Klima[1].NapacnoGesloAlarm:=Bit_0;
702:Klima[1].ExtTempHumAlarm:=Bit_0;
703:Klima[1].PoplavniAlarm:=Bit_0;
704:Klima[1].VisokPritiskKompresor1:=Bit_0;
705:Klima[1].VisokPritiskKompresor2:=Bit_0;
706:Klima[1].ElVentilKompresor1ERR:=Bit_0;
707:Klima[1].ElVentilKompresor2ERR:=Bit_0;
708:Klima[1].WrongPhaseSeqAlarm:=Bit_0;
709:Klima[1].PrekinjenLANalarm:=Bit_0;
710:Klima[1].CWTempHighForDehum:=Bit_0;
711:Klima[1].CWVentilErrOrLowFlow:=Bit_0;
712:Klima[1].NapakaPriPretokuVode:=Bit_0;
713:Klima[1].CWhighTemp:=Bit_0;
714:Klima[1].NapakaSenzorHotWTemp:=Bit_0;
715:Klima[1].NapakaSenzorCondWTemp:=Bit_0;
716:Klima[1].NapakaSenzorCW:=Bit_0;
717:Klima[1].Kompresor3naMejiObrUr:=Bit_0;
718:Klima[1].Kompresor4naMejiObrUr:=Bit_0;
719:Klima[1].ZracniFilterNaMejiObrUr:=Bit_0;
720:Klima[1].Grelec1naMejiObrUr:=Bit_0;
721:Klima[1].Grelec2naMejiObrUr:=Bit_0;
722:Klima[1].VlazilecNaMejiObrUr:=Bit_0;
723:Klima[1].AirCondUnitNaMejiObrUr:=Bit_0;
724:Klima[1].DigIn2Alarm:=Bit_0;
725:Klima[1].DigIn4Alarm:=Bit_0;
726:Klima[1].DigIn6Alarm:=Bit_0;
727:Klima[1].VlazilecGenAlarm:=Bit_0;
728:Klima[1].General2ndLevAlarm:=Bit_0;
729:Klima[1].UnitOnRotAlarm:=Bit_0;
730:Klima[1].UnitOnAlarmA:=Bit_0;
731:Klima[1].UnitOnAlarmB:=Bit_0;
732:Klima[1].UnitOnAlarmC:=Bit_0;
733:Klima[2].NapacnoGesloAlarm:=Bit_0;
734:Klima[2].ExtTempHumAlarm:=Bit_0;
735:Klima[2].PoplavniAlarm:=Bit_0;
736:Klima[2].VisokPritiskKompresor1:=Bit_0;
737:Klima[2].VisokPritiskKompresor2:=Bit_0;
738:Klima[2].ElVentilKompresor1ERR:=Bit_0;
739:Klima[2].ElVentilKompresor2ERR:=Bit_0;
740:Klima[2].WrongPhaseSeqAlarm:=Bit_0;
741:Klima[2].PrekinjenLANalarm:=Bit_0;
742:Klima[2].CWTempHighForDehum:=Bit_0;
743:Klima[2].CWVentilErrOrLowFlow:=Bit_0;
744:Klima[2].NapakaPriPretokuVode:=Bit_0;
745:Klima[2].CWhighTemp:=Bit_0;
746:Klima[2].NapakaSenzorHotWTemp:=Bit_0;
747:Klima[2].NapakaSenzorCondWTemp:=Bit_0;
748:Klima[2].NapakaSenzorCW:=Bit_0;
749:Klima[2].Kompresor3naMejiObrUr:=Bit_0;
750:Klima[2].Kompresor4naMejiObrUr:=Bit_0;
751:Klima[2].ZracniFilterNaMejiObrUr:=Bit_0;
752:Klima[2].Grelec1naMejiObrUr:=Bit_0;
753:Klima[2].Grelec2naMejiObrUr:=Bit_0;
754:Klima[2].VlazilecNaMejiObrUr:=Bit_0;
755:Klima[2].AirCondUnitNaMejiObrUr:=Bit_0;
756:Klima[2].DigIn2Alarm:=Bit_0;
757:Klima[2].DigIn4Alarm:=Bit_0;
758:Klima[2].DigIn6Alarm:=Bit_0;
759:Klima[2].VlazilecGenAlarm:=Bit_0;
760:Klima[2].General2ndLevAlarm:=Bit_0;
761:Klima[2].UnitOnRotAlarm:=Bit_0;
762:Klima[2].UnitOnAlarmA:=Bit_0;
763:Klima[2].UnitOnAlarmB:=Bit_0;
764:Klima[2].UnitOnAlarmC:=Bit_0;
765:Klima[3].NapacnoGesloAlarm:=Bit_0;
766:Klima[3].ExtTempHumAlarm:=Bit_0;
767:Klima[3].PoplavniAlarm:=Bit_0;
768:Klima[3].VisokPritiskKompresor1:=Bit_0;
769:Klima[3].VisokPritiskKompresor2:=Bit_0;
770:Klima[3].ElVentilKompresor1ERR:=Bit_0;
771:Klima[3].ElVentilKompresor2ERR:=Bit_0;
772:Klima[3].WrongPhaseSeqAlarm:=Bit_0;
773:Klima[3].PrekinjenLANalarm:=Bit_0;
774:Klima[3].CWTempHighForDehum:=Bit_0;
775:Klima[3].CWVentilErrOrLowFlow:=Bit_0;
776:Klima[3].NapakaPriPretokuVode:=Bit_0;
777:Klima[3].CWhighTemp:=Bit_0;
778:Klima[3].NapakaSenzorHotWTemp:=Bit_0;
779:Klima[3].NapakaSenzorCondWTemp:=Bit_0;
780:Klima[3].NapakaSenzorCW:=Bit_0;
781:Klima[3].Kompresor3naMejiObrUr:=Bit_0;
782:Klima[3].Kompresor4naMejiObrUr:=Bit_0;
783:Klima[3].ZracniFilterNaMejiObrUr:=Bit_0;
784:Klima[3].Grelec1naMejiObrUr:=Bit_0;
785:Klima[3].Grelec2naMejiObrUr:=Bit_0;
786:Klima[3].VlazilecNaMejiObrUr:=Bit_0;
787:Klima[3].AirCondUnitNaMejiObrUr:=Bit_0;
788:Klima[3].DigIn2Alarm:=Bit_0;
789:Klima[3].DigIn4Alarm:=Bit_0;
790:Klima[3].DigIn6Alarm:=Bit_0;
791:Klima[3].VlazilecGenAlarm:=Bit_0;
792:Klima[3].General2ndLevAlarm:=Bit_0;
793:Klima[3].UnitOnRotAlarm:=Bit_0;
794:Klima[3].UnitOnAlarmA:=Bit_0;
795:Klima[3].UnitOnAlarmB:=Bit_0;
796:Klima[3].UnitOnAlarmC:=Bit_0;
797:Klima[4].NapacnoGesloAlarm:=Bit_0;
798:Klima[4].ExtTempHumAlarm:=Bit_0;
799:Klima[4].PoplavniAlarm:=Bit_0;
800:Klima[4].VisokPritiskKompresor1:=Bit_0;
801:Klima[4].VisokPritiskKompresor2:=Bit_0;
802:Klima[4].ElVentilKompresor1ERR:=Bit_0;
803:Klima[4].ElVentilKompresor2ERR:=Bit_0;
804:Klima[4].WrongPhaseSeqAlarm:=Bit_0;
805:Klima[4].PrekinjenLANalarm:=Bit_0;
806:Klima[4].CWTempHighForDehum:=Bit_0;
807:Klima[4].CWVentilErrOrLowFlow:=Bit_0;
808:Klima[4].NapakaPriPretokuVode:=Bit_0;
809:Klima[4].CWhighTemp:=Bit_0;
810:Klima[4].NapakaSenzorHotWTemp:=Bit_0;
811:Klima[4].NapakaSenzorCondWTemp:=Bit_0;
812:Klima[4].NapakaSenzorCW:=Bit_0;
813:Klima[4].Kompresor3naMejiObrUr:=Bit_0;
814:Klima[4].Kompresor4naMejiObrUr:=Bit_0;
815:Klima[4].ZracniFilterNaMejiObrUr:=Bit_0;
816:Klima[4].Grelec1naMejiObrUr:=Bit_0;
817:Klima[4].Grelec2naMejiObrUr:=Bit_0;
818:Klima[4].VlazilecNaMejiObrUr:=Bit_0;
819:Klima[4].AirCondUnitNaMejiObrUr:=Bit_0;
820:Klima[4].DigIn2Alarm:=Bit_0;
821:Klima[4].DigIn4Alarm:=Bit_0;
822:Klima[4].DigIn6Alarm:=Bit_0;
823:Klima[4].VlazilecGenAlarm:=Bit_0;
824:Klima[4].General2ndLevAlarm:=Bit_0;
825:Klima[4].UnitOnRotAlarm:=Bit_0;
826:Klima[4].UnitOnAlarmA:=Bit_0;
827:Klima[4].UnitOnAlarmB:=Bit_0;
828:Klima[4].UnitOnAlarmC:=Bit_0;
829:Klima[5].NapacnoGesloAlarm:=Bit_0;
830:Klima[5].ExtTempHumAlarm:=Bit_0;
831:Klima[5].PoplavniAlarm:=Bit_0;
832:Klima[5].VisokPritiskKompresor1:=Bit_0;
833:Klima[5].VisokPritiskKompresor2:=Bit_0;
834:Klima[5].ElVentilKompresor1ERR:=Bit_0;
835:Klima[5].ElVentilKompresor2ERR:=Bit_0;
836:Klima[5].WrongPhaseSeqAlarm:=Bit_0;
837:Klima[5].PrekinjenLANalarm:=Bit_0;
838:Klima[5].CWTempHighForDehum:=Bit_0;
839:Klima[5].CWVentilErrOrLowFlow:=Bit_0;
840:Klima[5].NapakaPriPretokuVode:=Bit_0;
841:Klima[5].CWhighTemp:=Bit_0;
842:Klima[5].NapakaSenzorHotWTemp:=Bit_0;
843:Klima[5].NapakaSenzorCondWTemp:=Bit_0;
844:Klima[5].NapakaSenzorCW:=Bit_0;
845:Klima[5].Kompresor3naMejiObrUr:=Bit_0;
846:Klima[5].Kompresor4naMejiObrUr:=Bit_0;
847:Klima[5].ZracniFilterNaMejiObrUr:=Bit_0;
848:Klima[5].Grelec1naMejiObrUr:=Bit_0;
849:Klima[5].Grelec2naMejiObrUr:=Bit_0;
850:Klima[5].VlazilecNaMejiObrUr:=Bit_0;
851:Klima[5].AirCondUnitNaMejiObrUr:=Bit_0;
852:Klima[5].DigIn2Alarm:=Bit_0;
853:Klima[5].DigIn4Alarm:=Bit_0;
854:Klima[5].DigIn6Alarm:=Bit_0;
855:Klima[5].VlazilecGenAlarm:=Bit_0;
856:Klima[5].General2ndLevAlarm:=Bit_0;
857:Klima[5].UnitOnRotAlarm:=Bit_0;
858:Klima[5].UnitOnAlarmA:=Bit_0;
859:Klima[5].UnitOnAlarmB:=Bit_0;
860:Klima[5].UnitOnAlarmC:=Bit_0;
861:Klima[6].NapacnoGesloAlarm:=Bit_0;
862:Klima[6].ExtTempHumAlarm:=Bit_0;
863:Klima[6].PoplavniAlarm:=Bit_0;
864:Klima[6].VisokPritiskKompresor1:=Bit_0;
865:Klima[6].VisokPritiskKompresor2:=Bit_0;
866:Klima[6].ElVentilKompresor1ERR:=Bit_0;
867:Klima[6].ElVentilKompresor2ERR:=Bit_0;
868:Klima[6].WrongPhaseSeqAlarm:=Bit_0;
869:Klima[6].PrekinjenLANalarm:=Bit_0;
870:Klima[6].CWTempHighForDehum:=Bit_0;
871:Klima[6].CWVentilErrOrLowFlow:=Bit_0;
872:Klima[6].NapakaPriPretokuVode:=Bit_0;
873:Klima[6].CWhighTemp:=Bit_0;
874:Klima[6].NapakaSenzorHotWTemp:=Bit_0;
875:Klima[6].NapakaSenzorCondWTemp:=Bit_0;
876:Klima[6].NapakaSenzorCW:=Bit_0;
877:Klima[6].Kompresor3naMejiObrUr:=Bit_0;
878:Klima[6].Kompresor4naMejiObrUr:=Bit_0;
879:Klima[6].ZracniFilterNaMejiObrUr:=Bit_0;
880:Klima[6].Grelec1naMejiObrUr:=Bit_0;
881:Klima[6].Grelec2naMejiObrUr:=Bit_0;
882:Klima[6].VlazilecNaMejiObrUr:=Bit_0;
883:Klima[6].AirCondUnitNaMejiObrUr:=Bit_0;
884:Klima[6].DigIn2Alarm:=Bit_0;
885:Klima[6].DigIn4Alarm:=Bit_0;
886:Klima[6].DigIn6Alarm:=Bit_0;
887:Klima[6].VlazilecGenAlarm:=Bit_0;
888:Klima[6].General2ndLevAlarm:=Bit_0;
889:Klima[6].UnitOnRotAlarm:=Bit_0;
890:Klima[6].UnitOnAlarmA:=Bit_0;
891:Klima[6].UnitOnAlarmB:=Bit_0;
892:Klima[6].UnitOnAlarmC:=Bit_0;
893:Klima[1].Komp1On:=Bit_0;
894:Klima[1].Komp2On:=Bit_0;
895:Klima[1].Komp3On:=Bit_0;
896:Klima[1].Komp4On:=Bit_0;
897:Klima[2].Komp1On:=Bit_0;
898:Klima[2].Komp2On:=Bit_0;
899:Klima[2].Komp3On:=Bit_0;
900:Klima[2].Komp4On:=Bit_0;
901:Klima[3].Komp1On:=Bit_0;
902:Klima[3].Komp2On:=Bit_0;
903:Klima[3].Komp3On:=Bit_0;
904:Klima[3].Komp4On:=Bit_0;
905:Klima[4].Komp1On:=Bit_0;
906:Klima[4].Komp2On:=Bit_0;
907:Klima[4].Komp3On:=Bit_0;
908:Klima[4].Komp4On:=Bit_0;
909:Klima[5].Komp1On:=Bit_0;
910:Klima[5].Komp2On:=Bit_0;
911:Klima[5].Komp3On:=Bit_0;
912:Klima[5].Komp4On:=Bit_0;
913:Klima[6].Komp1On:=Bit_0;
914:Klima[6].Komp2On:=Bit_0;
915:Klima[6].Komp3On:=Bit_0;
916:Klima[6].Komp4On:=Bit_0;
917:Klima[1].GretjeStopnja1:=Bit_0;
918:Klima[1].GretjeStopnja2:=Bit_0;
919:Klima[1].GretjeStopnja3:=Bit_0;
920:Klima[2].GretjeStopnja1:=Bit_0;
921:Klima[2].GretjeStopnja2:=Bit_0;
922:Klima[2].GretjeStopnja3:=Bit_0;
923:Klima[3].GretjeStopnja1:=Bit_0;
924:Klima[3].GretjeStopnja2:=Bit_0;
925:Klima[3].GretjeStopnja3:=Bit_0;
926:Klima[4].GretjeStopnja1:=Bit_0;
927:Klima[4].GretjeStopnja2:=Bit_0;
928:Klima[4].GretjeStopnja3:=Bit_0;
929:Klima[5].GretjeStopnja1:=Bit_0;
930:Klima[5].GretjeStopnja2:=Bit_0;
931:Klima[5].GretjeStopnja3:=Bit_0;
932:Klima[6].GretjeStopnja1:=Bit_0;
933:Klima[6].GretjeStopnja2:=Bit_0;
934:Klima[6].GretjeStopnja3:=Bit_0;
935:Klima[1].HotGasOn:=Bit_0;
936:Klima[2].HotGasOn:=Bit_0;
937:Klima[3].HotGasOn:=Bit_0;
938:Klima[4].HotGasOn:=Bit_0;
939:Klima[5].HotGasOn:=Bit_0;
940:Klima[6].HotGasOn:=Bit_0;
941:Klima[1].EmergencyWorking:=Bit_0;
942:Klima[2].EmergencyWorking:=Bit_0;
943:Klima[3].EmergencyWorking:=Bit_0;
944:Klima[4].EmergencyWorking:=Bit_0;
945:Klima[5].EmergencyWorking:=Bit_0;
946:Klima[6].EmergencyWorking:=Bit_0;
947:DI_A1Q01_DovUpsB_ON:=Bit_0;
948:DI_A1Q0_GlavnoStiB_ON:=Bit_0;
949:DI_A1Q11_OdcUpsB_IZP:=Bit_0;
950:DI_A1Q11_OdcUpsB_ON:=Bit_0;
951:DI_A1Q12_OdcByUpsB_IZP:=Bit_0;
952:DI_A1Q12_OdcByUpsB_ON:=Bit_0;
953:DI_A1Q13_OdcByB_IZP:=Bit_0;
954:ErrCommScada2:=Bit_0;
955:ComSCADA2:=Bit_0;
956:ComSCADA3:=Bit_0;
(*BOOL*)
END_CASE
END_FUNCTION
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_dWord : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje LONG*)
(**)
(*Pisanje REAL*)
(**)
4001:Klima[1].ObratovalneUre:=Real_0;
4003:Klima[1].TemperaturaProstora:=Real_0;
4005:Klima[1].TempIzpihanegaZraka:=Real_0;
4007:Klima[1].VlaznostProstora:=Real_0;
4009:Klima[1].ZunanjaTemp:=Real_0;
4011:Klima[2].ObratovalneUre:=Real_0;
4013:Klima[2].TemperaturaProstora:=Real_0;
4015:Klima[2].TempIzpihanegaZraka:=Real_0;
4017:Klima[2].VlaznostProstora:=Real_0;
4019:Klima[2].ZunanjaTemp:=Real_0;
4021:Klima[3].ObratovalneUre:=Real_0;
4023:Klima[3].TemperaturaProstora:=Real_0;
4025:Klima[3].TempIzpihanegaZraka:=Real_0;
4027:Klima[3].VlaznostProstora:=Real_0;
4029:Klima[3].ZunanjaTemp:=Real_0;
4031:Klima[4].ObratovalneUre:=Real_0;
4033:Klima[4].TemperaturaProstora:=Real_0;
4035:Klima[4].TempIzpihanegaZraka:=Real_0;
4037:Klima[4].VlaznostProstora:=Real_0;
4039:Klima[4].ZunanjaTemp:=Real_0;
4041:Klima[5].ObratovalneUre:=Real_0;
4043:Klima[5].TemperaturaProstora:=Real_0;
4045:Klima[5].TempIzpihanegaZraka:=Real_0;
4047:Klima[5].VlaznostProstora:=Real_0;
4049:Klima[5].ZunanjaTemp:=Real_0;
4051:Klima[6].ObratovalneUre:=Real_0;
4053:Klima[6].TemperaturaProstora:=Real_0;
4055:Klima[6].TempIzpihanegaZraka:=Real_0;
4057:Klima[6].VlaznostProstora:=Real_0;
4059:Klima[6].ZunanjaTemp:=Real_0;
4061:PMM.ActiveEnergyConsumed_kWh:=Real_0;
4063:PMM.ActivePowerPhaseA_kW:=Real_0;
4065:PMM.ActivePowerPhaseB_kW:=Real_0;
4067:PMM.ActivePowerPhaseC_kW:=Real_0;
4069:PMM.AparentPowerPhaseA:=Real_0;
4071:PMM.AparentPowerPhaseB:=Real_0;
4073:PMM.AparentPowerPhaseC:=Real_0;
4075:PMM.AverageCurrent_A:=Real_0;
4077:PMM.AveragePhaseToNeutral_V:=Real_0;
4079:PMM.AveragePhaseToPhase_V:=Real_0;
4081:PMM.CurrentInPhaseA_A:=Real_0;
4083:PMM.CurrentInPhaseB_A:=Real_0;
4085:PMM.CurrentInPhaseC_A:=Real_0;
4087:PMM.Frequency_Hz:=Real_0;
4089:PMM.Phase[1].Current[10]:=Real_0;
4091:PMM.Phase[1].Current[11]:=Real_0;
4093:PMM.Phase[1].Current[12]:=Real_0;
4095:PMM.Phase[1].Current[13]:=Real_0;
4097:PMM.Phase[1].Current[14]:=Real_0;
4099:PMM.Phase[1].Current[15]:=Real_0;
4101:PMM.Phase[1].Current[16]:=Real_0;
4103:PMM.Phase[1].Current[17]:=Real_0;
4105:PMM.Phase[1].Current[18]:=Real_0;
4107:PMM.Phase[1].Current[19]:=Real_0;
4109:PMM.Phase[1].Current[1]:=Real_0;
4111:PMM.Phase[1].Current[20]:=Real_0;
4113:PMM.Phase[1].Current[21]:=Real_0;
4115:PMM.Phase[1].Current[22]:=Real_0;
4117:PMM.Phase[1].Current[23]:=Real_0;
4119:PMM.Phase[1].Current[24]:=Real_0;
4121:PMM.Phase[1].Current[25]:=Real_0;
4123:PMM.Phase[1].Current[26]:=Real_0;
4125:PMM.Phase[1].Current[27]:=Real_0;
4127:PMM.Phase[1].Current[28]:=Real_0;
4129:PMM.Phase[1].Current[29]:=Real_0;
4131:PMM.Phase[1].Current[2]:=Real_0;
4133:PMM.Phase[1].Current[30]:=Real_0;
4135:PMM.Phase[1].Current[31]:=Real_0;
4137:PMM.Phase[1].Current[32]:=Real_0;
4139:PMM.Phase[1].Current[33]:=Real_0;
4141:PMM.Phase[1].Current[34]:=Real_0;
4143:PMM.Phase[1].Current[35]:=Real_0;
4145:PMM.Phase[1].Current[36]:=Real_0;
4147:PMM.Phase[1].Current[37]:=Real_0;
4149:PMM.Phase[1].Current[38]:=Real_0;
4151:PMM.Phase[1].Current[39]:=Real_0;
4153:PMM.Phase[1].Current[3]:=Real_0;
4155:PMM.Phase[1].Current[40]:=Real_0;
4157:PMM.Phase[1].Current[41]:=Real_0;
4159:PMM.Phase[1].Current[42]:=Real_0;
4161:PMM.Phase[1].Current[4]:=Real_0;
4163:PMM.Phase[1].Current[5]:=Real_0;
4165:PMM.Phase[1].Current[6]:=Real_0;
4167:PMM.Phase[1].Current[7]:=Real_0;
4169:PMM.Phase[1].Current[8]:=Real_0;
4171:PMM.Phase[1].Current[9]:=Real_0;
4173:PMM.Phase[2].Current[10]:=Real_0;
4175:PMM.Phase[2].Current[11]:=Real_0;
4177:PMM.Phase[2].Current[12]:=Real_0;
4179:PMM.Phase[2].Current[13]:=Real_0;
4181:PMM.Phase[2].Current[14]:=Real_0;
4183:PMM.Phase[2].Current[15]:=Real_0;
4185:PMM.Phase[2].Current[16]:=Real_0;
4187:PMM.Phase[2].Current[17]:=Real_0;
4189:PMM.Phase[2].Current[18]:=Real_0;
4191:PMM.Phase[2].Current[19]:=Real_0;
4193:PMM.Phase[2].Current[1]:=Real_0;
4195:PMM.Phase[2].Current[20]:=Real_0;
4197:PMM.Phase[2].Current[21]:=Real_0;
4199:PMM.Phase[2].Current[22]:=Real_0;
4201:PMM.Phase[2].Current[23]:=Real_0;
4203:PMM.Phase[2].Current[24]:=Real_0;
4205:PMM.Phase[2].Current[25]:=Real_0;
4207:PMM.Phase[2].Current[26]:=Real_0;
4209:PMM.Phase[2].Current[27]:=Real_0;
4211:PMM.Phase[2].Current[28]:=Real_0;
4213:PMM.Phase[2].Current[29]:=Real_0;
4215:PMM.Phase[2].Current[2]:=Real_0;
4217:PMM.Phase[2].Current[30]:=Real_0;
4219:PMM.Phase[2].Current[31]:=Real_0;
4221:PMM.Phase[2].Current[32]:=Real_0;
4223:PMM.Phase[2].Current[33]:=Real_0;
4225:PMM.Phase[2].Current[34]:=Real_0;
4227:PMM.Phase[2].Current[35]:=Real_0;
4229:PMM.Phase[2].Current[36]:=Real_0;
4231:PMM.Phase[2].Current[37]:=Real_0;
4233:PMM.Phase[2].Current[38]:=Real_0;
4235:PMM.Phase[2].Current[39]:=Real_0;
4237:PMM.Phase[2].Current[3]:=Real_0;
4239:PMM.Phase[2].Current[40]:=Real_0;
4241:PMM.Phase[2].Current[41]:=Real_0;
4243:PMM.Phase[2].Current[42]:=Real_0;
4245:PMM.Phase[2].Current[4]:=Real_0;
4247:PMM.Phase[2].Current[5]:=Real_0;
4249:PMM.Phase[2].Current[6]:=Real_0;
4251:PMM.Phase[2].Current[7]:=Real_0;
4253:PMM.Phase[2].Current[8]:=Real_0;
4255:PMM.Phase[2].Current[9]:=Real_0;
4257:PMM.Phase[3].Current[10]:=Real_0;
4259:PMM.Phase[3].Current[11]:=Real_0;
4261:PMM.Phase[3].Current[12]:=Real_0;
4263:PMM.Phase[3].Current[13]:=Real_0;
4265:PMM.Phase[3].Current[14]:=Real_0;
4267:PMM.Phase[3].Current[15]:=Real_0;
4269:PMM.Phase[3].Current[16]:=Real_0;
4271:PMM.Phase[3].Current[17]:=Real_0;
4273:PMM.Phase[3].Current[18]:=Real_0;
4275:PMM.Phase[3].Current[19]:=Real_0;
4277:PMM.Phase[3].Current[1]:=Real_0;
4279:PMM.Phase[3].Current[20]:=Real_0;
4281:PMM.Phase[3].Current[21]:=Real_0;
4283:PMM.Phase[3].Current[22]:=Real_0;
4285:PMM.Phase[3].Current[23]:=Real_0;
4287:PMM.Phase[3].Current[24]:=Real_0;
4289:PMM.Phase[3].Current[25]:=Real_0;
4291:PMM.Phase[3].Current[26]:=Real_0;
4293:PMM.Phase[3].Current[27]:=Real_0;
4295:PMM.Phase[3].Current[28]:=Real_0;
4297:PMM.Phase[3].Current[29]:=Real_0;
4299:PMM.Phase[3].Current[2]:=Real_0;
4301:PMM.Phase[3].Current[30]:=Real_0;
4303:PMM.Phase[3].Current[31]:=Real_0;
4305:PMM.Phase[3].Current[32]:=Real_0;
4307:PMM.Phase[3].Current[33]:=Real_0;
4309:PMM.Phase[3].Current[34]:=Real_0;
4311:PMM.Phase[3].Current[35]:=Real_0;
4313:PMM.Phase[3].Current[36]:=Real_0;
4315:PMM.Phase[3].Current[37]:=Real_0;
4317:PMM.Phase[3].Current[38]:=Real_0;
4319:PMM.Phase[3].Current[39]:=Real_0;
4321:PMM.Phase[3].Current[3]:=Real_0;
4323:PMM.Phase[3].Current[40]:=Real_0;
4325:PMM.Phase[3].Current[41]:=Real_0;
4327:PMM.Phase[3].Current[42]:=Real_0;
4329:PMM.Phase[3].Current[4]:=Real_0;
4331:PMM.Phase[3].Current[5]:=Real_0;
4333:PMM.Phase[3].Current[6]:=Real_0;
4335:PMM.Phase[3].Current[7]:=Real_0;
4337:PMM.Phase[3].Current[8]:=Real_0;
4339:PMM.Phase[3].Current[9]:=Real_0;
4341:PMM.PowerFactorSys:=Real_0;
4343:PMM.ReactiveEnergyConsumed_kVARh:=Real_0;
4345:PMM.ReactivePowerPhaseA:=Real_0;
4347:PMM.ReactivePowerPhaseB:=Real_0;
4349:PMM.ReactivePowerPhaseC:=Real_0;
4351:PMM.TotalActivePower_kW:=Real_0;
4353:PMM.TotalAparentPower_kVA:=Real_0;
4355:PMM.TotalPowerFactor:=Real_0;
4357:PMM.TotalReactivePower_kVAR:=Real_0;
4359:PMM.VirA_fsys:=Real_0;
4361:PMM.VirA_Isys:=Real_0;
4363:PMM.VirA_PFsys:=Real_0;
4365:PMM.VirA_Psys:=Real_0;
4367:PMM.VirA_Qsys:=Real_0;
4369:PMM.VirA_Ssys:=Real_0;
4371:PMM.VirA_Usys:=Real_0;
4373:PMM.VirB_fsys:=Real_0;
4375:PMM.VirB_Isys:=Real_0;
4377:PMM.VirB_PFsys:=Real_0;
4379:PMM.VirB_Psys:=Real_0;
4381:PMM.VirB_Qsys:=Real_0;
4383:PMM.VirB_Ssys:=Real_0;
4385:PMM.VirB_Usys:=Real_0;
4387:PMM.VirBActiveEnergyConsumed_kWh:=Real_0;
4389:PMM.VirBActivePowerPhaseA_kW:=Real_0;
4391:PMM.VirBActivePowerPhaseB_kW:=Real_0;
4393:PMM.VirBActivePowerPhaseC_kW:=Real_0;
4395:PMM.VirBAparentPowerPhaseA:=Real_0;
4397:PMM.VirBAparentPowerPhaseB:=Real_0;
4399:PMM.VirBAparentPowerPhaseC:=Real_0;
4401:PMM.VirBAverageCurrent_A:=Real_0;
4403:PMM.VirBAveragePhaseToNeutral_V:=Real_0;
4405:PMM.VirBAveragePhaseToPhase_V:=Real_0;
4407:PMM.VirBCurrentInPhaseA_A:=Real_0;
4409:PMM.VirBCurrentInPhaseB_A:=Real_0;
4411:PMM.VirBCurrentInPhaseC_A:=Real_0;
4413:PMM.VirBFrequency_Hz:=Real_0;
4415:PMM.VirBPowerFactorSys:=Real_0;
4417:PMM.VirBReactiveEnergyConsumed_kVARh:=Real_0;
4419:PMM.VirBReactivePowerPhaseA:=Real_0;
4421:PMM.VirBReactivePowerPhaseB:=Real_0;
4423:PMM.VirBReactivePowerPhaseC:=Real_0;
4425:PMM.VirBTotalActivePower_kW:=Real_0;
4427:PMM.VirBTotalAparentPower_kVA:=Real_0;
4429:PMM.VirBTotalPowerFactor:=Real_0;
4431:PMM.VirBTotalReactivePower_kVAR:=Real_0;
4433:PMM.VirBVoltageBetweenPhaseAB_V:=Real_0;
4435:PMM.VirBVoltageBetweenPhaseAN_V:=Real_0;
4437:PMM.VirBVoltageBetweenPhaseBC_V:=Real_0;
4439:PMM.VirBVoltageBetweenPhaseBN_V:=Real_0;
4441:PMM.VirBVoltageBetweenPhaseCA_V:=Real_0;
4443:PMM.VirBVoltageBetweenPhaseCN_V:=Real_0;
4445:PMM.VoltageBetweenPhaseAB_V:=Real_0;
4447:PMM.VoltageBetweenPhaseAN_V:=Real_0;
4449:PMM.VoltageBetweenPhaseBC_V:=Real_0;
4451:PMM.VoltageBetweenPhaseBN_V:=Real_0;
4453:PMM.VoltageBetweenPhaseCA_V:=Real_0;
4455:PMM.VoltageBetweenPhaseCN_V:=Real_0;
4457:PMMfaza01:=Real_0;
4459:PMMfaza02:=Real_0;
4461:PMMfaza03:=Real_0;
4463:PMMfaza04:=Real_0;
4465:PMMfaza05:=Real_0;
4467:PMMfaza06:=Real_0;
4469:PMMfaza07:=Real_0;
4471:PMMfaza08:=Real_0;
4473:PMMfaza09:=Real_0;
4475:PMMfaza10:=Real_0;
4477:PMMfaza11:=Real_0;
4479:PMMfaza12:=Real_0;
4481:PMMfaza13:=Real_0;
4483:PMMfaza14:=Real_0;
4485:PMMfaza15:=Real_0;
4487:PMMfaza16:=Real_0;
4489:PMMfaza17:=Real_0;
4491:PMMfaza18:=Real_0;
4493:PMMfaza19:=Real_0;
4495:PMMfaza20:=Real_0;
4497:PMMfaza21:=Real_0;
4499:PMMfaza22:=Real_0;
4501:PMMfaza23:=Real_0;
4503:PMMfaza24:=Real_0;
4505:PMMfaza25:=Real_0;
4507:PMMfaza26:=Real_0;
4509:PMMfaza27:=Real_0;
4511:PMMfaza28:=Real_0;
4513:PMMfaza29:=Real_0;
4515:PMMfaza30:=Real_0;
4517:PMMfaza31:=Real_0;
4519:PMMfaza32:=Real_0;
4521:PMMfaza33:=Real_0;
4523:PMMfaza34:=Real_0;
4525:PMMfaza35:=Real_0;
4527:PMMfaza36:=Real_0;
4529:PMMfaza37:=Real_0;
4531:PMMfaza38:=Real_0;
4533:PMMfaza39:=Real_0;
4535:PMMfaza40:=Real_0;
4537:PMMfaza41:=Real_0;
4539:PMMfaza42:=Real_0;
4541:PMMfaza60[10]:=Real_0;
4543:PMMfaza60[11]:=Real_0;
4545:PMMfaza60[12]:=Real_0;
4547:PMMfaza60[13]:=Real_0;
4549:PMMfaza60[14]:=Real_0;
4551:PMMfaza60[15]:=Real_0;
4553:PMMfaza60[16]:=Real_0;
4555:PMMfaza60[17]:=Real_0;
4557:PMMfaza60[18]:=Real_0;
4559:PMMfaza60[19]:=Real_0;
4561:PMMfaza60[1]:=Real_0;
4563:PMMfaza60[20]:=Real_0;
4565:PMMfaza60[21]:=Real_0;
4567:PMMfaza60[22]:=Real_0;
4569:PMMfaza60[23]:=Real_0;
4571:PMMfaza60[24]:=Real_0;
4573:PMMfaza60[25]:=Real_0;
4575:PMMfaza60[26]:=Real_0;
4577:PMMfaza60[27]:=Real_0;
4579:PMMfaza60[28]:=Real_0;
4581:PMMfaza60[29]:=Real_0;
4583:PMMfaza60[2]:=Real_0;
4585:PMMfaza60[30]:=Real_0;
4587:PMMfaza60[31]:=Real_0;
4589:PMMfaza60[32]:=Real_0;
4591:PMMfaza60[33]:=Real_0;
4593:PMMfaza60[34]:=Real_0;
4595:PMMfaza60[35]:=Real_0;
4597:PMMfaza60[36]:=Real_0;
4599:PMMfaza60[37]:=Real_0;
4601:PMMfaza60[38]:=Real_0;
4603:PMMfaza60[39]:=Real_0;
4605:PMMfaza60[3]:=Real_0;
4607:PMMfaza60[40]:=Real_0;
4609:PMMfaza60[41]:=Real_0;
4611:PMMfaza60[42]:=Real_0;
4613:PMMfaza60[4]:=Real_0;
4615:PMMfaza60[5]:=Real_0;
4617:PMMfaza60[6]:=Real_0;
4619:PMMfaza60[7]:=Real_0;
4621:PMMfaza60[8]:=Real_0;
4623:PMMfaza60[9]:=Real_0;
4625:PMMfaza80[10]:=Real_0;
4627:PMMfaza80[11]:=Real_0;
4629:PMMfaza80[12]:=Real_0;
4631:PMMfaza80[13]:=Real_0;
4633:PMMfaza80[14]:=Real_0;
4635:PMMfaza80[15]:=Real_0;
4637:PMMfaza80[16]:=Real_0;
4639:PMMfaza80[17]:=Real_0;
4641:PMMfaza80[18]:=Real_0;
4643:PMMfaza80[19]:=Real_0;
4645:PMMfaza80[1]:=Real_0;
4647:PMMfaza80[20]:=Real_0;
4649:PMMfaza80[21]:=Real_0;
4651:PMMfaza80[22]:=Real_0;
4653:PMMfaza80[23]:=Real_0;
4655:PMMfaza80[24]:=Real_0;
4657:PMMfaza80[25]:=Real_0;
4659:PMMfaza80[26]:=Real_0;
4661:PMMfaza80[27]:=Real_0;
4663:PMMfaza80[28]:=Real_0;
4665:PMMfaza80[29]:=Real_0;
4667:PMMfaza80[2]:=Real_0;
4669:PMMfaza80[30]:=Real_0;
4671:PMMfaza80[31]:=Real_0;
4673:PMMfaza80[32]:=Real_0;
4675:PMMfaza80[33]:=Real_0;
4677:PMMfaza80[34]:=Real_0;
4679:PMMfaza80[35]:=Real_0;
4681:PMMfaza80[36]:=Real_0;
4683:PMMfaza80[37]:=Real_0;
4685:PMMfaza80[38]:=Real_0;
4687:PMMfaza80[39]:=Real_0;
4689:PMMfaza80[3]:=Real_0;
4691:PMMfaza80[40]:=Real_0;
4693:PMMfaza80[41]:=Real_0;
4695:PMMfaza80[42]:=Real_0;
4697:PMMfaza80[4]:=Real_0;
4699:PMMfaza80[5]:=Real_0;
4701:PMMfaza80[6]:=Real_0;
4703:PMMfaza80[7]:=Real_0;
4705:PMMfaza80[8]:=Real_0;
4707:PMMfaza80[9]:=Real_0;
4709:SenzorTemp[1]:=Real_0;
4711:SenzorTemp[2]:=Real_0;
4713:SenzorTemp[3]:=Real_0;
4715:SenzorTemp[4]:=Real_0;
4717:SenzorTemp[5]:=Real_0;
4719:SenzorTemp[6]:=Real_0;
4721:SenzorVlaga[1]:=Real_0;
4723:SenzorVlaga[2]:=Real_0;
4725:SenzorVlaga[3]:=Real_0;
4727:SenzorVlaga[4]:=Real_0;
4729:SenzorVlaga[5]:=Real_0;
4731:SenzorVlaga[6]:=Real_0;
4733:TempAlarmPoint[0]:=Real_0;
4735:TempAlarmPoint[1]:=Real_0;
4737:TempAlarmPoint[2]:=Real_0;
4739:TempAlarmPoint[3]:=Real_0;
4741:TempMaxPoint[0]:=Real_0;
4743:TempMaxPoint[1]:=Real_0;
4745:TempMaxPoint[2]:=Real_0;
4747:TempMaxPoint[3]:=Real_0;
4749:TempPovp[0]:=Real_0;
4751:TempPovp[1]:=Real_0;
4753:TempPovp[2]:=Real_0;
4755:TempPovp[3]:=Real_0;
4757:TempSetPoint[0]:=Real_0;
4759:TempSetPoint[1]:=Real_0;
4761:TempSetPoint[2]:=Real_0;
4763:TempSetPoint[3]:=Real_0;
4765:UPS[1].EstimatedChargeRemaining:=Real_0;
4767:UPS[1].EstimatedMinutesRemaining:=Real_0;
4769:UPS[1].IzhodMocL1:=Real_0;
4771:UPS[1].IzhodMocL2:=Real_0;
4773:UPS[1].IzhodMocL3:=Real_0;
4775:UPS[1].NapetostBaterije:=Real_0;
4777:UPS[1].TemperaturaBaterije:=Real_0;
4779:UPS[1].VhodFrekvencaL1:=Real_0;
4781:UPS[1].VhodFrekvencaL2:=Real_0;
4783:UPS[1].VhodFrekvencaL3:=Real_0;
4785:UPS[1].VhodNapetostL1:=Real_0;
4787:UPS[1].VhodNapetostL2:=Real_0;
4789:UPS[1].VhodNapetostL3:=Real_0;
4791:UPS[2].EstimatedChargeRemaining:=Real_0;
4793:UPS[2].EstimatedMinutesRemaining:=Real_0;
4795:UPS[2].IzhodMocL1:=Real_0;
4797:UPS[2].IzhodMocL2:=Real_0;
4799:UPS[2].IzhodMocL3:=Real_0;
4801:UPS[2].NapetostBaterije:=Real_0;
4803:UPS[2].TemperaturaBaterije:=Real_0;
4805:UPS[2].VhodFrekvencaL1:=Real_0;
4807:UPS[2].VhodFrekvencaL2:=Real_0;
4809:UPS[2].VhodFrekvencaL3:=Real_0;
4811:UPS[2].VhodNapetostL1:=Real_0;
4813:UPS[2].VhodNapetostL2:=Real_0;
4815:UPS[2].VhodNapetostL3:=Real_0;
4817:VlagaPovp[1]:=Real_0;
4819:VlagaPovp[2]:=Real_0;
4821:VlagaPovp[3]:=Real_0;
4823:RazlikaUr:=Real_0;
4825:Klima[1].NastTempHlajenje:=Real_0;
4827:Klima[2].NastTempHlajenje:=Real_0;
4829:Klima[3].NastTempHlajenje:=Real_0;
4831:Klima[4].NastTempHlajenje:=Real_0;
4833:Klima[5].NastTempHlajenje:=Real_0;
4835:Klima[6].NastTempHlajenje:=Real_0;
4837:Klima[1].NastTempGretje:=Real_0;
4839:Klima[2].NastTempGretje:=Real_0;
4841:Klima[3].NastTempGretje:=Real_0;
4843:Klima[4].NastTempGretje:=Real_0;
4845:Klima[5].NastTempGretje:=Real_0;
4847:Klima[6].NastTempGretje:=Real_0;
4849:Klima[1].TempHladneVode:=Real_0;
4851:Klima[2].TempHladneVode:=Real_0;
4853:Klima[3].TempHladneVode:=Real_0;
4855:Klima[4].TempHladneVode:=Real_0;
4857:Klima[5].TempHladneVode:=Real_0;
4859:Klima[6].TempHladneVode:=Real_0;
4861:Klima[1].TempTopleVode:=Real_0;
4863:Klima[2].TempTopleVode:=Real_0;
4865:Klima[3].TempTopleVode:=Real_0;
4867:Klima[4].TempTopleVode:=Real_0;
4869:Klima[5].TempTopleVode:=Real_0;
4871:Klima[6].TempTopleVode:=Real_0;
4873:ZamikVklopa:=Real_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_String : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje STRING*)
(**)
5000:Date_Time[0]:=String_0;
5015:Date_Time[1]:=String_0;
5030:Date_Time[2]:=String_0;
5045:Date_Time[3]:=String_0;
5060:UserCurrentName:=String_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Word : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje INT*)
(**)
0:DateTime.Dan:=Byte_0;
1:DateTime.Leto:=Byte_0;
2:DateTime.Mesec:=Byte_0;
3:DateTime.Minuta:=Byte_0;
4:DateTime.Sekunda:=Byte_0;
5:DateTime.Ura:=Byte_0;
6:ErrorComKlima[1].Code[10]:=Byte_0;
7:ErrorComKlima[1].Code[11]:=Byte_0;
8:ErrorComKlima[1].Code[12]:=Byte_0;
9:ErrorComKlima[1].Code[13]:=Byte_0;
10:ErrorComKlima[1].Code[14]:=Byte_0;
11:ErrorComKlima[1].Code[15]:=Byte_0;
12:ErrorComKlima[1].Code[1]:=Byte_0;
13:ErrorComKlima[1].Code[2]:=Byte_0;
14:ErrorComKlima[1].Code[3]:=Byte_0;
15:ErrorComKlima[1].Code[4]:=Byte_0;
16:ErrorComKlima[1].Code[5]:=Byte_0;
17:ErrorComKlima[1].Code[6]:=Byte_0;
18:ErrorComKlima[1].Code[7]:=Byte_0;
19:ErrorComKlima[1].Code[8]:=Byte_0;
20:ErrorComKlima[1].Code[9]:=Byte_0;
21:ErrorComKlima[1].Status:=Word_01;
22:ErrorComKlima[2].Code[10]:=Byte_0;
23:ErrorComKlima[2].Code[11]:=Byte_0;
24:ErrorComKlima[2].Code[12]:=Byte_0;
25:ErrorComKlima[2].Code[13]:=Byte_0;
26:ErrorComKlima[2].Code[14]:=Byte_0;
27:ErrorComKlima[2].Code[15]:=Byte_0;
28:ErrorComKlima[2].Code[1]:=Byte_0;
29:ErrorComKlima[2].Code[2]:=Byte_0;
30:ErrorComKlima[2].Code[3]:=Byte_0;
31:ErrorComKlima[2].Code[4]:=Byte_0;
32:ErrorComKlima[2].Code[5]:=Byte_0;
33:ErrorComKlima[2].Code[6]:=Byte_0;
34:ErrorComKlima[2].Code[7]:=Byte_0;
35:ErrorComKlima[2].Code[8]:=Byte_0;
36:ErrorComKlima[2].Code[9]:=Byte_0;
37:ErrorComKlima[2].Status:=Word_01;
38:ErrorComKlima[3].Code[10]:=Byte_0;
39:ErrorComKlima[3].Code[11]:=Byte_0;
40:ErrorComKlima[3].Code[12]:=Byte_0;
41:ErrorComKlima[3].Code[13]:=Byte_0;
42:ErrorComKlima[3].Code[14]:=Byte_0;
43:ErrorComKlima[3].Code[15]:=Byte_0;
44:ErrorComKlima[3].Code[1]:=Byte_0;
45:ErrorComKlima[3].Code[2]:=Byte_0;
46:ErrorComKlima[3].Code[3]:=Byte_0;
47:ErrorComKlima[3].Code[4]:=Byte_0;
48:ErrorComKlima[3].Code[5]:=Byte_0;
49:ErrorComKlima[3].Code[6]:=Byte_0;
50:ErrorComKlima[3].Code[7]:=Byte_0;
51:ErrorComKlima[3].Code[8]:=Byte_0;
52:ErrorComKlima[3].Code[9]:=Byte_0;
53:ErrorComKlima[3].Status:=Word_01;
54:ErrorComKlima[4].Code[10]:=Byte_0;
55:ErrorComKlima[4].Code[11]:=Byte_0;
56:ErrorComKlima[4].Code[12]:=Byte_0;
57:ErrorComKlima[4].Code[13]:=Byte_0;
58:ErrorComKlima[4].Code[14]:=Byte_0;
59:ErrorComKlima[4].Code[15]:=Byte_0;
60:ErrorComKlima[4].Code[1]:=Byte_0;
61:ErrorComKlima[4].Code[2]:=Byte_0;
62:ErrorComKlima[4].Code[3]:=Byte_0;
63:ErrorComKlima[4].Code[4]:=Byte_0;
64:ErrorComKlima[4].Code[5]:=Byte_0;
65:ErrorComKlima[4].Code[6]:=Byte_0;
66:ErrorComKlima[4].Code[7]:=Byte_0;
67:ErrorComKlima[4].Code[8]:=Byte_0;
68:ErrorComKlima[4].Code[9]:=Byte_0;
69:ErrorComKlima[4].Status:=Word_01;
70:ErrorComKlima[5].Code[10]:=Byte_0;
71:ErrorComKlima[5].Code[11]:=Byte_0;
72:ErrorComKlima[5].Code[12]:=Byte_0;
73:ErrorComKlima[5].Code[13]:=Byte_0;
74:ErrorComKlima[5].Code[14]:=Byte_0;
75:ErrorComKlima[5].Code[15]:=Byte_0;
76:ErrorComKlima[5].Code[1]:=Byte_0;
77:ErrorComKlima[5].Code[2]:=Byte_0;
78:ErrorComKlima[5].Code[3]:=Byte_0;
79:ErrorComKlima[5].Code[4]:=Byte_0;
80:ErrorComKlima[5].Code[5]:=Byte_0;
81:ErrorComKlima[5].Code[6]:=Byte_0;
82:ErrorComKlima[5].Code[7]:=Byte_0;
83:ErrorComKlima[5].Code[8]:=Byte_0;
84:ErrorComKlima[5].Code[9]:=Byte_0;
85:ErrorComKlima[5].Status:=Word_01;
86:ErrorComKlima[6].Code[10]:=Byte_0;
87:ErrorComKlima[6].Code[11]:=Byte_0;
88:ErrorComKlima[6].Code[12]:=Byte_0;
89:ErrorComKlima[6].Code[13]:=Byte_0;
90:ErrorComKlima[6].Code[14]:=Byte_0;
91:ErrorComKlima[6].Code[15]:=Byte_0;
92:ErrorComKlima[6].Code[1]:=Byte_0;
93:ErrorComKlima[6].Code[2]:=Byte_0;
94:ErrorComKlima[6].Code[3]:=Byte_0;
95:ErrorComKlima[6].Code[4]:=Byte_0;
96:ErrorComKlima[6].Code[5]:=Byte_0;
97:ErrorComKlima[6].Code[6]:=Byte_0;
98:ErrorComKlima[6].Code[7]:=Byte_0;
99:ErrorComKlima[6].Code[8]:=Byte_0;
100:ErrorComKlima[6].Code[9]:=Byte_0;
101:ErrorComKlima[6].Status:=Word_01;
102:ErrorComPMM.Code[10]:=Byte_0;
103:ErrorComPMM.Code[11]:=Byte_0;
104:ErrorComPMM.Code[12]:=Byte_0;
105:ErrorComPMM.Code[13]:=Byte_0;
106:ErrorComPMM.Code[14]:=Byte_0;
107:ErrorComPMM.Code[15]:=Byte_0;
108:ErrorComPMM.Code[1]:=Byte_0;
109:ErrorComPMM.Code[2]:=Byte_0;
110:ErrorComPMM.Code[3]:=Byte_0;
111:ErrorComPMM.Code[4]:=Byte_0;
112:ErrorComPMM.Code[5]:=Byte_0;
113:ErrorComPMM.Code[6]:=Byte_0;
114:ErrorComPMM.Code[7]:=Byte_0;
115:ErrorComPMM.Code[8]:=Byte_0;
116:ErrorComPMM.Code[9]:=Byte_0;
117:ErrorComPMM.Status:=Word_01;
118:ErrorComUPS[1].Code[10]:=Byte_0;
119:ErrorComUPS[1].Code[11]:=Byte_0;
120:ErrorComUPS[1].Code[12]:=Byte_0;
121:ErrorComUPS[1].Code[13]:=Byte_0;
122:ErrorComUPS[1].Code[14]:=Byte_0;
123:ErrorComUPS[1].Code[15]:=Byte_0;
124:ErrorComUPS[1].Code[1]:=Byte_0;
125:ErrorComUPS[1].Code[2]:=Byte_0;
126:ErrorComUPS[1].Code[3]:=Byte_0;
127:ErrorComUPS[1].Code[4]:=Byte_0;
128:ErrorComUPS[1].Code[5]:=Byte_0;
129:ErrorComUPS[1].Code[6]:=Byte_0;
130:ErrorComUPS[1].Code[7]:=Byte_0;
131:ErrorComUPS[1].Code[8]:=Byte_0;
132:ErrorComUPS[1].Code[9]:=Byte_0;
133:ErrorComUPS[1].Status:=Word_01;
134:ErrorComUPS[2].Code[10]:=Byte_0;
135:ErrorComUPS[2].Code[11]:=Byte_0;
136:ErrorComUPS[2].Code[12]:=Byte_0;
137:ErrorComUPS[2].Code[13]:=Byte_0;
138:ErrorComUPS[2].Code[14]:=Byte_0;
139:ErrorComUPS[2].Code[15]:=Byte_0;
140:ErrorComUPS[2].Code[1]:=Byte_0;
141:ErrorComUPS[2].Code[2]:=Byte_0;
142:ErrorComUPS[2].Code[3]:=Byte_0;
143:ErrorComUPS[2].Code[4]:=Byte_0;
144:ErrorComUPS[2].Code[5]:=Byte_0;
145:ErrorComUPS[2].Code[6]:=Byte_0;
146:ErrorComUPS[2].Code[7]:=Byte_0;
147:ErrorComUPS[2].Code[8]:=Byte_0;
148:ErrorComUPS[2].Code[9]:=Byte_0;
149:ErrorComUPS[2].Status:=Word_01;
150:Klima[1].GrelecStatus:=Byte_0;
151:Klima[1].IzhodniVentStatus:=Byte_0;
152:Klima[1].KompresorStatus:=Byte_0;
153:Klima[1].VlazilecStatus:=Byte_0;
154:Klima[2].GrelecStatus:=Byte_0;
155:Klima[2].IzhodniVentStatus:=Byte_0;
156:Klima[2].KompresorStatus:=Byte_0;
157:Klima[2].VlazilecStatus:=Byte_0;
158:Klima[3].GrelecStatus:=Byte_0;
159:Klima[3].IzhodniVentStatus:=Byte_0;
160:Klima[3].KompresorStatus:=Byte_0;
161:Klima[3].VlazilecStatus:=Byte_0;
162:Klima[4].GrelecStatus:=Byte_0;
163:Klima[4].IzhodniVentStatus:=Byte_0;
164:Klima[4].KompresorStatus:=Byte_0;
165:Klima[4].VlazilecStatus:=Byte_0;
166:Klima[5].GrelecStatus:=Byte_0;
167:Klima[5].IzhodniVentStatus:=Byte_0;
168:Klima[5].KompresorStatus:=Byte_0;
169:Klima[5].VlazilecStatus:=Byte_0;
170:Klima[6].GrelecStatus:=Byte_0;
171:Klima[6].IzhodniVentStatus:=Byte_0;
172:Klima[6].KompresorStatus:=Byte_0;
173:Klima[6].VlazilecStatus:=Byte_0;
174:MrezaIzpadVklopDelay[1]:=Word_01;
175:MrezaIzpadVklopDelay[2]:=Word_01;
176:MrezaIzpadVklopDelay[3]:=Word_01;
177:MrezaIzpadVklopDelay[4]:=Word_01;
178:MrezaIzpadVklopDelay[5]:=Word_01;
179:MrezaIzpadVklopDelay[6]:=Word_01;
180:PMM.AlarmPhase[1].C01_16_60to80:=Word_01;
181:PMM.AlarmPhase[1].C01_16_over80:=Word_01;
182:PMM.AlarmPhase[1].C17_32_60to80:=Word_01;
183:PMM.AlarmPhase[1].C17_32_over80:=Word_01;
184:PMM.AlarmPhase[1].C33_42_60to80:=Word_01;
185:PMM.AlarmPhase[1].C33_42_over80:=Word_01;
186:PMM.AlarmPhase[2].C01_16_60to80:=Word_01;
187:PMM.AlarmPhase[2].C01_16_over80:=Word_01;
188:PMM.AlarmPhase[2].C17_32_60to80:=Word_01;
189:PMM.AlarmPhase[2].C17_32_over80:=Word_01;
190:PMM.AlarmPhase[2].C33_42_60to80:=Word_01;
191:PMM.AlarmPhase[2].C33_42_over80:=Word_01;
192:PMM.AlarmPhase[3].C01_16_60to80:=Word_01;
193:PMM.AlarmPhase[3].C01_16_over80:=Word_01;
194:PMM.AlarmPhase[3].C17_32_60to80:=Word_01;
195:PMM.AlarmPhase[3].C17_32_over80:=Word_01;
196:PMM.AlarmPhase[3].C33_42_60to80:=Word_01;
197:PMM.AlarmPhase[3].C33_42_over80:=Word_01;
198:Qstanje[10]:=Byte_0;
199:Qstanje[11]:=Byte_0;
200:Qstanje[12]:=Byte_0;
201:Qstanje[13]:=Byte_0;
202:Qstanje[14]:=Byte_0;
203:Qstanje[15]:=Byte_0;
204:Qstanje[16]:=Byte_0;
205:Qstanje[17]:=Byte_0;
206:Qstanje[18]:=Byte_0;
207:Qstanje[19]:=Byte_0;
208:Qstanje[1]:=Byte_0;
209:Qstanje[20]:=Byte_0;
210:Qstanje[21]:=Byte_0;
211:Qstanje[22]:=Byte_0;
212:Qstanje[23]:=Byte_0;
213:Qstanje[24]:=Byte_0;
214:Qstanje[25]:=Byte_0;
215:Qstanje[26]:=Byte_0;
216:Qstanje[27]:=Byte_0;
217:Qstanje[28]:=Byte_0;
218:Qstanje[29]:=Byte_0;
219:Qstanje[2]:=Byte_0;
220:Qstanje[30]:=Byte_0;
221:Qstanje[31]:=Byte_0;
222:Qstanje[32]:=Byte_0;
223:Qstanje[33]:=Byte_0;
224:Qstanje[34]:=Byte_0;
225:Qstanje[35]:=Byte_0;
226:Qstanje[3]:=Byte_0;
227:Qstanje[4]:=Byte_0;
228:Qstanje[5]:=Byte_0;
229:Qstanje[6]:=Byte_0;
230:Qstanje[7]:=Byte_0;
231:Qstanje[8]:=Byte_0;
232:Qstanje[9]:=Byte_0;
233:UPS[1].InverterStatus:=Word_01;
234:UPS[1].OutputStatus:=Word_01;
235:UPS[1].StatusBaterije:=Word_01;
236:UPS[1].SteviloIzpadovVhodneLinije:=Word_01;
237:UPS[1].UnitStatus:=Word_01;
238:UPS[2].InverterStatus:=Word_01;
239:UPS[2].OutputStatus:=Word_01;
240:UPS[2].StatusBaterije:=Word_01;
241:UPS[2].SteviloIzpadovVhodneLinije:=Word_01;
242:UPS[2].UnitStatus:=Word_01;
243:UserCurrentLevel:=Byte_0;
(*Pisanje UINT*)
(**)
6000:kom_nast_cas_izpada:=Word_01;
;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
(*Modbus Slave Example*)
PROGRAM PLC_PRG_modnet
VAR
Slave_Adresa:BYTE:=2;
Slave_Port:INT:=502;
SlaveSetup:MBS_Setup;
SlavePoll:MBS_Poll;
SlaveAnswer:MBS_Answer;
step: USINT;
end :BOOL;
i: INT;
cycle :BOOL := FALSE; (* First cycle *)
OpenDefaultPort: BOOL;
Write_16: BOOL;
Write_15: BOOL;
Write_5: BOOL;
j: INT;
slavepollwOffset_temp: INT;
slaveanswerwCount_temp: INT;
slaveanswerwoffset_temp: INT;
END_VAR
(* @END_DECLARATION := '0' *)
(*Modbus Slave Example*)
IF Write_16=TRUE THEN (**)
FOR j := 0 TO (slaveanswerwCount_temp-1)/15 BY 1 DO (*vpiše se dword, real*)
wStr_0:=mind[slaveanswerwoffset_temp+j];
wStr_1:=mind[slaveanswerwoffset_temp+j+1];
wStr_2 :=mind[slaveanswerwoffset_temp+j+2];
wStr_3:=mind[slaveanswerwoffset_temp+j+3];
wStr_4:=mind[slaveanswerwoffset_temp+j+4];
wStr_5 :=mind[slaveanswerwoffset_temp+j+5];
wStr_6:=mind[slaveanswerwoffset_temp+j+6];
wStr_7:=mind[slaveanswerwoffset_temp+j+7];
wStr_8:=mind[slaveanswerwoffset_temp+j+8];
wStr_9:=mind[slaveanswerwoffset_temp+j+9];
wStr_10:=mind[slaveanswerwoffset_temp+j+10];
wStr_11:=mind[slaveanswerwoffset_temp+j+11];
wStr_12:=mind[slaveanswerwoffset_temp+j+12];
wStr_13:=mind[slaveanswerwoffset_temp+j+13];
wStr_14:=mind[slaveanswerwoffset_temp+j+14];
bStr_29:=0;
mod_Write_String(index:=slaveanswerwoffset_temp+j); (*vpis real in string*)
END_FOR;
FOR j := 1 TO slaveanswerwCount_temp-1 BY 2 DO (*vpiše se dword, real*)
Word_01:=mind[slaveanswerwoffset_temp+j-1];
Word_23:=mind[slaveanswerwoffset_temp+j];
mod_Write_dWord(index:=slaveanswerwoffset_temp+j); (*vpis real in dword*)
END_FOR;
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO (*vpiše se word*)
Word_01:=mind[slaveanswerwoffset_temp+j];
mod_Write_Word(index:=slaveanswerwoffset_temp+j); (*vpis word*)
END_FOR;
Write_16:=FALSE;
END_IF;
IF Write_5=TRUE OR Write_15=TRUE THEN (**)
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO
Bit_0:=mind_bool[slaveanswerwoffset_temp+j];
mod_Write_Bool(index:=slaveanswerwoffset_temp+j); (*vpis spremembe v spremenljivko*)
END_FOR;
Write_5:=FALSE;
Write_15:=FALSE;
END_IF;
(*iz scade ni komande za branje*)
IF Write_16=FALSE AND Write_5=FALSE AND Write_15=FALSE THEN
mod_Read();(*branje spremenljivk za scado*)
END_IF
(*Close all sockets on corresponding event*)
IF cycle = FALSE THEN
SysCallbackRegister(INDEXOF(Callback_Stop),event_stop);
SysCallbackRegister(INDEXOF(Callback_Reset),event_before_reset);
SysCallbackRegister(INDEXOF(Callback_Reset),event_shutdown);
cycle := TRUE;
END_IF
(*Close all connections via application *)
IF end = TRUE THEN
MBS_CloseAllConnections();
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=FALSE); (*Close port*)
step := 0;
END_IF
IF OpenDefaultPort=TRUE THEN
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=TRUE); (*Close port*)
step := 0;
OpenDefaultPort:=FALSE;
END_IF
(* State machine for setup, poll and answer *)
CASE step OF
0:(**)
SlaveSetup.bUnitIdentifier:=Slave_Adresa;(*Subunitnumber*)
slavesetup.wDefaultPort:=Slave_Port;(*Standartport *)
SlaveSetup.xAdditionalPortActive:=FALSE;(*Port opened or closed*)
SlaveSetup.xSecureMode:=FALSE;(*If TRUE only preset IPs are accepted*)
SlaveSetup.tTimeout:=T#3m;(*Timeout if no communication with slave established*)
SlaveSetup(xStrobe:=TRUE);(*Strobe starts function*)
IF slavesetup.xBusy = FALSE THEN
slavesetup(xstrobe := FALSE);
step := 1 ;
END_IF;
1:(**)
SlavePoll(xStrobe:=TRUE);(*Searching for master commands*)
IF NOT SlavePoll.xBusy THEN
step:=2;
SlavePoll(xStrobe:=FALSE);
END_IF;
2:(**)
step:= 1;
CASE SlavePoll.bFunctionCode OF (*Connect accepted pollparameters with answerparameters*)
8:(**)(*Poll answers*)
;
15:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind_bool[slaveanswer.woffset+i] := slavepoll.xarData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.xarData:=slavepoll.xarData;
Write_15:=TRUE;
16:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind[slaveanswer.woffset+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.wardata := slavepoll.warData;
Write_16:=TRUE;
1,2:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slavepoll.wcount-1 BY 1 DO
slaveanswer.xarData[i]:=mind_bool[slavepoll.woffset+i]; (*Read from Data-array*)
END_FOR
3,4:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slaveanswer.wCount-1 BY 1 DO
slaveanswer.warData[i]:=mind[slavepoll.woffset+i];(*Read from Data-array*)
END_FOR
5:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
mind_bool[slavepoll.woffset]:=slavepoll.xarData[0];(*Write to Data-array*)
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.xarData := slavepoll.xardata;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
Write_5:=TRUE;
6:
slaveanswer.bFunctionCode:= slavepoll.bFunctionCode;
mind[slavepoll.woffset]:= slavepoll.warData[0];(*Write to Data-array*)
slaveanswer.wOffset:= slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wardata := slavepoll.wardata;
23:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
FOR i:= 0 TO slavepoll.wCountAdd-1 BY 1 DO
mind[slavepoll.woffsetadd+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
FOR i := 0 TO slavepoll.wCount BY 1 DO
slaveanswer.warData[i] := mind[1+slavepoll.woffset+i];(*Read from Data-array*)
END_FOR;
END_CASE;
IF slavepoll.xAvailable = TRUE THEN
slaveanswer();(*When Data ready, send answer*)
END_IF
END_CASE;
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_dWord : BOOL
VAR_INPUT
dVAR: DWORD;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
DWord_0:=dVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_Real : BOOL
VAR_INPUT
rVAR: REAL;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
Real_0:=rVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_String : BOOL
VAR_INPUT
sVar: STRING;
start:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
String_0:=LEFT (sVar,29);
mind[start]:=wStr_0;
mind[start+1]:=wStr_1;
mind[start+2]:=wStr_2;
mind[start+3]:=wStr_3;
mind[start+4]:=wStr_4;
mind[start+5]:=wStr_5;
mind[start+6]:=wStr_6;
mind[start+7]:=wStr_7;
mind[start+8]:=wStr_8;
mind[start+9]:=wStr_9;
mind[start+10]:=wStr_10;
mind[start+11]:=wStr_11;
mind[start+12]:=wStr_12;
mind[start+13]:=wStr_13;
bStr_29:=0;
mind[start+14]:=wStr_14;
END_FUNCTION
(* @GLOBAL_VARIABLE_LIST := 'Global_Variables_Modnet' *)
(* @PATH := '' *)
(* @SYMFILEFLAGS := '2048' *)
VAR_GLOBAL
(*delovno polje za modnet komunikacijo*)
mind :ARRAY [0..9999] OF WORD;
mind_bool :ARRAY [0..9999] OF BOOL; (*Buffer-Array*)
(*Delovni markerji //*)
Bit_0 AT %MX0.0 : BOOL;
Byte_0 AT %MB0 : BYTE;
Byte_1 AT %MB1 : BYTE;
Byte_2 AT %MB2 : BYTE;
Byte_3 AT %MB3 : BYTE;
Real_0 AT %MR0:REAL;
DWord_0 AT %MD0:DWORD;
Word_01 AT %MW0:WORD;
Word_23 AT %MW2:WORD;
String_0 AT %MW10:STRING;
wStr_0 AT %MW10:WORD;
wStr_1 AT %MW12:WORD;
wStr_2 AT %MW14:WORD;
wStr_3 AT %MW16:WORD;
wStr_4 AT %MW18:WORD;
wStr_5 AT %MW20:WORD;
wStr_6 AT %MW22:WORD;
wStr_7 AT %MW24:WORD;
wStr_8 AT %MW26:WORD;
wStr_9 AT %MW28:WORD;
wStr_10 AT %MW30:WORD;
wStr_11 AT %MW32:WORD;
wStr_12 AT %MW34:WORD;
wStr_13 AT %MW36:WORD;
wStr_14 AT %MW38:WORD;
bStr_00 AT %MB10:BYTE;
bStr_01 AT %MB11:BYTE;
bStr_02 AT %MB12:BYTE;
bStr_03 AT %MB13:BYTE;
bStr_04 AT %MB14:BYTE;
bStr_05 AT %MB15:BYTE;
bStr_06 AT %MB16:BYTE;
bStr_07 AT %MB17:BYTE;
bStr_08 AT %MB18:BYTE;
bStr_09 AT %MB19:BYTE;
bStr_10 AT %MB20:BYTE;
bStr_11 AT %MB21:BYTE;
bStr_12 AT %MB22:BYTE;
bStr_13 AT %MB23:BYTE;
bStr_14 AT %MB24:BYTE;
bStr_15 AT %MB25:BYTE;
bStr_16 AT %MB26:BYTE;
bStr_17 AT %MB27:BYTE;
bStr_18 AT %MB28:BYTE;
bStr_19 AT %MB29:BYTE;
bStr_20 AT %MB30:BYTE;
bStr_21 AT %MB31:BYTE;
bStr_22 AT %MB32:BYTE;
bStr_23 AT %MB33:BYTE;
bStr_24 AT %MB34:BYTE;
bStr_25 AT %MB35:BYTE;
bStr_26 AT %MB36:BYTE;
bStr_27 AT %MB37:BYTE;
bStr_28 AT %MB38:BYTE;
bStr_29 AT %MB39:BYTE;
(********************************************)
END_VAR
(* @OBJECT_END := 'Global_Variables_Modnet' *)
(* @CONNECTIONS := Global_Variables_Modnet
FILENAME : ''
FILETIME : 0
EXPORT : 0
NUMOFCONNECTIONS : 0
*)
(*KONEC_KODA*)