## Prva stran
variable | 1793 | 1.KORAK | variable_1 | 2.KORAK | KORAKI!
Device name | Tip | število spremenljivk | Tip (izbrani) | Zamenjaj z | 1.V Sheet "variable" skopiraj vsebino iz variable.dbf - iz Citect SCAD-a projekta, ki ga želiš pretvoriti.
IOD_TPV | BCD | 0 | BCD | INT | 2.V polje A3 vpiši Device ime spremenljivk ki se bodo prenašale preko Modnet protokola
| BYTE | 0 | BYTE | BYTE | 3.V polje A6 vpiši ime krmilnika (npr.:PLC1, če je adresa v spremenljivkah PLC1:.NapakaKoncnega_stikala, drugače pusti polje prazno)
OPC name | DIGITAL | 202 | DIGITAL | DIGITAL | 4. Pritisni gumb 1.KORAK (V poljih C3:C10 se izpiše število spremenljivk, ki imajo Device enak tistemu v polju A3)
TPV | INT | 17 | INT | INT | 5. Pritisni gumb 2.KORAK (V Sheet-u variable_1 se naredi seznam spremenljivk, ki se bodo prenačale preko Modnet protokola)
| LONG | 1091 | LONG | LONG | 6. Pritisni gumb 3.KORAK (V poljih C15:C24 se izpiše število spremnljiv po tipih, v poljih F15:F24 se izpiše število potrebni wordow/coilov za prenos spremnljivk)
| REAL | 0 | REAL | REAL | 7. 4.KORAK: V polja C29:C38 je potrebno ročno vpisati začetne naslove spremnljivk. Potrebno je paziti na:
| STRING | 1 | UINT | UINT | *naslov se morajo začeti z lihim številom npr.:1, 101, 551
| UINT | 12 | STRING | STRING | *naslove je potrebno nastaviti tako, da se naslovi sremenljivk ne more prekrivati (naslovi spremenjivk gredo od (začetnega naslova) do (začetnega naslova+število potrebnih wordow))
8. Pritisni gumb 5.KORAK (V Sheet-u variable_2 se naredi seznam spremenljivk, ki so tokrat sortirana po tipih)
9. Pritisni gumb 6.KORAK (V Sheet-u variable_3 se naredi seznam spremenljivk, katerih Device se zamenja z devicom v polju C41)
Trajanje makroja | variable_1 |  |  | 3.KORAK | 10. Pritisni gumb 7.KORAK (V Sheet-u variable_new se generira seznam spremenljivk. To vsebino je potrebno skopirati v variable.dbf)
0 | Tip | število spremenljivk | TIP | št.potrebnih coilov/wordov | *ta korak traja nekoliko dalj časa (odvisno od števila spremenljivk)
| BCD | 0 | BCD | 0 | *če se pojavi težava z adresami ki se začnejo z 0000 (npr.: "00001" se spremeni na "1") je potrebno uporabiti priloženo (prazno) variable.dbf ali v
| BYTE | 0 | BYTE | 0 | ProjectEditoju/VariableTags na poljubni spremenljki nastaviti adreso" 00001"
| DIGITAL | 202 | DIGITAL | 202 (Coil) | 11. Pritisni gumb 8.KORAK in 9.KORAK (V Sheet-u Xsoft se generira koda)
| INT | 17 | INT | 17 (word) | 12. S pritiskom na gumb 10.KORAK se zgenerira EXP koda za Xsoft (Xsoft_EXP)
| LONG | 1091 | LONG | 2182 (word) | 13. S pritiskom na gumb Save*.EXP se avtomatsko generira datoka *.EXP
| REAL | 0 | REAL | 0 (word)
| STRING | 1 | STRING | 15 (word)
| UINT | 12 | UINT | 12 (word)
POZOR!
*V Sheet-u variable mora biti vsebina skopirana od polja A1 naprej (če je katera vrstica prazna makroji ne bodo delovali pravilno)
*Ena "STRING" spremenljivka zasede 15wordow (to pomeni 29 znakov, 1BYTE=1STRING)
|  | 4.KORAK(vpiši ročno) | variable_2 | 5.KORAK | *Dolžina "STRING" spremenljivk je 29 znakov (lahko tudi več vendar ne z uporabno tega dokumenta in XSoft programa,potrebna je modifikacija makrojev in Xsoft programa)
| Tip | Začetni naslov |  | Sortiraj | *Vsi stringi so enake dolžine (29)
| BCD |  |  | BCD | *"BYTE" spremenljivke se v variable.dbf spremenijo v "INT" (prenašanje posameznih bytov ni mogoče, niti naslavaljanje v citectscadi)
| BYTE |  |  | DIGITAL | *Naslovi spremenljivk se morajo obvezno začeti z lihim naslovom (preizkušeno je z začetnimi naslovi, ki se izpišejo po pritisku na gumb Ponastavi)
| DIGITAL | 1 |  | BYTE | *Z pritiskom na gumb RESET se pobriše vsebina vseh Sheet-ov razen Sheet-a variable (makor reset se izvaja precej časa)
| INT | 1 |  | INT | *makroji ne delujejo pravilno,če je v Sheet-u variable več kot 9999 vrstic oz. spremenljivk (število vseh spremnljivk je prikazano v polju B1)
| LONG | 3001 |  | LONG | *če se vsebine iz variable_new ne gre skpirat v variable.dbf datotek, vsebino skopirajte najprej v *.txt datoteko in nato v variable.dbf
| REAL | 4001 |  | REAL | *v polju A14 na Sheet-u Prva stran se prikazuje število ciklop do konca izvedbe makroja (samo za gumb 7.KORAK)
| STRING | 5001 |  | STRING
| UINT | 6001 |  | UINT
| variable_3 | 6.KORAK | variable_new | 7.KORAK
| New Device name | IOD_TPV_TCP |  | Nova variable dbf
|  |  | xSoft | 8.KORAK in 9.KORAK
xSoft koda
xSoft_EXP
Izvoz*.EXP
1.KORAK
2.KORAK
3.KORAK
5.KORAK
6.KORAK
7.KORAK
8.KORAK
9.KORAK
RESET
Ponastavi
10.KORAK
Save*.EXP

## variable
TPVBattery_voltageA1 | UINT | IOD_TPV | TPV:.Battery_voltageA1 | 0 | 400 | 0 | 40 | V | ##.# |  | 6157 | 1 | 0x03c00001
TPVBattery_voltageA2 | UINT | IOD_TPV | TPV:.Battery_voltageA2 | 0 | 400 | 0 | 40 | V | ##.# |  | 6157 | 1 | 0x03c00002
TPVCharge_alternator_voltageA1 | UINT | IOD_TPV | TPV:.Charge_alternator_voltageA1 | 0 | 400 | 0 | 40 | V | ##.# |  | 6157 | 1 | 0x03c00003
TPVCharge_alternator_voltageA2 | UINT | IOD_TPV | TPV:.Charge_alternator_voltageA2 | 0 | 400 | 0 | 40 | V | ###.# |  | 6157 | 1 | 0x03c00004
TPVCirc10CosFi_III | LONG | IOD_TPV | TPV:.Circ10CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00005
TPVCirc10DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ10DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c00006
TPVCirc10DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ10DelovnaMoc_III | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00007
TPVCirc10DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ10DelovnaMoc_L1 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00008
TPVCirc10DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ10DelovnaMoc_L2 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00009
TPVCirc10DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ10DelovnaMoc_L3 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c0000a
TPVCirc10Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ10Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c0000b
TPVCirc10InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ10InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c0000c
TPVCirc10InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ10InduktivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0000d
TPVCirc10JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ10JalovaMoc_L1 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0000e
TPVCirc10JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ10JalovaMoc_L2 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0000f
TPVCirc10JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ10JalovaMoc_L3 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00010
TPVCirc10KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ10KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c00011
TPVCirc10KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ10KapacitivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00012
TPVCirc10MaximumDemand | LONG | IOD_TPV | TPV:.Circ10MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c00013
TPVCirc10Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ10Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00014
TPVCirc10Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ10Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00015
TPVCirc10Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ10Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00016
TPVCirc10Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ10Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00017
TPVCirc10Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ10Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00018
TPVCirc10Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ10Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00019
TPVCirc10NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ10NavideznaMoc_III | 0 | 800 | 0 | 80.0 | kVA | ###.# |  | 6157 | 1 | 0x03c0001a
TPVCirc10NicelniTok | LONG | IOD_TPV | TPV:.Circ10NicelniTok | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c0001b
TPVCirc10PowerFactor_III | LONG | IOD_TPV | TPV:.Circ10PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0001c
TPVCirc10PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ10PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0001d
TPVCirc10PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ10PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0001e
TPVCirc10PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ10PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0001f
TPVCirc10THDI_L1 | LONG | IOD_TPV | TPV:.Circ10THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00020
TPVCirc10THDI_L2 | LONG | IOD_TPV | TPV:.Circ10THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00021
TPVCirc10THDI_L3 | LONG | IOD_TPV | TPV:.Circ10THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00022
TPVCirc10THDV_L1 | LONG | IOD_TPV | TPV:.Circ10THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00023
TPVCirc10THDV_L2 | LONG | IOD_TPV | TPV:.Circ10THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00024
TPVCirc10THDV_L3 | LONG | IOD_TPV | TPV:.Circ10THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00025
TPVCirc10Tok_L1 | LONG | IOD_TPV | TPV:.Circ10Tok_L1 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00026
TPVCirc10Tok_L2 | LONG | IOD_TPV | TPV:.Circ10Tok_L2 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00027
TPVCirc10Tok_L3 | LONG | IOD_TPV | TPV:.Circ10Tok_L3 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00028
TPVCirc10TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ10TokPovprecje_III | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00029
TPVCirc11CosFi_III | LONG | IOD_TPV | TPV:.Circ11CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0002a
TPVCirc11DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ11DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c0002b
TPVCirc11DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ11DelovnaMoc_III | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c0002c
TPVCirc11DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ11DelovnaMoc_L1 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c0002d
TPVCirc11DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ11DelovnaMoc_L2 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c0002e
TPVCirc11DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ11DelovnaMoc_L3 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c0002f
TPVCirc11Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ11Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c00030
TPVCirc11InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ11InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c00031
TPVCirc11InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ11InduktivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00032
TPVCirc11JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ11JalovaMoc_L1 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00033
TPVCirc11JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ11JalovaMoc_L2 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00034
TPVCirc11JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ11JalovaMoc_L3 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00035
TPVCirc11KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ11KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW |  |  | 6157 | 1 | 0x03c00036
TPVCirc11KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ11KapacitivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00037
TPVCirc11MaximumDemand | LONG | IOD_TPV | TPV:.Circ11MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c00038
TPVCirc11Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ11Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00039
TPVCirc11Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ11Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0003a
TPVCirc11Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ11Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0003b
TPVCirc11Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ11Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0003c
TPVCirc11Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ11Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0003d
TPVCirc11Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ11Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0003e
TPVCirc11NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ11NavideznaMoc_III | 0 | 800 | 0 | 80.0 | kVA | ###.# |  | 6157 | 1 | 0x03c0003f
TPVCirc11NicelniTok | LONG | IOD_TPV | TPV:.Circ11NicelniTok | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00040
TPVCirc11PowerFactor_III | LONG | IOD_TPV | TPV:.Circ11PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00041
TPVCirc11PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ11PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00042
TPVCirc11PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ11PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00043
TPVCirc11PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ11PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00044
TPVCirc11THDI_L1 | LONG | IOD_TPV | TPV:.Circ11THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00045
TPVCirc11THDI_L2 | LONG | IOD_TPV | TPV:.Circ11THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00046
TPVCirc11THDI_L3 | LONG | IOD_TPV | TPV:.Circ11THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00047
TPVCirc11THDV_L1 | LONG | IOD_TPV | TPV:.Circ11THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00048
TPVCirc11THDV_L2 | LONG | IOD_TPV | TPV:.Circ11THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00049
TPVCirc11THDV_L3 | LONG | IOD_TPV | TPV:.Circ11THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0004a
TPVCirc11Tok_L1 | LONG | IOD_TPV | TPV:.Circ11Tok_L1 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c0004b
TPVCirc11Tok_L2 | LONG | IOD_TPV | TPV:.Circ11Tok_L2 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c0004c
TPVCirc11Tok_L3 | LONG | IOD_TPV | TPV:.Circ11Tok_L3 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c0004d
TPVCirc11TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ11TokPovprecje_III | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c0004e
TPVCirc12CosFi_III | LONG | IOD_TPV | TPV:.Circ12CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0004f
TPVCirc12DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ12DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c00050
TPVCirc12DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ12DelovnaMoc_III | 0 | 12000 | 0 | 1200.0 | kW | ###.# |  | 6157 | 1 | 0x03c00051
TPVCirc12DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ12DelovnaMoc_L1 | 0 | 12000 | 0 | 1200.0 | kW | ###.# |  | 6157 | 1 | 0x03c00052
TPVCirc12DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ12DelovnaMoc_L2 | 0 | 12000 | 0 | 1200.0 | kW | ###.# |  | 6157 | 1 | 0x03c00053
TPVCirc12DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ12DelovnaMoc_L3 | 0 | 12000 | 0 | 1200.0 | kW | ###.# |  | 6157 | 1 | 0x03c00054
TPVCirc12Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ12Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c00055
TPVCirc12InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ12InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c00056
TPVCirc12InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ12InduktivnaMoc_III | 0 | 12000 | 0 | 1200.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00057
TPVCirc12JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ12JalovaMoc_L1 | 0 | 12000 | 0 | 1200.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00058
TPVCirc12JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ12JalovaMoc_L2 | 0 | 12000 | 0 | 1200.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00059
TPVCirc12JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ12JalovaMoc_L3 | 0 | 12000 | 0 | 1200.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0005a
TPVCirc12KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ12KapacitivnaEnergija | [7 empty] | 6157 | 1 | 0x03c0005b
TPVCirc12KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ12KapacitivnaMoc_III | 0 | 10000 | 0 | 1000.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0005c
TPVCirc12MaximumDemand | LONG | IOD_TPV | TPV:.Circ12MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c0005d
TPVCirc12Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ12Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0005e
TPVCirc12Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ12Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0005f
TPVCirc12Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ12Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00060
TPVCirc12Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ12Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00061
TPVCirc12Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ12Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00062
TPVCirc12Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ12Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00063
TPVCirc12NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ12NavideznaMoc_III | 0 | 12000 | 0 | 1200.0 | kVA | ###.# |  | 6157 | 1 | 0x03c00064
TPVCirc12NicelniTok | LONG | IOD_TPV | TPV:.Circ12NicelniTok | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c00065
TPVCirc12PowerFactor_III | LONG | IOD_TPV | TPV:.Circ12PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00066
TPVCirc12PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ12PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00067
TPVCirc12PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ12PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00068
TPVCirc12PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ12PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00069
TPVCirc12THDI_L1 | LONG | IOD_TPV | TPV:.Circ12THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0006a
TPVCirc12THDI_L2 | LONG | IOD_TPV | TPV:.Circ12THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0006b
TPVCirc12THDI_L3 | LONG | IOD_TPV | TPV:.Circ12THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0006c
TPVCirc12THDV_L1 | LONG | IOD_TPV | TPV:.Circ12THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0006d
TPVCirc12THDV_L2 | LONG | IOD_TPV | TPV:.Circ12THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0006e
TPVCirc12THDV_L3 | LONG | IOD_TPV | TPV:.Circ12THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0006f
TPVCirc12Tok_L1 | LONG | IOD_TPV | TPV:.Circ12Tok_L1 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c00070
TPVCirc12Tok_L2 | LONG | IOD_TPV | TPV:.Circ12Tok_L2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c00071
TPVCirc12Tok_L3 | LONG | IOD_TPV | TPV:.Circ12Tok_L3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c00072
TPVCirc12TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ12TokPovprecje_III | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c00073
TPVCirc13CosFi_III | LONG | IOD_TPV | TPV:.Circ13CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00074
TPVCirc13DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ13DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c00075
TPVCirc13DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ13DelovnaMoc_III | 0 | 4000 | 0 | 400.0 | kW | ###.# |  | 6157 | 1 | 0x03c00076
TPVCirc13DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ13DelovnaMoc_L1 | 0 | 4000 | 0 | 400.0 | kW | ###.# |  | 6157 | 1 | 0x03c00077
TPVCirc13DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ13DelovnaMoc_L2 | 0 | 4000 | 0 | 400.0 | kW | ###.# |  | 6157 | 1 | 0x03c00078
TPVCirc13DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ13DelovnaMoc_L3 | 0 | 4000 | 0 | 400.0 | kW | ###.# |  | 6157 | 1 | 0x03c00079
TPVCirc13Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ13Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c0007a
TPVCirc13InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ13InduktivnaEnergija | [7 empty] | 6157 | 1 | 0x03c0007b
TPVCirc13InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ13InduktivnaMoc_III | 0 | 4000 | 0 | 400.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0007c
TPVCirc13JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ13JalovaMoc_L1 | 0 | 4000 | 0 | 400.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0007d
TPVCirc13JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ13JalovaMoc_L2 | 0 | 4000 | 0 | 400.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0007e
TPVCirc13JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ13JalovaMoc_L3 | 0 | 4000 | 0 | 400.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0007f
TPVCirc13KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ13KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c00080
TPVCirc13KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ13KapacitivnaMoc_III | 0 | 10000 | 0 | 1000.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00081
TPVCirc13MaximumDemand | LONG | IOD_TPV | TPV:.Circ13MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c00082
TPVCirc13Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ13Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00083
TPVCirc13Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ13Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00084
TPVCirc13Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ13Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00085
TPVCirc13Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ13Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00086
TPVCirc13Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ13Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00087
TPVCirc13Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ13Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00088
TPVCirc13NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ13NavideznaMoc_III | 0 | 4000 | 0 | 400.0 | kVA | ###.# |  | 6157 | 1 | 0x03c00089
TPVCirc13NicelniTok | LONG | IOD_TPV | TPV:.Circ13NicelniTok | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c0008a
TPVCirc13PowerFactor_III | LONG | IOD_TPV | TPV:.Circ13PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0008b
TPVCirc13PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ13PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0008c
TPVCirc13PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ13PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0008d
TPVCirc13PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ13PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0008e
TPVCirc13THDI_L1 | LONG | IOD_TPV | TPV:.Circ13THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0008f
TPVCirc13THDI_L2 | LONG | IOD_TPV | TPV:.Circ13THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00090
TPVCirc13THDI_L3 | LONG | IOD_TPV | TPV:.Circ13THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00091
TPVCirc13THDV_L1 | LONG | IOD_TPV | TPV:.Circ13THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00092
TPVCirc13THDV_L2 | LONG | IOD_TPV | TPV:.Circ13THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00093
TPVCirc13THDV_L3 | LONG | IOD_TPV | TPV:.Circ13THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00094
TPVCirc13Tok_L1 | LONG | IOD_TPV | TPV:.Circ13Tok_L1 | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c00095
TPVCirc13Tok_L2 | LONG | IOD_TPV | TPV:.Circ13Tok_L2 | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c00096
TPVCirc13Tok_L3 | LONG | IOD_TPV | TPV:.Circ13Tok_L3 | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c00097
TPVCirc13TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ13TokPovprecje_III | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c00098
TPVCirc14CosFi_III | LONG | IOD_TPV | TPV:.Circ14CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00099
TPVCirc14DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ14DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c0009a
TPVCirc14DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ14DelovnaMoc_III | 0 | 4000 | 0 | 400.0 | kW | ###.# |  | 6157 | 1 | 0x03c0009b
TPVCirc14DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ14DelovnaMoc_L1 | 0 | 4000 | 0 | 400.0 | kW | ###.# |  | 6157 | 1 | 0x03c0009c
TPVCirc14DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ14DelovnaMoc_L2 | 0 | 4000 | 0 | 400.0 | kW | ###.# |  | 6157 | 1 | 0x03c0009d
TPVCirc14DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ14DelovnaMoc_L3 | 0 | 4000 | 0 | 400.0 | kW | ###.# |  | 6157 | 1 | 0x03c0009e
TPVCirc14Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ14Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c0009f
TPVCirc14InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ14InduktivnaEnergija | [5 empty] | ###.# |  | 6157 | 1 | 0x03c000a0
TPVCirc14InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ14InduktivnaMoc_III | 0 | 4000 | 0 | 400.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c000a1
TPVCirc14JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ14JalovaMoc_L1 | 0 | 4000 | 0 | 400.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c000a2
TPVCirc14JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ14JalovaMoc_L2 | 0 | 4000 | 0 | 400.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c000a3
TPVCirc14JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ14JalovaMoc_L3 | 0 | 4000 | 0 | 400.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c000a4
TPVCirc14KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ14KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c000a5
TPVCirc14KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ14KapacitivnaMoc_III | 0 | 10000 | 0 | 1000.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c000a6
TPVCirc14MaximumDemand | LONG | IOD_TPV | TPV:.Circ14MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c000a7
TPVCirc14Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ14Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c000a8
TPVCirc14Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ14Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c000a9
TPVCirc14Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ14Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c000aa
TPVCirc14Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ14Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c000ab
TPVCirc14Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ14Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c000ac
TPVCirc14Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ14Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c000ad
TPVCirc14NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ14NavideznaMoc_III | 0 | 4000 | 0 | 400 | kVA | ###.# |  | 6157 | 1 | 0x03c000ae
TPVCirc14NicelniTok | LONG | IOD_TPV | TPV:.Circ14NicelniTok | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c000af
TPVCirc14PowerFactor_III | LONG | IOD_TPV | TPV:.Circ14PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c000b0
TPVCirc14PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ14PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c000b1
TPVCirc14PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ14PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c000b2
TPVCirc14PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ14PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c000b3
TPVCirc14THDI_L1 | LONG | IOD_TPV | TPV:.Circ14THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c000b4
TPVCirc14THDI_L2 | LONG | IOD_TPV | TPV:.Circ14THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c000b5
TPVCirc14THDI_L3 | LONG | IOD_TPV | TPV:.Circ14THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c000b6
TPVCirc14THDV_L1 | LONG | IOD_TPV | TPV:.Circ14THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c000b7
TPVCirc14THDV_L2 | LONG | IOD_TPV | TPV:.Circ14THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c000b8
TPVCirc14THDV_L3 | LONG | IOD_TPV | TPV:.Circ14THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c000b9
TPVCirc14Tok_L1 | LONG | IOD_TPV | TPV:.Circ14Tok_L1 | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c000ba
TPVCirc14Tok_L2 | LONG | IOD_TPV | TPV:.Circ14Tok_L2 | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c000bb
TPVCirc14Tok_L3 | LONG | IOD_TPV | TPV:.Circ14Tok_L3 | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c000bc
TPVCirc14TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ14TokPovprecje_III | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c000bd
TPVCirc15CosFi_III | LONG | IOD_TPV | TPV:.Circ15CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c000be
TPVCirc15DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ15DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c000bf
TPVCirc15DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ15DelovnaMoc_III | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c000c0
TPVCirc15DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ15DelovnaMoc_L1 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c000c1
TPVCirc15DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ15DelovnaMoc_L2 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c000c2
TPVCirc15DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ15DelovnaMoc_L3 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c000c3
TPVCirc15Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ15Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c000c4
TPVCirc15InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ15InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c000c5
TPVCirc15InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ15InduktivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c000c6
TPVCirc15JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ15JalovaMoc_L1 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c000c7
TPVCirc15JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ15JalovaMoc_L2 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c000c8
TPVCirc15JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ15JalovaMoc_L3 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c000c9
TPVCirc15KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ15KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW |  |  | 6157 | 1 | 0x03c000ca
TPVCirc15KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ15KapacitivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c000cb
TPVCirc15MaximumDemand | LONG | IOD_TPV | TPV:.Circ15MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c000cc
TPVCirc15Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ15Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c000cd
TPVCirc15Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ15Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c000ce
TPVCirc15Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ15Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c000cf
TPVCirc15Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ15Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c000d0
TPVCirc15Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ15Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c000d1
TPVCirc15Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ15Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c000d2
TPVCirc15NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ15NavideznaMoc_III | 0 | 800 | 0 | 80.0 | kVA | ###.# |  | 6157 | 1 | 0x03c000d3
TPVCirc15NicelniTok | LONG | IOD_TPV | TPV:.Circ15NicelniTok | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c000d4
TPVCirc15PowerFactor_III | LONG | IOD_TPV | TPV:.Circ15PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c000d5
TPVCirc15PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ15PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c000d6
TPVCirc15PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ15PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c000d7
TPVCirc15PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ15PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c000d8
TPVCirc15THDI_L1 | LONG | IOD_TPV | TPV:.Circ15THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c000d9
TPVCirc15THDI_L2 | LONG | IOD_TPV | TPV:.Circ15THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c000da
TPVCirc15THDI_L3 | LONG | IOD_TPV | TPV:.Circ15THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c000db
TPVCirc15THDV_L1 | LONG | IOD_TPV | TPV:.Circ15THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c000dc
TPVCirc15THDV_L2 | LONG | IOD_TPV | TPV:.Circ15THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c000dd
TPVCirc15THDV_L3 | LONG | IOD_TPV | TPV:.Circ15THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c000de
TPVCirc15Tok_L1 | LONG | IOD_TPV | TPV:.Circ15Tok_L1 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c000df
TPVCirc15Tok_L2 | LONG | IOD_TPV | TPV:.Circ15Tok_L2 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c000e0
TPVCirc15Tok_L3 | LONG | IOD_TPV | TPV:.Circ15Tok_L3 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c000e1
TPVCirc15TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ15TokPovprecje_III | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c000e2
TPVCirc16CosFi_III | LONG | IOD_TPV | TPV:.Circ16CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c000e3
TPVCirc16DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ16DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c000e4
TPVCirc16DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ16DelovnaMoc_III | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c000e5
TPVCirc16DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ16DelovnaMoc_L1 | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c000e6
TPVCirc16DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ16DelovnaMoc_L2 | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c000e7
TPVCirc16DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ16DelovnaMoc_L3 | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c000e8
TPVCirc16Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ16Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c000e9
TPVCirc16InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ16InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c000ea
TPVCirc16InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ16InduktivnaMoc_III | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c000eb
TPVCirc16JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ16JalovaMoc_L1 | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c000ec
TPVCirc16JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ16JalovaMoc_L2 | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c000ed
TPVCirc16JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ16JalovaMoc_L3 | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c000ee
TPVCirc16KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ16KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c000ef
TPVCirc16KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ16KapacitivnaMoc_III | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c000f0
TPVCirc16MaximumDemand | LONG | IOD_TPV | TPV:.Circ16MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c000f1
TPVCirc16Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ16Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c000f2
TPVCirc16Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ16Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c000f3
TPVCirc16Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ16Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c000f4
TPVCirc16Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ16Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c000f5
TPVCirc16Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ16Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c000f6
TPVCirc16Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ16Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c000f7
TPVCirc16NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ16NavideznaMoc_III | 0 | 1200 | 0 | 120.0 | kVA | ###.# |  | 6157 | 1 | 0x03c000f8
TPVCirc16NicelniTok | LONG | IOD_TPV | TPV:.Circ16NicelniTok | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c000f9
TPVCirc16PowerFactor_III | LONG | IOD_TPV | TPV:.Circ16PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c000fa
TPVCirc16PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ16PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c000fb
TPVCirc16PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ16PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c000fc
TPVCirc16PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ16PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c000fd
TPVCirc16THDI_L1 | LONG | IOD_TPV | TPV:.Circ16THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c000fe
TPVCirc16THDI_L2 | LONG | IOD_TPV | TPV:.Circ16THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c000ff
TPVCirc16THDI_L3 | LONG | IOD_TPV | TPV:.Circ16THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00100
TPVCirc16THDV_L1 | LONG | IOD_TPV | TPV:.Circ16THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00101
TPVCirc16THDV_L2 | LONG | IOD_TPV | TPV:.Circ16THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00102
TPVCirc16THDV_L3 | LONG | IOD_TPV | TPV:.Circ16THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00103
TPVCirc16Tok_L1 | LONG | IOD_TPV | TPV:.Circ16Tok_L1 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00104
TPVCirc16Tok_L2 | LONG | IOD_TPV | TPV:.Circ16Tok_L2 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00105
TPVCirc16Tok_L3 | LONG | IOD_TPV | TPV:.Circ16Tok_L3 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00106
TPVCirc16TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ16TokPovprecje_III | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00107
TPVCirc17CosFi_III | LONG | IOD_TPV | TPV:.Circ17CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00108
TPVCirc17DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ17DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c00109
TPVCirc17DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ17DelovnaMoc_III | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c0010a
TPVCirc17DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ17DelovnaMoc_L1 | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c0010b
TPVCirc17DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ17DelovnaMoc_L2 | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c0010c
TPVCirc17DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ17DelovnaMoc_L3 | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c0010d
TPVCirc17Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ17Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c0010e
TPVCirc17InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ17InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c0010f
TPVCirc17InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ17InduktivnaMoc_III | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00110
TPVCirc17JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ17JalovaMoc_L1 | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00111
TPVCirc17JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ17JalovaMoc_L2 | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00112
TPVCirc17JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ17JalovaMoc_L3 | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00113
TPVCirc17KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ17KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c00114
TPVCirc17KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ17KapacitivnaMoc_III | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00115
TPVCirc17MaximumDemand | LONG | IOD_TPV | TPV:.Circ17MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c00116
TPVCirc17Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ17Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00117
TPVCirc17Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ17Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00118
TPVCirc17Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ17Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00119
TPVCirc17Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ17Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0011a
TPVCirc17Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ17Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0011b
TPVCirc17Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ17Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0011c
TPVCirc17NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ17NavideznaMoc_III | 0 | 1200 | 0 | 120.0 | kVA | ###.# |  | 6157 | 1 | 0x03c0011d
TPVCirc17NicelniTok | LONG | IOD_TPV | TPV:.Circ17NicelniTok | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c0011e
TPVCirc17PowerFactor_III | LONG | IOD_TPV | TPV:.Circ17PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0011f
TPVCirc17PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ17PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00120
TPVCirc17PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ17PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00121
TPVCirc17PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ17PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00122
TPVCirc17THDI_L1 | LONG | IOD_TPV | TPV:.Circ17THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00123
TPVCirc17THDI_L2 | LONG | IOD_TPV | TPV:.Circ17THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00124
TPVCirc17THDI_L3 | LONG | IOD_TPV | TPV:.Circ17THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00125
TPVCirc17THDV_L1 | LONG | IOD_TPV | TPV:.Circ17THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00126
TPVCirc17THDV_L2 | LONG | IOD_TPV | TPV:.Circ17THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00127
TPVCirc17THDV_L3 | LONG | IOD_TPV | TPV:.Circ17THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00128
TPVCirc17Tok_L1 | LONG | IOD_TPV | TPV:.Circ17Tok_L1 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00129
TPVCirc17Tok_L2 | LONG | IOD_TPV | TPV:.Circ17Tok_L2 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c0012a
TPVCirc17Tok_L3 | LONG | IOD_TPV | TPV:.Circ17Tok_L3 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c0012b
TPVCirc17TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ17TokPovprecje_III | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c0012c
TPVCirc18CosFi_III | LONG | IOD_TPV | TPV:.Circ18CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0012d
TPVCirc18DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ18DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c0012e
TPVCirc18DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ18DelovnaMoc_III | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c0012f
TPVCirc18DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ18DelovnaMoc_L1 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00130
TPVCirc18DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ18DelovnaMoc_L2 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00131
TPVCirc18DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ18DelovnaMoc_L3 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00132
TPVCirc18Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ18Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c00133
TPVCirc18InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ18InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c00134
TPVCirc18InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ18InduktivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00135
TPVCirc18JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ18JalovaMoc_L1 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00136
TPVCirc18JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ18JalovaMoc_L2 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00137
TPVCirc18JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ18JalovaMoc_L3 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00138
TPVCirc18KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ18KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c00139
TPVCirc18KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ18KapacitivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0013a
TPVCirc18MaximumDemand | LONG | IOD_TPV | TPV:.Circ18MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c0013b
TPVCirc18Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ18Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0013c
TPVCirc18Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ18Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0013d
TPVCirc18Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ18Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0013e
TPVCirc18Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ18Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0013f
TPVCirc18Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ18Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00140
TPVCirc18Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ18Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00141
TPVCirc18NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ18NavideznaMoc_III | 0 | 800 | 0 | 80.0 | kVA | ###.# |  | 6157 | 1 | 0x03c00142
TPVCirc18NicelniTok | LONG | IOD_TPV | TPV:.Circ18NicelniTok | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00143
TPVCirc18PowerFactor_III | LONG | IOD_TPV | TPV:.Circ18PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00144
TPVCirc18PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ18PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00145
TPVCirc18PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ18PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00146
TPVCirc18PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ18PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00147
TPVCirc18THDI_L1 | LONG | IOD_TPV | TPV:.Circ18THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00148
TPVCirc18THDI_L2 | LONG | IOD_TPV | TPV:.Circ18THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00149
TPVCirc18THDI_L3 | LONG | IOD_TPV | TPV:.Circ18THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0014a
TPVCirc18THDV_L1 | LONG | IOD_TPV | TPV:.Circ18THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0014b
TPVCirc18THDV_L2 | LONG | IOD_TPV | TPV:.Circ18THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0014c
TPVCirc18THDV_L3 | LONG | IOD_TPV | TPV:.Circ18THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0014d
TPVCirc18Tok_L1 | LONG | IOD_TPV | TPV:.Circ18Tok_L1 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c0014e
TPVCirc18Tok_L2 | LONG | IOD_TPV | TPV:.Circ18Tok_L2 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c0014f
TPVCirc18Tok_L3 | LONG | IOD_TPV | TPV:.Circ18Tok_L3 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00150
TPVCirc18TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ18TokPovprecje_III | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00151
TPVCirc19CosFi_III | LONG | IOD_TPV | TPV:.Circ19CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00152
TPVCirc19DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ19DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c00153
TPVCirc19DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ19DelovnaMoc_III | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00154
TPVCirc19DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ19DelovnaMoc_L1 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00155
TPVCirc19DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ19DelovnaMoc_L2 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00156
TPVCirc19DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ19DelovnaMoc_L3 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00157
TPVCirc19Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ19Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c00158
TPVCirc19InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ19InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c00159
TPVCirc19InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ19InduktivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0015a
TPVCirc19JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ19JalovaMoc_L1 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0015b
TPVCirc19JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ19JalovaMoc_L2 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0015c
TPVCirc19JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ19JalovaMoc_L3 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0015d
TPVCirc19KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ19KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c0015e
TPVCirc19KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ19KapacitivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0015f
TPVCirc19MaximumDemand | LONG | IOD_TPV | TPV:.Circ19MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c00160
TPVCirc19Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ19Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00161
TPVCirc19Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ19Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00162
TPVCirc19Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ19Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00163
TPVCirc19Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ19Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00164
TPVCirc19Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ19Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00165
TPVCirc19Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ19Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00166
TPVCirc19NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ19NavideznaMoc_III | 0 | 800 | 0 | 80.0 | kVA | ###.# |  | 6157 | 1 | 0x03c00167
TPVCirc19NicelniTok | LONG | IOD_TPV | TPV:.Circ19NicelniTok | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00168
TPVCirc19PowerFactor_III | LONG | IOD_TPV | TPV:.Circ19PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00169
TPVCirc19PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ19PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0016a
TPVCirc19PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ19PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0016b
TPVCirc19PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ19PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0016c
TPVCirc19THDI_L1 | LONG | IOD_TPV | TPV:.Circ19THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0016d
TPVCirc19THDI_L2 | LONG | IOD_TPV | TPV:.Circ19THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0016e
TPVCirc19THDI_L3 | LONG | IOD_TPV | TPV:.Circ19THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0016f
TPVCirc19THDV_L1 | LONG | IOD_TPV | TPV:.Circ19THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00170
TPVCirc19THDV_L2 | LONG | IOD_TPV | TPV:.Circ19THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00171
TPVCirc19THDV_L3 | LONG | IOD_TPV | TPV:.Circ19THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00172
TPVCirc19Tok_L1 | LONG | IOD_TPV | TPV:.Circ19Tok_L1 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00173
TPVCirc19Tok_L2 | LONG | IOD_TPV | TPV:.Circ19Tok_L2 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00174
TPVCirc19Tok_L3 | LONG | IOD_TPV | TPV:.Circ19Tok_L3 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00175
TPVCirc19TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ19TokPovprecje_III | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00176
TPVCirc1CosFi_III | LONG | IOD_TPV | TPV:.Circ1CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00177
TPVCirc1DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ1DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c00178
TPVCirc1DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ1DelovnaMoc_III | 0 | 3200 | 0 | 320.0 | kW | ###.# |  | 6157 | 1 | 0x03c00179
TPVCirc1DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ1DelovnaMoc_L1 | 0 | 3200 | 0 | 320.0 | kW | ###.# |  | 6157 | 1 | 0x03c0017a
TPVCirc1DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ1DelovnaMoc_L2 | 0 | 3200 | 0 | 320.0 | kW | ###.# |  | 6157 | 1 | 0x03c0017b
TPVCirc1DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ1DelovnaMoc_L3 | 0 | 3200 | 0 | 320.0 | kW | ###.# |  | 6157 | 1 | 0x03c0017c
TPVCirc1Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ1Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c0017d
TPVCirc1InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ1InduktivnaEnergija | 0 | 100000 | 0 | 10000.0 | kW | ####.# |  | 6157 | 1 | 0x03c0017e
TPVCirc1InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ1InduktivnaMoc_III | 0 | 3200 | 0 | 320.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c0017f
TPVCirc1JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ1JalovaMoc_L1 | 0 | 3200 | 0 | 320.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c00180
TPVCirc1JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ1JalovaMoc_L2 | 0 | 3200 | 0 | 320.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c00181
TPVCirc1JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ1JalovaMoc_L3 | 0 | 3200 | 0 | 320.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c00182
TPVCirc1KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ1KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c00183
TPVCirc1KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ1KapacitivnaMoc_III | 0 | 3200 | 0 | 320.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00184
TPVCirc1MaximumDemand | LONG | IOD_TPV | TPV:.Circ1MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c00185
TPVCirc1Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ1Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00186
TPVCirc1Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ1Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00187
TPVCirc1Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ1Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00188
TPVCirc1Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ1Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00189
TPVCirc1Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ1Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0018a
TPVCirc1Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ1Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0018b
TPVCirc1NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ1NavideznaMoc_III | 0 | 3200 | 0 | 320.0 | kVA | ###.# |  | 6157 | 1 | 0x03c0018c
TPVCirc1NicelniTok | LONG | IOD_TPV | TPV:.Circ1NicelniTok | 0 | 3200 | 0 | 320.0 | A | ###.# |  | 6157 | 1 | 0x03c0018d
TPVCirc1PowerFactor_III | LONG | IOD_TPV | TPV:.Circ1PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0018e
TPVCirc1PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ1PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0018f
TPVCirc1PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ1PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00190
TPVCirc1PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ1PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00191
TPVCirc1THDI_L1 | LONG | IOD_TPV | TPV:.Circ1THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00192
TPVCirc1THDI_L2 | LONG | IOD_TPV | TPV:.Circ1THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00193
TPVCirc1THDI_L3 | LONG | IOD_TPV | TPV:.Circ1THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00194
TPVCirc1THDV_L1 | LONG | IOD_TPV | TPV:.Circ1THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00195
TPVCirc1THDV_L2 | LONG | IOD_TPV | TPV:.Circ1THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00196
TPVCirc1THDV_L3 | LONG | IOD_TPV | TPV:.Circ1THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00197
TPVCirc1Tok_L1 | LONG | IOD_TPV | TPV:.Circ1Tok_L1 | 0 | 3200 | 0 | 320.0 | A | ###.# |  | 6157 | 1 | 0x03c00198
TPVCirc1Tok_L2 | LONG | IOD_TPV | TPV:.Circ1Tok_L2 | 0 | 3200 | 0 | 320.0 | A | ###.# |  | 6157 | 1 | 0x03c00199
TPVCirc1Tok_L3 | LONG | IOD_TPV | TPV:.Circ1Tok_L3 | 0 | 3200 | 0 | 320.0 | A | ###.# |  | 6157 | 1 | 0x03c0019a
TPVCirc1TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ1TokPovprecje_III | 0 | 3200 | 0 | 320.0 | A | ###.# |  | 6157 | 1 | 0x03c0019b
TPVCirc20CosFi_III | LONG | IOD_TPV | TPV:.Circ20CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0019c
TPVCirc20DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ20DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c0019d
TPVCirc20DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ20DelovnaMoc_III | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c0019e
TPVCirc20DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ20DelovnaMoc_L1 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c0019f
TPVCirc20DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ20DelovnaMoc_L2 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c001a0
TPVCirc20DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ20DelovnaMoc_L3 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c001a1
TPVCirc20Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ20Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c001a2
TPVCirc20InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ20InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c001a3
TPVCirc20InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ20InduktivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c001a4
TPVCirc20JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ20JalovaMoc_L1 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c001a5
TPVCirc20JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ20JalovaMoc_L2 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c001a6
TPVCirc20JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ20JalovaMoc_L3 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c001a7
TPVCirc20KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ20KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c001a8
TPVCirc20KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ20KapacitivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c001a9
TPVCirc20MaximumDemand | LONG | IOD_TPV | TPV:.Circ20MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c001aa
TPVCirc20Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ20Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c001ab
TPVCirc20Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ20Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c001ac
TPVCirc20Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ20Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c001ad
TPVCirc20Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ20Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c001ae
TPVCirc20Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ20Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c001af
TPVCirc20Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ20Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c001b0
TPVCirc20NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ20NavideznaMoc_III | 0 | 800 | 0 | 80.0 | kVA | ###.# |  | 6157 | 1 | 0x03c001b1
TPVCirc20NicelniTok | LONG | IOD_TPV | TPV:.Circ20NicelniTok | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c001b2
TPVCirc20PowerFactor_III | LONG | IOD_TPV | TPV:.Circ20PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c001b3
TPVCirc20PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ20PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c001b4
TPVCirc20PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ20PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c001b5
TPVCirc20PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ20PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c001b6
TPVCirc20THDI_L1 | LONG | IOD_TPV | TPV:.Circ20THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c001b7
TPVCirc20THDI_L2 | LONG | IOD_TPV | TPV:.Circ20THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c001b8
TPVCirc20THDI_L3 | LONG | IOD_TPV | TPV:.Circ20THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c001b9
TPVCirc20THDV_L1 | LONG | IOD_TPV | TPV:.Circ20THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c001ba
TPVCirc20THDV_L2 | LONG | IOD_TPV | TPV:.Circ20THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c001bb
TPVCirc20THDV_L3 | LONG | IOD_TPV | TPV:.Circ20THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c001bc
TPVCirc20Tok_L1 | LONG | IOD_TPV | TPV:.Circ20Tok_L1 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c001bd
TPVCirc20Tok_L2 | LONG | IOD_TPV | TPV:.Circ20Tok_L2 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c001be
TPVCirc20Tok_L3 | LONG | IOD_TPV | TPV:.Circ20Tok_L3 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c001bf
TPVCirc20TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ20TokPovprecje_III | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c001c0
TPVCirc21CosFi_III | LONG | IOD_TPV | TPV:.Circ21CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c001c1
TPVCirc21DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ21DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c001c2
TPVCirc21DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ21DelovnaMoc_III | 0 | 200 | 0 | 20.0 | kW | ###.# |  | 6157 | 1 | 0x03c001c3
TPVCirc21DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ21DelovnaMoc_L1 | 0 | 200 | 0 | 20.0 | kW | ###.# |  | 6157 | 1 | 0x03c001c4
TPVCirc21DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ21DelovnaMoc_L2 | 0 | 200 | 0 | 20.0 | kW | ###.# |  | 6157 | 1 | 0x03c001c5
TPVCirc21DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ21DelovnaMoc_L3 | 0 | 200 | 0 | 20.0 | kW | ###.# |  | 6157 | 1 | 0x03c001c6
TPVCirc21Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ21Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c001c7
TPVCirc21InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ21InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c001c8
TPVCirc21InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ21InduktivnaMoc_III | 0 | 200 | 0 | 20.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c001c9
TPVCirc21JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ21JalovaMoc_L1 | 0 | 200 | 0 | 20.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c001ca
TPVCirc21JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ21JalovaMoc_L2 | 0 | 200 | 0 | 20.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c001cb
TPVCirc21JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ21JalovaMoc_L3 | 0 | 200 | 0 | 20.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c001cc
TPVCirc21KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ21KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c001cd
TPVCirc21KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ21KapacitivnaMoc_III | 0 | 200 | 0 | 20.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c001ce
TPVCirc21MaximumDemand | LONG | IOD_TPV | TPV:.Circ21MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c001cf
TPVCirc21Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ21Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c001d0
TPVCirc21Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ21Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c001d1
TPVCirc21Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ21Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c001d2
TPVCirc21Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ21Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c001d3
TPVCirc21Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ21Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c001d4
TPVCirc21Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ21Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c001d5
TPVCirc21NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ21NavideznaMoc_III | 0 | 200 | 0 | 20.0 | kVA | ###.# |  | 6157 | 1 | 0x03c001d6
TPVCirc21NicelniTok | LONG | IOD_TPV | TPV:.Circ21NicelniTok | 0 | 200 | 0 | 20.0 | A | ###.# |  | 6157 | 1 | 0x03c001d7
TPVCirc21PowerFactor_III | LONG | IOD_TPV | TPV:.Circ21PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c001d8
TPVCirc21PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ21PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c001d9
TPVCirc21PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ21PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c001da
TPVCirc21PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ21PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c001db
TPVCirc21THDI_L1 | LONG | IOD_TPV | TPV:.Circ21THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c001dc
TPVCirc21THDI_L2 | LONG | IOD_TPV | TPV:.Circ21THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c001dd
TPVCirc21THDI_L3 | LONG | IOD_TPV | TPV:.Circ21THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c001de
TPVCirc21THDV_L1 | LONG | IOD_TPV | TPV:.Circ21THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c001df
TPVCirc21THDV_L2 | LONG | IOD_TPV | TPV:.Circ21THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c001e0
TPVCirc21THDV_L3 | LONG | IOD_TPV | TPV:.Circ21THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c001e1
TPVCirc21Tok_L1 | LONG | IOD_TPV | TPV:.Circ21Tok_L1 | 0 | 200 | 0 | 20.0 | A | ###.# |  | 6157 | 1 | 0x03c001e2
TPVCirc21Tok_L2 | LONG | IOD_TPV | TPV:.Circ21Tok_L2 | 0 | 200 | 0 | 20.0 | A | ###.# |  | 6157 | 1 | 0x03c001e3
TPVCirc21Tok_L3 | LONG | IOD_TPV | TPV:.Circ21Tok_L3 | 0 | 200 | 0 | 20.0 | A | ###.# |  | 6157 | 1 | 0x03c001e4
TPVCirc21TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ21TokPovprecje_III | 0 | 200 | 0 | 20.0 | A | ###.# |  | 6157 | 1 | 0x03c001e5
TPVCirc22CosFi_III | LONG | IOD_TPV | TPV:.Circ22CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c001e6
TPVCirc22DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ22DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c001e7
TPVCirc22DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ22DelovnaMoc_III | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c001e8
TPVCirc22DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ22DelovnaMoc_L1 | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c001e9
TPVCirc22DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ22DelovnaMoc_L2 | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c001ea
TPVCirc22DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ22DelovnaMoc_L3 | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c001eb
TPVCirc22Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ22Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c001ec
TPVCirc22InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ22InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c001ed
TPVCirc22InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ22InduktivnaMoc_III | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c001ee
TPVCirc22JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ22JalovaMoc_L1 | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c001ef
TPVCirc22JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ22JalovaMoc_L2 | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c001f0
TPVCirc22JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ22JalovaMoc_L3 | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c001f1
TPVCirc22KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ22KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c001f2
TPVCirc22KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ22KapacitivnaMoc_III | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c001f3
TPVCirc22MaximumDemand | LONG | IOD_TPV | TPV:.Circ22MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c001f4
TPVCirc22Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ22Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c001f5
TPVCirc22Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ22Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c001f6
TPVCirc22Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ22Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c001f7
TPVCirc22Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ22Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c001f8
TPVCirc22Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ22Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c001f9
TPVCirc22Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ22Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c001fa
TPVCirc22NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ22NavideznaMoc_III | 0 | 1200 | 0 | 120.0 | kVA | ###.# |  | 6157 | 1 | 0x03c001fb
TPVCirc22NicelniTok | LONG | IOD_TPV | TPV:.Circ22NicelniTok | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c001fc
TPVCirc22PowerFactor_III | LONG | IOD_TPV | TPV:.Circ22PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c001fd
TPVCirc22PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ22PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c001fe
TPVCirc22PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ22PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c001ff
TPVCirc22PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ22PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00200
TPVCirc22THDI_L1 | LONG | IOD_TPV | TPV:.Circ22THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00201
TPVCirc22THDI_L2 | LONG | IOD_TPV | TPV:.Circ22THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00202
TPVCirc22THDI_L3 | LONG | IOD_TPV | TPV:.Circ22THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00203
TPVCirc22THDV_L1 | LONG | IOD_TPV | TPV:.Circ22THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00204
TPVCirc22THDV_L2 | LONG | IOD_TPV | TPV:.Circ22THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00205
TPVCirc22THDV_L3 | LONG | IOD_TPV | TPV:.Circ22THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00206
TPVCirc22Tok_L1 | LONG | IOD_TPV | TPV:.Circ22Tok_L1 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00207
TPVCirc22Tok_L2 | LONG | IOD_TPV | TPV:.Circ22Tok_L2 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00208
TPVCirc22Tok_L3 | LONG | IOD_TPV | TPV:.Circ22Tok_L3 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00209
TPVCirc22TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ22TokPovprecje_III | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c0020a
TPVCirc23CosFi_III | LONG | IOD_TPV | TPV:.Circ23CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0020b
TPVCirc23DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ23DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c0020c
TPVCirc23DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ23DelovnaMoc_III | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c0020d
TPVCirc23DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ23DelovnaMoc_L1 | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c0020e
TPVCirc23DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ23DelovnaMoc_L2 | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c0020f
TPVCirc23DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ23DelovnaMoc_L3 | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c00210
TPVCirc23Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ23Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c00211
TPVCirc23InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ23InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c00212
TPVCirc23InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ23InduktivnaMoc_III | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00213
TPVCirc23JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ23JalovaMoc_L1 | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00214
TPVCirc23JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ23JalovaMoc_L2 | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00215
TPVCirc23JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ23JalovaMoc_L3 | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00216
TPVCirc23KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ23KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 |  |  |  | 6157 | 1 | 0x03c00217
TPVCirc23KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ23KapacitivnaMoc_III | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00218
TPVCirc23MaximumDemand | LONG | IOD_TPV | TPV:.Circ23MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c00219
TPVCirc23Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ23Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0021a
TPVCirc23Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ23Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0021b
TPVCirc23Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ23Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0021c
TPVCirc23Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ23Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0021d
TPVCirc23Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ23Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0021e
TPVCirc23Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ23Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0021f
TPVCirc23NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ23NavideznaMoc_III | 0 | 1200 | 0 | 120.0 | kVA | ###.# |  | 6157 | 1 | 0x03c00220
TPVCirc23NicelniTok | LONG | IOD_TPV | TPV:.Circ23NicelniTok | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00221
TPVCirc23PowerFactor_III | LONG | IOD_TPV | TPV:.Circ23PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00222
TPVCirc23PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ23PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00223
TPVCirc23PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ23PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00224
TPVCirc23PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ23PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00225
TPVCirc23THDI_L1 | LONG | IOD_TPV | TPV:.Circ23THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00226
TPVCirc23THDI_L2 | LONG | IOD_TPV | TPV:.Circ23THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00227
TPVCirc23THDI_L3 | LONG | IOD_TPV | TPV:.Circ23THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00228
TPVCirc23THDV_L1 | LONG | IOD_TPV | TPV:.Circ23THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00229
TPVCirc23THDV_L2 | LONG | IOD_TPV | TPV:.Circ23THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0022a
TPVCirc23THDV_L3 | LONG | IOD_TPV | TPV:.Circ23THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0022b
TPVCirc23Tok_L1 | LONG | IOD_TPV | TPV:.Circ23Tok_L1 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c0022c
TPVCirc23Tok_L2 | LONG | IOD_TPV | TPV:.Circ23Tok_L2 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c0022d
TPVCirc23Tok_L3 | LONG | IOD_TPV | TPV:.Circ23Tok_L3 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c0022e
TPVCirc23TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ23TokPovprecje_III | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c0022f
TPVCirc24CosFi_III | LONG | IOD_TPV | TPV:.Circ24CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00230
TPVCirc24DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ24DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c00231
TPVCirc24DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ24DelovnaMoc_III | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c00232
TPVCirc24DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ24DelovnaMoc_L1 | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c00233
TPVCirc24DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ24DelovnaMoc_L2 | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c00234
TPVCirc24DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ24DelovnaMoc_L3 | 0 | 1200 | 0 | 120.0 | kW | ###.# |  | 6157 | 1 | 0x03c00235
TPVCirc24Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ24Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c00236
TPVCirc24InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ24InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c00237
TPVCirc24InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ24InduktivnaMoc_III | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00238
TPVCirc24JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ24JalovaMoc_L1 | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00239
TPVCirc24JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ24JalovaMoc_L2 | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0023a
TPVCirc24JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ24JalovaMoc_L3 | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0023b
TPVCirc24KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ24KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c0023c
TPVCirc24KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ24KapacitivnaMoc_III | 0 | 1200 | 0 | 120.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0023d
TPVCirc24MaximumDemand | LONG | IOD_TPV | TPV:.Circ24MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c0023e
TPVCirc24Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ24Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0023f
TPVCirc24Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ24Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00240
TPVCirc24Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ24Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00241
TPVCirc24Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ24Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00242
TPVCirc24Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ24Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00243
TPVCirc24Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ24Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00244
TPVCirc24NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ24NavideznaMoc_III | 0 | 1200 | 0 | 120.0 | kVA | ###.# |  | 6157 | 1 | 0x03c00245
TPVCirc24NicelniTok | LONG | IOD_TPV | TPV:.Circ24NicelniTok | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00246
TPVCirc24PowerFactor_III | LONG | IOD_TPV | TPV:.Circ24PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00247
TPVCirc24PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ24PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00248
TPVCirc24PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ24PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00249
TPVCirc24PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ24PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0024a
TPVCirc24THDI_L1 | LONG | IOD_TPV | TPV:.Circ24THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0024b
TPVCirc24THDI_L2 | LONG | IOD_TPV | TPV:.Circ24THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0024c
TPVCirc24THDI_L3 | LONG | IOD_TPV | TPV:.Circ24THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0024d
TPVCirc24THDV_L1 | LONG | IOD_TPV | TPV:.Circ24THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0024e
TPVCirc24THDV_L2 | LONG | IOD_TPV | TPV:.Circ24THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0024f
TPVCirc24THDV_L3 | LONG | IOD_TPV | TPV:.Circ24THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00250
TPVCirc24Tok_L1 | LONG | IOD_TPV | TPV:.Circ24Tok_L1 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00251
TPVCirc24Tok_L2 | LONG | IOD_TPV | TPV:.Circ24Tok_L2 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00252
TPVCirc24Tok_L3 | LONG | IOD_TPV | TPV:.Circ24Tok_L3 | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00253
TPVCirc24TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ24TokPovprecje_III | 0 | 1200 | 0 | 120.0 | A | ###.# |  | 6157 | 1 | 0x03c00254
TPVCirc25CosFi_III | LONG | IOD_TPV | TPV:.Circ25CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00255
TPVCirc25DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ25DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c00256
TPVCirc25DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ25DelovnaMoc_III | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00257
TPVCirc25DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ25DelovnaMoc_L1 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00258
TPVCirc25DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ25DelovnaMoc_L2 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00259
TPVCirc25DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ25DelovnaMoc_L3 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c0025a
TPVCirc25Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ25Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c0025b
TPVCirc25InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ25InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c0025c
TPVCirc25InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ25InduktivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0025d
TPVCirc25JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ25JalovaMoc_L1 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0025e
TPVCirc25JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ25JalovaMoc_L2 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0025f
TPVCirc25JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ25JalovaMoc_L3 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00260
TPVCirc25KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ25KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c00261
TPVCirc25KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ25KapacitivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00262
TPVCirc25MaximumDemand | LONG | IOD_TPV | TPV:.Circ25MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c00263
TPVCirc25Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ25Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00264
TPVCirc25Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ25Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00265
TPVCirc25Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ25Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00266
TPVCirc25Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ25Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00267
TPVCirc25Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ25Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00268
TPVCirc25Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ25Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00269
TPVCirc25NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ25NavideznaMoc_III | 0 | 800 | 0 | 80.0 | kVA | ###.# |  | 6157 | 1 | 0x03c0026a
TPVCirc25NicelniTok | LONG | IOD_TPV | TPV:.Circ25NicelniTok | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c0026b
TPVCirc25PowerFactor_III | LONG | IOD_TPV | TPV:.Circ25PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0026c
TPVCirc25PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ25PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0026d
TPVCirc25PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ25PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0026e
TPVCirc25PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ25PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0026f
TPVCirc25THDI_L1 | LONG | IOD_TPV | TPV:.Circ25THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00270
TPVCirc25THDI_L2 | LONG | IOD_TPV | TPV:.Circ25THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00271
TPVCirc25THDI_L3 | LONG | IOD_TPV | TPV:.Circ25THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00272
TPVCirc25THDV_L1 | LONG | IOD_TPV | TPV:.Circ25THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00273
TPVCirc25THDV_L2 | LONG | IOD_TPV | TPV:.Circ25THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00274
TPVCirc25THDV_L3 | LONG | IOD_TPV | TPV:.Circ25THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00275
TPVCirc25Tok_L1 | LONG | IOD_TPV | TPV:.Circ25Tok_L1 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00276
TPVCirc25Tok_L2 | LONG | IOD_TPV | TPV:.Circ25Tok_L2 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00277
TPVCirc25Tok_L3 | LONG | IOD_TPV | TPV:.Circ25Tok_L3 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00278
TPVCirc25TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ25TokPovprecje_III | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00279
TPVCirc2CosFi_III | LONG | IOD_TPV | TPV:.Circ2CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0027a
TPVCirc2DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ2DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c0027b
TPVCirc2DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ2DelovnaMoc_III | 0 | 400 | 0 | 40.0 | kW | ###.# |  | 6157 | 1 | 0x03c0027c
TPVCirc2DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ2DelovnaMoc_L1 | 0 | 400 | 0 | 40.0 | kW | ###.# |  | 6157 | 1 | 0x03c0027d
TPVCirc2DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ2DelovnaMoc_L2 | 0 | 400 | 0 | 40.0 | kW | ###.# |  | 6157 | 1 | 0x03c0027e
TPVCirc2DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ2DelovnaMoc_L3 | 0 | 400 | 0 | 40.0 | kW | ###.# |  | 6157 | 1 | 0x03c0027f
TPVCirc2Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ2Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c00280
TPVCirc2InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ2InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c00281
TPVCirc2InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ2InduktivnaMoc_III | 0 | 400 | 0 | 40.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00282
TPVCirc2JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ2JalovaMoc_L1 | 0 | 400 | 0 | 40.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00283
TPVCirc2JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ2JalovaMoc_L2 | 0 | 400 | 0 | 40.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00284
TPVCirc2JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ2JalovaMoc_L3 | 0 | 400 | 0 | 40.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00285
TPVCirc2KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ2KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c00286
TPVCirc2KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ2KapacitivnaMoc_III | 0 | 400 | 0 | 40.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00287
TPVCirc2MaximumDemand | LONG | IOD_TPV | TPV:.Circ2MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c00288
TPVCirc2Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ2Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00289
TPVCirc2Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ2Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0028a
TPVCirc2Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ2Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0028b
TPVCirc2Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ2Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0028c
TPVCirc2Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ2Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0028d
TPVCirc2Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ2Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0028e
TPVCirc2NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ2NavideznaMoc_III | 0 | 400 | 0 | 40.0 | kVA | ###.# |  | 6157 | 1 | 0x03c0028f
TPVCirc2NicelniTok | LONG | IOD_TPV | TPV:.Circ2NicelniTok | 0 | 400 | 0 | 40.0 | A | ###.# |  | 6157 | 1 | 0x03c00290
TPVCirc2PowerFactor_III | LONG | IOD_TPV | TPV:.Circ2PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00291
TPVCirc2PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ2PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00292
TPVCirc2PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ2PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00293
TPVCirc2PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ2PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00294
TPVCirc2THDI_L1 | LONG | IOD_TPV | TPV:.Circ2THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00295
TPVCirc2THDI_L2 | LONG | IOD_TPV | TPV:.Circ2THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00296
TPVCirc2THDI_L3 | LONG | IOD_TPV | TPV:.Circ2THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00297
TPVCirc2THDV_L1 | LONG | IOD_TPV | TPV:.Circ2THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00298
TPVCirc2THDV_L2 | LONG | IOD_TPV | TPV:.Circ2THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00299
TPVCirc2THDV_L3 | LONG | IOD_TPV | TPV:.Circ2THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0029a
TPVCirc2Tok_L1 | LONG | IOD_TPV | TPV:.Circ2Tok_L1 | 0 | 400 | 0 | 40.0 | A | ###.# |  | 6157 | 1 | 0x03c0029b
TPVCirc2Tok_L2 | LONG | IOD_TPV | TPV:.Circ2Tok_L2 | 0 | 400 | 0 | 40.0 | A | ###.# |  | 6157 | 1 | 0x03c0029c
TPVCirc2Tok_L3 | LONG | IOD_TPV | TPV:.Circ2Tok_L3 | 0 | 400 | 0 | 40.0 | A | ###.# |  | 6157 | 1 | 0x03c0029d
TPVCirc2TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ2TokPovprecje_III | 0 | 400 | 0 | 40.0 | A | ###.# |  | 6157 | 1 | 0x03c0029e
TPVCirc3CosFi_III | LONG | IOD_TPV | TPV:.Circ3CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0029f
TPVCirc3DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ3DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c002a0
TPVCirc3DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ3DelovnaMoc_III | 0 | 400 | 0 | 40.0 | kW | ###.# |  | 6157 | 1 | 0x03c002a1
TPVCirc3DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ3DelovnaMoc_L1 | 0 | 400 | 0 | 40.0 | kW | ###.# |  | 6157 | 1 | 0x03c002a2
TPVCirc3DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ3DelovnaMoc_L2 | 0 | 400 | 0 | 40.0 | kW | ###.# |  | 6157 | 1 | 0x03c002a3
TPVCirc3DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ3DelovnaMoc_L3 | 0 | 400 | 0 | 40.0 | kW | ###.# |  | 6157 | 1 | 0x03c002a4
TPVCirc3Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ3Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c002a5
TPVCirc3InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ3InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c002a6
TPVCirc3InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ3InduktivnaMoc_III | 0 | 400 | 0 | 40.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c002a7
TPVCirc3JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ3JalovaMoc_L1 | 0 | 400 | 0 | 40.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c002a8
TPVCirc3JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ3JalovaMoc_L2 | 0 | 400 | 0 | 40.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c002a9
TPVCirc3JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ3JalovaMoc_L3 | 0 | 400 | 0 | 40.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c002aa
TPVCirc3KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ3KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c002ab
TPVCirc3KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ3KapacitivnaMoc_III | 0 | 400 | 0 | 40.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c002ac
TPVCirc3MaximumDemand | LONG | IOD_TPV | TPV:.Circ3MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c002ad
TPVCirc3Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ3Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c002ae
TPVCirc3Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ3Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c002af
TPVCirc3Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ3Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c002b0
TPVCirc3Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ3Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c002b1
TPVCirc3Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ3Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c002b2
TPVCirc3Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ3Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c002b3
TPVCirc3NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ3NavideznaMoc_III | 0 | 400 | 0 | 40.0 | kVA | ###.# |  | 6157 | 1 | 0x03c002b4
TPVCirc3NicelniTok | LONG | IOD_TPV | TPV:.Circ3NicelniTok | 0 | 400 | 0 | 40.0 | A | ###.# |  | 6157 | 1 | 0x03c002b5
TPVCirc3PowerFactor_III | LONG | IOD_TPV | TPV:.Circ3PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c002b6
TPVCirc3PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ3PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c002b7
TPVCirc3PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ3PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c002b8
TPVCirc3PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ3PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c002b9
TPVCirc3THDI_L1 | LONG | IOD_TPV | TPV:.Circ3THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c002ba
TPVCirc3THDI_L2 | LONG | IOD_TPV | TPV:.Circ3THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c002bb
TPVCirc3THDI_L3 | LONG | IOD_TPV | TPV:.Circ3THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c002bc
TPVCirc3THDV_L1 | LONG | IOD_TPV | TPV:.Circ3THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c002bd
TPVCirc3THDV_L2 | LONG | IOD_TPV | TPV:.Circ3THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c002be
TPVCirc3THDV_L3 | LONG | IOD_TPV | TPV:.Circ3THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c002bf
TPVCirc3Tok_L1 | LONG | IOD_TPV | TPV:.Circ3Tok_L1 | 0 | 400 | 0 | 40.0 | A | ###.# |  | 6157 | 1 | 0x03c002c0
TPVCirc3Tok_L2 | LONG | IOD_TPV | TPV:.Circ3Tok_L2 | 0 | 400 | 0 | 40.0 | A | ###.# |  | 6157 | 1 | 0x03c002c1
TPVCirc3Tok_L3 | LONG | IOD_TPV | TPV:.Circ3Tok_L3 | 0 | 400 | 0 | 40.0 | A | ###.# |  | 6157 | 1 | 0x03c002c2
TPVCirc3TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ3TokPovprecje_III | 0 | 400 | 0 | 40.0 | A | ###.# |  | 6157 | 1 | 0x03c002c3
TPVCirc4CosFi_III | LONG | IOD_TPV | TPV:.Circ4CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c002c4
TPVCirc4DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ4DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c002c5
TPVCirc4DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ4DelovnaMoc_III | 0 | 2000 | 0 | 200.0 | kW | ####.# |  | 6157 | 1 | 0x03c002c6
TPVCirc4DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ4DelovnaMoc_L1 | 0 | 2000 | 0 | 200.0 | kW | ####.# |  | 6157 | 1 | 0x03c002c7
TPVCirc4DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ4DelovnaMoc_L2 | 0 | 2000 | 0 | 200.0 | kW | ####.# |  | 6157 | 1 | 0x03c002c8
TPVCirc4DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ4DelovnaMoc_L3 | 0 | 2000 | 0 | 200.0 | kW | ####.# |  | 6157 | 1 | 0x03c002c9
TPVCirc4Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ4Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c002ca
TPVCirc4InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ4InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c002cb
TPVCirc4InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ4InduktivnaMoc_III | 0 | 2000 | 0 | 200.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c002cc
TPVCirc4JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ4JalovaMoc_L1 | 0 | 2000 | 0 | 200.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c002cd
TPVCirc4JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ4JalovaMoc_L2 | 0 | 2000 | 0 | 200.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c002ce
TPVCirc4JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ4JalovaMoc_L3 | 0 | 2000 | 0 | 200.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c002cf
TPVCirc4KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ4KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c002d0
TPVCirc4KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ4KapacitivnaMoc_III | 0 | 2000 | 0 | 200.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c002d1
TPVCirc4MaximumDemand | LONG | IOD_TPV | TPV:.Circ4MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c002d2
TPVCirc4Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ4Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c002d3
TPVCirc4Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ4Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c002d4
TPVCirc4Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ4Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c002d5
TPVCirc4Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ4Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c002d6
TPVCirc4Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ4Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c002d7
TPVCirc4Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ4Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c002d8
TPVCirc4NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ4NavideznaMoc_III | 0 | 2000 | 0 | 200.0 | kVA | ###.# |  | 6157 | 1 | 0x03c002d9
TPVCirc4NicelniTok | LONG | IOD_TPV | TPV:.Circ4NicelniTok | 0 | 2000 | 0 | 200.0 | A | ###.# |  | 6157 | 1 | 0x03c002da
TPVCirc4PowerFactor_III | LONG | IOD_TPV | TPV:.Circ4PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c002db
TPVCirc4PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ4PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c002dc
TPVCirc4PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ4PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c002dd
TPVCirc4PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ4PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c002de
TPVCirc4THDI_L1 | LONG | IOD_TPV | TPV:.Circ4THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c002df
TPVCirc4THDI_L2 | LONG | IOD_TPV | TPV:.Circ4THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c002e0
TPVCirc4THDI_L3 | LONG | IOD_TPV | TPV:.Circ4THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c002e1
TPVCirc4THDV_L1 | LONG | IOD_TPV | TPV:.Circ4THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c002e2
TPVCirc4THDV_L2 | LONG | IOD_TPV | TPV:.Circ4THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c002e3
TPVCirc4THDV_L3 | LONG | IOD_TPV | TPV:.Circ4THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c002e4
TPVCirc4Tok_L1 | LONG | IOD_TPV | TPV:.Circ4Tok_L1 | 0 | 2000 | 0 | 200.0 | A | ###.# |  | 6157 | 1 | 0x03c002e5
TPVCirc4Tok_L2 | LONG | IOD_TPV | TPV:.Circ4Tok_L2 | 0 | 2000 | 0 | 200.0 | A | ###.# |  | 6157 | 1 | 0x03c002e6
TPVCirc4Tok_L3 | LONG | IOD_TPV | TPV:.Circ4Tok_L3 | 0 | 2000 | 0 | 200.0 | A | ###.# |  | 6157 | 1 | 0x03c002e7
TPVCirc4TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ4TokPovprecje_III | 0 | 2000 | 0 | 200.0 | A | ###.# |  | 6157 | 1 | 0x03c002e8
TPVCirc5CosFi_III | LONG | IOD_TPV | TPV:.Circ5CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c002e9
TPVCirc5DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ5DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c002ea
TPVCirc5DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ5DelovnaMoc_III | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c002eb
TPVCirc5DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ5DelovnaMoc_L1 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c002ec
TPVCirc5DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ5DelovnaMoc_L2 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c002ed
TPVCirc5DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ5DelovnaMoc_L3 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c002ee
TPVCirc5Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ5Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c002ef
TPVCirc5InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ5InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ####.# |  | 6157 | 1 | 0x03c002f0
TPVCirc5InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ5InduktivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c002f1
TPVCirc5JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ5JalovaMoc_L1 | 0 | 800 | 0 | 80.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c002f2
TPVCirc5JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ5JalovaMoc_L2 | 0 | 800 | 0 | 80.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c002f3
TPVCirc5JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ5JalovaMoc_L3 | 0 | 800 | 0 | 80.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c002f4
TPVCirc5KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ5KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW |  |  | 6157 | 1 | 0x03c002f5
TPVCirc5KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ5KapacitivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c002f6
TPVCirc5MaximumDemand | LONG | IOD_TPV | TPV:.Circ5MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c002f7
TPVCirc5Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ5Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c002f8
TPVCirc5Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ5Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c002f9
TPVCirc5Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ5Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c002fa
TPVCirc5Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ5Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c002fb
TPVCirc5Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ5Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c002fc
TPVCirc5Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ5Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c002fd
TPVCirc5NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ5NavideznaMoc_III | 0 | 800 | 0 | 80.0 | kVA | ###.# |  | 6157 | 1 | 0x03c002fe
TPVCirc5NicelniTok | LONG | IOD_TPV | TPV:.Circ5NicelniTok | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c002ff
TPVCirc5PowerFactor_III | LONG | IOD_TPV | TPV:.Circ5PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00300
TPVCirc5PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ5PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00301
TPVCirc5PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ5PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00302
TPVCirc5PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ5PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00303
TPVCirc5THDI_L1 | LONG | IOD_TPV | TPV:.Circ5THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00304
TPVCirc5THDI_L2 | LONG | IOD_TPV | TPV:.Circ5THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00305
TPVCirc5THDI_L3 | LONG | IOD_TPV | TPV:.Circ5THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00306
TPVCirc5THDV_L1 | LONG | IOD_TPV | TPV:.Circ5THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00307
TPVCirc5THDV_L2 | LONG | IOD_TPV | TPV:.Circ5THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00308
TPVCirc5THDV_L3 | LONG | IOD_TPV | TPV:.Circ5THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00309
TPVCirc5Tok_L1 | LONG | IOD_TPV | TPV:.Circ5Tok_L1 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c0030a
TPVCirc5Tok_L2 | LONG | IOD_TPV | TPV:.Circ5Tok_L2 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c0030b
TPVCirc5Tok_L3 | LONG | IOD_TPV | TPV:.Circ5Tok_L3 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c0030c
TPVCirc5TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ5TokPovprecje_III | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c0030d
TPVCirc6CosFi_III | LONG | IOD_TPV | TPV:.Circ6CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0030e
TPVCirc6DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ6DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c0030f
TPVCirc6DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ6DelovnaMoc_III | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00310
TPVCirc6DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ6DelovnaMoc_L1 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00311
TPVCirc6DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ6DelovnaMoc_L2 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00312
TPVCirc6DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ6DelovnaMoc_L3 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00313
TPVCirc6Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ6Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c00314
TPVCirc6InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ6InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c00315
TPVCirc6InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ6InduktivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00316
TPVCirc6JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ6JalovaMoc_L1 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00317
TPVCirc6JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ6JalovaMoc_L2 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00318
TPVCirc6JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ6JalovaMoc_L3 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00319
TPVCirc6KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ6KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c0031a
TPVCirc6KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ6KapacitivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0031b
TPVCirc6MaximumDemand | LONG | IOD_TPV | TPV:.Circ6MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c0031c
TPVCirc6Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ6Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0031d
TPVCirc6Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ6Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0031e
TPVCirc6Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ6Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0031f
TPVCirc6Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ6Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00320
TPVCirc6Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ6Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00321
TPVCirc6Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ6Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00322
TPVCirc6NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ6NavideznaMoc_III | 0 | 800 | 0 | 80.0 | kVA | ###.# |  | 6157 | 1 | 0x03c00323
TPVCirc6NicelniTok | LONG | IOD_TPV | TPV:.Circ6NicelniTok | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00324
TPVCirc6PowerFactor_III | LONG | IOD_TPV | TPV:.Circ6PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00325
TPVCirc6PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ6PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00326
TPVCirc6PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ6PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00327
TPVCirc6PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ6PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00328
TPVCirc6THDI_L1 | LONG | IOD_TPV | TPV:.Circ6THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00329
TPVCirc6THDI_L2 | LONG | IOD_TPV | TPV:.Circ6THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0032a
TPVCirc6THDI_L3 | LONG | IOD_TPV | TPV:.Circ6THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0032b
TPVCirc6THDV_L1 | LONG | IOD_TPV | TPV:.Circ6THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0032c
TPVCirc6THDV_L2 | LONG | IOD_TPV | TPV:.Circ6THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0032d
TPVCirc6THDV_L3 | LONG | IOD_TPV | TPV:.Circ6THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0032e
TPVCirc6Tok_L1 | LONG | IOD_TPV | TPV:.Circ6Tok_L1 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c0032f
TPVCirc6Tok_L2 | LONG | IOD_TPV | TPV:.Circ6Tok_L2 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00330
TPVCirc6Tok_L3 | LONG | IOD_TPV | TPV:.Circ6Tok_L3 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00331
TPVCirc6TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ6TokPovprecje_III | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00332
TPVCirc7CosFi_III | LONG | IOD_TPV | TPV:.Circ7CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00333
TPVCirc7DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ7DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c00334
TPVCirc7DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ7DelovnaMoc_III | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00335
TPVCirc7DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ7DelovnaMoc_L1 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00336
TPVCirc7DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ7DelovnaMoc_L2 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00337
TPVCirc7DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ7DelovnaMoc_L3 | 0 | 800 | 0 | 80.0 | kW | ###.# |  | 6157 | 1 | 0x03c00338
TPVCirc7Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ7Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c00339
TPVCirc7InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ7InduktivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW | ###.# |  | 6157 | 1 | 0x03c0033a
TPVCirc7InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ7InduktivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0033b
TPVCirc7JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ7JalovaMoc_L1 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0033c
TPVCirc7JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ7JalovaMoc_L2 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0033d
TPVCirc7JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ7JalovaMoc_L3 | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c0033e
TPVCirc7KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ7KapacitivnaEnergija | 0 | 10000 | 0 | 1000.0 | kW |  |  | 6157 | 1 | 0x03c0033f
TPVCirc7KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ7KapacitivnaMoc_III | 0 | 800 | 0 | 80.0 | kVAR | ###.# |  | 6157 | 1 | 0x03c00340
TPVCirc7MaximumDemand | LONG | IOD_TPV | TPV:.Circ7MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c00341
TPVCirc7Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ7Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00342
TPVCirc7Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ7Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00343
TPVCirc7Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ7Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00344
TPVCirc7Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ7Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00345
TPVCirc7Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ7Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00346
TPVCirc7Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ7Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00347
TPVCirc7NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ7NavideznaMoc_III | 0 | 800 | 0 | 80.0 | kVA | ###.# |  | 6157 | 1 | 0x03c00348
TPVCirc7NicelniTok | LONG | IOD_TPV | TPV:.Circ7NicelniTok | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00349
TPVCirc7PowerFactor_III | LONG | IOD_TPV | TPV:.Circ7PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0034a
TPVCirc7PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ7PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0034b
TPVCirc7PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ7PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0034c
TPVCirc7PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ7PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0034d
TPVCirc7THDI_L1 | LONG | IOD_TPV | TPV:.Circ7THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0034e
TPVCirc7THDI_L2 | LONG | IOD_TPV | TPV:.Circ7THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0034f
TPVCirc7THDI_L3 | LONG | IOD_TPV | TPV:.Circ7THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00350
TPVCirc7THDV_L1 | LONG | IOD_TPV | TPV:.Circ7THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00351
TPVCirc7THDV_L2 | LONG | IOD_TPV | TPV:.Circ7THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00352
TPVCirc7THDV_L3 | LONG | IOD_TPV | TPV:.Circ7THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00353
TPVCirc7Tok_L1 | LONG | IOD_TPV | TPV:.Circ7Tok_L1 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00354
TPVCirc7Tok_L2 | LONG | IOD_TPV | TPV:.Circ7Tok_L2 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00355
TPVCirc7Tok_L3 | LONG | IOD_TPV | TPV:.Circ7Tok_L3 | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00356
TPVCirc7TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ7TokPovprecje_III | 0 | 800 | 0 | 80.0 | A | ###.# |  | 6157 | 1 | 0x03c00357
TPVCirc8CosFi_III | LONG | IOD_TPV | TPV:.Circ8CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00358
TPVCirc8DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ8DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c00359
TPVCirc8DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ8DelovnaMoc_III | 0 | 4000 | 0 | 400.0 | kW | ####.# |  | 6157 | 1 | 0x03c0035a
TPVCirc8DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ8DelovnaMoc_L1 | 0 | 4000 | 0 | 400.0 | kW | ####.# |  | 6157 | 1 | 0x03c0035b
TPVCirc8DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ8DelovnaMoc_L2 | 0 | 4000 | 0 | 400.0 | kW | ####.# |  | 6157 | 1 | 0x03c0035c
TPVCirc8DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ8DelovnaMoc_L3 | 0 | 4000 | 0 | 400.0 | kW | ####.# |  | 6157 | 1 | 0x03c0035d
TPVCirc8Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ8Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c0035e
TPVCirc8InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ8InduktivnaEnergija | 0 | 100000 | 0 | 10000.0 | kW | ####.# |  | 6157 | 1 | 0x03c0035f
TPVCirc8InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ8InduktivnaMoc_III | 0 | 4000 | 0 | 400.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c00360
TPVCirc8JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ8JalovaMoc_L1 | 0 | 4000 | 0 | 400.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c00361
TPVCirc8JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ8JalovaMoc_L2 | 0 | 4000 | 0 | 400.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c00362
TPVCirc8JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ8JalovaMoc_L3 | 0 | 4000 | 0 | 400.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c00363
TPVCirc8KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ8KapacitivnaEnergija | 0 | 100000 | 0 | 10000.0 | kW | ####.# |  | 6157 | 1 | 0x03c00364
TPVCirc8KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ8KapacitivnaMoc_III | 0 | 4000 | 0 | 400.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c00365
TPVCirc8MaximumDemand | LONG | IOD_TPV | TPV:.Circ8MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c00366
TPVCirc8Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ8Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00367
TPVCirc8Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ8Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00368
TPVCirc8Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ8Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00369
TPVCirc8Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ8Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0036a
TPVCirc8Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ8Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0036b
TPVCirc8Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ8Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0036c
TPVCirc8NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ8NavideznaMoc_III | 0 | 4000 | 0 | 400.0 | kVA | ###.# |  | 6157 | 1 | 0x03c0036d
TPVCirc8NicelniTok | LONG | IOD_TPV | TPV:.Circ8NicelniTok | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c0036e
TPVCirc8PowerFactor_III | LONG | IOD_TPV | TPV:.Circ8PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0036f
TPVCirc8PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ8PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00370
TPVCirc8PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ8PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00371
TPVCirc8PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ8PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00372
TPVCirc8THDI_L1 | LONG | IOD_TPV | TPV:.Circ8THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00373
TPVCirc8THDI_L2 | LONG | IOD_TPV | TPV:.Circ8THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00374
TPVCirc8THDI_L3 | LONG | IOD_TPV | TPV:.Circ8THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00375
TPVCirc8THDV_L1 | LONG | IOD_TPV | TPV:.Circ8THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00376
TPVCirc8THDV_L2 | LONG | IOD_TPV | TPV:.Circ8THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00377
TPVCirc8THDV_L3 | LONG | IOD_TPV | TPV:.Circ8THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00378
TPVCirc8Tok_L1 | LONG | IOD_TPV | TPV:.Circ8Tok_L1 | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c00379
TPVCirc8Tok_L2 | LONG | IOD_TPV | TPV:.Circ8Tok_L2 | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c0037a
TPVCirc8Tok_L3 | LONG | IOD_TPV | TPV:.Circ8Tok_L3 | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c0037b
TPVCirc8TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ8TokPovprecje_III | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c0037c
TPVCirc9CosFi_III | LONG | IOD_TPV | TPV:.Circ9CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c0037d
TPVCirc9DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ9DelovnaEnergija |  |  | 0 |  |  |  |  | 6157 | 1 | 0x03c0037e
TPVCirc9DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ9DelovnaMoc_III | 0 | 4000 | 0 | 400.0 | kW | ####.# |  | 6157 | 1 | 0x03c0037f
TPVCirc9DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ9DelovnaMoc_L1 | 0 | 4000 | 0 | 400.0 | kW | ####.# |  | 6157 | 1 | 0x03c00380
TPVCirc9DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ9DelovnaMoc_L2 | 0 | 4000 | 0 | 400.0 | kW | ####.# |  | 6157 | 1 | 0x03c00381
TPVCirc9DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ9DelovnaMoc_L3 | 0 | 4000 | 0 | 400.0 | kW | ####.# |  | 6157 | 1 | 0x03c00382
TPVCirc9Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ9Frekvenca_L1 | 0 | 600 | 0 | 60.0 | Hz | ##.# |  | 6157 | 1 | 0x03c00383
TPVCirc9InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ9InduktivnaEnergija | 0 | 100000 | 0 | 10000.0 | kW | ####.# |  | 6157 | 1 | 0x03c00384
TPVCirc9InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ9InduktivnaMoc_III | 0 | 4000 | 0 | 400.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c00385
TPVCirc9JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ9JalovaMoc_L1 | 0 | 4000 | 0 | 400.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c00386
TPVCirc9JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ9JalovaMoc_L2 | 0 | 4000 | 0 | 400.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c00387
TPVCirc9JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ9JalovaMoc_L3 | 0 | 4000 | 0 | 400.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c00388
TPVCirc9KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ9KapacitivnaEnergija | 0 | 100000 | 0 | 10000.0 | kW | ####.# |  | 6157 | 1 | 0x03c00389
TPVCirc9KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ9KapacitivnaMoc_III | 0 | 4000 | 0 | 400.0 | kVAR | ####.# |  | 6157 | 1 | 0x03c0038a
TPVCirc9MaximumDemand | LONG | IOD_TPV | TPV:.Circ9MaximumDemand | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x03c0038b
TPVCirc9Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ9Napetost_L1_L2 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0038c
TPVCirc9Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ9Napetost_L1_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0038d
TPVCirc9Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ9Napetost_L2_L3 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c0038e
TPVCirc9Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ9Napetost_L2_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c0038f
TPVCirc9Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ9Napetost_L3_L1 | 0 | 4500 | 0 | 450.0 | V | ###.# |  | 6157 | 1 | 0x03c00390
TPVCirc9Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ9Napetost_L3_N | 0 | 2700 | 0 | 270.0 | V | ###.# |  | 6157 | 1 | 0x03c00391
TPVCirc9NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ9NavideznaMoc_III | 0 | 4000 | 0 | 400.0 | kVA | ###.# |  | 6157 | 1 | 0x03c00392
TPVCirc9NicelniTok | LONG | IOD_TPV | TPV:.Circ9NicelniTok | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c00393
TPVCirc9PowerFactor_III | LONG | IOD_TPV | TPV:.Circ9PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00394
TPVCirc9PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ9PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00395
TPVCirc9PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ9PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00396
TPVCirc9PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ9PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## |  | 6157 | 1 | 0x03c00397
TPVCirc9THDI_L1 | LONG | IOD_TPV | TPV:.Circ9THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00398
TPVCirc9THDI_L2 | LONG | IOD_TPV | TPV:.Circ9THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c00399
TPVCirc9THDI_L3 | LONG | IOD_TPV | TPV:.Circ9THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0039a
TPVCirc9THDV_L1 | LONG | IOD_TPV | TPV:.Circ9THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0039b
TPVCirc9THDV_L2 | LONG | IOD_TPV | TPV:.Circ9THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0039c
TPVCirc9THDV_L3 | LONG | IOD_TPV | TPV:.Circ9THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# |  | 6157 | 1 | 0x03c0039d
TPVCirc9Tok_L1 | LONG | IOD_TPV | TPV:.Circ9Tok_L1 | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c0039e
TPVCirc9Tok_L2 | LONG | IOD_TPV | TPV:.Circ9Tok_L2 | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c0039f
TPVCirc9Tok_L3 | LONG | IOD_TPV | TPV:.Circ9Tok_L3 | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c003a0
TPVCirc9TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ9TokPovprecje_III | 0 | 4000 | 0 | 400.0 | A | ###.# |  | 6157 | 1 | 0x03c003a1
TPVCoolant_temperatureA1 | INT | IOD_TPV | TPV:.Coolant_temperatureA1 | -50 | 20000 | -50 | 200 | řC | ##.# |  | 6157 | 1 | 0x03c003a2
TPVCoolant_temperatureA2 | INT | IOD_TPV | TPV:.Coolant_temperatureA2 | -50 | 2000 | -50 | 200 | řC | ###.# |  | 6157 | 1 | 0x03c003a3
TPVDA3_rocno | DIGITAL | IOD_TPV | TPV:.DA3_rocno | [7 empty] | 6157 | 1 | 0x03c003b0
TPVDA3motorni_pogon_okvara | DIGITAL | IOD_TPV | TPV:.DA3motorni_pogon_okvara | [7 empty] | 6157 | 1 | 0x03c003c0
TPVdelovna_energ_trenutno | INT | IOD_TPV | TPV:.delovna_energ_trenutno | [7 empty] | 6157 | 1 | 0x03c003d0
TPVdelovna_energija_prej | INT | IOD_TPV | TPV:.delovna_energija_prej | [7 empty] | 6157 | 1 | 0x03c003d1
TPVDW_Napake1 | LONG | IOD_TPV | TPV:.DW_Napake1 | [7 empty] | 6157 | 1 | 0x03c003d2
TPVDW_Napake2 | LONG | IOD_TPV | TPV:.DW_Napake2 | [7 empty] | 6157 | 1 | 0x03c003d3
TPVDW_Napake3 | LONG | IOD_TPV | TPV:.DW_Napake3 | [7 empty] | 6157 | 1 | 0x03c003d4
TPVEngine_speedA1 | UINT | IOD_TPV | TPV:.Engine_speedA1 | 0 | 6000 | 0 | 6000 | obr/min | #### |  | 6157 | 1 | 0x03c003d5
TPVEngine_speedA2 | UINT | IOD_TPV | TPV:.Engine_speedA2 | 0 | 6000 | 0 | 6000 | obr/min | #### |  | 6157 | 1 | 0x03c003d6
TPV_Generator_current_lag_leadA1 | INT | IOD_TPV | TPV:.Generator_current_lag_leadA1 | -180 | 180 | -180 | 180 | ř | #### |  | 6157 | 1 | 0x03c003d7
TPV_Generator_current_lag_leadA2 | INT | IOD_TPV | TPV:.Generator_current_lag_leadA2 | -180 | 180 | -180 | 180 | ř | #### |  | 6157 | 1 | 0x03c003d8
TPV_Generator_earth_currentA1 | LONG | IOD_TPV | TPV:.Generator_earth_currentA1 | 0 | 4000 | 0 | 400.0 | A | ###.# | tok | 6157 | 1 | 0x03c003d9
TPV_Generator_earth_currentA2 | LONG | IOD_TPV | TPV:.Generator_earth_currentA2 | 0 | 4000 | 0 | 400.0 | A | ###.# | tok | 6157 | 1 | 0x03c003da
TPV_Generator_frequencyA1 | UINT | IOD_TPV | TPV:.Generator_frequencyA1 | 0 | 700 | 0 | 70 | Hz | ##.# | frekvenca | 6157 | 1 | 0x03c003db
TPV_Generator_frequencyA2 | UINT | IOD_TPV | TPV:.Generator_frequencyA2 | 0 | 700 | 0 | 70 | Hz | ##.# | frekvenca | 6157 | 1 | 0x03c003dc
TPV_Generator_L1_currentA1 | LONG | IOD_TPV | TPV:.Generator_L1_currentA1 | 0 | 4000 | 0 | 400.0 | A | ###.# | tok | 6157 | 1 | 0x03c003dd
TPV_Generator_L1_currentA2 | LONG | IOD_TPV | TPV:.Generator_L1_currentA2 | 0 | 4000 | 0 | 400.0 | A | ###.# | tok | 6157 | 1 | 0x03c003de
TPV_Generator_L1_L2_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L1_L2_voltageA1 | 0 | 4500 | 0 | 450.0 | V | ###.# | napetost | 6157 | 1 | 0x03c003df
TPV_Generator_L1_L2_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L1_L2_voltageA2 | 0 | 4500 | 0 | 450.0 | V | ###.# | napetost | 6157 | 1 | 0x03c003e0
TPV_Generator_L1_N_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L1_N_voltageA1 | 0 | 2700 | 0 | 270.0 | A | ###.# | napetost | 6157 | 1 | 0x03c003e1
TPV_Generator_L1_N_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L1_N_voltageA2 | 0 | 2700 | 0 | 270.0 | A | ###.# | napetost | 6157 | 1 | 0x03c003e2
TPV_Generator_L1_wattsA1 | LONG | IOD_TPV | TPV:.Generator_L1_wattsA1 | 0 | 4000 | 0 | 400.0 | kW | ###.# | moc | 6157 | 1 | 0x03c003e3
TPV_Generator_L1_wattsA2 | LONG | IOD_TPV | TPV:.Generator_L1_wattsA2 | 0 | 4000 | 0 | 400.0 | kW | ###.# | moc | 6157 | 1 | 0x03c003e4
TPV_Generator_L2_currentA1 | LONG | IOD_TPV | TPV:.Generator_L2_currentA1 | 0 | 4000 | 0 | 400.0 | A | ###.# | tok | 6157 | 1 | 0x03c003e5
TPV_Generator_L2_currentA2 | LONG | IOD_TPV | TPV:.Generator_L2_currentA2 | 0 | 4000 | 0 | 400.0 | A | ###.# | tok | 6157 | 1 | 0x03c003e6
TPV_Generator_L2_L3_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L2_L3_voltageA1 | 0 | 4500 | 0 | 450.0 | V | ###.# | napetost | 6157 | 1 | 0x03c003e7
TPV_Generator_L2_L3_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L2_L3_voltageA2 | 0 | 4500 | 0 | 450.0 | V | ###.# | napetost | 6157 | 1 | 0x03c003e8
TPV_Generator_L2_N_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L2_N_voltageA1 | 0 | 2700 | 0 | 270.0 | V | ###.# | napetost | 6157 | 1 | 0x03c003e9
TPV_Generator_L2_N_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L2_N_voltageA2 | 0 | 2700 | 0 | 270.0 | V | ###.# | napetost | 6157 | 1 | 0x03c003ea
TPV_Generator_L2_wattsA1 | LONG | IOD_TPV | TPV:.Generator_L2_wattsA1 | 0 | 4000 | 0 | 400.0 | kW | ###.# | moc | 6157 | 1 | 0x03c003eb
TPV_Generator_L2_wattsA2 | LONG | IOD_TPV | TPV:.Generator_L2_wattsA2 | 0 | 4000 | 0 | 400.0 | kW | ###.# | moc | 6157 | 1 | 0x03c003ec
TPV_Generator_L3_currentA1 | LONG | IOD_TPV | TPV:.Generator_L3_currentA1 | 0 | 4000 | 0 | 400.0 | A | ###.# | tok | 6157 | 1 | 0x03c003ed
TPV_Generator_L3_currentA2 | LONG | IOD_TPV | TPV:.Generator_L3_currentA2 | 0 | 4000 | 0 | 400.0 | A | ###.# | tok | 6157 | 1 | 0x03c003ee
TPV_Generator_L3_L1_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L3_L1_voltageA1 | 0 | 4500 | 0 | 450.0 | V | ###.# | napetost | 6157 | 1 | 0x03c003ef
TPV_Generator_L3_L1_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L3_L1_voltageA2 | 0 | 4500 | 0 | 450.0 | V | ###.# | napetost | 6157 | 1 | 0x03c003f0
TPV_Generator_L3_N_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L3_N_voltageA1 | 0 | 2700 | 0 | 270.0 | V | ###.# | napetost | 6157 | 1 | 0x03c003f1
TPV_Generator_L3_N_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L3_N_voltageA2 | 0 | 2700 | 0 | 270.0 | V | ###.# | napetost | 6157 | 1 | 0x03c003f2
TPV_Generator_L3_wattsA1 | LONG | IOD_TPV | TPV:.Generator_L3_wattsA1 | 0 | 4000 | 0 | 400.0 | kW | ###.# | moc | 6157 | 1 | 0x03c003f3
TPV_Generator_L3_wattsA2 | LONG | IOD_TPV | TPV:.Generator_L3_wattsA2 | 0 | 4000 | 0 | 400.0 | kW | ###.# | moc | 6157 | 1 | 0x03c003f4
TPV_Generator_phase_rotationA1 | UINT | IOD_TPV | TPV:.Generator_phase_rotationA1 | 0 | 2 | 0 | 2 | ř | # |  | 6157 | 1 | 0x03c003f5
TPV_Generator_phase_rotationA2 | UINT | IOD_TPV | TPV:.Generator_phase_rotationA2 | 0 | 2 | 0 | 2 | ř | # |  | 6157 | 1 | 0x03c003f6
TPVIzpad_CAN_med_K1_K2 | DIGITAL | IOD_TPV | TPV:.Izpad_CAN_med_K1_K2 | [7 empty] | 6157 | 1 | 0x03c00400
TPVjalova_energ_trenutno | INT | IOD_TPV | TPV:.jalova_energ_trenutno | [7 empty] | 6157 | 1 | 0x03c00410
TPVjalova_energija_prej | INT | IOD_TPV | TPV:.jalova_energija_prej | [7 empty] | 6157 | 1 | 0x03c00411
TPVKomanda | INT | IOD_TPV | TPV:.Komanda | [7 empty] | 6157 | 1 | 0x03c00412
TPVMI4agr_nap_RGM_A1 | DIGITAL | IOD_TPV | TPV:.MI4agr_nap_RGM_A1 | [7 empty] | 6157 | 1 | 0x03c00420
TPVMI4agr_nap_RGM_A2 | DIGITAL | IOD_TPV | TPV:.MI4agr_nap_RGM_A2 | [7 empty] | 6157 | 1 | 0x03c00430
TPVMI4DA1_2Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4DA1_2Q1_izklop | [7 empty] | 6157 | 1 | 0x03c00440
TPVMI4DA1_2Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4DA1_2Q1_vklop | [7 empty] | 6157 | 1 | 0x03c00450
TPVMI4DA1_del | DIGITAL | IOD_TPV | TPV:.MI4DA1_del | [7 empty] | 6157 | 1 | 0x03c00460
TPVMI4DA1_prip | DIGITAL | IOD_TPV | TPV:.MI4DA1_prip | [7 empty] | 6157 | 1 | 0x03c00470
TPVMI4DA1_rezerva | DIGITAL | IOD_TPV | TPV:.MI4DA1_rezerva | [7 empty] | 6157 | 1 | 0x03c00480
TPVMI4DA1_sinh | DIGITAL | IOD_TPV | TPV:.MI4DA1_sinh | [7 empty] | 6157 | 1 | 0x03c00490
TPVMI4DA1_zagon | DIGITAL | IOD_TPV | TPV:.MI4DA1_zagon | [7 empty] | 6157 | 1 | 0x03c004a0
TPVMI4DA2_2Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4DA2_2Q1_izklop | [7 empty] | 6157 | 1 | 0x03c004b0
TPVMI4DA2_2Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4DA2_2Q1_vklop | [7 empty] | 6157 | 1 | 0x03c004c0
TPVMI4DA2_del | DIGITAL | IOD_TPV | TPV:.MI4DA2_del | [7 empty] | 6157 | 1 | 0x03c004d0
TPVMI4DA2_prip | DIGITAL | IOD_TPV | TPV:.MI4DA2_prip | [7 empty] | 6157 | 1 | 0x03c004e0
TPVMI4DA2_rezerva | DIGITAL | IOD_TPV | TPV:.MI4DA2_rezerva | [7 empty] | 6157 | 1 | 0x03c004f0
TPVMI4DA2_sinh | DIGITAL | IOD_TPV | TPV:.MI4DA2_sinh | [7 empty] | 6157 | 1 | 0x03c00500
TPVMI4DA2_zagon | DIGITAL | IOD_TPV | TPV:.MI4DA2_zagon | [7 empty] | 6157 | 1 | 0x03c00510
TPVMI4del_zascA1_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_11Q1 | [7 empty] | 6157 | 1 | 0x03c00520
TPVMI4del_zascA1_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_12Q1 | [7 empty] | 6157 | 1 | 0x03c00530
TPVMI4del_zascA1_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_13Q1 | [7 empty] | 6157 | 1 | 0x03c00540
TPVMI4del_zascA1_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_14Q1 | [7 empty] | 6157 | 1 | 0x03c00550
TPVMI4del_zascA1_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_15Q1 | [7 empty] | 6157 | 1 | 0x03c00560
TPVMI4del_zascA1_16Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_16Q1 | [7 empty] | 6157 | 1 | 0x03c00570
TPVMI4del_zascA1_17Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_17Q1 | [7 empty] | 6157 | 1 | 0x03c00580
TPVMI4del_zascA1_2Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_2Q1 | [7 empty] | 6157 | 1 | 0x03c00590
TPVMI4del_zascA2_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA2_11Q1 | [7 empty] | 6157 | 1 | 0x03c005a0
TPVMI4del_zascA2_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA2_12Q1 | [7 empty] | 6157 | 1 | 0x03c005b0
TPVMI4del_zascA2_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA2_13Q1 | [7 empty] | 6157 | 1 | 0x03c005c0
TPVMI4del_zascA2_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA2_14Q1 | [7 empty] | 6157 | 1 | 0x03c005d0
TPVMI4K2agr_nap_RGM_A3 | DIGITAL | IOD_TPV | TPV:.MI4K2agr_nap_RGM_A3 | [7 empty] | 6157 | 1 | 0x03c005e0
TPVMI4K2DA3_2Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4K2DA3_2Q1_izklop | [7 empty] | 6157 | 1 | 0x03c005f0
TPVMI4K2DA3_2Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4K2DA3_2Q1_vklop | [7 empty] | 6157 | 1 | 0x03c00600
TPVMI4K2del_zasc0_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_11Q1 | [7 empty] | 6157 | 1 | 0x03c00610
TPVMI4K2del_zasc0_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_12Q1 | [7 empty] | 6157 | 1 | 0x03c00620
TPVMI4K2del_zasc0_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_13Q1 | [7 empty] | 6157 | 1 | 0x03c00630
TPVMI4K2del_zasc0_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_14Q1 | [7 empty] | 6157 | 1 | 0x03c00640
TPVMI4K2del_zasc0_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_15Q1 | [7 empty] | 6157 | 1 | 0x03c00650
TPVMI4K2del_zasc0_16Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_16Q1 | [7 empty] | 6157 | 1 | 0x03c00660
TPVMI4K2del_zasc0_17Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_17Q1 | [7 empty] | 6157 | 1 | 0x03c00670
TPVMI4K2del_zasc0_18Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_18Q1 | [7 empty] | 6157 | 1 | 0x03c00680
TPVMI4K2del_zasc0_19Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_19Q1 | [7 empty] | 6157 | 1 | 0x03c00690
TPVMI4K2del_zasc0_20Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_20Q1 | [7 empty] | 6157 | 1 | 0x03c006a0
TPVMI4K2del_zasc0_21Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_21Q1 | [7 empty] | 6157 | 1 | 0x03c006b0
TPVMI4K2del_zasc0_22Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_22Q1 | [7 empty] | 6157 | 1 | 0x03c006c0
TPVMI4K2del_zasc0_23Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_23Q1 | [7 empty] | 6157 | 1 | 0x03c006d0
TPVMI4K2del_zascA3_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zascA3_11Q1 | [7 empty] | 6157 | 1 | 0x03c006e0
TPVMI4K2del_zascA3_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zascA3_12Q1 | [7 empty] | 6157 | 1 | 0x03c006f0
TPVMI4K2del_zascA3_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zascA3_13Q1 | [7 empty] | 6157 | 1 | 0x03c00700
TPVMI4K2del_zascA3_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zascA3_14Q1 | [7 empty] | 6157 | 1 | 0x03c00710
TPVMI4K2del_zascA3_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zascA3_15Q1 | [7 empty] | 6157 | 1 | 0x03c00720
TPVMI4K2motorA3_1Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4K2motorA3_1Q1_prip | [7 empty] | 6157 | 1 | 0x03c00730
TPVMI4K2motorA3_2Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4K2motorA3_2Q1_prip | [7 empty] | 6157 | 1 | 0x03c00740
TPVMI4K2mrez_nap_RGM_A3 | DIGITAL | IOD_TPV | TPV:.MI4K2mrez_nap_RGM_A3 | [7 empty] | 6157 | 1 | 0x03c00750
TPVMI4K2mrezaA3_1Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4K2mrezaA3_1Q1_izklop | [7 empty] | 6157 | 1 | 0x03c00760
TPVMI4K2mrezaA3_1Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4K2mrezaA3_1Q1_vklop | [7 empty] | 6157 | 1 | 0x03c00770
TPVMI4K2prenap_zasc0_OK | DIGITAL | IOD_TPV | TPV:.MI4K2prenap_zasc0_OK | [7 empty] | 6157 | 1 | 0x03c00780
TPVMI4K2prenap_zascA3_OK | DIGITAL | IOD_TPV | TPV:.MI4K2prenap_zascA3_OK | [7 empty] | 6157 | 1 | 0x03c00790
TPVMI4K2rocni_izk0_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_11Q1 | [7 empty] | 6157 | 1 | 0x03c007a0
TPVMI4K2rocni_izk0_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_12Q1 | [7 empty] | 6157 | 1 | 0x03c007b0
TPVMI4K2rocni_izk0_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_13Q1 | [7 empty] | 6157 | 1 | 0x03c007c0
TPVMI4K2rocni_izk0_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_14Q1 | [7 empty] | 6157 | 1 | 0x03c007d0
TPVMI4K2rocni_izk0_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_15Q1 | [7 empty] | 6157 | 1 | 0x03c007e0
TPVMI4K2rocni_izk0_16Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_16Q1 | [7 empty] | 6157 | 1 | 0x03c007f0
TPVMI4K2rocni_izk0_17Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_17Q1 | [7 empty] | 6157 | 1 | 0x03c00800
TPVMI4K2rocni_izk0_18Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_18Q1 | [7 empty] | 6157 | 1 | 0x03c00810
TPVMI4K2rocni_izk0_19Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_19Q1 | [7 empty] | 6157 | 1 | 0x03c00820
TPVMI4K2rocni_izk0_20Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_20Q1 | [7 empty] | 6157 | 1 | 0x03c00830
TPVMI4K2rocni_izk0_21Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_21Q1 | [7 empty] | 6157 | 1 | 0x03c00840
TPVMI4K2rocni_izk0_22Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_22Q1 | [7 empty] | 6157 | 1 | 0x03c00850
TPVMI4K2rocni_izk0_23Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_23Q1 | [7 empty] | 6157 | 1 | 0x03c00860
TPVMI4K2rocni_izkA3_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izkA3_11Q1 | [7 empty] | 6157 | 1 | 0x03c00870
TPVMI4K2rocni_izkA3_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izkA3_12Q1 | [7 empty] | 6157 | 1 | 0x03c00880
TPVMI4K2rocni_izkA3_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izkA3_13Q1 | [7 empty] | 6157 | 1 | 0x03c00890
TPVMI4K2rocni_izkA3_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izkA3_14Q1 | [7 empty] | 6157 | 1 | 0x03c008a0
TPVMI4K2rocni_izkA3_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izkA3_15Q1 | [7 empty] | 6157 | 1 | 0x03c008b0
TPVMI4K2stik0_11Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_11Q1_vkl | [7 empty] | 6157 | 1 | 0x03c008c0
TPVMI4K2stik0_12Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_12Q1_vkl | [7 empty] | 6157 | 1 | 0x03c008d0
TPVMI4K2stik0_13Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_13Q1_vkl | [7 empty] | 6157 | 1 | 0x03c008e0
TPVMI4K2stik0_14Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_14Q1_vkl | [7 empty] | 6157 | 1 | 0x03c008f0
TPVMI4K2stik0_15Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_15Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00900
TPVMI4K2stik0_16Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_16Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00910
TPVMI4K2stik0_17Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_17Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00920
TPVMI4K2stik0_18Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_18Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00930
TPVMI4K2stik0_19Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_19Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00940
TPVMI4K2stik0_1Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_1Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00950
TPVMI4K2stik0_20Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_20Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00960
TPVMI4K2stik0_21Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_21Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00970
TPVMI4K2stik0_22Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_22Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00980
TPVMI4K2stik0_23Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_23Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00990
TPVMI4K2stikA3_11Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_11Q1_vkl | [7 empty] | 6157 | 1 | 0x03c009a0
TPVMI4K2stikA3_12Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_12Q1_vkl | [7 empty] | 6157 | 1 | 0x03c009b0
TPVMI4K2stikA3_13Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_13Q1_vkl | [7 empty] | 6157 | 1 | 0x03c009c0
TPVMI4K2stikA3_14Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_14Q1_vkl | [7 empty] | 6157 | 1 | 0x03c009d0
TPVMI4K2stikA3_15Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_15Q1_vkl | [7 empty] | 6157 | 1 | 0x03c009e0
TPVMI4K2stikA3_1Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_1Q1_vkl | [7 empty] | 6157 | 1 | 0x03c009f0
TPVMI4K2stikA3_2Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_2Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00a00
TPVMI4krmDA_daljinsko | DIGITAL | IOD_TPV | TPV:.MI4krmDA_daljinsko | [7 empty] | 6157 | 1 | 0x03c00a10
TPVMI4motorA1_1Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4motorA1_1Q1_prip | [7 empty] | 6157 | 1 | 0x03c00a20
TPVMI4motorA1_2Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4motorA1_2Q1_prip | [7 empty] | 6157 | 1 | 0x03c00a30
TPVMI4motorA2_1Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4motorA2_1Q1_prip | [7 empty] | 6157 | 1 | 0x03c00a40
TPVMI4motorA2_2Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4motorA2_2Q1_prip | [7 empty] | 6157 | 1 | 0x03c00a50
TPVMI4motorA2_6Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4motorA2_6Q1_prip | [7 empty] | 6157 | 1 | 0x03c00a60
TPVMI4mrez_nap_RGM_A1 | DIGITAL | IOD_TPV | TPV:.MI4mrez_nap_RGM_A1 | [7 empty] | 6157 | 1 | 0x03c00a70
TPVMI4mrez_nap_RGM_A2 | DIGITAL | IOD_TPV | TPV:.MI4mrez_nap_RGM_A2 | [7 empty] | 6157 | 1 | 0x03c00a80
TPVMI4mrezaA1_1Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4mrezaA1_1Q1_izklop | [7 empty] | 6157 | 1 | 0x03c00a90
TPVMI4mrezaA1_1Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4mrezaA1_1Q1_vklop | [7 empty] | 6157 | 1 | 0x03c00aa0
TPVMI4mrezaA2_1Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4mrezaA2_1Q1_izklop | [7 empty] | 6157 | 1 | 0x03c00ab0
TPVMI4mrezaA2_1Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4mrezaA2_1Q1_vklop | [7 empty] | 6157 | 1 | 0x03c00ac0
TPVMI4napaka_alarm_DA1 | DIGITAL | IOD_TPV | TPV:.MI4napaka_alarm_DA1 | [7 empty] | 6157 | 1 | 0x03c00ad0
TPVMI4napaka_alarm_DA2 | DIGITAL | IOD_TPV | TPV:.MI4napaka_alarm_DA2 | [7 empty] | 6157 | 1 | 0x03c00ae0
TPVMI4prenap_zascA1_OK | DIGITAL | IOD_TPV | TPV:.MI4prenap_zascA1_OK | [7 empty] | 6157 | 1 | 0x03c00af0
TPVMI4prenap_zascA2_OK | DIGITAL | IOD_TPV | TPV:.MI4prenap_zascA2_OK | [7 empty] | 6157 | 1 | 0x03c00b00
TPVMI4rezerva_DA1 | DIGITAL | IOD_TPV | TPV:.MI4rezerva_DA1 | [7 empty] | 6157 | 1 | 0x03c00b10
TPVMI4rocni_izkA1_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_11Q1 | [7 empty] | 6157 | 1 | 0x03c00b20
TPVMI4rocni_izkA1_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_12Q1 | [7 empty] | 6157 | 1 | 0x03c00b30
TPVMI4rocni_izkA1_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_13Q1 | [7 empty] | 6157 | 1 | 0x03c00b40
TPVMI4rocni_izkA1_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_14Q1 | [7 empty] | 6157 | 1 | 0x03c00b50
TPVMI4rocni_izkA1_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_15Q1 | [7 empty] | 6157 | 1 | 0x03c00b60
TPVMI4rocni_izkA1_16Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_16Q1 | [7 empty] | 6157 | 1 | 0x03c00b70
TPVMI4rocni_izkA1_17Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_17Q1 | [7 empty] | 6157 | 1 | 0x03c00b80
TPVMI4rocni_izkA2_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA2_11Q1 | [7 empty] | 6157 | 1 | 0x03c00b90
TPVMI4rocni_izkA2_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA2_12Q1 | [7 empty] | 6157 | 1 | 0x03c00ba0
TPVMI4rocni_izkA2_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA2_13Q1 | [7 empty] | 6157 | 1 | 0x03c00bb0
TPVMI4rocni_izkA2_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA2_14Q1 | [7 empty] | 6157 | 1 | 0x03c00bc0
TPVMI4sinhroniziranje_DA1 | DIGITAL | IOD_TPV | TPV:.MI4sinhroniziranje_DA1 | [7 empty] | 6157 | 1 | 0x03c00bd0
TPVMI4sinhroniziranje_DA2 | DIGITAL | IOD_TPV | TPV:.MI4sinhroniziranje_DA2 | [7 empty] | 6157 | 1 | 0x03c00be0
TPVMI4splosna_napaka_DA1 | DIGITAL | IOD_TPV | TPV:.MI4splosna_napaka_DA1 | [7 empty] | 6157 | 1 | 0x03c00bf0
TPVMI4splosna_napaka_DA2 | DIGITAL | IOD_TPV | TPV:.MI4splosna_napaka_DA2 | [7 empty] | 6157 | 1 | 0x03c00c00
TPVMI4stikA1_11Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_11Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00c10
TPVMI4stikA1_12Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_12Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00c20
TPVMI4stikA1_13Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_13Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00c30
TPVMI4stikA1_14Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_14Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00c40
TPVMI4stikA1_15Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_15Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00c50
TPVMI4stikA1_16Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_16Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00c60
TPVMI4stikA1_17Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_17Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00c70
TPVMI4stikA1_1Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_1Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00c80
TPVMI4stikA1_2Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_2Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00c90
TPVMI4stikA1_6Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_6Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00ca0
TPVMI4stikA2_11Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_11Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00cb0
TPVMI4stikA2_12Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_12Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00cc0
TPVMI4stikA2_13Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_13Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00cd0
TPVMI4stikA2_14Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_14Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00ce0
TPVMI4stikA2_1Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_1Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00cf0
TPVMI4stikA2_2Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_2Q1_vkl | [7 empty] | 6157 | 1 | 0x03c00d00
TPVMI4vezno_6Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4vezno_6Q1_izklop | [7 empty] | 6157 | 1 | 0x03c00d10
TPVMI4vezno_6Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4vezno_6Q1_vklop | [7 empty] | 6157 | 1 | 0x03c00d20
TPVMI4vzporedno_del_nikoli | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_nikoli | [7 empty] | 6157 | 1 | 0x03c00d30
TPVMI4vzporedno_del_nikoli_info | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_nikoli_info | [7 empty] | 6157 | 1 | 0x03c00d40
TPVMI4vzporedno_del_po_potrebi | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_po_potrebi | [7 empty] | 6157 | 1 | 0x03c00d50
TPVMI4vzporedno_del_po_potrebi_info | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_po_potrebi_info | [7 empty] | 6157 | 1 | 0x03c00d60
TPVMI4vzporedno_del_vedno | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_vedno | [7 empty] | 6157 | 1 | 0x03c00d70
TPVMI4vzporedno_del_vedno_info | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_vedno_info | [7 empty] | 6157 | 1 | 0x03c00d80
TPVMI4zaganjanje_DA1 | DIGITAL | IOD_TPV | TPV:.MI4zaganjanje_DA1 | [7 empty] | 6157 | 1 | 0x03c00d90
TPVMI4zaganjanje_DA2 | DIGITAL | IOD_TPV | TPV:.MI4zaganjanje_DA2 | [7 empty] | 6157 | 1 | 0x03c00da0
TPVmrezaDA3motorni_pogon_okvara | DIGITAL | IOD_TPV | TPV:.mrezaDA3motorni_pogon_okvara | [7 empty] | 6157 | 1 | 0x03c00db0
TPVmrezaDA3stikalo_okvara | DIGITAL | IOD_TPV | TPV:.mrezaDA3stikalo_okvara | [7 empty] | 6157 | 1 | 0x03c00dc0
TPVNapaka_v_kom_cirk_DA1 | DIGITAL | IOD_TPV | TPV:.Napaka_v_kom_cirk_DA1 | [7 empty] | 6157 | 1 | 0x03c00dd0
TPVNapaka_v_kom_cirk_DA2 | DIGITAL | IOD_TPV | TPV:.Napaka_v_kom_cirk_DA2 | [7 empty] | 6157 | 1 | 0x03c00de0
TPVNapakaCOMModBus | DIGITAL | IOD_TPV | TPV:.NapakaCOMModBus | [7 empty] | 6157 | 1 | 0x03c00df0
TPVNapakaVKomunikaciji_Circutor1 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor1 | [7 empty] | 6157 | 1 | 0x03c00e00
TPVNapakaVKomunikaciji_Circutor10 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor10 | [7 empty] | 6157 | 1 | 0x03c00e10
TPVNapakaVKomunikaciji_Circutor11 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor11 | [7 empty] | 6157 | 1 | 0x03c00e20
TPVNapakaVKomunikaciji_Circutor12 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor12 | [7 empty] | 6157 | 1 | 0x03c00e30
TPVNapakaVKomunikaciji_Circutor13 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor13 | [7 empty] | 6157 | 1 | 0x03c00e40
TPVNapakaVKomunikaciji_Circutor14 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor14 | [7 empty] | 6157 | 1 | 0x03c00e50
TPVNapakaVKomunikaciji_Circutor15 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor15 | [7 empty] | 6157 | 1 | 0x03c00e60
TPVNapakaVKomunikaciji_Circutor16 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor16 | [7 empty] | 6157 | 1 | 0x03c00e70
TPVNapakaVKomunikaciji_Circutor17 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor17 | [7 empty] | 6157 | 1 | 0x03c00e80
TPVNapakaVKomunikaciji_Circutor18 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor18 | [7 empty] | 6157 | 1 | 0x03c00e90
TPVNapakaVKomunikaciji_Circutor19 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor19 | [7 empty] | 6157 | 1 | 0x03c00ea0
TPVNapakaVKomunikaciji_Circutor2 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor2 | [7 empty] | 6157 | 1 | 0x03c00eb0
TPVNapakaVKomunikaciji_Circutor20 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor20 | [7 empty] | 6157 | 1 | 0x03c00ec0
TPVNapakaVKomunikaciji_Circutor21 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor21 | [7 empty] | 6157 | 1 | 0x03c00ed0
TPVNapakaVKomunikaciji_Circutor22 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor22 | [7 empty] | 6157 | 1 | 0x03c00ee0
TPVNapakaVKomunikaciji_Circutor23 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor23 | [7 empty] | 6157 | 1 | 0x03c00ef0
TPVNapakaVKomunikaciji_Circutor24 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor24 | [7 empty] | 6157 | 1 | 0x03c00f00
TPVNapakaVKomunikaciji_Circutor25 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor25 | [7 empty] | 6157 | 1 | 0x03c00f10
TPVNapakaVKomunikaciji_Circutor3 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor3 | [7 empty] | 6157 | 1 | 0x03c00f20
TPVNapakaVKomunikaciji_Circutor4 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor4 | [7 empty] | 6157 | 1 | 0x03c00f30
TPVNapakaVKomunikaciji_Circutor5 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor5 | [7 empty] | 6157 | 1 | 0x03c00f40
TPVNapakaVKomunikaciji_Circutor6 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor6 | [7 empty] | 6157 | 1 | 0x03c00f50
TPVNapakaVKomunikaciji_Circutor7 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor7 | [7 empty] | 6157 | 1 | 0x03c00f60
TPVNapakaVKomunikaciji_Circutor8 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor8 | [7 empty] | 6157 | 1 | 0x03c00f70
TPVNapakaVKomunikaciji_Circutor9 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor9 | [7 empty] | 6157 | 1 | 0x03c00f80
TPVNastaviDanMI | INT | IOD_TPV | TPV:.NastaviDanMI | [7 empty] | 6157 | 1 | 0x03c00f90
TPVNastaviLetoMI | INT | IOD_TPV | TPV:.NastaviLetoMI | [7 empty] | 6157 | 1 | 0x03c00f91
TPVNastaviMesecMI | INT | IOD_TPV | TPV:.NastaviMesecMI | [7 empty] | 6157 | 1 | 0x03c00f92
TPVNastaviMinutaMI | INT | IOD_TPV | TPV:.NastaviMinutaMI | [7 empty] | 6157 | 1 | 0x03c00f93
TPVNastaviSekundaMI | INT | IOD_TPV | TPV:.NastaviSekundaMI | [7 empty] | 6157 | 1 | 0x03c00f94
TPVNastaviUraMI | INT | IOD_TPV | TPV:.NastaviUraMI | [7 empty] | 6157 | 1 | 0x03c00f95
TPVOil_pressureA1 | UINT | IOD_TPV | TPV:.Oil_pressureA1 | 0 | 10000 | 0 | 10000 | Kpa |  |  | 6157 | 1 | 0x03c00f96
TPVOil_pressureA2 | UINT | IOD_TPV | TPV:.Oil_pressureA2 | 0 | 10000 | 0 | 10000 | Kpa |  |  | 6157 | 1 | 0x03c00f97
TPVRDASlabaBaterijaMI4 | DIGITAL | IOD_TPV | TPV:.RDASlabaBaterijaMI4 | [7 empty] | 6157 | 1 | 0x03c00fa0
TPVSlabaBaterijaMI4 | DIGITAL | IOD_TPV | TPV:.SlabaBaterijaMI4 | [7 empty] | 6157 | 1 | 0x03c00fb0
TPVSlabaBaterijaPLC1 | DIGITAL | IOD_TPV | TPV:.SlabaBaterijaPLC1 | [7 empty] | 6157 | 1 | 0x03c00fc0
TPVSlabaBaterijaPLC2 | DIGITAL | IOD_TPV | TPV:.SlabaBaterijaPLC2 | [7 empty] | 6157 | 1 | 0x03c00fd0
TPVStatus | INT | IOD_TPV | TPV:.Status | [7 empty] | 6157 | 1 | 0x03c00fe0
TPVstikaloDA3_okvara | DIGITAL | IOD_TPV | TPV:.stikaloDA3_okvara | [7 empty] | 6157 | 1 | 0x03c00ff0
TPVUI_MI4K2DA3_2Q1_izklop | DIGITAL | IOD_TPV | TPV:.UI_MI4K2DA3_2Q1_izklop | [7 empty] | 6157 | 1 | 0x03c01000
TPVUI_MI4K2DA3_2Q1_vklop | DIGITAL | IOD_TPV | TPV:.UI_MI4K2DA3_2Q1_vklop | [7 empty] | 6157 | 1 | 0x03c01010
TPVUI_MI4K2mrezaA3_1Q1_izklop | DIGITAL | IOD_TPV | TPV:.UI_MI4K2mrezaA3_1Q1_izklop | [7 empty] | 6157 | 1 | 0x03c01020
TPVUI_MI4K2mrezaA3_1Q1_vklop | DIGITAL | IOD_TPV | TPV:.UI_MI4K2mrezaA3_1Q1_vklop | [7 empty] | 6157 | 1 | 0x03c01030
s | DIGITAL | IOD_TPV_mem | D1 | [9 empty] | 0x03c01040
z | DIGITAL | IOD_TPV_mem | D2 | [9 empty] | 0x03c01050
TP_DanEnergCirc_DOVOD | REAL | IOD_TPV_disk | R7100[30] | [9 empty] | 0x03c01060
TP_CasDDanEnerg | INT | IOD_TPV_disk | I30[30] | [9 empty] | 0x03c01061
TP_CasMDanEnerg | INT | IOD_TPV_disk | I60[30] | [9 empty] | 0x03c01062
TP_TedenEnergCirc_DOVOD | REAL | IOD_TPV_disk | R7160[30] | [9 empty] | 0x03c01063
TP_CasDTedenEnerg | INT | IOD_TPV_disk | I120[30] | [9 empty] | 0x03c01064
TP_CasMTedenEnerg | INT | IOD_TPV_disk | I150[30] | [9 empty] | 0x03c01065
TP_MesecEnergCirc_DOVOD | REAL | IOD_TPV_disk | R7220[30] | [9 empty] | 0x03c01066
TP_CasDMesecEnerg | INT | IOD_TPV_disk | I210[30] | [9 empty] | 0x03c01067
TP_CasMMesecEnerg | INT | IOD_TPV_disk | I240[30] | [9 empty] | 0x03c01068
TP_StSt_DanEnergCirc_DOVOD | LONG | IOD_TPV_disk | L270 | [9 empty] | 0x03c01069
TP_StSt_TedenEnergCirc_DOVOD | LONG | IOD_TPV_disk | L272 | [9 empty] | 0x03c0106a
TP_StSt_MesecEnergCirc_DOVOD | LONG | IOD_TPV_disk | L274 | [9 empty] | 0x03c0106b
TP_StStCasDDanEnerg | LONG | IOD_TPV_disk | L276 | [9 empty] | 0x03c0106c
TP_StStCasMDanEnerg | LONG | IOD_TPV_disk | L278 | [9 empty] | 0x03c0106d
TP_StStCasDTedenEnerg | LONG | IOD_TPV_disk | L280 | [9 empty] | 0x03c0106e
TP_StStCasMTedenEnerg | LONG | IOD_TPV_disk | L282 | [9 empty] | 0x03c0106f
TP_StStCasDMesecEnerg | LONG | IOD_TPV_disk | L284 | [9 empty] | 0x03c01070
TP_StStCasMMesecEnerg | LONG | IOD_TPV_disk | L286 | [9 empty] | 0x03c01071
TP_DanEnergCirc_R2K1A | REAL | IOD_TPV_disk | R290[30] | [9 empty] | 0x03c01072
TP_TedenEnergCirc_R2K1A | REAL | IOD_TPV_disk | R320[30] | [9 empty] | 0x03c01073
TP_MesecEnergCirc_R2K1A | REAL | IOD_TPV_disk | R350[30] | [9 empty] | 0x03c01074
TP_DanEnergCirc_R2K2A | REAL | IOD_TPV_disk | R380[30] | [9 empty] | 0x03c01075
TP_TedenEnergCirc_R2K2A | REAL | IOD_TPV_disk | R410[30] | [9 empty] | 0x03c01076
TP_MesecEnergCirc_R2K2A | REAL | IOD_TPV_disk | R440[30] | [9 empty] | 0x03c01077
TP_DanEnergCirc_R3KCA | REAL | IOD_TPV_disk | R470[30] | [9 empty] | 0x03c01078
TP_TedenEnergCirc_R3KCA | REAL | IOD_TPV_disk | R500[30] | [9 empty] | 0x03c01079
TP_MesecEnergCirc_R3KCA | REAL | IOD_TPV_disk | R530[30] | [9 empty] | 0x03c0107a
TP_DanEnergCirc_RGUPS | REAL | IOD_TPV_disk | R560[30] | [9 empty] | 0x03c0107b
TP_TedenEnergCirc_RGUPS | REAL | IOD_TPV_disk | R590[30] | [9 empty] | 0x03c0107c
TP_MesecEnergCirc_RGUPS | REAL | IOD_TPV_disk | R620[30] | [9 empty] | 0x03c0107d
TP_DanEnergCirc_REZ1A | REAL | IOD_TPV_disk | R650[30] | [9 empty] | 0x03c0107e
TP_TedenEnergCirc_REZ1A | REAL | IOD_TPV_disk | R680[30] | [9 empty] | 0x03c0107f
TP_MesecEnergCirc_REZ1A | REAL | IOD_TPV_disk | R710[30] | [9 empty] | 0x03c01080
TP_DanEnergCirc_REZ2A | REAL | IOD_TPV_disk | R740[30] | [9 empty] | 0x03c01081
TP_TedenEnergCirc_REZ2A | REAL | IOD_TPV_disk | R770[30] | [9 empty] | 0x03c01082
TP_MesecEnergCirc_REZ2A | REAL | IOD_TPV_disk | R800[30] | [9 empty] | 0x03c01083
TP_DanEnergCirc_RGMA1 | REAL | IOD_TPV_disk | R830[30] | [9 empty] | 0x03c01084
TP_TedenEnergCirc_RGMA1 | REAL | IOD_TPV_disk | R860[30] | [9 empty] | 0x03c01085
TP_MesecEnergCirc_RGMA1 | REAL | IOD_TPV_disk | R890[30] | [9 empty] | 0x03c01086
TP_DanEnergCirc_RGMA2 | REAL | IOD_TPV_disk | R920[30] | [9 empty] | 0x03c01087
TP_TedenEnergCirc_RGMA2 | REAL | IOD_TPV_disk | R950[30] | [9 empty] | 0x03c01088
TP_MesecEnergCirc_RGMA2 | REAL | IOD_TPV_disk | R980[30] | [9 empty] | 0x03c01089
TP_DanEnergCirc_R1K4 | REAL | IOD_TPV_disk | R1010[30] | [9 empty] | 0x03c0108a
TP_TedenEnergCirc_R1K4 | REAL | IOD_TPV_disk | R1040[30] | [9 empty] | 0x03c0108b
TP_MesecEnergCirc_R1K4 | REAL | IOD_TPV_disk | R1070[30] | [9 empty] | 0x03c0108c
TP_DanEnergCirc_REZ1A2 | REAL | IOD_TPV_disk | R1100[30] | [9 empty] | 0x03c0108d
TP_TedenEnergCirc_REZ1A2 | REAL | IOD_TPV_disk | R1130[30] | [9 empty] | 0x03c0108e
TP_MesecEnergCirc_REZ1A2 | REAL | IOD_TPV_disk | R1160[30] | [9 empty] | 0x03c0108f
TP_DanEnergCirc_REZ2A2 | REAL | IOD_TPV_disk | R1190[30] | [9 empty] | 0x03c01090
TP_TedenEnergCirc_REZ2A2 | REAL | IOD_TPV_disk | R1220[30] | [9 empty] | 0x03c01091
TP_MesecEnergCirc_REZ2A2 | REAL | IOD_TPV_disk | R1250[30] | [9 empty] | 0x03c01092
TP_DanEnergCirc_RGM0A1 | REAL | IOD_TPV_disk | R1280[30] | [9 empty] | 0x03c01093
TP_TedenEnergCirc_RGM0A1 | REAL | IOD_TPV_disk | R1310[30] | [9 empty] | 0x03c01094
TP_MesecEnergCirc_RGM0A1 | REAL | IOD_TPV_disk | R1340[30] | [9 empty] | 0x03c01095
TP_DanEnergCirc_RGM0A2 | REAL | IOD_TPV_disk | R1370[30] | [9 empty] | 0x03c01096
TP_TedenEnergCirc_RGM0A2 | REAL | IOD_TPV_disk | R1400[30] | [9 empty] | 0x03c01097
TP_MesecEnergCirc_RGM0A2 | REAL | IOD_TPV_disk | R1430[30] | [9 empty] | 0x03c01098
TP_DanEnergCirc_RGM0A3 | REAL | IOD_TPV_disk | R1460[30] | [9 empty] | 0x03c01099
TP_TedenEnergCirc_RGM0A3 | REAL | IOD_TPV_disk | R1490[30] | [9 empty] | 0x03c0109a
TP_MesecEnergCirc_RGM0A3 | REAL | IOD_TPV_disk | R1520[30] | [9 empty] | 0x03c0109b
TP_DanEnergCirc_R2K1E | REAL | IOD_TPV_disk | R1550[30] | [9 empty] | 0x03c0109c
TP_TedenEnergCirc_R2K1E | REAL | IOD_TPV_disk | R1580[30] | [9 empty] | 0x03c0109d
TP_MesecEnergCirc_R2K1E | REAL | IOD_TPV_disk | R1610[30] | [9 empty] | 0x03c0109e
TP_DanEnergCirc_R2K2E | REAL | IOD_TPV_disk | R1640[30] | [9 empty] | 0x03c0109f
TP_TedenEnergCirc_R2K2E | REAL | IOD_TPV_disk | R1670[30] | [9 empty] | 0x03c010a0
TP_MesecEnergCirc_R2K2E | REAL | IOD_TPV_disk | R1700[30] | [9 empty] | 0x03c010a1
TP_DanEnergCirc_RDD | REAL | IOD_TPV_disk | R1730[30] | [9 empty] | 0x03c010a2
TP_TedenEnergCirc_RDD | REAL | IOD_TPV_disk | R1760[30] | [9 empty] | 0x03c010a3
TP_MesecEnergCirc_RDD | REAL | IOD_TPV_disk | R1790[30] | [9 empty] | 0x03c010a4
TP_DanEnergCirc_RKOM | REAL | IOD_TPV_disk | R1820[30] | [9 empty] | 0x03c010a5
TP_TedenEnergCirc_RKOM | REAL | IOD_TPV_disk | R1850[30] | [9 empty] | 0x03c010a6
TP_MesecEnergCirc_RKOM | REAL | IOD_TPV_disk | R1880[30] | [9 empty] | 0x03c010a7
TP_DanEnergCirc_ECP | REAL | IOD_TPV_disk | R1910[30] | [9 empty] | 0x03c010a8
TP_TedenEnergCirc_ECP | REAL | IOD_TPV_disk | R1940[30] | [9 empty] | 0x03c010a9
TP_MesecEnergCirc_ECP | REAL | IOD_TPV_disk | R1970[30] | [9 empty] | 0x03c010aa
TP_DanEnergCirc_ECPMNC | REAL | IOD_TPV_disk | R2000[30] | [9 empty] | 0x03c010ab
TP_TedenEnergCirc_ECPMNC | REAL | IOD_TPV_disk | R2030[30] | [9 empty] | 0x03c010ac
TP_MesecEnergCirc_ECPMNC | REAL | IOD_TPV_disk | R2060[30] | [9 empty] | 0x03c010ad
TP_DanEnergCirc_REZ1RGM0 | REAL | IOD_TPV_disk | R2090[30] | [9 empty] | 0x03c010ae
TP_TedenEnergCirc_REZ1RGM0 | REAL | IOD_TPV_disk | R2120[30] | [9 empty] | 0x03c010af
TP_MesecEnergCirc_REZ1RGM0 | REAL | IOD_TPV_disk | R2150[30] | [9 empty] | 0x03c010b0
TP_DanEnergCirc_REZ2RGM0 | REAL | IOD_TPV_disk | R2180[30] | [9 empty] | 0x03c010b1
TP_TedenEnergCirc_REZ2RGM0 | REAL | IOD_TPV_disk | R2210[30] | [9 empty] | 0x03c010b2
TP_MesecEnergCirc_REZ2RGM0 | REAL | IOD_TPV_disk | R2240[30] | [9 empty] | 0x03c010b3
TP_DanEnergCirc_REZ3RGM0 | REAL | IOD_TPV_disk | R2270[30] | [9 empty] | 0x03c010b4
TP_TedenEnergCirc_REZ3RGM0 | REAL | IOD_TPV_disk | R2300[30] | [9 empty] | 0x03c010b5
TP_MesecEnergCirc_REZ3RGM0 | REAL | IOD_TPV_disk | R2330[30] | [9 empty] | 0x03c010b6
TP_DanEnergCirc_RGMA3 | REAL | IOD_TPV_disk | R2360[30] | [9 empty] | 0x03c010b7
TP_TedenEnergCirc_RGMA3 | REAL | IOD_TPV_disk | R2390[30] | [9 empty] | 0x03c010b8
TP_MesecEnergCirc_RGMA3 | REAL | IOD_TPV_disk | R2420[30] | [9 empty] | 0x03c010b9
TP_StSt_DanEnergCirc_R2K1A | LONG | IOD_TPV_disk | L2456 | [9 empty] | 0x03c010ba
TP_StSt_TedenEnergCirc_R2K1A | LONG | IOD_TPV_disk | L2458 | [9 empty] | 0x03c010bb
TP_StSt_MesecEnergCirc_R2K1A | LONG | IOD_TPV_disk | L2460 | [9 empty] | 0x03c010bc
TP_StSt_DanEnergCirc_R2K2A | LONG | IOD_TPV_disk | L2462 | [9 empty] | 0x03c010bd
TP_StSt_TedenEnergCirc_R2K2A | LONG | IOD_TPV_disk | L2464 | [9 empty] | 0x03c010be
TP_StSt_MesecEnergCirc_R2K2A | LONG | IOD_TPV_disk | L2466 | [9 empty] | 0x03c010bf
TP_StSt_DanEnergCirc_R3KCA | LONG | IOD_TPV_disk | L2468 | [9 empty] | 0x03c010c0
TP_StSt_TedenEnergCirc_R3KCA | LONG | IOD_TPV_disk | L2470 | [9 empty] | 0x03c010c1
TP_StSt_MesecEnergCirc_R3KCA | LONG | IOD_TPV_disk | L2472 | [9 empty] | 0x03c010c2
TP_StSt_DanEnergCirc_RGUPS | LONG | IOD_TPV_disk | L2474 | [9 empty] | 0x03c010c3
TP_StSt_TedenEnergCirc_RGUPS | LONG | IOD_TPV_disk | L2476 | [9 empty] | 0x03c010c4
TP_StSt_MesecEnergCirc_RGUPS | LONG | IOD_TPV_disk | L2478 | [9 empty] | 0x03c010c5
TP_StSt_DanEnergCirc_REZ1A | LONG | IOD_TPV_disk | L2480 | [9 empty] | 0x03c010c6
TP_StSt_TedenEnergCirc_REZ1A | LONG | IOD_TPV_disk | L2482 | [9 empty] | 0x03c010c7
TP_StSt_MesecEnergCirc_REZ1A | LONG | IOD_TPV_disk | L2484 | [9 empty] | 0x03c010c8
TP_StSt_DanEnergCirc_REZ2A | LONG | IOD_TPV_disk | L2486 | [9 empty] | 0x03c010c9
TP_StSt_TedenEnergCirc_REZ2A | LONG | IOD_TPV_disk | L2488 | [9 empty] | 0x03c010ca
TP_StSt_MesecEnergCirc_REZ2A | LONG | IOD_TPV_disk | L2490 | [9 empty] | 0x03c010cb
TP_StSt_DanEnergCirc_RGMA1 | LONG | IOD_TPV_disk | L2492 | [9 empty] | 0x03c010cc
TP_StSt_TedenEnergCirc_RGMA1 | LONG | IOD_TPV_disk | L2494 | [9 empty] | 0x03c010cd
TP_StSt_MesecEnergCirc_RGMA1 | LONG | IOD_TPV_disk | L2496 | [9 empty] | 0x03c010ce
TP_StSt_DanEnergCirc_RGMA2 | LONG | IOD_TPV_disk | L2498 | [9 empty] | 0x03c010cf
TP_StSt_TedenEnergCirc_RGMA2 | LONG | IOD_TPV_disk | L2500 | [9 empty] | 0x03c010d0
TP_StSt_MesecEnergCirc_RGMA2 | LONG | IOD_TPV_disk | L2502 | [9 empty] | 0x03c010d1
TP_StSt_DanEnergCirc_R1K4 | LONG | IOD_TPV_disk | L2504 | [9 empty] | 0x03c010d2
TP_StSt_TedenEnergCirc_R1K4 | LONG | IOD_TPV_disk | L2506 | [9 empty] | 0x03c010d3
TP_StSt_MesecEnergCirc_R1K4 | LONG | IOD_TPV_disk | L2508 | [9 empty] | 0x03c010d4
TP_StSt_DanEnergCirc_REZ1A2 | LONG | IOD_TPV_disk | L2510 | [9 empty] | 0x03c010d5
TP_StSt_TedenEnergCirc_REZ1A2 | LONG | IOD_TPV_disk | L2512 | [9 empty] | 0x03c010d6
TP_StSt_MesecEnergCirc_REZ1A2 | LONG | IOD_TPV_disk | L2514 | [9 empty] | 0x03c010d7
TP_StSt_DanEnergCirc_REZ2A2 | LONG | IOD_TPV_disk | L2516 | [9 empty] | 0x03c010d8
TP_StSt_TedenEnergCirc_REZ2A2 | LONG | IOD_TPV_disk | L2518 | [9 empty] | 0x03c010d9
TP_StSt_MesecEnergCirc_REZ2A2 | LONG | IOD_TPV_disk | L2520 | [9 empty] | 0x03c010da
TP_StSt_DanEnergCirc_RGM0A1 | LONG | IOD_TPV_disk | L2522 | [9 empty] | 0x03c010db
TP_StSt_TedenEnergCirc_RGM0A1 | LONG | IOD_TPV_disk | L2524 | [9 empty] | 0x03c010dc
TP_StSt_MesecEnergCirc_RGM0A1 | LONG | IOD_TPV_disk | L2526 | [9 empty] | 0x03c010dd
TP_StSt_DanEnergCirc_RGM0A2 | LONG | IOD_TPV_disk | L2528 | [9 empty] | 0x03c010de
TP_StSt_TedenEnergCirc_RGM0A2 | LONG | IOD_TPV_disk | L2530 | [9 empty] | 0x03c010df
TP_StSt_MesecEnergCirc_RGM0A2 | LONG | IOD_TPV_disk | L2532 | [9 empty] | 0x03c010e0
TP_StSt_DanEnergCirc_RGM0A3 | LONG | IOD_TPV_disk | L2534 | [9 empty] | 0x03c010e1
TP_StSt_TedenEnergCirc_RGM0A3 | LONG | IOD_TPV_disk | L2536 | [9 empty] | 0x03c010e2
TP_StSt_MesecEnergCirc_RGM0A3 | LONG | IOD_TPV_disk | L2538 | [9 empty] | 0x03c010e3
TP_StSt_DanEnergCirc_R2K1E | LONG | IOD_TPV_disk | L2540 | [9 empty] | 0x03c010e4
TP_StSt_TedenEnergCirc_R2K1E | LONG | IOD_TPV_disk | L2542 | [9 empty] | 0x03c010e5
TP_StSt_MesecEnergCirc_R2K1E | LONG | IOD_TPV_disk | L2544 | [9 empty] | 0x03c010e6
TP_StSt_DanEnergCirc_R2K2E | LONG | IOD_TPV_disk | L2546 | [9 empty] | 0x03c010e7
TP_StSt_TedenEnergCirc_R2K2E | LONG | IOD_TPV_disk | L2548 | [9 empty] | 0x03c010e8
TP_StSt_MesecEnergCirc_R2K2E | LONG | IOD_TPV_disk | L2550 | [9 empty] | 0x03c010e9
TP_StSt_DanEnergCirc_RDD | LONG | IOD_TPV_disk | L2552 | [9 empty] | 0x03c010ea
TP_StSt_TedenEnergCirc_RDD | LONG | IOD_TPV_disk | L2554 | [9 empty] | 0x03c010eb
TP_StSt_MesecEnergCirc_RDD | LONG | IOD_TPV_disk | L2556 | [9 empty] | 0x03c010ec
TP_StSt_DanEnergCirc_RKOM | LONG | IOD_TPV_disk | L2558 | [9 empty] | 0x03c010ed
TP_StSt_TedenEnergCirc_RKOM | LONG | IOD_TPV_disk | L2560 | [9 empty] | 0x03c010ee
TP_StSt_MesecEnergCirc_RKOM | LONG | IOD_TPV_disk | L2562 | [9 empty] | 0x03c010ef
TP_StSt_DanEnergCirc_ECP | LONG | IOD_TPV_disk | L2564 | [9 empty] | 0x03c010f0
TP_StSt_TedenEnergCirc_ECP | LONG | IOD_TPV_disk | L2566 | [9 empty] | 0x03c010f1
TP_StSt_MesecEnergCirc_ECP | LONG | IOD_TPV_disk | L2568 | [9 empty] | 0x03c010f2
TP_StSt_DanEnergCirc_ECPMNC | LONG | IOD_TPV_disk | L2570 | [9 empty] | 0x03c010f3
TP_StSt_TedenEnergCirc_ECPMNC | LONG | IOD_TPV_disk | L2572 | [9 empty] | 0x03c010f4
TP_StSt_MesecEnergCirc_ECPMNC | LONG | IOD_TPV_disk | L2574 | [9 empty] | 0x03c010f5
TP_StSt_DanEnergCirc_REZ1RGM0 | LONG | IOD_TPV_disk | L2576 | [9 empty] | 0x03c010f6
TP_StSt_TedenEnergCirc_REZ1RGM0 | LONG | IOD_TPV_disk | L2578 | [9 empty] | 0x03c010f7
TP_StSt_MesecEnergCirc_REZ1RGM0 | LONG | IOD_TPV_disk | L2580 | [9 empty] | 0x03c010f8
TP_StSt_DanEnergCirc_REZ2RGM0 | LONG | IOD_TPV_disk | L2582 | [9 empty] | 0x03c010f9
TP_StSt_TedenEnergCirc_REZ2RGM0 | LONG | IOD_TPV_disk | L2584 | [9 empty] | 0x03c010fa
TP_StSt_MesecEnergCirc_REZ2RGM0 | LONG | IOD_TPV_disk | L2586 | [9 empty] | 0x03c010fb
TP_StSt_DanEnergCirc_REZ3RGM0 | LONG | IOD_TPV_disk | L2588 | [9 empty] | 0x03c010fc
TP_StSt_TedenEnergCirc_REZ3RGM0 | LONG | IOD_TPV_disk | L2590 | [9 empty] | 0x03c010fd
TP_StSt_MesecEnergCirc_REZ3RGM0 | LONG | IOD_TPV_disk | L2592 | [9 empty] | 0x03c010fe
TP_StSt_DanEnergCirc_RGMA3 | LONG | IOD_TPV_disk | L2594 | [9 empty] | 0x03c010ff
TP_StSt_TedenEnergCirc_RGMA3 | LONG | IOD_TPV_disk | L2596 | [9 empty] | 0x03c01100
TP_StSt_MesecEnergCirc_RGMA3 | LONG | IOD_TPV_disk | L2598 | [9 empty] | 0x03c01101
TPV_PULZ_1s | DIGITAL | IOD_TPV_mem | D2600 | [9 empty] | 0x03c01110
TP_op_alarm_Analizator1tok_L1 | DIGITAL | IOD_TPV_mem | D2601 | [9 empty] | 0x03c01120
TP_op_alarm_Analizator2tok_L1 | DIGITAL | IOD_TPV_mem | D2602 | [9 empty] | 0x03c01130
TP_op_alarm_Analizator3tok_L1 | DIGITAL | IOD_TPV_mem | D2603 | [9 empty] | 0x03c01140
TP_op_alarm_Analizator4tok_L1 | DIGITAL | IOD_TPV_mem | D2604 | [9 empty] | 0x03c01150
TP_op_alarm_Analizator5tok_L1 | DIGITAL | IOD_TPV_mem | D2605 | [9 empty] | 0x03c01160
TP_op_alarm_Analizator6tok_L1 | DIGITAL | IOD_TPV_mem | D2606 | [9 empty] | 0x03c01170
TP_op_alarm_Analizator7tok_L1 | DIGITAL | IOD_TPV_mem | D2607 | [9 empty] | 0x03c01180
TP_op_alarm_Analizator8tok_L1 | DIGITAL | IOD_TPV_mem | D2608 | [9 empty] | 0x03c01190
TP_op_alarm_Analizator9tok_L1 | DIGITAL | IOD_TPV_mem | D2609 | [9 empty] | 0x03c011a0
TP_op_alarm_Analizator10tok_L1 | DIGITAL | IOD_TPV_mem | D2610 | [9 empty] | 0x03c011b0
TP_op_alarm_Analizator11tok_L1 | DIGITAL | IOD_TPV_mem | D2611 | [9 empty] | 0x03c011c0
TP_op_alarm_Analizator12tok_L1 | DIGITAL | IOD_TPV_mem | D2612 | [9 empty] | 0x03c011d0
TP_op_alarm_Analizator13tok_L1 | DIGITAL | IOD_TPV_mem | D2613 | [9 empty] | 0x03c011e0
TP_op_alarm_Analizator14tok_L1 | DIGITAL | IOD_TPV_mem | D2614 | [9 empty] | 0x03c011f0
TP_op_alarm_Analizator15tok_L1 | DIGITAL | IOD_TPV_mem | D2615 | [9 empty] | 0x03c01200
TP_op_alarm_Analizator16tok_L1 | DIGITAL | IOD_TPV_mem | D2616 | [9 empty] | 0x03c01210
TP_op_alarm_Analizator17tok_L1 | DIGITAL | IOD_TPV_mem | D2617 | [9 empty] | 0x03c01220
TP_op_alarm_Analizator18tok_L1 | DIGITAL | IOD_TPV_mem | D2618 | [9 empty] | 0x03c01230
TP_op_alarm_Analizator19tok_L1 | DIGITAL | IOD_TPV_mem | D2619 | [9 empty] | 0x03c01240
TP_op_alarm_Analizator20tok_L1 | DIGITAL | IOD_TPV_mem | D2620 | [9 empty] | 0x03c01250
TP_op_alarm_Analizator21tok_L1 | DIGITAL | IOD_TPV_mem | D2621 | [9 empty] | 0x03c01260
TP_op_alarm_Analizator22tok_L1 | DIGITAL | IOD_TPV_mem | D2622 | [9 empty] | 0x03c01270
TP_op_alarm_Analizator23tok_L1 | DIGITAL | IOD_TPV_mem | D2623 | [9 empty] | 0x03c01280
TP_op_alarm_Analizator24tok_L1 | DIGITAL | IOD_TPV_mem | D2624 | [9 empty] | 0x03c01290
TP_op_alarm_Analizator25tok_L1 | DIGITAL | IOD_TPV_mem | D2625 | [9 empty] | 0x03c012a0
TP_op_om_alarm_Analizator_tok_L1 | DIGITAL | IOD_TPV_disk | D2628[30] | [9 empty] | 0x03c012b0
TP_op_pri_alarm_Analizator_tok_L1 | LONG | IOD_TPV_disk | L2658[30] | [9 empty] | 0x03c012c0
TP_op_alarm_Analizator1tok_L2 | DIGITAL | IOD_TPV_mem | D2689 | [9 empty] | 0x03c012d0
TP_op_alarm_Analizator2tok_L2 | DIGITAL | IOD_TPV_mem | D2690 | [9 empty] | 0x03c012e0
TP_op_alarm_Analizator3tok_L2 | DIGITAL | IOD_TPV_mem | D2691 | [9 empty] | 0x03c012f0
TP_op_alarm_Analizator4tok_L2 | DIGITAL | IOD_TPV_mem | D2692 | [9 empty] | 0x03c01300
TP_op_alarm_Analizator5tok_L2 | DIGITAL | IOD_TPV_mem | D2693 | [9 empty] | 0x03c01310
TP_op_alarm_Analizator6tok_L2 | DIGITAL | IOD_TPV_mem | D2694 | [9 empty] | 0x03c01320
TP_op_alarm_Analizator7tok_L2 | DIGITAL | IOD_TPV_mem | D2695 | [9 empty] | 0x03c01330
TP_op_alarm_Analizator8tok_L2 | DIGITAL | IOD_TPV_mem | D2696 | [9 empty] | 0x03c01340
TP_op_alarm_Analizator9tok_L2 | DIGITAL | IOD_TPV_mem | D2697 | [9 empty] | 0x03c01350
TP_op_alarm_Analizator10tok_L2 | DIGITAL | IOD_TPV_mem | D2698 | [9 empty] | 0x03c01360
TP_op_alarm_Analizator11tok_L2 | DIGITAL | IOD_TPV_mem | D2699 | [9 empty] | 0x03c01370
TP_op_alarm_Analizator12tok_L2 | DIGITAL | IOD_TPV_mem | D2700 | [9 empty] | 0x03c01380
TP_op_alarm_Analizator13tok_L2 | DIGITAL | IOD_TPV_mem | D2701 | [9 empty] | 0x03c01390
TP_op_alarm_Analizator14tok_L2 | DIGITAL | IOD_TPV_mem | D2702 | [9 empty] | 0x03c013a0
TP_op_alarm_Analizator15tok_L2 | DIGITAL | IOD_TPV_mem | D2703 | [9 empty] | 0x03c013b0
TP_op_alarm_Analizator16tok_L2 | DIGITAL | IOD_TPV_mem | D2704 | [9 empty] | 0x03c013c0
TP_op_alarm_Analizator17tok_L2 | DIGITAL | IOD_TPV_mem | D2705 | [9 empty] | 0x03c013d0
TP_op_alarm_Analizator18tok_L2 | DIGITAL | IOD_TPV_mem | D2706 | [9 empty] | 0x03c013e0
TP_op_alarm_Analizator19tok_L2 | DIGITAL | IOD_TPV_mem | D2707 | [9 empty] | 0x03c013f0
TP_op_alarm_Analizator20tok_L2 | DIGITAL | IOD_TPV_mem | D2708 | [9 empty] | 0x03c01400
TP_op_alarm_Analizator21tok_L2 | DIGITAL | IOD_TPV_mem | D2709 | [9 empty] | 0x03c01410
TP_op_alarm_Analizator22tok_L2 | DIGITAL | IOD_TPV_mem | D2710 | [9 empty] | 0x03c01420
TP_op_alarm_Analizator23tok_L2 | DIGITAL | IOD_TPV_mem | D2711 | [9 empty] | 0x03c01430
TP_op_alarm_Analizator24tok_L2 | DIGITAL | IOD_TPV_mem | D2712 | [9 empty] | 0x03c01440
TP_op_alarm_Analizator25tok_L2 | DIGITAL | IOD_TPV_mem | D2713 | [9 empty] | 0x03c01450
TP_op_om_alarm_Analizator_tok_L2 | DIGITAL | IOD_TPV_disk | D2714[30] | [9 empty] | 0x03c01460
TP_op_pri_alarm_Analizator_tok_L2 | LONG | IOD_TPV_disk | L2744[30] | [9 empty] | 0x03c01470
TP_op_alarm_Analizator1tok_L3 | DIGITAL | IOD_TPV_mem | D2774 | [9 empty] | 0x03c01480
TP_op_alarm_Analizator2tok_L3 | DIGITAL | IOD_TPV_mem | D2775 | [9 empty] | 0x03c01490
TP_op_alarm_Analizator3tok_L3 | DIGITAL | IOD_TPV_mem | D2776 | [9 empty] | 0x03c014a0
TP_op_alarm_Analizator4tok_L3 | DIGITAL | IOD_TPV_mem | D2777 | [9 empty] | 0x03c014b0
TP_op_alarm_Analizator5tok_L3 | DIGITAL | IOD_TPV_mem | D2778 | [9 empty] | 0x03c014c0
TP_op_alarm_Analizator6tok_L3 | DIGITAL | IOD_TPV_mem | D2779 | [9 empty] | 0x03c014d0
TP_op_alarm_Analizator7tok_L3 | DIGITAL | IOD_TPV_mem | D2780 | [9 empty] | 0x03c014e0
TP_op_alarm_Analizator8tok_L3 | DIGITAL | IOD_TPV_mem | D2781 | [9 empty] | 0x03c014f0
TP_op_alarm_Analizator9tok_L3 | DIGITAL | IOD_TPV_mem | D2782 | [9 empty] | 0x03c01500
TP_op_alarm_Analizator10tok_L3 | DIGITAL | IOD_TPV_mem | D2783 | [9 empty] | 0x03c01510
TP_op_alarm_Analizator11tok_L3 | DIGITAL | IOD_TPV_mem | D2784 | [9 empty] | 0x03c01520
TP_op_alarm_Analizator12tok_L3 | DIGITAL | IOD_TPV_mem | D2785 | [9 empty] | 0x03c01530
TP_op_alarm_Analizator13tok_L3 | DIGITAL | IOD_TPV_mem | D2786 | [9 empty] | 0x03c01540
TP_op_alarm_Analizator14tok_L3 | DIGITAL | IOD_TPV_mem | D2787 | [9 empty] | 0x03c01550
TP_op_alarm_Analizator15tok_L3 | DIGITAL | IOD_TPV_mem | D2788 | [9 empty] | 0x03c01560
TP_op_alarm_Analizator16tok_L3 | DIGITAL | IOD_TPV_mem | D2789 | [9 empty] | 0x03c01570
TP_op_alarm_Analizator17tok_L3 | DIGITAL | IOD_TPV_mem | D2790 | [9 empty] | 0x03c01580
TP_op_alarm_Analizator18tok_L3 | DIGITAL | IOD_TPV_mem | D2791 | [9 empty] | 0x03c01590
TP_op_alarm_Analizator19tok_L3 | DIGITAL | IOD_TPV_mem | D2792 | [9 empty] | 0x03c015a0
TP_op_alarm_Analizator20tok_L3 | DIGITAL | IOD_TPV_mem | D2793 | [9 empty] | 0x03c015b0
TP_op_alarm_Analizator21tok_L3 | DIGITAL | IOD_TPV_mem | D2794 | [9 empty] | 0x03c015c0
TP_op_alarm_Analizator22tok_L3 | DIGITAL | IOD_TPV_mem | D2795 | [9 empty] | 0x03c015d0
TP_op_alarm_Analizator23tok_L3 | DIGITAL | IOD_TPV_mem | D2796 | [9 empty] | 0x03c015e0
TP_op_alarm_Analizator24tok_L3 | DIGITAL | IOD_TPV_mem | D2797 | [9 empty] | 0x03c015f0
TP_op_alarm_Analizator25tok_L3 | DIGITAL | IOD_TPV_mem | D2798 | [9 empty] | 0x03c01600
TP_op_om_alarm_Analizator_tok_L3 | DIGITAL | IOD_TPV_disk | D2800[30] | [9 empty] | 0x03c01610
TP_op_pri_alarm_Analizator_tok_L3 | LONG | IOD_TPV_disk | L2840[30] | [9 empty] | 0x03c01620
TP_al_alarm_Analizator1tok_L1 | DIGITAL | IOD_TPV_mem | D2880 | [9 empty] | 0x03c01630
TP_al_alarm_Analizator2tok_L1 | DIGITAL | IOD_TPV_mem | D2881 | [9 empty] | 0x03c01640
TP_al_alarm_Analizator3tok_L1 | DIGITAL | IOD_TPV_mem | D2882 | [9 empty] | 0x03c01650
TP_al_alarm_Analizator4tok_L1 | DIGITAL | IOD_TPV_mem | D2883 | [9 empty] | 0x03c01660
TP_al_alarm_Analizator5tok_L1 | DIGITAL | IOD_TPV_mem | D2884 | [9 empty] | 0x03c01670
TP_al_alarm_Analizator6tok_L1 | DIGITAL | IOD_TPV_mem | D2885 | [9 empty] | 0x03c01680
TP_al_alarm_Analizator7tok_L1 | DIGITAL | IOD_TPV_mem | D2886 | [9 empty] | 0x03c01690
TP_al_alarm_Analizator8tok_L1 | DIGITAL | IOD_TPV_mem | D2887 | [9 empty] | 0x03c016a0
TP_al_alarm_Analizator9tok_L1 | DIGITAL | IOD_TPV_mem | D2888 | [9 empty] | 0x03c016b0
TP_al_alarm_Analizator10tok_L1 | DIGITAL | IOD_TPV_mem | D2889 | [9 empty] | 0x03c016c0
TP_al_alarm_Analizator11tok_L1 | DIGITAL | IOD_TPV_mem | D2890 | [9 empty] | 0x03c016d0
TP_al_alarm_Analizator12tok_L1 | DIGITAL | IOD_TPV_mem | D2891 | [9 empty] | 0x03c016e0
TP_al_alarm_Analizator13tok_L1 | DIGITAL | IOD_TPV_mem | D2892 | [9 empty] | 0x03c016f0
TP_al_alarm_Analizator14tok_L1 | DIGITAL | IOD_TPV_mem | D2893 | [9 empty] | 0x03c01700
TP_al_alarm_Analizator15tok_L1 | DIGITAL | IOD_TPV_mem | D2894 | [9 empty] | 0x03c01710
TP_al_alarm_Analizator16tok_L1 | DIGITAL | IOD_TPV_mem | D2895 | [9 empty] | 0x03c01720
TP_al_alarm_Analizator17tok_L1 | DIGITAL | IOD_TPV_mem | D2896 | [9 empty] | 0x03c01730
TP_al_alarm_Analizator18tok_L1 | DIGITAL | IOD_TPV_mem | D2897 | [9 empty] | 0x03c01740
TP_al_alarm_Analizator19tok_L1 | DIGITAL | IOD_TPV_mem | D2898 | [9 empty] | 0x03c01750
TP_al_alarm_Analizator20tok_L1 | DIGITAL | IOD_TPV_mem | D2899 | [9 empty] | 0x03c01760
TP_al_alarm_Analizator21tok_L1 | DIGITAL | IOD_TPV_mem | D2900 | [9 empty] | 0x03c01770
TP_al_alarm_Analizator22tok_L1 | DIGITAL | IOD_TPV_mem | D2901 | [9 empty] | 0x03c01780
TP_al_alarm_Analizator23tok_L1 | DIGITAL | IOD_TPV_mem | D2902 | [9 empty] | 0x03c01790
TP_al_alarm_Analizator24tok_L1 | DIGITAL | IOD_TPV_mem | D2903 | [9 empty] | 0x03c017a0
TP_al_alarm_Analizator25tok_L1 | DIGITAL | IOD_TPV_mem | D2904 | [9 empty] | 0x03c017b0
TP_al_om_alarm_Analizator_tok_L1 | DIGITAL | IOD_TPV_disk | D2934[30] | [9 empty] | 0x03c017c0
TP_al_pri_alarm_Analizator_tok_L1 | LONG | IOD_TPV_disk | L2950[30] | [9 empty] | 0x03c017d0
TP_al_alarm_Analizator1tok_L2 | DIGITAL | IOD_TPV_mem | D2980 | [9 empty] | 0x03c017e0
TP_al_alarm_Analizator2tok_L2 | DIGITAL | IOD_TPV_mem | D2981 | [9 empty] | 0x03c017f0
TP_al_alarm_Analizator3tok_L2 | DIGITAL | IOD_TPV_mem | D2982 | [9 empty] | 0x03c01800
TP_al_alarm_Analizator4tok_L2 | DIGITAL | IOD_TPV_mem | D2983 | [9 empty] | 0x03c01810
TP_al_alarm_Analizator5tok_L2 | DIGITAL | IOD_TPV_mem | D2984 | [9 empty] | 0x03c01820
TP_al_alarm_Analizator6tok_L2 | DIGITAL | IOD_TPV_mem | D2985 | [9 empty] | 0x03c01830
TP_al_alarm_Analizator7tok_L2 | DIGITAL | IOD_TPV_mem | D2986 | [9 empty] | 0x03c01840
TP_al_alarm_Analizator8tok_L2 | DIGITAL | IOD_TPV_mem | D2987 | [9 empty] | 0x03c01850
TP_al_alarm_Analizator9tok_L2 | DIGITAL | IOD_TPV_mem | D2988 | [9 empty] | 0x03c01860
TP_al_alarm_Analizator10tok_L2 | DIGITAL | IOD_TPV_mem | D2989 | [9 empty] | 0x03c01870
TP_al_alarm_Analizator11tok_L2 | DIGITAL | IOD_TPV_mem | D2990 | [9 empty] | 0x03c01880
TP_al_alarm_Analizator12tok_L2 | DIGITAL | IOD_TPV_mem | D2991 | [9 empty] | 0x03c01890
TP_al_alarm_Analizator13tok_L2 | DIGITAL | IOD_TPV_mem | D2992 | [9 empty] | 0x03c018a0
TP_al_alarm_Analizator14tok_L2 | DIGITAL | IOD_TPV_mem | D2993 | [9 empty] | 0x03c018b0
TP_al_alarm_Analizator15tok_L2 | DIGITAL | IOD_TPV_mem | D2994 | [9 empty] | 0x03c018c0
TP_al_alarm_Analizator16tok_L2 | DIGITAL | IOD_TPV_mem | D2995 | [9 empty] | 0x03c018d0
TP_al_alarm_Analizator17tok_L2 | DIGITAL | IOD_TPV_mem | D2996 | [9 empty] | 0x03c018e0
TP_al_alarm_Analizator18tok_L2 | DIGITAL | IOD_TPV_mem | D2997 | [9 empty] | 0x03c018f0
TP_al_alarm_Analizator19tok_L2 | DIGITAL | IOD_TPV_mem | D2998 | [9 empty] | 0x03c01900
TP_al_alarm_Analizator20tok_L2 | DIGITAL | IOD_TPV_mem | D2999 | [9 empty] | 0x03c01910
TP_al_alarm_Analizator21tok_L2 | DIGITAL | IOD_TPV_mem | D3000 | [9 empty] | 0x03c01920
TP_al_alarm_Analizator22tok_L2 | DIGITAL | IOD_TPV_mem | D3001 | [9 empty] | 0x03c01930
TP_al_alarm_Analizator23tok_L2 | DIGITAL | IOD_TPV_mem | D3002 | [9 empty] | 0x03c01940
TP_al_alarm_Analizator24tok_L2 | DIGITAL | IOD_TPV_mem | D3003 | [9 empty] | 0x03c01950
TP_al_alarm_Analizator25tok_L2 | DIGITAL | IOD_TPV_mem | D3004 | [9 empty] | 0x03c01960
TP_al_om_alarm_Analizator_tok_L2 | DIGITAL | IOD_TPV_disk | D3006[30] | [9 empty] | 0x03c01970
TP_al_pri_alarm_Analizator_tok_L2 | LONG | IOD_TPV_disk | L3040[30] | [9 empty] | 0x03c01980
TP_al_alarm_Analizator1tok_L3 | DIGITAL | IOD_TPV_mem | D3080 | [9 empty] | 0x03c01990
TP_al_alarm_Analizator2tok_L3 | DIGITAL | IOD_TPV_mem | D3081 | [9 empty] | 0x03c019a0
TP_al_alarm_Analizator3tok_L3 | DIGITAL | IOD_TPV_mem | D3082 | [9 empty] | 0x03c019b0
TP_al_alarm_Analizator4tok_L3 | DIGITAL | IOD_TPV_mem | D3083 | [9 empty] | 0x03c019c0
TP_al_alarm_Analizator5tok_L3 | DIGITAL | IOD_TPV_mem | D3084 | [9 empty] | 0x03c019d0
TP_al_alarm_Analizator6tok_L3 | DIGITAL | IOD_TPV_mem | D3085 | [9 empty] | 0x03c019e0
TP_al_alarm_Analizator7tok_L3 | DIGITAL | IOD_TPV_mem | D3086 | [9 empty] | 0x03c019f0
TP_al_alarm_Analizator8tok_L3 | DIGITAL | IOD_TPV_mem | D3087 | [9 empty] | 0x03c01a00
TP_al_alarm_Analizator9tok_L3 | DIGITAL | IOD_TPV_mem | D3088 | [9 empty] | 0x03c01a10
TP_al_alarm_Analizator10tok_L3 | DIGITAL | IOD_TPV_mem | D3089 | [9 empty] | 0x03c01a20
TP_al_alarm_Analizator11tok_L3 | DIGITAL | IOD_TPV_mem | D3090 | [9 empty] | 0x03c01a30
TP_al_alarm_Analizator12tok_L3 | DIGITAL | IOD_TPV_mem | D3091 | [9 empty] | 0x03c01a40
TP_al_alarm_Analizator13tok_L3 | DIGITAL | IOD_TPV_mem | D3092 | [9 empty] | 0x03c01a50
TP_al_alarm_Analizator14tok_L3 | DIGITAL | IOD_TPV_mem | D3093 | [9 empty] | 0x03c01a60
TP_al_alarm_Analizator15tok_L3 | DIGITAL | IOD_TPV_mem | D3094 | [9 empty] | 0x03c01a70
TP_al_alarm_Analizator16tok_L3 | DIGITAL | IOD_TPV_mem | D3095 | [9 empty] | 0x03c01a80
TP_al_alarm_Analizator17tok_L3 | DIGITAL | IOD_TPV_mem | D3096 | [9 empty] | 0x03c01a90
TP_al_alarm_Analizator18tok_L3 | DIGITAL | IOD_TPV_mem | D3097 | [9 empty] | 0x03c01aa0
TP_al_alarm_Analizator19tok_L3 | DIGITAL | IOD_TPV_mem | D3098 | [9 empty] | 0x03c01ab0
TP_al_alarm_Analizator20tok_L3 | DIGITAL | IOD_TPV_mem | D3099 | [9 empty] | 0x03c01ac0
TP_al_alarm_Analizator21tok_L3 | DIGITAL | IOD_TPV_mem | D3100 | [9 empty] | 0x03c01ad0
TP_al_alarm_Analizator22tok_L3 | DIGITAL | IOD_TPV_mem | D3101 | [9 empty] | 0x03c01ae0
TP_al_alarm_Analizator23tok_L3 | DIGITAL | IOD_TPV_mem | D3102 | [9 empty] | 0x03c01af0
TP_al_alarm_Analizator24tok_L3 | DIGITAL | IOD_TPV_mem | D3103 | [9 empty] | 0x03c01b00
TP_al_alarm_Analizator25tok_L3 | DIGITAL | IOD_TPV_mem | D3104 | [9 empty] | 0x03c01b10
TP_al_om_alarm_Analizator_tok_L3 | DIGITAL | IOD_TPV_disk | D3140[30] | [9 empty] | 0x03c01b20
TP_al_pri_alarm_Analizator_tok_L3 | LONG | IOD_TPV_disk | L3170[30] | [9 empty] | 0x03c01b30
TP_Gen_rdeca_spmeja_tlak_oljaA1 | INT | IOD_TPV_disk | I3210 | [9 empty] | 0x03c01b31
TP_Gen_rumena_spmeja_tlak_oljaA1 | INT | IOD_TPV_disk | I3212 | [9 empty] | 0x03c01b32
TP_Gen_rdeca_zgmeja_tlak_oljaA1 | INT | IOD_TPV_disk | I3214 | [9 empty] | 0x03c01b33
TP_Gen_rumena_zgmeja_tlak_oljaA1 | INT | IOD_TPV_disk | I3216 | [9 empty] | 0x03c01b34
TP_Gen_rdeca_spmeja_hitrostA1 | INT | IOD_TPV_disk | I3218 | [9 empty] | 0x03c01b35
TP_Gen_rumena_spmeja_hitrostA1 | INT | IOD_TPV_disk | I3220 | [9 empty] | 0x03c01b36
TP_Gen_rdeca_zgmeja_hitrostA1 | INT | IOD_TPV_disk | I3222 | [9 empty] | 0x03c01b37
TP_Gen_rumena_zgmeja_hitrostA1 | INT | IOD_TPV_disk | I3224 | [9 empty] | 0x03c01b38
TP_Gen_rdeca_spmeja_alter_napA1 | INT | IOD_TPV_disk | I3226 | [9 empty] | 0x03c01b39
TP_Gen_rumena_spmeja_alter_napA1 | INT | IOD_TPV_disk | I3228 | [9 empty] | 0x03c01b3a
TP_Gen_rdeca_spmeja_tempA1 | INT | IOD_TPV_disk | I3230 | [9 empty] | 0x03c01b3b
TP_Gen_rumena_spmeja_tempA1 | INT | IOD_TPV_disk | I3232 | [9 empty] | 0x03c01b3c
TP_Gen_rdeca_spmeja_bat_napA1 | INT | IOD_TPV_disk | I3234 | [9 empty] | 0x03c01b3d
TP_Gen_rumena_spmeja_bat_napA1 | INT | IOD_TPV_disk | I3236 | [9 empty] | 0x03c01b3e
TP_Gen_A1_omog_upozorila | DIGITAL | IOD_TPV_disk | D3238[30] | [9 empty] | 0x03c01b40
TP_Gen_A1_omog_alarm | DIGITAL | IOD_TPV_disk | D3268[30] | [9 empty] | 0x03c01b50
TP_Gen_A1_op_alarm_tlak_sp | DIGITAL | IOD_TPV_mem | D3300 | [9 empty] | 0x03c01b60
TP_Gen_A1_al_alarm_tlak_sp | DIGITAL | IOD_TPV_mem | D3301 | [9 empty] | 0x03c01b70
TP_Gen_A1_op_alarm_tlak_zg | DIGITAL | IOD_TPV_mem | D3302 | [9 empty] | 0x03c01b80
TP_Gen_A1_al_alarm_tlak_zg | DIGITAL | IOD_TPV_mem | D3303 | [9 empty] | 0x03c01b90
TP_Gen_A1_op_alarm_hitrost_sp | DIGITAL | IOD_TPV_mem | D3304 | [9 empty] | 0x03c01ba0
TP_Gen_A1_al_alarm_hitrost_sp | DIGITAL | IOD_TPV_mem | D3305 | [9 empty] | 0x03c01bb0
TP_Gen_A1_op_alarm_hitrost_zg | DIGITAL | IOD_TPV_mem | D3306 | [9 empty] | 0x03c01bc0
TP_Gen_A1_al_alarm_hitrost_zg | DIGITAL | IOD_TPV_mem | D3307 | [9 empty] | 0x03c01bd0
TP_Gen_A1_op_alarm_alter_nap | DIGITAL | IOD_TPV_mem | D3308 | [9 empty] | 0x03c01be0
TP_Gen_A1_al_alarm_alter_nap | DIGITAL | IOD_TPV_mem | D3309 | [9 empty] | 0x03c01bf0
TP_Gen_A1_op_alarm_temp | DIGITAL | IOD_TPV_mem | D3310 | [9 empty] | 0x03c01c00
TP_Gen_A1_al_alarm_temp | DIGITAL | IOD_TPV_mem | D3311 | [9 empty] | 0x03c01c10
TP_Gen_A1_op_alarm_bat_nap | DIGITAL | IOD_TPV_mem | D3312 | [9 empty] | 0x03c01c20
TP_Gen_A1_al_alarm_bat_nap | DIGITAL | IOD_TPV_mem | D3313 | [9 empty] | 0x03c01c30
TP_Gen_rdeca_spmeja_tlak_oljaA2 | INT | IOD_TPV_disk | I3316 | [9 empty] | 0x03c01c40
TP_Gen_rumena_spmeja_tlak_oljaA2 | INT | IOD_TPV_disk | I3318 | [9 empty] | 0x03c01c41
TP_Gen_rdeca_zgmeja_tlak_oljaA2 | INT | IOD_TPV_disk | I3320 | [9 empty] | 0x03c01c42
TP_Gen_rumena_zgmeja_tlak_oljaA2 | INT | IOD_TPV_disk | I3322 | [9 empty] | 0x03c01c43
TP_Gen_rdeca_spmeja_hitrostA2 | INT | IOD_TPV_disk | I3324 | [9 empty] | 0x03c01c44
TP_Gen_rumena_spmeja_hitrostA2 | INT | IOD_TPV_disk | I3326 | [9 empty] | 0x03c01c45
TP_Gen_rdeca_zgmeja_hitrostA2 | INT | IOD_TPV_disk | I3328 | [9 empty] | 0x03c01c46
TP_Gen_rumena_zgmeja_hitrostA2 | INT | IOD_TPV_disk | I3330 | [9 empty] | 0x03c01c47
TP_Gen_rdeca_spmeja_alter_napA2 | INT | IOD_TPV_disk | I3332 | [9 empty] | 0x03c01c48
TP_Gen_rumena_spmeja_alter_napA2 | INT | IOD_TPV_disk | I3334 | [9 empty] | 0x03c01c49
TP_Gen_rdeca_spmeja_tempA2 | INT | IOD_TPV_disk | I3336 | [9 empty] | 0x03c01c4a
TP_Gen_rumena_spmeja_tempA2 | INT | IOD_TPV_disk | I3338 | [9 empty] | 0x03c01c4b
TP_Gen_rdeca_spmeja_bat_napA2 | INT | IOD_TPV_disk | I3340 | [9 empty] | 0x03c01c4c
TP_Gen_rumena_spmeja_bat_napA2 | INT | IOD_TPV_disk | I3342 | [9 empty] | 0x03c01c4d
TP_Gen_A2_omog_upozorila | DIGITAL | IOD_TPV_disk | D3376[30] | [9 empty] | 0x03c01c50
TP_Gen_A2_omog_alarm | DIGITAL | IOD_TPV_disk | D3410[30] | [9 empty] | 0x03c01c60
TP_Gen_A2_op_alarm_tlak_sp | DIGITAL | IOD_TPV_mem | D3440 | [9 empty] | 0x03c01c70
TP_Gen_A2_al_alarm_tlak_sp | DIGITAL | IOD_TPV_mem | D3441 | [9 empty] | 0x03c01c80
TP_Gen_A2_op_alarm_tlak_zg | DIGITAL | IOD_TPV_mem | D3442 | [9 empty] | 0x03c01c90
TP_Gen_A2_al_alarm_tlak_zg | DIGITAL | IOD_TPV_mem | D3443 | [9 empty] | 0x03c01ca0
TP_Gen_A2_op_alarm_hitrost_sp | DIGITAL | IOD_TPV_mem | D3444 | [9 empty] | 0x03c01cb0
TP_Gen_A2_al_alarm_hitrost_sp | DIGITAL | IOD_TPV_mem | D3445 | [9 empty] | 0x03c01cc0
TP_Gen_A2_op_alarm_hitrost_zg | DIGITAL | IOD_TPV_mem | D3446 | [9 empty] | 0x03c01cd0
TP_Gen_A2_al_alarm_hitrost_zg | DIGITAL | IOD_TPV_mem | D3447 | [9 empty] | 0x03c01ce0
TP_Gen_A2_op_alarm_alter_nap | DIGITAL | IOD_TPV_mem | D3448 | [9 empty] | 0x03c01cf0
TP_Gen_A2_al_alarm_alter_nap | DIGITAL | IOD_TPV_mem | D3449 | [9 empty] | 0x03c01d00
TP_Gen_A2_op_alarm_temp | DIGITAL | IOD_TPV_mem | D3450 | [9 empty] | 0x03c01d10
TP_Gen_A2_al_alarm_temp | DIGITAL | IOD_TPV_mem | D3451 | [9 empty] | 0x03c01d20
TP_Gen_A2_op_alarm_bat_nap | DIGITAL | IOD_TPV_mem | D3452 | [9 empty] | 0x03c01d30
TP_Gen_A2_al_alarm_bat_nap | DIGITAL | IOD_TPV_mem | D3453 | [9 empty] | 0x03c01d40
TP_Gen_splosna_napaka_DA1 | DIGITAL | IOD_TPV_mem | D3454 | [9 empty] | 0x03c01d50
TP_Gen_splosna_napaka_DA2 | DIGITAL | IOD_TPV_mem | D3455 | [9 empty] | 0x03c01d60
TP_Stikala_rocni_izklop_omog_alarm | DIGITAL | IOD_TPV_disk | D3460[30] | [9 empty] | 0x03c01d70
TP_Stikala_rocni_izklop_alarm | DIGITAL | IOD_TPV_disk | D3490[30] | [9 empty] | 0x03c01d80
TP_Stikala_zasc_izklop_omog_alarm | DIGITAL | IOD_TPV_disk | D3520[30] | [9 empty] | 0x03c01d90
TP_Stikala_zasc_izklop_alarm | DIGITAL | IOD_TPV_disk | D3550[30] | [9 empty] | 0x03c01da0
TP_omog_komuk_alarmov | DIGITAL | IOD_TPV_disk | D3580[30] | [9 empty] | 0x03c01db0
TP_DA3_omog_alarma | DIGITAL | IOD_TPV_disk | D2587[7] | [9 empty] | 0x03c01dc0
TP_DA3_alarm | DIGITAL | IOD_TPV_mem | D2594[7] | [9 empty] | 0x03c01dd0
ATP_PoljeSmsAlarmi | DIGITAL | IOD_TPV_disk | D3600[300] | [9 empty] | 0x03c01de0
BTP_PoljeSmsAlarmi | DIGITAL | IOD_TPV_disk | D3900[300] | [9 empty] | 0x03c01df0
CTP_PoljeSmsAlarmi | DIGITAL | IOD_TPV_disk | D4200[300] | [9 empty] | 0x03c01e00
DTP_PoljeSmsAlarmi | DIGITAL | IOD_TPV_disk | D4500[300] | [9 empty] | 0x03c01e10
ETP_PoljeSmsAlarmi | DIGITAL | IOD_TPV_disk | D4800[300] | [9 empty] | 0x03c01e20
FTP_PoljeSmsAlarmi | DIGITAL | IOD_TPV_disk | D5100[300] | [9 empty] | 0x03c01e30
TP_delovna_energija | LONG | IOD_TPV_disk | L5400[50] | [9 empty] | 0x03c01e40
TP_jalova_energija | LONG | IOD_TPV_disk | L5450[50] | [9 empty] | 0x03c01e41
TP_Cas_dan | LONG | IOD_TPV_disk | L5500[50] | [9 empty] | 0x03c01e42
TP_Cas_teden | LONG | IOD_TPV_disk | L5550[50] | [9 empty] | 0x03c01e43
TP_st_delovna | LONG | IOD_TPV_disk | L5602 | [9 empty] | 0x03c01e44
TP_st_jalova | LONG | IOD_TPV_disk | L5604 | [9 empty] | 0x03c01e45
IzpadTPV | INT | IOD_TPV | TPV:.st_izpad_komTPV | [9 empty] | 0x03c01e46
TPVsinh_cas | STRING | IOD_TPV | TPV:.cas_scada | [9 empty] | 0x03c01e47
TPVsinh_cas_nastavi | DIGITAL | IOD_TPV | TPV:.cas_nastavi | [9 empty] | 0x03c01e50
TPVMax_dan_energija | REAL | IOD_TPV_disk | R5610[30] | [5 empty] | ########## |  |  |  | 0x03c01e60
TPVMax_mes_energija | REAL | IOD_TPV_disk | R5640[30] | [5 empty] | ########## |  |  |  | 0x03c01e61
TPVMax_let_energija | REAL | IOD_TPV_disk | R5670[30] | [5 empty] | ########## |  |  |  | 0x03c01e62
TPV_vklop_agregata_DA1 | DIGITAL | IOD_TPV_disk | D5700 | [9 empty] | 0x03c01e70
TPV_vklop_agregata_DA2 | DIGITAL | IOD_TPV_disk | D5701 | [9 empty] | 0x03c01e80
TPV_prisotnost_DA1_napetosti | DIGITAL | IOD_TPV_disk | D5702 | [9 empty] | 0x03c01e90
TPV_prisotnost_DA2_napetosti | DIGITAL | IOD_TPV_disk | D5703 | [9 empty] | 0x03c01ea0
TPV_prisotnost_DA3_napetosti | DIGITAL | IOD_TPV_disk | D5704 | [9 empty] | 0x03c01eb0
TPV_prisotnost_m_nap_rgm1 | DIGITAL | IOD_TPV_disk | D5705 | [9 empty] | 0x03c01ec0
TPV_prisotnost_m_nap_rgm2 | DIGITAL | IOD_TPV_disk | D5706 | [9 empty] | 0x03c01ed0
TPV_prisotnost_m_nap_rgm3 | DIGITAL | IOD_TPV_disk | D5707 | [9 empty] | 0x03c01ee0
TPV_izbira_mali_prikaz_circ | INT | IOD_TPV_disk | I5710 | [9 empty] | 0x03c01ef0
TPV_utrip_simbola_ob_alrmu | DIGITAL | IOD_TPV_disk | D5712 | [9 empty] | 0x03c01f00
TPV_report_vpis | DIGITAL | IOD_TPV_mem | D5713 | [9 empty] | 0x03c01f10
TPV_vklop_da1 | DIGITAL | IOD_TPV_disk | D5714 | [9 empty] | 0x03c01f20
TPV_vklop_da2 | DIGITAL | IOD_TPV_disk | D5715 | [9 empty] | 0x03c01f30
TPV_rez_av_da1da2 | DIGITAL | IOD_TPV_disk | D5716 | [9 empty] | 0x03c01f40
TPV_vzp_vedno_da1da2 | DIGITAL | IOD_TPV_disk | D5717 | [9 empty] | 0x03c01f50
TPV_vzp_nikoli_da1da2 | DIGITAL | IOD_TPV_disk | D5718 | [9 empty] | 0x03c01f60
TPV_vzp_popot_da1da2 | DIGITAL | IOD_TPV_disk | D5719 | [9 empty] | 0x03c01f70
TPV_rez_ro_da1da2 | DIGITAL | IOD_TPV_disk | D5720 | [9 empty] | 0x03c01f80
TPV_scroll_report | INT | IOD_TPV_disk | I5722 |  |  | 0 | 100 | % |  |  |  |  | 0x03c01f90
TPVMI4_not_mrez_nap_RGM_A1 | DIGITAL | IOD_TPV_disk | D5724 | [9 empty] | 0x03c01fa0
TPVMI4_not_mrez_nap_RGM_A2 | DIGITAL | IOD_TPV_disk | D5725 | [9 empty] | 0x03c01fb0
TPVMI4K2_not_mrez_nap_RGM_A3 | DIGITAL | IOD_TPV_disk | D5726 | [9 empty] | 0x03c01fc0
TPV_report_napetost_vpis | DIGITAL | IOD_TPV_mem | D5727 | [9 empty] | 0x03c01fd0
TPV_pom_nap_m_DA1 | DIGITAL | IOD_TPV_disk | D5728 | [9 empty] | 0x03c01fe0
TPV_pom_nap_m_DA2 | DIGITAL | IOD_TPV_disk | D5729 | [9 empty] | 0x03c01ff0
TPV_pom_nap_m_DA3 | DIGITAL | IOD_TPV_disk | D5730 | [9 empty] | 0x03c02000
TPV_pom_nap_DA1 | DIGITAL | IOD_TPV_disk | D5731 | [9 empty] | 0x03c02010
TPV_pom_nap_DA2 | DIGITAL | IOD_TPV_disk | D5732 | [9 empty] | 0x03c02020
TPV_pom_nap_DA3 | DIGITAL | IOD_TPV_disk | D5733 | [9 empty] | 0x03c02030
TPV_pom_DA1_deluje | DIGITAL | IOD_TPV_disk | D5734 | [9 empty] | 0x03c02040
TPV_pom_DA2_deluje | DIGITAL | IOD_TPV_disk | D5735 | [9 empty] | 0x03c02050
TPV_vzp_rez_av_DA3 | DIGITAL | IOD_TPV_disk | D5736 | [9 empty] | 0x03c02060
TPV_vzp_rez_ro_DA3 | DIGITAL | IOD_TPV_disk | D5737 | [9 empty] | 0x03c02070
TPV_po_zagonu_je_1 | DIGITAL | IOD_TPV_disk | D5738 | [9 empty] | 0x03c02080
TPV_stanje_vzp_nikoli_da1da2 | DIGITAL | IOD_TPV_disk | D5739 | [9 empty] | 0x03c02090
TPV_stanje_vzp_popot_da1da2 | DIGITAL | IOD_TPV_disk | D5740 | [9 empty] | 0x03c020a0
TPV_stanje_vzp_vedno_da1da2 | DIGITAL | IOD_TPV_disk | D5741 | [9 empty] | 0x03c020b0
TPV_stanje_av_ro_da1da2 | DIGITAL | IOD_TPV_disk | D5742 | [9 empty] | 0x03c020c0
TPV_stanje_av_ro_da3 | DIGITAL | IOD_TPV_disk | D5743 | [9 empty] | 0x03c020d0
TPVdelovna_energ_disk | INT | IOD_TPV_disk | I5746 | [9 empty] | 0x03c020e0
TPVjal_energ_skupna_max | INT | IOD_TPV_disk | I5748 | [9 empty] | 0x03c020e1
TPVdel_energ_skupna_max | INT | IOD_TPV_disk | I5750 | [9 empty] | 0x03c020e2
TPVjalova_energ_disk | INT | IOD_TPV_disk | I5752 | [9 empty] | 0x03c020e3
TPVenergija_prvi_vpis | INT | IOD_TPV_mem | I5754 | [9 empty] | 0x03c020e4
TPV_zacni_preverit_alarme | DIGITAL | IOD_TPV_mem | D5756 | [9 empty] | 0x03c020f0
TP_ralika_energ_dan | REAL | IOD_TPV_disk | R5800[30] | [9 empty] | 0x03c02100
TP_ralika_energ_ted | REAL | IOD_TPV_disk | R5830[30] | [9 empty] | 0x03c02101
TP_ralika_energ_mes | REAL | IOD_TPV_disk | R5860[30] | [9 empty] | 0x03c02102
TPVMI4napaka_alarm_DA1_omog | DIGITAL | IOD_TPV_disk | D6890 | [9 empty] | 0x03c02110
TPVMI4napaka_alarm_DA2_omog | DIGITAL | IOD_TPV_disk | D6891 | [9 empty] | 0x03c02120
TPV_Dnevna_energija | REAL | IOD_TPV_disk | R6900[30] | [9 empty] | 0x03c02130
TPV_Tedensa_energija | REAL | IOD_TPV_disk | R6930[30] | [9 empty] | 0x03c02131
TPV_Mesecna_energija | REAL | IOD_TPV_disk | R6960[30] | [9 empty] | 0x03c02132
TPVCirc14NicelniTok_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ14NicelniTok | 0 | 8000 | 0 | 800.0 | A | ###.# |  | 6157 | 1 | 0x03c02133
TPVCirc14Tok_L1_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ14Tok_L1 | 0 | 8000 | 0 | 800.0 | A | ###.# |  | 6157 | 1 | 0x03c02134
TPVCirc14Tok_L2_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ14Tok_L2 | 0 | 8000 | 0 | 800.0 | A | ###.# |  | 6157 | 1 | 0x03c02135
TPVCirc14Tok_L3_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ14Tok_L3 | 0 | 8000 | 0 | 800.0 | A | ###.# |  | 6157 | 1 | 0x03c02136
TPVCirc8NicelniTok_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ8NicelniTok | 0 | 8000 | 0 | 800.0 | A | ###.# |  | 6157 | 1 | 0x03c02137
TPVCirc8Tok_L1_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ8Tok_L1 | 0 | 8000 | 0 | 800.0 | A | ###.# |  | 6157 | 1 | 0x03c02138
TPVCirc8Tok_L2_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ8Tok_L2 | 0 | 8000 | 0 | 800.0 | A | ###.# |  | 6157 | 1 | 0x03c02139
TPVCirc8Tok_L3_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ8Tok_L3 | 0 | 8000 | 0 | 800.0 | A | ###.# |  | 6157 | 1 | 0x03c0213a
TPVCirc9NicelniTok_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ9NicelniTok | 0 | 8000 | 0 | 800.0 | A | ###.# |  | 6157 | 1 | 0x03c0213b
TPVCirc9Tok_L1_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ9Tok_L1 | 0 | 8000 | 0 | 800.0 | A | ###.# |  | 6157 | 1 | 0x03c0213c
TPVCirc9Tok_L2_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ9Tok_L2 | 0 | 8000 | 0 | 800.0 | A | ###.# |  | 6157 | 1 | 0x03c0213d
TPVCirc9Tok_L3_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ9Tok_L3 | 0 | 8000 | 0 | 800.0 | A | ###.# |  | 6157 | 1 | 0x03c0213e
TPVCirc1MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ1MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02171
TPVCirc1MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ1MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02172
TPVCirc2MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ2MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02173
TPVCirc2MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ2MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02174
TPVCirc3MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ3MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02175
TPVCirc3MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ3MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02176
TPVCirc4MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ4MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02177
TPVCirc4MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ4MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02178
TPVCirc5MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ5MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02179
TPVCirc5MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ5MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0217a
TPVCirc6MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ6MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0217b
TPVCirc6MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ6MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0217c
TPVCirc7MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ7MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0217d
TPVCirc7MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ7MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0217e
TPVCirc8MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ8MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0217f
TPVCirc8MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ8MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02180
TPVCirc9MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ9MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02181
TPVCirc9MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ9MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02182
TPVCirc10MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ10MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02183
TPVCirc10MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ10MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02184
TPVCirc11MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ11MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02185
TPVCirc11MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ11MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02186
TPVCirc12MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ12MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02187
TPVCirc12MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ12MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02188
TPVCirc13MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ13MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02189
TPVCirc13MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ13MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0218a
TPVCirc14MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ14MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0218b
TPVCirc14MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ14MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0218c
TPVCirc15MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ15MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0218d
TPVCirc15MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ15MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0218e
TPVCirc16MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ16MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0218f
TPVCirc16MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ16MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02190
TPVCirc17MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ17MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02191
TPVCirc17MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ17MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02192
TPVCirc18MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ18MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02193
TPVCirc18MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ18MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02194
TPVCirc19MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ19MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02195
TPVCirc19MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ19MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02196
TPVCirc20MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ20MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02197
TPVCirc20MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ20MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02198
TPVCirc21MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ21MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c02199
TPVCirc21MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ21MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0219a
TPVCirc22MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ22MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0219b
TPVCirc22MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ22MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0219c
TPVCirc23MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ23MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0219d
TPVCirc23MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ23MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0219e
TPVCirc24MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ24MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c0219f
TPVCirc24MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ24MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c021a0
TPVCirc25MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ25MaximumDemandA2 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c021a1
TPVCirc25MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ25MaximumDemandA3 | 0 | 12000 | 0 | 1200.0 | A | ###.# |  | 6157 |  | 0x03c021a2
TPVCirc1RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[1].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021a3
TPVCirc1RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[1].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021a4
TPVCirc1RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[1].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021a5
TPVCirc2RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[2].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021a6
TPVCirc2RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[2].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021a7
TPVCirc2RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[2].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021a8
TPVCirc3RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[3].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021a9
TPVCirc3RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[3].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021aa
TPVCirc3RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[3].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021ab
TPVCirc4RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[4].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021ac
TPVCirc4RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[4].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021ad
TPVCirc4RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[4].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021ae
TPVCirc5RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[5].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021af
TPVCirc5RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[5].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021b0
TPVCirc5RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[5].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021b1
TPVCirc6RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[6].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021b2
TPVCirc6RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[6].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021b3
TPVCirc6RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[6].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021b4
TPVCirc7RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[7].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021b5
TPVCirc7RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[7].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021b6
TPVCirc7RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[7].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021b7
TPVCirc8RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[8].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021b8
TPVCirc8RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[8].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021b9
TPVCirc8RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[8].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021ba
TPVCirc9RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[9].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021bb
TPVCirc9RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[9].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021bc
TPVCirc9RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[9].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021bd
TPVCirc10RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[10].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021be
TPVCirc10RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[10].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021bf
TPVCirc10RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[10].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021c0
TPVCirc11RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[11].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021c1
TPVCirc11RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[11].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021c2
TPVCirc11RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[11].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021c3
TPVCirc12RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[12].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021c4
TPVCirc12RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[12].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021c5
TPVCirc12RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[12].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021c6
TPVCirc13RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[13].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021c7
TPVCirc13RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[13].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021c8
TPVCirc13RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[13].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021c9
TPVCirc14RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[14].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021ca
TPVCirc14RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[14].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021cb
TPVCirc14RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[14].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021cc
TPVCirc15RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[15].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021cd
TPVCirc15RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[15].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021ce
TPVCirc15RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[15].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021cf
TPVCirc16RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[16].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021d0
TPVCirc16RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[16].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021d1
TPVCirc16RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[16].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021d2
TPVCirc17RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[17].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021d3
TPVCirc17RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[17].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021d4
TPVCirc17RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[17].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021d5
TPVCirc18RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[18].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021d6
TPVCirc18RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[18].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021d7
TPVCirc18RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[18].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021d8
TPVCirc19RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[19].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021d9
TPVCirc19RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[19].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021da
TPVCirc19RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[19].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021db
TPVCirc20RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[20].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021dc
TPVCirc20RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[20].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021dd
TPVCirc20RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[20].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021de
TPVCirc21RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[21].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021df
TPVCirc21RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[21].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021e0
TPVCirc21RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[21].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021e1
TPVCirc22RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[22].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021e2
TPVCirc22RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[22].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021e3
TPVCirc22RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[22].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021e4
TPVCirc23RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[23].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021e5
TPVCirc23RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[23].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021e6
TPVCirc23RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[23].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021e7
TPVCirc24RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[24].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021e8
TPVCirc24RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[24].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021e9
TPVCirc24RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[24].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021ea
TPVCirc25RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[25].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x03c021eb
TPVCirc25RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[25].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x03c021ec
TPVCirc25RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[25].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x03c021ed
TPVCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Dnevne_energija_scada1 | [7 empty] | 6157 | 1 | 0x03c021f0
TPVCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Dnevne_energija_scada2 | [7 empty] | 6157 | 1 | 0x03c02200
TPVCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Tedenska_energija_scada1 | [7 empty] | 6157 | 1 | 0x03c02210
TPVCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Tedenska_energija_scada2 | [7 empty] | 6157 | 1 | 0x03c02220
TPVCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Mesecna_energija_scada1 | [7 empty] | 6157 | 1 | 0x03c02230
TPVCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Mesecna_energija_scada2 | [7 empty] | 6157 | 1 | 0x03c02240
TPVCirc_Vpis_Dnevne_energija_scada1_mem | DIGITAL | IOD_TPV_disk | D9000 | [9 empty] | 0x03c02250
TPVCirc_Vpis_Dnevne_energija_scada2_mem | DIGITAL | IOD_TPV_disk | D9001 | [9 empty] | 0x03c02260
TPVCirc_Vpis_Tedenska_energija_scada1_mem | DIGITAL | IOD_TPV_disk | D9002 | [9 empty] | 0x03c02270
TPVCirc_Vpis_Tedenska_energija_scada2_mem | DIGITAL | IOD_TPV_disk | D9003 | [9 empty] | 0x03c02280
TPVCirc_Vpis_Mesecna_energija_scada1_mem | DIGITAL | IOD_TPV_disk | D9004 | [9 empty] | 0x03c02290
TPVCirc_Vpis_Mesecna_energija_scada2_mem | DIGITAL | IOD_TPV_disk | D9005 | [9 empty] | 0x03c022a0

## variable_1
TPVBattery_voltageA1 | UINT | IOD_TPV | TPV:.Battery_voltageA1
TPVBattery_voltageA2 | UINT | IOD_TPV | TPV:.Battery_voltageA2
TPVCharge_alternator_voltageA1 | UINT | IOD_TPV | TPV:.Charge_alternator_voltageA1
TPVCharge_alternator_voltageA2 | UINT | IOD_TPV | TPV:.Charge_alternator_voltageA2
TPVCirc10CosFi_III | LONG | IOD_TPV | TPV:.Circ10CosFi_III
TPVCirc10DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ10DelovnaEnergija
TPVCirc10DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ10DelovnaMoc_III
TPVCirc10DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ10DelovnaMoc_L1
TPVCirc10DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ10DelovnaMoc_L2
TPVCirc10DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ10DelovnaMoc_L3
TPVCirc10Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ10Frekvenca_L1
TPVCirc10InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ10InduktivnaEnergija
TPVCirc10InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ10InduktivnaMoc_III
TPVCirc10JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ10JalovaMoc_L1
TPVCirc10JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ10JalovaMoc_L2
TPVCirc10JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ10JalovaMoc_L3
TPVCirc10KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ10KapacitivnaEnergija
TPVCirc10KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ10KapacitivnaMoc_III
TPVCirc10MaximumDemand | LONG | IOD_TPV | TPV:.Circ10MaximumDemand
TPVCirc10Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ10Napetost_L1_L2
TPVCirc10Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ10Napetost_L1_N
TPVCirc10Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ10Napetost_L2_L3
TPVCirc10Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ10Napetost_L2_N
TPVCirc10Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ10Napetost_L3_L1
TPVCirc10Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ10Napetost_L3_N
TPVCirc10NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ10NavideznaMoc_III
TPVCirc10NicelniTok | LONG | IOD_TPV | TPV:.Circ10NicelniTok
TPVCirc10PowerFactor_III | LONG | IOD_TPV | TPV:.Circ10PowerFactor_III
TPVCirc10PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ10PowerFactor_L1
TPVCirc10PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ10PowerFactor_L2
TPVCirc10PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ10PowerFactor_L3
TPVCirc10THDI_L1 | LONG | IOD_TPV | TPV:.Circ10THDI_L1
TPVCirc10THDI_L2 | LONG | IOD_TPV | TPV:.Circ10THDI_L2
TPVCirc10THDI_L3 | LONG | IOD_TPV | TPV:.Circ10THDI_L3
TPVCirc10THDV_L1 | LONG | IOD_TPV | TPV:.Circ10THDV_L1
TPVCirc10THDV_L2 | LONG | IOD_TPV | TPV:.Circ10THDV_L2
TPVCirc10THDV_L3 | LONG | IOD_TPV | TPV:.Circ10THDV_L3
TPVCirc10Tok_L1 | LONG | IOD_TPV | TPV:.Circ10Tok_L1
TPVCirc10Tok_L2 | LONG | IOD_TPV | TPV:.Circ10Tok_L2
TPVCirc10Tok_L3 | LONG | IOD_TPV | TPV:.Circ10Tok_L3
TPVCirc10TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ10TokPovprecje_III
TPVCirc11CosFi_III | LONG | IOD_TPV | TPV:.Circ11CosFi_III
TPVCirc11DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ11DelovnaEnergija
TPVCirc11DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ11DelovnaMoc_III
TPVCirc11DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ11DelovnaMoc_L1
TPVCirc11DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ11DelovnaMoc_L2
TPVCirc11DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ11DelovnaMoc_L3
TPVCirc11Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ11Frekvenca_L1
TPVCirc11InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ11InduktivnaEnergija
TPVCirc11InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ11InduktivnaMoc_III
TPVCirc11JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ11JalovaMoc_L1
TPVCirc11JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ11JalovaMoc_L2
TPVCirc11JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ11JalovaMoc_L3
TPVCirc11KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ11KapacitivnaEnergija
TPVCirc11KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ11KapacitivnaMoc_III
TPVCirc11MaximumDemand | LONG | IOD_TPV | TPV:.Circ11MaximumDemand
TPVCirc11Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ11Napetost_L1_L2
TPVCirc11Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ11Napetost_L1_N
TPVCirc11Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ11Napetost_L2_L3
TPVCirc11Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ11Napetost_L2_N
TPVCirc11Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ11Napetost_L3_L1
TPVCirc11Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ11Napetost_L3_N
TPVCirc11NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ11NavideznaMoc_III
TPVCirc11NicelniTok | LONG | IOD_TPV | TPV:.Circ11NicelniTok
TPVCirc11PowerFactor_III | LONG | IOD_TPV | TPV:.Circ11PowerFactor_III
TPVCirc11PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ11PowerFactor_L1
TPVCirc11PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ11PowerFactor_L2
TPVCirc11PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ11PowerFactor_L3
TPVCirc11THDI_L1 | LONG | IOD_TPV | TPV:.Circ11THDI_L1
TPVCirc11THDI_L2 | LONG | IOD_TPV | TPV:.Circ11THDI_L2
TPVCirc11THDI_L3 | LONG | IOD_TPV | TPV:.Circ11THDI_L3
TPVCirc11THDV_L1 | LONG | IOD_TPV | TPV:.Circ11THDV_L1
TPVCirc11THDV_L2 | LONG | IOD_TPV | TPV:.Circ11THDV_L2
TPVCirc11THDV_L3 | LONG | IOD_TPV | TPV:.Circ11THDV_L3
TPVCirc11Tok_L1 | LONG | IOD_TPV | TPV:.Circ11Tok_L1
TPVCirc11Tok_L2 | LONG | IOD_TPV | TPV:.Circ11Tok_L2
TPVCirc11Tok_L3 | LONG | IOD_TPV | TPV:.Circ11Tok_L3
TPVCirc11TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ11TokPovprecje_III
TPVCirc12CosFi_III | LONG | IOD_TPV | TPV:.Circ12CosFi_III
TPVCirc12DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ12DelovnaEnergija
TPVCirc12DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ12DelovnaMoc_III
TPVCirc12DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ12DelovnaMoc_L1
TPVCirc12DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ12DelovnaMoc_L2
TPVCirc12DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ12DelovnaMoc_L3
TPVCirc12Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ12Frekvenca_L1
TPVCirc12InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ12InduktivnaEnergija
TPVCirc12InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ12InduktivnaMoc_III
TPVCirc12JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ12JalovaMoc_L1
TPVCirc12JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ12JalovaMoc_L2
TPVCirc12JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ12JalovaMoc_L3
TPVCirc12KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ12KapacitivnaEnergija
TPVCirc12KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ12KapacitivnaMoc_III
TPVCirc12MaximumDemand | LONG | IOD_TPV | TPV:.Circ12MaximumDemand
TPVCirc12Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ12Napetost_L1_L2
TPVCirc12Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ12Napetost_L1_N
TPVCirc12Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ12Napetost_L2_L3
TPVCirc12Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ12Napetost_L2_N
TPVCirc12Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ12Napetost_L3_L1
TPVCirc12Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ12Napetost_L3_N
TPVCirc12NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ12NavideznaMoc_III
TPVCirc12NicelniTok | LONG | IOD_TPV | TPV:.Circ12NicelniTok
TPVCirc12PowerFactor_III | LONG | IOD_TPV | TPV:.Circ12PowerFactor_III
TPVCirc12PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ12PowerFactor_L1
TPVCirc12PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ12PowerFactor_L2
TPVCirc12PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ12PowerFactor_L3
TPVCirc12THDI_L1 | LONG | IOD_TPV | TPV:.Circ12THDI_L1
TPVCirc12THDI_L2 | LONG | IOD_TPV | TPV:.Circ12THDI_L2
TPVCirc12THDI_L3 | LONG | IOD_TPV | TPV:.Circ12THDI_L3
TPVCirc12THDV_L1 | LONG | IOD_TPV | TPV:.Circ12THDV_L1
TPVCirc12THDV_L2 | LONG | IOD_TPV | TPV:.Circ12THDV_L2
TPVCirc12THDV_L3 | LONG | IOD_TPV | TPV:.Circ12THDV_L3
TPVCirc12Tok_L1 | LONG | IOD_TPV | TPV:.Circ12Tok_L1
TPVCirc12Tok_L2 | LONG | IOD_TPV | TPV:.Circ12Tok_L2
TPVCirc12Tok_L3 | LONG | IOD_TPV | TPV:.Circ12Tok_L3
TPVCirc12TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ12TokPovprecje_III
TPVCirc13CosFi_III | LONG | IOD_TPV | TPV:.Circ13CosFi_III
TPVCirc13DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ13DelovnaEnergija
TPVCirc13DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ13DelovnaMoc_III
TPVCirc13DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ13DelovnaMoc_L1
TPVCirc13DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ13DelovnaMoc_L2
TPVCirc13DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ13DelovnaMoc_L3
TPVCirc13Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ13Frekvenca_L1
TPVCirc13InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ13InduktivnaEnergija
TPVCirc13InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ13InduktivnaMoc_III
TPVCirc13JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ13JalovaMoc_L1
TPVCirc13JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ13JalovaMoc_L2
TPVCirc13JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ13JalovaMoc_L3
TPVCirc13KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ13KapacitivnaEnergija
TPVCirc13KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ13KapacitivnaMoc_III
TPVCirc13MaximumDemand | LONG | IOD_TPV | TPV:.Circ13MaximumDemand
TPVCirc13Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ13Napetost_L1_L2
TPVCirc13Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ13Napetost_L1_N
TPVCirc13Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ13Napetost_L2_L3
TPVCirc13Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ13Napetost_L2_N
TPVCirc13Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ13Napetost_L3_L1
TPVCirc13Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ13Napetost_L3_N
TPVCirc13NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ13NavideznaMoc_III
TPVCirc13NicelniTok | LONG | IOD_TPV | TPV:.Circ13NicelniTok
TPVCirc13PowerFactor_III | LONG | IOD_TPV | TPV:.Circ13PowerFactor_III
TPVCirc13PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ13PowerFactor_L1
TPVCirc13PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ13PowerFactor_L2
TPVCirc13PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ13PowerFactor_L3
TPVCirc13THDI_L1 | LONG | IOD_TPV | TPV:.Circ13THDI_L1
TPVCirc13THDI_L2 | LONG | IOD_TPV | TPV:.Circ13THDI_L2
TPVCirc13THDI_L3 | LONG | IOD_TPV | TPV:.Circ13THDI_L3
TPVCirc13THDV_L1 | LONG | IOD_TPV | TPV:.Circ13THDV_L1
TPVCirc13THDV_L2 | LONG | IOD_TPV | TPV:.Circ13THDV_L2
TPVCirc13THDV_L3 | LONG | IOD_TPV | TPV:.Circ13THDV_L3
TPVCirc13Tok_L1 | LONG | IOD_TPV | TPV:.Circ13Tok_L1
TPVCirc13Tok_L2 | LONG | IOD_TPV | TPV:.Circ13Tok_L2
TPVCirc13Tok_L3 | LONG | IOD_TPV | TPV:.Circ13Tok_L3
TPVCirc13TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ13TokPovprecje_III
TPVCirc14CosFi_III | LONG | IOD_TPV | TPV:.Circ14CosFi_III
TPVCirc14DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ14DelovnaEnergija
TPVCirc14DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ14DelovnaMoc_III
TPVCirc14DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ14DelovnaMoc_L1
TPVCirc14DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ14DelovnaMoc_L2
TPVCirc14DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ14DelovnaMoc_L3
TPVCirc14Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ14Frekvenca_L1
TPVCirc14InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ14InduktivnaEnergija
TPVCirc14InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ14InduktivnaMoc_III
TPVCirc14JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ14JalovaMoc_L1
TPVCirc14JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ14JalovaMoc_L2
TPVCirc14JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ14JalovaMoc_L3
TPVCirc14KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ14KapacitivnaEnergija
TPVCirc14KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ14KapacitivnaMoc_III
TPVCirc14MaximumDemand | LONG | IOD_TPV | TPV:.Circ14MaximumDemand
TPVCirc14Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ14Napetost_L1_L2
TPVCirc14Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ14Napetost_L1_N
TPVCirc14Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ14Napetost_L2_L3
TPVCirc14Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ14Napetost_L2_N
TPVCirc14Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ14Napetost_L3_L1
TPVCirc14Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ14Napetost_L3_N
TPVCirc14NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ14NavideznaMoc_III
TPVCirc14NicelniTok | LONG | IOD_TPV | TPV:.Circ14NicelniTok
TPVCirc14PowerFactor_III | LONG | IOD_TPV | TPV:.Circ14PowerFactor_III
TPVCirc14PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ14PowerFactor_L1
TPVCirc14PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ14PowerFactor_L2
TPVCirc14PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ14PowerFactor_L3
TPVCirc14THDI_L1 | LONG | IOD_TPV | TPV:.Circ14THDI_L1
TPVCirc14THDI_L2 | LONG | IOD_TPV | TPV:.Circ14THDI_L2
TPVCirc14THDI_L3 | LONG | IOD_TPV | TPV:.Circ14THDI_L3
TPVCirc14THDV_L1 | LONG | IOD_TPV | TPV:.Circ14THDV_L1
TPVCirc14THDV_L2 | LONG | IOD_TPV | TPV:.Circ14THDV_L2
TPVCirc14THDV_L3 | LONG | IOD_TPV | TPV:.Circ14THDV_L3
TPVCirc14Tok_L1 | LONG | IOD_TPV | TPV:.Circ14Tok_L1
TPVCirc14Tok_L2 | LONG | IOD_TPV | TPV:.Circ14Tok_L2
TPVCirc14Tok_L3 | LONG | IOD_TPV | TPV:.Circ14Tok_L3
TPVCirc14TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ14TokPovprecje_III
TPVCirc15CosFi_III | LONG | IOD_TPV | TPV:.Circ15CosFi_III
TPVCirc15DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ15DelovnaEnergija
TPVCirc15DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ15DelovnaMoc_III
TPVCirc15DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ15DelovnaMoc_L1
TPVCirc15DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ15DelovnaMoc_L2
TPVCirc15DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ15DelovnaMoc_L3
TPVCirc15Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ15Frekvenca_L1
TPVCirc15InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ15InduktivnaEnergija
TPVCirc15InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ15InduktivnaMoc_III
TPVCirc15JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ15JalovaMoc_L1
TPVCirc15JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ15JalovaMoc_L2
TPVCirc15JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ15JalovaMoc_L3
TPVCirc15KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ15KapacitivnaEnergija
TPVCirc15KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ15KapacitivnaMoc_III
TPVCirc15MaximumDemand | LONG | IOD_TPV | TPV:.Circ15MaximumDemand
TPVCirc15Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ15Napetost_L1_L2
TPVCirc15Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ15Napetost_L1_N
TPVCirc15Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ15Napetost_L2_L3
TPVCirc15Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ15Napetost_L2_N
TPVCirc15Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ15Napetost_L3_L1
TPVCirc15Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ15Napetost_L3_N
TPVCirc15NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ15NavideznaMoc_III
TPVCirc15NicelniTok | LONG | IOD_TPV | TPV:.Circ15NicelniTok
TPVCirc15PowerFactor_III | LONG | IOD_TPV | TPV:.Circ15PowerFactor_III
TPVCirc15PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ15PowerFactor_L1
TPVCirc15PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ15PowerFactor_L2
TPVCirc15PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ15PowerFactor_L3
TPVCirc15THDI_L1 | LONG | IOD_TPV | TPV:.Circ15THDI_L1
TPVCirc15THDI_L2 | LONG | IOD_TPV | TPV:.Circ15THDI_L2
TPVCirc15THDI_L3 | LONG | IOD_TPV | TPV:.Circ15THDI_L3
TPVCirc15THDV_L1 | LONG | IOD_TPV | TPV:.Circ15THDV_L1
TPVCirc15THDV_L2 | LONG | IOD_TPV | TPV:.Circ15THDV_L2
TPVCirc15THDV_L3 | LONG | IOD_TPV | TPV:.Circ15THDV_L3
TPVCirc15Tok_L1 | LONG | IOD_TPV | TPV:.Circ15Tok_L1
TPVCirc15Tok_L2 | LONG | IOD_TPV | TPV:.Circ15Tok_L2
TPVCirc15Tok_L3 | LONG | IOD_TPV | TPV:.Circ15Tok_L3
TPVCirc15TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ15TokPovprecje_III
TPVCirc16CosFi_III | LONG | IOD_TPV | TPV:.Circ16CosFi_III
TPVCirc16DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ16DelovnaEnergija
TPVCirc16DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ16DelovnaMoc_III
TPVCirc16DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ16DelovnaMoc_L1
TPVCirc16DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ16DelovnaMoc_L2
TPVCirc16DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ16DelovnaMoc_L3
TPVCirc16Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ16Frekvenca_L1
TPVCirc16InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ16InduktivnaEnergija
TPVCirc16InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ16InduktivnaMoc_III
TPVCirc16JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ16JalovaMoc_L1
TPVCirc16JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ16JalovaMoc_L2
TPVCirc16JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ16JalovaMoc_L3
TPVCirc16KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ16KapacitivnaEnergija
TPVCirc16KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ16KapacitivnaMoc_III
TPVCirc16MaximumDemand | LONG | IOD_TPV | TPV:.Circ16MaximumDemand
TPVCirc16Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ16Napetost_L1_L2
TPVCirc16Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ16Napetost_L1_N
TPVCirc16Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ16Napetost_L2_L3
TPVCirc16Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ16Napetost_L2_N
TPVCirc16Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ16Napetost_L3_L1
TPVCirc16Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ16Napetost_L3_N
TPVCirc16NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ16NavideznaMoc_III
TPVCirc16NicelniTok | LONG | IOD_TPV | TPV:.Circ16NicelniTok
TPVCirc16PowerFactor_III | LONG | IOD_TPV | TPV:.Circ16PowerFactor_III
TPVCirc16PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ16PowerFactor_L1
TPVCirc16PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ16PowerFactor_L2
TPVCirc16PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ16PowerFactor_L3
TPVCirc16THDI_L1 | LONG | IOD_TPV | TPV:.Circ16THDI_L1
TPVCirc16THDI_L2 | LONG | IOD_TPV | TPV:.Circ16THDI_L2
TPVCirc16THDI_L3 | LONG | IOD_TPV | TPV:.Circ16THDI_L3
TPVCirc16THDV_L1 | LONG | IOD_TPV | TPV:.Circ16THDV_L1
TPVCirc16THDV_L2 | LONG | IOD_TPV | TPV:.Circ16THDV_L2
TPVCirc16THDV_L3 | LONG | IOD_TPV | TPV:.Circ16THDV_L3
TPVCirc16Tok_L1 | LONG | IOD_TPV | TPV:.Circ16Tok_L1
TPVCirc16Tok_L2 | LONG | IOD_TPV | TPV:.Circ16Tok_L2
TPVCirc16Tok_L3 | LONG | IOD_TPV | TPV:.Circ16Tok_L3
TPVCirc16TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ16TokPovprecje_III
TPVCirc17CosFi_III | LONG | IOD_TPV | TPV:.Circ17CosFi_III
TPVCirc17DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ17DelovnaEnergija
TPVCirc17DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ17DelovnaMoc_III
TPVCirc17DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ17DelovnaMoc_L1
TPVCirc17DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ17DelovnaMoc_L2
TPVCirc17DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ17DelovnaMoc_L3
TPVCirc17Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ17Frekvenca_L1
TPVCirc17InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ17InduktivnaEnergija
TPVCirc17InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ17InduktivnaMoc_III
TPVCirc17JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ17JalovaMoc_L1
TPVCirc17JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ17JalovaMoc_L2
TPVCirc17JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ17JalovaMoc_L3
TPVCirc17KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ17KapacitivnaEnergija
TPVCirc17KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ17KapacitivnaMoc_III
TPVCirc17MaximumDemand | LONG | IOD_TPV | TPV:.Circ17MaximumDemand
TPVCirc17Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ17Napetost_L1_L2
TPVCirc17Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ17Napetost_L1_N
TPVCirc17Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ17Napetost_L2_L3
TPVCirc17Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ17Napetost_L2_N
TPVCirc17Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ17Napetost_L3_L1
TPVCirc17Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ17Napetost_L3_N
TPVCirc17NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ17NavideznaMoc_III
TPVCirc17NicelniTok | LONG | IOD_TPV | TPV:.Circ17NicelniTok
TPVCirc17PowerFactor_III | LONG | IOD_TPV | TPV:.Circ17PowerFactor_III
TPVCirc17PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ17PowerFactor_L1
TPVCirc17PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ17PowerFactor_L2
TPVCirc17PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ17PowerFactor_L3
TPVCirc17THDI_L1 | LONG | IOD_TPV | TPV:.Circ17THDI_L1
TPVCirc17THDI_L2 | LONG | IOD_TPV | TPV:.Circ17THDI_L2
TPVCirc17THDI_L3 | LONG | IOD_TPV | TPV:.Circ17THDI_L3
TPVCirc17THDV_L1 | LONG | IOD_TPV | TPV:.Circ17THDV_L1
TPVCirc17THDV_L2 | LONG | IOD_TPV | TPV:.Circ17THDV_L2
TPVCirc17THDV_L3 | LONG | IOD_TPV | TPV:.Circ17THDV_L3
TPVCirc17Tok_L1 | LONG | IOD_TPV | TPV:.Circ17Tok_L1
TPVCirc17Tok_L2 | LONG | IOD_TPV | TPV:.Circ17Tok_L2
TPVCirc17Tok_L3 | LONG | IOD_TPV | TPV:.Circ17Tok_L3
TPVCirc17TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ17TokPovprecje_III
TPVCirc18CosFi_III | LONG | IOD_TPV | TPV:.Circ18CosFi_III
TPVCirc18DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ18DelovnaEnergija
TPVCirc18DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ18DelovnaMoc_III
TPVCirc18DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ18DelovnaMoc_L1
TPVCirc18DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ18DelovnaMoc_L2
TPVCirc18DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ18DelovnaMoc_L3
TPVCirc18Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ18Frekvenca_L1
TPVCirc18InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ18InduktivnaEnergija
TPVCirc18InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ18InduktivnaMoc_III
TPVCirc18JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ18JalovaMoc_L1
TPVCirc18JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ18JalovaMoc_L2
TPVCirc18JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ18JalovaMoc_L3
TPVCirc18KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ18KapacitivnaEnergija
TPVCirc18KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ18KapacitivnaMoc_III
TPVCirc18MaximumDemand | LONG | IOD_TPV | TPV:.Circ18MaximumDemand
TPVCirc18Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ18Napetost_L1_L2
TPVCirc18Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ18Napetost_L1_N
TPVCirc18Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ18Napetost_L2_L3
TPVCirc18Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ18Napetost_L2_N
TPVCirc18Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ18Napetost_L3_L1
TPVCirc18Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ18Napetost_L3_N
TPVCirc18NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ18NavideznaMoc_III
TPVCirc18NicelniTok | LONG | IOD_TPV | TPV:.Circ18NicelniTok
TPVCirc18PowerFactor_III | LONG | IOD_TPV | TPV:.Circ18PowerFactor_III
TPVCirc18PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ18PowerFactor_L1
TPVCirc18PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ18PowerFactor_L2
TPVCirc18PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ18PowerFactor_L3
TPVCirc18THDI_L1 | LONG | IOD_TPV | TPV:.Circ18THDI_L1
TPVCirc18THDI_L2 | LONG | IOD_TPV | TPV:.Circ18THDI_L2
TPVCirc18THDI_L3 | LONG | IOD_TPV | TPV:.Circ18THDI_L3
TPVCirc18THDV_L1 | LONG | IOD_TPV | TPV:.Circ18THDV_L1
TPVCirc18THDV_L2 | LONG | IOD_TPV | TPV:.Circ18THDV_L2
TPVCirc18THDV_L3 | LONG | IOD_TPV | TPV:.Circ18THDV_L3
TPVCirc18Tok_L1 | LONG | IOD_TPV | TPV:.Circ18Tok_L1
TPVCirc18Tok_L2 | LONG | IOD_TPV | TPV:.Circ18Tok_L2
TPVCirc18Tok_L3 | LONG | IOD_TPV | TPV:.Circ18Tok_L3
TPVCirc18TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ18TokPovprecje_III
TPVCirc19CosFi_III | LONG | IOD_TPV | TPV:.Circ19CosFi_III
TPVCirc19DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ19DelovnaEnergija
TPVCirc19DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ19DelovnaMoc_III
TPVCirc19DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ19DelovnaMoc_L1
TPVCirc19DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ19DelovnaMoc_L2
TPVCirc19DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ19DelovnaMoc_L3
TPVCirc19Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ19Frekvenca_L1
TPVCirc19InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ19InduktivnaEnergija
TPVCirc19InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ19InduktivnaMoc_III
TPVCirc19JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ19JalovaMoc_L1
TPVCirc19JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ19JalovaMoc_L2
TPVCirc19JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ19JalovaMoc_L3
TPVCirc19KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ19KapacitivnaEnergija
TPVCirc19KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ19KapacitivnaMoc_III
TPVCirc19MaximumDemand | LONG | IOD_TPV | TPV:.Circ19MaximumDemand
TPVCirc19Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ19Napetost_L1_L2
TPVCirc19Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ19Napetost_L1_N
TPVCirc19Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ19Napetost_L2_L3
TPVCirc19Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ19Napetost_L2_N
TPVCirc19Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ19Napetost_L3_L1
TPVCirc19Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ19Napetost_L3_N
TPVCirc19NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ19NavideznaMoc_III
TPVCirc19NicelniTok | LONG | IOD_TPV | TPV:.Circ19NicelniTok
TPVCirc19PowerFactor_III | LONG | IOD_TPV | TPV:.Circ19PowerFactor_III
TPVCirc19PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ19PowerFactor_L1
TPVCirc19PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ19PowerFactor_L2
TPVCirc19PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ19PowerFactor_L3
TPVCirc19THDI_L1 | LONG | IOD_TPV | TPV:.Circ19THDI_L1
TPVCirc19THDI_L2 | LONG | IOD_TPV | TPV:.Circ19THDI_L2
TPVCirc19THDI_L3 | LONG | IOD_TPV | TPV:.Circ19THDI_L3
TPVCirc19THDV_L1 | LONG | IOD_TPV | TPV:.Circ19THDV_L1
TPVCirc19THDV_L2 | LONG | IOD_TPV | TPV:.Circ19THDV_L2
TPVCirc19THDV_L3 | LONG | IOD_TPV | TPV:.Circ19THDV_L3
TPVCirc19Tok_L1 | LONG | IOD_TPV | TPV:.Circ19Tok_L1
TPVCirc19Tok_L2 | LONG | IOD_TPV | TPV:.Circ19Tok_L2
TPVCirc19Tok_L3 | LONG | IOD_TPV | TPV:.Circ19Tok_L3
TPVCirc19TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ19TokPovprecje_III
TPVCirc1CosFi_III | LONG | IOD_TPV | TPV:.Circ1CosFi_III
TPVCirc1DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ1DelovnaEnergija
TPVCirc1DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ1DelovnaMoc_III
TPVCirc1DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ1DelovnaMoc_L1
TPVCirc1DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ1DelovnaMoc_L2
TPVCirc1DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ1DelovnaMoc_L3
TPVCirc1Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ1Frekvenca_L1
TPVCirc1InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ1InduktivnaEnergija
TPVCirc1InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ1InduktivnaMoc_III
TPVCirc1JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ1JalovaMoc_L1
TPVCirc1JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ1JalovaMoc_L2
TPVCirc1JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ1JalovaMoc_L3
TPVCirc1KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ1KapacitivnaEnergija
TPVCirc1KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ1KapacitivnaMoc_III
TPVCirc1MaximumDemand | LONG | IOD_TPV | TPV:.Circ1MaximumDemand
TPVCirc1Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ1Napetost_L1_L2
TPVCirc1Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ1Napetost_L1_N
TPVCirc1Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ1Napetost_L2_L3
TPVCirc1Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ1Napetost_L2_N
TPVCirc1Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ1Napetost_L3_L1
TPVCirc1Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ1Napetost_L3_N
TPVCirc1NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ1NavideznaMoc_III
TPVCirc1NicelniTok | LONG | IOD_TPV | TPV:.Circ1NicelniTok
TPVCirc1PowerFactor_III | LONG | IOD_TPV | TPV:.Circ1PowerFactor_III
TPVCirc1PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ1PowerFactor_L1
TPVCirc1PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ1PowerFactor_L2
TPVCirc1PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ1PowerFactor_L3
TPVCirc1THDI_L1 | LONG | IOD_TPV | TPV:.Circ1THDI_L1
TPVCirc1THDI_L2 | LONG | IOD_TPV | TPV:.Circ1THDI_L2
TPVCirc1THDI_L3 | LONG | IOD_TPV | TPV:.Circ1THDI_L3
TPVCirc1THDV_L1 | LONG | IOD_TPV | TPV:.Circ1THDV_L1
TPVCirc1THDV_L2 | LONG | IOD_TPV | TPV:.Circ1THDV_L2
TPVCirc1THDV_L3 | LONG | IOD_TPV | TPV:.Circ1THDV_L3
TPVCirc1Tok_L1 | LONG | IOD_TPV | TPV:.Circ1Tok_L1
TPVCirc1Tok_L2 | LONG | IOD_TPV | TPV:.Circ1Tok_L2
TPVCirc1Tok_L3 | LONG | IOD_TPV | TPV:.Circ1Tok_L3
TPVCirc1TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ1TokPovprecje_III
TPVCirc20CosFi_III | LONG | IOD_TPV | TPV:.Circ20CosFi_III
TPVCirc20DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ20DelovnaEnergija
TPVCirc20DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ20DelovnaMoc_III
TPVCirc20DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ20DelovnaMoc_L1
TPVCirc20DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ20DelovnaMoc_L2
TPVCirc20DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ20DelovnaMoc_L3
TPVCirc20Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ20Frekvenca_L1
TPVCirc20InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ20InduktivnaEnergija
TPVCirc20InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ20InduktivnaMoc_III
TPVCirc20JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ20JalovaMoc_L1
TPVCirc20JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ20JalovaMoc_L2
TPVCirc20JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ20JalovaMoc_L3
TPVCirc20KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ20KapacitivnaEnergija
TPVCirc20KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ20KapacitivnaMoc_III
TPVCirc20MaximumDemand | LONG | IOD_TPV | TPV:.Circ20MaximumDemand
TPVCirc20Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ20Napetost_L1_L2
TPVCirc20Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ20Napetost_L1_N
TPVCirc20Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ20Napetost_L2_L3
TPVCirc20Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ20Napetost_L2_N
TPVCirc20Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ20Napetost_L3_L1
TPVCirc20Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ20Napetost_L3_N
TPVCirc20NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ20NavideznaMoc_III
TPVCirc20NicelniTok | LONG | IOD_TPV | TPV:.Circ20NicelniTok
TPVCirc20PowerFactor_III | LONG | IOD_TPV | TPV:.Circ20PowerFactor_III
TPVCirc20PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ20PowerFactor_L1
TPVCirc20PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ20PowerFactor_L2
TPVCirc20PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ20PowerFactor_L3
TPVCirc20THDI_L1 | LONG | IOD_TPV | TPV:.Circ20THDI_L1
TPVCirc20THDI_L2 | LONG | IOD_TPV | TPV:.Circ20THDI_L2
TPVCirc20THDI_L3 | LONG | IOD_TPV | TPV:.Circ20THDI_L3
TPVCirc20THDV_L1 | LONG | IOD_TPV | TPV:.Circ20THDV_L1
TPVCirc20THDV_L2 | LONG | IOD_TPV | TPV:.Circ20THDV_L2
TPVCirc20THDV_L3 | LONG | IOD_TPV | TPV:.Circ20THDV_L3
TPVCirc20Tok_L1 | LONG | IOD_TPV | TPV:.Circ20Tok_L1
TPVCirc20Tok_L2 | LONG | IOD_TPV | TPV:.Circ20Tok_L2
TPVCirc20Tok_L3 | LONG | IOD_TPV | TPV:.Circ20Tok_L3
TPVCirc20TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ20TokPovprecje_III
TPVCirc21CosFi_III | LONG | IOD_TPV | TPV:.Circ21CosFi_III
TPVCirc21DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ21DelovnaEnergija
TPVCirc21DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ21DelovnaMoc_III
TPVCirc21DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ21DelovnaMoc_L1
TPVCirc21DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ21DelovnaMoc_L2
TPVCirc21DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ21DelovnaMoc_L3
TPVCirc21Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ21Frekvenca_L1
TPVCirc21InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ21InduktivnaEnergija
TPVCirc21InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ21InduktivnaMoc_III
TPVCirc21JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ21JalovaMoc_L1
TPVCirc21JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ21JalovaMoc_L2
TPVCirc21JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ21JalovaMoc_L3
TPVCirc21KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ21KapacitivnaEnergija
TPVCirc21KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ21KapacitivnaMoc_III
TPVCirc21MaximumDemand | LONG | IOD_TPV | TPV:.Circ21MaximumDemand
TPVCirc21Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ21Napetost_L1_L2
TPVCirc21Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ21Napetost_L1_N
TPVCirc21Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ21Napetost_L2_L3
TPVCirc21Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ21Napetost_L2_N
TPVCirc21Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ21Napetost_L3_L1
TPVCirc21Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ21Napetost_L3_N
TPVCirc21NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ21NavideznaMoc_III
TPVCirc21NicelniTok | LONG | IOD_TPV | TPV:.Circ21NicelniTok
TPVCirc21PowerFactor_III | LONG | IOD_TPV | TPV:.Circ21PowerFactor_III
TPVCirc21PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ21PowerFactor_L1
TPVCirc21PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ21PowerFactor_L2
TPVCirc21PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ21PowerFactor_L3
TPVCirc21THDI_L1 | LONG | IOD_TPV | TPV:.Circ21THDI_L1
TPVCirc21THDI_L2 | LONG | IOD_TPV | TPV:.Circ21THDI_L2
TPVCirc21THDI_L3 | LONG | IOD_TPV | TPV:.Circ21THDI_L3
TPVCirc21THDV_L1 | LONG | IOD_TPV | TPV:.Circ21THDV_L1
TPVCirc21THDV_L2 | LONG | IOD_TPV | TPV:.Circ21THDV_L2
TPVCirc21THDV_L3 | LONG | IOD_TPV | TPV:.Circ21THDV_L3
TPVCirc21Tok_L1 | LONG | IOD_TPV | TPV:.Circ21Tok_L1
TPVCirc21Tok_L2 | LONG | IOD_TPV | TPV:.Circ21Tok_L2
TPVCirc21Tok_L3 | LONG | IOD_TPV | TPV:.Circ21Tok_L3
TPVCirc21TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ21TokPovprecje_III
TPVCirc22CosFi_III | LONG | IOD_TPV | TPV:.Circ22CosFi_III
TPVCirc22DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ22DelovnaEnergija
TPVCirc22DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ22DelovnaMoc_III
TPVCirc22DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ22DelovnaMoc_L1
TPVCirc22DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ22DelovnaMoc_L2
TPVCirc22DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ22DelovnaMoc_L3
TPVCirc22Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ22Frekvenca_L1
TPVCirc22InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ22InduktivnaEnergija
TPVCirc22InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ22InduktivnaMoc_III
TPVCirc22JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ22JalovaMoc_L1
TPVCirc22JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ22JalovaMoc_L2
TPVCirc22JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ22JalovaMoc_L3
TPVCirc22KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ22KapacitivnaEnergija
TPVCirc22KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ22KapacitivnaMoc_III
TPVCirc22MaximumDemand | LONG | IOD_TPV | TPV:.Circ22MaximumDemand
TPVCirc22Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ22Napetost_L1_L2
TPVCirc22Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ22Napetost_L1_N
TPVCirc22Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ22Napetost_L2_L3
TPVCirc22Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ22Napetost_L2_N
TPVCirc22Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ22Napetost_L3_L1
TPVCirc22Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ22Napetost_L3_N
TPVCirc22NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ22NavideznaMoc_III
TPVCirc22NicelniTok | LONG | IOD_TPV | TPV:.Circ22NicelniTok
TPVCirc22PowerFactor_III | LONG | IOD_TPV | TPV:.Circ22PowerFactor_III
TPVCirc22PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ22PowerFactor_L1
TPVCirc22PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ22PowerFactor_L2
TPVCirc22PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ22PowerFactor_L3
TPVCirc22THDI_L1 | LONG | IOD_TPV | TPV:.Circ22THDI_L1
TPVCirc22THDI_L2 | LONG | IOD_TPV | TPV:.Circ22THDI_L2
TPVCirc22THDI_L3 | LONG | IOD_TPV | TPV:.Circ22THDI_L3
TPVCirc22THDV_L1 | LONG | IOD_TPV | TPV:.Circ22THDV_L1
TPVCirc22THDV_L2 | LONG | IOD_TPV | TPV:.Circ22THDV_L2
TPVCirc22THDV_L3 | LONG | IOD_TPV | TPV:.Circ22THDV_L3
TPVCirc22Tok_L1 | LONG | IOD_TPV | TPV:.Circ22Tok_L1
TPVCirc22Tok_L2 | LONG | IOD_TPV | TPV:.Circ22Tok_L2
TPVCirc22Tok_L3 | LONG | IOD_TPV | TPV:.Circ22Tok_L3
TPVCirc22TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ22TokPovprecje_III
TPVCirc23CosFi_III | LONG | IOD_TPV | TPV:.Circ23CosFi_III
TPVCirc23DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ23DelovnaEnergija
TPVCirc23DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ23DelovnaMoc_III
TPVCirc23DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ23DelovnaMoc_L1
TPVCirc23DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ23DelovnaMoc_L2
TPVCirc23DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ23DelovnaMoc_L3
TPVCirc23Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ23Frekvenca_L1
TPVCirc23InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ23InduktivnaEnergija
TPVCirc23InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ23InduktivnaMoc_III
TPVCirc23JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ23JalovaMoc_L1
TPVCirc23JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ23JalovaMoc_L2
TPVCirc23JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ23JalovaMoc_L3
TPVCirc23KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ23KapacitivnaEnergija
TPVCirc23KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ23KapacitivnaMoc_III
TPVCirc23MaximumDemand | LONG | IOD_TPV | TPV:.Circ23MaximumDemand
TPVCirc23Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ23Napetost_L1_L2
TPVCirc23Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ23Napetost_L1_N
TPVCirc23Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ23Napetost_L2_L3
TPVCirc23Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ23Napetost_L2_N
TPVCirc23Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ23Napetost_L3_L1
TPVCirc23Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ23Napetost_L3_N
TPVCirc23NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ23NavideznaMoc_III
TPVCirc23NicelniTok | LONG | IOD_TPV | TPV:.Circ23NicelniTok
TPVCirc23PowerFactor_III | LONG | IOD_TPV | TPV:.Circ23PowerFactor_III
TPVCirc23PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ23PowerFactor_L1
TPVCirc23PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ23PowerFactor_L2
TPVCirc23PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ23PowerFactor_L3
TPVCirc23THDI_L1 | LONG | IOD_TPV | TPV:.Circ23THDI_L1
TPVCirc23THDI_L2 | LONG | IOD_TPV | TPV:.Circ23THDI_L2
TPVCirc23THDI_L3 | LONG | IOD_TPV | TPV:.Circ23THDI_L3
TPVCirc23THDV_L1 | LONG | IOD_TPV | TPV:.Circ23THDV_L1
TPVCirc23THDV_L2 | LONG | IOD_TPV | TPV:.Circ23THDV_L2
TPVCirc23THDV_L3 | LONG | IOD_TPV | TPV:.Circ23THDV_L3
TPVCirc23Tok_L1 | LONG | IOD_TPV | TPV:.Circ23Tok_L1
TPVCirc23Tok_L2 | LONG | IOD_TPV | TPV:.Circ23Tok_L2
TPVCirc23Tok_L3 | LONG | IOD_TPV | TPV:.Circ23Tok_L3
TPVCirc23TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ23TokPovprecje_III
TPVCirc24CosFi_III | LONG | IOD_TPV | TPV:.Circ24CosFi_III
TPVCirc24DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ24DelovnaEnergija
TPVCirc24DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ24DelovnaMoc_III
TPVCirc24DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ24DelovnaMoc_L1
TPVCirc24DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ24DelovnaMoc_L2
TPVCirc24DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ24DelovnaMoc_L3
TPVCirc24Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ24Frekvenca_L1
TPVCirc24InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ24InduktivnaEnergija
TPVCirc24InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ24InduktivnaMoc_III
TPVCirc24JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ24JalovaMoc_L1
TPVCirc24JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ24JalovaMoc_L2
TPVCirc24JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ24JalovaMoc_L3
TPVCirc24KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ24KapacitivnaEnergija
TPVCirc24KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ24KapacitivnaMoc_III
TPVCirc24MaximumDemand | LONG | IOD_TPV | TPV:.Circ24MaximumDemand
TPVCirc24Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ24Napetost_L1_L2
TPVCirc24Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ24Napetost_L1_N
TPVCirc24Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ24Napetost_L2_L3
TPVCirc24Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ24Napetost_L2_N
TPVCirc24Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ24Napetost_L3_L1
TPVCirc24Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ24Napetost_L3_N
TPVCirc24NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ24NavideznaMoc_III
TPVCirc24NicelniTok | LONG | IOD_TPV | TPV:.Circ24NicelniTok
TPVCirc24PowerFactor_III | LONG | IOD_TPV | TPV:.Circ24PowerFactor_III
TPVCirc24PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ24PowerFactor_L1
TPVCirc24PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ24PowerFactor_L2
TPVCirc24PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ24PowerFactor_L3
TPVCirc24THDI_L1 | LONG | IOD_TPV | TPV:.Circ24THDI_L1
TPVCirc24THDI_L2 | LONG | IOD_TPV | TPV:.Circ24THDI_L2
TPVCirc24THDI_L3 | LONG | IOD_TPV | TPV:.Circ24THDI_L3
TPVCirc24THDV_L1 | LONG | IOD_TPV | TPV:.Circ24THDV_L1
TPVCirc24THDV_L2 | LONG | IOD_TPV | TPV:.Circ24THDV_L2
TPVCirc24THDV_L3 | LONG | IOD_TPV | TPV:.Circ24THDV_L3
TPVCirc24Tok_L1 | LONG | IOD_TPV | TPV:.Circ24Tok_L1
TPVCirc24Tok_L2 | LONG | IOD_TPV | TPV:.Circ24Tok_L2
TPVCirc24Tok_L3 | LONG | IOD_TPV | TPV:.Circ24Tok_L3
TPVCirc24TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ24TokPovprecje_III
TPVCirc25CosFi_III | LONG | IOD_TPV | TPV:.Circ25CosFi_III
TPVCirc25DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ25DelovnaEnergija
TPVCirc25DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ25DelovnaMoc_III
TPVCirc25DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ25DelovnaMoc_L1
TPVCirc25DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ25DelovnaMoc_L2
TPVCirc25DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ25DelovnaMoc_L3
TPVCirc25Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ25Frekvenca_L1
TPVCirc25InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ25InduktivnaEnergija
TPVCirc25InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ25InduktivnaMoc_III
TPVCirc25JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ25JalovaMoc_L1
TPVCirc25JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ25JalovaMoc_L2
TPVCirc25JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ25JalovaMoc_L3
TPVCirc25KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ25KapacitivnaEnergija
TPVCirc25KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ25KapacitivnaMoc_III
TPVCirc25MaximumDemand | LONG | IOD_TPV | TPV:.Circ25MaximumDemand
TPVCirc25Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ25Napetost_L1_L2
TPVCirc25Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ25Napetost_L1_N
TPVCirc25Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ25Napetost_L2_L3
TPVCirc25Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ25Napetost_L2_N
TPVCirc25Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ25Napetost_L3_L1
TPVCirc25Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ25Napetost_L3_N
TPVCirc25NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ25NavideznaMoc_III
TPVCirc25NicelniTok | LONG | IOD_TPV | TPV:.Circ25NicelniTok
TPVCirc25PowerFactor_III | LONG | IOD_TPV | TPV:.Circ25PowerFactor_III
TPVCirc25PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ25PowerFactor_L1
TPVCirc25PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ25PowerFactor_L2
TPVCirc25PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ25PowerFactor_L3
TPVCirc25THDI_L1 | LONG | IOD_TPV | TPV:.Circ25THDI_L1
TPVCirc25THDI_L2 | LONG | IOD_TPV | TPV:.Circ25THDI_L2
TPVCirc25THDI_L3 | LONG | IOD_TPV | TPV:.Circ25THDI_L3
TPVCirc25THDV_L1 | LONG | IOD_TPV | TPV:.Circ25THDV_L1
TPVCirc25THDV_L2 | LONG | IOD_TPV | TPV:.Circ25THDV_L2
TPVCirc25THDV_L3 | LONG | IOD_TPV | TPV:.Circ25THDV_L3
TPVCirc25Tok_L1 | LONG | IOD_TPV | TPV:.Circ25Tok_L1
TPVCirc25Tok_L2 | LONG | IOD_TPV | TPV:.Circ25Tok_L2
TPVCirc25Tok_L3 | LONG | IOD_TPV | TPV:.Circ25Tok_L3
TPVCirc25TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ25TokPovprecje_III
TPVCirc2CosFi_III | LONG | IOD_TPV | TPV:.Circ2CosFi_III
TPVCirc2DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ2DelovnaEnergija
TPVCirc2DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ2DelovnaMoc_III
TPVCirc2DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ2DelovnaMoc_L1
TPVCirc2DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ2DelovnaMoc_L2
TPVCirc2DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ2DelovnaMoc_L3
TPVCirc2Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ2Frekvenca_L1
TPVCirc2InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ2InduktivnaEnergija
TPVCirc2InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ2InduktivnaMoc_III
TPVCirc2JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ2JalovaMoc_L1
TPVCirc2JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ2JalovaMoc_L2
TPVCirc2JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ2JalovaMoc_L3
TPVCirc2KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ2KapacitivnaEnergija
TPVCirc2KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ2KapacitivnaMoc_III
TPVCirc2MaximumDemand | LONG | IOD_TPV | TPV:.Circ2MaximumDemand
TPVCirc2Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ2Napetost_L1_L2
TPVCirc2Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ2Napetost_L1_N
TPVCirc2Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ2Napetost_L2_L3
TPVCirc2Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ2Napetost_L2_N
TPVCirc2Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ2Napetost_L3_L1
TPVCirc2Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ2Napetost_L3_N
TPVCirc2NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ2NavideznaMoc_III
TPVCirc2NicelniTok | LONG | IOD_TPV | TPV:.Circ2NicelniTok
TPVCirc2PowerFactor_III | LONG | IOD_TPV | TPV:.Circ2PowerFactor_III
TPVCirc2PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ2PowerFactor_L1
TPVCirc2PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ2PowerFactor_L2
TPVCirc2PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ2PowerFactor_L3
TPVCirc2THDI_L1 | LONG | IOD_TPV | TPV:.Circ2THDI_L1
TPVCirc2THDI_L2 | LONG | IOD_TPV | TPV:.Circ2THDI_L2
TPVCirc2THDI_L3 | LONG | IOD_TPV | TPV:.Circ2THDI_L3
TPVCirc2THDV_L1 | LONG | IOD_TPV | TPV:.Circ2THDV_L1
TPVCirc2THDV_L2 | LONG | IOD_TPV | TPV:.Circ2THDV_L2
TPVCirc2THDV_L3 | LONG | IOD_TPV | TPV:.Circ2THDV_L3
TPVCirc2Tok_L1 | LONG | IOD_TPV | TPV:.Circ2Tok_L1
TPVCirc2Tok_L2 | LONG | IOD_TPV | TPV:.Circ2Tok_L2
TPVCirc2Tok_L3 | LONG | IOD_TPV | TPV:.Circ2Tok_L3
TPVCirc2TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ2TokPovprecje_III
TPVCirc3CosFi_III | LONG | IOD_TPV | TPV:.Circ3CosFi_III
TPVCirc3DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ3DelovnaEnergija
TPVCirc3DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ3DelovnaMoc_III
TPVCirc3DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ3DelovnaMoc_L1
TPVCirc3DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ3DelovnaMoc_L2
TPVCirc3DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ3DelovnaMoc_L3
TPVCirc3Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ3Frekvenca_L1
TPVCirc3InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ3InduktivnaEnergija
TPVCirc3InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ3InduktivnaMoc_III
TPVCirc3JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ3JalovaMoc_L1
TPVCirc3JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ3JalovaMoc_L2
TPVCirc3JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ3JalovaMoc_L3
TPVCirc3KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ3KapacitivnaEnergija
TPVCirc3KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ3KapacitivnaMoc_III
TPVCirc3MaximumDemand | LONG | IOD_TPV | TPV:.Circ3MaximumDemand
TPVCirc3Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ3Napetost_L1_L2
TPVCirc3Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ3Napetost_L1_N
TPVCirc3Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ3Napetost_L2_L3
TPVCirc3Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ3Napetost_L2_N
TPVCirc3Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ3Napetost_L3_L1
TPVCirc3Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ3Napetost_L3_N
TPVCirc3NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ3NavideznaMoc_III
TPVCirc3NicelniTok | LONG | IOD_TPV | TPV:.Circ3NicelniTok
TPVCirc3PowerFactor_III | LONG | IOD_TPV | TPV:.Circ3PowerFactor_III
TPVCirc3PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ3PowerFactor_L1
TPVCirc3PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ3PowerFactor_L2
TPVCirc3PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ3PowerFactor_L3
TPVCirc3THDI_L1 | LONG | IOD_TPV | TPV:.Circ3THDI_L1
TPVCirc3THDI_L2 | LONG | IOD_TPV | TPV:.Circ3THDI_L2
TPVCirc3THDI_L3 | LONG | IOD_TPV | TPV:.Circ3THDI_L3
TPVCirc3THDV_L1 | LONG | IOD_TPV | TPV:.Circ3THDV_L1
TPVCirc3THDV_L2 | LONG | IOD_TPV | TPV:.Circ3THDV_L2
TPVCirc3THDV_L3 | LONG | IOD_TPV | TPV:.Circ3THDV_L3
TPVCirc3Tok_L1 | LONG | IOD_TPV | TPV:.Circ3Tok_L1
TPVCirc3Tok_L2 | LONG | IOD_TPV | TPV:.Circ3Tok_L2
TPVCirc3Tok_L3 | LONG | IOD_TPV | TPV:.Circ3Tok_L3
TPVCirc3TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ3TokPovprecje_III
TPVCirc4CosFi_III | LONG | IOD_TPV | TPV:.Circ4CosFi_III
TPVCirc4DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ4DelovnaEnergija
TPVCirc4DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ4DelovnaMoc_III
TPVCirc4DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ4DelovnaMoc_L1
TPVCirc4DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ4DelovnaMoc_L2
TPVCirc4DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ4DelovnaMoc_L3
TPVCirc4Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ4Frekvenca_L1
TPVCirc4InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ4InduktivnaEnergija
TPVCirc4InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ4InduktivnaMoc_III
TPVCirc4JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ4JalovaMoc_L1
TPVCirc4JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ4JalovaMoc_L2
TPVCirc4JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ4JalovaMoc_L3
TPVCirc4KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ4KapacitivnaEnergija
TPVCirc4KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ4KapacitivnaMoc_III
TPVCirc4MaximumDemand | LONG | IOD_TPV | TPV:.Circ4MaximumDemand
TPVCirc4Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ4Napetost_L1_L2
TPVCirc4Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ4Napetost_L1_N
TPVCirc4Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ4Napetost_L2_L3
TPVCirc4Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ4Napetost_L2_N
TPVCirc4Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ4Napetost_L3_L1
TPVCirc4Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ4Napetost_L3_N
TPVCirc4NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ4NavideznaMoc_III
TPVCirc4NicelniTok | LONG | IOD_TPV | TPV:.Circ4NicelniTok
TPVCirc4PowerFactor_III | LONG | IOD_TPV | TPV:.Circ4PowerFactor_III
TPVCirc4PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ4PowerFactor_L1
TPVCirc4PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ4PowerFactor_L2
TPVCirc4PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ4PowerFactor_L3
TPVCirc4THDI_L1 | LONG | IOD_TPV | TPV:.Circ4THDI_L1
TPVCirc4THDI_L2 | LONG | IOD_TPV | TPV:.Circ4THDI_L2
TPVCirc4THDI_L3 | LONG | IOD_TPV | TPV:.Circ4THDI_L3
TPVCirc4THDV_L1 | LONG | IOD_TPV | TPV:.Circ4THDV_L1
TPVCirc4THDV_L2 | LONG | IOD_TPV | TPV:.Circ4THDV_L2
TPVCirc4THDV_L3 | LONG | IOD_TPV | TPV:.Circ4THDV_L3
TPVCirc4Tok_L1 | LONG | IOD_TPV | TPV:.Circ4Tok_L1
TPVCirc4Tok_L2 | LONG | IOD_TPV | TPV:.Circ4Tok_L2
TPVCirc4Tok_L3 | LONG | IOD_TPV | TPV:.Circ4Tok_L3
TPVCirc4TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ4TokPovprecje_III
TPVCirc5CosFi_III | LONG | IOD_TPV | TPV:.Circ5CosFi_III
TPVCirc5DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ5DelovnaEnergija
TPVCirc5DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ5DelovnaMoc_III
TPVCirc5DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ5DelovnaMoc_L1
TPVCirc5DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ5DelovnaMoc_L2
TPVCirc5DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ5DelovnaMoc_L3
TPVCirc5Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ5Frekvenca_L1
TPVCirc5InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ5InduktivnaEnergija
TPVCirc5InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ5InduktivnaMoc_III
TPVCirc5JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ5JalovaMoc_L1
TPVCirc5JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ5JalovaMoc_L2
TPVCirc5JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ5JalovaMoc_L3
TPVCirc5KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ5KapacitivnaEnergija
TPVCirc5KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ5KapacitivnaMoc_III
TPVCirc5MaximumDemand | LONG | IOD_TPV | TPV:.Circ5MaximumDemand
TPVCirc5Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ5Napetost_L1_L2
TPVCirc5Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ5Napetost_L1_N
TPVCirc5Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ5Napetost_L2_L3
TPVCirc5Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ5Napetost_L2_N
TPVCirc5Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ5Napetost_L3_L1
TPVCirc5Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ5Napetost_L3_N
TPVCirc5NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ5NavideznaMoc_III
TPVCirc5NicelniTok | LONG | IOD_TPV | TPV:.Circ5NicelniTok
TPVCirc5PowerFactor_III | LONG | IOD_TPV | TPV:.Circ5PowerFactor_III
TPVCirc5PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ5PowerFactor_L1
TPVCirc5PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ5PowerFactor_L2
TPVCirc5PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ5PowerFactor_L3
TPVCirc5THDI_L1 | LONG | IOD_TPV | TPV:.Circ5THDI_L1
TPVCirc5THDI_L2 | LONG | IOD_TPV | TPV:.Circ5THDI_L2
TPVCirc5THDI_L3 | LONG | IOD_TPV | TPV:.Circ5THDI_L3
TPVCirc5THDV_L1 | LONG | IOD_TPV | TPV:.Circ5THDV_L1
TPVCirc5THDV_L2 | LONG | IOD_TPV | TPV:.Circ5THDV_L2
TPVCirc5THDV_L3 | LONG | IOD_TPV | TPV:.Circ5THDV_L3
TPVCirc5Tok_L1 | LONG | IOD_TPV | TPV:.Circ5Tok_L1
TPVCirc5Tok_L2 | LONG | IOD_TPV | TPV:.Circ5Tok_L2
TPVCirc5Tok_L3 | LONG | IOD_TPV | TPV:.Circ5Tok_L3
TPVCirc5TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ5TokPovprecje_III
TPVCirc6CosFi_III | LONG | IOD_TPV | TPV:.Circ6CosFi_III
TPVCirc6DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ6DelovnaEnergija
TPVCirc6DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ6DelovnaMoc_III
TPVCirc6DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ6DelovnaMoc_L1
TPVCirc6DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ6DelovnaMoc_L2
TPVCirc6DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ6DelovnaMoc_L3
TPVCirc6Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ6Frekvenca_L1
TPVCirc6InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ6InduktivnaEnergija
TPVCirc6InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ6InduktivnaMoc_III
TPVCirc6JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ6JalovaMoc_L1
TPVCirc6JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ6JalovaMoc_L2
TPVCirc6JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ6JalovaMoc_L3
TPVCirc6KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ6KapacitivnaEnergija
TPVCirc6KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ6KapacitivnaMoc_III
TPVCirc6MaximumDemand | LONG | IOD_TPV | TPV:.Circ6MaximumDemand
TPVCirc6Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ6Napetost_L1_L2
TPVCirc6Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ6Napetost_L1_N
TPVCirc6Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ6Napetost_L2_L3
TPVCirc6Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ6Napetost_L2_N
TPVCirc6Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ6Napetost_L3_L1
TPVCirc6Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ6Napetost_L3_N
TPVCirc6NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ6NavideznaMoc_III
TPVCirc6NicelniTok | LONG | IOD_TPV | TPV:.Circ6NicelniTok
TPVCirc6PowerFactor_III | LONG | IOD_TPV | TPV:.Circ6PowerFactor_III
TPVCirc6PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ6PowerFactor_L1
TPVCirc6PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ6PowerFactor_L2
TPVCirc6PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ6PowerFactor_L3
TPVCirc6THDI_L1 | LONG | IOD_TPV | TPV:.Circ6THDI_L1
TPVCirc6THDI_L2 | LONG | IOD_TPV | TPV:.Circ6THDI_L2
TPVCirc6THDI_L3 | LONG | IOD_TPV | TPV:.Circ6THDI_L3
TPVCirc6THDV_L1 | LONG | IOD_TPV | TPV:.Circ6THDV_L1
TPVCirc6THDV_L2 | LONG | IOD_TPV | TPV:.Circ6THDV_L2
TPVCirc6THDV_L3 | LONG | IOD_TPV | TPV:.Circ6THDV_L3
TPVCirc6Tok_L1 | LONG | IOD_TPV | TPV:.Circ6Tok_L1
TPVCirc6Tok_L2 | LONG | IOD_TPV | TPV:.Circ6Tok_L2
TPVCirc6Tok_L3 | LONG | IOD_TPV | TPV:.Circ6Tok_L3
TPVCirc6TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ6TokPovprecje_III
TPVCirc7CosFi_III | LONG | IOD_TPV | TPV:.Circ7CosFi_III
TPVCirc7DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ7DelovnaEnergija
TPVCirc7DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ7DelovnaMoc_III
TPVCirc7DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ7DelovnaMoc_L1
TPVCirc7DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ7DelovnaMoc_L2
TPVCirc7DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ7DelovnaMoc_L3
TPVCirc7Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ7Frekvenca_L1
TPVCirc7InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ7InduktivnaEnergija
TPVCirc7InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ7InduktivnaMoc_III
TPVCirc7JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ7JalovaMoc_L1
TPVCirc7JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ7JalovaMoc_L2
TPVCirc7JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ7JalovaMoc_L3
TPVCirc7KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ7KapacitivnaEnergija
TPVCirc7KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ7KapacitivnaMoc_III
TPVCirc7MaximumDemand | LONG | IOD_TPV | TPV:.Circ7MaximumDemand
TPVCirc7Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ7Napetost_L1_L2
TPVCirc7Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ7Napetost_L1_N
TPVCirc7Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ7Napetost_L2_L3
TPVCirc7Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ7Napetost_L2_N
TPVCirc7Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ7Napetost_L3_L1
TPVCirc7Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ7Napetost_L3_N
TPVCirc7NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ7NavideznaMoc_III
TPVCirc7NicelniTok | LONG | IOD_TPV | TPV:.Circ7NicelniTok
TPVCirc7PowerFactor_III | LONG | IOD_TPV | TPV:.Circ7PowerFactor_III
TPVCirc7PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ7PowerFactor_L1
TPVCirc7PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ7PowerFactor_L2
TPVCirc7PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ7PowerFactor_L3
TPVCirc7THDI_L1 | LONG | IOD_TPV | TPV:.Circ7THDI_L1
TPVCirc7THDI_L2 | LONG | IOD_TPV | TPV:.Circ7THDI_L2
TPVCirc7THDI_L3 | LONG | IOD_TPV | TPV:.Circ7THDI_L3
TPVCirc7THDV_L1 | LONG | IOD_TPV | TPV:.Circ7THDV_L1
TPVCirc7THDV_L2 | LONG | IOD_TPV | TPV:.Circ7THDV_L2
TPVCirc7THDV_L3 | LONG | IOD_TPV | TPV:.Circ7THDV_L3
TPVCirc7Tok_L1 | LONG | IOD_TPV | TPV:.Circ7Tok_L1
TPVCirc7Tok_L2 | LONG | IOD_TPV | TPV:.Circ7Tok_L2
TPVCirc7Tok_L3 | LONG | IOD_TPV | TPV:.Circ7Tok_L3
TPVCirc7TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ7TokPovprecje_III
TPVCirc8CosFi_III | LONG | IOD_TPV | TPV:.Circ8CosFi_III
TPVCirc8DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ8DelovnaEnergija
TPVCirc8DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ8DelovnaMoc_III
TPVCirc8DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ8DelovnaMoc_L1
TPVCirc8DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ8DelovnaMoc_L2
TPVCirc8DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ8DelovnaMoc_L3
TPVCirc8Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ8Frekvenca_L1
TPVCirc8InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ8InduktivnaEnergija
TPVCirc8InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ8InduktivnaMoc_III
TPVCirc8JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ8JalovaMoc_L1
TPVCirc8JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ8JalovaMoc_L2
TPVCirc8JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ8JalovaMoc_L3
TPVCirc8KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ8KapacitivnaEnergija
TPVCirc8KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ8KapacitivnaMoc_III
TPVCirc8MaximumDemand | LONG | IOD_TPV | TPV:.Circ8MaximumDemand
TPVCirc8Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ8Napetost_L1_L2
TPVCirc8Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ8Napetost_L1_N
TPVCirc8Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ8Napetost_L2_L3
TPVCirc8Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ8Napetost_L2_N
TPVCirc8Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ8Napetost_L3_L1
TPVCirc8Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ8Napetost_L3_N
TPVCirc8NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ8NavideznaMoc_III
TPVCirc8NicelniTok | LONG | IOD_TPV | TPV:.Circ8NicelniTok
TPVCirc8PowerFactor_III | LONG | IOD_TPV | TPV:.Circ8PowerFactor_III
TPVCirc8PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ8PowerFactor_L1
TPVCirc8PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ8PowerFactor_L2
TPVCirc8PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ8PowerFactor_L3
TPVCirc8THDI_L1 | LONG | IOD_TPV | TPV:.Circ8THDI_L1
TPVCirc8THDI_L2 | LONG | IOD_TPV | TPV:.Circ8THDI_L2
TPVCirc8THDI_L3 | LONG | IOD_TPV | TPV:.Circ8THDI_L3
TPVCirc8THDV_L1 | LONG | IOD_TPV | TPV:.Circ8THDV_L1
TPVCirc8THDV_L2 | LONG | IOD_TPV | TPV:.Circ8THDV_L2
TPVCirc8THDV_L3 | LONG | IOD_TPV | TPV:.Circ8THDV_L3
TPVCirc8Tok_L1 | LONG | IOD_TPV | TPV:.Circ8Tok_L1
TPVCirc8Tok_L2 | LONG | IOD_TPV | TPV:.Circ8Tok_L2
TPVCirc8Tok_L3 | LONG | IOD_TPV | TPV:.Circ8Tok_L3
TPVCirc8TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ8TokPovprecje_III
TPVCirc9CosFi_III | LONG | IOD_TPV | TPV:.Circ9CosFi_III
TPVCirc9DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ9DelovnaEnergija
TPVCirc9DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ9DelovnaMoc_III
TPVCirc9DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ9DelovnaMoc_L1
TPVCirc9DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ9DelovnaMoc_L2
TPVCirc9DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ9DelovnaMoc_L3
TPVCirc9Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ9Frekvenca_L1
TPVCirc9InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ9InduktivnaEnergija
TPVCirc9InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ9InduktivnaMoc_III
TPVCirc9JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ9JalovaMoc_L1
TPVCirc9JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ9JalovaMoc_L2
TPVCirc9JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ9JalovaMoc_L3
TPVCirc9KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ9KapacitivnaEnergija
TPVCirc9KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ9KapacitivnaMoc_III
TPVCirc9MaximumDemand | LONG | IOD_TPV | TPV:.Circ9MaximumDemand
TPVCirc9Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ9Napetost_L1_L2
TPVCirc9Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ9Napetost_L1_N
TPVCirc9Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ9Napetost_L2_L3
TPVCirc9Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ9Napetost_L2_N
TPVCirc9Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ9Napetost_L3_L1
TPVCirc9Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ9Napetost_L3_N
TPVCirc9NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ9NavideznaMoc_III
TPVCirc9NicelniTok | LONG | IOD_TPV | TPV:.Circ9NicelniTok
TPVCirc9PowerFactor_III | LONG | IOD_TPV | TPV:.Circ9PowerFactor_III
TPVCirc9PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ9PowerFactor_L1
TPVCirc9PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ9PowerFactor_L2
TPVCirc9PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ9PowerFactor_L3
TPVCirc9THDI_L1 | LONG | IOD_TPV | TPV:.Circ9THDI_L1
TPVCirc9THDI_L2 | LONG | IOD_TPV | TPV:.Circ9THDI_L2
TPVCirc9THDI_L3 | LONG | IOD_TPV | TPV:.Circ9THDI_L3
TPVCirc9THDV_L1 | LONG | IOD_TPV | TPV:.Circ9THDV_L1
TPVCirc9THDV_L2 | LONG | IOD_TPV | TPV:.Circ9THDV_L2
TPVCirc9THDV_L3 | LONG | IOD_TPV | TPV:.Circ9THDV_L3
TPVCirc9Tok_L1 | LONG | IOD_TPV | TPV:.Circ9Tok_L1
TPVCirc9Tok_L2 | LONG | IOD_TPV | TPV:.Circ9Tok_L2
TPVCirc9Tok_L3 | LONG | IOD_TPV | TPV:.Circ9Tok_L3
TPVCirc9TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ9TokPovprecje_III
TPVCoolant_temperatureA1 | INT | IOD_TPV | TPV:.Coolant_temperatureA1
TPVCoolant_temperatureA2 | INT | IOD_TPV | TPV:.Coolant_temperatureA2
TPVDA3_rocno | DIGITAL | IOD_TPV | TPV:.DA3_rocno
TPVDA3motorni_pogon_okvara | DIGITAL | IOD_TPV | TPV:.DA3motorni_pogon_okvara
TPVdelovna_energ_trenutno | INT | IOD_TPV | TPV:.delovna_energ_trenutno
TPVdelovna_energija_prej | INT | IOD_TPV | TPV:.delovna_energija_prej
TPVDW_Napake1 | LONG | IOD_TPV | TPV:.DW_Napake1
TPVDW_Napake2 | LONG | IOD_TPV | TPV:.DW_Napake2
TPVDW_Napake3 | LONG | IOD_TPV | TPV:.DW_Napake3
TPVEngine_speedA1 | UINT | IOD_TPV | TPV:.Engine_speedA1
TPVEngine_speedA2 | UINT | IOD_TPV | TPV:.Engine_speedA2
TPV_Generator_current_lag_leadA1 | INT | IOD_TPV | TPV:.Generator_current_lag_leadA1
TPV_Generator_current_lag_leadA2 | INT | IOD_TPV | TPV:.Generator_current_lag_leadA2
TPV_Generator_earth_currentA1 | LONG | IOD_TPV | TPV:.Generator_earth_currentA1
TPV_Generator_earth_currentA2 | LONG | IOD_TPV | TPV:.Generator_earth_currentA2
TPV_Generator_frequencyA1 | UINT | IOD_TPV | TPV:.Generator_frequencyA1
TPV_Generator_frequencyA2 | UINT | IOD_TPV | TPV:.Generator_frequencyA2
TPV_Generator_L1_currentA1 | LONG | IOD_TPV | TPV:.Generator_L1_currentA1
TPV_Generator_L1_currentA2 | LONG | IOD_TPV | TPV:.Generator_L1_currentA2
TPV_Generator_L1_L2_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L1_L2_voltageA1
TPV_Generator_L1_L2_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L1_L2_voltageA2
TPV_Generator_L1_N_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L1_N_voltageA1
TPV_Generator_L1_N_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L1_N_voltageA2
TPV_Generator_L1_wattsA1 | LONG | IOD_TPV | TPV:.Generator_L1_wattsA1
TPV_Generator_L1_wattsA2 | LONG | IOD_TPV | TPV:.Generator_L1_wattsA2
TPV_Generator_L2_currentA1 | LONG | IOD_TPV | TPV:.Generator_L2_currentA1
TPV_Generator_L2_currentA2 | LONG | IOD_TPV | TPV:.Generator_L2_currentA2
TPV_Generator_L2_L3_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L2_L3_voltageA1
TPV_Generator_L2_L3_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L2_L3_voltageA2
TPV_Generator_L2_N_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L2_N_voltageA1
TPV_Generator_L2_N_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L2_N_voltageA2
TPV_Generator_L2_wattsA1 | LONG | IOD_TPV | TPV:.Generator_L2_wattsA1
TPV_Generator_L2_wattsA2 | LONG | IOD_TPV | TPV:.Generator_L2_wattsA2
TPV_Generator_L3_currentA1 | LONG | IOD_TPV | TPV:.Generator_L3_currentA1
TPV_Generator_L3_currentA2 | LONG | IOD_TPV | TPV:.Generator_L3_currentA2
TPV_Generator_L3_L1_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L3_L1_voltageA1
TPV_Generator_L3_L1_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L3_L1_voltageA2
TPV_Generator_L3_N_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L3_N_voltageA1
TPV_Generator_L3_N_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L3_N_voltageA2
TPV_Generator_L3_wattsA1 | LONG | IOD_TPV | TPV:.Generator_L3_wattsA1
TPV_Generator_L3_wattsA2 | LONG | IOD_TPV | TPV:.Generator_L3_wattsA2
TPV_Generator_phase_rotationA1 | UINT | IOD_TPV | TPV:.Generator_phase_rotationA1
TPV_Generator_phase_rotationA2 | UINT | IOD_TPV | TPV:.Generator_phase_rotationA2
TPVIzpad_CAN_med_K1_K2 | DIGITAL | IOD_TPV | TPV:.Izpad_CAN_med_K1_K2
TPVjalova_energ_trenutno | INT | IOD_TPV | TPV:.jalova_energ_trenutno
TPVjalova_energija_prej | INT | IOD_TPV | TPV:.jalova_energija_prej
TPVKomanda | INT | IOD_TPV | TPV:.Komanda
TPVMI4agr_nap_RGM_A1 | DIGITAL | IOD_TPV | TPV:.MI4agr_nap_RGM_A1
TPVMI4agr_nap_RGM_A2 | DIGITAL | IOD_TPV | TPV:.MI4agr_nap_RGM_A2
TPVMI4DA1_2Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4DA1_2Q1_izklop
TPVMI4DA1_2Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4DA1_2Q1_vklop
TPVMI4DA1_del | DIGITAL | IOD_TPV | TPV:.MI4DA1_del
TPVMI4DA1_prip | DIGITAL | IOD_TPV | TPV:.MI4DA1_prip
TPVMI4DA1_rezerva | DIGITAL | IOD_TPV | TPV:.MI4DA1_rezerva
TPVMI4DA1_sinh | DIGITAL | IOD_TPV | TPV:.MI4DA1_sinh
TPVMI4DA1_zagon | DIGITAL | IOD_TPV | TPV:.MI4DA1_zagon
TPVMI4DA2_2Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4DA2_2Q1_izklop
TPVMI4DA2_2Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4DA2_2Q1_vklop
TPVMI4DA2_del | DIGITAL | IOD_TPV | TPV:.MI4DA2_del
TPVMI4DA2_prip | DIGITAL | IOD_TPV | TPV:.MI4DA2_prip
TPVMI4DA2_rezerva | DIGITAL | IOD_TPV | TPV:.MI4DA2_rezerva
TPVMI4DA2_sinh | DIGITAL | IOD_TPV | TPV:.MI4DA2_sinh
TPVMI4DA2_zagon | DIGITAL | IOD_TPV | TPV:.MI4DA2_zagon
TPVMI4del_zascA1_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_11Q1
TPVMI4del_zascA1_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_12Q1
TPVMI4del_zascA1_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_13Q1
TPVMI4del_zascA1_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_14Q1
TPVMI4del_zascA1_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_15Q1
TPVMI4del_zascA1_16Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_16Q1
TPVMI4del_zascA1_17Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_17Q1
TPVMI4del_zascA1_2Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_2Q1
TPVMI4del_zascA2_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA2_11Q1
TPVMI4del_zascA2_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA2_12Q1
TPVMI4del_zascA2_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA2_13Q1
TPVMI4del_zascA2_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA2_14Q1
TPVMI4K2agr_nap_RGM_A3 | DIGITAL | IOD_TPV | TPV:.MI4K2agr_nap_RGM_A3
TPVMI4K2DA3_2Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4K2DA3_2Q1_izklop
TPVMI4K2DA3_2Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4K2DA3_2Q1_vklop
TPVMI4K2del_zasc0_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_11Q1
TPVMI4K2del_zasc0_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_12Q1
TPVMI4K2del_zasc0_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_13Q1
TPVMI4K2del_zasc0_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_14Q1
TPVMI4K2del_zasc0_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_15Q1
TPVMI4K2del_zasc0_16Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_16Q1
TPVMI4K2del_zasc0_17Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_17Q1
TPVMI4K2del_zasc0_18Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_18Q1
TPVMI4K2del_zasc0_19Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_19Q1
TPVMI4K2del_zasc0_20Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_20Q1
TPVMI4K2del_zasc0_21Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_21Q1
TPVMI4K2del_zasc0_22Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_22Q1
TPVMI4K2del_zasc0_23Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_23Q1
TPVMI4K2del_zascA3_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zascA3_11Q1
TPVMI4K2del_zascA3_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zascA3_12Q1
TPVMI4K2del_zascA3_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zascA3_13Q1
TPVMI4K2del_zascA3_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zascA3_14Q1
TPVMI4K2del_zascA3_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zascA3_15Q1
TPVMI4K2motorA3_1Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4K2motorA3_1Q1_prip
TPVMI4K2motorA3_2Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4K2motorA3_2Q1_prip
TPVMI4K2mrez_nap_RGM_A3 | DIGITAL | IOD_TPV | TPV:.MI4K2mrez_nap_RGM_A3
TPVMI4K2mrezaA3_1Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4K2mrezaA3_1Q1_izklop
TPVMI4K2mrezaA3_1Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4K2mrezaA3_1Q1_vklop
TPVMI4K2prenap_zasc0_OK | DIGITAL | IOD_TPV | TPV:.MI4K2prenap_zasc0_OK
TPVMI4K2prenap_zascA3_OK | DIGITAL | IOD_TPV | TPV:.MI4K2prenap_zascA3_OK
TPVMI4K2rocni_izk0_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_11Q1
TPVMI4K2rocni_izk0_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_12Q1
TPVMI4K2rocni_izk0_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_13Q1
TPVMI4K2rocni_izk0_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_14Q1
TPVMI4K2rocni_izk0_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_15Q1
TPVMI4K2rocni_izk0_16Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_16Q1
TPVMI4K2rocni_izk0_17Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_17Q1
TPVMI4K2rocni_izk0_18Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_18Q1
TPVMI4K2rocni_izk0_19Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_19Q1
TPVMI4K2rocni_izk0_20Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_20Q1
TPVMI4K2rocni_izk0_21Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_21Q1
TPVMI4K2rocni_izk0_22Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_22Q1
TPVMI4K2rocni_izk0_23Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_23Q1
TPVMI4K2rocni_izkA3_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izkA3_11Q1
TPVMI4K2rocni_izkA3_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izkA3_12Q1
TPVMI4K2rocni_izkA3_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izkA3_13Q1
TPVMI4K2rocni_izkA3_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izkA3_14Q1
TPVMI4K2rocni_izkA3_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izkA3_15Q1
TPVMI4K2stik0_11Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_11Q1_vkl
TPVMI4K2stik0_12Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_12Q1_vkl
TPVMI4K2stik0_13Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_13Q1_vkl
TPVMI4K2stik0_14Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_14Q1_vkl
TPVMI4K2stik0_15Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_15Q1_vkl
TPVMI4K2stik0_16Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_16Q1_vkl
TPVMI4K2stik0_17Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_17Q1_vkl
TPVMI4K2stik0_18Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_18Q1_vkl
TPVMI4K2stik0_19Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_19Q1_vkl
TPVMI4K2stik0_1Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_1Q1_vkl
TPVMI4K2stik0_20Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_20Q1_vkl
TPVMI4K2stik0_21Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_21Q1_vkl
TPVMI4K2stik0_22Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_22Q1_vkl
TPVMI4K2stik0_23Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_23Q1_vkl
TPVMI4K2stikA3_11Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_11Q1_vkl
TPVMI4K2stikA3_12Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_12Q1_vkl
TPVMI4K2stikA3_13Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_13Q1_vkl
TPVMI4K2stikA3_14Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_14Q1_vkl
TPVMI4K2stikA3_15Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_15Q1_vkl
TPVMI4K2stikA3_1Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_1Q1_vkl
TPVMI4K2stikA3_2Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_2Q1_vkl
TPVMI4krmDA_daljinsko | DIGITAL | IOD_TPV | TPV:.MI4krmDA_daljinsko
TPVMI4motorA1_1Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4motorA1_1Q1_prip
TPVMI4motorA1_2Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4motorA1_2Q1_prip
TPVMI4motorA2_1Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4motorA2_1Q1_prip
TPVMI4motorA2_2Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4motorA2_2Q1_prip
TPVMI4motorA2_6Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4motorA2_6Q1_prip
TPVMI4mrez_nap_RGM_A1 | DIGITAL | IOD_TPV | TPV:.MI4mrez_nap_RGM_A1
TPVMI4mrez_nap_RGM_A2 | DIGITAL | IOD_TPV | TPV:.MI4mrez_nap_RGM_A2
TPVMI4mrezaA1_1Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4mrezaA1_1Q1_izklop
TPVMI4mrezaA1_1Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4mrezaA1_1Q1_vklop
TPVMI4mrezaA2_1Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4mrezaA2_1Q1_izklop
TPVMI4mrezaA2_1Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4mrezaA2_1Q1_vklop
TPVMI4napaka_alarm_DA1 | DIGITAL | IOD_TPV | TPV:.MI4napaka_alarm_DA1
TPVMI4napaka_alarm_DA2 | DIGITAL | IOD_TPV | TPV:.MI4napaka_alarm_DA2
TPVMI4prenap_zascA1_OK | DIGITAL | IOD_TPV | TPV:.MI4prenap_zascA1_OK
TPVMI4prenap_zascA2_OK | DIGITAL | IOD_TPV | TPV:.MI4prenap_zascA2_OK
TPVMI4rezerva_DA1 | DIGITAL | IOD_TPV | TPV:.MI4rezerva_DA1
TPVMI4rocni_izkA1_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_11Q1
TPVMI4rocni_izkA1_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_12Q1
TPVMI4rocni_izkA1_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_13Q1
TPVMI4rocni_izkA1_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_14Q1
TPVMI4rocni_izkA1_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_15Q1
TPVMI4rocni_izkA1_16Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_16Q1
TPVMI4rocni_izkA1_17Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_17Q1
TPVMI4rocni_izkA2_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA2_11Q1
TPVMI4rocni_izkA2_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA2_12Q1
TPVMI4rocni_izkA2_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA2_13Q1
TPVMI4rocni_izkA2_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA2_14Q1
TPVMI4sinhroniziranje_DA1 | DIGITAL | IOD_TPV | TPV:.MI4sinhroniziranje_DA1
TPVMI4sinhroniziranje_DA2 | DIGITAL | IOD_TPV | TPV:.MI4sinhroniziranje_DA2
TPVMI4splosna_napaka_DA1 | DIGITAL | IOD_TPV | TPV:.MI4splosna_napaka_DA1
TPVMI4splosna_napaka_DA2 | DIGITAL | IOD_TPV | TPV:.MI4splosna_napaka_DA2
TPVMI4stikA1_11Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_11Q1_vkl
TPVMI4stikA1_12Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_12Q1_vkl
TPVMI4stikA1_13Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_13Q1_vkl
TPVMI4stikA1_14Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_14Q1_vkl
TPVMI4stikA1_15Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_15Q1_vkl
TPVMI4stikA1_16Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_16Q1_vkl
TPVMI4stikA1_17Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_17Q1_vkl
TPVMI4stikA1_1Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_1Q1_vkl
TPVMI4stikA1_2Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_2Q1_vkl
TPVMI4stikA1_6Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_6Q1_vkl
TPVMI4stikA2_11Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_11Q1_vkl
TPVMI4stikA2_12Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_12Q1_vkl
TPVMI4stikA2_13Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_13Q1_vkl
TPVMI4stikA2_14Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_14Q1_vkl
TPVMI4stikA2_1Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_1Q1_vkl
TPVMI4stikA2_2Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_2Q1_vkl
TPVMI4vezno_6Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4vezno_6Q1_izklop
TPVMI4vezno_6Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4vezno_6Q1_vklop
TPVMI4vzporedno_del_nikoli | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_nikoli
TPVMI4vzporedno_del_nikoli_info | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_nikoli_info
TPVMI4vzporedno_del_po_potrebi | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_po_potrebi
TPVMI4vzporedno_del_po_potrebi_info | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_po_potrebi_info
TPVMI4vzporedno_del_vedno | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_vedno
TPVMI4vzporedno_del_vedno_info | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_vedno_info
TPVMI4zaganjanje_DA1 | DIGITAL | IOD_TPV | TPV:.MI4zaganjanje_DA1
TPVMI4zaganjanje_DA2 | DIGITAL | IOD_TPV | TPV:.MI4zaganjanje_DA2
TPVmrezaDA3motorni_pogon_okvara | DIGITAL | IOD_TPV | TPV:.mrezaDA3motorni_pogon_okvara
TPVmrezaDA3stikalo_okvara | DIGITAL | IOD_TPV | TPV:.mrezaDA3stikalo_okvara
TPVNapaka_v_kom_cirk_DA1 | DIGITAL | IOD_TPV | TPV:.Napaka_v_kom_cirk_DA1
TPVNapaka_v_kom_cirk_DA2 | DIGITAL | IOD_TPV | TPV:.Napaka_v_kom_cirk_DA2
TPVNapakaCOMModBus | DIGITAL | IOD_TPV | TPV:.NapakaCOMModBus
TPVNapakaVKomunikaciji_Circutor1 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor1
TPVNapakaVKomunikaciji_Circutor10 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor10
TPVNapakaVKomunikaciji_Circutor11 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor11
TPVNapakaVKomunikaciji_Circutor12 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor12
TPVNapakaVKomunikaciji_Circutor13 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor13
TPVNapakaVKomunikaciji_Circutor14 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor14
TPVNapakaVKomunikaciji_Circutor15 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor15
TPVNapakaVKomunikaciji_Circutor16 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor16
TPVNapakaVKomunikaciji_Circutor17 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor17
TPVNapakaVKomunikaciji_Circutor18 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor18
TPVNapakaVKomunikaciji_Circutor19 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor19
TPVNapakaVKomunikaciji_Circutor2 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor2
TPVNapakaVKomunikaciji_Circutor20 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor20
TPVNapakaVKomunikaciji_Circutor21 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor21
TPVNapakaVKomunikaciji_Circutor22 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor22
TPVNapakaVKomunikaciji_Circutor23 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor23
TPVNapakaVKomunikaciji_Circutor24 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor24
TPVNapakaVKomunikaciji_Circutor25 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor25
TPVNapakaVKomunikaciji_Circutor3 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor3
TPVNapakaVKomunikaciji_Circutor4 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor4
TPVNapakaVKomunikaciji_Circutor5 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor5
TPVNapakaVKomunikaciji_Circutor6 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor6
TPVNapakaVKomunikaciji_Circutor7 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor7
TPVNapakaVKomunikaciji_Circutor8 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor8
TPVNapakaVKomunikaciji_Circutor9 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor9
TPVNastaviDanMI | INT | IOD_TPV | TPV:.NastaviDanMI
TPVNastaviLetoMI | INT | IOD_TPV | TPV:.NastaviLetoMI
TPVNastaviMesecMI | INT | IOD_TPV | TPV:.NastaviMesecMI
TPVNastaviMinutaMI | INT | IOD_TPV | TPV:.NastaviMinutaMI
TPVNastaviSekundaMI | INT | IOD_TPV | TPV:.NastaviSekundaMI
TPVNastaviUraMI | INT | IOD_TPV | TPV:.NastaviUraMI
TPVOil_pressureA1 | UINT | IOD_TPV | TPV:.Oil_pressureA1
TPVOil_pressureA2 | UINT | IOD_TPV | TPV:.Oil_pressureA2
TPVRDASlabaBaterijaMI4 | DIGITAL | IOD_TPV | TPV:.RDASlabaBaterijaMI4
TPVSlabaBaterijaMI4 | DIGITAL | IOD_TPV | TPV:.SlabaBaterijaMI4
TPVSlabaBaterijaPLC1 | DIGITAL | IOD_TPV | TPV:.SlabaBaterijaPLC1
TPVSlabaBaterijaPLC2 | DIGITAL | IOD_TPV | TPV:.SlabaBaterijaPLC2
TPVStatus | INT | IOD_TPV | TPV:.Status
TPVstikaloDA3_okvara | DIGITAL | IOD_TPV | TPV:.stikaloDA3_okvara
TPVUI_MI4K2DA3_2Q1_izklop | DIGITAL | IOD_TPV | TPV:.UI_MI4K2DA3_2Q1_izklop
TPVUI_MI4K2DA3_2Q1_vklop | DIGITAL | IOD_TPV | TPV:.UI_MI4K2DA3_2Q1_vklop
TPVUI_MI4K2mrezaA3_1Q1_izklop | DIGITAL | IOD_TPV | TPV:.UI_MI4K2mrezaA3_1Q1_izklop
TPVUI_MI4K2mrezaA3_1Q1_vklop | DIGITAL | IOD_TPV | TPV:.UI_MI4K2mrezaA3_1Q1_vklop
IzpadTPV | INT | IOD_TPV | TPV:.st_izpad_komTPV
TPVsinh_cas | STRING | IOD_TPV | TPV:.cas_scada
TPVsinh_cas_nastavi | DIGITAL | IOD_TPV | TPV:.cas_nastavi
TPVCirc14NicelniTok_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ14NicelniTok
TPVCirc14Tok_L1_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ14Tok_L1
TPVCirc14Tok_L2_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ14Tok_L2
TPVCirc14Tok_L3_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ14Tok_L3
TPVCirc8NicelniTok_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ8NicelniTok
TPVCirc8Tok_L1_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ8Tok_L1
TPVCirc8Tok_L2_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ8Tok_L2
TPVCirc8Tok_L3_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ8Tok_L3
TPVCirc9NicelniTok_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ9NicelniTok
TPVCirc9Tok_L1_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ9Tok_L1
TPVCirc9Tok_L2_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ9Tok_L2
TPVCirc9Tok_L3_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ9Tok_L3
TPVCirc1MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ1MaximumDemandA2
TPVCirc1MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ1MaximumDemandA3
TPVCirc2MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ2MaximumDemandA2
TPVCirc2MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ2MaximumDemandA3
TPVCirc3MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ3MaximumDemandA2
TPVCirc3MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ3MaximumDemandA3
TPVCirc4MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ4MaximumDemandA2
TPVCirc4MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ4MaximumDemandA3
TPVCirc5MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ5MaximumDemandA2
TPVCirc5MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ5MaximumDemandA3
TPVCirc6MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ6MaximumDemandA2
TPVCirc6MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ6MaximumDemandA3
TPVCirc7MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ7MaximumDemandA2
TPVCirc7MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ7MaximumDemandA3
TPVCirc8MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ8MaximumDemandA2
TPVCirc8MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ8MaximumDemandA3
TPVCirc9MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ9MaximumDemandA2
TPVCirc9MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ9MaximumDemandA3
TPVCirc10MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ10MaximumDemandA2
TPVCirc10MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ10MaximumDemandA3
TPVCirc11MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ11MaximumDemandA2
TPVCirc11MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ11MaximumDemandA3
TPVCirc12MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ12MaximumDemandA2
TPVCirc12MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ12MaximumDemandA3
TPVCirc13MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ13MaximumDemandA2
TPVCirc13MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ13MaximumDemandA3
TPVCirc14MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ14MaximumDemandA2
TPVCirc14MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ14MaximumDemandA3
TPVCirc15MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ15MaximumDemandA2
TPVCirc15MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ15MaximumDemandA3
TPVCirc16MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ16MaximumDemandA2
TPVCirc16MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ16MaximumDemandA3
TPVCirc17MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ17MaximumDemandA2
TPVCirc17MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ17MaximumDemandA3
TPVCirc18MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ18MaximumDemandA2
TPVCirc18MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ18MaximumDemandA3
TPVCirc19MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ19MaximumDemandA2
TPVCirc19MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ19MaximumDemandA3
TPVCirc20MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ20MaximumDemandA2
TPVCirc20MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ20MaximumDemandA3
TPVCirc21MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ21MaximumDemandA2
TPVCirc21MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ21MaximumDemandA3
TPVCirc22MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ22MaximumDemandA2
TPVCirc22MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ22MaximumDemandA3
TPVCirc23MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ23MaximumDemandA2
TPVCirc23MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ23MaximumDemandA3
TPVCirc24MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ24MaximumDemandA2
TPVCirc24MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ24MaximumDemandA3
TPVCirc25MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ25MaximumDemandA2
TPVCirc25MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ25MaximumDemandA3
TPVCirc1RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[1].RazEner_D_SCADA
TPVCirc1RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[1].RazEner_T_SCADA
TPVCirc1RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[1].RazEner_M_SCADA
TPVCirc2RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[2].RazEner_D_SCADA
TPVCirc2RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[2].RazEner_T_SCADA
TPVCirc2RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[2].RazEner_M_SCADA
TPVCirc3RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[3].RazEner_D_SCADA
TPVCirc3RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[3].RazEner_T_SCADA
TPVCirc3RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[3].RazEner_M_SCADA
TPVCirc4RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[4].RazEner_D_SCADA
TPVCirc4RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[4].RazEner_T_SCADA
TPVCirc4RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[4].RazEner_M_SCADA
TPVCirc5RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[5].RazEner_D_SCADA
TPVCirc5RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[5].RazEner_T_SCADA
TPVCirc5RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[5].RazEner_M_SCADA
TPVCirc6RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[6].RazEner_D_SCADA
TPVCirc6RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[6].RazEner_T_SCADA
TPVCirc6RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[6].RazEner_M_SCADA
TPVCirc7RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[7].RazEner_D_SCADA
TPVCirc7RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[7].RazEner_T_SCADA
TPVCirc7RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[7].RazEner_M_SCADA
TPVCirc8RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[8].RazEner_D_SCADA
TPVCirc8RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[8].RazEner_T_SCADA
TPVCirc8RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[8].RazEner_M_SCADA
TPVCirc9RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[9].RazEner_D_SCADA
TPVCirc9RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[9].RazEner_T_SCADA
TPVCirc9RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[9].RazEner_M_SCADA
TPVCirc10RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[10].RazEner_D_SCADA
TPVCirc10RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[10].RazEner_T_SCADA
TPVCirc10RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[10].RazEner_M_SCADA
TPVCirc11RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[11].RazEner_D_SCADA
TPVCirc11RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[11].RazEner_T_SCADA
TPVCirc11RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[11].RazEner_M_SCADA
TPVCirc12RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[12].RazEner_D_SCADA
TPVCirc12RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[12].RazEner_T_SCADA
TPVCirc12RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[12].RazEner_M_SCADA
TPVCirc13RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[13].RazEner_D_SCADA
TPVCirc13RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[13].RazEner_T_SCADA
TPVCirc13RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[13].RazEner_M_SCADA
TPVCirc14RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[14].RazEner_D_SCADA
TPVCirc14RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[14].RazEner_T_SCADA
TPVCirc14RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[14].RazEner_M_SCADA
TPVCirc15RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[15].RazEner_D_SCADA
TPVCirc15RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[15].RazEner_T_SCADA
TPVCirc15RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[15].RazEner_M_SCADA
TPVCirc16RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[16].RazEner_D_SCADA
TPVCirc16RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[16].RazEner_T_SCADA
TPVCirc16RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[16].RazEner_M_SCADA
TPVCirc17RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[17].RazEner_D_SCADA
TPVCirc17RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[17].RazEner_T_SCADA
TPVCirc17RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[17].RazEner_M_SCADA
TPVCirc18RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[18].RazEner_D_SCADA
TPVCirc18RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[18].RazEner_T_SCADA
TPVCirc18RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[18].RazEner_M_SCADA
TPVCirc19RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[19].RazEner_D_SCADA
TPVCirc19RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[19].RazEner_T_SCADA
TPVCirc19RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[19].RazEner_M_SCADA
TPVCirc20RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[20].RazEner_D_SCADA
TPVCirc20RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[20].RazEner_T_SCADA
TPVCirc20RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[20].RazEner_M_SCADA
TPVCirc21RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[21].RazEner_D_SCADA
TPVCirc21RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[21].RazEner_T_SCADA
TPVCirc21RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[21].RazEner_M_SCADA
TPVCirc22RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[22].RazEner_D_SCADA
TPVCirc22RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[22].RazEner_T_SCADA
TPVCirc22RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[22].RazEner_M_SCADA
TPVCirc23RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[23].RazEner_D_SCADA
TPVCirc23RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[23].RazEner_T_SCADA
TPVCirc23RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[23].RazEner_M_SCADA
TPVCirc24RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[24].RazEner_D_SCADA
TPVCirc24RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[24].RazEner_T_SCADA
TPVCirc24RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[24].RazEner_M_SCADA
TPVCirc25RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[25].RazEner_D_SCADA
TPVCirc25RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[25].RazEner_T_SCADA
TPVCirc25RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[25].RazEner_M_SCADA
TPVCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Dnevne_energija_scada1
TPVCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Dnevne_energija_scada2
TPVCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Tedenska_energija_scada1
TPVCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Tedenska_energija_scada2
TPVCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Mesecna_energija_scada1
TPVCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Mesecna_energija_scada2

## variable_2
TPVDA3_rocno | DIGITAL | IOD_TPV | TPV:.DA3_rocno
TPVDA3motorni_pogon_okvara | DIGITAL | IOD_TPV | TPV:.DA3motorni_pogon_okvara
TPVIzpad_CAN_med_K1_K2 | DIGITAL | IOD_TPV | TPV:.Izpad_CAN_med_K1_K2
TPVMI4agr_nap_RGM_A1 | DIGITAL | IOD_TPV | TPV:.MI4agr_nap_RGM_A1
TPVMI4agr_nap_RGM_A2 | DIGITAL | IOD_TPV | TPV:.MI4agr_nap_RGM_A2
TPVMI4DA1_2Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4DA1_2Q1_izklop
TPVMI4DA1_2Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4DA1_2Q1_vklop
TPVMI4DA1_del | DIGITAL | IOD_TPV | TPV:.MI4DA1_del
TPVMI4DA1_prip | DIGITAL | IOD_TPV | TPV:.MI4DA1_prip
TPVMI4DA1_rezerva | DIGITAL | IOD_TPV | TPV:.MI4DA1_rezerva
TPVMI4DA1_sinh | DIGITAL | IOD_TPV | TPV:.MI4DA1_sinh
TPVMI4DA1_zagon | DIGITAL | IOD_TPV | TPV:.MI4DA1_zagon
TPVMI4DA2_2Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4DA2_2Q1_izklop
TPVMI4DA2_2Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4DA2_2Q1_vklop
TPVMI4DA2_del | DIGITAL | IOD_TPV | TPV:.MI4DA2_del
TPVMI4DA2_prip | DIGITAL | IOD_TPV | TPV:.MI4DA2_prip
TPVMI4DA2_rezerva | DIGITAL | IOD_TPV | TPV:.MI4DA2_rezerva
TPVMI4DA2_sinh | DIGITAL | IOD_TPV | TPV:.MI4DA2_sinh
TPVMI4DA2_zagon | DIGITAL | IOD_TPV | TPV:.MI4DA2_zagon
TPVMI4del_zascA1_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_11Q1
TPVMI4del_zascA1_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_12Q1
TPVMI4del_zascA1_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_13Q1
TPVMI4del_zascA1_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_14Q1
TPVMI4del_zascA1_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_15Q1
TPVMI4del_zascA1_16Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_16Q1
TPVMI4del_zascA1_17Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_17Q1
TPVMI4del_zascA1_2Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA1_2Q1
TPVMI4del_zascA2_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA2_11Q1
TPVMI4del_zascA2_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA2_12Q1
TPVMI4del_zascA2_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA2_13Q1
TPVMI4del_zascA2_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4del_zascA2_14Q1
TPVMI4K2agr_nap_RGM_A3 | DIGITAL | IOD_TPV | TPV:.MI4K2agr_nap_RGM_A3
TPVMI4K2DA3_2Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4K2DA3_2Q1_izklop
TPVMI4K2DA3_2Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4K2DA3_2Q1_vklop
TPVMI4K2del_zasc0_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_11Q1
TPVMI4K2del_zasc0_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_12Q1
TPVMI4K2del_zasc0_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_13Q1
TPVMI4K2del_zasc0_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_14Q1
TPVMI4K2del_zasc0_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_15Q1
TPVMI4K2del_zasc0_16Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_16Q1
TPVMI4K2del_zasc0_17Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_17Q1
TPVMI4K2del_zasc0_18Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_18Q1
TPVMI4K2del_zasc0_19Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_19Q1
TPVMI4K2del_zasc0_20Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_20Q1
TPVMI4K2del_zasc0_21Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_21Q1
TPVMI4K2del_zasc0_22Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_22Q1
TPVMI4K2del_zasc0_23Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zasc0_23Q1
TPVMI4K2del_zascA3_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zascA3_11Q1
TPVMI4K2del_zascA3_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zascA3_12Q1
TPVMI4K2del_zascA3_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zascA3_13Q1
TPVMI4K2del_zascA3_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zascA3_14Q1
TPVMI4K2del_zascA3_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2del_zascA3_15Q1
TPVMI4K2motorA3_1Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4K2motorA3_1Q1_prip
TPVMI4K2motorA3_2Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4K2motorA3_2Q1_prip
TPVMI4K2mrez_nap_RGM_A3 | DIGITAL | IOD_TPV | TPV:.MI4K2mrez_nap_RGM_A3
TPVMI4K2mrezaA3_1Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4K2mrezaA3_1Q1_izklop
TPVMI4K2mrezaA3_1Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4K2mrezaA3_1Q1_vklop
TPVMI4K2prenap_zasc0_OK | DIGITAL | IOD_TPV | TPV:.MI4K2prenap_zasc0_OK
TPVMI4K2prenap_zascA3_OK | DIGITAL | IOD_TPV | TPV:.MI4K2prenap_zascA3_OK
TPVMI4K2rocni_izk0_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_11Q1
TPVMI4K2rocni_izk0_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_12Q1
TPVMI4K2rocni_izk0_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_13Q1
TPVMI4K2rocni_izk0_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_14Q1
TPVMI4K2rocni_izk0_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_15Q1
TPVMI4K2rocni_izk0_16Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_16Q1
TPVMI4K2rocni_izk0_17Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_17Q1
TPVMI4K2rocni_izk0_18Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_18Q1
TPVMI4K2rocni_izk0_19Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_19Q1
TPVMI4K2rocni_izk0_20Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_20Q1
TPVMI4K2rocni_izk0_21Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_21Q1
TPVMI4K2rocni_izk0_22Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_22Q1
TPVMI4K2rocni_izk0_23Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izk0_23Q1
TPVMI4K2rocni_izkA3_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izkA3_11Q1
TPVMI4K2rocni_izkA3_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izkA3_12Q1
TPVMI4K2rocni_izkA3_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izkA3_13Q1
TPVMI4K2rocni_izkA3_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izkA3_14Q1
TPVMI4K2rocni_izkA3_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4K2rocni_izkA3_15Q1
TPVMI4K2stik0_11Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_11Q1_vkl
TPVMI4K2stik0_12Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_12Q1_vkl
TPVMI4K2stik0_13Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_13Q1_vkl
TPVMI4K2stik0_14Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_14Q1_vkl
TPVMI4K2stik0_15Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_15Q1_vkl
TPVMI4K2stik0_16Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_16Q1_vkl
TPVMI4K2stik0_17Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_17Q1_vkl
TPVMI4K2stik0_18Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_18Q1_vkl
TPVMI4K2stik0_19Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_19Q1_vkl
TPVMI4K2stik0_1Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_1Q1_vkl
TPVMI4K2stik0_20Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_20Q1_vkl
TPVMI4K2stik0_21Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_21Q1_vkl
TPVMI4K2stik0_22Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_22Q1_vkl
TPVMI4K2stik0_23Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stik0_23Q1_vkl
TPVMI4K2stikA3_11Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_11Q1_vkl
TPVMI4K2stikA3_12Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_12Q1_vkl
TPVMI4K2stikA3_13Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_13Q1_vkl
TPVMI4K2stikA3_14Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_14Q1_vkl
TPVMI4K2stikA3_15Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_15Q1_vkl
TPVMI4K2stikA3_1Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_1Q1_vkl
TPVMI4K2stikA3_2Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4K2stikA3_2Q1_vkl
TPVMI4krmDA_daljinsko | DIGITAL | IOD_TPV | TPV:.MI4krmDA_daljinsko
TPVMI4motorA1_1Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4motorA1_1Q1_prip
TPVMI4motorA1_2Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4motorA1_2Q1_prip
TPVMI4motorA2_1Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4motorA2_1Q1_prip
TPVMI4motorA2_2Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4motorA2_2Q1_prip
TPVMI4motorA2_6Q1_prip | DIGITAL | IOD_TPV | TPV:.MI4motorA2_6Q1_prip
TPVMI4mrez_nap_RGM_A1 | DIGITAL | IOD_TPV | TPV:.MI4mrez_nap_RGM_A1
TPVMI4mrez_nap_RGM_A2 | DIGITAL | IOD_TPV | TPV:.MI4mrez_nap_RGM_A2
TPVMI4mrezaA1_1Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4mrezaA1_1Q1_izklop
TPVMI4mrezaA1_1Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4mrezaA1_1Q1_vklop
TPVMI4mrezaA2_1Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4mrezaA2_1Q1_izklop
TPVMI4mrezaA2_1Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4mrezaA2_1Q1_vklop
TPVMI4napaka_alarm_DA1 | DIGITAL | IOD_TPV | TPV:.MI4napaka_alarm_DA1
TPVMI4napaka_alarm_DA2 | DIGITAL | IOD_TPV | TPV:.MI4napaka_alarm_DA2
TPVMI4prenap_zascA1_OK | DIGITAL | IOD_TPV | TPV:.MI4prenap_zascA1_OK
TPVMI4prenap_zascA2_OK | DIGITAL | IOD_TPV | TPV:.MI4prenap_zascA2_OK
TPVMI4rezerva_DA1 | DIGITAL | IOD_TPV | TPV:.MI4rezerva_DA1
TPVMI4rocni_izkA1_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_11Q1
TPVMI4rocni_izkA1_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_12Q1
TPVMI4rocni_izkA1_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_13Q1
TPVMI4rocni_izkA1_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_14Q1
TPVMI4rocni_izkA1_15Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_15Q1
TPVMI4rocni_izkA1_16Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_16Q1
TPVMI4rocni_izkA1_17Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA1_17Q1
TPVMI4rocni_izkA2_11Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA2_11Q1
TPVMI4rocni_izkA2_12Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA2_12Q1
TPVMI4rocni_izkA2_13Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA2_13Q1
TPVMI4rocni_izkA2_14Q1 | DIGITAL | IOD_TPV | TPV:.MI4rocni_izkA2_14Q1
TPVMI4sinhroniziranje_DA1 | DIGITAL | IOD_TPV | TPV:.MI4sinhroniziranje_DA1
TPVMI4sinhroniziranje_DA2 | DIGITAL | IOD_TPV | TPV:.MI4sinhroniziranje_DA2
TPVMI4splosna_napaka_DA1 | DIGITAL | IOD_TPV | TPV:.MI4splosna_napaka_DA1
TPVMI4splosna_napaka_DA2 | DIGITAL | IOD_TPV | TPV:.MI4splosna_napaka_DA2
TPVMI4stikA1_11Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_11Q1_vkl
TPVMI4stikA1_12Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_12Q1_vkl
TPVMI4stikA1_13Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_13Q1_vkl
TPVMI4stikA1_14Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_14Q1_vkl
TPVMI4stikA1_15Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_15Q1_vkl
TPVMI4stikA1_16Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_16Q1_vkl
TPVMI4stikA1_17Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_17Q1_vkl
TPVMI4stikA1_1Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_1Q1_vkl
TPVMI4stikA1_2Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_2Q1_vkl
TPVMI4stikA1_6Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA1_6Q1_vkl
TPVMI4stikA2_11Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_11Q1_vkl
TPVMI4stikA2_12Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_12Q1_vkl
TPVMI4stikA2_13Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_13Q1_vkl
TPVMI4stikA2_14Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_14Q1_vkl
TPVMI4stikA2_1Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_1Q1_vkl
TPVMI4stikA2_2Q1_vkl | DIGITAL | IOD_TPV | TPV:.MI4stikA2_2Q1_vkl
TPVMI4vezno_6Q1_izklop | DIGITAL | IOD_TPV | TPV:.MI4vezno_6Q1_izklop
TPVMI4vezno_6Q1_vklop | DIGITAL | IOD_TPV | TPV:.MI4vezno_6Q1_vklop
TPVMI4vzporedno_del_nikoli | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_nikoli
TPVMI4vzporedno_del_nikoli_info | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_nikoli_info
TPVMI4vzporedno_del_po_potrebi | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_po_potrebi
TPVMI4vzporedno_del_po_potrebi_info | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_po_potrebi_info
TPVMI4vzporedno_del_vedno | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_vedno
TPVMI4vzporedno_del_vedno_info | DIGITAL | IOD_TPV | TPV:.MI4vzporedno_del_vedno_info
TPVMI4zaganjanje_DA1 | DIGITAL | IOD_TPV | TPV:.MI4zaganjanje_DA1
TPVMI4zaganjanje_DA2 | DIGITAL | IOD_TPV | TPV:.MI4zaganjanje_DA2
TPVmrezaDA3motorni_pogon_okvara | DIGITAL | IOD_TPV | TPV:.mrezaDA3motorni_pogon_okvara
TPVmrezaDA3stikalo_okvara | DIGITAL | IOD_TPV | TPV:.mrezaDA3stikalo_okvara
TPVNapaka_v_kom_cirk_DA1 | DIGITAL | IOD_TPV | TPV:.Napaka_v_kom_cirk_DA1
TPVNapaka_v_kom_cirk_DA2 | DIGITAL | IOD_TPV | TPV:.Napaka_v_kom_cirk_DA2
TPVNapakaCOMModBus | DIGITAL | IOD_TPV | TPV:.NapakaCOMModBus
TPVNapakaVKomunikaciji_Circutor1 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor1
TPVNapakaVKomunikaciji_Circutor10 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor10
TPVNapakaVKomunikaciji_Circutor11 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor11
TPVNapakaVKomunikaciji_Circutor12 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor12
TPVNapakaVKomunikaciji_Circutor13 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor13
TPVNapakaVKomunikaciji_Circutor14 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor14
TPVNapakaVKomunikaciji_Circutor15 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor15
TPVNapakaVKomunikaciji_Circutor16 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor16
TPVNapakaVKomunikaciji_Circutor17 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor17
TPVNapakaVKomunikaciji_Circutor18 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor18
TPVNapakaVKomunikaciji_Circutor19 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor19
TPVNapakaVKomunikaciji_Circutor2 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor2
TPVNapakaVKomunikaciji_Circutor20 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor20
TPVNapakaVKomunikaciji_Circutor21 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor21
TPVNapakaVKomunikaciji_Circutor22 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor22
TPVNapakaVKomunikaciji_Circutor23 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor23
TPVNapakaVKomunikaciji_Circutor24 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor24
TPVNapakaVKomunikaciji_Circutor25 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor25
TPVNapakaVKomunikaciji_Circutor3 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor3
TPVNapakaVKomunikaciji_Circutor4 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor4
TPVNapakaVKomunikaciji_Circutor5 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor5
TPVNapakaVKomunikaciji_Circutor6 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor6
TPVNapakaVKomunikaciji_Circutor7 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor7
TPVNapakaVKomunikaciji_Circutor8 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor8
TPVNapakaVKomunikaciji_Circutor9 | DIGITAL | IOD_TPV | TPV:.NapakaVKomunikaciji_Circutor9
TPVRDASlabaBaterijaMI4 | DIGITAL | IOD_TPV | TPV:.RDASlabaBaterijaMI4
TPVSlabaBaterijaMI4 | DIGITAL | IOD_TPV | TPV:.SlabaBaterijaMI4
TPVSlabaBaterijaPLC1 | DIGITAL | IOD_TPV | TPV:.SlabaBaterijaPLC1
TPVSlabaBaterijaPLC2 | DIGITAL | IOD_TPV | TPV:.SlabaBaterijaPLC2
TPVstikaloDA3_okvara | DIGITAL | IOD_TPV | TPV:.stikaloDA3_okvara
TPVUI_MI4K2DA3_2Q1_izklop | DIGITAL | IOD_TPV | TPV:.UI_MI4K2DA3_2Q1_izklop
TPVUI_MI4K2DA3_2Q1_vklop | DIGITAL | IOD_TPV | TPV:.UI_MI4K2DA3_2Q1_vklop
TPVUI_MI4K2mrezaA3_1Q1_izklop | DIGITAL | IOD_TPV | TPV:.UI_MI4K2mrezaA3_1Q1_izklop
TPVUI_MI4K2mrezaA3_1Q1_vklop | DIGITAL | IOD_TPV | TPV:.UI_MI4K2mrezaA3_1Q1_vklop
TPVsinh_cas_nastavi | DIGITAL | IOD_TPV | TPV:.cas_nastavi
TPVCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Dnevne_energija_scada1
TPVCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Dnevne_energija_scada2
TPVCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Tedenska_energija_scada1
TPVCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Tedenska_energija_scada2
TPVCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Mesecna_energija_scada1
TPVCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_TPV | TPV:.Circ_Vpis_Mesecna_energija_scada2
TPVCoolant_temperatureA1 | INT | IOD_TPV | TPV:.Coolant_temperatureA1
TPVCoolant_temperatureA2 | INT | IOD_TPV | TPV:.Coolant_temperatureA2
TPVdelovna_energ_trenutno | INT | IOD_TPV | TPV:.delovna_energ_trenutno
TPVdelovna_energija_prej | INT | IOD_TPV | TPV:.delovna_energija_prej
TPV_Generator_current_lag_leadA1 | INT | IOD_TPV | TPV:.Generator_current_lag_leadA1
TPV_Generator_current_lag_leadA2 | INT | IOD_TPV | TPV:.Generator_current_lag_leadA2
TPVjalova_energ_trenutno | INT | IOD_TPV | TPV:.jalova_energ_trenutno
TPVjalova_energija_prej | INT | IOD_TPV | TPV:.jalova_energija_prej
TPVKomanda | INT | IOD_TPV | TPV:.Komanda
TPVNastaviDanMI | INT | IOD_TPV | TPV:.NastaviDanMI
TPVNastaviLetoMI | INT | IOD_TPV | TPV:.NastaviLetoMI
TPVNastaviMesecMI | INT | IOD_TPV | TPV:.NastaviMesecMI
TPVNastaviMinutaMI | INT | IOD_TPV | TPV:.NastaviMinutaMI
TPVNastaviSekundaMI | INT | IOD_TPV | TPV:.NastaviSekundaMI
TPVNastaviUraMI | INT | IOD_TPV | TPV:.NastaviUraMI
TPVStatus | INT | IOD_TPV | TPV:.Status
IzpadTPV | INT | IOD_TPV | TPV:.st_izpad_komTPV
TPVCirc10CosFi_III | LONG | IOD_TPV | TPV:.Circ10CosFi_III
TPVCirc10DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ10DelovnaEnergija
TPVCirc10DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ10DelovnaMoc_III
TPVCirc10DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ10DelovnaMoc_L1
TPVCirc10DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ10DelovnaMoc_L2
TPVCirc10DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ10DelovnaMoc_L3
TPVCirc10Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ10Frekvenca_L1
TPVCirc10InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ10InduktivnaEnergija
TPVCirc10InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ10InduktivnaMoc_III
TPVCirc10JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ10JalovaMoc_L1
TPVCirc10JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ10JalovaMoc_L2
TPVCirc10JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ10JalovaMoc_L3
TPVCirc10KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ10KapacitivnaEnergija
TPVCirc10KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ10KapacitivnaMoc_III
TPVCirc10MaximumDemand | LONG | IOD_TPV | TPV:.Circ10MaximumDemand
TPVCirc10Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ10Napetost_L1_L2
TPVCirc10Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ10Napetost_L1_N
TPVCirc10Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ10Napetost_L2_L3
TPVCirc10Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ10Napetost_L2_N
TPVCirc10Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ10Napetost_L3_L1
TPVCirc10Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ10Napetost_L3_N
TPVCirc10NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ10NavideznaMoc_III
TPVCirc10NicelniTok | LONG | IOD_TPV | TPV:.Circ10NicelniTok
TPVCirc10PowerFactor_III | LONG | IOD_TPV | TPV:.Circ10PowerFactor_III
TPVCirc10PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ10PowerFactor_L1
TPVCirc10PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ10PowerFactor_L2
TPVCirc10PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ10PowerFactor_L3
TPVCirc10THDI_L1 | LONG | IOD_TPV | TPV:.Circ10THDI_L1
TPVCirc10THDI_L2 | LONG | IOD_TPV | TPV:.Circ10THDI_L2
TPVCirc10THDI_L3 | LONG | IOD_TPV | TPV:.Circ10THDI_L3
TPVCirc10THDV_L1 | LONG | IOD_TPV | TPV:.Circ10THDV_L1
TPVCirc10THDV_L2 | LONG | IOD_TPV | TPV:.Circ10THDV_L2
TPVCirc10THDV_L3 | LONG | IOD_TPV | TPV:.Circ10THDV_L3
TPVCirc10Tok_L1 | LONG | IOD_TPV | TPV:.Circ10Tok_L1
TPVCirc10Tok_L2 | LONG | IOD_TPV | TPV:.Circ10Tok_L2
TPVCirc10Tok_L3 | LONG | IOD_TPV | TPV:.Circ10Tok_L3
TPVCirc10TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ10TokPovprecje_III
TPVCirc11CosFi_III | LONG | IOD_TPV | TPV:.Circ11CosFi_III
TPVCirc11DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ11DelovnaEnergija
TPVCirc11DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ11DelovnaMoc_III
TPVCirc11DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ11DelovnaMoc_L1
TPVCirc11DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ11DelovnaMoc_L2
TPVCirc11DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ11DelovnaMoc_L3
TPVCirc11Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ11Frekvenca_L1
TPVCirc11InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ11InduktivnaEnergija
TPVCirc11InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ11InduktivnaMoc_III
TPVCirc11JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ11JalovaMoc_L1
TPVCirc11JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ11JalovaMoc_L2
TPVCirc11JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ11JalovaMoc_L3
TPVCirc11KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ11KapacitivnaEnergija
TPVCirc11KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ11KapacitivnaMoc_III
TPVCirc11MaximumDemand | LONG | IOD_TPV | TPV:.Circ11MaximumDemand
TPVCirc11Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ11Napetost_L1_L2
TPVCirc11Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ11Napetost_L1_N
TPVCirc11Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ11Napetost_L2_L3
TPVCirc11Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ11Napetost_L2_N
TPVCirc11Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ11Napetost_L3_L1
TPVCirc11Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ11Napetost_L3_N
TPVCirc11NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ11NavideznaMoc_III
TPVCirc11NicelniTok | LONG | IOD_TPV | TPV:.Circ11NicelniTok
TPVCirc11PowerFactor_III | LONG | IOD_TPV | TPV:.Circ11PowerFactor_III
TPVCirc11PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ11PowerFactor_L1
TPVCirc11PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ11PowerFactor_L2
TPVCirc11PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ11PowerFactor_L3
TPVCirc11THDI_L1 | LONG | IOD_TPV | TPV:.Circ11THDI_L1
TPVCirc11THDI_L2 | LONG | IOD_TPV | TPV:.Circ11THDI_L2
TPVCirc11THDI_L3 | LONG | IOD_TPV | TPV:.Circ11THDI_L3
TPVCirc11THDV_L1 | LONG | IOD_TPV | TPV:.Circ11THDV_L1
TPVCirc11THDV_L2 | LONG | IOD_TPV | TPV:.Circ11THDV_L2
TPVCirc11THDV_L3 | LONG | IOD_TPV | TPV:.Circ11THDV_L3
TPVCirc11Tok_L1 | LONG | IOD_TPV | TPV:.Circ11Tok_L1
TPVCirc11Tok_L2 | LONG | IOD_TPV | TPV:.Circ11Tok_L2
TPVCirc11Tok_L3 | LONG | IOD_TPV | TPV:.Circ11Tok_L3
TPVCirc11TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ11TokPovprecje_III
TPVCirc12CosFi_III | LONG | IOD_TPV | TPV:.Circ12CosFi_III
TPVCirc12DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ12DelovnaEnergija
TPVCirc12DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ12DelovnaMoc_III
TPVCirc12DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ12DelovnaMoc_L1
TPVCirc12DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ12DelovnaMoc_L2
TPVCirc12DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ12DelovnaMoc_L3
TPVCirc12Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ12Frekvenca_L1
TPVCirc12InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ12InduktivnaEnergija
TPVCirc12InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ12InduktivnaMoc_III
TPVCirc12JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ12JalovaMoc_L1
TPVCirc12JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ12JalovaMoc_L2
TPVCirc12JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ12JalovaMoc_L3
TPVCirc12KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ12KapacitivnaEnergija
TPVCirc12KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ12KapacitivnaMoc_III
TPVCirc12MaximumDemand | LONG | IOD_TPV | TPV:.Circ12MaximumDemand
TPVCirc12Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ12Napetost_L1_L2
TPVCirc12Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ12Napetost_L1_N
TPVCirc12Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ12Napetost_L2_L3
TPVCirc12Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ12Napetost_L2_N
TPVCirc12Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ12Napetost_L3_L1
TPVCirc12Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ12Napetost_L3_N
TPVCirc12NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ12NavideznaMoc_III
TPVCirc12NicelniTok | LONG | IOD_TPV | TPV:.Circ12NicelniTok
TPVCirc12PowerFactor_III | LONG | IOD_TPV | TPV:.Circ12PowerFactor_III
TPVCirc12PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ12PowerFactor_L1
TPVCirc12PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ12PowerFactor_L2
TPVCirc12PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ12PowerFactor_L3
TPVCirc12THDI_L1 | LONG | IOD_TPV | TPV:.Circ12THDI_L1
TPVCirc12THDI_L2 | LONG | IOD_TPV | TPV:.Circ12THDI_L2
TPVCirc12THDI_L3 | LONG | IOD_TPV | TPV:.Circ12THDI_L3
TPVCirc12THDV_L1 | LONG | IOD_TPV | TPV:.Circ12THDV_L1
TPVCirc12THDV_L2 | LONG | IOD_TPV | TPV:.Circ12THDV_L2
TPVCirc12THDV_L3 | LONG | IOD_TPV | TPV:.Circ12THDV_L3
TPVCirc12Tok_L1 | LONG | IOD_TPV | TPV:.Circ12Tok_L1
TPVCirc12Tok_L2 | LONG | IOD_TPV | TPV:.Circ12Tok_L2
TPVCirc12Tok_L3 | LONG | IOD_TPV | TPV:.Circ12Tok_L3
TPVCirc12TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ12TokPovprecje_III
TPVCirc13CosFi_III | LONG | IOD_TPV | TPV:.Circ13CosFi_III
TPVCirc13DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ13DelovnaEnergija
TPVCirc13DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ13DelovnaMoc_III
TPVCirc13DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ13DelovnaMoc_L1
TPVCirc13DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ13DelovnaMoc_L2
TPVCirc13DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ13DelovnaMoc_L3
TPVCirc13Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ13Frekvenca_L1
TPVCirc13InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ13InduktivnaEnergija
TPVCirc13InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ13InduktivnaMoc_III
TPVCirc13JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ13JalovaMoc_L1
TPVCirc13JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ13JalovaMoc_L2
TPVCirc13JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ13JalovaMoc_L3
TPVCirc13KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ13KapacitivnaEnergija
TPVCirc13KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ13KapacitivnaMoc_III
TPVCirc13MaximumDemand | LONG | IOD_TPV | TPV:.Circ13MaximumDemand
TPVCirc13Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ13Napetost_L1_L2
TPVCirc13Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ13Napetost_L1_N
TPVCirc13Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ13Napetost_L2_L3
TPVCirc13Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ13Napetost_L2_N
TPVCirc13Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ13Napetost_L3_L1
TPVCirc13Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ13Napetost_L3_N
TPVCirc13NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ13NavideznaMoc_III
TPVCirc13NicelniTok | LONG | IOD_TPV | TPV:.Circ13NicelniTok
TPVCirc13PowerFactor_III | LONG | IOD_TPV | TPV:.Circ13PowerFactor_III
TPVCirc13PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ13PowerFactor_L1
TPVCirc13PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ13PowerFactor_L2
TPVCirc13PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ13PowerFactor_L3
TPVCirc13THDI_L1 | LONG | IOD_TPV | TPV:.Circ13THDI_L1
TPVCirc13THDI_L2 | LONG | IOD_TPV | TPV:.Circ13THDI_L2
TPVCirc13THDI_L3 | LONG | IOD_TPV | TPV:.Circ13THDI_L3
TPVCirc13THDV_L1 | LONG | IOD_TPV | TPV:.Circ13THDV_L1
TPVCirc13THDV_L2 | LONG | IOD_TPV | TPV:.Circ13THDV_L2
TPVCirc13THDV_L3 | LONG | IOD_TPV | TPV:.Circ13THDV_L3
TPVCirc13Tok_L1 | LONG | IOD_TPV | TPV:.Circ13Tok_L1
TPVCirc13Tok_L2 | LONG | IOD_TPV | TPV:.Circ13Tok_L2
TPVCirc13Tok_L3 | LONG | IOD_TPV | TPV:.Circ13Tok_L3
TPVCirc13TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ13TokPovprecje_III
TPVCirc14CosFi_III | LONG | IOD_TPV | TPV:.Circ14CosFi_III
TPVCirc14DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ14DelovnaEnergija
TPVCirc14DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ14DelovnaMoc_III
TPVCirc14DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ14DelovnaMoc_L1
TPVCirc14DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ14DelovnaMoc_L2
TPVCirc14DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ14DelovnaMoc_L3
TPVCirc14Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ14Frekvenca_L1
TPVCirc14InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ14InduktivnaEnergija
TPVCirc14InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ14InduktivnaMoc_III
TPVCirc14JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ14JalovaMoc_L1
TPVCirc14JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ14JalovaMoc_L2
TPVCirc14JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ14JalovaMoc_L3
TPVCirc14KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ14KapacitivnaEnergija
TPVCirc14KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ14KapacitivnaMoc_III
TPVCirc14MaximumDemand | LONG | IOD_TPV | TPV:.Circ14MaximumDemand
TPVCirc14Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ14Napetost_L1_L2
TPVCirc14Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ14Napetost_L1_N
TPVCirc14Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ14Napetost_L2_L3
TPVCirc14Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ14Napetost_L2_N
TPVCirc14Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ14Napetost_L3_L1
TPVCirc14Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ14Napetost_L3_N
TPVCirc14NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ14NavideznaMoc_III
TPVCirc14NicelniTok | LONG | IOD_TPV | TPV:.Circ14NicelniTok
TPVCirc14PowerFactor_III | LONG | IOD_TPV | TPV:.Circ14PowerFactor_III
TPVCirc14PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ14PowerFactor_L1
TPVCirc14PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ14PowerFactor_L2
TPVCirc14PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ14PowerFactor_L3
TPVCirc14THDI_L1 | LONG | IOD_TPV | TPV:.Circ14THDI_L1
TPVCirc14THDI_L2 | LONG | IOD_TPV | TPV:.Circ14THDI_L2
TPVCirc14THDI_L3 | LONG | IOD_TPV | TPV:.Circ14THDI_L3
TPVCirc14THDV_L1 | LONG | IOD_TPV | TPV:.Circ14THDV_L1
TPVCirc14THDV_L2 | LONG | IOD_TPV | TPV:.Circ14THDV_L2
TPVCirc14THDV_L3 | LONG | IOD_TPV | TPV:.Circ14THDV_L3
TPVCirc14Tok_L1 | LONG | IOD_TPV | TPV:.Circ14Tok_L1
TPVCirc14Tok_L2 | LONG | IOD_TPV | TPV:.Circ14Tok_L2
TPVCirc14Tok_L3 | LONG | IOD_TPV | TPV:.Circ14Tok_L3
TPVCirc14TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ14TokPovprecje_III
TPVCirc15CosFi_III | LONG | IOD_TPV | TPV:.Circ15CosFi_III
TPVCirc15DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ15DelovnaEnergija
TPVCirc15DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ15DelovnaMoc_III
TPVCirc15DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ15DelovnaMoc_L1
TPVCirc15DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ15DelovnaMoc_L2
TPVCirc15DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ15DelovnaMoc_L3
TPVCirc15Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ15Frekvenca_L1
TPVCirc15InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ15InduktivnaEnergija
TPVCirc15InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ15InduktivnaMoc_III
TPVCirc15JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ15JalovaMoc_L1
TPVCirc15JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ15JalovaMoc_L2
TPVCirc15JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ15JalovaMoc_L3
TPVCirc15KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ15KapacitivnaEnergija
TPVCirc15KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ15KapacitivnaMoc_III
TPVCirc15MaximumDemand | LONG | IOD_TPV | TPV:.Circ15MaximumDemand
TPVCirc15Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ15Napetost_L1_L2
TPVCirc15Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ15Napetost_L1_N
TPVCirc15Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ15Napetost_L2_L3
TPVCirc15Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ15Napetost_L2_N
TPVCirc15Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ15Napetost_L3_L1
TPVCirc15Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ15Napetost_L3_N
TPVCirc15NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ15NavideznaMoc_III
TPVCirc15NicelniTok | LONG | IOD_TPV | TPV:.Circ15NicelniTok
TPVCirc15PowerFactor_III | LONG | IOD_TPV | TPV:.Circ15PowerFactor_III
TPVCirc15PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ15PowerFactor_L1
TPVCirc15PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ15PowerFactor_L2
TPVCirc15PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ15PowerFactor_L3
TPVCirc15THDI_L1 | LONG | IOD_TPV | TPV:.Circ15THDI_L1
TPVCirc15THDI_L2 | LONG | IOD_TPV | TPV:.Circ15THDI_L2
TPVCirc15THDI_L3 | LONG | IOD_TPV | TPV:.Circ15THDI_L3
TPVCirc15THDV_L1 | LONG | IOD_TPV | TPV:.Circ15THDV_L1
TPVCirc15THDV_L2 | LONG | IOD_TPV | TPV:.Circ15THDV_L2
TPVCirc15THDV_L3 | LONG | IOD_TPV | TPV:.Circ15THDV_L3
TPVCirc15Tok_L1 | LONG | IOD_TPV | TPV:.Circ15Tok_L1
TPVCirc15Tok_L2 | LONG | IOD_TPV | TPV:.Circ15Tok_L2
TPVCirc15Tok_L3 | LONG | IOD_TPV | TPV:.Circ15Tok_L3
TPVCirc15TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ15TokPovprecje_III
TPVCirc16CosFi_III | LONG | IOD_TPV | TPV:.Circ16CosFi_III
TPVCirc16DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ16DelovnaEnergija
TPVCirc16DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ16DelovnaMoc_III
TPVCirc16DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ16DelovnaMoc_L1
TPVCirc16DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ16DelovnaMoc_L2
TPVCirc16DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ16DelovnaMoc_L3
TPVCirc16Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ16Frekvenca_L1
TPVCirc16InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ16InduktivnaEnergija
TPVCirc16InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ16InduktivnaMoc_III
TPVCirc16JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ16JalovaMoc_L1
TPVCirc16JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ16JalovaMoc_L2
TPVCirc16JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ16JalovaMoc_L3
TPVCirc16KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ16KapacitivnaEnergija
TPVCirc16KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ16KapacitivnaMoc_III
TPVCirc16MaximumDemand | LONG | IOD_TPV | TPV:.Circ16MaximumDemand
TPVCirc16Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ16Napetost_L1_L2
TPVCirc16Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ16Napetost_L1_N
TPVCirc16Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ16Napetost_L2_L3
TPVCirc16Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ16Napetost_L2_N
TPVCirc16Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ16Napetost_L3_L1
TPVCirc16Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ16Napetost_L3_N
TPVCirc16NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ16NavideznaMoc_III
TPVCirc16NicelniTok | LONG | IOD_TPV | TPV:.Circ16NicelniTok
TPVCirc16PowerFactor_III | LONG | IOD_TPV | TPV:.Circ16PowerFactor_III
TPVCirc16PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ16PowerFactor_L1
TPVCirc16PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ16PowerFactor_L2
TPVCirc16PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ16PowerFactor_L3
TPVCirc16THDI_L1 | LONG | IOD_TPV | TPV:.Circ16THDI_L1
TPVCirc16THDI_L2 | LONG | IOD_TPV | TPV:.Circ16THDI_L2
TPVCirc16THDI_L3 | LONG | IOD_TPV | TPV:.Circ16THDI_L3
TPVCirc16THDV_L1 | LONG | IOD_TPV | TPV:.Circ16THDV_L1
TPVCirc16THDV_L2 | LONG | IOD_TPV | TPV:.Circ16THDV_L2
TPVCirc16THDV_L3 | LONG | IOD_TPV | TPV:.Circ16THDV_L3
TPVCirc16Tok_L1 | LONG | IOD_TPV | TPV:.Circ16Tok_L1
TPVCirc16Tok_L2 | LONG | IOD_TPV | TPV:.Circ16Tok_L2
TPVCirc16Tok_L3 | LONG | IOD_TPV | TPV:.Circ16Tok_L3
TPVCirc16TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ16TokPovprecje_III
TPVCirc17CosFi_III | LONG | IOD_TPV | TPV:.Circ17CosFi_III
TPVCirc17DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ17DelovnaEnergija
TPVCirc17DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ17DelovnaMoc_III
TPVCirc17DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ17DelovnaMoc_L1
TPVCirc17DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ17DelovnaMoc_L2
TPVCirc17DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ17DelovnaMoc_L3
TPVCirc17Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ17Frekvenca_L1
TPVCirc17InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ17InduktivnaEnergija
TPVCirc17InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ17InduktivnaMoc_III
TPVCirc17JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ17JalovaMoc_L1
TPVCirc17JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ17JalovaMoc_L2
TPVCirc17JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ17JalovaMoc_L3
TPVCirc17KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ17KapacitivnaEnergija
TPVCirc17KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ17KapacitivnaMoc_III
TPVCirc17MaximumDemand | LONG | IOD_TPV | TPV:.Circ17MaximumDemand
TPVCirc17Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ17Napetost_L1_L2
TPVCirc17Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ17Napetost_L1_N
TPVCirc17Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ17Napetost_L2_L3
TPVCirc17Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ17Napetost_L2_N
TPVCirc17Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ17Napetost_L3_L1
TPVCirc17Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ17Napetost_L3_N
TPVCirc17NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ17NavideznaMoc_III
TPVCirc17NicelniTok | LONG | IOD_TPV | TPV:.Circ17NicelniTok
TPVCirc17PowerFactor_III | LONG | IOD_TPV | TPV:.Circ17PowerFactor_III
TPVCirc17PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ17PowerFactor_L1
TPVCirc17PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ17PowerFactor_L2
TPVCirc17PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ17PowerFactor_L3
TPVCirc17THDI_L1 | LONG | IOD_TPV | TPV:.Circ17THDI_L1
TPVCirc17THDI_L2 | LONG | IOD_TPV | TPV:.Circ17THDI_L2
TPVCirc17THDI_L3 | LONG | IOD_TPV | TPV:.Circ17THDI_L3
TPVCirc17THDV_L1 | LONG | IOD_TPV | TPV:.Circ17THDV_L1
TPVCirc17THDV_L2 | LONG | IOD_TPV | TPV:.Circ17THDV_L2
TPVCirc17THDV_L3 | LONG | IOD_TPV | TPV:.Circ17THDV_L3
TPVCirc17Tok_L1 | LONG | IOD_TPV | TPV:.Circ17Tok_L1
TPVCirc17Tok_L2 | LONG | IOD_TPV | TPV:.Circ17Tok_L2
TPVCirc17Tok_L3 | LONG | IOD_TPV | TPV:.Circ17Tok_L3
TPVCirc17TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ17TokPovprecje_III
TPVCirc18CosFi_III | LONG | IOD_TPV | TPV:.Circ18CosFi_III
TPVCirc18DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ18DelovnaEnergija
TPVCirc18DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ18DelovnaMoc_III
TPVCirc18DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ18DelovnaMoc_L1
TPVCirc18DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ18DelovnaMoc_L2
TPVCirc18DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ18DelovnaMoc_L3
TPVCirc18Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ18Frekvenca_L1
TPVCirc18InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ18InduktivnaEnergija
TPVCirc18InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ18InduktivnaMoc_III
TPVCirc18JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ18JalovaMoc_L1
TPVCirc18JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ18JalovaMoc_L2
TPVCirc18JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ18JalovaMoc_L3
TPVCirc18KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ18KapacitivnaEnergija
TPVCirc18KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ18KapacitivnaMoc_III
TPVCirc18MaximumDemand | LONG | IOD_TPV | TPV:.Circ18MaximumDemand
TPVCirc18Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ18Napetost_L1_L2
TPVCirc18Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ18Napetost_L1_N
TPVCirc18Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ18Napetost_L2_L3
TPVCirc18Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ18Napetost_L2_N
TPVCirc18Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ18Napetost_L3_L1
TPVCirc18Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ18Napetost_L3_N
TPVCirc18NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ18NavideznaMoc_III
TPVCirc18NicelniTok | LONG | IOD_TPV | TPV:.Circ18NicelniTok
TPVCirc18PowerFactor_III | LONG | IOD_TPV | TPV:.Circ18PowerFactor_III
TPVCirc18PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ18PowerFactor_L1
TPVCirc18PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ18PowerFactor_L2
TPVCirc18PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ18PowerFactor_L3
TPVCirc18THDI_L1 | LONG | IOD_TPV | TPV:.Circ18THDI_L1
TPVCirc18THDI_L2 | LONG | IOD_TPV | TPV:.Circ18THDI_L2
TPVCirc18THDI_L3 | LONG | IOD_TPV | TPV:.Circ18THDI_L3
TPVCirc18THDV_L1 | LONG | IOD_TPV | TPV:.Circ18THDV_L1
TPVCirc18THDV_L2 | LONG | IOD_TPV | TPV:.Circ18THDV_L2
TPVCirc18THDV_L3 | LONG | IOD_TPV | TPV:.Circ18THDV_L3
TPVCirc18Tok_L1 | LONG | IOD_TPV | TPV:.Circ18Tok_L1
TPVCirc18Tok_L2 | LONG | IOD_TPV | TPV:.Circ18Tok_L2
TPVCirc18Tok_L3 | LONG | IOD_TPV | TPV:.Circ18Tok_L3
TPVCirc18TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ18TokPovprecje_III
TPVCirc19CosFi_III | LONG | IOD_TPV | TPV:.Circ19CosFi_III
TPVCirc19DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ19DelovnaEnergija
TPVCirc19DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ19DelovnaMoc_III
TPVCirc19DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ19DelovnaMoc_L1
TPVCirc19DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ19DelovnaMoc_L2
TPVCirc19DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ19DelovnaMoc_L3
TPVCirc19Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ19Frekvenca_L1
TPVCirc19InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ19InduktivnaEnergija
TPVCirc19InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ19InduktivnaMoc_III
TPVCirc19JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ19JalovaMoc_L1
TPVCirc19JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ19JalovaMoc_L2
TPVCirc19JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ19JalovaMoc_L3
TPVCirc19KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ19KapacitivnaEnergija
TPVCirc19KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ19KapacitivnaMoc_III
TPVCirc19MaximumDemand | LONG | IOD_TPV | TPV:.Circ19MaximumDemand
TPVCirc19Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ19Napetost_L1_L2
TPVCirc19Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ19Napetost_L1_N
TPVCirc19Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ19Napetost_L2_L3
TPVCirc19Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ19Napetost_L2_N
TPVCirc19Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ19Napetost_L3_L1
TPVCirc19Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ19Napetost_L3_N
TPVCirc19NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ19NavideznaMoc_III
TPVCirc19NicelniTok | LONG | IOD_TPV | TPV:.Circ19NicelniTok
TPVCirc19PowerFactor_III | LONG | IOD_TPV | TPV:.Circ19PowerFactor_III
TPVCirc19PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ19PowerFactor_L1
TPVCirc19PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ19PowerFactor_L2
TPVCirc19PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ19PowerFactor_L3
TPVCirc19THDI_L1 | LONG | IOD_TPV | TPV:.Circ19THDI_L1
TPVCirc19THDI_L2 | LONG | IOD_TPV | TPV:.Circ19THDI_L2
TPVCirc19THDI_L3 | LONG | IOD_TPV | TPV:.Circ19THDI_L3
TPVCirc19THDV_L1 | LONG | IOD_TPV | TPV:.Circ19THDV_L1
TPVCirc19THDV_L2 | LONG | IOD_TPV | TPV:.Circ19THDV_L2
TPVCirc19THDV_L3 | LONG | IOD_TPV | TPV:.Circ19THDV_L3
TPVCirc19Tok_L1 | LONG | IOD_TPV | TPV:.Circ19Tok_L1
TPVCirc19Tok_L2 | LONG | IOD_TPV | TPV:.Circ19Tok_L2
TPVCirc19Tok_L3 | LONG | IOD_TPV | TPV:.Circ19Tok_L3
TPVCirc19TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ19TokPovprecje_III
TPVCirc1CosFi_III | LONG | IOD_TPV | TPV:.Circ1CosFi_III
TPVCirc1DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ1DelovnaEnergija
TPVCirc1DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ1DelovnaMoc_III
TPVCirc1DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ1DelovnaMoc_L1
TPVCirc1DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ1DelovnaMoc_L2
TPVCirc1DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ1DelovnaMoc_L3
TPVCirc1Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ1Frekvenca_L1
TPVCirc1InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ1InduktivnaEnergija
TPVCirc1InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ1InduktivnaMoc_III
TPVCirc1JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ1JalovaMoc_L1
TPVCirc1JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ1JalovaMoc_L2
TPVCirc1JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ1JalovaMoc_L3
TPVCirc1KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ1KapacitivnaEnergija
TPVCirc1KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ1KapacitivnaMoc_III
TPVCirc1MaximumDemand | LONG | IOD_TPV | TPV:.Circ1MaximumDemand
TPVCirc1Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ1Napetost_L1_L2
TPVCirc1Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ1Napetost_L1_N
TPVCirc1Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ1Napetost_L2_L3
TPVCirc1Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ1Napetost_L2_N
TPVCirc1Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ1Napetost_L3_L1
TPVCirc1Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ1Napetost_L3_N
TPVCirc1NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ1NavideznaMoc_III
TPVCirc1NicelniTok | LONG | IOD_TPV | TPV:.Circ1NicelniTok
TPVCirc1PowerFactor_III | LONG | IOD_TPV | TPV:.Circ1PowerFactor_III
TPVCirc1PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ1PowerFactor_L1
TPVCirc1PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ1PowerFactor_L2
TPVCirc1PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ1PowerFactor_L3
TPVCirc1THDI_L1 | LONG | IOD_TPV | TPV:.Circ1THDI_L1
TPVCirc1THDI_L2 | LONG | IOD_TPV | TPV:.Circ1THDI_L2
TPVCirc1THDI_L3 | LONG | IOD_TPV | TPV:.Circ1THDI_L3
TPVCirc1THDV_L1 | LONG | IOD_TPV | TPV:.Circ1THDV_L1
TPVCirc1THDV_L2 | LONG | IOD_TPV | TPV:.Circ1THDV_L2
TPVCirc1THDV_L3 | LONG | IOD_TPV | TPV:.Circ1THDV_L3
TPVCirc1Tok_L1 | LONG | IOD_TPV | TPV:.Circ1Tok_L1
TPVCirc1Tok_L2 | LONG | IOD_TPV | TPV:.Circ1Tok_L2
TPVCirc1Tok_L3 | LONG | IOD_TPV | TPV:.Circ1Tok_L3
TPVCirc1TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ1TokPovprecje_III
TPVCirc20CosFi_III | LONG | IOD_TPV | TPV:.Circ20CosFi_III
TPVCirc20DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ20DelovnaEnergija
TPVCirc20DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ20DelovnaMoc_III
TPVCirc20DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ20DelovnaMoc_L1
TPVCirc20DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ20DelovnaMoc_L2
TPVCirc20DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ20DelovnaMoc_L3
TPVCirc20Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ20Frekvenca_L1
TPVCirc20InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ20InduktivnaEnergija
TPVCirc20InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ20InduktivnaMoc_III
TPVCirc20JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ20JalovaMoc_L1
TPVCirc20JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ20JalovaMoc_L2
TPVCirc20JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ20JalovaMoc_L3
TPVCirc20KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ20KapacitivnaEnergija
TPVCirc20KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ20KapacitivnaMoc_III
TPVCirc20MaximumDemand | LONG | IOD_TPV | TPV:.Circ20MaximumDemand
TPVCirc20Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ20Napetost_L1_L2
TPVCirc20Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ20Napetost_L1_N
TPVCirc20Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ20Napetost_L2_L3
TPVCirc20Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ20Napetost_L2_N
TPVCirc20Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ20Napetost_L3_L1
TPVCirc20Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ20Napetost_L3_N
TPVCirc20NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ20NavideznaMoc_III
TPVCirc20NicelniTok | LONG | IOD_TPV | TPV:.Circ20NicelniTok
TPVCirc20PowerFactor_III | LONG | IOD_TPV | TPV:.Circ20PowerFactor_III
TPVCirc20PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ20PowerFactor_L1
TPVCirc20PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ20PowerFactor_L2
TPVCirc20PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ20PowerFactor_L3
TPVCirc20THDI_L1 | LONG | IOD_TPV | TPV:.Circ20THDI_L1
TPVCirc20THDI_L2 | LONG | IOD_TPV | TPV:.Circ20THDI_L2
TPVCirc20THDI_L3 | LONG | IOD_TPV | TPV:.Circ20THDI_L3
TPVCirc20THDV_L1 | LONG | IOD_TPV | TPV:.Circ20THDV_L1
TPVCirc20THDV_L2 | LONG | IOD_TPV | TPV:.Circ20THDV_L2
TPVCirc20THDV_L3 | LONG | IOD_TPV | TPV:.Circ20THDV_L3
TPVCirc20Tok_L1 | LONG | IOD_TPV | TPV:.Circ20Tok_L1
TPVCirc20Tok_L2 | LONG | IOD_TPV | TPV:.Circ20Tok_L2
TPVCirc20Tok_L3 | LONG | IOD_TPV | TPV:.Circ20Tok_L3
TPVCirc20TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ20TokPovprecje_III
TPVCirc21CosFi_III | LONG | IOD_TPV | TPV:.Circ21CosFi_III
TPVCirc21DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ21DelovnaEnergija
TPVCirc21DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ21DelovnaMoc_III
TPVCirc21DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ21DelovnaMoc_L1
TPVCirc21DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ21DelovnaMoc_L2
TPVCirc21DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ21DelovnaMoc_L3
TPVCirc21Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ21Frekvenca_L1
TPVCirc21InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ21InduktivnaEnergija
TPVCirc21InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ21InduktivnaMoc_III
TPVCirc21JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ21JalovaMoc_L1
TPVCirc21JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ21JalovaMoc_L2
TPVCirc21JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ21JalovaMoc_L3
TPVCirc21KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ21KapacitivnaEnergija
TPVCirc21KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ21KapacitivnaMoc_III
TPVCirc21MaximumDemand | LONG | IOD_TPV | TPV:.Circ21MaximumDemand
TPVCirc21Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ21Napetost_L1_L2
TPVCirc21Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ21Napetost_L1_N
TPVCirc21Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ21Napetost_L2_L3
TPVCirc21Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ21Napetost_L2_N
TPVCirc21Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ21Napetost_L3_L1
TPVCirc21Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ21Napetost_L3_N
TPVCirc21NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ21NavideznaMoc_III
TPVCirc21NicelniTok | LONG | IOD_TPV | TPV:.Circ21NicelniTok
TPVCirc21PowerFactor_III | LONG | IOD_TPV | TPV:.Circ21PowerFactor_III
TPVCirc21PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ21PowerFactor_L1
TPVCirc21PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ21PowerFactor_L2
TPVCirc21PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ21PowerFactor_L3
TPVCirc21THDI_L1 | LONG | IOD_TPV | TPV:.Circ21THDI_L1
TPVCirc21THDI_L2 | LONG | IOD_TPV | TPV:.Circ21THDI_L2
TPVCirc21THDI_L3 | LONG | IOD_TPV | TPV:.Circ21THDI_L3
TPVCirc21THDV_L1 | LONG | IOD_TPV | TPV:.Circ21THDV_L1
TPVCirc21THDV_L2 | LONG | IOD_TPV | TPV:.Circ21THDV_L2
TPVCirc21THDV_L3 | LONG | IOD_TPV | TPV:.Circ21THDV_L3
TPVCirc21Tok_L1 | LONG | IOD_TPV | TPV:.Circ21Tok_L1
TPVCirc21Tok_L2 | LONG | IOD_TPV | TPV:.Circ21Tok_L2
TPVCirc21Tok_L3 | LONG | IOD_TPV | TPV:.Circ21Tok_L3
TPVCirc21TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ21TokPovprecje_III
TPVCirc22CosFi_III | LONG | IOD_TPV | TPV:.Circ22CosFi_III
TPVCirc22DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ22DelovnaEnergija
TPVCirc22DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ22DelovnaMoc_III
TPVCirc22DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ22DelovnaMoc_L1
TPVCirc22DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ22DelovnaMoc_L2
TPVCirc22DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ22DelovnaMoc_L3
TPVCirc22Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ22Frekvenca_L1
TPVCirc22InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ22InduktivnaEnergija
TPVCirc22InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ22InduktivnaMoc_III
TPVCirc22JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ22JalovaMoc_L1
TPVCirc22JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ22JalovaMoc_L2
TPVCirc22JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ22JalovaMoc_L3
TPVCirc22KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ22KapacitivnaEnergija
TPVCirc22KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ22KapacitivnaMoc_III
TPVCirc22MaximumDemand | LONG | IOD_TPV | TPV:.Circ22MaximumDemand
TPVCirc22Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ22Napetost_L1_L2
TPVCirc22Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ22Napetost_L1_N
TPVCirc22Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ22Napetost_L2_L3
TPVCirc22Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ22Napetost_L2_N
TPVCirc22Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ22Napetost_L3_L1
TPVCirc22Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ22Napetost_L3_N
TPVCirc22NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ22NavideznaMoc_III
TPVCirc22NicelniTok | LONG | IOD_TPV | TPV:.Circ22NicelniTok
TPVCirc22PowerFactor_III | LONG | IOD_TPV | TPV:.Circ22PowerFactor_III
TPVCirc22PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ22PowerFactor_L1
TPVCirc22PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ22PowerFactor_L2
TPVCirc22PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ22PowerFactor_L3
TPVCirc22THDI_L1 | LONG | IOD_TPV | TPV:.Circ22THDI_L1
TPVCirc22THDI_L2 | LONG | IOD_TPV | TPV:.Circ22THDI_L2
TPVCirc22THDI_L3 | LONG | IOD_TPV | TPV:.Circ22THDI_L3
TPVCirc22THDV_L1 | LONG | IOD_TPV | TPV:.Circ22THDV_L1
TPVCirc22THDV_L2 | LONG | IOD_TPV | TPV:.Circ22THDV_L2
TPVCirc22THDV_L3 | LONG | IOD_TPV | TPV:.Circ22THDV_L3
TPVCirc22Tok_L1 | LONG | IOD_TPV | TPV:.Circ22Tok_L1
TPVCirc22Tok_L2 | LONG | IOD_TPV | TPV:.Circ22Tok_L2
TPVCirc22Tok_L3 | LONG | IOD_TPV | TPV:.Circ22Tok_L3
TPVCirc22TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ22TokPovprecje_III
TPVCirc23CosFi_III | LONG | IOD_TPV | TPV:.Circ23CosFi_III
TPVCirc23DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ23DelovnaEnergija
TPVCirc23DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ23DelovnaMoc_III
TPVCirc23DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ23DelovnaMoc_L1
TPVCirc23DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ23DelovnaMoc_L2
TPVCirc23DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ23DelovnaMoc_L3
TPVCirc23Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ23Frekvenca_L1
TPVCirc23InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ23InduktivnaEnergija
TPVCirc23InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ23InduktivnaMoc_III
TPVCirc23JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ23JalovaMoc_L1
TPVCirc23JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ23JalovaMoc_L2
TPVCirc23JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ23JalovaMoc_L3
TPVCirc23KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ23KapacitivnaEnergija
TPVCirc23KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ23KapacitivnaMoc_III
TPVCirc23MaximumDemand | LONG | IOD_TPV | TPV:.Circ23MaximumDemand
TPVCirc23Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ23Napetost_L1_L2
TPVCirc23Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ23Napetost_L1_N
TPVCirc23Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ23Napetost_L2_L3
TPVCirc23Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ23Napetost_L2_N
TPVCirc23Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ23Napetost_L3_L1
TPVCirc23Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ23Napetost_L3_N
TPVCirc23NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ23NavideznaMoc_III
TPVCirc23NicelniTok | LONG | IOD_TPV | TPV:.Circ23NicelniTok
TPVCirc23PowerFactor_III | LONG | IOD_TPV | TPV:.Circ23PowerFactor_III
TPVCirc23PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ23PowerFactor_L1
TPVCirc23PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ23PowerFactor_L2
TPVCirc23PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ23PowerFactor_L3
TPVCirc23THDI_L1 | LONG | IOD_TPV | TPV:.Circ23THDI_L1
TPVCirc23THDI_L2 | LONG | IOD_TPV | TPV:.Circ23THDI_L2
TPVCirc23THDI_L3 | LONG | IOD_TPV | TPV:.Circ23THDI_L3
TPVCirc23THDV_L1 | LONG | IOD_TPV | TPV:.Circ23THDV_L1
TPVCirc23THDV_L2 | LONG | IOD_TPV | TPV:.Circ23THDV_L2
TPVCirc23THDV_L3 | LONG | IOD_TPV | TPV:.Circ23THDV_L3
TPVCirc23Tok_L1 | LONG | IOD_TPV | TPV:.Circ23Tok_L1
TPVCirc23Tok_L2 | LONG | IOD_TPV | TPV:.Circ23Tok_L2
TPVCirc23Tok_L3 | LONG | IOD_TPV | TPV:.Circ23Tok_L3
TPVCirc23TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ23TokPovprecje_III
TPVCirc24CosFi_III | LONG | IOD_TPV | TPV:.Circ24CosFi_III
TPVCirc24DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ24DelovnaEnergija
TPVCirc24DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ24DelovnaMoc_III
TPVCirc24DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ24DelovnaMoc_L1
TPVCirc24DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ24DelovnaMoc_L2
TPVCirc24DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ24DelovnaMoc_L3
TPVCirc24Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ24Frekvenca_L1
TPVCirc24InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ24InduktivnaEnergija
TPVCirc24InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ24InduktivnaMoc_III
TPVCirc24JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ24JalovaMoc_L1
TPVCirc24JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ24JalovaMoc_L2
TPVCirc24JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ24JalovaMoc_L3
TPVCirc24KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ24KapacitivnaEnergija
TPVCirc24KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ24KapacitivnaMoc_III
TPVCirc24MaximumDemand | LONG | IOD_TPV | TPV:.Circ24MaximumDemand
TPVCirc24Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ24Napetost_L1_L2
TPVCirc24Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ24Napetost_L1_N
TPVCirc24Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ24Napetost_L2_L3
TPVCirc24Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ24Napetost_L2_N
TPVCirc24Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ24Napetost_L3_L1
TPVCirc24Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ24Napetost_L3_N
TPVCirc24NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ24NavideznaMoc_III
TPVCirc24NicelniTok | LONG | IOD_TPV | TPV:.Circ24NicelniTok
TPVCirc24PowerFactor_III | LONG | IOD_TPV | TPV:.Circ24PowerFactor_III
TPVCirc24PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ24PowerFactor_L1
TPVCirc24PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ24PowerFactor_L2
TPVCirc24PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ24PowerFactor_L3
TPVCirc24THDI_L1 | LONG | IOD_TPV | TPV:.Circ24THDI_L1
TPVCirc24THDI_L2 | LONG | IOD_TPV | TPV:.Circ24THDI_L2
TPVCirc24THDI_L3 | LONG | IOD_TPV | TPV:.Circ24THDI_L3
TPVCirc24THDV_L1 | LONG | IOD_TPV | TPV:.Circ24THDV_L1
TPVCirc24THDV_L2 | LONG | IOD_TPV | TPV:.Circ24THDV_L2
TPVCirc24THDV_L3 | LONG | IOD_TPV | TPV:.Circ24THDV_L3
TPVCirc24Tok_L1 | LONG | IOD_TPV | TPV:.Circ24Tok_L1
TPVCirc24Tok_L2 | LONG | IOD_TPV | TPV:.Circ24Tok_L2
TPVCirc24Tok_L3 | LONG | IOD_TPV | TPV:.Circ24Tok_L3
TPVCirc24TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ24TokPovprecje_III
TPVCirc25CosFi_III | LONG | IOD_TPV | TPV:.Circ25CosFi_III
TPVCirc25DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ25DelovnaEnergija
TPVCirc25DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ25DelovnaMoc_III
TPVCirc25DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ25DelovnaMoc_L1
TPVCirc25DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ25DelovnaMoc_L2
TPVCirc25DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ25DelovnaMoc_L3
TPVCirc25Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ25Frekvenca_L1
TPVCirc25InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ25InduktivnaEnergija
TPVCirc25InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ25InduktivnaMoc_III
TPVCirc25JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ25JalovaMoc_L1
TPVCirc25JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ25JalovaMoc_L2
TPVCirc25JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ25JalovaMoc_L3
TPVCirc25KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ25KapacitivnaEnergija
TPVCirc25KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ25KapacitivnaMoc_III
TPVCirc25MaximumDemand | LONG | IOD_TPV | TPV:.Circ25MaximumDemand
TPVCirc25Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ25Napetost_L1_L2
TPVCirc25Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ25Napetost_L1_N
TPVCirc25Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ25Napetost_L2_L3
TPVCirc25Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ25Napetost_L2_N
TPVCirc25Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ25Napetost_L3_L1
TPVCirc25Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ25Napetost_L3_N
TPVCirc25NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ25NavideznaMoc_III
TPVCirc25NicelniTok | LONG | IOD_TPV | TPV:.Circ25NicelniTok
TPVCirc25PowerFactor_III | LONG | IOD_TPV | TPV:.Circ25PowerFactor_III
TPVCirc25PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ25PowerFactor_L1
TPVCirc25PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ25PowerFactor_L2
TPVCirc25PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ25PowerFactor_L3
TPVCirc25THDI_L1 | LONG | IOD_TPV | TPV:.Circ25THDI_L1
TPVCirc25THDI_L2 | LONG | IOD_TPV | TPV:.Circ25THDI_L2
TPVCirc25THDI_L3 | LONG | IOD_TPV | TPV:.Circ25THDI_L3
TPVCirc25THDV_L1 | LONG | IOD_TPV | TPV:.Circ25THDV_L1
TPVCirc25THDV_L2 | LONG | IOD_TPV | TPV:.Circ25THDV_L2
TPVCirc25THDV_L3 | LONG | IOD_TPV | TPV:.Circ25THDV_L3
TPVCirc25Tok_L1 | LONG | IOD_TPV | TPV:.Circ25Tok_L1
TPVCirc25Tok_L2 | LONG | IOD_TPV | TPV:.Circ25Tok_L2
TPVCirc25Tok_L3 | LONG | IOD_TPV | TPV:.Circ25Tok_L3
TPVCirc25TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ25TokPovprecje_III
TPVCirc2CosFi_III | LONG | IOD_TPV | TPV:.Circ2CosFi_III
TPVCirc2DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ2DelovnaEnergija
TPVCirc2DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ2DelovnaMoc_III
TPVCirc2DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ2DelovnaMoc_L1
TPVCirc2DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ2DelovnaMoc_L2
TPVCirc2DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ2DelovnaMoc_L3
TPVCirc2Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ2Frekvenca_L1
TPVCirc2InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ2InduktivnaEnergija
TPVCirc2InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ2InduktivnaMoc_III
TPVCirc2JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ2JalovaMoc_L1
TPVCirc2JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ2JalovaMoc_L2
TPVCirc2JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ2JalovaMoc_L3
TPVCirc2KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ2KapacitivnaEnergija
TPVCirc2KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ2KapacitivnaMoc_III
TPVCirc2MaximumDemand | LONG | IOD_TPV | TPV:.Circ2MaximumDemand
TPVCirc2Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ2Napetost_L1_L2
TPVCirc2Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ2Napetost_L1_N
TPVCirc2Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ2Napetost_L2_L3
TPVCirc2Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ2Napetost_L2_N
TPVCirc2Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ2Napetost_L3_L1
TPVCirc2Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ2Napetost_L3_N
TPVCirc2NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ2NavideznaMoc_III
TPVCirc2NicelniTok | LONG | IOD_TPV | TPV:.Circ2NicelniTok
TPVCirc2PowerFactor_III | LONG | IOD_TPV | TPV:.Circ2PowerFactor_III
TPVCirc2PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ2PowerFactor_L1
TPVCirc2PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ2PowerFactor_L2
TPVCirc2PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ2PowerFactor_L3
TPVCirc2THDI_L1 | LONG | IOD_TPV | TPV:.Circ2THDI_L1
TPVCirc2THDI_L2 | LONG | IOD_TPV | TPV:.Circ2THDI_L2
TPVCirc2THDI_L3 | LONG | IOD_TPV | TPV:.Circ2THDI_L3
TPVCirc2THDV_L1 | LONG | IOD_TPV | TPV:.Circ2THDV_L1
TPVCirc2THDV_L2 | LONG | IOD_TPV | TPV:.Circ2THDV_L2
TPVCirc2THDV_L3 | LONG | IOD_TPV | TPV:.Circ2THDV_L3
TPVCirc2Tok_L1 | LONG | IOD_TPV | TPV:.Circ2Tok_L1
TPVCirc2Tok_L2 | LONG | IOD_TPV | TPV:.Circ2Tok_L2
TPVCirc2Tok_L3 | LONG | IOD_TPV | TPV:.Circ2Tok_L3
TPVCirc2TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ2TokPovprecje_III
TPVCirc3CosFi_III | LONG | IOD_TPV | TPV:.Circ3CosFi_III
TPVCirc3DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ3DelovnaEnergija
TPVCirc3DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ3DelovnaMoc_III
TPVCirc3DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ3DelovnaMoc_L1
TPVCirc3DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ3DelovnaMoc_L2
TPVCirc3DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ3DelovnaMoc_L3
TPVCirc3Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ3Frekvenca_L1
TPVCirc3InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ3InduktivnaEnergija
TPVCirc3InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ3InduktivnaMoc_III
TPVCirc3JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ3JalovaMoc_L1
TPVCirc3JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ3JalovaMoc_L2
TPVCirc3JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ3JalovaMoc_L3
TPVCirc3KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ3KapacitivnaEnergija
TPVCirc3KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ3KapacitivnaMoc_III
TPVCirc3MaximumDemand | LONG | IOD_TPV | TPV:.Circ3MaximumDemand
TPVCirc3Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ3Napetost_L1_L2
TPVCirc3Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ3Napetost_L1_N
TPVCirc3Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ3Napetost_L2_L3
TPVCirc3Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ3Napetost_L2_N
TPVCirc3Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ3Napetost_L3_L1
TPVCirc3Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ3Napetost_L3_N
TPVCirc3NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ3NavideznaMoc_III
TPVCirc3NicelniTok | LONG | IOD_TPV | TPV:.Circ3NicelniTok
TPVCirc3PowerFactor_III | LONG | IOD_TPV | TPV:.Circ3PowerFactor_III
TPVCirc3PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ3PowerFactor_L1
TPVCirc3PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ3PowerFactor_L2
TPVCirc3PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ3PowerFactor_L3
TPVCirc3THDI_L1 | LONG | IOD_TPV | TPV:.Circ3THDI_L1
TPVCirc3THDI_L2 | LONG | IOD_TPV | TPV:.Circ3THDI_L2
TPVCirc3THDI_L3 | LONG | IOD_TPV | TPV:.Circ3THDI_L3
TPVCirc3THDV_L1 | LONG | IOD_TPV | TPV:.Circ3THDV_L1
TPVCirc3THDV_L2 | LONG | IOD_TPV | TPV:.Circ3THDV_L2
TPVCirc3THDV_L3 | LONG | IOD_TPV | TPV:.Circ3THDV_L3
TPVCirc3Tok_L1 | LONG | IOD_TPV | TPV:.Circ3Tok_L1
TPVCirc3Tok_L2 | LONG | IOD_TPV | TPV:.Circ3Tok_L2
TPVCirc3Tok_L3 | LONG | IOD_TPV | TPV:.Circ3Tok_L3
TPVCirc3TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ3TokPovprecje_III
TPVCirc4CosFi_III | LONG | IOD_TPV | TPV:.Circ4CosFi_III
TPVCirc4DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ4DelovnaEnergija
TPVCirc4DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ4DelovnaMoc_III
TPVCirc4DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ4DelovnaMoc_L1
TPVCirc4DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ4DelovnaMoc_L2
TPVCirc4DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ4DelovnaMoc_L3
TPVCirc4Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ4Frekvenca_L1
TPVCirc4InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ4InduktivnaEnergija
TPVCirc4InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ4InduktivnaMoc_III
TPVCirc4JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ4JalovaMoc_L1
TPVCirc4JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ4JalovaMoc_L2
TPVCirc4JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ4JalovaMoc_L3
TPVCirc4KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ4KapacitivnaEnergija
TPVCirc4KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ4KapacitivnaMoc_III
TPVCirc4MaximumDemand | LONG | IOD_TPV | TPV:.Circ4MaximumDemand
TPVCirc4Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ4Napetost_L1_L2
TPVCirc4Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ4Napetost_L1_N
TPVCirc4Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ4Napetost_L2_L3
TPVCirc4Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ4Napetost_L2_N
TPVCirc4Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ4Napetost_L3_L1
TPVCirc4Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ4Napetost_L3_N
TPVCirc4NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ4NavideznaMoc_III
TPVCirc4NicelniTok | LONG | IOD_TPV | TPV:.Circ4NicelniTok
TPVCirc4PowerFactor_III | LONG | IOD_TPV | TPV:.Circ4PowerFactor_III
TPVCirc4PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ4PowerFactor_L1
TPVCirc4PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ4PowerFactor_L2
TPVCirc4PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ4PowerFactor_L3
TPVCirc4THDI_L1 | LONG | IOD_TPV | TPV:.Circ4THDI_L1
TPVCirc4THDI_L2 | LONG | IOD_TPV | TPV:.Circ4THDI_L2
TPVCirc4THDI_L3 | LONG | IOD_TPV | TPV:.Circ4THDI_L3
TPVCirc4THDV_L1 | LONG | IOD_TPV | TPV:.Circ4THDV_L1
TPVCirc4THDV_L2 | LONG | IOD_TPV | TPV:.Circ4THDV_L2
TPVCirc4THDV_L3 | LONG | IOD_TPV | TPV:.Circ4THDV_L3
TPVCirc4Tok_L1 | LONG | IOD_TPV | TPV:.Circ4Tok_L1
TPVCirc4Tok_L2 | LONG | IOD_TPV | TPV:.Circ4Tok_L2
TPVCirc4Tok_L3 | LONG | IOD_TPV | TPV:.Circ4Tok_L3
TPVCirc4TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ4TokPovprecje_III
TPVCirc5CosFi_III | LONG | IOD_TPV | TPV:.Circ5CosFi_III
TPVCirc5DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ5DelovnaEnergija
TPVCirc5DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ5DelovnaMoc_III
TPVCirc5DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ5DelovnaMoc_L1
TPVCirc5DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ5DelovnaMoc_L2
TPVCirc5DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ5DelovnaMoc_L3
TPVCirc5Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ5Frekvenca_L1
TPVCirc5InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ5InduktivnaEnergija
TPVCirc5InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ5InduktivnaMoc_III
TPVCirc5JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ5JalovaMoc_L1
TPVCirc5JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ5JalovaMoc_L2
TPVCirc5JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ5JalovaMoc_L3
TPVCirc5KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ5KapacitivnaEnergija
TPVCirc5KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ5KapacitivnaMoc_III
TPVCirc5MaximumDemand | LONG | IOD_TPV | TPV:.Circ5MaximumDemand
TPVCirc5Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ5Napetost_L1_L2
TPVCirc5Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ5Napetost_L1_N
TPVCirc5Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ5Napetost_L2_L3
TPVCirc5Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ5Napetost_L2_N
TPVCirc5Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ5Napetost_L3_L1
TPVCirc5Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ5Napetost_L3_N
TPVCirc5NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ5NavideznaMoc_III
TPVCirc5NicelniTok | LONG | IOD_TPV | TPV:.Circ5NicelniTok
TPVCirc5PowerFactor_III | LONG | IOD_TPV | TPV:.Circ5PowerFactor_III
TPVCirc5PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ5PowerFactor_L1
TPVCirc5PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ5PowerFactor_L2
TPVCirc5PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ5PowerFactor_L3
TPVCirc5THDI_L1 | LONG | IOD_TPV | TPV:.Circ5THDI_L1
TPVCirc5THDI_L2 | LONG | IOD_TPV | TPV:.Circ5THDI_L2
TPVCirc5THDI_L3 | LONG | IOD_TPV | TPV:.Circ5THDI_L3
TPVCirc5THDV_L1 | LONG | IOD_TPV | TPV:.Circ5THDV_L1
TPVCirc5THDV_L2 | LONG | IOD_TPV | TPV:.Circ5THDV_L2
TPVCirc5THDV_L3 | LONG | IOD_TPV | TPV:.Circ5THDV_L3
TPVCirc5Tok_L1 | LONG | IOD_TPV | TPV:.Circ5Tok_L1
TPVCirc5Tok_L2 | LONG | IOD_TPV | TPV:.Circ5Tok_L2
TPVCirc5Tok_L3 | LONG | IOD_TPV | TPV:.Circ5Tok_L3
TPVCirc5TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ5TokPovprecje_III
TPVCirc6CosFi_III | LONG | IOD_TPV | TPV:.Circ6CosFi_III
TPVCirc6DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ6DelovnaEnergija
TPVCirc6DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ6DelovnaMoc_III
TPVCirc6DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ6DelovnaMoc_L1
TPVCirc6DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ6DelovnaMoc_L2
TPVCirc6DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ6DelovnaMoc_L3
TPVCirc6Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ6Frekvenca_L1
TPVCirc6InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ6InduktivnaEnergija
TPVCirc6InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ6InduktivnaMoc_III
TPVCirc6JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ6JalovaMoc_L1
TPVCirc6JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ6JalovaMoc_L2
TPVCirc6JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ6JalovaMoc_L3
TPVCirc6KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ6KapacitivnaEnergija
TPVCirc6KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ6KapacitivnaMoc_III
TPVCirc6MaximumDemand | LONG | IOD_TPV | TPV:.Circ6MaximumDemand
TPVCirc6Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ6Napetost_L1_L2
TPVCirc6Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ6Napetost_L1_N
TPVCirc6Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ6Napetost_L2_L3
TPVCirc6Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ6Napetost_L2_N
TPVCirc6Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ6Napetost_L3_L1
TPVCirc6Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ6Napetost_L3_N
TPVCirc6NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ6NavideznaMoc_III
TPVCirc6NicelniTok | LONG | IOD_TPV | TPV:.Circ6NicelniTok
TPVCirc6PowerFactor_III | LONG | IOD_TPV | TPV:.Circ6PowerFactor_III
TPVCirc6PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ6PowerFactor_L1
TPVCirc6PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ6PowerFactor_L2
TPVCirc6PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ6PowerFactor_L3
TPVCirc6THDI_L1 | LONG | IOD_TPV | TPV:.Circ6THDI_L1
TPVCirc6THDI_L2 | LONG | IOD_TPV | TPV:.Circ6THDI_L2
TPVCirc6THDI_L3 | LONG | IOD_TPV | TPV:.Circ6THDI_L3
TPVCirc6THDV_L1 | LONG | IOD_TPV | TPV:.Circ6THDV_L1
TPVCirc6THDV_L2 | LONG | IOD_TPV | TPV:.Circ6THDV_L2
TPVCirc6THDV_L3 | LONG | IOD_TPV | TPV:.Circ6THDV_L3
TPVCirc6Tok_L1 | LONG | IOD_TPV | TPV:.Circ6Tok_L1
TPVCirc6Tok_L2 | LONG | IOD_TPV | TPV:.Circ6Tok_L2
TPVCirc6Tok_L3 | LONG | IOD_TPV | TPV:.Circ6Tok_L3
TPVCirc6TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ6TokPovprecje_III
TPVCirc7CosFi_III | LONG | IOD_TPV | TPV:.Circ7CosFi_III
TPVCirc7DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ7DelovnaEnergija
TPVCirc7DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ7DelovnaMoc_III
TPVCirc7DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ7DelovnaMoc_L1
TPVCirc7DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ7DelovnaMoc_L2
TPVCirc7DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ7DelovnaMoc_L3
TPVCirc7Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ7Frekvenca_L1
TPVCirc7InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ7InduktivnaEnergija
TPVCirc7InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ7InduktivnaMoc_III
TPVCirc7JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ7JalovaMoc_L1
TPVCirc7JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ7JalovaMoc_L2
TPVCirc7JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ7JalovaMoc_L3
TPVCirc7KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ7KapacitivnaEnergija
TPVCirc7KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ7KapacitivnaMoc_III
TPVCirc7MaximumDemand | LONG | IOD_TPV | TPV:.Circ7MaximumDemand
TPVCirc7Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ7Napetost_L1_L2
TPVCirc7Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ7Napetost_L1_N
TPVCirc7Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ7Napetost_L2_L3
TPVCirc7Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ7Napetost_L2_N
TPVCirc7Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ7Napetost_L3_L1
TPVCirc7Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ7Napetost_L3_N
TPVCirc7NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ7NavideznaMoc_III
TPVCirc7NicelniTok | LONG | IOD_TPV | TPV:.Circ7NicelniTok
TPVCirc7PowerFactor_III | LONG | IOD_TPV | TPV:.Circ7PowerFactor_III
TPVCirc7PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ7PowerFactor_L1
TPVCirc7PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ7PowerFactor_L2
TPVCirc7PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ7PowerFactor_L3
TPVCirc7THDI_L1 | LONG | IOD_TPV | TPV:.Circ7THDI_L1
TPVCirc7THDI_L2 | LONG | IOD_TPV | TPV:.Circ7THDI_L2
TPVCirc7THDI_L3 | LONG | IOD_TPV | TPV:.Circ7THDI_L3
TPVCirc7THDV_L1 | LONG | IOD_TPV | TPV:.Circ7THDV_L1
TPVCirc7THDV_L2 | LONG | IOD_TPV | TPV:.Circ7THDV_L2
TPVCirc7THDV_L3 | LONG | IOD_TPV | TPV:.Circ7THDV_L3
TPVCirc7Tok_L1 | LONG | IOD_TPV | TPV:.Circ7Tok_L1
TPVCirc7Tok_L2 | LONG | IOD_TPV | TPV:.Circ7Tok_L2
TPVCirc7Tok_L3 | LONG | IOD_TPV | TPV:.Circ7Tok_L3
TPVCirc7TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ7TokPovprecje_III
TPVCirc8CosFi_III | LONG | IOD_TPV | TPV:.Circ8CosFi_III
TPVCirc8DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ8DelovnaEnergija
TPVCirc8DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ8DelovnaMoc_III
TPVCirc8DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ8DelovnaMoc_L1
TPVCirc8DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ8DelovnaMoc_L2
TPVCirc8DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ8DelovnaMoc_L3
TPVCirc8Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ8Frekvenca_L1
TPVCirc8InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ8InduktivnaEnergija
TPVCirc8InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ8InduktivnaMoc_III
TPVCirc8JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ8JalovaMoc_L1
TPVCirc8JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ8JalovaMoc_L2
TPVCirc8JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ8JalovaMoc_L3
TPVCirc8KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ8KapacitivnaEnergija
TPVCirc8KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ8KapacitivnaMoc_III
TPVCirc8MaximumDemand | LONG | IOD_TPV | TPV:.Circ8MaximumDemand
TPVCirc8Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ8Napetost_L1_L2
TPVCirc8Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ8Napetost_L1_N
TPVCirc8Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ8Napetost_L2_L3
TPVCirc8Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ8Napetost_L2_N
TPVCirc8Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ8Napetost_L3_L1
TPVCirc8Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ8Napetost_L3_N
TPVCirc8NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ8NavideznaMoc_III
TPVCirc8NicelniTok | LONG | IOD_TPV | TPV:.Circ8NicelniTok
TPVCirc8PowerFactor_III | LONG | IOD_TPV | TPV:.Circ8PowerFactor_III
TPVCirc8PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ8PowerFactor_L1
TPVCirc8PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ8PowerFactor_L2
TPVCirc8PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ8PowerFactor_L3
TPVCirc8THDI_L1 | LONG | IOD_TPV | TPV:.Circ8THDI_L1
TPVCirc8THDI_L2 | LONG | IOD_TPV | TPV:.Circ8THDI_L2
TPVCirc8THDI_L3 | LONG | IOD_TPV | TPV:.Circ8THDI_L3
TPVCirc8THDV_L1 | LONG | IOD_TPV | TPV:.Circ8THDV_L1
TPVCirc8THDV_L2 | LONG | IOD_TPV | TPV:.Circ8THDV_L2
TPVCirc8THDV_L3 | LONG | IOD_TPV | TPV:.Circ8THDV_L3
TPVCirc8Tok_L1 | LONG | IOD_TPV | TPV:.Circ8Tok_L1
TPVCirc8Tok_L2 | LONG | IOD_TPV | TPV:.Circ8Tok_L2
TPVCirc8Tok_L3 | LONG | IOD_TPV | TPV:.Circ8Tok_L3
TPVCirc8TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ8TokPovprecje_III
TPVCirc9CosFi_III | LONG | IOD_TPV | TPV:.Circ9CosFi_III
TPVCirc9DelovnaEnergija | LONG | IOD_TPV | TPV:.Circ9DelovnaEnergija
TPVCirc9DelovnaMoc_III | LONG | IOD_TPV | TPV:.Circ9DelovnaMoc_III
TPVCirc9DelovnaMoc_L1 | LONG | IOD_TPV | TPV:.Circ9DelovnaMoc_L1
TPVCirc9DelovnaMoc_L2 | LONG | IOD_TPV | TPV:.Circ9DelovnaMoc_L2
TPVCirc9DelovnaMoc_L3 | LONG | IOD_TPV | TPV:.Circ9DelovnaMoc_L3
TPVCirc9Frekvenca_L1 | LONG | IOD_TPV | TPV:.Circ9Frekvenca_L1
TPVCirc9InduktivnaEnergija | LONG | IOD_TPV | TPV:.Circ9InduktivnaEnergija
TPVCirc9InduktivnaMoc_III | LONG | IOD_TPV | TPV:.Circ9InduktivnaMoc_III
TPVCirc9JalovaMoc_L1 | LONG | IOD_TPV | TPV:.Circ9JalovaMoc_L1
TPVCirc9JalovaMoc_L2 | LONG | IOD_TPV | TPV:.Circ9JalovaMoc_L2
TPVCirc9JalovaMoc_L3 | LONG | IOD_TPV | TPV:.Circ9JalovaMoc_L3
TPVCirc9KapacitivnaEnergija | LONG | IOD_TPV | TPV:.Circ9KapacitivnaEnergija
TPVCirc9KapacitivnaMoc_III | LONG | IOD_TPV | TPV:.Circ9KapacitivnaMoc_III
TPVCirc9MaximumDemand | LONG | IOD_TPV | TPV:.Circ9MaximumDemand
TPVCirc9Napetost_L1_L2 | LONG | IOD_TPV | TPV:.Circ9Napetost_L1_L2
TPVCirc9Napetost_L1_N | LONG | IOD_TPV | TPV:.Circ9Napetost_L1_N
TPVCirc9Napetost_L2_L3 | LONG | IOD_TPV | TPV:.Circ9Napetost_L2_L3
TPVCirc9Napetost_L2_N | LONG | IOD_TPV | TPV:.Circ9Napetost_L2_N
TPVCirc9Napetost_L3_L1 | LONG | IOD_TPV | TPV:.Circ9Napetost_L3_L1
TPVCirc9Napetost_L3_N | LONG | IOD_TPV | TPV:.Circ9Napetost_L3_N
TPVCirc9NavideznaMoc_III | LONG | IOD_TPV | TPV:.Circ9NavideznaMoc_III
TPVCirc9NicelniTok | LONG | IOD_TPV | TPV:.Circ9NicelniTok
TPVCirc9PowerFactor_III | LONG | IOD_TPV | TPV:.Circ9PowerFactor_III
TPVCirc9PowerFactor_L1 | LONG | IOD_TPV | TPV:.Circ9PowerFactor_L1
TPVCirc9PowerFactor_L2 | LONG | IOD_TPV | TPV:.Circ9PowerFactor_L2
TPVCirc9PowerFactor_L3 | LONG | IOD_TPV | TPV:.Circ9PowerFactor_L3
TPVCirc9THDI_L1 | LONG | IOD_TPV | TPV:.Circ9THDI_L1
TPVCirc9THDI_L2 | LONG | IOD_TPV | TPV:.Circ9THDI_L2
TPVCirc9THDI_L3 | LONG | IOD_TPV | TPV:.Circ9THDI_L3
TPVCirc9THDV_L1 | LONG | IOD_TPV | TPV:.Circ9THDV_L1
TPVCirc9THDV_L2 | LONG | IOD_TPV | TPV:.Circ9THDV_L2
TPVCirc9THDV_L3 | LONG | IOD_TPV | TPV:.Circ9THDV_L3
TPVCirc9Tok_L1 | LONG | IOD_TPV | TPV:.Circ9Tok_L1
TPVCirc9Tok_L2 | LONG | IOD_TPV | TPV:.Circ9Tok_L2
TPVCirc9Tok_L3 | LONG | IOD_TPV | TPV:.Circ9Tok_L3
TPVCirc9TokPovprecje_III | LONG | IOD_TPV | TPV:.Circ9TokPovprecje_III
TPVDW_Napake1 | LONG | IOD_TPV | TPV:.DW_Napake1
TPVDW_Napake2 | LONG | IOD_TPV | TPV:.DW_Napake2
TPVDW_Napake3 | LONG | IOD_TPV | TPV:.DW_Napake3
TPV_Generator_earth_currentA1 | LONG | IOD_TPV | TPV:.Generator_earth_currentA1
TPV_Generator_earth_currentA2 | LONG | IOD_TPV | TPV:.Generator_earth_currentA2
TPV_Generator_L1_currentA1 | LONG | IOD_TPV | TPV:.Generator_L1_currentA1
TPV_Generator_L1_currentA2 | LONG | IOD_TPV | TPV:.Generator_L1_currentA2
TPV_Generator_L1_L2_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L1_L2_voltageA1
TPV_Generator_L1_L2_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L1_L2_voltageA2
TPV_Generator_L1_N_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L1_N_voltageA1
TPV_Generator_L1_N_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L1_N_voltageA2
TPV_Generator_L1_wattsA1 | LONG | IOD_TPV | TPV:.Generator_L1_wattsA1
TPV_Generator_L1_wattsA2 | LONG | IOD_TPV | TPV:.Generator_L1_wattsA2
TPV_Generator_L2_currentA1 | LONG | IOD_TPV | TPV:.Generator_L2_currentA1
TPV_Generator_L2_currentA2 | LONG | IOD_TPV | TPV:.Generator_L2_currentA2
TPV_Generator_L2_L3_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L2_L3_voltageA1
TPV_Generator_L2_L3_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L2_L3_voltageA2
TPV_Generator_L2_N_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L2_N_voltageA1
TPV_Generator_L2_N_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L2_N_voltageA2
TPV_Generator_L2_wattsA1 | LONG | IOD_TPV | TPV:.Generator_L2_wattsA1
TPV_Generator_L2_wattsA2 | LONG | IOD_TPV | TPV:.Generator_L2_wattsA2
TPV_Generator_L3_currentA1 | LONG | IOD_TPV | TPV:.Generator_L3_currentA1
TPV_Generator_L3_currentA2 | LONG | IOD_TPV | TPV:.Generator_L3_currentA2
TPV_Generator_L3_L1_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L3_L1_voltageA1
TPV_Generator_L3_L1_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L3_L1_voltageA2
TPV_Generator_L3_N_voltageA1 | LONG | IOD_TPV | TPV:.Generator_L3_N_voltageA1
TPV_Generator_L3_N_voltageA2 | LONG | IOD_TPV | TPV:.Generator_L3_N_voltageA2
TPV_Generator_L3_wattsA1 | LONG | IOD_TPV | TPV:.Generator_L3_wattsA1
TPV_Generator_L3_wattsA2 | LONG | IOD_TPV | TPV:.Generator_L3_wattsA2
TPVCirc14NicelniTok_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ14NicelniTok
TPVCirc14Tok_L1_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ14Tok_L1
TPVCirc14Tok_L2_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ14Tok_L2
TPVCirc14Tok_L3_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ14Tok_L3
TPVCirc8NicelniTok_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ8NicelniTok
TPVCirc8Tok_L1_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ8Tok_L1
TPVCirc8Tok_L2_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ8Tok_L2
TPVCirc8Tok_L3_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ8Tok_L3
TPVCirc9NicelniTok_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ9NicelniTok
TPVCirc9Tok_L1_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ9Tok_L1
TPVCirc9Tok_L2_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ9Tok_L2
TPVCirc9Tok_L3_NovoSkaliranje | LONG | IOD_TPV | TPV:.Circ9Tok_L3
TPVCirc1MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ1MaximumDemandA2
TPVCirc1MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ1MaximumDemandA3
TPVCirc2MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ2MaximumDemandA2
TPVCirc2MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ2MaximumDemandA3
TPVCirc3MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ3MaximumDemandA2
TPVCirc3MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ3MaximumDemandA3
TPVCirc4MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ4MaximumDemandA2
TPVCirc4MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ4MaximumDemandA3
TPVCirc5MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ5MaximumDemandA2
TPVCirc5MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ5MaximumDemandA3
TPVCirc6MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ6MaximumDemandA2
TPVCirc6MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ6MaximumDemandA3
TPVCirc7MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ7MaximumDemandA2
TPVCirc7MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ7MaximumDemandA3
TPVCirc8MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ8MaximumDemandA2
TPVCirc8MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ8MaximumDemandA3
TPVCirc9MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ9MaximumDemandA2
TPVCirc9MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ9MaximumDemandA3
TPVCirc10MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ10MaximumDemandA2
TPVCirc10MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ10MaximumDemandA3
TPVCirc11MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ11MaximumDemandA2
TPVCirc11MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ11MaximumDemandA3
TPVCirc12MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ12MaximumDemandA2
TPVCirc12MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ12MaximumDemandA3
TPVCirc13MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ13MaximumDemandA2
TPVCirc13MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ13MaximumDemandA3
TPVCirc14MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ14MaximumDemandA2
TPVCirc14MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ14MaximumDemandA3
TPVCirc15MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ15MaximumDemandA2
TPVCirc15MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ15MaximumDemandA3
TPVCirc16MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ16MaximumDemandA2
TPVCirc16MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ16MaximumDemandA3
TPVCirc17MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ17MaximumDemandA2
TPVCirc17MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ17MaximumDemandA3
TPVCirc18MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ18MaximumDemandA2
TPVCirc18MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ18MaximumDemandA3
TPVCirc19MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ19MaximumDemandA2
TPVCirc19MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ19MaximumDemandA3
TPVCirc20MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ20MaximumDemandA2
TPVCirc20MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ20MaximumDemandA3
TPVCirc21MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ21MaximumDemandA2
TPVCirc21MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ21MaximumDemandA3
TPVCirc22MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ22MaximumDemandA2
TPVCirc22MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ22MaximumDemandA3
TPVCirc23MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ23MaximumDemandA2
TPVCirc23MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ23MaximumDemandA3
TPVCirc24MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ24MaximumDemandA2
TPVCirc24MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ24MaximumDemandA3
TPVCirc25MaximumDemandA2 | LONG | IOD_TPV | TPV:.Circ25MaximumDemandA2
TPVCirc25MaximumDemandA3 | LONG | IOD_TPV | TPV:.Circ25MaximumDemandA3
TPVCirc1RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[1].RazEner_D_SCADA
TPVCirc1RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[1].RazEner_T_SCADA
TPVCirc1RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[1].RazEner_M_SCADA
TPVCirc2RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[2].RazEner_D_SCADA
TPVCirc2RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[2].RazEner_T_SCADA
TPVCirc2RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[2].RazEner_M_SCADA
TPVCirc3RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[3].RazEner_D_SCADA
TPVCirc3RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[3].RazEner_T_SCADA
TPVCirc3RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[3].RazEner_M_SCADA
TPVCirc4RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[4].RazEner_D_SCADA
TPVCirc4RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[4].RazEner_T_SCADA
TPVCirc4RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[4].RazEner_M_SCADA
TPVCirc5RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[5].RazEner_D_SCADA
TPVCirc5RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[5].RazEner_T_SCADA
TPVCirc5RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[5].RazEner_M_SCADA
TPVCirc6RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[6].RazEner_D_SCADA
TPVCirc6RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[6].RazEner_T_SCADA
TPVCirc6RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[6].RazEner_M_SCADA
TPVCirc7RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[7].RazEner_D_SCADA
TPVCirc7RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[7].RazEner_T_SCADA
TPVCirc7RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[7].RazEner_M_SCADA
TPVCirc8RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[8].RazEner_D_SCADA
TPVCirc8RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[8].RazEner_T_SCADA
TPVCirc8RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[8].RazEner_M_SCADA
TPVCirc9RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[9].RazEner_D_SCADA
TPVCirc9RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[9].RazEner_T_SCADA
TPVCirc9RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[9].RazEner_M_SCADA
TPVCirc10RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[10].RazEner_D_SCADA
TPVCirc10RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[10].RazEner_T_SCADA
TPVCirc10RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[10].RazEner_M_SCADA
TPVCirc11RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[11].RazEner_D_SCADA
TPVCirc11RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[11].RazEner_T_SCADA
TPVCirc11RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[11].RazEner_M_SCADA
TPVCirc12RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[12].RazEner_D_SCADA
TPVCirc12RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[12].RazEner_T_SCADA
TPVCirc12RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[12].RazEner_M_SCADA
TPVCirc13RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[13].RazEner_D_SCADA
TPVCirc13RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[13].RazEner_T_SCADA
TPVCirc13RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[13].RazEner_M_SCADA
TPVCirc14RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[14].RazEner_D_SCADA
TPVCirc14RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[14].RazEner_T_SCADA
TPVCirc14RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[14].RazEner_M_SCADA
TPVCirc15RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[15].RazEner_D_SCADA
TPVCirc15RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[15].RazEner_T_SCADA
TPVCirc15RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[15].RazEner_M_SCADA
TPVCirc16RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[16].RazEner_D_SCADA
TPVCirc16RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[16].RazEner_T_SCADA
TPVCirc16RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[16].RazEner_M_SCADA
TPVCirc17RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[17].RazEner_D_SCADA
TPVCirc17RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[17].RazEner_T_SCADA
TPVCirc17RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[17].RazEner_M_SCADA
TPVCirc18RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[18].RazEner_D_SCADA
TPVCirc18RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[18].RazEner_T_SCADA
TPVCirc18RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[18].RazEner_M_SCADA
TPVCirc19RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[19].RazEner_D_SCADA
TPVCirc19RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[19].RazEner_T_SCADA
TPVCirc19RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[19].RazEner_M_SCADA
TPVCirc20RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[20].RazEner_D_SCADA
TPVCirc20RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[20].RazEner_T_SCADA
TPVCirc20RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[20].RazEner_M_SCADA
TPVCirc21RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[21].RazEner_D_SCADA
TPVCirc21RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[21].RazEner_T_SCADA
TPVCirc21RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[21].RazEner_M_SCADA
TPVCirc22RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[22].RazEner_D_SCADA
TPVCirc22RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[22].RazEner_T_SCADA
TPVCirc22RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[22].RazEner_M_SCADA
TPVCirc23RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[23].RazEner_D_SCADA
TPVCirc23RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[23].RazEner_T_SCADA
TPVCirc23RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[23].RazEner_M_SCADA
TPVCirc24RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[24].RazEner_D_SCADA
TPVCirc24RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[24].RazEner_T_SCADA
TPVCirc24RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[24].RazEner_M_SCADA
TPVCirc25RazEner_D_SCADA | LONG | IOD_TPV | TPV:.Circ[25].RazEner_D_SCADA
TPVCirc25RazEner_T_SCADA | LONG | IOD_TPV | TPV:.Circ[25].RazEner_T_SCADA
TPVCirc25RazEner_M_SCADA | LONG | IOD_TPV | TPV:.Circ[25].RazEner_M_SCADA
TPVsinh_cas | STRING | IOD_TPV | TPV:.cas_scada
TPVBattery_voltageA1 | UINT | IOD_TPV | TPV:.Battery_voltageA1
TPVBattery_voltageA2 | UINT | IOD_TPV | TPV:.Battery_voltageA2
TPVCharge_alternator_voltageA1 | UINT | IOD_TPV | TPV:.Charge_alternator_voltageA1
TPVCharge_alternator_voltageA2 | UINT | IOD_TPV | TPV:.Charge_alternator_voltageA2
TPVEngine_speedA1 | UINT | IOD_TPV | TPV:.Engine_speedA1
TPVEngine_speedA2 | UINT | IOD_TPV | TPV:.Engine_speedA2
TPV_Generator_frequencyA1 | UINT | IOD_TPV | TPV:.Generator_frequencyA1
TPV_Generator_frequencyA2 | UINT | IOD_TPV | TPV:.Generator_frequencyA2
TPV_Generator_phase_rotationA1 | UINT | IOD_TPV | TPV:.Generator_phase_rotationA1
TPV_Generator_phase_rotationA2 | UINT | IOD_TPV | TPV:.Generator_phase_rotationA2
TPVOil_pressureA1 | UINT | IOD_TPV | TPV:.Oil_pressureA1
TPVOil_pressureA2 | UINT | IOD_TPV | TPV:.Oil_pressureA2

## variable_3
TPVDA3_rocno | DIGITAL | IOD_TPV_TCP | 1 | 00001 | DA3_rocno
TPVDA3motorni_pogon_okvara | DIGITAL | IOD_TPV_TCP | 2 | 00002 | DA3motorni_pogon_okvara
TPVIzpad_CAN_med_K1_K2 | DIGITAL | IOD_TPV_TCP | 3 | 00003 | Izpad_CAN_med_K1_K2
TPVMI4agr_nap_RGM_A1 | DIGITAL | IOD_TPV_TCP | 4 | 00004 | MI4agr_nap_RGM_A1
TPVMI4agr_nap_RGM_A2 | DIGITAL | IOD_TPV_TCP | 5 | 00005 | MI4agr_nap_RGM_A2
TPVMI4DA1_2Q1_izklop | DIGITAL | IOD_TPV_TCP | 6 | 00006 | MI4DA1_2Q1_izklop
TPVMI4DA1_2Q1_vklop | DIGITAL | IOD_TPV_TCP | 7 | 00007 | MI4DA1_2Q1_vklop
TPVMI4DA1_del | DIGITAL | IOD_TPV_TCP | 8 | 00008 | MI4DA1_del
TPVMI4DA1_prip | DIGITAL | IOD_TPV_TCP | 9 | 00009 | MI4DA1_prip
TPVMI4DA1_rezerva | DIGITAL | IOD_TPV_TCP | 10 | 00010 | MI4DA1_rezerva
TPVMI4DA1_sinh | DIGITAL | IOD_TPV_TCP | 11 | 00011 | MI4DA1_sinh
TPVMI4DA1_zagon | DIGITAL | IOD_TPV_TCP | 12 | 00012 | MI4DA1_zagon
TPVMI4DA2_2Q1_izklop | DIGITAL | IOD_TPV_TCP | 13 | 00013 | MI4DA2_2Q1_izklop
TPVMI4DA2_2Q1_vklop | DIGITAL | IOD_TPV_TCP | 14 | 00014 | MI4DA2_2Q1_vklop
TPVMI4DA2_del | DIGITAL | IOD_TPV_TCP | 15 | 00015 | MI4DA2_del
TPVMI4DA2_prip | DIGITAL | IOD_TPV_TCP | 16 | 00016 | MI4DA2_prip
TPVMI4DA2_rezerva | DIGITAL | IOD_TPV_TCP | 17 | 00017 | MI4DA2_rezerva
TPVMI4DA2_sinh | DIGITAL | IOD_TPV_TCP | 18 | 00018 | MI4DA2_sinh
TPVMI4DA2_zagon | DIGITAL | IOD_TPV_TCP | 19 | 00019 | MI4DA2_zagon
TPVMI4del_zascA1_11Q1 | DIGITAL | IOD_TPV_TCP | 20 | 00020 | MI4del_zascA1_11Q1
TPVMI4del_zascA1_12Q1 | DIGITAL | IOD_TPV_TCP | 21 | 00021 | MI4del_zascA1_12Q1
TPVMI4del_zascA1_13Q1 | DIGITAL | IOD_TPV_TCP | 22 | 00022 | MI4del_zascA1_13Q1
TPVMI4del_zascA1_14Q1 | DIGITAL | IOD_TPV_TCP | 23 | 00023 | MI4del_zascA1_14Q1
TPVMI4del_zascA1_15Q1 | DIGITAL | IOD_TPV_TCP | 24 | 00024 | MI4del_zascA1_15Q1
TPVMI4del_zascA1_16Q1 | DIGITAL | IOD_TPV_TCP | 25 | 00025 | MI4del_zascA1_16Q1
TPVMI4del_zascA1_17Q1 | DIGITAL | IOD_TPV_TCP | 26 | 00026 | MI4del_zascA1_17Q1
TPVMI4del_zascA1_2Q1 | DIGITAL | IOD_TPV_TCP | 27 | 00027 | MI4del_zascA1_2Q1
TPVMI4del_zascA2_11Q1 | DIGITAL | IOD_TPV_TCP | 28 | 00028 | MI4del_zascA2_11Q1
TPVMI4del_zascA2_12Q1 | DIGITAL | IOD_TPV_TCP | 29 | 00029 | MI4del_zascA2_12Q1
TPVMI4del_zascA2_13Q1 | DIGITAL | IOD_TPV_TCP | 30 | 00030 | MI4del_zascA2_13Q1
TPVMI4del_zascA2_14Q1 | DIGITAL | IOD_TPV_TCP | 31 | 00031 | MI4del_zascA2_14Q1
TPVMI4K2agr_nap_RGM_A3 | DIGITAL | IOD_TPV_TCP | 32 | 00032 | MI4K2agr_nap_RGM_A3
TPVMI4K2DA3_2Q1_izklop | DIGITAL | IOD_TPV_TCP | 33 | 00033 | MI4K2DA3_2Q1_izklop
TPVMI4K2DA3_2Q1_vklop | DIGITAL | IOD_TPV_TCP | 34 | 00034 | MI4K2DA3_2Q1_vklop
TPVMI4K2del_zasc0_11Q1 | DIGITAL | IOD_TPV_TCP | 35 | 00035 | MI4K2del_zasc0_11Q1
TPVMI4K2del_zasc0_12Q1 | DIGITAL | IOD_TPV_TCP | 36 | 00036 | MI4K2del_zasc0_12Q1
TPVMI4K2del_zasc0_13Q1 | DIGITAL | IOD_TPV_TCP | 37 | 00037 | MI4K2del_zasc0_13Q1
TPVMI4K2del_zasc0_14Q1 | DIGITAL | IOD_TPV_TCP | 38 | 00038 | MI4K2del_zasc0_14Q1
TPVMI4K2del_zasc0_15Q1 | DIGITAL | IOD_TPV_TCP | 39 | 00039 | MI4K2del_zasc0_15Q1
TPVMI4K2del_zasc0_16Q1 | DIGITAL | IOD_TPV_TCP | 40 | 00040 | MI4K2del_zasc0_16Q1
TPVMI4K2del_zasc0_17Q1 | DIGITAL | IOD_TPV_TCP | 41 | 00041 | MI4K2del_zasc0_17Q1
TPVMI4K2del_zasc0_18Q1 | DIGITAL | IOD_TPV_TCP | 42 | 00042 | MI4K2del_zasc0_18Q1
TPVMI4K2del_zasc0_19Q1 | DIGITAL | IOD_TPV_TCP | 43 | 00043 | MI4K2del_zasc0_19Q1
TPVMI4K2del_zasc0_20Q1 | DIGITAL | IOD_TPV_TCP | 44 | 00044 | MI4K2del_zasc0_20Q1
TPVMI4K2del_zasc0_21Q1 | DIGITAL | IOD_TPV_TCP | 45 | 00045 | MI4K2del_zasc0_21Q1
TPVMI4K2del_zasc0_22Q1 | DIGITAL | IOD_TPV_TCP | 46 | 00046 | MI4K2del_zasc0_22Q1
TPVMI4K2del_zasc0_23Q1 | DIGITAL | IOD_TPV_TCP | 47 | 00047 | MI4K2del_zasc0_23Q1
TPVMI4K2del_zascA3_11Q1 | DIGITAL | IOD_TPV_TCP | 48 | 00048 | MI4K2del_zascA3_11Q1
TPVMI4K2del_zascA3_12Q1 | DIGITAL | IOD_TPV_TCP | 49 | 00049 | MI4K2del_zascA3_12Q1
TPVMI4K2del_zascA3_13Q1 | DIGITAL | IOD_TPV_TCP | 50 | 00050 | MI4K2del_zascA3_13Q1
TPVMI4K2del_zascA3_14Q1 | DIGITAL | IOD_TPV_TCP | 51 | 00051 | MI4K2del_zascA3_14Q1
TPVMI4K2del_zascA3_15Q1 | DIGITAL | IOD_TPV_TCP | 52 | 00052 | MI4K2del_zascA3_15Q1
TPVMI4K2motorA3_1Q1_prip | DIGITAL | IOD_TPV_TCP | 53 | 00053 | MI4K2motorA3_1Q1_prip
TPVMI4K2motorA3_2Q1_prip | DIGITAL | IOD_TPV_TCP | 54 | 00054 | MI4K2motorA3_2Q1_prip
TPVMI4K2mrez_nap_RGM_A3 | DIGITAL | IOD_TPV_TCP | 55 | 00055 | MI4K2mrez_nap_RGM_A3
TPVMI4K2mrezaA3_1Q1_izklop | DIGITAL | IOD_TPV_TCP | 56 | 00056 | MI4K2mrezaA3_1Q1_izklop
TPVMI4K2mrezaA3_1Q1_vklop | DIGITAL | IOD_TPV_TCP | 57 | 00057 | MI4K2mrezaA3_1Q1_vklop
TPVMI4K2prenap_zasc0_OK | DIGITAL | IOD_TPV_TCP | 58 | 00058 | MI4K2prenap_zasc0_OK
TPVMI4K2prenap_zascA3_OK | DIGITAL | IOD_TPV_TCP | 59 | 00059 | MI4K2prenap_zascA3_OK
TPVMI4K2rocni_izk0_11Q1 | DIGITAL | IOD_TPV_TCP | 60 | 00060 | MI4K2rocni_izk0_11Q1
TPVMI4K2rocni_izk0_12Q1 | DIGITAL | IOD_TPV_TCP | 61 | 00061 | MI4K2rocni_izk0_12Q1
TPVMI4K2rocni_izk0_13Q1 | DIGITAL | IOD_TPV_TCP | 62 | 00062 | MI4K2rocni_izk0_13Q1
TPVMI4K2rocni_izk0_14Q1 | DIGITAL | IOD_TPV_TCP | 63 | 00063 | MI4K2rocni_izk0_14Q1
TPVMI4K2rocni_izk0_15Q1 | DIGITAL | IOD_TPV_TCP | 64 | 00064 | MI4K2rocni_izk0_15Q1
TPVMI4K2rocni_izk0_16Q1 | DIGITAL | IOD_TPV_TCP | 65 | 00065 | MI4K2rocni_izk0_16Q1
TPVMI4K2rocni_izk0_17Q1 | DIGITAL | IOD_TPV_TCP | 66 | 00066 | MI4K2rocni_izk0_17Q1
TPVMI4K2rocni_izk0_18Q1 | DIGITAL | IOD_TPV_TCP | 67 | 00067 | MI4K2rocni_izk0_18Q1
TPVMI4K2rocni_izk0_19Q1 | DIGITAL | IOD_TPV_TCP | 68 | 00068 | MI4K2rocni_izk0_19Q1
TPVMI4K2rocni_izk0_20Q1 | DIGITAL | IOD_TPV_TCP | 69 | 00069 | MI4K2rocni_izk0_20Q1
TPVMI4K2rocni_izk0_21Q1 | DIGITAL | IOD_TPV_TCP | 70 | 00070 | MI4K2rocni_izk0_21Q1
TPVMI4K2rocni_izk0_22Q1 | DIGITAL | IOD_TPV_TCP | 71 | 00071 | MI4K2rocni_izk0_22Q1
TPVMI4K2rocni_izk0_23Q1 | DIGITAL | IOD_TPV_TCP | 72 | 00072 | MI4K2rocni_izk0_23Q1
TPVMI4K2rocni_izkA3_11Q1 | DIGITAL | IOD_TPV_TCP | 73 | 00073 | MI4K2rocni_izkA3_11Q1
TPVMI4K2rocni_izkA3_12Q1 | DIGITAL | IOD_TPV_TCP | 74 | 00074 | MI4K2rocni_izkA3_12Q1
TPVMI4K2rocni_izkA3_13Q1 | DIGITAL | IOD_TPV_TCP | 75 | 00075 | MI4K2rocni_izkA3_13Q1
TPVMI4K2rocni_izkA3_14Q1 | DIGITAL | IOD_TPV_TCP | 76 | 00076 | MI4K2rocni_izkA3_14Q1
TPVMI4K2rocni_izkA3_15Q1 | DIGITAL | IOD_TPV_TCP | 77 | 00077 | MI4K2rocni_izkA3_15Q1
TPVMI4K2stik0_11Q1_vkl | DIGITAL | IOD_TPV_TCP | 78 | 00078 | MI4K2stik0_11Q1_vkl
TPVMI4K2stik0_12Q1_vkl | DIGITAL | IOD_TPV_TCP | 79 | 00079 | MI4K2stik0_12Q1_vkl
TPVMI4K2stik0_13Q1_vkl | DIGITAL | IOD_TPV_TCP | 80 | 00080 | MI4K2stik0_13Q1_vkl
TPVMI4K2stik0_14Q1_vkl | DIGITAL | IOD_TPV_TCP | 81 | 00081 | MI4K2stik0_14Q1_vkl
TPVMI4K2stik0_15Q1_vkl | DIGITAL | IOD_TPV_TCP | 82 | 00082 | MI4K2stik0_15Q1_vkl
TPVMI4K2stik0_16Q1_vkl | DIGITAL | IOD_TPV_TCP | 83 | 00083 | MI4K2stik0_16Q1_vkl
TPVMI4K2stik0_17Q1_vkl | DIGITAL | IOD_TPV_TCP | 84 | 00084 | MI4K2stik0_17Q1_vkl
TPVMI4K2stik0_18Q1_vkl | DIGITAL | IOD_TPV_TCP | 85 | 00085 | MI4K2stik0_18Q1_vkl
TPVMI4K2stik0_19Q1_vkl | DIGITAL | IOD_TPV_TCP | 86 | 00086 | MI4K2stik0_19Q1_vkl
TPVMI4K2stik0_1Q1_vkl | DIGITAL | IOD_TPV_TCP | 87 | 00087 | MI4K2stik0_1Q1_vkl
TPVMI4K2stik0_20Q1_vkl | DIGITAL | IOD_TPV_TCP | 88 | 00088 | MI4K2stik0_20Q1_vkl
TPVMI4K2stik0_21Q1_vkl | DIGITAL | IOD_TPV_TCP | 89 | 00089 | MI4K2stik0_21Q1_vkl
TPVMI4K2stik0_22Q1_vkl | DIGITAL | IOD_TPV_TCP | 90 | 00090 | MI4K2stik0_22Q1_vkl
TPVMI4K2stik0_23Q1_vkl | DIGITAL | IOD_TPV_TCP | 91 | 00091 | MI4K2stik0_23Q1_vkl
TPVMI4K2stikA3_11Q1_vkl | DIGITAL | IOD_TPV_TCP | 92 | 00092 | MI4K2stikA3_11Q1_vkl
TPVMI4K2stikA3_12Q1_vkl | DIGITAL | IOD_TPV_TCP | 93 | 00093 | MI4K2stikA3_12Q1_vkl
TPVMI4K2stikA3_13Q1_vkl | DIGITAL | IOD_TPV_TCP | 94 | 00094 | MI4K2stikA3_13Q1_vkl
TPVMI4K2stikA3_14Q1_vkl | DIGITAL | IOD_TPV_TCP | 95 | 00095 | MI4K2stikA3_14Q1_vkl
TPVMI4K2stikA3_15Q1_vkl | DIGITAL | IOD_TPV_TCP | 96 | 00096 | MI4K2stikA3_15Q1_vkl
TPVMI4K2stikA3_1Q1_vkl | DIGITAL | IOD_TPV_TCP | 97 | 00097 | MI4K2stikA3_1Q1_vkl
TPVMI4K2stikA3_2Q1_vkl | DIGITAL | IOD_TPV_TCP | 98 | 00098 | MI4K2stikA3_2Q1_vkl
TPVMI4krmDA_daljinsko | DIGITAL | IOD_TPV_TCP | 99 | 00099 | MI4krmDA_daljinsko
TPVMI4motorA1_1Q1_prip | DIGITAL | IOD_TPV_TCP | 100 | 00100 | MI4motorA1_1Q1_prip
TPVMI4motorA1_2Q1_prip | DIGITAL | IOD_TPV_TCP | 101 | 00101 | MI4motorA1_2Q1_prip
TPVMI4motorA2_1Q1_prip | DIGITAL | IOD_TPV_TCP | 102 | 00102 | MI4motorA2_1Q1_prip
TPVMI4motorA2_2Q1_prip | DIGITAL | IOD_TPV_TCP | 103 | 00103 | MI4motorA2_2Q1_prip
TPVMI4motorA2_6Q1_prip | DIGITAL | IOD_TPV_TCP | 104 | 00104 | MI4motorA2_6Q1_prip
TPVMI4mrez_nap_RGM_A1 | DIGITAL | IOD_TPV_TCP | 105 | 00105 | MI4mrez_nap_RGM_A1
TPVMI4mrez_nap_RGM_A2 | DIGITAL | IOD_TPV_TCP | 106 | 00106 | MI4mrez_nap_RGM_A2
TPVMI4mrezaA1_1Q1_izklop | DIGITAL | IOD_TPV_TCP | 107 | 00107 | MI4mrezaA1_1Q1_izklop
TPVMI4mrezaA1_1Q1_vklop | DIGITAL | IOD_TPV_TCP | 108 | 00108 | MI4mrezaA1_1Q1_vklop
TPVMI4mrezaA2_1Q1_izklop | DIGITAL | IOD_TPV_TCP | 109 | 00109 | MI4mrezaA2_1Q1_izklop
TPVMI4mrezaA2_1Q1_vklop | DIGITAL | IOD_TPV_TCP | 110 | 00110 | MI4mrezaA2_1Q1_vklop
TPVMI4napaka_alarm_DA1 | DIGITAL | IOD_TPV_TCP | 111 | 00111 | MI4napaka_alarm_DA1
TPVMI4napaka_alarm_DA2 | DIGITAL | IOD_TPV_TCP | 112 | 00112 | MI4napaka_alarm_DA2
TPVMI4prenap_zascA1_OK | DIGITAL | IOD_TPV_TCP | 113 | 00113 | MI4prenap_zascA1_OK
TPVMI4prenap_zascA2_OK | DIGITAL | IOD_TPV_TCP | 114 | 00114 | MI4prenap_zascA2_OK
TPVMI4rezerva_DA1 | DIGITAL | IOD_TPV_TCP | 115 | 00115 | MI4rezerva_DA1
TPVMI4rocni_izkA1_11Q1 | DIGITAL | IOD_TPV_TCP | 116 | 00116 | MI4rocni_izkA1_11Q1
TPVMI4rocni_izkA1_12Q1 | DIGITAL | IOD_TPV_TCP | 117 | 00117 | MI4rocni_izkA1_12Q1
TPVMI4rocni_izkA1_13Q1 | DIGITAL | IOD_TPV_TCP | 118 | 00118 | MI4rocni_izkA1_13Q1
TPVMI4rocni_izkA1_14Q1 | DIGITAL | IOD_TPV_TCP | 119 | 00119 | MI4rocni_izkA1_14Q1
TPVMI4rocni_izkA1_15Q1 | DIGITAL | IOD_TPV_TCP | 120 | 00120 | MI4rocni_izkA1_15Q1
TPVMI4rocni_izkA1_16Q1 | DIGITAL | IOD_TPV_TCP | 121 | 00121 | MI4rocni_izkA1_16Q1
TPVMI4rocni_izkA1_17Q1 | DIGITAL | IOD_TPV_TCP | 122 | 00122 | MI4rocni_izkA1_17Q1
TPVMI4rocni_izkA2_11Q1 | DIGITAL | IOD_TPV_TCP | 123 | 00123 | MI4rocni_izkA2_11Q1
TPVMI4rocni_izkA2_12Q1 | DIGITAL | IOD_TPV_TCP | 124 | 00124 | MI4rocni_izkA2_12Q1
TPVMI4rocni_izkA2_13Q1 | DIGITAL | IOD_TPV_TCP | 125 | 00125 | MI4rocni_izkA2_13Q1
TPVMI4rocni_izkA2_14Q1 | DIGITAL | IOD_TPV_TCP | 126 | 00126 | MI4rocni_izkA2_14Q1
TPVMI4sinhroniziranje_DA1 | DIGITAL | IOD_TPV_TCP | 127 | 00127 | MI4sinhroniziranje_DA1
TPVMI4sinhroniziranje_DA2 | DIGITAL | IOD_TPV_TCP | 128 | 00128 | MI4sinhroniziranje_DA2
TPVMI4splosna_napaka_DA1 | DIGITAL | IOD_TPV_TCP | 129 | 00129 | MI4splosna_napaka_DA1
TPVMI4splosna_napaka_DA2 | DIGITAL | IOD_TPV_TCP | 130 | 00130 | MI4splosna_napaka_DA2
TPVMI4stikA1_11Q1_vkl | DIGITAL | IOD_TPV_TCP | 131 | 00131 | MI4stikA1_11Q1_vkl
TPVMI4stikA1_12Q1_vkl | DIGITAL | IOD_TPV_TCP | 132 | 00132 | MI4stikA1_12Q1_vkl
TPVMI4stikA1_13Q1_vkl | DIGITAL | IOD_TPV_TCP | 133 | 00133 | MI4stikA1_13Q1_vkl
TPVMI4stikA1_14Q1_vkl | DIGITAL | IOD_TPV_TCP | 134 | 00134 | MI4stikA1_14Q1_vkl
TPVMI4stikA1_15Q1_vkl | DIGITAL | IOD_TPV_TCP | 135 | 00135 | MI4stikA1_15Q1_vkl
TPVMI4stikA1_16Q1_vkl | DIGITAL | IOD_TPV_TCP | 136 | 00136 | MI4stikA1_16Q1_vkl
TPVMI4stikA1_17Q1_vkl | DIGITAL | IOD_TPV_TCP | 137 | 00137 | MI4stikA1_17Q1_vkl
TPVMI4stikA1_1Q1_vkl | DIGITAL | IOD_TPV_TCP | 138 | 00138 | MI4stikA1_1Q1_vkl
TPVMI4stikA1_2Q1_vkl | DIGITAL | IOD_TPV_TCP | 139 | 00139 | MI4stikA1_2Q1_vkl
TPVMI4stikA1_6Q1_vkl | DIGITAL | IOD_TPV_TCP | 140 | 00140 | MI4stikA1_6Q1_vkl
TPVMI4stikA2_11Q1_vkl | DIGITAL | IOD_TPV_TCP | 141 | 00141 | MI4stikA2_11Q1_vkl
TPVMI4stikA2_12Q1_vkl | DIGITAL | IOD_TPV_TCP | 142 | 00142 | MI4stikA2_12Q1_vkl
TPVMI4stikA2_13Q1_vkl | DIGITAL | IOD_TPV_TCP | 143 | 00143 | MI4stikA2_13Q1_vkl
TPVMI4stikA2_14Q1_vkl | DIGITAL | IOD_TPV_TCP | 144 | 00144 | MI4stikA2_14Q1_vkl
TPVMI4stikA2_1Q1_vkl | DIGITAL | IOD_TPV_TCP | 145 | 00145 | MI4stikA2_1Q1_vkl
TPVMI4stikA2_2Q1_vkl | DIGITAL | IOD_TPV_TCP | 146 | 00146 | MI4stikA2_2Q1_vkl
TPVMI4vezno_6Q1_izklop | DIGITAL | IOD_TPV_TCP | 147 | 00147 | MI4vezno_6Q1_izklop
TPVMI4vezno_6Q1_vklop | DIGITAL | IOD_TPV_TCP | 148 | 00148 | MI4vezno_6Q1_vklop
TPVMI4vzporedno_del_nikoli | DIGITAL | IOD_TPV_TCP | 149 | 00149 | MI4vzporedno_del_nikoli
TPVMI4vzporedno_del_nikoli_info | DIGITAL | IOD_TPV_TCP | 150 | 00150 | MI4vzporedno_del_nikoli_info
TPVMI4vzporedno_del_po_potrebi | DIGITAL | IOD_TPV_TCP | 151 | 00151 | MI4vzporedno_del_po_potrebi
TPVMI4vzporedno_del_po_potrebi_info | DIGITAL | IOD_TPV_TCP | 152 | 00152 | MI4vzporedno_del_po_potrebi_info
TPVMI4vzporedno_del_vedno | DIGITAL | IOD_TPV_TCP | 153 | 00153 | MI4vzporedno_del_vedno
TPVMI4vzporedno_del_vedno_info | DIGITAL | IOD_TPV_TCP | 154 | 00154 | MI4vzporedno_del_vedno_info
TPVMI4zaganjanje_DA1 | DIGITAL | IOD_TPV_TCP | 155 | 00155 | MI4zaganjanje_DA1
TPVMI4zaganjanje_DA2 | DIGITAL | IOD_TPV_TCP | 156 | 00156 | MI4zaganjanje_DA2
TPVmrezaDA3motorni_pogon_okvara | DIGITAL | IOD_TPV_TCP | 157 | 00157 | mrezaDA3motorni_pogon_okvara
TPVmrezaDA3stikalo_okvara | DIGITAL | IOD_TPV_TCP | 158 | 00158 | mrezaDA3stikalo_okvara
TPVNapaka_v_kom_cirk_DA1 | DIGITAL | IOD_TPV_TCP | 159 | 00159 | Napaka_v_kom_cirk_DA1
TPVNapaka_v_kom_cirk_DA2 | DIGITAL | IOD_TPV_TCP | 160 | 00160 | Napaka_v_kom_cirk_DA2
TPVNapakaCOMModBus | DIGITAL | IOD_TPV_TCP | 161 | 00161 | NapakaCOMModBus
TPVNapakaVKomunikaciji_Circutor1 | DIGITAL | IOD_TPV_TCP | 162 | 00162 | NapakaVKomunikaciji_Circutor1
TPVNapakaVKomunikaciji_Circutor10 | DIGITAL | IOD_TPV_TCP | 163 | 00163 | NapakaVKomunikaciji_Circutor10
TPVNapakaVKomunikaciji_Circutor11 | DIGITAL | IOD_TPV_TCP | 164 | 00164 | NapakaVKomunikaciji_Circutor11
TPVNapakaVKomunikaciji_Circutor12 | DIGITAL | IOD_TPV_TCP | 165 | 00165 | NapakaVKomunikaciji_Circutor12
TPVNapakaVKomunikaciji_Circutor13 | DIGITAL | IOD_TPV_TCP | 166 | 00166 | NapakaVKomunikaciji_Circutor13
TPVNapakaVKomunikaciji_Circutor14 | DIGITAL | IOD_TPV_TCP | 167 | 00167 | NapakaVKomunikaciji_Circutor14
TPVNapakaVKomunikaciji_Circutor15 | DIGITAL | IOD_TPV_TCP | 168 | 00168 | NapakaVKomunikaciji_Circutor15
TPVNapakaVKomunikaciji_Circutor16 | DIGITAL | IOD_TPV_TCP | 169 | 00169 | NapakaVKomunikaciji_Circutor16
TPVNapakaVKomunikaciji_Circutor17 | DIGITAL | IOD_TPV_TCP | 170 | 00170 | NapakaVKomunikaciji_Circutor17
TPVNapakaVKomunikaciji_Circutor18 | DIGITAL | IOD_TPV_TCP | 171 | 00171 | NapakaVKomunikaciji_Circutor18
TPVNapakaVKomunikaciji_Circutor19 | DIGITAL | IOD_TPV_TCP | 172 | 00172 | NapakaVKomunikaciji_Circutor19
TPVNapakaVKomunikaciji_Circutor2 | DIGITAL | IOD_TPV_TCP | 173 | 00173 | NapakaVKomunikaciji_Circutor2
TPVNapakaVKomunikaciji_Circutor20 | DIGITAL | IOD_TPV_TCP | 174 | 00174 | NapakaVKomunikaciji_Circutor20
TPVNapakaVKomunikaciji_Circutor21 | DIGITAL | IOD_TPV_TCP | 175 | 00175 | NapakaVKomunikaciji_Circutor21
TPVNapakaVKomunikaciji_Circutor22 | DIGITAL | IOD_TPV_TCP | 176 | 00176 | NapakaVKomunikaciji_Circutor22
TPVNapakaVKomunikaciji_Circutor23 | DIGITAL | IOD_TPV_TCP | 177 | 00177 | NapakaVKomunikaciji_Circutor23
TPVNapakaVKomunikaciji_Circutor24 | DIGITAL | IOD_TPV_TCP | 178 | 00178 | NapakaVKomunikaciji_Circutor24
TPVNapakaVKomunikaciji_Circutor25 | DIGITAL | IOD_TPV_TCP | 179 | 00179 | NapakaVKomunikaciji_Circutor25
TPVNapakaVKomunikaciji_Circutor3 | DIGITAL | IOD_TPV_TCP | 180 | 00180 | NapakaVKomunikaciji_Circutor3
TPVNapakaVKomunikaciji_Circutor4 | DIGITAL | IOD_TPV_TCP | 181 | 00181 | NapakaVKomunikaciji_Circutor4
TPVNapakaVKomunikaciji_Circutor5 | DIGITAL | IOD_TPV_TCP | 182 | 00182 | NapakaVKomunikaciji_Circutor5
TPVNapakaVKomunikaciji_Circutor6 | DIGITAL | IOD_TPV_TCP | 183 | 00183 | NapakaVKomunikaciji_Circutor6
TPVNapakaVKomunikaciji_Circutor7 | DIGITAL | IOD_TPV_TCP | 184 | 00184 | NapakaVKomunikaciji_Circutor7
TPVNapakaVKomunikaciji_Circutor8 | DIGITAL | IOD_TPV_TCP | 185 | 00185 | NapakaVKomunikaciji_Circutor8
TPVNapakaVKomunikaciji_Circutor9 | DIGITAL | IOD_TPV_TCP | 186 | 00186 | NapakaVKomunikaciji_Circutor9
TPVRDASlabaBaterijaMI4 | DIGITAL | IOD_TPV_TCP | 187 | 00187 | RDASlabaBaterijaMI4
TPVSlabaBaterijaMI4 | DIGITAL | IOD_TPV_TCP | 188 | 00188 | SlabaBaterijaMI4
TPVSlabaBaterijaPLC1 | DIGITAL | IOD_TPV_TCP | 189 | 00189 | SlabaBaterijaPLC1
TPVSlabaBaterijaPLC2 | DIGITAL | IOD_TPV_TCP | 190 | 00190 | SlabaBaterijaPLC2
TPVstikaloDA3_okvara | DIGITAL | IOD_TPV_TCP | 191 | 00191 | stikaloDA3_okvara
TPVUI_MI4K2DA3_2Q1_izklop | DIGITAL | IOD_TPV_TCP | 192 | 00192 | UI_MI4K2DA3_2Q1_izklop
TPVUI_MI4K2DA3_2Q1_vklop | DIGITAL | IOD_TPV_TCP | 193 | 00193 | UI_MI4K2DA3_2Q1_vklop
TPVUI_MI4K2mrezaA3_1Q1_izklop | DIGITAL | IOD_TPV_TCP | 194 | 00194 | UI_MI4K2mrezaA3_1Q1_izklop
TPVUI_MI4K2mrezaA3_1Q1_vklop | DIGITAL | IOD_TPV_TCP | 195 | 00195 | UI_MI4K2mrezaA3_1Q1_vklop
TPVsinh_cas_nastavi | DIGITAL | IOD_TPV_TCP | 196 | 00196 | cas_nastavi
TPVCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_TPV_TCP | 197 | 00197 | Circ_Vpis_Dnevne_energija_scada1
TPVCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_TPV_TCP | 198 | 00198 | Circ_Vpis_Dnevne_energija_scada2
TPVCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_TPV_TCP | 199 | 00199 | Circ_Vpis_Tedenska_energija_scada1
TPVCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_TPV_TCP | 200 | 00200 | Circ_Vpis_Tedenska_energija_scada2
TPVCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_TPV_TCP | 201 | 00201 | Circ_Vpis_Mesecna_energija_scada1
TPVCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_TPV_TCP | 202 | 00202 | Circ_Vpis_Mesecna_energija_scada2
TPVCoolant_temperatureA1 | INT | IOD_TPV_TCP | 1 | 40001 | Coolant_temperatureA1
TPVCoolant_temperatureA2 | INT | IOD_TPV_TCP | 2 | 40002 | Coolant_temperatureA2
TPVdelovna_energ_trenutno | INT | IOD_TPV_TCP | 3 | 40003 | delovna_energ_trenutno
TPVdelovna_energija_prej | INT | IOD_TPV_TCP | 4 | 40004 | delovna_energija_prej
TPV_Generator_current_lag_leadA1 | INT | IOD_TPV_TCP | 5 | 40005 | Generator_current_lag_leadA1
TPV_Generator_current_lag_leadA2 | INT | IOD_TPV_TCP | 6 | 40006 | Generator_current_lag_leadA2
TPVjalova_energ_trenutno | INT | IOD_TPV_TCP | 7 | 40007 | jalova_energ_trenutno
TPVjalova_energija_prej | INT | IOD_TPV_TCP | 8 | 40008 | jalova_energija_prej
TPVKomanda | INT | IOD_TPV_TCP | 9 | 40009 | Komanda
TPVNastaviDanMI | INT | IOD_TPV_TCP | 10 | 40010 | NastaviDanMI
TPVNastaviLetoMI | INT | IOD_TPV_TCP | 11 | 40011 | NastaviLetoMI
TPVNastaviMesecMI | INT | IOD_TPV_TCP | 12 | 40012 | NastaviMesecMI
TPVNastaviMinutaMI | INT | IOD_TPV_TCP | 13 | 40013 | NastaviMinutaMI
TPVNastaviSekundaMI | INT | IOD_TPV_TCP | 14 | 40014 | NastaviSekundaMI
TPVNastaviUraMI | INT | IOD_TPV_TCP | 15 | 40015 | NastaviUraMI
TPVStatus | INT | IOD_TPV_TCP | 16 | 40016 | Status
IzpadTPV | INT | IOD_TPV_TCP | 17 | 40017 | st_izpad_komTPV
TPVCirc10CosFi_III | LONG | IOD_TPV_TCP | 3001 | 43001 | Circ10CosFi_III
TPVCirc10DelovnaEnergija | LONG | IOD_TPV_TCP | 3003 | 43003 | Circ10DelovnaEnergija
TPVCirc10DelovnaMoc_III | LONG | IOD_TPV_TCP | 3005 | 43005 | Circ10DelovnaMoc_III
TPVCirc10DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 3007 | 43007 | Circ10DelovnaMoc_L1
TPVCirc10DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 3009 | 43009 | Circ10DelovnaMoc_L2
TPVCirc10DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 3011 | 43011 | Circ10DelovnaMoc_L3
TPVCirc10Frekvenca_L1 | LONG | IOD_TPV_TCP | 3013 | 43013 | Circ10Frekvenca_L1
TPVCirc10InduktivnaEnergija | LONG | IOD_TPV_TCP | 3015 | 43015 | Circ10InduktivnaEnergija
TPVCirc10InduktivnaMoc_III | LONG | IOD_TPV_TCP | 3017 | 43017 | Circ10InduktivnaMoc_III
TPVCirc10JalovaMoc_L1 | LONG | IOD_TPV_TCP | 3019 | 43019 | Circ10JalovaMoc_L1
TPVCirc10JalovaMoc_L2 | LONG | IOD_TPV_TCP | 3021 | 43021 | Circ10JalovaMoc_L2
TPVCirc10JalovaMoc_L3 | LONG | IOD_TPV_TCP | 3023 | 43023 | Circ10JalovaMoc_L3
TPVCirc10KapacitivnaEnergija | LONG | IOD_TPV_TCP | 3025 | 43025 | Circ10KapacitivnaEnergija
TPVCirc10KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 3027 | 43027 | Circ10KapacitivnaMoc_III
TPVCirc10MaximumDemand | LONG | IOD_TPV_TCP | 3029 | 43029 | Circ10MaximumDemand
TPVCirc10Napetost_L1_L2 | LONG | IOD_TPV_TCP | 3031 | 43031 | Circ10Napetost_L1_L2
TPVCirc10Napetost_L1_N | LONG | IOD_TPV_TCP | 3033 | 43033 | Circ10Napetost_L1_N
TPVCirc10Napetost_L2_L3 | LONG | IOD_TPV_TCP | 3035 | 43035 | Circ10Napetost_L2_L3
TPVCirc10Napetost_L2_N | LONG | IOD_TPV_TCP | 3037 | 43037 | Circ10Napetost_L2_N
TPVCirc10Napetost_L3_L1 | LONG | IOD_TPV_TCP | 3039 | 43039 | Circ10Napetost_L3_L1
TPVCirc10Napetost_L3_N | LONG | IOD_TPV_TCP | 3041 | 43041 | Circ10Napetost_L3_N
TPVCirc10NavideznaMoc_III | LONG | IOD_TPV_TCP | 3043 | 43043 | Circ10NavideznaMoc_III
TPVCirc10NicelniTok | LONG | IOD_TPV_TCP | 3045 | 43045 | Circ10NicelniTok
TPVCirc10PowerFactor_III | LONG | IOD_TPV_TCP | 3047 | 43047 | Circ10PowerFactor_III
TPVCirc10PowerFactor_L1 | LONG | IOD_TPV_TCP | 3049 | 43049 | Circ10PowerFactor_L1
TPVCirc10PowerFactor_L2 | LONG | IOD_TPV_TCP | 3051 | 43051 | Circ10PowerFactor_L2
TPVCirc10PowerFactor_L3 | LONG | IOD_TPV_TCP | 3053 | 43053 | Circ10PowerFactor_L3
TPVCirc10THDI_L1 | LONG | IOD_TPV_TCP | 3055 | 43055 | Circ10THDI_L1
TPVCirc10THDI_L2 | LONG | IOD_TPV_TCP | 3057 | 43057 | Circ10THDI_L2
TPVCirc10THDI_L3 | LONG | IOD_TPV_TCP | 3059 | 43059 | Circ10THDI_L3
TPVCirc10THDV_L1 | LONG | IOD_TPV_TCP | 3061 | 43061 | Circ10THDV_L1
TPVCirc10THDV_L2 | LONG | IOD_TPV_TCP | 3063 | 43063 | Circ10THDV_L2
TPVCirc10THDV_L3 | LONG | IOD_TPV_TCP | 3065 | 43065 | Circ10THDV_L3
TPVCirc10Tok_L1 | LONG | IOD_TPV_TCP | 3067 | 43067 | Circ10Tok_L1
TPVCirc10Tok_L2 | LONG | IOD_TPV_TCP | 3069 | 43069 | Circ10Tok_L2
TPVCirc10Tok_L3 | LONG | IOD_TPV_TCP | 3071 | 43071 | Circ10Tok_L3
TPVCirc10TokPovprecje_III | LONG | IOD_TPV_TCP | 3073 | 43073 | Circ10TokPovprecje_III
TPVCirc11CosFi_III | LONG | IOD_TPV_TCP | 3075 | 43075 | Circ11CosFi_III
TPVCirc11DelovnaEnergija | LONG | IOD_TPV_TCP | 3077 | 43077 | Circ11DelovnaEnergija
TPVCirc11DelovnaMoc_III | LONG | IOD_TPV_TCP | 3079 | 43079 | Circ11DelovnaMoc_III
TPVCirc11DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 3081 | 43081 | Circ11DelovnaMoc_L1
TPVCirc11DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 3083 | 43083 | Circ11DelovnaMoc_L2
TPVCirc11DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 3085 | 43085 | Circ11DelovnaMoc_L3
TPVCirc11Frekvenca_L1 | LONG | IOD_TPV_TCP | 3087 | 43087 | Circ11Frekvenca_L1
TPVCirc11InduktivnaEnergija | LONG | IOD_TPV_TCP | 3089 | 43089 | Circ11InduktivnaEnergija
TPVCirc11InduktivnaMoc_III | LONG | IOD_TPV_TCP | 3091 | 43091 | Circ11InduktivnaMoc_III
TPVCirc11JalovaMoc_L1 | LONG | IOD_TPV_TCP | 3093 | 43093 | Circ11JalovaMoc_L1
TPVCirc11JalovaMoc_L2 | LONG | IOD_TPV_TCP | 3095 | 43095 | Circ11JalovaMoc_L2
TPVCirc11JalovaMoc_L3 | LONG | IOD_TPV_TCP | 3097 | 43097 | Circ11JalovaMoc_L3
TPVCirc11KapacitivnaEnergija | LONG | IOD_TPV_TCP | 3099 | 43099 | Circ11KapacitivnaEnergija
TPVCirc11KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 3101 | 43101 | Circ11KapacitivnaMoc_III
TPVCirc11MaximumDemand | LONG | IOD_TPV_TCP | 3103 | 43103 | Circ11MaximumDemand
TPVCirc11Napetost_L1_L2 | LONG | IOD_TPV_TCP | 3105 | 43105 | Circ11Napetost_L1_L2
TPVCirc11Napetost_L1_N | LONG | IOD_TPV_TCP | 3107 | 43107 | Circ11Napetost_L1_N
TPVCirc11Napetost_L2_L3 | LONG | IOD_TPV_TCP | 3109 | 43109 | Circ11Napetost_L2_L3
TPVCirc11Napetost_L2_N | LONG | IOD_TPV_TCP | 3111 | 43111 | Circ11Napetost_L2_N
TPVCirc11Napetost_L3_L1 | LONG | IOD_TPV_TCP | 3113 | 43113 | Circ11Napetost_L3_L1
TPVCirc11Napetost_L3_N | LONG | IOD_TPV_TCP | 3115 | 43115 | Circ11Napetost_L3_N
TPVCirc11NavideznaMoc_III | LONG | IOD_TPV_TCP | 3117 | 43117 | Circ11NavideznaMoc_III
TPVCirc11NicelniTok | LONG | IOD_TPV_TCP | 3119 | 43119 | Circ11NicelniTok
TPVCirc11PowerFactor_III | LONG | IOD_TPV_TCP | 3121 | 43121 | Circ11PowerFactor_III
TPVCirc11PowerFactor_L1 | LONG | IOD_TPV_TCP | 3123 | 43123 | Circ11PowerFactor_L1
TPVCirc11PowerFactor_L2 | LONG | IOD_TPV_TCP | 3125 | 43125 | Circ11PowerFactor_L2
TPVCirc11PowerFactor_L3 | LONG | IOD_TPV_TCP | 3127 | 43127 | Circ11PowerFactor_L3
TPVCirc11THDI_L1 | LONG | IOD_TPV_TCP | 3129 | 43129 | Circ11THDI_L1
TPVCirc11THDI_L2 | LONG | IOD_TPV_TCP | 3131 | 43131 | Circ11THDI_L2
TPVCirc11THDI_L3 | LONG | IOD_TPV_TCP | 3133 | 43133 | Circ11THDI_L3
TPVCirc11THDV_L1 | LONG | IOD_TPV_TCP | 3135 | 43135 | Circ11THDV_L1
TPVCirc11THDV_L2 | LONG | IOD_TPV_TCP | 3137 | 43137 | Circ11THDV_L2
TPVCirc11THDV_L3 | LONG | IOD_TPV_TCP | 3139 | 43139 | Circ11THDV_L3
TPVCirc11Tok_L1 | LONG | IOD_TPV_TCP | 3141 | 43141 | Circ11Tok_L1
TPVCirc11Tok_L2 | LONG | IOD_TPV_TCP | 3143 | 43143 | Circ11Tok_L2
TPVCirc11Tok_L3 | LONG | IOD_TPV_TCP | 3145 | 43145 | Circ11Tok_L3
TPVCirc11TokPovprecje_III | LONG | IOD_TPV_TCP | 3147 | 43147 | Circ11TokPovprecje_III
TPVCirc12CosFi_III | LONG | IOD_TPV_TCP | 3149 | 43149 | Circ12CosFi_III
TPVCirc12DelovnaEnergija | LONG | IOD_TPV_TCP | 3151 | 43151 | Circ12DelovnaEnergija
TPVCirc12DelovnaMoc_III | LONG | IOD_TPV_TCP | 3153 | 43153 | Circ12DelovnaMoc_III
TPVCirc12DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 3155 | 43155 | Circ12DelovnaMoc_L1
TPVCirc12DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 3157 | 43157 | Circ12DelovnaMoc_L2
TPVCirc12DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 3159 | 43159 | Circ12DelovnaMoc_L3
TPVCirc12Frekvenca_L1 | LONG | IOD_TPV_TCP | 3161 | 43161 | Circ12Frekvenca_L1
TPVCirc12InduktivnaEnergija | LONG | IOD_TPV_TCP | 3163 | 43163 | Circ12InduktivnaEnergija
TPVCirc12InduktivnaMoc_III | LONG | IOD_TPV_TCP | 3165 | 43165 | Circ12InduktivnaMoc_III
TPVCirc12JalovaMoc_L1 | LONG | IOD_TPV_TCP | 3167 | 43167 | Circ12JalovaMoc_L1
TPVCirc12JalovaMoc_L2 | LONG | IOD_TPV_TCP | 3169 | 43169 | Circ12JalovaMoc_L2
TPVCirc12JalovaMoc_L3 | LONG | IOD_TPV_TCP | 3171 | 43171 | Circ12JalovaMoc_L3
TPVCirc12KapacitivnaEnergija | LONG | IOD_TPV_TCP | 3173 | 43173 | Circ12KapacitivnaEnergija
TPVCirc12KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 3175 | 43175 | Circ12KapacitivnaMoc_III
TPVCirc12MaximumDemand | LONG | IOD_TPV_TCP | 3177 | 43177 | Circ12MaximumDemand
TPVCirc12Napetost_L1_L2 | LONG | IOD_TPV_TCP | 3179 | 43179 | Circ12Napetost_L1_L2
TPVCirc12Napetost_L1_N | LONG | IOD_TPV_TCP | 3181 | 43181 | Circ12Napetost_L1_N
TPVCirc12Napetost_L2_L3 | LONG | IOD_TPV_TCP | 3183 | 43183 | Circ12Napetost_L2_L3
TPVCirc12Napetost_L2_N | LONG | IOD_TPV_TCP | 3185 | 43185 | Circ12Napetost_L2_N
TPVCirc12Napetost_L3_L1 | LONG | IOD_TPV_TCP | 3187 | 43187 | Circ12Napetost_L3_L1
TPVCirc12Napetost_L3_N | LONG | IOD_TPV_TCP | 3189 | 43189 | Circ12Napetost_L3_N
TPVCirc12NavideznaMoc_III | LONG | IOD_TPV_TCP | 3191 | 43191 | Circ12NavideznaMoc_III
TPVCirc12NicelniTok | LONG | IOD_TPV_TCP | 3193 | 43193 | Circ12NicelniTok
TPVCirc12PowerFactor_III | LONG | IOD_TPV_TCP | 3195 | 43195 | Circ12PowerFactor_III
TPVCirc12PowerFactor_L1 | LONG | IOD_TPV_TCP | 3197 | 43197 | Circ12PowerFactor_L1
TPVCirc12PowerFactor_L2 | LONG | IOD_TPV_TCP | 3199 | 43199 | Circ12PowerFactor_L2
TPVCirc12PowerFactor_L3 | LONG | IOD_TPV_TCP | 3201 | 43201 | Circ12PowerFactor_L3
TPVCirc12THDI_L1 | LONG | IOD_TPV_TCP | 3203 | 43203 | Circ12THDI_L1
TPVCirc12THDI_L2 | LONG | IOD_TPV_TCP | 3205 | 43205 | Circ12THDI_L2
TPVCirc12THDI_L3 | LONG | IOD_TPV_TCP | 3207 | 43207 | Circ12THDI_L3
TPVCirc12THDV_L1 | LONG | IOD_TPV_TCP | 3209 | 43209 | Circ12THDV_L1
TPVCirc12THDV_L2 | LONG | IOD_TPV_TCP | 3211 | 43211 | Circ12THDV_L2
TPVCirc12THDV_L3 | LONG | IOD_TPV_TCP | 3213 | 43213 | Circ12THDV_L3
TPVCirc12Tok_L1 | LONG | IOD_TPV_TCP | 3215 | 43215 | Circ12Tok_L1
TPVCirc12Tok_L2 | LONG | IOD_TPV_TCP | 3217 | 43217 | Circ12Tok_L2
TPVCirc12Tok_L3 | LONG | IOD_TPV_TCP | 3219 | 43219 | Circ12Tok_L3
TPVCirc12TokPovprecje_III | LONG | IOD_TPV_TCP | 3221 | 43221 | Circ12TokPovprecje_III
TPVCirc13CosFi_III | LONG | IOD_TPV_TCP | 3223 | 43223 | Circ13CosFi_III
TPVCirc13DelovnaEnergija | LONG | IOD_TPV_TCP | 3225 | 43225 | Circ13DelovnaEnergija
TPVCirc13DelovnaMoc_III | LONG | IOD_TPV_TCP | 3227 | 43227 | Circ13DelovnaMoc_III
TPVCirc13DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 3229 | 43229 | Circ13DelovnaMoc_L1
TPVCirc13DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 3231 | 43231 | Circ13DelovnaMoc_L2
TPVCirc13DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 3233 | 43233 | Circ13DelovnaMoc_L3
TPVCirc13Frekvenca_L1 | LONG | IOD_TPV_TCP | 3235 | 43235 | Circ13Frekvenca_L1
TPVCirc13InduktivnaEnergija | LONG | IOD_TPV_TCP | 3237 | 43237 | Circ13InduktivnaEnergija
TPVCirc13InduktivnaMoc_III | LONG | IOD_TPV_TCP | 3239 | 43239 | Circ13InduktivnaMoc_III
TPVCirc13JalovaMoc_L1 | LONG | IOD_TPV_TCP | 3241 | 43241 | Circ13JalovaMoc_L1
TPVCirc13JalovaMoc_L2 | LONG | IOD_TPV_TCP | 3243 | 43243 | Circ13JalovaMoc_L2
TPVCirc13JalovaMoc_L3 | LONG | IOD_TPV_TCP | 3245 | 43245 | Circ13JalovaMoc_L3
TPVCirc13KapacitivnaEnergija | LONG | IOD_TPV_TCP | 3247 | 43247 | Circ13KapacitivnaEnergija
TPVCirc13KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 3249 | 43249 | Circ13KapacitivnaMoc_III
TPVCirc13MaximumDemand | LONG | IOD_TPV_TCP | 3251 | 43251 | Circ13MaximumDemand
TPVCirc13Napetost_L1_L2 | LONG | IOD_TPV_TCP | 3253 | 43253 | Circ13Napetost_L1_L2
TPVCirc13Napetost_L1_N | LONG | IOD_TPV_TCP | 3255 | 43255 | Circ13Napetost_L1_N
TPVCirc13Napetost_L2_L3 | LONG | IOD_TPV_TCP | 3257 | 43257 | Circ13Napetost_L2_L3
TPVCirc13Napetost_L2_N | LONG | IOD_TPV_TCP | 3259 | 43259 | Circ13Napetost_L2_N
TPVCirc13Napetost_L3_L1 | LONG | IOD_TPV_TCP | 3261 | 43261 | Circ13Napetost_L3_L1
TPVCirc13Napetost_L3_N | LONG | IOD_TPV_TCP | 3263 | 43263 | Circ13Napetost_L3_N
TPVCirc13NavideznaMoc_III | LONG | IOD_TPV_TCP | 3265 | 43265 | Circ13NavideznaMoc_III
TPVCirc13NicelniTok | LONG | IOD_TPV_TCP | 3267 | 43267 | Circ13NicelniTok
TPVCirc13PowerFactor_III | LONG | IOD_TPV_TCP | 3269 | 43269 | Circ13PowerFactor_III
TPVCirc13PowerFactor_L1 | LONG | IOD_TPV_TCP | 3271 | 43271 | Circ13PowerFactor_L1
TPVCirc13PowerFactor_L2 | LONG | IOD_TPV_TCP | 3273 | 43273 | Circ13PowerFactor_L2
TPVCirc13PowerFactor_L3 | LONG | IOD_TPV_TCP | 3275 | 43275 | Circ13PowerFactor_L3
TPVCirc13THDI_L1 | LONG | IOD_TPV_TCP | 3277 | 43277 | Circ13THDI_L1
TPVCirc13THDI_L2 | LONG | IOD_TPV_TCP | 3279 | 43279 | Circ13THDI_L2
TPVCirc13THDI_L3 | LONG | IOD_TPV_TCP | 3281 | 43281 | Circ13THDI_L3
TPVCirc13THDV_L1 | LONG | IOD_TPV_TCP | 3283 | 43283 | Circ13THDV_L1
TPVCirc13THDV_L2 | LONG | IOD_TPV_TCP | 3285 | 43285 | Circ13THDV_L2
TPVCirc13THDV_L3 | LONG | IOD_TPV_TCP | 3287 | 43287 | Circ13THDV_L3
TPVCirc13Tok_L1 | LONG | IOD_TPV_TCP | 3289 | 43289 | Circ13Tok_L1
TPVCirc13Tok_L2 | LONG | IOD_TPV_TCP | 3291 | 43291 | Circ13Tok_L2
TPVCirc13Tok_L3 | LONG | IOD_TPV_TCP | 3293 | 43293 | Circ13Tok_L3
TPVCirc13TokPovprecje_III | LONG | IOD_TPV_TCP | 3295 | 43295 | Circ13TokPovprecje_III
TPVCirc14CosFi_III | LONG | IOD_TPV_TCP | 3297 | 43297 | Circ14CosFi_III
TPVCirc14DelovnaEnergija | LONG | IOD_TPV_TCP | 3299 | 43299 | Circ14DelovnaEnergija
TPVCirc14DelovnaMoc_III | LONG | IOD_TPV_TCP | 3301 | 43301 | Circ14DelovnaMoc_III
TPVCirc14DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 3303 | 43303 | Circ14DelovnaMoc_L1
TPVCirc14DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 3305 | 43305 | Circ14DelovnaMoc_L2
TPVCirc14DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 3307 | 43307 | Circ14DelovnaMoc_L3
TPVCirc14Frekvenca_L1 | LONG | IOD_TPV_TCP | 3309 | 43309 | Circ14Frekvenca_L1
TPVCirc14InduktivnaEnergija | LONG | IOD_TPV_TCP | 3311 | 43311 | Circ14InduktivnaEnergija
TPVCirc14InduktivnaMoc_III | LONG | IOD_TPV_TCP | 3313 | 43313 | Circ14InduktivnaMoc_III
TPVCirc14JalovaMoc_L1 | LONG | IOD_TPV_TCP | 3315 | 43315 | Circ14JalovaMoc_L1
TPVCirc14JalovaMoc_L2 | LONG | IOD_TPV_TCP | 3317 | 43317 | Circ14JalovaMoc_L2
TPVCirc14JalovaMoc_L3 | LONG | IOD_TPV_TCP | 3319 | 43319 | Circ14JalovaMoc_L3
TPVCirc14KapacitivnaEnergija | LONG | IOD_TPV_TCP | 3321 | 43321 | Circ14KapacitivnaEnergija
TPVCirc14KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 3323 | 43323 | Circ14KapacitivnaMoc_III
TPVCirc14MaximumDemand | LONG | IOD_TPV_TCP | 3325 | 43325 | Circ14MaximumDemand
TPVCirc14Napetost_L1_L2 | LONG | IOD_TPV_TCP | 3327 | 43327 | Circ14Napetost_L1_L2
TPVCirc14Napetost_L1_N | LONG | IOD_TPV_TCP | 3329 | 43329 | Circ14Napetost_L1_N
TPVCirc14Napetost_L2_L3 | LONG | IOD_TPV_TCP | 3331 | 43331 | Circ14Napetost_L2_L3
TPVCirc14Napetost_L2_N | LONG | IOD_TPV_TCP | 3333 | 43333 | Circ14Napetost_L2_N
TPVCirc14Napetost_L3_L1 | LONG | IOD_TPV_TCP | 3335 | 43335 | Circ14Napetost_L3_L1
TPVCirc14Napetost_L3_N | LONG | IOD_TPV_TCP | 3337 | 43337 | Circ14Napetost_L3_N
TPVCirc14NavideznaMoc_III | LONG | IOD_TPV_TCP | 3339 | 43339 | Circ14NavideznaMoc_III
TPVCirc14NicelniTok | LONG | IOD_TPV_TCP | 3341 | 43341 | Circ14NicelniTok
TPVCirc14PowerFactor_III | LONG | IOD_TPV_TCP | 3343 | 43343 | Circ14PowerFactor_III
TPVCirc14PowerFactor_L1 | LONG | IOD_TPV_TCP | 3345 | 43345 | Circ14PowerFactor_L1
TPVCirc14PowerFactor_L2 | LONG | IOD_TPV_TCP | 3347 | 43347 | Circ14PowerFactor_L2
TPVCirc14PowerFactor_L3 | LONG | IOD_TPV_TCP | 3349 | 43349 | Circ14PowerFactor_L3
TPVCirc14THDI_L1 | LONG | IOD_TPV_TCP | 3351 | 43351 | Circ14THDI_L1
TPVCirc14THDI_L2 | LONG | IOD_TPV_TCP | 3353 | 43353 | Circ14THDI_L2
TPVCirc14THDI_L3 | LONG | IOD_TPV_TCP | 3355 | 43355 | Circ14THDI_L3
TPVCirc14THDV_L1 | LONG | IOD_TPV_TCP | 3357 | 43357 | Circ14THDV_L1
TPVCirc14THDV_L2 | LONG | IOD_TPV_TCP | 3359 | 43359 | Circ14THDV_L2
TPVCirc14THDV_L3 | LONG | IOD_TPV_TCP | 3361 | 43361 | Circ14THDV_L3
TPVCirc14Tok_L1 | LONG | IOD_TPV_TCP | 3363 | 43363 | Circ14Tok_L1
TPVCirc14Tok_L2 | LONG | IOD_TPV_TCP | 3365 | 43365 | Circ14Tok_L2
TPVCirc14Tok_L3 | LONG | IOD_TPV_TCP | 3367 | 43367 | Circ14Tok_L3
TPVCirc14TokPovprecje_III | LONG | IOD_TPV_TCP | 3369 | 43369 | Circ14TokPovprecje_III
TPVCirc15CosFi_III | LONG | IOD_TPV_TCP | 3371 | 43371 | Circ15CosFi_III
TPVCirc15DelovnaEnergija | LONG | IOD_TPV_TCP | 3373 | 43373 | Circ15DelovnaEnergija
TPVCirc15DelovnaMoc_III | LONG | IOD_TPV_TCP | 3375 | 43375 | Circ15DelovnaMoc_III
TPVCirc15DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 3377 | 43377 | Circ15DelovnaMoc_L1
TPVCirc15DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 3379 | 43379 | Circ15DelovnaMoc_L2
TPVCirc15DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 3381 | 43381 | Circ15DelovnaMoc_L3
TPVCirc15Frekvenca_L1 | LONG | IOD_TPV_TCP | 3383 | 43383 | Circ15Frekvenca_L1
TPVCirc15InduktivnaEnergija | LONG | IOD_TPV_TCP | 3385 | 43385 | Circ15InduktivnaEnergija
TPVCirc15InduktivnaMoc_III | LONG | IOD_TPV_TCP | 3387 | 43387 | Circ15InduktivnaMoc_III
TPVCirc15JalovaMoc_L1 | LONG | IOD_TPV_TCP | 3389 | 43389 | Circ15JalovaMoc_L1
TPVCirc15JalovaMoc_L2 | LONG | IOD_TPV_TCP | 3391 | 43391 | Circ15JalovaMoc_L2
TPVCirc15JalovaMoc_L3 | LONG | IOD_TPV_TCP | 3393 | 43393 | Circ15JalovaMoc_L3
TPVCirc15KapacitivnaEnergija | LONG | IOD_TPV_TCP | 3395 | 43395 | Circ15KapacitivnaEnergija
TPVCirc15KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 3397 | 43397 | Circ15KapacitivnaMoc_III
TPVCirc15MaximumDemand | LONG | IOD_TPV_TCP | 3399 | 43399 | Circ15MaximumDemand
TPVCirc15Napetost_L1_L2 | LONG | IOD_TPV_TCP | 3401 | 43401 | Circ15Napetost_L1_L2
TPVCirc15Napetost_L1_N | LONG | IOD_TPV_TCP | 3403 | 43403 | Circ15Napetost_L1_N
TPVCirc15Napetost_L2_L3 | LONG | IOD_TPV_TCP | 3405 | 43405 | Circ15Napetost_L2_L3
TPVCirc15Napetost_L2_N | LONG | IOD_TPV_TCP | 3407 | 43407 | Circ15Napetost_L2_N
TPVCirc15Napetost_L3_L1 | LONG | IOD_TPV_TCP | 3409 | 43409 | Circ15Napetost_L3_L1
TPVCirc15Napetost_L3_N | LONG | IOD_TPV_TCP | 3411 | 43411 | Circ15Napetost_L3_N
TPVCirc15NavideznaMoc_III | LONG | IOD_TPV_TCP | 3413 | 43413 | Circ15NavideznaMoc_III
TPVCirc15NicelniTok | LONG | IOD_TPV_TCP | 3415 | 43415 | Circ15NicelniTok
TPVCirc15PowerFactor_III | LONG | IOD_TPV_TCP | 3417 | 43417 | Circ15PowerFactor_III
TPVCirc15PowerFactor_L1 | LONG | IOD_TPV_TCP | 3419 | 43419 | Circ15PowerFactor_L1
TPVCirc15PowerFactor_L2 | LONG | IOD_TPV_TCP | 3421 | 43421 | Circ15PowerFactor_L2
TPVCirc15PowerFactor_L3 | LONG | IOD_TPV_TCP | 3423 | 43423 | Circ15PowerFactor_L3
TPVCirc15THDI_L1 | LONG | IOD_TPV_TCP | 3425 | 43425 | Circ15THDI_L1
TPVCirc15THDI_L2 | LONG | IOD_TPV_TCP | 3427 | 43427 | Circ15THDI_L2
TPVCirc15THDI_L3 | LONG | IOD_TPV_TCP | 3429 | 43429 | Circ15THDI_L3
TPVCirc15THDV_L1 | LONG | IOD_TPV_TCP | 3431 | 43431 | Circ15THDV_L1
TPVCirc15THDV_L2 | LONG | IOD_TPV_TCP | 3433 | 43433 | Circ15THDV_L2
TPVCirc15THDV_L3 | LONG | IOD_TPV_TCP | 3435 | 43435 | Circ15THDV_L3
TPVCirc15Tok_L1 | LONG | IOD_TPV_TCP | 3437 | 43437 | Circ15Tok_L1
TPVCirc15Tok_L2 | LONG | IOD_TPV_TCP | 3439 | 43439 | Circ15Tok_L2
TPVCirc15Tok_L3 | LONG | IOD_TPV_TCP | 3441 | 43441 | Circ15Tok_L3
TPVCirc15TokPovprecje_III | LONG | IOD_TPV_TCP | 3443 | 43443 | Circ15TokPovprecje_III
TPVCirc16CosFi_III | LONG | IOD_TPV_TCP | 3445 | 43445 | Circ16CosFi_III
TPVCirc16DelovnaEnergija | LONG | IOD_TPV_TCP | 3447 | 43447 | Circ16DelovnaEnergija
TPVCirc16DelovnaMoc_III | LONG | IOD_TPV_TCP | 3449 | 43449 | Circ16DelovnaMoc_III
TPVCirc16DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 3451 | 43451 | Circ16DelovnaMoc_L1
TPVCirc16DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 3453 | 43453 | Circ16DelovnaMoc_L2
TPVCirc16DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 3455 | 43455 | Circ16DelovnaMoc_L3
TPVCirc16Frekvenca_L1 | LONG | IOD_TPV_TCP | 3457 | 43457 | Circ16Frekvenca_L1
TPVCirc16InduktivnaEnergija | LONG | IOD_TPV_TCP | 3459 | 43459 | Circ16InduktivnaEnergija
TPVCirc16InduktivnaMoc_III | LONG | IOD_TPV_TCP | 3461 | 43461 | Circ16InduktivnaMoc_III
TPVCirc16JalovaMoc_L1 | LONG | IOD_TPV_TCP | 3463 | 43463 | Circ16JalovaMoc_L1
TPVCirc16JalovaMoc_L2 | LONG | IOD_TPV_TCP | 3465 | 43465 | Circ16JalovaMoc_L2
TPVCirc16JalovaMoc_L3 | LONG | IOD_TPV_TCP | 3467 | 43467 | Circ16JalovaMoc_L3
TPVCirc16KapacitivnaEnergija | LONG | IOD_TPV_TCP | 3469 | 43469 | Circ16KapacitivnaEnergija
TPVCirc16KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 3471 | 43471 | Circ16KapacitivnaMoc_III
TPVCirc16MaximumDemand | LONG | IOD_TPV_TCP | 3473 | 43473 | Circ16MaximumDemand
TPVCirc16Napetost_L1_L2 | LONG | IOD_TPV_TCP | 3475 | 43475 | Circ16Napetost_L1_L2
TPVCirc16Napetost_L1_N | LONG | IOD_TPV_TCP | 3477 | 43477 | Circ16Napetost_L1_N
TPVCirc16Napetost_L2_L3 | LONG | IOD_TPV_TCP | 3479 | 43479 | Circ16Napetost_L2_L3
TPVCirc16Napetost_L2_N | LONG | IOD_TPV_TCP | 3481 | 43481 | Circ16Napetost_L2_N
TPVCirc16Napetost_L3_L1 | LONG | IOD_TPV_TCP | 3483 | 43483 | Circ16Napetost_L3_L1
TPVCirc16Napetost_L3_N | LONG | IOD_TPV_TCP | 3485 | 43485 | Circ16Napetost_L3_N
TPVCirc16NavideznaMoc_III | LONG | IOD_TPV_TCP | 3487 | 43487 | Circ16NavideznaMoc_III
TPVCirc16NicelniTok | LONG | IOD_TPV_TCP | 3489 | 43489 | Circ16NicelniTok
TPVCirc16PowerFactor_III | LONG | IOD_TPV_TCP | 3491 | 43491 | Circ16PowerFactor_III
TPVCirc16PowerFactor_L1 | LONG | IOD_TPV_TCP | 3493 | 43493 | Circ16PowerFactor_L1
TPVCirc16PowerFactor_L2 | LONG | IOD_TPV_TCP | 3495 | 43495 | Circ16PowerFactor_L2
TPVCirc16PowerFactor_L3 | LONG | IOD_TPV_TCP | 3497 | 43497 | Circ16PowerFactor_L3
TPVCirc16THDI_L1 | LONG | IOD_TPV_TCP | 3499 | 43499 | Circ16THDI_L1
TPVCirc16THDI_L2 | LONG | IOD_TPV_TCP | 3501 | 43501 | Circ16THDI_L2
TPVCirc16THDI_L3 | LONG | IOD_TPV_TCP | 3503 | 43503 | Circ16THDI_L3
TPVCirc16THDV_L1 | LONG | IOD_TPV_TCP | 3505 | 43505 | Circ16THDV_L1
TPVCirc16THDV_L2 | LONG | IOD_TPV_TCP | 3507 | 43507 | Circ16THDV_L2
TPVCirc16THDV_L3 | LONG | IOD_TPV_TCP | 3509 | 43509 | Circ16THDV_L3
TPVCirc16Tok_L1 | LONG | IOD_TPV_TCP | 3511 | 43511 | Circ16Tok_L1
TPVCirc16Tok_L2 | LONG | IOD_TPV_TCP | 3513 | 43513 | Circ16Tok_L2
TPVCirc16Tok_L3 | LONG | IOD_TPV_TCP | 3515 | 43515 | Circ16Tok_L3
TPVCirc16TokPovprecje_III | LONG | IOD_TPV_TCP | 3517 | 43517 | Circ16TokPovprecje_III
TPVCirc17CosFi_III | LONG | IOD_TPV_TCP | 3519 | 43519 | Circ17CosFi_III
TPVCirc17DelovnaEnergija | LONG | IOD_TPV_TCP | 3521 | 43521 | Circ17DelovnaEnergija
TPVCirc17DelovnaMoc_III | LONG | IOD_TPV_TCP | 3523 | 43523 | Circ17DelovnaMoc_III
TPVCirc17DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 3525 | 43525 | Circ17DelovnaMoc_L1
TPVCirc17DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 3527 | 43527 | Circ17DelovnaMoc_L2
TPVCirc17DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 3529 | 43529 | Circ17DelovnaMoc_L3
TPVCirc17Frekvenca_L1 | LONG | IOD_TPV_TCP | 3531 | 43531 | Circ17Frekvenca_L1
TPVCirc17InduktivnaEnergija | LONG | IOD_TPV_TCP | 3533 | 43533 | Circ17InduktivnaEnergija
TPVCirc17InduktivnaMoc_III | LONG | IOD_TPV_TCP | 3535 | 43535 | Circ17InduktivnaMoc_III
TPVCirc17JalovaMoc_L1 | LONG | IOD_TPV_TCP | 3537 | 43537 | Circ17JalovaMoc_L1
TPVCirc17JalovaMoc_L2 | LONG | IOD_TPV_TCP | 3539 | 43539 | Circ17JalovaMoc_L2
TPVCirc17JalovaMoc_L3 | LONG | IOD_TPV_TCP | 3541 | 43541 | Circ17JalovaMoc_L3
TPVCirc17KapacitivnaEnergija | LONG | IOD_TPV_TCP | 3543 | 43543 | Circ17KapacitivnaEnergija
TPVCirc17KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 3545 | 43545 | Circ17KapacitivnaMoc_III
TPVCirc17MaximumDemand | LONG | IOD_TPV_TCP | 3547 | 43547 | Circ17MaximumDemand
TPVCirc17Napetost_L1_L2 | LONG | IOD_TPV_TCP | 3549 | 43549 | Circ17Napetost_L1_L2
TPVCirc17Napetost_L1_N | LONG | IOD_TPV_TCP | 3551 | 43551 | Circ17Napetost_L1_N
TPVCirc17Napetost_L2_L3 | LONG | IOD_TPV_TCP | 3553 | 43553 | Circ17Napetost_L2_L3
TPVCirc17Napetost_L2_N | LONG | IOD_TPV_TCP | 3555 | 43555 | Circ17Napetost_L2_N
TPVCirc17Napetost_L3_L1 | LONG | IOD_TPV_TCP | 3557 | 43557 | Circ17Napetost_L3_L1
TPVCirc17Napetost_L3_N | LONG | IOD_TPV_TCP | 3559 | 43559 | Circ17Napetost_L3_N
TPVCirc17NavideznaMoc_III | LONG | IOD_TPV_TCP | 3561 | 43561 | Circ17NavideznaMoc_III
TPVCirc17NicelniTok | LONG | IOD_TPV_TCP | 3563 | 43563 | Circ17NicelniTok
TPVCirc17PowerFactor_III | LONG | IOD_TPV_TCP | 3565 | 43565 | Circ17PowerFactor_III
TPVCirc17PowerFactor_L1 | LONG | IOD_TPV_TCP | 3567 | 43567 | Circ17PowerFactor_L1
TPVCirc17PowerFactor_L2 | LONG | IOD_TPV_TCP | 3569 | 43569 | Circ17PowerFactor_L2
TPVCirc17PowerFactor_L3 | LONG | IOD_TPV_TCP | 3571 | 43571 | Circ17PowerFactor_L3
TPVCirc17THDI_L1 | LONG | IOD_TPV_TCP | 3573 | 43573 | Circ17THDI_L1
TPVCirc17THDI_L2 | LONG | IOD_TPV_TCP | 3575 | 43575 | Circ17THDI_L2
TPVCirc17THDI_L3 | LONG | IOD_TPV_TCP | 3577 | 43577 | Circ17THDI_L3
TPVCirc17THDV_L1 | LONG | IOD_TPV_TCP | 3579 | 43579 | Circ17THDV_L1
TPVCirc17THDV_L2 | LONG | IOD_TPV_TCP | 3581 | 43581 | Circ17THDV_L2
TPVCirc17THDV_L3 | LONG | IOD_TPV_TCP | 3583 | 43583 | Circ17THDV_L3
TPVCirc17Tok_L1 | LONG | IOD_TPV_TCP | 3585 | 43585 | Circ17Tok_L1
TPVCirc17Tok_L2 | LONG | IOD_TPV_TCP | 3587 | 43587 | Circ17Tok_L2
TPVCirc17Tok_L3 | LONG | IOD_TPV_TCP | 3589 | 43589 | Circ17Tok_L3
TPVCirc17TokPovprecje_III | LONG | IOD_TPV_TCP | 3591 | 43591 | Circ17TokPovprecje_III
TPVCirc18CosFi_III | LONG | IOD_TPV_TCP | 3593 | 43593 | Circ18CosFi_III
TPVCirc18DelovnaEnergija | LONG | IOD_TPV_TCP | 3595 | 43595 | Circ18DelovnaEnergija
TPVCirc18DelovnaMoc_III | LONG | IOD_TPV_TCP | 3597 | 43597 | Circ18DelovnaMoc_III
TPVCirc18DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 3599 | 43599 | Circ18DelovnaMoc_L1
TPVCirc18DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 3601 | 43601 | Circ18DelovnaMoc_L2
TPVCirc18DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 3603 | 43603 | Circ18DelovnaMoc_L3
TPVCirc18Frekvenca_L1 | LONG | IOD_TPV_TCP | 3605 | 43605 | Circ18Frekvenca_L1
TPVCirc18InduktivnaEnergija | LONG | IOD_TPV_TCP | 3607 | 43607 | Circ18InduktivnaEnergija
TPVCirc18InduktivnaMoc_III | LONG | IOD_TPV_TCP | 3609 | 43609 | Circ18InduktivnaMoc_III
TPVCirc18JalovaMoc_L1 | LONG | IOD_TPV_TCP | 3611 | 43611 | Circ18JalovaMoc_L1
TPVCirc18JalovaMoc_L2 | LONG | IOD_TPV_TCP | 3613 | 43613 | Circ18JalovaMoc_L2
TPVCirc18JalovaMoc_L3 | LONG | IOD_TPV_TCP | 3615 | 43615 | Circ18JalovaMoc_L3
TPVCirc18KapacitivnaEnergija | LONG | IOD_TPV_TCP | 3617 | 43617 | Circ18KapacitivnaEnergija
TPVCirc18KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 3619 | 43619 | Circ18KapacitivnaMoc_III
TPVCirc18MaximumDemand | LONG | IOD_TPV_TCP | 3621 | 43621 | Circ18MaximumDemand
TPVCirc18Napetost_L1_L2 | LONG | IOD_TPV_TCP | 3623 | 43623 | Circ18Napetost_L1_L2
TPVCirc18Napetost_L1_N | LONG | IOD_TPV_TCP | 3625 | 43625 | Circ18Napetost_L1_N
TPVCirc18Napetost_L2_L3 | LONG | IOD_TPV_TCP | 3627 | 43627 | Circ18Napetost_L2_L3
TPVCirc18Napetost_L2_N | LONG | IOD_TPV_TCP | 3629 | 43629 | Circ18Napetost_L2_N
TPVCirc18Napetost_L3_L1 | LONG | IOD_TPV_TCP | 3631 | 43631 | Circ18Napetost_L3_L1
TPVCirc18Napetost_L3_N | LONG | IOD_TPV_TCP | 3633 | 43633 | Circ18Napetost_L3_N
TPVCirc18NavideznaMoc_III | LONG | IOD_TPV_TCP | 3635 | 43635 | Circ18NavideznaMoc_III
TPVCirc18NicelniTok | LONG | IOD_TPV_TCP | 3637 | 43637 | Circ18NicelniTok
TPVCirc18PowerFactor_III | LONG | IOD_TPV_TCP | 3639 | 43639 | Circ18PowerFactor_III
TPVCirc18PowerFactor_L1 | LONG | IOD_TPV_TCP | 3641 | 43641 | Circ18PowerFactor_L1
TPVCirc18PowerFactor_L2 | LONG | IOD_TPV_TCP | 3643 | 43643 | Circ18PowerFactor_L2
TPVCirc18PowerFactor_L3 | LONG | IOD_TPV_TCP | 3645 | 43645 | Circ18PowerFactor_L3
TPVCirc18THDI_L1 | LONG | IOD_TPV_TCP | 3647 | 43647 | Circ18THDI_L1
TPVCirc18THDI_L2 | LONG | IOD_TPV_TCP | 3649 | 43649 | Circ18THDI_L2
TPVCirc18THDI_L3 | LONG | IOD_TPV_TCP | 3651 | 43651 | Circ18THDI_L3
TPVCirc18THDV_L1 | LONG | IOD_TPV_TCP | 3653 | 43653 | Circ18THDV_L1
TPVCirc18THDV_L2 | LONG | IOD_TPV_TCP | 3655 | 43655 | Circ18THDV_L2
TPVCirc18THDV_L3 | LONG | IOD_TPV_TCP | 3657 | 43657 | Circ18THDV_L3
TPVCirc18Tok_L1 | LONG | IOD_TPV_TCP | 3659 | 43659 | Circ18Tok_L1
TPVCirc18Tok_L2 | LONG | IOD_TPV_TCP | 3661 | 43661 | Circ18Tok_L2
TPVCirc18Tok_L3 | LONG | IOD_TPV_TCP | 3663 | 43663 | Circ18Tok_L3
TPVCirc18TokPovprecje_III | LONG | IOD_TPV_TCP | 3665 | 43665 | Circ18TokPovprecje_III
TPVCirc19CosFi_III | LONG | IOD_TPV_TCP | 3667 | 43667 | Circ19CosFi_III
TPVCirc19DelovnaEnergija | LONG | IOD_TPV_TCP | 3669 | 43669 | Circ19DelovnaEnergija
TPVCirc19DelovnaMoc_III | LONG | IOD_TPV_TCP | 3671 | 43671 | Circ19DelovnaMoc_III
TPVCirc19DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 3673 | 43673 | Circ19DelovnaMoc_L1
TPVCirc19DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 3675 | 43675 | Circ19DelovnaMoc_L2
TPVCirc19DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 3677 | 43677 | Circ19DelovnaMoc_L3
TPVCirc19Frekvenca_L1 | LONG | IOD_TPV_TCP | 3679 | 43679 | Circ19Frekvenca_L1
TPVCirc19InduktivnaEnergija | LONG | IOD_TPV_TCP | 3681 | 43681 | Circ19InduktivnaEnergija
TPVCirc19InduktivnaMoc_III | LONG | IOD_TPV_TCP | 3683 | 43683 | Circ19InduktivnaMoc_III
TPVCirc19JalovaMoc_L1 | LONG | IOD_TPV_TCP | 3685 | 43685 | Circ19JalovaMoc_L1
TPVCirc19JalovaMoc_L2 | LONG | IOD_TPV_TCP | 3687 | 43687 | Circ19JalovaMoc_L2
TPVCirc19JalovaMoc_L3 | LONG | IOD_TPV_TCP | 3689 | 43689 | Circ19JalovaMoc_L3
TPVCirc19KapacitivnaEnergija | LONG | IOD_TPV_TCP | 3691 | 43691 | Circ19KapacitivnaEnergija
TPVCirc19KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 3693 | 43693 | Circ19KapacitivnaMoc_III
TPVCirc19MaximumDemand | LONG | IOD_TPV_TCP | 3695 | 43695 | Circ19MaximumDemand
TPVCirc19Napetost_L1_L2 | LONG | IOD_TPV_TCP | 3697 | 43697 | Circ19Napetost_L1_L2
TPVCirc19Napetost_L1_N | LONG | IOD_TPV_TCP | 3699 | 43699 | Circ19Napetost_L1_N
TPVCirc19Napetost_L2_L3 | LONG | IOD_TPV_TCP | 3701 | 43701 | Circ19Napetost_L2_L3
TPVCirc19Napetost_L2_N | LONG | IOD_TPV_TCP | 3703 | 43703 | Circ19Napetost_L2_N
TPVCirc19Napetost_L3_L1 | LONG | IOD_TPV_TCP | 3705 | 43705 | Circ19Napetost_L3_L1
TPVCirc19Napetost_L3_N | LONG | IOD_TPV_TCP | 3707 | 43707 | Circ19Napetost_L3_N
TPVCirc19NavideznaMoc_III | LONG | IOD_TPV_TCP | 3709 | 43709 | Circ19NavideznaMoc_III
TPVCirc19NicelniTok | LONG | IOD_TPV_TCP | 3711 | 43711 | Circ19NicelniTok
TPVCirc19PowerFactor_III | LONG | IOD_TPV_TCP | 3713 | 43713 | Circ19PowerFactor_III
TPVCirc19PowerFactor_L1 | LONG | IOD_TPV_TCP | 3715 | 43715 | Circ19PowerFactor_L1
TPVCirc19PowerFactor_L2 | LONG | IOD_TPV_TCP | 3717 | 43717 | Circ19PowerFactor_L2
TPVCirc19PowerFactor_L3 | LONG | IOD_TPV_TCP | 3719 | 43719 | Circ19PowerFactor_L3
TPVCirc19THDI_L1 | LONG | IOD_TPV_TCP | 3721 | 43721 | Circ19THDI_L1
TPVCirc19THDI_L2 | LONG | IOD_TPV_TCP | 3723 | 43723 | Circ19THDI_L2
TPVCirc19THDI_L3 | LONG | IOD_TPV_TCP | 3725 | 43725 | Circ19THDI_L3
TPVCirc19THDV_L1 | LONG | IOD_TPV_TCP | 3727 | 43727 | Circ19THDV_L1
TPVCirc19THDV_L2 | LONG | IOD_TPV_TCP | 3729 | 43729 | Circ19THDV_L2
TPVCirc19THDV_L3 | LONG | IOD_TPV_TCP | 3731 | 43731 | Circ19THDV_L3
TPVCirc19Tok_L1 | LONG | IOD_TPV_TCP | 3733 | 43733 | Circ19Tok_L1
TPVCirc19Tok_L2 | LONG | IOD_TPV_TCP | 3735 | 43735 | Circ19Tok_L2
TPVCirc19Tok_L3 | LONG | IOD_TPV_TCP | 3737 | 43737 | Circ19Tok_L3
TPVCirc19TokPovprecje_III | LONG | IOD_TPV_TCP | 3739 | 43739 | Circ19TokPovprecje_III
TPVCirc1CosFi_III | LONG | IOD_TPV_TCP | 3741 | 43741 | Circ1CosFi_III
TPVCirc1DelovnaEnergija | LONG | IOD_TPV_TCP | 3743 | 43743 | Circ1DelovnaEnergija
TPVCirc1DelovnaMoc_III | LONG | IOD_TPV_TCP | 3745 | 43745 | Circ1DelovnaMoc_III
TPVCirc1DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 3747 | 43747 | Circ1DelovnaMoc_L1
TPVCirc1DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 3749 | 43749 | Circ1DelovnaMoc_L2
TPVCirc1DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 3751 | 43751 | Circ1DelovnaMoc_L3
TPVCirc1Frekvenca_L1 | LONG | IOD_TPV_TCP | 3753 | 43753 | Circ1Frekvenca_L1
TPVCirc1InduktivnaEnergija | LONG | IOD_TPV_TCP | 3755 | 43755 | Circ1InduktivnaEnergija
TPVCirc1InduktivnaMoc_III | LONG | IOD_TPV_TCP | 3757 | 43757 | Circ1InduktivnaMoc_III
TPVCirc1JalovaMoc_L1 | LONG | IOD_TPV_TCP | 3759 | 43759 | Circ1JalovaMoc_L1
TPVCirc1JalovaMoc_L2 | LONG | IOD_TPV_TCP | 3761 | 43761 | Circ1JalovaMoc_L2
TPVCirc1JalovaMoc_L3 | LONG | IOD_TPV_TCP | 3763 | 43763 | Circ1JalovaMoc_L3
TPVCirc1KapacitivnaEnergija | LONG | IOD_TPV_TCP | 3765 | 43765 | Circ1KapacitivnaEnergija
TPVCirc1KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 3767 | 43767 | Circ1KapacitivnaMoc_III
TPVCirc1MaximumDemand | LONG | IOD_TPV_TCP | 3769 | 43769 | Circ1MaximumDemand
TPVCirc1Napetost_L1_L2 | LONG | IOD_TPV_TCP | 3771 | 43771 | Circ1Napetost_L1_L2
TPVCirc1Napetost_L1_N | LONG | IOD_TPV_TCP | 3773 | 43773 | Circ1Napetost_L1_N
TPVCirc1Napetost_L2_L3 | LONG | IOD_TPV_TCP | 3775 | 43775 | Circ1Napetost_L2_L3
TPVCirc1Napetost_L2_N | LONG | IOD_TPV_TCP | 3777 | 43777 | Circ1Napetost_L2_N
TPVCirc1Napetost_L3_L1 | LONG | IOD_TPV_TCP | 3779 | 43779 | Circ1Napetost_L3_L1
TPVCirc1Napetost_L3_N | LONG | IOD_TPV_TCP | 3781 | 43781 | Circ1Napetost_L3_N
TPVCirc1NavideznaMoc_III | LONG | IOD_TPV_TCP | 3783 | 43783 | Circ1NavideznaMoc_III
TPVCirc1NicelniTok | LONG | IOD_TPV_TCP | 3785 | 43785 | Circ1NicelniTok
TPVCirc1PowerFactor_III | LONG | IOD_TPV_TCP | 3787 | 43787 | Circ1PowerFactor_III
TPVCirc1PowerFactor_L1 | LONG | IOD_TPV_TCP | 3789 | 43789 | Circ1PowerFactor_L1
TPVCirc1PowerFactor_L2 | LONG | IOD_TPV_TCP | 3791 | 43791 | Circ1PowerFactor_L2
TPVCirc1PowerFactor_L3 | LONG | IOD_TPV_TCP | 3793 | 43793 | Circ1PowerFactor_L3
TPVCirc1THDI_L1 | LONG | IOD_TPV_TCP | 3795 | 43795 | Circ1THDI_L1
TPVCirc1THDI_L2 | LONG | IOD_TPV_TCP | 3797 | 43797 | Circ1THDI_L2
TPVCirc1THDI_L3 | LONG | IOD_TPV_TCP | 3799 | 43799 | Circ1THDI_L3
TPVCirc1THDV_L1 | LONG | IOD_TPV_TCP | 3801 | 43801 | Circ1THDV_L1
TPVCirc1THDV_L2 | LONG | IOD_TPV_TCP | 3803 | 43803 | Circ1THDV_L2
TPVCirc1THDV_L3 | LONG | IOD_TPV_TCP | 3805 | 43805 | Circ1THDV_L3
TPVCirc1Tok_L1 | LONG | IOD_TPV_TCP | 3807 | 43807 | Circ1Tok_L1
TPVCirc1Tok_L2 | LONG | IOD_TPV_TCP | 3809 | 43809 | Circ1Tok_L2
TPVCirc1Tok_L3 | LONG | IOD_TPV_TCP | 3811 | 43811 | Circ1Tok_L3
TPVCirc1TokPovprecje_III | LONG | IOD_TPV_TCP | 3813 | 43813 | Circ1TokPovprecje_III
TPVCirc20CosFi_III | LONG | IOD_TPV_TCP | 3815 | 43815 | Circ20CosFi_III
TPVCirc20DelovnaEnergija | LONG | IOD_TPV_TCP | 3817 | 43817 | Circ20DelovnaEnergija
TPVCirc20DelovnaMoc_III | LONG | IOD_TPV_TCP | 3819 | 43819 | Circ20DelovnaMoc_III
TPVCirc20DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 3821 | 43821 | Circ20DelovnaMoc_L1
TPVCirc20DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 3823 | 43823 | Circ20DelovnaMoc_L2
TPVCirc20DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 3825 | 43825 | Circ20DelovnaMoc_L3
TPVCirc20Frekvenca_L1 | LONG | IOD_TPV_TCP | 3827 | 43827 | Circ20Frekvenca_L1
TPVCirc20InduktivnaEnergija | LONG | IOD_TPV_TCP | 3829 | 43829 | Circ20InduktivnaEnergija
TPVCirc20InduktivnaMoc_III | LONG | IOD_TPV_TCP | 3831 | 43831 | Circ20InduktivnaMoc_III
TPVCirc20JalovaMoc_L1 | LONG | IOD_TPV_TCP | 3833 | 43833 | Circ20JalovaMoc_L1
TPVCirc20JalovaMoc_L2 | LONG | IOD_TPV_TCP | 3835 | 43835 | Circ20JalovaMoc_L2
TPVCirc20JalovaMoc_L3 | LONG | IOD_TPV_TCP | 3837 | 43837 | Circ20JalovaMoc_L3
TPVCirc20KapacitivnaEnergija | LONG | IOD_TPV_TCP | 3839 | 43839 | Circ20KapacitivnaEnergija
TPVCirc20KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 3841 | 43841 | Circ20KapacitivnaMoc_III
TPVCirc20MaximumDemand | LONG | IOD_TPV_TCP | 3843 | 43843 | Circ20MaximumDemand
TPVCirc20Napetost_L1_L2 | LONG | IOD_TPV_TCP | 3845 | 43845 | Circ20Napetost_L1_L2
TPVCirc20Napetost_L1_N | LONG | IOD_TPV_TCP | 3847 | 43847 | Circ20Napetost_L1_N
TPVCirc20Napetost_L2_L3 | LONG | IOD_TPV_TCP | 3849 | 43849 | Circ20Napetost_L2_L3
TPVCirc20Napetost_L2_N | LONG | IOD_TPV_TCP | 3851 | 43851 | Circ20Napetost_L2_N
TPVCirc20Napetost_L3_L1 | LONG | IOD_TPV_TCP | 3853 | 43853 | Circ20Napetost_L3_L1
TPVCirc20Napetost_L3_N | LONG | IOD_TPV_TCP | 3855 | 43855 | Circ20Napetost_L3_N
TPVCirc20NavideznaMoc_III | LONG | IOD_TPV_TCP | 3857 | 43857 | Circ20NavideznaMoc_III
TPVCirc20NicelniTok | LONG | IOD_TPV_TCP | 3859 | 43859 | Circ20NicelniTok
TPVCirc20PowerFactor_III | LONG | IOD_TPV_TCP | 3861 | 43861 | Circ20PowerFactor_III
TPVCirc20PowerFactor_L1 | LONG | IOD_TPV_TCP | 3863 | 43863 | Circ20PowerFactor_L1
TPVCirc20PowerFactor_L2 | LONG | IOD_TPV_TCP | 3865 | 43865 | Circ20PowerFactor_L2
TPVCirc20PowerFactor_L3 | LONG | IOD_TPV_TCP | 3867 | 43867 | Circ20PowerFactor_L3
TPVCirc20THDI_L1 | LONG | IOD_TPV_TCP | 3869 | 43869 | Circ20THDI_L1
TPVCirc20THDI_L2 | LONG | IOD_TPV_TCP | 3871 | 43871 | Circ20THDI_L2
TPVCirc20THDI_L3 | LONG | IOD_TPV_TCP | 3873 | 43873 | Circ20THDI_L3
TPVCirc20THDV_L1 | LONG | IOD_TPV_TCP | 3875 | 43875 | Circ20THDV_L1
TPVCirc20THDV_L2 | LONG | IOD_TPV_TCP | 3877 | 43877 | Circ20THDV_L2
TPVCirc20THDV_L3 | LONG | IOD_TPV_TCP | 3879 | 43879 | Circ20THDV_L3
TPVCirc20Tok_L1 | LONG | IOD_TPV_TCP | 3881 | 43881 | Circ20Tok_L1
TPVCirc20Tok_L2 | LONG | IOD_TPV_TCP | 3883 | 43883 | Circ20Tok_L2
TPVCirc20Tok_L3 | LONG | IOD_TPV_TCP | 3885 | 43885 | Circ20Tok_L3
TPVCirc20TokPovprecje_III | LONG | IOD_TPV_TCP | 3887 | 43887 | Circ20TokPovprecje_III
TPVCirc21CosFi_III | LONG | IOD_TPV_TCP | 3889 | 43889 | Circ21CosFi_III
TPVCirc21DelovnaEnergija | LONG | IOD_TPV_TCP | 3891 | 43891 | Circ21DelovnaEnergija
TPVCirc21DelovnaMoc_III | LONG | IOD_TPV_TCP | 3893 | 43893 | Circ21DelovnaMoc_III
TPVCirc21DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 3895 | 43895 | Circ21DelovnaMoc_L1
TPVCirc21DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 3897 | 43897 | Circ21DelovnaMoc_L2
TPVCirc21DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 3899 | 43899 | Circ21DelovnaMoc_L3
TPVCirc21Frekvenca_L1 | LONG | IOD_TPV_TCP | 3901 | 43901 | Circ21Frekvenca_L1
TPVCirc21InduktivnaEnergija | LONG | IOD_TPV_TCP | 3903 | 43903 | Circ21InduktivnaEnergija
TPVCirc21InduktivnaMoc_III | LONG | IOD_TPV_TCP | 3905 | 43905 | Circ21InduktivnaMoc_III
TPVCirc21JalovaMoc_L1 | LONG | IOD_TPV_TCP | 3907 | 43907 | Circ21JalovaMoc_L1
TPVCirc21JalovaMoc_L2 | LONG | IOD_TPV_TCP | 3909 | 43909 | Circ21JalovaMoc_L2
TPVCirc21JalovaMoc_L3 | LONG | IOD_TPV_TCP | 3911 | 43911 | Circ21JalovaMoc_L3
TPVCirc21KapacitivnaEnergija | LONG | IOD_TPV_TCP | 3913 | 43913 | Circ21KapacitivnaEnergija
TPVCirc21KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 3915 | 43915 | Circ21KapacitivnaMoc_III
TPVCirc21MaximumDemand | LONG | IOD_TPV_TCP | 3917 | 43917 | Circ21MaximumDemand
TPVCirc21Napetost_L1_L2 | LONG | IOD_TPV_TCP | 3919 | 43919 | Circ21Napetost_L1_L2
TPVCirc21Napetost_L1_N | LONG | IOD_TPV_TCP | 3921 | 43921 | Circ21Napetost_L1_N
TPVCirc21Napetost_L2_L3 | LONG | IOD_TPV_TCP | 3923 | 43923 | Circ21Napetost_L2_L3
TPVCirc21Napetost_L2_N | LONG | IOD_TPV_TCP | 3925 | 43925 | Circ21Napetost_L2_N
TPVCirc21Napetost_L3_L1 | LONG | IOD_TPV_TCP | 3927 | 43927 | Circ21Napetost_L3_L1
TPVCirc21Napetost_L3_N | LONG | IOD_TPV_TCP | 3929 | 43929 | Circ21Napetost_L3_N
TPVCirc21NavideznaMoc_III | LONG | IOD_TPV_TCP | 3931 | 43931 | Circ21NavideznaMoc_III
TPVCirc21NicelniTok | LONG | IOD_TPV_TCP | 3933 | 43933 | Circ21NicelniTok
TPVCirc21PowerFactor_III | LONG | IOD_TPV_TCP | 3935 | 43935 | Circ21PowerFactor_III
TPVCirc21PowerFactor_L1 | LONG | IOD_TPV_TCP | 3937 | 43937 | Circ21PowerFactor_L1
TPVCirc21PowerFactor_L2 | LONG | IOD_TPV_TCP | 3939 | 43939 | Circ21PowerFactor_L2
TPVCirc21PowerFactor_L3 | LONG | IOD_TPV_TCP | 3941 | 43941 | Circ21PowerFactor_L3
TPVCirc21THDI_L1 | LONG | IOD_TPV_TCP | 3943 | 43943 | Circ21THDI_L1
TPVCirc21THDI_L2 | LONG | IOD_TPV_TCP | 3945 | 43945 | Circ21THDI_L2
TPVCirc21THDI_L3 | LONG | IOD_TPV_TCP | 3947 | 43947 | Circ21THDI_L3
TPVCirc21THDV_L1 | LONG | IOD_TPV_TCP | 3949 | 43949 | Circ21THDV_L1
TPVCirc21THDV_L2 | LONG | IOD_TPV_TCP | 3951 | 43951 | Circ21THDV_L2
TPVCirc21THDV_L3 | LONG | IOD_TPV_TCP | 3953 | 43953 | Circ21THDV_L3
TPVCirc21Tok_L1 | LONG | IOD_TPV_TCP | 3955 | 43955 | Circ21Tok_L1
TPVCirc21Tok_L2 | LONG | IOD_TPV_TCP | 3957 | 43957 | Circ21Tok_L2
TPVCirc21Tok_L3 | LONG | IOD_TPV_TCP | 3959 | 43959 | Circ21Tok_L3
TPVCirc21TokPovprecje_III | LONG | IOD_TPV_TCP | 3961 | 43961 | Circ21TokPovprecje_III
TPVCirc22CosFi_III | LONG | IOD_TPV_TCP | 3963 | 43963 | Circ22CosFi_III
TPVCirc22DelovnaEnergija | LONG | IOD_TPV_TCP | 3965 | 43965 | Circ22DelovnaEnergija
TPVCirc22DelovnaMoc_III | LONG | IOD_TPV_TCP | 3967 | 43967 | Circ22DelovnaMoc_III
TPVCirc22DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 3969 | 43969 | Circ22DelovnaMoc_L1
TPVCirc22DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 3971 | 43971 | Circ22DelovnaMoc_L2
TPVCirc22DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 3973 | 43973 | Circ22DelovnaMoc_L3
TPVCirc22Frekvenca_L1 | LONG | IOD_TPV_TCP | 3975 | 43975 | Circ22Frekvenca_L1
TPVCirc22InduktivnaEnergija | LONG | IOD_TPV_TCP | 3977 | 43977 | Circ22InduktivnaEnergija
TPVCirc22InduktivnaMoc_III | LONG | IOD_TPV_TCP | 3979 | 43979 | Circ22InduktivnaMoc_III
TPVCirc22JalovaMoc_L1 | LONG | IOD_TPV_TCP | 3981 | 43981 | Circ22JalovaMoc_L1
TPVCirc22JalovaMoc_L2 | LONG | IOD_TPV_TCP | 3983 | 43983 | Circ22JalovaMoc_L2
TPVCirc22JalovaMoc_L3 | LONG | IOD_TPV_TCP | 3985 | 43985 | Circ22JalovaMoc_L3
TPVCirc22KapacitivnaEnergija | LONG | IOD_TPV_TCP | 3987 | 43987 | Circ22KapacitivnaEnergija
TPVCirc22KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 3989 | 43989 | Circ22KapacitivnaMoc_III
TPVCirc22MaximumDemand | LONG | IOD_TPV_TCP | 3991 | 43991 | Circ22MaximumDemand
TPVCirc22Napetost_L1_L2 | LONG | IOD_TPV_TCP | 3993 | 43993 | Circ22Napetost_L1_L2
TPVCirc22Napetost_L1_N | LONG | IOD_TPV_TCP | 3995 | 43995 | Circ22Napetost_L1_N
TPVCirc22Napetost_L2_L3 | LONG | IOD_TPV_TCP | 3997 | 43997 | Circ22Napetost_L2_L3
TPVCirc22Napetost_L2_N | LONG | IOD_TPV_TCP | 3999 | 43999 | Circ22Napetost_L2_N
TPVCirc22Napetost_L3_L1 | LONG | IOD_TPV_TCP | 4001 | 44001 | Circ22Napetost_L3_L1
TPVCirc22Napetost_L3_N | LONG | IOD_TPV_TCP | 4003 | 44003 | Circ22Napetost_L3_N
TPVCirc22NavideznaMoc_III | LONG | IOD_TPV_TCP | 4005 | 44005 | Circ22NavideznaMoc_III
TPVCirc22NicelniTok | LONG | IOD_TPV_TCP | 4007 | 44007 | Circ22NicelniTok
TPVCirc22PowerFactor_III | LONG | IOD_TPV_TCP | 4009 | 44009 | Circ22PowerFactor_III
TPVCirc22PowerFactor_L1 | LONG | IOD_TPV_TCP | 4011 | 44011 | Circ22PowerFactor_L1
TPVCirc22PowerFactor_L2 | LONG | IOD_TPV_TCP | 4013 | 44013 | Circ22PowerFactor_L2
TPVCirc22PowerFactor_L3 | LONG | IOD_TPV_TCP | 4015 | 44015 | Circ22PowerFactor_L3
TPVCirc22THDI_L1 | LONG | IOD_TPV_TCP | 4017 | 44017 | Circ22THDI_L1
TPVCirc22THDI_L2 | LONG | IOD_TPV_TCP | 4019 | 44019 | Circ22THDI_L2
TPVCirc22THDI_L3 | LONG | IOD_TPV_TCP | 4021 | 44021 | Circ22THDI_L3
TPVCirc22THDV_L1 | LONG | IOD_TPV_TCP | 4023 | 44023 | Circ22THDV_L1
TPVCirc22THDV_L2 | LONG | IOD_TPV_TCP | 4025 | 44025 | Circ22THDV_L2
TPVCirc22THDV_L3 | LONG | IOD_TPV_TCP | 4027 | 44027 | Circ22THDV_L3
TPVCirc22Tok_L1 | LONG | IOD_TPV_TCP | 4029 | 44029 | Circ22Tok_L1
TPVCirc22Tok_L2 | LONG | IOD_TPV_TCP | 4031 | 44031 | Circ22Tok_L2
TPVCirc22Tok_L3 | LONG | IOD_TPV_TCP | 4033 | 44033 | Circ22Tok_L3
TPVCirc22TokPovprecje_III | LONG | IOD_TPV_TCP | 4035 | 44035 | Circ22TokPovprecje_III
TPVCirc23CosFi_III | LONG | IOD_TPV_TCP | 4037 | 44037 | Circ23CosFi_III
TPVCirc23DelovnaEnergija | LONG | IOD_TPV_TCP | 4039 | 44039 | Circ23DelovnaEnergija
TPVCirc23DelovnaMoc_III | LONG | IOD_TPV_TCP | 4041 | 44041 | Circ23DelovnaMoc_III
TPVCirc23DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 4043 | 44043 | Circ23DelovnaMoc_L1
TPVCirc23DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 4045 | 44045 | Circ23DelovnaMoc_L2
TPVCirc23DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 4047 | 44047 | Circ23DelovnaMoc_L3
TPVCirc23Frekvenca_L1 | LONG | IOD_TPV_TCP | 4049 | 44049 | Circ23Frekvenca_L1
TPVCirc23InduktivnaEnergija | LONG | IOD_TPV_TCP | 4051 | 44051 | Circ23InduktivnaEnergija
TPVCirc23InduktivnaMoc_III | LONG | IOD_TPV_TCP | 4053 | 44053 | Circ23InduktivnaMoc_III
TPVCirc23JalovaMoc_L1 | LONG | IOD_TPV_TCP | 4055 | 44055 | Circ23JalovaMoc_L1
TPVCirc23JalovaMoc_L2 | LONG | IOD_TPV_TCP | 4057 | 44057 | Circ23JalovaMoc_L2
TPVCirc23JalovaMoc_L3 | LONG | IOD_TPV_TCP | 4059 | 44059 | Circ23JalovaMoc_L3
TPVCirc23KapacitivnaEnergija | LONG | IOD_TPV_TCP | 4061 | 44061 | Circ23KapacitivnaEnergija
TPVCirc23KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 4063 | 44063 | Circ23KapacitivnaMoc_III
TPVCirc23MaximumDemand | LONG | IOD_TPV_TCP | 4065 | 44065 | Circ23MaximumDemand
TPVCirc23Napetost_L1_L2 | LONG | IOD_TPV_TCP | 4067 | 44067 | Circ23Napetost_L1_L2
TPVCirc23Napetost_L1_N | LONG | IOD_TPV_TCP | 4069 | 44069 | Circ23Napetost_L1_N
TPVCirc23Napetost_L2_L3 | LONG | IOD_TPV_TCP | 4071 | 44071 | Circ23Napetost_L2_L3
TPVCirc23Napetost_L2_N | LONG | IOD_TPV_TCP | 4073 | 44073 | Circ23Napetost_L2_N
TPVCirc23Napetost_L3_L1 | LONG | IOD_TPV_TCP | 4075 | 44075 | Circ23Napetost_L3_L1
TPVCirc23Napetost_L3_N | LONG | IOD_TPV_TCP | 4077 | 44077 | Circ23Napetost_L3_N
TPVCirc23NavideznaMoc_III | LONG | IOD_TPV_TCP | 4079 | 44079 | Circ23NavideznaMoc_III
TPVCirc23NicelniTok | LONG | IOD_TPV_TCP | 4081 | 44081 | Circ23NicelniTok
TPVCirc23PowerFactor_III | LONG | IOD_TPV_TCP | 4083 | 44083 | Circ23PowerFactor_III
TPVCirc23PowerFactor_L1 | LONG | IOD_TPV_TCP | 4085 | 44085 | Circ23PowerFactor_L1
TPVCirc23PowerFactor_L2 | LONG | IOD_TPV_TCP | 4087 | 44087 | Circ23PowerFactor_L2
TPVCirc23PowerFactor_L3 | LONG | IOD_TPV_TCP | 4089 | 44089 | Circ23PowerFactor_L3
TPVCirc23THDI_L1 | LONG | IOD_TPV_TCP | 4091 | 44091 | Circ23THDI_L1
TPVCirc23THDI_L2 | LONG | IOD_TPV_TCP | 4093 | 44093 | Circ23THDI_L2
TPVCirc23THDI_L3 | LONG | IOD_TPV_TCP | 4095 | 44095 | Circ23THDI_L3
TPVCirc23THDV_L1 | LONG | IOD_TPV_TCP | 4097 | 44097 | Circ23THDV_L1
TPVCirc23THDV_L2 | LONG | IOD_TPV_TCP | 4099 | 44099 | Circ23THDV_L2
TPVCirc23THDV_L3 | LONG | IOD_TPV_TCP | 4101 | 44101 | Circ23THDV_L3
TPVCirc23Tok_L1 | LONG | IOD_TPV_TCP | 4103 | 44103 | Circ23Tok_L1
TPVCirc23Tok_L2 | LONG | IOD_TPV_TCP | 4105 | 44105 | Circ23Tok_L2
TPVCirc23Tok_L3 | LONG | IOD_TPV_TCP | 4107 | 44107 | Circ23Tok_L3
TPVCirc23TokPovprecje_III | LONG | IOD_TPV_TCP | 4109 | 44109 | Circ23TokPovprecje_III
TPVCirc24CosFi_III | LONG | IOD_TPV_TCP | 4111 | 44111 | Circ24CosFi_III
TPVCirc24DelovnaEnergija | LONG | IOD_TPV_TCP | 4113 | 44113 | Circ24DelovnaEnergija
TPVCirc24DelovnaMoc_III | LONG | IOD_TPV_TCP | 4115 | 44115 | Circ24DelovnaMoc_III
TPVCirc24DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 4117 | 44117 | Circ24DelovnaMoc_L1
TPVCirc24DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 4119 | 44119 | Circ24DelovnaMoc_L2
TPVCirc24DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 4121 | 44121 | Circ24DelovnaMoc_L3
TPVCirc24Frekvenca_L1 | LONG | IOD_TPV_TCP | 4123 | 44123 | Circ24Frekvenca_L1
TPVCirc24InduktivnaEnergija | LONG | IOD_TPV_TCP | 4125 | 44125 | Circ24InduktivnaEnergija
TPVCirc24InduktivnaMoc_III | LONG | IOD_TPV_TCP | 4127 | 44127 | Circ24InduktivnaMoc_III
TPVCirc24JalovaMoc_L1 | LONG | IOD_TPV_TCP | 4129 | 44129 | Circ24JalovaMoc_L1
TPVCirc24JalovaMoc_L2 | LONG | IOD_TPV_TCP | 4131 | 44131 | Circ24JalovaMoc_L2
TPVCirc24JalovaMoc_L3 | LONG | IOD_TPV_TCP | 4133 | 44133 | Circ24JalovaMoc_L3
TPVCirc24KapacitivnaEnergija | LONG | IOD_TPV_TCP | 4135 | 44135 | Circ24KapacitivnaEnergija
TPVCirc24KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 4137 | 44137 | Circ24KapacitivnaMoc_III
TPVCirc24MaximumDemand | LONG | IOD_TPV_TCP | 4139 | 44139 | Circ24MaximumDemand
TPVCirc24Napetost_L1_L2 | LONG | IOD_TPV_TCP | 4141 | 44141 | Circ24Napetost_L1_L2
TPVCirc24Napetost_L1_N | LONG | IOD_TPV_TCP | 4143 | 44143 | Circ24Napetost_L1_N
TPVCirc24Napetost_L2_L3 | LONG | IOD_TPV_TCP | 4145 | 44145 | Circ24Napetost_L2_L3
TPVCirc24Napetost_L2_N | LONG | IOD_TPV_TCP | 4147 | 44147 | Circ24Napetost_L2_N
TPVCirc24Napetost_L3_L1 | LONG | IOD_TPV_TCP | 4149 | 44149 | Circ24Napetost_L3_L1
TPVCirc24Napetost_L3_N | LONG | IOD_TPV_TCP | 4151 | 44151 | Circ24Napetost_L3_N
TPVCirc24NavideznaMoc_III | LONG | IOD_TPV_TCP | 4153 | 44153 | Circ24NavideznaMoc_III
TPVCirc24NicelniTok | LONG | IOD_TPV_TCP | 4155 | 44155 | Circ24NicelniTok
TPVCirc24PowerFactor_III | LONG | IOD_TPV_TCP | 4157 | 44157 | Circ24PowerFactor_III
TPVCirc24PowerFactor_L1 | LONG | IOD_TPV_TCP | 4159 | 44159 | Circ24PowerFactor_L1
TPVCirc24PowerFactor_L2 | LONG | IOD_TPV_TCP | 4161 | 44161 | Circ24PowerFactor_L2
TPVCirc24PowerFactor_L3 | LONG | IOD_TPV_TCP | 4163 | 44163 | Circ24PowerFactor_L3
TPVCirc24THDI_L1 | LONG | IOD_TPV_TCP | 4165 | 44165 | Circ24THDI_L1
TPVCirc24THDI_L2 | LONG | IOD_TPV_TCP | 4167 | 44167 | Circ24THDI_L2
TPVCirc24THDI_L3 | LONG | IOD_TPV_TCP | 4169 | 44169 | Circ24THDI_L3
TPVCirc24THDV_L1 | LONG | IOD_TPV_TCP | 4171 | 44171 | Circ24THDV_L1
TPVCirc24THDV_L2 | LONG | IOD_TPV_TCP | 4173 | 44173 | Circ24THDV_L2
TPVCirc24THDV_L3 | LONG | IOD_TPV_TCP | 4175 | 44175 | Circ24THDV_L3
TPVCirc24Tok_L1 | LONG | IOD_TPV_TCP | 4177 | 44177 | Circ24Tok_L1
TPVCirc24Tok_L2 | LONG | IOD_TPV_TCP | 4179 | 44179 | Circ24Tok_L2
TPVCirc24Tok_L3 | LONG | IOD_TPV_TCP | 4181 | 44181 | Circ24Tok_L3
TPVCirc24TokPovprecje_III | LONG | IOD_TPV_TCP | 4183 | 44183 | Circ24TokPovprecje_III
TPVCirc25CosFi_III | LONG | IOD_TPV_TCP | 4185 | 44185 | Circ25CosFi_III
TPVCirc25DelovnaEnergija | LONG | IOD_TPV_TCP | 4187 | 44187 | Circ25DelovnaEnergija
TPVCirc25DelovnaMoc_III | LONG | IOD_TPV_TCP | 4189 | 44189 | Circ25DelovnaMoc_III
TPVCirc25DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 4191 | 44191 | Circ25DelovnaMoc_L1
TPVCirc25DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 4193 | 44193 | Circ25DelovnaMoc_L2
TPVCirc25DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 4195 | 44195 | Circ25DelovnaMoc_L3
TPVCirc25Frekvenca_L1 | LONG | IOD_TPV_TCP | 4197 | 44197 | Circ25Frekvenca_L1
TPVCirc25InduktivnaEnergija | LONG | IOD_TPV_TCP | 4199 | 44199 | Circ25InduktivnaEnergija
TPVCirc25InduktivnaMoc_III | LONG | IOD_TPV_TCP | 4201 | 44201 | Circ25InduktivnaMoc_III
TPVCirc25JalovaMoc_L1 | LONG | IOD_TPV_TCP | 4203 | 44203 | Circ25JalovaMoc_L1
TPVCirc25JalovaMoc_L2 | LONG | IOD_TPV_TCP | 4205 | 44205 | Circ25JalovaMoc_L2
TPVCirc25JalovaMoc_L3 | LONG | IOD_TPV_TCP | 4207 | 44207 | Circ25JalovaMoc_L3
TPVCirc25KapacitivnaEnergija | LONG | IOD_TPV_TCP | 4209 | 44209 | Circ25KapacitivnaEnergija
TPVCirc25KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 4211 | 44211 | Circ25KapacitivnaMoc_III
TPVCirc25MaximumDemand | LONG | IOD_TPV_TCP | 4213 | 44213 | Circ25MaximumDemand
TPVCirc25Napetost_L1_L2 | LONG | IOD_TPV_TCP | 4215 | 44215 | Circ25Napetost_L1_L2
TPVCirc25Napetost_L1_N | LONG | IOD_TPV_TCP | 4217 | 44217 | Circ25Napetost_L1_N
TPVCirc25Napetost_L2_L3 | LONG | IOD_TPV_TCP | 4219 | 44219 | Circ25Napetost_L2_L3
TPVCirc25Napetost_L2_N | LONG | IOD_TPV_TCP | 4221 | 44221 | Circ25Napetost_L2_N
TPVCirc25Napetost_L3_L1 | LONG | IOD_TPV_TCP | 4223 | 44223 | Circ25Napetost_L3_L1
TPVCirc25Napetost_L3_N | LONG | IOD_TPV_TCP | 4225 | 44225 | Circ25Napetost_L3_N
TPVCirc25NavideznaMoc_III | LONG | IOD_TPV_TCP | 4227 | 44227 | Circ25NavideznaMoc_III
TPVCirc25NicelniTok | LONG | IOD_TPV_TCP | 4229 | 44229 | Circ25NicelniTok
TPVCirc25PowerFactor_III | LONG | IOD_TPV_TCP | 4231 | 44231 | Circ25PowerFactor_III
TPVCirc25PowerFactor_L1 | LONG | IOD_TPV_TCP | 4233 | 44233 | Circ25PowerFactor_L1
TPVCirc25PowerFactor_L2 | LONG | IOD_TPV_TCP | 4235 | 44235 | Circ25PowerFactor_L2
TPVCirc25PowerFactor_L3 | LONG | IOD_TPV_TCP | 4237 | 44237 | Circ25PowerFactor_L3
TPVCirc25THDI_L1 | LONG | IOD_TPV_TCP | 4239 | 44239 | Circ25THDI_L1
TPVCirc25THDI_L2 | LONG | IOD_TPV_TCP | 4241 | 44241 | Circ25THDI_L2
TPVCirc25THDI_L3 | LONG | IOD_TPV_TCP | 4243 | 44243 | Circ25THDI_L3
TPVCirc25THDV_L1 | LONG | IOD_TPV_TCP | 4245 | 44245 | Circ25THDV_L1
TPVCirc25THDV_L2 | LONG | IOD_TPV_TCP | 4247 | 44247 | Circ25THDV_L2
TPVCirc25THDV_L3 | LONG | IOD_TPV_TCP | 4249 | 44249 | Circ25THDV_L3
TPVCirc25Tok_L1 | LONG | IOD_TPV_TCP | 4251 | 44251 | Circ25Tok_L1
TPVCirc25Tok_L2 | LONG | IOD_TPV_TCP | 4253 | 44253 | Circ25Tok_L2
TPVCirc25Tok_L3 | LONG | IOD_TPV_TCP | 4255 | 44255 | Circ25Tok_L3
TPVCirc25TokPovprecje_III | LONG | IOD_TPV_TCP | 4257 | 44257 | Circ25TokPovprecje_III
TPVCirc2CosFi_III | LONG | IOD_TPV_TCP | 4259 | 44259 | Circ2CosFi_III
TPVCirc2DelovnaEnergija | LONG | IOD_TPV_TCP | 4261 | 44261 | Circ2DelovnaEnergija
TPVCirc2DelovnaMoc_III | LONG | IOD_TPV_TCP | 4263 | 44263 | Circ2DelovnaMoc_III
TPVCirc2DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 4265 | 44265 | Circ2DelovnaMoc_L1
TPVCirc2DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 4267 | 44267 | Circ2DelovnaMoc_L2
TPVCirc2DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 4269 | 44269 | Circ2DelovnaMoc_L3
TPVCirc2Frekvenca_L1 | LONG | IOD_TPV_TCP | 4271 | 44271 | Circ2Frekvenca_L1
TPVCirc2InduktivnaEnergija | LONG | IOD_TPV_TCP | 4273 | 44273 | Circ2InduktivnaEnergija
TPVCirc2InduktivnaMoc_III | LONG | IOD_TPV_TCP | 4275 | 44275 | Circ2InduktivnaMoc_III
TPVCirc2JalovaMoc_L1 | LONG | IOD_TPV_TCP | 4277 | 44277 | Circ2JalovaMoc_L1
TPVCirc2JalovaMoc_L2 | LONG | IOD_TPV_TCP | 4279 | 44279 | Circ2JalovaMoc_L2
TPVCirc2JalovaMoc_L3 | LONG | IOD_TPV_TCP | 4281 | 44281 | Circ2JalovaMoc_L3
TPVCirc2KapacitivnaEnergija | LONG | IOD_TPV_TCP | 4283 | 44283 | Circ2KapacitivnaEnergija
TPVCirc2KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 4285 | 44285 | Circ2KapacitivnaMoc_III
TPVCirc2MaximumDemand | LONG | IOD_TPV_TCP | 4287 | 44287 | Circ2MaximumDemand
TPVCirc2Napetost_L1_L2 | LONG | IOD_TPV_TCP | 4289 | 44289 | Circ2Napetost_L1_L2
TPVCirc2Napetost_L1_N | LONG | IOD_TPV_TCP | 4291 | 44291 | Circ2Napetost_L1_N
TPVCirc2Napetost_L2_L3 | LONG | IOD_TPV_TCP | 4293 | 44293 | Circ2Napetost_L2_L3
TPVCirc2Napetost_L2_N | LONG | IOD_TPV_TCP | 4295 | 44295 | Circ2Napetost_L2_N
TPVCirc2Napetost_L3_L1 | LONG | IOD_TPV_TCP | 4297 | 44297 | Circ2Napetost_L3_L1
TPVCirc2Napetost_L3_N | LONG | IOD_TPV_TCP | 4299 | 44299 | Circ2Napetost_L3_N
TPVCirc2NavideznaMoc_III | LONG | IOD_TPV_TCP | 4301 | 44301 | Circ2NavideznaMoc_III
TPVCirc2NicelniTok | LONG | IOD_TPV_TCP | 4303 | 44303 | Circ2NicelniTok
TPVCirc2PowerFactor_III | LONG | IOD_TPV_TCP | 4305 | 44305 | Circ2PowerFactor_III
TPVCirc2PowerFactor_L1 | LONG | IOD_TPV_TCP | 4307 | 44307 | Circ2PowerFactor_L1
TPVCirc2PowerFactor_L2 | LONG | IOD_TPV_TCP | 4309 | 44309 | Circ2PowerFactor_L2
TPVCirc2PowerFactor_L3 | LONG | IOD_TPV_TCP | 4311 | 44311 | Circ2PowerFactor_L3
TPVCirc2THDI_L1 | LONG | IOD_TPV_TCP | 4313 | 44313 | Circ2THDI_L1
TPVCirc2THDI_L2 | LONG | IOD_TPV_TCP | 4315 | 44315 | Circ2THDI_L2
TPVCirc2THDI_L3 | LONG | IOD_TPV_TCP | 4317 | 44317 | Circ2THDI_L3
TPVCirc2THDV_L1 | LONG | IOD_TPV_TCP | 4319 | 44319 | Circ2THDV_L1
TPVCirc2THDV_L2 | LONG | IOD_TPV_TCP | 4321 | 44321 | Circ2THDV_L2
TPVCirc2THDV_L3 | LONG | IOD_TPV_TCP | 4323 | 44323 | Circ2THDV_L3
TPVCirc2Tok_L1 | LONG | IOD_TPV_TCP | 4325 | 44325 | Circ2Tok_L1
TPVCirc2Tok_L2 | LONG | IOD_TPV_TCP | 4327 | 44327 | Circ2Tok_L2
TPVCirc2Tok_L3 | LONG | IOD_TPV_TCP | 4329 | 44329 | Circ2Tok_L3
TPVCirc2TokPovprecje_III | LONG | IOD_TPV_TCP | 4331 | 44331 | Circ2TokPovprecje_III
TPVCirc3CosFi_III | LONG | IOD_TPV_TCP | 4333 | 44333 | Circ3CosFi_III
TPVCirc3DelovnaEnergija | LONG | IOD_TPV_TCP | 4335 | 44335 | Circ3DelovnaEnergija
TPVCirc3DelovnaMoc_III | LONG | IOD_TPV_TCP | 4337 | 44337 | Circ3DelovnaMoc_III
TPVCirc3DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 4339 | 44339 | Circ3DelovnaMoc_L1
TPVCirc3DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 4341 | 44341 | Circ3DelovnaMoc_L2
TPVCirc3DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 4343 | 44343 | Circ3DelovnaMoc_L3
TPVCirc3Frekvenca_L1 | LONG | IOD_TPV_TCP | 4345 | 44345 | Circ3Frekvenca_L1
TPVCirc3InduktivnaEnergija | LONG | IOD_TPV_TCP | 4347 | 44347 | Circ3InduktivnaEnergija
TPVCirc3InduktivnaMoc_III | LONG | IOD_TPV_TCP | 4349 | 44349 | Circ3InduktivnaMoc_III
TPVCirc3JalovaMoc_L1 | LONG | IOD_TPV_TCP | 4351 | 44351 | Circ3JalovaMoc_L1
TPVCirc3JalovaMoc_L2 | LONG | IOD_TPV_TCP | 4353 | 44353 | Circ3JalovaMoc_L2
TPVCirc3JalovaMoc_L3 | LONG | IOD_TPV_TCP | 4355 | 44355 | Circ3JalovaMoc_L3
TPVCirc3KapacitivnaEnergija | LONG | IOD_TPV_TCP | 4357 | 44357 | Circ3KapacitivnaEnergija
TPVCirc3KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 4359 | 44359 | Circ3KapacitivnaMoc_III
TPVCirc3MaximumDemand | LONG | IOD_TPV_TCP | 4361 | 44361 | Circ3MaximumDemand
TPVCirc3Napetost_L1_L2 | LONG | IOD_TPV_TCP | 4363 | 44363 | Circ3Napetost_L1_L2
TPVCirc3Napetost_L1_N | LONG | IOD_TPV_TCP | 4365 | 44365 | Circ3Napetost_L1_N
TPVCirc3Napetost_L2_L3 | LONG | IOD_TPV_TCP | 4367 | 44367 | Circ3Napetost_L2_L3
TPVCirc3Napetost_L2_N | LONG | IOD_TPV_TCP | 4369 | 44369 | Circ3Napetost_L2_N
TPVCirc3Napetost_L3_L1 | LONG | IOD_TPV_TCP | 4371 | 44371 | Circ3Napetost_L3_L1
TPVCirc3Napetost_L3_N | LONG | IOD_TPV_TCP | 4373 | 44373 | Circ3Napetost_L3_N
TPVCirc3NavideznaMoc_III | LONG | IOD_TPV_TCP | 4375 | 44375 | Circ3NavideznaMoc_III
TPVCirc3NicelniTok | LONG | IOD_TPV_TCP | 4377 | 44377 | Circ3NicelniTok
TPVCirc3PowerFactor_III | LONG | IOD_TPV_TCP | 4379 | 44379 | Circ3PowerFactor_III
TPVCirc3PowerFactor_L1 | LONG | IOD_TPV_TCP | 4381 | 44381 | Circ3PowerFactor_L1
TPVCirc3PowerFactor_L2 | LONG | IOD_TPV_TCP | 4383 | 44383 | Circ3PowerFactor_L2
TPVCirc3PowerFactor_L3 | LONG | IOD_TPV_TCP | 4385 | 44385 | Circ3PowerFactor_L3
TPVCirc3THDI_L1 | LONG | IOD_TPV_TCP | 4387 | 44387 | Circ3THDI_L1
TPVCirc3THDI_L2 | LONG | IOD_TPV_TCP | 4389 | 44389 | Circ3THDI_L2
TPVCirc3THDI_L3 | LONG | IOD_TPV_TCP | 4391 | 44391 | Circ3THDI_L3
TPVCirc3THDV_L1 | LONG | IOD_TPV_TCP | 4393 | 44393 | Circ3THDV_L1
TPVCirc3THDV_L2 | LONG | IOD_TPV_TCP | 4395 | 44395 | Circ3THDV_L2
TPVCirc3THDV_L3 | LONG | IOD_TPV_TCP | 4397 | 44397 | Circ3THDV_L3
TPVCirc3Tok_L1 | LONG | IOD_TPV_TCP | 4399 | 44399 | Circ3Tok_L1
TPVCirc3Tok_L2 | LONG | IOD_TPV_TCP | 4401 | 44401 | Circ3Tok_L2
TPVCirc3Tok_L3 | LONG | IOD_TPV_TCP | 4403 | 44403 | Circ3Tok_L3
TPVCirc3TokPovprecje_III | LONG | IOD_TPV_TCP | 4405 | 44405 | Circ3TokPovprecje_III
TPVCirc4CosFi_III | LONG | IOD_TPV_TCP | 4407 | 44407 | Circ4CosFi_III
TPVCirc4DelovnaEnergija | LONG | IOD_TPV_TCP | 4409 | 44409 | Circ4DelovnaEnergija
TPVCirc4DelovnaMoc_III | LONG | IOD_TPV_TCP | 4411 | 44411 | Circ4DelovnaMoc_III
TPVCirc4DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 4413 | 44413 | Circ4DelovnaMoc_L1
TPVCirc4DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 4415 | 44415 | Circ4DelovnaMoc_L2
TPVCirc4DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 4417 | 44417 | Circ4DelovnaMoc_L3
TPVCirc4Frekvenca_L1 | LONG | IOD_TPV_TCP | 4419 | 44419 | Circ4Frekvenca_L1
TPVCirc4InduktivnaEnergija | LONG | IOD_TPV_TCP | 4421 | 44421 | Circ4InduktivnaEnergija
TPVCirc4InduktivnaMoc_III | LONG | IOD_TPV_TCP | 4423 | 44423 | Circ4InduktivnaMoc_III
TPVCirc4JalovaMoc_L1 | LONG | IOD_TPV_TCP | 4425 | 44425 | Circ4JalovaMoc_L1
TPVCirc4JalovaMoc_L2 | LONG | IOD_TPV_TCP | 4427 | 44427 | Circ4JalovaMoc_L2
TPVCirc4JalovaMoc_L3 | LONG | IOD_TPV_TCP | 4429 | 44429 | Circ4JalovaMoc_L3
TPVCirc4KapacitivnaEnergija | LONG | IOD_TPV_TCP | 4431 | 44431 | Circ4KapacitivnaEnergija
TPVCirc4KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 4433 | 44433 | Circ4KapacitivnaMoc_III
TPVCirc4MaximumDemand | LONG | IOD_TPV_TCP | 4435 | 44435 | Circ4MaximumDemand
TPVCirc4Napetost_L1_L2 | LONG | IOD_TPV_TCP | 4437 | 44437 | Circ4Napetost_L1_L2
TPVCirc4Napetost_L1_N | LONG | IOD_TPV_TCP | 4439 | 44439 | Circ4Napetost_L1_N
TPVCirc4Napetost_L2_L3 | LONG | IOD_TPV_TCP | 4441 | 44441 | Circ4Napetost_L2_L3
TPVCirc4Napetost_L2_N | LONG | IOD_TPV_TCP | 4443 | 44443 | Circ4Napetost_L2_N
TPVCirc4Napetost_L3_L1 | LONG | IOD_TPV_TCP | 4445 | 44445 | Circ4Napetost_L3_L1
TPVCirc4Napetost_L3_N | LONG | IOD_TPV_TCP | 4447 | 44447 | Circ4Napetost_L3_N
TPVCirc4NavideznaMoc_III | LONG | IOD_TPV_TCP | 4449 | 44449 | Circ4NavideznaMoc_III
TPVCirc4NicelniTok | LONG | IOD_TPV_TCP | 4451 | 44451 | Circ4NicelniTok
TPVCirc4PowerFactor_III | LONG | IOD_TPV_TCP | 4453 | 44453 | Circ4PowerFactor_III
TPVCirc4PowerFactor_L1 | LONG | IOD_TPV_TCP | 4455 | 44455 | Circ4PowerFactor_L1
TPVCirc4PowerFactor_L2 | LONG | IOD_TPV_TCP | 4457 | 44457 | Circ4PowerFactor_L2
TPVCirc4PowerFactor_L3 | LONG | IOD_TPV_TCP | 4459 | 44459 | Circ4PowerFactor_L3
TPVCirc4THDI_L1 | LONG | IOD_TPV_TCP | 4461 | 44461 | Circ4THDI_L1
TPVCirc4THDI_L2 | LONG | IOD_TPV_TCP | 4463 | 44463 | Circ4THDI_L2
TPVCirc4THDI_L3 | LONG | IOD_TPV_TCP | 4465 | 44465 | Circ4THDI_L3
TPVCirc4THDV_L1 | LONG | IOD_TPV_TCP | 4467 | 44467 | Circ4THDV_L1
TPVCirc4THDV_L2 | LONG | IOD_TPV_TCP | 4469 | 44469 | Circ4THDV_L2
TPVCirc4THDV_L3 | LONG | IOD_TPV_TCP | 4471 | 44471 | Circ4THDV_L3
TPVCirc4Tok_L1 | LONG | IOD_TPV_TCP | 4473 | 44473 | Circ4Tok_L1
TPVCirc4Tok_L2 | LONG | IOD_TPV_TCP | 4475 | 44475 | Circ4Tok_L2
TPVCirc4Tok_L3 | LONG | IOD_TPV_TCP | 4477 | 44477 | Circ4Tok_L3
TPVCirc4TokPovprecje_III | LONG | IOD_TPV_TCP | 4479 | 44479 | Circ4TokPovprecje_III
TPVCirc5CosFi_III | LONG | IOD_TPV_TCP | 4481 | 44481 | Circ5CosFi_III
TPVCirc5DelovnaEnergija | LONG | IOD_TPV_TCP | 4483 | 44483 | Circ5DelovnaEnergija
TPVCirc5DelovnaMoc_III | LONG | IOD_TPV_TCP | 4485 | 44485 | Circ5DelovnaMoc_III
TPVCirc5DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 4487 | 44487 | Circ5DelovnaMoc_L1
TPVCirc5DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 4489 | 44489 | Circ5DelovnaMoc_L2
TPVCirc5DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 4491 | 44491 | Circ5DelovnaMoc_L3
TPVCirc5Frekvenca_L1 | LONG | IOD_TPV_TCP | 4493 | 44493 | Circ5Frekvenca_L1
TPVCirc5InduktivnaEnergija | LONG | IOD_TPV_TCP | 4495 | 44495 | Circ5InduktivnaEnergija
TPVCirc5InduktivnaMoc_III | LONG | IOD_TPV_TCP | 4497 | 44497 | Circ5InduktivnaMoc_III
TPVCirc5JalovaMoc_L1 | LONG | IOD_TPV_TCP | 4499 | 44499 | Circ5JalovaMoc_L1
TPVCirc5JalovaMoc_L2 | LONG | IOD_TPV_TCP | 4501 | 44501 | Circ5JalovaMoc_L2
TPVCirc5JalovaMoc_L3 | LONG | IOD_TPV_TCP | 4503 | 44503 | Circ5JalovaMoc_L3
TPVCirc5KapacitivnaEnergija | LONG | IOD_TPV_TCP | 4505 | 44505 | Circ5KapacitivnaEnergija
TPVCirc5KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 4507 | 44507 | Circ5KapacitivnaMoc_III
TPVCirc5MaximumDemand | LONG | IOD_TPV_TCP | 4509 | 44509 | Circ5MaximumDemand
TPVCirc5Napetost_L1_L2 | LONG | IOD_TPV_TCP | 4511 | 44511 | Circ5Napetost_L1_L2
TPVCirc5Napetost_L1_N | LONG | IOD_TPV_TCP | 4513 | 44513 | Circ5Napetost_L1_N
TPVCirc5Napetost_L2_L3 | LONG | IOD_TPV_TCP | 4515 | 44515 | Circ5Napetost_L2_L3
TPVCirc5Napetost_L2_N | LONG | IOD_TPV_TCP | 4517 | 44517 | Circ5Napetost_L2_N
TPVCirc5Napetost_L3_L1 | LONG | IOD_TPV_TCP | 4519 | 44519 | Circ5Napetost_L3_L1
TPVCirc5Napetost_L3_N | LONG | IOD_TPV_TCP | 4521 | 44521 | Circ5Napetost_L3_N
TPVCirc5NavideznaMoc_III | LONG | IOD_TPV_TCP | 4523 | 44523 | Circ5NavideznaMoc_III
TPVCirc5NicelniTok | LONG | IOD_TPV_TCP | 4525 | 44525 | Circ5NicelniTok
TPVCirc5PowerFactor_III | LONG | IOD_TPV_TCP | 4527 | 44527 | Circ5PowerFactor_III
TPVCirc5PowerFactor_L1 | LONG | IOD_TPV_TCP | 4529 | 44529 | Circ5PowerFactor_L1
TPVCirc5PowerFactor_L2 | LONG | IOD_TPV_TCP | 4531 | 44531 | Circ5PowerFactor_L2
TPVCirc5PowerFactor_L3 | LONG | IOD_TPV_TCP | 4533 | 44533 | Circ5PowerFactor_L3
TPVCirc5THDI_L1 | LONG | IOD_TPV_TCP | 4535 | 44535 | Circ5THDI_L1
TPVCirc5THDI_L2 | LONG | IOD_TPV_TCP | 4537 | 44537 | Circ5THDI_L2
TPVCirc5THDI_L3 | LONG | IOD_TPV_TCP | 4539 | 44539 | Circ5THDI_L3
TPVCirc5THDV_L1 | LONG | IOD_TPV_TCP | 4541 | 44541 | Circ5THDV_L1
TPVCirc5THDV_L2 | LONG | IOD_TPV_TCP | 4543 | 44543 | Circ5THDV_L2
TPVCirc5THDV_L3 | LONG | IOD_TPV_TCP | 4545 | 44545 | Circ5THDV_L3
TPVCirc5Tok_L1 | LONG | IOD_TPV_TCP | 4547 | 44547 | Circ5Tok_L1
TPVCirc5Tok_L2 | LONG | IOD_TPV_TCP | 4549 | 44549 | Circ5Tok_L2
TPVCirc5Tok_L3 | LONG | IOD_TPV_TCP | 4551 | 44551 | Circ5Tok_L3
TPVCirc5TokPovprecje_III | LONG | IOD_TPV_TCP | 4553 | 44553 | Circ5TokPovprecje_III
TPVCirc6CosFi_III | LONG | IOD_TPV_TCP | 4555 | 44555 | Circ6CosFi_III
TPVCirc6DelovnaEnergija | LONG | IOD_TPV_TCP | 4557 | 44557 | Circ6DelovnaEnergija
TPVCirc6DelovnaMoc_III | LONG | IOD_TPV_TCP | 4559 | 44559 | Circ6DelovnaMoc_III
TPVCirc6DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 4561 | 44561 | Circ6DelovnaMoc_L1
TPVCirc6DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 4563 | 44563 | Circ6DelovnaMoc_L2
TPVCirc6DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 4565 | 44565 | Circ6DelovnaMoc_L3
TPVCirc6Frekvenca_L1 | LONG | IOD_TPV_TCP | 4567 | 44567 | Circ6Frekvenca_L1
TPVCirc6InduktivnaEnergija | LONG | IOD_TPV_TCP | 4569 | 44569 | Circ6InduktivnaEnergija
TPVCirc6InduktivnaMoc_III | LONG | IOD_TPV_TCP | 4571 | 44571 | Circ6InduktivnaMoc_III
TPVCirc6JalovaMoc_L1 | LONG | IOD_TPV_TCP | 4573 | 44573 | Circ6JalovaMoc_L1
TPVCirc6JalovaMoc_L2 | LONG | IOD_TPV_TCP | 4575 | 44575 | Circ6JalovaMoc_L2
TPVCirc6JalovaMoc_L3 | LONG | IOD_TPV_TCP | 4577 | 44577 | Circ6JalovaMoc_L3
TPVCirc6KapacitivnaEnergija | LONG | IOD_TPV_TCP | 4579 | 44579 | Circ6KapacitivnaEnergija
TPVCirc6KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 4581 | 44581 | Circ6KapacitivnaMoc_III
TPVCirc6MaximumDemand | LONG | IOD_TPV_TCP | 4583 | 44583 | Circ6MaximumDemand
TPVCirc6Napetost_L1_L2 | LONG | IOD_TPV_TCP | 4585 | 44585 | Circ6Napetost_L1_L2
TPVCirc6Napetost_L1_N | LONG | IOD_TPV_TCP | 4587 | 44587 | Circ6Napetost_L1_N
TPVCirc6Napetost_L2_L3 | LONG | IOD_TPV_TCP | 4589 | 44589 | Circ6Napetost_L2_L3
TPVCirc6Napetost_L2_N | LONG | IOD_TPV_TCP | 4591 | 44591 | Circ6Napetost_L2_N
TPVCirc6Napetost_L3_L1 | LONG | IOD_TPV_TCP | 4593 | 44593 | Circ6Napetost_L3_L1
TPVCirc6Napetost_L3_N | LONG | IOD_TPV_TCP | 4595 | 44595 | Circ6Napetost_L3_N
TPVCirc6NavideznaMoc_III | LONG | IOD_TPV_TCP | 4597 | 44597 | Circ6NavideznaMoc_III
TPVCirc6NicelniTok | LONG | IOD_TPV_TCP | 4599 | 44599 | Circ6NicelniTok
TPVCirc6PowerFactor_III | LONG | IOD_TPV_TCP | 4601 | 44601 | Circ6PowerFactor_III
TPVCirc6PowerFactor_L1 | LONG | IOD_TPV_TCP | 4603 | 44603 | Circ6PowerFactor_L1
TPVCirc6PowerFactor_L2 | LONG | IOD_TPV_TCP | 4605 | 44605 | Circ6PowerFactor_L2
TPVCirc6PowerFactor_L3 | LONG | IOD_TPV_TCP | 4607 | 44607 | Circ6PowerFactor_L3
TPVCirc6THDI_L1 | LONG | IOD_TPV_TCP | 4609 | 44609 | Circ6THDI_L1
TPVCirc6THDI_L2 | LONG | IOD_TPV_TCP | 4611 | 44611 | Circ6THDI_L2
TPVCirc6THDI_L3 | LONG | IOD_TPV_TCP | 4613 | 44613 | Circ6THDI_L3
TPVCirc6THDV_L1 | LONG | IOD_TPV_TCP | 4615 | 44615 | Circ6THDV_L1
TPVCirc6THDV_L2 | LONG | IOD_TPV_TCP | 4617 | 44617 | Circ6THDV_L2
TPVCirc6THDV_L3 | LONG | IOD_TPV_TCP | 4619 | 44619 | Circ6THDV_L3
TPVCirc6Tok_L1 | LONG | IOD_TPV_TCP | 4621 | 44621 | Circ6Tok_L1
TPVCirc6Tok_L2 | LONG | IOD_TPV_TCP | 4623 | 44623 | Circ6Tok_L2
TPVCirc6Tok_L3 | LONG | IOD_TPV_TCP | 4625 | 44625 | Circ6Tok_L3
TPVCirc6TokPovprecje_III | LONG | IOD_TPV_TCP | 4627 | 44627 | Circ6TokPovprecje_III
TPVCirc7CosFi_III | LONG | IOD_TPV_TCP | 4629 | 44629 | Circ7CosFi_III
TPVCirc7DelovnaEnergija | LONG | IOD_TPV_TCP | 4631 | 44631 | Circ7DelovnaEnergija
TPVCirc7DelovnaMoc_III | LONG | IOD_TPV_TCP | 4633 | 44633 | Circ7DelovnaMoc_III
TPVCirc7DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 4635 | 44635 | Circ7DelovnaMoc_L1
TPVCirc7DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 4637 | 44637 | Circ7DelovnaMoc_L2
TPVCirc7DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 4639 | 44639 | Circ7DelovnaMoc_L3
TPVCirc7Frekvenca_L1 | LONG | IOD_TPV_TCP | 4641 | 44641 | Circ7Frekvenca_L1
TPVCirc7InduktivnaEnergija | LONG | IOD_TPV_TCP | 4643 | 44643 | Circ7InduktivnaEnergija
TPVCirc7InduktivnaMoc_III | LONG | IOD_TPV_TCP | 4645 | 44645 | Circ7InduktivnaMoc_III
TPVCirc7JalovaMoc_L1 | LONG | IOD_TPV_TCP | 4647 | 44647 | Circ7JalovaMoc_L1
TPVCirc7JalovaMoc_L2 | LONG | IOD_TPV_TCP | 4649 | 44649 | Circ7JalovaMoc_L2
TPVCirc7JalovaMoc_L3 | LONG | IOD_TPV_TCP | 4651 | 44651 | Circ7JalovaMoc_L3
TPVCirc7KapacitivnaEnergija | LONG | IOD_TPV_TCP | 4653 | 44653 | Circ7KapacitivnaEnergija
TPVCirc7KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 4655 | 44655 | Circ7KapacitivnaMoc_III
TPVCirc7MaximumDemand | LONG | IOD_TPV_TCP | 4657 | 44657 | Circ7MaximumDemand
TPVCirc7Napetost_L1_L2 | LONG | IOD_TPV_TCP | 4659 | 44659 | Circ7Napetost_L1_L2
TPVCirc7Napetost_L1_N | LONG | IOD_TPV_TCP | 4661 | 44661 | Circ7Napetost_L1_N
TPVCirc7Napetost_L2_L3 | LONG | IOD_TPV_TCP | 4663 | 44663 | Circ7Napetost_L2_L3
TPVCirc7Napetost_L2_N | LONG | IOD_TPV_TCP | 4665 | 44665 | Circ7Napetost_L2_N
TPVCirc7Napetost_L3_L1 | LONG | IOD_TPV_TCP | 4667 | 44667 | Circ7Napetost_L3_L1
TPVCirc7Napetost_L3_N | LONG | IOD_TPV_TCP | 4669 | 44669 | Circ7Napetost_L3_N
TPVCirc7NavideznaMoc_III | LONG | IOD_TPV_TCP | 4671 | 44671 | Circ7NavideznaMoc_III
TPVCirc7NicelniTok | LONG | IOD_TPV_TCP | 4673 | 44673 | Circ7NicelniTok
TPVCirc7PowerFactor_III | LONG | IOD_TPV_TCP | 4675 | 44675 | Circ7PowerFactor_III
TPVCirc7PowerFactor_L1 | LONG | IOD_TPV_TCP | 4677 | 44677 | Circ7PowerFactor_L1
TPVCirc7PowerFactor_L2 | LONG | IOD_TPV_TCP | 4679 | 44679 | Circ7PowerFactor_L2
TPVCirc7PowerFactor_L3 | LONG | IOD_TPV_TCP | 4681 | 44681 | Circ7PowerFactor_L3
TPVCirc7THDI_L1 | LONG | IOD_TPV_TCP | 4683 | 44683 | Circ7THDI_L1
TPVCirc7THDI_L2 | LONG | IOD_TPV_TCP | 4685 | 44685 | Circ7THDI_L2
TPVCirc7THDI_L3 | LONG | IOD_TPV_TCP | 4687 | 44687 | Circ7THDI_L3
TPVCirc7THDV_L1 | LONG | IOD_TPV_TCP | 4689 | 44689 | Circ7THDV_L1
TPVCirc7THDV_L2 | LONG | IOD_TPV_TCP | 4691 | 44691 | Circ7THDV_L2
TPVCirc7THDV_L3 | LONG | IOD_TPV_TCP | 4693 | 44693 | Circ7THDV_L3
TPVCirc7Tok_L1 | LONG | IOD_TPV_TCP | 4695 | 44695 | Circ7Tok_L1
TPVCirc7Tok_L2 | LONG | IOD_TPV_TCP | 4697 | 44697 | Circ7Tok_L2
TPVCirc7Tok_L3 | LONG | IOD_TPV_TCP | 4699 | 44699 | Circ7Tok_L3
TPVCirc7TokPovprecje_III | LONG | IOD_TPV_TCP | 4701 | 44701 | Circ7TokPovprecje_III
TPVCirc8CosFi_III | LONG | IOD_TPV_TCP | 4703 | 44703 | Circ8CosFi_III
TPVCirc8DelovnaEnergija | LONG | IOD_TPV_TCP | 4705 | 44705 | Circ8DelovnaEnergija
TPVCirc8DelovnaMoc_III | LONG | IOD_TPV_TCP | 4707 | 44707 | Circ8DelovnaMoc_III
TPVCirc8DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 4709 | 44709 | Circ8DelovnaMoc_L1
TPVCirc8DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 4711 | 44711 | Circ8DelovnaMoc_L2
TPVCirc8DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 4713 | 44713 | Circ8DelovnaMoc_L3
TPVCirc8Frekvenca_L1 | LONG | IOD_TPV_TCP | 4715 | 44715 | Circ8Frekvenca_L1
TPVCirc8InduktivnaEnergija | LONG | IOD_TPV_TCP | 4717 | 44717 | Circ8InduktivnaEnergija
TPVCirc8InduktivnaMoc_III | LONG | IOD_TPV_TCP | 4719 | 44719 | Circ8InduktivnaMoc_III
TPVCirc8JalovaMoc_L1 | LONG | IOD_TPV_TCP | 4721 | 44721 | Circ8JalovaMoc_L1
TPVCirc8JalovaMoc_L2 | LONG | IOD_TPV_TCP | 4723 | 44723 | Circ8JalovaMoc_L2
TPVCirc8JalovaMoc_L3 | LONG | IOD_TPV_TCP | 4725 | 44725 | Circ8JalovaMoc_L3
TPVCirc8KapacitivnaEnergija | LONG | IOD_TPV_TCP | 4727 | 44727 | Circ8KapacitivnaEnergija
TPVCirc8KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 4729 | 44729 | Circ8KapacitivnaMoc_III
TPVCirc8MaximumDemand | LONG | IOD_TPV_TCP | 4731 | 44731 | Circ8MaximumDemand
TPVCirc8Napetost_L1_L2 | LONG | IOD_TPV_TCP | 4733 | 44733 | Circ8Napetost_L1_L2
TPVCirc8Napetost_L1_N | LONG | IOD_TPV_TCP | 4735 | 44735 | Circ8Napetost_L1_N
TPVCirc8Napetost_L2_L3 | LONG | IOD_TPV_TCP | 4737 | 44737 | Circ8Napetost_L2_L3
TPVCirc8Napetost_L2_N | LONG | IOD_TPV_TCP | 4739 | 44739 | Circ8Napetost_L2_N
TPVCirc8Napetost_L3_L1 | LONG | IOD_TPV_TCP | 4741 | 44741 | Circ8Napetost_L3_L1
TPVCirc8Napetost_L3_N | LONG | IOD_TPV_TCP | 4743 | 44743 | Circ8Napetost_L3_N
TPVCirc8NavideznaMoc_III | LONG | IOD_TPV_TCP | 4745 | 44745 | Circ8NavideznaMoc_III
TPVCirc8NicelniTok | LONG | IOD_TPV_TCP | 4747 | 44747 | Circ8NicelniTok
TPVCirc8PowerFactor_III | LONG | IOD_TPV_TCP | 4749 | 44749 | Circ8PowerFactor_III
TPVCirc8PowerFactor_L1 | LONG | IOD_TPV_TCP | 4751 | 44751 | Circ8PowerFactor_L1
TPVCirc8PowerFactor_L2 | LONG | IOD_TPV_TCP | 4753 | 44753 | Circ8PowerFactor_L2
TPVCirc8PowerFactor_L3 | LONG | IOD_TPV_TCP | 4755 | 44755 | Circ8PowerFactor_L3
TPVCirc8THDI_L1 | LONG | IOD_TPV_TCP | 4757 | 44757 | Circ8THDI_L1
TPVCirc8THDI_L2 | LONG | IOD_TPV_TCP | 4759 | 44759 | Circ8THDI_L2
TPVCirc8THDI_L3 | LONG | IOD_TPV_TCP | 4761 | 44761 | Circ8THDI_L3
TPVCirc8THDV_L1 | LONG | IOD_TPV_TCP | 4763 | 44763 | Circ8THDV_L1
TPVCirc8THDV_L2 | LONG | IOD_TPV_TCP | 4765 | 44765 | Circ8THDV_L2
TPVCirc8THDV_L3 | LONG | IOD_TPV_TCP | 4767 | 44767 | Circ8THDV_L3
TPVCirc8Tok_L1 | LONG | IOD_TPV_TCP | 4769 | 44769 | Circ8Tok_L1
TPVCirc8Tok_L2 | LONG | IOD_TPV_TCP | 4771 | 44771 | Circ8Tok_L2
TPVCirc8Tok_L3 | LONG | IOD_TPV_TCP | 4773 | 44773 | Circ8Tok_L3
TPVCirc8TokPovprecje_III | LONG | IOD_TPV_TCP | 4775 | 44775 | Circ8TokPovprecje_III
TPVCirc9CosFi_III | LONG | IOD_TPV_TCP | 4777 | 44777 | Circ9CosFi_III
TPVCirc9DelovnaEnergija | LONG | IOD_TPV_TCP | 4779 | 44779 | Circ9DelovnaEnergija
TPVCirc9DelovnaMoc_III | LONG | IOD_TPV_TCP | 4781 | 44781 | Circ9DelovnaMoc_III
TPVCirc9DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 4783 | 44783 | Circ9DelovnaMoc_L1
TPVCirc9DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 4785 | 44785 | Circ9DelovnaMoc_L2
TPVCirc9DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 4787 | 44787 | Circ9DelovnaMoc_L3
TPVCirc9Frekvenca_L1 | LONG | IOD_TPV_TCP | 4789 | 44789 | Circ9Frekvenca_L1
TPVCirc9InduktivnaEnergija | LONG | IOD_TPV_TCP | 4791 | 44791 | Circ9InduktivnaEnergija
TPVCirc9InduktivnaMoc_III | LONG | IOD_TPV_TCP | 4793 | 44793 | Circ9InduktivnaMoc_III
TPVCirc9JalovaMoc_L1 | LONG | IOD_TPV_TCP | 4795 | 44795 | Circ9JalovaMoc_L1
TPVCirc9JalovaMoc_L2 | LONG | IOD_TPV_TCP | 4797 | 44797 | Circ9JalovaMoc_L2
TPVCirc9JalovaMoc_L3 | LONG | IOD_TPV_TCP | 4799 | 44799 | Circ9JalovaMoc_L3
TPVCirc9KapacitivnaEnergija | LONG | IOD_TPV_TCP | 4801 | 44801 | Circ9KapacitivnaEnergija
TPVCirc9KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 4803 | 44803 | Circ9KapacitivnaMoc_III
TPVCirc9MaximumDemand | LONG | IOD_TPV_TCP | 4805 | 44805 | Circ9MaximumDemand
TPVCirc9Napetost_L1_L2 | LONG | IOD_TPV_TCP | 4807 | 44807 | Circ9Napetost_L1_L2
TPVCirc9Napetost_L1_N | LONG | IOD_TPV_TCP | 4809 | 44809 | Circ9Napetost_L1_N
TPVCirc9Napetost_L2_L3 | LONG | IOD_TPV_TCP | 4811 | 44811 | Circ9Napetost_L2_L3
TPVCirc9Napetost_L2_N | LONG | IOD_TPV_TCP | 4813 | 44813 | Circ9Napetost_L2_N
TPVCirc9Napetost_L3_L1 | LONG | IOD_TPV_TCP | 4815 | 44815 | Circ9Napetost_L3_L1
TPVCirc9Napetost_L3_N | LONG | IOD_TPV_TCP | 4817 | 44817 | Circ9Napetost_L3_N
TPVCirc9NavideznaMoc_III | LONG | IOD_TPV_TCP | 4819 | 44819 | Circ9NavideznaMoc_III
TPVCirc9NicelniTok | LONG | IOD_TPV_TCP | 4821 | 44821 | Circ9NicelniTok
TPVCirc9PowerFactor_III | LONG | IOD_TPV_TCP | 4823 | 44823 | Circ9PowerFactor_III
TPVCirc9PowerFactor_L1 | LONG | IOD_TPV_TCP | 4825 | 44825 | Circ9PowerFactor_L1
TPVCirc9PowerFactor_L2 | LONG | IOD_TPV_TCP | 4827 | 44827 | Circ9PowerFactor_L2
TPVCirc9PowerFactor_L3 | LONG | IOD_TPV_TCP | 4829 | 44829 | Circ9PowerFactor_L3
TPVCirc9THDI_L1 | LONG | IOD_TPV_TCP | 4831 | 44831 | Circ9THDI_L1
TPVCirc9THDI_L2 | LONG | IOD_TPV_TCP | 4833 | 44833 | Circ9THDI_L2
TPVCirc9THDI_L3 | LONG | IOD_TPV_TCP | 4835 | 44835 | Circ9THDI_L3
TPVCirc9THDV_L1 | LONG | IOD_TPV_TCP | 4837 | 44837 | Circ9THDV_L1
TPVCirc9THDV_L2 | LONG | IOD_TPV_TCP | 4839 | 44839 | Circ9THDV_L2
TPVCirc9THDV_L3 | LONG | IOD_TPV_TCP | 4841 | 44841 | Circ9THDV_L3
TPVCirc9Tok_L1 | LONG | IOD_TPV_TCP | 4843 | 44843 | Circ9Tok_L1
TPVCirc9Tok_L2 | LONG | IOD_TPV_TCP | 4845 | 44845 | Circ9Tok_L2
TPVCirc9Tok_L3 | LONG | IOD_TPV_TCP | 4847 | 44847 | Circ9Tok_L3
TPVCirc9TokPovprecje_III | LONG | IOD_TPV_TCP | 4849 | 44849 | Circ9TokPovprecje_III
TPVDW_Napake1 | LONG | IOD_TPV_TCP | 4851 | 44851 | DW_Napake1
TPVDW_Napake2 | LONG | IOD_TPV_TCP | 4853 | 44853 | DW_Napake2
TPVDW_Napake3 | LONG | IOD_TPV_TCP | 4855 | 44855 | DW_Napake3
TPV_Generator_earth_currentA1 | LONG | IOD_TPV_TCP | 4857 | 44857 | Generator_earth_currentA1
TPV_Generator_earth_currentA2 | LONG | IOD_TPV_TCP | 4859 | 44859 | Generator_earth_currentA2
TPV_Generator_L1_currentA1 | LONG | IOD_TPV_TCP | 4861 | 44861 | Generator_L1_currentA1
TPV_Generator_L1_currentA2 | LONG | IOD_TPV_TCP | 4863 | 44863 | Generator_L1_currentA2
TPV_Generator_L1_L2_voltageA1 | LONG | IOD_TPV_TCP | 4865 | 44865 | Generator_L1_L2_voltageA1
TPV_Generator_L1_L2_voltageA2 | LONG | IOD_TPV_TCP | 4867 | 44867 | Generator_L1_L2_voltageA2
TPV_Generator_L1_N_voltageA1 | LONG | IOD_TPV_TCP | 4869 | 44869 | Generator_L1_N_voltageA1
TPV_Generator_L1_N_voltageA2 | LONG | IOD_TPV_TCP | 4871 | 44871 | Generator_L1_N_voltageA2
TPV_Generator_L1_wattsA1 | LONG | IOD_TPV_TCP | 4873 | 44873 | Generator_L1_wattsA1
TPV_Generator_L1_wattsA2 | LONG | IOD_TPV_TCP | 4875 | 44875 | Generator_L1_wattsA2
TPV_Generator_L2_currentA1 | LONG | IOD_TPV_TCP | 4877 | 44877 | Generator_L2_currentA1
TPV_Generator_L2_currentA2 | LONG | IOD_TPV_TCP | 4879 | 44879 | Generator_L2_currentA2
TPV_Generator_L2_L3_voltageA1 | LONG | IOD_TPV_TCP | 4881 | 44881 | Generator_L2_L3_voltageA1
TPV_Generator_L2_L3_voltageA2 | LONG | IOD_TPV_TCP | 4883 | 44883 | Generator_L2_L3_voltageA2
TPV_Generator_L2_N_voltageA1 | LONG | IOD_TPV_TCP | 4885 | 44885 | Generator_L2_N_voltageA1
TPV_Generator_L2_N_voltageA2 | LONG | IOD_TPV_TCP | 4887 | 44887 | Generator_L2_N_voltageA2
TPV_Generator_L2_wattsA1 | LONG | IOD_TPV_TCP | 4889 | 44889 | Generator_L2_wattsA1
TPV_Generator_L2_wattsA2 | LONG | IOD_TPV_TCP | 4891 | 44891 | Generator_L2_wattsA2
TPV_Generator_L3_currentA1 | LONG | IOD_TPV_TCP | 4893 | 44893 | Generator_L3_currentA1
TPV_Generator_L3_currentA2 | LONG | IOD_TPV_TCP | 4895 | 44895 | Generator_L3_currentA2
TPV_Generator_L3_L1_voltageA1 | LONG | IOD_TPV_TCP | 4897 | 44897 | Generator_L3_L1_voltageA1
TPV_Generator_L3_L1_voltageA2 | LONG | IOD_TPV_TCP | 4899 | 44899 | Generator_L3_L1_voltageA2
TPV_Generator_L3_N_voltageA1 | LONG | IOD_TPV_TCP | 4901 | 44901 | Generator_L3_N_voltageA1
TPV_Generator_L3_N_voltageA2 | LONG | IOD_TPV_TCP | 4903 | 44903 | Generator_L3_N_voltageA2
TPV_Generator_L3_wattsA1 | LONG | IOD_TPV_TCP | 4905 | 44905 | Generator_L3_wattsA1
TPV_Generator_L3_wattsA2 | LONG | IOD_TPV_TCP | 4907 | 44907 | Generator_L3_wattsA2
TPVCirc14NicelniTok_NovoSkaliranje | LONG | IOD_TPV_TCP | 4909 | 44909 | Circ14NicelniTok
TPVCirc14Tok_L1_NovoSkaliranje | LONG | IOD_TPV_TCP | 4911 | 44911 | Circ14Tok_L1
TPVCirc14Tok_L2_NovoSkaliranje | LONG | IOD_TPV_TCP | 4913 | 44913 | Circ14Tok_L2
TPVCirc14Tok_L3_NovoSkaliranje | LONG | IOD_TPV_TCP | 4915 | 44915 | Circ14Tok_L3
TPVCirc8NicelniTok_NovoSkaliranje | LONG | IOD_TPV_TCP | 4917 | 44917 | Circ8NicelniTok
TPVCirc8Tok_L1_NovoSkaliranje | LONG | IOD_TPV_TCP | 4919 | 44919 | Circ8Tok_L1
TPVCirc8Tok_L2_NovoSkaliranje | LONG | IOD_TPV_TCP | 4921 | 44921 | Circ8Tok_L2
TPVCirc8Tok_L3_NovoSkaliranje | LONG | IOD_TPV_TCP | 4923 | 44923 | Circ8Tok_L3
TPVCirc9NicelniTok_NovoSkaliranje | LONG | IOD_TPV_TCP | 4925 | 44925 | Circ9NicelniTok
TPVCirc9Tok_L1_NovoSkaliranje | LONG | IOD_TPV_TCP | 4927 | 44927 | Circ9Tok_L1
TPVCirc9Tok_L2_NovoSkaliranje | LONG | IOD_TPV_TCP | 4929 | 44929 | Circ9Tok_L2
TPVCirc9Tok_L3_NovoSkaliranje | LONG | IOD_TPV_TCP | 4931 | 44931 | Circ9Tok_L3
TPVCirc1MaximumDemandA2 | LONG | IOD_TPV_TCP | 4933 | 44933 | Circ1MaximumDemandA2
TPVCirc1MaximumDemandA3 | LONG | IOD_TPV_TCP | 4935 | 44935 | Circ1MaximumDemandA3
TPVCirc2MaximumDemandA2 | LONG | IOD_TPV_TCP | 4937 | 44937 | Circ2MaximumDemandA2
TPVCirc2MaximumDemandA3 | LONG | IOD_TPV_TCP | 4939 | 44939 | Circ2MaximumDemandA3
TPVCirc3MaximumDemandA2 | LONG | IOD_TPV_TCP | 4941 | 44941 | Circ3MaximumDemandA2
TPVCirc3MaximumDemandA3 | LONG | IOD_TPV_TCP | 4943 | 44943 | Circ3MaximumDemandA3
TPVCirc4MaximumDemandA2 | LONG | IOD_TPV_TCP | 4945 | 44945 | Circ4MaximumDemandA2
TPVCirc4MaximumDemandA3 | LONG | IOD_TPV_TCP | 4947 | 44947 | Circ4MaximumDemandA3
TPVCirc5MaximumDemandA2 | LONG | IOD_TPV_TCP | 4949 | 44949 | Circ5MaximumDemandA2
TPVCirc5MaximumDemandA3 | LONG | IOD_TPV_TCP | 4951 | 44951 | Circ5MaximumDemandA3
TPVCirc6MaximumDemandA2 | LONG | IOD_TPV_TCP | 4953 | 44953 | Circ6MaximumDemandA2
TPVCirc6MaximumDemandA3 | LONG | IOD_TPV_TCP | 4955 | 44955 | Circ6MaximumDemandA3
TPVCirc7MaximumDemandA2 | LONG | IOD_TPV_TCP | 4957 | 44957 | Circ7MaximumDemandA2
TPVCirc7MaximumDemandA3 | LONG | IOD_TPV_TCP | 4959 | 44959 | Circ7MaximumDemandA3
TPVCirc8MaximumDemandA2 | LONG | IOD_TPV_TCP | 4961 | 44961 | Circ8MaximumDemandA2
TPVCirc8MaximumDemandA3 | LONG | IOD_TPV_TCP | 4963 | 44963 | Circ8MaximumDemandA3
TPVCirc9MaximumDemandA2 | LONG | IOD_TPV_TCP | 4965 | 44965 | Circ9MaximumDemandA2
TPVCirc9MaximumDemandA3 | LONG | IOD_TPV_TCP | 4967 | 44967 | Circ9MaximumDemandA3
TPVCirc10MaximumDemandA2 | LONG | IOD_TPV_TCP | 4969 | 44969 | Circ10MaximumDemandA2
TPVCirc10MaximumDemandA3 | LONG | IOD_TPV_TCP | 4971 | 44971 | Circ10MaximumDemandA3
TPVCirc11MaximumDemandA2 | LONG | IOD_TPV_TCP | 4973 | 44973 | Circ11MaximumDemandA2
TPVCirc11MaximumDemandA3 | LONG | IOD_TPV_TCP | 4975 | 44975 | Circ11MaximumDemandA3
TPVCirc12MaximumDemandA2 | LONG | IOD_TPV_TCP | 4977 | 44977 | Circ12MaximumDemandA2
TPVCirc12MaximumDemandA3 | LONG | IOD_TPV_TCP | 4979 | 44979 | Circ12MaximumDemandA3
TPVCirc13MaximumDemandA2 | LONG | IOD_TPV_TCP | 4981 | 44981 | Circ13MaximumDemandA2
TPVCirc13MaximumDemandA3 | LONG | IOD_TPV_TCP | 4983 | 44983 | Circ13MaximumDemandA3
TPVCirc14MaximumDemandA2 | LONG | IOD_TPV_TCP | 4985 | 44985 | Circ14MaximumDemandA2
TPVCirc14MaximumDemandA3 | LONG | IOD_TPV_TCP | 4987 | 44987 | Circ14MaximumDemandA3
TPVCirc15MaximumDemandA2 | LONG | IOD_TPV_TCP | 4989 | 44989 | Circ15MaximumDemandA2
TPVCirc15MaximumDemandA3 | LONG | IOD_TPV_TCP | 4991 | 44991 | Circ15MaximumDemandA3
TPVCirc16MaximumDemandA2 | LONG | IOD_TPV_TCP | 4993 | 44993 | Circ16MaximumDemandA2
TPVCirc16MaximumDemandA3 | LONG | IOD_TPV_TCP | 4995 | 44995 | Circ16MaximumDemandA3
TPVCirc17MaximumDemandA2 | LONG | IOD_TPV_TCP | 4997 | 44997 | Circ17MaximumDemandA2
TPVCirc17MaximumDemandA3 | LONG | IOD_TPV_TCP | 4999 | 44999 | Circ17MaximumDemandA3
TPVCirc18MaximumDemandA2 | LONG | IOD_TPV_TCP | 5001 | 45001 | Circ18MaximumDemandA2
TPVCirc18MaximumDemandA3 | LONG | IOD_TPV_TCP | 5003 | 45003 | Circ18MaximumDemandA3
TPVCirc19MaximumDemandA2 | LONG | IOD_TPV_TCP | 5005 | 45005 | Circ19MaximumDemandA2
TPVCirc19MaximumDemandA3 | LONG | IOD_TPV_TCP | 5007 | 45007 | Circ19MaximumDemandA3
TPVCirc20MaximumDemandA2 | LONG | IOD_TPV_TCP | 5009 | 45009 | Circ20MaximumDemandA2
TPVCirc20MaximumDemandA3 | LONG | IOD_TPV_TCP | 5011 | 45011 | Circ20MaximumDemandA3
TPVCirc21MaximumDemandA2 | LONG | IOD_TPV_TCP | 5013 | 45013 | Circ21MaximumDemandA2
TPVCirc21MaximumDemandA3 | LONG | IOD_TPV_TCP | 5015 | 45015 | Circ21MaximumDemandA3
TPVCirc22MaximumDemandA2 | LONG | IOD_TPV_TCP | 5017 | 45017 | Circ22MaximumDemandA2
TPVCirc22MaximumDemandA3 | LONG | IOD_TPV_TCP | 5019 | 45019 | Circ22MaximumDemandA3
TPVCirc23MaximumDemandA2 | LONG | IOD_TPV_TCP | 5021 | 45021 | Circ23MaximumDemandA2
TPVCirc23MaximumDemandA3 | LONG | IOD_TPV_TCP | 5023 | 45023 | Circ23MaximumDemandA3
TPVCirc24MaximumDemandA2 | LONG | IOD_TPV_TCP | 5025 | 45025 | Circ24MaximumDemandA2
TPVCirc24MaximumDemandA3 | LONG | IOD_TPV_TCP | 5027 | 45027 | Circ24MaximumDemandA3
TPVCirc25MaximumDemandA2 | LONG | IOD_TPV_TCP | 5029 | 45029 | Circ25MaximumDemandA2
TPVCirc25MaximumDemandA3 | LONG | IOD_TPV_TCP | 5031 | 45031 | Circ25MaximumDemandA3
TPVCirc1RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5033 | 45033 | Circ[1].RazEner_D_SCADA
TPVCirc1RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5035 | 45035 | Circ[1].RazEner_T_SCADA
TPVCirc1RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5037 | 45037 | Circ[1].RazEner_M_SCADA
TPVCirc2RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5039 | 45039 | Circ[2].RazEner_D_SCADA
TPVCirc2RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5041 | 45041 | Circ[2].RazEner_T_SCADA
TPVCirc2RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5043 | 45043 | Circ[2].RazEner_M_SCADA
TPVCirc3RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5045 | 45045 | Circ[3].RazEner_D_SCADA
TPVCirc3RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5047 | 45047 | Circ[3].RazEner_T_SCADA
TPVCirc3RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5049 | 45049 | Circ[3].RazEner_M_SCADA
TPVCirc4RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5051 | 45051 | Circ[4].RazEner_D_SCADA
TPVCirc4RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5053 | 45053 | Circ[4].RazEner_T_SCADA
TPVCirc4RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5055 | 45055 | Circ[4].RazEner_M_SCADA
TPVCirc5RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5057 | 45057 | Circ[5].RazEner_D_SCADA
TPVCirc5RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5059 | 45059 | Circ[5].RazEner_T_SCADA
TPVCirc5RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5061 | 45061 | Circ[5].RazEner_M_SCADA
TPVCirc6RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5063 | 45063 | Circ[6].RazEner_D_SCADA
TPVCirc6RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5065 | 45065 | Circ[6].RazEner_T_SCADA
TPVCirc6RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5067 | 45067 | Circ[6].RazEner_M_SCADA
TPVCirc7RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5069 | 45069 | Circ[7].RazEner_D_SCADA
TPVCirc7RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5071 | 45071 | Circ[7].RazEner_T_SCADA
TPVCirc7RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5073 | 45073 | Circ[7].RazEner_M_SCADA
TPVCirc8RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5075 | 45075 | Circ[8].RazEner_D_SCADA
TPVCirc8RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5077 | 45077 | Circ[8].RazEner_T_SCADA
TPVCirc8RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5079 | 45079 | Circ[8].RazEner_M_SCADA
TPVCirc9RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5081 | 45081 | Circ[9].RazEner_D_SCADA
TPVCirc9RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5083 | 45083 | Circ[9].RazEner_T_SCADA
TPVCirc9RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5085 | 45085 | Circ[9].RazEner_M_SCADA
TPVCirc10RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5087 | 45087 | Circ[10].RazEner_D_SCADA
TPVCirc10RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5089 | 45089 | Circ[10].RazEner_T_SCADA
TPVCirc10RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5091 | 45091 | Circ[10].RazEner_M_SCADA
TPVCirc11RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5093 | 45093 | Circ[11].RazEner_D_SCADA
TPVCirc11RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5095 | 45095 | Circ[11].RazEner_T_SCADA
TPVCirc11RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5097 | 45097 | Circ[11].RazEner_M_SCADA
TPVCirc12RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5099 | 45099 | Circ[12].RazEner_D_SCADA
TPVCirc12RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5101 | 45101 | Circ[12].RazEner_T_SCADA
TPVCirc12RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5103 | 45103 | Circ[12].RazEner_M_SCADA
TPVCirc13RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5105 | 45105 | Circ[13].RazEner_D_SCADA
TPVCirc13RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5107 | 45107 | Circ[13].RazEner_T_SCADA
TPVCirc13RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5109 | 45109 | Circ[13].RazEner_M_SCADA
TPVCirc14RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5111 | 45111 | Circ[14].RazEner_D_SCADA
TPVCirc14RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5113 | 45113 | Circ[14].RazEner_T_SCADA
TPVCirc14RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5115 | 45115 | Circ[14].RazEner_M_SCADA
TPVCirc15RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5117 | 45117 | Circ[15].RazEner_D_SCADA
TPVCirc15RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5119 | 45119 | Circ[15].RazEner_T_SCADA
TPVCirc15RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5121 | 45121 | Circ[15].RazEner_M_SCADA
TPVCirc16RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5123 | 45123 | Circ[16].RazEner_D_SCADA
TPVCirc16RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5125 | 45125 | Circ[16].RazEner_T_SCADA
TPVCirc16RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5127 | 45127 | Circ[16].RazEner_M_SCADA
TPVCirc17RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5129 | 45129 | Circ[17].RazEner_D_SCADA
TPVCirc17RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5131 | 45131 | Circ[17].RazEner_T_SCADA
TPVCirc17RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5133 | 45133 | Circ[17].RazEner_M_SCADA
TPVCirc18RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5135 | 45135 | Circ[18].RazEner_D_SCADA
TPVCirc18RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5137 | 45137 | Circ[18].RazEner_T_SCADA
TPVCirc18RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5139 | 45139 | Circ[18].RazEner_M_SCADA
TPVCirc19RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5141 | 45141 | Circ[19].RazEner_D_SCADA
TPVCirc19RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5143 | 45143 | Circ[19].RazEner_T_SCADA
TPVCirc19RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5145 | 45145 | Circ[19].RazEner_M_SCADA
TPVCirc20RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5147 | 45147 | Circ[20].RazEner_D_SCADA
TPVCirc20RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5149 | 45149 | Circ[20].RazEner_T_SCADA
TPVCirc20RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5151 | 45151 | Circ[20].RazEner_M_SCADA
TPVCirc21RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5153 | 45153 | Circ[21].RazEner_D_SCADA
TPVCirc21RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5155 | 45155 | Circ[21].RazEner_T_SCADA
TPVCirc21RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5157 | 45157 | Circ[21].RazEner_M_SCADA
TPVCirc22RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5159 | 45159 | Circ[22].RazEner_D_SCADA
TPVCirc22RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5161 | 45161 | Circ[22].RazEner_T_SCADA
TPVCirc22RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5163 | 45163 | Circ[22].RazEner_M_SCADA
TPVCirc23RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5165 | 45165 | Circ[23].RazEner_D_SCADA
TPVCirc23RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5167 | 45167 | Circ[23].RazEner_T_SCADA
TPVCirc23RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5169 | 45169 | Circ[23].RazEner_M_SCADA
TPVCirc24RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5171 | 45171 | Circ[24].RazEner_D_SCADA
TPVCirc24RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5173 | 45173 | Circ[24].RazEner_T_SCADA
TPVCirc24RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5175 | 45175 | Circ[24].RazEner_M_SCADA
TPVCirc25RazEner_D_SCADA | LONG | IOD_TPV_TCP | 5177 | 45177 | Circ[25].RazEner_D_SCADA
TPVCirc25RazEner_T_SCADA | LONG | IOD_TPV_TCP | 5179 | 45179 | Circ[25].RazEner_T_SCADA
TPVCirc25RazEner_M_SCADA | LONG | IOD_TPV_TCP | 5181 | 45181 | Circ[25].RazEner_M_SCADA
TPVsinh_cas | STRING | IOD_TPV_TCP | 5001 | 45001[15] | cas_scada
TPVBattery_voltageA1 | UINT | IOD_TPV_TCP | 6001 | 46001 | Battery_voltageA1
TPVBattery_voltageA2 | UINT | IOD_TPV_TCP | 6002 | 46002 | Battery_voltageA2
TPVCharge_alternator_voltageA1 | UINT | IOD_TPV_TCP | 6003 | 46003 | Charge_alternator_voltageA1
TPVCharge_alternator_voltageA2 | UINT | IOD_TPV_TCP | 6004 | 46004 | Charge_alternator_voltageA2
TPVEngine_speedA1 | UINT | IOD_TPV_TCP | 6005 | 46005 | Engine_speedA1
TPVEngine_speedA2 | UINT | IOD_TPV_TCP | 6006 | 46006 | Engine_speedA2
TPV_Generator_frequencyA1 | UINT | IOD_TPV_TCP | 6007 | 46007 | Generator_frequencyA1
TPV_Generator_frequencyA2 | UINT | IOD_TPV_TCP | 6008 | 46008 | Generator_frequencyA2
TPV_Generator_phase_rotationA1 | UINT | IOD_TPV_TCP | 6009 | 46009 | Generator_phase_rotationA1
TPV_Generator_phase_rotationA2 | UINT | IOD_TPV_TCP | 6010 | 46010 | Generator_phase_rotationA2
TPVOil_pressureA1 | UINT | IOD_TPV_TCP | 6011 | 46011 | Oil_pressureA1
TPVOil_pressureA2 | UINT | IOD_TPV_TCP | 6012 | 46012 | Oil_pressureA2

## variable_new
TPVBattery_voltageA1 | UINT | IOD_TPV_TCP | 46001 | 0 | 400 | 0 | 40 | V | ##.#
TPVBattery_voltageA2 | UINT | IOD_TPV_TCP | 46002 | 0 | 400 | 0 | 40 | V | ##.#
TPVCharge_alternator_voltageA1 | UINT | IOD_TPV_TCP | 46003 | 0 | 400 | 0 | 40 | V | ##.#
TPVCharge_alternator_voltageA2 | UINT | IOD_TPV_TCP | 46004 | 0 | 400 | 0 | 40 | V | ###.#
TPVCirc10CosFi_III | LONG | IOD_TPV_TCP | 43001 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc10DelovnaEnergija | LONG | IOD_TPV_TCP | 43003 |  |  | 0
TPVCirc10DelovnaMoc_III | LONG | IOD_TPV_TCP | 43005 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc10DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 43007 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc10DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 43009 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc10DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 43011 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc10Frekvenca_L1 | LONG | IOD_TPV_TCP | 43013 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc10InduktivnaEnergija | LONG | IOD_TPV_TCP | 43015 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc10InduktivnaMoc_III | LONG | IOD_TPV_TCP | 43017 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc10JalovaMoc_L1 | LONG | IOD_TPV_TCP | 43019 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc10JalovaMoc_L2 | LONG | IOD_TPV_TCP | 43021 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc10JalovaMoc_L3 | LONG | IOD_TPV_TCP | 43023 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc10KapacitivnaEnergija | LONG | IOD_TPV_TCP | 43025 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc10KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 43027 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc10MaximumDemand | LONG | IOD_TPV_TCP | 43029 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc10Napetost_L1_L2 | LONG | IOD_TPV_TCP | 43031 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc10Napetost_L1_N | LONG | IOD_TPV_TCP | 43033 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc10Napetost_L2_L3 | LONG | IOD_TPV_TCP | 43035 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc10Napetost_L2_N | LONG | IOD_TPV_TCP | 43037 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc10Napetost_L3_L1 | LONG | IOD_TPV_TCP | 43039 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc10Napetost_L3_N | LONG | IOD_TPV_TCP | 43041 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc10NavideznaMoc_III | LONG | IOD_TPV_TCP | 43043 | 0 | 800 | 0 | 80 | kVA | ###.#
TPVCirc10NicelniTok | LONG | IOD_TPV_TCP | 43045 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc10PowerFactor_III | LONG | IOD_TPV_TCP | 43047 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc10PowerFactor_L1 | LONG | IOD_TPV_TCP | 43049 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc10PowerFactor_L2 | LONG | IOD_TPV_TCP | 43051 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc10PowerFactor_L3 | LONG | IOD_TPV_TCP | 43053 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc10THDI_L1 | LONG | IOD_TPV_TCP | 43055 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc10THDI_L2 | LONG | IOD_TPV_TCP | 43057 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc10THDI_L3 | LONG | IOD_TPV_TCP | 43059 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc10THDV_L1 | LONG | IOD_TPV_TCP | 43061 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc10THDV_L2 | LONG | IOD_TPV_TCP | 43063 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc10THDV_L3 | LONG | IOD_TPV_TCP | 43065 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc10Tok_L1 | LONG | IOD_TPV_TCP | 43067 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc10Tok_L2 | LONG | IOD_TPV_TCP | 43069 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc10Tok_L3 | LONG | IOD_TPV_TCP | 43071 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc10TokPovprecje_III | LONG | IOD_TPV_TCP | 43073 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc11CosFi_III | LONG | IOD_TPV_TCP | 43075 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc11DelovnaEnergija | LONG | IOD_TPV_TCP | 43077 |  |  | 0
TPVCirc11DelovnaMoc_III | LONG | IOD_TPV_TCP | 43079 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc11DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 43081 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc11DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 43083 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc11DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 43085 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc11Frekvenca_L1 | LONG | IOD_TPV_TCP | 43087 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc11InduktivnaEnergija | LONG | IOD_TPV_TCP | 43089 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc11InduktivnaMoc_III | LONG | IOD_TPV_TCP | 43091 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc11JalovaMoc_L1 | LONG | IOD_TPV_TCP | 43093 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc11JalovaMoc_L2 | LONG | IOD_TPV_TCP | 43095 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc11JalovaMoc_L3 | LONG | IOD_TPV_TCP | 43097 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc11KapacitivnaEnergija | LONG | IOD_TPV_TCP | 43099 | 0 | 10000 | 0 | 1000 | kW
TPVCirc11KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 43101 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc11MaximumDemand | LONG | IOD_TPV_TCP | 43103 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc11Napetost_L1_L2 | LONG | IOD_TPV_TCP | 43105 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc11Napetost_L1_N | LONG | IOD_TPV_TCP | 43107 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc11Napetost_L2_L3 | LONG | IOD_TPV_TCP | 43109 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc11Napetost_L2_N | LONG | IOD_TPV_TCP | 43111 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc11Napetost_L3_L1 | LONG | IOD_TPV_TCP | 43113 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc11Napetost_L3_N | LONG | IOD_TPV_TCP | 43115 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc11NavideznaMoc_III | LONG | IOD_TPV_TCP | 43117 | 0 | 800 | 0 | 80 | kVA | ###.#
TPVCirc11NicelniTok | LONG | IOD_TPV_TCP | 43119 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc11PowerFactor_III | LONG | IOD_TPV_TCP | 43121 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc11PowerFactor_L1 | LONG | IOD_TPV_TCP | 43123 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc11PowerFactor_L2 | LONG | IOD_TPV_TCP | 43125 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc11PowerFactor_L3 | LONG | IOD_TPV_TCP | 43127 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc11THDI_L1 | LONG | IOD_TPV_TCP | 43129 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc11THDI_L2 | LONG | IOD_TPV_TCP | 43131 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc11THDI_L3 | LONG | IOD_TPV_TCP | 43133 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc11THDV_L1 | LONG | IOD_TPV_TCP | 43135 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc11THDV_L2 | LONG | IOD_TPV_TCP | 43137 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc11THDV_L3 | LONG | IOD_TPV_TCP | 43139 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc11Tok_L1 | LONG | IOD_TPV_TCP | 43141 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc11Tok_L2 | LONG | IOD_TPV_TCP | 43143 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc11Tok_L3 | LONG | IOD_TPV_TCP | 43145 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc11TokPovprecje_III | LONG | IOD_TPV_TCP | 43147 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc12CosFi_III | LONG | IOD_TPV_TCP | 43149 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc12DelovnaEnergija | LONG | IOD_TPV_TCP | 43151 |  |  | 0
TPVCirc12DelovnaMoc_III | LONG | IOD_TPV_TCP | 43153 | 0 | 12000 | 0 | 1200 | kW | ###.#
TPVCirc12DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 43155 | 0 | 12000 | 0 | 1200 | kW | ###.#
TPVCirc12DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 43157 | 0 | 12000 | 0 | 1200 | kW | ###.#
TPVCirc12DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 43159 | 0 | 12000 | 0 | 1200 | kW | ###.#
TPVCirc12Frekvenca_L1 | LONG | IOD_TPV_TCP | 43161 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc12InduktivnaEnergija | LONG | IOD_TPV_TCP | 43163 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc12InduktivnaMoc_III | LONG | IOD_TPV_TCP | 43165 | 0 | 12000 | 0 | 1200 | kVAR | ###.#
TPVCirc12JalovaMoc_L1 | LONG | IOD_TPV_TCP | 43167 | 0 | 12000 | 0 | 1200 | kVAR | ###.#
TPVCirc12JalovaMoc_L2 | LONG | IOD_TPV_TCP | 43169 | 0 | 12000 | 0 | 1200 | kVAR | ###.#
TPVCirc12JalovaMoc_L3 | LONG | IOD_TPV_TCP | 43171 | 0 | 12000 | 0 | 1200 | kVAR | ###.#
TPVCirc12KapacitivnaEnergija | LONG | IOD_TPV_TCP | 43173
TPVCirc12KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 43175 | 0 | 10000 | 0 | 1000 | kVAR | ###.#
TPVCirc12MaximumDemand | LONG | IOD_TPV_TCP | 43177 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc12Napetost_L1_L2 | LONG | IOD_TPV_TCP | 43179 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc12Napetost_L1_N | LONG | IOD_TPV_TCP | 43181 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc12Napetost_L2_L3 | LONG | IOD_TPV_TCP | 43183 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc12Napetost_L2_N | LONG | IOD_TPV_TCP | 43185 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc12Napetost_L3_L1 | LONG | IOD_TPV_TCP | 43187 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc12Napetost_L3_N | LONG | IOD_TPV_TCP | 43189 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc12NavideznaMoc_III | LONG | IOD_TPV_TCP | 43191 | 0 | 12000 | 0 | 1200 | kVA | ###.#
TPVCirc12NicelniTok | LONG | IOD_TPV_TCP | 43193 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc12PowerFactor_III | LONG | IOD_TPV_TCP | 43195 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc12PowerFactor_L1 | LONG | IOD_TPV_TCP | 43197 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc12PowerFactor_L2 | LONG | IOD_TPV_TCP | 43199 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc12PowerFactor_L3 | LONG | IOD_TPV_TCP | 43201 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc12THDI_L1 | LONG | IOD_TPV_TCP | 43203 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc12THDI_L2 | LONG | IOD_TPV_TCP | 43205 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc12THDI_L3 | LONG | IOD_TPV_TCP | 43207 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc12THDV_L1 | LONG | IOD_TPV_TCP | 43209 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc12THDV_L2 | LONG | IOD_TPV_TCP | 43211 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc12THDV_L3 | LONG | IOD_TPV_TCP | 43213 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc12Tok_L1 | LONG | IOD_TPV_TCP | 43215 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc12Tok_L2 | LONG | IOD_TPV_TCP | 43217 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc12Tok_L3 | LONG | IOD_TPV_TCP | 43219 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc12TokPovprecje_III | LONG | IOD_TPV_TCP | 43221 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc13CosFi_III | LONG | IOD_TPV_TCP | 43223 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc13DelovnaEnergija | LONG | IOD_TPV_TCP | 43225 |  |  | 0
TPVCirc13DelovnaMoc_III | LONG | IOD_TPV_TCP | 43227 | 0 | 4000 | 0 | 400 | kW | ###.#
TPVCirc13DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 43229 | 0 | 4000 | 0 | 400 | kW | ###.#
TPVCirc13DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 43231 | 0 | 4000 | 0 | 400 | kW | ###.#
TPVCirc13DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 43233 | 0 | 4000 | 0 | 400 | kW | ###.#
TPVCirc13Frekvenca_L1 | LONG | IOD_TPV_TCP | 43235 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc13InduktivnaEnergija | LONG | IOD_TPV_TCP | 43237
TPVCirc13InduktivnaMoc_III | LONG | IOD_TPV_TCP | 43239 | 0 | 4000 | 0 | 400 | kVAR | ###.#
TPVCirc13JalovaMoc_L1 | LONG | IOD_TPV_TCP | 43241 | 0 | 4000 | 0 | 400 | kVAR | ###.#
TPVCirc13JalovaMoc_L2 | LONG | IOD_TPV_TCP | 43243 | 0 | 4000 | 0 | 400 | kVAR | ###.#
TPVCirc13JalovaMoc_L3 | LONG | IOD_TPV_TCP | 43245 | 0 | 4000 | 0 | 400 | kVAR | ###.#
TPVCirc13KapacitivnaEnergija | LONG | IOD_TPV_TCP | 43247 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc13KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 43249 | 0 | 10000 | 0 | 1000 | kVAR | ###.#
TPVCirc13MaximumDemand | LONG | IOD_TPV_TCP | 43251 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc13Napetost_L1_L2 | LONG | IOD_TPV_TCP | 43253 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc13Napetost_L1_N | LONG | IOD_TPV_TCP | 43255 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc13Napetost_L2_L3 | LONG | IOD_TPV_TCP | 43257 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc13Napetost_L2_N | LONG | IOD_TPV_TCP | 43259 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc13Napetost_L3_L1 | LONG | IOD_TPV_TCP | 43261 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc13Napetost_L3_N | LONG | IOD_TPV_TCP | 43263 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc13NavideznaMoc_III | LONG | IOD_TPV_TCP | 43265 | 0 | 4000 | 0 | 400 | kVA | ###.#
TPVCirc13NicelniTok | LONG | IOD_TPV_TCP | 43267 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc13PowerFactor_III | LONG | IOD_TPV_TCP | 43269 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc13PowerFactor_L1 | LONG | IOD_TPV_TCP | 43271 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc13PowerFactor_L2 | LONG | IOD_TPV_TCP | 43273 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc13PowerFactor_L3 | LONG | IOD_TPV_TCP | 43275 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc13THDI_L1 | LONG | IOD_TPV_TCP | 43277 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc13THDI_L2 | LONG | IOD_TPV_TCP | 43279 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc13THDI_L3 | LONG | IOD_TPV_TCP | 43281 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc13THDV_L1 | LONG | IOD_TPV_TCP | 43283 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc13THDV_L2 | LONG | IOD_TPV_TCP | 43285 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc13THDV_L3 | LONG | IOD_TPV_TCP | 43287 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc13Tok_L1 | LONG | IOD_TPV_TCP | 43289 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc13Tok_L2 | LONG | IOD_TPV_TCP | 43291 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc13Tok_L3 | LONG | IOD_TPV_TCP | 43293 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc13TokPovprecje_III | LONG | IOD_TPV_TCP | 43295 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc14CosFi_III | LONG | IOD_TPV_TCP | 43297 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc14DelovnaEnergija | LONG | IOD_TPV_TCP | 43299 |  |  | 0
TPVCirc14DelovnaMoc_III | LONG | IOD_TPV_TCP | 43301 | 0 | 4000 | 0 | 400 | kW | ###.#
TPVCirc14DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 43303 | 0 | 4000 | 0 | 400 | kW | ###.#
TPVCirc14DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 43305 | 0 | 4000 | 0 | 400 | kW | ###.#
TPVCirc14DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 43307 | 0 | 4000 | 0 | 400 | kW | ###.#
TPVCirc14Frekvenca_L1 | LONG | IOD_TPV_TCP | 43309 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc14InduktivnaEnergija | LONG | IOD_TPV_TCP | 43311 | [5 empty] | ###.#
TPVCirc14InduktivnaMoc_III | LONG | IOD_TPV_TCP | 43313 | 0 | 4000 | 0 | 400 | kVAR | ###.#
TPVCirc14JalovaMoc_L1 | LONG | IOD_TPV_TCP | 43315 | 0 | 4000 | 0 | 400 | kVAR | ###.#
TPVCirc14JalovaMoc_L2 | LONG | IOD_TPV_TCP | 43317 | 0 | 4000 | 0 | 400 | kVAR | ###.#
TPVCirc14JalovaMoc_L3 | LONG | IOD_TPV_TCP | 43319 | 0 | 4000 | 0 | 400 | kVAR | ###.#
TPVCirc14KapacitivnaEnergija | LONG | IOD_TPV_TCP | 43321 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc14KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 43323 | 0 | 10000 | 0 | 1000 | kVAR | ###.#
TPVCirc14MaximumDemand | LONG | IOD_TPV_TCP | 43325 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc14Napetost_L1_L2 | LONG | IOD_TPV_TCP | 43327 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc14Napetost_L1_N | LONG | IOD_TPV_TCP | 43329 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc14Napetost_L2_L3 | LONG | IOD_TPV_TCP | 43331 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc14Napetost_L2_N | LONG | IOD_TPV_TCP | 43333 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc14Napetost_L3_L1 | LONG | IOD_TPV_TCP | 43335 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc14Napetost_L3_N | LONG | IOD_TPV_TCP | 43337 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc14NavideznaMoc_III | LONG | IOD_TPV_TCP | 43339 | 0 | 4000 | 0 | 400 | kVA | ###.#
TPVCirc14NicelniTok | LONG | IOD_TPV_TCP | 43341 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc14PowerFactor_III | LONG | IOD_TPV_TCP | 43343 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc14PowerFactor_L1 | LONG | IOD_TPV_TCP | 43345 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc14PowerFactor_L2 | LONG | IOD_TPV_TCP | 43347 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc14PowerFactor_L3 | LONG | IOD_TPV_TCP | 43349 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc14THDI_L1 | LONG | IOD_TPV_TCP | 43351 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc14THDI_L2 | LONG | IOD_TPV_TCP | 43353 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc14THDI_L3 | LONG | IOD_TPV_TCP | 43355 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc14THDV_L1 | LONG | IOD_TPV_TCP | 43357 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc14THDV_L2 | LONG | IOD_TPV_TCP | 43359 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc14THDV_L3 | LONG | IOD_TPV_TCP | 43361 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc14Tok_L1 | LONG | IOD_TPV_TCP | 43363 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc14Tok_L2 | LONG | IOD_TPV_TCP | 43365 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc14Tok_L3 | LONG | IOD_TPV_TCP | 43367 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc14TokPovprecje_III | LONG | IOD_TPV_TCP | 43369 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc15CosFi_III | LONG | IOD_TPV_TCP | 43371 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc15DelovnaEnergija | LONG | IOD_TPV_TCP | 43373 |  |  | 0
TPVCirc15DelovnaMoc_III | LONG | IOD_TPV_TCP | 43375 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc15DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 43377 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc15DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 43379 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc15DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 43381 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc15Frekvenca_L1 | LONG | IOD_TPV_TCP | 43383 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc15InduktivnaEnergija | LONG | IOD_TPV_TCP | 43385 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc15InduktivnaMoc_III | LONG | IOD_TPV_TCP | 43387 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc15JalovaMoc_L1 | LONG | IOD_TPV_TCP | 43389 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc15JalovaMoc_L2 | LONG | IOD_TPV_TCP | 43391 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc15JalovaMoc_L3 | LONG | IOD_TPV_TCP | 43393 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc15KapacitivnaEnergija | LONG | IOD_TPV_TCP | 43395 | 0 | 10000 | 0 | 1000 | kW
TPVCirc15KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 43397 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc15MaximumDemand | LONG | IOD_TPV_TCP | 43399 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc15Napetost_L1_L2 | LONG | IOD_TPV_TCP | 43401 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc15Napetost_L1_N | LONG | IOD_TPV_TCP | 43403 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc15Napetost_L2_L3 | LONG | IOD_TPV_TCP | 43405 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc15Napetost_L2_N | LONG | IOD_TPV_TCP | 43407 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc15Napetost_L3_L1 | LONG | IOD_TPV_TCP | 43409 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc15Napetost_L3_N | LONG | IOD_TPV_TCP | 43411 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc15NavideznaMoc_III | LONG | IOD_TPV_TCP | 43413 | 0 | 800 | 0 | 80 | kVA | ###.#
TPVCirc15NicelniTok | LONG | IOD_TPV_TCP | 43415 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc15PowerFactor_III | LONG | IOD_TPV_TCP | 43417 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc15PowerFactor_L1 | LONG | IOD_TPV_TCP | 43419 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc15PowerFactor_L2 | LONG | IOD_TPV_TCP | 43421 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc15PowerFactor_L3 | LONG | IOD_TPV_TCP | 43423 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc15THDI_L1 | LONG | IOD_TPV_TCP | 43425 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc15THDI_L2 | LONG | IOD_TPV_TCP | 43427 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc15THDI_L3 | LONG | IOD_TPV_TCP | 43429 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc15THDV_L1 | LONG | IOD_TPV_TCP | 43431 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc15THDV_L2 | LONG | IOD_TPV_TCP | 43433 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc15THDV_L3 | LONG | IOD_TPV_TCP | 43435 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc15Tok_L1 | LONG | IOD_TPV_TCP | 43437 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc15Tok_L2 | LONG | IOD_TPV_TCP | 43439 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc15Tok_L3 | LONG | IOD_TPV_TCP | 43441 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc15TokPovprecje_III | LONG | IOD_TPV_TCP | 43443 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc16CosFi_III | LONG | IOD_TPV_TCP | 43445 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc16DelovnaEnergija | LONG | IOD_TPV_TCP | 43447 |  |  | 0
TPVCirc16DelovnaMoc_III | LONG | IOD_TPV_TCP | 43449 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc16DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 43451 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc16DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 43453 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc16DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 43455 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc16Frekvenca_L1 | LONG | IOD_TPV_TCP | 43457 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc16InduktivnaEnergija | LONG | IOD_TPV_TCP | 43459 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc16InduktivnaMoc_III | LONG | IOD_TPV_TCP | 43461 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc16JalovaMoc_L1 | LONG | IOD_TPV_TCP | 43463 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc16JalovaMoc_L2 | LONG | IOD_TPV_TCP | 43465 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc16JalovaMoc_L3 | LONG | IOD_TPV_TCP | 43467 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc16KapacitivnaEnergija | LONG | IOD_TPV_TCP | 43469 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc16KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 43471 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc16MaximumDemand | LONG | IOD_TPV_TCP | 43473 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc16Napetost_L1_L2 | LONG | IOD_TPV_TCP | 43475 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc16Napetost_L1_N | LONG | IOD_TPV_TCP | 43477 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc16Napetost_L2_L3 | LONG | IOD_TPV_TCP | 43479 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc16Napetost_L2_N | LONG | IOD_TPV_TCP | 43481 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc16Napetost_L3_L1 | LONG | IOD_TPV_TCP | 43483 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc16Napetost_L3_N | LONG | IOD_TPV_TCP | 43485 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc16NavideznaMoc_III | LONG | IOD_TPV_TCP | 43487 | 0 | 1200 | 0 | 120 | kVA | ###.#
TPVCirc16NicelniTok | LONG | IOD_TPV_TCP | 43489 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc16PowerFactor_III | LONG | IOD_TPV_TCP | 43491 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc16PowerFactor_L1 | LONG | IOD_TPV_TCP | 43493 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc16PowerFactor_L2 | LONG | IOD_TPV_TCP | 43495 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc16PowerFactor_L3 | LONG | IOD_TPV_TCP | 43497 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc16THDI_L1 | LONG | IOD_TPV_TCP | 43499 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc16THDI_L2 | LONG | IOD_TPV_TCP | 43501 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc16THDI_L3 | LONG | IOD_TPV_TCP | 43503 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc16THDV_L1 | LONG | IOD_TPV_TCP | 43505 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc16THDV_L2 | LONG | IOD_TPV_TCP | 43507 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc16THDV_L3 | LONG | IOD_TPV_TCP | 43509 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc16Tok_L1 | LONG | IOD_TPV_TCP | 43511 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc16Tok_L2 | LONG | IOD_TPV_TCP | 43513 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc16Tok_L3 | LONG | IOD_TPV_TCP | 43515 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc16TokPovprecje_III | LONG | IOD_TPV_TCP | 43517 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc17CosFi_III | LONG | IOD_TPV_TCP | 43519 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc17DelovnaEnergija | LONG | IOD_TPV_TCP | 43521 |  |  | 0
TPVCirc17DelovnaMoc_III | LONG | IOD_TPV_TCP | 43523 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc17DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 43525 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc17DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 43527 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc17DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 43529 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc17Frekvenca_L1 | LONG | IOD_TPV_TCP | 43531 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc17InduktivnaEnergija | LONG | IOD_TPV_TCP | 43533 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc17InduktivnaMoc_III | LONG | IOD_TPV_TCP | 43535 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc17JalovaMoc_L1 | LONG | IOD_TPV_TCP | 43537 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc17JalovaMoc_L2 | LONG | IOD_TPV_TCP | 43539 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc17JalovaMoc_L3 | LONG | IOD_TPV_TCP | 43541 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc17KapacitivnaEnergija | LONG | IOD_TPV_TCP | 43543 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc17KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 43545 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc17MaximumDemand | LONG | IOD_TPV_TCP | 43547 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc17Napetost_L1_L2 | LONG | IOD_TPV_TCP | 43549 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc17Napetost_L1_N | LONG | IOD_TPV_TCP | 43551 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc17Napetost_L2_L3 | LONG | IOD_TPV_TCP | 43553 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc17Napetost_L2_N | LONG | IOD_TPV_TCP | 43555 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc17Napetost_L3_L1 | LONG | IOD_TPV_TCP | 43557 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc17Napetost_L3_N | LONG | IOD_TPV_TCP | 43559 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc17NavideznaMoc_III | LONG | IOD_TPV_TCP | 43561 | 0 | 1200 | 0 | 120 | kVA | ###.#
TPVCirc17NicelniTok | LONG | IOD_TPV_TCP | 43563 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc17PowerFactor_III | LONG | IOD_TPV_TCP | 43565 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc17PowerFactor_L1 | LONG | IOD_TPV_TCP | 43567 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc17PowerFactor_L2 | LONG | IOD_TPV_TCP | 43569 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc17PowerFactor_L3 | LONG | IOD_TPV_TCP | 43571 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc17THDI_L1 | LONG | IOD_TPV_TCP | 43573 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc17THDI_L2 | LONG | IOD_TPV_TCP | 43575 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc17THDI_L3 | LONG | IOD_TPV_TCP | 43577 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc17THDV_L1 | LONG | IOD_TPV_TCP | 43579 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc17THDV_L2 | LONG | IOD_TPV_TCP | 43581 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc17THDV_L3 | LONG | IOD_TPV_TCP | 43583 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc17Tok_L1 | LONG | IOD_TPV_TCP | 43585 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc17Tok_L2 | LONG | IOD_TPV_TCP | 43587 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc17Tok_L3 | LONG | IOD_TPV_TCP | 43589 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc17TokPovprecje_III | LONG | IOD_TPV_TCP | 43591 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc18CosFi_III | LONG | IOD_TPV_TCP | 43593 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc18DelovnaEnergija | LONG | IOD_TPV_TCP | 43595 |  |  | 0
TPVCirc18DelovnaMoc_III | LONG | IOD_TPV_TCP | 43597 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc18DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 43599 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc18DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 43601 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc18DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 43603 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc18Frekvenca_L1 | LONG | IOD_TPV_TCP | 43605 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc18InduktivnaEnergija | LONG | IOD_TPV_TCP | 43607 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc18InduktivnaMoc_III | LONG | IOD_TPV_TCP | 43609 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc18JalovaMoc_L1 | LONG | IOD_TPV_TCP | 43611 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc18JalovaMoc_L2 | LONG | IOD_TPV_TCP | 43613 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc18JalovaMoc_L3 | LONG | IOD_TPV_TCP | 43615 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc18KapacitivnaEnergija | LONG | IOD_TPV_TCP | 43617 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc18KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 43619 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc18MaximumDemand | LONG | IOD_TPV_TCP | 43621 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc18Napetost_L1_L2 | LONG | IOD_TPV_TCP | 43623 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc18Napetost_L1_N | LONG | IOD_TPV_TCP | 43625 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc18Napetost_L2_L3 | LONG | IOD_TPV_TCP | 43627 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc18Napetost_L2_N | LONG | IOD_TPV_TCP | 43629 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc18Napetost_L3_L1 | LONG | IOD_TPV_TCP | 43631 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc18Napetost_L3_N | LONG | IOD_TPV_TCP | 43633 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc18NavideznaMoc_III | LONG | IOD_TPV_TCP | 43635 | 0 | 800 | 0 | 80 | kVA | ###.#
TPVCirc18NicelniTok | LONG | IOD_TPV_TCP | 43637 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc18PowerFactor_III | LONG | IOD_TPV_TCP | 43639 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc18PowerFactor_L1 | LONG | IOD_TPV_TCP | 43641 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc18PowerFactor_L2 | LONG | IOD_TPV_TCP | 43643 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc18PowerFactor_L3 | LONG | IOD_TPV_TCP | 43645 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc18THDI_L1 | LONG | IOD_TPV_TCP | 43647 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc18THDI_L2 | LONG | IOD_TPV_TCP | 43649 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc18THDI_L3 | LONG | IOD_TPV_TCP | 43651 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc18THDV_L1 | LONG | IOD_TPV_TCP | 43653 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc18THDV_L2 | LONG | IOD_TPV_TCP | 43655 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc18THDV_L3 | LONG | IOD_TPV_TCP | 43657 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc18Tok_L1 | LONG | IOD_TPV_TCP | 43659 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc18Tok_L2 | LONG | IOD_TPV_TCP | 43661 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc18Tok_L3 | LONG | IOD_TPV_TCP | 43663 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc18TokPovprecje_III | LONG | IOD_TPV_TCP | 43665 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc19CosFi_III | LONG | IOD_TPV_TCP | 43667 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc19DelovnaEnergija | LONG | IOD_TPV_TCP | 43669 |  |  | 0
TPVCirc19DelovnaMoc_III | LONG | IOD_TPV_TCP | 43671 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc19DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 43673 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc19DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 43675 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc19DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 43677 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc19Frekvenca_L1 | LONG | IOD_TPV_TCP | 43679 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc19InduktivnaEnergija | LONG | IOD_TPV_TCP | 43681 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc19InduktivnaMoc_III | LONG | IOD_TPV_TCP | 43683 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc19JalovaMoc_L1 | LONG | IOD_TPV_TCP | 43685 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc19JalovaMoc_L2 | LONG | IOD_TPV_TCP | 43687 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc19JalovaMoc_L3 | LONG | IOD_TPV_TCP | 43689 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc19KapacitivnaEnergija | LONG | IOD_TPV_TCP | 43691 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc19KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 43693 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc19MaximumDemand | LONG | IOD_TPV_TCP | 43695 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc19Napetost_L1_L2 | LONG | IOD_TPV_TCP | 43697 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc19Napetost_L1_N | LONG | IOD_TPV_TCP | 43699 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc19Napetost_L2_L3 | LONG | IOD_TPV_TCP | 43701 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc19Napetost_L2_N | LONG | IOD_TPV_TCP | 43703 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc19Napetost_L3_L1 | LONG | IOD_TPV_TCP | 43705 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc19Napetost_L3_N | LONG | IOD_TPV_TCP | 43707 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc19NavideznaMoc_III | LONG | IOD_TPV_TCP | 43709 | 0 | 800 | 0 | 80 | kVA | ###.#
TPVCirc19NicelniTok | LONG | IOD_TPV_TCP | 43711 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc19PowerFactor_III | LONG | IOD_TPV_TCP | 43713 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc19PowerFactor_L1 | LONG | IOD_TPV_TCP | 43715 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc19PowerFactor_L2 | LONG | IOD_TPV_TCP | 43717 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc19PowerFactor_L3 | LONG | IOD_TPV_TCP | 43719 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc19THDI_L1 | LONG | IOD_TPV_TCP | 43721 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc19THDI_L2 | LONG | IOD_TPV_TCP | 43723 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc19THDI_L3 | LONG | IOD_TPV_TCP | 43725 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc19THDV_L1 | LONG | IOD_TPV_TCP | 43727 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc19THDV_L2 | LONG | IOD_TPV_TCP | 43729 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc19THDV_L3 | LONG | IOD_TPV_TCP | 43731 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc19Tok_L1 | LONG | IOD_TPV_TCP | 43733 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc19Tok_L2 | LONG | IOD_TPV_TCP | 43735 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc19Tok_L3 | LONG | IOD_TPV_TCP | 43737 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc19TokPovprecje_III | LONG | IOD_TPV_TCP | 43739 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc1CosFi_III | LONG | IOD_TPV_TCP | 43741 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc1DelovnaEnergija | LONG | IOD_TPV_TCP | 43743 |  |  | 0
TPVCirc1DelovnaMoc_III | LONG | IOD_TPV_TCP | 43745 | 0 | 3200 | 0 | 320 | kW | ###.#
TPVCirc1DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 43747 | 0 | 3200 | 0 | 320 | kW | ###.#
TPVCirc1DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 43749 | 0 | 3200 | 0 | 320 | kW | ###.#
TPVCirc1DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 43751 | 0 | 3200 | 0 | 320 | kW | ###.#
TPVCirc1Frekvenca_L1 | LONG | IOD_TPV_TCP | 43753 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc1InduktivnaEnergija | LONG | IOD_TPV_TCP | 43755 | 0 | 100000 | 0 | 10000 | kW | ####.#
TPVCirc1InduktivnaMoc_III | LONG | IOD_TPV_TCP | 43757 | 0 | 3200 | 0 | 320 | kVAR | ####.#
TPVCirc1JalovaMoc_L1 | LONG | IOD_TPV_TCP | 43759 | 0 | 3200 | 0 | 320 | kVAR | ####.#
TPVCirc1JalovaMoc_L2 | LONG | IOD_TPV_TCP | 43761 | 0 | 3200 | 0 | 320 | kVAR | ####.#
TPVCirc1JalovaMoc_L3 | LONG | IOD_TPV_TCP | 43763 | 0 | 3200 | 0 | 320 | kVAR | ####.#
TPVCirc1KapacitivnaEnergija | LONG | IOD_TPV_TCP | 43765 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc1KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 43767 | 0 | 3200 | 0 | 320 | kVAR | ###.#
TPVCirc1MaximumDemand | LONG | IOD_TPV_TCP | 43769 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc1Napetost_L1_L2 | LONG | IOD_TPV_TCP | 43771 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc1Napetost_L1_N | LONG | IOD_TPV_TCP | 43773 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc1Napetost_L2_L3 | LONG | IOD_TPV_TCP | 43775 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc1Napetost_L2_N | LONG | IOD_TPV_TCP | 43777 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc1Napetost_L3_L1 | LONG | IOD_TPV_TCP | 43779 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc1Napetost_L3_N | LONG | IOD_TPV_TCP | 43781 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc1NavideznaMoc_III | LONG | IOD_TPV_TCP | 43783 | 0 | 3200 | 0 | 320 | kVA | ###.#
TPVCirc1NicelniTok | LONG | IOD_TPV_TCP | 43785 | 0 | 3200 | 0 | 320 | A | ###.#
TPVCirc1PowerFactor_III | LONG | IOD_TPV_TCP | 43787 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc1PowerFactor_L1 | LONG | IOD_TPV_TCP | 43789 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc1PowerFactor_L2 | LONG | IOD_TPV_TCP | 43791 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc1PowerFactor_L3 | LONG | IOD_TPV_TCP | 43793 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc1THDI_L1 | LONG | IOD_TPV_TCP | 43795 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc1THDI_L2 | LONG | IOD_TPV_TCP | 43797 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc1THDI_L3 | LONG | IOD_TPV_TCP | 43799 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc1THDV_L1 | LONG | IOD_TPV_TCP | 43801 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc1THDV_L2 | LONG | IOD_TPV_TCP | 43803 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc1THDV_L3 | LONG | IOD_TPV_TCP | 43805 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc1Tok_L1 | LONG | IOD_TPV_TCP | 43807 | 0 | 3200 | 0 | 320 | A | ###.#
TPVCirc1Tok_L2 | LONG | IOD_TPV_TCP | 43809 | 0 | 3200 | 0 | 320 | A | ###.#
TPVCirc1Tok_L3 | LONG | IOD_TPV_TCP | 43811 | 0 | 3200 | 0 | 320 | A | ###.#
TPVCirc1TokPovprecje_III | LONG | IOD_TPV_TCP | 43813 | 0 | 3200 | 0 | 320 | A | ###.#
TPVCirc20CosFi_III | LONG | IOD_TPV_TCP | 43815 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc20DelovnaEnergija | LONG | IOD_TPV_TCP | 43817 |  |  | 0
TPVCirc20DelovnaMoc_III | LONG | IOD_TPV_TCP | 43819 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc20DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 43821 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc20DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 43823 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc20DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 43825 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc20Frekvenca_L1 | LONG | IOD_TPV_TCP | 43827 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc20InduktivnaEnergija | LONG | IOD_TPV_TCP | 43829 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc20InduktivnaMoc_III | LONG | IOD_TPV_TCP | 43831 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc20JalovaMoc_L1 | LONG | IOD_TPV_TCP | 43833 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc20JalovaMoc_L2 | LONG | IOD_TPV_TCP | 43835 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc20JalovaMoc_L3 | LONG | IOD_TPV_TCP | 43837 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc20KapacitivnaEnergija | LONG | IOD_TPV_TCP | 43839 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc20KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 43841 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc20MaximumDemand | LONG | IOD_TPV_TCP | 43843 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc20Napetost_L1_L2 | LONG | IOD_TPV_TCP | 43845 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc20Napetost_L1_N | LONG | IOD_TPV_TCP | 43847 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc20Napetost_L2_L3 | LONG | IOD_TPV_TCP | 43849 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc20Napetost_L2_N | LONG | IOD_TPV_TCP | 43851 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc20Napetost_L3_L1 | LONG | IOD_TPV_TCP | 43853 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc20Napetost_L3_N | LONG | IOD_TPV_TCP | 43855 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc20NavideznaMoc_III | LONG | IOD_TPV_TCP | 43857 | 0 | 800 | 0 | 80 | kVA | ###.#
TPVCirc20NicelniTok | LONG | IOD_TPV_TCP | 43859 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc20PowerFactor_III | LONG | IOD_TPV_TCP | 43861 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc20PowerFactor_L1 | LONG | IOD_TPV_TCP | 43863 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc20PowerFactor_L2 | LONG | IOD_TPV_TCP | 43865 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc20PowerFactor_L3 | LONG | IOD_TPV_TCP | 43867 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc20THDI_L1 | LONG | IOD_TPV_TCP | 43869 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc20THDI_L2 | LONG | IOD_TPV_TCP | 43871 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc20THDI_L3 | LONG | IOD_TPV_TCP | 43873 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc20THDV_L1 | LONG | IOD_TPV_TCP | 43875 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc20THDV_L2 | LONG | IOD_TPV_TCP | 43877 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc20THDV_L3 | LONG | IOD_TPV_TCP | 43879 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc20Tok_L1 | LONG | IOD_TPV_TCP | 43881 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc20Tok_L2 | LONG | IOD_TPV_TCP | 43883 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc20Tok_L3 | LONG | IOD_TPV_TCP | 43885 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc20TokPovprecje_III | LONG | IOD_TPV_TCP | 43887 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc21CosFi_III | LONG | IOD_TPV_TCP | 43889 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc21DelovnaEnergija | LONG | IOD_TPV_TCP | 43891 |  |  | 0
TPVCirc21DelovnaMoc_III | LONG | IOD_TPV_TCP | 43893 | 0 | 200 | 0 | 20 | kW | ###.#
TPVCirc21DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 43895 | 0 | 200 | 0 | 20 | kW | ###.#
TPVCirc21DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 43897 | 0 | 200 | 0 | 20 | kW | ###.#
TPVCirc21DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 43899 | 0 | 200 | 0 | 20 | kW | ###.#
TPVCirc21Frekvenca_L1 | LONG | IOD_TPV_TCP | 43901 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc21InduktivnaEnergija | LONG | IOD_TPV_TCP | 43903 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc21InduktivnaMoc_III | LONG | IOD_TPV_TCP | 43905 | 0 | 200 | 0 | 20 | kVAR | ###.#
TPVCirc21JalovaMoc_L1 | LONG | IOD_TPV_TCP | 43907 | 0 | 200 | 0 | 20 | kVAR | ###.#
TPVCirc21JalovaMoc_L2 | LONG | IOD_TPV_TCP | 43909 | 0 | 200 | 0 | 20 | kVAR | ###.#
TPVCirc21JalovaMoc_L3 | LONG | IOD_TPV_TCP | 43911 | 0 | 200 | 0 | 20 | kVAR | ###.#
TPVCirc21KapacitivnaEnergija | LONG | IOD_TPV_TCP | 43913 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc21KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 43915 | 0 | 200 | 0 | 20 | kVAR | ###.#
TPVCirc21MaximumDemand | LONG | IOD_TPV_TCP | 43917 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc21Napetost_L1_L2 | LONG | IOD_TPV_TCP | 43919 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc21Napetost_L1_N | LONG | IOD_TPV_TCP | 43921 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc21Napetost_L2_L3 | LONG | IOD_TPV_TCP | 43923 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc21Napetost_L2_N | LONG | IOD_TPV_TCP | 43925 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc21Napetost_L3_L1 | LONG | IOD_TPV_TCP | 43927 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc21Napetost_L3_N | LONG | IOD_TPV_TCP | 43929 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc21NavideznaMoc_III | LONG | IOD_TPV_TCP | 43931 | 0 | 200 | 0 | 20 | kVA | ###.#
TPVCirc21NicelniTok | LONG | IOD_TPV_TCP | 43933 | 0 | 200 | 0 | 20 | A | ###.#
TPVCirc21PowerFactor_III | LONG | IOD_TPV_TCP | 43935 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc21PowerFactor_L1 | LONG | IOD_TPV_TCP | 43937 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc21PowerFactor_L2 | LONG | IOD_TPV_TCP | 43939 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc21PowerFactor_L3 | LONG | IOD_TPV_TCP | 43941 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc21THDI_L1 | LONG | IOD_TPV_TCP | 43943 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc21THDI_L2 | LONG | IOD_TPV_TCP | 43945 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc21THDI_L3 | LONG | IOD_TPV_TCP | 43947 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc21THDV_L1 | LONG | IOD_TPV_TCP | 43949 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc21THDV_L2 | LONG | IOD_TPV_TCP | 43951 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc21THDV_L3 | LONG | IOD_TPV_TCP | 43953 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc21Tok_L1 | LONG | IOD_TPV_TCP | 43955 | 0 | 200 | 0 | 20 | A | ###.#
TPVCirc21Tok_L2 | LONG | IOD_TPV_TCP | 43957 | 0 | 200 | 0 | 20 | A | ###.#
TPVCirc21Tok_L3 | LONG | IOD_TPV_TCP | 43959 | 0 | 200 | 0 | 20 | A | ###.#
TPVCirc21TokPovprecje_III | LONG | IOD_TPV_TCP | 43961 | 0 | 200 | 0 | 20 | A | ###.#
TPVCirc22CosFi_III | LONG | IOD_TPV_TCP | 43963 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc22DelovnaEnergija | LONG | IOD_TPV_TCP | 43965 |  |  | 0
TPVCirc22DelovnaMoc_III | LONG | IOD_TPV_TCP | 43967 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc22DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 43969 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc22DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 43971 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc22DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 43973 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc22Frekvenca_L1 | LONG | IOD_TPV_TCP | 43975 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc22InduktivnaEnergija | LONG | IOD_TPV_TCP | 43977 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc22InduktivnaMoc_III | LONG | IOD_TPV_TCP | 43979 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc22JalovaMoc_L1 | LONG | IOD_TPV_TCP | 43981 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc22JalovaMoc_L2 | LONG | IOD_TPV_TCP | 43983 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc22JalovaMoc_L3 | LONG | IOD_TPV_TCP | 43985 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc22KapacitivnaEnergija | LONG | IOD_TPV_TCP | 43987 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc22KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 43989 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc22MaximumDemand | LONG | IOD_TPV_TCP | 43991 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc22Napetost_L1_L2 | LONG | IOD_TPV_TCP | 43993 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc22Napetost_L1_N | LONG | IOD_TPV_TCP | 43995 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc22Napetost_L2_L3 | LONG | IOD_TPV_TCP | 43997 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc22Napetost_L2_N | LONG | IOD_TPV_TCP | 43999 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc22Napetost_L3_L1 | LONG | IOD_TPV_TCP | 44001 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc22Napetost_L3_N | LONG | IOD_TPV_TCP | 44003 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc22NavideznaMoc_III | LONG | IOD_TPV_TCP | 44005 | 0 | 1200 | 0 | 120 | kVA | ###.#
TPVCirc22NicelniTok | LONG | IOD_TPV_TCP | 44007 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc22PowerFactor_III | LONG | IOD_TPV_TCP | 44009 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc22PowerFactor_L1 | LONG | IOD_TPV_TCP | 44011 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc22PowerFactor_L2 | LONG | IOD_TPV_TCP | 44013 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc22PowerFactor_L3 | LONG | IOD_TPV_TCP | 44015 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc22THDI_L1 | LONG | IOD_TPV_TCP | 44017 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc22THDI_L2 | LONG | IOD_TPV_TCP | 44019 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc22THDI_L3 | LONG | IOD_TPV_TCP | 44021 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc22THDV_L1 | LONG | IOD_TPV_TCP | 44023 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc22THDV_L2 | LONG | IOD_TPV_TCP | 44025 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc22THDV_L3 | LONG | IOD_TPV_TCP | 44027 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc22Tok_L1 | LONG | IOD_TPV_TCP | 44029 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc22Tok_L2 | LONG | IOD_TPV_TCP | 44031 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc22Tok_L3 | LONG | IOD_TPV_TCP | 44033 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc22TokPovprecje_III | LONG | IOD_TPV_TCP | 44035 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc23CosFi_III | LONG | IOD_TPV_TCP | 44037 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc23DelovnaEnergija | LONG | IOD_TPV_TCP | 44039 |  |  | 0
TPVCirc23DelovnaMoc_III | LONG | IOD_TPV_TCP | 44041 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc23DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 44043 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc23DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 44045 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc23DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 44047 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc23Frekvenca_L1 | LONG | IOD_TPV_TCP | 44049 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc23InduktivnaEnergija | LONG | IOD_TPV_TCP | 44051 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc23InduktivnaMoc_III | LONG | IOD_TPV_TCP | 44053 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc23JalovaMoc_L1 | LONG | IOD_TPV_TCP | 44055 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc23JalovaMoc_L2 | LONG | IOD_TPV_TCP | 44057 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc23JalovaMoc_L3 | LONG | IOD_TPV_TCP | 44059 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc23KapacitivnaEnergija | LONG | IOD_TPV_TCP | 44061 | 0 | 10000 | 0 | 1000
TPVCirc23KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 44063 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc23MaximumDemand | LONG | IOD_TPV_TCP | 44065 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc23Napetost_L1_L2 | LONG | IOD_TPV_TCP | 44067 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc23Napetost_L1_N | LONG | IOD_TPV_TCP | 44069 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc23Napetost_L2_L3 | LONG | IOD_TPV_TCP | 44071 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc23Napetost_L2_N | LONG | IOD_TPV_TCP | 44073 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc23Napetost_L3_L1 | LONG | IOD_TPV_TCP | 44075 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc23Napetost_L3_N | LONG | IOD_TPV_TCP | 44077 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc23NavideznaMoc_III | LONG | IOD_TPV_TCP | 44079 | 0 | 1200 | 0 | 120 | kVA | ###.#
TPVCirc23NicelniTok | LONG | IOD_TPV_TCP | 44081 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc23PowerFactor_III | LONG | IOD_TPV_TCP | 44083 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc23PowerFactor_L1 | LONG | IOD_TPV_TCP | 44085 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc23PowerFactor_L2 | LONG | IOD_TPV_TCP | 44087 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc23PowerFactor_L3 | LONG | IOD_TPV_TCP | 44089 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc23THDI_L1 | LONG | IOD_TPV_TCP | 44091 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc23THDI_L2 | LONG | IOD_TPV_TCP | 44093 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc23THDI_L3 | LONG | IOD_TPV_TCP | 44095 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc23THDV_L1 | LONG | IOD_TPV_TCP | 44097 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc23THDV_L2 | LONG | IOD_TPV_TCP | 44099 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc23THDV_L3 | LONG | IOD_TPV_TCP | 44101 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc23Tok_L1 | LONG | IOD_TPV_TCP | 44103 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc23Tok_L2 | LONG | IOD_TPV_TCP | 44105 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc23Tok_L3 | LONG | IOD_TPV_TCP | 44107 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc23TokPovprecje_III | LONG | IOD_TPV_TCP | 44109 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc24CosFi_III | LONG | IOD_TPV_TCP | 44111 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc24DelovnaEnergija | LONG | IOD_TPV_TCP | 44113 |  |  | 0
TPVCirc24DelovnaMoc_III | LONG | IOD_TPV_TCP | 44115 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc24DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 44117 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc24DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 44119 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc24DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 44121 | 0 | 1200 | 0 | 120 | kW | ###.#
TPVCirc24Frekvenca_L1 | LONG | IOD_TPV_TCP | 44123 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc24InduktivnaEnergija | LONG | IOD_TPV_TCP | 44125 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc24InduktivnaMoc_III | LONG | IOD_TPV_TCP | 44127 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc24JalovaMoc_L1 | LONG | IOD_TPV_TCP | 44129 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc24JalovaMoc_L2 | LONG | IOD_TPV_TCP | 44131 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc24JalovaMoc_L3 | LONG | IOD_TPV_TCP | 44133 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc24KapacitivnaEnergija | LONG | IOD_TPV_TCP | 44135 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc24KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 44137 | 0 | 1200 | 0 | 120 | kVAR | ###.#
TPVCirc24MaximumDemand | LONG | IOD_TPV_TCP | 44139 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc24Napetost_L1_L2 | LONG | IOD_TPV_TCP | 44141 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc24Napetost_L1_N | LONG | IOD_TPV_TCP | 44143 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc24Napetost_L2_L3 | LONG | IOD_TPV_TCP | 44145 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc24Napetost_L2_N | LONG | IOD_TPV_TCP | 44147 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc24Napetost_L3_L1 | LONG | IOD_TPV_TCP | 44149 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc24Napetost_L3_N | LONG | IOD_TPV_TCP | 44151 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc24NavideznaMoc_III | LONG | IOD_TPV_TCP | 44153 | 0 | 1200 | 0 | 120 | kVA | ###.#
TPVCirc24NicelniTok | LONG | IOD_TPV_TCP | 44155 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc24PowerFactor_III | LONG | IOD_TPV_TCP | 44157 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc24PowerFactor_L1 | LONG | IOD_TPV_TCP | 44159 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc24PowerFactor_L2 | LONG | IOD_TPV_TCP | 44161 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc24PowerFactor_L3 | LONG | IOD_TPV_TCP | 44163 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc24THDI_L1 | LONG | IOD_TPV_TCP | 44165 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc24THDI_L2 | LONG | IOD_TPV_TCP | 44167 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc24THDI_L3 | LONG | IOD_TPV_TCP | 44169 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc24THDV_L1 | LONG | IOD_TPV_TCP | 44171 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc24THDV_L2 | LONG | IOD_TPV_TCP | 44173 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc24THDV_L3 | LONG | IOD_TPV_TCP | 44175 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc24Tok_L1 | LONG | IOD_TPV_TCP | 44177 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc24Tok_L2 | LONG | IOD_TPV_TCP | 44179 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc24Tok_L3 | LONG | IOD_TPV_TCP | 44181 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc24TokPovprecje_III | LONG | IOD_TPV_TCP | 44183 | 0 | 1200 | 0 | 120 | A | ###.#
TPVCirc25CosFi_III | LONG | IOD_TPV_TCP | 44185 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc25DelovnaEnergija | LONG | IOD_TPV_TCP | 44187 |  |  | 0
TPVCirc25DelovnaMoc_III | LONG | IOD_TPV_TCP | 44189 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc25DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 44191 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc25DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 44193 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc25DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 44195 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc25Frekvenca_L1 | LONG | IOD_TPV_TCP | 44197 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc25InduktivnaEnergija | LONG | IOD_TPV_TCP | 44199 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc25InduktivnaMoc_III | LONG | IOD_TPV_TCP | 44201 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc25JalovaMoc_L1 | LONG | IOD_TPV_TCP | 44203 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc25JalovaMoc_L2 | LONG | IOD_TPV_TCP | 44205 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc25JalovaMoc_L3 | LONG | IOD_TPV_TCP | 44207 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc25KapacitivnaEnergija | LONG | IOD_TPV_TCP | 44209 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc25KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 44211 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc25MaximumDemand | LONG | IOD_TPV_TCP | 44213 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc25Napetost_L1_L2 | LONG | IOD_TPV_TCP | 44215 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc25Napetost_L1_N | LONG | IOD_TPV_TCP | 44217 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc25Napetost_L2_L3 | LONG | IOD_TPV_TCP | 44219 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc25Napetost_L2_N | LONG | IOD_TPV_TCP | 44221 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc25Napetost_L3_L1 | LONG | IOD_TPV_TCP | 44223 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc25Napetost_L3_N | LONG | IOD_TPV_TCP | 44225 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc25NavideznaMoc_III | LONG | IOD_TPV_TCP | 44227 | 0 | 800 | 0 | 80 | kVA | ###.#
TPVCirc25NicelniTok | LONG | IOD_TPV_TCP | 44229 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc25PowerFactor_III | LONG | IOD_TPV_TCP | 44231 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc25PowerFactor_L1 | LONG | IOD_TPV_TCP | 44233 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc25PowerFactor_L2 | LONG | IOD_TPV_TCP | 44235 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc25PowerFactor_L3 | LONG | IOD_TPV_TCP | 44237 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc25THDI_L1 | LONG | IOD_TPV_TCP | 44239 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc25THDI_L2 | LONG | IOD_TPV_TCP | 44241 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc25THDI_L3 | LONG | IOD_TPV_TCP | 44243 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc25THDV_L1 | LONG | IOD_TPV_TCP | 44245 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc25THDV_L2 | LONG | IOD_TPV_TCP | 44247 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc25THDV_L3 | LONG | IOD_TPV_TCP | 44249 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc25Tok_L1 | LONG | IOD_TPV_TCP | 44251 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc25Tok_L2 | LONG | IOD_TPV_TCP | 44253 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc25Tok_L3 | LONG | IOD_TPV_TCP | 44255 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc25TokPovprecje_III | LONG | IOD_TPV_TCP | 44257 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc2CosFi_III | LONG | IOD_TPV_TCP | 44259 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc2DelovnaEnergija | LONG | IOD_TPV_TCP | 44261 |  |  | 0
TPVCirc2DelovnaMoc_III | LONG | IOD_TPV_TCP | 44263 | 0 | 400 | 0 | 40 | kW | ###.#
TPVCirc2DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 44265 | 0 | 400 | 0 | 40 | kW | ###.#
TPVCirc2DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 44267 | 0 | 400 | 0 | 40 | kW | ###.#
TPVCirc2DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 44269 | 0 | 400 | 0 | 40 | kW | ###.#
TPVCirc2Frekvenca_L1 | LONG | IOD_TPV_TCP | 44271 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc2InduktivnaEnergija | LONG | IOD_TPV_TCP | 44273 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc2InduktivnaMoc_III | LONG | IOD_TPV_TCP | 44275 | 0 | 400 | 0 | 40 | kVAR | ###.#
TPVCirc2JalovaMoc_L1 | LONG | IOD_TPV_TCP | 44277 | 0 | 400 | 0 | 40 | kVAR | ###.#
TPVCirc2JalovaMoc_L2 | LONG | IOD_TPV_TCP | 44279 | 0 | 400 | 0 | 40 | kVAR | ###.#
TPVCirc2JalovaMoc_L3 | LONG | IOD_TPV_TCP | 44281 | 0 | 400 | 0 | 40 | kVAR | ###.#
TPVCirc2KapacitivnaEnergija | LONG | IOD_TPV_TCP | 44283 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc2KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 44285 | 0 | 400 | 0 | 40 | kVAR | ###.#
TPVCirc2MaximumDemand | LONG | IOD_TPV_TCP | 44287 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc2Napetost_L1_L2 | LONG | IOD_TPV_TCP | 44289 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc2Napetost_L1_N | LONG | IOD_TPV_TCP | 44291 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc2Napetost_L2_L3 | LONG | IOD_TPV_TCP | 44293 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc2Napetost_L2_N | LONG | IOD_TPV_TCP | 44295 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc2Napetost_L3_L1 | LONG | IOD_TPV_TCP | 44297 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc2Napetost_L3_N | LONG | IOD_TPV_TCP | 44299 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc2NavideznaMoc_III | LONG | IOD_TPV_TCP | 44301 | 0 | 400 | 0 | 40 | kVA | ###.#
TPVCirc2NicelniTok | LONG | IOD_TPV_TCP | 44303 | 0 | 400 | 0 | 40 | A | ###.#
TPVCirc2PowerFactor_III | LONG | IOD_TPV_TCP | 44305 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc2PowerFactor_L1 | LONG | IOD_TPV_TCP | 44307 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc2PowerFactor_L2 | LONG | IOD_TPV_TCP | 44309 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc2PowerFactor_L3 | LONG | IOD_TPV_TCP | 44311 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc2THDI_L1 | LONG | IOD_TPV_TCP | 44313 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc2THDI_L2 | LONG | IOD_TPV_TCP | 44315 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc2THDI_L3 | LONG | IOD_TPV_TCP | 44317 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc2THDV_L1 | LONG | IOD_TPV_TCP | 44319 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc2THDV_L2 | LONG | IOD_TPV_TCP | 44321 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc2THDV_L3 | LONG | IOD_TPV_TCP | 44323 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc2Tok_L1 | LONG | IOD_TPV_TCP | 44325 | 0 | 400 | 0 | 40 | A | ###.#
TPVCirc2Tok_L2 | LONG | IOD_TPV_TCP | 44327 | 0 | 400 | 0 | 40 | A | ###.#
TPVCirc2Tok_L3 | LONG | IOD_TPV_TCP | 44329 | 0 | 400 | 0 | 40 | A | ###.#
TPVCirc2TokPovprecje_III | LONG | IOD_TPV_TCP | 44331 | 0 | 400 | 0 | 40 | A | ###.#
TPVCirc3CosFi_III | LONG | IOD_TPV_TCP | 44333 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc3DelovnaEnergija | LONG | IOD_TPV_TCP | 44335 |  |  | 0
TPVCirc3DelovnaMoc_III | LONG | IOD_TPV_TCP | 44337 | 0 | 400 | 0 | 40 | kW | ###.#
TPVCirc3DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 44339 | 0 | 400 | 0 | 40 | kW | ###.#
TPVCirc3DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 44341 | 0 | 400 | 0 | 40 | kW | ###.#
TPVCirc3DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 44343 | 0 | 400 | 0 | 40 | kW | ###.#
TPVCirc3Frekvenca_L1 | LONG | IOD_TPV_TCP | 44345 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc3InduktivnaEnergija | LONG | IOD_TPV_TCP | 44347 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc3InduktivnaMoc_III | LONG | IOD_TPV_TCP | 44349 | 0 | 400 | 0 | 40 | kVAR | ###.#
TPVCirc3JalovaMoc_L1 | LONG | IOD_TPV_TCP | 44351 | 0 | 400 | 0 | 40 | kVAR | ####.#
TPVCirc3JalovaMoc_L2 | LONG | IOD_TPV_TCP | 44353 | 0 | 400 | 0 | 40 | kVAR | ####.#
TPVCirc3JalovaMoc_L3 | LONG | IOD_TPV_TCP | 44355 | 0 | 400 | 0 | 40 | kVAR | ####.#
TPVCirc3KapacitivnaEnergija | LONG | IOD_TPV_TCP | 44357 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc3KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 44359 | 0 | 400 | 0 | 40 | kVAR | ###.#
TPVCirc3MaximumDemand | LONG | IOD_TPV_TCP | 44361 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc3Napetost_L1_L2 | LONG | IOD_TPV_TCP | 44363 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc3Napetost_L1_N | LONG | IOD_TPV_TCP | 44365 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc3Napetost_L2_L3 | LONG | IOD_TPV_TCP | 44367 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc3Napetost_L2_N | LONG | IOD_TPV_TCP | 44369 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc3Napetost_L3_L1 | LONG | IOD_TPV_TCP | 44371 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc3Napetost_L3_N | LONG | IOD_TPV_TCP | 44373 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc3NavideznaMoc_III | LONG | IOD_TPV_TCP | 44375 | 0 | 400 | 0 | 40 | kVA | ###.#
TPVCirc3NicelniTok | LONG | IOD_TPV_TCP | 44377 | 0 | 400 | 0 | 40 | A | ###.#
TPVCirc3PowerFactor_III | LONG | IOD_TPV_TCP | 44379 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc3PowerFactor_L1 | LONG | IOD_TPV_TCP | 44381 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc3PowerFactor_L2 | LONG | IOD_TPV_TCP | 44383 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc3PowerFactor_L3 | LONG | IOD_TPV_TCP | 44385 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc3THDI_L1 | LONG | IOD_TPV_TCP | 44387 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc3THDI_L2 | LONG | IOD_TPV_TCP | 44389 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc3THDI_L3 | LONG | IOD_TPV_TCP | 44391 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc3THDV_L1 | LONG | IOD_TPV_TCP | 44393 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc3THDV_L2 | LONG | IOD_TPV_TCP | 44395 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc3THDV_L3 | LONG | IOD_TPV_TCP | 44397 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc3Tok_L1 | LONG | IOD_TPV_TCP | 44399 | 0 | 400 | 0 | 40 | A | ###.#
TPVCirc3Tok_L2 | LONG | IOD_TPV_TCP | 44401 | 0 | 400 | 0 | 40 | A | ###.#
TPVCirc3Tok_L3 | LONG | IOD_TPV_TCP | 44403 | 0 | 400 | 0 | 40 | A | ###.#
TPVCirc3TokPovprecje_III | LONG | IOD_TPV_TCP | 44405 | 0 | 400 | 0 | 40 | A | ###.#
TPVCirc4CosFi_III | LONG | IOD_TPV_TCP | 44407 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc4DelovnaEnergija | LONG | IOD_TPV_TCP | 44409 |  |  | 0
TPVCirc4DelovnaMoc_III | LONG | IOD_TPV_TCP | 44411 | 0 | 2000 | 0 | 200 | kW | ####.#
TPVCirc4DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 44413 | 0 | 2000 | 0 | 200 | kW | ####.#
TPVCirc4DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 44415 | 0 | 2000 | 0 | 200 | kW | ####.#
TPVCirc4DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 44417 | 0 | 2000 | 0 | 200 | kW | ####.#
TPVCirc4Frekvenca_L1 | LONG | IOD_TPV_TCP | 44419 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc4InduktivnaEnergija | LONG | IOD_TPV_TCP | 44421 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc4InduktivnaMoc_III | LONG | IOD_TPV_TCP | 44423 | 0 | 2000 | 0 | 200 | kVAR | ###.#
TPVCirc4JalovaMoc_L1 | LONG | IOD_TPV_TCP | 44425 | 0 | 2000 | 0 | 200 | kVAR | ###.#
TPVCirc4JalovaMoc_L2 | LONG | IOD_TPV_TCP | 44427 | 0 | 2000 | 0 | 200 | kVAR | ###.#
TPVCirc4JalovaMoc_L3 | LONG | IOD_TPV_TCP | 44429 | 0 | 2000 | 0 | 200 | kVAR | ###.#
TPVCirc4KapacitivnaEnergija | LONG | IOD_TPV_TCP | 44431 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc4KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 44433 | 0 | 2000 | 0 | 200 | kVAR | ###.#
TPVCirc4MaximumDemand | LONG | IOD_TPV_TCP | 44435 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc4Napetost_L1_L2 | LONG | IOD_TPV_TCP | 44437 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc4Napetost_L1_N | LONG | IOD_TPV_TCP | 44439 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc4Napetost_L2_L3 | LONG | IOD_TPV_TCP | 44441 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc4Napetost_L2_N | LONG | IOD_TPV_TCP | 44443 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc4Napetost_L3_L1 | LONG | IOD_TPV_TCP | 44445 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc4Napetost_L3_N | LONG | IOD_TPV_TCP | 44447 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc4NavideznaMoc_III | LONG | IOD_TPV_TCP | 44449 | 0 | 2000 | 0 | 200 | kVA | ###.#
TPVCirc4NicelniTok | LONG | IOD_TPV_TCP | 44451 | 0 | 2000 | 0 | 200 | A | ###.#
TPVCirc4PowerFactor_III | LONG | IOD_TPV_TCP | 44453 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc4PowerFactor_L1 | LONG | IOD_TPV_TCP | 44455 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc4PowerFactor_L2 | LONG | IOD_TPV_TCP | 44457 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc4PowerFactor_L3 | LONG | IOD_TPV_TCP | 44459 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc4THDI_L1 | LONG | IOD_TPV_TCP | 44461 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc4THDI_L2 | LONG | IOD_TPV_TCP | 44463 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc4THDI_L3 | LONG | IOD_TPV_TCP | 44465 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc4THDV_L1 | LONG | IOD_TPV_TCP | 44467 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc4THDV_L2 | LONG | IOD_TPV_TCP | 44469 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc4THDV_L3 | LONG | IOD_TPV_TCP | 44471 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc4Tok_L1 | LONG | IOD_TPV_TCP | 44473 | 0 | 2000 | 0 | 200 | A | ###.#
TPVCirc4Tok_L2 | LONG | IOD_TPV_TCP | 44475 | 0 | 2000 | 0 | 200 | A | ###.#
TPVCirc4Tok_L3 | LONG | IOD_TPV_TCP | 44477 | 0 | 2000 | 0 | 200 | A | ###.#
TPVCirc4TokPovprecje_III | LONG | IOD_TPV_TCP | 44479 | 0 | 2000 | 0 | 200 | A | ###.#
TPVCirc5CosFi_III | LONG | IOD_TPV_TCP | 44481 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc5DelovnaEnergija | LONG | IOD_TPV_TCP | 44483 |  |  | 0
TPVCirc5DelovnaMoc_III | LONG | IOD_TPV_TCP | 44485 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc5DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 44487 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc5DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 44489 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc5DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 44491 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc5Frekvenca_L1 | LONG | IOD_TPV_TCP | 44493 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc5InduktivnaEnergija | LONG | IOD_TPV_TCP | 44495 | 0 | 10000 | 0 | 1000 | kW | ####.#
TPVCirc5InduktivnaMoc_III | LONG | IOD_TPV_TCP | 44497 | 0 | 800 | 0 | 80 | kVAR | ####.#
TPVCirc5JalovaMoc_L1 | LONG | IOD_TPV_TCP | 44499 | 0 | 800 | 0 | 80 | kVAR | ####.#
TPVCirc5JalovaMoc_L2 | LONG | IOD_TPV_TCP | 44501 | 0 | 800 | 0 | 80 | kVAR | ####.#
TPVCirc5JalovaMoc_L3 | LONG | IOD_TPV_TCP | 44503 | 0 | 800 | 0 | 80 | kVAR | ####.#
TPVCirc5KapacitivnaEnergija | LONG | IOD_TPV_TCP | 44505 | 0 | 10000 | 0 | 1000 | kW
TPVCirc5KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 44507 | 0 | 800 | 0 | 80 | kVAR | ####.#
TPVCirc5MaximumDemand | LONG | IOD_TPV_TCP | 44509 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc5Napetost_L1_L2 | LONG | IOD_TPV_TCP | 44511 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc5Napetost_L1_N | LONG | IOD_TPV_TCP | 44513 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc5Napetost_L2_L3 | LONG | IOD_TPV_TCP | 44515 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc5Napetost_L2_N | LONG | IOD_TPV_TCP | 44517 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc5Napetost_L3_L1 | LONG | IOD_TPV_TCP | 44519 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc5Napetost_L3_N | LONG | IOD_TPV_TCP | 44521 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc5NavideznaMoc_III | LONG | IOD_TPV_TCP | 44523 | 0 | 800 | 0 | 80 | kVA | ###.#
TPVCirc5NicelniTok | LONG | IOD_TPV_TCP | 44525 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc5PowerFactor_III | LONG | IOD_TPV_TCP | 44527 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc5PowerFactor_L1 | LONG | IOD_TPV_TCP | 44529 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc5PowerFactor_L2 | LONG | IOD_TPV_TCP | 44531 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc5PowerFactor_L3 | LONG | IOD_TPV_TCP | 44533 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc5THDI_L1 | LONG | IOD_TPV_TCP | 44535 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc5THDI_L2 | LONG | IOD_TPV_TCP | 44537 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc5THDI_L3 | LONG | IOD_TPV_TCP | 44539 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc5THDV_L1 | LONG | IOD_TPV_TCP | 44541 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc5THDV_L2 | LONG | IOD_TPV_TCP | 44543 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc5THDV_L3 | LONG | IOD_TPV_TCP | 44545 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc5Tok_L1 | LONG | IOD_TPV_TCP | 44547 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc5Tok_L2 | LONG | IOD_TPV_TCP | 44549 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc5Tok_L3 | LONG | IOD_TPV_TCP | 44551 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc5TokPovprecje_III | LONG | IOD_TPV_TCP | 44553 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc6CosFi_III | LONG | IOD_TPV_TCP | 44555 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc6DelovnaEnergija | LONG | IOD_TPV_TCP | 44557 |  |  | 0
TPVCirc6DelovnaMoc_III | LONG | IOD_TPV_TCP | 44559 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc6DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 44561 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc6DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 44563 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc6DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 44565 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc6Frekvenca_L1 | LONG | IOD_TPV_TCP | 44567 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc6InduktivnaEnergija | LONG | IOD_TPV_TCP | 44569 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc6InduktivnaMoc_III | LONG | IOD_TPV_TCP | 44571 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc6JalovaMoc_L1 | LONG | IOD_TPV_TCP | 44573 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc6JalovaMoc_L2 | LONG | IOD_TPV_TCP | 44575 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc6JalovaMoc_L3 | LONG | IOD_TPV_TCP | 44577 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc6KapacitivnaEnergija | LONG | IOD_TPV_TCP | 44579 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc6KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 44581 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc6MaximumDemand | LONG | IOD_TPV_TCP | 44583 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc6Napetost_L1_L2 | LONG | IOD_TPV_TCP | 44585 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc6Napetost_L1_N | LONG | IOD_TPV_TCP | 44587 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc6Napetost_L2_L3 | LONG | IOD_TPV_TCP | 44589 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc6Napetost_L2_N | LONG | IOD_TPV_TCP | 44591 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc6Napetost_L3_L1 | LONG | IOD_TPV_TCP | 44593 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc6Napetost_L3_N | LONG | IOD_TPV_TCP | 44595 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc6NavideznaMoc_III | LONG | IOD_TPV_TCP | 44597 | 0 | 800 | 0 | 80 | kVA | ###.#
TPVCirc6NicelniTok | LONG | IOD_TPV_TCP | 44599 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc6PowerFactor_III | LONG | IOD_TPV_TCP | 44601 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc6PowerFactor_L1 | LONG | IOD_TPV_TCP | 44603 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc6PowerFactor_L2 | LONG | IOD_TPV_TCP | 44605 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc6PowerFactor_L3 | LONG | IOD_TPV_TCP | 44607 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc6THDI_L1 | LONG | IOD_TPV_TCP | 44609 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc6THDI_L2 | LONG | IOD_TPV_TCP | 44611 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc6THDI_L3 | LONG | IOD_TPV_TCP | 44613 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc6THDV_L1 | LONG | IOD_TPV_TCP | 44615 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc6THDV_L2 | LONG | IOD_TPV_TCP | 44617 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc6THDV_L3 | LONG | IOD_TPV_TCP | 44619 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc6Tok_L1 | LONG | IOD_TPV_TCP | 44621 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc6Tok_L2 | LONG | IOD_TPV_TCP | 44623 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc6Tok_L3 | LONG | IOD_TPV_TCP | 44625 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc6TokPovprecje_III | LONG | IOD_TPV_TCP | 44627 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc7CosFi_III | LONG | IOD_TPV_TCP | 44629 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc7DelovnaEnergija | LONG | IOD_TPV_TCP | 44631 |  |  | 0
TPVCirc7DelovnaMoc_III | LONG | IOD_TPV_TCP | 44633 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc7DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 44635 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc7DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 44637 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc7DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 44639 | 0 | 800 | 0 | 80 | kW | ###.#
TPVCirc7Frekvenca_L1 | LONG | IOD_TPV_TCP | 44641 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc7InduktivnaEnergija | LONG | IOD_TPV_TCP | 44643 | 0 | 10000 | 0 | 1000 | kW | ###.#
TPVCirc7InduktivnaMoc_III | LONG | IOD_TPV_TCP | 44645 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc7JalovaMoc_L1 | LONG | IOD_TPV_TCP | 44647 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc7JalovaMoc_L2 | LONG | IOD_TPV_TCP | 44649 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc7JalovaMoc_L3 | LONG | IOD_TPV_TCP | 44651 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc7KapacitivnaEnergija | LONG | IOD_TPV_TCP | 44653 | 0 | 10000 | 0 | 1000 | kW
TPVCirc7KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 44655 | 0 | 800 | 0 | 80 | kVAR | ###.#
TPVCirc7MaximumDemand | LONG | IOD_TPV_TCP | 44657 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc7Napetost_L1_L2 | LONG | IOD_TPV_TCP | 44659 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc7Napetost_L1_N | LONG | IOD_TPV_TCP | 44661 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc7Napetost_L2_L3 | LONG | IOD_TPV_TCP | 44663 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc7Napetost_L2_N | LONG | IOD_TPV_TCP | 44665 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc7Napetost_L3_L1 | LONG | IOD_TPV_TCP | 44667 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc7Napetost_L3_N | LONG | IOD_TPV_TCP | 44669 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc7NavideznaMoc_III | LONG | IOD_TPV_TCP | 44671 | 0 | 800 | 0 | 80 | kVA | ###.#
TPVCirc7NicelniTok | LONG | IOD_TPV_TCP | 44673 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc7PowerFactor_III | LONG | IOD_TPV_TCP | 44675 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc7PowerFactor_L1 | LONG | IOD_TPV_TCP | 44677 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc7PowerFactor_L2 | LONG | IOD_TPV_TCP | 44679 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc7PowerFactor_L3 | LONG | IOD_TPV_TCP | 44681 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc7THDI_L1 | LONG | IOD_TPV_TCP | 44683 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc7THDI_L2 | LONG | IOD_TPV_TCP | 44685 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc7THDI_L3 | LONG | IOD_TPV_TCP | 44687 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc7THDV_L1 | LONG | IOD_TPV_TCP | 44689 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc7THDV_L2 | LONG | IOD_TPV_TCP | 44691 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc7THDV_L3 | LONG | IOD_TPV_TCP | 44693 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc7Tok_L1 | LONG | IOD_TPV_TCP | 44695 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc7Tok_L2 | LONG | IOD_TPV_TCP | 44697 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc7Tok_L3 | LONG | IOD_TPV_TCP | 44699 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc7TokPovprecje_III | LONG | IOD_TPV_TCP | 44701 | 0 | 800 | 0 | 80 | A | ###.#
TPVCirc8CosFi_III | LONG | IOD_TPV_TCP | 44703 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc8DelovnaEnergija | LONG | IOD_TPV_TCP | 44705 |  |  | 0
TPVCirc8DelovnaMoc_III | LONG | IOD_TPV_TCP | 44707 | 0 | 4000 | 0 | 400 | kW | ####.#
TPVCirc8DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 44709 | 0 | 4000 | 0 | 400 | kW | ####.#
TPVCirc8DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 44711 | 0 | 4000 | 0 | 400 | kW | ####.#
TPVCirc8DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 44713 | 0 | 4000 | 0 | 400 | kW | ####.#
TPVCirc8Frekvenca_L1 | LONG | IOD_TPV_TCP | 44715 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc8InduktivnaEnergija | LONG | IOD_TPV_TCP | 44717 | 0 | 100000 | 0 | 10000 | kW | ####.#
TPVCirc8InduktivnaMoc_III | LONG | IOD_TPV_TCP | 44719 | 0 | 4000 | 0 | 400 | kVAR | ####.#
TPVCirc8JalovaMoc_L1 | LONG | IOD_TPV_TCP | 44721 | 0 | 4000 | 0 | 400 | kVAR | ####.#
TPVCirc8JalovaMoc_L2 | LONG | IOD_TPV_TCP | 44723 | 0 | 4000 | 0 | 400 | kVAR | ####.#
TPVCirc8JalovaMoc_L3 | LONG | IOD_TPV_TCP | 44725 | 0 | 4000 | 0 | 400 | kVAR | ####.#
TPVCirc8KapacitivnaEnergija | LONG | IOD_TPV_TCP | 44727 | 0 | 100000 | 0 | 10000 | kW | ####.#
TPVCirc8KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 44729 | 0 | 4000 | 0 | 400 | kVAR | ####.#
TPVCirc8MaximumDemand | LONG | IOD_TPV_TCP | 44731 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc8Napetost_L1_L2 | LONG | IOD_TPV_TCP | 44733 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc8Napetost_L1_N | LONG | IOD_TPV_TCP | 44735 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc8Napetost_L2_L3 | LONG | IOD_TPV_TCP | 44737 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc8Napetost_L2_N | LONG | IOD_TPV_TCP | 44739 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc8Napetost_L3_L1 | LONG | IOD_TPV_TCP | 44741 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc8Napetost_L3_N | LONG | IOD_TPV_TCP | 44743 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc8NavideznaMoc_III | LONG | IOD_TPV_TCP | 44745 | 0 | 4000 | 0 | 400 | kVA | ###.#
TPVCirc8NicelniTok | LONG | IOD_TPV_TCP | 44747 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc8PowerFactor_III | LONG | IOD_TPV_TCP | 44749 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc8PowerFactor_L1 | LONG | IOD_TPV_TCP | 44751 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc8PowerFactor_L2 | LONG | IOD_TPV_TCP | 44753 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc8PowerFactor_L3 | LONG | IOD_TPV_TCP | 44755 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc8THDI_L1 | LONG | IOD_TPV_TCP | 44757 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc8THDI_L2 | LONG | IOD_TPV_TCP | 44759 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc8THDI_L3 | LONG | IOD_TPV_TCP | 44761 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc8THDV_L1 | LONG | IOD_TPV_TCP | 44763 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc8THDV_L2 | LONG | IOD_TPV_TCP | 44765 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc8THDV_L3 | LONG | IOD_TPV_TCP | 44767 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc8Tok_L1 | LONG | IOD_TPV_TCP | 44769 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc8Tok_L2 | LONG | IOD_TPV_TCP | 44771 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc8Tok_L3 | LONG | IOD_TPV_TCP | 44773 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc8TokPovprecje_III | LONG | IOD_TPV_TCP | 44775 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc9CosFi_III | LONG | IOD_TPV_TCP | 44777 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc9DelovnaEnergija | LONG | IOD_TPV_TCP | 44779 |  |  | 0
TPVCirc9DelovnaMoc_III | LONG | IOD_TPV_TCP | 44781 | 0 | 4000 | 0 | 400 | kW | ####.#
TPVCirc9DelovnaMoc_L1 | LONG | IOD_TPV_TCP | 44783 | 0 | 4000 | 0 | 400 | kW | ####.#
TPVCirc9DelovnaMoc_L2 | LONG | IOD_TPV_TCP | 44785 | 0 | 4000 | 0 | 400 | kW | ####.#
TPVCirc9DelovnaMoc_L3 | LONG | IOD_TPV_TCP | 44787 | 0 | 4000 | 0 | 400 | kW | ####.#
TPVCirc9Frekvenca_L1 | LONG | IOD_TPV_TCP | 44789 | 0 | 600 | 0 | 60 | Hz | ##.#
TPVCirc9InduktivnaEnergija | LONG | IOD_TPV_TCP | 44791 | 0 | 100000 | 0 | 10000 | kW | ####.#
TPVCirc9InduktivnaMoc_III | LONG | IOD_TPV_TCP | 44793 | 0 | 4000 | 0 | 400 | kVAR | ####.#
TPVCirc9JalovaMoc_L1 | LONG | IOD_TPV_TCP | 44795 | 0 | 4000 | 0 | 400 | kVAR | ####.#
TPVCirc9JalovaMoc_L2 | LONG | IOD_TPV_TCP | 44797 | 0 | 4000 | 0 | 400 | kVAR | ####.#
TPVCirc9JalovaMoc_L3 | LONG | IOD_TPV_TCP | 44799 | 0 | 4000 | 0 | 400 | kVAR | ####.#
TPVCirc9KapacitivnaEnergija | LONG | IOD_TPV_TCP | 44801 | 0 | 100000 | 0 | 10000 | kW | ####.#
TPVCirc9KapacitivnaMoc_III | LONG | IOD_TPV_TCP | 44803 | 0 | 4000 | 0 | 400 | kVAR | ####.#
TPVCirc9MaximumDemand | LONG | IOD_TPV_TCP | 44805 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc9Napetost_L1_L2 | LONG | IOD_TPV_TCP | 44807 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc9Napetost_L1_N | LONG | IOD_TPV_TCP | 44809 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc9Napetost_L2_L3 | LONG | IOD_TPV_TCP | 44811 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc9Napetost_L2_N | LONG | IOD_TPV_TCP | 44813 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc9Napetost_L3_L1 | LONG | IOD_TPV_TCP | 44815 | 0 | 4500 | 0 | 450 | V | ###.#
TPVCirc9Napetost_L3_N | LONG | IOD_TPV_TCP | 44817 | 0 | 2700 | 0 | 270 | V | ###.#
TPVCirc9NavideznaMoc_III | LONG | IOD_TPV_TCP | 44819 | 0 | 4000 | 0 | 400 | kVA | ###.#
TPVCirc9NicelniTok | LONG | IOD_TPV_TCP | 44821 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc9PowerFactor_III | LONG | IOD_TPV_TCP | 44823 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc9PowerFactor_L1 | LONG | IOD_TPV_TCP | 44825 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc9PowerFactor_L2 | LONG | IOD_TPV_TCP | 44827 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc9PowerFactor_L3 | LONG | IOD_TPV_TCP | 44829 | -100 | 100 | -1 | 1 |  | ##.##
TPVCirc9THDI_L1 | LONG | IOD_TPV_TCP | 44831 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc9THDI_L2 | LONG | IOD_TPV_TCP | 44833 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc9THDI_L3 | LONG | IOD_TPV_TCP | 44835 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc9THDV_L1 | LONG | IOD_TPV_TCP | 44837 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc9THDV_L2 | LONG | IOD_TPV_TCP | 44839 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc9THDV_L3 | LONG | IOD_TPV_TCP | 44841 | 0 | 100 | 0 | 10 | % | ###.#
TPVCirc9Tok_L1 | LONG | IOD_TPV_TCP | 44843 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc9Tok_L2 | LONG | IOD_TPV_TCP | 44845 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc9Tok_L3 | LONG | IOD_TPV_TCP | 44847 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCirc9TokPovprecje_III | LONG | IOD_TPV_TCP | 44849 | 0 | 4000 | 0 | 400 | A | ###.#
TPVCoolant_temperatureA1 | INT | IOD_TPV_TCP | 40001 | -50 | 20000 | -50 | 200 | řC | ##.#
TPVCoolant_temperatureA2 | INT | IOD_TPV_TCP | 40002 | -50 | 2000 | -50 | 200 | řC | ###.#
TPVDA3_rocno | DIGITAL | IOD_TPV_TCP | 00001
TPVDA3motorni_pogon_okvara | DIGITAL | IOD_TPV_TCP | 00002
TPVdelovna_energ_trenutno | INT | IOD_TPV_TCP | 40003
TPVdelovna_energija_prej | INT | IOD_TPV_TCP | 40004
TPVDW_Napake1 | LONG | IOD_TPV_TCP | 44851
TPVDW_Napake2 | LONG | IOD_TPV_TCP | 44853
TPVDW_Napake3 | LONG | IOD_TPV_TCP | 44855
TPVEngine_speedA1 | UINT | IOD_TPV_TCP | 46005 | 0 | 6000 | 0 | 6000 | obr/min | ####
TPVEngine_speedA2 | UINT | IOD_TPV_TCP | 46006 | 0 | 6000 | 0 | 6000 | obr/min | ####
TPV_Generator_current_lag_leadA1 | INT | IOD_TPV_TCP | 40005 | -180 | 180 | -180 | 180 | ř | ####
TPV_Generator_current_lag_leadA2 | INT | IOD_TPV_TCP | 40006 | -180 | 180 | -180 | 180 | ř | ####
TPV_Generator_earth_currentA1 | LONG | IOD_TPV_TCP | 44857 | 0 | 4000 | 0 | 400 | A | ###.#
TPV_Generator_earth_currentA2 | LONG | IOD_TPV_TCP | 44859 | 0 | 4000 | 0 | 400 | A | ###.#
TPV_Generator_frequencyA1 | UINT | IOD_TPV_TCP | 46007 | 0 | 700 | 0 | 70 | Hz | ##.#
TPV_Generator_frequencyA2 | UINT | IOD_TPV_TCP | 46008 | 0 | 700 | 0 | 70 | Hz | ##.#
TPV_Generator_L1_currentA1 | LONG | IOD_TPV_TCP | 44861 | 0 | 4000 | 0 | 400 | A | ###.#
TPV_Generator_L1_currentA2 | LONG | IOD_TPV_TCP | 44863 | 0 | 4000 | 0 | 400 | A | ###.#
TPV_Generator_L1_L2_voltageA1 | LONG | IOD_TPV_TCP | 44865 | 0 | 4500 | 0 | 450 | V | ###.#
TPV_Generator_L1_L2_voltageA2 | LONG | IOD_TPV_TCP | 44867 | 0 | 4500 | 0 | 450 | V | ###.#
TPV_Generator_L1_N_voltageA1 | LONG | IOD_TPV_TCP | 44869 | 0 | 2700 | 0 | 270 | A | ###.#
TPV_Generator_L1_N_voltageA2 | LONG | IOD_TPV_TCP | 44871 | 0 | 2700 | 0 | 270 | A | ###.#
TPV_Generator_L1_wattsA1 | LONG | IOD_TPV_TCP | 44873 | 0 | 4000 | 0 | 400 | kW | ###.#
TPV_Generator_L1_wattsA2 | LONG | IOD_TPV_TCP | 44875 | 0 | 4000 | 0 | 400 | kW | ###.#
TPV_Generator_L2_currentA1 | LONG | IOD_TPV_TCP | 44877 | 0 | 4000 | 0 | 400 | A | ###.#
TPV_Generator_L2_currentA2 | LONG | IOD_TPV_TCP | 44879 | 0 | 4000 | 0 | 400 | A | ###.#
TPV_Generator_L2_L3_voltageA1 | LONG | IOD_TPV_TCP | 44881 | 0 | 4500 | 0 | 450 | V | ###.#
TPV_Generator_L2_L3_voltageA2 | LONG | IOD_TPV_TCP | 44883 | 0 | 4500 | 0 | 450 | V | ###.#
TPV_Generator_L2_N_voltageA1 | LONG | IOD_TPV_TCP | 44885 | 0 | 2700 | 0 | 270 | V | ###.#
TPV_Generator_L2_N_voltageA2 | LONG | IOD_TPV_TCP | 44887 | 0 | 2700 | 0 | 270 | V | ###.#
TPV_Generator_L2_wattsA1 | LONG | IOD_TPV_TCP | 44889 | 0 | 4000 | 0 | 400 | kW | ###.#
TPV_Generator_L2_wattsA2 | LONG | IOD_TPV_TCP | 44891 | 0 | 4000 | 0 | 400 | kW | ###.#
TPV_Generator_L3_currentA1 | LONG | IOD_TPV_TCP | 44893 | 0 | 4000 | 0 | 400 | A | ###.#
TPV_Generator_L3_currentA2 | LONG | IOD_TPV_TCP | 44895 | 0 | 4000 | 0 | 400 | A | ###.#
TPV_Generator_L3_L1_voltageA1 | LONG | IOD_TPV_TCP | 44897 | 0 | 4500 | 0 | 450 | V | ###.#
TPV_Generator_L3_L1_voltageA2 | LONG | IOD_TPV_TCP | 44899 | 0 | 4500 | 0 | 450 | V | ###.#
TPV_Generator_L3_N_voltageA1 | LONG | IOD_TPV_TCP | 44901 | 0 | 2700 | 0 | 270 | V | ###.#
TPV_Generator_L3_N_voltageA2 | LONG | IOD_TPV_TCP | 44903 | 0 | 2700 | 0 | 270 | V | ###.#
TPV_Generator_L3_wattsA1 | LONG | IOD_TPV_TCP | 44905 | 0 | 4000 | 0 | 400 | kW | ###.#
TPV_Generator_L3_wattsA2 | LONG | IOD_TPV_TCP | 44907 | 0 | 4000 | 0 | 400 | kW | ###.#
TPV_Generator_phase_rotationA1 | UINT | IOD_TPV_TCP | 46009 | 0 | 2 | 0 | 2 | ř | #
TPV_Generator_phase_rotationA2 | UINT | IOD_TPV_TCP | 46010 | 0 | 2 | 0 | 2 | ř | #
TPVIzpad_CAN_med_K1_K2 | DIGITAL | IOD_TPV_TCP | 00003
TPVjalova_energ_trenutno | INT | IOD_TPV_TCP | 40007
TPVjalova_energija_prej | INT | IOD_TPV_TCP | 40008
TPVKomanda | INT | IOD_TPV_TCP | 40009
TPVMI4agr_nap_RGM_A1 | DIGITAL | IOD_TPV_TCP | 00004
TPVMI4agr_nap_RGM_A2 | DIGITAL | IOD_TPV_TCP | 00005
TPVMI4DA1_2Q1_izklop | DIGITAL | IOD_TPV_TCP | 00006
TPVMI4DA1_2Q1_vklop | DIGITAL | IOD_TPV_TCP | 00007
TPVMI4DA1_del | DIGITAL | IOD_TPV_TCP | 00008
TPVMI4DA1_prip | DIGITAL | IOD_TPV_TCP | 00009
TPVMI4DA1_rezerva | DIGITAL | IOD_TPV_TCP | 00010
TPVMI4DA1_sinh | DIGITAL | IOD_TPV_TCP | 00011
TPVMI4DA1_zagon | DIGITAL | IOD_TPV_TCP | 00012
TPVMI4DA2_2Q1_izklop | DIGITAL | IOD_TPV_TCP | 00013
TPVMI4DA2_2Q1_vklop | DIGITAL | IOD_TPV_TCP | 00014
TPVMI4DA2_del | DIGITAL | IOD_TPV_TCP | 00015
TPVMI4DA2_prip | DIGITAL | IOD_TPV_TCP | 00016
TPVMI4DA2_rezerva | DIGITAL | IOD_TPV_TCP | 00017
TPVMI4DA2_sinh | DIGITAL | IOD_TPV_TCP | 00018
TPVMI4DA2_zagon | DIGITAL | IOD_TPV_TCP | 00019
TPVMI4del_zascA1_11Q1 | DIGITAL | IOD_TPV_TCP | 00020
TPVMI4del_zascA1_12Q1 | DIGITAL | IOD_TPV_TCP | 00021
TPVMI4del_zascA1_13Q1 | DIGITAL | IOD_TPV_TCP | 00022
TPVMI4del_zascA1_14Q1 | DIGITAL | IOD_TPV_TCP | 00023
TPVMI4del_zascA1_15Q1 | DIGITAL | IOD_TPV_TCP | 00024
TPVMI4del_zascA1_16Q1 | DIGITAL | IOD_TPV_TCP | 00025
TPVMI4del_zascA1_17Q1 | DIGITAL | IOD_TPV_TCP | 00026
TPVMI4del_zascA1_2Q1 | DIGITAL | IOD_TPV_TCP | 00027
TPVMI4del_zascA2_11Q1 | DIGITAL | IOD_TPV_TCP | 00028
TPVMI4del_zascA2_12Q1 | DIGITAL | IOD_TPV_TCP | 00029
TPVMI4del_zascA2_13Q1 | DIGITAL | IOD_TPV_TCP | 00030
TPVMI4del_zascA2_14Q1 | DIGITAL | IOD_TPV_TCP | 00031
TPVMI4K2agr_nap_RGM_A3 | DIGITAL | IOD_TPV_TCP | 00032
TPVMI4K2DA3_2Q1_izklop | DIGITAL | IOD_TPV_TCP | 00033
TPVMI4K2DA3_2Q1_vklop | DIGITAL | IOD_TPV_TCP | 00034
TPVMI4K2del_zasc0_11Q1 | DIGITAL | IOD_TPV_TCP | 00035
TPVMI4K2del_zasc0_12Q1 | DIGITAL | IOD_TPV_TCP | 00036
TPVMI4K2del_zasc0_13Q1 | DIGITAL | IOD_TPV_TCP | 00037
TPVMI4K2del_zasc0_14Q1 | DIGITAL | IOD_TPV_TCP | 00038
TPVMI4K2del_zasc0_15Q1 | DIGITAL | IOD_TPV_TCP | 00039
TPVMI4K2del_zasc0_16Q1 | DIGITAL | IOD_TPV_TCP | 00040
TPVMI4K2del_zasc0_17Q1 | DIGITAL | IOD_TPV_TCP | 00041
TPVMI4K2del_zasc0_18Q1 | DIGITAL | IOD_TPV_TCP | 00042
TPVMI4K2del_zasc0_19Q1 | DIGITAL | IOD_TPV_TCP | 00043
TPVMI4K2del_zasc0_20Q1 | DIGITAL | IOD_TPV_TCP | 00044
TPVMI4K2del_zasc0_21Q1 | DIGITAL | IOD_TPV_TCP | 00045
TPVMI4K2del_zasc0_22Q1 | DIGITAL | IOD_TPV_TCP | 00046
TPVMI4K2del_zasc0_23Q1 | DIGITAL | IOD_TPV_TCP | 00047
TPVMI4K2del_zascA3_11Q1 | DIGITAL | IOD_TPV_TCP | 00048
TPVMI4K2del_zascA3_12Q1 | DIGITAL | IOD_TPV_TCP | 00049
TPVMI4K2del_zascA3_13Q1 | DIGITAL | IOD_TPV_TCP | 00050
TPVMI4K2del_zascA3_14Q1 | DIGITAL | IOD_TPV_TCP | 00051
TPVMI4K2del_zascA3_15Q1 | DIGITAL | IOD_TPV_TCP | 00052
TPVMI4K2motorA3_1Q1_prip | DIGITAL | IOD_TPV_TCP | 00053
TPVMI4K2motorA3_2Q1_prip | DIGITAL | IOD_TPV_TCP | 00054
TPVMI4K2mrez_nap_RGM_A3 | DIGITAL | IOD_TPV_TCP | 00055
TPVMI4K2mrezaA3_1Q1_izklop | DIGITAL | IOD_TPV_TCP | 00056
TPVMI4K2mrezaA3_1Q1_vklop | DIGITAL | IOD_TPV_TCP | 00057
TPVMI4K2prenap_zasc0_OK | DIGITAL | IOD_TPV_TCP | 00058
TPVMI4K2prenap_zascA3_OK | DIGITAL | IOD_TPV_TCP | 00059
TPVMI4K2rocni_izk0_11Q1 | DIGITAL | IOD_TPV_TCP | 00060
TPVMI4K2rocni_izk0_12Q1 | DIGITAL | IOD_TPV_TCP | 00061
TPVMI4K2rocni_izk0_13Q1 | DIGITAL | IOD_TPV_TCP | 00062
TPVMI4K2rocni_izk0_14Q1 | DIGITAL | IOD_TPV_TCP | 00063
TPVMI4K2rocni_izk0_15Q1 | DIGITAL | IOD_TPV_TCP | 00064
TPVMI4K2rocni_izk0_16Q1 | DIGITAL | IOD_TPV_TCP | 00065
TPVMI4K2rocni_izk0_17Q1 | DIGITAL | IOD_TPV_TCP | 00066
TPVMI4K2rocni_izk0_18Q1 | DIGITAL | IOD_TPV_TCP | 00067
TPVMI4K2rocni_izk0_19Q1 | DIGITAL | IOD_TPV_TCP | 00068
TPVMI4K2rocni_izk0_20Q1 | DIGITAL | IOD_TPV_TCP | 00069
TPVMI4K2rocni_izk0_21Q1 | DIGITAL | IOD_TPV_TCP | 00070
TPVMI4K2rocni_izk0_22Q1 | DIGITAL | IOD_TPV_TCP | 00071
TPVMI4K2rocni_izk0_23Q1 | DIGITAL | IOD_TPV_TCP | 00072
TPVMI4K2rocni_izkA3_11Q1 | DIGITAL | IOD_TPV_TCP | 00073
TPVMI4K2rocni_izkA3_12Q1 | DIGITAL | IOD_TPV_TCP | 00074
TPVMI4K2rocni_izkA3_13Q1 | DIGITAL | IOD_TPV_TCP | 00075
TPVMI4K2rocni_izkA3_14Q1 | DIGITAL | IOD_TPV_TCP | 00076
TPVMI4K2rocni_izkA3_15Q1 | DIGITAL | IOD_TPV_TCP | 00077
TPVMI4K2stik0_11Q1_vkl | DIGITAL | IOD_TPV_TCP | 00078
TPVMI4K2stik0_12Q1_vkl | DIGITAL | IOD_TPV_TCP | 00079
TPVMI4K2stik0_13Q1_vkl | DIGITAL | IOD_TPV_TCP | 00080
TPVMI4K2stik0_14Q1_vkl | DIGITAL | IOD_TPV_TCP | 00081
TPVMI4K2stik0_15Q1_vkl | DIGITAL | IOD_TPV_TCP | 00082
TPVMI4K2stik0_16Q1_vkl | DIGITAL | IOD_TPV_TCP | 00083
TPVMI4K2stik0_17Q1_vkl | DIGITAL | IOD_TPV_TCP | 00084
TPVMI4K2stik0_18Q1_vkl | DIGITAL | IOD_TPV_TCP | 00085
TPVMI4K2stik0_19Q1_vkl | DIGITAL | IOD_TPV_TCP | 00086
TPVMI4K2stik0_1Q1_vkl | DIGITAL | IOD_TPV_TCP | 00087
TPVMI4K2stik0_20Q1_vkl | DIGITAL | IOD_TPV_TCP | 00088
TPVMI4K2stik0_21Q1_vkl | DIGITAL | IOD_TPV_TCP | 00089
TPVMI4K2stik0_22Q1_vkl | DIGITAL | IOD_TPV_TCP | 00090
TPVMI4K2stik0_23Q1_vkl | DIGITAL | IOD_TPV_TCP | 00091
TPVMI4K2stikA3_11Q1_vkl | DIGITAL | IOD_TPV_TCP | 00092
TPVMI4K2stikA3_12Q1_vkl | DIGITAL | IOD_TPV_TCP | 00093
TPVMI4K2stikA3_13Q1_vkl | DIGITAL | IOD_TPV_TCP | 00094
TPVMI4K2stikA3_14Q1_vkl | DIGITAL | IOD_TPV_TCP | 00095
TPVMI4K2stikA3_15Q1_vkl | DIGITAL | IOD_TPV_TCP | 00096
TPVMI4K2stikA3_1Q1_vkl | DIGITAL | IOD_TPV_TCP | 00097
TPVMI4K2stikA3_2Q1_vkl | DIGITAL | IOD_TPV_TCP | 00098
TPVMI4krmDA_daljinsko | DIGITAL | IOD_TPV_TCP | 00099
TPVMI4motorA1_1Q1_prip | DIGITAL | IOD_TPV_TCP | 00100
TPVMI4motorA1_2Q1_prip | DIGITAL | IOD_TPV_TCP | 00101
TPVMI4motorA2_1Q1_prip | DIGITAL | IOD_TPV_TCP | 00102
TPVMI4motorA2_2Q1_prip | DIGITAL | IOD_TPV_TCP | 00103
TPVMI4motorA2_6Q1_prip | DIGITAL | IOD_TPV_TCP | 00104
TPVMI4mrez_nap_RGM_A1 | DIGITAL | IOD_TPV_TCP | 00105
TPVMI4mrez_nap_RGM_A2 | DIGITAL | IOD_TPV_TCP | 00106
TPVMI4mrezaA1_1Q1_izklop | DIGITAL | IOD_TPV_TCP | 00107
TPVMI4mrezaA1_1Q1_vklop | DIGITAL | IOD_TPV_TCP | 00108
TPVMI4mrezaA2_1Q1_izklop | DIGITAL | IOD_TPV_TCP | 00109
TPVMI4mrezaA2_1Q1_vklop | DIGITAL | IOD_TPV_TCP | 00110
TPVMI4napaka_alarm_DA1 | DIGITAL | IOD_TPV_TCP | 00111
TPVMI4napaka_alarm_DA2 | DIGITAL | IOD_TPV_TCP | 00112
TPVMI4prenap_zascA1_OK | DIGITAL | IOD_TPV_TCP | 00113
TPVMI4prenap_zascA2_OK | DIGITAL | IOD_TPV_TCP | 00114
TPVMI4rezerva_DA1 | DIGITAL | IOD_TPV_TCP | 00115
TPVMI4rocni_izkA1_11Q1 | DIGITAL | IOD_TPV_TCP | 00116
TPVMI4rocni_izkA1_12Q1 | DIGITAL | IOD_TPV_TCP | 00117
TPVMI4rocni_izkA1_13Q1 | DIGITAL | IOD_TPV_TCP | 00118
TPVMI4rocni_izkA1_14Q1 | DIGITAL | IOD_TPV_TCP | 00119
TPVMI4rocni_izkA1_15Q1 | DIGITAL | IOD_TPV_TCP | 00120
TPVMI4rocni_izkA1_16Q1 | DIGITAL | IOD_TPV_TCP | 00121
TPVMI4rocni_izkA1_17Q1 | DIGITAL | IOD_TPV_TCP | 00122
TPVMI4rocni_izkA2_11Q1 | DIGITAL | IOD_TPV_TCP | 00123
TPVMI4rocni_izkA2_12Q1 | DIGITAL | IOD_TPV_TCP | 00124
TPVMI4rocni_izkA2_13Q1 | DIGITAL | IOD_TPV_TCP | 00125
TPVMI4rocni_izkA2_14Q1 | DIGITAL | IOD_TPV_TCP | 00126
TPVMI4sinhroniziranje_DA1 | DIGITAL | IOD_TPV_TCP | 00127
TPVMI4sinhroniziranje_DA2 | DIGITAL | IOD_TPV_TCP | 00128
TPVMI4splosna_napaka_DA1 | DIGITAL | IOD_TPV_TCP | 00129
TPVMI4splosna_napaka_DA2 | DIGITAL | IOD_TPV_TCP | 00130
TPVMI4stikA1_11Q1_vkl | DIGITAL | IOD_TPV_TCP | 00131
TPVMI4stikA1_12Q1_vkl | DIGITAL | IOD_TPV_TCP | 00132
TPVMI4stikA1_13Q1_vkl | DIGITAL | IOD_TPV_TCP | 00133
TPVMI4stikA1_14Q1_vkl | DIGITAL | IOD_TPV_TCP | 00134
TPVMI4stikA1_15Q1_vkl | DIGITAL | IOD_TPV_TCP | 00135
TPVMI4stikA1_16Q1_vkl | DIGITAL | IOD_TPV_TCP | 00136
TPVMI4stikA1_17Q1_vkl | DIGITAL | IOD_TPV_TCP | 00137
TPVMI4stikA1_1Q1_vkl | DIGITAL | IOD_TPV_TCP | 00138
TPVMI4stikA1_2Q1_vkl | DIGITAL | IOD_TPV_TCP | 00139
TPVMI4stikA1_6Q1_vkl | DIGITAL | IOD_TPV_TCP | 00140
TPVMI4stikA2_11Q1_vkl | DIGITAL | IOD_TPV_TCP | 00141
TPVMI4stikA2_12Q1_vkl | DIGITAL | IOD_TPV_TCP | 00142
TPVMI4stikA2_13Q1_vkl | DIGITAL | IOD_TPV_TCP | 00143
TPVMI4stikA2_14Q1_vkl | DIGITAL | IOD_TPV_TCP | 00144
TPVMI4stikA2_1Q1_vkl | DIGITAL | IOD_TPV_TCP | 00145
TPVMI4stikA2_2Q1_vkl | DIGITAL | IOD_TPV_TCP | 00146
TPVMI4vezno_6Q1_izklop | DIGITAL | IOD_TPV_TCP | 00147
TPVMI4vezno_6Q1_vklop | DIGITAL | IOD_TPV_TCP | 00148
TPVMI4vzporedno_del_nikoli | DIGITAL | IOD_TPV_TCP | 00149
TPVMI4vzporedno_del_nikoli_info | DIGITAL | IOD_TPV_TCP | 00150
TPVMI4vzporedno_del_po_potrebi | DIGITAL | IOD_TPV_TCP | 00151
TPVMI4vzporedno_del_po_potrebi_info | DIGITAL | IOD_TPV_TCP | 00152
TPVMI4vzporedno_del_vedno | DIGITAL | IOD_TPV_TCP | 00153
TPVMI4vzporedno_del_vedno_info | DIGITAL | IOD_TPV_TCP | 00154
TPVMI4zaganjanje_DA1 | DIGITAL | IOD_TPV_TCP | 00155
TPVMI4zaganjanje_DA2 | DIGITAL | IOD_TPV_TCP | 00156
TPVmrezaDA3motorni_pogon_okvara | DIGITAL | IOD_TPV_TCP | 00157
TPVmrezaDA3stikalo_okvara | DIGITAL | IOD_TPV_TCP | 00158
TPVNapaka_v_kom_cirk_DA1 | DIGITAL | IOD_TPV_TCP | 00159
TPVNapaka_v_kom_cirk_DA2 | DIGITAL | IOD_TPV_TCP | 00160
TPVNapakaCOMModBus | DIGITAL | IOD_TPV_TCP | 00161
TPVNapakaVKomunikaciji_Circutor1 | DIGITAL | IOD_TPV_TCP | 00162
TPVNapakaVKomunikaciji_Circutor10 | DIGITAL | IOD_TPV_TCP | 00163
TPVNapakaVKomunikaciji_Circutor11 | DIGITAL | IOD_TPV_TCP | 00164
TPVNapakaVKomunikaciji_Circutor12 | DIGITAL | IOD_TPV_TCP | 00165
TPVNapakaVKomunikaciji_Circutor13 | DIGITAL | IOD_TPV_TCP | 00166
TPVNapakaVKomunikaciji_Circutor14 | DIGITAL | IOD_TPV_TCP | 00167
TPVNapakaVKomunikaciji_Circutor15 | DIGITAL | IOD_TPV_TCP | 00168
TPVNapakaVKomunikaciji_Circutor16 | DIGITAL | IOD_TPV_TCP | 00169
TPVNapakaVKomunikaciji_Circutor17 | DIGITAL | IOD_TPV_TCP | 00170
TPVNapakaVKomunikaciji_Circutor18 | DIGITAL | IOD_TPV_TCP | 00171
TPVNapakaVKomunikaciji_Circutor19 | DIGITAL | IOD_TPV_TCP | 00172
TPVNapakaVKomunikaciji_Circutor2 | DIGITAL | IOD_TPV_TCP | 00173
TPVNapakaVKomunikaciji_Circutor20 | DIGITAL | IOD_TPV_TCP | 00174
TPVNapakaVKomunikaciji_Circutor21 | DIGITAL | IOD_TPV_TCP | 00175
TPVNapakaVKomunikaciji_Circutor22 | DIGITAL | IOD_TPV_TCP | 00176
TPVNapakaVKomunikaciji_Circutor23 | DIGITAL | IOD_TPV_TCP | 00177
TPVNapakaVKomunikaciji_Circutor24 | DIGITAL | IOD_TPV_TCP | 00178
TPVNapakaVKomunikaciji_Circutor25 | DIGITAL | IOD_TPV_TCP | 00179
TPVNapakaVKomunikaciji_Circutor3 | DIGITAL | IOD_TPV_TCP | 00180
TPVNapakaVKomunikaciji_Circutor4 | DIGITAL | IOD_TPV_TCP | 00181
TPVNapakaVKomunikaciji_Circutor5 | DIGITAL | IOD_TPV_TCP | 00182
TPVNapakaVKomunikaciji_Circutor6 | DIGITAL | IOD_TPV_TCP | 00183
TPVNapakaVKomunikaciji_Circutor7 | DIGITAL | IOD_TPV_TCP | 00184
TPVNapakaVKomunikaciji_Circutor8 | DIGITAL | IOD_TPV_TCP | 00185
TPVNapakaVKomunikaciji_Circutor9 | DIGITAL | IOD_TPV_TCP | 00186
TPVNastaviDanMI | INT | IOD_TPV_TCP | 40010
TPVNastaviLetoMI | INT | IOD_TPV_TCP | 40011
TPVNastaviMesecMI | INT | IOD_TPV_TCP | 40012
TPVNastaviMinutaMI | INT | IOD_TPV_TCP | 40013
TPVNastaviSekundaMI | INT | IOD_TPV_TCP | 40014
TPVNastaviUraMI | INT | IOD_TPV_TCP | 40015
TPVOil_pressureA1 | UINT | IOD_TPV_TCP | 46011 | 0 | 10000 | 0 | 10000 | Kpa
TPVOil_pressureA2 | UINT | IOD_TPV_TCP | 46012 | 0 | 10000 | 0 | 10000 | Kpa
TPVRDASlabaBaterijaMI4 | DIGITAL | IOD_TPV_TCP | 00187
TPVSlabaBaterijaMI4 | DIGITAL | IOD_TPV_TCP | 00188
TPVSlabaBaterijaPLC1 | DIGITAL | IOD_TPV_TCP | 00189
TPVSlabaBaterijaPLC2 | DIGITAL | IOD_TPV_TCP | 00190
TPVStatus | INT | IOD_TPV_TCP | 40016
TPVstikaloDA3_okvara | DIGITAL | IOD_TPV_TCP | 00191
TPVUI_MI4K2DA3_2Q1_izklop | DIGITAL | IOD_TPV_TCP | 00192
TPVUI_MI4K2DA3_2Q1_vklop | DIGITAL | IOD_TPV_TCP | 00193
TPVUI_MI4K2mrezaA3_1Q1_izklop | DIGITAL | IOD_TPV_TCP | 00194
TPVUI_MI4K2mrezaA3_1Q1_vklop | DIGITAL | IOD_TPV_TCP | 00195
s | DIGITAL | IOD_TPV_mem | D1
z | DIGITAL | IOD_TPV_mem | D2
TP_DanEnergCirc_DOVOD | REAL | IOD_TPV_disk | R7100[30]
TP_CasDDanEnerg | INT | IOD_TPV_disk | I30[30]
TP_CasMDanEnerg | INT | IOD_TPV_disk | I60[30]
TP_TedenEnergCirc_DOVOD | REAL | IOD_TPV_disk | R7160[30]
TP_CasDTedenEnerg | INT | IOD_TPV_disk | I120[30]
TP_CasMTedenEnerg | INT | IOD_TPV_disk | I150[30]
TP_MesecEnergCirc_DOVOD | REAL | IOD_TPV_disk | R7220[30]
TP_CasDMesecEnerg | INT | IOD_TPV_disk | I210[30]
TP_CasMMesecEnerg | INT | IOD_TPV_disk | I240[30]
TP_StSt_DanEnergCirc_DOVOD | LONG | IOD_TPV_disk | L270
TP_StSt_TedenEnergCirc_DOVOD | LONG | IOD_TPV_disk | L272
TP_StSt_MesecEnergCirc_DOVOD | LONG | IOD_TPV_disk | L274
TP_StStCasDDanEnerg | LONG | IOD_TPV_disk | L276
TP_StStCasMDanEnerg | LONG | IOD_TPV_disk | L278
TP_StStCasDTedenEnerg | LONG | IOD_TPV_disk | L280
TP_StStCasMTedenEnerg | LONG | IOD_TPV_disk | L282
TP_StStCasDMesecEnerg | LONG | IOD_TPV_disk | L284
TP_StStCasMMesecEnerg | LONG | IOD_TPV_disk | L286
TP_DanEnergCirc_R2K1A | REAL | IOD_TPV_disk | R290[30]
TP_TedenEnergCirc_R2K1A | REAL | IOD_TPV_disk | R320[30]
TP_MesecEnergCirc_R2K1A | REAL | IOD_TPV_disk | R350[30]
TP_DanEnergCirc_R2K2A | REAL | IOD_TPV_disk | R380[30]
TP_TedenEnergCirc_R2K2A | REAL | IOD_TPV_disk | R410[30]
TP_MesecEnergCirc_R2K2A | REAL | IOD_TPV_disk | R440[30]
TP_DanEnergCirc_R3KCA | REAL | IOD_TPV_disk | R470[30]
TP_TedenEnergCirc_R3KCA | REAL | IOD_TPV_disk | R500[30]
TP_MesecEnergCirc_R3KCA | REAL | IOD_TPV_disk | R530[30]
TP_DanEnergCirc_RGUPS | REAL | IOD_TPV_disk | R560[30]
TP_TedenEnergCirc_RGUPS | REAL | IOD_TPV_disk | R590[30]
TP_MesecEnergCirc_RGUPS | REAL | IOD_TPV_disk | R620[30]
TP_DanEnergCirc_REZ1A | REAL | IOD_TPV_disk | R650[30]
TP_TedenEnergCirc_REZ1A | REAL | IOD_TPV_disk | R680[30]
TP_MesecEnergCirc_REZ1A | REAL | IOD_TPV_disk | R710[30]
TP_DanEnergCirc_REZ2A | REAL | IOD_TPV_disk | R740[30]
TP_TedenEnergCirc_REZ2A | REAL | IOD_TPV_disk | R770[30]
TP_MesecEnergCirc_REZ2A | REAL | IOD_TPV_disk | R800[30]
TP_DanEnergCirc_RGMA1 | REAL | IOD_TPV_disk | R830[30]
TP_TedenEnergCirc_RGMA1 | REAL | IOD_TPV_disk | R860[30]
TP_MesecEnergCirc_RGMA1 | REAL | IOD_TPV_disk | R890[30]
TP_DanEnergCirc_RGMA2 | REAL | IOD_TPV_disk | R920[30]
TP_TedenEnergCirc_RGMA2 | REAL | IOD_TPV_disk | R950[30]
TP_MesecEnergCirc_RGMA2 | REAL | IOD_TPV_disk | R980[30]
TP_DanEnergCirc_R1K4 | REAL | IOD_TPV_disk | R1010[30]
TP_TedenEnergCirc_R1K4 | REAL | IOD_TPV_disk | R1040[30]
TP_MesecEnergCirc_R1K4 | REAL | IOD_TPV_disk | R1070[30]
TP_DanEnergCirc_REZ1A2 | REAL | IOD_TPV_disk | R1100[30]
TP_TedenEnergCirc_REZ1A2 | REAL | IOD_TPV_disk | R1130[30]
TP_MesecEnergCirc_REZ1A2 | REAL | IOD_TPV_disk | R1160[30]
TP_DanEnergCirc_REZ2A2 | REAL | IOD_TPV_disk | R1190[30]
TP_TedenEnergCirc_REZ2A2 | REAL | IOD_TPV_disk | R1220[30]
TP_MesecEnergCirc_REZ2A2 | REAL | IOD_TPV_disk | R1250[30]
TP_DanEnergCirc_RGM0A1 | REAL | IOD_TPV_disk | R1280[30]
TP_TedenEnergCirc_RGM0A1 | REAL | IOD_TPV_disk | R1310[30]
TP_MesecEnergCirc_RGM0A1 | REAL | IOD_TPV_disk | R1340[30]
TP_DanEnergCirc_RGM0A2 | REAL | IOD_TPV_disk | R1370[30]
TP_TedenEnergCirc_RGM0A2 | REAL | IOD_TPV_disk | R1400[30]
TP_MesecEnergCirc_RGM0A2 | REAL | IOD_TPV_disk | R1430[30]
TP_DanEnergCirc_RGM0A3 | REAL | IOD_TPV_disk | R1460[30]
TP_TedenEnergCirc_RGM0A3 | REAL | IOD_TPV_disk | R1490[30]
TP_MesecEnergCirc_RGM0A3 | REAL | IOD_TPV_disk | R1520[30]
TP_DanEnergCirc_R2K1E | REAL | IOD_TPV_disk | R1550[30]
TP_TedenEnergCirc_R2K1E | REAL | IOD_TPV_disk | R1580[30]
TP_MesecEnergCirc_R2K1E | REAL | IOD_TPV_disk | R1610[30]
TP_DanEnergCirc_R2K2E | REAL | IOD_TPV_disk | R1640[30]
TP_TedenEnergCirc_R2K2E | REAL | IOD_TPV_disk | R1670[30]
TP_MesecEnergCirc_R2K2E | REAL | IOD_TPV_disk | R1700[30]
TP_DanEnergCirc_RDD | REAL | IOD_TPV_disk | R1730[30]
TP_TedenEnergCirc_RDD | REAL | IOD_TPV_disk | R1760[30]
TP_MesecEnergCirc_RDD | REAL | IOD_TPV_disk | R1790[30]
TP_DanEnergCirc_RKOM | REAL | IOD_TPV_disk | R1820[30]
TP_TedenEnergCirc_RKOM | REAL | IOD_TPV_disk | R1850[30]
TP_MesecEnergCirc_RKOM | REAL | IOD_TPV_disk | R1880[30]
TP_DanEnergCirc_ECP | REAL | IOD_TPV_disk | R1910[30]
TP_TedenEnergCirc_ECP | REAL | IOD_TPV_disk | R1940[30]
TP_MesecEnergCirc_ECP | REAL | IOD_TPV_disk | R1970[30]
TP_DanEnergCirc_ECPMNC | REAL | IOD_TPV_disk | R2000[30]
TP_TedenEnergCirc_ECPMNC | REAL | IOD_TPV_disk | R2030[30]
TP_MesecEnergCirc_ECPMNC | REAL | IOD_TPV_disk | R2060[30]
TP_DanEnergCirc_REZ1RGM0 | REAL | IOD_TPV_disk | R2090[30]
TP_TedenEnergCirc_REZ1RGM0 | REAL | IOD_TPV_disk | R2120[30]
TP_MesecEnergCirc_REZ1RGM0 | REAL | IOD_TPV_disk | R2150[30]
TP_DanEnergCirc_REZ2RGM0 | REAL | IOD_TPV_disk | R2180[30]
TP_TedenEnergCirc_REZ2RGM0 | REAL | IOD_TPV_disk | R2210[30]
TP_MesecEnergCirc_REZ2RGM0 | REAL | IOD_TPV_disk | R2240[30]
TP_DanEnergCirc_REZ3RGM0 | REAL | IOD_TPV_disk | R2270[30]
TP_TedenEnergCirc_REZ3RGM0 | REAL | IOD_TPV_disk | R2300[30]
TP_MesecEnergCirc_REZ3RGM0 | REAL | IOD_TPV_disk | R2330[30]
TP_DanEnergCirc_RGMA3 | REAL | IOD_TPV_disk | R2360[30]
TP_TedenEnergCirc_RGMA3 | REAL | IOD_TPV_disk | R2390[30]
TP_MesecEnergCirc_RGMA3 | REAL | IOD_TPV_disk | R2420[30]
TP_StSt_DanEnergCirc_R2K1A | LONG | IOD_TPV_disk | L2456
TP_StSt_TedenEnergCirc_R2K1A | LONG | IOD_TPV_disk | L2458
TP_StSt_MesecEnergCirc_R2K1A | LONG | IOD_TPV_disk | L2460
TP_StSt_DanEnergCirc_R2K2A | LONG | IOD_TPV_disk | L2462
TP_StSt_TedenEnergCirc_R2K2A | LONG | IOD_TPV_disk | L2464
TP_StSt_MesecEnergCirc_R2K2A | LONG | IOD_TPV_disk | L2466
TP_StSt_DanEnergCirc_R3KCA | LONG | IOD_TPV_disk | L2468
TP_StSt_TedenEnergCirc_R3KCA | LONG | IOD_TPV_disk | L2470
TP_StSt_MesecEnergCirc_R3KCA | LONG | IOD_TPV_disk | L2472
TP_StSt_DanEnergCirc_RGUPS | LONG | IOD_TPV_disk | L2474
TP_StSt_TedenEnergCirc_RGUPS | LONG | IOD_TPV_disk | L2476
TP_StSt_MesecEnergCirc_RGUPS | LONG | IOD_TPV_disk | L2478
TP_StSt_DanEnergCirc_REZ1A | LONG | IOD_TPV_disk | L2480
TP_StSt_TedenEnergCirc_REZ1A | LONG | IOD_TPV_disk | L2482
TP_StSt_MesecEnergCirc_REZ1A | LONG | IOD_TPV_disk | L2484
TP_StSt_DanEnergCirc_REZ2A | LONG | IOD_TPV_disk | L2486
TP_StSt_TedenEnergCirc_REZ2A | LONG | IOD_TPV_disk | L2488
TP_StSt_MesecEnergCirc_REZ2A | LONG | IOD_TPV_disk | L2490
TP_StSt_DanEnergCirc_RGMA1 | LONG | IOD_TPV_disk | L2492
TP_StSt_TedenEnergCirc_RGMA1 | LONG | IOD_TPV_disk | L2494
TP_StSt_MesecEnergCirc_RGMA1 | LONG | IOD_TPV_disk | L2496
TP_StSt_DanEnergCirc_RGMA2 | LONG | IOD_TPV_disk | L2498
TP_StSt_TedenEnergCirc_RGMA2 | LONG | IOD_TPV_disk | L2500
TP_StSt_MesecEnergCirc_RGMA2 | LONG | IOD_TPV_disk | L2502
TP_StSt_DanEnergCirc_R1K4 | LONG | IOD_TPV_disk | L2504
TP_StSt_TedenEnergCirc_R1K4 | LONG | IOD_TPV_disk | L2506
TP_StSt_MesecEnergCirc_R1K4 | LONG | IOD_TPV_disk | L2508
TP_StSt_DanEnergCirc_REZ1A2 | LONG | IOD_TPV_disk | L2510
TP_StSt_TedenEnergCirc_REZ1A2 | LONG | IOD_TPV_disk | L2512
TP_StSt_MesecEnergCirc_REZ1A2 | LONG | IOD_TPV_disk | L2514
TP_StSt_DanEnergCirc_REZ2A2 | LONG | IOD_TPV_disk | L2516
TP_StSt_TedenEnergCirc_REZ2A2 | LONG | IOD_TPV_disk | L2518
TP_StSt_MesecEnergCirc_REZ2A2 | LONG | IOD_TPV_disk | L2520
TP_StSt_DanEnergCirc_RGM0A1 | LONG | IOD_TPV_disk | L2522
TP_StSt_TedenEnergCirc_RGM0A1 | LONG | IOD_TPV_disk | L2524
TP_StSt_MesecEnergCirc_RGM0A1 | LONG | IOD_TPV_disk | L2526
TP_StSt_DanEnergCirc_RGM0A2 | LONG | IOD_TPV_disk | L2528
TP_StSt_TedenEnergCirc_RGM0A2 | LONG | IOD_TPV_disk | L2530
TP_StSt_MesecEnergCirc_RGM0A2 | LONG | IOD_TPV_disk | L2532
TP_StSt_DanEnergCirc_RGM0A3 | LONG | IOD_TPV_disk | L2534
TP_StSt_TedenEnergCirc_RGM0A3 | LONG | IOD_TPV_disk | L2536
TP_StSt_MesecEnergCirc_RGM0A3 | LONG | IOD_TPV_disk | L2538
TP_StSt_DanEnergCirc_R2K1E | LONG | IOD_TPV_disk | L2540
TP_StSt_TedenEnergCirc_R2K1E | LONG | IOD_TPV_disk | L2542
TP_StSt_MesecEnergCirc_R2K1E | LONG | IOD_TPV_disk | L2544
TP_StSt_DanEnergCirc_R2K2E | LONG | IOD_TPV_disk | L2546
TP_StSt_TedenEnergCirc_R2K2E | LONG | IOD_TPV_disk | L2548
TP_StSt_MesecEnergCirc_R2K2E | LONG | IOD_TPV_disk | L2550
TP_StSt_DanEnergCirc_RDD | LONG | IOD_TPV_disk | L2552
TP_StSt_TedenEnergCirc_RDD | LONG | IOD_TPV_disk | L2554
TP_StSt_MesecEnergCirc_RDD | LONG | IOD_TPV_disk | L2556
TP_StSt_DanEnergCirc_RKOM | LONG | IOD_TPV_disk | L2558
TP_StSt_TedenEnergCirc_RKOM | LONG | IOD_TPV_disk | L2560
TP_StSt_MesecEnergCirc_RKOM | LONG | IOD_TPV_disk | L2562
TP_StSt_DanEnergCirc_ECP | LONG | IOD_TPV_disk | L2564
TP_StSt_TedenEnergCirc_ECP | LONG | IOD_TPV_disk | L2566
TP_StSt_MesecEnergCirc_ECP | LONG | IOD_TPV_disk | L2568
TP_StSt_DanEnergCirc_ECPMNC | LONG | IOD_TPV_disk | L2570
TP_StSt_TedenEnergCirc_ECPMNC | LONG | IOD_TPV_disk | L2572
TP_StSt_MesecEnergCirc_ECPMNC | LONG | IOD_TPV_disk | L2574
TP_StSt_DanEnergCirc_REZ1RGM0 | LONG | IOD_TPV_disk | L2576
TP_StSt_TedenEnergCirc_REZ1RGM0 | LONG | IOD_TPV_disk | L2578
TP_StSt_MesecEnergCirc_REZ1RGM0 | LONG | IOD_TPV_disk | L2580
TP_StSt_DanEnergCirc_REZ2RGM0 | LONG | IOD_TPV_disk | L2582
TP_StSt_TedenEnergCirc_REZ2RGM0 | LONG | IOD_TPV_disk | L2584
TP_StSt_MesecEnergCirc_REZ2RGM0 | LONG | IOD_TPV_disk | L2586
TP_StSt_DanEnergCirc_REZ3RGM0 | LONG | IOD_TPV_disk | L2588
TP_StSt_TedenEnergCirc_REZ3RGM0 | LONG | IOD_TPV_disk | L2590
TP_StSt_MesecEnergCirc_REZ3RGM0 | LONG | IOD_TPV_disk | L2592
TP_StSt_DanEnergCirc_RGMA3 | LONG | IOD_TPV_disk | L2594
TP_StSt_TedenEnergCirc_RGMA3 | LONG | IOD_TPV_disk | L2596
TP_StSt_MesecEnergCirc_RGMA3 | LONG | IOD_TPV_disk | L2598
TPV_PULZ_1s | DIGITAL | IOD_TPV_mem | D2600
TP_op_alarm_Analizator1tok_L1 | DIGITAL | IOD_TPV_mem | D2601
TP_op_alarm_Analizator2tok_L1 | DIGITAL | IOD_TPV_mem | D2602
TP_op_alarm_Analizator3tok_L1 | DIGITAL | IOD_TPV_mem | D2603
TP_op_alarm_Analizator4tok_L1 | DIGITAL | IOD_TPV_mem | D2604
TP_op_alarm_Analizator5tok_L1 | DIGITAL | IOD_TPV_mem | D2605
TP_op_alarm_Analizator6tok_L1 | DIGITAL | IOD_TPV_mem | D2606
TP_op_alarm_Analizator7tok_L1 | DIGITAL | IOD_TPV_mem | D2607
TP_op_alarm_Analizator8tok_L1 | DIGITAL | IOD_TPV_mem | D2608
TP_op_alarm_Analizator9tok_L1 | DIGITAL | IOD_TPV_mem | D2609
TP_op_alarm_Analizator10tok_L1 | DIGITAL | IOD_TPV_mem | D2610
TP_op_alarm_Analizator11tok_L1 | DIGITAL | IOD_TPV_mem | D2611
TP_op_alarm_Analizator12tok_L1 | DIGITAL | IOD_TPV_mem | D2612
TP_op_alarm_Analizator13tok_L1 | DIGITAL | IOD_TPV_mem | D2613
TP_op_alarm_Analizator14tok_L1 | DIGITAL | IOD_TPV_mem | D2614
TP_op_alarm_Analizator15tok_L1 | DIGITAL | IOD_TPV_mem | D2615
TP_op_alarm_Analizator16tok_L1 | DIGITAL | IOD_TPV_mem | D2616
TP_op_alarm_Analizator17tok_L1 | DIGITAL | IOD_TPV_mem | D2617
TP_op_alarm_Analizator18tok_L1 | DIGITAL | IOD_TPV_mem | D2618
TP_op_alarm_Analizator19tok_L1 | DIGITAL | IOD_TPV_mem | D2619
TP_op_alarm_Analizator20tok_L1 | DIGITAL | IOD_TPV_mem | D2620
TP_op_alarm_Analizator21tok_L1 | DIGITAL | IOD_TPV_mem | D2621
TP_op_alarm_Analizator22tok_L1 | DIGITAL | IOD_TPV_mem | D2622
TP_op_alarm_Analizator23tok_L1 | DIGITAL | IOD_TPV_mem | D2623
TP_op_alarm_Analizator24tok_L1 | DIGITAL | IOD_TPV_mem | D2624
TP_op_alarm_Analizator25tok_L1 | DIGITAL | IOD_TPV_mem | D2625
TP_op_om_alarm_Analizator_tok_L1 | DIGITAL | IOD_TPV_disk | D2628[30]
TP_op_pri_alarm_Analizator_tok_L1 | LONG | IOD_TPV_disk | L2658[30]
TP_op_alarm_Analizator1tok_L2 | DIGITAL | IOD_TPV_mem | D2689
TP_op_alarm_Analizator2tok_L2 | DIGITAL | IOD_TPV_mem | D2690
TP_op_alarm_Analizator3tok_L2 | DIGITAL | IOD_TPV_mem | D2691
TP_op_alarm_Analizator4tok_L2 | DIGITAL | IOD_TPV_mem | D2692
TP_op_alarm_Analizator5tok_L2 | DIGITAL | IOD_TPV_mem | D2693
TP_op_alarm_Analizator6tok_L2 | DIGITAL | IOD_TPV_mem | D2694
TP_op_alarm_Analizator7tok_L2 | DIGITAL | IOD_TPV_mem | D2695
TP_op_alarm_Analizator8tok_L2 | DIGITAL | IOD_TPV_mem | D2696
TP_op_alarm_Analizator9tok_L2 | DIGITAL | IOD_TPV_mem | D2697
TP_op_alarm_Analizator10tok_L2 | DIGITAL | IOD_TPV_mem | D2698
TP_op_alarm_Analizator11tok_L2 | DIGITAL | IOD_TPV_mem | D2699
TP_op_alarm_Analizator12tok_L2 | DIGITAL | IOD_TPV_mem | D2700
TP_op_alarm_Analizator13tok_L2 | DIGITAL | IOD_TPV_mem | D2701
TP_op_alarm_Analizator14tok_L2 | DIGITAL | IOD_TPV_mem | D2702
TP_op_alarm_Analizator15tok_L2 | DIGITAL | IOD_TPV_mem | D2703
TP_op_alarm_Analizator16tok_L2 | DIGITAL | IOD_TPV_mem | D2704
TP_op_alarm_Analizator17tok_L2 | DIGITAL | IOD_TPV_mem | D2705
TP_op_alarm_Analizator18tok_L2 | DIGITAL | IOD_TPV_mem | D2706
TP_op_alarm_Analizator19tok_L2 | DIGITAL | IOD_TPV_mem | D2707
TP_op_alarm_Analizator20tok_L2 | DIGITAL | IOD_TPV_mem | D2708
TP_op_alarm_Analizator21tok_L2 | DIGITAL | IOD_TPV_mem | D2709
TP_op_alarm_Analizator22tok_L2 | DIGITAL | IOD_TPV_mem | D2710
TP_op_alarm_Analizator23tok_L2 | DIGITAL | IOD_TPV_mem | D2711
TP_op_alarm_Analizator24tok_L2 | DIGITAL | IOD_TPV_mem | D2712
TP_op_alarm_Analizator25tok_L2 | DIGITAL | IOD_TPV_mem | D2713
TP_op_om_alarm_Analizator_tok_L2 | DIGITAL | IOD_TPV_disk | D2714[30]
TP_op_pri_alarm_Analizator_tok_L2 | LONG | IOD_TPV_disk | L2744[30]
TP_op_alarm_Analizator1tok_L3 | DIGITAL | IOD_TPV_mem | D2774
TP_op_alarm_Analizator2tok_L3 | DIGITAL | IOD_TPV_mem | D2775
TP_op_alarm_Analizator3tok_L3 | DIGITAL | IOD_TPV_mem | D2776
TP_op_alarm_Analizator4tok_L3 | DIGITAL | IOD_TPV_mem | D2777
TP_op_alarm_Analizator5tok_L3 | DIGITAL | IOD_TPV_mem | D2778
TP_op_alarm_Analizator6tok_L3 | DIGITAL | IOD_TPV_mem | D2779
TP_op_alarm_Analizator7tok_L3 | DIGITAL | IOD_TPV_mem | D2780
TP_op_alarm_Analizator8tok_L3 | DIGITAL | IOD_TPV_mem | D2781
TP_op_alarm_Analizator9tok_L3 | DIGITAL | IOD_TPV_mem | D2782
TP_op_alarm_Analizator10tok_L3 | DIGITAL | IOD_TPV_mem | D2783
TP_op_alarm_Analizator11tok_L3 | DIGITAL | IOD_TPV_mem | D2784
TP_op_alarm_Analizator12tok_L3 | DIGITAL | IOD_TPV_mem | D2785
TP_op_alarm_Analizator13tok_L3 | DIGITAL | IOD_TPV_mem | D2786
TP_op_alarm_Analizator14tok_L3 | DIGITAL | IOD_TPV_mem | D2787
TP_op_alarm_Analizator15tok_L3 | DIGITAL | IOD_TPV_mem | D2788
TP_op_alarm_Analizator16tok_L3 | DIGITAL | IOD_TPV_mem | D2789
TP_op_alarm_Analizator17tok_L3 | DIGITAL | IOD_TPV_mem | D2790
TP_op_alarm_Analizator18tok_L3 | DIGITAL | IOD_TPV_mem | D2791
TP_op_alarm_Analizator19tok_L3 | DIGITAL | IOD_TPV_mem | D2792
TP_op_alarm_Analizator20tok_L3 | DIGITAL | IOD_TPV_mem | D2793
TP_op_alarm_Analizator21tok_L3 | DIGITAL | IOD_TPV_mem | D2794
TP_op_alarm_Analizator22tok_L3 | DIGITAL | IOD_TPV_mem | D2795
TP_op_alarm_Analizator23tok_L3 | DIGITAL | IOD_TPV_mem | D2796
TP_op_alarm_Analizator24tok_L3 | DIGITAL | IOD_TPV_mem | D2797
TP_op_alarm_Analizator25tok_L3 | DIGITAL | IOD_TPV_mem | D2798
TP_op_om_alarm_Analizator_tok_L3 | DIGITAL | IOD_TPV_disk | D2800[30]
TP_op_pri_alarm_Analizator_tok_L3 | LONG | IOD_TPV_disk | L2840[30]
TP_al_alarm_Analizator1tok_L1 | DIGITAL | IOD_TPV_mem | D2880
TP_al_alarm_Analizator2tok_L1 | DIGITAL | IOD_TPV_mem | D2881
TP_al_alarm_Analizator3tok_L1 | DIGITAL | IOD_TPV_mem | D2882
TP_al_alarm_Analizator4tok_L1 | DIGITAL | IOD_TPV_mem | D2883
TP_al_alarm_Analizator5tok_L1 | DIGITAL | IOD_TPV_mem | D2884
TP_al_alarm_Analizator6tok_L1 | DIGITAL | IOD_TPV_mem | D2885
TP_al_alarm_Analizator7tok_L1 | DIGITAL | IOD_TPV_mem | D2886
TP_al_alarm_Analizator8tok_L1 | DIGITAL | IOD_TPV_mem | D2887
TP_al_alarm_Analizator9tok_L1 | DIGITAL | IOD_TPV_mem | D2888
TP_al_alarm_Analizator10tok_L1 | DIGITAL | IOD_TPV_mem | D2889
TP_al_alarm_Analizator11tok_L1 | DIGITAL | IOD_TPV_mem | D2890
TP_al_alarm_Analizator12tok_L1 | DIGITAL | IOD_TPV_mem | D2891
TP_al_alarm_Analizator13tok_L1 | DIGITAL | IOD_TPV_mem | D2892
TP_al_alarm_Analizator14tok_L1 | DIGITAL | IOD_TPV_mem | D2893
TP_al_alarm_Analizator15tok_L1 | DIGITAL | IOD_TPV_mem | D2894
TP_al_alarm_Analizator16tok_L1 | DIGITAL | IOD_TPV_mem | D2895
TP_al_alarm_Analizator17tok_L1 | DIGITAL | IOD_TPV_mem | D2896
TP_al_alarm_Analizator18tok_L1 | DIGITAL | IOD_TPV_mem | D2897
TP_al_alarm_Analizator19tok_L1 | DIGITAL | IOD_TPV_mem | D2898
TP_al_alarm_Analizator20tok_L1 | DIGITAL | IOD_TPV_mem | D2899
TP_al_alarm_Analizator21tok_L1 | DIGITAL | IOD_TPV_mem | D2900
TP_al_alarm_Analizator22tok_L1 | DIGITAL | IOD_TPV_mem | D2901
TP_al_alarm_Analizator23tok_L1 | DIGITAL | IOD_TPV_mem | D2902
TP_al_alarm_Analizator24tok_L1 | DIGITAL | IOD_TPV_mem | D2903
TP_al_alarm_Analizator25tok_L1 | DIGITAL | IOD_TPV_mem | D2904
TP_al_om_alarm_Analizator_tok_L1 | DIGITAL | IOD_TPV_disk | D2934[30]
TP_al_pri_alarm_Analizator_tok_L1 | LONG | IOD_TPV_disk | L2950[30]
TP_al_alarm_Analizator1tok_L2 | DIGITAL | IOD_TPV_mem | D2980
TP_al_alarm_Analizator2tok_L2 | DIGITAL | IOD_TPV_mem | D2981
TP_al_alarm_Analizator3tok_L2 | DIGITAL | IOD_TPV_mem | D2982
TP_al_alarm_Analizator4tok_L2 | DIGITAL | IOD_TPV_mem | D2983
TP_al_alarm_Analizator5tok_L2 | DIGITAL | IOD_TPV_mem | D2984
TP_al_alarm_Analizator6tok_L2 | DIGITAL | IOD_TPV_mem | D2985
TP_al_alarm_Analizator7tok_L2 | DIGITAL | IOD_TPV_mem | D2986
TP_al_alarm_Analizator8tok_L2 | DIGITAL | IOD_TPV_mem | D2987
TP_al_alarm_Analizator9tok_L2 | DIGITAL | IOD_TPV_mem | D2988
TP_al_alarm_Analizator10tok_L2 | DIGITAL | IOD_TPV_mem | D2989
TP_al_alarm_Analizator11tok_L2 | DIGITAL | IOD_TPV_mem | D2990
TP_al_alarm_Analizator12tok_L2 | DIGITAL | IOD_TPV_mem | D2991
TP_al_alarm_Analizator13tok_L2 | DIGITAL | IOD_TPV_mem | D2992
TP_al_alarm_Analizator14tok_L2 | DIGITAL | IOD_TPV_mem | D2993
TP_al_alarm_Analizator15tok_L2 | DIGITAL | IOD_TPV_mem | D2994
TP_al_alarm_Analizator16tok_L2 | DIGITAL | IOD_TPV_mem | D2995
TP_al_alarm_Analizator17tok_L2 | DIGITAL | IOD_TPV_mem | D2996
TP_al_alarm_Analizator18tok_L2 | DIGITAL | IOD_TPV_mem | D2997
TP_al_alarm_Analizator19tok_L2 | DIGITAL | IOD_TPV_mem | D2998
TP_al_alarm_Analizator20tok_L2 | DIGITAL | IOD_TPV_mem | D2999
TP_al_alarm_Analizator21tok_L2 | DIGITAL | IOD_TPV_mem | D3000
TP_al_alarm_Analizator22tok_L2 | DIGITAL | IOD_TPV_mem | D3001
TP_al_alarm_Analizator23tok_L2 | DIGITAL | IOD_TPV_mem | D3002
TP_al_alarm_Analizator24tok_L2 | DIGITAL | IOD_TPV_mem | D3003
TP_al_alarm_Analizator25tok_L2 | DIGITAL | IOD_TPV_mem | D3004
TP_al_om_alarm_Analizator_tok_L2 | DIGITAL | IOD_TPV_disk | D3006[30]
TP_al_pri_alarm_Analizator_tok_L2 | LONG | IOD_TPV_disk | L3040[30]
TP_al_alarm_Analizator1tok_L3 | DIGITAL | IOD_TPV_mem | D3080
TP_al_alarm_Analizator2tok_L3 | DIGITAL | IOD_TPV_mem | D3081
TP_al_alarm_Analizator3tok_L3 | DIGITAL | IOD_TPV_mem | D3082
TP_al_alarm_Analizator4tok_L3 | DIGITAL | IOD_TPV_mem | D3083
TP_al_alarm_Analizator5tok_L3 | DIGITAL | IOD_TPV_mem | D3084
TP_al_alarm_Analizator6tok_L3 | DIGITAL | IOD_TPV_mem | D3085
TP_al_alarm_Analizator7tok_L3 | DIGITAL | IOD_TPV_mem | D3086
TP_al_alarm_Analizator8tok_L3 | DIGITAL | IOD_TPV_mem | D3087
TP_al_alarm_Analizator9tok_L3 | DIGITAL | IOD_TPV_mem | D3088
TP_al_alarm_Analizator10tok_L3 | DIGITAL | IOD_TPV_mem | D3089
TP_al_alarm_Analizator11tok_L3 | DIGITAL | IOD_TPV_mem | D3090
TP_al_alarm_Analizator12tok_L3 | DIGITAL | IOD_TPV_mem | D3091
TP_al_alarm_Analizator13tok_L3 | DIGITAL | IOD_TPV_mem | D3092
TP_al_alarm_Analizator14tok_L3 | DIGITAL | IOD_TPV_mem | D3093
TP_al_alarm_Analizator15tok_L3 | DIGITAL | IOD_TPV_mem | D3094
TP_al_alarm_Analizator16tok_L3 | DIGITAL | IOD_TPV_mem | D3095
TP_al_alarm_Analizator17tok_L3 | DIGITAL | IOD_TPV_mem | D3096
TP_al_alarm_Analizator18tok_L3 | DIGITAL | IOD_TPV_mem | D3097
TP_al_alarm_Analizator19tok_L3 | DIGITAL | IOD_TPV_mem | D3098
TP_al_alarm_Analizator20tok_L3 | DIGITAL | IOD_TPV_mem | D3099
TP_al_alarm_Analizator21tok_L3 | DIGITAL | IOD_TPV_mem | D3100
TP_al_alarm_Analizator22tok_L3 | DIGITAL | IOD_TPV_mem | D3101
TP_al_alarm_Analizator23tok_L3 | DIGITAL | IOD_TPV_mem | D3102
TP_al_alarm_Analizator24tok_L3 | DIGITAL | IOD_TPV_mem | D3103
TP_al_alarm_Analizator25tok_L3 | DIGITAL | IOD_TPV_mem | D3104
TP_al_om_alarm_Analizator_tok_L3 | DIGITAL | IOD_TPV_disk | D3140[30]
TP_al_pri_alarm_Analizator_tok_L3 | LONG | IOD_TPV_disk | L3170[30]
TP_Gen_rdeca_spmeja_tlak_oljaA1 | INT | IOD_TPV_disk | I3210
TP_Gen_rumena_spmeja_tlak_oljaA1 | INT | IOD_TPV_disk | I3212
TP_Gen_rdeca_zgmeja_tlak_oljaA1 | INT | IOD_TPV_disk | I3214
TP_Gen_rumena_zgmeja_tlak_oljaA1 | INT | IOD_TPV_disk | I3216
TP_Gen_rdeca_spmeja_hitrostA1 | INT | IOD_TPV_disk | I3218
TP_Gen_rumena_spmeja_hitrostA1 | INT | IOD_TPV_disk | I3220
TP_Gen_rdeca_zgmeja_hitrostA1 | INT | IOD_TPV_disk | I3222
TP_Gen_rumena_zgmeja_hitrostA1 | INT | IOD_TPV_disk | I3224
TP_Gen_rdeca_spmeja_alter_napA1 | INT | IOD_TPV_disk | I3226
TP_Gen_rumena_spmeja_alter_napA1 | INT | IOD_TPV_disk | I3228
TP_Gen_rdeca_spmeja_tempA1 | INT | IOD_TPV_disk | I3230
TP_Gen_rumena_spmeja_tempA1 | INT | IOD_TPV_disk | I3232
TP_Gen_rdeca_spmeja_bat_napA1 | INT | IOD_TPV_disk | I3234
TP_Gen_rumena_spmeja_bat_napA1 | INT | IOD_TPV_disk | I3236
TP_Gen_A1_omog_upozorila | DIGITAL | IOD_TPV_disk | D3238[30]
TP_Gen_A1_omog_alarm | DIGITAL | IOD_TPV_disk | D3268[30]
TP_Gen_A1_op_alarm_tlak_sp | DIGITAL | IOD_TPV_mem | D3300
TP_Gen_A1_al_alarm_tlak_sp | DIGITAL | IOD_TPV_mem | D3301
TP_Gen_A1_op_alarm_tlak_zg | DIGITAL | IOD_TPV_mem | D3302
TP_Gen_A1_al_alarm_tlak_zg | DIGITAL | IOD_TPV_mem | D3303
TP_Gen_A1_op_alarm_hitrost_sp | DIGITAL | IOD_TPV_mem | D3304
TP_Gen_A1_al_alarm_hitrost_sp | DIGITAL | IOD_TPV_mem | D3305
TP_Gen_A1_op_alarm_hitrost_zg | DIGITAL | IOD_TPV_mem | D3306
TP_Gen_A1_al_alarm_hitrost_zg | DIGITAL | IOD_TPV_mem | D3307
TP_Gen_A1_op_alarm_alter_nap | DIGITAL | IOD_TPV_mem | D3308
TP_Gen_A1_al_alarm_alter_nap | DIGITAL | IOD_TPV_mem | D3309
TP_Gen_A1_op_alarm_temp | DIGITAL | IOD_TPV_mem | D3310
TP_Gen_A1_al_alarm_temp | DIGITAL | IOD_TPV_mem | D3311
TP_Gen_A1_op_alarm_bat_nap | DIGITAL | IOD_TPV_mem | D3312
TP_Gen_A1_al_alarm_bat_nap | DIGITAL | IOD_TPV_mem | D3313
TP_Gen_rdeca_spmeja_tlak_oljaA2 | INT | IOD_TPV_disk | I3316
TP_Gen_rumena_spmeja_tlak_oljaA2 | INT | IOD_TPV_disk | I3318
TP_Gen_rdeca_zgmeja_tlak_oljaA2 | INT | IOD_TPV_disk | I3320
TP_Gen_rumena_zgmeja_tlak_oljaA2 | INT | IOD_TPV_disk | I3322
TP_Gen_rdeca_spmeja_hitrostA2 | INT | IOD_TPV_disk | I3324
TP_Gen_rumena_spmeja_hitrostA2 | INT | IOD_TPV_disk | I3326
TP_Gen_rdeca_zgmeja_hitrostA2 | INT | IOD_TPV_disk | I3328
TP_Gen_rumena_zgmeja_hitrostA2 | INT | IOD_TPV_disk | I3330
TP_Gen_rdeca_spmeja_alter_napA2 | INT | IOD_TPV_disk | I3332
TP_Gen_rumena_spmeja_alter_napA2 | INT | IOD_TPV_disk | I3334
TP_Gen_rdeca_spmeja_tempA2 | INT | IOD_TPV_disk | I3336
TP_Gen_rumena_spmeja_tempA2 | INT | IOD_TPV_disk | I3338
TP_Gen_rdeca_spmeja_bat_napA2 | INT | IOD_TPV_disk | I3340
TP_Gen_rumena_spmeja_bat_napA2 | INT | IOD_TPV_disk | I3342
TP_Gen_A2_omog_upozorila | DIGITAL | IOD_TPV_disk | D3376[30]
TP_Gen_A2_omog_alarm | DIGITAL | IOD_TPV_disk | D3410[30]
TP_Gen_A2_op_alarm_tlak_sp | DIGITAL | IOD_TPV_mem | D3440
TP_Gen_A2_al_alarm_tlak_sp | DIGITAL | IOD_TPV_mem | D3441
TP_Gen_A2_op_alarm_tlak_zg | DIGITAL | IOD_TPV_mem | D3442
TP_Gen_A2_al_alarm_tlak_zg | DIGITAL | IOD_TPV_mem | D3443
TP_Gen_A2_op_alarm_hitrost_sp | DIGITAL | IOD_TPV_mem | D3444
TP_Gen_A2_al_alarm_hitrost_sp | DIGITAL | IOD_TPV_mem | D3445
TP_Gen_A2_op_alarm_hitrost_zg | DIGITAL | IOD_TPV_mem | D3446
TP_Gen_A2_al_alarm_hitrost_zg | DIGITAL | IOD_TPV_mem | D3447
TP_Gen_A2_op_alarm_alter_nap | DIGITAL | IOD_TPV_mem | D3448
TP_Gen_A2_al_alarm_alter_nap | DIGITAL | IOD_TPV_mem | D3449
TP_Gen_A2_op_alarm_temp | DIGITAL | IOD_TPV_mem | D3450
TP_Gen_A2_al_alarm_temp | DIGITAL | IOD_TPV_mem | D3451
TP_Gen_A2_op_alarm_bat_nap | DIGITAL | IOD_TPV_mem | D3452
TP_Gen_A2_al_alarm_bat_nap | DIGITAL | IOD_TPV_mem | D3453
TP_Gen_splosna_napaka_DA1 | DIGITAL | IOD_TPV_mem | D3454
TP_Gen_splosna_napaka_DA2 | DIGITAL | IOD_TPV_mem | D3455
TP_Stikala_rocni_izklop_omog_alarm | DIGITAL | IOD_TPV_disk | D3460[30]
TP_Stikala_rocni_izklop_alarm | DIGITAL | IOD_TPV_disk | D3490[30]
TP_Stikala_zasc_izklop_omog_alarm | DIGITAL | IOD_TPV_disk | D3520[30]
TP_Stikala_zasc_izklop_alarm | DIGITAL | IOD_TPV_disk | D3550[30]
TP_omog_komuk_alarmov | DIGITAL | IOD_TPV_disk | D3580[30]
TP_DA3_omog_alarma | DIGITAL | IOD_TPV_disk | D2587[7]
TP_DA3_alarm | DIGITAL | IOD_TPV_mem | D2594[7]
ATP_PoljeSmsAlarmi | DIGITAL | IOD_TPV_disk | D3600[300]
BTP_PoljeSmsAlarmi | DIGITAL | IOD_TPV_disk | D3900[300]
CTP_PoljeSmsAlarmi | DIGITAL | IOD_TPV_disk | D4200[300]
DTP_PoljeSmsAlarmi | DIGITAL | IOD_TPV_disk | D4500[300]
ETP_PoljeSmsAlarmi | DIGITAL | IOD_TPV_disk | D4800[300]
FTP_PoljeSmsAlarmi | DIGITAL | IOD_TPV_disk | D5100[300]
TP_delovna_energija | LONG | IOD_TPV_disk | L5400[50]
TP_jalova_energija | LONG | IOD_TPV_disk | L5450[50]
TP_Cas_dan | LONG | IOD_TPV_disk | L5500[50]
TP_Cas_teden | LONG | IOD_TPV_disk | L5550[50]
TP_st_delovna | LONG | IOD_TPV_disk | L5602
TP_st_jalova | LONG | IOD_TPV_disk | L5604
IzpadTPV | INT | IOD_TPV_TCP | 40017
TPVsinh_cas | STRING | IOD_TPV_TCP | 45001[15]
TPVsinh_cas_nastavi | DIGITAL | IOD_TPV_TCP | 00196
TPVMax_dan_energija | REAL | IOD_TPV_disk | R5610[30] | [5 empty] | ##########
TPVMax_mes_energija | REAL | IOD_TPV_disk | R5640[30] | [5 empty] | ##########
TPVMax_let_energija | REAL | IOD_TPV_disk | R5670[30] | [5 empty] | ##########
TPV_vklop_agregata_DA1 | DIGITAL | IOD_TPV_disk | D5700
TPV_vklop_agregata_DA2 | DIGITAL | IOD_TPV_disk | D5701
TPV_prisotnost_DA1_napetosti | DIGITAL | IOD_TPV_disk | D5702
TPV_prisotnost_DA2_napetosti | DIGITAL | IOD_TPV_disk | D5703
TPV_prisotnost_DA3_napetosti | DIGITAL | IOD_TPV_disk | D5704
TPV_prisotnost_m_nap_rgm1 | DIGITAL | IOD_TPV_disk | D5705
TPV_prisotnost_m_nap_rgm2 | DIGITAL | IOD_TPV_disk | D5706
TPV_prisotnost_m_nap_rgm3 | DIGITAL | IOD_TPV_disk | D5707
TPV_izbira_mali_prikaz_circ | INT | IOD_TPV_disk | I5710
TPV_utrip_simbola_ob_alrmu | DIGITAL | IOD_TPV_disk | D5712
TPV_report_vpis | DIGITAL | IOD_TPV_mem | D5713
TPV_vklop_da1 | DIGITAL | IOD_TPV_disk | D5714
TPV_vklop_da2 | DIGITAL | IOD_TPV_disk | D5715
TPV_rez_av_da1da2 | DIGITAL | IOD_TPV_disk | D5716
TPV_vzp_vedno_da1da2 | DIGITAL | IOD_TPV_disk | D5717
TPV_vzp_nikoli_da1da2 | DIGITAL | IOD_TPV_disk | D5718
TPV_vzp_popot_da1da2 | DIGITAL | IOD_TPV_disk | D5719
TPV_rez_ro_da1da2 | DIGITAL | IOD_TPV_disk | D5720
TPV_scroll_report | INT | IOD_TPV_disk | I5722 |  |  | 0 | 100 | %
TPVMI4_not_mrez_nap_RGM_A1 | DIGITAL | IOD_TPV_disk | D5724
TPVMI4_not_mrez_nap_RGM_A2 | DIGITAL | IOD_TPV_disk | D5725
TPVMI4K2_not_mrez_nap_RGM_A3 | DIGITAL | IOD_TPV_disk | D5726
TPV_report_napetost_vpis | DIGITAL | IOD_TPV_mem | D5727
TPV_pom_nap_m_DA1 | DIGITAL | IOD_TPV_disk | D5728
TPV_pom_nap_m_DA2 | DIGITAL | IOD_TPV_disk | D5729
TPV_pom_nap_m_DA3 | DIGITAL | IOD_TPV_disk | D5730
TPV_pom_nap_DA1 | DIGITAL | IOD_TPV_disk | D5731
TPV_pom_nap_DA2 | DIGITAL | IOD_TPV_disk | D5732
TPV_pom_nap_DA3 | DIGITAL | IOD_TPV_disk | D5733
TPV_pom_DA1_deluje | DIGITAL | IOD_TPV_disk | D5734
TPV_pom_DA2_deluje | DIGITAL | IOD_TPV_disk | D5735
TPV_vzp_rez_av_DA3 | DIGITAL | IOD_TPV_disk | D5736
TPV_vzp_rez_ro_DA3 | DIGITAL | IOD_TPV_disk | D5737
TPV_po_zagonu_je_1 | DIGITAL | IOD_TPV_disk | D5738
TPV_stanje_vzp_nikoli_da1da2 | DIGITAL | IOD_TPV_disk | D5739
TPV_stanje_vzp_popot_da1da2 | DIGITAL | IOD_TPV_disk | D5740
TPV_stanje_vzp_vedno_da1da2 | DIGITAL | IOD_TPV_disk | D5741
TPV_stanje_av_ro_da1da2 | DIGITAL | IOD_TPV_disk | D5742
TPV_stanje_av_ro_da3 | DIGITAL | IOD_TPV_disk | D5743
TPVdelovna_energ_disk | INT | IOD_TPV_disk | I5746
TPVjal_energ_skupna_max | INT | IOD_TPV_disk | I5748
TPVdel_energ_skupna_max | INT | IOD_TPV_disk | I5750
TPVjalova_energ_disk | INT | IOD_TPV_disk | I5752
TPVenergija_prvi_vpis | INT | IOD_TPV_mem | I5754
TPV_zacni_preverit_alarme | DIGITAL | IOD_TPV_mem | D5756
TP_ralika_energ_dan | REAL | IOD_TPV_disk | R5800[30]
TP_ralika_energ_ted | REAL | IOD_TPV_disk | R5830[30]
TP_ralika_energ_mes | REAL | IOD_TPV_disk | R5860[30]
TPVMI4napaka_alarm_DA1_omog | DIGITAL | IOD_TPV_disk | D6890
TPVMI4napaka_alarm_DA2_omog | DIGITAL | IOD_TPV_disk | D6891
TPV_Dnevna_energija | REAL | IOD_TPV_disk | R6900[30]
TPV_Tedensa_energija | REAL | IOD_TPV_disk | R6930[30]
TPV_Mesecna_energija | REAL | IOD_TPV_disk | R6960[30]
TPVCirc14NicelniTok_NovoSkaliranje | LONG | IOD_TPV_TCP | 44909 | 0 | 8000 | 0 | 800 | A | ###.#
TPVCirc14Tok_L1_NovoSkaliranje | LONG | IOD_TPV_TCP | 44911 | 0 | 8000 | 0 | 800 | A | ###.#
TPVCirc14Tok_L2_NovoSkaliranje | LONG | IOD_TPV_TCP | 44913 | 0 | 8000 | 0 | 800 | A | ###.#
TPVCirc14Tok_L3_NovoSkaliranje | LONG | IOD_TPV_TCP | 44915 | 0 | 8000 | 0 | 800 | A | ###.#
TPVCirc8NicelniTok_NovoSkaliranje | LONG | IOD_TPV_TCP | 44917 | 0 | 8000 | 0 | 800 | A | ###.#
TPVCirc8Tok_L1_NovoSkaliranje | LONG | IOD_TPV_TCP | 44919 | 0 | 8000 | 0 | 800 | A | ###.#
TPVCirc8Tok_L2_NovoSkaliranje | LONG | IOD_TPV_TCP | 44921 | 0 | 8000 | 0 | 800 | A | ###.#
TPVCirc8Tok_L3_NovoSkaliranje | LONG | IOD_TPV_TCP | 44923 | 0 | 8000 | 0 | 800 | A | ###.#
TPVCirc9NicelniTok_NovoSkaliranje | LONG | IOD_TPV_TCP | 44925 | 0 | 8000 | 0 | 800 | A | ###.#
TPVCirc9Tok_L1_NovoSkaliranje | LONG | IOD_TPV_TCP | 44927 | 0 | 8000 | 0 | 800 | A | ###.#
TPVCirc9Tok_L2_NovoSkaliranje | LONG | IOD_TPV_TCP | 44929 | 0 | 8000 | 0 | 800 | A | ###.#
TPVCirc9Tok_L3_NovoSkaliranje | LONG | IOD_TPV_TCP | 44931 | 0 | 8000 | 0 | 800 | A | ###.#
TPVCirc1MaximumDemandA2 | LONG | IOD_TPV_TCP | 44933 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc1MaximumDemandA3 | LONG | IOD_TPV_TCP | 44935 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc2MaximumDemandA2 | LONG | IOD_TPV_TCP | 44937 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc2MaximumDemandA3 | LONG | IOD_TPV_TCP | 44939 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc3MaximumDemandA2 | LONG | IOD_TPV_TCP | 44941 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc3MaximumDemandA3 | LONG | IOD_TPV_TCP | 44943 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc4MaximumDemandA2 | LONG | IOD_TPV_TCP | 44945 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc4MaximumDemandA3 | LONG | IOD_TPV_TCP | 44947 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc5MaximumDemandA2 | LONG | IOD_TPV_TCP | 44949 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc5MaximumDemandA3 | LONG | IOD_TPV_TCP | 44951 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc6MaximumDemandA2 | LONG | IOD_TPV_TCP | 44953 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc6MaximumDemandA3 | LONG | IOD_TPV_TCP | 44955 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc7MaximumDemandA2 | LONG | IOD_TPV_TCP | 44957 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc7MaximumDemandA3 | LONG | IOD_TPV_TCP | 44959 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc8MaximumDemandA2 | LONG | IOD_TPV_TCP | 44961 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc8MaximumDemandA3 | LONG | IOD_TPV_TCP | 44963 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc9MaximumDemandA2 | LONG | IOD_TPV_TCP | 44965 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc9MaximumDemandA3 | LONG | IOD_TPV_TCP | 44967 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc10MaximumDemandA2 | LONG | IOD_TPV_TCP | 44969 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc10MaximumDemandA3 | LONG | IOD_TPV_TCP | 44971 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc11MaximumDemandA2 | LONG | IOD_TPV_TCP | 44973 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc11MaximumDemandA3 | LONG | IOD_TPV_TCP | 44975 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc12MaximumDemandA2 | LONG | IOD_TPV_TCP | 44977 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc12MaximumDemandA3 | LONG | IOD_TPV_TCP | 44979 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc13MaximumDemandA2 | LONG | IOD_TPV_TCP | 44981 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc13MaximumDemandA3 | LONG | IOD_TPV_TCP | 44983 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc14MaximumDemandA2 | LONG | IOD_TPV_TCP | 44985 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc14MaximumDemandA3 | LONG | IOD_TPV_TCP | 44987 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc15MaximumDemandA2 | LONG | IOD_TPV_TCP | 44989 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc15MaximumDemandA3 | LONG | IOD_TPV_TCP | 44991 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc16MaximumDemandA2 | LONG | IOD_TPV_TCP | 44993 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc16MaximumDemandA3 | LONG | IOD_TPV_TCP | 44995 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc17MaximumDemandA2 | LONG | IOD_TPV_TCP | 44997 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc17MaximumDemandA3 | LONG | IOD_TPV_TCP | 44999 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc18MaximumDemandA2 | LONG | IOD_TPV_TCP | 45001 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc18MaximumDemandA3 | LONG | IOD_TPV_TCP | 45003 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc19MaximumDemandA2 | LONG | IOD_TPV_TCP | 45005 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc19MaximumDemandA3 | LONG | IOD_TPV_TCP | 45007 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc20MaximumDemandA2 | LONG | IOD_TPV_TCP | 45009 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc20MaximumDemandA3 | LONG | IOD_TPV_TCP | 45011 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc21MaximumDemandA2 | LONG | IOD_TPV_TCP | 45013 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc21MaximumDemandA3 | LONG | IOD_TPV_TCP | 45015 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc22MaximumDemandA2 | LONG | IOD_TPV_TCP | 45017 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc22MaximumDemandA3 | LONG | IOD_TPV_TCP | 45019 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc23MaximumDemandA2 | LONG | IOD_TPV_TCP | 45021 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc23MaximumDemandA3 | LONG | IOD_TPV_TCP | 45023 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc24MaximumDemandA2 | LONG | IOD_TPV_TCP | 45025 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc24MaximumDemandA3 | LONG | IOD_TPV_TCP | 45027 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc25MaximumDemandA2 | LONG | IOD_TPV_TCP | 45029 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc25MaximumDemandA3 | LONG | IOD_TPV_TCP | 45031 | 0 | 12000 | 0 | 1200 | A | ###.#
TPVCirc1RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45033
TPVCirc1RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45035
TPVCirc1RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45037
TPVCirc2RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45039
TPVCirc2RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45041
TPVCirc2RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45043
TPVCirc3RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45045
TPVCirc3RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45047
TPVCirc3RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45049
TPVCirc4RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45051
TPVCirc4RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45053
TPVCirc4RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45055
TPVCirc5RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45057
TPVCirc5RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45059
TPVCirc5RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45061
TPVCirc6RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45063
TPVCirc6RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45065
TPVCirc6RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45067
TPVCirc7RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45069
TPVCirc7RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45071
TPVCirc7RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45073
TPVCirc8RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45075
TPVCirc8RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45077
TPVCirc8RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45079
TPVCirc9RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45081
TPVCirc9RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45083
TPVCirc9RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45085
TPVCirc10RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45087
TPVCirc10RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45089
TPVCirc10RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45091
TPVCirc11RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45093
TPVCirc11RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45095
TPVCirc11RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45097
TPVCirc12RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45099
TPVCirc12RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45101
TPVCirc12RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45103
TPVCirc13RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45105
TPVCirc13RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45107
TPVCirc13RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45109
TPVCirc14RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45111
TPVCirc14RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45113
TPVCirc14RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45115
TPVCirc15RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45117
TPVCirc15RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45119
TPVCirc15RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45121
TPVCirc16RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45123
TPVCirc16RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45125
TPVCirc16RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45127
TPVCirc17RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45129
TPVCirc17RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45131
TPVCirc17RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45133
TPVCirc18RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45135
TPVCirc18RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45137
TPVCirc18RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45139
TPVCirc19RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45141
TPVCirc19RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45143
TPVCirc19RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45145
TPVCirc20RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45147
TPVCirc20RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45149
TPVCirc20RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45151
TPVCirc21RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45153
TPVCirc21RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45155
TPVCirc21RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45157
TPVCirc22RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45159
TPVCirc22RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45161
TPVCirc22RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45163
TPVCirc23RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45165
TPVCirc23RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45167
TPVCirc23RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45169
TPVCirc24RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45171
TPVCirc24RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45173
TPVCirc24RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45175
TPVCirc25RazEner_D_SCADA | LONG | IOD_TPV_TCP | 45177
TPVCirc25RazEner_T_SCADA | LONG | IOD_TPV_TCP | 45179
TPVCirc25RazEner_M_SCADA | LONG | IOD_TPV_TCP | 45181
TPVCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_TPV_TCP | 00197
TPVCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_TPV_TCP | 00198
TPVCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_TPV_TCP | 00199
TPVCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_TPV_TCP | 00200
TPVCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_TPV_TCP | 00201
TPVCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_TPV_TCP | 00202
TPVCirc_Vpis_Dnevne_energija_scada1_mem | DIGITAL | IOD_TPV_disk | D9000
TPVCirc_Vpis_Dnevne_energija_scada2_mem | DIGITAL | IOD_TPV_disk | D9001
TPVCirc_Vpis_Tedenska_energija_scada1_mem | DIGITAL | IOD_TPV_disk | D9002
TPVCirc_Vpis_Tedenska_energija_scada2_mem | DIGITAL | IOD_TPV_disk | D9003
TPVCirc_Vpis_Mesecna_energija_scada1_mem | DIGITAL | IOD_TPV_disk | D9004
TPVCirc_Vpis_Mesecna_energija_scada2_mem | DIGITAL | IOD_TPV_disk | D9005

## XSoft
mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Write_BOOL(FC) | mod_Write_Word(FC) | mod_Write_Word(FC) | mod_Write_dWord(FC) | mod_Write_dWord(FC) | mod_Write_String(FC)
(*Branje BOOL*) | (*Branje INT*) | (*Branje UINT*) | (*Branje LONG*) | (*Branje REAL*) | (*Branje STRING*) | (*Pisanje BOOL*) | (*Pisanje INT*) | (*Pisanje UINT*) | (*Pisanje LONG*) | (*Pisanje REAL*) | (*Pisanje STRING*)
(**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**)
mind_bool[0]:=DA3_rocno; | mind[0]:=Coolant_temperatureA1; | mind[6000]:=Battery_voltageA1; | Read_dWord(dVar:=Circ10CosFi_III,lo:=3000,hi:=3001); |  | Read_String(sVar:=cas_scada,start:=5000); | 0:DA3_rocno:=Bit_0; | 0:Coolant_temperatureA1:=Word_01; | 6000:Battery_voltageA1:=Word_01; | 3001:Circ10CosFi_III:=Long_0; |  | 5000:cas_scada:=String_0;
mind_bool[1]:=DA3motorni_pogon_okvara; | mind[1]:=Coolant_temperatureA2; | mind[6001]:=Battery_voltageA2; | Read_dWord(dVar:=Circ10DelovnaEnergija,lo:=3002,hi:=3003); |  |  | 1:DA3motorni_pogon_okvara:=Bit_0; | 1:Coolant_temperatureA2:=Word_01; | 6001:Battery_voltageA2:=Word_01; | 3003:Circ10DelovnaEnergija:=Long_0;
mind_bool[2]:=Izpad_CAN_med_K1_K2; | mind[2]:=delovna_energ_trenutno; | mind[6002]:=Charge_alternator_voltageA1; | Read_dWord(dVar:=Circ10DelovnaMoc_III,lo:=3004,hi:=3005); |  |  | 2:Izpad_CAN_med_K1_K2:=Bit_0; | 2:delovna_energ_trenutno:=Word_01; | 6002:Charge_alternator_voltageA1:=Word_01; | 3005:Circ10DelovnaMoc_III:=Long_0;
mind_bool[3]:=MI4agr_nap_RGM_A1; | mind[3]:=delovna_energija_prej; | mind[6003]:=Charge_alternator_voltageA2; | Read_dWord(dVar:=Circ10DelovnaMoc_L1,lo:=3006,hi:=3007); |  |  | 3:MI4agr_nap_RGM_A1:=Bit_0; | 3:delovna_energija_prej:=Word_01; | 6003:Charge_alternator_voltageA2:=Word_01; | 3007:Circ10DelovnaMoc_L1:=Long_0;
mind_bool[4]:=MI4agr_nap_RGM_A2; | mind[4]:=Generator_current_lag_leadA1; | mind[6004]:=Engine_speedA1; | Read_dWord(dVar:=Circ10DelovnaMoc_L2,lo:=3008,hi:=3009); |  |  | 4:MI4agr_nap_RGM_A2:=Bit_0; | 4:Generator_current_lag_leadA1:=Word_01; | 6004:Engine_speedA1:=Word_01; | 3009:Circ10DelovnaMoc_L2:=Long_0;
mind_bool[5]:=MI4DA1_2Q1_izklop; | mind[5]:=Generator_current_lag_leadA2; | mind[6005]:=Engine_speedA2; | Read_dWord(dVar:=Circ10DelovnaMoc_L3,lo:=3010,hi:=3011); |  |  | 5:MI4DA1_2Q1_izklop:=Bit_0; | 5:Generator_current_lag_leadA2:=Word_01; | 6005:Engine_speedA2:=Word_01; | 3011:Circ10DelovnaMoc_L3:=Long_0;
mind_bool[6]:=MI4DA1_2Q1_vklop; | mind[6]:=jalova_energ_trenutno; | mind[6006]:=Generator_frequencyA1; | Read_dWord(dVar:=Circ10Frekvenca_L1,lo:=3012,hi:=3013); |  |  | 6:MI4DA1_2Q1_vklop:=Bit_0; | 6:jalova_energ_trenutno:=Word_01; | 6006:Generator_frequencyA1:=Word_01; | 3013:Circ10Frekvenca_L1:=Long_0;
mind_bool[7]:=MI4DA1_del; | mind[7]:=jalova_energija_prej; | mind[6007]:=Generator_frequencyA2; | Read_dWord(dVar:=Circ10InduktivnaEnergija,lo:=3014,hi:=3015); |  |  | 7:MI4DA1_del:=Bit_0; | 7:jalova_energija_prej:=Word_01; | 6007:Generator_frequencyA2:=Word_01; | 3015:Circ10InduktivnaEnergija:=Long_0;
mind_bool[8]:=MI4DA1_prip; | mind[8]:=Komanda; | mind[6008]:=Generator_phase_rotationA1; | Read_dWord(dVar:=Circ10InduktivnaMoc_III,lo:=3016,hi:=3017); |  |  | 8:MI4DA1_prip:=Bit_0; | 8:Komanda:=Word_01; | 6008:Generator_phase_rotationA1:=Word_01; | 3017:Circ10InduktivnaMoc_III:=Long_0;
mind_bool[9]:=MI4DA1_rezerva; | mind[9]:=NastaviDanMI; | mind[6009]:=Generator_phase_rotationA2; | Read_dWord(dVar:=Circ10JalovaMoc_L1,lo:=3018,hi:=3019); |  |  | 9:MI4DA1_rezerva:=Bit_0; | 9:NastaviDanMI:=Word_01; | 6009:Generator_phase_rotationA2:=Word_01; | 3019:Circ10JalovaMoc_L1:=Long_0;
mind_bool[10]:=MI4DA1_sinh; | mind[10]:=NastaviLetoMI; | mind[6010]:=Oil_pressureA1; | Read_dWord(dVar:=Circ10JalovaMoc_L2,lo:=3020,hi:=3021); |  |  | 10:MI4DA1_sinh:=Bit_0; | 10:NastaviLetoMI:=Word_01; | 6010:Oil_pressureA1:=Word_01; | 3021:Circ10JalovaMoc_L2:=Long_0;
mind_bool[11]:=MI4DA1_zagon; | mind[11]:=NastaviMesecMI; | mind[6011]:=Oil_pressureA2; | Read_dWord(dVar:=Circ10JalovaMoc_L3,lo:=3022,hi:=3023); |  |  | 11:MI4DA1_zagon:=Bit_0; | 11:NastaviMesecMI:=Word_01; | 6011:Oil_pressureA2:=Word_01; | 3023:Circ10JalovaMoc_L3:=Long_0;
mind_bool[12]:=MI4DA2_2Q1_izklop; | mind[12]:=NastaviMinutaMI; |  | Read_dWord(dVar:=Circ10KapacitivnaEnergija,lo:=3024,hi:=3025); |  |  | 12:MI4DA2_2Q1_izklop:=Bit_0; | 12:NastaviMinutaMI:=Word_01; |  | 3025:Circ10KapacitivnaEnergija:=Long_0;
mind_bool[13]:=MI4DA2_2Q1_vklop; | mind[13]:=NastaviSekundaMI; |  | Read_dWord(dVar:=Circ10KapacitivnaMoc_III,lo:=3026,hi:=3027); |  |  | 13:MI4DA2_2Q1_vklop:=Bit_0; | 13:NastaviSekundaMI:=Word_01; |  | 3027:Circ10KapacitivnaMoc_III:=Long_0;
mind_bool[14]:=MI4DA2_del; | mind[14]:=NastaviUraMI; |  | Read_dWord(dVar:=Circ10MaximumDemand,lo:=3028,hi:=3029); |  |  | 14:MI4DA2_del:=Bit_0; | 14:NastaviUraMI:=Word_01; |  | 3029:Circ10MaximumDemand:=Long_0;
mind_bool[15]:=MI4DA2_prip; | mind[15]:=Status; |  | Read_dWord(dVar:=Circ10Napetost_L1_L2,lo:=3030,hi:=3031); |  |  | 15:MI4DA2_prip:=Bit_0; | 15:Status:=Word_01; |  | 3031:Circ10Napetost_L1_L2:=Long_0;
mind_bool[16]:=MI4DA2_rezerva; | mind[16]:=st_izpad_komTPV; |  | Read_dWord(dVar:=Circ10Napetost_L1_N,lo:=3032,hi:=3033); |  |  | 16:MI4DA2_rezerva:=Bit_0; | 16:st_izpad_komTPV:=Word_01; |  | 3033:Circ10Napetost_L1_N:=Long_0;
mind_bool[17]:=MI4DA2_sinh; |  |  | Read_dWord(dVar:=Circ10Napetost_L2_L3,lo:=3034,hi:=3035); |  |  | 17:MI4DA2_sinh:=Bit_0; |  |  | 3035:Circ10Napetost_L2_L3:=Long_0;
mind_bool[18]:=MI4DA2_zagon; |  |  | Read_dWord(dVar:=Circ10Napetost_L2_N,lo:=3036,hi:=3037); |  |  | 18:MI4DA2_zagon:=Bit_0; |  |  | 3037:Circ10Napetost_L2_N:=Long_0;
mind_bool[19]:=MI4del_zascA1_11Q1; |  |  | Read_dWord(dVar:=Circ10Napetost_L3_L1,lo:=3038,hi:=3039); |  |  | 19:MI4del_zascA1_11Q1:=Bit_0; |  |  | 3039:Circ10Napetost_L3_L1:=Long_0;
mind_bool[20]:=MI4del_zascA1_12Q1; |  |  | Read_dWord(dVar:=Circ10Napetost_L3_N,lo:=3040,hi:=3041); |  |  | 20:MI4del_zascA1_12Q1:=Bit_0; |  |  | 3041:Circ10Napetost_L3_N:=Long_0;
mind_bool[21]:=MI4del_zascA1_13Q1; |  |  | Read_dWord(dVar:=Circ10NavideznaMoc_III,lo:=3042,hi:=3043); |  |  | 21:MI4del_zascA1_13Q1:=Bit_0; |  |  | 3043:Circ10NavideznaMoc_III:=Long_0;
mind_bool[22]:=MI4del_zascA1_14Q1; |  |  | Read_dWord(dVar:=Circ10NicelniTok,lo:=3044,hi:=3045); |  |  | 22:MI4del_zascA1_14Q1:=Bit_0; |  |  | 3045:Circ10NicelniTok:=Long_0;
mind_bool[23]:=MI4del_zascA1_15Q1; |  |  | Read_dWord(dVar:=Circ10PowerFactor_III,lo:=3046,hi:=3047); |  |  | 23:MI4del_zascA1_15Q1:=Bit_0; |  |  | 3047:Circ10PowerFactor_III:=Long_0;
mind_bool[24]:=MI4del_zascA1_16Q1; |  |  | Read_dWord(dVar:=Circ10PowerFactor_L1,lo:=3048,hi:=3049); |  |  | 24:MI4del_zascA1_16Q1:=Bit_0; |  |  | 3049:Circ10PowerFactor_L1:=Long_0;
mind_bool[25]:=MI4del_zascA1_17Q1; |  |  | Read_dWord(dVar:=Circ10PowerFactor_L2,lo:=3050,hi:=3051); |  |  | 25:MI4del_zascA1_17Q1:=Bit_0; |  |  | 3051:Circ10PowerFactor_L2:=Long_0;
mind_bool[26]:=MI4del_zascA1_2Q1; |  |  | Read_dWord(dVar:=Circ10PowerFactor_L3,lo:=3052,hi:=3053); |  |  | 26:MI4del_zascA1_2Q1:=Bit_0; |  |  | 3053:Circ10PowerFactor_L3:=Long_0;
mind_bool[27]:=MI4del_zascA2_11Q1; |  |  | Read_dWord(dVar:=Circ10THDI_L1,lo:=3054,hi:=3055); |  |  | 27:MI4del_zascA2_11Q1:=Bit_0; |  |  | 3055:Circ10THDI_L1:=Long_0;
mind_bool[28]:=MI4del_zascA2_12Q1; |  |  | Read_dWord(dVar:=Circ10THDI_L2,lo:=3056,hi:=3057); |  |  | 28:MI4del_zascA2_12Q1:=Bit_0; |  |  | 3057:Circ10THDI_L2:=Long_0;
mind_bool[29]:=MI4del_zascA2_13Q1; |  |  | Read_dWord(dVar:=Circ10THDI_L3,lo:=3058,hi:=3059); |  |  | 29:MI4del_zascA2_13Q1:=Bit_0; |  |  | 3059:Circ10THDI_L3:=Long_0;
mind_bool[30]:=MI4del_zascA2_14Q1; |  |  | Read_dWord(dVar:=Circ10THDV_L1,lo:=3060,hi:=3061); |  |  | 30:MI4del_zascA2_14Q1:=Bit_0; |  |  | 3061:Circ10THDV_L1:=Long_0;
mind_bool[31]:=MI4K2agr_nap_RGM_A3; |  |  | Read_dWord(dVar:=Circ10THDV_L2,lo:=3062,hi:=3063); |  |  | 31:MI4K2agr_nap_RGM_A3:=Bit_0; |  |  | 3063:Circ10THDV_L2:=Long_0;
mind_bool[32]:=MI4K2DA3_2Q1_izklop; |  |  | Read_dWord(dVar:=Circ10THDV_L3,lo:=3064,hi:=3065); |  |  | 32:MI4K2DA3_2Q1_izklop:=Bit_0; |  |  | 3065:Circ10THDV_L3:=Long_0;
mind_bool[33]:=MI4K2DA3_2Q1_vklop; |  |  | Read_dWord(dVar:=Circ10Tok_L1,lo:=3066,hi:=3067); |  |  | 33:MI4K2DA3_2Q1_vklop:=Bit_0; |  |  | 3067:Circ10Tok_L1:=Long_0;
mind_bool[34]:=MI4K2del_zasc0_11Q1; |  |  | Read_dWord(dVar:=Circ10Tok_L2,lo:=3068,hi:=3069); |  |  | 34:MI4K2del_zasc0_11Q1:=Bit_0; |  |  | 3069:Circ10Tok_L2:=Long_0;
mind_bool[35]:=MI4K2del_zasc0_12Q1; |  |  | Read_dWord(dVar:=Circ10Tok_L3,lo:=3070,hi:=3071); |  |  | 35:MI4K2del_zasc0_12Q1:=Bit_0; |  |  | 3071:Circ10Tok_L3:=Long_0;
mind_bool[36]:=MI4K2del_zasc0_13Q1; |  |  | Read_dWord(dVar:=Circ10TokPovprecje_III,lo:=3072,hi:=3073); |  |  | 36:MI4K2del_zasc0_13Q1:=Bit_0; |  |  | 3073:Circ10TokPovprecje_III:=Long_0;
mind_bool[37]:=MI4K2del_zasc0_14Q1; |  |  | Read_dWord(dVar:=Circ11CosFi_III,lo:=3074,hi:=3075); |  |  | 37:MI4K2del_zasc0_14Q1:=Bit_0; |  |  | 3075:Circ11CosFi_III:=Long_0;
mind_bool[38]:=MI4K2del_zasc0_15Q1; |  |  | Read_dWord(dVar:=Circ11DelovnaEnergija,lo:=3076,hi:=3077); |  |  | 38:MI4K2del_zasc0_15Q1:=Bit_0; |  |  | 3077:Circ11DelovnaEnergija:=Long_0;
mind_bool[39]:=MI4K2del_zasc0_16Q1; |  |  | Read_dWord(dVar:=Circ11DelovnaMoc_III,lo:=3078,hi:=3079); |  |  | 39:MI4K2del_zasc0_16Q1:=Bit_0; |  |  | 3079:Circ11DelovnaMoc_III:=Long_0;
mind_bool[40]:=MI4K2del_zasc0_17Q1; |  |  | Read_dWord(dVar:=Circ11DelovnaMoc_L1,lo:=3080,hi:=3081); |  |  | 40:MI4K2del_zasc0_17Q1:=Bit_0; |  |  | 3081:Circ11DelovnaMoc_L1:=Long_0;
mind_bool[41]:=MI4K2del_zasc0_18Q1; |  |  | Read_dWord(dVar:=Circ11DelovnaMoc_L2,lo:=3082,hi:=3083); |  |  | 41:MI4K2del_zasc0_18Q1:=Bit_0; |  |  | 3083:Circ11DelovnaMoc_L2:=Long_0;
mind_bool[42]:=MI4K2del_zasc0_19Q1; |  |  | Read_dWord(dVar:=Circ11DelovnaMoc_L3,lo:=3084,hi:=3085); |  |  | 42:MI4K2del_zasc0_19Q1:=Bit_0; |  |  | 3085:Circ11DelovnaMoc_L3:=Long_0;
mind_bool[43]:=MI4K2del_zasc0_20Q1; |  |  | Read_dWord(dVar:=Circ11Frekvenca_L1,lo:=3086,hi:=3087); |  |  | 43:MI4K2del_zasc0_20Q1:=Bit_0; |  |  | 3087:Circ11Frekvenca_L1:=Long_0;
mind_bool[44]:=MI4K2del_zasc0_21Q1; |  |  | Read_dWord(dVar:=Circ11InduktivnaEnergija,lo:=3088,hi:=3089); |  |  | 44:MI4K2del_zasc0_21Q1:=Bit_0; |  |  | 3089:Circ11InduktivnaEnergija:=Long_0;
mind_bool[45]:=MI4K2del_zasc0_22Q1; |  |  | Read_dWord(dVar:=Circ11InduktivnaMoc_III,lo:=3090,hi:=3091); |  |  | 45:MI4K2del_zasc0_22Q1:=Bit_0; |  |  | 3091:Circ11InduktivnaMoc_III:=Long_0;
mind_bool[46]:=MI4K2del_zasc0_23Q1; |  |  | Read_dWord(dVar:=Circ11JalovaMoc_L1,lo:=3092,hi:=3093); |  |  | 46:MI4K2del_zasc0_23Q1:=Bit_0; |  |  | 3093:Circ11JalovaMoc_L1:=Long_0;
mind_bool[47]:=MI4K2del_zascA3_11Q1; |  |  | Read_dWord(dVar:=Circ11JalovaMoc_L2,lo:=3094,hi:=3095); |  |  | 47:MI4K2del_zascA3_11Q1:=Bit_0; |  |  | 3095:Circ11JalovaMoc_L2:=Long_0;
mind_bool[48]:=MI4K2del_zascA3_12Q1; |  |  | Read_dWord(dVar:=Circ11JalovaMoc_L3,lo:=3096,hi:=3097); |  |  | 48:MI4K2del_zascA3_12Q1:=Bit_0; |  |  | 3097:Circ11JalovaMoc_L3:=Long_0;
mind_bool[49]:=MI4K2del_zascA3_13Q1; |  |  | Read_dWord(dVar:=Circ11KapacitivnaEnergija,lo:=3098,hi:=3099); |  |  | 49:MI4K2del_zascA3_13Q1:=Bit_0; |  |  | 3099:Circ11KapacitivnaEnergija:=Long_0;
mind_bool[50]:=MI4K2del_zascA3_14Q1; |  |  | Read_dWord(dVar:=Circ11KapacitivnaMoc_III,lo:=3100,hi:=3101); |  |  | 50:MI4K2del_zascA3_14Q1:=Bit_0; |  |  | 3101:Circ11KapacitivnaMoc_III:=Long_0;
mind_bool[51]:=MI4K2del_zascA3_15Q1; |  |  | Read_dWord(dVar:=Circ11MaximumDemand,lo:=3102,hi:=3103); |  |  | 51:MI4K2del_zascA3_15Q1:=Bit_0; |  |  | 3103:Circ11MaximumDemand:=Long_0;
mind_bool[52]:=MI4K2motorA3_1Q1_prip; |  |  | Read_dWord(dVar:=Circ11Napetost_L1_L2,lo:=3104,hi:=3105); |  |  | 52:MI4K2motorA3_1Q1_prip:=Bit_0; |  |  | 3105:Circ11Napetost_L1_L2:=Long_0;
mind_bool[53]:=MI4K2motorA3_2Q1_prip; |  |  | Read_dWord(dVar:=Circ11Napetost_L1_N,lo:=3106,hi:=3107); |  |  | 53:MI4K2motorA3_2Q1_prip:=Bit_0; |  |  | 3107:Circ11Napetost_L1_N:=Long_0;
mind_bool[54]:=MI4K2mrez_nap_RGM_A3; |  |  | Read_dWord(dVar:=Circ11Napetost_L2_L3,lo:=3108,hi:=3109); |  |  | 54:MI4K2mrez_nap_RGM_A3:=Bit_0; |  |  | 3109:Circ11Napetost_L2_L3:=Long_0;
mind_bool[55]:=MI4K2mrezaA3_1Q1_izklop; |  |  | Read_dWord(dVar:=Circ11Napetost_L2_N,lo:=3110,hi:=3111); |  |  | 55:MI4K2mrezaA3_1Q1_izklop:=Bit_0; |  |  | 3111:Circ11Napetost_L2_N:=Long_0;
mind_bool[56]:=MI4K2mrezaA3_1Q1_vklop; |  |  | Read_dWord(dVar:=Circ11Napetost_L3_L1,lo:=3112,hi:=3113); |  |  | 56:MI4K2mrezaA3_1Q1_vklop:=Bit_0; |  |  | 3113:Circ11Napetost_L3_L1:=Long_0;
mind_bool[57]:=MI4K2prenap_zasc0_OK; |  |  | Read_dWord(dVar:=Circ11Napetost_L3_N,lo:=3114,hi:=3115); |  |  | 57:MI4K2prenap_zasc0_OK:=Bit_0; |  |  | 3115:Circ11Napetost_L3_N:=Long_0;
mind_bool[58]:=MI4K2prenap_zascA3_OK; |  |  | Read_dWord(dVar:=Circ11NavideznaMoc_III,lo:=3116,hi:=3117); |  |  | 58:MI4K2prenap_zascA3_OK:=Bit_0; |  |  | 3117:Circ11NavideznaMoc_III:=Long_0;
mind_bool[59]:=MI4K2rocni_izk0_11Q1; |  |  | Read_dWord(dVar:=Circ11NicelniTok,lo:=3118,hi:=3119); |  |  | 59:MI4K2rocni_izk0_11Q1:=Bit_0; |  |  | 3119:Circ11NicelniTok:=Long_0;
mind_bool[60]:=MI4K2rocni_izk0_12Q1; |  |  | Read_dWord(dVar:=Circ11PowerFactor_III,lo:=3120,hi:=3121); |  |  | 60:MI4K2rocni_izk0_12Q1:=Bit_0; |  |  | 3121:Circ11PowerFactor_III:=Long_0;
mind_bool[61]:=MI4K2rocni_izk0_13Q1; |  |  | Read_dWord(dVar:=Circ11PowerFactor_L1,lo:=3122,hi:=3123); |  |  | 61:MI4K2rocni_izk0_13Q1:=Bit_0; |  |  | 3123:Circ11PowerFactor_L1:=Long_0;
mind_bool[62]:=MI4K2rocni_izk0_14Q1; |  |  | Read_dWord(dVar:=Circ11PowerFactor_L2,lo:=3124,hi:=3125); |  |  | 62:MI4K2rocni_izk0_14Q1:=Bit_0; |  |  | 3125:Circ11PowerFactor_L2:=Long_0;
mind_bool[63]:=MI4K2rocni_izk0_15Q1; |  |  | Read_dWord(dVar:=Circ11PowerFactor_L3,lo:=3126,hi:=3127); |  |  | 63:MI4K2rocni_izk0_15Q1:=Bit_0; |  |  | 3127:Circ11PowerFactor_L3:=Long_0;
mind_bool[64]:=MI4K2rocni_izk0_16Q1; |  |  | Read_dWord(dVar:=Circ11THDI_L1,lo:=3128,hi:=3129); |  |  | 64:MI4K2rocni_izk0_16Q1:=Bit_0; |  |  | 3129:Circ11THDI_L1:=Long_0;
mind_bool[65]:=MI4K2rocni_izk0_17Q1; |  |  | Read_dWord(dVar:=Circ11THDI_L2,lo:=3130,hi:=3131); |  |  | 65:MI4K2rocni_izk0_17Q1:=Bit_0; |  |  | 3131:Circ11THDI_L2:=Long_0;
mind_bool[66]:=MI4K2rocni_izk0_18Q1; |  |  | Read_dWord(dVar:=Circ11THDI_L3,lo:=3132,hi:=3133); |  |  | 66:MI4K2rocni_izk0_18Q1:=Bit_0; |  |  | 3133:Circ11THDI_L3:=Long_0;
mind_bool[67]:=MI4K2rocni_izk0_19Q1; |  |  | Read_dWord(dVar:=Circ11THDV_L1,lo:=3134,hi:=3135); |  |  | 67:MI4K2rocni_izk0_19Q1:=Bit_0; |  |  | 3135:Circ11THDV_L1:=Long_0;
mind_bool[68]:=MI4K2rocni_izk0_20Q1; |  |  | Read_dWord(dVar:=Circ11THDV_L2,lo:=3136,hi:=3137); |  |  | 68:MI4K2rocni_izk0_20Q1:=Bit_0; |  |  | 3137:Circ11THDV_L2:=Long_0;
mind_bool[69]:=MI4K2rocni_izk0_21Q1; |  |  | Read_dWord(dVar:=Circ11THDV_L3,lo:=3138,hi:=3139); |  |  | 69:MI4K2rocni_izk0_21Q1:=Bit_0; |  |  | 3139:Circ11THDV_L3:=Long_0;
mind_bool[70]:=MI4K2rocni_izk0_22Q1; |  |  | Read_dWord(dVar:=Circ11Tok_L1,lo:=3140,hi:=3141); |  |  | 70:MI4K2rocni_izk0_22Q1:=Bit_0; |  |  | 3141:Circ11Tok_L1:=Long_0;
mind_bool[71]:=MI4K2rocni_izk0_23Q1; |  |  | Read_dWord(dVar:=Circ11Tok_L2,lo:=3142,hi:=3143); |  |  | 71:MI4K2rocni_izk0_23Q1:=Bit_0; |  |  | 3143:Circ11Tok_L2:=Long_0;
mind_bool[72]:=MI4K2rocni_izkA3_11Q1; |  |  | Read_dWord(dVar:=Circ11Tok_L3,lo:=3144,hi:=3145); |  |  | 72:MI4K2rocni_izkA3_11Q1:=Bit_0; |  |  | 3145:Circ11Tok_L3:=Long_0;
mind_bool[73]:=MI4K2rocni_izkA3_12Q1; |  |  | Read_dWord(dVar:=Circ11TokPovprecje_III,lo:=3146,hi:=3147); |  |  | 73:MI4K2rocni_izkA3_12Q1:=Bit_0; |  |  | 3147:Circ11TokPovprecje_III:=Long_0;
mind_bool[74]:=MI4K2rocni_izkA3_13Q1; |  |  | Read_dWord(dVar:=Circ12CosFi_III,lo:=3148,hi:=3149); |  |  | 74:MI4K2rocni_izkA3_13Q1:=Bit_0; |  |  | 3149:Circ12CosFi_III:=Long_0;
mind_bool[75]:=MI4K2rocni_izkA3_14Q1; |  |  | Read_dWord(dVar:=Circ12DelovnaEnergija,lo:=3150,hi:=3151); |  |  | 75:MI4K2rocni_izkA3_14Q1:=Bit_0; |  |  | 3151:Circ12DelovnaEnergija:=Long_0;
mind_bool[76]:=MI4K2rocni_izkA3_15Q1; |  |  | Read_dWord(dVar:=Circ12DelovnaMoc_III,lo:=3152,hi:=3153); |  |  | 76:MI4K2rocni_izkA3_15Q1:=Bit_0; |  |  | 3153:Circ12DelovnaMoc_III:=Long_0;
mind_bool[77]:=MI4K2stik0_11Q1_vkl; |  |  | Read_dWord(dVar:=Circ12DelovnaMoc_L1,lo:=3154,hi:=3155); |  |  | 77:MI4K2stik0_11Q1_vkl:=Bit_0; |  |  | 3155:Circ12DelovnaMoc_L1:=Long_0;
mind_bool[78]:=MI4K2stik0_12Q1_vkl; |  |  | Read_dWord(dVar:=Circ12DelovnaMoc_L2,lo:=3156,hi:=3157); |  |  | 78:MI4K2stik0_12Q1_vkl:=Bit_0; |  |  | 3157:Circ12DelovnaMoc_L2:=Long_0;
mind_bool[79]:=MI4K2stik0_13Q1_vkl; |  |  | Read_dWord(dVar:=Circ12DelovnaMoc_L3,lo:=3158,hi:=3159); |  |  | 79:MI4K2stik0_13Q1_vkl:=Bit_0; |  |  | 3159:Circ12DelovnaMoc_L3:=Long_0;
mind_bool[80]:=MI4K2stik0_14Q1_vkl; |  |  | Read_dWord(dVar:=Circ12Frekvenca_L1,lo:=3160,hi:=3161); |  |  | 80:MI4K2stik0_14Q1_vkl:=Bit_0; |  |  | 3161:Circ12Frekvenca_L1:=Long_0;
mind_bool[81]:=MI4K2stik0_15Q1_vkl; |  |  | Read_dWord(dVar:=Circ12InduktivnaEnergija,lo:=3162,hi:=3163); |  |  | 81:MI4K2stik0_15Q1_vkl:=Bit_0; |  |  | 3163:Circ12InduktivnaEnergija:=Long_0;
mind_bool[82]:=MI4K2stik0_16Q1_vkl; |  |  | Read_dWord(dVar:=Circ12InduktivnaMoc_III,lo:=3164,hi:=3165); |  |  | 82:MI4K2stik0_16Q1_vkl:=Bit_0; |  |  | 3165:Circ12InduktivnaMoc_III:=Long_0;
mind_bool[83]:=MI4K2stik0_17Q1_vkl; |  |  | Read_dWord(dVar:=Circ12JalovaMoc_L1,lo:=3166,hi:=3167); |  |  | 83:MI4K2stik0_17Q1_vkl:=Bit_0; |  |  | 3167:Circ12JalovaMoc_L1:=Long_0;
mind_bool[84]:=MI4K2stik0_18Q1_vkl; |  |  | Read_dWord(dVar:=Circ12JalovaMoc_L2,lo:=3168,hi:=3169); |  |  | 84:MI4K2stik0_18Q1_vkl:=Bit_0; |  |  | 3169:Circ12JalovaMoc_L2:=Long_0;
mind_bool[85]:=MI4K2stik0_19Q1_vkl; |  |  | Read_dWord(dVar:=Circ12JalovaMoc_L3,lo:=3170,hi:=3171); |  |  | 85:MI4K2stik0_19Q1_vkl:=Bit_0; |  |  | 3171:Circ12JalovaMoc_L3:=Long_0;
mind_bool[86]:=MI4K2stik0_1Q1_vkl; |  |  | Read_dWord(dVar:=Circ12KapacitivnaEnergija,lo:=3172,hi:=3173); |  |  | 86:MI4K2stik0_1Q1_vkl:=Bit_0; |  |  | 3173:Circ12KapacitivnaEnergija:=Long_0;
mind_bool[87]:=MI4K2stik0_20Q1_vkl; |  |  | Read_dWord(dVar:=Circ12KapacitivnaMoc_III,lo:=3174,hi:=3175); |  |  | 87:MI4K2stik0_20Q1_vkl:=Bit_0; |  |  | 3175:Circ12KapacitivnaMoc_III:=Long_0;
mind_bool[88]:=MI4K2stik0_21Q1_vkl; |  |  | Read_dWord(dVar:=Circ12MaximumDemand,lo:=3176,hi:=3177); |  |  | 88:MI4K2stik0_21Q1_vkl:=Bit_0; |  |  | 3177:Circ12MaximumDemand:=Long_0;
mind_bool[89]:=MI4K2stik0_22Q1_vkl; |  |  | Read_dWord(dVar:=Circ12Napetost_L1_L2,lo:=3178,hi:=3179); |  |  | 89:MI4K2stik0_22Q1_vkl:=Bit_0; |  |  | 3179:Circ12Napetost_L1_L2:=Long_0;
mind_bool[90]:=MI4K2stik0_23Q1_vkl; |  |  | Read_dWord(dVar:=Circ12Napetost_L1_N,lo:=3180,hi:=3181); |  |  | 90:MI4K2stik0_23Q1_vkl:=Bit_0; |  |  | 3181:Circ12Napetost_L1_N:=Long_0;
mind_bool[91]:=MI4K2stikA3_11Q1_vkl; |  |  | Read_dWord(dVar:=Circ12Napetost_L2_L3,lo:=3182,hi:=3183); |  |  | 91:MI4K2stikA3_11Q1_vkl:=Bit_0; |  |  | 3183:Circ12Napetost_L2_L3:=Long_0;
mind_bool[92]:=MI4K2stikA3_12Q1_vkl; |  |  | Read_dWord(dVar:=Circ12Napetost_L2_N,lo:=3184,hi:=3185); |  |  | 92:MI4K2stikA3_12Q1_vkl:=Bit_0; |  |  | 3185:Circ12Napetost_L2_N:=Long_0;
mind_bool[93]:=MI4K2stikA3_13Q1_vkl; |  |  | Read_dWord(dVar:=Circ12Napetost_L3_L1,lo:=3186,hi:=3187); |  |  | 93:MI4K2stikA3_13Q1_vkl:=Bit_0; |  |  | 3187:Circ12Napetost_L3_L1:=Long_0;
mind_bool[94]:=MI4K2stikA3_14Q1_vkl; |  |  | Read_dWord(dVar:=Circ12Napetost_L3_N,lo:=3188,hi:=3189); |  |  | 94:MI4K2stikA3_14Q1_vkl:=Bit_0; |  |  | 3189:Circ12Napetost_L3_N:=Long_0;
mind_bool[95]:=MI4K2stikA3_15Q1_vkl; |  |  | Read_dWord(dVar:=Circ12NavideznaMoc_III,lo:=3190,hi:=3191); |  |  | 95:MI4K2stikA3_15Q1_vkl:=Bit_0; |  |  | 3191:Circ12NavideznaMoc_III:=Long_0;
mind_bool[96]:=MI4K2stikA3_1Q1_vkl; |  |  | Read_dWord(dVar:=Circ12NicelniTok,lo:=3192,hi:=3193); |  |  | 96:MI4K2stikA3_1Q1_vkl:=Bit_0; |  |  | 3193:Circ12NicelniTok:=Long_0;
mind_bool[97]:=MI4K2stikA3_2Q1_vkl; |  |  | Read_dWord(dVar:=Circ12PowerFactor_III,lo:=3194,hi:=3195); |  |  | 97:MI4K2stikA3_2Q1_vkl:=Bit_0; |  |  | 3195:Circ12PowerFactor_III:=Long_0;
mind_bool[98]:=MI4krmDA_daljinsko; |  |  | Read_dWord(dVar:=Circ12PowerFactor_L1,lo:=3196,hi:=3197); |  |  | 98:MI4krmDA_daljinsko:=Bit_0; |  |  | 3197:Circ12PowerFactor_L1:=Long_0;
mind_bool[99]:=MI4motorA1_1Q1_prip; |  |  | Read_dWord(dVar:=Circ12PowerFactor_L2,lo:=3198,hi:=3199); |  |  | 99:MI4motorA1_1Q1_prip:=Bit_0; |  |  | 3199:Circ12PowerFactor_L2:=Long_0;
mind_bool[100]:=MI4motorA1_2Q1_prip; |  |  | Read_dWord(dVar:=Circ12PowerFactor_L3,lo:=3200,hi:=3201); |  |  | 100:MI4motorA1_2Q1_prip:=Bit_0; |  |  | 3201:Circ12PowerFactor_L3:=Long_0;
mind_bool[101]:=MI4motorA2_1Q1_prip; |  |  | Read_dWord(dVar:=Circ12THDI_L1,lo:=3202,hi:=3203); |  |  | 101:MI4motorA2_1Q1_prip:=Bit_0; |  |  | 3203:Circ12THDI_L1:=Long_0;
mind_bool[102]:=MI4motorA2_2Q1_prip; |  |  | Read_dWord(dVar:=Circ12THDI_L2,lo:=3204,hi:=3205); |  |  | 102:MI4motorA2_2Q1_prip:=Bit_0; |  |  | 3205:Circ12THDI_L2:=Long_0;
mind_bool[103]:=MI4motorA2_6Q1_prip; |  |  | Read_dWord(dVar:=Circ12THDI_L3,lo:=3206,hi:=3207); |  |  | 103:MI4motorA2_6Q1_prip:=Bit_0; |  |  | 3207:Circ12THDI_L3:=Long_0;
mind_bool[104]:=MI4mrez_nap_RGM_A1; |  |  | Read_dWord(dVar:=Circ12THDV_L1,lo:=3208,hi:=3209); |  |  | 104:MI4mrez_nap_RGM_A1:=Bit_0; |  |  | 3209:Circ12THDV_L1:=Long_0;
mind_bool[105]:=MI4mrez_nap_RGM_A2; |  |  | Read_dWord(dVar:=Circ12THDV_L2,lo:=3210,hi:=3211); |  |  | 105:MI4mrez_nap_RGM_A2:=Bit_0; |  |  | 3211:Circ12THDV_L2:=Long_0;
mind_bool[106]:=MI4mrezaA1_1Q1_izklop; |  |  | Read_dWord(dVar:=Circ12THDV_L3,lo:=3212,hi:=3213); |  |  | 106:MI4mrezaA1_1Q1_izklop:=Bit_0; |  |  | 3213:Circ12THDV_L3:=Long_0;
mind_bool[107]:=MI4mrezaA1_1Q1_vklop; |  |  | Read_dWord(dVar:=Circ12Tok_L1,lo:=3214,hi:=3215); |  |  | 107:MI4mrezaA1_1Q1_vklop:=Bit_0; |  |  | 3215:Circ12Tok_L1:=Long_0;
mind_bool[108]:=MI4mrezaA2_1Q1_izklop; |  |  | Read_dWord(dVar:=Circ12Tok_L2,lo:=3216,hi:=3217); |  |  | 108:MI4mrezaA2_1Q1_izklop:=Bit_0; |  |  | 3217:Circ12Tok_L2:=Long_0;
mind_bool[109]:=MI4mrezaA2_1Q1_vklop; |  |  | Read_dWord(dVar:=Circ12Tok_L3,lo:=3218,hi:=3219); |  |  | 109:MI4mrezaA2_1Q1_vklop:=Bit_0; |  |  | 3219:Circ12Tok_L3:=Long_0;
mind_bool[110]:=MI4napaka_alarm_DA1; |  |  | Read_dWord(dVar:=Circ12TokPovprecje_III,lo:=3220,hi:=3221); |  |  | 110:MI4napaka_alarm_DA1:=Bit_0; |  |  | 3221:Circ12TokPovprecje_III:=Long_0;
mind_bool[111]:=MI4napaka_alarm_DA2; |  |  | Read_dWord(dVar:=Circ13CosFi_III,lo:=3222,hi:=3223); |  |  | 111:MI4napaka_alarm_DA2:=Bit_0; |  |  | 3223:Circ13CosFi_III:=Long_0;
mind_bool[112]:=MI4prenap_zascA1_OK; |  |  | Read_dWord(dVar:=Circ13DelovnaEnergija,lo:=3224,hi:=3225); |  |  | 112:MI4prenap_zascA1_OK:=Bit_0; |  |  | 3225:Circ13DelovnaEnergija:=Long_0;
mind_bool[113]:=MI4prenap_zascA2_OK; |  |  | Read_dWord(dVar:=Circ13DelovnaMoc_III,lo:=3226,hi:=3227); |  |  | 113:MI4prenap_zascA2_OK:=Bit_0; |  |  | 3227:Circ13DelovnaMoc_III:=Long_0;
mind_bool[114]:=MI4rezerva_DA1; |  |  | Read_dWord(dVar:=Circ13DelovnaMoc_L1,lo:=3228,hi:=3229); |  |  | 114:MI4rezerva_DA1:=Bit_0; |  |  | 3229:Circ13DelovnaMoc_L1:=Long_0;
mind_bool[115]:=MI4rocni_izkA1_11Q1; |  |  | Read_dWord(dVar:=Circ13DelovnaMoc_L2,lo:=3230,hi:=3231); |  |  | 115:MI4rocni_izkA1_11Q1:=Bit_0; |  |  | 3231:Circ13DelovnaMoc_L2:=Long_0;
mind_bool[116]:=MI4rocni_izkA1_12Q1; |  |  | Read_dWord(dVar:=Circ13DelovnaMoc_L3,lo:=3232,hi:=3233); |  |  | 116:MI4rocni_izkA1_12Q1:=Bit_0; |  |  | 3233:Circ13DelovnaMoc_L3:=Long_0;
mind_bool[117]:=MI4rocni_izkA1_13Q1; |  |  | Read_dWord(dVar:=Circ13Frekvenca_L1,lo:=3234,hi:=3235); |  |  | 117:MI4rocni_izkA1_13Q1:=Bit_0; |  |  | 3235:Circ13Frekvenca_L1:=Long_0;
mind_bool[118]:=MI4rocni_izkA1_14Q1; |  |  | Read_dWord(dVar:=Circ13InduktivnaEnergija,lo:=3236,hi:=3237); |  |  | 118:MI4rocni_izkA1_14Q1:=Bit_0; |  |  | 3237:Circ13InduktivnaEnergija:=Long_0;
mind_bool[119]:=MI4rocni_izkA1_15Q1; |  |  | Read_dWord(dVar:=Circ13InduktivnaMoc_III,lo:=3238,hi:=3239); |  |  | 119:MI4rocni_izkA1_15Q1:=Bit_0; |  |  | 3239:Circ13InduktivnaMoc_III:=Long_0;
mind_bool[120]:=MI4rocni_izkA1_16Q1; |  |  | Read_dWord(dVar:=Circ13JalovaMoc_L1,lo:=3240,hi:=3241); |  |  | 120:MI4rocni_izkA1_16Q1:=Bit_0; |  |  | 3241:Circ13JalovaMoc_L1:=Long_0;
mind_bool[121]:=MI4rocni_izkA1_17Q1; |  |  | Read_dWord(dVar:=Circ13JalovaMoc_L2,lo:=3242,hi:=3243); |  |  | 121:MI4rocni_izkA1_17Q1:=Bit_0; |  |  | 3243:Circ13JalovaMoc_L2:=Long_0;
mind_bool[122]:=MI4rocni_izkA2_11Q1; |  |  | Read_dWord(dVar:=Circ13JalovaMoc_L3,lo:=3244,hi:=3245); |  |  | 122:MI4rocni_izkA2_11Q1:=Bit_0; |  |  | 3245:Circ13JalovaMoc_L3:=Long_0;
mind_bool[123]:=MI4rocni_izkA2_12Q1; |  |  | Read_dWord(dVar:=Circ13KapacitivnaEnergija,lo:=3246,hi:=3247); |  |  | 123:MI4rocni_izkA2_12Q1:=Bit_0; |  |  | 3247:Circ13KapacitivnaEnergija:=Long_0;
mind_bool[124]:=MI4rocni_izkA2_13Q1; |  |  | Read_dWord(dVar:=Circ13KapacitivnaMoc_III,lo:=3248,hi:=3249); |  |  | 124:MI4rocni_izkA2_13Q1:=Bit_0; |  |  | 3249:Circ13KapacitivnaMoc_III:=Long_0;
mind_bool[125]:=MI4rocni_izkA2_14Q1; |  |  | Read_dWord(dVar:=Circ13MaximumDemand,lo:=3250,hi:=3251); |  |  | 125:MI4rocni_izkA2_14Q1:=Bit_0; |  |  | 3251:Circ13MaximumDemand:=Long_0;
mind_bool[126]:=MI4sinhroniziranje_DA1; |  |  | Read_dWord(dVar:=Circ13Napetost_L1_L2,lo:=3252,hi:=3253); |  |  | 126:MI4sinhroniziranje_DA1:=Bit_0; |  |  | 3253:Circ13Napetost_L1_L2:=Long_0;
mind_bool[127]:=MI4sinhroniziranje_DA2; |  |  | Read_dWord(dVar:=Circ13Napetost_L1_N,lo:=3254,hi:=3255); |  |  | 127:MI4sinhroniziranje_DA2:=Bit_0; |  |  | 3255:Circ13Napetost_L1_N:=Long_0;
mind_bool[128]:=MI4splosna_napaka_DA1; |  |  | Read_dWord(dVar:=Circ13Napetost_L2_L3,lo:=3256,hi:=3257); |  |  | 128:MI4splosna_napaka_DA1:=Bit_0; |  |  | 3257:Circ13Napetost_L2_L3:=Long_0;
mind_bool[129]:=MI4splosna_napaka_DA2; |  |  | Read_dWord(dVar:=Circ13Napetost_L2_N,lo:=3258,hi:=3259); |  |  | 129:MI4splosna_napaka_DA2:=Bit_0; |  |  | 3259:Circ13Napetost_L2_N:=Long_0;
mind_bool[130]:=MI4stikA1_11Q1_vkl; |  |  | Read_dWord(dVar:=Circ13Napetost_L3_L1,lo:=3260,hi:=3261); |  |  | 130:MI4stikA1_11Q1_vkl:=Bit_0; |  |  | 3261:Circ13Napetost_L3_L1:=Long_0;
mind_bool[131]:=MI4stikA1_12Q1_vkl; |  |  | Read_dWord(dVar:=Circ13Napetost_L3_N,lo:=3262,hi:=3263); |  |  | 131:MI4stikA1_12Q1_vkl:=Bit_0; |  |  | 3263:Circ13Napetost_L3_N:=Long_0;
mind_bool[132]:=MI4stikA1_13Q1_vkl; |  |  | Read_dWord(dVar:=Circ13NavideznaMoc_III,lo:=3264,hi:=3265); |  |  | 132:MI4stikA1_13Q1_vkl:=Bit_0; |  |  | 3265:Circ13NavideznaMoc_III:=Long_0;
mind_bool[133]:=MI4stikA1_14Q1_vkl; |  |  | Read_dWord(dVar:=Circ13NicelniTok,lo:=3266,hi:=3267); |  |  | 133:MI4stikA1_14Q1_vkl:=Bit_0; |  |  | 3267:Circ13NicelniTok:=Long_0;
mind_bool[134]:=MI4stikA1_15Q1_vkl; |  |  | Read_dWord(dVar:=Circ13PowerFactor_III,lo:=3268,hi:=3269); |  |  | 134:MI4stikA1_15Q1_vkl:=Bit_0; |  |  | 3269:Circ13PowerFactor_III:=Long_0;
mind_bool[135]:=MI4stikA1_16Q1_vkl; |  |  | Read_dWord(dVar:=Circ13PowerFactor_L1,lo:=3270,hi:=3271); |  |  | 135:MI4stikA1_16Q1_vkl:=Bit_0; |  |  | 3271:Circ13PowerFactor_L1:=Long_0;
mind_bool[136]:=MI4stikA1_17Q1_vkl; |  |  | Read_dWord(dVar:=Circ13PowerFactor_L2,lo:=3272,hi:=3273); |  |  | 136:MI4stikA1_17Q1_vkl:=Bit_0; |  |  | 3273:Circ13PowerFactor_L2:=Long_0;
mind_bool[137]:=MI4stikA1_1Q1_vkl; |  |  | Read_dWord(dVar:=Circ13PowerFactor_L3,lo:=3274,hi:=3275); |  |  | 137:MI4stikA1_1Q1_vkl:=Bit_0; |  |  | 3275:Circ13PowerFactor_L3:=Long_0;
mind_bool[138]:=MI4stikA1_2Q1_vkl; |  |  | Read_dWord(dVar:=Circ13THDI_L1,lo:=3276,hi:=3277); |  |  | 138:MI4stikA1_2Q1_vkl:=Bit_0; |  |  | 3277:Circ13THDI_L1:=Long_0;
mind_bool[139]:=MI4stikA1_6Q1_vkl; |  |  | Read_dWord(dVar:=Circ13THDI_L2,lo:=3278,hi:=3279); |  |  | 139:MI4stikA1_6Q1_vkl:=Bit_0; |  |  | 3279:Circ13THDI_L2:=Long_0;
mind_bool[140]:=MI4stikA2_11Q1_vkl; |  |  | Read_dWord(dVar:=Circ13THDI_L3,lo:=3280,hi:=3281); |  |  | 140:MI4stikA2_11Q1_vkl:=Bit_0; |  |  | 3281:Circ13THDI_L3:=Long_0;
mind_bool[141]:=MI4stikA2_12Q1_vkl; |  |  | Read_dWord(dVar:=Circ13THDV_L1,lo:=3282,hi:=3283); |  |  | 141:MI4stikA2_12Q1_vkl:=Bit_0; |  |  | 3283:Circ13THDV_L1:=Long_0;
mind_bool[142]:=MI4stikA2_13Q1_vkl; |  |  | Read_dWord(dVar:=Circ13THDV_L2,lo:=3284,hi:=3285); |  |  | 142:MI4stikA2_13Q1_vkl:=Bit_0; |  |  | 3285:Circ13THDV_L2:=Long_0;
mind_bool[143]:=MI4stikA2_14Q1_vkl; |  |  | Read_dWord(dVar:=Circ13THDV_L3,lo:=3286,hi:=3287); |  |  | 143:MI4stikA2_14Q1_vkl:=Bit_0; |  |  | 3287:Circ13THDV_L3:=Long_0;
mind_bool[144]:=MI4stikA2_1Q1_vkl; |  |  | Read_dWord(dVar:=Circ13Tok_L1,lo:=3288,hi:=3289); |  |  | 144:MI4stikA2_1Q1_vkl:=Bit_0; |  |  | 3289:Circ13Tok_L1:=Long_0;
mind_bool[145]:=MI4stikA2_2Q1_vkl; |  |  | Read_dWord(dVar:=Circ13Tok_L2,lo:=3290,hi:=3291); |  |  | 145:MI4stikA2_2Q1_vkl:=Bit_0; |  |  | 3291:Circ13Tok_L2:=Long_0;
mind_bool[146]:=MI4vezno_6Q1_izklop; |  |  | Read_dWord(dVar:=Circ13Tok_L3,lo:=3292,hi:=3293); |  |  | 146:MI4vezno_6Q1_izklop:=Bit_0; |  |  | 3293:Circ13Tok_L3:=Long_0;
mind_bool[147]:=MI4vezno_6Q1_vklop; |  |  | Read_dWord(dVar:=Circ13TokPovprecje_III,lo:=3294,hi:=3295); |  |  | 147:MI4vezno_6Q1_vklop:=Bit_0; |  |  | 3295:Circ13TokPovprecje_III:=Long_0;
mind_bool[148]:=MI4vzporedno_del_nikoli; |  |  | Read_dWord(dVar:=Circ14CosFi_III,lo:=3296,hi:=3297); |  |  | 148:MI4vzporedno_del_nikoli:=Bit_0; |  |  | 3297:Circ14CosFi_III:=Long_0;
mind_bool[149]:=MI4vzporedno_del_nikoli_info; |  |  | Read_dWord(dVar:=Circ14DelovnaEnergija,lo:=3298,hi:=3299); |  |  | 149:MI4vzporedno_del_nikoli_info:=Bit_0; |  |  | 3299:Circ14DelovnaEnergija:=Long_0;
mind_bool[150]:=MI4vzporedno_del_po_potrebi; |  |  | Read_dWord(dVar:=Circ14DelovnaMoc_III,lo:=3300,hi:=3301); |  |  | 150:MI4vzporedno_del_po_potrebi:=Bit_0; |  |  | 3301:Circ14DelovnaMoc_III:=Long_0;
mind_bool[151]:=MI4vzporedno_del_po_potrebi_info; |  |  | Read_dWord(dVar:=Circ14DelovnaMoc_L1,lo:=3302,hi:=3303); |  |  | 151:MI4vzporedno_del_po_potrebi_info:=Bit_0; |  |  | 3303:Circ14DelovnaMoc_L1:=Long_0;
mind_bool[152]:=MI4vzporedno_del_vedno; |  |  | Read_dWord(dVar:=Circ14DelovnaMoc_L2,lo:=3304,hi:=3305); |  |  | 152:MI4vzporedno_del_vedno:=Bit_0; |  |  | 3305:Circ14DelovnaMoc_L2:=Long_0;
mind_bool[153]:=MI4vzporedno_del_vedno_info; |  |  | Read_dWord(dVar:=Circ14DelovnaMoc_L3,lo:=3306,hi:=3307); |  |  | 153:MI4vzporedno_del_vedno_info:=Bit_0; |  |  | 3307:Circ14DelovnaMoc_L3:=Long_0;
mind_bool[154]:=MI4zaganjanje_DA1; |  |  | Read_dWord(dVar:=Circ14Frekvenca_L1,lo:=3308,hi:=3309); |  |  | 154:MI4zaganjanje_DA1:=Bit_0; |  |  | 3309:Circ14Frekvenca_L1:=Long_0;
mind_bool[155]:=MI4zaganjanje_DA2; |  |  | Read_dWord(dVar:=Circ14InduktivnaEnergija,lo:=3310,hi:=3311); |  |  | 155:MI4zaganjanje_DA2:=Bit_0; |  |  | 3311:Circ14InduktivnaEnergija:=Long_0;
mind_bool[156]:=mrezaDA3motorni_pogon_okvara; |  |  | Read_dWord(dVar:=Circ14InduktivnaMoc_III,lo:=3312,hi:=3313); |  |  | 156:mrezaDA3motorni_pogon_okvara:=Bit_0; |  |  | 3313:Circ14InduktivnaMoc_III:=Long_0;
mind_bool[157]:=mrezaDA3stikalo_okvara; |  |  | Read_dWord(dVar:=Circ14JalovaMoc_L1,lo:=3314,hi:=3315); |  |  | 157:mrezaDA3stikalo_okvara:=Bit_0; |  |  | 3315:Circ14JalovaMoc_L1:=Long_0;
mind_bool[158]:=Napaka_v_kom_cirk_DA1; |  |  | Read_dWord(dVar:=Circ14JalovaMoc_L2,lo:=3316,hi:=3317); |  |  | 158:Napaka_v_kom_cirk_DA1:=Bit_0; |  |  | 3317:Circ14JalovaMoc_L2:=Long_0;
mind_bool[159]:=Napaka_v_kom_cirk_DA2; |  |  | Read_dWord(dVar:=Circ14JalovaMoc_L3,lo:=3318,hi:=3319); |  |  | 159:Napaka_v_kom_cirk_DA2:=Bit_0; |  |  | 3319:Circ14JalovaMoc_L3:=Long_0;
mind_bool[160]:=NapakaCOMModBus; |  |  | Read_dWord(dVar:=Circ14KapacitivnaEnergija,lo:=3320,hi:=3321); |  |  | 160:NapakaCOMModBus:=Bit_0; |  |  | 3321:Circ14KapacitivnaEnergija:=Long_0;
mind_bool[161]:=NapakaVKomunikaciji_Circutor1; |  |  | Read_dWord(dVar:=Circ14KapacitivnaMoc_III,lo:=3322,hi:=3323); |  |  | 161:NapakaVKomunikaciji_Circutor1:=Bit_0; |  |  | 3323:Circ14KapacitivnaMoc_III:=Long_0;
mind_bool[162]:=NapakaVKomunikaciji_Circutor10; |  |  | Read_dWord(dVar:=Circ14MaximumDemand,lo:=3324,hi:=3325); |  |  | 162:NapakaVKomunikaciji_Circutor10:=Bit_0; |  |  | 3325:Circ14MaximumDemand:=Long_0;
mind_bool[163]:=NapakaVKomunikaciji_Circutor11; |  |  | Read_dWord(dVar:=Circ14Napetost_L1_L2,lo:=3326,hi:=3327); |  |  | 163:NapakaVKomunikaciji_Circutor11:=Bit_0; |  |  | 3327:Circ14Napetost_L1_L2:=Long_0;
mind_bool[164]:=NapakaVKomunikaciji_Circutor12; |  |  | Read_dWord(dVar:=Circ14Napetost_L1_N,lo:=3328,hi:=3329); |  |  | 164:NapakaVKomunikaciji_Circutor12:=Bit_0; |  |  | 3329:Circ14Napetost_L1_N:=Long_0;
mind_bool[165]:=NapakaVKomunikaciji_Circutor13; |  |  | Read_dWord(dVar:=Circ14Napetost_L2_L3,lo:=3330,hi:=3331); |  |  | 165:NapakaVKomunikaciji_Circutor13:=Bit_0; |  |  | 3331:Circ14Napetost_L2_L3:=Long_0;
mind_bool[166]:=NapakaVKomunikaciji_Circutor14; |  |  | Read_dWord(dVar:=Circ14Napetost_L2_N,lo:=3332,hi:=3333); |  |  | 166:NapakaVKomunikaciji_Circutor14:=Bit_0; |  |  | 3333:Circ14Napetost_L2_N:=Long_0;
mind_bool[167]:=NapakaVKomunikaciji_Circutor15; |  |  | Read_dWord(dVar:=Circ14Napetost_L3_L1,lo:=3334,hi:=3335); |  |  | 167:NapakaVKomunikaciji_Circutor15:=Bit_0; |  |  | 3335:Circ14Napetost_L3_L1:=Long_0;
mind_bool[168]:=NapakaVKomunikaciji_Circutor16; |  |  | Read_dWord(dVar:=Circ14Napetost_L3_N,lo:=3336,hi:=3337); |  |  | 168:NapakaVKomunikaciji_Circutor16:=Bit_0; |  |  | 3337:Circ14Napetost_L3_N:=Long_0;
mind_bool[169]:=NapakaVKomunikaciji_Circutor17; |  |  | Read_dWord(dVar:=Circ14NavideznaMoc_III,lo:=3338,hi:=3339); |  |  | 169:NapakaVKomunikaciji_Circutor17:=Bit_0; |  |  | 3339:Circ14NavideznaMoc_III:=Long_0;
mind_bool[170]:=NapakaVKomunikaciji_Circutor18; |  |  | Read_dWord(dVar:=Circ14NicelniTok,lo:=3340,hi:=3341); |  |  | 170:NapakaVKomunikaciji_Circutor18:=Bit_0; |  |  | 3341:Circ14NicelniTok:=Long_0;
mind_bool[171]:=NapakaVKomunikaciji_Circutor19; |  |  | Read_dWord(dVar:=Circ14PowerFactor_III,lo:=3342,hi:=3343); |  |  | 171:NapakaVKomunikaciji_Circutor19:=Bit_0; |  |  | 3343:Circ14PowerFactor_III:=Long_0;
mind_bool[172]:=NapakaVKomunikaciji_Circutor2; |  |  | Read_dWord(dVar:=Circ14PowerFactor_L1,lo:=3344,hi:=3345); |  |  | 172:NapakaVKomunikaciji_Circutor2:=Bit_0; |  |  | 3345:Circ14PowerFactor_L1:=Long_0;
mind_bool[173]:=NapakaVKomunikaciji_Circutor20; |  |  | Read_dWord(dVar:=Circ14PowerFactor_L2,lo:=3346,hi:=3347); |  |  | 173:NapakaVKomunikaciji_Circutor20:=Bit_0; |  |  | 3347:Circ14PowerFactor_L2:=Long_0;
mind_bool[174]:=NapakaVKomunikaciji_Circutor21; |  |  | Read_dWord(dVar:=Circ14PowerFactor_L3,lo:=3348,hi:=3349); |  |  | 174:NapakaVKomunikaciji_Circutor21:=Bit_0; |  |  | 3349:Circ14PowerFactor_L3:=Long_0;
mind_bool[175]:=NapakaVKomunikaciji_Circutor22; |  |  | Read_dWord(dVar:=Circ14THDI_L1,lo:=3350,hi:=3351); |  |  | 175:NapakaVKomunikaciji_Circutor22:=Bit_0; |  |  | 3351:Circ14THDI_L1:=Long_0;
mind_bool[176]:=NapakaVKomunikaciji_Circutor23; |  |  | Read_dWord(dVar:=Circ14THDI_L2,lo:=3352,hi:=3353); |  |  | 176:NapakaVKomunikaciji_Circutor23:=Bit_0; |  |  | 3353:Circ14THDI_L2:=Long_0;
mind_bool[177]:=NapakaVKomunikaciji_Circutor24; |  |  | Read_dWord(dVar:=Circ14THDI_L3,lo:=3354,hi:=3355); |  |  | 177:NapakaVKomunikaciji_Circutor24:=Bit_0; |  |  | 3355:Circ14THDI_L3:=Long_0;
mind_bool[178]:=NapakaVKomunikaciji_Circutor25; |  |  | Read_dWord(dVar:=Circ14THDV_L1,lo:=3356,hi:=3357); |  |  | 178:NapakaVKomunikaciji_Circutor25:=Bit_0; |  |  | 3357:Circ14THDV_L1:=Long_0;
mind_bool[179]:=NapakaVKomunikaciji_Circutor3; |  |  | Read_dWord(dVar:=Circ14THDV_L2,lo:=3358,hi:=3359); |  |  | 179:NapakaVKomunikaciji_Circutor3:=Bit_0; |  |  | 3359:Circ14THDV_L2:=Long_0;
mind_bool[180]:=NapakaVKomunikaciji_Circutor4; |  |  | Read_dWord(dVar:=Circ14THDV_L3,lo:=3360,hi:=3361); |  |  | 180:NapakaVKomunikaciji_Circutor4:=Bit_0; |  |  | 3361:Circ14THDV_L3:=Long_0;
mind_bool[181]:=NapakaVKomunikaciji_Circutor5; |  |  | Read_dWord(dVar:=Circ14Tok_L1,lo:=3362,hi:=3363); |  |  | 181:NapakaVKomunikaciji_Circutor5:=Bit_0; |  |  | 3363:Circ14Tok_L1:=Long_0;
mind_bool[182]:=NapakaVKomunikaciji_Circutor6; |  |  | Read_dWord(dVar:=Circ14Tok_L2,lo:=3364,hi:=3365); |  |  | 182:NapakaVKomunikaciji_Circutor6:=Bit_0; |  |  | 3365:Circ14Tok_L2:=Long_0;
mind_bool[183]:=NapakaVKomunikaciji_Circutor7; |  |  | Read_dWord(dVar:=Circ14Tok_L3,lo:=3366,hi:=3367); |  |  | 183:NapakaVKomunikaciji_Circutor7:=Bit_0; |  |  | 3367:Circ14Tok_L3:=Long_0;
mind_bool[184]:=NapakaVKomunikaciji_Circutor8; |  |  | Read_dWord(dVar:=Circ14TokPovprecje_III,lo:=3368,hi:=3369); |  |  | 184:NapakaVKomunikaciji_Circutor8:=Bit_0; |  |  | 3369:Circ14TokPovprecje_III:=Long_0;
mind_bool[185]:=NapakaVKomunikaciji_Circutor9; |  |  | Read_dWord(dVar:=Circ15CosFi_III,lo:=3370,hi:=3371); |  |  | 185:NapakaVKomunikaciji_Circutor9:=Bit_0; |  |  | 3371:Circ15CosFi_III:=Long_0;
mind_bool[186]:=RDASlabaBaterijaMI4; |  |  | Read_dWord(dVar:=Circ15DelovnaEnergija,lo:=3372,hi:=3373); |  |  | 186:RDASlabaBaterijaMI4:=Bit_0; |  |  | 3373:Circ15DelovnaEnergija:=Long_0;
mind_bool[187]:=SlabaBaterijaMI4; |  |  | Read_dWord(dVar:=Circ15DelovnaMoc_III,lo:=3374,hi:=3375); |  |  | 187:SlabaBaterijaMI4:=Bit_0; |  |  | 3375:Circ15DelovnaMoc_III:=Long_0;
mind_bool[188]:=SlabaBaterijaPLC1; |  |  | Read_dWord(dVar:=Circ15DelovnaMoc_L1,lo:=3376,hi:=3377); |  |  | 188:SlabaBaterijaPLC1:=Bit_0; |  |  | 3377:Circ15DelovnaMoc_L1:=Long_0;
mind_bool[189]:=SlabaBaterijaPLC2; |  |  | Read_dWord(dVar:=Circ15DelovnaMoc_L2,lo:=3378,hi:=3379); |  |  | 189:SlabaBaterijaPLC2:=Bit_0; |  |  | 3379:Circ15DelovnaMoc_L2:=Long_0;
mind_bool[190]:=stikaloDA3_okvara; |  |  | Read_dWord(dVar:=Circ15DelovnaMoc_L3,lo:=3380,hi:=3381); |  |  | 190:stikaloDA3_okvara:=Bit_0; |  |  | 3381:Circ15DelovnaMoc_L3:=Long_0;
mind_bool[191]:=UI_MI4K2DA3_2Q1_izklop; |  |  | Read_dWord(dVar:=Circ15Frekvenca_L1,lo:=3382,hi:=3383); |  |  | 191:UI_MI4K2DA3_2Q1_izklop:=Bit_0; |  |  | 3383:Circ15Frekvenca_L1:=Long_0;
mind_bool[192]:=UI_MI4K2DA3_2Q1_vklop; |  |  | Read_dWord(dVar:=Circ15InduktivnaEnergija,lo:=3384,hi:=3385); |  |  | 192:UI_MI4K2DA3_2Q1_vklop:=Bit_0; |  |  | 3385:Circ15InduktivnaEnergija:=Long_0;
mind_bool[193]:=UI_MI4K2mrezaA3_1Q1_izklop; |  |  | Read_dWord(dVar:=Circ15InduktivnaMoc_III,lo:=3386,hi:=3387); |  |  | 193:UI_MI4K2mrezaA3_1Q1_izklop:=Bit_0; |  |  | 3387:Circ15InduktivnaMoc_III:=Long_0;
mind_bool[194]:=UI_MI4K2mrezaA3_1Q1_vklop; |  |  | Read_dWord(dVar:=Circ15JalovaMoc_L1,lo:=3388,hi:=3389); |  |  | 194:UI_MI4K2mrezaA3_1Q1_vklop:=Bit_0; |  |  | 3389:Circ15JalovaMoc_L1:=Long_0;
mind_bool[195]:=cas_nastavi; |  |  | Read_dWord(dVar:=Circ15JalovaMoc_L2,lo:=3390,hi:=3391); |  |  | 195:cas_nastavi:=Bit_0; |  |  | 3391:Circ15JalovaMoc_L2:=Long_0;
mind_bool[196]:=Circ_Vpis_Dnevne_energija_scada1; |  |  | Read_dWord(dVar:=Circ15JalovaMoc_L3,lo:=3392,hi:=3393); |  |  | 196:Circ_Vpis_Dnevne_energija_scada1:=Bit_0; |  |  | 3393:Circ15JalovaMoc_L3:=Long_0;
mind_bool[197]:=Circ_Vpis_Dnevne_energija_scada2; |  |  | Read_dWord(dVar:=Circ15KapacitivnaEnergija,lo:=3394,hi:=3395); |  |  | 197:Circ_Vpis_Dnevne_energija_scada2:=Bit_0; |  |  | 3395:Circ15KapacitivnaEnergija:=Long_0;
mind_bool[198]:=Circ_Vpis_Tedenska_energija_scada1; |  |  | Read_dWord(dVar:=Circ15KapacitivnaMoc_III,lo:=3396,hi:=3397); |  |  | 198:Circ_Vpis_Tedenska_energija_scada1:=Bit_0; |  |  | 3397:Circ15KapacitivnaMoc_III:=Long_0;
mind_bool[199]:=Circ_Vpis_Tedenska_energija_scada2; |  |  | Read_dWord(dVar:=Circ15MaximumDemand,lo:=3398,hi:=3399); |  |  | 199:Circ_Vpis_Tedenska_energija_scada2:=Bit_0; |  |  | 3399:Circ15MaximumDemand:=Long_0;
mind_bool[200]:=Circ_Vpis_Mesecna_energija_scada1; |  |  | Read_dWord(dVar:=Circ15Napetost_L1_L2,lo:=3400,hi:=3401); |  |  | 200:Circ_Vpis_Mesecna_energija_scada1:=Bit_0; |  |  | 3401:Circ15Napetost_L1_L2:=Long_0;
mind_bool[201]:=Circ_Vpis_Mesecna_energija_scada2; |  |  | Read_dWord(dVar:=Circ15Napetost_L1_N,lo:=3402,hi:=3403); |  |  | 201:Circ_Vpis_Mesecna_energija_scada2:=Bit_0; |  |  | 3403:Circ15Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ15Napetost_L2_L3,lo:=3404,hi:=3405); | [5 empty] | 3405:Circ15Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ15Napetost_L2_N,lo:=3406,hi:=3407); | [5 empty] | 3407:Circ15Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ15Napetost_L3_L1,lo:=3408,hi:=3409); | [5 empty] | 3409:Circ15Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ15Napetost_L3_N,lo:=3410,hi:=3411); | [5 empty] | 3411:Circ15Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ15NavideznaMoc_III,lo:=3412,hi:=3413); | [5 empty] | 3413:Circ15NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ15NicelniTok,lo:=3414,hi:=3415); | [5 empty] | 3415:Circ15NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ15PowerFactor_III,lo:=3416,hi:=3417); | [5 empty] | 3417:Circ15PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ15PowerFactor_L1,lo:=3418,hi:=3419); | [5 empty] | 3419:Circ15PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ15PowerFactor_L2,lo:=3420,hi:=3421); | [5 empty] | 3421:Circ15PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ15PowerFactor_L3,lo:=3422,hi:=3423); | [5 empty] | 3423:Circ15PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ15THDI_L1,lo:=3424,hi:=3425); | [5 empty] | 3425:Circ15THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ15THDI_L2,lo:=3426,hi:=3427); | [5 empty] | 3427:Circ15THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ15THDI_L3,lo:=3428,hi:=3429); | [5 empty] | 3429:Circ15THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ15THDV_L1,lo:=3430,hi:=3431); | [5 empty] | 3431:Circ15THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ15THDV_L2,lo:=3432,hi:=3433); | [5 empty] | 3433:Circ15THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ15THDV_L3,lo:=3434,hi:=3435); | [5 empty] | 3435:Circ15THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ15Tok_L1,lo:=3436,hi:=3437); | [5 empty] | 3437:Circ15Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ15Tok_L2,lo:=3438,hi:=3439); | [5 empty] | 3439:Circ15Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ15Tok_L3,lo:=3440,hi:=3441); | [5 empty] | 3441:Circ15Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ15TokPovprecje_III,lo:=3442,hi:=3443); | [5 empty] | 3443:Circ15TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ16CosFi_III,lo:=3444,hi:=3445); | [5 empty] | 3445:Circ16CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ16DelovnaEnergija,lo:=3446,hi:=3447); | [5 empty] | 3447:Circ16DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ16DelovnaMoc_III,lo:=3448,hi:=3449); | [5 empty] | 3449:Circ16DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ16DelovnaMoc_L1,lo:=3450,hi:=3451); | [5 empty] | 3451:Circ16DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ16DelovnaMoc_L2,lo:=3452,hi:=3453); | [5 empty] | 3453:Circ16DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ16DelovnaMoc_L3,lo:=3454,hi:=3455); | [5 empty] | 3455:Circ16DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ16Frekvenca_L1,lo:=3456,hi:=3457); | [5 empty] | 3457:Circ16Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ16InduktivnaEnergija,lo:=3458,hi:=3459); | [5 empty] | 3459:Circ16InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ16InduktivnaMoc_III,lo:=3460,hi:=3461); | [5 empty] | 3461:Circ16InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ16JalovaMoc_L1,lo:=3462,hi:=3463); | [5 empty] | 3463:Circ16JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ16JalovaMoc_L2,lo:=3464,hi:=3465); | [5 empty] | 3465:Circ16JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ16JalovaMoc_L3,lo:=3466,hi:=3467); | [5 empty] | 3467:Circ16JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ16KapacitivnaEnergija,lo:=3468,hi:=3469); | [5 empty] | 3469:Circ16KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ16KapacitivnaMoc_III,lo:=3470,hi:=3471); | [5 empty] | 3471:Circ16KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ16MaximumDemand,lo:=3472,hi:=3473); | [5 empty] | 3473:Circ16MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ16Napetost_L1_L2,lo:=3474,hi:=3475); | [5 empty] | 3475:Circ16Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ16Napetost_L1_N,lo:=3476,hi:=3477); | [5 empty] | 3477:Circ16Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ16Napetost_L2_L3,lo:=3478,hi:=3479); | [5 empty] | 3479:Circ16Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ16Napetost_L2_N,lo:=3480,hi:=3481); | [5 empty] | 3481:Circ16Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ16Napetost_L3_L1,lo:=3482,hi:=3483); | [5 empty] | 3483:Circ16Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ16Napetost_L3_N,lo:=3484,hi:=3485); | [5 empty] | 3485:Circ16Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ16NavideznaMoc_III,lo:=3486,hi:=3487); | [5 empty] | 3487:Circ16NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ16NicelniTok,lo:=3488,hi:=3489); | [5 empty] | 3489:Circ16NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ16PowerFactor_III,lo:=3490,hi:=3491); | [5 empty] | 3491:Circ16PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ16PowerFactor_L1,lo:=3492,hi:=3493); | [5 empty] | 3493:Circ16PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ16PowerFactor_L2,lo:=3494,hi:=3495); | [5 empty] | 3495:Circ16PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ16PowerFactor_L3,lo:=3496,hi:=3497); | [5 empty] | 3497:Circ16PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ16THDI_L1,lo:=3498,hi:=3499); | [5 empty] | 3499:Circ16THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ16THDI_L2,lo:=3500,hi:=3501); | [5 empty] | 3501:Circ16THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ16THDI_L3,lo:=3502,hi:=3503); | [5 empty] | 3503:Circ16THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ16THDV_L1,lo:=3504,hi:=3505); | [5 empty] | 3505:Circ16THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ16THDV_L2,lo:=3506,hi:=3507); | [5 empty] | 3507:Circ16THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ16THDV_L3,lo:=3508,hi:=3509); | [5 empty] | 3509:Circ16THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ16Tok_L1,lo:=3510,hi:=3511); | [5 empty] | 3511:Circ16Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ16Tok_L2,lo:=3512,hi:=3513); | [5 empty] | 3513:Circ16Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ16Tok_L3,lo:=3514,hi:=3515); | [5 empty] | 3515:Circ16Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ16TokPovprecje_III,lo:=3516,hi:=3517); | [5 empty] | 3517:Circ16TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ17CosFi_III,lo:=3518,hi:=3519); | [5 empty] | 3519:Circ17CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ17DelovnaEnergija,lo:=3520,hi:=3521); | [5 empty] | 3521:Circ17DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ17DelovnaMoc_III,lo:=3522,hi:=3523); | [5 empty] | 3523:Circ17DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ17DelovnaMoc_L1,lo:=3524,hi:=3525); | [5 empty] | 3525:Circ17DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ17DelovnaMoc_L2,lo:=3526,hi:=3527); | [5 empty] | 3527:Circ17DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ17DelovnaMoc_L3,lo:=3528,hi:=3529); | [5 empty] | 3529:Circ17DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ17Frekvenca_L1,lo:=3530,hi:=3531); | [5 empty] | 3531:Circ17Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ17InduktivnaEnergija,lo:=3532,hi:=3533); | [5 empty] | 3533:Circ17InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ17InduktivnaMoc_III,lo:=3534,hi:=3535); | [5 empty] | 3535:Circ17InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ17JalovaMoc_L1,lo:=3536,hi:=3537); | [5 empty] | 3537:Circ17JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ17JalovaMoc_L2,lo:=3538,hi:=3539); | [5 empty] | 3539:Circ17JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ17JalovaMoc_L3,lo:=3540,hi:=3541); | [5 empty] | 3541:Circ17JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ17KapacitivnaEnergija,lo:=3542,hi:=3543); | [5 empty] | 3543:Circ17KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ17KapacitivnaMoc_III,lo:=3544,hi:=3545); | [5 empty] | 3545:Circ17KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ17MaximumDemand,lo:=3546,hi:=3547); | [5 empty] | 3547:Circ17MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ17Napetost_L1_L2,lo:=3548,hi:=3549); | [5 empty] | 3549:Circ17Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ17Napetost_L1_N,lo:=3550,hi:=3551); | [5 empty] | 3551:Circ17Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ17Napetost_L2_L3,lo:=3552,hi:=3553); | [5 empty] | 3553:Circ17Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ17Napetost_L2_N,lo:=3554,hi:=3555); | [5 empty] | 3555:Circ17Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ17Napetost_L3_L1,lo:=3556,hi:=3557); | [5 empty] | 3557:Circ17Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ17Napetost_L3_N,lo:=3558,hi:=3559); | [5 empty] | 3559:Circ17Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ17NavideznaMoc_III,lo:=3560,hi:=3561); | [5 empty] | 3561:Circ17NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ17NicelniTok,lo:=3562,hi:=3563); | [5 empty] | 3563:Circ17NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ17PowerFactor_III,lo:=3564,hi:=3565); | [5 empty] | 3565:Circ17PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ17PowerFactor_L1,lo:=3566,hi:=3567); | [5 empty] | 3567:Circ17PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ17PowerFactor_L2,lo:=3568,hi:=3569); | [5 empty] | 3569:Circ17PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ17PowerFactor_L3,lo:=3570,hi:=3571); | [5 empty] | 3571:Circ17PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ17THDI_L1,lo:=3572,hi:=3573); | [5 empty] | 3573:Circ17THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ17THDI_L2,lo:=3574,hi:=3575); | [5 empty] | 3575:Circ17THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ17THDI_L3,lo:=3576,hi:=3577); | [5 empty] | 3577:Circ17THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ17THDV_L1,lo:=3578,hi:=3579); | [5 empty] | 3579:Circ17THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ17THDV_L2,lo:=3580,hi:=3581); | [5 empty] | 3581:Circ17THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ17THDV_L3,lo:=3582,hi:=3583); | [5 empty] | 3583:Circ17THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ17Tok_L1,lo:=3584,hi:=3585); | [5 empty] | 3585:Circ17Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ17Tok_L2,lo:=3586,hi:=3587); | [5 empty] | 3587:Circ17Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ17Tok_L3,lo:=3588,hi:=3589); | [5 empty] | 3589:Circ17Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ17TokPovprecje_III,lo:=3590,hi:=3591); | [5 empty] | 3591:Circ17TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ18CosFi_III,lo:=3592,hi:=3593); | [5 empty] | 3593:Circ18CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ18DelovnaEnergija,lo:=3594,hi:=3595); | [5 empty] | 3595:Circ18DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ18DelovnaMoc_III,lo:=3596,hi:=3597); | [5 empty] | 3597:Circ18DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ18DelovnaMoc_L1,lo:=3598,hi:=3599); | [5 empty] | 3599:Circ18DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ18DelovnaMoc_L2,lo:=3600,hi:=3601); | [5 empty] | 3601:Circ18DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ18DelovnaMoc_L3,lo:=3602,hi:=3603); | [5 empty] | 3603:Circ18DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ18Frekvenca_L1,lo:=3604,hi:=3605); | [5 empty] | 3605:Circ18Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ18InduktivnaEnergija,lo:=3606,hi:=3607); | [5 empty] | 3607:Circ18InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ18InduktivnaMoc_III,lo:=3608,hi:=3609); | [5 empty] | 3609:Circ18InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ18JalovaMoc_L1,lo:=3610,hi:=3611); | [5 empty] | 3611:Circ18JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ18JalovaMoc_L2,lo:=3612,hi:=3613); | [5 empty] | 3613:Circ18JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ18JalovaMoc_L3,lo:=3614,hi:=3615); | [5 empty] | 3615:Circ18JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ18KapacitivnaEnergija,lo:=3616,hi:=3617); | [5 empty] | 3617:Circ18KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ18KapacitivnaMoc_III,lo:=3618,hi:=3619); | [5 empty] | 3619:Circ18KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ18MaximumDemand,lo:=3620,hi:=3621); | [5 empty] | 3621:Circ18MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ18Napetost_L1_L2,lo:=3622,hi:=3623); | [5 empty] | 3623:Circ18Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ18Napetost_L1_N,lo:=3624,hi:=3625); | [5 empty] | 3625:Circ18Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ18Napetost_L2_L3,lo:=3626,hi:=3627); | [5 empty] | 3627:Circ18Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ18Napetost_L2_N,lo:=3628,hi:=3629); | [5 empty] | 3629:Circ18Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ18Napetost_L3_L1,lo:=3630,hi:=3631); | [5 empty] | 3631:Circ18Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ18Napetost_L3_N,lo:=3632,hi:=3633); | [5 empty] | 3633:Circ18Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ18NavideznaMoc_III,lo:=3634,hi:=3635); | [5 empty] | 3635:Circ18NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ18NicelniTok,lo:=3636,hi:=3637); | [5 empty] | 3637:Circ18NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ18PowerFactor_III,lo:=3638,hi:=3639); | [5 empty] | 3639:Circ18PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ18PowerFactor_L1,lo:=3640,hi:=3641); | [5 empty] | 3641:Circ18PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ18PowerFactor_L2,lo:=3642,hi:=3643); | [5 empty] | 3643:Circ18PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ18PowerFactor_L3,lo:=3644,hi:=3645); | [5 empty] | 3645:Circ18PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ18THDI_L1,lo:=3646,hi:=3647); | [5 empty] | 3647:Circ18THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ18THDI_L2,lo:=3648,hi:=3649); | [5 empty] | 3649:Circ18THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ18THDI_L3,lo:=3650,hi:=3651); | [5 empty] | 3651:Circ18THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ18THDV_L1,lo:=3652,hi:=3653); | [5 empty] | 3653:Circ18THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ18THDV_L2,lo:=3654,hi:=3655); | [5 empty] | 3655:Circ18THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ18THDV_L3,lo:=3656,hi:=3657); | [5 empty] | 3657:Circ18THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ18Tok_L1,lo:=3658,hi:=3659); | [5 empty] | 3659:Circ18Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ18Tok_L2,lo:=3660,hi:=3661); | [5 empty] | 3661:Circ18Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ18Tok_L3,lo:=3662,hi:=3663); | [5 empty] | 3663:Circ18Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ18TokPovprecje_III,lo:=3664,hi:=3665); | [5 empty] | 3665:Circ18TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ19CosFi_III,lo:=3666,hi:=3667); | [5 empty] | 3667:Circ19CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ19DelovnaEnergija,lo:=3668,hi:=3669); | [5 empty] | 3669:Circ19DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ19DelovnaMoc_III,lo:=3670,hi:=3671); | [5 empty] | 3671:Circ19DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ19DelovnaMoc_L1,lo:=3672,hi:=3673); | [5 empty] | 3673:Circ19DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ19DelovnaMoc_L2,lo:=3674,hi:=3675); | [5 empty] | 3675:Circ19DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ19DelovnaMoc_L3,lo:=3676,hi:=3677); | [5 empty] | 3677:Circ19DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ19Frekvenca_L1,lo:=3678,hi:=3679); | [5 empty] | 3679:Circ19Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ19InduktivnaEnergija,lo:=3680,hi:=3681); | [5 empty] | 3681:Circ19InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ19InduktivnaMoc_III,lo:=3682,hi:=3683); | [5 empty] | 3683:Circ19InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ19JalovaMoc_L1,lo:=3684,hi:=3685); | [5 empty] | 3685:Circ19JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ19JalovaMoc_L2,lo:=3686,hi:=3687); | [5 empty] | 3687:Circ19JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ19JalovaMoc_L3,lo:=3688,hi:=3689); | [5 empty] | 3689:Circ19JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ19KapacitivnaEnergija,lo:=3690,hi:=3691); | [5 empty] | 3691:Circ19KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ19KapacitivnaMoc_III,lo:=3692,hi:=3693); | [5 empty] | 3693:Circ19KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ19MaximumDemand,lo:=3694,hi:=3695); | [5 empty] | 3695:Circ19MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ19Napetost_L1_L2,lo:=3696,hi:=3697); | [5 empty] | 3697:Circ19Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ19Napetost_L1_N,lo:=3698,hi:=3699); | [5 empty] | 3699:Circ19Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ19Napetost_L2_L3,lo:=3700,hi:=3701); | [5 empty] | 3701:Circ19Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ19Napetost_L2_N,lo:=3702,hi:=3703); | [5 empty] | 3703:Circ19Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ19Napetost_L3_L1,lo:=3704,hi:=3705); | [5 empty] | 3705:Circ19Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ19Napetost_L3_N,lo:=3706,hi:=3707); | [5 empty] | 3707:Circ19Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ19NavideznaMoc_III,lo:=3708,hi:=3709); | [5 empty] | 3709:Circ19NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ19NicelniTok,lo:=3710,hi:=3711); | [5 empty] | 3711:Circ19NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ19PowerFactor_III,lo:=3712,hi:=3713); | [5 empty] | 3713:Circ19PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ19PowerFactor_L1,lo:=3714,hi:=3715); | [5 empty] | 3715:Circ19PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ19PowerFactor_L2,lo:=3716,hi:=3717); | [5 empty] | 3717:Circ19PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ19PowerFactor_L3,lo:=3718,hi:=3719); | [5 empty] | 3719:Circ19PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ19THDI_L1,lo:=3720,hi:=3721); | [5 empty] | 3721:Circ19THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ19THDI_L2,lo:=3722,hi:=3723); | [5 empty] | 3723:Circ19THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ19THDI_L3,lo:=3724,hi:=3725); | [5 empty] | 3725:Circ19THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ19THDV_L1,lo:=3726,hi:=3727); | [5 empty] | 3727:Circ19THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ19THDV_L2,lo:=3728,hi:=3729); | [5 empty] | 3729:Circ19THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ19THDV_L3,lo:=3730,hi:=3731); | [5 empty] | 3731:Circ19THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ19Tok_L1,lo:=3732,hi:=3733); | [5 empty] | 3733:Circ19Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ19Tok_L2,lo:=3734,hi:=3735); | [5 empty] | 3735:Circ19Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ19Tok_L3,lo:=3736,hi:=3737); | [5 empty] | 3737:Circ19Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ19TokPovprecje_III,lo:=3738,hi:=3739); | [5 empty] | 3739:Circ19TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ1CosFi_III,lo:=3740,hi:=3741); | [5 empty] | 3741:Circ1CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ1DelovnaEnergija,lo:=3742,hi:=3743); | [5 empty] | 3743:Circ1DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ1DelovnaMoc_III,lo:=3744,hi:=3745); | [5 empty] | 3745:Circ1DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ1DelovnaMoc_L1,lo:=3746,hi:=3747); | [5 empty] | 3747:Circ1DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ1DelovnaMoc_L2,lo:=3748,hi:=3749); | [5 empty] | 3749:Circ1DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ1DelovnaMoc_L3,lo:=3750,hi:=3751); | [5 empty] | 3751:Circ1DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ1Frekvenca_L1,lo:=3752,hi:=3753); | [5 empty] | 3753:Circ1Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ1InduktivnaEnergija,lo:=3754,hi:=3755); | [5 empty] | 3755:Circ1InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ1InduktivnaMoc_III,lo:=3756,hi:=3757); | [5 empty] | 3757:Circ1InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ1JalovaMoc_L1,lo:=3758,hi:=3759); | [5 empty] | 3759:Circ1JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ1JalovaMoc_L2,lo:=3760,hi:=3761); | [5 empty] | 3761:Circ1JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ1JalovaMoc_L3,lo:=3762,hi:=3763); | [5 empty] | 3763:Circ1JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ1KapacitivnaEnergija,lo:=3764,hi:=3765); | [5 empty] | 3765:Circ1KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ1KapacitivnaMoc_III,lo:=3766,hi:=3767); | [5 empty] | 3767:Circ1KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ1MaximumDemand,lo:=3768,hi:=3769); | [5 empty] | 3769:Circ1MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ1Napetost_L1_L2,lo:=3770,hi:=3771); | [5 empty] | 3771:Circ1Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ1Napetost_L1_N,lo:=3772,hi:=3773); | [5 empty] | 3773:Circ1Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ1Napetost_L2_L3,lo:=3774,hi:=3775); | [5 empty] | 3775:Circ1Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ1Napetost_L2_N,lo:=3776,hi:=3777); | [5 empty] | 3777:Circ1Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ1Napetost_L3_L1,lo:=3778,hi:=3779); | [5 empty] | 3779:Circ1Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ1Napetost_L3_N,lo:=3780,hi:=3781); | [5 empty] | 3781:Circ1Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ1NavideznaMoc_III,lo:=3782,hi:=3783); | [5 empty] | 3783:Circ1NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ1NicelniTok,lo:=3784,hi:=3785); | [5 empty] | 3785:Circ1NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ1PowerFactor_III,lo:=3786,hi:=3787); | [5 empty] | 3787:Circ1PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ1PowerFactor_L1,lo:=3788,hi:=3789); | [5 empty] | 3789:Circ1PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ1PowerFactor_L2,lo:=3790,hi:=3791); | [5 empty] | 3791:Circ1PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ1PowerFactor_L3,lo:=3792,hi:=3793); | [5 empty] | 3793:Circ1PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ1THDI_L1,lo:=3794,hi:=3795); | [5 empty] | 3795:Circ1THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ1THDI_L2,lo:=3796,hi:=3797); | [5 empty] | 3797:Circ1THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ1THDI_L3,lo:=3798,hi:=3799); | [5 empty] | 3799:Circ1THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ1THDV_L1,lo:=3800,hi:=3801); | [5 empty] | 3801:Circ1THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ1THDV_L2,lo:=3802,hi:=3803); | [5 empty] | 3803:Circ1THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ1THDV_L3,lo:=3804,hi:=3805); | [5 empty] | 3805:Circ1THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ1Tok_L1,lo:=3806,hi:=3807); | [5 empty] | 3807:Circ1Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ1Tok_L2,lo:=3808,hi:=3809); | [5 empty] | 3809:Circ1Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ1Tok_L3,lo:=3810,hi:=3811); | [5 empty] | 3811:Circ1Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ1TokPovprecje_III,lo:=3812,hi:=3813); | [5 empty] | 3813:Circ1TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ20CosFi_III,lo:=3814,hi:=3815); | [5 empty] | 3815:Circ20CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ20DelovnaEnergija,lo:=3816,hi:=3817); | [5 empty] | 3817:Circ20DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ20DelovnaMoc_III,lo:=3818,hi:=3819); | [5 empty] | 3819:Circ20DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ20DelovnaMoc_L1,lo:=3820,hi:=3821); | [5 empty] | 3821:Circ20DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ20DelovnaMoc_L2,lo:=3822,hi:=3823); | [5 empty] | 3823:Circ20DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ20DelovnaMoc_L3,lo:=3824,hi:=3825); | [5 empty] | 3825:Circ20DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ20Frekvenca_L1,lo:=3826,hi:=3827); | [5 empty] | 3827:Circ20Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ20InduktivnaEnergija,lo:=3828,hi:=3829); | [5 empty] | 3829:Circ20InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ20InduktivnaMoc_III,lo:=3830,hi:=3831); | [5 empty] | 3831:Circ20InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ20JalovaMoc_L1,lo:=3832,hi:=3833); | [5 empty] | 3833:Circ20JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ20JalovaMoc_L2,lo:=3834,hi:=3835); | [5 empty] | 3835:Circ20JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ20JalovaMoc_L3,lo:=3836,hi:=3837); | [5 empty] | 3837:Circ20JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ20KapacitivnaEnergija,lo:=3838,hi:=3839); | [5 empty] | 3839:Circ20KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ20KapacitivnaMoc_III,lo:=3840,hi:=3841); | [5 empty] | 3841:Circ20KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ20MaximumDemand,lo:=3842,hi:=3843); | [5 empty] | 3843:Circ20MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ20Napetost_L1_L2,lo:=3844,hi:=3845); | [5 empty] | 3845:Circ20Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ20Napetost_L1_N,lo:=3846,hi:=3847); | [5 empty] | 3847:Circ20Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ20Napetost_L2_L3,lo:=3848,hi:=3849); | [5 empty] | 3849:Circ20Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ20Napetost_L2_N,lo:=3850,hi:=3851); | [5 empty] | 3851:Circ20Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ20Napetost_L3_L1,lo:=3852,hi:=3853); | [5 empty] | 3853:Circ20Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ20Napetost_L3_N,lo:=3854,hi:=3855); | [5 empty] | 3855:Circ20Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ20NavideznaMoc_III,lo:=3856,hi:=3857); | [5 empty] | 3857:Circ20NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ20NicelniTok,lo:=3858,hi:=3859); | [5 empty] | 3859:Circ20NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ20PowerFactor_III,lo:=3860,hi:=3861); | [5 empty] | 3861:Circ20PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ20PowerFactor_L1,lo:=3862,hi:=3863); | [5 empty] | 3863:Circ20PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ20PowerFactor_L2,lo:=3864,hi:=3865); | [5 empty] | 3865:Circ20PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ20PowerFactor_L3,lo:=3866,hi:=3867); | [5 empty] | 3867:Circ20PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ20THDI_L1,lo:=3868,hi:=3869); | [5 empty] | 3869:Circ20THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ20THDI_L2,lo:=3870,hi:=3871); | [5 empty] | 3871:Circ20THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ20THDI_L3,lo:=3872,hi:=3873); | [5 empty] | 3873:Circ20THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ20THDV_L1,lo:=3874,hi:=3875); | [5 empty] | 3875:Circ20THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ20THDV_L2,lo:=3876,hi:=3877); | [5 empty] | 3877:Circ20THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ20THDV_L3,lo:=3878,hi:=3879); | [5 empty] | 3879:Circ20THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ20Tok_L1,lo:=3880,hi:=3881); | [5 empty] | 3881:Circ20Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ20Tok_L2,lo:=3882,hi:=3883); | [5 empty] | 3883:Circ20Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ20Tok_L3,lo:=3884,hi:=3885); | [5 empty] | 3885:Circ20Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ20TokPovprecje_III,lo:=3886,hi:=3887); | [5 empty] | 3887:Circ20TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ21CosFi_III,lo:=3888,hi:=3889); | [5 empty] | 3889:Circ21CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ21DelovnaEnergija,lo:=3890,hi:=3891); | [5 empty] | 3891:Circ21DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ21DelovnaMoc_III,lo:=3892,hi:=3893); | [5 empty] | 3893:Circ21DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ21DelovnaMoc_L1,lo:=3894,hi:=3895); | [5 empty] | 3895:Circ21DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ21DelovnaMoc_L2,lo:=3896,hi:=3897); | [5 empty] | 3897:Circ21DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ21DelovnaMoc_L3,lo:=3898,hi:=3899); | [5 empty] | 3899:Circ21DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ21Frekvenca_L1,lo:=3900,hi:=3901); | [5 empty] | 3901:Circ21Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ21InduktivnaEnergija,lo:=3902,hi:=3903); | [5 empty] | 3903:Circ21InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ21InduktivnaMoc_III,lo:=3904,hi:=3905); | [5 empty] | 3905:Circ21InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ21JalovaMoc_L1,lo:=3906,hi:=3907); | [5 empty] | 3907:Circ21JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ21JalovaMoc_L2,lo:=3908,hi:=3909); | [5 empty] | 3909:Circ21JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ21JalovaMoc_L3,lo:=3910,hi:=3911); | [5 empty] | 3911:Circ21JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ21KapacitivnaEnergija,lo:=3912,hi:=3913); | [5 empty] | 3913:Circ21KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ21KapacitivnaMoc_III,lo:=3914,hi:=3915); | [5 empty] | 3915:Circ21KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ21MaximumDemand,lo:=3916,hi:=3917); | [5 empty] | 3917:Circ21MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ21Napetost_L1_L2,lo:=3918,hi:=3919); | [5 empty] | 3919:Circ21Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ21Napetost_L1_N,lo:=3920,hi:=3921); | [5 empty] | 3921:Circ21Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ21Napetost_L2_L3,lo:=3922,hi:=3923); | [5 empty] | 3923:Circ21Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ21Napetost_L2_N,lo:=3924,hi:=3925); | [5 empty] | 3925:Circ21Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ21Napetost_L3_L1,lo:=3926,hi:=3927); | [5 empty] | 3927:Circ21Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ21Napetost_L3_N,lo:=3928,hi:=3929); | [5 empty] | 3929:Circ21Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ21NavideznaMoc_III,lo:=3930,hi:=3931); | [5 empty] | 3931:Circ21NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ21NicelniTok,lo:=3932,hi:=3933); | [5 empty] | 3933:Circ21NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ21PowerFactor_III,lo:=3934,hi:=3935); | [5 empty] | 3935:Circ21PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ21PowerFactor_L1,lo:=3936,hi:=3937); | [5 empty] | 3937:Circ21PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ21PowerFactor_L2,lo:=3938,hi:=3939); | [5 empty] | 3939:Circ21PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ21PowerFactor_L3,lo:=3940,hi:=3941); | [5 empty] | 3941:Circ21PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ21THDI_L1,lo:=3942,hi:=3943); | [5 empty] | 3943:Circ21THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ21THDI_L2,lo:=3944,hi:=3945); | [5 empty] | 3945:Circ21THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ21THDI_L3,lo:=3946,hi:=3947); | [5 empty] | 3947:Circ21THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ21THDV_L1,lo:=3948,hi:=3949); | [5 empty] | 3949:Circ21THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ21THDV_L2,lo:=3950,hi:=3951); | [5 empty] | 3951:Circ21THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ21THDV_L3,lo:=3952,hi:=3953); | [5 empty] | 3953:Circ21THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ21Tok_L1,lo:=3954,hi:=3955); | [5 empty] | 3955:Circ21Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ21Tok_L2,lo:=3956,hi:=3957); | [5 empty] | 3957:Circ21Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ21Tok_L3,lo:=3958,hi:=3959); | [5 empty] | 3959:Circ21Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ21TokPovprecje_III,lo:=3960,hi:=3961); | [5 empty] | 3961:Circ21TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ22CosFi_III,lo:=3962,hi:=3963); | [5 empty] | 3963:Circ22CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ22DelovnaEnergija,lo:=3964,hi:=3965); | [5 empty] | 3965:Circ22DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ22DelovnaMoc_III,lo:=3966,hi:=3967); | [5 empty] | 3967:Circ22DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ22DelovnaMoc_L1,lo:=3968,hi:=3969); | [5 empty] | 3969:Circ22DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ22DelovnaMoc_L2,lo:=3970,hi:=3971); | [5 empty] | 3971:Circ22DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ22DelovnaMoc_L3,lo:=3972,hi:=3973); | [5 empty] | 3973:Circ22DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ22Frekvenca_L1,lo:=3974,hi:=3975); | [5 empty] | 3975:Circ22Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ22InduktivnaEnergija,lo:=3976,hi:=3977); | [5 empty] | 3977:Circ22InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ22InduktivnaMoc_III,lo:=3978,hi:=3979); | [5 empty] | 3979:Circ22InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ22JalovaMoc_L1,lo:=3980,hi:=3981); | [5 empty] | 3981:Circ22JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ22JalovaMoc_L2,lo:=3982,hi:=3983); | [5 empty] | 3983:Circ22JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ22JalovaMoc_L3,lo:=3984,hi:=3985); | [5 empty] | 3985:Circ22JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ22KapacitivnaEnergija,lo:=3986,hi:=3987); | [5 empty] | 3987:Circ22KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ22KapacitivnaMoc_III,lo:=3988,hi:=3989); | [5 empty] | 3989:Circ22KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ22MaximumDemand,lo:=3990,hi:=3991); | [5 empty] | 3991:Circ22MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ22Napetost_L1_L2,lo:=3992,hi:=3993); | [5 empty] | 3993:Circ22Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ22Napetost_L1_N,lo:=3994,hi:=3995); | [5 empty] | 3995:Circ22Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ22Napetost_L2_L3,lo:=3996,hi:=3997); | [5 empty] | 3997:Circ22Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ22Napetost_L2_N,lo:=3998,hi:=3999); | [5 empty] | 3999:Circ22Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ22Napetost_L3_L1,lo:=4000,hi:=4001); | [5 empty] | 4001:Circ22Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ22Napetost_L3_N,lo:=4002,hi:=4003); | [5 empty] | 4003:Circ22Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ22NavideznaMoc_III,lo:=4004,hi:=4005); | [5 empty] | 4005:Circ22NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ22NicelniTok,lo:=4006,hi:=4007); | [5 empty] | 4007:Circ22NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ22PowerFactor_III,lo:=4008,hi:=4009); | [5 empty] | 4009:Circ22PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ22PowerFactor_L1,lo:=4010,hi:=4011); | [5 empty] | 4011:Circ22PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ22PowerFactor_L2,lo:=4012,hi:=4013); | [5 empty] | 4013:Circ22PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ22PowerFactor_L3,lo:=4014,hi:=4015); | [5 empty] | 4015:Circ22PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ22THDI_L1,lo:=4016,hi:=4017); | [5 empty] | 4017:Circ22THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ22THDI_L2,lo:=4018,hi:=4019); | [5 empty] | 4019:Circ22THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ22THDI_L3,lo:=4020,hi:=4021); | [5 empty] | 4021:Circ22THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ22THDV_L1,lo:=4022,hi:=4023); | [5 empty] | 4023:Circ22THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ22THDV_L2,lo:=4024,hi:=4025); | [5 empty] | 4025:Circ22THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ22THDV_L3,lo:=4026,hi:=4027); | [5 empty] | 4027:Circ22THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ22Tok_L1,lo:=4028,hi:=4029); | [5 empty] | 4029:Circ22Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ22Tok_L2,lo:=4030,hi:=4031); | [5 empty] | 4031:Circ22Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ22Tok_L3,lo:=4032,hi:=4033); | [5 empty] | 4033:Circ22Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ22TokPovprecje_III,lo:=4034,hi:=4035); | [5 empty] | 4035:Circ22TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ23CosFi_III,lo:=4036,hi:=4037); | [5 empty] | 4037:Circ23CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ23DelovnaEnergija,lo:=4038,hi:=4039); | [5 empty] | 4039:Circ23DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ23DelovnaMoc_III,lo:=4040,hi:=4041); | [5 empty] | 4041:Circ23DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ23DelovnaMoc_L1,lo:=4042,hi:=4043); | [5 empty] | 4043:Circ23DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ23DelovnaMoc_L2,lo:=4044,hi:=4045); | [5 empty] | 4045:Circ23DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ23DelovnaMoc_L3,lo:=4046,hi:=4047); | [5 empty] | 4047:Circ23DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ23Frekvenca_L1,lo:=4048,hi:=4049); | [5 empty] | 4049:Circ23Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ23InduktivnaEnergija,lo:=4050,hi:=4051); | [5 empty] | 4051:Circ23InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ23InduktivnaMoc_III,lo:=4052,hi:=4053); | [5 empty] | 4053:Circ23InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ23JalovaMoc_L1,lo:=4054,hi:=4055); | [5 empty] | 4055:Circ23JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ23JalovaMoc_L2,lo:=4056,hi:=4057); | [5 empty] | 4057:Circ23JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ23JalovaMoc_L3,lo:=4058,hi:=4059); | [5 empty] | 4059:Circ23JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ23KapacitivnaEnergija,lo:=4060,hi:=4061); | [5 empty] | 4061:Circ23KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ23KapacitivnaMoc_III,lo:=4062,hi:=4063); | [5 empty] | 4063:Circ23KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ23MaximumDemand,lo:=4064,hi:=4065); | [5 empty] | 4065:Circ23MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ23Napetost_L1_L2,lo:=4066,hi:=4067); | [5 empty] | 4067:Circ23Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ23Napetost_L1_N,lo:=4068,hi:=4069); | [5 empty] | 4069:Circ23Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ23Napetost_L2_L3,lo:=4070,hi:=4071); | [5 empty] | 4071:Circ23Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ23Napetost_L2_N,lo:=4072,hi:=4073); | [5 empty] | 4073:Circ23Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ23Napetost_L3_L1,lo:=4074,hi:=4075); | [5 empty] | 4075:Circ23Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ23Napetost_L3_N,lo:=4076,hi:=4077); | [5 empty] | 4077:Circ23Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ23NavideznaMoc_III,lo:=4078,hi:=4079); | [5 empty] | 4079:Circ23NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ23NicelniTok,lo:=4080,hi:=4081); | [5 empty] | 4081:Circ23NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ23PowerFactor_III,lo:=4082,hi:=4083); | [5 empty] | 4083:Circ23PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ23PowerFactor_L1,lo:=4084,hi:=4085); | [5 empty] | 4085:Circ23PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ23PowerFactor_L2,lo:=4086,hi:=4087); | [5 empty] | 4087:Circ23PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ23PowerFactor_L3,lo:=4088,hi:=4089); | [5 empty] | 4089:Circ23PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ23THDI_L1,lo:=4090,hi:=4091); | [5 empty] | 4091:Circ23THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ23THDI_L2,lo:=4092,hi:=4093); | [5 empty] | 4093:Circ23THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ23THDI_L3,lo:=4094,hi:=4095); | [5 empty] | 4095:Circ23THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ23THDV_L1,lo:=4096,hi:=4097); | [5 empty] | 4097:Circ23THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ23THDV_L2,lo:=4098,hi:=4099); | [5 empty] | 4099:Circ23THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ23THDV_L3,lo:=4100,hi:=4101); | [5 empty] | 4101:Circ23THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ23Tok_L1,lo:=4102,hi:=4103); | [5 empty] | 4103:Circ23Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ23Tok_L2,lo:=4104,hi:=4105); | [5 empty] | 4105:Circ23Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ23Tok_L3,lo:=4106,hi:=4107); | [5 empty] | 4107:Circ23Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ23TokPovprecje_III,lo:=4108,hi:=4109); | [5 empty] | 4109:Circ23TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ24CosFi_III,lo:=4110,hi:=4111); | [5 empty] | 4111:Circ24CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ24DelovnaEnergija,lo:=4112,hi:=4113); | [5 empty] | 4113:Circ24DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ24DelovnaMoc_III,lo:=4114,hi:=4115); | [5 empty] | 4115:Circ24DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ24DelovnaMoc_L1,lo:=4116,hi:=4117); | [5 empty] | 4117:Circ24DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ24DelovnaMoc_L2,lo:=4118,hi:=4119); | [5 empty] | 4119:Circ24DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ24DelovnaMoc_L3,lo:=4120,hi:=4121); | [5 empty] | 4121:Circ24DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ24Frekvenca_L1,lo:=4122,hi:=4123); | [5 empty] | 4123:Circ24Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ24InduktivnaEnergija,lo:=4124,hi:=4125); | [5 empty] | 4125:Circ24InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ24InduktivnaMoc_III,lo:=4126,hi:=4127); | [5 empty] | 4127:Circ24InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ24JalovaMoc_L1,lo:=4128,hi:=4129); | [5 empty] | 4129:Circ24JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ24JalovaMoc_L2,lo:=4130,hi:=4131); | [5 empty] | 4131:Circ24JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ24JalovaMoc_L3,lo:=4132,hi:=4133); | [5 empty] | 4133:Circ24JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ24KapacitivnaEnergija,lo:=4134,hi:=4135); | [5 empty] | 4135:Circ24KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ24KapacitivnaMoc_III,lo:=4136,hi:=4137); | [5 empty] | 4137:Circ24KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ24MaximumDemand,lo:=4138,hi:=4139); | [5 empty] | 4139:Circ24MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ24Napetost_L1_L2,lo:=4140,hi:=4141); | [5 empty] | 4141:Circ24Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ24Napetost_L1_N,lo:=4142,hi:=4143); | [5 empty] | 4143:Circ24Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ24Napetost_L2_L3,lo:=4144,hi:=4145); | [5 empty] | 4145:Circ24Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ24Napetost_L2_N,lo:=4146,hi:=4147); | [5 empty] | 4147:Circ24Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ24Napetost_L3_L1,lo:=4148,hi:=4149); | [5 empty] | 4149:Circ24Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ24Napetost_L3_N,lo:=4150,hi:=4151); | [5 empty] | 4151:Circ24Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ24NavideznaMoc_III,lo:=4152,hi:=4153); | [5 empty] | 4153:Circ24NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ24NicelniTok,lo:=4154,hi:=4155); | [5 empty] | 4155:Circ24NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ24PowerFactor_III,lo:=4156,hi:=4157); | [5 empty] | 4157:Circ24PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ24PowerFactor_L1,lo:=4158,hi:=4159); | [5 empty] | 4159:Circ24PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ24PowerFactor_L2,lo:=4160,hi:=4161); | [5 empty] | 4161:Circ24PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ24PowerFactor_L3,lo:=4162,hi:=4163); | [5 empty] | 4163:Circ24PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ24THDI_L1,lo:=4164,hi:=4165); | [5 empty] | 4165:Circ24THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ24THDI_L2,lo:=4166,hi:=4167); | [5 empty] | 4167:Circ24THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ24THDI_L3,lo:=4168,hi:=4169); | [5 empty] | 4169:Circ24THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ24THDV_L1,lo:=4170,hi:=4171); | [5 empty] | 4171:Circ24THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ24THDV_L2,lo:=4172,hi:=4173); | [5 empty] | 4173:Circ24THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ24THDV_L3,lo:=4174,hi:=4175); | [5 empty] | 4175:Circ24THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ24Tok_L1,lo:=4176,hi:=4177); | [5 empty] | 4177:Circ24Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ24Tok_L2,lo:=4178,hi:=4179); | [5 empty] | 4179:Circ24Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ24Tok_L3,lo:=4180,hi:=4181); | [5 empty] | 4181:Circ24Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ24TokPovprecje_III,lo:=4182,hi:=4183); | [5 empty] | 4183:Circ24TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ25CosFi_III,lo:=4184,hi:=4185); | [5 empty] | 4185:Circ25CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ25DelovnaEnergija,lo:=4186,hi:=4187); | [5 empty] | 4187:Circ25DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ25DelovnaMoc_III,lo:=4188,hi:=4189); | [5 empty] | 4189:Circ25DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ25DelovnaMoc_L1,lo:=4190,hi:=4191); | [5 empty] | 4191:Circ25DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ25DelovnaMoc_L2,lo:=4192,hi:=4193); | [5 empty] | 4193:Circ25DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ25DelovnaMoc_L3,lo:=4194,hi:=4195); | [5 empty] | 4195:Circ25DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ25Frekvenca_L1,lo:=4196,hi:=4197); | [5 empty] | 4197:Circ25Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ25InduktivnaEnergija,lo:=4198,hi:=4199); | [5 empty] | 4199:Circ25InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ25InduktivnaMoc_III,lo:=4200,hi:=4201); | [5 empty] | 4201:Circ25InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ25JalovaMoc_L1,lo:=4202,hi:=4203); | [5 empty] | 4203:Circ25JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ25JalovaMoc_L2,lo:=4204,hi:=4205); | [5 empty] | 4205:Circ25JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ25JalovaMoc_L3,lo:=4206,hi:=4207); | [5 empty] | 4207:Circ25JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ25KapacitivnaEnergija,lo:=4208,hi:=4209); | [5 empty] | 4209:Circ25KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ25KapacitivnaMoc_III,lo:=4210,hi:=4211); | [5 empty] | 4211:Circ25KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ25MaximumDemand,lo:=4212,hi:=4213); | [5 empty] | 4213:Circ25MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ25Napetost_L1_L2,lo:=4214,hi:=4215); | [5 empty] | 4215:Circ25Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ25Napetost_L1_N,lo:=4216,hi:=4217); | [5 empty] | 4217:Circ25Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ25Napetost_L2_L3,lo:=4218,hi:=4219); | [5 empty] | 4219:Circ25Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ25Napetost_L2_N,lo:=4220,hi:=4221); | [5 empty] | 4221:Circ25Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ25Napetost_L3_L1,lo:=4222,hi:=4223); | [5 empty] | 4223:Circ25Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ25Napetost_L3_N,lo:=4224,hi:=4225); | [5 empty] | 4225:Circ25Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ25NavideznaMoc_III,lo:=4226,hi:=4227); | [5 empty] | 4227:Circ25NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ25NicelniTok,lo:=4228,hi:=4229); | [5 empty] | 4229:Circ25NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ25PowerFactor_III,lo:=4230,hi:=4231); | [5 empty] | 4231:Circ25PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ25PowerFactor_L1,lo:=4232,hi:=4233); | [5 empty] | 4233:Circ25PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ25PowerFactor_L2,lo:=4234,hi:=4235); | [5 empty] | 4235:Circ25PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ25PowerFactor_L3,lo:=4236,hi:=4237); | [5 empty] | 4237:Circ25PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ25THDI_L1,lo:=4238,hi:=4239); | [5 empty] | 4239:Circ25THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ25THDI_L2,lo:=4240,hi:=4241); | [5 empty] | 4241:Circ25THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ25THDI_L3,lo:=4242,hi:=4243); | [5 empty] | 4243:Circ25THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ25THDV_L1,lo:=4244,hi:=4245); | [5 empty] | 4245:Circ25THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ25THDV_L2,lo:=4246,hi:=4247); | [5 empty] | 4247:Circ25THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ25THDV_L3,lo:=4248,hi:=4249); | [5 empty] | 4249:Circ25THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ25Tok_L1,lo:=4250,hi:=4251); | [5 empty] | 4251:Circ25Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ25Tok_L2,lo:=4252,hi:=4253); | [5 empty] | 4253:Circ25Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ25Tok_L3,lo:=4254,hi:=4255); | [5 empty] | 4255:Circ25Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ25TokPovprecje_III,lo:=4256,hi:=4257); | [5 empty] | 4257:Circ25TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ2CosFi_III,lo:=4258,hi:=4259); | [5 empty] | 4259:Circ2CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ2DelovnaEnergija,lo:=4260,hi:=4261); | [5 empty] | 4261:Circ2DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ2DelovnaMoc_III,lo:=4262,hi:=4263); | [5 empty] | 4263:Circ2DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ2DelovnaMoc_L1,lo:=4264,hi:=4265); | [5 empty] | 4265:Circ2DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ2DelovnaMoc_L2,lo:=4266,hi:=4267); | [5 empty] | 4267:Circ2DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ2DelovnaMoc_L3,lo:=4268,hi:=4269); | [5 empty] | 4269:Circ2DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ2Frekvenca_L1,lo:=4270,hi:=4271); | [5 empty] | 4271:Circ2Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ2InduktivnaEnergija,lo:=4272,hi:=4273); | [5 empty] | 4273:Circ2InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ2InduktivnaMoc_III,lo:=4274,hi:=4275); | [5 empty] | 4275:Circ2InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ2JalovaMoc_L1,lo:=4276,hi:=4277); | [5 empty] | 4277:Circ2JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ2JalovaMoc_L2,lo:=4278,hi:=4279); | [5 empty] | 4279:Circ2JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ2JalovaMoc_L3,lo:=4280,hi:=4281); | [5 empty] | 4281:Circ2JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ2KapacitivnaEnergija,lo:=4282,hi:=4283); | [5 empty] | 4283:Circ2KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ2KapacitivnaMoc_III,lo:=4284,hi:=4285); | [5 empty] | 4285:Circ2KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ2MaximumDemand,lo:=4286,hi:=4287); | [5 empty] | 4287:Circ2MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ2Napetost_L1_L2,lo:=4288,hi:=4289); | [5 empty] | 4289:Circ2Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ2Napetost_L1_N,lo:=4290,hi:=4291); | [5 empty] | 4291:Circ2Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ2Napetost_L2_L3,lo:=4292,hi:=4293); | [5 empty] | 4293:Circ2Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ2Napetost_L2_N,lo:=4294,hi:=4295); | [5 empty] | 4295:Circ2Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ2Napetost_L3_L1,lo:=4296,hi:=4297); | [5 empty] | 4297:Circ2Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ2Napetost_L3_N,lo:=4298,hi:=4299); | [5 empty] | 4299:Circ2Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ2NavideznaMoc_III,lo:=4300,hi:=4301); | [5 empty] | 4301:Circ2NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ2NicelniTok,lo:=4302,hi:=4303); | [5 empty] | 4303:Circ2NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ2PowerFactor_III,lo:=4304,hi:=4305); | [5 empty] | 4305:Circ2PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ2PowerFactor_L1,lo:=4306,hi:=4307); | [5 empty] | 4307:Circ2PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ2PowerFactor_L2,lo:=4308,hi:=4309); | [5 empty] | 4309:Circ2PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ2PowerFactor_L3,lo:=4310,hi:=4311); | [5 empty] | 4311:Circ2PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ2THDI_L1,lo:=4312,hi:=4313); | [5 empty] | 4313:Circ2THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ2THDI_L2,lo:=4314,hi:=4315); | [5 empty] | 4315:Circ2THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ2THDI_L3,lo:=4316,hi:=4317); | [5 empty] | 4317:Circ2THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ2THDV_L1,lo:=4318,hi:=4319); | [5 empty] | 4319:Circ2THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ2THDV_L2,lo:=4320,hi:=4321); | [5 empty] | 4321:Circ2THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ2THDV_L3,lo:=4322,hi:=4323); | [5 empty] | 4323:Circ2THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ2Tok_L1,lo:=4324,hi:=4325); | [5 empty] | 4325:Circ2Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ2Tok_L2,lo:=4326,hi:=4327); | [5 empty] | 4327:Circ2Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ2Tok_L3,lo:=4328,hi:=4329); | [5 empty] | 4329:Circ2Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ2TokPovprecje_III,lo:=4330,hi:=4331); | [5 empty] | 4331:Circ2TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ3CosFi_III,lo:=4332,hi:=4333); | [5 empty] | 4333:Circ3CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ3DelovnaEnergija,lo:=4334,hi:=4335); | [5 empty] | 4335:Circ3DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ3DelovnaMoc_III,lo:=4336,hi:=4337); | [5 empty] | 4337:Circ3DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ3DelovnaMoc_L1,lo:=4338,hi:=4339); | [5 empty] | 4339:Circ3DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ3DelovnaMoc_L2,lo:=4340,hi:=4341); | [5 empty] | 4341:Circ3DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ3DelovnaMoc_L3,lo:=4342,hi:=4343); | [5 empty] | 4343:Circ3DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ3Frekvenca_L1,lo:=4344,hi:=4345); | [5 empty] | 4345:Circ3Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ3InduktivnaEnergija,lo:=4346,hi:=4347); | [5 empty] | 4347:Circ3InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ3InduktivnaMoc_III,lo:=4348,hi:=4349); | [5 empty] | 4349:Circ3InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ3JalovaMoc_L1,lo:=4350,hi:=4351); | [5 empty] | 4351:Circ3JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ3JalovaMoc_L2,lo:=4352,hi:=4353); | [5 empty] | 4353:Circ3JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ3JalovaMoc_L3,lo:=4354,hi:=4355); | [5 empty] | 4355:Circ3JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ3KapacitivnaEnergija,lo:=4356,hi:=4357); | [5 empty] | 4357:Circ3KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ3KapacitivnaMoc_III,lo:=4358,hi:=4359); | [5 empty] | 4359:Circ3KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ3MaximumDemand,lo:=4360,hi:=4361); | [5 empty] | 4361:Circ3MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ3Napetost_L1_L2,lo:=4362,hi:=4363); | [5 empty] | 4363:Circ3Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ3Napetost_L1_N,lo:=4364,hi:=4365); | [5 empty] | 4365:Circ3Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ3Napetost_L2_L3,lo:=4366,hi:=4367); | [5 empty] | 4367:Circ3Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ3Napetost_L2_N,lo:=4368,hi:=4369); | [5 empty] | 4369:Circ3Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ3Napetost_L3_L1,lo:=4370,hi:=4371); | [5 empty] | 4371:Circ3Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ3Napetost_L3_N,lo:=4372,hi:=4373); | [5 empty] | 4373:Circ3Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ3NavideznaMoc_III,lo:=4374,hi:=4375); | [5 empty] | 4375:Circ3NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ3NicelniTok,lo:=4376,hi:=4377); | [5 empty] | 4377:Circ3NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ3PowerFactor_III,lo:=4378,hi:=4379); | [5 empty] | 4379:Circ3PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ3PowerFactor_L1,lo:=4380,hi:=4381); | [5 empty] | 4381:Circ3PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ3PowerFactor_L2,lo:=4382,hi:=4383); | [5 empty] | 4383:Circ3PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ3PowerFactor_L3,lo:=4384,hi:=4385); | [5 empty] | 4385:Circ3PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ3THDI_L1,lo:=4386,hi:=4387); | [5 empty] | 4387:Circ3THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ3THDI_L2,lo:=4388,hi:=4389); | [5 empty] | 4389:Circ3THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ3THDI_L3,lo:=4390,hi:=4391); | [5 empty] | 4391:Circ3THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ3THDV_L1,lo:=4392,hi:=4393); | [5 empty] | 4393:Circ3THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ3THDV_L2,lo:=4394,hi:=4395); | [5 empty] | 4395:Circ3THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ3THDV_L3,lo:=4396,hi:=4397); | [5 empty] | 4397:Circ3THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ3Tok_L1,lo:=4398,hi:=4399); | [5 empty] | 4399:Circ3Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ3Tok_L2,lo:=4400,hi:=4401); | [5 empty] | 4401:Circ3Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ3Tok_L3,lo:=4402,hi:=4403); | [5 empty] | 4403:Circ3Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ3TokPovprecje_III,lo:=4404,hi:=4405); | [5 empty] | 4405:Circ3TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ4CosFi_III,lo:=4406,hi:=4407); | [5 empty] | 4407:Circ4CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ4DelovnaEnergija,lo:=4408,hi:=4409); | [5 empty] | 4409:Circ4DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ4DelovnaMoc_III,lo:=4410,hi:=4411); | [5 empty] | 4411:Circ4DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ4DelovnaMoc_L1,lo:=4412,hi:=4413); | [5 empty] | 4413:Circ4DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ4DelovnaMoc_L2,lo:=4414,hi:=4415); | [5 empty] | 4415:Circ4DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ4DelovnaMoc_L3,lo:=4416,hi:=4417); | [5 empty] | 4417:Circ4DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ4Frekvenca_L1,lo:=4418,hi:=4419); | [5 empty] | 4419:Circ4Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ4InduktivnaEnergija,lo:=4420,hi:=4421); | [5 empty] | 4421:Circ4InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ4InduktivnaMoc_III,lo:=4422,hi:=4423); | [5 empty] | 4423:Circ4InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ4JalovaMoc_L1,lo:=4424,hi:=4425); | [5 empty] | 4425:Circ4JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ4JalovaMoc_L2,lo:=4426,hi:=4427); | [5 empty] | 4427:Circ4JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ4JalovaMoc_L3,lo:=4428,hi:=4429); | [5 empty] | 4429:Circ4JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ4KapacitivnaEnergija,lo:=4430,hi:=4431); | [5 empty] | 4431:Circ4KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ4KapacitivnaMoc_III,lo:=4432,hi:=4433); | [5 empty] | 4433:Circ4KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ4MaximumDemand,lo:=4434,hi:=4435); | [5 empty] | 4435:Circ4MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ4Napetost_L1_L2,lo:=4436,hi:=4437); | [5 empty] | 4437:Circ4Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ4Napetost_L1_N,lo:=4438,hi:=4439); | [5 empty] | 4439:Circ4Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ4Napetost_L2_L3,lo:=4440,hi:=4441); | [5 empty] | 4441:Circ4Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ4Napetost_L2_N,lo:=4442,hi:=4443); | [5 empty] | 4443:Circ4Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ4Napetost_L3_L1,lo:=4444,hi:=4445); | [5 empty] | 4445:Circ4Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ4Napetost_L3_N,lo:=4446,hi:=4447); | [5 empty] | 4447:Circ4Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ4NavideznaMoc_III,lo:=4448,hi:=4449); | [5 empty] | 4449:Circ4NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ4NicelniTok,lo:=4450,hi:=4451); | [5 empty] | 4451:Circ4NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ4PowerFactor_III,lo:=4452,hi:=4453); | [5 empty] | 4453:Circ4PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ4PowerFactor_L1,lo:=4454,hi:=4455); | [5 empty] | 4455:Circ4PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ4PowerFactor_L2,lo:=4456,hi:=4457); | [5 empty] | 4457:Circ4PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ4PowerFactor_L3,lo:=4458,hi:=4459); | [5 empty] | 4459:Circ4PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ4THDI_L1,lo:=4460,hi:=4461); | [5 empty] | 4461:Circ4THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ4THDI_L2,lo:=4462,hi:=4463); | [5 empty] | 4463:Circ4THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ4THDI_L3,lo:=4464,hi:=4465); | [5 empty] | 4465:Circ4THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ4THDV_L1,lo:=4466,hi:=4467); | [5 empty] | 4467:Circ4THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ4THDV_L2,lo:=4468,hi:=4469); | [5 empty] | 4469:Circ4THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ4THDV_L3,lo:=4470,hi:=4471); | [5 empty] | 4471:Circ4THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ4Tok_L1,lo:=4472,hi:=4473); | [5 empty] | 4473:Circ4Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ4Tok_L2,lo:=4474,hi:=4475); | [5 empty] | 4475:Circ4Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ4Tok_L3,lo:=4476,hi:=4477); | [5 empty] | 4477:Circ4Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ4TokPovprecje_III,lo:=4478,hi:=4479); | [5 empty] | 4479:Circ4TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ5CosFi_III,lo:=4480,hi:=4481); | [5 empty] | 4481:Circ5CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ5DelovnaEnergija,lo:=4482,hi:=4483); | [5 empty] | 4483:Circ5DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ5DelovnaMoc_III,lo:=4484,hi:=4485); | [5 empty] | 4485:Circ5DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ5DelovnaMoc_L1,lo:=4486,hi:=4487); | [5 empty] | 4487:Circ5DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ5DelovnaMoc_L2,lo:=4488,hi:=4489); | [5 empty] | 4489:Circ5DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ5DelovnaMoc_L3,lo:=4490,hi:=4491); | [5 empty] | 4491:Circ5DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ5Frekvenca_L1,lo:=4492,hi:=4493); | [5 empty] | 4493:Circ5Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ5InduktivnaEnergija,lo:=4494,hi:=4495); | [5 empty] | 4495:Circ5InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ5InduktivnaMoc_III,lo:=4496,hi:=4497); | [5 empty] | 4497:Circ5InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ5JalovaMoc_L1,lo:=4498,hi:=4499); | [5 empty] | 4499:Circ5JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ5JalovaMoc_L2,lo:=4500,hi:=4501); | [5 empty] | 4501:Circ5JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ5JalovaMoc_L3,lo:=4502,hi:=4503); | [5 empty] | 4503:Circ5JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ5KapacitivnaEnergija,lo:=4504,hi:=4505); | [5 empty] | 4505:Circ5KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ5KapacitivnaMoc_III,lo:=4506,hi:=4507); | [5 empty] | 4507:Circ5KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ5MaximumDemand,lo:=4508,hi:=4509); | [5 empty] | 4509:Circ5MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ5Napetost_L1_L2,lo:=4510,hi:=4511); | [5 empty] | 4511:Circ5Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ5Napetost_L1_N,lo:=4512,hi:=4513); | [5 empty] | 4513:Circ5Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ5Napetost_L2_L3,lo:=4514,hi:=4515); | [5 empty] | 4515:Circ5Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ5Napetost_L2_N,lo:=4516,hi:=4517); | [5 empty] | 4517:Circ5Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ5Napetost_L3_L1,lo:=4518,hi:=4519); | [5 empty] | 4519:Circ5Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ5Napetost_L3_N,lo:=4520,hi:=4521); | [5 empty] | 4521:Circ5Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ5NavideznaMoc_III,lo:=4522,hi:=4523); | [5 empty] | 4523:Circ5NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ5NicelniTok,lo:=4524,hi:=4525); | [5 empty] | 4525:Circ5NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ5PowerFactor_III,lo:=4526,hi:=4527); | [5 empty] | 4527:Circ5PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ5PowerFactor_L1,lo:=4528,hi:=4529); | [5 empty] | 4529:Circ5PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ5PowerFactor_L2,lo:=4530,hi:=4531); | [5 empty] | 4531:Circ5PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ5PowerFactor_L3,lo:=4532,hi:=4533); | [5 empty] | 4533:Circ5PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ5THDI_L1,lo:=4534,hi:=4535); | [5 empty] | 4535:Circ5THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ5THDI_L2,lo:=4536,hi:=4537); | [5 empty] | 4537:Circ5THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ5THDI_L3,lo:=4538,hi:=4539); | [5 empty] | 4539:Circ5THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ5THDV_L1,lo:=4540,hi:=4541); | [5 empty] | 4541:Circ5THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ5THDV_L2,lo:=4542,hi:=4543); | [5 empty] | 4543:Circ5THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ5THDV_L3,lo:=4544,hi:=4545); | [5 empty] | 4545:Circ5THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ5Tok_L1,lo:=4546,hi:=4547); | [5 empty] | 4547:Circ5Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ5Tok_L2,lo:=4548,hi:=4549); | [5 empty] | 4549:Circ5Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ5Tok_L3,lo:=4550,hi:=4551); | [5 empty] | 4551:Circ5Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ5TokPovprecje_III,lo:=4552,hi:=4553); | [5 empty] | 4553:Circ5TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ6CosFi_III,lo:=4554,hi:=4555); | [5 empty] | 4555:Circ6CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ6DelovnaEnergija,lo:=4556,hi:=4557); | [5 empty] | 4557:Circ6DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ6DelovnaMoc_III,lo:=4558,hi:=4559); | [5 empty] | 4559:Circ6DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ6DelovnaMoc_L1,lo:=4560,hi:=4561); | [5 empty] | 4561:Circ6DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ6DelovnaMoc_L2,lo:=4562,hi:=4563); | [5 empty] | 4563:Circ6DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ6DelovnaMoc_L3,lo:=4564,hi:=4565); | [5 empty] | 4565:Circ6DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ6Frekvenca_L1,lo:=4566,hi:=4567); | [5 empty] | 4567:Circ6Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ6InduktivnaEnergija,lo:=4568,hi:=4569); | [5 empty] | 4569:Circ6InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ6InduktivnaMoc_III,lo:=4570,hi:=4571); | [5 empty] | 4571:Circ6InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ6JalovaMoc_L1,lo:=4572,hi:=4573); | [5 empty] | 4573:Circ6JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ6JalovaMoc_L2,lo:=4574,hi:=4575); | [5 empty] | 4575:Circ6JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ6JalovaMoc_L3,lo:=4576,hi:=4577); | [5 empty] | 4577:Circ6JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ6KapacitivnaEnergija,lo:=4578,hi:=4579); | [5 empty] | 4579:Circ6KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ6KapacitivnaMoc_III,lo:=4580,hi:=4581); | [5 empty] | 4581:Circ6KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ6MaximumDemand,lo:=4582,hi:=4583); | [5 empty] | 4583:Circ6MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ6Napetost_L1_L2,lo:=4584,hi:=4585); | [5 empty] | 4585:Circ6Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ6Napetost_L1_N,lo:=4586,hi:=4587); | [5 empty] | 4587:Circ6Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ6Napetost_L2_L3,lo:=4588,hi:=4589); | [5 empty] | 4589:Circ6Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ6Napetost_L2_N,lo:=4590,hi:=4591); | [5 empty] | 4591:Circ6Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ6Napetost_L3_L1,lo:=4592,hi:=4593); | [5 empty] | 4593:Circ6Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ6Napetost_L3_N,lo:=4594,hi:=4595); | [5 empty] | 4595:Circ6Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ6NavideznaMoc_III,lo:=4596,hi:=4597); | [5 empty] | 4597:Circ6NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ6NicelniTok,lo:=4598,hi:=4599); | [5 empty] | 4599:Circ6NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ6PowerFactor_III,lo:=4600,hi:=4601); | [5 empty] | 4601:Circ6PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ6PowerFactor_L1,lo:=4602,hi:=4603); | [5 empty] | 4603:Circ6PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ6PowerFactor_L2,lo:=4604,hi:=4605); | [5 empty] | 4605:Circ6PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ6PowerFactor_L3,lo:=4606,hi:=4607); | [5 empty] | 4607:Circ6PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ6THDI_L1,lo:=4608,hi:=4609); | [5 empty] | 4609:Circ6THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ6THDI_L2,lo:=4610,hi:=4611); | [5 empty] | 4611:Circ6THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ6THDI_L3,lo:=4612,hi:=4613); | [5 empty] | 4613:Circ6THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ6THDV_L1,lo:=4614,hi:=4615); | [5 empty] | 4615:Circ6THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ6THDV_L2,lo:=4616,hi:=4617); | [5 empty] | 4617:Circ6THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ6THDV_L3,lo:=4618,hi:=4619); | [5 empty] | 4619:Circ6THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ6Tok_L1,lo:=4620,hi:=4621); | [5 empty] | 4621:Circ6Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ6Tok_L2,lo:=4622,hi:=4623); | [5 empty] | 4623:Circ6Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ6Tok_L3,lo:=4624,hi:=4625); | [5 empty] | 4625:Circ6Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ6TokPovprecje_III,lo:=4626,hi:=4627); | [5 empty] | 4627:Circ6TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ7CosFi_III,lo:=4628,hi:=4629); | [5 empty] | 4629:Circ7CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ7DelovnaEnergija,lo:=4630,hi:=4631); | [5 empty] | 4631:Circ7DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ7DelovnaMoc_III,lo:=4632,hi:=4633); | [5 empty] | 4633:Circ7DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ7DelovnaMoc_L1,lo:=4634,hi:=4635); | [5 empty] | 4635:Circ7DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ7DelovnaMoc_L2,lo:=4636,hi:=4637); | [5 empty] | 4637:Circ7DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ7DelovnaMoc_L3,lo:=4638,hi:=4639); | [5 empty] | 4639:Circ7DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ7Frekvenca_L1,lo:=4640,hi:=4641); | [5 empty] | 4641:Circ7Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ7InduktivnaEnergija,lo:=4642,hi:=4643); | [5 empty] | 4643:Circ7InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ7InduktivnaMoc_III,lo:=4644,hi:=4645); | [5 empty] | 4645:Circ7InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ7JalovaMoc_L1,lo:=4646,hi:=4647); | [5 empty] | 4647:Circ7JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ7JalovaMoc_L2,lo:=4648,hi:=4649); | [5 empty] | 4649:Circ7JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ7JalovaMoc_L3,lo:=4650,hi:=4651); | [5 empty] | 4651:Circ7JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ7KapacitivnaEnergija,lo:=4652,hi:=4653); | [5 empty] | 4653:Circ7KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ7KapacitivnaMoc_III,lo:=4654,hi:=4655); | [5 empty] | 4655:Circ7KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ7MaximumDemand,lo:=4656,hi:=4657); | [5 empty] | 4657:Circ7MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ7Napetost_L1_L2,lo:=4658,hi:=4659); | [5 empty] | 4659:Circ7Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ7Napetost_L1_N,lo:=4660,hi:=4661); | [5 empty] | 4661:Circ7Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ7Napetost_L2_L3,lo:=4662,hi:=4663); | [5 empty] | 4663:Circ7Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ7Napetost_L2_N,lo:=4664,hi:=4665); | [5 empty] | 4665:Circ7Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ7Napetost_L3_L1,lo:=4666,hi:=4667); | [5 empty] | 4667:Circ7Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ7Napetost_L3_N,lo:=4668,hi:=4669); | [5 empty] | 4669:Circ7Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ7NavideznaMoc_III,lo:=4670,hi:=4671); | [5 empty] | 4671:Circ7NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ7NicelniTok,lo:=4672,hi:=4673); | [5 empty] | 4673:Circ7NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ7PowerFactor_III,lo:=4674,hi:=4675); | [5 empty] | 4675:Circ7PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ7PowerFactor_L1,lo:=4676,hi:=4677); | [5 empty] | 4677:Circ7PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ7PowerFactor_L2,lo:=4678,hi:=4679); | [5 empty] | 4679:Circ7PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ7PowerFactor_L3,lo:=4680,hi:=4681); | [5 empty] | 4681:Circ7PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ7THDI_L1,lo:=4682,hi:=4683); | [5 empty] | 4683:Circ7THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ7THDI_L2,lo:=4684,hi:=4685); | [5 empty] | 4685:Circ7THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ7THDI_L3,lo:=4686,hi:=4687); | [5 empty] | 4687:Circ7THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ7THDV_L1,lo:=4688,hi:=4689); | [5 empty] | 4689:Circ7THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ7THDV_L2,lo:=4690,hi:=4691); | [5 empty] | 4691:Circ7THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ7THDV_L3,lo:=4692,hi:=4693); | [5 empty] | 4693:Circ7THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ7Tok_L1,lo:=4694,hi:=4695); | [5 empty] | 4695:Circ7Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ7Tok_L2,lo:=4696,hi:=4697); | [5 empty] | 4697:Circ7Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ7Tok_L3,lo:=4698,hi:=4699); | [5 empty] | 4699:Circ7Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ7TokPovprecje_III,lo:=4700,hi:=4701); | [5 empty] | 4701:Circ7TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ8CosFi_III,lo:=4702,hi:=4703); | [5 empty] | 4703:Circ8CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ8DelovnaEnergija,lo:=4704,hi:=4705); | [5 empty] | 4705:Circ8DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ8DelovnaMoc_III,lo:=4706,hi:=4707); | [5 empty] | 4707:Circ8DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ8DelovnaMoc_L1,lo:=4708,hi:=4709); | [5 empty] | 4709:Circ8DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ8DelovnaMoc_L2,lo:=4710,hi:=4711); | [5 empty] | 4711:Circ8DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ8DelovnaMoc_L3,lo:=4712,hi:=4713); | [5 empty] | 4713:Circ8DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ8Frekvenca_L1,lo:=4714,hi:=4715); | [5 empty] | 4715:Circ8Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ8InduktivnaEnergija,lo:=4716,hi:=4717); | [5 empty] | 4717:Circ8InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ8InduktivnaMoc_III,lo:=4718,hi:=4719); | [5 empty] | 4719:Circ8InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ8JalovaMoc_L1,lo:=4720,hi:=4721); | [5 empty] | 4721:Circ8JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ8JalovaMoc_L2,lo:=4722,hi:=4723); | [5 empty] | 4723:Circ8JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ8JalovaMoc_L3,lo:=4724,hi:=4725); | [5 empty] | 4725:Circ8JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ8KapacitivnaEnergija,lo:=4726,hi:=4727); | [5 empty] | 4727:Circ8KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ8KapacitivnaMoc_III,lo:=4728,hi:=4729); | [5 empty] | 4729:Circ8KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ8MaximumDemand,lo:=4730,hi:=4731); | [5 empty] | 4731:Circ8MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ8Napetost_L1_L2,lo:=4732,hi:=4733); | [5 empty] | 4733:Circ8Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ8Napetost_L1_N,lo:=4734,hi:=4735); | [5 empty] | 4735:Circ8Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ8Napetost_L2_L3,lo:=4736,hi:=4737); | [5 empty] | 4737:Circ8Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ8Napetost_L2_N,lo:=4738,hi:=4739); | [5 empty] | 4739:Circ8Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ8Napetost_L3_L1,lo:=4740,hi:=4741); | [5 empty] | 4741:Circ8Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ8Napetost_L3_N,lo:=4742,hi:=4743); | [5 empty] | 4743:Circ8Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ8NavideznaMoc_III,lo:=4744,hi:=4745); | [5 empty] | 4745:Circ8NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ8NicelniTok,lo:=4746,hi:=4747); | [5 empty] | 4747:Circ8NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ8PowerFactor_III,lo:=4748,hi:=4749); | [5 empty] | 4749:Circ8PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ8PowerFactor_L1,lo:=4750,hi:=4751); | [5 empty] | 4751:Circ8PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ8PowerFactor_L2,lo:=4752,hi:=4753); | [5 empty] | 4753:Circ8PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ8PowerFactor_L3,lo:=4754,hi:=4755); | [5 empty] | 4755:Circ8PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ8THDI_L1,lo:=4756,hi:=4757); | [5 empty] | 4757:Circ8THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ8THDI_L2,lo:=4758,hi:=4759); | [5 empty] | 4759:Circ8THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ8THDI_L3,lo:=4760,hi:=4761); | [5 empty] | 4761:Circ8THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ8THDV_L1,lo:=4762,hi:=4763); | [5 empty] | 4763:Circ8THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ8THDV_L2,lo:=4764,hi:=4765); | [5 empty] | 4765:Circ8THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ8THDV_L3,lo:=4766,hi:=4767); | [5 empty] | 4767:Circ8THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ8Tok_L1,lo:=4768,hi:=4769); | [5 empty] | 4769:Circ8Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ8Tok_L2,lo:=4770,hi:=4771); | [5 empty] | 4771:Circ8Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ8Tok_L3,lo:=4772,hi:=4773); | [5 empty] | 4773:Circ8Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ8TokPovprecje_III,lo:=4774,hi:=4775); | [5 empty] | 4775:Circ8TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ9CosFi_III,lo:=4776,hi:=4777); | [5 empty] | 4777:Circ9CosFi_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ9DelovnaEnergija,lo:=4778,hi:=4779); | [5 empty] | 4779:Circ9DelovnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ9DelovnaMoc_III,lo:=4780,hi:=4781); | [5 empty] | 4781:Circ9DelovnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ9DelovnaMoc_L1,lo:=4782,hi:=4783); | [5 empty] | 4783:Circ9DelovnaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ9DelovnaMoc_L2,lo:=4784,hi:=4785); | [5 empty] | 4785:Circ9DelovnaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ9DelovnaMoc_L3,lo:=4786,hi:=4787); | [5 empty] | 4787:Circ9DelovnaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ9Frekvenca_L1,lo:=4788,hi:=4789); | [5 empty] | 4789:Circ9Frekvenca_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ9InduktivnaEnergija,lo:=4790,hi:=4791); | [5 empty] | 4791:Circ9InduktivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ9InduktivnaMoc_III,lo:=4792,hi:=4793); | [5 empty] | 4793:Circ9InduktivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ9JalovaMoc_L1,lo:=4794,hi:=4795); | [5 empty] | 4795:Circ9JalovaMoc_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ9JalovaMoc_L2,lo:=4796,hi:=4797); | [5 empty] | 4797:Circ9JalovaMoc_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ9JalovaMoc_L3,lo:=4798,hi:=4799); | [5 empty] | 4799:Circ9JalovaMoc_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ9KapacitivnaEnergija,lo:=4800,hi:=4801); | [5 empty] | 4801:Circ9KapacitivnaEnergija:=Long_0;
|  |  | Read_dWord(dVar:=Circ9KapacitivnaMoc_III,lo:=4802,hi:=4803); | [5 empty] | 4803:Circ9KapacitivnaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ9MaximumDemand,lo:=4804,hi:=4805); | [5 empty] | 4805:Circ9MaximumDemand:=Long_0;
|  |  | Read_dWord(dVar:=Circ9Napetost_L1_L2,lo:=4806,hi:=4807); | [5 empty] | 4807:Circ9Napetost_L1_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ9Napetost_L1_N,lo:=4808,hi:=4809); | [5 empty] | 4809:Circ9Napetost_L1_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ9Napetost_L2_L3,lo:=4810,hi:=4811); | [5 empty] | 4811:Circ9Napetost_L2_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ9Napetost_L2_N,lo:=4812,hi:=4813); | [5 empty] | 4813:Circ9Napetost_L2_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ9Napetost_L3_L1,lo:=4814,hi:=4815); | [5 empty] | 4815:Circ9Napetost_L3_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ9Napetost_L3_N,lo:=4816,hi:=4817); | [5 empty] | 4817:Circ9Napetost_L3_N:=Long_0;
|  |  | Read_dWord(dVar:=Circ9NavideznaMoc_III,lo:=4818,hi:=4819); | [5 empty] | 4819:Circ9NavideznaMoc_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ9NicelniTok,lo:=4820,hi:=4821); | [5 empty] | 4821:Circ9NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ9PowerFactor_III,lo:=4822,hi:=4823); | [5 empty] | 4823:Circ9PowerFactor_III:=Long_0;
|  |  | Read_dWord(dVar:=Circ9PowerFactor_L1,lo:=4824,hi:=4825); | [5 empty] | 4825:Circ9PowerFactor_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ9PowerFactor_L2,lo:=4826,hi:=4827); | [5 empty] | 4827:Circ9PowerFactor_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ9PowerFactor_L3,lo:=4828,hi:=4829); | [5 empty] | 4829:Circ9PowerFactor_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ9THDI_L1,lo:=4830,hi:=4831); | [5 empty] | 4831:Circ9THDI_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ9THDI_L2,lo:=4832,hi:=4833); | [5 empty] | 4833:Circ9THDI_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ9THDI_L3,lo:=4834,hi:=4835); | [5 empty] | 4835:Circ9THDI_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ9THDV_L1,lo:=4836,hi:=4837); | [5 empty] | 4837:Circ9THDV_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ9THDV_L2,lo:=4838,hi:=4839); | [5 empty] | 4839:Circ9THDV_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ9THDV_L3,lo:=4840,hi:=4841); | [5 empty] | 4841:Circ9THDV_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ9Tok_L1,lo:=4842,hi:=4843); | [5 empty] | 4843:Circ9Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ9Tok_L2,lo:=4844,hi:=4845); | [5 empty] | 4845:Circ9Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ9Tok_L3,lo:=4846,hi:=4847); | [5 empty] | 4847:Circ9Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ9TokPovprecje_III,lo:=4848,hi:=4849); | [5 empty] | 4849:Circ9TokPovprecje_III:=Long_0;
|  |  | Read_dWord(dVar:=DW_Napake1,lo:=4850,hi:=4851); | [5 empty] | 4851:DW_Napake1:=Long_0;
|  |  | Read_dWord(dVar:=DW_Napake2,lo:=4852,hi:=4853); | [5 empty] | 4853:DW_Napake2:=Long_0;
|  |  | Read_dWord(dVar:=DW_Napake3,lo:=4854,hi:=4855); | [5 empty] | 4855:DW_Napake3:=Long_0;
|  |  | Read_dWord(dVar:=Generator_earth_currentA1,lo:=4856,hi:=4857); | [5 empty] | 4857:Generator_earth_currentA1:=Long_0;
|  |  | Read_dWord(dVar:=Generator_earth_currentA2,lo:=4858,hi:=4859); | [5 empty] | 4859:Generator_earth_currentA2:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L1_currentA1,lo:=4860,hi:=4861); | [5 empty] | 4861:Generator_L1_currentA1:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L1_currentA2,lo:=4862,hi:=4863); | [5 empty] | 4863:Generator_L1_currentA2:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L1_L2_voltageA1,lo:=4864,hi:=4865); | [5 empty] | 4865:Generator_L1_L2_voltageA1:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L1_L2_voltageA2,lo:=4866,hi:=4867); | [5 empty] | 4867:Generator_L1_L2_voltageA2:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L1_N_voltageA1,lo:=4868,hi:=4869); | [5 empty] | 4869:Generator_L1_N_voltageA1:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L1_N_voltageA2,lo:=4870,hi:=4871); | [5 empty] | 4871:Generator_L1_N_voltageA2:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L1_wattsA1,lo:=4872,hi:=4873); | [5 empty] | 4873:Generator_L1_wattsA1:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L1_wattsA2,lo:=4874,hi:=4875); | [5 empty] | 4875:Generator_L1_wattsA2:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L2_currentA1,lo:=4876,hi:=4877); | [5 empty] | 4877:Generator_L2_currentA1:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L2_currentA2,lo:=4878,hi:=4879); | [5 empty] | 4879:Generator_L2_currentA2:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L2_L3_voltageA1,lo:=4880,hi:=4881); | [5 empty] | 4881:Generator_L2_L3_voltageA1:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L2_L3_voltageA2,lo:=4882,hi:=4883); | [5 empty] | 4883:Generator_L2_L3_voltageA2:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L2_N_voltageA1,lo:=4884,hi:=4885); | [5 empty] | 4885:Generator_L2_N_voltageA1:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L2_N_voltageA2,lo:=4886,hi:=4887); | [5 empty] | 4887:Generator_L2_N_voltageA2:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L2_wattsA1,lo:=4888,hi:=4889); | [5 empty] | 4889:Generator_L2_wattsA1:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L2_wattsA2,lo:=4890,hi:=4891); | [5 empty] | 4891:Generator_L2_wattsA2:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L3_currentA1,lo:=4892,hi:=4893); | [5 empty] | 4893:Generator_L3_currentA1:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L3_currentA2,lo:=4894,hi:=4895); | [5 empty] | 4895:Generator_L3_currentA2:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L3_L1_voltageA1,lo:=4896,hi:=4897); | [5 empty] | 4897:Generator_L3_L1_voltageA1:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L3_L1_voltageA2,lo:=4898,hi:=4899); | [5 empty] | 4899:Generator_L3_L1_voltageA2:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L3_N_voltageA1,lo:=4900,hi:=4901); | [5 empty] | 4901:Generator_L3_N_voltageA1:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L3_N_voltageA2,lo:=4902,hi:=4903); | [5 empty] | 4903:Generator_L3_N_voltageA2:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L3_wattsA1,lo:=4904,hi:=4905); | [5 empty] | 4905:Generator_L3_wattsA1:=Long_0;
|  |  | Read_dWord(dVar:=Generator_L3_wattsA2,lo:=4906,hi:=4907); | [5 empty] | 4907:Generator_L3_wattsA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ14NicelniTok,lo:=4908,hi:=4909); | [5 empty] | 4909:Circ14NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ14Tok_L1,lo:=4910,hi:=4911); | [5 empty] | 4911:Circ14Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ14Tok_L2,lo:=4912,hi:=4913); | [5 empty] | 4913:Circ14Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ14Tok_L3,lo:=4914,hi:=4915); | [5 empty] | 4915:Circ14Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ8NicelniTok,lo:=4916,hi:=4917); | [5 empty] | 4917:Circ8NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ8Tok_L1,lo:=4918,hi:=4919); | [5 empty] | 4919:Circ8Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ8Tok_L2,lo:=4920,hi:=4921); | [5 empty] | 4921:Circ8Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ8Tok_L3,lo:=4922,hi:=4923); | [5 empty] | 4923:Circ8Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ9NicelniTok,lo:=4924,hi:=4925); | [5 empty] | 4925:Circ9NicelniTok:=Long_0;
|  |  | Read_dWord(dVar:=Circ9Tok_L1,lo:=4926,hi:=4927); | [5 empty] | 4927:Circ9Tok_L1:=Long_0;
|  |  | Read_dWord(dVar:=Circ9Tok_L2,lo:=4928,hi:=4929); | [5 empty] | 4929:Circ9Tok_L2:=Long_0;
|  |  | Read_dWord(dVar:=Circ9Tok_L3,lo:=4930,hi:=4931); | [5 empty] | 4931:Circ9Tok_L3:=Long_0;
|  |  | Read_dWord(dVar:=Circ1MaximumDemandA2,lo:=4932,hi:=4933); | [5 empty] | 4933:Circ1MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ1MaximumDemandA3,lo:=4934,hi:=4935); | [5 empty] | 4935:Circ1MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ2MaximumDemandA2,lo:=4936,hi:=4937); | [5 empty] | 4937:Circ2MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ2MaximumDemandA3,lo:=4938,hi:=4939); | [5 empty] | 4939:Circ2MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ3MaximumDemandA2,lo:=4940,hi:=4941); | [5 empty] | 4941:Circ3MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ3MaximumDemandA3,lo:=4942,hi:=4943); | [5 empty] | 4943:Circ3MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ4MaximumDemandA2,lo:=4944,hi:=4945); | [5 empty] | 4945:Circ4MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ4MaximumDemandA3,lo:=4946,hi:=4947); | [5 empty] | 4947:Circ4MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ5MaximumDemandA2,lo:=4948,hi:=4949); | [5 empty] | 4949:Circ5MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ5MaximumDemandA3,lo:=4950,hi:=4951); | [5 empty] | 4951:Circ5MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ6MaximumDemandA2,lo:=4952,hi:=4953); | [5 empty] | 4953:Circ6MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ6MaximumDemandA3,lo:=4954,hi:=4955); | [5 empty] | 4955:Circ6MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ7MaximumDemandA2,lo:=4956,hi:=4957); | [5 empty] | 4957:Circ7MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ7MaximumDemandA3,lo:=4958,hi:=4959); | [5 empty] | 4959:Circ7MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ8MaximumDemandA2,lo:=4960,hi:=4961); | [5 empty] | 4961:Circ8MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ8MaximumDemandA3,lo:=4962,hi:=4963); | [5 empty] | 4963:Circ8MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ9MaximumDemandA2,lo:=4964,hi:=4965); | [5 empty] | 4965:Circ9MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ9MaximumDemandA3,lo:=4966,hi:=4967); | [5 empty] | 4967:Circ9MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ10MaximumDemandA2,lo:=4968,hi:=4969); | [5 empty] | 4969:Circ10MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ10MaximumDemandA3,lo:=4970,hi:=4971); | [5 empty] | 4971:Circ10MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ11MaximumDemandA2,lo:=4972,hi:=4973); | [5 empty] | 4973:Circ11MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ11MaximumDemandA3,lo:=4974,hi:=4975); | [5 empty] | 4975:Circ11MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ12MaximumDemandA2,lo:=4976,hi:=4977); | [5 empty] | 4977:Circ12MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ12MaximumDemandA3,lo:=4978,hi:=4979); | [5 empty] | 4979:Circ12MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ13MaximumDemandA2,lo:=4980,hi:=4981); | [5 empty] | 4981:Circ13MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ13MaximumDemandA3,lo:=4982,hi:=4983); | [5 empty] | 4983:Circ13MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ14MaximumDemandA2,lo:=4984,hi:=4985); | [5 empty] | 4985:Circ14MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ14MaximumDemandA3,lo:=4986,hi:=4987); | [5 empty] | 4987:Circ14MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ15MaximumDemandA2,lo:=4988,hi:=4989); | [5 empty] | 4989:Circ15MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ15MaximumDemandA3,lo:=4990,hi:=4991); | [5 empty] | 4991:Circ15MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ16MaximumDemandA2,lo:=4992,hi:=4993); | [5 empty] | 4993:Circ16MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ16MaximumDemandA3,lo:=4994,hi:=4995); | [5 empty] | 4995:Circ16MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ17MaximumDemandA2,lo:=4996,hi:=4997); | [5 empty] | 4997:Circ17MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ17MaximumDemandA3,lo:=4998,hi:=4999); | [5 empty] | 4999:Circ17MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ18MaximumDemandA2,lo:=5000,hi:=5001); | [5 empty] | 5001:Circ18MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ18MaximumDemandA3,lo:=5002,hi:=5003); | [5 empty] | 5003:Circ18MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ19MaximumDemandA2,lo:=5004,hi:=5005); | [5 empty] | 5005:Circ19MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ19MaximumDemandA3,lo:=5006,hi:=5007); | [5 empty] | 5007:Circ19MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ20MaximumDemandA2,lo:=5008,hi:=5009); | [5 empty] | 5009:Circ20MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ20MaximumDemandA3,lo:=5010,hi:=5011); | [5 empty] | 5011:Circ20MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ21MaximumDemandA2,lo:=5012,hi:=5013); | [5 empty] | 5013:Circ21MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ21MaximumDemandA3,lo:=5014,hi:=5015); | [5 empty] | 5015:Circ21MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ22MaximumDemandA2,lo:=5016,hi:=5017); | [5 empty] | 5017:Circ22MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ22MaximumDemandA3,lo:=5018,hi:=5019); | [5 empty] | 5019:Circ22MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ23MaximumDemandA2,lo:=5020,hi:=5021); | [5 empty] | 5021:Circ23MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ23MaximumDemandA3,lo:=5022,hi:=5023); | [5 empty] | 5023:Circ23MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ24MaximumDemandA2,lo:=5024,hi:=5025); | [5 empty] | 5025:Circ24MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ24MaximumDemandA3,lo:=5026,hi:=5027); | [5 empty] | 5027:Circ24MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ25MaximumDemandA2,lo:=5028,hi:=5029); | [5 empty] | 5029:Circ25MaximumDemandA2:=Long_0;
|  |  | Read_dWord(dVar:=Circ25MaximumDemandA3,lo:=5030,hi:=5031); | [5 empty] | 5031:Circ25MaximumDemandA3:=Long_0;
|  |  | Read_dWord(dVar:=Circ[1].RazEner_D_SCADA,lo:=5032,hi:=5033); | [5 empty] | 5033:Circ[1].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[1].RazEner_T_SCADA,lo:=5034,hi:=5035); | [5 empty] | 5035:Circ[1].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[1].RazEner_M_SCADA,lo:=5036,hi:=5037); | [5 empty] | 5037:Circ[1].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[2].RazEner_D_SCADA,lo:=5038,hi:=5039); | [5 empty] | 5039:Circ[2].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[2].RazEner_T_SCADA,lo:=5040,hi:=5041); | [5 empty] | 5041:Circ[2].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[2].RazEner_M_SCADA,lo:=5042,hi:=5043); | [5 empty] | 5043:Circ[2].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[3].RazEner_D_SCADA,lo:=5044,hi:=5045); | [5 empty] | 5045:Circ[3].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[3].RazEner_T_SCADA,lo:=5046,hi:=5047); | [5 empty] | 5047:Circ[3].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[3].RazEner_M_SCADA,lo:=5048,hi:=5049); | [5 empty] | 5049:Circ[3].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[4].RazEner_D_SCADA,lo:=5050,hi:=5051); | [5 empty] | 5051:Circ[4].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[4].RazEner_T_SCADA,lo:=5052,hi:=5053); | [5 empty] | 5053:Circ[4].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[4].RazEner_M_SCADA,lo:=5054,hi:=5055); | [5 empty] | 5055:Circ[4].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[5].RazEner_D_SCADA,lo:=5056,hi:=5057); | [5 empty] | 5057:Circ[5].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[5].RazEner_T_SCADA,lo:=5058,hi:=5059); | [5 empty] | 5059:Circ[5].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[5].RazEner_M_SCADA,lo:=5060,hi:=5061); | [5 empty] | 5061:Circ[5].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[6].RazEner_D_SCADA,lo:=5062,hi:=5063); | [5 empty] | 5063:Circ[6].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[6].RazEner_T_SCADA,lo:=5064,hi:=5065); | [5 empty] | 5065:Circ[6].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[6].RazEner_M_SCADA,lo:=5066,hi:=5067); | [5 empty] | 5067:Circ[6].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[7].RazEner_D_SCADA,lo:=5068,hi:=5069); | [5 empty] | 5069:Circ[7].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[7].RazEner_T_SCADA,lo:=5070,hi:=5071); | [5 empty] | 5071:Circ[7].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[7].RazEner_M_SCADA,lo:=5072,hi:=5073); | [5 empty] | 5073:Circ[7].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[8].RazEner_D_SCADA,lo:=5074,hi:=5075); | [5 empty] | 5075:Circ[8].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[8].RazEner_T_SCADA,lo:=5076,hi:=5077); | [5 empty] | 5077:Circ[8].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[8].RazEner_M_SCADA,lo:=5078,hi:=5079); | [5 empty] | 5079:Circ[8].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[9].RazEner_D_SCADA,lo:=5080,hi:=5081); | [5 empty] | 5081:Circ[9].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[9].RazEner_T_SCADA,lo:=5082,hi:=5083); | [5 empty] | 5083:Circ[9].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[9].RazEner_M_SCADA,lo:=5084,hi:=5085); | [5 empty] | 5085:Circ[9].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[10].RazEner_D_SCADA,lo:=5086,hi:=5087); | [5 empty] | 5087:Circ[10].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[10].RazEner_T_SCADA,lo:=5088,hi:=5089); | [5 empty] | 5089:Circ[10].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[10].RazEner_M_SCADA,lo:=5090,hi:=5091); | [5 empty] | 5091:Circ[10].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[11].RazEner_D_SCADA,lo:=5092,hi:=5093); | [5 empty] | 5093:Circ[11].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[11].RazEner_T_SCADA,lo:=5094,hi:=5095); | [5 empty] | 5095:Circ[11].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[11].RazEner_M_SCADA,lo:=5096,hi:=5097); | [5 empty] | 5097:Circ[11].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[12].RazEner_D_SCADA,lo:=5098,hi:=5099); | [5 empty] | 5099:Circ[12].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[12].RazEner_T_SCADA,lo:=5100,hi:=5101); | [5 empty] | 5101:Circ[12].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[12].RazEner_M_SCADA,lo:=5102,hi:=5103); | [5 empty] | 5103:Circ[12].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[13].RazEner_D_SCADA,lo:=5104,hi:=5105); | [5 empty] | 5105:Circ[13].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[13].RazEner_T_SCADA,lo:=5106,hi:=5107); | [5 empty] | 5107:Circ[13].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[13].RazEner_M_SCADA,lo:=5108,hi:=5109); | [5 empty] | 5109:Circ[13].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[14].RazEner_D_SCADA,lo:=5110,hi:=5111); | [5 empty] | 5111:Circ[14].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[14].RazEner_T_SCADA,lo:=5112,hi:=5113); | [5 empty] | 5113:Circ[14].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[14].RazEner_M_SCADA,lo:=5114,hi:=5115); | [5 empty] | 5115:Circ[14].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[15].RazEner_D_SCADA,lo:=5116,hi:=5117); | [5 empty] | 5117:Circ[15].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[15].RazEner_T_SCADA,lo:=5118,hi:=5119); | [5 empty] | 5119:Circ[15].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[15].RazEner_M_SCADA,lo:=5120,hi:=5121); | [5 empty] | 5121:Circ[15].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[16].RazEner_D_SCADA,lo:=5122,hi:=5123); | [5 empty] | 5123:Circ[16].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[16].RazEner_T_SCADA,lo:=5124,hi:=5125); | [5 empty] | 5125:Circ[16].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[16].RazEner_M_SCADA,lo:=5126,hi:=5127); | [5 empty] | 5127:Circ[16].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[17].RazEner_D_SCADA,lo:=5128,hi:=5129); | [5 empty] | 5129:Circ[17].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[17].RazEner_T_SCADA,lo:=5130,hi:=5131); | [5 empty] | 5131:Circ[17].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[17].RazEner_M_SCADA,lo:=5132,hi:=5133); | [5 empty] | 5133:Circ[17].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[18].RazEner_D_SCADA,lo:=5134,hi:=5135); | [5 empty] | 5135:Circ[18].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[18].RazEner_T_SCADA,lo:=5136,hi:=5137); | [5 empty] | 5137:Circ[18].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[18].RazEner_M_SCADA,lo:=5138,hi:=5139); | [5 empty] | 5139:Circ[18].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[19].RazEner_D_SCADA,lo:=5140,hi:=5141); | [5 empty] | 5141:Circ[19].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[19].RazEner_T_SCADA,lo:=5142,hi:=5143); | [5 empty] | 5143:Circ[19].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[19].RazEner_M_SCADA,lo:=5144,hi:=5145); | [5 empty] | 5145:Circ[19].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[20].RazEner_D_SCADA,lo:=5146,hi:=5147); | [5 empty] | 5147:Circ[20].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[20].RazEner_T_SCADA,lo:=5148,hi:=5149); | [5 empty] | 5149:Circ[20].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[20].RazEner_M_SCADA,lo:=5150,hi:=5151); | [5 empty] | 5151:Circ[20].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[21].RazEner_D_SCADA,lo:=5152,hi:=5153); | [5 empty] | 5153:Circ[21].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[21].RazEner_T_SCADA,lo:=5154,hi:=5155); | [5 empty] | 5155:Circ[21].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[21].RazEner_M_SCADA,lo:=5156,hi:=5157); | [5 empty] | 5157:Circ[21].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[22].RazEner_D_SCADA,lo:=5158,hi:=5159); | [5 empty] | 5159:Circ[22].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[22].RazEner_T_SCADA,lo:=5160,hi:=5161); | [5 empty] | 5161:Circ[22].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[22].RazEner_M_SCADA,lo:=5162,hi:=5163); | [5 empty] | 5163:Circ[22].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[23].RazEner_D_SCADA,lo:=5164,hi:=5165); | [5 empty] | 5165:Circ[23].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[23].RazEner_T_SCADA,lo:=5166,hi:=5167); | [5 empty] | 5167:Circ[23].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[23].RazEner_M_SCADA,lo:=5168,hi:=5169); | [5 empty] | 5169:Circ[23].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[24].RazEner_D_SCADA,lo:=5170,hi:=5171); | [5 empty] | 5171:Circ[24].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[24].RazEner_T_SCADA,lo:=5172,hi:=5173); | [5 empty] | 5173:Circ[24].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[24].RazEner_M_SCADA,lo:=5174,hi:=5175); | [5 empty] | 5175:Circ[24].RazEner_M_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[25].RazEner_D_SCADA,lo:=5176,hi:=5177); | [5 empty] | 5177:Circ[25].RazEner_D_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[25].RazEner_T_SCADA,lo:=5178,hi:=5179); | [5 empty] | 5179:Circ[25].RazEner_T_SCADA:=Long_0;
|  |  | Read_dWord(dVar:=Circ[25].RazEner_M_SCADA,lo:=5180,hi:=5181); | [5 empty] | 5181:Circ[25].RazEner_M_SCADA:=Long_0;

## XSoft_EXP
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
PROGRAM mod_Read
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*Branje BOOL*)
(**)
mind_bool[0]:=DA3_rocno;
mind_bool[1]:=DA3motorni_pogon_okvara;
mind_bool[2]:=Izpad_CAN_med_K1_K2;
mind_bool[3]:=MI4agr_nap_RGM_A1;
mind_bool[4]:=MI4agr_nap_RGM_A2;
mind_bool[5]:=MI4DA1_2Q1_izklop;
mind_bool[6]:=MI4DA1_2Q1_vklop;
mind_bool[7]:=MI4DA1_del;
mind_bool[8]:=MI4DA1_prip;
mind_bool[9]:=MI4DA1_rezerva;
mind_bool[10]:=MI4DA1_sinh;
mind_bool[11]:=MI4DA1_zagon;
mind_bool[12]:=MI4DA2_2Q1_izklop;
mind_bool[13]:=MI4DA2_2Q1_vklop;
mind_bool[14]:=MI4DA2_del;
mind_bool[15]:=MI4DA2_prip;
mind_bool[16]:=MI4DA2_rezerva;
mind_bool[17]:=MI4DA2_sinh;
mind_bool[18]:=MI4DA2_zagon;
mind_bool[19]:=MI4del_zascA1_11Q1;
mind_bool[20]:=MI4del_zascA1_12Q1;
mind_bool[21]:=MI4del_zascA1_13Q1;
mind_bool[22]:=MI4del_zascA1_14Q1;
mind_bool[23]:=MI4del_zascA1_15Q1;
mind_bool[24]:=MI4del_zascA1_16Q1;
mind_bool[25]:=MI4del_zascA1_17Q1;
mind_bool[26]:=MI4del_zascA1_2Q1;
mind_bool[27]:=MI4del_zascA2_11Q1;
mind_bool[28]:=MI4del_zascA2_12Q1;
mind_bool[29]:=MI4del_zascA2_13Q1;
mind_bool[30]:=MI4del_zascA2_14Q1;
mind_bool[31]:=MI4K2agr_nap_RGM_A3;
mind_bool[32]:=MI4K2DA3_2Q1_izklop;
mind_bool[33]:=MI4K2DA3_2Q1_vklop;
mind_bool[34]:=MI4K2del_zasc0_11Q1;
mind_bool[35]:=MI4K2del_zasc0_12Q1;
mind_bool[36]:=MI4K2del_zasc0_13Q1;
mind_bool[37]:=MI4K2del_zasc0_14Q1;
mind_bool[38]:=MI4K2del_zasc0_15Q1;
mind_bool[39]:=MI4K2del_zasc0_16Q1;
mind_bool[40]:=MI4K2del_zasc0_17Q1;
mind_bool[41]:=MI4K2del_zasc0_18Q1;
mind_bool[42]:=MI4K2del_zasc0_19Q1;
mind_bool[43]:=MI4K2del_zasc0_20Q1;
mind_bool[44]:=MI4K2del_zasc0_21Q1;
mind_bool[45]:=MI4K2del_zasc0_22Q1;
mind_bool[46]:=MI4K2del_zasc0_23Q1;
mind_bool[47]:=MI4K2del_zascA3_11Q1;
mind_bool[48]:=MI4K2del_zascA3_12Q1;
mind_bool[49]:=MI4K2del_zascA3_13Q1;
mind_bool[50]:=MI4K2del_zascA3_14Q1;
mind_bool[51]:=MI4K2del_zascA3_15Q1;
mind_bool[52]:=MI4K2motorA3_1Q1_prip;
mind_bool[53]:=MI4K2motorA3_2Q1_prip;
mind_bool[54]:=MI4K2mrez_nap_RGM_A3;
mind_bool[55]:=MI4K2mrezaA3_1Q1_izklop;
mind_bool[56]:=MI4K2mrezaA3_1Q1_vklop;
mind_bool[57]:=MI4K2prenap_zasc0_OK;
mind_bool[58]:=MI4K2prenap_zascA3_OK;
mind_bool[59]:=MI4K2rocni_izk0_11Q1;
mind_bool[60]:=MI4K2rocni_izk0_12Q1;
mind_bool[61]:=MI4K2rocni_izk0_13Q1;
mind_bool[62]:=MI4K2rocni_izk0_14Q1;
mind_bool[63]:=MI4K2rocni_izk0_15Q1;
mind_bool[64]:=MI4K2rocni_izk0_16Q1;
mind_bool[65]:=MI4K2rocni_izk0_17Q1;
mind_bool[66]:=MI4K2rocni_izk0_18Q1;
mind_bool[67]:=MI4K2rocni_izk0_19Q1;
mind_bool[68]:=MI4K2rocni_izk0_20Q1;
mind_bool[69]:=MI4K2rocni_izk0_21Q1;
mind_bool[70]:=MI4K2rocni_izk0_22Q1;
mind_bool[71]:=MI4K2rocni_izk0_23Q1;
mind_bool[72]:=MI4K2rocni_izkA3_11Q1;
mind_bool[73]:=MI4K2rocni_izkA3_12Q1;
mind_bool[74]:=MI4K2rocni_izkA3_13Q1;
mind_bool[75]:=MI4K2rocni_izkA3_14Q1;
mind_bool[76]:=MI4K2rocni_izkA3_15Q1;
mind_bool[77]:=MI4K2stik0_11Q1_vkl;
mind_bool[78]:=MI4K2stik0_12Q1_vkl;
mind_bool[79]:=MI4K2stik0_13Q1_vkl;
mind_bool[80]:=MI4K2stik0_14Q1_vkl;
mind_bool[81]:=MI4K2stik0_15Q1_vkl;
mind_bool[82]:=MI4K2stik0_16Q1_vkl;
mind_bool[83]:=MI4K2stik0_17Q1_vkl;
mind_bool[84]:=MI4K2stik0_18Q1_vkl;
mind_bool[85]:=MI4K2stik0_19Q1_vkl;
mind_bool[86]:=MI4K2stik0_1Q1_vkl;
mind_bool[87]:=MI4K2stik0_20Q1_vkl;
mind_bool[88]:=MI4K2stik0_21Q1_vkl;
mind_bool[89]:=MI4K2stik0_22Q1_vkl;
mind_bool[90]:=MI4K2stik0_23Q1_vkl;
mind_bool[91]:=MI4K2stikA3_11Q1_vkl;
mind_bool[92]:=MI4K2stikA3_12Q1_vkl;
mind_bool[93]:=MI4K2stikA3_13Q1_vkl;
mind_bool[94]:=MI4K2stikA3_14Q1_vkl;
mind_bool[95]:=MI4K2stikA3_15Q1_vkl;
mind_bool[96]:=MI4K2stikA3_1Q1_vkl;
mind_bool[97]:=MI4K2stikA3_2Q1_vkl;
mind_bool[98]:=MI4krmDA_daljinsko;
mind_bool[99]:=MI4motorA1_1Q1_prip;
mind_bool[100]:=MI4motorA1_2Q1_prip;
mind_bool[101]:=MI4motorA2_1Q1_prip;
mind_bool[102]:=MI4motorA2_2Q1_prip;
mind_bool[103]:=MI4motorA2_6Q1_prip;
mind_bool[104]:=MI4mrez_nap_RGM_A1;
mind_bool[105]:=MI4mrez_nap_RGM_A2;
mind_bool[106]:=MI4mrezaA1_1Q1_izklop;
mind_bool[107]:=MI4mrezaA1_1Q1_vklop;
mind_bool[108]:=MI4mrezaA2_1Q1_izklop;
mind_bool[109]:=MI4mrezaA2_1Q1_vklop;
mind_bool[110]:=MI4napaka_alarm_DA1;
mind_bool[111]:=MI4napaka_alarm_DA2;
mind_bool[112]:=MI4prenap_zascA1_OK;
mind_bool[113]:=MI4prenap_zascA2_OK;
mind_bool[114]:=MI4rezerva_DA1;
mind_bool[115]:=MI4rocni_izkA1_11Q1;
mind_bool[116]:=MI4rocni_izkA1_12Q1;
mind_bool[117]:=MI4rocni_izkA1_13Q1;
mind_bool[118]:=MI4rocni_izkA1_14Q1;
mind_bool[119]:=MI4rocni_izkA1_15Q1;
mind_bool[120]:=MI4rocni_izkA1_16Q1;
mind_bool[121]:=MI4rocni_izkA1_17Q1;
mind_bool[122]:=MI4rocni_izkA2_11Q1;
mind_bool[123]:=MI4rocni_izkA2_12Q1;
mind_bool[124]:=MI4rocni_izkA2_13Q1;
mind_bool[125]:=MI4rocni_izkA2_14Q1;
mind_bool[126]:=MI4sinhroniziranje_DA1;
mind_bool[127]:=MI4sinhroniziranje_DA2;
mind_bool[128]:=MI4splosna_napaka_DA1;
mind_bool[129]:=MI4splosna_napaka_DA2;
mind_bool[130]:=MI4stikA1_11Q1_vkl;
mind_bool[131]:=MI4stikA1_12Q1_vkl;
mind_bool[132]:=MI4stikA1_13Q1_vkl;
mind_bool[133]:=MI4stikA1_14Q1_vkl;
mind_bool[134]:=MI4stikA1_15Q1_vkl;
mind_bool[135]:=MI4stikA1_16Q1_vkl;
mind_bool[136]:=MI4stikA1_17Q1_vkl;
mind_bool[137]:=MI4stikA1_1Q1_vkl;
mind_bool[138]:=MI4stikA1_2Q1_vkl;
mind_bool[139]:=MI4stikA1_6Q1_vkl;
mind_bool[140]:=MI4stikA2_11Q1_vkl;
mind_bool[141]:=MI4stikA2_12Q1_vkl;
mind_bool[142]:=MI4stikA2_13Q1_vkl;
mind_bool[143]:=MI4stikA2_14Q1_vkl;
mind_bool[144]:=MI4stikA2_1Q1_vkl;
mind_bool[145]:=MI4stikA2_2Q1_vkl;
mind_bool[146]:=MI4vezno_6Q1_izklop;
mind_bool[147]:=MI4vezno_6Q1_vklop;
mind_bool[148]:=MI4vzporedno_del_nikoli;
mind_bool[149]:=MI4vzporedno_del_nikoli_info;
mind_bool[150]:=MI4vzporedno_del_po_potrebi;
mind_bool[151]:=MI4vzporedno_del_po_potrebi_info;
mind_bool[152]:=MI4vzporedno_del_vedno;
mind_bool[153]:=MI4vzporedno_del_vedno_info;
mind_bool[154]:=MI4zaganjanje_DA1;
mind_bool[155]:=MI4zaganjanje_DA2;
mind_bool[156]:=mrezaDA3motorni_pogon_okvara;
mind_bool[157]:=mrezaDA3stikalo_okvara;
mind_bool[158]:=Napaka_v_kom_cirk_DA1;
mind_bool[159]:=Napaka_v_kom_cirk_DA2;
mind_bool[160]:=NapakaCOMModBus;
mind_bool[161]:=NapakaVKomunikaciji_Circutor1;
mind_bool[162]:=NapakaVKomunikaciji_Circutor10;
mind_bool[163]:=NapakaVKomunikaciji_Circutor11;
mind_bool[164]:=NapakaVKomunikaciji_Circutor12;
mind_bool[165]:=NapakaVKomunikaciji_Circutor13;
mind_bool[166]:=NapakaVKomunikaciji_Circutor14;
mind_bool[167]:=NapakaVKomunikaciji_Circutor15;
mind_bool[168]:=NapakaVKomunikaciji_Circutor16;
mind_bool[169]:=NapakaVKomunikaciji_Circutor17;
mind_bool[170]:=NapakaVKomunikaciji_Circutor18;
mind_bool[171]:=NapakaVKomunikaciji_Circutor19;
mind_bool[172]:=NapakaVKomunikaciji_Circutor2;
mind_bool[173]:=NapakaVKomunikaciji_Circutor20;
mind_bool[174]:=NapakaVKomunikaciji_Circutor21;
mind_bool[175]:=NapakaVKomunikaciji_Circutor22;
mind_bool[176]:=NapakaVKomunikaciji_Circutor23;
mind_bool[177]:=NapakaVKomunikaciji_Circutor24;
mind_bool[178]:=NapakaVKomunikaciji_Circutor25;
mind_bool[179]:=NapakaVKomunikaciji_Circutor3;
mind_bool[180]:=NapakaVKomunikaciji_Circutor4;
mind_bool[181]:=NapakaVKomunikaciji_Circutor5;
mind_bool[182]:=NapakaVKomunikaciji_Circutor6;
mind_bool[183]:=NapakaVKomunikaciji_Circutor7;
mind_bool[184]:=NapakaVKomunikaciji_Circutor8;
mind_bool[185]:=NapakaVKomunikaciji_Circutor9;
mind_bool[186]:=RDASlabaBaterijaMI4;
mind_bool[187]:=SlabaBaterijaMI4;
mind_bool[188]:=SlabaBaterijaPLC1;
mind_bool[189]:=SlabaBaterijaPLC2;
mind_bool[190]:=stikaloDA3_okvara;
mind_bool[191]:=UI_MI4K2DA3_2Q1_izklop;
mind_bool[192]:=UI_MI4K2DA3_2Q1_vklop;
mind_bool[193]:=UI_MI4K2mrezaA3_1Q1_izklop;
mind_bool[194]:=UI_MI4K2mrezaA3_1Q1_vklop;
mind_bool[195]:=cas_nastavi;
mind_bool[196]:=Circ_Vpis_Dnevne_energija_scada1;
mind_bool[197]:=Circ_Vpis_Dnevne_energija_scada2;
mind_bool[198]:=Circ_Vpis_Tedenska_energija_scada1;
mind_bool[199]:=Circ_Vpis_Tedenska_energija_scada2;
mind_bool[200]:=Circ_Vpis_Mesecna_energija_scada1;
mind_bool[201]:=Circ_Vpis_Mesecna_energija_scada2;
(*Branje INT*)
(**)
mind[0]:=Coolant_temperatureA1;
mind[1]:=Coolant_temperatureA2;
mind[2]:=delovna_energ_trenutno;
mind[3]:=delovna_energija_prej;
mind[4]:=Generator_current_lag_leadA1;
mind[5]:=Generator_current_lag_leadA2;
mind[6]:=jalova_energ_trenutno;
mind[7]:=jalova_energija_prej;
mind[8]:=Komanda;
mind[9]:=NastaviDanMI;
mind[10]:=NastaviLetoMI;
mind[11]:=NastaviMesecMI;
mind[12]:=NastaviMinutaMI;
mind[13]:=NastaviSekundaMI;
mind[14]:=NastaviUraMI;
mind[15]:=Status;
mind[16]:=st_izpad_komTPV;
(*Branje UINT*)
(**)
mind[6000]:=Battery_voltageA1;
mind[6001]:=Battery_voltageA2;
mind[6002]:=Charge_alternator_voltageA1;
mind[6003]:=Charge_alternator_voltageA2;
mind[6004]:=Engine_speedA1;
mind[6005]:=Engine_speedA2;
mind[6006]:=Generator_frequencyA1;
mind[6007]:=Generator_frequencyA2;
mind[6008]:=Generator_phase_rotationA1;
mind[6009]:=Generator_phase_rotationA2;
mind[6010]:=Oil_pressureA1;
mind[6011]:=Oil_pressureA2;
(*Branje LONG*)
(**)
Read_dWord(dVar:=Circ10CosFi_III,lo:=3000,hi:=3001);
Read_dWord(dVar:=Circ10DelovnaEnergija,lo:=3002,hi:=3003);
Read_dWord(dVar:=Circ10DelovnaMoc_III,lo:=3004,hi:=3005);
Read_dWord(dVar:=Circ10DelovnaMoc_L1,lo:=3006,hi:=3007);
Read_dWord(dVar:=Circ10DelovnaMoc_L2,lo:=3008,hi:=3009);
Read_dWord(dVar:=Circ10DelovnaMoc_L3,lo:=3010,hi:=3011);
Read_dWord(dVar:=Circ10Frekvenca_L1,lo:=3012,hi:=3013);
Read_dWord(dVar:=Circ10InduktivnaEnergija,lo:=3014,hi:=3015);
Read_dWord(dVar:=Circ10InduktivnaMoc_III,lo:=3016,hi:=3017);
Read_dWord(dVar:=Circ10JalovaMoc_L1,lo:=3018,hi:=3019);
Read_dWord(dVar:=Circ10JalovaMoc_L2,lo:=3020,hi:=3021);
Read_dWord(dVar:=Circ10JalovaMoc_L3,lo:=3022,hi:=3023);
Read_dWord(dVar:=Circ10KapacitivnaEnergija,lo:=3024,hi:=3025);
Read_dWord(dVar:=Circ10KapacitivnaMoc_III,lo:=3026,hi:=3027);
Read_dWord(dVar:=Circ10MaximumDemand,lo:=3028,hi:=3029);
Read_dWord(dVar:=Circ10Napetost_L1_L2,lo:=3030,hi:=3031);
Read_dWord(dVar:=Circ10Napetost_L1_N,lo:=3032,hi:=3033);
Read_dWord(dVar:=Circ10Napetost_L2_L3,lo:=3034,hi:=3035);
Read_dWord(dVar:=Circ10Napetost_L2_N,lo:=3036,hi:=3037);
Read_dWord(dVar:=Circ10Napetost_L3_L1,lo:=3038,hi:=3039);
Read_dWord(dVar:=Circ10Napetost_L3_N,lo:=3040,hi:=3041);
Read_dWord(dVar:=Circ10NavideznaMoc_III,lo:=3042,hi:=3043);
Read_dWord(dVar:=Circ10NicelniTok,lo:=3044,hi:=3045);
Read_dWord(dVar:=Circ10PowerFactor_III,lo:=3046,hi:=3047);
Read_dWord(dVar:=Circ10PowerFactor_L1,lo:=3048,hi:=3049);
Read_dWord(dVar:=Circ10PowerFactor_L2,lo:=3050,hi:=3051);
Read_dWord(dVar:=Circ10PowerFactor_L3,lo:=3052,hi:=3053);
Read_dWord(dVar:=Circ10THDI_L1,lo:=3054,hi:=3055);
Read_dWord(dVar:=Circ10THDI_L2,lo:=3056,hi:=3057);
Read_dWord(dVar:=Circ10THDI_L3,lo:=3058,hi:=3059);
Read_dWord(dVar:=Circ10THDV_L1,lo:=3060,hi:=3061);
Read_dWord(dVar:=Circ10THDV_L2,lo:=3062,hi:=3063);
Read_dWord(dVar:=Circ10THDV_L3,lo:=3064,hi:=3065);
Read_dWord(dVar:=Circ10Tok_L1,lo:=3066,hi:=3067);
Read_dWord(dVar:=Circ10Tok_L2,lo:=3068,hi:=3069);
Read_dWord(dVar:=Circ10Tok_L3,lo:=3070,hi:=3071);
Read_dWord(dVar:=Circ10TokPovprecje_III,lo:=3072,hi:=3073);
Read_dWord(dVar:=Circ11CosFi_III,lo:=3074,hi:=3075);
Read_dWord(dVar:=Circ11DelovnaEnergija,lo:=3076,hi:=3077);
Read_dWord(dVar:=Circ11DelovnaMoc_III,lo:=3078,hi:=3079);
Read_dWord(dVar:=Circ11DelovnaMoc_L1,lo:=3080,hi:=3081);
Read_dWord(dVar:=Circ11DelovnaMoc_L2,lo:=3082,hi:=3083);
Read_dWord(dVar:=Circ11DelovnaMoc_L3,lo:=3084,hi:=3085);
Read_dWord(dVar:=Circ11Frekvenca_L1,lo:=3086,hi:=3087);
Read_dWord(dVar:=Circ11InduktivnaEnergija,lo:=3088,hi:=3089);
Read_dWord(dVar:=Circ11InduktivnaMoc_III,lo:=3090,hi:=3091);
Read_dWord(dVar:=Circ11JalovaMoc_L1,lo:=3092,hi:=3093);
Read_dWord(dVar:=Circ11JalovaMoc_L2,lo:=3094,hi:=3095);
Read_dWord(dVar:=Circ11JalovaMoc_L3,lo:=3096,hi:=3097);
Read_dWord(dVar:=Circ11KapacitivnaEnergija,lo:=3098,hi:=3099);
Read_dWord(dVar:=Circ11KapacitivnaMoc_III,lo:=3100,hi:=3101);
Read_dWord(dVar:=Circ11MaximumDemand,lo:=3102,hi:=3103);
Read_dWord(dVar:=Circ11Napetost_L1_L2,lo:=3104,hi:=3105);
Read_dWord(dVar:=Circ11Napetost_L1_N,lo:=3106,hi:=3107);
Read_dWord(dVar:=Circ11Napetost_L2_L3,lo:=3108,hi:=3109);
Read_dWord(dVar:=Circ11Napetost_L2_N,lo:=3110,hi:=3111);
Read_dWord(dVar:=Circ11Napetost_L3_L1,lo:=3112,hi:=3113);
Read_dWord(dVar:=Circ11Napetost_L3_N,lo:=3114,hi:=3115);
Read_dWord(dVar:=Circ11NavideznaMoc_III,lo:=3116,hi:=3117);
Read_dWord(dVar:=Circ11NicelniTok,lo:=3118,hi:=3119);
Read_dWord(dVar:=Circ11PowerFactor_III,lo:=3120,hi:=3121);
Read_dWord(dVar:=Circ11PowerFactor_L1,lo:=3122,hi:=3123);
Read_dWord(dVar:=Circ11PowerFactor_L2,lo:=3124,hi:=3125);
Read_dWord(dVar:=Circ11PowerFactor_L3,lo:=3126,hi:=3127);
Read_dWord(dVar:=Circ11THDI_L1,lo:=3128,hi:=3129);
Read_dWord(dVar:=Circ11THDI_L2,lo:=3130,hi:=3131);
Read_dWord(dVar:=Circ11THDI_L3,lo:=3132,hi:=3133);
Read_dWord(dVar:=Circ11THDV_L1,lo:=3134,hi:=3135);
Read_dWord(dVar:=Circ11THDV_L2,lo:=3136,hi:=3137);
Read_dWord(dVar:=Circ11THDV_L3,lo:=3138,hi:=3139);
Read_dWord(dVar:=Circ11Tok_L1,lo:=3140,hi:=3141);
Read_dWord(dVar:=Circ11Tok_L2,lo:=3142,hi:=3143);
Read_dWord(dVar:=Circ11Tok_L3,lo:=3144,hi:=3145);
Read_dWord(dVar:=Circ11TokPovprecje_III,lo:=3146,hi:=3147);
Read_dWord(dVar:=Circ12CosFi_III,lo:=3148,hi:=3149);
Read_dWord(dVar:=Circ12DelovnaEnergija,lo:=3150,hi:=3151);
Read_dWord(dVar:=Circ12DelovnaMoc_III,lo:=3152,hi:=3153);
Read_dWord(dVar:=Circ12DelovnaMoc_L1,lo:=3154,hi:=3155);
Read_dWord(dVar:=Circ12DelovnaMoc_L2,lo:=3156,hi:=3157);
Read_dWord(dVar:=Circ12DelovnaMoc_L3,lo:=3158,hi:=3159);
Read_dWord(dVar:=Circ12Frekvenca_L1,lo:=3160,hi:=3161);
Read_dWord(dVar:=Circ12InduktivnaEnergija,lo:=3162,hi:=3163);
Read_dWord(dVar:=Circ12InduktivnaMoc_III,lo:=3164,hi:=3165);
Read_dWord(dVar:=Circ12JalovaMoc_L1,lo:=3166,hi:=3167);
Read_dWord(dVar:=Circ12JalovaMoc_L2,lo:=3168,hi:=3169);
Read_dWord(dVar:=Circ12JalovaMoc_L3,lo:=3170,hi:=3171);
Read_dWord(dVar:=Circ12KapacitivnaEnergija,lo:=3172,hi:=3173);
Read_dWord(dVar:=Circ12KapacitivnaMoc_III,lo:=3174,hi:=3175);
Read_dWord(dVar:=Circ12MaximumDemand,lo:=3176,hi:=3177);
Read_dWord(dVar:=Circ12Napetost_L1_L2,lo:=3178,hi:=3179);
Read_dWord(dVar:=Circ12Napetost_L1_N,lo:=3180,hi:=3181);
Read_dWord(dVar:=Circ12Napetost_L2_L3,lo:=3182,hi:=3183);
Read_dWord(dVar:=Circ12Napetost_L2_N,lo:=3184,hi:=3185);
Read_dWord(dVar:=Circ12Napetost_L3_L1,lo:=3186,hi:=3187);
Read_dWord(dVar:=Circ12Napetost_L3_N,lo:=3188,hi:=3189);
Read_dWord(dVar:=Circ12NavideznaMoc_III,lo:=3190,hi:=3191);
Read_dWord(dVar:=Circ12NicelniTok,lo:=3192,hi:=3193);
Read_dWord(dVar:=Circ12PowerFactor_III,lo:=3194,hi:=3195);
Read_dWord(dVar:=Circ12PowerFactor_L1,lo:=3196,hi:=3197);
Read_dWord(dVar:=Circ12PowerFactor_L2,lo:=3198,hi:=3199);
Read_dWord(dVar:=Circ12PowerFactor_L3,lo:=3200,hi:=3201);
Read_dWord(dVar:=Circ12THDI_L1,lo:=3202,hi:=3203);
Read_dWord(dVar:=Circ12THDI_L2,lo:=3204,hi:=3205);
Read_dWord(dVar:=Circ12THDI_L3,lo:=3206,hi:=3207);
Read_dWord(dVar:=Circ12THDV_L1,lo:=3208,hi:=3209);
Read_dWord(dVar:=Circ12THDV_L2,lo:=3210,hi:=3211);
Read_dWord(dVar:=Circ12THDV_L3,lo:=3212,hi:=3213);
Read_dWord(dVar:=Circ12Tok_L1,lo:=3214,hi:=3215);
Read_dWord(dVar:=Circ12Tok_L2,lo:=3216,hi:=3217);
Read_dWord(dVar:=Circ12Tok_L3,lo:=3218,hi:=3219);
Read_dWord(dVar:=Circ12TokPovprecje_III,lo:=3220,hi:=3221);
Read_dWord(dVar:=Circ13CosFi_III,lo:=3222,hi:=3223);
Read_dWord(dVar:=Circ13DelovnaEnergija,lo:=3224,hi:=3225);
Read_dWord(dVar:=Circ13DelovnaMoc_III,lo:=3226,hi:=3227);
Read_dWord(dVar:=Circ13DelovnaMoc_L1,lo:=3228,hi:=3229);
Read_dWord(dVar:=Circ13DelovnaMoc_L2,lo:=3230,hi:=3231);
Read_dWord(dVar:=Circ13DelovnaMoc_L3,lo:=3232,hi:=3233);
Read_dWord(dVar:=Circ13Frekvenca_L1,lo:=3234,hi:=3235);
Read_dWord(dVar:=Circ13InduktivnaEnergija,lo:=3236,hi:=3237);
Read_dWord(dVar:=Circ13InduktivnaMoc_III,lo:=3238,hi:=3239);
Read_dWord(dVar:=Circ13JalovaMoc_L1,lo:=3240,hi:=3241);
Read_dWord(dVar:=Circ13JalovaMoc_L2,lo:=3242,hi:=3243);
Read_dWord(dVar:=Circ13JalovaMoc_L3,lo:=3244,hi:=3245);
Read_dWord(dVar:=Circ13KapacitivnaEnergija,lo:=3246,hi:=3247);
Read_dWord(dVar:=Circ13KapacitivnaMoc_III,lo:=3248,hi:=3249);
Read_dWord(dVar:=Circ13MaximumDemand,lo:=3250,hi:=3251);
Read_dWord(dVar:=Circ13Napetost_L1_L2,lo:=3252,hi:=3253);
Read_dWord(dVar:=Circ13Napetost_L1_N,lo:=3254,hi:=3255);
Read_dWord(dVar:=Circ13Napetost_L2_L3,lo:=3256,hi:=3257);
Read_dWord(dVar:=Circ13Napetost_L2_N,lo:=3258,hi:=3259);
Read_dWord(dVar:=Circ13Napetost_L3_L1,lo:=3260,hi:=3261);
Read_dWord(dVar:=Circ13Napetost_L3_N,lo:=3262,hi:=3263);
Read_dWord(dVar:=Circ13NavideznaMoc_III,lo:=3264,hi:=3265);
Read_dWord(dVar:=Circ13NicelniTok,lo:=3266,hi:=3267);
Read_dWord(dVar:=Circ13PowerFactor_III,lo:=3268,hi:=3269);
Read_dWord(dVar:=Circ13PowerFactor_L1,lo:=3270,hi:=3271);
Read_dWord(dVar:=Circ13PowerFactor_L2,lo:=3272,hi:=3273);
Read_dWord(dVar:=Circ13PowerFactor_L3,lo:=3274,hi:=3275);
Read_dWord(dVar:=Circ13THDI_L1,lo:=3276,hi:=3277);
Read_dWord(dVar:=Circ13THDI_L2,lo:=3278,hi:=3279);
Read_dWord(dVar:=Circ13THDI_L3,lo:=3280,hi:=3281);
Read_dWord(dVar:=Circ13THDV_L1,lo:=3282,hi:=3283);
Read_dWord(dVar:=Circ13THDV_L2,lo:=3284,hi:=3285);
Read_dWord(dVar:=Circ13THDV_L3,lo:=3286,hi:=3287);
Read_dWord(dVar:=Circ13Tok_L1,lo:=3288,hi:=3289);
Read_dWord(dVar:=Circ13Tok_L2,lo:=3290,hi:=3291);
Read_dWord(dVar:=Circ13Tok_L3,lo:=3292,hi:=3293);
Read_dWord(dVar:=Circ13TokPovprecje_III,lo:=3294,hi:=3295);
Read_dWord(dVar:=Circ14CosFi_III,lo:=3296,hi:=3297);
Read_dWord(dVar:=Circ14DelovnaEnergija,lo:=3298,hi:=3299);
Read_dWord(dVar:=Circ14DelovnaMoc_III,lo:=3300,hi:=3301);
Read_dWord(dVar:=Circ14DelovnaMoc_L1,lo:=3302,hi:=3303);
Read_dWord(dVar:=Circ14DelovnaMoc_L2,lo:=3304,hi:=3305);
Read_dWord(dVar:=Circ14DelovnaMoc_L3,lo:=3306,hi:=3307);
Read_dWord(dVar:=Circ14Frekvenca_L1,lo:=3308,hi:=3309);
Read_dWord(dVar:=Circ14InduktivnaEnergija,lo:=3310,hi:=3311);
Read_dWord(dVar:=Circ14InduktivnaMoc_III,lo:=3312,hi:=3313);
Read_dWord(dVar:=Circ14JalovaMoc_L1,lo:=3314,hi:=3315);
Read_dWord(dVar:=Circ14JalovaMoc_L2,lo:=3316,hi:=3317);
Read_dWord(dVar:=Circ14JalovaMoc_L3,lo:=3318,hi:=3319);
Read_dWord(dVar:=Circ14KapacitivnaEnergija,lo:=3320,hi:=3321);
Read_dWord(dVar:=Circ14KapacitivnaMoc_III,lo:=3322,hi:=3323);
Read_dWord(dVar:=Circ14MaximumDemand,lo:=3324,hi:=3325);
Read_dWord(dVar:=Circ14Napetost_L1_L2,lo:=3326,hi:=3327);
Read_dWord(dVar:=Circ14Napetost_L1_N,lo:=3328,hi:=3329);
Read_dWord(dVar:=Circ14Napetost_L2_L3,lo:=3330,hi:=3331);
Read_dWord(dVar:=Circ14Napetost_L2_N,lo:=3332,hi:=3333);
Read_dWord(dVar:=Circ14Napetost_L3_L1,lo:=3334,hi:=3335);
Read_dWord(dVar:=Circ14Napetost_L3_N,lo:=3336,hi:=3337);
Read_dWord(dVar:=Circ14NavideznaMoc_III,lo:=3338,hi:=3339);
Read_dWord(dVar:=Circ14NicelniTok,lo:=3340,hi:=3341);
Read_dWord(dVar:=Circ14PowerFactor_III,lo:=3342,hi:=3343);
Read_dWord(dVar:=Circ14PowerFactor_L1,lo:=3344,hi:=3345);
Read_dWord(dVar:=Circ14PowerFactor_L2,lo:=3346,hi:=3347);
Read_dWord(dVar:=Circ14PowerFactor_L3,lo:=3348,hi:=3349);
Read_dWord(dVar:=Circ14THDI_L1,lo:=3350,hi:=3351);
Read_dWord(dVar:=Circ14THDI_L2,lo:=3352,hi:=3353);
Read_dWord(dVar:=Circ14THDI_L3,lo:=3354,hi:=3355);
Read_dWord(dVar:=Circ14THDV_L1,lo:=3356,hi:=3357);
Read_dWord(dVar:=Circ14THDV_L2,lo:=3358,hi:=3359);
Read_dWord(dVar:=Circ14THDV_L3,lo:=3360,hi:=3361);
Read_dWord(dVar:=Circ14Tok_L1,lo:=3362,hi:=3363);
Read_dWord(dVar:=Circ14Tok_L2,lo:=3364,hi:=3365);
Read_dWord(dVar:=Circ14Tok_L3,lo:=3366,hi:=3367);
Read_dWord(dVar:=Circ14TokPovprecje_III,lo:=3368,hi:=3369);
Read_dWord(dVar:=Circ15CosFi_III,lo:=3370,hi:=3371);
Read_dWord(dVar:=Circ15DelovnaEnergija,lo:=3372,hi:=3373);
Read_dWord(dVar:=Circ15DelovnaMoc_III,lo:=3374,hi:=3375);
Read_dWord(dVar:=Circ15DelovnaMoc_L1,lo:=3376,hi:=3377);
Read_dWord(dVar:=Circ15DelovnaMoc_L2,lo:=3378,hi:=3379);
Read_dWord(dVar:=Circ15DelovnaMoc_L3,lo:=3380,hi:=3381);
Read_dWord(dVar:=Circ15Frekvenca_L1,lo:=3382,hi:=3383);
Read_dWord(dVar:=Circ15InduktivnaEnergija,lo:=3384,hi:=3385);
Read_dWord(dVar:=Circ15InduktivnaMoc_III,lo:=3386,hi:=3387);
Read_dWord(dVar:=Circ15JalovaMoc_L1,lo:=3388,hi:=3389);
Read_dWord(dVar:=Circ15JalovaMoc_L2,lo:=3390,hi:=3391);
Read_dWord(dVar:=Circ15JalovaMoc_L3,lo:=3392,hi:=3393);
Read_dWord(dVar:=Circ15KapacitivnaEnergija,lo:=3394,hi:=3395);
Read_dWord(dVar:=Circ15KapacitivnaMoc_III,lo:=3396,hi:=3397);
Read_dWord(dVar:=Circ15MaximumDemand,lo:=3398,hi:=3399);
Read_dWord(dVar:=Circ15Napetost_L1_L2,lo:=3400,hi:=3401);
Read_dWord(dVar:=Circ15Napetost_L1_N,lo:=3402,hi:=3403);
Read_dWord(dVar:=Circ15Napetost_L2_L3,lo:=3404,hi:=3405);
Read_dWord(dVar:=Circ15Napetost_L2_N,lo:=3406,hi:=3407);
Read_dWord(dVar:=Circ15Napetost_L3_L1,lo:=3408,hi:=3409);
Read_dWord(dVar:=Circ15Napetost_L3_N,lo:=3410,hi:=3411);
Read_dWord(dVar:=Circ15NavideznaMoc_III,lo:=3412,hi:=3413);
Read_dWord(dVar:=Circ15NicelniTok,lo:=3414,hi:=3415);
Read_dWord(dVar:=Circ15PowerFactor_III,lo:=3416,hi:=3417);
Read_dWord(dVar:=Circ15PowerFactor_L1,lo:=3418,hi:=3419);
Read_dWord(dVar:=Circ15PowerFactor_L2,lo:=3420,hi:=3421);
Read_dWord(dVar:=Circ15PowerFactor_L3,lo:=3422,hi:=3423);
Read_dWord(dVar:=Circ15THDI_L1,lo:=3424,hi:=3425);
Read_dWord(dVar:=Circ15THDI_L2,lo:=3426,hi:=3427);
Read_dWord(dVar:=Circ15THDI_L3,lo:=3428,hi:=3429);
Read_dWord(dVar:=Circ15THDV_L1,lo:=3430,hi:=3431);
Read_dWord(dVar:=Circ15THDV_L2,lo:=3432,hi:=3433);
Read_dWord(dVar:=Circ15THDV_L3,lo:=3434,hi:=3435);
Read_dWord(dVar:=Circ15Tok_L1,lo:=3436,hi:=3437);
Read_dWord(dVar:=Circ15Tok_L2,lo:=3438,hi:=3439);
Read_dWord(dVar:=Circ15Tok_L3,lo:=3440,hi:=3441);
Read_dWord(dVar:=Circ15TokPovprecje_III,lo:=3442,hi:=3443);
Read_dWord(dVar:=Circ16CosFi_III,lo:=3444,hi:=3445);
Read_dWord(dVar:=Circ16DelovnaEnergija,lo:=3446,hi:=3447);
Read_dWord(dVar:=Circ16DelovnaMoc_III,lo:=3448,hi:=3449);
Read_dWord(dVar:=Circ16DelovnaMoc_L1,lo:=3450,hi:=3451);
Read_dWord(dVar:=Circ16DelovnaMoc_L2,lo:=3452,hi:=3453);
Read_dWord(dVar:=Circ16DelovnaMoc_L3,lo:=3454,hi:=3455);
Read_dWord(dVar:=Circ16Frekvenca_L1,lo:=3456,hi:=3457);
Read_dWord(dVar:=Circ16InduktivnaEnergija,lo:=3458,hi:=3459);
Read_dWord(dVar:=Circ16InduktivnaMoc_III,lo:=3460,hi:=3461);
Read_dWord(dVar:=Circ16JalovaMoc_L1,lo:=3462,hi:=3463);
Read_dWord(dVar:=Circ16JalovaMoc_L2,lo:=3464,hi:=3465);
Read_dWord(dVar:=Circ16JalovaMoc_L3,lo:=3466,hi:=3467);
Read_dWord(dVar:=Circ16KapacitivnaEnergija,lo:=3468,hi:=3469);
Read_dWord(dVar:=Circ16KapacitivnaMoc_III,lo:=3470,hi:=3471);
Read_dWord(dVar:=Circ16MaximumDemand,lo:=3472,hi:=3473);
Read_dWord(dVar:=Circ16Napetost_L1_L2,lo:=3474,hi:=3475);
Read_dWord(dVar:=Circ16Napetost_L1_N,lo:=3476,hi:=3477);
Read_dWord(dVar:=Circ16Napetost_L2_L3,lo:=3478,hi:=3479);
Read_dWord(dVar:=Circ16Napetost_L2_N,lo:=3480,hi:=3481);
Read_dWord(dVar:=Circ16Napetost_L3_L1,lo:=3482,hi:=3483);
Read_dWord(dVar:=Circ16Napetost_L3_N,lo:=3484,hi:=3485);
Read_dWord(dVar:=Circ16NavideznaMoc_III,lo:=3486,hi:=3487);
Read_dWord(dVar:=Circ16NicelniTok,lo:=3488,hi:=3489);
Read_dWord(dVar:=Circ16PowerFactor_III,lo:=3490,hi:=3491);
Read_dWord(dVar:=Circ16PowerFactor_L1,lo:=3492,hi:=3493);
Read_dWord(dVar:=Circ16PowerFactor_L2,lo:=3494,hi:=3495);
Read_dWord(dVar:=Circ16PowerFactor_L3,lo:=3496,hi:=3497);
Read_dWord(dVar:=Circ16THDI_L1,lo:=3498,hi:=3499);
Read_dWord(dVar:=Circ16THDI_L2,lo:=3500,hi:=3501);
Read_dWord(dVar:=Circ16THDI_L3,lo:=3502,hi:=3503);
Read_dWord(dVar:=Circ16THDV_L1,lo:=3504,hi:=3505);
Read_dWord(dVar:=Circ16THDV_L2,lo:=3506,hi:=3507);
Read_dWord(dVar:=Circ16THDV_L3,lo:=3508,hi:=3509);
Read_dWord(dVar:=Circ16Tok_L1,lo:=3510,hi:=3511);
Read_dWord(dVar:=Circ16Tok_L2,lo:=3512,hi:=3513);
Read_dWord(dVar:=Circ16Tok_L3,lo:=3514,hi:=3515);
Read_dWord(dVar:=Circ16TokPovprecje_III,lo:=3516,hi:=3517);
Read_dWord(dVar:=Circ17CosFi_III,lo:=3518,hi:=3519);
Read_dWord(dVar:=Circ17DelovnaEnergija,lo:=3520,hi:=3521);
Read_dWord(dVar:=Circ17DelovnaMoc_III,lo:=3522,hi:=3523);
Read_dWord(dVar:=Circ17DelovnaMoc_L1,lo:=3524,hi:=3525);
Read_dWord(dVar:=Circ17DelovnaMoc_L2,lo:=3526,hi:=3527);
Read_dWord(dVar:=Circ17DelovnaMoc_L3,lo:=3528,hi:=3529);
Read_dWord(dVar:=Circ17Frekvenca_L1,lo:=3530,hi:=3531);
Read_dWord(dVar:=Circ17InduktivnaEnergija,lo:=3532,hi:=3533);
Read_dWord(dVar:=Circ17InduktivnaMoc_III,lo:=3534,hi:=3535);
Read_dWord(dVar:=Circ17JalovaMoc_L1,lo:=3536,hi:=3537);
Read_dWord(dVar:=Circ17JalovaMoc_L2,lo:=3538,hi:=3539);
Read_dWord(dVar:=Circ17JalovaMoc_L3,lo:=3540,hi:=3541);
Read_dWord(dVar:=Circ17KapacitivnaEnergija,lo:=3542,hi:=3543);
Read_dWord(dVar:=Circ17KapacitivnaMoc_III,lo:=3544,hi:=3545);
Read_dWord(dVar:=Circ17MaximumDemand,lo:=3546,hi:=3547);
Read_dWord(dVar:=Circ17Napetost_L1_L2,lo:=3548,hi:=3549);
Read_dWord(dVar:=Circ17Napetost_L1_N,lo:=3550,hi:=3551);
Read_dWord(dVar:=Circ17Napetost_L2_L3,lo:=3552,hi:=3553);
Read_dWord(dVar:=Circ17Napetost_L2_N,lo:=3554,hi:=3555);
Read_dWord(dVar:=Circ17Napetost_L3_L1,lo:=3556,hi:=3557);
Read_dWord(dVar:=Circ17Napetost_L3_N,lo:=3558,hi:=3559);
Read_dWord(dVar:=Circ17NavideznaMoc_III,lo:=3560,hi:=3561);
Read_dWord(dVar:=Circ17NicelniTok,lo:=3562,hi:=3563);
Read_dWord(dVar:=Circ17PowerFactor_III,lo:=3564,hi:=3565);
Read_dWord(dVar:=Circ17PowerFactor_L1,lo:=3566,hi:=3567);
Read_dWord(dVar:=Circ17PowerFactor_L2,lo:=3568,hi:=3569);
Read_dWord(dVar:=Circ17PowerFactor_L3,lo:=3570,hi:=3571);
Read_dWord(dVar:=Circ17THDI_L1,lo:=3572,hi:=3573);
Read_dWord(dVar:=Circ17THDI_L2,lo:=3574,hi:=3575);
Read_dWord(dVar:=Circ17THDI_L3,lo:=3576,hi:=3577);
Read_dWord(dVar:=Circ17THDV_L1,lo:=3578,hi:=3579);
Read_dWord(dVar:=Circ17THDV_L2,lo:=3580,hi:=3581);
Read_dWord(dVar:=Circ17THDV_L3,lo:=3582,hi:=3583);
Read_dWord(dVar:=Circ17Tok_L1,lo:=3584,hi:=3585);
Read_dWord(dVar:=Circ17Tok_L2,lo:=3586,hi:=3587);
Read_dWord(dVar:=Circ17Tok_L3,lo:=3588,hi:=3589);
Read_dWord(dVar:=Circ17TokPovprecje_III,lo:=3590,hi:=3591);
Read_dWord(dVar:=Circ18CosFi_III,lo:=3592,hi:=3593);
Read_dWord(dVar:=Circ18DelovnaEnergija,lo:=3594,hi:=3595);
Read_dWord(dVar:=Circ18DelovnaMoc_III,lo:=3596,hi:=3597);
Read_dWord(dVar:=Circ18DelovnaMoc_L1,lo:=3598,hi:=3599);
Read_dWord(dVar:=Circ18DelovnaMoc_L2,lo:=3600,hi:=3601);
Read_dWord(dVar:=Circ18DelovnaMoc_L3,lo:=3602,hi:=3603);
Read_dWord(dVar:=Circ18Frekvenca_L1,lo:=3604,hi:=3605);
Read_dWord(dVar:=Circ18InduktivnaEnergija,lo:=3606,hi:=3607);
Read_dWord(dVar:=Circ18InduktivnaMoc_III,lo:=3608,hi:=3609);
Read_dWord(dVar:=Circ18JalovaMoc_L1,lo:=3610,hi:=3611);
Read_dWord(dVar:=Circ18JalovaMoc_L2,lo:=3612,hi:=3613);
Read_dWord(dVar:=Circ18JalovaMoc_L3,lo:=3614,hi:=3615);
Read_dWord(dVar:=Circ18KapacitivnaEnergija,lo:=3616,hi:=3617);
Read_dWord(dVar:=Circ18KapacitivnaMoc_III,lo:=3618,hi:=3619);
Read_dWord(dVar:=Circ18MaximumDemand,lo:=3620,hi:=3621);
Read_dWord(dVar:=Circ18Napetost_L1_L2,lo:=3622,hi:=3623);
Read_dWord(dVar:=Circ18Napetost_L1_N,lo:=3624,hi:=3625);
Read_dWord(dVar:=Circ18Napetost_L2_L3,lo:=3626,hi:=3627);
Read_dWord(dVar:=Circ18Napetost_L2_N,lo:=3628,hi:=3629);
Read_dWord(dVar:=Circ18Napetost_L3_L1,lo:=3630,hi:=3631);
Read_dWord(dVar:=Circ18Napetost_L3_N,lo:=3632,hi:=3633);
Read_dWord(dVar:=Circ18NavideznaMoc_III,lo:=3634,hi:=3635);
Read_dWord(dVar:=Circ18NicelniTok,lo:=3636,hi:=3637);
Read_dWord(dVar:=Circ18PowerFactor_III,lo:=3638,hi:=3639);
Read_dWord(dVar:=Circ18PowerFactor_L1,lo:=3640,hi:=3641);
Read_dWord(dVar:=Circ18PowerFactor_L2,lo:=3642,hi:=3643);
Read_dWord(dVar:=Circ18PowerFactor_L3,lo:=3644,hi:=3645);
Read_dWord(dVar:=Circ18THDI_L1,lo:=3646,hi:=3647);
Read_dWord(dVar:=Circ18THDI_L2,lo:=3648,hi:=3649);
Read_dWord(dVar:=Circ18THDI_L3,lo:=3650,hi:=3651);
Read_dWord(dVar:=Circ18THDV_L1,lo:=3652,hi:=3653);
Read_dWord(dVar:=Circ18THDV_L2,lo:=3654,hi:=3655);
Read_dWord(dVar:=Circ18THDV_L3,lo:=3656,hi:=3657);
Read_dWord(dVar:=Circ18Tok_L1,lo:=3658,hi:=3659);
Read_dWord(dVar:=Circ18Tok_L2,lo:=3660,hi:=3661);
Read_dWord(dVar:=Circ18Tok_L3,lo:=3662,hi:=3663);
Read_dWord(dVar:=Circ18TokPovprecje_III,lo:=3664,hi:=3665);
Read_dWord(dVar:=Circ19CosFi_III,lo:=3666,hi:=3667);
Read_dWord(dVar:=Circ19DelovnaEnergija,lo:=3668,hi:=3669);
Read_dWord(dVar:=Circ19DelovnaMoc_III,lo:=3670,hi:=3671);
Read_dWord(dVar:=Circ19DelovnaMoc_L1,lo:=3672,hi:=3673);
Read_dWord(dVar:=Circ19DelovnaMoc_L2,lo:=3674,hi:=3675);
Read_dWord(dVar:=Circ19DelovnaMoc_L3,lo:=3676,hi:=3677);
Read_dWord(dVar:=Circ19Frekvenca_L1,lo:=3678,hi:=3679);
Read_dWord(dVar:=Circ19InduktivnaEnergija,lo:=3680,hi:=3681);
Read_dWord(dVar:=Circ19InduktivnaMoc_III,lo:=3682,hi:=3683);
Read_dWord(dVar:=Circ19JalovaMoc_L1,lo:=3684,hi:=3685);
Read_dWord(dVar:=Circ19JalovaMoc_L2,lo:=3686,hi:=3687);
Read_dWord(dVar:=Circ19JalovaMoc_L3,lo:=3688,hi:=3689);
Read_dWord(dVar:=Circ19KapacitivnaEnergija,lo:=3690,hi:=3691);
Read_dWord(dVar:=Circ19KapacitivnaMoc_III,lo:=3692,hi:=3693);
Read_dWord(dVar:=Circ19MaximumDemand,lo:=3694,hi:=3695);
Read_dWord(dVar:=Circ19Napetost_L1_L2,lo:=3696,hi:=3697);
Read_dWord(dVar:=Circ19Napetost_L1_N,lo:=3698,hi:=3699);
Read_dWord(dVar:=Circ19Napetost_L2_L3,lo:=3700,hi:=3701);
Read_dWord(dVar:=Circ19Napetost_L2_N,lo:=3702,hi:=3703);
Read_dWord(dVar:=Circ19Napetost_L3_L1,lo:=3704,hi:=3705);
Read_dWord(dVar:=Circ19Napetost_L3_N,lo:=3706,hi:=3707);
Read_dWord(dVar:=Circ19NavideznaMoc_III,lo:=3708,hi:=3709);
Read_dWord(dVar:=Circ19NicelniTok,lo:=3710,hi:=3711);
Read_dWord(dVar:=Circ19PowerFactor_III,lo:=3712,hi:=3713);
Read_dWord(dVar:=Circ19PowerFactor_L1,lo:=3714,hi:=3715);
Read_dWord(dVar:=Circ19PowerFactor_L2,lo:=3716,hi:=3717);
Read_dWord(dVar:=Circ19PowerFactor_L3,lo:=3718,hi:=3719);
Read_dWord(dVar:=Circ19THDI_L1,lo:=3720,hi:=3721);
Read_dWord(dVar:=Circ19THDI_L2,lo:=3722,hi:=3723);
Read_dWord(dVar:=Circ19THDI_L3,lo:=3724,hi:=3725);
Read_dWord(dVar:=Circ19THDV_L1,lo:=3726,hi:=3727);
Read_dWord(dVar:=Circ19THDV_L2,lo:=3728,hi:=3729);
Read_dWord(dVar:=Circ19THDV_L3,lo:=3730,hi:=3731);
Read_dWord(dVar:=Circ19Tok_L1,lo:=3732,hi:=3733);
Read_dWord(dVar:=Circ19Tok_L2,lo:=3734,hi:=3735);
Read_dWord(dVar:=Circ19Tok_L3,lo:=3736,hi:=3737);
Read_dWord(dVar:=Circ19TokPovprecje_III,lo:=3738,hi:=3739);
Read_dWord(dVar:=Circ1CosFi_III,lo:=3740,hi:=3741);
Read_dWord(dVar:=Circ1DelovnaEnergija,lo:=3742,hi:=3743);
Read_dWord(dVar:=Circ1DelovnaMoc_III,lo:=3744,hi:=3745);
Read_dWord(dVar:=Circ1DelovnaMoc_L1,lo:=3746,hi:=3747);
Read_dWord(dVar:=Circ1DelovnaMoc_L2,lo:=3748,hi:=3749);
Read_dWord(dVar:=Circ1DelovnaMoc_L3,lo:=3750,hi:=3751);
Read_dWord(dVar:=Circ1Frekvenca_L1,lo:=3752,hi:=3753);
Read_dWord(dVar:=Circ1InduktivnaEnergija,lo:=3754,hi:=3755);
Read_dWord(dVar:=Circ1InduktivnaMoc_III,lo:=3756,hi:=3757);
Read_dWord(dVar:=Circ1JalovaMoc_L1,lo:=3758,hi:=3759);
Read_dWord(dVar:=Circ1JalovaMoc_L2,lo:=3760,hi:=3761);
Read_dWord(dVar:=Circ1JalovaMoc_L3,lo:=3762,hi:=3763);
Read_dWord(dVar:=Circ1KapacitivnaEnergija,lo:=3764,hi:=3765);
Read_dWord(dVar:=Circ1KapacitivnaMoc_III,lo:=3766,hi:=3767);
Read_dWord(dVar:=Circ1MaximumDemand,lo:=3768,hi:=3769);
Read_dWord(dVar:=Circ1Napetost_L1_L2,lo:=3770,hi:=3771);
Read_dWord(dVar:=Circ1Napetost_L1_N,lo:=3772,hi:=3773);
Read_dWord(dVar:=Circ1Napetost_L2_L3,lo:=3774,hi:=3775);
Read_dWord(dVar:=Circ1Napetost_L2_N,lo:=3776,hi:=3777);
Read_dWord(dVar:=Circ1Napetost_L3_L1,lo:=3778,hi:=3779);
Read_dWord(dVar:=Circ1Napetost_L3_N,lo:=3780,hi:=3781);
Read_dWord(dVar:=Circ1NavideznaMoc_III,lo:=3782,hi:=3783);
Read_dWord(dVar:=Circ1NicelniTok,lo:=3784,hi:=3785);
Read_dWord(dVar:=Circ1PowerFactor_III,lo:=3786,hi:=3787);
Read_dWord(dVar:=Circ1PowerFactor_L1,lo:=3788,hi:=3789);
Read_dWord(dVar:=Circ1PowerFactor_L2,lo:=3790,hi:=3791);
Read_dWord(dVar:=Circ1PowerFactor_L3,lo:=3792,hi:=3793);
Read_dWord(dVar:=Circ1THDI_L1,lo:=3794,hi:=3795);
Read_dWord(dVar:=Circ1THDI_L2,lo:=3796,hi:=3797);
Read_dWord(dVar:=Circ1THDI_L3,lo:=3798,hi:=3799);
Read_dWord(dVar:=Circ1THDV_L1,lo:=3800,hi:=3801);
Read_dWord(dVar:=Circ1THDV_L2,lo:=3802,hi:=3803);
Read_dWord(dVar:=Circ1THDV_L3,lo:=3804,hi:=3805);
Read_dWord(dVar:=Circ1Tok_L1,lo:=3806,hi:=3807);
Read_dWord(dVar:=Circ1Tok_L2,lo:=3808,hi:=3809);
Read_dWord(dVar:=Circ1Tok_L3,lo:=3810,hi:=3811);
Read_dWord(dVar:=Circ1TokPovprecje_III,lo:=3812,hi:=3813);
Read_dWord(dVar:=Circ20CosFi_III,lo:=3814,hi:=3815);
Read_dWord(dVar:=Circ20DelovnaEnergija,lo:=3816,hi:=3817);
Read_dWord(dVar:=Circ20DelovnaMoc_III,lo:=3818,hi:=3819);
Read_dWord(dVar:=Circ20DelovnaMoc_L1,lo:=3820,hi:=3821);
Read_dWord(dVar:=Circ20DelovnaMoc_L2,lo:=3822,hi:=3823);
Read_dWord(dVar:=Circ20DelovnaMoc_L3,lo:=3824,hi:=3825);
Read_dWord(dVar:=Circ20Frekvenca_L1,lo:=3826,hi:=3827);
Read_dWord(dVar:=Circ20InduktivnaEnergija,lo:=3828,hi:=3829);
Read_dWord(dVar:=Circ20InduktivnaMoc_III,lo:=3830,hi:=3831);
Read_dWord(dVar:=Circ20JalovaMoc_L1,lo:=3832,hi:=3833);
Read_dWord(dVar:=Circ20JalovaMoc_L2,lo:=3834,hi:=3835);
Read_dWord(dVar:=Circ20JalovaMoc_L3,lo:=3836,hi:=3837);
Read_dWord(dVar:=Circ20KapacitivnaEnergija,lo:=3838,hi:=3839);
Read_dWord(dVar:=Circ20KapacitivnaMoc_III,lo:=3840,hi:=3841);
Read_dWord(dVar:=Circ20MaximumDemand,lo:=3842,hi:=3843);
Read_dWord(dVar:=Circ20Napetost_L1_L2,lo:=3844,hi:=3845);
Read_dWord(dVar:=Circ20Napetost_L1_N,lo:=3846,hi:=3847);
Read_dWord(dVar:=Circ20Napetost_L2_L3,lo:=3848,hi:=3849);
Read_dWord(dVar:=Circ20Napetost_L2_N,lo:=3850,hi:=3851);
Read_dWord(dVar:=Circ20Napetost_L3_L1,lo:=3852,hi:=3853);
Read_dWord(dVar:=Circ20Napetost_L3_N,lo:=3854,hi:=3855);
Read_dWord(dVar:=Circ20NavideznaMoc_III,lo:=3856,hi:=3857);
Read_dWord(dVar:=Circ20NicelniTok,lo:=3858,hi:=3859);
Read_dWord(dVar:=Circ20PowerFactor_III,lo:=3860,hi:=3861);
Read_dWord(dVar:=Circ20PowerFactor_L1,lo:=3862,hi:=3863);
Read_dWord(dVar:=Circ20PowerFactor_L2,lo:=3864,hi:=3865);
Read_dWord(dVar:=Circ20PowerFactor_L3,lo:=3866,hi:=3867);
Read_dWord(dVar:=Circ20THDI_L1,lo:=3868,hi:=3869);
Read_dWord(dVar:=Circ20THDI_L2,lo:=3870,hi:=3871);
Read_dWord(dVar:=Circ20THDI_L3,lo:=3872,hi:=3873);
Read_dWord(dVar:=Circ20THDV_L1,lo:=3874,hi:=3875);
Read_dWord(dVar:=Circ20THDV_L2,lo:=3876,hi:=3877);
Read_dWord(dVar:=Circ20THDV_L3,lo:=3878,hi:=3879);
Read_dWord(dVar:=Circ20Tok_L1,lo:=3880,hi:=3881);
Read_dWord(dVar:=Circ20Tok_L2,lo:=3882,hi:=3883);
Read_dWord(dVar:=Circ20Tok_L3,lo:=3884,hi:=3885);
Read_dWord(dVar:=Circ20TokPovprecje_III,lo:=3886,hi:=3887);
Read_dWord(dVar:=Circ21CosFi_III,lo:=3888,hi:=3889);
Read_dWord(dVar:=Circ21DelovnaEnergija,lo:=3890,hi:=3891);
Read_dWord(dVar:=Circ21DelovnaMoc_III,lo:=3892,hi:=3893);
Read_dWord(dVar:=Circ21DelovnaMoc_L1,lo:=3894,hi:=3895);
Read_dWord(dVar:=Circ21DelovnaMoc_L2,lo:=3896,hi:=3897);
Read_dWord(dVar:=Circ21DelovnaMoc_L3,lo:=3898,hi:=3899);
Read_dWord(dVar:=Circ21Frekvenca_L1,lo:=3900,hi:=3901);
Read_dWord(dVar:=Circ21InduktivnaEnergija,lo:=3902,hi:=3903);
Read_dWord(dVar:=Circ21InduktivnaMoc_III,lo:=3904,hi:=3905);
Read_dWord(dVar:=Circ21JalovaMoc_L1,lo:=3906,hi:=3907);
Read_dWord(dVar:=Circ21JalovaMoc_L2,lo:=3908,hi:=3909);
Read_dWord(dVar:=Circ21JalovaMoc_L3,lo:=3910,hi:=3911);
Read_dWord(dVar:=Circ21KapacitivnaEnergija,lo:=3912,hi:=3913);
Read_dWord(dVar:=Circ21KapacitivnaMoc_III,lo:=3914,hi:=3915);
Read_dWord(dVar:=Circ21MaximumDemand,lo:=3916,hi:=3917);
Read_dWord(dVar:=Circ21Napetost_L1_L2,lo:=3918,hi:=3919);
Read_dWord(dVar:=Circ21Napetost_L1_N,lo:=3920,hi:=3921);
Read_dWord(dVar:=Circ21Napetost_L2_L3,lo:=3922,hi:=3923);
Read_dWord(dVar:=Circ21Napetost_L2_N,lo:=3924,hi:=3925);
Read_dWord(dVar:=Circ21Napetost_L3_L1,lo:=3926,hi:=3927);
Read_dWord(dVar:=Circ21Napetost_L3_N,lo:=3928,hi:=3929);
Read_dWord(dVar:=Circ21NavideznaMoc_III,lo:=3930,hi:=3931);
Read_dWord(dVar:=Circ21NicelniTok,lo:=3932,hi:=3933);
Read_dWord(dVar:=Circ21PowerFactor_III,lo:=3934,hi:=3935);
Read_dWord(dVar:=Circ21PowerFactor_L1,lo:=3936,hi:=3937);
Read_dWord(dVar:=Circ21PowerFactor_L2,lo:=3938,hi:=3939);
Read_dWord(dVar:=Circ21PowerFactor_L3,lo:=3940,hi:=3941);
Read_dWord(dVar:=Circ21THDI_L1,lo:=3942,hi:=3943);
Read_dWord(dVar:=Circ21THDI_L2,lo:=3944,hi:=3945);
Read_dWord(dVar:=Circ21THDI_L3,lo:=3946,hi:=3947);
Read_dWord(dVar:=Circ21THDV_L1,lo:=3948,hi:=3949);
Read_dWord(dVar:=Circ21THDV_L2,lo:=3950,hi:=3951);
Read_dWord(dVar:=Circ21THDV_L3,lo:=3952,hi:=3953);
Read_dWord(dVar:=Circ21Tok_L1,lo:=3954,hi:=3955);
Read_dWord(dVar:=Circ21Tok_L2,lo:=3956,hi:=3957);
Read_dWord(dVar:=Circ21Tok_L3,lo:=3958,hi:=3959);
Read_dWord(dVar:=Circ21TokPovprecje_III,lo:=3960,hi:=3961);
Read_dWord(dVar:=Circ22CosFi_III,lo:=3962,hi:=3963);
Read_dWord(dVar:=Circ22DelovnaEnergija,lo:=3964,hi:=3965);
Read_dWord(dVar:=Circ22DelovnaMoc_III,lo:=3966,hi:=3967);
Read_dWord(dVar:=Circ22DelovnaMoc_L1,lo:=3968,hi:=3969);
Read_dWord(dVar:=Circ22DelovnaMoc_L2,lo:=3970,hi:=3971);
Read_dWord(dVar:=Circ22DelovnaMoc_L3,lo:=3972,hi:=3973);
Read_dWord(dVar:=Circ22Frekvenca_L1,lo:=3974,hi:=3975);
Read_dWord(dVar:=Circ22InduktivnaEnergija,lo:=3976,hi:=3977);
Read_dWord(dVar:=Circ22InduktivnaMoc_III,lo:=3978,hi:=3979);
Read_dWord(dVar:=Circ22JalovaMoc_L1,lo:=3980,hi:=3981);
Read_dWord(dVar:=Circ22JalovaMoc_L2,lo:=3982,hi:=3983);
Read_dWord(dVar:=Circ22JalovaMoc_L3,lo:=3984,hi:=3985);
Read_dWord(dVar:=Circ22KapacitivnaEnergija,lo:=3986,hi:=3987);
Read_dWord(dVar:=Circ22KapacitivnaMoc_III,lo:=3988,hi:=3989);
Read_dWord(dVar:=Circ22MaximumDemand,lo:=3990,hi:=3991);
Read_dWord(dVar:=Circ22Napetost_L1_L2,lo:=3992,hi:=3993);
Read_dWord(dVar:=Circ22Napetost_L1_N,lo:=3994,hi:=3995);
Read_dWord(dVar:=Circ22Napetost_L2_L3,lo:=3996,hi:=3997);
Read_dWord(dVar:=Circ22Napetost_L2_N,lo:=3998,hi:=3999);
Read_dWord(dVar:=Circ22Napetost_L3_L1,lo:=4000,hi:=4001);
Read_dWord(dVar:=Circ22Napetost_L3_N,lo:=4002,hi:=4003);
Read_dWord(dVar:=Circ22NavideznaMoc_III,lo:=4004,hi:=4005);
Read_dWord(dVar:=Circ22NicelniTok,lo:=4006,hi:=4007);
Read_dWord(dVar:=Circ22PowerFactor_III,lo:=4008,hi:=4009);
Read_dWord(dVar:=Circ22PowerFactor_L1,lo:=4010,hi:=4011);
Read_dWord(dVar:=Circ22PowerFactor_L2,lo:=4012,hi:=4013);
Read_dWord(dVar:=Circ22PowerFactor_L3,lo:=4014,hi:=4015);
Read_dWord(dVar:=Circ22THDI_L1,lo:=4016,hi:=4017);
Read_dWord(dVar:=Circ22THDI_L2,lo:=4018,hi:=4019);
Read_dWord(dVar:=Circ22THDI_L3,lo:=4020,hi:=4021);
Read_dWord(dVar:=Circ22THDV_L1,lo:=4022,hi:=4023);
Read_dWord(dVar:=Circ22THDV_L2,lo:=4024,hi:=4025);
Read_dWord(dVar:=Circ22THDV_L3,lo:=4026,hi:=4027);
Read_dWord(dVar:=Circ22Tok_L1,lo:=4028,hi:=4029);
Read_dWord(dVar:=Circ22Tok_L2,lo:=4030,hi:=4031);
Read_dWord(dVar:=Circ22Tok_L3,lo:=4032,hi:=4033);
Read_dWord(dVar:=Circ22TokPovprecje_III,lo:=4034,hi:=4035);
Read_dWord(dVar:=Circ23CosFi_III,lo:=4036,hi:=4037);
Read_dWord(dVar:=Circ23DelovnaEnergija,lo:=4038,hi:=4039);
Read_dWord(dVar:=Circ23DelovnaMoc_III,lo:=4040,hi:=4041);
Read_dWord(dVar:=Circ23DelovnaMoc_L1,lo:=4042,hi:=4043);
Read_dWord(dVar:=Circ23DelovnaMoc_L2,lo:=4044,hi:=4045);
Read_dWord(dVar:=Circ23DelovnaMoc_L3,lo:=4046,hi:=4047);
Read_dWord(dVar:=Circ23Frekvenca_L1,lo:=4048,hi:=4049);
Read_dWord(dVar:=Circ23InduktivnaEnergija,lo:=4050,hi:=4051);
Read_dWord(dVar:=Circ23InduktivnaMoc_III,lo:=4052,hi:=4053);
Read_dWord(dVar:=Circ23JalovaMoc_L1,lo:=4054,hi:=4055);
Read_dWord(dVar:=Circ23JalovaMoc_L2,lo:=4056,hi:=4057);
Read_dWord(dVar:=Circ23JalovaMoc_L3,lo:=4058,hi:=4059);
Read_dWord(dVar:=Circ23KapacitivnaEnergija,lo:=4060,hi:=4061);
Read_dWord(dVar:=Circ23KapacitivnaMoc_III,lo:=4062,hi:=4063);
Read_dWord(dVar:=Circ23MaximumDemand,lo:=4064,hi:=4065);
Read_dWord(dVar:=Circ23Napetost_L1_L2,lo:=4066,hi:=4067);
Read_dWord(dVar:=Circ23Napetost_L1_N,lo:=4068,hi:=4069);
Read_dWord(dVar:=Circ23Napetost_L2_L3,lo:=4070,hi:=4071);
Read_dWord(dVar:=Circ23Napetost_L2_N,lo:=4072,hi:=4073);
Read_dWord(dVar:=Circ23Napetost_L3_L1,lo:=4074,hi:=4075);
Read_dWord(dVar:=Circ23Napetost_L3_N,lo:=4076,hi:=4077);
Read_dWord(dVar:=Circ23NavideznaMoc_III,lo:=4078,hi:=4079);
Read_dWord(dVar:=Circ23NicelniTok,lo:=4080,hi:=4081);
Read_dWord(dVar:=Circ23PowerFactor_III,lo:=4082,hi:=4083);
Read_dWord(dVar:=Circ23PowerFactor_L1,lo:=4084,hi:=4085);
Read_dWord(dVar:=Circ23PowerFactor_L2,lo:=4086,hi:=4087);
Read_dWord(dVar:=Circ23PowerFactor_L3,lo:=4088,hi:=4089);
Read_dWord(dVar:=Circ23THDI_L1,lo:=4090,hi:=4091);
Read_dWord(dVar:=Circ23THDI_L2,lo:=4092,hi:=4093);
Read_dWord(dVar:=Circ23THDI_L3,lo:=4094,hi:=4095);
Read_dWord(dVar:=Circ23THDV_L1,lo:=4096,hi:=4097);
Read_dWord(dVar:=Circ23THDV_L2,lo:=4098,hi:=4099);
Read_dWord(dVar:=Circ23THDV_L3,lo:=4100,hi:=4101);
Read_dWord(dVar:=Circ23Tok_L1,lo:=4102,hi:=4103);
Read_dWord(dVar:=Circ23Tok_L2,lo:=4104,hi:=4105);
Read_dWord(dVar:=Circ23Tok_L3,lo:=4106,hi:=4107);
Read_dWord(dVar:=Circ23TokPovprecje_III,lo:=4108,hi:=4109);
Read_dWord(dVar:=Circ24CosFi_III,lo:=4110,hi:=4111);
Read_dWord(dVar:=Circ24DelovnaEnergija,lo:=4112,hi:=4113);
Read_dWord(dVar:=Circ24DelovnaMoc_III,lo:=4114,hi:=4115);
Read_dWord(dVar:=Circ24DelovnaMoc_L1,lo:=4116,hi:=4117);
Read_dWord(dVar:=Circ24DelovnaMoc_L2,lo:=4118,hi:=4119);
Read_dWord(dVar:=Circ24DelovnaMoc_L3,lo:=4120,hi:=4121);
Read_dWord(dVar:=Circ24Frekvenca_L1,lo:=4122,hi:=4123);
Read_dWord(dVar:=Circ24InduktivnaEnergija,lo:=4124,hi:=4125);
Read_dWord(dVar:=Circ24InduktivnaMoc_III,lo:=4126,hi:=4127);
Read_dWord(dVar:=Circ24JalovaMoc_L1,lo:=4128,hi:=4129);
Read_dWord(dVar:=Circ24JalovaMoc_L2,lo:=4130,hi:=4131);
Read_dWord(dVar:=Circ24JalovaMoc_L3,lo:=4132,hi:=4133);
Read_dWord(dVar:=Circ24KapacitivnaEnergija,lo:=4134,hi:=4135);
Read_dWord(dVar:=Circ24KapacitivnaMoc_III,lo:=4136,hi:=4137);
Read_dWord(dVar:=Circ24MaximumDemand,lo:=4138,hi:=4139);
Read_dWord(dVar:=Circ24Napetost_L1_L2,lo:=4140,hi:=4141);
Read_dWord(dVar:=Circ24Napetost_L1_N,lo:=4142,hi:=4143);
Read_dWord(dVar:=Circ24Napetost_L2_L3,lo:=4144,hi:=4145);
Read_dWord(dVar:=Circ24Napetost_L2_N,lo:=4146,hi:=4147);
Read_dWord(dVar:=Circ24Napetost_L3_L1,lo:=4148,hi:=4149);
Read_dWord(dVar:=Circ24Napetost_L3_N,lo:=4150,hi:=4151);
Read_dWord(dVar:=Circ24NavideznaMoc_III,lo:=4152,hi:=4153);
Read_dWord(dVar:=Circ24NicelniTok,lo:=4154,hi:=4155);
Read_dWord(dVar:=Circ24PowerFactor_III,lo:=4156,hi:=4157);
Read_dWord(dVar:=Circ24PowerFactor_L1,lo:=4158,hi:=4159);
Read_dWord(dVar:=Circ24PowerFactor_L2,lo:=4160,hi:=4161);
Read_dWord(dVar:=Circ24PowerFactor_L3,lo:=4162,hi:=4163);
Read_dWord(dVar:=Circ24THDI_L1,lo:=4164,hi:=4165);
Read_dWord(dVar:=Circ24THDI_L2,lo:=4166,hi:=4167);
Read_dWord(dVar:=Circ24THDI_L3,lo:=4168,hi:=4169);
Read_dWord(dVar:=Circ24THDV_L1,lo:=4170,hi:=4171);
Read_dWord(dVar:=Circ24THDV_L2,lo:=4172,hi:=4173);
Read_dWord(dVar:=Circ24THDV_L3,lo:=4174,hi:=4175);
Read_dWord(dVar:=Circ24Tok_L1,lo:=4176,hi:=4177);
Read_dWord(dVar:=Circ24Tok_L2,lo:=4178,hi:=4179);
Read_dWord(dVar:=Circ24Tok_L3,lo:=4180,hi:=4181);
Read_dWord(dVar:=Circ24TokPovprecje_III,lo:=4182,hi:=4183);
Read_dWord(dVar:=Circ25CosFi_III,lo:=4184,hi:=4185);
Read_dWord(dVar:=Circ25DelovnaEnergija,lo:=4186,hi:=4187);
Read_dWord(dVar:=Circ25DelovnaMoc_III,lo:=4188,hi:=4189);
Read_dWord(dVar:=Circ25DelovnaMoc_L1,lo:=4190,hi:=4191);
Read_dWord(dVar:=Circ25DelovnaMoc_L2,lo:=4192,hi:=4193);
Read_dWord(dVar:=Circ25DelovnaMoc_L3,lo:=4194,hi:=4195);
Read_dWord(dVar:=Circ25Frekvenca_L1,lo:=4196,hi:=4197);
Read_dWord(dVar:=Circ25InduktivnaEnergija,lo:=4198,hi:=4199);
Read_dWord(dVar:=Circ25InduktivnaMoc_III,lo:=4200,hi:=4201);
Read_dWord(dVar:=Circ25JalovaMoc_L1,lo:=4202,hi:=4203);
Read_dWord(dVar:=Circ25JalovaMoc_L2,lo:=4204,hi:=4205);
Read_dWord(dVar:=Circ25JalovaMoc_L3,lo:=4206,hi:=4207);
Read_dWord(dVar:=Circ25KapacitivnaEnergija,lo:=4208,hi:=4209);
Read_dWord(dVar:=Circ25KapacitivnaMoc_III,lo:=4210,hi:=4211);
Read_dWord(dVar:=Circ25MaximumDemand,lo:=4212,hi:=4213);
Read_dWord(dVar:=Circ25Napetost_L1_L2,lo:=4214,hi:=4215);
Read_dWord(dVar:=Circ25Napetost_L1_N,lo:=4216,hi:=4217);
Read_dWord(dVar:=Circ25Napetost_L2_L3,lo:=4218,hi:=4219);
Read_dWord(dVar:=Circ25Napetost_L2_N,lo:=4220,hi:=4221);
Read_dWord(dVar:=Circ25Napetost_L3_L1,lo:=4222,hi:=4223);
Read_dWord(dVar:=Circ25Napetost_L3_N,lo:=4224,hi:=4225);
Read_dWord(dVar:=Circ25NavideznaMoc_III,lo:=4226,hi:=4227);
Read_dWord(dVar:=Circ25NicelniTok,lo:=4228,hi:=4229);
Read_dWord(dVar:=Circ25PowerFactor_III,lo:=4230,hi:=4231);
Read_dWord(dVar:=Circ25PowerFactor_L1,lo:=4232,hi:=4233);
Read_dWord(dVar:=Circ25PowerFactor_L2,lo:=4234,hi:=4235);
Read_dWord(dVar:=Circ25PowerFactor_L3,lo:=4236,hi:=4237);
Read_dWord(dVar:=Circ25THDI_L1,lo:=4238,hi:=4239);
Read_dWord(dVar:=Circ25THDI_L2,lo:=4240,hi:=4241);
Read_dWord(dVar:=Circ25THDI_L3,lo:=4242,hi:=4243);
Read_dWord(dVar:=Circ25THDV_L1,lo:=4244,hi:=4245);
Read_dWord(dVar:=Circ25THDV_L2,lo:=4246,hi:=4247);
Read_dWord(dVar:=Circ25THDV_L3,lo:=4248,hi:=4249);
Read_dWord(dVar:=Circ25Tok_L1,lo:=4250,hi:=4251);
Read_dWord(dVar:=Circ25Tok_L2,lo:=4252,hi:=4253);
Read_dWord(dVar:=Circ25Tok_L3,lo:=4254,hi:=4255);
Read_dWord(dVar:=Circ25TokPovprecje_III,lo:=4256,hi:=4257);
Read_dWord(dVar:=Circ2CosFi_III,lo:=4258,hi:=4259);
Read_dWord(dVar:=Circ2DelovnaEnergija,lo:=4260,hi:=4261);
Read_dWord(dVar:=Circ2DelovnaMoc_III,lo:=4262,hi:=4263);
Read_dWord(dVar:=Circ2DelovnaMoc_L1,lo:=4264,hi:=4265);
Read_dWord(dVar:=Circ2DelovnaMoc_L2,lo:=4266,hi:=4267);
Read_dWord(dVar:=Circ2DelovnaMoc_L3,lo:=4268,hi:=4269);
Read_dWord(dVar:=Circ2Frekvenca_L1,lo:=4270,hi:=4271);
Read_dWord(dVar:=Circ2InduktivnaEnergija,lo:=4272,hi:=4273);
Read_dWord(dVar:=Circ2InduktivnaMoc_III,lo:=4274,hi:=4275);
Read_dWord(dVar:=Circ2JalovaMoc_L1,lo:=4276,hi:=4277);
Read_dWord(dVar:=Circ2JalovaMoc_L2,lo:=4278,hi:=4279);
Read_dWord(dVar:=Circ2JalovaMoc_L3,lo:=4280,hi:=4281);
Read_dWord(dVar:=Circ2KapacitivnaEnergija,lo:=4282,hi:=4283);
Read_dWord(dVar:=Circ2KapacitivnaMoc_III,lo:=4284,hi:=4285);
Read_dWord(dVar:=Circ2MaximumDemand,lo:=4286,hi:=4287);
Read_dWord(dVar:=Circ2Napetost_L1_L2,lo:=4288,hi:=4289);
Read_dWord(dVar:=Circ2Napetost_L1_N,lo:=4290,hi:=4291);
Read_dWord(dVar:=Circ2Napetost_L2_L3,lo:=4292,hi:=4293);
Read_dWord(dVar:=Circ2Napetost_L2_N,lo:=4294,hi:=4295);
Read_dWord(dVar:=Circ2Napetost_L3_L1,lo:=4296,hi:=4297);
Read_dWord(dVar:=Circ2Napetost_L3_N,lo:=4298,hi:=4299);
Read_dWord(dVar:=Circ2NavideznaMoc_III,lo:=4300,hi:=4301);
Read_dWord(dVar:=Circ2NicelniTok,lo:=4302,hi:=4303);
Read_dWord(dVar:=Circ2PowerFactor_III,lo:=4304,hi:=4305);
Read_dWord(dVar:=Circ2PowerFactor_L1,lo:=4306,hi:=4307);
Read_dWord(dVar:=Circ2PowerFactor_L2,lo:=4308,hi:=4309);
Read_dWord(dVar:=Circ2PowerFactor_L3,lo:=4310,hi:=4311);
Read_dWord(dVar:=Circ2THDI_L1,lo:=4312,hi:=4313);
Read_dWord(dVar:=Circ2THDI_L2,lo:=4314,hi:=4315);
Read_dWord(dVar:=Circ2THDI_L3,lo:=4316,hi:=4317);
Read_dWord(dVar:=Circ2THDV_L1,lo:=4318,hi:=4319);
Read_dWord(dVar:=Circ2THDV_L2,lo:=4320,hi:=4321);
Read_dWord(dVar:=Circ2THDV_L3,lo:=4322,hi:=4323);
Read_dWord(dVar:=Circ2Tok_L1,lo:=4324,hi:=4325);
Read_dWord(dVar:=Circ2Tok_L2,lo:=4326,hi:=4327);
Read_dWord(dVar:=Circ2Tok_L3,lo:=4328,hi:=4329);
Read_dWord(dVar:=Circ2TokPovprecje_III,lo:=4330,hi:=4331);
Read_dWord(dVar:=Circ3CosFi_III,lo:=4332,hi:=4333);
Read_dWord(dVar:=Circ3DelovnaEnergija,lo:=4334,hi:=4335);
Read_dWord(dVar:=Circ3DelovnaMoc_III,lo:=4336,hi:=4337);
Read_dWord(dVar:=Circ3DelovnaMoc_L1,lo:=4338,hi:=4339);
Read_dWord(dVar:=Circ3DelovnaMoc_L2,lo:=4340,hi:=4341);
Read_dWord(dVar:=Circ3DelovnaMoc_L3,lo:=4342,hi:=4343);
Read_dWord(dVar:=Circ3Frekvenca_L1,lo:=4344,hi:=4345);
Read_dWord(dVar:=Circ3InduktivnaEnergija,lo:=4346,hi:=4347);
Read_dWord(dVar:=Circ3InduktivnaMoc_III,lo:=4348,hi:=4349);
Read_dWord(dVar:=Circ3JalovaMoc_L1,lo:=4350,hi:=4351);
Read_dWord(dVar:=Circ3JalovaMoc_L2,lo:=4352,hi:=4353);
Read_dWord(dVar:=Circ3JalovaMoc_L3,lo:=4354,hi:=4355);
Read_dWord(dVar:=Circ3KapacitivnaEnergija,lo:=4356,hi:=4357);
Read_dWord(dVar:=Circ3KapacitivnaMoc_III,lo:=4358,hi:=4359);
Read_dWord(dVar:=Circ3MaximumDemand,lo:=4360,hi:=4361);
Read_dWord(dVar:=Circ3Napetost_L1_L2,lo:=4362,hi:=4363);
Read_dWord(dVar:=Circ3Napetost_L1_N,lo:=4364,hi:=4365);
Read_dWord(dVar:=Circ3Napetost_L2_L3,lo:=4366,hi:=4367);
Read_dWord(dVar:=Circ3Napetost_L2_N,lo:=4368,hi:=4369);
Read_dWord(dVar:=Circ3Napetost_L3_L1,lo:=4370,hi:=4371);
Read_dWord(dVar:=Circ3Napetost_L3_N,lo:=4372,hi:=4373);
Read_dWord(dVar:=Circ3NavideznaMoc_III,lo:=4374,hi:=4375);
Read_dWord(dVar:=Circ3NicelniTok,lo:=4376,hi:=4377);
Read_dWord(dVar:=Circ3PowerFactor_III,lo:=4378,hi:=4379);
Read_dWord(dVar:=Circ3PowerFactor_L1,lo:=4380,hi:=4381);
Read_dWord(dVar:=Circ3PowerFactor_L2,lo:=4382,hi:=4383);
Read_dWord(dVar:=Circ3PowerFactor_L3,lo:=4384,hi:=4385);
Read_dWord(dVar:=Circ3THDI_L1,lo:=4386,hi:=4387);
Read_dWord(dVar:=Circ3THDI_L2,lo:=4388,hi:=4389);
Read_dWord(dVar:=Circ3THDI_L3,lo:=4390,hi:=4391);
Read_dWord(dVar:=Circ3THDV_L1,lo:=4392,hi:=4393);
Read_dWord(dVar:=Circ3THDV_L2,lo:=4394,hi:=4395);
Read_dWord(dVar:=Circ3THDV_L3,lo:=4396,hi:=4397);
Read_dWord(dVar:=Circ3Tok_L1,lo:=4398,hi:=4399);
Read_dWord(dVar:=Circ3Tok_L2,lo:=4400,hi:=4401);
Read_dWord(dVar:=Circ3Tok_L3,lo:=4402,hi:=4403);
Read_dWord(dVar:=Circ3TokPovprecje_III,lo:=4404,hi:=4405);
Read_dWord(dVar:=Circ4CosFi_III,lo:=4406,hi:=4407);
Read_dWord(dVar:=Circ4DelovnaEnergija,lo:=4408,hi:=4409);
Read_dWord(dVar:=Circ4DelovnaMoc_III,lo:=4410,hi:=4411);
Read_dWord(dVar:=Circ4DelovnaMoc_L1,lo:=4412,hi:=4413);
Read_dWord(dVar:=Circ4DelovnaMoc_L2,lo:=4414,hi:=4415);
Read_dWord(dVar:=Circ4DelovnaMoc_L3,lo:=4416,hi:=4417);
Read_dWord(dVar:=Circ4Frekvenca_L1,lo:=4418,hi:=4419);
Read_dWord(dVar:=Circ4InduktivnaEnergija,lo:=4420,hi:=4421);
Read_dWord(dVar:=Circ4InduktivnaMoc_III,lo:=4422,hi:=4423);
Read_dWord(dVar:=Circ4JalovaMoc_L1,lo:=4424,hi:=4425);
Read_dWord(dVar:=Circ4JalovaMoc_L2,lo:=4426,hi:=4427);
Read_dWord(dVar:=Circ4JalovaMoc_L3,lo:=4428,hi:=4429);
Read_dWord(dVar:=Circ4KapacitivnaEnergija,lo:=4430,hi:=4431);
Read_dWord(dVar:=Circ4KapacitivnaMoc_III,lo:=4432,hi:=4433);
Read_dWord(dVar:=Circ4MaximumDemand,lo:=4434,hi:=4435);
Read_dWord(dVar:=Circ4Napetost_L1_L2,lo:=4436,hi:=4437);
Read_dWord(dVar:=Circ4Napetost_L1_N,lo:=4438,hi:=4439);
Read_dWord(dVar:=Circ4Napetost_L2_L3,lo:=4440,hi:=4441);
Read_dWord(dVar:=Circ4Napetost_L2_N,lo:=4442,hi:=4443);
Read_dWord(dVar:=Circ4Napetost_L3_L1,lo:=4444,hi:=4445);
Read_dWord(dVar:=Circ4Napetost_L3_N,lo:=4446,hi:=4447);
Read_dWord(dVar:=Circ4NavideznaMoc_III,lo:=4448,hi:=4449);
Read_dWord(dVar:=Circ4NicelniTok,lo:=4450,hi:=4451);
Read_dWord(dVar:=Circ4PowerFactor_III,lo:=4452,hi:=4453);
Read_dWord(dVar:=Circ4PowerFactor_L1,lo:=4454,hi:=4455);
Read_dWord(dVar:=Circ4PowerFactor_L2,lo:=4456,hi:=4457);
Read_dWord(dVar:=Circ4PowerFactor_L3,lo:=4458,hi:=4459);
Read_dWord(dVar:=Circ4THDI_L1,lo:=4460,hi:=4461);
Read_dWord(dVar:=Circ4THDI_L2,lo:=4462,hi:=4463);
Read_dWord(dVar:=Circ4THDI_L3,lo:=4464,hi:=4465);
Read_dWord(dVar:=Circ4THDV_L1,lo:=4466,hi:=4467);
Read_dWord(dVar:=Circ4THDV_L2,lo:=4468,hi:=4469);
Read_dWord(dVar:=Circ4THDV_L3,lo:=4470,hi:=4471);
Read_dWord(dVar:=Circ4Tok_L1,lo:=4472,hi:=4473);
Read_dWord(dVar:=Circ4Tok_L2,lo:=4474,hi:=4475);
Read_dWord(dVar:=Circ4Tok_L3,lo:=4476,hi:=4477);
Read_dWord(dVar:=Circ4TokPovprecje_III,lo:=4478,hi:=4479);
Read_dWord(dVar:=Circ5CosFi_III,lo:=4480,hi:=4481);
Read_dWord(dVar:=Circ5DelovnaEnergija,lo:=4482,hi:=4483);
Read_dWord(dVar:=Circ5DelovnaMoc_III,lo:=4484,hi:=4485);
Read_dWord(dVar:=Circ5DelovnaMoc_L1,lo:=4486,hi:=4487);
Read_dWord(dVar:=Circ5DelovnaMoc_L2,lo:=4488,hi:=4489);
Read_dWord(dVar:=Circ5DelovnaMoc_L3,lo:=4490,hi:=4491);
Read_dWord(dVar:=Circ5Frekvenca_L1,lo:=4492,hi:=4493);
Read_dWord(dVar:=Circ5InduktivnaEnergija,lo:=4494,hi:=4495);
Read_dWord(dVar:=Circ5InduktivnaMoc_III,lo:=4496,hi:=4497);
Read_dWord(dVar:=Circ5JalovaMoc_L1,lo:=4498,hi:=4499);
Read_dWord(dVar:=Circ5JalovaMoc_L2,lo:=4500,hi:=4501);
Read_dWord(dVar:=Circ5JalovaMoc_L3,lo:=4502,hi:=4503);
Read_dWord(dVar:=Circ5KapacitivnaEnergija,lo:=4504,hi:=4505);
Read_dWord(dVar:=Circ5KapacitivnaMoc_III,lo:=4506,hi:=4507);
Read_dWord(dVar:=Circ5MaximumDemand,lo:=4508,hi:=4509);
Read_dWord(dVar:=Circ5Napetost_L1_L2,lo:=4510,hi:=4511);
Read_dWord(dVar:=Circ5Napetost_L1_N,lo:=4512,hi:=4513);
Read_dWord(dVar:=Circ5Napetost_L2_L3,lo:=4514,hi:=4515);
Read_dWord(dVar:=Circ5Napetost_L2_N,lo:=4516,hi:=4517);
Read_dWord(dVar:=Circ5Napetost_L3_L1,lo:=4518,hi:=4519);
Read_dWord(dVar:=Circ5Napetost_L3_N,lo:=4520,hi:=4521);
Read_dWord(dVar:=Circ5NavideznaMoc_III,lo:=4522,hi:=4523);
Read_dWord(dVar:=Circ5NicelniTok,lo:=4524,hi:=4525);
Read_dWord(dVar:=Circ5PowerFactor_III,lo:=4526,hi:=4527);
Read_dWord(dVar:=Circ5PowerFactor_L1,lo:=4528,hi:=4529);
Read_dWord(dVar:=Circ5PowerFactor_L2,lo:=4530,hi:=4531);
Read_dWord(dVar:=Circ5PowerFactor_L3,lo:=4532,hi:=4533);
Read_dWord(dVar:=Circ5THDI_L1,lo:=4534,hi:=4535);
Read_dWord(dVar:=Circ5THDI_L2,lo:=4536,hi:=4537);
Read_dWord(dVar:=Circ5THDI_L3,lo:=4538,hi:=4539);
Read_dWord(dVar:=Circ5THDV_L1,lo:=4540,hi:=4541);
Read_dWord(dVar:=Circ5THDV_L2,lo:=4542,hi:=4543);
Read_dWord(dVar:=Circ5THDV_L3,lo:=4544,hi:=4545);
Read_dWord(dVar:=Circ5Tok_L1,lo:=4546,hi:=4547);
Read_dWord(dVar:=Circ5Tok_L2,lo:=4548,hi:=4549);
Read_dWord(dVar:=Circ5Tok_L3,lo:=4550,hi:=4551);
Read_dWord(dVar:=Circ5TokPovprecje_III,lo:=4552,hi:=4553);
Read_dWord(dVar:=Circ6CosFi_III,lo:=4554,hi:=4555);
Read_dWord(dVar:=Circ6DelovnaEnergija,lo:=4556,hi:=4557);
Read_dWord(dVar:=Circ6DelovnaMoc_III,lo:=4558,hi:=4559);
Read_dWord(dVar:=Circ6DelovnaMoc_L1,lo:=4560,hi:=4561);
Read_dWord(dVar:=Circ6DelovnaMoc_L2,lo:=4562,hi:=4563);
Read_dWord(dVar:=Circ6DelovnaMoc_L3,lo:=4564,hi:=4565);
Read_dWord(dVar:=Circ6Frekvenca_L1,lo:=4566,hi:=4567);
Read_dWord(dVar:=Circ6InduktivnaEnergija,lo:=4568,hi:=4569);
Read_dWord(dVar:=Circ6InduktivnaMoc_III,lo:=4570,hi:=4571);
Read_dWord(dVar:=Circ6JalovaMoc_L1,lo:=4572,hi:=4573);
Read_dWord(dVar:=Circ6JalovaMoc_L2,lo:=4574,hi:=4575);
Read_dWord(dVar:=Circ6JalovaMoc_L3,lo:=4576,hi:=4577);
Read_dWord(dVar:=Circ6KapacitivnaEnergija,lo:=4578,hi:=4579);
Read_dWord(dVar:=Circ6KapacitivnaMoc_III,lo:=4580,hi:=4581);
Read_dWord(dVar:=Circ6MaximumDemand,lo:=4582,hi:=4583);
Read_dWord(dVar:=Circ6Napetost_L1_L2,lo:=4584,hi:=4585);
Read_dWord(dVar:=Circ6Napetost_L1_N,lo:=4586,hi:=4587);
Read_dWord(dVar:=Circ6Napetost_L2_L3,lo:=4588,hi:=4589);
Read_dWord(dVar:=Circ6Napetost_L2_N,lo:=4590,hi:=4591);
Read_dWord(dVar:=Circ6Napetost_L3_L1,lo:=4592,hi:=4593);
Read_dWord(dVar:=Circ6Napetost_L3_N,lo:=4594,hi:=4595);
Read_dWord(dVar:=Circ6NavideznaMoc_III,lo:=4596,hi:=4597);
Read_dWord(dVar:=Circ6NicelniTok,lo:=4598,hi:=4599);
Read_dWord(dVar:=Circ6PowerFactor_III,lo:=4600,hi:=4601);
Read_dWord(dVar:=Circ6PowerFactor_L1,lo:=4602,hi:=4603);
Read_dWord(dVar:=Circ6PowerFactor_L2,lo:=4604,hi:=4605);
Read_dWord(dVar:=Circ6PowerFactor_L3,lo:=4606,hi:=4607);
Read_dWord(dVar:=Circ6THDI_L1,lo:=4608,hi:=4609);
Read_dWord(dVar:=Circ6THDI_L2,lo:=4610,hi:=4611);
Read_dWord(dVar:=Circ6THDI_L3,lo:=4612,hi:=4613);
Read_dWord(dVar:=Circ6THDV_L1,lo:=4614,hi:=4615);
Read_dWord(dVar:=Circ6THDV_L2,lo:=4616,hi:=4617);
Read_dWord(dVar:=Circ6THDV_L3,lo:=4618,hi:=4619);
Read_dWord(dVar:=Circ6Tok_L1,lo:=4620,hi:=4621);
Read_dWord(dVar:=Circ6Tok_L2,lo:=4622,hi:=4623);
Read_dWord(dVar:=Circ6Tok_L3,lo:=4624,hi:=4625);
Read_dWord(dVar:=Circ6TokPovprecje_III,lo:=4626,hi:=4627);
Read_dWord(dVar:=Circ7CosFi_III,lo:=4628,hi:=4629);
Read_dWord(dVar:=Circ7DelovnaEnergija,lo:=4630,hi:=4631);
Read_dWord(dVar:=Circ7DelovnaMoc_III,lo:=4632,hi:=4633);
Read_dWord(dVar:=Circ7DelovnaMoc_L1,lo:=4634,hi:=4635);
Read_dWord(dVar:=Circ7DelovnaMoc_L2,lo:=4636,hi:=4637);
Read_dWord(dVar:=Circ7DelovnaMoc_L3,lo:=4638,hi:=4639);
Read_dWord(dVar:=Circ7Frekvenca_L1,lo:=4640,hi:=4641);
Read_dWord(dVar:=Circ7InduktivnaEnergija,lo:=4642,hi:=4643);
Read_dWord(dVar:=Circ7InduktivnaMoc_III,lo:=4644,hi:=4645);
Read_dWord(dVar:=Circ7JalovaMoc_L1,lo:=4646,hi:=4647);
Read_dWord(dVar:=Circ7JalovaMoc_L2,lo:=4648,hi:=4649);
Read_dWord(dVar:=Circ7JalovaMoc_L3,lo:=4650,hi:=4651);
Read_dWord(dVar:=Circ7KapacitivnaEnergija,lo:=4652,hi:=4653);
Read_dWord(dVar:=Circ7KapacitivnaMoc_III,lo:=4654,hi:=4655);
Read_dWord(dVar:=Circ7MaximumDemand,lo:=4656,hi:=4657);
Read_dWord(dVar:=Circ7Napetost_L1_L2,lo:=4658,hi:=4659);
Read_dWord(dVar:=Circ7Napetost_L1_N,lo:=4660,hi:=4661);
Read_dWord(dVar:=Circ7Napetost_L2_L3,lo:=4662,hi:=4663);
Read_dWord(dVar:=Circ7Napetost_L2_N,lo:=4664,hi:=4665);
Read_dWord(dVar:=Circ7Napetost_L3_L1,lo:=4666,hi:=4667);
Read_dWord(dVar:=Circ7Napetost_L3_N,lo:=4668,hi:=4669);
Read_dWord(dVar:=Circ7NavideznaMoc_III,lo:=4670,hi:=4671);
Read_dWord(dVar:=Circ7NicelniTok,lo:=4672,hi:=4673);
Read_dWord(dVar:=Circ7PowerFactor_III,lo:=4674,hi:=4675);
Read_dWord(dVar:=Circ7PowerFactor_L1,lo:=4676,hi:=4677);
Read_dWord(dVar:=Circ7PowerFactor_L2,lo:=4678,hi:=4679);
Read_dWord(dVar:=Circ7PowerFactor_L3,lo:=4680,hi:=4681);
Read_dWord(dVar:=Circ7THDI_L1,lo:=4682,hi:=4683);
Read_dWord(dVar:=Circ7THDI_L2,lo:=4684,hi:=4685);
Read_dWord(dVar:=Circ7THDI_L3,lo:=4686,hi:=4687);
Read_dWord(dVar:=Circ7THDV_L1,lo:=4688,hi:=4689);
Read_dWord(dVar:=Circ7THDV_L2,lo:=4690,hi:=4691);
Read_dWord(dVar:=Circ7THDV_L3,lo:=4692,hi:=4693);
Read_dWord(dVar:=Circ7Tok_L1,lo:=4694,hi:=4695);
Read_dWord(dVar:=Circ7Tok_L2,lo:=4696,hi:=4697);
Read_dWord(dVar:=Circ7Tok_L3,lo:=4698,hi:=4699);
Read_dWord(dVar:=Circ7TokPovprecje_III,lo:=4700,hi:=4701);
Read_dWord(dVar:=Circ8CosFi_III,lo:=4702,hi:=4703);
Read_dWord(dVar:=Circ8DelovnaEnergija,lo:=4704,hi:=4705);
Read_dWord(dVar:=Circ8DelovnaMoc_III,lo:=4706,hi:=4707);
Read_dWord(dVar:=Circ8DelovnaMoc_L1,lo:=4708,hi:=4709);
Read_dWord(dVar:=Circ8DelovnaMoc_L2,lo:=4710,hi:=4711);
Read_dWord(dVar:=Circ8DelovnaMoc_L3,lo:=4712,hi:=4713);
Read_dWord(dVar:=Circ8Frekvenca_L1,lo:=4714,hi:=4715);
Read_dWord(dVar:=Circ8InduktivnaEnergija,lo:=4716,hi:=4717);
Read_dWord(dVar:=Circ8InduktivnaMoc_III,lo:=4718,hi:=4719);
Read_dWord(dVar:=Circ8JalovaMoc_L1,lo:=4720,hi:=4721);
Read_dWord(dVar:=Circ8JalovaMoc_L2,lo:=4722,hi:=4723);
Read_dWord(dVar:=Circ8JalovaMoc_L3,lo:=4724,hi:=4725);
Read_dWord(dVar:=Circ8KapacitivnaEnergija,lo:=4726,hi:=4727);
Read_dWord(dVar:=Circ8KapacitivnaMoc_III,lo:=4728,hi:=4729);
Read_dWord(dVar:=Circ8MaximumDemand,lo:=4730,hi:=4731);
Read_dWord(dVar:=Circ8Napetost_L1_L2,lo:=4732,hi:=4733);
Read_dWord(dVar:=Circ8Napetost_L1_N,lo:=4734,hi:=4735);
Read_dWord(dVar:=Circ8Napetost_L2_L3,lo:=4736,hi:=4737);
Read_dWord(dVar:=Circ8Napetost_L2_N,lo:=4738,hi:=4739);
Read_dWord(dVar:=Circ8Napetost_L3_L1,lo:=4740,hi:=4741);
Read_dWord(dVar:=Circ8Napetost_L3_N,lo:=4742,hi:=4743);
Read_dWord(dVar:=Circ8NavideznaMoc_III,lo:=4744,hi:=4745);
Read_dWord(dVar:=Circ8NicelniTok,lo:=4746,hi:=4747);
Read_dWord(dVar:=Circ8PowerFactor_III,lo:=4748,hi:=4749);
Read_dWord(dVar:=Circ8PowerFactor_L1,lo:=4750,hi:=4751);
Read_dWord(dVar:=Circ8PowerFactor_L2,lo:=4752,hi:=4753);
Read_dWord(dVar:=Circ8PowerFactor_L3,lo:=4754,hi:=4755);
Read_dWord(dVar:=Circ8THDI_L1,lo:=4756,hi:=4757);
Read_dWord(dVar:=Circ8THDI_L2,lo:=4758,hi:=4759);
Read_dWord(dVar:=Circ8THDI_L3,lo:=4760,hi:=4761);
Read_dWord(dVar:=Circ8THDV_L1,lo:=4762,hi:=4763);
Read_dWord(dVar:=Circ8THDV_L2,lo:=4764,hi:=4765);
Read_dWord(dVar:=Circ8THDV_L3,lo:=4766,hi:=4767);
Read_dWord(dVar:=Circ8Tok_L1,lo:=4768,hi:=4769);
Read_dWord(dVar:=Circ8Tok_L2,lo:=4770,hi:=4771);
Read_dWord(dVar:=Circ8Tok_L3,lo:=4772,hi:=4773);
Read_dWord(dVar:=Circ8TokPovprecje_III,lo:=4774,hi:=4775);
Read_dWord(dVar:=Circ9CosFi_III,lo:=4776,hi:=4777);
Read_dWord(dVar:=Circ9DelovnaEnergija,lo:=4778,hi:=4779);
Read_dWord(dVar:=Circ9DelovnaMoc_III,lo:=4780,hi:=4781);
Read_dWord(dVar:=Circ9DelovnaMoc_L1,lo:=4782,hi:=4783);
Read_dWord(dVar:=Circ9DelovnaMoc_L2,lo:=4784,hi:=4785);
Read_dWord(dVar:=Circ9DelovnaMoc_L3,lo:=4786,hi:=4787);
Read_dWord(dVar:=Circ9Frekvenca_L1,lo:=4788,hi:=4789);
Read_dWord(dVar:=Circ9InduktivnaEnergija,lo:=4790,hi:=4791);
Read_dWord(dVar:=Circ9InduktivnaMoc_III,lo:=4792,hi:=4793);
Read_dWord(dVar:=Circ9JalovaMoc_L1,lo:=4794,hi:=4795);
Read_dWord(dVar:=Circ9JalovaMoc_L2,lo:=4796,hi:=4797);
Read_dWord(dVar:=Circ9JalovaMoc_L3,lo:=4798,hi:=4799);
Read_dWord(dVar:=Circ9KapacitivnaEnergija,lo:=4800,hi:=4801);
Read_dWord(dVar:=Circ9KapacitivnaMoc_III,lo:=4802,hi:=4803);
Read_dWord(dVar:=Circ9MaximumDemand,lo:=4804,hi:=4805);
Read_dWord(dVar:=Circ9Napetost_L1_L2,lo:=4806,hi:=4807);
Read_dWord(dVar:=Circ9Napetost_L1_N,lo:=4808,hi:=4809);
Read_dWord(dVar:=Circ9Napetost_L2_L3,lo:=4810,hi:=4811);
Read_dWord(dVar:=Circ9Napetost_L2_N,lo:=4812,hi:=4813);
Read_dWord(dVar:=Circ9Napetost_L3_L1,lo:=4814,hi:=4815);
Read_dWord(dVar:=Circ9Napetost_L3_N,lo:=4816,hi:=4817);
Read_dWord(dVar:=Circ9NavideznaMoc_III,lo:=4818,hi:=4819);
Read_dWord(dVar:=Circ9NicelniTok,lo:=4820,hi:=4821);
Read_dWord(dVar:=Circ9PowerFactor_III,lo:=4822,hi:=4823);
Read_dWord(dVar:=Circ9PowerFactor_L1,lo:=4824,hi:=4825);
Read_dWord(dVar:=Circ9PowerFactor_L2,lo:=4826,hi:=4827);
Read_dWord(dVar:=Circ9PowerFactor_L3,lo:=4828,hi:=4829);
Read_dWord(dVar:=Circ9THDI_L1,lo:=4830,hi:=4831);
Read_dWord(dVar:=Circ9THDI_L2,lo:=4832,hi:=4833);
Read_dWord(dVar:=Circ9THDI_L3,lo:=4834,hi:=4835);
Read_dWord(dVar:=Circ9THDV_L1,lo:=4836,hi:=4837);
Read_dWord(dVar:=Circ9THDV_L2,lo:=4838,hi:=4839);
Read_dWord(dVar:=Circ9THDV_L3,lo:=4840,hi:=4841);
Read_dWord(dVar:=Circ9Tok_L1,lo:=4842,hi:=4843);
Read_dWord(dVar:=Circ9Tok_L2,lo:=4844,hi:=4845);
Read_dWord(dVar:=Circ9Tok_L3,lo:=4846,hi:=4847);
Read_dWord(dVar:=Circ9TokPovprecje_III,lo:=4848,hi:=4849);
Read_dWord(dVar:=DW_Napake1,lo:=4850,hi:=4851);
Read_dWord(dVar:=DW_Napake2,lo:=4852,hi:=4853);
Read_dWord(dVar:=DW_Napake3,lo:=4854,hi:=4855);
Read_dWord(dVar:=Generator_earth_currentA1,lo:=4856,hi:=4857);
Read_dWord(dVar:=Generator_earth_currentA2,lo:=4858,hi:=4859);
Read_dWord(dVar:=Generator_L1_currentA1,lo:=4860,hi:=4861);
Read_dWord(dVar:=Generator_L1_currentA2,lo:=4862,hi:=4863);
Read_dWord(dVar:=Generator_L1_L2_voltageA1,lo:=4864,hi:=4865);
Read_dWord(dVar:=Generator_L1_L2_voltageA2,lo:=4866,hi:=4867);
Read_dWord(dVar:=Generator_L1_N_voltageA1,lo:=4868,hi:=4869);
Read_dWord(dVar:=Generator_L1_N_voltageA2,lo:=4870,hi:=4871);
Read_dWord(dVar:=Generator_L1_wattsA1,lo:=4872,hi:=4873);
Read_dWord(dVar:=Generator_L1_wattsA2,lo:=4874,hi:=4875);
Read_dWord(dVar:=Generator_L2_currentA1,lo:=4876,hi:=4877);
Read_dWord(dVar:=Generator_L2_currentA2,lo:=4878,hi:=4879);
Read_dWord(dVar:=Generator_L2_L3_voltageA1,lo:=4880,hi:=4881);
Read_dWord(dVar:=Generator_L2_L3_voltageA2,lo:=4882,hi:=4883);
Read_dWord(dVar:=Generator_L2_N_voltageA1,lo:=4884,hi:=4885);
Read_dWord(dVar:=Generator_L2_N_voltageA2,lo:=4886,hi:=4887);
Read_dWord(dVar:=Generator_L2_wattsA1,lo:=4888,hi:=4889);
Read_dWord(dVar:=Generator_L2_wattsA2,lo:=4890,hi:=4891);
Read_dWord(dVar:=Generator_L3_currentA1,lo:=4892,hi:=4893);
Read_dWord(dVar:=Generator_L3_currentA2,lo:=4894,hi:=4895);
Read_dWord(dVar:=Generator_L3_L1_voltageA1,lo:=4896,hi:=4897);
Read_dWord(dVar:=Generator_L3_L1_voltageA2,lo:=4898,hi:=4899);
Read_dWord(dVar:=Generator_L3_N_voltageA1,lo:=4900,hi:=4901);
Read_dWord(dVar:=Generator_L3_N_voltageA2,lo:=4902,hi:=4903);
Read_dWord(dVar:=Generator_L3_wattsA1,lo:=4904,hi:=4905);
Read_dWord(dVar:=Generator_L3_wattsA2,lo:=4906,hi:=4907);
Read_dWord(dVar:=Circ14NicelniTok,lo:=4908,hi:=4909);
Read_dWord(dVar:=Circ14Tok_L1,lo:=4910,hi:=4911);
Read_dWord(dVar:=Circ14Tok_L2,lo:=4912,hi:=4913);
Read_dWord(dVar:=Circ14Tok_L3,lo:=4914,hi:=4915);
Read_dWord(dVar:=Circ8NicelniTok,lo:=4916,hi:=4917);
Read_dWord(dVar:=Circ8Tok_L1,lo:=4918,hi:=4919);
Read_dWord(dVar:=Circ8Tok_L2,lo:=4920,hi:=4921);
Read_dWord(dVar:=Circ8Tok_L3,lo:=4922,hi:=4923);
Read_dWord(dVar:=Circ9NicelniTok,lo:=4924,hi:=4925);
Read_dWord(dVar:=Circ9Tok_L1,lo:=4926,hi:=4927);
Read_dWord(dVar:=Circ9Tok_L2,lo:=4928,hi:=4929);
Read_dWord(dVar:=Circ9Tok_L3,lo:=4930,hi:=4931);
Read_dWord(dVar:=Circ1MaximumDemandA2,lo:=4932,hi:=4933);
Read_dWord(dVar:=Circ1MaximumDemandA3,lo:=4934,hi:=4935);
Read_dWord(dVar:=Circ2MaximumDemandA2,lo:=4936,hi:=4937);
Read_dWord(dVar:=Circ2MaximumDemandA3,lo:=4938,hi:=4939);
Read_dWord(dVar:=Circ3MaximumDemandA2,lo:=4940,hi:=4941);
Read_dWord(dVar:=Circ3MaximumDemandA3,lo:=4942,hi:=4943);
Read_dWord(dVar:=Circ4MaximumDemandA2,lo:=4944,hi:=4945);
Read_dWord(dVar:=Circ4MaximumDemandA3,lo:=4946,hi:=4947);
Read_dWord(dVar:=Circ5MaximumDemandA2,lo:=4948,hi:=4949);
Read_dWord(dVar:=Circ5MaximumDemandA3,lo:=4950,hi:=4951);
Read_dWord(dVar:=Circ6MaximumDemandA2,lo:=4952,hi:=4953);
Read_dWord(dVar:=Circ6MaximumDemandA3,lo:=4954,hi:=4955);
Read_dWord(dVar:=Circ7MaximumDemandA2,lo:=4956,hi:=4957);
Read_dWord(dVar:=Circ7MaximumDemandA3,lo:=4958,hi:=4959);
Read_dWord(dVar:=Circ8MaximumDemandA2,lo:=4960,hi:=4961);
Read_dWord(dVar:=Circ8MaximumDemandA3,lo:=4962,hi:=4963);
Read_dWord(dVar:=Circ9MaximumDemandA2,lo:=4964,hi:=4965);
Read_dWord(dVar:=Circ9MaximumDemandA3,lo:=4966,hi:=4967);
Read_dWord(dVar:=Circ10MaximumDemandA2,lo:=4968,hi:=4969);
Read_dWord(dVar:=Circ10MaximumDemandA3,lo:=4970,hi:=4971);
Read_dWord(dVar:=Circ11MaximumDemandA2,lo:=4972,hi:=4973);
Read_dWord(dVar:=Circ11MaximumDemandA3,lo:=4974,hi:=4975);
Read_dWord(dVar:=Circ12MaximumDemandA2,lo:=4976,hi:=4977);
Read_dWord(dVar:=Circ12MaximumDemandA3,lo:=4978,hi:=4979);
Read_dWord(dVar:=Circ13MaximumDemandA2,lo:=4980,hi:=4981);
Read_dWord(dVar:=Circ13MaximumDemandA3,lo:=4982,hi:=4983);
Read_dWord(dVar:=Circ14MaximumDemandA2,lo:=4984,hi:=4985);
Read_dWord(dVar:=Circ14MaximumDemandA3,lo:=4986,hi:=4987);
Read_dWord(dVar:=Circ15MaximumDemandA2,lo:=4988,hi:=4989);
Read_dWord(dVar:=Circ15MaximumDemandA3,lo:=4990,hi:=4991);
Read_dWord(dVar:=Circ16MaximumDemandA2,lo:=4992,hi:=4993);
Read_dWord(dVar:=Circ16MaximumDemandA3,lo:=4994,hi:=4995);
Read_dWord(dVar:=Circ17MaximumDemandA2,lo:=4996,hi:=4997);
Read_dWord(dVar:=Circ17MaximumDemandA3,lo:=4998,hi:=4999);
Read_dWord(dVar:=Circ18MaximumDemandA2,lo:=5000,hi:=5001);
Read_dWord(dVar:=Circ18MaximumDemandA3,lo:=5002,hi:=5003);
Read_dWord(dVar:=Circ19MaximumDemandA2,lo:=5004,hi:=5005);
Read_dWord(dVar:=Circ19MaximumDemandA3,lo:=5006,hi:=5007);
Read_dWord(dVar:=Circ20MaximumDemandA2,lo:=5008,hi:=5009);
Read_dWord(dVar:=Circ20MaximumDemandA3,lo:=5010,hi:=5011);
Read_dWord(dVar:=Circ21MaximumDemandA2,lo:=5012,hi:=5013);
Read_dWord(dVar:=Circ21MaximumDemandA3,lo:=5014,hi:=5015);
Read_dWord(dVar:=Circ22MaximumDemandA2,lo:=5016,hi:=5017);
Read_dWord(dVar:=Circ22MaximumDemandA3,lo:=5018,hi:=5019);
Read_dWord(dVar:=Circ23MaximumDemandA2,lo:=5020,hi:=5021);
Read_dWord(dVar:=Circ23MaximumDemandA3,lo:=5022,hi:=5023);
Read_dWord(dVar:=Circ24MaximumDemandA2,lo:=5024,hi:=5025);
Read_dWord(dVar:=Circ24MaximumDemandA3,lo:=5026,hi:=5027);
Read_dWord(dVar:=Circ25MaximumDemandA2,lo:=5028,hi:=5029);
Read_dWord(dVar:=Circ25MaximumDemandA3,lo:=5030,hi:=5031);
Read_dWord(dVar:=Circ[1].RazEner_D_SCADA,lo:=5032,hi:=5033);
Read_dWord(dVar:=Circ[1].RazEner_T_SCADA,lo:=5034,hi:=5035);
Read_dWord(dVar:=Circ[1].RazEner_M_SCADA,lo:=5036,hi:=5037);
Read_dWord(dVar:=Circ[2].RazEner_D_SCADA,lo:=5038,hi:=5039);
Read_dWord(dVar:=Circ[2].RazEner_T_SCADA,lo:=5040,hi:=5041);
Read_dWord(dVar:=Circ[2].RazEner_M_SCADA,lo:=5042,hi:=5043);
Read_dWord(dVar:=Circ[3].RazEner_D_SCADA,lo:=5044,hi:=5045);
Read_dWord(dVar:=Circ[3].RazEner_T_SCADA,lo:=5046,hi:=5047);
Read_dWord(dVar:=Circ[3].RazEner_M_SCADA,lo:=5048,hi:=5049);
Read_dWord(dVar:=Circ[4].RazEner_D_SCADA,lo:=5050,hi:=5051);
Read_dWord(dVar:=Circ[4].RazEner_T_SCADA,lo:=5052,hi:=5053);
Read_dWord(dVar:=Circ[4].RazEner_M_SCADA,lo:=5054,hi:=5055);
Read_dWord(dVar:=Circ[5].RazEner_D_SCADA,lo:=5056,hi:=5057);
Read_dWord(dVar:=Circ[5].RazEner_T_SCADA,lo:=5058,hi:=5059);
Read_dWord(dVar:=Circ[5].RazEner_M_SCADA,lo:=5060,hi:=5061);
Read_dWord(dVar:=Circ[6].RazEner_D_SCADA,lo:=5062,hi:=5063);
Read_dWord(dVar:=Circ[6].RazEner_T_SCADA,lo:=5064,hi:=5065);
Read_dWord(dVar:=Circ[6].RazEner_M_SCADA,lo:=5066,hi:=5067);
Read_dWord(dVar:=Circ[7].RazEner_D_SCADA,lo:=5068,hi:=5069);
Read_dWord(dVar:=Circ[7].RazEner_T_SCADA,lo:=5070,hi:=5071);
Read_dWord(dVar:=Circ[7].RazEner_M_SCADA,lo:=5072,hi:=5073);
Read_dWord(dVar:=Circ[8].RazEner_D_SCADA,lo:=5074,hi:=5075);
Read_dWord(dVar:=Circ[8].RazEner_T_SCADA,lo:=5076,hi:=5077);
Read_dWord(dVar:=Circ[8].RazEner_M_SCADA,lo:=5078,hi:=5079);
Read_dWord(dVar:=Circ[9].RazEner_D_SCADA,lo:=5080,hi:=5081);
Read_dWord(dVar:=Circ[9].RazEner_T_SCADA,lo:=5082,hi:=5083);
Read_dWord(dVar:=Circ[9].RazEner_M_SCADA,lo:=5084,hi:=5085);
Read_dWord(dVar:=Circ[10].RazEner_D_SCADA,lo:=5086,hi:=5087);
Read_dWord(dVar:=Circ[10].RazEner_T_SCADA,lo:=5088,hi:=5089);
Read_dWord(dVar:=Circ[10].RazEner_M_SCADA,lo:=5090,hi:=5091);
Read_dWord(dVar:=Circ[11].RazEner_D_SCADA,lo:=5092,hi:=5093);
Read_dWord(dVar:=Circ[11].RazEner_T_SCADA,lo:=5094,hi:=5095);
Read_dWord(dVar:=Circ[11].RazEner_M_SCADA,lo:=5096,hi:=5097);
Read_dWord(dVar:=Circ[12].RazEner_D_SCADA,lo:=5098,hi:=5099);
Read_dWord(dVar:=Circ[12].RazEner_T_SCADA,lo:=5100,hi:=5101);
Read_dWord(dVar:=Circ[12].RazEner_M_SCADA,lo:=5102,hi:=5103);
Read_dWord(dVar:=Circ[13].RazEner_D_SCADA,lo:=5104,hi:=5105);
Read_dWord(dVar:=Circ[13].RazEner_T_SCADA,lo:=5106,hi:=5107);
Read_dWord(dVar:=Circ[13].RazEner_M_SCADA,lo:=5108,hi:=5109);
Read_dWord(dVar:=Circ[14].RazEner_D_SCADA,lo:=5110,hi:=5111);
Read_dWord(dVar:=Circ[14].RazEner_T_SCADA,lo:=5112,hi:=5113);
Read_dWord(dVar:=Circ[14].RazEner_M_SCADA,lo:=5114,hi:=5115);
Read_dWord(dVar:=Circ[15].RazEner_D_SCADA,lo:=5116,hi:=5117);
Read_dWord(dVar:=Circ[15].RazEner_T_SCADA,lo:=5118,hi:=5119);
Read_dWord(dVar:=Circ[15].RazEner_M_SCADA,lo:=5120,hi:=5121);
Read_dWord(dVar:=Circ[16].RazEner_D_SCADA,lo:=5122,hi:=5123);
Read_dWord(dVar:=Circ[16].RazEner_T_SCADA,lo:=5124,hi:=5125);
Read_dWord(dVar:=Circ[16].RazEner_M_SCADA,lo:=5126,hi:=5127);
Read_dWord(dVar:=Circ[17].RazEner_D_SCADA,lo:=5128,hi:=5129);
Read_dWord(dVar:=Circ[17].RazEner_T_SCADA,lo:=5130,hi:=5131);
Read_dWord(dVar:=Circ[17].RazEner_M_SCADA,lo:=5132,hi:=5133);
Read_dWord(dVar:=Circ[18].RazEner_D_SCADA,lo:=5134,hi:=5135);
Read_dWord(dVar:=Circ[18].RazEner_T_SCADA,lo:=5136,hi:=5137);
Read_dWord(dVar:=Circ[18].RazEner_M_SCADA,lo:=5138,hi:=5139);
Read_dWord(dVar:=Circ[19].RazEner_D_SCADA,lo:=5140,hi:=5141);
Read_dWord(dVar:=Circ[19].RazEner_T_SCADA,lo:=5142,hi:=5143);
Read_dWord(dVar:=Circ[19].RazEner_M_SCADA,lo:=5144,hi:=5145);
Read_dWord(dVar:=Circ[20].RazEner_D_SCADA,lo:=5146,hi:=5147);
Read_dWord(dVar:=Circ[20].RazEner_T_SCADA,lo:=5148,hi:=5149);
Read_dWord(dVar:=Circ[20].RazEner_M_SCADA,lo:=5150,hi:=5151);
Read_dWord(dVar:=Circ[21].RazEner_D_SCADA,lo:=5152,hi:=5153);
Read_dWord(dVar:=Circ[21].RazEner_T_SCADA,lo:=5154,hi:=5155);
Read_dWord(dVar:=Circ[21].RazEner_M_SCADA,lo:=5156,hi:=5157);
Read_dWord(dVar:=Circ[22].RazEner_D_SCADA,lo:=5158,hi:=5159);
Read_dWord(dVar:=Circ[22].RazEner_T_SCADA,lo:=5160,hi:=5161);
Read_dWord(dVar:=Circ[22].RazEner_M_SCADA,lo:=5162,hi:=5163);
Read_dWord(dVar:=Circ[23].RazEner_D_SCADA,lo:=5164,hi:=5165);
Read_dWord(dVar:=Circ[23].RazEner_T_SCADA,lo:=5166,hi:=5167);
Read_dWord(dVar:=Circ[23].RazEner_M_SCADA,lo:=5168,hi:=5169);
Read_dWord(dVar:=Circ[24].RazEner_D_SCADA,lo:=5170,hi:=5171);
Read_dWord(dVar:=Circ[24].RazEner_T_SCADA,lo:=5172,hi:=5173);
Read_dWord(dVar:=Circ[24].RazEner_M_SCADA,lo:=5174,hi:=5175);
Read_dWord(dVar:=Circ[25].RazEner_D_SCADA,lo:=5176,hi:=5177);
Read_dWord(dVar:=Circ[25].RazEner_T_SCADA,lo:=5178,hi:=5179);
Read_dWord(dVar:=Circ[25].RazEner_M_SCADA,lo:=5180,hi:=5181);
(*Branje REAL*)
(**)
(*Branje STRING*)
(**)
Read_String(sVar:=cas_scada,start:=5000);
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Bool : BOOL
VAR_INPUT
index: INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje BOOL*)
(**)
0:DA3_rocno:=Bit_0;
1:DA3motorni_pogon_okvara:=Bit_0;
2:Izpad_CAN_med_K1_K2:=Bit_0;
3:MI4agr_nap_RGM_A1:=Bit_0;
4:MI4agr_nap_RGM_A2:=Bit_0;
5:MI4DA1_2Q1_izklop:=Bit_0;
6:MI4DA1_2Q1_vklop:=Bit_0;
7:MI4DA1_del:=Bit_0;
8:MI4DA1_prip:=Bit_0;
9:MI4DA1_rezerva:=Bit_0;
10:MI4DA1_sinh:=Bit_0;
11:MI4DA1_zagon:=Bit_0;
12:MI4DA2_2Q1_izklop:=Bit_0;
13:MI4DA2_2Q1_vklop:=Bit_0;
14:MI4DA2_del:=Bit_0;
15:MI4DA2_prip:=Bit_0;
16:MI4DA2_rezerva:=Bit_0;
17:MI4DA2_sinh:=Bit_0;
18:MI4DA2_zagon:=Bit_0;
19:MI4del_zascA1_11Q1:=Bit_0;
20:MI4del_zascA1_12Q1:=Bit_0;
21:MI4del_zascA1_13Q1:=Bit_0;
22:MI4del_zascA1_14Q1:=Bit_0;
23:MI4del_zascA1_15Q1:=Bit_0;
24:MI4del_zascA1_16Q1:=Bit_0;
25:MI4del_zascA1_17Q1:=Bit_0;
26:MI4del_zascA1_2Q1:=Bit_0;
27:MI4del_zascA2_11Q1:=Bit_0;
28:MI4del_zascA2_12Q1:=Bit_0;
29:MI4del_zascA2_13Q1:=Bit_0;
30:MI4del_zascA2_14Q1:=Bit_0;
31:MI4K2agr_nap_RGM_A3:=Bit_0;
32:MI4K2DA3_2Q1_izklop:=Bit_0;
33:MI4K2DA3_2Q1_vklop:=Bit_0;
34:MI4K2del_zasc0_11Q1:=Bit_0;
35:MI4K2del_zasc0_12Q1:=Bit_0;
36:MI4K2del_zasc0_13Q1:=Bit_0;
37:MI4K2del_zasc0_14Q1:=Bit_0;
38:MI4K2del_zasc0_15Q1:=Bit_0;
39:MI4K2del_zasc0_16Q1:=Bit_0;
40:MI4K2del_zasc0_17Q1:=Bit_0;
41:MI4K2del_zasc0_18Q1:=Bit_0;
42:MI4K2del_zasc0_19Q1:=Bit_0;
43:MI4K2del_zasc0_20Q1:=Bit_0;
44:MI4K2del_zasc0_21Q1:=Bit_0;
45:MI4K2del_zasc0_22Q1:=Bit_0;
46:MI4K2del_zasc0_23Q1:=Bit_0;
47:MI4K2del_zascA3_11Q1:=Bit_0;
48:MI4K2del_zascA3_12Q1:=Bit_0;
49:MI4K2del_zascA3_13Q1:=Bit_0;
50:MI4K2del_zascA3_14Q1:=Bit_0;
51:MI4K2del_zascA3_15Q1:=Bit_0;
52:MI4K2motorA3_1Q1_prip:=Bit_0;
53:MI4K2motorA3_2Q1_prip:=Bit_0;
54:MI4K2mrez_nap_RGM_A3:=Bit_0;
55:MI4K2mrezaA3_1Q1_izklop:=Bit_0;
56:MI4K2mrezaA3_1Q1_vklop:=Bit_0;
57:MI4K2prenap_zasc0_OK:=Bit_0;
58:MI4K2prenap_zascA3_OK:=Bit_0;
59:MI4K2rocni_izk0_11Q1:=Bit_0;
60:MI4K2rocni_izk0_12Q1:=Bit_0;
61:MI4K2rocni_izk0_13Q1:=Bit_0;
62:MI4K2rocni_izk0_14Q1:=Bit_0;
63:MI4K2rocni_izk0_15Q1:=Bit_0;
64:MI4K2rocni_izk0_16Q1:=Bit_0;
65:MI4K2rocni_izk0_17Q1:=Bit_0;
66:MI4K2rocni_izk0_18Q1:=Bit_0;
67:MI4K2rocni_izk0_19Q1:=Bit_0;
68:MI4K2rocni_izk0_20Q1:=Bit_0;
69:MI4K2rocni_izk0_21Q1:=Bit_0;
70:MI4K2rocni_izk0_22Q1:=Bit_0;
71:MI4K2rocni_izk0_23Q1:=Bit_0;
72:MI4K2rocni_izkA3_11Q1:=Bit_0;
73:MI4K2rocni_izkA3_12Q1:=Bit_0;
74:MI4K2rocni_izkA3_13Q1:=Bit_0;
75:MI4K2rocni_izkA3_14Q1:=Bit_0;
76:MI4K2rocni_izkA3_15Q1:=Bit_0;
77:MI4K2stik0_11Q1_vkl:=Bit_0;
78:MI4K2stik0_12Q1_vkl:=Bit_0;
79:MI4K2stik0_13Q1_vkl:=Bit_0;
80:MI4K2stik0_14Q1_vkl:=Bit_0;
81:MI4K2stik0_15Q1_vkl:=Bit_0;
82:MI4K2stik0_16Q1_vkl:=Bit_0;
83:MI4K2stik0_17Q1_vkl:=Bit_0;
84:MI4K2stik0_18Q1_vkl:=Bit_0;
85:MI4K2stik0_19Q1_vkl:=Bit_0;
86:MI4K2stik0_1Q1_vkl:=Bit_0;
87:MI4K2stik0_20Q1_vkl:=Bit_0;
88:MI4K2stik0_21Q1_vkl:=Bit_0;
89:MI4K2stik0_22Q1_vkl:=Bit_0;
90:MI4K2stik0_23Q1_vkl:=Bit_0;
91:MI4K2stikA3_11Q1_vkl:=Bit_0;
92:MI4K2stikA3_12Q1_vkl:=Bit_0;
93:MI4K2stikA3_13Q1_vkl:=Bit_0;
94:MI4K2stikA3_14Q1_vkl:=Bit_0;
95:MI4K2stikA3_15Q1_vkl:=Bit_0;
96:MI4K2stikA3_1Q1_vkl:=Bit_0;
97:MI4K2stikA3_2Q1_vkl:=Bit_0;
98:MI4krmDA_daljinsko:=Bit_0;
99:MI4motorA1_1Q1_prip:=Bit_0;
100:MI4motorA1_2Q1_prip:=Bit_0;
101:MI4motorA2_1Q1_prip:=Bit_0;
102:MI4motorA2_2Q1_prip:=Bit_0;
103:MI4motorA2_6Q1_prip:=Bit_0;
104:MI4mrez_nap_RGM_A1:=Bit_0;
105:MI4mrez_nap_RGM_A2:=Bit_0;
106:MI4mrezaA1_1Q1_izklop:=Bit_0;
107:MI4mrezaA1_1Q1_vklop:=Bit_0;
108:MI4mrezaA2_1Q1_izklop:=Bit_0;
109:MI4mrezaA2_1Q1_vklop:=Bit_0;
110:MI4napaka_alarm_DA1:=Bit_0;
111:MI4napaka_alarm_DA2:=Bit_0;
112:MI4prenap_zascA1_OK:=Bit_0;
113:MI4prenap_zascA2_OK:=Bit_0;
114:MI4rezerva_DA1:=Bit_0;
115:MI4rocni_izkA1_11Q1:=Bit_0;
116:MI4rocni_izkA1_12Q1:=Bit_0;
117:MI4rocni_izkA1_13Q1:=Bit_0;
118:MI4rocni_izkA1_14Q1:=Bit_0;
119:MI4rocni_izkA1_15Q1:=Bit_0;
120:MI4rocni_izkA1_16Q1:=Bit_0;
121:MI4rocni_izkA1_17Q1:=Bit_0;
122:MI4rocni_izkA2_11Q1:=Bit_0;
123:MI4rocni_izkA2_12Q1:=Bit_0;
124:MI4rocni_izkA2_13Q1:=Bit_0;
125:MI4rocni_izkA2_14Q1:=Bit_0;
126:MI4sinhroniziranje_DA1:=Bit_0;
127:MI4sinhroniziranje_DA2:=Bit_0;
128:MI4splosna_napaka_DA1:=Bit_0;
129:MI4splosna_napaka_DA2:=Bit_0;
130:MI4stikA1_11Q1_vkl:=Bit_0;
131:MI4stikA1_12Q1_vkl:=Bit_0;
132:MI4stikA1_13Q1_vkl:=Bit_0;
133:MI4stikA1_14Q1_vkl:=Bit_0;
134:MI4stikA1_15Q1_vkl:=Bit_0;
135:MI4stikA1_16Q1_vkl:=Bit_0;
136:MI4stikA1_17Q1_vkl:=Bit_0;
137:MI4stikA1_1Q1_vkl:=Bit_0;
138:MI4stikA1_2Q1_vkl:=Bit_0;
139:MI4stikA1_6Q1_vkl:=Bit_0;
140:MI4stikA2_11Q1_vkl:=Bit_0;
141:MI4stikA2_12Q1_vkl:=Bit_0;
142:MI4stikA2_13Q1_vkl:=Bit_0;
143:MI4stikA2_14Q1_vkl:=Bit_0;
144:MI4stikA2_1Q1_vkl:=Bit_0;
145:MI4stikA2_2Q1_vkl:=Bit_0;
146:MI4vezno_6Q1_izklop:=Bit_0;
147:MI4vezno_6Q1_vklop:=Bit_0;
148:MI4vzporedno_del_nikoli:=Bit_0;
149:MI4vzporedno_del_nikoli_info:=Bit_0;
150:MI4vzporedno_del_po_potrebi:=Bit_0;
151:MI4vzporedno_del_po_potrebi_info:=Bit_0;
152:MI4vzporedno_del_vedno:=Bit_0;
153:MI4vzporedno_del_vedno_info:=Bit_0;
154:MI4zaganjanje_DA1:=Bit_0;
155:MI4zaganjanje_DA2:=Bit_0;
156:mrezaDA3motorni_pogon_okvara:=Bit_0;
157:mrezaDA3stikalo_okvara:=Bit_0;
158:Napaka_v_kom_cirk_DA1:=Bit_0;
159:Napaka_v_kom_cirk_DA2:=Bit_0;
160:NapakaCOMModBus:=Bit_0;
161:NapakaVKomunikaciji_Circutor1:=Bit_0;
162:NapakaVKomunikaciji_Circutor10:=Bit_0;
163:NapakaVKomunikaciji_Circutor11:=Bit_0;
164:NapakaVKomunikaciji_Circutor12:=Bit_0;
165:NapakaVKomunikaciji_Circutor13:=Bit_0;
166:NapakaVKomunikaciji_Circutor14:=Bit_0;
167:NapakaVKomunikaciji_Circutor15:=Bit_0;
168:NapakaVKomunikaciji_Circutor16:=Bit_0;
169:NapakaVKomunikaciji_Circutor17:=Bit_0;
170:NapakaVKomunikaciji_Circutor18:=Bit_0;
171:NapakaVKomunikaciji_Circutor19:=Bit_0;
172:NapakaVKomunikaciji_Circutor2:=Bit_0;
173:NapakaVKomunikaciji_Circutor20:=Bit_0;
174:NapakaVKomunikaciji_Circutor21:=Bit_0;
175:NapakaVKomunikaciji_Circutor22:=Bit_0;
176:NapakaVKomunikaciji_Circutor23:=Bit_0;
177:NapakaVKomunikaciji_Circutor24:=Bit_0;
178:NapakaVKomunikaciji_Circutor25:=Bit_0;
179:NapakaVKomunikaciji_Circutor3:=Bit_0;
180:NapakaVKomunikaciji_Circutor4:=Bit_0;
181:NapakaVKomunikaciji_Circutor5:=Bit_0;
182:NapakaVKomunikaciji_Circutor6:=Bit_0;
183:NapakaVKomunikaciji_Circutor7:=Bit_0;
184:NapakaVKomunikaciji_Circutor8:=Bit_0;
185:NapakaVKomunikaciji_Circutor9:=Bit_0;
186:RDASlabaBaterijaMI4:=Bit_0;
187:SlabaBaterijaMI4:=Bit_0;
188:SlabaBaterijaPLC1:=Bit_0;
189:SlabaBaterijaPLC2:=Bit_0;
190:stikaloDA3_okvara:=Bit_0;
191:UI_MI4K2DA3_2Q1_izklop:=Bit_0;
192:UI_MI4K2DA3_2Q1_vklop:=Bit_0;
193:UI_MI4K2mrezaA3_1Q1_izklop:=Bit_0;
194:UI_MI4K2mrezaA3_1Q1_vklop:=Bit_0;
195:cas_nastavi:=Bit_0;
196:Circ_Vpis_Dnevne_energija_scada1:=Bit_0;
197:Circ_Vpis_Dnevne_energija_scada2:=Bit_0;
198:Circ_Vpis_Tedenska_energija_scada1:=Bit_0;
199:Circ_Vpis_Tedenska_energija_scada2:=Bit_0;
200:Circ_Vpis_Mesecna_energija_scada1:=Bit_0;
201:Circ_Vpis_Mesecna_energija_scada2:=Bit_0;
(*BOOL*)
END_CASE
END_FUNCTION
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_dWord : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje LONG*)
(**)
3001:Circ10CosFi_III:=Long_0;
3003:Circ10DelovnaEnergija:=Long_0;
3005:Circ10DelovnaMoc_III:=Long_0;
3007:Circ10DelovnaMoc_L1:=Long_0;
3009:Circ10DelovnaMoc_L2:=Long_0;
3011:Circ10DelovnaMoc_L3:=Long_0;
3013:Circ10Frekvenca_L1:=Long_0;
3015:Circ10InduktivnaEnergija:=Long_0;
3017:Circ10InduktivnaMoc_III:=Long_0;
3019:Circ10JalovaMoc_L1:=Long_0;
3021:Circ10JalovaMoc_L2:=Long_0;
3023:Circ10JalovaMoc_L3:=Long_0;
3025:Circ10KapacitivnaEnergija:=Long_0;
3027:Circ10KapacitivnaMoc_III:=Long_0;
3029:Circ10MaximumDemand:=Long_0;
3031:Circ10Napetost_L1_L2:=Long_0;
3033:Circ10Napetost_L1_N:=Long_0;
3035:Circ10Napetost_L2_L3:=Long_0;
3037:Circ10Napetost_L2_N:=Long_0;
3039:Circ10Napetost_L3_L1:=Long_0;
3041:Circ10Napetost_L3_N:=Long_0;
3043:Circ10NavideznaMoc_III:=Long_0;
3045:Circ10NicelniTok:=Long_0;
3047:Circ10PowerFactor_III:=Long_0;
3049:Circ10PowerFactor_L1:=Long_0;
3051:Circ10PowerFactor_L2:=Long_0;
3053:Circ10PowerFactor_L3:=Long_0;
3055:Circ10THDI_L1:=Long_0;
3057:Circ10THDI_L2:=Long_0;
3059:Circ10THDI_L3:=Long_0;
3061:Circ10THDV_L1:=Long_0;
3063:Circ10THDV_L2:=Long_0;
3065:Circ10THDV_L3:=Long_0;
3067:Circ10Tok_L1:=Long_0;
3069:Circ10Tok_L2:=Long_0;
3071:Circ10Tok_L3:=Long_0;
3073:Circ10TokPovprecje_III:=Long_0;
3075:Circ11CosFi_III:=Long_0;
3077:Circ11DelovnaEnergija:=Long_0;
3079:Circ11DelovnaMoc_III:=Long_0;
3081:Circ11DelovnaMoc_L1:=Long_0;
3083:Circ11DelovnaMoc_L2:=Long_0;
3085:Circ11DelovnaMoc_L3:=Long_0;
3087:Circ11Frekvenca_L1:=Long_0;
3089:Circ11InduktivnaEnergija:=Long_0;
3091:Circ11InduktivnaMoc_III:=Long_0;
3093:Circ11JalovaMoc_L1:=Long_0;
3095:Circ11JalovaMoc_L2:=Long_0;
3097:Circ11JalovaMoc_L3:=Long_0;
3099:Circ11KapacitivnaEnergija:=Long_0;
3101:Circ11KapacitivnaMoc_III:=Long_0;
3103:Circ11MaximumDemand:=Long_0;
3105:Circ11Napetost_L1_L2:=Long_0;
3107:Circ11Napetost_L1_N:=Long_0;
3109:Circ11Napetost_L2_L3:=Long_0;
3111:Circ11Napetost_L2_N:=Long_0;
3113:Circ11Napetost_L3_L1:=Long_0;
3115:Circ11Napetost_L3_N:=Long_0;
3117:Circ11NavideznaMoc_III:=Long_0;
3119:Circ11NicelniTok:=Long_0;
3121:Circ11PowerFactor_III:=Long_0;
3123:Circ11PowerFactor_L1:=Long_0;
3125:Circ11PowerFactor_L2:=Long_0;
3127:Circ11PowerFactor_L3:=Long_0;
3129:Circ11THDI_L1:=Long_0;
3131:Circ11THDI_L2:=Long_0;
3133:Circ11THDI_L3:=Long_0;
3135:Circ11THDV_L1:=Long_0;
3137:Circ11THDV_L2:=Long_0;
3139:Circ11THDV_L3:=Long_0;
3141:Circ11Tok_L1:=Long_0;
3143:Circ11Tok_L2:=Long_0;
3145:Circ11Tok_L3:=Long_0;
3147:Circ11TokPovprecje_III:=Long_0;
3149:Circ12CosFi_III:=Long_0;
3151:Circ12DelovnaEnergija:=Long_0;
3153:Circ12DelovnaMoc_III:=Long_0;
3155:Circ12DelovnaMoc_L1:=Long_0;
3157:Circ12DelovnaMoc_L2:=Long_0;
3159:Circ12DelovnaMoc_L3:=Long_0;
3161:Circ12Frekvenca_L1:=Long_0;
3163:Circ12InduktivnaEnergija:=Long_0;
3165:Circ12InduktivnaMoc_III:=Long_0;
3167:Circ12JalovaMoc_L1:=Long_0;
3169:Circ12JalovaMoc_L2:=Long_0;
3171:Circ12JalovaMoc_L3:=Long_0;
3173:Circ12KapacitivnaEnergija:=Long_0;
3175:Circ12KapacitivnaMoc_III:=Long_0;
3177:Circ12MaximumDemand:=Long_0;
3179:Circ12Napetost_L1_L2:=Long_0;
3181:Circ12Napetost_L1_N:=Long_0;
3183:Circ12Napetost_L2_L3:=Long_0;
3185:Circ12Napetost_L2_N:=Long_0;
3187:Circ12Napetost_L3_L1:=Long_0;
3189:Circ12Napetost_L3_N:=Long_0;
3191:Circ12NavideznaMoc_III:=Long_0;
3193:Circ12NicelniTok:=Long_0;
3195:Circ12PowerFactor_III:=Long_0;
3197:Circ12PowerFactor_L1:=Long_0;
3199:Circ12PowerFactor_L2:=Long_0;
3201:Circ12PowerFactor_L3:=Long_0;
3203:Circ12THDI_L1:=Long_0;
3205:Circ12THDI_L2:=Long_0;
3207:Circ12THDI_L3:=Long_0;
3209:Circ12THDV_L1:=Long_0;
3211:Circ12THDV_L2:=Long_0;
3213:Circ12THDV_L3:=Long_0;
3215:Circ12Tok_L1:=Long_0;
3217:Circ12Tok_L2:=Long_0;
3219:Circ12Tok_L3:=Long_0;
3221:Circ12TokPovprecje_III:=Long_0;
3223:Circ13CosFi_III:=Long_0;
3225:Circ13DelovnaEnergija:=Long_0;
3227:Circ13DelovnaMoc_III:=Long_0;
3229:Circ13DelovnaMoc_L1:=Long_0;
3231:Circ13DelovnaMoc_L2:=Long_0;
3233:Circ13DelovnaMoc_L3:=Long_0;
3235:Circ13Frekvenca_L1:=Long_0;
3237:Circ13InduktivnaEnergija:=Long_0;
3239:Circ13InduktivnaMoc_III:=Long_0;
3241:Circ13JalovaMoc_L1:=Long_0;
3243:Circ13JalovaMoc_L2:=Long_0;
3245:Circ13JalovaMoc_L3:=Long_0;
3247:Circ13KapacitivnaEnergija:=Long_0;
3249:Circ13KapacitivnaMoc_III:=Long_0;
3251:Circ13MaximumDemand:=Long_0;
3253:Circ13Napetost_L1_L2:=Long_0;
3255:Circ13Napetost_L1_N:=Long_0;
3257:Circ13Napetost_L2_L3:=Long_0;
3259:Circ13Napetost_L2_N:=Long_0;
3261:Circ13Napetost_L3_L1:=Long_0;
3263:Circ13Napetost_L3_N:=Long_0;
3265:Circ13NavideznaMoc_III:=Long_0;
3267:Circ13NicelniTok:=Long_0;
3269:Circ13PowerFactor_III:=Long_0;
3271:Circ13PowerFactor_L1:=Long_0;
3273:Circ13PowerFactor_L2:=Long_0;
3275:Circ13PowerFactor_L3:=Long_0;
3277:Circ13THDI_L1:=Long_0;
3279:Circ13THDI_L2:=Long_0;
3281:Circ13THDI_L3:=Long_0;
3283:Circ13THDV_L1:=Long_0;
3285:Circ13THDV_L2:=Long_0;
3287:Circ13THDV_L3:=Long_0;
3289:Circ13Tok_L1:=Long_0;
3291:Circ13Tok_L2:=Long_0;
3293:Circ13Tok_L3:=Long_0;
3295:Circ13TokPovprecje_III:=Long_0;
3297:Circ14CosFi_III:=Long_0;
3299:Circ14DelovnaEnergija:=Long_0;
3301:Circ14DelovnaMoc_III:=Long_0;
3303:Circ14DelovnaMoc_L1:=Long_0;
3305:Circ14DelovnaMoc_L2:=Long_0;
3307:Circ14DelovnaMoc_L3:=Long_0;
3309:Circ14Frekvenca_L1:=Long_0;
3311:Circ14InduktivnaEnergija:=Long_0;
3313:Circ14InduktivnaMoc_III:=Long_0;
3315:Circ14JalovaMoc_L1:=Long_0;
3317:Circ14JalovaMoc_L2:=Long_0;
3319:Circ14JalovaMoc_L3:=Long_0;
3321:Circ14KapacitivnaEnergija:=Long_0;
3323:Circ14KapacitivnaMoc_III:=Long_0;
3325:Circ14MaximumDemand:=Long_0;
3327:Circ14Napetost_L1_L2:=Long_0;
3329:Circ14Napetost_L1_N:=Long_0;
3331:Circ14Napetost_L2_L3:=Long_0;
3333:Circ14Napetost_L2_N:=Long_0;
3335:Circ14Napetost_L3_L1:=Long_0;
3337:Circ14Napetost_L3_N:=Long_0;
3339:Circ14NavideznaMoc_III:=Long_0;
3341:Circ14NicelniTok:=Long_0;
3343:Circ14PowerFactor_III:=Long_0;
3345:Circ14PowerFactor_L1:=Long_0;
3347:Circ14PowerFactor_L2:=Long_0;
3349:Circ14PowerFactor_L3:=Long_0;
3351:Circ14THDI_L1:=Long_0;
3353:Circ14THDI_L2:=Long_0;
3355:Circ14THDI_L3:=Long_0;
3357:Circ14THDV_L1:=Long_0;
3359:Circ14THDV_L2:=Long_0;
3361:Circ14THDV_L3:=Long_0;
3363:Circ14Tok_L1:=Long_0;
3365:Circ14Tok_L2:=Long_0;
3367:Circ14Tok_L3:=Long_0;
3369:Circ14TokPovprecje_III:=Long_0;
3371:Circ15CosFi_III:=Long_0;
3373:Circ15DelovnaEnergija:=Long_0;
3375:Circ15DelovnaMoc_III:=Long_0;
3377:Circ15DelovnaMoc_L1:=Long_0;
3379:Circ15DelovnaMoc_L2:=Long_0;
3381:Circ15DelovnaMoc_L3:=Long_0;
3383:Circ15Frekvenca_L1:=Long_0;
3385:Circ15InduktivnaEnergija:=Long_0;
3387:Circ15InduktivnaMoc_III:=Long_0;
3389:Circ15JalovaMoc_L1:=Long_0;
3391:Circ15JalovaMoc_L2:=Long_0;
3393:Circ15JalovaMoc_L3:=Long_0;
3395:Circ15KapacitivnaEnergija:=Long_0;
3397:Circ15KapacitivnaMoc_III:=Long_0;
3399:Circ15MaximumDemand:=Long_0;
3401:Circ15Napetost_L1_L2:=Long_0;
3403:Circ15Napetost_L1_N:=Long_0;
3405:Circ15Napetost_L2_L3:=Long_0;
3407:Circ15Napetost_L2_N:=Long_0;
3409:Circ15Napetost_L3_L1:=Long_0;
3411:Circ15Napetost_L3_N:=Long_0;
3413:Circ15NavideznaMoc_III:=Long_0;
3415:Circ15NicelniTok:=Long_0;
3417:Circ15PowerFactor_III:=Long_0;
3419:Circ15PowerFactor_L1:=Long_0;
3421:Circ15PowerFactor_L2:=Long_0;
3423:Circ15PowerFactor_L3:=Long_0;
3425:Circ15THDI_L1:=Long_0;
3427:Circ15THDI_L2:=Long_0;
3429:Circ15THDI_L3:=Long_0;
3431:Circ15THDV_L1:=Long_0;
3433:Circ15THDV_L2:=Long_0;
3435:Circ15THDV_L3:=Long_0;
3437:Circ15Tok_L1:=Long_0;
3439:Circ15Tok_L2:=Long_0;
3441:Circ15Tok_L3:=Long_0;
3443:Circ15TokPovprecje_III:=Long_0;
3445:Circ16CosFi_III:=Long_0;
3447:Circ16DelovnaEnergija:=Long_0;
3449:Circ16DelovnaMoc_III:=Long_0;
3451:Circ16DelovnaMoc_L1:=Long_0;
3453:Circ16DelovnaMoc_L2:=Long_0;
3455:Circ16DelovnaMoc_L3:=Long_0;
3457:Circ16Frekvenca_L1:=Long_0;
3459:Circ16InduktivnaEnergija:=Long_0;
3461:Circ16InduktivnaMoc_III:=Long_0;
3463:Circ16JalovaMoc_L1:=Long_0;
3465:Circ16JalovaMoc_L2:=Long_0;
3467:Circ16JalovaMoc_L3:=Long_0;
3469:Circ16KapacitivnaEnergija:=Long_0;
3471:Circ16KapacitivnaMoc_III:=Long_0;
3473:Circ16MaximumDemand:=Long_0;
3475:Circ16Napetost_L1_L2:=Long_0;
3477:Circ16Napetost_L1_N:=Long_0;
3479:Circ16Napetost_L2_L3:=Long_0;
3481:Circ16Napetost_L2_N:=Long_0;
3483:Circ16Napetost_L3_L1:=Long_0;
3485:Circ16Napetost_L3_N:=Long_0;
3487:Circ16NavideznaMoc_III:=Long_0;
3489:Circ16NicelniTok:=Long_0;
3491:Circ16PowerFactor_III:=Long_0;
3493:Circ16PowerFactor_L1:=Long_0;
3495:Circ16PowerFactor_L2:=Long_0;
3497:Circ16PowerFactor_L3:=Long_0;
3499:Circ16THDI_L1:=Long_0;
3501:Circ16THDI_L2:=Long_0;
3503:Circ16THDI_L3:=Long_0;
3505:Circ16THDV_L1:=Long_0;
3507:Circ16THDV_L2:=Long_0;
3509:Circ16THDV_L3:=Long_0;
3511:Circ16Tok_L1:=Long_0;
3513:Circ16Tok_L2:=Long_0;
3515:Circ16Tok_L3:=Long_0;
3517:Circ16TokPovprecje_III:=Long_0;
3519:Circ17CosFi_III:=Long_0;
3521:Circ17DelovnaEnergija:=Long_0;
3523:Circ17DelovnaMoc_III:=Long_0;
3525:Circ17DelovnaMoc_L1:=Long_0;
3527:Circ17DelovnaMoc_L2:=Long_0;
3529:Circ17DelovnaMoc_L3:=Long_0;
3531:Circ17Frekvenca_L1:=Long_0;
3533:Circ17InduktivnaEnergija:=Long_0;
3535:Circ17InduktivnaMoc_III:=Long_0;
3537:Circ17JalovaMoc_L1:=Long_0;
3539:Circ17JalovaMoc_L2:=Long_0;
3541:Circ17JalovaMoc_L3:=Long_0;
3543:Circ17KapacitivnaEnergija:=Long_0;
3545:Circ17KapacitivnaMoc_III:=Long_0;
3547:Circ17MaximumDemand:=Long_0;
3549:Circ17Napetost_L1_L2:=Long_0;
3551:Circ17Napetost_L1_N:=Long_0;
3553:Circ17Napetost_L2_L3:=Long_0;
3555:Circ17Napetost_L2_N:=Long_0;
3557:Circ17Napetost_L3_L1:=Long_0;
3559:Circ17Napetost_L3_N:=Long_0;
3561:Circ17NavideznaMoc_III:=Long_0;
3563:Circ17NicelniTok:=Long_0;
3565:Circ17PowerFactor_III:=Long_0;
3567:Circ17PowerFactor_L1:=Long_0;
3569:Circ17PowerFactor_L2:=Long_0;
3571:Circ17PowerFactor_L3:=Long_0;
3573:Circ17THDI_L1:=Long_0;
3575:Circ17THDI_L2:=Long_0;
3577:Circ17THDI_L3:=Long_0;
3579:Circ17THDV_L1:=Long_0;
3581:Circ17THDV_L2:=Long_0;
3583:Circ17THDV_L3:=Long_0;
3585:Circ17Tok_L1:=Long_0;
3587:Circ17Tok_L2:=Long_0;
3589:Circ17Tok_L3:=Long_0;
3591:Circ17TokPovprecje_III:=Long_0;
3593:Circ18CosFi_III:=Long_0;
3595:Circ18DelovnaEnergija:=Long_0;
3597:Circ18DelovnaMoc_III:=Long_0;
3599:Circ18DelovnaMoc_L1:=Long_0;
3601:Circ18DelovnaMoc_L2:=Long_0;
3603:Circ18DelovnaMoc_L3:=Long_0;
3605:Circ18Frekvenca_L1:=Long_0;
3607:Circ18InduktivnaEnergija:=Long_0;
3609:Circ18InduktivnaMoc_III:=Long_0;
3611:Circ18JalovaMoc_L1:=Long_0;
3613:Circ18JalovaMoc_L2:=Long_0;
3615:Circ18JalovaMoc_L3:=Long_0;
3617:Circ18KapacitivnaEnergija:=Long_0;
3619:Circ18KapacitivnaMoc_III:=Long_0;
3621:Circ18MaximumDemand:=Long_0;
3623:Circ18Napetost_L1_L2:=Long_0;
3625:Circ18Napetost_L1_N:=Long_0;
3627:Circ18Napetost_L2_L3:=Long_0;
3629:Circ18Napetost_L2_N:=Long_0;
3631:Circ18Napetost_L3_L1:=Long_0;
3633:Circ18Napetost_L3_N:=Long_0;
3635:Circ18NavideznaMoc_III:=Long_0;
3637:Circ18NicelniTok:=Long_0;
3639:Circ18PowerFactor_III:=Long_0;
3641:Circ18PowerFactor_L1:=Long_0;
3643:Circ18PowerFactor_L2:=Long_0;
3645:Circ18PowerFactor_L3:=Long_0;
3647:Circ18THDI_L1:=Long_0;
3649:Circ18THDI_L2:=Long_0;
3651:Circ18THDI_L3:=Long_0;
3653:Circ18THDV_L1:=Long_0;
3655:Circ18THDV_L2:=Long_0;
3657:Circ18THDV_L3:=Long_0;
3659:Circ18Tok_L1:=Long_0;
3661:Circ18Tok_L2:=Long_0;
3663:Circ18Tok_L3:=Long_0;
3665:Circ18TokPovprecje_III:=Long_0;
3667:Circ19CosFi_III:=Long_0;
3669:Circ19DelovnaEnergija:=Long_0;
3671:Circ19DelovnaMoc_III:=Long_0;
3673:Circ19DelovnaMoc_L1:=Long_0;
3675:Circ19DelovnaMoc_L2:=Long_0;
3677:Circ19DelovnaMoc_L3:=Long_0;
3679:Circ19Frekvenca_L1:=Long_0;
3681:Circ19InduktivnaEnergija:=Long_0;
3683:Circ19InduktivnaMoc_III:=Long_0;
3685:Circ19JalovaMoc_L1:=Long_0;
3687:Circ19JalovaMoc_L2:=Long_0;
3689:Circ19JalovaMoc_L3:=Long_0;
3691:Circ19KapacitivnaEnergija:=Long_0;
3693:Circ19KapacitivnaMoc_III:=Long_0;
3695:Circ19MaximumDemand:=Long_0;
3697:Circ19Napetost_L1_L2:=Long_0;
3699:Circ19Napetost_L1_N:=Long_0;
3701:Circ19Napetost_L2_L3:=Long_0;
3703:Circ19Napetost_L2_N:=Long_0;
3705:Circ19Napetost_L3_L1:=Long_0;
3707:Circ19Napetost_L3_N:=Long_0;
3709:Circ19NavideznaMoc_III:=Long_0;
3711:Circ19NicelniTok:=Long_0;
3713:Circ19PowerFactor_III:=Long_0;
3715:Circ19PowerFactor_L1:=Long_0;
3717:Circ19PowerFactor_L2:=Long_0;
3719:Circ19PowerFactor_L3:=Long_0;
3721:Circ19THDI_L1:=Long_0;
3723:Circ19THDI_L2:=Long_0;
3725:Circ19THDI_L3:=Long_0;
3727:Circ19THDV_L1:=Long_0;
3729:Circ19THDV_L2:=Long_0;
3731:Circ19THDV_L3:=Long_0;
3733:Circ19Tok_L1:=Long_0;
3735:Circ19Tok_L2:=Long_0;
3737:Circ19Tok_L3:=Long_0;
3739:Circ19TokPovprecje_III:=Long_0;
3741:Circ1CosFi_III:=Long_0;
3743:Circ1DelovnaEnergija:=Long_0;
3745:Circ1DelovnaMoc_III:=Long_0;
3747:Circ1DelovnaMoc_L1:=Long_0;
3749:Circ1DelovnaMoc_L2:=Long_0;
3751:Circ1DelovnaMoc_L3:=Long_0;
3753:Circ1Frekvenca_L1:=Long_0;
3755:Circ1InduktivnaEnergija:=Long_0;
3757:Circ1InduktivnaMoc_III:=Long_0;
3759:Circ1JalovaMoc_L1:=Long_0;
3761:Circ1JalovaMoc_L2:=Long_0;
3763:Circ1JalovaMoc_L3:=Long_0;
3765:Circ1KapacitivnaEnergija:=Long_0;
3767:Circ1KapacitivnaMoc_III:=Long_0;
3769:Circ1MaximumDemand:=Long_0;
3771:Circ1Napetost_L1_L2:=Long_0;
3773:Circ1Napetost_L1_N:=Long_0;
3775:Circ1Napetost_L2_L3:=Long_0;
3777:Circ1Napetost_L2_N:=Long_0;
3779:Circ1Napetost_L3_L1:=Long_0;
3781:Circ1Napetost_L3_N:=Long_0;
3783:Circ1NavideznaMoc_III:=Long_0;
3785:Circ1NicelniTok:=Long_0;
3787:Circ1PowerFactor_III:=Long_0;
3789:Circ1PowerFactor_L1:=Long_0;
3791:Circ1PowerFactor_L2:=Long_0;
3793:Circ1PowerFactor_L3:=Long_0;
3795:Circ1THDI_L1:=Long_0;
3797:Circ1THDI_L2:=Long_0;
3799:Circ1THDI_L3:=Long_0;
3801:Circ1THDV_L1:=Long_0;
3803:Circ1THDV_L2:=Long_0;
3805:Circ1THDV_L3:=Long_0;
3807:Circ1Tok_L1:=Long_0;
3809:Circ1Tok_L2:=Long_0;
3811:Circ1Tok_L3:=Long_0;
3813:Circ1TokPovprecje_III:=Long_0;
3815:Circ20CosFi_III:=Long_0;
3817:Circ20DelovnaEnergija:=Long_0;
3819:Circ20DelovnaMoc_III:=Long_0;
3821:Circ20DelovnaMoc_L1:=Long_0;
3823:Circ20DelovnaMoc_L2:=Long_0;
3825:Circ20DelovnaMoc_L3:=Long_0;
3827:Circ20Frekvenca_L1:=Long_0;
3829:Circ20InduktivnaEnergija:=Long_0;
3831:Circ20InduktivnaMoc_III:=Long_0;
3833:Circ20JalovaMoc_L1:=Long_0;
3835:Circ20JalovaMoc_L2:=Long_0;
3837:Circ20JalovaMoc_L3:=Long_0;
3839:Circ20KapacitivnaEnergija:=Long_0;
3841:Circ20KapacitivnaMoc_III:=Long_0;
3843:Circ20MaximumDemand:=Long_0;
3845:Circ20Napetost_L1_L2:=Long_0;
3847:Circ20Napetost_L1_N:=Long_0;
3849:Circ20Napetost_L2_L3:=Long_0;
3851:Circ20Napetost_L2_N:=Long_0;
3853:Circ20Napetost_L3_L1:=Long_0;
3855:Circ20Napetost_L3_N:=Long_0;
3857:Circ20NavideznaMoc_III:=Long_0;
3859:Circ20NicelniTok:=Long_0;
3861:Circ20PowerFactor_III:=Long_0;
3863:Circ20PowerFactor_L1:=Long_0;
3865:Circ20PowerFactor_L2:=Long_0;
3867:Circ20PowerFactor_L3:=Long_0;
3869:Circ20THDI_L1:=Long_0;
3871:Circ20THDI_L2:=Long_0;
3873:Circ20THDI_L3:=Long_0;
3875:Circ20THDV_L1:=Long_0;
3877:Circ20THDV_L2:=Long_0;
3879:Circ20THDV_L3:=Long_0;
3881:Circ20Tok_L1:=Long_0;
3883:Circ20Tok_L2:=Long_0;
3885:Circ20Tok_L3:=Long_0;
3887:Circ20TokPovprecje_III:=Long_0;
3889:Circ21CosFi_III:=Long_0;
3891:Circ21DelovnaEnergija:=Long_0;
3893:Circ21DelovnaMoc_III:=Long_0;
3895:Circ21DelovnaMoc_L1:=Long_0;
3897:Circ21DelovnaMoc_L2:=Long_0;
3899:Circ21DelovnaMoc_L3:=Long_0;
3901:Circ21Frekvenca_L1:=Long_0;
3903:Circ21InduktivnaEnergija:=Long_0;
3905:Circ21InduktivnaMoc_III:=Long_0;
3907:Circ21JalovaMoc_L1:=Long_0;
3909:Circ21JalovaMoc_L2:=Long_0;
3911:Circ21JalovaMoc_L3:=Long_0;
3913:Circ21KapacitivnaEnergija:=Long_0;
3915:Circ21KapacitivnaMoc_III:=Long_0;
3917:Circ21MaximumDemand:=Long_0;
3919:Circ21Napetost_L1_L2:=Long_0;
3921:Circ21Napetost_L1_N:=Long_0;
3923:Circ21Napetost_L2_L3:=Long_0;
3925:Circ21Napetost_L2_N:=Long_0;
3927:Circ21Napetost_L3_L1:=Long_0;
3929:Circ21Napetost_L3_N:=Long_0;
3931:Circ21NavideznaMoc_III:=Long_0;
3933:Circ21NicelniTok:=Long_0;
3935:Circ21PowerFactor_III:=Long_0;
3937:Circ21PowerFactor_L1:=Long_0;
3939:Circ21PowerFactor_L2:=Long_0;
3941:Circ21PowerFactor_L3:=Long_0;
3943:Circ21THDI_L1:=Long_0;
3945:Circ21THDI_L2:=Long_0;
3947:Circ21THDI_L3:=Long_0;
3949:Circ21THDV_L1:=Long_0;
3951:Circ21THDV_L2:=Long_0;
3953:Circ21THDV_L3:=Long_0;
3955:Circ21Tok_L1:=Long_0;
3957:Circ21Tok_L2:=Long_0;
3959:Circ21Tok_L3:=Long_0;
3961:Circ21TokPovprecje_III:=Long_0;
3963:Circ22CosFi_III:=Long_0;
3965:Circ22DelovnaEnergija:=Long_0;
3967:Circ22DelovnaMoc_III:=Long_0;
3969:Circ22DelovnaMoc_L1:=Long_0;
3971:Circ22DelovnaMoc_L2:=Long_0;
3973:Circ22DelovnaMoc_L3:=Long_0;
3975:Circ22Frekvenca_L1:=Long_0;
3977:Circ22InduktivnaEnergija:=Long_0;
3979:Circ22InduktivnaMoc_III:=Long_0;
3981:Circ22JalovaMoc_L1:=Long_0;
3983:Circ22JalovaMoc_L2:=Long_0;
3985:Circ22JalovaMoc_L3:=Long_0;
3987:Circ22KapacitivnaEnergija:=Long_0;
3989:Circ22KapacitivnaMoc_III:=Long_0;
3991:Circ22MaximumDemand:=Long_0;
3993:Circ22Napetost_L1_L2:=Long_0;
3995:Circ22Napetost_L1_N:=Long_0;
3997:Circ22Napetost_L2_L3:=Long_0;
3999:Circ22Napetost_L2_N:=Long_0;
4001:Circ22Napetost_L3_L1:=Long_0;
4003:Circ22Napetost_L3_N:=Long_0;
4005:Circ22NavideznaMoc_III:=Long_0;
4007:Circ22NicelniTok:=Long_0;
4009:Circ22PowerFactor_III:=Long_0;
4011:Circ22PowerFactor_L1:=Long_0;
4013:Circ22PowerFactor_L2:=Long_0;
4015:Circ22PowerFactor_L3:=Long_0;
4017:Circ22THDI_L1:=Long_0;
4019:Circ22THDI_L2:=Long_0;
4021:Circ22THDI_L3:=Long_0;
4023:Circ22THDV_L1:=Long_0;
4025:Circ22THDV_L2:=Long_0;
4027:Circ22THDV_L3:=Long_0;
4029:Circ22Tok_L1:=Long_0;
4031:Circ22Tok_L2:=Long_0;
4033:Circ22Tok_L3:=Long_0;
4035:Circ22TokPovprecje_III:=Long_0;
4037:Circ23CosFi_III:=Long_0;
4039:Circ23DelovnaEnergija:=Long_0;
4041:Circ23DelovnaMoc_III:=Long_0;
4043:Circ23DelovnaMoc_L1:=Long_0;
4045:Circ23DelovnaMoc_L2:=Long_0;
4047:Circ23DelovnaMoc_L3:=Long_0;
4049:Circ23Frekvenca_L1:=Long_0;
4051:Circ23InduktivnaEnergija:=Long_0;
4053:Circ23InduktivnaMoc_III:=Long_0;
4055:Circ23JalovaMoc_L1:=Long_0;
4057:Circ23JalovaMoc_L2:=Long_0;
4059:Circ23JalovaMoc_L3:=Long_0;
4061:Circ23KapacitivnaEnergija:=Long_0;
4063:Circ23KapacitivnaMoc_III:=Long_0;
4065:Circ23MaximumDemand:=Long_0;
4067:Circ23Napetost_L1_L2:=Long_0;
4069:Circ23Napetost_L1_N:=Long_0;
4071:Circ23Napetost_L2_L3:=Long_0;
4073:Circ23Napetost_L2_N:=Long_0;
4075:Circ23Napetost_L3_L1:=Long_0;
4077:Circ23Napetost_L3_N:=Long_0;
4079:Circ23NavideznaMoc_III:=Long_0;
4081:Circ23NicelniTok:=Long_0;
4083:Circ23PowerFactor_III:=Long_0;
4085:Circ23PowerFactor_L1:=Long_0;
4087:Circ23PowerFactor_L2:=Long_0;
4089:Circ23PowerFactor_L3:=Long_0;
4091:Circ23THDI_L1:=Long_0;
4093:Circ23THDI_L2:=Long_0;
4095:Circ23THDI_L3:=Long_0;
4097:Circ23THDV_L1:=Long_0;
4099:Circ23THDV_L2:=Long_0;
4101:Circ23THDV_L3:=Long_0;
4103:Circ23Tok_L1:=Long_0;
4105:Circ23Tok_L2:=Long_0;
4107:Circ23Tok_L3:=Long_0;
4109:Circ23TokPovprecje_III:=Long_0;
4111:Circ24CosFi_III:=Long_0;
4113:Circ24DelovnaEnergija:=Long_0;
4115:Circ24DelovnaMoc_III:=Long_0;
4117:Circ24DelovnaMoc_L1:=Long_0;
4119:Circ24DelovnaMoc_L2:=Long_0;
4121:Circ24DelovnaMoc_L3:=Long_0;
4123:Circ24Frekvenca_L1:=Long_0;
4125:Circ24InduktivnaEnergija:=Long_0;
4127:Circ24InduktivnaMoc_III:=Long_0;
4129:Circ24JalovaMoc_L1:=Long_0;
4131:Circ24JalovaMoc_L2:=Long_0;
4133:Circ24JalovaMoc_L3:=Long_0;
4135:Circ24KapacitivnaEnergija:=Long_0;
4137:Circ24KapacitivnaMoc_III:=Long_0;
4139:Circ24MaximumDemand:=Long_0;
4141:Circ24Napetost_L1_L2:=Long_0;
4143:Circ24Napetost_L1_N:=Long_0;
4145:Circ24Napetost_L2_L3:=Long_0;
4147:Circ24Napetost_L2_N:=Long_0;
4149:Circ24Napetost_L3_L1:=Long_0;
4151:Circ24Napetost_L3_N:=Long_0;
4153:Circ24NavideznaMoc_III:=Long_0;
4155:Circ24NicelniTok:=Long_0;
4157:Circ24PowerFactor_III:=Long_0;
4159:Circ24PowerFactor_L1:=Long_0;
4161:Circ24PowerFactor_L2:=Long_0;
4163:Circ24PowerFactor_L3:=Long_0;
4165:Circ24THDI_L1:=Long_0;
4167:Circ24THDI_L2:=Long_0;
4169:Circ24THDI_L3:=Long_0;
4171:Circ24THDV_L1:=Long_0;
4173:Circ24THDV_L2:=Long_0;
4175:Circ24THDV_L3:=Long_0;
4177:Circ24Tok_L1:=Long_0;
4179:Circ24Tok_L2:=Long_0;
4181:Circ24Tok_L3:=Long_0;
4183:Circ24TokPovprecje_III:=Long_0;
4185:Circ25CosFi_III:=Long_0;
4187:Circ25DelovnaEnergija:=Long_0;
4189:Circ25DelovnaMoc_III:=Long_0;
4191:Circ25DelovnaMoc_L1:=Long_0;
4193:Circ25DelovnaMoc_L2:=Long_0;
4195:Circ25DelovnaMoc_L3:=Long_0;
4197:Circ25Frekvenca_L1:=Long_0;
4199:Circ25InduktivnaEnergija:=Long_0;
4201:Circ25InduktivnaMoc_III:=Long_0;
4203:Circ25JalovaMoc_L1:=Long_0;
4205:Circ25JalovaMoc_L2:=Long_0;
4207:Circ25JalovaMoc_L3:=Long_0;
4209:Circ25KapacitivnaEnergija:=Long_0;
4211:Circ25KapacitivnaMoc_III:=Long_0;
4213:Circ25MaximumDemand:=Long_0;
4215:Circ25Napetost_L1_L2:=Long_0;
4217:Circ25Napetost_L1_N:=Long_0;
4219:Circ25Napetost_L2_L3:=Long_0;
4221:Circ25Napetost_L2_N:=Long_0;
4223:Circ25Napetost_L3_L1:=Long_0;
4225:Circ25Napetost_L3_N:=Long_0;
4227:Circ25NavideznaMoc_III:=Long_0;
4229:Circ25NicelniTok:=Long_0;
4231:Circ25PowerFactor_III:=Long_0;
4233:Circ25PowerFactor_L1:=Long_0;
4235:Circ25PowerFactor_L2:=Long_0;
4237:Circ25PowerFactor_L3:=Long_0;
4239:Circ25THDI_L1:=Long_0;
4241:Circ25THDI_L2:=Long_0;
4243:Circ25THDI_L3:=Long_0;
4245:Circ25THDV_L1:=Long_0;
4247:Circ25THDV_L2:=Long_0;
4249:Circ25THDV_L3:=Long_0;
4251:Circ25Tok_L1:=Long_0;
4253:Circ25Tok_L2:=Long_0;
4255:Circ25Tok_L3:=Long_0;
4257:Circ25TokPovprecje_III:=Long_0;
4259:Circ2CosFi_III:=Long_0;
4261:Circ2DelovnaEnergija:=Long_0;
4263:Circ2DelovnaMoc_III:=Long_0;
4265:Circ2DelovnaMoc_L1:=Long_0;
4267:Circ2DelovnaMoc_L2:=Long_0;
4269:Circ2DelovnaMoc_L3:=Long_0;
4271:Circ2Frekvenca_L1:=Long_0;
4273:Circ2InduktivnaEnergija:=Long_0;
4275:Circ2InduktivnaMoc_III:=Long_0;
4277:Circ2JalovaMoc_L1:=Long_0;
4279:Circ2JalovaMoc_L2:=Long_0;
4281:Circ2JalovaMoc_L3:=Long_0;
4283:Circ2KapacitivnaEnergija:=Long_0;
4285:Circ2KapacitivnaMoc_III:=Long_0;
4287:Circ2MaximumDemand:=Long_0;
4289:Circ2Napetost_L1_L2:=Long_0;
4291:Circ2Napetost_L1_N:=Long_0;
4293:Circ2Napetost_L2_L3:=Long_0;
4295:Circ2Napetost_L2_N:=Long_0;
4297:Circ2Napetost_L3_L1:=Long_0;
4299:Circ2Napetost_L3_N:=Long_0;
4301:Circ2NavideznaMoc_III:=Long_0;
4303:Circ2NicelniTok:=Long_0;
4305:Circ2PowerFactor_III:=Long_0;
4307:Circ2PowerFactor_L1:=Long_0;
4309:Circ2PowerFactor_L2:=Long_0;
4311:Circ2PowerFactor_L3:=Long_0;
4313:Circ2THDI_L1:=Long_0;
4315:Circ2THDI_L2:=Long_0;
4317:Circ2THDI_L3:=Long_0;
4319:Circ2THDV_L1:=Long_0;
4321:Circ2THDV_L2:=Long_0;
4323:Circ2THDV_L3:=Long_0;
4325:Circ2Tok_L1:=Long_0;
4327:Circ2Tok_L2:=Long_0;
4329:Circ2Tok_L3:=Long_0;
4331:Circ2TokPovprecje_III:=Long_0;
4333:Circ3CosFi_III:=Long_0;
4335:Circ3DelovnaEnergija:=Long_0;
4337:Circ3DelovnaMoc_III:=Long_0;
4339:Circ3DelovnaMoc_L1:=Long_0;
4341:Circ3DelovnaMoc_L2:=Long_0;
4343:Circ3DelovnaMoc_L3:=Long_0;
4345:Circ3Frekvenca_L1:=Long_0;
4347:Circ3InduktivnaEnergija:=Long_0;
4349:Circ3InduktivnaMoc_III:=Long_0;
4351:Circ3JalovaMoc_L1:=Long_0;
4353:Circ3JalovaMoc_L2:=Long_0;
4355:Circ3JalovaMoc_L3:=Long_0;
4357:Circ3KapacitivnaEnergija:=Long_0;
4359:Circ3KapacitivnaMoc_III:=Long_0;
4361:Circ3MaximumDemand:=Long_0;
4363:Circ3Napetost_L1_L2:=Long_0;
4365:Circ3Napetost_L1_N:=Long_0;
4367:Circ3Napetost_L2_L3:=Long_0;
4369:Circ3Napetost_L2_N:=Long_0;
4371:Circ3Napetost_L3_L1:=Long_0;
4373:Circ3Napetost_L3_N:=Long_0;
4375:Circ3NavideznaMoc_III:=Long_0;
4377:Circ3NicelniTok:=Long_0;
4379:Circ3PowerFactor_III:=Long_0;
4381:Circ3PowerFactor_L1:=Long_0;
4383:Circ3PowerFactor_L2:=Long_0;
4385:Circ3PowerFactor_L3:=Long_0;
4387:Circ3THDI_L1:=Long_0;
4389:Circ3THDI_L2:=Long_0;
4391:Circ3THDI_L3:=Long_0;
4393:Circ3THDV_L1:=Long_0;
4395:Circ3THDV_L2:=Long_0;
4397:Circ3THDV_L3:=Long_0;
4399:Circ3Tok_L1:=Long_0;
4401:Circ3Tok_L2:=Long_0;
4403:Circ3Tok_L3:=Long_0;
4405:Circ3TokPovprecje_III:=Long_0;
4407:Circ4CosFi_III:=Long_0;
4409:Circ4DelovnaEnergija:=Long_0;
4411:Circ4DelovnaMoc_III:=Long_0;
4413:Circ4DelovnaMoc_L1:=Long_0;
4415:Circ4DelovnaMoc_L2:=Long_0;
4417:Circ4DelovnaMoc_L3:=Long_0;
4419:Circ4Frekvenca_L1:=Long_0;
4421:Circ4InduktivnaEnergija:=Long_0;
4423:Circ4InduktivnaMoc_III:=Long_0;
4425:Circ4JalovaMoc_L1:=Long_0;
4427:Circ4JalovaMoc_L2:=Long_0;
4429:Circ4JalovaMoc_L3:=Long_0;
4431:Circ4KapacitivnaEnergija:=Long_0;
4433:Circ4KapacitivnaMoc_III:=Long_0;
4435:Circ4MaximumDemand:=Long_0;
4437:Circ4Napetost_L1_L2:=Long_0;
4439:Circ4Napetost_L1_N:=Long_0;
4441:Circ4Napetost_L2_L3:=Long_0;
4443:Circ4Napetost_L2_N:=Long_0;
4445:Circ4Napetost_L3_L1:=Long_0;
4447:Circ4Napetost_L3_N:=Long_0;
4449:Circ4NavideznaMoc_III:=Long_0;
4451:Circ4NicelniTok:=Long_0;
4453:Circ4PowerFactor_III:=Long_0;
4455:Circ4PowerFactor_L1:=Long_0;
4457:Circ4PowerFactor_L2:=Long_0;
4459:Circ4PowerFactor_L3:=Long_0;
4461:Circ4THDI_L1:=Long_0;
4463:Circ4THDI_L2:=Long_0;
4465:Circ4THDI_L3:=Long_0;
4467:Circ4THDV_L1:=Long_0;
4469:Circ4THDV_L2:=Long_0;
4471:Circ4THDV_L3:=Long_0;
4473:Circ4Tok_L1:=Long_0;
4475:Circ4Tok_L2:=Long_0;
4477:Circ4Tok_L3:=Long_0;
4479:Circ4TokPovprecje_III:=Long_0;
4481:Circ5CosFi_III:=Long_0;
4483:Circ5DelovnaEnergija:=Long_0;
4485:Circ5DelovnaMoc_III:=Long_0;
4487:Circ5DelovnaMoc_L1:=Long_0;
4489:Circ5DelovnaMoc_L2:=Long_0;
4491:Circ5DelovnaMoc_L3:=Long_0;
4493:Circ5Frekvenca_L1:=Long_0;
4495:Circ5InduktivnaEnergija:=Long_0;
4497:Circ5InduktivnaMoc_III:=Long_0;
4499:Circ5JalovaMoc_L1:=Long_0;
4501:Circ5JalovaMoc_L2:=Long_0;
4503:Circ5JalovaMoc_L3:=Long_0;
4505:Circ5KapacitivnaEnergija:=Long_0;
4507:Circ5KapacitivnaMoc_III:=Long_0;
4509:Circ5MaximumDemand:=Long_0;
4511:Circ5Napetost_L1_L2:=Long_0;
4513:Circ5Napetost_L1_N:=Long_0;
4515:Circ5Napetost_L2_L3:=Long_0;
4517:Circ5Napetost_L2_N:=Long_0;
4519:Circ5Napetost_L3_L1:=Long_0;
4521:Circ5Napetost_L3_N:=Long_0;
4523:Circ5NavideznaMoc_III:=Long_0;
4525:Circ5NicelniTok:=Long_0;
4527:Circ5PowerFactor_III:=Long_0;
4529:Circ5PowerFactor_L1:=Long_0;
4531:Circ5PowerFactor_L2:=Long_0;
4533:Circ5PowerFactor_L3:=Long_0;
4535:Circ5THDI_L1:=Long_0;
4537:Circ5THDI_L2:=Long_0;
4539:Circ5THDI_L3:=Long_0;
4541:Circ5THDV_L1:=Long_0;
4543:Circ5THDV_L2:=Long_0;
4545:Circ5THDV_L3:=Long_0;
4547:Circ5Tok_L1:=Long_0;
4549:Circ5Tok_L2:=Long_0;
4551:Circ5Tok_L3:=Long_0;
4553:Circ5TokPovprecje_III:=Long_0;
4555:Circ6CosFi_III:=Long_0;
4557:Circ6DelovnaEnergija:=Long_0;
4559:Circ6DelovnaMoc_III:=Long_0;
4561:Circ6DelovnaMoc_L1:=Long_0;
4563:Circ6DelovnaMoc_L2:=Long_0;
4565:Circ6DelovnaMoc_L3:=Long_0;
4567:Circ6Frekvenca_L1:=Long_0;
4569:Circ6InduktivnaEnergija:=Long_0;
4571:Circ6InduktivnaMoc_III:=Long_0;
4573:Circ6JalovaMoc_L1:=Long_0;
4575:Circ6JalovaMoc_L2:=Long_0;
4577:Circ6JalovaMoc_L3:=Long_0;
4579:Circ6KapacitivnaEnergija:=Long_0;
4581:Circ6KapacitivnaMoc_III:=Long_0;
4583:Circ6MaximumDemand:=Long_0;
4585:Circ6Napetost_L1_L2:=Long_0;
4587:Circ6Napetost_L1_N:=Long_0;
4589:Circ6Napetost_L2_L3:=Long_0;
4591:Circ6Napetost_L2_N:=Long_0;
4593:Circ6Napetost_L3_L1:=Long_0;
4595:Circ6Napetost_L3_N:=Long_0;
4597:Circ6NavideznaMoc_III:=Long_0;
4599:Circ6NicelniTok:=Long_0;
4601:Circ6PowerFactor_III:=Long_0;
4603:Circ6PowerFactor_L1:=Long_0;
4605:Circ6PowerFactor_L2:=Long_0;
4607:Circ6PowerFactor_L3:=Long_0;
4609:Circ6THDI_L1:=Long_0;
4611:Circ6THDI_L2:=Long_0;
4613:Circ6THDI_L3:=Long_0;
4615:Circ6THDV_L1:=Long_0;
4617:Circ6THDV_L2:=Long_0;
4619:Circ6THDV_L3:=Long_0;
4621:Circ6Tok_L1:=Long_0;
4623:Circ6Tok_L2:=Long_0;
4625:Circ6Tok_L3:=Long_0;
4627:Circ6TokPovprecje_III:=Long_0;
4629:Circ7CosFi_III:=Long_0;
4631:Circ7DelovnaEnergija:=Long_0;
4633:Circ7DelovnaMoc_III:=Long_0;
4635:Circ7DelovnaMoc_L1:=Long_0;
4637:Circ7DelovnaMoc_L2:=Long_0;
4639:Circ7DelovnaMoc_L3:=Long_0;
4641:Circ7Frekvenca_L1:=Long_0;
4643:Circ7InduktivnaEnergija:=Long_0;
4645:Circ7InduktivnaMoc_III:=Long_0;
4647:Circ7JalovaMoc_L1:=Long_0;
4649:Circ7JalovaMoc_L2:=Long_0;
4651:Circ7JalovaMoc_L3:=Long_0;
4653:Circ7KapacitivnaEnergija:=Long_0;
4655:Circ7KapacitivnaMoc_III:=Long_0;
4657:Circ7MaximumDemand:=Long_0;
4659:Circ7Napetost_L1_L2:=Long_0;
4661:Circ7Napetost_L1_N:=Long_0;
4663:Circ7Napetost_L2_L3:=Long_0;
4665:Circ7Napetost_L2_N:=Long_0;
4667:Circ7Napetost_L3_L1:=Long_0;
4669:Circ7Napetost_L3_N:=Long_0;
4671:Circ7NavideznaMoc_III:=Long_0;
4673:Circ7NicelniTok:=Long_0;
4675:Circ7PowerFactor_III:=Long_0;
4677:Circ7PowerFactor_L1:=Long_0;
4679:Circ7PowerFactor_L2:=Long_0;
4681:Circ7PowerFactor_L3:=Long_0;
4683:Circ7THDI_L1:=Long_0;
4685:Circ7THDI_L2:=Long_0;
4687:Circ7THDI_L3:=Long_0;
4689:Circ7THDV_L1:=Long_0;
4691:Circ7THDV_L2:=Long_0;
4693:Circ7THDV_L3:=Long_0;
4695:Circ7Tok_L1:=Long_0;
4697:Circ7Tok_L2:=Long_0;
4699:Circ7Tok_L3:=Long_0;
4701:Circ7TokPovprecje_III:=Long_0;
4703:Circ8CosFi_III:=Long_0;
4705:Circ8DelovnaEnergija:=Long_0;
4707:Circ8DelovnaMoc_III:=Long_0;
4709:Circ8DelovnaMoc_L1:=Long_0;
4711:Circ8DelovnaMoc_L2:=Long_0;
4713:Circ8DelovnaMoc_L3:=Long_0;
4715:Circ8Frekvenca_L1:=Long_0;
4717:Circ8InduktivnaEnergija:=Long_0;
4719:Circ8InduktivnaMoc_III:=Long_0;
4721:Circ8JalovaMoc_L1:=Long_0;
4723:Circ8JalovaMoc_L2:=Long_0;
4725:Circ8JalovaMoc_L3:=Long_0;
4727:Circ8KapacitivnaEnergija:=Long_0;
4729:Circ8KapacitivnaMoc_III:=Long_0;
4731:Circ8MaximumDemand:=Long_0;
4733:Circ8Napetost_L1_L2:=Long_0;
4735:Circ8Napetost_L1_N:=Long_0;
4737:Circ8Napetost_L2_L3:=Long_0;
4739:Circ8Napetost_L2_N:=Long_0;
4741:Circ8Napetost_L3_L1:=Long_0;
4743:Circ8Napetost_L3_N:=Long_0;
4745:Circ8NavideznaMoc_III:=Long_0;
4747:Circ8NicelniTok:=Long_0;
4749:Circ8PowerFactor_III:=Long_0;
4751:Circ8PowerFactor_L1:=Long_0;
4753:Circ8PowerFactor_L2:=Long_0;
4755:Circ8PowerFactor_L3:=Long_0;
4757:Circ8THDI_L1:=Long_0;
4759:Circ8THDI_L2:=Long_0;
4761:Circ8THDI_L3:=Long_0;
4763:Circ8THDV_L1:=Long_0;
4765:Circ8THDV_L2:=Long_0;
4767:Circ8THDV_L3:=Long_0;
4769:Circ8Tok_L1:=Long_0;
4771:Circ8Tok_L2:=Long_0;
4773:Circ8Tok_L3:=Long_0;
4775:Circ8TokPovprecje_III:=Long_0;
4777:Circ9CosFi_III:=Long_0;
4779:Circ9DelovnaEnergija:=Long_0;
4781:Circ9DelovnaMoc_III:=Long_0;
4783:Circ9DelovnaMoc_L1:=Long_0;
4785:Circ9DelovnaMoc_L2:=Long_0;
4787:Circ9DelovnaMoc_L3:=Long_0;
4789:Circ9Frekvenca_L1:=Long_0;
4791:Circ9InduktivnaEnergija:=Long_0;
4793:Circ9InduktivnaMoc_III:=Long_0;
4795:Circ9JalovaMoc_L1:=Long_0;
4797:Circ9JalovaMoc_L2:=Long_0;
4799:Circ9JalovaMoc_L3:=Long_0;
4801:Circ9KapacitivnaEnergija:=Long_0;
4803:Circ9KapacitivnaMoc_III:=Long_0;
4805:Circ9MaximumDemand:=Long_0;
4807:Circ9Napetost_L1_L2:=Long_0;
4809:Circ9Napetost_L1_N:=Long_0;
4811:Circ9Napetost_L2_L3:=Long_0;
4813:Circ9Napetost_L2_N:=Long_0;
4815:Circ9Napetost_L3_L1:=Long_0;
4817:Circ9Napetost_L3_N:=Long_0;
4819:Circ9NavideznaMoc_III:=Long_0;
4821:Circ9NicelniTok:=Long_0;
4823:Circ9PowerFactor_III:=Long_0;
4825:Circ9PowerFactor_L1:=Long_0;
4827:Circ9PowerFactor_L2:=Long_0;
4829:Circ9PowerFactor_L3:=Long_0;
4831:Circ9THDI_L1:=Long_0;
4833:Circ9THDI_L2:=Long_0;
4835:Circ9THDI_L3:=Long_0;
4837:Circ9THDV_L1:=Long_0;
4839:Circ9THDV_L2:=Long_0;
4841:Circ9THDV_L3:=Long_0;
4843:Circ9Tok_L1:=Long_0;
4845:Circ9Tok_L2:=Long_0;
4847:Circ9Tok_L3:=Long_0;
4849:Circ9TokPovprecje_III:=Long_0;
4851:DW_Napake1:=Long_0;
4853:DW_Napake2:=Long_0;
4855:DW_Napake3:=Long_0;
4857:Generator_earth_currentA1:=Long_0;
4859:Generator_earth_currentA2:=Long_0;
4861:Generator_L1_currentA1:=Long_0;
4863:Generator_L1_currentA2:=Long_0;
4865:Generator_L1_L2_voltageA1:=Long_0;
4867:Generator_L1_L2_voltageA2:=Long_0;
4869:Generator_L1_N_voltageA1:=Long_0;
4871:Generator_L1_N_voltageA2:=Long_0;
4873:Generator_L1_wattsA1:=Long_0;
4875:Generator_L1_wattsA2:=Long_0;
4877:Generator_L2_currentA1:=Long_0;
4879:Generator_L2_currentA2:=Long_0;
4881:Generator_L2_L3_voltageA1:=Long_0;
4883:Generator_L2_L3_voltageA2:=Long_0;
4885:Generator_L2_N_voltageA1:=Long_0;
4887:Generator_L2_N_voltageA2:=Long_0;
4889:Generator_L2_wattsA1:=Long_0;
4891:Generator_L2_wattsA2:=Long_0;
4893:Generator_L3_currentA1:=Long_0;
4895:Generator_L3_currentA2:=Long_0;
4897:Generator_L3_L1_voltageA1:=Long_0;
4899:Generator_L3_L1_voltageA2:=Long_0;
4901:Generator_L3_N_voltageA1:=Long_0;
4903:Generator_L3_N_voltageA2:=Long_0;
4905:Generator_L3_wattsA1:=Long_0;
4907:Generator_L3_wattsA2:=Long_0;
4909:Circ14NicelniTok:=Long_0;
4911:Circ14Tok_L1:=Long_0;
4913:Circ14Tok_L2:=Long_0;
4915:Circ14Tok_L3:=Long_0;
4917:Circ8NicelniTok:=Long_0;
4919:Circ8Tok_L1:=Long_0;
4921:Circ8Tok_L2:=Long_0;
4923:Circ8Tok_L3:=Long_0;
4925:Circ9NicelniTok:=Long_0;
4927:Circ9Tok_L1:=Long_0;
4929:Circ9Tok_L2:=Long_0;
4931:Circ9Tok_L3:=Long_0;
4933:Circ1MaximumDemandA2:=Long_0;
4935:Circ1MaximumDemandA3:=Long_0;
4937:Circ2MaximumDemandA2:=Long_0;
4939:Circ2MaximumDemandA3:=Long_0;
4941:Circ3MaximumDemandA2:=Long_0;
4943:Circ3MaximumDemandA3:=Long_0;
4945:Circ4MaximumDemandA2:=Long_0;
4947:Circ4MaximumDemandA3:=Long_0;
4949:Circ5MaximumDemandA2:=Long_0;
4951:Circ5MaximumDemandA3:=Long_0;
4953:Circ6MaximumDemandA2:=Long_0;
4955:Circ6MaximumDemandA3:=Long_0;
4957:Circ7MaximumDemandA2:=Long_0;
4959:Circ7MaximumDemandA3:=Long_0;
4961:Circ8MaximumDemandA2:=Long_0;
4963:Circ8MaximumDemandA3:=Long_0;
4965:Circ9MaximumDemandA2:=Long_0;
4967:Circ9MaximumDemandA3:=Long_0;
4969:Circ10MaximumDemandA2:=Long_0;
4971:Circ10MaximumDemandA3:=Long_0;
4973:Circ11MaximumDemandA2:=Long_0;
4975:Circ11MaximumDemandA3:=Long_0;
4977:Circ12MaximumDemandA2:=Long_0;
4979:Circ12MaximumDemandA3:=Long_0;
4981:Circ13MaximumDemandA2:=Long_0;
4983:Circ13MaximumDemandA3:=Long_0;
4985:Circ14MaximumDemandA2:=Long_0;
4987:Circ14MaximumDemandA3:=Long_0;
4989:Circ15MaximumDemandA2:=Long_0;
4991:Circ15MaximumDemandA3:=Long_0;
4993:Circ16MaximumDemandA2:=Long_0;
4995:Circ16MaximumDemandA3:=Long_0;
4997:Circ17MaximumDemandA2:=Long_0;
4999:Circ17MaximumDemandA3:=Long_0;
5001:Circ18MaximumDemandA2:=Long_0;
5003:Circ18MaximumDemandA3:=Long_0;
5005:Circ19MaximumDemandA2:=Long_0;
5007:Circ19MaximumDemandA3:=Long_0;
5009:Circ20MaximumDemandA2:=Long_0;
5011:Circ20MaximumDemandA3:=Long_0;
5013:Circ21MaximumDemandA2:=Long_0;
5015:Circ21MaximumDemandA3:=Long_0;
5017:Circ22MaximumDemandA2:=Long_0;
5019:Circ22MaximumDemandA3:=Long_0;
5021:Circ23MaximumDemandA2:=Long_0;
5023:Circ23MaximumDemandA3:=Long_0;
5025:Circ24MaximumDemandA2:=Long_0;
5027:Circ24MaximumDemandA3:=Long_0;
5029:Circ25MaximumDemandA2:=Long_0;
5031:Circ25MaximumDemandA3:=Long_0;
5033:Circ[1].RazEner_D_SCADA:=Long_0;
5035:Circ[1].RazEner_T_SCADA:=Long_0;
5037:Circ[1].RazEner_M_SCADA:=Long_0;
5039:Circ[2].RazEner_D_SCADA:=Long_0;
5041:Circ[2].RazEner_T_SCADA:=Long_0;
5043:Circ[2].RazEner_M_SCADA:=Long_0;
5045:Circ[3].RazEner_D_SCADA:=Long_0;
5047:Circ[3].RazEner_T_SCADA:=Long_0;
5049:Circ[3].RazEner_M_SCADA:=Long_0;
5051:Circ[4].RazEner_D_SCADA:=Long_0;
5053:Circ[4].RazEner_T_SCADA:=Long_0;
5055:Circ[4].RazEner_M_SCADA:=Long_0;
5057:Circ[5].RazEner_D_SCADA:=Long_0;
5059:Circ[5].RazEner_T_SCADA:=Long_0;
5061:Circ[5].RazEner_M_SCADA:=Long_0;
5063:Circ[6].RazEner_D_SCADA:=Long_0;
5065:Circ[6].RazEner_T_SCADA:=Long_0;
5067:Circ[6].RazEner_M_SCADA:=Long_0;
5069:Circ[7].RazEner_D_SCADA:=Long_0;
5071:Circ[7].RazEner_T_SCADA:=Long_0;
5073:Circ[7].RazEner_M_SCADA:=Long_0;
5075:Circ[8].RazEner_D_SCADA:=Long_0;
5077:Circ[8].RazEner_T_SCADA:=Long_0;
5079:Circ[8].RazEner_M_SCADA:=Long_0;
5081:Circ[9].RazEner_D_SCADA:=Long_0;
5083:Circ[9].RazEner_T_SCADA:=Long_0;
5085:Circ[9].RazEner_M_SCADA:=Long_0;
5087:Circ[10].RazEner_D_SCADA:=Long_0;
5089:Circ[10].RazEner_T_SCADA:=Long_0;
5091:Circ[10].RazEner_M_SCADA:=Long_0;
5093:Circ[11].RazEner_D_SCADA:=Long_0;
5095:Circ[11].RazEner_T_SCADA:=Long_0;
5097:Circ[11].RazEner_M_SCADA:=Long_0;
5099:Circ[12].RazEner_D_SCADA:=Long_0;
5101:Circ[12].RazEner_T_SCADA:=Long_0;
5103:Circ[12].RazEner_M_SCADA:=Long_0;
5105:Circ[13].RazEner_D_SCADA:=Long_0;
5107:Circ[13].RazEner_T_SCADA:=Long_0;
5109:Circ[13].RazEner_M_SCADA:=Long_0;
5111:Circ[14].RazEner_D_SCADA:=Long_0;
5113:Circ[14].RazEner_T_SCADA:=Long_0;
5115:Circ[14].RazEner_M_SCADA:=Long_0;
5117:Circ[15].RazEner_D_SCADA:=Long_0;
5119:Circ[15].RazEner_T_SCADA:=Long_0;
5121:Circ[15].RazEner_M_SCADA:=Long_0;
5123:Circ[16].RazEner_D_SCADA:=Long_0;
5125:Circ[16].RazEner_T_SCADA:=Long_0;
5127:Circ[16].RazEner_M_SCADA:=Long_0;
5129:Circ[17].RazEner_D_SCADA:=Long_0;
5131:Circ[17].RazEner_T_SCADA:=Long_0;
5133:Circ[17].RazEner_M_SCADA:=Long_0;
5135:Circ[18].RazEner_D_SCADA:=Long_0;
5137:Circ[18].RazEner_T_SCADA:=Long_0;
5139:Circ[18].RazEner_M_SCADA:=Long_0;
5141:Circ[19].RazEner_D_SCADA:=Long_0;
5143:Circ[19].RazEner_T_SCADA:=Long_0;
5145:Circ[19].RazEner_M_SCADA:=Long_0;
5147:Circ[20].RazEner_D_SCADA:=Long_0;
5149:Circ[20].RazEner_T_SCADA:=Long_0;
5151:Circ[20].RazEner_M_SCADA:=Long_0;
5153:Circ[21].RazEner_D_SCADA:=Long_0;
5155:Circ[21].RazEner_T_SCADA:=Long_0;
5157:Circ[21].RazEner_M_SCADA:=Long_0;
5159:Circ[22].RazEner_D_SCADA:=Long_0;
5161:Circ[22].RazEner_T_SCADA:=Long_0;
5163:Circ[22].RazEner_M_SCADA:=Long_0;
5165:Circ[23].RazEner_D_SCADA:=Long_0;
5167:Circ[23].RazEner_T_SCADA:=Long_0;
5169:Circ[23].RazEner_M_SCADA:=Long_0;
5171:Circ[24].RazEner_D_SCADA:=Long_0;
5173:Circ[24].RazEner_T_SCADA:=Long_0;
5175:Circ[24].RazEner_M_SCADA:=Long_0;
5177:Circ[25].RazEner_D_SCADA:=Long_0;
5179:Circ[25].RazEner_T_SCADA:=Long_0;
5181:Circ[25].RazEner_M_SCADA:=Long_0;
(*Pisanje REAL*)
(**)
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_String : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje STRING*)
(**)
5000:cas_scada:=String_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Word : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje INT*)
(**)
0:Coolant_temperatureA1:=Word_01;
1:Coolant_temperatureA2:=Word_01;
2:delovna_energ_trenutno:=Word_01;
3:delovna_energija_prej:=Word_01;
4:Generator_current_lag_leadA1:=Word_01;
5:Generator_current_lag_leadA2:=Word_01;
6:jalova_energ_trenutno:=Word_01;
7:jalova_energija_prej:=Word_01;
8:Komanda:=Word_01;
9:NastaviDanMI:=Word_01;
10:NastaviLetoMI:=Word_01;
11:NastaviMesecMI:=Word_01;
12:NastaviMinutaMI:=Word_01;
13:NastaviSekundaMI:=Word_01;
14:NastaviUraMI:=Word_01;
15:Status:=Word_01;
16:st_izpad_komTPV:=Word_01;
(*Pisanje UINT*)
(**)
6000:Battery_voltageA1:=Word_01;
6001:Battery_voltageA2:=Word_01;
6002:Charge_alternator_voltageA1:=Word_01;
6003:Charge_alternator_voltageA2:=Word_01;
6004:Engine_speedA1:=Word_01;
6005:Engine_speedA2:=Word_01;
6006:Generator_frequencyA1:=Word_01;
6007:Generator_frequencyA2:=Word_01;
6008:Generator_phase_rotationA1:=Word_01;
6009:Generator_phase_rotationA2:=Word_01;
6010:Oil_pressureA1:=Word_01;
6011:Oil_pressureA2:=Word_01;
;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
(*Modbus Slave Example*)
PROGRAM PLC_PRG_modnet
VAR
Slave_Adresa:BYTE:=2;
Slave_Port:INT:=502;
SlaveSetup:MBS_Setup;
SlavePoll:MBS_Poll;
SlaveAnswer:MBS_Answer;
step: USINT;
end :BOOL;
i: INT;
cycle :BOOL := FALSE; (* First cycle *)
OpenDefaultPort: BOOL;
Write_16: BOOL;
Write_15: BOOL;
Write_5: BOOL;
j: INT;
slavepollwOffset_temp: INT;
slaveanswerwCount_temp: INT;
slaveanswerwoffset_temp: INT;
END_VAR
(* @END_DECLARATION := '0' *)
(*Modbus Slave Example*)
IF Write_16=TRUE THEN (**)
FOR j := 0 TO (slaveanswerwCount_temp-1)/15 BY 1 DO (*vpiše se dword, real*)
wStr_0:=mind[slaveanswerwoffset_temp+j];
wStr_1:=mind[slaveanswerwoffset_temp+j+1];
wStr_2 :=mind[slaveanswerwoffset_temp+j+2];
wStr_3:=mind[slaveanswerwoffset_temp+j+3];
wStr_4:=mind[slaveanswerwoffset_temp+j+4];
wStr_5 :=mind[slaveanswerwoffset_temp+j+5];
wStr_6:=mind[slaveanswerwoffset_temp+j+6];
wStr_7:=mind[slaveanswerwoffset_temp+j+7];
wStr_8:=mind[slaveanswerwoffset_temp+j+8];
wStr_9:=mind[slaveanswerwoffset_temp+j+9];
wStr_10:=mind[slaveanswerwoffset_temp+j+10];
wStr_11:=mind[slaveanswerwoffset_temp+j+11];
wStr_12:=mind[slaveanswerwoffset_temp+j+12];
wStr_13:=mind[slaveanswerwoffset_temp+j+13];
wStr_14:=mind[slaveanswerwoffset_temp+j+14];
bStr_29:=0;
mod_Write_String(index:=slaveanswerwoffset_temp+j); (*vpis real in string*)
END_FOR;
FOR j := 1 TO slaveanswerwCount_temp-1 BY 2 DO (*vpiše se dword, real*)
Word_01:=mind[slaveanswerwoffset_temp+j-1];
Word_23:=mind[slaveanswerwoffset_temp+j];
mod_Write_dWord(index:=slaveanswerwoffset_temp+j); (*vpis real in dword*)
END_FOR;
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO (*vpiše se word*)
Word_01:=mind[slaveanswerwoffset_temp+j];
mod_Write_Word(index:=slaveanswerwoffset_temp+j); (*vpis word*)
END_FOR;
Write_16:=FALSE;
END_IF;
IF Write_5=TRUE OR Write_15=TRUE THEN (**)
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO
Bit_0:=mind_bool[slaveanswerwoffset_temp+j];
mod_Write_Bool(index:=slaveanswerwoffset_temp+j); (*vpis spremembe v spremenljivko*)
END_FOR;
Write_5:=FALSE;
Write_15:=FALSE;
END_IF;
(*iz scade ni komande za branje*)
IF Write_16=FALSE AND Write_5=FALSE AND Write_15=FALSE THEN
mod_Read();(*branje spremenljivk za scado*)
END_IF
(*Close all sockets on corresponding event*)
IF cycle = FALSE THEN
SysCallbackRegister(INDEXOF(Callback_Stop),event_stop);
SysCallbackRegister(INDEXOF(Callback_Reset),event_before_reset);
SysCallbackRegister(INDEXOF(Callback_Reset),event_shutdown);
cycle := TRUE;
END_IF
(*Close all connections via application *)
IF end = TRUE THEN
MBS_CloseAllConnections();
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=FALSE); (*Close port*)
step := 0;
END_IF
IF OpenDefaultPort=TRUE THEN
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=TRUE); (*Close port*)
step := 0;
OpenDefaultPort:=FALSE;
END_IF
(* State machine for setup, poll and answer *)
CASE step OF
0:(**)
SlaveSetup.bUnitIdentifier:=Slave_Adresa;(*Subunitnumber*)
slavesetup.wDefaultPort:=Slave_Port;(*Standartport *)
SlaveSetup.xAdditionalPortActive:=FALSE;(*Port opened or closed*)
SlaveSetup.xSecureMode:=FALSE;(*If TRUE only preset IPs are accepted*)
SlaveSetup.tTimeout:=T#3m;(*Timeout if no communication with slave established*)
SlaveSetup(xStrobe:=TRUE);(*Strobe starts function*)
IF slavesetup.xBusy = FALSE THEN
slavesetup(xstrobe := FALSE);
step := 1 ;
END_IF;
1:(**)
SlavePoll(xStrobe:=TRUE);(*Searching for master commands*)
IF NOT SlavePoll.xBusy THEN
step:=2;
SlavePoll(xStrobe:=FALSE);
END_IF;
2:(**)
step:= 1;
CASE SlavePoll.bFunctionCode OF (*Connect accepted pollparameters with answerparameters*)
8:(**)(*Poll answers*)
;
15:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind_bool[slaveanswer.woffset+i] := slavepoll.xarData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.xarData:=slavepoll.xarData;
Write_15:=TRUE;
16:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind[slaveanswer.woffset+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.wardata := slavepoll.warData;
Write_16:=TRUE;
1,2:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slavepoll.wcount-1 BY 1 DO
slaveanswer.xarData[i]:=mind_bool[slavepoll.woffset+i]; (*Read from Data-array*)
END_FOR
3,4:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slaveanswer.wCount-1 BY 1 DO
slaveanswer.warData[i]:=mind[slavepoll.woffset+i];(*Read from Data-array*)
END_FOR
5:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
mind_bool[slavepoll.woffset]:=slavepoll.xarData[0];(*Write to Data-array*)
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.xarData := slavepoll.xardata;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
Write_5:=TRUE;
6:
slaveanswer.bFunctionCode:= slavepoll.bFunctionCode;
mind[slavepoll.woffset]:= slavepoll.warData[0];(*Write to Data-array*)
slaveanswer.wOffset:= slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wardata := slavepoll.wardata;
23:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
FOR i:= 0 TO slavepoll.wCountAdd-1 BY 1 DO
mind[slavepoll.woffsetadd+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
FOR i := 0 TO slavepoll.wCount BY 1 DO
slaveanswer.warData[i] := mind[1+slavepoll.woffset+i];(*Read from Data-array*)
END_FOR;
END_CASE;
IF slavepoll.xAvailable = TRUE THEN
slaveanswer();(*When Data ready, send answer*)
END_IF
END_CASE;
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_dWord : BOOL
VAR_INPUT
dVAR: DWORD;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
DWord_0:=dVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_Real : BOOL
VAR_INPUT
rVAR: REAL;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
Real_0:=rVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_String : BOOL
VAR_INPUT
sVar: STRING;
start:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
String_0:=LEFT (sVar,29);
mind[start]:=wStr_0;
mind[start+1]:=wStr_1;
mind[start+2]:=wStr_2;
mind[start+3]:=wStr_3;
mind[start+4]:=wStr_4;
mind[start+5]:=wStr_5;
mind[start+6]:=wStr_6;
mind[start+7]:=wStr_7;
mind[start+8]:=wStr_8;
mind[start+9]:=wStr_9;
mind[start+10]:=wStr_10;
mind[start+11]:=wStr_11;
mind[start+12]:=wStr_12;
mind[start+13]:=wStr_13;
bStr_29:=0;
mind[start+14]:=wStr_14;
END_FUNCTION
(* @GLOBAL_VARIABLE_LIST := 'Global_Variables_Modnet' *)
(* @PATH := '' *)
(* @SYMFILEFLAGS := '2048' *)
VAR_GLOBAL
(*delovno polje za modnet komunikacijo*)
mind :ARRAY [0..9999] OF WORD;
mind_bool :ARRAY [0..9999] OF BOOL; (*Buffer-Array*)
(*Delovni markerji //*)
Bit_0 AT %MX0.0 : BOOL;
Byte_0 AT %MB0 : BYTE;
Byte_1 AT %MB1 : BYTE;
Byte_2 AT %MB2 : BYTE;
Byte_3 AT %MB3 : BYTE;
Real_0 AT %MR0:REAL;
Long_0 AT %MD0:DINT;
DWord_0 AT %MD0:DWORD;
Word_01 AT %MW0:WORD;
Word_23 AT %MW2:WORD;
String_0 AT %MW10:STRING;
wStr_0 AT %MW10:WORD;
wStr_1 AT %MW12:WORD;
wStr_2 AT %MW14:WORD;
wStr_3 AT %MW16:WORD;
wStr_4 AT %MW18:WORD;
wStr_5 AT %MW20:WORD;
wStr_6 AT %MW22:WORD;
wStr_7 AT %MW24:WORD;
wStr_8 AT %MW26:WORD;
wStr_9 AT %MW28:WORD;
wStr_10 AT %MW30:WORD;
wStr_11 AT %MW32:WORD;
wStr_12 AT %MW34:WORD;
wStr_13 AT %MW36:WORD;
wStr_14 AT %MW38:WORD;
bStr_00 AT %MB10:BYTE;
bStr_01 AT %MB11:BYTE;
bStr_02 AT %MB12:BYTE;
bStr_03 AT %MB13:BYTE;
bStr_04 AT %MB14:BYTE;
bStr_05 AT %MB15:BYTE;
bStr_06 AT %MB16:BYTE;
bStr_07 AT %MB17:BYTE;
bStr_08 AT %MB18:BYTE;
bStr_09 AT %MB19:BYTE;
bStr_10 AT %MB20:BYTE;
bStr_11 AT %MB21:BYTE;
bStr_12 AT %MB22:BYTE;
bStr_13 AT %MB23:BYTE;
bStr_14 AT %MB24:BYTE;
bStr_15 AT %MB25:BYTE;
bStr_16 AT %MB26:BYTE;
bStr_17 AT %MB27:BYTE;
bStr_18 AT %MB28:BYTE;
bStr_19 AT %MB29:BYTE;
bStr_20 AT %MB30:BYTE;
bStr_21 AT %MB31:BYTE;
bStr_22 AT %MB32:BYTE;
bStr_23 AT %MB33:BYTE;
bStr_24 AT %MB34:BYTE;
bStr_25 AT %MB35:BYTE;
bStr_26 AT %MB36:BYTE;
bStr_27 AT %MB37:BYTE;
bStr_28 AT %MB38:BYTE;
bStr_29 AT %MB39:BYTE;
(********************************************)
END_VAR
(* @OBJECT_END := 'Global_Variables_Modnet' *)
(* @CONNECTIONS := Global_Variables_Modnet
FILENAME : ''
FILETIME : 0
EXPORT : 0
NUMOFCONNECTIONS : 0
*)
(*KONEC_KODA*)