## Prva stran
variable | 3857 | 1.KORAK | variable_1 | 2.KORAK | KORAKI!
Device name | Tip | število spremenljivk | Tip (izbrani) | Zamenjaj z | 1.V Sheet "variable" skopiraj vsebino iz variable.dbf - iz Citect SCAD-a projekta, ki ga želiš pretvoriti.
IOD_EP2 | BCD | 0 | BCD | INT | 2.V polje A3 vpiši Device ime spremenljivk ki se bodo prenašale preko Modnet protokola
| BYTE | 259 | BYTE | BYTE | 3.V polje A6 vpiši ime krmilnika (npr.:PLC1, če je adresa v spremenljivkah PLC1:.NapakaKoncnega_stikala, drugače pusti polje prazno)
OPC name | DIGITAL | 442 | DIGITAL | DIGITAL | 4. Pritisni gumb 1.KORAK (V poljih C3:C10 se izpiše število spremenljivk, ki imajo Device enak tistemu v polju A3)
EP2 | INT | 96 | INT | INT | 5. Pritisni gumb 2.KORAK (V Sheet-u variable_1 se naredi seznam spremenljivk, ki se bodo prenačale preko Modnet protokola)
| LONG | 0 | LONG | LONG | 6. Pritisni gumb 3.KORAK (V poljih C15:C24 se izpiše število spremnljiv po tipih, v poljih F15:F24 se izpiše število potrebni wordow/coilov za prenos spremnljivk)
| REAL | 799 | REAL | REAL | 7. 4.KORAK: V polja C29:C38 je potrebno ročno vpisati začetne naslove spremnljivk. Potrebno je paziti na:
| STRING | 1 | UINT | UINT | *naslov se morajo začeti z lihim številom npr.:1, 101, 551
| UINT | 19 | STRING | STRING | *naslove je potrebno nastaviti tako, da se naslovi sremenljivk ne more prekrivati (naslovi spremenjivk gredo od (začetnega naslova) do (začetnega naslova+število potrebnih wordow))
8. Pritisni gumb 5.KORAK (V Sheet-u variable_2 se naredi seznam spremenljivk, ki so tokrat sortirana po tipih)
9. Pritisni gumb 6.KORAK (V Sheet-u variable_3 se naredi seznam spremenljivk, katerih Device se zamenja z devicom v polju C41)
Trajanje makroja | variable_1 |  |  | 3.KORAK | 10. Pritisni gumb 7.KORAK (V Sheet-u variable_new se generira seznam spremenljivk. To vsebino je potrebno skopirati v variable.dbf)
0 | Tip | število spremenljivk | TIP | št.potrebnih coilov/wordov | *ta korak traja nekoliko dalj časa (odvisno od števila spremenljivk)
| BCD | 0 | BCD | 0 | *če se pojavi težava z adresami ki se začnejo z 0000 (npr.: "00001" se spremeni na "1") je potrebno uporabiti priloženo (prazno) variable.dbf ali v
| BYTE | 0 | BYTE | 0 | ProjectEditoju/VariableTags na poljubni spremenljki nastaviti adreso" 00001"
| DIGITAL | 442 | DIGITAL | 442 (Coil) | 11. Pritisni gumb 8.KORAK in 9.KORAK (V Sheet-u Xsoft se generira koda)
| INT | 355 | INT | 355 (word) | 12. S pritiskom na gumb 10.KORAK se zgenerira EXP koda za Xsoft (Xsoft_EXP)
| LONG | 0 | LONG | 0 (word) | 13. S pritiskom na gumb Save*.EXP se avtomatsko generira datoka *.EXP
| REAL | 799 | REAL | 1598 (word)
| STRING | 1 | STRING | 15 (word)
| UINT | 19 | UINT | 19 (word)
POZOR!
*V Sheet-u variable mora biti vsebina skopirana od polja A1 naprej (če je katera vrstica prazna makroji ne bodo delovali pravilno)
*Ena "STRING" spremenljivka zasede 15wordow (to pomeni 29 znakov, 1BYTE=1STRING)
|  | 4.KORAK(vpiši ročno) | variable_2 | 5.KORAK | *Dolžina "STRING" spremenljivk je 29 znakov (lahko tudi več vendar ne z uporabno tega dokumenta in XSoft programa,potrebna je modifikacija makrojev in Xsoft programa)
| Tip | Začetni naslov |  | Sortiraj | *Vsi stringi so enake dolžine (29)
| BCD |  |  | BCD | *"BYTE" spremenljivke se v variable.dbf spremenijo v "INT" (prenašanje posameznih bytov ni mogoče, niti naslavaljanje v citectscadi)
| BYTE |  |  | DIGITAL | *Naslovi spremenljivk se morajo obvezno začeti z lihim naslovom (preizkušeno je z začetnimi naslovi, ki se izpišejo po pritisku na gumb Ponastavi)
| DIGITAL | 1 |  | BYTE | *Z pritiskom na gumb RESET se pobriše vsebina vseh Sheet-ov razen Sheet-a variable (makor reset se izvaja precej časa)
| INT | 1 |  | INT | *makroji ne delujejo pravilno,če je v Sheet-u variable več kot 9999 vrstic oz. spremenljivk (število vseh spremnljivk je prikazano v polju B1)
| LONG | 3001 |  | LONG | *če se vsebine iz variable_new ne gre skpirat v variable.dbf datotek, vsebino skopirajte najprej v *.txt datoteko in nato v variable.dbf
| REAL | 4001 |  | REAL | *v polju A14 na Sheet-u Prva stran se prikazuje število ciklop do konca izvedbe makroja (samo za gumb 7.KORAK)
| STRING | 7001 |  | STRING
| UINT | 8001 |  | UINT
| variable_3 | 6.KORAK | variable_new | 7.KORAK
| New Device name | IOD_EP2_TCP |  | Nova variable dbf
|  |  | xSoft | 8.KORAK in 9.KORAK
xSoft koda
xSoft_EXP
Izvoz*.EXP
1.KORAK
2.KORAK
3.KORAK
5.KORAK
6.KORAK
7.KORAK
8.KORAK
9.KORAK
RESET
Ponastavi
10.KORAK
Save*.EXP

## variable
EP2_AlarmGenCirc1 | DIGITAL | IOD_EP2 | EP2:.AlarmGenCirc1
EP2_AlarmGenComm | DIGITAL | IOD_EP2 | EP2:.AlarmGenComm
EP2_AlarmGenDI | DIGITAL | IOD_EP2 | EP2:.AlarmGenDI
EP2_AlarmGenKlima5 | DIGITAL | IOD_EP2 | EP2:.AlarmGenKlima5
EP2_AlarmGenKlima6 | DIGITAL | IOD_EP2 | EP2:.AlarmGenKlima6
EP2_AlarmGenPMM1 | DIGITAL | IOD_EP2 | EP2:.AlarmGenPMM1
EP2_AlarmGenPMM2 | DIGITAL | IOD_EP2 | EP2:.AlarmGenPMM2
EP2_AlarmGenPMM3 | DIGITAL | IOD_EP2 | EP2:.AlarmGenPMM3
EP2_AlarmGenUPS1 | DIGITAL | IOD_EP2 | EP2:.AlarmGenUPS1
EP2_AlarmGenUPS2 | DIGITAL | IOD_EP2 | EP2:.AlarmGenUPS2
EP2_Circ1_CosFi_III | REAL | IOD_EP2 | EP2:.Circ[1].CosFi_III | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.##
EP2_Circ1_DelovnaEnergija | REAL | IOD_EP2 | EP2:.Circ[1].DelovnaEnergija | 0 | 600.0 | 0 | 600.0 | kW | ###.#
EP2_Circ1_DelovnaMoc_III | REAL | IOD_EP2 | EP2:.Circ[1].DelovnaMoc_III | 0 | 600.0 | 0 | 600.0 | kW | ###.#
EP2_Circ1_DelovnaMoc_L1 | REAL | IOD_EP2 | EP2:.Circ[1].DelovnaMoc_L1 | 0 | 600.0 | 0 | 600.0 | kW | ###.#
EP2_Circ1_DelovnaMoc_L2 | REAL | IOD_EP2 | EP2:.Circ[1].DelovnaMoc_L2 | 0 | 600.0 | 0 | 600.0 | kW | ###.#
EP2_Circ1_DelovnaMoc_L3 | REAL | IOD_EP2 | EP2:.Circ[1].DelovnaMoc_L3 | 0 | 600.0 | 0 | 600.0 | kW | ###.#
EP2_Circ1_Frekvenca_L1 | REAL | IOD_EP2 | EP2:.Circ[1].Frekvenca_L1 | 0 | 60.0 | 0 | 60.0 | Hz | ##.#
EP2_Circ1_InduktivnaEnergija | REAL | IOD_EP2 | EP2:.Circ[1].InduktivnaEnergija | 0 | 600.0 | 0 | 600.0 | kW | ###.#
EP2_Circ1_InduktivnaMoc_III | REAL | IOD_EP2 | EP2:.Circ[1].InduktivnaMoc_III | 0 | 600.0 | 0 | 600.0 | kVAR | ###.#
EP2_Circ1_JalovaMoc_L1 | REAL | IOD_EP2 | EP2:.Circ[1].JalovaMoc_L1 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.#
EP2_Circ1_JalovaMoc_L2 | REAL | IOD_EP2 | EP2:.Circ[1].JalovaMoc_L2 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.#
EP2_Circ1_JalovaMoc_L3 | REAL | IOD_EP2 | EP2:.Circ[1].JalovaMoc_L3 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.#
EP2_Circ1_KapacitivnaEnergija | REAL | IOD_EP2 | EP2:.Circ[1].KapacitivnaEnergija
EP2_Circ1_KapacitivnaMoc_III | REAL | IOD_EP2 | EP2:.Circ[1].KapacitivnaMoc_III | 0 | 600.0 | 0 | 600.0 | kVAR | ###.#
EP2_Circ1_MaximumDemand | REAL | IOD_EP2 | EP2:.Circ[1].MaximumDemand | 0 | 1200.0 | 0 | 1200.0 | A | ###.#
EP2_Circ1_Napetost_L1_L2 | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L1_L2 | 0 | 450.0 | 0 | 450.0 | V | ###.#
EP2_Circ1_Napetost_L1_N | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L1_N | 0 | 270.0 | 0 | 270.0 | V | ###.#
EP2_Circ1_Napetost_L2_L3 | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L2_L3 | 0 | 450.0 | 0 | 450.0 | V | ###.#
EP2_Circ1_Napetost_L2_N | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L2_N | 0 | 270.0 | 0 | 270.0 | V | ###.#
EP2_Circ1_Napetost_L3_L1 | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L3_L1 | 0 | 450.0 | 0 | 450.0 | V | ###.#
EP2_Circ1_Napetost_L3_N | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L3_N | 0 | 270.0 | 0 | 270.0 | V | ###.#
EP2_Circ1_NavideznaMoc_III | REAL | IOD_EP2 | EP2:.Circ[1].NavideznaMoc_III | 0 | 1200.0 | 0 | 1200.0 | kVA | ###.#
EP2_Circ1_NicelniTok | REAL | IOD_EP2 | EP2:.Circ[1].NicelniTok | 0 | 1200.0 | 0 | 1200.0 | A | ###.#
EP2_Circ1_PowerFactor_III | REAL | IOD_EP2 | EP2:.Circ[1].PowerFactor_III | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.##
EP2_Circ1_PowerFactor_L1 | REAL | IOD_EP2 | EP2:.Circ[1].PowerFactor_L1 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.##
EP2_Circ1_PowerFactor_L2 | REAL | IOD_EP2 | EP2:.Circ[1].PowerFactor_L2 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.##
EP2_Circ1_PowerFactor_L3 | REAL | IOD_EP2 | EP2:.Circ[1].PowerFactor_L3 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.##
EP2_Circ1_THDI_L1 | REAL | IOD_EP2 | EP2:.Circ[1].THDI_L1 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circ1_THDI_L2 | REAL | IOD_EP2 | EP2:.Circ[1].THDI_L2 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circ1_THDI_L3 | REAL | IOD_EP2 | EP2:.Circ[1].THDI_L3 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circ1_THDV_L1 | REAL | IOD_EP2 | EP2:.Circ[1].THDV_L1 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circ1_THDV_L2 | REAL | IOD_EP2 | EP2:.Circ[1].THDV_L2 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circ1_THDV_L3 | REAL | IOD_EP2 | EP2:.Circ[1].THDV_L3 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circ1_Tok_L1 | REAL | IOD_EP2 | EP2:.Circ[1].Tok_L1 | 0 | 600.0 | 0 | 600.0 | A | ###.#
EP2_Circ1_Tok_L2 | REAL | IOD_EP2 | EP2:.Circ[1].Tok_L2 | 0 | 600.0 | 0 | 600.0 | A | ###.#
EP2_Circ1_Tok_L3 | REAL | IOD_EP2 | EP2:.Circ[1].Tok_L3 | 0 | 600.0 | 0 | 600.0 | A | ###.#
EP2_Circ1_TokPovprecje_III | REAL | IOD_EP2 | EP2:.Circ[1].TokPovprecje_III | 0 | 600.0 | 0 | 600.0 | A | ###.#
EP2_Circutor_CosFi_III | REAL | IOD_EP2 | EP2:.Circutor.CosFi_III | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.##
EP2_Circutor_DelovnaEnergija | REAL | IOD_EP2 | EP2:.Circutor.DelovnaEnergija | 0 | 600.0 | 0 | 600.0 | kW | ###.#
EP2_Circutor_DelovnaMoc_III | REAL | IOD_EP2 | EP2:.Circutor.DelovnaMoc_III | 0 | 600.0 | 0 | 600.0 | kW | ###.#
EP2_Circutor_DelovnaMoc_L1 | REAL | IOD_EP2 | EP2:.Circutor.DelovnaMoc_L1 | 0 | 600.0 | 0 | 600.0 | kW | ###.#
EP2_Circutor_DelovnaMoc_L2 | REAL | IOD_EP2 | EP2:.Circutor.DelovnaMoc_L2 | 0 | 600.0 | 0 | 600.0 | kW | ###.#
EP2_Circutor_DelovnaMoc_L3 | REAL | IOD_EP2 | EP2:.Circutor.DelovnaMoc_L3 | 0 | 600.0 | 0 | 600.0 | kW | ###.#
EP2_Circutor_Frekvenca_L1 | REAL | IOD_EP2 | EP2:.Circutor.Frekvenca_L1 | 0 | 60.0 | 0 | 60.0 | Hz | ##.#
EP2_Circutor_InduktivnaEnergija | REAL | IOD_EP2 | EP2:.Circutor.InduktivnaEnergija | 0 | 600.0 | 0 | 600.0 | kW | ###.#
EP2_Circutor_InduktivnaMoc_III | REAL | IOD_EP2 | EP2:.Circutor.InduktivnaMoc_III | 0 | 600.0 | 0 | 600.0 | kVAR | ###.#
EP2_Circutor_JalovaMoc_L1 | REAL | IOD_EP2 | EP2:.Circutor.JalovaMoc_L1 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.#
EP2_Circutor_JalovaMoc_L2 | REAL | IOD_EP2 | EP2:.Circutor.JalovaMoc_L2 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.#
EP2_Circutor_JalovaMoc_L3 | REAL | IOD_EP2 | EP2:.Circutor.JalovaMoc_L3 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.#
EP2_Circutor_KapacitivnaEnergija | REAL | IOD_EP2 | EP2:.Circutor.KapacitivnaEnergija
EP2_Circutor_KapacitivnaMoc_III | REAL | IOD_EP2 | EP2:.Circutor.KapacitivnaMoc_III | 0 | 600.0 | 0 | 600.0 | kVAR | ###.#
EP2_Circutor_MaximumDemand | REAL | IOD_EP2 | EP2:.Circutor.MaximumDemand | 0 | 1200.0 | 0 | 1200.0 | A | ###.#
EP2_Circutor_Napetost_L1_L2 | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L1_L2 | 0 | 450.0 | 0 | 450.0 | V | ###.#
EP2_Circutor_Napetost_L1_N | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L1_N | 0 | 270.0 | 0 | 270.0 | V | ###.#
EP2_Circutor_Napetost_L2_L3 | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L2_L3 | 0 | 450.0 | 0 | 450.0 | V | ###.#
EP2_Circutor_Napetost_L2_N | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L2_N | 0 | 270.0 | 0 | 270.0 | V | ###.#
EP2_Circutor_Napetost_L3_L1 | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L3_L1 | 0 | 450.0 | 0 | 450.0 | V | ###.#
EP2_Circutor_Napetost_L3_N | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L3_N | 0 | 270.0 | 0 | 270.0 | V | ###.#
EP2_Circutor_NavideznaMoc_III | REAL | IOD_EP2 | EP2:.Circutor.NavideznaMoc_III | 0 | 1200.0 | 0 | 1200.0 | kVA | ###.#
EP2_Circutor_NicelniTok | REAL | IOD_EP2 | EP2:.Circutor.NicelniTok | 0 | 1200.0 | 0 | 1200.0 | A | ###.#
EP2_Circutor_PowerFactor_III | REAL | IOD_EP2 | EP2:.Circutor.PowerFactor_III | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.##
EP2_Circutor_PowerFactor_L1 | REAL | IOD_EP2 | EP2:.Circutor.PowerFactor_L1 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.##
EP2_Circutor_PowerFactor_L2 | REAL | IOD_EP2 | EP2:.Circutor.PowerFactor_L2 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.##
EP2_Circutor_PowerFactor_L3 | REAL | IOD_EP2 | EP2:.Circutor.PowerFactor_L3 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.##
EP2_Circutor_THDI_L1 | REAL | IOD_EP2 | EP2:.Circutor.THDI_L1 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circutor_THDI_L2 | REAL | IOD_EP2 | EP2:.Circutor.THDI_L2 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circutor_THDI_L3 | REAL | IOD_EP2 | EP2:.Circutor.THDI_L3 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circutor_THDV_L1 | REAL | IOD_EP2 | EP2:.Circutor.THDV_L1 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circutor_THDV_L2 | REAL | IOD_EP2 | EP2:.Circutor.THDV_L2 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circutor_THDV_L3 | REAL | IOD_EP2 | EP2:.Circutor.THDV_L3 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circutor_Tok_L1 | REAL | IOD_EP2 | EP2:.Circutor.Tok_L1 | 0 | 600.0 | 0 | 600.0 | A | ###.#
EP2_Circutor_Tok_L2 | REAL | IOD_EP2 | EP2:.Circutor.Tok_L2 | 0 | 600.0 | 0 | 600.0 | A | ###.#
EP2_Circutor_Tok_L3 | REAL | IOD_EP2 | EP2:.Circutor.Tok_L3 | 0 | 600.0 | 0 | 600.0 | A | ###.#
EP2_Circutor_TokPovprecje_III | REAL | IOD_EP2 | EP2:.Circutor.TokPovprecje_III | 0 | 600.0 | 0 | 600.0 | A | ###.#
EP2_ComSCADA | DIGITAL | IOD_EP2 | EP2:.ComSCADA
EP2_ComSCADA1 | DIGITAL | IOD_EP2 | EP2:.ComSCADA1
EP2_DateTime_Dan | BYTE | IOD_EP2 | EP2:.DateTime.Dan
EP2_DateTime_Leto | BYTE | IOD_EP2 | EP2:.DateTime.Leto
EP2_DateTime_Mesec | BYTE | IOD_EP2 | EP2:.DateTime.Mesec
EP2_DateTime_Minuta | BYTE | IOD_EP2 | EP2:.DateTime.Minuta
EP2_DateTime_Sekunda | BYTE | IOD_EP2 | EP2:.DateTime.Sekunda
EP2_DateTime_Ura | BYTE | IOD_EP2 | EP2:.DateTime.Ura
EP2_DI_Klima5_ERR | DIGITAL | IOD_EP2 | EP2:.DI_Klima5_ERR
EP2_DI_Klima5_ON | DIGITAL | IOD_EP2 | EP2:.DI_Klima5_ON
EP2_DI_Klima6_ERR | DIGITAL | IOD_EP2 | EP2:.DI_Klima6_ERR
EP2_DI_Klima6_ON | DIGITAL | IOD_EP2 | EP2:.DI_Klima6_ON
EP2_DI_KlimaSplit1_ERR | DIGITAL | IOD_EP2 | EP2:.DI_KlimaSplit1_ERR
EP2_DI_KlimaSplit1_ON | DIGITAL | IOD_EP2 | EP2:.DI_KlimaSplit1_ON
EP2_DI_Q10_OdcKlima6_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q10_OdcKlima6_IZP
EP2_DI_Q10_OdcKlima6_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q10_OdcKlima6_ON
EP2_DI_Q11_OdcVent1_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q11_OdcVent1_ON
EP2_DI_Q12_Rezerva_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q12_Rezerva_ON
EP2_DI_Q1_GlavnoStikalo_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q1_GlavnoStikalo_ON
EP2_DI_Q25_OdcUpsA_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q25_OdcUpsA_IZP
EP2_DI_Q25_OdcUpsA_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q25_OdcUpsA_ON
EP2_DI_Q26_OdcByA_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q26_OdcByA_IZP
EP2_DI_Q26_OdcByA_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q26_OdcByA_ON
EP2_DI_Q27_OdcByUpsA_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q27_OdcByUpsA_IZP
EP2_DI_Q27_OdcByUpsA_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q27_OdcByUpsA_ON
EP2_DI_Q28_OdcUpsB_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q28_OdcUpsB_IZP
EP2_DI_Q28_OdcUpsB_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q28_OdcUpsB_ON
EP2_DI_Q29_OdcByB_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q29_OdcByB_IZP
EP2_DI_Q29_OdcByB_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q29_OdcByB_ON
EP2_DI_Q2_Rezerva_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q2_Rezerva_IZP
EP2_DI_Q2_Rezerva_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q2_Rezerva_ON
EP2_DI_Q30_OdcByUpsB_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q30_OdcByUpsB_IZP
EP2_DI_Q30_OdcByUpsB_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q30_OdcByUpsB_ON
EP2_DI_Q31_DovByUpsA_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q31_DovByUpsA_ON
EP2_DI_Q32_DovByA_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q32_DovByA_ON
EP2_DI_Q33_DovByUpsB_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q33_DovByUpsB_ON
EP2_DI_Q34_DovByB_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q34_DovByB_ON
EP2_DI_Q5_OdcKlima1_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q5_OdcKlima1_IZP
EP2_DI_Q5_OdcKlima1_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q5_OdcKlima1_ON
EP2_DI_Q6_OdcKlima2_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q6_OdcKlima2_IZP
EP2_DI_Q6_OdcKlima2_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q6_OdcKlima2_ON
EP2_DI_Q7_OdcKlima3_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q7_OdcKlima3_IZP
EP2_DI_Q7_OdcKlima3_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q7_OdcKlima3_ON
EP2_DI_Q8_OdcKlima4_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q8_OdcKlima4_IZP
EP2_DI_Q8_OdcKlima4_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q8_OdcKlima4_ON
EP2_DI_Q9_OdcKlima5_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q9_OdcKlima5_IZP
EP2_DI_Q9_OdcKlima5_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q9_OdcKlima5_ON
EP2_DI_RazlitjeVodeK5K6 | DIGITAL | IOD_EP2 | EP2:.DI_RazlitjeVodeK5K6
EP2_DI_UPS_Alarm | DIGITAL | IOD_EP2 | EP2:.DI_UPS_Alarm
EP2_DI_UPS_BatNacin | DIGITAL | IOD_EP2 | EP2:.DI_UPS_BatNacin
EP2_DI_UPS_Polnjenje | DIGITAL | IOD_EP2 | EP2:.DI_UPS_Polnjenje
EP2_DI_UpsA_ERR | DIGITAL | IOD_EP2 | EP2:.DIN_UpsA_ERR
EP2_DI_UpsA_ON | DIGITAL | IOD_EP2 | EP2:.DIN_UpsA_BypassON
EP2_DI_UpsB_ERR | DIGITAL | IOD_EP2 | EP2:.DIN_UpsB_ERR
EP2_DI_UpsB_ON | DIGITAL | IOD_EP2 | EP2:.DIN_UpsB_BypassON
EP2_DO_Klima5_Izklop | DIGITAL | IOD_EP2 | EP2:.DO_Klima5_Izklop
EP2_DO_Klima6_Izklop | DIGITAL | IOD_EP2 | EP2:.DO_Klima6_Izklop
EP2_ErrComCirc1 | DIGITAL | IOD_EP2 | EP2:.ErrComCirc[1]
EP2_ErrComCirc2 | DIGITAL | IOD_EP2 | EP2:.ErrComCirc[2]
EP2_ErrComCirc3 | DIGITAL | IOD_EP2 | EP2:.ErrComCirc[3]
EP2_ErrComCirc4 | DIGITAL | IOD_EP2 | EP2:.ErrComCirc[4]
EP2_ErrComCirc5 | DIGITAL | IOD_EP2 | EP2:.ErrComCirc[5]
EP2_ErrComKlima1 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[1]
EP2_ErrComKlima2 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[2]
EP2_ErrComKlima3 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[3]
EP2_ErrComKlima4 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[4]
EP2_ErrComKlima5 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[5]
EP2_ErrComKlima6 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[6]
EP2_ErrCommScada | DIGITAL | IOD_EP2 | EP2:.ErrCommScada
EP2_ErrComPanelPLC | DIGITAL | IOD_EP2 | EP2:.ErrComPanelPLC
EP2_ErrComPMM1 | DIGITAL | IOD_EP2 | EP2:.ErrComPMM[1]
EP2_ErrComPMM2 | DIGITAL | IOD_EP2 | EP2:.ErrComPMM[2]
EP2_ErrComPMM3 | DIGITAL | IOD_EP2 | EP2:.ErrComPMM[3]
EP2_ErrComPort2 | DIGITAL | IOD_EP2 | EP2:.ErrComPort2
EP2_ErrComPort3 | DIGITAL | IOD_EP2 | EP2:.ErrComPort3
EP2_ErrComPort4 | DIGITAL | IOD_EP2 | EP2:.ErrComPort4
EP2_ErrComUPS1 | DIGITAL | IOD_EP2 | EP2:.ErrComUPS[1]
EP2_ErrComUPS2 | DIGITAL | IOD_EP2 | EP2:.ErrComUPS[2]
EP2_Klima1_AlarmKompresor1 | DIGITAL | IOD_EP2 | EP2:.Klima[1].AlarmKompresor1
EP2_Klima1_AlarmKompresor2 | DIGITAL | IOD_EP2 | EP2:.Klima[1].AlarmKompresor2
EP2_Klima1_Deluje | DIGITAL | IOD_EP2 | EP2:.Klima[1].Deluje
EP2_Klima1_EnergySaving | DIGITAL | IOD_EP2 | EP2:.Klima[1].EnergySaving
EP2_Klima1_FaultyEPROM | DIGITAL | IOD_EP2 | EP2:.Klima[1].FaultyEPROM
EP2_Klima1_FenThermalCutout | DIGITAL | IOD_EP2 | EP2:.Klima[1].FenThermalCutout
EP2_Klima1_GeneralAlarm | DIGITAL | IOD_EP2 | EP2:.Klima[1].GeneralAlarm
EP2_Klima1_GrelecStatus | BYTE | IOD_EP2 | EP2:.Klima[1].GrelecStatus
EP2_Klima1_IzhodniVentStatus | BYTE | IOD_EP2 | EP2:.Klima[1].IzhodniVentStatus
EP2_Klima1_Kompresor1naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[1].Kompresor1naMejiObrUr
EP2_Klima1_Kompresor2naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[1].Kompresor2naMejiObrUr
EP2_Klima1_KompresorStatus | BYTE | IOD_EP2 | EP2:.Klima[1].KompresorStatus
EP2_Klima1_Napaka | DIGITAL | IOD_EP2 | EP2:.Klima[1].Napaka
EP2_Klima1_NapakaPriPretokuZraka | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaPriPretokuZraka
EP2_Klima1_NapakaSenzorPovratVod | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaSenzorPovratVode
EP2_Klima1_NapakaSenzorTempIzpih | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaSenzorTempIzpiha
EP2_Klima1_NapakaSenzorTempProst | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaSenzorTempProstora
EP2_Klima1_NapakaSenzorVlaznosti | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaSenzorVlaznosti
EP2_Klima1_NapakaSenzorZunanjeTemp | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaSenzorZunanjeTemp
EP2_Klima1_NastMaxTemp | REAL | IOD_EP2 | EP2:.Klima[1].NastMaxTemp | 0 | 60.0 | 0 | 60.0 | °C | ##.#
EP2_Klima1_NastMaxVlaznost | REAL | IOD_EP2 | EP2:.Klima[1].NastMaxVlaznost | 0 | 100 | 0 | 100 | % | ##.#
EP2_Klima1_NastMinTemp | REAL | IOD_EP2 | EP2:.Klima[1].NastMinTemp | 0 | 60.0 | 0 | 60.0 | °C | ##.#
EP2_Klima1_NastMinVlaznost | REAL | IOD_EP2 | EP2:.Klima[1].NastMinVlaznost | 0 | 100 | 0 | 100 | % | ##.#
EP2_Klima1_NastTempProstora | REAL | IOD_EP2 | EP2:.Klima[1].NastTempProstora | 0 | 60.0 | 0 | 60.0 | °C | ##.#
EP2_Klima1_NastVlaznost | REAL | IOD_EP2 | EP2:.Klima[1].NastVlaznost | 0 | 100 | 0 | 100 | % | ##.#
EP2_Klima1_NiTokaVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[1].NiTokaVVlazilcu
EP2_Klima1_NiVodeVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[1].NiVodeVVlazilcu
EP2_Klima1_NizekPritiskKompresor1 | DIGITAL | IOD_EP2 | EP2:.Klima[1].NizekPritiskKompresor1
EP2_Klima1_NizekPritiskKompresor2 | DIGITAL | IOD_EP2 | EP2:.Klima[1].NizekPritiskKompresor2
EP2_Klima1_NizkaTempPovratneVode | DIGITAL | IOD_EP2 | EP2:.Klima[1].NizkaTempPovratneVode
EP2_Klima1_NizkaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.Klima[1].NizkaTempVProstoru
EP2_Klima1_NizkaVlaznost | DIGITAL | IOD_EP2 | EP2:.Klima[1].NizkaVlaznost
EP2_Klima1_ObratovalneUre | REAL | IOD_EP2 | EP2:.Klima[1].ObratovalneUre
EP2_Klima1_OnOffEnablingBySupervisor | DIGITAL | IOD_EP2 | EP2:.Klima[1].OnOffEnablingBySupervisor
EP2_Klima1_PozarniAlarm | DIGITAL | IOD_EP2 | EP2:.Klima[1].PozarniAlarm
EP2_Klima1_Razvlazevanje | DIGITAL | IOD_EP2 | EP2:.Klima[1].Razvlazevanje
EP2_Klima1_RemoteOFFtoOutput | DIGITAL | IOD_EP2 | EP2:.Klima[1].RemoteOFFtoOutput
EP2_Klima1_RemoteOnOff | DIGITAL | IOD_EP2 | EP2:.Klima[1].RemoteOnOff
EP2_Klima1_RocniIzklop | DIGITAL | IOD_EP2 | EP2:.Klima[1].RocniIzklop
EP2_Klima1_SenzorjiStatus | DIGITAL | IOD_EP2 | EP2:.Klima[1].SenzorjiStatus
EP2_Klima1_StoppedByAlarms | DIGITAL | IOD_EP2 | EP2:.Klima[1].StoppedByAlarms
EP2_Klima1_TemperaturaProstora | REAL | IOD_EP2 | EP2:.Klima[1].TemperaturaProstora | 0 | 60.0 | 0 | 60.0 | °C | ##.#
EP2_Klima1_TempIzpihanegaZraka | REAL | IOD_EP2 | EP2:.Klima[1].TempIzpihanegaZraka | 0 | 60.0 | 0 | 60.0 | °C | ##.#
EP2_Klima1_TempPovratneVode | REAL | IOD_EP2 | EP2:.Klima[1].TempPovratneVode | 0 | 60.0 | 0 | 60.0 | °C | ##.#
EP2_Klima1_ThermalCutoutHeater1 | DIGITAL | IOD_EP2 | EP2:.Klima[1].ThermalCutoutHeater1
EP2_Klima1_ThermalCutoutHeater2 | DIGITAL | IOD_EP2 | EP2:.Klima[1].ThermalCutoutHeater2
EP2_Klima1_UnitOnOff | DIGITAL | IOD_EP2 | EP2:.Klima[1].UnitOnOff
EP2_Klima1_VentilatorNaMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[1].VentilatorNaMejiObrUr
EP2_Klima1_VentilGretjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.Klima[1].VentilGretjeOdpiranje
EP2_Klima1_VentilGretjeZapiranje | DIGITAL | IOD_EP2 | EP2:.Klima[1].VentilGretjeZapiranje
EP2_Klima1_VentilHlajenjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.Klima[1].VentilHlajenjeOdpiranje
EP2_Klima1_VentilHlajenjeZapiranje | DIGITAL | IOD_EP2 | EP2:.Klima[1].VentilHlajenjeZapiranje
EP2_Klima1_VisokaTempPovratneVode | DIGITAL | IOD_EP2 | EP2:.Klima[1].VisokaTempPovratneVode
EP2_Klima1_VisokaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.Klima[1].VisokaTempVProstoru
EP2_Klima1_VisokaVlaznost | DIGITAL | IOD_EP2 | EP2:.Klima[1].VisokaVlaznost
EP2_Klima1_VisokTokVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[1].VisokTokVVlazilcu
EP2_Klima1_Vlazenje | DIGITAL | IOD_EP2 | EP2:.Klima[1].Vlazenje
EP2_Klima1_VlazilecStatus | BYTE | IOD_EP2 | EP2:.Klima[1].VlazilecStatus
EP2_Klima1_VlaznostProstora | REAL | IOD_EP2 | EP2:.Klima[1].VlaznostProstora | 0 | 100 | 0 | 100 | % | ##.#
EP2_Klima1_ZamasenFilter | DIGITAL | IOD_EP2 | EP2:.Klima[1].ZamasenFilter
EP2_Klima1_ZunanjaTemp | REAL | IOD_EP2 | EP2:.Klima[1].ZunanjaTemp
EP2_Klima2_AlarmKompresor1 | DIGITAL | IOD_EP2 | EP2:.Klima[2].AlarmKompresor1
EP2_Klima2_AlarmKompresor2 | DIGITAL | IOD_EP2 | EP2:.Klima[2].AlarmKompresor2
EP2_Klima2_Deluje | DIGITAL | IOD_EP2 | EP2:.Klima[2].Deluje
EP2_Klima2_EnergySaving | DIGITAL | IOD_EP2 | EP2:.Klima[2].EnergySaving
EP2_Klima2_FaultyEPROM | DIGITAL | IOD_EP2 | EP2:.Klima[2].FaultyEPROM
EP2_Klima2_FenThermalCutout | DIGITAL | IOD_EP2 | EP2:.Klima[2].FenThermalCutout
EP2_Klima2_GeneralAlarm | DIGITAL | IOD_EP2 | EP2:.Klima[2].GeneralAlarm
EP2_Klima2_GrelecStatus | BYTE | IOD_EP2 | EP2:.Klima[2].GrelecStatus
EP2_Klima2_IzhodniVentStatus | BYTE | IOD_EP2 | EP2:.Klima[2].IzhodniVentStatus
EP2_Klima2_Kompresor1naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[2].Kompresor1naMejiObrUr
EP2_Klima2_Kompresor2naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[2].Kompresor2naMejiObrUr
EP2_Klima2_KompresorStatus | BYTE | IOD_EP2 | EP2:.Klima[2].KompresorStatus
EP2_Klima2_Napaka | DIGITAL | IOD_EP2 | EP2:.Klima[2].Napaka
EP2_Klima2_NapakaPriPretokuZraka | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaPriPretokuZraka
EP2_Klima2_NapakaSenzorPovratVode | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaSenzorPovratVode
EP2_Klima2_NapakaSenzorTempIzpih | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaSenzorTempIzpiha
EP2_Klima2_NapakaSenzorTempProst | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaSenzorTempProstora
EP2_Klima2_NapakaSenzorVlaznosti | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaSenzorVlaznosti
EP2_Klima2_NapakaSenzorZunanjeTemp | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaSenzorZunanjeTemp
EP2_Klima2_NastMaxTemp | REAL | IOD_EP2 | EP2:.Klima[2].NastMaxTemp | 0 | 60.0 | 0 | 60.0 | °C | ##.#
EP2_Klima2_NastMaxVlaznost | REAL | IOD_EP2 | EP2:.Klima[2].NastMaxVlaznost | 0 | 100 | 0 | 100 | % | ##.#
EP2_Klima2_NastMinTemp | REAL | IOD_EP2 | EP2:.Klima[2].NastMinTemp | 0 | 60.0 | 0 | 60.0 | °C | ##.#
EP2_Klima2_NastMinVlaznost | REAL | IOD_EP2 | EP2:.Klima[2].NastMinVlaznost | 0 | 100 | 0 | 100 | % | ##.#
EP2_Klima2_NastTempProstora | REAL | IOD_EP2 | EP2:.Klima[2].NastTempProstora | 0 | 60.0 | 0 | 60.0 | °C | ##.#
EP2_Klima2_NastVlaznost | REAL | IOD_EP2 | EP2:.Klima[2].NastVlaznost | 0 | 100 | 0 | 100 | % | ##.#
EP2_Klima2_NiTokaVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[2].NiTokaVVlazilcu
EP2_Klima2_NiVodeVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[2].NiVodeVVlazilcu
EP2_Klima2_NizekPritiskKompresor1 | DIGITAL | IOD_EP2 | EP2:.Klima[2].NizekPritiskKompresor1
EP2_Klima2_NizekPritiskKompresor2 | DIGITAL | IOD_EP2 | EP2:.Klima[2].NizekPritiskKompresor2
EP2_Klima2_NizkaTempPovratneVode | DIGITAL | IOD_EP2 | EP2:.Klima[2].NizkaTempPovratneVode
EP2_Klima2_NizkaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.Klima[2].NizkaTempVProstoru
EP2_Klima2_NizkaVlaznost | DIGITAL | IOD_EP2 | EP2:.Klima[2].NizkaVlaznost
EP2_Klima2_ObratovalneUre | REAL | IOD_EP2 | EP2:.Klima[2].ObratovalneUre
EP2_Klima2_OnOffEnablingBySupervisor | DIGITAL | IOD_EP2 | EP2:.Klima[2].OnOffEnablingBySupervisor
EP2_Klima2_PozarniAlarm | DIGITAL | IOD_EP2 | EP2:.Klima[2].PozarniAlarm
EP2_Klima2_Razvlazevanje | DIGITAL | IOD_EP2 | EP2:.Klima[2].Razvlazevanje
EP2_Klima2_RemoteOFFtoOutput | DIGITAL | IOD_EP2 | EP2:.Klima[2].RemoteOFFtoOutput
EP2_Klima2_RemoteOnOff | DIGITAL | IOD_EP2 | EP2:.Klima[2].RemoteOnOff
EP2_Klima2_RocniIzklop | DIGITAL | IOD_EP2 | EP2:.Klima[2].RocniIzklop
EP2_Klima2_SenzorjiStatus | DIGITAL | IOD_EP2 | EP2:.Klima[2].SenzorjiStatus
EP2_Klima2_StoppedByAlarms | DIGITAL | IOD_EP2 | EP2:.Klima[2].StoppedByAlarms
EP2_Klima2_TemperaturaProstora | REAL | IOD_EP2 | EP2:.Klima[2].TemperaturaProstora | 0 | 60.0 | 0 | 60.0 | °C | ##.#
EP2_Klima2_TempIzpihanegaZraka | REAL | IOD_EP2 | EP2:.Klima[2].TempIzpihanegaZraka | 0 | 60.0 | 0 | 60.0 | °C | ##.#
EP2_Klima2_TempPovratneVode | REAL | IOD_EP2 | EP2:.Klima[2].TempPovratneVode | 0 | 60.0 | 0 | 60.0 | °C | ##.#
EP2_Klima2_ThermalCutoutHeater1 | DIGITAL | IOD_EP2 | EP2:.Klima[2].ThermalCutoutHeater1
EP2_Klima2_ThermalCutoutHeater2 | DIGITAL | IOD_EP2 | EP2:.Klima[2].ThermalCutoutHeater2
EP2_Klima2_UnitOnOff | DIGITAL | IOD_EP2 | EP2:.Klima[2].UnitOnOff
EP2_Klima2_VentilatorNaMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[2].VentilatorNaMejiObrUr
EP2_Klima2_VentilGretjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.Klima[2].VentilGretjeOdpiranje
EP2_Klima2_VentilGretjeZapiranje | DIGITAL | IOD_EP2 | EP2:.Klima[2].VentilGretjeZapiranje
EP2_Klima2_VentilHlajenjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.Klima[2].VentilHlajenjeOdpiranje
EP2_Klima2_VentilHlajenjeZapiranje | DIGITAL | IOD_EP2 | EP2:.Klima[2].VentilHlajenjeZapiranje
EP2_Klima2_VisokaTempPovratneVod | DIGITAL | IOD_EP2 | EP2:.Klima[2].VisokaTempPovratneVode
EP2_Klima2_VisokaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.Klima[2].VisokaTempVProstoru
EP2_Klima2_VisokaVlaznost | DIGITAL | IOD_EP2 | EP2:.Klima[2].VisokaVlaznost
EP2_Klima2_VisokTokVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[2].VisokTokVVlazilcu
EP2_Klima2_Vlazenje | DIGITAL | IOD_EP2 | EP2:.Klima[2].Vlazenje
EP2_Klima2_VlazilecStatus | BYTE | IOD_EP2 | EP2:.Klima[2].VlazilecStatus
EP2_Klima2_VlaznostProstora | REAL | IOD_EP2 | EP2:.Klima[2].VlaznostProstora | 0 | 100 | 0 | 100 | % | ##.#
EP2_Klima2_ZamasenFilter | DIGITAL | IOD_EP2 | EP2:.Klima[2].ZamasenFilter
EP2_Klima2_ZunanjaTemp | REAL | IOD_EP2 | EP2:.Klima[2].ZunanjaTemp
EP2_KlimeNaCas | DIGITAL | IOD_EP2 | EP2:.KlimeNaCas
EP2_NapakaSenzorTemp1 | DIGITAL | IOD_EP2 | EP2:.NapakaSenzorTemp[1]
EP2_NapakaSenzorTemp2 | DIGITAL | IOD_EP2 | EP2:.NapakaSenzorTemp[2]
EP2_NapakaSenzorVlaga1 | DIGITAL | IOD_EP2 | EP2:.NapakaSenzorVlaga[1]
EP2_NapakaSenzorVlaga2 | DIGITAL | IOD_EP2 | EP2:.NapakaSenzorVlaga[2]
EP2_PMM1OverCurrentBetw1 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentBetw[1]
EP2_PMM1OverCurrentBetw2 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentBetw[2]
EP2_PMM1OverCurrentBetw3 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentBetw[3]
EP2_PMM1OverCurrentOver1 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentOver[1]
EP2_PMM1OverCurrentOver2 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentOver[2]
EP2_PMM1OverCurrentOver3 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentOver[3]
EP2_PMM2OverCurrentBetw1 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentBetw[1]
EP2_PMM2OverCurrentBetw2 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentBetw[2]
EP2_PMM2OverCurrentBetw3 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentBetw[3]
EP2_PMM2OverCurrentOver1 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentOver[1]
EP2_PMM2OverCurrentOver2 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentOver[2]
EP2_PMM2OverCurrentOver3 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentOver[3]
EP2_PMM3OverCurrentBetw1 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentBetw[1]
EP2_PMM3OverCurrentBetw2 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentBetw[2]
EP2_PMM3OverCurrentBetw3 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentBetw[3]
EP2_PMM3OverCurrentOver1 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentOver[1]
EP2_PMM3OverCurrentOver2 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentOver[2]
EP2_PMM3OverCurrentOver3 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentOver[3]
EP2_PMM1_ActivePowerPhaseA_kW | REAL | IOD_EP2 | EP2:.PMM[1].ActivePowerPhaseA_kW | [5 empty] | ###.#
EP2_PMM1_ActivePowerPhaseB_kW | REAL | IOD_EP2 | EP2:.PMM[1].ActivePowerPhaseB_kW | [5 empty] | ###.#
EP2_PMM1_ActivePowerPhaseC_kW | REAL | IOD_EP2 | EP2:.PMM[1].ActivePowerPhaseC_kW | [5 empty] | ###.#
EP2_PMM1_AlarmPhase1_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C01_16_60to80
EP2_PMM1_AlarmPhase1_C01_16_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C01_16_over80
EP2_PMM1_AlarmPhase1_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C17_32_60to80
EP2_PMM1_AlarmPhase1_C17_32_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C17_32_over80
EP2_PMM1_AlarmPhase1_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C33_42_60to80
EP2_PMM1_AlarmPhase1_C33_42_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C33_42_over80
EP2_PMM1_AlarmPhase1_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].GlobalAlarmReg
EP2_PMM1_AlarmPhase2_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C01_16_60to80
EP2_PMM1_AlarmPhase2_C01_16_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C01_16_over80
EP2_PMM1_AlarmPhase2_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C17_32_60to80
EP2_PMM1_AlarmPhase2_C17_32_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C17_32_over80
EP2_PMM1_AlarmPhase2_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C33_42_60to80
EP2_PMM1_AlarmPhase2_C33_42_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C33_42_over80
EP2_PMM1_AlarmPhase2_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].GlobalAlarmReg
EP2_PMM1_AlarmPhase3_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C01_16_60to80
EP2_PMM1_AlarmPhase3_C01_16_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C01_16_over80
EP2_PMM1_AlarmPhase3_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C17_32_60to80
EP2_PMM1_AlarmPhase3_C17_32_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C17_32_over80
EP2_PMM1_AlarmPhase3_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C33_42_60to80
EP2_PMM1_AlarmPhase3_C33_42_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C33_42_over80
EP2_PMM1_AlarmPhase3_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].GlobalAlarmReg
EP2_PMM1_Alarms | INT | IOD_EP2 | EP2:.PMM[1].Alarms
EP2_PMM1_AverageCurrent_A | REAL | IOD_EP2 | EP2:.PMM[1].AverageCurrent_A | [5 empty] | ###.#
EP2_PMM1_AveragePhaseToNeutral_V | REAL | IOD_EP2 | EP2:.PMM[1].AveragePhaseToNeutral_V | [5 empty] | ###.#
EP2_PMM1_AveragePhaseToPhase_V | REAL | IOD_EP2 | EP2:.PMM[1].AveragePhaseToPhase_V | [5 empty] | ###.#
EP2_PMM1_CurrentInPhaseA_A | REAL | IOD_EP2 | EP2:.PMM[1].CurrentInPhaseA_A | [5 empty] | ###.#
EP2_PMM1_CurrentInPhaseB_A | REAL | IOD_EP2 | EP2:.PMM[1].CurrentInPhaseB_A | [5 empty] | ###.#
EP2_PMM1_CurrentInPhaseC_A | REAL | IOD_EP2 | EP2:.PMM[1].CurrentInPhaseC_A | [5 empty] | ###.#
EP2_PMM1_EnergyConsumed_kWh | REAL | IOD_EP2 | EP2:.PMM[1].EnergyConsumed_kWh | [5 empty] | ###.#
EP2_PMM1_Napaka | DIGITAL | IOD_EP2 | EP2:.PMM[1].Napaka
EP2_PMM1_Frequency_Hz | REAL | IOD_EP2 | EP2:.PMM[1].Frequency_Hz | [5 empty] | ###.#
EP2_PMM1_NeutralCurrent_A | REAL | IOD_EP2 | EP2:.PMM[1].NeutralCurrent_A | [5 empty] | ###.#
EP2_PMM1_Phase1_Current10 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[10] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current11 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[11] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current12 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[12] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current13 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[13] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current14 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[14] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current15 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[15] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current16 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[16] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current17 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[17] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current18 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[18] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current19 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[19] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current1 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[1] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current20 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[20] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current21 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[21] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current22 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[22] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current23 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[23] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current24 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[24] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current25 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[25] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current26 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[26] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current27 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[27] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current28 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[28] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current29 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[29] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current2 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[2] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current30 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[30] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current31 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[31] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current32 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[32] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current33 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[33] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current34 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[34] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current35 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[35] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current36 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[36] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current37 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[37] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current38 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[38] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current39 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[39] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current3 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[3] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current40 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[40] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current41 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[41] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current42 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[42] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current4 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[4] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current5 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[5] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current6 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[6] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current7 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[7] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current8 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[8] | [5 empty] | ###.#
EP2_PMM1_Phase1_Current9 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[9] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current10 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[10] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current11 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[11] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current12 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[12] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current13 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[13] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current14 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[14] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current15 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[15] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current16 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[16] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current17 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[17] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current18 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[18] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current19 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[19] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current1 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[1] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current20 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[20] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current21 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[21] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current22 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[22] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current23 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[23] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current24 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[24] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current25 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[25] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current26 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[26] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current27 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[27] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current28 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[28] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current29 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[29] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current2 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[2] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current30 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[30] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current31 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[31] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current32 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[32] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current33 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[33] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current34 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[34] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current35 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[35] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current36 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[36] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current37 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[37] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current38 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[38] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current39 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[39] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current3 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[3] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current40 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[40] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current41 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[41] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current42 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[42] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current4 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[4] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current5 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[5] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current6 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[6] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current7 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[7] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current8 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[8] | [5 empty] | ###.#
EP2_PMM1_Phase2_Current9 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[9] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current10 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[10] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current11 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[11] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current12 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[12] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current13 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[13] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current14 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[14] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current15 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[15] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current16 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[16] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current17 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[17] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current18 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[18] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current19 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[19] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current1 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[1] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current20 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[20] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current21 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[21] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current22 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[22] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current23 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[23] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current24 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[24] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current25 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[25] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current26 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[26] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current27 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[27] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current28 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[28] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current29 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[29] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current2 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[2] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current30 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[30] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current31 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[31] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current32 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[32] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current33 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[33] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current34 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[34] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current35 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[35] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current36 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[36] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current37 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[37] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current38 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[38] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current39 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[39] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current3 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[3] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current40 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[40] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current41 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[41] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current42 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[42] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current4 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[4] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current5 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[5] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current6 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[6] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current7 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[7] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current8 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[8] | [5 empty] | ###.#
EP2_PMM1_Phase3_Current9 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[9] | [5 empty] | ###.#
EP2_PMM1_PowerFactorPhaseA | REAL | IOD_EP2 | EP2:.PMM[1].PowerFactorPhaseA | [5 empty] | ###.#
EP2_PMM1_PowerFactorPhaseB | REAL | IOD_EP2 | EP2:.PMM[1].PowerFactorPhaseB | [5 empty] | ###.#
EP2_PMM1_PowerFactorPhaseC | REAL | IOD_EP2 | EP2:.PMM[1].PowerFactorPhaseC | [5 empty] | ###.#
EP2_PMM1_TotalActivePower_kW | REAL | IOD_EP2 | EP2:.PMM[1].TotalActivePower_kW | [5 empty] | ###.#
EP2_PMM1_TotalAparentPower_kVA | REAL | IOD_EP2 | EP2:.PMM[1].TotalAparentPower_kVA | [5 empty] | ###.#
EP2_PMM1_TotalPowerFactor | REAL | IOD_EP2 | EP2:.PMM[1].TotalPowerFactor | [5 empty] | ###.#
EP2_PMM1_TotalReactivePower_kVAR | REAL | IOD_EP2 | EP2:.PMM[1].TotalReactivePower_kVAR | [5 empty] | ###.#
EP2_PMM1_VoltageBetweenPhaseAB_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseAB_V | [5 empty] | ###.#
EP2_PMM1_VoltageBetweenPhaseAN_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseAN_V | [5 empty] | ###.#
EP2_PMM1_VoltageBetweenPhaseBC_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseBC_V | [5 empty] | ###.#
EP2_PMM1_VoltageBetweenPhaseBN_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseBN_V | [5 empty] | ###.#
EP2_PMM1_VoltageBetweenPhaseCA_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseCA_V | [5 empty] | ###.#
EP2_PMM1_VoltageBetweenPhaseCN_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseCN_V | [5 empty] | ###.#
EP2_PMM2_ActivePowerPhaseA_kW | REAL | IOD_EP2 | EP2:.PMM[2].ActivePowerPhaseA_kW | [5 empty] | ###.#
EP2_PMM2_ActivePowerPhaseB_kW | REAL | IOD_EP2 | EP2:.PMM[2].ActivePowerPhaseB_kW | [5 empty] | ###.#
EP2_PMM2_ActivePowerPhaseC_kW | REAL | IOD_EP2 | EP2:.PMM[2].ActivePowerPhaseC_kW | [5 empty] | ###.#
EP2_PMM2_AlarmPhase1_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C01_16_60to80
EP2_PMM2_AlarmPhase1_C01_16_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C01_16_over80
EP2_PMM2_AlarmPhase1_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C17_32_60to80
EP2_PMM2_AlarmPhase1_C17_32_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C17_32_over80
EP2_PMM2_AlarmPhase1_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C33_42_60to80
EP2_PMM2_AlarmPhase1_C33_42_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C33_42_over80
EP2_PMM2_AlarmPhase1_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].GlobalAlarmReg
EP2_PMM2_AlarmPhase2_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C01_16_60to80
EP2_PMM2_AlarmPhase2_C01_16_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C01_16_over80
EP2_PMM2_AlarmPhase2_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C17_32_60to80
EP2_PMM2_AlarmPhase2_C17_32_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C17_32_over80
EP2_PMM2_AlarmPhase2_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C33_42_60to80
EP2_PMM2_AlarmPhase2_C33_42_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C33_42_over80
EP2_PMM2_AlarmPhase2_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].GlobalAlarmReg
EP2_PMM2_AlarmPhase3_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C01_16_60to80
EP2_PMM2_AlarmPhase3_C01_16_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C01_16_over80
EP2_PMM2_AlarmPhase3_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C17_32_60to80
EP2_PMM2_AlarmPhase3_C17_32_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C17_32_over80
EP2_PMM2_AlarmPhase3_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C33_42_60to80
EP2_PMM2_AlarmPhase3_C33_42_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C33_42_over80
EP2_PMM2_AlarmPhase3_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].GlobalAlarmReg
EP2_PMM2_Alarms | INT | IOD_EP2 | EP2:.PMM[2].Alarms
EP2_PMM2_AverageCurrent_A | REAL | IOD_EP2 | EP2:.PMM[2].AverageCurrent_A | [5 empty] | ###.#
EP2_PMM2_AveragePhaseToNeutral_V | REAL | IOD_EP2 | EP2:.PMM[2].AveragePhaseToNeutral_V | [5 empty] | ###.#
EP2_PMM2_AveragePhaseToPhase_V | REAL | IOD_EP2 | EP2:.PMM[2].AveragePhaseToPhase_V | [5 empty] | ###.#
EP2_PMM2_CurrentInPhaseA_A | REAL | IOD_EP2 | EP2:.PMM[2].CurrentInPhaseA_A | [5 empty] | ###.#
EP2_PMM2_CurrentInPhaseB_A | REAL | IOD_EP2 | EP2:.PMM[2].CurrentInPhaseB_A | [5 empty] | ###.#
EP2_PMM2_CurrentInPhaseC_A | REAL | IOD_EP2 | EP2:.PMM[2].CurrentInPhaseC_A | [5 empty] | ###.#
EP2_PMM2_EnergyConsumed_kWh | REAL | IOD_EP2 | EP2:.PMM[2].EnergyConsumed_kWh | [5 empty] | ###.#
EP2_PMM2_Frequency_Hz | REAL | IOD_EP2 | EP2:.PMM[2].Frequency_Hz | [5 empty] | ###.#
EP2_PMM2_Napaka | DIGITAL | IOD_EP2 | EP2:.PMM[2].Napaka
EP2_PMM2_NeutralCurrent_A | REAL | IOD_EP2 | EP2:.PMM[2].NeutralCurrent_A | [5 empty] | ###.#
EP2_PMM2_Phase1_Current10 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[10] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current11 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[11] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current12 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[12] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current13 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[13] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current14 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[14] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current15 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[15] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current16 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[16] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current17 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[17] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current18 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[18] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current19 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[19] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current1 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[1] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current20 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[20] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current21 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[21] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current22 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[22] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current23 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[23] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current24 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[24] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current25 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[25] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current26 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[26] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current27 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[27] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current28 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[28] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current29 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[29] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current2 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[2] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current30 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[30] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current31 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[31] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current32 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[32] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current33 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[33] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current34 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[34] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current35 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[35] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current36 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[36] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current37 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[37] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current38 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[38] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current39 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[39] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current3 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[3] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current40 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[40] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current41 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[41] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current42 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[42] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current4 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[4] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current5 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[5] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current6 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[6] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current7 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[7] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current8 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[8] | [5 empty] | ###.#
EP2_PMM2_Phase1_Current9 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[9] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current10 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[10] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current11 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[11] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current12 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[12] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current13 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[13] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current14 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[14] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current15 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[15] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current16 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[16] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current17 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[17] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current18 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[18] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current19 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[19] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current1 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[1] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current20 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[20] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current21 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[21] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current22 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[22] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current23 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[23] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current24 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[24] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current25 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[25] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current26 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[26] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current27 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[27] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current28 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[28] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current29 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[29] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current2 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[2] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current30 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[30] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current31 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[31] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current32 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[32] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current33 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[33] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current34 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[34] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current35 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[35] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current36 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[36] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current37 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[37] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current38 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[38] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current39 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[39] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current3 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[3] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current40 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[40] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current41 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[41] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current42 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[42] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current4 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[4] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current5 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[5] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current6 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[6] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current7 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[7] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current8 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[8] | [5 empty] | ###.#
EP2_PMM2_Phase2_Current9 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[9] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current10 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[10] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current11 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[11] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current12 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[12] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current13 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[13] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current14 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[14] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current15 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[15] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current16 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[16] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current17 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[17] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current18 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[18] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current19 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[19] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current1 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[1] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current20 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[20] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current21 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[21] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current22 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[22] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current23 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[23] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current24 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[24] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current25 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[25] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current26 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[26] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current27 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[27] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current28 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[28] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current29 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[29] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current2 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[2] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current30 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[30] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current31 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[31] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current32 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[32] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current33 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[33] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current34 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[34] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current35 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[35] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current36 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[36] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current37 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[37] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current38 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[38] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current39 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[39] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current3 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[3] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current40 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[40] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current41 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[41] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current42 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[42] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current4 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[4] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current5 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[5] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current6 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[6] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current7 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[7] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current8 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[8] | [5 empty] | ###.#
EP2_PMM2_Phase3_Current9 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[9] | [5 empty] | ###.#
EP2_PMM2_PowerFactorPhaseA | REAL | IOD_EP2 | EP2:.PMM[2].PowerFactorPhaseA | [5 empty] | ###.#
EP2_PMM2_PowerFactorPhaseB | REAL | IOD_EP2 | EP2:.PMM[2].PowerFactorPhaseB | [5 empty] | ###.#
EP2_PMM2_PowerFactorPhaseC | REAL | IOD_EP2 | EP2:.PMM[2].PowerFactorPhaseC | [5 empty] | ###.#
EP2_PMM2_TotalActivePower_kW | REAL | IOD_EP2 | EP2:.PMM[2].TotalActivePower_kW | [5 empty] | ###.#
EP2_PMM2_TotalAparentPower_kVA | REAL | IOD_EP2 | EP2:.PMM[2].TotalAparentPower_kVA | [5 empty] | ###.#
EP2_PMM2_TotalPowerFactor | REAL | IOD_EP2 | EP2:.PMM[2].TotalPowerFactor | [5 empty] | ###.#
EP2_PMM2_TotalReactivePower_kVAR | REAL | IOD_EP2 | EP2:.PMM[2].TotalReactivePower_kVAR | [5 empty] | ###.#
EP2_PMM2_VoltageBetweenPhaseAB_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseAB_V | [5 empty] | ###.#
EP2_PMM2_VoltageBetweenPhaseAN_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseAN_V | [5 empty] | ###.#
EP2_PMM2_VoltageBetweenPhaseBC_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseBC_V | [5 empty] | ###.#
EP2_PMM2_VoltageBetweenPhaseBN_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseBN_V | [5 empty] | ###.#
EP2_PMM2_VoltageBetweenPhaseCA_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseCA_V | [5 empty] | ###.#
EP2_PMM2_VoltageBetweenPhaseCN_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseCN_V | [5 empty] | ###.#
EP2_PMM3_ActivePowerPhaseA_kW | REAL | IOD_EP2 | EP2:.PMM[3].ActivePowerPhaseA_kW | [5 empty] | ###.#
EP2_PMM3_ActivePowerPhaseB_kW | REAL | IOD_EP2 | EP2:.PMM[3].ActivePowerPhaseB_kW | [5 empty] | ###.#
EP2_PMM3_ActivePowerPhaseC_kW | REAL | IOD_EP2 | EP2:.PMM[3].ActivePowerPhaseC_kW | [5 empty] | ###.#
EP2_PMM3_AlarmPhase1_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C01_16_60to80
EP2_PMM3_AlarmPhase1_C01_16_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C01_16_over80
EP2_PMM3_AlarmPhase1_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C17_32_60to80
EP2_PMM3_AlarmPhase1_C17_32_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C17_32_over80
EP2_PMM3_AlarmPhase1_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C33_42_60to80
EP2_PMM3_AlarmPhase1_C33_42_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C33_42_over80
EP2_PMM3_AlarmPhase1_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].GlobalAlarmReg
EP2_PMM3_AlarmPhase2_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C01_16_60to80
EP2_PMM3_AlarmPhase2_C01_16_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C01_16_over80
EP2_PMM3_AlarmPhase2_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C17_32_60to80
EP2_PMM3_AlarmPhase2_C17_32_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C17_32_over80
EP2_PMM3_AlarmPhase2_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C33_42_60to80
EP2_PMM3_AlarmPhase2_C33_42_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C33_42_over80
EP2_PMM3_AlarmPhase2_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].GlobalAlarmReg
EP2_PMM3_AlarmPhase3_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C01_16_60to80
EP2_PMM3_AlarmPhase3_C01_16_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C01_16_over80
EP2_PMM3_AlarmPhase3_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C17_32_60to80
EP2_PMM3_AlarmPhase3_C17_32_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C17_32_over80
EP2_PMM3_AlarmPhase3_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C33_42_60to80
EP2_PMM3_AlarmPhase3_C33_42_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C33_42_over80
EP2_PMM3_AlarmPhase3_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].GlobalAlarmReg
EP2_PMM3_Alarms | INT | IOD_EP2 | EP2:.PMM[3].Alarms
EP2_PMM3_AverageCurrent_A | REAL | IOD_EP2 | EP2:.PMM[3].AverageCurrent_A | [5 empty] | ###.#
EP2_PMM3_AveragePhaseToNeutral_V | REAL | IOD_EP2 | EP2:.PMM[3].AveragePhaseToNeutral_V | [5 empty] | ###.#
EP2_PMM3_AveragePhaseToPhase_V | REAL | IOD_EP2 | EP2:.PMM[3].AveragePhaseToPhase_V | [5 empty] | ###.#
EP2_PMM3_CurrentInPhaseA_A | REAL | IOD_EP2 | EP2:.PMM[3].CurrentInPhaseA_A | [5 empty] | ###.#
EP2_PMM3_CurrentInPhaseB_A | REAL | IOD_EP2 | EP2:.PMM[3].CurrentInPhaseB_A | [5 empty] | ###.#
EP2_PMM3_CurrentInPhaseC_A | REAL | IOD_EP2 | EP2:.PMM[3].CurrentInPhaseC_A | [5 empty] | ###.#
EP2_PMM3_EnergyConsumed_kWh | REAL | IOD_EP2 | EP2:.PMM[3].EnergyConsumed_kWh | [5 empty] | ###.#
EP2_PMM3_Frequency_Hz | REAL | IOD_EP2 | EP2:.PMM[3].Frequency_Hz | [5 empty] | ###.#
EP2_PMM3_Napaka | DIGITAL | IOD_EP2 | EP2:.PMM[3].Napaka
EP2_PMM3_NeutralCurrent_A | REAL | IOD_EP2 | EP2:.PMM[3].NeutralCurrent_A | [5 empty] | ###.#
EP2_PMM3_Phase1_Current10 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[10] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current11 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[11] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current12 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[12] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current13 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[13] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current14 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[14] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current15 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[15] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current16 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[16] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current17 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[17] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current18 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[18] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current19 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[19] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current1 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[1] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current20 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[20] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current21 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[21] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current22 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[22] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current23 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[23] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current24 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[24] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current25 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[25] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current26 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[26] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current27 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[27] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current28 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[28] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current29 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[29] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current2 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[2] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current30 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[30] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current31 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[31] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current32 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[32] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current33 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[33] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current34 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[34] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current35 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[35] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current36 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[36] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current37 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[37] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current38 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[38] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current39 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[39] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current3 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[3] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current40 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[40] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current41 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[41] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current42 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[42] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current4 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[4] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current5 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[5] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current6 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[6] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current7 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[7] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current8 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[8] | [5 empty] | ###.#
EP2_PMM3_Phase1_Current9 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[9] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current10 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[10] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current11 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[11] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current12 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[12] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current13 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[13] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current14 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[14] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current15 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[15] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current16 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[16] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current17 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[17] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current18 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[18] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current19 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[19] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current1 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[1] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current20 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[20] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current21 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[21] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current22 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[22] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current23 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[23] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current24 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[24] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current25 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[25] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current26 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[26] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current27 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[27] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current28 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[28] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current29 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[29] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current2 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[2] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current30 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[30] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current31 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[31] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current32 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[32] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current33 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[33] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current34 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[34] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current35 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[35] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current36 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[36] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current37 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[37] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current38 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[38] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current39 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[39] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current3 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[3] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current40 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[40] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current41 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[41] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current42 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[42] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current4 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[4] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current5 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[5] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current6 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[6] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current7 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[7] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current8 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[8] | [5 empty] | ###.#
EP2_PMM3_Phase2_Current9 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[9] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current10 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[10] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current11 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[11] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current12 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[12] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current13 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[13] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current14 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[14] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current15 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[15] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current16 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[16] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current17 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[17] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current18 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[18] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current19 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[19] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current1 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[1] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current20 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[20] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current21 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[21] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current22 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[22] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current23 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[23] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current24 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[24] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current25 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[25] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current26 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[26] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current27 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[27] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current28 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[28] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current29 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[29] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current2 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[2] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current30 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[30] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current31 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[31] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current32 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[32] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current33 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[33] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current34 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[34] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current35 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[35] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current36 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[36] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current37 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[37] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current38 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[38] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current39 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[39] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current3 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[3] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current40 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[40] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current41 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[41] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current42 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[42] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current4 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[4] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current5 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[5] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current6 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[6] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current7 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[7] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current8 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[8] | [5 empty] | ###.#
EP2_PMM3_Phase3_Current9 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[9] | [5 empty] | ###.#
EP2_PMM3_PowerFactorPhaseA | REAL | IOD_EP2 | EP2:.PMM[3].PowerFactorPhaseA | [5 empty] | ###.#
EP2_PMM3_PowerFactorPhaseB | REAL | IOD_EP2 | EP2:.PMM[3].PowerFactorPhaseB | [5 empty] | ###.#
EP2_PMM3_PowerFactorPhaseC | REAL | IOD_EP2 | EP2:.PMM[3].PowerFactorPhaseC | [5 empty] | ###.#
EP2_PMM3_TotalActivePower_kW | REAL | IOD_EP2 | EP2:.PMM[3].TotalActivePower_kW | [5 empty] | ###.#
EP2_PMM3_TotalAparentPower_kVA | REAL | IOD_EP2 | EP2:.PMM[3].TotalAparentPower_kVA | [5 empty] | ###.#
EP2_PMM3_TotalPowerFactor | REAL | IOD_EP2 | EP2:.PMM[3].TotalPowerFactor | [5 empty] | ###.#
EP2_PMM3_TotalReactivePower_kVAR | REAL | IOD_EP2 | EP2:.PMM[3].TotalReactivePower_kVAR | [5 empty] | ###.#
EP2_PMM3_VoltageBetweenPhaseAB_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseAB_V | [5 empty] | ###.#
EP2_PMM3_VoltageBetweenPhaseAN_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseAN_V | [5 empty] | ###.#
EP2_PMM3_VoltageBetweenPhaseBC_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseBC_V | [5 empty] | ###.#
EP2_PMM3_VoltageBetweenPhaseBN_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseBN_V | [5 empty] | ###.#
EP2_PMM3_VoltageBetweenPhaseCA_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseCA_V | [5 empty] | ###.#
EP2_PMM3_VoltageBetweenPhaseCN_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseCN_V | [5 empty] | ###.#
EP2_rVersion | REAL | IOD_EP2 | EP2:.rVersion
EP2_SenzorTemp1 | REAL | IOD_EP2 | EP2:.SenzorTemp[1] | 0 | 60.0 | 0 | 60.0 | °C | ##.#
EP2_SenzorTemp2 | REAL | IOD_EP2 | EP2:.SenzorTemp[2] | 0 | 60.0 | 0 | 60.0 | °C | ##.#
EP2_SenzorVlaga1 | REAL | IOD_EP2 | EP2:.SenzorVlaga[1] | 0 | 100 | 0 | 100 | % | ##.#
EP2_SenzorVlaga2 | REAL | IOD_EP2 | EP2:.SenzorVlaga[2] | 0 | 100 | 0 | 100 | % | ##.#
EP2_SetDateTime | DIGITAL | IOD_EP2 | EP2:.SetDateTime
EP2_SetDateTimeDemand | DIGITAL | IOD_EP2 | EP2:.SetDateTimeDemand
EP2_SetDateTimeError | DIGITAL | IOD_EP2 | EP2:.SetDateTimeError
EP2_SetDateTimeFinished | DIGITAL | IOD_EP2 | EP2:.SetDateTimeFinished
EP2_SetRemoteOnOff1 | DIGITAL | IOD_EP2 | EP2:.SetRemoteOnOff[1]
EP2_SetRemoteOnOff2 | DIGITAL | IOD_EP2 | EP2:.SetRemoteOnOff[2]
EP2_SlabaBaterijaPLC_A1 | DIGITAL | IOD_EP2 | EP2:.SlabaBaterijaPLC_A1
EP2_TempMaxPoint | REAL | IOD_EP2 | EP2:.TempMaxPoint | 0 | 60.0 | 0 | 60.0 | °C | ##.#
EP2_TempSetPoint | REAL | IOD_EP2 | EP2:.TempSetPoint | 0 | 60.0 | 0 | 60.0 | °C | ##.#
EP2_TempTSprevisoka1 | DIGITAL | IOD_EP2 | EP2:.TempTSprevisoka[1]
EP2_TempTSprevisoka2 | DIGITAL | IOD_EP2 | EP2:.TempTSprevisoka[2]
EP2UPS1AlarmAwaitingPower | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmAwaitingPower
EP2UPS1AlarmBypassBad | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmBypassBad
EP2UPS1AlarmChargerFailed | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmChargerFailed
EP2UPS1AlarmCommunicationsLost | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmCommunicationsLost
EP2UPS1AlarmDepletedBattery | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmDepletedBattery
EP2UPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmDiagnosticTestFailed
EP2UPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmIzhodOffKotZahtevano
EP2UPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmIzhodPreobremenjen
EP2UPS1AlarmLowBattery | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmLowBattery
EP2UPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmNapakaNaVarovalki
EP2UPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmNapakaNaVentilatorju
EP2UPS1AlarmOnBattery | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmOnBattery
EP2UPS1AlarmOnBypass | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmOnBypass
EP2UPS1AlarmInverterError | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmInverterError
EP2UPS1AlarmShutdownImminent | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmShutdownImminent
EP2UPS1AlarmShutdownPending | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmShutdownPending
EP2UPS1AlarmSlabaBaterija | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmSlabaBaterija
EP2UPS1AlarmSplosnaNapaka | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmSplosnaNapaka
EP2UPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmStanjeIzhodaIzvenToleranc
EP2UPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmStanjeVhodaIzvenToleranc
EP2UPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmTemperaturaIzvenToleranc
EP2UPS1AlarmTestInProgres | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmTestInProgres
EP2UPS1AlarmUPSIzhodOff | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmUPSIzhodOff
EP2UPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmUPSOffKotZahtevano
EP2UPS1AlarmUPSSystemOff | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmUPSSystemOff
EP2UPS1EstimatedChargeRemaining | REAL | IOD_EP2 | EP2:.UPS[1].EstimatedChargeRemaining | 0 | 100 | 0 | 100 | % | ###
EP2UPS1EstimatedMinutesRemaining | REAL | IOD_EP2 | EP2:.UPS[1].EstimatedMinutesRemaining | 0 | 500 | 0 | 500 | min | ###
EP2UPS1InverterStatus | INT | IOD_EP2 | EP2:.UPS[1].InverterStatus
EP2UPS1IzhodMocL1 | REAL | IOD_EP2 | EP2:.UPS[1].IzhodMocL1 | 0 | 100 | 0 | 100 | % | ##.#
EP2UPS1IzhodMocL2 | REAL | IOD_EP2 | EP2:.UPS[1].IzhodMocL2 | 0 | 100 | 0 | 100 | % | ##.#
EP2UPS1IzhodMocL3 | REAL | IOD_EP2 | EP2:.UPS[1].IzhodMocL3 | 0 | 100 | 0 | 100 | % | ##.#
EP2UPS1Napaka | DIGITAL | IOD_EP2 | EP2:.UPS[1].Napaka
EP2UPS1NapetostBaterije | REAL | IOD_EP2 | EP2:.UPS[1].NapetostBaterije | 0 | 500.0 | 0 | 500.0 | V | ###.#
EP2UPS1OutputStatus | INT | IOD_EP2 | EP2:.UPS[1].OutputStatus
EP2UPS1StatusBaterije | INT | IOD_EP2 | EP2:.UPS[1].StatusBaterije | [5 empty] | ##
EP2UPS1StatusEcomodeAktiven | DIGITAL | IOD_EP2 | EP2:.UPS[1].StatusEcomodeAktiven
EP2UPS1StatusInverterIsOn | DIGITAL | IOD_EP2 | EP2:.UPS[1].StatusInverterIsOn
EP2UPS1StatusStopOperation | DIGITAL | IOD_EP2 | EP2:.UPS[1].StatusStopOperation
EP2UPS1SteviloIzpadovVhodneLinije | INT | IOD_EP2 | EP2:.UPS[1].SteviloIzpadovVhodneLinije | [5 empty] | #####
EP2UPS1TemperaturaBaterije | REAL | IOD_EP2 | EP2:.UPS[1].TemperaturaBaterije | 0 | 100 | 0 | 100 | °C | ###
EP2UPS1UnitStatus | INT | IOD_EP2 | EP2:.UPS[1].UnitStatus
EP2UPS1VhodFrekvencaL1 | REAL | IOD_EP2 | EP2:.UPS[1].VhodFrekvencaL1 | 0 | 60.0 | 0 | 60.0 | Hz | ##.#
EP2UPS1VhodFrekvencaL2 | REAL | IOD_EP2 | EP2:.UPS[1].VhodFrekvencaL2 | 0 | 60.0 | 0 | 60.0 | Hz | ##.#
EP2UPS1VhodFrekvencaL3 | REAL | IOD_EP2 | EP2:.UPS[1].VhodFrekvencaL3 | 0 | 60.0 | 0 | 60.0 | Hz | ##.#
EP2UPS1VhodNapetostL1 | REAL | IOD_EP2 | EP2:.UPS[1].VhodNapetostL1 | 0 | 500.0 | 0 | 500.0 | V | ###.#
EP2UPS1VhodNapetostL2 | REAL | IOD_EP2 | EP2:.UPS[1].VhodNapetostL2 | 0 | 500.0 | 0 | 500.0 | V | ###.#
EP2UPS1VhodNapetostL3 | REAL | IOD_EP2 | EP2:.UPS[1].VhodNapetostL3 | 0 | 500.0 | 0 | 500.0 | V | ###.#
EP2UPS2AlarmAwaitingPower | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmAwaitingPower
EP2UPS2AlarmBypassBad | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmBypassBad
EP2UPS2AlarmChargerFailed | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmChargerFailed
EP2UPS2AlarmCommunicationsLost | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmCommunicationsLost
EP2UPS2AlarmDepletedBattery | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmDepletedBattery
EP2UPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmDiagnosticTestFailed
EP2UPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmIzhodOffKotZahtevano
EP2UPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmIzhodPreobremenjen
EP2UPS2AlarmLowBattery | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmLowBattery
EP2UPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmNapakaNaVarovalki
EP2UPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmNapakaNaVentilatorju
EP2UPS2AlarmOnBattery | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmOnBattery
EP2UPS2AlarmOnBypass | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmOnBypass
EP2UPS2AlarmInverterError | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmInverterError
EP2UPS2AlarmShutdownImminent | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmShutdownImminent
EP2UPS2AlarmShutdownPending | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmShutdownPending
EP2UPS2AlarmSlabaBaterija | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmSlabaBaterija
EP2UPS2AlarmSplosnaNapaka | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmSplosnaNapaka
EP2UPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmStanjeIzhodaIzvenToleranc
EP2UPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmStanjeVhodaIzvenToleranc
EP2UPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmTemperaturaIzvenToleranc
EP2UPS2AlarmTestInProgres | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmTestInProgres
EP2UPS2AlarmUPSIzhodOff | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmUPSIzhodOff
EP2UPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmUPSOffKotZahtevano
EP2UPS2AlarmUPSSystemOff | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmUPSSystemOff
EP2UPS2EstimatedChargeRemaining | REAL | IOD_EP2 | EP2:.UPS[2].EstimatedChargeRemaining | 0 | 100 | 0 | 100 | % | ###
EP2UPS2EstimatedMinutesRemaining | REAL | IOD_EP2 | EP2:.UPS[2].EstimatedMinutesRemaining | 0 | 500 | 0 | 500 | min | ###
EP2UPS2InverterStatus | INT | IOD_EP2 | EP2:.UPS[2].InverterStatus
EP2UPS2IzhodMocL1 | REAL | IOD_EP2 | EP2:.UPS[2].IzhodMocL1 | 0 | 100 | 0 | 100 | % | ##.#
EP2UPS2IzhodMocL2 | REAL | IOD_EP2 | EP2:.UPS[2].IzhodMocL2 | 0 | 100 | 0 | 100 | % | ##.#
EP2UPS2IzhodMocL3 | REAL | IOD_EP2 | EP2:.UPS[2].IzhodMocL3 | 0 | 100 | 0 | 100 | % | ##.#
EP2UPS2Napaka | DIGITAL | IOD_EP2 | EP2:.UPS[2].Napaka
EP2UPS2NapetostBaterije | REAL | IOD_EP2 | EP2:.UPS[2].NapetostBaterije | 0 | 500.0 | 0 | 500.0 | V | ###.#
EP2UPS2OutputStatus | INT | IOD_EP2 | EP2:.UPS[2].OutputStatus
EP2UPS2StatusBaterije | INT | IOD_EP2 | EP2:.UPS[2].StatusBaterije | [5 empty] | ##
EP2UPS2StatusEcomodeAktiven | DIGITAL | IOD_EP2 | EP2:.UPS[2].StatusEcomodeAktiven
EP2UPS2StatusInverterIsOn | DIGITAL | IOD_EP2 | EP2:.UPS[2].StatusInverterIsOn
EP2UPS2StatusStopOperation | DIGITAL | IOD_EP2 | EP2:.UPS[2].StatusStopOperation
EP2UPS2SteviloIzpadovVhodneLinije | INT | IOD_EP2 | EP2:.UPS[2].SteviloIzpadovVhodneLinije | [5 empty] | #####
EP2UPS2TemperaturaBaterije | REAL | IOD_EP2 | EP2:.UPS[2].TemperaturaBaterije | 0 | 100 | 0 | 100 | °C | ###
EP2UPS2UnitStatus | INT | IOD_EP2 | EP2:.UPS[2].UnitStatus
EP2UPS2VhodFrekvencaL1 | REAL | IOD_EP2 | EP2:.UPS[2].VhodFrekvencaL1 | 0 | 60.0 | 0 | 60.0 | Hz | ##.#
EP2UPS2VhodFrekvencaL2 | REAL | IOD_EP2 | EP2:.UPS[2].VhodFrekvencaL2 | 0 | 60.0 | 0 | 60.0 | Hz | ##.#
EP2UPS2VhodFrekvencaL3 | REAL | IOD_EP2 | EP2:.UPS[2].VhodFrekvencaL3 | 0 | 60.0 | 0 | 60.0 | Hz | ##.#
EP2UPS2VhodNapetostL1 | REAL | IOD_EP2 | EP2:.UPS[2].VhodNapetostL1 | 0 | 500.0 | 0 | 500.0 | V | ###.#
EP2UPS2VhodNapetostL2 | REAL | IOD_EP2 | EP2:.UPS[2].VhodNapetostL2 | 0 | 500.0 | 0 | 500.0 | V | ###.#
EP2UPS2VhodNapetostL3 | REAL | IOD_EP2 | EP2:.UPS[2].VhodNapetostL3 | 0 | 500.0 | 0 | 500.0 | V | ###.#
EP2_UserCurrentLevel | BYTE | IOD_EP2 | EP2:.UserCurrentLevel
EP2_UserCurrentName | STRING | IOD_EP2 | EP2:.UserCurrentName
EP2_UserLoggedIn | DIGITAL | IOD_EP2 | EP2:.UserLoggedIn
EP2_PMM_3_Faza1_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D1
EP2_PMM_3_Faza1_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D2
EP2_PMM_3_Faza1_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D3
EP2_PMM_3_Faza1_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D4
EP2_PMM_3_Faza1_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D5
EP2_PMM_3_Faza1_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D6
EP2_PMM_3_Faza1_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D7
EP2_PMM_3_Faza1_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D8
EP2_PMM_3_Faza1_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D9
EP2_PMM_3_Faza1_Tok10_nad80 | DIGITAL | IOD_EP2_disk | D10
EP2_PMM_3_Faza1_Tok11_nad80 | DIGITAL | IOD_EP2_disk | D11
EP2_PMM_3_Faza1_Tok12_nad80 | DIGITAL | IOD_EP2_disk | D12
EP2_PMM_3_Faza1_Tok13_nad80 | DIGITAL | IOD_EP2_disk | D13
EP2_PMM_3_Faza1_Tok14_nad80 | DIGITAL | IOD_EP2_disk | D14
EP2_PMM_3_Faza1_Tok15_nad80 | DIGITAL | IOD_EP2_disk | D15
EP2_PMM_3_Faza1_Tok16_nad80 | DIGITAL | IOD_EP2_disk | D16
EP2_PMM_3_Faza1_Tok17_nad80 | DIGITAL | IOD_EP2_disk | D17
EP2_PMM_3_Faza1_Tok18_nad80 | DIGITAL | IOD_EP2_disk | D18
EP2_PMM_3_Faza1_Tok19_nad80 | DIGITAL | IOD_EP2_disk | D19
EP2_PMM_3_Faza1_Tok20_nad80 | DIGITAL | IOD_EP2_disk | D20
EP2_PMM_3_Faza1_Tok21_nad80 | DIGITAL | IOD_EP2_disk | D21
EP2_PMM_3_Faza1_Tok22_nad80 | DIGITAL | IOD_EP2_disk | D22
EP2_PMM_3_Faza1_Tok23_nad80 | DIGITAL | IOD_EP2_disk | D23
EP2_PMM_3_Faza1_Tok24_nad80 | DIGITAL | IOD_EP2_disk | D24
EP2_PMM_3_Faza1_Tok25_nad80 | DIGITAL | IOD_EP2_disk | D25
EP2_PMM_3_Faza1_Tok26_nad80 | DIGITAL | IOD_EP2_disk | D26
EP2_PMM_3_Faza1_Tok27_nad80 | DIGITAL | IOD_EP2_disk | D27
EP2_PMM_3_Faza1_Tok28_nad80 | DIGITAL | IOD_EP2_disk | D28
EP2_PMM_3_Faza1_Tok29_nad80 | DIGITAL | IOD_EP2_disk | D29
EP2_PMM_3_Faza1_Tok30_nad80 | DIGITAL | IOD_EP2_disk | D30
EP2_PMM_3_Faza1_Tok31_nad80 | DIGITAL | IOD_EP2_disk | D31
EP2_PMM_3_Faza1_Tok32_nad80 | DIGITAL | IOD_EP2_disk | D32
EP2_PMM_3_Faza1_Tok33_nad80 | DIGITAL | IOD_EP2_disk | D33
EP2_PMM_3_Faza1_Tok34_nad80 | DIGITAL | IOD_EP2_disk | D34
EP2_PMM_3_Faza1_Tok35_nad80 | DIGITAL | IOD_EP2_disk | D35
EP2_PMM_3_Faza1_Tok36_nad80 | DIGITAL | IOD_EP2_disk | D36
EP2_PMM_3_Faza1_Tok37_nad80 | DIGITAL | IOD_EP2_disk | D37
EP2_PMM_3_Faza1_Tok38_nad80 | DIGITAL | IOD_EP2_disk | D38
EP2_PMM_3_Faza1_Tok39_nad80 | DIGITAL | IOD_EP2_disk | D39
EP2_PMM_3_Faza1_Tok40_nad80 | DIGITAL | IOD_EP2_disk | D40
EP2_PMM_3_Faza1_Tok41_nad80 | DIGITAL | IOD_EP2_disk | D41
EP2_PMM_3_Faza1_Tok42_nad80 | DIGITAL | IOD_EP2_disk | D42
EP2_PMM_3_Faza2_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D43
EP2_PMM_3_Faza2_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D44
EP2_PMM_3_Faza2_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D45
EP2_PMM_3_Faza2_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D46
EP2_PMM_3_Faza2_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D47
EP2_PMM_3_Faza2_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D48
EP2_PMM_3_Faza2_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D49
EP2_PMM_3_Faza2_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D50
EP2_PMM_3_Faza2_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D51
EP2_PMM_3_Faza2_Tok10_nad80 | DIGITAL | IOD_EP2_disk | D52
EP2_PMM_3_Faza2_Tok11_nad80 | DIGITAL | IOD_EP2_disk | D53
EP2_PMM_3_Faza2_Tok12_nad80 | DIGITAL | IOD_EP2_disk | D54
EP2_PMM_3_Faza2_Tok13_nad80 | DIGITAL | IOD_EP2_disk | D55
EP2_PMM_3_Faza2_Tok14_nad80 | DIGITAL | IOD_EP2_disk | D56
EP2_PMM_3_Faza2_Tok15_nad80 | DIGITAL | IOD_EP2_disk | D57
EP2_PMM_3_Faza2_Tok16_nad80 | DIGITAL | IOD_EP2_disk | D58
EP2_PMM_3_Faza2_Tok17_nad80 | DIGITAL | IOD_EP2_disk | D59
EP2_PMM_3_Faza2_Tok18_nad80 | DIGITAL | IOD_EP2_disk | D60
EP2_PMM_3_Faza2_Tok19_nad80 | DIGITAL | IOD_EP2_disk | D61
EP2_PMM_3_Faza2_Tok20_nad80 | DIGITAL | IOD_EP2_disk | D62
EP2_PMM_3_Faza2_Tok21_nad80 | DIGITAL | IOD_EP2_disk | D63
EP2_PMM_3_Faza2_Tok22_nad80 | DIGITAL | IOD_EP2_disk | D64
EP2_PMM_3_Faza2_Tok23_nad80 | DIGITAL | IOD_EP2_disk | D65
EP2_PMM_3_Faza2_Tok24_nad80 | DIGITAL | IOD_EP2_disk | D66
EP2_PMM_3_Faza2_Tok25_nad80 | DIGITAL | IOD_EP2_disk | D67
EP2_PMM_3_Faza2_Tok26_nad80 | DIGITAL | IOD_EP2_disk | D68
EP2_PMM_3_Faza2_Tok27_nad80 | DIGITAL | IOD_EP2_disk | D69
EP2_PMM_3_Faza2_Tok28_nad80 | DIGITAL | IOD_EP2_disk | D70
EP2_PMM_3_Faza2_Tok29_nad80 | DIGITAL | IOD_EP2_disk | D71
EP2_PMM_3_Faza2_Tok30_nad80 | DIGITAL | IOD_EP2_disk | D72
EP2_PMM_3_Faza2_Tok31_nad80 | DIGITAL | IOD_EP2_disk | D73
EP2_PMM_3_Faza2_Tok32_nad80 | DIGITAL | IOD_EP2_disk | D74
EP2_PMM_3_Faza2_Tok33_nad80 | DIGITAL | IOD_EP2_disk | D75
EP2_PMM_3_Faza2_Tok34_nad80 | DIGITAL | IOD_EP2_disk | D76
EP2_PMM_3_Faza2_Tok35_nad80 | DIGITAL | IOD_EP2_disk | D77
EP2_PMM_3_Faza2_Tok36_nad80 | DIGITAL | IOD_EP2_disk | D78
EP2_PMM_3_Faza2_Tok37_nad80 | DIGITAL | IOD_EP2_disk | D79
EP2_PMM_3_Faza2_Tok38_nad80 | DIGITAL | IOD_EP2_disk | D80
EP2_PMM_3_Faza2_Tok39_nad80 | DIGITAL | IOD_EP2_disk | D81
EP2_PMM_3_Faza2_Tok40_nad80 | DIGITAL | IOD_EP2_disk | D82
EP2_PMM_3_Faza2_Tok41_nad80 | DIGITAL | IOD_EP2_disk | D83
EP2_PMM_3_Faza2_Tok42_nad80 | DIGITAL | IOD_EP2_disk | D84
EP2_PMM_3_Faza3_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D85
EP2_PMM_3_Faza3_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D86
EP2_PMM_3_Faza3_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D87
EP2_PMM_3_Faza3_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D88
EP2_PMM_3_Faza3_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D89
EP2_PMM_3_Faza3_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D90
EP2_PMM_3_Faza3_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D91
EP2_PMM_3_Faza3_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D92
EP2_PMM_3_Faza3_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D93
EP2_PMM_3_Faza3_Tok10_nad80 | DIGITAL | IOD_EP2_disk | D94
EP2_PMM_3_Faza3_Tok11_nad80 | DIGITAL | IOD_EP2_disk | D95
EP2_PMM_3_Faza3_Tok12_nad80 | DIGITAL | IOD_EP2_disk | D96
EP2_PMM_3_Faza3_Tok13_nad80 | DIGITAL | IOD_EP2_disk | D97
EP2_PMM_3_Faza3_Tok14_nad80 | DIGITAL | IOD_EP2_disk | D98
EP2_PMM_3_Faza3_Tok15_nad80 | DIGITAL | IOD_EP2_disk | D99
EP2_PMM_3_Faza3_Tok16_nad80 | DIGITAL | IOD_EP2_disk | D100
EP2_PMM_3_Faza3_Tok17_nad80 | DIGITAL | IOD_EP2_disk | D101
EP2_PMM_3_Faza3_Tok18_nad80 | DIGITAL | IOD_EP2_disk | D102
EP2_PMM_3_Faza3_Tok19_nad80 | DIGITAL | IOD_EP2_disk | D103
EP2_PMM_3_Faza3_Tok20_nad80 | DIGITAL | IOD_EP2_disk | D104
EP2_PMM_3_Faza3_Tok21_nad80 | DIGITAL | IOD_EP2_disk | D105
EP2_PMM_3_Faza3_Tok22_nad80 | DIGITAL | IOD_EP2_disk | D106
EP2_PMM_3_Faza3_Tok23_nad80 | DIGITAL | IOD_EP2_disk | D107
EP2_PMM_3_Faza3_Tok24_nad80 | DIGITAL | IOD_EP2_disk | D108
EP2_PMM_3_Faza3_Tok25_nad80 | DIGITAL | IOD_EP2_disk | D109
EP2_PMM_3_Faza3_Tok26_nad80 | DIGITAL | IOD_EP2_disk | D110
EP2_PMM_3_Faza3_Tok27_nad80 | DIGITAL | IOD_EP2_disk | D111
EP2_PMM_3_Faza3_Tok28_nad80 | DIGITAL | IOD_EP2_disk | D112
EP2_PMM_3_Faza3_Tok29_nad80 | DIGITAL | IOD_EP2_disk | D113
EP2_PMM_3_Faza3_Tok30_nad80 | DIGITAL | IOD_EP2_disk | D114
EP2_PMM_3_Faza3_Tok31_nad80 | DIGITAL | IOD_EP2_disk | D115
EP2_PMM_3_Faza3_Tok32_nad80 | DIGITAL | IOD_EP2_disk | D116
EP2_PMM_3_Faza3_Tok33_nad80 | DIGITAL | IOD_EP2_disk | D117
EP2_PMM_3_Faza3_Tok34_nad80 | DIGITAL | IOD_EP2_disk | D118
EP2_PMM_3_Faza3_Tok35_nad80 | DIGITAL | IOD_EP2_disk | D119
EP2_PMM_3_Faza3_Tok36_nad80 | DIGITAL | IOD_EP2_disk | D120
EP2_PMM_3_Faza3_Tok37_nad80 | DIGITAL | IOD_EP2_disk | D121
EP2_PMM_3_Faza3_Tok38_nad80 | DIGITAL | IOD_EP2_disk | D122
EP2_PMM_3_Faza3_Tok39_nad80 | DIGITAL | IOD_EP2_disk | D123
EP2_PMM_3_Faza3_Tok40_nad80 | DIGITAL | IOD_EP2_disk | D124
EP2_PMM_3_Faza3_Tok41_nad80 | DIGITAL | IOD_EP2_disk | D125
EP2_PMM_3_Faza3_Tok42_nad80 | DIGITAL | IOD_EP2_disk | D126
EP2_PMM_3_Faza1_Tok01_med60in80 | DIGITAL | IOD_EP2_disk | D127
EP2_PMM_3_Faza1_Tok02_med60in80 | DIGITAL | IOD_EP2_disk | D128
EP2_PMM_3_Faza1_Tok03_med60in80 | DIGITAL | IOD_EP2_disk | D129
EP2_PMM_3_Faza1_Tok04_med60in80 | DIGITAL | IOD_EP2_disk | D130
EP2_PMM_3_Faza1_Tok05_med60in80 | DIGITAL | IOD_EP2_disk | D131
EP2_PMM_3_Faza1_Tok06_med60in80 | DIGITAL | IOD_EP2_disk | D132
EP2_PMM_3_Faza1_Tok07_med60in80 | DIGITAL | IOD_EP2_disk | D133
EP2_PMM_3_Faza1_Tok08_med60in80 | DIGITAL | IOD_EP2_disk | D134
EP2_PMM_3_Faza1_Tok09_med60in80 | DIGITAL | IOD_EP2_disk | D135
EP2_PMM_3_Faza1_Tok10_med60in80 | DIGITAL | IOD_EP2_disk | D136
EP2_PMM_3_Faza1_Tok11_med60in80 | DIGITAL | IOD_EP2_disk | D137
EP2_PMM_3_Faza1_Tok12_med60in80 | DIGITAL | IOD_EP2_disk | D138
EP2_PMM_3_Faza1_Tok13_med60in80 | DIGITAL | IOD_EP2_disk | D139
EP2_PMM_3_Faza1_Tok14_med60in80 | DIGITAL | IOD_EP2_disk | D140
EP2_PMM_3_Faza1_Tok15_med60in80 | DIGITAL | IOD_EP2_disk | D141
EP2_PMM_3_Faza1_Tok16_med60in80 | DIGITAL | IOD_EP2_disk | D142
EP2_PMM_3_Faza1_Tok17_med60in80 | DIGITAL | IOD_EP2_disk | D143
EP2_PMM_3_Faza1_Tok18_med60in80 | DIGITAL | IOD_EP2_disk | D144
EP2_PMM_3_Faza1_Tok19_med60in80 | DIGITAL | IOD_EP2_disk | D145
EP2_PMM_3_Faza1_Tok20_med60in80 | DIGITAL | IOD_EP2_disk | D146
EP2_PMM_3_Faza1_Tok21_med60in80 | DIGITAL | IOD_EP2_disk | D147
EP2_PMM_3_Faza1_Tok22_med60in80 | DIGITAL | IOD_EP2_disk | D148
EP2_PMM_3_Faza1_Tok23_med60in80 | DIGITAL | IOD_EP2_disk | D149
EP2_PMM_3_Faza1_Tok24_med60in80 | DIGITAL | IOD_EP2_disk | D150
EP2_PMM_3_Faza1_Tok25_med60in80 | DIGITAL | IOD_EP2_disk | D151
EP2_PMM_3_Faza1_Tok26_med60in80 | DIGITAL | IOD_EP2_disk | D152
EP2_PMM_3_Faza1_Tok27_med60in80 | DIGITAL | IOD_EP2_disk | D153
EP2_PMM_3_Faza1_Tok28_med60in80 | DIGITAL | IOD_EP2_disk | D154
EP2_PMM_3_Faza1_Tok29_med60in80 | DIGITAL | IOD_EP2_disk | D155
EP2_PMM_3_Faza1_Tok30_med60in80 | DIGITAL | IOD_EP2_disk | D156
EP2_PMM_3_Faza1_Tok31_med60in80 | DIGITAL | IOD_EP2_disk | D157
EP2_PMM_3_Faza1_Tok32_med60in80 | DIGITAL | IOD_EP2_disk | D158
EP2_PMM_3_Faza1_Tok33_med60in80 | DIGITAL | IOD_EP2_disk | D159
EP2_PMM_3_Faza1_Tok34_med60in80 | DIGITAL | IOD_EP2_disk | D160
EP2_PMM_3_Faza1_Tok35_med60in80 | DIGITAL | IOD_EP2_disk | D161
EP2_PMM_3_Faza1_Tok36_med60in80 | DIGITAL | IOD_EP2_disk | D162
EP2_PMM_3_Faza1_Tok37_med60in80 | DIGITAL | IOD_EP2_disk | D163
EP2_PMM_3_Faza1_Tok38_med60in80 | DIGITAL | IOD_EP2_disk | D164
EP2_PMM_3_Faza1_Tok39_med60in80 | DIGITAL | IOD_EP2_disk | D165
EP2_PMM_3_Faza1_Tok40_med60in80 | DIGITAL | IOD_EP2_disk | D166
EP2_PMM_3_Faza1_Tok41_med60in80 | DIGITAL | IOD_EP2_disk | D167
EP2_PMM_3_Faza1_Tok42_med60in80 | DIGITAL | IOD_EP2_disk | D168
EP2_PMM_3_Faza2_Tok01_med60in80 | DIGITAL | IOD_EP2_disk | D169
EP2_PMM_3_Faza2_Tok02_med60in80 | DIGITAL | IOD_EP2_disk | D170
EP2_PMM_3_Faza2_Tok03_med60in80 | DIGITAL | IOD_EP2_disk | D171
EP2_PMM_3_Faza2_Tok04_med60in80 | DIGITAL | IOD_EP2_disk | D172
EP2_PMM_3_Faza2_Tok05_med60in80 | DIGITAL | IOD_EP2_disk | D173
EP2_PMM_3_Faza2_Tok06_med60in80 | DIGITAL | IOD_EP2_disk | D174
EP2_PMM_3_Faza2_Tok07_med60in80 | DIGITAL | IOD_EP2_disk | D175
EP2_PMM_3_Faza2_Tok08_med60in80 | DIGITAL | IOD_EP2_disk | D176
EP2_PMM_3_Faza2_Tok09_med60in80 | DIGITAL | IOD_EP2_disk | D177
EP2_PMM_3_Faza2_Tok10_med60in80 | DIGITAL | IOD_EP2_disk | D178
EP2_PMM_3_Faza2_Tok11_med60in80 | DIGITAL | IOD_EP2_disk | D179
EP2_PMM_3_Faza2_Tok12_med60in80 | DIGITAL | IOD_EP2_disk | D180
EP2_PMM_3_Faza2_Tok13_med60in80 | DIGITAL | IOD_EP2_disk | D181
EP2_PMM_3_Faza2_Tok14_med60in80 | DIGITAL | IOD_EP2_disk | D182
EP2_PMM_3_Faza2_Tok15_med60in80 | DIGITAL | IOD_EP2_disk | D183
EP2_PMM_3_Faza2_Tok16_med60in80 | DIGITAL | IOD_EP2_disk | D184
EP2_PMM_3_Faza2_Tok17_med60in80 | DIGITAL | IOD_EP2_disk | D185
EP2_PMM_3_Faza2_Tok18_med60in80 | DIGITAL | IOD_EP2_disk | D186
EP2_PMM_3_Faza2_Tok19_med60in80 | DIGITAL | IOD_EP2_disk | D187
EP2_PMM_3_Faza2_Tok20_med60in80 | DIGITAL | IOD_EP2_disk | D188
EP2_PMM_3_Faza2_Tok21_med60in80 | DIGITAL | IOD_EP2_disk | D189
EP2_PMM_3_Faza2_Tok22_med60in80 | DIGITAL | IOD_EP2_disk | D190
EP2_PMM_3_Faza2_Tok23_med60in80 | DIGITAL | IOD_EP2_disk | D191
EP2_PMM_3_Faza2_Tok24_med60in80 | DIGITAL | IOD_EP2_disk | D192
EP2_PMM_3_Faza2_Tok25_med60in80 | DIGITAL | IOD_EP2_disk | D193
EP2_PMM_3_Faza2_Tok26_med60in80 | DIGITAL | IOD_EP2_disk | D194
EP2_PMM_3_Faza2_Tok27_med60in80 | DIGITAL | IOD_EP2_disk | D195
EP2_PMM_3_Faza2_Tok28_med60in80 | DIGITAL | IOD_EP2_disk | D196
EP2_PMM_3_Faza2_Tok29_med60in80 | DIGITAL | IOD_EP2_disk | D197
EP2_PMM_3_Faza2_Tok30_med60in80 | DIGITAL | IOD_EP2_disk | D198
EP2_PMM_3_Faza2_Tok31_med60in80 | DIGITAL | IOD_EP2_disk | D199
EP2_PMM_3_Faza2_Tok32_med60in80 | DIGITAL | IOD_EP2_disk | D200
EP2_PMM_3_Faza2_Tok33_med60in80 | DIGITAL | IOD_EP2_disk | D201
EP2_PMM_3_Faza2_Tok34_med60in80 | DIGITAL | IOD_EP2_disk | D202
EP2_PMM_3_Faza2_Tok35_med60in80 | DIGITAL | IOD_EP2_disk | D203
EP2_PMM_3_Faza2_Tok36_med60in80 | DIGITAL | IOD_EP2_disk | D204
EP2_PMM_3_Faza2_Tok37_med60in80 | DIGITAL | IOD_EP2_disk | D205
EP2_PMM_3_Faza2_Tok38_med60in80 | DIGITAL | IOD_EP2_disk | D206
EP2_PMM_3_Faza2_Tok39_med60in80 | DIGITAL | IOD_EP2_disk | D207
EP2_PMM_3_Faza2_Tok40_med60in80 | DIGITAL | IOD_EP2_disk | D208
EP2_PMM_3_Faza2_Tok41_med60in80 | DIGITAL | IOD_EP2_disk | D209
EP2_PMM_3_Faza2_Tok42_med60in80 | DIGITAL | IOD_EP2_disk | D210
EP2_PMM_3_Faza3_Tok01_med60in80 | DIGITAL | IOD_EP2_disk | D211
EP2_PMM_3_Faza3_Tok02_med60in80 | DIGITAL | IOD_EP2_disk | D212
EP2_PMM_3_Faza3_Tok03_med60in80 | DIGITAL | IOD_EP2_disk | D213
EP2_PMM_3_Faza3_Tok04_med60in80 | DIGITAL | IOD_EP2_disk | D214
EP2_PMM_3_Faza3_Tok05_med60in80 | DIGITAL | IOD_EP2_disk | D215
EP2_PMM_3_Faza3_Tok06_med60in80 | DIGITAL | IOD_EP2_disk | D216
EP2_PMM_3_Faza3_Tok07_med60in80 | DIGITAL | IOD_EP2_disk | D217
EP2_PMM_3_Faza3_Tok08_med60in80 | DIGITAL | IOD_EP2_disk | D218
EP2_PMM_3_Faza3_Tok09_med60in80 | DIGITAL | IOD_EP2_disk | D219
EP2_PMM_3_Faza3_Tok10_med60in80 | DIGITAL | IOD_EP2_disk | D220
EP2_PMM_3_Faza3_Tok11_med60in80 | DIGITAL | IOD_EP2_disk | D221
EP2_PMM_3_Faza3_Tok12_med60in80 | DIGITAL | IOD_EP2_disk | D222
EP2_PMM_3_Faza3_Tok13_med60in80 | DIGITAL | IOD_EP2_disk | D223
EP2_PMM_3_Faza3_Tok14_med60in80 | DIGITAL | IOD_EP2_disk | D224
EP2_PMM_3_Faza3_Tok15_med60in80 | DIGITAL | IOD_EP2_disk | D225
EP2_PMM_3_Faza3_Tok16_med60in80 | DIGITAL | IOD_EP2_disk | D226
EP2_PMM_3_Faza3_Tok17_med60in80 | DIGITAL | IOD_EP2_disk | D227
EP2_PMM_3_Faza3_Tok18_med60in80 | DIGITAL | IOD_EP2_disk | D228
EP2_PMM_3_Faza3_Tok19_med60in80 | DIGITAL | IOD_EP2_disk | D229
EP2_PMM_3_Faza3_Tok20_med60in80 | DIGITAL | IOD_EP2_disk | D230
EP2_PMM_3_Faza3_Tok21_med60in80 | DIGITAL | IOD_EP2_disk | D231
EP2_PMM_3_Faza3_Tok22_med60in80 | DIGITAL | IOD_EP2_disk | D232
EP2_PMM_3_Faza3_Tok23_med60in80 | DIGITAL | IOD_EP2_disk | D233
EP2_PMM_3_Faza3_Tok24_med60in80 | DIGITAL | IOD_EP2_disk | D234
EP2_PMM_3_Faza3_Tok25_med60in80 | DIGITAL | IOD_EP2_disk | D235
EP2_PMM_3_Faza3_Tok26_med60in80 | DIGITAL | IOD_EP2_disk | D236
EP2_PMM_3_Faza3_Tok27_med60in80 | DIGITAL | IOD_EP2_disk | D237
EP2_PMM_3_Faza3_Tok28_med60in80 | DIGITAL | IOD_EP2_disk | D238
EP2_PMM_3_Faza3_Tok29_med60in80 | DIGITAL | IOD_EP2_disk | D239
EP2_PMM_3_Faza3_Tok30_med60in80 | DIGITAL | IOD_EP2_disk | D240
EP2_PMM_3_Faza3_Tok31_med60in80 | DIGITAL | IOD_EP2_disk | D241
EP2_PMM_3_Faza3_Tok32_med60in80 | DIGITAL | IOD_EP2_disk | D242
EP2_PMM_3_Faza3_Tok33_med60in80 | DIGITAL | IOD_EP2_disk | D243
EP2_PMM_3_Faza3_Tok34_med60in80 | DIGITAL | IOD_EP2_disk | D244
EP2_PMM_3_Faza3_Tok35_med60in80 | DIGITAL | IOD_EP2_disk | D245
EP2_PMM_3_Faza3_Tok36_med60in80 | DIGITAL | IOD_EP2_disk | D246
EP2_PMM_3_Faza3_Tok37_med60in80 | DIGITAL | IOD_EP2_disk | D247
EP2_PMM_3_Faza3_Tok38_med60in80 | DIGITAL | IOD_EP2_disk | D248
EP2_PMM_3_Faza3_Tok39_med60in80 | DIGITAL | IOD_EP2_disk | D249
EP2_PMM_3_Faza3_Tok40_med60in80 | DIGITAL | IOD_EP2_disk | D250
EP2_PMM_3_Faza3_Tok41_med60in80 | DIGITAL | IOD_EP2_disk | D251
EP2_PMM_3_Faza3_Tok42_med60in80 | DIGITAL | IOD_EP2_disk | D252
EP2_PMM_2_Faza1_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D253
EP2_PMM_2_Faza1_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D254
EP2_PMM_2_Faza1_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D255
EP2_PMM_2_Faza1_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D256
EP2_PMM_2_Faza1_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D257
EP2_PMM_2_Faza1_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D258
EP2_PMM_2_Faza1_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D259
EP2_PMM_2_Faza1_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D260
EP2_PMM_2_Faza1_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D261
EP2_PMM_2_Faza1_Tok10_nad80 | DIGITAL | IOD_EP2_disk | D262
EP2_PMM_2_Faza1_Tok11_nad80 | DIGITAL | IOD_EP2_disk | D263
EP2_PMM_2_Faza1_Tok12_nad80 | DIGITAL | IOD_EP2_disk | D264
EP2_PMM_2_Faza1_Tok13_nad80 | DIGITAL | IOD_EP2_disk | D265
EP2_PMM_2_Faza1_Tok14_nad80 | DIGITAL | IOD_EP2_disk | D266
EP2_PMM_2_Faza1_Tok15_nad80 | DIGITAL | IOD_EP2_disk | D267
EP2_PMM_2_Faza1_Tok16_nad80 | DIGITAL | IOD_EP2_disk | D268
EP2_PMM_2_Faza1_Tok17_nad80 | DIGITAL | IOD_EP2_disk | D269
EP2_PMM_2_Faza1_Tok18_nad80 | DIGITAL | IOD_EP2_disk | D270
EP2_PMM_2_Faza1_Tok19_nad80 | DIGITAL | IOD_EP2_disk | D271
EP2_PMM_2_Faza1_Tok20_nad80 | DIGITAL | IOD_EP2_disk | D272
EP2_PMM_2_Faza1_Tok21_nad80 | DIGITAL | IOD_EP2_disk | D273
EP2_PMM_2_Faza1_Tok22_nad80 | DIGITAL | IOD_EP2_disk | D274
EP2_PMM_2_Faza1_Tok23_nad80 | DIGITAL | IOD_EP2_disk | D275
EP2_PMM_2_Faza1_Tok24_nad80 | DIGITAL | IOD_EP2_disk | D276
EP2_PMM_2_Faza1_Tok25_nad80 | DIGITAL | IOD_EP2_disk | D277
EP2_PMM_2_Faza1_Tok26_nad80 | DIGITAL | IOD_EP2_disk | D278
EP2_PMM_2_Faza1_Tok27_nad80 | DIGITAL | IOD_EP2_disk | D279
EP2_PMM_2_Faza1_Tok28_nad80 | DIGITAL | IOD_EP2_disk | D280
EP2_PMM_2_Faza1_Tok29_nad80 | DIGITAL | IOD_EP2_disk | D281
EP2_PMM_2_Faza1_Tok30_nad80 | DIGITAL | IOD_EP2_disk | D282
EP2_PMM_2_Faza1_Tok31_nad80 | DIGITAL | IOD_EP2_disk | D283
EP2_PMM_2_Faza1_Tok32_nad80 | DIGITAL | IOD_EP2_disk | D284
EP2_PMM_2_Faza1_Tok33_nad80 | DIGITAL | IOD_EP2_disk | D285
EP2_PMM_2_Faza1_Tok34_nad80 | DIGITAL | IOD_EP2_disk | D286
EP2_PMM_2_Faza1_Tok35_nad80 | DIGITAL | IOD_EP2_disk | D287
EP2_PMM_2_Faza1_Tok36_nad80 | DIGITAL | IOD_EP2_disk | D288
EP2_PMM_2_Faza1_Tok37_nad80 | DIGITAL | IOD_EP2_disk | D289
EP2_PMM_2_Faza1_Tok38_nad80 | DIGITAL | IOD_EP2_disk | D290
EP2_PMM_2_Faza1_Tok39_nad80 | DIGITAL | IOD_EP2_disk | D291
EP2_PMM_2_Faza1_Tok40_nad80 | DIGITAL | IOD_EP2_disk | D292
EP2_PMM_2_Faza1_Tok41_nad80 | DIGITAL | IOD_EP2_disk | D293
EP2_PMM_2_Faza1_Tok42_nad80 | DIGITAL | IOD_EP2_disk | D294
EP2_PMM_2_Faza2_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D295
EP2_PMM_2_Faza2_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D296
EP2_PMM_2_Faza2_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D297
EP2_PMM_2_Faza2_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D298
EP2_PMM_2_Faza2_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D299
EP2_PMM_2_Faza2_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D300
EP2_PMM_2_Faza2_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D301
EP2_PMM_2_Faza2_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D302
EP2_PMM_2_Faza2_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D303
EP2_PMM_2_Faza2_Tok10_nad80 | DIGITAL | IOD_EP2_disk | D304
EP2_PMM_2_Faza2_Tok11_nad80 | DIGITAL | IOD_EP2_disk | D305
EP2_PMM_2_Faza2_Tok12_nad80 | DIGITAL | IOD_EP2_disk | D306
EP2_PMM_2_Faza2_Tok13_nad80 | DIGITAL | IOD_EP2_disk | D307
EP2_PMM_2_Faza2_Tok14_nad80 | DIGITAL | IOD_EP2_disk | D308
EP2_PMM_2_Faza2_Tok15_nad80 | DIGITAL | IOD_EP2_disk | D309
EP2_PMM_2_Faza2_Tok16_nad80 | DIGITAL | IOD_EP2_disk | D310
EP2_PMM_2_Faza2_Tok17_nad80 | DIGITAL | IOD_EP2_disk | D311
EP2_PMM_2_Faza2_Tok18_nad80 | DIGITAL | IOD_EP2_disk | D312
EP2_PMM_2_Faza2_Tok19_nad80 | DIGITAL | IOD_EP2_disk | D313
EP2_PMM_2_Faza2_Tok20_nad80 | DIGITAL | IOD_EP2_disk | D314
EP2_PMM_2_Faza2_Tok21_nad80 | DIGITAL | IOD_EP2_disk | D315
EP2_PMM_2_Faza2_Tok22_nad80 | DIGITAL | IOD_EP2_disk | D316
EP2_PMM_2_Faza2_Tok23_nad80 | DIGITAL | IOD_EP2_disk | D317
EP2_PMM_2_Faza2_Tok24_nad80 | DIGITAL | IOD_EP2_disk | D318
EP2_PMM_2_Faza2_Tok25_nad80 | DIGITAL | IOD_EP2_disk | D319
EP2_PMM_2_Faza2_Tok26_nad80 | DIGITAL | IOD_EP2_disk | D320
EP2_PMM_2_Faza2_Tok27_nad80 | DIGITAL | IOD_EP2_disk | D321
EP2_PMM_2_Faza2_Tok28_nad80 | DIGITAL | IOD_EP2_disk | D322
EP2_PMM_2_Faza2_Tok29_nad80 | DIGITAL | IOD_EP2_disk | D323
EP2_PMM_2_Faza2_Tok30_nad80 | DIGITAL | IOD_EP2_disk | D324
EP2_PMM_2_Faza2_Tok31_nad80 | DIGITAL | IOD_EP2_disk | D325
EP2_PMM_2_Faza2_Tok32_nad80 | DIGITAL | IOD_EP2_disk | D326
EP2_PMM_2_Faza2_Tok33_nad80 | DIGITAL | IOD_EP2_disk | D327
EP2_PMM_2_Faza2_Tok34_nad80 | DIGITAL | IOD_EP2_disk | D328
EP2_PMM_2_Faza2_Tok35_nad80 | DIGITAL | IOD_EP2_disk | D329
EP2_PMM_2_Faza2_Tok36_nad80 | DIGITAL | IOD_EP2_disk | D330
EP2_PMM_2_Faza2_Tok37_nad80 | DIGITAL | IOD_EP2_disk | D331
EP2_PMM_2_Faza2_Tok38_nad80 | DIGITAL | IOD_EP2_disk | D332
EP2_PMM_2_Faza2_Tok39_nad80 | DIGITAL | IOD_EP2_disk | D333
EP2_PMM_2_Faza2_Tok40_nad80 | DIGITAL | IOD_EP2_disk | D334
EP2_PMM_2_Faza2_Tok41_nad80 | DIGITAL | IOD_EP2_disk | D335
EP2_PMM_2_Faza2_Tok42_nad80 | DIGITAL | IOD_EP2_disk | D336
EP2_PMM_2_Faza3_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D337
EP2_PMM_2_Faza3_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D338
EP2_PMM_2_Faza3_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D339
EP2_PMM_2_Faza3_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D340
EP2_PMM_2_Faza3_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D341
EP2_PMM_2_Faza3_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D342
EP2_PMM_2_Faza3_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D343
EP2_PMM_2_Faza3_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D344
EP2_PMM_2_Faza3_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D345
EP2_PMM_2_Faza3_Tok10_nad80 | DIGITAL | IOD_EP2_disk | D346
EP2_PMM_2_Faza3_Tok11_nad80 | DIGITAL | IOD_EP2_disk | D347
EP2_PMM_2_Faza3_Tok12_nad80 | DIGITAL | IOD_EP2_disk | D348
EP2_PMM_2_Faza3_Tok13_nad80 | DIGITAL | IOD_EP2_disk | D349
EP2_PMM_2_Faza3_Tok14_nad80 | DIGITAL | IOD_EP2_disk | D350
EP2_PMM_2_Faza3_Tok15_nad80 | DIGITAL | IOD_EP2_disk | D351
EP2_PMM_2_Faza3_Tok16_nad80 | DIGITAL | IOD_EP2_disk | D352
EP2_PMM_2_Faza3_Tok17_nad80 | DIGITAL | IOD_EP2_disk | D353
EP2_PMM_2_Faza3_Tok18_nad80 | DIGITAL | IOD_EP2_disk | D354
EP2_PMM_2_Faza3_Tok19_nad80 | DIGITAL | IOD_EP2_disk | D355
EP2_PMM_2_Faza3_Tok20_nad80 | DIGITAL | IOD_EP2_disk | D356
EP2_PMM_2_Faza3_Tok21_nad80 | DIGITAL | IOD_EP2_disk | D357
EP2_PMM_2_Faza3_Tok22_nad80 | DIGITAL | IOD_EP2_disk | D358
EP2_PMM_2_Faza3_Tok23_nad80 | DIGITAL | IOD_EP2_disk | D359
EP2_PMM_2_Faza3_Tok24_nad80 | DIGITAL | IOD_EP2_disk | D360
EP2_PMM_2_Faza3_Tok25_nad80 | DIGITAL | IOD_EP2_disk | D361
EP2_PMM_2_Faza3_Tok26_nad80 | DIGITAL | IOD_EP2_disk | D362
EP2_PMM_2_Faza3_Tok27_nad80 | DIGITAL | IOD_EP2_disk | D363
EP2_PMM_2_Faza3_Tok28_nad80 | DIGITAL | IOD_EP2_disk | D364
EP2_PMM_2_Faza3_Tok29_nad80 | DIGITAL | IOD_EP2_disk | D365
EP2_PMM_2_Faza3_Tok30_nad80 | DIGITAL | IOD_EP2_disk | D366
EP2_PMM_2_Faza3_Tok31_nad80 | DIGITAL | IOD_EP2_disk | D367
EP2_PMM_2_Faza3_Tok32_nad80 | DIGITAL | IOD_EP2_disk | D368
EP2_PMM_2_Faza3_Tok33_nad80 | DIGITAL | IOD_EP2_disk | D369
EP2_PMM_2_Faza3_Tok34_nad80 | DIGITAL | IOD_EP2_disk | D370
EP2_PMM_2_Faza3_Tok35_nad80 | DIGITAL | IOD_EP2_disk | D371
EP2_PMM_2_Faza3_Tok36_nad80 | DIGITAL | IOD_EP2_disk | D372
EP2_PMM_2_Faza3_Tok37_nad80 | DIGITAL | IOD_EP2_disk | D373
EP2_PMM_2_Faza3_Tok38_nad80 | DIGITAL | IOD_EP2_disk | D374
EP2_PMM_2_Faza3_Tok39_nad80 | DIGITAL | IOD_EP2_disk | D375
EP2_PMM_2_Faza3_Tok40_nad80 | DIGITAL | IOD_EP2_disk | D376
EP2_PMM_2_Faza3_Tok41_nad80 | DIGITAL | IOD_EP2_disk | D377
EP2_PMM_2_Faza3_Tok42_nad80 | DIGITAL | IOD_EP2_disk | D378
EP2_PMM_2_Faza1_Tok01_med60in80 | DIGITAL | IOD_EP2_disk | D379
EP2_PMM_2_Faza1_Tok02_med60in80 | DIGITAL | IOD_EP2_disk | D380
EP2_PMM_2_Faza1_Tok03_med60in80 | DIGITAL | IOD_EP2_disk | D381
EP2_PMM_2_Faza1_Tok04_med60in80 | DIGITAL | IOD_EP2_disk | D382
EP2_PMM_2_Faza1_Tok05_med60in80 | DIGITAL | IOD_EP2_disk | D383
EP2_PMM_2_Faza1_Tok06_med60in80 | DIGITAL | IOD_EP2_disk | D384
EP2_PMM_2_Faza1_Tok07_med60in80 | DIGITAL | IOD_EP2_disk | D385
EP2_PMM_2_Faza1_Tok08_med60in80 | DIGITAL | IOD_EP2_disk | D386
EP2_PMM_2_Faza1_Tok09_med60in80 | DIGITAL | IOD_EP2_disk | D387
EP2_PMM_2_Faza1_Tok10_med60in80 | DIGITAL | IOD_EP2_disk | D388
EP2_PMM_2_Faza1_Tok11_med60in80 | DIGITAL | IOD_EP2_disk | D389
EP2_PMM_2_Faza1_Tok12_med60in80 | DIGITAL | IOD_EP2_disk | D390
EP2_PMM_2_Faza1_Tok13_med60in80 | DIGITAL | IOD_EP2_disk | D391
EP2_PMM_2_Faza1_Tok14_med60in80 | DIGITAL | IOD_EP2_disk | D392
EP2_PMM_2_Faza1_Tok15_med60in80 | DIGITAL | IOD_EP2_disk | D393
EP2_PMM_2_Faza1_Tok16_med60in80 | DIGITAL | IOD_EP2_disk | D394
EP2_PMM_2_Faza1_Tok17_med60in80 | DIGITAL | IOD_EP2_disk | D395
EP2_PMM_2_Faza1_Tok18_med60in80 | DIGITAL | IOD_EP2_disk | D396
EP2_PMM_2_Faza1_Tok19_med60in80 | DIGITAL | IOD_EP2_disk | D397
EP2_PMM_2_Faza1_Tok20_med60in80 | DIGITAL | IOD_EP2_disk | D398
EP2_PMM_2_Faza1_Tok21_med60in80 | DIGITAL | IOD_EP2_disk | D399
EP2_PMM_2_Faza1_Tok22_med60in80 | DIGITAL | IOD_EP2_disk | D400
EP2_PMM_2_Faza1_Tok23_med60in80 | DIGITAL | IOD_EP2_disk | D401
EP2_PMM_2_Faza1_Tok24_med60in80 | DIGITAL | IOD_EP2_disk | D402
EP2_PMM_2_Faza1_Tok25_med60in80 | DIGITAL | IOD_EP2_disk | D403
EP2_PMM_2_Faza1_Tok26_med60in80 | DIGITAL | IOD_EP2_disk | D404
EP2_PMM_2_Faza1_Tok27_med60in80 | DIGITAL | IOD_EP2_disk | D405
EP2_PMM_2_Faza1_Tok28_med60in80 | DIGITAL | IOD_EP2_disk | D406
EP2_PMM_2_Faza1_Tok29_med60in80 | DIGITAL | IOD_EP2_disk | D407
EP2_PMM_2_Faza1_Tok30_med60in80 | DIGITAL | IOD_EP2_disk | D408
EP2_PMM_2_Faza1_Tok31_med60in80 | DIGITAL | IOD_EP2_disk | D409
EP2_PMM_2_Faza1_Tok32_med60in80 | DIGITAL | IOD_EP2_disk | D410
EP2_PMM_2_Faza1_Tok33_med60in80 | DIGITAL | IOD_EP2_disk | D411
EP2_PMM_2_Faza1_Tok34_med60in80 | DIGITAL | IOD_EP2_disk | D412
EP2_PMM_2_Faza1_Tok35_med60in80 | DIGITAL | IOD_EP2_disk | D413
EP2_PMM_2_Faza1_Tok36_med60in80 | DIGITAL | IOD_EP2_disk | D414
EP2_PMM_2_Faza1_Tok37_med60in80 | DIGITAL | IOD_EP2_disk | D415
EP2_PMM_2_Faza1_Tok38_med60in80 | DIGITAL | IOD_EP2_disk | D416
EP2_PMM_2_Faza1_Tok39_med60in80 | DIGITAL | IOD_EP2_disk | D417
EP2_PMM_2_Faza1_Tok40_med60in80 | DIGITAL | IOD_EP2_disk | D418
EP2_PMM_2_Faza1_Tok41_med60in80 | DIGITAL | IOD_EP2_disk | D419
EP2_PMM_2_Faza1_Tok42_med60in80 | DIGITAL | IOD_EP2_disk | D420
EP2_PMM_2_Faza2_Tok01_med60in80 | DIGITAL | IOD_EP2_disk | D421
EP2_PMM_2_Faza2_Tok02_med60in80 | DIGITAL | IOD_EP2_disk | D422
EP2_PMM_2_Faza2_Tok03_med60in80 | DIGITAL | IOD_EP2_disk | D423
EP2_PMM_2_Faza2_Tok04_med60in80 | DIGITAL | IOD_EP2_disk | D424
EP2_PMM_2_Faza2_Tok05_med60in80 | DIGITAL | IOD_EP2_disk | D425
EP2_PMM_2_Faza2_Tok06_med60in80 | DIGITAL | IOD_EP2_disk | D426
EP2_PMM_2_Faza2_Tok07_med60in80 | DIGITAL | IOD_EP2_disk | D427
EP2_PMM_2_Faza2_Tok08_med60in80 | DIGITAL | IOD_EP2_disk | D428
EP2_PMM_2_Faza2_Tok09_med60in80 | DIGITAL | IOD_EP2_disk | D429
EP2_PMM_2_Faza2_Tok10_med60in80 | DIGITAL | IOD_EP2_disk | D430
EP2_PMM_2_Faza2_Tok11_med60in80 | DIGITAL | IOD_EP2_disk | D431
EP2_PMM_2_Faza2_Tok12_med60in80 | DIGITAL | IOD_EP2_disk | D432
EP2_PMM_2_Faza2_Tok13_med60in80 | DIGITAL | IOD_EP2_disk | D433
EP2_PMM_2_Faza2_Tok14_med60in80 | DIGITAL | IOD_EP2_disk | D434
EP2_PMM_2_Faza2_Tok15_med60in80 | DIGITAL | IOD_EP2_disk | D435
EP2_PMM_2_Faza2_Tok16_med60in80 | DIGITAL | IOD_EP2_disk | D436
EP2_PMM_2_Faza2_Tok17_med60in80 | DIGITAL | IOD_EP2_disk | D437
EP2_PMM_2_Faza2_Tok18_med60in80 | DIGITAL | IOD_EP2_disk | D438
EP2_PMM_2_Faza2_Tok19_med60in80 | DIGITAL | IOD_EP2_disk | D439
EP2_PMM_2_Faza2_Tok20_med60in80 | DIGITAL | IOD_EP2_disk | D440
EP2_PMM_2_Faza2_Tok21_med60in80 | DIGITAL | IOD_EP2_disk | D441
EP2_PMM_2_Faza2_Tok22_med60in80 | DIGITAL | IOD_EP2_disk | D442
EP2_PMM_2_Faza2_Tok23_med60in80 | DIGITAL | IOD_EP2_disk | D443
EP2_PMM_2_Faza2_Tok24_med60in80 | DIGITAL | IOD_EP2_disk | D444
EP2_PMM_2_Faza2_Tok25_med60in80 | DIGITAL | IOD_EP2_disk | D445
EP2_PMM_2_Faza2_Tok26_med60in80 | DIGITAL | IOD_EP2_disk | D446
EP2_PMM_2_Faza2_Tok27_med60in80 | DIGITAL | IOD_EP2_disk | D447
EP2_PMM_2_Faza2_Tok28_med60in80 | DIGITAL | IOD_EP2_disk | D448
EP2_PMM_2_Faza2_Tok29_med60in80 | DIGITAL | IOD_EP2_disk | D449
EP2_PMM_2_Faza2_Tok30_med60in80 | DIGITAL | IOD_EP2_disk | D450
EP2_PMM_2_Faza2_Tok31_med60in80 | DIGITAL | IOD_EP2_disk | D451
EP2_PMM_2_Faza2_Tok32_med60in80 | DIGITAL | IOD_EP2_disk | D452
EP2_PMM_2_Faza2_Tok33_med60in80 | DIGITAL | IOD_EP2_disk | D453
EP2_PMM_2_Faza2_Tok34_med60in80 | DIGITAL | IOD_EP2_disk | D454
EP2_PMM_2_Faza2_Tok35_med60in80 | DIGITAL | IOD_EP2_disk | D455
EP2_PMM_2_Faza2_Tok36_med60in80 | DIGITAL | IOD_EP2_disk | D456
EP2_PMM_2_Faza2_Tok37_med60in80 | DIGITAL | IOD_EP2_disk | D457
EP2_PMM_2_Faza2_Tok38_med60in80 | DIGITAL | IOD_EP2_disk | D458
EP2_PMM_2_Faza2_Tok39_med60in80 | DIGITAL | IOD_EP2_disk | D459
EP2_PMM_2_Faza2_Tok40_med60in80 | DIGITAL | IOD_EP2_disk | D460
EP2_PMM_2_Faza2_Tok41_med60in80 | DIGITAL | IOD_EP2_disk | D461
EP2_PMM_2_Faza2_Tok42_med60in80 | DIGITAL | IOD_EP2_disk | D462
EP2_PMM_2_Faza3_Tok01_med60in80 | DIGITAL | IOD_EP2_disk | D463
EP2_PMM_2_Faza3_Tok02_med60in80 | DIGITAL | IOD_EP2_disk | D464
EP2_PMM_2_Faza3_Tok03_med60in80 | DIGITAL | IOD_EP2_disk | D465
EP2_PMM_2_Faza3_Tok04_med60in80 | DIGITAL | IOD_EP2_disk | D466
EP2_PMM_2_Faza3_Tok05_med60in80 | DIGITAL | IOD_EP2_disk | D467
EP2_PMM_2_Faza3_Tok06_med60in80 | DIGITAL | IOD_EP2_disk | D468
EP2_PMM_2_Faza3_Tok07_med60in80 | DIGITAL | IOD_EP2_disk | D469
EP2_PMM_2_Faza3_Tok08_med60in80 | DIGITAL | IOD_EP2_disk | D470
EP2_PMM_2_Faza3_Tok09_med60in80 | DIGITAL | IOD_EP2_disk | D471
EP2_PMM_2_Faza3_Tok10_med60in80 | DIGITAL | IOD_EP2_disk | D472
EP2_PMM_2_Faza3_Tok11_med60in80 | DIGITAL | IOD_EP2_disk | D473
EP2_PMM_2_Faza3_Tok12_med60in80 | DIGITAL | IOD_EP2_disk | D474
EP2_PMM_2_Faza3_Tok13_med60in80 | DIGITAL | IOD_EP2_disk | D475
EP2_PMM_2_Faza3_Tok14_med60in80 | DIGITAL | IOD_EP2_disk | D476
EP2_PMM_2_Faza3_Tok15_med60in80 | DIGITAL | IOD_EP2_disk | D477
EP2_PMM_2_Faza3_Tok16_med60in80 | DIGITAL | IOD_EP2_disk | D478
EP2_PMM_2_Faza3_Tok17_med60in80 | DIGITAL | IOD_EP2_disk | D479
EP2_PMM_2_Faza3_Tok18_med60in80 | DIGITAL | IOD_EP2_disk | D480
EP2_PMM_2_Faza3_Tok19_med60in80 | DIGITAL | IOD_EP2_disk | D481
EP2_PMM_2_Faza3_Tok20_med60in80 | DIGITAL | IOD_EP2_disk | D482
EP2_PMM_2_Faza3_Tok21_med60in80 | DIGITAL | IOD_EP2_disk | D483
EP2_PMM_2_Faza3_Tok22_med60in80 | DIGITAL | IOD_EP2_disk | D484
EP2_PMM_2_Faza3_Tok23_med60in80 | DIGITAL | IOD_EP2_disk | D485
EP2_PMM_2_Faza3_Tok24_med60in80 | DIGITAL | IOD_EP2_disk | D486
EP2_PMM_2_Faza3_Tok25_med60in80 | DIGITAL | IOD_EP2_disk | D487
EP2_PMM_2_Faza3_Tok26_med60in80 | DIGITAL | IOD_EP2_disk | D488
EP2_PMM_2_Faza3_Tok27_med60in80 | DIGITAL | IOD_EP2_disk | D489
EP2_PMM_2_Faza3_Tok28_med60in80 | DIGITAL | IOD_EP2_disk | D490
EP2_PMM_2_Faza3_Tok29_med60in80 | DIGITAL | IOD_EP2_disk | D491
EP2_PMM_2_Faza3_Tok30_med60in80 | DIGITAL | IOD_EP2_disk | D492
EP2_PMM_2_Faza3_Tok31_med60in80 | DIGITAL | IOD_EP2_disk | D493
EP2_PMM_2_Faza3_Tok32_med60in80 | DIGITAL | IOD_EP2_disk | D494
EP2_PMM_2_Faza3_Tok33_med60in80 | DIGITAL | IOD_EP2_disk | D495
EP2_PMM_2_Faza3_Tok34_med60in80 | DIGITAL | IOD_EP2_disk | D496
EP2_PMM_2_Faza3_Tok35_med60in80 | DIGITAL | IOD_EP2_disk | D497
EP2_PMM_2_Faza3_Tok36_med60in80 | DIGITAL | IOD_EP2_disk | D498
EP2_PMM_2_Faza3_Tok37_med60in80 | DIGITAL | IOD_EP2_disk | D499
EP2_PMM_2_Faza3_Tok38_med60in80 | DIGITAL | IOD_EP2_disk | D500
EP2_PMM_2_Faza3_Tok39_med60in80 | DIGITAL | IOD_EP2_disk | D501
EP2_PMM_2_Faza3_Tok40_med60in80 | DIGITAL | IOD_EP2_disk | D502
EP2_PMM_2_Faza3_Tok41_med60in80 | DIGITAL | IOD_EP2_disk | D503
EP2_PMM_2_Faza3_Tok42_med60in80 | DIGITAL | IOD_EP2_disk | D504
EP2_PMM_1_Faza1_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D505
EP2_PMM_1_Faza1_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D506
EP2_PMM_1_Faza1_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D507
EP2_PMM_1_Faza1_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D508
EP2_PMM_1_Faza1_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D509
EP2_PMM_1_Faza1_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D510
EP2_PMM_1_Faza1_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D511
EP2_PMM_1_Faza1_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D512
EP2_PMM_1_Faza1_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D513
EP2_PMM_1_Faza2_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D514
EP2_PMM_1_Faza2_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D515
EP2_PMM_1_Faza2_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D516
EP2_PMM_1_Faza2_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D517
EP2_PMM_1_Faza2_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D518
EP2_PMM_1_Faza2_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D519
EP2_PMM_1_Faza2_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D520
EP2_PMM_1_Faza2_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D521
EP2_PMM_1_Faza2_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D522
EP2_PMM_1_Polje2_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D523
EP2_PMM_1_Polje2_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D524
EP2_PMM_1_Polje2_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D525
EP2_PMM_1_Polje2_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D526
EP2_PMM_1_Polje2_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D527
EP2_PMM_1_Polje2_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D528
EP2_PMM_1_Polje2_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D529
EP2_PMM_1_Polje2_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D530
EP2_PMM_1_Polje2_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D531
EP2_PMM_UC_PoljeB_Tok10_nad80 | DIGITAL | IOD_EP2_disk | D532
EP2_PMM_UC_PoljeB_Tok11_nad80 | DIGITAL | IOD_EP2_disk | D533
EP2_PMM_UC_PoljeB_Tok12_nad80 | DIGITAL | IOD_EP2_disk | D534
EP2_PMM_1_Faza1_Tok01_med60in80 | DIGITAL | IOD_EP2_disk | D535
EP2_PMM_1_Faza1_Tok02_med60in80 | DIGITAL | IOD_EP2_disk | D536
EP2_PMM_1_Faza1_Tok03_med60in80 | DIGITAL | IOD_EP2_disk | D537
EP2_PMM_1_Faza1_Tok04_med60in80 | DIGITAL | IOD_EP2_disk | D538
EP2_PMM_1_Faza1_Tok05_med60in80 | DIGITAL | IOD_EP2_disk | D539
EP2_PMM_1_Faza1_Tok06_med60in80 | DIGITAL | IOD_EP2_disk | D540
EP2_PMM_1_Faza1_Tok07_med60in80 | DIGITAL | IOD_EP2_disk | D541
EP2_PMM_1_Faza1_Tok08_med60in80 | DIGITAL | IOD_EP2_disk | D542
EP2_PMM_1_Faza1_Tok09_med60in80 | DIGITAL | IOD_EP2_disk | D543
EP2_PMM_UC_PoljeA_Tok10_med60in80 | DIGITAL | IOD_EP2_disk | D544
EP2_PMM_UC_PoljeA_Tok11_med60in80 | DIGITAL | IOD_EP2_disk | D545
EP2_PMM_UC_PoljeA_Tok12_med60in80 | DIGITAL | IOD_EP2_disk | D546
EP2_PMM_1_Faza2_Tok01_med60in80 | DIGITAL | IOD_EP2_disk | D547
EP2_PMM_1_Faza2_Tok02_med60in80 | DIGITAL | IOD_EP2_disk | D548
EP2_PMM_1_Faza2_Tok03_med60in80 | DIGITAL | IOD_EP2_disk | D549
EP2_PMM_1_Faza2_Tok04_med60in80 | DIGITAL | IOD_EP2_disk | D550
EP2_PMM_1_Faza2_Tok05_med60in80 | DIGITAL | IOD_EP2_disk | D551
EP2_PMM_1_Faza2_Tok06_med60in80 | DIGITAL | IOD_EP2_disk | D552
EP2_PMM_1_Faza2_Tok07_med60in80 | DIGITAL | IOD_EP2_disk | D553
EP2_PMM_1_Faza2_Tok08_med60in80 | DIGITAL | IOD_EP2_disk | D554
EP2_PMM_1_Faza2_Tok09_med60in80 | DIGITAL | IOD_EP2_disk | D555
EP2_PMM_UC_PoljeB_Tok10_med60in80 | DIGITAL | IOD_EP2_disk | D556
EP2_PMM_UC_PoljeB_Tok11_med60in80 | DIGITAL | IOD_EP2_disk | D557
EP2_PMM_UC_PoljeB_Tok12_med60in80 | DIGITAL | IOD_EP2_disk | D558
EP2_Polje_3Faza1_Tok01_16_nad80 | DIGITAL | IOD_EP2_disk | D2000[16]
EP2_Polje_3Faza1_Tok17_32_nad80 | DIGITAL | IOD_EP2_disk | D2016[16]
EP2_Polje_3Faza1_Tok33_42_nad80 | DIGITAL | IOD_EP2_disk | D2032[16]
EP2_Polje_3Faza2_Tok01_16_nad80 | DIGITAL | IOD_EP2_disk | D2048[16]
EP2_Polje_3Faza2_Tok17_32_nad80 | DIGITAL | IOD_EP2_disk | D2064[16]
EP2_Polje_3Faza2_Tok33_42_nad80 | DIGITAL | IOD_EP2_disk | D2080[16]
EP2_Polje_3Faza3_Tok01_16_nad80 | DIGITAL | IOD_EP2_disk | D2096[16]
EP2_Polje_3Faza3_Tok17_32_nad80 | DIGITAL | IOD_EP2_disk | D2112[16]
EP2_Polje_3Faza3_Tok33_42_nad80 | DIGITAL | IOD_EP2_disk | D2128[16]
EP2_Polje_2Faza1_Tok01_16_nad80 | DIGITAL | IOD_EP2_disk | D2144[16]
EP2_Polje_2Faza1_Tok17_32_nad80 | DIGITAL | IOD_EP2_disk | D2160[16]
EP2_Polje_2Faza1_Tok33_42_nad80 | DIGITAL | IOD_EP2_disk | D2176[16]
EP2_Polje_2Faza2_Tok01_16_nad80 | DIGITAL | IOD_EP2_disk | D2192[16]
EP2_Polje_2Faza2_Tok17_32_nad80 | DIGITAL | IOD_EP2_disk | D2208[16]
EP2_Polje_2Faza2_Tok33_42_nad80 | DIGITAL | IOD_EP2_disk | D2224[16]
EP2_Polje_2Faza3_Tok01_16_nad80 | DIGITAL | IOD_EP2_disk | D2240[16]
EP2_Polje_2Faza3_Tok17_32_nad80 | DIGITAL | IOD_EP2_disk | D2256[16]
EP2_Polje_2Faza3_Tok33_42_nad80 | DIGITAL | IOD_EP2_disk | D2272[16]
EP2_Polje_1Faza1_Tok01_16_nad80 | DIGITAL | IOD_EP2_disk | D2288[16]
EP2_Polje_1Faza2_Tok01_16_nad80 | DIGITAL | IOD_EP2_disk | D2304[16]
EP2_Polje_3Faza1_Tok01_16_med60_80 | DIGITAL | IOD_EP2_disk | D2320[16]
EP2_Polje_3Faza1_Tok17_32_med60_80 | DIGITAL | IOD_EP2_disk | D2336[16]
EP2_Polje_3Faza1_Tok33_42_med60_80 | DIGITAL | IOD_EP2_disk | D2352[16]
EP2_Polje_3Faza2_Tok01_16_med60_80 | DIGITAL | IOD_EP2_disk | D2368[16]
EP2_Polje_3Faza2_Tok17_32_med60_80 | DIGITAL | IOD_EP2_disk | D2384[16]
EP2_Polje_3Faza2_Tok33_42_med60_80 | DIGITAL | IOD_EP2_disk | D2400[16]
EP2_Polje_3Faza3_Tok01_16_med60_80 | DIGITAL | IOD_EP2_disk | D2416[16]
EP2_Polje_3Faza3_Tok17_32_med60_80 | DIGITAL | IOD_EP2_disk | D2432[16]
EP2_Polje_3Faza3_Tok33_42_med60_80 | DIGITAL | IOD_EP2_disk | D2448[16]
EP2_Polje_2Faza1_Tok01_16_med60_80 | DIGITAL | IOD_EP2_disk | D2464[16]
EP2_Polje_2Faza1_Tok17_32_med60_80 | DIGITAL | IOD_EP2_disk | D2480[16]
EP2_Polje_2Faza1_Tok33_42_med60_80 | DIGITAL | IOD_EP2_disk | D2496[16]
EP2_Polje_2Faza2_Tok01_16_med60_80 | DIGITAL | IOD_EP2_disk | D2512[16]
EP2_Polje_2Faza2_Tok17_32_med60_80 | DIGITAL | IOD_EP2_disk | D2528[16]
EP2_Polje_2Faza2_Tok33_42_med60_80 | DIGITAL | IOD_EP2_disk | D2544[16]
EP2_Polje_2Faza3_Tok01_16_med60_80 | DIGITAL | IOD_EP2_disk | D2560[16]
EP2_Polje_2Faza3_Tok17_32_med60_80 | DIGITAL | IOD_EP2_disk | D2576[16]
EP2_Polje_2Faza3_Tok33_42_med60_80 | DIGITAL | IOD_EP2_disk | D2592[16]
EP2_Polje_1Faza1_Tok01_16_med60_80 | DIGITAL | IOD_EP2_disk | D2608[16]
EP2_Polje_1Faza2_Tok01_16_med60_80 | DIGITAL | IOD_EP2_disk | D2634[16]
EP2Pulz1s | DIGITAL | IOD_EP2_disk | D3000
EP2_DanEnergCircE1K4_A | REAL | IOD_EP2_disk | R7286[30] | [5 empty] | ###.#
EP2_CasDDanEnergCircE1K4_A | INT | IOD_EP2_disk | I3060[30] | [5 empty] | ###.#
EP2_CasMDanEnergCircE1K4_A | INT | IOD_EP2_disk | I3090[30] | [5 empty] | ###.#
EP2_TedenEnergCircE1K4_A | REAL | IOD_EP2_disk | R7316[30] | [5 empty] | ###.#
EP2_CasDTedenEnergCircE1K4_A | INT | IOD_EP2_disk | I3150[30] | [5 empty] | ###.#
EP2_CasMTedenEnergCircE1K4_A | INT | IOD_EP2_disk | I3480[30] | [5 empty] | ###.#
EP2_MesecEnergCircE1K4_A | REAL | IOD_EP2_disk | R3746[30] | [5 empty] | ###.#
EP2_CasDMesecEnergCircE1K4_A | INT | IOD_EP2_disk | I3540[30] | [5 empty] | ###.#
EP2_CasMMesecEnergCircE1K4_A | INT | IOD_EP2_disk | I3570[30] | [5 empty] | ###.#
EP2_StSt_DanEnergCircE1K4_A | REAL | IOD_EP2_disk | R3776 | [5 empty] | ###.#
EP2_StSt_TedenEnergCircE1K4_A | REAL | IOD_EP2_disk | R3780 | [5 empty] | ###.#
EP2_StSt_MesecEnergCircE1K4_A | REAL | IOD_EP2_disk | R3784 | [5 empty] | ###.#
EP2_StStCasDDanEnergCircE1K4_A | INT | IOD_EP2_disk | I3606 | [5 empty] | ###.#
EP2_StStCasMDanEnergCircE1K4_A | INT | IOD_EP2_disk | I3608
EP2_StStCasDTedenEnergCircE1K4_A | INT | IOD_EP2_disk | I3610
EP2_StStCasMTedenEnergCircE1K4_A | INT | IOD_EP2_disk | I3612
EP2_StStCasDMesecEnergCircE1K4_A | INT | IOD_EP2_disk | I3614
EP2_StStCasMMesecEnergCircE1K4_A | INT | IOD_EP2_disk | I3616
EP2_PrviZagon | DIGITAL | IOD_EP2_disk | D3017
EP2_Prikaz_PMM_AA_med60in80 | DIGITAL | IOD_EP2_mem | D3018
EP2_Prikaz_PMM_AA_nad80 | DIGITAL | IOD_EP2_mem | D3019
EP2_Prikaz_PMM_BB_med60in80 | DIGITAL | IOD_EP2_mem | D3020
EP2_Prikaz_PMM_BB_nad80 | DIGITAL | IOD_EP2_mem | D3021
EP2_Prikaz_PMM_UC_med60in80 | DIGITAL | IOD_EP2_mem | D3022
EP2_Prikaz_PMM_UC_nad80 | DIGITAL | IOD_EP2_mem | D3023
AEP2_omogoci_sms | DIGITAL | IOD_EP2_disk | D3550[500]
BEP2_omogoci_sms | DIGITAL | IOD_EP2_disk | D4050[500]
CEP2_omogoci_sms | DIGITAL | IOD_EP2_disk | D4550[500]
DEP2_omogoci_sms | DIGITAL | IOD_EP2_disk | D5050[500]
EEP2_omogoci_sms | DIGITAL | IOD_EP2_disk | D5550[500]
FEP2_omogoci_sms | DIGITAL | IOD_EP2_disk | D6050[500]
EP2_ComSCADA_stevec1 | INT | IOD_EP2_mem | I6550
EP2_ComSCADA_stevec2 | INT | IOD_EP2_mem | I6552
EP2_PrikaziSP1 | DIGITAL | IOD_EP2_disk | D6553
EP2_PrikaziSP2 | DIGITAL | IOD_EP2_disk | D6554
EP2_PrikaziSP3 | DIGITAL | IOD_EP2_disk | D6555
EP2_PrikaziSP4 | DIGITAL | IOD_EP2_disk | D6556
EP2_PrikaziSP5 | DIGITAL | IOD_EP2_disk | D6557
EP2_PrikaziKlimat1 | DIGITAL | IOD_EP2_disk | D6558
EP2_PrikaziKlimat2 | DIGITAL | IOD_EP2_disk | D6559
EP2_PrikaziKlimat3 | DIGITAL | IOD_EP2_disk | D6560
EP2_ErrCommScada_omogoci | DIGITAL | IOD_EP2_disk | D6561
EP2_ErrComPanelPLC_omogoci | DIGITAL | IOD_EP2_disk | D6562
EP2_ErrComPort2_omogoci | DIGITAL | IOD_EP2_disk | D6563
EP2_ErrComPort3_omogoci | DIGITAL | IOD_EP2_disk | D6564
EP2_ErrComPort4_omogoci | DIGITAL | IOD_EP2_disk | D6565
EP2_ErrComUPS1_omogoci | DIGITAL | IOD_EP2_disk | D6566
EP2_ErrComUPS2_omogoci | DIGITAL | IOD_EP2_disk | D6567
EP2_ErrComPMM1_omogoci | DIGITAL | IOD_EP2_disk | D6568
EP2_ErrComPMM2_omogoci | DIGITAL | IOD_EP2_disk | D6569
EP2_ErrComPMM3_omogoci | DIGITAL | IOD_EP2_disk | D6570
EP2_ErrComCirc1_omogoci | DIGITAL | IOD_EP2_disk | D6571
EP2_ErrComKlima5_omogoci | DIGITAL | IOD_EP2_disk | D6572
EP2_ErrComKlima6_omogoci | DIGITAL | IOD_EP2_disk | D6573
EP2_PMM3OverCurrentBetw1_omogoci | DIGITAL | IOD_EP2_disk | D6574
EP2_PMM3OverCurrentBetw2_omogoci | DIGITAL | IOD_EP2_disk | D6575
EP2_PMM3OverCurrentBetw3_omogoci | DIGITAL | IOD_EP2_disk | D6576
EP2_PMM3OverCurrentOver1_omogoci | DIGITAL | IOD_EP2_disk | D6577
EP2_PMM3OverCurrentOver2_omogoci | DIGITAL | IOD_EP2_disk | D6578
EP2_PMM3OverCurrentOver3_omogoci | DIGITAL | IOD_EP2_disk | D6579
EP2_PMM2OverCurrentBetw1_omogoci | DIGITAL | IOD_EP2_disk | D6580
EP2_PMM2OverCurrentBetw2_omogoci | DIGITAL | IOD_EP2_disk | D6581
EP2_PMM2OverCurrentBetw3_omogoci | DIGITAL | IOD_EP2_disk | D6582
EP2_PMM2OverCurrentOver1_omogoci | DIGITAL | IOD_EP2_disk | D6583
EP2_PMM2OverCurrentOver2_omogoci | DIGITAL | IOD_EP2_disk | D6584
EP2_PMM2OverCurrentOver3_omogoci | DIGITAL | IOD_EP2_disk | D6585
EP2_PMM1OverCurrentBetw1_omogoci | DIGITAL | IOD_EP2_disk | D6586
EP2_PMM1OverCurrentBetw2_omogoci | DIGITAL | IOD_EP2_disk | D6587
EP2_PMM1OverCurrentOver1_omogoci | DIGITAL | IOD_EP2_disk | D6588
EP2_PMM1OverCurrentOver2_omogoci | DIGITAL | IOD_EP2_disk | D6589
EP2_PMM3OverVoltage_omogoci | DIGITAL | IOD_EP2_disk | D6590
EP2_PMM2OverVoltage_omogoci | DIGITAL | IOD_EP2_disk | D6591
EP2UPS1AlarmAwaitingPower_omog | DIGITAL | IOD_EP2_disk | D6592
EP2UPS1AlarmBypassBad_omog | DIGITAL | IOD_EP2_disk | D6593
EP2UPS1AlarmChargerFailed_omog | DIGITAL | IOD_EP2_disk | D6594
EP2UPS1AlarmCommunicationsLost_omog | DIGITAL | IOD_EP2_disk | D6595
EP2UPS1AlarmDepletedBattery_omog | DIGITAL | IOD_EP2_disk | D6596
EP2UPS1AlarmDiagnosticTestFailed_omog | DIGITAL | IOD_EP2_disk | D6597
EP2UPS1AlarmIzhodOffKotZahtevano_omog | DIGITAL | IOD_EP2_disk | D6598
EP2UPS1AlarmIzhodPreobremenjen_omog | DIGITAL | IOD_EP2_disk | D6599
EP2UPS1AlarmLowBattery_omog | DIGITAL | IOD_EP2_disk | D6600
EP2UPS1AlarmNapakaNaVarovalki_omog | DIGITAL | IOD_EP2_disk | D6601
EP2UPS1AlarmNapakaNaVentilatorju_omog | DIGITAL | IOD_EP2_disk | D6602
EP2UPS1AlarmOnBattery_omog | DIGITAL | IOD_EP2_disk | D6603
EP2UPS1AlarmOnBypass_omog | DIGITAL | IOD_EP2_disk | D6604
EP2UPS1AlarmShutdownImminent_omog | DIGITAL | IOD_EP2_disk | D6605
EP2UPS1AlarmShutdownPending_omog | DIGITAL | IOD_EP2_disk | D6606
EP2UPS1AlarmSlabaBaterija_omog | DIGITAL | IOD_EP2_disk | D6607
EP2UPS1AlarmSplosnaNapaka_omog | DIGITAL | IOD_EP2_disk | D6608
EP2UPS1AlarmStanjeIzhodaIzvenToleranc_omog | DIGITAL | IOD_EP2_disk | D6609
EP2UPS1AlarmStanjeVhodaIzvenToleranc_omog | DIGITAL | IOD_EP2_disk | D6610
EP2UPS1AlarmTemperaturaIzvenToleranc_omog | DIGITAL | IOD_EP2_disk | D6611
EP2UPS1AlarmTestInProgres_omog | DIGITAL | IOD_EP2_disk | D6612
EP2UPS1AlarmUPSIzhodOff_omog | DIGITAL | IOD_EP2_disk | D6613
EP2UPS1AlarmUPSOffKotZahtevano_omog | DIGITAL | IOD_EP2_disk | D6614
EP2UPS1AlarmUPSSystemOff_omog | DIGITAL | IOD_EP2_disk | D6615
EP2UPS1AlarmInverterError_omog | DIGITAL | IOD_EP2_disk | D6616
EP2UPS2AlarmAwaitingPower_omog | DIGITAL | IOD_EP2_disk | D6617
EP2UPS2AlarmBypassBad_omog | DIGITAL | IOD_EP2_disk | D6618
EP2UPS2AlarmChargerFailed_omog | DIGITAL | IOD_EP2_disk | D6619
EP2UPS2AlarmCommunicationsLost_omog | DIGITAL | IOD_EP2_disk | D6620
EP2UPS2AlarmDepletedBattery_omog | DIGITAL | IOD_EP2_disk | D6621
EP2UPS2AlarmDiagnosticTestFailed_omog | DIGITAL | IOD_EP2_disk | D6622
EP2UPS2AlarmIzhodOffKotZahtevano_omog | DIGITAL | IOD_EP2_disk | D6623
EP2UPS2AlarmIzhodPreobremenjen_omog | DIGITAL | IOD_EP2_disk | D6624
EP2UPS2AlarmLowBattery_omog | DIGITAL | IOD_EP2_disk | D6625
EP2UPS2AlarmNapakaNaVarovalki_omog | DIGITAL | IOD_EP2_disk | D6626
EP2UPS2AlarmNapakaNaVentilatorju_omog | DIGITAL | IOD_EP2_disk | D6627
EP2UPS2AlarmOnBattery_omog | DIGITAL | IOD_EP2_disk | D6628
EP2UPS2AlarmOnBypass_omog | DIGITAL | IOD_EP2_disk | D6629
EP2UPS2AlarmShutdownImminent_omog | DIGITAL | IOD_EP2_disk | D6630
EP2UPS2AlarmShutdownPending_omog | DIGITAL | IOD_EP2_disk | D6631
EP2UPS2AlarmSlabaBaterija_omog | DIGITAL | IOD_EP2_disk | D6632
EP2UPS2AlarmSplosnaNapaka_omog | DIGITAL | IOD_EP2_disk | D6633
EP2UPS2AlarmStanjeIzhodaIzvenToleranc_omog | DIGITAL | IOD_EP2_disk | D6634
EP2UPS2AlarmStanjeVhodaIzvenToleranc_omog | DIGITAL | IOD_EP2_disk | D6635
EP2UPS2AlarmTemperaturaIzvenToleranc_omog | DIGITAL | IOD_EP2_disk | D6636
EP2UPS2AlarmTestInProgres_omog | DIGITAL | IOD_EP2_disk | D6637
EP2UPS2AlarmUPSIzhodOff_omog | DIGITAL | IOD_EP2_disk | D6638
EP2UPS2AlarmUPSOffKotZahtevano_omog | DIGITAL | IOD_EP2_disk | D6639
EP2UPS2AlarmUPSSystemOff_omog | DIGITAL | IOD_EP2_disk | D6640
EP2UPS2AlarmInverterError_omog | DIGITAL | IOD_EP2_disk | D6641
EP2_DI_Q2_Rezerva_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6642
EP2_DI_Q5_OdcKlima1_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6643
EP2_DI_Q6_OdcKlima2_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6644
EP2_DI_Q7_OdcKlima3_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6645
EP2_DI_Q8_OdcKlima4_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6646
EP2_DI_Q9_OdcKlima5_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6647
EP2_DI_Q10_OdcKlima6_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6648
EP2_DI_Q25_OdcUpsA_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6649
EP2_DI_Q26_OdcByA_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6650
EP2_DI_Q27_OdcByUpsA_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6651
EP2_DI_Q28_OdcUpsB_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6652
EP2_DI_Q29_OdcByB_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6653
EP2_DI_Q30_OdcByUpsB_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6654
EP2_DI_Klima5_ERR_omogoci | DIGITAL | IOD_EP2_disk | D6655
EP2_DI_Klima6_ERR_omogoci | DIGITAL | IOD_EP2_disk | D6656
EP2_DI_KlimaSplit1_ERR_omogoci | DIGITAL | IOD_EP2_disk | D6657
EP2_DI_UpsA_ON_omogoci | DIGITAL | IOD_EP2_disk | D6658
EP2_DI_UpsA_ERR_omogoci | DIGITAL | IOD_EP2_disk | D6659
EP2_DI_UpsB_ON_omogoci | DIGITAL | IOD_EP2_disk | D6660
EP2_DI_UpsB_ERR_omogoci | DIGITAL | IOD_EP2_disk | D6661
EP2_DI_UPS_Alarm_omogoci | DIGITAL | IOD_EP2_disk | D6662
EP2_DI_UPS_BatNacin_omogoci | DIGITAL | IOD_EP2_disk | D6663
EP2_DI_UPS_Polnjenje_omogoci | DIGITAL | IOD_EP2_disk | D6664
EP2_DI_RazlitjeVodeK5K6_omogoci | DIGITAL | IOD_EP2_disk | D6665
EP2_SetDateTimeError_omogoci | DIGITAL | IOD_EP2_disk | D6666
EP2_TempTSprevisoka1_omogoci | DIGITAL | IOD_EP2_disk | D6667
EP2_NapakaSenzorTemp1_omogoci | DIGITAL | IOD_EP2_disk | D6668
EP2_NapakaSenzorVlaga1_omogoci | DIGITAL | IOD_EP2_disk | D6669
EP2_SlabaBaterijaPLC_A1_omogoci | DIGITAL | IOD_EP2_disk | D6670
EP2_Klima1_GeneralAlarm_omogoci | DIGITAL | IOD_EP2_disk | D6671
EP2_Klima1_AlarmKompresor1_omogoci | DIGITAL | IOD_EP2_disk | D6672
EP2_Klima1_AlarmKompresor2_omogoci | DIGITAL | IOD_EP2_disk | D6673
EP2_Klima1_NizekPritiskKompresor1_omogoci | DIGITAL | IOD_EP2_disk | D6674
EP2_Klima1_NizekPritiskKompresor2_omogoci | DIGITAL | IOD_EP2_disk | D6675
EP2_Klima1_NapakaPriPretokuZraka_omogoci | DIGITAL | IOD_EP2_disk | D6676
EP2_Klima1_FenThermalCutout_omogoci | DIGITAL | IOD_EP2_disk | D6677
EP2_Klima1_ThermalCutoutHeater1_omogoci | DIGITAL | IOD_EP2_disk | D6678
EP2_Klima1_ThermalCutoutHeater2_omogoci | DIGITAL | IOD_EP2_disk | D6679
EP2_Klima1_PozarniAlarm_omogoci | DIGITAL | IOD_EP2_disk | D6680
EP2_Klima1_ZamasenFilter_omogoci | DIGITAL | IOD_EP2_disk | D6681
EP2_Klima1_VisokaTempVProstoru_omogoci | DIGITAL | IOD_EP2_disk | D6682
EP2_Klima1_NizkaTempVProstoru_omogoci | DIGITAL | IOD_EP2_disk | D6683
EP2_Klima1_VisokaVlaznost_omogoci | DIGITAL | IOD_EP2_disk | D6684
EP2_Klima1_NizkaVlaznost_omogoci | DIGITAL | IOD_EP2_disk | D6685
EP2_Klima1_Kompresor1naMejiObrUr_omogoci | DIGITAL | IOD_EP2_disk | D6686
EP2_Klima1_Kompresor2naMejiObrUr_omogoci | DIGITAL | IOD_EP2_disk | D6687
EP2_Klima1_VentilatorNaMejiObrU_omogoci | DIGITAL | IOD_EP2_disk | D6688
EP2_Klima1_VisokaTempPovratneVod_omogoci | DIGITAL | IOD_EP2_disk | D6689
EP2_Klima1_NizkaTempPovratneVode_omogoci | DIGITAL | IOD_EP2_disk | D6690
EP2_Klima1_NapakaSenzorTempPros_omogoci | DIGITAL | IOD_EP2_disk | D6691
EP2_Klima1_NapakaSenzorTempIzih_omogoci | DIGITAL | IOD_EP2_disk | D6692
EP2_Klima1_NapakaSenzorPovratVod_omogoci | DIGITAL | IOD_EP2_disk | D6693
EP2_Klima1_NapakaSenzorZunanjeTe_omogoci | DIGITAL | IOD_EP2_disk | D6694
EP2_Klima1_NapakaSenzorVlaznosti_omogoci | DIGITAL | IOD_EP2_disk | D6695
EP2_Klima1_FaultyEPROM_omogoci | DIGITAL | IOD_EP2_disk | D6696
EP2_Klima1_StoppedByAlarms_omogoci | DIGITAL | IOD_EP2_disk | D6697
EP2_Klima1_VisokTokVVlazilcu_omogoci | DIGITAL | IOD_EP2_disk | D6698
EP2_Klima1_NiVodeVVlazilcu_omogoci | DIGITAL | IOD_EP2_disk | D6699
EP2_Klima1_NiTokaVVlazilcu_omogoci | DIGITAL | IOD_EP2_disk | D6700
EP2_Klima1_RocniIzklop_omogoci | DIGITAL | IOD_EP2_disk | D6701
EP2_Klima2_GeneralAlarm_omogoci | DIGITAL | IOD_EP2_disk | D6702
EP2_Klima2_AlarmKompresor1_omogoci | DIGITAL | IOD_EP2_disk | D6703
EP2_Klima2_AlarmKompresor2_omogoci | DIGITAL | IOD_EP2_disk | D6704
EP2_Klima2_NizekPritiskKompresor1_omogoci | DIGITAL | IOD_EP2_disk | D6705
EP2_Klima2_NizekPritiskKompresor2_omogoci | DIGITAL | IOD_EP2_disk | D6706
EP2_Klima2_NapakaPriPretokuZraka_omogoci | DIGITAL | IOD_EP2_disk | D6707
EP2_Klima2_FenThermalCutout_omogoci | DIGITAL | IOD_EP2_disk | D6708
EP2_Klima2_ThermalCutoutHeater1_omogoci | DIGITAL | IOD_EP2_disk | D6709
EP2_Klima2_ThermalCutoutHeater2_omogoci | DIGITAL | IOD_EP2_disk | D6710
EP2_Klima2_PozarniAlarm_omogoci | DIGITAL | IOD_EP2_disk | D6711
EP2_Klima2_ZamasenFilter_omogoci | DIGITAL | IOD_EP2_disk | D6712
EP2_Klima2_VisokaTempVProstoru_omogoci | DIGITAL | IOD_EP2_disk | D6713
EP2_Klima2_NizkaTempVProstoru_omogoci | DIGITAL | IOD_EP2_disk | D6714
EP2_Klima2_VisokaVlaznost_omogoci | DIGITAL | IOD_EP2_disk | D6715
EP2_Klima2_NizkaVlaznost_omogoci | DIGITAL | IOD_EP2_disk | D6716
EP2_Klima2_Kompresor1naMejiObrUr_omogoci | DIGITAL | IOD_EP2_disk | D6717
EP2_Klima2_Kompresor2naMejiObrUr_omogoci | DIGITAL | IOD_EP2_disk | D6718
EP2_Klima2_VentilatorNaMejiObrU_omogoci | DIGITAL | IOD_EP2_disk | D6719
EP2_Klima2_VisokaTempPovratneVod_omogoci | DIGITAL | IOD_EP2_disk | D6720
EP2_Klima2_NizkaTempPovratneVode_omogoci | DIGITAL | IOD_EP2_disk | D6721
EP2_Klima2_NapakaSenzorTempPros_omogoci | DIGITAL | IOD_EP2_disk | D6722
EP2_Klima2_NapakaSenzorPovratVod_omogoci | DIGITAL | IOD_EP2_disk | D6723
EP2_Klima2_NapakaSenzorZunanjeTe_omogoci | DIGITAL | IOD_EP2_disk | D6724
EP2_Klima2_NapakaSenzorTempIzpih_omogoci | DIGITAL | IOD_EP2_disk | D6725
EP2_Klima2_NapakaSenzorVlaznosti_omogoci | DIGITAL | IOD_EP2_disk | D6726
EP2_Klima2_FaultyEPROM_omogoci | DIGITAL | IOD_EP2_disk | D6727
EP2_Klima2_StoppedByAlarms_omogoci | DIGITAL | IOD_EP2_disk | D6728
EP2_Klima2_VisokTokVVlazilcu_omogoci | DIGITAL | IOD_EP2_disk | D6729
EP2_Klima2_NiVodeVVlazilcu_omogoci | DIGITAL | IOD_EP2_disk | D6730
EP2_Klima2_NiTokaVVlazilcu_omogoci | DIGITAL | IOD_EP2_disk | D6731
EP2_Klima2_RocniIzklop_omogoci | DIGITAL | IOD_EP2_disk | D6732
EP2_PMM_3_Faza1_Tok01_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6733
EP2_PMM_3_Faza1_Tok02_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6734
EP2_PMM_3_Faza1_Tok03_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6735
EP2_PMM_3_Faza1_Tok04_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6736
EP2_PMM_3_Faza1_Tok05_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6737
EP2_PMM_3_Faza1_Tok06_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6738
EP2_PMM_3_Faza1_Tok07_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6739
EP2_PMM_3_Faza1_Tok08_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6740
EP2_PMM_3_Faza1_Tok09_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6741
EP2_PMM_3_Faza1_Tok10_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6742
EP2_PMM_3_Faza1_Tok11_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6743
EP2_PMM_3_Faza1_Tok12_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6744
EP2_PMM_3_Faza1_Tok13_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6745
EP2_PMM_3_Faza1_Tok14_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6746
EP2_PMM_3_Faza1_Tok15_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6747
EP2_PMM_3_Faza1_Tok16_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6748
EP2_PMM_3_Faza1_Tok17_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6749
EP2_PMM_3_Faza1_Tok18_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6750
EP2_PMM_3_Faza1_Tok19_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6751
EP2_PMM_3_Faza1_Tok20_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6752
EP2_PMM_3_Faza1_Tok21_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6753
EP2_PMM_3_Faza1_Tok22_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6754
EP2_PMM_3_Faza1_Tok23_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6755
EP2_PMM_3_Faza1_Tok24_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6756
EP2_PMM_3_Faza1_Tok25_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6757
EP2_PMM_3_Faza1_Tok26_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6758
EP2_PMM_3_Faza1_Tok27_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6759
EP2_PMM_3_Faza1_Tok28_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6760
EP2_PMM_3_Faza1_Tok29_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6761
EP2_PMM_3_Faza1_Tok30_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6762
EP2_PMM_3_Faza1_Tok31_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6763
EP2_PMM_3_Faza1_Tok32_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6764
EP2_PMM_3_Faza1_Tok33_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6765
EP2_PMM_3_Faza1_Tok34_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6766
EP2_PMM_3_Faza1_Tok35_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6767
EP2_PMM_3_Faza1_Tok36_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6768
EP2_PMM_3_Faza1_Tok37_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6769
EP2_PMM_3_Faza1_Tok38_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6770
EP2_PMM_3_Faza1_Tok39_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6771
EP2_PMM_3_Faza1_Tok40_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6772
EP2_PMM_3_Faza1_Tok41_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6773
EP2_PMM_3_Faza1_Tok42_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6774
EP2_PMM_3_Faza2_Tok01_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6775
EP2_PMM_3_Faza2_Tok02_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6776
EP2_PMM_3_Faza2_Tok03_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6777
EP2_PMM_3_Faza2_Tok04_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6778
EP2_PMM_3_Faza2_Tok05_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6779
EP2_PMM_3_Faza2_Tok06_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6780
EP2_PMM_3_Faza2_Tok07_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6781
EP2_PMM_3_Faza2_Tok08_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6782
EP2_PMM_3_Faza2_Tok09_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6783
EP2_PMM_3_Faza2_Tok10_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6784
EP2_PMM_3_Faza2_Tok11_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6785
EP2_PMM_3_Faza2_Tok12_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6786
EP2_PMM_3_Faza2_Tok13_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6787
EP2_PMM_3_Faza2_Tok14_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6788
EP2_PMM_3_Faza2_Tok15_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6789
EP2_PMM_3_Faza2_Tok16_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6790
EP2_PMM_3_Faza2_Tok17_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6791
EP2_PMM_3_Faza2_Tok18_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6792
EP2_PMM_3_Faza2_Tok19_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6793
EP2_PMM_3_Faza2_Tok20_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6794
EP2_PMM_3_Faza2_Tok21_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6795
EP2_PMM_3_Faza2_Tok22_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6796
EP2_PMM_3_Faza2_Tok23_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6797
EP2_PMM_3_Faza2_Tok24_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6798
EP2_PMM_3_Faza2_Tok25_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6799
EP2_PMM_3_Faza2_Tok26_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6800
EP2_PMM_3_Faza2_Tok27_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6801
EP2_PMM_3_Faza2_Tok28_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6802
EP2_PMM_3_Faza2_Tok29_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6803
EP2_PMM_3_Faza2_Tok30_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6804
EP2_PMM_3_Faza2_Tok31_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6805
EP2_PMM_3_Faza2_Tok32_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6806
EP2_PMM_3_Faza2_Tok33_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6807
EP2_PMM_3_Faza2_Tok34_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6808
EP2_PMM_3_Faza2_Tok35_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6809
EP2_PMM_3_Faza2_Tok36_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6810
EP2_PMM_3_Faza2_Tok37_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6811
EP2_PMM_3_Faza2_Tok38_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6812
EP2_PMM_3_Faza2_Tok39_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6813
EP2_PMM_3_Faza2_Tok40_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6814
EP2_PMM_3_Faza2_Tok41_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6815
EP2_PMM_3_Faza2_Tok42_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6816
EP2_PMM_3_Faza3_Tok01_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6817
EP2_PMM_3_Faza3_Tok02_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6818
EP2_PMM_3_Faza3_Tok03_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6819
EP2_PMM_3_Faza3_Tok04_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6820
EP2_PMM_3_Faza3_Tok05_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6821
EP2_PMM_3_Faza3_Tok06_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6822
EP2_PMM_3_Faza3_Tok07_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6823
EP2_PMM_3_Faza3_Tok08_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6824
EP2_PMM_3_Faza3_Tok09_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6825
EP2_PMM_3_Faza3_Tok10_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6826
EP2_PMM_3_Faza3_Tok11_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6827
EP2_PMM_3_Faza3_Tok12_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6828
EP2_PMM_3_Faza3_Tok13_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6829
EP2_PMM_3_Faza3_Tok14_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6830
EP2_PMM_3_Faza3_Tok15_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6831
EP2_PMM_3_Faza3_Tok16_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6832
EP2_PMM_3_Faza3_Tok17_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6833
EP2_PMM_3_Faza3_Tok18_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6834
EP2_PMM_3_Faza3_Tok19_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6835
EP2_PMM_3_Faza3_Tok20_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6836
EP2_PMM_3_Faza3_Tok21_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6837
EP2_PMM_3_Faza3_Tok22_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6838
EP2_PMM_3_Faza3_Tok23_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6839
EP2_PMM_3_Faza3_Tok24_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6840
EP2_PMM_3_Faza3_Tok25_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6841
EP2_PMM_3_Faza3_Tok26_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6842
EP2_PMM_3_Faza3_Tok27_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6843
EP2_PMM_3_Faza3_Tok28_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6844
EP2_PMM_3_Faza3_Tok29_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6845
EP2_PMM_3_Faza3_Tok30_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6846
EP2_PMM_3_Faza3_Tok31_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6847
EP2_PMM_3_Faza3_Tok32_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6848
EP2_PMM_3_Faza3_Tok33_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6849
EP2_PMM_3_Faza3_Tok34_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6850
EP2_PMM_3_Faza3_Tok35_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6851
EP2_PMM_3_Faza3_Tok36_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6852
EP2_PMM_3_Faza3_Tok37_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6853
EP2_PMM_3_Faza3_Tok38_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6854
EP2_PMM_3_Faza3_Tok39_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6855
EP2_PMM_3_Faza3_Tok40_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6856
EP2_PMM_3_Faza3_Tok41_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6857
EP2_PMM_3_Faza3_Tok42_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6858
EP2_PMM_3_Faza1_Tok01_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6859
EP2_PMM_3_Faza1_Tok02_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6860
EP2_PMM_3_Faza1_Tok03_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6861
EP2_PMM_3_Faza1_Tok04_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6862
EP2_PMM_3_Faza1_Tok05_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6863
EP2_PMM_3_Faza1_Tok06_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6864
EP2_PMM_3_Faza1_Tok07_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6865
EP2_PMM_3_Faza1_Tok08_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6866
EP2_PMM_3_Faza1_Tok09_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6867
EP2_PMM_3_Faza1_Tok10_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6868
EP2_PMM_3_Faza1_Tok11_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6869
EP2_PMM_3_Faza1_Tok12_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6870
EP2_PMM_3_Faza1_Tok13_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6871
EP2_PMM_3_Faza1_Tok14_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6872
EP2_PMM_3_Faza1_Tok15_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6873
EP2_PMM_3_Faza1_Tok16_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6874
EP2_PMM_3_Faza1_Tok17_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6875
EP2_PMM_3_Faza1_Tok18_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6876
EP2_PMM_3_Faza1_Tok19_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6877
EP2_PMM_3_Faza1_Tok20_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6878
EP2_PMM_3_Faza1_Tok21_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6879
EP2_PMM_3_Faza1_Tok22_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6880
EP2_PMM_3_Faza1_Tok23_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6881
EP2_PMM_3_Faza1_Tok24_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6882
EP2_PMM_3_Faza1_Tok25_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6883
EP2_PMM_3_Faza1_Tok26_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6884
EP2_PMM_3_Faza1_Tok27_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6885
EP2_PMM_3_Faza1_Tok28_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6886
EP2_PMM_3_Faza1_Tok29_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6887
EP2_PMM_3_Faza1_Tok30_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6888
EP2_PMM_3_Faza1_Tok31_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6889
EP2_PMM_3_Faza1_Tok32_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6890
EP2_PMM_3_Faza1_Tok33_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6891
EP2_PMM_3_Faza1_Tok34_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6892
EP2_PMM_3_Faza1_Tok35_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6893
EP2_PMM_3_Faza1_Tok36_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6894
EP2_PMM_3_Faza1_Tok37_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6895
EP2_PMM_3_Faza1_Tok38_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6896
EP2_PMM_3_Faza1_Tok39_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6897
EP2_PMM_3_Faza1_Tok40_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6898
EP2_PMM_3_Faza1_Tok41_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6899
EP2_PMM_3_Faza1_Tok42_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6900
EP2_PMM_3_Faza2_Tok01_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6901
EP2_PMM_3_Faza2_Tok02_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6902
EP2_PMM_3_Faza2_Tok03_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6903
EP2_PMM_3_Faza2_Tok04_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6904
EP2_PMM_3_Faza2_Tok05_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6905
EP2_PMM_3_Faza2_Tok06_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6906
EP2_PMM_3_Faza2_Tok07_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6907
EP2_PMM_3_Faza2_Tok08_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6908
EP2_PMM_3_Faza2_Tok09_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6909
EP2_PMM_3_Faza2_Tok10_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6910
EP2_PMM_3_Faza2_Tok11_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6911
EP2_PMM_3_Faza2_Tok12_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6912
EP2_PMM_3_Faza2_Tok13_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6913
EP2_PMM_3_Faza2_Tok14_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6914
EP2_PMM_3_Faza2_Tok15_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6915
EP2_PMM_3_Faza2_Tok16_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6916
EP2_PMM_3_Faza2_Tok17_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6917
EP2_PMM_3_Faza2_Tok18_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6918
EP2_PMM_3_Faza2_Tok19_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6919
EP2_PMM_3_Faza2_Tok20_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6920
EP2_PMM_3_Faza2_Tok21_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6921
EP2_PMM_3_Faza2_Tok22_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6922
EP2_PMM_3_Faza2_Tok23_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6923
EP2_PMM_3_Faza2_Tok24_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6924
EP2_PMM_3_Faza2_Tok25_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6925
EP2_PMM_3_Faza2_Tok26_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6926
EP2_PMM_3_Faza2_Tok27_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6927
EP2_PMM_3_Faza2_Tok28_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6928
EP2_PMM_3_Faza2_Tok29_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6929
EP2_PMM_3_Faza2_Tok30_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6930
EP2_PMM_3_Faza2_Tok31_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6931
EP2_PMM_3_Faza2_Tok32_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6932
EP2_PMM_3_Faza2_Tok33_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6933
EP2_PMM_3_Faza2_Tok34_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6934
EP2_PMM_3_Faza2_Tok35_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6935
EP2_PMM_3_Faza2_Tok36_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6936
EP2_PMM_3_Faza2_Tok37_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6937
EP2_PMM_3_Faza2_Tok38_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6938
EP2_PMM_3_Faza2_Tok39_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6939
EP2_PMM_3_Faza2_Tok40_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6940
EP2_PMM_3_Faza2_Tok41_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6941
EP2_PMM_3_Faza2_Tok42_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6942
EP2_PMM_3_Faza3_Tok01_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6943
EP2_PMM_3_Faza3_Tok02_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6944
EP2_PMM_3_Faza3_Tok03_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6945
EP2_PMM_3_Faza3_Tok04_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6946
EP2_PMM_3_Faza3_Tok05_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6947
EP2_PMM_3_Faza3_Tok06_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6948
EP2_PMM_3_Faza3_Tok07_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6949
EP2_PMM_3_Faza3_Tok08_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6950
EP2_PMM_3_Faza3_Tok09_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6951
EP2_PMM_3_Faza3_Tok10_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6952
EP2_PMM_3_Faza3_Tok11_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6953
EP2_PMM_3_Faza3_Tok12_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6954
EP2_PMM_3_Faza3_Tok13_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6955
EP2_PMM_3_Faza3_Tok14_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6956
EP2_PMM_3_Faza3_Tok15_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6957
EP2_PMM_3_Faza3_Tok16_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6958
EP2_PMM_3_Faza3_Tok17_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6959
EP2_PMM_3_Faza3_Tok18_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6960
EP2_PMM_3_Faza3_Tok19_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6961
EP2_PMM_3_Faza3_Tok20_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6962
EP2_PMM_3_Faza3_Tok21_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6963
EP2_PMM_3_Faza3_Tok22_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6964
EP2_PMM_3_Faza3_Tok23_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6965
EP2_PMM_3_Faza3_Tok24_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6966
EP2_PMM_3_Faza3_Tok25_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6967
EP2_PMM_3_Faza3_Tok26_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6968
EP2_PMM_3_Faza3_Tok27_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6969
EP2_PMM_3_Faza3_Tok28_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6970
EP2_PMM_3_Faza3_Tok29_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6971
EP2_PMM_3_Faza3_Tok30_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6972
EP2_PMM_3_Faza3_Tok31_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6973
EP2_PMM_3_Faza3_Tok32_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6974
EP2_PMM_3_Faza3_Tok33_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6975
EP2_PMM_3_Faza3_Tok34_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6976
EP2_PMM_3_Faza3_Tok35_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6977
EP2_PMM_3_Faza3_Tok36_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6978
EP2_PMM_3_Faza3_Tok37_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6979
EP2_PMM_3_Faza3_Tok38_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6980
EP2_PMM_3_Faza3_Tok39_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6981
EP2_PMM_3_Faza3_Tok40_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6982
EP2_PMM_3_Faza3_Tok41_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6983
EP2_PMM_3_Faza3_Tok42_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6984
EP2_PMM_2_Faza1_Tok01_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6985
EP2_PMM_2_Faza1_Tok02_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6986
EP2_PMM_2_Faza1_Tok03_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6987
EP2_PMM_2_Faza1_Tok04_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6988
EP2_PMM_2_Faza1_Tok05_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6989
EP2_PMM_2_Faza1_Tok06_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6990
EP2_PMM_2_Faza1_Tok07_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6991
EP2_PMM_2_Faza1_Tok08_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6992
EP2_PMM_2_Faza1_Tok09_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6993
EP2_PMM_2_Faza1_Tok10_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6994
EP2_PMM_2_Faza1_Tok11_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6995
EP2_PMM_2_Faza1_Tok12_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6996
EP2_PMM_2_Faza1_Tok13_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6997
EP2_PMM_2_Faza1_Tok14_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6998
EP2_PMM_2_Faza1_Tok15_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6999
EP2_PMM_2_Faza1_Tok16_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7000
EP2_PMM_2_Faza1_Tok17_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7001
EP2_PMM_2_Faza1_Tok18_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7002
EP2_PMM_2_Faza1_Tok19_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7003
EP2_PMM_2_Faza1_Tok20_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7004
EP2_PMM_2_Faza1_Tok21_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7005
EP2_PMM_2_Faza1_Tok22_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7006
EP2_PMM_2_Faza1_Tok23_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7007
EP2_PMM_2_Faza1_Tok24_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7008
EP2_PMM_2_Faza1_Tok25_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7009
EP2_PMM_2_Faza1_Tok26_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7010
EP2_PMM_2_Faza1_Tok27_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7011
EP2_PMM_2_Faza1_Tok28_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7012
EP2_PMM_2_Faza1_Tok29_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7013
EP2_PMM_2_Faza1_Tok30_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7014
EP2_PMM_2_Faza1_Tok31_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7015
EP2_PMM_2_Faza1_Tok32_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7016
EP2_PMM_2_Faza1_Tok33_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7017
EP2_PMM_2_Faza1_Tok34_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7018
EP2_PMM_2_Faza1_Tok35_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7019
EP2_PMM_2_Faza1_Tok36_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7020
EP2_PMM_2_Faza1_Tok37_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7021
EP2_PMM_2_Faza1_Tok38_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7022
EP2_PMM_2_Faza1_Tok39_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7023
EP2_PMM_2_Faza1_Tok40_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7024
EP2_PMM_2_Faza1_Tok41_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7025
EP2_PMM_2_Faza1_Tok42_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7026
EP2_PMM_2_Faza2_Tok01_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7027
EP2_PMM_2_Faza2_Tok02_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7028
EP2_PMM_2_Faza2_Tok03_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7029
EP2_PMM_2_Faza2_Tok04_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7030
EP2_PMM_2_Faza2_Tok05_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7031
EP2_PMM_2_Faza2_Tok06_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7032
EP2_PMM_2_Faza2_Tok07_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7033
EP2_PMM_2_Faza2_Tok08_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7034
EP2_PMM_2_Faza2_Tok09_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7035
EP2_PMM_2_Faza2_Tok10_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7036
EP2_PMM_2_Faza2_Tok11_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7037
EP2_PMM_2_Faza2_Tok12_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7038
EP2_PMM_2_Faza2_Tok13_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7039
EP2_PMM_2_Faza2_Tok14_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7040
EP2_PMM_2_Faza2_Tok15_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7041
EP2_PMM_2_Faza2_Tok16_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7042
EP2_PMM_2_Faza2_Tok17_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7043
EP2_PMM_2_Faza2_Tok18_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7044
EP2_PMM_2_Faza2_Tok19_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7045
EP2_PMM_2_Faza2_Tok20_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7046
EP2_PMM_2_Faza2_Tok21_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7047
EP2_PMM_2_Faza2_Tok22_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7048
EP2_PMM_2_Faza2_Tok23_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7049
EP2_PMM_2_Faza2_Tok24_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7050
EP2_PMM_2_Faza2_Tok25_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7051
EP2_PMM_2_Faza2_Tok26_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7052
EP2_PMM_2_Faza2_Tok27_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7053
EP2_PMM_2_Faza2_Tok28_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7054
EP2_PMM_2_Faza2_Tok29_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7055
EP2_PMM_2_Faza2_Tok30_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7056
EP2_PMM_2_Faza2_Tok31_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7057
EP2_PMM_2_Faza2_Tok32_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7058
EP2_PMM_2_Faza2_Tok33_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7059
EP2_PMM_2_Faza2_Tok34_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7060
EP2_PMM_2_Faza2_Tok35_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7061
EP2_PMM_2_Faza2_Tok36_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7062
EP2_PMM_2_Faza2_Tok37_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7063
EP2_PMM_2_Faza2_Tok38_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7064
EP2_PMM_2_Faza2_Tok39_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7065
EP2_PMM_2_Faza2_Tok40_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7066
EP2_PMM_2_Faza2_Tok41_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7067
EP2_PMM_2_Faza2_Tok42_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7068
EP2_PMM_2_Faza3_Tok01_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7069
EP2_PMM_2_Faza3_Tok02_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7070
EP2_PMM_2_Faza3_Tok03_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7071
EP2_PMM_2_Faza3_Tok04_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7072
EP2_PMM_2_Faza3_Tok05_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7073
EP2_PMM_2_Faza3_Tok06_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7074
EP2_PMM_2_Faza3_Tok07_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7075
EP2_PMM_2_Faza3_Tok08_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7076
EP2_PMM_2_Faza3_Tok09_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7077
EP2_PMM_2_Faza3_Tok10_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7078
EP2_PMM_2_Faza3_Tok11_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7079
EP2_PMM_2_Faza3_Tok12_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7080
EP2_PMM_2_Faza3_Tok13_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7081
EP2_PMM_2_Faza3_Tok14_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7082
EP2_PMM_2_Faza3_Tok15_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7083
EP2_PMM_2_Faza3_Tok16_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7084
EP2_PMM_2_Faza3_Tok17_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7085
EP2_PMM_2_Faza3_Tok18_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7086
EP2_PMM_2_Faza3_Tok19_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7087
EP2_PMM_2_Faza3_Tok20_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7088
EP2_PMM_2_Faza3_Tok21_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7089
EP2_PMM_2_Faza3_Tok22_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7090
EP2_PMM_2_Faza3_Tok23_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7091
EP2_PMM_2_Faza3_Tok24_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7092
EP2_PMM_2_Faza3_Tok25_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7093
EP2_PMM_2_Faza3_Tok26_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7094
EP2_PMM_2_Faza3_Tok27_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7095
EP2_PMM_2_Faza3_Tok28_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7096
EP2_PMM_2_Faza3_Tok29_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7097
EP2_PMM_2_Faza3_Tok30_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7098
EP2_PMM_2_Faza3_Tok31_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7099
EP2_PMM_2_Faza3_Tok32_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7100
EP2_PMM_2_Faza3_Tok33_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7101
EP2_PMM_2_Faza3_Tok34_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7102
EP2_PMM_2_Faza3_Tok35_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7103
EP2_PMM_2_Faza3_Tok36_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7104
EP2_PMM_2_Faza3_Tok37_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7105
EP2_PMM_2_Faza3_Tok38_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7106
EP2_PMM_2_Faza3_Tok39_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7107
EP2_PMM_2_Faza3_Tok40_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7108
EP2_PMM_2_Faza3_Tok41_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7109
EP2_PMM_2_Faza3_Tok42_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7110
EP2_PMM_2_Faza1_Tok01_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7111
EP2_PMM_2_Faza1_Tok02_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7112
EP2_PMM_2_Faza1_Tok03_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7113
EP2_PMM_2_Faza1_Tok04_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7114
EP2_PMM_2_Faza1_Tok05_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7115
EP2_PMM_2_Faza1_Tok06_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7116
EP2_PMM_2_Faza1_Tok07_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7117
EP2_PMM_2_Faza1_Tok08_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7118
EP2_PMM_2_Faza1_Tok09_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7119
EP2_PMM_2_Faza1_Tok10_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7120
EP2_PMM_2_Faza1_Tok11_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7121
EP2_PMM_2_Faza1_Tok12_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7122
EP2_PMM_2_Faza1_Tok13_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7123
EP2_PMM_2_Faza1_Tok14_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7124
EP2_PMM_2_Faza1_Tok15_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7125
EP2_PMM_2_Faza1_Tok16_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7126
EP2_PMM_2_Faza1_Tok17_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7127
EP2_PMM_2_Faza1_Tok18_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7128
EP2_PMM_2_Faza1_Tok19_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7129
EP2_PMM_2_Faza1_Tok20_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7130
EP2_PMM_2_Faza1_Tok21_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7131
EP2_PMM_2_Faza1_Tok22_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7132
EP2_PMM_2_Faza1_Tok23_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7133
EP2_PMM_2_Faza1_Tok24_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7134
EP2_PMM_2_Faza1_Tok25_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7135
EP2_PMM_2_Faza1_Tok26_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7136
EP2_PMM_2_Faza1_Tok27_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7137
EP2_PMM_2_Faza1_Tok28_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7138
EP2_PMM_2_Faza1_Tok29_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7139
EP2_PMM_2_Faza1_Tok30_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7140
EP2_PMM_2_Faza1_Tok31_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7141
EP2_PMM_2_Faza1_Tok32_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7142
EP2_PMM_2_Faza1_Tok33_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7143
EP2_PMM_2_Faza1_Tok34_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7144
EP2_PMM_2_Faza1_Tok35_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7145
EP2_PMM_2_Faza1_Tok36_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7146
EP2_PMM_2_Faza1_Tok37_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7147
EP2_PMM_2_Faza1_Tok38_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7148
EP2_PMM_2_Faza1_Tok39_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7149
EP2_PMM_2_Faza1_Tok40_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7150
EP2_PMM_2_Faza1_Tok41_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7151
EP2_PMM_2_Faza1_Tok42_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7152
EP2_PMM_2_Faza2_Tok01_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7153
EP2_PMM_2_Faza2_Tok02_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7154
EP2_PMM_2_Faza2_Tok03_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7155
EP2_PMM_2_Faza2_Tok04_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7156
EP2_PMM_2_Faza2_Tok05_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7157
EP2_PMM_2_Faza2_Tok06_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7158
EP2_PMM_2_Faza2_Tok07_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7159
EP2_PMM_2_Faza2_Tok08_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7160
EP2_PMM_2_Faza2_Tok09_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7161
EP2_PMM_2_Faza2_Tok10_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7162
EP2_PMM_2_Faza2_Tok11_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7163
EP2_PMM_2_Faza2_Tok12_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7164
EP2_PMM_2_Faza2_Tok13_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7165
EP2_PMM_2_Faza2_Tok14_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7166
EP2_PMM_2_Faza2_Tok15_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7167
EP2_PMM_2_Faza2_Tok16_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7168
EP2_PMM_2_Faza2_Tok17_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7169
EP2_PMM_2_Faza2_Tok18_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7170
EP2_PMM_2_Faza2_Tok19_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7171
EP2_PMM_2_Faza2_Tok20_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7172
EP2_PMM_2_Faza2_Tok21_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7173
EP2_PMM_2_Faza2_Tok22_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7174
EP2_PMM_2_Faza2_Tok23_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7175
EP2_PMM_2_Faza2_Tok24_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7176
EP2_PMM_2_Faza2_Tok25_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7177
EP2_PMM_2_Faza2_Tok26_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7178
EP2_PMM_2_Faza2_Tok27_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7179
EP2_PMM_2_Faza2_Tok28_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7180
EP2_PMM_2_Faza2_Tok29_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7181
EP2_PMM_2_Faza2_Tok30_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7182
EP2_PMM_2_Faza2_Tok31_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7183
EP2_PMM_2_Faza2_Tok32_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7184
EP2_PMM_2_Faza2_Tok33_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7185
EP2_PMM_2_Faza2_Tok34_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7186
EP2_PMM_2_Faza2_Tok35_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7187
EP2_PMM_2_Faza2_Tok36_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7188
EP2_PMM_2_Faza2_Tok37_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7189
EP2_PMM_2_Faza2_Tok38_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7190
EP2_PMM_2_Faza2_Tok39_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7191
EP2_PMM_2_Faza2_Tok40_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7192
EP2_PMM_2_Faza2_Tok41_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7193
EP2_PMM_2_Faza2_Tok42_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7194
EP2_PMM_2_Faza3_Tok01_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7195
EP2_PMM_2_Faza3_Tok02_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7196
EP2_PMM_2_Faza3_Tok03_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7197
EP2_PMM_2_Faza3_Tok04_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7198
EP2_PMM_2_Faza3_Tok05_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7199
EP2_PMM_2_Faza3_Tok06_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7200
EP2_PMM_2_Faza3_Tok07_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7201
EP2_PMM_2_Faza3_Tok08_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7202
EP2_PMM_2_Faza3_Tok09_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7203
EP2_PMM_2_Faza3_Tok10_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7204
EP2_PMM_2_Faza3_Tok11_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7205
EP2_PMM_2_Faza3_Tok12_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7206
EP2_PMM_2_Faza3_Tok13_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7207
EP2_PMM_2_Faza3_Tok14_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7208
EP2_PMM_2_Faza3_Tok15_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7209
EP2_PMM_2_Faza3_Tok16_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7210
EP2_PMM_2_Faza3_Tok17_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7211
EP2_PMM_2_Faza3_Tok18_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7212
EP2_PMM_2_Faza3_Tok19_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7213
EP2_PMM_2_Faza3_Tok20_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7214
EP2_PMM_2_Faza3_Tok21_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7215
EP2_PMM_2_Faza3_Tok22_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7216
EP2_PMM_2_Faza3_Tok23_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7217
EP2_PMM_2_Faza3_Tok24_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7218
EP2_PMM_2_Faza3_Tok25_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7219
EP2_PMM_2_Faza3_Tok26_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7220
EP2_PMM_2_Faza3_Tok27_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7221
EP2_PMM_2_Faza3_Tok28_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7222
EP2_PMM_2_Faza3_Tok29_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7223
EP2_PMM_2_Faza3_Tok30_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7224
EP2_PMM_2_Faza3_Tok31_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7225
EP2_PMM_2_Faza3_Tok32_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7226
EP2_PMM_2_Faza3_Tok33_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7227
EP2_PMM_2_Faza3_Tok34_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7228
EP2_PMM_2_Faza3_Tok35_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7229
EP2_PMM_2_Faza3_Tok36_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7230
EP2_PMM_2_Faza3_Tok37_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7231
EP2_PMM_2_Faza3_Tok38_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7232
EP2_PMM_2_Faza3_Tok39_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7233
EP2_PMM_2_Faza3_Tok40_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7234
EP2_PMM_2_Faza3_Tok41_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7235
EP2_PMM_2_Faza3_Tok42_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7236
EP2_PMM_1_Faza1_Tok01_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7237
EP2_PMM_1_Faza1_Tok02_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7238
EP2_PMM_1_Faza1_Tok03_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7239
EP2_PMM_1_Faza1_Tok04_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7240
EP2_PMM_1_Faza1_Tok05_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7241
EP2_PMM_1_Faza1_Tok06_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7242
EP2_PMM_1_Faza1_Tok07_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7243
EP2_PMM_1_Faza1_Tok08_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7244
EP2_PMM_1_Faza1_Tok09_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7245
EP2_PMM_1_Faza2_Tok01_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7246
EP2_PMM_1_Faza2_Tok02_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7247
EP2_PMM_1_Faza2_Tok03_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7248
EP2_PMM_1_Faza2_Tok04_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7249
EP2_PMM_1_Faza2_Tok05_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7250
EP2_PMM_1_Faza2_Tok06_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7251
EP2_PMM_1_Faza2_Tok07_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7252
EP2_PMM_1_Faza2_Tok08_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7253
EP2_PMM_1_Faza2_Tok09_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7254
EP2_PMM_1_Faza1_Tok01_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7255
EP2_PMM_1_Faza1_Tok02_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7256
EP2_PMM_1_Faza1_Tok03_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7257
EP2_PMM_1_Faza1_Tok04_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7258
EP2_PMM_1_Faza1_Tok05_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7259
EP2_PMM_1_Faza1_Tok06_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7260
EP2_PMM_1_Faza1_Tok07_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7261
EP2_PMM_1_Faza1_Tok08_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7262
EP2_PMM_1_Faza1_Tok09_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7263
EP2_PMM_1_Faza2_Tok01_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7264
EP2_PMM_1_Faza2_Tok02_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7265
EP2_PMM_1_Faza2_Tok03_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7266
EP2_PMM_1_Faza2_Tok04_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7267
EP2_PMM_1_Faza2_Tok05_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7268
EP2_PMM_1_Faza2_Tok06_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7269
EP2_PMM_1_Faza2_Tok07_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7270
EP2_PMM_1_Faza2_Tok08_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7271
EP2_PMM_1_Faza2_Tok09_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7272
EP2Max_analizator1 | REAL | IOD_EP2_disk | R7800 | [5 empty] | ##########
EP2Max_analizator2 | REAL | IOD_EP2_disk | R7804 | [5 empty] | ##########
EP2Max_analizator3 | REAL | IOD_EP2_disk | R7808 | [5 empty] | ##########
EP2_Anali_razlika_dnevna_E1K4 | REAL | IOD_EP2_disk | R7788 | [5 empty] | ###.#
EP2_Anali_razlika_teden_E1K4 | REAL | IOD_EP2_disk | R7792 | [5 empty] | ###.#
EP2_Anali_razlika_mes_E1K4 | REAL | IOD_EP2_disk | R7796 | [5 empty] | ###.#
EP2_XVH_AlarmOn | DIGITAL | IOD_EP2 | EP2:.XVH_AlarmOn
EP2_UserloggedIn_mem | DIGITAL | IOD_EP2_mem | D7285
EP2OmogociVseAlarme | DIGITAL | IOD_EP2_disk | D8000
EP2OmogociVseSMSAlarme | DIGITAL | IOD_EP2_disk | D8001
EP2OmogociVseDogodke_DO | DIGITAL | IOD_EP2_disk | D8002
EP2OmogociVseDogodke_DI | DIGITAL | IOD_EP2_disk | D8003
EP2OmogociVseDogodke_COM | DIGITAL | IOD_EP2_disk | D8004
EP2_OnemAlarmPon | DIGITAL | IOD_EP2_disk | D8005
EP2_PricetekSMSAlarmov1 | INT | IOD_EP2_disk | I8006
EP2_KonecSMSAlarmov1 | INT | IOD_EP2_disk | I8008
EP2_omogocanje_tok_opozorila | DIGITAL | IOD_EP2_disk | D8010[4]
EP2_omogocanje_tok_alarm | DIGITAL | IOD_EP2_disk | D8014[4]
EP2_meja_tok_opozorilo | LONG | IOD_EP2_disk | L8018[4]
EP2_meja_tok_alarm | LONG | IOD_EP2_disk | L8032[4]
EP2AlarmGenCirc1 | DIGITAL | 1 | EP2:.AlarmGenCirc1
EP2AlarmGenComm | DIGITAL | 2 | EP2:.AlarmGenComm
EP2AlarmGenDI | DIGITAL | 3 | EP2:.AlarmGenDI
EP2AlarmGenKlima5 | DIGITAL | 4 | EP2:.AlarmGenKlima5
EP2AlarmGenKlima6 | DIGITAL | 5 | EP2:.AlarmGenKlima6
EP2AlarmGenPMM1 | DIGITAL | 6 | EP2:.AlarmGenPMM1
EP2AlarmGenPMM2 | DIGITAL | 7 | EP2:.AlarmGenPMM2
EP2AlarmGenPMM3 | DIGITAL | 8 | EP2:.AlarmGenPMM3
EP2AlarmGenRest | DIGITAL | IOD_EP2 | EP2:.AlarmGenRest
EP2AlarmGenUPS1 | DIGITAL | 9 | EP2:.AlarmGenUPS1
EP2AlarmGenUPS2 | DIGITAL | 10 | EP2:.AlarmGenUPS2
EP2Circ1CosFi_III | REAL | 11 | EP2:.Circ[1].CosFi_III
EP2Circ1DelovnaEnergija | REAL | 12 | EP2:.Circ[1].DelovnaEnergija
EP2Circ1DelovnaMoc_III | REAL | 13 | EP2:.Circ[1].DelovnaMoc_III
EP2Circ1DelovnaMoc_L1 | REAL | 14 | EP2:.Circ[1].DelovnaMoc_L1
EP2Circ1DelovnaMoc_L2 | REAL | 15 | EP2:.Circ[1].DelovnaMoc_L2
EP2Circ1DelovnaMoc_L3 | REAL | 16 | EP2:.Circ[1].DelovnaMoc_L3
EP2Circ1Frekvenca_L1 | REAL | 17 | EP2:.Circ[1].Frekvenca_L1
EP2Circ1InduktivnaEnergija | REAL | 18 | EP2:.Circ[1].InduktivnaEnergija
EP2Circ1InduktivnaMoc_III | REAL | 19 | EP2:.Circ[1].InduktivnaMoc_III
EP2Circ1JalovaMoc_L1 | REAL | 20 | EP2:.Circ[1].JalovaMoc_L1
EP2Circ1JalovaMoc_L2 | REAL | 21 | EP2:.Circ[1].JalovaMoc_L2
EP2Circ1JalovaMoc_L3 | REAL | 22 | EP2:.Circ[1].JalovaMoc_L3
EP2Circ1KapacitivnaEnergija | REAL | 23 | EP2:.Circ[1].KapacitivnaEnergija
EP2Circ1KapacitivnaMoc_III | REAL | 24 | EP2:.Circ[1].KapacitivnaMoc_III
EP2Circ1MaximumDemand | REAL | 25 | EP2:.Circ[1].MaximumDemand
EP2Circ1Napetost_L1_L2 | REAL | 26 | EP2:.Circ[1].Napetost_L1_L2
EP2Circ1Napetost_L1_N | REAL | 27 | EP2:.Circ[1].Napetost_L1_N
EP2Circ1Napetost_L2_L3 | REAL | 28 | EP2:.Circ[1].Napetost_L2_L3
EP2Circ1Napetost_L2_N | REAL | 29 | EP2:.Circ[1].Napetost_L2_N
EP2Circ1Napetost_L3_L1 | REAL | 30 | EP2:.Circ[1].Napetost_L3_L1
EP2Circ1Napetost_L3_N | REAL | 31 | EP2:.Circ[1].Napetost_L3_N
EP2Circ1NavideznaMoc_III | REAL | 32 | EP2:.Circ[1].NavideznaMoc_III
EP2Circ1NicelniTok | REAL | 33 | EP2:.Circ[1].NicelniTok
EP2Circ1PowerFactor_III | REAL | 34 | EP2:.Circ[1].PowerFactor_III
EP2Circ1PowerFactor_L1 | REAL | 35 | EP2:.Circ[1].PowerFactor_L1
EP2Circ1PowerFactor_L2 | REAL | 36 | EP2:.Circ[1].PowerFactor_L2
EP2Circ1PowerFactor_L3 | REAL | 37 | EP2:.Circ[1].PowerFactor_L3
EP2Circ1THDI_L1 | REAL | 38 | EP2:.Circ[1].THDI_L1
EP2Circ1THDI_L2 | REAL | 39 | EP2:.Circ[1].THDI_L2
EP2Circ1THDI_L3 | REAL | 40 | EP2:.Circ[1].THDI_L3
EP2Circ1THDV_L1 | REAL | 41 | EP2:.Circ[1].THDV_L1
EP2Circ1THDV_L2 | REAL | 42 | EP2:.Circ[1].THDV_L2
EP2Circ1THDV_L3 | REAL | 43 | EP2:.Circ[1].THDV_L3
EP2Circ1Tok_L1 | REAL | 44 | EP2:.Circ[1].Tok_L1
EP2Circ1Tok_L2 | REAL | 45 | EP2:.Circ[1].Tok_L2
EP2Circ1Tok_L3 | REAL | 46 | EP2:.Circ[1].Tok_L3
EP2Circ1TokPovprecje_III | REAL | 47 | EP2:.Circ[1].TokPovprecje_III
EP2CircutorCosFi_III | REAL | 48 | EP2:.Circutor.CosFi_III
EP2CircutorDelovnaEnergija | REAL | 49 | EP2:.Circutor.DelovnaEnergija
EP2CircutorDelovnaMoc_III | REAL | 50 | EP2:.Circutor.DelovnaMoc_III
EP2CircutorDelovnaMoc_L1 | REAL | 51 | EP2:.Circutor.DelovnaMoc_L1
EP2CircutorDelovnaMoc_L2 | REAL | 52 | EP2:.Circutor.DelovnaMoc_L2
EP2CircutorDelovnaMoc_L3 | REAL | 53 | EP2:.Circutor.DelovnaMoc_L3
EP2CircutorFrekvenca_L1 | REAL | 54 | EP2:.Circutor.Frekvenca_L1
EP2CircutorInduktivnaEnergija | REAL | 55 | EP2:.Circutor.InduktivnaEnergija
EP2CircutorInduktivnaMoc_III | REAL | 56 | EP2:.Circutor.InduktivnaMoc_III
EP2CircutorJalovaMoc_L1 | REAL | 57 | EP2:.Circutor.JalovaMoc_L1
EP2CircutorJalovaMoc_L2 | REAL | 58 | EP2:.Circutor.JalovaMoc_L2
EP2CircutorJalovaMoc_L3 | REAL | 59 | EP2:.Circutor.JalovaMoc_L3
EP2CircutorKapacitivnaEnergija | REAL | 60 | EP2:.Circutor.KapacitivnaEnergija
EP2CircutorKapacitivnaMoc_III | REAL | 61 | EP2:.Circutor.KapacitivnaMoc_III
EP2CircutorMaximumDemand | REAL | 62 | EP2:.Circutor.MaximumDemand
EP2CircutorNapetost_L1_L2 | REAL | 63 | EP2:.Circutor.Napetost_L1_L2
EP2CircutorNapetost_L1_N | REAL | 64 | EP2:.Circutor.Napetost_L1_N
EP2CircutorNapetost_L2_L3 | REAL | 65 | EP2:.Circutor.Napetost_L2_L3
EP2CircutorNapetost_L2_N | REAL | 66 | EP2:.Circutor.Napetost_L2_N
EP2CircutorNapetost_L3_L1 | REAL | 67 | EP2:.Circutor.Napetost_L3_L1
EP2CircutorNapetost_L3_N | REAL | 68 | EP2:.Circutor.Napetost_L3_N
EP2CircutorNavideznaMoc_III | REAL | 69 | EP2:.Circutor.NavideznaMoc_III
EP2CircutorNicelniTok | REAL | 70 | EP2:.Circutor.NicelniTok
EP2CircutorPowerFactor_III | REAL | 71 | EP2:.Circutor.PowerFactor_III
EP2CircutorPowerFactor_L1 | REAL | 72 | EP2:.Circutor.PowerFactor_L1
EP2CircutorPowerFactor_L2 | REAL | 73 | EP2:.Circutor.PowerFactor_L2
EP2CircutorPowerFactor_L3 | REAL | 74 | EP2:.Circutor.PowerFactor_L3
EP2CircutorTHDI_L1 | REAL | 75 | EP2:.Circutor.THDI_L1
EP2CircutorTHDI_L2 | REAL | 76 | EP2:.Circutor.THDI_L2
EP2CircutorTHDI_L3 | REAL | 77 | EP2:.Circutor.THDI_L3
EP2CircutorTHDV_L1 | REAL | 78 | EP2:.Circutor.THDV_L1
EP2CircutorTHDV_L2 | REAL | 79 | EP2:.Circutor.THDV_L2
EP2CircutorTHDV_L3 | REAL | 80 | EP2:.Circutor.THDV_L3
EP2CircutorTok_L1 | REAL | 81 | EP2:.Circutor.Tok_L1
EP2CircutorTok_L2 | REAL | 82 | EP2:.Circutor.Tok_L2
EP2CircutorTok_L3 | REAL | 83 | EP2:.Circutor.Tok_L3
EP2CircutorTokPovprecje_III | REAL | 84 | EP2:.Circutor.TokPovprecje_III
EP2ComSCADA | DIGITAL | 85 | EP2:.ComSCADA
EP2ComSCADA1 | DIGITAL | 86 | EP2:.ComSCADA1
EP2DateTimeDan | BYTE | 87 | EP2:.DateTime.Dan
EP2DateTimeLeto | BYTE | 88 | EP2:.DateTime.Leto
EP2DateTimeMesec | BYTE | 89 | EP2:.DateTime.Mesec
EP2DateTimeMinuta | BYTE | 90 | EP2:.DateTime.Minuta
EP2DateTimeSekunda | BYTE | 91 | EP2:.DateTime.Sekunda
EP2DateTimeUra | BYTE | 92 | EP2:.DateTime.Ura
EP2DI_Klima5_ERR | DIGITAL | 93 | EP2:.DI_Klima5_ERR
EP2DI_Klima5_ON | DIGITAL | 94 | EP2:.DI_Klima5_ON
EP2DI_Klima6_ERR | DIGITAL | 95 | EP2:.DI_Klima6_ERR
EP2DI_Klima6_ON | DIGITAL | 96 | EP2:.DI_Klima6_ON
EP2DI_KlimaSplit1_ERR | DIGITAL | 97 | EP2:.DI_KlimaSplit1_ERR
EP2DI_KlimaSplit1_ON | DIGITAL | 98 | EP2:.DI_KlimaSplit1_ON
EP2DI_Q10_OdcKlima6_IZP | DIGITAL | 99 | EP2:.DI_Q10_OdcKlima6_IZP
EP2DI_Q10_OdcKlima6_ON | DIGITAL | 100 | EP2:.DI_Q10_OdcKlima6_ON
EP2DI_Q11_OdcVent1_ON | DIGITAL | 101 | EP2:.DI_Q11_OdcVent1_ON
EP2DI_Q12_Rezerva_ON | DIGITAL | 102 | EP2:.DI_Q12_Rezerva_ON
EP2DI_Q1_GlavnoStikalo_ON | DIGITAL | 103 | EP2:.DI_Q1_GlavnoStikalo_ON
EP2DI_Q25_OdcUpsA_IZP | DIGITAL | 104 | EP2:.DI_Q25_OdcUpsA_IZP
EP2DI_Q25_OdcUpsA_ON | DIGITAL | 105 | EP2:.DI_Q25_OdcUpsA_ON
EP2DI_Q26_OdcByA_IZP | DIGITAL | 106 | EP2:.DI_Q26_OdcByA_IZP
EP2DI_Q26_OdcByA_ON | DIGITAL | 107 | EP2:.DI_Q26_OdcByA_ON
EP2DI_Q27_OdcByUpsA_IZP | DIGITAL | 108 | EP2:.DI_Q27_OdcByUpsA_IZP
EP2DI_Q27_OdcByUpsA_ON | DIGITAL | 109 | EP2:.DI_Q27_OdcByUpsA_ON
EP2DI_Q28_OdcUpsB_IZP | DIGITAL | 110 | EP2:.DI_Q28_OdcUpsB_IZP
EP2DI_Q28_OdcUpsB_ON | DIGITAL | 111 | EP2:.DI_Q28_OdcUpsB_ON
EP2DI_Q29_OdcByB_IZP | DIGITAL | 112 | EP2:.DI_Q29_OdcByB_IZP
EP2DI_Q29_OdcByB_ON | DIGITAL | 113 | EP2:.DI_Q29_OdcByB_ON
EP2DI_Q2_Rezerva_IZP | DIGITAL | 114 | EP2:.DI_Q2_Rezerva_IZP
EP2DI_Q2_Rezerva_ON | DIGITAL | 115 | EP2:.DI_Q2_Rezerva_ON
EP2DI_Q30_OdcByUpsB_IZP | DIGITAL | 116 | EP2:.DI_Q30_OdcByUpsB_IZP
EP2DI_Q30_OdcByUpsB_ON | DIGITAL | 117 | EP2:.DI_Q30_OdcByUpsB_ON
EP2DI_Q31_DovByUpsA_ON | DIGITAL | 118 | EP2:.DI_Q31_DovByUpsA_ON
EP2DI_Q32_DovByA_ON | DIGITAL | 119 | EP2:.DI_Q32_DovByA_ON
EP2DI_Q33_DovByUpsB_ON | DIGITAL | 120 | EP2:.DI_Q33_DovByUpsB_ON
EP2DI_Q34_DovByB_ON | DIGITAL | 121 | EP2:.DI_Q34_DovByB_ON
EP2DI_Q5_OdcKlima1_IZP | DIGITAL | 122 | EP2:.DI_Q5_OdcKlima1_IZP
EP2DI_Q5_OdcKlima1_ON | DIGITAL | 123 | EP2:.DI_Q5_OdcKlima1_ON
EP2DI_Q6_OdcKlima2_IZP | DIGITAL | 124 | EP2:.DI_Q6_OdcKlima2_IZP
EP2DI_Q6_OdcKlima2_ON | DIGITAL | 125 | EP2:.DI_Q6_OdcKlima2_ON
EP2DI_Q7_OdcKlima3_IZP | DIGITAL | 126 | EP2:.DI_Q7_OdcKlima3_IZP
EP2DI_Q7_OdcKlima3_ON | DIGITAL | 127 | EP2:.DI_Q7_OdcKlima3_ON
EP2DI_Q8_OdcKlima4_IZP | DIGITAL | 128 | EP2:.DI_Q8_OdcKlima4_IZP
EP2DI_Q8_OdcKlima4_ON | DIGITAL | 129 | EP2:.DI_Q8_OdcKlima4_ON
EP2DI_Q9_OdcKlima5_IZP | DIGITAL | 130 | EP2:.DI_Q9_OdcKlima5_IZP
EP2DI_Q9_OdcKlima5_ON | DIGITAL | 131 | EP2:.DI_Q9_OdcKlima5_ON
EP2DI_RazlitjeVodeK5K6 | DIGITAL | 132 | EP2:.DI_RazlitjeVodeK5K6
EP2DI_UPS_Alarm | DIGITAL | 133 | EP2:.DI_UPS_Alarm
EP2DI_UPS_BatNacin | DIGITAL | 134 | EP2:.DI_UPS_BatNacin
EP2DI_UPS_Polnjenje | DIGITAL | 135 | EP2:.DI_UPS_Polnjenje
EP2DI_UpsA_BypassON | DIGITAL | IOD_EP2 | EP2:.DI_UpsA_BypassON
EP2DI_UpsA_ERR | DIGITAL | IOD_EP2 | EP2:.DI_UpsA_ERR
EP2DI_UpsB_BypassON | DIGITAL | IOD_EP2 | EP2:.DI_UpsB_BypassON
EP2DI_UpsB_ERR | DIGITAL | IOD_EP2 | EP2:.DI_UpsB_ERR
EP2DIN_Klima5_ERR | DIGITAL | IOD_EP2 | EP2:.DIN_Klima5_ERR
EP2DIN_Klima6_ERR | DIGITAL | IOD_EP2 | EP2:.DIN_Klima6_ERR
EP2DIN_KlimaSplit1_ERR | DIGITAL | IOD_EP2 | EP2:.DIN_KlimaSplit1_ERR
EP2DIN_Q10_OdcKlima6_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q10_OdcKlima6_IZP
EP2DIN_Q25_OdcUpsA_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q25_OdcUpsA_IZP
EP2DIN_Q26_OdcByA_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q26_OdcByA_IZP
EP2DIN_Q27_OdcByUpsA_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q27_OdcByUpsA_IZP
EP2DIN_Q28_OdcUpsB_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q28_OdcUpsB_IZP
EP2DIN_Q29_OdcByB_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q29_OdcByB_IZP
EP2DIN_Q2_Rezerva_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q2_Rezerva_IZP
EP2DIN_Q30_OdcByUpsB_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q30_OdcByUpsB_IZP
EP2DIN_Q5_OdcKlima1_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q5_OdcKlima1_IZP
EP2DIN_Q6_OdcKlima2_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q6_OdcKlima2_IZP
EP2DIN_Q7_OdcKlima3_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q7_OdcKlima3_IZP
EP2DIN_Q8_OdcKlima4_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q8_OdcKlima4_IZP
EP2DIN_Q9_OdcKlima5_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q9_OdcKlima5_IZP
EP2DIN_UpsA_BypassON | DIGITAL | 137 | EP2:.DIN_UpsA_BypassON
EP2DIN_UpsA_ERR | DIGITAL | 136 | EP2:.DIN_UpsA_ERR
EP2DIN_UpsB_BypassON | DIGITAL | 139 | EP2:.DIN_UpsB_BypassON
EP2DIN_UpsB_ERR | DIGITAL | 138 | EP2:.DIN_UpsB_ERR
EP2DO_Klima5_Izklop | DIGITAL | 140 | EP2:.DO_Klima5_Izklop
EP2DO_Klima6_Izklop | DIGITAL | 141 | EP2:.DO_Klima6_Izklop
EP2ErrComCirc1 | DIGITAL | 142 | EP2:.ErrComCirc[1]
EP2ErrComCirc2 | DIGITAL | 143 | EP2:.ErrComCirc[2]
EP2ErrComCirc3 | DIGITAL | 144 | EP2:.ErrComCirc[3]
EP2ErrComCirc4 | DIGITAL | 145 | EP2:.ErrComCirc[4]
EP2ErrComCirc5 | DIGITAL | 146 | EP2:.ErrComCirc[5]
EP2ErrComKlima1 | DIGITAL | 147 | EP2:.ErrComKlima[1]
EP2ErrComKlima2 | DIGITAL | 148 | EP2:.ErrComKlima[2]
EP2ErrComKlima3 | DIGITAL | 149 | EP2:.ErrComKlima[3]
EP2ErrComKlima4 | DIGITAL | 150 | EP2:.ErrComKlima[4]
EP2ErrComKlima5 | DIGITAL | 151 | EP2:.ErrComKlima[5]
EP2ErrComKlima6 | DIGITAL | 152 | EP2:.ErrComKlima[6]
EP2ErrCommScada | DIGITAL | 153 | EP2:.ErrCommScada
EP2ErrComPanelPLC | DIGITAL | 154 | EP2:.ErrComPanelPLC
EP2ErrComPMM1 | DIGITAL | 155 | EP2:.ErrComPMM[1]
EP2ErrComPMM2 | DIGITAL | 156 | EP2:.ErrComPMM[2]
EP2ErrComPMM3 | DIGITAL | 157 | EP2:.ErrComPMM[3]
EP2ErrComPort2 | DIGITAL | 158 | EP2:.ErrComPort2
EP2ErrComPort3 | DIGITAL | 159 | EP2:.ErrComPort3
EP2ErrComPort4 | DIGITAL | 160 | EP2:.ErrComPort4
EP2ErrComUPS1 | DIGITAL | 161 | EP2:.ErrComUPS[1]
EP2ErrComUPS2 | DIGITAL | 162 | EP2:.ErrComUPS[2]
EP2ErrorComCirc1Code10 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[1].Code[10]
EP2ErrorComCirc1Code11 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[1].Code[11]
EP2ErrorComCirc1Code12 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[1].Code[12]
EP2ErrorComCirc1Code13 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[1].Code[13]
EP2ErrorComCirc1Code14 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[1].Code[14]
EP2ErrorComCirc1Code15 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[1].Code[15]
EP2ErrorComCirc1Code1 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[1].Code[1]
EP2ErrorComCirc1Code2 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[1].Code[2]
EP2ErrorComCirc1Code3 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[1].Code[3]
EP2ErrorComCirc1Code4 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[1].Code[4]
EP2ErrorComCirc1Code5 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[1].Code[5]
EP2ErrorComCirc1Code6 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[1].Code[6]
EP2ErrorComCirc1Code7 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[1].Code[7]
EP2ErrorComCirc1Code8 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[1].Code[8]
EP2ErrorComCirc1Code9 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[1].Code[9]
EP2ErrorComCirc1Error | DIGITAL | IOD_EP2 | EP2:.ErrorComCirc[1].Error
EP2ErrorComCirc1Status | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Status
EP2ErrorComCirc2Code10 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[2].Code[10]
EP2ErrorComCirc2Code11 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[2].Code[11]
EP2ErrorComCirc2Code12 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[2].Code[12]
EP2ErrorComCirc2Code13 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[2].Code[13]
EP2ErrorComCirc2Code14 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[2].Code[14]
EP2ErrorComCirc2Code15 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[2].Code[15]
EP2ErrorComCirc2Code1 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[2].Code[1]
EP2ErrorComCirc2Code2 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[2].Code[2]
EP2ErrorComCirc2Code3 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[2].Code[3]
EP2ErrorComCirc2Code4 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[2].Code[4]
EP2ErrorComCirc2Code5 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[2].Code[5]
EP2ErrorComCirc2Code6 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[2].Code[6]
EP2ErrorComCirc2Code7 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[2].Code[7]
EP2ErrorComCirc2Code8 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[2].Code[8]
EP2ErrorComCirc2Code9 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[2].Code[9]
EP2ErrorComCirc2Error | DIGITAL | IOD_EP2 | EP2:.ErrorComCirc[2].Error
EP2ErrorComCirc2Status | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Status
EP2ErrorComCirc3Code10 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[3].Code[10]
EP2ErrorComCirc3Code11 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[3].Code[11]
EP2ErrorComCirc3Code12 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[3].Code[12]
EP2ErrorComCirc3Code13 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[3].Code[13]
EP2ErrorComCirc3Code14 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[3].Code[14]
EP2ErrorComCirc3Code15 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[3].Code[15]
EP2ErrorComCirc3Code1 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[3].Code[1]
EP2ErrorComCirc3Code2 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[3].Code[2]
EP2ErrorComCirc3Code3 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[3].Code[3]
EP2ErrorComCirc3Code4 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[3].Code[4]
EP2ErrorComCirc3Code5 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[3].Code[5]
EP2ErrorComCirc3Code6 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[3].Code[6]
EP2ErrorComCirc3Code7 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[3].Code[7]
EP2ErrorComCirc3Code8 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[3].Code[8]
EP2ErrorComCirc3Code9 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[3].Code[9]
EP2ErrorComCirc3Error | DIGITAL | IOD_EP2 | EP2:.ErrorComCirc[3].Error
EP2ErrorComCirc3Status | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Status
EP2ErrorComCirc4Code10 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[4].Code[10]
EP2ErrorComCirc4Code11 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[4].Code[11]
EP2ErrorComCirc4Code12 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[4].Code[12]
EP2ErrorComCirc4Code13 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[4].Code[13]
EP2ErrorComCirc4Code14 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[4].Code[14]
EP2ErrorComCirc4Code15 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[4].Code[15]
EP2ErrorComCirc4Code1 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[4].Code[1]
EP2ErrorComCirc4Code2 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[4].Code[2]
EP2ErrorComCirc4Code3 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[4].Code[3]
EP2ErrorComCirc4Code4 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[4].Code[4]
EP2ErrorComCirc4Code5 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[4].Code[5]
EP2ErrorComCirc4Code6 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[4].Code[6]
EP2ErrorComCirc4Code7 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[4].Code[7]
EP2ErrorComCirc4Code8 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[4].Code[8]
EP2ErrorComCirc4Code9 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[4].Code[9]
EP2ErrorComCirc4Error | DIGITAL | IOD_EP2 | EP2:.ErrorComCirc[4].Error
EP2ErrorComCirc4Status | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Status
EP2ErrorComCirc5Code10 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[5].Code[10]
EP2ErrorComCirc5Code11 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[5].Code[11]
EP2ErrorComCirc5Code12 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[5].Code[12]
EP2ErrorComCirc5Code13 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[5].Code[13]
EP2ErrorComCirc5Code14 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[5].Code[14]
EP2ErrorComCirc5Code15 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[5].Code[15]
EP2ErrorComCirc5Code1 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[5].Code[1]
EP2ErrorComCirc5Code2 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[5].Code[2]
EP2ErrorComCirc5Code3 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[5].Code[3]
EP2ErrorComCirc5Code4 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[5].Code[4]
EP2ErrorComCirc5Code5 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[5].Code[5]
EP2ErrorComCirc5Code6 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[5].Code[6]
EP2ErrorComCirc5Code7 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[5].Code[7]
EP2ErrorComCirc5Code8 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[5].Code[8]
EP2ErrorComCirc5Code9 | BYTE | IOD_EP2 | EP2:.ErrorComCirc[5].Code[9]
EP2ErrorComCirc5Error | DIGITAL | IOD_EP2 | EP2:.ErrorComCirc[5].Error
EP2ErrorComCirc5Status | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Status
EP2ErrorComKlima1Code10 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[1].Code[10]
EP2ErrorComKlima1Code11 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[1].Code[11]
EP2ErrorComKlima1Code12 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[1].Code[12]
EP2ErrorComKlima1Code13 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[1].Code[13]
EP2ErrorComKlima1Code14 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[1].Code[14]
EP2ErrorComKlima1Code15 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[1].Code[15]
EP2ErrorComKlima1Code1 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[1].Code[1]
EP2ErrorComKlima1Code2 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[1].Code[2]
EP2ErrorComKlima1Code3 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[1].Code[3]
EP2ErrorComKlima1Code4 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[1].Code[4]
EP2ErrorComKlima1Code5 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[1].Code[5]
EP2ErrorComKlima1Code6 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[1].Code[6]
EP2ErrorComKlima1Code7 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[1].Code[7]
EP2ErrorComKlima1Code8 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[1].Code[8]
EP2ErrorComKlima1Code9 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[1].Code[9]
EP2ErrorComKlima1Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[1].Error
EP2ErrorComKlima1Status | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Status
EP2ErrorComKlima2Code10 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[2].Code[10]
EP2ErrorComKlima2Code11 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[2].Code[11]
EP2ErrorComKlima2Code12 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[2].Code[12]
EP2ErrorComKlima2Code13 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[2].Code[13]
EP2ErrorComKlima2Code14 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[2].Code[14]
EP2ErrorComKlima2Code15 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[2].Code[15]
EP2ErrorComKlima2Code1 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[2].Code[1]
EP2ErrorComKlima2Code2 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[2].Code[2]
EP2ErrorComKlima2Code3 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[2].Code[3]
EP2ErrorComKlima2Code4 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[2].Code[4]
EP2ErrorComKlima2Code5 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[2].Code[5]
EP2ErrorComKlima2Code6 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[2].Code[6]
EP2ErrorComKlima2Code7 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[2].Code[7]
EP2ErrorComKlima2Code8 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[2].Code[8]
EP2ErrorComKlima2Code9 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[2].Code[9]
EP2ErrorComKlima2Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[2].Error
EP2ErrorComKlima2Status | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Status
EP2ErrorComKlima3Code10 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[3].Code[10]
EP2ErrorComKlima3Code11 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[3].Code[11]
EP2ErrorComKlima3Code12 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[3].Code[12]
EP2ErrorComKlima3Code13 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[3].Code[13]
EP2ErrorComKlima3Code14 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[3].Code[14]
EP2ErrorComKlima3Code15 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[3].Code[15]
EP2ErrorComKlima3Code1 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[3].Code[1]
EP2ErrorComKlima3Code2 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[3].Code[2]
EP2ErrorComKlima3Code3 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[3].Code[3]
EP2ErrorComKlima3Code4 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[3].Code[4]
EP2ErrorComKlima3Code5 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[3].Code[5]
EP2ErrorComKlima3Code6 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[3].Code[6]
EP2ErrorComKlima3Code7 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[3].Code[7]
EP2ErrorComKlima3Code8 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[3].Code[8]
EP2ErrorComKlima3Code9 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[3].Code[9]
EP2ErrorComKlima3Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[3].Error
EP2ErrorComKlima3Status | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Status
EP2ErrorComKlima4Code10 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[4].Code[10]
EP2ErrorComKlima4Code11 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[4].Code[11]
EP2ErrorComKlima4Code12 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[4].Code[12]
EP2ErrorComKlima4Code13 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[4].Code[13]
EP2ErrorComKlima4Code14 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[4].Code[14]
EP2ErrorComKlima4Code15 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[4].Code[15]
EP2ErrorComKlima4Code1 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[4].Code[1]
EP2ErrorComKlima4Code2 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[4].Code[2]
EP2ErrorComKlima4Code3 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[4].Code[3]
EP2ErrorComKlima4Code4 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[4].Code[4]
EP2ErrorComKlima4Code5 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[4].Code[5]
EP2ErrorComKlima4Code6 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[4].Code[6]
EP2ErrorComKlima4Code7 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[4].Code[7]
EP2ErrorComKlima4Code8 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[4].Code[8]
EP2ErrorComKlima4Code9 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[4].Code[9]
EP2ErrorComKlima4Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[4].Error
EP2ErrorComKlima4Status | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Status
EP2ErrorComKlima5Code10 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[5].Code[10]
EP2ErrorComKlima5Code11 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[5].Code[11]
EP2ErrorComKlima5Code12 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[5].Code[12]
EP2ErrorComKlima5Code13 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[5].Code[13]
EP2ErrorComKlima5Code14 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[5].Code[14]
EP2ErrorComKlima5Code15 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[5].Code[15]
EP2ErrorComKlima5Code1 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[5].Code[1]
EP2ErrorComKlima5Code2 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[5].Code[2]
EP2ErrorComKlima5Code3 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[5].Code[3]
EP2ErrorComKlima5Code4 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[5].Code[4]
EP2ErrorComKlima5Code5 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[5].Code[5]
EP2ErrorComKlima5Code6 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[5].Code[6]
EP2ErrorComKlima5Code7 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[5].Code[7]
EP2ErrorComKlima5Code8 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[5].Code[8]
EP2ErrorComKlima5Code9 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[5].Code[9]
EP2ErrorComKlima5Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[5].Error
EP2ErrorComKlima5Status | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Status
EP2ErrorComKlima6Code10 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[6].Code[10]
EP2ErrorComKlima6Code11 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[6].Code[11]
EP2ErrorComKlima6Code12 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[6].Code[12]
EP2ErrorComKlima6Code13 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[6].Code[13]
EP2ErrorComKlima6Code14 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[6].Code[14]
EP2ErrorComKlima6Code15 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[6].Code[15]
EP2ErrorComKlima6Code1 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[6].Code[1]
EP2ErrorComKlima6Code2 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[6].Code[2]
EP2ErrorComKlima6Code3 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[6].Code[3]
EP2ErrorComKlima6Code4 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[6].Code[4]
EP2ErrorComKlima6Code5 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[6].Code[5]
EP2ErrorComKlima6Code6 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[6].Code[6]
EP2ErrorComKlima6Code7 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[6].Code[7]
EP2ErrorComKlima6Code8 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[6].Code[8]
EP2ErrorComKlima6Code9 | BYTE | IOD_EP2 | EP2:.ErrorComKlima[6].Code[9]
EP2ErrorComKlima6Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[6].Error
EP2ErrorComKlima6Status | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Status
EP2ErrorComPMM1Code10 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[1].Code[10]
EP2ErrorComPMM1Code11 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[1].Code[11]
EP2ErrorComPMM1Code12 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[1].Code[12]
EP2ErrorComPMM1Code13 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[1].Code[13]
EP2ErrorComPMM1Code14 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[1].Code[14]
EP2ErrorComPMM1Code15 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[1].Code[15]
EP2ErrorComPMM1Code1 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[1].Code[1]
EP2ErrorComPMM1Code2 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[1].Code[2]
EP2ErrorComPMM1Code3 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[1].Code[3]
EP2ErrorComPMM1Code4 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[1].Code[4]
EP2ErrorComPMM1Code5 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[1].Code[5]
EP2ErrorComPMM1Code6 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[1].Code[6]
EP2ErrorComPMM1Code7 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[1].Code[7]
EP2ErrorComPMM1Code8 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[1].Code[8]
EP2ErrorComPMM1Code9 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[1].Code[9]
EP2ErrorComPMM1Error | DIGITAL | IOD_EP2 | EP2:.ErrorComPMM[1].Error
EP2ErrorComPMM1Status | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Status
EP2ErrorComPMM2Code10 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[2].Code[10]
EP2ErrorComPMM2Code11 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[2].Code[11]
EP2ErrorComPMM2Code12 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[2].Code[12]
EP2ErrorComPMM2Code13 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[2].Code[13]
EP2ErrorComPMM2Code14 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[2].Code[14]
EP2ErrorComPMM2Code15 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[2].Code[15]
EP2ErrorComPMM2Code1 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[2].Code[1]
EP2ErrorComPMM2Code2 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[2].Code[2]
EP2ErrorComPMM2Code3 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[2].Code[3]
EP2ErrorComPMM2Code4 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[2].Code[4]
EP2ErrorComPMM2Code5 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[2].Code[5]
EP2ErrorComPMM2Code6 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[2].Code[6]
EP2ErrorComPMM2Code7 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[2].Code[7]
EP2ErrorComPMM2Code8 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[2].Code[8]
EP2ErrorComPMM2Code9 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[2].Code[9]
EP2ErrorComPMM2Error | DIGITAL | IOD_EP2 | EP2:.ErrorComPMM[2].Error
EP2ErrorComPMM2Status | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Status
EP2ErrorComPMM3Code10 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[3].Code[10]
EP2ErrorComPMM3Code11 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[3].Code[11]
EP2ErrorComPMM3Code12 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[3].Code[12]
EP2ErrorComPMM3Code13 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[3].Code[13]
EP2ErrorComPMM3Code14 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[3].Code[14]
EP2ErrorComPMM3Code15 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[3].Code[15]
EP2ErrorComPMM3Code1 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[3].Code[1]
EP2ErrorComPMM3Code2 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[3].Code[2]
EP2ErrorComPMM3Code3 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[3].Code[3]
EP2ErrorComPMM3Code4 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[3].Code[4]
EP2ErrorComPMM3Code5 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[3].Code[5]
EP2ErrorComPMM3Code6 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[3].Code[6]
EP2ErrorComPMM3Code7 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[3].Code[7]
EP2ErrorComPMM3Code8 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[3].Code[8]
EP2ErrorComPMM3Code9 | BYTE | IOD_EP2 | EP2:.ErrorComPMM[3].Code[9]
EP2ErrorComPMM3Error | DIGITAL | IOD_EP2 | EP2:.ErrorComPMM[3].Error
EP2ErrorComPMM3Status | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Status
EP2ErrorComUPS1Code10 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[1].Code[10]
EP2ErrorComUPS1Code11 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[1].Code[11]
EP2ErrorComUPS1Code12 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[1].Code[12]
EP2ErrorComUPS1Code13 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[1].Code[13]
EP2ErrorComUPS1Code14 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[1].Code[14]
EP2ErrorComUPS1Code15 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[1].Code[15]
EP2ErrorComUPS1Code1 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[1].Code[1]
EP2ErrorComUPS1Code2 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[1].Code[2]
EP2ErrorComUPS1Code3 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[1].Code[3]
EP2ErrorComUPS1Code4 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[1].Code[4]
EP2ErrorComUPS1Code5 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[1].Code[5]
EP2ErrorComUPS1Code6 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[1].Code[6]
EP2ErrorComUPS1Code7 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[1].Code[7]
EP2ErrorComUPS1Code8 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[1].Code[8]
EP2ErrorComUPS1Code9 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[1].Code[9]
EP2ErrorComUPS1Error | DIGITAL | IOD_EP2 | EP2:.ErrorComUPS[1].Error
EP2ErrorComUPS1Status | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Status
EP2ErrorComUPS2Code10 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[2].Code[10]
EP2ErrorComUPS2Code11 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[2].Code[11]
EP2ErrorComUPS2Code12 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[2].Code[12]
EP2ErrorComUPS2Code13 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[2].Code[13]
EP2ErrorComUPS2Code14 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[2].Code[14]
EP2ErrorComUPS2Code15 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[2].Code[15]
EP2ErrorComUPS2Code1 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[2].Code[1]
EP2ErrorComUPS2Code2 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[2].Code[2]
EP2ErrorComUPS2Code3 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[2].Code[3]
EP2ErrorComUPS2Code4 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[2].Code[4]
EP2ErrorComUPS2Code5 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[2].Code[5]
EP2ErrorComUPS2Code6 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[2].Code[6]
EP2ErrorComUPS2Code7 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[2].Code[7]
EP2ErrorComUPS2Code8 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[2].Code[8]
EP2ErrorComUPS2Code9 | BYTE | IOD_EP2 | EP2:.ErrorComUPS[2].Code[9]
EP2ErrorComUPS2Error | DIGITAL | IOD_EP2 | EP2:.ErrorComUPS[2].Error
EP2ErrorComUPS2Status | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Status
EP2Klima1AlarmKompresor1 | DIGITAL | 163 | EP2:.Klima[1].AlarmKompresor1
EP2Klima1AlarmKompresor2 | DIGITAL | 164 | EP2:.Klima[1].AlarmKompresor2
EP2Klima1Deluje | DIGITAL | 165 | EP2:.Klima[1].Deluje
EP2Klima1EnergySaving | DIGITAL | 166 | EP2:.Klima[1].EnergySaving
EP2Klima1FaultyEPROM | DIGITAL | 167 | EP2:.Klima[1].FaultyEPROM
EP2Klima1FenThermalCutout | DIGITAL | 168 | EP2:.Klima[1].FenThermalCutout
EP2Klima1GeneralAlarm | DIGITAL | 169 | EP2:.Klima[1].GeneralAlarm
EP2Klima1GrelecStatus | BYTE | 170 | EP2:.Klima[1].GrelecStatus
EP2Klima1IzhodniVentStatus | BYTE | 171 | EP2:.Klima[1].IzhodniVentStatus
EP2Klima1Kompresor1naMejiObrUr | DIGITAL | 172 | EP2:.Klima[1].Kompresor1naMejiObrUr
EP2Klima1Kompresor2naMejiObrUr | DIGITAL | 173 | EP2:.Klima[1].Kompresor2naMejiObrUr
EP2Klima1KompresorStatus | BYTE | 174 | EP2:.Klima[1].KompresorStatus
EP2Klima1Napaka | DIGITAL | 175 | EP2:.Klima[1].Napaka
EP2Klima1NapakaPriPretokuZraka | DIGITAL | 176 | EP2:.Klima[1].NapakaPriPretokuZraka
EP2Klima1NapakaSenzorPovratVode | DIGITAL | 177 | EP2:.Klima[1].NapakaSenzorPovratVode
EP2Klima1NapakaSenzorTempIzpiha | DIGITAL | 178 | EP2:.Klima[1].NapakaSenzorTempIzpiha
EP2Klima1NapakaSenzorTempProstora | DIGITAL | 179 | EP2:.Klima[1].NapakaSenzorTempProstora
EP2Klima1NapakaSenzorVlaznosti | DIGITAL | 180 | EP2:.Klima[1].NapakaSenzorVlaznosti
EP2Klima1NapakaSenzorZunanjeTemp | DIGITAL | 181 | EP2:.Klima[1].NapakaSenzorZunanjeTemp
EP2Klima1NastMaxTemp | REAL | 182 | EP2:.Klima[1].NastMaxTemp
EP2Klima1NastMaxVlaznost | REAL | 183 | EP2:.Klima[1].NastMaxVlaznost
EP2Klima1NastMinTemp | REAL | 184 | EP2:.Klima[1].NastMinTemp
EP2Klima1NastMinVlaznost | REAL | 185 | EP2:.Klima[1].NastMinVlaznost
EP2Klima1NastTempProstora | REAL | 186 | EP2:.Klima[1].NastTempProstora
EP2Klima1NastVlaznost | REAL | 187 | EP2:.Klima[1].NastVlaznost
EP2Klima1NiTokaVVlazilcu | DIGITAL | 188 | EP2:.Klima[1].NiTokaVVlazilcu
EP2Klima1NiVodeVVlazilcu | DIGITAL | 189 | EP2:.Klima[1].NiVodeVVlazilcu
EP2Klima1NizekPritiskKompresor1 | DIGITAL | 190 | EP2:.Klima[1].NizekPritiskKompresor1
EP2Klima1NizekPritiskKompresor2 | DIGITAL | 191 | EP2:.Klima[1].NizekPritiskKompresor2
EP2Klima1NizkaTempPovratneVode | DIGITAL | 192 | EP2:.Klima[1].NizkaTempPovratneVode
EP2Klima1NizkaTempVProstoru | DIGITAL | 193 | EP2:.Klima[1].NizkaTempVProstoru
EP2Klima1NizkaVlaznost | DIGITAL | 194 | EP2:.Klima[1].NizkaVlaznost
EP2Klima1ObratovalneUre | REAL | 195 | EP2:.Klima[1].ObratovalneUre
EP2Klima1OnOffEnablingBySupervisor | DIGITAL | 196 | EP2:.Klima[1].OnOffEnablingBySupervisor
EP2Klima1PozarniAlarm | DIGITAL | 197 | EP2:.Klima[1].PozarniAlarm
EP2Klima1Razvlazevanje | DIGITAL | 198 | EP2:.Klima[1].Razvlazevanje
EP2Klima1RemoteOFFtoOutput | DIGITAL | 199 | EP2:.Klima[1].RemoteOFFtoOutput
EP2Klima1RemoteOnOff | DIGITAL | 200 | EP2:.Klima[1].RemoteOnOff
EP2Klima1RocniIzklop | DIGITAL | 201 | EP2:.Klima[1].RocniIzklop
EP2Klima1SenzorjiStatus | DIGITAL | 202 | EP2:.Klima[1].SenzorjiStatus
EP2Klima1StoppedByAlarms | DIGITAL | 203 | EP2:.Klima[1].StoppedByAlarms
EP2Klima1TemperaturaProstora | REAL | 204 | EP2:.Klima[1].TemperaturaProstora
EP2Klima1TempIzpihanegaZraka | REAL | 205 | EP2:.Klima[1].TempIzpihanegaZraka
EP2Klima1TempPovratneVode | REAL | 206 | EP2:.Klima[1].TempPovratneVode
EP2Klima1ThermalCutoutHeater1 | DIGITAL | 207 | EP2:.Klima[1].ThermalCutoutHeater1
EP2Klima1ThermalCutoutHeater2 | DIGITAL | 208 | EP2:.Klima[1].ThermalCutoutHeater2
EP2Klima1UnitOnOff | DIGITAL | 209 | EP2:.Klima[1].UnitOnOff
EP2Klima1VentilatorNaMejiObrUr | DIGITAL | 210 | EP2:.Klima[1].VentilatorNaMejiObrUr
EP2Klima1VentilGretjeOdpiranje | DIGITAL | 211 | EP2:.Klima[1].VentilGretjeOdpiranje
EP2Klima1VentilGretjeZapiranje | DIGITAL | 212 | EP2:.Klima[1].VentilGretjeZapiranje
EP2Klima1VentilHlajenjeOdpiranje | DIGITAL | 213 | EP2:.Klima[1].VentilHlajenjeOdpiranje
EP2Klima1VentilHlajenjeZapiranje | DIGITAL | 214 | EP2:.Klima[1].VentilHlajenjeZapiranje
EP2Klima1VisokaTempPovratneVode | DIGITAL | 215 | EP2:.Klima[1].VisokaTempPovratneVode
EP2Klima1VisokaTempVProstoru | DIGITAL | 216 | EP2:.Klima[1].VisokaTempVProstoru
EP2Klima1VisokaVlaznost | DIGITAL | 217 | EP2:.Klima[1].VisokaVlaznost
EP2Klima1VisokTokVVlazilcu | DIGITAL | 218 | EP2:.Klima[1].VisokTokVVlazilcu
EP2Klima1Vlazenje | DIGITAL | 219 | EP2:.Klima[1].Vlazenje
EP2Klima1VlazilecStatus | BYTE | 220 | EP2:.Klima[1].VlazilecStatus
EP2Klima1VlaznostProstora | REAL | 221 | EP2:.Klima[1].VlaznostProstora
EP2Klima1ZamasenFilter | DIGITAL | 222 | EP2:.Klima[1].ZamasenFilter
EP2Klima1ZunanjaTemp | REAL | 223 | EP2:.Klima[1].ZunanjaTemp
EP2Klima2AlarmKompresor1 | DIGITAL | 224 | EP2:.Klima[2].AlarmKompresor1
EP2Klima2AlarmKompresor2 | DIGITAL | 225 | EP2:.Klima[2].AlarmKompresor2
EP2Klima2Deluje | DIGITAL | 226 | EP2:.Klima[2].Deluje
EP2Klima2EnergySaving | DIGITAL | 227 | EP2:.Klima[2].EnergySaving
EP2Klima2FaultyEPROM | DIGITAL | 228 | EP2:.Klima[2].FaultyEPROM
EP2Klima2FenThermalCutout | DIGITAL | 229 | EP2:.Klima[2].FenThermalCutout
EP2Klima2GeneralAlarm | DIGITAL | 230 | EP2:.Klima[2].GeneralAlarm
EP2Klima2GrelecStatus | BYTE | 231 | EP2:.Klima[2].GrelecStatus
EP2Klima2IzhodniVentStatus | BYTE | 232 | EP2:.Klima[2].IzhodniVentStatus
EP2Klima2Kompresor1naMejiObrUr | DIGITAL | 233 | EP2:.Klima[2].Kompresor1naMejiObrUr
EP2Klima2Kompresor2naMejiObrUr | DIGITAL | 234 | EP2:.Klima[2].Kompresor2naMejiObrUr
EP2Klima2KompresorStatus | BYTE | 235 | EP2:.Klima[2].KompresorStatus
EP2Klima2Napaka | DIGITAL | 236 | EP2:.Klima[2].Napaka
EP2Klima2NapakaPriPretokuZraka | DIGITAL | 237 | EP2:.Klima[2].NapakaPriPretokuZraka
EP2Klima2NapakaSenzorPovratVode | DIGITAL | 238 | EP2:.Klima[2].NapakaSenzorPovratVode
EP2Klima2NapakaSenzorTempIzpiha | DIGITAL | 239 | EP2:.Klima[2].NapakaSenzorTempIzpiha
EP2Klima2NapakaSenzorTempProstora | DIGITAL | 240 | EP2:.Klima[2].NapakaSenzorTempProstora
EP2Klima2NapakaSenzorVlaznosti | DIGITAL | 241 | EP2:.Klima[2].NapakaSenzorVlaznosti
EP2Klima2NapakaSenzorZunanjeTemp | DIGITAL | 242 | EP2:.Klima[2].NapakaSenzorZunanjeTemp
EP2Klima2NastMaxTemp | REAL | 243 | EP2:.Klima[2].NastMaxTemp
EP2Klima2NastMaxVlaznost | REAL | 244 | EP2:.Klima[2].NastMaxVlaznost
EP2Klima2NastMinTemp | REAL | 245 | EP2:.Klima[2].NastMinTemp
EP2Klima2NastMinVlaznost | REAL | 246 | EP2:.Klima[2].NastMinVlaznost
EP2Klima2NastTempProstora | REAL | 247 | EP2:.Klima[2].NastTempProstora
EP2Klima2NastVlaznost | REAL | 248 | EP2:.Klima[2].NastVlaznost
EP2Klima2NiTokaVVlazilcu | DIGITAL | 249 | EP2:.Klima[2].NiTokaVVlazilcu
EP2Klima2NiVodeVVlazilcu | DIGITAL | 250 | EP2:.Klima[2].NiVodeVVlazilcu
EP2Klima2NizekPritiskKompresor1 | DIGITAL | 251 | EP2:.Klima[2].NizekPritiskKompresor1
EP2Klima2NizekPritiskKompresor2 | DIGITAL | 252 | EP2:.Klima[2].NizekPritiskKompresor2
EP2Klima2NizkaTempPovratneVode | DIGITAL | 253 | EP2:.Klima[2].NizkaTempPovratneVode
EP2Klima2NizkaTempVProstoru | DIGITAL | 254 | EP2:.Klima[2].NizkaTempVProstoru
EP2Klima2NizkaVlaznost | DIGITAL | 255 | EP2:.Klima[2].NizkaVlaznost
EP2Klima2ObratovalneUre | REAL | 256 | EP2:.Klima[2].ObratovalneUre
EP2Klima2OnOffEnablingBySupervisor | DIGITAL | 257 | EP2:.Klima[2].OnOffEnablingBySupervisor
EP2Klima2PozarniAlarm | DIGITAL | 258 | EP2:.Klima[2].PozarniAlarm
EP2Klima2Razvlazevanje | DIGITAL | 259 | EP2:.Klima[2].Razvlazevanje
EP2Klima2RemoteOFFtoOutput | DIGITAL | 260 | EP2:.Klima[2].RemoteOFFtoOutput
EP2Klima2RemoteOnOff | DIGITAL | 261 | EP2:.Klima[2].RemoteOnOff
EP2Klima2RocniIzklop | DIGITAL | 262 | EP2:.Klima[2].RocniIzklop
EP2Klima2SenzorjiStatus | DIGITAL | 263 | EP2:.Klima[2].SenzorjiStatus
EP2Klima2StoppedByAlarms | DIGITAL | 264 | EP2:.Klima[2].StoppedByAlarms
EP2Klima2TemperaturaProstora | REAL | 265 | EP2:.Klima[2].TemperaturaProstora
EP2Klima2TempIzpihanegaZraka | REAL | 266 | EP2:.Klima[2].TempIzpihanegaZraka
EP2Klima2TempPovratneVode | REAL | 267 | EP2:.Klima[2].TempPovratneVode
EP2Klima2ThermalCutoutHeater1 | DIGITAL | 268 | EP2:.Klima[2].ThermalCutoutHeater1
EP2Klima2ThermalCutoutHeater2 | DIGITAL | 269 | EP2:.Klima[2].ThermalCutoutHeater2
EP2Klima2UnitOnOff | DIGITAL | 270 | EP2:.Klima[2].UnitOnOff
EP2Klima2VentilatorNaMejiObrUr | DIGITAL | 271 | EP2:.Klima[2].VentilatorNaMejiObrUr
EP2Klima2VentilGretjeOdpiranje | DIGITAL | 272 | EP2:.Klima[2].VentilGretjeOdpiranje
EP2Klima2VentilGretjeZapiranje | DIGITAL | 273 | EP2:.Klima[2].VentilGretjeZapiranje
EP2Klima2VentilHlajenjeOdpiranje | DIGITAL | 274 | EP2:.Klima[2].VentilHlajenjeOdpiranje
EP2Klima2VentilHlajenjeZapiranje | DIGITAL | 275 | EP2:.Klima[2].VentilHlajenjeZapiranje
EP2Klima2VisokaTempPovratneVode | DIGITAL | 276 | EP2:.Klima[2].VisokaTempPovratneVode
EP2Klima2VisokaTempVProstoru | DIGITAL | 277 | EP2:.Klima[2].VisokaTempVProstoru
EP2Klima2VisokaVlaznost | DIGITAL | 278 | EP2:.Klima[2].VisokaVlaznost
EP2Klima2VisokTokVVlazilcu | DIGITAL | 279 | EP2:.Klima[2].VisokTokVVlazilcu
EP2Klima2Vlazenje | DIGITAL | 280 | EP2:.Klima[2].Vlazenje
EP2Klima2VlazilecStatus | BYTE | 281 | EP2:.Klima[2].VlazilecStatus
EP2Klima2VlaznostProstora | REAL | 282 | EP2:.Klima[2].VlaznostProstora
EP2Klima2ZamasenFilter | DIGITAL | 283 | EP2:.Klima[2].ZamasenFilter
EP2Klima2ZunanjaTemp | REAL | 284 | EP2:.Klima[2].ZunanjaTemp
EP2KlimaAErrors10 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[10]
EP2KlimaAErrors11 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[11]
EP2KlimaAErrors12 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[12]
EP2KlimaAErrors13 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[13]
EP2KlimaAErrors14 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[14]
EP2KlimaAErrors15 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[15]
EP2KlimaAErrors16 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[16]
EP2KlimaAErrors17 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[17]
EP2KlimaAErrors18 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[18]
EP2KlimaAErrors19 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[19]
EP2KlimaAErrors1 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[1]
EP2KlimaAErrors20 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[20]
EP2KlimaAErrors21 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[21]
EP2KlimaAErrors22 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[22]
EP2KlimaAErrors23 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[23]
EP2KlimaAErrors24 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[24]
EP2KlimaAErrors25 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[25]
EP2KlimaAErrors26 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[26]
EP2KlimaAErrors27 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[27]
EP2KlimaAErrors28 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[28]
EP2KlimaAErrors29 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[29]
EP2KlimaAErrors2 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[2]
EP2KlimaAErrors30 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[30]
EP2KlimaAErrors31 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[31]
EP2KlimaAErrors32 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[32]
EP2KlimaAErrors33 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[33]
EP2KlimaAErrors34 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[34]
EP2KlimaAErrors35 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[35]
EP2KlimaAErrors36 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[36]
EP2KlimaAErrors37 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[37]
EP2KlimaAErrors38 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[38]
EP2KlimaAErrors39 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[39]
EP2KlimaAErrors3 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[3]
EP2KlimaAErrors40 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[40]
EP2KlimaAErrors4 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[4]
EP2KlimaAErrors5 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[5]
EP2KlimaAErrors6 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[6]
EP2KlimaAErrors7 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[7]
EP2KlimaAErrors8 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[8]
EP2KlimaAErrors9 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[9]
EP2KlimaBErrors10 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[10]
EP2KlimaBErrors11 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[11]
EP2KlimaBErrors12 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[12]
EP2KlimaBErrors13 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[13]
EP2KlimaBErrors14 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[14]
EP2KlimaBErrors15 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[15]
EP2KlimaBErrors16 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[16]
EP2KlimaBErrors17 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[17]
EP2KlimaBErrors18 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[18]
EP2KlimaBErrors19 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[19]
EP2KlimaBErrors1 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[1]
EP2KlimaBErrors20 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[20]
EP2KlimaBErrors21 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[21]
EP2KlimaBErrors22 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[22]
EP2KlimaBErrors23 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[23]
EP2KlimaBErrors24 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[24]
EP2KlimaBErrors25 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[25]
EP2KlimaBErrors26 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[26]
EP2KlimaBErrors27 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[27]
EP2KlimaBErrors28 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[28]
EP2KlimaBErrors29 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[29]
EP2KlimaBErrors2 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[2]
EP2KlimaBErrors30 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[30]
EP2KlimaBErrors31 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[31]
EP2KlimaBErrors32 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[32]
EP2KlimaBErrors33 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[33]
EP2KlimaBErrors34 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[34]
EP2KlimaBErrors35 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[35]
EP2KlimaBErrors36 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[36]
EP2KlimaBErrors37 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[37]
EP2KlimaBErrors38 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[38]
EP2KlimaBErrors39 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[39]
EP2KlimaBErrors3 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[3]
EP2KlimaBErrors40 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[40]
EP2KlimaBErrors4 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[4]
EP2KlimaBErrors5 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[5]
EP2KlimaBErrors6 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[6]
EP2KlimaBErrors7 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[7]
EP2KlimaBErrors8 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[8]
EP2KlimaBErrors9 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[9]
EP2KlimaGalAlarmKompresor1 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.AlarmKompresor1
EP2KlimaGalAlarmKompresor2 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.AlarmKompresor2
EP2KlimaGalDeluje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Deluje
EP2KlimaGalEnergySaving | DIGITAL | IOD_EP2 | EP2:.KlimaGal.EnergySaving
EP2KlimaGalFaultyEPROM | DIGITAL | IOD_EP2 | EP2:.KlimaGal.FaultyEPROM
EP2KlimaGalFenThermalCutout | DIGITAL | IOD_EP2 | EP2:.KlimaGal.FenThermalCutout
EP2KlimaGalGeneralAlarm | DIGITAL | IOD_EP2 | EP2:.KlimaGal.GeneralAlarm
EP2KlimaGalGrelecStatus | BYTE | IOD_EP2 | EP2:.KlimaGal.GrelecStatus
EP2KlimaGalIzhodniVentStatus | BYTE | IOD_EP2 | EP2:.KlimaGal.IzhodniVentStatus
EP2KlimaGalKompresor1naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Kompresor1naMejiObrUr
EP2KlimaGalKompresor2naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Kompresor2naMejiObrUr
EP2KlimaGalKompresorStatus | BYTE | IOD_EP2 | EP2:.KlimaGal.KompresorStatus
EP2KlimaGalNapaka | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Napaka
EP2KlimaGalNapakaPriPretokuZraka | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaPriPretokuZraka
EP2KlimaGalNapakaSenzorPovratVode | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaSenzorPovratVode
EP2KlimaGalNapakaSenzorTempIzpiha | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaSenzorTempIzpiha
EP2KlimaGalNapakaSenzorTempProstora | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaSenzorTempProstora
EP2KlimaGalNapakaSenzorVlaznosti | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaSenzorVlaznosti
EP2KlimaGalNapakaSenzorZunanjeTemp | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaSenzorZunanjeTemp
EP2KlimaGalNastMaxTemp | REAL | IOD_EP2 | EP2:.KlimaGal.NastMaxTemp
EP2KlimaGalNastMaxVlaznost | REAL | IOD_EP2 | EP2:.KlimaGal.NastMaxVlaznost
EP2KlimaGalNastMinTemp | REAL | IOD_EP2 | EP2:.KlimaGal.NastMinTemp
EP2KlimaGalNastMinVlaznost | REAL | IOD_EP2 | EP2:.KlimaGal.NastMinVlaznost
EP2KlimaGalNastTempProstora | REAL | IOD_EP2 | EP2:.KlimaGal.NastTempProstora
EP2KlimaGalNastVlaznost | REAL | IOD_EP2 | EP2:.KlimaGal.NastVlaznost
EP2KlimaGalNiTokaVVlazilcu | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NiTokaVVlazilcu
EP2KlimaGalNiVodeVVlazilcu | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NiVodeVVlazilcu
EP2KlimaGalNizekPritiskKompresor1 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NizekPritiskKompresor1
EP2KlimaGalNizekPritiskKompresor2 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NizekPritiskKompresor2
EP2KlimaGalNizkaTempPovratneVode | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NizkaTempPovratneVode
EP2KlimaGalNizkaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NizkaTempVProstoru
EP2KlimaGalNizkaVlaznost | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NizkaVlaznost
EP2KlimaGalObratovalneUre | REAL | IOD_EP2 | EP2:.KlimaGal.ObratovalneUre
EP2KlimaGalOnOffEnablingBySupervisor | DIGITAL | IOD_EP2 | EP2:.KlimaGal.OnOffEnablingBySupervisor
EP2KlimaGalPozarniAlarm | DIGITAL | IOD_EP2 | EP2:.KlimaGal.PozarniAlarm
EP2KlimaGalRazvlazevanje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Razvlazevanje
EP2KlimaGalRemoteOFFtoOutput | DIGITAL | IOD_EP2 | EP2:.KlimaGal.RemoteOFFtoOutput
EP2KlimaGalRemoteOnOff | DIGITAL | IOD_EP2 | EP2:.KlimaGal.RemoteOnOff
EP2KlimaGalRocniIzklop | DIGITAL | IOD_EP2 | EP2:.KlimaGal.RocniIzklop
EP2KlimaGalSenzorjiStatus | DIGITAL | IOD_EP2 | EP2:.KlimaGal.SenzorjiStatus
EP2KlimaGalStoppedByAlarms | DIGITAL | IOD_EP2 | EP2:.KlimaGal.StoppedByAlarms
EP2KlimaGalTemperaturaProstora | REAL | IOD_EP2 | EP2:.KlimaGal.TemperaturaProstora
EP2KlimaGalTempIzpihanegaZraka | REAL | IOD_EP2 | EP2:.KlimaGal.TempIzpihanegaZraka
EP2KlimaGalTempPovratneVode | REAL | IOD_EP2 | EP2:.KlimaGal.TempPovratneVode
EP2KlimaGalThermalCutoutHeater1 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.ThermalCutoutHeater1
EP2KlimaGalThermalCutoutHeater2 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.ThermalCutoutHeater2
EP2KlimaGalUnitOnOff | DIGITAL | IOD_EP2 | EP2:.KlimaGal.UnitOnOff
EP2KlimaGalVentilatorNaMejiObrUr | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VentilatorNaMejiObrUr
EP2KlimaGalVentilGretjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VentilGretjeOdpiranje
EP2KlimaGalVentilGretjeZapiranje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VentilGretjeZapiranje
EP2KlimaGalVentilHlajenjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VentilHlajenjeOdpiranje
EP2KlimaGalVentilHlajenjeZapiranje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VentilHlajenjeZapiranje
EP2KlimaGalVisokaTempPovratneVode | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VisokaTempPovratneVode
EP2KlimaGalVisokaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VisokaTempVProstoru
EP2KlimaGalVisokaVlaznost | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VisokaVlaznost
EP2KlimaGalVisokTokVVlazilcu | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VisokTokVVlazilcu
EP2KlimaGalVlazenje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Vlazenje
EP2KlimaGalVlazilecStatus | BYTE | IOD_EP2 | EP2:.KlimaGal.VlazilecStatus
EP2KlimaGalVlaznostProstora | REAL | IOD_EP2 | EP2:.KlimaGal.VlaznostProstora
EP2KlimaGalZamasenFilter | DIGITAL | IOD_EP2 | EP2:.KlimaGal.ZamasenFilter
EP2KlimaGalZunanjaTemp | REAL | IOD_EP2 | EP2:.KlimaGal.ZunanjaTemp
EP2KlimeNaCas | DIGITAL | 285 | EP2:.KlimeNaCas
EP2NapakaSenzorTemp1 | DIGITAL | 286 | EP2:.NapakaSenzorTemp[1]
EP2NapakaSenzorTemp2 | DIGITAL | 287 | EP2:.NapakaSenzorTemp[2]
EP2NapakaSenzorVlaga1 | DIGITAL | 288 | EP2:.NapakaSenzorVlaga[1]
EP2NapakaSenzorVlaga2 | DIGITAL | 289 | EP2:.NapakaSenzorVlaga[2]
EP2PMM1OverCurrentBetw1 | DIGITAL | 290 | EP2:.PMM1OverCurrentBetw[1]
EP2PMM1OverCurrentBetw2 | DIGITAL | 291 | EP2:.PMM1OverCurrentBetw[2]
EP2PMM1OverCurrentBetw3 | DIGITAL | 292 | EP2:.PMM1OverCurrentBetw[3]
EP2PMM1OverCurrentOver1 | DIGITAL | 293 | EP2:.PMM1OverCurrentOver[1]
EP2PMM1OverCurrentOver2 | DIGITAL | 294 | EP2:.PMM1OverCurrentOver[2]
EP2PMM1OverCurrentOver3 | DIGITAL | 295 | EP2:.PMM1OverCurrentOver[3]
EP2PMM1OverVoltage | DIGITAL | IOD_EP2 | EP2:.PMM1OverVoltage
EP2PMM2OverCurrentBetw1 | DIGITAL | 296 | EP2:.PMM2OverCurrentBetw[1]
EP2PMM2OverCurrentBetw2 | DIGITAL | 297 | EP2:.PMM2OverCurrentBetw[2]
EP2PMM2OverCurrentBetw3 | DIGITAL | 298 | EP2:.PMM2OverCurrentBetw[3]
EP2PMM2OverCurrentOver1 | DIGITAL | 299 | EP2:.PMM2OverCurrentOver[1]
EP2PMM2OverCurrentOver2 | DIGITAL | 300 | EP2:.PMM2OverCurrentOver[2]
EP2PMM2OverCurrentOver3 | DIGITAL | 301 | EP2:.PMM2OverCurrentOver[3]
EP2PMM2OverVoltage | DIGITAL | IOD_EP2 | EP2:.PMM2OverVoltage
EP2PMM3OverCurrentBetw1 | DIGITAL | 302 | EP2:.PMM3OverCurrentBetw[1]
EP2PMM3OverCurrentBetw2 | DIGITAL | 303 | EP2:.PMM3OverCurrentBetw[2]
EP2PMM3OverCurrentBetw3 | DIGITAL | 304 | EP2:.PMM3OverCurrentBetw[3]
EP2PMM3OverCurrentOver1 | DIGITAL | 305 | EP2:.PMM3OverCurrentOver[1]
EP2PMM3OverCurrentOver2 | DIGITAL | 306 | EP2:.PMM3OverCurrentOver[2]
EP2PMM3OverCurrentOver3 | DIGITAL | 307 | EP2:.PMM3OverCurrentOver[3]
EP2PMM3OverVoltage | DIGITAL | IOD_EP2 | EP2:.PMM3OverVoltage
EP2PMM1ActivePowerPhaseA_kW | REAL | 308 | EP2:.PMM[1].ActivePowerPhaseA_kW
EP2PMM1ActivePowerPhaseB_kW | REAL | 309 | EP2:.PMM[1].ActivePowerPhaseB_kW
EP2PMM1ActivePowerPhaseC_kW | REAL | 310 | EP2:.PMM[1].ActivePowerPhaseC_kW
EP2PMM1AlarmPhase1C01_16_60to80 | UINT | 311 | EP2:.PMM[1].AlarmPhase[1].C01_16_60to80
EP2PMM1AlarmPhase1C01_16_over80 | UINT | 312 | EP2:.PMM[1].AlarmPhase[1].C01_16_over80
EP2PMM1AlarmPhase1C17_32_60to80 | UINT | 313 | EP2:.PMM[1].AlarmPhase[1].C17_32_60to80
EP2PMM1AlarmPhase1C17_32_over80 | UINT | 314 | EP2:.PMM[1].AlarmPhase[1].C17_32_over80
EP2PMM1AlarmPhase1C33_42_60to80 | UINT | 315 | EP2:.PMM[1].AlarmPhase[1].C33_42_60to80
EP2PMM1AlarmPhase1C33_42_over80 | UINT | 316 | EP2:.PMM[1].AlarmPhase[1].C33_42_over80
EP2PMM1AlarmPhase1GlobalAlarmReg | INT | 317 | EP2:.PMM[1].AlarmPhase[1].GlobalAlarmReg
EP2PMM1AlarmPhase2C01_16_60to80 | UINT | 318 | EP2:.PMM[1].AlarmPhase[2].C01_16_60to80
EP2PMM1AlarmPhase2C01_16_over80 | UINT | 319 | EP2:.PMM[1].AlarmPhase[2].C01_16_over80
EP2PMM1AlarmPhase2C17_32_60to80 | UINT | 320 | EP2:.PMM[1].AlarmPhase[2].C17_32_60to80
EP2PMM1AlarmPhase2C17_32_over80 | UINT | 321 | EP2:.PMM[1].AlarmPhase[2].C17_32_over80
EP2PMM1AlarmPhase2C33_42_60to80 | UINT | 322 | EP2:.PMM[1].AlarmPhase[2].C33_42_60to80
EP2PMM1AlarmPhase2C33_42_over80 | UINT | 323 | EP2:.PMM[1].AlarmPhase[2].C33_42_over80
EP2PMM1AlarmPhase2GlobalAlarmReg | INT | 324 | EP2:.PMM[1].AlarmPhase[2].GlobalAlarmReg
EP2PMM1AlarmPhase3C01_16_60to80 | UINT | 325 | EP2:.PMM[1].AlarmPhase[3].C01_16_60to80
EP2PMM1AlarmPhase3C01_16_over80 | UINT | 326 | EP2:.PMM[1].AlarmPhase[3].C01_16_over80
EP2PMM1AlarmPhase3C17_32_60to80 | UINT | 327 | EP2:.PMM[1].AlarmPhase[3].C17_32_60to80
EP2PMM1AlarmPhase3C17_32_over80 | UINT | 328 | EP2:.PMM[1].AlarmPhase[3].C17_32_over80
EP2PMM1AlarmPhase3C33_42_60to80 | UINT | 329 | EP2:.PMM[1].AlarmPhase[3].C33_42_60to80
EP2PMM1AlarmPhase3C33_42_over80 | UINT | 330 | EP2:.PMM[1].AlarmPhase[3].C33_42_over80
EP2PMM1AlarmPhase3GlobalAlarmReg | INT | 331 | EP2:.PMM[1].AlarmPhase[3].GlobalAlarmReg
EP2PMM1Alarms | UINT | 332 | EP2:.PMM[1].Alarms
EP2PMM1AverageCurrent_A | REAL | 333 | EP2:.PMM[1].AverageCurrent_A
EP2PMM1AveragePhaseToNeutral_V | REAL | 334 | EP2:.PMM[1].AveragePhaseToNeutral_V
EP2PMM1AveragePhaseToPhase_V | REAL | 335 | EP2:.PMM[1].AveragePhaseToPhase_V
EP2PMM1CurrentInPhaseA_A | REAL | 336 | EP2:.PMM[1].CurrentInPhaseA_A
EP2PMM1CurrentInPhaseB_A | REAL | 337 | EP2:.PMM[1].CurrentInPhaseB_A
EP2PMM1CurrentInPhaseC_A | REAL | 338 | EP2:.PMM[1].CurrentInPhaseC_A
EP2PMM1EnergyConsumed_kWh | REAL | 339 | EP2:.PMM[1].EnergyConsumed_kWh
EP2PMM1Frequency_Hz | REAL | 341 | EP2:.PMM[1].Frequency_Hz
EP2PMM1Napaka | DIGITAL | 340 | EP2:.PMM[1].Napaka
EP2PMM1NeutralCurrent_A | REAL | 342 | EP2:.PMM[1].NeutralCurrent_A
EP2PMM1Phase1Current10 | REAL | 343 | EP2:.PMM[1].Phase[1].Current[10]
EP2PMM1Phase1Current11 | REAL | 344 | EP2:.PMM[1].Phase[1].Current[11]
EP2PMM1Phase1Current12 | REAL | 345 | EP2:.PMM[1].Phase[1].Current[12]
EP2PMM1Phase1Current13 | REAL | 346 | EP2:.PMM[1].Phase[1].Current[13]
EP2PMM1Phase1Current14 | REAL | 347 | EP2:.PMM[1].Phase[1].Current[14]
EP2PMM1Phase1Current15 | REAL | 348 | EP2:.PMM[1].Phase[1].Current[15]
EP2PMM1Phase1Current16 | REAL | 349 | EP2:.PMM[1].Phase[1].Current[16]
EP2PMM1Phase1Current17 | REAL | 350 | EP2:.PMM[1].Phase[1].Current[17]
EP2PMM1Phase1Current18 | REAL | 351 | EP2:.PMM[1].Phase[1].Current[18]
EP2PMM1Phase1Current19 | REAL | 352 | EP2:.PMM[1].Phase[1].Current[19]
EP2PMM1Phase1Current1 | REAL | 353 | EP2:.PMM[1].Phase[1].Current[1]
EP2PMM1Phase1Current20 | REAL | 354 | EP2:.PMM[1].Phase[1].Current[20]
EP2PMM1Phase1Current21 | REAL | 355 | EP2:.PMM[1].Phase[1].Current[21]
EP2PMM1Phase1Current22 | REAL | 356 | EP2:.PMM[1].Phase[1].Current[22]
EP2PMM1Phase1Current23 | REAL | 357 | EP2:.PMM[1].Phase[1].Current[23]
EP2PMM1Phase1Current24 | REAL | 358 | EP2:.PMM[1].Phase[1].Current[24]
EP2PMM1Phase1Current25 | REAL | 359 | EP2:.PMM[1].Phase[1].Current[25]
EP2PMM1Phase1Current26 | REAL | 360 | EP2:.PMM[1].Phase[1].Current[26]
EP2PMM1Phase1Current27 | REAL | 361 | EP2:.PMM[1].Phase[1].Current[27]
EP2PMM1Phase1Current28 | REAL | 362 | EP2:.PMM[1].Phase[1].Current[28]
EP2PMM1Phase1Current29 | REAL | 363 | EP2:.PMM[1].Phase[1].Current[29]
EP2PMM1Phase1Current2 | REAL | 364 | EP2:.PMM[1].Phase[1].Current[2]
EP2PMM1Phase1Current30 | REAL | 365 | EP2:.PMM[1].Phase[1].Current[30]
EP2PMM1Phase1Current31 | REAL | 366 | EP2:.PMM[1].Phase[1].Current[31]
EP2PMM1Phase1Current32 | REAL | 367 | EP2:.PMM[1].Phase[1].Current[32]
EP2PMM1Phase1Current33 | REAL | 368 | EP2:.PMM[1].Phase[1].Current[33]
EP2PMM1Phase1Current34 | REAL | 369 | EP2:.PMM[1].Phase[1].Current[34]
EP2PMM1Phase1Current35 | REAL | 370 | EP2:.PMM[1].Phase[1].Current[35]
EP2PMM1Phase1Current36 | REAL | 371 | EP2:.PMM[1].Phase[1].Current[36]
EP2PMM1Phase1Current37 | REAL | 372 | EP2:.PMM[1].Phase[1].Current[37]
EP2PMM1Phase1Current38 | REAL | 373 | EP2:.PMM[1].Phase[1].Current[38]
EP2PMM1Phase1Current39 | REAL | 374 | EP2:.PMM[1].Phase[1].Current[39]
EP2PMM1Phase1Current3 | REAL | 375 | EP2:.PMM[1].Phase[1].Current[3]
EP2PMM1Phase1Current40 | REAL | 376 | EP2:.PMM[1].Phase[1].Current[40]
EP2PMM1Phase1Current41 | REAL | 377 | EP2:.PMM[1].Phase[1].Current[41]
EP2PMM1Phase1Current42 | REAL | 378 | EP2:.PMM[1].Phase[1].Current[42]
EP2PMM1Phase1Current4 | REAL | 379 | EP2:.PMM[1].Phase[1].Current[4]
EP2PMM1Phase1Current5 | REAL | 380 | EP2:.PMM[1].Phase[1].Current[5]
EP2PMM1Phase1Current6 | REAL | 381 | EP2:.PMM[1].Phase[1].Current[6]
EP2PMM1Phase1Current7 | REAL | 382 | EP2:.PMM[1].Phase[1].Current[7]
EP2PMM1Phase1Current8 | REAL | 383 | EP2:.PMM[1].Phase[1].Current[8]
EP2PMM1Phase1Current9 | REAL | 384 | EP2:.PMM[1].Phase[1].Current[9]
EP2PMM1Phase2Current10 | REAL | 385 | EP2:.PMM[1].Phase[2].Current[10]
EP2PMM1Phase2Current11 | REAL | 386 | EP2:.PMM[1].Phase[2].Current[11]
EP2PMM1Phase2Current12 | REAL | 387 | EP2:.PMM[1].Phase[2].Current[12]
EP2PMM1Phase2Current13 | REAL | 388 | EP2:.PMM[1].Phase[2].Current[13]
EP2PMM1Phase2Current14 | REAL | 389 | EP2:.PMM[1].Phase[2].Current[14]
EP2PMM1Phase2Current15 | REAL | 390 | EP2:.PMM[1].Phase[2].Current[15]
EP2PMM1Phase2Current16 | REAL | 391 | EP2:.PMM[1].Phase[2].Current[16]
EP2PMM1Phase2Current17 | REAL | 392 | EP2:.PMM[1].Phase[2].Current[17]
EP2PMM1Phase2Current18 | REAL | 393 | EP2:.PMM[1].Phase[2].Current[18]
EP2PMM1Phase2Current19 | REAL | 394 | EP2:.PMM[1].Phase[2].Current[19]
EP2PMM1Phase2Current1 | REAL | 395 | EP2:.PMM[1].Phase[2].Current[1]
EP2PMM1Phase2Current20 | REAL | 396 | EP2:.PMM[1].Phase[2].Current[20]
EP2PMM1Phase2Current21 | REAL | 397 | EP2:.PMM[1].Phase[2].Current[21]
EP2PMM1Phase2Current22 | REAL | 398 | EP2:.PMM[1].Phase[2].Current[22]
EP2PMM1Phase2Current23 | REAL | 399 | EP2:.PMM[1].Phase[2].Current[23]
EP2PMM1Phase2Current24 | REAL | 400 | EP2:.PMM[1].Phase[2].Current[24]
EP2PMM1Phase2Current25 | REAL | 401 | EP2:.PMM[1].Phase[2].Current[25]
EP2PMM1Phase2Current26 | REAL | 402 | EP2:.PMM[1].Phase[2].Current[26]
EP2PMM1Phase2Current27 | REAL | 403 | EP2:.PMM[1].Phase[2].Current[27]
EP2PMM1Phase2Current28 | REAL | 404 | EP2:.PMM[1].Phase[2].Current[28]
EP2PMM1Phase2Current29 | REAL | 405 | EP2:.PMM[1].Phase[2].Current[29]
EP2PMM1Phase2Current2 | REAL | 406 | EP2:.PMM[1].Phase[2].Current[2]
EP2PMM1Phase2Current30 | REAL | 407 | EP2:.PMM[1].Phase[2].Current[30]
EP2PMM1Phase2Current31 | REAL | 408 | EP2:.PMM[1].Phase[2].Current[31]
EP2PMM1Phase2Current32 | REAL | 409 | EP2:.PMM[1].Phase[2].Current[32]
EP2PMM1Phase2Current33 | REAL | 410 | EP2:.PMM[1].Phase[2].Current[33]
EP2PMM1Phase2Current34 | REAL | 411 | EP2:.PMM[1].Phase[2].Current[34]
EP2PMM1Phase2Current35 | REAL | 412 | EP2:.PMM[1].Phase[2].Current[35]
EP2PMM1Phase2Current36 | REAL | 413 | EP2:.PMM[1].Phase[2].Current[36]
EP2PMM1Phase2Current37 | REAL | 414 | EP2:.PMM[1].Phase[2].Current[37]
EP2PMM1Phase2Current38 | REAL | 415 | EP2:.PMM[1].Phase[2].Current[38]
EP2PMM1Phase2Current39 | REAL | 416 | EP2:.PMM[1].Phase[2].Current[39]
EP2PMM1Phase2Current3 | REAL | 417 | EP2:.PMM[1].Phase[2].Current[3]
EP2PMM1Phase2Current40 | REAL | 418 | EP2:.PMM[1].Phase[2].Current[40]
EP2PMM1Phase2Current41 | REAL | 419 | EP2:.PMM[1].Phase[2].Current[41]
EP2PMM1Phase2Current42 | REAL | 420 | EP2:.PMM[1].Phase[2].Current[42]
EP2PMM1Phase2Current4 | REAL | 421 | EP2:.PMM[1].Phase[2].Current[4]
EP2PMM1Phase2Current5 | REAL | 422 | EP2:.PMM[1].Phase[2].Current[5]
EP2PMM1Phase2Current6 | REAL | 423 | EP2:.PMM[1].Phase[2].Current[6]
EP2PMM1Phase2Current7 | REAL | 424 | EP2:.PMM[1].Phase[2].Current[7]
EP2PMM1Phase2Current8 | REAL | 425 | EP2:.PMM[1].Phase[2].Current[8]
EP2PMM1Phase2Current9 | REAL | 426 | EP2:.PMM[1].Phase[2].Current[9]
EP2PMM1Phase3Current10 | REAL | 427 | EP2:.PMM[1].Phase[3].Current[10]
EP2PMM1Phase3Current11 | REAL | 428 | EP2:.PMM[1].Phase[3].Current[11]
EP2PMM1Phase3Current12 | REAL | 429 | EP2:.PMM[1].Phase[3].Current[12]
EP2PMM1Phase3Current13 | REAL | 430 | EP2:.PMM[1].Phase[3].Current[13]
EP2PMM1Phase3Current14 | REAL | 431 | EP2:.PMM[1].Phase[3].Current[14]
EP2PMM1Phase3Current15 | REAL | 432 | EP2:.PMM[1].Phase[3].Current[15]
EP2PMM1Phase3Current16 | REAL | 433 | EP2:.PMM[1].Phase[3].Current[16]
EP2PMM1Phase3Current17 | REAL | 434 | EP2:.PMM[1].Phase[3].Current[17]
EP2PMM1Phase3Current18 | REAL | 435 | EP2:.PMM[1].Phase[3].Current[18]
EP2PMM1Phase3Current19 | REAL | 436 | EP2:.PMM[1].Phase[3].Current[19]
EP2PMM1Phase3Current1 | REAL | 437 | EP2:.PMM[1].Phase[3].Current[1]
EP2PMM1Phase3Current20 | REAL | 438 | EP2:.PMM[1].Phase[3].Current[20]
EP2PMM1Phase3Current21 | REAL | 439 | EP2:.PMM[1].Phase[3].Current[21]
EP2PMM1Phase3Current22 | REAL | 440 | EP2:.PMM[1].Phase[3].Current[22]
EP2PMM1Phase3Current23 | REAL | 441 | EP2:.PMM[1].Phase[3].Current[23]
EP2PMM1Phase3Current24 | REAL | 442 | EP2:.PMM[1].Phase[3].Current[24]
EP2PMM1Phase3Current25 | REAL | 443 | EP2:.PMM[1].Phase[3].Current[25]
EP2PMM1Phase3Current26 | REAL | 444 | EP2:.PMM[1].Phase[3].Current[26]
EP2PMM1Phase3Current27 | REAL | 445 | EP2:.PMM[1].Phase[3].Current[27]
EP2PMM1Phase3Current28 | REAL | 446 | EP2:.PMM[1].Phase[3].Current[28]
EP2PMM1Phase3Current29 | REAL | 447 | EP2:.PMM[1].Phase[3].Current[29]
EP2PMM1Phase3Current2 | REAL | 448 | EP2:.PMM[1].Phase[3].Current[2]
EP2PMM1Phase3Current30 | REAL | 449 | EP2:.PMM[1].Phase[3].Current[30]
EP2PMM1Phase3Current31 | REAL | 450 | EP2:.PMM[1].Phase[3].Current[31]
EP2PMM1Phase3Current32 | REAL | 451 | EP2:.PMM[1].Phase[3].Current[32]
EP2PMM1Phase3Current33 | REAL | 452 | EP2:.PMM[1].Phase[3].Current[33]
EP2PMM1Phase3Current34 | REAL | 453 | EP2:.PMM[1].Phase[3].Current[34]
EP2PMM1Phase3Current35 | REAL | 454 | EP2:.PMM[1].Phase[3].Current[35]
EP2PMM1Phase3Current36 | REAL | 455 | EP2:.PMM[1].Phase[3].Current[36]
EP2PMM1Phase3Current37 | REAL | 456 | EP2:.PMM[1].Phase[3].Current[37]
EP2PMM1Phase3Current38 | REAL | 457 | EP2:.PMM[1].Phase[3].Current[38]
EP2PMM1Phase3Current39 | REAL | 458 | EP2:.PMM[1].Phase[3].Current[39]
EP2PMM1Phase3Current3 | REAL | 459 | EP2:.PMM[1].Phase[3].Current[3]
EP2PMM1Phase3Current40 | REAL | 460 | EP2:.PMM[1].Phase[3].Current[40]
EP2PMM1Phase3Current41 | REAL | 461 | EP2:.PMM[1].Phase[3].Current[41]
EP2PMM1Phase3Current42 | REAL | 462 | EP2:.PMM[1].Phase[3].Current[42]
EP2PMM1Phase3Current4 | REAL | 463 | EP2:.PMM[1].Phase[3].Current[4]
EP2PMM1Phase3Current5 | REAL | 464 | EP2:.PMM[1].Phase[3].Current[5]
EP2PMM1Phase3Current6 | REAL | 465 | EP2:.PMM[1].Phase[3].Current[6]
EP2PMM1Phase3Current7 | REAL | 466 | EP2:.PMM[1].Phase[3].Current[7]
EP2PMM1Phase3Current8 | REAL | 467 | EP2:.PMM[1].Phase[3].Current[8]
EP2PMM1Phase3Current9 | REAL | 468 | EP2:.PMM[1].Phase[3].Current[9]
EP2PMM1PowerFactorPhaseA | REAL | 469 | EP2:.PMM[1].PowerFactorPhaseA
EP2PMM1PowerFactorPhaseB | REAL | 470 | EP2:.PMM[1].PowerFactorPhaseB
EP2PMM1PowerFactorPhaseC | REAL | 471 | EP2:.PMM[1].PowerFactorPhaseC
EP2PMM1TotalActivePower_kW | REAL | 472 | EP2:.PMM[1].TotalActivePower_kW
EP2PMM1TotalAparentPower_kVA | REAL | 473 | EP2:.PMM[1].TotalAparentPower_kVA
EP2PMM1TotalPowerFactor | REAL | 474 | EP2:.PMM[1].TotalPowerFactor
EP2PMM1TotalReactivePower_kVAR | REAL | 475 | EP2:.PMM[1].TotalReactivePower_kVAR
EP2PMM1VoltageBetweenPhaseAB_V | REAL | 476 | EP2:.PMM[1].VoltageBetweenPhaseAB_V
EP2PMM1VoltageBetweenPhaseAN_V | REAL | 477 | EP2:.PMM[1].VoltageBetweenPhaseAN_V
EP2PMM1VoltageBetweenPhaseBC_V | REAL | 478 | EP2:.PMM[1].VoltageBetweenPhaseBC_V
EP2PMM1VoltageBetweenPhaseBN_V | REAL | 479 | EP2:.PMM[1].VoltageBetweenPhaseBN_V
EP2PMM1VoltageBetweenPhaseCA_V | REAL | 480 | EP2:.PMM[1].VoltageBetweenPhaseCA_V
EP2PMM1VoltageBetweenPhaseCN_V | REAL | 481 | EP2:.PMM[1].VoltageBetweenPhaseCN_V
EP2PMM2ActivePowerPhaseA_kW | REAL | 482 | EP2:.PMM[2].ActivePowerPhaseA_kW
EP2PMM2ActivePowerPhaseB_kW | REAL | 483 | EP2:.PMM[2].ActivePowerPhaseB_kW
EP2PMM2ActivePowerPhaseC_kW | REAL | 484 | EP2:.PMM[2].ActivePowerPhaseC_kW
EP2PMM2AlarmPhase1C01_16_60to80 | UINT | 485 | EP2:.PMM[2].AlarmPhase[1].C01_16_60to80
EP2PMM2AlarmPhase1C01_16_over80 | UINT | 486 | EP2:.PMM[2].AlarmPhase[1].C01_16_over80
EP2PMM2AlarmPhase1C17_32_60to80 | UINT | 487 | EP2:.PMM[2].AlarmPhase[1].C17_32_60to80
EP2PMM2AlarmPhase1C17_32_over80 | UINT | 488 | EP2:.PMM[2].AlarmPhase[1].C17_32_over80
EP2PMM2AlarmPhase1C33_42_60to80 | UINT | 489 | EP2:.PMM[2].AlarmPhase[1].C33_42_60to80
EP2PMM2AlarmPhase1C33_42_over80 | UINT | 490 | EP2:.PMM[2].AlarmPhase[1].C33_42_over80
EP2PMM2AlarmPhase1GlobalAlarmReg | INT | 491 | EP2:.PMM[2].AlarmPhase[1].GlobalAlarmReg
EP2PMM2AlarmPhase2C01_16_60to80 | UINT | 492 | EP2:.PMM[2].AlarmPhase[2].C01_16_60to80
EP2PMM2AlarmPhase2C01_16_over80 | UINT | 493 | EP2:.PMM[2].AlarmPhase[2].C01_16_over80
EP2PMM2AlarmPhase2C17_32_60to80 | UINT | 494 | EP2:.PMM[2].AlarmPhase[2].C17_32_60to80
EP2PMM2AlarmPhase2C17_32_over80 | UINT | 495 | EP2:.PMM[2].AlarmPhase[2].C17_32_over80
EP2PMM2AlarmPhase2C33_42_60to80 | UINT | 496 | EP2:.PMM[2].AlarmPhase[2].C33_42_60to80
EP2PMM2AlarmPhase2C33_42_over80 | UINT | 497 | EP2:.PMM[2].AlarmPhase[2].C33_42_over80
EP2PMM2AlarmPhase2GlobalAlarmReg | INT | 498 | EP2:.PMM[2].AlarmPhase[2].GlobalAlarmReg
EP2PMM2AlarmPhase3C01_16_60to80 | UINT | 499 | EP2:.PMM[2].AlarmPhase[3].C01_16_60to80
EP2PMM2AlarmPhase3C01_16_over80 | UINT | 500 | EP2:.PMM[2].AlarmPhase[3].C01_16_over80
EP2PMM2AlarmPhase3C17_32_60to80 | UINT | 501 | EP2:.PMM[2].AlarmPhase[3].C17_32_60to80
EP2PMM2AlarmPhase3C17_32_over80 | UINT | 502 | EP2:.PMM[2].AlarmPhase[3].C17_32_over80
EP2PMM2AlarmPhase3C33_42_60to80 | UINT | 503 | EP2:.PMM[2].AlarmPhase[3].C33_42_60to80
EP2PMM2AlarmPhase3C33_42_over80 | UINT | 504 | EP2:.PMM[2].AlarmPhase[3].C33_42_over80
EP2PMM2AlarmPhase3GlobalAlarmReg | INT | 505 | EP2:.PMM[2].AlarmPhase[3].GlobalAlarmReg
EP2PMM2Alarms | UINT | 506 | EP2:.PMM[2].Alarms
EP2PMM2AverageCurrent_A | REAL | 507 | EP2:.PMM[2].AverageCurrent_A
EP2PMM2AveragePhaseToNeutral_V | REAL | 508 | EP2:.PMM[2].AveragePhaseToNeutral_V
EP2PMM2AveragePhaseToPhase_V | REAL | 509 | EP2:.PMM[2].AveragePhaseToPhase_V
EP2PMM2CurrentInPhaseA_A | REAL | 510 | EP2:.PMM[2].CurrentInPhaseA_A
EP2PMM2CurrentInPhaseB_A | REAL | 511 | EP2:.PMM[2].CurrentInPhaseB_A
EP2PMM2CurrentInPhaseC_A | REAL | 512 | EP2:.PMM[2].CurrentInPhaseC_A
EP2PMM2EnergyConsumed_kWh | REAL | 513 | EP2:.PMM[2].EnergyConsumed_kWh
EP2PMM2Frequency_Hz | REAL | 514 | EP2:.PMM[2].Frequency_Hz
EP2PMM2Napaka | DIGITAL | 515 | EP2:.PMM[2].Napaka
EP2PMM2NeutralCurrent_A | REAL | 516 | EP2:.PMM[2].NeutralCurrent_A
EP2PMM2Phase1Current10 | REAL | 517 | EP2:.PMM[2].Phase[1].Current[10]
EP2PMM2Phase1Current11 | REAL | 518 | EP2:.PMM[2].Phase[1].Current[11]
EP2PMM2Phase1Current12 | REAL | 519 | EP2:.PMM[2].Phase[1].Current[12]
EP2PMM2Phase1Current13 | REAL | 520 | EP2:.PMM[2].Phase[1].Current[13]
EP2PMM2Phase1Current14 | REAL | 521 | EP2:.PMM[2].Phase[1].Current[14]
EP2PMM2Phase1Current15 | REAL | 522 | EP2:.PMM[2].Phase[1].Current[15]
EP2PMM2Phase1Current16 | REAL | 523 | EP2:.PMM[2].Phase[1].Current[16]
EP2PMM2Phase1Current17 | REAL | 524 | EP2:.PMM[2].Phase[1].Current[17]
EP2PMM2Phase1Current18 | REAL | 525 | EP2:.PMM[2].Phase[1].Current[18]
EP2PMM2Phase1Current19 | REAL | 526 | EP2:.PMM[2].Phase[1].Current[19]
EP2PMM2Phase1Current1 | REAL | 527 | EP2:.PMM[2].Phase[1].Current[1]
EP2PMM2Phase1Current20 | REAL | 528 | EP2:.PMM[2].Phase[1].Current[20]
EP2PMM2Phase1Current21 | REAL | 529 | EP2:.PMM[2].Phase[1].Current[21]
EP2PMM2Phase1Current22 | REAL | 530 | EP2:.PMM[2].Phase[1].Current[22]
EP2PMM2Phase1Current23 | REAL | 531 | EP2:.PMM[2].Phase[1].Current[23]
EP2PMM2Phase1Current24 | REAL | 532 | EP2:.PMM[2].Phase[1].Current[24]
EP2PMM2Phase1Current25 | REAL | 533 | EP2:.PMM[2].Phase[1].Current[25]
EP2PMM2Phase1Current26 | REAL | 534 | EP2:.PMM[2].Phase[1].Current[26]
EP2PMM2Phase1Current27 | REAL | 535 | EP2:.PMM[2].Phase[1].Current[27]
EP2PMM2Phase1Current28 | REAL | 536 | EP2:.PMM[2].Phase[1].Current[28]
EP2PMM2Phase1Current29 | REAL | 537 | EP2:.PMM[2].Phase[1].Current[29]
EP2PMM2Phase1Current2 | REAL | 538 | EP2:.PMM[2].Phase[1].Current[2]
EP2PMM2Phase1Current30 | REAL | 539 | EP2:.PMM[2].Phase[1].Current[30]
EP2PMM2Phase1Current31 | REAL | 540 | EP2:.PMM[2].Phase[1].Current[31]
EP2PMM2Phase1Current32 | REAL | 541 | EP2:.PMM[2].Phase[1].Current[32]
EP2PMM2Phase1Current33 | REAL | 542 | EP2:.PMM[2].Phase[1].Current[33]
EP2PMM2Phase1Current34 | REAL | 543 | EP2:.PMM[2].Phase[1].Current[34]
EP2PMM2Phase1Current35 | REAL | 544 | EP2:.PMM[2].Phase[1].Current[35]
EP2PMM2Phase1Current36 | REAL | 545 | EP2:.PMM[2].Phase[1].Current[36]
EP2PMM2Phase1Current37 | REAL | 546 | EP2:.PMM[2].Phase[1].Current[37]
EP2PMM2Phase1Current38 | REAL | 547 | EP2:.PMM[2].Phase[1].Current[38]
EP2PMM2Phase1Current39 | REAL | 548 | EP2:.PMM[2].Phase[1].Current[39]
EP2PMM2Phase1Current3 | REAL | 549 | EP2:.PMM[2].Phase[1].Current[3]
EP2PMM2Phase1Current40 | REAL | 550 | EP2:.PMM[2].Phase[1].Current[40]
EP2PMM2Phase1Current41 | REAL | 551 | EP2:.PMM[2].Phase[1].Current[41]
EP2PMM2Phase1Current42 | REAL | 552 | EP2:.PMM[2].Phase[1].Current[42]
EP2PMM2Phase1Current4 | REAL | 553 | EP2:.PMM[2].Phase[1].Current[4]
EP2PMM2Phase1Current5 | REAL | 554 | EP2:.PMM[2].Phase[1].Current[5]
EP2PMM2Phase1Current6 | REAL | 555 | EP2:.PMM[2].Phase[1].Current[6]
EP2PMM2Phase1Current7 | REAL | 556 | EP2:.PMM[2].Phase[1].Current[7]
EP2PMM2Phase1Current8 | REAL | 557 | EP2:.PMM[2].Phase[1].Current[8]
EP2PMM2Phase1Current9 | REAL | 558 | EP2:.PMM[2].Phase[1].Current[9]
EP2PMM2Phase2Current10 | REAL | 559 | EP2:.PMM[2].Phase[2].Current[10]
EP2PMM2Phase2Current11 | REAL | 560 | EP2:.PMM[2].Phase[2].Current[11]
EP2PMM2Phase2Current12 | REAL | 561 | EP2:.PMM[2].Phase[2].Current[12]
EP2PMM2Phase2Current13 | REAL | 562 | EP2:.PMM[2].Phase[2].Current[13]
EP2PMM2Phase2Current14 | REAL | 563 | EP2:.PMM[2].Phase[2].Current[14]
EP2PMM2Phase2Current15 | REAL | 564 | EP2:.PMM[2].Phase[2].Current[15]
EP2PMM2Phase2Current16 | REAL | 565 | EP2:.PMM[2].Phase[2].Current[16]
EP2PMM2Phase2Current17 | REAL | 566 | EP2:.PMM[2].Phase[2].Current[17]
EP2PMM2Phase2Current18 | REAL | 567 | EP2:.PMM[2].Phase[2].Current[18]
EP2PMM2Phase2Current19 | REAL | 568 | EP2:.PMM[2].Phase[2].Current[19]
EP2PMM2Phase2Current1 | REAL | 569 | EP2:.PMM[2].Phase[2].Current[1]
EP2PMM2Phase2Current20 | REAL | 570 | EP2:.PMM[2].Phase[2].Current[20]
EP2PMM2Phase2Current21 | REAL | 571 | EP2:.PMM[2].Phase[2].Current[21]
EP2PMM2Phase2Current22 | REAL | 572 | EP2:.PMM[2].Phase[2].Current[22]
EP2PMM2Phase2Current23 | REAL | 573 | EP2:.PMM[2].Phase[2].Current[23]
EP2PMM2Phase2Current24 | REAL | 574 | EP2:.PMM[2].Phase[2].Current[24]
EP2PMM2Phase2Current25 | REAL | 575 | EP2:.PMM[2].Phase[2].Current[25]
EP2PMM2Phase2Current26 | REAL | 576 | EP2:.PMM[2].Phase[2].Current[26]
EP2PMM2Phase2Current27 | REAL | 577 | EP2:.PMM[2].Phase[2].Current[27]
EP2PMM2Phase2Current28 | REAL | 578 | EP2:.PMM[2].Phase[2].Current[28]
EP2PMM2Phase2Current29 | REAL | 579 | EP2:.PMM[2].Phase[2].Current[29]
EP2PMM2Phase2Current2 | REAL | 580 | EP2:.PMM[2].Phase[2].Current[2]
EP2PMM2Phase2Current30 | REAL | 581 | EP2:.PMM[2].Phase[2].Current[30]
EP2PMM2Phase2Current31 | REAL | 582 | EP2:.PMM[2].Phase[2].Current[31]
EP2PMM2Phase2Current32 | REAL | 583 | EP2:.PMM[2].Phase[2].Current[32]
EP2PMM2Phase2Current33 | REAL | 584 | EP2:.PMM[2].Phase[2].Current[33]
EP2PMM2Phase2Current34 | REAL | 585 | EP2:.PMM[2].Phase[2].Current[34]
EP2PMM2Phase2Current35 | REAL | 586 | EP2:.PMM[2].Phase[2].Current[35]
EP2PMM2Phase2Current36 | REAL | 587 | EP2:.PMM[2].Phase[2].Current[36]
EP2PMM2Phase2Current37 | REAL | 588 | EP2:.PMM[2].Phase[2].Current[37]
EP2PMM2Phase2Current38 | REAL | 589 | EP2:.PMM[2].Phase[2].Current[38]
EP2PMM2Phase2Current39 | REAL | 590 | EP2:.PMM[2].Phase[2].Current[39]
EP2PMM2Phase2Current3 | REAL | 591 | EP2:.PMM[2].Phase[2].Current[3]
EP2PMM2Phase2Current40 | REAL | 592 | EP2:.PMM[2].Phase[2].Current[40]
EP2PMM2Phase2Current41 | REAL | 593 | EP2:.PMM[2].Phase[2].Current[41]
EP2PMM2Phase2Current42 | REAL | 594 | EP2:.PMM[2].Phase[2].Current[42]
EP2PMM2Phase2Current4 | REAL | 595 | EP2:.PMM[2].Phase[2].Current[4]
EP2PMM2Phase2Current5 | REAL | 596 | EP2:.PMM[2].Phase[2].Current[5]
EP2PMM2Phase2Current6 | REAL | 597 | EP2:.PMM[2].Phase[2].Current[6]
EP2PMM2Phase2Current7 | REAL | 598 | EP2:.PMM[2].Phase[2].Current[7]
EP2PMM2Phase2Current8 | REAL | 599 | EP2:.PMM[2].Phase[2].Current[8]
EP2PMM2Phase2Current9 | REAL | 600 | EP2:.PMM[2].Phase[2].Current[9]
EP2PMM2Phase3Current10 | REAL | 601 | EP2:.PMM[2].Phase[3].Current[10]
EP2PMM2Phase3Current11 | REAL | 602 | EP2:.PMM[2].Phase[3].Current[11]
EP2PMM2Phase3Current12 | REAL | 603 | EP2:.PMM[2].Phase[3].Current[12]
EP2PMM2Phase3Current13 | REAL | 604 | EP2:.PMM[2].Phase[3].Current[13]
EP2PMM2Phase3Current14 | REAL | 605 | EP2:.PMM[2].Phase[3].Current[14]
EP2PMM2Phase3Current15 | REAL | 606 | EP2:.PMM[2].Phase[3].Current[15]
EP2PMM2Phase3Current16 | REAL | 607 | EP2:.PMM[2].Phase[3].Current[16]
EP2PMM2Phase3Current17 | REAL | 608 | EP2:.PMM[2].Phase[3].Current[17]
EP2PMM2Phase3Current18 | REAL | 609 | EP2:.PMM[2].Phase[3].Current[18]
EP2PMM2Phase3Current19 | REAL | 610 | EP2:.PMM[2].Phase[3].Current[19]
EP2PMM2Phase3Current1 | REAL | 611 | EP2:.PMM[2].Phase[3].Current[1]
EP2PMM2Phase3Current20 | REAL | 612 | EP2:.PMM[2].Phase[3].Current[20]
EP2PMM2Phase3Current21 | REAL | 613 | EP2:.PMM[2].Phase[3].Current[21]
EP2PMM2Phase3Current22 | REAL | 614 | EP2:.PMM[2].Phase[3].Current[22]
EP2PMM2Phase3Current23 | REAL | 615 | EP2:.PMM[2].Phase[3].Current[23]
EP2PMM2Phase3Current24 | REAL | 616 | EP2:.PMM[2].Phase[3].Current[24]
EP2PMM2Phase3Current25 | REAL | 617 | EP2:.PMM[2].Phase[3].Current[25]
EP2PMM2Phase3Current26 | REAL | 618 | EP2:.PMM[2].Phase[3].Current[26]
EP2PMM2Phase3Current27 | REAL | 619 | EP2:.PMM[2].Phase[3].Current[27]
EP2PMM2Phase3Current28 | REAL | 620 | EP2:.PMM[2].Phase[3].Current[28]
EP2PMM2Phase3Current29 | REAL | 621 | EP2:.PMM[2].Phase[3].Current[29]
EP2PMM2Phase3Current2 | REAL | 622 | EP2:.PMM[2].Phase[3].Current[2]
EP2PMM2Phase3Current30 | REAL | 623 | EP2:.PMM[2].Phase[3].Current[30]
EP2PMM2Phase3Current31 | REAL | 624 | EP2:.PMM[2].Phase[3].Current[31]
EP2PMM2Phase3Current32 | REAL | 625 | EP2:.PMM[2].Phase[3].Current[32]
EP2PMM2Phase3Current33 | REAL | 626 | EP2:.PMM[2].Phase[3].Current[33]
EP2PMM2Phase3Current34 | REAL | 627 | EP2:.PMM[2].Phase[3].Current[34]
EP2PMM2Phase3Current35 | REAL | 628 | EP2:.PMM[2].Phase[3].Current[35]
EP2PMM2Phase3Current36 | REAL | 629 | EP2:.PMM[2].Phase[3].Current[36]
EP2PMM2Phase3Current37 | REAL | 630 | EP2:.PMM[2].Phase[3].Current[37]
EP2PMM2Phase3Current38 | REAL | 631 | EP2:.PMM[2].Phase[3].Current[38]
EP2PMM2Phase3Current39 | REAL | 632 | EP2:.PMM[2].Phase[3].Current[39]
EP2PMM2Phase3Current3 | REAL | 633 | EP2:.PMM[2].Phase[3].Current[3]
EP2PMM2Phase3Current40 | REAL | 634 | EP2:.PMM[2].Phase[3].Current[40]
EP2PMM2Phase3Current41 | REAL | 635 | EP2:.PMM[2].Phase[3].Current[41]
EP2PMM2Phase3Current42 | REAL | 636 | EP2:.PMM[2].Phase[3].Current[42]
EP2PMM2Phase3Current4 | REAL | 637 | EP2:.PMM[2].Phase[3].Current[4]
EP2PMM2Phase3Current5 | REAL | 638 | EP2:.PMM[2].Phase[3].Current[5]
EP2PMM2Phase3Current6 | REAL | 639 | EP2:.PMM[2].Phase[3].Current[6]
EP2PMM2Phase3Current7 | REAL | 640 | EP2:.PMM[2].Phase[3].Current[7]
EP2PMM2Phase3Current8 | REAL | 641 | EP2:.PMM[2].Phase[3].Current[8]
EP2PMM2Phase3Current9 | REAL | 642 | EP2:.PMM[2].Phase[3].Current[9]
EP2PMM2PowerFactorPhaseA | REAL | 643 | EP2:.PMM[2].PowerFactorPhaseA
EP2PMM2PowerFactorPhaseB | REAL | 644 | EP2:.PMM[2].PowerFactorPhaseB
EP2PMM2PowerFactorPhaseC | REAL | 645 | EP2:.PMM[2].PowerFactorPhaseC
EP2PMM2TotalActivePower_kW | REAL | 646 | EP2:.PMM[2].TotalActivePower_kW
EP2PMM2TotalAparentPower_kVA | REAL | 647 | EP2:.PMM[2].TotalAparentPower_kVA
EP2PMM2TotalPowerFactor | REAL | 648 | EP2:.PMM[2].TotalPowerFactor
EP2PMM2TotalReactivePower_kVAR | REAL | 649 | EP2:.PMM[2].TotalReactivePower_kVAR
EP2PMM2VoltageBetweenPhaseAB_V | REAL | 650 | EP2:.PMM[2].VoltageBetweenPhaseAB_V
EP2PMM2VoltageBetweenPhaseAN_V | REAL | 651 | EP2:.PMM[2].VoltageBetweenPhaseAN_V
EP2PMM2VoltageBetweenPhaseBC_V | REAL | 652 | EP2:.PMM[2].VoltageBetweenPhaseBC_V
EP2PMM2VoltageBetweenPhaseBN_V | REAL | 653 | EP2:.PMM[2].VoltageBetweenPhaseBN_V
EP2PMM2VoltageBetweenPhaseCA_V | REAL | 654 | EP2:.PMM[2].VoltageBetweenPhaseCA_V
EP2PMM2VoltageBetweenPhaseCN_V | REAL | 655 | EP2:.PMM[2].VoltageBetweenPhaseCN_V
EP2PMM3ActivePowerPhaseA_kW | REAL | 656 | EP2:.PMM[3].ActivePowerPhaseA_kW
EP2PMM3ActivePowerPhaseB_kW | REAL | 657 | EP2:.PMM[3].ActivePowerPhaseB_kW
EP2PMM3ActivePowerPhaseC_kW | REAL | 658 | EP2:.PMM[3].ActivePowerPhaseC_kW
EP2PMM3AlarmPhase1C01_16_60to80 | UINT | 659 | EP2:.PMM[3].AlarmPhase[1].C01_16_60to80
EP2PMM3AlarmPhase1C01_16_over80 | UINT | 660 | EP2:.PMM[3].AlarmPhase[1].C01_16_over80
EP2PMM3AlarmPhase1C17_32_60to80 | UINT | 661 | EP2:.PMM[3].AlarmPhase[1].C17_32_60to80
EP2PMM3AlarmPhase1C17_32_over80 | UINT | 662 | EP2:.PMM[3].AlarmPhase[1].C17_32_over80
EP2PMM3AlarmPhase1C33_42_60to80 | UINT | 663 | EP2:.PMM[3].AlarmPhase[1].C33_42_60to80
EP2PMM3AlarmPhase1C33_42_over80 | UINT | 664 | EP2:.PMM[3].AlarmPhase[1].C33_42_over80
EP2PMM3AlarmPhase1GlobalAlarmReg | INT | 665 | EP2:.PMM[3].AlarmPhase[1].GlobalAlarmReg
EP2PMM3AlarmPhase2C01_16_60to80 | UINT | 666 | EP2:.PMM[3].AlarmPhase[2].C01_16_60to80
EP2PMM3AlarmPhase2C01_16_over80 | UINT | 667 | EP2:.PMM[3].AlarmPhase[2].C01_16_over80
EP2PMM3AlarmPhase2C17_32_60to80 | UINT | 668 | EP2:.PMM[3].AlarmPhase[2].C17_32_60to80
EP2PMM3AlarmPhase2C17_32_over80 | UINT | 669 | EP2:.PMM[3].AlarmPhase[2].C17_32_over80
EP2PMM3AlarmPhase2C33_42_60to80 | UINT | 670 | EP2:.PMM[3].AlarmPhase[2].C33_42_60to80
EP2PMM3AlarmPhase2C33_42_over80 | UINT | 671 | EP2:.PMM[3].AlarmPhase[2].C33_42_over80
EP2PMM3AlarmPhase2GlobalAlarmReg | INT | 672 | EP2:.PMM[3].AlarmPhase[2].GlobalAlarmReg
EP2PMM3AlarmPhase3C01_16_60to80 | UINT | 673 | EP2:.PMM[3].AlarmPhase[3].C01_16_60to80
EP2PMM3AlarmPhase3C01_16_over80 | UINT | 674 | EP2:.PMM[3].AlarmPhase[3].C01_16_over80
EP2PMM3AlarmPhase3C17_32_60to80 | UINT | 675 | EP2:.PMM[3].AlarmPhase[3].C17_32_60to80
EP2PMM3AlarmPhase3C17_32_over80 | UINT | 676 | EP2:.PMM[3].AlarmPhase[3].C17_32_over80
EP2PMM3AlarmPhase3C33_42_60to80 | UINT | 677 | EP2:.PMM[3].AlarmPhase[3].C33_42_60to80
EP2PMM3AlarmPhase3C33_42_over80 | UINT | 678 | EP2:.PMM[3].AlarmPhase[3].C33_42_over80
EP2PMM3AlarmPhase3GlobalAlarmReg | INT | 679 | EP2:.PMM[3].AlarmPhase[3].GlobalAlarmReg
EP2PMM3Alarms | UINT | 680 | EP2:.PMM[3].Alarms
EP2PMM3AverageCurrent_A | REAL | 681 | EP2:.PMM[3].AverageCurrent_A
EP2PMM3AveragePhaseToNeutral_V | REAL | 682 | EP2:.PMM[3].AveragePhaseToNeutral_V
EP2PMM3AveragePhaseToPhase_V | REAL | 683 | EP2:.PMM[3].AveragePhaseToPhase_V
EP2PMM3CurrentInPhaseA_A | REAL | 684 | EP2:.PMM[3].CurrentInPhaseA_A
EP2PMM3CurrentInPhaseB_A | REAL | 685 | EP2:.PMM[3].CurrentInPhaseB_A
EP2PMM3CurrentInPhaseC_A | REAL | 686 | EP2:.PMM[3].CurrentInPhaseC_A
EP2PMM3EnergyConsumed_kWh | REAL | 687 | EP2:.PMM[3].EnergyConsumed_kWh
EP2PMM3Frequency_Hz | REAL | 688 | EP2:.PMM[3].Frequency_Hz
EP2PMM3Napaka | DIGITAL | 689 | EP2:.PMM[3].Napaka
EP2PMM3NeutralCurrent_A | REAL | 690 | EP2:.PMM[3].NeutralCurrent_A
EP2PMM3Phase1Current10 | REAL | 691 | EP2:.PMM[3].Phase[1].Current[10]
EP2PMM3Phase1Current11 | REAL | 692 | EP2:.PMM[3].Phase[1].Current[11]
EP2PMM3Phase1Current12 | REAL | 693 | EP2:.PMM[3].Phase[1].Current[12]
EP2PMM3Phase1Current13 | REAL | 694 | EP2:.PMM[3].Phase[1].Current[13]
EP2PMM3Phase1Current14 | REAL | 695 | EP2:.PMM[3].Phase[1].Current[14]
EP2PMM3Phase1Current15 | REAL | 696 | EP2:.PMM[3].Phase[1].Current[15]
EP2PMM3Phase1Current16 | REAL | 697 | EP2:.PMM[3].Phase[1].Current[16]
EP2PMM3Phase1Current17 | REAL | 698 | EP2:.PMM[3].Phase[1].Current[17]
EP2PMM3Phase1Current18 | REAL | 699 | EP2:.PMM[3].Phase[1].Current[18]
EP2PMM3Phase1Current19 | REAL | 700 | EP2:.PMM[3].Phase[1].Current[19]
EP2PMM3Phase1Current1 | REAL | 701 | EP2:.PMM[3].Phase[1].Current[1]
EP2PMM3Phase1Current20 | REAL | 702 | EP2:.PMM[3].Phase[1].Current[20]
EP2PMM3Phase1Current21 | REAL | 703 | EP2:.PMM[3].Phase[1].Current[21]
EP2PMM3Phase1Current22 | REAL | 704 | EP2:.PMM[3].Phase[1].Current[22]
EP2PMM3Phase1Current23 | REAL | 705 | EP2:.PMM[3].Phase[1].Current[23]
EP2PMM3Phase1Current24 | REAL | 706 | EP2:.PMM[3].Phase[1].Current[24]
EP2PMM3Phase1Current25 | REAL | 707 | EP2:.PMM[3].Phase[1].Current[25]
EP2PMM3Phase1Current26 | REAL | 708 | EP2:.PMM[3].Phase[1].Current[26]
EP2PMM3Phase1Current27 | REAL | 709 | EP2:.PMM[3].Phase[1].Current[27]
EP2PMM3Phase1Current28 | REAL | 710 | EP2:.PMM[3].Phase[1].Current[28]
EP2PMM3Phase1Current29 | REAL | 711 | EP2:.PMM[3].Phase[1].Current[29]
EP2PMM3Phase1Current2 | REAL | 712 | EP2:.PMM[3].Phase[1].Current[2]
EP2PMM3Phase1Current30 | REAL | 713 | EP2:.PMM[3].Phase[1].Current[30]
EP2PMM3Phase1Current31 | REAL | 714 | EP2:.PMM[3].Phase[1].Current[31]
EP2PMM3Phase1Current32 | REAL | 715 | EP2:.PMM[3].Phase[1].Current[32]
EP2PMM3Phase1Current33 | REAL | 716 | EP2:.PMM[3].Phase[1].Current[33]
EP2PMM3Phase1Current34 | REAL | 717 | EP2:.PMM[3].Phase[1].Current[34]
EP2PMM3Phase1Current35 | REAL | 718 | EP2:.PMM[3].Phase[1].Current[35]
EP2PMM3Phase1Current36 | REAL | 719 | EP2:.PMM[3].Phase[1].Current[36]
EP2PMM3Phase1Current37 | REAL | 720 | EP2:.PMM[3].Phase[1].Current[37]
EP2PMM3Phase1Current38 | REAL | 721 | EP2:.PMM[3].Phase[1].Current[38]
EP2PMM3Phase1Current39 | REAL | 722 | EP2:.PMM[3].Phase[1].Current[39]
EP2PMM3Phase1Current3 | REAL | 723 | EP2:.PMM[3].Phase[1].Current[3]
EP2PMM3Phase1Current40 | REAL | 724 | EP2:.PMM[3].Phase[1].Current[40]
EP2PMM3Phase1Current41 | REAL | 725 | EP2:.PMM[3].Phase[1].Current[41]
EP2PMM3Phase1Current42 | REAL | 726 | EP2:.PMM[3].Phase[1].Current[42]
EP2PMM3Phase1Current4 | REAL | 727 | EP2:.PMM[3].Phase[1].Current[4]
EP2PMM3Phase1Current5 | REAL | 728 | EP2:.PMM[3].Phase[1].Current[5]
EP2PMM3Phase1Current6 | REAL | 729 | EP2:.PMM[3].Phase[1].Current[6]
EP2PMM3Phase1Current7 | REAL | 730 | EP2:.PMM[3].Phase[1].Current[7]
EP2PMM3Phase1Current8 | REAL | 731 | EP2:.PMM[3].Phase[1].Current[8]
EP2PMM3Phase1Current9 | REAL | 732 | EP2:.PMM[3].Phase[1].Current[9]
EP2PMM3Phase2Current10 | REAL | 733 | EP2:.PMM[3].Phase[2].Current[10]
EP2PMM3Phase2Current11 | REAL | 734 | EP2:.PMM[3].Phase[2].Current[11]
EP2PMM3Phase2Current12 | REAL | 735 | EP2:.PMM[3].Phase[2].Current[12]
EP2PMM3Phase2Current13 | REAL | 736 | EP2:.PMM[3].Phase[2].Current[13]
EP2PMM3Phase2Current14 | REAL | 737 | EP2:.PMM[3].Phase[2].Current[14]
EP2PMM3Phase2Current15 | REAL | 738 | EP2:.PMM[3].Phase[2].Current[15]
EP2PMM3Phase2Current16 | REAL | 739 | EP2:.PMM[3].Phase[2].Current[16]
EP2PMM3Phase2Current17 | REAL | 740 | EP2:.PMM[3].Phase[2].Current[17]
EP2PMM3Phase2Current18 | REAL | 741 | EP2:.PMM[3].Phase[2].Current[18]
EP2PMM3Phase2Current19 | REAL | 742 | EP2:.PMM[3].Phase[2].Current[19]
EP2PMM3Phase2Current1 | REAL | 743 | EP2:.PMM[3].Phase[2].Current[1]
EP2PMM3Phase2Current20 | REAL | 744 | EP2:.PMM[3].Phase[2].Current[20]
EP2PMM3Phase2Current21 | REAL | 745 | EP2:.PMM[3].Phase[2].Current[21]
EP2PMM3Phase2Current22 | REAL | 746 | EP2:.PMM[3].Phase[2].Current[22]
EP2PMM3Phase2Current23 | REAL | 747 | EP2:.PMM[3].Phase[2].Current[23]
EP2PMM3Phase2Current24 | REAL | 748 | EP2:.PMM[3].Phase[2].Current[24]
EP2PMM3Phase2Current25 | REAL | 749 | EP2:.PMM[3].Phase[2].Current[25]
EP2PMM3Phase2Current26 | REAL | 750 | EP2:.PMM[3].Phase[2].Current[26]
EP2PMM3Phase2Current27 | REAL | 751 | EP2:.PMM[3].Phase[2].Current[27]
EP2PMM3Phase2Current28 | REAL | 752 | EP2:.PMM[3].Phase[2].Current[28]
EP2PMM3Phase2Current29 | REAL | 753 | EP2:.PMM[3].Phase[2].Current[29]
EP2PMM3Phase2Current2 | REAL | 754 | EP2:.PMM[3].Phase[2].Current[2]
EP2PMM3Phase2Current30 | REAL | 755 | EP2:.PMM[3].Phase[2].Current[30]
EP2PMM3Phase2Current31 | REAL | 756 | EP2:.PMM[3].Phase[2].Current[31]
EP2PMM3Phase2Current32 | REAL | 757 | EP2:.PMM[3].Phase[2].Current[32]
EP2PMM3Phase2Current33 | REAL | 758 | EP2:.PMM[3].Phase[2].Current[33]
EP2PMM3Phase2Current34 | REAL | 759 | EP2:.PMM[3].Phase[2].Current[34]
EP2PMM3Phase2Current35 | REAL | 760 | EP2:.PMM[3].Phase[2].Current[35]
EP2PMM3Phase2Current36 | REAL | 761 | EP2:.PMM[3].Phase[2].Current[36]
EP2PMM3Phase2Current37 | REAL | 762 | EP2:.PMM[3].Phase[2].Current[37]
EP2PMM3Phase2Current38 | REAL | 763 | EP2:.PMM[3].Phase[2].Current[38]
EP2PMM3Phase2Current39 | REAL | 764 | EP2:.PMM[3].Phase[2].Current[39]
EP2PMM3Phase2Current3 | REAL | 765 | EP2:.PMM[3].Phase[2].Current[3]
EP2PMM3Phase2Current40 | REAL | 766 | EP2:.PMM[3].Phase[2].Current[40]
EP2PMM3Phase2Current41 | REAL | 767 | EP2:.PMM[3].Phase[2].Current[41]
EP2PMM3Phase2Current42 | REAL | 768 | EP2:.PMM[3].Phase[2].Current[42]
EP2PMM3Phase2Current4 | REAL | 769 | EP2:.PMM[3].Phase[2].Current[4]
EP2PMM3Phase2Current5 | REAL | 770 | EP2:.PMM[3].Phase[2].Current[5]
EP2PMM3Phase2Current6 | REAL | 771 | EP2:.PMM[3].Phase[2].Current[6]
EP2PMM3Phase2Current7 | REAL | 772 | EP2:.PMM[3].Phase[2].Current[7]
EP2PMM3Phase2Current8 | REAL | 773 | EP2:.PMM[3].Phase[2].Current[8]
EP2PMM3Phase2Current9 | REAL | 774 | EP2:.PMM[3].Phase[2].Current[9]
EP2PMM3Phase3Current10 | REAL | 775 | EP2:.PMM[3].Phase[3].Current[10]
EP2PMM3Phase3Current11 | REAL | 776 | EP2:.PMM[3].Phase[3].Current[11]
EP2PMM3Phase3Current12 | REAL | 777 | EP2:.PMM[3].Phase[3].Current[12]
EP2PMM3Phase3Current13 | REAL | 778 | EP2:.PMM[3].Phase[3].Current[13]
EP2PMM3Phase3Current14 | REAL | 779 | EP2:.PMM[3].Phase[3].Current[14]
EP2PMM3Phase3Current15 | REAL | 780 | EP2:.PMM[3].Phase[3].Current[15]
EP2PMM3Phase3Current16 | REAL | 781 | EP2:.PMM[3].Phase[3].Current[16]
EP2PMM3Phase3Current17 | REAL | 782 | EP2:.PMM[3].Phase[3].Current[17]
EP2PMM3Phase3Current18 | REAL | 783 | EP2:.PMM[3].Phase[3].Current[18]
EP2PMM3Phase3Current19 | REAL | 784 | EP2:.PMM[3].Phase[3].Current[19]
EP2PMM3Phase3Current1 | REAL | 785 | EP2:.PMM[3].Phase[3].Current[1]
EP2PMM3Phase3Current20 | REAL | 786 | EP2:.PMM[3].Phase[3].Current[20]
EP2PMM3Phase3Current21 | REAL | 787 | EP2:.PMM[3].Phase[3].Current[21]
EP2PMM3Phase3Current22 | REAL | 788 | EP2:.PMM[3].Phase[3].Current[22]
EP2PMM3Phase3Current23 | REAL | 789 | EP2:.PMM[3].Phase[3].Current[23]
EP2PMM3Phase3Current24 | REAL | 790 | EP2:.PMM[3].Phase[3].Current[24]
EP2PMM3Phase3Current25 | REAL | 791 | EP2:.PMM[3].Phase[3].Current[25]
EP2PMM3Phase3Current26 | REAL | 792 | EP2:.PMM[3].Phase[3].Current[26]
EP2PMM3Phase3Current27 | REAL | 793 | EP2:.PMM[3].Phase[3].Current[27]
EP2PMM3Phase3Current28 | REAL | 794 | EP2:.PMM[3].Phase[3].Current[28]
EP2PMM3Phase3Current29 | REAL | 795 | EP2:.PMM[3].Phase[3].Current[29]
EP2PMM3Phase3Current2 | REAL | 796 | EP2:.PMM[3].Phase[3].Current[2]
EP2PMM3Phase3Current30 | REAL | 797 | EP2:.PMM[3].Phase[3].Current[30]
EP2PMM3Phase3Current31 | REAL | 798 | EP2:.PMM[3].Phase[3].Current[31]
EP2PMM3Phase3Current32 | REAL | 799 | EP2:.PMM[3].Phase[3].Current[32]
EP2PMM3Phase3Current33 | REAL | 800 | EP2:.PMM[3].Phase[3].Current[33]
EP2PMM3Phase3Current34 | REAL | 801 | EP2:.PMM[3].Phase[3].Current[34]
EP2PMM3Phase3Current35 | REAL | 802 | EP2:.PMM[3].Phase[3].Current[35]
EP2PMM3Phase3Current36 | REAL | 803 | EP2:.PMM[3].Phase[3].Current[36]
EP2PMM3Phase3Current37 | REAL | 804 | EP2:.PMM[3].Phase[3].Current[37]
EP2PMM3Phase3Current38 | REAL | 805 | EP2:.PMM[3].Phase[3].Current[38]
EP2PMM3Phase3Current39 | REAL | 806 | EP2:.PMM[3].Phase[3].Current[39]
EP2PMM3Phase3Current3 | REAL | 807 | EP2:.PMM[3].Phase[3].Current[3]
EP2PMM3Phase3Current40 | REAL | 808 | EP2:.PMM[3].Phase[3].Current[40]
EP2PMM3Phase3Current41 | REAL | 809 | EP2:.PMM[3].Phase[3].Current[41]
EP2PMM3Phase3Current42 | REAL | 810 | EP2:.PMM[3].Phase[3].Current[42]
EP2PMM3Phase3Current4 | REAL | 811 | EP2:.PMM[3].Phase[3].Current[4]
EP2PMM3Phase3Current5 | REAL | 812 | EP2:.PMM[3].Phase[3].Current[5]
EP2PMM3Phase3Current6 | REAL | 813 | EP2:.PMM[3].Phase[3].Current[6]
EP2PMM3Phase3Current7 | REAL | 814 | EP2:.PMM[3].Phase[3].Current[7]
EP2PMM3Phase3Current8 | REAL | 815 | EP2:.PMM[3].Phase[3].Current[8]
EP2PMM3Phase3Current9 | REAL | 816 | EP2:.PMM[3].Phase[3].Current[9]
EP2PMM3PowerFactorPhaseA | REAL | 817 | EP2:.PMM[3].PowerFactorPhaseA
EP2PMM3PowerFactorPhaseB | REAL | 818 | EP2:.PMM[3].PowerFactorPhaseB
EP2PMM3PowerFactorPhaseC | REAL | 819 | EP2:.PMM[3].PowerFactorPhaseC
EP2PMM3TotalActivePower_kW | REAL | 820 | EP2:.PMM[3].TotalActivePower_kW
EP2PMM3TotalAparentPower_kVA | REAL | 821 | EP2:.PMM[3].TotalAparentPower_kVA
EP2PMM3TotalPowerFactor | REAL | 822 | EP2:.PMM[3].TotalPowerFactor
EP2PMM3TotalReactivePower_kVAR | REAL | 823 | EP2:.PMM[3].TotalReactivePower_kVAR
EP2PMM3VoltageBetweenPhaseAB_V | REAL | 824 | EP2:.PMM[3].VoltageBetweenPhaseAB_V
EP2PMM3VoltageBetweenPhaseAN_V | REAL | 825 | EP2:.PMM[3].VoltageBetweenPhaseAN_V
EP2PMM3VoltageBetweenPhaseBC_V | REAL | 826 | EP2:.PMM[3].VoltageBetweenPhaseBC_V
EP2PMM3VoltageBetweenPhaseBN_V | REAL | 827 | EP2:.PMM[3].VoltageBetweenPhaseBN_V
EP2PMM3VoltageBetweenPhaseCA_V | REAL | 828 | EP2:.PMM[3].VoltageBetweenPhaseCA_V
EP2PMM3VoltageBetweenPhaseCN_V | REAL | 829 | EP2:.PMM[3].VoltageBetweenPhaseCN_V
EP2PMMfaza01 | REAL | IOD_EP2 | EP2:.PMMfaza01
EP2PMMfaza02 | REAL | IOD_EP2 | EP2:.PMMfaza02
EP2PMMfaza03 | REAL | IOD_EP2 | EP2:.PMMfaza03
EP2PMMfaza04 | REAL | IOD_EP2 | EP2:.PMMfaza04
EP2PMMfaza05 | REAL | IOD_EP2 | EP2:.PMMfaza05
EP2PMMfaza06 | REAL | IOD_EP2 | EP2:.PMMfaza06
EP2PMMfaza07 | REAL | IOD_EP2 | EP2:.PMMfaza07
EP2PMMfaza08 | REAL | IOD_EP2 | EP2:.PMMfaza08
EP2PMMfaza09 | REAL | IOD_EP2 | EP2:.PMMfaza09
EP2PMMfaza10 | REAL | IOD_EP2 | EP2:.PMMfaza10
EP2PMMfaza11 | REAL | IOD_EP2 | EP2:.PMMfaza11
EP2PMMfaza12 | REAL | IOD_EP2 | EP2:.PMMfaza12
EP2PMMfaza13 | REAL | IOD_EP2 | EP2:.PMMfaza13
EP2PMMfaza14 | REAL | IOD_EP2 | EP2:.PMMfaza14
EP2PMMfaza15 | REAL | IOD_EP2 | EP2:.PMMfaza15
EP2PMMfaza16 | REAL | IOD_EP2 | EP2:.PMMfaza16
EP2PMMfaza17 | REAL | IOD_EP2 | EP2:.PMMfaza17
EP2PMMfaza18 | REAL | IOD_EP2 | EP2:.PMMfaza18
EP2PMMfaza19 | REAL | IOD_EP2 | EP2:.PMMfaza19
EP2PMMfaza20 | REAL | IOD_EP2 | EP2:.PMMfaza20
EP2PMMfaza21 | REAL | IOD_EP2 | EP2:.PMMfaza21
EP2PMMfaza22 | REAL | IOD_EP2 | EP2:.PMMfaza22
EP2PMMfaza23 | REAL | IOD_EP2 | EP2:.PMMfaza23
EP2PMMfaza24 | REAL | IOD_EP2 | EP2:.PMMfaza24
EP2PMMfaza25 | REAL | IOD_EP2 | EP2:.PMMfaza25
EP2PMMfaza26 | REAL | IOD_EP2 | EP2:.PMMfaza26
EP2PMMfaza27 | REAL | IOD_EP2 | EP2:.PMMfaza27
EP2PMMfaza28 | REAL | IOD_EP2 | EP2:.PMMfaza28
EP2PMMfaza29 | REAL | IOD_EP2 | EP2:.PMMfaza29
EP2PMMfaza30 | REAL | IOD_EP2 | EP2:.PMMfaza30
EP2PMMfaza31 | REAL | IOD_EP2 | EP2:.PMMfaza31
EP2PMMfaza32 | REAL | IOD_EP2 | EP2:.PMMfaza32
EP2PMMfaza33 | REAL | IOD_EP2 | EP2:.PMMfaza33
EP2PMMfaza34 | REAL | IOD_EP2 | EP2:.PMMfaza34
EP2PMMfaza35 | REAL | IOD_EP2 | EP2:.PMMfaza35
EP2PMMfaza36 | REAL | IOD_EP2 | EP2:.PMMfaza36
EP2PMMfaza37 | REAL | IOD_EP2 | EP2:.PMMfaza37
EP2PMMfaza38 | REAL | IOD_EP2 | EP2:.PMMfaza38
EP2PMMfaza39 | REAL | IOD_EP2 | EP2:.PMMfaza39
EP2PMMfaza40 | REAL | IOD_EP2 | EP2:.PMMfaza40
EP2PMMfaza41 | REAL | IOD_EP2 | EP2:.PMMfaza41
EP2PMMfaza42 | REAL | IOD_EP2 | EP2:.PMMfaza42
EP2PMMfaza6010 | REAL | IOD_EP2 | EP2:.PMMfaza60[10]
EP2PMMfaza6011 | REAL | IOD_EP2 | EP2:.PMMfaza60[11]
EP2PMMfaza6012 | REAL | IOD_EP2 | EP2:.PMMfaza60[12]
EP2PMMfaza6013 | REAL | IOD_EP2 | EP2:.PMMfaza60[13]
EP2PMMfaza6014 | REAL | IOD_EP2 | EP2:.PMMfaza60[14]
EP2PMMfaza6015 | REAL | IOD_EP2 | EP2:.PMMfaza60[15]
EP2PMMfaza6016 | REAL | IOD_EP2 | EP2:.PMMfaza60[16]
EP2PMMfaza6017 | REAL | IOD_EP2 | EP2:.PMMfaza60[17]
EP2PMMfaza6018 | REAL | IOD_EP2 | EP2:.PMMfaza60[18]
EP2PMMfaza6019 | REAL | IOD_EP2 | EP2:.PMMfaza60[19]
EP2PMMfaza601 | REAL | IOD_EP2 | EP2:.PMMfaza60[1]
EP2PMMfaza6020 | REAL | IOD_EP2 | EP2:.PMMfaza60[20]
EP2PMMfaza6021 | REAL | IOD_EP2 | EP2:.PMMfaza60[21]
EP2PMMfaza6022 | REAL | IOD_EP2 | EP2:.PMMfaza60[22]
EP2PMMfaza6023 | REAL | IOD_EP2 | EP2:.PMMfaza60[23]
EP2PMMfaza6024 | REAL | IOD_EP2 | EP2:.PMMfaza60[24]
EP2PMMfaza6025 | REAL | IOD_EP2 | EP2:.PMMfaza60[25]
EP2PMMfaza6026 | REAL | IOD_EP2 | EP2:.PMMfaza60[26]
EP2PMMfaza6027 | REAL | IOD_EP2 | EP2:.PMMfaza60[27]
EP2PMMfaza6028 | REAL | IOD_EP2 | EP2:.PMMfaza60[28]
EP2PMMfaza6029 | REAL | IOD_EP2 | EP2:.PMMfaza60[29]
EP2PMMfaza602 | REAL | IOD_EP2 | EP2:.PMMfaza60[2]
EP2PMMfaza6030 | REAL | IOD_EP2 | EP2:.PMMfaza60[30]
EP2PMMfaza6031 | REAL | IOD_EP2 | EP2:.PMMfaza60[31]
EP2PMMfaza6032 | REAL | IOD_EP2 | EP2:.PMMfaza60[32]
EP2PMMfaza6033 | REAL | IOD_EP2 | EP2:.PMMfaza60[33]
EP2PMMfaza6034 | REAL | IOD_EP2 | EP2:.PMMfaza60[34]
EP2PMMfaza6035 | REAL | IOD_EP2 | EP2:.PMMfaza60[35]
EP2PMMfaza6036 | REAL | IOD_EP2 | EP2:.PMMfaza60[36]
EP2PMMfaza6037 | REAL | IOD_EP2 | EP2:.PMMfaza60[37]
EP2PMMfaza6038 | REAL | IOD_EP2 | EP2:.PMMfaza60[38]
EP2PMMfaza6039 | REAL | IOD_EP2 | EP2:.PMMfaza60[39]
EP2PMMfaza603 | REAL | IOD_EP2 | EP2:.PMMfaza60[3]
EP2PMMfaza6040 | REAL | IOD_EP2 | EP2:.PMMfaza60[40]
EP2PMMfaza6041 | REAL | IOD_EP2 | EP2:.PMMfaza60[41]
EP2PMMfaza6042 | REAL | IOD_EP2 | EP2:.PMMfaza60[42]
EP2PMMfaza604 | REAL | IOD_EP2 | EP2:.PMMfaza60[4]
EP2PMMfaza605 | REAL | IOD_EP2 | EP2:.PMMfaza60[5]
EP2PMMfaza606 | REAL | IOD_EP2 | EP2:.PMMfaza60[6]
EP2PMMfaza607 | REAL | IOD_EP2 | EP2:.PMMfaza60[7]
EP2PMMfaza608 | REAL | IOD_EP2 | EP2:.PMMfaza60[8]
EP2PMMfaza609 | REAL | IOD_EP2 | EP2:.PMMfaza60[9]
EP2PMMfaza8010 | REAL | IOD_EP2 | EP2:.PMMfaza80[10]
EP2PMMfaza8011 | REAL | IOD_EP2 | EP2:.PMMfaza80[11]
EP2PMMfaza8012 | REAL | IOD_EP2 | EP2:.PMMfaza80[12]
EP2PMMfaza8013 | REAL | IOD_EP2 | EP2:.PMMfaza80[13]
EP2PMMfaza8014 | REAL | IOD_EP2 | EP2:.PMMfaza80[14]
EP2PMMfaza8015 | REAL | IOD_EP2 | EP2:.PMMfaza80[15]
EP2PMMfaza8016 | REAL | IOD_EP2 | EP2:.PMMfaza80[16]
EP2PMMfaza8017 | REAL | IOD_EP2 | EP2:.PMMfaza80[17]
EP2PMMfaza8018 | REAL | IOD_EP2 | EP2:.PMMfaza80[18]
EP2PMMfaza8019 | REAL | IOD_EP2 | EP2:.PMMfaza80[19]
EP2PMMfaza801 | REAL | IOD_EP2 | EP2:.PMMfaza80[1]
EP2PMMfaza8020 | REAL | IOD_EP2 | EP2:.PMMfaza80[20]
EP2PMMfaza8021 | REAL | IOD_EP2 | EP2:.PMMfaza80[21]
EP2PMMfaza8022 | REAL | IOD_EP2 | EP2:.PMMfaza80[22]
EP2PMMfaza8023 | REAL | IOD_EP2 | EP2:.PMMfaza80[23]
EP2PMMfaza8024 | REAL | IOD_EP2 | EP2:.PMMfaza80[24]
EP2PMMfaza8025 | REAL | IOD_EP2 | EP2:.PMMfaza80[25]
EP2PMMfaza8026 | REAL | IOD_EP2 | EP2:.PMMfaza80[26]
EP2PMMfaza8027 | REAL | IOD_EP2 | EP2:.PMMfaza80[27]
EP2PMMfaza8028 | REAL | IOD_EP2 | EP2:.PMMfaza80[28]
EP2PMMfaza8029 | REAL | IOD_EP2 | EP2:.PMMfaza80[29]
EP2PMMfaza802 | REAL | IOD_EP2 | EP2:.PMMfaza80[2]
EP2PMMfaza8030 | REAL | IOD_EP2 | EP2:.PMMfaza80[30]
EP2PMMfaza8031 | REAL | IOD_EP2 | EP2:.PMMfaza80[31]
EP2PMMfaza8032 | REAL | IOD_EP2 | EP2:.PMMfaza80[32]
EP2PMMfaza8033 | REAL | IOD_EP2 | EP2:.PMMfaza80[33]
EP2PMMfaza8034 | REAL | IOD_EP2 | EP2:.PMMfaza80[34]
EP2PMMfaza8035 | REAL | IOD_EP2 | EP2:.PMMfaza80[35]
EP2PMMfaza8036 | REAL | IOD_EP2 | EP2:.PMMfaza80[36]
EP2PMMfaza8037 | REAL | IOD_EP2 | EP2:.PMMfaza80[37]
EP2PMMfaza8038 | REAL | IOD_EP2 | EP2:.PMMfaza80[38]
EP2PMMfaza8039 | REAL | IOD_EP2 | EP2:.PMMfaza80[39]
EP2PMMfaza803 | REAL | IOD_EP2 | EP2:.PMMfaza80[3]
EP2PMMfaza8040 | REAL | IOD_EP2 | EP2:.PMMfaza80[40]
EP2PMMfaza8041 | REAL | IOD_EP2 | EP2:.PMMfaza80[41]
EP2PMMfaza8042 | REAL | IOD_EP2 | EP2:.PMMfaza80[42]
EP2PMMfaza804 | REAL | IOD_EP2 | EP2:.PMMfaza80[4]
EP2PMMfaza805 | REAL | IOD_EP2 | EP2:.PMMfaza80[5]
EP2PMMfaza806 | REAL | IOD_EP2 | EP2:.PMMfaza80[6]
EP2PMMfaza807 | REAL | IOD_EP2 | EP2:.PMMfaza80[7]
EP2PMMfaza808 | REAL | IOD_EP2 | EP2:.PMMfaza80[8]
EP2PMMfaza809 | REAL | IOD_EP2 | EP2:.PMMfaza80[9]
EP2PMMgalActivePowerPhaseA_kW | REAL | IOD_EP2 | EP2:.PMMgal.ActivePowerPhaseA_kW
EP2PMMgalActivePowerPhaseB_kW | REAL | IOD_EP2 | EP2:.PMMgal.ActivePowerPhaseB_kW
EP2PMMgalActivePowerPhaseC_kW | REAL | IOD_EP2 | EP2:.PMMgal.ActivePowerPhaseC_kW
EP2PMMgalAlarmPhase1C01_16_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C01_16_60to80
EP2PMMgalAlarmPhase1C01_16_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C01_16_over80
EP2PMMgalAlarmPhase1C17_32_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C17_32_60to80
EP2PMMgalAlarmPhase1C17_32_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C17_32_over80
EP2PMMgalAlarmPhase1C33_42_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C33_42_60to80
EP2PMMgalAlarmPhase1C33_42_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C33_42_over80
EP2PMMgalAlarmPhase1GlobalAlarmReg | INT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].GlobalAlarmReg
EP2PMMgalAlarmPhase2C01_16_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C01_16_60to80
EP2PMMgalAlarmPhase2C01_16_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C01_16_over80
EP2PMMgalAlarmPhase2C17_32_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C17_32_60to80
EP2PMMgalAlarmPhase2C17_32_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C17_32_over80
EP2PMMgalAlarmPhase2C33_42_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C33_42_60to80
EP2PMMgalAlarmPhase2C33_42_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C33_42_over80
EP2PMMgalAlarmPhase2GlobalAlarmReg | INT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].GlobalAlarmReg
EP2PMMgalAlarmPhase3C01_16_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C01_16_60to80
EP2PMMgalAlarmPhase3C01_16_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C01_16_over80
EP2PMMgalAlarmPhase3C17_32_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C17_32_60to80
EP2PMMgalAlarmPhase3C17_32_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C17_32_over80
EP2PMMgalAlarmPhase3C33_42_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C33_42_60to80
EP2PMMgalAlarmPhase3C33_42_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C33_42_over80
EP2PMMgalAlarmPhase3GlobalAlarmReg | INT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].GlobalAlarmReg
EP2PMMgalAlarms | UINT | IOD_EP2 | EP2:.PMMgal.Alarms
EP2PMMgalAverageCurrent_A | REAL | IOD_EP2 | EP2:.PMMgal.AverageCurrent_A
EP2PMMgalAveragePhaseToNeutral_V | REAL | IOD_EP2 | EP2:.PMMgal.AveragePhaseToNeutral_V
EP2PMMgalAveragePhaseToPhase_V | REAL | IOD_EP2 | EP2:.PMMgal.AveragePhaseToPhase_V
EP2PMMgalCurrentInPhaseA_A | REAL | IOD_EP2 | EP2:.PMMgal.CurrentInPhaseA_A
EP2PMMgalCurrentInPhaseB_A | REAL | IOD_EP2 | EP2:.PMMgal.CurrentInPhaseB_A
EP2PMMgalCurrentInPhaseC_A | REAL | IOD_EP2 | EP2:.PMMgal.CurrentInPhaseC_A
EP2PMMgalEnergyConsumed_kWh | REAL | IOD_EP2 | EP2:.PMMgal.EnergyConsumed_kWh
EP2PMMgalFrequency_Hz | REAL | IOD_EP2 | EP2:.PMMgal.Frequency_Hz
EP2PMMgalNapaka | DIGITAL | IOD_EP2 | EP2:.PMMgal.Napaka
EP2PMMgalNeutralCurrent_A | REAL | IOD_EP2 | EP2:.PMMgal.NeutralCurrent_A
EP2PMMgalPhase1Current10 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[10]
EP2PMMgalPhase1Current11 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[11]
EP2PMMgalPhase1Current12 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[12]
EP2PMMgalPhase1Current13 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[13]
EP2PMMgalPhase1Current14 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[14]
EP2PMMgalPhase1Current15 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[15]
EP2PMMgalPhase1Current16 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[16]
EP2PMMgalPhase1Current17 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[17]
EP2PMMgalPhase1Current18 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[18]
EP2PMMgalPhase1Current19 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[19]
EP2PMMgalPhase1Current1 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[1]
EP2PMMgalPhase1Current20 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[20]
EP2PMMgalPhase1Current21 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[21]
EP2PMMgalPhase1Current22 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[22]
EP2PMMgalPhase1Current23 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[23]
EP2PMMgalPhase1Current24 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[24]
EP2PMMgalPhase1Current25 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[25]
EP2PMMgalPhase1Current26 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[26]
EP2PMMgalPhase1Current27 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[27]
EP2PMMgalPhase1Current28 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[28]
EP2PMMgalPhase1Current29 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[29]
EP2PMMgalPhase1Current2 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[2]
EP2PMMgalPhase1Current30 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[30]
EP2PMMgalPhase1Current31 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[31]
EP2PMMgalPhase1Current32 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[32]
EP2PMMgalPhase1Current33 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[33]
EP2PMMgalPhase1Current34 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[34]
EP2PMMgalPhase1Current35 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[35]
EP2PMMgalPhase1Current36 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[36]
EP2PMMgalPhase1Current37 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[37]
EP2PMMgalPhase1Current38 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[38]
EP2PMMgalPhase1Current39 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[39]
EP2PMMgalPhase1Current3 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[3]
EP2PMMgalPhase1Current40 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[40]
EP2PMMgalPhase1Current41 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[41]
EP2PMMgalPhase1Current42 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[42]
EP2PMMgalPhase1Current4 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[4]
EP2PMMgalPhase1Current5 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[5]
EP2PMMgalPhase1Current6 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[6]
EP2PMMgalPhase1Current7 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[7]
EP2PMMgalPhase1Current8 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[8]
EP2PMMgalPhase1Current9 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[9]
EP2PMMgalPhase2Current10 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[10]
EP2PMMgalPhase2Current11 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[11]
EP2PMMgalPhase2Current12 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[12]
EP2PMMgalPhase2Current13 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[13]
EP2PMMgalPhase2Current14 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[14]
EP2PMMgalPhase2Current15 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[15]
EP2PMMgalPhase2Current16 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[16]
EP2PMMgalPhase2Current17 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[17]
EP2PMMgalPhase2Current18 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[18]
EP2PMMgalPhase2Current19 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[19]
EP2PMMgalPhase2Current1 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[1]
EP2PMMgalPhase2Current20 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[20]
EP2PMMgalPhase2Current21 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[21]
EP2PMMgalPhase2Current22 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[22]
EP2PMMgalPhase2Current23 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[23]
EP2PMMgalPhase2Current24 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[24]
EP2_DI_Q32_IZKLJUCENO_omogoci | DIGITAL | IOD_EP2_disk | D9011
EP2_DI_Q27_IZKLJUCENO_omogoci | DIGITAL | IOD_EP2_disk | D9012
EP2_DI_Q34_IZKLJUCENO_omogoci | DIGITAL | IOD_EP2_disk | D9013
EP2_DI_Q30_IZKLJUCENO_omogoci | DIGITAL | IOD_EP2_disk | D9014
EP2_DI_Q32_VKLJUCENO_omogoci | DIGITAL | IOD_EP2_disk | D9015
EP2_DI_Q27_VKLJUCENO_omogoci | DIGITAL | IOD_EP2_disk | D9016
EP2_DI_Q34_VKLJUCENO_omogoci | DIGITAL | IOD_EP2_disk | D9017
EP2_DI_Q30_VKLJUCENO_omogoci | DIGITAL | IOD_EP2_disk | D9018
NOT_EP2_DI_Q1_GlavnoStikalo_ON_omogoci | DIGITAL | IOD_EP2_disk | D9019
NOT_EP2_DI_Q2_Rezerva_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9020
NOT_EP2_DI_Q5_OdcKlima1_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9021
NOT_EP2_DI_Q6_OdcKlima2_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9022
NOT_EP2_DI_Q7_OdcKlima3_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9023
NOT_EP2_DI_Q8_OdcKlima4_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9024
NOT_EP2_DI_Q9_OdcKlima5_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9025
NOT_EP2_DI_Q10_OdcKlima6_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9026
NOT_EP2_DI_Q11_OdcVent1_ON_omogoci | DIGITAL | IOD_EP2_disk | D9027
NOT_EP2_DI_Q12_Rezerva_ON_omogoci | DIGITAL | IOD_EP2_disk | D9028
NOT_EP2_DI_Q25_OdcUpsA_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9029
NOT_EP2_DI_Q26_OdcByA_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9030
NOT_EP2_DI_Q27_OdcByUpsA_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9031
NOT_EP2_DI_Q31_DovByUpsA_ON_omogoci | DIGITAL | IOD_EP2_disk | D9032
EP2_DI_Q32_DovByA_ON_omogoci | DIGITAL | IOD_EP2_disk | D9033
NOT_EP2_DI_Q28_OdcUpsB_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9034
EP2DI_Q29_OdcByB_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9035
NOT_EP2_DI_Q30_OdcByUpsB_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9036
NOT_EP2_DI_Q33_DovByUpsB_ON_omogoci | DIGITAL | IOD_EP2_disk | D9037
EP2DI_Q34_DovByB_ON_omogoci | DIGITAL | IOD_EP2_disk | D9038
NOT_EP2_DI_Klima5_ERR_omogoci | DIGITAL | IOD_EP2_disk | D9039
NOT_EP2_DI_Klima6_ERR_omogoci | DIGITAL | IOD_EP2_disk | D9040
EP2TempAlarmPoint | REAL | IOD_EP2 | EP2:.TempAlarmPoint | 0 | 60.0 | 0 | 60.0 | °C | ##.#
EP2ErrCommScada2 | DIGITAL | IOD_EP2 | EP2:.ErrCommScada2
EP2ComSCADA2 | DIGITAL | IOD_EP2 | EP2:.ComSCADA2
EP2_ErrCommScada_omogoci2 | DIGITAL | IOD_EP2_disk | D9043
EP2Server_A_Izpad | DIGITAL | IOD_EP2_disk | D9044
EP2Server_B_Izpad | DIGITAL | IOD_EP2_disk | D9045
EP2_RazlikaUr | REAL | IOD_EP2 | EP2:.RazlikaUr | [5 empty] | ##.#
EP2_ComSCADA_stevec3 | INT | IOD_EP2_mem | I9048
EP2_ComSCADA_stevec | INT | IOD_EP2_mem | I9050
EP2ComSCADA3 | DIGITAL | IOD_EP2 | EP2:.ComSCADA3
EP2kom_nast_cas_izpada | INT | IOD_EP2 | EP2:.kom_nast_cas_izpada
EP2_Circ1_MaximumDemandA2 | REAL | IOD_EP2 | EP2:.Circ[1].MaximumDemandA2 | 0 | 1200.0 | 0 | 1200.0 | A | ###.# | 6157 | 1
EP2_Circ1_MaximumDemandA3 | REAL | IOD_EP2 | EP2:.Circ[1].MaximumDemandA3 | 0 | 1200.0 | 0 | 1200.0 | A | ###.# | 6157 | 1
EP2Circ1RazEner_D_SCADA | REAL | IOD_EP2 | EP2:.Circ[1].RazEner_D_SCADA | [6 empty] | 6157 | 1
EP2Circ1RazEner_T_SCADA | REAL | IOD_EP2 | EP2:.Circ[1].RazEner_T_SCADA | [6 empty] | 6157 | 1
EP2Circ1RazEner_M_SCADA | REAL | IOD_EP2 | EP2:.Circ[1].RazEner_M_SCADA | [6 empty] | 6157 | 1
EP2Circ_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Dnevne_energija_scada1 | [6 empty] | 6157 | 1
EP2Circ_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Dnevne_energija_scada2 | [6 empty] | 6157 | 1
EP2Circ_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Tedenska_energija_scada1 | [6 empty] | 6157 | 1
EP2Circ_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Tedenska_energija_scada2 | [6 empty] | 6157 | 1
EP2Circ_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Mesecna_energija_scada1 | [6 empty] | 6157 | 1
EP2Circ_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Mesecna_energija_scada2 | [6 empty] | 6157 | 1
EP2Circ_Vpis_Dnevne_energija_scada1_mem | DIGITAL | IOD_EP2_disk | D10000
EP2Circ_Vpis_Dnevne_energija_scada2_mem | DIGITAL | IOD_EP2_disk | D10001
EP2Circ_Vpis_Tedenska_energija_scada1_mem | DIGITAL | IOD_EP2_disk | D10002
EP2Circ_Vpis_Tedenska_energija_scada2_mem | DIGITAL | IOD_EP2_disk | D10003
EP2Circ_Vpis_Mesecna_energija_scada1_mem | DIGITAL | IOD_EP2_disk | D10004
EP2Circ_Vpis_Mesecna_energija_scada2_mem | DIGITAL | IOD_EP2_disk | D10005
[10 empty] | 6157 | 1
[10 empty] | 6157 | 1
[10 empty] | 6157 | 1
[10 empty] | 6157 | 1
[10 empty] | 6157 | 1
[10 empty] | 6157 | 1
[10 empty] | 6157 | 1
[10 empty] | 6157 | 1
[10 empty] | 6157 | 1
[10 empty] | 6157 | 1
[10 empty] | 6157 | 1

## variable_1
EP2_AlarmGenCirc1 | DIGITAL | IOD_EP2 | EP2:.AlarmGenCirc1
EP2_AlarmGenComm | DIGITAL | IOD_EP2 | EP2:.AlarmGenComm
EP2_AlarmGenDI | DIGITAL | IOD_EP2 | EP2:.AlarmGenDI
EP2_AlarmGenKlima5 | DIGITAL | IOD_EP2 | EP2:.AlarmGenKlima5
EP2_AlarmGenKlima6 | DIGITAL | IOD_EP2 | EP2:.AlarmGenKlima6
EP2_AlarmGenPMM1 | DIGITAL | IOD_EP2 | EP2:.AlarmGenPMM1
EP2_AlarmGenPMM2 | DIGITAL | IOD_EP2 | EP2:.AlarmGenPMM2
EP2_AlarmGenPMM3 | DIGITAL | IOD_EP2 | EP2:.AlarmGenPMM3
EP2_AlarmGenUPS1 | DIGITAL | IOD_EP2 | EP2:.AlarmGenUPS1
EP2_AlarmGenUPS2 | DIGITAL | IOD_EP2 | EP2:.AlarmGenUPS2
EP2_Circ1_CosFi_III | REAL | IOD_EP2 | EP2:.Circ[1].CosFi_III
EP2_Circ1_DelovnaEnergija | REAL | IOD_EP2 | EP2:.Circ[1].DelovnaEnergija
EP2_Circ1_DelovnaMoc_III | REAL | IOD_EP2 | EP2:.Circ[1].DelovnaMoc_III
EP2_Circ1_DelovnaMoc_L1 | REAL | IOD_EP2 | EP2:.Circ[1].DelovnaMoc_L1
EP2_Circ1_DelovnaMoc_L2 | REAL | IOD_EP2 | EP2:.Circ[1].DelovnaMoc_L2
EP2_Circ1_DelovnaMoc_L3 | REAL | IOD_EP2 | EP2:.Circ[1].DelovnaMoc_L3
EP2_Circ1_Frekvenca_L1 | REAL | IOD_EP2 | EP2:.Circ[1].Frekvenca_L1
EP2_Circ1_InduktivnaEnergija | REAL | IOD_EP2 | EP2:.Circ[1].InduktivnaEnergija
EP2_Circ1_InduktivnaMoc_III | REAL | IOD_EP2 | EP2:.Circ[1].InduktivnaMoc_III
EP2_Circ1_JalovaMoc_L1 | REAL | IOD_EP2 | EP2:.Circ[1].JalovaMoc_L1
EP2_Circ1_JalovaMoc_L2 | REAL | IOD_EP2 | EP2:.Circ[1].JalovaMoc_L2
EP2_Circ1_JalovaMoc_L3 | REAL | IOD_EP2 | EP2:.Circ[1].JalovaMoc_L3
EP2_Circ1_KapacitivnaEnergija | REAL | IOD_EP2 | EP2:.Circ[1].KapacitivnaEnergija
EP2_Circ1_KapacitivnaMoc_III | REAL | IOD_EP2 | EP2:.Circ[1].KapacitivnaMoc_III
EP2_Circ1_MaximumDemand | REAL | IOD_EP2 | EP2:.Circ[1].MaximumDemand
EP2_Circ1_Napetost_L1_L2 | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L1_L2
EP2_Circ1_Napetost_L1_N | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L1_N
EP2_Circ1_Napetost_L2_L3 | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L2_L3
EP2_Circ1_Napetost_L2_N | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L2_N
EP2_Circ1_Napetost_L3_L1 | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L3_L1
EP2_Circ1_Napetost_L3_N | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L3_N
EP2_Circ1_NavideznaMoc_III | REAL | IOD_EP2 | EP2:.Circ[1].NavideznaMoc_III
EP2_Circ1_NicelniTok | REAL | IOD_EP2 | EP2:.Circ[1].NicelniTok
EP2_Circ1_PowerFactor_III | REAL | IOD_EP2 | EP2:.Circ[1].PowerFactor_III
EP2_Circ1_PowerFactor_L1 | REAL | IOD_EP2 | EP2:.Circ[1].PowerFactor_L1
EP2_Circ1_PowerFactor_L2 | REAL | IOD_EP2 | EP2:.Circ[1].PowerFactor_L2
EP2_Circ1_PowerFactor_L3 | REAL | IOD_EP2 | EP2:.Circ[1].PowerFactor_L3
EP2_Circ1_THDI_L1 | REAL | IOD_EP2 | EP2:.Circ[1].THDI_L1
EP2_Circ1_THDI_L2 | REAL | IOD_EP2 | EP2:.Circ[1].THDI_L2
EP2_Circ1_THDI_L3 | REAL | IOD_EP2 | EP2:.Circ[1].THDI_L3
EP2_Circ1_THDV_L1 | REAL | IOD_EP2 | EP2:.Circ[1].THDV_L1
EP2_Circ1_THDV_L2 | REAL | IOD_EP2 | EP2:.Circ[1].THDV_L2
EP2_Circ1_THDV_L3 | REAL | IOD_EP2 | EP2:.Circ[1].THDV_L3
EP2_Circ1_Tok_L1 | REAL | IOD_EP2 | EP2:.Circ[1].Tok_L1
EP2_Circ1_Tok_L2 | REAL | IOD_EP2 | EP2:.Circ[1].Tok_L2
EP2_Circ1_Tok_L3 | REAL | IOD_EP2 | EP2:.Circ[1].Tok_L3
EP2_Circ1_TokPovprecje_III | REAL | IOD_EP2 | EP2:.Circ[1].TokPovprecje_III
EP2_Circutor_CosFi_III | REAL | IOD_EP2 | EP2:.Circutor.CosFi_III
EP2_Circutor_DelovnaEnergija | REAL | IOD_EP2 | EP2:.Circutor.DelovnaEnergija
EP2_Circutor_DelovnaMoc_III | REAL | IOD_EP2 | EP2:.Circutor.DelovnaMoc_III
EP2_Circutor_DelovnaMoc_L1 | REAL | IOD_EP2 | EP2:.Circutor.DelovnaMoc_L1
EP2_Circutor_DelovnaMoc_L2 | REAL | IOD_EP2 | EP2:.Circutor.DelovnaMoc_L2
EP2_Circutor_DelovnaMoc_L3 | REAL | IOD_EP2 | EP2:.Circutor.DelovnaMoc_L3
EP2_Circutor_Frekvenca_L1 | REAL | IOD_EP2 | EP2:.Circutor.Frekvenca_L1
EP2_Circutor_InduktivnaEnergija | REAL | IOD_EP2 | EP2:.Circutor.InduktivnaEnergija
EP2_Circutor_InduktivnaMoc_III | REAL | IOD_EP2 | EP2:.Circutor.InduktivnaMoc_III
EP2_Circutor_JalovaMoc_L1 | REAL | IOD_EP2 | EP2:.Circutor.JalovaMoc_L1
EP2_Circutor_JalovaMoc_L2 | REAL | IOD_EP2 | EP2:.Circutor.JalovaMoc_L2
EP2_Circutor_JalovaMoc_L3 | REAL | IOD_EP2 | EP2:.Circutor.JalovaMoc_L3
EP2_Circutor_KapacitivnaEnergija | REAL | IOD_EP2 | EP2:.Circutor.KapacitivnaEnergija
EP2_Circutor_KapacitivnaMoc_III | REAL | IOD_EP2 | EP2:.Circutor.KapacitivnaMoc_III
EP2_Circutor_MaximumDemand | REAL | IOD_EP2 | EP2:.Circutor.MaximumDemand
EP2_Circutor_Napetost_L1_L2 | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L1_L2
EP2_Circutor_Napetost_L1_N | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L1_N
EP2_Circutor_Napetost_L2_L3 | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L2_L3
EP2_Circutor_Napetost_L2_N | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L2_N
EP2_Circutor_Napetost_L3_L1 | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L3_L1
EP2_Circutor_Napetost_L3_N | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L3_N
EP2_Circutor_NavideznaMoc_III | REAL | IOD_EP2 | EP2:.Circutor.NavideznaMoc_III
EP2_Circutor_NicelniTok | REAL | IOD_EP2 | EP2:.Circutor.NicelniTok
EP2_Circutor_PowerFactor_III | REAL | IOD_EP2 | EP2:.Circutor.PowerFactor_III
EP2_Circutor_PowerFactor_L1 | REAL | IOD_EP2 | EP2:.Circutor.PowerFactor_L1
EP2_Circutor_PowerFactor_L2 | REAL | IOD_EP2 | EP2:.Circutor.PowerFactor_L2
EP2_Circutor_PowerFactor_L3 | REAL | IOD_EP2 | EP2:.Circutor.PowerFactor_L3
EP2_Circutor_THDI_L1 | REAL | IOD_EP2 | EP2:.Circutor.THDI_L1
EP2_Circutor_THDI_L2 | REAL | IOD_EP2 | EP2:.Circutor.THDI_L2
EP2_Circutor_THDI_L3 | REAL | IOD_EP2 | EP2:.Circutor.THDI_L3
EP2_Circutor_THDV_L1 | REAL | IOD_EP2 | EP2:.Circutor.THDV_L1
EP2_Circutor_THDV_L2 | REAL | IOD_EP2 | EP2:.Circutor.THDV_L2
EP2_Circutor_THDV_L3 | REAL | IOD_EP2 | EP2:.Circutor.THDV_L3
EP2_Circutor_Tok_L1 | REAL | IOD_EP2 | EP2:.Circutor.Tok_L1
EP2_Circutor_Tok_L2 | REAL | IOD_EP2 | EP2:.Circutor.Tok_L2
EP2_Circutor_Tok_L3 | REAL | IOD_EP2 | EP2:.Circutor.Tok_L3
EP2_Circutor_TokPovprecje_III | REAL | IOD_EP2 | EP2:.Circutor.TokPovprecje_III
EP2_ComSCADA | DIGITAL | IOD_EP2 | EP2:.ComSCADA
EP2_ComSCADA1 | DIGITAL | IOD_EP2 | EP2:.ComSCADA1
EP2_DateTime_Dan | INT | IOD_EP2 | EP2:.DateTime.Dan | BYTE
EP2_DateTime_Leto | INT | IOD_EP2 | EP2:.DateTime.Leto | BYTE
EP2_DateTime_Mesec | INT | IOD_EP2 | EP2:.DateTime.Mesec | BYTE
EP2_DateTime_Minuta | INT | IOD_EP2 | EP2:.DateTime.Minuta | BYTE
EP2_DateTime_Sekunda | INT | IOD_EP2 | EP2:.DateTime.Sekunda | BYTE
EP2_DateTime_Ura | INT | IOD_EP2 | EP2:.DateTime.Ura | BYTE
EP2_DI_Klima5_ERR | DIGITAL | IOD_EP2 | EP2:.DI_Klima5_ERR
EP2_DI_Klima5_ON | DIGITAL | IOD_EP2 | EP2:.DI_Klima5_ON
EP2_DI_Klima6_ERR | DIGITAL | IOD_EP2 | EP2:.DI_Klima6_ERR
EP2_DI_Klima6_ON | DIGITAL | IOD_EP2 | EP2:.DI_Klima6_ON
EP2_DI_KlimaSplit1_ERR | DIGITAL | IOD_EP2 | EP2:.DI_KlimaSplit1_ERR
EP2_DI_KlimaSplit1_ON | DIGITAL | IOD_EP2 | EP2:.DI_KlimaSplit1_ON
EP2_DI_Q10_OdcKlima6_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q10_OdcKlima6_IZP
EP2_DI_Q10_OdcKlima6_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q10_OdcKlima6_ON
EP2_DI_Q11_OdcVent1_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q11_OdcVent1_ON
EP2_DI_Q12_Rezerva_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q12_Rezerva_ON
EP2_DI_Q1_GlavnoStikalo_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q1_GlavnoStikalo_ON
EP2_DI_Q25_OdcUpsA_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q25_OdcUpsA_IZP
EP2_DI_Q25_OdcUpsA_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q25_OdcUpsA_ON
EP2_DI_Q26_OdcByA_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q26_OdcByA_IZP
EP2_DI_Q26_OdcByA_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q26_OdcByA_ON
EP2_DI_Q27_OdcByUpsA_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q27_OdcByUpsA_IZP
EP2_DI_Q27_OdcByUpsA_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q27_OdcByUpsA_ON
EP2_DI_Q28_OdcUpsB_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q28_OdcUpsB_IZP
EP2_DI_Q28_OdcUpsB_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q28_OdcUpsB_ON
EP2_DI_Q29_OdcByB_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q29_OdcByB_IZP
EP2_DI_Q29_OdcByB_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q29_OdcByB_ON
EP2_DI_Q2_Rezerva_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q2_Rezerva_IZP
EP2_DI_Q2_Rezerva_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q2_Rezerva_ON
EP2_DI_Q30_OdcByUpsB_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q30_OdcByUpsB_IZP
EP2_DI_Q30_OdcByUpsB_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q30_OdcByUpsB_ON
EP2_DI_Q31_DovByUpsA_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q31_DovByUpsA_ON
EP2_DI_Q32_DovByA_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q32_DovByA_ON
EP2_DI_Q33_DovByUpsB_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q33_DovByUpsB_ON
EP2_DI_Q34_DovByB_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q34_DovByB_ON
EP2_DI_Q5_OdcKlima1_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q5_OdcKlima1_IZP
EP2_DI_Q5_OdcKlima1_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q5_OdcKlima1_ON
EP2_DI_Q6_OdcKlima2_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q6_OdcKlima2_IZP
EP2_DI_Q6_OdcKlima2_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q6_OdcKlima2_ON
EP2_DI_Q7_OdcKlima3_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q7_OdcKlima3_IZP
EP2_DI_Q7_OdcKlima3_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q7_OdcKlima3_ON
EP2_DI_Q8_OdcKlima4_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q8_OdcKlima4_IZP
EP2_DI_Q8_OdcKlima4_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q8_OdcKlima4_ON
EP2_DI_Q9_OdcKlima5_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q9_OdcKlima5_IZP
EP2_DI_Q9_OdcKlima5_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q9_OdcKlima5_ON
EP2_DI_RazlitjeVodeK5K6 | DIGITAL | IOD_EP2 | EP2:.DI_RazlitjeVodeK5K6
EP2_DI_UPS_Alarm | DIGITAL | IOD_EP2 | EP2:.DI_UPS_Alarm
EP2_DI_UPS_BatNacin | DIGITAL | IOD_EP2 | EP2:.DI_UPS_BatNacin
EP2_DI_UPS_Polnjenje | DIGITAL | IOD_EP2 | EP2:.DI_UPS_Polnjenje
EP2_DI_UpsA_ERR | DIGITAL | IOD_EP2 | EP2:.DIN_UpsA_ERR
EP2_DI_UpsA_ON | DIGITAL | IOD_EP2 | EP2:.DIN_UpsA_BypassON
EP2_DI_UpsB_ERR | DIGITAL | IOD_EP2 | EP2:.DIN_UpsB_ERR
EP2_DI_UpsB_ON | DIGITAL | IOD_EP2 | EP2:.DIN_UpsB_BypassON
EP2_DO_Klima5_Izklop | DIGITAL | IOD_EP2 | EP2:.DO_Klima5_Izklop
EP2_DO_Klima6_Izklop | DIGITAL | IOD_EP2 | EP2:.DO_Klima6_Izklop
EP2_ErrComCirc1 | DIGITAL | IOD_EP2 | EP2:.ErrComCirc[1]
EP2_ErrComCirc2 | DIGITAL | IOD_EP2 | EP2:.ErrComCirc[2]
EP2_ErrComCirc3 | DIGITAL | IOD_EP2 | EP2:.ErrComCirc[3]
EP2_ErrComCirc4 | DIGITAL | IOD_EP2 | EP2:.ErrComCirc[4]
EP2_ErrComCirc5 | DIGITAL | IOD_EP2 | EP2:.ErrComCirc[5]
EP2_ErrComKlima1 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[1]
EP2_ErrComKlima2 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[2]
EP2_ErrComKlima3 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[3]
EP2_ErrComKlima4 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[4]
EP2_ErrComKlima5 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[5]
EP2_ErrComKlima6 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[6]
EP2_ErrCommScada | DIGITAL | IOD_EP2 | EP2:.ErrCommScada
EP2_ErrComPanelPLC | DIGITAL | IOD_EP2 | EP2:.ErrComPanelPLC
EP2_ErrComPMM1 | DIGITAL | IOD_EP2 | EP2:.ErrComPMM[1]
EP2_ErrComPMM2 | DIGITAL | IOD_EP2 | EP2:.ErrComPMM[2]
EP2_ErrComPMM3 | DIGITAL | IOD_EP2 | EP2:.ErrComPMM[3]
EP2_ErrComPort2 | DIGITAL | IOD_EP2 | EP2:.ErrComPort2
EP2_ErrComPort3 | DIGITAL | IOD_EP2 | EP2:.ErrComPort3
EP2_ErrComPort4 | DIGITAL | IOD_EP2 | EP2:.ErrComPort4
EP2_ErrComUPS1 | DIGITAL | IOD_EP2 | EP2:.ErrComUPS[1]
EP2_ErrComUPS2 | DIGITAL | IOD_EP2 | EP2:.ErrComUPS[2]
EP2_Klima1_AlarmKompresor1 | DIGITAL | IOD_EP2 | EP2:.Klima[1].AlarmKompresor1
EP2_Klima1_AlarmKompresor2 | DIGITAL | IOD_EP2 | EP2:.Klima[1].AlarmKompresor2
EP2_Klima1_Deluje | DIGITAL | IOD_EP2 | EP2:.Klima[1].Deluje
EP2_Klima1_EnergySaving | DIGITAL | IOD_EP2 | EP2:.Klima[1].EnergySaving
EP2_Klima1_FaultyEPROM | DIGITAL | IOD_EP2 | EP2:.Klima[1].FaultyEPROM
EP2_Klima1_FenThermalCutout | DIGITAL | IOD_EP2 | EP2:.Klima[1].FenThermalCutout
EP2_Klima1_GeneralAlarm | DIGITAL | IOD_EP2 | EP2:.Klima[1].GeneralAlarm
EP2_Klima1_GrelecStatus | INT | IOD_EP2 | EP2:.Klima[1].GrelecStatus | BYTE
EP2_Klima1_IzhodniVentStatus | INT | IOD_EP2 | EP2:.Klima[1].IzhodniVentStatus | BYTE
EP2_Klima1_Kompresor1naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[1].Kompresor1naMejiObrUr
EP2_Klima1_Kompresor2naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[1].Kompresor2naMejiObrUr
EP2_Klima1_KompresorStatus | INT | IOD_EP2 | EP2:.Klima[1].KompresorStatus | BYTE
EP2_Klima1_Napaka | DIGITAL | IOD_EP2 | EP2:.Klima[1].Napaka
EP2_Klima1_NapakaPriPretokuZraka | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaPriPretokuZraka
EP2_Klima1_NapakaSenzorPovratVod | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaSenzorPovratVode
EP2_Klima1_NapakaSenzorTempIzpih | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaSenzorTempIzpiha
EP2_Klima1_NapakaSenzorTempProst | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaSenzorTempProstora
EP2_Klima1_NapakaSenzorVlaznosti | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaSenzorVlaznosti
EP2_Klima1_NapakaSenzorZunanjeTemp | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaSenzorZunanjeTemp
EP2_Klima1_NastMaxTemp | REAL | IOD_EP2 | EP2:.Klima[1].NastMaxTemp
EP2_Klima1_NastMaxVlaznost | REAL | IOD_EP2 | EP2:.Klima[1].NastMaxVlaznost
EP2_Klima1_NastMinTemp | REAL | IOD_EP2 | EP2:.Klima[1].NastMinTemp
EP2_Klima1_NastMinVlaznost | REAL | IOD_EP2 | EP2:.Klima[1].NastMinVlaznost
EP2_Klima1_NastTempProstora | REAL | IOD_EP2 | EP2:.Klima[1].NastTempProstora
EP2_Klima1_NastVlaznost | REAL | IOD_EP2 | EP2:.Klima[1].NastVlaznost
EP2_Klima1_NiTokaVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[1].NiTokaVVlazilcu
EP2_Klima1_NiVodeVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[1].NiVodeVVlazilcu
EP2_Klima1_NizekPritiskKompresor1 | DIGITAL | IOD_EP2 | EP2:.Klima[1].NizekPritiskKompresor1
EP2_Klima1_NizekPritiskKompresor2 | DIGITAL | IOD_EP2 | EP2:.Klima[1].NizekPritiskKompresor2
EP2_Klima1_NizkaTempPovratneVode | DIGITAL | IOD_EP2 | EP2:.Klima[1].NizkaTempPovratneVode
EP2_Klima1_NizkaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.Klima[1].NizkaTempVProstoru
EP2_Klima1_NizkaVlaznost | DIGITAL | IOD_EP2 | EP2:.Klima[1].NizkaVlaznost
EP2_Klima1_ObratovalneUre | REAL | IOD_EP2 | EP2:.Klima[1].ObratovalneUre
EP2_Klima1_OnOffEnablingBySupervisor | DIGITAL | IOD_EP2 | EP2:.Klima[1].OnOffEnablingBySupervisor
EP2_Klima1_PozarniAlarm | DIGITAL | IOD_EP2 | EP2:.Klima[1].PozarniAlarm
EP2_Klima1_Razvlazevanje | DIGITAL | IOD_EP2 | EP2:.Klima[1].Razvlazevanje
EP2_Klima1_RemoteOFFtoOutput | DIGITAL | IOD_EP2 | EP2:.Klima[1].RemoteOFFtoOutput
EP2_Klima1_RemoteOnOff | DIGITAL | IOD_EP2 | EP2:.Klima[1].RemoteOnOff
EP2_Klima1_RocniIzklop | DIGITAL | IOD_EP2 | EP2:.Klima[1].RocniIzklop
EP2_Klima1_SenzorjiStatus | DIGITAL | IOD_EP2 | EP2:.Klima[1].SenzorjiStatus
EP2_Klima1_StoppedByAlarms | DIGITAL | IOD_EP2 | EP2:.Klima[1].StoppedByAlarms
EP2_Klima1_TemperaturaProstora | REAL | IOD_EP2 | EP2:.Klima[1].TemperaturaProstora
EP2_Klima1_TempIzpihanegaZraka | REAL | IOD_EP2 | EP2:.Klima[1].TempIzpihanegaZraka
EP2_Klima1_TempPovratneVode | REAL | IOD_EP2 | EP2:.Klima[1].TempPovratneVode
EP2_Klima1_ThermalCutoutHeater1 | DIGITAL | IOD_EP2 | EP2:.Klima[1].ThermalCutoutHeater1
EP2_Klima1_ThermalCutoutHeater2 | DIGITAL | IOD_EP2 | EP2:.Klima[1].ThermalCutoutHeater2
EP2_Klima1_UnitOnOff | DIGITAL | IOD_EP2 | EP2:.Klima[1].UnitOnOff
EP2_Klima1_VentilatorNaMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[1].VentilatorNaMejiObrUr
EP2_Klima1_VentilGretjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.Klima[1].VentilGretjeOdpiranje
EP2_Klima1_VentilGretjeZapiranje | DIGITAL | IOD_EP2 | EP2:.Klima[1].VentilGretjeZapiranje
EP2_Klima1_VentilHlajenjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.Klima[1].VentilHlajenjeOdpiranje
EP2_Klima1_VentilHlajenjeZapiranje | DIGITAL | IOD_EP2 | EP2:.Klima[1].VentilHlajenjeZapiranje
EP2_Klima1_VisokaTempPovratneVode | DIGITAL | IOD_EP2 | EP2:.Klima[1].VisokaTempPovratneVode
EP2_Klima1_VisokaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.Klima[1].VisokaTempVProstoru
EP2_Klima1_VisokaVlaznost | DIGITAL | IOD_EP2 | EP2:.Klima[1].VisokaVlaznost
EP2_Klima1_VisokTokVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[1].VisokTokVVlazilcu
EP2_Klima1_Vlazenje | DIGITAL | IOD_EP2 | EP2:.Klima[1].Vlazenje
EP2_Klima1_VlazilecStatus | INT | IOD_EP2 | EP2:.Klima[1].VlazilecStatus | BYTE
EP2_Klima1_VlaznostProstora | REAL | IOD_EP2 | EP2:.Klima[1].VlaznostProstora
EP2_Klima1_ZamasenFilter | DIGITAL | IOD_EP2 | EP2:.Klima[1].ZamasenFilter
EP2_Klima1_ZunanjaTemp | REAL | IOD_EP2 | EP2:.Klima[1].ZunanjaTemp
EP2_Klima2_AlarmKompresor1 | DIGITAL | IOD_EP2 | EP2:.Klima[2].AlarmKompresor1
EP2_Klima2_AlarmKompresor2 | DIGITAL | IOD_EP2 | EP2:.Klima[2].AlarmKompresor2
EP2_Klima2_Deluje | DIGITAL | IOD_EP2 | EP2:.Klima[2].Deluje
EP2_Klima2_EnergySaving | DIGITAL | IOD_EP2 | EP2:.Klima[2].EnergySaving
EP2_Klima2_FaultyEPROM | DIGITAL | IOD_EP2 | EP2:.Klima[2].FaultyEPROM
EP2_Klima2_FenThermalCutout | DIGITAL | IOD_EP2 | EP2:.Klima[2].FenThermalCutout
EP2_Klima2_GeneralAlarm | DIGITAL | IOD_EP2 | EP2:.Klima[2].GeneralAlarm
EP2_Klima2_GrelecStatus | INT | IOD_EP2 | EP2:.Klima[2].GrelecStatus | BYTE
EP2_Klima2_IzhodniVentStatus | INT | IOD_EP2 | EP2:.Klima[2].IzhodniVentStatus | BYTE
EP2_Klima2_Kompresor1naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[2].Kompresor1naMejiObrUr
EP2_Klima2_Kompresor2naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[2].Kompresor2naMejiObrUr
EP2_Klima2_KompresorStatus | INT | IOD_EP2 | EP2:.Klima[2].KompresorStatus | BYTE
EP2_Klima2_Napaka | DIGITAL | IOD_EP2 | EP2:.Klima[2].Napaka
EP2_Klima2_NapakaPriPretokuZraka | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaPriPretokuZraka
EP2_Klima2_NapakaSenzorPovratVode | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaSenzorPovratVode
EP2_Klima2_NapakaSenzorTempIzpih | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaSenzorTempIzpiha
EP2_Klima2_NapakaSenzorTempProst | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaSenzorTempProstora
EP2_Klima2_NapakaSenzorVlaznosti | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaSenzorVlaznosti
EP2_Klima2_NapakaSenzorZunanjeTemp | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaSenzorZunanjeTemp
EP2_Klima2_NastMaxTemp | REAL | IOD_EP2 | EP2:.Klima[2].NastMaxTemp
EP2_Klima2_NastMaxVlaznost | REAL | IOD_EP2 | EP2:.Klima[2].NastMaxVlaznost
EP2_Klima2_NastMinTemp | REAL | IOD_EP2 | EP2:.Klima[2].NastMinTemp
EP2_Klima2_NastMinVlaznost | REAL | IOD_EP2 | EP2:.Klima[2].NastMinVlaznost
EP2_Klima2_NastTempProstora | REAL | IOD_EP2 | EP2:.Klima[2].NastTempProstora
EP2_Klima2_NastVlaznost | REAL | IOD_EP2 | EP2:.Klima[2].NastVlaznost
EP2_Klima2_NiTokaVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[2].NiTokaVVlazilcu
EP2_Klima2_NiVodeVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[2].NiVodeVVlazilcu
EP2_Klima2_NizekPritiskKompresor1 | DIGITAL | IOD_EP2 | EP2:.Klima[2].NizekPritiskKompresor1
EP2_Klima2_NizekPritiskKompresor2 | DIGITAL | IOD_EP2 | EP2:.Klima[2].NizekPritiskKompresor2
EP2_Klima2_NizkaTempPovratneVode | DIGITAL | IOD_EP2 | EP2:.Klima[2].NizkaTempPovratneVode
EP2_Klima2_NizkaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.Klima[2].NizkaTempVProstoru
EP2_Klima2_NizkaVlaznost | DIGITAL | IOD_EP2 | EP2:.Klima[2].NizkaVlaznost
EP2_Klima2_ObratovalneUre | REAL | IOD_EP2 | EP2:.Klima[2].ObratovalneUre
EP2_Klima2_OnOffEnablingBySupervisor | DIGITAL | IOD_EP2 | EP2:.Klima[2].OnOffEnablingBySupervisor
EP2_Klima2_PozarniAlarm | DIGITAL | IOD_EP2 | EP2:.Klima[2].PozarniAlarm
EP2_Klima2_Razvlazevanje | DIGITAL | IOD_EP2 | EP2:.Klima[2].Razvlazevanje
EP2_Klima2_RemoteOFFtoOutput | DIGITAL | IOD_EP2 | EP2:.Klima[2].RemoteOFFtoOutput
EP2_Klima2_RemoteOnOff | DIGITAL | IOD_EP2 | EP2:.Klima[2].RemoteOnOff
EP2_Klima2_RocniIzklop | DIGITAL | IOD_EP2 | EP2:.Klima[2].RocniIzklop
EP2_Klima2_SenzorjiStatus | DIGITAL | IOD_EP2 | EP2:.Klima[2].SenzorjiStatus
EP2_Klima2_StoppedByAlarms | DIGITAL | IOD_EP2 | EP2:.Klima[2].StoppedByAlarms
EP2_Klima2_TemperaturaProstora | REAL | IOD_EP2 | EP2:.Klima[2].TemperaturaProstora
EP2_Klima2_TempIzpihanegaZraka | REAL | IOD_EP2 | EP2:.Klima[2].TempIzpihanegaZraka
EP2_Klima2_TempPovratneVode | REAL | IOD_EP2 | EP2:.Klima[2].TempPovratneVode
EP2_Klima2_ThermalCutoutHeater1 | DIGITAL | IOD_EP2 | EP2:.Klima[2].ThermalCutoutHeater1
EP2_Klima2_ThermalCutoutHeater2 | DIGITAL | IOD_EP2 | EP2:.Klima[2].ThermalCutoutHeater2
EP2_Klima2_UnitOnOff | DIGITAL | IOD_EP2 | EP2:.Klima[2].UnitOnOff
EP2_Klima2_VentilatorNaMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[2].VentilatorNaMejiObrUr
EP2_Klima2_VentilGretjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.Klima[2].VentilGretjeOdpiranje
EP2_Klima2_VentilGretjeZapiranje | DIGITAL | IOD_EP2 | EP2:.Klima[2].VentilGretjeZapiranje
EP2_Klima2_VentilHlajenjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.Klima[2].VentilHlajenjeOdpiranje
EP2_Klima2_VentilHlajenjeZapiranje | DIGITAL | IOD_EP2 | EP2:.Klima[2].VentilHlajenjeZapiranje
EP2_Klima2_VisokaTempPovratneVod | DIGITAL | IOD_EP2 | EP2:.Klima[2].VisokaTempPovratneVode
EP2_Klima2_VisokaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.Klima[2].VisokaTempVProstoru
EP2_Klima2_VisokaVlaznost | DIGITAL | IOD_EP2 | EP2:.Klima[2].VisokaVlaznost
EP2_Klima2_VisokTokVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[2].VisokTokVVlazilcu
EP2_Klima2_Vlazenje | DIGITAL | IOD_EP2 | EP2:.Klima[2].Vlazenje
EP2_Klima2_VlazilecStatus | INT | IOD_EP2 | EP2:.Klima[2].VlazilecStatus | BYTE
EP2_Klima2_VlaznostProstora | REAL | IOD_EP2 | EP2:.Klima[2].VlaznostProstora
EP2_Klima2_ZamasenFilter | DIGITAL | IOD_EP2 | EP2:.Klima[2].ZamasenFilter
EP2_Klima2_ZunanjaTemp | REAL | IOD_EP2 | EP2:.Klima[2].ZunanjaTemp
EP2_KlimeNaCas | DIGITAL | IOD_EP2 | EP2:.KlimeNaCas
EP2_NapakaSenzorTemp1 | DIGITAL | IOD_EP2 | EP2:.NapakaSenzorTemp[1]
EP2_NapakaSenzorTemp2 | DIGITAL | IOD_EP2 | EP2:.NapakaSenzorTemp[2]
EP2_NapakaSenzorVlaga1 | DIGITAL | IOD_EP2 | EP2:.NapakaSenzorVlaga[1]
EP2_NapakaSenzorVlaga2 | DIGITAL | IOD_EP2 | EP2:.NapakaSenzorVlaga[2]
EP2_PMM1OverCurrentBetw1 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentBetw[1]
EP2_PMM1OverCurrentBetw2 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentBetw[2]
EP2_PMM1OverCurrentBetw3 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentBetw[3]
EP2_PMM1OverCurrentOver1 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentOver[1]
EP2_PMM1OverCurrentOver2 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentOver[2]
EP2_PMM1OverCurrentOver3 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentOver[3]
EP2_PMM2OverCurrentBetw1 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentBetw[1]
EP2_PMM2OverCurrentBetw2 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentBetw[2]
EP2_PMM2OverCurrentBetw3 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentBetw[3]
EP2_PMM2OverCurrentOver1 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentOver[1]
EP2_PMM2OverCurrentOver2 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentOver[2]
EP2_PMM2OverCurrentOver3 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentOver[3]
EP2_PMM3OverCurrentBetw1 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentBetw[1]
EP2_PMM3OverCurrentBetw2 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentBetw[2]
EP2_PMM3OverCurrentBetw3 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentBetw[3]
EP2_PMM3OverCurrentOver1 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentOver[1]
EP2_PMM3OverCurrentOver2 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentOver[2]
EP2_PMM3OverCurrentOver3 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentOver[3]
EP2_PMM1_ActivePowerPhaseA_kW | REAL | IOD_EP2 | EP2:.PMM[1].ActivePowerPhaseA_kW
EP2_PMM1_ActivePowerPhaseB_kW | REAL | IOD_EP2 | EP2:.PMM[1].ActivePowerPhaseB_kW
EP2_PMM1_ActivePowerPhaseC_kW | REAL | IOD_EP2 | EP2:.PMM[1].ActivePowerPhaseC_kW
EP2_PMM1_AlarmPhase1_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C01_16_60to80
EP2_PMM1_AlarmPhase1_C01_16_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C01_16_over80
EP2_PMM1_AlarmPhase1_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C17_32_60to80
EP2_PMM1_AlarmPhase1_C17_32_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C17_32_over80
EP2_PMM1_AlarmPhase1_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C33_42_60to80
EP2_PMM1_AlarmPhase1_C33_42_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C33_42_over80
EP2_PMM1_AlarmPhase1_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].GlobalAlarmReg
EP2_PMM1_AlarmPhase2_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C01_16_60to80
EP2_PMM1_AlarmPhase2_C01_16_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C01_16_over80
EP2_PMM1_AlarmPhase2_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C17_32_60to80
EP2_PMM1_AlarmPhase2_C17_32_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C17_32_over80
EP2_PMM1_AlarmPhase2_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C33_42_60to80
EP2_PMM1_AlarmPhase2_C33_42_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C33_42_over80
EP2_PMM1_AlarmPhase2_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].GlobalAlarmReg
EP2_PMM1_AlarmPhase3_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C01_16_60to80
EP2_PMM1_AlarmPhase3_C01_16_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C01_16_over80
EP2_PMM1_AlarmPhase3_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C17_32_60to80
EP2_PMM1_AlarmPhase3_C17_32_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C17_32_over80
EP2_PMM1_AlarmPhase3_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C33_42_60to80
EP2_PMM1_AlarmPhase3_C33_42_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C33_42_over80
EP2_PMM1_AlarmPhase3_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].GlobalAlarmReg
EP2_PMM1_Alarms | INT | IOD_EP2 | EP2:.PMM[1].Alarms
EP2_PMM1_AverageCurrent_A | REAL | IOD_EP2 | EP2:.PMM[1].AverageCurrent_A
EP2_PMM1_AveragePhaseToNeutral_V | REAL | IOD_EP2 | EP2:.PMM[1].AveragePhaseToNeutral_V
EP2_PMM1_AveragePhaseToPhase_V | REAL | IOD_EP2 | EP2:.PMM[1].AveragePhaseToPhase_V
EP2_PMM1_CurrentInPhaseA_A | REAL | IOD_EP2 | EP2:.PMM[1].CurrentInPhaseA_A
EP2_PMM1_CurrentInPhaseB_A | REAL | IOD_EP2 | EP2:.PMM[1].CurrentInPhaseB_A
EP2_PMM1_CurrentInPhaseC_A | REAL | IOD_EP2 | EP2:.PMM[1].CurrentInPhaseC_A
EP2_PMM1_EnergyConsumed_kWh | REAL | IOD_EP2 | EP2:.PMM[1].EnergyConsumed_kWh
EP2_PMM1_Napaka | DIGITAL | IOD_EP2 | EP2:.PMM[1].Napaka
EP2_PMM1_Frequency_Hz | REAL | IOD_EP2 | EP2:.PMM[1].Frequency_Hz
EP2_PMM1_NeutralCurrent_A | REAL | IOD_EP2 | EP2:.PMM[1].NeutralCurrent_A
EP2_PMM1_Phase1_Current10 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[10]
EP2_PMM1_Phase1_Current11 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[11]
EP2_PMM1_Phase1_Current12 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[12]
EP2_PMM1_Phase1_Current13 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[13]
EP2_PMM1_Phase1_Current14 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[14]
EP2_PMM1_Phase1_Current15 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[15]
EP2_PMM1_Phase1_Current16 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[16]
EP2_PMM1_Phase1_Current17 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[17]
EP2_PMM1_Phase1_Current18 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[18]
EP2_PMM1_Phase1_Current19 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[19]
EP2_PMM1_Phase1_Current1 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[1]
EP2_PMM1_Phase1_Current20 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[20]
EP2_PMM1_Phase1_Current21 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[21]
EP2_PMM1_Phase1_Current22 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[22]
EP2_PMM1_Phase1_Current23 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[23]
EP2_PMM1_Phase1_Current24 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[24]
EP2_PMM1_Phase1_Current25 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[25]
EP2_PMM1_Phase1_Current26 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[26]
EP2_PMM1_Phase1_Current27 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[27]
EP2_PMM1_Phase1_Current28 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[28]
EP2_PMM1_Phase1_Current29 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[29]
EP2_PMM1_Phase1_Current2 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[2]
EP2_PMM1_Phase1_Current30 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[30]
EP2_PMM1_Phase1_Current31 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[31]
EP2_PMM1_Phase1_Current32 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[32]
EP2_PMM1_Phase1_Current33 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[33]
EP2_PMM1_Phase1_Current34 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[34]
EP2_PMM1_Phase1_Current35 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[35]
EP2_PMM1_Phase1_Current36 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[36]
EP2_PMM1_Phase1_Current37 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[37]
EP2_PMM1_Phase1_Current38 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[38]
EP2_PMM1_Phase1_Current39 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[39]
EP2_PMM1_Phase1_Current3 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[3]
EP2_PMM1_Phase1_Current40 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[40]
EP2_PMM1_Phase1_Current41 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[41]
EP2_PMM1_Phase1_Current42 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[42]
EP2_PMM1_Phase1_Current4 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[4]
EP2_PMM1_Phase1_Current5 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[5]
EP2_PMM1_Phase1_Current6 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[6]
EP2_PMM1_Phase1_Current7 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[7]
EP2_PMM1_Phase1_Current8 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[8]
EP2_PMM1_Phase1_Current9 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[9]
EP2_PMM1_Phase2_Current10 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[10]
EP2_PMM1_Phase2_Current11 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[11]
EP2_PMM1_Phase2_Current12 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[12]
EP2_PMM1_Phase2_Current13 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[13]
EP2_PMM1_Phase2_Current14 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[14]
EP2_PMM1_Phase2_Current15 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[15]
EP2_PMM1_Phase2_Current16 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[16]
EP2_PMM1_Phase2_Current17 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[17]
EP2_PMM1_Phase2_Current18 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[18]
EP2_PMM1_Phase2_Current19 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[19]
EP2_PMM1_Phase2_Current1 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[1]
EP2_PMM1_Phase2_Current20 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[20]
EP2_PMM1_Phase2_Current21 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[21]
EP2_PMM1_Phase2_Current22 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[22]
EP2_PMM1_Phase2_Current23 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[23]
EP2_PMM1_Phase2_Current24 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[24]
EP2_PMM1_Phase2_Current25 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[25]
EP2_PMM1_Phase2_Current26 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[26]
EP2_PMM1_Phase2_Current27 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[27]
EP2_PMM1_Phase2_Current28 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[28]
EP2_PMM1_Phase2_Current29 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[29]
EP2_PMM1_Phase2_Current2 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[2]
EP2_PMM1_Phase2_Current30 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[30]
EP2_PMM1_Phase2_Current31 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[31]
EP2_PMM1_Phase2_Current32 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[32]
EP2_PMM1_Phase2_Current33 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[33]
EP2_PMM1_Phase2_Current34 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[34]
EP2_PMM1_Phase2_Current35 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[35]
EP2_PMM1_Phase2_Current36 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[36]
EP2_PMM1_Phase2_Current37 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[37]
EP2_PMM1_Phase2_Current38 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[38]
EP2_PMM1_Phase2_Current39 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[39]
EP2_PMM1_Phase2_Current3 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[3]
EP2_PMM1_Phase2_Current40 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[40]
EP2_PMM1_Phase2_Current41 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[41]
EP2_PMM1_Phase2_Current42 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[42]
EP2_PMM1_Phase2_Current4 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[4]
EP2_PMM1_Phase2_Current5 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[5]
EP2_PMM1_Phase2_Current6 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[6]
EP2_PMM1_Phase2_Current7 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[7]
EP2_PMM1_Phase2_Current8 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[8]
EP2_PMM1_Phase2_Current9 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[9]
EP2_PMM1_Phase3_Current10 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[10]
EP2_PMM1_Phase3_Current11 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[11]
EP2_PMM1_Phase3_Current12 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[12]
EP2_PMM1_Phase3_Current13 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[13]
EP2_PMM1_Phase3_Current14 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[14]
EP2_PMM1_Phase3_Current15 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[15]
EP2_PMM1_Phase3_Current16 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[16]
EP2_PMM1_Phase3_Current17 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[17]
EP2_PMM1_Phase3_Current18 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[18]
EP2_PMM1_Phase3_Current19 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[19]
EP2_PMM1_Phase3_Current1 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[1]
EP2_PMM1_Phase3_Current20 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[20]
EP2_PMM1_Phase3_Current21 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[21]
EP2_PMM1_Phase3_Current22 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[22]
EP2_PMM1_Phase3_Current23 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[23]
EP2_PMM1_Phase3_Current24 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[24]
EP2_PMM1_Phase3_Current25 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[25]
EP2_PMM1_Phase3_Current26 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[26]
EP2_PMM1_Phase3_Current27 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[27]
EP2_PMM1_Phase3_Current28 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[28]
EP2_PMM1_Phase3_Current29 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[29]
EP2_PMM1_Phase3_Current2 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[2]
EP2_PMM1_Phase3_Current30 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[30]
EP2_PMM1_Phase3_Current31 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[31]
EP2_PMM1_Phase3_Current32 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[32]
EP2_PMM1_Phase3_Current33 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[33]
EP2_PMM1_Phase3_Current34 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[34]
EP2_PMM1_Phase3_Current35 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[35]
EP2_PMM1_Phase3_Current36 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[36]
EP2_PMM1_Phase3_Current37 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[37]
EP2_PMM1_Phase3_Current38 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[38]
EP2_PMM1_Phase3_Current39 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[39]
EP2_PMM1_Phase3_Current3 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[3]
EP2_PMM1_Phase3_Current40 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[40]
EP2_PMM1_Phase3_Current41 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[41]
EP2_PMM1_Phase3_Current42 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[42]
EP2_PMM1_Phase3_Current4 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[4]
EP2_PMM1_Phase3_Current5 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[5]
EP2_PMM1_Phase3_Current6 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[6]
EP2_PMM1_Phase3_Current7 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[7]
EP2_PMM1_Phase3_Current8 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[8]
EP2_PMM1_Phase3_Current9 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[9]
EP2_PMM1_PowerFactorPhaseA | REAL | IOD_EP2 | EP2:.PMM[1].PowerFactorPhaseA
EP2_PMM1_PowerFactorPhaseB | REAL | IOD_EP2 | EP2:.PMM[1].PowerFactorPhaseB
EP2_PMM1_PowerFactorPhaseC | REAL | IOD_EP2 | EP2:.PMM[1].PowerFactorPhaseC
EP2_PMM1_TotalActivePower_kW | REAL | IOD_EP2 | EP2:.PMM[1].TotalActivePower_kW
EP2_PMM1_TotalAparentPower_kVA | REAL | IOD_EP2 | EP2:.PMM[1].TotalAparentPower_kVA
EP2_PMM1_TotalPowerFactor | REAL | IOD_EP2 | EP2:.PMM[1].TotalPowerFactor
EP2_PMM1_TotalReactivePower_kVAR | REAL | IOD_EP2 | EP2:.PMM[1].TotalReactivePower_kVAR
EP2_PMM1_VoltageBetweenPhaseAB_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseAB_V
EP2_PMM1_VoltageBetweenPhaseAN_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseAN_V
EP2_PMM1_VoltageBetweenPhaseBC_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseBC_V
EP2_PMM1_VoltageBetweenPhaseBN_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseBN_V
EP2_PMM1_VoltageBetweenPhaseCA_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseCA_V
EP2_PMM1_VoltageBetweenPhaseCN_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseCN_V
EP2_PMM2_ActivePowerPhaseA_kW | REAL | IOD_EP2 | EP2:.PMM[2].ActivePowerPhaseA_kW
EP2_PMM2_ActivePowerPhaseB_kW | REAL | IOD_EP2 | EP2:.PMM[2].ActivePowerPhaseB_kW
EP2_PMM2_ActivePowerPhaseC_kW | REAL | IOD_EP2 | EP2:.PMM[2].ActivePowerPhaseC_kW
EP2_PMM2_AlarmPhase1_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C01_16_60to80
EP2_PMM2_AlarmPhase1_C01_16_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C01_16_over80
EP2_PMM2_AlarmPhase1_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C17_32_60to80
EP2_PMM2_AlarmPhase1_C17_32_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C17_32_over80
EP2_PMM2_AlarmPhase1_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C33_42_60to80
EP2_PMM2_AlarmPhase1_C33_42_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C33_42_over80
EP2_PMM2_AlarmPhase1_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].GlobalAlarmReg
EP2_PMM2_AlarmPhase2_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C01_16_60to80
EP2_PMM2_AlarmPhase2_C01_16_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C01_16_over80
EP2_PMM2_AlarmPhase2_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C17_32_60to80
EP2_PMM2_AlarmPhase2_C17_32_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C17_32_over80
EP2_PMM2_AlarmPhase2_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C33_42_60to80
EP2_PMM2_AlarmPhase2_C33_42_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C33_42_over80
EP2_PMM2_AlarmPhase2_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].GlobalAlarmReg
EP2_PMM2_AlarmPhase3_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C01_16_60to80
EP2_PMM2_AlarmPhase3_C01_16_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C01_16_over80
EP2_PMM2_AlarmPhase3_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C17_32_60to80
EP2_PMM2_AlarmPhase3_C17_32_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C17_32_over80
EP2_PMM2_AlarmPhase3_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C33_42_60to80
EP2_PMM2_AlarmPhase3_C33_42_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C33_42_over80
EP2_PMM2_AlarmPhase3_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].GlobalAlarmReg
EP2_PMM2_Alarms | INT | IOD_EP2 | EP2:.PMM[2].Alarms
EP2_PMM2_AverageCurrent_A | REAL | IOD_EP2 | EP2:.PMM[2].AverageCurrent_A
EP2_PMM2_AveragePhaseToNeutral_V | REAL | IOD_EP2 | EP2:.PMM[2].AveragePhaseToNeutral_V
EP2_PMM2_AveragePhaseToPhase_V | REAL | IOD_EP2 | EP2:.PMM[2].AveragePhaseToPhase_V
EP2_PMM2_CurrentInPhaseA_A | REAL | IOD_EP2 | EP2:.PMM[2].CurrentInPhaseA_A
EP2_PMM2_CurrentInPhaseB_A | REAL | IOD_EP2 | EP2:.PMM[2].CurrentInPhaseB_A
EP2_PMM2_CurrentInPhaseC_A | REAL | IOD_EP2 | EP2:.PMM[2].CurrentInPhaseC_A
EP2_PMM2_EnergyConsumed_kWh | REAL | IOD_EP2 | EP2:.PMM[2].EnergyConsumed_kWh
EP2_PMM2_Frequency_Hz | REAL | IOD_EP2 | EP2:.PMM[2].Frequency_Hz
EP2_PMM2_Napaka | DIGITAL | IOD_EP2 | EP2:.PMM[2].Napaka
EP2_PMM2_NeutralCurrent_A | REAL | IOD_EP2 | EP2:.PMM[2].NeutralCurrent_A
EP2_PMM2_Phase1_Current10 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[10]
EP2_PMM2_Phase1_Current11 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[11]
EP2_PMM2_Phase1_Current12 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[12]
EP2_PMM2_Phase1_Current13 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[13]
EP2_PMM2_Phase1_Current14 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[14]
EP2_PMM2_Phase1_Current15 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[15]
EP2_PMM2_Phase1_Current16 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[16]
EP2_PMM2_Phase1_Current17 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[17]
EP2_PMM2_Phase1_Current18 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[18]
EP2_PMM2_Phase1_Current19 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[19]
EP2_PMM2_Phase1_Current1 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[1]
EP2_PMM2_Phase1_Current20 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[20]
EP2_PMM2_Phase1_Current21 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[21]
EP2_PMM2_Phase1_Current22 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[22]
EP2_PMM2_Phase1_Current23 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[23]
EP2_PMM2_Phase1_Current24 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[24]
EP2_PMM2_Phase1_Current25 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[25]
EP2_PMM2_Phase1_Current26 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[26]
EP2_PMM2_Phase1_Current27 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[27]
EP2_PMM2_Phase1_Current28 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[28]
EP2_PMM2_Phase1_Current29 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[29]
EP2_PMM2_Phase1_Current2 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[2]
EP2_PMM2_Phase1_Current30 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[30]
EP2_PMM2_Phase1_Current31 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[31]
EP2_PMM2_Phase1_Current32 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[32]
EP2_PMM2_Phase1_Current33 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[33]
EP2_PMM2_Phase1_Current34 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[34]
EP2_PMM2_Phase1_Current35 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[35]
EP2_PMM2_Phase1_Current36 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[36]
EP2_PMM2_Phase1_Current37 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[37]
EP2_PMM2_Phase1_Current38 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[38]
EP2_PMM2_Phase1_Current39 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[39]
EP2_PMM2_Phase1_Current3 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[3]
EP2_PMM2_Phase1_Current40 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[40]
EP2_PMM2_Phase1_Current41 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[41]
EP2_PMM2_Phase1_Current42 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[42]
EP2_PMM2_Phase1_Current4 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[4]
EP2_PMM2_Phase1_Current5 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[5]
EP2_PMM2_Phase1_Current6 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[6]
EP2_PMM2_Phase1_Current7 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[7]
EP2_PMM2_Phase1_Current8 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[8]
EP2_PMM2_Phase1_Current9 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[9]
EP2_PMM2_Phase2_Current10 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[10]
EP2_PMM2_Phase2_Current11 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[11]
EP2_PMM2_Phase2_Current12 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[12]
EP2_PMM2_Phase2_Current13 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[13]
EP2_PMM2_Phase2_Current14 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[14]
EP2_PMM2_Phase2_Current15 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[15]
EP2_PMM2_Phase2_Current16 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[16]
EP2_PMM2_Phase2_Current17 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[17]
EP2_PMM2_Phase2_Current18 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[18]
EP2_PMM2_Phase2_Current19 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[19]
EP2_PMM2_Phase2_Current1 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[1]
EP2_PMM2_Phase2_Current20 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[20]
EP2_PMM2_Phase2_Current21 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[21]
EP2_PMM2_Phase2_Current22 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[22]
EP2_PMM2_Phase2_Current23 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[23]
EP2_PMM2_Phase2_Current24 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[24]
EP2_PMM2_Phase2_Current25 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[25]
EP2_PMM2_Phase2_Current26 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[26]
EP2_PMM2_Phase2_Current27 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[27]
EP2_PMM2_Phase2_Current28 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[28]
EP2_PMM2_Phase2_Current29 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[29]
EP2_PMM2_Phase2_Current2 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[2]
EP2_PMM2_Phase2_Current30 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[30]
EP2_PMM2_Phase2_Current31 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[31]
EP2_PMM2_Phase2_Current32 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[32]
EP2_PMM2_Phase2_Current33 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[33]
EP2_PMM2_Phase2_Current34 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[34]
EP2_PMM2_Phase2_Current35 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[35]
EP2_PMM2_Phase2_Current36 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[36]
EP2_PMM2_Phase2_Current37 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[37]
EP2_PMM2_Phase2_Current38 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[38]
EP2_PMM2_Phase2_Current39 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[39]
EP2_PMM2_Phase2_Current3 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[3]
EP2_PMM2_Phase2_Current40 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[40]
EP2_PMM2_Phase2_Current41 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[41]
EP2_PMM2_Phase2_Current42 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[42]
EP2_PMM2_Phase2_Current4 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[4]
EP2_PMM2_Phase2_Current5 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[5]
EP2_PMM2_Phase2_Current6 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[6]
EP2_PMM2_Phase2_Current7 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[7]
EP2_PMM2_Phase2_Current8 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[8]
EP2_PMM2_Phase2_Current9 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[9]
EP2_PMM2_Phase3_Current10 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[10]
EP2_PMM2_Phase3_Current11 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[11]
EP2_PMM2_Phase3_Current12 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[12]
EP2_PMM2_Phase3_Current13 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[13]
EP2_PMM2_Phase3_Current14 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[14]
EP2_PMM2_Phase3_Current15 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[15]
EP2_PMM2_Phase3_Current16 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[16]
EP2_PMM2_Phase3_Current17 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[17]
EP2_PMM2_Phase3_Current18 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[18]
EP2_PMM2_Phase3_Current19 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[19]
EP2_PMM2_Phase3_Current1 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[1]
EP2_PMM2_Phase3_Current20 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[20]
EP2_PMM2_Phase3_Current21 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[21]
EP2_PMM2_Phase3_Current22 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[22]
EP2_PMM2_Phase3_Current23 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[23]
EP2_PMM2_Phase3_Current24 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[24]
EP2_PMM2_Phase3_Current25 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[25]
EP2_PMM2_Phase3_Current26 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[26]
EP2_PMM2_Phase3_Current27 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[27]
EP2_PMM2_Phase3_Current28 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[28]
EP2_PMM2_Phase3_Current29 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[29]
EP2_PMM2_Phase3_Current2 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[2]
EP2_PMM2_Phase3_Current30 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[30]
EP2_PMM2_Phase3_Current31 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[31]
EP2_PMM2_Phase3_Current32 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[32]
EP2_PMM2_Phase3_Current33 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[33]
EP2_PMM2_Phase3_Current34 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[34]
EP2_PMM2_Phase3_Current35 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[35]
EP2_PMM2_Phase3_Current36 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[36]
EP2_PMM2_Phase3_Current37 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[37]
EP2_PMM2_Phase3_Current38 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[38]
EP2_PMM2_Phase3_Current39 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[39]
EP2_PMM2_Phase3_Current3 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[3]
EP2_PMM2_Phase3_Current40 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[40]
EP2_PMM2_Phase3_Current41 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[41]
EP2_PMM2_Phase3_Current42 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[42]
EP2_PMM2_Phase3_Current4 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[4]
EP2_PMM2_Phase3_Current5 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[5]
EP2_PMM2_Phase3_Current6 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[6]
EP2_PMM2_Phase3_Current7 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[7]
EP2_PMM2_Phase3_Current8 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[8]
EP2_PMM2_Phase3_Current9 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[9]
EP2_PMM2_PowerFactorPhaseA | REAL | IOD_EP2 | EP2:.PMM[2].PowerFactorPhaseA
EP2_PMM2_PowerFactorPhaseB | REAL | IOD_EP2 | EP2:.PMM[2].PowerFactorPhaseB
EP2_PMM2_PowerFactorPhaseC | REAL | IOD_EP2 | EP2:.PMM[2].PowerFactorPhaseC
EP2_PMM2_TotalActivePower_kW | REAL | IOD_EP2 | EP2:.PMM[2].TotalActivePower_kW
EP2_PMM2_TotalAparentPower_kVA | REAL | IOD_EP2 | EP2:.PMM[2].TotalAparentPower_kVA
EP2_PMM2_TotalPowerFactor | REAL | IOD_EP2 | EP2:.PMM[2].TotalPowerFactor
EP2_PMM2_TotalReactivePower_kVAR | REAL | IOD_EP2 | EP2:.PMM[2].TotalReactivePower_kVAR
EP2_PMM2_VoltageBetweenPhaseAB_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseAB_V
EP2_PMM2_VoltageBetweenPhaseAN_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseAN_V
EP2_PMM2_VoltageBetweenPhaseBC_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseBC_V
EP2_PMM2_VoltageBetweenPhaseBN_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseBN_V
EP2_PMM2_VoltageBetweenPhaseCA_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseCA_V
EP2_PMM2_VoltageBetweenPhaseCN_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseCN_V
EP2_PMM3_ActivePowerPhaseA_kW | REAL | IOD_EP2 | EP2:.PMM[3].ActivePowerPhaseA_kW
EP2_PMM3_ActivePowerPhaseB_kW | REAL | IOD_EP2 | EP2:.PMM[3].ActivePowerPhaseB_kW
EP2_PMM3_ActivePowerPhaseC_kW | REAL | IOD_EP2 | EP2:.PMM[3].ActivePowerPhaseC_kW
EP2_PMM3_AlarmPhase1_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C01_16_60to80
EP2_PMM3_AlarmPhase1_C01_16_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C01_16_over80
EP2_PMM3_AlarmPhase1_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C17_32_60to80
EP2_PMM3_AlarmPhase1_C17_32_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C17_32_over80
EP2_PMM3_AlarmPhase1_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C33_42_60to80
EP2_PMM3_AlarmPhase1_C33_42_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C33_42_over80
EP2_PMM3_AlarmPhase1_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].GlobalAlarmReg
EP2_PMM3_AlarmPhase2_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C01_16_60to80
EP2_PMM3_AlarmPhase2_C01_16_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C01_16_over80
EP2_PMM3_AlarmPhase2_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C17_32_60to80
EP2_PMM3_AlarmPhase2_C17_32_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C17_32_over80
EP2_PMM3_AlarmPhase2_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C33_42_60to80
EP2_PMM3_AlarmPhase2_C33_42_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C33_42_over80
EP2_PMM3_AlarmPhase2_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].GlobalAlarmReg
EP2_PMM3_AlarmPhase3_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C01_16_60to80
EP2_PMM3_AlarmPhase3_C01_16_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C01_16_over80
EP2_PMM3_AlarmPhase3_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C17_32_60to80
EP2_PMM3_AlarmPhase3_C17_32_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C17_32_over80
EP2_PMM3_AlarmPhase3_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C33_42_60to80
EP2_PMM3_AlarmPhase3_C33_42_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C33_42_over80
EP2_PMM3_AlarmPhase3_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].GlobalAlarmReg
EP2_PMM3_Alarms | INT | IOD_EP2 | EP2:.PMM[3].Alarms
EP2_PMM3_AverageCurrent_A | REAL | IOD_EP2 | EP2:.PMM[3].AverageCurrent_A
EP2_PMM3_AveragePhaseToNeutral_V | REAL | IOD_EP2 | EP2:.PMM[3].AveragePhaseToNeutral_V
EP2_PMM3_AveragePhaseToPhase_V | REAL | IOD_EP2 | EP2:.PMM[3].AveragePhaseToPhase_V
EP2_PMM3_CurrentInPhaseA_A | REAL | IOD_EP2 | EP2:.PMM[3].CurrentInPhaseA_A
EP2_PMM3_CurrentInPhaseB_A | REAL | IOD_EP2 | EP2:.PMM[3].CurrentInPhaseB_A
EP2_PMM3_CurrentInPhaseC_A | REAL | IOD_EP2 | EP2:.PMM[3].CurrentInPhaseC_A
EP2_PMM3_EnergyConsumed_kWh | REAL | IOD_EP2 | EP2:.PMM[3].EnergyConsumed_kWh
EP2_PMM3_Frequency_Hz | REAL | IOD_EP2 | EP2:.PMM[3].Frequency_Hz
EP2_PMM3_Napaka | DIGITAL | IOD_EP2 | EP2:.PMM[3].Napaka
EP2_PMM3_NeutralCurrent_A | REAL | IOD_EP2 | EP2:.PMM[3].NeutralCurrent_A
EP2_PMM3_Phase1_Current10 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[10]
EP2_PMM3_Phase1_Current11 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[11]
EP2_PMM3_Phase1_Current12 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[12]
EP2_PMM3_Phase1_Current13 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[13]
EP2_PMM3_Phase1_Current14 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[14]
EP2_PMM3_Phase1_Current15 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[15]
EP2_PMM3_Phase1_Current16 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[16]
EP2_PMM3_Phase1_Current17 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[17]
EP2_PMM3_Phase1_Current18 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[18]
EP2_PMM3_Phase1_Current19 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[19]
EP2_PMM3_Phase1_Current1 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[1]
EP2_PMM3_Phase1_Current20 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[20]
EP2_PMM3_Phase1_Current21 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[21]
EP2_PMM3_Phase1_Current22 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[22]
EP2_PMM3_Phase1_Current23 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[23]
EP2_PMM3_Phase1_Current24 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[24]
EP2_PMM3_Phase1_Current25 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[25]
EP2_PMM3_Phase1_Current26 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[26]
EP2_PMM3_Phase1_Current27 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[27]
EP2_PMM3_Phase1_Current28 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[28]
EP2_PMM3_Phase1_Current29 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[29]
EP2_PMM3_Phase1_Current2 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[2]
EP2_PMM3_Phase1_Current30 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[30]
EP2_PMM3_Phase1_Current31 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[31]
EP2_PMM3_Phase1_Current32 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[32]
EP2_PMM3_Phase1_Current33 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[33]
EP2_PMM3_Phase1_Current34 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[34]
EP2_PMM3_Phase1_Current35 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[35]
EP2_PMM3_Phase1_Current36 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[36]
EP2_PMM3_Phase1_Current37 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[37]
EP2_PMM3_Phase1_Current38 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[38]
EP2_PMM3_Phase1_Current39 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[39]
EP2_PMM3_Phase1_Current3 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[3]
EP2_PMM3_Phase1_Current40 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[40]
EP2_PMM3_Phase1_Current41 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[41]
EP2_PMM3_Phase1_Current42 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[42]
EP2_PMM3_Phase1_Current4 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[4]
EP2_PMM3_Phase1_Current5 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[5]
EP2_PMM3_Phase1_Current6 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[6]
EP2_PMM3_Phase1_Current7 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[7]
EP2_PMM3_Phase1_Current8 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[8]
EP2_PMM3_Phase1_Current9 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[9]
EP2_PMM3_Phase2_Current10 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[10]
EP2_PMM3_Phase2_Current11 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[11]
EP2_PMM3_Phase2_Current12 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[12]
EP2_PMM3_Phase2_Current13 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[13]
EP2_PMM3_Phase2_Current14 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[14]
EP2_PMM3_Phase2_Current15 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[15]
EP2_PMM3_Phase2_Current16 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[16]
EP2_PMM3_Phase2_Current17 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[17]
EP2_PMM3_Phase2_Current18 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[18]
EP2_PMM3_Phase2_Current19 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[19]
EP2_PMM3_Phase2_Current1 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[1]
EP2_PMM3_Phase2_Current20 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[20]
EP2_PMM3_Phase2_Current21 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[21]
EP2_PMM3_Phase2_Current22 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[22]
EP2_PMM3_Phase2_Current23 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[23]
EP2_PMM3_Phase2_Current24 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[24]
EP2_PMM3_Phase2_Current25 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[25]
EP2_PMM3_Phase2_Current26 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[26]
EP2_PMM3_Phase2_Current27 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[27]
EP2_PMM3_Phase2_Current28 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[28]
EP2_PMM3_Phase2_Current29 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[29]
EP2_PMM3_Phase2_Current2 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[2]
EP2_PMM3_Phase2_Current30 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[30]
EP2_PMM3_Phase2_Current31 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[31]
EP2_PMM3_Phase2_Current32 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[32]
EP2_PMM3_Phase2_Current33 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[33]
EP2_PMM3_Phase2_Current34 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[34]
EP2_PMM3_Phase2_Current35 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[35]
EP2_PMM3_Phase2_Current36 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[36]
EP2_PMM3_Phase2_Current37 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[37]
EP2_PMM3_Phase2_Current38 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[38]
EP2_PMM3_Phase2_Current39 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[39]
EP2_PMM3_Phase2_Current3 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[3]
EP2_PMM3_Phase2_Current40 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[40]
EP2_PMM3_Phase2_Current41 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[41]
EP2_PMM3_Phase2_Current42 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[42]
EP2_PMM3_Phase2_Current4 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[4]
EP2_PMM3_Phase2_Current5 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[5]
EP2_PMM3_Phase2_Current6 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[6]
EP2_PMM3_Phase2_Current7 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[7]
EP2_PMM3_Phase2_Current8 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[8]
EP2_PMM3_Phase2_Current9 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[9]
EP2_PMM3_Phase3_Current10 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[10]
EP2_PMM3_Phase3_Current11 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[11]
EP2_PMM3_Phase3_Current12 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[12]
EP2_PMM3_Phase3_Current13 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[13]
EP2_PMM3_Phase3_Current14 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[14]
EP2_PMM3_Phase3_Current15 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[15]
EP2_PMM3_Phase3_Current16 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[16]
EP2_PMM3_Phase3_Current17 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[17]
EP2_PMM3_Phase3_Current18 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[18]
EP2_PMM3_Phase3_Current19 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[19]
EP2_PMM3_Phase3_Current1 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[1]
EP2_PMM3_Phase3_Current20 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[20]
EP2_PMM3_Phase3_Current21 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[21]
EP2_PMM3_Phase3_Current22 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[22]
EP2_PMM3_Phase3_Current23 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[23]
EP2_PMM3_Phase3_Current24 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[24]
EP2_PMM3_Phase3_Current25 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[25]
EP2_PMM3_Phase3_Current26 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[26]
EP2_PMM3_Phase3_Current27 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[27]
EP2_PMM3_Phase3_Current28 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[28]
EP2_PMM3_Phase3_Current29 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[29]
EP2_PMM3_Phase3_Current2 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[2]
EP2_PMM3_Phase3_Current30 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[30]
EP2_PMM3_Phase3_Current31 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[31]
EP2_PMM3_Phase3_Current32 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[32]
EP2_PMM3_Phase3_Current33 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[33]
EP2_PMM3_Phase3_Current34 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[34]
EP2_PMM3_Phase3_Current35 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[35]
EP2_PMM3_Phase3_Current36 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[36]
EP2_PMM3_Phase3_Current37 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[37]
EP2_PMM3_Phase3_Current38 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[38]
EP2_PMM3_Phase3_Current39 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[39]
EP2_PMM3_Phase3_Current3 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[3]
EP2_PMM3_Phase3_Current40 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[40]
EP2_PMM3_Phase3_Current41 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[41]
EP2_PMM3_Phase3_Current42 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[42]
EP2_PMM3_Phase3_Current4 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[4]
EP2_PMM3_Phase3_Current5 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[5]
EP2_PMM3_Phase3_Current6 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[6]
EP2_PMM3_Phase3_Current7 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[7]
EP2_PMM3_Phase3_Current8 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[8]
EP2_PMM3_Phase3_Current9 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[9]
EP2_PMM3_PowerFactorPhaseA | REAL | IOD_EP2 | EP2:.PMM[3].PowerFactorPhaseA
EP2_PMM3_PowerFactorPhaseB | REAL | IOD_EP2 | EP2:.PMM[3].PowerFactorPhaseB
EP2_PMM3_PowerFactorPhaseC | REAL | IOD_EP2 | EP2:.PMM[3].PowerFactorPhaseC
EP2_PMM3_TotalActivePower_kW | REAL | IOD_EP2 | EP2:.PMM[3].TotalActivePower_kW
EP2_PMM3_TotalAparentPower_kVA | REAL | IOD_EP2 | EP2:.PMM[3].TotalAparentPower_kVA
EP2_PMM3_TotalPowerFactor | REAL | IOD_EP2 | EP2:.PMM[3].TotalPowerFactor
EP2_PMM3_TotalReactivePower_kVAR | REAL | IOD_EP2 | EP2:.PMM[3].TotalReactivePower_kVAR
EP2_PMM3_VoltageBetweenPhaseAB_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseAB_V
EP2_PMM3_VoltageBetweenPhaseAN_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseAN_V
EP2_PMM3_VoltageBetweenPhaseBC_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseBC_V
EP2_PMM3_VoltageBetweenPhaseBN_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseBN_V
EP2_PMM3_VoltageBetweenPhaseCA_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseCA_V
EP2_PMM3_VoltageBetweenPhaseCN_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseCN_V
EP2_rVersion | REAL | IOD_EP2 | EP2:.rVersion
EP2_SenzorTemp1 | REAL | IOD_EP2 | EP2:.SenzorTemp[1]
EP2_SenzorTemp2 | REAL | IOD_EP2 | EP2:.SenzorTemp[2]
EP2_SenzorVlaga1 | REAL | IOD_EP2 | EP2:.SenzorVlaga[1]
EP2_SenzorVlaga2 | REAL | IOD_EP2 | EP2:.SenzorVlaga[2]
EP2_SetDateTime | DIGITAL | IOD_EP2 | EP2:.SetDateTime
EP2_SetDateTimeDemand | DIGITAL | IOD_EP2 | EP2:.SetDateTimeDemand
EP2_SetDateTimeError | DIGITAL | IOD_EP2 | EP2:.SetDateTimeError
EP2_SetDateTimeFinished | DIGITAL | IOD_EP2 | EP2:.SetDateTimeFinished
EP2_SetRemoteOnOff1 | DIGITAL | IOD_EP2 | EP2:.SetRemoteOnOff[1]
EP2_SetRemoteOnOff2 | DIGITAL | IOD_EP2 | EP2:.SetRemoteOnOff[2]
EP2_SlabaBaterijaPLC_A1 | DIGITAL | IOD_EP2 | EP2:.SlabaBaterijaPLC_A1
EP2_TempMaxPoint | REAL | IOD_EP2 | EP2:.TempMaxPoint
EP2_TempSetPoint | REAL | IOD_EP2 | EP2:.TempSetPoint
EP2_TempTSprevisoka1 | DIGITAL | IOD_EP2 | EP2:.TempTSprevisoka[1]
EP2_TempTSprevisoka2 | DIGITAL | IOD_EP2 | EP2:.TempTSprevisoka[2]
EP2UPS1AlarmAwaitingPower | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmAwaitingPower
EP2UPS1AlarmBypassBad | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmBypassBad
EP2UPS1AlarmChargerFailed | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmChargerFailed
EP2UPS1AlarmCommunicationsLost | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmCommunicationsLost
EP2UPS1AlarmDepletedBattery | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmDepletedBattery
EP2UPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmDiagnosticTestFailed
EP2UPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmIzhodOffKotZahtevano
EP2UPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmIzhodPreobremenjen
EP2UPS1AlarmLowBattery | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmLowBattery
EP2UPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmNapakaNaVarovalki
EP2UPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmNapakaNaVentilatorju
EP2UPS1AlarmOnBattery | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmOnBattery
EP2UPS1AlarmOnBypass | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmOnBypass
EP2UPS1AlarmInverterError | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmInverterError
EP2UPS1AlarmShutdownImminent | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmShutdownImminent
EP2UPS1AlarmShutdownPending | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmShutdownPending
EP2UPS1AlarmSlabaBaterija | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmSlabaBaterija
EP2UPS1AlarmSplosnaNapaka | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmSplosnaNapaka
EP2UPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmStanjeIzhodaIzvenToleranc
EP2UPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmStanjeVhodaIzvenToleranc
EP2UPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmTemperaturaIzvenToleranc
EP2UPS1AlarmTestInProgres | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmTestInProgres
EP2UPS1AlarmUPSIzhodOff | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmUPSIzhodOff
EP2UPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmUPSOffKotZahtevano
EP2UPS1AlarmUPSSystemOff | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmUPSSystemOff
EP2UPS1EstimatedChargeRemaining | REAL | IOD_EP2 | EP2:.UPS[1].EstimatedChargeRemaining
EP2UPS1EstimatedMinutesRemaining | REAL | IOD_EP2 | EP2:.UPS[1].EstimatedMinutesRemaining
EP2UPS1InverterStatus | INT | IOD_EP2 | EP2:.UPS[1].InverterStatus
EP2UPS1IzhodMocL1 | REAL | IOD_EP2 | EP2:.UPS[1].IzhodMocL1
EP2UPS1IzhodMocL2 | REAL | IOD_EP2 | EP2:.UPS[1].IzhodMocL2
EP2UPS1IzhodMocL3 | REAL | IOD_EP2 | EP2:.UPS[1].IzhodMocL3
EP2UPS1Napaka | DIGITAL | IOD_EP2 | EP2:.UPS[1].Napaka
EP2UPS1NapetostBaterije | REAL | IOD_EP2 | EP2:.UPS[1].NapetostBaterije
EP2UPS1OutputStatus | INT | IOD_EP2 | EP2:.UPS[1].OutputStatus
EP2UPS1StatusBaterije | INT | IOD_EP2 | EP2:.UPS[1].StatusBaterije
EP2UPS1StatusEcomodeAktiven | DIGITAL | IOD_EP2 | EP2:.UPS[1].StatusEcomodeAktiven
EP2UPS1StatusInverterIsOn | DIGITAL | IOD_EP2 | EP2:.UPS[1].StatusInverterIsOn
EP2UPS1StatusStopOperation | DIGITAL | IOD_EP2 | EP2:.UPS[1].StatusStopOperation
EP2UPS1SteviloIzpadovVhodneLinije | INT | IOD_EP2 | EP2:.UPS[1].SteviloIzpadovVhodneLinije
EP2UPS1TemperaturaBaterije | REAL | IOD_EP2 | EP2:.UPS[1].TemperaturaBaterije
EP2UPS1UnitStatus | INT | IOD_EP2 | EP2:.UPS[1].UnitStatus
EP2UPS1VhodFrekvencaL1 | REAL | IOD_EP2 | EP2:.UPS[1].VhodFrekvencaL1
EP2UPS1VhodFrekvencaL2 | REAL | IOD_EP2 | EP2:.UPS[1].VhodFrekvencaL2
EP2UPS1VhodFrekvencaL3 | REAL | IOD_EP2 | EP2:.UPS[1].VhodFrekvencaL3
EP2UPS1VhodNapetostL1 | REAL | IOD_EP2 | EP2:.UPS[1].VhodNapetostL1
EP2UPS1VhodNapetostL2 | REAL | IOD_EP2 | EP2:.UPS[1].VhodNapetostL2
EP2UPS1VhodNapetostL3 | REAL | IOD_EP2 | EP2:.UPS[1].VhodNapetostL3
EP2UPS2AlarmAwaitingPower | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmAwaitingPower
EP2UPS2AlarmBypassBad | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmBypassBad
EP2UPS2AlarmChargerFailed | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmChargerFailed
EP2UPS2AlarmCommunicationsLost | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmCommunicationsLost
EP2UPS2AlarmDepletedBattery | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmDepletedBattery
EP2UPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmDiagnosticTestFailed
EP2UPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmIzhodOffKotZahtevano
EP2UPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmIzhodPreobremenjen
EP2UPS2AlarmLowBattery | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmLowBattery
EP2UPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmNapakaNaVarovalki
EP2UPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmNapakaNaVentilatorju
EP2UPS2AlarmOnBattery | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmOnBattery
EP2UPS2AlarmOnBypass | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmOnBypass
EP2UPS2AlarmInverterError | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmInverterError
EP2UPS2AlarmShutdownImminent | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmShutdownImminent
EP2UPS2AlarmShutdownPending | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmShutdownPending
EP2UPS2AlarmSlabaBaterija | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmSlabaBaterija
EP2UPS2AlarmSplosnaNapaka | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmSplosnaNapaka
EP2UPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmStanjeIzhodaIzvenToleranc
EP2UPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmStanjeVhodaIzvenToleranc
EP2UPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmTemperaturaIzvenToleranc
EP2UPS2AlarmTestInProgres | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmTestInProgres
EP2UPS2AlarmUPSIzhodOff | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmUPSIzhodOff
EP2UPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmUPSOffKotZahtevano
EP2UPS2AlarmUPSSystemOff | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmUPSSystemOff
EP2UPS2EstimatedChargeRemaining | REAL | IOD_EP2 | EP2:.UPS[2].EstimatedChargeRemaining
EP2UPS2EstimatedMinutesRemaining | REAL | IOD_EP2 | EP2:.UPS[2].EstimatedMinutesRemaining
EP2UPS2InverterStatus | INT | IOD_EP2 | EP2:.UPS[2].InverterStatus
EP2UPS2IzhodMocL1 | REAL | IOD_EP2 | EP2:.UPS[2].IzhodMocL1
EP2UPS2IzhodMocL2 | REAL | IOD_EP2 | EP2:.UPS[2].IzhodMocL2
EP2UPS2IzhodMocL3 | REAL | IOD_EP2 | EP2:.UPS[2].IzhodMocL3
EP2UPS2Napaka | DIGITAL | IOD_EP2 | EP2:.UPS[2].Napaka
EP2UPS2NapetostBaterije | REAL | IOD_EP2 | EP2:.UPS[2].NapetostBaterije
EP2UPS2OutputStatus | INT | IOD_EP2 | EP2:.UPS[2].OutputStatus
EP2UPS2StatusBaterije | INT | IOD_EP2 | EP2:.UPS[2].StatusBaterije
EP2UPS2StatusEcomodeAktiven | DIGITAL | IOD_EP2 | EP2:.UPS[2].StatusEcomodeAktiven
EP2UPS2StatusInverterIsOn | DIGITAL | IOD_EP2 | EP2:.UPS[2].StatusInverterIsOn
EP2UPS2StatusStopOperation | DIGITAL | IOD_EP2 | EP2:.UPS[2].StatusStopOperation
EP2UPS2SteviloIzpadovVhodneLinije | INT | IOD_EP2 | EP2:.UPS[2].SteviloIzpadovVhodneLinije
EP2UPS2TemperaturaBaterije | REAL | IOD_EP2 | EP2:.UPS[2].TemperaturaBaterije
EP2UPS2UnitStatus | INT | IOD_EP2 | EP2:.UPS[2].UnitStatus
EP2UPS2VhodFrekvencaL1 | REAL | IOD_EP2 | EP2:.UPS[2].VhodFrekvencaL1
EP2UPS2VhodFrekvencaL2 | REAL | IOD_EP2 | EP2:.UPS[2].VhodFrekvencaL2
EP2UPS2VhodFrekvencaL3 | REAL | IOD_EP2 | EP2:.UPS[2].VhodFrekvencaL3
EP2UPS2VhodNapetostL1 | REAL | IOD_EP2 | EP2:.UPS[2].VhodNapetostL1
EP2UPS2VhodNapetostL2 | REAL | IOD_EP2 | EP2:.UPS[2].VhodNapetostL2
EP2UPS2VhodNapetostL3 | REAL | IOD_EP2 | EP2:.UPS[2].VhodNapetostL3
EP2_UserCurrentLevel | INT | IOD_EP2 | EP2:.UserCurrentLevel | BYTE
EP2_UserCurrentName | STRING | IOD_EP2 | EP2:.UserCurrentName
EP2_UserLoggedIn | DIGITAL | IOD_EP2 | EP2:.UserLoggedIn
EP2_XVH_AlarmOn | DIGITAL | IOD_EP2 | EP2:.XVH_AlarmOn
EP2AlarmGenRest | DIGITAL | IOD_EP2 | EP2:.AlarmGenRest
EP2DI_UpsA_BypassON | DIGITAL | IOD_EP2 | EP2:.DI_UpsA_BypassON
EP2DI_UpsA_ERR | DIGITAL | IOD_EP2 | EP2:.DI_UpsA_ERR
EP2DI_UpsB_BypassON | DIGITAL | IOD_EP2 | EP2:.DI_UpsB_BypassON
EP2DI_UpsB_ERR | DIGITAL | IOD_EP2 | EP2:.DI_UpsB_ERR
EP2DIN_Klima5_ERR | DIGITAL | IOD_EP2 | EP2:.DIN_Klima5_ERR
EP2DIN_Klima6_ERR | DIGITAL | IOD_EP2 | EP2:.DIN_Klima6_ERR
EP2DIN_KlimaSplit1_ERR | DIGITAL | IOD_EP2 | EP2:.DIN_KlimaSplit1_ERR
EP2DIN_Q10_OdcKlima6_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q10_OdcKlima6_IZP
EP2DIN_Q25_OdcUpsA_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q25_OdcUpsA_IZP
EP2DIN_Q26_OdcByA_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q26_OdcByA_IZP
EP2DIN_Q27_OdcByUpsA_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q27_OdcByUpsA_IZP
EP2DIN_Q28_OdcUpsB_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q28_OdcUpsB_IZP
EP2DIN_Q29_OdcByB_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q29_OdcByB_IZP
EP2DIN_Q2_Rezerva_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q2_Rezerva_IZP
EP2DIN_Q30_OdcByUpsB_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q30_OdcByUpsB_IZP
EP2DIN_Q5_OdcKlima1_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q5_OdcKlima1_IZP
EP2DIN_Q6_OdcKlima2_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q6_OdcKlima2_IZP
EP2DIN_Q7_OdcKlima3_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q7_OdcKlima3_IZP
EP2DIN_Q8_OdcKlima4_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q8_OdcKlima4_IZP
EP2DIN_Q9_OdcKlima5_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q9_OdcKlima5_IZP
EP2ErrorComCirc1Code10 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[10] | BYTE
EP2ErrorComCirc1Code11 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[11] | BYTE
EP2ErrorComCirc1Code12 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[12] | BYTE
EP2ErrorComCirc1Code13 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[13] | BYTE
EP2ErrorComCirc1Code14 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[14] | BYTE
EP2ErrorComCirc1Code15 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[15] | BYTE
EP2ErrorComCirc1Code1 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[1] | BYTE
EP2ErrorComCirc1Code2 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[2] | BYTE
EP2ErrorComCirc1Code3 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[3] | BYTE
EP2ErrorComCirc1Code4 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[4] | BYTE
EP2ErrorComCirc1Code5 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[5] | BYTE
EP2ErrorComCirc1Code6 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[6] | BYTE
EP2ErrorComCirc1Code7 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[7] | BYTE
EP2ErrorComCirc1Code8 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[8] | BYTE
EP2ErrorComCirc1Code9 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[9] | BYTE
EP2ErrorComCirc1Error | DIGITAL | IOD_EP2 | EP2:.ErrorComCirc[1].Error
EP2ErrorComCirc1Status | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Status
EP2ErrorComCirc2Code10 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[10] | BYTE
EP2ErrorComCirc2Code11 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[11] | BYTE
EP2ErrorComCirc2Code12 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[12] | BYTE
EP2ErrorComCirc2Code13 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[13] | BYTE
EP2ErrorComCirc2Code14 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[14] | BYTE
EP2ErrorComCirc2Code15 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[15] | BYTE
EP2ErrorComCirc2Code1 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[1] | BYTE
EP2ErrorComCirc2Code2 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[2] | BYTE
EP2ErrorComCirc2Code3 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[3] | BYTE
EP2ErrorComCirc2Code4 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[4] | BYTE
EP2ErrorComCirc2Code5 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[5] | BYTE
EP2ErrorComCirc2Code6 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[6] | BYTE
EP2ErrorComCirc2Code7 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[7] | BYTE
EP2ErrorComCirc2Code8 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[8] | BYTE
EP2ErrorComCirc2Code9 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[9] | BYTE
EP2ErrorComCirc2Error | DIGITAL | IOD_EP2 | EP2:.ErrorComCirc[2].Error
EP2ErrorComCirc2Status | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Status
EP2ErrorComCirc3Code10 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[10] | BYTE
EP2ErrorComCirc3Code11 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[11] | BYTE
EP2ErrorComCirc3Code12 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[12] | BYTE
EP2ErrorComCirc3Code13 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[13] | BYTE
EP2ErrorComCirc3Code14 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[14] | BYTE
EP2ErrorComCirc3Code15 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[15] | BYTE
EP2ErrorComCirc3Code1 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[1] | BYTE
EP2ErrorComCirc3Code2 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[2] | BYTE
EP2ErrorComCirc3Code3 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[3] | BYTE
EP2ErrorComCirc3Code4 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[4] | BYTE
EP2ErrorComCirc3Code5 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[5] | BYTE
EP2ErrorComCirc3Code6 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[6] | BYTE
EP2ErrorComCirc3Code7 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[7] | BYTE
EP2ErrorComCirc3Code8 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[8] | BYTE
EP2ErrorComCirc3Code9 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[9] | BYTE
EP2ErrorComCirc3Error | DIGITAL | IOD_EP2 | EP2:.ErrorComCirc[3].Error
EP2ErrorComCirc3Status | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Status
EP2ErrorComCirc4Code10 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[10] | BYTE
EP2ErrorComCirc4Code11 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[11] | BYTE
EP2ErrorComCirc4Code12 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[12] | BYTE
EP2ErrorComCirc4Code13 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[13] | BYTE
EP2ErrorComCirc4Code14 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[14] | BYTE
EP2ErrorComCirc4Code15 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[15] | BYTE
EP2ErrorComCirc4Code1 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[1] | BYTE
EP2ErrorComCirc4Code2 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[2] | BYTE
EP2ErrorComCirc4Code3 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[3] | BYTE
EP2ErrorComCirc4Code4 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[4] | BYTE
EP2ErrorComCirc4Code5 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[5] | BYTE
EP2ErrorComCirc4Code6 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[6] | BYTE
EP2ErrorComCirc4Code7 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[7] | BYTE
EP2ErrorComCirc4Code8 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[8] | BYTE
EP2ErrorComCirc4Code9 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[9] | BYTE
EP2ErrorComCirc4Error | DIGITAL | IOD_EP2 | EP2:.ErrorComCirc[4].Error
EP2ErrorComCirc4Status | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Status
EP2ErrorComCirc5Code10 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[10] | BYTE
EP2ErrorComCirc5Code11 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[11] | BYTE
EP2ErrorComCirc5Code12 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[12] | BYTE
EP2ErrorComCirc5Code13 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[13] | BYTE
EP2ErrorComCirc5Code14 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[14] | BYTE
EP2ErrorComCirc5Code15 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[15] | BYTE
EP2ErrorComCirc5Code1 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[1] | BYTE
EP2ErrorComCirc5Code2 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[2] | BYTE
EP2ErrorComCirc5Code3 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[3] | BYTE
EP2ErrorComCirc5Code4 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[4] | BYTE
EP2ErrorComCirc5Code5 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[5] | BYTE
EP2ErrorComCirc5Code6 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[6] | BYTE
EP2ErrorComCirc5Code7 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[7] | BYTE
EP2ErrorComCirc5Code8 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[8] | BYTE
EP2ErrorComCirc5Code9 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[9] | BYTE
EP2ErrorComCirc5Error | DIGITAL | IOD_EP2 | EP2:.ErrorComCirc[5].Error
EP2ErrorComCirc5Status | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Status
EP2ErrorComKlima1Code10 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[10] | BYTE
EP2ErrorComKlima1Code11 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[11] | BYTE
EP2ErrorComKlima1Code12 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[12] | BYTE
EP2ErrorComKlima1Code13 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[13] | BYTE
EP2ErrorComKlima1Code14 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[14] | BYTE
EP2ErrorComKlima1Code15 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[15] | BYTE
EP2ErrorComKlima1Code1 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[1] | BYTE
EP2ErrorComKlima1Code2 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[2] | BYTE
EP2ErrorComKlima1Code3 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[3] | BYTE
EP2ErrorComKlima1Code4 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[4] | BYTE
EP2ErrorComKlima1Code5 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[5] | BYTE
EP2ErrorComKlima1Code6 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[6] | BYTE
EP2ErrorComKlima1Code7 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[7] | BYTE
EP2ErrorComKlima1Code8 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[8] | BYTE
EP2ErrorComKlima1Code9 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[9] | BYTE
EP2ErrorComKlima1Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[1].Error
EP2ErrorComKlima1Status | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Status
EP2ErrorComKlima2Code10 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[10] | BYTE
EP2ErrorComKlima2Code11 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[11] | BYTE
EP2ErrorComKlima2Code12 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[12] | BYTE
EP2ErrorComKlima2Code13 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[13] | BYTE
EP2ErrorComKlima2Code14 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[14] | BYTE
EP2ErrorComKlima2Code15 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[15] | BYTE
EP2ErrorComKlima2Code1 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[1] | BYTE
EP2ErrorComKlima2Code2 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[2] | BYTE
EP2ErrorComKlima2Code3 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[3] | BYTE
EP2ErrorComKlima2Code4 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[4] | BYTE
EP2ErrorComKlima2Code5 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[5] | BYTE
EP2ErrorComKlima2Code6 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[6] | BYTE
EP2ErrorComKlima2Code7 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[7] | BYTE
EP2ErrorComKlima2Code8 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[8] | BYTE
EP2ErrorComKlima2Code9 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[9] | BYTE
EP2ErrorComKlima2Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[2].Error
EP2ErrorComKlima2Status | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Status
EP2ErrorComKlima3Code10 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[10] | BYTE
EP2ErrorComKlima3Code11 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[11] | BYTE
EP2ErrorComKlima3Code12 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[12] | BYTE
EP2ErrorComKlima3Code13 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[13] | BYTE
EP2ErrorComKlima3Code14 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[14] | BYTE
EP2ErrorComKlima3Code15 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[15] | BYTE
EP2ErrorComKlima3Code1 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[1] | BYTE
EP2ErrorComKlima3Code2 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[2] | BYTE
EP2ErrorComKlima3Code3 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[3] | BYTE
EP2ErrorComKlima3Code4 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[4] | BYTE
EP2ErrorComKlima3Code5 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[5] | BYTE
EP2ErrorComKlima3Code6 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[6] | BYTE
EP2ErrorComKlima3Code7 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[7] | BYTE
EP2ErrorComKlima3Code8 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[8] | BYTE
EP2ErrorComKlima3Code9 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[9] | BYTE
EP2ErrorComKlima3Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[3].Error
EP2ErrorComKlima3Status | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Status
EP2ErrorComKlima4Code10 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[10] | BYTE
EP2ErrorComKlima4Code11 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[11] | BYTE
EP2ErrorComKlima4Code12 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[12] | BYTE
EP2ErrorComKlima4Code13 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[13] | BYTE
EP2ErrorComKlima4Code14 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[14] | BYTE
EP2ErrorComKlima4Code15 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[15] | BYTE
EP2ErrorComKlima4Code1 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[1] | BYTE
EP2ErrorComKlima4Code2 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[2] | BYTE
EP2ErrorComKlima4Code3 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[3] | BYTE
EP2ErrorComKlima4Code4 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[4] | BYTE
EP2ErrorComKlima4Code5 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[5] | BYTE
EP2ErrorComKlima4Code6 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[6] | BYTE
EP2ErrorComKlima4Code7 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[7] | BYTE
EP2ErrorComKlima4Code8 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[8] | BYTE
EP2ErrorComKlima4Code9 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[9] | BYTE
EP2ErrorComKlima4Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[4].Error
EP2ErrorComKlima4Status | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Status
EP2ErrorComKlima5Code10 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[10] | BYTE
EP2ErrorComKlima5Code11 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[11] | BYTE
EP2ErrorComKlima5Code12 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[12] | BYTE
EP2ErrorComKlima5Code13 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[13] | BYTE
EP2ErrorComKlima5Code14 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[14] | BYTE
EP2ErrorComKlima5Code15 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[15] | BYTE
EP2ErrorComKlima5Code1 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[1] | BYTE
EP2ErrorComKlima5Code2 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[2] | BYTE
EP2ErrorComKlima5Code3 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[3] | BYTE
EP2ErrorComKlima5Code4 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[4] | BYTE
EP2ErrorComKlima5Code5 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[5] | BYTE
EP2ErrorComKlima5Code6 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[6] | BYTE
EP2ErrorComKlima5Code7 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[7] | BYTE
EP2ErrorComKlima5Code8 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[8] | BYTE
EP2ErrorComKlima5Code9 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[9] | BYTE
EP2ErrorComKlima5Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[5].Error
EP2ErrorComKlima5Status | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Status
EP2ErrorComKlima6Code10 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[10] | BYTE
EP2ErrorComKlima6Code11 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[11] | BYTE
EP2ErrorComKlima6Code12 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[12] | BYTE
EP2ErrorComKlima6Code13 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[13] | BYTE
EP2ErrorComKlima6Code14 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[14] | BYTE
EP2ErrorComKlima6Code15 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[15] | BYTE
EP2ErrorComKlima6Code1 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[1] | BYTE
EP2ErrorComKlima6Code2 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[2] | BYTE
EP2ErrorComKlima6Code3 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[3] | BYTE
EP2ErrorComKlima6Code4 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[4] | BYTE
EP2ErrorComKlima6Code5 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[5] | BYTE
EP2ErrorComKlima6Code6 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[6] | BYTE
EP2ErrorComKlima6Code7 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[7] | BYTE
EP2ErrorComKlima6Code8 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[8] | BYTE
EP2ErrorComKlima6Code9 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[9] | BYTE
EP2ErrorComKlima6Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[6].Error
EP2ErrorComKlima6Status | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Status
EP2ErrorComPMM1Code10 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[10] | BYTE
EP2ErrorComPMM1Code11 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[11] | BYTE
EP2ErrorComPMM1Code12 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[12] | BYTE
EP2ErrorComPMM1Code13 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[13] | BYTE
EP2ErrorComPMM1Code14 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[14] | BYTE
EP2ErrorComPMM1Code15 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[15] | BYTE
EP2ErrorComPMM1Code1 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[1] | BYTE
EP2ErrorComPMM1Code2 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[2] | BYTE
EP2ErrorComPMM1Code3 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[3] | BYTE
EP2ErrorComPMM1Code4 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[4] | BYTE
EP2ErrorComPMM1Code5 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[5] | BYTE
EP2ErrorComPMM1Code6 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[6] | BYTE
EP2ErrorComPMM1Code7 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[7] | BYTE
EP2ErrorComPMM1Code8 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[8] | BYTE
EP2ErrorComPMM1Code9 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[9] | BYTE
EP2ErrorComPMM1Error | DIGITAL | IOD_EP2 | EP2:.ErrorComPMM[1].Error
EP2ErrorComPMM1Status | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Status
EP2ErrorComPMM2Code10 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[10] | BYTE
EP2ErrorComPMM2Code11 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[11] | BYTE
EP2ErrorComPMM2Code12 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[12] | BYTE
EP2ErrorComPMM2Code13 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[13] | BYTE
EP2ErrorComPMM2Code14 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[14] | BYTE
EP2ErrorComPMM2Code15 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[15] | BYTE
EP2ErrorComPMM2Code1 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[1] | BYTE
EP2ErrorComPMM2Code2 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[2] | BYTE
EP2ErrorComPMM2Code3 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[3] | BYTE
EP2ErrorComPMM2Code4 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[4] | BYTE
EP2ErrorComPMM2Code5 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[5] | BYTE
EP2ErrorComPMM2Code6 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[6] | BYTE
EP2ErrorComPMM2Code7 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[7] | BYTE
EP2ErrorComPMM2Code8 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[8] | BYTE
EP2ErrorComPMM2Code9 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[9] | BYTE
EP2ErrorComPMM2Error | DIGITAL | IOD_EP2 | EP2:.ErrorComPMM[2].Error
EP2ErrorComPMM2Status | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Status
EP2ErrorComPMM3Code10 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[10] | BYTE
EP2ErrorComPMM3Code11 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[11] | BYTE
EP2ErrorComPMM3Code12 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[12] | BYTE
EP2ErrorComPMM3Code13 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[13] | BYTE
EP2ErrorComPMM3Code14 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[14] | BYTE
EP2ErrorComPMM3Code15 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[15] | BYTE
EP2ErrorComPMM3Code1 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[1] | BYTE
EP2ErrorComPMM3Code2 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[2] | BYTE
EP2ErrorComPMM3Code3 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[3] | BYTE
EP2ErrorComPMM3Code4 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[4] | BYTE
EP2ErrorComPMM3Code5 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[5] | BYTE
EP2ErrorComPMM3Code6 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[6] | BYTE
EP2ErrorComPMM3Code7 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[7] | BYTE
EP2ErrorComPMM3Code8 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[8] | BYTE
EP2ErrorComPMM3Code9 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[9] | BYTE
EP2ErrorComPMM3Error | DIGITAL | IOD_EP2 | EP2:.ErrorComPMM[3].Error
EP2ErrorComPMM3Status | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Status
EP2ErrorComUPS1Code10 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[10] | BYTE
EP2ErrorComUPS1Code11 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[11] | BYTE
EP2ErrorComUPS1Code12 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[12] | BYTE
EP2ErrorComUPS1Code13 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[13] | BYTE
EP2ErrorComUPS1Code14 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[14] | BYTE
EP2ErrorComUPS1Code15 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[15] | BYTE
EP2ErrorComUPS1Code1 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[1] | BYTE
EP2ErrorComUPS1Code2 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[2] | BYTE
EP2ErrorComUPS1Code3 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[3] | BYTE
EP2ErrorComUPS1Code4 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[4] | BYTE
EP2ErrorComUPS1Code5 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[5] | BYTE
EP2ErrorComUPS1Code6 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[6] | BYTE
EP2ErrorComUPS1Code7 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[7] | BYTE
EP2ErrorComUPS1Code8 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[8] | BYTE
EP2ErrorComUPS1Code9 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[9] | BYTE
EP2ErrorComUPS1Error | DIGITAL | IOD_EP2 | EP2:.ErrorComUPS[1].Error
EP2ErrorComUPS1Status | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Status
EP2ErrorComUPS2Code10 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[10] | BYTE
EP2ErrorComUPS2Code11 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[11] | BYTE
EP2ErrorComUPS2Code12 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[12] | BYTE
EP2ErrorComUPS2Code13 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[13] | BYTE
EP2ErrorComUPS2Code14 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[14] | BYTE
EP2ErrorComUPS2Code15 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[15] | BYTE
EP2ErrorComUPS2Code1 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[1] | BYTE
EP2ErrorComUPS2Code2 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[2] | BYTE
EP2ErrorComUPS2Code3 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[3] | BYTE
EP2ErrorComUPS2Code4 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[4] | BYTE
EP2ErrorComUPS2Code5 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[5] | BYTE
EP2ErrorComUPS2Code6 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[6] | BYTE
EP2ErrorComUPS2Code7 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[7] | BYTE
EP2ErrorComUPS2Code8 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[8] | BYTE
EP2ErrorComUPS2Code9 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[9] | BYTE
EP2ErrorComUPS2Error | DIGITAL | IOD_EP2 | EP2:.ErrorComUPS[2].Error
EP2ErrorComUPS2Status | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Status
EP2KlimaAErrors10 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[10]
EP2KlimaAErrors11 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[11]
EP2KlimaAErrors12 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[12]
EP2KlimaAErrors13 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[13]
EP2KlimaAErrors14 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[14]
EP2KlimaAErrors15 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[15]
EP2KlimaAErrors16 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[16]
EP2KlimaAErrors17 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[17]
EP2KlimaAErrors18 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[18]
EP2KlimaAErrors19 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[19]
EP2KlimaAErrors1 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[1]
EP2KlimaAErrors20 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[20]
EP2KlimaAErrors21 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[21]
EP2KlimaAErrors22 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[22]
EP2KlimaAErrors23 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[23]
EP2KlimaAErrors24 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[24]
EP2KlimaAErrors25 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[25]
EP2KlimaAErrors26 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[26]
EP2KlimaAErrors27 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[27]
EP2KlimaAErrors28 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[28]
EP2KlimaAErrors29 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[29]
EP2KlimaAErrors2 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[2]
EP2KlimaAErrors30 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[30]
EP2KlimaAErrors31 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[31]
EP2KlimaAErrors32 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[32]
EP2KlimaAErrors33 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[33]
EP2KlimaAErrors34 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[34]
EP2KlimaAErrors35 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[35]
EP2KlimaAErrors36 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[36]
EP2KlimaAErrors37 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[37]
EP2KlimaAErrors38 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[38]
EP2KlimaAErrors39 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[39]
EP2KlimaAErrors3 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[3]
EP2KlimaAErrors40 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[40]
EP2KlimaAErrors4 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[4]
EP2KlimaAErrors5 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[5]
EP2KlimaAErrors6 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[6]
EP2KlimaAErrors7 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[7]
EP2KlimaAErrors8 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[8]
EP2KlimaAErrors9 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[9]
EP2KlimaBErrors10 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[10]
EP2KlimaBErrors11 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[11]
EP2KlimaBErrors12 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[12]
EP2KlimaBErrors13 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[13]
EP2KlimaBErrors14 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[14]
EP2KlimaBErrors15 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[15]
EP2KlimaBErrors16 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[16]
EP2KlimaBErrors17 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[17]
EP2KlimaBErrors18 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[18]
EP2KlimaBErrors19 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[19]
EP2KlimaBErrors1 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[1]
EP2KlimaBErrors20 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[20]
EP2KlimaBErrors21 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[21]
EP2KlimaBErrors22 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[22]
EP2KlimaBErrors23 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[23]
EP2KlimaBErrors24 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[24]
EP2KlimaBErrors25 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[25]
EP2KlimaBErrors26 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[26]
EP2KlimaBErrors27 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[27]
EP2KlimaBErrors28 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[28]
EP2KlimaBErrors29 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[29]
EP2KlimaBErrors2 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[2]
EP2KlimaBErrors30 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[30]
EP2KlimaBErrors31 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[31]
EP2KlimaBErrors32 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[32]
EP2KlimaBErrors33 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[33]
EP2KlimaBErrors34 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[34]
EP2KlimaBErrors35 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[35]
EP2KlimaBErrors36 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[36]
EP2KlimaBErrors37 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[37]
EP2KlimaBErrors38 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[38]
EP2KlimaBErrors39 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[39]
EP2KlimaBErrors3 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[3]
EP2KlimaBErrors40 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[40]
EP2KlimaBErrors4 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[4]
EP2KlimaBErrors5 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[5]
EP2KlimaBErrors6 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[6]
EP2KlimaBErrors7 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[7]
EP2KlimaBErrors8 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[8]
EP2KlimaBErrors9 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[9]
EP2KlimaGalAlarmKompresor1 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.AlarmKompresor1
EP2KlimaGalAlarmKompresor2 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.AlarmKompresor2
EP2KlimaGalDeluje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Deluje
EP2KlimaGalEnergySaving | DIGITAL | IOD_EP2 | EP2:.KlimaGal.EnergySaving
EP2KlimaGalFaultyEPROM | DIGITAL | IOD_EP2 | EP2:.KlimaGal.FaultyEPROM
EP2KlimaGalFenThermalCutout | DIGITAL | IOD_EP2 | EP2:.KlimaGal.FenThermalCutout
EP2KlimaGalGeneralAlarm | DIGITAL | IOD_EP2 | EP2:.KlimaGal.GeneralAlarm
EP2KlimaGalGrelecStatus | INT | IOD_EP2 | EP2:.KlimaGal.GrelecStatus | BYTE
EP2KlimaGalIzhodniVentStatus | INT | IOD_EP2 | EP2:.KlimaGal.IzhodniVentStatus | BYTE
EP2KlimaGalKompresor1naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Kompresor1naMejiObrUr
EP2KlimaGalKompresor2naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Kompresor2naMejiObrUr
EP2KlimaGalKompresorStatus | INT | IOD_EP2 | EP2:.KlimaGal.KompresorStatus | BYTE
EP2KlimaGalNapaka | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Napaka
EP2KlimaGalNapakaPriPretokuZraka | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaPriPretokuZraka
EP2KlimaGalNapakaSenzorPovratVode | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaSenzorPovratVode
EP2KlimaGalNapakaSenzorTempIzpiha | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaSenzorTempIzpiha
EP2KlimaGalNapakaSenzorTempProstora | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaSenzorTempProstora
EP2KlimaGalNapakaSenzorVlaznosti | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaSenzorVlaznosti
EP2KlimaGalNapakaSenzorZunanjeTemp | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaSenzorZunanjeTemp
EP2KlimaGalNastMaxTemp | REAL | IOD_EP2 | EP2:.KlimaGal.NastMaxTemp
EP2KlimaGalNastMaxVlaznost | REAL | IOD_EP2 | EP2:.KlimaGal.NastMaxVlaznost
EP2KlimaGalNastMinTemp | REAL | IOD_EP2 | EP2:.KlimaGal.NastMinTemp
EP2KlimaGalNastMinVlaznost | REAL | IOD_EP2 | EP2:.KlimaGal.NastMinVlaznost
EP2KlimaGalNastTempProstora | REAL | IOD_EP2 | EP2:.KlimaGal.NastTempProstora
EP2KlimaGalNastVlaznost | REAL | IOD_EP2 | EP2:.KlimaGal.NastVlaznost
EP2KlimaGalNiTokaVVlazilcu | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NiTokaVVlazilcu
EP2KlimaGalNiVodeVVlazilcu | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NiVodeVVlazilcu
EP2KlimaGalNizekPritiskKompresor1 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NizekPritiskKompresor1
EP2KlimaGalNizekPritiskKompresor2 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NizekPritiskKompresor2
EP2KlimaGalNizkaTempPovratneVode | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NizkaTempPovratneVode
EP2KlimaGalNizkaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NizkaTempVProstoru
EP2KlimaGalNizkaVlaznost | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NizkaVlaznost
EP2KlimaGalObratovalneUre | REAL | IOD_EP2 | EP2:.KlimaGal.ObratovalneUre
EP2KlimaGalOnOffEnablingBySupervisor | DIGITAL | IOD_EP2 | EP2:.KlimaGal.OnOffEnablingBySupervisor
EP2KlimaGalPozarniAlarm | DIGITAL | IOD_EP2 | EP2:.KlimaGal.PozarniAlarm
EP2KlimaGalRazvlazevanje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Razvlazevanje
EP2KlimaGalRemoteOFFtoOutput | DIGITAL | IOD_EP2 | EP2:.KlimaGal.RemoteOFFtoOutput
EP2KlimaGalRemoteOnOff | DIGITAL | IOD_EP2 | EP2:.KlimaGal.RemoteOnOff
EP2KlimaGalRocniIzklop | DIGITAL | IOD_EP2 | EP2:.KlimaGal.RocniIzklop
EP2KlimaGalSenzorjiStatus | DIGITAL | IOD_EP2 | EP2:.KlimaGal.SenzorjiStatus
EP2KlimaGalStoppedByAlarms | DIGITAL | IOD_EP2 | EP2:.KlimaGal.StoppedByAlarms
EP2KlimaGalTemperaturaProstora | REAL | IOD_EP2 | EP2:.KlimaGal.TemperaturaProstora
EP2KlimaGalTempIzpihanegaZraka | REAL | IOD_EP2 | EP2:.KlimaGal.TempIzpihanegaZraka
EP2KlimaGalTempPovratneVode | REAL | IOD_EP2 | EP2:.KlimaGal.TempPovratneVode
EP2KlimaGalThermalCutoutHeater1 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.ThermalCutoutHeater1
EP2KlimaGalThermalCutoutHeater2 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.ThermalCutoutHeater2
EP2KlimaGalUnitOnOff | DIGITAL | IOD_EP2 | EP2:.KlimaGal.UnitOnOff
EP2KlimaGalVentilatorNaMejiObrUr | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VentilatorNaMejiObrUr
EP2KlimaGalVentilGretjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VentilGretjeOdpiranje
EP2KlimaGalVentilGretjeZapiranje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VentilGretjeZapiranje
EP2KlimaGalVentilHlajenjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VentilHlajenjeOdpiranje
EP2KlimaGalVentilHlajenjeZapiranje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VentilHlajenjeZapiranje
EP2KlimaGalVisokaTempPovratneVode | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VisokaTempPovratneVode
EP2KlimaGalVisokaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VisokaTempVProstoru
EP2KlimaGalVisokaVlaznost | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VisokaVlaznost
EP2KlimaGalVisokTokVVlazilcu | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VisokTokVVlazilcu
EP2KlimaGalVlazenje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Vlazenje
EP2KlimaGalVlazilecStatus | INT | IOD_EP2 | EP2:.KlimaGal.VlazilecStatus | BYTE
EP2KlimaGalVlaznostProstora | REAL | IOD_EP2 | EP2:.KlimaGal.VlaznostProstora
EP2KlimaGalZamasenFilter | DIGITAL | IOD_EP2 | EP2:.KlimaGal.ZamasenFilter
EP2KlimaGalZunanjaTemp | REAL | IOD_EP2 | EP2:.KlimaGal.ZunanjaTemp
EP2PMM1OverVoltage | DIGITAL | IOD_EP2 | EP2:.PMM1OverVoltage
EP2PMM2OverVoltage | DIGITAL | IOD_EP2 | EP2:.PMM2OverVoltage
EP2PMM3OverVoltage | DIGITAL | IOD_EP2 | EP2:.PMM3OverVoltage
EP2PMMfaza01 | REAL | IOD_EP2 | EP2:.PMMfaza01
EP2PMMfaza02 | REAL | IOD_EP2 | EP2:.PMMfaza02
EP2PMMfaza03 | REAL | IOD_EP2 | EP2:.PMMfaza03
EP2PMMfaza04 | REAL | IOD_EP2 | EP2:.PMMfaza04
EP2PMMfaza05 | REAL | IOD_EP2 | EP2:.PMMfaza05
EP2PMMfaza06 | REAL | IOD_EP2 | EP2:.PMMfaza06
EP2PMMfaza07 | REAL | IOD_EP2 | EP2:.PMMfaza07
EP2PMMfaza08 | REAL | IOD_EP2 | EP2:.PMMfaza08
EP2PMMfaza09 | REAL | IOD_EP2 | EP2:.PMMfaza09
EP2PMMfaza10 | REAL | IOD_EP2 | EP2:.PMMfaza10
EP2PMMfaza11 | REAL | IOD_EP2 | EP2:.PMMfaza11
EP2PMMfaza12 | REAL | IOD_EP2 | EP2:.PMMfaza12
EP2PMMfaza13 | REAL | IOD_EP2 | EP2:.PMMfaza13
EP2PMMfaza14 | REAL | IOD_EP2 | EP2:.PMMfaza14
EP2PMMfaza15 | REAL | IOD_EP2 | EP2:.PMMfaza15
EP2PMMfaza16 | REAL | IOD_EP2 | EP2:.PMMfaza16
EP2PMMfaza17 | REAL | IOD_EP2 | EP2:.PMMfaza17
EP2PMMfaza18 | REAL | IOD_EP2 | EP2:.PMMfaza18
EP2PMMfaza19 | REAL | IOD_EP2 | EP2:.PMMfaza19
EP2PMMfaza20 | REAL | IOD_EP2 | EP2:.PMMfaza20
EP2PMMfaza21 | REAL | IOD_EP2 | EP2:.PMMfaza21
EP2PMMfaza22 | REAL | IOD_EP2 | EP2:.PMMfaza22
EP2PMMfaza23 | REAL | IOD_EP2 | EP2:.PMMfaza23
EP2PMMfaza24 | REAL | IOD_EP2 | EP2:.PMMfaza24
EP2PMMfaza25 | REAL | IOD_EP2 | EP2:.PMMfaza25
EP2PMMfaza26 | REAL | IOD_EP2 | EP2:.PMMfaza26
EP2PMMfaza27 | REAL | IOD_EP2 | EP2:.PMMfaza27
EP2PMMfaza28 | REAL | IOD_EP2 | EP2:.PMMfaza28
EP2PMMfaza29 | REAL | IOD_EP2 | EP2:.PMMfaza29
EP2PMMfaza30 | REAL | IOD_EP2 | EP2:.PMMfaza30
EP2PMMfaza31 | REAL | IOD_EP2 | EP2:.PMMfaza31
EP2PMMfaza32 | REAL | IOD_EP2 | EP2:.PMMfaza32
EP2PMMfaza33 | REAL | IOD_EP2 | EP2:.PMMfaza33
EP2PMMfaza34 | REAL | IOD_EP2 | EP2:.PMMfaza34
EP2PMMfaza35 | REAL | IOD_EP2 | EP2:.PMMfaza35
EP2PMMfaza36 | REAL | IOD_EP2 | EP2:.PMMfaza36
EP2PMMfaza37 | REAL | IOD_EP2 | EP2:.PMMfaza37
EP2PMMfaza38 | REAL | IOD_EP2 | EP2:.PMMfaza38
EP2PMMfaza39 | REAL | IOD_EP2 | EP2:.PMMfaza39
EP2PMMfaza40 | REAL | IOD_EP2 | EP2:.PMMfaza40
EP2PMMfaza41 | REAL | IOD_EP2 | EP2:.PMMfaza41
EP2PMMfaza42 | REAL | IOD_EP2 | EP2:.PMMfaza42
EP2PMMfaza6010 | REAL | IOD_EP2 | EP2:.PMMfaza60[10]
EP2PMMfaza6011 | REAL | IOD_EP2 | EP2:.PMMfaza60[11]
EP2PMMfaza6012 | REAL | IOD_EP2 | EP2:.PMMfaza60[12]
EP2PMMfaza6013 | REAL | IOD_EP2 | EP2:.PMMfaza60[13]
EP2PMMfaza6014 | REAL | IOD_EP2 | EP2:.PMMfaza60[14]
EP2PMMfaza6015 | REAL | IOD_EP2 | EP2:.PMMfaza60[15]
EP2PMMfaza6016 | REAL | IOD_EP2 | EP2:.PMMfaza60[16]
EP2PMMfaza6017 | REAL | IOD_EP2 | EP2:.PMMfaza60[17]
EP2PMMfaza6018 | REAL | IOD_EP2 | EP2:.PMMfaza60[18]
EP2PMMfaza6019 | REAL | IOD_EP2 | EP2:.PMMfaza60[19]
EP2PMMfaza601 | REAL | IOD_EP2 | EP2:.PMMfaza60[1]
EP2PMMfaza6020 | REAL | IOD_EP2 | EP2:.PMMfaza60[20]
EP2PMMfaza6021 | REAL | IOD_EP2 | EP2:.PMMfaza60[21]
EP2PMMfaza6022 | REAL | IOD_EP2 | EP2:.PMMfaza60[22]
EP2PMMfaza6023 | REAL | IOD_EP2 | EP2:.PMMfaza60[23]
EP2PMMfaza6024 | REAL | IOD_EP2 | EP2:.PMMfaza60[24]
EP2PMMfaza6025 | REAL | IOD_EP2 | EP2:.PMMfaza60[25]
EP2PMMfaza6026 | REAL | IOD_EP2 | EP2:.PMMfaza60[26]
EP2PMMfaza6027 | REAL | IOD_EP2 | EP2:.PMMfaza60[27]
EP2PMMfaza6028 | REAL | IOD_EP2 | EP2:.PMMfaza60[28]
EP2PMMfaza6029 | REAL | IOD_EP2 | EP2:.PMMfaza60[29]
EP2PMMfaza602 | REAL | IOD_EP2 | EP2:.PMMfaza60[2]
EP2PMMfaza6030 | REAL | IOD_EP2 | EP2:.PMMfaza60[30]
EP2PMMfaza6031 | REAL | IOD_EP2 | EP2:.PMMfaza60[31]
EP2PMMfaza6032 | REAL | IOD_EP2 | EP2:.PMMfaza60[32]
EP2PMMfaza6033 | REAL | IOD_EP2 | EP2:.PMMfaza60[33]
EP2PMMfaza6034 | REAL | IOD_EP2 | EP2:.PMMfaza60[34]
EP2PMMfaza6035 | REAL | IOD_EP2 | EP2:.PMMfaza60[35]
EP2PMMfaza6036 | REAL | IOD_EP2 | EP2:.PMMfaza60[36]
EP2PMMfaza6037 | REAL | IOD_EP2 | EP2:.PMMfaza60[37]
EP2PMMfaza6038 | REAL | IOD_EP2 | EP2:.PMMfaza60[38]
EP2PMMfaza6039 | REAL | IOD_EP2 | EP2:.PMMfaza60[39]
EP2PMMfaza603 | REAL | IOD_EP2 | EP2:.PMMfaza60[3]
EP2PMMfaza6040 | REAL | IOD_EP2 | EP2:.PMMfaza60[40]
EP2PMMfaza6041 | REAL | IOD_EP2 | EP2:.PMMfaza60[41]
EP2PMMfaza6042 | REAL | IOD_EP2 | EP2:.PMMfaza60[42]
EP2PMMfaza604 | REAL | IOD_EP2 | EP2:.PMMfaza60[4]
EP2PMMfaza605 | REAL | IOD_EP2 | EP2:.PMMfaza60[5]
EP2PMMfaza606 | REAL | IOD_EP2 | EP2:.PMMfaza60[6]
EP2PMMfaza607 | REAL | IOD_EP2 | EP2:.PMMfaza60[7]
EP2PMMfaza608 | REAL | IOD_EP2 | EP2:.PMMfaza60[8]
EP2PMMfaza609 | REAL | IOD_EP2 | EP2:.PMMfaza60[9]
EP2PMMfaza8010 | REAL | IOD_EP2 | EP2:.PMMfaza80[10]
EP2PMMfaza8011 | REAL | IOD_EP2 | EP2:.PMMfaza80[11]
EP2PMMfaza8012 | REAL | IOD_EP2 | EP2:.PMMfaza80[12]
EP2PMMfaza8013 | REAL | IOD_EP2 | EP2:.PMMfaza80[13]
EP2PMMfaza8014 | REAL | IOD_EP2 | EP2:.PMMfaza80[14]
EP2PMMfaza8015 | REAL | IOD_EP2 | EP2:.PMMfaza80[15]
EP2PMMfaza8016 | REAL | IOD_EP2 | EP2:.PMMfaza80[16]
EP2PMMfaza8017 | REAL | IOD_EP2 | EP2:.PMMfaza80[17]
EP2PMMfaza8018 | REAL | IOD_EP2 | EP2:.PMMfaza80[18]
EP2PMMfaza8019 | REAL | IOD_EP2 | EP2:.PMMfaza80[19]
EP2PMMfaza801 | REAL | IOD_EP2 | EP2:.PMMfaza80[1]
EP2PMMfaza8020 | REAL | IOD_EP2 | EP2:.PMMfaza80[20]
EP2PMMfaza8021 | REAL | IOD_EP2 | EP2:.PMMfaza80[21]
EP2PMMfaza8022 | REAL | IOD_EP2 | EP2:.PMMfaza80[22]
EP2PMMfaza8023 | REAL | IOD_EP2 | EP2:.PMMfaza80[23]
EP2PMMfaza8024 | REAL | IOD_EP2 | EP2:.PMMfaza80[24]
EP2PMMfaza8025 | REAL | IOD_EP2 | EP2:.PMMfaza80[25]
EP2PMMfaza8026 | REAL | IOD_EP2 | EP2:.PMMfaza80[26]
EP2PMMfaza8027 | REAL | IOD_EP2 | EP2:.PMMfaza80[27]
EP2PMMfaza8028 | REAL | IOD_EP2 | EP2:.PMMfaza80[28]
EP2PMMfaza8029 | REAL | IOD_EP2 | EP2:.PMMfaza80[29]
EP2PMMfaza802 | REAL | IOD_EP2 | EP2:.PMMfaza80[2]
EP2PMMfaza8030 | REAL | IOD_EP2 | EP2:.PMMfaza80[30]
EP2PMMfaza8031 | REAL | IOD_EP2 | EP2:.PMMfaza80[31]
EP2PMMfaza8032 | REAL | IOD_EP2 | EP2:.PMMfaza80[32]
EP2PMMfaza8033 | REAL | IOD_EP2 | EP2:.PMMfaza80[33]
EP2PMMfaza8034 | REAL | IOD_EP2 | EP2:.PMMfaza80[34]
EP2PMMfaza8035 | REAL | IOD_EP2 | EP2:.PMMfaza80[35]
EP2PMMfaza8036 | REAL | IOD_EP2 | EP2:.PMMfaza80[36]
EP2PMMfaza8037 | REAL | IOD_EP2 | EP2:.PMMfaza80[37]
EP2PMMfaza8038 | REAL | IOD_EP2 | EP2:.PMMfaza80[38]
EP2PMMfaza8039 | REAL | IOD_EP2 | EP2:.PMMfaza80[39]
EP2PMMfaza803 | REAL | IOD_EP2 | EP2:.PMMfaza80[3]
EP2PMMfaza8040 | REAL | IOD_EP2 | EP2:.PMMfaza80[40]
EP2PMMfaza8041 | REAL | IOD_EP2 | EP2:.PMMfaza80[41]
EP2PMMfaza8042 | REAL | IOD_EP2 | EP2:.PMMfaza80[42]
EP2PMMfaza804 | REAL | IOD_EP2 | EP2:.PMMfaza80[4]
EP2PMMfaza805 | REAL | IOD_EP2 | EP2:.PMMfaza80[5]
EP2PMMfaza806 | REAL | IOD_EP2 | EP2:.PMMfaza80[6]
EP2PMMfaza807 | REAL | IOD_EP2 | EP2:.PMMfaza80[7]
EP2PMMfaza808 | REAL | IOD_EP2 | EP2:.PMMfaza80[8]
EP2PMMfaza809 | REAL | IOD_EP2 | EP2:.PMMfaza80[9]
EP2PMMgalActivePowerPhaseA_kW | REAL | IOD_EP2 | EP2:.PMMgal.ActivePowerPhaseA_kW
EP2PMMgalActivePowerPhaseB_kW | REAL | IOD_EP2 | EP2:.PMMgal.ActivePowerPhaseB_kW
EP2PMMgalActivePowerPhaseC_kW | REAL | IOD_EP2 | EP2:.PMMgal.ActivePowerPhaseC_kW
EP2PMMgalAlarmPhase1C01_16_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C01_16_60to80
EP2PMMgalAlarmPhase1C01_16_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C01_16_over80
EP2PMMgalAlarmPhase1C17_32_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C17_32_60to80
EP2PMMgalAlarmPhase1C17_32_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C17_32_over80
EP2PMMgalAlarmPhase1C33_42_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C33_42_60to80
EP2PMMgalAlarmPhase1C33_42_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C33_42_over80
EP2PMMgalAlarmPhase1GlobalAlarmReg | INT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].GlobalAlarmReg
EP2PMMgalAlarmPhase2C01_16_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C01_16_60to80
EP2PMMgalAlarmPhase2C01_16_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C01_16_over80
EP2PMMgalAlarmPhase2C17_32_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C17_32_60to80
EP2PMMgalAlarmPhase2C17_32_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C17_32_over80
EP2PMMgalAlarmPhase2C33_42_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C33_42_60to80
EP2PMMgalAlarmPhase2C33_42_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C33_42_over80
EP2PMMgalAlarmPhase2GlobalAlarmReg | INT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].GlobalAlarmReg
EP2PMMgalAlarmPhase3C01_16_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C01_16_60to80
EP2PMMgalAlarmPhase3C01_16_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C01_16_over80
EP2PMMgalAlarmPhase3C17_32_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C17_32_60to80
EP2PMMgalAlarmPhase3C17_32_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C17_32_over80
EP2PMMgalAlarmPhase3C33_42_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C33_42_60to80
EP2PMMgalAlarmPhase3C33_42_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C33_42_over80
EP2PMMgalAlarmPhase3GlobalAlarmReg | INT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].GlobalAlarmReg
EP2PMMgalAlarms | UINT | IOD_EP2 | EP2:.PMMgal.Alarms
EP2PMMgalAverageCurrent_A | REAL | IOD_EP2 | EP2:.PMMgal.AverageCurrent_A
EP2PMMgalAveragePhaseToNeutral_V | REAL | IOD_EP2 | EP2:.PMMgal.AveragePhaseToNeutral_V
EP2PMMgalAveragePhaseToPhase_V | REAL | IOD_EP2 | EP2:.PMMgal.AveragePhaseToPhase_V
EP2PMMgalCurrentInPhaseA_A | REAL | IOD_EP2 | EP2:.PMMgal.CurrentInPhaseA_A
EP2PMMgalCurrentInPhaseB_A | REAL | IOD_EP2 | EP2:.PMMgal.CurrentInPhaseB_A
EP2PMMgalCurrentInPhaseC_A | REAL | IOD_EP2 | EP2:.PMMgal.CurrentInPhaseC_A
EP2PMMgalEnergyConsumed_kWh | REAL | IOD_EP2 | EP2:.PMMgal.EnergyConsumed_kWh
EP2PMMgalFrequency_Hz | REAL | IOD_EP2 | EP2:.PMMgal.Frequency_Hz
EP2PMMgalNapaka | DIGITAL | IOD_EP2 | EP2:.PMMgal.Napaka
EP2PMMgalNeutralCurrent_A | REAL | IOD_EP2 | EP2:.PMMgal.NeutralCurrent_A
EP2PMMgalPhase1Current10 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[10]
EP2PMMgalPhase1Current11 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[11]
EP2PMMgalPhase1Current12 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[12]
EP2PMMgalPhase1Current13 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[13]
EP2PMMgalPhase1Current14 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[14]
EP2PMMgalPhase1Current15 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[15]
EP2PMMgalPhase1Current16 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[16]
EP2PMMgalPhase1Current17 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[17]
EP2PMMgalPhase1Current18 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[18]
EP2PMMgalPhase1Current19 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[19]
EP2PMMgalPhase1Current1 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[1]
EP2PMMgalPhase1Current20 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[20]
EP2PMMgalPhase1Current21 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[21]
EP2PMMgalPhase1Current22 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[22]
EP2PMMgalPhase1Current23 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[23]
EP2PMMgalPhase1Current24 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[24]
EP2PMMgalPhase1Current25 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[25]
EP2PMMgalPhase1Current26 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[26]
EP2PMMgalPhase1Current27 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[27]
EP2PMMgalPhase1Current28 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[28]
EP2PMMgalPhase1Current29 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[29]
EP2PMMgalPhase1Current2 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[2]
EP2PMMgalPhase1Current30 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[30]
EP2PMMgalPhase1Current31 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[31]
EP2PMMgalPhase1Current32 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[32]
EP2PMMgalPhase1Current33 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[33]
EP2PMMgalPhase1Current34 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[34]
EP2PMMgalPhase1Current35 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[35]
EP2PMMgalPhase1Current36 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[36]
EP2PMMgalPhase1Current37 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[37]
EP2PMMgalPhase1Current38 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[38]
EP2PMMgalPhase1Current39 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[39]
EP2PMMgalPhase1Current3 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[3]
EP2PMMgalPhase1Current40 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[40]
EP2PMMgalPhase1Current41 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[41]
EP2PMMgalPhase1Current42 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[42]
EP2PMMgalPhase1Current4 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[4]
EP2PMMgalPhase1Current5 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[5]
EP2PMMgalPhase1Current6 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[6]
EP2PMMgalPhase1Current7 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[7]
EP2PMMgalPhase1Current8 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[8]
EP2PMMgalPhase1Current9 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[9]
EP2PMMgalPhase2Current10 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[10]
EP2PMMgalPhase2Current11 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[11]
EP2PMMgalPhase2Current12 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[12]
EP2PMMgalPhase2Current13 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[13]
EP2PMMgalPhase2Current14 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[14]
EP2PMMgalPhase2Current15 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[15]
EP2PMMgalPhase2Current16 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[16]
EP2PMMgalPhase2Current17 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[17]
EP2PMMgalPhase2Current18 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[18]
EP2PMMgalPhase2Current19 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[19]
EP2PMMgalPhase2Current1 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[1]
EP2PMMgalPhase2Current20 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[20]
EP2PMMgalPhase2Current21 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[21]
EP2PMMgalPhase2Current22 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[22]
EP2PMMgalPhase2Current23 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[23]
EP2PMMgalPhase2Current24 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[24]
EP2TempAlarmPoint | REAL | IOD_EP2 | EP2:.TempAlarmPoint
EP2ErrCommScada2 | DIGITAL | IOD_EP2 | EP2:.ErrCommScada2
EP2ComSCADA2 | DIGITAL | IOD_EP2 | EP2:.ComSCADA2
EP2_RazlikaUr | REAL | IOD_EP2 | EP2:.RazlikaUr
EP2ComSCADA3 | DIGITAL | IOD_EP2 | EP2:.ComSCADA3
EP2kom_nast_cas_izpada | INT | IOD_EP2 | EP2:.kom_nast_cas_izpada
EP2_Circ1_MaximumDemandA2 | REAL | IOD_EP2 | EP2:.Circ[1].MaximumDemandA2
EP2_Circ1_MaximumDemandA3 | REAL | IOD_EP2 | EP2:.Circ[1].MaximumDemandA3
EP2Circ1RazEner_D_SCADA | REAL | IOD_EP2 | EP2:.Circ[1].RazEner_D_SCADA
EP2Circ1RazEner_T_SCADA | REAL | IOD_EP2 | EP2:.Circ[1].RazEner_T_SCADA
EP2Circ1RazEner_M_SCADA | REAL | IOD_EP2 | EP2:.Circ[1].RazEner_M_SCADA
EP2Circ_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Dnevne_energija_scada1
EP2Circ_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Dnevne_energija_scada2
EP2Circ_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Tedenska_energija_scada1
EP2Circ_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Tedenska_energija_scada2
EP2Circ_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Mesecna_energija_scada1
EP2Circ_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Mesecna_energija_scada2

## variable_2
EP2_AlarmGenCirc1 | DIGITAL | IOD_EP2 | EP2:.AlarmGenCirc1
EP2_AlarmGenComm | DIGITAL | IOD_EP2 | EP2:.AlarmGenComm
EP2_AlarmGenDI | DIGITAL | IOD_EP2 | EP2:.AlarmGenDI
EP2_AlarmGenKlima5 | DIGITAL | IOD_EP2 | EP2:.AlarmGenKlima5
EP2_AlarmGenKlima6 | DIGITAL | IOD_EP2 | EP2:.AlarmGenKlima6
EP2_AlarmGenPMM1 | DIGITAL | IOD_EP2 | EP2:.AlarmGenPMM1
EP2_AlarmGenPMM2 | DIGITAL | IOD_EP2 | EP2:.AlarmGenPMM2
EP2_AlarmGenPMM3 | DIGITAL | IOD_EP2 | EP2:.AlarmGenPMM3
EP2_AlarmGenUPS1 | DIGITAL | IOD_EP2 | EP2:.AlarmGenUPS1
EP2_AlarmGenUPS2 | DIGITAL | IOD_EP2 | EP2:.AlarmGenUPS2
EP2_ComSCADA | DIGITAL | IOD_EP2 | EP2:.ComSCADA
EP2_ComSCADA1 | DIGITAL | IOD_EP2 | EP2:.ComSCADA1
EP2_DI_Klima5_ERR | DIGITAL | IOD_EP2 | EP2:.DI_Klima5_ERR
EP2_DI_Klima5_ON | DIGITAL | IOD_EP2 | EP2:.DI_Klima5_ON
EP2_DI_Klima6_ERR | DIGITAL | IOD_EP2 | EP2:.DI_Klima6_ERR
EP2_DI_Klima6_ON | DIGITAL | IOD_EP2 | EP2:.DI_Klima6_ON
EP2_DI_KlimaSplit1_ERR | DIGITAL | IOD_EP2 | EP2:.DI_KlimaSplit1_ERR
EP2_DI_KlimaSplit1_ON | DIGITAL | IOD_EP2 | EP2:.DI_KlimaSplit1_ON
EP2_DI_Q10_OdcKlima6_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q10_OdcKlima6_IZP
EP2_DI_Q10_OdcKlima6_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q10_OdcKlima6_ON
EP2_DI_Q11_OdcVent1_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q11_OdcVent1_ON
EP2_DI_Q12_Rezerva_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q12_Rezerva_ON
EP2_DI_Q1_GlavnoStikalo_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q1_GlavnoStikalo_ON
EP2_DI_Q25_OdcUpsA_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q25_OdcUpsA_IZP
EP2_DI_Q25_OdcUpsA_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q25_OdcUpsA_ON
EP2_DI_Q26_OdcByA_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q26_OdcByA_IZP
EP2_DI_Q26_OdcByA_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q26_OdcByA_ON
EP2_DI_Q27_OdcByUpsA_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q27_OdcByUpsA_IZP
EP2_DI_Q27_OdcByUpsA_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q27_OdcByUpsA_ON
EP2_DI_Q28_OdcUpsB_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q28_OdcUpsB_IZP
EP2_DI_Q28_OdcUpsB_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q28_OdcUpsB_ON
EP2_DI_Q29_OdcByB_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q29_OdcByB_IZP
EP2_DI_Q29_OdcByB_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q29_OdcByB_ON
EP2_DI_Q2_Rezerva_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q2_Rezerva_IZP
EP2_DI_Q2_Rezerva_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q2_Rezerva_ON
EP2_DI_Q30_OdcByUpsB_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q30_OdcByUpsB_IZP
EP2_DI_Q30_OdcByUpsB_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q30_OdcByUpsB_ON
EP2_DI_Q31_DovByUpsA_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q31_DovByUpsA_ON
EP2_DI_Q32_DovByA_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q32_DovByA_ON
EP2_DI_Q33_DovByUpsB_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q33_DovByUpsB_ON
EP2_DI_Q34_DovByB_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q34_DovByB_ON
EP2_DI_Q5_OdcKlima1_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q5_OdcKlima1_IZP
EP2_DI_Q5_OdcKlima1_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q5_OdcKlima1_ON
EP2_DI_Q6_OdcKlima2_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q6_OdcKlima2_IZP
EP2_DI_Q6_OdcKlima2_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q6_OdcKlima2_ON
EP2_DI_Q7_OdcKlima3_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q7_OdcKlima3_IZP
EP2_DI_Q7_OdcKlima3_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q7_OdcKlima3_ON
EP2_DI_Q8_OdcKlima4_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q8_OdcKlima4_IZP
EP2_DI_Q8_OdcKlima4_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q8_OdcKlima4_ON
EP2_DI_Q9_OdcKlima5_IZP | DIGITAL | IOD_EP2 | EP2:.DI_Q9_OdcKlima5_IZP
EP2_DI_Q9_OdcKlima5_ON | DIGITAL | IOD_EP2 | EP2:.DI_Q9_OdcKlima5_ON
EP2_DI_RazlitjeVodeK5K6 | DIGITAL | IOD_EP2 | EP2:.DI_RazlitjeVodeK5K6
EP2_DI_UPS_Alarm | DIGITAL | IOD_EP2 | EP2:.DI_UPS_Alarm
EP2_DI_UPS_BatNacin | DIGITAL | IOD_EP2 | EP2:.DI_UPS_BatNacin
EP2_DI_UPS_Polnjenje | DIGITAL | IOD_EP2 | EP2:.DI_UPS_Polnjenje
EP2_DI_UpsA_ERR | DIGITAL | IOD_EP2 | EP2:.DIN_UpsA_ERR
EP2_DI_UpsA_ON | DIGITAL | IOD_EP2 | EP2:.DIN_UpsA_BypassON
EP2_DI_UpsB_ERR | DIGITAL | IOD_EP2 | EP2:.DIN_UpsB_ERR
EP2_DI_UpsB_ON | DIGITAL | IOD_EP2 | EP2:.DIN_UpsB_BypassON
EP2_DO_Klima5_Izklop | DIGITAL | IOD_EP2 | EP2:.DO_Klima5_Izklop
EP2_DO_Klima6_Izklop | DIGITAL | IOD_EP2 | EP2:.DO_Klima6_Izklop
EP2_ErrComCirc1 | DIGITAL | IOD_EP2 | EP2:.ErrComCirc[1]
EP2_ErrComCirc2 | DIGITAL | IOD_EP2 | EP2:.ErrComCirc[2]
EP2_ErrComCirc3 | DIGITAL | IOD_EP2 | EP2:.ErrComCirc[3]
EP2_ErrComCirc4 | DIGITAL | IOD_EP2 | EP2:.ErrComCirc[4]
EP2_ErrComCirc5 | DIGITAL | IOD_EP2 | EP2:.ErrComCirc[5]
EP2_ErrComKlima1 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[1]
EP2_ErrComKlima2 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[2]
EP2_ErrComKlima3 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[3]
EP2_ErrComKlima4 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[4]
EP2_ErrComKlima5 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[5]
EP2_ErrComKlima6 | DIGITAL | IOD_EP2 | EP2:.ErrComKlima[6]
EP2_ErrCommScada | DIGITAL | IOD_EP2 | EP2:.ErrCommScada
EP2_ErrComPanelPLC | DIGITAL | IOD_EP2 | EP2:.ErrComPanelPLC
EP2_ErrComPMM1 | DIGITAL | IOD_EP2 | EP2:.ErrComPMM[1]
EP2_ErrComPMM2 | DIGITAL | IOD_EP2 | EP2:.ErrComPMM[2]
EP2_ErrComPMM3 | DIGITAL | IOD_EP2 | EP2:.ErrComPMM[3]
EP2_ErrComPort2 | DIGITAL | IOD_EP2 | EP2:.ErrComPort2
EP2_ErrComPort3 | DIGITAL | IOD_EP2 | EP2:.ErrComPort3
EP2_ErrComPort4 | DIGITAL | IOD_EP2 | EP2:.ErrComPort4
EP2_ErrComUPS1 | DIGITAL | IOD_EP2 | EP2:.ErrComUPS[1]
EP2_ErrComUPS2 | DIGITAL | IOD_EP2 | EP2:.ErrComUPS[2]
EP2_Klima1_AlarmKompresor1 | DIGITAL | IOD_EP2 | EP2:.Klima[1].AlarmKompresor1
EP2_Klima1_AlarmKompresor2 | DIGITAL | IOD_EP2 | EP2:.Klima[1].AlarmKompresor2
EP2_Klima1_Deluje | DIGITAL | IOD_EP2 | EP2:.Klima[1].Deluje
EP2_Klima1_EnergySaving | DIGITAL | IOD_EP2 | EP2:.Klima[1].EnergySaving
EP2_Klima1_FaultyEPROM | DIGITAL | IOD_EP2 | EP2:.Klima[1].FaultyEPROM
EP2_Klima1_FenThermalCutout | DIGITAL | IOD_EP2 | EP2:.Klima[1].FenThermalCutout
EP2_Klima1_GeneralAlarm | DIGITAL | IOD_EP2 | EP2:.Klima[1].GeneralAlarm
EP2_Klima1_Kompresor1naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[1].Kompresor1naMejiObrUr
EP2_Klima1_Kompresor2naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[1].Kompresor2naMejiObrUr
EP2_Klima1_Napaka | DIGITAL | IOD_EP2 | EP2:.Klima[1].Napaka
EP2_Klima1_NapakaPriPretokuZraka | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaPriPretokuZraka
EP2_Klima1_NapakaSenzorPovratVod | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaSenzorPovratVode
EP2_Klima1_NapakaSenzorTempIzpih | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaSenzorTempIzpiha
EP2_Klima1_NapakaSenzorTempProst | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaSenzorTempProstora
EP2_Klima1_NapakaSenzorVlaznosti | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaSenzorVlaznosti
EP2_Klima1_NapakaSenzorZunanjeTemp | DIGITAL | IOD_EP2 | EP2:.Klima[1].NapakaSenzorZunanjeTemp
EP2_Klima1_NiTokaVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[1].NiTokaVVlazilcu
EP2_Klima1_NiVodeVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[1].NiVodeVVlazilcu
EP2_Klima1_NizekPritiskKompresor1 | DIGITAL | IOD_EP2 | EP2:.Klima[1].NizekPritiskKompresor1
EP2_Klima1_NizekPritiskKompresor2 | DIGITAL | IOD_EP2 | EP2:.Klima[1].NizekPritiskKompresor2
EP2_Klima1_NizkaTempPovratneVode | DIGITAL | IOD_EP2 | EP2:.Klima[1].NizkaTempPovratneVode
EP2_Klima1_NizkaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.Klima[1].NizkaTempVProstoru
EP2_Klima1_NizkaVlaznost | DIGITAL | IOD_EP2 | EP2:.Klima[1].NizkaVlaznost
EP2_Klima1_OnOffEnablingBySupervisor | DIGITAL | IOD_EP2 | EP2:.Klima[1].OnOffEnablingBySupervisor
EP2_Klima1_PozarniAlarm | DIGITAL | IOD_EP2 | EP2:.Klima[1].PozarniAlarm
EP2_Klima1_Razvlazevanje | DIGITAL | IOD_EP2 | EP2:.Klima[1].Razvlazevanje
EP2_Klima1_RemoteOFFtoOutput | DIGITAL | IOD_EP2 | EP2:.Klima[1].RemoteOFFtoOutput
EP2_Klima1_RemoteOnOff | DIGITAL | IOD_EP2 | EP2:.Klima[1].RemoteOnOff
EP2_Klima1_RocniIzklop | DIGITAL | IOD_EP2 | EP2:.Klima[1].RocniIzklop
EP2_Klima1_SenzorjiStatus | DIGITAL | IOD_EP2 | EP2:.Klima[1].SenzorjiStatus
EP2_Klima1_StoppedByAlarms | DIGITAL | IOD_EP2 | EP2:.Klima[1].StoppedByAlarms
EP2_Klima1_ThermalCutoutHeater1 | DIGITAL | IOD_EP2 | EP2:.Klima[1].ThermalCutoutHeater1
EP2_Klima1_ThermalCutoutHeater2 | DIGITAL | IOD_EP2 | EP2:.Klima[1].ThermalCutoutHeater2
EP2_Klima1_UnitOnOff | DIGITAL | IOD_EP2 | EP2:.Klima[1].UnitOnOff
EP2_Klima1_VentilatorNaMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[1].VentilatorNaMejiObrUr
EP2_Klima1_VentilGretjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.Klima[1].VentilGretjeOdpiranje
EP2_Klima1_VentilGretjeZapiranje | DIGITAL | IOD_EP2 | EP2:.Klima[1].VentilGretjeZapiranje
EP2_Klima1_VentilHlajenjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.Klima[1].VentilHlajenjeOdpiranje
EP2_Klima1_VentilHlajenjeZapiranje | DIGITAL | IOD_EP2 | EP2:.Klima[1].VentilHlajenjeZapiranje
EP2_Klima1_VisokaTempPovratneVode | DIGITAL | IOD_EP2 | EP2:.Klima[1].VisokaTempPovratneVode
EP2_Klima1_VisokaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.Klima[1].VisokaTempVProstoru
EP2_Klima1_VisokaVlaznost | DIGITAL | IOD_EP2 | EP2:.Klima[1].VisokaVlaznost
EP2_Klima1_VisokTokVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[1].VisokTokVVlazilcu
EP2_Klima1_Vlazenje | DIGITAL | IOD_EP2 | EP2:.Klima[1].Vlazenje
EP2_Klima1_ZamasenFilter | DIGITAL | IOD_EP2 | EP2:.Klima[1].ZamasenFilter
EP2_Klima2_AlarmKompresor1 | DIGITAL | IOD_EP2 | EP2:.Klima[2].AlarmKompresor1
EP2_Klima2_AlarmKompresor2 | DIGITAL | IOD_EP2 | EP2:.Klima[2].AlarmKompresor2
EP2_Klima2_Deluje | DIGITAL | IOD_EP2 | EP2:.Klima[2].Deluje
EP2_Klima2_EnergySaving | DIGITAL | IOD_EP2 | EP2:.Klima[2].EnergySaving
EP2_Klima2_FaultyEPROM | DIGITAL | IOD_EP2 | EP2:.Klima[2].FaultyEPROM
EP2_Klima2_FenThermalCutout | DIGITAL | IOD_EP2 | EP2:.Klima[2].FenThermalCutout
EP2_Klima2_GeneralAlarm | DIGITAL | IOD_EP2 | EP2:.Klima[2].GeneralAlarm
EP2_Klima2_Kompresor1naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[2].Kompresor1naMejiObrUr
EP2_Klima2_Kompresor2naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[2].Kompresor2naMejiObrUr
EP2_Klima2_Napaka | DIGITAL | IOD_EP2 | EP2:.Klima[2].Napaka
EP2_Klima2_NapakaPriPretokuZraka | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaPriPretokuZraka
EP2_Klima2_NapakaSenzorPovratVode | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaSenzorPovratVode
EP2_Klima2_NapakaSenzorTempIzpih | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaSenzorTempIzpiha
EP2_Klima2_NapakaSenzorTempProst | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaSenzorTempProstora
EP2_Klima2_NapakaSenzorVlaznosti | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaSenzorVlaznosti
EP2_Klima2_NapakaSenzorZunanjeTemp | DIGITAL | IOD_EP2 | EP2:.Klima[2].NapakaSenzorZunanjeTemp
EP2_Klima2_NiTokaVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[2].NiTokaVVlazilcu
EP2_Klima2_NiVodeVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[2].NiVodeVVlazilcu
EP2_Klima2_NizekPritiskKompresor1 | DIGITAL | IOD_EP2 | EP2:.Klima[2].NizekPritiskKompresor1
EP2_Klima2_NizekPritiskKompresor2 | DIGITAL | IOD_EP2 | EP2:.Klima[2].NizekPritiskKompresor2
EP2_Klima2_NizkaTempPovratneVode | DIGITAL | IOD_EP2 | EP2:.Klima[2].NizkaTempPovratneVode
EP2_Klima2_NizkaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.Klima[2].NizkaTempVProstoru
EP2_Klima2_NizkaVlaznost | DIGITAL | IOD_EP2 | EP2:.Klima[2].NizkaVlaznost
EP2_Klima2_OnOffEnablingBySupervisor | DIGITAL | IOD_EP2 | EP2:.Klima[2].OnOffEnablingBySupervisor
EP2_Klima2_PozarniAlarm | DIGITAL | IOD_EP2 | EP2:.Klima[2].PozarniAlarm
EP2_Klima2_Razvlazevanje | DIGITAL | IOD_EP2 | EP2:.Klima[2].Razvlazevanje
EP2_Klima2_RemoteOFFtoOutput | DIGITAL | IOD_EP2 | EP2:.Klima[2].RemoteOFFtoOutput
EP2_Klima2_RemoteOnOff | DIGITAL | IOD_EP2 | EP2:.Klima[2].RemoteOnOff
EP2_Klima2_RocniIzklop | DIGITAL | IOD_EP2 | EP2:.Klima[2].RocniIzklop
EP2_Klima2_SenzorjiStatus | DIGITAL | IOD_EP2 | EP2:.Klima[2].SenzorjiStatus
EP2_Klima2_StoppedByAlarms | DIGITAL | IOD_EP2 | EP2:.Klima[2].StoppedByAlarms
EP2_Klima2_ThermalCutoutHeater1 | DIGITAL | IOD_EP2 | EP2:.Klima[2].ThermalCutoutHeater1
EP2_Klima2_ThermalCutoutHeater2 | DIGITAL | IOD_EP2 | EP2:.Klima[2].ThermalCutoutHeater2
EP2_Klima2_UnitOnOff | DIGITAL | IOD_EP2 | EP2:.Klima[2].UnitOnOff
EP2_Klima2_VentilatorNaMejiObrUr | DIGITAL | IOD_EP2 | EP2:.Klima[2].VentilatorNaMejiObrUr
EP2_Klima2_VentilGretjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.Klima[2].VentilGretjeOdpiranje
EP2_Klima2_VentilGretjeZapiranje | DIGITAL | IOD_EP2 | EP2:.Klima[2].VentilGretjeZapiranje
EP2_Klima2_VentilHlajenjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.Klima[2].VentilHlajenjeOdpiranje
EP2_Klima2_VentilHlajenjeZapiranje | DIGITAL | IOD_EP2 | EP2:.Klima[2].VentilHlajenjeZapiranje
EP2_Klima2_VisokaTempPovratneVod | DIGITAL | IOD_EP2 | EP2:.Klima[2].VisokaTempPovratneVode
EP2_Klima2_VisokaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.Klima[2].VisokaTempVProstoru
EP2_Klima2_VisokaVlaznost | DIGITAL | IOD_EP2 | EP2:.Klima[2].VisokaVlaznost
EP2_Klima2_VisokTokVVlazilcu | DIGITAL | IOD_EP2 | EP2:.Klima[2].VisokTokVVlazilcu
EP2_Klima2_Vlazenje | DIGITAL | IOD_EP2 | EP2:.Klima[2].Vlazenje
EP2_Klima2_ZamasenFilter | DIGITAL | IOD_EP2 | EP2:.Klima[2].ZamasenFilter
EP2_KlimeNaCas | DIGITAL | IOD_EP2 | EP2:.KlimeNaCas
EP2_NapakaSenzorTemp1 | DIGITAL | IOD_EP2 | EP2:.NapakaSenzorTemp[1]
EP2_NapakaSenzorTemp2 | DIGITAL | IOD_EP2 | EP2:.NapakaSenzorTemp[2]
EP2_NapakaSenzorVlaga1 | DIGITAL | IOD_EP2 | EP2:.NapakaSenzorVlaga[1]
EP2_NapakaSenzorVlaga2 | DIGITAL | IOD_EP2 | EP2:.NapakaSenzorVlaga[2]
EP2_PMM1OverCurrentBetw1 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentBetw[1]
EP2_PMM1OverCurrentBetw2 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentBetw[2]
EP2_PMM1OverCurrentBetw3 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentBetw[3]
EP2_PMM1OverCurrentOver1 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentOver[1]
EP2_PMM1OverCurrentOver2 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentOver[2]
EP2_PMM1OverCurrentOver3 | DIGITAL | IOD_EP2 | EP2:.PMM1OverCurrentOver[3]
EP2_PMM2OverCurrentBetw1 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentBetw[1]
EP2_PMM2OverCurrentBetw2 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentBetw[2]
EP2_PMM2OverCurrentBetw3 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentBetw[3]
EP2_PMM2OverCurrentOver1 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentOver[1]
EP2_PMM2OverCurrentOver2 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentOver[2]
EP2_PMM2OverCurrentOver3 | DIGITAL | IOD_EP2 | EP2:.PMM2OverCurrentOver[3]
EP2_PMM3OverCurrentBetw1 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentBetw[1]
EP2_PMM3OverCurrentBetw2 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentBetw[2]
EP2_PMM3OverCurrentBetw3 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentBetw[3]
EP2_PMM3OverCurrentOver1 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentOver[1]
EP2_PMM3OverCurrentOver2 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentOver[2]
EP2_PMM3OverCurrentOver3 | DIGITAL | IOD_EP2 | EP2:.PMM3OverCurrentOver[3]
EP2_PMM1_Napaka | DIGITAL | IOD_EP2 | EP2:.PMM[1].Napaka
EP2_PMM2_Napaka | DIGITAL | IOD_EP2 | EP2:.PMM[2].Napaka
EP2_PMM3_Napaka | DIGITAL | IOD_EP2 | EP2:.PMM[3].Napaka
EP2_SetDateTime | DIGITAL | IOD_EP2 | EP2:.SetDateTime
EP2_SetDateTimeDemand | DIGITAL | IOD_EP2 | EP2:.SetDateTimeDemand
EP2_SetDateTimeError | DIGITAL | IOD_EP2 | EP2:.SetDateTimeError
EP2_SetDateTimeFinished | DIGITAL | IOD_EP2 | EP2:.SetDateTimeFinished
EP2_SetRemoteOnOff1 | DIGITAL | IOD_EP2 | EP2:.SetRemoteOnOff[1]
EP2_SetRemoteOnOff2 | DIGITAL | IOD_EP2 | EP2:.SetRemoteOnOff[2]
EP2_SlabaBaterijaPLC_A1 | DIGITAL | IOD_EP2 | EP2:.SlabaBaterijaPLC_A1
EP2_TempTSprevisoka1 | DIGITAL | IOD_EP2 | EP2:.TempTSprevisoka[1]
EP2_TempTSprevisoka2 | DIGITAL | IOD_EP2 | EP2:.TempTSprevisoka[2]
EP2UPS1AlarmAwaitingPower | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmAwaitingPower
EP2UPS1AlarmBypassBad | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmBypassBad
EP2UPS1AlarmChargerFailed | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmChargerFailed
EP2UPS1AlarmCommunicationsLost | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmCommunicationsLost
EP2UPS1AlarmDepletedBattery | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmDepletedBattery
EP2UPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmDiagnosticTestFailed
EP2UPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmIzhodOffKotZahtevano
EP2UPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmIzhodPreobremenjen
EP2UPS1AlarmLowBattery | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmLowBattery
EP2UPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmNapakaNaVarovalki
EP2UPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmNapakaNaVentilatorju
EP2UPS1AlarmOnBattery | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmOnBattery
EP2UPS1AlarmOnBypass | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmOnBypass
EP2UPS1AlarmInverterError | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmInverterError
EP2UPS1AlarmShutdownImminent | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmShutdownImminent
EP2UPS1AlarmShutdownPending | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmShutdownPending
EP2UPS1AlarmSlabaBaterija | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmSlabaBaterija
EP2UPS1AlarmSplosnaNapaka | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmSplosnaNapaka
EP2UPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmStanjeIzhodaIzvenToleranc
EP2UPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmStanjeVhodaIzvenToleranc
EP2UPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmTemperaturaIzvenToleranc
EP2UPS1AlarmTestInProgres | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmTestInProgres
EP2UPS1AlarmUPSIzhodOff | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmUPSIzhodOff
EP2UPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmUPSOffKotZahtevano
EP2UPS1AlarmUPSSystemOff | DIGITAL | IOD_EP2 | EP2:.UPS[1].AlarmUPSSystemOff
EP2UPS1Napaka | DIGITAL | IOD_EP2 | EP2:.UPS[1].Napaka
EP2UPS1StatusEcomodeAktiven | DIGITAL | IOD_EP2 | EP2:.UPS[1].StatusEcomodeAktiven
EP2UPS1StatusInverterIsOn | DIGITAL | IOD_EP2 | EP2:.UPS[1].StatusInverterIsOn
EP2UPS1StatusStopOperation | DIGITAL | IOD_EP2 | EP2:.UPS[1].StatusStopOperation
EP2UPS2AlarmAwaitingPower | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmAwaitingPower
EP2UPS2AlarmBypassBad | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmBypassBad
EP2UPS2AlarmChargerFailed | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmChargerFailed
EP2UPS2AlarmCommunicationsLost | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmCommunicationsLost
EP2UPS2AlarmDepletedBattery | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmDepletedBattery
EP2UPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmDiagnosticTestFailed
EP2UPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmIzhodOffKotZahtevano
EP2UPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmIzhodPreobremenjen
EP2UPS2AlarmLowBattery | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmLowBattery
EP2UPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmNapakaNaVarovalki
EP2UPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmNapakaNaVentilatorju
EP2UPS2AlarmOnBattery | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmOnBattery
EP2UPS2AlarmOnBypass | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmOnBypass
EP2UPS2AlarmInverterError | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmInverterError
EP2UPS2AlarmShutdownImminent | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmShutdownImminent
EP2UPS2AlarmShutdownPending | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmShutdownPending
EP2UPS2AlarmSlabaBaterija | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmSlabaBaterija
EP2UPS2AlarmSplosnaNapaka | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmSplosnaNapaka
EP2UPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmStanjeIzhodaIzvenToleranc
EP2UPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmStanjeVhodaIzvenToleranc
EP2UPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmTemperaturaIzvenToleranc
EP2UPS2AlarmTestInProgres | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmTestInProgres
EP2UPS2AlarmUPSIzhodOff | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmUPSIzhodOff
EP2UPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmUPSOffKotZahtevano
EP2UPS2AlarmUPSSystemOff | DIGITAL | IOD_EP2 | EP2:.UPS[2].AlarmUPSSystemOff
EP2UPS2Napaka | DIGITAL | IOD_EP2 | EP2:.UPS[2].Napaka
EP2UPS2StatusEcomodeAktiven | DIGITAL | IOD_EP2 | EP2:.UPS[2].StatusEcomodeAktiven
EP2UPS2StatusInverterIsOn | DIGITAL | IOD_EP2 | EP2:.UPS[2].StatusInverterIsOn
EP2UPS2StatusStopOperation | DIGITAL | IOD_EP2 | EP2:.UPS[2].StatusStopOperation
EP2_UserLoggedIn | DIGITAL | IOD_EP2 | EP2:.UserLoggedIn
EP2_XVH_AlarmOn | DIGITAL | IOD_EP2 | EP2:.XVH_AlarmOn
EP2AlarmGenRest | DIGITAL | IOD_EP2 | EP2:.AlarmGenRest
EP2DI_UpsA_BypassON | DIGITAL | IOD_EP2 | EP2:.DI_UpsA_BypassON
EP2DI_UpsA_ERR | DIGITAL | IOD_EP2 | EP2:.DI_UpsA_ERR
EP2DI_UpsB_BypassON | DIGITAL | IOD_EP2 | EP2:.DI_UpsB_BypassON
EP2DI_UpsB_ERR | DIGITAL | IOD_EP2 | EP2:.DI_UpsB_ERR
EP2DIN_Klima5_ERR | DIGITAL | IOD_EP2 | EP2:.DIN_Klima5_ERR
EP2DIN_Klima6_ERR | DIGITAL | IOD_EP2 | EP2:.DIN_Klima6_ERR
EP2DIN_KlimaSplit1_ERR | DIGITAL | IOD_EP2 | EP2:.DIN_KlimaSplit1_ERR
EP2DIN_Q10_OdcKlima6_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q10_OdcKlima6_IZP
EP2DIN_Q25_OdcUpsA_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q25_OdcUpsA_IZP
EP2DIN_Q26_OdcByA_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q26_OdcByA_IZP
EP2DIN_Q27_OdcByUpsA_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q27_OdcByUpsA_IZP
EP2DIN_Q28_OdcUpsB_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q28_OdcUpsB_IZP
EP2DIN_Q29_OdcByB_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q29_OdcByB_IZP
EP2DIN_Q2_Rezerva_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q2_Rezerva_IZP
EP2DIN_Q30_OdcByUpsB_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q30_OdcByUpsB_IZP
EP2DIN_Q5_OdcKlima1_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q5_OdcKlima1_IZP
EP2DIN_Q6_OdcKlima2_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q6_OdcKlima2_IZP
EP2DIN_Q7_OdcKlima3_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q7_OdcKlima3_IZP
EP2DIN_Q8_OdcKlima4_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q8_OdcKlima4_IZP
EP2DIN_Q9_OdcKlima5_IZP | DIGITAL | IOD_EP2 | EP2:.DIN_Q9_OdcKlima5_IZP
EP2ErrorComCirc1Error | DIGITAL | IOD_EP2 | EP2:.ErrorComCirc[1].Error
EP2ErrorComCirc2Error | DIGITAL | IOD_EP2 | EP2:.ErrorComCirc[2].Error
EP2ErrorComCirc3Error | DIGITAL | IOD_EP2 | EP2:.ErrorComCirc[3].Error
EP2ErrorComCirc4Error | DIGITAL | IOD_EP2 | EP2:.ErrorComCirc[4].Error
EP2ErrorComCirc5Error | DIGITAL | IOD_EP2 | EP2:.ErrorComCirc[5].Error
EP2ErrorComKlima1Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[1].Error
EP2ErrorComKlima2Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[2].Error
EP2ErrorComKlima3Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[3].Error
EP2ErrorComKlima4Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[4].Error
EP2ErrorComKlima5Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[5].Error
EP2ErrorComKlima6Error | DIGITAL | IOD_EP2 | EP2:.ErrorComKlima[6].Error
EP2ErrorComPMM1Error | DIGITAL | IOD_EP2 | EP2:.ErrorComPMM[1].Error
EP2ErrorComPMM2Error | DIGITAL | IOD_EP2 | EP2:.ErrorComPMM[2].Error
EP2ErrorComPMM3Error | DIGITAL | IOD_EP2 | EP2:.ErrorComPMM[3].Error
EP2ErrorComUPS1Error | DIGITAL | IOD_EP2 | EP2:.ErrorComUPS[1].Error
EP2ErrorComUPS2Error | DIGITAL | IOD_EP2 | EP2:.ErrorComUPS[2].Error
EP2KlimaAErrors10 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[10]
EP2KlimaAErrors11 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[11]
EP2KlimaAErrors12 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[12]
EP2KlimaAErrors13 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[13]
EP2KlimaAErrors14 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[14]
EP2KlimaAErrors15 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[15]
EP2KlimaAErrors16 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[16]
EP2KlimaAErrors17 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[17]
EP2KlimaAErrors18 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[18]
EP2KlimaAErrors19 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[19]
EP2KlimaAErrors1 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[1]
EP2KlimaAErrors20 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[20]
EP2KlimaAErrors21 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[21]
EP2KlimaAErrors22 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[22]
EP2KlimaAErrors23 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[23]
EP2KlimaAErrors24 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[24]
EP2KlimaAErrors25 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[25]
EP2KlimaAErrors26 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[26]
EP2KlimaAErrors27 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[27]
EP2KlimaAErrors28 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[28]
EP2KlimaAErrors29 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[29]
EP2KlimaAErrors2 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[2]
EP2KlimaAErrors30 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[30]
EP2KlimaAErrors31 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[31]
EP2KlimaAErrors32 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[32]
EP2KlimaAErrors33 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[33]
EP2KlimaAErrors34 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[34]
EP2KlimaAErrors35 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[35]
EP2KlimaAErrors36 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[36]
EP2KlimaAErrors37 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[37]
EP2KlimaAErrors38 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[38]
EP2KlimaAErrors39 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[39]
EP2KlimaAErrors3 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[3]
EP2KlimaAErrors40 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[40]
EP2KlimaAErrors4 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[4]
EP2KlimaAErrors5 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[5]
EP2KlimaAErrors6 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[6]
EP2KlimaAErrors7 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[7]
EP2KlimaAErrors8 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[8]
EP2KlimaAErrors9 | DIGITAL | IOD_EP2 | EP2:.KlimaAErrors[9]
EP2KlimaBErrors10 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[10]
EP2KlimaBErrors11 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[11]
EP2KlimaBErrors12 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[12]
EP2KlimaBErrors13 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[13]
EP2KlimaBErrors14 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[14]
EP2KlimaBErrors15 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[15]
EP2KlimaBErrors16 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[16]
EP2KlimaBErrors17 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[17]
EP2KlimaBErrors18 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[18]
EP2KlimaBErrors19 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[19]
EP2KlimaBErrors1 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[1]
EP2KlimaBErrors20 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[20]
EP2KlimaBErrors21 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[21]
EP2KlimaBErrors22 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[22]
EP2KlimaBErrors23 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[23]
EP2KlimaBErrors24 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[24]
EP2KlimaBErrors25 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[25]
EP2KlimaBErrors26 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[26]
EP2KlimaBErrors27 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[27]
EP2KlimaBErrors28 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[28]
EP2KlimaBErrors29 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[29]
EP2KlimaBErrors2 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[2]
EP2KlimaBErrors30 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[30]
EP2KlimaBErrors31 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[31]
EP2KlimaBErrors32 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[32]
EP2KlimaBErrors33 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[33]
EP2KlimaBErrors34 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[34]
EP2KlimaBErrors35 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[35]
EP2KlimaBErrors36 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[36]
EP2KlimaBErrors37 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[37]
EP2KlimaBErrors38 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[38]
EP2KlimaBErrors39 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[39]
EP2KlimaBErrors3 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[3]
EP2KlimaBErrors40 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[40]
EP2KlimaBErrors4 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[4]
EP2KlimaBErrors5 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[5]
EP2KlimaBErrors6 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[6]
EP2KlimaBErrors7 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[7]
EP2KlimaBErrors8 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[8]
EP2KlimaBErrors9 | DIGITAL | IOD_EP2 | EP2:.KlimaBErrors[9]
EP2KlimaGalAlarmKompresor1 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.AlarmKompresor1
EP2KlimaGalAlarmKompresor2 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.AlarmKompresor2
EP2KlimaGalDeluje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Deluje
EP2KlimaGalEnergySaving | DIGITAL | IOD_EP2 | EP2:.KlimaGal.EnergySaving
EP2KlimaGalFaultyEPROM | DIGITAL | IOD_EP2 | EP2:.KlimaGal.FaultyEPROM
EP2KlimaGalFenThermalCutout | DIGITAL | IOD_EP2 | EP2:.KlimaGal.FenThermalCutout
EP2KlimaGalGeneralAlarm | DIGITAL | IOD_EP2 | EP2:.KlimaGal.GeneralAlarm
EP2KlimaGalKompresor1naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Kompresor1naMejiObrUr
EP2KlimaGalKompresor2naMejiObrUr | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Kompresor2naMejiObrUr
EP2KlimaGalNapaka | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Napaka
EP2KlimaGalNapakaPriPretokuZraka | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaPriPretokuZraka
EP2KlimaGalNapakaSenzorPovratVode | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaSenzorPovratVode
EP2KlimaGalNapakaSenzorTempIzpiha | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaSenzorTempIzpiha
EP2KlimaGalNapakaSenzorTempProstora | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaSenzorTempProstora
EP2KlimaGalNapakaSenzorVlaznosti | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaSenzorVlaznosti
EP2KlimaGalNapakaSenzorZunanjeTemp | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NapakaSenzorZunanjeTemp
EP2KlimaGalNiTokaVVlazilcu | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NiTokaVVlazilcu
EP2KlimaGalNiVodeVVlazilcu | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NiVodeVVlazilcu
EP2KlimaGalNizekPritiskKompresor1 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NizekPritiskKompresor1
EP2KlimaGalNizekPritiskKompresor2 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NizekPritiskKompresor2
EP2KlimaGalNizkaTempPovratneVode | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NizkaTempPovratneVode
EP2KlimaGalNizkaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NizkaTempVProstoru
EP2KlimaGalNizkaVlaznost | DIGITAL | IOD_EP2 | EP2:.KlimaGal.NizkaVlaznost
EP2KlimaGalOnOffEnablingBySupervisor | DIGITAL | IOD_EP2 | EP2:.KlimaGal.OnOffEnablingBySupervisor
EP2KlimaGalPozarniAlarm | DIGITAL | IOD_EP2 | EP2:.KlimaGal.PozarniAlarm
EP2KlimaGalRazvlazevanje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Razvlazevanje
EP2KlimaGalRemoteOFFtoOutput | DIGITAL | IOD_EP2 | EP2:.KlimaGal.RemoteOFFtoOutput
EP2KlimaGalRemoteOnOff | DIGITAL | IOD_EP2 | EP2:.KlimaGal.RemoteOnOff
EP2KlimaGalRocniIzklop | DIGITAL | IOD_EP2 | EP2:.KlimaGal.RocniIzklop
EP2KlimaGalSenzorjiStatus | DIGITAL | IOD_EP2 | EP2:.KlimaGal.SenzorjiStatus
EP2KlimaGalStoppedByAlarms | DIGITAL | IOD_EP2 | EP2:.KlimaGal.StoppedByAlarms
EP2KlimaGalThermalCutoutHeater1 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.ThermalCutoutHeater1
EP2KlimaGalThermalCutoutHeater2 | DIGITAL | IOD_EP2 | EP2:.KlimaGal.ThermalCutoutHeater2
EP2KlimaGalUnitOnOff | DIGITAL | IOD_EP2 | EP2:.KlimaGal.UnitOnOff
EP2KlimaGalVentilatorNaMejiObrUr | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VentilatorNaMejiObrUr
EP2KlimaGalVentilGretjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VentilGretjeOdpiranje
EP2KlimaGalVentilGretjeZapiranje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VentilGretjeZapiranje
EP2KlimaGalVentilHlajenjeOdpiranje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VentilHlajenjeOdpiranje
EP2KlimaGalVentilHlajenjeZapiranje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VentilHlajenjeZapiranje
EP2KlimaGalVisokaTempPovratneVode | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VisokaTempPovratneVode
EP2KlimaGalVisokaTempVProstoru | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VisokaTempVProstoru
EP2KlimaGalVisokaVlaznost | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VisokaVlaznost
EP2KlimaGalVisokTokVVlazilcu | DIGITAL | IOD_EP2 | EP2:.KlimaGal.VisokTokVVlazilcu
EP2KlimaGalVlazenje | DIGITAL | IOD_EP2 | EP2:.KlimaGal.Vlazenje
EP2KlimaGalZamasenFilter | DIGITAL | IOD_EP2 | EP2:.KlimaGal.ZamasenFilter
EP2PMM1OverVoltage | DIGITAL | IOD_EP2 | EP2:.PMM1OverVoltage
EP2PMM2OverVoltage | DIGITAL | IOD_EP2 | EP2:.PMM2OverVoltage
EP2PMM3OverVoltage | DIGITAL | IOD_EP2 | EP2:.PMM3OverVoltage
EP2PMMgalNapaka | DIGITAL | IOD_EP2 | EP2:.PMMgal.Napaka
EP2ErrCommScada2 | DIGITAL | IOD_EP2 | EP2:.ErrCommScada2
EP2ComSCADA2 | DIGITAL | IOD_EP2 | EP2:.ComSCADA2
EP2ComSCADA3 | DIGITAL | IOD_EP2 | EP2:.ComSCADA3
EP2Circ_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Dnevne_energija_scada1
EP2Circ_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Dnevne_energija_scada2
EP2Circ_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Tedenska_energija_scada1
EP2Circ_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Tedenska_energija_scada2
EP2Circ_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Mesecna_energija_scada1
EP2Circ_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_EP2 | EP2:.Circ_Vpis_Mesecna_energija_scada2
EP2_DateTime_Dan | INT | IOD_EP2 | EP2:.DateTime.Dan | BYTE
EP2_DateTime_Leto | INT | IOD_EP2 | EP2:.DateTime.Leto | BYTE
EP2_DateTime_Mesec | INT | IOD_EP2 | EP2:.DateTime.Mesec | BYTE
EP2_DateTime_Minuta | INT | IOD_EP2 | EP2:.DateTime.Minuta | BYTE
EP2_DateTime_Sekunda | INT | IOD_EP2 | EP2:.DateTime.Sekunda | BYTE
EP2_DateTime_Ura | INT | IOD_EP2 | EP2:.DateTime.Ura | BYTE
EP2_Klima1_GrelecStatus | INT | IOD_EP2 | EP2:.Klima[1].GrelecStatus | BYTE
EP2_Klima1_IzhodniVentStatus | INT | IOD_EP2 | EP2:.Klima[1].IzhodniVentStatus | BYTE
EP2_Klima1_KompresorStatus | INT | IOD_EP2 | EP2:.Klima[1].KompresorStatus | BYTE
EP2_Klima1_VlazilecStatus | INT | IOD_EP2 | EP2:.Klima[1].VlazilecStatus | BYTE
EP2_Klima2_GrelecStatus | INT | IOD_EP2 | EP2:.Klima[2].GrelecStatus | BYTE
EP2_Klima2_IzhodniVentStatus | INT | IOD_EP2 | EP2:.Klima[2].IzhodniVentStatus | BYTE
EP2_Klima2_KompresorStatus | INT | IOD_EP2 | EP2:.Klima[2].KompresorStatus | BYTE
EP2_Klima2_VlazilecStatus | INT | IOD_EP2 | EP2:.Klima[2].VlazilecStatus | BYTE
EP2_PMM1_AlarmPhase1_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C01_16_60to80
EP2_PMM1_AlarmPhase1_C01_16_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C01_16_over80
EP2_PMM1_AlarmPhase1_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C17_32_60to80
EP2_PMM1_AlarmPhase1_C17_32_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C17_32_over80
EP2_PMM1_AlarmPhase1_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C33_42_60to80
EP2_PMM1_AlarmPhase1_C33_42_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].C33_42_over80
EP2_PMM1_AlarmPhase1_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[1].GlobalAlarmReg
EP2_PMM1_AlarmPhase2_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C01_16_60to80
EP2_PMM1_AlarmPhase2_C01_16_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C01_16_over80
EP2_PMM1_AlarmPhase2_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C17_32_60to80
EP2_PMM1_AlarmPhase2_C17_32_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C17_32_over80
EP2_PMM1_AlarmPhase2_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C33_42_60to80
EP2_PMM1_AlarmPhase2_C33_42_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].C33_42_over80
EP2_PMM1_AlarmPhase2_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[2].GlobalAlarmReg
EP2_PMM1_AlarmPhase3_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C01_16_60to80
EP2_PMM1_AlarmPhase3_C01_16_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C01_16_over80
EP2_PMM1_AlarmPhase3_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C17_32_60to80
EP2_PMM1_AlarmPhase3_C17_32_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C17_32_over80
EP2_PMM1_AlarmPhase3_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C33_42_60to80
EP2_PMM1_AlarmPhase3_C33_42_over | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].C33_42_over80
EP2_PMM1_AlarmPhase3_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[1].AlarmPhase[3].GlobalAlarmReg
EP2_PMM1_Alarms | INT | IOD_EP2 | EP2:.PMM[1].Alarms
EP2_PMM2_AlarmPhase1_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C01_16_60to80
EP2_PMM2_AlarmPhase1_C01_16_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C01_16_over80
EP2_PMM2_AlarmPhase1_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C17_32_60to80
EP2_PMM2_AlarmPhase1_C17_32_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C17_32_over80
EP2_PMM2_AlarmPhase1_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C33_42_60to80
EP2_PMM2_AlarmPhase1_C33_42_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].C33_42_over80
EP2_PMM2_AlarmPhase1_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[1].GlobalAlarmReg
EP2_PMM2_AlarmPhase2_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C01_16_60to80
EP2_PMM2_AlarmPhase2_C01_16_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C01_16_over80
EP2_PMM2_AlarmPhase2_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C17_32_60to80
EP2_PMM2_AlarmPhase2_C17_32_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C17_32_over80
EP2_PMM2_AlarmPhase2_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C33_42_60to80
EP2_PMM2_AlarmPhase2_C33_42_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].C33_42_over80
EP2_PMM2_AlarmPhase2_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[2].GlobalAlarmReg
EP2_PMM2_AlarmPhase3_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C01_16_60to80
EP2_PMM2_AlarmPhase3_C01_16_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C01_16_over80
EP2_PMM2_AlarmPhase3_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C17_32_60to80
EP2_PMM2_AlarmPhase3_C17_32_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C17_32_over80
EP2_PMM2_AlarmPhase3_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C33_42_60to80
EP2_PMM2_AlarmPhase3_C33_42_over | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].C33_42_over80
EP2_PMM2_AlarmPhase3_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[2].AlarmPhase[3].GlobalAlarmReg
EP2_PMM2_Alarms | INT | IOD_EP2 | EP2:.PMM[2].Alarms
EP2_PMM3_AlarmPhase1_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C01_16_60to80
EP2_PMM3_AlarmPhase1_C01_16_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C01_16_over80
EP2_PMM3_AlarmPhase1_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C17_32_60to80
EP2_PMM3_AlarmPhase1_C17_32_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C17_32_over80
EP2_PMM3_AlarmPhase1_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C33_42_60to80
EP2_PMM3_AlarmPhase1_C33_42_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].C33_42_over80
EP2_PMM3_AlarmPhase1_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[1].GlobalAlarmReg
EP2_PMM3_AlarmPhase2_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C01_16_60to80
EP2_PMM3_AlarmPhase2_C01_16_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C01_16_over80
EP2_PMM3_AlarmPhase2_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C17_32_60to80
EP2_PMM3_AlarmPhase2_C17_32_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C17_32_over80
EP2_PMM3_AlarmPhase2_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C33_42_60to80
EP2_PMM3_AlarmPhase2_C33_42_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].C33_42_over80
EP2_PMM3_AlarmPhase2_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[2].GlobalAlarmReg
EP2_PMM3_AlarmPhase3_C01_16_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C01_16_60to80
EP2_PMM3_AlarmPhase3_C01_16_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C01_16_over80
EP2_PMM3_AlarmPhase3_C17_32_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C17_32_60to80
EP2_PMM3_AlarmPhase3_C17_32_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C17_32_over80
EP2_PMM3_AlarmPhase3_C33_42_60to | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C33_42_60to80
EP2_PMM3_AlarmPhase3_C33_42_over | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].C33_42_over80
EP2_PMM3_AlarmPhase3_GlobalAlarm | INT | IOD_EP2 | EP2:.PMM[3].AlarmPhase[3].GlobalAlarmReg
EP2_PMM3_Alarms | INT | IOD_EP2 | EP2:.PMM[3].Alarms
EP2UPS1InverterStatus | INT | IOD_EP2 | EP2:.UPS[1].InverterStatus
EP2UPS1OutputStatus | INT | IOD_EP2 | EP2:.UPS[1].OutputStatus
EP2UPS1StatusBaterije | INT | IOD_EP2 | EP2:.UPS[1].StatusBaterije
EP2UPS1SteviloIzpadovVhodneLinije | INT | IOD_EP2 | EP2:.UPS[1].SteviloIzpadovVhodneLinije
EP2UPS1UnitStatus | INT | IOD_EP2 | EP2:.UPS[1].UnitStatus
EP2UPS2InverterStatus | INT | IOD_EP2 | EP2:.UPS[2].InverterStatus
EP2UPS2OutputStatus | INT | IOD_EP2 | EP2:.UPS[2].OutputStatus
EP2UPS2StatusBaterije | INT | IOD_EP2 | EP2:.UPS[2].StatusBaterije
EP2UPS2SteviloIzpadovVhodneLinije | INT | IOD_EP2 | EP2:.UPS[2].SteviloIzpadovVhodneLinije
EP2UPS2UnitStatus | INT | IOD_EP2 | EP2:.UPS[2].UnitStatus
EP2_UserCurrentLevel | INT | IOD_EP2 | EP2:.UserCurrentLevel | BYTE
EP2ErrorComCirc1Code10 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[10] | BYTE
EP2ErrorComCirc1Code11 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[11] | BYTE
EP2ErrorComCirc1Code12 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[12] | BYTE
EP2ErrorComCirc1Code13 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[13] | BYTE
EP2ErrorComCirc1Code14 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[14] | BYTE
EP2ErrorComCirc1Code15 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[15] | BYTE
EP2ErrorComCirc1Code1 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[1] | BYTE
EP2ErrorComCirc1Code2 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[2] | BYTE
EP2ErrorComCirc1Code3 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[3] | BYTE
EP2ErrorComCirc1Code4 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[4] | BYTE
EP2ErrorComCirc1Code5 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[5] | BYTE
EP2ErrorComCirc1Code6 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[6] | BYTE
EP2ErrorComCirc1Code7 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[7] | BYTE
EP2ErrorComCirc1Code8 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[8] | BYTE
EP2ErrorComCirc1Code9 | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Code[9] | BYTE
EP2ErrorComCirc1Status | INT | IOD_EP2 | EP2:.ErrorComCirc[1].Status
EP2ErrorComCirc2Code10 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[10] | BYTE
EP2ErrorComCirc2Code11 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[11] | BYTE
EP2ErrorComCirc2Code12 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[12] | BYTE
EP2ErrorComCirc2Code13 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[13] | BYTE
EP2ErrorComCirc2Code14 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[14] | BYTE
EP2ErrorComCirc2Code15 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[15] | BYTE
EP2ErrorComCirc2Code1 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[1] | BYTE
EP2ErrorComCirc2Code2 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[2] | BYTE
EP2ErrorComCirc2Code3 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[3] | BYTE
EP2ErrorComCirc2Code4 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[4] | BYTE
EP2ErrorComCirc2Code5 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[5] | BYTE
EP2ErrorComCirc2Code6 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[6] | BYTE
EP2ErrorComCirc2Code7 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[7] | BYTE
EP2ErrorComCirc2Code8 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[8] | BYTE
EP2ErrorComCirc2Code9 | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Code[9] | BYTE
EP2ErrorComCirc2Status | INT | IOD_EP2 | EP2:.ErrorComCirc[2].Status
EP2ErrorComCirc3Code10 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[10] | BYTE
EP2ErrorComCirc3Code11 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[11] | BYTE
EP2ErrorComCirc3Code12 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[12] | BYTE
EP2ErrorComCirc3Code13 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[13] | BYTE
EP2ErrorComCirc3Code14 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[14] | BYTE
EP2ErrorComCirc3Code15 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[15] | BYTE
EP2ErrorComCirc3Code1 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[1] | BYTE
EP2ErrorComCirc3Code2 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[2] | BYTE
EP2ErrorComCirc3Code3 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[3] | BYTE
EP2ErrorComCirc3Code4 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[4] | BYTE
EP2ErrorComCirc3Code5 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[5] | BYTE
EP2ErrorComCirc3Code6 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[6] | BYTE
EP2ErrorComCirc3Code7 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[7] | BYTE
EP2ErrorComCirc3Code8 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[8] | BYTE
EP2ErrorComCirc3Code9 | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Code[9] | BYTE
EP2ErrorComCirc3Status | INT | IOD_EP2 | EP2:.ErrorComCirc[3].Status
EP2ErrorComCirc4Code10 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[10] | BYTE
EP2ErrorComCirc4Code11 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[11] | BYTE
EP2ErrorComCirc4Code12 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[12] | BYTE
EP2ErrorComCirc4Code13 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[13] | BYTE
EP2ErrorComCirc4Code14 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[14] | BYTE
EP2ErrorComCirc4Code15 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[15] | BYTE
EP2ErrorComCirc4Code1 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[1] | BYTE
EP2ErrorComCirc4Code2 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[2] | BYTE
EP2ErrorComCirc4Code3 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[3] | BYTE
EP2ErrorComCirc4Code4 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[4] | BYTE
EP2ErrorComCirc4Code5 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[5] | BYTE
EP2ErrorComCirc4Code6 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[6] | BYTE
EP2ErrorComCirc4Code7 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[7] | BYTE
EP2ErrorComCirc4Code8 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[8] | BYTE
EP2ErrorComCirc4Code9 | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Code[9] | BYTE
EP2ErrorComCirc4Status | INT | IOD_EP2 | EP2:.ErrorComCirc[4].Status
EP2ErrorComCirc5Code10 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[10] | BYTE
EP2ErrorComCirc5Code11 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[11] | BYTE
EP2ErrorComCirc5Code12 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[12] | BYTE
EP2ErrorComCirc5Code13 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[13] | BYTE
EP2ErrorComCirc5Code14 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[14] | BYTE
EP2ErrorComCirc5Code15 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[15] | BYTE
EP2ErrorComCirc5Code1 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[1] | BYTE
EP2ErrorComCirc5Code2 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[2] | BYTE
EP2ErrorComCirc5Code3 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[3] | BYTE
EP2ErrorComCirc5Code4 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[4] | BYTE
EP2ErrorComCirc5Code5 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[5] | BYTE
EP2ErrorComCirc5Code6 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[6] | BYTE
EP2ErrorComCirc5Code7 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[7] | BYTE
EP2ErrorComCirc5Code8 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[8] | BYTE
EP2ErrorComCirc5Code9 | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Code[9] | BYTE
EP2ErrorComCirc5Status | INT | IOD_EP2 | EP2:.ErrorComCirc[5].Status
EP2ErrorComKlima1Code10 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[10] | BYTE
EP2ErrorComKlima1Code11 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[11] | BYTE
EP2ErrorComKlima1Code12 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[12] | BYTE
EP2ErrorComKlima1Code13 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[13] | BYTE
EP2ErrorComKlima1Code14 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[14] | BYTE
EP2ErrorComKlima1Code15 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[15] | BYTE
EP2ErrorComKlima1Code1 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[1] | BYTE
EP2ErrorComKlima1Code2 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[2] | BYTE
EP2ErrorComKlima1Code3 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[3] | BYTE
EP2ErrorComKlima1Code4 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[4] | BYTE
EP2ErrorComKlima1Code5 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[5] | BYTE
EP2ErrorComKlima1Code6 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[6] | BYTE
EP2ErrorComKlima1Code7 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[7] | BYTE
EP2ErrorComKlima1Code8 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[8] | BYTE
EP2ErrorComKlima1Code9 | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Code[9] | BYTE
EP2ErrorComKlima1Status | INT | IOD_EP2 | EP2:.ErrorComKlima[1].Status
EP2ErrorComKlima2Code10 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[10] | BYTE
EP2ErrorComKlima2Code11 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[11] | BYTE
EP2ErrorComKlima2Code12 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[12] | BYTE
EP2ErrorComKlima2Code13 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[13] | BYTE
EP2ErrorComKlima2Code14 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[14] | BYTE
EP2ErrorComKlima2Code15 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[15] | BYTE
EP2ErrorComKlima2Code1 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[1] | BYTE
EP2ErrorComKlima2Code2 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[2] | BYTE
EP2ErrorComKlima2Code3 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[3] | BYTE
EP2ErrorComKlima2Code4 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[4] | BYTE
EP2ErrorComKlima2Code5 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[5] | BYTE
EP2ErrorComKlima2Code6 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[6] | BYTE
EP2ErrorComKlima2Code7 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[7] | BYTE
EP2ErrorComKlima2Code8 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[8] | BYTE
EP2ErrorComKlima2Code9 | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Code[9] | BYTE
EP2ErrorComKlima2Status | INT | IOD_EP2 | EP2:.ErrorComKlima[2].Status
EP2ErrorComKlima3Code10 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[10] | BYTE
EP2ErrorComKlima3Code11 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[11] | BYTE
EP2ErrorComKlima3Code12 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[12] | BYTE
EP2ErrorComKlima3Code13 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[13] | BYTE
EP2ErrorComKlima3Code14 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[14] | BYTE
EP2ErrorComKlima3Code15 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[15] | BYTE
EP2ErrorComKlima3Code1 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[1] | BYTE
EP2ErrorComKlima3Code2 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[2] | BYTE
EP2ErrorComKlima3Code3 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[3] | BYTE
EP2ErrorComKlima3Code4 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[4] | BYTE
EP2ErrorComKlima3Code5 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[5] | BYTE
EP2ErrorComKlima3Code6 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[6] | BYTE
EP2ErrorComKlima3Code7 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[7] | BYTE
EP2ErrorComKlima3Code8 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[8] | BYTE
EP2ErrorComKlima3Code9 | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Code[9] | BYTE
EP2ErrorComKlima3Status | INT | IOD_EP2 | EP2:.ErrorComKlima[3].Status
EP2ErrorComKlima4Code10 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[10] | BYTE
EP2ErrorComKlima4Code11 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[11] | BYTE
EP2ErrorComKlima4Code12 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[12] | BYTE
EP2ErrorComKlima4Code13 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[13] | BYTE
EP2ErrorComKlima4Code14 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[14] | BYTE
EP2ErrorComKlima4Code15 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[15] | BYTE
EP2ErrorComKlima4Code1 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[1] | BYTE
EP2ErrorComKlima4Code2 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[2] | BYTE
EP2ErrorComKlima4Code3 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[3] | BYTE
EP2ErrorComKlima4Code4 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[4] | BYTE
EP2ErrorComKlima4Code5 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[5] | BYTE
EP2ErrorComKlima4Code6 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[6] | BYTE
EP2ErrorComKlima4Code7 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[7] | BYTE
EP2ErrorComKlima4Code8 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[8] | BYTE
EP2ErrorComKlima4Code9 | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Code[9] | BYTE
EP2ErrorComKlima4Status | INT | IOD_EP2 | EP2:.ErrorComKlima[4].Status
EP2ErrorComKlima5Code10 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[10] | BYTE
EP2ErrorComKlima5Code11 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[11] | BYTE
EP2ErrorComKlima5Code12 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[12] | BYTE
EP2ErrorComKlima5Code13 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[13] | BYTE
EP2ErrorComKlima5Code14 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[14] | BYTE
EP2ErrorComKlima5Code15 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[15] | BYTE
EP2ErrorComKlima5Code1 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[1] | BYTE
EP2ErrorComKlima5Code2 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[2] | BYTE
EP2ErrorComKlima5Code3 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[3] | BYTE
EP2ErrorComKlima5Code4 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[4] | BYTE
EP2ErrorComKlima5Code5 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[5] | BYTE
EP2ErrorComKlima5Code6 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[6] | BYTE
EP2ErrorComKlima5Code7 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[7] | BYTE
EP2ErrorComKlima5Code8 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[8] | BYTE
EP2ErrorComKlima5Code9 | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Code[9] | BYTE
EP2ErrorComKlima5Status | INT | IOD_EP2 | EP2:.ErrorComKlima[5].Status
EP2ErrorComKlima6Code10 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[10] | BYTE
EP2ErrorComKlima6Code11 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[11] | BYTE
EP2ErrorComKlima6Code12 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[12] | BYTE
EP2ErrorComKlima6Code13 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[13] | BYTE
EP2ErrorComKlima6Code14 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[14] | BYTE
EP2ErrorComKlima6Code15 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[15] | BYTE
EP2ErrorComKlima6Code1 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[1] | BYTE
EP2ErrorComKlima6Code2 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[2] | BYTE
EP2ErrorComKlima6Code3 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[3] | BYTE
EP2ErrorComKlima6Code4 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[4] | BYTE
EP2ErrorComKlima6Code5 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[5] | BYTE
EP2ErrorComKlima6Code6 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[6] | BYTE
EP2ErrorComKlima6Code7 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[7] | BYTE
EP2ErrorComKlima6Code8 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[8] | BYTE
EP2ErrorComKlima6Code9 | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Code[9] | BYTE
EP2ErrorComKlima6Status | INT | IOD_EP2 | EP2:.ErrorComKlima[6].Status
EP2ErrorComPMM1Code10 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[10] | BYTE
EP2ErrorComPMM1Code11 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[11] | BYTE
EP2ErrorComPMM1Code12 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[12] | BYTE
EP2ErrorComPMM1Code13 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[13] | BYTE
EP2ErrorComPMM1Code14 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[14] | BYTE
EP2ErrorComPMM1Code15 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[15] | BYTE
EP2ErrorComPMM1Code1 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[1] | BYTE
EP2ErrorComPMM1Code2 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[2] | BYTE
EP2ErrorComPMM1Code3 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[3] | BYTE
EP2ErrorComPMM1Code4 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[4] | BYTE
EP2ErrorComPMM1Code5 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[5] | BYTE
EP2ErrorComPMM1Code6 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[6] | BYTE
EP2ErrorComPMM1Code7 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[7] | BYTE
EP2ErrorComPMM1Code8 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[8] | BYTE
EP2ErrorComPMM1Code9 | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Code[9] | BYTE
EP2ErrorComPMM1Status | INT | IOD_EP2 | EP2:.ErrorComPMM[1].Status
EP2ErrorComPMM2Code10 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[10] | BYTE
EP2ErrorComPMM2Code11 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[11] | BYTE
EP2ErrorComPMM2Code12 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[12] | BYTE
EP2ErrorComPMM2Code13 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[13] | BYTE
EP2ErrorComPMM2Code14 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[14] | BYTE
EP2ErrorComPMM2Code15 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[15] | BYTE
EP2ErrorComPMM2Code1 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[1] | BYTE
EP2ErrorComPMM2Code2 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[2] | BYTE
EP2ErrorComPMM2Code3 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[3] | BYTE
EP2ErrorComPMM2Code4 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[4] | BYTE
EP2ErrorComPMM2Code5 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[5] | BYTE
EP2ErrorComPMM2Code6 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[6] | BYTE
EP2ErrorComPMM2Code7 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[7] | BYTE
EP2ErrorComPMM2Code8 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[8] | BYTE
EP2ErrorComPMM2Code9 | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Code[9] | BYTE
EP2ErrorComPMM2Status | INT | IOD_EP2 | EP2:.ErrorComPMM[2].Status
EP2ErrorComPMM3Code10 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[10] | BYTE
EP2ErrorComPMM3Code11 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[11] | BYTE
EP2ErrorComPMM3Code12 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[12] | BYTE
EP2ErrorComPMM3Code13 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[13] | BYTE
EP2ErrorComPMM3Code14 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[14] | BYTE
EP2ErrorComPMM3Code15 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[15] | BYTE
EP2ErrorComPMM3Code1 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[1] | BYTE
EP2ErrorComPMM3Code2 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[2] | BYTE
EP2ErrorComPMM3Code3 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[3] | BYTE
EP2ErrorComPMM3Code4 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[4] | BYTE
EP2ErrorComPMM3Code5 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[5] | BYTE
EP2ErrorComPMM3Code6 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[6] | BYTE
EP2ErrorComPMM3Code7 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[7] | BYTE
EP2ErrorComPMM3Code8 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[8] | BYTE
EP2ErrorComPMM3Code9 | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Code[9] | BYTE
EP2ErrorComPMM3Status | INT | IOD_EP2 | EP2:.ErrorComPMM[3].Status
EP2ErrorComUPS1Code10 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[10] | BYTE
EP2ErrorComUPS1Code11 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[11] | BYTE
EP2ErrorComUPS1Code12 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[12] | BYTE
EP2ErrorComUPS1Code13 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[13] | BYTE
EP2ErrorComUPS1Code14 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[14] | BYTE
EP2ErrorComUPS1Code15 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[15] | BYTE
EP2ErrorComUPS1Code1 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[1] | BYTE
EP2ErrorComUPS1Code2 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[2] | BYTE
EP2ErrorComUPS1Code3 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[3] | BYTE
EP2ErrorComUPS1Code4 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[4] | BYTE
EP2ErrorComUPS1Code5 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[5] | BYTE
EP2ErrorComUPS1Code6 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[6] | BYTE
EP2ErrorComUPS1Code7 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[7] | BYTE
EP2ErrorComUPS1Code8 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[8] | BYTE
EP2ErrorComUPS1Code9 | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Code[9] | BYTE
EP2ErrorComUPS1Status | INT | IOD_EP2 | EP2:.ErrorComUPS[1].Status
EP2ErrorComUPS2Code10 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[10] | BYTE
EP2ErrorComUPS2Code11 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[11] | BYTE
EP2ErrorComUPS2Code12 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[12] | BYTE
EP2ErrorComUPS2Code13 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[13] | BYTE
EP2ErrorComUPS2Code14 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[14] | BYTE
EP2ErrorComUPS2Code15 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[15] | BYTE
EP2ErrorComUPS2Code1 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[1] | BYTE
EP2ErrorComUPS2Code2 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[2] | BYTE
EP2ErrorComUPS2Code3 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[3] | BYTE
EP2ErrorComUPS2Code4 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[4] | BYTE
EP2ErrorComUPS2Code5 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[5] | BYTE
EP2ErrorComUPS2Code6 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[6] | BYTE
EP2ErrorComUPS2Code7 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[7] | BYTE
EP2ErrorComUPS2Code8 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[8] | BYTE
EP2ErrorComUPS2Code9 | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Code[9] | BYTE
EP2ErrorComUPS2Status | INT | IOD_EP2 | EP2:.ErrorComUPS[2].Status
EP2KlimaGalGrelecStatus | INT | IOD_EP2 | EP2:.KlimaGal.GrelecStatus | BYTE
EP2KlimaGalIzhodniVentStatus | INT | IOD_EP2 | EP2:.KlimaGal.IzhodniVentStatus | BYTE
EP2KlimaGalKompresorStatus | INT | IOD_EP2 | EP2:.KlimaGal.KompresorStatus | BYTE
EP2KlimaGalVlazilecStatus | INT | IOD_EP2 | EP2:.KlimaGal.VlazilecStatus | BYTE
EP2PMMgalAlarmPhase1GlobalAlarmReg | INT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].GlobalAlarmReg
EP2PMMgalAlarmPhase2GlobalAlarmReg | INT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].GlobalAlarmReg
EP2PMMgalAlarmPhase3GlobalAlarmReg | INT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].GlobalAlarmReg
EP2kom_nast_cas_izpada | INT | IOD_EP2 | EP2:.kom_nast_cas_izpada
EP2_Circ1_CosFi_III | REAL | IOD_EP2 | EP2:.Circ[1].CosFi_III
EP2_Circ1_DelovnaEnergija | REAL | IOD_EP2 | EP2:.Circ[1].DelovnaEnergija
EP2_Circ1_DelovnaMoc_III | REAL | IOD_EP2 | EP2:.Circ[1].DelovnaMoc_III
EP2_Circ1_DelovnaMoc_L1 | REAL | IOD_EP2 | EP2:.Circ[1].DelovnaMoc_L1
EP2_Circ1_DelovnaMoc_L2 | REAL | IOD_EP2 | EP2:.Circ[1].DelovnaMoc_L2
EP2_Circ1_DelovnaMoc_L3 | REAL | IOD_EP2 | EP2:.Circ[1].DelovnaMoc_L3
EP2_Circ1_Frekvenca_L1 | REAL | IOD_EP2 | EP2:.Circ[1].Frekvenca_L1
EP2_Circ1_InduktivnaEnergija | REAL | IOD_EP2 | EP2:.Circ[1].InduktivnaEnergija
EP2_Circ1_InduktivnaMoc_III | REAL | IOD_EP2 | EP2:.Circ[1].InduktivnaMoc_III
EP2_Circ1_JalovaMoc_L1 | REAL | IOD_EP2 | EP2:.Circ[1].JalovaMoc_L1
EP2_Circ1_JalovaMoc_L2 | REAL | IOD_EP2 | EP2:.Circ[1].JalovaMoc_L2
EP2_Circ1_JalovaMoc_L3 | REAL | IOD_EP2 | EP2:.Circ[1].JalovaMoc_L3
EP2_Circ1_KapacitivnaEnergija | REAL | IOD_EP2 | EP2:.Circ[1].KapacitivnaEnergija
EP2_Circ1_KapacitivnaMoc_III | REAL | IOD_EP2 | EP2:.Circ[1].KapacitivnaMoc_III
EP2_Circ1_MaximumDemand | REAL | IOD_EP2 | EP2:.Circ[1].MaximumDemand
EP2_Circ1_Napetost_L1_L2 | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L1_L2
EP2_Circ1_Napetost_L1_N | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L1_N
EP2_Circ1_Napetost_L2_L3 | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L2_L3
EP2_Circ1_Napetost_L2_N | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L2_N
EP2_Circ1_Napetost_L3_L1 | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L3_L1
EP2_Circ1_Napetost_L3_N | REAL | IOD_EP2 | EP2:.Circ[1].Napetost_L3_N
EP2_Circ1_NavideznaMoc_III | REAL | IOD_EP2 | EP2:.Circ[1].NavideznaMoc_III
EP2_Circ1_NicelniTok | REAL | IOD_EP2 | EP2:.Circ[1].NicelniTok
EP2_Circ1_PowerFactor_III | REAL | IOD_EP2 | EP2:.Circ[1].PowerFactor_III
EP2_Circ1_PowerFactor_L1 | REAL | IOD_EP2 | EP2:.Circ[1].PowerFactor_L1
EP2_Circ1_PowerFactor_L2 | REAL | IOD_EP2 | EP2:.Circ[1].PowerFactor_L2
EP2_Circ1_PowerFactor_L3 | REAL | IOD_EP2 | EP2:.Circ[1].PowerFactor_L3
EP2_Circ1_THDI_L1 | REAL | IOD_EP2 | EP2:.Circ[1].THDI_L1
EP2_Circ1_THDI_L2 | REAL | IOD_EP2 | EP2:.Circ[1].THDI_L2
EP2_Circ1_THDI_L3 | REAL | IOD_EP2 | EP2:.Circ[1].THDI_L3
EP2_Circ1_THDV_L1 | REAL | IOD_EP2 | EP2:.Circ[1].THDV_L1
EP2_Circ1_THDV_L2 | REAL | IOD_EP2 | EP2:.Circ[1].THDV_L2
EP2_Circ1_THDV_L3 | REAL | IOD_EP2 | EP2:.Circ[1].THDV_L3
EP2_Circ1_Tok_L1 | REAL | IOD_EP2 | EP2:.Circ[1].Tok_L1
EP2_Circ1_Tok_L2 | REAL | IOD_EP2 | EP2:.Circ[1].Tok_L2
EP2_Circ1_Tok_L3 | REAL | IOD_EP2 | EP2:.Circ[1].Tok_L3
EP2_Circ1_TokPovprecje_III | REAL | IOD_EP2 | EP2:.Circ[1].TokPovprecje_III
EP2_Circutor_CosFi_III | REAL | IOD_EP2 | EP2:.Circutor.CosFi_III
EP2_Circutor_DelovnaEnergija | REAL | IOD_EP2 | EP2:.Circutor.DelovnaEnergija
EP2_Circutor_DelovnaMoc_III | REAL | IOD_EP2 | EP2:.Circutor.DelovnaMoc_III
EP2_Circutor_DelovnaMoc_L1 | REAL | IOD_EP2 | EP2:.Circutor.DelovnaMoc_L1
EP2_Circutor_DelovnaMoc_L2 | REAL | IOD_EP2 | EP2:.Circutor.DelovnaMoc_L2
EP2_Circutor_DelovnaMoc_L3 | REAL | IOD_EP2 | EP2:.Circutor.DelovnaMoc_L3
EP2_Circutor_Frekvenca_L1 | REAL | IOD_EP2 | EP2:.Circutor.Frekvenca_L1
EP2_Circutor_InduktivnaEnergija | REAL | IOD_EP2 | EP2:.Circutor.InduktivnaEnergija
EP2_Circutor_InduktivnaMoc_III | REAL | IOD_EP2 | EP2:.Circutor.InduktivnaMoc_III
EP2_Circutor_JalovaMoc_L1 | REAL | IOD_EP2 | EP2:.Circutor.JalovaMoc_L1
EP2_Circutor_JalovaMoc_L2 | REAL | IOD_EP2 | EP2:.Circutor.JalovaMoc_L2
EP2_Circutor_JalovaMoc_L3 | REAL | IOD_EP2 | EP2:.Circutor.JalovaMoc_L3
EP2_Circutor_KapacitivnaEnergija | REAL | IOD_EP2 | EP2:.Circutor.KapacitivnaEnergija
EP2_Circutor_KapacitivnaMoc_III | REAL | IOD_EP2 | EP2:.Circutor.KapacitivnaMoc_III
EP2_Circutor_MaximumDemand | REAL | IOD_EP2 | EP2:.Circutor.MaximumDemand
EP2_Circutor_Napetost_L1_L2 | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L1_L2
EP2_Circutor_Napetost_L1_N | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L1_N
EP2_Circutor_Napetost_L2_L3 | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L2_L3
EP2_Circutor_Napetost_L2_N | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L2_N
EP2_Circutor_Napetost_L3_L1 | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L3_L1
EP2_Circutor_Napetost_L3_N | REAL | IOD_EP2 | EP2:.Circutor.Napetost_L3_N
EP2_Circutor_NavideznaMoc_III | REAL | IOD_EP2 | EP2:.Circutor.NavideznaMoc_III
EP2_Circutor_NicelniTok | REAL | IOD_EP2 | EP2:.Circutor.NicelniTok
EP2_Circutor_PowerFactor_III | REAL | IOD_EP2 | EP2:.Circutor.PowerFactor_III
EP2_Circutor_PowerFactor_L1 | REAL | IOD_EP2 | EP2:.Circutor.PowerFactor_L1
EP2_Circutor_PowerFactor_L2 | REAL | IOD_EP2 | EP2:.Circutor.PowerFactor_L2
EP2_Circutor_PowerFactor_L3 | REAL | IOD_EP2 | EP2:.Circutor.PowerFactor_L3
EP2_Circutor_THDI_L1 | REAL | IOD_EP2 | EP2:.Circutor.THDI_L1
EP2_Circutor_THDI_L2 | REAL | IOD_EP2 | EP2:.Circutor.THDI_L2
EP2_Circutor_THDI_L3 | REAL | IOD_EP2 | EP2:.Circutor.THDI_L3
EP2_Circutor_THDV_L1 | REAL | IOD_EP2 | EP2:.Circutor.THDV_L1
EP2_Circutor_THDV_L2 | REAL | IOD_EP2 | EP2:.Circutor.THDV_L2
EP2_Circutor_THDV_L3 | REAL | IOD_EP2 | EP2:.Circutor.THDV_L3
EP2_Circutor_Tok_L1 | REAL | IOD_EP2 | EP2:.Circutor.Tok_L1
EP2_Circutor_Tok_L2 | REAL | IOD_EP2 | EP2:.Circutor.Tok_L2
EP2_Circutor_Tok_L3 | REAL | IOD_EP2 | EP2:.Circutor.Tok_L3
EP2_Circutor_TokPovprecje_III | REAL | IOD_EP2 | EP2:.Circutor.TokPovprecje_III
EP2_Klima1_NastMaxTemp | REAL | IOD_EP2 | EP2:.Klima[1].NastMaxTemp
EP2_Klima1_NastMaxVlaznost | REAL | IOD_EP2 | EP2:.Klima[1].NastMaxVlaznost
EP2_Klima1_NastMinTemp | REAL | IOD_EP2 | EP2:.Klima[1].NastMinTemp
EP2_Klima1_NastMinVlaznost | REAL | IOD_EP2 | EP2:.Klima[1].NastMinVlaznost
EP2_Klima1_NastTempProstora | REAL | IOD_EP2 | EP2:.Klima[1].NastTempProstora
EP2_Klima1_NastVlaznost | REAL | IOD_EP2 | EP2:.Klima[1].NastVlaznost
EP2_Klima1_ObratovalneUre | REAL | IOD_EP2 | EP2:.Klima[1].ObratovalneUre
EP2_Klima1_TemperaturaProstora | REAL | IOD_EP2 | EP2:.Klima[1].TemperaturaProstora
EP2_Klima1_TempIzpihanegaZraka | REAL | IOD_EP2 | EP2:.Klima[1].TempIzpihanegaZraka
EP2_Klima1_TempPovratneVode | REAL | IOD_EP2 | EP2:.Klima[1].TempPovratneVode
EP2_Klima1_VlaznostProstora | REAL | IOD_EP2 | EP2:.Klima[1].VlaznostProstora
EP2_Klima1_ZunanjaTemp | REAL | IOD_EP2 | EP2:.Klima[1].ZunanjaTemp
EP2_Klima2_NastMaxTemp | REAL | IOD_EP2 | EP2:.Klima[2].NastMaxTemp
EP2_Klima2_NastMaxVlaznost | REAL | IOD_EP2 | EP2:.Klima[2].NastMaxVlaznost
EP2_Klima2_NastMinTemp | REAL | IOD_EP2 | EP2:.Klima[2].NastMinTemp
EP2_Klima2_NastMinVlaznost | REAL | IOD_EP2 | EP2:.Klima[2].NastMinVlaznost
EP2_Klima2_NastTempProstora | REAL | IOD_EP2 | EP2:.Klima[2].NastTempProstora
EP2_Klima2_NastVlaznost | REAL | IOD_EP2 | EP2:.Klima[2].NastVlaznost
EP2_Klima2_ObratovalneUre | REAL | IOD_EP2 | EP2:.Klima[2].ObratovalneUre
EP2_Klima2_TemperaturaProstora | REAL | IOD_EP2 | EP2:.Klima[2].TemperaturaProstora
EP2_Klima2_TempIzpihanegaZraka | REAL | IOD_EP2 | EP2:.Klima[2].TempIzpihanegaZraka
EP2_Klima2_TempPovratneVode | REAL | IOD_EP2 | EP2:.Klima[2].TempPovratneVode
EP2_Klima2_VlaznostProstora | REAL | IOD_EP2 | EP2:.Klima[2].VlaznostProstora
EP2_Klima2_ZunanjaTemp | REAL | IOD_EP2 | EP2:.Klima[2].ZunanjaTemp
EP2_PMM1_ActivePowerPhaseA_kW | REAL | IOD_EP2 | EP2:.PMM[1].ActivePowerPhaseA_kW
EP2_PMM1_ActivePowerPhaseB_kW | REAL | IOD_EP2 | EP2:.PMM[1].ActivePowerPhaseB_kW
EP2_PMM1_ActivePowerPhaseC_kW | REAL | IOD_EP2 | EP2:.PMM[1].ActivePowerPhaseC_kW
EP2_PMM1_AverageCurrent_A | REAL | IOD_EP2 | EP2:.PMM[1].AverageCurrent_A
EP2_PMM1_AveragePhaseToNeutral_V | REAL | IOD_EP2 | EP2:.PMM[1].AveragePhaseToNeutral_V
EP2_PMM1_AveragePhaseToPhase_V | REAL | IOD_EP2 | EP2:.PMM[1].AveragePhaseToPhase_V
EP2_PMM1_CurrentInPhaseA_A | REAL | IOD_EP2 | EP2:.PMM[1].CurrentInPhaseA_A
EP2_PMM1_CurrentInPhaseB_A | REAL | IOD_EP2 | EP2:.PMM[1].CurrentInPhaseB_A
EP2_PMM1_CurrentInPhaseC_A | REAL | IOD_EP2 | EP2:.PMM[1].CurrentInPhaseC_A
EP2_PMM1_EnergyConsumed_kWh | REAL | IOD_EP2 | EP2:.PMM[1].EnergyConsumed_kWh
EP2_PMM1_Frequency_Hz | REAL | IOD_EP2 | EP2:.PMM[1].Frequency_Hz
EP2_PMM1_NeutralCurrent_A | REAL | IOD_EP2 | EP2:.PMM[1].NeutralCurrent_A
EP2_PMM1_Phase1_Current10 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[10]
EP2_PMM1_Phase1_Current11 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[11]
EP2_PMM1_Phase1_Current12 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[12]
EP2_PMM1_Phase1_Current13 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[13]
EP2_PMM1_Phase1_Current14 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[14]
EP2_PMM1_Phase1_Current15 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[15]
EP2_PMM1_Phase1_Current16 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[16]
EP2_PMM1_Phase1_Current17 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[17]
EP2_PMM1_Phase1_Current18 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[18]
EP2_PMM1_Phase1_Current19 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[19]
EP2_PMM1_Phase1_Current1 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[1]
EP2_PMM1_Phase1_Current20 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[20]
EP2_PMM1_Phase1_Current21 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[21]
EP2_PMM1_Phase1_Current22 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[22]
EP2_PMM1_Phase1_Current23 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[23]
EP2_PMM1_Phase1_Current24 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[24]
EP2_PMM1_Phase1_Current25 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[25]
EP2_PMM1_Phase1_Current26 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[26]
EP2_PMM1_Phase1_Current27 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[27]
EP2_PMM1_Phase1_Current28 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[28]
EP2_PMM1_Phase1_Current29 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[29]
EP2_PMM1_Phase1_Current2 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[2]
EP2_PMM1_Phase1_Current30 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[30]
EP2_PMM1_Phase1_Current31 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[31]
EP2_PMM1_Phase1_Current32 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[32]
EP2_PMM1_Phase1_Current33 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[33]
EP2_PMM1_Phase1_Current34 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[34]
EP2_PMM1_Phase1_Current35 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[35]
EP2_PMM1_Phase1_Current36 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[36]
EP2_PMM1_Phase1_Current37 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[37]
EP2_PMM1_Phase1_Current38 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[38]
EP2_PMM1_Phase1_Current39 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[39]
EP2_PMM1_Phase1_Current3 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[3]
EP2_PMM1_Phase1_Current40 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[40]
EP2_PMM1_Phase1_Current41 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[41]
EP2_PMM1_Phase1_Current42 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[42]
EP2_PMM1_Phase1_Current4 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[4]
EP2_PMM1_Phase1_Current5 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[5]
EP2_PMM1_Phase1_Current6 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[6]
EP2_PMM1_Phase1_Current7 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[7]
EP2_PMM1_Phase1_Current8 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[8]
EP2_PMM1_Phase1_Current9 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[1].Current[9]
EP2_PMM1_Phase2_Current10 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[10]
EP2_PMM1_Phase2_Current11 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[11]
EP2_PMM1_Phase2_Current12 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[12]
EP2_PMM1_Phase2_Current13 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[13]
EP2_PMM1_Phase2_Current14 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[14]
EP2_PMM1_Phase2_Current15 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[15]
EP2_PMM1_Phase2_Current16 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[16]
EP2_PMM1_Phase2_Current17 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[17]
EP2_PMM1_Phase2_Current18 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[18]
EP2_PMM1_Phase2_Current19 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[19]
EP2_PMM1_Phase2_Current1 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[1]
EP2_PMM1_Phase2_Current20 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[20]
EP2_PMM1_Phase2_Current21 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[21]
EP2_PMM1_Phase2_Current22 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[22]
EP2_PMM1_Phase2_Current23 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[23]
EP2_PMM1_Phase2_Current24 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[24]
EP2_PMM1_Phase2_Current25 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[25]
EP2_PMM1_Phase2_Current26 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[26]
EP2_PMM1_Phase2_Current27 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[27]
EP2_PMM1_Phase2_Current28 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[28]
EP2_PMM1_Phase2_Current29 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[29]
EP2_PMM1_Phase2_Current2 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[2]
EP2_PMM1_Phase2_Current30 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[30]
EP2_PMM1_Phase2_Current31 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[31]
EP2_PMM1_Phase2_Current32 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[32]
EP2_PMM1_Phase2_Current33 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[33]
EP2_PMM1_Phase2_Current34 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[34]
EP2_PMM1_Phase2_Current35 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[35]
EP2_PMM1_Phase2_Current36 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[36]
EP2_PMM1_Phase2_Current37 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[37]
EP2_PMM1_Phase2_Current38 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[38]
EP2_PMM1_Phase2_Current39 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[39]
EP2_PMM1_Phase2_Current3 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[3]
EP2_PMM1_Phase2_Current40 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[40]
EP2_PMM1_Phase2_Current41 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[41]
EP2_PMM1_Phase2_Current42 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[42]
EP2_PMM1_Phase2_Current4 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[4]
EP2_PMM1_Phase2_Current5 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[5]
EP2_PMM1_Phase2_Current6 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[6]
EP2_PMM1_Phase2_Current7 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[7]
EP2_PMM1_Phase2_Current8 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[8]
EP2_PMM1_Phase2_Current9 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[2].Current[9]
EP2_PMM1_Phase3_Current10 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[10]
EP2_PMM1_Phase3_Current11 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[11]
EP2_PMM1_Phase3_Current12 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[12]
EP2_PMM1_Phase3_Current13 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[13]
EP2_PMM1_Phase3_Current14 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[14]
EP2_PMM1_Phase3_Current15 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[15]
EP2_PMM1_Phase3_Current16 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[16]
EP2_PMM1_Phase3_Current17 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[17]
EP2_PMM1_Phase3_Current18 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[18]
EP2_PMM1_Phase3_Current19 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[19]
EP2_PMM1_Phase3_Current1 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[1]
EP2_PMM1_Phase3_Current20 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[20]
EP2_PMM1_Phase3_Current21 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[21]
EP2_PMM1_Phase3_Current22 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[22]
EP2_PMM1_Phase3_Current23 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[23]
EP2_PMM1_Phase3_Current24 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[24]
EP2_PMM1_Phase3_Current25 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[25]
EP2_PMM1_Phase3_Current26 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[26]
EP2_PMM1_Phase3_Current27 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[27]
EP2_PMM1_Phase3_Current28 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[28]
EP2_PMM1_Phase3_Current29 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[29]
EP2_PMM1_Phase3_Current2 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[2]
EP2_PMM1_Phase3_Current30 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[30]
EP2_PMM1_Phase3_Current31 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[31]
EP2_PMM1_Phase3_Current32 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[32]
EP2_PMM1_Phase3_Current33 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[33]
EP2_PMM1_Phase3_Current34 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[34]
EP2_PMM1_Phase3_Current35 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[35]
EP2_PMM1_Phase3_Current36 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[36]
EP2_PMM1_Phase3_Current37 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[37]
EP2_PMM1_Phase3_Current38 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[38]
EP2_PMM1_Phase3_Current39 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[39]
EP2_PMM1_Phase3_Current3 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[3]
EP2_PMM1_Phase3_Current40 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[40]
EP2_PMM1_Phase3_Current41 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[41]
EP2_PMM1_Phase3_Current42 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[42]
EP2_PMM1_Phase3_Current4 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[4]
EP2_PMM1_Phase3_Current5 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[5]
EP2_PMM1_Phase3_Current6 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[6]
EP2_PMM1_Phase3_Current7 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[7]
EP2_PMM1_Phase3_Current8 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[8]
EP2_PMM1_Phase3_Current9 | REAL | IOD_EP2 | EP2:.PMM[1].Phase[3].Current[9]
EP2_PMM1_PowerFactorPhaseA | REAL | IOD_EP2 | EP2:.PMM[1].PowerFactorPhaseA
EP2_PMM1_PowerFactorPhaseB | REAL | IOD_EP2 | EP2:.PMM[1].PowerFactorPhaseB
EP2_PMM1_PowerFactorPhaseC | REAL | IOD_EP2 | EP2:.PMM[1].PowerFactorPhaseC
EP2_PMM1_TotalActivePower_kW | REAL | IOD_EP2 | EP2:.PMM[1].TotalActivePower_kW
EP2_PMM1_TotalAparentPower_kVA | REAL | IOD_EP2 | EP2:.PMM[1].TotalAparentPower_kVA
EP2_PMM1_TotalPowerFactor | REAL | IOD_EP2 | EP2:.PMM[1].TotalPowerFactor
EP2_PMM1_TotalReactivePower_kVAR | REAL | IOD_EP2 | EP2:.PMM[1].TotalReactivePower_kVAR
EP2_PMM1_VoltageBetweenPhaseAB_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseAB_V
EP2_PMM1_VoltageBetweenPhaseAN_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseAN_V
EP2_PMM1_VoltageBetweenPhaseBC_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseBC_V
EP2_PMM1_VoltageBetweenPhaseBN_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseBN_V
EP2_PMM1_VoltageBetweenPhaseCA_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseCA_V
EP2_PMM1_VoltageBetweenPhaseCN_V | REAL | IOD_EP2 | EP2:.PMM[1].VoltageBetweenPhaseCN_V
EP2_PMM2_ActivePowerPhaseA_kW | REAL | IOD_EP2 | EP2:.PMM[2].ActivePowerPhaseA_kW
EP2_PMM2_ActivePowerPhaseB_kW | REAL | IOD_EP2 | EP2:.PMM[2].ActivePowerPhaseB_kW
EP2_PMM2_ActivePowerPhaseC_kW | REAL | IOD_EP2 | EP2:.PMM[2].ActivePowerPhaseC_kW
EP2_PMM2_AverageCurrent_A | REAL | IOD_EP2 | EP2:.PMM[2].AverageCurrent_A
EP2_PMM2_AveragePhaseToNeutral_V | REAL | IOD_EP2 | EP2:.PMM[2].AveragePhaseToNeutral_V
EP2_PMM2_AveragePhaseToPhase_V | REAL | IOD_EP2 | EP2:.PMM[2].AveragePhaseToPhase_V
EP2_PMM2_CurrentInPhaseA_A | REAL | IOD_EP2 | EP2:.PMM[2].CurrentInPhaseA_A
EP2_PMM2_CurrentInPhaseB_A | REAL | IOD_EP2 | EP2:.PMM[2].CurrentInPhaseB_A
EP2_PMM2_CurrentInPhaseC_A | REAL | IOD_EP2 | EP2:.PMM[2].CurrentInPhaseC_A
EP2_PMM2_EnergyConsumed_kWh | REAL | IOD_EP2 | EP2:.PMM[2].EnergyConsumed_kWh
EP2_PMM2_Frequency_Hz | REAL | IOD_EP2 | EP2:.PMM[2].Frequency_Hz
EP2_PMM2_NeutralCurrent_A | REAL | IOD_EP2 | EP2:.PMM[2].NeutralCurrent_A
EP2_PMM2_Phase1_Current10 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[10]
EP2_PMM2_Phase1_Current11 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[11]
EP2_PMM2_Phase1_Current12 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[12]
EP2_PMM2_Phase1_Current13 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[13]
EP2_PMM2_Phase1_Current14 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[14]
EP2_PMM2_Phase1_Current15 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[15]
EP2_PMM2_Phase1_Current16 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[16]
EP2_PMM2_Phase1_Current17 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[17]
EP2_PMM2_Phase1_Current18 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[18]
EP2_PMM2_Phase1_Current19 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[19]
EP2_PMM2_Phase1_Current1 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[1]
EP2_PMM2_Phase1_Current20 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[20]
EP2_PMM2_Phase1_Current21 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[21]
EP2_PMM2_Phase1_Current22 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[22]
EP2_PMM2_Phase1_Current23 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[23]
EP2_PMM2_Phase1_Current24 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[24]
EP2_PMM2_Phase1_Current25 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[25]
EP2_PMM2_Phase1_Current26 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[26]
EP2_PMM2_Phase1_Current27 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[27]
EP2_PMM2_Phase1_Current28 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[28]
EP2_PMM2_Phase1_Current29 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[29]
EP2_PMM2_Phase1_Current2 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[2]
EP2_PMM2_Phase1_Current30 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[30]
EP2_PMM2_Phase1_Current31 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[31]
EP2_PMM2_Phase1_Current32 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[32]
EP2_PMM2_Phase1_Current33 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[33]
EP2_PMM2_Phase1_Current34 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[34]
EP2_PMM2_Phase1_Current35 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[35]
EP2_PMM2_Phase1_Current36 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[36]
EP2_PMM2_Phase1_Current37 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[37]
EP2_PMM2_Phase1_Current38 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[38]
EP2_PMM2_Phase1_Current39 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[39]
EP2_PMM2_Phase1_Current3 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[3]
EP2_PMM2_Phase1_Current40 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[40]
EP2_PMM2_Phase1_Current41 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[41]
EP2_PMM2_Phase1_Current42 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[42]
EP2_PMM2_Phase1_Current4 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[4]
EP2_PMM2_Phase1_Current5 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[5]
EP2_PMM2_Phase1_Current6 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[6]
EP2_PMM2_Phase1_Current7 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[7]
EP2_PMM2_Phase1_Current8 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[8]
EP2_PMM2_Phase1_Current9 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[1].Current[9]
EP2_PMM2_Phase2_Current10 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[10]
EP2_PMM2_Phase2_Current11 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[11]
EP2_PMM2_Phase2_Current12 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[12]
EP2_PMM2_Phase2_Current13 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[13]
EP2_PMM2_Phase2_Current14 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[14]
EP2_PMM2_Phase2_Current15 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[15]
EP2_PMM2_Phase2_Current16 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[16]
EP2_PMM2_Phase2_Current17 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[17]
EP2_PMM2_Phase2_Current18 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[18]
EP2_PMM2_Phase2_Current19 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[19]
EP2_PMM2_Phase2_Current1 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[1]
EP2_PMM2_Phase2_Current20 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[20]
EP2_PMM2_Phase2_Current21 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[21]
EP2_PMM2_Phase2_Current22 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[22]
EP2_PMM2_Phase2_Current23 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[23]
EP2_PMM2_Phase2_Current24 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[24]
EP2_PMM2_Phase2_Current25 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[25]
EP2_PMM2_Phase2_Current26 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[26]
EP2_PMM2_Phase2_Current27 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[27]
EP2_PMM2_Phase2_Current28 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[28]
EP2_PMM2_Phase2_Current29 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[29]
EP2_PMM2_Phase2_Current2 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[2]
EP2_PMM2_Phase2_Current30 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[30]
EP2_PMM2_Phase2_Current31 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[31]
EP2_PMM2_Phase2_Current32 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[32]
EP2_PMM2_Phase2_Current33 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[33]
EP2_PMM2_Phase2_Current34 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[34]
EP2_PMM2_Phase2_Current35 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[35]
EP2_PMM2_Phase2_Current36 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[36]
EP2_PMM2_Phase2_Current37 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[37]
EP2_PMM2_Phase2_Current38 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[38]
EP2_PMM2_Phase2_Current39 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[39]
EP2_PMM2_Phase2_Current3 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[3]
EP2_PMM2_Phase2_Current40 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[40]
EP2_PMM2_Phase2_Current41 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[41]
EP2_PMM2_Phase2_Current42 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[42]
EP2_PMM2_Phase2_Current4 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[4]
EP2_PMM2_Phase2_Current5 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[5]
EP2_PMM2_Phase2_Current6 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[6]
EP2_PMM2_Phase2_Current7 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[7]
EP2_PMM2_Phase2_Current8 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[8]
EP2_PMM2_Phase2_Current9 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[2].Current[9]
EP2_PMM2_Phase3_Current10 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[10]
EP2_PMM2_Phase3_Current11 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[11]
EP2_PMM2_Phase3_Current12 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[12]
EP2_PMM2_Phase3_Current13 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[13]
EP2_PMM2_Phase3_Current14 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[14]
EP2_PMM2_Phase3_Current15 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[15]
EP2_PMM2_Phase3_Current16 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[16]
EP2_PMM2_Phase3_Current17 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[17]
EP2_PMM2_Phase3_Current18 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[18]
EP2_PMM2_Phase3_Current19 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[19]
EP2_PMM2_Phase3_Current1 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[1]
EP2_PMM2_Phase3_Current20 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[20]
EP2_PMM2_Phase3_Current21 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[21]
EP2_PMM2_Phase3_Current22 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[22]
EP2_PMM2_Phase3_Current23 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[23]
EP2_PMM2_Phase3_Current24 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[24]
EP2_PMM2_Phase3_Current25 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[25]
EP2_PMM2_Phase3_Current26 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[26]
EP2_PMM2_Phase3_Current27 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[27]
EP2_PMM2_Phase3_Current28 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[28]
EP2_PMM2_Phase3_Current29 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[29]
EP2_PMM2_Phase3_Current2 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[2]
EP2_PMM2_Phase3_Current30 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[30]
EP2_PMM2_Phase3_Current31 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[31]
EP2_PMM2_Phase3_Current32 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[32]
EP2_PMM2_Phase3_Current33 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[33]
EP2_PMM2_Phase3_Current34 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[34]
EP2_PMM2_Phase3_Current35 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[35]
EP2_PMM2_Phase3_Current36 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[36]
EP2_PMM2_Phase3_Current37 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[37]
EP2_PMM2_Phase3_Current38 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[38]
EP2_PMM2_Phase3_Current39 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[39]
EP2_PMM2_Phase3_Current3 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[3]
EP2_PMM2_Phase3_Current40 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[40]
EP2_PMM2_Phase3_Current41 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[41]
EP2_PMM2_Phase3_Current42 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[42]
EP2_PMM2_Phase3_Current4 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[4]
EP2_PMM2_Phase3_Current5 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[5]
EP2_PMM2_Phase3_Current6 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[6]
EP2_PMM2_Phase3_Current7 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[7]
EP2_PMM2_Phase3_Current8 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[8]
EP2_PMM2_Phase3_Current9 | REAL | IOD_EP2 | EP2:.PMM[2].Phase[3].Current[9]
EP2_PMM2_PowerFactorPhaseA | REAL | IOD_EP2 | EP2:.PMM[2].PowerFactorPhaseA
EP2_PMM2_PowerFactorPhaseB | REAL | IOD_EP2 | EP2:.PMM[2].PowerFactorPhaseB
EP2_PMM2_PowerFactorPhaseC | REAL | IOD_EP2 | EP2:.PMM[2].PowerFactorPhaseC
EP2_PMM2_TotalActivePower_kW | REAL | IOD_EP2 | EP2:.PMM[2].TotalActivePower_kW
EP2_PMM2_TotalAparentPower_kVA | REAL | IOD_EP2 | EP2:.PMM[2].TotalAparentPower_kVA
EP2_PMM2_TotalPowerFactor | REAL | IOD_EP2 | EP2:.PMM[2].TotalPowerFactor
EP2_PMM2_TotalReactivePower_kVAR | REAL | IOD_EP2 | EP2:.PMM[2].TotalReactivePower_kVAR
EP2_PMM2_VoltageBetweenPhaseAB_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseAB_V
EP2_PMM2_VoltageBetweenPhaseAN_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseAN_V
EP2_PMM2_VoltageBetweenPhaseBC_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseBC_V
EP2_PMM2_VoltageBetweenPhaseBN_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseBN_V
EP2_PMM2_VoltageBetweenPhaseCA_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseCA_V
EP2_PMM2_VoltageBetweenPhaseCN_V | REAL | IOD_EP2 | EP2:.PMM[2].VoltageBetweenPhaseCN_V
EP2_PMM3_ActivePowerPhaseA_kW | REAL | IOD_EP2 | EP2:.PMM[3].ActivePowerPhaseA_kW
EP2_PMM3_ActivePowerPhaseB_kW | REAL | IOD_EP2 | EP2:.PMM[3].ActivePowerPhaseB_kW
EP2_PMM3_ActivePowerPhaseC_kW | REAL | IOD_EP2 | EP2:.PMM[3].ActivePowerPhaseC_kW
EP2_PMM3_AverageCurrent_A | REAL | IOD_EP2 | EP2:.PMM[3].AverageCurrent_A
EP2_PMM3_AveragePhaseToNeutral_V | REAL | IOD_EP2 | EP2:.PMM[3].AveragePhaseToNeutral_V
EP2_PMM3_AveragePhaseToPhase_V | REAL | IOD_EP2 | EP2:.PMM[3].AveragePhaseToPhase_V
EP2_PMM3_CurrentInPhaseA_A | REAL | IOD_EP2 | EP2:.PMM[3].CurrentInPhaseA_A
EP2_PMM3_CurrentInPhaseB_A | REAL | IOD_EP2 | EP2:.PMM[3].CurrentInPhaseB_A
EP2_PMM3_CurrentInPhaseC_A | REAL | IOD_EP2 | EP2:.PMM[3].CurrentInPhaseC_A
EP2_PMM3_EnergyConsumed_kWh | REAL | IOD_EP2 | EP2:.PMM[3].EnergyConsumed_kWh
EP2_PMM3_Frequency_Hz | REAL | IOD_EP2 | EP2:.PMM[3].Frequency_Hz
EP2_PMM3_NeutralCurrent_A | REAL | IOD_EP2 | EP2:.PMM[3].NeutralCurrent_A
EP2_PMM3_Phase1_Current10 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[10]
EP2_PMM3_Phase1_Current11 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[11]
EP2_PMM3_Phase1_Current12 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[12]
EP2_PMM3_Phase1_Current13 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[13]
EP2_PMM3_Phase1_Current14 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[14]
EP2_PMM3_Phase1_Current15 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[15]
EP2_PMM3_Phase1_Current16 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[16]
EP2_PMM3_Phase1_Current17 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[17]
EP2_PMM3_Phase1_Current18 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[18]
EP2_PMM3_Phase1_Current19 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[19]
EP2_PMM3_Phase1_Current1 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[1]
EP2_PMM3_Phase1_Current20 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[20]
EP2_PMM3_Phase1_Current21 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[21]
EP2_PMM3_Phase1_Current22 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[22]
EP2_PMM3_Phase1_Current23 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[23]
EP2_PMM3_Phase1_Current24 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[24]
EP2_PMM3_Phase1_Current25 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[25]
EP2_PMM3_Phase1_Current26 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[26]
EP2_PMM3_Phase1_Current27 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[27]
EP2_PMM3_Phase1_Current28 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[28]
EP2_PMM3_Phase1_Current29 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[29]
EP2_PMM3_Phase1_Current2 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[2]
EP2_PMM3_Phase1_Current30 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[30]
EP2_PMM3_Phase1_Current31 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[31]
EP2_PMM3_Phase1_Current32 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[32]
EP2_PMM3_Phase1_Current33 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[33]
EP2_PMM3_Phase1_Current34 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[34]
EP2_PMM3_Phase1_Current35 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[35]
EP2_PMM3_Phase1_Current36 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[36]
EP2_PMM3_Phase1_Current37 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[37]
EP2_PMM3_Phase1_Current38 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[38]
EP2_PMM3_Phase1_Current39 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[39]
EP2_PMM3_Phase1_Current3 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[3]
EP2_PMM3_Phase1_Current40 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[40]
EP2_PMM3_Phase1_Current41 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[41]
EP2_PMM3_Phase1_Current42 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[42]
EP2_PMM3_Phase1_Current4 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[4]
EP2_PMM3_Phase1_Current5 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[5]
EP2_PMM3_Phase1_Current6 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[6]
EP2_PMM3_Phase1_Current7 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[7]
EP2_PMM3_Phase1_Current8 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[8]
EP2_PMM3_Phase1_Current9 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[1].Current[9]
EP2_PMM3_Phase2_Current10 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[10]
EP2_PMM3_Phase2_Current11 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[11]
EP2_PMM3_Phase2_Current12 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[12]
EP2_PMM3_Phase2_Current13 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[13]
EP2_PMM3_Phase2_Current14 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[14]
EP2_PMM3_Phase2_Current15 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[15]
EP2_PMM3_Phase2_Current16 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[16]
EP2_PMM3_Phase2_Current17 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[17]
EP2_PMM3_Phase2_Current18 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[18]
EP2_PMM3_Phase2_Current19 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[19]
EP2_PMM3_Phase2_Current1 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[1]
EP2_PMM3_Phase2_Current20 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[20]
EP2_PMM3_Phase2_Current21 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[21]
EP2_PMM3_Phase2_Current22 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[22]
EP2_PMM3_Phase2_Current23 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[23]
EP2_PMM3_Phase2_Current24 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[24]
EP2_PMM3_Phase2_Current25 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[25]
EP2_PMM3_Phase2_Current26 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[26]
EP2_PMM3_Phase2_Current27 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[27]
EP2_PMM3_Phase2_Current28 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[28]
EP2_PMM3_Phase2_Current29 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[29]
EP2_PMM3_Phase2_Current2 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[2]
EP2_PMM3_Phase2_Current30 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[30]
EP2_PMM3_Phase2_Current31 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[31]
EP2_PMM3_Phase2_Current32 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[32]
EP2_PMM3_Phase2_Current33 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[33]
EP2_PMM3_Phase2_Current34 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[34]
EP2_PMM3_Phase2_Current35 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[35]
EP2_PMM3_Phase2_Current36 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[36]
EP2_PMM3_Phase2_Current37 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[37]
EP2_PMM3_Phase2_Current38 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[38]
EP2_PMM3_Phase2_Current39 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[39]
EP2_PMM3_Phase2_Current3 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[3]
EP2_PMM3_Phase2_Current40 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[40]
EP2_PMM3_Phase2_Current41 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[41]
EP2_PMM3_Phase2_Current42 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[42]
EP2_PMM3_Phase2_Current4 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[4]
EP2_PMM3_Phase2_Current5 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[5]
EP2_PMM3_Phase2_Current6 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[6]
EP2_PMM3_Phase2_Current7 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[7]
EP2_PMM3_Phase2_Current8 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[8]
EP2_PMM3_Phase2_Current9 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[2].Current[9]
EP2_PMM3_Phase3_Current10 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[10]
EP2_PMM3_Phase3_Current11 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[11]
EP2_PMM3_Phase3_Current12 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[12]
EP2_PMM3_Phase3_Current13 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[13]
EP2_PMM3_Phase3_Current14 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[14]
EP2_PMM3_Phase3_Current15 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[15]
EP2_PMM3_Phase3_Current16 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[16]
EP2_PMM3_Phase3_Current17 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[17]
EP2_PMM3_Phase3_Current18 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[18]
EP2_PMM3_Phase3_Current19 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[19]
EP2_PMM3_Phase3_Current1 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[1]
EP2_PMM3_Phase3_Current20 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[20]
EP2_PMM3_Phase3_Current21 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[21]
EP2_PMM3_Phase3_Current22 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[22]
EP2_PMM3_Phase3_Current23 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[23]
EP2_PMM3_Phase3_Current24 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[24]
EP2_PMM3_Phase3_Current25 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[25]
EP2_PMM3_Phase3_Current26 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[26]
EP2_PMM3_Phase3_Current27 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[27]
EP2_PMM3_Phase3_Current28 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[28]
EP2_PMM3_Phase3_Current29 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[29]
EP2_PMM3_Phase3_Current2 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[2]
EP2_PMM3_Phase3_Current30 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[30]
EP2_PMM3_Phase3_Current31 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[31]
EP2_PMM3_Phase3_Current32 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[32]
EP2_PMM3_Phase3_Current33 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[33]
EP2_PMM3_Phase3_Current34 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[34]
EP2_PMM3_Phase3_Current35 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[35]
EP2_PMM3_Phase3_Current36 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[36]
EP2_PMM3_Phase3_Current37 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[37]
EP2_PMM3_Phase3_Current38 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[38]
EP2_PMM3_Phase3_Current39 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[39]
EP2_PMM3_Phase3_Current3 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[3]
EP2_PMM3_Phase3_Current40 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[40]
EP2_PMM3_Phase3_Current41 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[41]
EP2_PMM3_Phase3_Current42 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[42]
EP2_PMM3_Phase3_Current4 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[4]
EP2_PMM3_Phase3_Current5 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[5]
EP2_PMM3_Phase3_Current6 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[6]
EP2_PMM3_Phase3_Current7 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[7]
EP2_PMM3_Phase3_Current8 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[8]
EP2_PMM3_Phase3_Current9 | REAL | IOD_EP2 | EP2:.PMM[3].Phase[3].Current[9]
EP2_PMM3_PowerFactorPhaseA | REAL | IOD_EP2 | EP2:.PMM[3].PowerFactorPhaseA
EP2_PMM3_PowerFactorPhaseB | REAL | IOD_EP2 | EP2:.PMM[3].PowerFactorPhaseB
EP2_PMM3_PowerFactorPhaseC | REAL | IOD_EP2 | EP2:.PMM[3].PowerFactorPhaseC
EP2_PMM3_TotalActivePower_kW | REAL | IOD_EP2 | EP2:.PMM[3].TotalActivePower_kW
EP2_PMM3_TotalAparentPower_kVA | REAL | IOD_EP2 | EP2:.PMM[3].TotalAparentPower_kVA
EP2_PMM3_TotalPowerFactor | REAL | IOD_EP2 | EP2:.PMM[3].TotalPowerFactor
EP2_PMM3_TotalReactivePower_kVAR | REAL | IOD_EP2 | EP2:.PMM[3].TotalReactivePower_kVAR
EP2_PMM3_VoltageBetweenPhaseAB_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseAB_V
EP2_PMM3_VoltageBetweenPhaseAN_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseAN_V
EP2_PMM3_VoltageBetweenPhaseBC_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseBC_V
EP2_PMM3_VoltageBetweenPhaseBN_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseBN_V
EP2_PMM3_VoltageBetweenPhaseCA_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseCA_V
EP2_PMM3_VoltageBetweenPhaseCN_V | REAL | IOD_EP2 | EP2:.PMM[3].VoltageBetweenPhaseCN_V
EP2_rVersion | REAL | IOD_EP2 | EP2:.rVersion
EP2_SenzorTemp1 | REAL | IOD_EP2 | EP2:.SenzorTemp[1]
EP2_SenzorTemp2 | REAL | IOD_EP2 | EP2:.SenzorTemp[2]
EP2_SenzorVlaga1 | REAL | IOD_EP2 | EP2:.SenzorVlaga[1]
EP2_SenzorVlaga2 | REAL | IOD_EP2 | EP2:.SenzorVlaga[2]
EP2_TempMaxPoint | REAL | IOD_EP2 | EP2:.TempMaxPoint
EP2_TempSetPoint | REAL | IOD_EP2 | EP2:.TempSetPoint
EP2UPS1EstimatedChargeRemaining | REAL | IOD_EP2 | EP2:.UPS[1].EstimatedChargeRemaining
EP2UPS1EstimatedMinutesRemaining | REAL | IOD_EP2 | EP2:.UPS[1].EstimatedMinutesRemaining
EP2UPS1IzhodMocL1 | REAL | IOD_EP2 | EP2:.UPS[1].IzhodMocL1
EP2UPS1IzhodMocL2 | REAL | IOD_EP2 | EP2:.UPS[1].IzhodMocL2
EP2UPS1IzhodMocL3 | REAL | IOD_EP2 | EP2:.UPS[1].IzhodMocL3
EP2UPS1NapetostBaterije | REAL | IOD_EP2 | EP2:.UPS[1].NapetostBaterije
EP2UPS1TemperaturaBaterije | REAL | IOD_EP2 | EP2:.UPS[1].TemperaturaBaterije
EP2UPS1VhodFrekvencaL1 | REAL | IOD_EP2 | EP2:.UPS[1].VhodFrekvencaL1
EP2UPS1VhodFrekvencaL2 | REAL | IOD_EP2 | EP2:.UPS[1].VhodFrekvencaL2
EP2UPS1VhodFrekvencaL3 | REAL | IOD_EP2 | EP2:.UPS[1].VhodFrekvencaL3
EP2UPS1VhodNapetostL1 | REAL | IOD_EP2 | EP2:.UPS[1].VhodNapetostL1
EP2UPS1VhodNapetostL2 | REAL | IOD_EP2 | EP2:.UPS[1].VhodNapetostL2
EP2UPS1VhodNapetostL3 | REAL | IOD_EP2 | EP2:.UPS[1].VhodNapetostL3
EP2UPS2EstimatedChargeRemaining | REAL | IOD_EP2 | EP2:.UPS[2].EstimatedChargeRemaining
EP2UPS2EstimatedMinutesRemaining | REAL | IOD_EP2 | EP2:.UPS[2].EstimatedMinutesRemaining
EP2UPS2IzhodMocL1 | REAL | IOD_EP2 | EP2:.UPS[2].IzhodMocL1
EP2UPS2IzhodMocL2 | REAL | IOD_EP2 | EP2:.UPS[2].IzhodMocL2
EP2UPS2IzhodMocL3 | REAL | IOD_EP2 | EP2:.UPS[2].IzhodMocL3
EP2UPS2NapetostBaterije | REAL | IOD_EP2 | EP2:.UPS[2].NapetostBaterije
EP2UPS2TemperaturaBaterije | REAL | IOD_EP2 | EP2:.UPS[2].TemperaturaBaterije
EP2UPS2VhodFrekvencaL1 | REAL | IOD_EP2 | EP2:.UPS[2].VhodFrekvencaL1
EP2UPS2VhodFrekvencaL2 | REAL | IOD_EP2 | EP2:.UPS[2].VhodFrekvencaL2
EP2UPS2VhodFrekvencaL3 | REAL | IOD_EP2 | EP2:.UPS[2].VhodFrekvencaL3
EP2UPS2VhodNapetostL1 | REAL | IOD_EP2 | EP2:.UPS[2].VhodNapetostL1
EP2UPS2VhodNapetostL2 | REAL | IOD_EP2 | EP2:.UPS[2].VhodNapetostL2
EP2UPS2VhodNapetostL3 | REAL | IOD_EP2 | EP2:.UPS[2].VhodNapetostL3
EP2KlimaGalNastMaxTemp | REAL | IOD_EP2 | EP2:.KlimaGal.NastMaxTemp
EP2KlimaGalNastMaxVlaznost | REAL | IOD_EP2 | EP2:.KlimaGal.NastMaxVlaznost
EP2KlimaGalNastMinTemp | REAL | IOD_EP2 | EP2:.KlimaGal.NastMinTemp
EP2KlimaGalNastMinVlaznost | REAL | IOD_EP2 | EP2:.KlimaGal.NastMinVlaznost
EP2KlimaGalNastTempProstora | REAL | IOD_EP2 | EP2:.KlimaGal.NastTempProstora
EP2KlimaGalNastVlaznost | REAL | IOD_EP2 | EP2:.KlimaGal.NastVlaznost
EP2KlimaGalObratovalneUre | REAL | IOD_EP2 | EP2:.KlimaGal.ObratovalneUre
EP2KlimaGalTemperaturaProstora | REAL | IOD_EP2 | EP2:.KlimaGal.TemperaturaProstora
EP2KlimaGalTempIzpihanegaZraka | REAL | IOD_EP2 | EP2:.KlimaGal.TempIzpihanegaZraka
EP2KlimaGalTempPovratneVode | REAL | IOD_EP2 | EP2:.KlimaGal.TempPovratneVode
EP2KlimaGalVlaznostProstora | REAL | IOD_EP2 | EP2:.KlimaGal.VlaznostProstora
EP2KlimaGalZunanjaTemp | REAL | IOD_EP2 | EP2:.KlimaGal.ZunanjaTemp
EP2PMMfaza01 | REAL | IOD_EP2 | EP2:.PMMfaza01
EP2PMMfaza02 | REAL | IOD_EP2 | EP2:.PMMfaza02
EP2PMMfaza03 | REAL | IOD_EP2 | EP2:.PMMfaza03
EP2PMMfaza04 | REAL | IOD_EP2 | EP2:.PMMfaza04
EP2PMMfaza05 | REAL | IOD_EP2 | EP2:.PMMfaza05
EP2PMMfaza06 | REAL | IOD_EP2 | EP2:.PMMfaza06
EP2PMMfaza07 | REAL | IOD_EP2 | EP2:.PMMfaza07
EP2PMMfaza08 | REAL | IOD_EP2 | EP2:.PMMfaza08
EP2PMMfaza09 | REAL | IOD_EP2 | EP2:.PMMfaza09
EP2PMMfaza10 | REAL | IOD_EP2 | EP2:.PMMfaza10
EP2PMMfaza11 | REAL | IOD_EP2 | EP2:.PMMfaza11
EP2PMMfaza12 | REAL | IOD_EP2 | EP2:.PMMfaza12
EP2PMMfaza13 | REAL | IOD_EP2 | EP2:.PMMfaza13
EP2PMMfaza14 | REAL | IOD_EP2 | EP2:.PMMfaza14
EP2PMMfaza15 | REAL | IOD_EP2 | EP2:.PMMfaza15
EP2PMMfaza16 | REAL | IOD_EP2 | EP2:.PMMfaza16
EP2PMMfaza17 | REAL | IOD_EP2 | EP2:.PMMfaza17
EP2PMMfaza18 | REAL | IOD_EP2 | EP2:.PMMfaza18
EP2PMMfaza19 | REAL | IOD_EP2 | EP2:.PMMfaza19
EP2PMMfaza20 | REAL | IOD_EP2 | EP2:.PMMfaza20
EP2PMMfaza21 | REAL | IOD_EP2 | EP2:.PMMfaza21
EP2PMMfaza22 | REAL | IOD_EP2 | EP2:.PMMfaza22
EP2PMMfaza23 | REAL | IOD_EP2 | EP2:.PMMfaza23
EP2PMMfaza24 | REAL | IOD_EP2 | EP2:.PMMfaza24
EP2PMMfaza25 | REAL | IOD_EP2 | EP2:.PMMfaza25
EP2PMMfaza26 | REAL | IOD_EP2 | EP2:.PMMfaza26
EP2PMMfaza27 | REAL | IOD_EP2 | EP2:.PMMfaza27
EP2PMMfaza28 | REAL | IOD_EP2 | EP2:.PMMfaza28
EP2PMMfaza29 | REAL | IOD_EP2 | EP2:.PMMfaza29
EP2PMMfaza30 | REAL | IOD_EP2 | EP2:.PMMfaza30
EP2PMMfaza31 | REAL | IOD_EP2 | EP2:.PMMfaza31
EP2PMMfaza32 | REAL | IOD_EP2 | EP2:.PMMfaza32
EP2PMMfaza33 | REAL | IOD_EP2 | EP2:.PMMfaza33
EP2PMMfaza34 | REAL | IOD_EP2 | EP2:.PMMfaza34
EP2PMMfaza35 | REAL | IOD_EP2 | EP2:.PMMfaza35
EP2PMMfaza36 | REAL | IOD_EP2 | EP2:.PMMfaza36
EP2PMMfaza37 | REAL | IOD_EP2 | EP2:.PMMfaza37
EP2PMMfaza38 | REAL | IOD_EP2 | EP2:.PMMfaza38
EP2PMMfaza39 | REAL | IOD_EP2 | EP2:.PMMfaza39
EP2PMMfaza40 | REAL | IOD_EP2 | EP2:.PMMfaza40
EP2PMMfaza41 | REAL | IOD_EP2 | EP2:.PMMfaza41
EP2PMMfaza42 | REAL | IOD_EP2 | EP2:.PMMfaza42
EP2PMMfaza6010 | REAL | IOD_EP2 | EP2:.PMMfaza60[10]
EP2PMMfaza6011 | REAL | IOD_EP2 | EP2:.PMMfaza60[11]
EP2PMMfaza6012 | REAL | IOD_EP2 | EP2:.PMMfaza60[12]
EP2PMMfaza6013 | REAL | IOD_EP2 | EP2:.PMMfaza60[13]
EP2PMMfaza6014 | REAL | IOD_EP2 | EP2:.PMMfaza60[14]
EP2PMMfaza6015 | REAL | IOD_EP2 | EP2:.PMMfaza60[15]
EP2PMMfaza6016 | REAL | IOD_EP2 | EP2:.PMMfaza60[16]
EP2PMMfaza6017 | REAL | IOD_EP2 | EP2:.PMMfaza60[17]
EP2PMMfaza6018 | REAL | IOD_EP2 | EP2:.PMMfaza60[18]
EP2PMMfaza6019 | REAL | IOD_EP2 | EP2:.PMMfaza60[19]
EP2PMMfaza601 | REAL | IOD_EP2 | EP2:.PMMfaza60[1]
EP2PMMfaza6020 | REAL | IOD_EP2 | EP2:.PMMfaza60[20]
EP2PMMfaza6021 | REAL | IOD_EP2 | EP2:.PMMfaza60[21]
EP2PMMfaza6022 | REAL | IOD_EP2 | EP2:.PMMfaza60[22]
EP2PMMfaza6023 | REAL | IOD_EP2 | EP2:.PMMfaza60[23]
EP2PMMfaza6024 | REAL | IOD_EP2 | EP2:.PMMfaza60[24]
EP2PMMfaza6025 | REAL | IOD_EP2 | EP2:.PMMfaza60[25]
EP2PMMfaza6026 | REAL | IOD_EP2 | EP2:.PMMfaza60[26]
EP2PMMfaza6027 | REAL | IOD_EP2 | EP2:.PMMfaza60[27]
EP2PMMfaza6028 | REAL | IOD_EP2 | EP2:.PMMfaza60[28]
EP2PMMfaza6029 | REAL | IOD_EP2 | EP2:.PMMfaza60[29]
EP2PMMfaza602 | REAL | IOD_EP2 | EP2:.PMMfaza60[2]
EP2PMMfaza6030 | REAL | IOD_EP2 | EP2:.PMMfaza60[30]
EP2PMMfaza6031 | REAL | IOD_EP2 | EP2:.PMMfaza60[31]
EP2PMMfaza6032 | REAL | IOD_EP2 | EP2:.PMMfaza60[32]
EP2PMMfaza6033 | REAL | IOD_EP2 | EP2:.PMMfaza60[33]
EP2PMMfaza6034 | REAL | IOD_EP2 | EP2:.PMMfaza60[34]
EP2PMMfaza6035 | REAL | IOD_EP2 | EP2:.PMMfaza60[35]
EP2PMMfaza6036 | REAL | IOD_EP2 | EP2:.PMMfaza60[36]
EP2PMMfaza6037 | REAL | IOD_EP2 | EP2:.PMMfaza60[37]
EP2PMMfaza6038 | REAL | IOD_EP2 | EP2:.PMMfaza60[38]
EP2PMMfaza6039 | REAL | IOD_EP2 | EP2:.PMMfaza60[39]
EP2PMMfaza603 | REAL | IOD_EP2 | EP2:.PMMfaza60[3]
EP2PMMfaza6040 | REAL | IOD_EP2 | EP2:.PMMfaza60[40]
EP2PMMfaza6041 | REAL | IOD_EP2 | EP2:.PMMfaza60[41]
EP2PMMfaza6042 | REAL | IOD_EP2 | EP2:.PMMfaza60[42]
EP2PMMfaza604 | REAL | IOD_EP2 | EP2:.PMMfaza60[4]
EP2PMMfaza605 | REAL | IOD_EP2 | EP2:.PMMfaza60[5]
EP2PMMfaza606 | REAL | IOD_EP2 | EP2:.PMMfaza60[6]
EP2PMMfaza607 | REAL | IOD_EP2 | EP2:.PMMfaza60[7]
EP2PMMfaza608 | REAL | IOD_EP2 | EP2:.PMMfaza60[8]
EP2PMMfaza609 | REAL | IOD_EP2 | EP2:.PMMfaza60[9]
EP2PMMfaza8010 | REAL | IOD_EP2 | EP2:.PMMfaza80[10]
EP2PMMfaza8011 | REAL | IOD_EP2 | EP2:.PMMfaza80[11]
EP2PMMfaza8012 | REAL | IOD_EP2 | EP2:.PMMfaza80[12]
EP2PMMfaza8013 | REAL | IOD_EP2 | EP2:.PMMfaza80[13]
EP2PMMfaza8014 | REAL | IOD_EP2 | EP2:.PMMfaza80[14]
EP2PMMfaza8015 | REAL | IOD_EP2 | EP2:.PMMfaza80[15]
EP2PMMfaza8016 | REAL | IOD_EP2 | EP2:.PMMfaza80[16]
EP2PMMfaza8017 | REAL | IOD_EP2 | EP2:.PMMfaza80[17]
EP2PMMfaza8018 | REAL | IOD_EP2 | EP2:.PMMfaza80[18]
EP2PMMfaza8019 | REAL | IOD_EP2 | EP2:.PMMfaza80[19]
EP2PMMfaza801 | REAL | IOD_EP2 | EP2:.PMMfaza80[1]
EP2PMMfaza8020 | REAL | IOD_EP2 | EP2:.PMMfaza80[20]
EP2PMMfaza8021 | REAL | IOD_EP2 | EP2:.PMMfaza80[21]
EP2PMMfaza8022 | REAL | IOD_EP2 | EP2:.PMMfaza80[22]
EP2PMMfaza8023 | REAL | IOD_EP2 | EP2:.PMMfaza80[23]
EP2PMMfaza8024 | REAL | IOD_EP2 | EP2:.PMMfaza80[24]
EP2PMMfaza8025 | REAL | IOD_EP2 | EP2:.PMMfaza80[25]
EP2PMMfaza8026 | REAL | IOD_EP2 | EP2:.PMMfaza80[26]
EP2PMMfaza8027 | REAL | IOD_EP2 | EP2:.PMMfaza80[27]
EP2PMMfaza8028 | REAL | IOD_EP2 | EP2:.PMMfaza80[28]
EP2PMMfaza8029 | REAL | IOD_EP2 | EP2:.PMMfaza80[29]
EP2PMMfaza802 | REAL | IOD_EP2 | EP2:.PMMfaza80[2]
EP2PMMfaza8030 | REAL | IOD_EP2 | EP2:.PMMfaza80[30]
EP2PMMfaza8031 | REAL | IOD_EP2 | EP2:.PMMfaza80[31]
EP2PMMfaza8032 | REAL | IOD_EP2 | EP2:.PMMfaza80[32]
EP2PMMfaza8033 | REAL | IOD_EP2 | EP2:.PMMfaza80[33]
EP2PMMfaza8034 | REAL | IOD_EP2 | EP2:.PMMfaza80[34]
EP2PMMfaza8035 | REAL | IOD_EP2 | EP2:.PMMfaza80[35]
EP2PMMfaza8036 | REAL | IOD_EP2 | EP2:.PMMfaza80[36]
EP2PMMfaza8037 | REAL | IOD_EP2 | EP2:.PMMfaza80[37]
EP2PMMfaza8038 | REAL | IOD_EP2 | EP2:.PMMfaza80[38]
EP2PMMfaza8039 | REAL | IOD_EP2 | EP2:.PMMfaza80[39]
EP2PMMfaza803 | REAL | IOD_EP2 | EP2:.PMMfaza80[3]
EP2PMMfaza8040 | REAL | IOD_EP2 | EP2:.PMMfaza80[40]
EP2PMMfaza8041 | REAL | IOD_EP2 | EP2:.PMMfaza80[41]
EP2PMMfaza8042 | REAL | IOD_EP2 | EP2:.PMMfaza80[42]
EP2PMMfaza804 | REAL | IOD_EP2 | EP2:.PMMfaza80[4]
EP2PMMfaza805 | REAL | IOD_EP2 | EP2:.PMMfaza80[5]
EP2PMMfaza806 | REAL | IOD_EP2 | EP2:.PMMfaza80[6]
EP2PMMfaza807 | REAL | IOD_EP2 | EP2:.PMMfaza80[7]
EP2PMMfaza808 | REAL | IOD_EP2 | EP2:.PMMfaza80[8]
EP2PMMfaza809 | REAL | IOD_EP2 | EP2:.PMMfaza80[9]
EP2PMMgalActivePowerPhaseA_kW | REAL | IOD_EP2 | EP2:.PMMgal.ActivePowerPhaseA_kW
EP2PMMgalActivePowerPhaseB_kW | REAL | IOD_EP2 | EP2:.PMMgal.ActivePowerPhaseB_kW
EP2PMMgalActivePowerPhaseC_kW | REAL | IOD_EP2 | EP2:.PMMgal.ActivePowerPhaseC_kW
EP2PMMgalAverageCurrent_A | REAL | IOD_EP2 | EP2:.PMMgal.AverageCurrent_A
EP2PMMgalAveragePhaseToNeutral_V | REAL | IOD_EP2 | EP2:.PMMgal.AveragePhaseToNeutral_V
EP2PMMgalAveragePhaseToPhase_V | REAL | IOD_EP2 | EP2:.PMMgal.AveragePhaseToPhase_V
EP2PMMgalCurrentInPhaseA_A | REAL | IOD_EP2 | EP2:.PMMgal.CurrentInPhaseA_A
EP2PMMgalCurrentInPhaseB_A | REAL | IOD_EP2 | EP2:.PMMgal.CurrentInPhaseB_A
EP2PMMgalCurrentInPhaseC_A | REAL | IOD_EP2 | EP2:.PMMgal.CurrentInPhaseC_A
EP2PMMgalEnergyConsumed_kWh | REAL | IOD_EP2 | EP2:.PMMgal.EnergyConsumed_kWh
EP2PMMgalFrequency_Hz | REAL | IOD_EP2 | EP2:.PMMgal.Frequency_Hz
EP2PMMgalNeutralCurrent_A | REAL | IOD_EP2 | EP2:.PMMgal.NeutralCurrent_A
EP2PMMgalPhase1Current10 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[10]
EP2PMMgalPhase1Current11 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[11]
EP2PMMgalPhase1Current12 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[12]
EP2PMMgalPhase1Current13 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[13]
EP2PMMgalPhase1Current14 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[14]
EP2PMMgalPhase1Current15 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[15]
EP2PMMgalPhase1Current16 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[16]
EP2PMMgalPhase1Current17 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[17]
EP2PMMgalPhase1Current18 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[18]
EP2PMMgalPhase1Current19 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[19]
EP2PMMgalPhase1Current1 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[1]
EP2PMMgalPhase1Current20 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[20]
EP2PMMgalPhase1Current21 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[21]
EP2PMMgalPhase1Current22 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[22]
EP2PMMgalPhase1Current23 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[23]
EP2PMMgalPhase1Current24 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[24]
EP2PMMgalPhase1Current25 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[25]
EP2PMMgalPhase1Current26 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[26]
EP2PMMgalPhase1Current27 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[27]
EP2PMMgalPhase1Current28 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[28]
EP2PMMgalPhase1Current29 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[29]
EP2PMMgalPhase1Current2 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[2]
EP2PMMgalPhase1Current30 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[30]
EP2PMMgalPhase1Current31 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[31]
EP2PMMgalPhase1Current32 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[32]
EP2PMMgalPhase1Current33 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[33]
EP2PMMgalPhase1Current34 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[34]
EP2PMMgalPhase1Current35 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[35]
EP2PMMgalPhase1Current36 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[36]
EP2PMMgalPhase1Current37 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[37]
EP2PMMgalPhase1Current38 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[38]
EP2PMMgalPhase1Current39 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[39]
EP2PMMgalPhase1Current3 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[3]
EP2PMMgalPhase1Current40 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[40]
EP2PMMgalPhase1Current41 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[41]
EP2PMMgalPhase1Current42 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[42]
EP2PMMgalPhase1Current4 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[4]
EP2PMMgalPhase1Current5 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[5]
EP2PMMgalPhase1Current6 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[6]
EP2PMMgalPhase1Current7 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[7]
EP2PMMgalPhase1Current8 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[8]
EP2PMMgalPhase1Current9 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[1].Current[9]
EP2PMMgalPhase2Current10 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[10]
EP2PMMgalPhase2Current11 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[11]
EP2PMMgalPhase2Current12 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[12]
EP2PMMgalPhase2Current13 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[13]
EP2PMMgalPhase2Current14 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[14]
EP2PMMgalPhase2Current15 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[15]
EP2PMMgalPhase2Current16 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[16]
EP2PMMgalPhase2Current17 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[17]
EP2PMMgalPhase2Current18 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[18]
EP2PMMgalPhase2Current19 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[19]
EP2PMMgalPhase2Current1 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[1]
EP2PMMgalPhase2Current20 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[20]
EP2PMMgalPhase2Current21 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[21]
EP2PMMgalPhase2Current22 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[22]
EP2PMMgalPhase2Current23 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[23]
EP2PMMgalPhase2Current24 | REAL | IOD_EP2 | EP2:.PMMgal.Phase[2].Current[24]
EP2TempAlarmPoint | REAL | IOD_EP2 | EP2:.TempAlarmPoint
EP2_RazlikaUr | REAL | IOD_EP2 | EP2:.RazlikaUr
EP2_Circ1_MaximumDemandA2 | REAL | IOD_EP2 | EP2:.Circ[1].MaximumDemandA2
EP2_Circ1_MaximumDemandA3 | REAL | IOD_EP2 | EP2:.Circ[1].MaximumDemandA3
EP2Circ1RazEner_D_SCADA | REAL | IOD_EP2 | EP2:.Circ[1].RazEner_D_SCADA
EP2Circ1RazEner_T_SCADA | REAL | IOD_EP2 | EP2:.Circ[1].RazEner_T_SCADA
EP2Circ1RazEner_M_SCADA | REAL | IOD_EP2 | EP2:.Circ[1].RazEner_M_SCADA
EP2_UserCurrentName | STRING | IOD_EP2 | EP2:.UserCurrentName
EP2PMMgalAlarmPhase1C01_16_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C01_16_60to80
EP2PMMgalAlarmPhase1C01_16_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C01_16_over80
EP2PMMgalAlarmPhase1C17_32_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C17_32_60to80
EP2PMMgalAlarmPhase1C17_32_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C17_32_over80
EP2PMMgalAlarmPhase1C33_42_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C33_42_60to80
EP2PMMgalAlarmPhase1C33_42_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[1].C33_42_over80
EP2PMMgalAlarmPhase2C01_16_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C01_16_60to80
EP2PMMgalAlarmPhase2C01_16_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C01_16_over80
EP2PMMgalAlarmPhase2C17_32_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C17_32_60to80
EP2PMMgalAlarmPhase2C17_32_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C17_32_over80
EP2PMMgalAlarmPhase2C33_42_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C33_42_60to80
EP2PMMgalAlarmPhase2C33_42_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[2].C33_42_over80
EP2PMMgalAlarmPhase3C01_16_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C01_16_60to80
EP2PMMgalAlarmPhase3C01_16_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C01_16_over80
EP2PMMgalAlarmPhase3C17_32_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C17_32_60to80
EP2PMMgalAlarmPhase3C17_32_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C17_32_over80
EP2PMMgalAlarmPhase3C33_42_60to80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C33_42_60to80
EP2PMMgalAlarmPhase3C33_42_over80 | UINT | IOD_EP2 | EP2:.PMMgal.AlarmPhase[3].C33_42_over80
EP2PMMgalAlarms | UINT | IOD_EP2 | EP2:.PMMgal.Alarms

## variable_3
EP2_AlarmGenCirc1 | DIGITAL | IOD_EP2_TCP | 1 | 00001 | AlarmGenCirc1
EP2_AlarmGenComm | DIGITAL | IOD_EP2_TCP | 2 | 00002 | AlarmGenComm
EP2_AlarmGenDI | DIGITAL | IOD_EP2_TCP | 3 | 00003 | AlarmGenDI
EP2_AlarmGenKlima5 | DIGITAL | IOD_EP2_TCP | 4 | 00004 | AlarmGenKlima5
EP2_AlarmGenKlima6 | DIGITAL | IOD_EP2_TCP | 5 | 00005 | AlarmGenKlima6
EP2_AlarmGenPMM1 | DIGITAL | IOD_EP2_TCP | 6 | 00006 | AlarmGenPMM1
EP2_AlarmGenPMM2 | DIGITAL | IOD_EP2_TCP | 7 | 00007 | AlarmGenPMM2
EP2_AlarmGenPMM3 | DIGITAL | IOD_EP2_TCP | 8 | 00008 | AlarmGenPMM3
EP2_AlarmGenUPS1 | DIGITAL | IOD_EP2_TCP | 9 | 00009 | AlarmGenUPS1
EP2_AlarmGenUPS2 | DIGITAL | IOD_EP2_TCP | 10 | 00010 | AlarmGenUPS2
EP2_ComSCADA | DIGITAL | IOD_EP2_TCP | 11 | 00011 | ComSCADA
EP2_ComSCADA1 | DIGITAL | IOD_EP2_TCP | 12 | 00012 | ComSCADA1
EP2_DI_Klima5_ERR | DIGITAL | IOD_EP2_TCP | 13 | 00013 | DI_Klima5_ERR
EP2_DI_Klima5_ON | DIGITAL | IOD_EP2_TCP | 14 | 00014 | DI_Klima5_ON
EP2_DI_Klima6_ERR | DIGITAL | IOD_EP2_TCP | 15 | 00015 | DI_Klima6_ERR
EP2_DI_Klima6_ON | DIGITAL | IOD_EP2_TCP | 16 | 00016 | DI_Klima6_ON
EP2_DI_KlimaSplit1_ERR | DIGITAL | IOD_EP2_TCP | 17 | 00017 | DI_KlimaSplit1_ERR
EP2_DI_KlimaSplit1_ON | DIGITAL | IOD_EP2_TCP | 18 | 00018 | DI_KlimaSplit1_ON
EP2_DI_Q10_OdcKlima6_IZP | DIGITAL | IOD_EP2_TCP | 19 | 00019 | DI_Q10_OdcKlima6_IZP
EP2_DI_Q10_OdcKlima6_ON | DIGITAL | IOD_EP2_TCP | 20 | 00020 | DI_Q10_OdcKlima6_ON
EP2_DI_Q11_OdcVent1_ON | DIGITAL | IOD_EP2_TCP | 21 | 00021 | DI_Q11_OdcVent1_ON
EP2_DI_Q12_Rezerva_ON | DIGITAL | IOD_EP2_TCP | 22 | 00022 | DI_Q12_Rezerva_ON
EP2_DI_Q1_GlavnoStikalo_ON | DIGITAL | IOD_EP2_TCP | 23 | 00023 | DI_Q1_GlavnoStikalo_ON
EP2_DI_Q25_OdcUpsA_IZP | DIGITAL | IOD_EP2_TCP | 24 | 00024 | DI_Q25_OdcUpsA_IZP
EP2_DI_Q25_OdcUpsA_ON | DIGITAL | IOD_EP2_TCP | 25 | 00025 | DI_Q25_OdcUpsA_ON
EP2_DI_Q26_OdcByA_IZP | DIGITAL | IOD_EP2_TCP | 26 | 00026 | DI_Q26_OdcByA_IZP
EP2_DI_Q26_OdcByA_ON | DIGITAL | IOD_EP2_TCP | 27 | 00027 | DI_Q26_OdcByA_ON
EP2_DI_Q27_OdcByUpsA_IZP | DIGITAL | IOD_EP2_TCP | 28 | 00028 | DI_Q27_OdcByUpsA_IZP
EP2_DI_Q27_OdcByUpsA_ON | DIGITAL | IOD_EP2_TCP | 29 | 00029 | DI_Q27_OdcByUpsA_ON
EP2_DI_Q28_OdcUpsB_IZP | DIGITAL | IOD_EP2_TCP | 30 | 00030 | DI_Q28_OdcUpsB_IZP
EP2_DI_Q28_OdcUpsB_ON | DIGITAL | IOD_EP2_TCP | 31 | 00031 | DI_Q28_OdcUpsB_ON
EP2_DI_Q29_OdcByB_IZP | DIGITAL | IOD_EP2_TCP | 32 | 00032 | DI_Q29_OdcByB_IZP
EP2_DI_Q29_OdcByB_ON | DIGITAL | IOD_EP2_TCP | 33 | 00033 | DI_Q29_OdcByB_ON
EP2_DI_Q2_Rezerva_IZP | DIGITAL | IOD_EP2_TCP | 34 | 00034 | DI_Q2_Rezerva_IZP
EP2_DI_Q2_Rezerva_ON | DIGITAL | IOD_EP2_TCP | 35 | 00035 | DI_Q2_Rezerva_ON
EP2_DI_Q30_OdcByUpsB_IZP | DIGITAL | IOD_EP2_TCP | 36 | 00036 | DI_Q30_OdcByUpsB_IZP
EP2_DI_Q30_OdcByUpsB_ON | DIGITAL | IOD_EP2_TCP | 37 | 00037 | DI_Q30_OdcByUpsB_ON
EP2_DI_Q31_DovByUpsA_ON | DIGITAL | IOD_EP2_TCP | 38 | 00038 | DI_Q31_DovByUpsA_ON
EP2_DI_Q32_DovByA_ON | DIGITAL | IOD_EP2_TCP | 39 | 00039 | DI_Q32_DovByA_ON
EP2_DI_Q33_DovByUpsB_ON | DIGITAL | IOD_EP2_TCP | 40 | 00040 | DI_Q33_DovByUpsB_ON
EP2_DI_Q34_DovByB_ON | DIGITAL | IOD_EP2_TCP | 41 | 00041 | DI_Q34_DovByB_ON
EP2_DI_Q5_OdcKlima1_IZP | DIGITAL | IOD_EP2_TCP | 42 | 00042 | DI_Q5_OdcKlima1_IZP
EP2_DI_Q5_OdcKlima1_ON | DIGITAL | IOD_EP2_TCP | 43 | 00043 | DI_Q5_OdcKlima1_ON
EP2_DI_Q6_OdcKlima2_IZP | DIGITAL | IOD_EP2_TCP | 44 | 00044 | DI_Q6_OdcKlima2_IZP
EP2_DI_Q6_OdcKlima2_ON | DIGITAL | IOD_EP2_TCP | 45 | 00045 | DI_Q6_OdcKlima2_ON
EP2_DI_Q7_OdcKlima3_IZP | DIGITAL | IOD_EP2_TCP | 46 | 00046 | DI_Q7_OdcKlima3_IZP
EP2_DI_Q7_OdcKlima3_ON | DIGITAL | IOD_EP2_TCP | 47 | 00047 | DI_Q7_OdcKlima3_ON
EP2_DI_Q8_OdcKlima4_IZP | DIGITAL | IOD_EP2_TCP | 48 | 00048 | DI_Q8_OdcKlima4_IZP
EP2_DI_Q8_OdcKlima4_ON | DIGITAL | IOD_EP2_TCP | 49 | 00049 | DI_Q8_OdcKlima4_ON
EP2_DI_Q9_OdcKlima5_IZP | DIGITAL | IOD_EP2_TCP | 50 | 00050 | DI_Q9_OdcKlima5_IZP
EP2_DI_Q9_OdcKlima5_ON | DIGITAL | IOD_EP2_TCP | 51 | 00051 | DI_Q9_OdcKlima5_ON
EP2_DI_RazlitjeVodeK5K6 | DIGITAL | IOD_EP2_TCP | 52 | 00052 | DI_RazlitjeVodeK5K6
EP2_DI_UPS_Alarm | DIGITAL | IOD_EP2_TCP | 53 | 00053 | DI_UPS_Alarm
EP2_DI_UPS_BatNacin | DIGITAL | IOD_EP2_TCP | 54 | 00054 | DI_UPS_BatNacin
EP2_DI_UPS_Polnjenje | DIGITAL | IOD_EP2_TCP | 55 | 00055 | DI_UPS_Polnjenje
EP2_DI_UpsA_ERR | DIGITAL | IOD_EP2_TCP | 56 | 00056 | DIN_UpsA_ERR
EP2_DI_UpsA_ON | DIGITAL | IOD_EP2_TCP | 57 | 00057 | DIN_UpsA_BypassON
EP2_DI_UpsB_ERR | DIGITAL | IOD_EP2_TCP | 58 | 00058 | DIN_UpsB_ERR
EP2_DI_UpsB_ON | DIGITAL | IOD_EP2_TCP | 59 | 00059 | DIN_UpsB_BypassON
EP2_DO_Klima5_Izklop | DIGITAL | IOD_EP2_TCP | 60 | 00060 | DO_Klima5_Izklop
EP2_DO_Klima6_Izklop | DIGITAL | IOD_EP2_TCP | 61 | 00061 | DO_Klima6_Izklop
EP2_ErrComCirc1 | DIGITAL | IOD_EP2_TCP | 62 | 00062 | ErrComCirc[1]
EP2_ErrComCirc2 | DIGITAL | IOD_EP2_TCP | 63 | 00063 | ErrComCirc[2]
EP2_ErrComCirc3 | DIGITAL | IOD_EP2_TCP | 64 | 00064 | ErrComCirc[3]
EP2_ErrComCirc4 | DIGITAL | IOD_EP2_TCP | 65 | 00065 | ErrComCirc[4]
EP2_ErrComCirc5 | DIGITAL | IOD_EP2_TCP | 66 | 00066 | ErrComCirc[5]
EP2_ErrComKlima1 | DIGITAL | IOD_EP2_TCP | 67 | 00067 | ErrComKlima[1]
EP2_ErrComKlima2 | DIGITAL | IOD_EP2_TCP | 68 | 00068 | ErrComKlima[2]
EP2_ErrComKlima3 | DIGITAL | IOD_EP2_TCP | 69 | 00069 | ErrComKlima[3]
EP2_ErrComKlima4 | DIGITAL | IOD_EP2_TCP | 70 | 00070 | ErrComKlima[4]
EP2_ErrComKlima5 | DIGITAL | IOD_EP2_TCP | 71 | 00071 | ErrComKlima[5]
EP2_ErrComKlima6 | DIGITAL | IOD_EP2_TCP | 72 | 00072 | ErrComKlima[6]
EP2_ErrCommScada | DIGITAL | IOD_EP2_TCP | 73 | 00073 | ErrCommScada
EP2_ErrComPanelPLC | DIGITAL | IOD_EP2_TCP | 74 | 00074 | ErrComPanelPLC
EP2_ErrComPMM1 | DIGITAL | IOD_EP2_TCP | 75 | 00075 | ErrComPMM[1]
EP2_ErrComPMM2 | DIGITAL | IOD_EP2_TCP | 76 | 00076 | ErrComPMM[2]
EP2_ErrComPMM3 | DIGITAL | IOD_EP2_TCP | 77 | 00077 | ErrComPMM[3]
EP2_ErrComPort2 | DIGITAL | IOD_EP2_TCP | 78 | 00078 | ErrComPort2
EP2_ErrComPort3 | DIGITAL | IOD_EP2_TCP | 79 | 00079 | ErrComPort3
EP2_ErrComPort4 | DIGITAL | IOD_EP2_TCP | 80 | 00080 | ErrComPort4
EP2_ErrComUPS1 | DIGITAL | IOD_EP2_TCP | 81 | 00081 | ErrComUPS[1]
EP2_ErrComUPS2 | DIGITAL | IOD_EP2_TCP | 82 | 00082 | ErrComUPS[2]
EP2_Klima1_AlarmKompresor1 | DIGITAL | IOD_EP2_TCP | 83 | 00083 | Klima[1].AlarmKompresor1
EP2_Klima1_AlarmKompresor2 | DIGITAL | IOD_EP2_TCP | 84 | 00084 | Klima[1].AlarmKompresor2
EP2_Klima1_Deluje | DIGITAL | IOD_EP2_TCP | 85 | 00085 | Klima[1].Deluje
EP2_Klima1_EnergySaving | DIGITAL | IOD_EP2_TCP | 86 | 00086 | Klima[1].EnergySaving
EP2_Klima1_FaultyEPROM | DIGITAL | IOD_EP2_TCP | 87 | 00087 | Klima[1].FaultyEPROM
EP2_Klima1_FenThermalCutout | DIGITAL | IOD_EP2_TCP | 88 | 00088 | Klima[1].FenThermalCutout
EP2_Klima1_GeneralAlarm | DIGITAL | IOD_EP2_TCP | 89 | 00089 | Klima[1].GeneralAlarm
EP2_Klima1_Kompresor1naMejiObrUr | DIGITAL | IOD_EP2_TCP | 90 | 00090 | Klima[1].Kompresor1naMejiObrUr
EP2_Klima1_Kompresor2naMejiObrUr | DIGITAL | IOD_EP2_TCP | 91 | 00091 | Klima[1].Kompresor2naMejiObrUr
EP2_Klima1_Napaka | DIGITAL | IOD_EP2_TCP | 92 | 00092 | Klima[1].Napaka
EP2_Klima1_NapakaPriPretokuZraka | DIGITAL | IOD_EP2_TCP | 93 | 00093 | Klima[1].NapakaPriPretokuZraka
EP2_Klima1_NapakaSenzorPovratVod | DIGITAL | IOD_EP2_TCP | 94 | 00094 | Klima[1].NapakaSenzorPovratVode
EP2_Klima1_NapakaSenzorTempIzpih | DIGITAL | IOD_EP2_TCP | 95 | 00095 | Klima[1].NapakaSenzorTempIzpiha
EP2_Klima1_NapakaSenzorTempProst | DIGITAL | IOD_EP2_TCP | 96 | 00096 | Klima[1].NapakaSenzorTempProstora
EP2_Klima1_NapakaSenzorVlaznosti | DIGITAL | IOD_EP2_TCP | 97 | 00097 | Klima[1].NapakaSenzorVlaznosti
EP2_Klima1_NapakaSenzorZunanjeTemp | DIGITAL | IOD_EP2_TCP | 98 | 00098 | Klima[1].NapakaSenzorZunanjeTemp
EP2_Klima1_NiTokaVVlazilcu | DIGITAL | IOD_EP2_TCP | 99 | 00099 | Klima[1].NiTokaVVlazilcu
EP2_Klima1_NiVodeVVlazilcu | DIGITAL | IOD_EP2_TCP | 100 | 00100 | Klima[1].NiVodeVVlazilcu
EP2_Klima1_NizekPritiskKompresor1 | DIGITAL | IOD_EP2_TCP | 101 | 00101 | Klima[1].NizekPritiskKompresor1
EP2_Klima1_NizekPritiskKompresor2 | DIGITAL | IOD_EP2_TCP | 102 | 00102 | Klima[1].NizekPritiskKompresor2
EP2_Klima1_NizkaTempPovratneVode | DIGITAL | IOD_EP2_TCP | 103 | 00103 | Klima[1].NizkaTempPovratneVode
EP2_Klima1_NizkaTempVProstoru | DIGITAL | IOD_EP2_TCP | 104 | 00104 | Klima[1].NizkaTempVProstoru
EP2_Klima1_NizkaVlaznost | DIGITAL | IOD_EP2_TCP | 105 | 00105 | Klima[1].NizkaVlaznost
EP2_Klima1_OnOffEnablingBySupervisor | DIGITAL | IOD_EP2_TCP | 106 | 00106 | Klima[1].OnOffEnablingBySupervisor
EP2_Klima1_PozarniAlarm | DIGITAL | IOD_EP2_TCP | 107 | 00107 | Klima[1].PozarniAlarm
EP2_Klima1_Razvlazevanje | DIGITAL | IOD_EP2_TCP | 108 | 00108 | Klima[1].Razvlazevanje
EP2_Klima1_RemoteOFFtoOutput | DIGITAL | IOD_EP2_TCP | 109 | 00109 | Klima[1].RemoteOFFtoOutput
EP2_Klima1_RemoteOnOff | DIGITAL | IOD_EP2_TCP | 110 | 00110 | Klima[1].RemoteOnOff
EP2_Klima1_RocniIzklop | DIGITAL | IOD_EP2_TCP | 111 | 00111 | Klima[1].RocniIzklop
EP2_Klima1_SenzorjiStatus | DIGITAL | IOD_EP2_TCP | 112 | 00112 | Klima[1].SenzorjiStatus
EP2_Klima1_StoppedByAlarms | DIGITAL | IOD_EP2_TCP | 113 | 00113 | Klima[1].StoppedByAlarms
EP2_Klima1_ThermalCutoutHeater1 | DIGITAL | IOD_EP2_TCP | 114 | 00114 | Klima[1].ThermalCutoutHeater1
EP2_Klima1_ThermalCutoutHeater2 | DIGITAL | IOD_EP2_TCP | 115 | 00115 | Klima[1].ThermalCutoutHeater2
EP2_Klima1_UnitOnOff | DIGITAL | IOD_EP2_TCP | 116 | 00116 | Klima[1].UnitOnOff
EP2_Klima1_VentilatorNaMejiObrUr | DIGITAL | IOD_EP2_TCP | 117 | 00117 | Klima[1].VentilatorNaMejiObrUr
EP2_Klima1_VentilGretjeOdpiranje | DIGITAL | IOD_EP2_TCP | 118 | 00118 | Klima[1].VentilGretjeOdpiranje
EP2_Klima1_VentilGretjeZapiranje | DIGITAL | IOD_EP2_TCP | 119 | 00119 | Klima[1].VentilGretjeZapiranje
EP2_Klima1_VentilHlajenjeOdpiranje | DIGITAL | IOD_EP2_TCP | 120 | 00120 | Klima[1].VentilHlajenjeOdpiranje
EP2_Klima1_VentilHlajenjeZapiranje | DIGITAL | IOD_EP2_TCP | 121 | 00121 | Klima[1].VentilHlajenjeZapiranje
EP2_Klima1_VisokaTempPovratneVode | DIGITAL | IOD_EP2_TCP | 122 | 00122 | Klima[1].VisokaTempPovratneVode
EP2_Klima1_VisokaTempVProstoru | DIGITAL | IOD_EP2_TCP | 123 | 00123 | Klima[1].VisokaTempVProstoru
EP2_Klima1_VisokaVlaznost | DIGITAL | IOD_EP2_TCP | 124 | 00124 | Klima[1].VisokaVlaznost
EP2_Klima1_VisokTokVVlazilcu | DIGITAL | IOD_EP2_TCP | 125 | 00125 | Klima[1].VisokTokVVlazilcu
EP2_Klima1_Vlazenje | DIGITAL | IOD_EP2_TCP | 126 | 00126 | Klima[1].Vlazenje
EP2_Klima1_ZamasenFilter | DIGITAL | IOD_EP2_TCP | 127 | 00127 | Klima[1].ZamasenFilter
EP2_Klima2_AlarmKompresor1 | DIGITAL | IOD_EP2_TCP | 128 | 00128 | Klima[2].AlarmKompresor1
EP2_Klima2_AlarmKompresor2 | DIGITAL | IOD_EP2_TCP | 129 | 00129 | Klima[2].AlarmKompresor2
EP2_Klima2_Deluje | DIGITAL | IOD_EP2_TCP | 130 | 00130 | Klima[2].Deluje
EP2_Klima2_EnergySaving | DIGITAL | IOD_EP2_TCP | 131 | 00131 | Klima[2].EnergySaving
EP2_Klima2_FaultyEPROM | DIGITAL | IOD_EP2_TCP | 132 | 00132 | Klima[2].FaultyEPROM
EP2_Klima2_FenThermalCutout | DIGITAL | IOD_EP2_TCP | 133 | 00133 | Klima[2].FenThermalCutout
EP2_Klima2_GeneralAlarm | DIGITAL | IOD_EP2_TCP | 134 | 00134 | Klima[2].GeneralAlarm
EP2_Klima2_Kompresor1naMejiObrUr | DIGITAL | IOD_EP2_TCP | 135 | 00135 | Klima[2].Kompresor1naMejiObrUr
EP2_Klima2_Kompresor2naMejiObrUr | DIGITAL | IOD_EP2_TCP | 136 | 00136 | Klima[2].Kompresor2naMejiObrUr
EP2_Klima2_Napaka | DIGITAL | IOD_EP2_TCP | 137 | 00137 | Klima[2].Napaka
EP2_Klima2_NapakaPriPretokuZraka | DIGITAL | IOD_EP2_TCP | 138 | 00138 | Klima[2].NapakaPriPretokuZraka
EP2_Klima2_NapakaSenzorPovratVode | DIGITAL | IOD_EP2_TCP | 139 | 00139 | Klima[2].NapakaSenzorPovratVode
EP2_Klima2_NapakaSenzorTempIzpih | DIGITAL | IOD_EP2_TCP | 140 | 00140 | Klima[2].NapakaSenzorTempIzpiha
EP2_Klima2_NapakaSenzorTempProst | DIGITAL | IOD_EP2_TCP | 141 | 00141 | Klima[2].NapakaSenzorTempProstora
EP2_Klima2_NapakaSenzorVlaznosti | DIGITAL | IOD_EP2_TCP | 142 | 00142 | Klima[2].NapakaSenzorVlaznosti
EP2_Klima2_NapakaSenzorZunanjeTemp | DIGITAL | IOD_EP2_TCP | 143 | 00143 | Klima[2].NapakaSenzorZunanjeTemp
EP2_Klima2_NiTokaVVlazilcu | DIGITAL | IOD_EP2_TCP | 144 | 00144 | Klima[2].NiTokaVVlazilcu
EP2_Klima2_NiVodeVVlazilcu | DIGITAL | IOD_EP2_TCP | 145 | 00145 | Klima[2].NiVodeVVlazilcu
EP2_Klima2_NizekPritiskKompresor1 | DIGITAL | IOD_EP2_TCP | 146 | 00146 | Klima[2].NizekPritiskKompresor1
EP2_Klima2_NizekPritiskKompresor2 | DIGITAL | IOD_EP2_TCP | 147 | 00147 | Klima[2].NizekPritiskKompresor2
EP2_Klima2_NizkaTempPovratneVode | DIGITAL | IOD_EP2_TCP | 148 | 00148 | Klima[2].NizkaTempPovratneVode
EP2_Klima2_NizkaTempVProstoru | DIGITAL | IOD_EP2_TCP | 149 | 00149 | Klima[2].NizkaTempVProstoru
EP2_Klima2_NizkaVlaznost | DIGITAL | IOD_EP2_TCP | 150 | 00150 | Klima[2].NizkaVlaznost
EP2_Klima2_OnOffEnablingBySupervisor | DIGITAL | IOD_EP2_TCP | 151 | 00151 | Klima[2].OnOffEnablingBySupervisor
EP2_Klima2_PozarniAlarm | DIGITAL | IOD_EP2_TCP | 152 | 00152 | Klima[2].PozarniAlarm
EP2_Klima2_Razvlazevanje | DIGITAL | IOD_EP2_TCP | 153 | 00153 | Klima[2].Razvlazevanje
EP2_Klima2_RemoteOFFtoOutput | DIGITAL | IOD_EP2_TCP | 154 | 00154 | Klima[2].RemoteOFFtoOutput
EP2_Klima2_RemoteOnOff | DIGITAL | IOD_EP2_TCP | 155 | 00155 | Klima[2].RemoteOnOff
EP2_Klima2_RocniIzklop | DIGITAL | IOD_EP2_TCP | 156 | 00156 | Klima[2].RocniIzklop
EP2_Klima2_SenzorjiStatus | DIGITAL | IOD_EP2_TCP | 157 | 00157 | Klima[2].SenzorjiStatus
EP2_Klima2_StoppedByAlarms | DIGITAL | IOD_EP2_TCP | 158 | 00158 | Klima[2].StoppedByAlarms
EP2_Klima2_ThermalCutoutHeater1 | DIGITAL | IOD_EP2_TCP | 159 | 00159 | Klima[2].ThermalCutoutHeater1
EP2_Klima2_ThermalCutoutHeater2 | DIGITAL | IOD_EP2_TCP | 160 | 00160 | Klima[2].ThermalCutoutHeater2
EP2_Klima2_UnitOnOff | DIGITAL | IOD_EP2_TCP | 161 | 00161 | Klima[2].UnitOnOff
EP2_Klima2_VentilatorNaMejiObrUr | DIGITAL | IOD_EP2_TCP | 162 | 00162 | Klima[2].VentilatorNaMejiObrUr
EP2_Klima2_VentilGretjeOdpiranje | DIGITAL | IOD_EP2_TCP | 163 | 00163 | Klima[2].VentilGretjeOdpiranje
EP2_Klima2_VentilGretjeZapiranje | DIGITAL | IOD_EP2_TCP | 164 | 00164 | Klima[2].VentilGretjeZapiranje
EP2_Klima2_VentilHlajenjeOdpiranje | DIGITAL | IOD_EP2_TCP | 165 | 00165 | Klima[2].VentilHlajenjeOdpiranje
EP2_Klima2_VentilHlajenjeZapiranje | DIGITAL | IOD_EP2_TCP | 166 | 00166 | Klima[2].VentilHlajenjeZapiranje
EP2_Klima2_VisokaTempPovratneVod | DIGITAL | IOD_EP2_TCP | 167 | 00167 | Klima[2].VisokaTempPovratneVode
EP2_Klima2_VisokaTempVProstoru | DIGITAL | IOD_EP2_TCP | 168 | 00168 | Klima[2].VisokaTempVProstoru
EP2_Klima2_VisokaVlaznost | DIGITAL | IOD_EP2_TCP | 169 | 00169 | Klima[2].VisokaVlaznost
EP2_Klima2_VisokTokVVlazilcu | DIGITAL | IOD_EP2_TCP | 170 | 00170 | Klima[2].VisokTokVVlazilcu
EP2_Klima2_Vlazenje | DIGITAL | IOD_EP2_TCP | 171 | 00171 | Klima[2].Vlazenje
EP2_Klima2_ZamasenFilter | DIGITAL | IOD_EP2_TCP | 172 | 00172 | Klima[2].ZamasenFilter
EP2_KlimeNaCas | DIGITAL | IOD_EP2_TCP | 173 | 00173 | KlimeNaCas
EP2_NapakaSenzorTemp1 | DIGITAL | IOD_EP2_TCP | 174 | 00174 | NapakaSenzorTemp[1]
EP2_NapakaSenzorTemp2 | DIGITAL | IOD_EP2_TCP | 175 | 00175 | NapakaSenzorTemp[2]
EP2_NapakaSenzorVlaga1 | DIGITAL | IOD_EP2_TCP | 176 | 00176 | NapakaSenzorVlaga[1]
EP2_NapakaSenzorVlaga2 | DIGITAL | IOD_EP2_TCP | 177 | 00177 | NapakaSenzorVlaga[2]
EP2_PMM1OverCurrentBetw1 | DIGITAL | IOD_EP2_TCP | 178 | 00178 | PMM1OverCurrentBetw[1]
EP2_PMM1OverCurrentBetw2 | DIGITAL | IOD_EP2_TCP | 179 | 00179 | PMM1OverCurrentBetw[2]
EP2_PMM1OverCurrentBetw3 | DIGITAL | IOD_EP2_TCP | 180 | 00180 | PMM1OverCurrentBetw[3]
EP2_PMM1OverCurrentOver1 | DIGITAL | IOD_EP2_TCP | 181 | 00181 | PMM1OverCurrentOver[1]
EP2_PMM1OverCurrentOver2 | DIGITAL | IOD_EP2_TCP | 182 | 00182 | PMM1OverCurrentOver[2]
EP2_PMM1OverCurrentOver3 | DIGITAL | IOD_EP2_TCP | 183 | 00183 | PMM1OverCurrentOver[3]
EP2_PMM2OverCurrentBetw1 | DIGITAL | IOD_EP2_TCP | 184 | 00184 | PMM2OverCurrentBetw[1]
EP2_PMM2OverCurrentBetw2 | DIGITAL | IOD_EP2_TCP | 185 | 00185 | PMM2OverCurrentBetw[2]
EP2_PMM2OverCurrentBetw3 | DIGITAL | IOD_EP2_TCP | 186 | 00186 | PMM2OverCurrentBetw[3]
EP2_PMM2OverCurrentOver1 | DIGITAL | IOD_EP2_TCP | 187 | 00187 | PMM2OverCurrentOver[1]
EP2_PMM2OverCurrentOver2 | DIGITAL | IOD_EP2_TCP | 188 | 00188 | PMM2OverCurrentOver[2]
EP2_PMM2OverCurrentOver3 | DIGITAL | IOD_EP2_TCP | 189 | 00189 | PMM2OverCurrentOver[3]
EP2_PMM3OverCurrentBetw1 | DIGITAL | IOD_EP2_TCP | 190 | 00190 | PMM3OverCurrentBetw[1]
EP2_PMM3OverCurrentBetw2 | DIGITAL | IOD_EP2_TCP | 191 | 00191 | PMM3OverCurrentBetw[2]
EP2_PMM3OverCurrentBetw3 | DIGITAL | IOD_EP2_TCP | 192 | 00192 | PMM3OverCurrentBetw[3]
EP2_PMM3OverCurrentOver1 | DIGITAL | IOD_EP2_TCP | 193 | 00193 | PMM3OverCurrentOver[1]
EP2_PMM3OverCurrentOver2 | DIGITAL | IOD_EP2_TCP | 194 | 00194 | PMM3OverCurrentOver[2]
EP2_PMM3OverCurrentOver3 | DIGITAL | IOD_EP2_TCP | 195 | 00195 | PMM3OverCurrentOver[3]
EP2_PMM1_Napaka | DIGITAL | IOD_EP2_TCP | 196 | 00196 | PMM[1].Napaka
EP2_PMM2_Napaka | DIGITAL | IOD_EP2_TCP | 197 | 00197 | PMM[2].Napaka
EP2_PMM3_Napaka | DIGITAL | IOD_EP2_TCP | 198 | 00198 | PMM[3].Napaka
EP2_SetDateTime | DIGITAL | IOD_EP2_TCP | 199 | 00199 | SetDateTime
EP2_SetDateTimeDemand | DIGITAL | IOD_EP2_TCP | 200 | 00200 | SetDateTimeDemand
EP2_SetDateTimeError | DIGITAL | IOD_EP2_TCP | 201 | 00201 | SetDateTimeError
EP2_SetDateTimeFinished | DIGITAL | IOD_EP2_TCP | 202 | 00202 | SetDateTimeFinished
EP2_SetRemoteOnOff1 | DIGITAL | IOD_EP2_TCP | 203 | 00203 | SetRemoteOnOff[1]
EP2_SetRemoteOnOff2 | DIGITAL | IOD_EP2_TCP | 204 | 00204 | SetRemoteOnOff[2]
EP2_SlabaBaterijaPLC_A1 | DIGITAL | IOD_EP2_TCP | 205 | 00205 | SlabaBaterijaPLC_A1
EP2_TempTSprevisoka1 | DIGITAL | IOD_EP2_TCP | 206 | 00206 | TempTSprevisoka[1]
EP2_TempTSprevisoka2 | DIGITAL | IOD_EP2_TCP | 207 | 00207 | TempTSprevisoka[2]
EP2UPS1AlarmAwaitingPower | DIGITAL | IOD_EP2_TCP | 208 | 00208 | UPS[1].AlarmAwaitingPower
EP2UPS1AlarmBypassBad | DIGITAL | IOD_EP2_TCP | 209 | 00209 | UPS[1].AlarmBypassBad
EP2UPS1AlarmChargerFailed | DIGITAL | IOD_EP2_TCP | 210 | 00210 | UPS[1].AlarmChargerFailed
EP2UPS1AlarmCommunicationsLost | DIGITAL | IOD_EP2_TCP | 211 | 00211 | UPS[1].AlarmCommunicationsLost
EP2UPS1AlarmDepletedBattery | DIGITAL | IOD_EP2_TCP | 212 | 00212 | UPS[1].AlarmDepletedBattery
EP2UPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_EP2_TCP | 213 | 00213 | UPS[1].AlarmDiagnosticTestFailed
EP2UPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_EP2_TCP | 214 | 00214 | UPS[1].AlarmIzhodOffKotZahtevano
EP2UPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_EP2_TCP | 215 | 00215 | UPS[1].AlarmIzhodPreobremenjen
EP2UPS1AlarmLowBattery | DIGITAL | IOD_EP2_TCP | 216 | 00216 | UPS[1].AlarmLowBattery
EP2UPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_EP2_TCP | 217 | 00217 | UPS[1].AlarmNapakaNaVarovalki
EP2UPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_EP2_TCP | 218 | 00218 | UPS[1].AlarmNapakaNaVentilatorju
EP2UPS1AlarmOnBattery | DIGITAL | IOD_EP2_TCP | 219 | 00219 | UPS[1].AlarmOnBattery
EP2UPS1AlarmOnBypass | DIGITAL | IOD_EP2_TCP | 220 | 00220 | UPS[1].AlarmOnBypass
EP2UPS1AlarmInverterError | DIGITAL | IOD_EP2_TCP | 221 | 00221 | UPS[1].AlarmInverterError
EP2UPS1AlarmShutdownImminent | DIGITAL | IOD_EP2_TCP | 222 | 00222 | UPS[1].AlarmShutdownImminent
EP2UPS1AlarmShutdownPending | DIGITAL | IOD_EP2_TCP | 223 | 00223 | UPS[1].AlarmShutdownPending
EP2UPS1AlarmSlabaBaterija | DIGITAL | IOD_EP2_TCP | 224 | 00224 | UPS[1].AlarmSlabaBaterija
EP2UPS1AlarmSplosnaNapaka | DIGITAL | IOD_EP2_TCP | 225 | 00225 | UPS[1].AlarmSplosnaNapaka
EP2UPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_EP2_TCP | 226 | 00226 | UPS[1].AlarmStanjeIzhodaIzvenToleranc
EP2UPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_EP2_TCP | 227 | 00227 | UPS[1].AlarmStanjeVhodaIzvenToleranc
EP2UPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_EP2_TCP | 228 | 00228 | UPS[1].AlarmTemperaturaIzvenToleranc
EP2UPS1AlarmTestInProgres | DIGITAL | IOD_EP2_TCP | 229 | 00229 | UPS[1].AlarmTestInProgres
EP2UPS1AlarmUPSIzhodOff | DIGITAL | IOD_EP2_TCP | 230 | 00230 | UPS[1].AlarmUPSIzhodOff
EP2UPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_EP2_TCP | 231 | 00231 | UPS[1].AlarmUPSOffKotZahtevano
EP2UPS1AlarmUPSSystemOff | DIGITAL | IOD_EP2_TCP | 232 | 00232 | UPS[1].AlarmUPSSystemOff
EP2UPS1Napaka | DIGITAL | IOD_EP2_TCP | 233 | 00233 | UPS[1].Napaka
EP2UPS1StatusEcomodeAktiven | DIGITAL | IOD_EP2_TCP | 234 | 00234 | UPS[1].StatusEcomodeAktiven
EP2UPS1StatusInverterIsOn | DIGITAL | IOD_EP2_TCP | 235 | 00235 | UPS[1].StatusInverterIsOn
EP2UPS1StatusStopOperation | DIGITAL | IOD_EP2_TCP | 236 | 00236 | UPS[1].StatusStopOperation
EP2UPS2AlarmAwaitingPower | DIGITAL | IOD_EP2_TCP | 237 | 00237 | UPS[2].AlarmAwaitingPower
EP2UPS2AlarmBypassBad | DIGITAL | IOD_EP2_TCP | 238 | 00238 | UPS[2].AlarmBypassBad
EP2UPS2AlarmChargerFailed | DIGITAL | IOD_EP2_TCP | 239 | 00239 | UPS[2].AlarmChargerFailed
EP2UPS2AlarmCommunicationsLost | DIGITAL | IOD_EP2_TCP | 240 | 00240 | UPS[2].AlarmCommunicationsLost
EP2UPS2AlarmDepletedBattery | DIGITAL | IOD_EP2_TCP | 241 | 00241 | UPS[2].AlarmDepletedBattery
EP2UPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_EP2_TCP | 242 | 00242 | UPS[2].AlarmDiagnosticTestFailed
EP2UPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_EP2_TCP | 243 | 00243 | UPS[2].AlarmIzhodOffKotZahtevano
EP2UPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_EP2_TCP | 244 | 00244 | UPS[2].AlarmIzhodPreobremenjen
EP2UPS2AlarmLowBattery | DIGITAL | IOD_EP2_TCP | 245 | 00245 | UPS[2].AlarmLowBattery
EP2UPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_EP2_TCP | 246 | 00246 | UPS[2].AlarmNapakaNaVarovalki
EP2UPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_EP2_TCP | 247 | 00247 | UPS[2].AlarmNapakaNaVentilatorju
EP2UPS2AlarmOnBattery | DIGITAL | IOD_EP2_TCP | 248 | 00248 | UPS[2].AlarmOnBattery
EP2UPS2AlarmOnBypass | DIGITAL | IOD_EP2_TCP | 249 | 00249 | UPS[2].AlarmOnBypass
EP2UPS2AlarmInverterError | DIGITAL | IOD_EP2_TCP | 250 | 00250 | UPS[2].AlarmInverterError
EP2UPS2AlarmShutdownImminent | DIGITAL | IOD_EP2_TCP | 251 | 00251 | UPS[2].AlarmShutdownImminent
EP2UPS2AlarmShutdownPending | DIGITAL | IOD_EP2_TCP | 252 | 00252 | UPS[2].AlarmShutdownPending
EP2UPS2AlarmSlabaBaterija | DIGITAL | IOD_EP2_TCP | 253 | 00253 | UPS[2].AlarmSlabaBaterija
EP2UPS2AlarmSplosnaNapaka | DIGITAL | IOD_EP2_TCP | 254 | 00254 | UPS[2].AlarmSplosnaNapaka
EP2UPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_EP2_TCP | 255 | 00255 | UPS[2].AlarmStanjeIzhodaIzvenToleranc
EP2UPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_EP2_TCP | 256 | 00256 | UPS[2].AlarmStanjeVhodaIzvenToleranc
EP2UPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_EP2_TCP | 257 | 00257 | UPS[2].AlarmTemperaturaIzvenToleranc
EP2UPS2AlarmTestInProgres | DIGITAL | IOD_EP2_TCP | 258 | 00258 | UPS[2].AlarmTestInProgres
EP2UPS2AlarmUPSIzhodOff | DIGITAL | IOD_EP2_TCP | 259 | 00259 | UPS[2].AlarmUPSIzhodOff
EP2UPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_EP2_TCP | 260 | 00260 | UPS[2].AlarmUPSOffKotZahtevano
EP2UPS2AlarmUPSSystemOff | DIGITAL | IOD_EP2_TCP | 261 | 00261 | UPS[2].AlarmUPSSystemOff
EP2UPS2Napaka | DIGITAL | IOD_EP2_TCP | 262 | 00262 | UPS[2].Napaka
EP2UPS2StatusEcomodeAktiven | DIGITAL | IOD_EP2_TCP | 263 | 00263 | UPS[2].StatusEcomodeAktiven
EP2UPS2StatusInverterIsOn | DIGITAL | IOD_EP2_TCP | 264 | 00264 | UPS[2].StatusInverterIsOn
EP2UPS2StatusStopOperation | DIGITAL | IOD_EP2_TCP | 265 | 00265 | UPS[2].StatusStopOperation
EP2_UserLoggedIn | DIGITAL | IOD_EP2_TCP | 266 | 00266 | UserLoggedIn
EP2_XVH_AlarmOn | DIGITAL | IOD_EP2_TCP | 267 | 00267 | XVH_AlarmOn
EP2AlarmGenRest | DIGITAL | IOD_EP2_TCP | 268 | 00268 | AlarmGenRest
EP2DI_UpsA_BypassON | DIGITAL | IOD_EP2_TCP | 269 | 00269 | DI_UpsA_BypassON
EP2DI_UpsA_ERR | DIGITAL | IOD_EP2_TCP | 270 | 00270 | DI_UpsA_ERR
EP2DI_UpsB_BypassON | DIGITAL | IOD_EP2_TCP | 271 | 00271 | DI_UpsB_BypassON
EP2DI_UpsB_ERR | DIGITAL | IOD_EP2_TCP | 272 | 00272 | DI_UpsB_ERR
EP2DIN_Klima5_ERR | DIGITAL | IOD_EP2_TCP | 273 | 00273 | DIN_Klima5_ERR
EP2DIN_Klima6_ERR | DIGITAL | IOD_EP2_TCP | 274 | 00274 | DIN_Klima6_ERR
EP2DIN_KlimaSplit1_ERR | DIGITAL | IOD_EP2_TCP | 275 | 00275 | DIN_KlimaSplit1_ERR
EP2DIN_Q10_OdcKlima6_IZP | DIGITAL | IOD_EP2_TCP | 276 | 00276 | DIN_Q10_OdcKlima6_IZP
EP2DIN_Q25_OdcUpsA_IZP | DIGITAL | IOD_EP2_TCP | 277 | 00277 | DIN_Q25_OdcUpsA_IZP
EP2DIN_Q26_OdcByA_IZP | DIGITAL | IOD_EP2_TCP | 278 | 00278 | DIN_Q26_OdcByA_IZP
EP2DIN_Q27_OdcByUpsA_IZP | DIGITAL | IOD_EP2_TCP | 279 | 00279 | DIN_Q27_OdcByUpsA_IZP
EP2DIN_Q28_OdcUpsB_IZP | DIGITAL | IOD_EP2_TCP | 280 | 00280 | DIN_Q28_OdcUpsB_IZP
EP2DIN_Q29_OdcByB_IZP | DIGITAL | IOD_EP2_TCP | 281 | 00281 | DIN_Q29_OdcByB_IZP
EP2DIN_Q2_Rezerva_IZP | DIGITAL | IOD_EP2_TCP | 282 | 00282 | DIN_Q2_Rezerva_IZP
EP2DIN_Q30_OdcByUpsB_IZP | DIGITAL | IOD_EP2_TCP | 283 | 00283 | DIN_Q30_OdcByUpsB_IZP
EP2DIN_Q5_OdcKlima1_IZP | DIGITAL | IOD_EP2_TCP | 284 | 00284 | DIN_Q5_OdcKlima1_IZP
EP2DIN_Q6_OdcKlima2_IZP | DIGITAL | IOD_EP2_TCP | 285 | 00285 | DIN_Q6_OdcKlima2_IZP
EP2DIN_Q7_OdcKlima3_IZP | DIGITAL | IOD_EP2_TCP | 286 | 00286 | DIN_Q7_OdcKlima3_IZP
EP2DIN_Q8_OdcKlima4_IZP | DIGITAL | IOD_EP2_TCP | 287 | 00287 | DIN_Q8_OdcKlima4_IZP
EP2DIN_Q9_OdcKlima5_IZP | DIGITAL | IOD_EP2_TCP | 288 | 00288 | DIN_Q9_OdcKlima5_IZP
EP2ErrorComCirc1Error | DIGITAL | IOD_EP2_TCP | 289 | 00289 | ErrorComCirc[1].Error
EP2ErrorComCirc2Error | DIGITAL | IOD_EP2_TCP | 290 | 00290 | ErrorComCirc[2].Error
EP2ErrorComCirc3Error | DIGITAL | IOD_EP2_TCP | 291 | 00291 | ErrorComCirc[3].Error
EP2ErrorComCirc4Error | DIGITAL | IOD_EP2_TCP | 292 | 00292 | ErrorComCirc[4].Error
EP2ErrorComCirc5Error | DIGITAL | IOD_EP2_TCP | 293 | 00293 | ErrorComCirc[5].Error
EP2ErrorComKlima1Error | DIGITAL | IOD_EP2_TCP | 294 | 00294 | ErrorComKlima[1].Error
EP2ErrorComKlima2Error | DIGITAL | IOD_EP2_TCP | 295 | 00295 | ErrorComKlima[2].Error
EP2ErrorComKlima3Error | DIGITAL | IOD_EP2_TCP | 296 | 00296 | ErrorComKlima[3].Error
EP2ErrorComKlima4Error | DIGITAL | IOD_EP2_TCP | 297 | 00297 | ErrorComKlima[4].Error
EP2ErrorComKlima5Error | DIGITAL | IOD_EP2_TCP | 298 | 00298 | ErrorComKlima[5].Error
EP2ErrorComKlima6Error | DIGITAL | IOD_EP2_TCP | 299 | 00299 | ErrorComKlima[6].Error
EP2ErrorComPMM1Error | DIGITAL | IOD_EP2_TCP | 300 | 00300 | ErrorComPMM[1].Error
EP2ErrorComPMM2Error | DIGITAL | IOD_EP2_TCP | 301 | 00301 | ErrorComPMM[2].Error
EP2ErrorComPMM3Error | DIGITAL | IOD_EP2_TCP | 302 | 00302 | ErrorComPMM[3].Error
EP2ErrorComUPS1Error | DIGITAL | IOD_EP2_TCP | 303 | 00303 | ErrorComUPS[1].Error
EP2ErrorComUPS2Error | DIGITAL | IOD_EP2_TCP | 304 | 00304 | ErrorComUPS[2].Error
EP2KlimaAErrors10 | DIGITAL | IOD_EP2_TCP | 305 | 00305 | KlimaAErrors[10]
EP2KlimaAErrors11 | DIGITAL | IOD_EP2_TCP | 306 | 00306 | KlimaAErrors[11]
EP2KlimaAErrors12 | DIGITAL | IOD_EP2_TCP | 307 | 00307 | KlimaAErrors[12]
EP2KlimaAErrors13 | DIGITAL | IOD_EP2_TCP | 308 | 00308 | KlimaAErrors[13]
EP2KlimaAErrors14 | DIGITAL | IOD_EP2_TCP | 309 | 00309 | KlimaAErrors[14]
EP2KlimaAErrors15 | DIGITAL | IOD_EP2_TCP | 310 | 00310 | KlimaAErrors[15]
EP2KlimaAErrors16 | DIGITAL | IOD_EP2_TCP | 311 | 00311 | KlimaAErrors[16]
EP2KlimaAErrors17 | DIGITAL | IOD_EP2_TCP | 312 | 00312 | KlimaAErrors[17]
EP2KlimaAErrors18 | DIGITAL | IOD_EP2_TCP | 313 | 00313 | KlimaAErrors[18]
EP2KlimaAErrors19 | DIGITAL | IOD_EP2_TCP | 314 | 00314 | KlimaAErrors[19]
EP2KlimaAErrors1 | DIGITAL | IOD_EP2_TCP | 315 | 00315 | KlimaAErrors[1]
EP2KlimaAErrors20 | DIGITAL | IOD_EP2_TCP | 316 | 00316 | KlimaAErrors[20]
EP2KlimaAErrors21 | DIGITAL | IOD_EP2_TCP | 317 | 00317 | KlimaAErrors[21]
EP2KlimaAErrors22 | DIGITAL | IOD_EP2_TCP | 318 | 00318 | KlimaAErrors[22]
EP2KlimaAErrors23 | DIGITAL | IOD_EP2_TCP | 319 | 00319 | KlimaAErrors[23]
EP2KlimaAErrors24 | DIGITAL | IOD_EP2_TCP | 320 | 00320 | KlimaAErrors[24]
EP2KlimaAErrors25 | DIGITAL | IOD_EP2_TCP | 321 | 00321 | KlimaAErrors[25]
EP2KlimaAErrors26 | DIGITAL | IOD_EP2_TCP | 322 | 00322 | KlimaAErrors[26]
EP2KlimaAErrors27 | DIGITAL | IOD_EP2_TCP | 323 | 00323 | KlimaAErrors[27]
EP2KlimaAErrors28 | DIGITAL | IOD_EP2_TCP | 324 | 00324 | KlimaAErrors[28]
EP2KlimaAErrors29 | DIGITAL | IOD_EP2_TCP | 325 | 00325 | KlimaAErrors[29]
EP2KlimaAErrors2 | DIGITAL | IOD_EP2_TCP | 326 | 00326 | KlimaAErrors[2]
EP2KlimaAErrors30 | DIGITAL | IOD_EP2_TCP | 327 | 00327 | KlimaAErrors[30]
EP2KlimaAErrors31 | DIGITAL | IOD_EP2_TCP | 328 | 00328 | KlimaAErrors[31]
EP2KlimaAErrors32 | DIGITAL | IOD_EP2_TCP | 329 | 00329 | KlimaAErrors[32]
EP2KlimaAErrors33 | DIGITAL | IOD_EP2_TCP | 330 | 00330 | KlimaAErrors[33]
EP2KlimaAErrors34 | DIGITAL | IOD_EP2_TCP | 331 | 00331 | KlimaAErrors[34]
EP2KlimaAErrors35 | DIGITAL | IOD_EP2_TCP | 332 | 00332 | KlimaAErrors[35]
EP2KlimaAErrors36 | DIGITAL | IOD_EP2_TCP | 333 | 00333 | KlimaAErrors[36]
EP2KlimaAErrors37 | DIGITAL | IOD_EP2_TCP | 334 | 00334 | KlimaAErrors[37]
EP2KlimaAErrors38 | DIGITAL | IOD_EP2_TCP | 335 | 00335 | KlimaAErrors[38]
EP2KlimaAErrors39 | DIGITAL | IOD_EP2_TCP | 336 | 00336 | KlimaAErrors[39]
EP2KlimaAErrors3 | DIGITAL | IOD_EP2_TCP | 337 | 00337 | KlimaAErrors[3]
EP2KlimaAErrors40 | DIGITAL | IOD_EP2_TCP | 338 | 00338 | KlimaAErrors[40]
EP2KlimaAErrors4 | DIGITAL | IOD_EP2_TCP | 339 | 00339 | KlimaAErrors[4]
EP2KlimaAErrors5 | DIGITAL | IOD_EP2_TCP | 340 | 00340 | KlimaAErrors[5]
EP2KlimaAErrors6 | DIGITAL | IOD_EP2_TCP | 341 | 00341 | KlimaAErrors[6]
EP2KlimaAErrors7 | DIGITAL | IOD_EP2_TCP | 342 | 00342 | KlimaAErrors[7]
EP2KlimaAErrors8 | DIGITAL | IOD_EP2_TCP | 343 | 00343 | KlimaAErrors[8]
EP2KlimaAErrors9 | DIGITAL | IOD_EP2_TCP | 344 | 00344 | KlimaAErrors[9]
EP2KlimaBErrors10 | DIGITAL | IOD_EP2_TCP | 345 | 00345 | KlimaBErrors[10]
EP2KlimaBErrors11 | DIGITAL | IOD_EP2_TCP | 346 | 00346 | KlimaBErrors[11]
EP2KlimaBErrors12 | DIGITAL | IOD_EP2_TCP | 347 | 00347 | KlimaBErrors[12]
EP2KlimaBErrors13 | DIGITAL | IOD_EP2_TCP | 348 | 00348 | KlimaBErrors[13]
EP2KlimaBErrors14 | DIGITAL | IOD_EP2_TCP | 349 | 00349 | KlimaBErrors[14]
EP2KlimaBErrors15 | DIGITAL | IOD_EP2_TCP | 350 | 00350 | KlimaBErrors[15]
EP2KlimaBErrors16 | DIGITAL | IOD_EP2_TCP | 351 | 00351 | KlimaBErrors[16]
EP2KlimaBErrors17 | DIGITAL | IOD_EP2_TCP | 352 | 00352 | KlimaBErrors[17]
EP2KlimaBErrors18 | DIGITAL | IOD_EP2_TCP | 353 | 00353 | KlimaBErrors[18]
EP2KlimaBErrors19 | DIGITAL | IOD_EP2_TCP | 354 | 00354 | KlimaBErrors[19]
EP2KlimaBErrors1 | DIGITAL | IOD_EP2_TCP | 355 | 00355 | KlimaBErrors[1]
EP2KlimaBErrors20 | DIGITAL | IOD_EP2_TCP | 356 | 00356 | KlimaBErrors[20]
EP2KlimaBErrors21 | DIGITAL | IOD_EP2_TCP | 357 | 00357 | KlimaBErrors[21]
EP2KlimaBErrors22 | DIGITAL | IOD_EP2_TCP | 358 | 00358 | KlimaBErrors[22]
EP2KlimaBErrors23 | DIGITAL | IOD_EP2_TCP | 359 | 00359 | KlimaBErrors[23]
EP2KlimaBErrors24 | DIGITAL | IOD_EP2_TCP | 360 | 00360 | KlimaBErrors[24]
EP2KlimaBErrors25 | DIGITAL | IOD_EP2_TCP | 361 | 00361 | KlimaBErrors[25]
EP2KlimaBErrors26 | DIGITAL | IOD_EP2_TCP | 362 | 00362 | KlimaBErrors[26]
EP2KlimaBErrors27 | DIGITAL | IOD_EP2_TCP | 363 | 00363 | KlimaBErrors[27]
EP2KlimaBErrors28 | DIGITAL | IOD_EP2_TCP | 364 | 00364 | KlimaBErrors[28]
EP2KlimaBErrors29 | DIGITAL | IOD_EP2_TCP | 365 | 00365 | KlimaBErrors[29]
EP2KlimaBErrors2 | DIGITAL | IOD_EP2_TCP | 366 | 00366 | KlimaBErrors[2]
EP2KlimaBErrors30 | DIGITAL | IOD_EP2_TCP | 367 | 00367 | KlimaBErrors[30]
EP2KlimaBErrors31 | DIGITAL | IOD_EP2_TCP | 368 | 00368 | KlimaBErrors[31]
EP2KlimaBErrors32 | DIGITAL | IOD_EP2_TCP | 369 | 00369 | KlimaBErrors[32]
EP2KlimaBErrors33 | DIGITAL | IOD_EP2_TCP | 370 | 00370 | KlimaBErrors[33]
EP2KlimaBErrors34 | DIGITAL | IOD_EP2_TCP | 371 | 00371 | KlimaBErrors[34]
EP2KlimaBErrors35 | DIGITAL | IOD_EP2_TCP | 372 | 00372 | KlimaBErrors[35]
EP2KlimaBErrors36 | DIGITAL | IOD_EP2_TCP | 373 | 00373 | KlimaBErrors[36]
EP2KlimaBErrors37 | DIGITAL | IOD_EP2_TCP | 374 | 00374 | KlimaBErrors[37]
EP2KlimaBErrors38 | DIGITAL | IOD_EP2_TCP | 375 | 00375 | KlimaBErrors[38]
EP2KlimaBErrors39 | DIGITAL | IOD_EP2_TCP | 376 | 00376 | KlimaBErrors[39]
EP2KlimaBErrors3 | DIGITAL | IOD_EP2_TCP | 377 | 00377 | KlimaBErrors[3]
EP2KlimaBErrors40 | DIGITAL | IOD_EP2_TCP | 378 | 00378 | KlimaBErrors[40]
EP2KlimaBErrors4 | DIGITAL | IOD_EP2_TCP | 379 | 00379 | KlimaBErrors[4]
EP2KlimaBErrors5 | DIGITAL | IOD_EP2_TCP | 380 | 00380 | KlimaBErrors[5]
EP2KlimaBErrors6 | DIGITAL | IOD_EP2_TCP | 381 | 00381 | KlimaBErrors[6]
EP2KlimaBErrors7 | DIGITAL | IOD_EP2_TCP | 382 | 00382 | KlimaBErrors[7]
EP2KlimaBErrors8 | DIGITAL | IOD_EP2_TCP | 383 | 00383 | KlimaBErrors[8]
EP2KlimaBErrors9 | DIGITAL | IOD_EP2_TCP | 384 | 00384 | KlimaBErrors[9]
EP2KlimaGalAlarmKompresor1 | DIGITAL | IOD_EP2_TCP | 385 | 00385 | KlimaGal.AlarmKompresor1
EP2KlimaGalAlarmKompresor2 | DIGITAL | IOD_EP2_TCP | 386 | 00386 | KlimaGal.AlarmKompresor2
EP2KlimaGalDeluje | DIGITAL | IOD_EP2_TCP | 387 | 00387 | KlimaGal.Deluje
EP2KlimaGalEnergySaving | DIGITAL | IOD_EP2_TCP | 388 | 00388 | KlimaGal.EnergySaving
EP2KlimaGalFaultyEPROM | DIGITAL | IOD_EP2_TCP | 389 | 00389 | KlimaGal.FaultyEPROM
EP2KlimaGalFenThermalCutout | DIGITAL | IOD_EP2_TCP | 390 | 00390 | KlimaGal.FenThermalCutout
EP2KlimaGalGeneralAlarm | DIGITAL | IOD_EP2_TCP | 391 | 00391 | KlimaGal.GeneralAlarm
EP2KlimaGalKompresor1naMejiObrUr | DIGITAL | IOD_EP2_TCP | 392 | 00392 | KlimaGal.Kompresor1naMejiObrUr
EP2KlimaGalKompresor2naMejiObrUr | DIGITAL | IOD_EP2_TCP | 393 | 00393 | KlimaGal.Kompresor2naMejiObrUr
EP2KlimaGalNapaka | DIGITAL | IOD_EP2_TCP | 394 | 00394 | KlimaGal.Napaka
EP2KlimaGalNapakaPriPretokuZraka | DIGITAL | IOD_EP2_TCP | 395 | 00395 | KlimaGal.NapakaPriPretokuZraka
EP2KlimaGalNapakaSenzorPovratVode | DIGITAL | IOD_EP2_TCP | 396 | 00396 | KlimaGal.NapakaSenzorPovratVode
EP2KlimaGalNapakaSenzorTempIzpiha | DIGITAL | IOD_EP2_TCP | 397 | 00397 | KlimaGal.NapakaSenzorTempIzpiha
EP2KlimaGalNapakaSenzorTempProstora | DIGITAL | IOD_EP2_TCP | 398 | 00398 | KlimaGal.NapakaSenzorTempProstora
EP2KlimaGalNapakaSenzorVlaznosti | DIGITAL | IOD_EP2_TCP | 399 | 00399 | KlimaGal.NapakaSenzorVlaznosti
EP2KlimaGalNapakaSenzorZunanjeTemp | DIGITAL | IOD_EP2_TCP | 400 | 00400 | KlimaGal.NapakaSenzorZunanjeTemp
EP2KlimaGalNiTokaVVlazilcu | DIGITAL | IOD_EP2_TCP | 401 | 00401 | KlimaGal.NiTokaVVlazilcu
EP2KlimaGalNiVodeVVlazilcu | DIGITAL | IOD_EP2_TCP | 402 | 00402 | KlimaGal.NiVodeVVlazilcu
EP2KlimaGalNizekPritiskKompresor1 | DIGITAL | IOD_EP2_TCP | 403 | 00403 | KlimaGal.NizekPritiskKompresor1
EP2KlimaGalNizekPritiskKompresor2 | DIGITAL | IOD_EP2_TCP | 404 | 00404 | KlimaGal.NizekPritiskKompresor2
EP2KlimaGalNizkaTempPovratneVode | DIGITAL | IOD_EP2_TCP | 405 | 00405 | KlimaGal.NizkaTempPovratneVode
EP2KlimaGalNizkaTempVProstoru | DIGITAL | IOD_EP2_TCP | 406 | 00406 | KlimaGal.NizkaTempVProstoru
EP2KlimaGalNizkaVlaznost | DIGITAL | IOD_EP2_TCP | 407 | 00407 | KlimaGal.NizkaVlaznost
EP2KlimaGalOnOffEnablingBySupervisor | DIGITAL | IOD_EP2_TCP | 408 | 00408 | KlimaGal.OnOffEnablingBySupervisor
EP2KlimaGalPozarniAlarm | DIGITAL | IOD_EP2_TCP | 409 | 00409 | KlimaGal.PozarniAlarm
EP2KlimaGalRazvlazevanje | DIGITAL | IOD_EP2_TCP | 410 | 00410 | KlimaGal.Razvlazevanje
EP2KlimaGalRemoteOFFtoOutput | DIGITAL | IOD_EP2_TCP | 411 | 00411 | KlimaGal.RemoteOFFtoOutput
EP2KlimaGalRemoteOnOff | DIGITAL | IOD_EP2_TCP | 412 | 00412 | KlimaGal.RemoteOnOff
EP2KlimaGalRocniIzklop | DIGITAL | IOD_EP2_TCP | 413 | 00413 | KlimaGal.RocniIzklop
EP2KlimaGalSenzorjiStatus | DIGITAL | IOD_EP2_TCP | 414 | 00414 | KlimaGal.SenzorjiStatus
EP2KlimaGalStoppedByAlarms | DIGITAL | IOD_EP2_TCP | 415 | 00415 | KlimaGal.StoppedByAlarms
EP2KlimaGalThermalCutoutHeater1 | DIGITAL | IOD_EP2_TCP | 416 | 00416 | KlimaGal.ThermalCutoutHeater1
EP2KlimaGalThermalCutoutHeater2 | DIGITAL | IOD_EP2_TCP | 417 | 00417 | KlimaGal.ThermalCutoutHeater2
EP2KlimaGalUnitOnOff | DIGITAL | IOD_EP2_TCP | 418 | 00418 | KlimaGal.UnitOnOff
EP2KlimaGalVentilatorNaMejiObrUr | DIGITAL | IOD_EP2_TCP | 419 | 00419 | KlimaGal.VentilatorNaMejiObrUr
EP2KlimaGalVentilGretjeOdpiranje | DIGITAL | IOD_EP2_TCP | 420 | 00420 | KlimaGal.VentilGretjeOdpiranje
EP2KlimaGalVentilGretjeZapiranje | DIGITAL | IOD_EP2_TCP | 421 | 00421 | KlimaGal.VentilGretjeZapiranje
EP2KlimaGalVentilHlajenjeOdpiranje | DIGITAL | IOD_EP2_TCP | 422 | 00422 | KlimaGal.VentilHlajenjeOdpiranje
EP2KlimaGalVentilHlajenjeZapiranje | DIGITAL | IOD_EP2_TCP | 423 | 00423 | KlimaGal.VentilHlajenjeZapiranje
EP2KlimaGalVisokaTempPovratneVode | DIGITAL | IOD_EP2_TCP | 424 | 00424 | KlimaGal.VisokaTempPovratneVode
EP2KlimaGalVisokaTempVProstoru | DIGITAL | IOD_EP2_TCP | 425 | 00425 | KlimaGal.VisokaTempVProstoru
EP2KlimaGalVisokaVlaznost | DIGITAL | IOD_EP2_TCP | 426 | 00426 | KlimaGal.VisokaVlaznost
EP2KlimaGalVisokTokVVlazilcu | DIGITAL | IOD_EP2_TCP | 427 | 00427 | KlimaGal.VisokTokVVlazilcu
EP2KlimaGalVlazenje | DIGITAL | IOD_EP2_TCP | 428 | 00428 | KlimaGal.Vlazenje
EP2KlimaGalZamasenFilter | DIGITAL | IOD_EP2_TCP | 429 | 00429 | KlimaGal.ZamasenFilter
EP2PMM1OverVoltage | DIGITAL | IOD_EP2_TCP | 430 | 00430 | PMM1OverVoltage
EP2PMM2OverVoltage | DIGITAL | IOD_EP2_TCP | 431 | 00431 | PMM2OverVoltage
EP2PMM3OverVoltage | DIGITAL | IOD_EP2_TCP | 432 | 00432 | PMM3OverVoltage
EP2PMMgalNapaka | DIGITAL | IOD_EP2_TCP | 433 | 00433 | PMMgal.Napaka
EP2ErrCommScada2 | DIGITAL | IOD_EP2_TCP | 434 | 00434 | ErrCommScada2
EP2ComSCADA2 | DIGITAL | IOD_EP2_TCP | 435 | 00435 | ComSCADA2
EP2ComSCADA3 | DIGITAL | IOD_EP2_TCP | 436 | 00436 | ComSCADA3
EP2Circ_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_EP2_TCP | 437 | 00437 | Circ_Vpis_Dnevne_energija_scada1
EP2Circ_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_EP2_TCP | 438 | 00438 | Circ_Vpis_Dnevne_energija_scada2
EP2Circ_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_EP2_TCP | 439 | 00439 | Circ_Vpis_Tedenska_energija_scada1
EP2Circ_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_EP2_TCP | 440 | 00440 | Circ_Vpis_Tedenska_energija_scada2
EP2Circ_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_EP2_TCP | 441 | 00441 | Circ_Vpis_Mesecna_energija_scada1
EP2Circ_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_EP2_TCP | 442 | 00442 | Circ_Vpis_Mesecna_energija_scada2
EP2_DateTime_Dan | INT | IOD_EP2_TCP | 1 | 40001 | DateTime.Dan | BYTE
EP2_DateTime_Leto | INT | IOD_EP2_TCP | 2 | 40002 | DateTime.Leto | BYTE
EP2_DateTime_Mesec | INT | IOD_EP2_TCP | 3 | 40003 | DateTime.Mesec | BYTE
EP2_DateTime_Minuta | INT | IOD_EP2_TCP | 4 | 40004 | DateTime.Minuta | BYTE
EP2_DateTime_Sekunda | INT | IOD_EP2_TCP | 5 | 40005 | DateTime.Sekunda | BYTE
EP2_DateTime_Ura | INT | IOD_EP2_TCP | 6 | 40006 | DateTime.Ura | BYTE
EP2_Klima1_GrelecStatus | INT | IOD_EP2_TCP | 7 | 40007 | Klima[1].GrelecStatus | BYTE
EP2_Klima1_IzhodniVentStatus | INT | IOD_EP2_TCP | 8 | 40008 | Klima[1].IzhodniVentStatus | BYTE
EP2_Klima1_KompresorStatus | INT | IOD_EP2_TCP | 9 | 40009 | Klima[1].KompresorStatus | BYTE
EP2_Klima1_VlazilecStatus | INT | IOD_EP2_TCP | 10 | 40010 | Klima[1].VlazilecStatus | BYTE
EP2_Klima2_GrelecStatus | INT | IOD_EP2_TCP | 11 | 40011 | Klima[2].GrelecStatus | BYTE
EP2_Klima2_IzhodniVentStatus | INT | IOD_EP2_TCP | 12 | 40012 | Klima[2].IzhodniVentStatus | BYTE
EP2_Klima2_KompresorStatus | INT | IOD_EP2_TCP | 13 | 40013 | Klima[2].KompresorStatus | BYTE
EP2_Klima2_VlazilecStatus | INT | IOD_EP2_TCP | 14 | 40014 | Klima[2].VlazilecStatus | BYTE
EP2_PMM1_AlarmPhase1_C01_16_60to | INT | IOD_EP2_TCP | 15 | 40015 | PMM[1].AlarmPhase[1].C01_16_60to80
EP2_PMM1_AlarmPhase1_C01_16_over | INT | IOD_EP2_TCP | 16 | 40016 | PMM[1].AlarmPhase[1].C01_16_over80
EP2_PMM1_AlarmPhase1_C17_32_60to | INT | IOD_EP2_TCP | 17 | 40017 | PMM[1].AlarmPhase[1].C17_32_60to80
EP2_PMM1_AlarmPhase1_C17_32_over | INT | IOD_EP2_TCP | 18 | 40018 | PMM[1].AlarmPhase[1].C17_32_over80
EP2_PMM1_AlarmPhase1_C33_42_60to | INT | IOD_EP2_TCP | 19 | 40019 | PMM[1].AlarmPhase[1].C33_42_60to80
EP2_PMM1_AlarmPhase1_C33_42_over | INT | IOD_EP2_TCP | 20 | 40020 | PMM[1].AlarmPhase[1].C33_42_over80
EP2_PMM1_AlarmPhase1_GlobalAlarm | INT | IOD_EP2_TCP | 21 | 40021 | PMM[1].AlarmPhase[1].GlobalAlarmReg
EP2_PMM1_AlarmPhase2_C01_16_60to | INT | IOD_EP2_TCP | 22 | 40022 | PMM[1].AlarmPhase[2].C01_16_60to80
EP2_PMM1_AlarmPhase2_C01_16_over | INT | IOD_EP2_TCP | 23 | 40023 | PMM[1].AlarmPhase[2].C01_16_over80
EP2_PMM1_AlarmPhase2_C17_32_60to | INT | IOD_EP2_TCP | 24 | 40024 | PMM[1].AlarmPhase[2].C17_32_60to80
EP2_PMM1_AlarmPhase2_C17_32_over | INT | IOD_EP2_TCP | 25 | 40025 | PMM[1].AlarmPhase[2].C17_32_over80
EP2_PMM1_AlarmPhase2_C33_42_60to | INT | IOD_EP2_TCP | 26 | 40026 | PMM[1].AlarmPhase[2].C33_42_60to80
EP2_PMM1_AlarmPhase2_C33_42_over | INT | IOD_EP2_TCP | 27 | 40027 | PMM[1].AlarmPhase[2].C33_42_over80
EP2_PMM1_AlarmPhase2_GlobalAlarm | INT | IOD_EP2_TCP | 28 | 40028 | PMM[1].AlarmPhase[2].GlobalAlarmReg
EP2_PMM1_AlarmPhase3_C01_16_60to | INT | IOD_EP2_TCP | 29 | 40029 | PMM[1].AlarmPhase[3].C01_16_60to80
EP2_PMM1_AlarmPhase3_C01_16_over | INT | IOD_EP2_TCP | 30 | 40030 | PMM[1].AlarmPhase[3].C01_16_over80
EP2_PMM1_AlarmPhase3_C17_32_60to | INT | IOD_EP2_TCP | 31 | 40031 | PMM[1].AlarmPhase[3].C17_32_60to80
EP2_PMM1_AlarmPhase3_C17_32_over | INT | IOD_EP2_TCP | 32 | 40032 | PMM[1].AlarmPhase[3].C17_32_over80
EP2_PMM1_AlarmPhase3_C33_42_60to | INT | IOD_EP2_TCP | 33 | 40033 | PMM[1].AlarmPhase[3].C33_42_60to80
EP2_PMM1_AlarmPhase3_C33_42_over | INT | IOD_EP2_TCP | 34 | 40034 | PMM[1].AlarmPhase[3].C33_42_over80
EP2_PMM1_AlarmPhase3_GlobalAlarm | INT | IOD_EP2_TCP | 35 | 40035 | PMM[1].AlarmPhase[3].GlobalAlarmReg
EP2_PMM1_Alarms | INT | IOD_EP2_TCP | 36 | 40036 | PMM[1].Alarms
EP2_PMM2_AlarmPhase1_C01_16_60to | INT | IOD_EP2_TCP | 37 | 40037 | PMM[2].AlarmPhase[1].C01_16_60to80
EP2_PMM2_AlarmPhase1_C01_16_over | INT | IOD_EP2_TCP | 38 | 40038 | PMM[2].AlarmPhase[1].C01_16_over80
EP2_PMM2_AlarmPhase1_C17_32_60to | INT | IOD_EP2_TCP | 39 | 40039 | PMM[2].AlarmPhase[1].C17_32_60to80
EP2_PMM2_AlarmPhase1_C17_32_over | INT | IOD_EP2_TCP | 40 | 40040 | PMM[2].AlarmPhase[1].C17_32_over80
EP2_PMM2_AlarmPhase1_C33_42_60to | INT | IOD_EP2_TCP | 41 | 40041 | PMM[2].AlarmPhase[1].C33_42_60to80
EP2_PMM2_AlarmPhase1_C33_42_over | INT | IOD_EP2_TCP | 42 | 40042 | PMM[2].AlarmPhase[1].C33_42_over80
EP2_PMM2_AlarmPhase1_GlobalAlarm | INT | IOD_EP2_TCP | 43 | 40043 | PMM[2].AlarmPhase[1].GlobalAlarmReg
EP2_PMM2_AlarmPhase2_C01_16_60to | INT | IOD_EP2_TCP | 44 | 40044 | PMM[2].AlarmPhase[2].C01_16_60to80
EP2_PMM2_AlarmPhase2_C01_16_over | INT | IOD_EP2_TCP | 45 | 40045 | PMM[2].AlarmPhase[2].C01_16_over80
EP2_PMM2_AlarmPhase2_C17_32_60to | INT | IOD_EP2_TCP | 46 | 40046 | PMM[2].AlarmPhase[2].C17_32_60to80
EP2_PMM2_AlarmPhase2_C17_32_over | INT | IOD_EP2_TCP | 47 | 40047 | PMM[2].AlarmPhase[2].C17_32_over80
EP2_PMM2_AlarmPhase2_C33_42_60to | INT | IOD_EP2_TCP | 48 | 40048 | PMM[2].AlarmPhase[2].C33_42_60to80
EP2_PMM2_AlarmPhase2_C33_42_over | INT | IOD_EP2_TCP | 49 | 40049 | PMM[2].AlarmPhase[2].C33_42_over80
EP2_PMM2_AlarmPhase2_GlobalAlarm | INT | IOD_EP2_TCP | 50 | 40050 | PMM[2].AlarmPhase[2].GlobalAlarmReg
EP2_PMM2_AlarmPhase3_C01_16_60to | INT | IOD_EP2_TCP | 51 | 40051 | PMM[2].AlarmPhase[3].C01_16_60to80
EP2_PMM2_AlarmPhase3_C01_16_over | INT | IOD_EP2_TCP | 52 | 40052 | PMM[2].AlarmPhase[3].C01_16_over80
EP2_PMM2_AlarmPhase3_C17_32_60to | INT | IOD_EP2_TCP | 53 | 40053 | PMM[2].AlarmPhase[3].C17_32_60to80
EP2_PMM2_AlarmPhase3_C17_32_over | INT | IOD_EP2_TCP | 54 | 40054 | PMM[2].AlarmPhase[3].C17_32_over80
EP2_PMM2_AlarmPhase3_C33_42_60to | INT | IOD_EP2_TCP | 55 | 40055 | PMM[2].AlarmPhase[3].C33_42_60to80
EP2_PMM2_AlarmPhase3_C33_42_over | INT | IOD_EP2_TCP | 56 | 40056 | PMM[2].AlarmPhase[3].C33_42_over80
EP2_PMM2_AlarmPhase3_GlobalAlarm | INT | IOD_EP2_TCP | 57 | 40057 | PMM[2].AlarmPhase[3].GlobalAlarmReg
EP2_PMM2_Alarms | INT | IOD_EP2_TCP | 58 | 40058 | PMM[2].Alarms
EP2_PMM3_AlarmPhase1_C01_16_60to | INT | IOD_EP2_TCP | 59 | 40059 | PMM[3].AlarmPhase[1].C01_16_60to80
EP2_PMM3_AlarmPhase1_C01_16_over | INT | IOD_EP2_TCP | 60 | 40060 | PMM[3].AlarmPhase[1].C01_16_over80
EP2_PMM3_AlarmPhase1_C17_32_60to | INT | IOD_EP2_TCP | 61 | 40061 | PMM[3].AlarmPhase[1].C17_32_60to80
EP2_PMM3_AlarmPhase1_C17_32_over | INT | IOD_EP2_TCP | 62 | 40062 | PMM[3].AlarmPhase[1].C17_32_over80
EP2_PMM3_AlarmPhase1_C33_42_60to | INT | IOD_EP2_TCP | 63 | 40063 | PMM[3].AlarmPhase[1].C33_42_60to80
EP2_PMM3_AlarmPhase1_C33_42_over | INT | IOD_EP2_TCP | 64 | 40064 | PMM[3].AlarmPhase[1].C33_42_over80
EP2_PMM3_AlarmPhase1_GlobalAlarm | INT | IOD_EP2_TCP | 65 | 40065 | PMM[3].AlarmPhase[1].GlobalAlarmReg
EP2_PMM3_AlarmPhase2_C01_16_60to | INT | IOD_EP2_TCP | 66 | 40066 | PMM[3].AlarmPhase[2].C01_16_60to80
EP2_PMM3_AlarmPhase2_C01_16_over | INT | IOD_EP2_TCP | 67 | 40067 | PMM[3].AlarmPhase[2].C01_16_over80
EP2_PMM3_AlarmPhase2_C17_32_60to | INT | IOD_EP2_TCP | 68 | 40068 | PMM[3].AlarmPhase[2].C17_32_60to80
EP2_PMM3_AlarmPhase2_C17_32_over | INT | IOD_EP2_TCP | 69 | 40069 | PMM[3].AlarmPhase[2].C17_32_over80
EP2_PMM3_AlarmPhase2_C33_42_60to | INT | IOD_EP2_TCP | 70 | 40070 | PMM[3].AlarmPhase[2].C33_42_60to80
EP2_PMM3_AlarmPhase2_C33_42_over | INT | IOD_EP2_TCP | 71 | 40071 | PMM[3].AlarmPhase[2].C33_42_over80
EP2_PMM3_AlarmPhase2_GlobalAlarm | INT | IOD_EP2_TCP | 72 | 40072 | PMM[3].AlarmPhase[2].GlobalAlarmReg
EP2_PMM3_AlarmPhase3_C01_16_60to | INT | IOD_EP2_TCP | 73 | 40073 | PMM[3].AlarmPhase[3].C01_16_60to80
EP2_PMM3_AlarmPhase3_C01_16_over | INT | IOD_EP2_TCP | 74 | 40074 | PMM[3].AlarmPhase[3].C01_16_over80
EP2_PMM3_AlarmPhase3_C17_32_60to | INT | IOD_EP2_TCP | 75 | 40075 | PMM[3].AlarmPhase[3].C17_32_60to80
EP2_PMM3_AlarmPhase3_C17_32_over | INT | IOD_EP2_TCP | 76 | 40076 | PMM[3].AlarmPhase[3].C17_32_over80
EP2_PMM3_AlarmPhase3_C33_42_60to | INT | IOD_EP2_TCP | 77 | 40077 | PMM[3].AlarmPhase[3].C33_42_60to80
EP2_PMM3_AlarmPhase3_C33_42_over | INT | IOD_EP2_TCP | 78 | 40078 | PMM[3].AlarmPhase[3].C33_42_over80
EP2_PMM3_AlarmPhase3_GlobalAlarm | INT | IOD_EP2_TCP | 79 | 40079 | PMM[3].AlarmPhase[3].GlobalAlarmReg
EP2_PMM3_Alarms | INT | IOD_EP2_TCP | 80 | 40080 | PMM[3].Alarms
EP2UPS1InverterStatus | INT | IOD_EP2_TCP | 81 | 40081 | UPS[1].InverterStatus
EP2UPS1OutputStatus | INT | IOD_EP2_TCP | 82 | 40082 | UPS[1].OutputStatus
EP2UPS1StatusBaterije | INT | IOD_EP2_TCP | 83 | 40083 | UPS[1].StatusBaterije
EP2UPS1SteviloIzpadovVhodneLinije | INT | IOD_EP2_TCP | 84 | 40084 | UPS[1].SteviloIzpadovVhodneLinije
EP2UPS1UnitStatus | INT | IOD_EP2_TCP | 85 | 40085 | UPS[1].UnitStatus
EP2UPS2InverterStatus | INT | IOD_EP2_TCP | 86 | 40086 | UPS[2].InverterStatus
EP2UPS2OutputStatus | INT | IOD_EP2_TCP | 87 | 40087 | UPS[2].OutputStatus
EP2UPS2StatusBaterije | INT | IOD_EP2_TCP | 88 | 40088 | UPS[2].StatusBaterije
EP2UPS2SteviloIzpadovVhodneLinije | INT | IOD_EP2_TCP | 89 | 40089 | UPS[2].SteviloIzpadovVhodneLinije
EP2UPS2UnitStatus | INT | IOD_EP2_TCP | 90 | 40090 | UPS[2].UnitStatus
EP2_UserCurrentLevel | INT | IOD_EP2_TCP | 91 | 40091 | UserCurrentLevel | BYTE
EP2ErrorComCirc1Code10 | INT | IOD_EP2_TCP | 92 | 40092 | ErrorComCirc[1].Code[10] | BYTE
EP2ErrorComCirc1Code11 | INT | IOD_EP2_TCP | 93 | 40093 | ErrorComCirc[1].Code[11] | BYTE
EP2ErrorComCirc1Code12 | INT | IOD_EP2_TCP | 94 | 40094 | ErrorComCirc[1].Code[12] | BYTE
EP2ErrorComCirc1Code13 | INT | IOD_EP2_TCP | 95 | 40095 | ErrorComCirc[1].Code[13] | BYTE
EP2ErrorComCirc1Code14 | INT | IOD_EP2_TCP | 96 | 40096 | ErrorComCirc[1].Code[14] | BYTE
EP2ErrorComCirc1Code15 | INT | IOD_EP2_TCP | 97 | 40097 | ErrorComCirc[1].Code[15] | BYTE
EP2ErrorComCirc1Code1 | INT | IOD_EP2_TCP | 98 | 40098 | ErrorComCirc[1].Code[1] | BYTE
EP2ErrorComCirc1Code2 | INT | IOD_EP2_TCP | 99 | 40099 | ErrorComCirc[1].Code[2] | BYTE
EP2ErrorComCirc1Code3 | INT | IOD_EP2_TCP | 100 | 40100 | ErrorComCirc[1].Code[3] | BYTE
EP2ErrorComCirc1Code4 | INT | IOD_EP2_TCP | 101 | 40101 | ErrorComCirc[1].Code[4] | BYTE
EP2ErrorComCirc1Code5 | INT | IOD_EP2_TCP | 102 | 40102 | ErrorComCirc[1].Code[5] | BYTE
EP2ErrorComCirc1Code6 | INT | IOD_EP2_TCP | 103 | 40103 | ErrorComCirc[1].Code[6] | BYTE
EP2ErrorComCirc1Code7 | INT | IOD_EP2_TCP | 104 | 40104 | ErrorComCirc[1].Code[7] | BYTE
EP2ErrorComCirc1Code8 | INT | IOD_EP2_TCP | 105 | 40105 | ErrorComCirc[1].Code[8] | BYTE
EP2ErrorComCirc1Code9 | INT | IOD_EP2_TCP | 106 | 40106 | ErrorComCirc[1].Code[9] | BYTE
EP2ErrorComCirc1Status | INT | IOD_EP2_TCP | 107 | 40107 | ErrorComCirc[1].Status
EP2ErrorComCirc2Code10 | INT | IOD_EP2_TCP | 108 | 40108 | ErrorComCirc[2].Code[10] | BYTE
EP2ErrorComCirc2Code11 | INT | IOD_EP2_TCP | 109 | 40109 | ErrorComCirc[2].Code[11] | BYTE
EP2ErrorComCirc2Code12 | INT | IOD_EP2_TCP | 110 | 40110 | ErrorComCirc[2].Code[12] | BYTE
EP2ErrorComCirc2Code13 | INT | IOD_EP2_TCP | 111 | 40111 | ErrorComCirc[2].Code[13] | BYTE
EP2ErrorComCirc2Code14 | INT | IOD_EP2_TCP | 112 | 40112 | ErrorComCirc[2].Code[14] | BYTE
EP2ErrorComCirc2Code15 | INT | IOD_EP2_TCP | 113 | 40113 | ErrorComCirc[2].Code[15] | BYTE
EP2ErrorComCirc2Code1 | INT | IOD_EP2_TCP | 114 | 40114 | ErrorComCirc[2].Code[1] | BYTE
EP2ErrorComCirc2Code2 | INT | IOD_EP2_TCP | 115 | 40115 | ErrorComCirc[2].Code[2] | BYTE
EP2ErrorComCirc2Code3 | INT | IOD_EP2_TCP | 116 | 40116 | ErrorComCirc[2].Code[3] | BYTE
EP2ErrorComCirc2Code4 | INT | IOD_EP2_TCP | 117 | 40117 | ErrorComCirc[2].Code[4] | BYTE
EP2ErrorComCirc2Code5 | INT | IOD_EP2_TCP | 118 | 40118 | ErrorComCirc[2].Code[5] | BYTE
EP2ErrorComCirc2Code6 | INT | IOD_EP2_TCP | 119 | 40119 | ErrorComCirc[2].Code[6] | BYTE
EP2ErrorComCirc2Code7 | INT | IOD_EP2_TCP | 120 | 40120 | ErrorComCirc[2].Code[7] | BYTE
EP2ErrorComCirc2Code8 | INT | IOD_EP2_TCP | 121 | 40121 | ErrorComCirc[2].Code[8] | BYTE
EP2ErrorComCirc2Code9 | INT | IOD_EP2_TCP | 122 | 40122 | ErrorComCirc[2].Code[9] | BYTE
EP2ErrorComCirc2Status | INT | IOD_EP2_TCP | 123 | 40123 | ErrorComCirc[2].Status
EP2ErrorComCirc3Code10 | INT | IOD_EP2_TCP | 124 | 40124 | ErrorComCirc[3].Code[10] | BYTE
EP2ErrorComCirc3Code11 | INT | IOD_EP2_TCP | 125 | 40125 | ErrorComCirc[3].Code[11] | BYTE
EP2ErrorComCirc3Code12 | INT | IOD_EP2_TCP | 126 | 40126 | ErrorComCirc[3].Code[12] | BYTE
EP2ErrorComCirc3Code13 | INT | IOD_EP2_TCP | 127 | 40127 | ErrorComCirc[3].Code[13] | BYTE
EP2ErrorComCirc3Code14 | INT | IOD_EP2_TCP | 128 | 40128 | ErrorComCirc[3].Code[14] | BYTE
EP2ErrorComCirc3Code15 | INT | IOD_EP2_TCP | 129 | 40129 | ErrorComCirc[3].Code[15] | BYTE
EP2ErrorComCirc3Code1 | INT | IOD_EP2_TCP | 130 | 40130 | ErrorComCirc[3].Code[1] | BYTE
EP2ErrorComCirc3Code2 | INT | IOD_EP2_TCP | 131 | 40131 | ErrorComCirc[3].Code[2] | BYTE
EP2ErrorComCirc3Code3 | INT | IOD_EP2_TCP | 132 | 40132 | ErrorComCirc[3].Code[3] | BYTE
EP2ErrorComCirc3Code4 | INT | IOD_EP2_TCP | 133 | 40133 | ErrorComCirc[3].Code[4] | BYTE
EP2ErrorComCirc3Code5 | INT | IOD_EP2_TCP | 134 | 40134 | ErrorComCirc[3].Code[5] | BYTE
EP2ErrorComCirc3Code6 | INT | IOD_EP2_TCP | 135 | 40135 | ErrorComCirc[3].Code[6] | BYTE
EP2ErrorComCirc3Code7 | INT | IOD_EP2_TCP | 136 | 40136 | ErrorComCirc[3].Code[7] | BYTE
EP2ErrorComCirc3Code8 | INT | IOD_EP2_TCP | 137 | 40137 | ErrorComCirc[3].Code[8] | BYTE
EP2ErrorComCirc3Code9 | INT | IOD_EP2_TCP | 138 | 40138 | ErrorComCirc[3].Code[9] | BYTE
EP2ErrorComCirc3Status | INT | IOD_EP2_TCP | 139 | 40139 | ErrorComCirc[3].Status
EP2ErrorComCirc4Code10 | INT | IOD_EP2_TCP | 140 | 40140 | ErrorComCirc[4].Code[10] | BYTE
EP2ErrorComCirc4Code11 | INT | IOD_EP2_TCP | 141 | 40141 | ErrorComCirc[4].Code[11] | BYTE
EP2ErrorComCirc4Code12 | INT | IOD_EP2_TCP | 142 | 40142 | ErrorComCirc[4].Code[12] | BYTE
EP2ErrorComCirc4Code13 | INT | IOD_EP2_TCP | 143 | 40143 | ErrorComCirc[4].Code[13] | BYTE
EP2ErrorComCirc4Code14 | INT | IOD_EP2_TCP | 144 | 40144 | ErrorComCirc[4].Code[14] | BYTE
EP2ErrorComCirc4Code15 | INT | IOD_EP2_TCP | 145 | 40145 | ErrorComCirc[4].Code[15] | BYTE
EP2ErrorComCirc4Code1 | INT | IOD_EP2_TCP | 146 | 40146 | ErrorComCirc[4].Code[1] | BYTE
EP2ErrorComCirc4Code2 | INT | IOD_EP2_TCP | 147 | 40147 | ErrorComCirc[4].Code[2] | BYTE
EP2ErrorComCirc4Code3 | INT | IOD_EP2_TCP | 148 | 40148 | ErrorComCirc[4].Code[3] | BYTE
EP2ErrorComCirc4Code4 | INT | IOD_EP2_TCP | 149 | 40149 | ErrorComCirc[4].Code[4] | BYTE
EP2ErrorComCirc4Code5 | INT | IOD_EP2_TCP | 150 | 40150 | ErrorComCirc[4].Code[5] | BYTE
EP2ErrorComCirc4Code6 | INT | IOD_EP2_TCP | 151 | 40151 | ErrorComCirc[4].Code[6] | BYTE
EP2ErrorComCirc4Code7 | INT | IOD_EP2_TCP | 152 | 40152 | ErrorComCirc[4].Code[7] | BYTE
EP2ErrorComCirc4Code8 | INT | IOD_EP2_TCP | 153 | 40153 | ErrorComCirc[4].Code[8] | BYTE
EP2ErrorComCirc4Code9 | INT | IOD_EP2_TCP | 154 | 40154 | ErrorComCirc[4].Code[9] | BYTE
EP2ErrorComCirc4Status | INT | IOD_EP2_TCP | 155 | 40155 | ErrorComCirc[4].Status
EP2ErrorComCirc5Code10 | INT | IOD_EP2_TCP | 156 | 40156 | ErrorComCirc[5].Code[10] | BYTE
EP2ErrorComCirc5Code11 | INT | IOD_EP2_TCP | 157 | 40157 | ErrorComCirc[5].Code[11] | BYTE
EP2ErrorComCirc5Code12 | INT | IOD_EP2_TCP | 158 | 40158 | ErrorComCirc[5].Code[12] | BYTE
EP2ErrorComCirc5Code13 | INT | IOD_EP2_TCP | 159 | 40159 | ErrorComCirc[5].Code[13] | BYTE
EP2ErrorComCirc5Code14 | INT | IOD_EP2_TCP | 160 | 40160 | ErrorComCirc[5].Code[14] | BYTE
EP2ErrorComCirc5Code15 | INT | IOD_EP2_TCP | 161 | 40161 | ErrorComCirc[5].Code[15] | BYTE
EP2ErrorComCirc5Code1 | INT | IOD_EP2_TCP | 162 | 40162 | ErrorComCirc[5].Code[1] | BYTE
EP2ErrorComCirc5Code2 | INT | IOD_EP2_TCP | 163 | 40163 | ErrorComCirc[5].Code[2] | BYTE
EP2ErrorComCirc5Code3 | INT | IOD_EP2_TCP | 164 | 40164 | ErrorComCirc[5].Code[3] | BYTE
EP2ErrorComCirc5Code4 | INT | IOD_EP2_TCP | 165 | 40165 | ErrorComCirc[5].Code[4] | BYTE
EP2ErrorComCirc5Code5 | INT | IOD_EP2_TCP | 166 | 40166 | ErrorComCirc[5].Code[5] | BYTE
EP2ErrorComCirc5Code6 | INT | IOD_EP2_TCP | 167 | 40167 | ErrorComCirc[5].Code[6] | BYTE
EP2ErrorComCirc5Code7 | INT | IOD_EP2_TCP | 168 | 40168 | ErrorComCirc[5].Code[7] | BYTE
EP2ErrorComCirc5Code8 | INT | IOD_EP2_TCP | 169 | 40169 | ErrorComCirc[5].Code[8] | BYTE
EP2ErrorComCirc5Code9 | INT | IOD_EP2_TCP | 170 | 40170 | ErrorComCirc[5].Code[9] | BYTE
EP2ErrorComCirc5Status | INT | IOD_EP2_TCP | 171 | 40171 | ErrorComCirc[5].Status
EP2ErrorComKlima1Code10 | INT | IOD_EP2_TCP | 172 | 40172 | ErrorComKlima[1].Code[10] | BYTE
EP2ErrorComKlima1Code11 | INT | IOD_EP2_TCP | 173 | 40173 | ErrorComKlima[1].Code[11] | BYTE
EP2ErrorComKlima1Code12 | INT | IOD_EP2_TCP | 174 | 40174 | ErrorComKlima[1].Code[12] | BYTE
EP2ErrorComKlima1Code13 | INT | IOD_EP2_TCP | 175 | 40175 | ErrorComKlima[1].Code[13] | BYTE
EP2ErrorComKlima1Code14 | INT | IOD_EP2_TCP | 176 | 40176 | ErrorComKlima[1].Code[14] | BYTE
EP2ErrorComKlima1Code15 | INT | IOD_EP2_TCP | 177 | 40177 | ErrorComKlima[1].Code[15] | BYTE
EP2ErrorComKlima1Code1 | INT | IOD_EP2_TCP | 178 | 40178 | ErrorComKlima[1].Code[1] | BYTE
EP2ErrorComKlima1Code2 | INT | IOD_EP2_TCP | 179 | 40179 | ErrorComKlima[1].Code[2] | BYTE
EP2ErrorComKlima1Code3 | INT | IOD_EP2_TCP | 180 | 40180 | ErrorComKlima[1].Code[3] | BYTE
EP2ErrorComKlima1Code4 | INT | IOD_EP2_TCP | 181 | 40181 | ErrorComKlima[1].Code[4] | BYTE
EP2ErrorComKlima1Code5 | INT | IOD_EP2_TCP | 182 | 40182 | ErrorComKlima[1].Code[5] | BYTE
EP2ErrorComKlima1Code6 | INT | IOD_EP2_TCP | 183 | 40183 | ErrorComKlima[1].Code[6] | BYTE
EP2ErrorComKlima1Code7 | INT | IOD_EP2_TCP | 184 | 40184 | ErrorComKlima[1].Code[7] | BYTE
EP2ErrorComKlima1Code8 | INT | IOD_EP2_TCP | 185 | 40185 | ErrorComKlima[1].Code[8] | BYTE
EP2ErrorComKlima1Code9 | INT | IOD_EP2_TCP | 186 | 40186 | ErrorComKlima[1].Code[9] | BYTE
EP2ErrorComKlima1Status | INT | IOD_EP2_TCP | 187 | 40187 | ErrorComKlima[1].Status
EP2ErrorComKlima2Code10 | INT | IOD_EP2_TCP | 188 | 40188 | ErrorComKlima[2].Code[10] | BYTE
EP2ErrorComKlima2Code11 | INT | IOD_EP2_TCP | 189 | 40189 | ErrorComKlima[2].Code[11] | BYTE
EP2ErrorComKlima2Code12 | INT | IOD_EP2_TCP | 190 | 40190 | ErrorComKlima[2].Code[12] | BYTE
EP2ErrorComKlima2Code13 | INT | IOD_EP2_TCP | 191 | 40191 | ErrorComKlima[2].Code[13] | BYTE
EP2ErrorComKlima2Code14 | INT | IOD_EP2_TCP | 192 | 40192 | ErrorComKlima[2].Code[14] | BYTE
EP2ErrorComKlima2Code15 | INT | IOD_EP2_TCP | 193 | 40193 | ErrorComKlima[2].Code[15] | BYTE
EP2ErrorComKlima2Code1 | INT | IOD_EP2_TCP | 194 | 40194 | ErrorComKlima[2].Code[1] | BYTE
EP2ErrorComKlima2Code2 | INT | IOD_EP2_TCP | 195 | 40195 | ErrorComKlima[2].Code[2] | BYTE
EP2ErrorComKlima2Code3 | INT | IOD_EP2_TCP | 196 | 40196 | ErrorComKlima[2].Code[3] | BYTE
EP2ErrorComKlima2Code4 | INT | IOD_EP2_TCP | 197 | 40197 | ErrorComKlima[2].Code[4] | BYTE
EP2ErrorComKlima2Code5 | INT | IOD_EP2_TCP | 198 | 40198 | ErrorComKlima[2].Code[5] | BYTE
EP2ErrorComKlima2Code6 | INT | IOD_EP2_TCP | 199 | 40199 | ErrorComKlima[2].Code[6] | BYTE
EP2ErrorComKlima2Code7 | INT | IOD_EP2_TCP | 200 | 40200 | ErrorComKlima[2].Code[7] | BYTE
EP2ErrorComKlima2Code8 | INT | IOD_EP2_TCP | 201 | 40201 | ErrorComKlima[2].Code[8] | BYTE
EP2ErrorComKlima2Code9 | INT | IOD_EP2_TCP | 202 | 40202 | ErrorComKlima[2].Code[9] | BYTE
EP2ErrorComKlima2Status | INT | IOD_EP2_TCP | 203 | 40203 | ErrorComKlima[2].Status
EP2ErrorComKlima3Code10 | INT | IOD_EP2_TCP | 204 | 40204 | ErrorComKlima[3].Code[10] | BYTE
EP2ErrorComKlima3Code11 | INT | IOD_EP2_TCP | 205 | 40205 | ErrorComKlima[3].Code[11] | BYTE
EP2ErrorComKlima3Code12 | INT | IOD_EP2_TCP | 206 | 40206 | ErrorComKlima[3].Code[12] | BYTE
EP2ErrorComKlima3Code13 | INT | IOD_EP2_TCP | 207 | 40207 | ErrorComKlima[3].Code[13] | BYTE
EP2ErrorComKlima3Code14 | INT | IOD_EP2_TCP | 208 | 40208 | ErrorComKlima[3].Code[14] | BYTE
EP2ErrorComKlima3Code15 | INT | IOD_EP2_TCP | 209 | 40209 | ErrorComKlima[3].Code[15] | BYTE
EP2ErrorComKlima3Code1 | INT | IOD_EP2_TCP | 210 | 40210 | ErrorComKlima[3].Code[1] | BYTE
EP2ErrorComKlima3Code2 | INT | IOD_EP2_TCP | 211 | 40211 | ErrorComKlima[3].Code[2] | BYTE
EP2ErrorComKlima3Code3 | INT | IOD_EP2_TCP | 212 | 40212 | ErrorComKlima[3].Code[3] | BYTE
EP2ErrorComKlima3Code4 | INT | IOD_EP2_TCP | 213 | 40213 | ErrorComKlima[3].Code[4] | BYTE
EP2ErrorComKlima3Code5 | INT | IOD_EP2_TCP | 214 | 40214 | ErrorComKlima[3].Code[5] | BYTE
EP2ErrorComKlima3Code6 | INT | IOD_EP2_TCP | 215 | 40215 | ErrorComKlima[3].Code[6] | BYTE
EP2ErrorComKlima3Code7 | INT | IOD_EP2_TCP | 216 | 40216 | ErrorComKlima[3].Code[7] | BYTE
EP2ErrorComKlima3Code8 | INT | IOD_EP2_TCP | 217 | 40217 | ErrorComKlima[3].Code[8] | BYTE
EP2ErrorComKlima3Code9 | INT | IOD_EP2_TCP | 218 | 40218 | ErrorComKlima[3].Code[9] | BYTE
EP2ErrorComKlima3Status | INT | IOD_EP2_TCP | 219 | 40219 | ErrorComKlima[3].Status
EP2ErrorComKlima4Code10 | INT | IOD_EP2_TCP | 220 | 40220 | ErrorComKlima[4].Code[10] | BYTE
EP2ErrorComKlima4Code11 | INT | IOD_EP2_TCP | 221 | 40221 | ErrorComKlima[4].Code[11] | BYTE
EP2ErrorComKlima4Code12 | INT | IOD_EP2_TCP | 222 | 40222 | ErrorComKlima[4].Code[12] | BYTE
EP2ErrorComKlima4Code13 | INT | IOD_EP2_TCP | 223 | 40223 | ErrorComKlima[4].Code[13] | BYTE
EP2ErrorComKlima4Code14 | INT | IOD_EP2_TCP | 224 | 40224 | ErrorComKlima[4].Code[14] | BYTE
EP2ErrorComKlima4Code15 | INT | IOD_EP2_TCP | 225 | 40225 | ErrorComKlima[4].Code[15] | BYTE
EP2ErrorComKlima4Code1 | INT | IOD_EP2_TCP | 226 | 40226 | ErrorComKlima[4].Code[1] | BYTE
EP2ErrorComKlima4Code2 | INT | IOD_EP2_TCP | 227 | 40227 | ErrorComKlima[4].Code[2] | BYTE
EP2ErrorComKlima4Code3 | INT | IOD_EP2_TCP | 228 | 40228 | ErrorComKlima[4].Code[3] | BYTE
EP2ErrorComKlima4Code4 | INT | IOD_EP2_TCP | 229 | 40229 | ErrorComKlima[4].Code[4] | BYTE
EP2ErrorComKlima4Code5 | INT | IOD_EP2_TCP | 230 | 40230 | ErrorComKlima[4].Code[5] | BYTE
EP2ErrorComKlima4Code6 | INT | IOD_EP2_TCP | 231 | 40231 | ErrorComKlima[4].Code[6] | BYTE
EP2ErrorComKlima4Code7 | INT | IOD_EP2_TCP | 232 | 40232 | ErrorComKlima[4].Code[7] | BYTE
EP2ErrorComKlima4Code8 | INT | IOD_EP2_TCP | 233 | 40233 | ErrorComKlima[4].Code[8] | BYTE
EP2ErrorComKlima4Code9 | INT | IOD_EP2_TCP | 234 | 40234 | ErrorComKlima[4].Code[9] | BYTE
EP2ErrorComKlima4Status | INT | IOD_EP2_TCP | 235 | 40235 | ErrorComKlima[4].Status
EP2ErrorComKlima5Code10 | INT | IOD_EP2_TCP | 236 | 40236 | ErrorComKlima[5].Code[10] | BYTE
EP2ErrorComKlima5Code11 | INT | IOD_EP2_TCP | 237 | 40237 | ErrorComKlima[5].Code[11] | BYTE
EP2ErrorComKlima5Code12 | INT | IOD_EP2_TCP | 238 | 40238 | ErrorComKlima[5].Code[12] | BYTE
EP2ErrorComKlima5Code13 | INT | IOD_EP2_TCP | 239 | 40239 | ErrorComKlima[5].Code[13] | BYTE
EP2ErrorComKlima5Code14 | INT | IOD_EP2_TCP | 240 | 40240 | ErrorComKlima[5].Code[14] | BYTE
EP2ErrorComKlima5Code15 | INT | IOD_EP2_TCP | 241 | 40241 | ErrorComKlima[5].Code[15] | BYTE
EP2ErrorComKlima5Code1 | INT | IOD_EP2_TCP | 242 | 40242 | ErrorComKlima[5].Code[1] | BYTE
EP2ErrorComKlima5Code2 | INT | IOD_EP2_TCP | 243 | 40243 | ErrorComKlima[5].Code[2] | BYTE
EP2ErrorComKlima5Code3 | INT | IOD_EP2_TCP | 244 | 40244 | ErrorComKlima[5].Code[3] | BYTE
EP2ErrorComKlima5Code4 | INT | IOD_EP2_TCP | 245 | 40245 | ErrorComKlima[5].Code[4] | BYTE
EP2ErrorComKlima5Code5 | INT | IOD_EP2_TCP | 246 | 40246 | ErrorComKlima[5].Code[5] | BYTE
EP2ErrorComKlima5Code6 | INT | IOD_EP2_TCP | 247 | 40247 | ErrorComKlima[5].Code[6] | BYTE
EP2ErrorComKlima5Code7 | INT | IOD_EP2_TCP | 248 | 40248 | ErrorComKlima[5].Code[7] | BYTE
EP2ErrorComKlima5Code8 | INT | IOD_EP2_TCP | 249 | 40249 | ErrorComKlima[5].Code[8] | BYTE
EP2ErrorComKlima5Code9 | INT | IOD_EP2_TCP | 250 | 40250 | ErrorComKlima[5].Code[9] | BYTE
EP2ErrorComKlima5Status | INT | IOD_EP2_TCP | 251 | 40251 | ErrorComKlima[5].Status
EP2ErrorComKlima6Code10 | INT | IOD_EP2_TCP | 252 | 40252 | ErrorComKlima[6].Code[10] | BYTE
EP2ErrorComKlima6Code11 | INT | IOD_EP2_TCP | 253 | 40253 | ErrorComKlima[6].Code[11] | BYTE
EP2ErrorComKlima6Code12 | INT | IOD_EP2_TCP | 254 | 40254 | ErrorComKlima[6].Code[12] | BYTE
EP2ErrorComKlima6Code13 | INT | IOD_EP2_TCP | 255 | 40255 | ErrorComKlima[6].Code[13] | BYTE
EP2ErrorComKlima6Code14 | INT | IOD_EP2_TCP | 256 | 40256 | ErrorComKlima[6].Code[14] | BYTE
EP2ErrorComKlima6Code15 | INT | IOD_EP2_TCP | 257 | 40257 | ErrorComKlima[6].Code[15] | BYTE
EP2ErrorComKlima6Code1 | INT | IOD_EP2_TCP | 258 | 40258 | ErrorComKlima[6].Code[1] | BYTE
EP2ErrorComKlima6Code2 | INT | IOD_EP2_TCP | 259 | 40259 | ErrorComKlima[6].Code[2] | BYTE
EP2ErrorComKlima6Code3 | INT | IOD_EP2_TCP | 260 | 40260 | ErrorComKlima[6].Code[3] | BYTE
EP2ErrorComKlima6Code4 | INT | IOD_EP2_TCP | 261 | 40261 | ErrorComKlima[6].Code[4] | BYTE
EP2ErrorComKlima6Code5 | INT | IOD_EP2_TCP | 262 | 40262 | ErrorComKlima[6].Code[5] | BYTE
EP2ErrorComKlima6Code6 | INT | IOD_EP2_TCP | 263 | 40263 | ErrorComKlima[6].Code[6] | BYTE
EP2ErrorComKlima6Code7 | INT | IOD_EP2_TCP | 264 | 40264 | ErrorComKlima[6].Code[7] | BYTE
EP2ErrorComKlima6Code8 | INT | IOD_EP2_TCP | 265 | 40265 | ErrorComKlima[6].Code[8] | BYTE
EP2ErrorComKlima6Code9 | INT | IOD_EP2_TCP | 266 | 40266 | ErrorComKlima[6].Code[9] | BYTE
EP2ErrorComKlima6Status | INT | IOD_EP2_TCP | 267 | 40267 | ErrorComKlima[6].Status
EP2ErrorComPMM1Code10 | INT | IOD_EP2_TCP | 268 | 40268 | ErrorComPMM[1].Code[10] | BYTE
EP2ErrorComPMM1Code11 | INT | IOD_EP2_TCP | 269 | 40269 | ErrorComPMM[1].Code[11] | BYTE
EP2ErrorComPMM1Code12 | INT | IOD_EP2_TCP | 270 | 40270 | ErrorComPMM[1].Code[12] | BYTE
EP2ErrorComPMM1Code13 | INT | IOD_EP2_TCP | 271 | 40271 | ErrorComPMM[1].Code[13] | BYTE
EP2ErrorComPMM1Code14 | INT | IOD_EP2_TCP | 272 | 40272 | ErrorComPMM[1].Code[14] | BYTE
EP2ErrorComPMM1Code15 | INT | IOD_EP2_TCP | 273 | 40273 | ErrorComPMM[1].Code[15] | BYTE
EP2ErrorComPMM1Code1 | INT | IOD_EP2_TCP | 274 | 40274 | ErrorComPMM[1].Code[1] | BYTE
EP2ErrorComPMM1Code2 | INT | IOD_EP2_TCP | 275 | 40275 | ErrorComPMM[1].Code[2] | BYTE
EP2ErrorComPMM1Code3 | INT | IOD_EP2_TCP | 276 | 40276 | ErrorComPMM[1].Code[3] | BYTE
EP2ErrorComPMM1Code4 | INT | IOD_EP2_TCP | 277 | 40277 | ErrorComPMM[1].Code[4] | BYTE
EP2ErrorComPMM1Code5 | INT | IOD_EP2_TCP | 278 | 40278 | ErrorComPMM[1].Code[5] | BYTE
EP2ErrorComPMM1Code6 | INT | IOD_EP2_TCP | 279 | 40279 | ErrorComPMM[1].Code[6] | BYTE
EP2ErrorComPMM1Code7 | INT | IOD_EP2_TCP | 280 | 40280 | ErrorComPMM[1].Code[7] | BYTE
EP2ErrorComPMM1Code8 | INT | IOD_EP2_TCP | 281 | 40281 | ErrorComPMM[1].Code[8] | BYTE
EP2ErrorComPMM1Code9 | INT | IOD_EP2_TCP | 282 | 40282 | ErrorComPMM[1].Code[9] | BYTE
EP2ErrorComPMM1Status | INT | IOD_EP2_TCP | 283 | 40283 | ErrorComPMM[1].Status
EP2ErrorComPMM2Code10 | INT | IOD_EP2_TCP | 284 | 40284 | ErrorComPMM[2].Code[10] | BYTE
EP2ErrorComPMM2Code11 | INT | IOD_EP2_TCP | 285 | 40285 | ErrorComPMM[2].Code[11] | BYTE
EP2ErrorComPMM2Code12 | INT | IOD_EP2_TCP | 286 | 40286 | ErrorComPMM[2].Code[12] | BYTE
EP2ErrorComPMM2Code13 | INT | IOD_EP2_TCP | 287 | 40287 | ErrorComPMM[2].Code[13] | BYTE
EP2ErrorComPMM2Code14 | INT | IOD_EP2_TCP | 288 | 40288 | ErrorComPMM[2].Code[14] | BYTE
EP2ErrorComPMM2Code15 | INT | IOD_EP2_TCP | 289 | 40289 | ErrorComPMM[2].Code[15] | BYTE
EP2ErrorComPMM2Code1 | INT | IOD_EP2_TCP | 290 | 40290 | ErrorComPMM[2].Code[1] | BYTE
EP2ErrorComPMM2Code2 | INT | IOD_EP2_TCP | 291 | 40291 | ErrorComPMM[2].Code[2] | BYTE
EP2ErrorComPMM2Code3 | INT | IOD_EP2_TCP | 292 | 40292 | ErrorComPMM[2].Code[3] | BYTE
EP2ErrorComPMM2Code4 | INT | IOD_EP2_TCP | 293 | 40293 | ErrorComPMM[2].Code[4] | BYTE
EP2ErrorComPMM2Code5 | INT | IOD_EP2_TCP | 294 | 40294 | ErrorComPMM[2].Code[5] | BYTE
EP2ErrorComPMM2Code6 | INT | IOD_EP2_TCP | 295 | 40295 | ErrorComPMM[2].Code[6] | BYTE
EP2ErrorComPMM2Code7 | INT | IOD_EP2_TCP | 296 | 40296 | ErrorComPMM[2].Code[7] | BYTE
EP2ErrorComPMM2Code8 | INT | IOD_EP2_TCP | 297 | 40297 | ErrorComPMM[2].Code[8] | BYTE
EP2ErrorComPMM2Code9 | INT | IOD_EP2_TCP | 298 | 40298 | ErrorComPMM[2].Code[9] | BYTE
EP2ErrorComPMM2Status | INT | IOD_EP2_TCP | 299 | 40299 | ErrorComPMM[2].Status
EP2ErrorComPMM3Code10 | INT | IOD_EP2_TCP | 300 | 40300 | ErrorComPMM[3].Code[10] | BYTE
EP2ErrorComPMM3Code11 | INT | IOD_EP2_TCP | 301 | 40301 | ErrorComPMM[3].Code[11] | BYTE
EP2ErrorComPMM3Code12 | INT | IOD_EP2_TCP | 302 | 40302 | ErrorComPMM[3].Code[12] | BYTE
EP2ErrorComPMM3Code13 | INT | IOD_EP2_TCP | 303 | 40303 | ErrorComPMM[3].Code[13] | BYTE
EP2ErrorComPMM3Code14 | INT | IOD_EP2_TCP | 304 | 40304 | ErrorComPMM[3].Code[14] | BYTE
EP2ErrorComPMM3Code15 | INT | IOD_EP2_TCP | 305 | 40305 | ErrorComPMM[3].Code[15] | BYTE
EP2ErrorComPMM3Code1 | INT | IOD_EP2_TCP | 306 | 40306 | ErrorComPMM[3].Code[1] | BYTE
EP2ErrorComPMM3Code2 | INT | IOD_EP2_TCP | 307 | 40307 | ErrorComPMM[3].Code[2] | BYTE
EP2ErrorComPMM3Code3 | INT | IOD_EP2_TCP | 308 | 40308 | ErrorComPMM[3].Code[3] | BYTE
EP2ErrorComPMM3Code4 | INT | IOD_EP2_TCP | 309 | 40309 | ErrorComPMM[3].Code[4] | BYTE
EP2ErrorComPMM3Code5 | INT | IOD_EP2_TCP | 310 | 40310 | ErrorComPMM[3].Code[5] | BYTE
EP2ErrorComPMM3Code6 | INT | IOD_EP2_TCP | 311 | 40311 | ErrorComPMM[3].Code[6] | BYTE
EP2ErrorComPMM3Code7 | INT | IOD_EP2_TCP | 312 | 40312 | ErrorComPMM[3].Code[7] | BYTE
EP2ErrorComPMM3Code8 | INT | IOD_EP2_TCP | 313 | 40313 | ErrorComPMM[3].Code[8] | BYTE
EP2ErrorComPMM3Code9 | INT | IOD_EP2_TCP | 314 | 40314 | ErrorComPMM[3].Code[9] | BYTE
EP2ErrorComPMM3Status | INT | IOD_EP2_TCP | 315 | 40315 | ErrorComPMM[3].Status
EP2ErrorComUPS1Code10 | INT | IOD_EP2_TCP | 316 | 40316 | ErrorComUPS[1].Code[10] | BYTE
EP2ErrorComUPS1Code11 | INT | IOD_EP2_TCP | 317 | 40317 | ErrorComUPS[1].Code[11] | BYTE
EP2ErrorComUPS1Code12 | INT | IOD_EP2_TCP | 318 | 40318 | ErrorComUPS[1].Code[12] | BYTE
EP2ErrorComUPS1Code13 | INT | IOD_EP2_TCP | 319 | 40319 | ErrorComUPS[1].Code[13] | BYTE
EP2ErrorComUPS1Code14 | INT | IOD_EP2_TCP | 320 | 40320 | ErrorComUPS[1].Code[14] | BYTE
EP2ErrorComUPS1Code15 | INT | IOD_EP2_TCP | 321 | 40321 | ErrorComUPS[1].Code[15] | BYTE
EP2ErrorComUPS1Code1 | INT | IOD_EP2_TCP | 322 | 40322 | ErrorComUPS[1].Code[1] | BYTE
EP2ErrorComUPS1Code2 | INT | IOD_EP2_TCP | 323 | 40323 | ErrorComUPS[1].Code[2] | BYTE
EP2ErrorComUPS1Code3 | INT | IOD_EP2_TCP | 324 | 40324 | ErrorComUPS[1].Code[3] | BYTE
EP2ErrorComUPS1Code4 | INT | IOD_EP2_TCP | 325 | 40325 | ErrorComUPS[1].Code[4] | BYTE
EP2ErrorComUPS1Code5 | INT | IOD_EP2_TCP | 326 | 40326 | ErrorComUPS[1].Code[5] | BYTE
EP2ErrorComUPS1Code6 | INT | IOD_EP2_TCP | 327 | 40327 | ErrorComUPS[1].Code[6] | BYTE
EP2ErrorComUPS1Code7 | INT | IOD_EP2_TCP | 328 | 40328 | ErrorComUPS[1].Code[7] | BYTE
EP2ErrorComUPS1Code8 | INT | IOD_EP2_TCP | 329 | 40329 | ErrorComUPS[1].Code[8] | BYTE
EP2ErrorComUPS1Code9 | INT | IOD_EP2_TCP | 330 | 40330 | ErrorComUPS[1].Code[9] | BYTE
EP2ErrorComUPS1Status | INT | IOD_EP2_TCP | 331 | 40331 | ErrorComUPS[1].Status
EP2ErrorComUPS2Code10 | INT | IOD_EP2_TCP | 332 | 40332 | ErrorComUPS[2].Code[10] | BYTE
EP2ErrorComUPS2Code11 | INT | IOD_EP2_TCP | 333 | 40333 | ErrorComUPS[2].Code[11] | BYTE
EP2ErrorComUPS2Code12 | INT | IOD_EP2_TCP | 334 | 40334 | ErrorComUPS[2].Code[12] | BYTE
EP2ErrorComUPS2Code13 | INT | IOD_EP2_TCP | 335 | 40335 | ErrorComUPS[2].Code[13] | BYTE
EP2ErrorComUPS2Code14 | INT | IOD_EP2_TCP | 336 | 40336 | ErrorComUPS[2].Code[14] | BYTE
EP2ErrorComUPS2Code15 | INT | IOD_EP2_TCP | 337 | 40337 | ErrorComUPS[2].Code[15] | BYTE
EP2ErrorComUPS2Code1 | INT | IOD_EP2_TCP | 338 | 40338 | ErrorComUPS[2].Code[1] | BYTE
EP2ErrorComUPS2Code2 | INT | IOD_EP2_TCP | 339 | 40339 | ErrorComUPS[2].Code[2] | BYTE
EP2ErrorComUPS2Code3 | INT | IOD_EP2_TCP | 340 | 40340 | ErrorComUPS[2].Code[3] | BYTE
EP2ErrorComUPS2Code4 | INT | IOD_EP2_TCP | 341 | 40341 | ErrorComUPS[2].Code[4] | BYTE
EP2ErrorComUPS2Code5 | INT | IOD_EP2_TCP | 342 | 40342 | ErrorComUPS[2].Code[5] | BYTE
EP2ErrorComUPS2Code6 | INT | IOD_EP2_TCP | 343 | 40343 | ErrorComUPS[2].Code[6] | BYTE
EP2ErrorComUPS2Code7 | INT | IOD_EP2_TCP | 344 | 40344 | ErrorComUPS[2].Code[7] | BYTE
EP2ErrorComUPS2Code8 | INT | IOD_EP2_TCP | 345 | 40345 | ErrorComUPS[2].Code[8] | BYTE
EP2ErrorComUPS2Code9 | INT | IOD_EP2_TCP | 346 | 40346 | ErrorComUPS[2].Code[9] | BYTE
EP2ErrorComUPS2Status | INT | IOD_EP2_TCP | 347 | 40347 | ErrorComUPS[2].Status
EP2KlimaGalGrelecStatus | INT | IOD_EP2_TCP | 348 | 40348 | KlimaGal.GrelecStatus | BYTE
EP2KlimaGalIzhodniVentStatus | INT | IOD_EP2_TCP | 349 | 40349 | KlimaGal.IzhodniVentStatus | BYTE
EP2KlimaGalKompresorStatus | INT | IOD_EP2_TCP | 350 | 40350 | KlimaGal.KompresorStatus | BYTE
EP2KlimaGalVlazilecStatus | INT | IOD_EP2_TCP | 351 | 40351 | KlimaGal.VlazilecStatus | BYTE
EP2PMMgalAlarmPhase1GlobalAlarmReg | INT | IOD_EP2_TCP | 352 | 40352 | PMMgal.AlarmPhase[1].GlobalAlarmReg
EP2PMMgalAlarmPhase2GlobalAlarmReg | INT | IOD_EP2_TCP | 353 | 40353 | PMMgal.AlarmPhase[2].GlobalAlarmReg
EP2PMMgalAlarmPhase3GlobalAlarmReg | INT | IOD_EP2_TCP | 354 | 40354 | PMMgal.AlarmPhase[3].GlobalAlarmReg
EP2kom_nast_cas_izpada | INT | IOD_EP2_TCP | 355 | 40355 | kom_nast_cas_izpada
EP2_Circ1_CosFi_III | REAL | IOD_EP2_TCP | 4001 | 44001 | Circ[1].CosFi_III
EP2_Circ1_DelovnaEnergija | REAL | IOD_EP2_TCP | 4003 | 44003 | Circ[1].DelovnaEnergija
EP2_Circ1_DelovnaMoc_III | REAL | IOD_EP2_TCP | 4005 | 44005 | Circ[1].DelovnaMoc_III
EP2_Circ1_DelovnaMoc_L1 | REAL | IOD_EP2_TCP | 4007 | 44007 | Circ[1].DelovnaMoc_L1
EP2_Circ1_DelovnaMoc_L2 | REAL | IOD_EP2_TCP | 4009 | 44009 | Circ[1].DelovnaMoc_L2
EP2_Circ1_DelovnaMoc_L3 | REAL | IOD_EP2_TCP | 4011 | 44011 | Circ[1].DelovnaMoc_L3
EP2_Circ1_Frekvenca_L1 | REAL | IOD_EP2_TCP | 4013 | 44013 | Circ[1].Frekvenca_L1
EP2_Circ1_InduktivnaEnergija | REAL | IOD_EP2_TCP | 4015 | 44015 | Circ[1].InduktivnaEnergija
EP2_Circ1_InduktivnaMoc_III | REAL | IOD_EP2_TCP | 4017 | 44017 | Circ[1].InduktivnaMoc_III
EP2_Circ1_JalovaMoc_L1 | REAL | IOD_EP2_TCP | 4019 | 44019 | Circ[1].JalovaMoc_L1
EP2_Circ1_JalovaMoc_L2 | REAL | IOD_EP2_TCP | 4021 | 44021 | Circ[1].JalovaMoc_L2
EP2_Circ1_JalovaMoc_L3 | REAL | IOD_EP2_TCP | 4023 | 44023 | Circ[1].JalovaMoc_L3
EP2_Circ1_KapacitivnaEnergija | REAL | IOD_EP2_TCP | 4025 | 44025 | Circ[1].KapacitivnaEnergija
EP2_Circ1_KapacitivnaMoc_III | REAL | IOD_EP2_TCP | 4027 | 44027 | Circ[1].KapacitivnaMoc_III
EP2_Circ1_MaximumDemand | REAL | IOD_EP2_TCP | 4029 | 44029 | Circ[1].MaximumDemand
EP2_Circ1_Napetost_L1_L2 | REAL | IOD_EP2_TCP | 4031 | 44031 | Circ[1].Napetost_L1_L2
EP2_Circ1_Napetost_L1_N | REAL | IOD_EP2_TCP | 4033 | 44033 | Circ[1].Napetost_L1_N
EP2_Circ1_Napetost_L2_L3 | REAL | IOD_EP2_TCP | 4035 | 44035 | Circ[1].Napetost_L2_L3
EP2_Circ1_Napetost_L2_N | REAL | IOD_EP2_TCP | 4037 | 44037 | Circ[1].Napetost_L2_N
EP2_Circ1_Napetost_L3_L1 | REAL | IOD_EP2_TCP | 4039 | 44039 | Circ[1].Napetost_L3_L1
EP2_Circ1_Napetost_L3_N | REAL | IOD_EP2_TCP | 4041 | 44041 | Circ[1].Napetost_L3_N
EP2_Circ1_NavideznaMoc_III | REAL | IOD_EP2_TCP | 4043 | 44043 | Circ[1].NavideznaMoc_III
EP2_Circ1_NicelniTok | REAL | IOD_EP2_TCP | 4045 | 44045 | Circ[1].NicelniTok
EP2_Circ1_PowerFactor_III | REAL | IOD_EP2_TCP | 4047 | 44047 | Circ[1].PowerFactor_III
EP2_Circ1_PowerFactor_L1 | REAL | IOD_EP2_TCP | 4049 | 44049 | Circ[1].PowerFactor_L1
EP2_Circ1_PowerFactor_L2 | REAL | IOD_EP2_TCP | 4051 | 44051 | Circ[1].PowerFactor_L2
EP2_Circ1_PowerFactor_L3 | REAL | IOD_EP2_TCP | 4053 | 44053 | Circ[1].PowerFactor_L3
EP2_Circ1_THDI_L1 | REAL | IOD_EP2_TCP | 4055 | 44055 | Circ[1].THDI_L1
EP2_Circ1_THDI_L2 | REAL | IOD_EP2_TCP | 4057 | 44057 | Circ[1].THDI_L2
EP2_Circ1_THDI_L3 | REAL | IOD_EP2_TCP | 4059 | 44059 | Circ[1].THDI_L3
EP2_Circ1_THDV_L1 | REAL | IOD_EP2_TCP | 4061 | 44061 | Circ[1].THDV_L1
EP2_Circ1_THDV_L2 | REAL | IOD_EP2_TCP | 4063 | 44063 | Circ[1].THDV_L2
EP2_Circ1_THDV_L3 | REAL | IOD_EP2_TCP | 4065 | 44065 | Circ[1].THDV_L3
EP2_Circ1_Tok_L1 | REAL | IOD_EP2_TCP | 4067 | 44067 | Circ[1].Tok_L1
EP2_Circ1_Tok_L2 | REAL | IOD_EP2_TCP | 4069 | 44069 | Circ[1].Tok_L2
EP2_Circ1_Tok_L3 | REAL | IOD_EP2_TCP | 4071 | 44071 | Circ[1].Tok_L3
EP2_Circ1_TokPovprecje_III | REAL | IOD_EP2_TCP | 4073 | 44073 | Circ[1].TokPovprecje_III
EP2_Circutor_CosFi_III | REAL | IOD_EP2_TCP | 4075 | 44075 | Circutor.CosFi_III
EP2_Circutor_DelovnaEnergija | REAL | IOD_EP2_TCP | 4077 | 44077 | Circutor.DelovnaEnergija
EP2_Circutor_DelovnaMoc_III | REAL | IOD_EP2_TCP | 4079 | 44079 | Circutor.DelovnaMoc_III
EP2_Circutor_DelovnaMoc_L1 | REAL | IOD_EP2_TCP | 4081 | 44081 | Circutor.DelovnaMoc_L1
EP2_Circutor_DelovnaMoc_L2 | REAL | IOD_EP2_TCP | 4083 | 44083 | Circutor.DelovnaMoc_L2
EP2_Circutor_DelovnaMoc_L3 | REAL | IOD_EP2_TCP | 4085 | 44085 | Circutor.DelovnaMoc_L3
EP2_Circutor_Frekvenca_L1 | REAL | IOD_EP2_TCP | 4087 | 44087 | Circutor.Frekvenca_L1
EP2_Circutor_InduktivnaEnergija | REAL | IOD_EP2_TCP | 4089 | 44089 | Circutor.InduktivnaEnergija
EP2_Circutor_InduktivnaMoc_III | REAL | IOD_EP2_TCP | 4091 | 44091 | Circutor.InduktivnaMoc_III
EP2_Circutor_JalovaMoc_L1 | REAL | IOD_EP2_TCP | 4093 | 44093 | Circutor.JalovaMoc_L1
EP2_Circutor_JalovaMoc_L2 | REAL | IOD_EP2_TCP | 4095 | 44095 | Circutor.JalovaMoc_L2
EP2_Circutor_JalovaMoc_L3 | REAL | IOD_EP2_TCP | 4097 | 44097 | Circutor.JalovaMoc_L3
EP2_Circutor_KapacitivnaEnergija | REAL | IOD_EP2_TCP | 4099 | 44099 | Circutor.KapacitivnaEnergija
EP2_Circutor_KapacitivnaMoc_III | REAL | IOD_EP2_TCP | 4101 | 44101 | Circutor.KapacitivnaMoc_III
EP2_Circutor_MaximumDemand | REAL | IOD_EP2_TCP | 4103 | 44103 | Circutor.MaximumDemand
EP2_Circutor_Napetost_L1_L2 | REAL | IOD_EP2_TCP | 4105 | 44105 | Circutor.Napetost_L1_L2
EP2_Circutor_Napetost_L1_N | REAL | IOD_EP2_TCP | 4107 | 44107 | Circutor.Napetost_L1_N
EP2_Circutor_Napetost_L2_L3 | REAL | IOD_EP2_TCP | 4109 | 44109 | Circutor.Napetost_L2_L3
EP2_Circutor_Napetost_L2_N | REAL | IOD_EP2_TCP | 4111 | 44111 | Circutor.Napetost_L2_N
EP2_Circutor_Napetost_L3_L1 | REAL | IOD_EP2_TCP | 4113 | 44113 | Circutor.Napetost_L3_L1
EP2_Circutor_Napetost_L3_N | REAL | IOD_EP2_TCP | 4115 | 44115 | Circutor.Napetost_L3_N
EP2_Circutor_NavideznaMoc_III | REAL | IOD_EP2_TCP | 4117 | 44117 | Circutor.NavideznaMoc_III
EP2_Circutor_NicelniTok | REAL | IOD_EP2_TCP | 4119 | 44119 | Circutor.NicelniTok
EP2_Circutor_PowerFactor_III | REAL | IOD_EP2_TCP | 4121 | 44121 | Circutor.PowerFactor_III
EP2_Circutor_PowerFactor_L1 | REAL | IOD_EP2_TCP | 4123 | 44123 | Circutor.PowerFactor_L1
EP2_Circutor_PowerFactor_L2 | REAL | IOD_EP2_TCP | 4125 | 44125 | Circutor.PowerFactor_L2
EP2_Circutor_PowerFactor_L3 | REAL | IOD_EP2_TCP | 4127 | 44127 | Circutor.PowerFactor_L3
EP2_Circutor_THDI_L1 | REAL | IOD_EP2_TCP | 4129 | 44129 | Circutor.THDI_L1
EP2_Circutor_THDI_L2 | REAL | IOD_EP2_TCP | 4131 | 44131 | Circutor.THDI_L2
EP2_Circutor_THDI_L3 | REAL | IOD_EP2_TCP | 4133 | 44133 | Circutor.THDI_L3
EP2_Circutor_THDV_L1 | REAL | IOD_EP2_TCP | 4135 | 44135 | Circutor.THDV_L1
EP2_Circutor_THDV_L2 | REAL | IOD_EP2_TCP | 4137 | 44137 | Circutor.THDV_L2
EP2_Circutor_THDV_L3 | REAL | IOD_EP2_TCP | 4139 | 44139 | Circutor.THDV_L3
EP2_Circutor_Tok_L1 | REAL | IOD_EP2_TCP | 4141 | 44141 | Circutor.Tok_L1
EP2_Circutor_Tok_L2 | REAL | IOD_EP2_TCP | 4143 | 44143 | Circutor.Tok_L2
EP2_Circutor_Tok_L3 | REAL | IOD_EP2_TCP | 4145 | 44145 | Circutor.Tok_L3
EP2_Circutor_TokPovprecje_III | REAL | IOD_EP2_TCP | 4147 | 44147 | Circutor.TokPovprecje_III
EP2_Klima1_NastMaxTemp | REAL | IOD_EP2_TCP | 4149 | 44149 | Klima[1].NastMaxTemp
EP2_Klima1_NastMaxVlaznost | REAL | IOD_EP2_TCP | 4151 | 44151 | Klima[1].NastMaxVlaznost
EP2_Klima1_NastMinTemp | REAL | IOD_EP2_TCP | 4153 | 44153 | Klima[1].NastMinTemp
EP2_Klima1_NastMinVlaznost | REAL | IOD_EP2_TCP | 4155 | 44155 | Klima[1].NastMinVlaznost
EP2_Klima1_NastTempProstora | REAL | IOD_EP2_TCP | 4157 | 44157 | Klima[1].NastTempProstora
EP2_Klima1_NastVlaznost | REAL | IOD_EP2_TCP | 4159 | 44159 | Klima[1].NastVlaznost
EP2_Klima1_ObratovalneUre | REAL | IOD_EP2_TCP | 4161 | 44161 | Klima[1].ObratovalneUre
EP2_Klima1_TemperaturaProstora | REAL | IOD_EP2_TCP | 4163 | 44163 | Klima[1].TemperaturaProstora
EP2_Klima1_TempIzpihanegaZraka | REAL | IOD_EP2_TCP | 4165 | 44165 | Klima[1].TempIzpihanegaZraka
EP2_Klima1_TempPovratneVode | REAL | IOD_EP2_TCP | 4167 | 44167 | Klima[1].TempPovratneVode
EP2_Klima1_VlaznostProstora | REAL | IOD_EP2_TCP | 4169 | 44169 | Klima[1].VlaznostProstora
EP2_Klima1_ZunanjaTemp | REAL | IOD_EP2_TCP | 4171 | 44171 | Klima[1].ZunanjaTemp
EP2_Klima2_NastMaxTemp | REAL | IOD_EP2_TCP | 4173 | 44173 | Klima[2].NastMaxTemp
EP2_Klima2_NastMaxVlaznost | REAL | IOD_EP2_TCP | 4175 | 44175 | Klima[2].NastMaxVlaznost
EP2_Klima2_NastMinTemp | REAL | IOD_EP2_TCP | 4177 | 44177 | Klima[2].NastMinTemp
EP2_Klima2_NastMinVlaznost | REAL | IOD_EP2_TCP | 4179 | 44179 | Klima[2].NastMinVlaznost
EP2_Klima2_NastTempProstora | REAL | IOD_EP2_TCP | 4181 | 44181 | Klima[2].NastTempProstora
EP2_Klima2_NastVlaznost | REAL | IOD_EP2_TCP | 4183 | 44183 | Klima[2].NastVlaznost
EP2_Klima2_ObratovalneUre | REAL | IOD_EP2_TCP | 4185 | 44185 | Klima[2].ObratovalneUre
EP2_Klima2_TemperaturaProstora | REAL | IOD_EP2_TCP | 4187 | 44187 | Klima[2].TemperaturaProstora
EP2_Klima2_TempIzpihanegaZraka | REAL | IOD_EP2_TCP | 4189 | 44189 | Klima[2].TempIzpihanegaZraka
EP2_Klima2_TempPovratneVode | REAL | IOD_EP2_TCP | 4191 | 44191 | Klima[2].TempPovratneVode
EP2_Klima2_VlaznostProstora | REAL | IOD_EP2_TCP | 4193 | 44193 | Klima[2].VlaznostProstora
EP2_Klima2_ZunanjaTemp | REAL | IOD_EP2_TCP | 4195 | 44195 | Klima[2].ZunanjaTemp
EP2_PMM1_ActivePowerPhaseA_kW | REAL | IOD_EP2_TCP | 4197 | 44197 | PMM[1].ActivePowerPhaseA_kW
EP2_PMM1_ActivePowerPhaseB_kW | REAL | IOD_EP2_TCP | 4199 | 44199 | PMM[1].ActivePowerPhaseB_kW
EP2_PMM1_ActivePowerPhaseC_kW | REAL | IOD_EP2_TCP | 4201 | 44201 | PMM[1].ActivePowerPhaseC_kW
EP2_PMM1_AverageCurrent_A | REAL | IOD_EP2_TCP | 4203 | 44203 | PMM[1].AverageCurrent_A
EP2_PMM1_AveragePhaseToNeutral_V | REAL | IOD_EP2_TCP | 4205 | 44205 | PMM[1].AveragePhaseToNeutral_V
EP2_PMM1_AveragePhaseToPhase_V | REAL | IOD_EP2_TCP | 4207 | 44207 | PMM[1].AveragePhaseToPhase_V
EP2_PMM1_CurrentInPhaseA_A | REAL | IOD_EP2_TCP | 4209 | 44209 | PMM[1].CurrentInPhaseA_A
EP2_PMM1_CurrentInPhaseB_A | REAL | IOD_EP2_TCP | 4211 | 44211 | PMM[1].CurrentInPhaseB_A
EP2_PMM1_CurrentInPhaseC_A | REAL | IOD_EP2_TCP | 4213 | 44213 | PMM[1].CurrentInPhaseC_A
EP2_PMM1_EnergyConsumed_kWh | REAL | IOD_EP2_TCP | 4215 | 44215 | PMM[1].EnergyConsumed_kWh
EP2_PMM1_Frequency_Hz | REAL | IOD_EP2_TCP | 4217 | 44217 | PMM[1].Frequency_Hz
EP2_PMM1_NeutralCurrent_A | REAL | IOD_EP2_TCP | 4219 | 44219 | PMM[1].NeutralCurrent_A
EP2_PMM1_Phase1_Current10 | REAL | IOD_EP2_TCP | 4221 | 44221 | PMM[1].Phase[1].Current[10]
EP2_PMM1_Phase1_Current11 | REAL | IOD_EP2_TCP | 4223 | 44223 | PMM[1].Phase[1].Current[11]
EP2_PMM1_Phase1_Current12 | REAL | IOD_EP2_TCP | 4225 | 44225 | PMM[1].Phase[1].Current[12]
EP2_PMM1_Phase1_Current13 | REAL | IOD_EP2_TCP | 4227 | 44227 | PMM[1].Phase[1].Current[13]
EP2_PMM1_Phase1_Current14 | REAL | IOD_EP2_TCP | 4229 | 44229 | PMM[1].Phase[1].Current[14]
EP2_PMM1_Phase1_Current15 | REAL | IOD_EP2_TCP | 4231 | 44231 | PMM[1].Phase[1].Current[15]
EP2_PMM1_Phase1_Current16 | REAL | IOD_EP2_TCP | 4233 | 44233 | PMM[1].Phase[1].Current[16]
EP2_PMM1_Phase1_Current17 | REAL | IOD_EP2_TCP | 4235 | 44235 | PMM[1].Phase[1].Current[17]
EP2_PMM1_Phase1_Current18 | REAL | IOD_EP2_TCP | 4237 | 44237 | PMM[1].Phase[1].Current[18]
EP2_PMM1_Phase1_Current19 | REAL | IOD_EP2_TCP | 4239 | 44239 | PMM[1].Phase[1].Current[19]
EP2_PMM1_Phase1_Current1 | REAL | IOD_EP2_TCP | 4241 | 44241 | PMM[1].Phase[1].Current[1]
EP2_PMM1_Phase1_Current20 | REAL | IOD_EP2_TCP | 4243 | 44243 | PMM[1].Phase[1].Current[20]
EP2_PMM1_Phase1_Current21 | REAL | IOD_EP2_TCP | 4245 | 44245 | PMM[1].Phase[1].Current[21]
EP2_PMM1_Phase1_Current22 | REAL | IOD_EP2_TCP | 4247 | 44247 | PMM[1].Phase[1].Current[22]
EP2_PMM1_Phase1_Current23 | REAL | IOD_EP2_TCP | 4249 | 44249 | PMM[1].Phase[1].Current[23]
EP2_PMM1_Phase1_Current24 | REAL | IOD_EP2_TCP | 4251 | 44251 | PMM[1].Phase[1].Current[24]
EP2_PMM1_Phase1_Current25 | REAL | IOD_EP2_TCP | 4253 | 44253 | PMM[1].Phase[1].Current[25]
EP2_PMM1_Phase1_Current26 | REAL | IOD_EP2_TCP | 4255 | 44255 | PMM[1].Phase[1].Current[26]
EP2_PMM1_Phase1_Current27 | REAL | IOD_EP2_TCP | 4257 | 44257 | PMM[1].Phase[1].Current[27]
EP2_PMM1_Phase1_Current28 | REAL | IOD_EP2_TCP | 4259 | 44259 | PMM[1].Phase[1].Current[28]
EP2_PMM1_Phase1_Current29 | REAL | IOD_EP2_TCP | 4261 | 44261 | PMM[1].Phase[1].Current[29]
EP2_PMM1_Phase1_Current2 | REAL | IOD_EP2_TCP | 4263 | 44263 | PMM[1].Phase[1].Current[2]
EP2_PMM1_Phase1_Current30 | REAL | IOD_EP2_TCP | 4265 | 44265 | PMM[1].Phase[1].Current[30]
EP2_PMM1_Phase1_Current31 | REAL | IOD_EP2_TCP | 4267 | 44267 | PMM[1].Phase[1].Current[31]
EP2_PMM1_Phase1_Current32 | REAL | IOD_EP2_TCP | 4269 | 44269 | PMM[1].Phase[1].Current[32]
EP2_PMM1_Phase1_Current33 | REAL | IOD_EP2_TCP | 4271 | 44271 | PMM[1].Phase[1].Current[33]
EP2_PMM1_Phase1_Current34 | REAL | IOD_EP2_TCP | 4273 | 44273 | PMM[1].Phase[1].Current[34]
EP2_PMM1_Phase1_Current35 | REAL | IOD_EP2_TCP | 4275 | 44275 | PMM[1].Phase[1].Current[35]
EP2_PMM1_Phase1_Current36 | REAL | IOD_EP2_TCP | 4277 | 44277 | PMM[1].Phase[1].Current[36]
EP2_PMM1_Phase1_Current37 | REAL | IOD_EP2_TCP | 4279 | 44279 | PMM[1].Phase[1].Current[37]
EP2_PMM1_Phase1_Current38 | REAL | IOD_EP2_TCP | 4281 | 44281 | PMM[1].Phase[1].Current[38]
EP2_PMM1_Phase1_Current39 | REAL | IOD_EP2_TCP | 4283 | 44283 | PMM[1].Phase[1].Current[39]
EP2_PMM1_Phase1_Current3 | REAL | IOD_EP2_TCP | 4285 | 44285 | PMM[1].Phase[1].Current[3]
EP2_PMM1_Phase1_Current40 | REAL | IOD_EP2_TCP | 4287 | 44287 | PMM[1].Phase[1].Current[40]
EP2_PMM1_Phase1_Current41 | REAL | IOD_EP2_TCP | 4289 | 44289 | PMM[1].Phase[1].Current[41]
EP2_PMM1_Phase1_Current42 | REAL | IOD_EP2_TCP | 4291 | 44291 | PMM[1].Phase[1].Current[42]
EP2_PMM1_Phase1_Current4 | REAL | IOD_EP2_TCP | 4293 | 44293 | PMM[1].Phase[1].Current[4]
EP2_PMM1_Phase1_Current5 | REAL | IOD_EP2_TCP | 4295 | 44295 | PMM[1].Phase[1].Current[5]
EP2_PMM1_Phase1_Current6 | REAL | IOD_EP2_TCP | 4297 | 44297 | PMM[1].Phase[1].Current[6]
EP2_PMM1_Phase1_Current7 | REAL | IOD_EP2_TCP | 4299 | 44299 | PMM[1].Phase[1].Current[7]
EP2_PMM1_Phase1_Current8 | REAL | IOD_EP2_TCP | 4301 | 44301 | PMM[1].Phase[1].Current[8]
EP2_PMM1_Phase1_Current9 | REAL | IOD_EP2_TCP | 4303 | 44303 | PMM[1].Phase[1].Current[9]
EP2_PMM1_Phase2_Current10 | REAL | IOD_EP2_TCP | 4305 | 44305 | PMM[1].Phase[2].Current[10]
EP2_PMM1_Phase2_Current11 | REAL | IOD_EP2_TCP | 4307 | 44307 | PMM[1].Phase[2].Current[11]
EP2_PMM1_Phase2_Current12 | REAL | IOD_EP2_TCP | 4309 | 44309 | PMM[1].Phase[2].Current[12]
EP2_PMM1_Phase2_Current13 | REAL | IOD_EP2_TCP | 4311 | 44311 | PMM[1].Phase[2].Current[13]
EP2_PMM1_Phase2_Current14 | REAL | IOD_EP2_TCP | 4313 | 44313 | PMM[1].Phase[2].Current[14]
EP2_PMM1_Phase2_Current15 | REAL | IOD_EP2_TCP | 4315 | 44315 | PMM[1].Phase[2].Current[15]
EP2_PMM1_Phase2_Current16 | REAL | IOD_EP2_TCP | 4317 | 44317 | PMM[1].Phase[2].Current[16]
EP2_PMM1_Phase2_Current17 | REAL | IOD_EP2_TCP | 4319 | 44319 | PMM[1].Phase[2].Current[17]
EP2_PMM1_Phase2_Current18 | REAL | IOD_EP2_TCP | 4321 | 44321 | PMM[1].Phase[2].Current[18]
EP2_PMM1_Phase2_Current19 | REAL | IOD_EP2_TCP | 4323 | 44323 | PMM[1].Phase[2].Current[19]
EP2_PMM1_Phase2_Current1 | REAL | IOD_EP2_TCP | 4325 | 44325 | PMM[1].Phase[2].Current[1]
EP2_PMM1_Phase2_Current20 | REAL | IOD_EP2_TCP | 4327 | 44327 | PMM[1].Phase[2].Current[20]
EP2_PMM1_Phase2_Current21 | REAL | IOD_EP2_TCP | 4329 | 44329 | PMM[1].Phase[2].Current[21]
EP2_PMM1_Phase2_Current22 | REAL | IOD_EP2_TCP | 4331 | 44331 | PMM[1].Phase[2].Current[22]
EP2_PMM1_Phase2_Current23 | REAL | IOD_EP2_TCP | 4333 | 44333 | PMM[1].Phase[2].Current[23]
EP2_PMM1_Phase2_Current24 | REAL | IOD_EP2_TCP | 4335 | 44335 | PMM[1].Phase[2].Current[24]
EP2_PMM1_Phase2_Current25 | REAL | IOD_EP2_TCP | 4337 | 44337 | PMM[1].Phase[2].Current[25]
EP2_PMM1_Phase2_Current26 | REAL | IOD_EP2_TCP | 4339 | 44339 | PMM[1].Phase[2].Current[26]
EP2_PMM1_Phase2_Current27 | REAL | IOD_EP2_TCP | 4341 | 44341 | PMM[1].Phase[2].Current[27]
EP2_PMM1_Phase2_Current28 | REAL | IOD_EP2_TCP | 4343 | 44343 | PMM[1].Phase[2].Current[28]
EP2_PMM1_Phase2_Current29 | REAL | IOD_EP2_TCP | 4345 | 44345 | PMM[1].Phase[2].Current[29]
EP2_PMM1_Phase2_Current2 | REAL | IOD_EP2_TCP | 4347 | 44347 | PMM[1].Phase[2].Current[2]
EP2_PMM1_Phase2_Current30 | REAL | IOD_EP2_TCP | 4349 | 44349 | PMM[1].Phase[2].Current[30]
EP2_PMM1_Phase2_Current31 | REAL | IOD_EP2_TCP | 4351 | 44351 | PMM[1].Phase[2].Current[31]
EP2_PMM1_Phase2_Current32 | REAL | IOD_EP2_TCP | 4353 | 44353 | PMM[1].Phase[2].Current[32]
EP2_PMM1_Phase2_Current33 | REAL | IOD_EP2_TCP | 4355 | 44355 | PMM[1].Phase[2].Current[33]
EP2_PMM1_Phase2_Current34 | REAL | IOD_EP2_TCP | 4357 | 44357 | PMM[1].Phase[2].Current[34]
EP2_PMM1_Phase2_Current35 | REAL | IOD_EP2_TCP | 4359 | 44359 | PMM[1].Phase[2].Current[35]
EP2_PMM1_Phase2_Current36 | REAL | IOD_EP2_TCP | 4361 | 44361 | PMM[1].Phase[2].Current[36]
EP2_PMM1_Phase2_Current37 | REAL | IOD_EP2_TCP | 4363 | 44363 | PMM[1].Phase[2].Current[37]
EP2_PMM1_Phase2_Current38 | REAL | IOD_EP2_TCP | 4365 | 44365 | PMM[1].Phase[2].Current[38]
EP2_PMM1_Phase2_Current39 | REAL | IOD_EP2_TCP | 4367 | 44367 | PMM[1].Phase[2].Current[39]
EP2_PMM1_Phase2_Current3 | REAL | IOD_EP2_TCP | 4369 | 44369 | PMM[1].Phase[2].Current[3]
EP2_PMM1_Phase2_Current40 | REAL | IOD_EP2_TCP | 4371 | 44371 | PMM[1].Phase[2].Current[40]
EP2_PMM1_Phase2_Current41 | REAL | IOD_EP2_TCP | 4373 | 44373 | PMM[1].Phase[2].Current[41]
EP2_PMM1_Phase2_Current42 | REAL | IOD_EP2_TCP | 4375 | 44375 | PMM[1].Phase[2].Current[42]
EP2_PMM1_Phase2_Current4 | REAL | IOD_EP2_TCP | 4377 | 44377 | PMM[1].Phase[2].Current[4]
EP2_PMM1_Phase2_Current5 | REAL | IOD_EP2_TCP | 4379 | 44379 | PMM[1].Phase[2].Current[5]
EP2_PMM1_Phase2_Current6 | REAL | IOD_EP2_TCP | 4381 | 44381 | PMM[1].Phase[2].Current[6]
EP2_PMM1_Phase2_Current7 | REAL | IOD_EP2_TCP | 4383 | 44383 | PMM[1].Phase[2].Current[7]
EP2_PMM1_Phase2_Current8 | REAL | IOD_EP2_TCP | 4385 | 44385 | PMM[1].Phase[2].Current[8]
EP2_PMM1_Phase2_Current9 | REAL | IOD_EP2_TCP | 4387 | 44387 | PMM[1].Phase[2].Current[9]
EP2_PMM1_Phase3_Current10 | REAL | IOD_EP2_TCP | 4389 | 44389 | PMM[1].Phase[3].Current[10]
EP2_PMM1_Phase3_Current11 | REAL | IOD_EP2_TCP | 4391 | 44391 | PMM[1].Phase[3].Current[11]
EP2_PMM1_Phase3_Current12 | REAL | IOD_EP2_TCP | 4393 | 44393 | PMM[1].Phase[3].Current[12]
EP2_PMM1_Phase3_Current13 | REAL | IOD_EP2_TCP | 4395 | 44395 | PMM[1].Phase[3].Current[13]
EP2_PMM1_Phase3_Current14 | REAL | IOD_EP2_TCP | 4397 | 44397 | PMM[1].Phase[3].Current[14]
EP2_PMM1_Phase3_Current15 | REAL | IOD_EP2_TCP | 4399 | 44399 | PMM[1].Phase[3].Current[15]
EP2_PMM1_Phase3_Current16 | REAL | IOD_EP2_TCP | 4401 | 44401 | PMM[1].Phase[3].Current[16]
EP2_PMM1_Phase3_Current17 | REAL | IOD_EP2_TCP | 4403 | 44403 | PMM[1].Phase[3].Current[17]
EP2_PMM1_Phase3_Current18 | REAL | IOD_EP2_TCP | 4405 | 44405 | PMM[1].Phase[3].Current[18]
EP2_PMM1_Phase3_Current19 | REAL | IOD_EP2_TCP | 4407 | 44407 | PMM[1].Phase[3].Current[19]
EP2_PMM1_Phase3_Current1 | REAL | IOD_EP2_TCP | 4409 | 44409 | PMM[1].Phase[3].Current[1]
EP2_PMM1_Phase3_Current20 | REAL | IOD_EP2_TCP | 4411 | 44411 | PMM[1].Phase[3].Current[20]
EP2_PMM1_Phase3_Current21 | REAL | IOD_EP2_TCP | 4413 | 44413 | PMM[1].Phase[3].Current[21]
EP2_PMM1_Phase3_Current22 | REAL | IOD_EP2_TCP | 4415 | 44415 | PMM[1].Phase[3].Current[22]
EP2_PMM1_Phase3_Current23 | REAL | IOD_EP2_TCP | 4417 | 44417 | PMM[1].Phase[3].Current[23]
EP2_PMM1_Phase3_Current24 | REAL | IOD_EP2_TCP | 4419 | 44419 | PMM[1].Phase[3].Current[24]
EP2_PMM1_Phase3_Current25 | REAL | IOD_EP2_TCP | 4421 | 44421 | PMM[1].Phase[3].Current[25]
EP2_PMM1_Phase3_Current26 | REAL | IOD_EP2_TCP | 4423 | 44423 | PMM[1].Phase[3].Current[26]
EP2_PMM1_Phase3_Current27 | REAL | IOD_EP2_TCP | 4425 | 44425 | PMM[1].Phase[3].Current[27]
EP2_PMM1_Phase3_Current28 | REAL | IOD_EP2_TCP | 4427 | 44427 | PMM[1].Phase[3].Current[28]
EP2_PMM1_Phase3_Current29 | REAL | IOD_EP2_TCP | 4429 | 44429 | PMM[1].Phase[3].Current[29]
EP2_PMM1_Phase3_Current2 | REAL | IOD_EP2_TCP | 4431 | 44431 | PMM[1].Phase[3].Current[2]
EP2_PMM1_Phase3_Current30 | REAL | IOD_EP2_TCP | 4433 | 44433 | PMM[1].Phase[3].Current[30]
EP2_PMM1_Phase3_Current31 | REAL | IOD_EP2_TCP | 4435 | 44435 | PMM[1].Phase[3].Current[31]
EP2_PMM1_Phase3_Current32 | REAL | IOD_EP2_TCP | 4437 | 44437 | PMM[1].Phase[3].Current[32]
EP2_PMM1_Phase3_Current33 | REAL | IOD_EP2_TCP | 4439 | 44439 | PMM[1].Phase[3].Current[33]
EP2_PMM1_Phase3_Current34 | REAL | IOD_EP2_TCP | 4441 | 44441 | PMM[1].Phase[3].Current[34]
EP2_PMM1_Phase3_Current35 | REAL | IOD_EP2_TCP | 4443 | 44443 | PMM[1].Phase[3].Current[35]
EP2_PMM1_Phase3_Current36 | REAL | IOD_EP2_TCP | 4445 | 44445 | PMM[1].Phase[3].Current[36]
EP2_PMM1_Phase3_Current37 | REAL | IOD_EP2_TCP | 4447 | 44447 | PMM[1].Phase[3].Current[37]
EP2_PMM1_Phase3_Current38 | REAL | IOD_EP2_TCP | 4449 | 44449 | PMM[1].Phase[3].Current[38]
EP2_PMM1_Phase3_Current39 | REAL | IOD_EP2_TCP | 4451 | 44451 | PMM[1].Phase[3].Current[39]
EP2_PMM1_Phase3_Current3 | REAL | IOD_EP2_TCP | 4453 | 44453 | PMM[1].Phase[3].Current[3]
EP2_PMM1_Phase3_Current40 | REAL | IOD_EP2_TCP | 4455 | 44455 | PMM[1].Phase[3].Current[40]
EP2_PMM1_Phase3_Current41 | REAL | IOD_EP2_TCP | 4457 | 44457 | PMM[1].Phase[3].Current[41]
EP2_PMM1_Phase3_Current42 | REAL | IOD_EP2_TCP | 4459 | 44459 | PMM[1].Phase[3].Current[42]
EP2_PMM1_Phase3_Current4 | REAL | IOD_EP2_TCP | 4461 | 44461 | PMM[1].Phase[3].Current[4]
EP2_PMM1_Phase3_Current5 | REAL | IOD_EP2_TCP | 4463 | 44463 | PMM[1].Phase[3].Current[5]
EP2_PMM1_Phase3_Current6 | REAL | IOD_EP2_TCP | 4465 | 44465 | PMM[1].Phase[3].Current[6]
EP2_PMM1_Phase3_Current7 | REAL | IOD_EP2_TCP | 4467 | 44467 | PMM[1].Phase[3].Current[7]
EP2_PMM1_Phase3_Current8 | REAL | IOD_EP2_TCP | 4469 | 44469 | PMM[1].Phase[3].Current[8]
EP2_PMM1_Phase3_Current9 | REAL | IOD_EP2_TCP | 4471 | 44471 | PMM[1].Phase[3].Current[9]
EP2_PMM1_PowerFactorPhaseA | REAL | IOD_EP2_TCP | 4473 | 44473 | PMM[1].PowerFactorPhaseA
EP2_PMM1_PowerFactorPhaseB | REAL | IOD_EP2_TCP | 4475 | 44475 | PMM[1].PowerFactorPhaseB
EP2_PMM1_PowerFactorPhaseC | REAL | IOD_EP2_TCP | 4477 | 44477 | PMM[1].PowerFactorPhaseC
EP2_PMM1_TotalActivePower_kW | REAL | IOD_EP2_TCP | 4479 | 44479 | PMM[1].TotalActivePower_kW
EP2_PMM1_TotalAparentPower_kVA | REAL | IOD_EP2_TCP | 4481 | 44481 | PMM[1].TotalAparentPower_kVA
EP2_PMM1_TotalPowerFactor | REAL | IOD_EP2_TCP | 4483 | 44483 | PMM[1].TotalPowerFactor
EP2_PMM1_TotalReactivePower_kVAR | REAL | IOD_EP2_TCP | 4485 | 44485 | PMM[1].TotalReactivePower_kVAR
EP2_PMM1_VoltageBetweenPhaseAB_V | REAL | IOD_EP2_TCP | 4487 | 44487 | PMM[1].VoltageBetweenPhaseAB_V
EP2_PMM1_VoltageBetweenPhaseAN_V | REAL | IOD_EP2_TCP | 4489 | 44489 | PMM[1].VoltageBetweenPhaseAN_V
EP2_PMM1_VoltageBetweenPhaseBC_V | REAL | IOD_EP2_TCP | 4491 | 44491 | PMM[1].VoltageBetweenPhaseBC_V
EP2_PMM1_VoltageBetweenPhaseBN_V | REAL | IOD_EP2_TCP | 4493 | 44493 | PMM[1].VoltageBetweenPhaseBN_V
EP2_PMM1_VoltageBetweenPhaseCA_V | REAL | IOD_EP2_TCP | 4495 | 44495 | PMM[1].VoltageBetweenPhaseCA_V
EP2_PMM1_VoltageBetweenPhaseCN_V | REAL | IOD_EP2_TCP | 4497 | 44497 | PMM[1].VoltageBetweenPhaseCN_V
EP2_PMM2_ActivePowerPhaseA_kW | REAL | IOD_EP2_TCP | 4499 | 44499 | PMM[2].ActivePowerPhaseA_kW
EP2_PMM2_ActivePowerPhaseB_kW | REAL | IOD_EP2_TCP | 4501 | 44501 | PMM[2].ActivePowerPhaseB_kW
EP2_PMM2_ActivePowerPhaseC_kW | REAL | IOD_EP2_TCP | 4503 | 44503 | PMM[2].ActivePowerPhaseC_kW
EP2_PMM2_AverageCurrent_A | REAL | IOD_EP2_TCP | 4505 | 44505 | PMM[2].AverageCurrent_A
EP2_PMM2_AveragePhaseToNeutral_V | REAL | IOD_EP2_TCP | 4507 | 44507 | PMM[2].AveragePhaseToNeutral_V
EP2_PMM2_AveragePhaseToPhase_V | REAL | IOD_EP2_TCP | 4509 | 44509 | PMM[2].AveragePhaseToPhase_V
EP2_PMM2_CurrentInPhaseA_A | REAL | IOD_EP2_TCP | 4511 | 44511 | PMM[2].CurrentInPhaseA_A
EP2_PMM2_CurrentInPhaseB_A | REAL | IOD_EP2_TCP | 4513 | 44513 | PMM[2].CurrentInPhaseB_A
EP2_PMM2_CurrentInPhaseC_A | REAL | IOD_EP2_TCP | 4515 | 44515 | PMM[2].CurrentInPhaseC_A
EP2_PMM2_EnergyConsumed_kWh | REAL | IOD_EP2_TCP | 4517 | 44517 | PMM[2].EnergyConsumed_kWh
EP2_PMM2_Frequency_Hz | REAL | IOD_EP2_TCP | 4519 | 44519 | PMM[2].Frequency_Hz
EP2_PMM2_NeutralCurrent_A | REAL | IOD_EP2_TCP | 4521 | 44521 | PMM[2].NeutralCurrent_A
EP2_PMM2_Phase1_Current10 | REAL | IOD_EP2_TCP | 4523 | 44523 | PMM[2].Phase[1].Current[10]
EP2_PMM2_Phase1_Current11 | REAL | IOD_EP2_TCP | 4525 | 44525 | PMM[2].Phase[1].Current[11]
EP2_PMM2_Phase1_Current12 | REAL | IOD_EP2_TCP | 4527 | 44527 | PMM[2].Phase[1].Current[12]
EP2_PMM2_Phase1_Current13 | REAL | IOD_EP2_TCP | 4529 | 44529 | PMM[2].Phase[1].Current[13]
EP2_PMM2_Phase1_Current14 | REAL | IOD_EP2_TCP | 4531 | 44531 | PMM[2].Phase[1].Current[14]
EP2_PMM2_Phase1_Current15 | REAL | IOD_EP2_TCP | 4533 | 44533 | PMM[2].Phase[1].Current[15]
EP2_PMM2_Phase1_Current16 | REAL | IOD_EP2_TCP | 4535 | 44535 | PMM[2].Phase[1].Current[16]
EP2_PMM2_Phase1_Current17 | REAL | IOD_EP2_TCP | 4537 | 44537 | PMM[2].Phase[1].Current[17]
EP2_PMM2_Phase1_Current18 | REAL | IOD_EP2_TCP | 4539 | 44539 | PMM[2].Phase[1].Current[18]
EP2_PMM2_Phase1_Current19 | REAL | IOD_EP2_TCP | 4541 | 44541 | PMM[2].Phase[1].Current[19]
EP2_PMM2_Phase1_Current1 | REAL | IOD_EP2_TCP | 4543 | 44543 | PMM[2].Phase[1].Current[1]
EP2_PMM2_Phase1_Current20 | REAL | IOD_EP2_TCP | 4545 | 44545 | PMM[2].Phase[1].Current[20]
EP2_PMM2_Phase1_Current21 | REAL | IOD_EP2_TCP | 4547 | 44547 | PMM[2].Phase[1].Current[21]
EP2_PMM2_Phase1_Current22 | REAL | IOD_EP2_TCP | 4549 | 44549 | PMM[2].Phase[1].Current[22]
EP2_PMM2_Phase1_Current23 | REAL | IOD_EP2_TCP | 4551 | 44551 | PMM[2].Phase[1].Current[23]
EP2_PMM2_Phase1_Current24 | REAL | IOD_EP2_TCP | 4553 | 44553 | PMM[2].Phase[1].Current[24]
EP2_PMM2_Phase1_Current25 | REAL | IOD_EP2_TCP | 4555 | 44555 | PMM[2].Phase[1].Current[25]
EP2_PMM2_Phase1_Current26 | REAL | IOD_EP2_TCP | 4557 | 44557 | PMM[2].Phase[1].Current[26]
EP2_PMM2_Phase1_Current27 | REAL | IOD_EP2_TCP | 4559 | 44559 | PMM[2].Phase[1].Current[27]
EP2_PMM2_Phase1_Current28 | REAL | IOD_EP2_TCP | 4561 | 44561 | PMM[2].Phase[1].Current[28]
EP2_PMM2_Phase1_Current29 | REAL | IOD_EP2_TCP | 4563 | 44563 | PMM[2].Phase[1].Current[29]
EP2_PMM2_Phase1_Current2 | REAL | IOD_EP2_TCP | 4565 | 44565 | PMM[2].Phase[1].Current[2]
EP2_PMM2_Phase1_Current30 | REAL | IOD_EP2_TCP | 4567 | 44567 | PMM[2].Phase[1].Current[30]
EP2_PMM2_Phase1_Current31 | REAL | IOD_EP2_TCP | 4569 | 44569 | PMM[2].Phase[1].Current[31]
EP2_PMM2_Phase1_Current32 | REAL | IOD_EP2_TCP | 4571 | 44571 | PMM[2].Phase[1].Current[32]
EP2_PMM2_Phase1_Current33 | REAL | IOD_EP2_TCP | 4573 | 44573 | PMM[2].Phase[1].Current[33]
EP2_PMM2_Phase1_Current34 | REAL | IOD_EP2_TCP | 4575 | 44575 | PMM[2].Phase[1].Current[34]
EP2_PMM2_Phase1_Current35 | REAL | IOD_EP2_TCP | 4577 | 44577 | PMM[2].Phase[1].Current[35]
EP2_PMM2_Phase1_Current36 | REAL | IOD_EP2_TCP | 4579 | 44579 | PMM[2].Phase[1].Current[36]
EP2_PMM2_Phase1_Current37 | REAL | IOD_EP2_TCP | 4581 | 44581 | PMM[2].Phase[1].Current[37]
EP2_PMM2_Phase1_Current38 | REAL | IOD_EP2_TCP | 4583 | 44583 | PMM[2].Phase[1].Current[38]
EP2_PMM2_Phase1_Current39 | REAL | IOD_EP2_TCP | 4585 | 44585 | PMM[2].Phase[1].Current[39]
EP2_PMM2_Phase1_Current3 | REAL | IOD_EP2_TCP | 4587 | 44587 | PMM[2].Phase[1].Current[3]
EP2_PMM2_Phase1_Current40 | REAL | IOD_EP2_TCP | 4589 | 44589 | PMM[2].Phase[1].Current[40]
EP2_PMM2_Phase1_Current41 | REAL | IOD_EP2_TCP | 4591 | 44591 | PMM[2].Phase[1].Current[41]
EP2_PMM2_Phase1_Current42 | REAL | IOD_EP2_TCP | 4593 | 44593 | PMM[2].Phase[1].Current[42]
EP2_PMM2_Phase1_Current4 | REAL | IOD_EP2_TCP | 4595 | 44595 | PMM[2].Phase[1].Current[4]
EP2_PMM2_Phase1_Current5 | REAL | IOD_EP2_TCP | 4597 | 44597 | PMM[2].Phase[1].Current[5]
EP2_PMM2_Phase1_Current6 | REAL | IOD_EP2_TCP | 4599 | 44599 | PMM[2].Phase[1].Current[6]
EP2_PMM2_Phase1_Current7 | REAL | IOD_EP2_TCP | 4601 | 44601 | PMM[2].Phase[1].Current[7]
EP2_PMM2_Phase1_Current8 | REAL | IOD_EP2_TCP | 4603 | 44603 | PMM[2].Phase[1].Current[8]
EP2_PMM2_Phase1_Current9 | REAL | IOD_EP2_TCP | 4605 | 44605 | PMM[2].Phase[1].Current[9]
EP2_PMM2_Phase2_Current10 | REAL | IOD_EP2_TCP | 4607 | 44607 | PMM[2].Phase[2].Current[10]
EP2_PMM2_Phase2_Current11 | REAL | IOD_EP2_TCP | 4609 | 44609 | PMM[2].Phase[2].Current[11]
EP2_PMM2_Phase2_Current12 | REAL | IOD_EP2_TCP | 4611 | 44611 | PMM[2].Phase[2].Current[12]
EP2_PMM2_Phase2_Current13 | REAL | IOD_EP2_TCP | 4613 | 44613 | PMM[2].Phase[2].Current[13]
EP2_PMM2_Phase2_Current14 | REAL | IOD_EP2_TCP | 4615 | 44615 | PMM[2].Phase[2].Current[14]
EP2_PMM2_Phase2_Current15 | REAL | IOD_EP2_TCP | 4617 | 44617 | PMM[2].Phase[2].Current[15]
EP2_PMM2_Phase2_Current16 | REAL | IOD_EP2_TCP | 4619 | 44619 | PMM[2].Phase[2].Current[16]
EP2_PMM2_Phase2_Current17 | REAL | IOD_EP2_TCP | 4621 | 44621 | PMM[2].Phase[2].Current[17]
EP2_PMM2_Phase2_Current18 | REAL | IOD_EP2_TCP | 4623 | 44623 | PMM[2].Phase[2].Current[18]
EP2_PMM2_Phase2_Current19 | REAL | IOD_EP2_TCP | 4625 | 44625 | PMM[2].Phase[2].Current[19]
EP2_PMM2_Phase2_Current1 | REAL | IOD_EP2_TCP | 4627 | 44627 | PMM[2].Phase[2].Current[1]
EP2_PMM2_Phase2_Current20 | REAL | IOD_EP2_TCP | 4629 | 44629 | PMM[2].Phase[2].Current[20]
EP2_PMM2_Phase2_Current21 | REAL | IOD_EP2_TCP | 4631 | 44631 | PMM[2].Phase[2].Current[21]
EP2_PMM2_Phase2_Current22 | REAL | IOD_EP2_TCP | 4633 | 44633 | PMM[2].Phase[2].Current[22]
EP2_PMM2_Phase2_Current23 | REAL | IOD_EP2_TCP | 4635 | 44635 | PMM[2].Phase[2].Current[23]
EP2_PMM2_Phase2_Current24 | REAL | IOD_EP2_TCP | 4637 | 44637 | PMM[2].Phase[2].Current[24]
EP2_PMM2_Phase2_Current25 | REAL | IOD_EP2_TCP | 4639 | 44639 | PMM[2].Phase[2].Current[25]
EP2_PMM2_Phase2_Current26 | REAL | IOD_EP2_TCP | 4641 | 44641 | PMM[2].Phase[2].Current[26]
EP2_PMM2_Phase2_Current27 | REAL | IOD_EP2_TCP | 4643 | 44643 | PMM[2].Phase[2].Current[27]
EP2_PMM2_Phase2_Current28 | REAL | IOD_EP2_TCP | 4645 | 44645 | PMM[2].Phase[2].Current[28]
EP2_PMM2_Phase2_Current29 | REAL | IOD_EP2_TCP | 4647 | 44647 | PMM[2].Phase[2].Current[29]
EP2_PMM2_Phase2_Current2 | REAL | IOD_EP2_TCP | 4649 | 44649 | PMM[2].Phase[2].Current[2]
EP2_PMM2_Phase2_Current30 | REAL | IOD_EP2_TCP | 4651 | 44651 | PMM[2].Phase[2].Current[30]
EP2_PMM2_Phase2_Current31 | REAL | IOD_EP2_TCP | 4653 | 44653 | PMM[2].Phase[2].Current[31]
EP2_PMM2_Phase2_Current32 | REAL | IOD_EP2_TCP | 4655 | 44655 | PMM[2].Phase[2].Current[32]
EP2_PMM2_Phase2_Current33 | REAL | IOD_EP2_TCP | 4657 | 44657 | PMM[2].Phase[2].Current[33]
EP2_PMM2_Phase2_Current34 | REAL | IOD_EP2_TCP | 4659 | 44659 | PMM[2].Phase[2].Current[34]
EP2_PMM2_Phase2_Current35 | REAL | IOD_EP2_TCP | 4661 | 44661 | PMM[2].Phase[2].Current[35]
EP2_PMM2_Phase2_Current36 | REAL | IOD_EP2_TCP | 4663 | 44663 | PMM[2].Phase[2].Current[36]
EP2_PMM2_Phase2_Current37 | REAL | IOD_EP2_TCP | 4665 | 44665 | PMM[2].Phase[2].Current[37]
EP2_PMM2_Phase2_Current38 | REAL | IOD_EP2_TCP | 4667 | 44667 | PMM[2].Phase[2].Current[38]
EP2_PMM2_Phase2_Current39 | REAL | IOD_EP2_TCP | 4669 | 44669 | PMM[2].Phase[2].Current[39]
EP2_PMM2_Phase2_Current3 | REAL | IOD_EP2_TCP | 4671 | 44671 | PMM[2].Phase[2].Current[3]
EP2_PMM2_Phase2_Current40 | REAL | IOD_EP2_TCP | 4673 | 44673 | PMM[2].Phase[2].Current[40]
EP2_PMM2_Phase2_Current41 | REAL | IOD_EP2_TCP | 4675 | 44675 | PMM[2].Phase[2].Current[41]
EP2_PMM2_Phase2_Current42 | REAL | IOD_EP2_TCP | 4677 | 44677 | PMM[2].Phase[2].Current[42]
EP2_PMM2_Phase2_Current4 | REAL | IOD_EP2_TCP | 4679 | 44679 | PMM[2].Phase[2].Current[4]
EP2_PMM2_Phase2_Current5 | REAL | IOD_EP2_TCP | 4681 | 44681 | PMM[2].Phase[2].Current[5]
EP2_PMM2_Phase2_Current6 | REAL | IOD_EP2_TCP | 4683 | 44683 | PMM[2].Phase[2].Current[6]
EP2_PMM2_Phase2_Current7 | REAL | IOD_EP2_TCP | 4685 | 44685 | PMM[2].Phase[2].Current[7]
EP2_PMM2_Phase2_Current8 | REAL | IOD_EP2_TCP | 4687 | 44687 | PMM[2].Phase[2].Current[8]
EP2_PMM2_Phase2_Current9 | REAL | IOD_EP2_TCP | 4689 | 44689 | PMM[2].Phase[2].Current[9]
EP2_PMM2_Phase3_Current10 | REAL | IOD_EP2_TCP | 4691 | 44691 | PMM[2].Phase[3].Current[10]
EP2_PMM2_Phase3_Current11 | REAL | IOD_EP2_TCP | 4693 | 44693 | PMM[2].Phase[3].Current[11]
EP2_PMM2_Phase3_Current12 | REAL | IOD_EP2_TCP | 4695 | 44695 | PMM[2].Phase[3].Current[12]
EP2_PMM2_Phase3_Current13 | REAL | IOD_EP2_TCP | 4697 | 44697 | PMM[2].Phase[3].Current[13]
EP2_PMM2_Phase3_Current14 | REAL | IOD_EP2_TCP | 4699 | 44699 | PMM[2].Phase[3].Current[14]
EP2_PMM2_Phase3_Current15 | REAL | IOD_EP2_TCP | 4701 | 44701 | PMM[2].Phase[3].Current[15]
EP2_PMM2_Phase3_Current16 | REAL | IOD_EP2_TCP | 4703 | 44703 | PMM[2].Phase[3].Current[16]
EP2_PMM2_Phase3_Current17 | REAL | IOD_EP2_TCP | 4705 | 44705 | PMM[2].Phase[3].Current[17]
EP2_PMM2_Phase3_Current18 | REAL | IOD_EP2_TCP | 4707 | 44707 | PMM[2].Phase[3].Current[18]
EP2_PMM2_Phase3_Current19 | REAL | IOD_EP2_TCP | 4709 | 44709 | PMM[2].Phase[3].Current[19]
EP2_PMM2_Phase3_Current1 | REAL | IOD_EP2_TCP | 4711 | 44711 | PMM[2].Phase[3].Current[1]
EP2_PMM2_Phase3_Current20 | REAL | IOD_EP2_TCP | 4713 | 44713 | PMM[2].Phase[3].Current[20]
EP2_PMM2_Phase3_Current21 | REAL | IOD_EP2_TCP | 4715 | 44715 | PMM[2].Phase[3].Current[21]
EP2_PMM2_Phase3_Current22 | REAL | IOD_EP2_TCP | 4717 | 44717 | PMM[2].Phase[3].Current[22]
EP2_PMM2_Phase3_Current23 | REAL | IOD_EP2_TCP | 4719 | 44719 | PMM[2].Phase[3].Current[23]
EP2_PMM2_Phase3_Current24 | REAL | IOD_EP2_TCP | 4721 | 44721 | PMM[2].Phase[3].Current[24]
EP2_PMM2_Phase3_Current25 | REAL | IOD_EP2_TCP | 4723 | 44723 | PMM[2].Phase[3].Current[25]
EP2_PMM2_Phase3_Current26 | REAL | IOD_EP2_TCP | 4725 | 44725 | PMM[2].Phase[3].Current[26]
EP2_PMM2_Phase3_Current27 | REAL | IOD_EP2_TCP | 4727 | 44727 | PMM[2].Phase[3].Current[27]
EP2_PMM2_Phase3_Current28 | REAL | IOD_EP2_TCP | 4729 | 44729 | PMM[2].Phase[3].Current[28]
EP2_PMM2_Phase3_Current29 | REAL | IOD_EP2_TCP | 4731 | 44731 | PMM[2].Phase[3].Current[29]
EP2_PMM2_Phase3_Current2 | REAL | IOD_EP2_TCP | 4733 | 44733 | PMM[2].Phase[3].Current[2]
EP2_PMM2_Phase3_Current30 | REAL | IOD_EP2_TCP | 4735 | 44735 | PMM[2].Phase[3].Current[30]
EP2_PMM2_Phase3_Current31 | REAL | IOD_EP2_TCP | 4737 | 44737 | PMM[2].Phase[3].Current[31]
EP2_PMM2_Phase3_Current32 | REAL | IOD_EP2_TCP | 4739 | 44739 | PMM[2].Phase[3].Current[32]
EP2_PMM2_Phase3_Current33 | REAL | IOD_EP2_TCP | 4741 | 44741 | PMM[2].Phase[3].Current[33]
EP2_PMM2_Phase3_Current34 | REAL | IOD_EP2_TCP | 4743 | 44743 | PMM[2].Phase[3].Current[34]
EP2_PMM2_Phase3_Current35 | REAL | IOD_EP2_TCP | 4745 | 44745 | PMM[2].Phase[3].Current[35]
EP2_PMM2_Phase3_Current36 | REAL | IOD_EP2_TCP | 4747 | 44747 | PMM[2].Phase[3].Current[36]
EP2_PMM2_Phase3_Current37 | REAL | IOD_EP2_TCP | 4749 | 44749 | PMM[2].Phase[3].Current[37]
EP2_PMM2_Phase3_Current38 | REAL | IOD_EP2_TCP | 4751 | 44751 | PMM[2].Phase[3].Current[38]
EP2_PMM2_Phase3_Current39 | REAL | IOD_EP2_TCP | 4753 | 44753 | PMM[2].Phase[3].Current[39]
EP2_PMM2_Phase3_Current3 | REAL | IOD_EP2_TCP | 4755 | 44755 | PMM[2].Phase[3].Current[3]
EP2_PMM2_Phase3_Current40 | REAL | IOD_EP2_TCP | 4757 | 44757 | PMM[2].Phase[3].Current[40]
EP2_PMM2_Phase3_Current41 | REAL | IOD_EP2_TCP | 4759 | 44759 | PMM[2].Phase[3].Current[41]
EP2_PMM2_Phase3_Current42 | REAL | IOD_EP2_TCP | 4761 | 44761 | PMM[2].Phase[3].Current[42]
EP2_PMM2_Phase3_Current4 | REAL | IOD_EP2_TCP | 4763 | 44763 | PMM[2].Phase[3].Current[4]
EP2_PMM2_Phase3_Current5 | REAL | IOD_EP2_TCP | 4765 | 44765 | PMM[2].Phase[3].Current[5]
EP2_PMM2_Phase3_Current6 | REAL | IOD_EP2_TCP | 4767 | 44767 | PMM[2].Phase[3].Current[6]
EP2_PMM2_Phase3_Current7 | REAL | IOD_EP2_TCP | 4769 | 44769 | PMM[2].Phase[3].Current[7]
EP2_PMM2_Phase3_Current8 | REAL | IOD_EP2_TCP | 4771 | 44771 | PMM[2].Phase[3].Current[8]
EP2_PMM2_Phase3_Current9 | REAL | IOD_EP2_TCP | 4773 | 44773 | PMM[2].Phase[3].Current[9]
EP2_PMM2_PowerFactorPhaseA | REAL | IOD_EP2_TCP | 4775 | 44775 | PMM[2].PowerFactorPhaseA
EP2_PMM2_PowerFactorPhaseB | REAL | IOD_EP2_TCP | 4777 | 44777 | PMM[2].PowerFactorPhaseB
EP2_PMM2_PowerFactorPhaseC | REAL | IOD_EP2_TCP | 4779 | 44779 | PMM[2].PowerFactorPhaseC
EP2_PMM2_TotalActivePower_kW | REAL | IOD_EP2_TCP | 4781 | 44781 | PMM[2].TotalActivePower_kW
EP2_PMM2_TotalAparentPower_kVA | REAL | IOD_EP2_TCP | 4783 | 44783 | PMM[2].TotalAparentPower_kVA
EP2_PMM2_TotalPowerFactor | REAL | IOD_EP2_TCP | 4785 | 44785 | PMM[2].TotalPowerFactor
EP2_PMM2_TotalReactivePower_kVAR | REAL | IOD_EP2_TCP | 4787 | 44787 | PMM[2].TotalReactivePower_kVAR
EP2_PMM2_VoltageBetweenPhaseAB_V | REAL | IOD_EP2_TCP | 4789 | 44789 | PMM[2].VoltageBetweenPhaseAB_V
EP2_PMM2_VoltageBetweenPhaseAN_V | REAL | IOD_EP2_TCP | 4791 | 44791 | PMM[2].VoltageBetweenPhaseAN_V
EP2_PMM2_VoltageBetweenPhaseBC_V | REAL | IOD_EP2_TCP | 4793 | 44793 | PMM[2].VoltageBetweenPhaseBC_V
EP2_PMM2_VoltageBetweenPhaseBN_V | REAL | IOD_EP2_TCP | 4795 | 44795 | PMM[2].VoltageBetweenPhaseBN_V
EP2_PMM2_VoltageBetweenPhaseCA_V | REAL | IOD_EP2_TCP | 4797 | 44797 | PMM[2].VoltageBetweenPhaseCA_V
EP2_PMM2_VoltageBetweenPhaseCN_V | REAL | IOD_EP2_TCP | 4799 | 44799 | PMM[2].VoltageBetweenPhaseCN_V
EP2_PMM3_ActivePowerPhaseA_kW | REAL | IOD_EP2_TCP | 4801 | 44801 | PMM[3].ActivePowerPhaseA_kW
EP2_PMM3_ActivePowerPhaseB_kW | REAL | IOD_EP2_TCP | 4803 | 44803 | PMM[3].ActivePowerPhaseB_kW
EP2_PMM3_ActivePowerPhaseC_kW | REAL | IOD_EP2_TCP | 4805 | 44805 | PMM[3].ActivePowerPhaseC_kW
EP2_PMM3_AverageCurrent_A | REAL | IOD_EP2_TCP | 4807 | 44807 | PMM[3].AverageCurrent_A
EP2_PMM3_AveragePhaseToNeutral_V | REAL | IOD_EP2_TCP | 4809 | 44809 | PMM[3].AveragePhaseToNeutral_V
EP2_PMM3_AveragePhaseToPhase_V | REAL | IOD_EP2_TCP | 4811 | 44811 | PMM[3].AveragePhaseToPhase_V
EP2_PMM3_CurrentInPhaseA_A | REAL | IOD_EP2_TCP | 4813 | 44813 | PMM[3].CurrentInPhaseA_A
EP2_PMM3_CurrentInPhaseB_A | REAL | IOD_EP2_TCP | 4815 | 44815 | PMM[3].CurrentInPhaseB_A
EP2_PMM3_CurrentInPhaseC_A | REAL | IOD_EP2_TCP | 4817 | 44817 | PMM[3].CurrentInPhaseC_A
EP2_PMM3_EnergyConsumed_kWh | REAL | IOD_EP2_TCP | 4819 | 44819 | PMM[3].EnergyConsumed_kWh
EP2_PMM3_Frequency_Hz | REAL | IOD_EP2_TCP | 4821 | 44821 | PMM[3].Frequency_Hz
EP2_PMM3_NeutralCurrent_A | REAL | IOD_EP2_TCP | 4823 | 44823 | PMM[3].NeutralCurrent_A
EP2_PMM3_Phase1_Current10 | REAL | IOD_EP2_TCP | 4825 | 44825 | PMM[3].Phase[1].Current[10]
EP2_PMM3_Phase1_Current11 | REAL | IOD_EP2_TCP | 4827 | 44827 | PMM[3].Phase[1].Current[11]
EP2_PMM3_Phase1_Current12 | REAL | IOD_EP2_TCP | 4829 | 44829 | PMM[3].Phase[1].Current[12]
EP2_PMM3_Phase1_Current13 | REAL | IOD_EP2_TCP | 4831 | 44831 | PMM[3].Phase[1].Current[13]
EP2_PMM3_Phase1_Current14 | REAL | IOD_EP2_TCP | 4833 | 44833 | PMM[3].Phase[1].Current[14]
EP2_PMM3_Phase1_Current15 | REAL | IOD_EP2_TCP | 4835 | 44835 | PMM[3].Phase[1].Current[15]
EP2_PMM3_Phase1_Current16 | REAL | IOD_EP2_TCP | 4837 | 44837 | PMM[3].Phase[1].Current[16]
EP2_PMM3_Phase1_Current17 | REAL | IOD_EP2_TCP | 4839 | 44839 | PMM[3].Phase[1].Current[17]
EP2_PMM3_Phase1_Current18 | REAL | IOD_EP2_TCP | 4841 | 44841 | PMM[3].Phase[1].Current[18]
EP2_PMM3_Phase1_Current19 | REAL | IOD_EP2_TCP | 4843 | 44843 | PMM[3].Phase[1].Current[19]
EP2_PMM3_Phase1_Current1 | REAL | IOD_EP2_TCP | 4845 | 44845 | PMM[3].Phase[1].Current[1]
EP2_PMM3_Phase1_Current20 | REAL | IOD_EP2_TCP | 4847 | 44847 | PMM[3].Phase[1].Current[20]
EP2_PMM3_Phase1_Current21 | REAL | IOD_EP2_TCP | 4849 | 44849 | PMM[3].Phase[1].Current[21]
EP2_PMM3_Phase1_Current22 | REAL | IOD_EP2_TCP | 4851 | 44851 | PMM[3].Phase[1].Current[22]
EP2_PMM3_Phase1_Current23 | REAL | IOD_EP2_TCP | 4853 | 44853 | PMM[3].Phase[1].Current[23]
EP2_PMM3_Phase1_Current24 | REAL | IOD_EP2_TCP | 4855 | 44855 | PMM[3].Phase[1].Current[24]
EP2_PMM3_Phase1_Current25 | REAL | IOD_EP2_TCP | 4857 | 44857 | PMM[3].Phase[1].Current[25]
EP2_PMM3_Phase1_Current26 | REAL | IOD_EP2_TCP | 4859 | 44859 | PMM[3].Phase[1].Current[26]
EP2_PMM3_Phase1_Current27 | REAL | IOD_EP2_TCP | 4861 | 44861 | PMM[3].Phase[1].Current[27]
EP2_PMM3_Phase1_Current28 | REAL | IOD_EP2_TCP | 4863 | 44863 | PMM[3].Phase[1].Current[28]
EP2_PMM3_Phase1_Current29 | REAL | IOD_EP2_TCP | 4865 | 44865 | PMM[3].Phase[1].Current[29]
EP2_PMM3_Phase1_Current2 | REAL | IOD_EP2_TCP | 4867 | 44867 | PMM[3].Phase[1].Current[2]
EP2_PMM3_Phase1_Current30 | REAL | IOD_EP2_TCP | 4869 | 44869 | PMM[3].Phase[1].Current[30]
EP2_PMM3_Phase1_Current31 | REAL | IOD_EP2_TCP | 4871 | 44871 | PMM[3].Phase[1].Current[31]
EP2_PMM3_Phase1_Current32 | REAL | IOD_EP2_TCP | 4873 | 44873 | PMM[3].Phase[1].Current[32]
EP2_PMM3_Phase1_Current33 | REAL | IOD_EP2_TCP | 4875 | 44875 | PMM[3].Phase[1].Current[33]
EP2_PMM3_Phase1_Current34 | REAL | IOD_EP2_TCP | 4877 | 44877 | PMM[3].Phase[1].Current[34]
EP2_PMM3_Phase1_Current35 | REAL | IOD_EP2_TCP | 4879 | 44879 | PMM[3].Phase[1].Current[35]
EP2_PMM3_Phase1_Current36 | REAL | IOD_EP2_TCP | 4881 | 44881 | PMM[3].Phase[1].Current[36]
EP2_PMM3_Phase1_Current37 | REAL | IOD_EP2_TCP | 4883 | 44883 | PMM[3].Phase[1].Current[37]
EP2_PMM3_Phase1_Current38 | REAL | IOD_EP2_TCP | 4885 | 44885 | PMM[3].Phase[1].Current[38]
EP2_PMM3_Phase1_Current39 | REAL | IOD_EP2_TCP | 4887 | 44887 | PMM[3].Phase[1].Current[39]
EP2_PMM3_Phase1_Current3 | REAL | IOD_EP2_TCP | 4889 | 44889 | PMM[3].Phase[1].Current[3]
EP2_PMM3_Phase1_Current40 | REAL | IOD_EP2_TCP | 4891 | 44891 | PMM[3].Phase[1].Current[40]
EP2_PMM3_Phase1_Current41 | REAL | IOD_EP2_TCP | 4893 | 44893 | PMM[3].Phase[1].Current[41]
EP2_PMM3_Phase1_Current42 | REAL | IOD_EP2_TCP | 4895 | 44895 | PMM[3].Phase[1].Current[42]
EP2_PMM3_Phase1_Current4 | REAL | IOD_EP2_TCP | 4897 | 44897 | PMM[3].Phase[1].Current[4]
EP2_PMM3_Phase1_Current5 | REAL | IOD_EP2_TCP | 4899 | 44899 | PMM[3].Phase[1].Current[5]
EP2_PMM3_Phase1_Current6 | REAL | IOD_EP2_TCP | 4901 | 44901 | PMM[3].Phase[1].Current[6]
EP2_PMM3_Phase1_Current7 | REAL | IOD_EP2_TCP | 4903 | 44903 | PMM[3].Phase[1].Current[7]
EP2_PMM3_Phase1_Current8 | REAL | IOD_EP2_TCP | 4905 | 44905 | PMM[3].Phase[1].Current[8]
EP2_PMM3_Phase1_Current9 | REAL | IOD_EP2_TCP | 4907 | 44907 | PMM[3].Phase[1].Current[9]
EP2_PMM3_Phase2_Current10 | REAL | IOD_EP2_TCP | 4909 | 44909 | PMM[3].Phase[2].Current[10]
EP2_PMM3_Phase2_Current11 | REAL | IOD_EP2_TCP | 4911 | 44911 | PMM[3].Phase[2].Current[11]
EP2_PMM3_Phase2_Current12 | REAL | IOD_EP2_TCP | 4913 | 44913 | PMM[3].Phase[2].Current[12]
EP2_PMM3_Phase2_Current13 | REAL | IOD_EP2_TCP | 4915 | 44915 | PMM[3].Phase[2].Current[13]
EP2_PMM3_Phase2_Current14 | REAL | IOD_EP2_TCP | 4917 | 44917 | PMM[3].Phase[2].Current[14]
EP2_PMM3_Phase2_Current15 | REAL | IOD_EP2_TCP | 4919 | 44919 | PMM[3].Phase[2].Current[15]
EP2_PMM3_Phase2_Current16 | REAL | IOD_EP2_TCP | 4921 | 44921 | PMM[3].Phase[2].Current[16]
EP2_PMM3_Phase2_Current17 | REAL | IOD_EP2_TCP | 4923 | 44923 | PMM[3].Phase[2].Current[17]
EP2_PMM3_Phase2_Current18 | REAL | IOD_EP2_TCP | 4925 | 44925 | PMM[3].Phase[2].Current[18]
EP2_PMM3_Phase2_Current19 | REAL | IOD_EP2_TCP | 4927 | 44927 | PMM[3].Phase[2].Current[19]
EP2_PMM3_Phase2_Current1 | REAL | IOD_EP2_TCP | 4929 | 44929 | PMM[3].Phase[2].Current[1]
EP2_PMM3_Phase2_Current20 | REAL | IOD_EP2_TCP | 4931 | 44931 | PMM[3].Phase[2].Current[20]
EP2_PMM3_Phase2_Current21 | REAL | IOD_EP2_TCP | 4933 | 44933 | PMM[3].Phase[2].Current[21]
EP2_PMM3_Phase2_Current22 | REAL | IOD_EP2_TCP | 4935 | 44935 | PMM[3].Phase[2].Current[22]
EP2_PMM3_Phase2_Current23 | REAL | IOD_EP2_TCP | 4937 | 44937 | PMM[3].Phase[2].Current[23]
EP2_PMM3_Phase2_Current24 | REAL | IOD_EP2_TCP | 4939 | 44939 | PMM[3].Phase[2].Current[24]
EP2_PMM3_Phase2_Current25 | REAL | IOD_EP2_TCP | 4941 | 44941 | PMM[3].Phase[2].Current[25]
EP2_PMM3_Phase2_Current26 | REAL | IOD_EP2_TCP | 4943 | 44943 | PMM[3].Phase[2].Current[26]
EP2_PMM3_Phase2_Current27 | REAL | IOD_EP2_TCP | 4945 | 44945 | PMM[3].Phase[2].Current[27]
EP2_PMM3_Phase2_Current28 | REAL | IOD_EP2_TCP | 4947 | 44947 | PMM[3].Phase[2].Current[28]
EP2_PMM3_Phase2_Current29 | REAL | IOD_EP2_TCP | 4949 | 44949 | PMM[3].Phase[2].Current[29]
EP2_PMM3_Phase2_Current2 | REAL | IOD_EP2_TCP | 4951 | 44951 | PMM[3].Phase[2].Current[2]
EP2_PMM3_Phase2_Current30 | REAL | IOD_EP2_TCP | 4953 | 44953 | PMM[3].Phase[2].Current[30]
EP2_PMM3_Phase2_Current31 | REAL | IOD_EP2_TCP | 4955 | 44955 | PMM[3].Phase[2].Current[31]
EP2_PMM3_Phase2_Current32 | REAL | IOD_EP2_TCP | 4957 | 44957 | PMM[3].Phase[2].Current[32]
EP2_PMM3_Phase2_Current33 | REAL | IOD_EP2_TCP | 4959 | 44959 | PMM[3].Phase[2].Current[33]
EP2_PMM3_Phase2_Current34 | REAL | IOD_EP2_TCP | 4961 | 44961 | PMM[3].Phase[2].Current[34]
EP2_PMM3_Phase2_Current35 | REAL | IOD_EP2_TCP | 4963 | 44963 | PMM[3].Phase[2].Current[35]
EP2_PMM3_Phase2_Current36 | REAL | IOD_EP2_TCP | 4965 | 44965 | PMM[3].Phase[2].Current[36]
EP2_PMM3_Phase2_Current37 | REAL | IOD_EP2_TCP | 4967 | 44967 | PMM[3].Phase[2].Current[37]
EP2_PMM3_Phase2_Current38 | REAL | IOD_EP2_TCP | 4969 | 44969 | PMM[3].Phase[2].Current[38]
EP2_PMM3_Phase2_Current39 | REAL | IOD_EP2_TCP | 4971 | 44971 | PMM[3].Phase[2].Current[39]
EP2_PMM3_Phase2_Current3 | REAL | IOD_EP2_TCP | 4973 | 44973 | PMM[3].Phase[2].Current[3]
EP2_PMM3_Phase2_Current40 | REAL | IOD_EP2_TCP | 4975 | 44975 | PMM[3].Phase[2].Current[40]
EP2_PMM3_Phase2_Current41 | REAL | IOD_EP2_TCP | 4977 | 44977 | PMM[3].Phase[2].Current[41]
EP2_PMM3_Phase2_Current42 | REAL | IOD_EP2_TCP | 4979 | 44979 | PMM[3].Phase[2].Current[42]
EP2_PMM3_Phase2_Current4 | REAL | IOD_EP2_TCP | 4981 | 44981 | PMM[3].Phase[2].Current[4]
EP2_PMM3_Phase2_Current5 | REAL | IOD_EP2_TCP | 4983 | 44983 | PMM[3].Phase[2].Current[5]
EP2_PMM3_Phase2_Current6 | REAL | IOD_EP2_TCP | 4985 | 44985 | PMM[3].Phase[2].Current[6]
EP2_PMM3_Phase2_Current7 | REAL | IOD_EP2_TCP | 4987 | 44987 | PMM[3].Phase[2].Current[7]
EP2_PMM3_Phase2_Current8 | REAL | IOD_EP2_TCP | 4989 | 44989 | PMM[3].Phase[2].Current[8]
EP2_PMM3_Phase2_Current9 | REAL | IOD_EP2_TCP | 4991 | 44991 | PMM[3].Phase[2].Current[9]
EP2_PMM3_Phase3_Current10 | REAL | IOD_EP2_TCP | 4993 | 44993 | PMM[3].Phase[3].Current[10]
EP2_PMM3_Phase3_Current11 | REAL | IOD_EP2_TCP | 4995 | 44995 | PMM[3].Phase[3].Current[11]
EP2_PMM3_Phase3_Current12 | REAL | IOD_EP2_TCP | 4997 | 44997 | PMM[3].Phase[3].Current[12]
EP2_PMM3_Phase3_Current13 | REAL | IOD_EP2_TCP | 4999 | 44999 | PMM[3].Phase[3].Current[13]
EP2_PMM3_Phase3_Current14 | REAL | IOD_EP2_TCP | 5001 | 45001 | PMM[3].Phase[3].Current[14]
EP2_PMM3_Phase3_Current15 | REAL | IOD_EP2_TCP | 5003 | 45003 | PMM[3].Phase[3].Current[15]
EP2_PMM3_Phase3_Current16 | REAL | IOD_EP2_TCP | 5005 | 45005 | PMM[3].Phase[3].Current[16]
EP2_PMM3_Phase3_Current17 | REAL | IOD_EP2_TCP | 5007 | 45007 | PMM[3].Phase[3].Current[17]
EP2_PMM3_Phase3_Current18 | REAL | IOD_EP2_TCP | 5009 | 45009 | PMM[3].Phase[3].Current[18]
EP2_PMM3_Phase3_Current19 | REAL | IOD_EP2_TCP | 5011 | 45011 | PMM[3].Phase[3].Current[19]
EP2_PMM3_Phase3_Current1 | REAL | IOD_EP2_TCP | 5013 | 45013 | PMM[3].Phase[3].Current[1]
EP2_PMM3_Phase3_Current20 | REAL | IOD_EP2_TCP | 5015 | 45015 | PMM[3].Phase[3].Current[20]
EP2_PMM3_Phase3_Current21 | REAL | IOD_EP2_TCP | 5017 | 45017 | PMM[3].Phase[3].Current[21]
EP2_PMM3_Phase3_Current22 | REAL | IOD_EP2_TCP | 5019 | 45019 | PMM[3].Phase[3].Current[22]
EP2_PMM3_Phase3_Current23 | REAL | IOD_EP2_TCP | 5021 | 45021 | PMM[3].Phase[3].Current[23]
EP2_PMM3_Phase3_Current24 | REAL | IOD_EP2_TCP | 5023 | 45023 | PMM[3].Phase[3].Current[24]
EP2_PMM3_Phase3_Current25 | REAL | IOD_EP2_TCP | 5025 | 45025 | PMM[3].Phase[3].Current[25]
EP2_PMM3_Phase3_Current26 | REAL | IOD_EP2_TCP | 5027 | 45027 | PMM[3].Phase[3].Current[26]
EP2_PMM3_Phase3_Current27 | REAL | IOD_EP2_TCP | 5029 | 45029 | PMM[3].Phase[3].Current[27]
EP2_PMM3_Phase3_Current28 | REAL | IOD_EP2_TCP | 5031 | 45031 | PMM[3].Phase[3].Current[28]
EP2_PMM3_Phase3_Current29 | REAL | IOD_EP2_TCP | 5033 | 45033 | PMM[3].Phase[3].Current[29]
EP2_PMM3_Phase3_Current2 | REAL | IOD_EP2_TCP | 5035 | 45035 | PMM[3].Phase[3].Current[2]
EP2_PMM3_Phase3_Current30 | REAL | IOD_EP2_TCP | 5037 | 45037 | PMM[3].Phase[3].Current[30]
EP2_PMM3_Phase3_Current31 | REAL | IOD_EP2_TCP | 5039 | 45039 | PMM[3].Phase[3].Current[31]
EP2_PMM3_Phase3_Current32 | REAL | IOD_EP2_TCP | 5041 | 45041 | PMM[3].Phase[3].Current[32]
EP2_PMM3_Phase3_Current33 | REAL | IOD_EP2_TCP | 5043 | 45043 | PMM[3].Phase[3].Current[33]
EP2_PMM3_Phase3_Current34 | REAL | IOD_EP2_TCP | 5045 | 45045 | PMM[3].Phase[3].Current[34]
EP2_PMM3_Phase3_Current35 | REAL | IOD_EP2_TCP | 5047 | 45047 | PMM[3].Phase[3].Current[35]
EP2_PMM3_Phase3_Current36 | REAL | IOD_EP2_TCP | 5049 | 45049 | PMM[3].Phase[3].Current[36]
EP2_PMM3_Phase3_Current37 | REAL | IOD_EP2_TCP | 5051 | 45051 | PMM[3].Phase[3].Current[37]
EP2_PMM3_Phase3_Current38 | REAL | IOD_EP2_TCP | 5053 | 45053 | PMM[3].Phase[3].Current[38]
EP2_PMM3_Phase3_Current39 | REAL | IOD_EP2_TCP | 5055 | 45055 | PMM[3].Phase[3].Current[39]
EP2_PMM3_Phase3_Current3 | REAL | IOD_EP2_TCP | 5057 | 45057 | PMM[3].Phase[3].Current[3]
EP2_PMM3_Phase3_Current40 | REAL | IOD_EP2_TCP | 5059 | 45059 | PMM[3].Phase[3].Current[40]
EP2_PMM3_Phase3_Current41 | REAL | IOD_EP2_TCP | 5061 | 45061 | PMM[3].Phase[3].Current[41]
EP2_PMM3_Phase3_Current42 | REAL | IOD_EP2_TCP | 5063 | 45063 | PMM[3].Phase[3].Current[42]
EP2_PMM3_Phase3_Current4 | REAL | IOD_EP2_TCP | 5065 | 45065 | PMM[3].Phase[3].Current[4]
EP2_PMM3_Phase3_Current5 | REAL | IOD_EP2_TCP | 5067 | 45067 | PMM[3].Phase[3].Current[5]
EP2_PMM3_Phase3_Current6 | REAL | IOD_EP2_TCP | 5069 | 45069 | PMM[3].Phase[3].Current[6]
EP2_PMM3_Phase3_Current7 | REAL | IOD_EP2_TCP | 5071 | 45071 | PMM[3].Phase[3].Current[7]
EP2_PMM3_Phase3_Current8 | REAL | IOD_EP2_TCP | 5073 | 45073 | PMM[3].Phase[3].Current[8]
EP2_PMM3_Phase3_Current9 | REAL | IOD_EP2_TCP | 5075 | 45075 | PMM[3].Phase[3].Current[9]
EP2_PMM3_PowerFactorPhaseA | REAL | IOD_EP2_TCP | 5077 | 45077 | PMM[3].PowerFactorPhaseA
EP2_PMM3_PowerFactorPhaseB | REAL | IOD_EP2_TCP | 5079 | 45079 | PMM[3].PowerFactorPhaseB
EP2_PMM3_PowerFactorPhaseC | REAL | IOD_EP2_TCP | 5081 | 45081 | PMM[3].PowerFactorPhaseC
EP2_PMM3_TotalActivePower_kW | REAL | IOD_EP2_TCP | 5083 | 45083 | PMM[3].TotalActivePower_kW
EP2_PMM3_TotalAparentPower_kVA | REAL | IOD_EP2_TCP | 5085 | 45085 | PMM[3].TotalAparentPower_kVA
EP2_PMM3_TotalPowerFactor | REAL | IOD_EP2_TCP | 5087 | 45087 | PMM[3].TotalPowerFactor
EP2_PMM3_TotalReactivePower_kVAR | REAL | IOD_EP2_TCP | 5089 | 45089 | PMM[3].TotalReactivePower_kVAR
EP2_PMM3_VoltageBetweenPhaseAB_V | REAL | IOD_EP2_TCP | 5091 | 45091 | PMM[3].VoltageBetweenPhaseAB_V
EP2_PMM3_VoltageBetweenPhaseAN_V | REAL | IOD_EP2_TCP | 5093 | 45093 | PMM[3].VoltageBetweenPhaseAN_V
EP2_PMM3_VoltageBetweenPhaseBC_V | REAL | IOD_EP2_TCP | 5095 | 45095 | PMM[3].VoltageBetweenPhaseBC_V
EP2_PMM3_VoltageBetweenPhaseBN_V | REAL | IOD_EP2_TCP | 5097 | 45097 | PMM[3].VoltageBetweenPhaseBN_V
EP2_PMM3_VoltageBetweenPhaseCA_V | REAL | IOD_EP2_TCP | 5099 | 45099 | PMM[3].VoltageBetweenPhaseCA_V
EP2_PMM3_VoltageBetweenPhaseCN_V | REAL | IOD_EP2_TCP | 5101 | 45101 | PMM[3].VoltageBetweenPhaseCN_V
EP2_rVersion | REAL | IOD_EP2_TCP | 5103 | 45103 | rVersion
EP2_SenzorTemp1 | REAL | IOD_EP2_TCP | 5105 | 45105 | SenzorTemp[1]
EP2_SenzorTemp2 | REAL | IOD_EP2_TCP | 5107 | 45107 | SenzorTemp[2]
EP2_SenzorVlaga1 | REAL | IOD_EP2_TCP | 5109 | 45109 | SenzorVlaga[1]
EP2_SenzorVlaga2 | REAL | IOD_EP2_TCP | 5111 | 45111 | SenzorVlaga[2]
EP2_TempMaxPoint | REAL | IOD_EP2_TCP | 5113 | 45113 | TempMaxPoint
EP2_TempSetPoint | REAL | IOD_EP2_TCP | 5115 | 45115 | TempSetPoint
EP2UPS1EstimatedChargeRemaining | REAL | IOD_EP2_TCP | 5117 | 45117 | UPS[1].EstimatedChargeRemaining
EP2UPS1EstimatedMinutesRemaining | REAL | IOD_EP2_TCP | 5119 | 45119 | UPS[1].EstimatedMinutesRemaining
EP2UPS1IzhodMocL1 | REAL | IOD_EP2_TCP | 5121 | 45121 | UPS[1].IzhodMocL1
EP2UPS1IzhodMocL2 | REAL | IOD_EP2_TCP | 5123 | 45123 | UPS[1].IzhodMocL2
EP2UPS1IzhodMocL3 | REAL | IOD_EP2_TCP | 5125 | 45125 | UPS[1].IzhodMocL3
EP2UPS1NapetostBaterije | REAL | IOD_EP2_TCP | 5127 | 45127 | UPS[1].NapetostBaterije
EP2UPS1TemperaturaBaterije | REAL | IOD_EP2_TCP | 5129 | 45129 | UPS[1].TemperaturaBaterije
EP2UPS1VhodFrekvencaL1 | REAL | IOD_EP2_TCP | 5131 | 45131 | UPS[1].VhodFrekvencaL1
EP2UPS1VhodFrekvencaL2 | REAL | IOD_EP2_TCP | 5133 | 45133 | UPS[1].VhodFrekvencaL2
EP2UPS1VhodFrekvencaL3 | REAL | IOD_EP2_TCP | 5135 | 45135 | UPS[1].VhodFrekvencaL3
EP2UPS1VhodNapetostL1 | REAL | IOD_EP2_TCP | 5137 | 45137 | UPS[1].VhodNapetostL1
EP2UPS1VhodNapetostL2 | REAL | IOD_EP2_TCP | 5139 | 45139 | UPS[1].VhodNapetostL2
EP2UPS1VhodNapetostL3 | REAL | IOD_EP2_TCP | 5141 | 45141 | UPS[1].VhodNapetostL3
EP2UPS2EstimatedChargeRemaining | REAL | IOD_EP2_TCP | 5143 | 45143 | UPS[2].EstimatedChargeRemaining
EP2UPS2EstimatedMinutesRemaining | REAL | IOD_EP2_TCP | 5145 | 45145 | UPS[2].EstimatedMinutesRemaining
EP2UPS2IzhodMocL1 | REAL | IOD_EP2_TCP | 5147 | 45147 | UPS[2].IzhodMocL1
EP2UPS2IzhodMocL2 | REAL | IOD_EP2_TCP | 5149 | 45149 | UPS[2].IzhodMocL2
EP2UPS2IzhodMocL3 | REAL | IOD_EP2_TCP | 5151 | 45151 | UPS[2].IzhodMocL3
EP2UPS2NapetostBaterije | REAL | IOD_EP2_TCP | 5153 | 45153 | UPS[2].NapetostBaterije
EP2UPS2TemperaturaBaterije | REAL | IOD_EP2_TCP | 5155 | 45155 | UPS[2].TemperaturaBaterije
EP2UPS2VhodFrekvencaL1 | REAL | IOD_EP2_TCP | 5157 | 45157 | UPS[2].VhodFrekvencaL1
EP2UPS2VhodFrekvencaL2 | REAL | IOD_EP2_TCP | 5159 | 45159 | UPS[2].VhodFrekvencaL2
EP2UPS2VhodFrekvencaL3 | REAL | IOD_EP2_TCP | 5161 | 45161 | UPS[2].VhodFrekvencaL3
EP2UPS2VhodNapetostL1 | REAL | IOD_EP2_TCP | 5163 | 45163 | UPS[2].VhodNapetostL1
EP2UPS2VhodNapetostL2 | REAL | IOD_EP2_TCP | 5165 | 45165 | UPS[2].VhodNapetostL2
EP2UPS2VhodNapetostL3 | REAL | IOD_EP2_TCP | 5167 | 45167 | UPS[2].VhodNapetostL3
EP2KlimaGalNastMaxTemp | REAL | IOD_EP2_TCP | 5169 | 45169 | KlimaGal.NastMaxTemp
EP2KlimaGalNastMaxVlaznost | REAL | IOD_EP2_TCP | 5171 | 45171 | KlimaGal.NastMaxVlaznost
EP2KlimaGalNastMinTemp | REAL | IOD_EP2_TCP | 5173 | 45173 | KlimaGal.NastMinTemp
EP2KlimaGalNastMinVlaznost | REAL | IOD_EP2_TCP | 5175 | 45175 | KlimaGal.NastMinVlaznost
EP2KlimaGalNastTempProstora | REAL | IOD_EP2_TCP | 5177 | 45177 | KlimaGal.NastTempProstora
EP2KlimaGalNastVlaznost | REAL | IOD_EP2_TCP | 5179 | 45179 | KlimaGal.NastVlaznost
EP2KlimaGalObratovalneUre | REAL | IOD_EP2_TCP | 5181 | 45181 | KlimaGal.ObratovalneUre
EP2KlimaGalTemperaturaProstora | REAL | IOD_EP2_TCP | 5183 | 45183 | KlimaGal.TemperaturaProstora
EP2KlimaGalTempIzpihanegaZraka | REAL | IOD_EP2_TCP | 5185 | 45185 | KlimaGal.TempIzpihanegaZraka
EP2KlimaGalTempPovratneVode | REAL | IOD_EP2_TCP | 5187 | 45187 | KlimaGal.TempPovratneVode
EP2KlimaGalVlaznostProstora | REAL | IOD_EP2_TCP | 5189 | 45189 | KlimaGal.VlaznostProstora
EP2KlimaGalZunanjaTemp | REAL | IOD_EP2_TCP | 5191 | 45191 | KlimaGal.ZunanjaTemp
EP2PMMfaza01 | REAL | IOD_EP2_TCP | 5193 | 45193 | PMMfaza01
EP2PMMfaza02 | REAL | IOD_EP2_TCP | 5195 | 45195 | PMMfaza02
EP2PMMfaza03 | REAL | IOD_EP2_TCP | 5197 | 45197 | PMMfaza03
EP2PMMfaza04 | REAL | IOD_EP2_TCP | 5199 | 45199 | PMMfaza04
EP2PMMfaza05 | REAL | IOD_EP2_TCP | 5201 | 45201 | PMMfaza05
EP2PMMfaza06 | REAL | IOD_EP2_TCP | 5203 | 45203 | PMMfaza06
EP2PMMfaza07 | REAL | IOD_EP2_TCP | 5205 | 45205 | PMMfaza07
EP2PMMfaza08 | REAL | IOD_EP2_TCP | 5207 | 45207 | PMMfaza08
EP2PMMfaza09 | REAL | IOD_EP2_TCP | 5209 | 45209 | PMMfaza09
EP2PMMfaza10 | REAL | IOD_EP2_TCP | 5211 | 45211 | PMMfaza10
EP2PMMfaza11 | REAL | IOD_EP2_TCP | 5213 | 45213 | PMMfaza11
EP2PMMfaza12 | REAL | IOD_EP2_TCP | 5215 | 45215 | PMMfaza12
EP2PMMfaza13 | REAL | IOD_EP2_TCP | 5217 | 45217 | PMMfaza13
EP2PMMfaza14 | REAL | IOD_EP2_TCP | 5219 | 45219 | PMMfaza14
EP2PMMfaza15 | REAL | IOD_EP2_TCP | 5221 | 45221 | PMMfaza15
EP2PMMfaza16 | REAL | IOD_EP2_TCP | 5223 | 45223 | PMMfaza16
EP2PMMfaza17 | REAL | IOD_EP2_TCP | 5225 | 45225 | PMMfaza17
EP2PMMfaza18 | REAL | IOD_EP2_TCP | 5227 | 45227 | PMMfaza18
EP2PMMfaza19 | REAL | IOD_EP2_TCP | 5229 | 45229 | PMMfaza19
EP2PMMfaza20 | REAL | IOD_EP2_TCP | 5231 | 45231 | PMMfaza20
EP2PMMfaza21 | REAL | IOD_EP2_TCP | 5233 | 45233 | PMMfaza21
EP2PMMfaza22 | REAL | IOD_EP2_TCP | 5235 | 45235 | PMMfaza22
EP2PMMfaza23 | REAL | IOD_EP2_TCP | 5237 | 45237 | PMMfaza23
EP2PMMfaza24 | REAL | IOD_EP2_TCP | 5239 | 45239 | PMMfaza24
EP2PMMfaza25 | REAL | IOD_EP2_TCP | 5241 | 45241 | PMMfaza25
EP2PMMfaza26 | REAL | IOD_EP2_TCP | 5243 | 45243 | PMMfaza26
EP2PMMfaza27 | REAL | IOD_EP2_TCP | 5245 | 45245 | PMMfaza27
EP2PMMfaza28 | REAL | IOD_EP2_TCP | 5247 | 45247 | PMMfaza28
EP2PMMfaza29 | REAL | IOD_EP2_TCP | 5249 | 45249 | PMMfaza29
EP2PMMfaza30 | REAL | IOD_EP2_TCP | 5251 | 45251 | PMMfaza30
EP2PMMfaza31 | REAL | IOD_EP2_TCP | 5253 | 45253 | PMMfaza31
EP2PMMfaza32 | REAL | IOD_EP2_TCP | 5255 | 45255 | PMMfaza32
EP2PMMfaza33 | REAL | IOD_EP2_TCP | 5257 | 45257 | PMMfaza33
EP2PMMfaza34 | REAL | IOD_EP2_TCP | 5259 | 45259 | PMMfaza34
EP2PMMfaza35 | REAL | IOD_EP2_TCP | 5261 | 45261 | PMMfaza35
EP2PMMfaza36 | REAL | IOD_EP2_TCP | 5263 | 45263 | PMMfaza36
EP2PMMfaza37 | REAL | IOD_EP2_TCP | 5265 | 45265 | PMMfaza37
EP2PMMfaza38 | REAL | IOD_EP2_TCP | 5267 | 45267 | PMMfaza38
EP2PMMfaza39 | REAL | IOD_EP2_TCP | 5269 | 45269 | PMMfaza39
EP2PMMfaza40 | REAL | IOD_EP2_TCP | 5271 | 45271 | PMMfaza40
EP2PMMfaza41 | REAL | IOD_EP2_TCP | 5273 | 45273 | PMMfaza41
EP2PMMfaza42 | REAL | IOD_EP2_TCP | 5275 | 45275 | PMMfaza42
EP2PMMfaza6010 | REAL | IOD_EP2_TCP | 5277 | 45277 | PMMfaza60[10]
EP2PMMfaza6011 | REAL | IOD_EP2_TCP | 5279 | 45279 | PMMfaza60[11]
EP2PMMfaza6012 | REAL | IOD_EP2_TCP | 5281 | 45281 | PMMfaza60[12]
EP2PMMfaza6013 | REAL | IOD_EP2_TCP | 5283 | 45283 | PMMfaza60[13]
EP2PMMfaza6014 | REAL | IOD_EP2_TCP | 5285 | 45285 | PMMfaza60[14]
EP2PMMfaza6015 | REAL | IOD_EP2_TCP | 5287 | 45287 | PMMfaza60[15]
EP2PMMfaza6016 | REAL | IOD_EP2_TCP | 5289 | 45289 | PMMfaza60[16]
EP2PMMfaza6017 | REAL | IOD_EP2_TCP | 5291 | 45291 | PMMfaza60[17]
EP2PMMfaza6018 | REAL | IOD_EP2_TCP | 5293 | 45293 | PMMfaza60[18]
EP2PMMfaza6019 | REAL | IOD_EP2_TCP | 5295 | 45295 | PMMfaza60[19]
EP2PMMfaza601 | REAL | IOD_EP2_TCP | 5297 | 45297 | PMMfaza60[1]
EP2PMMfaza6020 | REAL | IOD_EP2_TCP | 5299 | 45299 | PMMfaza60[20]
EP2PMMfaza6021 | REAL | IOD_EP2_TCP | 5301 | 45301 | PMMfaza60[21]
EP2PMMfaza6022 | REAL | IOD_EP2_TCP | 5303 | 45303 | PMMfaza60[22]
EP2PMMfaza6023 | REAL | IOD_EP2_TCP | 5305 | 45305 | PMMfaza60[23]
EP2PMMfaza6024 | REAL | IOD_EP2_TCP | 5307 | 45307 | PMMfaza60[24]
EP2PMMfaza6025 | REAL | IOD_EP2_TCP | 5309 | 45309 | PMMfaza60[25]
EP2PMMfaza6026 | REAL | IOD_EP2_TCP | 5311 | 45311 | PMMfaza60[26]
EP2PMMfaza6027 | REAL | IOD_EP2_TCP | 5313 | 45313 | PMMfaza60[27]
EP2PMMfaza6028 | REAL | IOD_EP2_TCP | 5315 | 45315 | PMMfaza60[28]
EP2PMMfaza6029 | REAL | IOD_EP2_TCP | 5317 | 45317 | PMMfaza60[29]
EP2PMMfaza602 | REAL | IOD_EP2_TCP | 5319 | 45319 | PMMfaza60[2]
EP2PMMfaza6030 | REAL | IOD_EP2_TCP | 5321 | 45321 | PMMfaza60[30]
EP2PMMfaza6031 | REAL | IOD_EP2_TCP | 5323 | 45323 | PMMfaza60[31]
EP2PMMfaza6032 | REAL | IOD_EP2_TCP | 5325 | 45325 | PMMfaza60[32]
EP2PMMfaza6033 | REAL | IOD_EP2_TCP | 5327 | 45327 | PMMfaza60[33]
EP2PMMfaza6034 | REAL | IOD_EP2_TCP | 5329 | 45329 | PMMfaza60[34]
EP2PMMfaza6035 | REAL | IOD_EP2_TCP | 5331 | 45331 | PMMfaza60[35]
EP2PMMfaza6036 | REAL | IOD_EP2_TCP | 5333 | 45333 | PMMfaza60[36]
EP2PMMfaza6037 | REAL | IOD_EP2_TCP | 5335 | 45335 | PMMfaza60[37]
EP2PMMfaza6038 | REAL | IOD_EP2_TCP | 5337 | 45337 | PMMfaza60[38]
EP2PMMfaza6039 | REAL | IOD_EP2_TCP | 5339 | 45339 | PMMfaza60[39]
EP2PMMfaza603 | REAL | IOD_EP2_TCP | 5341 | 45341 | PMMfaza60[3]
EP2PMMfaza6040 | REAL | IOD_EP2_TCP | 5343 | 45343 | PMMfaza60[40]
EP2PMMfaza6041 | REAL | IOD_EP2_TCP | 5345 | 45345 | PMMfaza60[41]
EP2PMMfaza6042 | REAL | IOD_EP2_TCP | 5347 | 45347 | PMMfaza60[42]
EP2PMMfaza604 | REAL | IOD_EP2_TCP | 5349 | 45349 | PMMfaza60[4]
EP2PMMfaza605 | REAL | IOD_EP2_TCP | 5351 | 45351 | PMMfaza60[5]
EP2PMMfaza606 | REAL | IOD_EP2_TCP | 5353 | 45353 | PMMfaza60[6]
EP2PMMfaza607 | REAL | IOD_EP2_TCP | 5355 | 45355 | PMMfaza60[7]
EP2PMMfaza608 | REAL | IOD_EP2_TCP | 5357 | 45357 | PMMfaza60[8]
EP2PMMfaza609 | REAL | IOD_EP2_TCP | 5359 | 45359 | PMMfaza60[9]
EP2PMMfaza8010 | REAL | IOD_EP2_TCP | 5361 | 45361 | PMMfaza80[10]
EP2PMMfaza8011 | REAL | IOD_EP2_TCP | 5363 | 45363 | PMMfaza80[11]
EP2PMMfaza8012 | REAL | IOD_EP2_TCP | 5365 | 45365 | PMMfaza80[12]
EP2PMMfaza8013 | REAL | IOD_EP2_TCP | 5367 | 45367 | PMMfaza80[13]
EP2PMMfaza8014 | REAL | IOD_EP2_TCP | 5369 | 45369 | PMMfaza80[14]
EP2PMMfaza8015 | REAL | IOD_EP2_TCP | 5371 | 45371 | PMMfaza80[15]
EP2PMMfaza8016 | REAL | IOD_EP2_TCP | 5373 | 45373 | PMMfaza80[16]
EP2PMMfaza8017 | REAL | IOD_EP2_TCP | 5375 | 45375 | PMMfaza80[17]
EP2PMMfaza8018 | REAL | IOD_EP2_TCP | 5377 | 45377 | PMMfaza80[18]
EP2PMMfaza8019 | REAL | IOD_EP2_TCP | 5379 | 45379 | PMMfaza80[19]
EP2PMMfaza801 | REAL | IOD_EP2_TCP | 5381 | 45381 | PMMfaza80[1]
EP2PMMfaza8020 | REAL | IOD_EP2_TCP | 5383 | 45383 | PMMfaza80[20]
EP2PMMfaza8021 | REAL | IOD_EP2_TCP | 5385 | 45385 | PMMfaza80[21]
EP2PMMfaza8022 | REAL | IOD_EP2_TCP | 5387 | 45387 | PMMfaza80[22]
EP2PMMfaza8023 | REAL | IOD_EP2_TCP | 5389 | 45389 | PMMfaza80[23]
EP2PMMfaza8024 | REAL | IOD_EP2_TCP | 5391 | 45391 | PMMfaza80[24]
EP2PMMfaza8025 | REAL | IOD_EP2_TCP | 5393 | 45393 | PMMfaza80[25]
EP2PMMfaza8026 | REAL | IOD_EP2_TCP | 5395 | 45395 | PMMfaza80[26]
EP2PMMfaza8027 | REAL | IOD_EP2_TCP | 5397 | 45397 | PMMfaza80[27]
EP2PMMfaza8028 | REAL | IOD_EP2_TCP | 5399 | 45399 | PMMfaza80[28]
EP2PMMfaza8029 | REAL | IOD_EP2_TCP | 5401 | 45401 | PMMfaza80[29]
EP2PMMfaza802 | REAL | IOD_EP2_TCP | 5403 | 45403 | PMMfaza80[2]
EP2PMMfaza8030 | REAL | IOD_EP2_TCP | 5405 | 45405 | PMMfaza80[30]
EP2PMMfaza8031 | REAL | IOD_EP2_TCP | 5407 | 45407 | PMMfaza80[31]
EP2PMMfaza8032 | REAL | IOD_EP2_TCP | 5409 | 45409 | PMMfaza80[32]
EP2PMMfaza8033 | REAL | IOD_EP2_TCP | 5411 | 45411 | PMMfaza80[33]
EP2PMMfaza8034 | REAL | IOD_EP2_TCP | 5413 | 45413 | PMMfaza80[34]
EP2PMMfaza8035 | REAL | IOD_EP2_TCP | 5415 | 45415 | PMMfaza80[35]
EP2PMMfaza8036 | REAL | IOD_EP2_TCP | 5417 | 45417 | PMMfaza80[36]
EP2PMMfaza8037 | REAL | IOD_EP2_TCP | 5419 | 45419 | PMMfaza80[37]
EP2PMMfaza8038 | REAL | IOD_EP2_TCP | 5421 | 45421 | PMMfaza80[38]
EP2PMMfaza8039 | REAL | IOD_EP2_TCP | 5423 | 45423 | PMMfaza80[39]
EP2PMMfaza803 | REAL | IOD_EP2_TCP | 5425 | 45425 | PMMfaza80[3]
EP2PMMfaza8040 | REAL | IOD_EP2_TCP | 5427 | 45427 | PMMfaza80[40]
EP2PMMfaza8041 | REAL | IOD_EP2_TCP | 5429 | 45429 | PMMfaza80[41]
EP2PMMfaza8042 | REAL | IOD_EP2_TCP | 5431 | 45431 | PMMfaza80[42]
EP2PMMfaza804 | REAL | IOD_EP2_TCP | 5433 | 45433 | PMMfaza80[4]
EP2PMMfaza805 | REAL | IOD_EP2_TCP | 5435 | 45435 | PMMfaza80[5]
EP2PMMfaza806 | REAL | IOD_EP2_TCP | 5437 | 45437 | PMMfaza80[6]
EP2PMMfaza807 | REAL | IOD_EP2_TCP | 5439 | 45439 | PMMfaza80[7]
EP2PMMfaza808 | REAL | IOD_EP2_TCP | 5441 | 45441 | PMMfaza80[8]
EP2PMMfaza809 | REAL | IOD_EP2_TCP | 5443 | 45443 | PMMfaza80[9]
EP2PMMgalActivePowerPhaseA_kW | REAL | IOD_EP2_TCP | 5445 | 45445 | PMMgal.ActivePowerPhaseA_kW
EP2PMMgalActivePowerPhaseB_kW | REAL | IOD_EP2_TCP | 5447 | 45447 | PMMgal.ActivePowerPhaseB_kW
EP2PMMgalActivePowerPhaseC_kW | REAL | IOD_EP2_TCP | 5449 | 45449 | PMMgal.ActivePowerPhaseC_kW
EP2PMMgalAverageCurrent_A | REAL | IOD_EP2_TCP | 5451 | 45451 | PMMgal.AverageCurrent_A
EP2PMMgalAveragePhaseToNeutral_V | REAL | IOD_EP2_TCP | 5453 | 45453 | PMMgal.AveragePhaseToNeutral_V
EP2PMMgalAveragePhaseToPhase_V | REAL | IOD_EP2_TCP | 5455 | 45455 | PMMgal.AveragePhaseToPhase_V
EP2PMMgalCurrentInPhaseA_A | REAL | IOD_EP2_TCP | 5457 | 45457 | PMMgal.CurrentInPhaseA_A
EP2PMMgalCurrentInPhaseB_A | REAL | IOD_EP2_TCP | 5459 | 45459 | PMMgal.CurrentInPhaseB_A
EP2PMMgalCurrentInPhaseC_A | REAL | IOD_EP2_TCP | 5461 | 45461 | PMMgal.CurrentInPhaseC_A
EP2PMMgalEnergyConsumed_kWh | REAL | IOD_EP2_TCP | 5463 | 45463 | PMMgal.EnergyConsumed_kWh
EP2PMMgalFrequency_Hz | REAL | IOD_EP2_TCP | 5465 | 45465 | PMMgal.Frequency_Hz
EP2PMMgalNeutralCurrent_A | REAL | IOD_EP2_TCP | 5467 | 45467 | PMMgal.NeutralCurrent_A
EP2PMMgalPhase1Current10 | REAL | IOD_EP2_TCP | 5469 | 45469 | PMMgal.Phase[1].Current[10]
EP2PMMgalPhase1Current11 | REAL | IOD_EP2_TCP | 5471 | 45471 | PMMgal.Phase[1].Current[11]
EP2PMMgalPhase1Current12 | REAL | IOD_EP2_TCP | 5473 | 45473 | PMMgal.Phase[1].Current[12]
EP2PMMgalPhase1Current13 | REAL | IOD_EP2_TCP | 5475 | 45475 | PMMgal.Phase[1].Current[13]
EP2PMMgalPhase1Current14 | REAL | IOD_EP2_TCP | 5477 | 45477 | PMMgal.Phase[1].Current[14]
EP2PMMgalPhase1Current15 | REAL | IOD_EP2_TCP | 5479 | 45479 | PMMgal.Phase[1].Current[15]
EP2PMMgalPhase1Current16 | REAL | IOD_EP2_TCP | 5481 | 45481 | PMMgal.Phase[1].Current[16]
EP2PMMgalPhase1Current17 | REAL | IOD_EP2_TCP | 5483 | 45483 | PMMgal.Phase[1].Current[17]
EP2PMMgalPhase1Current18 | REAL | IOD_EP2_TCP | 5485 | 45485 | PMMgal.Phase[1].Current[18]
EP2PMMgalPhase1Current19 | REAL | IOD_EP2_TCP | 5487 | 45487 | PMMgal.Phase[1].Current[19]
EP2PMMgalPhase1Current1 | REAL | IOD_EP2_TCP | 5489 | 45489 | PMMgal.Phase[1].Current[1]
EP2PMMgalPhase1Current20 | REAL | IOD_EP2_TCP | 5491 | 45491 | PMMgal.Phase[1].Current[20]
EP2PMMgalPhase1Current21 | REAL | IOD_EP2_TCP | 5493 | 45493 | PMMgal.Phase[1].Current[21]
EP2PMMgalPhase1Current22 | REAL | IOD_EP2_TCP | 5495 | 45495 | PMMgal.Phase[1].Current[22]
EP2PMMgalPhase1Current23 | REAL | IOD_EP2_TCP | 5497 | 45497 | PMMgal.Phase[1].Current[23]
EP2PMMgalPhase1Current24 | REAL | IOD_EP2_TCP | 5499 | 45499 | PMMgal.Phase[1].Current[24]
EP2PMMgalPhase1Current25 | REAL | IOD_EP2_TCP | 5501 | 45501 | PMMgal.Phase[1].Current[25]
EP2PMMgalPhase1Current26 | REAL | IOD_EP2_TCP | 5503 | 45503 | PMMgal.Phase[1].Current[26]
EP2PMMgalPhase1Current27 | REAL | IOD_EP2_TCP | 5505 | 45505 | PMMgal.Phase[1].Current[27]
EP2PMMgalPhase1Current28 | REAL | IOD_EP2_TCP | 5507 | 45507 | PMMgal.Phase[1].Current[28]
EP2PMMgalPhase1Current29 | REAL | IOD_EP2_TCP | 5509 | 45509 | PMMgal.Phase[1].Current[29]
EP2PMMgalPhase1Current2 | REAL | IOD_EP2_TCP | 5511 | 45511 | PMMgal.Phase[1].Current[2]
EP2PMMgalPhase1Current30 | REAL | IOD_EP2_TCP | 5513 | 45513 | PMMgal.Phase[1].Current[30]
EP2PMMgalPhase1Current31 | REAL | IOD_EP2_TCP | 5515 | 45515 | PMMgal.Phase[1].Current[31]
EP2PMMgalPhase1Current32 | REAL | IOD_EP2_TCP | 5517 | 45517 | PMMgal.Phase[1].Current[32]
EP2PMMgalPhase1Current33 | REAL | IOD_EP2_TCP | 5519 | 45519 | PMMgal.Phase[1].Current[33]
EP2PMMgalPhase1Current34 | REAL | IOD_EP2_TCP | 5521 | 45521 | PMMgal.Phase[1].Current[34]
EP2PMMgalPhase1Current35 | REAL | IOD_EP2_TCP | 5523 | 45523 | PMMgal.Phase[1].Current[35]
EP2PMMgalPhase1Current36 | REAL | IOD_EP2_TCP | 5525 | 45525 | PMMgal.Phase[1].Current[36]
EP2PMMgalPhase1Current37 | REAL | IOD_EP2_TCP | 5527 | 45527 | PMMgal.Phase[1].Current[37]
EP2PMMgalPhase1Current38 | REAL | IOD_EP2_TCP | 5529 | 45529 | PMMgal.Phase[1].Current[38]
EP2PMMgalPhase1Current39 | REAL | IOD_EP2_TCP | 5531 | 45531 | PMMgal.Phase[1].Current[39]
EP2PMMgalPhase1Current3 | REAL | IOD_EP2_TCP | 5533 | 45533 | PMMgal.Phase[1].Current[3]
EP2PMMgalPhase1Current40 | REAL | IOD_EP2_TCP | 5535 | 45535 | PMMgal.Phase[1].Current[40]
EP2PMMgalPhase1Current41 | REAL | IOD_EP2_TCP | 5537 | 45537 | PMMgal.Phase[1].Current[41]
EP2PMMgalPhase1Current42 | REAL | IOD_EP2_TCP | 5539 | 45539 | PMMgal.Phase[1].Current[42]
EP2PMMgalPhase1Current4 | REAL | IOD_EP2_TCP | 5541 | 45541 | PMMgal.Phase[1].Current[4]
EP2PMMgalPhase1Current5 | REAL | IOD_EP2_TCP | 5543 | 45543 | PMMgal.Phase[1].Current[5]
EP2PMMgalPhase1Current6 | REAL | IOD_EP2_TCP | 5545 | 45545 | PMMgal.Phase[1].Current[6]
EP2PMMgalPhase1Current7 | REAL | IOD_EP2_TCP | 5547 | 45547 | PMMgal.Phase[1].Current[7]
EP2PMMgalPhase1Current8 | REAL | IOD_EP2_TCP | 5549 | 45549 | PMMgal.Phase[1].Current[8]
EP2PMMgalPhase1Current9 | REAL | IOD_EP2_TCP | 5551 | 45551 | PMMgal.Phase[1].Current[9]
EP2PMMgalPhase2Current10 | REAL | IOD_EP2_TCP | 5553 | 45553 | PMMgal.Phase[2].Current[10]
EP2PMMgalPhase2Current11 | REAL | IOD_EP2_TCP | 5555 | 45555 | PMMgal.Phase[2].Current[11]
EP2PMMgalPhase2Current12 | REAL | IOD_EP2_TCP | 5557 | 45557 | PMMgal.Phase[2].Current[12]
EP2PMMgalPhase2Current13 | REAL | IOD_EP2_TCP | 5559 | 45559 | PMMgal.Phase[2].Current[13]
EP2PMMgalPhase2Current14 | REAL | IOD_EP2_TCP | 5561 | 45561 | PMMgal.Phase[2].Current[14]
EP2PMMgalPhase2Current15 | REAL | IOD_EP2_TCP | 5563 | 45563 | PMMgal.Phase[2].Current[15]
EP2PMMgalPhase2Current16 | REAL | IOD_EP2_TCP | 5565 | 45565 | PMMgal.Phase[2].Current[16]
EP2PMMgalPhase2Current17 | REAL | IOD_EP2_TCP | 5567 | 45567 | PMMgal.Phase[2].Current[17]
EP2PMMgalPhase2Current18 | REAL | IOD_EP2_TCP | 5569 | 45569 | PMMgal.Phase[2].Current[18]
EP2PMMgalPhase2Current19 | REAL | IOD_EP2_TCP | 5571 | 45571 | PMMgal.Phase[2].Current[19]
EP2PMMgalPhase2Current1 | REAL | IOD_EP2_TCP | 5573 | 45573 | PMMgal.Phase[2].Current[1]
EP2PMMgalPhase2Current20 | REAL | IOD_EP2_TCP | 5575 | 45575 | PMMgal.Phase[2].Current[20]
EP2PMMgalPhase2Current21 | REAL | IOD_EP2_TCP | 5577 | 45577 | PMMgal.Phase[2].Current[21]
EP2PMMgalPhase2Current22 | REAL | IOD_EP2_TCP | 5579 | 45579 | PMMgal.Phase[2].Current[22]
EP2PMMgalPhase2Current23 | REAL | IOD_EP2_TCP | 5581 | 45581 | PMMgal.Phase[2].Current[23]
EP2PMMgalPhase2Current24 | REAL | IOD_EP2_TCP | 5583 | 45583 | PMMgal.Phase[2].Current[24]
EP2TempAlarmPoint | REAL | IOD_EP2_TCP | 5585 | 45585 | TempAlarmPoint
EP2_RazlikaUr | REAL | IOD_EP2_TCP | 5587 | 45587 | RazlikaUr
EP2_Circ1_MaximumDemandA2 | REAL | IOD_EP2_TCP | 5589 | 45589 | Circ[1].MaximumDemandA2
EP2_Circ1_MaximumDemandA3 | REAL | IOD_EP2_TCP | 5591 | 45591 | Circ[1].MaximumDemandA3
EP2Circ1RazEner_D_SCADA | REAL | IOD_EP2_TCP | 5593 | 45593 | Circ[1].RazEner_D_SCADA
EP2Circ1RazEner_T_SCADA | REAL | IOD_EP2_TCP | 5595 | 45595 | Circ[1].RazEner_T_SCADA
EP2Circ1RazEner_M_SCADA | REAL | IOD_EP2_TCP | 5597 | 45597 | Circ[1].RazEner_M_SCADA
EP2_UserCurrentName | STRING | IOD_EP2_TCP | 7001 | 47001[15] | UserCurrentName
EP2PMMgalAlarmPhase1C01_16_60to80 | UINT | IOD_EP2_TCP | 8001 | 48001 | PMMgal.AlarmPhase[1].C01_16_60to80
EP2PMMgalAlarmPhase1C01_16_over80 | UINT | IOD_EP2_TCP | 8002 | 48002 | PMMgal.AlarmPhase[1].C01_16_over80
EP2PMMgalAlarmPhase1C17_32_60to80 | UINT | IOD_EP2_TCP | 8003 | 48003 | PMMgal.AlarmPhase[1].C17_32_60to80
EP2PMMgalAlarmPhase1C17_32_over80 | UINT | IOD_EP2_TCP | 8004 | 48004 | PMMgal.AlarmPhase[1].C17_32_over80
EP2PMMgalAlarmPhase1C33_42_60to80 | UINT | IOD_EP2_TCP | 8005 | 48005 | PMMgal.AlarmPhase[1].C33_42_60to80
EP2PMMgalAlarmPhase1C33_42_over80 | UINT | IOD_EP2_TCP | 8006 | 48006 | PMMgal.AlarmPhase[1].C33_42_over80
EP2PMMgalAlarmPhase2C01_16_60to80 | UINT | IOD_EP2_TCP | 8007 | 48007 | PMMgal.AlarmPhase[2].C01_16_60to80
EP2PMMgalAlarmPhase2C01_16_over80 | UINT | IOD_EP2_TCP | 8008 | 48008 | PMMgal.AlarmPhase[2].C01_16_over80
EP2PMMgalAlarmPhase2C17_32_60to80 | UINT | IOD_EP2_TCP | 8009 | 48009 | PMMgal.AlarmPhase[2].C17_32_60to80
EP2PMMgalAlarmPhase2C17_32_over80 | UINT | IOD_EP2_TCP | 8010 | 48010 | PMMgal.AlarmPhase[2].C17_32_over80
EP2PMMgalAlarmPhase2C33_42_60to80 | UINT | IOD_EP2_TCP | 8011 | 48011 | PMMgal.AlarmPhase[2].C33_42_60to80
EP2PMMgalAlarmPhase2C33_42_over80 | UINT | IOD_EP2_TCP | 8012 | 48012 | PMMgal.AlarmPhase[2].C33_42_over80
EP2PMMgalAlarmPhase3C01_16_60to80 | UINT | IOD_EP2_TCP | 8013 | 48013 | PMMgal.AlarmPhase[3].C01_16_60to80
EP2PMMgalAlarmPhase3C01_16_over80 | UINT | IOD_EP2_TCP | 8014 | 48014 | PMMgal.AlarmPhase[3].C01_16_over80
EP2PMMgalAlarmPhase3C17_32_60to80 | UINT | IOD_EP2_TCP | 8015 | 48015 | PMMgal.AlarmPhase[3].C17_32_60to80
EP2PMMgalAlarmPhase3C17_32_over80 | UINT | IOD_EP2_TCP | 8016 | 48016 | PMMgal.AlarmPhase[3].C17_32_over80
EP2PMMgalAlarmPhase3C33_42_60to80 | UINT | IOD_EP2_TCP | 8017 | 48017 | PMMgal.AlarmPhase[3].C33_42_60to80
EP2PMMgalAlarmPhase3C33_42_over80 | UINT | IOD_EP2_TCP | 8018 | 48018 | PMMgal.AlarmPhase[3].C33_42_over80
EP2PMMgalAlarms | UINT | IOD_EP2_TCP | 8019 | 48019 | PMMgal.Alarms

## variable_new
EP2_AlarmGenCirc1 | DIGITAL | IOD_EP2_TCP | 00001
EP2_AlarmGenComm | DIGITAL | IOD_EP2_TCP | 00002
EP2_AlarmGenDI | DIGITAL | IOD_EP2_TCP | 00003
EP2_AlarmGenKlima5 | DIGITAL | IOD_EP2_TCP | 00004
EP2_AlarmGenKlima6 | DIGITAL | IOD_EP2_TCP | 00005
EP2_AlarmGenPMM1 | DIGITAL | IOD_EP2_TCP | 00006
EP2_AlarmGenPMM2 | DIGITAL | IOD_EP2_TCP | 00007
EP2_AlarmGenPMM3 | DIGITAL | IOD_EP2_TCP | 00008
EP2_AlarmGenUPS1 | DIGITAL | IOD_EP2_TCP | 00009
EP2_AlarmGenUPS2 | DIGITAL | IOD_EP2_TCP | 00010
EP2_Circ1_CosFi_III | REAL | IOD_EP2_TCP | 44001 | -1 | 1 | -1 | 1 |  | ##.##
EP2_Circ1_DelovnaEnergija | REAL | IOD_EP2_TCP | 44003 | 0 | 600 | 0 | 600 | kW | ###.#
EP2_Circ1_DelovnaMoc_III | REAL | IOD_EP2_TCP | 44005 | 0 | 600 | 0 | 600 | kW | ###.#
EP2_Circ1_DelovnaMoc_L1 | REAL | IOD_EP2_TCP | 44007 | 0 | 600 | 0 | 600 | kW | ###.#
EP2_Circ1_DelovnaMoc_L2 | REAL | IOD_EP2_TCP | 44009 | 0 | 600 | 0 | 600 | kW | ###.#
EP2_Circ1_DelovnaMoc_L3 | REAL | IOD_EP2_TCP | 44011 | 0 | 600 | 0 | 600 | kW | ###.#
EP2_Circ1_Frekvenca_L1 | REAL | IOD_EP2_TCP | 44013 | 0 | 60 | 0 | 60 | Hz | ##.#
EP2_Circ1_InduktivnaEnergija | REAL | IOD_EP2_TCP | 44015 | 0 | 600 | 0 | 600 | kW | ###.#
EP2_Circ1_InduktivnaMoc_III | REAL | IOD_EP2_TCP | 44017 | 0 | 600 | 0 | 600 | kVAR | ###.#
EP2_Circ1_JalovaMoc_L1 | REAL | IOD_EP2_TCP | 44019 | 0 | 600 | 0 | 600 | kVAR | ###.#
EP2_Circ1_JalovaMoc_L2 | REAL | IOD_EP2_TCP | 44021 | 0 | 600 | 0 | 600 | kVAR | ###.#
EP2_Circ1_JalovaMoc_L3 | REAL | IOD_EP2_TCP | 44023 | 0 | 600 | 0 | 600 | kVAR | ###.#
EP2_Circ1_KapacitivnaEnergija | REAL | IOD_EP2_TCP | 44025
EP2_Circ1_KapacitivnaMoc_III | REAL | IOD_EP2_TCP | 44027 | 0 | 600 | 0 | 600 | kVAR | ###.#
EP2_Circ1_MaximumDemand | REAL | IOD_EP2_TCP | 44029 | 0 | 1200 | 0 | 1200 | A | ###.#
EP2_Circ1_Napetost_L1_L2 | REAL | IOD_EP2_TCP | 44031 | 0 | 450 | 0 | 450 | V | ###.#
EP2_Circ1_Napetost_L1_N | REAL | IOD_EP2_TCP | 44033 | 0 | 270 | 0 | 270 | V | ###.#
EP2_Circ1_Napetost_L2_L3 | REAL | IOD_EP2_TCP | 44035 | 0 | 450 | 0 | 450 | V | ###.#
EP2_Circ1_Napetost_L2_N | REAL | IOD_EP2_TCP | 44037 | 0 | 270 | 0 | 270 | V | ###.#
EP2_Circ1_Napetost_L3_L1 | REAL | IOD_EP2_TCP | 44039 | 0 | 450 | 0 | 450 | V | ###.#
EP2_Circ1_Napetost_L3_N | REAL | IOD_EP2_TCP | 44041 | 0 | 270 | 0 | 270 | V | ###.#
EP2_Circ1_NavideznaMoc_III | REAL | IOD_EP2_TCP | 44043 | 0 | 1200 | 0 | 1200 | kVA | ###.#
EP2_Circ1_NicelniTok | REAL | IOD_EP2_TCP | 44045 | 0 | 1200 | 0 | 1200 | A | ###.#
EP2_Circ1_PowerFactor_III | REAL | IOD_EP2_TCP | 44047 | -1 | 1 | -1 | 1 |  | ##.##
EP2_Circ1_PowerFactor_L1 | REAL | IOD_EP2_TCP | 44049 | -1 | 1 | -1 | 1 |  | ##.##
EP2_Circ1_PowerFactor_L2 | REAL | IOD_EP2_TCP | 44051 | -1 | 1 | -1 | 1 |  | ##.##
EP2_Circ1_PowerFactor_L3 | REAL | IOD_EP2_TCP | 44053 | -1 | 1 | -1 | 1 |  | ##.##
EP2_Circ1_THDI_L1 | REAL | IOD_EP2_TCP | 44055 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circ1_THDI_L2 | REAL | IOD_EP2_TCP | 44057 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circ1_THDI_L3 | REAL | IOD_EP2_TCP | 44059 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circ1_THDV_L1 | REAL | IOD_EP2_TCP | 44061 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circ1_THDV_L2 | REAL | IOD_EP2_TCP | 44063 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circ1_THDV_L3 | REAL | IOD_EP2_TCP | 44065 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circ1_Tok_L1 | REAL | IOD_EP2_TCP | 44067 | 0 | 600 | 0 | 600 | A | ###.#
EP2_Circ1_Tok_L2 | REAL | IOD_EP2_TCP | 44069 | 0 | 600 | 0 | 600 | A | ###.#
EP2_Circ1_Tok_L3 | REAL | IOD_EP2_TCP | 44071 | 0 | 600 | 0 | 600 | A | ###.#
EP2_Circ1_TokPovprecje_III | REAL | IOD_EP2_TCP | 44073 | 0 | 600 | 0 | 600 | A | ###.#
EP2_Circutor_CosFi_III | REAL | IOD_EP2_TCP | 44075 | -1 | 1 | -1 | 1 |  | ##.##
EP2_Circutor_DelovnaEnergija | REAL | IOD_EP2_TCP | 44077 | 0 | 600 | 0 | 600 | kW | ###.#
EP2_Circutor_DelovnaMoc_III | REAL | IOD_EP2_TCP | 44079 | 0 | 600 | 0 | 600 | kW | ###.#
EP2_Circutor_DelovnaMoc_L1 | REAL | IOD_EP2_TCP | 44081 | 0 | 600 | 0 | 600 | kW | ###.#
EP2_Circutor_DelovnaMoc_L2 | REAL | IOD_EP2_TCP | 44083 | 0 | 600 | 0 | 600 | kW | ###.#
EP2_Circutor_DelovnaMoc_L3 | REAL | IOD_EP2_TCP | 44085 | 0 | 600 | 0 | 600 | kW | ###.#
EP2_Circutor_Frekvenca_L1 | REAL | IOD_EP2_TCP | 44087 | 0 | 60 | 0 | 60 | Hz | ##.#
EP2_Circutor_InduktivnaEnergija | REAL | IOD_EP2_TCP | 44089 | 0 | 600 | 0 | 600 | kW | ###.#
EP2_Circutor_InduktivnaMoc_III | REAL | IOD_EP2_TCP | 44091 | 0 | 600 | 0 | 600 | kVAR | ###.#
EP2_Circutor_JalovaMoc_L1 | REAL | IOD_EP2_TCP | 44093 | 0 | 600 | 0 | 600 | kVAR | ###.#
EP2_Circutor_JalovaMoc_L2 | REAL | IOD_EP2_TCP | 44095 | 0 | 600 | 0 | 600 | kVAR | ###.#
EP2_Circutor_JalovaMoc_L3 | REAL | IOD_EP2_TCP | 44097 | 0 | 600 | 0 | 600 | kVAR | ###.#
EP2_Circutor_KapacitivnaEnergija | REAL | IOD_EP2_TCP | 44099
EP2_Circutor_KapacitivnaMoc_III | REAL | IOD_EP2_TCP | 44101 | 0 | 600 | 0 | 600 | kVAR | ###.#
EP2_Circutor_MaximumDemand | REAL | IOD_EP2_TCP | 44103 | 0 | 1200 | 0 | 1200 | A | ###.#
EP2_Circutor_Napetost_L1_L2 | REAL | IOD_EP2_TCP | 44105 | 0 | 450 | 0 | 450 | V | ###.#
EP2_Circutor_Napetost_L1_N | REAL | IOD_EP2_TCP | 44107 | 0 | 270 | 0 | 270 | V | ###.#
EP2_Circutor_Napetost_L2_L3 | REAL | IOD_EP2_TCP | 44109 | 0 | 450 | 0 | 450 | V | ###.#
EP2_Circutor_Napetost_L2_N | REAL | IOD_EP2_TCP | 44111 | 0 | 270 | 0 | 270 | V | ###.#
EP2_Circutor_Napetost_L3_L1 | REAL | IOD_EP2_TCP | 44113 | 0 | 450 | 0 | 450 | V | ###.#
EP2_Circutor_Napetost_L3_N | REAL | IOD_EP2_TCP | 44115 | 0 | 270 | 0 | 270 | V | ###.#
EP2_Circutor_NavideznaMoc_III | REAL | IOD_EP2_TCP | 44117 | 0 | 1200 | 0 | 1200 | kVA | ###.#
EP2_Circutor_NicelniTok | REAL | IOD_EP2_TCP | 44119 | 0 | 1200 | 0 | 1200 | A | ###.#
EP2_Circutor_PowerFactor_III | REAL | IOD_EP2_TCP | 44121 | -1 | 1 | -1 | 1 |  | ##.##
EP2_Circutor_PowerFactor_L1 | REAL | IOD_EP2_TCP | 44123 | -1 | 1 | -1 | 1 |  | ##.##
EP2_Circutor_PowerFactor_L2 | REAL | IOD_EP2_TCP | 44125 | -1 | 1 | -1 | 1 |  | ##.##
EP2_Circutor_PowerFactor_L3 | REAL | IOD_EP2_TCP | 44127 | -1 | 1 | -1 | 1 |  | ##.##
EP2_Circutor_THDI_L1 | REAL | IOD_EP2_TCP | 44129 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circutor_THDI_L2 | REAL | IOD_EP2_TCP | 44131 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circutor_THDI_L3 | REAL | IOD_EP2_TCP | 44133 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circutor_THDV_L1 | REAL | IOD_EP2_TCP | 44135 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circutor_THDV_L2 | REAL | IOD_EP2_TCP | 44137 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circutor_THDV_L3 | REAL | IOD_EP2_TCP | 44139 | 0 | 10 | 0 | 10 | % | ###.#
EP2_Circutor_Tok_L1 | REAL | IOD_EP2_TCP | 44141 | 0 | 600 | 0 | 600 | A | ###.#
EP2_Circutor_Tok_L2 | REAL | IOD_EP2_TCP | 44143 | 0 | 600 | 0 | 600 | A | ###.#
EP2_Circutor_Tok_L3 | REAL | IOD_EP2_TCP | 44145 | 0 | 600 | 0 | 600 | A | ###.#
EP2_Circutor_TokPovprecje_III | REAL | IOD_EP2_TCP | 44147 | 0 | 600 | 0 | 600 | A | ###.#
EP2_ComSCADA | DIGITAL | IOD_EP2_TCP | 00011
EP2_ComSCADA1 | DIGITAL | IOD_EP2_TCP | 00012
EP2_DateTime_Dan | INT | IOD_EP2_TCP | 40001
EP2_DateTime_Leto | INT | IOD_EP2_TCP | 40002
EP2_DateTime_Mesec | INT | IOD_EP2_TCP | 40003
EP2_DateTime_Minuta | INT | IOD_EP2_TCP | 40004
EP2_DateTime_Sekunda | INT | IOD_EP2_TCP | 40005
EP2_DateTime_Ura | INT | IOD_EP2_TCP | 40006
EP2_DI_Klima5_ERR | DIGITAL | IOD_EP2_TCP | 00013
EP2_DI_Klima5_ON | DIGITAL | IOD_EP2_TCP | 00014
EP2_DI_Klima6_ERR | DIGITAL | IOD_EP2_TCP | 00015
EP2_DI_Klima6_ON | DIGITAL | IOD_EP2_TCP | 00016
EP2_DI_KlimaSplit1_ERR | DIGITAL | IOD_EP2_TCP | 00017
EP2_DI_KlimaSplit1_ON | DIGITAL | IOD_EP2_TCP | 00018
EP2_DI_Q10_OdcKlima6_IZP | DIGITAL | IOD_EP2_TCP | 00019
EP2_DI_Q10_OdcKlima6_ON | DIGITAL | IOD_EP2_TCP | 00020
EP2_DI_Q11_OdcVent1_ON | DIGITAL | IOD_EP2_TCP | 00021
EP2_DI_Q12_Rezerva_ON | DIGITAL | IOD_EP2_TCP | 00022
EP2_DI_Q1_GlavnoStikalo_ON | DIGITAL | IOD_EP2_TCP | 00023
EP2_DI_Q25_OdcUpsA_IZP | DIGITAL | IOD_EP2_TCP | 00024
EP2_DI_Q25_OdcUpsA_ON | DIGITAL | IOD_EP2_TCP | 00025
EP2_DI_Q26_OdcByA_IZP | DIGITAL | IOD_EP2_TCP | 00026
EP2_DI_Q26_OdcByA_ON | DIGITAL | IOD_EP2_TCP | 00027
EP2_DI_Q27_OdcByUpsA_IZP | DIGITAL | IOD_EP2_TCP | 00028
EP2_DI_Q27_OdcByUpsA_ON | DIGITAL | IOD_EP2_TCP | 00029
EP2_DI_Q28_OdcUpsB_IZP | DIGITAL | IOD_EP2_TCP | 00030
EP2_DI_Q28_OdcUpsB_ON | DIGITAL | IOD_EP2_TCP | 00031
EP2_DI_Q29_OdcByB_IZP | DIGITAL | IOD_EP2_TCP | 00032
EP2_DI_Q29_OdcByB_ON | DIGITAL | IOD_EP2_TCP | 00033
EP2_DI_Q2_Rezerva_IZP | DIGITAL | IOD_EP2_TCP | 00034
EP2_DI_Q2_Rezerva_ON | DIGITAL | IOD_EP2_TCP | 00035
EP2_DI_Q30_OdcByUpsB_IZP | DIGITAL | IOD_EP2_TCP | 00036
EP2_DI_Q30_OdcByUpsB_ON | DIGITAL | IOD_EP2_TCP | 00037
EP2_DI_Q31_DovByUpsA_ON | DIGITAL | IOD_EP2_TCP | 00038
EP2_DI_Q32_DovByA_ON | DIGITAL | IOD_EP2_TCP | 00039
EP2_DI_Q33_DovByUpsB_ON | DIGITAL | IOD_EP2_TCP | 00040
EP2_DI_Q34_DovByB_ON | DIGITAL | IOD_EP2_TCP | 00041
EP2_DI_Q5_OdcKlima1_IZP | DIGITAL | IOD_EP2_TCP | 00042
EP2_DI_Q5_OdcKlima1_ON | DIGITAL | IOD_EP2_TCP | 00043
EP2_DI_Q6_OdcKlima2_IZP | DIGITAL | IOD_EP2_TCP | 00044
EP2_DI_Q6_OdcKlima2_ON | DIGITAL | IOD_EP2_TCP | 00045
EP2_DI_Q7_OdcKlima3_IZP | DIGITAL | IOD_EP2_TCP | 00046
EP2_DI_Q7_OdcKlima3_ON | DIGITAL | IOD_EP2_TCP | 00047
EP2_DI_Q8_OdcKlima4_IZP | DIGITAL | IOD_EP2_TCP | 00048
EP2_DI_Q8_OdcKlima4_ON | DIGITAL | IOD_EP2_TCP | 00049
EP2_DI_Q9_OdcKlima5_IZP | DIGITAL | IOD_EP2_TCP | 00050
EP2_DI_Q9_OdcKlima5_ON | DIGITAL | IOD_EP2_TCP | 00051
EP2_DI_RazlitjeVodeK5K6 | DIGITAL | IOD_EP2_TCP | 00052
EP2_DI_UPS_Alarm | DIGITAL | IOD_EP2_TCP | 00053
EP2_DI_UPS_BatNacin | DIGITAL | IOD_EP2_TCP | 00054
EP2_DI_UPS_Polnjenje | DIGITAL | IOD_EP2_TCP | 00055
EP2_DI_UpsA_ERR | DIGITAL | IOD_EP2_TCP | 00056
EP2_DI_UpsA_ON | DIGITAL | IOD_EP2_TCP | 00057
EP2_DI_UpsB_ERR | DIGITAL | IOD_EP2_TCP | 00058
EP2_DI_UpsB_ON | DIGITAL | IOD_EP2_TCP | 00059
EP2_DO_Klima5_Izklop | DIGITAL | IOD_EP2_TCP | 00060
EP2_DO_Klima6_Izklop | DIGITAL | IOD_EP2_TCP | 00061
EP2_ErrComCirc1 | DIGITAL | IOD_EP2_TCP | 00062
EP2_ErrComCirc2 | DIGITAL | IOD_EP2_TCP | 00063
EP2_ErrComCirc3 | DIGITAL | IOD_EP2_TCP | 00064
EP2_ErrComCirc4 | DIGITAL | IOD_EP2_TCP | 00065
EP2_ErrComCirc5 | DIGITAL | IOD_EP2_TCP | 00066
EP2_ErrComKlima1 | DIGITAL | IOD_EP2_TCP | 00067
EP2_ErrComKlima2 | DIGITAL | IOD_EP2_TCP | 00068
EP2_ErrComKlima3 | DIGITAL | IOD_EP2_TCP | 00069
EP2_ErrComKlima4 | DIGITAL | IOD_EP2_TCP | 00070
EP2_ErrComKlima5 | DIGITAL | IOD_EP2_TCP | 00071
EP2_ErrComKlima6 | DIGITAL | IOD_EP2_TCP | 00072
EP2_ErrCommScada | DIGITAL | IOD_EP2_TCP | 00073
EP2_ErrComPanelPLC | DIGITAL | IOD_EP2_TCP | 00074
EP2_ErrComPMM1 | DIGITAL | IOD_EP2_TCP | 00075
EP2_ErrComPMM2 | DIGITAL | IOD_EP2_TCP | 00076
EP2_ErrComPMM3 | DIGITAL | IOD_EP2_TCP | 00077
EP2_ErrComPort2 | DIGITAL | IOD_EP2_TCP | 00078
EP2_ErrComPort3 | DIGITAL | IOD_EP2_TCP | 00079
EP2_ErrComPort4 | DIGITAL | IOD_EP2_TCP | 00080
EP2_ErrComUPS1 | DIGITAL | IOD_EP2_TCP | 00081
EP2_ErrComUPS2 | DIGITAL | IOD_EP2_TCP | 00082
EP2_Klima1_AlarmKompresor1 | DIGITAL | IOD_EP2_TCP | 00083
EP2_Klima1_AlarmKompresor2 | DIGITAL | IOD_EP2_TCP | 00084
EP2_Klima1_Deluje | DIGITAL | IOD_EP2_TCP | 00085
EP2_Klima1_EnergySaving | DIGITAL | IOD_EP2_TCP | 00086
EP2_Klima1_FaultyEPROM | DIGITAL | IOD_EP2_TCP | 00087
EP2_Klima1_FenThermalCutout | DIGITAL | IOD_EP2_TCP | 00088
EP2_Klima1_GeneralAlarm | DIGITAL | IOD_EP2_TCP | 00089
EP2_Klima1_GrelecStatus | INT | IOD_EP2_TCP | 40007
EP2_Klima1_IzhodniVentStatus | INT | IOD_EP2_TCP | 40008
EP2_Klima1_Kompresor1naMejiObrUr | DIGITAL | IOD_EP2_TCP | 00090
EP2_Klima1_Kompresor2naMejiObrUr | DIGITAL | IOD_EP2_TCP | 00091
EP2_Klima1_KompresorStatus | INT | IOD_EP2_TCP | 40009
EP2_Klima1_Napaka | DIGITAL | IOD_EP2_TCP | 00092
EP2_Klima1_NapakaPriPretokuZraka | DIGITAL | IOD_EP2_TCP | 00093
EP2_Klima1_NapakaSenzorPovratVod | DIGITAL | IOD_EP2_TCP | 00094
EP2_Klima1_NapakaSenzorTempIzpih | DIGITAL | IOD_EP2_TCP | 00095
EP2_Klima1_NapakaSenzorTempProst | DIGITAL | IOD_EP2_TCP | 00096
EP2_Klima1_NapakaSenzorVlaznosti | DIGITAL | IOD_EP2_TCP | 00097
EP2_Klima1_NapakaSenzorZunanjeTemp | DIGITAL | IOD_EP2_TCP | 00098
EP2_Klima1_NastMaxTemp | REAL | IOD_EP2_TCP | 44149 | 0 | 60 | 0 | 60 | °C | ##.#
EP2_Klima1_NastMaxVlaznost | REAL | IOD_EP2_TCP | 44151 | 0 | 100 | 0 | 100 | % | ##.#
EP2_Klima1_NastMinTemp | REAL | IOD_EP2_TCP | 44153 | 0 | 60 | 0 | 60 | °C | ##.#
EP2_Klima1_NastMinVlaznost | REAL | IOD_EP2_TCP | 44155 | 0 | 100 | 0 | 100 | % | ##.#
EP2_Klima1_NastTempProstora | REAL | IOD_EP2_TCP | 44157 | 0 | 60 | 0 | 60 | °C | ##.#
EP2_Klima1_NastVlaznost | REAL | IOD_EP2_TCP | 44159 | 0 | 100 | 0 | 100 | % | ##.#
EP2_Klima1_NiTokaVVlazilcu | DIGITAL | IOD_EP2_TCP | 00099
EP2_Klima1_NiVodeVVlazilcu | DIGITAL | IOD_EP2_TCP | 00100
EP2_Klima1_NizekPritiskKompresor1 | DIGITAL | IOD_EP2_TCP | 00101
EP2_Klima1_NizekPritiskKompresor2 | DIGITAL | IOD_EP2_TCP | 00102
EP2_Klima1_NizkaTempPovratneVode | DIGITAL | IOD_EP2_TCP | 00103
EP2_Klima1_NizkaTempVProstoru | DIGITAL | IOD_EP2_TCP | 00104
EP2_Klima1_NizkaVlaznost | DIGITAL | IOD_EP2_TCP | 00105
EP2_Klima1_ObratovalneUre | REAL | IOD_EP2_TCP | 44161
EP2_Klima1_OnOffEnablingBySupervisor | DIGITAL | IOD_EP2_TCP | 00106
EP2_Klima1_PozarniAlarm | DIGITAL | IOD_EP2_TCP | 00107
EP2_Klima1_Razvlazevanje | DIGITAL | IOD_EP2_TCP | 00108
EP2_Klima1_RemoteOFFtoOutput | DIGITAL | IOD_EP2_TCP | 00109
EP2_Klima1_RemoteOnOff | DIGITAL | IOD_EP2_TCP | 00110
EP2_Klima1_RocniIzklop | DIGITAL | IOD_EP2_TCP | 00111
EP2_Klima1_SenzorjiStatus | DIGITAL | IOD_EP2_TCP | 00112
EP2_Klima1_StoppedByAlarms | DIGITAL | IOD_EP2_TCP | 00113
EP2_Klima1_TemperaturaProstora | REAL | IOD_EP2_TCP | 44163 | 0 | 60 | 0 | 60 | °C | ##.#
EP2_Klima1_TempIzpihanegaZraka | REAL | IOD_EP2_TCP | 44165 | 0 | 60 | 0 | 60 | °C | ##.#
EP2_Klima1_TempPovratneVode | REAL | IOD_EP2_TCP | 44167 | 0 | 60 | 0 | 60 | °C | ##.#
EP2_Klima1_ThermalCutoutHeater1 | DIGITAL | IOD_EP2_TCP | 00114
EP2_Klima1_ThermalCutoutHeater2 | DIGITAL | IOD_EP2_TCP | 00115
EP2_Klima1_UnitOnOff | DIGITAL | IOD_EP2_TCP | 00116
EP2_Klima1_VentilatorNaMejiObrUr | DIGITAL | IOD_EP2_TCP | 00117
EP2_Klima1_VentilGretjeOdpiranje | DIGITAL | IOD_EP2_TCP | 00118
EP2_Klima1_VentilGretjeZapiranje | DIGITAL | IOD_EP2_TCP | 00119
EP2_Klima1_VentilHlajenjeOdpiranje | DIGITAL | IOD_EP2_TCP | 00120
EP2_Klima1_VentilHlajenjeZapiranje | DIGITAL | IOD_EP2_TCP | 00121
EP2_Klima1_VisokaTempPovratneVode | DIGITAL | IOD_EP2_TCP | 00122
EP2_Klima1_VisokaTempVProstoru | DIGITAL | IOD_EP2_TCP | 00123
EP2_Klima1_VisokaVlaznost | DIGITAL | IOD_EP2_TCP | 00124
EP2_Klima1_VisokTokVVlazilcu | DIGITAL | IOD_EP2_TCP | 00125
EP2_Klima1_Vlazenje | DIGITAL | IOD_EP2_TCP | 00126
EP2_Klima1_VlazilecStatus | INT | IOD_EP2_TCP | 40010
EP2_Klima1_VlaznostProstora | REAL | IOD_EP2_TCP | 44169 | 0 | 100 | 0 | 100 | % | ##.#
EP2_Klima1_ZamasenFilter | DIGITAL | IOD_EP2_TCP | 00127
EP2_Klima1_ZunanjaTemp | REAL | IOD_EP2_TCP | 44171
EP2_Klima2_AlarmKompresor1 | DIGITAL | IOD_EP2_TCP | 00128
EP2_Klima2_AlarmKompresor2 | DIGITAL | IOD_EP2_TCP | 00129
EP2_Klima2_Deluje | DIGITAL | IOD_EP2_TCP | 00130
EP2_Klima2_EnergySaving | DIGITAL | IOD_EP2_TCP | 00131
EP2_Klima2_FaultyEPROM | DIGITAL | IOD_EP2_TCP | 00132
EP2_Klima2_FenThermalCutout | DIGITAL | IOD_EP2_TCP | 00133
EP2_Klima2_GeneralAlarm | DIGITAL | IOD_EP2_TCP | 00134
EP2_Klima2_GrelecStatus | INT | IOD_EP2_TCP | 40011
EP2_Klima2_IzhodniVentStatus | INT | IOD_EP2_TCP | 40012
EP2_Klima2_Kompresor1naMejiObrUr | DIGITAL | IOD_EP2_TCP | 00135
EP2_Klima2_Kompresor2naMejiObrUr | DIGITAL | IOD_EP2_TCP | 00136
EP2_Klima2_KompresorStatus | INT | IOD_EP2_TCP | 40013
EP2_Klima2_Napaka | DIGITAL | IOD_EP2_TCP | 00137
EP2_Klima2_NapakaPriPretokuZraka | DIGITAL | IOD_EP2_TCP | 00138
EP2_Klima2_NapakaSenzorPovratVode | DIGITAL | IOD_EP2_TCP | 00139
EP2_Klima2_NapakaSenzorTempIzpih | DIGITAL | IOD_EP2_TCP | 00140
EP2_Klima2_NapakaSenzorTempProst | DIGITAL | IOD_EP2_TCP | 00141
EP2_Klima2_NapakaSenzorVlaznosti | DIGITAL | IOD_EP2_TCP | 00142
EP2_Klima2_NapakaSenzorZunanjeTemp | DIGITAL | IOD_EP2_TCP | 00143
EP2_Klima2_NastMaxTemp | REAL | IOD_EP2_TCP | 44173 | 0 | 60 | 0 | 60 | °C | ##.#
EP2_Klima2_NastMaxVlaznost | REAL | IOD_EP2_TCP | 44175 | 0 | 100 | 0 | 100 | % | ##.#
EP2_Klima2_NastMinTemp | REAL | IOD_EP2_TCP | 44177 | 0 | 60 | 0 | 60 | °C | ##.#
EP2_Klima2_NastMinVlaznost | REAL | IOD_EP2_TCP | 44179 | 0 | 100 | 0 | 100 | % | ##.#
EP2_Klima2_NastTempProstora | REAL | IOD_EP2_TCP | 44181 | 0 | 60 | 0 | 60 | °C | ##.#
EP2_Klima2_NastVlaznost | REAL | IOD_EP2_TCP | 44183 | 0 | 100 | 0 | 100 | % | ##.#
EP2_Klima2_NiTokaVVlazilcu | DIGITAL | IOD_EP2_TCP | 00144
EP2_Klima2_NiVodeVVlazilcu | DIGITAL | IOD_EP2_TCP | 00145
EP2_Klima2_NizekPritiskKompresor1 | DIGITAL | IOD_EP2_TCP | 00146
EP2_Klima2_NizekPritiskKompresor2 | DIGITAL | IOD_EP2_TCP | 00147
EP2_Klima2_NizkaTempPovratneVode | DIGITAL | IOD_EP2_TCP | 00148
EP2_Klima2_NizkaTempVProstoru | DIGITAL | IOD_EP2_TCP | 00149
EP2_Klima2_NizkaVlaznost | DIGITAL | IOD_EP2_TCP | 00150
EP2_Klima2_ObratovalneUre | REAL | IOD_EP2_TCP | 44185
EP2_Klima2_OnOffEnablingBySupervisor | DIGITAL | IOD_EP2_TCP | 00151
EP2_Klima2_PozarniAlarm | DIGITAL | IOD_EP2_TCP | 00152
EP2_Klima2_Razvlazevanje | DIGITAL | IOD_EP2_TCP | 00153
EP2_Klima2_RemoteOFFtoOutput | DIGITAL | IOD_EP2_TCP | 00154
EP2_Klima2_RemoteOnOff | DIGITAL | IOD_EP2_TCP | 00155
EP2_Klima2_RocniIzklop | DIGITAL | IOD_EP2_TCP | 00156
EP2_Klima2_SenzorjiStatus | DIGITAL | IOD_EP2_TCP | 00157
EP2_Klima2_StoppedByAlarms | DIGITAL | IOD_EP2_TCP | 00158
EP2_Klima2_TemperaturaProstora | REAL | IOD_EP2_TCP | 44187 | 0 | 60 | 0 | 60 | °C | ##.#
EP2_Klima2_TempIzpihanegaZraka | REAL | IOD_EP2_TCP | 44189 | 0 | 60 | 0 | 60 | °C | ##.#
EP2_Klima2_TempPovratneVode | REAL | IOD_EP2_TCP | 44191 | 0 | 60 | 0 | 60 | °C | ##.#
EP2_Klima2_ThermalCutoutHeater1 | DIGITAL | IOD_EP2_TCP | 00159
EP2_Klima2_ThermalCutoutHeater2 | DIGITAL | IOD_EP2_TCP | 00160
EP2_Klima2_UnitOnOff | DIGITAL | IOD_EP2_TCP | 00161
EP2_Klima2_VentilatorNaMejiObrUr | DIGITAL | IOD_EP2_TCP | 00162
EP2_Klima2_VentilGretjeOdpiranje | DIGITAL | IOD_EP2_TCP | 00163
EP2_Klima2_VentilGretjeZapiranje | DIGITAL | IOD_EP2_TCP | 00164
EP2_Klima2_VentilHlajenjeOdpiranje | DIGITAL | IOD_EP2_TCP | 00165
EP2_Klima2_VentilHlajenjeZapiranje | DIGITAL | IOD_EP2_TCP | 00166
EP2_Klima2_VisokaTempPovratneVod | DIGITAL | IOD_EP2_TCP | 00167
EP2_Klima2_VisokaTempVProstoru | DIGITAL | IOD_EP2_TCP | 00168
EP2_Klima2_VisokaVlaznost | DIGITAL | IOD_EP2_TCP | 00169
EP2_Klima2_VisokTokVVlazilcu | DIGITAL | IOD_EP2_TCP | 00170
EP2_Klima2_Vlazenje | DIGITAL | IOD_EP2_TCP | 00171
EP2_Klima2_VlazilecStatus | INT | IOD_EP2_TCP | 40014
EP2_Klima2_VlaznostProstora | REAL | IOD_EP2_TCP | 44193 | 0 | 100 | 0 | 100 | % | ##.#
EP2_Klima2_ZamasenFilter | DIGITAL | IOD_EP2_TCP | 00172
EP2_Klima2_ZunanjaTemp | REAL | IOD_EP2_TCP | 44195
EP2_KlimeNaCas | DIGITAL | IOD_EP2_TCP | 00173
EP2_NapakaSenzorTemp1 | DIGITAL | IOD_EP2_TCP | 00174
EP2_NapakaSenzorTemp2 | DIGITAL | IOD_EP2_TCP | 00175
EP2_NapakaSenzorVlaga1 | DIGITAL | IOD_EP2_TCP | 00176
EP2_NapakaSenzorVlaga2 | DIGITAL | IOD_EP2_TCP | 00177
EP2_PMM1OverCurrentBetw1 | DIGITAL | IOD_EP2_TCP | 00178
EP2_PMM1OverCurrentBetw2 | DIGITAL | IOD_EP2_TCP | 00179
EP2_PMM1OverCurrentBetw3 | DIGITAL | IOD_EP2_TCP | 00180
EP2_PMM1OverCurrentOver1 | DIGITAL | IOD_EP2_TCP | 00181
EP2_PMM1OverCurrentOver2 | DIGITAL | IOD_EP2_TCP | 00182
EP2_PMM1OverCurrentOver3 | DIGITAL | IOD_EP2_TCP | 00183
EP2_PMM2OverCurrentBetw1 | DIGITAL | IOD_EP2_TCP | 00184
EP2_PMM2OverCurrentBetw2 | DIGITAL | IOD_EP2_TCP | 00185
EP2_PMM2OverCurrentBetw3 | DIGITAL | IOD_EP2_TCP | 00186
EP2_PMM2OverCurrentOver1 | DIGITAL | IOD_EP2_TCP | 00187
EP2_PMM2OverCurrentOver2 | DIGITAL | IOD_EP2_TCP | 00188
EP2_PMM2OverCurrentOver3 | DIGITAL | IOD_EP2_TCP | 00189
EP2_PMM3OverCurrentBetw1 | DIGITAL | IOD_EP2_TCP | 00190
EP2_PMM3OverCurrentBetw2 | DIGITAL | IOD_EP2_TCP | 00191
EP2_PMM3OverCurrentBetw3 | DIGITAL | IOD_EP2_TCP | 00192
EP2_PMM3OverCurrentOver1 | DIGITAL | IOD_EP2_TCP | 00193
EP2_PMM3OverCurrentOver2 | DIGITAL | IOD_EP2_TCP | 00194
EP2_PMM3OverCurrentOver3 | DIGITAL | IOD_EP2_TCP | 00195
EP2_PMM1_ActivePowerPhaseA_kW | REAL | IOD_EP2_TCP | 44197 | [5 empty] | ###.#
EP2_PMM1_ActivePowerPhaseB_kW | REAL | IOD_EP2_TCP | 44199 | [5 empty] | ###.#
EP2_PMM1_ActivePowerPhaseC_kW | REAL | IOD_EP2_TCP | 44201 | [5 empty] | ###.#
EP2_PMM1_AlarmPhase1_C01_16_60to | INT | IOD_EP2_TCP | 40015
EP2_PMM1_AlarmPhase1_C01_16_over | INT | IOD_EP2_TCP | 40016
EP2_PMM1_AlarmPhase1_C17_32_60to | INT | IOD_EP2_TCP | 40017
EP2_PMM1_AlarmPhase1_C17_32_over | INT | IOD_EP2_TCP | 40018
EP2_PMM1_AlarmPhase1_C33_42_60to | INT | IOD_EP2_TCP | 40019
EP2_PMM1_AlarmPhase1_C33_42_over | INT | IOD_EP2_TCP | 40020
EP2_PMM1_AlarmPhase1_GlobalAlarm | INT | IOD_EP2_TCP | 40021
EP2_PMM1_AlarmPhase2_C01_16_60to | INT | IOD_EP2_TCP | 40022
EP2_PMM1_AlarmPhase2_C01_16_over | INT | IOD_EP2_TCP | 40023
EP2_PMM1_AlarmPhase2_C17_32_60to | INT | IOD_EP2_TCP | 40024
EP2_PMM1_AlarmPhase2_C17_32_over | INT | IOD_EP2_TCP | 40025
EP2_PMM1_AlarmPhase2_C33_42_60to | INT | IOD_EP2_TCP | 40026
EP2_PMM1_AlarmPhase2_C33_42_over | INT | IOD_EP2_TCP | 40027
EP2_PMM1_AlarmPhase2_GlobalAlarm | INT | IOD_EP2_TCP | 40028
EP2_PMM1_AlarmPhase3_C01_16_60to | INT | IOD_EP2_TCP | 40029
EP2_PMM1_AlarmPhase3_C01_16_over | INT | IOD_EP2_TCP | 40030
EP2_PMM1_AlarmPhase3_C17_32_60to | INT | IOD_EP2_TCP | 40031
EP2_PMM1_AlarmPhase3_C17_32_over | INT | IOD_EP2_TCP | 40032
EP2_PMM1_AlarmPhase3_C33_42_60to | INT | IOD_EP2_TCP | 40033
EP2_PMM1_AlarmPhase3_C33_42_over | INT | IOD_EP2_TCP | 40034
EP2_PMM1_AlarmPhase3_GlobalAlarm | INT | IOD_EP2_TCP | 40035
EP2_PMM1_Alarms | INT | IOD_EP2_TCP | 40036
EP2_PMM1_AverageCurrent_A | REAL | IOD_EP2_TCP | 44203 | [5 empty] | ###.#
EP2_PMM1_AveragePhaseToNeutral_V | REAL | IOD_EP2_TCP | 44205 | [5 empty] | ###.#
EP2_PMM1_AveragePhaseToPhase_V | REAL | IOD_EP2_TCP | 44207 | [5 empty] | ###.#
EP2_PMM1_CurrentInPhaseA_A | REAL | IOD_EP2_TCP | 44209 | [5 empty] | ###.#
EP2_PMM1_CurrentInPhaseB_A | REAL | IOD_EP2_TCP | 44211 | [5 empty] | ###.#
EP2_PMM1_CurrentInPhaseC_A | REAL | IOD_EP2_TCP | 44213 | [5 empty] | ###.#
EP2_PMM1_EnergyConsumed_kWh | REAL | IOD_EP2_TCP | 44215 | [5 empty] | ###.#
EP2_PMM1_Napaka | DIGITAL | IOD_EP2_TCP | 00196
EP2_PMM1_Frequency_Hz | REAL | IOD_EP2_TCP | 44217 | [5 empty] | ###.#
EP2_PMM1_NeutralCurrent_A | REAL | IOD_EP2_TCP | 44219 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current10 | REAL | IOD_EP2_TCP | 44221 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current11 | REAL | IOD_EP2_TCP | 44223 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current12 | REAL | IOD_EP2_TCP | 44225 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current13 | REAL | IOD_EP2_TCP | 44227 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current14 | REAL | IOD_EP2_TCP | 44229 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current15 | REAL | IOD_EP2_TCP | 44231 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current16 | REAL | IOD_EP2_TCP | 44233 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current17 | REAL | IOD_EP2_TCP | 44235 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current18 | REAL | IOD_EP2_TCP | 44237 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current19 | REAL | IOD_EP2_TCP | 44239 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current1 | REAL | IOD_EP2_TCP | 44241 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current20 | REAL | IOD_EP2_TCP | 44243 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current21 | REAL | IOD_EP2_TCP | 44245 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current22 | REAL | IOD_EP2_TCP | 44247 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current23 | REAL | IOD_EP2_TCP | 44249 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current24 | REAL | IOD_EP2_TCP | 44251 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current25 | REAL | IOD_EP2_TCP | 44253 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current26 | REAL | IOD_EP2_TCP | 44255 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current27 | REAL | IOD_EP2_TCP | 44257 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current28 | REAL | IOD_EP2_TCP | 44259 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current29 | REAL | IOD_EP2_TCP | 44261 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current2 | REAL | IOD_EP2_TCP | 44263 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current30 | REAL | IOD_EP2_TCP | 44265 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current31 | REAL | IOD_EP2_TCP | 44267 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current32 | REAL | IOD_EP2_TCP | 44269 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current33 | REAL | IOD_EP2_TCP | 44271 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current34 | REAL | IOD_EP2_TCP | 44273 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current35 | REAL | IOD_EP2_TCP | 44275 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current36 | REAL | IOD_EP2_TCP | 44277 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current37 | REAL | IOD_EP2_TCP | 44279 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current38 | REAL | IOD_EP2_TCP | 44281 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current39 | REAL | IOD_EP2_TCP | 44283 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current3 | REAL | IOD_EP2_TCP | 44285 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current40 | REAL | IOD_EP2_TCP | 44287 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current41 | REAL | IOD_EP2_TCP | 44289 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current42 | REAL | IOD_EP2_TCP | 44291 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current4 | REAL | IOD_EP2_TCP | 44293 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current5 | REAL | IOD_EP2_TCP | 44295 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current6 | REAL | IOD_EP2_TCP | 44297 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current7 | REAL | IOD_EP2_TCP | 44299 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current8 | REAL | IOD_EP2_TCP | 44301 | [5 empty] | ###.#
EP2_PMM1_Phase1_Current9 | REAL | IOD_EP2_TCP | 44303 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current10 | REAL | IOD_EP2_TCP | 44305 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current11 | REAL | IOD_EP2_TCP | 44307 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current12 | REAL | IOD_EP2_TCP | 44309 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current13 | REAL | IOD_EP2_TCP | 44311 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current14 | REAL | IOD_EP2_TCP | 44313 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current15 | REAL | IOD_EP2_TCP | 44315 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current16 | REAL | IOD_EP2_TCP | 44317 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current17 | REAL | IOD_EP2_TCP | 44319 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current18 | REAL | IOD_EP2_TCP | 44321 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current19 | REAL | IOD_EP2_TCP | 44323 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current1 | REAL | IOD_EP2_TCP | 44325 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current20 | REAL | IOD_EP2_TCP | 44327 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current21 | REAL | IOD_EP2_TCP | 44329 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current22 | REAL | IOD_EP2_TCP | 44331 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current23 | REAL | IOD_EP2_TCP | 44333 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current24 | REAL | IOD_EP2_TCP | 44335 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current25 | REAL | IOD_EP2_TCP | 44337 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current26 | REAL | IOD_EP2_TCP | 44339 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current27 | REAL | IOD_EP2_TCP | 44341 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current28 | REAL | IOD_EP2_TCP | 44343 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current29 | REAL | IOD_EP2_TCP | 44345 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current2 | REAL | IOD_EP2_TCP | 44347 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current30 | REAL | IOD_EP2_TCP | 44349 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current31 | REAL | IOD_EP2_TCP | 44351 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current32 | REAL | IOD_EP2_TCP | 44353 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current33 | REAL | IOD_EP2_TCP | 44355 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current34 | REAL | IOD_EP2_TCP | 44357 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current35 | REAL | IOD_EP2_TCP | 44359 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current36 | REAL | IOD_EP2_TCP | 44361 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current37 | REAL | IOD_EP2_TCP | 44363 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current38 | REAL | IOD_EP2_TCP | 44365 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current39 | REAL | IOD_EP2_TCP | 44367 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current3 | REAL | IOD_EP2_TCP | 44369 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current40 | REAL | IOD_EP2_TCP | 44371 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current41 | REAL | IOD_EP2_TCP | 44373 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current42 | REAL | IOD_EP2_TCP | 44375 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current4 | REAL | IOD_EP2_TCP | 44377 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current5 | REAL | IOD_EP2_TCP | 44379 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current6 | REAL | IOD_EP2_TCP | 44381 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current7 | REAL | IOD_EP2_TCP | 44383 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current8 | REAL | IOD_EP2_TCP | 44385 | [5 empty] | ###.#
EP2_PMM1_Phase2_Current9 | REAL | IOD_EP2_TCP | 44387 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current10 | REAL | IOD_EP2_TCP | 44389 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current11 | REAL | IOD_EP2_TCP | 44391 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current12 | REAL | IOD_EP2_TCP | 44393 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current13 | REAL | IOD_EP2_TCP | 44395 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current14 | REAL | IOD_EP2_TCP | 44397 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current15 | REAL | IOD_EP2_TCP | 44399 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current16 | REAL | IOD_EP2_TCP | 44401 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current17 | REAL | IOD_EP2_TCP | 44403 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current18 | REAL | IOD_EP2_TCP | 44405 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current19 | REAL | IOD_EP2_TCP | 44407 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current1 | REAL | IOD_EP2_TCP | 44409 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current20 | REAL | IOD_EP2_TCP | 44411 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current21 | REAL | IOD_EP2_TCP | 44413 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current22 | REAL | IOD_EP2_TCP | 44415 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current23 | REAL | IOD_EP2_TCP | 44417 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current24 | REAL | IOD_EP2_TCP | 44419 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current25 | REAL | IOD_EP2_TCP | 44421 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current26 | REAL | IOD_EP2_TCP | 44423 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current27 | REAL | IOD_EP2_TCP | 44425 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current28 | REAL | IOD_EP2_TCP | 44427 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current29 | REAL | IOD_EP2_TCP | 44429 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current2 | REAL | IOD_EP2_TCP | 44431 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current30 | REAL | IOD_EP2_TCP | 44433 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current31 | REAL | IOD_EP2_TCP | 44435 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current32 | REAL | IOD_EP2_TCP | 44437 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current33 | REAL | IOD_EP2_TCP | 44439 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current34 | REAL | IOD_EP2_TCP | 44441 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current35 | REAL | IOD_EP2_TCP | 44443 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current36 | REAL | IOD_EP2_TCP | 44445 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current37 | REAL | IOD_EP2_TCP | 44447 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current38 | REAL | IOD_EP2_TCP | 44449 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current39 | REAL | IOD_EP2_TCP | 44451 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current3 | REAL | IOD_EP2_TCP | 44453 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current40 | REAL | IOD_EP2_TCP | 44455 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current41 | REAL | IOD_EP2_TCP | 44457 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current42 | REAL | IOD_EP2_TCP | 44459 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current4 | REAL | IOD_EP2_TCP | 44461 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current5 | REAL | IOD_EP2_TCP | 44463 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current6 | REAL | IOD_EP2_TCP | 44465 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current7 | REAL | IOD_EP2_TCP | 44467 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current8 | REAL | IOD_EP2_TCP | 44469 | [5 empty] | ###.#
EP2_PMM1_Phase3_Current9 | REAL | IOD_EP2_TCP | 44471 | [5 empty] | ###.#
EP2_PMM1_PowerFactorPhaseA | REAL | IOD_EP2_TCP | 44473 | [5 empty] | ###.#
EP2_PMM1_PowerFactorPhaseB | REAL | IOD_EP2_TCP | 44475 | [5 empty] | ###.#
EP2_PMM1_PowerFactorPhaseC | REAL | IOD_EP2_TCP | 44477 | [5 empty] | ###.#
EP2_PMM1_TotalActivePower_kW | REAL | IOD_EP2_TCP | 44479 | [5 empty] | ###.#
EP2_PMM1_TotalAparentPower_kVA | REAL | IOD_EP2_TCP | 44481 | [5 empty] | ###.#
EP2_PMM1_TotalPowerFactor | REAL | IOD_EP2_TCP | 44483 | [5 empty] | ###.#
EP2_PMM1_TotalReactivePower_kVAR | REAL | IOD_EP2_TCP | 44485 | [5 empty] | ###.#
EP2_PMM1_VoltageBetweenPhaseAB_V | REAL | IOD_EP2_TCP | 44487 | [5 empty] | ###.#
EP2_PMM1_VoltageBetweenPhaseAN_V | REAL | IOD_EP2_TCP | 44489 | [5 empty] | ###.#
EP2_PMM1_VoltageBetweenPhaseBC_V | REAL | IOD_EP2_TCP | 44491 | [5 empty] | ###.#
EP2_PMM1_VoltageBetweenPhaseBN_V | REAL | IOD_EP2_TCP | 44493 | [5 empty] | ###.#
EP2_PMM1_VoltageBetweenPhaseCA_V | REAL | IOD_EP2_TCP | 44495 | [5 empty] | ###.#
EP2_PMM1_VoltageBetweenPhaseCN_V | REAL | IOD_EP2_TCP | 44497 | [5 empty] | ###.#
EP2_PMM2_ActivePowerPhaseA_kW | REAL | IOD_EP2_TCP | 44499 | [5 empty] | ###.#
EP2_PMM2_ActivePowerPhaseB_kW | REAL | IOD_EP2_TCP | 44501 | [5 empty] | ###.#
EP2_PMM2_ActivePowerPhaseC_kW | REAL | IOD_EP2_TCP | 44503 | [5 empty] | ###.#
EP2_PMM2_AlarmPhase1_C01_16_60to | INT | IOD_EP2_TCP | 40037
EP2_PMM2_AlarmPhase1_C01_16_over | INT | IOD_EP2_TCP | 40038
EP2_PMM2_AlarmPhase1_C17_32_60to | INT | IOD_EP2_TCP | 40039
EP2_PMM2_AlarmPhase1_C17_32_over | INT | IOD_EP2_TCP | 40040
EP2_PMM2_AlarmPhase1_C33_42_60to | INT | IOD_EP2_TCP | 40041
EP2_PMM2_AlarmPhase1_C33_42_over | INT | IOD_EP2_TCP | 40042
EP2_PMM2_AlarmPhase1_GlobalAlarm | INT | IOD_EP2_TCP | 40043
EP2_PMM2_AlarmPhase2_C01_16_60to | INT | IOD_EP2_TCP | 40044
EP2_PMM2_AlarmPhase2_C01_16_over | INT | IOD_EP2_TCP | 40045
EP2_PMM2_AlarmPhase2_C17_32_60to | INT | IOD_EP2_TCP | 40046
EP2_PMM2_AlarmPhase2_C17_32_over | INT | IOD_EP2_TCP | 40047
EP2_PMM2_AlarmPhase2_C33_42_60to | INT | IOD_EP2_TCP | 40048
EP2_PMM2_AlarmPhase2_C33_42_over | INT | IOD_EP2_TCP | 40049
EP2_PMM2_AlarmPhase2_GlobalAlarm | INT | IOD_EP2_TCP | 40050
EP2_PMM2_AlarmPhase3_C01_16_60to | INT | IOD_EP2_TCP | 40051
EP2_PMM2_AlarmPhase3_C01_16_over | INT | IOD_EP2_TCP | 40052
EP2_PMM2_AlarmPhase3_C17_32_60to | INT | IOD_EP2_TCP | 40053
EP2_PMM2_AlarmPhase3_C17_32_over | INT | IOD_EP2_TCP | 40054
EP2_PMM2_AlarmPhase3_C33_42_60to | INT | IOD_EP2_TCP | 40055
EP2_PMM2_AlarmPhase3_C33_42_over | INT | IOD_EP2_TCP | 40056
EP2_PMM2_AlarmPhase3_GlobalAlarm | INT | IOD_EP2_TCP | 40057
EP2_PMM2_Alarms | INT | IOD_EP2_TCP | 40058
EP2_PMM2_AverageCurrent_A | REAL | IOD_EP2_TCP | 44505 | [5 empty] | ###.#
EP2_PMM2_AveragePhaseToNeutral_V | REAL | IOD_EP2_TCP | 44507 | [5 empty] | ###.#
EP2_PMM2_AveragePhaseToPhase_V | REAL | IOD_EP2_TCP | 44509 | [5 empty] | ###.#
EP2_PMM2_CurrentInPhaseA_A | REAL | IOD_EP2_TCP | 44511 | [5 empty] | ###.#
EP2_PMM2_CurrentInPhaseB_A | REAL | IOD_EP2_TCP | 44513 | [5 empty] | ###.#
EP2_PMM2_CurrentInPhaseC_A | REAL | IOD_EP2_TCP | 44515 | [5 empty] | ###.#
EP2_PMM2_EnergyConsumed_kWh | REAL | IOD_EP2_TCP | 44517 | [5 empty] | ###.#
EP2_PMM2_Frequency_Hz | REAL | IOD_EP2_TCP | 44519 | [5 empty] | ###.#
EP2_PMM2_Napaka | DIGITAL | IOD_EP2_TCP | 00197
EP2_PMM2_NeutralCurrent_A | REAL | IOD_EP2_TCP | 44521 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current10 | REAL | IOD_EP2_TCP | 44523 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current11 | REAL | IOD_EP2_TCP | 44525 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current12 | REAL | IOD_EP2_TCP | 44527 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current13 | REAL | IOD_EP2_TCP | 44529 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current14 | REAL | IOD_EP2_TCP | 44531 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current15 | REAL | IOD_EP2_TCP | 44533 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current16 | REAL | IOD_EP2_TCP | 44535 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current17 | REAL | IOD_EP2_TCP | 44537 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current18 | REAL | IOD_EP2_TCP | 44539 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current19 | REAL | IOD_EP2_TCP | 44541 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current1 | REAL | IOD_EP2_TCP | 44543 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current20 | REAL | IOD_EP2_TCP | 44545 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current21 | REAL | IOD_EP2_TCP | 44547 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current22 | REAL | IOD_EP2_TCP | 44549 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current23 | REAL | IOD_EP2_TCP | 44551 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current24 | REAL | IOD_EP2_TCP | 44553 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current25 | REAL | IOD_EP2_TCP | 44555 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current26 | REAL | IOD_EP2_TCP | 44557 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current27 | REAL | IOD_EP2_TCP | 44559 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current28 | REAL | IOD_EP2_TCP | 44561 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current29 | REAL | IOD_EP2_TCP | 44563 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current2 | REAL | IOD_EP2_TCP | 44565 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current30 | REAL | IOD_EP2_TCP | 44567 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current31 | REAL | IOD_EP2_TCP | 44569 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current32 | REAL | IOD_EP2_TCP | 44571 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current33 | REAL | IOD_EP2_TCP | 44573 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current34 | REAL | IOD_EP2_TCP | 44575 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current35 | REAL | IOD_EP2_TCP | 44577 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current36 | REAL | IOD_EP2_TCP | 44579 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current37 | REAL | IOD_EP2_TCP | 44581 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current38 | REAL | IOD_EP2_TCP | 44583 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current39 | REAL | IOD_EP2_TCP | 44585 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current3 | REAL | IOD_EP2_TCP | 44587 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current40 | REAL | IOD_EP2_TCP | 44589 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current41 | REAL | IOD_EP2_TCP | 44591 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current42 | REAL | IOD_EP2_TCP | 44593 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current4 | REAL | IOD_EP2_TCP | 44595 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current5 | REAL | IOD_EP2_TCP | 44597 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current6 | REAL | IOD_EP2_TCP | 44599 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current7 | REAL | IOD_EP2_TCP | 44601 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current8 | REAL | IOD_EP2_TCP | 44603 | [5 empty] | ###.#
EP2_PMM2_Phase1_Current9 | REAL | IOD_EP2_TCP | 44605 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current10 | REAL | IOD_EP2_TCP | 44607 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current11 | REAL | IOD_EP2_TCP | 44609 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current12 | REAL | IOD_EP2_TCP | 44611 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current13 | REAL | IOD_EP2_TCP | 44613 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current14 | REAL | IOD_EP2_TCP | 44615 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current15 | REAL | IOD_EP2_TCP | 44617 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current16 | REAL | IOD_EP2_TCP | 44619 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current17 | REAL | IOD_EP2_TCP | 44621 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current18 | REAL | IOD_EP2_TCP | 44623 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current19 | REAL | IOD_EP2_TCP | 44625 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current1 | REAL | IOD_EP2_TCP | 44627 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current20 | REAL | IOD_EP2_TCP | 44629 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current21 | REAL | IOD_EP2_TCP | 44631 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current22 | REAL | IOD_EP2_TCP | 44633 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current23 | REAL | IOD_EP2_TCP | 44635 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current24 | REAL | IOD_EP2_TCP | 44637 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current25 | REAL | IOD_EP2_TCP | 44639 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current26 | REAL | IOD_EP2_TCP | 44641 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current27 | REAL | IOD_EP2_TCP | 44643 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current28 | REAL | IOD_EP2_TCP | 44645 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current29 | REAL | IOD_EP2_TCP | 44647 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current2 | REAL | IOD_EP2_TCP | 44649 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current30 | REAL | IOD_EP2_TCP | 44651 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current31 | REAL | IOD_EP2_TCP | 44653 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current32 | REAL | IOD_EP2_TCP | 44655 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current33 | REAL | IOD_EP2_TCP | 44657 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current34 | REAL | IOD_EP2_TCP | 44659 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current35 | REAL | IOD_EP2_TCP | 44661 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current36 | REAL | IOD_EP2_TCP | 44663 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current37 | REAL | IOD_EP2_TCP | 44665 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current38 | REAL | IOD_EP2_TCP | 44667 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current39 | REAL | IOD_EP2_TCP | 44669 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current3 | REAL | IOD_EP2_TCP | 44671 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current40 | REAL | IOD_EP2_TCP | 44673 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current41 | REAL | IOD_EP2_TCP | 44675 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current42 | REAL | IOD_EP2_TCP | 44677 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current4 | REAL | IOD_EP2_TCP | 44679 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current5 | REAL | IOD_EP2_TCP | 44681 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current6 | REAL | IOD_EP2_TCP | 44683 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current7 | REAL | IOD_EP2_TCP | 44685 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current8 | REAL | IOD_EP2_TCP | 44687 | [5 empty] | ###.#
EP2_PMM2_Phase2_Current9 | REAL | IOD_EP2_TCP | 44689 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current10 | REAL | IOD_EP2_TCP | 44691 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current11 | REAL | IOD_EP2_TCP | 44693 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current12 | REAL | IOD_EP2_TCP | 44695 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current13 | REAL | IOD_EP2_TCP | 44697 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current14 | REAL | IOD_EP2_TCP | 44699 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current15 | REAL | IOD_EP2_TCP | 44701 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current16 | REAL | IOD_EP2_TCP | 44703 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current17 | REAL | IOD_EP2_TCP | 44705 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current18 | REAL | IOD_EP2_TCP | 44707 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current19 | REAL | IOD_EP2_TCP | 44709 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current1 | REAL | IOD_EP2_TCP | 44711 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current20 | REAL | IOD_EP2_TCP | 44713 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current21 | REAL | IOD_EP2_TCP | 44715 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current22 | REAL | IOD_EP2_TCP | 44717 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current23 | REAL | IOD_EP2_TCP | 44719 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current24 | REAL | IOD_EP2_TCP | 44721 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current25 | REAL | IOD_EP2_TCP | 44723 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current26 | REAL | IOD_EP2_TCP | 44725 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current27 | REAL | IOD_EP2_TCP | 44727 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current28 | REAL | IOD_EP2_TCP | 44729 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current29 | REAL | IOD_EP2_TCP | 44731 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current2 | REAL | IOD_EP2_TCP | 44733 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current30 | REAL | IOD_EP2_TCP | 44735 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current31 | REAL | IOD_EP2_TCP | 44737 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current32 | REAL | IOD_EP2_TCP | 44739 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current33 | REAL | IOD_EP2_TCP | 44741 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current34 | REAL | IOD_EP2_TCP | 44743 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current35 | REAL | IOD_EP2_TCP | 44745 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current36 | REAL | IOD_EP2_TCP | 44747 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current37 | REAL | IOD_EP2_TCP | 44749 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current38 | REAL | IOD_EP2_TCP | 44751 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current39 | REAL | IOD_EP2_TCP | 44753 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current3 | REAL | IOD_EP2_TCP | 44755 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current40 | REAL | IOD_EP2_TCP | 44757 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current41 | REAL | IOD_EP2_TCP | 44759 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current42 | REAL | IOD_EP2_TCP | 44761 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current4 | REAL | IOD_EP2_TCP | 44763 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current5 | REAL | IOD_EP2_TCP | 44765 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current6 | REAL | IOD_EP2_TCP | 44767 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current7 | REAL | IOD_EP2_TCP | 44769 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current8 | REAL | IOD_EP2_TCP | 44771 | [5 empty] | ###.#
EP2_PMM2_Phase3_Current9 | REAL | IOD_EP2_TCP | 44773 | [5 empty] | ###.#
EP2_PMM2_PowerFactorPhaseA | REAL | IOD_EP2_TCP | 44775 | [5 empty] | ###.#
EP2_PMM2_PowerFactorPhaseB | REAL | IOD_EP2_TCP | 44777 | [5 empty] | ###.#
EP2_PMM2_PowerFactorPhaseC | REAL | IOD_EP2_TCP | 44779 | [5 empty] | ###.#
EP2_PMM2_TotalActivePower_kW | REAL | IOD_EP2_TCP | 44781 | [5 empty] | ###.#
EP2_PMM2_TotalAparentPower_kVA | REAL | IOD_EP2_TCP | 44783 | [5 empty] | ###.#
EP2_PMM2_TotalPowerFactor | REAL | IOD_EP2_TCP | 44785 | [5 empty] | ###.#
EP2_PMM2_TotalReactivePower_kVAR | REAL | IOD_EP2_TCP | 44787 | [5 empty] | ###.#
EP2_PMM2_VoltageBetweenPhaseAB_V | REAL | IOD_EP2_TCP | 44789 | [5 empty] | ###.#
EP2_PMM2_VoltageBetweenPhaseAN_V | REAL | IOD_EP2_TCP | 44791 | [5 empty] | ###.#
EP2_PMM2_VoltageBetweenPhaseBC_V | REAL | IOD_EP2_TCP | 44793 | [5 empty] | ###.#
EP2_PMM2_VoltageBetweenPhaseBN_V | REAL | IOD_EP2_TCP | 44795 | [5 empty] | ###.#
EP2_PMM2_VoltageBetweenPhaseCA_V | REAL | IOD_EP2_TCP | 44797 | [5 empty] | ###.#
EP2_PMM2_VoltageBetweenPhaseCN_V | REAL | IOD_EP2_TCP | 44799 | [5 empty] | ###.#
EP2_PMM3_ActivePowerPhaseA_kW | REAL | IOD_EP2_TCP | 44801 | [5 empty] | ###.#
EP2_PMM3_ActivePowerPhaseB_kW | REAL | IOD_EP2_TCP | 44803 | [5 empty] | ###.#
EP2_PMM3_ActivePowerPhaseC_kW | REAL | IOD_EP2_TCP | 44805 | [5 empty] | ###.#
EP2_PMM3_AlarmPhase1_C01_16_60to | INT | IOD_EP2_TCP | 40059
EP2_PMM3_AlarmPhase1_C01_16_over | INT | IOD_EP2_TCP | 40060
EP2_PMM3_AlarmPhase1_C17_32_60to | INT | IOD_EP2_TCP | 40061
EP2_PMM3_AlarmPhase1_C17_32_over | INT | IOD_EP2_TCP | 40062
EP2_PMM3_AlarmPhase1_C33_42_60to | INT | IOD_EP2_TCP | 40063
EP2_PMM3_AlarmPhase1_C33_42_over | INT | IOD_EP2_TCP | 40064
EP2_PMM3_AlarmPhase1_GlobalAlarm | INT | IOD_EP2_TCP | 40065
EP2_PMM3_AlarmPhase2_C01_16_60to | INT | IOD_EP2_TCP | 40066
EP2_PMM3_AlarmPhase2_C01_16_over | INT | IOD_EP2_TCP | 40067
EP2_PMM3_AlarmPhase2_C17_32_60to | INT | IOD_EP2_TCP | 40068
EP2_PMM3_AlarmPhase2_C17_32_over | INT | IOD_EP2_TCP | 40069
EP2_PMM3_AlarmPhase2_C33_42_60to | INT | IOD_EP2_TCP | 40070
EP2_PMM3_AlarmPhase2_C33_42_over | INT | IOD_EP2_TCP | 40071
EP2_PMM3_AlarmPhase2_GlobalAlarm | INT | IOD_EP2_TCP | 40072
EP2_PMM3_AlarmPhase3_C01_16_60to | INT | IOD_EP2_TCP | 40073
EP2_PMM3_AlarmPhase3_C01_16_over | INT | IOD_EP2_TCP | 40074
EP2_PMM3_AlarmPhase3_C17_32_60to | INT | IOD_EP2_TCP | 40075
EP2_PMM3_AlarmPhase3_C17_32_over | INT | IOD_EP2_TCP | 40076
EP2_PMM3_AlarmPhase3_C33_42_60to | INT | IOD_EP2_TCP | 40077
EP2_PMM3_AlarmPhase3_C33_42_over | INT | IOD_EP2_TCP | 40078
EP2_PMM3_AlarmPhase3_GlobalAlarm | INT | IOD_EP2_TCP | 40079
EP2_PMM3_Alarms | INT | IOD_EP2_TCP | 40080
EP2_PMM3_AverageCurrent_A | REAL | IOD_EP2_TCP | 44807 | [5 empty] | ###.#
EP2_PMM3_AveragePhaseToNeutral_V | REAL | IOD_EP2_TCP | 44809 | [5 empty] | ###.#
EP2_PMM3_AveragePhaseToPhase_V | REAL | IOD_EP2_TCP | 44811 | [5 empty] | ###.#
EP2_PMM3_CurrentInPhaseA_A | REAL | IOD_EP2_TCP | 44813 | [5 empty] | ###.#
EP2_PMM3_CurrentInPhaseB_A | REAL | IOD_EP2_TCP | 44815 | [5 empty] | ###.#
EP2_PMM3_CurrentInPhaseC_A | REAL | IOD_EP2_TCP | 44817 | [5 empty] | ###.#
EP2_PMM3_EnergyConsumed_kWh | REAL | IOD_EP2_TCP | 44819 | [5 empty] | ###.#
EP2_PMM3_Frequency_Hz | REAL | IOD_EP2_TCP | 44821 | [5 empty] | ###.#
EP2_PMM3_Napaka | DIGITAL | IOD_EP2_TCP | 00198
EP2_PMM3_NeutralCurrent_A | REAL | IOD_EP2_TCP | 44823 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current10 | REAL | IOD_EP2_TCP | 44825 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current11 | REAL | IOD_EP2_TCP | 44827 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current12 | REAL | IOD_EP2_TCP | 44829 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current13 | REAL | IOD_EP2_TCP | 44831 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current14 | REAL | IOD_EP2_TCP | 44833 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current15 | REAL | IOD_EP2_TCP | 44835 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current16 | REAL | IOD_EP2_TCP | 44837 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current17 | REAL | IOD_EP2_TCP | 44839 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current18 | REAL | IOD_EP2_TCP | 44841 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current19 | REAL | IOD_EP2_TCP | 44843 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current1 | REAL | IOD_EP2_TCP | 44845 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current20 | REAL | IOD_EP2_TCP | 44847 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current21 | REAL | IOD_EP2_TCP | 44849 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current22 | REAL | IOD_EP2_TCP | 44851 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current23 | REAL | IOD_EP2_TCP | 44853 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current24 | REAL | IOD_EP2_TCP | 44855 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current25 | REAL | IOD_EP2_TCP | 44857 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current26 | REAL | IOD_EP2_TCP | 44859 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current27 | REAL | IOD_EP2_TCP | 44861 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current28 | REAL | IOD_EP2_TCP | 44863 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current29 | REAL | IOD_EP2_TCP | 44865 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current2 | REAL | IOD_EP2_TCP | 44867 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current30 | REAL | IOD_EP2_TCP | 44869 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current31 | REAL | IOD_EP2_TCP | 44871 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current32 | REAL | IOD_EP2_TCP | 44873 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current33 | REAL | IOD_EP2_TCP | 44875 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current34 | REAL | IOD_EP2_TCP | 44877 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current35 | REAL | IOD_EP2_TCP | 44879 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current36 | REAL | IOD_EP2_TCP | 44881 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current37 | REAL | IOD_EP2_TCP | 44883 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current38 | REAL | IOD_EP2_TCP | 44885 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current39 | REAL | IOD_EP2_TCP | 44887 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current3 | REAL | IOD_EP2_TCP | 44889 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current40 | REAL | IOD_EP2_TCP | 44891 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current41 | REAL | IOD_EP2_TCP | 44893 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current42 | REAL | IOD_EP2_TCP | 44895 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current4 | REAL | IOD_EP2_TCP | 44897 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current5 | REAL | IOD_EP2_TCP | 44899 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current6 | REAL | IOD_EP2_TCP | 44901 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current7 | REAL | IOD_EP2_TCP | 44903 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current8 | REAL | IOD_EP2_TCP | 44905 | [5 empty] | ###.#
EP2_PMM3_Phase1_Current9 | REAL | IOD_EP2_TCP | 44907 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current10 | REAL | IOD_EP2_TCP | 44909 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current11 | REAL | IOD_EP2_TCP | 44911 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current12 | REAL | IOD_EP2_TCP | 44913 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current13 | REAL | IOD_EP2_TCP | 44915 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current14 | REAL | IOD_EP2_TCP | 44917 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current15 | REAL | IOD_EP2_TCP | 44919 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current16 | REAL | IOD_EP2_TCP | 44921 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current17 | REAL | IOD_EP2_TCP | 44923 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current18 | REAL | IOD_EP2_TCP | 44925 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current19 | REAL | IOD_EP2_TCP | 44927 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current1 | REAL | IOD_EP2_TCP | 44929 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current20 | REAL | IOD_EP2_TCP | 44931 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current21 | REAL | IOD_EP2_TCP | 44933 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current22 | REAL | IOD_EP2_TCP | 44935 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current23 | REAL | IOD_EP2_TCP | 44937 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current24 | REAL | IOD_EP2_TCP | 44939 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current25 | REAL | IOD_EP2_TCP | 44941 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current26 | REAL | IOD_EP2_TCP | 44943 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current27 | REAL | IOD_EP2_TCP | 44945 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current28 | REAL | IOD_EP2_TCP | 44947 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current29 | REAL | IOD_EP2_TCP | 44949 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current2 | REAL | IOD_EP2_TCP | 44951 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current30 | REAL | IOD_EP2_TCP | 44953 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current31 | REAL | IOD_EP2_TCP | 44955 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current32 | REAL | IOD_EP2_TCP | 44957 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current33 | REAL | IOD_EP2_TCP | 44959 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current34 | REAL | IOD_EP2_TCP | 44961 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current35 | REAL | IOD_EP2_TCP | 44963 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current36 | REAL | IOD_EP2_TCP | 44965 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current37 | REAL | IOD_EP2_TCP | 44967 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current38 | REAL | IOD_EP2_TCP | 44969 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current39 | REAL | IOD_EP2_TCP | 44971 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current3 | REAL | IOD_EP2_TCP | 44973 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current40 | REAL | IOD_EP2_TCP | 44975 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current41 | REAL | IOD_EP2_TCP | 44977 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current42 | REAL | IOD_EP2_TCP | 44979 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current4 | REAL | IOD_EP2_TCP | 44981 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current5 | REAL | IOD_EP2_TCP | 44983 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current6 | REAL | IOD_EP2_TCP | 44985 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current7 | REAL | IOD_EP2_TCP | 44987 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current8 | REAL | IOD_EP2_TCP | 44989 | [5 empty] | ###.#
EP2_PMM3_Phase2_Current9 | REAL | IOD_EP2_TCP | 44991 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current10 | REAL | IOD_EP2_TCP | 44993 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current11 | REAL | IOD_EP2_TCP | 44995 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current12 | REAL | IOD_EP2_TCP | 44997 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current13 | REAL | IOD_EP2_TCP | 44999 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current14 | REAL | IOD_EP2_TCP | 45001 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current15 | REAL | IOD_EP2_TCP | 45003 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current16 | REAL | IOD_EP2_TCP | 45005 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current17 | REAL | IOD_EP2_TCP | 45007 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current18 | REAL | IOD_EP2_TCP | 45009 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current19 | REAL | IOD_EP2_TCP | 45011 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current1 | REAL | IOD_EP2_TCP | 45013 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current20 | REAL | IOD_EP2_TCP | 45015 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current21 | REAL | IOD_EP2_TCP | 45017 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current22 | REAL | IOD_EP2_TCP | 45019 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current23 | REAL | IOD_EP2_TCP | 45021 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current24 | REAL | IOD_EP2_TCP | 45023 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current25 | REAL | IOD_EP2_TCP | 45025 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current26 | REAL | IOD_EP2_TCP | 45027 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current27 | REAL | IOD_EP2_TCP | 45029 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current28 | REAL | IOD_EP2_TCP | 45031 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current29 | REAL | IOD_EP2_TCP | 45033 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current2 | REAL | IOD_EP2_TCP | 45035 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current30 | REAL | IOD_EP2_TCP | 45037 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current31 | REAL | IOD_EP2_TCP | 45039 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current32 | REAL | IOD_EP2_TCP | 45041 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current33 | REAL | IOD_EP2_TCP | 45043 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current34 | REAL | IOD_EP2_TCP | 45045 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current35 | REAL | IOD_EP2_TCP | 45047 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current36 | REAL | IOD_EP2_TCP | 45049 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current37 | REAL | IOD_EP2_TCP | 45051 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current38 | REAL | IOD_EP2_TCP | 45053 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current39 | REAL | IOD_EP2_TCP | 45055 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current3 | REAL | IOD_EP2_TCP | 45057 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current40 | REAL | IOD_EP2_TCP | 45059 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current41 | REAL | IOD_EP2_TCP | 45061 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current42 | REAL | IOD_EP2_TCP | 45063 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current4 | REAL | IOD_EP2_TCP | 45065 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current5 | REAL | IOD_EP2_TCP | 45067 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current6 | REAL | IOD_EP2_TCP | 45069 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current7 | REAL | IOD_EP2_TCP | 45071 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current8 | REAL | IOD_EP2_TCP | 45073 | [5 empty] | ###.#
EP2_PMM3_Phase3_Current9 | REAL | IOD_EP2_TCP | 45075 | [5 empty] | ###.#
EP2_PMM3_PowerFactorPhaseA | REAL | IOD_EP2_TCP | 45077 | [5 empty] | ###.#
EP2_PMM3_PowerFactorPhaseB | REAL | IOD_EP2_TCP | 45079 | [5 empty] | ###.#
EP2_PMM3_PowerFactorPhaseC | REAL | IOD_EP2_TCP | 45081 | [5 empty] | ###.#
EP2_PMM3_TotalActivePower_kW | REAL | IOD_EP2_TCP | 45083 | [5 empty] | ###.#
EP2_PMM3_TotalAparentPower_kVA | REAL | IOD_EP2_TCP | 45085 | [5 empty] | ###.#
EP2_PMM3_TotalPowerFactor | REAL | IOD_EP2_TCP | 45087 | [5 empty] | ###.#
EP2_PMM3_TotalReactivePower_kVAR | REAL | IOD_EP2_TCP | 45089 | [5 empty] | ###.#
EP2_PMM3_VoltageBetweenPhaseAB_V | REAL | IOD_EP2_TCP | 45091 | [5 empty] | ###.#
EP2_PMM3_VoltageBetweenPhaseAN_V | REAL | IOD_EP2_TCP | 45093 | [5 empty] | ###.#
EP2_PMM3_VoltageBetweenPhaseBC_V | REAL | IOD_EP2_TCP | 45095 | [5 empty] | ###.#
EP2_PMM3_VoltageBetweenPhaseBN_V | REAL | IOD_EP2_TCP | 45097 | [5 empty] | ###.#
EP2_PMM3_VoltageBetweenPhaseCA_V | REAL | IOD_EP2_TCP | 45099 | [5 empty] | ###.#
EP2_PMM3_VoltageBetweenPhaseCN_V | REAL | IOD_EP2_TCP | 45101 | [5 empty] | ###.#
EP2_rVersion | REAL | IOD_EP2_TCP | 45103
EP2_SenzorTemp1 | REAL | IOD_EP2_TCP | 45105 | 0 | 60 | 0 | 60 | °C | ##.#
EP2_SenzorTemp2 | REAL | IOD_EP2_TCP | 45107 | 0 | 60 | 0 | 60 | °C | ##.#
EP2_SenzorVlaga1 | REAL | IOD_EP2_TCP | 45109 | 0 | 100 | 0 | 100 | % | ##.#
EP2_SenzorVlaga2 | REAL | IOD_EP2_TCP | 45111 | 0 | 100 | 0 | 100 | % | ##.#
EP2_SetDateTime | DIGITAL | IOD_EP2_TCP | 00199
EP2_SetDateTimeDemand | DIGITAL | IOD_EP2_TCP | 00200
EP2_SetDateTimeError | DIGITAL | IOD_EP2_TCP | 00201
EP2_SetDateTimeFinished | DIGITAL | IOD_EP2_TCP | 00202
EP2_SetRemoteOnOff1 | DIGITAL | IOD_EP2_TCP | 00203
EP2_SetRemoteOnOff2 | DIGITAL | IOD_EP2_TCP | 00204
EP2_SlabaBaterijaPLC_A1 | DIGITAL | IOD_EP2_TCP | 00205
EP2_TempMaxPoint | REAL | IOD_EP2_TCP | 45113 | 0 | 60 | 0 | 60 | °C | ##.#
EP2_TempSetPoint | REAL | IOD_EP2_TCP | 45115 | 0 | 60 | 0 | 60 | °C | ##.#
EP2_TempTSprevisoka1 | DIGITAL | IOD_EP2_TCP | 00206
EP2_TempTSprevisoka2 | DIGITAL | IOD_EP2_TCP | 00207
EP2UPS1AlarmAwaitingPower | DIGITAL | IOD_EP2_TCP | 00208
EP2UPS1AlarmBypassBad | DIGITAL | IOD_EP2_TCP | 00209
EP2UPS1AlarmChargerFailed | DIGITAL | IOD_EP2_TCP | 00210
EP2UPS1AlarmCommunicationsLost | DIGITAL | IOD_EP2_TCP | 00211
EP2UPS1AlarmDepletedBattery | DIGITAL | IOD_EP2_TCP | 00212
EP2UPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_EP2_TCP | 00213
EP2UPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_EP2_TCP | 00214
EP2UPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_EP2_TCP | 00215
EP2UPS1AlarmLowBattery | DIGITAL | IOD_EP2_TCP | 00216
EP2UPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_EP2_TCP | 00217
EP2UPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_EP2_TCP | 00218
EP2UPS1AlarmOnBattery | DIGITAL | IOD_EP2_TCP | 00219
EP2UPS1AlarmOnBypass | DIGITAL | IOD_EP2_TCP | 00220
EP2UPS1AlarmInverterError | DIGITAL | IOD_EP2_TCP | 00221
EP2UPS1AlarmShutdownImminent | DIGITAL | IOD_EP2_TCP | 00222
EP2UPS1AlarmShutdownPending | DIGITAL | IOD_EP2_TCP | 00223
EP2UPS1AlarmSlabaBaterija | DIGITAL | IOD_EP2_TCP | 00224
EP2UPS1AlarmSplosnaNapaka | DIGITAL | IOD_EP2_TCP | 00225
EP2UPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_EP2_TCP | 00226
EP2UPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_EP2_TCP | 00227
EP2UPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_EP2_TCP | 00228
EP2UPS1AlarmTestInProgres | DIGITAL | IOD_EP2_TCP | 00229
EP2UPS1AlarmUPSIzhodOff | DIGITAL | IOD_EP2_TCP | 00230
EP2UPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_EP2_TCP | 00231
EP2UPS1AlarmUPSSystemOff | DIGITAL | IOD_EP2_TCP | 00232
EP2UPS1EstimatedChargeRemaining | REAL | IOD_EP2_TCP | 45117 | 0 | 100 | 0 | 100 | % | ###
EP2UPS1EstimatedMinutesRemaining | REAL | IOD_EP2_TCP | 45119 | 0 | 500 | 0 | 500 | min | ###
EP2UPS1InverterStatus | INT | IOD_EP2_TCP | 40081
EP2UPS1IzhodMocL1 | REAL | IOD_EP2_TCP | 45121 | 0 | 100 | 0 | 100 | % | ##.#
EP2UPS1IzhodMocL2 | REAL | IOD_EP2_TCP | 45123 | 0 | 100 | 0 | 100 | % | ##.#
EP2UPS1IzhodMocL3 | REAL | IOD_EP2_TCP | 45125 | 0 | 100 | 0 | 100 | % | ##.#
EP2UPS1Napaka | DIGITAL | IOD_EP2_TCP | 00233
EP2UPS1NapetostBaterije | REAL | IOD_EP2_TCP | 45127 | 0 | 500 | 0 | 500 | V | ###.#
EP2UPS1OutputStatus | INT | IOD_EP2_TCP | 40082
EP2UPS1StatusBaterije | INT | IOD_EP2_TCP | 40083 | [5 empty] | ##
EP2UPS1StatusEcomodeAktiven | DIGITAL | IOD_EP2_TCP | 00234
EP2UPS1StatusInverterIsOn | DIGITAL | IOD_EP2_TCP | 00235
EP2UPS1StatusStopOperation | DIGITAL | IOD_EP2_TCP | 00236
EP2UPS1SteviloIzpadovVhodneLinije | INT | IOD_EP2_TCP | 40084 | [5 empty] | #####
EP2UPS1TemperaturaBaterije | REAL | IOD_EP2_TCP | 45129 | 0 | 100 | 0 | 100 | °C | ###
EP2UPS1UnitStatus | INT | IOD_EP2_TCP | 40085
EP2UPS1VhodFrekvencaL1 | REAL | IOD_EP2_TCP | 45131 | 0 | 60 | 0 | 60 | Hz | ##.#
EP2UPS1VhodFrekvencaL2 | REAL | IOD_EP2_TCP | 45133 | 0 | 60 | 0 | 60 | Hz | ##.#
EP2UPS1VhodFrekvencaL3 | REAL | IOD_EP2_TCP | 45135 | 0 | 60 | 0 | 60 | Hz | ##.#
EP2UPS1VhodNapetostL1 | REAL | IOD_EP2_TCP | 45137 | 0 | 500 | 0 | 500 | V | ###.#
EP2UPS1VhodNapetostL2 | REAL | IOD_EP2_TCP | 45139 | 0 | 500 | 0 | 500 | V | ###.#
EP2UPS1VhodNapetostL3 | REAL | IOD_EP2_TCP | 45141 | 0 | 500 | 0 | 500 | V | ###.#
EP2UPS2AlarmAwaitingPower | DIGITAL | IOD_EP2_TCP | 00237
EP2UPS2AlarmBypassBad | DIGITAL | IOD_EP2_TCP | 00238
EP2UPS2AlarmChargerFailed | DIGITAL | IOD_EP2_TCP | 00239
EP2UPS2AlarmCommunicationsLost | DIGITAL | IOD_EP2_TCP | 00240
EP2UPS2AlarmDepletedBattery | DIGITAL | IOD_EP2_TCP | 00241
EP2UPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_EP2_TCP | 00242
EP2UPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_EP2_TCP | 00243
EP2UPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_EP2_TCP | 00244
EP2UPS2AlarmLowBattery | DIGITAL | IOD_EP2_TCP | 00245
EP2UPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_EP2_TCP | 00246
EP2UPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_EP2_TCP | 00247
EP2UPS2AlarmOnBattery | DIGITAL | IOD_EP2_TCP | 00248
EP2UPS2AlarmOnBypass | DIGITAL | IOD_EP2_TCP | 00249
EP2UPS2AlarmInverterError | DIGITAL | IOD_EP2_TCP | 00250
EP2UPS2AlarmShutdownImminent | DIGITAL | IOD_EP2_TCP | 00251
EP2UPS2AlarmShutdownPending | DIGITAL | IOD_EP2_TCP | 00252
EP2UPS2AlarmSlabaBaterija | DIGITAL | IOD_EP2_TCP | 00253
EP2UPS2AlarmSplosnaNapaka | DIGITAL | IOD_EP2_TCP | 00254
EP2UPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_EP2_TCP | 00255
EP2UPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_EP2_TCP | 00256
EP2UPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_EP2_TCP | 00257
EP2UPS2AlarmTestInProgres | DIGITAL | IOD_EP2_TCP | 00258
EP2UPS2AlarmUPSIzhodOff | DIGITAL | IOD_EP2_TCP | 00259
EP2UPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_EP2_TCP | 00260
EP2UPS2AlarmUPSSystemOff | DIGITAL | IOD_EP2_TCP | 00261
EP2UPS2EstimatedChargeRemaining | REAL | IOD_EP2_TCP | 45143 | 0 | 100 | 0 | 100 | % | ###
EP2UPS2EstimatedMinutesRemaining | REAL | IOD_EP2_TCP | 45145 | 0 | 500 | 0 | 500 | min | ###
EP2UPS2InverterStatus | INT | IOD_EP2_TCP | 40086
EP2UPS2IzhodMocL1 | REAL | IOD_EP2_TCP | 45147 | 0 | 100 | 0 | 100 | % | ##.#
EP2UPS2IzhodMocL2 | REAL | IOD_EP2_TCP | 45149 | 0 | 100 | 0 | 100 | % | ##.#
EP2UPS2IzhodMocL3 | REAL | IOD_EP2_TCP | 45151 | 0 | 100 | 0 | 100 | % | ##.#
EP2UPS2Napaka | DIGITAL | IOD_EP2_TCP | 00262
EP2UPS2NapetostBaterije | REAL | IOD_EP2_TCP | 45153 | 0 | 500 | 0 | 500 | V | ###.#
EP2UPS2OutputStatus | INT | IOD_EP2_TCP | 40087
EP2UPS2StatusBaterije | INT | IOD_EP2_TCP | 40088 | [5 empty] | ##
EP2UPS2StatusEcomodeAktiven | DIGITAL | IOD_EP2_TCP | 00263
EP2UPS2StatusInverterIsOn | DIGITAL | IOD_EP2_TCP | 00264
EP2UPS2StatusStopOperation | DIGITAL | IOD_EP2_TCP | 00265
EP2UPS2SteviloIzpadovVhodneLinije | INT | IOD_EP2_TCP | 40089 | [5 empty] | #####
EP2UPS2TemperaturaBaterije | REAL | IOD_EP2_TCP | 45155 | 0 | 100 | 0 | 100 | °C | ###
EP2UPS2UnitStatus | INT | IOD_EP2_TCP | 40090
EP2UPS2VhodFrekvencaL1 | REAL | IOD_EP2_TCP | 45157 | 0 | 60 | 0 | 60 | Hz | ##.#
EP2UPS2VhodFrekvencaL2 | REAL | IOD_EP2_TCP | 45159 | 0 | 60 | 0 | 60 | Hz | ##.#
EP2UPS2VhodFrekvencaL3 | REAL | IOD_EP2_TCP | 45161 | 0 | 60 | 0 | 60 | Hz | ##.#
EP2UPS2VhodNapetostL1 | REAL | IOD_EP2_TCP | 45163 | 0 | 500 | 0 | 500 | V | ###.#
EP2UPS2VhodNapetostL2 | REAL | IOD_EP2_TCP | 45165 | 0 | 500 | 0 | 500 | V | ###.#
EP2UPS2VhodNapetostL3 | REAL | IOD_EP2_TCP | 45167 | 0 | 500 | 0 | 500 | V | ###.#
EP2_UserCurrentLevel | INT | IOD_EP2_TCP | 40091
EP2_UserCurrentName | STRING | IOD_EP2_TCP | 47001[15]
EP2_UserLoggedIn | DIGITAL | IOD_EP2_TCP | 00266
EP2_PMM_3_Faza1_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D1
EP2_PMM_3_Faza1_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D2
EP2_PMM_3_Faza1_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D3
EP2_PMM_3_Faza1_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D4
EP2_PMM_3_Faza1_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D5
EP2_PMM_3_Faza1_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D6
EP2_PMM_3_Faza1_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D7
EP2_PMM_3_Faza1_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D8
EP2_PMM_3_Faza1_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D9
EP2_PMM_3_Faza1_Tok10_nad80 | DIGITAL | IOD_EP2_disk | D10
EP2_PMM_3_Faza1_Tok11_nad80 | DIGITAL | IOD_EP2_disk | D11
EP2_PMM_3_Faza1_Tok12_nad80 | DIGITAL | IOD_EP2_disk | D12
EP2_PMM_3_Faza1_Tok13_nad80 | DIGITAL | IOD_EP2_disk | D13
EP2_PMM_3_Faza1_Tok14_nad80 | DIGITAL | IOD_EP2_disk | D14
EP2_PMM_3_Faza1_Tok15_nad80 | DIGITAL | IOD_EP2_disk | D15
EP2_PMM_3_Faza1_Tok16_nad80 | DIGITAL | IOD_EP2_disk | D16
EP2_PMM_3_Faza1_Tok17_nad80 | DIGITAL | IOD_EP2_disk | D17
EP2_PMM_3_Faza1_Tok18_nad80 | DIGITAL | IOD_EP2_disk | D18
EP2_PMM_3_Faza1_Tok19_nad80 | DIGITAL | IOD_EP2_disk | D19
EP2_PMM_3_Faza1_Tok20_nad80 | DIGITAL | IOD_EP2_disk | D20
EP2_PMM_3_Faza1_Tok21_nad80 | DIGITAL | IOD_EP2_disk | D21
EP2_PMM_3_Faza1_Tok22_nad80 | DIGITAL | IOD_EP2_disk | D22
EP2_PMM_3_Faza1_Tok23_nad80 | DIGITAL | IOD_EP2_disk | D23
EP2_PMM_3_Faza1_Tok24_nad80 | DIGITAL | IOD_EP2_disk | D24
EP2_PMM_3_Faza1_Tok25_nad80 | DIGITAL | IOD_EP2_disk | D25
EP2_PMM_3_Faza1_Tok26_nad80 | DIGITAL | IOD_EP2_disk | D26
EP2_PMM_3_Faza1_Tok27_nad80 | DIGITAL | IOD_EP2_disk | D27
EP2_PMM_3_Faza1_Tok28_nad80 | DIGITAL | IOD_EP2_disk | D28
EP2_PMM_3_Faza1_Tok29_nad80 | DIGITAL | IOD_EP2_disk | D29
EP2_PMM_3_Faza1_Tok30_nad80 | DIGITAL | IOD_EP2_disk | D30
EP2_PMM_3_Faza1_Tok31_nad80 | DIGITAL | IOD_EP2_disk | D31
EP2_PMM_3_Faza1_Tok32_nad80 | DIGITAL | IOD_EP2_disk | D32
EP2_PMM_3_Faza1_Tok33_nad80 | DIGITAL | IOD_EP2_disk | D33
EP2_PMM_3_Faza1_Tok34_nad80 | DIGITAL | IOD_EP2_disk | D34
EP2_PMM_3_Faza1_Tok35_nad80 | DIGITAL | IOD_EP2_disk | D35
EP2_PMM_3_Faza1_Tok36_nad80 | DIGITAL | IOD_EP2_disk | D36
EP2_PMM_3_Faza1_Tok37_nad80 | DIGITAL | IOD_EP2_disk | D37
EP2_PMM_3_Faza1_Tok38_nad80 | DIGITAL | IOD_EP2_disk | D38
EP2_PMM_3_Faza1_Tok39_nad80 | DIGITAL | IOD_EP2_disk | D39
EP2_PMM_3_Faza1_Tok40_nad80 | DIGITAL | IOD_EP2_disk | D40
EP2_PMM_3_Faza1_Tok41_nad80 | DIGITAL | IOD_EP2_disk | D41
EP2_PMM_3_Faza1_Tok42_nad80 | DIGITAL | IOD_EP2_disk | D42
EP2_PMM_3_Faza2_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D43
EP2_PMM_3_Faza2_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D44
EP2_PMM_3_Faza2_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D45
EP2_PMM_3_Faza2_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D46
EP2_PMM_3_Faza2_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D47
EP2_PMM_3_Faza2_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D48
EP2_PMM_3_Faza2_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D49
EP2_PMM_3_Faza2_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D50
EP2_PMM_3_Faza2_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D51
EP2_PMM_3_Faza2_Tok10_nad80 | DIGITAL | IOD_EP2_disk | D52
EP2_PMM_3_Faza2_Tok11_nad80 | DIGITAL | IOD_EP2_disk | D53
EP2_PMM_3_Faza2_Tok12_nad80 | DIGITAL | IOD_EP2_disk | D54
EP2_PMM_3_Faza2_Tok13_nad80 | DIGITAL | IOD_EP2_disk | D55
EP2_PMM_3_Faza2_Tok14_nad80 | DIGITAL | IOD_EP2_disk | D56
EP2_PMM_3_Faza2_Tok15_nad80 | DIGITAL | IOD_EP2_disk | D57
EP2_PMM_3_Faza2_Tok16_nad80 | DIGITAL | IOD_EP2_disk | D58
EP2_PMM_3_Faza2_Tok17_nad80 | DIGITAL | IOD_EP2_disk | D59
EP2_PMM_3_Faza2_Tok18_nad80 | DIGITAL | IOD_EP2_disk | D60
EP2_PMM_3_Faza2_Tok19_nad80 | DIGITAL | IOD_EP2_disk | D61
EP2_PMM_3_Faza2_Tok20_nad80 | DIGITAL | IOD_EP2_disk | D62
EP2_PMM_3_Faza2_Tok21_nad80 | DIGITAL | IOD_EP2_disk | D63
EP2_PMM_3_Faza2_Tok22_nad80 | DIGITAL | IOD_EP2_disk | D64
EP2_PMM_3_Faza2_Tok23_nad80 | DIGITAL | IOD_EP2_disk | D65
EP2_PMM_3_Faza2_Tok24_nad80 | DIGITAL | IOD_EP2_disk | D66
EP2_PMM_3_Faza2_Tok25_nad80 | DIGITAL | IOD_EP2_disk | D67
EP2_PMM_3_Faza2_Tok26_nad80 | DIGITAL | IOD_EP2_disk | D68
EP2_PMM_3_Faza2_Tok27_nad80 | DIGITAL | IOD_EP2_disk | D69
EP2_PMM_3_Faza2_Tok28_nad80 | DIGITAL | IOD_EP2_disk | D70
EP2_PMM_3_Faza2_Tok29_nad80 | DIGITAL | IOD_EP2_disk | D71
EP2_PMM_3_Faza2_Tok30_nad80 | DIGITAL | IOD_EP2_disk | D72
EP2_PMM_3_Faza2_Tok31_nad80 | DIGITAL | IOD_EP2_disk | D73
EP2_PMM_3_Faza2_Tok32_nad80 | DIGITAL | IOD_EP2_disk | D74
EP2_PMM_3_Faza2_Tok33_nad80 | DIGITAL | IOD_EP2_disk | D75
EP2_PMM_3_Faza2_Tok34_nad80 | DIGITAL | IOD_EP2_disk | D76
EP2_PMM_3_Faza2_Tok35_nad80 | DIGITAL | IOD_EP2_disk | D77
EP2_PMM_3_Faza2_Tok36_nad80 | DIGITAL | IOD_EP2_disk | D78
EP2_PMM_3_Faza2_Tok37_nad80 | DIGITAL | IOD_EP2_disk | D79
EP2_PMM_3_Faza2_Tok38_nad80 | DIGITAL | IOD_EP2_disk | D80
EP2_PMM_3_Faza2_Tok39_nad80 | DIGITAL | IOD_EP2_disk | D81
EP2_PMM_3_Faza2_Tok40_nad80 | DIGITAL | IOD_EP2_disk | D82
EP2_PMM_3_Faza2_Tok41_nad80 | DIGITAL | IOD_EP2_disk | D83
EP2_PMM_3_Faza2_Tok42_nad80 | DIGITAL | IOD_EP2_disk | D84
EP2_PMM_3_Faza3_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D85
EP2_PMM_3_Faza3_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D86
EP2_PMM_3_Faza3_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D87
EP2_PMM_3_Faza3_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D88
EP2_PMM_3_Faza3_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D89
EP2_PMM_3_Faza3_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D90
EP2_PMM_3_Faza3_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D91
EP2_PMM_3_Faza3_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D92
EP2_PMM_3_Faza3_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D93
EP2_PMM_3_Faza3_Tok10_nad80 | DIGITAL | IOD_EP2_disk | D94
EP2_PMM_3_Faza3_Tok11_nad80 | DIGITAL | IOD_EP2_disk | D95
EP2_PMM_3_Faza3_Tok12_nad80 | DIGITAL | IOD_EP2_disk | D96
EP2_PMM_3_Faza3_Tok13_nad80 | DIGITAL | IOD_EP2_disk | D97
EP2_PMM_3_Faza3_Tok14_nad80 | DIGITAL | IOD_EP2_disk | D98
EP2_PMM_3_Faza3_Tok15_nad80 | DIGITAL | IOD_EP2_disk | D99
EP2_PMM_3_Faza3_Tok16_nad80 | DIGITAL | IOD_EP2_disk | D100
EP2_PMM_3_Faza3_Tok17_nad80 | DIGITAL | IOD_EP2_disk | D101
EP2_PMM_3_Faza3_Tok18_nad80 | DIGITAL | IOD_EP2_disk | D102
EP2_PMM_3_Faza3_Tok19_nad80 | DIGITAL | IOD_EP2_disk | D103
EP2_PMM_3_Faza3_Tok20_nad80 | DIGITAL | IOD_EP2_disk | D104
EP2_PMM_3_Faza3_Tok21_nad80 | DIGITAL | IOD_EP2_disk | D105
EP2_PMM_3_Faza3_Tok22_nad80 | DIGITAL | IOD_EP2_disk | D106
EP2_PMM_3_Faza3_Tok23_nad80 | DIGITAL | IOD_EP2_disk | D107
EP2_PMM_3_Faza3_Tok24_nad80 | DIGITAL | IOD_EP2_disk | D108
EP2_PMM_3_Faza3_Tok25_nad80 | DIGITAL | IOD_EP2_disk | D109
EP2_PMM_3_Faza3_Tok26_nad80 | DIGITAL | IOD_EP2_disk | D110
EP2_PMM_3_Faza3_Tok27_nad80 | DIGITAL | IOD_EP2_disk | D111
EP2_PMM_3_Faza3_Tok28_nad80 | DIGITAL | IOD_EP2_disk | D112
EP2_PMM_3_Faza3_Tok29_nad80 | DIGITAL | IOD_EP2_disk | D113
EP2_PMM_3_Faza3_Tok30_nad80 | DIGITAL | IOD_EP2_disk | D114
EP2_PMM_3_Faza3_Tok31_nad80 | DIGITAL | IOD_EP2_disk | D115
EP2_PMM_3_Faza3_Tok32_nad80 | DIGITAL | IOD_EP2_disk | D116
EP2_PMM_3_Faza3_Tok33_nad80 | DIGITAL | IOD_EP2_disk | D117
EP2_PMM_3_Faza3_Tok34_nad80 | DIGITAL | IOD_EP2_disk | D118
EP2_PMM_3_Faza3_Tok35_nad80 | DIGITAL | IOD_EP2_disk | D119
EP2_PMM_3_Faza3_Tok36_nad80 | DIGITAL | IOD_EP2_disk | D120
EP2_PMM_3_Faza3_Tok37_nad80 | DIGITAL | IOD_EP2_disk | D121
EP2_PMM_3_Faza3_Tok38_nad80 | DIGITAL | IOD_EP2_disk | D122
EP2_PMM_3_Faza3_Tok39_nad80 | DIGITAL | IOD_EP2_disk | D123
EP2_PMM_3_Faza3_Tok40_nad80 | DIGITAL | IOD_EP2_disk | D124
EP2_PMM_3_Faza3_Tok41_nad80 | DIGITAL | IOD_EP2_disk | D125
EP2_PMM_3_Faza3_Tok42_nad80 | DIGITAL | IOD_EP2_disk | D126
EP2_PMM_3_Faza1_Tok01_med60in80 | DIGITAL | IOD_EP2_disk | D127
EP2_PMM_3_Faza1_Tok02_med60in80 | DIGITAL | IOD_EP2_disk | D128
EP2_PMM_3_Faza1_Tok03_med60in80 | DIGITAL | IOD_EP2_disk | D129
EP2_PMM_3_Faza1_Tok04_med60in80 | DIGITAL | IOD_EP2_disk | D130
EP2_PMM_3_Faza1_Tok05_med60in80 | DIGITAL | IOD_EP2_disk | D131
EP2_PMM_3_Faza1_Tok06_med60in80 | DIGITAL | IOD_EP2_disk | D132
EP2_PMM_3_Faza1_Tok07_med60in80 | DIGITAL | IOD_EP2_disk | D133
EP2_PMM_3_Faza1_Tok08_med60in80 | DIGITAL | IOD_EP2_disk | D134
EP2_PMM_3_Faza1_Tok09_med60in80 | DIGITAL | IOD_EP2_disk | D135
EP2_PMM_3_Faza1_Tok10_med60in80 | DIGITAL | IOD_EP2_disk | D136
EP2_PMM_3_Faza1_Tok11_med60in80 | DIGITAL | IOD_EP2_disk | D137
EP2_PMM_3_Faza1_Tok12_med60in80 | DIGITAL | IOD_EP2_disk | D138
EP2_PMM_3_Faza1_Tok13_med60in80 | DIGITAL | IOD_EP2_disk | D139
EP2_PMM_3_Faza1_Tok14_med60in80 | DIGITAL | IOD_EP2_disk | D140
EP2_PMM_3_Faza1_Tok15_med60in80 | DIGITAL | IOD_EP2_disk | D141
EP2_PMM_3_Faza1_Tok16_med60in80 | DIGITAL | IOD_EP2_disk | D142
EP2_PMM_3_Faza1_Tok17_med60in80 | DIGITAL | IOD_EP2_disk | D143
EP2_PMM_3_Faza1_Tok18_med60in80 | DIGITAL | IOD_EP2_disk | D144
EP2_PMM_3_Faza1_Tok19_med60in80 | DIGITAL | IOD_EP2_disk | D145
EP2_PMM_3_Faza1_Tok20_med60in80 | DIGITAL | IOD_EP2_disk | D146
EP2_PMM_3_Faza1_Tok21_med60in80 | DIGITAL | IOD_EP2_disk | D147
EP2_PMM_3_Faza1_Tok22_med60in80 | DIGITAL | IOD_EP2_disk | D148
EP2_PMM_3_Faza1_Tok23_med60in80 | DIGITAL | IOD_EP2_disk | D149
EP2_PMM_3_Faza1_Tok24_med60in80 | DIGITAL | IOD_EP2_disk | D150
EP2_PMM_3_Faza1_Tok25_med60in80 | DIGITAL | IOD_EP2_disk | D151
EP2_PMM_3_Faza1_Tok26_med60in80 | DIGITAL | IOD_EP2_disk | D152
EP2_PMM_3_Faza1_Tok27_med60in80 | DIGITAL | IOD_EP2_disk | D153
EP2_PMM_3_Faza1_Tok28_med60in80 | DIGITAL | IOD_EP2_disk | D154
EP2_PMM_3_Faza1_Tok29_med60in80 | DIGITAL | IOD_EP2_disk | D155
EP2_PMM_3_Faza1_Tok30_med60in80 | DIGITAL | IOD_EP2_disk | D156
EP2_PMM_3_Faza1_Tok31_med60in80 | DIGITAL | IOD_EP2_disk | D157
EP2_PMM_3_Faza1_Tok32_med60in80 | DIGITAL | IOD_EP2_disk | D158
EP2_PMM_3_Faza1_Tok33_med60in80 | DIGITAL | IOD_EP2_disk | D159
EP2_PMM_3_Faza1_Tok34_med60in80 | DIGITAL | IOD_EP2_disk | D160
EP2_PMM_3_Faza1_Tok35_med60in80 | DIGITAL | IOD_EP2_disk | D161
EP2_PMM_3_Faza1_Tok36_med60in80 | DIGITAL | IOD_EP2_disk | D162
EP2_PMM_3_Faza1_Tok37_med60in80 | DIGITAL | IOD_EP2_disk | D163
EP2_PMM_3_Faza1_Tok38_med60in80 | DIGITAL | IOD_EP2_disk | D164
EP2_PMM_3_Faza1_Tok39_med60in80 | DIGITAL | IOD_EP2_disk | D165
EP2_PMM_3_Faza1_Tok40_med60in80 | DIGITAL | IOD_EP2_disk | D166
EP2_PMM_3_Faza1_Tok41_med60in80 | DIGITAL | IOD_EP2_disk | D167
EP2_PMM_3_Faza1_Tok42_med60in80 | DIGITAL | IOD_EP2_disk | D168
EP2_PMM_3_Faza2_Tok01_med60in80 | DIGITAL | IOD_EP2_disk | D169
EP2_PMM_3_Faza2_Tok02_med60in80 | DIGITAL | IOD_EP2_disk | D170
EP2_PMM_3_Faza2_Tok03_med60in80 | DIGITAL | IOD_EP2_disk | D171
EP2_PMM_3_Faza2_Tok04_med60in80 | DIGITAL | IOD_EP2_disk | D172
EP2_PMM_3_Faza2_Tok05_med60in80 | DIGITAL | IOD_EP2_disk | D173
EP2_PMM_3_Faza2_Tok06_med60in80 | DIGITAL | IOD_EP2_disk | D174
EP2_PMM_3_Faza2_Tok07_med60in80 | DIGITAL | IOD_EP2_disk | D175
EP2_PMM_3_Faza2_Tok08_med60in80 | DIGITAL | IOD_EP2_disk | D176
EP2_PMM_3_Faza2_Tok09_med60in80 | DIGITAL | IOD_EP2_disk | D177
EP2_PMM_3_Faza2_Tok10_med60in80 | DIGITAL | IOD_EP2_disk | D178
EP2_PMM_3_Faza2_Tok11_med60in80 | DIGITAL | IOD_EP2_disk | D179
EP2_PMM_3_Faza2_Tok12_med60in80 | DIGITAL | IOD_EP2_disk | D180
EP2_PMM_3_Faza2_Tok13_med60in80 | DIGITAL | IOD_EP2_disk | D181
EP2_PMM_3_Faza2_Tok14_med60in80 | DIGITAL | IOD_EP2_disk | D182
EP2_PMM_3_Faza2_Tok15_med60in80 | DIGITAL | IOD_EP2_disk | D183
EP2_PMM_3_Faza2_Tok16_med60in80 | DIGITAL | IOD_EP2_disk | D184
EP2_PMM_3_Faza2_Tok17_med60in80 | DIGITAL | IOD_EP2_disk | D185
EP2_PMM_3_Faza2_Tok18_med60in80 | DIGITAL | IOD_EP2_disk | D186
EP2_PMM_3_Faza2_Tok19_med60in80 | DIGITAL | IOD_EP2_disk | D187
EP2_PMM_3_Faza2_Tok20_med60in80 | DIGITAL | IOD_EP2_disk | D188
EP2_PMM_3_Faza2_Tok21_med60in80 | DIGITAL | IOD_EP2_disk | D189
EP2_PMM_3_Faza2_Tok22_med60in80 | DIGITAL | IOD_EP2_disk | D190
EP2_PMM_3_Faza2_Tok23_med60in80 | DIGITAL | IOD_EP2_disk | D191
EP2_PMM_3_Faza2_Tok24_med60in80 | DIGITAL | IOD_EP2_disk | D192
EP2_PMM_3_Faza2_Tok25_med60in80 | DIGITAL | IOD_EP2_disk | D193
EP2_PMM_3_Faza2_Tok26_med60in80 | DIGITAL | IOD_EP2_disk | D194
EP2_PMM_3_Faza2_Tok27_med60in80 | DIGITAL | IOD_EP2_disk | D195
EP2_PMM_3_Faza2_Tok28_med60in80 | DIGITAL | IOD_EP2_disk | D196
EP2_PMM_3_Faza2_Tok29_med60in80 | DIGITAL | IOD_EP2_disk | D197
EP2_PMM_3_Faza2_Tok30_med60in80 | DIGITAL | IOD_EP2_disk | D198
EP2_PMM_3_Faza2_Tok31_med60in80 | DIGITAL | IOD_EP2_disk | D199
EP2_PMM_3_Faza2_Tok32_med60in80 | DIGITAL | IOD_EP2_disk | D200
EP2_PMM_3_Faza2_Tok33_med60in80 | DIGITAL | IOD_EP2_disk | D201
EP2_PMM_3_Faza2_Tok34_med60in80 | DIGITAL | IOD_EP2_disk | D202
EP2_PMM_3_Faza2_Tok35_med60in80 | DIGITAL | IOD_EP2_disk | D203
EP2_PMM_3_Faza2_Tok36_med60in80 | DIGITAL | IOD_EP2_disk | D204
EP2_PMM_3_Faza2_Tok37_med60in80 | DIGITAL | IOD_EP2_disk | D205
EP2_PMM_3_Faza2_Tok38_med60in80 | DIGITAL | IOD_EP2_disk | D206
EP2_PMM_3_Faza2_Tok39_med60in80 | DIGITAL | IOD_EP2_disk | D207
EP2_PMM_3_Faza2_Tok40_med60in80 | DIGITAL | IOD_EP2_disk | D208
EP2_PMM_3_Faza2_Tok41_med60in80 | DIGITAL | IOD_EP2_disk | D209
EP2_PMM_3_Faza2_Tok42_med60in80 | DIGITAL | IOD_EP2_disk | D210
EP2_PMM_3_Faza3_Tok01_med60in80 | DIGITAL | IOD_EP2_disk | D211
EP2_PMM_3_Faza3_Tok02_med60in80 | DIGITAL | IOD_EP2_disk | D212
EP2_PMM_3_Faza3_Tok03_med60in80 | DIGITAL | IOD_EP2_disk | D213
EP2_PMM_3_Faza3_Tok04_med60in80 | DIGITAL | IOD_EP2_disk | D214
EP2_PMM_3_Faza3_Tok05_med60in80 | DIGITAL | IOD_EP2_disk | D215
EP2_PMM_3_Faza3_Tok06_med60in80 | DIGITAL | IOD_EP2_disk | D216
EP2_PMM_3_Faza3_Tok07_med60in80 | DIGITAL | IOD_EP2_disk | D217
EP2_PMM_3_Faza3_Tok08_med60in80 | DIGITAL | IOD_EP2_disk | D218
EP2_PMM_3_Faza3_Tok09_med60in80 | DIGITAL | IOD_EP2_disk | D219
EP2_PMM_3_Faza3_Tok10_med60in80 | DIGITAL | IOD_EP2_disk | D220
EP2_PMM_3_Faza3_Tok11_med60in80 | DIGITAL | IOD_EP2_disk | D221
EP2_PMM_3_Faza3_Tok12_med60in80 | DIGITAL | IOD_EP2_disk | D222
EP2_PMM_3_Faza3_Tok13_med60in80 | DIGITAL | IOD_EP2_disk | D223
EP2_PMM_3_Faza3_Tok14_med60in80 | DIGITAL | IOD_EP2_disk | D224
EP2_PMM_3_Faza3_Tok15_med60in80 | DIGITAL | IOD_EP2_disk | D225
EP2_PMM_3_Faza3_Tok16_med60in80 | DIGITAL | IOD_EP2_disk | D226
EP2_PMM_3_Faza3_Tok17_med60in80 | DIGITAL | IOD_EP2_disk | D227
EP2_PMM_3_Faza3_Tok18_med60in80 | DIGITAL | IOD_EP2_disk | D228
EP2_PMM_3_Faza3_Tok19_med60in80 | DIGITAL | IOD_EP2_disk | D229
EP2_PMM_3_Faza3_Tok20_med60in80 | DIGITAL | IOD_EP2_disk | D230
EP2_PMM_3_Faza3_Tok21_med60in80 | DIGITAL | IOD_EP2_disk | D231
EP2_PMM_3_Faza3_Tok22_med60in80 | DIGITAL | IOD_EP2_disk | D232
EP2_PMM_3_Faza3_Tok23_med60in80 | DIGITAL | IOD_EP2_disk | D233
EP2_PMM_3_Faza3_Tok24_med60in80 | DIGITAL | IOD_EP2_disk | D234
EP2_PMM_3_Faza3_Tok25_med60in80 | DIGITAL | IOD_EP2_disk | D235
EP2_PMM_3_Faza3_Tok26_med60in80 | DIGITAL | IOD_EP2_disk | D236
EP2_PMM_3_Faza3_Tok27_med60in80 | DIGITAL | IOD_EP2_disk | D237
EP2_PMM_3_Faza3_Tok28_med60in80 | DIGITAL | IOD_EP2_disk | D238
EP2_PMM_3_Faza3_Tok29_med60in80 | DIGITAL | IOD_EP2_disk | D239
EP2_PMM_3_Faza3_Tok30_med60in80 | DIGITAL | IOD_EP2_disk | D240
EP2_PMM_3_Faza3_Tok31_med60in80 | DIGITAL | IOD_EP2_disk | D241
EP2_PMM_3_Faza3_Tok32_med60in80 | DIGITAL | IOD_EP2_disk | D242
EP2_PMM_3_Faza3_Tok33_med60in80 | DIGITAL | IOD_EP2_disk | D243
EP2_PMM_3_Faza3_Tok34_med60in80 | DIGITAL | IOD_EP2_disk | D244
EP2_PMM_3_Faza3_Tok35_med60in80 | DIGITAL | IOD_EP2_disk | D245
EP2_PMM_3_Faza3_Tok36_med60in80 | DIGITAL | IOD_EP2_disk | D246
EP2_PMM_3_Faza3_Tok37_med60in80 | DIGITAL | IOD_EP2_disk | D247
EP2_PMM_3_Faza3_Tok38_med60in80 | DIGITAL | IOD_EP2_disk | D248
EP2_PMM_3_Faza3_Tok39_med60in80 | DIGITAL | IOD_EP2_disk | D249
EP2_PMM_3_Faza3_Tok40_med60in80 | DIGITAL | IOD_EP2_disk | D250
EP2_PMM_3_Faza3_Tok41_med60in80 | DIGITAL | IOD_EP2_disk | D251
EP2_PMM_3_Faza3_Tok42_med60in80 | DIGITAL | IOD_EP2_disk | D252
EP2_PMM_2_Faza1_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D253
EP2_PMM_2_Faza1_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D254
EP2_PMM_2_Faza1_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D255
EP2_PMM_2_Faza1_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D256
EP2_PMM_2_Faza1_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D257
EP2_PMM_2_Faza1_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D258
EP2_PMM_2_Faza1_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D259
EP2_PMM_2_Faza1_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D260
EP2_PMM_2_Faza1_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D261
EP2_PMM_2_Faza1_Tok10_nad80 | DIGITAL | IOD_EP2_disk | D262
EP2_PMM_2_Faza1_Tok11_nad80 | DIGITAL | IOD_EP2_disk | D263
EP2_PMM_2_Faza1_Tok12_nad80 | DIGITAL | IOD_EP2_disk | D264
EP2_PMM_2_Faza1_Tok13_nad80 | DIGITAL | IOD_EP2_disk | D265
EP2_PMM_2_Faza1_Tok14_nad80 | DIGITAL | IOD_EP2_disk | D266
EP2_PMM_2_Faza1_Tok15_nad80 | DIGITAL | IOD_EP2_disk | D267
EP2_PMM_2_Faza1_Tok16_nad80 | DIGITAL | IOD_EP2_disk | D268
EP2_PMM_2_Faza1_Tok17_nad80 | DIGITAL | IOD_EP2_disk | D269
EP2_PMM_2_Faza1_Tok18_nad80 | DIGITAL | IOD_EP2_disk | D270
EP2_PMM_2_Faza1_Tok19_nad80 | DIGITAL | IOD_EP2_disk | D271
EP2_PMM_2_Faza1_Tok20_nad80 | DIGITAL | IOD_EP2_disk | D272
EP2_PMM_2_Faza1_Tok21_nad80 | DIGITAL | IOD_EP2_disk | D273
EP2_PMM_2_Faza1_Tok22_nad80 | DIGITAL | IOD_EP2_disk | D274
EP2_PMM_2_Faza1_Tok23_nad80 | DIGITAL | IOD_EP2_disk | D275
EP2_PMM_2_Faza1_Tok24_nad80 | DIGITAL | IOD_EP2_disk | D276
EP2_PMM_2_Faza1_Tok25_nad80 | DIGITAL | IOD_EP2_disk | D277
EP2_PMM_2_Faza1_Tok26_nad80 | DIGITAL | IOD_EP2_disk | D278
EP2_PMM_2_Faza1_Tok27_nad80 | DIGITAL | IOD_EP2_disk | D279
EP2_PMM_2_Faza1_Tok28_nad80 | DIGITAL | IOD_EP2_disk | D280
EP2_PMM_2_Faza1_Tok29_nad80 | DIGITAL | IOD_EP2_disk | D281
EP2_PMM_2_Faza1_Tok30_nad80 | DIGITAL | IOD_EP2_disk | D282
EP2_PMM_2_Faza1_Tok31_nad80 | DIGITAL | IOD_EP2_disk | D283
EP2_PMM_2_Faza1_Tok32_nad80 | DIGITAL | IOD_EP2_disk | D284
EP2_PMM_2_Faza1_Tok33_nad80 | DIGITAL | IOD_EP2_disk | D285
EP2_PMM_2_Faza1_Tok34_nad80 | DIGITAL | IOD_EP2_disk | D286
EP2_PMM_2_Faza1_Tok35_nad80 | DIGITAL | IOD_EP2_disk | D287
EP2_PMM_2_Faza1_Tok36_nad80 | DIGITAL | IOD_EP2_disk | D288
EP2_PMM_2_Faza1_Tok37_nad80 | DIGITAL | IOD_EP2_disk | D289
EP2_PMM_2_Faza1_Tok38_nad80 | DIGITAL | IOD_EP2_disk | D290
EP2_PMM_2_Faza1_Tok39_nad80 | DIGITAL | IOD_EP2_disk | D291
EP2_PMM_2_Faza1_Tok40_nad80 | DIGITAL | IOD_EP2_disk | D292
EP2_PMM_2_Faza1_Tok41_nad80 | DIGITAL | IOD_EP2_disk | D293
EP2_PMM_2_Faza1_Tok42_nad80 | DIGITAL | IOD_EP2_disk | D294
EP2_PMM_2_Faza2_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D295
EP2_PMM_2_Faza2_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D296
EP2_PMM_2_Faza2_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D297
EP2_PMM_2_Faza2_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D298
EP2_PMM_2_Faza2_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D299
EP2_PMM_2_Faza2_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D300
EP2_PMM_2_Faza2_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D301
EP2_PMM_2_Faza2_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D302
EP2_PMM_2_Faza2_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D303
EP2_PMM_2_Faza2_Tok10_nad80 | DIGITAL | IOD_EP2_disk | D304
EP2_PMM_2_Faza2_Tok11_nad80 | DIGITAL | IOD_EP2_disk | D305
EP2_PMM_2_Faza2_Tok12_nad80 | DIGITAL | IOD_EP2_disk | D306
EP2_PMM_2_Faza2_Tok13_nad80 | DIGITAL | IOD_EP2_disk | D307
EP2_PMM_2_Faza2_Tok14_nad80 | DIGITAL | IOD_EP2_disk | D308
EP2_PMM_2_Faza2_Tok15_nad80 | DIGITAL | IOD_EP2_disk | D309
EP2_PMM_2_Faza2_Tok16_nad80 | DIGITAL | IOD_EP2_disk | D310
EP2_PMM_2_Faza2_Tok17_nad80 | DIGITAL | IOD_EP2_disk | D311
EP2_PMM_2_Faza2_Tok18_nad80 | DIGITAL | IOD_EP2_disk | D312
EP2_PMM_2_Faza2_Tok19_nad80 | DIGITAL | IOD_EP2_disk | D313
EP2_PMM_2_Faza2_Tok20_nad80 | DIGITAL | IOD_EP2_disk | D314
EP2_PMM_2_Faza2_Tok21_nad80 | DIGITAL | IOD_EP2_disk | D315
EP2_PMM_2_Faza2_Tok22_nad80 | DIGITAL | IOD_EP2_disk | D316
EP2_PMM_2_Faza2_Tok23_nad80 | DIGITAL | IOD_EP2_disk | D317
EP2_PMM_2_Faza2_Tok24_nad80 | DIGITAL | IOD_EP2_disk | D318
EP2_PMM_2_Faza2_Tok25_nad80 | DIGITAL | IOD_EP2_disk | D319
EP2_PMM_2_Faza2_Tok26_nad80 | DIGITAL | IOD_EP2_disk | D320
EP2_PMM_2_Faza2_Tok27_nad80 | DIGITAL | IOD_EP2_disk | D321
EP2_PMM_2_Faza2_Tok28_nad80 | DIGITAL | IOD_EP2_disk | D322
EP2_PMM_2_Faza2_Tok29_nad80 | DIGITAL | IOD_EP2_disk | D323
EP2_PMM_2_Faza2_Tok30_nad80 | DIGITAL | IOD_EP2_disk | D324
EP2_PMM_2_Faza2_Tok31_nad80 | DIGITAL | IOD_EP2_disk | D325
EP2_PMM_2_Faza2_Tok32_nad80 | DIGITAL | IOD_EP2_disk | D326
EP2_PMM_2_Faza2_Tok33_nad80 | DIGITAL | IOD_EP2_disk | D327
EP2_PMM_2_Faza2_Tok34_nad80 | DIGITAL | IOD_EP2_disk | D328
EP2_PMM_2_Faza2_Tok35_nad80 | DIGITAL | IOD_EP2_disk | D329
EP2_PMM_2_Faza2_Tok36_nad80 | DIGITAL | IOD_EP2_disk | D330
EP2_PMM_2_Faza2_Tok37_nad80 | DIGITAL | IOD_EP2_disk | D331
EP2_PMM_2_Faza2_Tok38_nad80 | DIGITAL | IOD_EP2_disk | D332
EP2_PMM_2_Faza2_Tok39_nad80 | DIGITAL | IOD_EP2_disk | D333
EP2_PMM_2_Faza2_Tok40_nad80 | DIGITAL | IOD_EP2_disk | D334
EP2_PMM_2_Faza2_Tok41_nad80 | DIGITAL | IOD_EP2_disk | D335
EP2_PMM_2_Faza2_Tok42_nad80 | DIGITAL | IOD_EP2_disk | D336
EP2_PMM_2_Faza3_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D337
EP2_PMM_2_Faza3_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D338
EP2_PMM_2_Faza3_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D339
EP2_PMM_2_Faza3_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D340
EP2_PMM_2_Faza3_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D341
EP2_PMM_2_Faza3_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D342
EP2_PMM_2_Faza3_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D343
EP2_PMM_2_Faza3_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D344
EP2_PMM_2_Faza3_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D345
EP2_PMM_2_Faza3_Tok10_nad80 | DIGITAL | IOD_EP2_disk | D346
EP2_PMM_2_Faza3_Tok11_nad80 | DIGITAL | IOD_EP2_disk | D347
EP2_PMM_2_Faza3_Tok12_nad80 | DIGITAL | IOD_EP2_disk | D348
EP2_PMM_2_Faza3_Tok13_nad80 | DIGITAL | IOD_EP2_disk | D349
EP2_PMM_2_Faza3_Tok14_nad80 | DIGITAL | IOD_EP2_disk | D350
EP2_PMM_2_Faza3_Tok15_nad80 | DIGITAL | IOD_EP2_disk | D351
EP2_PMM_2_Faza3_Tok16_nad80 | DIGITAL | IOD_EP2_disk | D352
EP2_PMM_2_Faza3_Tok17_nad80 | DIGITAL | IOD_EP2_disk | D353
EP2_PMM_2_Faza3_Tok18_nad80 | DIGITAL | IOD_EP2_disk | D354
EP2_PMM_2_Faza3_Tok19_nad80 | DIGITAL | IOD_EP2_disk | D355
EP2_PMM_2_Faza3_Tok20_nad80 | DIGITAL | IOD_EP2_disk | D356
EP2_PMM_2_Faza3_Tok21_nad80 | DIGITAL | IOD_EP2_disk | D357
EP2_PMM_2_Faza3_Tok22_nad80 | DIGITAL | IOD_EP2_disk | D358
EP2_PMM_2_Faza3_Tok23_nad80 | DIGITAL | IOD_EP2_disk | D359
EP2_PMM_2_Faza3_Tok24_nad80 | DIGITAL | IOD_EP2_disk | D360
EP2_PMM_2_Faza3_Tok25_nad80 | DIGITAL | IOD_EP2_disk | D361
EP2_PMM_2_Faza3_Tok26_nad80 | DIGITAL | IOD_EP2_disk | D362
EP2_PMM_2_Faza3_Tok27_nad80 | DIGITAL | IOD_EP2_disk | D363
EP2_PMM_2_Faza3_Tok28_nad80 | DIGITAL | IOD_EP2_disk | D364
EP2_PMM_2_Faza3_Tok29_nad80 | DIGITAL | IOD_EP2_disk | D365
EP2_PMM_2_Faza3_Tok30_nad80 | DIGITAL | IOD_EP2_disk | D366
EP2_PMM_2_Faza3_Tok31_nad80 | DIGITAL | IOD_EP2_disk | D367
EP2_PMM_2_Faza3_Tok32_nad80 | DIGITAL | IOD_EP2_disk | D368
EP2_PMM_2_Faza3_Tok33_nad80 | DIGITAL | IOD_EP2_disk | D369
EP2_PMM_2_Faza3_Tok34_nad80 | DIGITAL | IOD_EP2_disk | D370
EP2_PMM_2_Faza3_Tok35_nad80 | DIGITAL | IOD_EP2_disk | D371
EP2_PMM_2_Faza3_Tok36_nad80 | DIGITAL | IOD_EP2_disk | D372
EP2_PMM_2_Faza3_Tok37_nad80 | DIGITAL | IOD_EP2_disk | D373
EP2_PMM_2_Faza3_Tok38_nad80 | DIGITAL | IOD_EP2_disk | D374
EP2_PMM_2_Faza3_Tok39_nad80 | DIGITAL | IOD_EP2_disk | D375
EP2_PMM_2_Faza3_Tok40_nad80 | DIGITAL | IOD_EP2_disk | D376
EP2_PMM_2_Faza3_Tok41_nad80 | DIGITAL | IOD_EP2_disk | D377
EP2_PMM_2_Faza3_Tok42_nad80 | DIGITAL | IOD_EP2_disk | D378
EP2_PMM_2_Faza1_Tok01_med60in80 | DIGITAL | IOD_EP2_disk | D379
EP2_PMM_2_Faza1_Tok02_med60in80 | DIGITAL | IOD_EP2_disk | D380
EP2_PMM_2_Faza1_Tok03_med60in80 | DIGITAL | IOD_EP2_disk | D381
EP2_PMM_2_Faza1_Tok04_med60in80 | DIGITAL | IOD_EP2_disk | D382
EP2_PMM_2_Faza1_Tok05_med60in80 | DIGITAL | IOD_EP2_disk | D383
EP2_PMM_2_Faza1_Tok06_med60in80 | DIGITAL | IOD_EP2_disk | D384
EP2_PMM_2_Faza1_Tok07_med60in80 | DIGITAL | IOD_EP2_disk | D385
EP2_PMM_2_Faza1_Tok08_med60in80 | DIGITAL | IOD_EP2_disk | D386
EP2_PMM_2_Faza1_Tok09_med60in80 | DIGITAL | IOD_EP2_disk | D387
EP2_PMM_2_Faza1_Tok10_med60in80 | DIGITAL | IOD_EP2_disk | D388
EP2_PMM_2_Faza1_Tok11_med60in80 | DIGITAL | IOD_EP2_disk | D389
EP2_PMM_2_Faza1_Tok12_med60in80 | DIGITAL | IOD_EP2_disk | D390
EP2_PMM_2_Faza1_Tok13_med60in80 | DIGITAL | IOD_EP2_disk | D391
EP2_PMM_2_Faza1_Tok14_med60in80 | DIGITAL | IOD_EP2_disk | D392
EP2_PMM_2_Faza1_Tok15_med60in80 | DIGITAL | IOD_EP2_disk | D393
EP2_PMM_2_Faza1_Tok16_med60in80 | DIGITAL | IOD_EP2_disk | D394
EP2_PMM_2_Faza1_Tok17_med60in80 | DIGITAL | IOD_EP2_disk | D395
EP2_PMM_2_Faza1_Tok18_med60in80 | DIGITAL | IOD_EP2_disk | D396
EP2_PMM_2_Faza1_Tok19_med60in80 | DIGITAL | IOD_EP2_disk | D397
EP2_PMM_2_Faza1_Tok20_med60in80 | DIGITAL | IOD_EP2_disk | D398
EP2_PMM_2_Faza1_Tok21_med60in80 | DIGITAL | IOD_EP2_disk | D399
EP2_PMM_2_Faza1_Tok22_med60in80 | DIGITAL | IOD_EP2_disk | D400
EP2_PMM_2_Faza1_Tok23_med60in80 | DIGITAL | IOD_EP2_disk | D401
EP2_PMM_2_Faza1_Tok24_med60in80 | DIGITAL | IOD_EP2_disk | D402
EP2_PMM_2_Faza1_Tok25_med60in80 | DIGITAL | IOD_EP2_disk | D403
EP2_PMM_2_Faza1_Tok26_med60in80 | DIGITAL | IOD_EP2_disk | D404
EP2_PMM_2_Faza1_Tok27_med60in80 | DIGITAL | IOD_EP2_disk | D405
EP2_PMM_2_Faza1_Tok28_med60in80 | DIGITAL | IOD_EP2_disk | D406
EP2_PMM_2_Faza1_Tok29_med60in80 | DIGITAL | IOD_EP2_disk | D407
EP2_PMM_2_Faza1_Tok30_med60in80 | DIGITAL | IOD_EP2_disk | D408
EP2_PMM_2_Faza1_Tok31_med60in80 | DIGITAL | IOD_EP2_disk | D409
EP2_PMM_2_Faza1_Tok32_med60in80 | DIGITAL | IOD_EP2_disk | D410
EP2_PMM_2_Faza1_Tok33_med60in80 | DIGITAL | IOD_EP2_disk | D411
EP2_PMM_2_Faza1_Tok34_med60in80 | DIGITAL | IOD_EP2_disk | D412
EP2_PMM_2_Faza1_Tok35_med60in80 | DIGITAL | IOD_EP2_disk | D413
EP2_PMM_2_Faza1_Tok36_med60in80 | DIGITAL | IOD_EP2_disk | D414
EP2_PMM_2_Faza1_Tok37_med60in80 | DIGITAL | IOD_EP2_disk | D415
EP2_PMM_2_Faza1_Tok38_med60in80 | DIGITAL | IOD_EP2_disk | D416
EP2_PMM_2_Faza1_Tok39_med60in80 | DIGITAL | IOD_EP2_disk | D417
EP2_PMM_2_Faza1_Tok40_med60in80 | DIGITAL | IOD_EP2_disk | D418
EP2_PMM_2_Faza1_Tok41_med60in80 | DIGITAL | IOD_EP2_disk | D419
EP2_PMM_2_Faza1_Tok42_med60in80 | DIGITAL | IOD_EP2_disk | D420
EP2_PMM_2_Faza2_Tok01_med60in80 | DIGITAL | IOD_EP2_disk | D421
EP2_PMM_2_Faza2_Tok02_med60in80 | DIGITAL | IOD_EP2_disk | D422
EP2_PMM_2_Faza2_Tok03_med60in80 | DIGITAL | IOD_EP2_disk | D423
EP2_PMM_2_Faza2_Tok04_med60in80 | DIGITAL | IOD_EP2_disk | D424
EP2_PMM_2_Faza2_Tok05_med60in80 | DIGITAL | IOD_EP2_disk | D425
EP2_PMM_2_Faza2_Tok06_med60in80 | DIGITAL | IOD_EP2_disk | D426
EP2_PMM_2_Faza2_Tok07_med60in80 | DIGITAL | IOD_EP2_disk | D427
EP2_PMM_2_Faza2_Tok08_med60in80 | DIGITAL | IOD_EP2_disk | D428
EP2_PMM_2_Faza2_Tok09_med60in80 | DIGITAL | IOD_EP2_disk | D429
EP2_PMM_2_Faza2_Tok10_med60in80 | DIGITAL | IOD_EP2_disk | D430
EP2_PMM_2_Faza2_Tok11_med60in80 | DIGITAL | IOD_EP2_disk | D431
EP2_PMM_2_Faza2_Tok12_med60in80 | DIGITAL | IOD_EP2_disk | D432
EP2_PMM_2_Faza2_Tok13_med60in80 | DIGITAL | IOD_EP2_disk | D433
EP2_PMM_2_Faza2_Tok14_med60in80 | DIGITAL | IOD_EP2_disk | D434
EP2_PMM_2_Faza2_Tok15_med60in80 | DIGITAL | IOD_EP2_disk | D435
EP2_PMM_2_Faza2_Tok16_med60in80 | DIGITAL | IOD_EP2_disk | D436
EP2_PMM_2_Faza2_Tok17_med60in80 | DIGITAL | IOD_EP2_disk | D437
EP2_PMM_2_Faza2_Tok18_med60in80 | DIGITAL | IOD_EP2_disk | D438
EP2_PMM_2_Faza2_Tok19_med60in80 | DIGITAL | IOD_EP2_disk | D439
EP2_PMM_2_Faza2_Tok20_med60in80 | DIGITAL | IOD_EP2_disk | D440
EP2_PMM_2_Faza2_Tok21_med60in80 | DIGITAL | IOD_EP2_disk | D441
EP2_PMM_2_Faza2_Tok22_med60in80 | DIGITAL | IOD_EP2_disk | D442
EP2_PMM_2_Faza2_Tok23_med60in80 | DIGITAL | IOD_EP2_disk | D443
EP2_PMM_2_Faza2_Tok24_med60in80 | DIGITAL | IOD_EP2_disk | D444
EP2_PMM_2_Faza2_Tok25_med60in80 | DIGITAL | IOD_EP2_disk | D445
EP2_PMM_2_Faza2_Tok26_med60in80 | DIGITAL | IOD_EP2_disk | D446
EP2_PMM_2_Faza2_Tok27_med60in80 | DIGITAL | IOD_EP2_disk | D447
EP2_PMM_2_Faza2_Tok28_med60in80 | DIGITAL | IOD_EP2_disk | D448
EP2_PMM_2_Faza2_Tok29_med60in80 | DIGITAL | IOD_EP2_disk | D449
EP2_PMM_2_Faza2_Tok30_med60in80 | DIGITAL | IOD_EP2_disk | D450
EP2_PMM_2_Faza2_Tok31_med60in80 | DIGITAL | IOD_EP2_disk | D451
EP2_PMM_2_Faza2_Tok32_med60in80 | DIGITAL | IOD_EP2_disk | D452
EP2_PMM_2_Faza2_Tok33_med60in80 | DIGITAL | IOD_EP2_disk | D453
EP2_PMM_2_Faza2_Tok34_med60in80 | DIGITAL | IOD_EP2_disk | D454
EP2_PMM_2_Faza2_Tok35_med60in80 | DIGITAL | IOD_EP2_disk | D455
EP2_PMM_2_Faza2_Tok36_med60in80 | DIGITAL | IOD_EP2_disk | D456
EP2_PMM_2_Faza2_Tok37_med60in80 | DIGITAL | IOD_EP2_disk | D457
EP2_PMM_2_Faza2_Tok38_med60in80 | DIGITAL | IOD_EP2_disk | D458
EP2_PMM_2_Faza2_Tok39_med60in80 | DIGITAL | IOD_EP2_disk | D459
EP2_PMM_2_Faza2_Tok40_med60in80 | DIGITAL | IOD_EP2_disk | D460
EP2_PMM_2_Faza2_Tok41_med60in80 | DIGITAL | IOD_EP2_disk | D461
EP2_PMM_2_Faza2_Tok42_med60in80 | DIGITAL | IOD_EP2_disk | D462
EP2_PMM_2_Faza3_Tok01_med60in80 | DIGITAL | IOD_EP2_disk | D463
EP2_PMM_2_Faza3_Tok02_med60in80 | DIGITAL | IOD_EP2_disk | D464
EP2_PMM_2_Faza3_Tok03_med60in80 | DIGITAL | IOD_EP2_disk | D465
EP2_PMM_2_Faza3_Tok04_med60in80 | DIGITAL | IOD_EP2_disk | D466
EP2_PMM_2_Faza3_Tok05_med60in80 | DIGITAL | IOD_EP2_disk | D467
EP2_PMM_2_Faza3_Tok06_med60in80 | DIGITAL | IOD_EP2_disk | D468
EP2_PMM_2_Faza3_Tok07_med60in80 | DIGITAL | IOD_EP2_disk | D469
EP2_PMM_2_Faza3_Tok08_med60in80 | DIGITAL | IOD_EP2_disk | D470
EP2_PMM_2_Faza3_Tok09_med60in80 | DIGITAL | IOD_EP2_disk | D471
EP2_PMM_2_Faza3_Tok10_med60in80 | DIGITAL | IOD_EP2_disk | D472
EP2_PMM_2_Faza3_Tok11_med60in80 | DIGITAL | IOD_EP2_disk | D473
EP2_PMM_2_Faza3_Tok12_med60in80 | DIGITAL | IOD_EP2_disk | D474
EP2_PMM_2_Faza3_Tok13_med60in80 | DIGITAL | IOD_EP2_disk | D475
EP2_PMM_2_Faza3_Tok14_med60in80 | DIGITAL | IOD_EP2_disk | D476
EP2_PMM_2_Faza3_Tok15_med60in80 | DIGITAL | IOD_EP2_disk | D477
EP2_PMM_2_Faza3_Tok16_med60in80 | DIGITAL | IOD_EP2_disk | D478
EP2_PMM_2_Faza3_Tok17_med60in80 | DIGITAL | IOD_EP2_disk | D479
EP2_PMM_2_Faza3_Tok18_med60in80 | DIGITAL | IOD_EP2_disk | D480
EP2_PMM_2_Faza3_Tok19_med60in80 | DIGITAL | IOD_EP2_disk | D481
EP2_PMM_2_Faza3_Tok20_med60in80 | DIGITAL | IOD_EP2_disk | D482
EP2_PMM_2_Faza3_Tok21_med60in80 | DIGITAL | IOD_EP2_disk | D483
EP2_PMM_2_Faza3_Tok22_med60in80 | DIGITAL | IOD_EP2_disk | D484
EP2_PMM_2_Faza3_Tok23_med60in80 | DIGITAL | IOD_EP2_disk | D485
EP2_PMM_2_Faza3_Tok24_med60in80 | DIGITAL | IOD_EP2_disk | D486
EP2_PMM_2_Faza3_Tok25_med60in80 | DIGITAL | IOD_EP2_disk | D487
EP2_PMM_2_Faza3_Tok26_med60in80 | DIGITAL | IOD_EP2_disk | D488
EP2_PMM_2_Faza3_Tok27_med60in80 | DIGITAL | IOD_EP2_disk | D489
EP2_PMM_2_Faza3_Tok28_med60in80 | DIGITAL | IOD_EP2_disk | D490
EP2_PMM_2_Faza3_Tok29_med60in80 | DIGITAL | IOD_EP2_disk | D491
EP2_PMM_2_Faza3_Tok30_med60in80 | DIGITAL | IOD_EP2_disk | D492
EP2_PMM_2_Faza3_Tok31_med60in80 | DIGITAL | IOD_EP2_disk | D493
EP2_PMM_2_Faza3_Tok32_med60in80 | DIGITAL | IOD_EP2_disk | D494
EP2_PMM_2_Faza3_Tok33_med60in80 | DIGITAL | IOD_EP2_disk | D495
EP2_PMM_2_Faza3_Tok34_med60in80 | DIGITAL | IOD_EP2_disk | D496
EP2_PMM_2_Faza3_Tok35_med60in80 | DIGITAL | IOD_EP2_disk | D497
EP2_PMM_2_Faza3_Tok36_med60in80 | DIGITAL | IOD_EP2_disk | D498
EP2_PMM_2_Faza3_Tok37_med60in80 | DIGITAL | IOD_EP2_disk | D499
EP2_PMM_2_Faza3_Tok38_med60in80 | DIGITAL | IOD_EP2_disk | D500
EP2_PMM_2_Faza3_Tok39_med60in80 | DIGITAL | IOD_EP2_disk | D501
EP2_PMM_2_Faza3_Tok40_med60in80 | DIGITAL | IOD_EP2_disk | D502
EP2_PMM_2_Faza3_Tok41_med60in80 | DIGITAL | IOD_EP2_disk | D503
EP2_PMM_2_Faza3_Tok42_med60in80 | DIGITAL | IOD_EP2_disk | D504
EP2_PMM_1_Faza1_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D505
EP2_PMM_1_Faza1_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D506
EP2_PMM_1_Faza1_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D507
EP2_PMM_1_Faza1_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D508
EP2_PMM_1_Faza1_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D509
EP2_PMM_1_Faza1_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D510
EP2_PMM_1_Faza1_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D511
EP2_PMM_1_Faza1_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D512
EP2_PMM_1_Faza1_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D513
EP2_PMM_1_Faza2_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D514
EP2_PMM_1_Faza2_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D515
EP2_PMM_1_Faza2_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D516
EP2_PMM_1_Faza2_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D517
EP2_PMM_1_Faza2_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D518
EP2_PMM_1_Faza2_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D519
EP2_PMM_1_Faza2_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D520
EP2_PMM_1_Faza2_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D521
EP2_PMM_1_Faza2_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D522
EP2_PMM_1_Polje2_Tok01_nad80 | DIGITAL | IOD_EP2_disk | D523
EP2_PMM_1_Polje2_Tok02_nad80 | DIGITAL | IOD_EP2_disk | D524
EP2_PMM_1_Polje2_Tok03_nad80 | DIGITAL | IOD_EP2_disk | D525
EP2_PMM_1_Polje2_Tok04_nad80 | DIGITAL | IOD_EP2_disk | D526
EP2_PMM_1_Polje2_Tok05_nad80 | DIGITAL | IOD_EP2_disk | D527
EP2_PMM_1_Polje2_Tok06_nad80 | DIGITAL | IOD_EP2_disk | D528
EP2_PMM_1_Polje2_Tok07_nad80 | DIGITAL | IOD_EP2_disk | D529
EP2_PMM_1_Polje2_Tok08_nad80 | DIGITAL | IOD_EP2_disk | D530
EP2_PMM_1_Polje2_Tok09_nad80 | DIGITAL | IOD_EP2_disk | D531
EP2_PMM_UC_PoljeB_Tok10_nad80 | DIGITAL | IOD_EP2_disk | D532
EP2_PMM_UC_PoljeB_Tok11_nad80 | DIGITAL | IOD_EP2_disk | D533
EP2_PMM_UC_PoljeB_Tok12_nad80 | DIGITAL | IOD_EP2_disk | D534
EP2_PMM_1_Faza1_Tok01_med60in80 | DIGITAL | IOD_EP2_disk | D535
EP2_PMM_1_Faza1_Tok02_med60in80 | DIGITAL | IOD_EP2_disk | D536
EP2_PMM_1_Faza1_Tok03_med60in80 | DIGITAL | IOD_EP2_disk | D537
EP2_PMM_1_Faza1_Tok04_med60in80 | DIGITAL | IOD_EP2_disk | D538
EP2_PMM_1_Faza1_Tok05_med60in80 | DIGITAL | IOD_EP2_disk | D539
EP2_PMM_1_Faza1_Tok06_med60in80 | DIGITAL | IOD_EP2_disk | D540
EP2_PMM_1_Faza1_Tok07_med60in80 | DIGITAL | IOD_EP2_disk | D541
EP2_PMM_1_Faza1_Tok08_med60in80 | DIGITAL | IOD_EP2_disk | D542
EP2_PMM_1_Faza1_Tok09_med60in80 | DIGITAL | IOD_EP2_disk | D543
EP2_PMM_UC_PoljeA_Tok10_med60in80 | DIGITAL | IOD_EP2_disk | D544
EP2_PMM_UC_PoljeA_Tok11_med60in80 | DIGITAL | IOD_EP2_disk | D545
EP2_PMM_UC_PoljeA_Tok12_med60in80 | DIGITAL | IOD_EP2_disk | D546
EP2_PMM_1_Faza2_Tok01_med60in80 | DIGITAL | IOD_EP2_disk | D547
EP2_PMM_1_Faza2_Tok02_med60in80 | DIGITAL | IOD_EP2_disk | D548
EP2_PMM_1_Faza2_Tok03_med60in80 | DIGITAL | IOD_EP2_disk | D549
EP2_PMM_1_Faza2_Tok04_med60in80 | DIGITAL | IOD_EP2_disk | D550
EP2_PMM_1_Faza2_Tok05_med60in80 | DIGITAL | IOD_EP2_disk | D551
EP2_PMM_1_Faza2_Tok06_med60in80 | DIGITAL | IOD_EP2_disk | D552
EP2_PMM_1_Faza2_Tok07_med60in80 | DIGITAL | IOD_EP2_disk | D553
EP2_PMM_1_Faza2_Tok08_med60in80 | DIGITAL | IOD_EP2_disk | D554
EP2_PMM_1_Faza2_Tok09_med60in80 | DIGITAL | IOD_EP2_disk | D555
EP2_PMM_UC_PoljeB_Tok10_med60in80 | DIGITAL | IOD_EP2_disk | D556
EP2_PMM_UC_PoljeB_Tok11_med60in80 | DIGITAL | IOD_EP2_disk | D557
EP2_PMM_UC_PoljeB_Tok12_med60in80 | DIGITAL | IOD_EP2_disk | D558
EP2_Polje_3Faza1_Tok01_16_nad80 | DIGITAL | IOD_EP2_disk | D2000[16]
EP2_Polje_3Faza1_Tok17_32_nad80 | DIGITAL | IOD_EP2_disk | D2016[16]
EP2_Polje_3Faza1_Tok33_42_nad80 | DIGITAL | IOD_EP2_disk | D2032[16]
EP2_Polje_3Faza2_Tok01_16_nad80 | DIGITAL | IOD_EP2_disk | D2048[16]
EP2_Polje_3Faza2_Tok17_32_nad80 | DIGITAL | IOD_EP2_disk | D2064[16]
EP2_Polje_3Faza2_Tok33_42_nad80 | DIGITAL | IOD_EP2_disk | D2080[16]
EP2_Polje_3Faza3_Tok01_16_nad80 | DIGITAL | IOD_EP2_disk | D2096[16]
EP2_Polje_3Faza3_Tok17_32_nad80 | DIGITAL | IOD_EP2_disk | D2112[16]
EP2_Polje_3Faza3_Tok33_42_nad80 | DIGITAL | IOD_EP2_disk | D2128[16]
EP2_Polje_2Faza1_Tok01_16_nad80 | DIGITAL | IOD_EP2_disk | D2144[16]
EP2_Polje_2Faza1_Tok17_32_nad80 | DIGITAL | IOD_EP2_disk | D2160[16]
EP2_Polje_2Faza1_Tok33_42_nad80 | DIGITAL | IOD_EP2_disk | D2176[16]
EP2_Polje_2Faza2_Tok01_16_nad80 | DIGITAL | IOD_EP2_disk | D2192[16]
EP2_Polje_2Faza2_Tok17_32_nad80 | DIGITAL | IOD_EP2_disk | D2208[16]
EP2_Polje_2Faza2_Tok33_42_nad80 | DIGITAL | IOD_EP2_disk | D2224[16]
EP2_Polje_2Faza3_Tok01_16_nad80 | DIGITAL | IOD_EP2_disk | D2240[16]
EP2_Polje_2Faza3_Tok17_32_nad80 | DIGITAL | IOD_EP2_disk | D2256[16]
EP2_Polje_2Faza3_Tok33_42_nad80 | DIGITAL | IOD_EP2_disk | D2272[16]
EP2_Polje_1Faza1_Tok01_16_nad80 | DIGITAL | IOD_EP2_disk | D2288[16]
EP2_Polje_1Faza2_Tok01_16_nad80 | DIGITAL | IOD_EP2_disk | D2304[16]
EP2_Polje_3Faza1_Tok01_16_med60_80 | DIGITAL | IOD_EP2_disk | D2320[16]
EP2_Polje_3Faza1_Tok17_32_med60_80 | DIGITAL | IOD_EP2_disk | D2336[16]
EP2_Polje_3Faza1_Tok33_42_med60_80 | DIGITAL | IOD_EP2_disk | D2352[16]
EP2_Polje_3Faza2_Tok01_16_med60_80 | DIGITAL | IOD_EP2_disk | D2368[16]
EP2_Polje_3Faza2_Tok17_32_med60_80 | DIGITAL | IOD_EP2_disk | D2384[16]
EP2_Polje_3Faza2_Tok33_42_med60_80 | DIGITAL | IOD_EP2_disk | D2400[16]
EP2_Polje_3Faza3_Tok01_16_med60_80 | DIGITAL | IOD_EP2_disk | D2416[16]
EP2_Polje_3Faza3_Tok17_32_med60_80 | DIGITAL | IOD_EP2_disk | D2432[16]
EP2_Polje_3Faza3_Tok33_42_med60_80 | DIGITAL | IOD_EP2_disk | D2448[16]
EP2_Polje_2Faza1_Tok01_16_med60_80 | DIGITAL | IOD_EP2_disk | D2464[16]
EP2_Polje_2Faza1_Tok17_32_med60_80 | DIGITAL | IOD_EP2_disk | D2480[16]
EP2_Polje_2Faza1_Tok33_42_med60_80 | DIGITAL | IOD_EP2_disk | D2496[16]
EP2_Polje_2Faza2_Tok01_16_med60_80 | DIGITAL | IOD_EP2_disk | D2512[16]
EP2_Polje_2Faza2_Tok17_32_med60_80 | DIGITAL | IOD_EP2_disk | D2528[16]
EP2_Polje_2Faza2_Tok33_42_med60_80 | DIGITAL | IOD_EP2_disk | D2544[16]
EP2_Polje_2Faza3_Tok01_16_med60_80 | DIGITAL | IOD_EP2_disk | D2560[16]
EP2_Polje_2Faza3_Tok17_32_med60_80 | DIGITAL | IOD_EP2_disk | D2576[16]
EP2_Polje_2Faza3_Tok33_42_med60_80 | DIGITAL | IOD_EP2_disk | D2592[16]
EP2_Polje_1Faza1_Tok01_16_med60_80 | DIGITAL | IOD_EP2_disk | D2608[16]
EP2_Polje_1Faza2_Tok01_16_med60_80 | DIGITAL | IOD_EP2_disk | D2634[16]
EP2Pulz1s | DIGITAL | IOD_EP2_disk | D3000
EP2_DanEnergCircE1K4_A | REAL | IOD_EP2_disk | R7286[30] | [5 empty] | ###.#
EP2_CasDDanEnergCircE1K4_A | INT | IOD_EP2_disk | I3060[30] | [5 empty] | ###.#
EP2_CasMDanEnergCircE1K4_A | INT | IOD_EP2_disk | I3090[30] | [5 empty] | ###.#
EP2_TedenEnergCircE1K4_A | REAL | IOD_EP2_disk | R7316[30] | [5 empty] | ###.#
EP2_CasDTedenEnergCircE1K4_A | INT | IOD_EP2_disk | I3150[30] | [5 empty] | ###.#
EP2_CasMTedenEnergCircE1K4_A | INT | IOD_EP2_disk | I3480[30] | [5 empty] | ###.#
EP2_MesecEnergCircE1K4_A | REAL | IOD_EP2_disk | R3746[30] | [5 empty] | ###.#
EP2_CasDMesecEnergCircE1K4_A | INT | IOD_EP2_disk | I3540[30] | [5 empty] | ###.#
EP2_CasMMesecEnergCircE1K4_A | INT | IOD_EP2_disk | I3570[30] | [5 empty] | ###.#
EP2_StSt_DanEnergCircE1K4_A | REAL | IOD_EP2_disk | R3776 | [5 empty] | ###.#
EP2_StSt_TedenEnergCircE1K4_A | REAL | IOD_EP2_disk | R3780 | [5 empty] | ###.#
EP2_StSt_MesecEnergCircE1K4_A | REAL | IOD_EP2_disk | R3784 | [5 empty] | ###.#
EP2_StStCasDDanEnergCircE1K4_A | INT | IOD_EP2_disk | I3606 | [5 empty] | ###.#
EP2_StStCasMDanEnergCircE1K4_A | INT | IOD_EP2_disk | I3608
EP2_StStCasDTedenEnergCircE1K4_A | INT | IOD_EP2_disk | I3610
EP2_StStCasMTedenEnergCircE1K4_A | INT | IOD_EP2_disk | I3612
EP2_StStCasDMesecEnergCircE1K4_A | INT | IOD_EP2_disk | I3614
EP2_StStCasMMesecEnergCircE1K4_A | INT | IOD_EP2_disk | I3616
EP2_PrviZagon | DIGITAL | IOD_EP2_disk | D3017
EP2_Prikaz_PMM_AA_med60in80 | DIGITAL | IOD_EP2_mem | D3018
EP2_Prikaz_PMM_AA_nad80 | DIGITAL | IOD_EP2_mem | D3019
EP2_Prikaz_PMM_BB_med60in80 | DIGITAL | IOD_EP2_mem | D3020
EP2_Prikaz_PMM_BB_nad80 | DIGITAL | IOD_EP2_mem | D3021
EP2_Prikaz_PMM_UC_med60in80 | DIGITAL | IOD_EP2_mem | D3022
EP2_Prikaz_PMM_UC_nad80 | DIGITAL | IOD_EP2_mem | D3023
AEP2_omogoci_sms | DIGITAL | IOD_EP2_disk | D3550[500]
BEP2_omogoci_sms | DIGITAL | IOD_EP2_disk | D4050[500]
CEP2_omogoci_sms | DIGITAL | IOD_EP2_disk | D4550[500]
DEP2_omogoci_sms | DIGITAL | IOD_EP2_disk | D5050[500]
EEP2_omogoci_sms | DIGITAL | IOD_EP2_disk | D5550[500]
FEP2_omogoci_sms | DIGITAL | IOD_EP2_disk | D6050[500]
EP2_ComSCADA_stevec1 | INT | IOD_EP2_mem | I6550
EP2_ComSCADA_stevec2 | INT | IOD_EP2_mem | I6552
EP2_PrikaziSP1 | DIGITAL | IOD_EP2_disk | D6553
EP2_PrikaziSP2 | DIGITAL | IOD_EP2_disk | D6554
EP2_PrikaziSP3 | DIGITAL | IOD_EP2_disk | D6555
EP2_PrikaziSP4 | DIGITAL | IOD_EP2_disk | D6556
EP2_PrikaziSP5 | DIGITAL | IOD_EP2_disk | D6557
EP2_PrikaziKlimat1 | DIGITAL | IOD_EP2_disk | D6558
EP2_PrikaziKlimat2 | DIGITAL | IOD_EP2_disk | D6559
EP2_PrikaziKlimat3 | DIGITAL | IOD_EP2_disk | D6560
EP2_ErrCommScada_omogoci | DIGITAL | IOD_EP2_disk | D6561
EP2_ErrComPanelPLC_omogoci | DIGITAL | IOD_EP2_disk | D6562
EP2_ErrComPort2_omogoci | DIGITAL | IOD_EP2_disk | D6563
EP2_ErrComPort3_omogoci | DIGITAL | IOD_EP2_disk | D6564
EP2_ErrComPort4_omogoci | DIGITAL | IOD_EP2_disk | D6565
EP2_ErrComUPS1_omogoci | DIGITAL | IOD_EP2_disk | D6566
EP2_ErrComUPS2_omogoci | DIGITAL | IOD_EP2_disk | D6567
EP2_ErrComPMM1_omogoci | DIGITAL | IOD_EP2_disk | D6568
EP2_ErrComPMM2_omogoci | DIGITAL | IOD_EP2_disk | D6569
EP2_ErrComPMM3_omogoci | DIGITAL | IOD_EP2_disk | D6570
EP2_ErrComCirc1_omogoci | DIGITAL | IOD_EP2_disk | D6571
EP2_ErrComKlima5_omogoci | DIGITAL | IOD_EP2_disk | D6572
EP2_ErrComKlima6_omogoci | DIGITAL | IOD_EP2_disk | D6573
EP2_PMM3OverCurrentBetw1_omogoci | DIGITAL | IOD_EP2_disk | D6574
EP2_PMM3OverCurrentBetw2_omogoci | DIGITAL | IOD_EP2_disk | D6575
EP2_PMM3OverCurrentBetw3_omogoci | DIGITAL | IOD_EP2_disk | D6576
EP2_PMM3OverCurrentOver1_omogoci | DIGITAL | IOD_EP2_disk | D6577
EP2_PMM3OverCurrentOver2_omogoci | DIGITAL | IOD_EP2_disk | D6578
EP2_PMM3OverCurrentOver3_omogoci | DIGITAL | IOD_EP2_disk | D6579
EP2_PMM2OverCurrentBetw1_omogoci | DIGITAL | IOD_EP2_disk | D6580
EP2_PMM2OverCurrentBetw2_omogoci | DIGITAL | IOD_EP2_disk | D6581
EP2_PMM2OverCurrentBetw3_omogoci | DIGITAL | IOD_EP2_disk | D6582
EP2_PMM2OverCurrentOver1_omogoci | DIGITAL | IOD_EP2_disk | D6583
EP2_PMM2OverCurrentOver2_omogoci | DIGITAL | IOD_EP2_disk | D6584
EP2_PMM2OverCurrentOver3_omogoci | DIGITAL | IOD_EP2_disk | D6585
EP2_PMM1OverCurrentBetw1_omogoci | DIGITAL | IOD_EP2_disk | D6586
EP2_PMM1OverCurrentBetw2_omogoci | DIGITAL | IOD_EP2_disk | D6587
EP2_PMM1OverCurrentOver1_omogoci | DIGITAL | IOD_EP2_disk | D6588
EP2_PMM1OverCurrentOver2_omogoci | DIGITAL | IOD_EP2_disk | D6589
EP2_PMM3OverVoltage_omogoci | DIGITAL | IOD_EP2_disk | D6590
EP2_PMM2OverVoltage_omogoci | DIGITAL | IOD_EP2_disk | D6591
EP2UPS1AlarmAwaitingPower_omog | DIGITAL | IOD_EP2_disk | D6592
EP2UPS1AlarmBypassBad_omog | DIGITAL | IOD_EP2_disk | D6593
EP2UPS1AlarmChargerFailed_omog | DIGITAL | IOD_EP2_disk | D6594
EP2UPS1AlarmCommunicationsLost_omog | DIGITAL | IOD_EP2_disk | D6595
EP2UPS1AlarmDepletedBattery_omog | DIGITAL | IOD_EP2_disk | D6596
EP2UPS1AlarmDiagnosticTestFailed_omog | DIGITAL | IOD_EP2_disk | D6597
EP2UPS1AlarmIzhodOffKotZahtevano_omog | DIGITAL | IOD_EP2_disk | D6598
EP2UPS1AlarmIzhodPreobremenjen_omog | DIGITAL | IOD_EP2_disk | D6599
EP2UPS1AlarmLowBattery_omog | DIGITAL | IOD_EP2_disk | D6600
EP2UPS1AlarmNapakaNaVarovalki_omog | DIGITAL | IOD_EP2_disk | D6601
EP2UPS1AlarmNapakaNaVentilatorju_omog | DIGITAL | IOD_EP2_disk | D6602
EP2UPS1AlarmOnBattery_omog | DIGITAL | IOD_EP2_disk | D6603
EP2UPS1AlarmOnBypass_omog | DIGITAL | IOD_EP2_disk | D6604
EP2UPS1AlarmShutdownImminent_omog | DIGITAL | IOD_EP2_disk | D6605
EP2UPS1AlarmShutdownPending_omog | DIGITAL | IOD_EP2_disk | D6606
EP2UPS1AlarmSlabaBaterija_omog | DIGITAL | IOD_EP2_disk | D6607
EP2UPS1AlarmSplosnaNapaka_omog | DIGITAL | IOD_EP2_disk | D6608
EP2UPS1AlarmStanjeIzhodaIzvenToleranc_omog | DIGITAL | IOD_EP2_disk | D6609
EP2UPS1AlarmStanjeVhodaIzvenToleranc_omog | DIGITAL | IOD_EP2_disk | D6610
EP2UPS1AlarmTemperaturaIzvenToleranc_omog | DIGITAL | IOD_EP2_disk | D6611
EP2UPS1AlarmTestInProgres_omog | DIGITAL | IOD_EP2_disk | D6612
EP2UPS1AlarmUPSIzhodOff_omog | DIGITAL | IOD_EP2_disk | D6613
EP2UPS1AlarmUPSOffKotZahtevano_omog | DIGITAL | IOD_EP2_disk | D6614
EP2UPS1AlarmUPSSystemOff_omog | DIGITAL | IOD_EP2_disk | D6615
EP2UPS1AlarmInverterError_omog | DIGITAL | IOD_EP2_disk | D6616
EP2UPS2AlarmAwaitingPower_omog | DIGITAL | IOD_EP2_disk | D6617
EP2UPS2AlarmBypassBad_omog | DIGITAL | IOD_EP2_disk | D6618
EP2UPS2AlarmChargerFailed_omog | DIGITAL | IOD_EP2_disk | D6619
EP2UPS2AlarmCommunicationsLost_omog | DIGITAL | IOD_EP2_disk | D6620
EP2UPS2AlarmDepletedBattery_omog | DIGITAL | IOD_EP2_disk | D6621
EP2UPS2AlarmDiagnosticTestFailed_omog | DIGITAL | IOD_EP2_disk | D6622
EP2UPS2AlarmIzhodOffKotZahtevano_omog | DIGITAL | IOD_EP2_disk | D6623
EP2UPS2AlarmIzhodPreobremenjen_omog | DIGITAL | IOD_EP2_disk | D6624
EP2UPS2AlarmLowBattery_omog | DIGITAL | IOD_EP2_disk | D6625
EP2UPS2AlarmNapakaNaVarovalki_omog | DIGITAL | IOD_EP2_disk | D6626
EP2UPS2AlarmNapakaNaVentilatorju_omog | DIGITAL | IOD_EP2_disk | D6627
EP2UPS2AlarmOnBattery_omog | DIGITAL | IOD_EP2_disk | D6628
EP2UPS2AlarmOnBypass_omog | DIGITAL | IOD_EP2_disk | D6629
EP2UPS2AlarmShutdownImminent_omog | DIGITAL | IOD_EP2_disk | D6630
EP2UPS2AlarmShutdownPending_omog | DIGITAL | IOD_EP2_disk | D6631
EP2UPS2AlarmSlabaBaterija_omog | DIGITAL | IOD_EP2_disk | D6632
EP2UPS2AlarmSplosnaNapaka_omog | DIGITAL | IOD_EP2_disk | D6633
EP2UPS2AlarmStanjeIzhodaIzvenToleranc_omog | DIGITAL | IOD_EP2_disk | D6634
EP2UPS2AlarmStanjeVhodaIzvenToleranc_omog | DIGITAL | IOD_EP2_disk | D6635
EP2UPS2AlarmTemperaturaIzvenToleranc_omog | DIGITAL | IOD_EP2_disk | D6636
EP2UPS2AlarmTestInProgres_omog | DIGITAL | IOD_EP2_disk | D6637
EP2UPS2AlarmUPSIzhodOff_omog | DIGITAL | IOD_EP2_disk | D6638
EP2UPS2AlarmUPSOffKotZahtevano_omog | DIGITAL | IOD_EP2_disk | D6639
EP2UPS2AlarmUPSSystemOff_omog | DIGITAL | IOD_EP2_disk | D6640
EP2UPS2AlarmInverterError_omog | DIGITAL | IOD_EP2_disk | D6641
EP2_DI_Q2_Rezerva_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6642
EP2_DI_Q5_OdcKlima1_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6643
EP2_DI_Q6_OdcKlima2_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6644
EP2_DI_Q7_OdcKlima3_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6645
EP2_DI_Q8_OdcKlima4_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6646
EP2_DI_Q9_OdcKlima5_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6647
EP2_DI_Q10_OdcKlima6_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6648
EP2_DI_Q25_OdcUpsA_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6649
EP2_DI_Q26_OdcByA_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6650
EP2_DI_Q27_OdcByUpsA_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6651
EP2_DI_Q28_OdcUpsB_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6652
EP2_DI_Q29_OdcByB_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6653
EP2_DI_Q30_OdcByUpsB_IZP_omogoci | DIGITAL | IOD_EP2_disk | D6654
EP2_DI_Klima5_ERR_omogoci | DIGITAL | IOD_EP2_disk | D6655
EP2_DI_Klima6_ERR_omogoci | DIGITAL | IOD_EP2_disk | D6656
EP2_DI_KlimaSplit1_ERR_omogoci | DIGITAL | IOD_EP2_disk | D6657
EP2_DI_UpsA_ON_omogoci | DIGITAL | IOD_EP2_disk | D6658
EP2_DI_UpsA_ERR_omogoci | DIGITAL | IOD_EP2_disk | D6659
EP2_DI_UpsB_ON_omogoci | DIGITAL | IOD_EP2_disk | D6660
EP2_DI_UpsB_ERR_omogoci | DIGITAL | IOD_EP2_disk | D6661
EP2_DI_UPS_Alarm_omogoci | DIGITAL | IOD_EP2_disk | D6662
EP2_DI_UPS_BatNacin_omogoci | DIGITAL | IOD_EP2_disk | D6663
EP2_DI_UPS_Polnjenje_omogoci | DIGITAL | IOD_EP2_disk | D6664
EP2_DI_RazlitjeVodeK5K6_omogoci | DIGITAL | IOD_EP2_disk | D6665
EP2_SetDateTimeError_omogoci | DIGITAL | IOD_EP2_disk | D6666
EP2_TempTSprevisoka1_omogoci | DIGITAL | IOD_EP2_disk | D6667
EP2_NapakaSenzorTemp1_omogoci | DIGITAL | IOD_EP2_disk | D6668
EP2_NapakaSenzorVlaga1_omogoci | DIGITAL | IOD_EP2_disk | D6669
EP2_SlabaBaterijaPLC_A1_omogoci | DIGITAL | IOD_EP2_disk | D6670
EP2_Klima1_GeneralAlarm_omogoci | DIGITAL | IOD_EP2_disk | D6671
EP2_Klima1_AlarmKompresor1_omogoci | DIGITAL | IOD_EP2_disk | D6672
EP2_Klima1_AlarmKompresor2_omogoci | DIGITAL | IOD_EP2_disk | D6673
EP2_Klima1_NizekPritiskKompresor1_omogoci | DIGITAL | IOD_EP2_disk | D6674
EP2_Klima1_NizekPritiskKompresor2_omogoci | DIGITAL | IOD_EP2_disk | D6675
EP2_Klima1_NapakaPriPretokuZraka_omogoci | DIGITAL | IOD_EP2_disk | D6676
EP2_Klima1_FenThermalCutout_omogoci | DIGITAL | IOD_EP2_disk | D6677
EP2_Klima1_ThermalCutoutHeater1_omogoci | DIGITAL | IOD_EP2_disk | D6678
EP2_Klima1_ThermalCutoutHeater2_omogoci | DIGITAL | IOD_EP2_disk | D6679
EP2_Klima1_PozarniAlarm_omogoci | DIGITAL | IOD_EP2_disk | D6680
EP2_Klima1_ZamasenFilter_omogoci | DIGITAL | IOD_EP2_disk | D6681
EP2_Klima1_VisokaTempVProstoru_omogoci | DIGITAL | IOD_EP2_disk | D6682
EP2_Klima1_NizkaTempVProstoru_omogoci | DIGITAL | IOD_EP2_disk | D6683
EP2_Klima1_VisokaVlaznost_omogoci | DIGITAL | IOD_EP2_disk | D6684
EP2_Klima1_NizkaVlaznost_omogoci | DIGITAL | IOD_EP2_disk | D6685
EP2_Klima1_Kompresor1naMejiObrUr_omogoci | DIGITAL | IOD_EP2_disk | D6686
EP2_Klima1_Kompresor2naMejiObrUr_omogoci | DIGITAL | IOD_EP2_disk | D6687
EP2_Klima1_VentilatorNaMejiObrU_omogoci | DIGITAL | IOD_EP2_disk | D6688
EP2_Klima1_VisokaTempPovratneVod_omogoci | DIGITAL | IOD_EP2_disk | D6689
EP2_Klima1_NizkaTempPovratneVode_omogoci | DIGITAL | IOD_EP2_disk | D6690
EP2_Klima1_NapakaSenzorTempPros_omogoci | DIGITAL | IOD_EP2_disk | D6691
EP2_Klima1_NapakaSenzorTempIzih_omogoci | DIGITAL | IOD_EP2_disk | D6692
EP2_Klima1_NapakaSenzorPovratVod_omogoci | DIGITAL | IOD_EP2_disk | D6693
EP2_Klima1_NapakaSenzorZunanjeTe_omogoci | DIGITAL | IOD_EP2_disk | D6694
EP2_Klima1_NapakaSenzorVlaznosti_omogoci | DIGITAL | IOD_EP2_disk | D6695
EP2_Klima1_FaultyEPROM_omogoci | DIGITAL | IOD_EP2_disk | D6696
EP2_Klima1_StoppedByAlarms_omogoci | DIGITAL | IOD_EP2_disk | D6697
EP2_Klima1_VisokTokVVlazilcu_omogoci | DIGITAL | IOD_EP2_disk | D6698
EP2_Klima1_NiVodeVVlazilcu_omogoci | DIGITAL | IOD_EP2_disk | D6699
EP2_Klima1_NiTokaVVlazilcu_omogoci | DIGITAL | IOD_EP2_disk | D6700
EP2_Klima1_RocniIzklop_omogoci | DIGITAL | IOD_EP2_disk | D6701
EP2_Klima2_GeneralAlarm_omogoci | DIGITAL | IOD_EP2_disk | D6702
EP2_Klima2_AlarmKompresor1_omogoci | DIGITAL | IOD_EP2_disk | D6703
EP2_Klima2_AlarmKompresor2_omogoci | DIGITAL | IOD_EP2_disk | D6704
EP2_Klima2_NizekPritiskKompresor1_omogoci | DIGITAL | IOD_EP2_disk | D6705
EP2_Klima2_NizekPritiskKompresor2_omogoci | DIGITAL | IOD_EP2_disk | D6706
EP2_Klima2_NapakaPriPretokuZraka_omogoci | DIGITAL | IOD_EP2_disk | D6707
EP2_Klima2_FenThermalCutout_omogoci | DIGITAL | IOD_EP2_disk | D6708
EP2_Klima2_ThermalCutoutHeater1_omogoci | DIGITAL | IOD_EP2_disk | D6709
EP2_Klima2_ThermalCutoutHeater2_omogoci | DIGITAL | IOD_EP2_disk | D6710
EP2_Klima2_PozarniAlarm_omogoci | DIGITAL | IOD_EP2_disk | D6711
EP2_Klima2_ZamasenFilter_omogoci | DIGITAL | IOD_EP2_disk | D6712
EP2_Klima2_VisokaTempVProstoru_omogoci | DIGITAL | IOD_EP2_disk | D6713
EP2_Klima2_NizkaTempVProstoru_omogoci | DIGITAL | IOD_EP2_disk | D6714
EP2_Klima2_VisokaVlaznost_omogoci | DIGITAL | IOD_EP2_disk | D6715
EP2_Klima2_NizkaVlaznost_omogoci | DIGITAL | IOD_EP2_disk | D6716
EP2_Klima2_Kompresor1naMejiObrUr_omogoci | DIGITAL | IOD_EP2_disk | D6717
EP2_Klima2_Kompresor2naMejiObrUr_omogoci | DIGITAL | IOD_EP2_disk | D6718
EP2_Klima2_VentilatorNaMejiObrU_omogoci | DIGITAL | IOD_EP2_disk | D6719
EP2_Klima2_VisokaTempPovratneVod_omogoci | DIGITAL | IOD_EP2_disk | D6720
EP2_Klima2_NizkaTempPovratneVode_omogoci | DIGITAL | IOD_EP2_disk | D6721
EP2_Klima2_NapakaSenzorTempPros_omogoci | DIGITAL | IOD_EP2_disk | D6722
EP2_Klima2_NapakaSenzorPovratVod_omogoci | DIGITAL | IOD_EP2_disk | D6723
EP2_Klima2_NapakaSenzorZunanjeTe_omogoci | DIGITAL | IOD_EP2_disk | D6724
EP2_Klima2_NapakaSenzorTempIzpih_omogoci | DIGITAL | IOD_EP2_disk | D6725
EP2_Klima2_NapakaSenzorVlaznosti_omogoci | DIGITAL | IOD_EP2_disk | D6726
EP2_Klima2_FaultyEPROM_omogoci | DIGITAL | IOD_EP2_disk | D6727
EP2_Klima2_StoppedByAlarms_omogoci | DIGITAL | IOD_EP2_disk | D6728
EP2_Klima2_VisokTokVVlazilcu_omogoci | DIGITAL | IOD_EP2_disk | D6729
EP2_Klima2_NiVodeVVlazilcu_omogoci | DIGITAL | IOD_EP2_disk | D6730
EP2_Klima2_NiTokaVVlazilcu_omogoci | DIGITAL | IOD_EP2_disk | D6731
EP2_Klima2_RocniIzklop_omogoci | DIGITAL | IOD_EP2_disk | D6732
EP2_PMM_3_Faza1_Tok01_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6733
EP2_PMM_3_Faza1_Tok02_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6734
EP2_PMM_3_Faza1_Tok03_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6735
EP2_PMM_3_Faza1_Tok04_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6736
EP2_PMM_3_Faza1_Tok05_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6737
EP2_PMM_3_Faza1_Tok06_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6738
EP2_PMM_3_Faza1_Tok07_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6739
EP2_PMM_3_Faza1_Tok08_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6740
EP2_PMM_3_Faza1_Tok09_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6741
EP2_PMM_3_Faza1_Tok10_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6742
EP2_PMM_3_Faza1_Tok11_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6743
EP2_PMM_3_Faza1_Tok12_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6744
EP2_PMM_3_Faza1_Tok13_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6745
EP2_PMM_3_Faza1_Tok14_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6746
EP2_PMM_3_Faza1_Tok15_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6747
EP2_PMM_3_Faza1_Tok16_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6748
EP2_PMM_3_Faza1_Tok17_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6749
EP2_PMM_3_Faza1_Tok18_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6750
EP2_PMM_3_Faza1_Tok19_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6751
EP2_PMM_3_Faza1_Tok20_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6752
EP2_PMM_3_Faza1_Tok21_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6753
EP2_PMM_3_Faza1_Tok22_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6754
EP2_PMM_3_Faza1_Tok23_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6755
EP2_PMM_3_Faza1_Tok24_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6756
EP2_PMM_3_Faza1_Tok25_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6757
EP2_PMM_3_Faza1_Tok26_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6758
EP2_PMM_3_Faza1_Tok27_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6759
EP2_PMM_3_Faza1_Tok28_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6760
EP2_PMM_3_Faza1_Tok29_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6761
EP2_PMM_3_Faza1_Tok30_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6762
EP2_PMM_3_Faza1_Tok31_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6763
EP2_PMM_3_Faza1_Tok32_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6764
EP2_PMM_3_Faza1_Tok33_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6765
EP2_PMM_3_Faza1_Tok34_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6766
EP2_PMM_3_Faza1_Tok35_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6767
EP2_PMM_3_Faza1_Tok36_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6768
EP2_PMM_3_Faza1_Tok37_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6769
EP2_PMM_3_Faza1_Tok38_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6770
EP2_PMM_3_Faza1_Tok39_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6771
EP2_PMM_3_Faza1_Tok40_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6772
EP2_PMM_3_Faza1_Tok41_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6773
EP2_PMM_3_Faza1_Tok42_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6774
EP2_PMM_3_Faza2_Tok01_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6775
EP2_PMM_3_Faza2_Tok02_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6776
EP2_PMM_3_Faza2_Tok03_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6777
EP2_PMM_3_Faza2_Tok04_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6778
EP2_PMM_3_Faza2_Tok05_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6779
EP2_PMM_3_Faza2_Tok06_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6780
EP2_PMM_3_Faza2_Tok07_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6781
EP2_PMM_3_Faza2_Tok08_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6782
EP2_PMM_3_Faza2_Tok09_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6783
EP2_PMM_3_Faza2_Tok10_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6784
EP2_PMM_3_Faza2_Tok11_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6785
EP2_PMM_3_Faza2_Tok12_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6786
EP2_PMM_3_Faza2_Tok13_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6787
EP2_PMM_3_Faza2_Tok14_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6788
EP2_PMM_3_Faza2_Tok15_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6789
EP2_PMM_3_Faza2_Tok16_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6790
EP2_PMM_3_Faza2_Tok17_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6791
EP2_PMM_3_Faza2_Tok18_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6792
EP2_PMM_3_Faza2_Tok19_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6793
EP2_PMM_3_Faza2_Tok20_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6794
EP2_PMM_3_Faza2_Tok21_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6795
EP2_PMM_3_Faza2_Tok22_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6796
EP2_PMM_3_Faza2_Tok23_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6797
EP2_PMM_3_Faza2_Tok24_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6798
EP2_PMM_3_Faza2_Tok25_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6799
EP2_PMM_3_Faza2_Tok26_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6800
EP2_PMM_3_Faza2_Tok27_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6801
EP2_PMM_3_Faza2_Tok28_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6802
EP2_PMM_3_Faza2_Tok29_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6803
EP2_PMM_3_Faza2_Tok30_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6804
EP2_PMM_3_Faza2_Tok31_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6805
EP2_PMM_3_Faza2_Tok32_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6806
EP2_PMM_3_Faza2_Tok33_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6807
EP2_PMM_3_Faza2_Tok34_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6808
EP2_PMM_3_Faza2_Tok35_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6809
EP2_PMM_3_Faza2_Tok36_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6810
EP2_PMM_3_Faza2_Tok37_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6811
EP2_PMM_3_Faza2_Tok38_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6812
EP2_PMM_3_Faza2_Tok39_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6813
EP2_PMM_3_Faza2_Tok40_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6814
EP2_PMM_3_Faza2_Tok41_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6815
EP2_PMM_3_Faza2_Tok42_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6816
EP2_PMM_3_Faza3_Tok01_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6817
EP2_PMM_3_Faza3_Tok02_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6818
EP2_PMM_3_Faza3_Tok03_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6819
EP2_PMM_3_Faza3_Tok04_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6820
EP2_PMM_3_Faza3_Tok05_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6821
EP2_PMM_3_Faza3_Tok06_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6822
EP2_PMM_3_Faza3_Tok07_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6823
EP2_PMM_3_Faza3_Tok08_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6824
EP2_PMM_3_Faza3_Tok09_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6825
EP2_PMM_3_Faza3_Tok10_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6826
EP2_PMM_3_Faza3_Tok11_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6827
EP2_PMM_3_Faza3_Tok12_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6828
EP2_PMM_3_Faza3_Tok13_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6829
EP2_PMM_3_Faza3_Tok14_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6830
EP2_PMM_3_Faza3_Tok15_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6831
EP2_PMM_3_Faza3_Tok16_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6832
EP2_PMM_3_Faza3_Tok17_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6833
EP2_PMM_3_Faza3_Tok18_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6834
EP2_PMM_3_Faza3_Tok19_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6835
EP2_PMM_3_Faza3_Tok20_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6836
EP2_PMM_3_Faza3_Tok21_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6837
EP2_PMM_3_Faza3_Tok22_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6838
EP2_PMM_3_Faza3_Tok23_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6839
EP2_PMM_3_Faza3_Tok24_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6840
EP2_PMM_3_Faza3_Tok25_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6841
EP2_PMM_3_Faza3_Tok26_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6842
EP2_PMM_3_Faza3_Tok27_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6843
EP2_PMM_3_Faza3_Tok28_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6844
EP2_PMM_3_Faza3_Tok29_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6845
EP2_PMM_3_Faza3_Tok30_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6846
EP2_PMM_3_Faza3_Tok31_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6847
EP2_PMM_3_Faza3_Tok32_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6848
EP2_PMM_3_Faza3_Tok33_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6849
EP2_PMM_3_Faza3_Tok34_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6850
EP2_PMM_3_Faza3_Tok35_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6851
EP2_PMM_3_Faza3_Tok36_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6852
EP2_PMM_3_Faza3_Tok37_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6853
EP2_PMM_3_Faza3_Tok38_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6854
EP2_PMM_3_Faza3_Tok39_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6855
EP2_PMM_3_Faza3_Tok40_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6856
EP2_PMM_3_Faza3_Tok41_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6857
EP2_PMM_3_Faza3_Tok42_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6858
EP2_PMM_3_Faza1_Tok01_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6859
EP2_PMM_3_Faza1_Tok02_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6860
EP2_PMM_3_Faza1_Tok03_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6861
EP2_PMM_3_Faza1_Tok04_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6862
EP2_PMM_3_Faza1_Tok05_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6863
EP2_PMM_3_Faza1_Tok06_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6864
EP2_PMM_3_Faza1_Tok07_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6865
EP2_PMM_3_Faza1_Tok08_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6866
EP2_PMM_3_Faza1_Tok09_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6867
EP2_PMM_3_Faza1_Tok10_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6868
EP2_PMM_3_Faza1_Tok11_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6869
EP2_PMM_3_Faza1_Tok12_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6870
EP2_PMM_3_Faza1_Tok13_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6871
EP2_PMM_3_Faza1_Tok14_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6872
EP2_PMM_3_Faza1_Tok15_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6873
EP2_PMM_3_Faza1_Tok16_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6874
EP2_PMM_3_Faza1_Tok17_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6875
EP2_PMM_3_Faza1_Tok18_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6876
EP2_PMM_3_Faza1_Tok19_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6877
EP2_PMM_3_Faza1_Tok20_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6878
EP2_PMM_3_Faza1_Tok21_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6879
EP2_PMM_3_Faza1_Tok22_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6880
EP2_PMM_3_Faza1_Tok23_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6881
EP2_PMM_3_Faza1_Tok24_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6882
EP2_PMM_3_Faza1_Tok25_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6883
EP2_PMM_3_Faza1_Tok26_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6884
EP2_PMM_3_Faza1_Tok27_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6885
EP2_PMM_3_Faza1_Tok28_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6886
EP2_PMM_3_Faza1_Tok29_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6887
EP2_PMM_3_Faza1_Tok30_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6888
EP2_PMM_3_Faza1_Tok31_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6889
EP2_PMM_3_Faza1_Tok32_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6890
EP2_PMM_3_Faza1_Tok33_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6891
EP2_PMM_3_Faza1_Tok34_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6892
EP2_PMM_3_Faza1_Tok35_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6893
EP2_PMM_3_Faza1_Tok36_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6894
EP2_PMM_3_Faza1_Tok37_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6895
EP2_PMM_3_Faza1_Tok38_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6896
EP2_PMM_3_Faza1_Tok39_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6897
EP2_PMM_3_Faza1_Tok40_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6898
EP2_PMM_3_Faza1_Tok41_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6899
EP2_PMM_3_Faza1_Tok42_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6900
EP2_PMM_3_Faza2_Tok01_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6901
EP2_PMM_3_Faza2_Tok02_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6902
EP2_PMM_3_Faza2_Tok03_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6903
EP2_PMM_3_Faza2_Tok04_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6904
EP2_PMM_3_Faza2_Tok05_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6905
EP2_PMM_3_Faza2_Tok06_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6906
EP2_PMM_3_Faza2_Tok07_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6907
EP2_PMM_3_Faza2_Tok08_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6908
EP2_PMM_3_Faza2_Tok09_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6909
EP2_PMM_3_Faza2_Tok10_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6910
EP2_PMM_3_Faza2_Tok11_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6911
EP2_PMM_3_Faza2_Tok12_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6912
EP2_PMM_3_Faza2_Tok13_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6913
EP2_PMM_3_Faza2_Tok14_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6914
EP2_PMM_3_Faza2_Tok15_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6915
EP2_PMM_3_Faza2_Tok16_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6916
EP2_PMM_3_Faza2_Tok17_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6917
EP2_PMM_3_Faza2_Tok18_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6918
EP2_PMM_3_Faza2_Tok19_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6919
EP2_PMM_3_Faza2_Tok20_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6920
EP2_PMM_3_Faza2_Tok21_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6921
EP2_PMM_3_Faza2_Tok22_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6922
EP2_PMM_3_Faza2_Tok23_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6923
EP2_PMM_3_Faza2_Tok24_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6924
EP2_PMM_3_Faza2_Tok25_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6925
EP2_PMM_3_Faza2_Tok26_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6926
EP2_PMM_3_Faza2_Tok27_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6927
EP2_PMM_3_Faza2_Tok28_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6928
EP2_PMM_3_Faza2_Tok29_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6929
EP2_PMM_3_Faza2_Tok30_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6930
EP2_PMM_3_Faza2_Tok31_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6931
EP2_PMM_3_Faza2_Tok32_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6932
EP2_PMM_3_Faza2_Tok33_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6933
EP2_PMM_3_Faza2_Tok34_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6934
EP2_PMM_3_Faza2_Tok35_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6935
EP2_PMM_3_Faza2_Tok36_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6936
EP2_PMM_3_Faza2_Tok37_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6937
EP2_PMM_3_Faza2_Tok38_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6938
EP2_PMM_3_Faza2_Tok39_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6939
EP2_PMM_3_Faza2_Tok40_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6940
EP2_PMM_3_Faza2_Tok41_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6941
EP2_PMM_3_Faza2_Tok42_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6942
EP2_PMM_3_Faza3_Tok01_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6943
EP2_PMM_3_Faza3_Tok02_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6944
EP2_PMM_3_Faza3_Tok03_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6945
EP2_PMM_3_Faza3_Tok04_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6946
EP2_PMM_3_Faza3_Tok05_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6947
EP2_PMM_3_Faza3_Tok06_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6948
EP2_PMM_3_Faza3_Tok07_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6949
EP2_PMM_3_Faza3_Tok08_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6950
EP2_PMM_3_Faza3_Tok09_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6951
EP2_PMM_3_Faza3_Tok10_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6952
EP2_PMM_3_Faza3_Tok11_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6953
EP2_PMM_3_Faza3_Tok12_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6954
EP2_PMM_3_Faza3_Tok13_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6955
EP2_PMM_3_Faza3_Tok14_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6956
EP2_PMM_3_Faza3_Tok15_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6957
EP2_PMM_3_Faza3_Tok16_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6958
EP2_PMM_3_Faza3_Tok17_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6959
EP2_PMM_3_Faza3_Tok18_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6960
EP2_PMM_3_Faza3_Tok19_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6961
EP2_PMM_3_Faza3_Tok20_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6962
EP2_PMM_3_Faza3_Tok21_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6963
EP2_PMM_3_Faza3_Tok22_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6964
EP2_PMM_3_Faza3_Tok23_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6965
EP2_PMM_3_Faza3_Tok24_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6966
EP2_PMM_3_Faza3_Tok25_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6967
EP2_PMM_3_Faza3_Tok26_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6968
EP2_PMM_3_Faza3_Tok27_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6969
EP2_PMM_3_Faza3_Tok28_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6970
EP2_PMM_3_Faza3_Tok29_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6971
EP2_PMM_3_Faza3_Tok30_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6972
EP2_PMM_3_Faza3_Tok31_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6973
EP2_PMM_3_Faza3_Tok32_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6974
EP2_PMM_3_Faza3_Tok33_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6975
EP2_PMM_3_Faza3_Tok34_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6976
EP2_PMM_3_Faza3_Tok35_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6977
EP2_PMM_3_Faza3_Tok36_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6978
EP2_PMM_3_Faza3_Tok37_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6979
EP2_PMM_3_Faza3_Tok38_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6980
EP2_PMM_3_Faza3_Tok39_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6981
EP2_PMM_3_Faza3_Tok40_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6982
EP2_PMM_3_Faza3_Tok41_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6983
EP2_PMM_3_Faza3_Tok42_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D6984
EP2_PMM_2_Faza1_Tok01_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6985
EP2_PMM_2_Faza1_Tok02_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6986
EP2_PMM_2_Faza1_Tok03_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6987
EP2_PMM_2_Faza1_Tok04_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6988
EP2_PMM_2_Faza1_Tok05_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6989
EP2_PMM_2_Faza1_Tok06_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6990
EP2_PMM_2_Faza1_Tok07_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6991
EP2_PMM_2_Faza1_Tok08_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6992
EP2_PMM_2_Faza1_Tok09_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6993
EP2_PMM_2_Faza1_Tok10_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6994
EP2_PMM_2_Faza1_Tok11_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6995
EP2_PMM_2_Faza1_Tok12_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6996
EP2_PMM_2_Faza1_Tok13_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6997
EP2_PMM_2_Faza1_Tok14_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6998
EP2_PMM_2_Faza1_Tok15_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D6999
EP2_PMM_2_Faza1_Tok16_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7000
EP2_PMM_2_Faza1_Tok17_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7001
EP2_PMM_2_Faza1_Tok18_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7002
EP2_PMM_2_Faza1_Tok19_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7003
EP2_PMM_2_Faza1_Tok20_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7004
EP2_PMM_2_Faza1_Tok21_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7005
EP2_PMM_2_Faza1_Tok22_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7006
EP2_PMM_2_Faza1_Tok23_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7007
EP2_PMM_2_Faza1_Tok24_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7008
EP2_PMM_2_Faza1_Tok25_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7009
EP2_PMM_2_Faza1_Tok26_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7010
EP2_PMM_2_Faza1_Tok27_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7011
EP2_PMM_2_Faza1_Tok28_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7012
EP2_PMM_2_Faza1_Tok29_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7013
EP2_PMM_2_Faza1_Tok30_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7014
EP2_PMM_2_Faza1_Tok31_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7015
EP2_PMM_2_Faza1_Tok32_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7016
EP2_PMM_2_Faza1_Tok33_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7017
EP2_PMM_2_Faza1_Tok34_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7018
EP2_PMM_2_Faza1_Tok35_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7019
EP2_PMM_2_Faza1_Tok36_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7020
EP2_PMM_2_Faza1_Tok37_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7021
EP2_PMM_2_Faza1_Tok38_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7022
EP2_PMM_2_Faza1_Tok39_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7023
EP2_PMM_2_Faza1_Tok40_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7024
EP2_PMM_2_Faza1_Tok41_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7025
EP2_PMM_2_Faza1_Tok42_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7026
EP2_PMM_2_Faza2_Tok01_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7027
EP2_PMM_2_Faza2_Tok02_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7028
EP2_PMM_2_Faza2_Tok03_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7029
EP2_PMM_2_Faza2_Tok04_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7030
EP2_PMM_2_Faza2_Tok05_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7031
EP2_PMM_2_Faza2_Tok06_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7032
EP2_PMM_2_Faza2_Tok07_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7033
EP2_PMM_2_Faza2_Tok08_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7034
EP2_PMM_2_Faza2_Tok09_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7035
EP2_PMM_2_Faza2_Tok10_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7036
EP2_PMM_2_Faza2_Tok11_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7037
EP2_PMM_2_Faza2_Tok12_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7038
EP2_PMM_2_Faza2_Tok13_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7039
EP2_PMM_2_Faza2_Tok14_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7040
EP2_PMM_2_Faza2_Tok15_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7041
EP2_PMM_2_Faza2_Tok16_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7042
EP2_PMM_2_Faza2_Tok17_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7043
EP2_PMM_2_Faza2_Tok18_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7044
EP2_PMM_2_Faza2_Tok19_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7045
EP2_PMM_2_Faza2_Tok20_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7046
EP2_PMM_2_Faza2_Tok21_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7047
EP2_PMM_2_Faza2_Tok22_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7048
EP2_PMM_2_Faza2_Tok23_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7049
EP2_PMM_2_Faza2_Tok24_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7050
EP2_PMM_2_Faza2_Tok25_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7051
EP2_PMM_2_Faza2_Tok26_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7052
EP2_PMM_2_Faza2_Tok27_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7053
EP2_PMM_2_Faza2_Tok28_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7054
EP2_PMM_2_Faza2_Tok29_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7055
EP2_PMM_2_Faza2_Tok30_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7056
EP2_PMM_2_Faza2_Tok31_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7057
EP2_PMM_2_Faza2_Tok32_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7058
EP2_PMM_2_Faza2_Tok33_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7059
EP2_PMM_2_Faza2_Tok34_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7060
EP2_PMM_2_Faza2_Tok35_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7061
EP2_PMM_2_Faza2_Tok36_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7062
EP2_PMM_2_Faza2_Tok37_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7063
EP2_PMM_2_Faza2_Tok38_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7064
EP2_PMM_2_Faza2_Tok39_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7065
EP2_PMM_2_Faza2_Tok40_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7066
EP2_PMM_2_Faza2_Tok41_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7067
EP2_PMM_2_Faza2_Tok42_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7068
EP2_PMM_2_Faza3_Tok01_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7069
EP2_PMM_2_Faza3_Tok02_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7070
EP2_PMM_2_Faza3_Tok03_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7071
EP2_PMM_2_Faza3_Tok04_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7072
EP2_PMM_2_Faza3_Tok05_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7073
EP2_PMM_2_Faza3_Tok06_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7074
EP2_PMM_2_Faza3_Tok07_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7075
EP2_PMM_2_Faza3_Tok08_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7076
EP2_PMM_2_Faza3_Tok09_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7077
EP2_PMM_2_Faza3_Tok10_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7078
EP2_PMM_2_Faza3_Tok11_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7079
EP2_PMM_2_Faza3_Tok12_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7080
EP2_PMM_2_Faza3_Tok13_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7081
EP2_PMM_2_Faza3_Tok14_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7082
EP2_PMM_2_Faza3_Tok15_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7083
EP2_PMM_2_Faza3_Tok16_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7084
EP2_PMM_2_Faza3_Tok17_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7085
EP2_PMM_2_Faza3_Tok18_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7086
EP2_PMM_2_Faza3_Tok19_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7087
EP2_PMM_2_Faza3_Tok20_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7088
EP2_PMM_2_Faza3_Tok21_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7089
EP2_PMM_2_Faza3_Tok22_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7090
EP2_PMM_2_Faza3_Tok23_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7091
EP2_PMM_2_Faza3_Tok24_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7092
EP2_PMM_2_Faza3_Tok25_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7093
EP2_PMM_2_Faza3_Tok26_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7094
EP2_PMM_2_Faza3_Tok27_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7095
EP2_PMM_2_Faza3_Tok28_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7096
EP2_PMM_2_Faza3_Tok29_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7097
EP2_PMM_2_Faza3_Tok30_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7098
EP2_PMM_2_Faza3_Tok31_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7099
EP2_PMM_2_Faza3_Tok32_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7100
EP2_PMM_2_Faza3_Tok33_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7101
EP2_PMM_2_Faza3_Tok34_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7102
EP2_PMM_2_Faza3_Tok35_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7103
EP2_PMM_2_Faza3_Tok36_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7104
EP2_PMM_2_Faza3_Tok37_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7105
EP2_PMM_2_Faza3_Tok38_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7106
EP2_PMM_2_Faza3_Tok39_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7107
EP2_PMM_2_Faza3_Tok40_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7108
EP2_PMM_2_Faza3_Tok41_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7109
EP2_PMM_2_Faza3_Tok42_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7110
EP2_PMM_2_Faza1_Tok01_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7111
EP2_PMM_2_Faza1_Tok02_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7112
EP2_PMM_2_Faza1_Tok03_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7113
EP2_PMM_2_Faza1_Tok04_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7114
EP2_PMM_2_Faza1_Tok05_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7115
EP2_PMM_2_Faza1_Tok06_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7116
EP2_PMM_2_Faza1_Tok07_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7117
EP2_PMM_2_Faza1_Tok08_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7118
EP2_PMM_2_Faza1_Tok09_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7119
EP2_PMM_2_Faza1_Tok10_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7120
EP2_PMM_2_Faza1_Tok11_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7121
EP2_PMM_2_Faza1_Tok12_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7122
EP2_PMM_2_Faza1_Tok13_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7123
EP2_PMM_2_Faza1_Tok14_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7124
EP2_PMM_2_Faza1_Tok15_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7125
EP2_PMM_2_Faza1_Tok16_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7126
EP2_PMM_2_Faza1_Tok17_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7127
EP2_PMM_2_Faza1_Tok18_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7128
EP2_PMM_2_Faza1_Tok19_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7129
EP2_PMM_2_Faza1_Tok20_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7130
EP2_PMM_2_Faza1_Tok21_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7131
EP2_PMM_2_Faza1_Tok22_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7132
EP2_PMM_2_Faza1_Tok23_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7133
EP2_PMM_2_Faza1_Tok24_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7134
EP2_PMM_2_Faza1_Tok25_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7135
EP2_PMM_2_Faza1_Tok26_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7136
EP2_PMM_2_Faza1_Tok27_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7137
EP2_PMM_2_Faza1_Tok28_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7138
EP2_PMM_2_Faza1_Tok29_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7139
EP2_PMM_2_Faza1_Tok30_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7140
EP2_PMM_2_Faza1_Tok31_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7141
EP2_PMM_2_Faza1_Tok32_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7142
EP2_PMM_2_Faza1_Tok33_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7143
EP2_PMM_2_Faza1_Tok34_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7144
EP2_PMM_2_Faza1_Tok35_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7145
EP2_PMM_2_Faza1_Tok36_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7146
EP2_PMM_2_Faza1_Tok37_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7147
EP2_PMM_2_Faza1_Tok38_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7148
EP2_PMM_2_Faza1_Tok39_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7149
EP2_PMM_2_Faza1_Tok40_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7150
EP2_PMM_2_Faza1_Tok41_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7151
EP2_PMM_2_Faza1_Tok42_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7152
EP2_PMM_2_Faza2_Tok01_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7153
EP2_PMM_2_Faza2_Tok02_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7154
EP2_PMM_2_Faza2_Tok03_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7155
EP2_PMM_2_Faza2_Tok04_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7156
EP2_PMM_2_Faza2_Tok05_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7157
EP2_PMM_2_Faza2_Tok06_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7158
EP2_PMM_2_Faza2_Tok07_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7159
EP2_PMM_2_Faza2_Tok08_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7160
EP2_PMM_2_Faza2_Tok09_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7161
EP2_PMM_2_Faza2_Tok10_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7162
EP2_PMM_2_Faza2_Tok11_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7163
EP2_PMM_2_Faza2_Tok12_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7164
EP2_PMM_2_Faza2_Tok13_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7165
EP2_PMM_2_Faza2_Tok14_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7166
EP2_PMM_2_Faza2_Tok15_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7167
EP2_PMM_2_Faza2_Tok16_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7168
EP2_PMM_2_Faza2_Tok17_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7169
EP2_PMM_2_Faza2_Tok18_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7170
EP2_PMM_2_Faza2_Tok19_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7171
EP2_PMM_2_Faza2_Tok20_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7172
EP2_PMM_2_Faza2_Tok21_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7173
EP2_PMM_2_Faza2_Tok22_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7174
EP2_PMM_2_Faza2_Tok23_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7175
EP2_PMM_2_Faza2_Tok24_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7176
EP2_PMM_2_Faza2_Tok25_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7177
EP2_PMM_2_Faza2_Tok26_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7178
EP2_PMM_2_Faza2_Tok27_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7179
EP2_PMM_2_Faza2_Tok28_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7180
EP2_PMM_2_Faza2_Tok29_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7181
EP2_PMM_2_Faza2_Tok30_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7182
EP2_PMM_2_Faza2_Tok31_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7183
EP2_PMM_2_Faza2_Tok32_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7184
EP2_PMM_2_Faza2_Tok33_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7185
EP2_PMM_2_Faza2_Tok34_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7186
EP2_PMM_2_Faza2_Tok35_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7187
EP2_PMM_2_Faza2_Tok36_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7188
EP2_PMM_2_Faza2_Tok37_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7189
EP2_PMM_2_Faza2_Tok38_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7190
EP2_PMM_2_Faza2_Tok39_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7191
EP2_PMM_2_Faza2_Tok40_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7192
EP2_PMM_2_Faza2_Tok41_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7193
EP2_PMM_2_Faza2_Tok42_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7194
EP2_PMM_2_Faza3_Tok01_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7195
EP2_PMM_2_Faza3_Tok02_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7196
EP2_PMM_2_Faza3_Tok03_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7197
EP2_PMM_2_Faza3_Tok04_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7198
EP2_PMM_2_Faza3_Tok05_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7199
EP2_PMM_2_Faza3_Tok06_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7200
EP2_PMM_2_Faza3_Tok07_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7201
EP2_PMM_2_Faza3_Tok08_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7202
EP2_PMM_2_Faza3_Tok09_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7203
EP2_PMM_2_Faza3_Tok10_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7204
EP2_PMM_2_Faza3_Tok11_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7205
EP2_PMM_2_Faza3_Tok12_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7206
EP2_PMM_2_Faza3_Tok13_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7207
EP2_PMM_2_Faza3_Tok14_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7208
EP2_PMM_2_Faza3_Tok15_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7209
EP2_PMM_2_Faza3_Tok16_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7210
EP2_PMM_2_Faza3_Tok17_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7211
EP2_PMM_2_Faza3_Tok18_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7212
EP2_PMM_2_Faza3_Tok19_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7213
EP2_PMM_2_Faza3_Tok20_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7214
EP2_PMM_2_Faza3_Tok21_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7215
EP2_PMM_2_Faza3_Tok22_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7216
EP2_PMM_2_Faza3_Tok23_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7217
EP2_PMM_2_Faza3_Tok24_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7218
EP2_PMM_2_Faza3_Tok25_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7219
EP2_PMM_2_Faza3_Tok26_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7220
EP2_PMM_2_Faza3_Tok27_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7221
EP2_PMM_2_Faza3_Tok28_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7222
EP2_PMM_2_Faza3_Tok29_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7223
EP2_PMM_2_Faza3_Tok30_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7224
EP2_PMM_2_Faza3_Tok31_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7225
EP2_PMM_2_Faza3_Tok32_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7226
EP2_PMM_2_Faza3_Tok33_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7227
EP2_PMM_2_Faza3_Tok34_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7228
EP2_PMM_2_Faza3_Tok35_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7229
EP2_PMM_2_Faza3_Tok36_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7230
EP2_PMM_2_Faza3_Tok37_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7231
EP2_PMM_2_Faza3_Tok38_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7232
EP2_PMM_2_Faza3_Tok39_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7233
EP2_PMM_2_Faza3_Tok40_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7234
EP2_PMM_2_Faza3_Tok41_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7235
EP2_PMM_2_Faza3_Tok42_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7236
EP2_PMM_1_Faza1_Tok01_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7237
EP2_PMM_1_Faza1_Tok02_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7238
EP2_PMM_1_Faza1_Tok03_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7239
EP2_PMM_1_Faza1_Tok04_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7240
EP2_PMM_1_Faza1_Tok05_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7241
EP2_PMM_1_Faza1_Tok06_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7242
EP2_PMM_1_Faza1_Tok07_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7243
EP2_PMM_1_Faza1_Tok08_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7244
EP2_PMM_1_Faza1_Tok09_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7245
EP2_PMM_1_Faza2_Tok01_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7246
EP2_PMM_1_Faza2_Tok02_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7247
EP2_PMM_1_Faza2_Tok03_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7248
EP2_PMM_1_Faza2_Tok04_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7249
EP2_PMM_1_Faza2_Tok05_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7250
EP2_PMM_1_Faza2_Tok06_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7251
EP2_PMM_1_Faza2_Tok07_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7252
EP2_PMM_1_Faza2_Tok08_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7253
EP2_PMM_1_Faza2_Tok09_nad80_Omogoci | DIGITAL | IOD_EP2_disk | D7254
EP2_PMM_1_Faza1_Tok01_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7255
EP2_PMM_1_Faza1_Tok02_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7256
EP2_PMM_1_Faza1_Tok03_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7257
EP2_PMM_1_Faza1_Tok04_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7258
EP2_PMM_1_Faza1_Tok05_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7259
EP2_PMM_1_Faza1_Tok06_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7260
EP2_PMM_1_Faza1_Tok07_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7261
EP2_PMM_1_Faza1_Tok08_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7262
EP2_PMM_1_Faza1_Tok09_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7263
EP2_PMM_1_Faza2_Tok01_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7264
EP2_PMM_1_Faza2_Tok02_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7265
EP2_PMM_1_Faza2_Tok03_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7266
EP2_PMM_1_Faza2_Tok04_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7267
EP2_PMM_1_Faza2_Tok05_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7268
EP2_PMM_1_Faza2_Tok06_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7269
EP2_PMM_1_Faza2_Tok07_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7270
EP2_PMM_1_Faza2_Tok08_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7271
EP2_PMM_1_Faza2_Tok09_med60in80_Omogoci | DIGITAL | IOD_EP2_disk | D7272
EP2Max_analizator1 | REAL | IOD_EP2_disk | R7800 | [5 empty] | ##########
EP2Max_analizator2 | REAL | IOD_EP2_disk | R7804 | [5 empty] | ##########
EP2Max_analizator3 | REAL | IOD_EP2_disk | R7808 | [5 empty] | ##########
EP2_Anali_razlika_dnevna_E1K4 | REAL | IOD_EP2_disk | R7788 | [5 empty] | ###.#
EP2_Anali_razlika_teden_E1K4 | REAL | IOD_EP2_disk | R7792 | [5 empty] | ###.#
EP2_Anali_razlika_mes_E1K4 | REAL | IOD_EP2_disk | R7796 | [5 empty] | ###.#
EP2_XVH_AlarmOn | DIGITAL | IOD_EP2_TCP | 00267
EP2_UserloggedIn_mem | DIGITAL | IOD_EP2_mem | D7285
EP2OmogociVseAlarme | DIGITAL | IOD_EP2_disk | D8000
EP2OmogociVseSMSAlarme | DIGITAL | IOD_EP2_disk | D8001
EP2OmogociVseDogodke_DO | DIGITAL | IOD_EP2_disk | D8002
EP2OmogociVseDogodke_DI | DIGITAL | IOD_EP2_disk | D8003
EP2OmogociVseDogodke_COM | DIGITAL | IOD_EP2_disk | D8004
EP2_OnemAlarmPon | DIGITAL | IOD_EP2_disk | D8005
EP2_PricetekSMSAlarmov1 | INT | IOD_EP2_disk | I8006
EP2_KonecSMSAlarmov1 | INT | IOD_EP2_disk | I8008
EP2_omogocanje_tok_opozorila | DIGITAL | IOD_EP2_disk | D8010[4]
EP2_omogocanje_tok_alarm | DIGITAL | IOD_EP2_disk | D8014[4]
EP2_meja_tok_opozorilo | LONG | IOD_EP2_disk | L8018[4]
EP2_meja_tok_alarm | LONG | IOD_EP2_disk | L8032[4]
EP2AlarmGenCirc1 | DIGITAL | 1 | EP2:.AlarmGenCirc1
EP2AlarmGenComm | DIGITAL | 2 | EP2:.AlarmGenComm
EP2AlarmGenDI | DIGITAL | 3 | EP2:.AlarmGenDI
EP2AlarmGenKlima5 | DIGITAL | 4 | EP2:.AlarmGenKlima5
EP2AlarmGenKlima6 | DIGITAL | 5 | EP2:.AlarmGenKlima6
EP2AlarmGenPMM1 | DIGITAL | 6 | EP2:.AlarmGenPMM1
EP2AlarmGenPMM2 | DIGITAL | 7 | EP2:.AlarmGenPMM2
EP2AlarmGenPMM3 | DIGITAL | 8 | EP2:.AlarmGenPMM3
EP2AlarmGenRest | DIGITAL | IOD_EP2_TCP | 00268
EP2AlarmGenUPS1 | DIGITAL | 9 | EP2:.AlarmGenUPS1
EP2AlarmGenUPS2 | DIGITAL | 10 | EP2:.AlarmGenUPS2
EP2Circ1CosFi_III | REAL | 11 | EP2:.Circ[1].CosFi_III
EP2Circ1DelovnaEnergija | REAL | 12 | EP2:.Circ[1].DelovnaEnergija
EP2Circ1DelovnaMoc_III | REAL | 13 | EP2:.Circ[1].DelovnaMoc_III
EP2Circ1DelovnaMoc_L1 | REAL | 14 | EP2:.Circ[1].DelovnaMoc_L1
EP2Circ1DelovnaMoc_L2 | REAL | 15 | EP2:.Circ[1].DelovnaMoc_L2
EP2Circ1DelovnaMoc_L3 | REAL | 16 | EP2:.Circ[1].DelovnaMoc_L3
EP2Circ1Frekvenca_L1 | REAL | 17 | EP2:.Circ[1].Frekvenca_L1
EP2Circ1InduktivnaEnergija | REAL | 18 | EP2:.Circ[1].InduktivnaEnergija
EP2Circ1InduktivnaMoc_III | REAL | 19 | EP2:.Circ[1].InduktivnaMoc_III
EP2Circ1JalovaMoc_L1 | REAL | 20 | EP2:.Circ[1].JalovaMoc_L1
EP2Circ1JalovaMoc_L2 | REAL | 21 | EP2:.Circ[1].JalovaMoc_L2
EP2Circ1JalovaMoc_L3 | REAL | 22 | EP2:.Circ[1].JalovaMoc_L3
EP2Circ1KapacitivnaEnergija | REAL | 23 | EP2:.Circ[1].KapacitivnaEnergija
EP2Circ1KapacitivnaMoc_III | REAL | 24 | EP2:.Circ[1].KapacitivnaMoc_III
EP2Circ1MaximumDemand | REAL | 25 | EP2:.Circ[1].MaximumDemand
EP2Circ1Napetost_L1_L2 | REAL | 26 | EP2:.Circ[1].Napetost_L1_L2
EP2Circ1Napetost_L1_N | REAL | 27 | EP2:.Circ[1].Napetost_L1_N
EP2Circ1Napetost_L2_L3 | REAL | 28 | EP2:.Circ[1].Napetost_L2_L3
EP2Circ1Napetost_L2_N | REAL | 29 | EP2:.Circ[1].Napetost_L2_N
EP2Circ1Napetost_L3_L1 | REAL | 30 | EP2:.Circ[1].Napetost_L3_L1
EP2Circ1Napetost_L3_N | REAL | 31 | EP2:.Circ[1].Napetost_L3_N
EP2Circ1NavideznaMoc_III | REAL | 32 | EP2:.Circ[1].NavideznaMoc_III
EP2Circ1NicelniTok | REAL | 33 | EP2:.Circ[1].NicelniTok
EP2Circ1PowerFactor_III | REAL | 34 | EP2:.Circ[1].PowerFactor_III
EP2Circ1PowerFactor_L1 | REAL | 35 | EP2:.Circ[1].PowerFactor_L1
EP2Circ1PowerFactor_L2 | REAL | 36 | EP2:.Circ[1].PowerFactor_L2
EP2Circ1PowerFactor_L3 | REAL | 37 | EP2:.Circ[1].PowerFactor_L3
EP2Circ1THDI_L1 | REAL | 38 | EP2:.Circ[1].THDI_L1
EP2Circ1THDI_L2 | REAL | 39 | EP2:.Circ[1].THDI_L2
EP2Circ1THDI_L3 | REAL | 40 | EP2:.Circ[1].THDI_L3
EP2Circ1THDV_L1 | REAL | 41 | EP2:.Circ[1].THDV_L1
EP2Circ1THDV_L2 | REAL | 42 | EP2:.Circ[1].THDV_L2
EP2Circ1THDV_L3 | REAL | 43 | EP2:.Circ[1].THDV_L3
EP2Circ1Tok_L1 | REAL | 44 | EP2:.Circ[1].Tok_L1
EP2Circ1Tok_L2 | REAL | 45 | EP2:.Circ[1].Tok_L2
EP2Circ1Tok_L3 | REAL | 46 | EP2:.Circ[1].Tok_L3
EP2Circ1TokPovprecje_III | REAL | 47 | EP2:.Circ[1].TokPovprecje_III
EP2CircutorCosFi_III | REAL | 48 | EP2:.Circutor.CosFi_III
EP2CircutorDelovnaEnergija | REAL | 49 | EP2:.Circutor.DelovnaEnergija
EP2CircutorDelovnaMoc_III | REAL | 50 | EP2:.Circutor.DelovnaMoc_III
EP2CircutorDelovnaMoc_L1 | REAL | 51 | EP2:.Circutor.DelovnaMoc_L1
EP2CircutorDelovnaMoc_L2 | REAL | 52 | EP2:.Circutor.DelovnaMoc_L2
EP2CircutorDelovnaMoc_L3 | REAL | 53 | EP2:.Circutor.DelovnaMoc_L3
EP2CircutorFrekvenca_L1 | REAL | 54 | EP2:.Circutor.Frekvenca_L1
EP2CircutorInduktivnaEnergija | REAL | 55 | EP2:.Circutor.InduktivnaEnergija
EP2CircutorInduktivnaMoc_III | REAL | 56 | EP2:.Circutor.InduktivnaMoc_III
EP2CircutorJalovaMoc_L1 | REAL | 57 | EP2:.Circutor.JalovaMoc_L1
EP2CircutorJalovaMoc_L2 | REAL | 58 | EP2:.Circutor.JalovaMoc_L2
EP2CircutorJalovaMoc_L3 | REAL | 59 | EP2:.Circutor.JalovaMoc_L3
EP2CircutorKapacitivnaEnergija | REAL | 60 | EP2:.Circutor.KapacitivnaEnergija
EP2CircutorKapacitivnaMoc_III | REAL | 61 | EP2:.Circutor.KapacitivnaMoc_III
EP2CircutorMaximumDemand | REAL | 62 | EP2:.Circutor.MaximumDemand
EP2CircutorNapetost_L1_L2 | REAL | 63 | EP2:.Circutor.Napetost_L1_L2
EP2CircutorNapetost_L1_N | REAL | 64 | EP2:.Circutor.Napetost_L1_N
EP2CircutorNapetost_L2_L3 | REAL | 65 | EP2:.Circutor.Napetost_L2_L3
EP2CircutorNapetost_L2_N | REAL | 66 | EP2:.Circutor.Napetost_L2_N
EP2CircutorNapetost_L3_L1 | REAL | 67 | EP2:.Circutor.Napetost_L3_L1
EP2CircutorNapetost_L3_N | REAL | 68 | EP2:.Circutor.Napetost_L3_N
EP2CircutorNavideznaMoc_III | REAL | 69 | EP2:.Circutor.NavideznaMoc_III
EP2CircutorNicelniTok | REAL | 70 | EP2:.Circutor.NicelniTok
EP2CircutorPowerFactor_III | REAL | 71 | EP2:.Circutor.PowerFactor_III
EP2CircutorPowerFactor_L1 | REAL | 72 | EP2:.Circutor.PowerFactor_L1
EP2CircutorPowerFactor_L2 | REAL | 73 | EP2:.Circutor.PowerFactor_L2
EP2CircutorPowerFactor_L3 | REAL | 74 | EP2:.Circutor.PowerFactor_L3
EP2CircutorTHDI_L1 | REAL | 75 | EP2:.Circutor.THDI_L1
EP2CircutorTHDI_L2 | REAL | 76 | EP2:.Circutor.THDI_L2
EP2CircutorTHDI_L3 | REAL | 77 | EP2:.Circutor.THDI_L3
EP2CircutorTHDV_L1 | REAL | 78 | EP2:.Circutor.THDV_L1
EP2CircutorTHDV_L2 | REAL | 79 | EP2:.Circutor.THDV_L2
EP2CircutorTHDV_L3 | REAL | 80 | EP2:.Circutor.THDV_L3
EP2CircutorTok_L1 | REAL | 81 | EP2:.Circutor.Tok_L1
EP2CircutorTok_L2 | REAL | 82 | EP2:.Circutor.Tok_L2
EP2CircutorTok_L3 | REAL | 83 | EP2:.Circutor.Tok_L3
EP2CircutorTokPovprecje_III | REAL | 84 | EP2:.Circutor.TokPovprecje_III
EP2ComSCADA | DIGITAL | 85 | EP2:.ComSCADA
EP2ComSCADA1 | DIGITAL | 86 | EP2:.ComSCADA1
EP2DateTimeDan | BYTE | 87 | EP2:.DateTime.Dan
EP2DateTimeLeto | BYTE | 88 | EP2:.DateTime.Leto
EP2DateTimeMesec | BYTE | 89 | EP2:.DateTime.Mesec
EP2DateTimeMinuta | BYTE | 90 | EP2:.DateTime.Minuta
EP2DateTimeSekunda | BYTE | 91 | EP2:.DateTime.Sekunda
EP2DateTimeUra | BYTE | 92 | EP2:.DateTime.Ura
EP2DI_Klima5_ERR | DIGITAL | 93 | EP2:.DI_Klima5_ERR
EP2DI_Klima5_ON | DIGITAL | 94 | EP2:.DI_Klima5_ON
EP2DI_Klima6_ERR | DIGITAL | 95 | EP2:.DI_Klima6_ERR
EP2DI_Klima6_ON | DIGITAL | 96 | EP2:.DI_Klima6_ON
EP2DI_KlimaSplit1_ERR | DIGITAL | 97 | EP2:.DI_KlimaSplit1_ERR
EP2DI_KlimaSplit1_ON | DIGITAL | 98 | EP2:.DI_KlimaSplit1_ON
EP2DI_Q10_OdcKlima6_IZP | DIGITAL | 99 | EP2:.DI_Q10_OdcKlima6_IZP
EP2DI_Q10_OdcKlima6_ON | DIGITAL | 100 | EP2:.DI_Q10_OdcKlima6_ON
EP2DI_Q11_OdcVent1_ON | DIGITAL | 101 | EP2:.DI_Q11_OdcVent1_ON
EP2DI_Q12_Rezerva_ON | DIGITAL | 102 | EP2:.DI_Q12_Rezerva_ON
EP2DI_Q1_GlavnoStikalo_ON | DIGITAL | 103 | EP2:.DI_Q1_GlavnoStikalo_ON
EP2DI_Q25_OdcUpsA_IZP | DIGITAL | 104 | EP2:.DI_Q25_OdcUpsA_IZP
EP2DI_Q25_OdcUpsA_ON | DIGITAL | 105 | EP2:.DI_Q25_OdcUpsA_ON
EP2DI_Q26_OdcByA_IZP | DIGITAL | 106 | EP2:.DI_Q26_OdcByA_IZP
EP2DI_Q26_OdcByA_ON | DIGITAL | 107 | EP2:.DI_Q26_OdcByA_ON
EP2DI_Q27_OdcByUpsA_IZP | DIGITAL | 108 | EP2:.DI_Q27_OdcByUpsA_IZP
EP2DI_Q27_OdcByUpsA_ON | DIGITAL | 109 | EP2:.DI_Q27_OdcByUpsA_ON
EP2DI_Q28_OdcUpsB_IZP | DIGITAL | 110 | EP2:.DI_Q28_OdcUpsB_IZP
EP2DI_Q28_OdcUpsB_ON | DIGITAL | 111 | EP2:.DI_Q28_OdcUpsB_ON
EP2DI_Q29_OdcByB_IZP | DIGITAL | 112 | EP2:.DI_Q29_OdcByB_IZP
EP2DI_Q29_OdcByB_ON | DIGITAL | 113 | EP2:.DI_Q29_OdcByB_ON
EP2DI_Q2_Rezerva_IZP | DIGITAL | 114 | EP2:.DI_Q2_Rezerva_IZP
EP2DI_Q2_Rezerva_ON | DIGITAL | 115 | EP2:.DI_Q2_Rezerva_ON
EP2DI_Q30_OdcByUpsB_IZP | DIGITAL | 116 | EP2:.DI_Q30_OdcByUpsB_IZP
EP2DI_Q30_OdcByUpsB_ON | DIGITAL | 117 | EP2:.DI_Q30_OdcByUpsB_ON
EP2DI_Q31_DovByUpsA_ON | DIGITAL | 118 | EP2:.DI_Q31_DovByUpsA_ON
EP2DI_Q32_DovByA_ON | DIGITAL | 119 | EP2:.DI_Q32_DovByA_ON
EP2DI_Q33_DovByUpsB_ON | DIGITAL | 120 | EP2:.DI_Q33_DovByUpsB_ON
EP2DI_Q34_DovByB_ON | DIGITAL | 121 | EP2:.DI_Q34_DovByB_ON
EP2DI_Q5_OdcKlima1_IZP | DIGITAL | 122 | EP2:.DI_Q5_OdcKlima1_IZP
EP2DI_Q5_OdcKlima1_ON | DIGITAL | 123 | EP2:.DI_Q5_OdcKlima1_ON
EP2DI_Q6_OdcKlima2_IZP | DIGITAL | 124 | EP2:.DI_Q6_OdcKlima2_IZP
EP2DI_Q6_OdcKlima2_ON | DIGITAL | 125 | EP2:.DI_Q6_OdcKlima2_ON
EP2DI_Q7_OdcKlima3_IZP | DIGITAL | 126 | EP2:.DI_Q7_OdcKlima3_IZP
EP2DI_Q7_OdcKlima3_ON | DIGITAL | 127 | EP2:.DI_Q7_OdcKlima3_ON
EP2DI_Q8_OdcKlima4_IZP | DIGITAL | 128 | EP2:.DI_Q8_OdcKlima4_IZP
EP2DI_Q8_OdcKlima4_ON | DIGITAL | 129 | EP2:.DI_Q8_OdcKlima4_ON
EP2DI_Q9_OdcKlima5_IZP | DIGITAL | 130 | EP2:.DI_Q9_OdcKlima5_IZP
EP2DI_Q9_OdcKlima5_ON | DIGITAL | 131 | EP2:.DI_Q9_OdcKlima5_ON
EP2DI_RazlitjeVodeK5K6 | DIGITAL | 132 | EP2:.DI_RazlitjeVodeK5K6
EP2DI_UPS_Alarm | DIGITAL | 133 | EP2:.DI_UPS_Alarm
EP2DI_UPS_BatNacin | DIGITAL | 134 | EP2:.DI_UPS_BatNacin
EP2DI_UPS_Polnjenje | DIGITAL | 135 | EP2:.DI_UPS_Polnjenje
EP2DI_UpsA_BypassON | DIGITAL | IOD_EP2_TCP | 00269
EP2DI_UpsA_ERR | DIGITAL | IOD_EP2_TCP | 00270
EP2DI_UpsB_BypassON | DIGITAL | IOD_EP2_TCP | 00271
EP2DI_UpsB_ERR | DIGITAL | IOD_EP2_TCP | 00272
EP2DIN_Klima5_ERR | DIGITAL | IOD_EP2_TCP | 00273
EP2DIN_Klima6_ERR | DIGITAL | IOD_EP2_TCP | 00274
EP2DIN_KlimaSplit1_ERR | DIGITAL | IOD_EP2_TCP | 00275
EP2DIN_Q10_OdcKlima6_IZP | DIGITAL | IOD_EP2_TCP | 00276
EP2DIN_Q25_OdcUpsA_IZP | DIGITAL | IOD_EP2_TCP | 00277
EP2DIN_Q26_OdcByA_IZP | DIGITAL | IOD_EP2_TCP | 00278
EP2DIN_Q27_OdcByUpsA_IZP | DIGITAL | IOD_EP2_TCP | 00279
EP2DIN_Q28_OdcUpsB_IZP | DIGITAL | IOD_EP2_TCP | 00280
EP2DIN_Q29_OdcByB_IZP | DIGITAL | IOD_EP2_TCP | 00281
EP2DIN_Q2_Rezerva_IZP | DIGITAL | IOD_EP2_TCP | 00282
EP2DIN_Q30_OdcByUpsB_IZP | DIGITAL | IOD_EP2_TCP | 00283
EP2DIN_Q5_OdcKlima1_IZP | DIGITAL | IOD_EP2_TCP | 00284
EP2DIN_Q6_OdcKlima2_IZP | DIGITAL | IOD_EP2_TCP | 00285
EP2DIN_Q7_OdcKlima3_IZP | DIGITAL | IOD_EP2_TCP | 00286
EP2DIN_Q8_OdcKlima4_IZP | DIGITAL | IOD_EP2_TCP | 00287
EP2DIN_Q9_OdcKlima5_IZP | DIGITAL | IOD_EP2_TCP | 00288
EP2DIN_UpsA_BypassON | DIGITAL | 137 | EP2:.DIN_UpsA_BypassON
EP2DIN_UpsA_ERR | DIGITAL | 136 | EP2:.DIN_UpsA_ERR
EP2DIN_UpsB_BypassON | DIGITAL | 139 | EP2:.DIN_UpsB_BypassON
EP2DIN_UpsB_ERR | DIGITAL | 138 | EP2:.DIN_UpsB_ERR
EP2DO_Klima5_Izklop | DIGITAL | 140 | EP2:.DO_Klima5_Izklop
EP2DO_Klima6_Izklop | DIGITAL | 141 | EP2:.DO_Klima6_Izklop
EP2ErrComCirc1 | DIGITAL | 142 | EP2:.ErrComCirc[1]
EP2ErrComCirc2 | DIGITAL | 143 | EP2:.ErrComCirc[2]
EP2ErrComCirc3 | DIGITAL | 144 | EP2:.ErrComCirc[3]
EP2ErrComCirc4 | DIGITAL | 145 | EP2:.ErrComCirc[4]
EP2ErrComCirc5 | DIGITAL | 146 | EP2:.ErrComCirc[5]
EP2ErrComKlima1 | DIGITAL | 147 | EP2:.ErrComKlima[1]
EP2ErrComKlima2 | DIGITAL | 148 | EP2:.ErrComKlima[2]
EP2ErrComKlima3 | DIGITAL | 149 | EP2:.ErrComKlima[3]
EP2ErrComKlima4 | DIGITAL | 150 | EP2:.ErrComKlima[4]
EP2ErrComKlima5 | DIGITAL | 151 | EP2:.ErrComKlima[5]
EP2ErrComKlima6 | DIGITAL | 152 | EP2:.ErrComKlima[6]
EP2ErrCommScada | DIGITAL | 153 | EP2:.ErrCommScada
EP2ErrComPanelPLC | DIGITAL | 154 | EP2:.ErrComPanelPLC
EP2ErrComPMM1 | DIGITAL | 155 | EP2:.ErrComPMM[1]
EP2ErrComPMM2 | DIGITAL | 156 | EP2:.ErrComPMM[2]
EP2ErrComPMM3 | DIGITAL | 157 | EP2:.ErrComPMM[3]
EP2ErrComPort2 | DIGITAL | 158 | EP2:.ErrComPort2
EP2ErrComPort3 | DIGITAL | 159 | EP2:.ErrComPort3
EP2ErrComPort4 | DIGITAL | 160 | EP2:.ErrComPort4
EP2ErrComUPS1 | DIGITAL | 161 | EP2:.ErrComUPS[1]
EP2ErrComUPS2 | DIGITAL | 162 | EP2:.ErrComUPS[2]
EP2ErrorComCirc1Code10 | INT | IOD_EP2_TCP | 40092
EP2ErrorComCirc1Code11 | INT | IOD_EP2_TCP | 40093
EP2ErrorComCirc1Code12 | INT | IOD_EP2_TCP | 40094
EP2ErrorComCirc1Code13 | INT | IOD_EP2_TCP | 40095
EP2ErrorComCirc1Code14 | INT | IOD_EP2_TCP | 40096
EP2ErrorComCirc1Code15 | INT | IOD_EP2_TCP | 40097
EP2ErrorComCirc1Code1 | INT | IOD_EP2_TCP | 40098
EP2ErrorComCirc1Code2 | INT | IOD_EP2_TCP | 40099
EP2ErrorComCirc1Code3 | INT | IOD_EP2_TCP | 40100
EP2ErrorComCirc1Code4 | INT | IOD_EP2_TCP | 40101
EP2ErrorComCirc1Code5 | INT | IOD_EP2_TCP | 40102
EP2ErrorComCirc1Code6 | INT | IOD_EP2_TCP | 40103
EP2ErrorComCirc1Code7 | INT | IOD_EP2_TCP | 40104
EP2ErrorComCirc1Code8 | INT | IOD_EP2_TCP | 40105
EP2ErrorComCirc1Code9 | INT | IOD_EP2_TCP | 40106
EP2ErrorComCirc1Error | DIGITAL | IOD_EP2_TCP | 00289
EP2ErrorComCirc1Status | INT | IOD_EP2_TCP | 40107
EP2ErrorComCirc2Code10 | INT | IOD_EP2_TCP | 40108
EP2ErrorComCirc2Code11 | INT | IOD_EP2_TCP | 40109
EP2ErrorComCirc2Code12 | INT | IOD_EP2_TCP | 40110
EP2ErrorComCirc2Code13 | INT | IOD_EP2_TCP | 40111
EP2ErrorComCirc2Code14 | INT | IOD_EP2_TCP | 40112
EP2ErrorComCirc2Code15 | INT | IOD_EP2_TCP | 40113
EP2ErrorComCirc2Code1 | INT | IOD_EP2_TCP | 40114
EP2ErrorComCirc2Code2 | INT | IOD_EP2_TCP | 40115
EP2ErrorComCirc2Code3 | INT | IOD_EP2_TCP | 40116
EP2ErrorComCirc2Code4 | INT | IOD_EP2_TCP | 40117
EP2ErrorComCirc2Code5 | INT | IOD_EP2_TCP | 40118
EP2ErrorComCirc2Code6 | INT | IOD_EP2_TCP | 40119
EP2ErrorComCirc2Code7 | INT | IOD_EP2_TCP | 40120
EP2ErrorComCirc2Code8 | INT | IOD_EP2_TCP | 40121
EP2ErrorComCirc2Code9 | INT | IOD_EP2_TCP | 40122
EP2ErrorComCirc2Error | DIGITAL | IOD_EP2_TCP | 00290
EP2ErrorComCirc2Status | INT | IOD_EP2_TCP | 40123
EP2ErrorComCirc3Code10 | INT | IOD_EP2_TCP | 40124
EP2ErrorComCirc3Code11 | INT | IOD_EP2_TCP | 40125
EP2ErrorComCirc3Code12 | INT | IOD_EP2_TCP | 40126
EP2ErrorComCirc3Code13 | INT | IOD_EP2_TCP | 40127
EP2ErrorComCirc3Code14 | INT | IOD_EP2_TCP | 40128
EP2ErrorComCirc3Code15 | INT | IOD_EP2_TCP | 40129
EP2ErrorComCirc3Code1 | INT | IOD_EP2_TCP | 40130
EP2ErrorComCirc3Code2 | INT | IOD_EP2_TCP | 40131
EP2ErrorComCirc3Code3 | INT | IOD_EP2_TCP | 40132
EP2ErrorComCirc3Code4 | INT | IOD_EP2_TCP | 40133
EP2ErrorComCirc3Code5 | INT | IOD_EP2_TCP | 40134
EP2ErrorComCirc3Code6 | INT | IOD_EP2_TCP | 40135
EP2ErrorComCirc3Code7 | INT | IOD_EP2_TCP | 40136
EP2ErrorComCirc3Code8 | INT | IOD_EP2_TCP | 40137
EP2ErrorComCirc3Code9 | INT | IOD_EP2_TCP | 40138
EP2ErrorComCirc3Error | DIGITAL | IOD_EP2_TCP | 00291
EP2ErrorComCirc3Status | INT | IOD_EP2_TCP | 40139
EP2ErrorComCirc4Code10 | INT | IOD_EP2_TCP | 40140
EP2ErrorComCirc4Code11 | INT | IOD_EP2_TCP | 40141
EP2ErrorComCirc4Code12 | INT | IOD_EP2_TCP | 40142
EP2ErrorComCirc4Code13 | INT | IOD_EP2_TCP | 40143
EP2ErrorComCirc4Code14 | INT | IOD_EP2_TCP | 40144
EP2ErrorComCirc4Code15 | INT | IOD_EP2_TCP | 40145
EP2ErrorComCirc4Code1 | INT | IOD_EP2_TCP | 40146
EP2ErrorComCirc4Code2 | INT | IOD_EP2_TCP | 40147
EP2ErrorComCirc4Code3 | INT | IOD_EP2_TCP | 40148
EP2ErrorComCirc4Code4 | INT | IOD_EP2_TCP | 40149
EP2ErrorComCirc4Code5 | INT | IOD_EP2_TCP | 40150
EP2ErrorComCirc4Code6 | INT | IOD_EP2_TCP | 40151
EP2ErrorComCirc4Code7 | INT | IOD_EP2_TCP | 40152
EP2ErrorComCirc4Code8 | INT | IOD_EP2_TCP | 40153
EP2ErrorComCirc4Code9 | INT | IOD_EP2_TCP | 40154
EP2ErrorComCirc4Error | DIGITAL | IOD_EP2_TCP | 00292
EP2ErrorComCirc4Status | INT | IOD_EP2_TCP | 40155
EP2ErrorComCirc5Code10 | INT | IOD_EP2_TCP | 40156
EP2ErrorComCirc5Code11 | INT | IOD_EP2_TCP | 40157
EP2ErrorComCirc5Code12 | INT | IOD_EP2_TCP | 40158
EP2ErrorComCirc5Code13 | INT | IOD_EP2_TCP | 40159
EP2ErrorComCirc5Code14 | INT | IOD_EP2_TCP | 40160
EP2ErrorComCirc5Code15 | INT | IOD_EP2_TCP | 40161
EP2ErrorComCirc5Code1 | INT | IOD_EP2_TCP | 40162
EP2ErrorComCirc5Code2 | INT | IOD_EP2_TCP | 40163
EP2ErrorComCirc5Code3 | INT | IOD_EP2_TCP | 40164
EP2ErrorComCirc5Code4 | INT | IOD_EP2_TCP | 40165
EP2ErrorComCirc5Code5 | INT | IOD_EP2_TCP | 40166
EP2ErrorComCirc5Code6 | INT | IOD_EP2_TCP | 40167
EP2ErrorComCirc5Code7 | INT | IOD_EP2_TCP | 40168
EP2ErrorComCirc5Code8 | INT | IOD_EP2_TCP | 40169
EP2ErrorComCirc5Code9 | INT | IOD_EP2_TCP | 40170
EP2ErrorComCirc5Error | DIGITAL | IOD_EP2_TCP | 00293
EP2ErrorComCirc5Status | INT | IOD_EP2_TCP | 40171
EP2ErrorComKlima1Code10 | INT | IOD_EP2_TCP | 40172
EP2ErrorComKlima1Code11 | INT | IOD_EP2_TCP | 40173
EP2ErrorComKlima1Code12 | INT | IOD_EP2_TCP | 40174
EP2ErrorComKlima1Code13 | INT | IOD_EP2_TCP | 40175
EP2ErrorComKlima1Code14 | INT | IOD_EP2_TCP | 40176
EP2ErrorComKlima1Code15 | INT | IOD_EP2_TCP | 40177
EP2ErrorComKlima1Code1 | INT | IOD_EP2_TCP | 40178
EP2ErrorComKlima1Code2 | INT | IOD_EP2_TCP | 40179
EP2ErrorComKlima1Code3 | INT | IOD_EP2_TCP | 40180
EP2ErrorComKlima1Code4 | INT | IOD_EP2_TCP | 40181
EP2ErrorComKlima1Code5 | INT | IOD_EP2_TCP | 40182
EP2ErrorComKlima1Code6 | INT | IOD_EP2_TCP | 40183
EP2ErrorComKlima1Code7 | INT | IOD_EP2_TCP | 40184
EP2ErrorComKlima1Code8 | INT | IOD_EP2_TCP | 40185
EP2ErrorComKlima1Code9 | INT | IOD_EP2_TCP | 40186
EP2ErrorComKlima1Error | DIGITAL | IOD_EP2_TCP | 00294
EP2ErrorComKlima1Status | INT | IOD_EP2_TCP | 40187
EP2ErrorComKlima2Code10 | INT | IOD_EP2_TCP | 40188
EP2ErrorComKlima2Code11 | INT | IOD_EP2_TCP | 40189
EP2ErrorComKlima2Code12 | INT | IOD_EP2_TCP | 40190
EP2ErrorComKlima2Code13 | INT | IOD_EP2_TCP | 40191
EP2ErrorComKlima2Code14 | INT | IOD_EP2_TCP | 40192
EP2ErrorComKlima2Code15 | INT | IOD_EP2_TCP | 40193
EP2ErrorComKlima2Code1 | INT | IOD_EP2_TCP | 40194
EP2ErrorComKlima2Code2 | INT | IOD_EP2_TCP | 40195
EP2ErrorComKlima2Code3 | INT | IOD_EP2_TCP | 40196
EP2ErrorComKlima2Code4 | INT | IOD_EP2_TCP | 40197
EP2ErrorComKlima2Code5 | INT | IOD_EP2_TCP | 40198
EP2ErrorComKlima2Code6 | INT | IOD_EP2_TCP | 40199
EP2ErrorComKlima2Code7 | INT | IOD_EP2_TCP | 40200
EP2ErrorComKlima2Code8 | INT | IOD_EP2_TCP | 40201
EP2ErrorComKlima2Code9 | INT | IOD_EP2_TCP | 40202
EP2ErrorComKlima2Error | DIGITAL | IOD_EP2_TCP | 00295
EP2ErrorComKlima2Status | INT | IOD_EP2_TCP | 40203
EP2ErrorComKlima3Code10 | INT | IOD_EP2_TCP | 40204
EP2ErrorComKlima3Code11 | INT | IOD_EP2_TCP | 40205
EP2ErrorComKlima3Code12 | INT | IOD_EP2_TCP | 40206
EP2ErrorComKlima3Code13 | INT | IOD_EP2_TCP | 40207
EP2ErrorComKlima3Code14 | INT | IOD_EP2_TCP | 40208
EP2ErrorComKlima3Code15 | INT | IOD_EP2_TCP | 40209
EP2ErrorComKlima3Code1 | INT | IOD_EP2_TCP | 40210
EP2ErrorComKlima3Code2 | INT | IOD_EP2_TCP | 40211
EP2ErrorComKlima3Code3 | INT | IOD_EP2_TCP | 40212
EP2ErrorComKlima3Code4 | INT | IOD_EP2_TCP | 40213
EP2ErrorComKlima3Code5 | INT | IOD_EP2_TCP | 40214
EP2ErrorComKlima3Code6 | INT | IOD_EP2_TCP | 40215
EP2ErrorComKlima3Code7 | INT | IOD_EP2_TCP | 40216
EP2ErrorComKlima3Code8 | INT | IOD_EP2_TCP | 40217
EP2ErrorComKlima3Code9 | INT | IOD_EP2_TCP | 40218
EP2ErrorComKlima3Error | DIGITAL | IOD_EP2_TCP | 00296
EP2ErrorComKlima3Status | INT | IOD_EP2_TCP | 40219
EP2ErrorComKlima4Code10 | INT | IOD_EP2_TCP | 40220
EP2ErrorComKlima4Code11 | INT | IOD_EP2_TCP | 40221
EP2ErrorComKlima4Code12 | INT | IOD_EP2_TCP | 40222
EP2ErrorComKlima4Code13 | INT | IOD_EP2_TCP | 40223
EP2ErrorComKlima4Code14 | INT | IOD_EP2_TCP | 40224
EP2ErrorComKlima4Code15 | INT | IOD_EP2_TCP | 40225
EP2ErrorComKlima4Code1 | INT | IOD_EP2_TCP | 40226
EP2ErrorComKlima4Code2 | INT | IOD_EP2_TCP | 40227
EP2ErrorComKlima4Code3 | INT | IOD_EP2_TCP | 40228
EP2ErrorComKlima4Code4 | INT | IOD_EP2_TCP | 40229
EP2ErrorComKlima4Code5 | INT | IOD_EP2_TCP | 40230
EP2ErrorComKlima4Code6 | INT | IOD_EP2_TCP | 40231
EP2ErrorComKlima4Code7 | INT | IOD_EP2_TCP | 40232
EP2ErrorComKlima4Code8 | INT | IOD_EP2_TCP | 40233
EP2ErrorComKlima4Code9 | INT | IOD_EP2_TCP | 40234
EP2ErrorComKlima4Error | DIGITAL | IOD_EP2_TCP | 00297
EP2ErrorComKlima4Status | INT | IOD_EP2_TCP | 40235
EP2ErrorComKlima5Code10 | INT | IOD_EP2_TCP | 40236
EP2ErrorComKlima5Code11 | INT | IOD_EP2_TCP | 40237
EP2ErrorComKlima5Code12 | INT | IOD_EP2_TCP | 40238
EP2ErrorComKlima5Code13 | INT | IOD_EP2_TCP | 40239
EP2ErrorComKlima5Code14 | INT | IOD_EP2_TCP | 40240
EP2ErrorComKlima5Code15 | INT | IOD_EP2_TCP | 40241
EP2ErrorComKlima5Code1 | INT | IOD_EP2_TCP | 40242
EP2ErrorComKlima5Code2 | INT | IOD_EP2_TCP | 40243
EP2ErrorComKlima5Code3 | INT | IOD_EP2_TCP | 40244
EP2ErrorComKlima5Code4 | INT | IOD_EP2_TCP | 40245
EP2ErrorComKlima5Code5 | INT | IOD_EP2_TCP | 40246
EP2ErrorComKlima5Code6 | INT | IOD_EP2_TCP | 40247
EP2ErrorComKlima5Code7 | INT | IOD_EP2_TCP | 40248
EP2ErrorComKlima5Code8 | INT | IOD_EP2_TCP | 40249
EP2ErrorComKlima5Code9 | INT | IOD_EP2_TCP | 40250
EP2ErrorComKlima5Error | DIGITAL | IOD_EP2_TCP | 00298
EP2ErrorComKlima5Status | INT | IOD_EP2_TCP | 40251
EP2ErrorComKlima6Code10 | INT | IOD_EP2_TCP | 40252
EP2ErrorComKlima6Code11 | INT | IOD_EP2_TCP | 40253
EP2ErrorComKlima6Code12 | INT | IOD_EP2_TCP | 40254
EP2ErrorComKlima6Code13 | INT | IOD_EP2_TCP | 40255
EP2ErrorComKlima6Code14 | INT | IOD_EP2_TCP | 40256
EP2ErrorComKlima6Code15 | INT | IOD_EP2_TCP | 40257
EP2ErrorComKlima6Code1 | INT | IOD_EP2_TCP | 40258
EP2ErrorComKlima6Code2 | INT | IOD_EP2_TCP | 40259
EP2ErrorComKlima6Code3 | INT | IOD_EP2_TCP | 40260
EP2ErrorComKlima6Code4 | INT | IOD_EP2_TCP | 40261
EP2ErrorComKlima6Code5 | INT | IOD_EP2_TCP | 40262
EP2ErrorComKlima6Code6 | INT | IOD_EP2_TCP | 40263
EP2ErrorComKlima6Code7 | INT | IOD_EP2_TCP | 40264
EP2ErrorComKlima6Code8 | INT | IOD_EP2_TCP | 40265
EP2ErrorComKlima6Code9 | INT | IOD_EP2_TCP | 40266
EP2ErrorComKlima6Error | DIGITAL | IOD_EP2_TCP | 00299
EP2ErrorComKlima6Status | INT | IOD_EP2_TCP | 40267
EP2ErrorComPMM1Code10 | INT | IOD_EP2_TCP | 40268
EP2ErrorComPMM1Code11 | INT | IOD_EP2_TCP | 40269
EP2ErrorComPMM1Code12 | INT | IOD_EP2_TCP | 40270
EP2ErrorComPMM1Code13 | INT | IOD_EP2_TCP | 40271
EP2ErrorComPMM1Code14 | INT | IOD_EP2_TCP | 40272
EP2ErrorComPMM1Code15 | INT | IOD_EP2_TCP | 40273
EP2ErrorComPMM1Code1 | INT | IOD_EP2_TCP | 40274
EP2ErrorComPMM1Code2 | INT | IOD_EP2_TCP | 40275
EP2ErrorComPMM1Code3 | INT | IOD_EP2_TCP | 40276
EP2ErrorComPMM1Code4 | INT | IOD_EP2_TCP | 40277
EP2ErrorComPMM1Code5 | INT | IOD_EP2_TCP | 40278
EP2ErrorComPMM1Code6 | INT | IOD_EP2_TCP | 40279
EP2ErrorComPMM1Code7 | INT | IOD_EP2_TCP | 40280
EP2ErrorComPMM1Code8 | INT | IOD_EP2_TCP | 40281
EP2ErrorComPMM1Code9 | INT | IOD_EP2_TCP | 40282
EP2ErrorComPMM1Error | DIGITAL | IOD_EP2_TCP | 00300
EP2ErrorComPMM1Status | INT | IOD_EP2_TCP | 40283
EP2ErrorComPMM2Code10 | INT | IOD_EP2_TCP | 40284
EP2ErrorComPMM2Code11 | INT | IOD_EP2_TCP | 40285
EP2ErrorComPMM2Code12 | INT | IOD_EP2_TCP | 40286
EP2ErrorComPMM2Code13 | INT | IOD_EP2_TCP | 40287
EP2ErrorComPMM2Code14 | INT | IOD_EP2_TCP | 40288
EP2ErrorComPMM2Code15 | INT | IOD_EP2_TCP | 40289
EP2ErrorComPMM2Code1 | INT | IOD_EP2_TCP | 40290
EP2ErrorComPMM2Code2 | INT | IOD_EP2_TCP | 40291
EP2ErrorComPMM2Code3 | INT | IOD_EP2_TCP | 40292
EP2ErrorComPMM2Code4 | INT | IOD_EP2_TCP | 40293
EP2ErrorComPMM2Code5 | INT | IOD_EP2_TCP | 40294
EP2ErrorComPMM2Code6 | INT | IOD_EP2_TCP | 40295
EP2ErrorComPMM2Code7 | INT | IOD_EP2_TCP | 40296
EP2ErrorComPMM2Code8 | INT | IOD_EP2_TCP | 40297
EP2ErrorComPMM2Code9 | INT | IOD_EP2_TCP | 40298
EP2ErrorComPMM2Error | DIGITAL | IOD_EP2_TCP | 00301
EP2ErrorComPMM2Status | INT | IOD_EP2_TCP | 40299
EP2ErrorComPMM3Code10 | INT | IOD_EP2_TCP | 40300
EP2ErrorComPMM3Code11 | INT | IOD_EP2_TCP | 40301
EP2ErrorComPMM3Code12 | INT | IOD_EP2_TCP | 40302
EP2ErrorComPMM3Code13 | INT | IOD_EP2_TCP | 40303
EP2ErrorComPMM3Code14 | INT | IOD_EP2_TCP | 40304
EP2ErrorComPMM3Code15 | INT | IOD_EP2_TCP | 40305
EP2ErrorComPMM3Code1 | INT | IOD_EP2_TCP | 40306
EP2ErrorComPMM3Code2 | INT | IOD_EP2_TCP | 40307
EP2ErrorComPMM3Code3 | INT | IOD_EP2_TCP | 40308
EP2ErrorComPMM3Code4 | INT | IOD_EP2_TCP | 40309
EP2ErrorComPMM3Code5 | INT | IOD_EP2_TCP | 40310
EP2ErrorComPMM3Code6 | INT | IOD_EP2_TCP | 40311
EP2ErrorComPMM3Code7 | INT | IOD_EP2_TCP | 40312
EP2ErrorComPMM3Code8 | INT | IOD_EP2_TCP | 40313
EP2ErrorComPMM3Code9 | INT | IOD_EP2_TCP | 40314
EP2ErrorComPMM3Error | DIGITAL | IOD_EP2_TCP | 00302
EP2ErrorComPMM3Status | INT | IOD_EP2_TCP | 40315
EP2ErrorComUPS1Code10 | INT | IOD_EP2_TCP | 40316
EP2ErrorComUPS1Code11 | INT | IOD_EP2_TCP | 40317
EP2ErrorComUPS1Code12 | INT | IOD_EP2_TCP | 40318
EP2ErrorComUPS1Code13 | INT | IOD_EP2_TCP | 40319
EP2ErrorComUPS1Code14 | INT | IOD_EP2_TCP | 40320
EP2ErrorComUPS1Code15 | INT | IOD_EP2_TCP | 40321
EP2ErrorComUPS1Code1 | INT | IOD_EP2_TCP | 40322
EP2ErrorComUPS1Code2 | INT | IOD_EP2_TCP | 40323
EP2ErrorComUPS1Code3 | INT | IOD_EP2_TCP | 40324
EP2ErrorComUPS1Code4 | INT | IOD_EP2_TCP | 40325
EP2ErrorComUPS1Code5 | INT | IOD_EP2_TCP | 40326
EP2ErrorComUPS1Code6 | INT | IOD_EP2_TCP | 40327
EP2ErrorComUPS1Code7 | INT | IOD_EP2_TCP | 40328
EP2ErrorComUPS1Code8 | INT | IOD_EP2_TCP | 40329
EP2ErrorComUPS1Code9 | INT | IOD_EP2_TCP | 40330
EP2ErrorComUPS1Error | DIGITAL | IOD_EP2_TCP | 00303
EP2ErrorComUPS1Status | INT | IOD_EP2_TCP | 40331
EP2ErrorComUPS2Code10 | INT | IOD_EP2_TCP | 40332
EP2ErrorComUPS2Code11 | INT | IOD_EP2_TCP | 40333
EP2ErrorComUPS2Code12 | INT | IOD_EP2_TCP | 40334
EP2ErrorComUPS2Code13 | INT | IOD_EP2_TCP | 40335
EP2ErrorComUPS2Code14 | INT | IOD_EP2_TCP | 40336
EP2ErrorComUPS2Code15 | INT | IOD_EP2_TCP | 40337
EP2ErrorComUPS2Code1 | INT | IOD_EP2_TCP | 40338
EP2ErrorComUPS2Code2 | INT | IOD_EP2_TCP | 40339
EP2ErrorComUPS2Code3 | INT | IOD_EP2_TCP | 40340
EP2ErrorComUPS2Code4 | INT | IOD_EP2_TCP | 40341
EP2ErrorComUPS2Code5 | INT | IOD_EP2_TCP | 40342
EP2ErrorComUPS2Code6 | INT | IOD_EP2_TCP | 40343
EP2ErrorComUPS2Code7 | INT | IOD_EP2_TCP | 40344
EP2ErrorComUPS2Code8 | INT | IOD_EP2_TCP | 40345
EP2ErrorComUPS2Code9 | INT | IOD_EP2_TCP | 40346
EP2ErrorComUPS2Error | DIGITAL | IOD_EP2_TCP | 00304
EP2ErrorComUPS2Status | INT | IOD_EP2_TCP | 40347
EP2Klima1AlarmKompresor1 | DIGITAL | 163 | EP2:.Klima[1].AlarmKompresor1
EP2Klima1AlarmKompresor2 | DIGITAL | 164 | EP2:.Klima[1].AlarmKompresor2
EP2Klima1Deluje | DIGITAL | 165 | EP2:.Klima[1].Deluje
EP2Klima1EnergySaving | DIGITAL | 166 | EP2:.Klima[1].EnergySaving
EP2Klima1FaultyEPROM | DIGITAL | 167 | EP2:.Klima[1].FaultyEPROM
EP2Klima1FenThermalCutout | DIGITAL | 168 | EP2:.Klima[1].FenThermalCutout
EP2Klima1GeneralAlarm | DIGITAL | 169 | EP2:.Klima[1].GeneralAlarm
EP2Klima1GrelecStatus | BYTE | 170 | EP2:.Klima[1].GrelecStatus
EP2Klima1IzhodniVentStatus | BYTE | 171 | EP2:.Klima[1].IzhodniVentStatus
EP2Klima1Kompresor1naMejiObrUr | DIGITAL | 172 | EP2:.Klima[1].Kompresor1naMejiObrUr
EP2Klima1Kompresor2naMejiObrUr | DIGITAL | 173 | EP2:.Klima[1].Kompresor2naMejiObrUr
EP2Klima1KompresorStatus | BYTE | 174 | EP2:.Klima[1].KompresorStatus
EP2Klima1Napaka | DIGITAL | 175 | EP2:.Klima[1].Napaka
EP2Klima1NapakaPriPretokuZraka | DIGITAL | 176 | EP2:.Klima[1].NapakaPriPretokuZraka
EP2Klima1NapakaSenzorPovratVode | DIGITAL | 177 | EP2:.Klima[1].NapakaSenzorPovratVode
EP2Klima1NapakaSenzorTempIzpiha | DIGITAL | 178 | EP2:.Klima[1].NapakaSenzorTempIzpiha
EP2Klima1NapakaSenzorTempProstora | DIGITAL | 179 | EP2:.Klima[1].NapakaSenzorTempProstora
EP2Klima1NapakaSenzorVlaznosti | DIGITAL | 180 | EP2:.Klima[1].NapakaSenzorVlaznosti
EP2Klima1NapakaSenzorZunanjeTemp | DIGITAL | 181 | EP2:.Klima[1].NapakaSenzorZunanjeTemp
EP2Klima1NastMaxTemp | REAL | 182 | EP2:.Klima[1].NastMaxTemp
EP2Klima1NastMaxVlaznost | REAL | 183 | EP2:.Klima[1].NastMaxVlaznost
EP2Klima1NastMinTemp | REAL | 184 | EP2:.Klima[1].NastMinTemp
EP2Klima1NastMinVlaznost | REAL | 185 | EP2:.Klima[1].NastMinVlaznost
EP2Klima1NastTempProstora | REAL | 186 | EP2:.Klima[1].NastTempProstora
EP2Klima1NastVlaznost | REAL | 187 | EP2:.Klima[1].NastVlaznost
EP2Klima1NiTokaVVlazilcu | DIGITAL | 188 | EP2:.Klima[1].NiTokaVVlazilcu
EP2Klima1NiVodeVVlazilcu | DIGITAL | 189 | EP2:.Klima[1].NiVodeVVlazilcu
EP2Klima1NizekPritiskKompresor1 | DIGITAL | 190 | EP2:.Klima[1].NizekPritiskKompresor1
EP2Klima1NizekPritiskKompresor2 | DIGITAL | 191 | EP2:.Klima[1].NizekPritiskKompresor2
EP2Klima1NizkaTempPovratneVode | DIGITAL | 192 | EP2:.Klima[1].NizkaTempPovratneVode
EP2Klima1NizkaTempVProstoru | DIGITAL | 193 | EP2:.Klima[1].NizkaTempVProstoru
EP2Klima1NizkaVlaznost | DIGITAL | 194 | EP2:.Klima[1].NizkaVlaznost
EP2Klima1ObratovalneUre | REAL | 195 | EP2:.Klima[1].ObratovalneUre
EP2Klima1OnOffEnablingBySupervisor | DIGITAL | 196 | EP2:.Klima[1].OnOffEnablingBySupervisor
EP2Klima1PozarniAlarm | DIGITAL | 197 | EP2:.Klima[1].PozarniAlarm
EP2Klima1Razvlazevanje | DIGITAL | 198 | EP2:.Klima[1].Razvlazevanje
EP2Klima1RemoteOFFtoOutput | DIGITAL | 199 | EP2:.Klima[1].RemoteOFFtoOutput
EP2Klima1RemoteOnOff | DIGITAL | 200 | EP2:.Klima[1].RemoteOnOff
EP2Klima1RocniIzklop | DIGITAL | 201 | EP2:.Klima[1].RocniIzklop
EP2Klima1SenzorjiStatus | DIGITAL | 202 | EP2:.Klima[1].SenzorjiStatus
EP2Klima1StoppedByAlarms | DIGITAL | 203 | EP2:.Klima[1].StoppedByAlarms
EP2Klima1TemperaturaProstora | REAL | 204 | EP2:.Klima[1].TemperaturaProstora
EP2Klima1TempIzpihanegaZraka | REAL | 205 | EP2:.Klima[1].TempIzpihanegaZraka
EP2Klima1TempPovratneVode | REAL | 206 | EP2:.Klima[1].TempPovratneVode
EP2Klima1ThermalCutoutHeater1 | DIGITAL | 207 | EP2:.Klima[1].ThermalCutoutHeater1
EP2Klima1ThermalCutoutHeater2 | DIGITAL | 208 | EP2:.Klima[1].ThermalCutoutHeater2
EP2Klima1UnitOnOff | DIGITAL | 209 | EP2:.Klima[1].UnitOnOff
EP2Klima1VentilatorNaMejiObrUr | DIGITAL | 210 | EP2:.Klima[1].VentilatorNaMejiObrUr
EP2Klima1VentilGretjeOdpiranje | DIGITAL | 211 | EP2:.Klima[1].VentilGretjeOdpiranje
EP2Klima1VentilGretjeZapiranje | DIGITAL | 212 | EP2:.Klima[1].VentilGretjeZapiranje
EP2Klima1VentilHlajenjeOdpiranje | DIGITAL | 213 | EP2:.Klima[1].VentilHlajenjeOdpiranje
EP2Klima1VentilHlajenjeZapiranje | DIGITAL | 214 | EP2:.Klima[1].VentilHlajenjeZapiranje
EP2Klima1VisokaTempPovratneVode | DIGITAL | 215 | EP2:.Klima[1].VisokaTempPovratneVode
EP2Klima1VisokaTempVProstoru | DIGITAL | 216 | EP2:.Klima[1].VisokaTempVProstoru
EP2Klima1VisokaVlaznost | DIGITAL | 217 | EP2:.Klima[1].VisokaVlaznost
EP2Klima1VisokTokVVlazilcu | DIGITAL | 218 | EP2:.Klima[1].VisokTokVVlazilcu
EP2Klima1Vlazenje | DIGITAL | 219 | EP2:.Klima[1].Vlazenje
EP2Klima1VlazilecStatus | BYTE | 220 | EP2:.Klima[1].VlazilecStatus
EP2Klima1VlaznostProstora | REAL | 221 | EP2:.Klima[1].VlaznostProstora
EP2Klima1ZamasenFilter | DIGITAL | 222 | EP2:.Klima[1].ZamasenFilter
EP2Klima1ZunanjaTemp | REAL | 223 | EP2:.Klima[1].ZunanjaTemp
EP2Klima2AlarmKompresor1 | DIGITAL | 224 | EP2:.Klima[2].AlarmKompresor1
EP2Klima2AlarmKompresor2 | DIGITAL | 225 | EP2:.Klima[2].AlarmKompresor2
EP2Klima2Deluje | DIGITAL | 226 | EP2:.Klima[2].Deluje
EP2Klima2EnergySaving | DIGITAL | 227 | EP2:.Klima[2].EnergySaving
EP2Klima2FaultyEPROM | DIGITAL | 228 | EP2:.Klima[2].FaultyEPROM
EP2Klima2FenThermalCutout | DIGITAL | 229 | EP2:.Klima[2].FenThermalCutout
EP2Klima2GeneralAlarm | DIGITAL | 230 | EP2:.Klima[2].GeneralAlarm
EP2Klima2GrelecStatus | BYTE | 231 | EP2:.Klima[2].GrelecStatus
EP2Klima2IzhodniVentStatus | BYTE | 232 | EP2:.Klima[2].IzhodniVentStatus
EP2Klima2Kompresor1naMejiObrUr | DIGITAL | 233 | EP2:.Klima[2].Kompresor1naMejiObrUr
EP2Klima2Kompresor2naMejiObrUr | DIGITAL | 234 | EP2:.Klima[2].Kompresor2naMejiObrUr
EP2Klima2KompresorStatus | BYTE | 235 | EP2:.Klima[2].KompresorStatus
EP2Klima2Napaka | DIGITAL | 236 | EP2:.Klima[2].Napaka
EP2Klima2NapakaPriPretokuZraka | DIGITAL | 237 | EP2:.Klima[2].NapakaPriPretokuZraka
EP2Klima2NapakaSenzorPovratVode | DIGITAL | 238 | EP2:.Klima[2].NapakaSenzorPovratVode
EP2Klima2NapakaSenzorTempIzpiha | DIGITAL | 239 | EP2:.Klima[2].NapakaSenzorTempIzpiha
EP2Klima2NapakaSenzorTempProstora | DIGITAL | 240 | EP2:.Klima[2].NapakaSenzorTempProstora
EP2Klima2NapakaSenzorVlaznosti | DIGITAL | 241 | EP2:.Klima[2].NapakaSenzorVlaznosti
EP2Klima2NapakaSenzorZunanjeTemp | DIGITAL | 242 | EP2:.Klima[2].NapakaSenzorZunanjeTemp
EP2Klima2NastMaxTemp | REAL | 243 | EP2:.Klima[2].NastMaxTemp
EP2Klima2NastMaxVlaznost | REAL | 244 | EP2:.Klima[2].NastMaxVlaznost
EP2Klima2NastMinTemp | REAL | 245 | EP2:.Klima[2].NastMinTemp
EP2Klima2NastMinVlaznost | REAL | 246 | EP2:.Klima[2].NastMinVlaznost
EP2Klima2NastTempProstora | REAL | 247 | EP2:.Klima[2].NastTempProstora
EP2Klima2NastVlaznost | REAL | 248 | EP2:.Klima[2].NastVlaznost
EP2Klima2NiTokaVVlazilcu | DIGITAL | 249 | EP2:.Klima[2].NiTokaVVlazilcu
EP2Klima2NiVodeVVlazilcu | DIGITAL | 250 | EP2:.Klima[2].NiVodeVVlazilcu
EP2Klima2NizekPritiskKompresor1 | DIGITAL | 251 | EP2:.Klima[2].NizekPritiskKompresor1
EP2Klima2NizekPritiskKompresor2 | DIGITAL | 252 | EP2:.Klima[2].NizekPritiskKompresor2
EP2Klima2NizkaTempPovratneVode | DIGITAL | 253 | EP2:.Klima[2].NizkaTempPovratneVode
EP2Klima2NizkaTempVProstoru | DIGITAL | 254 | EP2:.Klima[2].NizkaTempVProstoru
EP2Klima2NizkaVlaznost | DIGITAL | 255 | EP2:.Klima[2].NizkaVlaznost
EP2Klima2ObratovalneUre | REAL | 256 | EP2:.Klima[2].ObratovalneUre
EP2Klima2OnOffEnablingBySupervisor | DIGITAL | 257 | EP2:.Klima[2].OnOffEnablingBySupervisor
EP2Klima2PozarniAlarm | DIGITAL | 258 | EP2:.Klima[2].PozarniAlarm
EP2Klima2Razvlazevanje | DIGITAL | 259 | EP2:.Klima[2].Razvlazevanje
EP2Klima2RemoteOFFtoOutput | DIGITAL | 260 | EP2:.Klima[2].RemoteOFFtoOutput
EP2Klima2RemoteOnOff | DIGITAL | 261 | EP2:.Klima[2].RemoteOnOff
EP2Klima2RocniIzklop | DIGITAL | 262 | EP2:.Klima[2].RocniIzklop
EP2Klima2SenzorjiStatus | DIGITAL | 263 | EP2:.Klima[2].SenzorjiStatus
EP2Klima2StoppedByAlarms | DIGITAL | 264 | EP2:.Klima[2].StoppedByAlarms
EP2Klima2TemperaturaProstora | REAL | 265 | EP2:.Klima[2].TemperaturaProstora
EP2Klima2TempIzpihanegaZraka | REAL | 266 | EP2:.Klima[2].TempIzpihanegaZraka
EP2Klima2TempPovratneVode | REAL | 267 | EP2:.Klima[2].TempPovratneVode
EP2Klima2ThermalCutoutHeater1 | DIGITAL | 268 | EP2:.Klima[2].ThermalCutoutHeater1
EP2Klima2ThermalCutoutHeater2 | DIGITAL | 269 | EP2:.Klima[2].ThermalCutoutHeater2
EP2Klima2UnitOnOff | DIGITAL | 270 | EP2:.Klima[2].UnitOnOff
EP2Klima2VentilatorNaMejiObrUr | DIGITAL | 271 | EP2:.Klima[2].VentilatorNaMejiObrUr
EP2Klima2VentilGretjeOdpiranje | DIGITAL | 272 | EP2:.Klima[2].VentilGretjeOdpiranje
EP2Klima2VentilGretjeZapiranje | DIGITAL | 273 | EP2:.Klima[2].VentilGretjeZapiranje
EP2Klima2VentilHlajenjeOdpiranje | DIGITAL | 274 | EP2:.Klima[2].VentilHlajenjeOdpiranje
EP2Klima2VentilHlajenjeZapiranje | DIGITAL | 275 | EP2:.Klima[2].VentilHlajenjeZapiranje
EP2Klima2VisokaTempPovratneVode | DIGITAL | 276 | EP2:.Klima[2].VisokaTempPovratneVode
EP2Klima2VisokaTempVProstoru | DIGITAL | 277 | EP2:.Klima[2].VisokaTempVProstoru
EP2Klima2VisokaVlaznost | DIGITAL | 278 | EP2:.Klima[2].VisokaVlaznost
EP2Klima2VisokTokVVlazilcu | DIGITAL | 279 | EP2:.Klima[2].VisokTokVVlazilcu
EP2Klima2Vlazenje | DIGITAL | 280 | EP2:.Klima[2].Vlazenje
EP2Klima2VlazilecStatus | BYTE | 281 | EP2:.Klima[2].VlazilecStatus
EP2Klima2VlaznostProstora | REAL | 282 | EP2:.Klima[2].VlaznostProstora
EP2Klima2ZamasenFilter | DIGITAL | 283 | EP2:.Klima[2].ZamasenFilter
EP2Klima2ZunanjaTemp | REAL | 284 | EP2:.Klima[2].ZunanjaTemp
EP2KlimaAErrors10 | DIGITAL | IOD_EP2_TCP | 00305
EP2KlimaAErrors11 | DIGITAL | IOD_EP2_TCP | 00306
EP2KlimaAErrors12 | DIGITAL | IOD_EP2_TCP | 00307
EP2KlimaAErrors13 | DIGITAL | IOD_EP2_TCP | 00308
EP2KlimaAErrors14 | DIGITAL | IOD_EP2_TCP | 00309
EP2KlimaAErrors15 | DIGITAL | IOD_EP2_TCP | 00310
EP2KlimaAErrors16 | DIGITAL | IOD_EP2_TCP | 00311
EP2KlimaAErrors17 | DIGITAL | IOD_EP2_TCP | 00312
EP2KlimaAErrors18 | DIGITAL | IOD_EP2_TCP | 00313
EP2KlimaAErrors19 | DIGITAL | IOD_EP2_TCP | 00314
EP2KlimaAErrors1 | DIGITAL | IOD_EP2_TCP | 00315
EP2KlimaAErrors20 | DIGITAL | IOD_EP2_TCP | 00316
EP2KlimaAErrors21 | DIGITAL | IOD_EP2_TCP | 00317
EP2KlimaAErrors22 | DIGITAL | IOD_EP2_TCP | 00318
EP2KlimaAErrors23 | DIGITAL | IOD_EP2_TCP | 00319
EP2KlimaAErrors24 | DIGITAL | IOD_EP2_TCP | 00320
EP2KlimaAErrors25 | DIGITAL | IOD_EP2_TCP | 00321
EP2KlimaAErrors26 | DIGITAL | IOD_EP2_TCP | 00322
EP2KlimaAErrors27 | DIGITAL | IOD_EP2_TCP | 00323
EP2KlimaAErrors28 | DIGITAL | IOD_EP2_TCP | 00324
EP2KlimaAErrors29 | DIGITAL | IOD_EP2_TCP | 00325
EP2KlimaAErrors2 | DIGITAL | IOD_EP2_TCP | 00326
EP2KlimaAErrors30 | DIGITAL | IOD_EP2_TCP | 00327
EP2KlimaAErrors31 | DIGITAL | IOD_EP2_TCP | 00328
EP2KlimaAErrors32 | DIGITAL | IOD_EP2_TCP | 00329
EP2KlimaAErrors33 | DIGITAL | IOD_EP2_TCP | 00330
EP2KlimaAErrors34 | DIGITAL | IOD_EP2_TCP | 00331
EP2KlimaAErrors35 | DIGITAL | IOD_EP2_TCP | 00332
EP2KlimaAErrors36 | DIGITAL | IOD_EP2_TCP | 00333
EP2KlimaAErrors37 | DIGITAL | IOD_EP2_TCP | 00334
EP2KlimaAErrors38 | DIGITAL | IOD_EP2_TCP | 00335
EP2KlimaAErrors39 | DIGITAL | IOD_EP2_TCP | 00336
EP2KlimaAErrors3 | DIGITAL | IOD_EP2_TCP | 00337
EP2KlimaAErrors40 | DIGITAL | IOD_EP2_TCP | 00338
EP2KlimaAErrors4 | DIGITAL | IOD_EP2_TCP | 00339
EP2KlimaAErrors5 | DIGITAL | IOD_EP2_TCP | 00340
EP2KlimaAErrors6 | DIGITAL | IOD_EP2_TCP | 00341
EP2KlimaAErrors7 | DIGITAL | IOD_EP2_TCP | 00342
EP2KlimaAErrors8 | DIGITAL | IOD_EP2_TCP | 00343
EP2KlimaAErrors9 | DIGITAL | IOD_EP2_TCP | 00344
EP2KlimaBErrors10 | DIGITAL | IOD_EP2_TCP | 00345
EP2KlimaBErrors11 | DIGITAL | IOD_EP2_TCP | 00346
EP2KlimaBErrors12 | DIGITAL | IOD_EP2_TCP | 00347
EP2KlimaBErrors13 | DIGITAL | IOD_EP2_TCP | 00348
EP2KlimaBErrors14 | DIGITAL | IOD_EP2_TCP | 00349
EP2KlimaBErrors15 | DIGITAL | IOD_EP2_TCP | 00350
EP2KlimaBErrors16 | DIGITAL | IOD_EP2_TCP | 00351
EP2KlimaBErrors17 | DIGITAL | IOD_EP2_TCP | 00352
EP2KlimaBErrors18 | DIGITAL | IOD_EP2_TCP | 00353
EP2KlimaBErrors19 | DIGITAL | IOD_EP2_TCP | 00354
EP2KlimaBErrors1 | DIGITAL | IOD_EP2_TCP | 00355
EP2KlimaBErrors20 | DIGITAL | IOD_EP2_TCP | 00356
EP2KlimaBErrors21 | DIGITAL | IOD_EP2_TCP | 00357
EP2KlimaBErrors22 | DIGITAL | IOD_EP2_TCP | 00358
EP2KlimaBErrors23 | DIGITAL | IOD_EP2_TCP | 00359
EP2KlimaBErrors24 | DIGITAL | IOD_EP2_TCP | 00360
EP2KlimaBErrors25 | DIGITAL | IOD_EP2_TCP | 00361
EP2KlimaBErrors26 | DIGITAL | IOD_EP2_TCP | 00362
EP2KlimaBErrors27 | DIGITAL | IOD_EP2_TCP | 00363
EP2KlimaBErrors28 | DIGITAL | IOD_EP2_TCP | 00364
EP2KlimaBErrors29 | DIGITAL | IOD_EP2_TCP | 00365
EP2KlimaBErrors2 | DIGITAL | IOD_EP2_TCP | 00366
EP2KlimaBErrors30 | DIGITAL | IOD_EP2_TCP | 00367
EP2KlimaBErrors31 | DIGITAL | IOD_EP2_TCP | 00368
EP2KlimaBErrors32 | DIGITAL | IOD_EP2_TCP | 00369
EP2KlimaBErrors33 | DIGITAL | IOD_EP2_TCP | 00370
EP2KlimaBErrors34 | DIGITAL | IOD_EP2_TCP | 00371
EP2KlimaBErrors35 | DIGITAL | IOD_EP2_TCP | 00372
EP2KlimaBErrors36 | DIGITAL | IOD_EP2_TCP | 00373
EP2KlimaBErrors37 | DIGITAL | IOD_EP2_TCP | 00374
EP2KlimaBErrors38 | DIGITAL | IOD_EP2_TCP | 00375
EP2KlimaBErrors39 | DIGITAL | IOD_EP2_TCP | 00376
EP2KlimaBErrors3 | DIGITAL | IOD_EP2_TCP | 00377
EP2KlimaBErrors40 | DIGITAL | IOD_EP2_TCP | 00378
EP2KlimaBErrors4 | DIGITAL | IOD_EP2_TCP | 00379
EP2KlimaBErrors5 | DIGITAL | IOD_EP2_TCP | 00380
EP2KlimaBErrors6 | DIGITAL | IOD_EP2_TCP | 00381
EP2KlimaBErrors7 | DIGITAL | IOD_EP2_TCP | 00382
EP2KlimaBErrors8 | DIGITAL | IOD_EP2_TCP | 00383
EP2KlimaBErrors9 | DIGITAL | IOD_EP2_TCP | 00384
EP2KlimaGalAlarmKompresor1 | DIGITAL | IOD_EP2_TCP | 00385
EP2KlimaGalAlarmKompresor2 | DIGITAL | IOD_EP2_TCP | 00386
EP2KlimaGalDeluje | DIGITAL | IOD_EP2_TCP | 00387
EP2KlimaGalEnergySaving | DIGITAL | IOD_EP2_TCP | 00388
EP2KlimaGalFaultyEPROM | DIGITAL | IOD_EP2_TCP | 00389
EP2KlimaGalFenThermalCutout | DIGITAL | IOD_EP2_TCP | 00390
EP2KlimaGalGeneralAlarm | DIGITAL | IOD_EP2_TCP | 00391
EP2KlimaGalGrelecStatus | INT | IOD_EP2_TCP | 40348
EP2KlimaGalIzhodniVentStatus | INT | IOD_EP2_TCP | 40349
EP2KlimaGalKompresor1naMejiObrUr | DIGITAL | IOD_EP2_TCP | 00392
EP2KlimaGalKompresor2naMejiObrUr | DIGITAL | IOD_EP2_TCP | 00393
EP2KlimaGalKompresorStatus | INT | IOD_EP2_TCP | 40350
EP2KlimaGalNapaka | DIGITAL | IOD_EP2_TCP | 00394
EP2KlimaGalNapakaPriPretokuZraka | DIGITAL | IOD_EP2_TCP | 00395
EP2KlimaGalNapakaSenzorPovratVode | DIGITAL | IOD_EP2_TCP | 00396
EP2KlimaGalNapakaSenzorTempIzpiha | DIGITAL | IOD_EP2_TCP | 00397
EP2KlimaGalNapakaSenzorTempProstora | DIGITAL | IOD_EP2_TCP | 00398
EP2KlimaGalNapakaSenzorVlaznosti | DIGITAL | IOD_EP2_TCP | 00399
EP2KlimaGalNapakaSenzorZunanjeTemp | DIGITAL | IOD_EP2_TCP | 00400
EP2KlimaGalNastMaxTemp | REAL | IOD_EP2_TCP | 45169
EP2KlimaGalNastMaxVlaznost | REAL | IOD_EP2_TCP | 45171
EP2KlimaGalNastMinTemp | REAL | IOD_EP2_TCP | 45173
EP2KlimaGalNastMinVlaznost | REAL | IOD_EP2_TCP | 45175
EP2KlimaGalNastTempProstora | REAL | IOD_EP2_TCP | 45177
EP2KlimaGalNastVlaznost | REAL | IOD_EP2_TCP | 45179
EP2KlimaGalNiTokaVVlazilcu | DIGITAL | IOD_EP2_TCP | 00401
EP2KlimaGalNiVodeVVlazilcu | DIGITAL | IOD_EP2_TCP | 00402
EP2KlimaGalNizekPritiskKompresor1 | DIGITAL | IOD_EP2_TCP | 00403
EP2KlimaGalNizekPritiskKompresor2 | DIGITAL | IOD_EP2_TCP | 00404
EP2KlimaGalNizkaTempPovratneVode | DIGITAL | IOD_EP2_TCP | 00405
EP2KlimaGalNizkaTempVProstoru | DIGITAL | IOD_EP2_TCP | 00406
EP2KlimaGalNizkaVlaznost | DIGITAL | IOD_EP2_TCP | 00407
EP2KlimaGalObratovalneUre | REAL | IOD_EP2_TCP | 45181
EP2KlimaGalOnOffEnablingBySupervisor | DIGITAL | IOD_EP2_TCP | 00408
EP2KlimaGalPozarniAlarm | DIGITAL | IOD_EP2_TCP | 00409
EP2KlimaGalRazvlazevanje | DIGITAL | IOD_EP2_TCP | 00410
EP2KlimaGalRemoteOFFtoOutput | DIGITAL | IOD_EP2_TCP | 00411
EP2KlimaGalRemoteOnOff | DIGITAL | IOD_EP2_TCP | 00412
EP2KlimaGalRocniIzklop | DIGITAL | IOD_EP2_TCP | 00413
EP2KlimaGalSenzorjiStatus | DIGITAL | IOD_EP2_TCP | 00414
EP2KlimaGalStoppedByAlarms | DIGITAL | IOD_EP2_TCP | 00415
EP2KlimaGalTemperaturaProstora | REAL | IOD_EP2_TCP | 45183
EP2KlimaGalTempIzpihanegaZraka | REAL | IOD_EP2_TCP | 45185
EP2KlimaGalTempPovratneVode | REAL | IOD_EP2_TCP | 45187
EP2KlimaGalThermalCutoutHeater1 | DIGITAL | IOD_EP2_TCP | 00416
EP2KlimaGalThermalCutoutHeater2 | DIGITAL | IOD_EP2_TCP | 00417
EP2KlimaGalUnitOnOff | DIGITAL | IOD_EP2_TCP | 00418
EP2KlimaGalVentilatorNaMejiObrUr | DIGITAL | IOD_EP2_TCP | 00419
EP2KlimaGalVentilGretjeOdpiranje | DIGITAL | IOD_EP2_TCP | 00420
EP2KlimaGalVentilGretjeZapiranje | DIGITAL | IOD_EP2_TCP | 00421
EP2KlimaGalVentilHlajenjeOdpiranje | DIGITAL | IOD_EP2_TCP | 00422
EP2KlimaGalVentilHlajenjeZapiranje | DIGITAL | IOD_EP2_TCP | 00423
EP2KlimaGalVisokaTempPovratneVode | DIGITAL | IOD_EP2_TCP | 00424
EP2KlimaGalVisokaTempVProstoru | DIGITAL | IOD_EP2_TCP | 00425
EP2KlimaGalVisokaVlaznost | DIGITAL | IOD_EP2_TCP | 00426
EP2KlimaGalVisokTokVVlazilcu | DIGITAL | IOD_EP2_TCP | 00427
EP2KlimaGalVlazenje | DIGITAL | IOD_EP2_TCP | 00428
EP2KlimaGalVlazilecStatus | INT | IOD_EP2_TCP | 40351
EP2KlimaGalVlaznostProstora | REAL | IOD_EP2_TCP | 45189
EP2KlimaGalZamasenFilter | DIGITAL | IOD_EP2_TCP | 00429
EP2KlimaGalZunanjaTemp | REAL | IOD_EP2_TCP | 45191
EP2KlimeNaCas | DIGITAL | 285 | EP2:.KlimeNaCas
EP2NapakaSenzorTemp1 | DIGITAL | 286 | EP2:.NapakaSenzorTemp[1]
EP2NapakaSenzorTemp2 | DIGITAL | 287 | EP2:.NapakaSenzorTemp[2]
EP2NapakaSenzorVlaga1 | DIGITAL | 288 | EP2:.NapakaSenzorVlaga[1]
EP2NapakaSenzorVlaga2 | DIGITAL | 289 | EP2:.NapakaSenzorVlaga[2]
EP2PMM1OverCurrentBetw1 | DIGITAL | 290 | EP2:.PMM1OverCurrentBetw[1]
EP2PMM1OverCurrentBetw2 | DIGITAL | 291 | EP2:.PMM1OverCurrentBetw[2]
EP2PMM1OverCurrentBetw3 | DIGITAL | 292 | EP2:.PMM1OverCurrentBetw[3]
EP2PMM1OverCurrentOver1 | DIGITAL | 293 | EP2:.PMM1OverCurrentOver[1]
EP2PMM1OverCurrentOver2 | DIGITAL | 294 | EP2:.PMM1OverCurrentOver[2]
EP2PMM1OverCurrentOver3 | DIGITAL | 295 | EP2:.PMM1OverCurrentOver[3]
EP2PMM1OverVoltage | DIGITAL | IOD_EP2_TCP | 00430
EP2PMM2OverCurrentBetw1 | DIGITAL | 296 | EP2:.PMM2OverCurrentBetw[1]
EP2PMM2OverCurrentBetw2 | DIGITAL | 297 | EP2:.PMM2OverCurrentBetw[2]
EP2PMM2OverCurrentBetw3 | DIGITAL | 298 | EP2:.PMM2OverCurrentBetw[3]
EP2PMM2OverCurrentOver1 | DIGITAL | 299 | EP2:.PMM2OverCurrentOver[1]
EP2PMM2OverCurrentOver2 | DIGITAL | 300 | EP2:.PMM2OverCurrentOver[2]
EP2PMM2OverCurrentOver3 | DIGITAL | 301 | EP2:.PMM2OverCurrentOver[3]
EP2PMM2OverVoltage | DIGITAL | IOD_EP2_TCP | 00431
EP2PMM3OverCurrentBetw1 | DIGITAL | 302 | EP2:.PMM3OverCurrentBetw[1]
EP2PMM3OverCurrentBetw2 | DIGITAL | 303 | EP2:.PMM3OverCurrentBetw[2]
EP2PMM3OverCurrentBetw3 | DIGITAL | 304 | EP2:.PMM3OverCurrentBetw[3]
EP2PMM3OverCurrentOver1 | DIGITAL | 305 | EP2:.PMM3OverCurrentOver[1]
EP2PMM3OverCurrentOver2 | DIGITAL | 306 | EP2:.PMM3OverCurrentOver[2]
EP2PMM3OverCurrentOver3 | DIGITAL | 307 | EP2:.PMM3OverCurrentOver[3]
EP2PMM3OverVoltage | DIGITAL | IOD_EP2_TCP | 00432
EP2PMM1ActivePowerPhaseA_kW | REAL | 308 | EP2:.PMM[1].ActivePowerPhaseA_kW
EP2PMM1ActivePowerPhaseB_kW | REAL | 309 | EP2:.PMM[1].ActivePowerPhaseB_kW
EP2PMM1ActivePowerPhaseC_kW | REAL | 310 | EP2:.PMM[1].ActivePowerPhaseC_kW
EP2PMM1AlarmPhase1C01_16_60to80 | UINT | 311 | EP2:.PMM[1].AlarmPhase[1].C01_16_60to80
EP2PMM1AlarmPhase1C01_16_over80 | UINT | 312 | EP2:.PMM[1].AlarmPhase[1].C01_16_over80
EP2PMM1AlarmPhase1C17_32_60to80 | UINT | 313 | EP2:.PMM[1].AlarmPhase[1].C17_32_60to80
EP2PMM1AlarmPhase1C17_32_over80 | UINT | 314 | EP2:.PMM[1].AlarmPhase[1].C17_32_over80
EP2PMM1AlarmPhase1C33_42_60to80 | UINT | 315 | EP2:.PMM[1].AlarmPhase[1].C33_42_60to80
EP2PMM1AlarmPhase1C33_42_over80 | UINT | 316 | EP2:.PMM[1].AlarmPhase[1].C33_42_over80
EP2PMM1AlarmPhase1GlobalAlarmReg | INT | 317 | EP2:.PMM[1].AlarmPhase[1].GlobalAlarmReg
EP2PMM1AlarmPhase2C01_16_60to80 | UINT | 318 | EP2:.PMM[1].AlarmPhase[2].C01_16_60to80
EP2PMM1AlarmPhase2C01_16_over80 | UINT | 319 | EP2:.PMM[1].AlarmPhase[2].C01_16_over80
EP2PMM1AlarmPhase2C17_32_60to80 | UINT | 320 | EP2:.PMM[1].AlarmPhase[2].C17_32_60to80
EP2PMM1AlarmPhase2C17_32_over80 | UINT | 321 | EP2:.PMM[1].AlarmPhase[2].C17_32_over80
EP2PMM1AlarmPhase2C33_42_60to80 | UINT | 322 | EP2:.PMM[1].AlarmPhase[2].C33_42_60to80
EP2PMM1AlarmPhase2C33_42_over80 | UINT | 323 | EP2:.PMM[1].AlarmPhase[2].C33_42_over80
EP2PMM1AlarmPhase2GlobalAlarmReg | INT | 324 | EP2:.PMM[1].AlarmPhase[2].GlobalAlarmReg
EP2PMM1AlarmPhase3C01_16_60to80 | UINT | 325 | EP2:.PMM[1].AlarmPhase[3].C01_16_60to80
EP2PMM1AlarmPhase3C01_16_over80 | UINT | 326 | EP2:.PMM[1].AlarmPhase[3].C01_16_over80
EP2PMM1AlarmPhase3C17_32_60to80 | UINT | 327 | EP2:.PMM[1].AlarmPhase[3].C17_32_60to80
EP2PMM1AlarmPhase3C17_32_over80 | UINT | 328 | EP2:.PMM[1].AlarmPhase[3].C17_32_over80
EP2PMM1AlarmPhase3C33_42_60to80 | UINT | 329 | EP2:.PMM[1].AlarmPhase[3].C33_42_60to80
EP2PMM1AlarmPhase3C33_42_over80 | UINT | 330 | EP2:.PMM[1].AlarmPhase[3].C33_42_over80
EP2PMM1AlarmPhase3GlobalAlarmReg | INT | 331 | EP2:.PMM[1].AlarmPhase[3].GlobalAlarmReg
EP2PMM1Alarms | UINT | 332 | EP2:.PMM[1].Alarms
EP2PMM1AverageCurrent_A | REAL | 333 | EP2:.PMM[1].AverageCurrent_A
EP2PMM1AveragePhaseToNeutral_V | REAL | 334 | EP2:.PMM[1].AveragePhaseToNeutral_V
EP2PMM1AveragePhaseToPhase_V | REAL | 335 | EP2:.PMM[1].AveragePhaseToPhase_V
EP2PMM1CurrentInPhaseA_A | REAL | 336 | EP2:.PMM[1].CurrentInPhaseA_A
EP2PMM1CurrentInPhaseB_A | REAL | 337 | EP2:.PMM[1].CurrentInPhaseB_A
EP2PMM1CurrentInPhaseC_A | REAL | 338 | EP2:.PMM[1].CurrentInPhaseC_A
EP2PMM1EnergyConsumed_kWh | REAL | 339 | EP2:.PMM[1].EnergyConsumed_kWh
EP2PMM1Frequency_Hz | REAL | 341 | EP2:.PMM[1].Frequency_Hz
EP2PMM1Napaka | DIGITAL | 340 | EP2:.PMM[1].Napaka
EP2PMM1NeutralCurrent_A | REAL | 342 | EP2:.PMM[1].NeutralCurrent_A
EP2PMM1Phase1Current10 | REAL | 343 | EP2:.PMM[1].Phase[1].Current[10]
EP2PMM1Phase1Current11 | REAL | 344 | EP2:.PMM[1].Phase[1].Current[11]
EP2PMM1Phase1Current12 | REAL | 345 | EP2:.PMM[1].Phase[1].Current[12]
EP2PMM1Phase1Current13 | REAL | 346 | EP2:.PMM[1].Phase[1].Current[13]
EP2PMM1Phase1Current14 | REAL | 347 | EP2:.PMM[1].Phase[1].Current[14]
EP2PMM1Phase1Current15 | REAL | 348 | EP2:.PMM[1].Phase[1].Current[15]
EP2PMM1Phase1Current16 | REAL | 349 | EP2:.PMM[1].Phase[1].Current[16]
EP2PMM1Phase1Current17 | REAL | 350 | EP2:.PMM[1].Phase[1].Current[17]
EP2PMM1Phase1Current18 | REAL | 351 | EP2:.PMM[1].Phase[1].Current[18]
EP2PMM1Phase1Current19 | REAL | 352 | EP2:.PMM[1].Phase[1].Current[19]
EP2PMM1Phase1Current1 | REAL | 353 | EP2:.PMM[1].Phase[1].Current[1]
EP2PMM1Phase1Current20 | REAL | 354 | EP2:.PMM[1].Phase[1].Current[20]
EP2PMM1Phase1Current21 | REAL | 355 | EP2:.PMM[1].Phase[1].Current[21]
EP2PMM1Phase1Current22 | REAL | 356 | EP2:.PMM[1].Phase[1].Current[22]
EP2PMM1Phase1Current23 | REAL | 357 | EP2:.PMM[1].Phase[1].Current[23]
EP2PMM1Phase1Current24 | REAL | 358 | EP2:.PMM[1].Phase[1].Current[24]
EP2PMM1Phase1Current25 | REAL | 359 | EP2:.PMM[1].Phase[1].Current[25]
EP2PMM1Phase1Current26 | REAL | 360 | EP2:.PMM[1].Phase[1].Current[26]
EP2PMM1Phase1Current27 | REAL | 361 | EP2:.PMM[1].Phase[1].Current[27]
EP2PMM1Phase1Current28 | REAL | 362 | EP2:.PMM[1].Phase[1].Current[28]
EP2PMM1Phase1Current29 | REAL | 363 | EP2:.PMM[1].Phase[1].Current[29]
EP2PMM1Phase1Current2 | REAL | 364 | EP2:.PMM[1].Phase[1].Current[2]
EP2PMM1Phase1Current30 | REAL | 365 | EP2:.PMM[1].Phase[1].Current[30]
EP2PMM1Phase1Current31 | REAL | 366 | EP2:.PMM[1].Phase[1].Current[31]
EP2PMM1Phase1Current32 | REAL | 367 | EP2:.PMM[1].Phase[1].Current[32]
EP2PMM1Phase1Current33 | REAL | 368 | EP2:.PMM[1].Phase[1].Current[33]
EP2PMM1Phase1Current34 | REAL | 369 | EP2:.PMM[1].Phase[1].Current[34]
EP2PMM1Phase1Current35 | REAL | 370 | EP2:.PMM[1].Phase[1].Current[35]
EP2PMM1Phase1Current36 | REAL | 371 | EP2:.PMM[1].Phase[1].Current[36]
EP2PMM1Phase1Current37 | REAL | 372 | EP2:.PMM[1].Phase[1].Current[37]
EP2PMM1Phase1Current38 | REAL | 373 | EP2:.PMM[1].Phase[1].Current[38]
EP2PMM1Phase1Current39 | REAL | 374 | EP2:.PMM[1].Phase[1].Current[39]
EP2PMM1Phase1Current3 | REAL | 375 | EP2:.PMM[1].Phase[1].Current[3]
EP2PMM1Phase1Current40 | REAL | 376 | EP2:.PMM[1].Phase[1].Current[40]
EP2PMM1Phase1Current41 | REAL | 377 | EP2:.PMM[1].Phase[1].Current[41]
EP2PMM1Phase1Current42 | REAL | 378 | EP2:.PMM[1].Phase[1].Current[42]
EP2PMM1Phase1Current4 | REAL | 379 | EP2:.PMM[1].Phase[1].Current[4]
EP2PMM1Phase1Current5 | REAL | 380 | EP2:.PMM[1].Phase[1].Current[5]
EP2PMM1Phase1Current6 | REAL | 381 | EP2:.PMM[1].Phase[1].Current[6]
EP2PMM1Phase1Current7 | REAL | 382 | EP2:.PMM[1].Phase[1].Current[7]
EP2PMM1Phase1Current8 | REAL | 383 | EP2:.PMM[1].Phase[1].Current[8]
EP2PMM1Phase1Current9 | REAL | 384 | EP2:.PMM[1].Phase[1].Current[9]
EP2PMM1Phase2Current10 | REAL | 385 | EP2:.PMM[1].Phase[2].Current[10]
EP2PMM1Phase2Current11 | REAL | 386 | EP2:.PMM[1].Phase[2].Current[11]
EP2PMM1Phase2Current12 | REAL | 387 | EP2:.PMM[1].Phase[2].Current[12]
EP2PMM1Phase2Current13 | REAL | 388 | EP2:.PMM[1].Phase[2].Current[13]
EP2PMM1Phase2Current14 | REAL | 389 | EP2:.PMM[1].Phase[2].Current[14]
EP2PMM1Phase2Current15 | REAL | 390 | EP2:.PMM[1].Phase[2].Current[15]
EP2PMM1Phase2Current16 | REAL | 391 | EP2:.PMM[1].Phase[2].Current[16]
EP2PMM1Phase2Current17 | REAL | 392 | EP2:.PMM[1].Phase[2].Current[17]
EP2PMM1Phase2Current18 | REAL | 393 | EP2:.PMM[1].Phase[2].Current[18]
EP2PMM1Phase2Current19 | REAL | 394 | EP2:.PMM[1].Phase[2].Current[19]
EP2PMM1Phase2Current1 | REAL | 395 | EP2:.PMM[1].Phase[2].Current[1]
EP2PMM1Phase2Current20 | REAL | 396 | EP2:.PMM[1].Phase[2].Current[20]
EP2PMM1Phase2Current21 | REAL | 397 | EP2:.PMM[1].Phase[2].Current[21]
EP2PMM1Phase2Current22 | REAL | 398 | EP2:.PMM[1].Phase[2].Current[22]
EP2PMM1Phase2Current23 | REAL | 399 | EP2:.PMM[1].Phase[2].Current[23]
EP2PMM1Phase2Current24 | REAL | 400 | EP2:.PMM[1].Phase[2].Current[24]
EP2PMM1Phase2Current25 | REAL | 401 | EP2:.PMM[1].Phase[2].Current[25]
EP2PMM1Phase2Current26 | REAL | 402 | EP2:.PMM[1].Phase[2].Current[26]
EP2PMM1Phase2Current27 | REAL | 403 | EP2:.PMM[1].Phase[2].Current[27]
EP2PMM1Phase2Current28 | REAL | 404 | EP2:.PMM[1].Phase[2].Current[28]
EP2PMM1Phase2Current29 | REAL | 405 | EP2:.PMM[1].Phase[2].Current[29]
EP2PMM1Phase2Current2 | REAL | 406 | EP2:.PMM[1].Phase[2].Current[2]
EP2PMM1Phase2Current30 | REAL | 407 | EP2:.PMM[1].Phase[2].Current[30]
EP2PMM1Phase2Current31 | REAL | 408 | EP2:.PMM[1].Phase[2].Current[31]
EP2PMM1Phase2Current32 | REAL | 409 | EP2:.PMM[1].Phase[2].Current[32]
EP2PMM1Phase2Current33 | REAL | 410 | EP2:.PMM[1].Phase[2].Current[33]
EP2PMM1Phase2Current34 | REAL | 411 | EP2:.PMM[1].Phase[2].Current[34]
EP2PMM1Phase2Current35 | REAL | 412 | EP2:.PMM[1].Phase[2].Current[35]
EP2PMM1Phase2Current36 | REAL | 413 | EP2:.PMM[1].Phase[2].Current[36]
EP2PMM1Phase2Current37 | REAL | 414 | EP2:.PMM[1].Phase[2].Current[37]
EP2PMM1Phase2Current38 | REAL | 415 | EP2:.PMM[1].Phase[2].Current[38]
EP2PMM1Phase2Current39 | REAL | 416 | EP2:.PMM[1].Phase[2].Current[39]
EP2PMM1Phase2Current3 | REAL | 417 | EP2:.PMM[1].Phase[2].Current[3]
EP2PMM1Phase2Current40 | REAL | 418 | EP2:.PMM[1].Phase[2].Current[40]
EP2PMM1Phase2Current41 | REAL | 419 | EP2:.PMM[1].Phase[2].Current[41]
EP2PMM1Phase2Current42 | REAL | 420 | EP2:.PMM[1].Phase[2].Current[42]
EP2PMM1Phase2Current4 | REAL | 421 | EP2:.PMM[1].Phase[2].Current[4]
EP2PMM1Phase2Current5 | REAL | 422 | EP2:.PMM[1].Phase[2].Current[5]
EP2PMM1Phase2Current6 | REAL | 423 | EP2:.PMM[1].Phase[2].Current[6]
EP2PMM1Phase2Current7 | REAL | 424 | EP2:.PMM[1].Phase[2].Current[7]
EP2PMM1Phase2Current8 | REAL | 425 | EP2:.PMM[1].Phase[2].Current[8]
EP2PMM1Phase2Current9 | REAL | 426 | EP2:.PMM[1].Phase[2].Current[9]
EP2PMM1Phase3Current10 | REAL | 427 | EP2:.PMM[1].Phase[3].Current[10]
EP2PMM1Phase3Current11 | REAL | 428 | EP2:.PMM[1].Phase[3].Current[11]
EP2PMM1Phase3Current12 | REAL | 429 | EP2:.PMM[1].Phase[3].Current[12]
EP2PMM1Phase3Current13 | REAL | 430 | EP2:.PMM[1].Phase[3].Current[13]
EP2PMM1Phase3Current14 | REAL | 431 | EP2:.PMM[1].Phase[3].Current[14]
EP2PMM1Phase3Current15 | REAL | 432 | EP2:.PMM[1].Phase[3].Current[15]
EP2PMM1Phase3Current16 | REAL | 433 | EP2:.PMM[1].Phase[3].Current[16]
EP2PMM1Phase3Current17 | REAL | 434 | EP2:.PMM[1].Phase[3].Current[17]
EP2PMM1Phase3Current18 | REAL | 435 | EP2:.PMM[1].Phase[3].Current[18]
EP2PMM1Phase3Current19 | REAL | 436 | EP2:.PMM[1].Phase[3].Current[19]
EP2PMM1Phase3Current1 | REAL | 437 | EP2:.PMM[1].Phase[3].Current[1]
EP2PMM1Phase3Current20 | REAL | 438 | EP2:.PMM[1].Phase[3].Current[20]
EP2PMM1Phase3Current21 | REAL | 439 | EP2:.PMM[1].Phase[3].Current[21]
EP2PMM1Phase3Current22 | REAL | 440 | EP2:.PMM[1].Phase[3].Current[22]
EP2PMM1Phase3Current23 | REAL | 441 | EP2:.PMM[1].Phase[3].Current[23]
EP2PMM1Phase3Current24 | REAL | 442 | EP2:.PMM[1].Phase[3].Current[24]
EP2PMM1Phase3Current25 | REAL | 443 | EP2:.PMM[1].Phase[3].Current[25]
EP2PMM1Phase3Current26 | REAL | 444 | EP2:.PMM[1].Phase[3].Current[26]
EP2PMM1Phase3Current27 | REAL | 445 | EP2:.PMM[1].Phase[3].Current[27]
EP2PMM1Phase3Current28 | REAL | 446 | EP2:.PMM[1].Phase[3].Current[28]
EP2PMM1Phase3Current29 | REAL | 447 | EP2:.PMM[1].Phase[3].Current[29]
EP2PMM1Phase3Current2 | REAL | 448 | EP2:.PMM[1].Phase[3].Current[2]
EP2PMM1Phase3Current30 | REAL | 449 | EP2:.PMM[1].Phase[3].Current[30]
EP2PMM1Phase3Current31 | REAL | 450 | EP2:.PMM[1].Phase[3].Current[31]
EP2PMM1Phase3Current32 | REAL | 451 | EP2:.PMM[1].Phase[3].Current[32]
EP2PMM1Phase3Current33 | REAL | 452 | EP2:.PMM[1].Phase[3].Current[33]
EP2PMM1Phase3Current34 | REAL | 453 | EP2:.PMM[1].Phase[3].Current[34]
EP2PMM1Phase3Current35 | REAL | 454 | EP2:.PMM[1].Phase[3].Current[35]
EP2PMM1Phase3Current36 | REAL | 455 | EP2:.PMM[1].Phase[3].Current[36]
EP2PMM1Phase3Current37 | REAL | 456 | EP2:.PMM[1].Phase[3].Current[37]
EP2PMM1Phase3Current38 | REAL | 457 | EP2:.PMM[1].Phase[3].Current[38]
EP2PMM1Phase3Current39 | REAL | 458 | EP2:.PMM[1].Phase[3].Current[39]
EP2PMM1Phase3Current3 | REAL | 459 | EP2:.PMM[1].Phase[3].Current[3]
EP2PMM1Phase3Current40 | REAL | 460 | EP2:.PMM[1].Phase[3].Current[40]
EP2PMM1Phase3Current41 | REAL | 461 | EP2:.PMM[1].Phase[3].Current[41]
EP2PMM1Phase3Current42 | REAL | 462 | EP2:.PMM[1].Phase[3].Current[42]
EP2PMM1Phase3Current4 | REAL | 463 | EP2:.PMM[1].Phase[3].Current[4]
EP2PMM1Phase3Current5 | REAL | 464 | EP2:.PMM[1].Phase[3].Current[5]
EP2PMM1Phase3Current6 | REAL | 465 | EP2:.PMM[1].Phase[3].Current[6]
EP2PMM1Phase3Current7 | REAL | 466 | EP2:.PMM[1].Phase[3].Current[7]
EP2PMM1Phase3Current8 | REAL | 467 | EP2:.PMM[1].Phase[3].Current[8]
EP2PMM1Phase3Current9 | REAL | 468 | EP2:.PMM[1].Phase[3].Current[9]
EP2PMM1PowerFactorPhaseA | REAL | 469 | EP2:.PMM[1].PowerFactorPhaseA
EP2PMM1PowerFactorPhaseB | REAL | 470 | EP2:.PMM[1].PowerFactorPhaseB
EP2PMM1PowerFactorPhaseC | REAL | 471 | EP2:.PMM[1].PowerFactorPhaseC
EP2PMM1TotalActivePower_kW | REAL | 472 | EP2:.PMM[1].TotalActivePower_kW
EP2PMM1TotalAparentPower_kVA | REAL | 473 | EP2:.PMM[1].TotalAparentPower_kVA
EP2PMM1TotalPowerFactor | REAL | 474 | EP2:.PMM[1].TotalPowerFactor
EP2PMM1TotalReactivePower_kVAR | REAL | 475 | EP2:.PMM[1].TotalReactivePower_kVAR
EP2PMM1VoltageBetweenPhaseAB_V | REAL | 476 | EP2:.PMM[1].VoltageBetweenPhaseAB_V
EP2PMM1VoltageBetweenPhaseAN_V | REAL | 477 | EP2:.PMM[1].VoltageBetweenPhaseAN_V
EP2PMM1VoltageBetweenPhaseBC_V | REAL | 478 | EP2:.PMM[1].VoltageBetweenPhaseBC_V
EP2PMM1VoltageBetweenPhaseBN_V | REAL | 479 | EP2:.PMM[1].VoltageBetweenPhaseBN_V
EP2PMM1VoltageBetweenPhaseCA_V | REAL | 480 | EP2:.PMM[1].VoltageBetweenPhaseCA_V
EP2PMM1VoltageBetweenPhaseCN_V | REAL | 481 | EP2:.PMM[1].VoltageBetweenPhaseCN_V
EP2PMM2ActivePowerPhaseA_kW | REAL | 482 | EP2:.PMM[2].ActivePowerPhaseA_kW
EP2PMM2ActivePowerPhaseB_kW | REAL | 483 | EP2:.PMM[2].ActivePowerPhaseB_kW
EP2PMM2ActivePowerPhaseC_kW | REAL | 484 | EP2:.PMM[2].ActivePowerPhaseC_kW
EP2PMM2AlarmPhase1C01_16_60to80 | UINT | 485 | EP2:.PMM[2].AlarmPhase[1].C01_16_60to80
EP2PMM2AlarmPhase1C01_16_over80 | UINT | 486 | EP2:.PMM[2].AlarmPhase[1].C01_16_over80
EP2PMM2AlarmPhase1C17_32_60to80 | UINT | 487 | EP2:.PMM[2].AlarmPhase[1].C17_32_60to80
EP2PMM2AlarmPhase1C17_32_over80 | UINT | 488 | EP2:.PMM[2].AlarmPhase[1].C17_32_over80
EP2PMM2AlarmPhase1C33_42_60to80 | UINT | 489 | EP2:.PMM[2].AlarmPhase[1].C33_42_60to80
EP2PMM2AlarmPhase1C33_42_over80 | UINT | 490 | EP2:.PMM[2].AlarmPhase[1].C33_42_over80
EP2PMM2AlarmPhase1GlobalAlarmReg | INT | 491 | EP2:.PMM[2].AlarmPhase[1].GlobalAlarmReg
EP2PMM2AlarmPhase2C01_16_60to80 | UINT | 492 | EP2:.PMM[2].AlarmPhase[2].C01_16_60to80
EP2PMM2AlarmPhase2C01_16_over80 | UINT | 493 | EP2:.PMM[2].AlarmPhase[2].C01_16_over80
EP2PMM2AlarmPhase2C17_32_60to80 | UINT | 494 | EP2:.PMM[2].AlarmPhase[2].C17_32_60to80
EP2PMM2AlarmPhase2C17_32_over80 | UINT | 495 | EP2:.PMM[2].AlarmPhase[2].C17_32_over80
EP2PMM2AlarmPhase2C33_42_60to80 | UINT | 496 | EP2:.PMM[2].AlarmPhase[2].C33_42_60to80
EP2PMM2AlarmPhase2C33_42_over80 | UINT | 497 | EP2:.PMM[2].AlarmPhase[2].C33_42_over80
EP2PMM2AlarmPhase2GlobalAlarmReg | INT | 498 | EP2:.PMM[2].AlarmPhase[2].GlobalAlarmReg
EP2PMM2AlarmPhase3C01_16_60to80 | UINT | 499 | EP2:.PMM[2].AlarmPhase[3].C01_16_60to80
EP2PMM2AlarmPhase3C01_16_over80 | UINT | 500 | EP2:.PMM[2].AlarmPhase[3].C01_16_over80
EP2PMM2AlarmPhase3C17_32_60to80 | UINT | 501 | EP2:.PMM[2].AlarmPhase[3].C17_32_60to80
EP2PMM2AlarmPhase3C17_32_over80 | UINT | 502 | EP2:.PMM[2].AlarmPhase[3].C17_32_over80
EP2PMM2AlarmPhase3C33_42_60to80 | UINT | 503 | EP2:.PMM[2].AlarmPhase[3].C33_42_60to80
EP2PMM2AlarmPhase3C33_42_over80 | UINT | 504 | EP2:.PMM[2].AlarmPhase[3].C33_42_over80
EP2PMM2AlarmPhase3GlobalAlarmReg | INT | 505 | EP2:.PMM[2].AlarmPhase[3].GlobalAlarmReg
EP2PMM2Alarms | UINT | 506 | EP2:.PMM[2].Alarms
EP2PMM2AverageCurrent_A | REAL | 507 | EP2:.PMM[2].AverageCurrent_A
EP2PMM2AveragePhaseToNeutral_V | REAL | 508 | EP2:.PMM[2].AveragePhaseToNeutral_V
EP2PMM2AveragePhaseToPhase_V | REAL | 509 | EP2:.PMM[2].AveragePhaseToPhase_V
EP2PMM2CurrentInPhaseA_A | REAL | 510 | EP2:.PMM[2].CurrentInPhaseA_A
EP2PMM2CurrentInPhaseB_A | REAL | 511 | EP2:.PMM[2].CurrentInPhaseB_A
EP2PMM2CurrentInPhaseC_A | REAL | 512 | EP2:.PMM[2].CurrentInPhaseC_A
EP2PMM2EnergyConsumed_kWh | REAL | 513 | EP2:.PMM[2].EnergyConsumed_kWh
EP2PMM2Frequency_Hz | REAL | 514 | EP2:.PMM[2].Frequency_Hz
EP2PMM2Napaka | DIGITAL | 515 | EP2:.PMM[2].Napaka
EP2PMM2NeutralCurrent_A | REAL | 516 | EP2:.PMM[2].NeutralCurrent_A
EP2PMM2Phase1Current10 | REAL | 517 | EP2:.PMM[2].Phase[1].Current[10]
EP2PMM2Phase1Current11 | REAL | 518 | EP2:.PMM[2].Phase[1].Current[11]
EP2PMM2Phase1Current12 | REAL | 519 | EP2:.PMM[2].Phase[1].Current[12]
EP2PMM2Phase1Current13 | REAL | 520 | EP2:.PMM[2].Phase[1].Current[13]
EP2PMM2Phase1Current14 | REAL | 521 | EP2:.PMM[2].Phase[1].Current[14]
EP2PMM2Phase1Current15 | REAL | 522 | EP2:.PMM[2].Phase[1].Current[15]
EP2PMM2Phase1Current16 | REAL | 523 | EP2:.PMM[2].Phase[1].Current[16]
EP2PMM2Phase1Current17 | REAL | 524 | EP2:.PMM[2].Phase[1].Current[17]
EP2PMM2Phase1Current18 | REAL | 525 | EP2:.PMM[2].Phase[1].Current[18]
EP2PMM2Phase1Current19 | REAL | 526 | EP2:.PMM[2].Phase[1].Current[19]
EP2PMM2Phase1Current1 | REAL | 527 | EP2:.PMM[2].Phase[1].Current[1]
EP2PMM2Phase1Current20 | REAL | 528 | EP2:.PMM[2].Phase[1].Current[20]
EP2PMM2Phase1Current21 | REAL | 529 | EP2:.PMM[2].Phase[1].Current[21]
EP2PMM2Phase1Current22 | REAL | 530 | EP2:.PMM[2].Phase[1].Current[22]
EP2PMM2Phase1Current23 | REAL | 531 | EP2:.PMM[2].Phase[1].Current[23]
EP2PMM2Phase1Current24 | REAL | 532 | EP2:.PMM[2].Phase[1].Current[24]
EP2PMM2Phase1Current25 | REAL | 533 | EP2:.PMM[2].Phase[1].Current[25]
EP2PMM2Phase1Current26 | REAL | 534 | EP2:.PMM[2].Phase[1].Current[26]
EP2PMM2Phase1Current27 | REAL | 535 | EP2:.PMM[2].Phase[1].Current[27]
EP2PMM2Phase1Current28 | REAL | 536 | EP2:.PMM[2].Phase[1].Current[28]
EP2PMM2Phase1Current29 | REAL | 537 | EP2:.PMM[2].Phase[1].Current[29]
EP2PMM2Phase1Current2 | REAL | 538 | EP2:.PMM[2].Phase[1].Current[2]
EP2PMM2Phase1Current30 | REAL | 539 | EP2:.PMM[2].Phase[1].Current[30]
EP2PMM2Phase1Current31 | REAL | 540 | EP2:.PMM[2].Phase[1].Current[31]
EP2PMM2Phase1Current32 | REAL | 541 | EP2:.PMM[2].Phase[1].Current[32]
EP2PMM2Phase1Current33 | REAL | 542 | EP2:.PMM[2].Phase[1].Current[33]
EP2PMM2Phase1Current34 | REAL | 543 | EP2:.PMM[2].Phase[1].Current[34]
EP2PMM2Phase1Current35 | REAL | 544 | EP2:.PMM[2].Phase[1].Current[35]
EP2PMM2Phase1Current36 | REAL | 545 | EP2:.PMM[2].Phase[1].Current[36]
EP2PMM2Phase1Current37 | REAL | 546 | EP2:.PMM[2].Phase[1].Current[37]
EP2PMM2Phase1Current38 | REAL | 547 | EP2:.PMM[2].Phase[1].Current[38]
EP2PMM2Phase1Current39 | REAL | 548 | EP2:.PMM[2].Phase[1].Current[39]
EP2PMM2Phase1Current3 | REAL | 549 | EP2:.PMM[2].Phase[1].Current[3]
EP2PMM2Phase1Current40 | REAL | 550 | EP2:.PMM[2].Phase[1].Current[40]
EP2PMM2Phase1Current41 | REAL | 551 | EP2:.PMM[2].Phase[1].Current[41]
EP2PMM2Phase1Current42 | REAL | 552 | EP2:.PMM[2].Phase[1].Current[42]
EP2PMM2Phase1Current4 | REAL | 553 | EP2:.PMM[2].Phase[1].Current[4]
EP2PMM2Phase1Current5 | REAL | 554 | EP2:.PMM[2].Phase[1].Current[5]
EP2PMM2Phase1Current6 | REAL | 555 | EP2:.PMM[2].Phase[1].Current[6]
EP2PMM2Phase1Current7 | REAL | 556 | EP2:.PMM[2].Phase[1].Current[7]
EP2PMM2Phase1Current8 | REAL | 557 | EP2:.PMM[2].Phase[1].Current[8]
EP2PMM2Phase1Current9 | REAL | 558 | EP2:.PMM[2].Phase[1].Current[9]
EP2PMM2Phase2Current10 | REAL | 559 | EP2:.PMM[2].Phase[2].Current[10]
EP2PMM2Phase2Current11 | REAL | 560 | EP2:.PMM[2].Phase[2].Current[11]
EP2PMM2Phase2Current12 | REAL | 561 | EP2:.PMM[2].Phase[2].Current[12]
EP2PMM2Phase2Current13 | REAL | 562 | EP2:.PMM[2].Phase[2].Current[13]
EP2PMM2Phase2Current14 | REAL | 563 | EP2:.PMM[2].Phase[2].Current[14]
EP2PMM2Phase2Current15 | REAL | 564 | EP2:.PMM[2].Phase[2].Current[15]
EP2PMM2Phase2Current16 | REAL | 565 | EP2:.PMM[2].Phase[2].Current[16]
EP2PMM2Phase2Current17 | REAL | 566 | EP2:.PMM[2].Phase[2].Current[17]
EP2PMM2Phase2Current18 | REAL | 567 | EP2:.PMM[2].Phase[2].Current[18]
EP2PMM2Phase2Current19 | REAL | 568 | EP2:.PMM[2].Phase[2].Current[19]
EP2PMM2Phase2Current1 | REAL | 569 | EP2:.PMM[2].Phase[2].Current[1]
EP2PMM2Phase2Current20 | REAL | 570 | EP2:.PMM[2].Phase[2].Current[20]
EP2PMM2Phase2Current21 | REAL | 571 | EP2:.PMM[2].Phase[2].Current[21]
EP2PMM2Phase2Current22 | REAL | 572 | EP2:.PMM[2].Phase[2].Current[22]
EP2PMM2Phase2Current23 | REAL | 573 | EP2:.PMM[2].Phase[2].Current[23]
EP2PMM2Phase2Current24 | REAL | 574 | EP2:.PMM[2].Phase[2].Current[24]
EP2PMM2Phase2Current25 | REAL | 575 | EP2:.PMM[2].Phase[2].Current[25]
EP2PMM2Phase2Current26 | REAL | 576 | EP2:.PMM[2].Phase[2].Current[26]
EP2PMM2Phase2Current27 | REAL | 577 | EP2:.PMM[2].Phase[2].Current[27]
EP2PMM2Phase2Current28 | REAL | 578 | EP2:.PMM[2].Phase[2].Current[28]
EP2PMM2Phase2Current29 | REAL | 579 | EP2:.PMM[2].Phase[2].Current[29]
EP2PMM2Phase2Current2 | REAL | 580 | EP2:.PMM[2].Phase[2].Current[2]
EP2PMM2Phase2Current30 | REAL | 581 | EP2:.PMM[2].Phase[2].Current[30]
EP2PMM2Phase2Current31 | REAL | 582 | EP2:.PMM[2].Phase[2].Current[31]
EP2PMM2Phase2Current32 | REAL | 583 | EP2:.PMM[2].Phase[2].Current[32]
EP2PMM2Phase2Current33 | REAL | 584 | EP2:.PMM[2].Phase[2].Current[33]
EP2PMM2Phase2Current34 | REAL | 585 | EP2:.PMM[2].Phase[2].Current[34]
EP2PMM2Phase2Current35 | REAL | 586 | EP2:.PMM[2].Phase[2].Current[35]
EP2PMM2Phase2Current36 | REAL | 587 | EP2:.PMM[2].Phase[2].Current[36]
EP2PMM2Phase2Current37 | REAL | 588 | EP2:.PMM[2].Phase[2].Current[37]
EP2PMM2Phase2Current38 | REAL | 589 | EP2:.PMM[2].Phase[2].Current[38]
EP2PMM2Phase2Current39 | REAL | 590 | EP2:.PMM[2].Phase[2].Current[39]
EP2PMM2Phase2Current3 | REAL | 591 | EP2:.PMM[2].Phase[2].Current[3]
EP2PMM2Phase2Current40 | REAL | 592 | EP2:.PMM[2].Phase[2].Current[40]
EP2PMM2Phase2Current41 | REAL | 593 | EP2:.PMM[2].Phase[2].Current[41]
EP2PMM2Phase2Current42 | REAL | 594 | EP2:.PMM[2].Phase[2].Current[42]
EP2PMM2Phase2Current4 | REAL | 595 | EP2:.PMM[2].Phase[2].Current[4]
EP2PMM2Phase2Current5 | REAL | 596 | EP2:.PMM[2].Phase[2].Current[5]
EP2PMM2Phase2Current6 | REAL | 597 | EP2:.PMM[2].Phase[2].Current[6]
EP2PMM2Phase2Current7 | REAL | 598 | EP2:.PMM[2].Phase[2].Current[7]
EP2PMM2Phase2Current8 | REAL | 599 | EP2:.PMM[2].Phase[2].Current[8]
EP2PMM2Phase2Current9 | REAL | 600 | EP2:.PMM[2].Phase[2].Current[9]
EP2PMM2Phase3Current10 | REAL | 601 | EP2:.PMM[2].Phase[3].Current[10]
EP2PMM2Phase3Current11 | REAL | 602 | EP2:.PMM[2].Phase[3].Current[11]
EP2PMM2Phase3Current12 | REAL | 603 | EP2:.PMM[2].Phase[3].Current[12]
EP2PMM2Phase3Current13 | REAL | 604 | EP2:.PMM[2].Phase[3].Current[13]
EP2PMM2Phase3Current14 | REAL | 605 | EP2:.PMM[2].Phase[3].Current[14]
EP2PMM2Phase3Current15 | REAL | 606 | EP2:.PMM[2].Phase[3].Current[15]
EP2PMM2Phase3Current16 | REAL | 607 | EP2:.PMM[2].Phase[3].Current[16]
EP2PMM2Phase3Current17 | REAL | 608 | EP2:.PMM[2].Phase[3].Current[17]
EP2PMM2Phase3Current18 | REAL | 609 | EP2:.PMM[2].Phase[3].Current[18]
EP2PMM2Phase3Current19 | REAL | 610 | EP2:.PMM[2].Phase[3].Current[19]
EP2PMM2Phase3Current1 | REAL | 611 | EP2:.PMM[2].Phase[3].Current[1]
EP2PMM2Phase3Current20 | REAL | 612 | EP2:.PMM[2].Phase[3].Current[20]
EP2PMM2Phase3Current21 | REAL | 613 | EP2:.PMM[2].Phase[3].Current[21]
EP2PMM2Phase3Current22 | REAL | 614 | EP2:.PMM[2].Phase[3].Current[22]
EP2PMM2Phase3Current23 | REAL | 615 | EP2:.PMM[2].Phase[3].Current[23]
EP2PMM2Phase3Current24 | REAL | 616 | EP2:.PMM[2].Phase[3].Current[24]
EP2PMM2Phase3Current25 | REAL | 617 | EP2:.PMM[2].Phase[3].Current[25]
EP2PMM2Phase3Current26 | REAL | 618 | EP2:.PMM[2].Phase[3].Current[26]
EP2PMM2Phase3Current27 | REAL | 619 | EP2:.PMM[2].Phase[3].Current[27]
EP2PMM2Phase3Current28 | REAL | 620 | EP2:.PMM[2].Phase[3].Current[28]
EP2PMM2Phase3Current29 | REAL | 621 | EP2:.PMM[2].Phase[3].Current[29]
EP2PMM2Phase3Current2 | REAL | 622 | EP2:.PMM[2].Phase[3].Current[2]
EP2PMM2Phase3Current30 | REAL | 623 | EP2:.PMM[2].Phase[3].Current[30]
EP2PMM2Phase3Current31 | REAL | 624 | EP2:.PMM[2].Phase[3].Current[31]
EP2PMM2Phase3Current32 | REAL | 625 | EP2:.PMM[2].Phase[3].Current[32]
EP2PMM2Phase3Current33 | REAL | 626 | EP2:.PMM[2].Phase[3].Current[33]
EP2PMM2Phase3Current34 | REAL | 627 | EP2:.PMM[2].Phase[3].Current[34]
EP2PMM2Phase3Current35 | REAL | 628 | EP2:.PMM[2].Phase[3].Current[35]
EP2PMM2Phase3Current36 | REAL | 629 | EP2:.PMM[2].Phase[3].Current[36]
EP2PMM2Phase3Current37 | REAL | 630 | EP2:.PMM[2].Phase[3].Current[37]
EP2PMM2Phase3Current38 | REAL | 631 | EP2:.PMM[2].Phase[3].Current[38]
EP2PMM2Phase3Current39 | REAL | 632 | EP2:.PMM[2].Phase[3].Current[39]
EP2PMM2Phase3Current3 | REAL | 633 | EP2:.PMM[2].Phase[3].Current[3]
EP2PMM2Phase3Current40 | REAL | 634 | EP2:.PMM[2].Phase[3].Current[40]
EP2PMM2Phase3Current41 | REAL | 635 | EP2:.PMM[2].Phase[3].Current[41]
EP2PMM2Phase3Current42 | REAL | 636 | EP2:.PMM[2].Phase[3].Current[42]
EP2PMM2Phase3Current4 | REAL | 637 | EP2:.PMM[2].Phase[3].Current[4]
EP2PMM2Phase3Current5 | REAL | 638 | EP2:.PMM[2].Phase[3].Current[5]
EP2PMM2Phase3Current6 | REAL | 639 | EP2:.PMM[2].Phase[3].Current[6]
EP2PMM2Phase3Current7 | REAL | 640 | EP2:.PMM[2].Phase[3].Current[7]
EP2PMM2Phase3Current8 | REAL | 641 | EP2:.PMM[2].Phase[3].Current[8]
EP2PMM2Phase3Current9 | REAL | 642 | EP2:.PMM[2].Phase[3].Current[9]
EP2PMM2PowerFactorPhaseA | REAL | 643 | EP2:.PMM[2].PowerFactorPhaseA
EP2PMM2PowerFactorPhaseB | REAL | 644 | EP2:.PMM[2].PowerFactorPhaseB
EP2PMM2PowerFactorPhaseC | REAL | 645 | EP2:.PMM[2].PowerFactorPhaseC
EP2PMM2TotalActivePower_kW | REAL | 646 | EP2:.PMM[2].TotalActivePower_kW
EP2PMM2TotalAparentPower_kVA | REAL | 647 | EP2:.PMM[2].TotalAparentPower_kVA
EP2PMM2TotalPowerFactor | REAL | 648 | EP2:.PMM[2].TotalPowerFactor
EP2PMM2TotalReactivePower_kVAR | REAL | 649 | EP2:.PMM[2].TotalReactivePower_kVAR
EP2PMM2VoltageBetweenPhaseAB_V | REAL | 650 | EP2:.PMM[2].VoltageBetweenPhaseAB_V
EP2PMM2VoltageBetweenPhaseAN_V | REAL | 651 | EP2:.PMM[2].VoltageBetweenPhaseAN_V
EP2PMM2VoltageBetweenPhaseBC_V | REAL | 652 | EP2:.PMM[2].VoltageBetweenPhaseBC_V
EP2PMM2VoltageBetweenPhaseBN_V | REAL | 653 | EP2:.PMM[2].VoltageBetweenPhaseBN_V
EP2PMM2VoltageBetweenPhaseCA_V | REAL | 654 | EP2:.PMM[2].VoltageBetweenPhaseCA_V
EP2PMM2VoltageBetweenPhaseCN_V | REAL | 655 | EP2:.PMM[2].VoltageBetweenPhaseCN_V
EP2PMM3ActivePowerPhaseA_kW | REAL | 656 | EP2:.PMM[3].ActivePowerPhaseA_kW
EP2PMM3ActivePowerPhaseB_kW | REAL | 657 | EP2:.PMM[3].ActivePowerPhaseB_kW
EP2PMM3ActivePowerPhaseC_kW | REAL | 658 | EP2:.PMM[3].ActivePowerPhaseC_kW
EP2PMM3AlarmPhase1C01_16_60to80 | UINT | 659 | EP2:.PMM[3].AlarmPhase[1].C01_16_60to80
EP2PMM3AlarmPhase1C01_16_over80 | UINT | 660 | EP2:.PMM[3].AlarmPhase[1].C01_16_over80
EP2PMM3AlarmPhase1C17_32_60to80 | UINT | 661 | EP2:.PMM[3].AlarmPhase[1].C17_32_60to80
EP2PMM3AlarmPhase1C17_32_over80 | UINT | 662 | EP2:.PMM[3].AlarmPhase[1].C17_32_over80
EP2PMM3AlarmPhase1C33_42_60to80 | UINT | 663 | EP2:.PMM[3].AlarmPhase[1].C33_42_60to80
EP2PMM3AlarmPhase1C33_42_over80 | UINT | 664 | EP2:.PMM[3].AlarmPhase[1].C33_42_over80
EP2PMM3AlarmPhase1GlobalAlarmReg | INT | 665 | EP2:.PMM[3].AlarmPhase[1].GlobalAlarmReg
EP2PMM3AlarmPhase2C01_16_60to80 | UINT | 666 | EP2:.PMM[3].AlarmPhase[2].C01_16_60to80
EP2PMM3AlarmPhase2C01_16_over80 | UINT | 667 | EP2:.PMM[3].AlarmPhase[2].C01_16_over80
EP2PMM3AlarmPhase2C17_32_60to80 | UINT | 668 | EP2:.PMM[3].AlarmPhase[2].C17_32_60to80
EP2PMM3AlarmPhase2C17_32_over80 | UINT | 669 | EP2:.PMM[3].AlarmPhase[2].C17_32_over80
EP2PMM3AlarmPhase2C33_42_60to80 | UINT | 670 | EP2:.PMM[3].AlarmPhase[2].C33_42_60to80
EP2PMM3AlarmPhase2C33_42_over80 | UINT | 671 | EP2:.PMM[3].AlarmPhase[2].C33_42_over80
EP2PMM3AlarmPhase2GlobalAlarmReg | INT | 672 | EP2:.PMM[3].AlarmPhase[2].GlobalAlarmReg
EP2PMM3AlarmPhase3C01_16_60to80 | UINT | 673 | EP2:.PMM[3].AlarmPhase[3].C01_16_60to80
EP2PMM3AlarmPhase3C01_16_over80 | UINT | 674 | EP2:.PMM[3].AlarmPhase[3].C01_16_over80
EP2PMM3AlarmPhase3C17_32_60to80 | UINT | 675 | EP2:.PMM[3].AlarmPhase[3].C17_32_60to80
EP2PMM3AlarmPhase3C17_32_over80 | UINT | 676 | EP2:.PMM[3].AlarmPhase[3].C17_32_over80
EP2PMM3AlarmPhase3C33_42_60to80 | UINT | 677 | EP2:.PMM[3].AlarmPhase[3].C33_42_60to80
EP2PMM3AlarmPhase3C33_42_over80 | UINT | 678 | EP2:.PMM[3].AlarmPhase[3].C33_42_over80
EP2PMM3AlarmPhase3GlobalAlarmReg | INT | 679 | EP2:.PMM[3].AlarmPhase[3].GlobalAlarmReg
EP2PMM3Alarms | UINT | 680 | EP2:.PMM[3].Alarms
EP2PMM3AverageCurrent_A | REAL | 681 | EP2:.PMM[3].AverageCurrent_A
EP2PMM3AveragePhaseToNeutral_V | REAL | 682 | EP2:.PMM[3].AveragePhaseToNeutral_V
EP2PMM3AveragePhaseToPhase_V | REAL | 683 | EP2:.PMM[3].AveragePhaseToPhase_V
EP2PMM3CurrentInPhaseA_A | REAL | 684 | EP2:.PMM[3].CurrentInPhaseA_A
EP2PMM3CurrentInPhaseB_A | REAL | 685 | EP2:.PMM[3].CurrentInPhaseB_A
EP2PMM3CurrentInPhaseC_A | REAL | 686 | EP2:.PMM[3].CurrentInPhaseC_A
EP2PMM3EnergyConsumed_kWh | REAL | 687 | EP2:.PMM[3].EnergyConsumed_kWh
EP2PMM3Frequency_Hz | REAL | 688 | EP2:.PMM[3].Frequency_Hz
EP2PMM3Napaka | DIGITAL | 689 | EP2:.PMM[3].Napaka
EP2PMM3NeutralCurrent_A | REAL | 690 | EP2:.PMM[3].NeutralCurrent_A
EP2PMM3Phase1Current10 | REAL | 691 | EP2:.PMM[3].Phase[1].Current[10]
EP2PMM3Phase1Current11 | REAL | 692 | EP2:.PMM[3].Phase[1].Current[11]
EP2PMM3Phase1Current12 | REAL | 693 | EP2:.PMM[3].Phase[1].Current[12]
EP2PMM3Phase1Current13 | REAL | 694 | EP2:.PMM[3].Phase[1].Current[13]
EP2PMM3Phase1Current14 | REAL | 695 | EP2:.PMM[3].Phase[1].Current[14]
EP2PMM3Phase1Current15 | REAL | 696 | EP2:.PMM[3].Phase[1].Current[15]
EP2PMM3Phase1Current16 | REAL | 697 | EP2:.PMM[3].Phase[1].Current[16]
EP2PMM3Phase1Current17 | REAL | 698 | EP2:.PMM[3].Phase[1].Current[17]
EP2PMM3Phase1Current18 | REAL | 699 | EP2:.PMM[3].Phase[1].Current[18]
EP2PMM3Phase1Current19 | REAL | 700 | EP2:.PMM[3].Phase[1].Current[19]
EP2PMM3Phase1Current1 | REAL | 701 | EP2:.PMM[3].Phase[1].Current[1]
EP2PMM3Phase1Current20 | REAL | 702 | EP2:.PMM[3].Phase[1].Current[20]
EP2PMM3Phase1Current21 | REAL | 703 | EP2:.PMM[3].Phase[1].Current[21]
EP2PMM3Phase1Current22 | REAL | 704 | EP2:.PMM[3].Phase[1].Current[22]
EP2PMM3Phase1Current23 | REAL | 705 | EP2:.PMM[3].Phase[1].Current[23]
EP2PMM3Phase1Current24 | REAL | 706 | EP2:.PMM[3].Phase[1].Current[24]
EP2PMM3Phase1Current25 | REAL | 707 | EP2:.PMM[3].Phase[1].Current[25]
EP2PMM3Phase1Current26 | REAL | 708 | EP2:.PMM[3].Phase[1].Current[26]
EP2PMM3Phase1Current27 | REAL | 709 | EP2:.PMM[3].Phase[1].Current[27]
EP2PMM3Phase1Current28 | REAL | 710 | EP2:.PMM[3].Phase[1].Current[28]
EP2PMM3Phase1Current29 | REAL | 711 | EP2:.PMM[3].Phase[1].Current[29]
EP2PMM3Phase1Current2 | REAL | 712 | EP2:.PMM[3].Phase[1].Current[2]
EP2PMM3Phase1Current30 | REAL | 713 | EP2:.PMM[3].Phase[1].Current[30]
EP2PMM3Phase1Current31 | REAL | 714 | EP2:.PMM[3].Phase[1].Current[31]
EP2PMM3Phase1Current32 | REAL | 715 | EP2:.PMM[3].Phase[1].Current[32]
EP2PMM3Phase1Current33 | REAL | 716 | EP2:.PMM[3].Phase[1].Current[33]
EP2PMM3Phase1Current34 | REAL | 717 | EP2:.PMM[3].Phase[1].Current[34]
EP2PMM3Phase1Current35 | REAL | 718 | EP2:.PMM[3].Phase[1].Current[35]
EP2PMM3Phase1Current36 | REAL | 719 | EP2:.PMM[3].Phase[1].Current[36]
EP2PMM3Phase1Current37 | REAL | 720 | EP2:.PMM[3].Phase[1].Current[37]
EP2PMM3Phase1Current38 | REAL | 721 | EP2:.PMM[3].Phase[1].Current[38]
EP2PMM3Phase1Current39 | REAL | 722 | EP2:.PMM[3].Phase[1].Current[39]
EP2PMM3Phase1Current3 | REAL | 723 | EP2:.PMM[3].Phase[1].Current[3]
EP2PMM3Phase1Current40 | REAL | 724 | EP2:.PMM[3].Phase[1].Current[40]
EP2PMM3Phase1Current41 | REAL | 725 | EP2:.PMM[3].Phase[1].Current[41]
EP2PMM3Phase1Current42 | REAL | 726 | EP2:.PMM[3].Phase[1].Current[42]
EP2PMM3Phase1Current4 | REAL | 727 | EP2:.PMM[3].Phase[1].Current[4]
EP2PMM3Phase1Current5 | REAL | 728 | EP2:.PMM[3].Phase[1].Current[5]
EP2PMM3Phase1Current6 | REAL | 729 | EP2:.PMM[3].Phase[1].Current[6]
EP2PMM3Phase1Current7 | REAL | 730 | EP2:.PMM[3].Phase[1].Current[7]
EP2PMM3Phase1Current8 | REAL | 731 | EP2:.PMM[3].Phase[1].Current[8]
EP2PMM3Phase1Current9 | REAL | 732 | EP2:.PMM[3].Phase[1].Current[9]
EP2PMM3Phase2Current10 | REAL | 733 | EP2:.PMM[3].Phase[2].Current[10]
EP2PMM3Phase2Current11 | REAL | 734 | EP2:.PMM[3].Phase[2].Current[11]
EP2PMM3Phase2Current12 | REAL | 735 | EP2:.PMM[3].Phase[2].Current[12]
EP2PMM3Phase2Current13 | REAL | 736 | EP2:.PMM[3].Phase[2].Current[13]
EP2PMM3Phase2Current14 | REAL | 737 | EP2:.PMM[3].Phase[2].Current[14]
EP2PMM3Phase2Current15 | REAL | 738 | EP2:.PMM[3].Phase[2].Current[15]
EP2PMM3Phase2Current16 | REAL | 739 | EP2:.PMM[3].Phase[2].Current[16]
EP2PMM3Phase2Current17 | REAL | 740 | EP2:.PMM[3].Phase[2].Current[17]
EP2PMM3Phase2Current18 | REAL | 741 | EP2:.PMM[3].Phase[2].Current[18]
EP2PMM3Phase2Current19 | REAL | 742 | EP2:.PMM[3].Phase[2].Current[19]
EP2PMM3Phase2Current1 | REAL | 743 | EP2:.PMM[3].Phase[2].Current[1]
EP2PMM3Phase2Current20 | REAL | 744 | EP2:.PMM[3].Phase[2].Current[20]
EP2PMM3Phase2Current21 | REAL | 745 | EP2:.PMM[3].Phase[2].Current[21]
EP2PMM3Phase2Current22 | REAL | 746 | EP2:.PMM[3].Phase[2].Current[22]
EP2PMM3Phase2Current23 | REAL | 747 | EP2:.PMM[3].Phase[2].Current[23]
EP2PMM3Phase2Current24 | REAL | 748 | EP2:.PMM[3].Phase[2].Current[24]
EP2PMM3Phase2Current25 | REAL | 749 | EP2:.PMM[3].Phase[2].Current[25]
EP2PMM3Phase2Current26 | REAL | 750 | EP2:.PMM[3].Phase[2].Current[26]
EP2PMM3Phase2Current27 | REAL | 751 | EP2:.PMM[3].Phase[2].Current[27]
EP2PMM3Phase2Current28 | REAL | 752 | EP2:.PMM[3].Phase[2].Current[28]
EP2PMM3Phase2Current29 | REAL | 753 | EP2:.PMM[3].Phase[2].Current[29]
EP2PMM3Phase2Current2 | REAL | 754 | EP2:.PMM[3].Phase[2].Current[2]
EP2PMM3Phase2Current30 | REAL | 755 | EP2:.PMM[3].Phase[2].Current[30]
EP2PMM3Phase2Current31 | REAL | 756 | EP2:.PMM[3].Phase[2].Current[31]
EP2PMM3Phase2Current32 | REAL | 757 | EP2:.PMM[3].Phase[2].Current[32]
EP2PMM3Phase2Current33 | REAL | 758 | EP2:.PMM[3].Phase[2].Current[33]
EP2PMM3Phase2Current34 | REAL | 759 | EP2:.PMM[3].Phase[2].Current[34]
EP2PMM3Phase2Current35 | REAL | 760 | EP2:.PMM[3].Phase[2].Current[35]
EP2PMM3Phase2Current36 | REAL | 761 | EP2:.PMM[3].Phase[2].Current[36]
EP2PMM3Phase2Current37 | REAL | 762 | EP2:.PMM[3].Phase[2].Current[37]
EP2PMM3Phase2Current38 | REAL | 763 | EP2:.PMM[3].Phase[2].Current[38]
EP2PMM3Phase2Current39 | REAL | 764 | EP2:.PMM[3].Phase[2].Current[39]
EP2PMM3Phase2Current3 | REAL | 765 | EP2:.PMM[3].Phase[2].Current[3]
EP2PMM3Phase2Current40 | REAL | 766 | EP2:.PMM[3].Phase[2].Current[40]
EP2PMM3Phase2Current41 | REAL | 767 | EP2:.PMM[3].Phase[2].Current[41]
EP2PMM3Phase2Current42 | REAL | 768 | EP2:.PMM[3].Phase[2].Current[42]
EP2PMM3Phase2Current4 | REAL | 769 | EP2:.PMM[3].Phase[2].Current[4]
EP2PMM3Phase2Current5 | REAL | 770 | EP2:.PMM[3].Phase[2].Current[5]
EP2PMM3Phase2Current6 | REAL | 771 | EP2:.PMM[3].Phase[2].Current[6]
EP2PMM3Phase2Current7 | REAL | 772 | EP2:.PMM[3].Phase[2].Current[7]
EP2PMM3Phase2Current8 | REAL | 773 | EP2:.PMM[3].Phase[2].Current[8]
EP2PMM3Phase2Current9 | REAL | 774 | EP2:.PMM[3].Phase[2].Current[9]
EP2PMM3Phase3Current10 | REAL | 775 | EP2:.PMM[3].Phase[3].Current[10]
EP2PMM3Phase3Current11 | REAL | 776 | EP2:.PMM[3].Phase[3].Current[11]
EP2PMM3Phase3Current12 | REAL | 777 | EP2:.PMM[3].Phase[3].Current[12]
EP2PMM3Phase3Current13 | REAL | 778 | EP2:.PMM[3].Phase[3].Current[13]
EP2PMM3Phase3Current14 | REAL | 779 | EP2:.PMM[3].Phase[3].Current[14]
EP2PMM3Phase3Current15 | REAL | 780 | EP2:.PMM[3].Phase[3].Current[15]
EP2PMM3Phase3Current16 | REAL | 781 | EP2:.PMM[3].Phase[3].Current[16]
EP2PMM3Phase3Current17 | REAL | 782 | EP2:.PMM[3].Phase[3].Current[17]
EP2PMM3Phase3Current18 | REAL | 783 | EP2:.PMM[3].Phase[3].Current[18]
EP2PMM3Phase3Current19 | REAL | 784 | EP2:.PMM[3].Phase[3].Current[19]
EP2PMM3Phase3Current1 | REAL | 785 | EP2:.PMM[3].Phase[3].Current[1]
EP2PMM3Phase3Current20 | REAL | 786 | EP2:.PMM[3].Phase[3].Current[20]
EP2PMM3Phase3Current21 | REAL | 787 | EP2:.PMM[3].Phase[3].Current[21]
EP2PMM3Phase3Current22 | REAL | 788 | EP2:.PMM[3].Phase[3].Current[22]
EP2PMM3Phase3Current23 | REAL | 789 | EP2:.PMM[3].Phase[3].Current[23]
EP2PMM3Phase3Current24 | REAL | 790 | EP2:.PMM[3].Phase[3].Current[24]
EP2PMM3Phase3Current25 | REAL | 791 | EP2:.PMM[3].Phase[3].Current[25]
EP2PMM3Phase3Current26 | REAL | 792 | EP2:.PMM[3].Phase[3].Current[26]
EP2PMM3Phase3Current27 | REAL | 793 | EP2:.PMM[3].Phase[3].Current[27]
EP2PMM3Phase3Current28 | REAL | 794 | EP2:.PMM[3].Phase[3].Current[28]
EP2PMM3Phase3Current29 | REAL | 795 | EP2:.PMM[3].Phase[3].Current[29]
EP2PMM3Phase3Current2 | REAL | 796 | EP2:.PMM[3].Phase[3].Current[2]
EP2PMM3Phase3Current30 | REAL | 797 | EP2:.PMM[3].Phase[3].Current[30]
EP2PMM3Phase3Current31 | REAL | 798 | EP2:.PMM[3].Phase[3].Current[31]
EP2PMM3Phase3Current32 | REAL | 799 | EP2:.PMM[3].Phase[3].Current[32]
EP2PMM3Phase3Current33 | REAL | 800 | EP2:.PMM[3].Phase[3].Current[33]
EP2PMM3Phase3Current34 | REAL | 801 | EP2:.PMM[3].Phase[3].Current[34]
EP2PMM3Phase3Current35 | REAL | 802 | EP2:.PMM[3].Phase[3].Current[35]
EP2PMM3Phase3Current36 | REAL | 803 | EP2:.PMM[3].Phase[3].Current[36]
EP2PMM3Phase3Current37 | REAL | 804 | EP2:.PMM[3].Phase[3].Current[37]
EP2PMM3Phase3Current38 | REAL | 805 | EP2:.PMM[3].Phase[3].Current[38]
EP2PMM3Phase3Current39 | REAL | 806 | EP2:.PMM[3].Phase[3].Current[39]
EP2PMM3Phase3Current3 | REAL | 807 | EP2:.PMM[3].Phase[3].Current[3]
EP2PMM3Phase3Current40 | REAL | 808 | EP2:.PMM[3].Phase[3].Current[40]
EP2PMM3Phase3Current41 | REAL | 809 | EP2:.PMM[3].Phase[3].Current[41]
EP2PMM3Phase3Current42 | REAL | 810 | EP2:.PMM[3].Phase[3].Current[42]
EP2PMM3Phase3Current4 | REAL | 811 | EP2:.PMM[3].Phase[3].Current[4]
EP2PMM3Phase3Current5 | REAL | 812 | EP2:.PMM[3].Phase[3].Current[5]
EP2PMM3Phase3Current6 | REAL | 813 | EP2:.PMM[3].Phase[3].Current[6]
EP2PMM3Phase3Current7 | REAL | 814 | EP2:.PMM[3].Phase[3].Current[7]
EP2PMM3Phase3Current8 | REAL | 815 | EP2:.PMM[3].Phase[3].Current[8]
EP2PMM3Phase3Current9 | REAL | 816 | EP2:.PMM[3].Phase[3].Current[9]
EP2PMM3PowerFactorPhaseA | REAL | 817 | EP2:.PMM[3].PowerFactorPhaseA
EP2PMM3PowerFactorPhaseB | REAL | 818 | EP2:.PMM[3].PowerFactorPhaseB
EP2PMM3PowerFactorPhaseC | REAL | 819 | EP2:.PMM[3].PowerFactorPhaseC
EP2PMM3TotalActivePower_kW | REAL | 820 | EP2:.PMM[3].TotalActivePower_kW
EP2PMM3TotalAparentPower_kVA | REAL | 821 | EP2:.PMM[3].TotalAparentPower_kVA
EP2PMM3TotalPowerFactor | REAL | 822 | EP2:.PMM[3].TotalPowerFactor
EP2PMM3TotalReactivePower_kVAR | REAL | 823 | EP2:.PMM[3].TotalReactivePower_kVAR
EP2PMM3VoltageBetweenPhaseAB_V | REAL | 824 | EP2:.PMM[3].VoltageBetweenPhaseAB_V
EP2PMM3VoltageBetweenPhaseAN_V | REAL | 825 | EP2:.PMM[3].VoltageBetweenPhaseAN_V
EP2PMM3VoltageBetweenPhaseBC_V | REAL | 826 | EP2:.PMM[3].VoltageBetweenPhaseBC_V
EP2PMM3VoltageBetweenPhaseBN_V | REAL | 827 | EP2:.PMM[3].VoltageBetweenPhaseBN_V
EP2PMM3VoltageBetweenPhaseCA_V | REAL | 828 | EP2:.PMM[3].VoltageBetweenPhaseCA_V
EP2PMM3VoltageBetweenPhaseCN_V | REAL | 829 | EP2:.PMM[3].VoltageBetweenPhaseCN_V
EP2PMMfaza01 | REAL | IOD_EP2_TCP | 45193
EP2PMMfaza02 | REAL | IOD_EP2_TCP | 45195
EP2PMMfaza03 | REAL | IOD_EP2_TCP | 45197
EP2PMMfaza04 | REAL | IOD_EP2_TCP | 45199
EP2PMMfaza05 | REAL | IOD_EP2_TCP | 45201
EP2PMMfaza06 | REAL | IOD_EP2_TCP | 45203
EP2PMMfaza07 | REAL | IOD_EP2_TCP | 45205
EP2PMMfaza08 | REAL | IOD_EP2_TCP | 45207
EP2PMMfaza09 | REAL | IOD_EP2_TCP | 45209
EP2PMMfaza10 | REAL | IOD_EP2_TCP | 45211
EP2PMMfaza11 | REAL | IOD_EP2_TCP | 45213
EP2PMMfaza12 | REAL | IOD_EP2_TCP | 45215
EP2PMMfaza13 | REAL | IOD_EP2_TCP | 45217
EP2PMMfaza14 | REAL | IOD_EP2_TCP | 45219
EP2PMMfaza15 | REAL | IOD_EP2_TCP | 45221
EP2PMMfaza16 | REAL | IOD_EP2_TCP | 45223
EP2PMMfaza17 | REAL | IOD_EP2_TCP | 45225
EP2PMMfaza18 | REAL | IOD_EP2_TCP | 45227
EP2PMMfaza19 | REAL | IOD_EP2_TCP | 45229
EP2PMMfaza20 | REAL | IOD_EP2_TCP | 45231
EP2PMMfaza21 | REAL | IOD_EP2_TCP | 45233
EP2PMMfaza22 | REAL | IOD_EP2_TCP | 45235
EP2PMMfaza23 | REAL | IOD_EP2_TCP | 45237
EP2PMMfaza24 | REAL | IOD_EP2_TCP | 45239
EP2PMMfaza25 | REAL | IOD_EP2_TCP | 45241
EP2PMMfaza26 | REAL | IOD_EP2_TCP | 45243
EP2PMMfaza27 | REAL | IOD_EP2_TCP | 45245
EP2PMMfaza28 | REAL | IOD_EP2_TCP | 45247
EP2PMMfaza29 | REAL | IOD_EP2_TCP | 45249
EP2PMMfaza30 | REAL | IOD_EP2_TCP | 45251
EP2PMMfaza31 | REAL | IOD_EP2_TCP | 45253
EP2PMMfaza32 | REAL | IOD_EP2_TCP | 45255
EP2PMMfaza33 | REAL | IOD_EP2_TCP | 45257
EP2PMMfaza34 | REAL | IOD_EP2_TCP | 45259
EP2PMMfaza35 | REAL | IOD_EP2_TCP | 45261
EP2PMMfaza36 | REAL | IOD_EP2_TCP | 45263
EP2PMMfaza37 | REAL | IOD_EP2_TCP | 45265
EP2PMMfaza38 | REAL | IOD_EP2_TCP | 45267
EP2PMMfaza39 | REAL | IOD_EP2_TCP | 45269
EP2PMMfaza40 | REAL | IOD_EP2_TCP | 45271
EP2PMMfaza41 | REAL | IOD_EP2_TCP | 45273
EP2PMMfaza42 | REAL | IOD_EP2_TCP | 45275
EP2PMMfaza6010 | REAL | IOD_EP2_TCP | 45277
EP2PMMfaza6011 | REAL | IOD_EP2_TCP | 45279
EP2PMMfaza6012 | REAL | IOD_EP2_TCP | 45281
EP2PMMfaza6013 | REAL | IOD_EP2_TCP | 45283
EP2PMMfaza6014 | REAL | IOD_EP2_TCP | 45285
EP2PMMfaza6015 | REAL | IOD_EP2_TCP | 45287
EP2PMMfaza6016 | REAL | IOD_EP2_TCP | 45289
EP2PMMfaza6017 | REAL | IOD_EP2_TCP | 45291
EP2PMMfaza6018 | REAL | IOD_EP2_TCP | 45293
EP2PMMfaza6019 | REAL | IOD_EP2_TCP | 45295
EP2PMMfaza601 | REAL | IOD_EP2_TCP | 45297
EP2PMMfaza6020 | REAL | IOD_EP2_TCP | 45299
EP2PMMfaza6021 | REAL | IOD_EP2_TCP | 45301
EP2PMMfaza6022 | REAL | IOD_EP2_TCP | 45303
EP2PMMfaza6023 | REAL | IOD_EP2_TCP | 45305
EP2PMMfaza6024 | REAL | IOD_EP2_TCP | 45307
EP2PMMfaza6025 | REAL | IOD_EP2_TCP | 45309
EP2PMMfaza6026 | REAL | IOD_EP2_TCP | 45311
EP2PMMfaza6027 | REAL | IOD_EP2_TCP | 45313
EP2PMMfaza6028 | REAL | IOD_EP2_TCP | 45315
EP2PMMfaza6029 | REAL | IOD_EP2_TCP | 45317
EP2PMMfaza602 | REAL | IOD_EP2_TCP | 45319
EP2PMMfaza6030 | REAL | IOD_EP2_TCP | 45321
EP2PMMfaza6031 | REAL | IOD_EP2_TCP | 45323
EP2PMMfaza6032 | REAL | IOD_EP2_TCP | 45325
EP2PMMfaza6033 | REAL | IOD_EP2_TCP | 45327
EP2PMMfaza6034 | REAL | IOD_EP2_TCP | 45329
EP2PMMfaza6035 | REAL | IOD_EP2_TCP | 45331
EP2PMMfaza6036 | REAL | IOD_EP2_TCP | 45333
EP2PMMfaza6037 | REAL | IOD_EP2_TCP | 45335
EP2PMMfaza6038 | REAL | IOD_EP2_TCP | 45337
EP2PMMfaza6039 | REAL | IOD_EP2_TCP | 45339
EP2PMMfaza603 | REAL | IOD_EP2_TCP | 45341
EP2PMMfaza6040 | REAL | IOD_EP2_TCP | 45343
EP2PMMfaza6041 | REAL | IOD_EP2_TCP | 45345
EP2PMMfaza6042 | REAL | IOD_EP2_TCP | 45347
EP2PMMfaza604 | REAL | IOD_EP2_TCP | 45349
EP2PMMfaza605 | REAL | IOD_EP2_TCP | 45351
EP2PMMfaza606 | REAL | IOD_EP2_TCP | 45353
EP2PMMfaza607 | REAL | IOD_EP2_TCP | 45355
EP2PMMfaza608 | REAL | IOD_EP2_TCP | 45357
EP2PMMfaza609 | REAL | IOD_EP2_TCP | 45359
EP2PMMfaza8010 | REAL | IOD_EP2_TCP | 45361
EP2PMMfaza8011 | REAL | IOD_EP2_TCP | 45363
EP2PMMfaza8012 | REAL | IOD_EP2_TCP | 45365
EP2PMMfaza8013 | REAL | IOD_EP2_TCP | 45367
EP2PMMfaza8014 | REAL | IOD_EP2_TCP | 45369
EP2PMMfaza8015 | REAL | IOD_EP2_TCP | 45371
EP2PMMfaza8016 | REAL | IOD_EP2_TCP | 45373
EP2PMMfaza8017 | REAL | IOD_EP2_TCP | 45375
EP2PMMfaza8018 | REAL | IOD_EP2_TCP | 45377
EP2PMMfaza8019 | REAL | IOD_EP2_TCP | 45379
EP2PMMfaza801 | REAL | IOD_EP2_TCP | 45381
EP2PMMfaza8020 | REAL | IOD_EP2_TCP | 45383
EP2PMMfaza8021 | REAL | IOD_EP2_TCP | 45385
EP2PMMfaza8022 | REAL | IOD_EP2_TCP | 45387
EP2PMMfaza8023 | REAL | IOD_EP2_TCP | 45389
EP2PMMfaza8024 | REAL | IOD_EP2_TCP | 45391
EP2PMMfaza8025 | REAL | IOD_EP2_TCP | 45393
EP2PMMfaza8026 | REAL | IOD_EP2_TCP | 45395
EP2PMMfaza8027 | REAL | IOD_EP2_TCP | 45397
EP2PMMfaza8028 | REAL | IOD_EP2_TCP | 45399
EP2PMMfaza8029 | REAL | IOD_EP2_TCP | 45401
EP2PMMfaza802 | REAL | IOD_EP2_TCP | 45403
EP2PMMfaza8030 | REAL | IOD_EP2_TCP | 45405
EP2PMMfaza8031 | REAL | IOD_EP2_TCP | 45407
EP2PMMfaza8032 | REAL | IOD_EP2_TCP | 45409
EP2PMMfaza8033 | REAL | IOD_EP2_TCP | 45411
EP2PMMfaza8034 | REAL | IOD_EP2_TCP | 45413
EP2PMMfaza8035 | REAL | IOD_EP2_TCP | 45415
EP2PMMfaza8036 | REAL | IOD_EP2_TCP | 45417
EP2PMMfaza8037 | REAL | IOD_EP2_TCP | 45419
EP2PMMfaza8038 | REAL | IOD_EP2_TCP | 45421
EP2PMMfaza8039 | REAL | IOD_EP2_TCP | 45423
EP2PMMfaza803 | REAL | IOD_EP2_TCP | 45425
EP2PMMfaza8040 | REAL | IOD_EP2_TCP | 45427
EP2PMMfaza8041 | REAL | IOD_EP2_TCP | 45429
EP2PMMfaza8042 | REAL | IOD_EP2_TCP | 45431
EP2PMMfaza804 | REAL | IOD_EP2_TCP | 45433
EP2PMMfaza805 | REAL | IOD_EP2_TCP | 45435
EP2PMMfaza806 | REAL | IOD_EP2_TCP | 45437
EP2PMMfaza807 | REAL | IOD_EP2_TCP | 45439
EP2PMMfaza808 | REAL | IOD_EP2_TCP | 45441
EP2PMMfaza809 | REAL | IOD_EP2_TCP | 45443
EP2PMMgalActivePowerPhaseA_kW | REAL | IOD_EP2_TCP | 45445
EP2PMMgalActivePowerPhaseB_kW | REAL | IOD_EP2_TCP | 45447
EP2PMMgalActivePowerPhaseC_kW | REAL | IOD_EP2_TCP | 45449
EP2PMMgalAlarmPhase1C01_16_60to80 | UINT | IOD_EP2_TCP | 48001
EP2PMMgalAlarmPhase1C01_16_over80 | UINT | IOD_EP2_TCP | 48002
EP2PMMgalAlarmPhase1C17_32_60to80 | UINT | IOD_EP2_TCP | 48003
EP2PMMgalAlarmPhase1C17_32_over80 | UINT | IOD_EP2_TCP | 48004
EP2PMMgalAlarmPhase1C33_42_60to80 | UINT | IOD_EP2_TCP | 48005
EP2PMMgalAlarmPhase1C33_42_over80 | UINT | IOD_EP2_TCP | 48006
EP2PMMgalAlarmPhase1GlobalAlarmReg | INT | IOD_EP2_TCP | 40352
EP2PMMgalAlarmPhase2C01_16_60to80 | UINT | IOD_EP2_TCP | 48007
EP2PMMgalAlarmPhase2C01_16_over80 | UINT | IOD_EP2_TCP | 48008
EP2PMMgalAlarmPhase2C17_32_60to80 | UINT | IOD_EP2_TCP | 48009
EP2PMMgalAlarmPhase2C17_32_over80 | UINT | IOD_EP2_TCP | 48010
EP2PMMgalAlarmPhase2C33_42_60to80 | UINT | IOD_EP2_TCP | 48011
EP2PMMgalAlarmPhase2C33_42_over80 | UINT | IOD_EP2_TCP | 48012
EP2PMMgalAlarmPhase2GlobalAlarmReg | INT | IOD_EP2_TCP | 40353
EP2PMMgalAlarmPhase3C01_16_60to80 | UINT | IOD_EP2_TCP | 48013
EP2PMMgalAlarmPhase3C01_16_over80 | UINT | IOD_EP2_TCP | 48014
EP2PMMgalAlarmPhase3C17_32_60to80 | UINT | IOD_EP2_TCP | 48015
EP2PMMgalAlarmPhase3C17_32_over80 | UINT | IOD_EP2_TCP | 48016
EP2PMMgalAlarmPhase3C33_42_60to80 | UINT | IOD_EP2_TCP | 48017
EP2PMMgalAlarmPhase3C33_42_over80 | UINT | IOD_EP2_TCP | 48018
EP2PMMgalAlarmPhase3GlobalAlarmReg | INT | IOD_EP2_TCP | 40354
EP2PMMgalAlarms | UINT | IOD_EP2_TCP | 48019
EP2PMMgalAverageCurrent_A | REAL | IOD_EP2_TCP | 45451
EP2PMMgalAveragePhaseToNeutral_V | REAL | IOD_EP2_TCP | 45453
EP2PMMgalAveragePhaseToPhase_V | REAL | IOD_EP2_TCP | 45455
EP2PMMgalCurrentInPhaseA_A | REAL | IOD_EP2_TCP | 45457
EP2PMMgalCurrentInPhaseB_A | REAL | IOD_EP2_TCP | 45459
EP2PMMgalCurrentInPhaseC_A | REAL | IOD_EP2_TCP | 45461
EP2PMMgalEnergyConsumed_kWh | REAL | IOD_EP2_TCP | 45463
EP2PMMgalFrequency_Hz | REAL | IOD_EP2_TCP | 45465
EP2PMMgalNapaka | DIGITAL | IOD_EP2_TCP | 00433
EP2PMMgalNeutralCurrent_A | REAL | IOD_EP2_TCP | 45467
EP2PMMgalPhase1Current10 | REAL | IOD_EP2_TCP | 45469
EP2PMMgalPhase1Current11 | REAL | IOD_EP2_TCP | 45471
EP2PMMgalPhase1Current12 | REAL | IOD_EP2_TCP | 45473
EP2PMMgalPhase1Current13 | REAL | IOD_EP2_TCP | 45475
EP2PMMgalPhase1Current14 | REAL | IOD_EP2_TCP | 45477
EP2PMMgalPhase1Current15 | REAL | IOD_EP2_TCP | 45479
EP2PMMgalPhase1Current16 | REAL | IOD_EP2_TCP | 45481
EP2PMMgalPhase1Current17 | REAL | IOD_EP2_TCP | 45483
EP2PMMgalPhase1Current18 | REAL | IOD_EP2_TCP | 45485
EP2PMMgalPhase1Current19 | REAL | IOD_EP2_TCP | 45487
EP2PMMgalPhase1Current1 | REAL | IOD_EP2_TCP | 45489
EP2PMMgalPhase1Current20 | REAL | IOD_EP2_TCP | 45491
EP2PMMgalPhase1Current21 | REAL | IOD_EP2_TCP | 45493
EP2PMMgalPhase1Current22 | REAL | IOD_EP2_TCP | 45495
EP2PMMgalPhase1Current23 | REAL | IOD_EP2_TCP | 45497
EP2PMMgalPhase1Current24 | REAL | IOD_EP2_TCP | 45499
EP2PMMgalPhase1Current25 | REAL | IOD_EP2_TCP | 45501
EP2PMMgalPhase1Current26 | REAL | IOD_EP2_TCP | 45503
EP2PMMgalPhase1Current27 | REAL | IOD_EP2_TCP | 45505
EP2PMMgalPhase1Current28 | REAL | IOD_EP2_TCP | 45507
EP2PMMgalPhase1Current29 | REAL | IOD_EP2_TCP | 45509
EP2PMMgalPhase1Current2 | REAL | IOD_EP2_TCP | 45511
EP2PMMgalPhase1Current30 | REAL | IOD_EP2_TCP | 45513
EP2PMMgalPhase1Current31 | REAL | IOD_EP2_TCP | 45515
EP2PMMgalPhase1Current32 | REAL | IOD_EP2_TCP | 45517
EP2PMMgalPhase1Current33 | REAL | IOD_EP2_TCP | 45519
EP2PMMgalPhase1Current34 | REAL | IOD_EP2_TCP | 45521
EP2PMMgalPhase1Current35 | REAL | IOD_EP2_TCP | 45523
EP2PMMgalPhase1Current36 | REAL | IOD_EP2_TCP | 45525
EP2PMMgalPhase1Current37 | REAL | IOD_EP2_TCP | 45527
EP2PMMgalPhase1Current38 | REAL | IOD_EP2_TCP | 45529
EP2PMMgalPhase1Current39 | REAL | IOD_EP2_TCP | 45531
EP2PMMgalPhase1Current3 | REAL | IOD_EP2_TCP | 45533
EP2PMMgalPhase1Current40 | REAL | IOD_EP2_TCP | 45535
EP2PMMgalPhase1Current41 | REAL | IOD_EP2_TCP | 45537
EP2PMMgalPhase1Current42 | REAL | IOD_EP2_TCP | 45539
EP2PMMgalPhase1Current4 | REAL | IOD_EP2_TCP | 45541
EP2PMMgalPhase1Current5 | REAL | IOD_EP2_TCP | 45543
EP2PMMgalPhase1Current6 | REAL | IOD_EP2_TCP | 45545
EP2PMMgalPhase1Current7 | REAL | IOD_EP2_TCP | 45547
EP2PMMgalPhase1Current8 | REAL | IOD_EP2_TCP | 45549
EP2PMMgalPhase1Current9 | REAL | IOD_EP2_TCP | 45551
EP2PMMgalPhase2Current10 | REAL | IOD_EP2_TCP | 45553
EP2PMMgalPhase2Current11 | REAL | IOD_EP2_TCP | 45555
EP2PMMgalPhase2Current12 | REAL | IOD_EP2_TCP | 45557
EP2PMMgalPhase2Current13 | REAL | IOD_EP2_TCP | 45559
EP2PMMgalPhase2Current14 | REAL | IOD_EP2_TCP | 45561
EP2PMMgalPhase2Current15 | REAL | IOD_EP2_TCP | 45563
EP2PMMgalPhase2Current16 | REAL | IOD_EP2_TCP | 45565
EP2PMMgalPhase2Current17 | REAL | IOD_EP2_TCP | 45567
EP2PMMgalPhase2Current18 | REAL | IOD_EP2_TCP | 45569
EP2PMMgalPhase2Current19 | REAL | IOD_EP2_TCP | 45571
EP2PMMgalPhase2Current1 | REAL | IOD_EP2_TCP | 45573
EP2PMMgalPhase2Current20 | REAL | IOD_EP2_TCP | 45575
EP2PMMgalPhase2Current21 | REAL | IOD_EP2_TCP | 45577
EP2PMMgalPhase2Current22 | REAL | IOD_EP2_TCP | 45579
EP2PMMgalPhase2Current23 | REAL | IOD_EP2_TCP | 45581
EP2PMMgalPhase2Current24 | REAL | IOD_EP2_TCP | 45583
EP2_DI_Q32_IZKLJUCENO_omogoci | DIGITAL | IOD_EP2_disk | D9011
EP2_DI_Q27_IZKLJUCENO_omogoci | DIGITAL | IOD_EP2_disk | D9012
EP2_DI_Q34_IZKLJUCENO_omogoci | DIGITAL | IOD_EP2_disk | D9013
EP2_DI_Q30_IZKLJUCENO_omogoci | DIGITAL | IOD_EP2_disk | D9014
EP2_DI_Q32_VKLJUCENO_omogoci | DIGITAL | IOD_EP2_disk | D9015
EP2_DI_Q27_VKLJUCENO_omogoci | DIGITAL | IOD_EP2_disk | D9016
EP2_DI_Q34_VKLJUCENO_omogoci | DIGITAL | IOD_EP2_disk | D9017
EP2_DI_Q30_VKLJUCENO_omogoci | DIGITAL | IOD_EP2_disk | D9018
NOT_EP2_DI_Q1_GlavnoStikalo_ON_omogoci | DIGITAL | IOD_EP2_disk | D9019
NOT_EP2_DI_Q2_Rezerva_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9020
NOT_EP2_DI_Q5_OdcKlima1_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9021
NOT_EP2_DI_Q6_OdcKlima2_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9022
NOT_EP2_DI_Q7_OdcKlima3_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9023
NOT_EP2_DI_Q8_OdcKlima4_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9024
NOT_EP2_DI_Q9_OdcKlima5_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9025
NOT_EP2_DI_Q10_OdcKlima6_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9026
NOT_EP2_DI_Q11_OdcVent1_ON_omogoci | DIGITAL | IOD_EP2_disk | D9027
NOT_EP2_DI_Q12_Rezerva_ON_omogoci | DIGITAL | IOD_EP2_disk | D9028
NOT_EP2_DI_Q25_OdcUpsA_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9029
NOT_EP2_DI_Q26_OdcByA_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9030
NOT_EP2_DI_Q27_OdcByUpsA_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9031
NOT_EP2_DI_Q31_DovByUpsA_ON_omogoci | DIGITAL | IOD_EP2_disk | D9032
EP2_DI_Q32_DovByA_ON_omogoci | DIGITAL | IOD_EP2_disk | D9033
NOT_EP2_DI_Q28_OdcUpsB_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9034
EP2DI_Q29_OdcByB_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9035
NOT_EP2_DI_Q30_OdcByUpsB_IZP_omogoci | DIGITAL | IOD_EP2_disk | D9036
NOT_EP2_DI_Q33_DovByUpsB_ON_omogoci | DIGITAL | IOD_EP2_disk | D9037
EP2DI_Q34_DovByB_ON_omogoci | DIGITAL | IOD_EP2_disk | D9038
NOT_EP2_DI_Klima5_ERR_omogoci | DIGITAL | IOD_EP2_disk | D9039
NOT_EP2_DI_Klima6_ERR_omogoci | DIGITAL | IOD_EP2_disk | D9040
EP2TempAlarmPoint | REAL | IOD_EP2_TCP | 45585 | 0 | 60 | 0 | 60 | °C | ##.#
EP2ErrCommScada2 | DIGITAL | IOD_EP2_TCP | 00434
EP2ComSCADA2 | DIGITAL | IOD_EP2_TCP | 00435
EP2_ErrCommScada_omogoci2 | DIGITAL | IOD_EP2_disk | D9043
EP2Server_A_Izpad | DIGITAL | IOD_EP2_disk | D9044
EP2Server_B_Izpad | DIGITAL | IOD_EP2_disk | D9045
EP2_RazlikaUr | REAL | IOD_EP2_TCP | 45587 | [5 empty] | ##.#
EP2_ComSCADA_stevec3 | INT | IOD_EP2_mem | I9048
EP2_ComSCADA_stevec | INT | IOD_EP2_mem | I9050
EP2ComSCADA3 | DIGITAL | IOD_EP2_TCP | 00436
EP2kom_nast_cas_izpada | INT | IOD_EP2_TCP | 40355
EP2_Circ1_MaximumDemandA2 | REAL | IOD_EP2_TCP | 45589 | 0 | 1200 | 0 | 1200 | A | ###.#
EP2_Circ1_MaximumDemandA3 | REAL | IOD_EP2_TCP | 45591 | 0 | 1200 | 0 | 1200 | A | ###.#
EP2Circ1RazEner_D_SCADA | REAL | IOD_EP2_TCP | 45593
EP2Circ1RazEner_T_SCADA | REAL | IOD_EP2_TCP | 45595
EP2Circ1RazEner_M_SCADA | REAL | IOD_EP2_TCP | 45597
EP2Circ_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_EP2_TCP | 00437
EP2Circ_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_EP2_TCP | 00438
EP2Circ_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_EP2_TCP | 00439
EP2Circ_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_EP2_TCP | 00440
EP2Circ_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_EP2_TCP | 00441
EP2Circ_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_EP2_TCP | 00442
EP2Circ_Vpis_Dnevne_energija_scada1_mem | DIGITAL | IOD_EP2_disk | D10000
EP2Circ_Vpis_Dnevne_energija_scada2_mem | DIGITAL | IOD_EP2_disk | D10001
EP2Circ_Vpis_Tedenska_energija_scada1_mem | DIGITAL | IOD_EP2_disk | D10002
EP2Circ_Vpis_Tedenska_energija_scada2_mem | DIGITAL | IOD_EP2_disk | D10003
EP2Circ_Vpis_Mesecna_energija_scada1_mem | DIGITAL | IOD_EP2_disk | D10004
EP2Circ_Vpis_Mesecna_energija_scada2_mem | DIGITAL | IOD_EP2_disk | D10005

## XSoft
mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Write_BOOL(FC) | mod_Write_Word(FC) | mod_Write_Word(FC) | mod_Write_dWord(FC) | mod_Write_dWord(FC) | mod_Write_String(FC)
(*Branje BOOL*) | (*Branje INT*) | (*Branje UINT*) | (*Branje LONG*) | (*Branje REAL*) | (*Branje STRING*) | (*Pisanje BOOL*) | (*Pisanje INT*) | (*Pisanje UINT*) | (*Pisanje LONG*) | (*Pisanje REAL*) | (*Pisanje STRING*)
(**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**)
mind_bool[0]:=AlarmGenCirc1; | mind[0]:=DateTime.Dan; | mind[8000]:=PMMgal.AlarmPhase[1].C01_16_60to80; |  | Read_Real(rVar:=Circ[1].CosFi_III,lo:=4000,hi:=4001); | Read_String(sVar:=UserCurrentName,start:=7000); | 0:AlarmGenCirc1:=Bit_0; | 0:DateTime.Dan:=Byte_0; | 8000:PMMgal.AlarmPhase[1].C01_16_60to80:=Word_01; |  | 4001:Circ[1].CosFi_III:=Real_0; | 7000:UserCurrentName:=String_0;
mind_bool[1]:=AlarmGenComm; | mind[1]:=DateTime.Leto; | mind[8001]:=PMMgal.AlarmPhase[1].C01_16_over80; |  | Read_Real(rVar:=Circ[1].DelovnaEnergija,lo:=4002,hi:=4003); |  | 1:AlarmGenComm:=Bit_0; | 1:DateTime.Leto:=Byte_0; | 8001:PMMgal.AlarmPhase[1].C01_16_over80:=Word_01; |  | 4003:Circ[1].DelovnaEnergija:=Real_0;
mind_bool[2]:=AlarmGenDI; | mind[2]:=DateTime.Mesec; | mind[8002]:=PMMgal.AlarmPhase[1].C17_32_60to80; |  | Read_Real(rVar:=Circ[1].DelovnaMoc_III,lo:=4004,hi:=4005); |  | 2:AlarmGenDI:=Bit_0; | 2:DateTime.Mesec:=Byte_0; | 8002:PMMgal.AlarmPhase[1].C17_32_60to80:=Word_01; |  | 4005:Circ[1].DelovnaMoc_III:=Real_0;
mind_bool[3]:=AlarmGenKlima5; | mind[3]:=DateTime.Minuta; | mind[8003]:=PMMgal.AlarmPhase[1].C17_32_over80; |  | Read_Real(rVar:=Circ[1].DelovnaMoc_L1,lo:=4006,hi:=4007); |  | 3:AlarmGenKlima5:=Bit_0; | 3:DateTime.Minuta:=Byte_0; | 8003:PMMgal.AlarmPhase[1].C17_32_over80:=Word_01; |  | 4007:Circ[1].DelovnaMoc_L1:=Real_0;
mind_bool[4]:=AlarmGenKlima6; | mind[4]:=DateTime.Sekunda; | mind[8004]:=PMMgal.AlarmPhase[1].C33_42_60to80; |  | Read_Real(rVar:=Circ[1].DelovnaMoc_L2,lo:=4008,hi:=4009); |  | 4:AlarmGenKlima6:=Bit_0; | 4:DateTime.Sekunda:=Byte_0; | 8004:PMMgal.AlarmPhase[1].C33_42_60to80:=Word_01; |  | 4009:Circ[1].DelovnaMoc_L2:=Real_0;
mind_bool[5]:=AlarmGenPMM1; | mind[5]:=DateTime.Ura; | mind[8005]:=PMMgal.AlarmPhase[1].C33_42_over80; |  | Read_Real(rVar:=Circ[1].DelovnaMoc_L3,lo:=4010,hi:=4011); |  | 5:AlarmGenPMM1:=Bit_0; | 5:DateTime.Ura:=Byte_0; | 8005:PMMgal.AlarmPhase[1].C33_42_over80:=Word_01; |  | 4011:Circ[1].DelovnaMoc_L3:=Real_0;
mind_bool[6]:=AlarmGenPMM2; | mind[6]:=Klima[1].GrelecStatus; | mind[8006]:=PMMgal.AlarmPhase[2].C01_16_60to80; |  | Read_Real(rVar:=Circ[1].Frekvenca_L1,lo:=4012,hi:=4013); |  | 6:AlarmGenPMM2:=Bit_0; | 6:Klima[1].GrelecStatus:=Byte_0; | 8006:PMMgal.AlarmPhase[2].C01_16_60to80:=Word_01; |  | 4013:Circ[1].Frekvenca_L1:=Real_0;
mind_bool[7]:=AlarmGenPMM3; | mind[7]:=Klima[1].IzhodniVentStatus; | mind[8007]:=PMMgal.AlarmPhase[2].C01_16_over80; |  | Read_Real(rVar:=Circ[1].InduktivnaEnergija,lo:=4014,hi:=4015); |  | 7:AlarmGenPMM3:=Bit_0; | 7:Klima[1].IzhodniVentStatus:=Byte_0; | 8007:PMMgal.AlarmPhase[2].C01_16_over80:=Word_01; |  | 4015:Circ[1].InduktivnaEnergija:=Real_0;
mind_bool[8]:=AlarmGenUPS1; | mind[8]:=Klima[1].KompresorStatus; | mind[8008]:=PMMgal.AlarmPhase[2].C17_32_60to80; |  | Read_Real(rVar:=Circ[1].InduktivnaMoc_III,lo:=4016,hi:=4017); |  | 8:AlarmGenUPS1:=Bit_0; | 8:Klima[1].KompresorStatus:=Byte_0; | 8008:PMMgal.AlarmPhase[2].C17_32_60to80:=Word_01; |  | 4017:Circ[1].InduktivnaMoc_III:=Real_0;
mind_bool[9]:=AlarmGenUPS2; | mind[9]:=Klima[1].VlazilecStatus; | mind[8009]:=PMMgal.AlarmPhase[2].C17_32_over80; |  | Read_Real(rVar:=Circ[1].JalovaMoc_L1,lo:=4018,hi:=4019); |  | 9:AlarmGenUPS2:=Bit_0; | 9:Klima[1].VlazilecStatus:=Byte_0; | 8009:PMMgal.AlarmPhase[2].C17_32_over80:=Word_01; |  | 4019:Circ[1].JalovaMoc_L1:=Real_0;
mind_bool[10]:=ComSCADA; | mind[10]:=Klima[2].GrelecStatus; | mind[8010]:=PMMgal.AlarmPhase[2].C33_42_60to80; |  | Read_Real(rVar:=Circ[1].JalovaMoc_L2,lo:=4020,hi:=4021); |  | 10:ComSCADA:=Bit_0; | 10:Klima[2].GrelecStatus:=Byte_0; | 8010:PMMgal.AlarmPhase[2].C33_42_60to80:=Word_01; |  | 4021:Circ[1].JalovaMoc_L2:=Real_0;
mind_bool[11]:=ComSCADA1; | mind[11]:=Klima[2].IzhodniVentStatus; | mind[8011]:=PMMgal.AlarmPhase[2].C33_42_over80; |  | Read_Real(rVar:=Circ[1].JalovaMoc_L3,lo:=4022,hi:=4023); |  | 11:ComSCADA1:=Bit_0; | 11:Klima[2].IzhodniVentStatus:=Byte_0; | 8011:PMMgal.AlarmPhase[2].C33_42_over80:=Word_01; |  | 4023:Circ[1].JalovaMoc_L3:=Real_0;
mind_bool[12]:=DI_Klima5_ERR; | mind[12]:=Klima[2].KompresorStatus; | mind[8012]:=PMMgal.AlarmPhase[3].C01_16_60to80; |  | Read_Real(rVar:=Circ[1].KapacitivnaEnergija,lo:=4024,hi:=4025); |  | 12:DI_Klima5_ERR:=Bit_0; | 12:Klima[2].KompresorStatus:=Byte_0; | 8012:PMMgal.AlarmPhase[3].C01_16_60to80:=Word_01; |  | 4025:Circ[1].KapacitivnaEnergija:=Real_0;
mind_bool[13]:=DI_Klima5_ON; | mind[13]:=Klima[2].VlazilecStatus; | mind[8013]:=PMMgal.AlarmPhase[3].C01_16_over80; |  | Read_Real(rVar:=Circ[1].KapacitivnaMoc_III,lo:=4026,hi:=4027); |  | 13:DI_Klima5_ON:=Bit_0; | 13:Klima[2].VlazilecStatus:=Byte_0; | 8013:PMMgal.AlarmPhase[3].C01_16_over80:=Word_01; |  | 4027:Circ[1].KapacitivnaMoc_III:=Real_0;
mind_bool[14]:=DI_Klima6_ERR; | mind[14]:=PMM[1].AlarmPhase[1].C01_16_60to80; | mind[8014]:=PMMgal.AlarmPhase[3].C17_32_60to80; |  | Read_Real(rVar:=Circ[1].MaximumDemand,lo:=4028,hi:=4029); |  | 14:DI_Klima6_ERR:=Bit_0; | 14:PMM[1].AlarmPhase[1].C01_16_60to80:=Word_01; | 8014:PMMgal.AlarmPhase[3].C17_32_60to80:=Word_01; |  | 4029:Circ[1].MaximumDemand:=Real_0;
mind_bool[15]:=DI_Klima6_ON; | mind[15]:=PMM[1].AlarmPhase[1].C01_16_over80; | mind[8015]:=PMMgal.AlarmPhase[3].C17_32_over80; |  | Read_Real(rVar:=Circ[1].Napetost_L1_L2,lo:=4030,hi:=4031); |  | 15:DI_Klima6_ON:=Bit_0; | 15:PMM[1].AlarmPhase[1].C01_16_over80:=Word_01; | 8015:PMMgal.AlarmPhase[3].C17_32_over80:=Word_01; |  | 4031:Circ[1].Napetost_L1_L2:=Real_0;
mind_bool[16]:=DI_KlimaSplit1_ERR; | mind[16]:=PMM[1].AlarmPhase[1].C17_32_60to80; | mind[8016]:=PMMgal.AlarmPhase[3].C33_42_60to80; |  | Read_Real(rVar:=Circ[1].Napetost_L1_N,lo:=4032,hi:=4033); |  | 16:DI_KlimaSplit1_ERR:=Bit_0; | 16:PMM[1].AlarmPhase[1].C17_32_60to80:=Word_01; | 8016:PMMgal.AlarmPhase[3].C33_42_60to80:=Word_01; |  | 4033:Circ[1].Napetost_L1_N:=Real_0;
mind_bool[17]:=DI_KlimaSplit1_ON; | mind[17]:=PMM[1].AlarmPhase[1].C17_32_over80; | mind[8017]:=PMMgal.AlarmPhase[3].C33_42_over80; |  | Read_Real(rVar:=Circ[1].Napetost_L2_L3,lo:=4034,hi:=4035); |  | 17:DI_KlimaSplit1_ON:=Bit_0; | 17:PMM[1].AlarmPhase[1].C17_32_over80:=Word_01; | 8017:PMMgal.AlarmPhase[3].C33_42_over80:=Word_01; |  | 4035:Circ[1].Napetost_L2_L3:=Real_0;
mind_bool[18]:=DI_Q10_OdcKlima6_IZP; | mind[18]:=PMM[1].AlarmPhase[1].C33_42_60to80; | mind[8018]:=PMMgal.Alarms; |  | Read_Real(rVar:=Circ[1].Napetost_L2_N,lo:=4036,hi:=4037); |  | 18:DI_Q10_OdcKlima6_IZP:=Bit_0; | 18:PMM[1].AlarmPhase[1].C33_42_60to80:=Word_01; | 8018:PMMgal.Alarms:=Word_01; |  | 4037:Circ[1].Napetost_L2_N:=Real_0;
mind_bool[19]:=DI_Q10_OdcKlima6_ON; | mind[19]:=PMM[1].AlarmPhase[1].C33_42_over80; |  |  | Read_Real(rVar:=Circ[1].Napetost_L3_L1,lo:=4038,hi:=4039); |  | 19:DI_Q10_OdcKlima6_ON:=Bit_0; | 19:PMM[1].AlarmPhase[1].C33_42_over80:=Word_01; |  |  | 4039:Circ[1].Napetost_L3_L1:=Real_0;
mind_bool[20]:=DI_Q11_OdcVent1_ON; | mind[20]:=PMM[1].AlarmPhase[1].GlobalAlarmReg; |  |  | Read_Real(rVar:=Circ[1].Napetost_L3_N,lo:=4040,hi:=4041); |  | 20:DI_Q11_OdcVent1_ON:=Bit_0; | 20:PMM[1].AlarmPhase[1].GlobalAlarmReg:=Word_01; |  |  | 4041:Circ[1].Napetost_L3_N:=Real_0;
mind_bool[21]:=DI_Q12_Rezerva_ON; | mind[21]:=PMM[1].AlarmPhase[2].C01_16_60to80; |  |  | Read_Real(rVar:=Circ[1].NavideznaMoc_III,lo:=4042,hi:=4043); |  | 21:DI_Q12_Rezerva_ON:=Bit_0; | 21:PMM[1].AlarmPhase[2].C01_16_60to80:=Word_01; |  |  | 4043:Circ[1].NavideznaMoc_III:=Real_0;
mind_bool[22]:=DI_Q1_GlavnoStikalo_ON; | mind[22]:=PMM[1].AlarmPhase[2].C01_16_over80; |  |  | Read_Real(rVar:=Circ[1].NicelniTok,lo:=4044,hi:=4045); |  | 22:DI_Q1_GlavnoStikalo_ON:=Bit_0; | 22:PMM[1].AlarmPhase[2].C01_16_over80:=Word_01; |  |  | 4045:Circ[1].NicelniTok:=Real_0;
mind_bool[23]:=DI_Q25_OdcUpsA_IZP; | mind[23]:=PMM[1].AlarmPhase[2].C17_32_60to80; |  |  | Read_Real(rVar:=Circ[1].PowerFactor_III,lo:=4046,hi:=4047); |  | 23:DI_Q25_OdcUpsA_IZP:=Bit_0; | 23:PMM[1].AlarmPhase[2].C17_32_60to80:=Word_01; |  |  | 4047:Circ[1].PowerFactor_III:=Real_0;
mind_bool[24]:=DI_Q25_OdcUpsA_ON; | mind[24]:=PMM[1].AlarmPhase[2].C17_32_over80; |  |  | Read_Real(rVar:=Circ[1].PowerFactor_L1,lo:=4048,hi:=4049); |  | 24:DI_Q25_OdcUpsA_ON:=Bit_0; | 24:PMM[1].AlarmPhase[2].C17_32_over80:=Word_01; |  |  | 4049:Circ[1].PowerFactor_L1:=Real_0;
mind_bool[25]:=DI_Q26_OdcByA_IZP; | mind[25]:=PMM[1].AlarmPhase[2].C33_42_60to80; |  |  | Read_Real(rVar:=Circ[1].PowerFactor_L2,lo:=4050,hi:=4051); |  | 25:DI_Q26_OdcByA_IZP:=Bit_0; | 25:PMM[1].AlarmPhase[2].C33_42_60to80:=Word_01; |  |  | 4051:Circ[1].PowerFactor_L2:=Real_0;
mind_bool[26]:=DI_Q26_OdcByA_ON; | mind[26]:=PMM[1].AlarmPhase[2].C33_42_over80; |  |  | Read_Real(rVar:=Circ[1].PowerFactor_L3,lo:=4052,hi:=4053); |  | 26:DI_Q26_OdcByA_ON:=Bit_0; | 26:PMM[1].AlarmPhase[2].C33_42_over80:=Word_01; |  |  | 4053:Circ[1].PowerFactor_L3:=Real_0;
mind_bool[27]:=DI_Q27_OdcByUpsA_IZP; | mind[27]:=PMM[1].AlarmPhase[2].GlobalAlarmReg; |  |  | Read_Real(rVar:=Circ[1].THDI_L1,lo:=4054,hi:=4055); |  | 27:DI_Q27_OdcByUpsA_IZP:=Bit_0; | 27:PMM[1].AlarmPhase[2].GlobalAlarmReg:=Word_01; |  |  | 4055:Circ[1].THDI_L1:=Real_0;
mind_bool[28]:=DI_Q27_OdcByUpsA_ON; | mind[28]:=PMM[1].AlarmPhase[3].C01_16_60to80; |  |  | Read_Real(rVar:=Circ[1].THDI_L2,lo:=4056,hi:=4057); |  | 28:DI_Q27_OdcByUpsA_ON:=Bit_0; | 28:PMM[1].AlarmPhase[3].C01_16_60to80:=Word_01; |  |  | 4057:Circ[1].THDI_L2:=Real_0;
mind_bool[29]:=DI_Q28_OdcUpsB_IZP; | mind[29]:=PMM[1].AlarmPhase[3].C01_16_over80; |  |  | Read_Real(rVar:=Circ[1].THDI_L3,lo:=4058,hi:=4059); |  | 29:DI_Q28_OdcUpsB_IZP:=Bit_0; | 29:PMM[1].AlarmPhase[3].C01_16_over80:=Word_01; |  |  | 4059:Circ[1].THDI_L3:=Real_0;
mind_bool[30]:=DI_Q28_OdcUpsB_ON; | mind[30]:=PMM[1].AlarmPhase[3].C17_32_60to80; |  |  | Read_Real(rVar:=Circ[1].THDV_L1,lo:=4060,hi:=4061); |  | 30:DI_Q28_OdcUpsB_ON:=Bit_0; | 30:PMM[1].AlarmPhase[3].C17_32_60to80:=Word_01; |  |  | 4061:Circ[1].THDV_L1:=Real_0;
mind_bool[31]:=DI_Q29_OdcByB_IZP; | mind[31]:=PMM[1].AlarmPhase[3].C17_32_over80; |  |  | Read_Real(rVar:=Circ[1].THDV_L2,lo:=4062,hi:=4063); |  | 31:DI_Q29_OdcByB_IZP:=Bit_0; | 31:PMM[1].AlarmPhase[3].C17_32_over80:=Word_01; |  |  | 4063:Circ[1].THDV_L2:=Real_0;
mind_bool[32]:=DI_Q29_OdcByB_ON; | mind[32]:=PMM[1].AlarmPhase[3].C33_42_60to80; |  |  | Read_Real(rVar:=Circ[1].THDV_L3,lo:=4064,hi:=4065); |  | 32:DI_Q29_OdcByB_ON:=Bit_0; | 32:PMM[1].AlarmPhase[3].C33_42_60to80:=Word_01; |  |  | 4065:Circ[1].THDV_L3:=Real_0;
mind_bool[33]:=DI_Q2_Rezerva_IZP; | mind[33]:=PMM[1].AlarmPhase[3].C33_42_over80; |  |  | Read_Real(rVar:=Circ[1].Tok_L1,lo:=4066,hi:=4067); |  | 33:DI_Q2_Rezerva_IZP:=Bit_0; | 33:PMM[1].AlarmPhase[3].C33_42_over80:=Word_01; |  |  | 4067:Circ[1].Tok_L1:=Real_0;
mind_bool[34]:=DI_Q2_Rezerva_ON; | mind[34]:=PMM[1].AlarmPhase[3].GlobalAlarmReg; |  |  | Read_Real(rVar:=Circ[1].Tok_L2,lo:=4068,hi:=4069); |  | 34:DI_Q2_Rezerva_ON:=Bit_0; | 34:PMM[1].AlarmPhase[3].GlobalAlarmReg:=Word_01; |  |  | 4069:Circ[1].Tok_L2:=Real_0;
mind_bool[35]:=DI_Q30_OdcByUpsB_IZP; | mind[35]:=PMM[1].Alarms; |  |  | Read_Real(rVar:=Circ[1].Tok_L3,lo:=4070,hi:=4071); |  | 35:DI_Q30_OdcByUpsB_IZP:=Bit_0; | 35:PMM[1].Alarms:=Word_01; |  |  | 4071:Circ[1].Tok_L3:=Real_0;
mind_bool[36]:=DI_Q30_OdcByUpsB_ON; | mind[36]:=PMM[2].AlarmPhase[1].C01_16_60to80; |  |  | Read_Real(rVar:=Circ[1].TokPovprecje_III,lo:=4072,hi:=4073); |  | 36:DI_Q30_OdcByUpsB_ON:=Bit_0; | 36:PMM[2].AlarmPhase[1].C01_16_60to80:=Word_01; |  |  | 4073:Circ[1].TokPovprecje_III:=Real_0;
mind_bool[37]:=DI_Q31_DovByUpsA_ON; | mind[37]:=PMM[2].AlarmPhase[1].C01_16_over80; |  |  | Read_Real(rVar:=Circutor.CosFi_III,lo:=4074,hi:=4075); |  | 37:DI_Q31_DovByUpsA_ON:=Bit_0; | 37:PMM[2].AlarmPhase[1].C01_16_over80:=Word_01; |  |  | 4075:Circutor.CosFi_III:=Real_0;
mind_bool[38]:=DI_Q32_DovByA_ON; | mind[38]:=PMM[2].AlarmPhase[1].C17_32_60to80; |  |  | Read_Real(rVar:=Circutor.DelovnaEnergija,lo:=4076,hi:=4077); |  | 38:DI_Q32_DovByA_ON:=Bit_0; | 38:PMM[2].AlarmPhase[1].C17_32_60to80:=Word_01; |  |  | 4077:Circutor.DelovnaEnergija:=Real_0;
mind_bool[39]:=DI_Q33_DovByUpsB_ON; | mind[39]:=PMM[2].AlarmPhase[1].C17_32_over80; |  |  | Read_Real(rVar:=Circutor.DelovnaMoc_III,lo:=4078,hi:=4079); |  | 39:DI_Q33_DovByUpsB_ON:=Bit_0; | 39:PMM[2].AlarmPhase[1].C17_32_over80:=Word_01; |  |  | 4079:Circutor.DelovnaMoc_III:=Real_0;
mind_bool[40]:=DI_Q34_DovByB_ON; | mind[40]:=PMM[2].AlarmPhase[1].C33_42_60to80; |  |  | Read_Real(rVar:=Circutor.DelovnaMoc_L1,lo:=4080,hi:=4081); |  | 40:DI_Q34_DovByB_ON:=Bit_0; | 40:PMM[2].AlarmPhase[1].C33_42_60to80:=Word_01; |  |  | 4081:Circutor.DelovnaMoc_L1:=Real_0;
mind_bool[41]:=DI_Q5_OdcKlima1_IZP; | mind[41]:=PMM[2].AlarmPhase[1].C33_42_over80; |  |  | Read_Real(rVar:=Circutor.DelovnaMoc_L2,lo:=4082,hi:=4083); |  | 41:DI_Q5_OdcKlima1_IZP:=Bit_0; | 41:PMM[2].AlarmPhase[1].C33_42_over80:=Word_01; |  |  | 4083:Circutor.DelovnaMoc_L2:=Real_0;
mind_bool[42]:=DI_Q5_OdcKlima1_ON; | mind[42]:=PMM[2].AlarmPhase[1].GlobalAlarmReg; |  |  | Read_Real(rVar:=Circutor.DelovnaMoc_L3,lo:=4084,hi:=4085); |  | 42:DI_Q5_OdcKlima1_ON:=Bit_0; | 42:PMM[2].AlarmPhase[1].GlobalAlarmReg:=Word_01; |  |  | 4085:Circutor.DelovnaMoc_L3:=Real_0;
mind_bool[43]:=DI_Q6_OdcKlima2_IZP; | mind[43]:=PMM[2].AlarmPhase[2].C01_16_60to80; |  |  | Read_Real(rVar:=Circutor.Frekvenca_L1,lo:=4086,hi:=4087); |  | 43:DI_Q6_OdcKlima2_IZP:=Bit_0; | 43:PMM[2].AlarmPhase[2].C01_16_60to80:=Word_01; |  |  | 4087:Circutor.Frekvenca_L1:=Real_0;
mind_bool[44]:=DI_Q6_OdcKlima2_ON; | mind[44]:=PMM[2].AlarmPhase[2].C01_16_over80; |  |  | Read_Real(rVar:=Circutor.InduktivnaEnergija,lo:=4088,hi:=4089); |  | 44:DI_Q6_OdcKlima2_ON:=Bit_0; | 44:PMM[2].AlarmPhase[2].C01_16_over80:=Word_01; |  |  | 4089:Circutor.InduktivnaEnergija:=Real_0;
mind_bool[45]:=DI_Q7_OdcKlima3_IZP; | mind[45]:=PMM[2].AlarmPhase[2].C17_32_60to80; |  |  | Read_Real(rVar:=Circutor.InduktivnaMoc_III,lo:=4090,hi:=4091); |  | 45:DI_Q7_OdcKlima3_IZP:=Bit_0; | 45:PMM[2].AlarmPhase[2].C17_32_60to80:=Word_01; |  |  | 4091:Circutor.InduktivnaMoc_III:=Real_0;
mind_bool[46]:=DI_Q7_OdcKlima3_ON; | mind[46]:=PMM[2].AlarmPhase[2].C17_32_over80; |  |  | Read_Real(rVar:=Circutor.JalovaMoc_L1,lo:=4092,hi:=4093); |  | 46:DI_Q7_OdcKlima3_ON:=Bit_0; | 46:PMM[2].AlarmPhase[2].C17_32_over80:=Word_01; |  |  | 4093:Circutor.JalovaMoc_L1:=Real_0;
mind_bool[47]:=DI_Q8_OdcKlima4_IZP; | mind[47]:=PMM[2].AlarmPhase[2].C33_42_60to80; |  |  | Read_Real(rVar:=Circutor.JalovaMoc_L2,lo:=4094,hi:=4095); |  | 47:DI_Q8_OdcKlima4_IZP:=Bit_0; | 47:PMM[2].AlarmPhase[2].C33_42_60to80:=Word_01; |  |  | 4095:Circutor.JalovaMoc_L2:=Real_0;
mind_bool[48]:=DI_Q8_OdcKlima4_ON; | mind[48]:=PMM[2].AlarmPhase[2].C33_42_over80; |  |  | Read_Real(rVar:=Circutor.JalovaMoc_L3,lo:=4096,hi:=4097); |  | 48:DI_Q8_OdcKlima4_ON:=Bit_0; | 48:PMM[2].AlarmPhase[2].C33_42_over80:=Word_01; |  |  | 4097:Circutor.JalovaMoc_L3:=Real_0;
mind_bool[49]:=DI_Q9_OdcKlima5_IZP; | mind[49]:=PMM[2].AlarmPhase[2].GlobalAlarmReg; |  |  | Read_Real(rVar:=Circutor.KapacitivnaEnergija,lo:=4098,hi:=4099); |  | 49:DI_Q9_OdcKlima5_IZP:=Bit_0; | 49:PMM[2].AlarmPhase[2].GlobalAlarmReg:=Word_01; |  |  | 4099:Circutor.KapacitivnaEnergija:=Real_0;
mind_bool[50]:=DI_Q9_OdcKlima5_ON; | mind[50]:=PMM[2].AlarmPhase[3].C01_16_60to80; |  |  | Read_Real(rVar:=Circutor.KapacitivnaMoc_III,lo:=4100,hi:=4101); |  | 50:DI_Q9_OdcKlima5_ON:=Bit_0; | 50:PMM[2].AlarmPhase[3].C01_16_60to80:=Word_01; |  |  | 4101:Circutor.KapacitivnaMoc_III:=Real_0;
mind_bool[51]:=DI_RazlitjeVodeK5K6; | mind[51]:=PMM[2].AlarmPhase[3].C01_16_over80; |  |  | Read_Real(rVar:=Circutor.MaximumDemand,lo:=4102,hi:=4103); |  | 51:DI_RazlitjeVodeK5K6:=Bit_0; | 51:PMM[2].AlarmPhase[3].C01_16_over80:=Word_01; |  |  | 4103:Circutor.MaximumDemand:=Real_0;
mind_bool[52]:=DI_UPS_Alarm; | mind[52]:=PMM[2].AlarmPhase[3].C17_32_60to80; |  |  | Read_Real(rVar:=Circutor.Napetost_L1_L2,lo:=4104,hi:=4105); |  | 52:DI_UPS_Alarm:=Bit_0; | 52:PMM[2].AlarmPhase[3].C17_32_60to80:=Word_01; |  |  | 4105:Circutor.Napetost_L1_L2:=Real_0;
mind_bool[53]:=DI_UPS_BatNacin; | mind[53]:=PMM[2].AlarmPhase[3].C17_32_over80; |  |  | Read_Real(rVar:=Circutor.Napetost_L1_N,lo:=4106,hi:=4107); |  | 53:DI_UPS_BatNacin:=Bit_0; | 53:PMM[2].AlarmPhase[3].C17_32_over80:=Word_01; |  |  | 4107:Circutor.Napetost_L1_N:=Real_0;
mind_bool[54]:=DI_UPS_Polnjenje; | mind[54]:=PMM[2].AlarmPhase[3].C33_42_60to80; |  |  | Read_Real(rVar:=Circutor.Napetost_L2_L3,lo:=4108,hi:=4109); |  | 54:DI_UPS_Polnjenje:=Bit_0; | 54:PMM[2].AlarmPhase[3].C33_42_60to80:=Word_01; |  |  | 4109:Circutor.Napetost_L2_L3:=Real_0;
mind_bool[55]:=DIN_UpsA_ERR; | mind[55]:=PMM[2].AlarmPhase[3].C33_42_over80; |  |  | Read_Real(rVar:=Circutor.Napetost_L2_N,lo:=4110,hi:=4111); |  | 55:DIN_UpsA_ERR:=Bit_0; | 55:PMM[2].AlarmPhase[3].C33_42_over80:=Word_01; |  |  | 4111:Circutor.Napetost_L2_N:=Real_0;
mind_bool[56]:=DIN_UpsA_BypassON; | mind[56]:=PMM[2].AlarmPhase[3].GlobalAlarmReg; |  |  | Read_Real(rVar:=Circutor.Napetost_L3_L1,lo:=4112,hi:=4113); |  | 56:DIN_UpsA_BypassON:=Bit_0; | 56:PMM[2].AlarmPhase[3].GlobalAlarmReg:=Word_01; |  |  | 4113:Circutor.Napetost_L3_L1:=Real_0;
mind_bool[57]:=DIN_UpsB_ERR; | mind[57]:=PMM[2].Alarms; |  |  | Read_Real(rVar:=Circutor.Napetost_L3_N,lo:=4114,hi:=4115); |  | 57:DIN_UpsB_ERR:=Bit_0; | 57:PMM[2].Alarms:=Word_01; |  |  | 4115:Circutor.Napetost_L3_N:=Real_0;
mind_bool[58]:=DIN_UpsB_BypassON; | mind[58]:=PMM[3].AlarmPhase[1].C01_16_60to80; |  |  | Read_Real(rVar:=Circutor.NavideznaMoc_III,lo:=4116,hi:=4117); |  | 58:DIN_UpsB_BypassON:=Bit_0; | 58:PMM[3].AlarmPhase[1].C01_16_60to80:=Word_01; |  |  | 4117:Circutor.NavideznaMoc_III:=Real_0;
mind_bool[59]:=DO_Klima5_Izklop; | mind[59]:=PMM[3].AlarmPhase[1].C01_16_over80; |  |  | Read_Real(rVar:=Circutor.NicelniTok,lo:=4118,hi:=4119); |  | 59:DO_Klima5_Izklop:=Bit_0; | 59:PMM[3].AlarmPhase[1].C01_16_over80:=Word_01; |  |  | 4119:Circutor.NicelniTok:=Real_0;
mind_bool[60]:=DO_Klima6_Izklop; | mind[60]:=PMM[3].AlarmPhase[1].C17_32_60to80; |  |  | Read_Real(rVar:=Circutor.PowerFactor_III,lo:=4120,hi:=4121); |  | 60:DO_Klima6_Izklop:=Bit_0; | 60:PMM[3].AlarmPhase[1].C17_32_60to80:=Word_01; |  |  | 4121:Circutor.PowerFactor_III:=Real_0;
mind_bool[61]:=ErrComCirc[1]; | mind[61]:=PMM[3].AlarmPhase[1].C17_32_over80; |  |  | Read_Real(rVar:=Circutor.PowerFactor_L1,lo:=4122,hi:=4123); |  | 61:ErrComCirc[1]:=Bit_0; | 61:PMM[3].AlarmPhase[1].C17_32_over80:=Word_01; |  |  | 4123:Circutor.PowerFactor_L1:=Real_0;
mind_bool[62]:=ErrComCirc[2]; | mind[62]:=PMM[3].AlarmPhase[1].C33_42_60to80; |  |  | Read_Real(rVar:=Circutor.PowerFactor_L2,lo:=4124,hi:=4125); |  | 62:ErrComCirc[2]:=Bit_0; | 62:PMM[3].AlarmPhase[1].C33_42_60to80:=Word_01; |  |  | 4125:Circutor.PowerFactor_L2:=Real_0;
mind_bool[63]:=ErrComCirc[3]; | mind[63]:=PMM[3].AlarmPhase[1].C33_42_over80; |  |  | Read_Real(rVar:=Circutor.PowerFactor_L3,lo:=4126,hi:=4127); |  | 63:ErrComCirc[3]:=Bit_0; | 63:PMM[3].AlarmPhase[1].C33_42_over80:=Word_01; |  |  | 4127:Circutor.PowerFactor_L3:=Real_0;
mind_bool[64]:=ErrComCirc[4]; | mind[64]:=PMM[3].AlarmPhase[1].GlobalAlarmReg; |  |  | Read_Real(rVar:=Circutor.THDI_L1,lo:=4128,hi:=4129); |  | 64:ErrComCirc[4]:=Bit_0; | 64:PMM[3].AlarmPhase[1].GlobalAlarmReg:=Word_01; |  |  | 4129:Circutor.THDI_L1:=Real_0;
mind_bool[65]:=ErrComCirc[5]; | mind[65]:=PMM[3].AlarmPhase[2].C01_16_60to80; |  |  | Read_Real(rVar:=Circutor.THDI_L2,lo:=4130,hi:=4131); |  | 65:ErrComCirc[5]:=Bit_0; | 65:PMM[3].AlarmPhase[2].C01_16_60to80:=Word_01; |  |  | 4131:Circutor.THDI_L2:=Real_0;
mind_bool[66]:=ErrComKlima[1]; | mind[66]:=PMM[3].AlarmPhase[2].C01_16_over80; |  |  | Read_Real(rVar:=Circutor.THDI_L3,lo:=4132,hi:=4133); |  | 66:ErrComKlima[1]:=Bit_0; | 66:PMM[3].AlarmPhase[2].C01_16_over80:=Word_01; |  |  | 4133:Circutor.THDI_L3:=Real_0;
mind_bool[67]:=ErrComKlima[2]; | mind[67]:=PMM[3].AlarmPhase[2].C17_32_60to80; |  |  | Read_Real(rVar:=Circutor.THDV_L1,lo:=4134,hi:=4135); |  | 67:ErrComKlima[2]:=Bit_0; | 67:PMM[3].AlarmPhase[2].C17_32_60to80:=Word_01; |  |  | 4135:Circutor.THDV_L1:=Real_0;
mind_bool[68]:=ErrComKlima[3]; | mind[68]:=PMM[3].AlarmPhase[2].C17_32_over80; |  |  | Read_Real(rVar:=Circutor.THDV_L2,lo:=4136,hi:=4137); |  | 68:ErrComKlima[3]:=Bit_0; | 68:PMM[3].AlarmPhase[2].C17_32_over80:=Word_01; |  |  | 4137:Circutor.THDV_L2:=Real_0;
mind_bool[69]:=ErrComKlima[4]; | mind[69]:=PMM[3].AlarmPhase[2].C33_42_60to80; |  |  | Read_Real(rVar:=Circutor.THDV_L3,lo:=4138,hi:=4139); |  | 69:ErrComKlima[4]:=Bit_0; | 69:PMM[3].AlarmPhase[2].C33_42_60to80:=Word_01; |  |  | 4139:Circutor.THDV_L3:=Real_0;
mind_bool[70]:=ErrComKlima[5]; | mind[70]:=PMM[3].AlarmPhase[2].C33_42_over80; |  |  | Read_Real(rVar:=Circutor.Tok_L1,lo:=4140,hi:=4141); |  | 70:ErrComKlima[5]:=Bit_0; | 70:PMM[3].AlarmPhase[2].C33_42_over80:=Word_01; |  |  | 4141:Circutor.Tok_L1:=Real_0;
mind_bool[71]:=ErrComKlima[6]; | mind[71]:=PMM[3].AlarmPhase[2].GlobalAlarmReg; |  |  | Read_Real(rVar:=Circutor.Tok_L2,lo:=4142,hi:=4143); |  | 71:ErrComKlima[6]:=Bit_0; | 71:PMM[3].AlarmPhase[2].GlobalAlarmReg:=Word_01; |  |  | 4143:Circutor.Tok_L2:=Real_0;
mind_bool[72]:=ErrCommScada; | mind[72]:=PMM[3].AlarmPhase[3].C01_16_60to80; |  |  | Read_Real(rVar:=Circutor.Tok_L3,lo:=4144,hi:=4145); |  | 72:ErrCommScada:=Bit_0; | 72:PMM[3].AlarmPhase[3].C01_16_60to80:=Word_01; |  |  | 4145:Circutor.Tok_L3:=Real_0;
mind_bool[73]:=ErrComPanelPLC; | mind[73]:=PMM[3].AlarmPhase[3].C01_16_over80; |  |  | Read_Real(rVar:=Circutor.TokPovprecje_III,lo:=4146,hi:=4147); |  | 73:ErrComPanelPLC:=Bit_0; | 73:PMM[3].AlarmPhase[3].C01_16_over80:=Word_01; |  |  | 4147:Circutor.TokPovprecje_III:=Real_0;
mind_bool[74]:=ErrComPMM[1]; | mind[74]:=PMM[3].AlarmPhase[3].C17_32_60to80; |  |  | Read_Real(rVar:=Klima[1].NastMaxTemp,lo:=4148,hi:=4149); |  | 74:ErrComPMM[1]:=Bit_0; | 74:PMM[3].AlarmPhase[3].C17_32_60to80:=Word_01; |  |  | 4149:Klima[1].NastMaxTemp:=Real_0;
mind_bool[75]:=ErrComPMM[2]; | mind[75]:=PMM[3].AlarmPhase[3].C17_32_over80; |  |  | Read_Real(rVar:=Klima[1].NastMaxVlaznost,lo:=4150,hi:=4151); |  | 75:ErrComPMM[2]:=Bit_0; | 75:PMM[3].AlarmPhase[3].C17_32_over80:=Word_01; |  |  | 4151:Klima[1].NastMaxVlaznost:=Real_0;
mind_bool[76]:=ErrComPMM[3]; | mind[76]:=PMM[3].AlarmPhase[3].C33_42_60to80; |  |  | Read_Real(rVar:=Klima[1].NastMinTemp,lo:=4152,hi:=4153); |  | 76:ErrComPMM[3]:=Bit_0; | 76:PMM[3].AlarmPhase[3].C33_42_60to80:=Word_01; |  |  | 4153:Klima[1].NastMinTemp:=Real_0;
mind_bool[77]:=ErrComPort2; | mind[77]:=PMM[3].AlarmPhase[3].C33_42_over80; |  |  | Read_Real(rVar:=Klima[1].NastMinVlaznost,lo:=4154,hi:=4155); |  | 77:ErrComPort2:=Bit_0; | 77:PMM[3].AlarmPhase[3].C33_42_over80:=Word_01; |  |  | 4155:Klima[1].NastMinVlaznost:=Real_0;
mind_bool[78]:=ErrComPort3; | mind[78]:=PMM[3].AlarmPhase[3].GlobalAlarmReg; |  |  | Read_Real(rVar:=Klima[1].NastTempProstora,lo:=4156,hi:=4157); |  | 78:ErrComPort3:=Bit_0; | 78:PMM[3].AlarmPhase[3].GlobalAlarmReg:=Word_01; |  |  | 4157:Klima[1].NastTempProstora:=Real_0;
mind_bool[79]:=ErrComPort4; | mind[79]:=PMM[3].Alarms; |  |  | Read_Real(rVar:=Klima[1].NastVlaznost,lo:=4158,hi:=4159); |  | 79:ErrComPort4:=Bit_0; | 79:PMM[3].Alarms:=Word_01; |  |  | 4159:Klima[1].NastVlaznost:=Real_0;
mind_bool[80]:=ErrComUPS[1]; | mind[80]:=UPS[1].InverterStatus; |  |  | Read_Real(rVar:=Klima[1].ObratovalneUre,lo:=4160,hi:=4161); |  | 80:ErrComUPS[1]:=Bit_0; | 80:UPS[1].InverterStatus:=Word_01; |  |  | 4161:Klima[1].ObratovalneUre:=Real_0;
mind_bool[81]:=ErrComUPS[2]; | mind[81]:=UPS[1].OutputStatus; |  |  | Read_Real(rVar:=Klima[1].TemperaturaProstora,lo:=4162,hi:=4163); |  | 81:ErrComUPS[2]:=Bit_0; | 81:UPS[1].OutputStatus:=Word_01; |  |  | 4163:Klima[1].TemperaturaProstora:=Real_0;
mind_bool[82]:=Klima[1].AlarmKompresor1; | mind[82]:=UPS[1].StatusBaterije; |  |  | Read_Real(rVar:=Klima[1].TempIzpihanegaZraka,lo:=4164,hi:=4165); |  | 82:Klima[1].AlarmKompresor1:=Bit_0; | 82:UPS[1].StatusBaterije:=Word_01; |  |  | 4165:Klima[1].TempIzpihanegaZraka:=Real_0;
mind_bool[83]:=Klima[1].AlarmKompresor2; | mind[83]:=UPS[1].SteviloIzpadovVhodneLinije; |  |  | Read_Real(rVar:=Klima[1].TempPovratneVode,lo:=4166,hi:=4167); |  | 83:Klima[1].AlarmKompresor2:=Bit_0; | 83:UPS[1].SteviloIzpadovVhodneLinije:=Word_01; |  |  | 4167:Klima[1].TempPovratneVode:=Real_0;
mind_bool[84]:=Klima[1].Deluje; | mind[84]:=UPS[1].UnitStatus; |  |  | Read_Real(rVar:=Klima[1].VlaznostProstora,lo:=4168,hi:=4169); |  | 84:Klima[1].Deluje:=Bit_0; | 84:UPS[1].UnitStatus:=Word_01; |  |  | 4169:Klima[1].VlaznostProstora:=Real_0;
mind_bool[85]:=Klima[1].EnergySaving; | mind[85]:=UPS[2].InverterStatus; |  |  | Read_Real(rVar:=Klima[1].ZunanjaTemp,lo:=4170,hi:=4171); |  | 85:Klima[1].EnergySaving:=Bit_0; | 85:UPS[2].InverterStatus:=Word_01; |  |  | 4171:Klima[1].ZunanjaTemp:=Real_0;
mind_bool[86]:=Klima[1].FaultyEPROM; | mind[86]:=UPS[2].OutputStatus; |  |  | Read_Real(rVar:=Klima[2].NastMaxTemp,lo:=4172,hi:=4173); |  | 86:Klima[1].FaultyEPROM:=Bit_0; | 86:UPS[2].OutputStatus:=Word_01; |  |  | 4173:Klima[2].NastMaxTemp:=Real_0;
mind_bool[87]:=Klima[1].FenThermalCutout; | mind[87]:=UPS[2].StatusBaterije; |  |  | Read_Real(rVar:=Klima[2].NastMaxVlaznost,lo:=4174,hi:=4175); |  | 87:Klima[1].FenThermalCutout:=Bit_0; | 87:UPS[2].StatusBaterije:=Word_01; |  |  | 4175:Klima[2].NastMaxVlaznost:=Real_0;
mind_bool[88]:=Klima[1].GeneralAlarm; | mind[88]:=UPS[2].SteviloIzpadovVhodneLinije; |  |  | Read_Real(rVar:=Klima[2].NastMinTemp,lo:=4176,hi:=4177); |  | 88:Klima[1].GeneralAlarm:=Bit_0; | 88:UPS[2].SteviloIzpadovVhodneLinije:=Word_01; |  |  | 4177:Klima[2].NastMinTemp:=Real_0;
mind_bool[89]:=Klima[1].Kompresor1naMejiObrUr; | mind[89]:=UPS[2].UnitStatus; |  |  | Read_Real(rVar:=Klima[2].NastMinVlaznost,lo:=4178,hi:=4179); |  | 89:Klima[1].Kompresor1naMejiObrUr:=Bit_0; | 89:UPS[2].UnitStatus:=Word_01; |  |  | 4179:Klima[2].NastMinVlaznost:=Real_0;
mind_bool[90]:=Klima[1].Kompresor2naMejiObrUr; | mind[90]:=UserCurrentLevel; |  |  | Read_Real(rVar:=Klima[2].NastTempProstora,lo:=4180,hi:=4181); |  | 90:Klima[1].Kompresor2naMejiObrUr:=Bit_0; | 90:UserCurrentLevel:=Byte_0; |  |  | 4181:Klima[2].NastTempProstora:=Real_0;
mind_bool[91]:=Klima[1].Napaka; | mind[91]:=ErrorComCirc[1].Code[10]; |  |  | Read_Real(rVar:=Klima[2].NastVlaznost,lo:=4182,hi:=4183); |  | 91:Klima[1].Napaka:=Bit_0; | 91:ErrorComCirc[1].Code[10]:=Byte_0; |  |  | 4183:Klima[2].NastVlaznost:=Real_0;
mind_bool[92]:=Klima[1].NapakaPriPretokuZraka; | mind[92]:=ErrorComCirc[1].Code[11]; |  |  | Read_Real(rVar:=Klima[2].ObratovalneUre,lo:=4184,hi:=4185); |  | 92:Klima[1].NapakaPriPretokuZraka:=Bit_0; | 92:ErrorComCirc[1].Code[11]:=Byte_0; |  |  | 4185:Klima[2].ObratovalneUre:=Real_0;
mind_bool[93]:=Klima[1].NapakaSenzorPovratVode; | mind[93]:=ErrorComCirc[1].Code[12]; |  |  | Read_Real(rVar:=Klima[2].TemperaturaProstora,lo:=4186,hi:=4187); |  | 93:Klima[1].NapakaSenzorPovratVode:=Bit_0; | 93:ErrorComCirc[1].Code[12]:=Byte_0; |  |  | 4187:Klima[2].TemperaturaProstora:=Real_0;
mind_bool[94]:=Klima[1].NapakaSenzorTempIzpiha; | mind[94]:=ErrorComCirc[1].Code[13]; |  |  | Read_Real(rVar:=Klima[2].TempIzpihanegaZraka,lo:=4188,hi:=4189); |  | 94:Klima[1].NapakaSenzorTempIzpiha:=Bit_0; | 94:ErrorComCirc[1].Code[13]:=Byte_0; |  |  | 4189:Klima[2].TempIzpihanegaZraka:=Real_0;
mind_bool[95]:=Klima[1].NapakaSenzorTempProstora; | mind[95]:=ErrorComCirc[1].Code[14]; |  |  | Read_Real(rVar:=Klima[2].TempPovratneVode,lo:=4190,hi:=4191); |  | 95:Klima[1].NapakaSenzorTempProstora:=Bit_0; | 95:ErrorComCirc[1].Code[14]:=Byte_0; |  |  | 4191:Klima[2].TempPovratneVode:=Real_0;
mind_bool[96]:=Klima[1].NapakaSenzorVlaznosti; | mind[96]:=ErrorComCirc[1].Code[15]; |  |  | Read_Real(rVar:=Klima[2].VlaznostProstora,lo:=4192,hi:=4193); |  | 96:Klima[1].NapakaSenzorVlaznosti:=Bit_0; | 96:ErrorComCirc[1].Code[15]:=Byte_0; |  |  | 4193:Klima[2].VlaznostProstora:=Real_0;
mind_bool[97]:=Klima[1].NapakaSenzorZunanjeTemp; | mind[97]:=ErrorComCirc[1].Code[1]; |  |  | Read_Real(rVar:=Klima[2].ZunanjaTemp,lo:=4194,hi:=4195); |  | 97:Klima[1].NapakaSenzorZunanjeTemp:=Bit_0; | 97:ErrorComCirc[1].Code[1]:=Byte_0; |  |  | 4195:Klima[2].ZunanjaTemp:=Real_0;
mind_bool[98]:=Klima[1].NiTokaVVlazilcu; | mind[98]:=ErrorComCirc[1].Code[2]; |  |  | Read_Real(rVar:=PMM[1].ActivePowerPhaseA_kW,lo:=4196,hi:=4197); |  | 98:Klima[1].NiTokaVVlazilcu:=Bit_0; | 98:ErrorComCirc[1].Code[2]:=Byte_0; |  |  | 4197:PMM[1].ActivePowerPhaseA_kW:=Real_0;
mind_bool[99]:=Klima[1].NiVodeVVlazilcu; | mind[99]:=ErrorComCirc[1].Code[3]; |  |  | Read_Real(rVar:=PMM[1].ActivePowerPhaseB_kW,lo:=4198,hi:=4199); |  | 99:Klima[1].NiVodeVVlazilcu:=Bit_0; | 99:ErrorComCirc[1].Code[3]:=Byte_0; |  |  | 4199:PMM[1].ActivePowerPhaseB_kW:=Real_0;
mind_bool[100]:=Klima[1].NizekPritiskKompresor1; | mind[100]:=ErrorComCirc[1].Code[4]; |  |  | Read_Real(rVar:=PMM[1].ActivePowerPhaseC_kW,lo:=4200,hi:=4201); |  | 100:Klima[1].NizekPritiskKompresor1:=Bit_0; | 100:ErrorComCirc[1].Code[4]:=Byte_0; |  |  | 4201:PMM[1].ActivePowerPhaseC_kW:=Real_0;
mind_bool[101]:=Klima[1].NizekPritiskKompresor2; | mind[101]:=ErrorComCirc[1].Code[5]; |  |  | Read_Real(rVar:=PMM[1].AverageCurrent_A,lo:=4202,hi:=4203); |  | 101:Klima[1].NizekPritiskKompresor2:=Bit_0; | 101:ErrorComCirc[1].Code[5]:=Byte_0; |  |  | 4203:PMM[1].AverageCurrent_A:=Real_0;
mind_bool[102]:=Klima[1].NizkaTempPovratneVode; | mind[102]:=ErrorComCirc[1].Code[6]; |  |  | Read_Real(rVar:=PMM[1].AveragePhaseToNeutral_V,lo:=4204,hi:=4205); |  | 102:Klima[1].NizkaTempPovratneVode:=Bit_0; | 102:ErrorComCirc[1].Code[6]:=Byte_0; |  |  | 4205:PMM[1].AveragePhaseToNeutral_V:=Real_0;
mind_bool[103]:=Klima[1].NizkaTempVProstoru; | mind[103]:=ErrorComCirc[1].Code[7]; |  |  | Read_Real(rVar:=PMM[1].AveragePhaseToPhase_V,lo:=4206,hi:=4207); |  | 103:Klima[1].NizkaTempVProstoru:=Bit_0; | 103:ErrorComCirc[1].Code[7]:=Byte_0; |  |  | 4207:PMM[1].AveragePhaseToPhase_V:=Real_0;
mind_bool[104]:=Klima[1].NizkaVlaznost; | mind[104]:=ErrorComCirc[1].Code[8]; |  |  | Read_Real(rVar:=PMM[1].CurrentInPhaseA_A,lo:=4208,hi:=4209); |  | 104:Klima[1].NizkaVlaznost:=Bit_0; | 104:ErrorComCirc[1].Code[8]:=Byte_0; |  |  | 4209:PMM[1].CurrentInPhaseA_A:=Real_0;
mind_bool[105]:=Klima[1].OnOffEnablingBySupervisor; | mind[105]:=ErrorComCirc[1].Code[9]; |  |  | Read_Real(rVar:=PMM[1].CurrentInPhaseB_A,lo:=4210,hi:=4211); |  | 105:Klima[1].OnOffEnablingBySupervisor:=Bit_0; | 105:ErrorComCirc[1].Code[9]:=Byte_0; |  |  | 4211:PMM[1].CurrentInPhaseB_A:=Real_0;
mind_bool[106]:=Klima[1].PozarniAlarm; | mind[106]:=ErrorComCirc[1].Status; |  |  | Read_Real(rVar:=PMM[1].CurrentInPhaseC_A,lo:=4212,hi:=4213); |  | 106:Klima[1].PozarniAlarm:=Bit_0; | 106:ErrorComCirc[1].Status:=Word_01; |  |  | 4213:PMM[1].CurrentInPhaseC_A:=Real_0;
mind_bool[107]:=Klima[1].Razvlazevanje; | mind[107]:=ErrorComCirc[2].Code[10]; |  |  | Read_Real(rVar:=PMM[1].EnergyConsumed_kWh,lo:=4214,hi:=4215); |  | 107:Klima[1].Razvlazevanje:=Bit_0; | 107:ErrorComCirc[2].Code[10]:=Byte_0; |  |  | 4215:PMM[1].EnergyConsumed_kWh:=Real_0;
mind_bool[108]:=Klima[1].RemoteOFFtoOutput; | mind[108]:=ErrorComCirc[2].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Frequency_Hz,lo:=4216,hi:=4217); |  | 108:Klima[1].RemoteOFFtoOutput:=Bit_0; | 108:ErrorComCirc[2].Code[11]:=Byte_0; |  |  | 4217:PMM[1].Frequency_Hz:=Real_0;
mind_bool[109]:=Klima[1].RemoteOnOff; | mind[109]:=ErrorComCirc[2].Code[12]; |  |  | Read_Real(rVar:=PMM[1].NeutralCurrent_A,lo:=4218,hi:=4219); |  | 109:Klima[1].RemoteOnOff:=Bit_0; | 109:ErrorComCirc[2].Code[12]:=Byte_0; |  |  | 4219:PMM[1].NeutralCurrent_A:=Real_0;
mind_bool[110]:=Klima[1].RocniIzklop; | mind[110]:=ErrorComCirc[2].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[10],lo:=4220,hi:=4221); |  | 110:Klima[1].RocniIzklop:=Bit_0; | 110:ErrorComCirc[2].Code[13]:=Byte_0; |  |  | 4221:PMM[1].Phase[1].Current[10]:=Real_0;
mind_bool[111]:=Klima[1].SenzorjiStatus; | mind[111]:=ErrorComCirc[2].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[11],lo:=4222,hi:=4223); |  | 111:Klima[1].SenzorjiStatus:=Bit_0; | 111:ErrorComCirc[2].Code[14]:=Byte_0; |  |  | 4223:PMM[1].Phase[1].Current[11]:=Real_0;
mind_bool[112]:=Klima[1].StoppedByAlarms; | mind[112]:=ErrorComCirc[2].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[12],lo:=4224,hi:=4225); |  | 112:Klima[1].StoppedByAlarms:=Bit_0; | 112:ErrorComCirc[2].Code[15]:=Byte_0; |  |  | 4225:PMM[1].Phase[1].Current[12]:=Real_0;
mind_bool[113]:=Klima[1].ThermalCutoutHeater1; | mind[113]:=ErrorComCirc[2].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[13],lo:=4226,hi:=4227); |  | 113:Klima[1].ThermalCutoutHeater1:=Bit_0; | 113:ErrorComCirc[2].Code[1]:=Byte_0; |  |  | 4227:PMM[1].Phase[1].Current[13]:=Real_0;
mind_bool[114]:=Klima[1].ThermalCutoutHeater2; | mind[114]:=ErrorComCirc[2].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[14],lo:=4228,hi:=4229); |  | 114:Klima[1].ThermalCutoutHeater2:=Bit_0; | 114:ErrorComCirc[2].Code[2]:=Byte_0; |  |  | 4229:PMM[1].Phase[1].Current[14]:=Real_0;
mind_bool[115]:=Klima[1].UnitOnOff; | mind[115]:=ErrorComCirc[2].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[15],lo:=4230,hi:=4231); |  | 115:Klima[1].UnitOnOff:=Bit_0; | 115:ErrorComCirc[2].Code[3]:=Byte_0; |  |  | 4231:PMM[1].Phase[1].Current[15]:=Real_0;
mind_bool[116]:=Klima[1].VentilatorNaMejiObrUr; | mind[116]:=ErrorComCirc[2].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[16],lo:=4232,hi:=4233); |  | 116:Klima[1].VentilatorNaMejiObrUr:=Bit_0; | 116:ErrorComCirc[2].Code[4]:=Byte_0; |  |  | 4233:PMM[1].Phase[1].Current[16]:=Real_0;
mind_bool[117]:=Klima[1].VentilGretjeOdpiranje; | mind[117]:=ErrorComCirc[2].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[17],lo:=4234,hi:=4235); |  | 117:Klima[1].VentilGretjeOdpiranje:=Bit_0; | 117:ErrorComCirc[2].Code[5]:=Byte_0; |  |  | 4235:PMM[1].Phase[1].Current[17]:=Real_0;
mind_bool[118]:=Klima[1].VentilGretjeZapiranje; | mind[118]:=ErrorComCirc[2].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[18],lo:=4236,hi:=4237); |  | 118:Klima[1].VentilGretjeZapiranje:=Bit_0; | 118:ErrorComCirc[2].Code[6]:=Byte_0; |  |  | 4237:PMM[1].Phase[1].Current[18]:=Real_0;
mind_bool[119]:=Klima[1].VentilHlajenjeOdpiranje; | mind[119]:=ErrorComCirc[2].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[19],lo:=4238,hi:=4239); |  | 119:Klima[1].VentilHlajenjeOdpiranje:=Bit_0; | 119:ErrorComCirc[2].Code[7]:=Byte_0; |  |  | 4239:PMM[1].Phase[1].Current[19]:=Real_0;
mind_bool[120]:=Klima[1].VentilHlajenjeZapiranje; | mind[120]:=ErrorComCirc[2].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[1],lo:=4240,hi:=4241); |  | 120:Klima[1].VentilHlajenjeZapiranje:=Bit_0; | 120:ErrorComCirc[2].Code[8]:=Byte_0; |  |  | 4241:PMM[1].Phase[1].Current[1]:=Real_0;
mind_bool[121]:=Klima[1].VisokaTempPovratneVode; | mind[121]:=ErrorComCirc[2].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[20],lo:=4242,hi:=4243); |  | 121:Klima[1].VisokaTempPovratneVode:=Bit_0; | 121:ErrorComCirc[2].Code[9]:=Byte_0; |  |  | 4243:PMM[1].Phase[1].Current[20]:=Real_0;
mind_bool[122]:=Klima[1].VisokaTempVProstoru; | mind[122]:=ErrorComCirc[2].Status; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[21],lo:=4244,hi:=4245); |  | 122:Klima[1].VisokaTempVProstoru:=Bit_0; | 122:ErrorComCirc[2].Status:=Word_01; |  |  | 4245:PMM[1].Phase[1].Current[21]:=Real_0;
mind_bool[123]:=Klima[1].VisokaVlaznost; | mind[123]:=ErrorComCirc[3].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[22],lo:=4246,hi:=4247); |  | 123:Klima[1].VisokaVlaznost:=Bit_0; | 123:ErrorComCirc[3].Code[10]:=Byte_0; |  |  | 4247:PMM[1].Phase[1].Current[22]:=Real_0;
mind_bool[124]:=Klima[1].VisokTokVVlazilcu; | mind[124]:=ErrorComCirc[3].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[23],lo:=4248,hi:=4249); |  | 124:Klima[1].VisokTokVVlazilcu:=Bit_0; | 124:ErrorComCirc[3].Code[11]:=Byte_0; |  |  | 4249:PMM[1].Phase[1].Current[23]:=Real_0;
mind_bool[125]:=Klima[1].Vlazenje; | mind[125]:=ErrorComCirc[3].Code[12]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[24],lo:=4250,hi:=4251); |  | 125:Klima[1].Vlazenje:=Bit_0; | 125:ErrorComCirc[3].Code[12]:=Byte_0; |  |  | 4251:PMM[1].Phase[1].Current[24]:=Real_0;
mind_bool[126]:=Klima[1].ZamasenFilter; | mind[126]:=ErrorComCirc[3].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[25],lo:=4252,hi:=4253); |  | 126:Klima[1].ZamasenFilter:=Bit_0; | 126:ErrorComCirc[3].Code[13]:=Byte_0; |  |  | 4253:PMM[1].Phase[1].Current[25]:=Real_0;
mind_bool[127]:=Klima[2].AlarmKompresor1; | mind[127]:=ErrorComCirc[3].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[26],lo:=4254,hi:=4255); |  | 127:Klima[2].AlarmKompresor1:=Bit_0; | 127:ErrorComCirc[3].Code[14]:=Byte_0; |  |  | 4255:PMM[1].Phase[1].Current[26]:=Real_0;
mind_bool[128]:=Klima[2].AlarmKompresor2; | mind[128]:=ErrorComCirc[3].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[27],lo:=4256,hi:=4257); |  | 128:Klima[2].AlarmKompresor2:=Bit_0; | 128:ErrorComCirc[3].Code[15]:=Byte_0; |  |  | 4257:PMM[1].Phase[1].Current[27]:=Real_0;
mind_bool[129]:=Klima[2].Deluje; | mind[129]:=ErrorComCirc[3].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[28],lo:=4258,hi:=4259); |  | 129:Klima[2].Deluje:=Bit_0; | 129:ErrorComCirc[3].Code[1]:=Byte_0; |  |  | 4259:PMM[1].Phase[1].Current[28]:=Real_0;
mind_bool[130]:=Klima[2].EnergySaving; | mind[130]:=ErrorComCirc[3].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[29],lo:=4260,hi:=4261); |  | 130:Klima[2].EnergySaving:=Bit_0; | 130:ErrorComCirc[3].Code[2]:=Byte_0; |  |  | 4261:PMM[1].Phase[1].Current[29]:=Real_0;
mind_bool[131]:=Klima[2].FaultyEPROM; | mind[131]:=ErrorComCirc[3].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[2],lo:=4262,hi:=4263); |  | 131:Klima[2].FaultyEPROM:=Bit_0; | 131:ErrorComCirc[3].Code[3]:=Byte_0; |  |  | 4263:PMM[1].Phase[1].Current[2]:=Real_0;
mind_bool[132]:=Klima[2].FenThermalCutout; | mind[132]:=ErrorComCirc[3].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[30],lo:=4264,hi:=4265); |  | 132:Klima[2].FenThermalCutout:=Bit_0; | 132:ErrorComCirc[3].Code[4]:=Byte_0; |  |  | 4265:PMM[1].Phase[1].Current[30]:=Real_0;
mind_bool[133]:=Klima[2].GeneralAlarm; | mind[133]:=ErrorComCirc[3].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[31],lo:=4266,hi:=4267); |  | 133:Klima[2].GeneralAlarm:=Bit_0; | 133:ErrorComCirc[3].Code[5]:=Byte_0; |  |  | 4267:PMM[1].Phase[1].Current[31]:=Real_0;
mind_bool[134]:=Klima[2].Kompresor1naMejiObrUr; | mind[134]:=ErrorComCirc[3].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[32],lo:=4268,hi:=4269); |  | 134:Klima[2].Kompresor1naMejiObrUr:=Bit_0; | 134:ErrorComCirc[3].Code[6]:=Byte_0; |  |  | 4269:PMM[1].Phase[1].Current[32]:=Real_0;
mind_bool[135]:=Klima[2].Kompresor2naMejiObrUr; | mind[135]:=ErrorComCirc[3].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[33],lo:=4270,hi:=4271); |  | 135:Klima[2].Kompresor2naMejiObrUr:=Bit_0; | 135:ErrorComCirc[3].Code[7]:=Byte_0; |  |  | 4271:PMM[1].Phase[1].Current[33]:=Real_0;
mind_bool[136]:=Klima[2].Napaka; | mind[136]:=ErrorComCirc[3].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[34],lo:=4272,hi:=4273); |  | 136:Klima[2].Napaka:=Bit_0; | 136:ErrorComCirc[3].Code[8]:=Byte_0; |  |  | 4273:PMM[1].Phase[1].Current[34]:=Real_0;
mind_bool[137]:=Klima[2].NapakaPriPretokuZraka; | mind[137]:=ErrorComCirc[3].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[35],lo:=4274,hi:=4275); |  | 137:Klima[2].NapakaPriPretokuZraka:=Bit_0; | 137:ErrorComCirc[3].Code[9]:=Byte_0; |  |  | 4275:PMM[1].Phase[1].Current[35]:=Real_0;
mind_bool[138]:=Klima[2].NapakaSenzorPovratVode; | mind[138]:=ErrorComCirc[3].Status; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[36],lo:=4276,hi:=4277); |  | 138:Klima[2].NapakaSenzorPovratVode:=Bit_0; | 138:ErrorComCirc[3].Status:=Word_01; |  |  | 4277:PMM[1].Phase[1].Current[36]:=Real_0;
mind_bool[139]:=Klima[2].NapakaSenzorTempIzpiha; | mind[139]:=ErrorComCirc[4].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[37],lo:=4278,hi:=4279); |  | 139:Klima[2].NapakaSenzorTempIzpiha:=Bit_0; | 139:ErrorComCirc[4].Code[10]:=Byte_0; |  |  | 4279:PMM[1].Phase[1].Current[37]:=Real_0;
mind_bool[140]:=Klima[2].NapakaSenzorTempProstora; | mind[140]:=ErrorComCirc[4].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[38],lo:=4280,hi:=4281); |  | 140:Klima[2].NapakaSenzorTempProstora:=Bit_0; | 140:ErrorComCirc[4].Code[11]:=Byte_0; |  |  | 4281:PMM[1].Phase[1].Current[38]:=Real_0;
mind_bool[141]:=Klima[2].NapakaSenzorVlaznosti; | mind[141]:=ErrorComCirc[4].Code[12]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[39],lo:=4282,hi:=4283); |  | 141:Klima[2].NapakaSenzorVlaznosti:=Bit_0; | 141:ErrorComCirc[4].Code[12]:=Byte_0; |  |  | 4283:PMM[1].Phase[1].Current[39]:=Real_0;
mind_bool[142]:=Klima[2].NapakaSenzorZunanjeTemp; | mind[142]:=ErrorComCirc[4].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[3],lo:=4284,hi:=4285); |  | 142:Klima[2].NapakaSenzorZunanjeTemp:=Bit_0; | 142:ErrorComCirc[4].Code[13]:=Byte_0; |  |  | 4285:PMM[1].Phase[1].Current[3]:=Real_0;
mind_bool[143]:=Klima[2].NiTokaVVlazilcu; | mind[143]:=ErrorComCirc[4].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[40],lo:=4286,hi:=4287); |  | 143:Klima[2].NiTokaVVlazilcu:=Bit_0; | 143:ErrorComCirc[4].Code[14]:=Byte_0; |  |  | 4287:PMM[1].Phase[1].Current[40]:=Real_0;
mind_bool[144]:=Klima[2].NiVodeVVlazilcu; | mind[144]:=ErrorComCirc[4].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[41],lo:=4288,hi:=4289); |  | 144:Klima[2].NiVodeVVlazilcu:=Bit_0; | 144:ErrorComCirc[4].Code[15]:=Byte_0; |  |  | 4289:PMM[1].Phase[1].Current[41]:=Real_0;
mind_bool[145]:=Klima[2].NizekPritiskKompresor1; | mind[145]:=ErrorComCirc[4].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[42],lo:=4290,hi:=4291); |  | 145:Klima[2].NizekPritiskKompresor1:=Bit_0; | 145:ErrorComCirc[4].Code[1]:=Byte_0; |  |  | 4291:PMM[1].Phase[1].Current[42]:=Real_0;
mind_bool[146]:=Klima[2].NizekPritiskKompresor2; | mind[146]:=ErrorComCirc[4].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[4],lo:=4292,hi:=4293); |  | 146:Klima[2].NizekPritiskKompresor2:=Bit_0; | 146:ErrorComCirc[4].Code[2]:=Byte_0; |  |  | 4293:PMM[1].Phase[1].Current[4]:=Real_0;
mind_bool[147]:=Klima[2].NizkaTempPovratneVode; | mind[147]:=ErrorComCirc[4].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[5],lo:=4294,hi:=4295); |  | 147:Klima[2].NizkaTempPovratneVode:=Bit_0; | 147:ErrorComCirc[4].Code[3]:=Byte_0; |  |  | 4295:PMM[1].Phase[1].Current[5]:=Real_0;
mind_bool[148]:=Klima[2].NizkaTempVProstoru; | mind[148]:=ErrorComCirc[4].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[6],lo:=4296,hi:=4297); |  | 148:Klima[2].NizkaTempVProstoru:=Bit_0; | 148:ErrorComCirc[4].Code[4]:=Byte_0; |  |  | 4297:PMM[1].Phase[1].Current[6]:=Real_0;
mind_bool[149]:=Klima[2].NizkaVlaznost; | mind[149]:=ErrorComCirc[4].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[7],lo:=4298,hi:=4299); |  | 149:Klima[2].NizkaVlaznost:=Bit_0; | 149:ErrorComCirc[4].Code[5]:=Byte_0; |  |  | 4299:PMM[1].Phase[1].Current[7]:=Real_0;
mind_bool[150]:=Klima[2].OnOffEnablingBySupervisor; | mind[150]:=ErrorComCirc[4].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[8],lo:=4300,hi:=4301); |  | 150:Klima[2].OnOffEnablingBySupervisor:=Bit_0; | 150:ErrorComCirc[4].Code[6]:=Byte_0; |  |  | 4301:PMM[1].Phase[1].Current[8]:=Real_0;
mind_bool[151]:=Klima[2].PozarniAlarm; | mind[151]:=ErrorComCirc[4].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[9],lo:=4302,hi:=4303); |  | 151:Klima[2].PozarniAlarm:=Bit_0; | 151:ErrorComCirc[4].Code[7]:=Byte_0; |  |  | 4303:PMM[1].Phase[1].Current[9]:=Real_0;
mind_bool[152]:=Klima[2].Razvlazevanje; | mind[152]:=ErrorComCirc[4].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[10],lo:=4304,hi:=4305); |  | 152:Klima[2].Razvlazevanje:=Bit_0; | 152:ErrorComCirc[4].Code[8]:=Byte_0; |  |  | 4305:PMM[1].Phase[2].Current[10]:=Real_0;
mind_bool[153]:=Klima[2].RemoteOFFtoOutput; | mind[153]:=ErrorComCirc[4].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[11],lo:=4306,hi:=4307); |  | 153:Klima[2].RemoteOFFtoOutput:=Bit_0; | 153:ErrorComCirc[4].Code[9]:=Byte_0; |  |  | 4307:PMM[1].Phase[2].Current[11]:=Real_0;
mind_bool[154]:=Klima[2].RemoteOnOff; | mind[154]:=ErrorComCirc[4].Status; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[12],lo:=4308,hi:=4309); |  | 154:Klima[2].RemoteOnOff:=Bit_0; | 154:ErrorComCirc[4].Status:=Word_01; |  |  | 4309:PMM[1].Phase[2].Current[12]:=Real_0;
mind_bool[155]:=Klima[2].RocniIzklop; | mind[155]:=ErrorComCirc[5].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[13],lo:=4310,hi:=4311); |  | 155:Klima[2].RocniIzklop:=Bit_0; | 155:ErrorComCirc[5].Code[10]:=Byte_0; |  |  | 4311:PMM[1].Phase[2].Current[13]:=Real_0;
mind_bool[156]:=Klima[2].SenzorjiStatus; | mind[156]:=ErrorComCirc[5].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[14],lo:=4312,hi:=4313); |  | 156:Klima[2].SenzorjiStatus:=Bit_0; | 156:ErrorComCirc[5].Code[11]:=Byte_0; |  |  | 4313:PMM[1].Phase[2].Current[14]:=Real_0;
mind_bool[157]:=Klima[2].StoppedByAlarms; | mind[157]:=ErrorComCirc[5].Code[12]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[15],lo:=4314,hi:=4315); |  | 157:Klima[2].StoppedByAlarms:=Bit_0; | 157:ErrorComCirc[5].Code[12]:=Byte_0; |  |  | 4315:PMM[1].Phase[2].Current[15]:=Real_0;
mind_bool[158]:=Klima[2].ThermalCutoutHeater1; | mind[158]:=ErrorComCirc[5].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[16],lo:=4316,hi:=4317); |  | 158:Klima[2].ThermalCutoutHeater1:=Bit_0; | 158:ErrorComCirc[5].Code[13]:=Byte_0; |  |  | 4317:PMM[1].Phase[2].Current[16]:=Real_0;
mind_bool[159]:=Klima[2].ThermalCutoutHeater2; | mind[159]:=ErrorComCirc[5].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[17],lo:=4318,hi:=4319); |  | 159:Klima[2].ThermalCutoutHeater2:=Bit_0; | 159:ErrorComCirc[5].Code[14]:=Byte_0; |  |  | 4319:PMM[1].Phase[2].Current[17]:=Real_0;
mind_bool[160]:=Klima[2].UnitOnOff; | mind[160]:=ErrorComCirc[5].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[18],lo:=4320,hi:=4321); |  | 160:Klima[2].UnitOnOff:=Bit_0; | 160:ErrorComCirc[5].Code[15]:=Byte_0; |  |  | 4321:PMM[1].Phase[2].Current[18]:=Real_0;
mind_bool[161]:=Klima[2].VentilatorNaMejiObrUr; | mind[161]:=ErrorComCirc[5].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[19],lo:=4322,hi:=4323); |  | 161:Klima[2].VentilatorNaMejiObrUr:=Bit_0; | 161:ErrorComCirc[5].Code[1]:=Byte_0; |  |  | 4323:PMM[1].Phase[2].Current[19]:=Real_0;
mind_bool[162]:=Klima[2].VentilGretjeOdpiranje; | mind[162]:=ErrorComCirc[5].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[1],lo:=4324,hi:=4325); |  | 162:Klima[2].VentilGretjeOdpiranje:=Bit_0; | 162:ErrorComCirc[5].Code[2]:=Byte_0; |  |  | 4325:PMM[1].Phase[2].Current[1]:=Real_0;
mind_bool[163]:=Klima[2].VentilGretjeZapiranje; | mind[163]:=ErrorComCirc[5].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[20],lo:=4326,hi:=4327); |  | 163:Klima[2].VentilGretjeZapiranje:=Bit_0; | 163:ErrorComCirc[5].Code[3]:=Byte_0; |  |  | 4327:PMM[1].Phase[2].Current[20]:=Real_0;
mind_bool[164]:=Klima[2].VentilHlajenjeOdpiranje; | mind[164]:=ErrorComCirc[5].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[21],lo:=4328,hi:=4329); |  | 164:Klima[2].VentilHlajenjeOdpiranje:=Bit_0; | 164:ErrorComCirc[5].Code[4]:=Byte_0; |  |  | 4329:PMM[1].Phase[2].Current[21]:=Real_0;
mind_bool[165]:=Klima[2].VentilHlajenjeZapiranje; | mind[165]:=ErrorComCirc[5].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[22],lo:=4330,hi:=4331); |  | 165:Klima[2].VentilHlajenjeZapiranje:=Bit_0; | 165:ErrorComCirc[5].Code[5]:=Byte_0; |  |  | 4331:PMM[1].Phase[2].Current[22]:=Real_0;
mind_bool[166]:=Klima[2].VisokaTempPovratneVode; | mind[166]:=ErrorComCirc[5].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[23],lo:=4332,hi:=4333); |  | 166:Klima[2].VisokaTempPovratneVode:=Bit_0; | 166:ErrorComCirc[5].Code[6]:=Byte_0; |  |  | 4333:PMM[1].Phase[2].Current[23]:=Real_0;
mind_bool[167]:=Klima[2].VisokaTempVProstoru; | mind[167]:=ErrorComCirc[5].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[24],lo:=4334,hi:=4335); |  | 167:Klima[2].VisokaTempVProstoru:=Bit_0; | 167:ErrorComCirc[5].Code[7]:=Byte_0; |  |  | 4335:PMM[1].Phase[2].Current[24]:=Real_0;
mind_bool[168]:=Klima[2].VisokaVlaznost; | mind[168]:=ErrorComCirc[5].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[25],lo:=4336,hi:=4337); |  | 168:Klima[2].VisokaVlaznost:=Bit_0; | 168:ErrorComCirc[5].Code[8]:=Byte_0; |  |  | 4337:PMM[1].Phase[2].Current[25]:=Real_0;
mind_bool[169]:=Klima[2].VisokTokVVlazilcu; | mind[169]:=ErrorComCirc[5].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[26],lo:=4338,hi:=4339); |  | 169:Klima[2].VisokTokVVlazilcu:=Bit_0; | 169:ErrorComCirc[5].Code[9]:=Byte_0; |  |  | 4339:PMM[1].Phase[2].Current[26]:=Real_0;
mind_bool[170]:=Klima[2].Vlazenje; | mind[170]:=ErrorComCirc[5].Status; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[27],lo:=4340,hi:=4341); |  | 170:Klima[2].Vlazenje:=Bit_0; | 170:ErrorComCirc[5].Status:=Word_01; |  |  | 4341:PMM[1].Phase[2].Current[27]:=Real_0;
mind_bool[171]:=Klima[2].ZamasenFilter; | mind[171]:=ErrorComKlima[1].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[28],lo:=4342,hi:=4343); |  | 171:Klima[2].ZamasenFilter:=Bit_0; | 171:ErrorComKlima[1].Code[10]:=Byte_0; |  |  | 4343:PMM[1].Phase[2].Current[28]:=Real_0;
mind_bool[172]:=KlimeNaCas; | mind[172]:=ErrorComKlima[1].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[29],lo:=4344,hi:=4345); |  | 172:KlimeNaCas:=Bit_0; | 172:ErrorComKlima[1].Code[11]:=Byte_0; |  |  | 4345:PMM[1].Phase[2].Current[29]:=Real_0;
mind_bool[173]:=NapakaSenzorTemp[1]; | mind[173]:=ErrorComKlima[1].Code[12]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[2],lo:=4346,hi:=4347); |  | 173:NapakaSenzorTemp[1]:=Bit_0; | 173:ErrorComKlima[1].Code[12]:=Byte_0; |  |  | 4347:PMM[1].Phase[2].Current[2]:=Real_0;
mind_bool[174]:=NapakaSenzorTemp[2]; | mind[174]:=ErrorComKlima[1].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[30],lo:=4348,hi:=4349); |  | 174:NapakaSenzorTemp[2]:=Bit_0; | 174:ErrorComKlima[1].Code[13]:=Byte_0; |  |  | 4349:PMM[1].Phase[2].Current[30]:=Real_0;
mind_bool[175]:=NapakaSenzorVlaga[1]; | mind[175]:=ErrorComKlima[1].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[31],lo:=4350,hi:=4351); |  | 175:NapakaSenzorVlaga[1]:=Bit_0; | 175:ErrorComKlima[1].Code[14]:=Byte_0; |  |  | 4351:PMM[1].Phase[2].Current[31]:=Real_0;
mind_bool[176]:=NapakaSenzorVlaga[2]; | mind[176]:=ErrorComKlima[1].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[32],lo:=4352,hi:=4353); |  | 176:NapakaSenzorVlaga[2]:=Bit_0; | 176:ErrorComKlima[1].Code[15]:=Byte_0; |  |  | 4353:PMM[1].Phase[2].Current[32]:=Real_0;
mind_bool[177]:=PMM1OverCurrentBetw[1]; | mind[177]:=ErrorComKlima[1].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[33],lo:=4354,hi:=4355); |  | 177:PMM1OverCurrentBetw[1]:=Bit_0; | 177:ErrorComKlima[1].Code[1]:=Byte_0; |  |  | 4355:PMM[1].Phase[2].Current[33]:=Real_0;
mind_bool[178]:=PMM1OverCurrentBetw[2]; | mind[178]:=ErrorComKlima[1].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[34],lo:=4356,hi:=4357); |  | 178:PMM1OverCurrentBetw[2]:=Bit_0; | 178:ErrorComKlima[1].Code[2]:=Byte_0; |  |  | 4357:PMM[1].Phase[2].Current[34]:=Real_0;
mind_bool[179]:=PMM1OverCurrentBetw[3]; | mind[179]:=ErrorComKlima[1].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[35],lo:=4358,hi:=4359); |  | 179:PMM1OverCurrentBetw[3]:=Bit_0; | 179:ErrorComKlima[1].Code[3]:=Byte_0; |  |  | 4359:PMM[1].Phase[2].Current[35]:=Real_0;
mind_bool[180]:=PMM1OverCurrentOver[1]; | mind[180]:=ErrorComKlima[1].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[36],lo:=4360,hi:=4361); |  | 180:PMM1OverCurrentOver[1]:=Bit_0; | 180:ErrorComKlima[1].Code[4]:=Byte_0; |  |  | 4361:PMM[1].Phase[2].Current[36]:=Real_0;
mind_bool[181]:=PMM1OverCurrentOver[2]; | mind[181]:=ErrorComKlima[1].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[37],lo:=4362,hi:=4363); |  | 181:PMM1OverCurrentOver[2]:=Bit_0; | 181:ErrorComKlima[1].Code[5]:=Byte_0; |  |  | 4363:PMM[1].Phase[2].Current[37]:=Real_0;
mind_bool[182]:=PMM1OverCurrentOver[3]; | mind[182]:=ErrorComKlima[1].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[38],lo:=4364,hi:=4365); |  | 182:PMM1OverCurrentOver[3]:=Bit_0; | 182:ErrorComKlima[1].Code[6]:=Byte_0; |  |  | 4365:PMM[1].Phase[2].Current[38]:=Real_0;
mind_bool[183]:=PMM2OverCurrentBetw[1]; | mind[183]:=ErrorComKlima[1].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[39],lo:=4366,hi:=4367); |  | 183:PMM2OverCurrentBetw[1]:=Bit_0; | 183:ErrorComKlima[1].Code[7]:=Byte_0; |  |  | 4367:PMM[1].Phase[2].Current[39]:=Real_0;
mind_bool[184]:=PMM2OverCurrentBetw[2]; | mind[184]:=ErrorComKlima[1].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[3],lo:=4368,hi:=4369); |  | 184:PMM2OverCurrentBetw[2]:=Bit_0; | 184:ErrorComKlima[1].Code[8]:=Byte_0; |  |  | 4369:PMM[1].Phase[2].Current[3]:=Real_0;
mind_bool[185]:=PMM2OverCurrentBetw[3]; | mind[185]:=ErrorComKlima[1].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[40],lo:=4370,hi:=4371); |  | 185:PMM2OverCurrentBetw[3]:=Bit_0; | 185:ErrorComKlima[1].Code[9]:=Byte_0; |  |  | 4371:PMM[1].Phase[2].Current[40]:=Real_0;
mind_bool[186]:=PMM2OverCurrentOver[1]; | mind[186]:=ErrorComKlima[1].Status; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[41],lo:=4372,hi:=4373); |  | 186:PMM2OverCurrentOver[1]:=Bit_0; | 186:ErrorComKlima[1].Status:=Word_01; |  |  | 4373:PMM[1].Phase[2].Current[41]:=Real_0;
mind_bool[187]:=PMM2OverCurrentOver[2]; | mind[187]:=ErrorComKlima[2].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[42],lo:=4374,hi:=4375); |  | 187:PMM2OverCurrentOver[2]:=Bit_0; | 187:ErrorComKlima[2].Code[10]:=Byte_0; |  |  | 4375:PMM[1].Phase[2].Current[42]:=Real_0;
mind_bool[188]:=PMM2OverCurrentOver[3]; | mind[188]:=ErrorComKlima[2].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[4],lo:=4376,hi:=4377); |  | 188:PMM2OverCurrentOver[3]:=Bit_0; | 188:ErrorComKlima[2].Code[11]:=Byte_0; |  |  | 4377:PMM[1].Phase[2].Current[4]:=Real_0;
mind_bool[189]:=PMM3OverCurrentBetw[1]; | mind[189]:=ErrorComKlima[2].Code[12]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[5],lo:=4378,hi:=4379); |  | 189:PMM3OverCurrentBetw[1]:=Bit_0; | 189:ErrorComKlima[2].Code[12]:=Byte_0; |  |  | 4379:PMM[1].Phase[2].Current[5]:=Real_0;
mind_bool[190]:=PMM3OverCurrentBetw[2]; | mind[190]:=ErrorComKlima[2].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[6],lo:=4380,hi:=4381); |  | 190:PMM3OverCurrentBetw[2]:=Bit_0; | 190:ErrorComKlima[2].Code[13]:=Byte_0; |  |  | 4381:PMM[1].Phase[2].Current[6]:=Real_0;
mind_bool[191]:=PMM3OverCurrentBetw[3]; | mind[191]:=ErrorComKlima[2].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[7],lo:=4382,hi:=4383); |  | 191:PMM3OverCurrentBetw[3]:=Bit_0; | 191:ErrorComKlima[2].Code[14]:=Byte_0; |  |  | 4383:PMM[1].Phase[2].Current[7]:=Real_0;
mind_bool[192]:=PMM3OverCurrentOver[1]; | mind[192]:=ErrorComKlima[2].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[8],lo:=4384,hi:=4385); |  | 192:PMM3OverCurrentOver[1]:=Bit_0; | 192:ErrorComKlima[2].Code[15]:=Byte_0; |  |  | 4385:PMM[1].Phase[2].Current[8]:=Real_0;
mind_bool[193]:=PMM3OverCurrentOver[2]; | mind[193]:=ErrorComKlima[2].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[9],lo:=4386,hi:=4387); |  | 193:PMM3OverCurrentOver[2]:=Bit_0; | 193:ErrorComKlima[2].Code[1]:=Byte_0; |  |  | 4387:PMM[1].Phase[2].Current[9]:=Real_0;
mind_bool[194]:=PMM3OverCurrentOver[3]; | mind[194]:=ErrorComKlima[2].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[10],lo:=4388,hi:=4389); |  | 194:PMM3OverCurrentOver[3]:=Bit_0; | 194:ErrorComKlima[2].Code[2]:=Byte_0; |  |  | 4389:PMM[1].Phase[3].Current[10]:=Real_0;
mind_bool[195]:=PMM[1].Napaka; | mind[195]:=ErrorComKlima[2].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[11],lo:=4390,hi:=4391); |  | 195:PMM[1].Napaka:=Bit_0; | 195:ErrorComKlima[2].Code[3]:=Byte_0; |  |  | 4391:PMM[1].Phase[3].Current[11]:=Real_0;
mind_bool[196]:=PMM[2].Napaka; | mind[196]:=ErrorComKlima[2].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[12],lo:=4392,hi:=4393); |  | 196:PMM[2].Napaka:=Bit_0; | 196:ErrorComKlima[2].Code[4]:=Byte_0; |  |  | 4393:PMM[1].Phase[3].Current[12]:=Real_0;
mind_bool[197]:=PMM[3].Napaka; | mind[197]:=ErrorComKlima[2].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[13],lo:=4394,hi:=4395); |  | 197:PMM[3].Napaka:=Bit_0; | 197:ErrorComKlima[2].Code[5]:=Byte_0; |  |  | 4395:PMM[1].Phase[3].Current[13]:=Real_0;
mind_bool[198]:=SetDateTime; | mind[198]:=ErrorComKlima[2].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[14],lo:=4396,hi:=4397); |  | 198:SetDateTime:=Bit_0; | 198:ErrorComKlima[2].Code[6]:=Byte_0; |  |  | 4397:PMM[1].Phase[3].Current[14]:=Real_0;
mind_bool[199]:=SetDateTimeDemand; | mind[199]:=ErrorComKlima[2].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[15],lo:=4398,hi:=4399); |  | 199:SetDateTimeDemand:=Bit_0; | 199:ErrorComKlima[2].Code[7]:=Byte_0; |  |  | 4399:PMM[1].Phase[3].Current[15]:=Real_0;
mind_bool[200]:=SetDateTimeError; | mind[200]:=ErrorComKlima[2].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[16],lo:=4400,hi:=4401); |  | 200:SetDateTimeError:=Bit_0; | 200:ErrorComKlima[2].Code[8]:=Byte_0; |  |  | 4401:PMM[1].Phase[3].Current[16]:=Real_0;
mind_bool[201]:=SetDateTimeFinished; | mind[201]:=ErrorComKlima[2].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[17],lo:=4402,hi:=4403); |  | 201:SetDateTimeFinished:=Bit_0; | 201:ErrorComKlima[2].Code[9]:=Byte_0; |  |  | 4403:PMM[1].Phase[3].Current[17]:=Real_0;
mind_bool[202]:=SetRemoteOnOff[1]; | mind[202]:=ErrorComKlima[2].Status; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[18],lo:=4404,hi:=4405); |  | 202:SetRemoteOnOff[1]:=Bit_0; | 202:ErrorComKlima[2].Status:=Word_01; |  |  | 4405:PMM[1].Phase[3].Current[18]:=Real_0;
mind_bool[203]:=SetRemoteOnOff[2]; | mind[203]:=ErrorComKlima[3].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[19],lo:=4406,hi:=4407); |  | 203:SetRemoteOnOff[2]:=Bit_0; | 203:ErrorComKlima[3].Code[10]:=Byte_0; |  |  | 4407:PMM[1].Phase[3].Current[19]:=Real_0;
mind_bool[204]:=SlabaBaterijaPLC_A1; | mind[204]:=ErrorComKlima[3].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[1],lo:=4408,hi:=4409); |  | 204:SlabaBaterijaPLC_A1:=Bit_0; | 204:ErrorComKlima[3].Code[11]:=Byte_0; |  |  | 4409:PMM[1].Phase[3].Current[1]:=Real_0;
mind_bool[205]:=TempTSprevisoka[1]; | mind[205]:=ErrorComKlima[3].Code[12]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[20],lo:=4410,hi:=4411); |  | 205:TempTSprevisoka[1]:=Bit_0; | 205:ErrorComKlima[3].Code[12]:=Byte_0; |  |  | 4411:PMM[1].Phase[3].Current[20]:=Real_0;
mind_bool[206]:=TempTSprevisoka[2]; | mind[206]:=ErrorComKlima[3].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[21],lo:=4412,hi:=4413); |  | 206:TempTSprevisoka[2]:=Bit_0; | 206:ErrorComKlima[3].Code[13]:=Byte_0; |  |  | 4413:PMM[1].Phase[3].Current[21]:=Real_0;
mind_bool[207]:=UPS[1].AlarmAwaitingPower; | mind[207]:=ErrorComKlima[3].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[22],lo:=4414,hi:=4415); |  | 207:UPS[1].AlarmAwaitingPower:=Bit_0; | 207:ErrorComKlima[3].Code[14]:=Byte_0; |  |  | 4415:PMM[1].Phase[3].Current[22]:=Real_0;
mind_bool[208]:=UPS[1].AlarmBypassBad; | mind[208]:=ErrorComKlima[3].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[23],lo:=4416,hi:=4417); |  | 208:UPS[1].AlarmBypassBad:=Bit_0; | 208:ErrorComKlima[3].Code[15]:=Byte_0; |  |  | 4417:PMM[1].Phase[3].Current[23]:=Real_0;
mind_bool[209]:=UPS[1].AlarmChargerFailed; | mind[209]:=ErrorComKlima[3].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[24],lo:=4418,hi:=4419); |  | 209:UPS[1].AlarmChargerFailed:=Bit_0; | 209:ErrorComKlima[3].Code[1]:=Byte_0; |  |  | 4419:PMM[1].Phase[3].Current[24]:=Real_0;
mind_bool[210]:=UPS[1].AlarmCommunicationsLost; | mind[210]:=ErrorComKlima[3].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[25],lo:=4420,hi:=4421); |  | 210:UPS[1].AlarmCommunicationsLost:=Bit_0; | 210:ErrorComKlima[3].Code[2]:=Byte_0; |  |  | 4421:PMM[1].Phase[3].Current[25]:=Real_0;
mind_bool[211]:=UPS[1].AlarmDepletedBattery; | mind[211]:=ErrorComKlima[3].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[26],lo:=4422,hi:=4423); |  | 211:UPS[1].AlarmDepletedBattery:=Bit_0; | 211:ErrorComKlima[3].Code[3]:=Byte_0; |  |  | 4423:PMM[1].Phase[3].Current[26]:=Real_0;
mind_bool[212]:=UPS[1].AlarmDiagnosticTestFailed; | mind[212]:=ErrorComKlima[3].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[27],lo:=4424,hi:=4425); |  | 212:UPS[1].AlarmDiagnosticTestFailed:=Bit_0; | 212:ErrorComKlima[3].Code[4]:=Byte_0; |  |  | 4425:PMM[1].Phase[3].Current[27]:=Real_0;
mind_bool[213]:=UPS[1].AlarmIzhodOffKotZahtevano; | mind[213]:=ErrorComKlima[3].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[28],lo:=4426,hi:=4427); |  | 213:UPS[1].AlarmIzhodOffKotZahtevano:=Bit_0; | 213:ErrorComKlima[3].Code[5]:=Byte_0; |  |  | 4427:PMM[1].Phase[3].Current[28]:=Real_0;
mind_bool[214]:=UPS[1].AlarmIzhodPreobremenjen; | mind[214]:=ErrorComKlima[3].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[29],lo:=4428,hi:=4429); |  | 214:UPS[1].AlarmIzhodPreobremenjen:=Bit_0; | 214:ErrorComKlima[3].Code[6]:=Byte_0; |  |  | 4429:PMM[1].Phase[3].Current[29]:=Real_0;
mind_bool[215]:=UPS[1].AlarmLowBattery; | mind[215]:=ErrorComKlima[3].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[2],lo:=4430,hi:=4431); |  | 215:UPS[1].AlarmLowBattery:=Bit_0; | 215:ErrorComKlima[3].Code[7]:=Byte_0; |  |  | 4431:PMM[1].Phase[3].Current[2]:=Real_0;
mind_bool[216]:=UPS[1].AlarmNapakaNaVarovalki; | mind[216]:=ErrorComKlima[3].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[30],lo:=4432,hi:=4433); |  | 216:UPS[1].AlarmNapakaNaVarovalki:=Bit_0; | 216:ErrorComKlima[3].Code[8]:=Byte_0; |  |  | 4433:PMM[1].Phase[3].Current[30]:=Real_0;
mind_bool[217]:=UPS[1].AlarmNapakaNaVentilatorju; | mind[217]:=ErrorComKlima[3].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[31],lo:=4434,hi:=4435); |  | 217:UPS[1].AlarmNapakaNaVentilatorju:=Bit_0; | 217:ErrorComKlima[3].Code[9]:=Byte_0; |  |  | 4435:PMM[1].Phase[3].Current[31]:=Real_0;
mind_bool[218]:=UPS[1].AlarmOnBattery; | mind[218]:=ErrorComKlima[3].Status; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[32],lo:=4436,hi:=4437); |  | 218:UPS[1].AlarmOnBattery:=Bit_0; | 218:ErrorComKlima[3].Status:=Word_01; |  |  | 4437:PMM[1].Phase[3].Current[32]:=Real_0;
mind_bool[219]:=UPS[1].AlarmOnBypass; | mind[219]:=ErrorComKlima[4].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[33],lo:=4438,hi:=4439); |  | 219:UPS[1].AlarmOnBypass:=Bit_0; | 219:ErrorComKlima[4].Code[10]:=Byte_0; |  |  | 4439:PMM[1].Phase[3].Current[33]:=Real_0;
mind_bool[220]:=UPS[1].AlarmInverterError; | mind[220]:=ErrorComKlima[4].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[34],lo:=4440,hi:=4441); |  | 220:UPS[1].AlarmInverterError:=Bit_0; | 220:ErrorComKlima[4].Code[11]:=Byte_0; |  |  | 4441:PMM[1].Phase[3].Current[34]:=Real_0;
mind_bool[221]:=UPS[1].AlarmShutdownImminent; | mind[221]:=ErrorComKlima[4].Code[12]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[35],lo:=4442,hi:=4443); |  | 221:UPS[1].AlarmShutdownImminent:=Bit_0; | 221:ErrorComKlima[4].Code[12]:=Byte_0; |  |  | 4443:PMM[1].Phase[3].Current[35]:=Real_0;
mind_bool[222]:=UPS[1].AlarmShutdownPending; | mind[222]:=ErrorComKlima[4].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[36],lo:=4444,hi:=4445); |  | 222:UPS[1].AlarmShutdownPending:=Bit_0; | 222:ErrorComKlima[4].Code[13]:=Byte_0; |  |  | 4445:PMM[1].Phase[3].Current[36]:=Real_0;
mind_bool[223]:=UPS[1].AlarmSlabaBaterija; | mind[223]:=ErrorComKlima[4].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[37],lo:=4446,hi:=4447); |  | 223:UPS[1].AlarmSlabaBaterija:=Bit_0; | 223:ErrorComKlima[4].Code[14]:=Byte_0; |  |  | 4447:PMM[1].Phase[3].Current[37]:=Real_0;
mind_bool[224]:=UPS[1].AlarmSplosnaNapaka; | mind[224]:=ErrorComKlima[4].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[38],lo:=4448,hi:=4449); |  | 224:UPS[1].AlarmSplosnaNapaka:=Bit_0; | 224:ErrorComKlima[4].Code[15]:=Byte_0; |  |  | 4449:PMM[1].Phase[3].Current[38]:=Real_0;
mind_bool[225]:=UPS[1].AlarmStanjeIzhodaIzvenToleranc; | mind[225]:=ErrorComKlima[4].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[39],lo:=4450,hi:=4451); |  | 225:UPS[1].AlarmStanjeIzhodaIzvenToleranc:=Bit_0; | 225:ErrorComKlima[4].Code[1]:=Byte_0; |  |  | 4451:PMM[1].Phase[3].Current[39]:=Real_0;
mind_bool[226]:=UPS[1].AlarmStanjeVhodaIzvenToleranc; | mind[226]:=ErrorComKlima[4].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[3],lo:=4452,hi:=4453); |  | 226:UPS[1].AlarmStanjeVhodaIzvenToleranc:=Bit_0; | 226:ErrorComKlima[4].Code[2]:=Byte_0; |  |  | 4453:PMM[1].Phase[3].Current[3]:=Real_0;
mind_bool[227]:=UPS[1].AlarmTemperaturaIzvenToleranc; | mind[227]:=ErrorComKlima[4].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[40],lo:=4454,hi:=4455); |  | 227:UPS[1].AlarmTemperaturaIzvenToleranc:=Bit_0; | 227:ErrorComKlima[4].Code[3]:=Byte_0; |  |  | 4455:PMM[1].Phase[3].Current[40]:=Real_0;
mind_bool[228]:=UPS[1].AlarmTestInProgres; | mind[228]:=ErrorComKlima[4].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[41],lo:=4456,hi:=4457); |  | 228:UPS[1].AlarmTestInProgres:=Bit_0; | 228:ErrorComKlima[4].Code[4]:=Byte_0; |  |  | 4457:PMM[1].Phase[3].Current[41]:=Real_0;
mind_bool[229]:=UPS[1].AlarmUPSIzhodOff; | mind[229]:=ErrorComKlima[4].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[42],lo:=4458,hi:=4459); |  | 229:UPS[1].AlarmUPSIzhodOff:=Bit_0; | 229:ErrorComKlima[4].Code[5]:=Byte_0; |  |  | 4459:PMM[1].Phase[3].Current[42]:=Real_0;
mind_bool[230]:=UPS[1].AlarmUPSOffKotZahtevano; | mind[230]:=ErrorComKlima[4].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[4],lo:=4460,hi:=4461); |  | 230:UPS[1].AlarmUPSOffKotZahtevano:=Bit_0; | 230:ErrorComKlima[4].Code[6]:=Byte_0; |  |  | 4461:PMM[1].Phase[3].Current[4]:=Real_0;
mind_bool[231]:=UPS[1].AlarmUPSSystemOff; | mind[231]:=ErrorComKlima[4].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[5],lo:=4462,hi:=4463); |  | 231:UPS[1].AlarmUPSSystemOff:=Bit_0; | 231:ErrorComKlima[4].Code[7]:=Byte_0; |  |  | 4463:PMM[1].Phase[3].Current[5]:=Real_0;
mind_bool[232]:=UPS[1].Napaka; | mind[232]:=ErrorComKlima[4].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[6],lo:=4464,hi:=4465); |  | 232:UPS[1].Napaka:=Bit_0; | 232:ErrorComKlima[4].Code[8]:=Byte_0; |  |  | 4465:PMM[1].Phase[3].Current[6]:=Real_0;
mind_bool[233]:=UPS[1].StatusEcomodeAktiven; | mind[233]:=ErrorComKlima[4].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[7],lo:=4466,hi:=4467); |  | 233:UPS[1].StatusEcomodeAktiven:=Bit_0; | 233:ErrorComKlima[4].Code[9]:=Byte_0; |  |  | 4467:PMM[1].Phase[3].Current[7]:=Real_0;
mind_bool[234]:=UPS[1].StatusInverterIsOn; | mind[234]:=ErrorComKlima[4].Status; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[8],lo:=4468,hi:=4469); |  | 234:UPS[1].StatusInverterIsOn:=Bit_0; | 234:ErrorComKlima[4].Status:=Word_01; |  |  | 4469:PMM[1].Phase[3].Current[8]:=Real_0;
mind_bool[235]:=UPS[1].StatusStopOperation; | mind[235]:=ErrorComKlima[5].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[9],lo:=4470,hi:=4471); |  | 235:UPS[1].StatusStopOperation:=Bit_0; | 235:ErrorComKlima[5].Code[10]:=Byte_0; |  |  | 4471:PMM[1].Phase[3].Current[9]:=Real_0;
mind_bool[236]:=UPS[2].AlarmAwaitingPower; | mind[236]:=ErrorComKlima[5].Code[11]; |  |  | Read_Real(rVar:=PMM[1].PowerFactorPhaseA,lo:=4472,hi:=4473); |  | 236:UPS[2].AlarmAwaitingPower:=Bit_0; | 236:ErrorComKlima[5].Code[11]:=Byte_0; |  |  | 4473:PMM[1].PowerFactorPhaseA:=Real_0;
mind_bool[237]:=UPS[2].AlarmBypassBad; | mind[237]:=ErrorComKlima[5].Code[12]; |  |  | Read_Real(rVar:=PMM[1].PowerFactorPhaseB,lo:=4474,hi:=4475); |  | 237:UPS[2].AlarmBypassBad:=Bit_0; | 237:ErrorComKlima[5].Code[12]:=Byte_0; |  |  | 4475:PMM[1].PowerFactorPhaseB:=Real_0;
mind_bool[238]:=UPS[2].AlarmChargerFailed; | mind[238]:=ErrorComKlima[5].Code[13]; |  |  | Read_Real(rVar:=PMM[1].PowerFactorPhaseC,lo:=4476,hi:=4477); |  | 238:UPS[2].AlarmChargerFailed:=Bit_0; | 238:ErrorComKlima[5].Code[13]:=Byte_0; |  |  | 4477:PMM[1].PowerFactorPhaseC:=Real_0;
mind_bool[239]:=UPS[2].AlarmCommunicationsLost; | mind[239]:=ErrorComKlima[5].Code[14]; |  |  | Read_Real(rVar:=PMM[1].TotalActivePower_kW,lo:=4478,hi:=4479); |  | 239:UPS[2].AlarmCommunicationsLost:=Bit_0; | 239:ErrorComKlima[5].Code[14]:=Byte_0; |  |  | 4479:PMM[1].TotalActivePower_kW:=Real_0;
mind_bool[240]:=UPS[2].AlarmDepletedBattery; | mind[240]:=ErrorComKlima[5].Code[15]; |  |  | Read_Real(rVar:=PMM[1].TotalAparentPower_kVA,lo:=4480,hi:=4481); |  | 240:UPS[2].AlarmDepletedBattery:=Bit_0; | 240:ErrorComKlima[5].Code[15]:=Byte_0; |  |  | 4481:PMM[1].TotalAparentPower_kVA:=Real_0;
mind_bool[241]:=UPS[2].AlarmDiagnosticTestFailed; | mind[241]:=ErrorComKlima[5].Code[1]; |  |  | Read_Real(rVar:=PMM[1].TotalPowerFactor,lo:=4482,hi:=4483); |  | 241:UPS[2].AlarmDiagnosticTestFailed:=Bit_0; | 241:ErrorComKlima[5].Code[1]:=Byte_0; |  |  | 4483:PMM[1].TotalPowerFactor:=Real_0;
mind_bool[242]:=UPS[2].AlarmIzhodOffKotZahtevano; | mind[242]:=ErrorComKlima[5].Code[2]; |  |  | Read_Real(rVar:=PMM[1].TotalReactivePower_kVAR,lo:=4484,hi:=4485); |  | 242:UPS[2].AlarmIzhodOffKotZahtevano:=Bit_0; | 242:ErrorComKlima[5].Code[2]:=Byte_0; |  |  | 4485:PMM[1].TotalReactivePower_kVAR:=Real_0;
mind_bool[243]:=UPS[2].AlarmIzhodPreobremenjen; | mind[243]:=ErrorComKlima[5].Code[3]; |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseAB_V,lo:=4486,hi:=4487); |  | 243:UPS[2].AlarmIzhodPreobremenjen:=Bit_0; | 243:ErrorComKlima[5].Code[3]:=Byte_0; |  |  | 4487:PMM[1].VoltageBetweenPhaseAB_V:=Real_0;
mind_bool[244]:=UPS[2].AlarmLowBattery; | mind[244]:=ErrorComKlima[5].Code[4]; |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseAN_V,lo:=4488,hi:=4489); |  | 244:UPS[2].AlarmLowBattery:=Bit_0; | 244:ErrorComKlima[5].Code[4]:=Byte_0; |  |  | 4489:PMM[1].VoltageBetweenPhaseAN_V:=Real_0;
mind_bool[245]:=UPS[2].AlarmNapakaNaVarovalki; | mind[245]:=ErrorComKlima[5].Code[5]; |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseBC_V,lo:=4490,hi:=4491); |  | 245:UPS[2].AlarmNapakaNaVarovalki:=Bit_0; | 245:ErrorComKlima[5].Code[5]:=Byte_0; |  |  | 4491:PMM[1].VoltageBetweenPhaseBC_V:=Real_0;
mind_bool[246]:=UPS[2].AlarmNapakaNaVentilatorju; | mind[246]:=ErrorComKlima[5].Code[6]; |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseBN_V,lo:=4492,hi:=4493); |  | 246:UPS[2].AlarmNapakaNaVentilatorju:=Bit_0; | 246:ErrorComKlima[5].Code[6]:=Byte_0; |  |  | 4493:PMM[1].VoltageBetweenPhaseBN_V:=Real_0;
mind_bool[247]:=UPS[2].AlarmOnBattery; | mind[247]:=ErrorComKlima[5].Code[7]; |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseCA_V,lo:=4494,hi:=4495); |  | 247:UPS[2].AlarmOnBattery:=Bit_0; | 247:ErrorComKlima[5].Code[7]:=Byte_0; |  |  | 4495:PMM[1].VoltageBetweenPhaseCA_V:=Real_0;
mind_bool[248]:=UPS[2].AlarmOnBypass; | mind[248]:=ErrorComKlima[5].Code[8]; |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseCN_V,lo:=4496,hi:=4497); |  | 248:UPS[2].AlarmOnBypass:=Bit_0; | 248:ErrorComKlima[5].Code[8]:=Byte_0; |  |  | 4497:PMM[1].VoltageBetweenPhaseCN_V:=Real_0;
mind_bool[249]:=UPS[2].AlarmInverterError; | mind[249]:=ErrorComKlima[5].Code[9]; |  |  | Read_Real(rVar:=PMM[2].ActivePowerPhaseA_kW,lo:=4498,hi:=4499); |  | 249:UPS[2].AlarmInverterError:=Bit_0; | 249:ErrorComKlima[5].Code[9]:=Byte_0; |  |  | 4499:PMM[2].ActivePowerPhaseA_kW:=Real_0;
mind_bool[250]:=UPS[2].AlarmShutdownImminent; | mind[250]:=ErrorComKlima[5].Status; |  |  | Read_Real(rVar:=PMM[2].ActivePowerPhaseB_kW,lo:=4500,hi:=4501); |  | 250:UPS[2].AlarmShutdownImminent:=Bit_0; | 250:ErrorComKlima[5].Status:=Word_01; |  |  | 4501:PMM[2].ActivePowerPhaseB_kW:=Real_0;
mind_bool[251]:=UPS[2].AlarmShutdownPending; | mind[251]:=ErrorComKlima[6].Code[10]; |  |  | Read_Real(rVar:=PMM[2].ActivePowerPhaseC_kW,lo:=4502,hi:=4503); |  | 251:UPS[2].AlarmShutdownPending:=Bit_0; | 251:ErrorComKlima[6].Code[10]:=Byte_0; |  |  | 4503:PMM[2].ActivePowerPhaseC_kW:=Real_0;
mind_bool[252]:=UPS[2].AlarmSlabaBaterija; | mind[252]:=ErrorComKlima[6].Code[11]; |  |  | Read_Real(rVar:=PMM[2].AverageCurrent_A,lo:=4504,hi:=4505); |  | 252:UPS[2].AlarmSlabaBaterija:=Bit_0; | 252:ErrorComKlima[6].Code[11]:=Byte_0; |  |  | 4505:PMM[2].AverageCurrent_A:=Real_0;
mind_bool[253]:=UPS[2].AlarmSplosnaNapaka; | mind[253]:=ErrorComKlima[6].Code[12]; |  |  | Read_Real(rVar:=PMM[2].AveragePhaseToNeutral_V,lo:=4506,hi:=4507); |  | 253:UPS[2].AlarmSplosnaNapaka:=Bit_0; | 253:ErrorComKlima[6].Code[12]:=Byte_0; |  |  | 4507:PMM[2].AveragePhaseToNeutral_V:=Real_0;
mind_bool[254]:=UPS[2].AlarmStanjeIzhodaIzvenToleranc; | mind[254]:=ErrorComKlima[6].Code[13]; |  |  | Read_Real(rVar:=PMM[2].AveragePhaseToPhase_V,lo:=4508,hi:=4509); |  | 254:UPS[2].AlarmStanjeIzhodaIzvenToleranc:=Bit_0; | 254:ErrorComKlima[6].Code[13]:=Byte_0; |  |  | 4509:PMM[2].AveragePhaseToPhase_V:=Real_0;
mind_bool[255]:=UPS[2].AlarmStanjeVhodaIzvenToleranc; | mind[255]:=ErrorComKlima[6].Code[14]; |  |  | Read_Real(rVar:=PMM[2].CurrentInPhaseA_A,lo:=4510,hi:=4511); |  | 255:UPS[2].AlarmStanjeVhodaIzvenToleranc:=Bit_0; | 255:ErrorComKlima[6].Code[14]:=Byte_0; |  |  | 4511:PMM[2].CurrentInPhaseA_A:=Real_0;
mind_bool[256]:=UPS[2].AlarmTemperaturaIzvenToleranc; | mind[256]:=ErrorComKlima[6].Code[15]; |  |  | Read_Real(rVar:=PMM[2].CurrentInPhaseB_A,lo:=4512,hi:=4513); |  | 256:UPS[2].AlarmTemperaturaIzvenToleranc:=Bit_0; | 256:ErrorComKlima[6].Code[15]:=Byte_0; |  |  | 4513:PMM[2].CurrentInPhaseB_A:=Real_0;
mind_bool[257]:=UPS[2].AlarmTestInProgres; | mind[257]:=ErrorComKlima[6].Code[1]; |  |  | Read_Real(rVar:=PMM[2].CurrentInPhaseC_A,lo:=4514,hi:=4515); |  | 257:UPS[2].AlarmTestInProgres:=Bit_0; | 257:ErrorComKlima[6].Code[1]:=Byte_0; |  |  | 4515:PMM[2].CurrentInPhaseC_A:=Real_0;
mind_bool[258]:=UPS[2].AlarmUPSIzhodOff; | mind[258]:=ErrorComKlima[6].Code[2]; |  |  | Read_Real(rVar:=PMM[2].EnergyConsumed_kWh,lo:=4516,hi:=4517); |  | 258:UPS[2].AlarmUPSIzhodOff:=Bit_0; | 258:ErrorComKlima[6].Code[2]:=Byte_0; |  |  | 4517:PMM[2].EnergyConsumed_kWh:=Real_0;
mind_bool[259]:=UPS[2].AlarmUPSOffKotZahtevano; | mind[259]:=ErrorComKlima[6].Code[3]; |  |  | Read_Real(rVar:=PMM[2].Frequency_Hz,lo:=4518,hi:=4519); |  | 259:UPS[2].AlarmUPSOffKotZahtevano:=Bit_0; | 259:ErrorComKlima[6].Code[3]:=Byte_0; |  |  | 4519:PMM[2].Frequency_Hz:=Real_0;
mind_bool[260]:=UPS[2].AlarmUPSSystemOff; | mind[260]:=ErrorComKlima[6].Code[4]; |  |  | Read_Real(rVar:=PMM[2].NeutralCurrent_A,lo:=4520,hi:=4521); |  | 260:UPS[2].AlarmUPSSystemOff:=Bit_0; | 260:ErrorComKlima[6].Code[4]:=Byte_0; |  |  | 4521:PMM[2].NeutralCurrent_A:=Real_0;
mind_bool[261]:=UPS[2].Napaka; | mind[261]:=ErrorComKlima[6].Code[5]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[10],lo:=4522,hi:=4523); |  | 261:UPS[2].Napaka:=Bit_0; | 261:ErrorComKlima[6].Code[5]:=Byte_0; |  |  | 4523:PMM[2].Phase[1].Current[10]:=Real_0;
mind_bool[262]:=UPS[2].StatusEcomodeAktiven; | mind[262]:=ErrorComKlima[6].Code[6]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[11],lo:=4524,hi:=4525); |  | 262:UPS[2].StatusEcomodeAktiven:=Bit_0; | 262:ErrorComKlima[6].Code[6]:=Byte_0; |  |  | 4525:PMM[2].Phase[1].Current[11]:=Real_0;
mind_bool[263]:=UPS[2].StatusInverterIsOn; | mind[263]:=ErrorComKlima[6].Code[7]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[12],lo:=4526,hi:=4527); |  | 263:UPS[2].StatusInverterIsOn:=Bit_0; | 263:ErrorComKlima[6].Code[7]:=Byte_0; |  |  | 4527:PMM[2].Phase[1].Current[12]:=Real_0;
mind_bool[264]:=UPS[2].StatusStopOperation; | mind[264]:=ErrorComKlima[6].Code[8]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[13],lo:=4528,hi:=4529); |  | 264:UPS[2].StatusStopOperation:=Bit_0; | 264:ErrorComKlima[6].Code[8]:=Byte_0; |  |  | 4529:PMM[2].Phase[1].Current[13]:=Real_0;
mind_bool[265]:=UserLoggedIn; | mind[265]:=ErrorComKlima[6].Code[9]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[14],lo:=4530,hi:=4531); |  | 265:UserLoggedIn:=Bit_0; | 265:ErrorComKlima[6].Code[9]:=Byte_0; |  |  | 4531:PMM[2].Phase[1].Current[14]:=Real_0;
mind_bool[266]:=XVH_AlarmOn; | mind[266]:=ErrorComKlima[6].Status; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[15],lo:=4532,hi:=4533); |  | 266:XVH_AlarmOn:=Bit_0; | 266:ErrorComKlima[6].Status:=Word_01; |  |  | 4533:PMM[2].Phase[1].Current[15]:=Real_0;
mind_bool[267]:=AlarmGenRest; | mind[267]:=ErrorComPMM[1].Code[10]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[16],lo:=4534,hi:=4535); |  | 267:AlarmGenRest:=Bit_0; | 267:ErrorComPMM[1].Code[10]:=Byte_0; |  |  | 4535:PMM[2].Phase[1].Current[16]:=Real_0;
mind_bool[268]:=DI_UpsA_BypassON; | mind[268]:=ErrorComPMM[1].Code[11]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[17],lo:=4536,hi:=4537); |  | 268:DI_UpsA_BypassON:=Bit_0; | 268:ErrorComPMM[1].Code[11]:=Byte_0; |  |  | 4537:PMM[2].Phase[1].Current[17]:=Real_0;
mind_bool[269]:=DI_UpsA_ERR; | mind[269]:=ErrorComPMM[1].Code[12]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[18],lo:=4538,hi:=4539); |  | 269:DI_UpsA_ERR:=Bit_0; | 269:ErrorComPMM[1].Code[12]:=Byte_0; |  |  | 4539:PMM[2].Phase[1].Current[18]:=Real_0;
mind_bool[270]:=DI_UpsB_BypassON; | mind[270]:=ErrorComPMM[1].Code[13]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[19],lo:=4540,hi:=4541); |  | 270:DI_UpsB_BypassON:=Bit_0; | 270:ErrorComPMM[1].Code[13]:=Byte_0; |  |  | 4541:PMM[2].Phase[1].Current[19]:=Real_0;
mind_bool[271]:=DI_UpsB_ERR; | mind[271]:=ErrorComPMM[1].Code[14]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[1],lo:=4542,hi:=4543); |  | 271:DI_UpsB_ERR:=Bit_0; | 271:ErrorComPMM[1].Code[14]:=Byte_0; |  |  | 4543:PMM[2].Phase[1].Current[1]:=Real_0;
mind_bool[272]:=DIN_Klima5_ERR; | mind[272]:=ErrorComPMM[1].Code[15]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[20],lo:=4544,hi:=4545); |  | 272:DIN_Klima5_ERR:=Bit_0; | 272:ErrorComPMM[1].Code[15]:=Byte_0; |  |  | 4545:PMM[2].Phase[1].Current[20]:=Real_0;
mind_bool[273]:=DIN_Klima6_ERR; | mind[273]:=ErrorComPMM[1].Code[1]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[21],lo:=4546,hi:=4547); |  | 273:DIN_Klima6_ERR:=Bit_0; | 273:ErrorComPMM[1].Code[1]:=Byte_0; |  |  | 4547:PMM[2].Phase[1].Current[21]:=Real_0;
mind_bool[274]:=DIN_KlimaSplit1_ERR; | mind[274]:=ErrorComPMM[1].Code[2]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[22],lo:=4548,hi:=4549); |  | 274:DIN_KlimaSplit1_ERR:=Bit_0; | 274:ErrorComPMM[1].Code[2]:=Byte_0; |  |  | 4549:PMM[2].Phase[1].Current[22]:=Real_0;
mind_bool[275]:=DIN_Q10_OdcKlima6_IZP; | mind[275]:=ErrorComPMM[1].Code[3]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[23],lo:=4550,hi:=4551); |  | 275:DIN_Q10_OdcKlima6_IZP:=Bit_0; | 275:ErrorComPMM[1].Code[3]:=Byte_0; |  |  | 4551:PMM[2].Phase[1].Current[23]:=Real_0;
mind_bool[276]:=DIN_Q25_OdcUpsA_IZP; | mind[276]:=ErrorComPMM[1].Code[4]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[24],lo:=4552,hi:=4553); |  | 276:DIN_Q25_OdcUpsA_IZP:=Bit_0; | 276:ErrorComPMM[1].Code[4]:=Byte_0; |  |  | 4553:PMM[2].Phase[1].Current[24]:=Real_0;
mind_bool[277]:=DIN_Q26_OdcByA_IZP; | mind[277]:=ErrorComPMM[1].Code[5]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[25],lo:=4554,hi:=4555); |  | 277:DIN_Q26_OdcByA_IZP:=Bit_0; | 277:ErrorComPMM[1].Code[5]:=Byte_0; |  |  | 4555:PMM[2].Phase[1].Current[25]:=Real_0;
mind_bool[278]:=DIN_Q27_OdcByUpsA_IZP; | mind[278]:=ErrorComPMM[1].Code[6]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[26],lo:=4556,hi:=4557); |  | 278:DIN_Q27_OdcByUpsA_IZP:=Bit_0; | 278:ErrorComPMM[1].Code[6]:=Byte_0; |  |  | 4557:PMM[2].Phase[1].Current[26]:=Real_0;
mind_bool[279]:=DIN_Q28_OdcUpsB_IZP; | mind[279]:=ErrorComPMM[1].Code[7]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[27],lo:=4558,hi:=4559); |  | 279:DIN_Q28_OdcUpsB_IZP:=Bit_0; | 279:ErrorComPMM[1].Code[7]:=Byte_0; |  |  | 4559:PMM[2].Phase[1].Current[27]:=Real_0;
mind_bool[280]:=DIN_Q29_OdcByB_IZP; | mind[280]:=ErrorComPMM[1].Code[8]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[28],lo:=4560,hi:=4561); |  | 280:DIN_Q29_OdcByB_IZP:=Bit_0; | 280:ErrorComPMM[1].Code[8]:=Byte_0; |  |  | 4561:PMM[2].Phase[1].Current[28]:=Real_0;
mind_bool[281]:=DIN_Q2_Rezerva_IZP; | mind[281]:=ErrorComPMM[1].Code[9]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[29],lo:=4562,hi:=4563); |  | 281:DIN_Q2_Rezerva_IZP:=Bit_0; | 281:ErrorComPMM[1].Code[9]:=Byte_0; |  |  | 4563:PMM[2].Phase[1].Current[29]:=Real_0;
mind_bool[282]:=DIN_Q30_OdcByUpsB_IZP; | mind[282]:=ErrorComPMM[1].Status; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[2],lo:=4564,hi:=4565); |  | 282:DIN_Q30_OdcByUpsB_IZP:=Bit_0; | 282:ErrorComPMM[1].Status:=Word_01; |  |  | 4565:PMM[2].Phase[1].Current[2]:=Real_0;
mind_bool[283]:=DIN_Q5_OdcKlima1_IZP; | mind[283]:=ErrorComPMM[2].Code[10]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[30],lo:=4566,hi:=4567); |  | 283:DIN_Q5_OdcKlima1_IZP:=Bit_0; | 283:ErrorComPMM[2].Code[10]:=Byte_0; |  |  | 4567:PMM[2].Phase[1].Current[30]:=Real_0;
mind_bool[284]:=DIN_Q6_OdcKlima2_IZP; | mind[284]:=ErrorComPMM[2].Code[11]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[31],lo:=4568,hi:=4569); |  | 284:DIN_Q6_OdcKlima2_IZP:=Bit_0; | 284:ErrorComPMM[2].Code[11]:=Byte_0; |  |  | 4569:PMM[2].Phase[1].Current[31]:=Real_0;
mind_bool[285]:=DIN_Q7_OdcKlima3_IZP; | mind[285]:=ErrorComPMM[2].Code[12]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[32],lo:=4570,hi:=4571); |  | 285:DIN_Q7_OdcKlima3_IZP:=Bit_0; | 285:ErrorComPMM[2].Code[12]:=Byte_0; |  |  | 4571:PMM[2].Phase[1].Current[32]:=Real_0;
mind_bool[286]:=DIN_Q8_OdcKlima4_IZP; | mind[286]:=ErrorComPMM[2].Code[13]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[33],lo:=4572,hi:=4573); |  | 286:DIN_Q8_OdcKlima4_IZP:=Bit_0; | 286:ErrorComPMM[2].Code[13]:=Byte_0; |  |  | 4573:PMM[2].Phase[1].Current[33]:=Real_0;
mind_bool[287]:=DIN_Q9_OdcKlima5_IZP; | mind[287]:=ErrorComPMM[2].Code[14]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[34],lo:=4574,hi:=4575); |  | 287:DIN_Q9_OdcKlima5_IZP:=Bit_0; | 287:ErrorComPMM[2].Code[14]:=Byte_0; |  |  | 4575:PMM[2].Phase[1].Current[34]:=Real_0;
mind_bool[288]:=ErrorComCirc[1].Error; | mind[288]:=ErrorComPMM[2].Code[15]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[35],lo:=4576,hi:=4577); |  | 288:ErrorComCirc[1].Error:=Bit_0; | 288:ErrorComPMM[2].Code[15]:=Byte_0; |  |  | 4577:PMM[2].Phase[1].Current[35]:=Real_0;
mind_bool[289]:=ErrorComCirc[2].Error; | mind[289]:=ErrorComPMM[2].Code[1]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[36],lo:=4578,hi:=4579); |  | 289:ErrorComCirc[2].Error:=Bit_0; | 289:ErrorComPMM[2].Code[1]:=Byte_0; |  |  | 4579:PMM[2].Phase[1].Current[36]:=Real_0;
mind_bool[290]:=ErrorComCirc[3].Error; | mind[290]:=ErrorComPMM[2].Code[2]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[37],lo:=4580,hi:=4581); |  | 290:ErrorComCirc[3].Error:=Bit_0; | 290:ErrorComPMM[2].Code[2]:=Byte_0; |  |  | 4581:PMM[2].Phase[1].Current[37]:=Real_0;
mind_bool[291]:=ErrorComCirc[4].Error; | mind[291]:=ErrorComPMM[2].Code[3]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[38],lo:=4582,hi:=4583); |  | 291:ErrorComCirc[4].Error:=Bit_0; | 291:ErrorComPMM[2].Code[3]:=Byte_0; |  |  | 4583:PMM[2].Phase[1].Current[38]:=Real_0;
mind_bool[292]:=ErrorComCirc[5].Error; | mind[292]:=ErrorComPMM[2].Code[4]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[39],lo:=4584,hi:=4585); |  | 292:ErrorComCirc[5].Error:=Bit_0; | 292:ErrorComPMM[2].Code[4]:=Byte_0; |  |  | 4585:PMM[2].Phase[1].Current[39]:=Real_0;
mind_bool[293]:=ErrorComKlima[1].Error; | mind[293]:=ErrorComPMM[2].Code[5]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[3],lo:=4586,hi:=4587); |  | 293:ErrorComKlima[1].Error:=Bit_0; | 293:ErrorComPMM[2].Code[5]:=Byte_0; |  |  | 4587:PMM[2].Phase[1].Current[3]:=Real_0;
mind_bool[294]:=ErrorComKlima[2].Error; | mind[294]:=ErrorComPMM[2].Code[6]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[40],lo:=4588,hi:=4589); |  | 294:ErrorComKlima[2].Error:=Bit_0; | 294:ErrorComPMM[2].Code[6]:=Byte_0; |  |  | 4589:PMM[2].Phase[1].Current[40]:=Real_0;
mind_bool[295]:=ErrorComKlima[3].Error; | mind[295]:=ErrorComPMM[2].Code[7]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[41],lo:=4590,hi:=4591); |  | 295:ErrorComKlima[3].Error:=Bit_0; | 295:ErrorComPMM[2].Code[7]:=Byte_0; |  |  | 4591:PMM[2].Phase[1].Current[41]:=Real_0;
mind_bool[296]:=ErrorComKlima[4].Error; | mind[296]:=ErrorComPMM[2].Code[8]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[42],lo:=4592,hi:=4593); |  | 296:ErrorComKlima[4].Error:=Bit_0; | 296:ErrorComPMM[2].Code[8]:=Byte_0; |  |  | 4593:PMM[2].Phase[1].Current[42]:=Real_0;
mind_bool[297]:=ErrorComKlima[5].Error; | mind[297]:=ErrorComPMM[2].Code[9]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[4],lo:=4594,hi:=4595); |  | 297:ErrorComKlima[5].Error:=Bit_0; | 297:ErrorComPMM[2].Code[9]:=Byte_0; |  |  | 4595:PMM[2].Phase[1].Current[4]:=Real_0;
mind_bool[298]:=ErrorComKlima[6].Error; | mind[298]:=ErrorComPMM[2].Status; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[5],lo:=4596,hi:=4597); |  | 298:ErrorComKlima[6].Error:=Bit_0; | 298:ErrorComPMM[2].Status:=Word_01; |  |  | 4597:PMM[2].Phase[1].Current[5]:=Real_0;
mind_bool[299]:=ErrorComPMM[1].Error; | mind[299]:=ErrorComPMM[3].Code[10]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[6],lo:=4598,hi:=4599); |  | 299:ErrorComPMM[1].Error:=Bit_0; | 299:ErrorComPMM[3].Code[10]:=Byte_0; |  |  | 4599:PMM[2].Phase[1].Current[6]:=Real_0;
mind_bool[300]:=ErrorComPMM[2].Error; | mind[300]:=ErrorComPMM[3].Code[11]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[7],lo:=4600,hi:=4601); |  | 300:ErrorComPMM[2].Error:=Bit_0; | 300:ErrorComPMM[3].Code[11]:=Byte_0; |  |  | 4601:PMM[2].Phase[1].Current[7]:=Real_0;
mind_bool[301]:=ErrorComPMM[3].Error; | mind[301]:=ErrorComPMM[3].Code[12]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[8],lo:=4602,hi:=4603); |  | 301:ErrorComPMM[3].Error:=Bit_0; | 301:ErrorComPMM[3].Code[12]:=Byte_0; |  |  | 4603:PMM[2].Phase[1].Current[8]:=Real_0;
mind_bool[302]:=ErrorComUPS[1].Error; | mind[302]:=ErrorComPMM[3].Code[13]; |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[9],lo:=4604,hi:=4605); |  | 302:ErrorComUPS[1].Error:=Bit_0; | 302:ErrorComPMM[3].Code[13]:=Byte_0; |  |  | 4605:PMM[2].Phase[1].Current[9]:=Real_0;
mind_bool[303]:=ErrorComUPS[2].Error; | mind[303]:=ErrorComPMM[3].Code[14]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[10],lo:=4606,hi:=4607); |  | 303:ErrorComUPS[2].Error:=Bit_0; | 303:ErrorComPMM[3].Code[14]:=Byte_0; |  |  | 4607:PMM[2].Phase[2].Current[10]:=Real_0;
mind_bool[304]:=KlimaAErrors[10]; | mind[304]:=ErrorComPMM[3].Code[15]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[11],lo:=4608,hi:=4609); |  | 304:KlimaAErrors[10]:=Bit_0; | 304:ErrorComPMM[3].Code[15]:=Byte_0; |  |  | 4609:PMM[2].Phase[2].Current[11]:=Real_0;
mind_bool[305]:=KlimaAErrors[11]; | mind[305]:=ErrorComPMM[3].Code[1]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[12],lo:=4610,hi:=4611); |  | 305:KlimaAErrors[11]:=Bit_0; | 305:ErrorComPMM[3].Code[1]:=Byte_0; |  |  | 4611:PMM[2].Phase[2].Current[12]:=Real_0;
mind_bool[306]:=KlimaAErrors[12]; | mind[306]:=ErrorComPMM[3].Code[2]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[13],lo:=4612,hi:=4613); |  | 306:KlimaAErrors[12]:=Bit_0; | 306:ErrorComPMM[3].Code[2]:=Byte_0; |  |  | 4613:PMM[2].Phase[2].Current[13]:=Real_0;
mind_bool[307]:=KlimaAErrors[13]; | mind[307]:=ErrorComPMM[3].Code[3]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[14],lo:=4614,hi:=4615); |  | 307:KlimaAErrors[13]:=Bit_0; | 307:ErrorComPMM[3].Code[3]:=Byte_0; |  |  | 4615:PMM[2].Phase[2].Current[14]:=Real_0;
mind_bool[308]:=KlimaAErrors[14]; | mind[308]:=ErrorComPMM[3].Code[4]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[15],lo:=4616,hi:=4617); |  | 308:KlimaAErrors[14]:=Bit_0; | 308:ErrorComPMM[3].Code[4]:=Byte_0; |  |  | 4617:PMM[2].Phase[2].Current[15]:=Real_0;
mind_bool[309]:=KlimaAErrors[15]; | mind[309]:=ErrorComPMM[3].Code[5]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[16],lo:=4618,hi:=4619); |  | 309:KlimaAErrors[15]:=Bit_0; | 309:ErrorComPMM[3].Code[5]:=Byte_0; |  |  | 4619:PMM[2].Phase[2].Current[16]:=Real_0;
mind_bool[310]:=KlimaAErrors[16]; | mind[310]:=ErrorComPMM[3].Code[6]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[17],lo:=4620,hi:=4621); |  | 310:KlimaAErrors[16]:=Bit_0; | 310:ErrorComPMM[3].Code[6]:=Byte_0; |  |  | 4621:PMM[2].Phase[2].Current[17]:=Real_0;
mind_bool[311]:=KlimaAErrors[17]; | mind[311]:=ErrorComPMM[3].Code[7]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[18],lo:=4622,hi:=4623); |  | 311:KlimaAErrors[17]:=Bit_0; | 311:ErrorComPMM[3].Code[7]:=Byte_0; |  |  | 4623:PMM[2].Phase[2].Current[18]:=Real_0;
mind_bool[312]:=KlimaAErrors[18]; | mind[312]:=ErrorComPMM[3].Code[8]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[19],lo:=4624,hi:=4625); |  | 312:KlimaAErrors[18]:=Bit_0; | 312:ErrorComPMM[3].Code[8]:=Byte_0; |  |  | 4625:PMM[2].Phase[2].Current[19]:=Real_0;
mind_bool[313]:=KlimaAErrors[19]; | mind[313]:=ErrorComPMM[3].Code[9]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[1],lo:=4626,hi:=4627); |  | 313:KlimaAErrors[19]:=Bit_0; | 313:ErrorComPMM[3].Code[9]:=Byte_0; |  |  | 4627:PMM[2].Phase[2].Current[1]:=Real_0;
mind_bool[314]:=KlimaAErrors[1]; | mind[314]:=ErrorComPMM[3].Status; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[20],lo:=4628,hi:=4629); |  | 314:KlimaAErrors[1]:=Bit_0; | 314:ErrorComPMM[3].Status:=Word_01; |  |  | 4629:PMM[2].Phase[2].Current[20]:=Real_0;
mind_bool[315]:=KlimaAErrors[20]; | mind[315]:=ErrorComUPS[1].Code[10]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[21],lo:=4630,hi:=4631); |  | 315:KlimaAErrors[20]:=Bit_0; | 315:ErrorComUPS[1].Code[10]:=Byte_0; |  |  | 4631:PMM[2].Phase[2].Current[21]:=Real_0;
mind_bool[316]:=KlimaAErrors[21]; | mind[316]:=ErrorComUPS[1].Code[11]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[22],lo:=4632,hi:=4633); |  | 316:KlimaAErrors[21]:=Bit_0; | 316:ErrorComUPS[1].Code[11]:=Byte_0; |  |  | 4633:PMM[2].Phase[2].Current[22]:=Real_0;
mind_bool[317]:=KlimaAErrors[22]; | mind[317]:=ErrorComUPS[1].Code[12]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[23],lo:=4634,hi:=4635); |  | 317:KlimaAErrors[22]:=Bit_0; | 317:ErrorComUPS[1].Code[12]:=Byte_0; |  |  | 4635:PMM[2].Phase[2].Current[23]:=Real_0;
mind_bool[318]:=KlimaAErrors[23]; | mind[318]:=ErrorComUPS[1].Code[13]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[24],lo:=4636,hi:=4637); |  | 318:KlimaAErrors[23]:=Bit_0; | 318:ErrorComUPS[1].Code[13]:=Byte_0; |  |  | 4637:PMM[2].Phase[2].Current[24]:=Real_0;
mind_bool[319]:=KlimaAErrors[24]; | mind[319]:=ErrorComUPS[1].Code[14]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[25],lo:=4638,hi:=4639); |  | 319:KlimaAErrors[24]:=Bit_0; | 319:ErrorComUPS[1].Code[14]:=Byte_0; |  |  | 4639:PMM[2].Phase[2].Current[25]:=Real_0;
mind_bool[320]:=KlimaAErrors[25]; | mind[320]:=ErrorComUPS[1].Code[15]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[26],lo:=4640,hi:=4641); |  | 320:KlimaAErrors[25]:=Bit_0; | 320:ErrorComUPS[1].Code[15]:=Byte_0; |  |  | 4641:PMM[2].Phase[2].Current[26]:=Real_0;
mind_bool[321]:=KlimaAErrors[26]; | mind[321]:=ErrorComUPS[1].Code[1]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[27],lo:=4642,hi:=4643); |  | 321:KlimaAErrors[26]:=Bit_0; | 321:ErrorComUPS[1].Code[1]:=Byte_0; |  |  | 4643:PMM[2].Phase[2].Current[27]:=Real_0;
mind_bool[322]:=KlimaAErrors[27]; | mind[322]:=ErrorComUPS[1].Code[2]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[28],lo:=4644,hi:=4645); |  | 322:KlimaAErrors[27]:=Bit_0; | 322:ErrorComUPS[1].Code[2]:=Byte_0; |  |  | 4645:PMM[2].Phase[2].Current[28]:=Real_0;
mind_bool[323]:=KlimaAErrors[28]; | mind[323]:=ErrorComUPS[1].Code[3]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[29],lo:=4646,hi:=4647); |  | 323:KlimaAErrors[28]:=Bit_0; | 323:ErrorComUPS[1].Code[3]:=Byte_0; |  |  | 4647:PMM[2].Phase[2].Current[29]:=Real_0;
mind_bool[324]:=KlimaAErrors[29]; | mind[324]:=ErrorComUPS[1].Code[4]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[2],lo:=4648,hi:=4649); |  | 324:KlimaAErrors[29]:=Bit_0; | 324:ErrorComUPS[1].Code[4]:=Byte_0; |  |  | 4649:PMM[2].Phase[2].Current[2]:=Real_0;
mind_bool[325]:=KlimaAErrors[2]; | mind[325]:=ErrorComUPS[1].Code[5]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[30],lo:=4650,hi:=4651); |  | 325:KlimaAErrors[2]:=Bit_0; | 325:ErrorComUPS[1].Code[5]:=Byte_0; |  |  | 4651:PMM[2].Phase[2].Current[30]:=Real_0;
mind_bool[326]:=KlimaAErrors[30]; | mind[326]:=ErrorComUPS[1].Code[6]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[31],lo:=4652,hi:=4653); |  | 326:KlimaAErrors[30]:=Bit_0; | 326:ErrorComUPS[1].Code[6]:=Byte_0; |  |  | 4653:PMM[2].Phase[2].Current[31]:=Real_0;
mind_bool[327]:=KlimaAErrors[31]; | mind[327]:=ErrorComUPS[1].Code[7]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[32],lo:=4654,hi:=4655); |  | 327:KlimaAErrors[31]:=Bit_0; | 327:ErrorComUPS[1].Code[7]:=Byte_0; |  |  | 4655:PMM[2].Phase[2].Current[32]:=Real_0;
mind_bool[328]:=KlimaAErrors[32]; | mind[328]:=ErrorComUPS[1].Code[8]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[33],lo:=4656,hi:=4657); |  | 328:KlimaAErrors[32]:=Bit_0; | 328:ErrorComUPS[1].Code[8]:=Byte_0; |  |  | 4657:PMM[2].Phase[2].Current[33]:=Real_0;
mind_bool[329]:=KlimaAErrors[33]; | mind[329]:=ErrorComUPS[1].Code[9]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[34],lo:=4658,hi:=4659); |  | 329:KlimaAErrors[33]:=Bit_0; | 329:ErrorComUPS[1].Code[9]:=Byte_0; |  |  | 4659:PMM[2].Phase[2].Current[34]:=Real_0;
mind_bool[330]:=KlimaAErrors[34]; | mind[330]:=ErrorComUPS[1].Status; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[35],lo:=4660,hi:=4661); |  | 330:KlimaAErrors[34]:=Bit_0; | 330:ErrorComUPS[1].Status:=Word_01; |  |  | 4661:PMM[2].Phase[2].Current[35]:=Real_0;
mind_bool[331]:=KlimaAErrors[35]; | mind[331]:=ErrorComUPS[2].Code[10]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[36],lo:=4662,hi:=4663); |  | 331:KlimaAErrors[35]:=Bit_0; | 331:ErrorComUPS[2].Code[10]:=Byte_0; |  |  | 4663:PMM[2].Phase[2].Current[36]:=Real_0;
mind_bool[332]:=KlimaAErrors[36]; | mind[332]:=ErrorComUPS[2].Code[11]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[37],lo:=4664,hi:=4665); |  | 332:KlimaAErrors[36]:=Bit_0; | 332:ErrorComUPS[2].Code[11]:=Byte_0; |  |  | 4665:PMM[2].Phase[2].Current[37]:=Real_0;
mind_bool[333]:=KlimaAErrors[37]; | mind[333]:=ErrorComUPS[2].Code[12]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[38],lo:=4666,hi:=4667); |  | 333:KlimaAErrors[37]:=Bit_0; | 333:ErrorComUPS[2].Code[12]:=Byte_0; |  |  | 4667:PMM[2].Phase[2].Current[38]:=Real_0;
mind_bool[334]:=KlimaAErrors[38]; | mind[334]:=ErrorComUPS[2].Code[13]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[39],lo:=4668,hi:=4669); |  | 334:KlimaAErrors[38]:=Bit_0; | 334:ErrorComUPS[2].Code[13]:=Byte_0; |  |  | 4669:PMM[2].Phase[2].Current[39]:=Real_0;
mind_bool[335]:=KlimaAErrors[39]; | mind[335]:=ErrorComUPS[2].Code[14]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[3],lo:=4670,hi:=4671); |  | 335:KlimaAErrors[39]:=Bit_0; | 335:ErrorComUPS[2].Code[14]:=Byte_0; |  |  | 4671:PMM[2].Phase[2].Current[3]:=Real_0;
mind_bool[336]:=KlimaAErrors[3]; | mind[336]:=ErrorComUPS[2].Code[15]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[40],lo:=4672,hi:=4673); |  | 336:KlimaAErrors[3]:=Bit_0; | 336:ErrorComUPS[2].Code[15]:=Byte_0; |  |  | 4673:PMM[2].Phase[2].Current[40]:=Real_0;
mind_bool[337]:=KlimaAErrors[40]; | mind[337]:=ErrorComUPS[2].Code[1]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[41],lo:=4674,hi:=4675); |  | 337:KlimaAErrors[40]:=Bit_0; | 337:ErrorComUPS[2].Code[1]:=Byte_0; |  |  | 4675:PMM[2].Phase[2].Current[41]:=Real_0;
mind_bool[338]:=KlimaAErrors[4]; | mind[338]:=ErrorComUPS[2].Code[2]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[42],lo:=4676,hi:=4677); |  | 338:KlimaAErrors[4]:=Bit_0; | 338:ErrorComUPS[2].Code[2]:=Byte_0; |  |  | 4677:PMM[2].Phase[2].Current[42]:=Real_0;
mind_bool[339]:=KlimaAErrors[5]; | mind[339]:=ErrorComUPS[2].Code[3]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[4],lo:=4678,hi:=4679); |  | 339:KlimaAErrors[5]:=Bit_0; | 339:ErrorComUPS[2].Code[3]:=Byte_0; |  |  | 4679:PMM[2].Phase[2].Current[4]:=Real_0;
mind_bool[340]:=KlimaAErrors[6]; | mind[340]:=ErrorComUPS[2].Code[4]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[5],lo:=4680,hi:=4681); |  | 340:KlimaAErrors[6]:=Bit_0; | 340:ErrorComUPS[2].Code[4]:=Byte_0; |  |  | 4681:PMM[2].Phase[2].Current[5]:=Real_0;
mind_bool[341]:=KlimaAErrors[7]; | mind[341]:=ErrorComUPS[2].Code[5]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[6],lo:=4682,hi:=4683); |  | 341:KlimaAErrors[7]:=Bit_0; | 341:ErrorComUPS[2].Code[5]:=Byte_0; |  |  | 4683:PMM[2].Phase[2].Current[6]:=Real_0;
mind_bool[342]:=KlimaAErrors[8]; | mind[342]:=ErrorComUPS[2].Code[6]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[7],lo:=4684,hi:=4685); |  | 342:KlimaAErrors[8]:=Bit_0; | 342:ErrorComUPS[2].Code[6]:=Byte_0; |  |  | 4685:PMM[2].Phase[2].Current[7]:=Real_0;
mind_bool[343]:=KlimaAErrors[9]; | mind[343]:=ErrorComUPS[2].Code[7]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[8],lo:=4686,hi:=4687); |  | 343:KlimaAErrors[9]:=Bit_0; | 343:ErrorComUPS[2].Code[7]:=Byte_0; |  |  | 4687:PMM[2].Phase[2].Current[8]:=Real_0;
mind_bool[344]:=KlimaBErrors[10]; | mind[344]:=ErrorComUPS[2].Code[8]; |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[9],lo:=4688,hi:=4689); |  | 344:KlimaBErrors[10]:=Bit_0; | 344:ErrorComUPS[2].Code[8]:=Byte_0; |  |  | 4689:PMM[2].Phase[2].Current[9]:=Real_0;
mind_bool[345]:=KlimaBErrors[11]; | mind[345]:=ErrorComUPS[2].Code[9]; |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[10],lo:=4690,hi:=4691); |  | 345:KlimaBErrors[11]:=Bit_0; | 345:ErrorComUPS[2].Code[9]:=Byte_0; |  |  | 4691:PMM[2].Phase[3].Current[10]:=Real_0;
mind_bool[346]:=KlimaBErrors[12]; | mind[346]:=ErrorComUPS[2].Status; |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[11],lo:=4692,hi:=4693); |  | 346:KlimaBErrors[12]:=Bit_0; | 346:ErrorComUPS[2].Status:=Word_01; |  |  | 4693:PMM[2].Phase[3].Current[11]:=Real_0;
mind_bool[347]:=KlimaBErrors[13]; | mind[347]:=KlimaGal.GrelecStatus; |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[12],lo:=4694,hi:=4695); |  | 347:KlimaBErrors[13]:=Bit_0; | 347:KlimaGal.GrelecStatus:=Byte_0; |  |  | 4695:PMM[2].Phase[3].Current[12]:=Real_0;
mind_bool[348]:=KlimaBErrors[14]; | mind[348]:=KlimaGal.IzhodniVentStatus; |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[13],lo:=4696,hi:=4697); |  | 348:KlimaBErrors[14]:=Bit_0; | 348:KlimaGal.IzhodniVentStatus:=Byte_0; |  |  | 4697:PMM[2].Phase[3].Current[13]:=Real_0;
mind_bool[349]:=KlimaBErrors[15]; | mind[349]:=KlimaGal.KompresorStatus; |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[14],lo:=4698,hi:=4699); |  | 349:KlimaBErrors[15]:=Bit_0; | 349:KlimaGal.KompresorStatus:=Byte_0; |  |  | 4699:PMM[2].Phase[3].Current[14]:=Real_0;
mind_bool[350]:=KlimaBErrors[16]; | mind[350]:=KlimaGal.VlazilecStatus; |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[15],lo:=4700,hi:=4701); |  | 350:KlimaBErrors[16]:=Bit_0; | 350:KlimaGal.VlazilecStatus:=Byte_0; |  |  | 4701:PMM[2].Phase[3].Current[15]:=Real_0;
mind_bool[351]:=KlimaBErrors[17]; | mind[351]:=PMMgal.AlarmPhase[1].GlobalAlarmReg; |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[16],lo:=4702,hi:=4703); |  | 351:KlimaBErrors[17]:=Bit_0; | 351:PMMgal.AlarmPhase[1].GlobalAlarmReg:=Word_01; |  |  | 4703:PMM[2].Phase[3].Current[16]:=Real_0;
mind_bool[352]:=KlimaBErrors[18]; | mind[352]:=PMMgal.AlarmPhase[2].GlobalAlarmReg; |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[17],lo:=4704,hi:=4705); |  | 352:KlimaBErrors[18]:=Bit_0; | 352:PMMgal.AlarmPhase[2].GlobalAlarmReg:=Word_01; |  |  | 4705:PMM[2].Phase[3].Current[17]:=Real_0;
mind_bool[353]:=KlimaBErrors[19]; | mind[353]:=PMMgal.AlarmPhase[3].GlobalAlarmReg; |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[18],lo:=4706,hi:=4707); |  | 353:KlimaBErrors[19]:=Bit_0; | 353:PMMgal.AlarmPhase[3].GlobalAlarmReg:=Word_01; |  |  | 4707:PMM[2].Phase[3].Current[18]:=Real_0;
mind_bool[354]:=KlimaBErrors[1]; | mind[354]:=kom_nast_cas_izpada; |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[19],lo:=4708,hi:=4709); |  | 354:KlimaBErrors[1]:=Bit_0; | 354:kom_nast_cas_izpada:=Word_01; |  |  | 4709:PMM[2].Phase[3].Current[19]:=Real_0;
mind_bool[355]:=KlimaBErrors[20]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[1],lo:=4710,hi:=4711); |  | 355:KlimaBErrors[20]:=Bit_0; |  |  |  | 4711:PMM[2].Phase[3].Current[1]:=Real_0;
mind_bool[356]:=KlimaBErrors[21]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[20],lo:=4712,hi:=4713); |  | 356:KlimaBErrors[21]:=Bit_0; |  |  |  | 4713:PMM[2].Phase[3].Current[20]:=Real_0;
mind_bool[357]:=KlimaBErrors[22]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[21],lo:=4714,hi:=4715); |  | 357:KlimaBErrors[22]:=Bit_0; |  |  |  | 4715:PMM[2].Phase[3].Current[21]:=Real_0;
mind_bool[358]:=KlimaBErrors[23]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[22],lo:=4716,hi:=4717); |  | 358:KlimaBErrors[23]:=Bit_0; |  |  |  | 4717:PMM[2].Phase[3].Current[22]:=Real_0;
mind_bool[359]:=KlimaBErrors[24]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[23],lo:=4718,hi:=4719); |  | 359:KlimaBErrors[24]:=Bit_0; |  |  |  | 4719:PMM[2].Phase[3].Current[23]:=Real_0;
mind_bool[360]:=KlimaBErrors[25]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[24],lo:=4720,hi:=4721); |  | 360:KlimaBErrors[25]:=Bit_0; |  |  |  | 4721:PMM[2].Phase[3].Current[24]:=Real_0;
mind_bool[361]:=KlimaBErrors[26]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[25],lo:=4722,hi:=4723); |  | 361:KlimaBErrors[26]:=Bit_0; |  |  |  | 4723:PMM[2].Phase[3].Current[25]:=Real_0;
mind_bool[362]:=KlimaBErrors[27]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[26],lo:=4724,hi:=4725); |  | 362:KlimaBErrors[27]:=Bit_0; |  |  |  | 4725:PMM[2].Phase[3].Current[26]:=Real_0;
mind_bool[363]:=KlimaBErrors[28]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[27],lo:=4726,hi:=4727); |  | 363:KlimaBErrors[28]:=Bit_0; |  |  |  | 4727:PMM[2].Phase[3].Current[27]:=Real_0;
mind_bool[364]:=KlimaBErrors[29]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[28],lo:=4728,hi:=4729); |  | 364:KlimaBErrors[29]:=Bit_0; |  |  |  | 4729:PMM[2].Phase[3].Current[28]:=Real_0;
mind_bool[365]:=KlimaBErrors[2]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[29],lo:=4730,hi:=4731); |  | 365:KlimaBErrors[2]:=Bit_0; |  |  |  | 4731:PMM[2].Phase[3].Current[29]:=Real_0;
mind_bool[366]:=KlimaBErrors[30]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[2],lo:=4732,hi:=4733); |  | 366:KlimaBErrors[30]:=Bit_0; |  |  |  | 4733:PMM[2].Phase[3].Current[2]:=Real_0;
mind_bool[367]:=KlimaBErrors[31]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[30],lo:=4734,hi:=4735); |  | 367:KlimaBErrors[31]:=Bit_0; |  |  |  | 4735:PMM[2].Phase[3].Current[30]:=Real_0;
mind_bool[368]:=KlimaBErrors[32]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[31],lo:=4736,hi:=4737); |  | 368:KlimaBErrors[32]:=Bit_0; |  |  |  | 4737:PMM[2].Phase[3].Current[31]:=Real_0;
mind_bool[369]:=KlimaBErrors[33]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[32],lo:=4738,hi:=4739); |  | 369:KlimaBErrors[33]:=Bit_0; |  |  |  | 4739:PMM[2].Phase[3].Current[32]:=Real_0;
mind_bool[370]:=KlimaBErrors[34]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[33],lo:=4740,hi:=4741); |  | 370:KlimaBErrors[34]:=Bit_0; |  |  |  | 4741:PMM[2].Phase[3].Current[33]:=Real_0;
mind_bool[371]:=KlimaBErrors[35]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[34],lo:=4742,hi:=4743); |  | 371:KlimaBErrors[35]:=Bit_0; |  |  |  | 4743:PMM[2].Phase[3].Current[34]:=Real_0;
mind_bool[372]:=KlimaBErrors[36]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[35],lo:=4744,hi:=4745); |  | 372:KlimaBErrors[36]:=Bit_0; |  |  |  | 4745:PMM[2].Phase[3].Current[35]:=Real_0;
mind_bool[373]:=KlimaBErrors[37]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[36],lo:=4746,hi:=4747); |  | 373:KlimaBErrors[37]:=Bit_0; |  |  |  | 4747:PMM[2].Phase[3].Current[36]:=Real_0;
mind_bool[374]:=KlimaBErrors[38]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[37],lo:=4748,hi:=4749); |  | 374:KlimaBErrors[38]:=Bit_0; |  |  |  | 4749:PMM[2].Phase[3].Current[37]:=Real_0;
mind_bool[375]:=KlimaBErrors[39]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[38],lo:=4750,hi:=4751); |  | 375:KlimaBErrors[39]:=Bit_0; |  |  |  | 4751:PMM[2].Phase[3].Current[38]:=Real_0;
mind_bool[376]:=KlimaBErrors[3]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[39],lo:=4752,hi:=4753); |  | 376:KlimaBErrors[3]:=Bit_0; |  |  |  | 4753:PMM[2].Phase[3].Current[39]:=Real_0;
mind_bool[377]:=KlimaBErrors[40]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[3],lo:=4754,hi:=4755); |  | 377:KlimaBErrors[40]:=Bit_0; |  |  |  | 4755:PMM[2].Phase[3].Current[3]:=Real_0;
mind_bool[378]:=KlimaBErrors[4]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[40],lo:=4756,hi:=4757); |  | 378:KlimaBErrors[4]:=Bit_0; |  |  |  | 4757:PMM[2].Phase[3].Current[40]:=Real_0;
mind_bool[379]:=KlimaBErrors[5]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[41],lo:=4758,hi:=4759); |  | 379:KlimaBErrors[5]:=Bit_0; |  |  |  | 4759:PMM[2].Phase[3].Current[41]:=Real_0;
mind_bool[380]:=KlimaBErrors[6]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[42],lo:=4760,hi:=4761); |  | 380:KlimaBErrors[6]:=Bit_0; |  |  |  | 4761:PMM[2].Phase[3].Current[42]:=Real_0;
mind_bool[381]:=KlimaBErrors[7]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[4],lo:=4762,hi:=4763); |  | 381:KlimaBErrors[7]:=Bit_0; |  |  |  | 4763:PMM[2].Phase[3].Current[4]:=Real_0;
mind_bool[382]:=KlimaBErrors[8]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[5],lo:=4764,hi:=4765); |  | 382:KlimaBErrors[8]:=Bit_0; |  |  |  | 4765:PMM[2].Phase[3].Current[5]:=Real_0;
mind_bool[383]:=KlimaBErrors[9]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[6],lo:=4766,hi:=4767); |  | 383:KlimaBErrors[9]:=Bit_0; |  |  |  | 4767:PMM[2].Phase[3].Current[6]:=Real_0;
mind_bool[384]:=KlimaGal.AlarmKompresor1; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[7],lo:=4768,hi:=4769); |  | 384:KlimaGal.AlarmKompresor1:=Bit_0; |  |  |  | 4769:PMM[2].Phase[3].Current[7]:=Real_0;
mind_bool[385]:=KlimaGal.AlarmKompresor2; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[8],lo:=4770,hi:=4771); |  | 385:KlimaGal.AlarmKompresor2:=Bit_0; |  |  |  | 4771:PMM[2].Phase[3].Current[8]:=Real_0;
mind_bool[386]:=KlimaGal.Deluje; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[9],lo:=4772,hi:=4773); |  | 386:KlimaGal.Deluje:=Bit_0; |  |  |  | 4773:PMM[2].Phase[3].Current[9]:=Real_0;
mind_bool[387]:=KlimaGal.EnergySaving; |  |  |  | Read_Real(rVar:=PMM[2].PowerFactorPhaseA,lo:=4774,hi:=4775); |  | 387:KlimaGal.EnergySaving:=Bit_0; |  |  |  | 4775:PMM[2].PowerFactorPhaseA:=Real_0;
mind_bool[388]:=KlimaGal.FaultyEPROM; |  |  |  | Read_Real(rVar:=PMM[2].PowerFactorPhaseB,lo:=4776,hi:=4777); |  | 388:KlimaGal.FaultyEPROM:=Bit_0; |  |  |  | 4777:PMM[2].PowerFactorPhaseB:=Real_0;
mind_bool[389]:=KlimaGal.FenThermalCutout; |  |  |  | Read_Real(rVar:=PMM[2].PowerFactorPhaseC,lo:=4778,hi:=4779); |  | 389:KlimaGal.FenThermalCutout:=Bit_0; |  |  |  | 4779:PMM[2].PowerFactorPhaseC:=Real_0;
mind_bool[390]:=KlimaGal.GeneralAlarm; |  |  |  | Read_Real(rVar:=PMM[2].TotalActivePower_kW,lo:=4780,hi:=4781); |  | 390:KlimaGal.GeneralAlarm:=Bit_0; |  |  |  | 4781:PMM[2].TotalActivePower_kW:=Real_0;
mind_bool[391]:=KlimaGal.Kompresor1naMejiObrUr; |  |  |  | Read_Real(rVar:=PMM[2].TotalAparentPower_kVA,lo:=4782,hi:=4783); |  | 391:KlimaGal.Kompresor1naMejiObrUr:=Bit_0; |  |  |  | 4783:PMM[2].TotalAparentPower_kVA:=Real_0;
mind_bool[392]:=KlimaGal.Kompresor2naMejiObrUr; |  |  |  | Read_Real(rVar:=PMM[2].TotalPowerFactor,lo:=4784,hi:=4785); |  | 392:KlimaGal.Kompresor2naMejiObrUr:=Bit_0; |  |  |  | 4785:PMM[2].TotalPowerFactor:=Real_0;
mind_bool[393]:=KlimaGal.Napaka; |  |  |  | Read_Real(rVar:=PMM[2].TotalReactivePower_kVAR,lo:=4786,hi:=4787); |  | 393:KlimaGal.Napaka:=Bit_0; |  |  |  | 4787:PMM[2].TotalReactivePower_kVAR:=Real_0;
mind_bool[394]:=KlimaGal.NapakaPriPretokuZraka; |  |  |  | Read_Real(rVar:=PMM[2].VoltageBetweenPhaseAB_V,lo:=4788,hi:=4789); |  | 394:KlimaGal.NapakaPriPretokuZraka:=Bit_0; |  |  |  | 4789:PMM[2].VoltageBetweenPhaseAB_V:=Real_0;
mind_bool[395]:=KlimaGal.NapakaSenzorPovratVode; |  |  |  | Read_Real(rVar:=PMM[2].VoltageBetweenPhaseAN_V,lo:=4790,hi:=4791); |  | 395:KlimaGal.NapakaSenzorPovratVode:=Bit_0; |  |  |  | 4791:PMM[2].VoltageBetweenPhaseAN_V:=Real_0;
mind_bool[396]:=KlimaGal.NapakaSenzorTempIzpiha; |  |  |  | Read_Real(rVar:=PMM[2].VoltageBetweenPhaseBC_V,lo:=4792,hi:=4793); |  | 396:KlimaGal.NapakaSenzorTempIzpiha:=Bit_0; |  |  |  | 4793:PMM[2].VoltageBetweenPhaseBC_V:=Real_0;
mind_bool[397]:=KlimaGal.NapakaSenzorTempProstora; |  |  |  | Read_Real(rVar:=PMM[2].VoltageBetweenPhaseBN_V,lo:=4794,hi:=4795); |  | 397:KlimaGal.NapakaSenzorTempProstora:=Bit_0; |  |  |  | 4795:PMM[2].VoltageBetweenPhaseBN_V:=Real_0;
mind_bool[398]:=KlimaGal.NapakaSenzorVlaznosti; |  |  |  | Read_Real(rVar:=PMM[2].VoltageBetweenPhaseCA_V,lo:=4796,hi:=4797); |  | 398:KlimaGal.NapakaSenzorVlaznosti:=Bit_0; |  |  |  | 4797:PMM[2].VoltageBetweenPhaseCA_V:=Real_0;
mind_bool[399]:=KlimaGal.NapakaSenzorZunanjeTemp; |  |  |  | Read_Real(rVar:=PMM[2].VoltageBetweenPhaseCN_V,lo:=4798,hi:=4799); |  | 399:KlimaGal.NapakaSenzorZunanjeTemp:=Bit_0; |  |  |  | 4799:PMM[2].VoltageBetweenPhaseCN_V:=Real_0;
mind_bool[400]:=KlimaGal.NiTokaVVlazilcu; |  |  |  | Read_Real(rVar:=PMM[3].ActivePowerPhaseA_kW,lo:=4800,hi:=4801); |  | 400:KlimaGal.NiTokaVVlazilcu:=Bit_0; |  |  |  | 4801:PMM[3].ActivePowerPhaseA_kW:=Real_0;
mind_bool[401]:=KlimaGal.NiVodeVVlazilcu; |  |  |  | Read_Real(rVar:=PMM[3].ActivePowerPhaseB_kW,lo:=4802,hi:=4803); |  | 401:KlimaGal.NiVodeVVlazilcu:=Bit_0; |  |  |  | 4803:PMM[3].ActivePowerPhaseB_kW:=Real_0;
mind_bool[402]:=KlimaGal.NizekPritiskKompresor1; |  |  |  | Read_Real(rVar:=PMM[3].ActivePowerPhaseC_kW,lo:=4804,hi:=4805); |  | 402:KlimaGal.NizekPritiskKompresor1:=Bit_0; |  |  |  | 4805:PMM[3].ActivePowerPhaseC_kW:=Real_0;
mind_bool[403]:=KlimaGal.NizekPritiskKompresor2; |  |  |  | Read_Real(rVar:=PMM[3].AverageCurrent_A,lo:=4806,hi:=4807); |  | 403:KlimaGal.NizekPritiskKompresor2:=Bit_0; |  |  |  | 4807:PMM[3].AverageCurrent_A:=Real_0;
mind_bool[404]:=KlimaGal.NizkaTempPovratneVode; |  |  |  | Read_Real(rVar:=PMM[3].AveragePhaseToNeutral_V,lo:=4808,hi:=4809); |  | 404:KlimaGal.NizkaTempPovratneVode:=Bit_0; |  |  |  | 4809:PMM[3].AveragePhaseToNeutral_V:=Real_0;
mind_bool[405]:=KlimaGal.NizkaTempVProstoru; |  |  |  | Read_Real(rVar:=PMM[3].AveragePhaseToPhase_V,lo:=4810,hi:=4811); |  | 405:KlimaGal.NizkaTempVProstoru:=Bit_0; |  |  |  | 4811:PMM[3].AveragePhaseToPhase_V:=Real_0;
mind_bool[406]:=KlimaGal.NizkaVlaznost; |  |  |  | Read_Real(rVar:=PMM[3].CurrentInPhaseA_A,lo:=4812,hi:=4813); |  | 406:KlimaGal.NizkaVlaznost:=Bit_0; |  |  |  | 4813:PMM[3].CurrentInPhaseA_A:=Real_0;
mind_bool[407]:=KlimaGal.OnOffEnablingBySupervisor; |  |  |  | Read_Real(rVar:=PMM[3].CurrentInPhaseB_A,lo:=4814,hi:=4815); |  | 407:KlimaGal.OnOffEnablingBySupervisor:=Bit_0; |  |  |  | 4815:PMM[3].CurrentInPhaseB_A:=Real_0;
mind_bool[408]:=KlimaGal.PozarniAlarm; |  |  |  | Read_Real(rVar:=PMM[3].CurrentInPhaseC_A,lo:=4816,hi:=4817); |  | 408:KlimaGal.PozarniAlarm:=Bit_0; |  |  |  | 4817:PMM[3].CurrentInPhaseC_A:=Real_0;
mind_bool[409]:=KlimaGal.Razvlazevanje; |  |  |  | Read_Real(rVar:=PMM[3].EnergyConsumed_kWh,lo:=4818,hi:=4819); |  | 409:KlimaGal.Razvlazevanje:=Bit_0; |  |  |  | 4819:PMM[3].EnergyConsumed_kWh:=Real_0;
mind_bool[410]:=KlimaGal.RemoteOFFtoOutput; |  |  |  | Read_Real(rVar:=PMM[3].Frequency_Hz,lo:=4820,hi:=4821); |  | 410:KlimaGal.RemoteOFFtoOutput:=Bit_0; |  |  |  | 4821:PMM[3].Frequency_Hz:=Real_0;
mind_bool[411]:=KlimaGal.RemoteOnOff; |  |  |  | Read_Real(rVar:=PMM[3].NeutralCurrent_A,lo:=4822,hi:=4823); |  | 411:KlimaGal.RemoteOnOff:=Bit_0; |  |  |  | 4823:PMM[3].NeutralCurrent_A:=Real_0;
mind_bool[412]:=KlimaGal.RocniIzklop; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[10],lo:=4824,hi:=4825); |  | 412:KlimaGal.RocniIzklop:=Bit_0; |  |  |  | 4825:PMM[3].Phase[1].Current[10]:=Real_0;
mind_bool[413]:=KlimaGal.SenzorjiStatus; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[11],lo:=4826,hi:=4827); |  | 413:KlimaGal.SenzorjiStatus:=Bit_0; |  |  |  | 4827:PMM[3].Phase[1].Current[11]:=Real_0;
mind_bool[414]:=KlimaGal.StoppedByAlarms; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[12],lo:=4828,hi:=4829); |  | 414:KlimaGal.StoppedByAlarms:=Bit_0; |  |  |  | 4829:PMM[3].Phase[1].Current[12]:=Real_0;
mind_bool[415]:=KlimaGal.ThermalCutoutHeater1; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[13],lo:=4830,hi:=4831); |  | 415:KlimaGal.ThermalCutoutHeater1:=Bit_0; |  |  |  | 4831:PMM[3].Phase[1].Current[13]:=Real_0;
mind_bool[416]:=KlimaGal.ThermalCutoutHeater2; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[14],lo:=4832,hi:=4833); |  | 416:KlimaGal.ThermalCutoutHeater2:=Bit_0; |  |  |  | 4833:PMM[3].Phase[1].Current[14]:=Real_0;
mind_bool[417]:=KlimaGal.UnitOnOff; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[15],lo:=4834,hi:=4835); |  | 417:KlimaGal.UnitOnOff:=Bit_0; |  |  |  | 4835:PMM[3].Phase[1].Current[15]:=Real_0;
mind_bool[418]:=KlimaGal.VentilatorNaMejiObrUr; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[16],lo:=4836,hi:=4837); |  | 418:KlimaGal.VentilatorNaMejiObrUr:=Bit_0; |  |  |  | 4837:PMM[3].Phase[1].Current[16]:=Real_0;
mind_bool[419]:=KlimaGal.VentilGretjeOdpiranje; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[17],lo:=4838,hi:=4839); |  | 419:KlimaGal.VentilGretjeOdpiranje:=Bit_0; |  |  |  | 4839:PMM[3].Phase[1].Current[17]:=Real_0;
mind_bool[420]:=KlimaGal.VentilGretjeZapiranje; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[18],lo:=4840,hi:=4841); |  | 420:KlimaGal.VentilGretjeZapiranje:=Bit_0; |  |  |  | 4841:PMM[3].Phase[1].Current[18]:=Real_0;
mind_bool[421]:=KlimaGal.VentilHlajenjeOdpiranje; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[19],lo:=4842,hi:=4843); |  | 421:KlimaGal.VentilHlajenjeOdpiranje:=Bit_0; |  |  |  | 4843:PMM[3].Phase[1].Current[19]:=Real_0;
mind_bool[422]:=KlimaGal.VentilHlajenjeZapiranje; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[1],lo:=4844,hi:=4845); |  | 422:KlimaGal.VentilHlajenjeZapiranje:=Bit_0; |  |  |  | 4845:PMM[3].Phase[1].Current[1]:=Real_0;
mind_bool[423]:=KlimaGal.VisokaTempPovratneVode; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[20],lo:=4846,hi:=4847); |  | 423:KlimaGal.VisokaTempPovratneVode:=Bit_0; |  |  |  | 4847:PMM[3].Phase[1].Current[20]:=Real_0;
mind_bool[424]:=KlimaGal.VisokaTempVProstoru; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[21],lo:=4848,hi:=4849); |  | 424:KlimaGal.VisokaTempVProstoru:=Bit_0; |  |  |  | 4849:PMM[3].Phase[1].Current[21]:=Real_0;
mind_bool[425]:=KlimaGal.VisokaVlaznost; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[22],lo:=4850,hi:=4851); |  | 425:KlimaGal.VisokaVlaznost:=Bit_0; |  |  |  | 4851:PMM[3].Phase[1].Current[22]:=Real_0;
mind_bool[426]:=KlimaGal.VisokTokVVlazilcu; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[23],lo:=4852,hi:=4853); |  | 426:KlimaGal.VisokTokVVlazilcu:=Bit_0; |  |  |  | 4853:PMM[3].Phase[1].Current[23]:=Real_0;
mind_bool[427]:=KlimaGal.Vlazenje; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[24],lo:=4854,hi:=4855); |  | 427:KlimaGal.Vlazenje:=Bit_0; |  |  |  | 4855:PMM[3].Phase[1].Current[24]:=Real_0;
mind_bool[428]:=KlimaGal.ZamasenFilter; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[25],lo:=4856,hi:=4857); |  | 428:KlimaGal.ZamasenFilter:=Bit_0; |  |  |  | 4857:PMM[3].Phase[1].Current[25]:=Real_0;
mind_bool[429]:=PMM1OverVoltage; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[26],lo:=4858,hi:=4859); |  | 429:PMM1OverVoltage:=Bit_0; |  |  |  | 4859:PMM[3].Phase[1].Current[26]:=Real_0;
mind_bool[430]:=PMM2OverVoltage; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[27],lo:=4860,hi:=4861); |  | 430:PMM2OverVoltage:=Bit_0; |  |  |  | 4861:PMM[3].Phase[1].Current[27]:=Real_0;
mind_bool[431]:=PMM3OverVoltage; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[28],lo:=4862,hi:=4863); |  | 431:PMM3OverVoltage:=Bit_0; |  |  |  | 4863:PMM[3].Phase[1].Current[28]:=Real_0;
mind_bool[432]:=PMMgal.Napaka; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[29],lo:=4864,hi:=4865); |  | 432:PMMgal.Napaka:=Bit_0; |  |  |  | 4865:PMM[3].Phase[1].Current[29]:=Real_0;
mind_bool[433]:=ErrCommScada2; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[2],lo:=4866,hi:=4867); |  | 433:ErrCommScada2:=Bit_0; |  |  |  | 4867:PMM[3].Phase[1].Current[2]:=Real_0;
mind_bool[434]:=ComSCADA2; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[30],lo:=4868,hi:=4869); |  | 434:ComSCADA2:=Bit_0; |  |  |  | 4869:PMM[3].Phase[1].Current[30]:=Real_0;
mind_bool[435]:=ComSCADA3; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[31],lo:=4870,hi:=4871); |  | 435:ComSCADA3:=Bit_0; |  |  |  | 4871:PMM[3].Phase[1].Current[31]:=Real_0;
mind_bool[436]:=Circ_Vpis_Dnevne_energija_scada1; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[32],lo:=4872,hi:=4873); |  | 436:Circ_Vpis_Dnevne_energija_scada1:=Bit_0; |  |  |  | 4873:PMM[3].Phase[1].Current[32]:=Real_0;
mind_bool[437]:=Circ_Vpis_Dnevne_energija_scada2; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[33],lo:=4874,hi:=4875); |  | 437:Circ_Vpis_Dnevne_energija_scada2:=Bit_0; |  |  |  | 4875:PMM[3].Phase[1].Current[33]:=Real_0;
mind_bool[438]:=Circ_Vpis_Tedenska_energija_scada1; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[34],lo:=4876,hi:=4877); |  | 438:Circ_Vpis_Tedenska_energija_scada1:=Bit_0; |  |  |  | 4877:PMM[3].Phase[1].Current[34]:=Real_0;
mind_bool[439]:=Circ_Vpis_Tedenska_energija_scada2; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[35],lo:=4878,hi:=4879); |  | 439:Circ_Vpis_Tedenska_energija_scada2:=Bit_0; |  |  |  | 4879:PMM[3].Phase[1].Current[35]:=Real_0;
mind_bool[440]:=Circ_Vpis_Mesecna_energija_scada1; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[36],lo:=4880,hi:=4881); |  | 440:Circ_Vpis_Mesecna_energija_scada1:=Bit_0; |  |  |  | 4881:PMM[3].Phase[1].Current[36]:=Real_0;
mind_bool[441]:=Circ_Vpis_Mesecna_energija_scada2; |  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[37],lo:=4882,hi:=4883); |  | 441:Circ_Vpis_Mesecna_energija_scada2:=Bit_0; |  |  |  | 4883:PMM[3].Phase[1].Current[37]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[38],lo:=4884,hi:=4885); | [5 empty] | 4885:PMM[3].Phase[1].Current[38]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[39],lo:=4886,hi:=4887); | [5 empty] | 4887:PMM[3].Phase[1].Current[39]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[3],lo:=4888,hi:=4889); | [5 empty] | 4889:PMM[3].Phase[1].Current[3]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[40],lo:=4890,hi:=4891); | [5 empty] | 4891:PMM[3].Phase[1].Current[40]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[41],lo:=4892,hi:=4893); | [5 empty] | 4893:PMM[3].Phase[1].Current[41]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[42],lo:=4894,hi:=4895); | [5 empty] | 4895:PMM[3].Phase[1].Current[42]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[4],lo:=4896,hi:=4897); | [5 empty] | 4897:PMM[3].Phase[1].Current[4]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[5],lo:=4898,hi:=4899); | [5 empty] | 4899:PMM[3].Phase[1].Current[5]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[6],lo:=4900,hi:=4901); | [5 empty] | 4901:PMM[3].Phase[1].Current[6]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[7],lo:=4902,hi:=4903); | [5 empty] | 4903:PMM[3].Phase[1].Current[7]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[8],lo:=4904,hi:=4905); | [5 empty] | 4905:PMM[3].Phase[1].Current[8]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[1].Current[9],lo:=4906,hi:=4907); | [5 empty] | 4907:PMM[3].Phase[1].Current[9]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[10],lo:=4908,hi:=4909); | [5 empty] | 4909:PMM[3].Phase[2].Current[10]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[11],lo:=4910,hi:=4911); | [5 empty] | 4911:PMM[3].Phase[2].Current[11]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[12],lo:=4912,hi:=4913); | [5 empty] | 4913:PMM[3].Phase[2].Current[12]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[13],lo:=4914,hi:=4915); | [5 empty] | 4915:PMM[3].Phase[2].Current[13]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[14],lo:=4916,hi:=4917); | [5 empty] | 4917:PMM[3].Phase[2].Current[14]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[15],lo:=4918,hi:=4919); | [5 empty] | 4919:PMM[3].Phase[2].Current[15]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[16],lo:=4920,hi:=4921); | [5 empty] | 4921:PMM[3].Phase[2].Current[16]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[17],lo:=4922,hi:=4923); | [5 empty] | 4923:PMM[3].Phase[2].Current[17]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[18],lo:=4924,hi:=4925); | [5 empty] | 4925:PMM[3].Phase[2].Current[18]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[19],lo:=4926,hi:=4927); | [5 empty] | 4927:PMM[3].Phase[2].Current[19]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[1],lo:=4928,hi:=4929); | [5 empty] | 4929:PMM[3].Phase[2].Current[1]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[20],lo:=4930,hi:=4931); | [5 empty] | 4931:PMM[3].Phase[2].Current[20]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[21],lo:=4932,hi:=4933); | [5 empty] | 4933:PMM[3].Phase[2].Current[21]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[22],lo:=4934,hi:=4935); | [5 empty] | 4935:PMM[3].Phase[2].Current[22]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[23],lo:=4936,hi:=4937); | [5 empty] | 4937:PMM[3].Phase[2].Current[23]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[24],lo:=4938,hi:=4939); | [5 empty] | 4939:PMM[3].Phase[2].Current[24]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[25],lo:=4940,hi:=4941); | [5 empty] | 4941:PMM[3].Phase[2].Current[25]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[26],lo:=4942,hi:=4943); | [5 empty] | 4943:PMM[3].Phase[2].Current[26]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[27],lo:=4944,hi:=4945); | [5 empty] | 4945:PMM[3].Phase[2].Current[27]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[28],lo:=4946,hi:=4947); | [5 empty] | 4947:PMM[3].Phase[2].Current[28]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[29],lo:=4948,hi:=4949); | [5 empty] | 4949:PMM[3].Phase[2].Current[29]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[2],lo:=4950,hi:=4951); | [5 empty] | 4951:PMM[3].Phase[2].Current[2]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[30],lo:=4952,hi:=4953); | [5 empty] | 4953:PMM[3].Phase[2].Current[30]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[31],lo:=4954,hi:=4955); | [5 empty] | 4955:PMM[3].Phase[2].Current[31]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[32],lo:=4956,hi:=4957); | [5 empty] | 4957:PMM[3].Phase[2].Current[32]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[33],lo:=4958,hi:=4959); | [5 empty] | 4959:PMM[3].Phase[2].Current[33]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[34],lo:=4960,hi:=4961); | [5 empty] | 4961:PMM[3].Phase[2].Current[34]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[35],lo:=4962,hi:=4963); | [5 empty] | 4963:PMM[3].Phase[2].Current[35]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[36],lo:=4964,hi:=4965); | [5 empty] | 4965:PMM[3].Phase[2].Current[36]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[37],lo:=4966,hi:=4967); | [5 empty] | 4967:PMM[3].Phase[2].Current[37]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[38],lo:=4968,hi:=4969); | [5 empty] | 4969:PMM[3].Phase[2].Current[38]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[39],lo:=4970,hi:=4971); | [5 empty] | 4971:PMM[3].Phase[2].Current[39]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[3],lo:=4972,hi:=4973); | [5 empty] | 4973:PMM[3].Phase[2].Current[3]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[40],lo:=4974,hi:=4975); | [5 empty] | 4975:PMM[3].Phase[2].Current[40]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[41],lo:=4976,hi:=4977); | [5 empty] | 4977:PMM[3].Phase[2].Current[41]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[42],lo:=4978,hi:=4979); | [5 empty] | 4979:PMM[3].Phase[2].Current[42]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[4],lo:=4980,hi:=4981); | [5 empty] | 4981:PMM[3].Phase[2].Current[4]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[5],lo:=4982,hi:=4983); | [5 empty] | 4983:PMM[3].Phase[2].Current[5]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[6],lo:=4984,hi:=4985); | [5 empty] | 4985:PMM[3].Phase[2].Current[6]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[7],lo:=4986,hi:=4987); | [5 empty] | 4987:PMM[3].Phase[2].Current[7]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[8],lo:=4988,hi:=4989); | [5 empty] | 4989:PMM[3].Phase[2].Current[8]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[2].Current[9],lo:=4990,hi:=4991); | [5 empty] | 4991:PMM[3].Phase[2].Current[9]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[10],lo:=4992,hi:=4993); | [5 empty] | 4993:PMM[3].Phase[3].Current[10]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[11],lo:=4994,hi:=4995); | [5 empty] | 4995:PMM[3].Phase[3].Current[11]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[12],lo:=4996,hi:=4997); | [5 empty] | 4997:PMM[3].Phase[3].Current[12]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[13],lo:=4998,hi:=4999); | [5 empty] | 4999:PMM[3].Phase[3].Current[13]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[14],lo:=5000,hi:=5001); | [5 empty] | 5001:PMM[3].Phase[3].Current[14]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[15],lo:=5002,hi:=5003); | [5 empty] | 5003:PMM[3].Phase[3].Current[15]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[16],lo:=5004,hi:=5005); | [5 empty] | 5005:PMM[3].Phase[3].Current[16]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[17],lo:=5006,hi:=5007); | [5 empty] | 5007:PMM[3].Phase[3].Current[17]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[18],lo:=5008,hi:=5009); | [5 empty] | 5009:PMM[3].Phase[3].Current[18]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[19],lo:=5010,hi:=5011); | [5 empty] | 5011:PMM[3].Phase[3].Current[19]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[1],lo:=5012,hi:=5013); | [5 empty] | 5013:PMM[3].Phase[3].Current[1]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[20],lo:=5014,hi:=5015); | [5 empty] | 5015:PMM[3].Phase[3].Current[20]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[21],lo:=5016,hi:=5017); | [5 empty] | 5017:PMM[3].Phase[3].Current[21]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[22],lo:=5018,hi:=5019); | [5 empty] | 5019:PMM[3].Phase[3].Current[22]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[23],lo:=5020,hi:=5021); | [5 empty] | 5021:PMM[3].Phase[3].Current[23]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[24],lo:=5022,hi:=5023); | [5 empty] | 5023:PMM[3].Phase[3].Current[24]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[25],lo:=5024,hi:=5025); | [5 empty] | 5025:PMM[3].Phase[3].Current[25]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[26],lo:=5026,hi:=5027); | [5 empty] | 5027:PMM[3].Phase[3].Current[26]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[27],lo:=5028,hi:=5029); | [5 empty] | 5029:PMM[3].Phase[3].Current[27]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[28],lo:=5030,hi:=5031); | [5 empty] | 5031:PMM[3].Phase[3].Current[28]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[29],lo:=5032,hi:=5033); | [5 empty] | 5033:PMM[3].Phase[3].Current[29]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[2],lo:=5034,hi:=5035); | [5 empty] | 5035:PMM[3].Phase[3].Current[2]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[30],lo:=5036,hi:=5037); | [5 empty] | 5037:PMM[3].Phase[3].Current[30]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[31],lo:=5038,hi:=5039); | [5 empty] | 5039:PMM[3].Phase[3].Current[31]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[32],lo:=5040,hi:=5041); | [5 empty] | 5041:PMM[3].Phase[3].Current[32]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[33],lo:=5042,hi:=5043); | [5 empty] | 5043:PMM[3].Phase[3].Current[33]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[34],lo:=5044,hi:=5045); | [5 empty] | 5045:PMM[3].Phase[3].Current[34]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[35],lo:=5046,hi:=5047); | [5 empty] | 5047:PMM[3].Phase[3].Current[35]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[36],lo:=5048,hi:=5049); | [5 empty] | 5049:PMM[3].Phase[3].Current[36]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[37],lo:=5050,hi:=5051); | [5 empty] | 5051:PMM[3].Phase[3].Current[37]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[38],lo:=5052,hi:=5053); | [5 empty] | 5053:PMM[3].Phase[3].Current[38]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[39],lo:=5054,hi:=5055); | [5 empty] | 5055:PMM[3].Phase[3].Current[39]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[3],lo:=5056,hi:=5057); | [5 empty] | 5057:PMM[3].Phase[3].Current[3]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[40],lo:=5058,hi:=5059); | [5 empty] | 5059:PMM[3].Phase[3].Current[40]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[41],lo:=5060,hi:=5061); | [5 empty] | 5061:PMM[3].Phase[3].Current[41]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[42],lo:=5062,hi:=5063); | [5 empty] | 5063:PMM[3].Phase[3].Current[42]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[4],lo:=5064,hi:=5065); | [5 empty] | 5065:PMM[3].Phase[3].Current[4]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[5],lo:=5066,hi:=5067); | [5 empty] | 5067:PMM[3].Phase[3].Current[5]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[6],lo:=5068,hi:=5069); | [5 empty] | 5069:PMM[3].Phase[3].Current[6]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[7],lo:=5070,hi:=5071); | [5 empty] | 5071:PMM[3].Phase[3].Current[7]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[8],lo:=5072,hi:=5073); | [5 empty] | 5073:PMM[3].Phase[3].Current[8]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].Phase[3].Current[9],lo:=5074,hi:=5075); | [5 empty] | 5075:PMM[3].Phase[3].Current[9]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].PowerFactorPhaseA,lo:=5076,hi:=5077); | [5 empty] | 5077:PMM[3].PowerFactorPhaseA:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].PowerFactorPhaseB,lo:=5078,hi:=5079); | [5 empty] | 5079:PMM[3].PowerFactorPhaseB:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].PowerFactorPhaseC,lo:=5080,hi:=5081); | [5 empty] | 5081:PMM[3].PowerFactorPhaseC:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].TotalActivePower_kW,lo:=5082,hi:=5083); | [5 empty] | 5083:PMM[3].TotalActivePower_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].TotalAparentPower_kVA,lo:=5084,hi:=5085); | [5 empty] | 5085:PMM[3].TotalAparentPower_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].TotalPowerFactor,lo:=5086,hi:=5087); | [5 empty] | 5087:PMM[3].TotalPowerFactor:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].TotalReactivePower_kVAR,lo:=5088,hi:=5089); | [5 empty] | 5089:PMM[3].TotalReactivePower_kVAR:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].VoltageBetweenPhaseAB_V,lo:=5090,hi:=5091); | [5 empty] | 5091:PMM[3].VoltageBetweenPhaseAB_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].VoltageBetweenPhaseAN_V,lo:=5092,hi:=5093); | [5 empty] | 5093:PMM[3].VoltageBetweenPhaseAN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].VoltageBetweenPhaseBC_V,lo:=5094,hi:=5095); | [5 empty] | 5095:PMM[3].VoltageBetweenPhaseBC_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].VoltageBetweenPhaseBN_V,lo:=5096,hi:=5097); | [5 empty] | 5097:PMM[3].VoltageBetweenPhaseBN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].VoltageBetweenPhaseCA_V,lo:=5098,hi:=5099); | [5 empty] | 5099:PMM[3].VoltageBetweenPhaseCA_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[3].VoltageBetweenPhaseCN_V,lo:=5100,hi:=5101); | [5 empty] | 5101:PMM[3].VoltageBetweenPhaseCN_V:=Real_0;
|  |  |  | Read_Real(rVar:=rVersion,lo:=5102,hi:=5103); | [5 empty] | 5103:rVersion:=Real_0;
|  |  |  | Read_Real(rVar:=SenzorTemp[1],lo:=5104,hi:=5105); | [5 empty] | 5105:SenzorTemp[1]:=Real_0;
|  |  |  | Read_Real(rVar:=SenzorTemp[2],lo:=5106,hi:=5107); | [5 empty] | 5107:SenzorTemp[2]:=Real_0;
|  |  |  | Read_Real(rVar:=SenzorVlaga[1],lo:=5108,hi:=5109); | [5 empty] | 5109:SenzorVlaga[1]:=Real_0;
|  |  |  | Read_Real(rVar:=SenzorVlaga[2],lo:=5110,hi:=5111); | [5 empty] | 5111:SenzorVlaga[2]:=Real_0;
|  |  |  | Read_Real(rVar:=TempMaxPoint,lo:=5112,hi:=5113); | [5 empty] | 5113:TempMaxPoint:=Real_0;
|  |  |  | Read_Real(rVar:=TempSetPoint,lo:=5114,hi:=5115); | [5 empty] | 5115:TempSetPoint:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[1].EstimatedChargeRemaining,lo:=5116,hi:=5117); | [5 empty] | 5117:UPS[1].EstimatedChargeRemaining:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[1].EstimatedMinutesRemaining,lo:=5118,hi:=5119); | [5 empty] | 5119:UPS[1].EstimatedMinutesRemaining:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[1].IzhodMocL1,lo:=5120,hi:=5121); | [5 empty] | 5121:UPS[1].IzhodMocL1:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[1].IzhodMocL2,lo:=5122,hi:=5123); | [5 empty] | 5123:UPS[1].IzhodMocL2:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[1].IzhodMocL3,lo:=5124,hi:=5125); | [5 empty] | 5125:UPS[1].IzhodMocL3:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[1].NapetostBaterije,lo:=5126,hi:=5127); | [5 empty] | 5127:UPS[1].NapetostBaterije:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[1].TemperaturaBaterije,lo:=5128,hi:=5129); | [5 empty] | 5129:UPS[1].TemperaturaBaterije:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[1].VhodFrekvencaL1,lo:=5130,hi:=5131); | [5 empty] | 5131:UPS[1].VhodFrekvencaL1:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[1].VhodFrekvencaL2,lo:=5132,hi:=5133); | [5 empty] | 5133:UPS[1].VhodFrekvencaL2:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[1].VhodFrekvencaL3,lo:=5134,hi:=5135); | [5 empty] | 5135:UPS[1].VhodFrekvencaL3:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[1].VhodNapetostL1,lo:=5136,hi:=5137); | [5 empty] | 5137:UPS[1].VhodNapetostL1:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[1].VhodNapetostL2,lo:=5138,hi:=5139); | [5 empty] | 5139:UPS[1].VhodNapetostL2:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[1].VhodNapetostL3,lo:=5140,hi:=5141); | [5 empty] | 5141:UPS[1].VhodNapetostL3:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[2].EstimatedChargeRemaining,lo:=5142,hi:=5143); | [5 empty] | 5143:UPS[2].EstimatedChargeRemaining:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[2].EstimatedMinutesRemaining,lo:=5144,hi:=5145); | [5 empty] | 5145:UPS[2].EstimatedMinutesRemaining:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[2].IzhodMocL1,lo:=5146,hi:=5147); | [5 empty] | 5147:UPS[2].IzhodMocL1:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[2].IzhodMocL2,lo:=5148,hi:=5149); | [5 empty] | 5149:UPS[2].IzhodMocL2:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[2].IzhodMocL3,lo:=5150,hi:=5151); | [5 empty] | 5151:UPS[2].IzhodMocL3:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[2].NapetostBaterije,lo:=5152,hi:=5153); | [5 empty] | 5153:UPS[2].NapetostBaterije:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[2].TemperaturaBaterije,lo:=5154,hi:=5155); | [5 empty] | 5155:UPS[2].TemperaturaBaterije:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[2].VhodFrekvencaL1,lo:=5156,hi:=5157); | [5 empty] | 5157:UPS[2].VhodFrekvencaL1:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[2].VhodFrekvencaL2,lo:=5158,hi:=5159); | [5 empty] | 5159:UPS[2].VhodFrekvencaL2:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[2].VhodFrekvencaL3,lo:=5160,hi:=5161); | [5 empty] | 5161:UPS[2].VhodFrekvencaL3:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[2].VhodNapetostL1,lo:=5162,hi:=5163); | [5 empty] | 5163:UPS[2].VhodNapetostL1:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[2].VhodNapetostL2,lo:=5164,hi:=5165); | [5 empty] | 5165:UPS[2].VhodNapetostL2:=Real_0;
|  |  |  | Read_Real(rVar:=UPS[2].VhodNapetostL3,lo:=5166,hi:=5167); | [5 empty] | 5167:UPS[2].VhodNapetostL3:=Real_0;
|  |  |  | Read_Real(rVar:=KlimaGal.NastMaxTemp,lo:=5168,hi:=5169); | [5 empty] | 5169:KlimaGal.NastMaxTemp:=Real_0;
|  |  |  | Read_Real(rVar:=KlimaGal.NastMaxVlaznost,lo:=5170,hi:=5171); | [5 empty] | 5171:KlimaGal.NastMaxVlaznost:=Real_0;
|  |  |  | Read_Real(rVar:=KlimaGal.NastMinTemp,lo:=5172,hi:=5173); | [5 empty] | 5173:KlimaGal.NastMinTemp:=Real_0;
|  |  |  | Read_Real(rVar:=KlimaGal.NastMinVlaznost,lo:=5174,hi:=5175); | [5 empty] | 5175:KlimaGal.NastMinVlaznost:=Real_0;
|  |  |  | Read_Real(rVar:=KlimaGal.NastTempProstora,lo:=5176,hi:=5177); | [5 empty] | 5177:KlimaGal.NastTempProstora:=Real_0;
|  |  |  | Read_Real(rVar:=KlimaGal.NastVlaznost,lo:=5178,hi:=5179); | [5 empty] | 5179:KlimaGal.NastVlaznost:=Real_0;
|  |  |  | Read_Real(rVar:=KlimaGal.ObratovalneUre,lo:=5180,hi:=5181); | [5 empty] | 5181:KlimaGal.ObratovalneUre:=Real_0;
|  |  |  | Read_Real(rVar:=KlimaGal.TemperaturaProstora,lo:=5182,hi:=5183); | [5 empty] | 5183:KlimaGal.TemperaturaProstora:=Real_0;
|  |  |  | Read_Real(rVar:=KlimaGal.TempIzpihanegaZraka,lo:=5184,hi:=5185); | [5 empty] | 5185:KlimaGal.TempIzpihanegaZraka:=Real_0;
|  |  |  | Read_Real(rVar:=KlimaGal.TempPovratneVode,lo:=5186,hi:=5187); | [5 empty] | 5187:KlimaGal.TempPovratneVode:=Real_0;
|  |  |  | Read_Real(rVar:=KlimaGal.VlaznostProstora,lo:=5188,hi:=5189); | [5 empty] | 5189:KlimaGal.VlaznostProstora:=Real_0;
|  |  |  | Read_Real(rVar:=KlimaGal.ZunanjaTemp,lo:=5190,hi:=5191); | [5 empty] | 5191:KlimaGal.ZunanjaTemp:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza01,lo:=5192,hi:=5193); | [5 empty] | 5193:PMMfaza01:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza02,lo:=5194,hi:=5195); | [5 empty] | 5195:PMMfaza02:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza03,lo:=5196,hi:=5197); | [5 empty] | 5197:PMMfaza03:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza04,lo:=5198,hi:=5199); | [5 empty] | 5199:PMMfaza04:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza05,lo:=5200,hi:=5201); | [5 empty] | 5201:PMMfaza05:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza06,lo:=5202,hi:=5203); | [5 empty] | 5203:PMMfaza06:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza07,lo:=5204,hi:=5205); | [5 empty] | 5205:PMMfaza07:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza08,lo:=5206,hi:=5207); | [5 empty] | 5207:PMMfaza08:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza09,lo:=5208,hi:=5209); | [5 empty] | 5209:PMMfaza09:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza10,lo:=5210,hi:=5211); | [5 empty] | 5211:PMMfaza10:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza11,lo:=5212,hi:=5213); | [5 empty] | 5213:PMMfaza11:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza12,lo:=5214,hi:=5215); | [5 empty] | 5215:PMMfaza12:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza13,lo:=5216,hi:=5217); | [5 empty] | 5217:PMMfaza13:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza14,lo:=5218,hi:=5219); | [5 empty] | 5219:PMMfaza14:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza15,lo:=5220,hi:=5221); | [5 empty] | 5221:PMMfaza15:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza16,lo:=5222,hi:=5223); | [5 empty] | 5223:PMMfaza16:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza17,lo:=5224,hi:=5225); | [5 empty] | 5225:PMMfaza17:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza18,lo:=5226,hi:=5227); | [5 empty] | 5227:PMMfaza18:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza19,lo:=5228,hi:=5229); | [5 empty] | 5229:PMMfaza19:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza20,lo:=5230,hi:=5231); | [5 empty] | 5231:PMMfaza20:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza21,lo:=5232,hi:=5233); | [5 empty] | 5233:PMMfaza21:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza22,lo:=5234,hi:=5235); | [5 empty] | 5235:PMMfaza22:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza23,lo:=5236,hi:=5237); | [5 empty] | 5237:PMMfaza23:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza24,lo:=5238,hi:=5239); | [5 empty] | 5239:PMMfaza24:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza25,lo:=5240,hi:=5241); | [5 empty] | 5241:PMMfaza25:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza26,lo:=5242,hi:=5243); | [5 empty] | 5243:PMMfaza26:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza27,lo:=5244,hi:=5245); | [5 empty] | 5245:PMMfaza27:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza28,lo:=5246,hi:=5247); | [5 empty] | 5247:PMMfaza28:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza29,lo:=5248,hi:=5249); | [5 empty] | 5249:PMMfaza29:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza30,lo:=5250,hi:=5251); | [5 empty] | 5251:PMMfaza30:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza31,lo:=5252,hi:=5253); | [5 empty] | 5253:PMMfaza31:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza32,lo:=5254,hi:=5255); | [5 empty] | 5255:PMMfaza32:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza33,lo:=5256,hi:=5257); | [5 empty] | 5257:PMMfaza33:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza34,lo:=5258,hi:=5259); | [5 empty] | 5259:PMMfaza34:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza35,lo:=5260,hi:=5261); | [5 empty] | 5261:PMMfaza35:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza36,lo:=5262,hi:=5263); | [5 empty] | 5263:PMMfaza36:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza37,lo:=5264,hi:=5265); | [5 empty] | 5265:PMMfaza37:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza38,lo:=5266,hi:=5267); | [5 empty] | 5267:PMMfaza38:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza39,lo:=5268,hi:=5269); | [5 empty] | 5269:PMMfaza39:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza40,lo:=5270,hi:=5271); | [5 empty] | 5271:PMMfaza40:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza41,lo:=5272,hi:=5273); | [5 empty] | 5273:PMMfaza41:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza42,lo:=5274,hi:=5275); | [5 empty] | 5275:PMMfaza42:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[10],lo:=5276,hi:=5277); | [5 empty] | 5277:PMMfaza60[10]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[11],lo:=5278,hi:=5279); | [5 empty] | 5279:PMMfaza60[11]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[12],lo:=5280,hi:=5281); | [5 empty] | 5281:PMMfaza60[12]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[13],lo:=5282,hi:=5283); | [5 empty] | 5283:PMMfaza60[13]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[14],lo:=5284,hi:=5285); | [5 empty] | 5285:PMMfaza60[14]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[15],lo:=5286,hi:=5287); | [5 empty] | 5287:PMMfaza60[15]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[16],lo:=5288,hi:=5289); | [5 empty] | 5289:PMMfaza60[16]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[17],lo:=5290,hi:=5291); | [5 empty] | 5291:PMMfaza60[17]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[18],lo:=5292,hi:=5293); | [5 empty] | 5293:PMMfaza60[18]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[19],lo:=5294,hi:=5295); | [5 empty] | 5295:PMMfaza60[19]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[1],lo:=5296,hi:=5297); | [5 empty] | 5297:PMMfaza60[1]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[20],lo:=5298,hi:=5299); | [5 empty] | 5299:PMMfaza60[20]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[21],lo:=5300,hi:=5301); | [5 empty] | 5301:PMMfaza60[21]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[22],lo:=5302,hi:=5303); | [5 empty] | 5303:PMMfaza60[22]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[23],lo:=5304,hi:=5305); | [5 empty] | 5305:PMMfaza60[23]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[24],lo:=5306,hi:=5307); | [5 empty] | 5307:PMMfaza60[24]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[25],lo:=5308,hi:=5309); | [5 empty] | 5309:PMMfaza60[25]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[26],lo:=5310,hi:=5311); | [5 empty] | 5311:PMMfaza60[26]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[27],lo:=5312,hi:=5313); | [5 empty] | 5313:PMMfaza60[27]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[28],lo:=5314,hi:=5315); | [5 empty] | 5315:PMMfaza60[28]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[29],lo:=5316,hi:=5317); | [5 empty] | 5317:PMMfaza60[29]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[2],lo:=5318,hi:=5319); | [5 empty] | 5319:PMMfaza60[2]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[30],lo:=5320,hi:=5321); | [5 empty] | 5321:PMMfaza60[30]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[31],lo:=5322,hi:=5323); | [5 empty] | 5323:PMMfaza60[31]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[32],lo:=5324,hi:=5325); | [5 empty] | 5325:PMMfaza60[32]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[33],lo:=5326,hi:=5327); | [5 empty] | 5327:PMMfaza60[33]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[34],lo:=5328,hi:=5329); | [5 empty] | 5329:PMMfaza60[34]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[35],lo:=5330,hi:=5331); | [5 empty] | 5331:PMMfaza60[35]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[36],lo:=5332,hi:=5333); | [5 empty] | 5333:PMMfaza60[36]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[37],lo:=5334,hi:=5335); | [5 empty] | 5335:PMMfaza60[37]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[38],lo:=5336,hi:=5337); | [5 empty] | 5337:PMMfaza60[38]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[39],lo:=5338,hi:=5339); | [5 empty] | 5339:PMMfaza60[39]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[3],lo:=5340,hi:=5341); | [5 empty] | 5341:PMMfaza60[3]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[40],lo:=5342,hi:=5343); | [5 empty] | 5343:PMMfaza60[40]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[41],lo:=5344,hi:=5345); | [5 empty] | 5345:PMMfaza60[41]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[42],lo:=5346,hi:=5347); | [5 empty] | 5347:PMMfaza60[42]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[4],lo:=5348,hi:=5349); | [5 empty] | 5349:PMMfaza60[4]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[5],lo:=5350,hi:=5351); | [5 empty] | 5351:PMMfaza60[5]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[6],lo:=5352,hi:=5353); | [5 empty] | 5353:PMMfaza60[6]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[7],lo:=5354,hi:=5355); | [5 empty] | 5355:PMMfaza60[7]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[8],lo:=5356,hi:=5357); | [5 empty] | 5357:PMMfaza60[8]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza60[9],lo:=5358,hi:=5359); | [5 empty] | 5359:PMMfaza60[9]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[10],lo:=5360,hi:=5361); | [5 empty] | 5361:PMMfaza80[10]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[11],lo:=5362,hi:=5363); | [5 empty] | 5363:PMMfaza80[11]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[12],lo:=5364,hi:=5365); | [5 empty] | 5365:PMMfaza80[12]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[13],lo:=5366,hi:=5367); | [5 empty] | 5367:PMMfaza80[13]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[14],lo:=5368,hi:=5369); | [5 empty] | 5369:PMMfaza80[14]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[15],lo:=5370,hi:=5371); | [5 empty] | 5371:PMMfaza80[15]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[16],lo:=5372,hi:=5373); | [5 empty] | 5373:PMMfaza80[16]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[17],lo:=5374,hi:=5375); | [5 empty] | 5375:PMMfaza80[17]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[18],lo:=5376,hi:=5377); | [5 empty] | 5377:PMMfaza80[18]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[19],lo:=5378,hi:=5379); | [5 empty] | 5379:PMMfaza80[19]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[1],lo:=5380,hi:=5381); | [5 empty] | 5381:PMMfaza80[1]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[20],lo:=5382,hi:=5383); | [5 empty] | 5383:PMMfaza80[20]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[21],lo:=5384,hi:=5385); | [5 empty] | 5385:PMMfaza80[21]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[22],lo:=5386,hi:=5387); | [5 empty] | 5387:PMMfaza80[22]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[23],lo:=5388,hi:=5389); | [5 empty] | 5389:PMMfaza80[23]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[24],lo:=5390,hi:=5391); | [5 empty] | 5391:PMMfaza80[24]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[25],lo:=5392,hi:=5393); | [5 empty] | 5393:PMMfaza80[25]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[26],lo:=5394,hi:=5395); | [5 empty] | 5395:PMMfaza80[26]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[27],lo:=5396,hi:=5397); | [5 empty] | 5397:PMMfaza80[27]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[28],lo:=5398,hi:=5399); | [5 empty] | 5399:PMMfaza80[28]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[29],lo:=5400,hi:=5401); | [5 empty] | 5401:PMMfaza80[29]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[2],lo:=5402,hi:=5403); | [5 empty] | 5403:PMMfaza80[2]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[30],lo:=5404,hi:=5405); | [5 empty] | 5405:PMMfaza80[30]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[31],lo:=5406,hi:=5407); | [5 empty] | 5407:PMMfaza80[31]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[32],lo:=5408,hi:=5409); | [5 empty] | 5409:PMMfaza80[32]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[33],lo:=5410,hi:=5411); | [5 empty] | 5411:PMMfaza80[33]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[34],lo:=5412,hi:=5413); | [5 empty] | 5413:PMMfaza80[34]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[35],lo:=5414,hi:=5415); | [5 empty] | 5415:PMMfaza80[35]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[36],lo:=5416,hi:=5417); | [5 empty] | 5417:PMMfaza80[36]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[37],lo:=5418,hi:=5419); | [5 empty] | 5419:PMMfaza80[37]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[38],lo:=5420,hi:=5421); | [5 empty] | 5421:PMMfaza80[38]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[39],lo:=5422,hi:=5423); | [5 empty] | 5423:PMMfaza80[39]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[3],lo:=5424,hi:=5425); | [5 empty] | 5425:PMMfaza80[3]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[40],lo:=5426,hi:=5427); | [5 empty] | 5427:PMMfaza80[40]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[41],lo:=5428,hi:=5429); | [5 empty] | 5429:PMMfaza80[41]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[42],lo:=5430,hi:=5431); | [5 empty] | 5431:PMMfaza80[42]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[4],lo:=5432,hi:=5433); | [5 empty] | 5433:PMMfaza80[4]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[5],lo:=5434,hi:=5435); | [5 empty] | 5435:PMMfaza80[5]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[6],lo:=5436,hi:=5437); | [5 empty] | 5437:PMMfaza80[6]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[7],lo:=5438,hi:=5439); | [5 empty] | 5439:PMMfaza80[7]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[8],lo:=5440,hi:=5441); | [5 empty] | 5441:PMMfaza80[8]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMfaza80[9],lo:=5442,hi:=5443); | [5 empty] | 5443:PMMfaza80[9]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.ActivePowerPhaseA_kW,lo:=5444,hi:=5445); | [5 empty] | 5445:PMMgal.ActivePowerPhaseA_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.ActivePowerPhaseB_kW,lo:=5446,hi:=5447); | [5 empty] | 5447:PMMgal.ActivePowerPhaseB_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.ActivePowerPhaseC_kW,lo:=5448,hi:=5449); | [5 empty] | 5449:PMMgal.ActivePowerPhaseC_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.AverageCurrent_A,lo:=5450,hi:=5451); | [5 empty] | 5451:PMMgal.AverageCurrent_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.AveragePhaseToNeutral_V,lo:=5452,hi:=5453); | [5 empty] | 5453:PMMgal.AveragePhaseToNeutral_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.AveragePhaseToPhase_V,lo:=5454,hi:=5455); | [5 empty] | 5455:PMMgal.AveragePhaseToPhase_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.CurrentInPhaseA_A,lo:=5456,hi:=5457); | [5 empty] | 5457:PMMgal.CurrentInPhaseA_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.CurrentInPhaseB_A,lo:=5458,hi:=5459); | [5 empty] | 5459:PMMgal.CurrentInPhaseB_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.CurrentInPhaseC_A,lo:=5460,hi:=5461); | [5 empty] | 5461:PMMgal.CurrentInPhaseC_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.EnergyConsumed_kWh,lo:=5462,hi:=5463); | [5 empty] | 5463:PMMgal.EnergyConsumed_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Frequency_Hz,lo:=5464,hi:=5465); | [5 empty] | 5465:PMMgal.Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.NeutralCurrent_A,lo:=5466,hi:=5467); | [5 empty] | 5467:PMMgal.NeutralCurrent_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[10],lo:=5468,hi:=5469); | [5 empty] | 5469:PMMgal.Phase[1].Current[10]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[11],lo:=5470,hi:=5471); | [5 empty] | 5471:PMMgal.Phase[1].Current[11]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[12],lo:=5472,hi:=5473); | [5 empty] | 5473:PMMgal.Phase[1].Current[12]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[13],lo:=5474,hi:=5475); | [5 empty] | 5475:PMMgal.Phase[1].Current[13]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[14],lo:=5476,hi:=5477); | [5 empty] | 5477:PMMgal.Phase[1].Current[14]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[15],lo:=5478,hi:=5479); | [5 empty] | 5479:PMMgal.Phase[1].Current[15]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[16],lo:=5480,hi:=5481); | [5 empty] | 5481:PMMgal.Phase[1].Current[16]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[17],lo:=5482,hi:=5483); | [5 empty] | 5483:PMMgal.Phase[1].Current[17]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[18],lo:=5484,hi:=5485); | [5 empty] | 5485:PMMgal.Phase[1].Current[18]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[19],lo:=5486,hi:=5487); | [5 empty] | 5487:PMMgal.Phase[1].Current[19]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[1],lo:=5488,hi:=5489); | [5 empty] | 5489:PMMgal.Phase[1].Current[1]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[20],lo:=5490,hi:=5491); | [5 empty] | 5491:PMMgal.Phase[1].Current[20]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[21],lo:=5492,hi:=5493); | [5 empty] | 5493:PMMgal.Phase[1].Current[21]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[22],lo:=5494,hi:=5495); | [5 empty] | 5495:PMMgal.Phase[1].Current[22]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[23],lo:=5496,hi:=5497); | [5 empty] | 5497:PMMgal.Phase[1].Current[23]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[24],lo:=5498,hi:=5499); | [5 empty] | 5499:PMMgal.Phase[1].Current[24]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[25],lo:=5500,hi:=5501); | [5 empty] | 5501:PMMgal.Phase[1].Current[25]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[26],lo:=5502,hi:=5503); | [5 empty] | 5503:PMMgal.Phase[1].Current[26]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[27],lo:=5504,hi:=5505); | [5 empty] | 5505:PMMgal.Phase[1].Current[27]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[28],lo:=5506,hi:=5507); | [5 empty] | 5507:PMMgal.Phase[1].Current[28]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[29],lo:=5508,hi:=5509); | [5 empty] | 5509:PMMgal.Phase[1].Current[29]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[2],lo:=5510,hi:=5511); | [5 empty] | 5511:PMMgal.Phase[1].Current[2]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[30],lo:=5512,hi:=5513); | [5 empty] | 5513:PMMgal.Phase[1].Current[30]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[31],lo:=5514,hi:=5515); | [5 empty] | 5515:PMMgal.Phase[1].Current[31]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[32],lo:=5516,hi:=5517); | [5 empty] | 5517:PMMgal.Phase[1].Current[32]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[33],lo:=5518,hi:=5519); | [5 empty] | 5519:PMMgal.Phase[1].Current[33]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[34],lo:=5520,hi:=5521); | [5 empty] | 5521:PMMgal.Phase[1].Current[34]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[35],lo:=5522,hi:=5523); | [5 empty] | 5523:PMMgal.Phase[1].Current[35]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[36],lo:=5524,hi:=5525); | [5 empty] | 5525:PMMgal.Phase[1].Current[36]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[37],lo:=5526,hi:=5527); | [5 empty] | 5527:PMMgal.Phase[1].Current[37]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[38],lo:=5528,hi:=5529); | [5 empty] | 5529:PMMgal.Phase[1].Current[38]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[39],lo:=5530,hi:=5531); | [5 empty] | 5531:PMMgal.Phase[1].Current[39]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[3],lo:=5532,hi:=5533); | [5 empty] | 5533:PMMgal.Phase[1].Current[3]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[40],lo:=5534,hi:=5535); | [5 empty] | 5535:PMMgal.Phase[1].Current[40]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[41],lo:=5536,hi:=5537); | [5 empty] | 5537:PMMgal.Phase[1].Current[41]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[42],lo:=5538,hi:=5539); | [5 empty] | 5539:PMMgal.Phase[1].Current[42]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[4],lo:=5540,hi:=5541); | [5 empty] | 5541:PMMgal.Phase[1].Current[4]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[5],lo:=5542,hi:=5543); | [5 empty] | 5543:PMMgal.Phase[1].Current[5]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[6],lo:=5544,hi:=5545); | [5 empty] | 5545:PMMgal.Phase[1].Current[6]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[7],lo:=5546,hi:=5547); | [5 empty] | 5547:PMMgal.Phase[1].Current[7]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[8],lo:=5548,hi:=5549); | [5 empty] | 5549:PMMgal.Phase[1].Current[8]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[1].Current[9],lo:=5550,hi:=5551); | [5 empty] | 5551:PMMgal.Phase[1].Current[9]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[2].Current[10],lo:=5552,hi:=5553); | [5 empty] | 5553:PMMgal.Phase[2].Current[10]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[2].Current[11],lo:=5554,hi:=5555); | [5 empty] | 5555:PMMgal.Phase[2].Current[11]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[2].Current[12],lo:=5556,hi:=5557); | [5 empty] | 5557:PMMgal.Phase[2].Current[12]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[2].Current[13],lo:=5558,hi:=5559); | [5 empty] | 5559:PMMgal.Phase[2].Current[13]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[2].Current[14],lo:=5560,hi:=5561); | [5 empty] | 5561:PMMgal.Phase[2].Current[14]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[2].Current[15],lo:=5562,hi:=5563); | [5 empty] | 5563:PMMgal.Phase[2].Current[15]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[2].Current[16],lo:=5564,hi:=5565); | [5 empty] | 5565:PMMgal.Phase[2].Current[16]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[2].Current[17],lo:=5566,hi:=5567); | [5 empty] | 5567:PMMgal.Phase[2].Current[17]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[2].Current[18],lo:=5568,hi:=5569); | [5 empty] | 5569:PMMgal.Phase[2].Current[18]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[2].Current[19],lo:=5570,hi:=5571); | [5 empty] | 5571:PMMgal.Phase[2].Current[19]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[2].Current[1],lo:=5572,hi:=5573); | [5 empty] | 5573:PMMgal.Phase[2].Current[1]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[2].Current[20],lo:=5574,hi:=5575); | [5 empty] | 5575:PMMgal.Phase[2].Current[20]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[2].Current[21],lo:=5576,hi:=5577); | [5 empty] | 5577:PMMgal.Phase[2].Current[21]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[2].Current[22],lo:=5578,hi:=5579); | [5 empty] | 5579:PMMgal.Phase[2].Current[22]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[2].Current[23],lo:=5580,hi:=5581); | [5 empty] | 5581:PMMgal.Phase[2].Current[23]:=Real_0;
|  |  |  | Read_Real(rVar:=PMMgal.Phase[2].Current[24],lo:=5582,hi:=5583); | [5 empty] | 5583:PMMgal.Phase[2].Current[24]:=Real_0;
|  |  |  | Read_Real(rVar:=TempAlarmPoint,lo:=5584,hi:=5585); | [5 empty] | 5585:TempAlarmPoint:=Real_0;
|  |  |  | Read_Real(rVar:=RazlikaUr,lo:=5586,hi:=5587); | [5 empty] | 5587:RazlikaUr:=Real_0;
|  |  |  | Read_Real(rVar:=Circ[1].MaximumDemandA2,lo:=5588,hi:=5589); | [5 empty] | 5589:Circ[1].MaximumDemandA2:=Real_0;
|  |  |  | Read_Real(rVar:=Circ[1].MaximumDemandA3,lo:=5590,hi:=5591); | [5 empty] | 5591:Circ[1].MaximumDemandA3:=Real_0;
|  |  |  | Read_Real(rVar:=Circ[1].RazEner_D_SCADA,lo:=5592,hi:=5593); | [5 empty] | 5593:Circ[1].RazEner_D_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=Circ[1].RazEner_T_SCADA,lo:=5594,hi:=5595); | [5 empty] | 5595:Circ[1].RazEner_T_SCADA:=Real_0;
|  |  |  | Read_Real(rVar:=Circ[1].RazEner_M_SCADA,lo:=5596,hi:=5597); | [5 empty] | 5597:Circ[1].RazEner_M_SCADA:=Real_0;

## XSoft_EXP
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
PROGRAM mod_Read
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*Branje BOOL*)
(**)
mind_bool[0]:=AlarmGenCirc1;
mind_bool[1]:=AlarmGenComm;
mind_bool[2]:=AlarmGenDI;
mind_bool[3]:=AlarmGenKlima5;
mind_bool[4]:=AlarmGenKlima6;
mind_bool[5]:=AlarmGenPMM1;
mind_bool[6]:=AlarmGenPMM2;
mind_bool[7]:=AlarmGenPMM3;
mind_bool[8]:=AlarmGenUPS1;
mind_bool[9]:=AlarmGenUPS2;
mind_bool[10]:=ComSCADA;
mind_bool[11]:=ComSCADA1;
mind_bool[12]:=DI_Klima5_ERR;
mind_bool[13]:=DI_Klima5_ON;
mind_bool[14]:=DI_Klima6_ERR;
mind_bool[15]:=DI_Klima6_ON;
mind_bool[16]:=DI_KlimaSplit1_ERR;
mind_bool[17]:=DI_KlimaSplit1_ON;
mind_bool[18]:=DI_Q10_OdcKlima6_IZP;
mind_bool[19]:=DI_Q10_OdcKlima6_ON;
mind_bool[20]:=DI_Q11_OdcVent1_ON;
mind_bool[21]:=DI_Q12_Rezerva_ON;
mind_bool[22]:=DI_Q1_GlavnoStikalo_ON;
mind_bool[23]:=DI_Q25_OdcUpsA_IZP;
mind_bool[24]:=DI_Q25_OdcUpsA_ON;
mind_bool[25]:=DI_Q26_OdcByA_IZP;
mind_bool[26]:=DI_Q26_OdcByA_ON;
mind_bool[27]:=DI_Q27_OdcByUpsA_IZP;
mind_bool[28]:=DI_Q27_OdcByUpsA_ON;
mind_bool[29]:=DI_Q28_OdcUpsB_IZP;
mind_bool[30]:=DI_Q28_OdcUpsB_ON;
mind_bool[31]:=DI_Q29_OdcByB_IZP;
mind_bool[32]:=DI_Q29_OdcByB_ON;
mind_bool[33]:=DI_Q2_Rezerva_IZP;
mind_bool[34]:=DI_Q2_Rezerva_ON;
mind_bool[35]:=DI_Q30_OdcByUpsB_IZP;
mind_bool[36]:=DI_Q30_OdcByUpsB_ON;
mind_bool[37]:=DI_Q31_DovByUpsA_ON;
mind_bool[38]:=DI_Q32_DovByA_ON;
mind_bool[39]:=DI_Q33_DovByUpsB_ON;
mind_bool[40]:=DI_Q34_DovByB_ON;
mind_bool[41]:=DI_Q5_OdcKlima1_IZP;
mind_bool[42]:=DI_Q5_OdcKlima1_ON;
mind_bool[43]:=DI_Q6_OdcKlima2_IZP;
mind_bool[44]:=DI_Q6_OdcKlima2_ON;
mind_bool[45]:=DI_Q7_OdcKlima3_IZP;
mind_bool[46]:=DI_Q7_OdcKlima3_ON;
mind_bool[47]:=DI_Q8_OdcKlima4_IZP;
mind_bool[48]:=DI_Q8_OdcKlima4_ON;
mind_bool[49]:=DI_Q9_OdcKlima5_IZP;
mind_bool[50]:=DI_Q9_OdcKlima5_ON;
mind_bool[51]:=DI_RazlitjeVodeK5K6;
mind_bool[52]:=DI_UPS_Alarm;
mind_bool[53]:=DI_UPS_BatNacin;
mind_bool[54]:=DI_UPS_Polnjenje;
mind_bool[55]:=DIN_UpsA_ERR;
mind_bool[56]:=DIN_UpsA_BypassON;
mind_bool[57]:=DIN_UpsB_ERR;
mind_bool[58]:=DIN_UpsB_BypassON;
mind_bool[59]:=DO_Klima5_Izklop;
mind_bool[60]:=DO_Klima6_Izklop;
mind_bool[61]:=ErrComCirc[1];
mind_bool[62]:=ErrComCirc[2];
mind_bool[63]:=ErrComCirc[3];
mind_bool[64]:=ErrComCirc[4];
mind_bool[65]:=ErrComCirc[5];
mind_bool[66]:=ErrComKlima[1];
mind_bool[67]:=ErrComKlima[2];
mind_bool[68]:=ErrComKlima[3];
mind_bool[69]:=ErrComKlima[4];
mind_bool[70]:=ErrComKlima[5];
mind_bool[71]:=ErrComKlima[6];
mind_bool[72]:=ErrCommScada;
mind_bool[73]:=ErrComPanelPLC;
mind_bool[74]:=ErrComPMM[1];
mind_bool[75]:=ErrComPMM[2];
mind_bool[76]:=ErrComPMM[3];
mind_bool[77]:=ErrComPort2;
mind_bool[78]:=ErrComPort3;
mind_bool[79]:=ErrComPort4;
mind_bool[80]:=ErrComUPS[1];
mind_bool[81]:=ErrComUPS[2];
mind_bool[82]:=Klima[1].AlarmKompresor1;
mind_bool[83]:=Klima[1].AlarmKompresor2;
mind_bool[84]:=Klima[1].Deluje;
mind_bool[85]:=Klima[1].EnergySaving;
mind_bool[86]:=Klima[1].FaultyEPROM;
mind_bool[87]:=Klima[1].FenThermalCutout;
mind_bool[88]:=Klima[1].GeneralAlarm;
mind_bool[89]:=Klima[1].Kompresor1naMejiObrUr;
mind_bool[90]:=Klima[1].Kompresor2naMejiObrUr;
mind_bool[91]:=Klima[1].Napaka;
mind_bool[92]:=Klima[1].NapakaPriPretokuZraka;
mind_bool[93]:=Klima[1].NapakaSenzorPovratVode;
mind_bool[94]:=Klima[1].NapakaSenzorTempIzpiha;
mind_bool[95]:=Klima[1].NapakaSenzorTempProstora;
mind_bool[96]:=Klima[1].NapakaSenzorVlaznosti;
mind_bool[97]:=Klima[1].NapakaSenzorZunanjeTemp;
mind_bool[98]:=Klima[1].NiTokaVVlazilcu;
mind_bool[99]:=Klima[1].NiVodeVVlazilcu;
mind_bool[100]:=Klima[1].NizekPritiskKompresor1;
mind_bool[101]:=Klima[1].NizekPritiskKompresor2;
mind_bool[102]:=Klima[1].NizkaTempPovratneVode;
mind_bool[103]:=Klima[1].NizkaTempVProstoru;
mind_bool[104]:=Klima[1].NizkaVlaznost;
mind_bool[105]:=Klima[1].OnOffEnablingBySupervisor;
mind_bool[106]:=Klima[1].PozarniAlarm;
mind_bool[107]:=Klima[1].Razvlazevanje;
mind_bool[108]:=Klima[1].RemoteOFFtoOutput;
mind_bool[109]:=Klima[1].RemoteOnOff;
mind_bool[110]:=Klima[1].RocniIzklop;
mind_bool[111]:=Klima[1].SenzorjiStatus;
mind_bool[112]:=Klima[1].StoppedByAlarms;
mind_bool[113]:=Klima[1].ThermalCutoutHeater1;
mind_bool[114]:=Klima[1].ThermalCutoutHeater2;
mind_bool[115]:=Klima[1].UnitOnOff;
mind_bool[116]:=Klima[1].VentilatorNaMejiObrUr;
mind_bool[117]:=Klima[1].VentilGretjeOdpiranje;
mind_bool[118]:=Klima[1].VentilGretjeZapiranje;
mind_bool[119]:=Klima[1].VentilHlajenjeOdpiranje;
mind_bool[120]:=Klima[1].VentilHlajenjeZapiranje;
mind_bool[121]:=Klima[1].VisokaTempPovratneVode;
mind_bool[122]:=Klima[1].VisokaTempVProstoru;
mind_bool[123]:=Klima[1].VisokaVlaznost;
mind_bool[124]:=Klima[1].VisokTokVVlazilcu;
mind_bool[125]:=Klima[1].Vlazenje;
mind_bool[126]:=Klima[1].ZamasenFilter;
mind_bool[127]:=Klima[2].AlarmKompresor1;
mind_bool[128]:=Klima[2].AlarmKompresor2;
mind_bool[129]:=Klima[2].Deluje;
mind_bool[130]:=Klima[2].EnergySaving;
mind_bool[131]:=Klima[2].FaultyEPROM;
mind_bool[132]:=Klima[2].FenThermalCutout;
mind_bool[133]:=Klima[2].GeneralAlarm;
mind_bool[134]:=Klima[2].Kompresor1naMejiObrUr;
mind_bool[135]:=Klima[2].Kompresor2naMejiObrUr;
mind_bool[136]:=Klima[2].Napaka;
mind_bool[137]:=Klima[2].NapakaPriPretokuZraka;
mind_bool[138]:=Klima[2].NapakaSenzorPovratVode;
mind_bool[139]:=Klima[2].NapakaSenzorTempIzpiha;
mind_bool[140]:=Klima[2].NapakaSenzorTempProstora;
mind_bool[141]:=Klima[2].NapakaSenzorVlaznosti;
mind_bool[142]:=Klima[2].NapakaSenzorZunanjeTemp;
mind_bool[143]:=Klima[2].NiTokaVVlazilcu;
mind_bool[144]:=Klima[2].NiVodeVVlazilcu;
mind_bool[145]:=Klima[2].NizekPritiskKompresor1;
mind_bool[146]:=Klima[2].NizekPritiskKompresor2;
mind_bool[147]:=Klima[2].NizkaTempPovratneVode;
mind_bool[148]:=Klima[2].NizkaTempVProstoru;
mind_bool[149]:=Klima[2].NizkaVlaznost;
mind_bool[150]:=Klima[2].OnOffEnablingBySupervisor;
mind_bool[151]:=Klima[2].PozarniAlarm;
mind_bool[152]:=Klima[2].Razvlazevanje;
mind_bool[153]:=Klima[2].RemoteOFFtoOutput;
mind_bool[154]:=Klima[2].RemoteOnOff;
mind_bool[155]:=Klima[2].RocniIzklop;
mind_bool[156]:=Klima[2].SenzorjiStatus;
mind_bool[157]:=Klima[2].StoppedByAlarms;
mind_bool[158]:=Klima[2].ThermalCutoutHeater1;
mind_bool[159]:=Klima[2].ThermalCutoutHeater2;
mind_bool[160]:=Klima[2].UnitOnOff;
mind_bool[161]:=Klima[2].VentilatorNaMejiObrUr;
mind_bool[162]:=Klima[2].VentilGretjeOdpiranje;
mind_bool[163]:=Klima[2].VentilGretjeZapiranje;
mind_bool[164]:=Klima[2].VentilHlajenjeOdpiranje;
mind_bool[165]:=Klima[2].VentilHlajenjeZapiranje;
mind_bool[166]:=Klima[2].VisokaTempPovratneVode;
mind_bool[167]:=Klima[2].VisokaTempVProstoru;
mind_bool[168]:=Klima[2].VisokaVlaznost;
mind_bool[169]:=Klima[2].VisokTokVVlazilcu;
mind_bool[170]:=Klima[2].Vlazenje;
mind_bool[171]:=Klima[2].ZamasenFilter;
mind_bool[172]:=KlimeNaCas;
mind_bool[173]:=NapakaSenzorTemp[1];
mind_bool[174]:=NapakaSenzorTemp[2];
mind_bool[175]:=NapakaSenzorVlaga[1];
mind_bool[176]:=NapakaSenzorVlaga[2];
mind_bool[177]:=PMM1OverCurrentBetw[1];
mind_bool[178]:=PMM1OverCurrentBetw[2];
mind_bool[179]:=PMM1OverCurrentBetw[3];
mind_bool[180]:=PMM1OverCurrentOver[1];
mind_bool[181]:=PMM1OverCurrentOver[2];
mind_bool[182]:=PMM1OverCurrentOver[3];
mind_bool[183]:=PMM2OverCurrentBetw[1];
mind_bool[184]:=PMM2OverCurrentBetw[2];
mind_bool[185]:=PMM2OverCurrentBetw[3];
mind_bool[186]:=PMM2OverCurrentOver[1];
mind_bool[187]:=PMM2OverCurrentOver[2];
mind_bool[188]:=PMM2OverCurrentOver[3];
mind_bool[189]:=PMM3OverCurrentBetw[1];
mind_bool[190]:=PMM3OverCurrentBetw[2];
mind_bool[191]:=PMM3OverCurrentBetw[3];
mind_bool[192]:=PMM3OverCurrentOver[1];
mind_bool[193]:=PMM3OverCurrentOver[2];
mind_bool[194]:=PMM3OverCurrentOver[3];
mind_bool[195]:=PMM[1].Napaka;
mind_bool[196]:=PMM[2].Napaka;
mind_bool[197]:=PMM[3].Napaka;
mind_bool[198]:=SetDateTime;
mind_bool[199]:=SetDateTimeDemand;
mind_bool[200]:=SetDateTimeError;
mind_bool[201]:=SetDateTimeFinished;
mind_bool[202]:=SetRemoteOnOff[1];
mind_bool[203]:=SetRemoteOnOff[2];
mind_bool[204]:=SlabaBaterijaPLC_A1;
mind_bool[205]:=TempTSprevisoka[1];
mind_bool[206]:=TempTSprevisoka[2];
mind_bool[207]:=UPS[1].AlarmAwaitingPower;
mind_bool[208]:=UPS[1].AlarmBypassBad;
mind_bool[209]:=UPS[1].AlarmChargerFailed;
mind_bool[210]:=UPS[1].AlarmCommunicationsLost;
mind_bool[211]:=UPS[1].AlarmDepletedBattery;
mind_bool[212]:=UPS[1].AlarmDiagnosticTestFailed;
mind_bool[213]:=UPS[1].AlarmIzhodOffKotZahtevano;
mind_bool[214]:=UPS[1].AlarmIzhodPreobremenjen;
mind_bool[215]:=UPS[1].AlarmLowBattery;
mind_bool[216]:=UPS[1].AlarmNapakaNaVarovalki;
mind_bool[217]:=UPS[1].AlarmNapakaNaVentilatorju;
mind_bool[218]:=UPS[1].AlarmOnBattery;
mind_bool[219]:=UPS[1].AlarmOnBypass;
mind_bool[220]:=UPS[1].AlarmInverterError;
mind_bool[221]:=UPS[1].AlarmShutdownImminent;
mind_bool[222]:=UPS[1].AlarmShutdownPending;
mind_bool[223]:=UPS[1].AlarmSlabaBaterija;
mind_bool[224]:=UPS[1].AlarmSplosnaNapaka;
mind_bool[225]:=UPS[1].AlarmStanjeIzhodaIzvenToleranc;
mind_bool[226]:=UPS[1].AlarmStanjeVhodaIzvenToleranc;
mind_bool[227]:=UPS[1].AlarmTemperaturaIzvenToleranc;
mind_bool[228]:=UPS[1].AlarmTestInProgres;
mind_bool[229]:=UPS[1].AlarmUPSIzhodOff;
mind_bool[230]:=UPS[1].AlarmUPSOffKotZahtevano;
mind_bool[231]:=UPS[1].AlarmUPSSystemOff;
mind_bool[232]:=UPS[1].Napaka;
mind_bool[233]:=UPS[1].StatusEcomodeAktiven;
mind_bool[234]:=UPS[1].StatusInverterIsOn;
mind_bool[235]:=UPS[1].StatusStopOperation;
mind_bool[236]:=UPS[2].AlarmAwaitingPower;
mind_bool[237]:=UPS[2].AlarmBypassBad;
mind_bool[238]:=UPS[2].AlarmChargerFailed;
mind_bool[239]:=UPS[2].AlarmCommunicationsLost;
mind_bool[240]:=UPS[2].AlarmDepletedBattery;
mind_bool[241]:=UPS[2].AlarmDiagnosticTestFailed;
mind_bool[242]:=UPS[2].AlarmIzhodOffKotZahtevano;
mind_bool[243]:=UPS[2].AlarmIzhodPreobremenjen;
mind_bool[244]:=UPS[2].AlarmLowBattery;
mind_bool[245]:=UPS[2].AlarmNapakaNaVarovalki;
mind_bool[246]:=UPS[2].AlarmNapakaNaVentilatorju;
mind_bool[247]:=UPS[2].AlarmOnBattery;
mind_bool[248]:=UPS[2].AlarmOnBypass;
mind_bool[249]:=UPS[2].AlarmInverterError;
mind_bool[250]:=UPS[2].AlarmShutdownImminent;
mind_bool[251]:=UPS[2].AlarmShutdownPending;
mind_bool[252]:=UPS[2].AlarmSlabaBaterija;
mind_bool[253]:=UPS[2].AlarmSplosnaNapaka;
mind_bool[254]:=UPS[2].AlarmStanjeIzhodaIzvenToleranc;
mind_bool[255]:=UPS[2].AlarmStanjeVhodaIzvenToleranc;
mind_bool[256]:=UPS[2].AlarmTemperaturaIzvenToleranc;
mind_bool[257]:=UPS[2].AlarmTestInProgres;
mind_bool[258]:=UPS[2].AlarmUPSIzhodOff;
mind_bool[259]:=UPS[2].AlarmUPSOffKotZahtevano;
mind_bool[260]:=UPS[2].AlarmUPSSystemOff;
mind_bool[261]:=UPS[2].Napaka;
mind_bool[262]:=UPS[2].StatusEcomodeAktiven;
mind_bool[263]:=UPS[2].StatusInverterIsOn;
mind_bool[264]:=UPS[2].StatusStopOperation;
mind_bool[265]:=UserLoggedIn;
mind_bool[266]:=XVH_AlarmOn;
mind_bool[267]:=AlarmGenRest;
mind_bool[268]:=DI_UpsA_BypassON;
mind_bool[269]:=DI_UpsA_ERR;
mind_bool[270]:=DI_UpsB_BypassON;
mind_bool[271]:=DI_UpsB_ERR;
mind_bool[272]:=DIN_Klima5_ERR;
mind_bool[273]:=DIN_Klima6_ERR;
mind_bool[274]:=DIN_KlimaSplit1_ERR;
mind_bool[275]:=DIN_Q10_OdcKlima6_IZP;
mind_bool[276]:=DIN_Q25_OdcUpsA_IZP;
mind_bool[277]:=DIN_Q26_OdcByA_IZP;
mind_bool[278]:=DIN_Q27_OdcByUpsA_IZP;
mind_bool[279]:=DIN_Q28_OdcUpsB_IZP;
mind_bool[280]:=DIN_Q29_OdcByB_IZP;
mind_bool[281]:=DIN_Q2_Rezerva_IZP;
mind_bool[282]:=DIN_Q30_OdcByUpsB_IZP;
mind_bool[283]:=DIN_Q5_OdcKlima1_IZP;
mind_bool[284]:=DIN_Q6_OdcKlima2_IZP;
mind_bool[285]:=DIN_Q7_OdcKlima3_IZP;
mind_bool[286]:=DIN_Q8_OdcKlima4_IZP;
mind_bool[287]:=DIN_Q9_OdcKlima5_IZP;
mind_bool[288]:=ErrorComCirc[1].Error;
mind_bool[289]:=ErrorComCirc[2].Error;
mind_bool[290]:=ErrorComCirc[3].Error;
mind_bool[291]:=ErrorComCirc[4].Error;
mind_bool[292]:=ErrorComCirc[5].Error;
mind_bool[293]:=ErrorComKlima[1].Error;
mind_bool[294]:=ErrorComKlima[2].Error;
mind_bool[295]:=ErrorComKlima[3].Error;
mind_bool[296]:=ErrorComKlima[4].Error;
mind_bool[297]:=ErrorComKlima[5].Error;
mind_bool[298]:=ErrorComKlima[6].Error;
mind_bool[299]:=ErrorComPMM[1].Error;
mind_bool[300]:=ErrorComPMM[2].Error;
mind_bool[301]:=ErrorComPMM[3].Error;
mind_bool[302]:=ErrorComUPS[1].Error;
mind_bool[303]:=ErrorComUPS[2].Error;
mind_bool[304]:=KlimaAErrors[10];
mind_bool[305]:=KlimaAErrors[11];
mind_bool[306]:=KlimaAErrors[12];
mind_bool[307]:=KlimaAErrors[13];
mind_bool[308]:=KlimaAErrors[14];
mind_bool[309]:=KlimaAErrors[15];
mind_bool[310]:=KlimaAErrors[16];
mind_bool[311]:=KlimaAErrors[17];
mind_bool[312]:=KlimaAErrors[18];
mind_bool[313]:=KlimaAErrors[19];
mind_bool[314]:=KlimaAErrors[1];
mind_bool[315]:=KlimaAErrors[20];
mind_bool[316]:=KlimaAErrors[21];
mind_bool[317]:=KlimaAErrors[22];
mind_bool[318]:=KlimaAErrors[23];
mind_bool[319]:=KlimaAErrors[24];
mind_bool[320]:=KlimaAErrors[25];
mind_bool[321]:=KlimaAErrors[26];
mind_bool[322]:=KlimaAErrors[27];
mind_bool[323]:=KlimaAErrors[28];
mind_bool[324]:=KlimaAErrors[29];
mind_bool[325]:=KlimaAErrors[2];
mind_bool[326]:=KlimaAErrors[30];
mind_bool[327]:=KlimaAErrors[31];
mind_bool[328]:=KlimaAErrors[32];
mind_bool[329]:=KlimaAErrors[33];
mind_bool[330]:=KlimaAErrors[34];
mind_bool[331]:=KlimaAErrors[35];
mind_bool[332]:=KlimaAErrors[36];
mind_bool[333]:=KlimaAErrors[37];
mind_bool[334]:=KlimaAErrors[38];
mind_bool[335]:=KlimaAErrors[39];
mind_bool[336]:=KlimaAErrors[3];
mind_bool[337]:=KlimaAErrors[40];
mind_bool[338]:=KlimaAErrors[4];
mind_bool[339]:=KlimaAErrors[5];
mind_bool[340]:=KlimaAErrors[6];
mind_bool[341]:=KlimaAErrors[7];
mind_bool[342]:=KlimaAErrors[8];
mind_bool[343]:=KlimaAErrors[9];
mind_bool[344]:=KlimaBErrors[10];
mind_bool[345]:=KlimaBErrors[11];
mind_bool[346]:=KlimaBErrors[12];
mind_bool[347]:=KlimaBErrors[13];
mind_bool[348]:=KlimaBErrors[14];
mind_bool[349]:=KlimaBErrors[15];
mind_bool[350]:=KlimaBErrors[16];
mind_bool[351]:=KlimaBErrors[17];
mind_bool[352]:=KlimaBErrors[18];
mind_bool[353]:=KlimaBErrors[19];
mind_bool[354]:=KlimaBErrors[1];
mind_bool[355]:=KlimaBErrors[20];
mind_bool[356]:=KlimaBErrors[21];
mind_bool[357]:=KlimaBErrors[22];
mind_bool[358]:=KlimaBErrors[23];
mind_bool[359]:=KlimaBErrors[24];
mind_bool[360]:=KlimaBErrors[25];
mind_bool[361]:=KlimaBErrors[26];
mind_bool[362]:=KlimaBErrors[27];
mind_bool[363]:=KlimaBErrors[28];
mind_bool[364]:=KlimaBErrors[29];
mind_bool[365]:=KlimaBErrors[2];
mind_bool[366]:=KlimaBErrors[30];
mind_bool[367]:=KlimaBErrors[31];
mind_bool[368]:=KlimaBErrors[32];
mind_bool[369]:=KlimaBErrors[33];
mind_bool[370]:=KlimaBErrors[34];
mind_bool[371]:=KlimaBErrors[35];
mind_bool[372]:=KlimaBErrors[36];
mind_bool[373]:=KlimaBErrors[37];
mind_bool[374]:=KlimaBErrors[38];
mind_bool[375]:=KlimaBErrors[39];
mind_bool[376]:=KlimaBErrors[3];
mind_bool[377]:=KlimaBErrors[40];
mind_bool[378]:=KlimaBErrors[4];
mind_bool[379]:=KlimaBErrors[5];
mind_bool[380]:=KlimaBErrors[6];
mind_bool[381]:=KlimaBErrors[7];
mind_bool[382]:=KlimaBErrors[8];
mind_bool[383]:=KlimaBErrors[9];
mind_bool[384]:=KlimaGal.AlarmKompresor1;
mind_bool[385]:=KlimaGal.AlarmKompresor2;
mind_bool[386]:=KlimaGal.Deluje;
mind_bool[387]:=KlimaGal.EnergySaving;
mind_bool[388]:=KlimaGal.FaultyEPROM;
mind_bool[389]:=KlimaGal.FenThermalCutout;
mind_bool[390]:=KlimaGal.GeneralAlarm;
mind_bool[391]:=KlimaGal.Kompresor1naMejiObrUr;
mind_bool[392]:=KlimaGal.Kompresor2naMejiObrUr;
mind_bool[393]:=KlimaGal.Napaka;
mind_bool[394]:=KlimaGal.NapakaPriPretokuZraka;
mind_bool[395]:=KlimaGal.NapakaSenzorPovratVode;
mind_bool[396]:=KlimaGal.NapakaSenzorTempIzpiha;
mind_bool[397]:=KlimaGal.NapakaSenzorTempProstora;
mind_bool[398]:=KlimaGal.NapakaSenzorVlaznosti;
mind_bool[399]:=KlimaGal.NapakaSenzorZunanjeTemp;
mind_bool[400]:=KlimaGal.NiTokaVVlazilcu;
mind_bool[401]:=KlimaGal.NiVodeVVlazilcu;
mind_bool[402]:=KlimaGal.NizekPritiskKompresor1;
mind_bool[403]:=KlimaGal.NizekPritiskKompresor2;
mind_bool[404]:=KlimaGal.NizkaTempPovratneVode;
mind_bool[405]:=KlimaGal.NizkaTempVProstoru;
mind_bool[406]:=KlimaGal.NizkaVlaznost;
mind_bool[407]:=KlimaGal.OnOffEnablingBySupervisor;
mind_bool[408]:=KlimaGal.PozarniAlarm;
mind_bool[409]:=KlimaGal.Razvlazevanje;
mind_bool[410]:=KlimaGal.RemoteOFFtoOutput;
mind_bool[411]:=KlimaGal.RemoteOnOff;
mind_bool[412]:=KlimaGal.RocniIzklop;
mind_bool[413]:=KlimaGal.SenzorjiStatus;
mind_bool[414]:=KlimaGal.StoppedByAlarms;
mind_bool[415]:=KlimaGal.ThermalCutoutHeater1;
mind_bool[416]:=KlimaGal.ThermalCutoutHeater2;
mind_bool[417]:=KlimaGal.UnitOnOff;
mind_bool[418]:=KlimaGal.VentilatorNaMejiObrUr;
mind_bool[419]:=KlimaGal.VentilGretjeOdpiranje;
mind_bool[420]:=KlimaGal.VentilGretjeZapiranje;
mind_bool[421]:=KlimaGal.VentilHlajenjeOdpiranje;
mind_bool[422]:=KlimaGal.VentilHlajenjeZapiranje;
mind_bool[423]:=KlimaGal.VisokaTempPovratneVode;
mind_bool[424]:=KlimaGal.VisokaTempVProstoru;
mind_bool[425]:=KlimaGal.VisokaVlaznost;
mind_bool[426]:=KlimaGal.VisokTokVVlazilcu;
mind_bool[427]:=KlimaGal.Vlazenje;
mind_bool[428]:=KlimaGal.ZamasenFilter;
mind_bool[429]:=PMM1OverVoltage;
mind_bool[430]:=PMM2OverVoltage;
mind_bool[431]:=PMM3OverVoltage;
mind_bool[432]:=PMMgal.Napaka;
mind_bool[433]:=ErrCommScada2;
mind_bool[434]:=ComSCADA2;
mind_bool[435]:=ComSCADA3;
mind_bool[436]:=Circ_Vpis_Dnevne_energija_scada1;
mind_bool[437]:=Circ_Vpis_Dnevne_energija_scada2;
mind_bool[438]:=Circ_Vpis_Tedenska_energija_scada1;
mind_bool[439]:=Circ_Vpis_Tedenska_energija_scada2;
mind_bool[440]:=Circ_Vpis_Mesecna_energija_scada1;
mind_bool[441]:=Circ_Vpis_Mesecna_energija_scada2;
(*Branje INT*)
(**)
mind[0]:=DateTime.Dan;
mind[1]:=DateTime.Leto;
mind[2]:=DateTime.Mesec;
mind[3]:=DateTime.Minuta;
mind[4]:=DateTime.Sekunda;
mind[5]:=DateTime.Ura;
mind[6]:=Klima[1].GrelecStatus;
mind[7]:=Klima[1].IzhodniVentStatus;
mind[8]:=Klima[1].KompresorStatus;
mind[9]:=Klima[1].VlazilecStatus;
mind[10]:=Klima[2].GrelecStatus;
mind[11]:=Klima[2].IzhodniVentStatus;
mind[12]:=Klima[2].KompresorStatus;
mind[13]:=Klima[2].VlazilecStatus;
mind[14]:=PMM[1].AlarmPhase[1].C01_16_60to80;
mind[15]:=PMM[1].AlarmPhase[1].C01_16_over80;
mind[16]:=PMM[1].AlarmPhase[1].C17_32_60to80;
mind[17]:=PMM[1].AlarmPhase[1].C17_32_over80;
mind[18]:=PMM[1].AlarmPhase[1].C33_42_60to80;
mind[19]:=PMM[1].AlarmPhase[1].C33_42_over80;
mind[20]:=PMM[1].AlarmPhase[1].GlobalAlarmReg;
mind[21]:=PMM[1].AlarmPhase[2].C01_16_60to80;
mind[22]:=PMM[1].AlarmPhase[2].C01_16_over80;
mind[23]:=PMM[1].AlarmPhase[2].C17_32_60to80;
mind[24]:=PMM[1].AlarmPhase[2].C17_32_over80;
mind[25]:=PMM[1].AlarmPhase[2].C33_42_60to80;
mind[26]:=PMM[1].AlarmPhase[2].C33_42_over80;
mind[27]:=PMM[1].AlarmPhase[2].GlobalAlarmReg;
mind[28]:=PMM[1].AlarmPhase[3].C01_16_60to80;
mind[29]:=PMM[1].AlarmPhase[3].C01_16_over80;
mind[30]:=PMM[1].AlarmPhase[3].C17_32_60to80;
mind[31]:=PMM[1].AlarmPhase[3].C17_32_over80;
mind[32]:=PMM[1].AlarmPhase[3].C33_42_60to80;
mind[33]:=PMM[1].AlarmPhase[3].C33_42_over80;
mind[34]:=PMM[1].AlarmPhase[3].GlobalAlarmReg;
mind[35]:=PMM[1].Alarms;
mind[36]:=PMM[2].AlarmPhase[1].C01_16_60to80;
mind[37]:=PMM[2].AlarmPhase[1].C01_16_over80;
mind[38]:=PMM[2].AlarmPhase[1].C17_32_60to80;
mind[39]:=PMM[2].AlarmPhase[1].C17_32_over80;
mind[40]:=PMM[2].AlarmPhase[1].C33_42_60to80;
mind[41]:=PMM[2].AlarmPhase[1].C33_42_over80;
mind[42]:=PMM[2].AlarmPhase[1].GlobalAlarmReg;
mind[43]:=PMM[2].AlarmPhase[2].C01_16_60to80;
mind[44]:=PMM[2].AlarmPhase[2].C01_16_over80;
mind[45]:=PMM[2].AlarmPhase[2].C17_32_60to80;
mind[46]:=PMM[2].AlarmPhase[2].C17_32_over80;
mind[47]:=PMM[2].AlarmPhase[2].C33_42_60to80;
mind[48]:=PMM[2].AlarmPhase[2].C33_42_over80;
mind[49]:=PMM[2].AlarmPhase[2].GlobalAlarmReg;
mind[50]:=PMM[2].AlarmPhase[3].C01_16_60to80;
mind[51]:=PMM[2].AlarmPhase[3].C01_16_over80;
mind[52]:=PMM[2].AlarmPhase[3].C17_32_60to80;
mind[53]:=PMM[2].AlarmPhase[3].C17_32_over80;
mind[54]:=PMM[2].AlarmPhase[3].C33_42_60to80;
mind[55]:=PMM[2].AlarmPhase[3].C33_42_over80;
mind[56]:=PMM[2].AlarmPhase[3].GlobalAlarmReg;
mind[57]:=PMM[2].Alarms;
mind[58]:=PMM[3].AlarmPhase[1].C01_16_60to80;
mind[59]:=PMM[3].AlarmPhase[1].C01_16_over80;
mind[60]:=PMM[3].AlarmPhase[1].C17_32_60to80;
mind[61]:=PMM[3].AlarmPhase[1].C17_32_over80;
mind[62]:=PMM[3].AlarmPhase[1].C33_42_60to80;
mind[63]:=PMM[3].AlarmPhase[1].C33_42_over80;
mind[64]:=PMM[3].AlarmPhase[1].GlobalAlarmReg;
mind[65]:=PMM[3].AlarmPhase[2].C01_16_60to80;
mind[66]:=PMM[3].AlarmPhase[2].C01_16_over80;
mind[67]:=PMM[3].AlarmPhase[2].C17_32_60to80;
mind[68]:=PMM[3].AlarmPhase[2].C17_32_over80;
mind[69]:=PMM[3].AlarmPhase[2].C33_42_60to80;
mind[70]:=PMM[3].AlarmPhase[2].C33_42_over80;
mind[71]:=PMM[3].AlarmPhase[2].GlobalAlarmReg;
mind[72]:=PMM[3].AlarmPhase[3].C01_16_60to80;
mind[73]:=PMM[3].AlarmPhase[3].C01_16_over80;
mind[74]:=PMM[3].AlarmPhase[3].C17_32_60to80;
mind[75]:=PMM[3].AlarmPhase[3].C17_32_over80;
mind[76]:=PMM[3].AlarmPhase[3].C33_42_60to80;
mind[77]:=PMM[3].AlarmPhase[3].C33_42_over80;
mind[78]:=PMM[3].AlarmPhase[3].GlobalAlarmReg;
mind[79]:=PMM[3].Alarms;
mind[80]:=UPS[1].InverterStatus;
mind[81]:=UPS[1].OutputStatus;
mind[82]:=UPS[1].StatusBaterije;
mind[83]:=UPS[1].SteviloIzpadovVhodneLinije;
mind[84]:=UPS[1].UnitStatus;
mind[85]:=UPS[2].InverterStatus;
mind[86]:=UPS[2].OutputStatus;
mind[87]:=UPS[2].StatusBaterije;
mind[88]:=UPS[2].SteviloIzpadovVhodneLinije;
mind[89]:=UPS[2].UnitStatus;
mind[90]:=UserCurrentLevel;
mind[91]:=ErrorComCirc[1].Code[10];
mind[92]:=ErrorComCirc[1].Code[11];
mind[93]:=ErrorComCirc[1].Code[12];
mind[94]:=ErrorComCirc[1].Code[13];
mind[95]:=ErrorComCirc[1].Code[14];
mind[96]:=ErrorComCirc[1].Code[15];
mind[97]:=ErrorComCirc[1].Code[1];
mind[98]:=ErrorComCirc[1].Code[2];
mind[99]:=ErrorComCirc[1].Code[3];
mind[100]:=ErrorComCirc[1].Code[4];
mind[101]:=ErrorComCirc[1].Code[5];
mind[102]:=ErrorComCirc[1].Code[6];
mind[103]:=ErrorComCirc[1].Code[7];
mind[104]:=ErrorComCirc[1].Code[8];
mind[105]:=ErrorComCirc[1].Code[9];
mind[106]:=ErrorComCirc[1].Status;
mind[107]:=ErrorComCirc[2].Code[10];
mind[108]:=ErrorComCirc[2].Code[11];
mind[109]:=ErrorComCirc[2].Code[12];
mind[110]:=ErrorComCirc[2].Code[13];
mind[111]:=ErrorComCirc[2].Code[14];
mind[112]:=ErrorComCirc[2].Code[15];
mind[113]:=ErrorComCirc[2].Code[1];
mind[114]:=ErrorComCirc[2].Code[2];
mind[115]:=ErrorComCirc[2].Code[3];
mind[116]:=ErrorComCirc[2].Code[4];
mind[117]:=ErrorComCirc[2].Code[5];
mind[118]:=ErrorComCirc[2].Code[6];
mind[119]:=ErrorComCirc[2].Code[7];
mind[120]:=ErrorComCirc[2].Code[8];
mind[121]:=ErrorComCirc[2].Code[9];
mind[122]:=ErrorComCirc[2].Status;
mind[123]:=ErrorComCirc[3].Code[10];
mind[124]:=ErrorComCirc[3].Code[11];
mind[125]:=ErrorComCirc[3].Code[12];
mind[126]:=ErrorComCirc[3].Code[13];
mind[127]:=ErrorComCirc[3].Code[14];
mind[128]:=ErrorComCirc[3].Code[15];
mind[129]:=ErrorComCirc[3].Code[1];
mind[130]:=ErrorComCirc[3].Code[2];
mind[131]:=ErrorComCirc[3].Code[3];
mind[132]:=ErrorComCirc[3].Code[4];
mind[133]:=ErrorComCirc[3].Code[5];
mind[134]:=ErrorComCirc[3].Code[6];
mind[135]:=ErrorComCirc[3].Code[7];
mind[136]:=ErrorComCirc[3].Code[8];
mind[137]:=ErrorComCirc[3].Code[9];
mind[138]:=ErrorComCirc[3].Status;
mind[139]:=ErrorComCirc[4].Code[10];
mind[140]:=ErrorComCirc[4].Code[11];
mind[141]:=ErrorComCirc[4].Code[12];
mind[142]:=ErrorComCirc[4].Code[13];
mind[143]:=ErrorComCirc[4].Code[14];
mind[144]:=ErrorComCirc[4].Code[15];
mind[145]:=ErrorComCirc[4].Code[1];
mind[146]:=ErrorComCirc[4].Code[2];
mind[147]:=ErrorComCirc[4].Code[3];
mind[148]:=ErrorComCirc[4].Code[4];
mind[149]:=ErrorComCirc[4].Code[5];
mind[150]:=ErrorComCirc[4].Code[6];
mind[151]:=ErrorComCirc[4].Code[7];
mind[152]:=ErrorComCirc[4].Code[8];
mind[153]:=ErrorComCirc[4].Code[9];
mind[154]:=ErrorComCirc[4].Status;
mind[155]:=ErrorComCirc[5].Code[10];
mind[156]:=ErrorComCirc[5].Code[11];
mind[157]:=ErrorComCirc[5].Code[12];
mind[158]:=ErrorComCirc[5].Code[13];
mind[159]:=ErrorComCirc[5].Code[14];
mind[160]:=ErrorComCirc[5].Code[15];
mind[161]:=ErrorComCirc[5].Code[1];
mind[162]:=ErrorComCirc[5].Code[2];
mind[163]:=ErrorComCirc[5].Code[3];
mind[164]:=ErrorComCirc[5].Code[4];
mind[165]:=ErrorComCirc[5].Code[5];
mind[166]:=ErrorComCirc[5].Code[6];
mind[167]:=ErrorComCirc[5].Code[7];
mind[168]:=ErrorComCirc[5].Code[8];
mind[169]:=ErrorComCirc[5].Code[9];
mind[170]:=ErrorComCirc[5].Status;
mind[171]:=ErrorComKlima[1].Code[10];
mind[172]:=ErrorComKlima[1].Code[11];
mind[173]:=ErrorComKlima[1].Code[12];
mind[174]:=ErrorComKlima[1].Code[13];
mind[175]:=ErrorComKlima[1].Code[14];
mind[176]:=ErrorComKlima[1].Code[15];
mind[177]:=ErrorComKlima[1].Code[1];
mind[178]:=ErrorComKlima[1].Code[2];
mind[179]:=ErrorComKlima[1].Code[3];
mind[180]:=ErrorComKlima[1].Code[4];
mind[181]:=ErrorComKlima[1].Code[5];
mind[182]:=ErrorComKlima[1].Code[6];
mind[183]:=ErrorComKlima[1].Code[7];
mind[184]:=ErrorComKlima[1].Code[8];
mind[185]:=ErrorComKlima[1].Code[9];
mind[186]:=ErrorComKlima[1].Status;
mind[187]:=ErrorComKlima[2].Code[10];
mind[188]:=ErrorComKlima[2].Code[11];
mind[189]:=ErrorComKlima[2].Code[12];
mind[190]:=ErrorComKlima[2].Code[13];
mind[191]:=ErrorComKlima[2].Code[14];
mind[192]:=ErrorComKlima[2].Code[15];
mind[193]:=ErrorComKlima[2].Code[1];
mind[194]:=ErrorComKlima[2].Code[2];
mind[195]:=ErrorComKlima[2].Code[3];
mind[196]:=ErrorComKlima[2].Code[4];
mind[197]:=ErrorComKlima[2].Code[5];
mind[198]:=ErrorComKlima[2].Code[6];
mind[199]:=ErrorComKlima[2].Code[7];
mind[200]:=ErrorComKlima[2].Code[8];
mind[201]:=ErrorComKlima[2].Code[9];
mind[202]:=ErrorComKlima[2].Status;
mind[203]:=ErrorComKlima[3].Code[10];
mind[204]:=ErrorComKlima[3].Code[11];
mind[205]:=ErrorComKlima[3].Code[12];
mind[206]:=ErrorComKlima[3].Code[13];
mind[207]:=ErrorComKlima[3].Code[14];
mind[208]:=ErrorComKlima[3].Code[15];
mind[209]:=ErrorComKlima[3].Code[1];
mind[210]:=ErrorComKlima[3].Code[2];
mind[211]:=ErrorComKlima[3].Code[3];
mind[212]:=ErrorComKlima[3].Code[4];
mind[213]:=ErrorComKlima[3].Code[5];
mind[214]:=ErrorComKlima[3].Code[6];
mind[215]:=ErrorComKlima[3].Code[7];
mind[216]:=ErrorComKlima[3].Code[8];
mind[217]:=ErrorComKlima[3].Code[9];
mind[218]:=ErrorComKlima[3].Status;
mind[219]:=ErrorComKlima[4].Code[10];
mind[220]:=ErrorComKlima[4].Code[11];
mind[221]:=ErrorComKlima[4].Code[12];
mind[222]:=ErrorComKlima[4].Code[13];
mind[223]:=ErrorComKlima[4].Code[14];
mind[224]:=ErrorComKlima[4].Code[15];
mind[225]:=ErrorComKlima[4].Code[1];
mind[226]:=ErrorComKlima[4].Code[2];
mind[227]:=ErrorComKlima[4].Code[3];
mind[228]:=ErrorComKlima[4].Code[4];
mind[229]:=ErrorComKlima[4].Code[5];
mind[230]:=ErrorComKlima[4].Code[6];
mind[231]:=ErrorComKlima[4].Code[7];
mind[232]:=ErrorComKlima[4].Code[8];
mind[233]:=ErrorComKlima[4].Code[9];
mind[234]:=ErrorComKlima[4].Status;
mind[235]:=ErrorComKlima[5].Code[10];
mind[236]:=ErrorComKlima[5].Code[11];
mind[237]:=ErrorComKlima[5].Code[12];
mind[238]:=ErrorComKlima[5].Code[13];
mind[239]:=ErrorComKlima[5].Code[14];
mind[240]:=ErrorComKlima[5].Code[15];
mind[241]:=ErrorComKlima[5].Code[1];
mind[242]:=ErrorComKlima[5].Code[2];
mind[243]:=ErrorComKlima[5].Code[3];
mind[244]:=ErrorComKlima[5].Code[4];
mind[245]:=ErrorComKlima[5].Code[5];
mind[246]:=ErrorComKlima[5].Code[6];
mind[247]:=ErrorComKlima[5].Code[7];
mind[248]:=ErrorComKlima[5].Code[8];
mind[249]:=ErrorComKlima[5].Code[9];
mind[250]:=ErrorComKlima[5].Status;
mind[251]:=ErrorComKlima[6].Code[10];
mind[252]:=ErrorComKlima[6].Code[11];
mind[253]:=ErrorComKlima[6].Code[12];
mind[254]:=ErrorComKlima[6].Code[13];
mind[255]:=ErrorComKlima[6].Code[14];
mind[256]:=ErrorComKlima[6].Code[15];
mind[257]:=ErrorComKlima[6].Code[1];
mind[258]:=ErrorComKlima[6].Code[2];
mind[259]:=ErrorComKlima[6].Code[3];
mind[260]:=ErrorComKlima[6].Code[4];
mind[261]:=ErrorComKlima[6].Code[5];
mind[262]:=ErrorComKlima[6].Code[6];
mind[263]:=ErrorComKlima[6].Code[7];
mind[264]:=ErrorComKlima[6].Code[8];
mind[265]:=ErrorComKlima[6].Code[9];
mind[266]:=ErrorComKlima[6].Status;
mind[267]:=ErrorComPMM[1].Code[10];
mind[268]:=ErrorComPMM[1].Code[11];
mind[269]:=ErrorComPMM[1].Code[12];
mind[270]:=ErrorComPMM[1].Code[13];
mind[271]:=ErrorComPMM[1].Code[14];
mind[272]:=ErrorComPMM[1].Code[15];
mind[273]:=ErrorComPMM[1].Code[1];
mind[274]:=ErrorComPMM[1].Code[2];
mind[275]:=ErrorComPMM[1].Code[3];
mind[276]:=ErrorComPMM[1].Code[4];
mind[277]:=ErrorComPMM[1].Code[5];
mind[278]:=ErrorComPMM[1].Code[6];
mind[279]:=ErrorComPMM[1].Code[7];
mind[280]:=ErrorComPMM[1].Code[8];
mind[281]:=ErrorComPMM[1].Code[9];
mind[282]:=ErrorComPMM[1].Status;
mind[283]:=ErrorComPMM[2].Code[10];
mind[284]:=ErrorComPMM[2].Code[11];
mind[285]:=ErrorComPMM[2].Code[12];
mind[286]:=ErrorComPMM[2].Code[13];
mind[287]:=ErrorComPMM[2].Code[14];
mind[288]:=ErrorComPMM[2].Code[15];
mind[289]:=ErrorComPMM[2].Code[1];
mind[290]:=ErrorComPMM[2].Code[2];
mind[291]:=ErrorComPMM[2].Code[3];
mind[292]:=ErrorComPMM[2].Code[4];
mind[293]:=ErrorComPMM[2].Code[5];
mind[294]:=ErrorComPMM[2].Code[6];
mind[295]:=ErrorComPMM[2].Code[7];
mind[296]:=ErrorComPMM[2].Code[8];
mind[297]:=ErrorComPMM[2].Code[9];
mind[298]:=ErrorComPMM[2].Status;
mind[299]:=ErrorComPMM[3].Code[10];
mind[300]:=ErrorComPMM[3].Code[11];
mind[301]:=ErrorComPMM[3].Code[12];
mind[302]:=ErrorComPMM[3].Code[13];
mind[303]:=ErrorComPMM[3].Code[14];
mind[304]:=ErrorComPMM[3].Code[15];
mind[305]:=ErrorComPMM[3].Code[1];
mind[306]:=ErrorComPMM[3].Code[2];
mind[307]:=ErrorComPMM[3].Code[3];
mind[308]:=ErrorComPMM[3].Code[4];
mind[309]:=ErrorComPMM[3].Code[5];
mind[310]:=ErrorComPMM[3].Code[6];
mind[311]:=ErrorComPMM[3].Code[7];
mind[312]:=ErrorComPMM[3].Code[8];
mind[313]:=ErrorComPMM[3].Code[9];
mind[314]:=ErrorComPMM[3].Status;
mind[315]:=ErrorComUPS[1].Code[10];
mind[316]:=ErrorComUPS[1].Code[11];
mind[317]:=ErrorComUPS[1].Code[12];
mind[318]:=ErrorComUPS[1].Code[13];
mind[319]:=ErrorComUPS[1].Code[14];
mind[320]:=ErrorComUPS[1].Code[15];
mind[321]:=ErrorComUPS[1].Code[1];
mind[322]:=ErrorComUPS[1].Code[2];
mind[323]:=ErrorComUPS[1].Code[3];
mind[324]:=ErrorComUPS[1].Code[4];
mind[325]:=ErrorComUPS[1].Code[5];
mind[326]:=ErrorComUPS[1].Code[6];
mind[327]:=ErrorComUPS[1].Code[7];
mind[328]:=ErrorComUPS[1].Code[8];
mind[329]:=ErrorComUPS[1].Code[9];
mind[330]:=ErrorComUPS[1].Status;
mind[331]:=ErrorComUPS[2].Code[10];
mind[332]:=ErrorComUPS[2].Code[11];
mind[333]:=ErrorComUPS[2].Code[12];
mind[334]:=ErrorComUPS[2].Code[13];
mind[335]:=ErrorComUPS[2].Code[14];
mind[336]:=ErrorComUPS[2].Code[15];
mind[337]:=ErrorComUPS[2].Code[1];
mind[338]:=ErrorComUPS[2].Code[2];
mind[339]:=ErrorComUPS[2].Code[3];
mind[340]:=ErrorComUPS[2].Code[4];
mind[341]:=ErrorComUPS[2].Code[5];
mind[342]:=ErrorComUPS[2].Code[6];
mind[343]:=ErrorComUPS[2].Code[7];
mind[344]:=ErrorComUPS[2].Code[8];
mind[345]:=ErrorComUPS[2].Code[9];
mind[346]:=ErrorComUPS[2].Status;
mind[347]:=KlimaGal.GrelecStatus;
mind[348]:=KlimaGal.IzhodniVentStatus;
mind[349]:=KlimaGal.KompresorStatus;
mind[350]:=KlimaGal.VlazilecStatus;
mind[351]:=PMMgal.AlarmPhase[1].GlobalAlarmReg;
mind[352]:=PMMgal.AlarmPhase[2].GlobalAlarmReg;
mind[353]:=PMMgal.AlarmPhase[3].GlobalAlarmReg;
mind[354]:=kom_nast_cas_izpada;
(*Branje UINT*)
(**)
mind[8000]:=PMMgal.AlarmPhase[1].C01_16_60to80;
mind[8001]:=PMMgal.AlarmPhase[1].C01_16_over80;
mind[8002]:=PMMgal.AlarmPhase[1].C17_32_60to80;
mind[8003]:=PMMgal.AlarmPhase[1].C17_32_over80;
mind[8004]:=PMMgal.AlarmPhase[1].C33_42_60to80;
mind[8005]:=PMMgal.AlarmPhase[1].C33_42_over80;
mind[8006]:=PMMgal.AlarmPhase[2].C01_16_60to80;
mind[8007]:=PMMgal.AlarmPhase[2].C01_16_over80;
mind[8008]:=PMMgal.AlarmPhase[2].C17_32_60to80;
mind[8009]:=PMMgal.AlarmPhase[2].C17_32_over80;
mind[8010]:=PMMgal.AlarmPhase[2].C33_42_60to80;
mind[8011]:=PMMgal.AlarmPhase[2].C33_42_over80;
mind[8012]:=PMMgal.AlarmPhase[3].C01_16_60to80;
mind[8013]:=PMMgal.AlarmPhase[3].C01_16_over80;
mind[8014]:=PMMgal.AlarmPhase[3].C17_32_60to80;
mind[8015]:=PMMgal.AlarmPhase[3].C17_32_over80;
mind[8016]:=PMMgal.AlarmPhase[3].C33_42_60to80;
mind[8017]:=PMMgal.AlarmPhase[3].C33_42_over80;
mind[8018]:=PMMgal.Alarms;
(*Branje LONG*)
(**)
(*Branje REAL*)
(**)
Read_Real(rVar:=Circ[1].CosFi_III,lo:=4000,hi:=4001);
Read_Real(rVar:=Circ[1].DelovnaEnergija,lo:=4002,hi:=4003);
Read_Real(rVar:=Circ[1].DelovnaMoc_III,lo:=4004,hi:=4005);
Read_Real(rVar:=Circ[1].DelovnaMoc_L1,lo:=4006,hi:=4007);
Read_Real(rVar:=Circ[1].DelovnaMoc_L2,lo:=4008,hi:=4009);
Read_Real(rVar:=Circ[1].DelovnaMoc_L3,lo:=4010,hi:=4011);
Read_Real(rVar:=Circ[1].Frekvenca_L1,lo:=4012,hi:=4013);
Read_Real(rVar:=Circ[1].InduktivnaEnergija,lo:=4014,hi:=4015);
Read_Real(rVar:=Circ[1].InduktivnaMoc_III,lo:=4016,hi:=4017);
Read_Real(rVar:=Circ[1].JalovaMoc_L1,lo:=4018,hi:=4019);
Read_Real(rVar:=Circ[1].JalovaMoc_L2,lo:=4020,hi:=4021);
Read_Real(rVar:=Circ[1].JalovaMoc_L3,lo:=4022,hi:=4023);
Read_Real(rVar:=Circ[1].KapacitivnaEnergija,lo:=4024,hi:=4025);
Read_Real(rVar:=Circ[1].KapacitivnaMoc_III,lo:=4026,hi:=4027);
Read_Real(rVar:=Circ[1].MaximumDemand,lo:=4028,hi:=4029);
Read_Real(rVar:=Circ[1].Napetost_L1_L2,lo:=4030,hi:=4031);
Read_Real(rVar:=Circ[1].Napetost_L1_N,lo:=4032,hi:=4033);
Read_Real(rVar:=Circ[1].Napetost_L2_L3,lo:=4034,hi:=4035);
Read_Real(rVar:=Circ[1].Napetost_L2_N,lo:=4036,hi:=4037);
Read_Real(rVar:=Circ[1].Napetost_L3_L1,lo:=4038,hi:=4039);
Read_Real(rVar:=Circ[1].Napetost_L3_N,lo:=4040,hi:=4041);
Read_Real(rVar:=Circ[1].NavideznaMoc_III,lo:=4042,hi:=4043);
Read_Real(rVar:=Circ[1].NicelniTok,lo:=4044,hi:=4045);
Read_Real(rVar:=Circ[1].PowerFactor_III,lo:=4046,hi:=4047);
Read_Real(rVar:=Circ[1].PowerFactor_L1,lo:=4048,hi:=4049);
Read_Real(rVar:=Circ[1].PowerFactor_L2,lo:=4050,hi:=4051);
Read_Real(rVar:=Circ[1].PowerFactor_L3,lo:=4052,hi:=4053);
Read_Real(rVar:=Circ[1].THDI_L1,lo:=4054,hi:=4055);
Read_Real(rVar:=Circ[1].THDI_L2,lo:=4056,hi:=4057);
Read_Real(rVar:=Circ[1].THDI_L3,lo:=4058,hi:=4059);
Read_Real(rVar:=Circ[1].THDV_L1,lo:=4060,hi:=4061);
Read_Real(rVar:=Circ[1].THDV_L2,lo:=4062,hi:=4063);
Read_Real(rVar:=Circ[1].THDV_L3,lo:=4064,hi:=4065);
Read_Real(rVar:=Circ[1].Tok_L1,lo:=4066,hi:=4067);
Read_Real(rVar:=Circ[1].Tok_L2,lo:=4068,hi:=4069);
Read_Real(rVar:=Circ[1].Tok_L3,lo:=4070,hi:=4071);
Read_Real(rVar:=Circ[1].TokPovprecje_III,lo:=4072,hi:=4073);
Read_Real(rVar:=Circutor.CosFi_III,lo:=4074,hi:=4075);
Read_Real(rVar:=Circutor.DelovnaEnergija,lo:=4076,hi:=4077);
Read_Real(rVar:=Circutor.DelovnaMoc_III,lo:=4078,hi:=4079);
Read_Real(rVar:=Circutor.DelovnaMoc_L1,lo:=4080,hi:=4081);
Read_Real(rVar:=Circutor.DelovnaMoc_L2,lo:=4082,hi:=4083);
Read_Real(rVar:=Circutor.DelovnaMoc_L3,lo:=4084,hi:=4085);
Read_Real(rVar:=Circutor.Frekvenca_L1,lo:=4086,hi:=4087);
Read_Real(rVar:=Circutor.InduktivnaEnergija,lo:=4088,hi:=4089);
Read_Real(rVar:=Circutor.InduktivnaMoc_III,lo:=4090,hi:=4091);
Read_Real(rVar:=Circutor.JalovaMoc_L1,lo:=4092,hi:=4093);
Read_Real(rVar:=Circutor.JalovaMoc_L2,lo:=4094,hi:=4095);
Read_Real(rVar:=Circutor.JalovaMoc_L3,lo:=4096,hi:=4097);
Read_Real(rVar:=Circutor.KapacitivnaEnergija,lo:=4098,hi:=4099);
Read_Real(rVar:=Circutor.KapacitivnaMoc_III,lo:=4100,hi:=4101);
Read_Real(rVar:=Circutor.MaximumDemand,lo:=4102,hi:=4103);
Read_Real(rVar:=Circutor.Napetost_L1_L2,lo:=4104,hi:=4105);
Read_Real(rVar:=Circutor.Napetost_L1_N,lo:=4106,hi:=4107);
Read_Real(rVar:=Circutor.Napetost_L2_L3,lo:=4108,hi:=4109);
Read_Real(rVar:=Circutor.Napetost_L2_N,lo:=4110,hi:=4111);
Read_Real(rVar:=Circutor.Napetost_L3_L1,lo:=4112,hi:=4113);
Read_Real(rVar:=Circutor.Napetost_L3_N,lo:=4114,hi:=4115);
Read_Real(rVar:=Circutor.NavideznaMoc_III,lo:=4116,hi:=4117);
Read_Real(rVar:=Circutor.NicelniTok,lo:=4118,hi:=4119);
Read_Real(rVar:=Circutor.PowerFactor_III,lo:=4120,hi:=4121);
Read_Real(rVar:=Circutor.PowerFactor_L1,lo:=4122,hi:=4123);
Read_Real(rVar:=Circutor.PowerFactor_L2,lo:=4124,hi:=4125);
Read_Real(rVar:=Circutor.PowerFactor_L3,lo:=4126,hi:=4127);
Read_Real(rVar:=Circutor.THDI_L1,lo:=4128,hi:=4129);
Read_Real(rVar:=Circutor.THDI_L2,lo:=4130,hi:=4131);
Read_Real(rVar:=Circutor.THDI_L3,lo:=4132,hi:=4133);
Read_Real(rVar:=Circutor.THDV_L1,lo:=4134,hi:=4135);
Read_Real(rVar:=Circutor.THDV_L2,lo:=4136,hi:=4137);
Read_Real(rVar:=Circutor.THDV_L3,lo:=4138,hi:=4139);
Read_Real(rVar:=Circutor.Tok_L1,lo:=4140,hi:=4141);
Read_Real(rVar:=Circutor.Tok_L2,lo:=4142,hi:=4143);
Read_Real(rVar:=Circutor.Tok_L3,lo:=4144,hi:=4145);
Read_Real(rVar:=Circutor.TokPovprecje_III,lo:=4146,hi:=4147);
Read_Real(rVar:=Klima[1].NastMaxTemp,lo:=4148,hi:=4149);
Read_Real(rVar:=Klima[1].NastMaxVlaznost,lo:=4150,hi:=4151);
Read_Real(rVar:=Klima[1].NastMinTemp,lo:=4152,hi:=4153);
Read_Real(rVar:=Klima[1].NastMinVlaznost,lo:=4154,hi:=4155);
Read_Real(rVar:=Klima[1].NastTempProstora,lo:=4156,hi:=4157);
Read_Real(rVar:=Klima[1].NastVlaznost,lo:=4158,hi:=4159);
Read_Real(rVar:=Klima[1].ObratovalneUre,lo:=4160,hi:=4161);
Read_Real(rVar:=Klima[1].TemperaturaProstora,lo:=4162,hi:=4163);
Read_Real(rVar:=Klima[1].TempIzpihanegaZraka,lo:=4164,hi:=4165);
Read_Real(rVar:=Klima[1].TempPovratneVode,lo:=4166,hi:=4167);
Read_Real(rVar:=Klima[1].VlaznostProstora,lo:=4168,hi:=4169);
Read_Real(rVar:=Klima[1].ZunanjaTemp,lo:=4170,hi:=4171);
Read_Real(rVar:=Klima[2].NastMaxTemp,lo:=4172,hi:=4173);
Read_Real(rVar:=Klima[2].NastMaxVlaznost,lo:=4174,hi:=4175);
Read_Real(rVar:=Klima[2].NastMinTemp,lo:=4176,hi:=4177);
Read_Real(rVar:=Klima[2].NastMinVlaznost,lo:=4178,hi:=4179);
Read_Real(rVar:=Klima[2].NastTempProstora,lo:=4180,hi:=4181);
Read_Real(rVar:=Klima[2].NastVlaznost,lo:=4182,hi:=4183);
Read_Real(rVar:=Klima[2].ObratovalneUre,lo:=4184,hi:=4185);
Read_Real(rVar:=Klima[2].TemperaturaProstora,lo:=4186,hi:=4187);
Read_Real(rVar:=Klima[2].TempIzpihanegaZraka,lo:=4188,hi:=4189);
Read_Real(rVar:=Klima[2].TempPovratneVode,lo:=4190,hi:=4191);
Read_Real(rVar:=Klima[2].VlaznostProstora,lo:=4192,hi:=4193);
Read_Real(rVar:=Klima[2].ZunanjaTemp,lo:=4194,hi:=4195);
Read_Real(rVar:=PMM[1].ActivePowerPhaseA_kW,lo:=4196,hi:=4197);
Read_Real(rVar:=PMM[1].ActivePowerPhaseB_kW,lo:=4198,hi:=4199);
Read_Real(rVar:=PMM[1].ActivePowerPhaseC_kW,lo:=4200,hi:=4201);
Read_Real(rVar:=PMM[1].AverageCurrent_A,lo:=4202,hi:=4203);
Read_Real(rVar:=PMM[1].AveragePhaseToNeutral_V,lo:=4204,hi:=4205);
Read_Real(rVar:=PMM[1].AveragePhaseToPhase_V,lo:=4206,hi:=4207);
Read_Real(rVar:=PMM[1].CurrentInPhaseA_A,lo:=4208,hi:=4209);
Read_Real(rVar:=PMM[1].CurrentInPhaseB_A,lo:=4210,hi:=4211);
Read_Real(rVar:=PMM[1].CurrentInPhaseC_A,lo:=4212,hi:=4213);
Read_Real(rVar:=PMM[1].EnergyConsumed_kWh,lo:=4214,hi:=4215);
Read_Real(rVar:=PMM[1].Frequency_Hz,lo:=4216,hi:=4217);
Read_Real(rVar:=PMM[1].NeutralCurrent_A,lo:=4218,hi:=4219);
Read_Real(rVar:=PMM[1].Phase[1].Current[10],lo:=4220,hi:=4221);
Read_Real(rVar:=PMM[1].Phase[1].Current[11],lo:=4222,hi:=4223);
Read_Real(rVar:=PMM[1].Phase[1].Current[12],lo:=4224,hi:=4225);
Read_Real(rVar:=PMM[1].Phase[1].Current[13],lo:=4226,hi:=4227);
Read_Real(rVar:=PMM[1].Phase[1].Current[14],lo:=4228,hi:=4229);
Read_Real(rVar:=PMM[1].Phase[1].Current[15],lo:=4230,hi:=4231);
Read_Real(rVar:=PMM[1].Phase[1].Current[16],lo:=4232,hi:=4233);
Read_Real(rVar:=PMM[1].Phase[1].Current[17],lo:=4234,hi:=4235);
Read_Real(rVar:=PMM[1].Phase[1].Current[18],lo:=4236,hi:=4237);
Read_Real(rVar:=PMM[1].Phase[1].Current[19],lo:=4238,hi:=4239);
Read_Real(rVar:=PMM[1].Phase[1].Current[1],lo:=4240,hi:=4241);
Read_Real(rVar:=PMM[1].Phase[1].Current[20],lo:=4242,hi:=4243);
Read_Real(rVar:=PMM[1].Phase[1].Current[21],lo:=4244,hi:=4245);
Read_Real(rVar:=PMM[1].Phase[1].Current[22],lo:=4246,hi:=4247);
Read_Real(rVar:=PMM[1].Phase[1].Current[23],lo:=4248,hi:=4249);
Read_Real(rVar:=PMM[1].Phase[1].Current[24],lo:=4250,hi:=4251);
Read_Real(rVar:=PMM[1].Phase[1].Current[25],lo:=4252,hi:=4253);
Read_Real(rVar:=PMM[1].Phase[1].Current[26],lo:=4254,hi:=4255);
Read_Real(rVar:=PMM[1].Phase[1].Current[27],lo:=4256,hi:=4257);
Read_Real(rVar:=PMM[1].Phase[1].Current[28],lo:=4258,hi:=4259);
Read_Real(rVar:=PMM[1].Phase[1].Current[29],lo:=4260,hi:=4261);
Read_Real(rVar:=PMM[1].Phase[1].Current[2],lo:=4262,hi:=4263);
Read_Real(rVar:=PMM[1].Phase[1].Current[30],lo:=4264,hi:=4265);
Read_Real(rVar:=PMM[1].Phase[1].Current[31],lo:=4266,hi:=4267);
Read_Real(rVar:=PMM[1].Phase[1].Current[32],lo:=4268,hi:=4269);
Read_Real(rVar:=PMM[1].Phase[1].Current[33],lo:=4270,hi:=4271);
Read_Real(rVar:=PMM[1].Phase[1].Current[34],lo:=4272,hi:=4273);
Read_Real(rVar:=PMM[1].Phase[1].Current[35],lo:=4274,hi:=4275);
Read_Real(rVar:=PMM[1].Phase[1].Current[36],lo:=4276,hi:=4277);
Read_Real(rVar:=PMM[1].Phase[1].Current[37],lo:=4278,hi:=4279);
Read_Real(rVar:=PMM[1].Phase[1].Current[38],lo:=4280,hi:=4281);
Read_Real(rVar:=PMM[1].Phase[1].Current[39],lo:=4282,hi:=4283);
Read_Real(rVar:=PMM[1].Phase[1].Current[3],lo:=4284,hi:=4285);
Read_Real(rVar:=PMM[1].Phase[1].Current[40],lo:=4286,hi:=4287);
Read_Real(rVar:=PMM[1].Phase[1].Current[41],lo:=4288,hi:=4289);
Read_Real(rVar:=PMM[1].Phase[1].Current[42],lo:=4290,hi:=4291);
Read_Real(rVar:=PMM[1].Phase[1].Current[4],lo:=4292,hi:=4293);
Read_Real(rVar:=PMM[1].Phase[1].Current[5],lo:=4294,hi:=4295);
Read_Real(rVar:=PMM[1].Phase[1].Current[6],lo:=4296,hi:=4297);
Read_Real(rVar:=PMM[1].Phase[1].Current[7],lo:=4298,hi:=4299);
Read_Real(rVar:=PMM[1].Phase[1].Current[8],lo:=4300,hi:=4301);
Read_Real(rVar:=PMM[1].Phase[1].Current[9],lo:=4302,hi:=4303);
Read_Real(rVar:=PMM[1].Phase[2].Current[10],lo:=4304,hi:=4305);
Read_Real(rVar:=PMM[1].Phase[2].Current[11],lo:=4306,hi:=4307);
Read_Real(rVar:=PMM[1].Phase[2].Current[12],lo:=4308,hi:=4309);
Read_Real(rVar:=PMM[1].Phase[2].Current[13],lo:=4310,hi:=4311);
Read_Real(rVar:=PMM[1].Phase[2].Current[14],lo:=4312,hi:=4313);
Read_Real(rVar:=PMM[1].Phase[2].Current[15],lo:=4314,hi:=4315);
Read_Real(rVar:=PMM[1].Phase[2].Current[16],lo:=4316,hi:=4317);
Read_Real(rVar:=PMM[1].Phase[2].Current[17],lo:=4318,hi:=4319);
Read_Real(rVar:=PMM[1].Phase[2].Current[18],lo:=4320,hi:=4321);
Read_Real(rVar:=PMM[1].Phase[2].Current[19],lo:=4322,hi:=4323);
Read_Real(rVar:=PMM[1].Phase[2].Current[1],lo:=4324,hi:=4325);
Read_Real(rVar:=PMM[1].Phase[2].Current[20],lo:=4326,hi:=4327);
Read_Real(rVar:=PMM[1].Phase[2].Current[21],lo:=4328,hi:=4329);
Read_Real(rVar:=PMM[1].Phase[2].Current[22],lo:=4330,hi:=4331);
Read_Real(rVar:=PMM[1].Phase[2].Current[23],lo:=4332,hi:=4333);
Read_Real(rVar:=PMM[1].Phase[2].Current[24],lo:=4334,hi:=4335);
Read_Real(rVar:=PMM[1].Phase[2].Current[25],lo:=4336,hi:=4337);
Read_Real(rVar:=PMM[1].Phase[2].Current[26],lo:=4338,hi:=4339);
Read_Real(rVar:=PMM[1].Phase[2].Current[27],lo:=4340,hi:=4341);
Read_Real(rVar:=PMM[1].Phase[2].Current[28],lo:=4342,hi:=4343);
Read_Real(rVar:=PMM[1].Phase[2].Current[29],lo:=4344,hi:=4345);
Read_Real(rVar:=PMM[1].Phase[2].Current[2],lo:=4346,hi:=4347);
Read_Real(rVar:=PMM[1].Phase[2].Current[30],lo:=4348,hi:=4349);
Read_Real(rVar:=PMM[1].Phase[2].Current[31],lo:=4350,hi:=4351);
Read_Real(rVar:=PMM[1].Phase[2].Current[32],lo:=4352,hi:=4353);
Read_Real(rVar:=PMM[1].Phase[2].Current[33],lo:=4354,hi:=4355);
Read_Real(rVar:=PMM[1].Phase[2].Current[34],lo:=4356,hi:=4357);
Read_Real(rVar:=PMM[1].Phase[2].Current[35],lo:=4358,hi:=4359);
Read_Real(rVar:=PMM[1].Phase[2].Current[36],lo:=4360,hi:=4361);
Read_Real(rVar:=PMM[1].Phase[2].Current[37],lo:=4362,hi:=4363);
Read_Real(rVar:=PMM[1].Phase[2].Current[38],lo:=4364,hi:=4365);
Read_Real(rVar:=PMM[1].Phase[2].Current[39],lo:=4366,hi:=4367);
Read_Real(rVar:=PMM[1].Phase[2].Current[3],lo:=4368,hi:=4369);
Read_Real(rVar:=PMM[1].Phase[2].Current[40],lo:=4370,hi:=4371);
Read_Real(rVar:=PMM[1].Phase[2].Current[41],lo:=4372,hi:=4373);
Read_Real(rVar:=PMM[1].Phase[2].Current[42],lo:=4374,hi:=4375);
Read_Real(rVar:=PMM[1].Phase[2].Current[4],lo:=4376,hi:=4377);
Read_Real(rVar:=PMM[1].Phase[2].Current[5],lo:=4378,hi:=4379);
Read_Real(rVar:=PMM[1].Phase[2].Current[6],lo:=4380,hi:=4381);
Read_Real(rVar:=PMM[1].Phase[2].Current[7],lo:=4382,hi:=4383);
Read_Real(rVar:=PMM[1].Phase[2].Current[8],lo:=4384,hi:=4385);
Read_Real(rVar:=PMM[1].Phase[2].Current[9],lo:=4386,hi:=4387);
Read_Real(rVar:=PMM[1].Phase[3].Current[10],lo:=4388,hi:=4389);
Read_Real(rVar:=PMM[1].Phase[3].Current[11],lo:=4390,hi:=4391);
Read_Real(rVar:=PMM[1].Phase[3].Current[12],lo:=4392,hi:=4393);
Read_Real(rVar:=PMM[1].Phase[3].Current[13],lo:=4394,hi:=4395);
Read_Real(rVar:=PMM[1].Phase[3].Current[14],lo:=4396,hi:=4397);
Read_Real(rVar:=PMM[1].Phase[3].Current[15],lo:=4398,hi:=4399);
Read_Real(rVar:=PMM[1].Phase[3].Current[16],lo:=4400,hi:=4401);
Read_Real(rVar:=PMM[1].Phase[3].Current[17],lo:=4402,hi:=4403);
Read_Real(rVar:=PMM[1].Phase[3].Current[18],lo:=4404,hi:=4405);
Read_Real(rVar:=PMM[1].Phase[3].Current[19],lo:=4406,hi:=4407);
Read_Real(rVar:=PMM[1].Phase[3].Current[1],lo:=4408,hi:=4409);
Read_Real(rVar:=PMM[1].Phase[3].Current[20],lo:=4410,hi:=4411);
Read_Real(rVar:=PMM[1].Phase[3].Current[21],lo:=4412,hi:=4413);
Read_Real(rVar:=PMM[1].Phase[3].Current[22],lo:=4414,hi:=4415);
Read_Real(rVar:=PMM[1].Phase[3].Current[23],lo:=4416,hi:=4417);
Read_Real(rVar:=PMM[1].Phase[3].Current[24],lo:=4418,hi:=4419);
Read_Real(rVar:=PMM[1].Phase[3].Current[25],lo:=4420,hi:=4421);
Read_Real(rVar:=PMM[1].Phase[3].Current[26],lo:=4422,hi:=4423);
Read_Real(rVar:=PMM[1].Phase[3].Current[27],lo:=4424,hi:=4425);
Read_Real(rVar:=PMM[1].Phase[3].Current[28],lo:=4426,hi:=4427);
Read_Real(rVar:=PMM[1].Phase[3].Current[29],lo:=4428,hi:=4429);
Read_Real(rVar:=PMM[1].Phase[3].Current[2],lo:=4430,hi:=4431);
Read_Real(rVar:=PMM[1].Phase[3].Current[30],lo:=4432,hi:=4433);
Read_Real(rVar:=PMM[1].Phase[3].Current[31],lo:=4434,hi:=4435);
Read_Real(rVar:=PMM[1].Phase[3].Current[32],lo:=4436,hi:=4437);
Read_Real(rVar:=PMM[1].Phase[3].Current[33],lo:=4438,hi:=4439);
Read_Real(rVar:=PMM[1].Phase[3].Current[34],lo:=4440,hi:=4441);
Read_Real(rVar:=PMM[1].Phase[3].Current[35],lo:=4442,hi:=4443);
Read_Real(rVar:=PMM[1].Phase[3].Current[36],lo:=4444,hi:=4445);
Read_Real(rVar:=PMM[1].Phase[3].Current[37],lo:=4446,hi:=4447);
Read_Real(rVar:=PMM[1].Phase[3].Current[38],lo:=4448,hi:=4449);
Read_Real(rVar:=PMM[1].Phase[3].Current[39],lo:=4450,hi:=4451);
Read_Real(rVar:=PMM[1].Phase[3].Current[3],lo:=4452,hi:=4453);
Read_Real(rVar:=PMM[1].Phase[3].Current[40],lo:=4454,hi:=4455);
Read_Real(rVar:=PMM[1].Phase[3].Current[41],lo:=4456,hi:=4457);
Read_Real(rVar:=PMM[1].Phase[3].Current[42],lo:=4458,hi:=4459);
Read_Real(rVar:=PMM[1].Phase[3].Current[4],lo:=4460,hi:=4461);
Read_Real(rVar:=PMM[1].Phase[3].Current[5],lo:=4462,hi:=4463);
Read_Real(rVar:=PMM[1].Phase[3].Current[6],lo:=4464,hi:=4465);
Read_Real(rVar:=PMM[1].Phase[3].Current[7],lo:=4466,hi:=4467);
Read_Real(rVar:=PMM[1].Phase[3].Current[8],lo:=4468,hi:=4469);
Read_Real(rVar:=PMM[1].Phase[3].Current[9],lo:=4470,hi:=4471);
Read_Real(rVar:=PMM[1].PowerFactorPhaseA,lo:=4472,hi:=4473);
Read_Real(rVar:=PMM[1].PowerFactorPhaseB,lo:=4474,hi:=4475);
Read_Real(rVar:=PMM[1].PowerFactorPhaseC,lo:=4476,hi:=4477);
Read_Real(rVar:=PMM[1].TotalActivePower_kW,lo:=4478,hi:=4479);
Read_Real(rVar:=PMM[1].TotalAparentPower_kVA,lo:=4480,hi:=4481);
Read_Real(rVar:=PMM[1].TotalPowerFactor,lo:=4482,hi:=4483);
Read_Real(rVar:=PMM[1].TotalReactivePower_kVAR,lo:=4484,hi:=4485);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseAB_V,lo:=4486,hi:=4487);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseAN_V,lo:=4488,hi:=4489);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseBC_V,lo:=4490,hi:=4491);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseBN_V,lo:=4492,hi:=4493);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseCA_V,lo:=4494,hi:=4495);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseCN_V,lo:=4496,hi:=4497);
Read_Real(rVar:=PMM[2].ActivePowerPhaseA_kW,lo:=4498,hi:=4499);
Read_Real(rVar:=PMM[2].ActivePowerPhaseB_kW,lo:=4500,hi:=4501);
Read_Real(rVar:=PMM[2].ActivePowerPhaseC_kW,lo:=4502,hi:=4503);
Read_Real(rVar:=PMM[2].AverageCurrent_A,lo:=4504,hi:=4505);
Read_Real(rVar:=PMM[2].AveragePhaseToNeutral_V,lo:=4506,hi:=4507);
Read_Real(rVar:=PMM[2].AveragePhaseToPhase_V,lo:=4508,hi:=4509);
Read_Real(rVar:=PMM[2].CurrentInPhaseA_A,lo:=4510,hi:=4511);
Read_Real(rVar:=PMM[2].CurrentInPhaseB_A,lo:=4512,hi:=4513);
Read_Real(rVar:=PMM[2].CurrentInPhaseC_A,lo:=4514,hi:=4515);
Read_Real(rVar:=PMM[2].EnergyConsumed_kWh,lo:=4516,hi:=4517);
Read_Real(rVar:=PMM[2].Frequency_Hz,lo:=4518,hi:=4519);
Read_Real(rVar:=PMM[2].NeutralCurrent_A,lo:=4520,hi:=4521);
Read_Real(rVar:=PMM[2].Phase[1].Current[10],lo:=4522,hi:=4523);
Read_Real(rVar:=PMM[2].Phase[1].Current[11],lo:=4524,hi:=4525);
Read_Real(rVar:=PMM[2].Phase[1].Current[12],lo:=4526,hi:=4527);
Read_Real(rVar:=PMM[2].Phase[1].Current[13],lo:=4528,hi:=4529);
Read_Real(rVar:=PMM[2].Phase[1].Current[14],lo:=4530,hi:=4531);
Read_Real(rVar:=PMM[2].Phase[1].Current[15],lo:=4532,hi:=4533);
Read_Real(rVar:=PMM[2].Phase[1].Current[16],lo:=4534,hi:=4535);
Read_Real(rVar:=PMM[2].Phase[1].Current[17],lo:=4536,hi:=4537);
Read_Real(rVar:=PMM[2].Phase[1].Current[18],lo:=4538,hi:=4539);
Read_Real(rVar:=PMM[2].Phase[1].Current[19],lo:=4540,hi:=4541);
Read_Real(rVar:=PMM[2].Phase[1].Current[1],lo:=4542,hi:=4543);
Read_Real(rVar:=PMM[2].Phase[1].Current[20],lo:=4544,hi:=4545);
Read_Real(rVar:=PMM[2].Phase[1].Current[21],lo:=4546,hi:=4547);
Read_Real(rVar:=PMM[2].Phase[1].Current[22],lo:=4548,hi:=4549);
Read_Real(rVar:=PMM[2].Phase[1].Current[23],lo:=4550,hi:=4551);
Read_Real(rVar:=PMM[2].Phase[1].Current[24],lo:=4552,hi:=4553);
Read_Real(rVar:=PMM[2].Phase[1].Current[25],lo:=4554,hi:=4555);
Read_Real(rVar:=PMM[2].Phase[1].Current[26],lo:=4556,hi:=4557);
Read_Real(rVar:=PMM[2].Phase[1].Current[27],lo:=4558,hi:=4559);
Read_Real(rVar:=PMM[2].Phase[1].Current[28],lo:=4560,hi:=4561);
Read_Real(rVar:=PMM[2].Phase[1].Current[29],lo:=4562,hi:=4563);
Read_Real(rVar:=PMM[2].Phase[1].Current[2],lo:=4564,hi:=4565);
Read_Real(rVar:=PMM[2].Phase[1].Current[30],lo:=4566,hi:=4567);
Read_Real(rVar:=PMM[2].Phase[1].Current[31],lo:=4568,hi:=4569);
Read_Real(rVar:=PMM[2].Phase[1].Current[32],lo:=4570,hi:=4571);
Read_Real(rVar:=PMM[2].Phase[1].Current[33],lo:=4572,hi:=4573);
Read_Real(rVar:=PMM[2].Phase[1].Current[34],lo:=4574,hi:=4575);
Read_Real(rVar:=PMM[2].Phase[1].Current[35],lo:=4576,hi:=4577);
Read_Real(rVar:=PMM[2].Phase[1].Current[36],lo:=4578,hi:=4579);
Read_Real(rVar:=PMM[2].Phase[1].Current[37],lo:=4580,hi:=4581);
Read_Real(rVar:=PMM[2].Phase[1].Current[38],lo:=4582,hi:=4583);
Read_Real(rVar:=PMM[2].Phase[1].Current[39],lo:=4584,hi:=4585);
Read_Real(rVar:=PMM[2].Phase[1].Current[3],lo:=4586,hi:=4587);
Read_Real(rVar:=PMM[2].Phase[1].Current[40],lo:=4588,hi:=4589);
Read_Real(rVar:=PMM[2].Phase[1].Current[41],lo:=4590,hi:=4591);
Read_Real(rVar:=PMM[2].Phase[1].Current[42],lo:=4592,hi:=4593);
Read_Real(rVar:=PMM[2].Phase[1].Current[4],lo:=4594,hi:=4595);
Read_Real(rVar:=PMM[2].Phase[1].Current[5],lo:=4596,hi:=4597);
Read_Real(rVar:=PMM[2].Phase[1].Current[6],lo:=4598,hi:=4599);
Read_Real(rVar:=PMM[2].Phase[1].Current[7],lo:=4600,hi:=4601);
Read_Real(rVar:=PMM[2].Phase[1].Current[8],lo:=4602,hi:=4603);
Read_Real(rVar:=PMM[2].Phase[1].Current[9],lo:=4604,hi:=4605);
Read_Real(rVar:=PMM[2].Phase[2].Current[10],lo:=4606,hi:=4607);
Read_Real(rVar:=PMM[2].Phase[2].Current[11],lo:=4608,hi:=4609);
Read_Real(rVar:=PMM[2].Phase[2].Current[12],lo:=4610,hi:=4611);
Read_Real(rVar:=PMM[2].Phase[2].Current[13],lo:=4612,hi:=4613);
Read_Real(rVar:=PMM[2].Phase[2].Current[14],lo:=4614,hi:=4615);
Read_Real(rVar:=PMM[2].Phase[2].Current[15],lo:=4616,hi:=4617);
Read_Real(rVar:=PMM[2].Phase[2].Current[16],lo:=4618,hi:=4619);
Read_Real(rVar:=PMM[2].Phase[2].Current[17],lo:=4620,hi:=4621);
Read_Real(rVar:=PMM[2].Phase[2].Current[18],lo:=4622,hi:=4623);
Read_Real(rVar:=PMM[2].Phase[2].Current[19],lo:=4624,hi:=4625);
Read_Real(rVar:=PMM[2].Phase[2].Current[1],lo:=4626,hi:=4627);
Read_Real(rVar:=PMM[2].Phase[2].Current[20],lo:=4628,hi:=4629);
Read_Real(rVar:=PMM[2].Phase[2].Current[21],lo:=4630,hi:=4631);
Read_Real(rVar:=PMM[2].Phase[2].Current[22],lo:=4632,hi:=4633);
Read_Real(rVar:=PMM[2].Phase[2].Current[23],lo:=4634,hi:=4635);
Read_Real(rVar:=PMM[2].Phase[2].Current[24],lo:=4636,hi:=4637);
Read_Real(rVar:=PMM[2].Phase[2].Current[25],lo:=4638,hi:=4639);
Read_Real(rVar:=PMM[2].Phase[2].Current[26],lo:=4640,hi:=4641);
Read_Real(rVar:=PMM[2].Phase[2].Current[27],lo:=4642,hi:=4643);
Read_Real(rVar:=PMM[2].Phase[2].Current[28],lo:=4644,hi:=4645);
Read_Real(rVar:=PMM[2].Phase[2].Current[29],lo:=4646,hi:=4647);
Read_Real(rVar:=PMM[2].Phase[2].Current[2],lo:=4648,hi:=4649);
Read_Real(rVar:=PMM[2].Phase[2].Current[30],lo:=4650,hi:=4651);
Read_Real(rVar:=PMM[2].Phase[2].Current[31],lo:=4652,hi:=4653);
Read_Real(rVar:=PMM[2].Phase[2].Current[32],lo:=4654,hi:=4655);
Read_Real(rVar:=PMM[2].Phase[2].Current[33],lo:=4656,hi:=4657);
Read_Real(rVar:=PMM[2].Phase[2].Current[34],lo:=4658,hi:=4659);
Read_Real(rVar:=PMM[2].Phase[2].Current[35],lo:=4660,hi:=4661);
Read_Real(rVar:=PMM[2].Phase[2].Current[36],lo:=4662,hi:=4663);
Read_Real(rVar:=PMM[2].Phase[2].Current[37],lo:=4664,hi:=4665);
Read_Real(rVar:=PMM[2].Phase[2].Current[38],lo:=4666,hi:=4667);
Read_Real(rVar:=PMM[2].Phase[2].Current[39],lo:=4668,hi:=4669);
Read_Real(rVar:=PMM[2].Phase[2].Current[3],lo:=4670,hi:=4671);
Read_Real(rVar:=PMM[2].Phase[2].Current[40],lo:=4672,hi:=4673);
Read_Real(rVar:=PMM[2].Phase[2].Current[41],lo:=4674,hi:=4675);
Read_Real(rVar:=PMM[2].Phase[2].Current[42],lo:=4676,hi:=4677);
Read_Real(rVar:=PMM[2].Phase[2].Current[4],lo:=4678,hi:=4679);
Read_Real(rVar:=PMM[2].Phase[2].Current[5],lo:=4680,hi:=4681);
Read_Real(rVar:=PMM[2].Phase[2].Current[6],lo:=4682,hi:=4683);
Read_Real(rVar:=PMM[2].Phase[2].Current[7],lo:=4684,hi:=4685);
Read_Real(rVar:=PMM[2].Phase[2].Current[8],lo:=4686,hi:=4687);
Read_Real(rVar:=PMM[2].Phase[2].Current[9],lo:=4688,hi:=4689);
Read_Real(rVar:=PMM[2].Phase[3].Current[10],lo:=4690,hi:=4691);
Read_Real(rVar:=PMM[2].Phase[3].Current[11],lo:=4692,hi:=4693);
Read_Real(rVar:=PMM[2].Phase[3].Current[12],lo:=4694,hi:=4695);
Read_Real(rVar:=PMM[2].Phase[3].Current[13],lo:=4696,hi:=4697);
Read_Real(rVar:=PMM[2].Phase[3].Current[14],lo:=4698,hi:=4699);
Read_Real(rVar:=PMM[2].Phase[3].Current[15],lo:=4700,hi:=4701);
Read_Real(rVar:=PMM[2].Phase[3].Current[16],lo:=4702,hi:=4703);
Read_Real(rVar:=PMM[2].Phase[3].Current[17],lo:=4704,hi:=4705);
Read_Real(rVar:=PMM[2].Phase[3].Current[18],lo:=4706,hi:=4707);
Read_Real(rVar:=PMM[2].Phase[3].Current[19],lo:=4708,hi:=4709);
Read_Real(rVar:=PMM[2].Phase[3].Current[1],lo:=4710,hi:=4711);
Read_Real(rVar:=PMM[2].Phase[3].Current[20],lo:=4712,hi:=4713);
Read_Real(rVar:=PMM[2].Phase[3].Current[21],lo:=4714,hi:=4715);
Read_Real(rVar:=PMM[2].Phase[3].Current[22],lo:=4716,hi:=4717);
Read_Real(rVar:=PMM[2].Phase[3].Current[23],lo:=4718,hi:=4719);
Read_Real(rVar:=PMM[2].Phase[3].Current[24],lo:=4720,hi:=4721);
Read_Real(rVar:=PMM[2].Phase[3].Current[25],lo:=4722,hi:=4723);
Read_Real(rVar:=PMM[2].Phase[3].Current[26],lo:=4724,hi:=4725);
Read_Real(rVar:=PMM[2].Phase[3].Current[27],lo:=4726,hi:=4727);
Read_Real(rVar:=PMM[2].Phase[3].Current[28],lo:=4728,hi:=4729);
Read_Real(rVar:=PMM[2].Phase[3].Current[29],lo:=4730,hi:=4731);
Read_Real(rVar:=PMM[2].Phase[3].Current[2],lo:=4732,hi:=4733);
Read_Real(rVar:=PMM[2].Phase[3].Current[30],lo:=4734,hi:=4735);
Read_Real(rVar:=PMM[2].Phase[3].Current[31],lo:=4736,hi:=4737);
Read_Real(rVar:=PMM[2].Phase[3].Current[32],lo:=4738,hi:=4739);
Read_Real(rVar:=PMM[2].Phase[3].Current[33],lo:=4740,hi:=4741);
Read_Real(rVar:=PMM[2].Phase[3].Current[34],lo:=4742,hi:=4743);
Read_Real(rVar:=PMM[2].Phase[3].Current[35],lo:=4744,hi:=4745);
Read_Real(rVar:=PMM[2].Phase[3].Current[36],lo:=4746,hi:=4747);
Read_Real(rVar:=PMM[2].Phase[3].Current[37],lo:=4748,hi:=4749);
Read_Real(rVar:=PMM[2].Phase[3].Current[38],lo:=4750,hi:=4751);
Read_Real(rVar:=PMM[2].Phase[3].Current[39],lo:=4752,hi:=4753);
Read_Real(rVar:=PMM[2].Phase[3].Current[3],lo:=4754,hi:=4755);
Read_Real(rVar:=PMM[2].Phase[3].Current[40],lo:=4756,hi:=4757);
Read_Real(rVar:=PMM[2].Phase[3].Current[41],lo:=4758,hi:=4759);
Read_Real(rVar:=PMM[2].Phase[3].Current[42],lo:=4760,hi:=4761);
Read_Real(rVar:=PMM[2].Phase[3].Current[4],lo:=4762,hi:=4763);
Read_Real(rVar:=PMM[2].Phase[3].Current[5],lo:=4764,hi:=4765);
Read_Real(rVar:=PMM[2].Phase[3].Current[6],lo:=4766,hi:=4767);
Read_Real(rVar:=PMM[2].Phase[3].Current[7],lo:=4768,hi:=4769);
Read_Real(rVar:=PMM[2].Phase[3].Current[8],lo:=4770,hi:=4771);
Read_Real(rVar:=PMM[2].Phase[3].Current[9],lo:=4772,hi:=4773);
Read_Real(rVar:=PMM[2].PowerFactorPhaseA,lo:=4774,hi:=4775);
Read_Real(rVar:=PMM[2].PowerFactorPhaseB,lo:=4776,hi:=4777);
Read_Real(rVar:=PMM[2].PowerFactorPhaseC,lo:=4778,hi:=4779);
Read_Real(rVar:=PMM[2].TotalActivePower_kW,lo:=4780,hi:=4781);
Read_Real(rVar:=PMM[2].TotalAparentPower_kVA,lo:=4782,hi:=4783);
Read_Real(rVar:=PMM[2].TotalPowerFactor,lo:=4784,hi:=4785);
Read_Real(rVar:=PMM[2].TotalReactivePower_kVAR,lo:=4786,hi:=4787);
Read_Real(rVar:=PMM[2].VoltageBetweenPhaseAB_V,lo:=4788,hi:=4789);
Read_Real(rVar:=PMM[2].VoltageBetweenPhaseAN_V,lo:=4790,hi:=4791);
Read_Real(rVar:=PMM[2].VoltageBetweenPhaseBC_V,lo:=4792,hi:=4793);
Read_Real(rVar:=PMM[2].VoltageBetweenPhaseBN_V,lo:=4794,hi:=4795);
Read_Real(rVar:=PMM[2].VoltageBetweenPhaseCA_V,lo:=4796,hi:=4797);
Read_Real(rVar:=PMM[2].VoltageBetweenPhaseCN_V,lo:=4798,hi:=4799);
Read_Real(rVar:=PMM[3].ActivePowerPhaseA_kW,lo:=4800,hi:=4801);
Read_Real(rVar:=PMM[3].ActivePowerPhaseB_kW,lo:=4802,hi:=4803);
Read_Real(rVar:=PMM[3].ActivePowerPhaseC_kW,lo:=4804,hi:=4805);
Read_Real(rVar:=PMM[3].AverageCurrent_A,lo:=4806,hi:=4807);
Read_Real(rVar:=PMM[3].AveragePhaseToNeutral_V,lo:=4808,hi:=4809);
Read_Real(rVar:=PMM[3].AveragePhaseToPhase_V,lo:=4810,hi:=4811);
Read_Real(rVar:=PMM[3].CurrentInPhaseA_A,lo:=4812,hi:=4813);
Read_Real(rVar:=PMM[3].CurrentInPhaseB_A,lo:=4814,hi:=4815);
Read_Real(rVar:=PMM[3].CurrentInPhaseC_A,lo:=4816,hi:=4817);
Read_Real(rVar:=PMM[3].EnergyConsumed_kWh,lo:=4818,hi:=4819);
Read_Real(rVar:=PMM[3].Frequency_Hz,lo:=4820,hi:=4821);
Read_Real(rVar:=PMM[3].NeutralCurrent_A,lo:=4822,hi:=4823);
Read_Real(rVar:=PMM[3].Phase[1].Current[10],lo:=4824,hi:=4825);
Read_Real(rVar:=PMM[3].Phase[1].Current[11],lo:=4826,hi:=4827);
Read_Real(rVar:=PMM[3].Phase[1].Current[12],lo:=4828,hi:=4829);
Read_Real(rVar:=PMM[3].Phase[1].Current[13],lo:=4830,hi:=4831);
Read_Real(rVar:=PMM[3].Phase[1].Current[14],lo:=4832,hi:=4833);
Read_Real(rVar:=PMM[3].Phase[1].Current[15],lo:=4834,hi:=4835);
Read_Real(rVar:=PMM[3].Phase[1].Current[16],lo:=4836,hi:=4837);
Read_Real(rVar:=PMM[3].Phase[1].Current[17],lo:=4838,hi:=4839);
Read_Real(rVar:=PMM[3].Phase[1].Current[18],lo:=4840,hi:=4841);
Read_Real(rVar:=PMM[3].Phase[1].Current[19],lo:=4842,hi:=4843);
Read_Real(rVar:=PMM[3].Phase[1].Current[1],lo:=4844,hi:=4845);
Read_Real(rVar:=PMM[3].Phase[1].Current[20],lo:=4846,hi:=4847);
Read_Real(rVar:=PMM[3].Phase[1].Current[21],lo:=4848,hi:=4849);
Read_Real(rVar:=PMM[3].Phase[1].Current[22],lo:=4850,hi:=4851);
Read_Real(rVar:=PMM[3].Phase[1].Current[23],lo:=4852,hi:=4853);
Read_Real(rVar:=PMM[3].Phase[1].Current[24],lo:=4854,hi:=4855);
Read_Real(rVar:=PMM[3].Phase[1].Current[25],lo:=4856,hi:=4857);
Read_Real(rVar:=PMM[3].Phase[1].Current[26],lo:=4858,hi:=4859);
Read_Real(rVar:=PMM[3].Phase[1].Current[27],lo:=4860,hi:=4861);
Read_Real(rVar:=PMM[3].Phase[1].Current[28],lo:=4862,hi:=4863);
Read_Real(rVar:=PMM[3].Phase[1].Current[29],lo:=4864,hi:=4865);
Read_Real(rVar:=PMM[3].Phase[1].Current[2],lo:=4866,hi:=4867);
Read_Real(rVar:=PMM[3].Phase[1].Current[30],lo:=4868,hi:=4869);
Read_Real(rVar:=PMM[3].Phase[1].Current[31],lo:=4870,hi:=4871);
Read_Real(rVar:=PMM[3].Phase[1].Current[32],lo:=4872,hi:=4873);
Read_Real(rVar:=PMM[3].Phase[1].Current[33],lo:=4874,hi:=4875);
Read_Real(rVar:=PMM[3].Phase[1].Current[34],lo:=4876,hi:=4877);
Read_Real(rVar:=PMM[3].Phase[1].Current[35],lo:=4878,hi:=4879);
Read_Real(rVar:=PMM[3].Phase[1].Current[36],lo:=4880,hi:=4881);
Read_Real(rVar:=PMM[3].Phase[1].Current[37],lo:=4882,hi:=4883);
Read_Real(rVar:=PMM[3].Phase[1].Current[38],lo:=4884,hi:=4885);
Read_Real(rVar:=PMM[3].Phase[1].Current[39],lo:=4886,hi:=4887);
Read_Real(rVar:=PMM[3].Phase[1].Current[3],lo:=4888,hi:=4889);
Read_Real(rVar:=PMM[3].Phase[1].Current[40],lo:=4890,hi:=4891);
Read_Real(rVar:=PMM[3].Phase[1].Current[41],lo:=4892,hi:=4893);
Read_Real(rVar:=PMM[3].Phase[1].Current[42],lo:=4894,hi:=4895);
Read_Real(rVar:=PMM[3].Phase[1].Current[4],lo:=4896,hi:=4897);
Read_Real(rVar:=PMM[3].Phase[1].Current[5],lo:=4898,hi:=4899);
Read_Real(rVar:=PMM[3].Phase[1].Current[6],lo:=4900,hi:=4901);
Read_Real(rVar:=PMM[3].Phase[1].Current[7],lo:=4902,hi:=4903);
Read_Real(rVar:=PMM[3].Phase[1].Current[8],lo:=4904,hi:=4905);
Read_Real(rVar:=PMM[3].Phase[1].Current[9],lo:=4906,hi:=4907);
Read_Real(rVar:=PMM[3].Phase[2].Current[10],lo:=4908,hi:=4909);
Read_Real(rVar:=PMM[3].Phase[2].Current[11],lo:=4910,hi:=4911);
Read_Real(rVar:=PMM[3].Phase[2].Current[12],lo:=4912,hi:=4913);
Read_Real(rVar:=PMM[3].Phase[2].Current[13],lo:=4914,hi:=4915);
Read_Real(rVar:=PMM[3].Phase[2].Current[14],lo:=4916,hi:=4917);
Read_Real(rVar:=PMM[3].Phase[2].Current[15],lo:=4918,hi:=4919);
Read_Real(rVar:=PMM[3].Phase[2].Current[16],lo:=4920,hi:=4921);
Read_Real(rVar:=PMM[3].Phase[2].Current[17],lo:=4922,hi:=4923);
Read_Real(rVar:=PMM[3].Phase[2].Current[18],lo:=4924,hi:=4925);
Read_Real(rVar:=PMM[3].Phase[2].Current[19],lo:=4926,hi:=4927);
Read_Real(rVar:=PMM[3].Phase[2].Current[1],lo:=4928,hi:=4929);
Read_Real(rVar:=PMM[3].Phase[2].Current[20],lo:=4930,hi:=4931);
Read_Real(rVar:=PMM[3].Phase[2].Current[21],lo:=4932,hi:=4933);
Read_Real(rVar:=PMM[3].Phase[2].Current[22],lo:=4934,hi:=4935);
Read_Real(rVar:=PMM[3].Phase[2].Current[23],lo:=4936,hi:=4937);
Read_Real(rVar:=PMM[3].Phase[2].Current[24],lo:=4938,hi:=4939);
Read_Real(rVar:=PMM[3].Phase[2].Current[25],lo:=4940,hi:=4941);
Read_Real(rVar:=PMM[3].Phase[2].Current[26],lo:=4942,hi:=4943);
Read_Real(rVar:=PMM[3].Phase[2].Current[27],lo:=4944,hi:=4945);
Read_Real(rVar:=PMM[3].Phase[2].Current[28],lo:=4946,hi:=4947);
Read_Real(rVar:=PMM[3].Phase[2].Current[29],lo:=4948,hi:=4949);
Read_Real(rVar:=PMM[3].Phase[2].Current[2],lo:=4950,hi:=4951);
Read_Real(rVar:=PMM[3].Phase[2].Current[30],lo:=4952,hi:=4953);
Read_Real(rVar:=PMM[3].Phase[2].Current[31],lo:=4954,hi:=4955);
Read_Real(rVar:=PMM[3].Phase[2].Current[32],lo:=4956,hi:=4957);
Read_Real(rVar:=PMM[3].Phase[2].Current[33],lo:=4958,hi:=4959);
Read_Real(rVar:=PMM[3].Phase[2].Current[34],lo:=4960,hi:=4961);
Read_Real(rVar:=PMM[3].Phase[2].Current[35],lo:=4962,hi:=4963);
Read_Real(rVar:=PMM[3].Phase[2].Current[36],lo:=4964,hi:=4965);
Read_Real(rVar:=PMM[3].Phase[2].Current[37],lo:=4966,hi:=4967);
Read_Real(rVar:=PMM[3].Phase[2].Current[38],lo:=4968,hi:=4969);
Read_Real(rVar:=PMM[3].Phase[2].Current[39],lo:=4970,hi:=4971);
Read_Real(rVar:=PMM[3].Phase[2].Current[3],lo:=4972,hi:=4973);
Read_Real(rVar:=PMM[3].Phase[2].Current[40],lo:=4974,hi:=4975);
Read_Real(rVar:=PMM[3].Phase[2].Current[41],lo:=4976,hi:=4977);
Read_Real(rVar:=PMM[3].Phase[2].Current[42],lo:=4978,hi:=4979);
Read_Real(rVar:=PMM[3].Phase[2].Current[4],lo:=4980,hi:=4981);
Read_Real(rVar:=PMM[3].Phase[2].Current[5],lo:=4982,hi:=4983);
Read_Real(rVar:=PMM[3].Phase[2].Current[6],lo:=4984,hi:=4985);
Read_Real(rVar:=PMM[3].Phase[2].Current[7],lo:=4986,hi:=4987);
Read_Real(rVar:=PMM[3].Phase[2].Current[8],lo:=4988,hi:=4989);
Read_Real(rVar:=PMM[3].Phase[2].Current[9],lo:=4990,hi:=4991);
Read_Real(rVar:=PMM[3].Phase[3].Current[10],lo:=4992,hi:=4993);
Read_Real(rVar:=PMM[3].Phase[3].Current[11],lo:=4994,hi:=4995);
Read_Real(rVar:=PMM[3].Phase[3].Current[12],lo:=4996,hi:=4997);
Read_Real(rVar:=PMM[3].Phase[3].Current[13],lo:=4998,hi:=4999);
Read_Real(rVar:=PMM[3].Phase[3].Current[14],lo:=5000,hi:=5001);
Read_Real(rVar:=PMM[3].Phase[3].Current[15],lo:=5002,hi:=5003);
Read_Real(rVar:=PMM[3].Phase[3].Current[16],lo:=5004,hi:=5005);
Read_Real(rVar:=PMM[3].Phase[3].Current[17],lo:=5006,hi:=5007);
Read_Real(rVar:=PMM[3].Phase[3].Current[18],lo:=5008,hi:=5009);
Read_Real(rVar:=PMM[3].Phase[3].Current[19],lo:=5010,hi:=5011);
Read_Real(rVar:=PMM[3].Phase[3].Current[1],lo:=5012,hi:=5013);
Read_Real(rVar:=PMM[3].Phase[3].Current[20],lo:=5014,hi:=5015);
Read_Real(rVar:=PMM[3].Phase[3].Current[21],lo:=5016,hi:=5017);
Read_Real(rVar:=PMM[3].Phase[3].Current[22],lo:=5018,hi:=5019);
Read_Real(rVar:=PMM[3].Phase[3].Current[23],lo:=5020,hi:=5021);
Read_Real(rVar:=PMM[3].Phase[3].Current[24],lo:=5022,hi:=5023);
Read_Real(rVar:=PMM[3].Phase[3].Current[25],lo:=5024,hi:=5025);
Read_Real(rVar:=PMM[3].Phase[3].Current[26],lo:=5026,hi:=5027);
Read_Real(rVar:=PMM[3].Phase[3].Current[27],lo:=5028,hi:=5029);
Read_Real(rVar:=PMM[3].Phase[3].Current[28],lo:=5030,hi:=5031);
Read_Real(rVar:=PMM[3].Phase[3].Current[29],lo:=5032,hi:=5033);
Read_Real(rVar:=PMM[3].Phase[3].Current[2],lo:=5034,hi:=5035);
Read_Real(rVar:=PMM[3].Phase[3].Current[30],lo:=5036,hi:=5037);
Read_Real(rVar:=PMM[3].Phase[3].Current[31],lo:=5038,hi:=5039);
Read_Real(rVar:=PMM[3].Phase[3].Current[32],lo:=5040,hi:=5041);
Read_Real(rVar:=PMM[3].Phase[3].Current[33],lo:=5042,hi:=5043);
Read_Real(rVar:=PMM[3].Phase[3].Current[34],lo:=5044,hi:=5045);
Read_Real(rVar:=PMM[3].Phase[3].Current[35],lo:=5046,hi:=5047);
Read_Real(rVar:=PMM[3].Phase[3].Current[36],lo:=5048,hi:=5049);
Read_Real(rVar:=PMM[3].Phase[3].Current[37],lo:=5050,hi:=5051);
Read_Real(rVar:=PMM[3].Phase[3].Current[38],lo:=5052,hi:=5053);
Read_Real(rVar:=PMM[3].Phase[3].Current[39],lo:=5054,hi:=5055);
Read_Real(rVar:=PMM[3].Phase[3].Current[3],lo:=5056,hi:=5057);
Read_Real(rVar:=PMM[3].Phase[3].Current[40],lo:=5058,hi:=5059);
Read_Real(rVar:=PMM[3].Phase[3].Current[41],lo:=5060,hi:=5061);
Read_Real(rVar:=PMM[3].Phase[3].Current[42],lo:=5062,hi:=5063);
Read_Real(rVar:=PMM[3].Phase[3].Current[4],lo:=5064,hi:=5065);
Read_Real(rVar:=PMM[3].Phase[3].Current[5],lo:=5066,hi:=5067);
Read_Real(rVar:=PMM[3].Phase[3].Current[6],lo:=5068,hi:=5069);
Read_Real(rVar:=PMM[3].Phase[3].Current[7],lo:=5070,hi:=5071);
Read_Real(rVar:=PMM[3].Phase[3].Current[8],lo:=5072,hi:=5073);
Read_Real(rVar:=PMM[3].Phase[3].Current[9],lo:=5074,hi:=5075);
Read_Real(rVar:=PMM[3].PowerFactorPhaseA,lo:=5076,hi:=5077);
Read_Real(rVar:=PMM[3].PowerFactorPhaseB,lo:=5078,hi:=5079);
Read_Real(rVar:=PMM[3].PowerFactorPhaseC,lo:=5080,hi:=5081);
Read_Real(rVar:=PMM[3].TotalActivePower_kW,lo:=5082,hi:=5083);
Read_Real(rVar:=PMM[3].TotalAparentPower_kVA,lo:=5084,hi:=5085);
Read_Real(rVar:=PMM[3].TotalPowerFactor,lo:=5086,hi:=5087);
Read_Real(rVar:=PMM[3].TotalReactivePower_kVAR,lo:=5088,hi:=5089);
Read_Real(rVar:=PMM[3].VoltageBetweenPhaseAB_V,lo:=5090,hi:=5091);
Read_Real(rVar:=PMM[3].VoltageBetweenPhaseAN_V,lo:=5092,hi:=5093);
Read_Real(rVar:=PMM[3].VoltageBetweenPhaseBC_V,lo:=5094,hi:=5095);
Read_Real(rVar:=PMM[3].VoltageBetweenPhaseBN_V,lo:=5096,hi:=5097);
Read_Real(rVar:=PMM[3].VoltageBetweenPhaseCA_V,lo:=5098,hi:=5099);
Read_Real(rVar:=PMM[3].VoltageBetweenPhaseCN_V,lo:=5100,hi:=5101);
Read_Real(rVar:=rVersion,lo:=5102,hi:=5103);
Read_Real(rVar:=SenzorTemp[1],lo:=5104,hi:=5105);
Read_Real(rVar:=SenzorTemp[2],lo:=5106,hi:=5107);
Read_Real(rVar:=SenzorVlaga[1],lo:=5108,hi:=5109);
Read_Real(rVar:=SenzorVlaga[2],lo:=5110,hi:=5111);
Read_Real(rVar:=TempMaxPoint,lo:=5112,hi:=5113);
Read_Real(rVar:=TempSetPoint,lo:=5114,hi:=5115);
Read_Real(rVar:=UPS[1].EstimatedChargeRemaining,lo:=5116,hi:=5117);
Read_Real(rVar:=UPS[1].EstimatedMinutesRemaining,lo:=5118,hi:=5119);
Read_Real(rVar:=UPS[1].IzhodMocL1,lo:=5120,hi:=5121);
Read_Real(rVar:=UPS[1].IzhodMocL2,lo:=5122,hi:=5123);
Read_Real(rVar:=UPS[1].IzhodMocL3,lo:=5124,hi:=5125);
Read_Real(rVar:=UPS[1].NapetostBaterije,lo:=5126,hi:=5127);
Read_Real(rVar:=UPS[1].TemperaturaBaterije,lo:=5128,hi:=5129);
Read_Real(rVar:=UPS[1].VhodFrekvencaL1,lo:=5130,hi:=5131);
Read_Real(rVar:=UPS[1].VhodFrekvencaL2,lo:=5132,hi:=5133);
Read_Real(rVar:=UPS[1].VhodFrekvencaL3,lo:=5134,hi:=5135);
Read_Real(rVar:=UPS[1].VhodNapetostL1,lo:=5136,hi:=5137);
Read_Real(rVar:=UPS[1].VhodNapetostL2,lo:=5138,hi:=5139);
Read_Real(rVar:=UPS[1].VhodNapetostL3,lo:=5140,hi:=5141);
Read_Real(rVar:=UPS[2].EstimatedChargeRemaining,lo:=5142,hi:=5143);
Read_Real(rVar:=UPS[2].EstimatedMinutesRemaining,lo:=5144,hi:=5145);
Read_Real(rVar:=UPS[2].IzhodMocL1,lo:=5146,hi:=5147);
Read_Real(rVar:=UPS[2].IzhodMocL2,lo:=5148,hi:=5149);
Read_Real(rVar:=UPS[2].IzhodMocL3,lo:=5150,hi:=5151);
Read_Real(rVar:=UPS[2].NapetostBaterije,lo:=5152,hi:=5153);
Read_Real(rVar:=UPS[2].TemperaturaBaterije,lo:=5154,hi:=5155);
Read_Real(rVar:=UPS[2].VhodFrekvencaL1,lo:=5156,hi:=5157);
Read_Real(rVar:=UPS[2].VhodFrekvencaL2,lo:=5158,hi:=5159);
Read_Real(rVar:=UPS[2].VhodFrekvencaL3,lo:=5160,hi:=5161);
Read_Real(rVar:=UPS[2].VhodNapetostL1,lo:=5162,hi:=5163);
Read_Real(rVar:=UPS[2].VhodNapetostL2,lo:=5164,hi:=5165);
Read_Real(rVar:=UPS[2].VhodNapetostL3,lo:=5166,hi:=5167);
Read_Real(rVar:=KlimaGal.NastMaxTemp,lo:=5168,hi:=5169);
Read_Real(rVar:=KlimaGal.NastMaxVlaznost,lo:=5170,hi:=5171);
Read_Real(rVar:=KlimaGal.NastMinTemp,lo:=5172,hi:=5173);
Read_Real(rVar:=KlimaGal.NastMinVlaznost,lo:=5174,hi:=5175);
Read_Real(rVar:=KlimaGal.NastTempProstora,lo:=5176,hi:=5177);
Read_Real(rVar:=KlimaGal.NastVlaznost,lo:=5178,hi:=5179);
Read_Real(rVar:=KlimaGal.ObratovalneUre,lo:=5180,hi:=5181);
Read_Real(rVar:=KlimaGal.TemperaturaProstora,lo:=5182,hi:=5183);
Read_Real(rVar:=KlimaGal.TempIzpihanegaZraka,lo:=5184,hi:=5185);
Read_Real(rVar:=KlimaGal.TempPovratneVode,lo:=5186,hi:=5187);
Read_Real(rVar:=KlimaGal.VlaznostProstora,lo:=5188,hi:=5189);
Read_Real(rVar:=KlimaGal.ZunanjaTemp,lo:=5190,hi:=5191);
Read_Real(rVar:=PMMfaza01,lo:=5192,hi:=5193);
Read_Real(rVar:=PMMfaza02,lo:=5194,hi:=5195);
Read_Real(rVar:=PMMfaza03,lo:=5196,hi:=5197);
Read_Real(rVar:=PMMfaza04,lo:=5198,hi:=5199);
Read_Real(rVar:=PMMfaza05,lo:=5200,hi:=5201);
Read_Real(rVar:=PMMfaza06,lo:=5202,hi:=5203);
Read_Real(rVar:=PMMfaza07,lo:=5204,hi:=5205);
Read_Real(rVar:=PMMfaza08,lo:=5206,hi:=5207);
Read_Real(rVar:=PMMfaza09,lo:=5208,hi:=5209);
Read_Real(rVar:=PMMfaza10,lo:=5210,hi:=5211);
Read_Real(rVar:=PMMfaza11,lo:=5212,hi:=5213);
Read_Real(rVar:=PMMfaza12,lo:=5214,hi:=5215);
Read_Real(rVar:=PMMfaza13,lo:=5216,hi:=5217);
Read_Real(rVar:=PMMfaza14,lo:=5218,hi:=5219);
Read_Real(rVar:=PMMfaza15,lo:=5220,hi:=5221);
Read_Real(rVar:=PMMfaza16,lo:=5222,hi:=5223);
Read_Real(rVar:=PMMfaza17,lo:=5224,hi:=5225);
Read_Real(rVar:=PMMfaza18,lo:=5226,hi:=5227);
Read_Real(rVar:=PMMfaza19,lo:=5228,hi:=5229);
Read_Real(rVar:=PMMfaza20,lo:=5230,hi:=5231);
Read_Real(rVar:=PMMfaza21,lo:=5232,hi:=5233);
Read_Real(rVar:=PMMfaza22,lo:=5234,hi:=5235);
Read_Real(rVar:=PMMfaza23,lo:=5236,hi:=5237);
Read_Real(rVar:=PMMfaza24,lo:=5238,hi:=5239);
Read_Real(rVar:=PMMfaza25,lo:=5240,hi:=5241);
Read_Real(rVar:=PMMfaza26,lo:=5242,hi:=5243);
Read_Real(rVar:=PMMfaza27,lo:=5244,hi:=5245);
Read_Real(rVar:=PMMfaza28,lo:=5246,hi:=5247);
Read_Real(rVar:=PMMfaza29,lo:=5248,hi:=5249);
Read_Real(rVar:=PMMfaza30,lo:=5250,hi:=5251);
Read_Real(rVar:=PMMfaza31,lo:=5252,hi:=5253);
Read_Real(rVar:=PMMfaza32,lo:=5254,hi:=5255);
Read_Real(rVar:=PMMfaza33,lo:=5256,hi:=5257);
Read_Real(rVar:=PMMfaza34,lo:=5258,hi:=5259);
Read_Real(rVar:=PMMfaza35,lo:=5260,hi:=5261);
Read_Real(rVar:=PMMfaza36,lo:=5262,hi:=5263);
Read_Real(rVar:=PMMfaza37,lo:=5264,hi:=5265);
Read_Real(rVar:=PMMfaza38,lo:=5266,hi:=5267);
Read_Real(rVar:=PMMfaza39,lo:=5268,hi:=5269);
Read_Real(rVar:=PMMfaza40,lo:=5270,hi:=5271);
Read_Real(rVar:=PMMfaza41,lo:=5272,hi:=5273);
Read_Real(rVar:=PMMfaza42,lo:=5274,hi:=5275);
Read_Real(rVar:=PMMfaza60[10],lo:=5276,hi:=5277);
Read_Real(rVar:=PMMfaza60[11],lo:=5278,hi:=5279);
Read_Real(rVar:=PMMfaza60[12],lo:=5280,hi:=5281);
Read_Real(rVar:=PMMfaza60[13],lo:=5282,hi:=5283);
Read_Real(rVar:=PMMfaza60[14],lo:=5284,hi:=5285);
Read_Real(rVar:=PMMfaza60[15],lo:=5286,hi:=5287);
Read_Real(rVar:=PMMfaza60[16],lo:=5288,hi:=5289);
Read_Real(rVar:=PMMfaza60[17],lo:=5290,hi:=5291);
Read_Real(rVar:=PMMfaza60[18],lo:=5292,hi:=5293);
Read_Real(rVar:=PMMfaza60[19],lo:=5294,hi:=5295);
Read_Real(rVar:=PMMfaza60[1],lo:=5296,hi:=5297);
Read_Real(rVar:=PMMfaza60[20],lo:=5298,hi:=5299);
Read_Real(rVar:=PMMfaza60[21],lo:=5300,hi:=5301);
Read_Real(rVar:=PMMfaza60[22],lo:=5302,hi:=5303);
Read_Real(rVar:=PMMfaza60[23],lo:=5304,hi:=5305);
Read_Real(rVar:=PMMfaza60[24],lo:=5306,hi:=5307);
Read_Real(rVar:=PMMfaza60[25],lo:=5308,hi:=5309);
Read_Real(rVar:=PMMfaza60[26],lo:=5310,hi:=5311);
Read_Real(rVar:=PMMfaza60[27],lo:=5312,hi:=5313);
Read_Real(rVar:=PMMfaza60[28],lo:=5314,hi:=5315);
Read_Real(rVar:=PMMfaza60[29],lo:=5316,hi:=5317);
Read_Real(rVar:=PMMfaza60[2],lo:=5318,hi:=5319);
Read_Real(rVar:=PMMfaza60[30],lo:=5320,hi:=5321);
Read_Real(rVar:=PMMfaza60[31],lo:=5322,hi:=5323);
Read_Real(rVar:=PMMfaza60[32],lo:=5324,hi:=5325);
Read_Real(rVar:=PMMfaza60[33],lo:=5326,hi:=5327);
Read_Real(rVar:=PMMfaza60[34],lo:=5328,hi:=5329);
Read_Real(rVar:=PMMfaza60[35],lo:=5330,hi:=5331);
Read_Real(rVar:=PMMfaza60[36],lo:=5332,hi:=5333);
Read_Real(rVar:=PMMfaza60[37],lo:=5334,hi:=5335);
Read_Real(rVar:=PMMfaza60[38],lo:=5336,hi:=5337);
Read_Real(rVar:=PMMfaza60[39],lo:=5338,hi:=5339);
Read_Real(rVar:=PMMfaza60[3],lo:=5340,hi:=5341);
Read_Real(rVar:=PMMfaza60[40],lo:=5342,hi:=5343);
Read_Real(rVar:=PMMfaza60[41],lo:=5344,hi:=5345);
Read_Real(rVar:=PMMfaza60[42],lo:=5346,hi:=5347);
Read_Real(rVar:=PMMfaza60[4],lo:=5348,hi:=5349);
Read_Real(rVar:=PMMfaza60[5],lo:=5350,hi:=5351);
Read_Real(rVar:=PMMfaza60[6],lo:=5352,hi:=5353);
Read_Real(rVar:=PMMfaza60[7],lo:=5354,hi:=5355);
Read_Real(rVar:=PMMfaza60[8],lo:=5356,hi:=5357);
Read_Real(rVar:=PMMfaza60[9],lo:=5358,hi:=5359);
Read_Real(rVar:=PMMfaza80[10],lo:=5360,hi:=5361);
Read_Real(rVar:=PMMfaza80[11],lo:=5362,hi:=5363);
Read_Real(rVar:=PMMfaza80[12],lo:=5364,hi:=5365);
Read_Real(rVar:=PMMfaza80[13],lo:=5366,hi:=5367);
Read_Real(rVar:=PMMfaza80[14],lo:=5368,hi:=5369);
Read_Real(rVar:=PMMfaza80[15],lo:=5370,hi:=5371);
Read_Real(rVar:=PMMfaza80[16],lo:=5372,hi:=5373);
Read_Real(rVar:=PMMfaza80[17],lo:=5374,hi:=5375);
Read_Real(rVar:=PMMfaza80[18],lo:=5376,hi:=5377);
Read_Real(rVar:=PMMfaza80[19],lo:=5378,hi:=5379);
Read_Real(rVar:=PMMfaza80[1],lo:=5380,hi:=5381);
Read_Real(rVar:=PMMfaza80[20],lo:=5382,hi:=5383);
Read_Real(rVar:=PMMfaza80[21],lo:=5384,hi:=5385);
Read_Real(rVar:=PMMfaza80[22],lo:=5386,hi:=5387);
Read_Real(rVar:=PMMfaza80[23],lo:=5388,hi:=5389);
Read_Real(rVar:=PMMfaza80[24],lo:=5390,hi:=5391);
Read_Real(rVar:=PMMfaza80[25],lo:=5392,hi:=5393);
Read_Real(rVar:=PMMfaza80[26],lo:=5394,hi:=5395);
Read_Real(rVar:=PMMfaza80[27],lo:=5396,hi:=5397);
Read_Real(rVar:=PMMfaza80[28],lo:=5398,hi:=5399);
Read_Real(rVar:=PMMfaza80[29],lo:=5400,hi:=5401);
Read_Real(rVar:=PMMfaza80[2],lo:=5402,hi:=5403);
Read_Real(rVar:=PMMfaza80[30],lo:=5404,hi:=5405);
Read_Real(rVar:=PMMfaza80[31],lo:=5406,hi:=5407);
Read_Real(rVar:=PMMfaza80[32],lo:=5408,hi:=5409);
Read_Real(rVar:=PMMfaza80[33],lo:=5410,hi:=5411);
Read_Real(rVar:=PMMfaza80[34],lo:=5412,hi:=5413);
Read_Real(rVar:=PMMfaza80[35],lo:=5414,hi:=5415);
Read_Real(rVar:=PMMfaza80[36],lo:=5416,hi:=5417);
Read_Real(rVar:=PMMfaza80[37],lo:=5418,hi:=5419);
Read_Real(rVar:=PMMfaza80[38],lo:=5420,hi:=5421);
Read_Real(rVar:=PMMfaza80[39],lo:=5422,hi:=5423);
Read_Real(rVar:=PMMfaza80[3],lo:=5424,hi:=5425);
Read_Real(rVar:=PMMfaza80[40],lo:=5426,hi:=5427);
Read_Real(rVar:=PMMfaza80[41],lo:=5428,hi:=5429);
Read_Real(rVar:=PMMfaza80[42],lo:=5430,hi:=5431);
Read_Real(rVar:=PMMfaza80[4],lo:=5432,hi:=5433);
Read_Real(rVar:=PMMfaza80[5],lo:=5434,hi:=5435);
Read_Real(rVar:=PMMfaza80[6],lo:=5436,hi:=5437);
Read_Real(rVar:=PMMfaza80[7],lo:=5438,hi:=5439);
Read_Real(rVar:=PMMfaza80[8],lo:=5440,hi:=5441);
Read_Real(rVar:=PMMfaza80[9],lo:=5442,hi:=5443);
Read_Real(rVar:=PMMgal.ActivePowerPhaseA_kW,lo:=5444,hi:=5445);
Read_Real(rVar:=PMMgal.ActivePowerPhaseB_kW,lo:=5446,hi:=5447);
Read_Real(rVar:=PMMgal.ActivePowerPhaseC_kW,lo:=5448,hi:=5449);
Read_Real(rVar:=PMMgal.AverageCurrent_A,lo:=5450,hi:=5451);
Read_Real(rVar:=PMMgal.AveragePhaseToNeutral_V,lo:=5452,hi:=5453);
Read_Real(rVar:=PMMgal.AveragePhaseToPhase_V,lo:=5454,hi:=5455);
Read_Real(rVar:=PMMgal.CurrentInPhaseA_A,lo:=5456,hi:=5457);
Read_Real(rVar:=PMMgal.CurrentInPhaseB_A,lo:=5458,hi:=5459);
Read_Real(rVar:=PMMgal.CurrentInPhaseC_A,lo:=5460,hi:=5461);
Read_Real(rVar:=PMMgal.EnergyConsumed_kWh,lo:=5462,hi:=5463);
Read_Real(rVar:=PMMgal.Frequency_Hz,lo:=5464,hi:=5465);
Read_Real(rVar:=PMMgal.NeutralCurrent_A,lo:=5466,hi:=5467);
Read_Real(rVar:=PMMgal.Phase[1].Current[10],lo:=5468,hi:=5469);
Read_Real(rVar:=PMMgal.Phase[1].Current[11],lo:=5470,hi:=5471);
Read_Real(rVar:=PMMgal.Phase[1].Current[12],lo:=5472,hi:=5473);
Read_Real(rVar:=PMMgal.Phase[1].Current[13],lo:=5474,hi:=5475);
Read_Real(rVar:=PMMgal.Phase[1].Current[14],lo:=5476,hi:=5477);
Read_Real(rVar:=PMMgal.Phase[1].Current[15],lo:=5478,hi:=5479);
Read_Real(rVar:=PMMgal.Phase[1].Current[16],lo:=5480,hi:=5481);
Read_Real(rVar:=PMMgal.Phase[1].Current[17],lo:=5482,hi:=5483);
Read_Real(rVar:=PMMgal.Phase[1].Current[18],lo:=5484,hi:=5485);
Read_Real(rVar:=PMMgal.Phase[1].Current[19],lo:=5486,hi:=5487);
Read_Real(rVar:=PMMgal.Phase[1].Current[1],lo:=5488,hi:=5489);
Read_Real(rVar:=PMMgal.Phase[1].Current[20],lo:=5490,hi:=5491);
Read_Real(rVar:=PMMgal.Phase[1].Current[21],lo:=5492,hi:=5493);
Read_Real(rVar:=PMMgal.Phase[1].Current[22],lo:=5494,hi:=5495);
Read_Real(rVar:=PMMgal.Phase[1].Current[23],lo:=5496,hi:=5497);
Read_Real(rVar:=PMMgal.Phase[1].Current[24],lo:=5498,hi:=5499);
Read_Real(rVar:=PMMgal.Phase[1].Current[25],lo:=5500,hi:=5501);
Read_Real(rVar:=PMMgal.Phase[1].Current[26],lo:=5502,hi:=5503);
Read_Real(rVar:=PMMgal.Phase[1].Current[27],lo:=5504,hi:=5505);
Read_Real(rVar:=PMMgal.Phase[1].Current[28],lo:=5506,hi:=5507);
Read_Real(rVar:=PMMgal.Phase[1].Current[29],lo:=5508,hi:=5509);
Read_Real(rVar:=PMMgal.Phase[1].Current[2],lo:=5510,hi:=5511);
Read_Real(rVar:=PMMgal.Phase[1].Current[30],lo:=5512,hi:=5513);
Read_Real(rVar:=PMMgal.Phase[1].Current[31],lo:=5514,hi:=5515);
Read_Real(rVar:=PMMgal.Phase[1].Current[32],lo:=5516,hi:=5517);
Read_Real(rVar:=PMMgal.Phase[1].Current[33],lo:=5518,hi:=5519);
Read_Real(rVar:=PMMgal.Phase[1].Current[34],lo:=5520,hi:=5521);
Read_Real(rVar:=PMMgal.Phase[1].Current[35],lo:=5522,hi:=5523);
Read_Real(rVar:=PMMgal.Phase[1].Current[36],lo:=5524,hi:=5525);
Read_Real(rVar:=PMMgal.Phase[1].Current[37],lo:=5526,hi:=5527);
Read_Real(rVar:=PMMgal.Phase[1].Current[38],lo:=5528,hi:=5529);
Read_Real(rVar:=PMMgal.Phase[1].Current[39],lo:=5530,hi:=5531);
Read_Real(rVar:=PMMgal.Phase[1].Current[3],lo:=5532,hi:=5533);
Read_Real(rVar:=PMMgal.Phase[1].Current[40],lo:=5534,hi:=5535);
Read_Real(rVar:=PMMgal.Phase[1].Current[41],lo:=5536,hi:=5537);
Read_Real(rVar:=PMMgal.Phase[1].Current[42],lo:=5538,hi:=5539);
Read_Real(rVar:=PMMgal.Phase[1].Current[4],lo:=5540,hi:=5541);
Read_Real(rVar:=PMMgal.Phase[1].Current[5],lo:=5542,hi:=5543);
Read_Real(rVar:=PMMgal.Phase[1].Current[6],lo:=5544,hi:=5545);
Read_Real(rVar:=PMMgal.Phase[1].Current[7],lo:=5546,hi:=5547);
Read_Real(rVar:=PMMgal.Phase[1].Current[8],lo:=5548,hi:=5549);
Read_Real(rVar:=PMMgal.Phase[1].Current[9],lo:=5550,hi:=5551);
Read_Real(rVar:=PMMgal.Phase[2].Current[10],lo:=5552,hi:=5553);
Read_Real(rVar:=PMMgal.Phase[2].Current[11],lo:=5554,hi:=5555);
Read_Real(rVar:=PMMgal.Phase[2].Current[12],lo:=5556,hi:=5557);
Read_Real(rVar:=PMMgal.Phase[2].Current[13],lo:=5558,hi:=5559);
Read_Real(rVar:=PMMgal.Phase[2].Current[14],lo:=5560,hi:=5561);
Read_Real(rVar:=PMMgal.Phase[2].Current[15],lo:=5562,hi:=5563);
Read_Real(rVar:=PMMgal.Phase[2].Current[16],lo:=5564,hi:=5565);
Read_Real(rVar:=PMMgal.Phase[2].Current[17],lo:=5566,hi:=5567);
Read_Real(rVar:=PMMgal.Phase[2].Current[18],lo:=5568,hi:=5569);
Read_Real(rVar:=PMMgal.Phase[2].Current[19],lo:=5570,hi:=5571);
Read_Real(rVar:=PMMgal.Phase[2].Current[1],lo:=5572,hi:=5573);
Read_Real(rVar:=PMMgal.Phase[2].Current[20],lo:=5574,hi:=5575);
Read_Real(rVar:=PMMgal.Phase[2].Current[21],lo:=5576,hi:=5577);
Read_Real(rVar:=PMMgal.Phase[2].Current[22],lo:=5578,hi:=5579);
Read_Real(rVar:=PMMgal.Phase[2].Current[23],lo:=5580,hi:=5581);
Read_Real(rVar:=PMMgal.Phase[2].Current[24],lo:=5582,hi:=5583);
Read_Real(rVar:=TempAlarmPoint,lo:=5584,hi:=5585);
Read_Real(rVar:=RazlikaUr,lo:=5586,hi:=5587);
Read_Real(rVar:=Circ[1].MaximumDemandA2,lo:=5588,hi:=5589);
Read_Real(rVar:=Circ[1].MaximumDemandA3,lo:=5590,hi:=5591);
Read_Real(rVar:=Circ[1].RazEner_D_SCADA,lo:=5592,hi:=5593);
Read_Real(rVar:=Circ[1].RazEner_T_SCADA,lo:=5594,hi:=5595);
Read_Real(rVar:=Circ[1].RazEner_M_SCADA,lo:=5596,hi:=5597);
(*Branje STRING*)
(**)
Read_String(sVar:=UserCurrentName,start:=7000);
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Bool : BOOL
VAR_INPUT
index: INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje BOOL*)
(**)
0:AlarmGenCirc1:=Bit_0;
1:AlarmGenComm:=Bit_0;
2:AlarmGenDI:=Bit_0;
3:AlarmGenKlima5:=Bit_0;
4:AlarmGenKlima6:=Bit_0;
5:AlarmGenPMM1:=Bit_0;
6:AlarmGenPMM2:=Bit_0;
7:AlarmGenPMM3:=Bit_0;
8:AlarmGenUPS1:=Bit_0;
9:AlarmGenUPS2:=Bit_0;
10:ComSCADA:=Bit_0;
11:ComSCADA1:=Bit_0;
12:DI_Klima5_ERR:=Bit_0;
13:DI_Klima5_ON:=Bit_0;
14:DI_Klima6_ERR:=Bit_0;
15:DI_Klima6_ON:=Bit_0;
16:DI_KlimaSplit1_ERR:=Bit_0;
17:DI_KlimaSplit1_ON:=Bit_0;
18:DI_Q10_OdcKlima6_IZP:=Bit_0;
19:DI_Q10_OdcKlima6_ON:=Bit_0;
20:DI_Q11_OdcVent1_ON:=Bit_0;
21:DI_Q12_Rezerva_ON:=Bit_0;
22:DI_Q1_GlavnoStikalo_ON:=Bit_0;
23:DI_Q25_OdcUpsA_IZP:=Bit_0;
24:DI_Q25_OdcUpsA_ON:=Bit_0;
25:DI_Q26_OdcByA_IZP:=Bit_0;
26:DI_Q26_OdcByA_ON:=Bit_0;
27:DI_Q27_OdcByUpsA_IZP:=Bit_0;
28:DI_Q27_OdcByUpsA_ON:=Bit_0;
29:DI_Q28_OdcUpsB_IZP:=Bit_0;
30:DI_Q28_OdcUpsB_ON:=Bit_0;
31:DI_Q29_OdcByB_IZP:=Bit_0;
32:DI_Q29_OdcByB_ON:=Bit_0;
33:DI_Q2_Rezerva_IZP:=Bit_0;
34:DI_Q2_Rezerva_ON:=Bit_0;
35:DI_Q30_OdcByUpsB_IZP:=Bit_0;
36:DI_Q30_OdcByUpsB_ON:=Bit_0;
37:DI_Q31_DovByUpsA_ON:=Bit_0;
38:DI_Q32_DovByA_ON:=Bit_0;
39:DI_Q33_DovByUpsB_ON:=Bit_0;
40:DI_Q34_DovByB_ON:=Bit_0;
41:DI_Q5_OdcKlima1_IZP:=Bit_0;
42:DI_Q5_OdcKlima1_ON:=Bit_0;
43:DI_Q6_OdcKlima2_IZP:=Bit_0;
44:DI_Q6_OdcKlima2_ON:=Bit_0;
45:DI_Q7_OdcKlima3_IZP:=Bit_0;
46:DI_Q7_OdcKlima3_ON:=Bit_0;
47:DI_Q8_OdcKlima4_IZP:=Bit_0;
48:DI_Q8_OdcKlima4_ON:=Bit_0;
49:DI_Q9_OdcKlima5_IZP:=Bit_0;
50:DI_Q9_OdcKlima5_ON:=Bit_0;
51:DI_RazlitjeVodeK5K6:=Bit_0;
52:DI_UPS_Alarm:=Bit_0;
53:DI_UPS_BatNacin:=Bit_0;
54:DI_UPS_Polnjenje:=Bit_0;
55:DIN_UpsA_ERR:=Bit_0;
56:DIN_UpsA_BypassON:=Bit_0;
57:DIN_UpsB_ERR:=Bit_0;
58:DIN_UpsB_BypassON:=Bit_0;
59:DO_Klima5_Izklop:=Bit_0;
60:DO_Klima6_Izklop:=Bit_0;
61:ErrComCirc[1]:=Bit_0;
62:ErrComCirc[2]:=Bit_0;
63:ErrComCirc[3]:=Bit_0;
64:ErrComCirc[4]:=Bit_0;
65:ErrComCirc[5]:=Bit_0;
66:ErrComKlima[1]:=Bit_0;
67:ErrComKlima[2]:=Bit_0;
68:ErrComKlima[3]:=Bit_0;
69:ErrComKlima[4]:=Bit_0;
70:ErrComKlima[5]:=Bit_0;
71:ErrComKlima[6]:=Bit_0;
72:ErrCommScada:=Bit_0;
73:ErrComPanelPLC:=Bit_0;
74:ErrComPMM[1]:=Bit_0;
75:ErrComPMM[2]:=Bit_0;
76:ErrComPMM[3]:=Bit_0;
77:ErrComPort2:=Bit_0;
78:ErrComPort3:=Bit_0;
79:ErrComPort4:=Bit_0;
80:ErrComUPS[1]:=Bit_0;
81:ErrComUPS[2]:=Bit_0;
82:Klima[1].AlarmKompresor1:=Bit_0;
83:Klima[1].AlarmKompresor2:=Bit_0;
84:Klima[1].Deluje:=Bit_0;
85:Klima[1].EnergySaving:=Bit_0;
86:Klima[1].FaultyEPROM:=Bit_0;
87:Klima[1].FenThermalCutout:=Bit_0;
88:Klima[1].GeneralAlarm:=Bit_0;
89:Klima[1].Kompresor1naMejiObrUr:=Bit_0;
90:Klima[1].Kompresor2naMejiObrUr:=Bit_0;
91:Klima[1].Napaka:=Bit_0;
92:Klima[1].NapakaPriPretokuZraka:=Bit_0;
93:Klima[1].NapakaSenzorPovratVode:=Bit_0;
94:Klima[1].NapakaSenzorTempIzpiha:=Bit_0;
95:Klima[1].NapakaSenzorTempProstora:=Bit_0;
96:Klima[1].NapakaSenzorVlaznosti:=Bit_0;
97:Klima[1].NapakaSenzorZunanjeTemp:=Bit_0;
98:Klima[1].NiTokaVVlazilcu:=Bit_0;
99:Klima[1].NiVodeVVlazilcu:=Bit_0;
100:Klima[1].NizekPritiskKompresor1:=Bit_0;
101:Klima[1].NizekPritiskKompresor2:=Bit_0;
102:Klima[1].NizkaTempPovratneVode:=Bit_0;
103:Klima[1].NizkaTempVProstoru:=Bit_0;
104:Klima[1].NizkaVlaznost:=Bit_0;
105:Klima[1].OnOffEnablingBySupervisor:=Bit_0;
106:Klima[1].PozarniAlarm:=Bit_0;
107:Klima[1].Razvlazevanje:=Bit_0;
108:Klima[1].RemoteOFFtoOutput:=Bit_0;
109:Klima[1].RemoteOnOff:=Bit_0;
110:Klima[1].RocniIzklop:=Bit_0;
111:Klima[1].SenzorjiStatus:=Bit_0;
112:Klima[1].StoppedByAlarms:=Bit_0;
113:Klima[1].ThermalCutoutHeater1:=Bit_0;
114:Klima[1].ThermalCutoutHeater2:=Bit_0;
115:Klima[1].UnitOnOff:=Bit_0;
116:Klima[1].VentilatorNaMejiObrUr:=Bit_0;
117:Klima[1].VentilGretjeOdpiranje:=Bit_0;
118:Klima[1].VentilGretjeZapiranje:=Bit_0;
119:Klima[1].VentilHlajenjeOdpiranje:=Bit_0;
120:Klima[1].VentilHlajenjeZapiranje:=Bit_0;
121:Klima[1].VisokaTempPovratneVode:=Bit_0;
122:Klima[1].VisokaTempVProstoru:=Bit_0;
123:Klima[1].VisokaVlaznost:=Bit_0;
124:Klima[1].VisokTokVVlazilcu:=Bit_0;
125:Klima[1].Vlazenje:=Bit_0;
126:Klima[1].ZamasenFilter:=Bit_0;
127:Klima[2].AlarmKompresor1:=Bit_0;
128:Klima[2].AlarmKompresor2:=Bit_0;
129:Klima[2].Deluje:=Bit_0;
130:Klima[2].EnergySaving:=Bit_0;
131:Klima[2].FaultyEPROM:=Bit_0;
132:Klima[2].FenThermalCutout:=Bit_0;
133:Klima[2].GeneralAlarm:=Bit_0;
134:Klima[2].Kompresor1naMejiObrUr:=Bit_0;
135:Klima[2].Kompresor2naMejiObrUr:=Bit_0;
136:Klima[2].Napaka:=Bit_0;
137:Klima[2].NapakaPriPretokuZraka:=Bit_0;
138:Klima[2].NapakaSenzorPovratVode:=Bit_0;
139:Klima[2].NapakaSenzorTempIzpiha:=Bit_0;
140:Klima[2].NapakaSenzorTempProstora:=Bit_0;
141:Klima[2].NapakaSenzorVlaznosti:=Bit_0;
142:Klima[2].NapakaSenzorZunanjeTemp:=Bit_0;
143:Klima[2].NiTokaVVlazilcu:=Bit_0;
144:Klima[2].NiVodeVVlazilcu:=Bit_0;
145:Klima[2].NizekPritiskKompresor1:=Bit_0;
146:Klima[2].NizekPritiskKompresor2:=Bit_0;
147:Klima[2].NizkaTempPovratneVode:=Bit_0;
148:Klima[2].NizkaTempVProstoru:=Bit_0;
149:Klima[2].NizkaVlaznost:=Bit_0;
150:Klima[2].OnOffEnablingBySupervisor:=Bit_0;
151:Klima[2].PozarniAlarm:=Bit_0;
152:Klima[2].Razvlazevanje:=Bit_0;
153:Klima[2].RemoteOFFtoOutput:=Bit_0;
154:Klima[2].RemoteOnOff:=Bit_0;
155:Klima[2].RocniIzklop:=Bit_0;
156:Klima[2].SenzorjiStatus:=Bit_0;
157:Klima[2].StoppedByAlarms:=Bit_0;
158:Klima[2].ThermalCutoutHeater1:=Bit_0;
159:Klima[2].ThermalCutoutHeater2:=Bit_0;
160:Klima[2].UnitOnOff:=Bit_0;
161:Klima[2].VentilatorNaMejiObrUr:=Bit_0;
162:Klima[2].VentilGretjeOdpiranje:=Bit_0;
163:Klima[2].VentilGretjeZapiranje:=Bit_0;
164:Klima[2].VentilHlajenjeOdpiranje:=Bit_0;
165:Klima[2].VentilHlajenjeZapiranje:=Bit_0;
166:Klima[2].VisokaTempPovratneVode:=Bit_0;
167:Klima[2].VisokaTempVProstoru:=Bit_0;
168:Klima[2].VisokaVlaznost:=Bit_0;
169:Klima[2].VisokTokVVlazilcu:=Bit_0;
170:Klima[2].Vlazenje:=Bit_0;
171:Klima[2].ZamasenFilter:=Bit_0;
172:KlimeNaCas:=Bit_0;
173:NapakaSenzorTemp[1]:=Bit_0;
174:NapakaSenzorTemp[2]:=Bit_0;
175:NapakaSenzorVlaga[1]:=Bit_0;
176:NapakaSenzorVlaga[2]:=Bit_0;
177:PMM1OverCurrentBetw[1]:=Bit_0;
178:PMM1OverCurrentBetw[2]:=Bit_0;
179:PMM1OverCurrentBetw[3]:=Bit_0;
180:PMM1OverCurrentOver[1]:=Bit_0;
181:PMM1OverCurrentOver[2]:=Bit_0;
182:PMM1OverCurrentOver[3]:=Bit_0;
183:PMM2OverCurrentBetw[1]:=Bit_0;
184:PMM2OverCurrentBetw[2]:=Bit_0;
185:PMM2OverCurrentBetw[3]:=Bit_0;
186:PMM2OverCurrentOver[1]:=Bit_0;
187:PMM2OverCurrentOver[2]:=Bit_0;
188:PMM2OverCurrentOver[3]:=Bit_0;
189:PMM3OverCurrentBetw[1]:=Bit_0;
190:PMM3OverCurrentBetw[2]:=Bit_0;
191:PMM3OverCurrentBetw[3]:=Bit_0;
192:PMM3OverCurrentOver[1]:=Bit_0;
193:PMM3OverCurrentOver[2]:=Bit_0;
194:PMM3OverCurrentOver[3]:=Bit_0;
195:PMM[1].Napaka:=Bit_0;
196:PMM[2].Napaka:=Bit_0;
197:PMM[3].Napaka:=Bit_0;
198:SetDateTime:=Bit_0;
199:SetDateTimeDemand:=Bit_0;
200:SetDateTimeError:=Bit_0;
201:SetDateTimeFinished:=Bit_0;
202:SetRemoteOnOff[1]:=Bit_0;
203:SetRemoteOnOff[2]:=Bit_0;
204:SlabaBaterijaPLC_A1:=Bit_0;
205:TempTSprevisoka[1]:=Bit_0;
206:TempTSprevisoka[2]:=Bit_0;
207:UPS[1].AlarmAwaitingPower:=Bit_0;
208:UPS[1].AlarmBypassBad:=Bit_0;
209:UPS[1].AlarmChargerFailed:=Bit_0;
210:UPS[1].AlarmCommunicationsLost:=Bit_0;
211:UPS[1].AlarmDepletedBattery:=Bit_0;
212:UPS[1].AlarmDiagnosticTestFailed:=Bit_0;
213:UPS[1].AlarmIzhodOffKotZahtevano:=Bit_0;
214:UPS[1].AlarmIzhodPreobremenjen:=Bit_0;
215:UPS[1].AlarmLowBattery:=Bit_0;
216:UPS[1].AlarmNapakaNaVarovalki:=Bit_0;
217:UPS[1].AlarmNapakaNaVentilatorju:=Bit_0;
218:UPS[1].AlarmOnBattery:=Bit_0;
219:UPS[1].AlarmOnBypass:=Bit_0;
220:UPS[1].AlarmInverterError:=Bit_0;
221:UPS[1].AlarmShutdownImminent:=Bit_0;
222:UPS[1].AlarmShutdownPending:=Bit_0;
223:UPS[1].AlarmSlabaBaterija:=Bit_0;
224:UPS[1].AlarmSplosnaNapaka:=Bit_0;
225:UPS[1].AlarmStanjeIzhodaIzvenToleranc:=Bit_0;
226:UPS[1].AlarmStanjeVhodaIzvenToleranc:=Bit_0;
227:UPS[1].AlarmTemperaturaIzvenToleranc:=Bit_0;
228:UPS[1].AlarmTestInProgres:=Bit_0;
229:UPS[1].AlarmUPSIzhodOff:=Bit_0;
230:UPS[1].AlarmUPSOffKotZahtevano:=Bit_0;
231:UPS[1].AlarmUPSSystemOff:=Bit_0;
232:UPS[1].Napaka:=Bit_0;
233:UPS[1].StatusEcomodeAktiven:=Bit_0;
234:UPS[1].StatusInverterIsOn:=Bit_0;
235:UPS[1].StatusStopOperation:=Bit_0;
236:UPS[2].AlarmAwaitingPower:=Bit_0;
237:UPS[2].AlarmBypassBad:=Bit_0;
238:UPS[2].AlarmChargerFailed:=Bit_0;
239:UPS[2].AlarmCommunicationsLost:=Bit_0;
240:UPS[2].AlarmDepletedBattery:=Bit_0;
241:UPS[2].AlarmDiagnosticTestFailed:=Bit_0;
242:UPS[2].AlarmIzhodOffKotZahtevano:=Bit_0;
243:UPS[2].AlarmIzhodPreobremenjen:=Bit_0;
244:UPS[2].AlarmLowBattery:=Bit_0;
245:UPS[2].AlarmNapakaNaVarovalki:=Bit_0;
246:UPS[2].AlarmNapakaNaVentilatorju:=Bit_0;
247:UPS[2].AlarmOnBattery:=Bit_0;
248:UPS[2].AlarmOnBypass:=Bit_0;
249:UPS[2].AlarmInverterError:=Bit_0;
250:UPS[2].AlarmShutdownImminent:=Bit_0;
251:UPS[2].AlarmShutdownPending:=Bit_0;
252:UPS[2].AlarmSlabaBaterija:=Bit_0;
253:UPS[2].AlarmSplosnaNapaka:=Bit_0;
254:UPS[2].AlarmStanjeIzhodaIzvenToleranc:=Bit_0;
255:UPS[2].AlarmStanjeVhodaIzvenToleranc:=Bit_0;
256:UPS[2].AlarmTemperaturaIzvenToleranc:=Bit_0;
257:UPS[2].AlarmTestInProgres:=Bit_0;
258:UPS[2].AlarmUPSIzhodOff:=Bit_0;
259:UPS[2].AlarmUPSOffKotZahtevano:=Bit_0;
260:UPS[2].AlarmUPSSystemOff:=Bit_0;
261:UPS[2].Napaka:=Bit_0;
262:UPS[2].StatusEcomodeAktiven:=Bit_0;
263:UPS[2].StatusInverterIsOn:=Bit_0;
264:UPS[2].StatusStopOperation:=Bit_0;
265:UserLoggedIn:=Bit_0;
266:XVH_AlarmOn:=Bit_0;
267:AlarmGenRest:=Bit_0;
268:DI_UpsA_BypassON:=Bit_0;
269:DI_UpsA_ERR:=Bit_0;
270:DI_UpsB_BypassON:=Bit_0;
271:DI_UpsB_ERR:=Bit_0;
272:DIN_Klima5_ERR:=Bit_0;
273:DIN_Klima6_ERR:=Bit_0;
274:DIN_KlimaSplit1_ERR:=Bit_0;
275:DIN_Q10_OdcKlima6_IZP:=Bit_0;
276:DIN_Q25_OdcUpsA_IZP:=Bit_0;
277:DIN_Q26_OdcByA_IZP:=Bit_0;
278:DIN_Q27_OdcByUpsA_IZP:=Bit_0;
279:DIN_Q28_OdcUpsB_IZP:=Bit_0;
280:DIN_Q29_OdcByB_IZP:=Bit_0;
281:DIN_Q2_Rezerva_IZP:=Bit_0;
282:DIN_Q30_OdcByUpsB_IZP:=Bit_0;
283:DIN_Q5_OdcKlima1_IZP:=Bit_0;
284:DIN_Q6_OdcKlima2_IZP:=Bit_0;
285:DIN_Q7_OdcKlima3_IZP:=Bit_0;
286:DIN_Q8_OdcKlima4_IZP:=Bit_0;
287:DIN_Q9_OdcKlima5_IZP:=Bit_0;
288:ErrorComCirc[1].Error:=Bit_0;
289:ErrorComCirc[2].Error:=Bit_0;
290:ErrorComCirc[3].Error:=Bit_0;
291:ErrorComCirc[4].Error:=Bit_0;
292:ErrorComCirc[5].Error:=Bit_0;
293:ErrorComKlima[1].Error:=Bit_0;
294:ErrorComKlima[2].Error:=Bit_0;
295:ErrorComKlima[3].Error:=Bit_0;
296:ErrorComKlima[4].Error:=Bit_0;
297:ErrorComKlima[5].Error:=Bit_0;
298:ErrorComKlima[6].Error:=Bit_0;
299:ErrorComPMM[1].Error:=Bit_0;
300:ErrorComPMM[2].Error:=Bit_0;
301:ErrorComPMM[3].Error:=Bit_0;
302:ErrorComUPS[1].Error:=Bit_0;
303:ErrorComUPS[2].Error:=Bit_0;
304:KlimaAErrors[10]:=Bit_0;
305:KlimaAErrors[11]:=Bit_0;
306:KlimaAErrors[12]:=Bit_0;
307:KlimaAErrors[13]:=Bit_0;
308:KlimaAErrors[14]:=Bit_0;
309:KlimaAErrors[15]:=Bit_0;
310:KlimaAErrors[16]:=Bit_0;
311:KlimaAErrors[17]:=Bit_0;
312:KlimaAErrors[18]:=Bit_0;
313:KlimaAErrors[19]:=Bit_0;
314:KlimaAErrors[1]:=Bit_0;
315:KlimaAErrors[20]:=Bit_0;
316:KlimaAErrors[21]:=Bit_0;
317:KlimaAErrors[22]:=Bit_0;
318:KlimaAErrors[23]:=Bit_0;
319:KlimaAErrors[24]:=Bit_0;
320:KlimaAErrors[25]:=Bit_0;
321:KlimaAErrors[26]:=Bit_0;
322:KlimaAErrors[27]:=Bit_0;
323:KlimaAErrors[28]:=Bit_0;
324:KlimaAErrors[29]:=Bit_0;
325:KlimaAErrors[2]:=Bit_0;
326:KlimaAErrors[30]:=Bit_0;
327:KlimaAErrors[31]:=Bit_0;
328:KlimaAErrors[32]:=Bit_0;
329:KlimaAErrors[33]:=Bit_0;
330:KlimaAErrors[34]:=Bit_0;
331:KlimaAErrors[35]:=Bit_0;
332:KlimaAErrors[36]:=Bit_0;
333:KlimaAErrors[37]:=Bit_0;
334:KlimaAErrors[38]:=Bit_0;
335:KlimaAErrors[39]:=Bit_0;
336:KlimaAErrors[3]:=Bit_0;
337:KlimaAErrors[40]:=Bit_0;
338:KlimaAErrors[4]:=Bit_0;
339:KlimaAErrors[5]:=Bit_0;
340:KlimaAErrors[6]:=Bit_0;
341:KlimaAErrors[7]:=Bit_0;
342:KlimaAErrors[8]:=Bit_0;
343:KlimaAErrors[9]:=Bit_0;
344:KlimaBErrors[10]:=Bit_0;
345:KlimaBErrors[11]:=Bit_0;
346:KlimaBErrors[12]:=Bit_0;
347:KlimaBErrors[13]:=Bit_0;
348:KlimaBErrors[14]:=Bit_0;
349:KlimaBErrors[15]:=Bit_0;
350:KlimaBErrors[16]:=Bit_0;
351:KlimaBErrors[17]:=Bit_0;
352:KlimaBErrors[18]:=Bit_0;
353:KlimaBErrors[19]:=Bit_0;
354:KlimaBErrors[1]:=Bit_0;
355:KlimaBErrors[20]:=Bit_0;
356:KlimaBErrors[21]:=Bit_0;
357:KlimaBErrors[22]:=Bit_0;
358:KlimaBErrors[23]:=Bit_0;
359:KlimaBErrors[24]:=Bit_0;
360:KlimaBErrors[25]:=Bit_0;
361:KlimaBErrors[26]:=Bit_0;
362:KlimaBErrors[27]:=Bit_0;
363:KlimaBErrors[28]:=Bit_0;
364:KlimaBErrors[29]:=Bit_0;
365:KlimaBErrors[2]:=Bit_0;
366:KlimaBErrors[30]:=Bit_0;
367:KlimaBErrors[31]:=Bit_0;
368:KlimaBErrors[32]:=Bit_0;
369:KlimaBErrors[33]:=Bit_0;
370:KlimaBErrors[34]:=Bit_0;
371:KlimaBErrors[35]:=Bit_0;
372:KlimaBErrors[36]:=Bit_0;
373:KlimaBErrors[37]:=Bit_0;
374:KlimaBErrors[38]:=Bit_0;
375:KlimaBErrors[39]:=Bit_0;
376:KlimaBErrors[3]:=Bit_0;
377:KlimaBErrors[40]:=Bit_0;
378:KlimaBErrors[4]:=Bit_0;
379:KlimaBErrors[5]:=Bit_0;
380:KlimaBErrors[6]:=Bit_0;
381:KlimaBErrors[7]:=Bit_0;
382:KlimaBErrors[8]:=Bit_0;
383:KlimaBErrors[9]:=Bit_0;
384:KlimaGal.AlarmKompresor1:=Bit_0;
385:KlimaGal.AlarmKompresor2:=Bit_0;
386:KlimaGal.Deluje:=Bit_0;
387:KlimaGal.EnergySaving:=Bit_0;
388:KlimaGal.FaultyEPROM:=Bit_0;
389:KlimaGal.FenThermalCutout:=Bit_0;
390:KlimaGal.GeneralAlarm:=Bit_0;
391:KlimaGal.Kompresor1naMejiObrUr:=Bit_0;
392:KlimaGal.Kompresor2naMejiObrUr:=Bit_0;
393:KlimaGal.Napaka:=Bit_0;
394:KlimaGal.NapakaPriPretokuZraka:=Bit_0;
395:KlimaGal.NapakaSenzorPovratVode:=Bit_0;
396:KlimaGal.NapakaSenzorTempIzpiha:=Bit_0;
397:KlimaGal.NapakaSenzorTempProstora:=Bit_0;
398:KlimaGal.NapakaSenzorVlaznosti:=Bit_0;
399:KlimaGal.NapakaSenzorZunanjeTemp:=Bit_0;
400:KlimaGal.NiTokaVVlazilcu:=Bit_0;
401:KlimaGal.NiVodeVVlazilcu:=Bit_0;
402:KlimaGal.NizekPritiskKompresor1:=Bit_0;
403:KlimaGal.NizekPritiskKompresor2:=Bit_0;
404:KlimaGal.NizkaTempPovratneVode:=Bit_0;
405:KlimaGal.NizkaTempVProstoru:=Bit_0;
406:KlimaGal.NizkaVlaznost:=Bit_0;
407:KlimaGal.OnOffEnablingBySupervisor:=Bit_0;
408:KlimaGal.PozarniAlarm:=Bit_0;
409:KlimaGal.Razvlazevanje:=Bit_0;
410:KlimaGal.RemoteOFFtoOutput:=Bit_0;
411:KlimaGal.RemoteOnOff:=Bit_0;
412:KlimaGal.RocniIzklop:=Bit_0;
413:KlimaGal.SenzorjiStatus:=Bit_0;
414:KlimaGal.StoppedByAlarms:=Bit_0;
415:KlimaGal.ThermalCutoutHeater1:=Bit_0;
416:KlimaGal.ThermalCutoutHeater2:=Bit_0;
417:KlimaGal.UnitOnOff:=Bit_0;
418:KlimaGal.VentilatorNaMejiObrUr:=Bit_0;
419:KlimaGal.VentilGretjeOdpiranje:=Bit_0;
420:KlimaGal.VentilGretjeZapiranje:=Bit_0;
421:KlimaGal.VentilHlajenjeOdpiranje:=Bit_0;
422:KlimaGal.VentilHlajenjeZapiranje:=Bit_0;
423:KlimaGal.VisokaTempPovratneVode:=Bit_0;
424:KlimaGal.VisokaTempVProstoru:=Bit_0;
425:KlimaGal.VisokaVlaznost:=Bit_0;
426:KlimaGal.VisokTokVVlazilcu:=Bit_0;
427:KlimaGal.Vlazenje:=Bit_0;
428:KlimaGal.ZamasenFilter:=Bit_0;
429:PMM1OverVoltage:=Bit_0;
430:PMM2OverVoltage:=Bit_0;
431:PMM3OverVoltage:=Bit_0;
432:PMMgal.Napaka:=Bit_0;
433:ErrCommScada2:=Bit_0;
434:ComSCADA2:=Bit_0;
435:ComSCADA3:=Bit_0;
436:Circ_Vpis_Dnevne_energija_scada1:=Bit_0;
437:Circ_Vpis_Dnevne_energija_scada2:=Bit_0;
438:Circ_Vpis_Tedenska_energija_scada1:=Bit_0;
439:Circ_Vpis_Tedenska_energija_scada2:=Bit_0;
440:Circ_Vpis_Mesecna_energija_scada1:=Bit_0;
441:Circ_Vpis_Mesecna_energija_scada2:=Bit_0;
(*BOOL*)
END_CASE
END_FUNCTION
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_dWord : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje LONG*)
(**)
(*Pisanje REAL*)
(**)
4001:Circ[1].CosFi_III:=Real_0;
4003:Circ[1].DelovnaEnergija:=Real_0;
4005:Circ[1].DelovnaMoc_III:=Real_0;
4007:Circ[1].DelovnaMoc_L1:=Real_0;
4009:Circ[1].DelovnaMoc_L2:=Real_0;
4011:Circ[1].DelovnaMoc_L3:=Real_0;
4013:Circ[1].Frekvenca_L1:=Real_0;
4015:Circ[1].InduktivnaEnergija:=Real_0;
4017:Circ[1].InduktivnaMoc_III:=Real_0;
4019:Circ[1].JalovaMoc_L1:=Real_0;
4021:Circ[1].JalovaMoc_L2:=Real_0;
4023:Circ[1].JalovaMoc_L3:=Real_0;
4025:Circ[1].KapacitivnaEnergija:=Real_0;
4027:Circ[1].KapacitivnaMoc_III:=Real_0;
4029:Circ[1].MaximumDemand:=Real_0;
4031:Circ[1].Napetost_L1_L2:=Real_0;
4033:Circ[1].Napetost_L1_N:=Real_0;
4035:Circ[1].Napetost_L2_L3:=Real_0;
4037:Circ[1].Napetost_L2_N:=Real_0;
4039:Circ[1].Napetost_L3_L1:=Real_0;
4041:Circ[1].Napetost_L3_N:=Real_0;
4043:Circ[1].NavideznaMoc_III:=Real_0;
4045:Circ[1].NicelniTok:=Real_0;
4047:Circ[1].PowerFactor_III:=Real_0;
4049:Circ[1].PowerFactor_L1:=Real_0;
4051:Circ[1].PowerFactor_L2:=Real_0;
4053:Circ[1].PowerFactor_L3:=Real_0;
4055:Circ[1].THDI_L1:=Real_0;
4057:Circ[1].THDI_L2:=Real_0;
4059:Circ[1].THDI_L3:=Real_0;
4061:Circ[1].THDV_L1:=Real_0;
4063:Circ[1].THDV_L2:=Real_0;
4065:Circ[1].THDV_L3:=Real_0;
4067:Circ[1].Tok_L1:=Real_0;
4069:Circ[1].Tok_L2:=Real_0;
4071:Circ[1].Tok_L3:=Real_0;
4073:Circ[1].TokPovprecje_III:=Real_0;
4075:Circutor.CosFi_III:=Real_0;
4077:Circutor.DelovnaEnergija:=Real_0;
4079:Circutor.DelovnaMoc_III:=Real_0;
4081:Circutor.DelovnaMoc_L1:=Real_0;
4083:Circutor.DelovnaMoc_L2:=Real_0;
4085:Circutor.DelovnaMoc_L3:=Real_0;
4087:Circutor.Frekvenca_L1:=Real_0;
4089:Circutor.InduktivnaEnergija:=Real_0;
4091:Circutor.InduktivnaMoc_III:=Real_0;
4093:Circutor.JalovaMoc_L1:=Real_0;
4095:Circutor.JalovaMoc_L2:=Real_0;
4097:Circutor.JalovaMoc_L3:=Real_0;
4099:Circutor.KapacitivnaEnergija:=Real_0;
4101:Circutor.KapacitivnaMoc_III:=Real_0;
4103:Circutor.MaximumDemand:=Real_0;
4105:Circutor.Napetost_L1_L2:=Real_0;
4107:Circutor.Napetost_L1_N:=Real_0;
4109:Circutor.Napetost_L2_L3:=Real_0;
4111:Circutor.Napetost_L2_N:=Real_0;
4113:Circutor.Napetost_L3_L1:=Real_0;
4115:Circutor.Napetost_L3_N:=Real_0;
4117:Circutor.NavideznaMoc_III:=Real_0;
4119:Circutor.NicelniTok:=Real_0;
4121:Circutor.PowerFactor_III:=Real_0;
4123:Circutor.PowerFactor_L1:=Real_0;
4125:Circutor.PowerFactor_L2:=Real_0;
4127:Circutor.PowerFactor_L3:=Real_0;
4129:Circutor.THDI_L1:=Real_0;
4131:Circutor.THDI_L2:=Real_0;
4133:Circutor.THDI_L3:=Real_0;
4135:Circutor.THDV_L1:=Real_0;
4137:Circutor.THDV_L2:=Real_0;
4139:Circutor.THDV_L3:=Real_0;
4141:Circutor.Tok_L1:=Real_0;
4143:Circutor.Tok_L2:=Real_0;
4145:Circutor.Tok_L3:=Real_0;
4147:Circutor.TokPovprecje_III:=Real_0;
4149:Klima[1].NastMaxTemp:=Real_0;
4151:Klima[1].NastMaxVlaznost:=Real_0;
4153:Klima[1].NastMinTemp:=Real_0;
4155:Klima[1].NastMinVlaznost:=Real_0;
4157:Klima[1].NastTempProstora:=Real_0;
4159:Klima[1].NastVlaznost:=Real_0;
4161:Klima[1].ObratovalneUre:=Real_0;
4163:Klima[1].TemperaturaProstora:=Real_0;
4165:Klima[1].TempIzpihanegaZraka:=Real_0;
4167:Klima[1].TempPovratneVode:=Real_0;
4169:Klima[1].VlaznostProstora:=Real_0;
4171:Klima[1].ZunanjaTemp:=Real_0;
4173:Klima[2].NastMaxTemp:=Real_0;
4175:Klima[2].NastMaxVlaznost:=Real_0;
4177:Klima[2].NastMinTemp:=Real_0;
4179:Klima[2].NastMinVlaznost:=Real_0;
4181:Klima[2].NastTempProstora:=Real_0;
4183:Klima[2].NastVlaznost:=Real_0;
4185:Klima[2].ObratovalneUre:=Real_0;
4187:Klima[2].TemperaturaProstora:=Real_0;
4189:Klima[2].TempIzpihanegaZraka:=Real_0;
4191:Klima[2].TempPovratneVode:=Real_0;
4193:Klima[2].VlaznostProstora:=Real_0;
4195:Klima[2].ZunanjaTemp:=Real_0;
4197:PMM[1].ActivePowerPhaseA_kW:=Real_0;
4199:PMM[1].ActivePowerPhaseB_kW:=Real_0;
4201:PMM[1].ActivePowerPhaseC_kW:=Real_0;
4203:PMM[1].AverageCurrent_A:=Real_0;
4205:PMM[1].AveragePhaseToNeutral_V:=Real_0;
4207:PMM[1].AveragePhaseToPhase_V:=Real_0;
4209:PMM[1].CurrentInPhaseA_A:=Real_0;
4211:PMM[1].CurrentInPhaseB_A:=Real_0;
4213:PMM[1].CurrentInPhaseC_A:=Real_0;
4215:PMM[1].EnergyConsumed_kWh:=Real_0;
4217:PMM[1].Frequency_Hz:=Real_0;
4219:PMM[1].NeutralCurrent_A:=Real_0;
4221:PMM[1].Phase[1].Current[10]:=Real_0;
4223:PMM[1].Phase[1].Current[11]:=Real_0;
4225:PMM[1].Phase[1].Current[12]:=Real_0;
4227:PMM[1].Phase[1].Current[13]:=Real_0;
4229:PMM[1].Phase[1].Current[14]:=Real_0;
4231:PMM[1].Phase[1].Current[15]:=Real_0;
4233:PMM[1].Phase[1].Current[16]:=Real_0;
4235:PMM[1].Phase[1].Current[17]:=Real_0;
4237:PMM[1].Phase[1].Current[18]:=Real_0;
4239:PMM[1].Phase[1].Current[19]:=Real_0;
4241:PMM[1].Phase[1].Current[1]:=Real_0;
4243:PMM[1].Phase[1].Current[20]:=Real_0;
4245:PMM[1].Phase[1].Current[21]:=Real_0;
4247:PMM[1].Phase[1].Current[22]:=Real_0;
4249:PMM[1].Phase[1].Current[23]:=Real_0;
4251:PMM[1].Phase[1].Current[24]:=Real_0;
4253:PMM[1].Phase[1].Current[25]:=Real_0;
4255:PMM[1].Phase[1].Current[26]:=Real_0;
4257:PMM[1].Phase[1].Current[27]:=Real_0;
4259:PMM[1].Phase[1].Current[28]:=Real_0;
4261:PMM[1].Phase[1].Current[29]:=Real_0;
4263:PMM[1].Phase[1].Current[2]:=Real_0;
4265:PMM[1].Phase[1].Current[30]:=Real_0;
4267:PMM[1].Phase[1].Current[31]:=Real_0;
4269:PMM[1].Phase[1].Current[32]:=Real_0;
4271:PMM[1].Phase[1].Current[33]:=Real_0;
4273:PMM[1].Phase[1].Current[34]:=Real_0;
4275:PMM[1].Phase[1].Current[35]:=Real_0;
4277:PMM[1].Phase[1].Current[36]:=Real_0;
4279:PMM[1].Phase[1].Current[37]:=Real_0;
4281:PMM[1].Phase[1].Current[38]:=Real_0;
4283:PMM[1].Phase[1].Current[39]:=Real_0;
4285:PMM[1].Phase[1].Current[3]:=Real_0;
4287:PMM[1].Phase[1].Current[40]:=Real_0;
4289:PMM[1].Phase[1].Current[41]:=Real_0;
4291:PMM[1].Phase[1].Current[42]:=Real_0;
4293:PMM[1].Phase[1].Current[4]:=Real_0;
4295:PMM[1].Phase[1].Current[5]:=Real_0;
4297:PMM[1].Phase[1].Current[6]:=Real_0;
4299:PMM[1].Phase[1].Current[7]:=Real_0;
4301:PMM[1].Phase[1].Current[8]:=Real_0;
4303:PMM[1].Phase[1].Current[9]:=Real_0;
4305:PMM[1].Phase[2].Current[10]:=Real_0;
4307:PMM[1].Phase[2].Current[11]:=Real_0;
4309:PMM[1].Phase[2].Current[12]:=Real_0;
4311:PMM[1].Phase[2].Current[13]:=Real_0;
4313:PMM[1].Phase[2].Current[14]:=Real_0;
4315:PMM[1].Phase[2].Current[15]:=Real_0;
4317:PMM[1].Phase[2].Current[16]:=Real_0;
4319:PMM[1].Phase[2].Current[17]:=Real_0;
4321:PMM[1].Phase[2].Current[18]:=Real_0;
4323:PMM[1].Phase[2].Current[19]:=Real_0;
4325:PMM[1].Phase[2].Current[1]:=Real_0;
4327:PMM[1].Phase[2].Current[20]:=Real_0;
4329:PMM[1].Phase[2].Current[21]:=Real_0;
4331:PMM[1].Phase[2].Current[22]:=Real_0;
4333:PMM[1].Phase[2].Current[23]:=Real_0;
4335:PMM[1].Phase[2].Current[24]:=Real_0;
4337:PMM[1].Phase[2].Current[25]:=Real_0;
4339:PMM[1].Phase[2].Current[26]:=Real_0;
4341:PMM[1].Phase[2].Current[27]:=Real_0;
4343:PMM[1].Phase[2].Current[28]:=Real_0;
4345:PMM[1].Phase[2].Current[29]:=Real_0;
4347:PMM[1].Phase[2].Current[2]:=Real_0;
4349:PMM[1].Phase[2].Current[30]:=Real_0;
4351:PMM[1].Phase[2].Current[31]:=Real_0;
4353:PMM[1].Phase[2].Current[32]:=Real_0;
4355:PMM[1].Phase[2].Current[33]:=Real_0;
4357:PMM[1].Phase[2].Current[34]:=Real_0;
4359:PMM[1].Phase[2].Current[35]:=Real_0;
4361:PMM[1].Phase[2].Current[36]:=Real_0;
4363:PMM[1].Phase[2].Current[37]:=Real_0;
4365:PMM[1].Phase[2].Current[38]:=Real_0;
4367:PMM[1].Phase[2].Current[39]:=Real_0;
4369:PMM[1].Phase[2].Current[3]:=Real_0;
4371:PMM[1].Phase[2].Current[40]:=Real_0;
4373:PMM[1].Phase[2].Current[41]:=Real_0;
4375:PMM[1].Phase[2].Current[42]:=Real_0;
4377:PMM[1].Phase[2].Current[4]:=Real_0;
4379:PMM[1].Phase[2].Current[5]:=Real_0;
4381:PMM[1].Phase[2].Current[6]:=Real_0;
4383:PMM[1].Phase[2].Current[7]:=Real_0;
4385:PMM[1].Phase[2].Current[8]:=Real_0;
4387:PMM[1].Phase[2].Current[9]:=Real_0;
4389:PMM[1].Phase[3].Current[10]:=Real_0;
4391:PMM[1].Phase[3].Current[11]:=Real_0;
4393:PMM[1].Phase[3].Current[12]:=Real_0;
4395:PMM[1].Phase[3].Current[13]:=Real_0;
4397:PMM[1].Phase[3].Current[14]:=Real_0;
4399:PMM[1].Phase[3].Current[15]:=Real_0;
4401:PMM[1].Phase[3].Current[16]:=Real_0;
4403:PMM[1].Phase[3].Current[17]:=Real_0;
4405:PMM[1].Phase[3].Current[18]:=Real_0;
4407:PMM[1].Phase[3].Current[19]:=Real_0;
4409:PMM[1].Phase[3].Current[1]:=Real_0;
4411:PMM[1].Phase[3].Current[20]:=Real_0;
4413:PMM[1].Phase[3].Current[21]:=Real_0;
4415:PMM[1].Phase[3].Current[22]:=Real_0;
4417:PMM[1].Phase[3].Current[23]:=Real_0;
4419:PMM[1].Phase[3].Current[24]:=Real_0;
4421:PMM[1].Phase[3].Current[25]:=Real_0;
4423:PMM[1].Phase[3].Current[26]:=Real_0;
4425:PMM[1].Phase[3].Current[27]:=Real_0;
4427:PMM[1].Phase[3].Current[28]:=Real_0;
4429:PMM[1].Phase[3].Current[29]:=Real_0;
4431:PMM[1].Phase[3].Current[2]:=Real_0;
4433:PMM[1].Phase[3].Current[30]:=Real_0;
4435:PMM[1].Phase[3].Current[31]:=Real_0;
4437:PMM[1].Phase[3].Current[32]:=Real_0;
4439:PMM[1].Phase[3].Current[33]:=Real_0;
4441:PMM[1].Phase[3].Current[34]:=Real_0;
4443:PMM[1].Phase[3].Current[35]:=Real_0;
4445:PMM[1].Phase[3].Current[36]:=Real_0;
4447:PMM[1].Phase[3].Current[37]:=Real_0;
4449:PMM[1].Phase[3].Current[38]:=Real_0;
4451:PMM[1].Phase[3].Current[39]:=Real_0;
4453:PMM[1].Phase[3].Current[3]:=Real_0;
4455:PMM[1].Phase[3].Current[40]:=Real_0;
4457:PMM[1].Phase[3].Current[41]:=Real_0;
4459:PMM[1].Phase[3].Current[42]:=Real_0;
4461:PMM[1].Phase[3].Current[4]:=Real_0;
4463:PMM[1].Phase[3].Current[5]:=Real_0;
4465:PMM[1].Phase[3].Current[6]:=Real_0;
4467:PMM[1].Phase[3].Current[7]:=Real_0;
4469:PMM[1].Phase[3].Current[8]:=Real_0;
4471:PMM[1].Phase[3].Current[9]:=Real_0;
4473:PMM[1].PowerFactorPhaseA:=Real_0;
4475:PMM[1].PowerFactorPhaseB:=Real_0;
4477:PMM[1].PowerFactorPhaseC:=Real_0;
4479:PMM[1].TotalActivePower_kW:=Real_0;
4481:PMM[1].TotalAparentPower_kVA:=Real_0;
4483:PMM[1].TotalPowerFactor:=Real_0;
4485:PMM[1].TotalReactivePower_kVAR:=Real_0;
4487:PMM[1].VoltageBetweenPhaseAB_V:=Real_0;
4489:PMM[1].VoltageBetweenPhaseAN_V:=Real_0;
4491:PMM[1].VoltageBetweenPhaseBC_V:=Real_0;
4493:PMM[1].VoltageBetweenPhaseBN_V:=Real_0;
4495:PMM[1].VoltageBetweenPhaseCA_V:=Real_0;
4497:PMM[1].VoltageBetweenPhaseCN_V:=Real_0;
4499:PMM[2].ActivePowerPhaseA_kW:=Real_0;
4501:PMM[2].ActivePowerPhaseB_kW:=Real_0;
4503:PMM[2].ActivePowerPhaseC_kW:=Real_0;
4505:PMM[2].AverageCurrent_A:=Real_0;
4507:PMM[2].AveragePhaseToNeutral_V:=Real_0;
4509:PMM[2].AveragePhaseToPhase_V:=Real_0;
4511:PMM[2].CurrentInPhaseA_A:=Real_0;
4513:PMM[2].CurrentInPhaseB_A:=Real_0;
4515:PMM[2].CurrentInPhaseC_A:=Real_0;
4517:PMM[2].EnergyConsumed_kWh:=Real_0;
4519:PMM[2].Frequency_Hz:=Real_0;
4521:PMM[2].NeutralCurrent_A:=Real_0;
4523:PMM[2].Phase[1].Current[10]:=Real_0;
4525:PMM[2].Phase[1].Current[11]:=Real_0;
4527:PMM[2].Phase[1].Current[12]:=Real_0;
4529:PMM[2].Phase[1].Current[13]:=Real_0;
4531:PMM[2].Phase[1].Current[14]:=Real_0;
4533:PMM[2].Phase[1].Current[15]:=Real_0;
4535:PMM[2].Phase[1].Current[16]:=Real_0;
4537:PMM[2].Phase[1].Current[17]:=Real_0;
4539:PMM[2].Phase[1].Current[18]:=Real_0;
4541:PMM[2].Phase[1].Current[19]:=Real_0;
4543:PMM[2].Phase[1].Current[1]:=Real_0;
4545:PMM[2].Phase[1].Current[20]:=Real_0;
4547:PMM[2].Phase[1].Current[21]:=Real_0;
4549:PMM[2].Phase[1].Current[22]:=Real_0;
4551:PMM[2].Phase[1].Current[23]:=Real_0;
4553:PMM[2].Phase[1].Current[24]:=Real_0;
4555:PMM[2].Phase[1].Current[25]:=Real_0;
4557:PMM[2].Phase[1].Current[26]:=Real_0;
4559:PMM[2].Phase[1].Current[27]:=Real_0;
4561:PMM[2].Phase[1].Current[28]:=Real_0;
4563:PMM[2].Phase[1].Current[29]:=Real_0;
4565:PMM[2].Phase[1].Current[2]:=Real_0;
4567:PMM[2].Phase[1].Current[30]:=Real_0;
4569:PMM[2].Phase[1].Current[31]:=Real_0;
4571:PMM[2].Phase[1].Current[32]:=Real_0;
4573:PMM[2].Phase[1].Current[33]:=Real_0;
4575:PMM[2].Phase[1].Current[34]:=Real_0;
4577:PMM[2].Phase[1].Current[35]:=Real_0;
4579:PMM[2].Phase[1].Current[36]:=Real_0;
4581:PMM[2].Phase[1].Current[37]:=Real_0;
4583:PMM[2].Phase[1].Current[38]:=Real_0;
4585:PMM[2].Phase[1].Current[39]:=Real_0;
4587:PMM[2].Phase[1].Current[3]:=Real_0;
4589:PMM[2].Phase[1].Current[40]:=Real_0;
4591:PMM[2].Phase[1].Current[41]:=Real_0;
4593:PMM[2].Phase[1].Current[42]:=Real_0;
4595:PMM[2].Phase[1].Current[4]:=Real_0;
4597:PMM[2].Phase[1].Current[5]:=Real_0;
4599:PMM[2].Phase[1].Current[6]:=Real_0;
4601:PMM[2].Phase[1].Current[7]:=Real_0;
4603:PMM[2].Phase[1].Current[8]:=Real_0;
4605:PMM[2].Phase[1].Current[9]:=Real_0;
4607:PMM[2].Phase[2].Current[10]:=Real_0;
4609:PMM[2].Phase[2].Current[11]:=Real_0;
4611:PMM[2].Phase[2].Current[12]:=Real_0;
4613:PMM[2].Phase[2].Current[13]:=Real_0;
4615:PMM[2].Phase[2].Current[14]:=Real_0;
4617:PMM[2].Phase[2].Current[15]:=Real_0;
4619:PMM[2].Phase[2].Current[16]:=Real_0;
4621:PMM[2].Phase[2].Current[17]:=Real_0;
4623:PMM[2].Phase[2].Current[18]:=Real_0;
4625:PMM[2].Phase[2].Current[19]:=Real_0;
4627:PMM[2].Phase[2].Current[1]:=Real_0;
4629:PMM[2].Phase[2].Current[20]:=Real_0;
4631:PMM[2].Phase[2].Current[21]:=Real_0;
4633:PMM[2].Phase[2].Current[22]:=Real_0;
4635:PMM[2].Phase[2].Current[23]:=Real_0;
4637:PMM[2].Phase[2].Current[24]:=Real_0;
4639:PMM[2].Phase[2].Current[25]:=Real_0;
4641:PMM[2].Phase[2].Current[26]:=Real_0;
4643:PMM[2].Phase[2].Current[27]:=Real_0;
4645:PMM[2].Phase[2].Current[28]:=Real_0;
4647:PMM[2].Phase[2].Current[29]:=Real_0;
4649:PMM[2].Phase[2].Current[2]:=Real_0;
4651:PMM[2].Phase[2].Current[30]:=Real_0;
4653:PMM[2].Phase[2].Current[31]:=Real_0;
4655:PMM[2].Phase[2].Current[32]:=Real_0;
4657:PMM[2].Phase[2].Current[33]:=Real_0;
4659:PMM[2].Phase[2].Current[34]:=Real_0;
4661:PMM[2].Phase[2].Current[35]:=Real_0;
4663:PMM[2].Phase[2].Current[36]:=Real_0;
4665:PMM[2].Phase[2].Current[37]:=Real_0;
4667:PMM[2].Phase[2].Current[38]:=Real_0;
4669:PMM[2].Phase[2].Current[39]:=Real_0;
4671:PMM[2].Phase[2].Current[3]:=Real_0;
4673:PMM[2].Phase[2].Current[40]:=Real_0;
4675:PMM[2].Phase[2].Current[41]:=Real_0;
4677:PMM[2].Phase[2].Current[42]:=Real_0;
4679:PMM[2].Phase[2].Current[4]:=Real_0;
4681:PMM[2].Phase[2].Current[5]:=Real_0;
4683:PMM[2].Phase[2].Current[6]:=Real_0;
4685:PMM[2].Phase[2].Current[7]:=Real_0;
4687:PMM[2].Phase[2].Current[8]:=Real_0;
4689:PMM[2].Phase[2].Current[9]:=Real_0;
4691:PMM[2].Phase[3].Current[10]:=Real_0;
4693:PMM[2].Phase[3].Current[11]:=Real_0;
4695:PMM[2].Phase[3].Current[12]:=Real_0;
4697:PMM[2].Phase[3].Current[13]:=Real_0;
4699:PMM[2].Phase[3].Current[14]:=Real_0;
4701:PMM[2].Phase[3].Current[15]:=Real_0;
4703:PMM[2].Phase[3].Current[16]:=Real_0;
4705:PMM[2].Phase[3].Current[17]:=Real_0;
4707:PMM[2].Phase[3].Current[18]:=Real_0;
4709:PMM[2].Phase[3].Current[19]:=Real_0;
4711:PMM[2].Phase[3].Current[1]:=Real_0;
4713:PMM[2].Phase[3].Current[20]:=Real_0;
4715:PMM[2].Phase[3].Current[21]:=Real_0;
4717:PMM[2].Phase[3].Current[22]:=Real_0;
4719:PMM[2].Phase[3].Current[23]:=Real_0;
4721:PMM[2].Phase[3].Current[24]:=Real_0;
4723:PMM[2].Phase[3].Current[25]:=Real_0;
4725:PMM[2].Phase[3].Current[26]:=Real_0;
4727:PMM[2].Phase[3].Current[27]:=Real_0;
4729:PMM[2].Phase[3].Current[28]:=Real_0;
4731:PMM[2].Phase[3].Current[29]:=Real_0;
4733:PMM[2].Phase[3].Current[2]:=Real_0;
4735:PMM[2].Phase[3].Current[30]:=Real_0;
4737:PMM[2].Phase[3].Current[31]:=Real_0;
4739:PMM[2].Phase[3].Current[32]:=Real_0;
4741:PMM[2].Phase[3].Current[33]:=Real_0;
4743:PMM[2].Phase[3].Current[34]:=Real_0;
4745:PMM[2].Phase[3].Current[35]:=Real_0;
4747:PMM[2].Phase[3].Current[36]:=Real_0;
4749:PMM[2].Phase[3].Current[37]:=Real_0;
4751:PMM[2].Phase[3].Current[38]:=Real_0;
4753:PMM[2].Phase[3].Current[39]:=Real_0;
4755:PMM[2].Phase[3].Current[3]:=Real_0;
4757:PMM[2].Phase[3].Current[40]:=Real_0;
4759:PMM[2].Phase[3].Current[41]:=Real_0;
4761:PMM[2].Phase[3].Current[42]:=Real_0;
4763:PMM[2].Phase[3].Current[4]:=Real_0;
4765:PMM[2].Phase[3].Current[5]:=Real_0;
4767:PMM[2].Phase[3].Current[6]:=Real_0;
4769:PMM[2].Phase[3].Current[7]:=Real_0;
4771:PMM[2].Phase[3].Current[8]:=Real_0;
4773:PMM[2].Phase[3].Current[9]:=Real_0;
4775:PMM[2].PowerFactorPhaseA:=Real_0;
4777:PMM[2].PowerFactorPhaseB:=Real_0;
4779:PMM[2].PowerFactorPhaseC:=Real_0;
4781:PMM[2].TotalActivePower_kW:=Real_0;
4783:PMM[2].TotalAparentPower_kVA:=Real_0;
4785:PMM[2].TotalPowerFactor:=Real_0;
4787:PMM[2].TotalReactivePower_kVAR:=Real_0;
4789:PMM[2].VoltageBetweenPhaseAB_V:=Real_0;
4791:PMM[2].VoltageBetweenPhaseAN_V:=Real_0;
4793:PMM[2].VoltageBetweenPhaseBC_V:=Real_0;
4795:PMM[2].VoltageBetweenPhaseBN_V:=Real_0;
4797:PMM[2].VoltageBetweenPhaseCA_V:=Real_0;
4799:PMM[2].VoltageBetweenPhaseCN_V:=Real_0;
4801:PMM[3].ActivePowerPhaseA_kW:=Real_0;
4803:PMM[3].ActivePowerPhaseB_kW:=Real_0;
4805:PMM[3].ActivePowerPhaseC_kW:=Real_0;
4807:PMM[3].AverageCurrent_A:=Real_0;
4809:PMM[3].AveragePhaseToNeutral_V:=Real_0;
4811:PMM[3].AveragePhaseToPhase_V:=Real_0;
4813:PMM[3].CurrentInPhaseA_A:=Real_0;
4815:PMM[3].CurrentInPhaseB_A:=Real_0;
4817:PMM[3].CurrentInPhaseC_A:=Real_0;
4819:PMM[3].EnergyConsumed_kWh:=Real_0;
4821:PMM[3].Frequency_Hz:=Real_0;
4823:PMM[3].NeutralCurrent_A:=Real_0;
4825:PMM[3].Phase[1].Current[10]:=Real_0;
4827:PMM[3].Phase[1].Current[11]:=Real_0;
4829:PMM[3].Phase[1].Current[12]:=Real_0;
4831:PMM[3].Phase[1].Current[13]:=Real_0;
4833:PMM[3].Phase[1].Current[14]:=Real_0;
4835:PMM[3].Phase[1].Current[15]:=Real_0;
4837:PMM[3].Phase[1].Current[16]:=Real_0;
4839:PMM[3].Phase[1].Current[17]:=Real_0;
4841:PMM[3].Phase[1].Current[18]:=Real_0;
4843:PMM[3].Phase[1].Current[19]:=Real_0;
4845:PMM[3].Phase[1].Current[1]:=Real_0;
4847:PMM[3].Phase[1].Current[20]:=Real_0;
4849:PMM[3].Phase[1].Current[21]:=Real_0;
4851:PMM[3].Phase[1].Current[22]:=Real_0;
4853:PMM[3].Phase[1].Current[23]:=Real_0;
4855:PMM[3].Phase[1].Current[24]:=Real_0;
4857:PMM[3].Phase[1].Current[25]:=Real_0;
4859:PMM[3].Phase[1].Current[26]:=Real_0;
4861:PMM[3].Phase[1].Current[27]:=Real_0;
4863:PMM[3].Phase[1].Current[28]:=Real_0;
4865:PMM[3].Phase[1].Current[29]:=Real_0;
4867:PMM[3].Phase[1].Current[2]:=Real_0;
4869:PMM[3].Phase[1].Current[30]:=Real_0;
4871:PMM[3].Phase[1].Current[31]:=Real_0;
4873:PMM[3].Phase[1].Current[32]:=Real_0;
4875:PMM[3].Phase[1].Current[33]:=Real_0;
4877:PMM[3].Phase[1].Current[34]:=Real_0;
4879:PMM[3].Phase[1].Current[35]:=Real_0;
4881:PMM[3].Phase[1].Current[36]:=Real_0;
4883:PMM[3].Phase[1].Current[37]:=Real_0;
4885:PMM[3].Phase[1].Current[38]:=Real_0;
4887:PMM[3].Phase[1].Current[39]:=Real_0;
4889:PMM[3].Phase[1].Current[3]:=Real_0;
4891:PMM[3].Phase[1].Current[40]:=Real_0;
4893:PMM[3].Phase[1].Current[41]:=Real_0;
4895:PMM[3].Phase[1].Current[42]:=Real_0;
4897:PMM[3].Phase[1].Current[4]:=Real_0;
4899:PMM[3].Phase[1].Current[5]:=Real_0;
4901:PMM[3].Phase[1].Current[6]:=Real_0;
4903:PMM[3].Phase[1].Current[7]:=Real_0;
4905:PMM[3].Phase[1].Current[8]:=Real_0;
4907:PMM[3].Phase[1].Current[9]:=Real_0;
4909:PMM[3].Phase[2].Current[10]:=Real_0;
4911:PMM[3].Phase[2].Current[11]:=Real_0;
4913:PMM[3].Phase[2].Current[12]:=Real_0;
4915:PMM[3].Phase[2].Current[13]:=Real_0;
4917:PMM[3].Phase[2].Current[14]:=Real_0;
4919:PMM[3].Phase[2].Current[15]:=Real_0;
4921:PMM[3].Phase[2].Current[16]:=Real_0;
4923:PMM[3].Phase[2].Current[17]:=Real_0;
4925:PMM[3].Phase[2].Current[18]:=Real_0;
4927:PMM[3].Phase[2].Current[19]:=Real_0;
4929:PMM[3].Phase[2].Current[1]:=Real_0;
4931:PMM[3].Phase[2].Current[20]:=Real_0;
4933:PMM[3].Phase[2].Current[21]:=Real_0;
4935:PMM[3].Phase[2].Current[22]:=Real_0;
4937:PMM[3].Phase[2].Current[23]:=Real_0;
4939:PMM[3].Phase[2].Current[24]:=Real_0;
4941:PMM[3].Phase[2].Current[25]:=Real_0;
4943:PMM[3].Phase[2].Current[26]:=Real_0;
4945:PMM[3].Phase[2].Current[27]:=Real_0;
4947:PMM[3].Phase[2].Current[28]:=Real_0;
4949:PMM[3].Phase[2].Current[29]:=Real_0;
4951:PMM[3].Phase[2].Current[2]:=Real_0;
4953:PMM[3].Phase[2].Current[30]:=Real_0;
4955:PMM[3].Phase[2].Current[31]:=Real_0;
4957:PMM[3].Phase[2].Current[32]:=Real_0;
4959:PMM[3].Phase[2].Current[33]:=Real_0;
4961:PMM[3].Phase[2].Current[34]:=Real_0;
4963:PMM[3].Phase[2].Current[35]:=Real_0;
4965:PMM[3].Phase[2].Current[36]:=Real_0;
4967:PMM[3].Phase[2].Current[37]:=Real_0;
4969:PMM[3].Phase[2].Current[38]:=Real_0;
4971:PMM[3].Phase[2].Current[39]:=Real_0;
4973:PMM[3].Phase[2].Current[3]:=Real_0;
4975:PMM[3].Phase[2].Current[40]:=Real_0;
4977:PMM[3].Phase[2].Current[41]:=Real_0;
4979:PMM[3].Phase[2].Current[42]:=Real_0;
4981:PMM[3].Phase[2].Current[4]:=Real_0;
4983:PMM[3].Phase[2].Current[5]:=Real_0;
4985:PMM[3].Phase[2].Current[6]:=Real_0;
4987:PMM[3].Phase[2].Current[7]:=Real_0;
4989:PMM[3].Phase[2].Current[8]:=Real_0;
4991:PMM[3].Phase[2].Current[9]:=Real_0;
4993:PMM[3].Phase[3].Current[10]:=Real_0;
4995:PMM[3].Phase[3].Current[11]:=Real_0;
4997:PMM[3].Phase[3].Current[12]:=Real_0;
4999:PMM[3].Phase[3].Current[13]:=Real_0;
5001:PMM[3].Phase[3].Current[14]:=Real_0;
5003:PMM[3].Phase[3].Current[15]:=Real_0;
5005:PMM[3].Phase[3].Current[16]:=Real_0;
5007:PMM[3].Phase[3].Current[17]:=Real_0;
5009:PMM[3].Phase[3].Current[18]:=Real_0;
5011:PMM[3].Phase[3].Current[19]:=Real_0;
5013:PMM[3].Phase[3].Current[1]:=Real_0;
5015:PMM[3].Phase[3].Current[20]:=Real_0;
5017:PMM[3].Phase[3].Current[21]:=Real_0;
5019:PMM[3].Phase[3].Current[22]:=Real_0;
5021:PMM[3].Phase[3].Current[23]:=Real_0;
5023:PMM[3].Phase[3].Current[24]:=Real_0;
5025:PMM[3].Phase[3].Current[25]:=Real_0;
5027:PMM[3].Phase[3].Current[26]:=Real_0;
5029:PMM[3].Phase[3].Current[27]:=Real_0;
5031:PMM[3].Phase[3].Current[28]:=Real_0;
5033:PMM[3].Phase[3].Current[29]:=Real_0;
5035:PMM[3].Phase[3].Current[2]:=Real_0;
5037:PMM[3].Phase[3].Current[30]:=Real_0;
5039:PMM[3].Phase[3].Current[31]:=Real_0;
5041:PMM[3].Phase[3].Current[32]:=Real_0;
5043:PMM[3].Phase[3].Current[33]:=Real_0;
5045:PMM[3].Phase[3].Current[34]:=Real_0;
5047:PMM[3].Phase[3].Current[35]:=Real_0;
5049:PMM[3].Phase[3].Current[36]:=Real_0;
5051:PMM[3].Phase[3].Current[37]:=Real_0;
5053:PMM[3].Phase[3].Current[38]:=Real_0;
5055:PMM[3].Phase[3].Current[39]:=Real_0;
5057:PMM[3].Phase[3].Current[3]:=Real_0;
5059:PMM[3].Phase[3].Current[40]:=Real_0;
5061:PMM[3].Phase[3].Current[41]:=Real_0;
5063:PMM[3].Phase[3].Current[42]:=Real_0;
5065:PMM[3].Phase[3].Current[4]:=Real_0;
5067:PMM[3].Phase[3].Current[5]:=Real_0;
5069:PMM[3].Phase[3].Current[6]:=Real_0;
5071:PMM[3].Phase[3].Current[7]:=Real_0;
5073:PMM[3].Phase[3].Current[8]:=Real_0;
5075:PMM[3].Phase[3].Current[9]:=Real_0;
5077:PMM[3].PowerFactorPhaseA:=Real_0;
5079:PMM[3].PowerFactorPhaseB:=Real_0;
5081:PMM[3].PowerFactorPhaseC:=Real_0;
5083:PMM[3].TotalActivePower_kW:=Real_0;
5085:PMM[3].TotalAparentPower_kVA:=Real_0;
5087:PMM[3].TotalPowerFactor:=Real_0;
5089:PMM[3].TotalReactivePower_kVAR:=Real_0;
5091:PMM[3].VoltageBetweenPhaseAB_V:=Real_0;
5093:PMM[3].VoltageBetweenPhaseAN_V:=Real_0;
5095:PMM[3].VoltageBetweenPhaseBC_V:=Real_0;
5097:PMM[3].VoltageBetweenPhaseBN_V:=Real_0;
5099:PMM[3].VoltageBetweenPhaseCA_V:=Real_0;
5101:PMM[3].VoltageBetweenPhaseCN_V:=Real_0;
5103:rVersion:=Real_0;
5105:SenzorTemp[1]:=Real_0;
5107:SenzorTemp[2]:=Real_0;
5109:SenzorVlaga[1]:=Real_0;
5111:SenzorVlaga[2]:=Real_0;
5113:TempMaxPoint:=Real_0;
5115:TempSetPoint:=Real_0;
5117:UPS[1].EstimatedChargeRemaining:=Real_0;
5119:UPS[1].EstimatedMinutesRemaining:=Real_0;
5121:UPS[1].IzhodMocL1:=Real_0;
5123:UPS[1].IzhodMocL2:=Real_0;
5125:UPS[1].IzhodMocL3:=Real_0;
5127:UPS[1].NapetostBaterije:=Real_0;
5129:UPS[1].TemperaturaBaterije:=Real_0;
5131:UPS[1].VhodFrekvencaL1:=Real_0;
5133:UPS[1].VhodFrekvencaL2:=Real_0;
5135:UPS[1].VhodFrekvencaL3:=Real_0;
5137:UPS[1].VhodNapetostL1:=Real_0;
5139:UPS[1].VhodNapetostL2:=Real_0;
5141:UPS[1].VhodNapetostL3:=Real_0;
5143:UPS[2].EstimatedChargeRemaining:=Real_0;
5145:UPS[2].EstimatedMinutesRemaining:=Real_0;
5147:UPS[2].IzhodMocL1:=Real_0;
5149:UPS[2].IzhodMocL2:=Real_0;
5151:UPS[2].IzhodMocL3:=Real_0;
5153:UPS[2].NapetostBaterije:=Real_0;
5155:UPS[2].TemperaturaBaterije:=Real_0;
5157:UPS[2].VhodFrekvencaL1:=Real_0;
5159:UPS[2].VhodFrekvencaL2:=Real_0;
5161:UPS[2].VhodFrekvencaL3:=Real_0;
5163:UPS[2].VhodNapetostL1:=Real_0;
5165:UPS[2].VhodNapetostL2:=Real_0;
5167:UPS[2].VhodNapetostL3:=Real_0;
5169:KlimaGal.NastMaxTemp:=Real_0;
5171:KlimaGal.NastMaxVlaznost:=Real_0;
5173:KlimaGal.NastMinTemp:=Real_0;
5175:KlimaGal.NastMinVlaznost:=Real_0;
5177:KlimaGal.NastTempProstora:=Real_0;
5179:KlimaGal.NastVlaznost:=Real_0;
5181:KlimaGal.ObratovalneUre:=Real_0;
5183:KlimaGal.TemperaturaProstora:=Real_0;
5185:KlimaGal.TempIzpihanegaZraka:=Real_0;
5187:KlimaGal.TempPovratneVode:=Real_0;
5189:KlimaGal.VlaznostProstora:=Real_0;
5191:KlimaGal.ZunanjaTemp:=Real_0;
5193:PMMfaza01:=Real_0;
5195:PMMfaza02:=Real_0;
5197:PMMfaza03:=Real_0;
5199:PMMfaza04:=Real_0;
5201:PMMfaza05:=Real_0;
5203:PMMfaza06:=Real_0;
5205:PMMfaza07:=Real_0;
5207:PMMfaza08:=Real_0;
5209:PMMfaza09:=Real_0;
5211:PMMfaza10:=Real_0;
5213:PMMfaza11:=Real_0;
5215:PMMfaza12:=Real_0;
5217:PMMfaza13:=Real_0;
5219:PMMfaza14:=Real_0;
5221:PMMfaza15:=Real_0;
5223:PMMfaza16:=Real_0;
5225:PMMfaza17:=Real_0;
5227:PMMfaza18:=Real_0;
5229:PMMfaza19:=Real_0;
5231:PMMfaza20:=Real_0;
5233:PMMfaza21:=Real_0;
5235:PMMfaza22:=Real_0;
5237:PMMfaza23:=Real_0;
5239:PMMfaza24:=Real_0;
5241:PMMfaza25:=Real_0;
5243:PMMfaza26:=Real_0;
5245:PMMfaza27:=Real_0;
5247:PMMfaza28:=Real_0;
5249:PMMfaza29:=Real_0;
5251:PMMfaza30:=Real_0;
5253:PMMfaza31:=Real_0;
5255:PMMfaza32:=Real_0;
5257:PMMfaza33:=Real_0;
5259:PMMfaza34:=Real_0;
5261:PMMfaza35:=Real_0;
5263:PMMfaza36:=Real_0;
5265:PMMfaza37:=Real_0;
5267:PMMfaza38:=Real_0;
5269:PMMfaza39:=Real_0;
5271:PMMfaza40:=Real_0;
5273:PMMfaza41:=Real_0;
5275:PMMfaza42:=Real_0;
5277:PMMfaza60[10]:=Real_0;
5279:PMMfaza60[11]:=Real_0;
5281:PMMfaza60[12]:=Real_0;
5283:PMMfaza60[13]:=Real_0;
5285:PMMfaza60[14]:=Real_0;
5287:PMMfaza60[15]:=Real_0;
5289:PMMfaza60[16]:=Real_0;
5291:PMMfaza60[17]:=Real_0;
5293:PMMfaza60[18]:=Real_0;
5295:PMMfaza60[19]:=Real_0;
5297:PMMfaza60[1]:=Real_0;
5299:PMMfaza60[20]:=Real_0;
5301:PMMfaza60[21]:=Real_0;
5303:PMMfaza60[22]:=Real_0;
5305:PMMfaza60[23]:=Real_0;
5307:PMMfaza60[24]:=Real_0;
5309:PMMfaza60[25]:=Real_0;
5311:PMMfaza60[26]:=Real_0;
5313:PMMfaza60[27]:=Real_0;
5315:PMMfaza60[28]:=Real_0;
5317:PMMfaza60[29]:=Real_0;
5319:PMMfaza60[2]:=Real_0;
5321:PMMfaza60[30]:=Real_0;
5323:PMMfaza60[31]:=Real_0;
5325:PMMfaza60[32]:=Real_0;
5327:PMMfaza60[33]:=Real_0;
5329:PMMfaza60[34]:=Real_0;
5331:PMMfaza60[35]:=Real_0;
5333:PMMfaza60[36]:=Real_0;
5335:PMMfaza60[37]:=Real_0;
5337:PMMfaza60[38]:=Real_0;
5339:PMMfaza60[39]:=Real_0;
5341:PMMfaza60[3]:=Real_0;
5343:PMMfaza60[40]:=Real_0;
5345:PMMfaza60[41]:=Real_0;
5347:PMMfaza60[42]:=Real_0;
5349:PMMfaza60[4]:=Real_0;
5351:PMMfaza60[5]:=Real_0;
5353:PMMfaza60[6]:=Real_0;
5355:PMMfaza60[7]:=Real_0;
5357:PMMfaza60[8]:=Real_0;
5359:PMMfaza60[9]:=Real_0;
5361:PMMfaza80[10]:=Real_0;
5363:PMMfaza80[11]:=Real_0;
5365:PMMfaza80[12]:=Real_0;
5367:PMMfaza80[13]:=Real_0;
5369:PMMfaza80[14]:=Real_0;
5371:PMMfaza80[15]:=Real_0;
5373:PMMfaza80[16]:=Real_0;
5375:PMMfaza80[17]:=Real_0;
5377:PMMfaza80[18]:=Real_0;
5379:PMMfaza80[19]:=Real_0;
5381:PMMfaza80[1]:=Real_0;
5383:PMMfaza80[20]:=Real_0;
5385:PMMfaza80[21]:=Real_0;
5387:PMMfaza80[22]:=Real_0;
5389:PMMfaza80[23]:=Real_0;
5391:PMMfaza80[24]:=Real_0;
5393:PMMfaza80[25]:=Real_0;
5395:PMMfaza80[26]:=Real_0;
5397:PMMfaza80[27]:=Real_0;
5399:PMMfaza80[28]:=Real_0;
5401:PMMfaza80[29]:=Real_0;
5403:PMMfaza80[2]:=Real_0;
5405:PMMfaza80[30]:=Real_0;
5407:PMMfaza80[31]:=Real_0;
5409:PMMfaza80[32]:=Real_0;
5411:PMMfaza80[33]:=Real_0;
5413:PMMfaza80[34]:=Real_0;
5415:PMMfaza80[35]:=Real_0;
5417:PMMfaza80[36]:=Real_0;
5419:PMMfaza80[37]:=Real_0;
5421:PMMfaza80[38]:=Real_0;
5423:PMMfaza80[39]:=Real_0;
5425:PMMfaza80[3]:=Real_0;
5427:PMMfaza80[40]:=Real_0;
5429:PMMfaza80[41]:=Real_0;
5431:PMMfaza80[42]:=Real_0;
5433:PMMfaza80[4]:=Real_0;
5435:PMMfaza80[5]:=Real_0;
5437:PMMfaza80[6]:=Real_0;
5439:PMMfaza80[7]:=Real_0;
5441:PMMfaza80[8]:=Real_0;
5443:PMMfaza80[9]:=Real_0;
5445:PMMgal.ActivePowerPhaseA_kW:=Real_0;
5447:PMMgal.ActivePowerPhaseB_kW:=Real_0;
5449:PMMgal.ActivePowerPhaseC_kW:=Real_0;
5451:PMMgal.AverageCurrent_A:=Real_0;
5453:PMMgal.AveragePhaseToNeutral_V:=Real_0;
5455:PMMgal.AveragePhaseToPhase_V:=Real_0;
5457:PMMgal.CurrentInPhaseA_A:=Real_0;
5459:PMMgal.CurrentInPhaseB_A:=Real_0;
5461:PMMgal.CurrentInPhaseC_A:=Real_0;
5463:PMMgal.EnergyConsumed_kWh:=Real_0;
5465:PMMgal.Frequency_Hz:=Real_0;
5467:PMMgal.NeutralCurrent_A:=Real_0;
5469:PMMgal.Phase[1].Current[10]:=Real_0;
5471:PMMgal.Phase[1].Current[11]:=Real_0;
5473:PMMgal.Phase[1].Current[12]:=Real_0;
5475:PMMgal.Phase[1].Current[13]:=Real_0;
5477:PMMgal.Phase[1].Current[14]:=Real_0;
5479:PMMgal.Phase[1].Current[15]:=Real_0;
5481:PMMgal.Phase[1].Current[16]:=Real_0;
5483:PMMgal.Phase[1].Current[17]:=Real_0;
5485:PMMgal.Phase[1].Current[18]:=Real_0;
5487:PMMgal.Phase[1].Current[19]:=Real_0;
5489:PMMgal.Phase[1].Current[1]:=Real_0;
5491:PMMgal.Phase[1].Current[20]:=Real_0;
5493:PMMgal.Phase[1].Current[21]:=Real_0;
5495:PMMgal.Phase[1].Current[22]:=Real_0;
5497:PMMgal.Phase[1].Current[23]:=Real_0;
5499:PMMgal.Phase[1].Current[24]:=Real_0;
5501:PMMgal.Phase[1].Current[25]:=Real_0;
5503:PMMgal.Phase[1].Current[26]:=Real_0;
5505:PMMgal.Phase[1].Current[27]:=Real_0;
5507:PMMgal.Phase[1].Current[28]:=Real_0;
5509:PMMgal.Phase[1].Current[29]:=Real_0;
5511:PMMgal.Phase[1].Current[2]:=Real_0;
5513:PMMgal.Phase[1].Current[30]:=Real_0;
5515:PMMgal.Phase[1].Current[31]:=Real_0;
5517:PMMgal.Phase[1].Current[32]:=Real_0;
5519:PMMgal.Phase[1].Current[33]:=Real_0;
5521:PMMgal.Phase[1].Current[34]:=Real_0;
5523:PMMgal.Phase[1].Current[35]:=Real_0;
5525:PMMgal.Phase[1].Current[36]:=Real_0;
5527:PMMgal.Phase[1].Current[37]:=Real_0;
5529:PMMgal.Phase[1].Current[38]:=Real_0;
5531:PMMgal.Phase[1].Current[39]:=Real_0;
5533:PMMgal.Phase[1].Current[3]:=Real_0;
5535:PMMgal.Phase[1].Current[40]:=Real_0;
5537:PMMgal.Phase[1].Current[41]:=Real_0;
5539:PMMgal.Phase[1].Current[42]:=Real_0;
5541:PMMgal.Phase[1].Current[4]:=Real_0;
5543:PMMgal.Phase[1].Current[5]:=Real_0;
5545:PMMgal.Phase[1].Current[6]:=Real_0;
5547:PMMgal.Phase[1].Current[7]:=Real_0;
5549:PMMgal.Phase[1].Current[8]:=Real_0;
5551:PMMgal.Phase[1].Current[9]:=Real_0;
5553:PMMgal.Phase[2].Current[10]:=Real_0;
5555:PMMgal.Phase[2].Current[11]:=Real_0;
5557:PMMgal.Phase[2].Current[12]:=Real_0;
5559:PMMgal.Phase[2].Current[13]:=Real_0;
5561:PMMgal.Phase[2].Current[14]:=Real_0;
5563:PMMgal.Phase[2].Current[15]:=Real_0;
5565:PMMgal.Phase[2].Current[16]:=Real_0;
5567:PMMgal.Phase[2].Current[17]:=Real_0;
5569:PMMgal.Phase[2].Current[18]:=Real_0;
5571:PMMgal.Phase[2].Current[19]:=Real_0;
5573:PMMgal.Phase[2].Current[1]:=Real_0;
5575:PMMgal.Phase[2].Current[20]:=Real_0;
5577:PMMgal.Phase[2].Current[21]:=Real_0;
5579:PMMgal.Phase[2].Current[22]:=Real_0;
5581:PMMgal.Phase[2].Current[23]:=Real_0;
5583:PMMgal.Phase[2].Current[24]:=Real_0;
5585:TempAlarmPoint:=Real_0;
5587:RazlikaUr:=Real_0;
5589:Circ[1].MaximumDemandA2:=Real_0;
5591:Circ[1].MaximumDemandA3:=Real_0;
5593:Circ[1].RazEner_D_SCADA:=Real_0;
5595:Circ[1].RazEner_T_SCADA:=Real_0;
5597:Circ[1].RazEner_M_SCADA:=Real_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_String : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje STRING*)
(**)
7000:UserCurrentName:=String_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Word : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje INT*)
(**)
0:DateTime.Dan:=Byte_0;
1:DateTime.Leto:=Byte_0;
2:DateTime.Mesec:=Byte_0;
3:DateTime.Minuta:=Byte_0;
4:DateTime.Sekunda:=Byte_0;
5:DateTime.Ura:=Byte_0;
6:Klima[1].GrelecStatus:=Byte_0;
7:Klima[1].IzhodniVentStatus:=Byte_0;
8:Klima[1].KompresorStatus:=Byte_0;
9:Klima[1].VlazilecStatus:=Byte_0;
10:Klima[2].GrelecStatus:=Byte_0;
11:Klima[2].IzhodniVentStatus:=Byte_0;
12:Klima[2].KompresorStatus:=Byte_0;
13:Klima[2].VlazilecStatus:=Byte_0;
14:PMM[1].AlarmPhase[1].C01_16_60to80:=Word_01;
15:PMM[1].AlarmPhase[1].C01_16_over80:=Word_01;
16:PMM[1].AlarmPhase[1].C17_32_60to80:=Word_01;
17:PMM[1].AlarmPhase[1].C17_32_over80:=Word_01;
18:PMM[1].AlarmPhase[1].C33_42_60to80:=Word_01;
19:PMM[1].AlarmPhase[1].C33_42_over80:=Word_01;
20:PMM[1].AlarmPhase[1].GlobalAlarmReg:=Word_01;
21:PMM[1].AlarmPhase[2].C01_16_60to80:=Word_01;
22:PMM[1].AlarmPhase[2].C01_16_over80:=Word_01;
23:PMM[1].AlarmPhase[2].C17_32_60to80:=Word_01;
24:PMM[1].AlarmPhase[2].C17_32_over80:=Word_01;
25:PMM[1].AlarmPhase[2].C33_42_60to80:=Word_01;
26:PMM[1].AlarmPhase[2].C33_42_over80:=Word_01;
27:PMM[1].AlarmPhase[2].GlobalAlarmReg:=Word_01;
28:PMM[1].AlarmPhase[3].C01_16_60to80:=Word_01;
29:PMM[1].AlarmPhase[3].C01_16_over80:=Word_01;
30:PMM[1].AlarmPhase[3].C17_32_60to80:=Word_01;
31:PMM[1].AlarmPhase[3].C17_32_over80:=Word_01;
32:PMM[1].AlarmPhase[3].C33_42_60to80:=Word_01;
33:PMM[1].AlarmPhase[3].C33_42_over80:=Word_01;
34:PMM[1].AlarmPhase[3].GlobalAlarmReg:=Word_01;
35:PMM[1].Alarms:=Word_01;
36:PMM[2].AlarmPhase[1].C01_16_60to80:=Word_01;
37:PMM[2].AlarmPhase[1].C01_16_over80:=Word_01;
38:PMM[2].AlarmPhase[1].C17_32_60to80:=Word_01;
39:PMM[2].AlarmPhase[1].C17_32_over80:=Word_01;
40:PMM[2].AlarmPhase[1].C33_42_60to80:=Word_01;
41:PMM[2].AlarmPhase[1].C33_42_over80:=Word_01;
42:PMM[2].AlarmPhase[1].GlobalAlarmReg:=Word_01;
43:PMM[2].AlarmPhase[2].C01_16_60to80:=Word_01;
44:PMM[2].AlarmPhase[2].C01_16_over80:=Word_01;
45:PMM[2].AlarmPhase[2].C17_32_60to80:=Word_01;
46:PMM[2].AlarmPhase[2].C17_32_over80:=Word_01;
47:PMM[2].AlarmPhase[2].C33_42_60to80:=Word_01;
48:PMM[2].AlarmPhase[2].C33_42_over80:=Word_01;
49:PMM[2].AlarmPhase[2].GlobalAlarmReg:=Word_01;
50:PMM[2].AlarmPhase[3].C01_16_60to80:=Word_01;
51:PMM[2].AlarmPhase[3].C01_16_over80:=Word_01;
52:PMM[2].AlarmPhase[3].C17_32_60to80:=Word_01;
53:PMM[2].AlarmPhase[3].C17_32_over80:=Word_01;
54:PMM[2].AlarmPhase[3].C33_42_60to80:=Word_01;
55:PMM[2].AlarmPhase[3].C33_42_over80:=Word_01;
56:PMM[2].AlarmPhase[3].GlobalAlarmReg:=Word_01;
57:PMM[2].Alarms:=Word_01;
58:PMM[3].AlarmPhase[1].C01_16_60to80:=Word_01;
59:PMM[3].AlarmPhase[1].C01_16_over80:=Word_01;
60:PMM[3].AlarmPhase[1].C17_32_60to80:=Word_01;
61:PMM[3].AlarmPhase[1].C17_32_over80:=Word_01;
62:PMM[3].AlarmPhase[1].C33_42_60to80:=Word_01;
63:PMM[3].AlarmPhase[1].C33_42_over80:=Word_01;
64:PMM[3].AlarmPhase[1].GlobalAlarmReg:=Word_01;
65:PMM[3].AlarmPhase[2].C01_16_60to80:=Word_01;
66:PMM[3].AlarmPhase[2].C01_16_over80:=Word_01;
67:PMM[3].AlarmPhase[2].C17_32_60to80:=Word_01;
68:PMM[3].AlarmPhase[2].C17_32_over80:=Word_01;
69:PMM[3].AlarmPhase[2].C33_42_60to80:=Word_01;
70:PMM[3].AlarmPhase[2].C33_42_over80:=Word_01;
71:PMM[3].AlarmPhase[2].GlobalAlarmReg:=Word_01;
72:PMM[3].AlarmPhase[3].C01_16_60to80:=Word_01;
73:PMM[3].AlarmPhase[3].C01_16_over80:=Word_01;
74:PMM[3].AlarmPhase[3].C17_32_60to80:=Word_01;
75:PMM[3].AlarmPhase[3].C17_32_over80:=Word_01;
76:PMM[3].AlarmPhase[3].C33_42_60to80:=Word_01;
77:PMM[3].AlarmPhase[3].C33_42_over80:=Word_01;
78:PMM[3].AlarmPhase[3].GlobalAlarmReg:=Word_01;
79:PMM[3].Alarms:=Word_01;
80:UPS[1].InverterStatus:=Word_01;
81:UPS[1].OutputStatus:=Word_01;
82:UPS[1].StatusBaterije:=Word_01;
83:UPS[1].SteviloIzpadovVhodneLinije:=Word_01;
84:UPS[1].UnitStatus:=Word_01;
85:UPS[2].InverterStatus:=Word_01;
86:UPS[2].OutputStatus:=Word_01;
87:UPS[2].StatusBaterije:=Word_01;
88:UPS[2].SteviloIzpadovVhodneLinije:=Word_01;
89:UPS[2].UnitStatus:=Word_01;
90:UserCurrentLevel:=Byte_0;
91:ErrorComCirc[1].Code[10]:=Byte_0;
92:ErrorComCirc[1].Code[11]:=Byte_0;
93:ErrorComCirc[1].Code[12]:=Byte_0;
94:ErrorComCirc[1].Code[13]:=Byte_0;
95:ErrorComCirc[1].Code[14]:=Byte_0;
96:ErrorComCirc[1].Code[15]:=Byte_0;
97:ErrorComCirc[1].Code[1]:=Byte_0;
98:ErrorComCirc[1].Code[2]:=Byte_0;
99:ErrorComCirc[1].Code[3]:=Byte_0;
100:ErrorComCirc[1].Code[4]:=Byte_0;
101:ErrorComCirc[1].Code[5]:=Byte_0;
102:ErrorComCirc[1].Code[6]:=Byte_0;
103:ErrorComCirc[1].Code[7]:=Byte_0;
104:ErrorComCirc[1].Code[8]:=Byte_0;
105:ErrorComCirc[1].Code[9]:=Byte_0;
106:ErrorComCirc[1].Status:=Word_01;
107:ErrorComCirc[2].Code[10]:=Byte_0;
108:ErrorComCirc[2].Code[11]:=Byte_0;
109:ErrorComCirc[2].Code[12]:=Byte_0;
110:ErrorComCirc[2].Code[13]:=Byte_0;
111:ErrorComCirc[2].Code[14]:=Byte_0;
112:ErrorComCirc[2].Code[15]:=Byte_0;
113:ErrorComCirc[2].Code[1]:=Byte_0;
114:ErrorComCirc[2].Code[2]:=Byte_0;
115:ErrorComCirc[2].Code[3]:=Byte_0;
116:ErrorComCirc[2].Code[4]:=Byte_0;
117:ErrorComCirc[2].Code[5]:=Byte_0;
118:ErrorComCirc[2].Code[6]:=Byte_0;
119:ErrorComCirc[2].Code[7]:=Byte_0;
120:ErrorComCirc[2].Code[8]:=Byte_0;
121:ErrorComCirc[2].Code[9]:=Byte_0;
122:ErrorComCirc[2].Status:=Word_01;
123:ErrorComCirc[3].Code[10]:=Byte_0;
124:ErrorComCirc[3].Code[11]:=Byte_0;
125:ErrorComCirc[3].Code[12]:=Byte_0;
126:ErrorComCirc[3].Code[13]:=Byte_0;
127:ErrorComCirc[3].Code[14]:=Byte_0;
128:ErrorComCirc[3].Code[15]:=Byte_0;
129:ErrorComCirc[3].Code[1]:=Byte_0;
130:ErrorComCirc[3].Code[2]:=Byte_0;
131:ErrorComCirc[3].Code[3]:=Byte_0;
132:ErrorComCirc[3].Code[4]:=Byte_0;
133:ErrorComCirc[3].Code[5]:=Byte_0;
134:ErrorComCirc[3].Code[6]:=Byte_0;
135:ErrorComCirc[3].Code[7]:=Byte_0;
136:ErrorComCirc[3].Code[8]:=Byte_0;
137:ErrorComCirc[3].Code[9]:=Byte_0;
138:ErrorComCirc[3].Status:=Word_01;
139:ErrorComCirc[4].Code[10]:=Byte_0;
140:ErrorComCirc[4].Code[11]:=Byte_0;
141:ErrorComCirc[4].Code[12]:=Byte_0;
142:ErrorComCirc[4].Code[13]:=Byte_0;
143:ErrorComCirc[4].Code[14]:=Byte_0;
144:ErrorComCirc[4].Code[15]:=Byte_0;
145:ErrorComCirc[4].Code[1]:=Byte_0;
146:ErrorComCirc[4].Code[2]:=Byte_0;
147:ErrorComCirc[4].Code[3]:=Byte_0;
148:ErrorComCirc[4].Code[4]:=Byte_0;
149:ErrorComCirc[4].Code[5]:=Byte_0;
150:ErrorComCirc[4].Code[6]:=Byte_0;
151:ErrorComCirc[4].Code[7]:=Byte_0;
152:ErrorComCirc[4].Code[8]:=Byte_0;
153:ErrorComCirc[4].Code[9]:=Byte_0;
154:ErrorComCirc[4].Status:=Word_01;
155:ErrorComCirc[5].Code[10]:=Byte_0;
156:ErrorComCirc[5].Code[11]:=Byte_0;
157:ErrorComCirc[5].Code[12]:=Byte_0;
158:ErrorComCirc[5].Code[13]:=Byte_0;
159:ErrorComCirc[5].Code[14]:=Byte_0;
160:ErrorComCirc[5].Code[15]:=Byte_0;
161:ErrorComCirc[5].Code[1]:=Byte_0;
162:ErrorComCirc[5].Code[2]:=Byte_0;
163:ErrorComCirc[5].Code[3]:=Byte_0;
164:ErrorComCirc[5].Code[4]:=Byte_0;
165:ErrorComCirc[5].Code[5]:=Byte_0;
166:ErrorComCirc[5].Code[6]:=Byte_0;
167:ErrorComCirc[5].Code[7]:=Byte_0;
168:ErrorComCirc[5].Code[8]:=Byte_0;
169:ErrorComCirc[5].Code[9]:=Byte_0;
170:ErrorComCirc[5].Status:=Word_01;
171:ErrorComKlima[1].Code[10]:=Byte_0;
172:ErrorComKlima[1].Code[11]:=Byte_0;
173:ErrorComKlima[1].Code[12]:=Byte_0;
174:ErrorComKlima[1].Code[13]:=Byte_0;
175:ErrorComKlima[1].Code[14]:=Byte_0;
176:ErrorComKlima[1].Code[15]:=Byte_0;
177:ErrorComKlima[1].Code[1]:=Byte_0;
178:ErrorComKlima[1].Code[2]:=Byte_0;
179:ErrorComKlima[1].Code[3]:=Byte_0;
180:ErrorComKlima[1].Code[4]:=Byte_0;
181:ErrorComKlima[1].Code[5]:=Byte_0;
182:ErrorComKlima[1].Code[6]:=Byte_0;
183:ErrorComKlima[1].Code[7]:=Byte_0;
184:ErrorComKlima[1].Code[8]:=Byte_0;
185:ErrorComKlima[1].Code[9]:=Byte_0;
186:ErrorComKlima[1].Status:=Word_01;
187:ErrorComKlima[2].Code[10]:=Byte_0;
188:ErrorComKlima[2].Code[11]:=Byte_0;
189:ErrorComKlima[2].Code[12]:=Byte_0;
190:ErrorComKlima[2].Code[13]:=Byte_0;
191:ErrorComKlima[2].Code[14]:=Byte_0;
192:ErrorComKlima[2].Code[15]:=Byte_0;
193:ErrorComKlima[2].Code[1]:=Byte_0;
194:ErrorComKlima[2].Code[2]:=Byte_0;
195:ErrorComKlima[2].Code[3]:=Byte_0;
196:ErrorComKlima[2].Code[4]:=Byte_0;
197:ErrorComKlima[2].Code[5]:=Byte_0;
198:ErrorComKlima[2].Code[6]:=Byte_0;
199:ErrorComKlima[2].Code[7]:=Byte_0;
200:ErrorComKlima[2].Code[8]:=Byte_0;
201:ErrorComKlima[2].Code[9]:=Byte_0;
202:ErrorComKlima[2].Status:=Word_01;
203:ErrorComKlima[3].Code[10]:=Byte_0;
204:ErrorComKlima[3].Code[11]:=Byte_0;
205:ErrorComKlima[3].Code[12]:=Byte_0;
206:ErrorComKlima[3].Code[13]:=Byte_0;
207:ErrorComKlima[3].Code[14]:=Byte_0;
208:ErrorComKlima[3].Code[15]:=Byte_0;
209:ErrorComKlima[3].Code[1]:=Byte_0;
210:ErrorComKlima[3].Code[2]:=Byte_0;
211:ErrorComKlima[3].Code[3]:=Byte_0;
212:ErrorComKlima[3].Code[4]:=Byte_0;
213:ErrorComKlima[3].Code[5]:=Byte_0;
214:ErrorComKlima[3].Code[6]:=Byte_0;
215:ErrorComKlima[3].Code[7]:=Byte_0;
216:ErrorComKlima[3].Code[8]:=Byte_0;
217:ErrorComKlima[3].Code[9]:=Byte_0;
218:ErrorComKlima[3].Status:=Word_01;
219:ErrorComKlima[4].Code[10]:=Byte_0;
220:ErrorComKlima[4].Code[11]:=Byte_0;
221:ErrorComKlima[4].Code[12]:=Byte_0;
222:ErrorComKlima[4].Code[13]:=Byte_0;
223:ErrorComKlima[4].Code[14]:=Byte_0;
224:ErrorComKlima[4].Code[15]:=Byte_0;
225:ErrorComKlima[4].Code[1]:=Byte_0;
226:ErrorComKlima[4].Code[2]:=Byte_0;
227:ErrorComKlima[4].Code[3]:=Byte_0;
228:ErrorComKlima[4].Code[4]:=Byte_0;
229:ErrorComKlima[4].Code[5]:=Byte_0;
230:ErrorComKlima[4].Code[6]:=Byte_0;
231:ErrorComKlima[4].Code[7]:=Byte_0;
232:ErrorComKlima[4].Code[8]:=Byte_0;
233:ErrorComKlima[4].Code[9]:=Byte_0;
234:ErrorComKlima[4].Status:=Word_01;
235:ErrorComKlima[5].Code[10]:=Byte_0;
236:ErrorComKlima[5].Code[11]:=Byte_0;
237:ErrorComKlima[5].Code[12]:=Byte_0;
238:ErrorComKlima[5].Code[13]:=Byte_0;
239:ErrorComKlima[5].Code[14]:=Byte_0;
240:ErrorComKlima[5].Code[15]:=Byte_0;
241:ErrorComKlima[5].Code[1]:=Byte_0;
242:ErrorComKlima[5].Code[2]:=Byte_0;
243:ErrorComKlima[5].Code[3]:=Byte_0;
244:ErrorComKlima[5].Code[4]:=Byte_0;
245:ErrorComKlima[5].Code[5]:=Byte_0;
246:ErrorComKlima[5].Code[6]:=Byte_0;
247:ErrorComKlima[5].Code[7]:=Byte_0;
248:ErrorComKlima[5].Code[8]:=Byte_0;
249:ErrorComKlima[5].Code[9]:=Byte_0;
250:ErrorComKlima[5].Status:=Word_01;
251:ErrorComKlima[6].Code[10]:=Byte_0;
252:ErrorComKlima[6].Code[11]:=Byte_0;
253:ErrorComKlima[6].Code[12]:=Byte_0;
254:ErrorComKlima[6].Code[13]:=Byte_0;
255:ErrorComKlima[6].Code[14]:=Byte_0;
256:ErrorComKlima[6].Code[15]:=Byte_0;
257:ErrorComKlima[6].Code[1]:=Byte_0;
258:ErrorComKlima[6].Code[2]:=Byte_0;
259:ErrorComKlima[6].Code[3]:=Byte_0;
260:ErrorComKlima[6].Code[4]:=Byte_0;
261:ErrorComKlima[6].Code[5]:=Byte_0;
262:ErrorComKlima[6].Code[6]:=Byte_0;
263:ErrorComKlima[6].Code[7]:=Byte_0;
264:ErrorComKlima[6].Code[8]:=Byte_0;
265:ErrorComKlima[6].Code[9]:=Byte_0;
266:ErrorComKlima[6].Status:=Word_01;
267:ErrorComPMM[1].Code[10]:=Byte_0;
268:ErrorComPMM[1].Code[11]:=Byte_0;
269:ErrorComPMM[1].Code[12]:=Byte_0;
270:ErrorComPMM[1].Code[13]:=Byte_0;
271:ErrorComPMM[1].Code[14]:=Byte_0;
272:ErrorComPMM[1].Code[15]:=Byte_0;
273:ErrorComPMM[1].Code[1]:=Byte_0;
274:ErrorComPMM[1].Code[2]:=Byte_0;
275:ErrorComPMM[1].Code[3]:=Byte_0;
276:ErrorComPMM[1].Code[4]:=Byte_0;
277:ErrorComPMM[1].Code[5]:=Byte_0;
278:ErrorComPMM[1].Code[6]:=Byte_0;
279:ErrorComPMM[1].Code[7]:=Byte_0;
280:ErrorComPMM[1].Code[8]:=Byte_0;
281:ErrorComPMM[1].Code[9]:=Byte_0;
282:ErrorComPMM[1].Status:=Word_01;
283:ErrorComPMM[2].Code[10]:=Byte_0;
284:ErrorComPMM[2].Code[11]:=Byte_0;
285:ErrorComPMM[2].Code[12]:=Byte_0;
286:ErrorComPMM[2].Code[13]:=Byte_0;
287:ErrorComPMM[2].Code[14]:=Byte_0;
288:ErrorComPMM[2].Code[15]:=Byte_0;
289:ErrorComPMM[2].Code[1]:=Byte_0;
290:ErrorComPMM[2].Code[2]:=Byte_0;
291:ErrorComPMM[2].Code[3]:=Byte_0;
292:ErrorComPMM[2].Code[4]:=Byte_0;
293:ErrorComPMM[2].Code[5]:=Byte_0;
294:ErrorComPMM[2].Code[6]:=Byte_0;
295:ErrorComPMM[2].Code[7]:=Byte_0;
296:ErrorComPMM[2].Code[8]:=Byte_0;
297:ErrorComPMM[2].Code[9]:=Byte_0;
298:ErrorComPMM[2].Status:=Word_01;
299:ErrorComPMM[3].Code[10]:=Byte_0;
300:ErrorComPMM[3].Code[11]:=Byte_0;
301:ErrorComPMM[3].Code[12]:=Byte_0;
302:ErrorComPMM[3].Code[13]:=Byte_0;
303:ErrorComPMM[3].Code[14]:=Byte_0;
304:ErrorComPMM[3].Code[15]:=Byte_0;
305:ErrorComPMM[3].Code[1]:=Byte_0;
306:ErrorComPMM[3].Code[2]:=Byte_0;
307:ErrorComPMM[3].Code[3]:=Byte_0;
308:ErrorComPMM[3].Code[4]:=Byte_0;
309:ErrorComPMM[3].Code[5]:=Byte_0;
310:ErrorComPMM[3].Code[6]:=Byte_0;
311:ErrorComPMM[3].Code[7]:=Byte_0;
312:ErrorComPMM[3].Code[8]:=Byte_0;
313:ErrorComPMM[3].Code[9]:=Byte_0;
314:ErrorComPMM[3].Status:=Word_01;
315:ErrorComUPS[1].Code[10]:=Byte_0;
316:ErrorComUPS[1].Code[11]:=Byte_0;
317:ErrorComUPS[1].Code[12]:=Byte_0;
318:ErrorComUPS[1].Code[13]:=Byte_0;
319:ErrorComUPS[1].Code[14]:=Byte_0;
320:ErrorComUPS[1].Code[15]:=Byte_0;
321:ErrorComUPS[1].Code[1]:=Byte_0;
322:ErrorComUPS[1].Code[2]:=Byte_0;
323:ErrorComUPS[1].Code[3]:=Byte_0;
324:ErrorComUPS[1].Code[4]:=Byte_0;
325:ErrorComUPS[1].Code[5]:=Byte_0;
326:ErrorComUPS[1].Code[6]:=Byte_0;
327:ErrorComUPS[1].Code[7]:=Byte_0;
328:ErrorComUPS[1].Code[8]:=Byte_0;
329:ErrorComUPS[1].Code[9]:=Byte_0;
330:ErrorComUPS[1].Status:=Word_01;
331:ErrorComUPS[2].Code[10]:=Byte_0;
332:ErrorComUPS[2].Code[11]:=Byte_0;
333:ErrorComUPS[2].Code[12]:=Byte_0;
334:ErrorComUPS[2].Code[13]:=Byte_0;
335:ErrorComUPS[2].Code[14]:=Byte_0;
336:ErrorComUPS[2].Code[15]:=Byte_0;
337:ErrorComUPS[2].Code[1]:=Byte_0;
338:ErrorComUPS[2].Code[2]:=Byte_0;
339:ErrorComUPS[2].Code[3]:=Byte_0;
340:ErrorComUPS[2].Code[4]:=Byte_0;
341:ErrorComUPS[2].Code[5]:=Byte_0;
342:ErrorComUPS[2].Code[6]:=Byte_0;
343:ErrorComUPS[2].Code[7]:=Byte_0;
344:ErrorComUPS[2].Code[8]:=Byte_0;
345:ErrorComUPS[2].Code[9]:=Byte_0;
346:ErrorComUPS[2].Status:=Word_01;
347:KlimaGal.GrelecStatus:=Byte_0;
348:KlimaGal.IzhodniVentStatus:=Byte_0;
349:KlimaGal.KompresorStatus:=Byte_0;
350:KlimaGal.VlazilecStatus:=Byte_0;
351:PMMgal.AlarmPhase[1].GlobalAlarmReg:=Word_01;
352:PMMgal.AlarmPhase[2].GlobalAlarmReg:=Word_01;
353:PMMgal.AlarmPhase[3].GlobalAlarmReg:=Word_01;
354:kom_nast_cas_izpada:=Word_01;
(*Pisanje UINT*)
(**)
8000:PMMgal.AlarmPhase[1].C01_16_60to80:=Word_01;
8001:PMMgal.AlarmPhase[1].C01_16_over80:=Word_01;
8002:PMMgal.AlarmPhase[1].C17_32_60to80:=Word_01;
8003:PMMgal.AlarmPhase[1].C17_32_over80:=Word_01;
8004:PMMgal.AlarmPhase[1].C33_42_60to80:=Word_01;
8005:PMMgal.AlarmPhase[1].C33_42_over80:=Word_01;
8006:PMMgal.AlarmPhase[2].C01_16_60to80:=Word_01;
8007:PMMgal.AlarmPhase[2].C01_16_over80:=Word_01;
8008:PMMgal.AlarmPhase[2].C17_32_60to80:=Word_01;
8009:PMMgal.AlarmPhase[2].C17_32_over80:=Word_01;
8010:PMMgal.AlarmPhase[2].C33_42_60to80:=Word_01;
8011:PMMgal.AlarmPhase[2].C33_42_over80:=Word_01;
8012:PMMgal.AlarmPhase[3].C01_16_60to80:=Word_01;
8013:PMMgal.AlarmPhase[3].C01_16_over80:=Word_01;
8014:PMMgal.AlarmPhase[3].C17_32_60to80:=Word_01;
8015:PMMgal.AlarmPhase[3].C17_32_over80:=Word_01;
8016:PMMgal.AlarmPhase[3].C33_42_60to80:=Word_01;
8017:PMMgal.AlarmPhase[3].C33_42_over80:=Word_01;
8018:PMMgal.Alarms:=Word_01;
;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
(*Modbus Slave Example*)
PROGRAM PLC_PRG_modnet
VAR
Slave_Adresa:BYTE:=2;
Slave_Port:INT:=502;
SlaveSetup:MBS_Setup;
SlavePoll:MBS_Poll;
SlaveAnswer:MBS_Answer;
step: USINT;
end :BOOL;
i: INT;
cycle :BOOL := FALSE; (* First cycle *)
OpenDefaultPort: BOOL;
Write_16: BOOL;
Write_15: BOOL;
Write_5: BOOL;
j: INT;
slavepollwOffset_temp: INT;
slaveanswerwCount_temp: INT;
slaveanswerwoffset_temp: INT;
END_VAR
(* @END_DECLARATION := '0' *)
(*Modbus Slave Example*)
IF Write_16=TRUE THEN (**)
FOR j := 0 TO (slaveanswerwCount_temp-1)/15 BY 1 DO (*vpiše se dword, real*)
wStr_0:=mind[slaveanswerwoffset_temp+j];
wStr_1:=mind[slaveanswerwoffset_temp+j+1];
wStr_2 :=mind[slaveanswerwoffset_temp+j+2];
wStr_3:=mind[slaveanswerwoffset_temp+j+3];
wStr_4:=mind[slaveanswerwoffset_temp+j+4];
wStr_5 :=mind[slaveanswerwoffset_temp+j+5];
wStr_6:=mind[slaveanswerwoffset_temp+j+6];
wStr_7:=mind[slaveanswerwoffset_temp+j+7];
wStr_8:=mind[slaveanswerwoffset_temp+j+8];
wStr_9:=mind[slaveanswerwoffset_temp+j+9];
wStr_10:=mind[slaveanswerwoffset_temp+j+10];
wStr_11:=mind[slaveanswerwoffset_temp+j+11];
wStr_12:=mind[slaveanswerwoffset_temp+j+12];
wStr_13:=mind[slaveanswerwoffset_temp+j+13];
wStr_14:=mind[slaveanswerwoffset_temp+j+14];
bStr_29:=0;
mod_Write_String(index:=slaveanswerwoffset_temp+j); (*vpis real in string*)
END_FOR;
FOR j := 1 TO slaveanswerwCount_temp-1 BY 2 DO (*vpiše se dword, real*)
Word_01:=mind[slaveanswerwoffset_temp+j-1];
Word_23:=mind[slaveanswerwoffset_temp+j];
mod_Write_dWord(index:=slaveanswerwoffset_temp+j); (*vpis real in dword*)
END_FOR;
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO (*vpiše se word*)
Word_01:=mind[slaveanswerwoffset_temp+j];
mod_Write_Word(index:=slaveanswerwoffset_temp+j); (*vpis word*)
END_FOR;
Write_16:=FALSE;
END_IF;
IF Write_5=TRUE OR Write_15=TRUE THEN (**)
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO
Bit_0:=mind_bool[slaveanswerwoffset_temp+j];
mod_Write_Bool(index:=slaveanswerwoffset_temp+j); (*vpis spremembe v spremenljivko*)
END_FOR;
Write_5:=FALSE;
Write_15:=FALSE;
END_IF;
(*iz scade ni komande za branje*)
IF Write_16=FALSE AND Write_5=FALSE AND Write_15=FALSE THEN
mod_Read();(*branje spremenljivk za scado*)
END_IF
(*Close all sockets on corresponding event*)
IF cycle = FALSE THEN
SysCallbackRegister(INDEXOF(Callback_Stop),event_stop);
SysCallbackRegister(INDEXOF(Callback_Reset),event_before_reset);
SysCallbackRegister(INDEXOF(Callback_Reset),event_shutdown);
cycle := TRUE;
END_IF
(*Close all connections via application *)
IF end = TRUE THEN
MBS_CloseAllConnections();
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=FALSE); (*Close port*)
step := 0;
END_IF
IF OpenDefaultPort=TRUE THEN
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=TRUE); (*Close port*)
step := 0;
OpenDefaultPort:=FALSE;
END_IF
(* State machine for setup, poll and answer *)
CASE step OF
0:(**)
SlaveSetup.bUnitIdentifier:=Slave_Adresa;(*Subunitnumber*)
slavesetup.wDefaultPort:=Slave_Port;(*Standartport *)
SlaveSetup.xAdditionalPortActive:=FALSE;(*Port opened or closed*)
SlaveSetup.xSecureMode:=FALSE;(*If TRUE only preset IPs are accepted*)
SlaveSetup.tTimeout:=T#3m;(*Timeout if no communication with slave established*)
SlaveSetup(xStrobe:=TRUE);(*Strobe starts function*)
IF slavesetup.xBusy = FALSE THEN
slavesetup(xstrobe := FALSE);
step := 1 ;
END_IF;
1:(**)
SlavePoll(xStrobe:=TRUE);(*Searching for master commands*)
IF NOT SlavePoll.xBusy THEN
step:=2;
SlavePoll(xStrobe:=FALSE);
END_IF;
2:(**)
step:= 1;
CASE SlavePoll.bFunctionCode OF (*Connect accepted pollparameters with answerparameters*)
8:(**)(*Poll answers*)
;
15:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind_bool[slaveanswer.woffset+i] := slavepoll.xarData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.xarData:=slavepoll.xarData;
Write_15:=TRUE;
16:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind[slaveanswer.woffset+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.wardata := slavepoll.warData;
Write_16:=TRUE;
1,2:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slavepoll.wcount-1 BY 1 DO
slaveanswer.xarData[i]:=mind_bool[slavepoll.woffset+i]; (*Read from Data-array*)
END_FOR
3,4:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slaveanswer.wCount-1 BY 1 DO
slaveanswer.warData[i]:=mind[slavepoll.woffset+i];(*Read from Data-array*)
END_FOR
5:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
mind_bool[slavepoll.woffset]:=slavepoll.xarData[0];(*Write to Data-array*)
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.xarData := slavepoll.xardata;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
Write_5:=TRUE;
6:
slaveanswer.bFunctionCode:= slavepoll.bFunctionCode;
mind[slavepoll.woffset]:= slavepoll.warData[0];(*Write to Data-array*)
slaveanswer.wOffset:= slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wardata := slavepoll.wardata;
23:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
FOR i:= 0 TO slavepoll.wCountAdd-1 BY 1 DO
mind[slavepoll.woffsetadd+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
FOR i := 0 TO slavepoll.wCount BY 1 DO
slaveanswer.warData[i] := mind[1+slavepoll.woffset+i];(*Read from Data-array*)
END_FOR;
END_CASE;
IF slavepoll.xAvailable = TRUE THEN
slaveanswer();(*When Data ready, send answer*)
END_IF
END_CASE;
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_dWord : BOOL
VAR_INPUT
dVAR: DWORD;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
DWord_0:=dVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_Real : BOOL
VAR_INPUT
rVAR: REAL;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
Real_0:=rVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_String : BOOL
VAR_INPUT
sVar: STRING;
start:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
String_0:=LEFT (sVar,29);
mind[start]:=wStr_0;
mind[start+1]:=wStr_1;
mind[start+2]:=wStr_2;
mind[start+3]:=wStr_3;
mind[start+4]:=wStr_4;
mind[start+5]:=wStr_5;
mind[start+6]:=wStr_6;
mind[start+7]:=wStr_7;
mind[start+8]:=wStr_8;
mind[start+9]:=wStr_9;
mind[start+10]:=wStr_10;
mind[start+11]:=wStr_11;
mind[start+12]:=wStr_12;
mind[start+13]:=wStr_13;
bStr_29:=0;
mind[start+14]:=wStr_14;
END_FUNCTION
(* @GLOBAL_VARIABLE_LIST := 'Global_Variables_Modnet' *)
(* @PATH := '' *)
(* @SYMFILEFLAGS := '2048' *)
VAR_GLOBAL
(*delovno polje za modnet komunikacijo*)
mind :ARRAY [0..9999] OF WORD;
mind_bool :ARRAY [0..9999] OF BOOL; (*Buffer-Array*)
(*Delovni markerji //*)
Bit_0 AT %MX0.0 : BOOL;
Byte_0 AT %MB0 : BYTE;
Byte_1 AT %MB1 : BYTE;
Byte_2 AT %MB2 : BYTE;
Byte_3 AT %MB3 : BYTE;
Real_0 AT %MR0:REAL;
DWord_0 AT %MD0:DWORD;
Word_01 AT %MW0:WORD;
Word_23 AT %MW2:WORD;
String_0 AT %MW10:STRING;
wStr_0 AT %MW10:WORD;
wStr_1 AT %MW12:WORD;
wStr_2 AT %MW14:WORD;
wStr_3 AT %MW16:WORD;
wStr_4 AT %MW18:WORD;
wStr_5 AT %MW20:WORD;
wStr_6 AT %MW22:WORD;
wStr_7 AT %MW24:WORD;
wStr_8 AT %MW26:WORD;
wStr_9 AT %MW28:WORD;
wStr_10 AT %MW30:WORD;
wStr_11 AT %MW32:WORD;
wStr_12 AT %MW34:WORD;
wStr_13 AT %MW36:WORD;
wStr_14 AT %MW38:WORD;
bStr_00 AT %MB10:BYTE;
bStr_01 AT %MB11:BYTE;
bStr_02 AT %MB12:BYTE;
bStr_03 AT %MB13:BYTE;
bStr_04 AT %MB14:BYTE;
bStr_05 AT %MB15:BYTE;
bStr_06 AT %MB16:BYTE;
bStr_07 AT %MB17:BYTE;
bStr_08 AT %MB18:BYTE;
bStr_09 AT %MB19:BYTE;
bStr_10 AT %MB20:BYTE;
bStr_11 AT %MB21:BYTE;
bStr_12 AT %MB22:BYTE;
bStr_13 AT %MB23:BYTE;
bStr_14 AT %MB24:BYTE;
bStr_15 AT %MB25:BYTE;
bStr_16 AT %MB26:BYTE;
bStr_17 AT %MB27:BYTE;
bStr_18 AT %MB28:BYTE;
bStr_19 AT %MB29:BYTE;
bStr_20 AT %MB30:BYTE;
bStr_21 AT %MB31:BYTE;
bStr_22 AT %MB32:BYTE;
bStr_23 AT %MB33:BYTE;
bStr_24 AT %MB34:BYTE;
bStr_25 AT %MB35:BYTE;
bStr_26 AT %MB36:BYTE;
bStr_27 AT %MB37:BYTE;
bStr_28 AT %MB38:BYTE;
bStr_29 AT %MB39:BYTE;
(********************************************)
END_VAR
(* @OBJECT_END := 'Global_Variables_Modnet' *)
(* @CONNECTIONS := Global_Variables_Modnet
FILENAME : ''
FILETIME : 0
EXPORT : 0
NUMOFCONNECTIONS : 0
*)
(*KONEC_KODA*)