## Prva stran
variable | 174 | 1.KORAK | variable_1 | 2.KORAK | KORAKI!
Device name | Tip | število spremenljivk | Tip (izbrani) | Zamenjaj z | 1.V Sheet "variable" skopiraj vsebino iz variable.dbf - iz Citect SCAD-a projekta, ki ga želiš pretvoriti.
IOD_EPS306 | BCD | 0 | BCD | INT | 2.V polje A3 vpiši Device ime spremenljivk ki se bodo prenašale preko Modnet protokola
| BYTE | 13 | BYTE | BYTE | 3.V polje A6 vpiši ime krmilnika (npr.:PLC1, če je adresa v spremenljivkah PLC1:.NapakaKoncnega_stikala, drugače pusti polje prazno)
OPC name | DIGITAL | 69 | DIGITAL | DIGITAL | 4. Pritisni gumb 1.KORAK (V poljih C3:C10 se izpiše število spremenljivk, ki imajo Device enak tistemu v polju A3)
EPS306 | INT | 23 | INT | INT | 5. Pritisni gumb 2.KORAK (V Sheet-u variable_1 se naredi seznam spremenljivk, ki se bodo prenačale preko Modnet protokola)
| LONG | 0 | LONG | LONG | 6. Pritisni gumb 3.KORAK (V poljih C15:C24 se izpiše število spremnljiv po tipih, v poljih F15:F24 se izpiše število potrebni wordow/coilov za prenos spremnljivk)
| REAL | 0 | REAL | REAL | 7. 4.KORAK: V polja C29:C38 je potrebno ročno vpisati začetne naslove spremnljivk. Potrebno je paziti na:
| STRING | 1 | UINT | UINT | *naslov se morajo začeti z lihim številom npr.:1, 101, 551
| UINT | 0 | STRING | STRING | *naslove je potrebno nastaviti tako, da se naslovi sremenljivk ne more prekrivati (naslovi spremenjivk gredo od (začetnega naslova) do (začetnega naslova+število potrebnih wordow))
8. Pritisni gumb 5.KORAK (V Sheet-u variable_2 se naredi seznam spremenljivk, ki so tokrat sortirana po tipih)
9. Pritisni gumb 6.KORAK (V Sheet-u variable_3 se naredi seznam spremenljivk, katerih Device se zamenja z devicom v polju C41)
Trajanje makroja | variable_1 |  |  | 3.KORAK | 10. Pritisni gumb 7.KORAK (V Sheet-u variable_new se generira seznam spremenljivk. To vsebino je potrebno skopirati v variable.dbf)
0 | Tip | število spremenljivk | TIP | št.potrebnih coilov/wordov | *ta korak traja nekoliko dalj časa (odvisno od števila spremenljivk)
| BCD | 0 | BCD | 0 | *če se pojavi težava z adresami ki se začnejo z 0000 (npr.: "00001" se spremeni na "1") je potrebno uporabiti priloženo (prazno) variable.dbf ali v
| BYTE | 0 | BYTE | 0 | ProjectEditoju/VariableTags na poljubni spremenljki nastaviti adreso" 00001"
| DIGITAL | 69 | DIGITAL | 69 (Coil) | 11. Pritisni gumb 8.KORAK in 9.KORAK (V Sheet-u Xsoft se generira koda)
| INT | 36 | INT | 36 (word) | 12. S pritiskom na gumb 10.KORAK se zgenerira EXP koda za Xsoft (Xsoft_EXP)
| LONG | 0 | LONG | 0 (word) | 13. S pritiskom na gumb Save*.EXP se avtomatsko generira datoka *.EXP
| REAL | 0 | REAL | 0 (word)
| STRING | 1 | STRING | 15 (word)
| UINT | 0 | UINT | 0 (word)
POZOR!
*V Sheet-u variable mora biti vsebina skopirana od polja A1 naprej (če je katera vrstica prazna makroji ne bodo delovali pravilno)
*Ena "STRING" spremenljivka zasede 15wordow (to pomeni 29 znakov, 1BYTE=1STRING)
|  | 4.KORAK(vpiši ročno) | variable_2 | 5.KORAK | *Dolžina "STRING" spremenljivk je 29 znakov (lahko tudi več vendar ne z uporabno tega dokumenta in XSoft programa,potrebna je modifikacija makrojev in Xsoft programa)
| Tip | Začetni naslov |  | Sortiraj | *Vsi stringi so enake dolžine (29)
| BCD |  |  | BCD | *"BYTE" spremenljivke se v variable.dbf spremenijo v "INT" (prenašanje posameznih bytov ni mogoče, niti naslavaljanje v citectscadi)
| BYTE |  |  | DIGITAL | *Naslovi spremenljivk se morajo obvezno začeti z lihim naslovom (preizkušeno je z začetnimi naslovi, ki se izpišejo po pritisku na gumb Ponastavi)
| DIGITAL | 1 |  | BYTE | *Z pritiskom na gumb RESET se pobriše vsebina vseh Sheet-ov razen Sheet-a variable (makor reset se izvaja precej časa)
| INT | 1 |  | INT | *makroji ne delujejo pravilno,če je v Sheet-u variable več kot 9999 vrstic oz. spremenljivk (število vseh spremnljivk je prikazano v polju B1)
| LONG | 3001 |  | LONG | *če se vsebine iz variable_new ne gre skpirat v variable.dbf datotek, vsebino skopirajte najprej v *.txt datoteko in nato v variable.dbf
| REAL | 4001 |  | REAL | *v polju A14 na Sheet-u Prva stran se prikazuje število ciklop do konca izvedbe makroja (samo za gumb 7.KORAK)
| STRING | 5001 |  | STRING
| UINT | 6001 |  | UINT
| variable_3 | 6.KORAK | variable_new | 7.KORAK
| New Device name | IOD_EPS306_TCP |  | Nova variable dbf
|  |  | xSoft | 8.KORAK in 9.KORAK
xSoft koda
xSoft_EXP
Izvoz*.EXP
1.KORAK
2.KORAK
3.KORAK
5.KORAK
6.KORAK
7.KORAK
8.KORAK
9.KORAK
RESET
Ponastavi
10.KORAK
Save*.EXP

## variable
EPS306Alarm_E5M | DIGITAL | IOD_EPS306 | EPS306:.Alarm_E5M | [6 empty] | 6157 | 1 | 0x04800010
EPS306ComSCADA | DIGITAL | IOD_EPS306 | EPS306:.ComSCADA | [6 empty] | 6157 | 1 | 0x04800020
EPS306ComSCADA1 | DIGITAL | IOD_EPS306 | EPS306:.ComSCADA1 | [6 empty] | 6157 | 1 | 0x04800030
EPS306DateTimeDan | BYTE | IOD_EPS306 | EPS306:.DateTime.Dan | [6 empty] | 6157 | 1 | 0x04800040
EPS306DateTimeLeto | BYTE | IOD_EPS306 | EPS306:.DateTime.Leto | [6 empty] | 6157 | 1 | 0x04800041
EPS306DateTimeLeto2 | INT | IOD_EPS306 | EPS306:.DateTime.Leto2 | [6 empty] | 6157 | 1 | 0x04800042
EPS306DateTimeMesec | BYTE | IOD_EPS306 | EPS306:.DateTime.Mesec | [6 empty] | 6157 | 1 | 0x04800043
EPS306DateTimeMinuta | BYTE | IOD_EPS306 | EPS306:.DateTime.Minuta | [6 empty] | 6157 | 1 | 0x04800044
EPS306DateTimeSekunda | BYTE | IOD_EPS306 | EPS306:.DateTime.Sekunda | [6 empty] | 6157 | 1 | 0x04800045
EPS306DateTimeUra | BYTE | IOD_EPS306 | EPS306:.DateTime.Ura | [6 empty] | 6157 | 1 | 0x04800046
EPS306E5_F1_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_F1_delovanje | [6 empty] | 6157 | 1 | 0x04800050
EPS306E5_F1_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_F1_napaka | [6 empty] | 6157 | 1 | 0x04800060
EPS306E5_F2_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_F2_delovanje | [6 empty] | 6157 | 1 | 0x04800070
EPS306E5_F2_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_F2_napaka | [6 empty] | 6157 | 1 | 0x04800080
EPS306E5_F3_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_F3_delovanje | [6 empty] | 6157 | 1 | 0x04800090
EPS306E5_F3_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_F3_napaka | [6 empty] | 6157 | 1 | 0x048000a0
EPS306E5_Q0_vkljuceno | DIGITAL | IOD_EPS306 | EPS306:.E5_Q0_vkljuceno | [6 empty] | 6157 | 1 | 0x048000b0
EPS306E5_U1_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_U1_delovanje | [6 empty] | 6157 | 1 | 0x048000c0
EPS306E5_U1_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_U1_napaka | [6 empty] | 6157 | 1 | 0x048000d0
EPS306E5_U2_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_U2_delovanje | [6 empty] | 6157 | 1 | 0x048000e0
EPS306E5_U2_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_U2_napaka | [6 empty] | 6157 | 1 | 0x048000f0
EPS306E5_U3_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_U3_delovanje | [6 empty] | 6157 | 1 | 0x04800100
EPS306E5_U3_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_U3_napaka | [6 empty] | 6157 | 1 | 0x04800110
EPS306ErrComCybro | DIGITAL | IOD_EPS306 | EPS306:.ErrComCybro | [6 empty] | 6157 | 1 | 0x04800120
EPS306ErrComPort2 | DIGITAL | IOD_EPS306 | EPS306:.ErrComPort2 | [6 empty] | 6157 | 1 | 0x04800130
EPS306HIA1_vlaga_s | INT | IOD_EPS306 | EPS306:.HIA1_vlaga_s | 0 | 1000 | 0 | 100 | % | ##.# | 6157 | 1 | 0x04800141
EPS306HIA2_vlaga_s | INT | IOD_EPS306 | EPS306:.HIA2_vlaga_s | 0 | 1000 | 0 | 100 | % | ##.# | 6157 | 1 | 0x04800143
EPS306HIA3_vlaga_s | INT | IOD_EPS306 | EPS306:.HIA3_vlaga_s | 0 | 1000 | 0 | 100 | % | ##.# | 6157 | 1 | 0x04800145
EPS306KLIMA_SPLIT1_delovanje | DIGITAL | IOD_EPS306 | EPS306:.KLIMA_SPLIT1_delovanje | [6 empty] | 6157 | 1 | 0x04800150
EPS306KLIMA_SPLIT1_napaka | DIGITAL | IOD_EPS306 | EPS306:.KLIMA_SPLIT1_napaka | [6 empty] | 6157 | 1 | 0x04800160
EPS306KLIMA_SPLIT2_delovanje | DIGITAL | IOD_EPS306 | EPS306:.KLIMA_SPLIT2_delovanje | [6 empty] | 6157 | 1 | 0x04800170
EPS306KLIMA_SPLIT2_napaka | DIGITAL | IOD_EPS306 | EPS306:.KLIMA_SPLIT2_napaka | [6 empty] | 6157 | 1 | 0x04800180
EPS306KomunikacijaErr | DIGITAL | IOD_EPS306 | EPS306:.KomunikacijaErr | [6 empty] | 6157 | 1 | 0x04800190
EPS306N_E5_F1_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_F1_napaka | [6 empty] | 6157 | 1 | 0x048001a0
EPS306N_E5_F2_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_F2_napaka | [6 empty] | 6157 | 1 | 0x048001b0
EPS306N_E5_F3_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_F3_napaka | [6 empty] | 6157 | 1 | 0x048001c0
EPS306N_E5_U1_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_U1_napaka | [6 empty] | 6157 | 1 | 0x048001d0
EPS306N_E5_U2_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_U2_napaka | [6 empty] | 6157 | 1 | 0x048001e0
EPS306N_E5_U3_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_U3_napaka | [6 empty] | 6157 | 1 | 0x048001f0
EPS306napaka_kom_panel | DIGITAL | IOD_EPS306 | EPS306:.napaka_kom_panel | [6 empty] | 6157 | 1 | 0x04800200
EPS306napaka_kom_scada | DIGITAL | IOD_EPS306 | EPS306:.napaka_kom_scada | [6 empty] | 6157 | 1 | 0x04800210
EPS306NapakaSenzorSkupno | DIGITAL | IOD_EPS306 | EPS306:.NapakaSenzorSkupno | [6 empty] | 6157 | 1 | 0x04800220
EPS306NapakaSenzorVlagaHIA1 | DIGITAL | IOD_EPS306 | EPS306:.NapakaSenzorVlagaHIA1 | [6 empty] | 6157 | 1 | 0x04800230
EPS306NapakaSenzorVlagaHIA2 | DIGITAL | IOD_EPS306 | EPS306:.NapakaSenzorVlagaHIA2 | [6 empty] | 6157 | 1 | 0x04800240
EPS306NapakaSenzorVlagaHIA3 | DIGITAL | IOD_EPS306 | EPS306:.NapakaSenzorVlagaHIA3 | [6 empty] | 6157 | 1 | 0x04800250
EPS306NapakaTSTempTIA1 | DIGITAL | IOD_EPS306 | EPS306:.NapakaTSTempTIA1 | [6 empty] | 6157 | 1 | 0x04800260
EPS306NapakaTSTempTIA2 | DIGITAL | IOD_EPS306 | EPS306:.NapakaTSTempTIA2 | [6 empty] | 6157 | 1 | 0x04800270
EPS306NapakaTSTempTIA3 | DIGITAL | IOD_EPS306 | EPS306:.NapakaTSTempTIA3 | [6 empty] | 6157 | 1 | 0x04800280
EPS306PrevisokaTemp | DIGITAL | IOD_EPS306 | EPS306:.PrevisokaTemp | [6 empty] | 6157 | 1 | 0x04800290
EPS306razlitje_vode_LAH1 | DIGITAL | IOD_EPS306 | EPS306:.razlitje_vode_LAH1 | [6 empty] | 6157 | 1 | 0x048002a0
EPS306razlitje_vode_LAH2 | DIGITAL | IOD_EPS306 | EPS306:.razlitje_vode_LAH2 | [6 empty] | 6157 | 1 | 0x048002b0
EPS306RezimVent1 | BYTE | IOD_EPS306 | EPS306:.RezimVent1 | [6 empty] | 6157 | 1 | 0x048002c0
EPS306RezimVent2 | BYTE | IOD_EPS306 | EPS306:.RezimVent2 | [6 empty] | 6157 | 1 | 0x048002c1
EPS306RezimVent3 | BYTE | IOD_EPS306 | EPS306:.RezimVent3 | [6 empty] | 6157 | 1 | 0x048002c2
EPS306SetDateTime | DIGITAL | IOD_EPS306 | EPS306:.SetDateTime | [6 empty] | 6157 | 1 | 0x048002d0
EPS306SetDateTimeDemand | DIGITAL | IOD_EPS306 | EPS306:.SetDateTimeDemand | [6 empty] | 6157 | 1 | 0x048002e0
EPS306SetDateTimeError | DIGITAL | IOD_EPS306 | EPS306:.SetDateTimeError | [6 empty] | 6157 | 1 | 0x048002f0
EPS306SetDateTimeFinished | DIGITAL | IOD_EPS306 | EPS306:.SetDateTimeFinished | [6 empty] | 6157 | 1 | 0x04800300
EPS306SlabaBaterijaPLC | DIGITAL | IOD_EPS306 | EPS306:.SlabaBaterijaPLC | [6 empty] | 6157 | 1 | 0x04800310
EPS306TIA1_alarm | INT | IOD_EPS306 | EPS306:.TIA1_alarm | 0 | 60 | 0 | 60 | řC | ## | 6157 | 1 | 0x04800320
EPS306TIA1_previs_temp | DIGITAL | IOD_EPS306 | EPS306:.TIA1_previs_temp | [6 empty] | 6157 | 1 | 0x04800330
EPS306TIA1_temp_s | INT | IOD_EPS306 | EPS306:.TIA1_temp_s | 0 | 600 | 0 | 60 | řC | ##.# | 6157 | 1 | 0x04800341
EPS306TIA2_alarm | INT | IOD_EPS306 | EPS306:.TIA2_alarm | 0 | 60 | 0 | 60 | řC | ## | 6157 | 1 | 0x04800342
EPS306TIA2_previs_temp | DIGITAL | IOD_EPS306 | EPS306:.TIA2_previs_temp | [6 empty] | 6157 | 1 | 0x04800350
EPS306TIA2_temp_s | INT | IOD_EPS306 | EPS306:.TIA2_temp_s | 0 | 600 | 0 | 60 | řC | ##.# | 6157 | 1 | 0x04800361
EPS306TIA3_alarm | INT | IOD_EPS306 | EPS306:.TIA3_alarm | 0 | 60 | 0 | 60 | řC | ## | 6157 | 1 | 0x04800362
EPS306TIA3_previs_temp | DIGITAL | IOD_EPS306 | EPS306:.TIA3_previs_temp | [6 empty] | 6157 | 1 | 0x04800370
EPS306TIA3_temp_s | INT | IOD_EPS306 | EPS306:.TIA3_temp_s | 0 | 600 | 0 | 60 | řC | ##.# | 6157 | 1 | 0x04800381
EPS306ups_alarm | DIGITAL | IOD_EPS306 | EPS306:.ups_alarm | [6 empty] | 6157 | 1 | 0x04800390
EPS306ups_baterijski_nac | DIGITAL | IOD_EPS306 | EPS306:.ups_baterijski_nac | [6 empty] | 6157 | 1 | 0x048003a0
EPS306ups_polnjenje | DIGITAL | IOD_EPS306 | EPS306:.ups_polnjenje | [6 empty] | 6157 | 1 | 0x048003b0
EPS306UserCurrentLevel | BYTE | IOD_EPS306 | EPS306:.UserCurrentLevel | [6 empty] | 6157 | 1 | 0x048003c0
EPS306UserCurrentName | STRING | IOD_EPS306 | EPS306:.UserCurrentName | [6 empty] | 6157 | 1 | 0x048003c1
EPS306UserLoggedIn | DIGITAL | IOD_EPS306 | EPS306:.UserLoggedIn | [6 empty] | 6157 | 1 | 0x048003d0
EPS306VentilatorjiAlarm | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiAlarm | [6 empty] | 6157 | 1 | 0x048003e0
EPS306VentilatorjiCybroAlarm_lucka | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.Alarm_lucka | [6 empty] | 6157 | 1 | 0x048003f0
EPS306VentilatorjiCybroHisterezaTEMP_HI | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.HisterezaTEMP_HI | 0 | 60 | 0 | 60 | řC | ## | 6157 | 1 | 0x048003f1
EPS306VentilatorjiCybroHisterezaTEMP_LO | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.HisterezaTEMP_LO | 0 | 60 | 0 | 60 | řC | ## | 6157 | 1 | 0x048003f2
EPS306VentilatorjiCybroHisterezaVLAGA_HI | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.HisterezaVLAGA_HI | 0 | 60 | 0 | 60 | řC | ## | 6157 | 1 | 0x048003f3
EPS306VentilatorjiCybroHisterezaVLAGA_LO | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.HisterezaVLAGA_LO | 0 | 60 | 0 | 60 | řC | ## | 6157 | 1 | 0x048003f4
EPS306VentilatorjiCybroHitrost_Vent1_MAX | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.Hitrost_Vent1_MAX | 0 | 60 | 0 | 50 | Hz | ## | 6157 | 1 | 0x048003f5
EPS306VentilatorjiCybroHitrost_Vent1_MIN | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.Hitrost_Vent1_MIN | 0 | 60 | 0 | 50 | Hz | ## | 6157 | 1 | 0x048003f6
EPS306VentilatorjiCybroI_ERR_Vent1 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.I_ERR_Vent1 | [6 empty] | 6157 | 1 | 0x04800400
EPS306VentilatorjiCybroI_ERR_Vent2 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.I_ERR_Vent2 | [6 empty] | 6157 | 1 | 0x04800410
EPS306VentilatorjiCybroI_ERR_Vent3 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.I_ERR_Vent3 | [6 empty] | 6157 | 1 | 0x04800420
EPS306VentilatorjiCybroO_Hitrost_Vent1 | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.O_Hitrost_Vent1 | 0 | 50 | 0 | 50 | Hz | ## | 6157 | 1 | 0x04800430
EPS306VentilatorjiCybroO_Hitrost_Vent2 | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.O_Hitrost_Vent2 | 0 | 50 | 0 | 50 | Hz | ## | 6157 | 1 | 0x04800431
EPS306VentilatorjiCybroO_Hitrost_Vent3 | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.O_Hitrost_Vent3 | 0 | 50 | 0 | 50 | Hz | ## | 6157 | 1 | 0x04800432
EPS306VentilatorjiCybroSAvtomatsko_Vent1 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SAvtomatsko_Vent1 | [6 empty] | 6157 | 1 | 0x04800440
EPS306VentilatorjiCybroSAvtomatsko_Vent2 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SAvtomatsko_Vent2 | [6 empty] | 6157 | 1 | 0x04800450
EPS306VentilatorjiCybroSAvtomatsko_Vent3 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SAvtomatsko_Vent3 | [6 empty] | 6157 | 1 | 0x04800460
EPS306VentilatorjiCybroSRocno_Vent1 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SRocno_Vent1 | [6 empty] | 6157 | 1 | 0x04800470
EPS306VentilatorjiCybroSRocno_Vent2 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SRocno_Vent2 | [6 empty] | 6157 | 1 | 0x04800480
EPS306VentilatorjiCybroSRocno_Vent3 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SRocno_Vent3 | [6 empty] | 6157 | 1 | 0x04800490
EPS306VentilatorjiCybroTempSKUPNA | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.TempSKUPNA | 0 | 60 | 0 | 60 | řC | ## | 6157 | 1 | 0x048004a0
EPS306VentilatorjiCybroVlagaSKUPNA | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.VlagaSKUPNA | 0 | 60 | 0 | 60 | řC | ## | 6157 | 1 | 0x048004a1
EPS306VentilatorjiNapaka | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiNapaka | [6 empty] | 6157 | 1 | 0x048004b0
EPS306XVH_AlarmOn | DIGITAL | IOD_EPS306 | EPS306:.XVH_AlarmOn | [6 empty] | 6157 | 1 | 0x048004c0
EPS306XVH_KlimaSplitStatus1 | BYTE | IOD_EPS306 | EPS306:.XVH_KlimaSplitStatus[1] | [6 empty] | 6157 | 1 | 0x048004d0
EPS306XVH_KlimaSplitStatus2 | BYTE | IOD_EPS306 | EPS306:.XVH_KlimaSplitStatus[2] | [6 empty] | 6157 | 1 | 0x048004d1
EPS306XVH_KonvekorErr | DIGITAL | IOD_EPS306 | EPS306:.XVH_KonvekorErr | [6 empty] | 6157 | 1 | 0x048004e0
EPS306XVH_UPSstatus | BYTE | IOD_EPS306 | EPS306:.XVH_UPSstatus | [6 empty] | 6157 | 1 | 0x048004f0
EPS306ComSCADA_stevec1 | INT | IOD_EPS306_mem | I1 | [6 empty] | 6157 | 1 | 0x048004f1
EPS306ComSCADA_stevec2 | INT | IOD_EPS306_mem | I2 | [6 empty] | 6157 | 1 | 0x048004f2
EPS306_Sekunda1s_utripanje | DIGITAL | IOD_EPS306_mem | D3 | [6 empty] | 6157 | 1 | 0x04800500
EP306_prikaz_ups_ce_je1 | DIGITAL | IOD_EPS306_mem | D4 | [6 empty] | 6157 | 1 | 0x04800510
EPS306E5_F1_napaka_omog | DIGITAL | IOD_EPS306_disk | D5 | [6 empty] | 6157 | 1 | 0x04800520
EPS306E5_F2_napaka_omog | DIGITAL | IOD_EPS306_disk | D6 | [6 empty] | 6157 | 1 | 0x04800530
EPS306E5_F3_napaka_omog | DIGITAL | IOD_EPS306_disk | D7 | [6 empty] | 6157 | 1 | 0x04800540
EPS306E5_U1_napaka_omog | DIGITAL | IOD_EPS306_disk | D8 | [6 empty] | 6157 | 1 | 0x04800550
EPS306E5_U2_napaka_omog | DIGITAL | IOD_EPS306_disk | D9 | [6 empty] | 6157 | 1 | 0x04800560
EPS306E5_U3_napaka_omog | DIGITAL | IOD_EPS306_disk | D10 | [6 empty] | 6157 | 1 | 0x04800570
EPS306KLIMA_SPLIT1_napaka_omog | DIGITAL | IOD_EPS306_disk | D11 | [6 empty] | 6157 | 1 | 0x04800580
EPS306KLIMA_SPLIT2_napaka_omog | DIGITAL | IOD_EPS306_disk | D12 | [6 empty] | 6157 | 1 | 0x04800590
EPS306NapakaTSTempTIA3_omog | DIGITAL | IOD_EPS306_disk | D13 | [6 empty] | 6157 | 1 | 0x048005a0
EPS306napaka_kom_panel_omog | DIGITAL | IOD_EPS306_disk | D14 | [6 empty] | 6157 | 1 | 0x048005b0
EPS306NapakaSenzorVlagaHIA1_omog | DIGITAL | IOD_EPS306_disk | D15 | [6 empty] | 6157 | 1 | 0x048005c0
EPS306NapakaSenzorVlagaHIA2_omog | DIGITAL | IOD_EPS306_disk | D16 | [6 empty] | 6157 | 1 | 0x048005d0
EPS306NapakaTSTempTIA1_omog | DIGITAL | IOD_EPS306_disk | D17 | [6 empty] | 6157 | 1 | 0x048005e0
EPS306NapakaTSTempTIA2_omog | DIGITAL | IOD_EPS306_disk | D18 | [6 empty] | 6157 | 1 | 0x048005f0
EPS306razlitje_vode_LAH1_omog | DIGITAL | IOD_EPS306_disk | D19 | [6 empty] | 6157 | 1 | 0x04800600
EPS306razlitje_vode_LAH2_omog | DIGITAL | IOD_EPS306_disk | D20 | [6 empty] | 6157 | 1 | 0x04800610
EPS306ups_alarm_omog | DIGITAL | IOD_EPS306_disk | D21 | [6 empty] | 6157 | 1 | 0x04800620
EPS306E5_F1_delovanje_omog | DIGITAL | IOD_EPS306_disk | D22 | [6 empty] | 6157 | 1 | 0x04800630
EPS306E5_F2_delovanje_omog | DIGITAL | IOD_EPS306_disk | D23 | [6 empty] | 6157 | 1 | 0x04800640
EPS306E5_F3_delovanje_omog | DIGITAL | IOD_EPS306_disk | D24 | [6 empty] | 6157 | 1 | 0x04800650
EPS306E5_U1_delovanje_omog | DIGITAL | IOD_EPS306_disk | D25 | [6 empty] | 6157 | 1 | 0x04800660
EPS306E5_U2_delovanje_omog | DIGITAL | IOD_EPS306_disk | D26 | [6 empty] | 6157 | 1 | 0x04800670
EPS306E5_U3_delovanje_omog | DIGITAL | IOD_EPS306_disk | D27 | [6 empty] | 6157 | 1 | 0x04800680
EPS306KLIMA_SPLIT1_delovanje_omog | DIGITAL | IOD_EPS306_disk | D28 | [6 empty] | 6157 | 1 | 0x04800690
EPS306NapakaSenzorVlagaHIA3_omog | DIGITAL | IOD_EPS306_disk | D29 | [6 empty] | 6157 | 1 | 0x048006a0
EPS306SlabaBaterijaPLC_omog | DIGITAL | IOD_EPS306_disk | D30 | [6 empty] | 6157 | 1 | 0x048006b0
EPS306ups_baterijski_nac_omog | DIGITAL | IOD_EPS306_disk | D31 | [6 empty] | 6157 | 1 | 0x048006c0
EPS306ups_polnjenje_omog | DIGITAL | IOD_EPS306_disk | D32 | [6 empty] | 6157 | 1 | 0x048006d0
EPS306napaka_kom_krm_omogoci | DIGITAL | IOD_EPS306_disk | D33 | [6 empty] | 6157 | 1 | 0x048006e0
AEP306_omogoci_sms | DIGITAL | IOD_EPS306_disk | D34[50] | [6 empty] | 6157 | 1 | 0x048006f0
BEP306_omogoci_sms | DIGITAL | IOD_EPS306_disk | D84[50] | [6 empty] | 6157 | 1 | 0x04800700
CEP306_omogoci_sms | DIGITAL | IOD_EPS306_disk | D134[50] | [6 empty] | 6157 | 1 | 0x04800710
DEP306_omogoci_sms | DIGITAL | IOD_EPS306_disk | D184[50] | [6 empty] | 6157 | 1 | 0x04800720
EEP306_omogoci_sms | DIGITAL | IOD_EPS306_disk | D234[50] | [6 empty] | 6157 | 1 | 0x04800730
FEP306_omogoci_sms | DIGITAL | IOD_EPS306_disk | D284[50] | [6 empty] | 6157 | 1 | 0x04800740
EPS306KLIMA_SPLIT2_delovanje_omog | DIGITAL | IOD_EPS306_disk | D335 | [8 empty] | 0x04800750
EPS306VentilatorjiCybroI_ERR_Vent1_omog | DIGITAL | IOD_EPS306_disk | D336 | [8 empty] | 0x04800760
EPS306VentilatorjiCybroI_ERR_Vent2_omog | DIGITAL | IOD_EPS306_disk | D337 | [8 empty] | 0x04800770
EPS306VentilatorjiCybroI_ERR_Vent3_omog | DIGITAL | IOD_EPS306_disk | D338 | [8 empty] | 0x04800780
EPS306VentilatorjiNapaka_omog | DIGITAL | IOD_EPS306_disk | D339 | [8 empty] | 0x04800790
EPS306VentilatorjiCybroAlarm_lucka_omog | DIGITAL | IOD_EPS306_disk | D340 | [8 empty] | 0x048007a0
EPS306TIA1_previs_temp_omog | DIGITAL | IOD_EPS306_disk | D341 | [8 empty] | 0x048007b0
EPS306TIA2_previs_temp_omog | DIGITAL | IOD_EPS306_disk | D342 | [8 empty] | 0x048007c0
EPS306TIA3_previs_temp_omog | DIGITAL | IOD_EPS306_disk | D343 | [8 empty] | 0x048007d0
EPS306SetDateTimeError_omog | DIGITAL | IOD_EPS306_disk | D344 | [8 empty] | 0x048007e0
EPS306VentilatorjiCybroSAvtomatsko_Vent1_omog | DIGITAL | IOD_EPS306_disk | D345 | [8 empty] | 0x048007f0
EPS306VentilatorjiCybroSAvtomatsko_Vent2_omog | DIGITAL | IOD_EPS306_disk | D346 | [8 empty] | 0x04800800
EPS306VentilatorjiCybroSAvtomatsko_Vent3_omog | DIGITAL | IOD_EPS306_disk | D347 | [8 empty] | 0x04800810
EPS306VentilatorjiCybroSRocno_Vent1_omog | DIGITAL | IOD_EPS306_disk | D348 | [8 empty] | 0x04800820
EPS306VentilatorjiCybroSRocno_Vent2_omog | DIGITAL | IOD_EPS306_disk | D349 | [8 empty] | 0x04800830
EPS306VentilatorjiCybroSRocno_Vent3_omog | DIGITAL | IOD_EPS306_disk | D350 | [8 empty] | 0x04800840
EPS306ErrComPort2_omog | DIGITAL | IOD_EPS306_disk | D351 | [8 empty] | 0x04800850
EPS306ErrComCybro_omog | DIGITAL | IOD_EPS306_disk | D352 | [8 empty] | 0x04800860
EPS306UserLoggedIn_mem | DIGITAL | IOD_EPS306_mem | D353 | [8 empty] | 0x04800870
neEPS306E5_F1_delovanje_omog | DIGITAL | IOD_EPS306_disk | D354 | [8 empty] | 0x04800880
neEPS306E5_F2_delovanje_omog | DIGITAL | IOD_EPS306_mem | D355 | [8 empty] | 0x04800890
neEPS306E5_F3_delovanje_omog | DIGITAL | IOD_EPS306_disk | D356 | [8 empty] | 0x048008a0
neEPS306E5_Q0_vkljuceno_omog | DIGITAL | IOD_EPS306_mem | D357 | [8 empty] | 0x048008b0
EPS306E5_Q0_vkljuceno_omog | DIGITAL | IOD_EPS306_disk | D358 | [8 empty] | 0x048008c0
EPS306napaka_kom_scada2 | DIGITAL | IOD_EPS306 | EPS306:.napaka_kom_scada2 | [8 empty] | 0x048008d0
EPS306ComSCADA2 | DIGITAL | IOD_EPS306 | EPS306:.ComSCADA2 | [8 empty] | 0x048008e0
EPS306napaka_kom_krm_omogoci2 | DIGITAL | IOD_EPS306_disk | D361 | [8 empty] | 0x048008f0
EPS306Server_A_Izpad | DIGITAL | IOD_EPS306_disk | D362 | [8 empty] | 0x04800900
EPS306Server_B_Izpad | DIGITAL | IOD_EPS306_disk | D363 | [8 empty] | 0x04800910
EPS306ComSCADA_stevec3 | INT | IOD_EPS306_mem | I366 | [8 empty] | 0x04800920
EPS306ComSCADA_stevec | INT | IOD_EPS306_mem | I368 | [8 empty] | 0x04800921
EPS306ComSCADA3 | DIGITAL | IOD_EPS306 | EPS306:.ComSCADA3 | [8 empty] | 0x04800930
EPS306kom_nast_cas_izpada | INT | IOD_EPS306 | EPS306:.kom_nast_cas_izpada | [8 empty] | 0x04800940

## variable_1
EPS306Alarm_E5M | DIGITAL | IOD_EPS306 | EPS306:.Alarm_E5M
EPS306ComSCADA | DIGITAL | IOD_EPS306 | EPS306:.ComSCADA
EPS306ComSCADA1 | DIGITAL | IOD_EPS306 | EPS306:.ComSCADA1
EPS306DateTimeDan | INT | IOD_EPS306 | EPS306:.DateTime.Dan | BYTE
EPS306DateTimeLeto | INT | IOD_EPS306 | EPS306:.DateTime.Leto | BYTE
EPS306DateTimeLeto2 | INT | IOD_EPS306 | EPS306:.DateTime.Leto2
EPS306DateTimeMesec | INT | IOD_EPS306 | EPS306:.DateTime.Mesec | BYTE
EPS306DateTimeMinuta | INT | IOD_EPS306 | EPS306:.DateTime.Minuta | BYTE
EPS306DateTimeSekunda | INT | IOD_EPS306 | EPS306:.DateTime.Sekunda | BYTE
EPS306DateTimeUra | INT | IOD_EPS306 | EPS306:.DateTime.Ura | BYTE
EPS306E5_F1_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_F1_delovanje
EPS306E5_F1_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_F1_napaka
EPS306E5_F2_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_F2_delovanje
EPS306E5_F2_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_F2_napaka
EPS306E5_F3_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_F3_delovanje
EPS306E5_F3_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_F3_napaka
EPS306E5_Q0_vkljuceno | DIGITAL | IOD_EPS306 | EPS306:.E5_Q0_vkljuceno
EPS306E5_U1_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_U1_delovanje
EPS306E5_U1_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_U1_napaka
EPS306E5_U2_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_U2_delovanje
EPS306E5_U2_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_U2_napaka
EPS306E5_U3_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_U3_delovanje
EPS306E5_U3_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_U3_napaka
EPS306ErrComCybro | DIGITAL | IOD_EPS306 | EPS306:.ErrComCybro
EPS306ErrComPort2 | DIGITAL | IOD_EPS306 | EPS306:.ErrComPort2
EPS306HIA1_vlaga_s | INT | IOD_EPS306 | EPS306:.HIA1_vlaga_s
EPS306HIA2_vlaga_s | INT | IOD_EPS306 | EPS306:.HIA2_vlaga_s
EPS306HIA3_vlaga_s | INT | IOD_EPS306 | EPS306:.HIA3_vlaga_s
EPS306KLIMA_SPLIT1_delovanje | DIGITAL | IOD_EPS306 | EPS306:.KLIMA_SPLIT1_delovanje
EPS306KLIMA_SPLIT1_napaka | DIGITAL | IOD_EPS306 | EPS306:.KLIMA_SPLIT1_napaka
EPS306KLIMA_SPLIT2_delovanje | DIGITAL | IOD_EPS306 | EPS306:.KLIMA_SPLIT2_delovanje
EPS306KLIMA_SPLIT2_napaka | DIGITAL | IOD_EPS306 | EPS306:.KLIMA_SPLIT2_napaka
EPS306KomunikacijaErr | DIGITAL | IOD_EPS306 | EPS306:.KomunikacijaErr
EPS306N_E5_F1_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_F1_napaka
EPS306N_E5_F2_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_F2_napaka
EPS306N_E5_F3_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_F3_napaka
EPS306N_E5_U1_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_U1_napaka
EPS306N_E5_U2_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_U2_napaka
EPS306N_E5_U3_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_U3_napaka
EPS306napaka_kom_panel | DIGITAL | IOD_EPS306 | EPS306:.napaka_kom_panel
EPS306napaka_kom_scada | DIGITAL | IOD_EPS306 | EPS306:.napaka_kom_scada
EPS306NapakaSenzorSkupno | DIGITAL | IOD_EPS306 | EPS306:.NapakaSenzorSkupno
EPS306NapakaSenzorVlagaHIA1 | DIGITAL | IOD_EPS306 | EPS306:.NapakaSenzorVlagaHIA1
EPS306NapakaSenzorVlagaHIA2 | DIGITAL | IOD_EPS306 | EPS306:.NapakaSenzorVlagaHIA2
EPS306NapakaSenzorVlagaHIA3 | DIGITAL | IOD_EPS306 | EPS306:.NapakaSenzorVlagaHIA3
EPS306NapakaTSTempTIA1 | DIGITAL | IOD_EPS306 | EPS306:.NapakaTSTempTIA1
EPS306NapakaTSTempTIA2 | DIGITAL | IOD_EPS306 | EPS306:.NapakaTSTempTIA2
EPS306NapakaTSTempTIA3 | DIGITAL | IOD_EPS306 | EPS306:.NapakaTSTempTIA3
EPS306PrevisokaTemp | DIGITAL | IOD_EPS306 | EPS306:.PrevisokaTemp
EPS306razlitje_vode_LAH1 | DIGITAL | IOD_EPS306 | EPS306:.razlitje_vode_LAH1
EPS306razlitje_vode_LAH2 | DIGITAL | IOD_EPS306 | EPS306:.razlitje_vode_LAH2
EPS306RezimVent1 | INT | IOD_EPS306 | EPS306:.RezimVent1 | BYTE
EPS306RezimVent2 | INT | IOD_EPS306 | EPS306:.RezimVent2 | BYTE
EPS306RezimVent3 | INT | IOD_EPS306 | EPS306:.RezimVent3 | BYTE
EPS306SetDateTime | DIGITAL | IOD_EPS306 | EPS306:.SetDateTime
EPS306SetDateTimeDemand | DIGITAL | IOD_EPS306 | EPS306:.SetDateTimeDemand
EPS306SetDateTimeError | DIGITAL | IOD_EPS306 | EPS306:.SetDateTimeError
EPS306SetDateTimeFinished | DIGITAL | IOD_EPS306 | EPS306:.SetDateTimeFinished
EPS306SlabaBaterijaPLC | DIGITAL | IOD_EPS306 | EPS306:.SlabaBaterijaPLC
EPS306TIA1_alarm | INT | IOD_EPS306 | EPS306:.TIA1_alarm
EPS306TIA1_previs_temp | DIGITAL | IOD_EPS306 | EPS306:.TIA1_previs_temp
EPS306TIA1_temp_s | INT | IOD_EPS306 | EPS306:.TIA1_temp_s
EPS306TIA2_alarm | INT | IOD_EPS306 | EPS306:.TIA2_alarm
EPS306TIA2_previs_temp | DIGITAL | IOD_EPS306 | EPS306:.TIA2_previs_temp
EPS306TIA2_temp_s | INT | IOD_EPS306 | EPS306:.TIA2_temp_s
EPS306TIA3_alarm | INT | IOD_EPS306 | EPS306:.TIA3_alarm
EPS306TIA3_previs_temp | DIGITAL | IOD_EPS306 | EPS306:.TIA3_previs_temp
EPS306TIA3_temp_s | INT | IOD_EPS306 | EPS306:.TIA3_temp_s
EPS306ups_alarm | DIGITAL | IOD_EPS306 | EPS306:.ups_alarm
EPS306ups_baterijski_nac | DIGITAL | IOD_EPS306 | EPS306:.ups_baterijski_nac
EPS306ups_polnjenje | DIGITAL | IOD_EPS306 | EPS306:.ups_polnjenje
EPS306UserCurrentLevel | INT | IOD_EPS306 | EPS306:.UserCurrentLevel | BYTE
EPS306UserCurrentName | STRING | IOD_EPS306 | EPS306:.UserCurrentName
EPS306UserLoggedIn | DIGITAL | IOD_EPS306 | EPS306:.UserLoggedIn
EPS306VentilatorjiAlarm | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiAlarm
EPS306VentilatorjiCybroAlarm_lucka | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.Alarm_lucka
EPS306VentilatorjiCybroHisterezaTEMP_HI | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.HisterezaTEMP_HI
EPS306VentilatorjiCybroHisterezaTEMP_LO | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.HisterezaTEMP_LO
EPS306VentilatorjiCybroHisterezaVLAGA_HI | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.HisterezaVLAGA_HI
EPS306VentilatorjiCybroHisterezaVLAGA_LO | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.HisterezaVLAGA_LO
EPS306VentilatorjiCybroHitrost_Vent1_MAX | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.Hitrost_Vent1_MAX
EPS306VentilatorjiCybroHitrost_Vent1_MIN | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.Hitrost_Vent1_MIN
EPS306VentilatorjiCybroI_ERR_Vent1 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.I_ERR_Vent1
EPS306VentilatorjiCybroI_ERR_Vent2 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.I_ERR_Vent2
EPS306VentilatorjiCybroI_ERR_Vent3 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.I_ERR_Vent3
EPS306VentilatorjiCybroO_Hitrost_Vent1 | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.O_Hitrost_Vent1
EPS306VentilatorjiCybroO_Hitrost_Vent2 | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.O_Hitrost_Vent2
EPS306VentilatorjiCybroO_Hitrost_Vent3 | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.O_Hitrost_Vent3
EPS306VentilatorjiCybroSAvtomatsko_Vent1 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SAvtomatsko_Vent1
EPS306VentilatorjiCybroSAvtomatsko_Vent2 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SAvtomatsko_Vent2
EPS306VentilatorjiCybroSAvtomatsko_Vent3 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SAvtomatsko_Vent3
EPS306VentilatorjiCybroSRocno_Vent1 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SRocno_Vent1
EPS306VentilatorjiCybroSRocno_Vent2 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SRocno_Vent2
EPS306VentilatorjiCybroSRocno_Vent3 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SRocno_Vent3
EPS306VentilatorjiCybroTempSKUPNA | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.TempSKUPNA
EPS306VentilatorjiCybroVlagaSKUPNA | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.VlagaSKUPNA
EPS306VentilatorjiNapaka | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiNapaka
EPS306XVH_AlarmOn | DIGITAL | IOD_EPS306 | EPS306:.XVH_AlarmOn
EPS306XVH_KlimaSplitStatus1 | INT | IOD_EPS306 | EPS306:.XVH_KlimaSplitStatus[1] | BYTE
EPS306XVH_KlimaSplitStatus2 | INT | IOD_EPS306 | EPS306:.XVH_KlimaSplitStatus[2] | BYTE
EPS306XVH_KonvekorErr | DIGITAL | IOD_EPS306 | EPS306:.XVH_KonvekorErr
EPS306XVH_UPSstatus | INT | IOD_EPS306 | EPS306:.XVH_UPSstatus | BYTE
EPS306napaka_kom_scada2 | DIGITAL | IOD_EPS306 | EPS306:.napaka_kom_scada2
EPS306ComSCADA2 | DIGITAL | IOD_EPS306 | EPS306:.ComSCADA2
EPS306ComSCADA3 | DIGITAL | IOD_EPS306 | EPS306:.ComSCADA3
EPS306kom_nast_cas_izpada | INT | IOD_EPS306 | EPS306:.kom_nast_cas_izpada

## variable_2
EPS306Alarm_E5M | DIGITAL | IOD_EPS306 | EPS306:.Alarm_E5M
EPS306ComSCADA | DIGITAL | IOD_EPS306 | EPS306:.ComSCADA
EPS306ComSCADA1 | DIGITAL | IOD_EPS306 | EPS306:.ComSCADA1
EPS306E5_F1_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_F1_delovanje
EPS306E5_F1_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_F1_napaka
EPS306E5_F2_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_F2_delovanje
EPS306E5_F2_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_F2_napaka
EPS306E5_F3_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_F3_delovanje
EPS306E5_F3_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_F3_napaka
EPS306E5_Q0_vkljuceno | DIGITAL | IOD_EPS306 | EPS306:.E5_Q0_vkljuceno
EPS306E5_U1_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_U1_delovanje
EPS306E5_U1_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_U1_napaka
EPS306E5_U2_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_U2_delovanje
EPS306E5_U2_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_U2_napaka
EPS306E5_U3_delovanje | DIGITAL | IOD_EPS306 | EPS306:.E5_U3_delovanje
EPS306E5_U3_napaka | DIGITAL | IOD_EPS306 | EPS306:.E5_U3_napaka
EPS306ErrComCybro | DIGITAL | IOD_EPS306 | EPS306:.ErrComCybro
EPS306ErrComPort2 | DIGITAL | IOD_EPS306 | EPS306:.ErrComPort2
EPS306KLIMA_SPLIT1_delovanje | DIGITAL | IOD_EPS306 | EPS306:.KLIMA_SPLIT1_delovanje
EPS306KLIMA_SPLIT1_napaka | DIGITAL | IOD_EPS306 | EPS306:.KLIMA_SPLIT1_napaka
EPS306KLIMA_SPLIT2_delovanje | DIGITAL | IOD_EPS306 | EPS306:.KLIMA_SPLIT2_delovanje
EPS306KLIMA_SPLIT2_napaka | DIGITAL | IOD_EPS306 | EPS306:.KLIMA_SPLIT2_napaka
EPS306KomunikacijaErr | DIGITAL | IOD_EPS306 | EPS306:.KomunikacijaErr
EPS306N_E5_F1_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_F1_napaka
EPS306N_E5_F2_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_F2_napaka
EPS306N_E5_F3_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_F3_napaka
EPS306N_E5_U1_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_U1_napaka
EPS306N_E5_U2_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_U2_napaka
EPS306N_E5_U3_napaka | DIGITAL | IOD_EPS306 | EPS306:.N_E5_U3_napaka
EPS306napaka_kom_panel | DIGITAL | IOD_EPS306 | EPS306:.napaka_kom_panel
EPS306napaka_kom_scada | DIGITAL | IOD_EPS306 | EPS306:.napaka_kom_scada
EPS306NapakaSenzorSkupno | DIGITAL | IOD_EPS306 | EPS306:.NapakaSenzorSkupno
EPS306NapakaSenzorVlagaHIA1 | DIGITAL | IOD_EPS306 | EPS306:.NapakaSenzorVlagaHIA1
EPS306NapakaSenzorVlagaHIA2 | DIGITAL | IOD_EPS306 | EPS306:.NapakaSenzorVlagaHIA2
EPS306NapakaSenzorVlagaHIA3 | DIGITAL | IOD_EPS306 | EPS306:.NapakaSenzorVlagaHIA3
EPS306NapakaTSTempTIA1 | DIGITAL | IOD_EPS306 | EPS306:.NapakaTSTempTIA1
EPS306NapakaTSTempTIA2 | DIGITAL | IOD_EPS306 | EPS306:.NapakaTSTempTIA2
EPS306NapakaTSTempTIA3 | DIGITAL | IOD_EPS306 | EPS306:.NapakaTSTempTIA3
EPS306PrevisokaTemp | DIGITAL | IOD_EPS306 | EPS306:.PrevisokaTemp
EPS306razlitje_vode_LAH1 | DIGITAL | IOD_EPS306 | EPS306:.razlitje_vode_LAH1
EPS306razlitje_vode_LAH2 | DIGITAL | IOD_EPS306 | EPS306:.razlitje_vode_LAH2
EPS306SetDateTime | DIGITAL | IOD_EPS306 | EPS306:.SetDateTime
EPS306SetDateTimeDemand | DIGITAL | IOD_EPS306 | EPS306:.SetDateTimeDemand
EPS306SetDateTimeError | DIGITAL | IOD_EPS306 | EPS306:.SetDateTimeError
EPS306SetDateTimeFinished | DIGITAL | IOD_EPS306 | EPS306:.SetDateTimeFinished
EPS306SlabaBaterijaPLC | DIGITAL | IOD_EPS306 | EPS306:.SlabaBaterijaPLC
EPS306TIA1_previs_temp | DIGITAL | IOD_EPS306 | EPS306:.TIA1_previs_temp
EPS306TIA2_previs_temp | DIGITAL | IOD_EPS306 | EPS306:.TIA2_previs_temp
EPS306TIA3_previs_temp | DIGITAL | IOD_EPS306 | EPS306:.TIA3_previs_temp
EPS306ups_alarm | DIGITAL | IOD_EPS306 | EPS306:.ups_alarm
EPS306ups_baterijski_nac | DIGITAL | IOD_EPS306 | EPS306:.ups_baterijski_nac
EPS306ups_polnjenje | DIGITAL | IOD_EPS306 | EPS306:.ups_polnjenje
EPS306UserLoggedIn | DIGITAL | IOD_EPS306 | EPS306:.UserLoggedIn
EPS306VentilatorjiAlarm | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiAlarm
EPS306VentilatorjiCybroI_ERR_Vent1 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.I_ERR_Vent1
EPS306VentilatorjiCybroI_ERR_Vent2 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.I_ERR_Vent2
EPS306VentilatorjiCybroI_ERR_Vent3 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.I_ERR_Vent3
EPS306VentilatorjiCybroSAvtomatsko_Vent1 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SAvtomatsko_Vent1
EPS306VentilatorjiCybroSAvtomatsko_Vent2 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SAvtomatsko_Vent2
EPS306VentilatorjiCybroSAvtomatsko_Vent3 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SAvtomatsko_Vent3
EPS306VentilatorjiCybroSRocno_Vent1 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SRocno_Vent1
EPS306VentilatorjiCybroSRocno_Vent2 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SRocno_Vent2
EPS306VentilatorjiCybroSRocno_Vent3 | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiCybro.SRocno_Vent3
EPS306VentilatorjiNapaka | DIGITAL | IOD_EPS306 | EPS306:.VentilatorjiNapaka
EPS306XVH_AlarmOn | DIGITAL | IOD_EPS306 | EPS306:.XVH_AlarmOn
EPS306XVH_KonvekorErr | DIGITAL | IOD_EPS306 | EPS306:.XVH_KonvekorErr
EPS306napaka_kom_scada2 | DIGITAL | IOD_EPS306 | EPS306:.napaka_kom_scada2
EPS306ComSCADA2 | DIGITAL | IOD_EPS306 | EPS306:.ComSCADA2
EPS306ComSCADA3 | DIGITAL | IOD_EPS306 | EPS306:.ComSCADA3
EPS306DateTimeDan | INT | IOD_EPS306 | EPS306:.DateTime.Dan | BYTE
EPS306DateTimeLeto | INT | IOD_EPS306 | EPS306:.DateTime.Leto | BYTE
EPS306DateTimeLeto2 | INT | IOD_EPS306 | EPS306:.DateTime.Leto2
EPS306DateTimeMesec | INT | IOD_EPS306 | EPS306:.DateTime.Mesec | BYTE
EPS306DateTimeMinuta | INT | IOD_EPS306 | EPS306:.DateTime.Minuta | BYTE
EPS306DateTimeSekunda | INT | IOD_EPS306 | EPS306:.DateTime.Sekunda | BYTE
EPS306DateTimeUra | INT | IOD_EPS306 | EPS306:.DateTime.Ura | BYTE
EPS306HIA1_vlaga_s | INT | IOD_EPS306 | EPS306:.HIA1_vlaga_s
EPS306HIA2_vlaga_s | INT | IOD_EPS306 | EPS306:.HIA2_vlaga_s
EPS306HIA3_vlaga_s | INT | IOD_EPS306 | EPS306:.HIA3_vlaga_s
EPS306RezimVent1 | INT | IOD_EPS306 | EPS306:.RezimVent1 | BYTE
EPS306RezimVent2 | INT | IOD_EPS306 | EPS306:.RezimVent2 | BYTE
EPS306RezimVent3 | INT | IOD_EPS306 | EPS306:.RezimVent3 | BYTE
EPS306TIA1_alarm | INT | IOD_EPS306 | EPS306:.TIA1_alarm
EPS306TIA1_temp_s | INT | IOD_EPS306 | EPS306:.TIA1_temp_s
EPS306TIA2_alarm | INT | IOD_EPS306 | EPS306:.TIA2_alarm
EPS306TIA2_temp_s | INT | IOD_EPS306 | EPS306:.TIA2_temp_s
EPS306TIA3_alarm | INT | IOD_EPS306 | EPS306:.TIA3_alarm
EPS306TIA3_temp_s | INT | IOD_EPS306 | EPS306:.TIA3_temp_s
EPS306UserCurrentLevel | INT | IOD_EPS306 | EPS306:.UserCurrentLevel | BYTE
EPS306VentilatorjiCybroAlarm_lucka | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.Alarm_lucka
EPS306VentilatorjiCybroHisterezaTEMP_HI | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.HisterezaTEMP_HI
EPS306VentilatorjiCybroHisterezaTEMP_LO | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.HisterezaTEMP_LO
EPS306VentilatorjiCybroHisterezaVLAGA_HI | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.HisterezaVLAGA_HI
EPS306VentilatorjiCybroHisterezaVLAGA_LO | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.HisterezaVLAGA_LO
EPS306VentilatorjiCybroHitrost_Vent1_MAX | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.Hitrost_Vent1_MAX
EPS306VentilatorjiCybroHitrost_Vent1_MIN | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.Hitrost_Vent1_MIN
EPS306VentilatorjiCybroO_Hitrost_Vent1 | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.O_Hitrost_Vent1
EPS306VentilatorjiCybroO_Hitrost_Vent2 | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.O_Hitrost_Vent2
EPS306VentilatorjiCybroO_Hitrost_Vent3 | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.O_Hitrost_Vent3
EPS306VentilatorjiCybroTempSKUPNA | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.TempSKUPNA
EPS306VentilatorjiCybroVlagaSKUPNA | INT | IOD_EPS306 | EPS306:.VentilatorjiCybro.VlagaSKUPNA
EPS306XVH_KlimaSplitStatus1 | INT | IOD_EPS306 | EPS306:.XVH_KlimaSplitStatus[1] | BYTE
EPS306XVH_KlimaSplitStatus2 | INT | IOD_EPS306 | EPS306:.XVH_KlimaSplitStatus[2] | BYTE
EPS306XVH_UPSstatus | INT | IOD_EPS306 | EPS306:.XVH_UPSstatus | BYTE
EPS306kom_nast_cas_izpada | INT | IOD_EPS306 | EPS306:.kom_nast_cas_izpada
EPS306UserCurrentName | STRING | IOD_EPS306 | EPS306:.UserCurrentName

## variable_3
EPS306Alarm_E5M | DIGITAL | IOD_EPS306_TCP | 1 | 00001 | Alarm_E5M
EPS306ComSCADA | DIGITAL | IOD_EPS306_TCP | 2 | 00002 | ComSCADA
EPS306ComSCADA1 | DIGITAL | IOD_EPS306_TCP | 3 | 00003 | ComSCADA1
EPS306E5_F1_delovanje | DIGITAL | IOD_EPS306_TCP | 4 | 00004 | E5_F1_delovanje
EPS306E5_F1_napaka | DIGITAL | IOD_EPS306_TCP | 5 | 00005 | E5_F1_napaka
EPS306E5_F2_delovanje | DIGITAL | IOD_EPS306_TCP | 6 | 00006 | E5_F2_delovanje
EPS306E5_F2_napaka | DIGITAL | IOD_EPS306_TCP | 7 | 00007 | E5_F2_napaka
EPS306E5_F3_delovanje | DIGITAL | IOD_EPS306_TCP | 8 | 00008 | E5_F3_delovanje
EPS306E5_F3_napaka | DIGITAL | IOD_EPS306_TCP | 9 | 00009 | E5_F3_napaka
EPS306E5_Q0_vkljuceno | DIGITAL | IOD_EPS306_TCP | 10 | 00010 | E5_Q0_vkljuceno
EPS306E5_U1_delovanje | DIGITAL | IOD_EPS306_TCP | 11 | 00011 | E5_U1_delovanje
EPS306E5_U1_napaka | DIGITAL | IOD_EPS306_TCP | 12 | 00012 | E5_U1_napaka
EPS306E5_U2_delovanje | DIGITAL | IOD_EPS306_TCP | 13 | 00013 | E5_U2_delovanje
EPS306E5_U2_napaka | DIGITAL | IOD_EPS306_TCP | 14 | 00014 | E5_U2_napaka
EPS306E5_U3_delovanje | DIGITAL | IOD_EPS306_TCP | 15 | 00015 | E5_U3_delovanje
EPS306E5_U3_napaka | DIGITAL | IOD_EPS306_TCP | 16 | 00016 | E5_U3_napaka
EPS306ErrComCybro | DIGITAL | IOD_EPS306_TCP | 17 | 00017 | ErrComCybro
EPS306ErrComPort2 | DIGITAL | IOD_EPS306_TCP | 18 | 00018 | ErrComPort2
EPS306KLIMA_SPLIT1_delovanje | DIGITAL | IOD_EPS306_TCP | 19 | 00019 | KLIMA_SPLIT1_delovanje
EPS306KLIMA_SPLIT1_napaka | DIGITAL | IOD_EPS306_TCP | 20 | 00020 | KLIMA_SPLIT1_napaka
EPS306KLIMA_SPLIT2_delovanje | DIGITAL | IOD_EPS306_TCP | 21 | 00021 | KLIMA_SPLIT2_delovanje
EPS306KLIMA_SPLIT2_napaka | DIGITAL | IOD_EPS306_TCP | 22 | 00022 | KLIMA_SPLIT2_napaka
EPS306KomunikacijaErr | DIGITAL | IOD_EPS306_TCP | 23 | 00023 | KomunikacijaErr
EPS306N_E5_F1_napaka | DIGITAL | IOD_EPS306_TCP | 24 | 00024 | N_E5_F1_napaka
EPS306N_E5_F2_napaka | DIGITAL | IOD_EPS306_TCP | 25 | 00025 | N_E5_F2_napaka
EPS306N_E5_F3_napaka | DIGITAL | IOD_EPS306_TCP | 26 | 00026 | N_E5_F3_napaka
EPS306N_E5_U1_napaka | DIGITAL | IOD_EPS306_TCP | 27 | 00027 | N_E5_U1_napaka
EPS306N_E5_U2_napaka | DIGITAL | IOD_EPS306_TCP | 28 | 00028 | N_E5_U2_napaka
EPS306N_E5_U3_napaka | DIGITAL | IOD_EPS306_TCP | 29 | 00029 | N_E5_U3_napaka
EPS306napaka_kom_panel | DIGITAL | IOD_EPS306_TCP | 30 | 00030 | napaka_kom_panel
EPS306napaka_kom_scada | DIGITAL | IOD_EPS306_TCP | 31 | 00031 | napaka_kom_scada
EPS306NapakaSenzorSkupno | DIGITAL | IOD_EPS306_TCP | 32 | 00032 | NapakaSenzorSkupno
EPS306NapakaSenzorVlagaHIA1 | DIGITAL | IOD_EPS306_TCP | 33 | 00033 | NapakaSenzorVlagaHIA1
EPS306NapakaSenzorVlagaHIA2 | DIGITAL | IOD_EPS306_TCP | 34 | 00034 | NapakaSenzorVlagaHIA2
EPS306NapakaSenzorVlagaHIA3 | DIGITAL | IOD_EPS306_TCP | 35 | 00035 | NapakaSenzorVlagaHIA3
EPS306NapakaTSTempTIA1 | DIGITAL | IOD_EPS306_TCP | 36 | 00036 | NapakaTSTempTIA1
EPS306NapakaTSTempTIA2 | DIGITAL | IOD_EPS306_TCP | 37 | 00037 | NapakaTSTempTIA2
EPS306NapakaTSTempTIA3 | DIGITAL | IOD_EPS306_TCP | 38 | 00038 | NapakaTSTempTIA3
EPS306PrevisokaTemp | DIGITAL | IOD_EPS306_TCP | 39 | 00039 | PrevisokaTemp
EPS306razlitje_vode_LAH1 | DIGITAL | IOD_EPS306_TCP | 40 | 00040 | razlitje_vode_LAH1
EPS306razlitje_vode_LAH2 | DIGITAL | IOD_EPS306_TCP | 41 | 00041 | razlitje_vode_LAH2
EPS306SetDateTime | DIGITAL | IOD_EPS306_TCP | 42 | 00042 | SetDateTime
EPS306SetDateTimeDemand | DIGITAL | IOD_EPS306_TCP | 43 | 00043 | SetDateTimeDemand
EPS306SetDateTimeError | DIGITAL | IOD_EPS306_TCP | 44 | 00044 | SetDateTimeError
EPS306SetDateTimeFinished | DIGITAL | IOD_EPS306_TCP | 45 | 00045 | SetDateTimeFinished
EPS306SlabaBaterijaPLC | DIGITAL | IOD_EPS306_TCP | 46 | 00046 | SlabaBaterijaPLC
EPS306TIA1_previs_temp | DIGITAL | IOD_EPS306_TCP | 47 | 00047 | TIA1_previs_temp
EPS306TIA2_previs_temp | DIGITAL | IOD_EPS306_TCP | 48 | 00048 | TIA2_previs_temp
EPS306TIA3_previs_temp | DIGITAL | IOD_EPS306_TCP | 49 | 00049 | TIA3_previs_temp
EPS306ups_alarm | DIGITAL | IOD_EPS306_TCP | 50 | 00050 | ups_alarm
EPS306ups_baterijski_nac | DIGITAL | IOD_EPS306_TCP | 51 | 00051 | ups_baterijski_nac
EPS306ups_polnjenje | DIGITAL | IOD_EPS306_TCP | 52 | 00052 | ups_polnjenje
EPS306UserLoggedIn | DIGITAL | IOD_EPS306_TCP | 53 | 00053 | UserLoggedIn
EPS306VentilatorjiAlarm | DIGITAL | IOD_EPS306_TCP | 54 | 00054 | VentilatorjiAlarm
EPS306VentilatorjiCybroI_ERR_Vent1 | DIGITAL | IOD_EPS306_TCP | 55 | 00055 | VentilatorjiCybro.I_ERR_Vent1
EPS306VentilatorjiCybroI_ERR_Vent2 | DIGITAL | IOD_EPS306_TCP | 56 | 00056 | VentilatorjiCybro.I_ERR_Vent2
EPS306VentilatorjiCybroI_ERR_Vent3 | DIGITAL | IOD_EPS306_TCP | 57 | 00057 | VentilatorjiCybro.I_ERR_Vent3
EPS306VentilatorjiCybroSAvtomatsko_Vent1 | DIGITAL | IOD_EPS306_TCP | 58 | 00058 | VentilatorjiCybro.SAvtomatsko_Vent1
EPS306VentilatorjiCybroSAvtomatsko_Vent2 | DIGITAL | IOD_EPS306_TCP | 59 | 00059 | VentilatorjiCybro.SAvtomatsko_Vent2
EPS306VentilatorjiCybroSAvtomatsko_Vent3 | DIGITAL | IOD_EPS306_TCP | 60 | 00060 | VentilatorjiCybro.SAvtomatsko_Vent3
EPS306VentilatorjiCybroSRocno_Vent1 | DIGITAL | IOD_EPS306_TCP | 61 | 00061 | VentilatorjiCybro.SRocno_Vent1
EPS306VentilatorjiCybroSRocno_Vent2 | DIGITAL | IOD_EPS306_TCP | 62 | 00062 | VentilatorjiCybro.SRocno_Vent2
EPS306VentilatorjiCybroSRocno_Vent3 | DIGITAL | IOD_EPS306_TCP | 63 | 00063 | VentilatorjiCybro.SRocno_Vent3
EPS306VentilatorjiNapaka | DIGITAL | IOD_EPS306_TCP | 64 | 00064 | VentilatorjiNapaka
EPS306XVH_AlarmOn | DIGITAL | IOD_EPS306_TCP | 65 | 00065 | XVH_AlarmOn
EPS306XVH_KonvekorErr | DIGITAL | IOD_EPS306_TCP | 66 | 00066 | XVH_KonvekorErr
EPS306napaka_kom_scada2 | DIGITAL | IOD_EPS306_TCP | 67 | 00067 | napaka_kom_scada2
EPS306ComSCADA2 | DIGITAL | IOD_EPS306_TCP | 68 | 00068 | ComSCADA2
EPS306ComSCADA3 | DIGITAL | IOD_EPS306_TCP | 69 | 00069 | ComSCADA3
EPS306DateTimeDan | INT | IOD_EPS306_TCP | 1 | 40001 | DateTime.Dan | BYTE
EPS306DateTimeLeto | INT | IOD_EPS306_TCP | 2 | 40002 | DateTime.Leto | BYTE
EPS306DateTimeLeto2 | INT | IOD_EPS306_TCP | 3 | 40003 | DateTime.Leto2
EPS306DateTimeMesec | INT | IOD_EPS306_TCP | 4 | 40004 | DateTime.Mesec | BYTE
EPS306DateTimeMinuta | INT | IOD_EPS306_TCP | 5 | 40005 | DateTime.Minuta | BYTE
EPS306DateTimeSekunda | INT | IOD_EPS306_TCP | 6 | 40006 | DateTime.Sekunda | BYTE
EPS306DateTimeUra | INT | IOD_EPS306_TCP | 7 | 40007 | DateTime.Ura | BYTE
EPS306HIA1_vlaga_s | INT | IOD_EPS306_TCP | 8 | 40008 | HIA1_vlaga_s
EPS306HIA2_vlaga_s | INT | IOD_EPS306_TCP | 9 | 40009 | HIA2_vlaga_s
EPS306HIA3_vlaga_s | INT | IOD_EPS306_TCP | 10 | 40010 | HIA3_vlaga_s
EPS306RezimVent1 | INT | IOD_EPS306_TCP | 11 | 40011 | RezimVent1 | BYTE
EPS306RezimVent2 | INT | IOD_EPS306_TCP | 12 | 40012 | RezimVent2 | BYTE
EPS306RezimVent3 | INT | IOD_EPS306_TCP | 13 | 40013 | RezimVent3 | BYTE
EPS306TIA1_alarm | INT | IOD_EPS306_TCP | 14 | 40014 | TIA1_alarm
EPS306TIA1_temp_s | INT | IOD_EPS306_TCP | 15 | 40015 | TIA1_temp_s
EPS306TIA2_alarm | INT | IOD_EPS306_TCP | 16 | 40016 | TIA2_alarm
EPS306TIA2_temp_s | INT | IOD_EPS306_TCP | 17 | 40017 | TIA2_temp_s
EPS306TIA3_alarm | INT | IOD_EPS306_TCP | 18 | 40018 | TIA3_alarm
EPS306TIA3_temp_s | INT | IOD_EPS306_TCP | 19 | 40019 | TIA3_temp_s
EPS306UserCurrentLevel | INT | IOD_EPS306_TCP | 20 | 40020 | UserCurrentLevel | BYTE
EPS306VentilatorjiCybroAlarm_lucka | INT | IOD_EPS306_TCP | 21 | 40021 | VentilatorjiCybro.Alarm_lucka
EPS306VentilatorjiCybroHisterezaTEMP_HI | INT | IOD_EPS306_TCP | 22 | 40022 | VentilatorjiCybro.HisterezaTEMP_HI
EPS306VentilatorjiCybroHisterezaTEMP_LO | INT | IOD_EPS306_TCP | 23 | 40023 | VentilatorjiCybro.HisterezaTEMP_LO
EPS306VentilatorjiCybroHisterezaVLAGA_HI | INT | IOD_EPS306_TCP | 24 | 40024 | VentilatorjiCybro.HisterezaVLAGA_HI
EPS306VentilatorjiCybroHisterezaVLAGA_LO | INT | IOD_EPS306_TCP | 25 | 40025 | VentilatorjiCybro.HisterezaVLAGA_LO
EPS306VentilatorjiCybroHitrost_Vent1_MAX | INT | IOD_EPS306_TCP | 26 | 40026 | VentilatorjiCybro.Hitrost_Vent1_MAX
EPS306VentilatorjiCybroHitrost_Vent1_MIN | INT | IOD_EPS306_TCP | 27 | 40027 | VentilatorjiCybro.Hitrost_Vent1_MIN
EPS306VentilatorjiCybroO_Hitrost_Vent1 | INT | IOD_EPS306_TCP | 28 | 40028 | VentilatorjiCybro.O_Hitrost_Vent1
EPS306VentilatorjiCybroO_Hitrost_Vent2 | INT | IOD_EPS306_TCP | 29 | 40029 | VentilatorjiCybro.O_Hitrost_Vent2
EPS306VentilatorjiCybroO_Hitrost_Vent3 | INT | IOD_EPS306_TCP | 30 | 40030 | VentilatorjiCybro.O_Hitrost_Vent3
EPS306VentilatorjiCybroTempSKUPNA | INT | IOD_EPS306_TCP | 31 | 40031 | VentilatorjiCybro.TempSKUPNA
EPS306VentilatorjiCybroVlagaSKUPNA | INT | IOD_EPS306_TCP | 32 | 40032 | VentilatorjiCybro.VlagaSKUPNA
EPS306XVH_KlimaSplitStatus1 | INT | IOD_EPS306_TCP | 33 | 40033 | XVH_KlimaSplitStatus[1] | BYTE
EPS306XVH_KlimaSplitStatus2 | INT | IOD_EPS306_TCP | 34 | 40034 | XVH_KlimaSplitStatus[2] | BYTE
EPS306XVH_UPSstatus | INT | IOD_EPS306_TCP | 35 | 40035 | XVH_UPSstatus | BYTE
EPS306kom_nast_cas_izpada | INT | IOD_EPS306_TCP | 36 | 40036 | kom_nast_cas_izpada
EPS306UserCurrentName | STRING | IOD_EPS306_TCP | 5001 | 45001[15] | UserCurrentName

## variable_new
EPS306Alarm_E5M | DIGITAL | IOD_EPS306_TCP | 00001
EPS306ComSCADA | DIGITAL | IOD_EPS306_TCP | 00002
EPS306ComSCADA1 | DIGITAL | IOD_EPS306_TCP | 00003
EPS306DateTimeDan | INT | IOD_EPS306_TCP | 40001
EPS306DateTimeLeto | INT | IOD_EPS306_TCP | 40002
EPS306DateTimeLeto2 | INT | IOD_EPS306_TCP | 40003
EPS306DateTimeMesec | INT | IOD_EPS306_TCP | 40004
EPS306DateTimeMinuta | INT | IOD_EPS306_TCP | 40005
EPS306DateTimeSekunda | INT | IOD_EPS306_TCP | 40006
EPS306DateTimeUra | INT | IOD_EPS306_TCP | 40007
EPS306E5_F1_delovanje | DIGITAL | IOD_EPS306_TCP | 00004
EPS306E5_F1_napaka | DIGITAL | IOD_EPS306_TCP | 00005
EPS306E5_F2_delovanje | DIGITAL | IOD_EPS306_TCP | 00006
EPS306E5_F2_napaka | DIGITAL | IOD_EPS306_TCP | 00007
EPS306E5_F3_delovanje | DIGITAL | IOD_EPS306_TCP | 00008
EPS306E5_F3_napaka | DIGITAL | IOD_EPS306_TCP | 00009
EPS306E5_Q0_vkljuceno | DIGITAL | IOD_EPS306_TCP | 00010
EPS306E5_U1_delovanje | DIGITAL | IOD_EPS306_TCP | 00011
EPS306E5_U1_napaka | DIGITAL | IOD_EPS306_TCP | 00012
EPS306E5_U2_delovanje | DIGITAL | IOD_EPS306_TCP | 00013
EPS306E5_U2_napaka | DIGITAL | IOD_EPS306_TCP | 00014
EPS306E5_U3_delovanje | DIGITAL | IOD_EPS306_TCP | 00015
EPS306E5_U3_napaka | DIGITAL | IOD_EPS306_TCP | 00016
EPS306ErrComCybro | DIGITAL | IOD_EPS306_TCP | 00017
EPS306ErrComPort2 | DIGITAL | IOD_EPS306_TCP | 00018
EPS306HIA1_vlaga_s | INT | IOD_EPS306_TCP | 40008 | 0 | 1000 | 0 | 100 | % | ##.#
EPS306HIA2_vlaga_s | INT | IOD_EPS306_TCP | 40009 | 0 | 1000 | 0 | 100 | % | ##.#
EPS306HIA3_vlaga_s | INT | IOD_EPS306_TCP | 40010 | 0 | 1000 | 0 | 100 | % | ##.#
EPS306KLIMA_SPLIT1_delovanje | DIGITAL | IOD_EPS306_TCP | 00019
EPS306KLIMA_SPLIT1_napaka | DIGITAL | IOD_EPS306_TCP | 00020
EPS306KLIMA_SPLIT2_delovanje | DIGITAL | IOD_EPS306_TCP | 00021
EPS306KLIMA_SPLIT2_napaka | DIGITAL | IOD_EPS306_TCP | 00022
EPS306KomunikacijaErr | DIGITAL | IOD_EPS306_TCP | 00023
EPS306N_E5_F1_napaka | DIGITAL | IOD_EPS306_TCP | 00024
EPS306N_E5_F2_napaka | DIGITAL | IOD_EPS306_TCP | 00025
EPS306N_E5_F3_napaka | DIGITAL | IOD_EPS306_TCP | 00026
EPS306N_E5_U1_napaka | DIGITAL | IOD_EPS306_TCP | 00027
EPS306N_E5_U2_napaka | DIGITAL | IOD_EPS306_TCP | 00028
EPS306N_E5_U3_napaka | DIGITAL | IOD_EPS306_TCP | 00029
EPS306napaka_kom_panel | DIGITAL | IOD_EPS306_TCP | 00030
EPS306napaka_kom_scada | DIGITAL | IOD_EPS306_TCP | 00031
EPS306NapakaSenzorSkupno | DIGITAL | IOD_EPS306_TCP | 00032
EPS306NapakaSenzorVlagaHIA1 | DIGITAL | IOD_EPS306_TCP | 00033
EPS306NapakaSenzorVlagaHIA2 | DIGITAL | IOD_EPS306_TCP | 00034
EPS306NapakaSenzorVlagaHIA3 | DIGITAL | IOD_EPS306_TCP | 00035
EPS306NapakaTSTempTIA1 | DIGITAL | IOD_EPS306_TCP | 00036
EPS306NapakaTSTempTIA2 | DIGITAL | IOD_EPS306_TCP | 00037
EPS306NapakaTSTempTIA3 | DIGITAL | IOD_EPS306_TCP | 00038
EPS306PrevisokaTemp | DIGITAL | IOD_EPS306_TCP | 00039
EPS306razlitje_vode_LAH1 | DIGITAL | IOD_EPS306_TCP | 00040
EPS306razlitje_vode_LAH2 | DIGITAL | IOD_EPS306_TCP | 00041
EPS306RezimVent1 | INT | IOD_EPS306_TCP | 40011
EPS306RezimVent2 | INT | IOD_EPS306_TCP | 40012
EPS306RezimVent3 | INT | IOD_EPS306_TCP | 40013
EPS306SetDateTime | DIGITAL | IOD_EPS306_TCP | 00042
EPS306SetDateTimeDemand | DIGITAL | IOD_EPS306_TCP | 00043
EPS306SetDateTimeError | DIGITAL | IOD_EPS306_TCP | 00044
EPS306SetDateTimeFinished | DIGITAL | IOD_EPS306_TCP | 00045
EPS306SlabaBaterijaPLC | DIGITAL | IOD_EPS306_TCP | 00046
EPS306TIA1_alarm | INT | IOD_EPS306_TCP | 40014 | 0 | 60 | 0 | 60 | řC | ##
EPS306TIA1_previs_temp | DIGITAL | IOD_EPS306_TCP | 00047
EPS306TIA1_temp_s | INT | IOD_EPS306_TCP | 40015 | 0 | 600 | 0 | 60 | řC | ##.#
EPS306TIA2_alarm | INT | IOD_EPS306_TCP | 40016 | 0 | 60 | 0 | 60 | řC | ##
EPS306TIA2_previs_temp | DIGITAL | IOD_EPS306_TCP | 00048
EPS306TIA2_temp_s | INT | IOD_EPS306_TCP | 40017 | 0 | 600 | 0 | 60 | řC | ##.#
EPS306TIA3_alarm | INT | IOD_EPS306_TCP | 40018 | 0 | 60 | 0 | 60 | řC | ##
EPS306TIA3_previs_temp | DIGITAL | IOD_EPS306_TCP | 00049
EPS306TIA3_temp_s | INT | IOD_EPS306_TCP | 40019 | 0 | 600 | 0 | 60 | řC | ##.#
EPS306ups_alarm | DIGITAL | IOD_EPS306_TCP | 00050
EPS306ups_baterijski_nac | DIGITAL | IOD_EPS306_TCP | 00051
EPS306ups_polnjenje | DIGITAL | IOD_EPS306_TCP | 00052
EPS306UserCurrentLevel | INT | IOD_EPS306_TCP | 40020
EPS306UserCurrentName | STRING | IOD_EPS306_TCP | 45001[15]
EPS306UserLoggedIn | DIGITAL | IOD_EPS306_TCP | 00053
EPS306VentilatorjiAlarm | DIGITAL | IOD_EPS306_TCP | 00054
EPS306VentilatorjiCybroAlarm_lucka | INT | IOD_EPS306_TCP | 40021
EPS306VentilatorjiCybroHisterezaTEMP_HI | INT | IOD_EPS306_TCP | 40022 | 0 | 60 | 0 | 60 | řC | ##
EPS306VentilatorjiCybroHisterezaTEMP_LO | INT | IOD_EPS306_TCP | 40023 | 0 | 60 | 0 | 60 | řC | ##
EPS306VentilatorjiCybroHisterezaVLAGA_HI | INT | IOD_EPS306_TCP | 40024 | 0 | 60 | 0 | 60 | řC | ##
EPS306VentilatorjiCybroHisterezaVLAGA_LO | INT | IOD_EPS306_TCP | 40025 | 0 | 60 | 0 | 60 | řC | ##
EPS306VentilatorjiCybroHitrost_Vent1_MAX | INT | IOD_EPS306_TCP | 40026 | 0 | 60 | 0 | 50 | Hz | ##
EPS306VentilatorjiCybroHitrost_Vent1_MIN | INT | IOD_EPS306_TCP | 40027 | 0 | 60 | 0 | 50 | Hz | ##
EPS306VentilatorjiCybroI_ERR_Vent1 | DIGITAL | IOD_EPS306_TCP | 00055
EPS306VentilatorjiCybroI_ERR_Vent2 | DIGITAL | IOD_EPS306_TCP | 00056
EPS306VentilatorjiCybroI_ERR_Vent3 | DIGITAL | IOD_EPS306_TCP | 00057
EPS306VentilatorjiCybroO_Hitrost_Vent1 | INT | IOD_EPS306_TCP | 40028 | 0 | 50 | 0 | 50 | Hz | ##
EPS306VentilatorjiCybroO_Hitrost_Vent2 | INT | IOD_EPS306_TCP | 40029 | 0 | 50 | 0 | 50 | Hz | ##
EPS306VentilatorjiCybroO_Hitrost_Vent3 | INT | IOD_EPS306_TCP | 40030 | 0 | 50 | 0 | 50 | Hz | ##
EPS306VentilatorjiCybroSAvtomatsko_Vent1 | DIGITAL | IOD_EPS306_TCP | 00058
EPS306VentilatorjiCybroSAvtomatsko_Vent2 | DIGITAL | IOD_EPS306_TCP | 00059
EPS306VentilatorjiCybroSAvtomatsko_Vent3 | DIGITAL | IOD_EPS306_TCP | 00060
EPS306VentilatorjiCybroSRocno_Vent1 | DIGITAL | IOD_EPS306_TCP | 00061
EPS306VentilatorjiCybroSRocno_Vent2 | DIGITAL | IOD_EPS306_TCP | 00062
EPS306VentilatorjiCybroSRocno_Vent3 | DIGITAL | IOD_EPS306_TCP | 00063
EPS306VentilatorjiCybroTempSKUPNA | INT | IOD_EPS306_TCP | 40031 | 0 | 60 | 0 | 60 | řC | ##
EPS306VentilatorjiCybroVlagaSKUPNA | INT | IOD_EPS306_TCP | 40032 | 0 | 60 | 0 | 60 | řC | ##
EPS306VentilatorjiNapaka | DIGITAL | IOD_EPS306_TCP | 00064
EPS306XVH_AlarmOn | DIGITAL | IOD_EPS306_TCP | 00065
EPS306XVH_KlimaSplitStatus1 | INT | IOD_EPS306_TCP | 40033
EPS306XVH_KlimaSplitStatus2 | INT | IOD_EPS306_TCP | 40034
EPS306XVH_KonvekorErr | DIGITAL | IOD_EPS306_TCP | 00066
EPS306XVH_UPSstatus | INT | IOD_EPS306_TCP | 40035
EPS306ComSCADA_stevec1 | INT | IOD_EPS306_mem | I1 | [6 empty] | 6157 | 1
EPS306ComSCADA_stevec2 | INT | IOD_EPS306_mem | I2 | [6 empty] | 6157 | 1
EPS306_Sekunda1s_utripanje | DIGITAL | IOD_EPS306_mem | D3 | [6 empty] | 6157 | 1
EP306_prikaz_ups_ce_je1 | DIGITAL | IOD_EPS306_mem | D4 | [6 empty] | 6157 | 1
EPS306E5_F1_napaka_omog | DIGITAL | IOD_EPS306_disk | D5 | [6 empty] | 6157 | 1
EPS306E5_F2_napaka_omog | DIGITAL | IOD_EPS306_disk | D6 | [6 empty] | 6157 | 1
EPS306E5_F3_napaka_omog | DIGITAL | IOD_EPS306_disk | D7 | [6 empty] | 6157 | 1
EPS306E5_U1_napaka_omog | DIGITAL | IOD_EPS306_disk | D8 | [6 empty] | 6157 | 1
EPS306E5_U2_napaka_omog | DIGITAL | IOD_EPS306_disk | D9 | [6 empty] | 6157 | 1
EPS306E5_U3_napaka_omog | DIGITAL | IOD_EPS306_disk | D10 | [6 empty] | 6157 | 1
EPS306KLIMA_SPLIT1_napaka_omog | DIGITAL | IOD_EPS306_disk | D11 | [6 empty] | 6157 | 1
EPS306KLIMA_SPLIT2_napaka_omog | DIGITAL | IOD_EPS306_disk | D12 | [6 empty] | 6157 | 1
EPS306NapakaTSTempTIA3_omog | DIGITAL | IOD_EPS306_disk | D13 | [6 empty] | 6157 | 1
EPS306napaka_kom_panel_omog | DIGITAL | IOD_EPS306_disk | D14 | [6 empty] | 6157 | 1
EPS306NapakaSenzorVlagaHIA1_omog | DIGITAL | IOD_EPS306_disk | D15 | [6 empty] | 6157 | 1
EPS306NapakaSenzorVlagaHIA2_omog | DIGITAL | IOD_EPS306_disk | D16 | [6 empty] | 6157 | 1
EPS306NapakaTSTempTIA1_omog | DIGITAL | IOD_EPS306_disk | D17 | [6 empty] | 6157 | 1
EPS306NapakaTSTempTIA2_omog | DIGITAL | IOD_EPS306_disk | D18 | [6 empty] | 6157 | 1
EPS306razlitje_vode_LAH1_omog | DIGITAL | IOD_EPS306_disk | D19 | [6 empty] | 6157 | 1
EPS306razlitje_vode_LAH2_omog | DIGITAL | IOD_EPS306_disk | D20 | [6 empty] | 6157 | 1
EPS306ups_alarm_omog | DIGITAL | IOD_EPS306_disk | D21 | [6 empty] | 6157 | 1
EPS306E5_F1_delovanje_omog | DIGITAL | IOD_EPS306_disk | D22 | [6 empty] | 6157 | 1
EPS306E5_F2_delovanje_omog | DIGITAL | IOD_EPS306_disk | D23 | [6 empty] | 6157 | 1
EPS306E5_F3_delovanje_omog | DIGITAL | IOD_EPS306_disk | D24 | [6 empty] | 6157 | 1
EPS306E5_U1_delovanje_omog | DIGITAL | IOD_EPS306_disk | D25 | [6 empty] | 6157 | 1
EPS306E5_U2_delovanje_omog | DIGITAL | IOD_EPS306_disk | D26 | [6 empty] | 6157 | 1
EPS306E5_U3_delovanje_omog | DIGITAL | IOD_EPS306_disk | D27 | [6 empty] | 6157 | 1
EPS306KLIMA_SPLIT1_delovanje_omog | DIGITAL | IOD_EPS306_disk | D28 | [6 empty] | 6157 | 1
EPS306NapakaSenzorVlagaHIA3_omog | DIGITAL | IOD_EPS306_disk | D29 | [6 empty] | 6157 | 1
EPS306SlabaBaterijaPLC_omog | DIGITAL | IOD_EPS306_disk | D30 | [6 empty] | 6157 | 1
EPS306ups_baterijski_nac_omog | DIGITAL | IOD_EPS306_disk | D31 | [6 empty] | 6157 | 1
EPS306ups_polnjenje_omog | DIGITAL | IOD_EPS306_disk | D32 | [6 empty] | 6157 | 1
EPS306napaka_kom_krm_omogoci | DIGITAL | IOD_EPS306_disk | D33 | [6 empty] | 6157 | 1
AEP306_omogoci_sms | DIGITAL | IOD_EPS306_disk | D34[50] | [6 empty] | 6157 | 1
BEP306_omogoci_sms | DIGITAL | IOD_EPS306_disk | D84[50] | [6 empty] | 6157 | 1
CEP306_omogoci_sms | DIGITAL | IOD_EPS306_disk | D134[50] | [6 empty] | 6157 | 1
DEP306_omogoci_sms | DIGITAL | IOD_EPS306_disk | D184[50] | [6 empty] | 6157 | 1
EEP306_omogoci_sms | DIGITAL | IOD_EPS306_disk | D234[50] | [6 empty] | 6157 | 1
FEP306_omogoci_sms | DIGITAL | IOD_EPS306_disk | D284[50] | [6 empty] | 6157 | 1
EPS306KLIMA_SPLIT2_delovanje_omog | DIGITAL | IOD_EPS306_disk | D335
EPS306VentilatorjiCybroI_ERR_Vent1_omog | DIGITAL | IOD_EPS306_disk | D336
EPS306VentilatorjiCybroI_ERR_Vent2_omog | DIGITAL | IOD_EPS306_disk | D337
EPS306VentilatorjiCybroI_ERR_Vent3_omog | DIGITAL | IOD_EPS306_disk | D338
EPS306VentilatorjiNapaka_omog | DIGITAL | IOD_EPS306_disk | D339
EPS306VentilatorjiCybroAlarm_lucka_omog | DIGITAL | IOD_EPS306_disk | D340
EPS306TIA1_previs_temp_omog | DIGITAL | IOD_EPS306_disk | D341
EPS306TIA2_previs_temp_omog | DIGITAL | IOD_EPS306_disk | D342
EPS306TIA3_previs_temp_omog | DIGITAL | IOD_EPS306_disk | D343
EPS306SetDateTimeError_omog | DIGITAL | IOD_EPS306_disk | D344
EPS306VentilatorjiCybroSAvtomatsko_Vent1_omog | DIGITAL | IOD_EPS306_disk | D345
EPS306VentilatorjiCybroSAvtomatsko_Vent2_omog | DIGITAL | IOD_EPS306_disk | D346
EPS306VentilatorjiCybroSAvtomatsko_Vent3_omog | DIGITAL | IOD_EPS306_disk | D347
EPS306VentilatorjiCybroSRocno_Vent1_omog | DIGITAL | IOD_EPS306_disk | D348
EPS306VentilatorjiCybroSRocno_Vent2_omog | DIGITAL | IOD_EPS306_disk | D349
EPS306VentilatorjiCybroSRocno_Vent3_omog | DIGITAL | IOD_EPS306_disk | D350
EPS306ErrComPort2_omog | DIGITAL | IOD_EPS306_disk | D351
EPS306ErrComCybro_omog | DIGITAL | IOD_EPS306_disk | D352
EPS306UserLoggedIn_mem | DIGITAL | IOD_EPS306_mem | D353
neEPS306E5_F1_delovanje_omog | DIGITAL | IOD_EPS306_disk | D354
neEPS306E5_F2_delovanje_omog | DIGITAL | IOD_EPS306_mem | D355
neEPS306E5_F3_delovanje_omog | DIGITAL | IOD_EPS306_disk | D356
neEPS306E5_Q0_vkljuceno_omog | DIGITAL | IOD_EPS306_mem | D357
EPS306E5_Q0_vkljuceno_omog | DIGITAL | IOD_EPS306_disk | D358
EPS306napaka_kom_scada2 | DIGITAL | IOD_EPS306_TCP | 00067
EPS306ComSCADA2 | DIGITAL | IOD_EPS306_TCP | 00068
EPS306napaka_kom_krm_omogoci2 | DIGITAL | IOD_EPS306_disk | D361
EPS306Server_A_Izpad | DIGITAL | IOD_EPS306_disk | D362
EPS306Server_B_Izpad | DIGITAL | IOD_EPS306_disk | D363
EPS306ComSCADA_stevec3 | INT | IOD_EPS306_mem | I366
EPS306ComSCADA_stevec | INT | IOD_EPS306_mem | I368
EPS306ComSCADA3 | DIGITAL | IOD_EPS306_TCP | 00069
EPS306kom_nast_cas_izpada | INT | IOD_EPS306_TCP | 40036

## XSoft
mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Write_BOOL(FC) | mod_Write_Word(FC) | mod_Write_Word(FC) | mod_Write_dWord(FC) | mod_Write_dWord(FC) | mod_Write_String(FC)
(*Branje BOOL*) | (*Branje INT*) | (*Branje UINT*) | (*Branje LONG*) | (*Branje REAL*) | (*Branje STRING*) | (*Pisanje BOOL*) | (*Pisanje INT*) | (*Pisanje UINT*) | (*Pisanje LONG*) | (*Pisanje REAL*) | (*Pisanje STRING*)
(**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**)
mind_bool[0]:=Alarm_E5M; | mind[0]:=DateTime.Dan; |  |  |  | Read_String(sVar:=UserCurrentName,start:=5000); | 0:Alarm_E5M:=Bit_0; | 0:DateTime.Dan:=Byte_0; |  |  |  | 5000:UserCurrentName:=String_0;
mind_bool[1]:=ComSCADA; | mind[1]:=DateTime.Leto; |  |  |  |  | 1:ComSCADA:=Bit_0; | 1:DateTime.Leto:=Byte_0;
mind_bool[2]:=ComSCADA1; | mind[2]:=DateTime.Leto2; |  |  |  |  | 2:ComSCADA1:=Bit_0; | 2:DateTime.Leto2:=Word_01;
mind_bool[3]:=E5_F1_delovanje; | mind[3]:=DateTime.Mesec; |  |  |  |  | 3:E5_F1_delovanje:=Bit_0; | 3:DateTime.Mesec:=Byte_0;
mind_bool[4]:=E5_F1_napaka; | mind[4]:=DateTime.Minuta; |  |  |  |  | 4:E5_F1_napaka:=Bit_0; | 4:DateTime.Minuta:=Byte_0;
mind_bool[5]:=E5_F2_delovanje; | mind[5]:=DateTime.Sekunda; |  |  |  |  | 5:E5_F2_delovanje:=Bit_0; | 5:DateTime.Sekunda:=Byte_0;
mind_bool[6]:=E5_F2_napaka; | mind[6]:=DateTime.Ura; |  |  |  |  | 6:E5_F2_napaka:=Bit_0; | 6:DateTime.Ura:=Byte_0;
mind_bool[7]:=E5_F3_delovanje; | mind[7]:=HIA1_vlaga_s; |  |  |  |  | 7:E5_F3_delovanje:=Bit_0; | 7:HIA1_vlaga_s:=Word_01;
mind_bool[8]:=E5_F3_napaka; | mind[8]:=HIA2_vlaga_s; |  |  |  |  | 8:E5_F3_napaka:=Bit_0; | 8:HIA2_vlaga_s:=Word_01;
mind_bool[9]:=E5_Q0_vkljuceno; | mind[9]:=HIA3_vlaga_s; |  |  |  |  | 9:E5_Q0_vkljuceno:=Bit_0; | 9:HIA3_vlaga_s:=Word_01;
mind_bool[10]:=E5_U1_delovanje; | mind[10]:=RezimVent1; |  |  |  |  | 10:E5_U1_delovanje:=Bit_0; | 10:RezimVent1:=Byte_0;
mind_bool[11]:=E5_U1_napaka; | mind[11]:=RezimVent2; |  |  |  |  | 11:E5_U1_napaka:=Bit_0; | 11:RezimVent2:=Byte_0;
mind_bool[12]:=E5_U2_delovanje; | mind[12]:=RezimVent3; |  |  |  |  | 12:E5_U2_delovanje:=Bit_0; | 12:RezimVent3:=Byte_0;
mind_bool[13]:=E5_U2_napaka; | mind[13]:=TIA1_alarm; |  |  |  |  | 13:E5_U2_napaka:=Bit_0; | 13:TIA1_alarm:=Word_01;
mind_bool[14]:=E5_U3_delovanje; | mind[14]:=TIA1_temp_s; |  |  |  |  | 14:E5_U3_delovanje:=Bit_0; | 14:TIA1_temp_s:=Word_01;
mind_bool[15]:=E5_U3_napaka; | mind[15]:=TIA2_alarm; |  |  |  |  | 15:E5_U3_napaka:=Bit_0; | 15:TIA2_alarm:=Word_01;
mind_bool[16]:=ErrComCybro; | mind[16]:=TIA2_temp_s; |  |  |  |  | 16:ErrComCybro:=Bit_0; | 16:TIA2_temp_s:=Word_01;
mind_bool[17]:=ErrComPort2; | mind[17]:=TIA3_alarm; |  |  |  |  | 17:ErrComPort2:=Bit_0; | 17:TIA3_alarm:=Word_01;
mind_bool[18]:=KLIMA_SPLIT1_delovanje; | mind[18]:=TIA3_temp_s; |  |  |  |  | 18:KLIMA_SPLIT1_delovanje:=Bit_0; | 18:TIA3_temp_s:=Word_01;
mind_bool[19]:=KLIMA_SPLIT1_napaka; | mind[19]:=UserCurrentLevel; |  |  |  |  | 19:KLIMA_SPLIT1_napaka:=Bit_0; | 19:UserCurrentLevel:=Byte_0;
mind_bool[20]:=KLIMA_SPLIT2_delovanje; | mind[20]:=VentilatorjiCybro.Alarm_lucka; |  |  |  |  | 20:KLIMA_SPLIT2_delovanje:=Bit_0; | 20:VentilatorjiCybro.Alarm_lucka:=Word_01;
mind_bool[21]:=KLIMA_SPLIT2_napaka; | mind[21]:=VentilatorjiCybro.HisterezaTEMP_HI; |  |  |  |  | 21:KLIMA_SPLIT2_napaka:=Bit_0; | 21:VentilatorjiCybro.HisterezaTEMP_HI:=Word_01;
mind_bool[22]:=KomunikacijaErr; | mind[22]:=VentilatorjiCybro.HisterezaTEMP_LO; |  |  |  |  | 22:KomunikacijaErr:=Bit_0; | 22:VentilatorjiCybro.HisterezaTEMP_LO:=Word_01;
mind_bool[23]:=N_E5_F1_napaka; | mind[23]:=VentilatorjiCybro.HisterezaVLAGA_HI; |  |  |  |  | 23:N_E5_F1_napaka:=Bit_0; | 23:VentilatorjiCybro.HisterezaVLAGA_HI:=Word_01;
mind_bool[24]:=N_E5_F2_napaka; | mind[24]:=VentilatorjiCybro.HisterezaVLAGA_LO; |  |  |  |  | 24:N_E5_F2_napaka:=Bit_0; | 24:VentilatorjiCybro.HisterezaVLAGA_LO:=Word_01;
mind_bool[25]:=N_E5_F3_napaka; | mind[25]:=VentilatorjiCybro.Hitrost_Vent1_MAX; |  |  |  |  | 25:N_E5_F3_napaka:=Bit_0; | 25:VentilatorjiCybro.Hitrost_Vent1_MAX:=Word_01;
mind_bool[26]:=N_E5_U1_napaka; | mind[26]:=VentilatorjiCybro.Hitrost_Vent1_MIN; |  |  |  |  | 26:N_E5_U1_napaka:=Bit_0; | 26:VentilatorjiCybro.Hitrost_Vent1_MIN:=Word_01;
mind_bool[27]:=N_E5_U2_napaka; | mind[27]:=VentilatorjiCybro.O_Hitrost_Vent1; |  |  |  |  | 27:N_E5_U2_napaka:=Bit_0; | 27:VentilatorjiCybro.O_Hitrost_Vent1:=Word_01;
mind_bool[28]:=N_E5_U3_napaka; | mind[28]:=VentilatorjiCybro.O_Hitrost_Vent2; |  |  |  |  | 28:N_E5_U3_napaka:=Bit_0; | 28:VentilatorjiCybro.O_Hitrost_Vent2:=Word_01;
mind_bool[29]:=napaka_kom_panel; | mind[29]:=VentilatorjiCybro.O_Hitrost_Vent3; |  |  |  |  | 29:napaka_kom_panel:=Bit_0; | 29:VentilatorjiCybro.O_Hitrost_Vent3:=Word_01;
mind_bool[30]:=napaka_kom_scada; | mind[30]:=VentilatorjiCybro.TempSKUPNA; |  |  |  |  | 30:napaka_kom_scada:=Bit_0; | 30:VentilatorjiCybro.TempSKUPNA:=Word_01;
mind_bool[31]:=NapakaSenzorSkupno; | mind[31]:=VentilatorjiCybro.VlagaSKUPNA; |  |  |  |  | 31:NapakaSenzorSkupno:=Bit_0; | 31:VentilatorjiCybro.VlagaSKUPNA:=Word_01;
mind_bool[32]:=NapakaSenzorVlagaHIA1; | mind[32]:=XVH_KlimaSplitStatus[1]; |  |  |  |  | 32:NapakaSenzorVlagaHIA1:=Bit_0; | 32:XVH_KlimaSplitStatus[1]:=Byte_0;
mind_bool[33]:=NapakaSenzorVlagaHIA2; | mind[33]:=XVH_KlimaSplitStatus[2]; |  |  |  |  | 33:NapakaSenzorVlagaHIA2:=Bit_0; | 33:XVH_KlimaSplitStatus[2]:=Byte_0;
mind_bool[34]:=NapakaSenzorVlagaHIA3; | mind[34]:=XVH_UPSstatus; |  |  |  |  | 34:NapakaSenzorVlagaHIA3:=Bit_0; | 34:XVH_UPSstatus:=Byte_0;
mind_bool[35]:=NapakaTSTempTIA1; | mind[35]:=kom_nast_cas_izpada; |  |  |  |  | 35:NapakaTSTempTIA1:=Bit_0; | 35:kom_nast_cas_izpada:=Word_01;
mind_bool[36]:=NapakaTSTempTIA2; | [5 empty] | 36:NapakaTSTempTIA2:=Bit_0;
mind_bool[37]:=NapakaTSTempTIA3; | [5 empty] | 37:NapakaTSTempTIA3:=Bit_0;
mind_bool[38]:=PrevisokaTemp; | [5 empty] | 38:PrevisokaTemp:=Bit_0;
mind_bool[39]:=razlitje_vode_LAH1; | [5 empty] | 39:razlitje_vode_LAH1:=Bit_0;
mind_bool[40]:=razlitje_vode_LAH2; | [5 empty] | 40:razlitje_vode_LAH2:=Bit_0;
mind_bool[41]:=SetDateTime; | [5 empty] | 41:SetDateTime:=Bit_0;
mind_bool[42]:=SetDateTimeDemand; | [5 empty] | 42:SetDateTimeDemand:=Bit_0;
mind_bool[43]:=SetDateTimeError; | [5 empty] | 43:SetDateTimeError:=Bit_0;
mind_bool[44]:=SetDateTimeFinished; | [5 empty] | 44:SetDateTimeFinished:=Bit_0;
mind_bool[45]:=SlabaBaterijaPLC; | [5 empty] | 45:SlabaBaterijaPLC:=Bit_0;
mind_bool[46]:=TIA1_previs_temp; | [5 empty] | 46:TIA1_previs_temp:=Bit_0;
mind_bool[47]:=TIA2_previs_temp; | [5 empty] | 47:TIA2_previs_temp:=Bit_0;
mind_bool[48]:=TIA3_previs_temp; | [5 empty] | 48:TIA3_previs_temp:=Bit_0;
mind_bool[49]:=ups_alarm; | [5 empty] | 49:ups_alarm:=Bit_0;
mind_bool[50]:=ups_baterijski_nac; | [5 empty] | 50:ups_baterijski_nac:=Bit_0;
mind_bool[51]:=ups_polnjenje; | [5 empty] | 51:ups_polnjenje:=Bit_0;
mind_bool[52]:=UserLoggedIn; | [5 empty] | 52:UserLoggedIn:=Bit_0;
mind_bool[53]:=VentilatorjiAlarm; | [5 empty] | 53:VentilatorjiAlarm:=Bit_0;
mind_bool[54]:=VentilatorjiCybro.I_ERR_Vent1; | [5 empty] | 54:VentilatorjiCybro.I_ERR_Vent1:=Bit_0;
mind_bool[55]:=VentilatorjiCybro.I_ERR_Vent2; | [5 empty] | 55:VentilatorjiCybro.I_ERR_Vent2:=Bit_0;
mind_bool[56]:=VentilatorjiCybro.I_ERR_Vent3; | [5 empty] | 56:VentilatorjiCybro.I_ERR_Vent3:=Bit_0;
mind_bool[57]:=VentilatorjiCybro.SAvtomatsko_Vent1; | [5 empty] | 57:VentilatorjiCybro.SAvtomatsko_Vent1:=Bit_0;
mind_bool[58]:=VentilatorjiCybro.SAvtomatsko_Vent2; | [5 empty] | 58:VentilatorjiCybro.SAvtomatsko_Vent2:=Bit_0;
mind_bool[59]:=VentilatorjiCybro.SAvtomatsko_Vent3; | [5 empty] | 59:VentilatorjiCybro.SAvtomatsko_Vent3:=Bit_0;
mind_bool[60]:=VentilatorjiCybro.SRocno_Vent1; | [5 empty] | 60:VentilatorjiCybro.SRocno_Vent1:=Bit_0;
mind_bool[61]:=VentilatorjiCybro.SRocno_Vent2; | [5 empty] | 61:VentilatorjiCybro.SRocno_Vent2:=Bit_0;
mind_bool[62]:=VentilatorjiCybro.SRocno_Vent3; | [5 empty] | 62:VentilatorjiCybro.SRocno_Vent3:=Bit_0;
mind_bool[63]:=VentilatorjiNapaka; | [5 empty] | 63:VentilatorjiNapaka:=Bit_0;
mind_bool[64]:=XVH_AlarmOn; | [5 empty] | 64:XVH_AlarmOn:=Bit_0;
mind_bool[65]:=XVH_KonvekorErr; | [5 empty] | 65:XVH_KonvekorErr:=Bit_0;
mind_bool[66]:=napaka_kom_scada2; | [5 empty] | 66:napaka_kom_scada2:=Bit_0;
mind_bool[67]:=ComSCADA2; | [5 empty] | 67:ComSCADA2:=Bit_0;
mind_bool[68]:=ComSCADA3; | [5 empty] | 68:ComSCADA3:=Bit_0;

## XSoft_EXP
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
PROGRAM mod_Read
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*Branje BOOL*)
(**)
mind_bool[0]:=Alarm_E5M;
mind_bool[1]:=ComSCADA;
mind_bool[2]:=ComSCADA1;
mind_bool[3]:=E5_F1_delovanje;
mind_bool[4]:=E5_F1_napaka;
mind_bool[5]:=E5_F2_delovanje;
mind_bool[6]:=E5_F2_napaka;
mind_bool[7]:=E5_F3_delovanje;
mind_bool[8]:=E5_F3_napaka;
mind_bool[9]:=E5_Q0_vkljuceno;
mind_bool[10]:=E5_U1_delovanje;
mind_bool[11]:=E5_U1_napaka;
mind_bool[12]:=E5_U2_delovanje;
mind_bool[13]:=E5_U2_napaka;
mind_bool[14]:=E5_U3_delovanje;
mind_bool[15]:=E5_U3_napaka;
mind_bool[16]:=ErrComCybro;
mind_bool[17]:=ErrComPort2;
mind_bool[18]:=KLIMA_SPLIT1_delovanje;
mind_bool[19]:=KLIMA_SPLIT1_napaka;
mind_bool[20]:=KLIMA_SPLIT2_delovanje;
mind_bool[21]:=KLIMA_SPLIT2_napaka;
mind_bool[22]:=KomunikacijaErr;
mind_bool[23]:=N_E5_F1_napaka;
mind_bool[24]:=N_E5_F2_napaka;
mind_bool[25]:=N_E5_F3_napaka;
mind_bool[26]:=N_E5_U1_napaka;
mind_bool[27]:=N_E5_U2_napaka;
mind_bool[28]:=N_E5_U3_napaka;
mind_bool[29]:=napaka_kom_panel;
mind_bool[30]:=napaka_kom_scada;
mind_bool[31]:=NapakaSenzorSkupno;
mind_bool[32]:=NapakaSenzorVlagaHIA1;
mind_bool[33]:=NapakaSenzorVlagaHIA2;
mind_bool[34]:=NapakaSenzorVlagaHIA3;
mind_bool[35]:=NapakaTSTempTIA1;
mind_bool[36]:=NapakaTSTempTIA2;
mind_bool[37]:=NapakaTSTempTIA3;
mind_bool[38]:=PrevisokaTemp;
mind_bool[39]:=razlitje_vode_LAH1;
mind_bool[40]:=razlitje_vode_LAH2;
mind_bool[41]:=SetDateTime;
mind_bool[42]:=SetDateTimeDemand;
mind_bool[43]:=SetDateTimeError;
mind_bool[44]:=SetDateTimeFinished;
mind_bool[45]:=SlabaBaterijaPLC;
mind_bool[46]:=TIA1_previs_temp;
mind_bool[47]:=TIA2_previs_temp;
mind_bool[48]:=TIA3_previs_temp;
mind_bool[49]:=ups_alarm;
mind_bool[50]:=ups_baterijski_nac;
mind_bool[51]:=ups_polnjenje;
mind_bool[52]:=UserLoggedIn;
mind_bool[53]:=VentilatorjiAlarm;
mind_bool[54]:=VentilatorjiCybro.I_ERR_Vent1;
mind_bool[55]:=VentilatorjiCybro.I_ERR_Vent2;
mind_bool[56]:=VentilatorjiCybro.I_ERR_Vent3;
mind_bool[57]:=VentilatorjiCybro.SAvtomatsko_Vent1;
mind_bool[58]:=VentilatorjiCybro.SAvtomatsko_Vent2;
mind_bool[59]:=VentilatorjiCybro.SAvtomatsko_Vent3;
mind_bool[60]:=VentilatorjiCybro.SRocno_Vent1;
mind_bool[61]:=VentilatorjiCybro.SRocno_Vent2;
mind_bool[62]:=VentilatorjiCybro.SRocno_Vent3;
mind_bool[63]:=VentilatorjiNapaka;
mind_bool[64]:=XVH_AlarmOn;
mind_bool[65]:=XVH_KonvekorErr;
mind_bool[66]:=napaka_kom_scada2;
mind_bool[67]:=ComSCADA2;
mind_bool[68]:=ComSCADA3;
(*Branje INT*)
(**)
mind[0]:=DateTime.Dan;
mind[1]:=DateTime.Leto;
mind[2]:=DateTime.Leto2;
mind[3]:=DateTime.Mesec;
mind[4]:=DateTime.Minuta;
mind[5]:=DateTime.Sekunda;
mind[6]:=DateTime.Ura;
mind[7]:=HIA1_vlaga_s;
mind[8]:=HIA2_vlaga_s;
mind[9]:=HIA3_vlaga_s;
mind[10]:=RezimVent1;
mind[11]:=RezimVent2;
mind[12]:=RezimVent3;
mind[13]:=TIA1_alarm;
mind[14]:=TIA1_temp_s;
mind[15]:=TIA2_alarm;
mind[16]:=TIA2_temp_s;
mind[17]:=TIA3_alarm;
mind[18]:=TIA3_temp_s;
mind[19]:=UserCurrentLevel;
mind[20]:=VentilatorjiCybro.Alarm_lucka;
mind[21]:=VentilatorjiCybro.HisterezaTEMP_HI;
mind[22]:=VentilatorjiCybro.HisterezaTEMP_LO;
mind[23]:=VentilatorjiCybro.HisterezaVLAGA_HI;
mind[24]:=VentilatorjiCybro.HisterezaVLAGA_LO;
mind[25]:=VentilatorjiCybro.Hitrost_Vent1_MAX;
mind[26]:=VentilatorjiCybro.Hitrost_Vent1_MIN;
mind[27]:=VentilatorjiCybro.O_Hitrost_Vent1;
mind[28]:=VentilatorjiCybro.O_Hitrost_Vent2;
mind[29]:=VentilatorjiCybro.O_Hitrost_Vent3;
mind[30]:=VentilatorjiCybro.TempSKUPNA;
mind[31]:=VentilatorjiCybro.VlagaSKUPNA;
mind[32]:=XVH_KlimaSplitStatus[1];
mind[33]:=XVH_KlimaSplitStatus[2];
mind[34]:=XVH_UPSstatus;
mind[35]:=kom_nast_cas_izpada;
(*Branje UINT*)
(**)
(*Branje LONG*)
(**)
(*Branje REAL*)
(**)
(*Branje STRING*)
(**)
Read_String(sVar:=UserCurrentName,start:=5000);
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Bool : BOOL
VAR_INPUT
index: INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje BOOL*)
(**)
0:Alarm_E5M:=Bit_0;
1:ComSCADA:=Bit_0;
2:ComSCADA1:=Bit_0;
3:E5_F1_delovanje:=Bit_0;
4:E5_F1_napaka:=Bit_0;
5:E5_F2_delovanje:=Bit_0;
6:E5_F2_napaka:=Bit_0;
7:E5_F3_delovanje:=Bit_0;
8:E5_F3_napaka:=Bit_0;
9:E5_Q0_vkljuceno:=Bit_0;
10:E5_U1_delovanje:=Bit_0;
11:E5_U1_napaka:=Bit_0;
12:E5_U2_delovanje:=Bit_0;
13:E5_U2_napaka:=Bit_0;
14:E5_U3_delovanje:=Bit_0;
15:E5_U3_napaka:=Bit_0;
16:ErrComCybro:=Bit_0;
17:ErrComPort2:=Bit_0;
18:KLIMA_SPLIT1_delovanje:=Bit_0;
19:KLIMA_SPLIT1_napaka:=Bit_0;
20:KLIMA_SPLIT2_delovanje:=Bit_0;
21:KLIMA_SPLIT2_napaka:=Bit_0;
22:KomunikacijaErr:=Bit_0;
23:N_E5_F1_napaka:=Bit_0;
24:N_E5_F2_napaka:=Bit_0;
25:N_E5_F3_napaka:=Bit_0;
26:N_E5_U1_napaka:=Bit_0;
27:N_E5_U2_napaka:=Bit_0;
28:N_E5_U3_napaka:=Bit_0;
29:napaka_kom_panel:=Bit_0;
30:napaka_kom_scada:=Bit_0;
31:NapakaSenzorSkupno:=Bit_0;
32:NapakaSenzorVlagaHIA1:=Bit_0;
33:NapakaSenzorVlagaHIA2:=Bit_0;
34:NapakaSenzorVlagaHIA3:=Bit_0;
35:NapakaTSTempTIA1:=Bit_0;
36:NapakaTSTempTIA2:=Bit_0;
37:NapakaTSTempTIA3:=Bit_0;
38:PrevisokaTemp:=Bit_0;
39:razlitje_vode_LAH1:=Bit_0;
40:razlitje_vode_LAH2:=Bit_0;
41:SetDateTime:=Bit_0;
42:SetDateTimeDemand:=Bit_0;
43:SetDateTimeError:=Bit_0;
44:SetDateTimeFinished:=Bit_0;
45:SlabaBaterijaPLC:=Bit_0;
46:TIA1_previs_temp:=Bit_0;
47:TIA2_previs_temp:=Bit_0;
48:TIA3_previs_temp:=Bit_0;
49:ups_alarm:=Bit_0;
50:ups_baterijski_nac:=Bit_0;
51:ups_polnjenje:=Bit_0;
52:UserLoggedIn:=Bit_0;
53:VentilatorjiAlarm:=Bit_0;
54:VentilatorjiCybro.I_ERR_Vent1:=Bit_0;
55:VentilatorjiCybro.I_ERR_Vent2:=Bit_0;
56:VentilatorjiCybro.I_ERR_Vent3:=Bit_0;
57:VentilatorjiCybro.SAvtomatsko_Vent1:=Bit_0;
58:VentilatorjiCybro.SAvtomatsko_Vent2:=Bit_0;
59:VentilatorjiCybro.SAvtomatsko_Vent3:=Bit_0;
60:VentilatorjiCybro.SRocno_Vent1:=Bit_0;
61:VentilatorjiCybro.SRocno_Vent2:=Bit_0;
62:VentilatorjiCybro.SRocno_Vent3:=Bit_0;
63:VentilatorjiNapaka:=Bit_0;
64:XVH_AlarmOn:=Bit_0;
65:XVH_KonvekorErr:=Bit_0;
66:napaka_kom_scada2:=Bit_0;
67:ComSCADA2:=Bit_0;
68:ComSCADA3:=Bit_0;
(*BOOL*)
END_CASE
END_FUNCTION
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_dWord : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje LONG*)
(**)
(*Pisanje REAL*)
(**)
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_String : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje STRING*)
(**)
5000:UserCurrentName:=String_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Word : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje INT*)
(**)
0:DateTime.Dan:=Byte_0;
1:DateTime.Leto:=Byte_0;
2:DateTime.Leto2:=Word_01;
3:DateTime.Mesec:=Byte_0;
4:DateTime.Minuta:=Byte_0;
5:DateTime.Sekunda:=Byte_0;
6:DateTime.Ura:=Byte_0;
7:HIA1_vlaga_s:=Word_01;
8:HIA2_vlaga_s:=Word_01;
9:HIA3_vlaga_s:=Word_01;
10:RezimVent1:=Byte_0;
11:RezimVent2:=Byte_0;
12:RezimVent3:=Byte_0;
13:TIA1_alarm:=Word_01;
14:TIA1_temp_s:=Word_01;
15:TIA2_alarm:=Word_01;
16:TIA2_temp_s:=Word_01;
17:TIA3_alarm:=Word_01;
18:TIA3_temp_s:=Word_01;
19:UserCurrentLevel:=Byte_0;
20:VentilatorjiCybro.Alarm_lucka:=Word_01;
21:VentilatorjiCybro.HisterezaTEMP_HI:=Word_01;
22:VentilatorjiCybro.HisterezaTEMP_LO:=Word_01;
23:VentilatorjiCybro.HisterezaVLAGA_HI:=Word_01;
24:VentilatorjiCybro.HisterezaVLAGA_LO:=Word_01;
25:VentilatorjiCybro.Hitrost_Vent1_MAX:=Word_01;
26:VentilatorjiCybro.Hitrost_Vent1_MIN:=Word_01;
27:VentilatorjiCybro.O_Hitrost_Vent1:=Word_01;
28:VentilatorjiCybro.O_Hitrost_Vent2:=Word_01;
29:VentilatorjiCybro.O_Hitrost_Vent3:=Word_01;
30:VentilatorjiCybro.TempSKUPNA:=Word_01;
31:VentilatorjiCybro.VlagaSKUPNA:=Word_01;
32:XVH_KlimaSplitStatus[1]:=Byte_0;
33:XVH_KlimaSplitStatus[2]:=Byte_0;
34:XVH_UPSstatus:=Byte_0;
35:kom_nast_cas_izpada:=Word_01;
(*Pisanje UINT*)
(**)
;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
(*Modbus Slave Example*)
PROGRAM PLC_PRG_modnet
VAR
Slave_Adresa:BYTE:=2;
Slave_Port:INT:=502;
SlaveSetup:MBS_Setup;
SlavePoll:MBS_Poll;
SlaveAnswer:MBS_Answer;
step: USINT;
end :BOOL;
i: INT;
cycle :BOOL := FALSE; (* First cycle *)
OpenDefaultPort: BOOL;
Write_16: BOOL;
Write_15: BOOL;
Write_5: BOOL;
j: INT;
slavepollwOffset_temp: INT;
slaveanswerwCount_temp: INT;
slaveanswerwoffset_temp: INT;
END_VAR
(* @END_DECLARATION := '0' *)
(*Modbus Slave Example*)
IF Write_16=TRUE THEN (**)
FOR j := 0 TO (slaveanswerwCount_temp-1)/15 BY 1 DO (*vpiše se dword, real*)
wStr_0:=mind[slaveanswerwoffset_temp+j];
wStr_1:=mind[slaveanswerwoffset_temp+j+1];
wStr_2 :=mind[slaveanswerwoffset_temp+j+2];
wStr_3:=mind[slaveanswerwoffset_temp+j+3];
wStr_4:=mind[slaveanswerwoffset_temp+j+4];
wStr_5 :=mind[slaveanswerwoffset_temp+j+5];
wStr_6:=mind[slaveanswerwoffset_temp+j+6];
wStr_7:=mind[slaveanswerwoffset_temp+j+7];
wStr_8:=mind[slaveanswerwoffset_temp+j+8];
wStr_9:=mind[slaveanswerwoffset_temp+j+9];
wStr_10:=mind[slaveanswerwoffset_temp+j+10];
wStr_11:=mind[slaveanswerwoffset_temp+j+11];
wStr_12:=mind[slaveanswerwoffset_temp+j+12];
wStr_13:=mind[slaveanswerwoffset_temp+j+13];
wStr_14:=mind[slaveanswerwoffset_temp+j+14];
bStr_29:=0;
mod_Write_String(index:=slaveanswerwoffset_temp+j); (*vpis real in string*)
END_FOR;
FOR j := 1 TO slaveanswerwCount_temp-1 BY 2 DO (*vpiše se dword, real*)
Word_01:=mind[slaveanswerwoffset_temp+j-1];
Word_23:=mind[slaveanswerwoffset_temp+j];
mod_Write_dWord(index:=slaveanswerwoffset_temp+j); (*vpis real in dword*)
END_FOR;
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO (*vpiše se word*)
Word_01:=mind[slaveanswerwoffset_temp+j];
mod_Write_Word(index:=slaveanswerwoffset_temp+j); (*vpis word*)
END_FOR;
Write_16:=FALSE;
END_IF;
IF Write_5=TRUE OR Write_15=TRUE THEN (**)
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO
Bit_0:=mind_bool[slaveanswerwoffset_temp+j];
mod_Write_Bool(index:=slaveanswerwoffset_temp+j); (*vpis spremembe v spremenljivko*)
END_FOR;
Write_5:=FALSE;
Write_15:=FALSE;
END_IF;
(*iz scade ni komande za branje*)
IF Write_16=FALSE AND Write_5=FALSE AND Write_15=FALSE THEN
mod_Read();(*branje spremenljivk za scado*)
END_IF
(*Close all sockets on corresponding event*)
IF cycle = FALSE THEN
SysCallbackRegister(INDEXOF(Callback_Stop),event_stop);
SysCallbackRegister(INDEXOF(Callback_Reset),event_before_reset);
SysCallbackRegister(INDEXOF(Callback_Reset),event_shutdown);
cycle := TRUE;
END_IF
(*Close all connections via application *)
IF end = TRUE THEN
MBS_CloseAllConnections();
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=FALSE); (*Close port*)
step := 0;
END_IF
IF OpenDefaultPort=TRUE THEN
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=TRUE); (*Close port*)
step := 0;
OpenDefaultPort:=FALSE;
END_IF
(* State machine for setup, poll and answer *)
CASE step OF
0:(**)
SlaveSetup.bUnitIdentifier:=Slave_Adresa;(*Subunitnumber*)
slavesetup.wDefaultPort:=Slave_Port;(*Standartport *)
SlaveSetup.xAdditionalPortActive:=FALSE;(*Port opened or closed*)
SlaveSetup.xSecureMode:=FALSE;(*If TRUE only preset IPs are accepted*)
SlaveSetup.tTimeout:=T#3m;(*Timeout if no communication with slave established*)
SlaveSetup(xStrobe:=TRUE);(*Strobe starts function*)
IF slavesetup.xBusy = FALSE THEN
slavesetup(xstrobe := FALSE);
step := 1 ;
END_IF;
1:(**)
SlavePoll(xStrobe:=TRUE);(*Searching for master commands*)
IF NOT SlavePoll.xBusy THEN
step:=2;
SlavePoll(xStrobe:=FALSE);
END_IF;
2:(**)
step:= 1;
CASE SlavePoll.bFunctionCode OF (*Connect accepted pollparameters with answerparameters*)
8:(**)(*Poll answers*)
;
15:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind_bool[slaveanswer.woffset+i] := slavepoll.xarData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.xarData:=slavepoll.xarData;
Write_15:=TRUE;
16:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind[slaveanswer.woffset+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.wardata := slavepoll.warData;
Write_16:=TRUE;
1,2:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slavepoll.wcount-1 BY 1 DO
slaveanswer.xarData[i]:=mind_bool[slavepoll.woffset+i]; (*Read from Data-array*)
END_FOR
3,4:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slaveanswer.wCount-1 BY 1 DO
slaveanswer.warData[i]:=mind[slavepoll.woffset+i];(*Read from Data-array*)
END_FOR
5:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
mind_bool[slavepoll.woffset]:=slavepoll.xarData[0];(*Write to Data-array*)
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.xarData := slavepoll.xardata;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
Write_5:=TRUE;
6:
slaveanswer.bFunctionCode:= slavepoll.bFunctionCode;
mind[slavepoll.woffset]:= slavepoll.warData[0];(*Write to Data-array*)
slaveanswer.wOffset:= slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wardata := slavepoll.wardata;
23:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
FOR i:= 0 TO slavepoll.wCountAdd-1 BY 1 DO
mind[slavepoll.woffsetadd+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
FOR i := 0 TO slavepoll.wCount BY 1 DO
slaveanswer.warData[i] := mind[1+slavepoll.woffset+i];(*Read from Data-array*)
END_FOR;
END_CASE;
IF slavepoll.xAvailable = TRUE THEN
slaveanswer();(*When Data ready, send answer*)
END_IF
END_CASE;
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_dWord : BOOL
VAR_INPUT
dVAR: DWORD;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
DWord_0:=dVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_Real : BOOL
VAR_INPUT
rVAR: REAL;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
Real_0:=rVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_String : BOOL
VAR_INPUT
sVar: STRING;
start:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
String_0:=LEFT (sVar,29);
mind[start]:=wStr_0;
mind[start+1]:=wStr_1;
mind[start+2]:=wStr_2;
mind[start+3]:=wStr_3;
mind[start+4]:=wStr_4;
mind[start+5]:=wStr_5;
mind[start+6]:=wStr_6;
mind[start+7]:=wStr_7;
mind[start+8]:=wStr_8;
mind[start+9]:=wStr_9;
mind[start+10]:=wStr_10;
mind[start+11]:=wStr_11;
mind[start+12]:=wStr_12;
mind[start+13]:=wStr_13;
bStr_29:=0;
mind[start+14]:=wStr_14;
END_FUNCTION
(* @GLOBAL_VARIABLE_LIST := 'Global_Variables_Modnet' *)
(* @PATH := '' *)
(* @SYMFILEFLAGS := '2048' *)
VAR_GLOBAL
(*delovno polje za modnet komunikacijo*)
mind :ARRAY [0..9999] OF WORD;
mind_bool :ARRAY [0..9999] OF BOOL; (*Buffer-Array*)
(*Delovni markerji //*)
Bit_0 AT %MX0.0 : BOOL;
Byte_0 AT %MB0 : BYTE;
Byte_1 AT %MB1 : BYTE;
Byte_2 AT %MB2 : BYTE;
Byte_3 AT %MB3 : BYTE;
Real_0 AT %MR0:REAL;
DWord_0 AT %MD0:DWORD;
Word_01 AT %MW0:WORD;
Word_23 AT %MW2:WORD;
String_0 AT %MW10:STRING;
wStr_0 AT %MW10:WORD;
wStr_1 AT %MW12:WORD;
wStr_2 AT %MW14:WORD;
wStr_3 AT %MW16:WORD;
wStr_4 AT %MW18:WORD;
wStr_5 AT %MW20:WORD;
wStr_6 AT %MW22:WORD;
wStr_7 AT %MW24:WORD;
wStr_8 AT %MW26:WORD;
wStr_9 AT %MW28:WORD;
wStr_10 AT %MW30:WORD;
wStr_11 AT %MW32:WORD;
wStr_12 AT %MW34:WORD;
wStr_13 AT %MW36:WORD;
wStr_14 AT %MW38:WORD;
bStr_00 AT %MB10:BYTE;
bStr_01 AT %MB11:BYTE;
bStr_02 AT %MB12:BYTE;
bStr_03 AT %MB13:BYTE;
bStr_04 AT %MB14:BYTE;
bStr_05 AT %MB15:BYTE;
bStr_06 AT %MB16:BYTE;
bStr_07 AT %MB17:BYTE;
bStr_08 AT %MB18:BYTE;
bStr_09 AT %MB19:BYTE;
bStr_10 AT %MB20:BYTE;
bStr_11 AT %MB21:BYTE;
bStr_12 AT %MB22:BYTE;
bStr_13 AT %MB23:BYTE;
bStr_14 AT %MB24:BYTE;
bStr_15 AT %MB25:BYTE;
bStr_16 AT %MB26:BYTE;
bStr_17 AT %MB27:BYTE;
bStr_18 AT %MB28:BYTE;
bStr_19 AT %MB29:BYTE;
bStr_20 AT %MB30:BYTE;
bStr_21 AT %MB31:BYTE;
bStr_22 AT %MB32:BYTE;
bStr_23 AT %MB33:BYTE;
bStr_24 AT %MB34:BYTE;
bStr_25 AT %MB35:BYTE;
bStr_26 AT %MB36:BYTE;
bStr_27 AT %MB37:BYTE;
bStr_28 AT %MB38:BYTE;
bStr_29 AT %MB39:BYTE;
(********************************************)
END_VAR
(* @OBJECT_END := 'Global_Variables_Modnet' *)
(* @CONNECTIONS := Global_Variables_Modnet
FILENAME : ''
FILETIME : 0
EXPORT : 0
NUMOFCONNECTIONS : 0
*)
(*KONEC_KODA*)