## Prva stran
variable | 185 | 1.KORAK | variable_1 | 2.KORAK | KORAKI!
Device name | Tip | število spremenljivk | Tip (izbrani) | Zamenjaj z | 1.V Sheet "variable" skopiraj vsebino iz variable.dbf - iz Citect SCAD-a projekta, ki ga želiš pretvoriti.
IOD_PEP | BCD | 0 | BCD | INT | 2.V polje A3 vpiši Device ime spremenljivk ki se bodo prenašale preko Modnet protokola
| BYTE | 24 | BYTE | BYTE | 3.V polje A6 vpiši ime krmilnika (npr.:PLC1, če je adresa v spremenljivkah PLC1:.NapakaKoncnega_stikala, drugače pusti polje prazno)
OPC name | DIGITAL | 57 | DIGITAL | DIGITAL | 4. Pritisni gumb 1.KORAK (V poljih C3:C10 se izpiše število spremenljivk, ki imajo Device enak tistemu v polju A3)
PEP | INT | 39 | INT | INT | 5. Pritisni gumb 2.KORAK (V Sheet-u variable_1 se naredi seznam spremenljivk, ki se bodo prenačale preko Modnet protokola)
| LONG | 0 | LONG | LONG | 6. Pritisni gumb 3.KORAK (V poljih C15:C24 se izpiše število spremnljiv po tipih, v poljih F15:F24 se izpiše število potrebni wordow/coilov za prenos spremnljivk)
| REAL | 0 | REAL | REAL | 7. 4.KORAK: V polja C29:C38 je potrebno ročno vpisati začetne naslove spremnljivk. Potrebno je paziti na:
| STRING | 5 | UINT | UINT | *naslov se morajo začeti z lihim številom npr.:1, 101, 551
| UINT | 0 | STRING | STRING | *naslove je potrebno nastaviti tako, da se naslovi sremenljivk ne more prekrivati (naslovi spremenjivk gredo od (začetnega naslova) do (začetnega naslova+število potrebnih wordow))
8. Pritisni gumb 5.KORAK (V Sheet-u variable_2 se naredi seznam spremenljivk, ki so tokrat sortirana po tipih)
9. Pritisni gumb 6.KORAK (V Sheet-u variable_3 se naredi seznam spremenljivk, katerih Device se zamenja z devicom v polju C41)
Trajanje makroja | variable_1 |  |  | 3.KORAK | 10. Pritisni gumb 7.KORAK (V Sheet-u variable_new se generira seznam spremenljivk. To vsebino je potrebno skopirati v variable.dbf)
0 | Tip | število spremenljivk | TIP | št.potrebnih coilov/wordov | *ta korak traja nekoliko dalj časa (odvisno od števila spremenljivk)
| BCD | 0 | BCD | 0 | *če se pojavi težava z adresami ki se začnejo z 0000 (npr.: "00001" se spremeni na "1") je potrebno uporabiti priloženo (prazno) variable.dbf ali v
| BYTE | 0 | BYTE | 0 | ProjectEditoju/VariableTags na poljubni spremenljki nastaviti adreso" 00001"
| DIGITAL | 57 | DIGITAL | 57 (Coil) | 11. Pritisni gumb 8.KORAK in 9.KORAK (V Sheet-u Xsoft se generira koda)
| INT | 63 | INT | 63 (word) | 12. S pritiskom na gumb 10.KORAK se zgenerira EXP koda za Xsoft (Xsoft_EXP)
| LONG | 0 | LONG | 0 (word) | 13. S pritiskom na gumb Save*.EXP se avtomatsko generira datoka *.EXP
| REAL | 0 | REAL | 0 (word)
| STRING | 5 | STRING | 75 (word)
| UINT | 0 | UINT | 0 (word)
POZOR!
*V Sheet-u variable mora biti vsebina skopirana od polja A1 naprej (če je katera vrstica prazna makroji ne bodo delovali pravilno)
*Ena "STRING" spremenljivka zasede 15wordow (to pomeni 29 znakov, 1BYTE=1STRING)
|  | 4.KORAK(vpiši ročno) | variable_2 | 5.KORAK | *Dolžina "STRING" spremenljivk je 29 znakov (lahko tudi več vendar ne z uporabno tega dokumenta in XSoft programa,potrebna je modifikacija makrojev in Xsoft programa)
| Tip | Začetni naslov |  | Sortiraj | *Vsi stringi so enake dolžine (29)
| BCD |  |  | BCD | *"BYTE" spremenljivke se v variable.dbf spremenijo v "INT" (prenašanje posameznih bytov ni mogoče, niti naslavaljanje v citectscadi)
| BYTE |  |  | DIGITAL | *Naslovi spremenljivk se morajo obvezno začeti z lihim naslovom (preizkušeno je z začetnimi naslovi, ki se izpišejo po pritisku na gumb Ponastavi)
| DIGITAL | 1 |  | BYTE | *Z pritiskom na gumb RESET se pobriše vsebina vseh Sheet-ov razen Sheet-a variable (makor reset se izvaja precej časa)
| INT | 1 |  | INT | *makroji ne delujejo pravilno,če je v Sheet-u variable več kot 9999 vrstic oz. spremenljivk (število vseh spremnljivk je prikazano v polju B1)
| LONG | 3001 |  | LONG | *če se vsebine iz variable_new ne gre skpirat v variable.dbf datotek, vsebino skopirajte najprej v *.txt datoteko in nato v variable.dbf
| REAL | 4001 |  | REAL | *v polju A14 na Sheet-u Prva stran se prikazuje število ciklop do konca izvedbe makroja (samo za gumb 7.KORAK)
| STRING | 5001 |  | STRING
| UINT | 6001 |  | UINT
| variable_3 | 6.KORAK | variable_new | 7.KORAK
| New Device name | IOD_PEP_TCP |  | Nova variable dbf
|  |  | xSoft | 8.KORAK in 9.KORAK
xSoft koda
xSoft_EXP
Izvoz*.EXP
1.KORAK
2.KORAK
3.KORAK
5.KORAK
6.KORAK
7.KORAK
8.KORAK
9.KORAK
RESET
Ponastavi
10.KORAK
Save*.EXP

## variable
PEPAlarmPozara | DIGITAL | IOD_PEP | PEP:.AlarmPozara | [6 empty] | 6157 | 1 | 0x04400010
PEPComSCADA | DIGITAL | IOD_PEP | PEP:.ComSCADA | [6 empty] | 6157 | 1 | 0x04400020
PEPComSCADA1 | DIGITAL | IOD_PEP | PEP:.ComSCADA1 | [6 empty] | 6157 | 1 | 0x04400030
PEPDate_Time0 | STRING | IOD_PEP | PEP:.Date_Time[0] | [6 empty] | 6157 | 1 | 0x04400048
PEPDate_Time1 | STRING | IOD_PEP | PEP:.Date_Time[1] | [6 empty] | 6157 | 1 | 0x04400049
PEPDate_Time2 | STRING | IOD_PEP | PEP:.Date_Time[2] | [6 empty] | 6157 | 1 | 0x0440004a
PEPDate_Time3 | STRING | IOD_PEP | PEP:.Date_Time[3] | [6 empty] | 6157 | 1 | 0x0440004b
PEPDateTimeDan | BYTE | IOD_PEP | PEP:.DateTime.Dan | [6 empty] | 6157 | 1 | 0x0440004c
PEPDateTimeLeto | BYTE | IOD_PEP | PEP:.DateTime.Leto | [6 empty] | 6157 | 1 | 0x0440004d
PEPDateTimeLeto2 | INT | IOD_PEP | PEP:.DateTime.Leto2 | [6 empty] | 6157 | 1 | 0x0440004e
PEPDateTimeMesec | BYTE | IOD_PEP | PEP:.DateTime.Mesec | [6 empty] | 6157 | 1 | 0x0440004f
PEPDateTimeMinuta | BYTE | IOD_PEP | PEP:.DateTime.Minuta | [6 empty] | 6157 | 1 | 0x04400050
PEPDateTimeSekunda | BYTE | IOD_PEP | PEP:.DateTime.Sekunda | [6 empty] | 6157 | 1 | 0x04400051
PEPDateTimeUra | BYTE | IOD_PEP | PEP:.DateTime.Ura | [6 empty] | 6157 | 1 | 0x04400052
PEPErrComKlima | DIGITAL | IOD_PEP | PEP:.ErrComKlima | [6 empty] | 6157 | 1 | 0x04400060
PEPErrComPort2 | DIGITAL | IOD_PEP | PEP:.ErrComPort2 | [6 empty] | 6157 | 1 | 0x04400070
PEPErrorComKlimaCode10 | BYTE | IOD_PEP | PEP:.ErrorComKlima.Code[10] | [6 empty] | 6157 | 1 | 0x04400080
PEPErrorComKlimaCode11 | BYTE | IOD_PEP | PEP:.ErrorComKlima.Code[11] | [6 empty] | 6157 | 1 | 0x04400081
PEPErrorComKlimaCode12 | BYTE | IOD_PEP | PEP:.ErrorComKlima.Code[12] | [6 empty] | 6157 | 1 | 0x04400082
PEPErrorComKlimaCode13 | BYTE | IOD_PEP | PEP:.ErrorComKlima.Code[13] | [6 empty] | 6157 | 1 | 0x04400083
PEPErrorComKlimaCode14 | BYTE | IOD_PEP | PEP:.ErrorComKlima.Code[14] | [6 empty] | 6157 | 1 | 0x04400084
PEPErrorComKlimaCode15 | BYTE | IOD_PEP | PEP:.ErrorComKlima.Code[15] | [6 empty] | 6157 | 1 | 0x04400085
PEPErrorComKlimaCode1 | BYTE | IOD_PEP | PEP:.ErrorComKlima.Code[1] | [6 empty] | 6157 | 1 | 0x04400086
PEPErrorComKlimaCode2 | BYTE | IOD_PEP | PEP:.ErrorComKlima.Code[2] | [6 empty] | 6157 | 1 | 0x04400087
PEPErrorComKlimaCode3 | BYTE | IOD_PEP | PEP:.ErrorComKlima.Code[3] | [6 empty] | 6157 | 1 | 0x04400088
PEPErrorComKlimaCode4 | BYTE | IOD_PEP | PEP:.ErrorComKlima.Code[4] | [6 empty] | 6157 | 1 | 0x04400089
PEPErrorComKlimaCode5 | BYTE | IOD_PEP | PEP:.ErrorComKlima.Code[5] | [6 empty] | 6157 | 1 | 0x0440008a
PEPErrorComKlimaCode6 | BYTE | IOD_PEP | PEP:.ErrorComKlima.Code[6] | [6 empty] | 6157 | 1 | 0x0440008b
PEPErrorComKlimaCode7 | BYTE | IOD_PEP | PEP:.ErrorComKlima.Code[7] | [6 empty] | 6157 | 1 | 0x0440008c
PEPErrorComKlimaCode8 | BYTE | IOD_PEP | PEP:.ErrorComKlima.Code[8] | [6 empty] | 6157 | 1 | 0x0440008d
PEPErrorComKlimaCode9 | BYTE | IOD_PEP | PEP:.ErrorComKlima.Code[9] | [6 empty] | 6157 | 1 | 0x0440008e
PEPErrorComKlimaError | DIGITAL | IOD_PEP | PEP:.ErrorComKlima.Error | [6 empty] | 6157 | 1 | 0x04400090
PEPErrorComKlimaStatus | INT | IOD_PEP | PEP:.ErrorComKlima.Status | [6 empty] | 6157 | 1 | 0x044000a0
PEPHIA1_vlaga_s | INT | IOD_PEP | PEP:.HIA1_vlaga_s | 0 | 1000 | 0 | 100.0 | % | ###.# | 6157 | 1 | 0x044000a2
PEPKlima1Alarm_pozar | DIGITAL | IOD_PEP | PEP:.Klima[1].Alarm_pozar | [6 empty] | 6157 | 1 | 0x044000b0
PEPKlima1Analog_izh_mesanje | INT | IOD_PEP | PEP:.Klima[1].Analog_izh_mesanje | [6 empty] | 6157 | 1 | 0x044000c0
PEPKlima1Analog_izh_rekuperator | INT | IOD_PEP | PEP:.Klima[1].Analog_izh_rekuperator | [6 empty] | 6157 | 1 | 0x044000c1
PEPKlima1Analog_izh_VentGrelnika | INT | IOD_PEP | PEP:.Klima[1].Analog_izh_VentGrelnika | [6 empty] | 6157 | 1 | 0x044000c2
PEPKlima1Analog_izh_VentHlajenja | INT | IOD_PEP | PEP:.Klima[1].Analog_izh_VentHlajenja | [6 empty] | 6157 | 1 | 0x044000c3
PEPKlima1Dejanska_zel_temp | INT | IOD_PEP | PEP:.Klima[1].Dejanska_zel_temp | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 1 | 0x044000c4
PEPKlima1DelVentHit1 | DIGITAL | IOD_PEP | PEP:.Klima[1].DelVentHit1 | 0 | 1000 | 0 | 1000 | % | ###.# | 6157 | 1 | 0x044000d0
PEPKlima1DelVentHit2 | DIGITAL | IOD_PEP | PEP:.Klima[1].DelVentHit2 | 0 | 1000 | 0 | 1000 | % | ###.# | 6157 | 1 | 0x044000e0
PEPKlima1Hitrost_del_vent_disp | INT | IOD_PEP | PEP:.Klima[1].Hitrost_del_vent_disp | 0 | 100 | 0 | 100 | Hz | ##.# | 6157 | 1 | 0x044000f0
PEPKlima1Max_vpih | INT | IOD_PEP | PEP:.Klima[1].Max_vpih | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 1 | 0x044000f1
PEPKlima1Min_vpih | INT | IOD_PEP | PEP:.Klima[1].Min_vpih | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 1 | 0x044000f2
PEPKlima1Ni_pretoka | DIGITAL | IOD_PEP | PEP:.Klima[1].Ni_pretoka | [6 empty] | 6157 | 1 | 0x04400100
PEPKlima1Obrat_ure_Vent_h1 | INT | IOD_PEP | PEP:.Klima[1].Obrat_ure_Vent_h1 | [6 empty] | 6157 | 1 | 0x04400110
PEPKlima1Obrat_ure_Vent_h2 | INT | IOD_PEP | PEP:.Klima[1].Obrat_ure_Vent_h2 | [6 empty] | 6157 | 1 | 0x04400111
PEPKlima1OkvaraRototerm | DIGITAL | IOD_PEP | PEP:.Klima[1].OkvaraRototerm | [6 empty] | 6157 | 1 | 0x04400120
PEPKlima1OkvaraVlazNap | DIGITAL | IOD_PEP | PEP:.Klima[1].OkvaraVlazNap | [6 empty] | 6157 | 1 | 0x04400130
PEPKlima1Pol_komp_konec | INT | IOD_PEP | PEP:.Klima[1].Pol_komp_konec | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 1 | 0x04400140
PEPKlima1Pol_komp_sprem_zel_vr | INT | IOD_PEP | PEP:.Klima[1].Pol_komp_sprem_zel_vr | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 1 | 0x04400141
PEPKlima1Pol_komp_zacetek | INT | IOD_PEP | PEP:.Klima[1].Pol_komp_zacetek | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 1 | 0x04400142
PEPKlima1PreklopHitDelVent | INT | IOD_PEP | PEP:.Klima[1].PreklopHitDelVent | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 1 | 0x04400143
PEPKlima1PreobMotCrpGrel | DIGITAL | IOD_PEP | PEP:.Klima[1].PreobMotCrpGrel | [6 empty] | 6157 | 1 | 0x04400150
PEPKlima1PreobMotVent | DIGITAL | IOD_PEP | PEP:.Klima[1].PreobMotVent | [6 empty] | 6157 | 1 | 0x04400160
PEPKlima1Protizamrz_zascita | INT | IOD_PEP | PEP:.Klima[1].Protizamrz_zascita | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 1 | 0x04400170
PEPKlima1ProtizamrzZascAktivna | DIGITAL | IOD_PEP | PEP:.Klima[1].ProtizamrzZascAktivna | [6 empty] | 6157 | 1 | 0x04400180
PEPKlima1Rezim_delovanja | INT | IOD_PEP | PEP:.Klima[1].Rezim_delovanja | [6 empty] | 6157 | 1 | 0x04400190
PEPKlima1Temperatura_dovoda | INT | IOD_PEP | PEP:.Klima[1].Temperatura_dovoda | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 1 | 0x04400191
PEPKlima1Temperatura_prostora | INT | IOD_PEP | PEP:.Klima[1].Temperatura_prostora | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 1 | 0x04400192
PEPKlima1TempPredPloscnimRekup | INT | IOD_PEP | PEP:.Klima[1].TempPredPloscnimRekup | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 1 | 0x04400193
PEPKlima1TempZaPloscnimRekup | INT | IOD_PEP | PEP:.Klima[1].TempZaPloscnimRekup | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 1 | 0x04400194
PEPKlima1VklopRegKlimata | DIGITAL | IOD_PEP | PEP:.Klima[1].VklopRegKlimata | [6 empty] | 6157 | 1 | 0x044001a0
PEPKlima1Vlaga_v_prostoru | INT | IOD_PEP | PEP:.Klima[1].Vlaga_v_prostoru | 0 | 1000 | 0 | 100 | % | ##.# | 6157 | 1 | 0x044001b0
PEPKlima1VlagaVstopZrakaProstor | INT | IOD_PEP | PEP:.Klima[1].VlagaVstopZrakaProstor | 0 | 1000 | 0 | 100 | % | ##.# | 6157 | 1 | 0x044001b1
PEPKlima1ZamasenostFiltra | DIGITAL | IOD_PEP | PEP:.Klima[1].ZamasenostFiltra | [6 empty] | 6157 | 1 | 0x044001c0
PEPKlima1ZdruzAlarmA | DIGITAL | IOD_PEP | PEP:.Klima[1].ZdruzAlarmA | [6 empty] | 6157 | 1 | 0x044001d0
PEPKlima1ZdruzAlarmB | DIGITAL | IOD_PEP | PEP:.Klima[1].ZdruzAlarmB | [6 empty] | 6157 | 1 | 0x044001e0
PEPKlima1Zel_temp_eko_gretja | INT | IOD_PEP | PEP:.Klima[1].Zel_temp_eko_gretja | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 1 | 0x044001f0
PEPKlima1Zel_temp_eko_hlajenja | INT | IOD_PEP | PEP:.Klima[1].Zel_temp_eko_hlajenja | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 1 | 0x044001f1
PEPKlima1Zel_temp_komf_gretja | INT | IOD_PEP | PEP:.Klima[1].Zel_temp_komf_gretja | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 1 | 0x044001f2
PEPKlima1Zel_temp_komf_hlajenja | INT | IOD_PEP | PEP:.Klima[1].Zel_temp_komf_hlajenja | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 1 | 0x044001f3
PEPKlima1Zim_komp_konec | INT | IOD_PEP | PEP:.Klima[1].Zim_komp_konec | -400 | 600 | -40 | 60.0 | °C | ##.# | 6157 | 1 | 0x044001f4
PEPKlima1Zim_komp_sprem_zel_vr | INT | IOD_PEP | PEP:.Klima[1].Zim_komp_sprem_zel_vr | -400 | 600 | -40 | 60.0 | °C | ##.# | 6157 | 1 | 0x044001f5
PEPKlima1Zim_komp_zacetek | INT | IOD_PEP | PEP:.Klima[1].Zim_komp_zacetek | -400 | 600 | -40 | 60.0 | °C | ##.# | 6157 | 1 | 0x044001f6
PEPKlima1ZimKompMinVpihKonec | INT | IOD_PEP | PEP:.Klima[1].ZimKompMinVpihKonec | -400 | 600 | -40 | 60.0 | °C | ##.# | 6157 | 1 | 0x044001f7
PEPKlima1ZimKompMinVpihZac | INT | IOD_PEP | PEP:.Klima[1].ZimKompMinVpihZac | -400 | 600 | -40 | 60.0 | °C | ##.# | 6157 | 1 | 0x044001f8
PEPKlima1ZkompMinVpihSpremZelVr | INT | IOD_PEP | PEP:.Klima[1].ZkompMinVpihSpremZelVr | -400 | 600 | -40 | 60.0 | °C | ##.# | 6157 | 1 | 0x044001f9
PEPKlima1Zunanja_temp | INT | IOD_PEP | PEP:.Klima[1].Zunanja_temp | -400 | 600 | -40 | 60.0 | °C | ##.# | 6157 | 1 | 0x044001fa
PEPKlima_rezim | BYTE | IOD_PEP | PEP:.Klima_rezim | [6 empty] | 6157 | 1 | 0x044001fb
PEPKLIMAT_delovanje | DIGITAL | IOD_PEP | PEP:.KLIMAT_delovanje | [6 empty] | 6157 | 1 | 0x04400200
PEPKLIMAT_napaka | DIGITAL | IOD_PEP | PEP:.KLIMAT_napaka | [6 empty] | 6157 | 1 | 0x04400210
PEPKLIMAT_rezim1 | DIGITAL | IOD_PEP | PEP:.KLIMAT_rezim1 | [6 empty] | 6157 | 1 | 0x04400220
PEPKLIMAT_rezim2 | DIGITAL | IOD_PEP | PEP:.KLIMAT_rezim2 | [6 empty] | 6157 | 1 | 0x04400230
PEPKlimaZdruzenAlarm | DIGITAL | IOD_PEP | PEP:.KlimaZdruzenAlarm | [6 empty] | 6157 | 1 | 0x04400240
PEPKomunikacijaErr | DIGITAL | IOD_PEP | PEP:.KomunikacijaErr | [6 empty] | 6157 | 1 | 0x04400250
PEPMEHCALEC_delovanje | DIGITAL | IOD_PEP | PEP:.MEHCALEC_delovanje | [6 empty] | 6157 | 1 | 0x04400260
PEPMEHCALEC_napaka | DIGITAL | IOD_PEP | PEP:.MEHCALEC_napaka | [6 empty] | 6157 | 1 | 0x04400270
PEPN_KLIMAT_napaka | DIGITAL | IOD_PEP | PEP:.N_KLIMAT_napaka | [6 empty] | 6157 | 1 | 0x04400280
PEPN_ROTOTERM_napaka | DIGITAL | IOD_PEP | PEP:.N_ROTOTERM_napaka | [6 empty] | 6157 | 1 | 0x04400290
PEPnapaka_kom_panel | DIGITAL | IOD_PEP | PEP:.napaka_kom_panel | [6 empty] | 6157 | 1 | 0x044002a0
PEPnapaka_kom_scada | DIGITAL | IOD_PEP | PEP:.napaka_kom_scada | [6 empty] | 6157 | 1 | 0x044002b0
PEPNapakaSenzorVlagaHIA1 | DIGITAL | IOD_PEP | PEP:.NapakaSenzorVlagaHIA1 | [6 empty] | 6157 | 1 | 0x044002c0
PEPNapakaTSTempTIA1 | DIGITAL | IOD_PEP | PEP:.NapakaTSTempTIA1 | [6 empty] | 6157 | 1 | 0x044002d0
PEPNiPretoka | DIGITAL | IOD_PEP | PEP:.NiPretoka | [6 empty] | 6157 | 1 | 0x044002e0
PEPOkvaraRototerma | DIGITAL | IOD_PEP | PEP:.OkvaraRototerma | [6 empty] | 6157 | 1 | 0x044002f0
PEPOkvaraVlazNap | DIGITAL | IOD_PEP | PEP:.OkvaraVlazNap | [6 empty] | 6157 | 1 | 0x04400300
PEPPreobMotCrpGr | DIGITAL | IOD_PEP | PEP:.PreobMotCrpGr | [6 empty] | 6157 | 1 | 0x04400310
PEPPreobMotVent | DIGITAL | IOD_PEP | PEP:.PreobMotVent | [6 empty] | 6157 | 1 | 0x04400320
PEPProtizamrzZascAkt | DIGITAL | IOD_PEP | PEP:.ProtizamrzZascAkt | [6 empty] | 6157 | 1 | 0x04400330
PEPROTOTERM_napaka | DIGITAL | IOD_PEP | PEP:.ROTOTERM_napaka | [6 empty] | 6157 | 1 | 0x04400340
PEPSetDateTime | DIGITAL | IOD_PEP | PEP:.SetDateTime | [6 empty] | 6157 | 1 | 0x04400350
PEPSetDateTimeDemand | DIGITAL | IOD_PEP | PEP:.SetDateTimeDemand | [6 empty] | 6157 | 1 | 0x04400360
PEPSetDateTimeError | DIGITAL | IOD_PEP | PEP:.SetDateTimeError | [6 empty] | 6157 | 1 | 0x04400370
PEPSetDateTimeFinished | DIGITAL | IOD_PEP | PEP:.SetDateTimeFinished | [6 empty] | 6157 | 1 | 0x04400380
PEPSlabaBaterijaPLC | DIGITAL | IOD_PEP | PEP:.SlabaBaterijaPLC | [6 empty] | 6157 | 1 | 0x04400390
PEPTIA1_alarm | INT | IOD_PEP | PEP:.TIA1_alarm | 0 | 60 | 0 | 60 | °C | ## | 6157 | 1 | 0x044003a8
PEPTIA1_previs_temp | DIGITAL | IOD_PEP | PEP:.TIA1_previs_temp | [6 empty] | 6157 | 1 | 0x044003b0
PEPTIA1_temp_s | INT | IOD_PEP | PEP:.TIA1_temp_s | 0 | 600 | 0 | 60.0 | °C | ##.# | 6157 | 1 | 0x044003c1
PEPups_alarm | DIGITAL | IOD_PEP | PEP:.ups_alarm | [6 empty] | 6157 | 1 | 0x044003d0
PEPups_baterijski_nac | DIGITAL | IOD_PEP | PEP:.ups_baterijski_nac | [6 empty] | 6157 | 1 | 0x044003e0
PEPups_polnjenje | DIGITAL | IOD_PEP | PEP:.ups_polnjenje | [6 empty] | 6157 | 1 | 0x044003f0
PEPUserCurrentLevel | BYTE | IOD_PEP | PEP:.UserCurrentLevel | [6 empty] | 6157 | 1 | 0x04400400
PEPUserCurrentName | STRING | IOD_PEP | PEP:.UserCurrentName | [6 empty] | 6157 | 1 | 0x04400401
PEPUserLoggedIn | DIGITAL | IOD_PEP | PEP:.UserLoggedIn | [6 empty] | 6157 | 1 | 0x04400410
PEPVLAZILEC_delovanje | DIGITAL | IOD_PEP | PEP:.VLAZILEC_delovanje | [6 empty] | 6157 | 1 | 0x04400420
PEPVLAZILEC_napaka | DIGITAL | IOD_PEP | PEP:.VLAZILEC_napaka | [6 empty] | 6157 | 1 | 0x04400430
PEPXVH_AlarmOn | DIGITAL | IOD_PEP | PEP:.XVH_AlarmOn | [6 empty] | 6157 | 1 | 0x04400440
PEPXVH_UPSstatus | BYTE | IOD_PEP | PEP:.XVH_UPSstatus | [6 empty] | 6157 | 1 | 0x04400450
PEPZamasenostFiltra | DIGITAL | IOD_PEP | PEP:.ZamasenostFiltra | [6 empty] | 6157 | 1 | 0x04400460
APEP_omogoci_sms | DIGITAL | IOD_PEP_disk | D24[40] | [8 empty] | 0x04400470
BPEP_omogoci_sms | DIGITAL | IOD_PEP_disk | D64[40] | [8 empty] | 0x04400480
CPEP_omogoci_sms | DIGITAL | IOD_PEP_disk | D104[40] | [8 empty] | 0x04400490
DPEP_omogoci_sms | DIGITAL | IOD_PEP_disk | D144[40] | [8 empty] | 0x044004a0
EPEP_omogoci_sms | DIGITAL | IOD_PEP_disk | D184[40] | [8 empty] | 0x044004b0
FPEP_omogoci_sms | DIGITAL | IOD_PEP_disk | D224[40] | [8 empty] | 0x044004c0
PEPN_KLIMAT_napaka_omog | DIGITAL | IOD_PEP_disk | D266 | [8 empty] | 0x044004d0
PEPN_ROTOTERM_napaka_omog | DIGITAL | IOD_PEP_disk | D267 | [8 empty] | 0x044004e0
PEPN_VLAZILEC_napaka_omog | DIGITAL | IOD_PEP_disk | D268 | [8 empty] | 0x044004f0
PEPErrComKlima_omog | DIGITAL | IOD_PEP_disk | D269 | [8 empty] | 0x04400500
PEPSetDateTimeError_omog | DIGITAL | IOD_PEP_disk | D270 | [8 empty] | 0x04400510
PEPErrComPort2_omog | DIGITAL | IOD_PEP_disk | D271 | [8 empty] | 0x04400520
PEPKlima1Alarm_pozar_omog | DIGITAL | IOD_PEP_disk | D272 | [8 empty] | 0x04400530
PEPKlimaZdruzenAlarm_omog | DIGITAL | IOD_PEP_disk | D273 | [8 empty] | 0x04400540
PEPKlima1Ni_pretoka_omog | DIGITAL | IOD_PEP_disk | D274 | [8 empty] | 0x04400550
PEPKlima1OkvaraRototerm_omog | DIGITAL | IOD_PEP_disk | D275 | [8 empty] | 0x04400560
PEPKlima1OkvaraVlazNap_omog | DIGITAL | IOD_PEP_disk | D276 | [8 empty] | 0x04400570
PEPKlima1PreobMotCrpGrel_omog | DIGITAL | IOD_PEP_disk | D277 | [8 empty] | 0x04400580
PEPKlima1PreobMotVent_omog | DIGITAL | IOD_PEP_disk | D278 | [8 empty] | 0x04400590
PEPKlima1ProtizamrzZascAktivna_omog | DIGITAL | IOD_PEP_disk | D279 | [8 empty] | 0x044005a0
PEPKlima1ZamasenostFiltra_omog | DIGITAL | IOD_PEP_disk | D280 | [8 empty] | 0x044005b0
PEPOkvaraRototerma_omog | DIGITAL | IOD_PEP_disk | D281 | [8 empty] | 0x044005c0
PEPOkvaraVlazNap_omog | DIGITAL | IOD_PEP_disk | D282 | [8 empty] | 0x044005d0
PEPTIA1_previs_temp_omog | DIGITAL | IOD_PEP_disk | D283 | [8 empty] | 0x044005e0
PEPUserLoggedIn_mem | DIGITAL | IOD_PEP_disk | D284 | [8 empty] | 0x044005f0
PEPMEHCALEC_napaka_om | DIGITAL | IOD_PEP_disk | D285 | [8 empty] | 0x04400600
PEP_Sekunda1s_utripanje | DIGITAL | IOD_PEP_mem | D1 | [8 empty] | 0x04400610
PEP_Prikaz_klimata_ce_je1 | DIGITAL | IOD_PEP_mem | D2 | [8 empty] | 0x04400620
PEP_Prikaz_temp_v_ce_je1 | DIGITAL | IOD_PEP_mem | D3 | [8 empty] | 0x04400630
PEP_Prikaz_vlazilec_ce_je1 | DIGITAL | IOD_PEP_mem | D4 | [8 empty] | 0x04400640
PEP_prikaz_ups_ce_je1 | DIGITAL | IOD_PEP_mem | D5 | [8 empty] | 0x04400650
PEP_prikaz_rototerm_ce_je1 | DIGITAL | IOD_PEP_mem | D6 | [8 empty] | 0x04400660
PEPKLIMAT_napaka_omog | DIGITAL | IOD_PEP_disk | D7 | [8 empty] | 0x04400670
PEPROTOTERM_napaka_omog | DIGITAL | IOD_PEP_disk | D8 | [8 empty] | 0x04400680
PEPups_alarm_omog | DIGITAL | IOD_PEP_disk | D9 | [8 empty] | 0x04400690
PEPVLAZILEC_napaka_omog | DIGITAL | IOD_PEP_disk | D10 | [8 empty] | 0x044006a0
PEPNapakaSenzorVlagaHIA1_omog | DIGITAL | IOD_PEP_disk | D11 | [8 empty] | 0x044006b0
PEPNapakaTSTempTIA1_omog | DIGITAL | IOD_PEP_disk | D12 | [8 empty] | 0x044006c0
PEPComSCADA_stevec1 | INT | IOD_PEP_mem | I13 | [8 empty] | 0x044006d0
PEPComSCADA_stevec2 | INT | IOD_PEP_mem | I14 | [8 empty] | 0x044006d1
PEPnapaka_kom_scada_omog | DIGITAL | IOD_PEP_disk | D15 | [8 empty] | 0x044006e0
PEPnapaka_kom_panel_omog | DIGITAL | IOD_PEP_disk | D16 | [8 empty] | 0x044006f0
PEPKLIMAT_delovanje_omog | DIGITAL | IOD_PEP_disk | D17 | [8 empty] | 0x04400700
PEPROTOTERM_delovanje_omog | DIGITAL | IOD_PEP_disk | D18 | [8 empty] | 0x04400710
PEPups_baterijski_nac_omog | DIGITAL | IOD_PEP_disk | D19 | [8 empty] | 0x04400720
PEPups_polnjenje_omog | DIGITAL | IOD_PEP_disk | D20 | [8 empty] | 0x04400730
PEPVLAZILEC_delovanje_omog | DIGITAL | IOD_PEP_disk | D21 | [8 empty] | 0x04400740
PEPSlabaBaterijaPLC_omog | DIGITAL | IOD_PEP_disk | D22 | [8 empty] | 0x04400750
PEPnapaka_kom_krm_omogoci | DIGITAL | IOD_PEP_disk | D23 | [8 empty] | 0x04400760
PEPKLIMAT_delovanje_omogoci | DIGITAL | IOD_PEP_disk | D286 | [8 empty] | 0x04400770
PEPKlima1VklopRegKlimata_omogoci | DIGITAL | IOD_PEP_disk | D287 | [8 empty] | 0x04400780
PEPKlima_rezim1_omogoci | DIGITAL | IOD_PEP_disk | D288 | [8 empty] | 0x04400790
PEPKlima_rezim2_omogoci | DIGITAL | IOD_PEP_disk | D289 | [8 empty] | 0x044007a0
PEPKlima_rezim3_omogoci | DIGITAL | IOD_PEP_disk | D290 | [8 empty] | 0x044007b0
PEPKlima_rezim4_omogoci | DIGITAL | IOD_PEP_disk | D291 | [8 empty] | 0x044007c0
PEPnapaka_kom_scada2 | DIGITAL | IOD_PEP | PEP:.napaka_kom_scada2 | [8 empty] | 0x044007d0
PEPComSCADA2 | DIGITAL | IOD_PEP | PEP:.ComSCADA2 | [8 empty] | 0x044007e0
PEPnapaka_kom_krm_omogoci2 | DIGITAL | IOD_PEP_disk | D295 | [8 empty] | 0x044007f0
PEPServer_A_Izpad | DIGITAL | IOD_PEP_disk | D296 | [8 empty] | 0x04400800
PEPServer_B_Izpad | DIGITAL | IOD_PEP_disk | D297 | [8 empty] | 0x04400810
PEPComSCADA_stevec3 | INT | IOD_PEP_mem | I298 | [8 empty] | 0x04400820
PEPComSCADA_stevec | INT | IOD_PEP_mem | I300 | [8 empty] | 0x04400821
PEPComSCADA3 | DIGITAL | IOD_PEP | PEP:.ComSCADA3 | [8 empty] | 0x04400830
PEPkom_nast_cas_izpada | INT | IOD_PEP | PEP:.kom_nast_cas_izpada | [8 empty] | 0x04400840

## variable_1
PEPAlarmPozara | DIGITAL | IOD_PEP | PEP:.AlarmPozara
PEPComSCADA | DIGITAL | IOD_PEP | PEP:.ComSCADA
PEPComSCADA1 | DIGITAL | IOD_PEP | PEP:.ComSCADA1
PEPDate_Time0 | STRING | IOD_PEP | PEP:.Date_Time[0]
PEPDate_Time1 | STRING | IOD_PEP | PEP:.Date_Time[1]
PEPDate_Time2 | STRING | IOD_PEP | PEP:.Date_Time[2]
PEPDate_Time3 | STRING | IOD_PEP | PEP:.Date_Time[3]
PEPDateTimeDan | INT | IOD_PEP | PEP:.DateTime.Dan | BYTE
PEPDateTimeLeto | INT | IOD_PEP | PEP:.DateTime.Leto | BYTE
PEPDateTimeLeto2 | INT | IOD_PEP | PEP:.DateTime.Leto2
PEPDateTimeMesec | INT | IOD_PEP | PEP:.DateTime.Mesec | BYTE
PEPDateTimeMinuta | INT | IOD_PEP | PEP:.DateTime.Minuta | BYTE
PEPDateTimeSekunda | INT | IOD_PEP | PEP:.DateTime.Sekunda | BYTE
PEPDateTimeUra | INT | IOD_PEP | PEP:.DateTime.Ura | BYTE
PEPErrComKlima | DIGITAL | IOD_PEP | PEP:.ErrComKlima
PEPErrComPort2 | DIGITAL | IOD_PEP | PEP:.ErrComPort2
PEPErrorComKlimaCode10 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[10] | BYTE
PEPErrorComKlimaCode11 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[11] | BYTE
PEPErrorComKlimaCode12 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[12] | BYTE
PEPErrorComKlimaCode13 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[13] | BYTE
PEPErrorComKlimaCode14 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[14] | BYTE
PEPErrorComKlimaCode15 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[15] | BYTE
PEPErrorComKlimaCode1 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[1] | BYTE
PEPErrorComKlimaCode2 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[2] | BYTE
PEPErrorComKlimaCode3 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[3] | BYTE
PEPErrorComKlimaCode4 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[4] | BYTE
PEPErrorComKlimaCode5 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[5] | BYTE
PEPErrorComKlimaCode6 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[6] | BYTE
PEPErrorComKlimaCode7 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[7] | BYTE
PEPErrorComKlimaCode8 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[8] | BYTE
PEPErrorComKlimaCode9 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[9] | BYTE
PEPErrorComKlimaError | DIGITAL | IOD_PEP | PEP:.ErrorComKlima.Error
PEPErrorComKlimaStatus | INT | IOD_PEP | PEP:.ErrorComKlima.Status
PEPHIA1_vlaga_s | INT | IOD_PEP | PEP:.HIA1_vlaga_s
PEPKlima1Alarm_pozar | DIGITAL | IOD_PEP | PEP:.Klima[1].Alarm_pozar
PEPKlima1Analog_izh_mesanje | INT | IOD_PEP | PEP:.Klima[1].Analog_izh_mesanje
PEPKlima1Analog_izh_rekuperator | INT | IOD_PEP | PEP:.Klima[1].Analog_izh_rekuperator
PEPKlima1Analog_izh_VentGrelnika | INT | IOD_PEP | PEP:.Klima[1].Analog_izh_VentGrelnika
PEPKlima1Analog_izh_VentHlajenja | INT | IOD_PEP | PEP:.Klima[1].Analog_izh_VentHlajenja
PEPKlima1Dejanska_zel_temp | INT | IOD_PEP | PEP:.Klima[1].Dejanska_zel_temp
PEPKlima1DelVentHit1 | DIGITAL | IOD_PEP | PEP:.Klima[1].DelVentHit1
PEPKlima1DelVentHit2 | DIGITAL | IOD_PEP | PEP:.Klima[1].DelVentHit2
PEPKlima1Hitrost_del_vent_disp | INT | IOD_PEP | PEP:.Klima[1].Hitrost_del_vent_disp
PEPKlima1Max_vpih | INT | IOD_PEP | PEP:.Klima[1].Max_vpih
PEPKlima1Min_vpih | INT | IOD_PEP | PEP:.Klima[1].Min_vpih
PEPKlima1Ni_pretoka | DIGITAL | IOD_PEP | PEP:.Klima[1].Ni_pretoka
PEPKlima1Obrat_ure_Vent_h1 | INT | IOD_PEP | PEP:.Klima[1].Obrat_ure_Vent_h1
PEPKlima1Obrat_ure_Vent_h2 | INT | IOD_PEP | PEP:.Klima[1].Obrat_ure_Vent_h2
PEPKlima1OkvaraRototerm | DIGITAL | IOD_PEP | PEP:.Klima[1].OkvaraRototerm
PEPKlima1OkvaraVlazNap | DIGITAL | IOD_PEP | PEP:.Klima[1].OkvaraVlazNap
PEPKlima1Pol_komp_konec | INT | IOD_PEP | PEP:.Klima[1].Pol_komp_konec
PEPKlima1Pol_komp_sprem_zel_vr | INT | IOD_PEP | PEP:.Klima[1].Pol_komp_sprem_zel_vr
PEPKlima1Pol_komp_zacetek | INT | IOD_PEP | PEP:.Klima[1].Pol_komp_zacetek
PEPKlima1PreklopHitDelVent | INT | IOD_PEP | PEP:.Klima[1].PreklopHitDelVent
PEPKlima1PreobMotCrpGrel | DIGITAL | IOD_PEP | PEP:.Klima[1].PreobMotCrpGrel
PEPKlima1PreobMotVent | DIGITAL | IOD_PEP | PEP:.Klima[1].PreobMotVent
PEPKlima1Protizamrz_zascita | INT | IOD_PEP | PEP:.Klima[1].Protizamrz_zascita
PEPKlima1ProtizamrzZascAktivna | DIGITAL | IOD_PEP | PEP:.Klima[1].ProtizamrzZascAktivna
PEPKlima1Rezim_delovanja | INT | IOD_PEP | PEP:.Klima[1].Rezim_delovanja
PEPKlima1Temperatura_dovoda | INT | IOD_PEP | PEP:.Klima[1].Temperatura_dovoda
PEPKlima1Temperatura_prostora | INT | IOD_PEP | PEP:.Klima[1].Temperatura_prostora
PEPKlima1TempPredPloscnimRekup | INT | IOD_PEP | PEP:.Klima[1].TempPredPloscnimRekup
PEPKlima1TempZaPloscnimRekup | INT | IOD_PEP | PEP:.Klima[1].TempZaPloscnimRekup
PEPKlima1VklopRegKlimata | DIGITAL | IOD_PEP | PEP:.Klima[1].VklopRegKlimata
PEPKlima1Vlaga_v_prostoru | INT | IOD_PEP | PEP:.Klima[1].Vlaga_v_prostoru
PEPKlima1VlagaVstopZrakaProstor | INT | IOD_PEP | PEP:.Klima[1].VlagaVstopZrakaProstor
PEPKlima1ZamasenostFiltra | DIGITAL | IOD_PEP | PEP:.Klima[1].ZamasenostFiltra
PEPKlima1ZdruzAlarmA | DIGITAL | IOD_PEP | PEP:.Klima[1].ZdruzAlarmA
PEPKlima1ZdruzAlarmB | DIGITAL | IOD_PEP | PEP:.Klima[1].ZdruzAlarmB
PEPKlima1Zel_temp_eko_gretja | INT | IOD_PEP | PEP:.Klima[1].Zel_temp_eko_gretja
PEPKlima1Zel_temp_eko_hlajenja | INT | IOD_PEP | PEP:.Klima[1].Zel_temp_eko_hlajenja
PEPKlima1Zel_temp_komf_gretja | INT | IOD_PEP | PEP:.Klima[1].Zel_temp_komf_gretja
PEPKlima1Zel_temp_komf_hlajenja | INT | IOD_PEP | PEP:.Klima[1].Zel_temp_komf_hlajenja
PEPKlima1Zim_komp_konec | INT | IOD_PEP | PEP:.Klima[1].Zim_komp_konec
PEPKlima1Zim_komp_sprem_zel_vr | INT | IOD_PEP | PEP:.Klima[1].Zim_komp_sprem_zel_vr
PEPKlima1Zim_komp_zacetek | INT | IOD_PEP | PEP:.Klima[1].Zim_komp_zacetek
PEPKlima1ZimKompMinVpihKonec | INT | IOD_PEP | PEP:.Klima[1].ZimKompMinVpihKonec
PEPKlima1ZimKompMinVpihZac | INT | IOD_PEP | PEP:.Klima[1].ZimKompMinVpihZac
PEPKlima1ZkompMinVpihSpremZelVr | INT | IOD_PEP | PEP:.Klima[1].ZkompMinVpihSpremZelVr
PEPKlima1Zunanja_temp | INT | IOD_PEP | PEP:.Klima[1].Zunanja_temp
PEPKlima_rezim | INT | IOD_PEP | PEP:.Klima_rezim | BYTE
PEPKLIMAT_delovanje | DIGITAL | IOD_PEP | PEP:.KLIMAT_delovanje
PEPKLIMAT_napaka | DIGITAL | IOD_PEP | PEP:.KLIMAT_napaka
PEPKLIMAT_rezim1 | DIGITAL | IOD_PEP | PEP:.KLIMAT_rezim1
PEPKLIMAT_rezim2 | DIGITAL | IOD_PEP | PEP:.KLIMAT_rezim2
PEPKlimaZdruzenAlarm | DIGITAL | IOD_PEP | PEP:.KlimaZdruzenAlarm
PEPKomunikacijaErr | DIGITAL | IOD_PEP | PEP:.KomunikacijaErr
PEPMEHCALEC_delovanje | DIGITAL | IOD_PEP | PEP:.MEHCALEC_delovanje
PEPMEHCALEC_napaka | DIGITAL | IOD_PEP | PEP:.MEHCALEC_napaka
PEPN_KLIMAT_napaka | DIGITAL | IOD_PEP | PEP:.N_KLIMAT_napaka
PEPN_ROTOTERM_napaka | DIGITAL | IOD_PEP | PEP:.N_ROTOTERM_napaka
PEPnapaka_kom_panel | DIGITAL | IOD_PEP | PEP:.napaka_kom_panel
PEPnapaka_kom_scada | DIGITAL | IOD_PEP | PEP:.napaka_kom_scada
PEPNapakaSenzorVlagaHIA1 | DIGITAL | IOD_PEP | PEP:.NapakaSenzorVlagaHIA1
PEPNapakaTSTempTIA1 | DIGITAL | IOD_PEP | PEP:.NapakaTSTempTIA1
PEPNiPretoka | DIGITAL | IOD_PEP | PEP:.NiPretoka
PEPOkvaraRototerma | DIGITAL | IOD_PEP | PEP:.OkvaraRototerma
PEPOkvaraVlazNap | DIGITAL | IOD_PEP | PEP:.OkvaraVlazNap
PEPPreobMotCrpGr | DIGITAL | IOD_PEP | PEP:.PreobMotCrpGr
PEPPreobMotVent | DIGITAL | IOD_PEP | PEP:.PreobMotVent
PEPProtizamrzZascAkt | DIGITAL | IOD_PEP | PEP:.ProtizamrzZascAkt
PEPROTOTERM_napaka | DIGITAL | IOD_PEP | PEP:.ROTOTERM_napaka
PEPSetDateTime | DIGITAL | IOD_PEP | PEP:.SetDateTime
PEPSetDateTimeDemand | DIGITAL | IOD_PEP | PEP:.SetDateTimeDemand
PEPSetDateTimeError | DIGITAL | IOD_PEP | PEP:.SetDateTimeError
PEPSetDateTimeFinished | DIGITAL | IOD_PEP | PEP:.SetDateTimeFinished
PEPSlabaBaterijaPLC | DIGITAL | IOD_PEP | PEP:.SlabaBaterijaPLC
PEPTIA1_alarm | INT | IOD_PEP | PEP:.TIA1_alarm
PEPTIA1_previs_temp | DIGITAL | IOD_PEP | PEP:.TIA1_previs_temp
PEPTIA1_temp_s | INT | IOD_PEP | PEP:.TIA1_temp_s
PEPups_alarm | DIGITAL | IOD_PEP | PEP:.ups_alarm
PEPups_baterijski_nac | DIGITAL | IOD_PEP | PEP:.ups_baterijski_nac
PEPups_polnjenje | DIGITAL | IOD_PEP | PEP:.ups_polnjenje
PEPUserCurrentLevel | INT | IOD_PEP | PEP:.UserCurrentLevel | BYTE
PEPUserCurrentName | STRING | IOD_PEP | PEP:.UserCurrentName
PEPUserLoggedIn | DIGITAL | IOD_PEP | PEP:.UserLoggedIn
PEPVLAZILEC_delovanje | DIGITAL | IOD_PEP | PEP:.VLAZILEC_delovanje
PEPVLAZILEC_napaka | DIGITAL | IOD_PEP | PEP:.VLAZILEC_napaka
PEPXVH_AlarmOn | DIGITAL | IOD_PEP | PEP:.XVH_AlarmOn
PEPXVH_UPSstatus | INT | IOD_PEP | PEP:.XVH_UPSstatus | BYTE
PEPZamasenostFiltra | DIGITAL | IOD_PEP | PEP:.ZamasenostFiltra
PEPnapaka_kom_scada2 | DIGITAL | IOD_PEP | PEP:.napaka_kom_scada2
PEPComSCADA2 | DIGITAL | IOD_PEP | PEP:.ComSCADA2
PEPComSCADA3 | DIGITAL | IOD_PEP | PEP:.ComSCADA3
PEPkom_nast_cas_izpada | INT | IOD_PEP | PEP:.kom_nast_cas_izpada

## variable_2
PEPAlarmPozara | DIGITAL | IOD_PEP | PEP:.AlarmPozara
PEPComSCADA | DIGITAL | IOD_PEP | PEP:.ComSCADA
PEPComSCADA1 | DIGITAL | IOD_PEP | PEP:.ComSCADA1
PEPErrComKlima | DIGITAL | IOD_PEP | PEP:.ErrComKlima
PEPErrComPort2 | DIGITAL | IOD_PEP | PEP:.ErrComPort2
PEPErrorComKlimaError | DIGITAL | IOD_PEP | PEP:.ErrorComKlima.Error
PEPKlima1Alarm_pozar | DIGITAL | IOD_PEP | PEP:.Klima[1].Alarm_pozar
PEPKlima1DelVentHit1 | DIGITAL | IOD_PEP | PEP:.Klima[1].DelVentHit1
PEPKlima1DelVentHit2 | DIGITAL | IOD_PEP | PEP:.Klima[1].DelVentHit2
PEPKlima1Ni_pretoka | DIGITAL | IOD_PEP | PEP:.Klima[1].Ni_pretoka
PEPKlima1OkvaraRototerm | DIGITAL | IOD_PEP | PEP:.Klima[1].OkvaraRototerm
PEPKlima1OkvaraVlazNap | DIGITAL | IOD_PEP | PEP:.Klima[1].OkvaraVlazNap
PEPKlima1PreobMotCrpGrel | DIGITAL | IOD_PEP | PEP:.Klima[1].PreobMotCrpGrel
PEPKlima1PreobMotVent | DIGITAL | IOD_PEP | PEP:.Klima[1].PreobMotVent
PEPKlima1ProtizamrzZascAktivna | DIGITAL | IOD_PEP | PEP:.Klima[1].ProtizamrzZascAktivna
PEPKlima1VklopRegKlimata | DIGITAL | IOD_PEP | PEP:.Klima[1].VklopRegKlimata
PEPKlima1ZamasenostFiltra | DIGITAL | IOD_PEP | PEP:.Klima[1].ZamasenostFiltra
PEPKlima1ZdruzAlarmA | DIGITAL | IOD_PEP | PEP:.Klima[1].ZdruzAlarmA
PEPKlima1ZdruzAlarmB | DIGITAL | IOD_PEP | PEP:.Klima[1].ZdruzAlarmB
PEPKLIMAT_delovanje | DIGITAL | IOD_PEP | PEP:.KLIMAT_delovanje
PEPKLIMAT_napaka | DIGITAL | IOD_PEP | PEP:.KLIMAT_napaka
PEPKLIMAT_rezim1 | DIGITAL | IOD_PEP | PEP:.KLIMAT_rezim1
PEPKLIMAT_rezim2 | DIGITAL | IOD_PEP | PEP:.KLIMAT_rezim2
PEPKlimaZdruzenAlarm | DIGITAL | IOD_PEP | PEP:.KlimaZdruzenAlarm
PEPKomunikacijaErr | DIGITAL | IOD_PEP | PEP:.KomunikacijaErr
PEPMEHCALEC_delovanje | DIGITAL | IOD_PEP | PEP:.MEHCALEC_delovanje
PEPMEHCALEC_napaka | DIGITAL | IOD_PEP | PEP:.MEHCALEC_napaka
PEPN_KLIMAT_napaka | DIGITAL | IOD_PEP | PEP:.N_KLIMAT_napaka
PEPN_ROTOTERM_napaka | DIGITAL | IOD_PEP | PEP:.N_ROTOTERM_napaka
PEPnapaka_kom_panel | DIGITAL | IOD_PEP | PEP:.napaka_kom_panel
PEPnapaka_kom_scada | DIGITAL | IOD_PEP | PEP:.napaka_kom_scada
PEPNapakaSenzorVlagaHIA1 | DIGITAL | IOD_PEP | PEP:.NapakaSenzorVlagaHIA1
PEPNapakaTSTempTIA1 | DIGITAL | IOD_PEP | PEP:.NapakaTSTempTIA1
PEPNiPretoka | DIGITAL | IOD_PEP | PEP:.NiPretoka
PEPOkvaraRototerma | DIGITAL | IOD_PEP | PEP:.OkvaraRototerma
PEPOkvaraVlazNap | DIGITAL | IOD_PEP | PEP:.OkvaraVlazNap
PEPPreobMotCrpGr | DIGITAL | IOD_PEP | PEP:.PreobMotCrpGr
PEPPreobMotVent | DIGITAL | IOD_PEP | PEP:.PreobMotVent
PEPProtizamrzZascAkt | DIGITAL | IOD_PEP | PEP:.ProtizamrzZascAkt
PEPROTOTERM_napaka | DIGITAL | IOD_PEP | PEP:.ROTOTERM_napaka
PEPSetDateTime | DIGITAL | IOD_PEP | PEP:.SetDateTime
PEPSetDateTimeDemand | DIGITAL | IOD_PEP | PEP:.SetDateTimeDemand
PEPSetDateTimeError | DIGITAL | IOD_PEP | PEP:.SetDateTimeError
PEPSetDateTimeFinished | DIGITAL | IOD_PEP | PEP:.SetDateTimeFinished
PEPSlabaBaterijaPLC | DIGITAL | IOD_PEP | PEP:.SlabaBaterijaPLC
PEPTIA1_previs_temp | DIGITAL | IOD_PEP | PEP:.TIA1_previs_temp
PEPups_alarm | DIGITAL | IOD_PEP | PEP:.ups_alarm
PEPups_baterijski_nac | DIGITAL | IOD_PEP | PEP:.ups_baterijski_nac
PEPups_polnjenje | DIGITAL | IOD_PEP | PEP:.ups_polnjenje
PEPUserLoggedIn | DIGITAL | IOD_PEP | PEP:.UserLoggedIn
PEPVLAZILEC_delovanje | DIGITAL | IOD_PEP | PEP:.VLAZILEC_delovanje
PEPVLAZILEC_napaka | DIGITAL | IOD_PEP | PEP:.VLAZILEC_napaka
PEPXVH_AlarmOn | DIGITAL | IOD_PEP | PEP:.XVH_AlarmOn
PEPZamasenostFiltra | DIGITAL | IOD_PEP | PEP:.ZamasenostFiltra
PEPnapaka_kom_scada2 | DIGITAL | IOD_PEP | PEP:.napaka_kom_scada2
PEPComSCADA2 | DIGITAL | IOD_PEP | PEP:.ComSCADA2
PEPComSCADA3 | DIGITAL | IOD_PEP | PEP:.ComSCADA3
PEPDateTimeDan | INT | IOD_PEP | PEP:.DateTime.Dan | BYTE
PEPDateTimeLeto | INT | IOD_PEP | PEP:.DateTime.Leto | BYTE
PEPDateTimeLeto2 | INT | IOD_PEP | PEP:.DateTime.Leto2
PEPDateTimeMesec | INT | IOD_PEP | PEP:.DateTime.Mesec | BYTE
PEPDateTimeMinuta | INT | IOD_PEP | PEP:.DateTime.Minuta | BYTE
PEPDateTimeSekunda | INT | IOD_PEP | PEP:.DateTime.Sekunda | BYTE
PEPDateTimeUra | INT | IOD_PEP | PEP:.DateTime.Ura | BYTE
PEPErrorComKlimaCode10 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[10] | BYTE
PEPErrorComKlimaCode11 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[11] | BYTE
PEPErrorComKlimaCode12 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[12] | BYTE
PEPErrorComKlimaCode13 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[13] | BYTE
PEPErrorComKlimaCode14 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[14] | BYTE
PEPErrorComKlimaCode15 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[15] | BYTE
PEPErrorComKlimaCode1 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[1] | BYTE
PEPErrorComKlimaCode2 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[2] | BYTE
PEPErrorComKlimaCode3 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[3] | BYTE
PEPErrorComKlimaCode4 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[4] | BYTE
PEPErrorComKlimaCode5 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[5] | BYTE
PEPErrorComKlimaCode6 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[6] | BYTE
PEPErrorComKlimaCode7 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[7] | BYTE
PEPErrorComKlimaCode8 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[8] | BYTE
PEPErrorComKlimaCode9 | INT | IOD_PEP | PEP:.ErrorComKlima.Code[9] | BYTE
PEPErrorComKlimaStatus | INT | IOD_PEP | PEP:.ErrorComKlima.Status
PEPHIA1_vlaga_s | INT | IOD_PEP | PEP:.HIA1_vlaga_s
PEPKlima1Analog_izh_mesanje | INT | IOD_PEP | PEP:.Klima[1].Analog_izh_mesanje
PEPKlima1Analog_izh_rekuperator | INT | IOD_PEP | PEP:.Klima[1].Analog_izh_rekuperator
PEPKlima1Analog_izh_VentGrelnika | INT | IOD_PEP | PEP:.Klima[1].Analog_izh_VentGrelnika
PEPKlima1Analog_izh_VentHlajenja | INT | IOD_PEP | PEP:.Klima[1].Analog_izh_VentHlajenja
PEPKlima1Dejanska_zel_temp | INT | IOD_PEP | PEP:.Klima[1].Dejanska_zel_temp
PEPKlima1Hitrost_del_vent_disp | INT | IOD_PEP | PEP:.Klima[1].Hitrost_del_vent_disp
PEPKlima1Max_vpih | INT | IOD_PEP | PEP:.Klima[1].Max_vpih
PEPKlima1Min_vpih | INT | IOD_PEP | PEP:.Klima[1].Min_vpih
PEPKlima1Obrat_ure_Vent_h1 | INT | IOD_PEP | PEP:.Klima[1].Obrat_ure_Vent_h1
PEPKlima1Obrat_ure_Vent_h2 | INT | IOD_PEP | PEP:.Klima[1].Obrat_ure_Vent_h2
PEPKlima1Pol_komp_konec | INT | IOD_PEP | PEP:.Klima[1].Pol_komp_konec
PEPKlima1Pol_komp_sprem_zel_vr | INT | IOD_PEP | PEP:.Klima[1].Pol_komp_sprem_zel_vr
PEPKlima1Pol_komp_zacetek | INT | IOD_PEP | PEP:.Klima[1].Pol_komp_zacetek
PEPKlima1PreklopHitDelVent | INT | IOD_PEP | PEP:.Klima[1].PreklopHitDelVent
PEPKlima1Protizamrz_zascita | INT | IOD_PEP | PEP:.Klima[1].Protizamrz_zascita
PEPKlima1Rezim_delovanja | INT | IOD_PEP | PEP:.Klima[1].Rezim_delovanja
PEPKlima1Temperatura_dovoda | INT | IOD_PEP | PEP:.Klima[1].Temperatura_dovoda
PEPKlima1Temperatura_prostora | INT | IOD_PEP | PEP:.Klima[1].Temperatura_prostora
PEPKlima1TempPredPloscnimRekup | INT | IOD_PEP | PEP:.Klima[1].TempPredPloscnimRekup
PEPKlima1TempZaPloscnimRekup | INT | IOD_PEP | PEP:.Klima[1].TempZaPloscnimRekup
PEPKlima1Vlaga_v_prostoru | INT | IOD_PEP | PEP:.Klima[1].Vlaga_v_prostoru
PEPKlima1VlagaVstopZrakaProstor | INT | IOD_PEP | PEP:.Klima[1].VlagaVstopZrakaProstor
PEPKlima1Zel_temp_eko_gretja | INT | IOD_PEP | PEP:.Klima[1].Zel_temp_eko_gretja
PEPKlima1Zel_temp_eko_hlajenja | INT | IOD_PEP | PEP:.Klima[1].Zel_temp_eko_hlajenja
PEPKlima1Zel_temp_komf_gretja | INT | IOD_PEP | PEP:.Klima[1].Zel_temp_komf_gretja
PEPKlima1Zel_temp_komf_hlajenja | INT | IOD_PEP | PEP:.Klima[1].Zel_temp_komf_hlajenja
PEPKlima1Zim_komp_konec | INT | IOD_PEP | PEP:.Klima[1].Zim_komp_konec
PEPKlima1Zim_komp_sprem_zel_vr | INT | IOD_PEP | PEP:.Klima[1].Zim_komp_sprem_zel_vr
PEPKlima1Zim_komp_zacetek | INT | IOD_PEP | PEP:.Klima[1].Zim_komp_zacetek
PEPKlima1ZimKompMinVpihKonec | INT | IOD_PEP | PEP:.Klima[1].ZimKompMinVpihKonec
PEPKlima1ZimKompMinVpihZac | INT | IOD_PEP | PEP:.Klima[1].ZimKompMinVpihZac
PEPKlima1ZkompMinVpihSpremZelVr | INT | IOD_PEP | PEP:.Klima[1].ZkompMinVpihSpremZelVr
PEPKlima1Zunanja_temp | INT | IOD_PEP | PEP:.Klima[1].Zunanja_temp
PEPKlima_rezim | INT | IOD_PEP | PEP:.Klima_rezim | BYTE
PEPTIA1_alarm | INT | IOD_PEP | PEP:.TIA1_alarm
PEPTIA1_temp_s | INT | IOD_PEP | PEP:.TIA1_temp_s
PEPUserCurrentLevel | INT | IOD_PEP | PEP:.UserCurrentLevel | BYTE
PEPXVH_UPSstatus | INT | IOD_PEP | PEP:.XVH_UPSstatus | BYTE
PEPkom_nast_cas_izpada | INT | IOD_PEP | PEP:.kom_nast_cas_izpada
PEPDate_Time0 | STRING | IOD_PEP | PEP:.Date_Time[0]
PEPDate_Time1 | STRING | IOD_PEP | PEP:.Date_Time[1]
PEPDate_Time2 | STRING | IOD_PEP | PEP:.Date_Time[2]
PEPDate_Time3 | STRING | IOD_PEP | PEP:.Date_Time[3]
PEPUserCurrentName | STRING | IOD_PEP | PEP:.UserCurrentName

## variable_3
PEPAlarmPozara | DIGITAL | IOD_PEP_TCP | 1 | 00001 | AlarmPozara
PEPComSCADA | DIGITAL | IOD_PEP_TCP | 2 | 00002 | ComSCADA
PEPComSCADA1 | DIGITAL | IOD_PEP_TCP | 3 | 00003 | ComSCADA1
PEPErrComKlima | DIGITAL | IOD_PEP_TCP | 4 | 00004 | ErrComKlima
PEPErrComPort2 | DIGITAL | IOD_PEP_TCP | 5 | 00005 | ErrComPort2
PEPErrorComKlimaError | DIGITAL | IOD_PEP_TCP | 6 | 00006 | ErrorComKlima.Error
PEPKlima1Alarm_pozar | DIGITAL | IOD_PEP_TCP | 7 | 00007 | Klima[1].Alarm_pozar
PEPKlima1DelVentHit1 | DIGITAL | IOD_PEP_TCP | 8 | 00008 | Klima[1].DelVentHit1
PEPKlima1DelVentHit2 | DIGITAL | IOD_PEP_TCP | 9 | 00009 | Klima[1].DelVentHit2
PEPKlima1Ni_pretoka | DIGITAL | IOD_PEP_TCP | 10 | 00010 | Klima[1].Ni_pretoka
PEPKlima1OkvaraRototerm | DIGITAL | IOD_PEP_TCP | 11 | 00011 | Klima[1].OkvaraRototerm
PEPKlima1OkvaraVlazNap | DIGITAL | IOD_PEP_TCP | 12 | 00012 | Klima[1].OkvaraVlazNap
PEPKlima1PreobMotCrpGrel | DIGITAL | IOD_PEP_TCP | 13 | 00013 | Klima[1].PreobMotCrpGrel
PEPKlima1PreobMotVent | DIGITAL | IOD_PEP_TCP | 14 | 00014 | Klima[1].PreobMotVent
PEPKlima1ProtizamrzZascAktivna | DIGITAL | IOD_PEP_TCP | 15 | 00015 | Klima[1].ProtizamrzZascAktivna
PEPKlima1VklopRegKlimata | DIGITAL | IOD_PEP_TCP | 16 | 00016 | Klima[1].VklopRegKlimata
PEPKlima1ZamasenostFiltra | DIGITAL | IOD_PEP_TCP | 17 | 00017 | Klima[1].ZamasenostFiltra
PEPKlima1ZdruzAlarmA | DIGITAL | IOD_PEP_TCP | 18 | 00018 | Klima[1].ZdruzAlarmA
PEPKlima1ZdruzAlarmB | DIGITAL | IOD_PEP_TCP | 19 | 00019 | Klima[1].ZdruzAlarmB
PEPKLIMAT_delovanje | DIGITAL | IOD_PEP_TCP | 20 | 00020 | KLIMAT_delovanje
PEPKLIMAT_napaka | DIGITAL | IOD_PEP_TCP | 21 | 00021 | KLIMAT_napaka
PEPKLIMAT_rezim1 | DIGITAL | IOD_PEP_TCP | 22 | 00022 | KLIMAT_rezim1
PEPKLIMAT_rezim2 | DIGITAL | IOD_PEP_TCP | 23 | 00023 | KLIMAT_rezim2
PEPKlimaZdruzenAlarm | DIGITAL | IOD_PEP_TCP | 24 | 00024 | KlimaZdruzenAlarm
PEPKomunikacijaErr | DIGITAL | IOD_PEP_TCP | 25 | 00025 | KomunikacijaErr
PEPMEHCALEC_delovanje | DIGITAL | IOD_PEP_TCP | 26 | 00026 | MEHCALEC_delovanje
PEPMEHCALEC_napaka | DIGITAL | IOD_PEP_TCP | 27 | 00027 | MEHCALEC_napaka
PEPN_KLIMAT_napaka | DIGITAL | IOD_PEP_TCP | 28 | 00028 | N_KLIMAT_napaka
PEPN_ROTOTERM_napaka | DIGITAL | IOD_PEP_TCP | 29 | 00029 | N_ROTOTERM_napaka
PEPnapaka_kom_panel | DIGITAL | IOD_PEP_TCP | 30 | 00030 | napaka_kom_panel
PEPnapaka_kom_scada | DIGITAL | IOD_PEP_TCP | 31 | 00031 | napaka_kom_scada
PEPNapakaSenzorVlagaHIA1 | DIGITAL | IOD_PEP_TCP | 32 | 00032 | NapakaSenzorVlagaHIA1
PEPNapakaTSTempTIA1 | DIGITAL | IOD_PEP_TCP | 33 | 00033 | NapakaTSTempTIA1
PEPNiPretoka | DIGITAL | IOD_PEP_TCP | 34 | 00034 | NiPretoka
PEPOkvaraRototerma | DIGITAL | IOD_PEP_TCP | 35 | 00035 | OkvaraRototerma
PEPOkvaraVlazNap | DIGITAL | IOD_PEP_TCP | 36 | 00036 | OkvaraVlazNap
PEPPreobMotCrpGr | DIGITAL | IOD_PEP_TCP | 37 | 00037 | PreobMotCrpGr
PEPPreobMotVent | DIGITAL | IOD_PEP_TCP | 38 | 00038 | PreobMotVent
PEPProtizamrzZascAkt | DIGITAL | IOD_PEP_TCP | 39 | 00039 | ProtizamrzZascAkt
PEPROTOTERM_napaka | DIGITAL | IOD_PEP_TCP | 40 | 00040 | ROTOTERM_napaka
PEPSetDateTime | DIGITAL | IOD_PEP_TCP | 41 | 00041 | SetDateTime
PEPSetDateTimeDemand | DIGITAL | IOD_PEP_TCP | 42 | 00042 | SetDateTimeDemand
PEPSetDateTimeError | DIGITAL | IOD_PEP_TCP | 43 | 00043 | SetDateTimeError
PEPSetDateTimeFinished | DIGITAL | IOD_PEP_TCP | 44 | 00044 | SetDateTimeFinished
PEPSlabaBaterijaPLC | DIGITAL | IOD_PEP_TCP | 45 | 00045 | SlabaBaterijaPLC
PEPTIA1_previs_temp | DIGITAL | IOD_PEP_TCP | 46 | 00046 | TIA1_previs_temp
PEPups_alarm | DIGITAL | IOD_PEP_TCP | 47 | 00047 | ups_alarm
PEPups_baterijski_nac | DIGITAL | IOD_PEP_TCP | 48 | 00048 | ups_baterijski_nac
PEPups_polnjenje | DIGITAL | IOD_PEP_TCP | 49 | 00049 | ups_polnjenje
PEPUserLoggedIn | DIGITAL | IOD_PEP_TCP | 50 | 00050 | UserLoggedIn
PEPVLAZILEC_delovanje | DIGITAL | IOD_PEP_TCP | 51 | 00051 | VLAZILEC_delovanje
PEPVLAZILEC_napaka | DIGITAL | IOD_PEP_TCP | 52 | 00052 | VLAZILEC_napaka
PEPXVH_AlarmOn | DIGITAL | IOD_PEP_TCP | 53 | 00053 | XVH_AlarmOn
PEPZamasenostFiltra | DIGITAL | IOD_PEP_TCP | 54 | 00054 | ZamasenostFiltra
PEPnapaka_kom_scada2 | DIGITAL | IOD_PEP_TCP | 55 | 00055 | napaka_kom_scada2
PEPComSCADA2 | DIGITAL | IOD_PEP_TCP | 56 | 00056 | ComSCADA2
PEPComSCADA3 | DIGITAL | IOD_PEP_TCP | 57 | 00057 | ComSCADA3
PEPDateTimeDan | INT | IOD_PEP_TCP | 1 | 40001 | DateTime.Dan | BYTE
PEPDateTimeLeto | INT | IOD_PEP_TCP | 2 | 40002 | DateTime.Leto | BYTE
PEPDateTimeLeto2 | INT | IOD_PEP_TCP | 3 | 40003 | DateTime.Leto2
PEPDateTimeMesec | INT | IOD_PEP_TCP | 4 | 40004 | DateTime.Mesec | BYTE
PEPDateTimeMinuta | INT | IOD_PEP_TCP | 5 | 40005 | DateTime.Minuta | BYTE
PEPDateTimeSekunda | INT | IOD_PEP_TCP | 6 | 40006 | DateTime.Sekunda | BYTE
PEPDateTimeUra | INT | IOD_PEP_TCP | 7 | 40007 | DateTime.Ura | BYTE
PEPErrorComKlimaCode10 | INT | IOD_PEP_TCP | 8 | 40008 | ErrorComKlima.Code[10] | BYTE
PEPErrorComKlimaCode11 | INT | IOD_PEP_TCP | 9 | 40009 | ErrorComKlima.Code[11] | BYTE
PEPErrorComKlimaCode12 | INT | IOD_PEP_TCP | 10 | 40010 | ErrorComKlima.Code[12] | BYTE
PEPErrorComKlimaCode13 | INT | IOD_PEP_TCP | 11 | 40011 | ErrorComKlima.Code[13] | BYTE
PEPErrorComKlimaCode14 | INT | IOD_PEP_TCP | 12 | 40012 | ErrorComKlima.Code[14] | BYTE
PEPErrorComKlimaCode15 | INT | IOD_PEP_TCP | 13 | 40013 | ErrorComKlima.Code[15] | BYTE
PEPErrorComKlimaCode1 | INT | IOD_PEP_TCP | 14 | 40014 | ErrorComKlima.Code[1] | BYTE
PEPErrorComKlimaCode2 | INT | IOD_PEP_TCP | 15 | 40015 | ErrorComKlima.Code[2] | BYTE
PEPErrorComKlimaCode3 | INT | IOD_PEP_TCP | 16 | 40016 | ErrorComKlima.Code[3] | BYTE
PEPErrorComKlimaCode4 | INT | IOD_PEP_TCP | 17 | 40017 | ErrorComKlima.Code[4] | BYTE
PEPErrorComKlimaCode5 | INT | IOD_PEP_TCP | 18 | 40018 | ErrorComKlima.Code[5] | BYTE
PEPErrorComKlimaCode6 | INT | IOD_PEP_TCP | 19 | 40019 | ErrorComKlima.Code[6] | BYTE
PEPErrorComKlimaCode7 | INT | IOD_PEP_TCP | 20 | 40020 | ErrorComKlima.Code[7] | BYTE
PEPErrorComKlimaCode8 | INT | IOD_PEP_TCP | 21 | 40021 | ErrorComKlima.Code[8] | BYTE
PEPErrorComKlimaCode9 | INT | IOD_PEP_TCP | 22 | 40022 | ErrorComKlima.Code[9] | BYTE
PEPErrorComKlimaStatus | INT | IOD_PEP_TCP | 23 | 40023 | ErrorComKlima.Status
PEPHIA1_vlaga_s | INT | IOD_PEP_TCP | 24 | 40024 | HIA1_vlaga_s
PEPKlima1Analog_izh_mesanje | INT | IOD_PEP_TCP | 25 | 40025 | Klima[1].Analog_izh_mesanje
PEPKlima1Analog_izh_rekuperator | INT | IOD_PEP_TCP | 26 | 40026 | Klima[1].Analog_izh_rekuperator
PEPKlima1Analog_izh_VentGrelnika | INT | IOD_PEP_TCP | 27 | 40027 | Klima[1].Analog_izh_VentGrelnika
PEPKlima1Analog_izh_VentHlajenja | INT | IOD_PEP_TCP | 28 | 40028 | Klima[1].Analog_izh_VentHlajenja
PEPKlima1Dejanska_zel_temp | INT | IOD_PEP_TCP | 29 | 40029 | Klima[1].Dejanska_zel_temp
PEPKlima1Hitrost_del_vent_disp | INT | IOD_PEP_TCP | 30 | 40030 | Klima[1].Hitrost_del_vent_disp
PEPKlima1Max_vpih | INT | IOD_PEP_TCP | 31 | 40031 | Klima[1].Max_vpih
PEPKlima1Min_vpih | INT | IOD_PEP_TCP | 32 | 40032 | Klima[1].Min_vpih
PEPKlima1Obrat_ure_Vent_h1 | INT | IOD_PEP_TCP | 33 | 40033 | Klima[1].Obrat_ure_Vent_h1
PEPKlima1Obrat_ure_Vent_h2 | INT | IOD_PEP_TCP | 34 | 40034 | Klima[1].Obrat_ure_Vent_h2
PEPKlima1Pol_komp_konec | INT | IOD_PEP_TCP | 35 | 40035 | Klima[1].Pol_komp_konec
PEPKlima1Pol_komp_sprem_zel_vr | INT | IOD_PEP_TCP | 36 | 40036 | Klima[1].Pol_komp_sprem_zel_vr
PEPKlima1Pol_komp_zacetek | INT | IOD_PEP_TCP | 37 | 40037 | Klima[1].Pol_komp_zacetek
PEPKlima1PreklopHitDelVent | INT | IOD_PEP_TCP | 38 | 40038 | Klima[1].PreklopHitDelVent
PEPKlima1Protizamrz_zascita | INT | IOD_PEP_TCP | 39 | 40039 | Klima[1].Protizamrz_zascita
PEPKlima1Rezim_delovanja | INT | IOD_PEP_TCP | 40 | 40040 | Klima[1].Rezim_delovanja
PEPKlima1Temperatura_dovoda | INT | IOD_PEP_TCP | 41 | 40041 | Klima[1].Temperatura_dovoda
PEPKlima1Temperatura_prostora | INT | IOD_PEP_TCP | 42 | 40042 | Klima[1].Temperatura_prostora
PEPKlima1TempPredPloscnimRekup | INT | IOD_PEP_TCP | 43 | 40043 | Klima[1].TempPredPloscnimRekup
PEPKlima1TempZaPloscnimRekup | INT | IOD_PEP_TCP | 44 | 40044 | Klima[1].TempZaPloscnimRekup
PEPKlima1Vlaga_v_prostoru | INT | IOD_PEP_TCP | 45 | 40045 | Klima[1].Vlaga_v_prostoru
PEPKlima1VlagaVstopZrakaProstor | INT | IOD_PEP_TCP | 46 | 40046 | Klima[1].VlagaVstopZrakaProstor
PEPKlima1Zel_temp_eko_gretja | INT | IOD_PEP_TCP | 47 | 40047 | Klima[1].Zel_temp_eko_gretja
PEPKlima1Zel_temp_eko_hlajenja | INT | IOD_PEP_TCP | 48 | 40048 | Klima[1].Zel_temp_eko_hlajenja
PEPKlima1Zel_temp_komf_gretja | INT | IOD_PEP_TCP | 49 | 40049 | Klima[1].Zel_temp_komf_gretja
PEPKlima1Zel_temp_komf_hlajenja | INT | IOD_PEP_TCP | 50 | 40050 | Klima[1].Zel_temp_komf_hlajenja
PEPKlima1Zim_komp_konec | INT | IOD_PEP_TCP | 51 | 40051 | Klima[1].Zim_komp_konec
PEPKlima1Zim_komp_sprem_zel_vr | INT | IOD_PEP_TCP | 52 | 40052 | Klima[1].Zim_komp_sprem_zel_vr
PEPKlima1Zim_komp_zacetek | INT | IOD_PEP_TCP | 53 | 40053 | Klima[1].Zim_komp_zacetek
PEPKlima1ZimKompMinVpihKonec | INT | IOD_PEP_TCP | 54 | 40054 | Klima[1].ZimKompMinVpihKonec
PEPKlima1ZimKompMinVpihZac | INT | IOD_PEP_TCP | 55 | 40055 | Klima[1].ZimKompMinVpihZac
PEPKlima1ZkompMinVpihSpremZelVr | INT | IOD_PEP_TCP | 56 | 40056 | Klima[1].ZkompMinVpihSpremZelVr
PEPKlima1Zunanja_temp | INT | IOD_PEP_TCP | 57 | 40057 | Klima[1].Zunanja_temp
PEPKlima_rezim | INT | IOD_PEP_TCP | 58 | 40058 | Klima_rezim | BYTE
PEPTIA1_alarm | INT | IOD_PEP_TCP | 59 | 40059 | TIA1_alarm
PEPTIA1_temp_s | INT | IOD_PEP_TCP | 60 | 40060 | TIA1_temp_s
PEPUserCurrentLevel | INT | IOD_PEP_TCP | 61 | 40061 | UserCurrentLevel | BYTE
PEPXVH_UPSstatus | INT | IOD_PEP_TCP | 62 | 40062 | XVH_UPSstatus | BYTE
PEPkom_nast_cas_izpada | INT | IOD_PEP_TCP | 63 | 40063 | kom_nast_cas_izpada
PEPDate_Time0 | STRING | IOD_PEP_TCP | 5001 | 45001[15] | Date_Time[0]
PEPDate_Time1 | STRING | IOD_PEP_TCP | 5016 | 45016[15] | Date_Time[1]
PEPDate_Time2 | STRING | IOD_PEP_TCP | 5031 | 45031[15] | Date_Time[2]
PEPDate_Time3 | STRING | IOD_PEP_TCP | 5046 | 45046[15] | Date_Time[3]
PEPUserCurrentName | STRING | IOD_PEP_TCP | 5061 | 45061[15] | UserCurrentName

## variable_new
PEPAlarmPozara | DIGITAL | IOD_PEP_TCP | 00001
PEPComSCADA | DIGITAL | IOD_PEP_TCP | 00002
PEPComSCADA1 | DIGITAL | IOD_PEP_TCP | 00003
PEPDate_Time0 | STRING | IOD_PEP_TCP | 45001[15]
PEPDate_Time1 | STRING | IOD_PEP_TCP | 45016[15]
PEPDate_Time2 | STRING | IOD_PEP_TCP | 45031[15]
PEPDate_Time3 | STRING | IOD_PEP_TCP | 45046[15]
PEPDateTimeDan | INT | IOD_PEP_TCP | 40001
PEPDateTimeLeto | INT | IOD_PEP_TCP | 40002
PEPDateTimeLeto2 | INT | IOD_PEP_TCP | 40003
PEPDateTimeMesec | INT | IOD_PEP_TCP | 40004
PEPDateTimeMinuta | INT | IOD_PEP_TCP | 40005
PEPDateTimeSekunda | INT | IOD_PEP_TCP | 40006
PEPDateTimeUra | INT | IOD_PEP_TCP | 40007
PEPErrComKlima | DIGITAL | IOD_PEP_TCP | 00004
PEPErrComPort2 | DIGITAL | IOD_PEP_TCP | 00005
PEPErrorComKlimaCode10 | INT | IOD_PEP_TCP | 40008
PEPErrorComKlimaCode11 | INT | IOD_PEP_TCP | 40009
PEPErrorComKlimaCode12 | INT | IOD_PEP_TCP | 40010
PEPErrorComKlimaCode13 | INT | IOD_PEP_TCP | 40011
PEPErrorComKlimaCode14 | INT | IOD_PEP_TCP | 40012
PEPErrorComKlimaCode15 | INT | IOD_PEP_TCP | 40013
PEPErrorComKlimaCode1 | INT | IOD_PEP_TCP | 40014
PEPErrorComKlimaCode2 | INT | IOD_PEP_TCP | 40015
PEPErrorComKlimaCode3 | INT | IOD_PEP_TCP | 40016
PEPErrorComKlimaCode4 | INT | IOD_PEP_TCP | 40017
PEPErrorComKlimaCode5 | INT | IOD_PEP_TCP | 40018
PEPErrorComKlimaCode6 | INT | IOD_PEP_TCP | 40019
PEPErrorComKlimaCode7 | INT | IOD_PEP_TCP | 40020
PEPErrorComKlimaCode8 | INT | IOD_PEP_TCP | 40021
PEPErrorComKlimaCode9 | INT | IOD_PEP_TCP | 40022
PEPErrorComKlimaError | DIGITAL | IOD_PEP_TCP | 00006
PEPErrorComKlimaStatus | INT | IOD_PEP_TCP | 40023
PEPHIA1_vlaga_s | INT | IOD_PEP_TCP | 40024 | 0 | 1000 | 0 | 100 | % | ###.#
PEPKlima1Alarm_pozar | DIGITAL | IOD_PEP_TCP | 00007
PEPKlima1Analog_izh_mesanje | INT | IOD_PEP_TCP | 40025
PEPKlima1Analog_izh_rekuperator | INT | IOD_PEP_TCP | 40026
PEPKlima1Analog_izh_VentGrelnika | INT | IOD_PEP_TCP | 40027
PEPKlima1Analog_izh_VentHlajenja | INT | IOD_PEP_TCP | 40028
PEPKlima1Dejanska_zel_temp | INT | IOD_PEP_TCP | 40029 | 0 | 600 | 0 | 60 | °C | ##.#
PEPKlima1DelVentHit1 | DIGITAL | IOD_PEP_TCP | 00008 | 0 | 1000 | 0 | 1000 | % | ###.#
PEPKlima1DelVentHit2 | DIGITAL | IOD_PEP_TCP | 00009 | 0 | 1000 | 0 | 1000 | % | ###.#
PEPKlima1Hitrost_del_vent_disp | INT | IOD_PEP_TCP | 40030 | 0 | 100 | 0 | 100 | Hz | ##.#
PEPKlima1Max_vpih | INT | IOD_PEP_TCP | 40031 | 0 | 600 | 0 | 60 | °C | ##.#
PEPKlima1Min_vpih | INT | IOD_PEP_TCP | 40032 | 0 | 600 | 0 | 60 | °C | ##.#
PEPKlima1Ni_pretoka | DIGITAL | IOD_PEP_TCP | 00010
PEPKlima1Obrat_ure_Vent_h1 | INT | IOD_PEP_TCP | 40033
PEPKlima1Obrat_ure_Vent_h2 | INT | IOD_PEP_TCP | 40034
PEPKlima1OkvaraRototerm | DIGITAL | IOD_PEP_TCP | 00011
PEPKlima1OkvaraVlazNap | DIGITAL | IOD_PEP_TCP | 00012
PEPKlima1Pol_komp_konec | INT | IOD_PEP_TCP | 40035 | 0 | 600 | 0 | 60 | °C | ##.#
PEPKlima1Pol_komp_sprem_zel_vr | INT | IOD_PEP_TCP | 40036 | 0 | 600 | 0 | 60 | °C | ##.#
PEPKlima1Pol_komp_zacetek | INT | IOD_PEP_TCP | 40037 | 0 | 600 | 0 | 60 | °C | ##.#
PEPKlima1PreklopHitDelVent | INT | IOD_PEP_TCP | 40038 | 0 | 600 | 0 | 60 | °C | ##.#
PEPKlima1PreobMotCrpGrel | DIGITAL | IOD_PEP_TCP | 00013
PEPKlima1PreobMotVent | DIGITAL | IOD_PEP_TCP | 00014
PEPKlima1Protizamrz_zascita | INT | IOD_PEP_TCP | 40039 | 0 | 600 | 0 | 60 | °C | ##.#
PEPKlima1ProtizamrzZascAktivna | DIGITAL | IOD_PEP_TCP | 00015
PEPKlima1Rezim_delovanja | INT | IOD_PEP_TCP | 40040
PEPKlima1Temperatura_dovoda | INT | IOD_PEP_TCP | 40041 | 0 | 600 | 0 | 60 | °C | ##.#
PEPKlima1Temperatura_prostora | INT | IOD_PEP_TCP | 40042 | 0 | 600 | 0 | 60 | °C | ##.#
PEPKlima1TempPredPloscnimRekup | INT | IOD_PEP_TCP | 40043 | 0 | 600 | 0 | 60 | °C | ##.#
PEPKlima1TempZaPloscnimRekup | INT | IOD_PEP_TCP | 40044 | 0 | 600 | 0 | 60 | °C | ##.#
PEPKlima1VklopRegKlimata | DIGITAL | IOD_PEP_TCP | 00016
PEPKlima1Vlaga_v_prostoru | INT | IOD_PEP_TCP | 40045 | 0 | 1000 | 0 | 100 | % | ##.#
PEPKlima1VlagaVstopZrakaProstor | INT | IOD_PEP_TCP | 40046 | 0 | 1000 | 0 | 100 | % | ##.#
PEPKlima1ZamasenostFiltra | DIGITAL | IOD_PEP_TCP | 00017
PEPKlima1ZdruzAlarmA | DIGITAL | IOD_PEP_TCP | 00018
PEPKlima1ZdruzAlarmB | DIGITAL | IOD_PEP_TCP | 00019
PEPKlima1Zel_temp_eko_gretja | INT | IOD_PEP_TCP | 40047 | 0 | 600 | 0 | 60 | °C | ##.#
PEPKlima1Zel_temp_eko_hlajenja | INT | IOD_PEP_TCP | 40048 | 0 | 600 | 0 | 60 | °C | ##.#
PEPKlima1Zel_temp_komf_gretja | INT | IOD_PEP_TCP | 40049 | 0 | 600 | 0 | 60 | °C | ##.#
PEPKlima1Zel_temp_komf_hlajenja | INT | IOD_PEP_TCP | 40050 | 0 | 600 | 0 | 60 | °C | ##.#
PEPKlima1Zim_komp_konec | INT | IOD_PEP_TCP | 40051 | -400 | 600 | -40 | 60 | °C | ##.#
PEPKlima1Zim_komp_sprem_zel_vr | INT | IOD_PEP_TCP | 40052 | -400 | 600 | -40 | 60 | °C | ##.#
PEPKlima1Zim_komp_zacetek | INT | IOD_PEP_TCP | 40053 | -400 | 600 | -40 | 60 | °C | ##.#
PEPKlima1ZimKompMinVpihKonec | INT | IOD_PEP_TCP | 40054 | -400 | 600 | -40 | 60 | °C | ##.#
PEPKlima1ZimKompMinVpihZac | INT | IOD_PEP_TCP | 40055 | -400 | 600 | -40 | 60 | °C | ##.#
PEPKlima1ZkompMinVpihSpremZelVr | INT | IOD_PEP_TCP | 40056 | -400 | 600 | -40 | 60 | °C | ##.#
PEPKlima1Zunanja_temp | INT | IOD_PEP_TCP | 40057 | -400 | 600 | -40 | 60 | °C | ##.#
PEPKlima_rezim | INT | IOD_PEP_TCP | 40058
PEPKLIMAT_delovanje | DIGITAL | IOD_PEP_TCP | 00020
PEPKLIMAT_napaka | DIGITAL | IOD_PEP_TCP | 00021
PEPKLIMAT_rezim1 | DIGITAL | IOD_PEP_TCP | 00022
PEPKLIMAT_rezim2 | DIGITAL | IOD_PEP_TCP | 00023
PEPKlimaZdruzenAlarm | DIGITAL | IOD_PEP_TCP | 00024
PEPKomunikacijaErr | DIGITAL | IOD_PEP_TCP | 00025
PEPMEHCALEC_delovanje | DIGITAL | IOD_PEP_TCP | 00026
PEPMEHCALEC_napaka | DIGITAL | IOD_PEP_TCP | 00027
PEPN_KLIMAT_napaka | DIGITAL | IOD_PEP_TCP | 00028
PEPN_ROTOTERM_napaka | DIGITAL | IOD_PEP_TCP | 00029
PEPnapaka_kom_panel | DIGITAL | IOD_PEP_TCP | 00030
PEPnapaka_kom_scada | DIGITAL | IOD_PEP_TCP | 00031
PEPNapakaSenzorVlagaHIA1 | DIGITAL | IOD_PEP_TCP | 00032
PEPNapakaTSTempTIA1 | DIGITAL | IOD_PEP_TCP | 00033
PEPNiPretoka | DIGITAL | IOD_PEP_TCP | 00034
PEPOkvaraRototerma | DIGITAL | IOD_PEP_TCP | 00035
PEPOkvaraVlazNap | DIGITAL | IOD_PEP_TCP | 00036
PEPPreobMotCrpGr | DIGITAL | IOD_PEP_TCP | 00037
PEPPreobMotVent | DIGITAL | IOD_PEP_TCP | 00038
PEPProtizamrzZascAkt | DIGITAL | IOD_PEP_TCP | 00039
PEPROTOTERM_napaka | DIGITAL | IOD_PEP_TCP | 00040
PEPSetDateTime | DIGITAL | IOD_PEP_TCP | 00041
PEPSetDateTimeDemand | DIGITAL | IOD_PEP_TCP | 00042
PEPSetDateTimeError | DIGITAL | IOD_PEP_TCP | 00043
PEPSetDateTimeFinished | DIGITAL | IOD_PEP_TCP | 00044
PEPSlabaBaterijaPLC | DIGITAL | IOD_PEP_TCP | 00045
PEPTIA1_alarm | INT | IOD_PEP_TCP | 40059 | 0 | 60 | 0 | 60 | °C | ##
PEPTIA1_previs_temp | DIGITAL | IOD_PEP_TCP | 00046
PEPTIA1_temp_s | INT | IOD_PEP_TCP | 40060 | 0 | 600 | 0 | 60 | °C | ##.#
PEPups_alarm | DIGITAL | IOD_PEP_TCP | 00047
PEPups_baterijski_nac | DIGITAL | IOD_PEP_TCP | 00048
PEPups_polnjenje | DIGITAL | IOD_PEP_TCP | 00049
PEPUserCurrentLevel | INT | IOD_PEP_TCP | 40061
PEPUserCurrentName | STRING | IOD_PEP_TCP | 45061[15]
PEPUserLoggedIn | DIGITAL | IOD_PEP_TCP | 00050
PEPVLAZILEC_delovanje | DIGITAL | IOD_PEP_TCP | 00051
PEPVLAZILEC_napaka | DIGITAL | IOD_PEP_TCP | 00052
PEPXVH_AlarmOn | DIGITAL | IOD_PEP_TCP | 00053
PEPXVH_UPSstatus | INT | IOD_PEP_TCP | 40062
PEPZamasenostFiltra | DIGITAL | IOD_PEP_TCP | 00054
APEP_omogoci_sms | DIGITAL | IOD_PEP_disk | D24[40]
BPEP_omogoci_sms | DIGITAL | IOD_PEP_disk | D64[40]
CPEP_omogoci_sms | DIGITAL | IOD_PEP_disk | D104[40]
DPEP_omogoci_sms | DIGITAL | IOD_PEP_disk | D144[40]
EPEP_omogoci_sms | DIGITAL | IOD_PEP_disk | D184[40]
FPEP_omogoci_sms | DIGITAL | IOD_PEP_disk | D224[40]
PEPN_KLIMAT_napaka_omog | DIGITAL | IOD_PEP_disk | D266
PEPN_ROTOTERM_napaka_omog | DIGITAL | IOD_PEP_disk | D267
PEPN_VLAZILEC_napaka_omog | DIGITAL | IOD_PEP_disk | D268
PEPErrComKlima_omog | DIGITAL | IOD_PEP_disk | D269
PEPSetDateTimeError_omog | DIGITAL | IOD_PEP_disk | D270
PEPErrComPort2_omog | DIGITAL | IOD_PEP_disk | D271
PEPKlima1Alarm_pozar_omog | DIGITAL | IOD_PEP_disk | D272
PEPKlimaZdruzenAlarm_omog | DIGITAL | IOD_PEP_disk | D273
PEPKlima1Ni_pretoka_omog | DIGITAL | IOD_PEP_disk | D274
PEPKlima1OkvaraRototerm_omog | DIGITAL | IOD_PEP_disk | D275
PEPKlima1OkvaraVlazNap_omog | DIGITAL | IOD_PEP_disk | D276
PEPKlima1PreobMotCrpGrel_omog | DIGITAL | IOD_PEP_disk | D277
PEPKlima1PreobMotVent_omog | DIGITAL | IOD_PEP_disk | D278
PEPKlima1ProtizamrzZascAktivna_omog | DIGITAL | IOD_PEP_disk | D279
PEPKlima1ZamasenostFiltra_omog | DIGITAL | IOD_PEP_disk | D280
PEPOkvaraRototerma_omog | DIGITAL | IOD_PEP_disk | D281
PEPOkvaraVlazNap_omog | DIGITAL | IOD_PEP_disk | D282
PEPTIA1_previs_temp_omog | DIGITAL | IOD_PEP_disk | D283
PEPUserLoggedIn_mem | DIGITAL | IOD_PEP_disk | D284
PEPMEHCALEC_napaka_om | DIGITAL | IOD_PEP_disk | D285
PEP_Sekunda1s_utripanje | DIGITAL | IOD_PEP_mem | D1
PEP_Prikaz_klimata_ce_je1 | DIGITAL | IOD_PEP_mem | D2
PEP_Prikaz_temp_v_ce_je1 | DIGITAL | IOD_PEP_mem | D3
PEP_Prikaz_vlazilec_ce_je1 | DIGITAL | IOD_PEP_mem | D4
PEP_prikaz_ups_ce_je1 | DIGITAL | IOD_PEP_mem | D5
PEP_prikaz_rototerm_ce_je1 | DIGITAL | IOD_PEP_mem | D6
PEPKLIMAT_napaka_omog | DIGITAL | IOD_PEP_disk | D7
PEPROTOTERM_napaka_omog | DIGITAL | IOD_PEP_disk | D8
PEPups_alarm_omog | DIGITAL | IOD_PEP_disk | D9
PEPVLAZILEC_napaka_omog | DIGITAL | IOD_PEP_disk | D10
PEPNapakaSenzorVlagaHIA1_omog | DIGITAL | IOD_PEP_disk | D11
PEPNapakaTSTempTIA1_omog | DIGITAL | IOD_PEP_disk | D12
PEPComSCADA_stevec1 | INT | IOD_PEP_mem | I13
PEPComSCADA_stevec2 | INT | IOD_PEP_mem | I14
PEPnapaka_kom_scada_omog | DIGITAL | IOD_PEP_disk | D15
PEPnapaka_kom_panel_omog | DIGITAL | IOD_PEP_disk | D16
PEPKLIMAT_delovanje_omog | DIGITAL | IOD_PEP_disk | D17
PEPROTOTERM_delovanje_omog | DIGITAL | IOD_PEP_disk | D18
PEPups_baterijski_nac_omog | DIGITAL | IOD_PEP_disk | D19
PEPups_polnjenje_omog | DIGITAL | IOD_PEP_disk | D20
PEPVLAZILEC_delovanje_omog | DIGITAL | IOD_PEP_disk | D21
PEPSlabaBaterijaPLC_omog | DIGITAL | IOD_PEP_disk | D22
PEPnapaka_kom_krm_omogoci | DIGITAL | IOD_PEP_disk | D23
PEPKLIMAT_delovanje_omogoci | DIGITAL | IOD_PEP_disk | D286
PEPKlima1VklopRegKlimata_omogoci | DIGITAL | IOD_PEP_disk | D287
PEPKlima_rezim1_omogoci | DIGITAL | IOD_PEP_disk | D288
PEPKlima_rezim2_omogoci | DIGITAL | IOD_PEP_disk | D289
PEPKlima_rezim3_omogoci | DIGITAL | IOD_PEP_disk | D290
PEPKlima_rezim4_omogoci | DIGITAL | IOD_PEP_disk | D291
PEPnapaka_kom_scada2 | DIGITAL | IOD_PEP_TCP | 00055
PEPComSCADA2 | DIGITAL | IOD_PEP_TCP | 00056
PEPnapaka_kom_krm_omogoci2 | DIGITAL | IOD_PEP_disk | D295
PEPServer_A_Izpad | DIGITAL | IOD_PEP_disk | D296
PEPServer_B_Izpad | DIGITAL | IOD_PEP_disk | D297
PEPComSCADA_stevec3 | INT | IOD_PEP_mem | I298
PEPComSCADA_stevec | INT | IOD_PEP_mem | I300
PEPComSCADA3 | DIGITAL | IOD_PEP_TCP | 00057
PEPkom_nast_cas_izpada | INT | IOD_PEP_TCP | 40063

## XSoft
mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Write_BOOL(FC) | mod_Write_Word(FC) | mod_Write_Word(FC) | mod_Write_dWord(FC) | mod_Write_dWord(FC) | mod_Write_String(FC)
(*Branje BOOL*) | (*Branje INT*) | (*Branje UINT*) | (*Branje LONG*) | (*Branje REAL*) | (*Branje STRING*) | (*Pisanje BOOL*) | (*Pisanje INT*) | (*Pisanje UINT*) | (*Pisanje LONG*) | (*Pisanje REAL*) | (*Pisanje STRING*)
(**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**)
mind_bool[0]:=AlarmPozara; | mind[0]:=DateTime.Dan; |  |  |  | Read_String(sVar:=Date_Time[0],start:=5000); | 0:AlarmPozara:=Bit_0; | 0:DateTime.Dan:=Byte_0; |  |  |  | 5000:Date_Time[0]:=String_0;
mind_bool[1]:=ComSCADA; | mind[1]:=DateTime.Leto; |  |  |  | Read_String(sVar:=Date_Time[1],start:=5015); | 1:ComSCADA:=Bit_0; | 1:DateTime.Leto:=Byte_0; |  |  |  | 5015:Date_Time[1]:=String_0;
mind_bool[2]:=ComSCADA1; | mind[2]:=DateTime.Leto2; |  |  |  | Read_String(sVar:=Date_Time[2],start:=5030); | 2:ComSCADA1:=Bit_0; | 2:DateTime.Leto2:=Word_01; |  |  |  | 5030:Date_Time[2]:=String_0;
mind_bool[3]:=ErrComKlima; | mind[3]:=DateTime.Mesec; |  |  |  | Read_String(sVar:=Date_Time[3],start:=5045); | 3:ErrComKlima:=Bit_0; | 3:DateTime.Mesec:=Byte_0; |  |  |  | 5045:Date_Time[3]:=String_0;
mind_bool[4]:=ErrComPort2; | mind[4]:=DateTime.Minuta; |  |  |  | Read_String(sVar:=UserCurrentName,start:=5060); | 4:ErrComPort2:=Bit_0; | 4:DateTime.Minuta:=Byte_0; |  |  |  | 5060:UserCurrentName:=String_0;
mind_bool[5]:=ErrorComKlima.Error; | mind[5]:=DateTime.Sekunda; |  |  |  |  | 5:ErrorComKlima.Error:=Bit_0; | 5:DateTime.Sekunda:=Byte_0;
mind_bool[6]:=Klima[1].Alarm_pozar; | mind[6]:=DateTime.Ura; |  |  |  |  | 6:Klima[1].Alarm_pozar:=Bit_0; | 6:DateTime.Ura:=Byte_0;
mind_bool[7]:=Klima[1].DelVentHit1; | mind[7]:=ErrorComKlima.Code[10]; |  |  |  |  | 7:Klima[1].DelVentHit1:=Bit_0; | 7:ErrorComKlima.Code[10]:=Byte_0;
mind_bool[8]:=Klima[1].DelVentHit2; | mind[8]:=ErrorComKlima.Code[11]; |  |  |  |  | 8:Klima[1].DelVentHit2:=Bit_0; | 8:ErrorComKlima.Code[11]:=Byte_0;
mind_bool[9]:=Klima[1].Ni_pretoka; | mind[9]:=ErrorComKlima.Code[12]; |  |  |  |  | 9:Klima[1].Ni_pretoka:=Bit_0; | 9:ErrorComKlima.Code[12]:=Byte_0;
mind_bool[10]:=Klima[1].OkvaraRototerm; | mind[10]:=ErrorComKlima.Code[13]; |  |  |  |  | 10:Klima[1].OkvaraRototerm:=Bit_0; | 10:ErrorComKlima.Code[13]:=Byte_0;
mind_bool[11]:=Klima[1].OkvaraVlazNap; | mind[11]:=ErrorComKlima.Code[14]; |  |  |  |  | 11:Klima[1].OkvaraVlazNap:=Bit_0; | 11:ErrorComKlima.Code[14]:=Byte_0;
mind_bool[12]:=Klima[1].PreobMotCrpGrel; | mind[12]:=ErrorComKlima.Code[15]; |  |  |  |  | 12:Klima[1].PreobMotCrpGrel:=Bit_0; | 12:ErrorComKlima.Code[15]:=Byte_0;
mind_bool[13]:=Klima[1].PreobMotVent; | mind[13]:=ErrorComKlima.Code[1]; |  |  |  |  | 13:Klima[1].PreobMotVent:=Bit_0; | 13:ErrorComKlima.Code[1]:=Byte_0;
mind_bool[14]:=Klima[1].ProtizamrzZascAktivna; | mind[14]:=ErrorComKlima.Code[2]; |  |  |  |  | 14:Klima[1].ProtizamrzZascAktivna:=Bit_0; | 14:ErrorComKlima.Code[2]:=Byte_0;
mind_bool[15]:=Klima[1].VklopRegKlimata; | mind[15]:=ErrorComKlima.Code[3]; |  |  |  |  | 15:Klima[1].VklopRegKlimata:=Bit_0; | 15:ErrorComKlima.Code[3]:=Byte_0;
mind_bool[16]:=Klima[1].ZamasenostFiltra; | mind[16]:=ErrorComKlima.Code[4]; |  |  |  |  | 16:Klima[1].ZamasenostFiltra:=Bit_0; | 16:ErrorComKlima.Code[4]:=Byte_0;
mind_bool[17]:=Klima[1].ZdruzAlarmA; | mind[17]:=ErrorComKlima.Code[5]; |  |  |  |  | 17:Klima[1].ZdruzAlarmA:=Bit_0; | 17:ErrorComKlima.Code[5]:=Byte_0;
mind_bool[18]:=Klima[1].ZdruzAlarmB; | mind[18]:=ErrorComKlima.Code[6]; |  |  |  |  | 18:Klima[1].ZdruzAlarmB:=Bit_0; | 18:ErrorComKlima.Code[6]:=Byte_0;
mind_bool[19]:=KLIMAT_delovanje; | mind[19]:=ErrorComKlima.Code[7]; |  |  |  |  | 19:KLIMAT_delovanje:=Bit_0; | 19:ErrorComKlima.Code[7]:=Byte_0;
mind_bool[20]:=KLIMAT_napaka; | mind[20]:=ErrorComKlima.Code[8]; |  |  |  |  | 20:KLIMAT_napaka:=Bit_0; | 20:ErrorComKlima.Code[8]:=Byte_0;
mind_bool[21]:=KLIMAT_rezim1; | mind[21]:=ErrorComKlima.Code[9]; |  |  |  |  | 21:KLIMAT_rezim1:=Bit_0; | 21:ErrorComKlima.Code[9]:=Byte_0;
mind_bool[22]:=KLIMAT_rezim2; | mind[22]:=ErrorComKlima.Status; |  |  |  |  | 22:KLIMAT_rezim2:=Bit_0; | 22:ErrorComKlima.Status:=Word_01;
mind_bool[23]:=KlimaZdruzenAlarm; | mind[23]:=HIA1_vlaga_s; |  |  |  |  | 23:KlimaZdruzenAlarm:=Bit_0; | 23:HIA1_vlaga_s:=Word_01;
mind_bool[24]:=KomunikacijaErr; | mind[24]:=Klima[1].Analog_izh_mesanje; |  |  |  |  | 24:KomunikacijaErr:=Bit_0; | 24:Klima[1].Analog_izh_mesanje:=Word_01;
mind_bool[25]:=MEHCALEC_delovanje; | mind[25]:=Klima[1].Analog_izh_rekuperator; |  |  |  |  | 25:MEHCALEC_delovanje:=Bit_0; | 25:Klima[1].Analog_izh_rekuperator:=Word_01;
mind_bool[26]:=MEHCALEC_napaka; | mind[26]:=Klima[1].Analog_izh_VentGrelnika; |  |  |  |  | 26:MEHCALEC_napaka:=Bit_0; | 26:Klima[1].Analog_izh_VentGrelnika:=Word_01;
mind_bool[27]:=N_KLIMAT_napaka; | mind[27]:=Klima[1].Analog_izh_VentHlajenja; |  |  |  |  | 27:N_KLIMAT_napaka:=Bit_0; | 27:Klima[1].Analog_izh_VentHlajenja:=Word_01;
mind_bool[28]:=N_ROTOTERM_napaka; | mind[28]:=Klima[1].Dejanska_zel_temp; |  |  |  |  | 28:N_ROTOTERM_napaka:=Bit_0; | 28:Klima[1].Dejanska_zel_temp:=Word_01;
mind_bool[29]:=napaka_kom_panel; | mind[29]:=Klima[1].Hitrost_del_vent_disp; |  |  |  |  | 29:napaka_kom_panel:=Bit_0; | 29:Klima[1].Hitrost_del_vent_disp:=Word_01;
mind_bool[30]:=napaka_kom_scada; | mind[30]:=Klima[1].Max_vpih; |  |  |  |  | 30:napaka_kom_scada:=Bit_0; | 30:Klima[1].Max_vpih:=Word_01;
mind_bool[31]:=NapakaSenzorVlagaHIA1; | mind[31]:=Klima[1].Min_vpih; |  |  |  |  | 31:NapakaSenzorVlagaHIA1:=Bit_0; | 31:Klima[1].Min_vpih:=Word_01;
mind_bool[32]:=NapakaTSTempTIA1; | mind[32]:=Klima[1].Obrat_ure_Vent_h1; |  |  |  |  | 32:NapakaTSTempTIA1:=Bit_0; | 32:Klima[1].Obrat_ure_Vent_h1:=Word_01;
mind_bool[33]:=NiPretoka; | mind[33]:=Klima[1].Obrat_ure_Vent_h2; |  |  |  |  | 33:NiPretoka:=Bit_0; | 33:Klima[1].Obrat_ure_Vent_h2:=Word_01;
mind_bool[34]:=OkvaraRototerma; | mind[34]:=Klima[1].Pol_komp_konec; |  |  |  |  | 34:OkvaraRototerma:=Bit_0; | 34:Klima[1].Pol_komp_konec:=Word_01;
mind_bool[35]:=OkvaraVlazNap; | mind[35]:=Klima[1].Pol_komp_sprem_zel_vr; |  |  |  |  | 35:OkvaraVlazNap:=Bit_0; | 35:Klima[1].Pol_komp_sprem_zel_vr:=Word_01;
mind_bool[36]:=PreobMotCrpGr; | mind[36]:=Klima[1].Pol_komp_zacetek; |  |  |  |  | 36:PreobMotCrpGr:=Bit_0; | 36:Klima[1].Pol_komp_zacetek:=Word_01;
mind_bool[37]:=PreobMotVent; | mind[37]:=Klima[1].PreklopHitDelVent; |  |  |  |  | 37:PreobMotVent:=Bit_0; | 37:Klima[1].PreklopHitDelVent:=Word_01;
mind_bool[38]:=ProtizamrzZascAkt; | mind[38]:=Klima[1].Protizamrz_zascita; |  |  |  |  | 38:ProtizamrzZascAkt:=Bit_0; | 38:Klima[1].Protizamrz_zascita:=Word_01;
mind_bool[39]:=ROTOTERM_napaka; | mind[39]:=Klima[1].Rezim_delovanja; |  |  |  |  | 39:ROTOTERM_napaka:=Bit_0; | 39:Klima[1].Rezim_delovanja:=Word_01;
mind_bool[40]:=SetDateTime; | mind[40]:=Klima[1].Temperatura_dovoda; |  |  |  |  | 40:SetDateTime:=Bit_0; | 40:Klima[1].Temperatura_dovoda:=Word_01;
mind_bool[41]:=SetDateTimeDemand; | mind[41]:=Klima[1].Temperatura_prostora; |  |  |  |  | 41:SetDateTimeDemand:=Bit_0; | 41:Klima[1].Temperatura_prostora:=Word_01;
mind_bool[42]:=SetDateTimeError; | mind[42]:=Klima[1].TempPredPloscnimRekup; |  |  |  |  | 42:SetDateTimeError:=Bit_0; | 42:Klima[1].TempPredPloscnimRekup:=Word_01;
mind_bool[43]:=SetDateTimeFinished; | mind[43]:=Klima[1].TempZaPloscnimRekup; |  |  |  |  | 43:SetDateTimeFinished:=Bit_0; | 43:Klima[1].TempZaPloscnimRekup:=Word_01;
mind_bool[44]:=SlabaBaterijaPLC; | mind[44]:=Klima[1].Vlaga_v_prostoru; |  |  |  |  | 44:SlabaBaterijaPLC:=Bit_0; | 44:Klima[1].Vlaga_v_prostoru:=Word_01;
mind_bool[45]:=TIA1_previs_temp; | mind[45]:=Klima[1].VlagaVstopZrakaProstor; |  |  |  |  | 45:TIA1_previs_temp:=Bit_0; | 45:Klima[1].VlagaVstopZrakaProstor:=Word_01;
mind_bool[46]:=ups_alarm; | mind[46]:=Klima[1].Zel_temp_eko_gretja; |  |  |  |  | 46:ups_alarm:=Bit_0; | 46:Klima[1].Zel_temp_eko_gretja:=Word_01;
mind_bool[47]:=ups_baterijski_nac; | mind[47]:=Klima[1].Zel_temp_eko_hlajenja; |  |  |  |  | 47:ups_baterijski_nac:=Bit_0; | 47:Klima[1].Zel_temp_eko_hlajenja:=Word_01;
mind_bool[48]:=ups_polnjenje; | mind[48]:=Klima[1].Zel_temp_komf_gretja; |  |  |  |  | 48:ups_polnjenje:=Bit_0; | 48:Klima[1].Zel_temp_komf_gretja:=Word_01;
mind_bool[49]:=UserLoggedIn; | mind[49]:=Klima[1].Zel_temp_komf_hlajenja; |  |  |  |  | 49:UserLoggedIn:=Bit_0; | 49:Klima[1].Zel_temp_komf_hlajenja:=Word_01;
mind_bool[50]:=VLAZILEC_delovanje; | mind[50]:=Klima[1].Zim_komp_konec; |  |  |  |  | 50:VLAZILEC_delovanje:=Bit_0; | 50:Klima[1].Zim_komp_konec:=Word_01;
mind_bool[51]:=VLAZILEC_napaka; | mind[51]:=Klima[1].Zim_komp_sprem_zel_vr; |  |  |  |  | 51:VLAZILEC_napaka:=Bit_0; | 51:Klima[1].Zim_komp_sprem_zel_vr:=Word_01;
mind_bool[52]:=XVH_AlarmOn; | mind[52]:=Klima[1].Zim_komp_zacetek; |  |  |  |  | 52:XVH_AlarmOn:=Bit_0; | 52:Klima[1].Zim_komp_zacetek:=Word_01;
mind_bool[53]:=ZamasenostFiltra; | mind[53]:=Klima[1].ZimKompMinVpihKonec; |  |  |  |  | 53:ZamasenostFiltra:=Bit_0; | 53:Klima[1].ZimKompMinVpihKonec:=Word_01;
mind_bool[54]:=napaka_kom_scada2; | mind[54]:=Klima[1].ZimKompMinVpihZac; |  |  |  |  | 54:napaka_kom_scada2:=Bit_0; | 54:Klima[1].ZimKompMinVpihZac:=Word_01;
mind_bool[55]:=ComSCADA2; | mind[55]:=Klima[1].ZkompMinVpihSpremZelVr; |  |  |  |  | 55:ComSCADA2:=Bit_0; | 55:Klima[1].ZkompMinVpihSpremZelVr:=Word_01;
mind_bool[56]:=ComSCADA3; | mind[56]:=Klima[1].Zunanja_temp; |  |  |  |  | 56:ComSCADA3:=Bit_0; | 56:Klima[1].Zunanja_temp:=Word_01;
| mind[57]:=Klima_rezim; | [5 empty] | 57:Klima_rezim:=Byte_0;
| mind[58]:=TIA1_alarm; | [5 empty] | 58:TIA1_alarm:=Word_01;
| mind[59]:=TIA1_temp_s; | [5 empty] | 59:TIA1_temp_s:=Word_01;
| mind[60]:=UserCurrentLevel; | [5 empty] | 60:UserCurrentLevel:=Byte_0;
| mind[61]:=XVH_UPSstatus; | [5 empty] | 61:XVH_UPSstatus:=Byte_0;
| mind[62]:=kom_nast_cas_izpada; | [5 empty] | 62:kom_nast_cas_izpada:=Word_01;

## XSoft_EXP
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
PROGRAM mod_Read
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*Branje BOOL*)
(**)
mind_bool[0]:=AlarmPozara;
mind_bool[1]:=ComSCADA;
mind_bool[2]:=ComSCADA1;
mind_bool[3]:=ErrComKlima;
mind_bool[4]:=ErrComPort2;
mind_bool[5]:=ErrorComKlima.Error;
mind_bool[6]:=Klima[1].Alarm_pozar;
mind_bool[7]:=Klima[1].DelVentHit1;
mind_bool[8]:=Klima[1].DelVentHit2;
mind_bool[9]:=Klima[1].Ni_pretoka;
mind_bool[10]:=Klima[1].OkvaraRototerm;
mind_bool[11]:=Klima[1].OkvaraVlazNap;
mind_bool[12]:=Klima[1].PreobMotCrpGrel;
mind_bool[13]:=Klima[1].PreobMotVent;
mind_bool[14]:=Klima[1].ProtizamrzZascAktivna;
mind_bool[15]:=Klima[1].VklopRegKlimata;
mind_bool[16]:=Klima[1].ZamasenostFiltra;
mind_bool[17]:=Klima[1].ZdruzAlarmA;
mind_bool[18]:=Klima[1].ZdruzAlarmB;
mind_bool[19]:=KLIMAT_delovanje;
mind_bool[20]:=KLIMAT_napaka;
mind_bool[21]:=KLIMAT_rezim1;
mind_bool[22]:=KLIMAT_rezim2;
mind_bool[23]:=KlimaZdruzenAlarm;
mind_bool[24]:=KomunikacijaErr;
mind_bool[25]:=MEHCALEC_delovanje;
mind_bool[26]:=MEHCALEC_napaka;
mind_bool[27]:=N_KLIMAT_napaka;
mind_bool[28]:=N_ROTOTERM_napaka;
mind_bool[29]:=napaka_kom_panel;
mind_bool[30]:=napaka_kom_scada;
mind_bool[31]:=NapakaSenzorVlagaHIA1;
mind_bool[32]:=NapakaTSTempTIA1;
mind_bool[33]:=NiPretoka;
mind_bool[34]:=OkvaraRototerma;
mind_bool[35]:=OkvaraVlazNap;
mind_bool[36]:=PreobMotCrpGr;
mind_bool[37]:=PreobMotVent;
mind_bool[38]:=ProtizamrzZascAkt;
mind_bool[39]:=ROTOTERM_napaka;
mind_bool[40]:=SetDateTime;
mind_bool[41]:=SetDateTimeDemand;
mind_bool[42]:=SetDateTimeError;
mind_bool[43]:=SetDateTimeFinished;
mind_bool[44]:=SlabaBaterijaPLC;
mind_bool[45]:=TIA1_previs_temp;
mind_bool[46]:=ups_alarm;
mind_bool[47]:=ups_baterijski_nac;
mind_bool[48]:=ups_polnjenje;
mind_bool[49]:=UserLoggedIn;
mind_bool[50]:=VLAZILEC_delovanje;
mind_bool[51]:=VLAZILEC_napaka;
mind_bool[52]:=XVH_AlarmOn;
mind_bool[53]:=ZamasenostFiltra;
mind_bool[54]:=napaka_kom_scada2;
mind_bool[55]:=ComSCADA2;
mind_bool[56]:=ComSCADA3;
(*Branje INT*)
(**)
mind[0]:=DateTime.Dan;
mind[1]:=DateTime.Leto;
mind[2]:=DateTime.Leto2;
mind[3]:=DateTime.Mesec;
mind[4]:=DateTime.Minuta;
mind[5]:=DateTime.Sekunda;
mind[6]:=DateTime.Ura;
mind[7]:=ErrorComKlima.Code[10];
mind[8]:=ErrorComKlima.Code[11];
mind[9]:=ErrorComKlima.Code[12];
mind[10]:=ErrorComKlima.Code[13];
mind[11]:=ErrorComKlima.Code[14];
mind[12]:=ErrorComKlima.Code[15];
mind[13]:=ErrorComKlima.Code[1];
mind[14]:=ErrorComKlima.Code[2];
mind[15]:=ErrorComKlima.Code[3];
mind[16]:=ErrorComKlima.Code[4];
mind[17]:=ErrorComKlima.Code[5];
mind[18]:=ErrorComKlima.Code[6];
mind[19]:=ErrorComKlima.Code[7];
mind[20]:=ErrorComKlima.Code[8];
mind[21]:=ErrorComKlima.Code[9];
mind[22]:=ErrorComKlima.Status;
mind[23]:=HIA1_vlaga_s;
mind[24]:=Klima[1].Analog_izh_mesanje;
mind[25]:=Klima[1].Analog_izh_rekuperator;
mind[26]:=Klima[1].Analog_izh_VentGrelnika;
mind[27]:=Klima[1].Analog_izh_VentHlajenja;
mind[28]:=Klima[1].Dejanska_zel_temp;
mind[29]:=Klima[1].Hitrost_del_vent_disp;
mind[30]:=Klima[1].Max_vpih;
mind[31]:=Klima[1].Min_vpih;
mind[32]:=Klima[1].Obrat_ure_Vent_h1;
mind[33]:=Klima[1].Obrat_ure_Vent_h2;
mind[34]:=Klima[1].Pol_komp_konec;
mind[35]:=Klima[1].Pol_komp_sprem_zel_vr;
mind[36]:=Klima[1].Pol_komp_zacetek;
mind[37]:=Klima[1].PreklopHitDelVent;
mind[38]:=Klima[1].Protizamrz_zascita;
mind[39]:=Klima[1].Rezim_delovanja;
mind[40]:=Klima[1].Temperatura_dovoda;
mind[41]:=Klima[1].Temperatura_prostora;
mind[42]:=Klima[1].TempPredPloscnimRekup;
mind[43]:=Klima[1].TempZaPloscnimRekup;
mind[44]:=Klima[1].Vlaga_v_prostoru;
mind[45]:=Klima[1].VlagaVstopZrakaProstor;
mind[46]:=Klima[1].Zel_temp_eko_gretja;
mind[47]:=Klima[1].Zel_temp_eko_hlajenja;
mind[48]:=Klima[1].Zel_temp_komf_gretja;
mind[49]:=Klima[1].Zel_temp_komf_hlajenja;
mind[50]:=Klima[1].Zim_komp_konec;
mind[51]:=Klima[1].Zim_komp_sprem_zel_vr;
mind[52]:=Klima[1].Zim_komp_zacetek;
mind[53]:=Klima[1].ZimKompMinVpihKonec;
mind[54]:=Klima[1].ZimKompMinVpihZac;
mind[55]:=Klima[1].ZkompMinVpihSpremZelVr;
mind[56]:=Klima[1].Zunanja_temp;
mind[57]:=Klima_rezim;
mind[58]:=TIA1_alarm;
mind[59]:=TIA1_temp_s;
mind[60]:=UserCurrentLevel;
mind[61]:=XVH_UPSstatus;
mind[62]:=kom_nast_cas_izpada;
(*Branje UINT*)
(**)
(*Branje LONG*)
(**)
(*Branje REAL*)
(**)
(*Branje STRING*)
(**)
Read_String(sVar:=Date_Time[0],start:=5000);
Read_String(sVar:=Date_Time[1],start:=5015);
Read_String(sVar:=Date_Time[2],start:=5030);
Read_String(sVar:=Date_Time[3],start:=5045);
Read_String(sVar:=UserCurrentName,start:=5060);
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Bool : BOOL
VAR_INPUT
index: INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje BOOL*)
(**)
0:AlarmPozara:=Bit_0;
1:ComSCADA:=Bit_0;
2:ComSCADA1:=Bit_0;
3:ErrComKlima:=Bit_0;
4:ErrComPort2:=Bit_0;
5:ErrorComKlima.Error:=Bit_0;
6:Klima[1].Alarm_pozar:=Bit_0;
7:Klima[1].DelVentHit1:=Bit_0;
8:Klima[1].DelVentHit2:=Bit_0;
9:Klima[1].Ni_pretoka:=Bit_0;
10:Klima[1].OkvaraRototerm:=Bit_0;
11:Klima[1].OkvaraVlazNap:=Bit_0;
12:Klima[1].PreobMotCrpGrel:=Bit_0;
13:Klima[1].PreobMotVent:=Bit_0;
14:Klima[1].ProtizamrzZascAktivna:=Bit_0;
15:Klima[1].VklopRegKlimata:=Bit_0;
16:Klima[1].ZamasenostFiltra:=Bit_0;
17:Klima[1].ZdruzAlarmA:=Bit_0;
18:Klima[1].ZdruzAlarmB:=Bit_0;
19:KLIMAT_delovanje:=Bit_0;
20:KLIMAT_napaka:=Bit_0;
21:KLIMAT_rezim1:=Bit_0;
22:KLIMAT_rezim2:=Bit_0;
23:KlimaZdruzenAlarm:=Bit_0;
24:KomunikacijaErr:=Bit_0;
25:MEHCALEC_delovanje:=Bit_0;
26:MEHCALEC_napaka:=Bit_0;
27:N_KLIMAT_napaka:=Bit_0;
28:N_ROTOTERM_napaka:=Bit_0;
29:napaka_kom_panel:=Bit_0;
30:napaka_kom_scada:=Bit_0;
31:NapakaSenzorVlagaHIA1:=Bit_0;
32:NapakaTSTempTIA1:=Bit_0;
33:NiPretoka:=Bit_0;
34:OkvaraRototerma:=Bit_0;
35:OkvaraVlazNap:=Bit_0;
36:PreobMotCrpGr:=Bit_0;
37:PreobMotVent:=Bit_0;
38:ProtizamrzZascAkt:=Bit_0;
39:ROTOTERM_napaka:=Bit_0;
40:SetDateTime:=Bit_0;
41:SetDateTimeDemand:=Bit_0;
42:SetDateTimeError:=Bit_0;
43:SetDateTimeFinished:=Bit_0;
44:SlabaBaterijaPLC:=Bit_0;
45:TIA1_previs_temp:=Bit_0;
46:ups_alarm:=Bit_0;
47:ups_baterijski_nac:=Bit_0;
48:ups_polnjenje:=Bit_0;
49:UserLoggedIn:=Bit_0;
50:VLAZILEC_delovanje:=Bit_0;
51:VLAZILEC_napaka:=Bit_0;
52:XVH_AlarmOn:=Bit_0;
53:ZamasenostFiltra:=Bit_0;
54:napaka_kom_scada2:=Bit_0;
55:ComSCADA2:=Bit_0;
56:ComSCADA3:=Bit_0;
(*BOOL*)
END_CASE
END_FUNCTION
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_dWord : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje LONG*)
(**)
(*Pisanje REAL*)
(**)
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_String : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje STRING*)
(**)
5000:Date_Time[0]:=String_0;
5015:Date_Time[1]:=String_0;
5030:Date_Time[2]:=String_0;
5045:Date_Time[3]:=String_0;
5060:UserCurrentName:=String_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Word : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje INT*)
(**)
0:DateTime.Dan:=Byte_0;
1:DateTime.Leto:=Byte_0;
2:DateTime.Leto2:=Word_01;
3:DateTime.Mesec:=Byte_0;
4:DateTime.Minuta:=Byte_0;
5:DateTime.Sekunda:=Byte_0;
6:DateTime.Ura:=Byte_0;
7:ErrorComKlima.Code[10]:=Byte_0;
8:ErrorComKlima.Code[11]:=Byte_0;
9:ErrorComKlima.Code[12]:=Byte_0;
10:ErrorComKlima.Code[13]:=Byte_0;
11:ErrorComKlima.Code[14]:=Byte_0;
12:ErrorComKlima.Code[15]:=Byte_0;
13:ErrorComKlima.Code[1]:=Byte_0;
14:ErrorComKlima.Code[2]:=Byte_0;
15:ErrorComKlima.Code[3]:=Byte_0;
16:ErrorComKlima.Code[4]:=Byte_0;
17:ErrorComKlima.Code[5]:=Byte_0;
18:ErrorComKlima.Code[6]:=Byte_0;
19:ErrorComKlima.Code[7]:=Byte_0;
20:ErrorComKlima.Code[8]:=Byte_0;
21:ErrorComKlima.Code[9]:=Byte_0;
22:ErrorComKlima.Status:=Word_01;
23:HIA1_vlaga_s:=Word_01;
24:Klima[1].Analog_izh_mesanje:=Word_01;
25:Klima[1].Analog_izh_rekuperator:=Word_01;
26:Klima[1].Analog_izh_VentGrelnika:=Word_01;
27:Klima[1].Analog_izh_VentHlajenja:=Word_01;
28:Klima[1].Dejanska_zel_temp:=Word_01;
29:Klima[1].Hitrost_del_vent_disp:=Word_01;
30:Klima[1].Max_vpih:=Word_01;
31:Klima[1].Min_vpih:=Word_01;
32:Klima[1].Obrat_ure_Vent_h1:=Word_01;
33:Klima[1].Obrat_ure_Vent_h2:=Word_01;
34:Klima[1].Pol_komp_konec:=Word_01;
35:Klima[1].Pol_komp_sprem_zel_vr:=Word_01;
36:Klima[1].Pol_komp_zacetek:=Word_01;
37:Klima[1].PreklopHitDelVent:=Word_01;
38:Klima[1].Protizamrz_zascita:=Word_01;
39:Klima[1].Rezim_delovanja:=Word_01;
40:Klima[1].Temperatura_dovoda:=Word_01;
41:Klima[1].Temperatura_prostora:=Word_01;
42:Klima[1].TempPredPloscnimRekup:=Word_01;
43:Klima[1].TempZaPloscnimRekup:=Word_01;
44:Klima[1].Vlaga_v_prostoru:=Word_01;
45:Klima[1].VlagaVstopZrakaProstor:=Word_01;
46:Klima[1].Zel_temp_eko_gretja:=Word_01;
47:Klima[1].Zel_temp_eko_hlajenja:=Word_01;
48:Klima[1].Zel_temp_komf_gretja:=Word_01;
49:Klima[1].Zel_temp_komf_hlajenja:=Word_01;
50:Klima[1].Zim_komp_konec:=Word_01;
51:Klima[1].Zim_komp_sprem_zel_vr:=Word_01;
52:Klima[1].Zim_komp_zacetek:=Word_01;
53:Klima[1].ZimKompMinVpihKonec:=Word_01;
54:Klima[1].ZimKompMinVpihZac:=Word_01;
55:Klima[1].ZkompMinVpihSpremZelVr:=Word_01;
56:Klima[1].Zunanja_temp:=Word_01;
57:Klima_rezim:=Byte_0;
58:TIA1_alarm:=Word_01;
59:TIA1_temp_s:=Word_01;
60:UserCurrentLevel:=Byte_0;
61:XVH_UPSstatus:=Byte_0;
62:kom_nast_cas_izpada:=Word_01;
(*Pisanje UINT*)
(**)
;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
(*Modbus Slave Example*)
PROGRAM PLC_PRG_modnet
VAR
Slave_Adresa:BYTE:=2;
Slave_Port:INT:=502;
SlaveSetup:MBS_Setup;
SlavePoll:MBS_Poll;
SlaveAnswer:MBS_Answer;
step: USINT;
end :BOOL;
i: INT;
cycle :BOOL := FALSE; (* First cycle *)
OpenDefaultPort: BOOL;
Write_16: BOOL;
Write_15: BOOL;
Write_5: BOOL;
j: INT;
slavepollwOffset_temp: INT;
slaveanswerwCount_temp: INT;
slaveanswerwoffset_temp: INT;
END_VAR
(* @END_DECLARATION := '0' *)
(*Modbus Slave Example*)
IF Write_16=TRUE THEN (**)
FOR j := 0 TO (slaveanswerwCount_temp-1)/15 BY 1 DO (*vpiše se dword, real*)
wStr_0:=mind[slaveanswerwoffset_temp+j];
wStr_1:=mind[slaveanswerwoffset_temp+j+1];
wStr_2 :=mind[slaveanswerwoffset_temp+j+2];
wStr_3:=mind[slaveanswerwoffset_temp+j+3];
wStr_4:=mind[slaveanswerwoffset_temp+j+4];
wStr_5 :=mind[slaveanswerwoffset_temp+j+5];
wStr_6:=mind[slaveanswerwoffset_temp+j+6];
wStr_7:=mind[slaveanswerwoffset_temp+j+7];
wStr_8:=mind[slaveanswerwoffset_temp+j+8];
wStr_9:=mind[slaveanswerwoffset_temp+j+9];
wStr_10:=mind[slaveanswerwoffset_temp+j+10];
wStr_11:=mind[slaveanswerwoffset_temp+j+11];
wStr_12:=mind[slaveanswerwoffset_temp+j+12];
wStr_13:=mind[slaveanswerwoffset_temp+j+13];
wStr_14:=mind[slaveanswerwoffset_temp+j+14];
bStr_29:=0;
mod_Write_String(index:=slaveanswerwoffset_temp+j); (*vpis real in string*)
END_FOR;
FOR j := 1 TO slaveanswerwCount_temp-1 BY 2 DO (*vpiše se dword, real*)
Word_01:=mind[slaveanswerwoffset_temp+j-1];
Word_23:=mind[slaveanswerwoffset_temp+j];
mod_Write_dWord(index:=slaveanswerwoffset_temp+j); (*vpis real in dword*)
END_FOR;
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO (*vpiše se word*)
Word_01:=mind[slaveanswerwoffset_temp+j];
mod_Write_Word(index:=slaveanswerwoffset_temp+j); (*vpis word*)
END_FOR;
Write_16:=FALSE;
END_IF;
IF Write_5=TRUE OR Write_15=TRUE THEN (**)
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO
Bit_0:=mind_bool[slaveanswerwoffset_temp+j];
mod_Write_Bool(index:=slaveanswerwoffset_temp+j); (*vpis spremembe v spremenljivko*)
END_FOR;
Write_5:=FALSE;
Write_15:=FALSE;
END_IF;
(*iz scade ni komande za branje*)
IF Write_16=FALSE AND Write_5=FALSE AND Write_15=FALSE THEN
mod_Read();(*branje spremenljivk za scado*)
END_IF
(*Close all sockets on corresponding event*)
IF cycle = FALSE THEN
SysCallbackRegister(INDEXOF(Callback_Stop),event_stop);
SysCallbackRegister(INDEXOF(Callback_Reset),event_before_reset);
SysCallbackRegister(INDEXOF(Callback_Reset),event_shutdown);
cycle := TRUE;
END_IF
(*Close all connections via application *)
IF end = TRUE THEN
MBS_CloseAllConnections();
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=FALSE); (*Close port*)
step := 0;
END_IF
IF OpenDefaultPort=TRUE THEN
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=TRUE); (*Close port*)
step := 0;
OpenDefaultPort:=FALSE;
END_IF
(* State machine for setup, poll and answer *)
CASE step OF
0:(**)
SlaveSetup.bUnitIdentifier:=Slave_Adresa;(*Subunitnumber*)
slavesetup.wDefaultPort:=Slave_Port;(*Standartport *)
SlaveSetup.xAdditionalPortActive:=FALSE;(*Port opened or closed*)
SlaveSetup.xSecureMode:=FALSE;(*If TRUE only preset IPs are accepted*)
SlaveSetup.tTimeout:=T#3m;(*Timeout if no communication with slave established*)
SlaveSetup(xStrobe:=TRUE);(*Strobe starts function*)
IF slavesetup.xBusy = FALSE THEN
slavesetup(xstrobe := FALSE);
step := 1 ;
END_IF;
1:(**)
SlavePoll(xStrobe:=TRUE);(*Searching for master commands*)
IF NOT SlavePoll.xBusy THEN
step:=2;
SlavePoll(xStrobe:=FALSE);
END_IF;
2:(**)
step:= 1;
CASE SlavePoll.bFunctionCode OF (*Connect accepted pollparameters with answerparameters*)
8:(**)(*Poll answers*)
;
15:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind_bool[slaveanswer.woffset+i] := slavepoll.xarData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.xarData:=slavepoll.xarData;
Write_15:=TRUE;
16:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind[slaveanswer.woffset+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.wardata := slavepoll.warData;
Write_16:=TRUE;
1,2:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slavepoll.wcount-1 BY 1 DO
slaveanswer.xarData[i]:=mind_bool[slavepoll.woffset+i]; (*Read from Data-array*)
END_FOR
3,4:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slaveanswer.wCount-1 BY 1 DO
slaveanswer.warData[i]:=mind[slavepoll.woffset+i];(*Read from Data-array*)
END_FOR
5:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
mind_bool[slavepoll.woffset]:=slavepoll.xarData[0];(*Write to Data-array*)
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.xarData := slavepoll.xardata;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
Write_5:=TRUE;
6:
slaveanswer.bFunctionCode:= slavepoll.bFunctionCode;
mind[slavepoll.woffset]:= slavepoll.warData[0];(*Write to Data-array*)
slaveanswer.wOffset:= slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wardata := slavepoll.wardata;
23:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
FOR i:= 0 TO slavepoll.wCountAdd-1 BY 1 DO
mind[slavepoll.woffsetadd+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
FOR i := 0 TO slavepoll.wCount BY 1 DO
slaveanswer.warData[i] := mind[1+slavepoll.woffset+i];(*Read from Data-array*)
END_FOR;
END_CASE;
IF slavepoll.xAvailable = TRUE THEN
slaveanswer();(*When Data ready, send answer*)
END_IF
END_CASE;
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_dWord : BOOL
VAR_INPUT
dVAR: DWORD;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
DWord_0:=dVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_Real : BOOL
VAR_INPUT
rVAR: REAL;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
Real_0:=rVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_String : BOOL
VAR_INPUT
sVar: STRING;
start:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
String_0:=LEFT (sVar,29);
mind[start]:=wStr_0;
mind[start+1]:=wStr_1;
mind[start+2]:=wStr_2;
mind[start+3]:=wStr_3;
mind[start+4]:=wStr_4;
mind[start+5]:=wStr_5;
mind[start+6]:=wStr_6;
mind[start+7]:=wStr_7;
mind[start+8]:=wStr_8;
mind[start+9]:=wStr_9;
mind[start+10]:=wStr_10;
mind[start+11]:=wStr_11;
mind[start+12]:=wStr_12;
mind[start+13]:=wStr_13;
bStr_29:=0;
mind[start+14]:=wStr_14;
END_FUNCTION
(* @GLOBAL_VARIABLE_LIST := 'Global_Variables_Modnet' *)
(* @PATH := '' *)
(* @SYMFILEFLAGS := '2048' *)
VAR_GLOBAL
(*delovno polje za modnet komunikacijo*)
mind :ARRAY [0..9999] OF WORD;
mind_bool :ARRAY [0..9999] OF BOOL; (*Buffer-Array*)
(*Delovni markerji //*)
Bit_0 AT %MX0.0 : BOOL;
Byte_0 AT %MB0 : BYTE;
Byte_1 AT %MB1 : BYTE;
Byte_2 AT %MB2 : BYTE;
Byte_3 AT %MB3 : BYTE;
Real_0 AT %MR0:REAL;
DWord_0 AT %MD0:DWORD;
Word_01 AT %MW0:WORD;
Word_23 AT %MW2:WORD;
String_0 AT %MW10:STRING;
wStr_0 AT %MW10:WORD;
wStr_1 AT %MW12:WORD;
wStr_2 AT %MW14:WORD;
wStr_3 AT %MW16:WORD;
wStr_4 AT %MW18:WORD;
wStr_5 AT %MW20:WORD;
wStr_6 AT %MW22:WORD;
wStr_7 AT %MW24:WORD;
wStr_8 AT %MW26:WORD;
wStr_9 AT %MW28:WORD;
wStr_10 AT %MW30:WORD;
wStr_11 AT %MW32:WORD;
wStr_12 AT %MW34:WORD;
wStr_13 AT %MW36:WORD;
wStr_14 AT %MW38:WORD;
bStr_00 AT %MB10:BYTE;
bStr_01 AT %MB11:BYTE;
bStr_02 AT %MB12:BYTE;
bStr_03 AT %MB13:BYTE;
bStr_04 AT %MB14:BYTE;
bStr_05 AT %MB15:BYTE;
bStr_06 AT %MB16:BYTE;
bStr_07 AT %MB17:BYTE;
bStr_08 AT %MB18:BYTE;
bStr_09 AT %MB19:BYTE;
bStr_10 AT %MB20:BYTE;
bStr_11 AT %MB21:BYTE;
bStr_12 AT %MB22:BYTE;
bStr_13 AT %MB23:BYTE;
bStr_14 AT %MB24:BYTE;
bStr_15 AT %MB25:BYTE;
bStr_16 AT %MB26:BYTE;
bStr_17 AT %MB27:BYTE;
bStr_18 AT %MB28:BYTE;
bStr_19 AT %MB29:BYTE;
bStr_20 AT %MB30:BYTE;
bStr_21 AT %MB31:BYTE;
bStr_22 AT %MB32:BYTE;
bStr_23 AT %MB33:BYTE;
bStr_24 AT %MB34:BYTE;
bStr_25 AT %MB35:BYTE;
bStr_26 AT %MB36:BYTE;
bStr_27 AT %MB37:BYTE;
bStr_28 AT %MB38:BYTE;
bStr_29 AT %MB39:BYTE;
(********************************************)
END_VAR
(* @OBJECT_END := 'Global_Variables_Modnet' *)
(* @CONNECTIONS := Global_Variables_Modnet
FILENAME : ''
FILETIME : 0
EXPORT : 0
NUMOFCONNECTIONS : 0
*)
(*KONEC_KODA*)