## Prva stran
variable | 1236 | 1.KORAK | variable_1 | 2.KORAK | KORAKI!
Device name | Tip | število spremenljivk | Tip (izbrani) | Zamenjaj z | 1.V Sheet "variable" skopiraj vsebino iz variable.dbf - iz Citect SCAD-a projekta, ki ga želiš pretvoriti.
IOD_SS1 | BCD | 0 | BCD | INT | 2.V polje A3 vpiši Device ime spremenljivk ki se bodo prenašale preko Modnet protokola
| BYTE | 11 | BYTE | BYTE | 3.V polje A6 vpiši ime krmilnika (npr.:PLC1, če je adresa v spremenljivkah PLC1:.NapakaKoncnega_stikala, drugače pusti polje prazno)
OPC name | DIGITAL | 201 | DIGITAL | DIGITAL | 4. Pritisni gumb 1.KORAK (V poljih C3:C10 se izpiše število spremenljivk, ki imajo Device enak tistemu v polju A3)
SS1 | INT | 2 | INT | INT | 5. Pritisni gumb 2.KORAK (V Sheet-u variable_1 se naredi seznam spremenljivk, ki se bodo prenačale preko Modnet protokola)
| LONG | 0 | LONG | LONG | 6. Pritisni gumb 3.KORAK (V poljih C15:C24 se izpiše število spremnljiv po tipih, v poljih F15:F24 se izpiše število potrebni wordow/coilov za prenos spremnljivk)
| REAL | 245 | REAL | REAL | 7. 4.KORAK: V polja C29:C38 je potrebno ročno vpisati začetne naslove spremnljivk. Potrebno je paziti na:
| STRING | 1 | UINT | UINT | *naslov se morajo začeti z lihim številom npr.:1, 101, 551
| UINT | 19 | STRING | STRING | *naslove je potrebno nastaviti tako, da se naslovi sremenljivk ne more prekrivati (naslovi spremenjivk gredo od (začetnega naslova) do (začetnega naslova+število potrebnih wordow))
8. Pritisni gumb 5.KORAK (V Sheet-u variable_2 se naredi seznam spremenljivk, ki so tokrat sortirana po tipih)
9. Pritisni gumb 6.KORAK (V Sheet-u variable_3 se naredi seznam spremenljivk, katerih Device se zamenja z devicom v polju C41)
Trajanje makroja | variable_1 |  |  | 3.KORAK | 10. Pritisni gumb 7.KORAK (V Sheet-u variable_new se generira seznam spremenljivk. To vsebino je potrebno skopirati v variable.dbf)
0 | Tip | število spremenljivk | TIP | št.potrebnih coilov/wordov | *ta korak traja nekoliko dalj časa (odvisno od števila spremenljivk)
| BCD | 0 | BCD | 0 | *če se pojavi težava z adresami ki se začnejo z 0000 (npr.: "00001" se spremeni na "1") je potrebno uporabiti priloženo (prazno) variable.dbf ali v
| BYTE | 0 | BYTE | 0 | ProjectEditoju/VariableTags na poljubni spremenljki nastaviti adreso" 00001"
| DIGITAL | 201 | DIGITAL | 201 (Coil) | 11. Pritisni gumb 8.KORAK in 9.KORAK (V Sheet-u Xsoft se generira koda)
| INT | 13 | INT | 13 (word) | 12. S pritiskom na gumb 10.KORAK se zgenerira EXP koda za Xsoft (Xsoft_EXP)
| LONG | 0 | LONG | 0 (word) | 13. S pritiskom na gumb Save*.EXP se avtomatsko generira datoka *.EXP
| REAL | 245 | REAL | 490 (word)
| STRING | 1 | STRING | 15 (word)
| UINT | 19 | UINT | 19 (word)
POZOR!
*V Sheet-u variable mora biti vsebina skopirana od polja A1 naprej (če je katera vrstica prazna makroji ne bodo delovali pravilno)
*Ena "STRING" spremenljivka zasede 15wordow (to pomeni 29 znakov, 1BYTE=1STRING)
|  | 4.KORAK(vpiši ročno) | variable_2 | 5.KORAK | *Dolžina "STRING" spremenljivk je 29 znakov (lahko tudi več vendar ne z uporabno tega dokumenta in XSoft programa,potrebna je modifikacija makrojev in Xsoft programa)
| Tip | Začetni naslov |  | Sortiraj | *Vsi stringi so enake dolžine (29)
| BCD |  |  | BCD | *"BYTE" spremenljivke se v variable.dbf spremenijo v "INT" (prenašanje posameznih bytov ni mogoče, niti naslavaljanje v citectscadi)
| BYTE |  |  | DIGITAL | *Naslovi spremenljivk se morajo obvezno začeti z lihim naslovom (preizkušeno je z začetnimi naslovi, ki se izpišejo po pritisku na gumb Ponastavi)
| DIGITAL | 1 |  | BYTE | *Z pritiskom na gumb RESET se pobriše vsebina vseh Sheet-ov razen Sheet-a variable (makor reset se izvaja precej časa)
| INT | 1 |  | INT | *makroji ne delujejo pravilno,če je v Sheet-u variable več kot 9999 vrstic oz. spremenljivk (število vseh spremnljivk je prikazano v polju B1)
| LONG | 3001 |  | LONG | *če se vsebine iz variable_new ne gre skpirat v variable.dbf datotek, vsebino skopirajte najprej v *.txt datoteko in nato v variable.dbf
| REAL | 4001 |  | REAL | *v polju A14 na Sheet-u Prva stran se prikazuje število ciklop do konca izvedbe makroja (samo za gumb 7.KORAK)
| STRING | 5001 |  | STRING
| UINT | 6001 |  | UINT
| variable_3 | 6.KORAK | variable_new | 7.KORAK
| New Device name | IOD_SS1_TCP |  | Nova variable dbf
|  |  | xSoft | 8.KORAK in 9.KORAK
xSoft koda
xSoft_EXP
Izvoz*.EXP
1.KORAK
2.KORAK
3.KORAK
5.KORAK
6.KORAK
7.KORAK
8.KORAK
9.KORAK
RESET
Ponastavi
10.KORAK
Save*.EXP

## variable
SS1Pulzi1s | DIGITAL | IOD_SS1_disk | D1 | [8 empty] | 0x05c00010
SS1PMMPhase1Current1_med60in80 | DIGITAL | IOD_SS1_disk | D2 | [8 empty] | 0x05c00020
SS1PMMPhase1Current2_med60in80 | DIGITAL | IOD_SS1_disk | D3 | [8 empty] | 0x05c00030
SS1PMMPhase1Current3_med60in80 | DIGITAL | IOD_SS1_disk | D4 | [8 empty] | 0x05c00040
SS1PMMPhase1Current4_med60in80 | DIGITAL | IOD_SS1_disk | D5 | [8 empty] | 0x05c00050
SS1PMMPhase1Current5_med60in80 | DIGITAL | IOD_SS1_disk | D6 | [8 empty] | 0x05c00060
SS1PMMPhase1Current6_med60in80 | DIGITAL | IOD_SS1_disk | D7 | [8 empty] | 0x05c00070
SS1PMMPhase1Current7_med60in80 | DIGITAL | IOD_SS1_disk | D8 | [8 empty] | 0x05c00080
SS1PMMPhase1Current8_med60in80 | DIGITAL | IOD_SS1_disk | D9 | [8 empty] | 0x05c00090
SS1PMMPhase1Current9_med60in80 | DIGITAL | IOD_SS1_disk | D10 | [8 empty] | 0x05c000a0
SS1PMMPhase1Current10_med60in80 | DIGITAL | IOD_SS1_disk | D11 | [8 empty] | 0x05c000b0
SS1PMMPhase1Current11_med60in80 | DIGITAL | IOD_SS1_disk | D12 | [8 empty] | 0x05c000c0
SS1PMMPhase1Current12_med60in80 | DIGITAL | IOD_SS1_disk | D13 | [8 empty] | 0x05c000d0
SS1PMMPhase1Current13_med60in80 | DIGITAL | IOD_SS1_disk | D14 | [8 empty] | 0x05c000e0
SS1PMMPhase1Current14_med60in80 | DIGITAL | IOD_SS1_disk | D15 | [8 empty] | 0x05c000f0
SS1PMMPhase1Current15_med60in80 | DIGITAL | IOD_SS1_disk | D16 | [8 empty] | 0x05c00100
SS1PMMPhase1Current16_med60in80 | DIGITAL | IOD_SS1_disk | D17 | [8 empty] | 0x05c00110
SS1PMMPhase1Current17_med60in80 | DIGITAL | IOD_SS1_disk | D18 | [8 empty] | 0x05c00120
SS1PMMPhase1Current18_med60in80 | DIGITAL | IOD_SS1_disk | D19 | [8 empty] | 0x05c00130
SS1PMMPhase1Current19_med60in80 | DIGITAL | IOD_SS1_disk | D20 | [8 empty] | 0x05c00140
SS1PMMPhase1Current20_med60in80 | DIGITAL | IOD_SS1_disk | D21 | [8 empty] | 0x05c00150
SS1PMMPhase1Current21_med60in80 | DIGITAL | IOD_SS1_disk | D22 | [8 empty] | 0x05c00160
SS1PMMPhase1Current22_med60in80 | DIGITAL | IOD_SS1_disk | D23 | [8 empty] | 0x05c00170
SS1PMMPhase1Current23_med60in80 | DIGITAL | IOD_SS1_disk | D24 | [8 empty] | 0x05c00180
SS1PMMPhase1Current24_med60in80 | DIGITAL | IOD_SS1_disk | D25 | [8 empty] | 0x05c00190
SS1PMMPhase1Current25_med60in80 | DIGITAL | IOD_SS1_disk | D26 | [8 empty] | 0x05c001a0
SS1PMMPhase1Current26_med60in80 | DIGITAL | IOD_SS1_disk | D27 | [8 empty] | 0x05c001b0
SS1PMMPhase1Current27_med60in80 | DIGITAL | IOD_SS1_disk | D28 | [8 empty] | 0x05c001c0
SS1PMMPhase1Current28_med60in80 | DIGITAL | IOD_SS1_disk | D29 | [8 empty] | 0x05c001d0
SS1PMMPhase1Current29_med60in80 | DIGITAL | IOD_SS1_disk | D30 | [8 empty] | 0x05c001e0
SS1PMMPhase1Current30_med60in80 | DIGITAL | IOD_SS1_disk | D31 | [8 empty] | 0x05c001f0
SS1PMMPhase1Current31_med60in80 | DIGITAL | IOD_SS1_disk | D32 | [8 empty] | 0x05c00200
SS1PMMPhase1Current32_med60in80 | DIGITAL | IOD_SS1_disk | D33 | [8 empty] | 0x05c00210
SS1PMMPhase1Current33_med60in80 | DIGITAL | IOD_SS1_disk | D34 | [8 empty] | 0x05c00220
SS1PMMPhase1Current34_med60in80 | DIGITAL | IOD_SS1_disk | D35 | [8 empty] | 0x05c00230
SS1PMMPhase1Current35_med60in80 | DIGITAL | IOD_SS1_disk | D36 | [8 empty] | 0x05c00240
SS1PMMPhase1Current36_med60in80 | DIGITAL | IOD_SS1_disk | D37 | [8 empty] | 0x05c00250
SS1PMMPhase1Current37_med60in80 | DIGITAL | IOD_SS1_disk | D38 | [8 empty] | 0x05c00260
SS1PMMPhase1Current38_med60in80 | DIGITAL | IOD_SS1_disk | D39 | [8 empty] | 0x05c00270
SS1PMMPhase1Current39_med60in80 | DIGITAL | IOD_SS1_disk | D40 | [8 empty] | 0x05c00280
SS1PMMPhase1Current40_med60in80 | DIGITAL | IOD_SS1_disk | D41 | [8 empty] | 0x05c00290
SS1PMMPhase1Current41_med60in80 | DIGITAL | IOD_SS1_disk | D42 | [8 empty] | 0x05c002a0
SS1PMMPhase1Current42_med60in80 | DIGITAL | IOD_SS1_disk | D43 | [8 empty] | 0x05c002b0
SS1PMMPhase1Current1_nad80 | DIGITAL | IOD_SS1_disk | D44 | [8 empty] | 0x05c002c0
SS1PMMPhase1Current2_nad80 | DIGITAL | IOD_SS1_disk | D45 | [8 empty] | 0x05c002d0
SS1PMMPhase1Current3_nad80 | DIGITAL | IOD_SS1_disk | D46 | [8 empty] | 0x05c002e0
SS1PMMPhase1Current4_nad80 | DIGITAL | IOD_SS1_disk | D47 | [8 empty] | 0x05c002f0
SS1PMMPhase1Current5_nad80 | DIGITAL | IOD_SS1_disk | D48 | [8 empty] | 0x05c00300
SS1PMMPhase1Current6_nad80 | DIGITAL | IOD_SS1_disk | D49 | [8 empty] | 0x05c00310
SS1PMMPhase1Current7_nad80 | DIGITAL | IOD_SS1_disk | D50 | [8 empty] | 0x05c00320
SS1PMMPhase1Current8_nad80 | DIGITAL | IOD_SS1_disk | D51 | [8 empty] | 0x05c00330
SS1PMMPhase1Current9_nad80 | DIGITAL | IOD_SS1_disk | D52 | [8 empty] | 0x05c00340
SS1PMMPhase1Current10_nad80 | DIGITAL | IOD_SS1_disk | D53 | [8 empty] | 0x05c00350
SS1PMMPhase1Current11_nad80 | DIGITAL | IOD_SS1_disk | D54 | [8 empty] | 0x05c00360
SS1PMMPhase1Current12_nad80 | DIGITAL | IOD_SS1_disk | D55 | [8 empty] | 0x05c00370
SS1PMMPhase1Current13_nad80 | DIGITAL | IOD_SS1_disk | D56 | [8 empty] | 0x05c00380
SS1PMMPhase1Current14_nad80 | DIGITAL | IOD_SS1_disk | D57 | [8 empty] | 0x05c00390
SS1PMMPhase1Current15_nad80 | DIGITAL | IOD_SS1_disk | D58 | [8 empty] | 0x05c003a0
SS1PMMPhase1Current16_nad80 | DIGITAL | IOD_SS1_disk | D59 | [8 empty] | 0x05c003b0
SS1PMMPhase1Current17_nad80 | DIGITAL | IOD_SS1_disk | D60 | [8 empty] | 0x05c003c0
SS1PMMPhase1Current18_nad80 | DIGITAL | IOD_SS1_disk | D61 | [8 empty] | 0x05c003d0
SS1PMMPhase1Current19_nad80 | DIGITAL | IOD_SS1_disk | D62 | [8 empty] | 0x05c003e0
SS1PMMPhase1Current20_nad80 | DIGITAL | IOD_SS1_disk | D63 | [8 empty] | 0x05c003f0
SS1PMMPhase1Current21_nad80 | DIGITAL | IOD_SS1_disk | D64 | [8 empty] | 0x05c00400
SS1PMMPhase1Current22_nad80 | DIGITAL | IOD_SS1_disk | D65 | [8 empty] | 0x05c00410
SS1PMMPhase1Current23_nad80 | DIGITAL | IOD_SS1_disk | D66 | [8 empty] | 0x05c00420
SS1PMMPhase1Current24_nad80 | DIGITAL | IOD_SS1_disk | D67 | [8 empty] | 0x05c00430
SS1PMMPhase1Current25_nad80 | DIGITAL | IOD_SS1_disk | D68 | [8 empty] | 0x05c00440
SS1PMMPhase1Current26_nad80 | DIGITAL | IOD_SS1_disk | D69 | [8 empty] | 0x05c00450
SS1PMMPhase1Current27_nad80 | DIGITAL | IOD_SS1_disk | D70 | [8 empty] | 0x05c00460
SS1PMMPhase1Current28_nad80 | DIGITAL | IOD_SS1_disk | D71 | [8 empty] | 0x05c00470
SS1PMMPhase1Current29_nad80 | DIGITAL | IOD_SS1_disk | D72 | [8 empty] | 0x05c00480
SS1PMMPhase1Current30_nad80 | DIGITAL | IOD_SS1_disk | D73 | [8 empty] | 0x05c00490
SS1PMMPhase1Current31_nad80 | DIGITAL | IOD_SS1_disk | D74 | [8 empty] | 0x05c004a0
SS1PMMPhase1Current32_nad80 | DIGITAL | IOD_SS1_disk | D75 | [8 empty] | 0x05c004b0
SS1PMMPhase1Current33_nad80 | DIGITAL | IOD_SS1_disk | D76 | [8 empty] | 0x05c004c0
SS1PMMPhase1Current34_nad80 | DIGITAL | IOD_SS1_disk | D77 | [8 empty] | 0x05c004d0
SS1PMMPhase1Current35_nad80 | DIGITAL | IOD_SS1_disk | D78 | [8 empty] | 0x05c004e0
SS1PMMPhase1Current36_nad80 | DIGITAL | IOD_SS1_disk | D79 | [8 empty] | 0x05c004f0
SS1PMMPhase1Current37_nad80 | DIGITAL | IOD_SS1_disk | D80 | [8 empty] | 0x05c00500
SS1PMMPhase1Current38_nad80 | DIGITAL | IOD_SS1_disk | D81 | [8 empty] | 0x05c00510
SS1PMMPhase1Current39_nad80 | DIGITAL | IOD_SS1_disk | D82 | [8 empty] | 0x05c00520
SS1PMMPhase1Current40_nad80 | DIGITAL | IOD_SS1_disk | D83 | [8 empty] | 0x05c00530
SS1PMMPhase1Current41_nad80 | DIGITAL | IOD_SS1_disk | D84 | [8 empty] | 0x05c00540
SS1PMMPhase1Current42_nad80 | DIGITAL | IOD_SS1_disk | D85 | [8 empty] | 0x05c00550
SS1PMMPhase2Current1_nad80 | DIGITAL | IOD_SS1_disk | D86 | [8 empty] | 0x05c00560
SS1PMMPhase2Current2_nad80 | DIGITAL | IOD_SS1_disk | D87 | [8 empty] | 0x05c00570
SS1PMMPhase2Current3_nad80 | DIGITAL | IOD_SS1_disk | D88 | [8 empty] | 0x05c00580
SS1PMMPhase2Current4_nad80 | DIGITAL | IOD_SS1_disk | D89 | [8 empty] | 0x05c00590
SS1PMMPhase2Current5_nad80 | DIGITAL | IOD_SS1_disk | D90 | [8 empty] | 0x05c005a0
SS1PMMPhase2Current6_nad80 | DIGITAL | IOD_SS1_disk | D91 | [8 empty] | 0x05c005b0
SS1PMMPhase2Current7_nad80 | DIGITAL | IOD_SS1_disk | D92 | [8 empty] | 0x05c005c0
SS1PMMPhase2Current8_nad80 | DIGITAL | IOD_SS1_disk | D93 | [8 empty] | 0x05c005d0
SS1PMMPhase2Current9_nad80 | DIGITAL | IOD_SS1_disk | D94 | [8 empty] | 0x05c005e0
SS1PMMPhase2Current10_nad80 | DIGITAL | IOD_SS1_disk | D95 | [8 empty] | 0x05c005f0
SS1PMMPhase2Current11_nad80 | DIGITAL | IOD_SS1_disk | D96 | [8 empty] | 0x05c00600
SS1PMMPhase2Current12_nad80 | DIGITAL | IOD_SS1_disk | D97 | [8 empty] | 0x05c00610
SS1PMMPhase2Current13_nad80 | DIGITAL | IOD_SS1_disk | D98 | [8 empty] | 0x05c00620
SS1PMMPhase2Current14_nad80 | DIGITAL | IOD_SS1_disk | D99 | [8 empty] | 0x05c00630
SS1PMMPhase2Current15_nad80 | DIGITAL | IOD_SS1_disk | D100 | [8 empty] | 0x05c00640
SS1PMMPhase2Current16_nad80 | DIGITAL | IOD_SS1_disk | D101 | [8 empty] | 0x05c00650
SS1PMMPhase2Current17_nad80 | DIGITAL | IOD_SS1_disk | D102 | [8 empty] | 0x05c00660
SS1PMMPhase2Current18_nad80 | DIGITAL | IOD_SS1_disk | D103 | [8 empty] | 0x05c00670
SS1PMMPhase2Current19_nad80 | DIGITAL | IOD_SS1_disk | D104 | [8 empty] | 0x05c00680
SS1PMMPhase2Current20_nad80 | DIGITAL | IOD_SS1_disk | D105 | [8 empty] | 0x05c00690
SS1PMMPhase2Current21_nad80 | DIGITAL | IOD_SS1_disk | D106 | [8 empty] | 0x05c006a0
SS1PMMPhase2Current22_nad80 | DIGITAL | IOD_SS1_disk | D107 | [8 empty] | 0x05c006b0
SS1PMMPhase2Current23_nad80 | DIGITAL | IOD_SS1_disk | D108 | [8 empty] | 0x05c006c0
SS1PMMPhase2Current24_nad80 | DIGITAL | IOD_SS1_disk | D109 | [8 empty] | 0x05c006d0
SS1PMMPhase2Current25_nad80 | DIGITAL | IOD_SS1_disk | D110 | [8 empty] | 0x05c006e0
SS1PMMPhase2Current26_nad80 | DIGITAL | IOD_SS1_disk | D111 | [8 empty] | 0x05c006f0
SS1PMMPhase2Current27_nad80 | DIGITAL | IOD_SS1_disk | D112 | [8 empty] | 0x05c00700
SS1PMMPhase2Current28_nad80 | DIGITAL | IOD_SS1_disk | D113 | [8 empty] | 0x05c00710
SS1PMMPhase2Current29_nad80 | DIGITAL | IOD_SS1_disk | D114 | [8 empty] | 0x05c00720
SS1PMMPhase2Current30_nad80 | DIGITAL | IOD_SS1_disk | D115 | [8 empty] | 0x05c00730
SS1PMMPhase2Current31_nad80 | DIGITAL | IOD_SS1_disk | D116 | [8 empty] | 0x05c00740
SS1PMMPhase2Current32_nad80 | DIGITAL | IOD_SS1_disk | D117 | [8 empty] | 0x05c00750
SS1PMMPhase2Current33_nad80 | DIGITAL | IOD_SS1_disk | D118 | [8 empty] | 0x05c00760
SS1PMMPhase2Current34_nad80 | DIGITAL | IOD_SS1_disk | D119 | [8 empty] | 0x05c00770
SS1PMMPhase2Current35_nad80 | DIGITAL | IOD_SS1_disk | D120 | [8 empty] | 0x05c00780
SS1PMMPhase2Current36_nad80 | DIGITAL | IOD_SS1_disk | D121 | [8 empty] | 0x05c00790
SS1PMMPhase2Current37_nad80 | DIGITAL | IOD_SS1_disk | D122 | [8 empty] | 0x05c007a0
SS1PMMPhase2Current38_nad80 | DIGITAL | IOD_SS1_disk | D123 | [8 empty] | 0x05c007b0
SS1PMMPhase2Current39_nad80 | DIGITAL | IOD_SS1_disk | D124 | [8 empty] | 0x05c007c0
SS1PMMPhase2Current40_nad80 | DIGITAL | IOD_SS1_disk | D125 | [8 empty] | 0x05c007d0
SS1PMMPhase2Current41_nad80 | DIGITAL | IOD_SS1_disk | D126 | [8 empty] | 0x05c007e0
SS1PMMPhase2Current42_nad80 | DIGITAL | IOD_SS1_disk | D127 | [8 empty] | 0x05c007f0
SS1PMMPhase3Current1_nad80 | DIGITAL | IOD_SS1_disk | D128 | [8 empty] | 0x05c00800
SS1PMMPhase3Current2_nad80 | DIGITAL | IOD_SS1_disk | D129 | [8 empty] | 0x05c00810
SS1PMMPhase3Current3_nad80 | DIGITAL | IOD_SS1_disk | D130 | [8 empty] | 0x05c00820
SS1PMMPhase3Current4_nad80 | DIGITAL | IOD_SS1_disk | D131 | [8 empty] | 0x05c00830
SS1PMMPhase3Current5_nad80 | DIGITAL | IOD_SS1_disk | D132 | [8 empty] | 0x05c00840
SS1PMMPhase3Current6_nad80 | DIGITAL | IOD_SS1_disk | D133 | [8 empty] | 0x05c00850
SS1PMMPhase3Current7_nad80 | DIGITAL | IOD_SS1_disk | D134 | [8 empty] | 0x05c00860
SS1PMMPhase3Current8_nad80 | DIGITAL | IOD_SS1_disk | D135 | [8 empty] | 0x05c00870
SS1PMMPhase3Current9_nad80 | DIGITAL | IOD_SS1_disk | D136 | [8 empty] | 0x05c00880
SS1PMMPhase3Current10_nad80 | DIGITAL | IOD_SS1_disk | D137 | [8 empty] | 0x05c00890
SS1PMMPhase3Current11_nad80 | DIGITAL | IOD_SS1_disk | D138 | [8 empty] | 0x05c008a0
SS1PMMPhase3Current12_nad80 | DIGITAL | IOD_SS1_disk | D139 | [8 empty] | 0x05c008b0
SS1PMMPhase3Current13_nad80 | DIGITAL | IOD_SS1_disk | D140 | [8 empty] | 0x05c008c0
SS1PMMPhase3Current14_nad80 | DIGITAL | IOD_SS1_disk | D141 | [8 empty] | 0x05c008d0
SS1PMMPhase3Current15_nad80 | DIGITAL | IOD_SS1_disk | D142 | [8 empty] | 0x05c008e0
SS1PMMPhase3Current16_nad80 | DIGITAL | IOD_SS1_disk | D143 | [8 empty] | 0x05c008f0
SS1PMMPhase3Current17_nad80 | DIGITAL | IOD_SS1_disk | D144 | [8 empty] | 0x05c00900
SS1PMMPhase3Current18_nad80 | DIGITAL | IOD_SS1_disk | D145 | [8 empty] | 0x05c00910
SS1PMMPhase3Current19_nad80 | DIGITAL | IOD_SS1_disk | D146 | [8 empty] | 0x05c00920
SS1PMMPhase3Current20_nad80 | DIGITAL | IOD_SS1_disk | D147 | [8 empty] | 0x05c00930
SS1PMMPhase3Current21_nad80 | DIGITAL | IOD_SS1_disk | D148 | [8 empty] | 0x05c00940
SS1PMMPhase3Current22_nad80 | DIGITAL | IOD_SS1_disk | D149 | [8 empty] | 0x05c00950
SS1PMMPhase3Current23_nad80 | DIGITAL | IOD_SS1_disk | D150 | [8 empty] | 0x05c00960
SS1PMMPhase3Current24_nad80 | DIGITAL | IOD_SS1_disk | D151 | [8 empty] | 0x05c00970
SS1PMMPhase3Current25_nad80 | DIGITAL | IOD_SS1_disk | D152 | [8 empty] | 0x05c00980
SS1PMMPhase3Current26_nad80 | DIGITAL | IOD_SS1_disk | D153 | [8 empty] | 0x05c00990
SS1PMMPhase3Current27_nad80 | DIGITAL | IOD_SS1_disk | D154 | [8 empty] | 0x05c009a0
SS1PMMPhase3Current28_nad80 | DIGITAL | IOD_SS1_disk | D155 | [8 empty] | 0x05c009b0
SS1PMMPhase3Current29_nad80 | DIGITAL | IOD_SS1_disk | D156 | [8 empty] | 0x05c009c0
SS1PMMPhase3Current30_nad80 | DIGITAL | IOD_SS1_disk | D157 | [8 empty] | 0x05c009d0
SS1PMMPhase3Current31_nad80 | DIGITAL | IOD_SS1_disk | D158 | [8 empty] | 0x05c009e0
SS1PMMPhase3Current32_nad80 | DIGITAL | IOD_SS1_disk | D159 | [8 empty] | 0x05c009f0
SS1PMMPhase3Current33_nad80 | DIGITAL | IOD_SS1_disk | D160 | [8 empty] | 0x05c00a00
SS1PMMPhase3Current34_nad80 | DIGITAL | IOD_SS1_disk | D161 | [8 empty] | 0x05c00a10
SS1PMMPhase3Current35_nad80 | DIGITAL | IOD_SS1_disk | D162 | [8 empty] | 0x05c00a20
SS1PMMPhase3Current36_nad80 | DIGITAL | IOD_SS1_disk | D163 | [8 empty] | 0x05c00a30
SS1PMMPhase3Current37_nad80 | DIGITAL | IOD_SS1_disk | D164 | [8 empty] | 0x05c00a40
SS1PMMPhase3Current38_nad80 | DIGITAL | IOD_SS1_disk | D165 | [8 empty] | 0x05c00a50
SS1PMMPhase3Current39_nad80 | DIGITAL | IOD_SS1_disk | D166 | [8 empty] | 0x05c00a60
SS1PMMPhase3Current40_nad80 | DIGITAL | IOD_SS1_disk | D167 | [8 empty] | 0x05c00a70
SS1PMMPhase3Current41_nad80 | DIGITAL | IOD_SS1_disk | D168 | [8 empty] | 0x05c00a80
SS1PMMPhase3Current42_nad80 | DIGITAL | IOD_SS1_disk | D169 | [8 empty] | 0x05c00a90
SS1PMMPhase2Current1_med60in80 | DIGITAL | IOD_SS1_disk | D170 | [8 empty] | 0x05c00aa0
SS1PMMPhase2Current2_med60in80 | DIGITAL | IOD_SS1_disk | D171 | [8 empty] | 0x05c00ab0
SS1PMMPhase2Current3_med60in80 | DIGITAL | IOD_SS1_disk | D172 | [8 empty] | 0x05c00ac0
SS1PMMPhase2Current4_med60in80 | DIGITAL | IOD_SS1_disk | D173 | [8 empty] | 0x05c00ad0
SS1PMMPhase2Current5_med60in80 | DIGITAL | IOD_SS1_disk | D174 | [8 empty] | 0x05c00ae0
SS1PMMPhase2Current6_med60in80 | DIGITAL | IOD_SS1_disk | D175 | [8 empty] | 0x05c00af0
SS1PMMPhase2Current7_med60in80 | DIGITAL | IOD_SS1_disk | D176 | [8 empty] | 0x05c00b00
SS1PMMPhase2Current8_med60in80 | DIGITAL | IOD_SS1_disk | D177 | [8 empty] | 0x05c00b10
SS1PMMPhase2Current9_med60in80 | DIGITAL | IOD_SS1_disk | D178 | [8 empty] | 0x05c00b20
SS1PMMPhase2Current10_med60in80 | DIGITAL | IOD_SS1_disk | D179 | [8 empty] | 0x05c00b30
SS1PMMPhase2Current11_med60in80 | DIGITAL | IOD_SS1_disk | D180 | [8 empty] | 0x05c00b40
SS1PMMPhase2Current12_med60in80 | DIGITAL | IOD_SS1_disk | D181 | [8 empty] | 0x05c00b50
SS1PMMPhase2Current13_med60in80 | DIGITAL | IOD_SS1_disk | D182 | [8 empty] | 0x05c00b60
SS1PMMPhase2Current14_med60in80 | DIGITAL | IOD_SS1_disk | D183 | [8 empty] | 0x05c00b70
SS1PMMPhase2Current15_med60in80 | DIGITAL | IOD_SS1_disk | D184 | [8 empty] | 0x05c00b80
SS1PMMPhase2Current16_med60in80 | DIGITAL | IOD_SS1_disk | D185 | [8 empty] | 0x05c00b90
SS1PMMPhase2Current17_med60in80 | DIGITAL | IOD_SS1_disk | D186 | [8 empty] | 0x05c00ba0
SS1PMMPhase2Current18_med60in80 | DIGITAL | IOD_SS1_disk | D187 | [8 empty] | 0x05c00bb0
SS1PMMPhase2Current19_med60in80 | DIGITAL | IOD_SS1_disk | D188 | [8 empty] | 0x05c00bc0
SS1PMMPhase2Current20_med60in80 | DIGITAL | IOD_SS1_disk | D189 | [8 empty] | 0x05c00bd0
SS1PMMPhase2Current21_med60in80 | DIGITAL | IOD_SS1_disk | D190 | [8 empty] | 0x05c00be0
SS1PMMPhase2Current22_med60in80 | DIGITAL | IOD_SS1_disk | D191 | [8 empty] | 0x05c00bf0
SS1PMMPhase2Current23_med60in80 | DIGITAL | IOD_SS1_disk | D192 | [8 empty] | 0x05c00c00
SS1PMMPhase2Current24_med60in80 | DIGITAL | IOD_SS1_disk | D193 | [8 empty] | 0x05c00c10
SS1PMMPhase2Current25_med60in80 | DIGITAL | IOD_SS1_disk | D194 | [8 empty] | 0x05c00c20
SS1PMMPhase2Current26_med60in80 | DIGITAL | IOD_SS1_disk | D195 | [8 empty] | 0x05c00c30
SS1PMMPhase2Current27_med60in80 | DIGITAL | IOD_SS1_disk | D196 | [8 empty] | 0x05c00c40
SS1PMMPhase2Current28_med60in80 | DIGITAL | IOD_SS1_disk | D197 | [8 empty] | 0x05c00c50
SS1PMMPhase2Current29_med60in80 | DIGITAL | IOD_SS1_disk | D198 | [8 empty] | 0x05c00c60
SS1PMMPhase2Current30_med60in80 | DIGITAL | IOD_SS1_disk | D199 | [8 empty] | 0x05c00c70
SS1PMMPhase2Current31_med60in80 | DIGITAL | IOD_SS1_disk | D200 | [8 empty] | 0x05c00c80
SS1PMMPhase2Current32_med60in80 | DIGITAL | IOD_SS1_disk | D201 | [8 empty] | 0x05c00c90
SS1PMMPhase2Current33_med60in80 | DIGITAL | IOD_SS1_disk | D202 | [8 empty] | 0x05c00ca0
SS1PMMPhase2Current34_med60in80 | DIGITAL | IOD_SS1_disk | D203 | [8 empty] | 0x05c00cb0
SS1PMMPhase2Current35_med60in80 | DIGITAL | IOD_SS1_disk | D204 | [8 empty] | 0x05c00cc0
SS1PMMPhase2Current36_med60in80 | DIGITAL | IOD_SS1_disk | D205 | [8 empty] | 0x05c00cd0
SS1PMMPhase2Current37_med60in80 | DIGITAL | IOD_SS1_disk | D206 | [8 empty] | 0x05c00ce0
SS1PMMPhase2Current38_med60in80 | DIGITAL | IOD_SS1_disk | D207 | [8 empty] | 0x05c00cf0
SS1PMMPhase2Current39_med60in80 | DIGITAL | IOD_SS1_disk | D208 | [8 empty] | 0x05c00d00
SS1PMMPhase2Current40_med60in80 | DIGITAL | IOD_SS1_disk | D209 | [8 empty] | 0x05c00d10
SS1PMMPhase2Current41_med60in80 | DIGITAL | IOD_SS1_disk | D210 | [8 empty] | 0x05c00d20
SS1PMMPhase2Current42_med60in80 | DIGITAL | IOD_SS1_disk | D211 | [8 empty] | 0x05c00d30
SS1PMMPhase3Current1_med60in80 | DIGITAL | IOD_SS1_disk | D212 | [8 empty] | 0x05c00d40
SS1PMMPhase3Current2_med60in80 | DIGITAL | IOD_SS1_disk | D213 | [8 empty] | 0x05c00d50
SS1PMMPhase3Current3_med60in80 | DIGITAL | IOD_SS1_disk | D214 | [8 empty] | 0x05c00d60
SS1PMMPhase3Current4_med60in80 | DIGITAL | IOD_SS1_disk | D215 | [8 empty] | 0x05c00d70
SS1PMMPhase3Current5_med60in80 | DIGITAL | IOD_SS1_disk | D216 | [8 empty] | 0x05c00d80
SS1PMMPhase3Current6_med60in80 | DIGITAL | IOD_SS1_disk | D217 | [8 empty] | 0x05c00d90
SS1PMMPhase3Current7_med60in80 | DIGITAL | IOD_SS1_disk | D218 | [8 empty] | 0x05c00da0
SS1PMMPhase3Current8_med60in80 | DIGITAL | IOD_SS1_disk | D219 | [8 empty] | 0x05c00db0
SS1PMMPhase3Current9_med60in80 | DIGITAL | IOD_SS1_disk | D220 | [8 empty] | 0x05c00dc0
SS1PMMPhase3Current10_med60in80 | DIGITAL | IOD_SS1_disk | D221 | [8 empty] | 0x05c00dd0
SS1PMMPhase3Current11_med60in80 | DIGITAL | IOD_SS1_disk | D222 | [8 empty] | 0x05c00de0
SS1PMMPhase3Current12_med60in80 | DIGITAL | IOD_SS1_disk | D223 | [8 empty] | 0x05c00df0
SS1PMMPhase3Current13_med60in80 | DIGITAL | IOD_SS1_disk | D224 | [8 empty] | 0x05c00e00
SS1PMMPhase3Current14_med60in80 | DIGITAL | IOD_SS1_disk | D225 | [8 empty] | 0x05c00e10
SS1PMMPhase3Current15_med60in80 | DIGITAL | IOD_SS1_disk | D226 | [8 empty] | 0x05c00e20
SS1PMMPhase3Current16_med60in80 | DIGITAL | IOD_SS1_disk | D227 | [8 empty] | 0x05c00e30
SS1PMMPhase3Current17_med60in80 | DIGITAL | IOD_SS1_disk | D228 | [8 empty] | 0x05c00e40
SS1PMMPhase3Current18_med60in80 | DIGITAL | IOD_SS1_disk | D229 | [8 empty] | 0x05c00e50
SS1PMMPhase3Current19_med60in80 | DIGITAL | IOD_SS1_disk | D230 | [8 empty] | 0x05c00e60
SS1PMMPhase3Current20_med60in80 | DIGITAL | IOD_SS1_disk | D231 | [8 empty] | 0x05c00e70
SS1PMMPhase3Current21_med60in80 | DIGITAL | IOD_SS1_disk | D232 | [8 empty] | 0x05c00e80
SS1PMMPhase3Current22_med60in80 | DIGITAL | IOD_SS1_disk | D233 | [8 empty] | 0x05c00e90
SS1PMMPhase3Current23_med60in80 | DIGITAL | IOD_SS1_disk | D234 | [8 empty] | 0x05c00ea0
SS1PMMPhase3Current24_med60in80 | DIGITAL | IOD_SS1_disk | D235 | [8 empty] | 0x05c00eb0
SS1PMMPhase3Current25_med60in80 | DIGITAL | IOD_SS1_disk | D236 | [8 empty] | 0x05c00ec0
SS1PMMPhase3Current26_med60in80 | DIGITAL | IOD_SS1_disk | D237 | [8 empty] | 0x05c00ed0
SS1PMMPhase3Current27_med60in80 | DIGITAL | IOD_SS1_disk | D238 | [8 empty] | 0x05c00ee0
SS1PMMPhase3Current28_med60in80 | DIGITAL | IOD_SS1_disk | D239 | [8 empty] | 0x05c00ef0
SS1PMMPhase3Current29_med60in80 | DIGITAL | IOD_SS1_disk | D240 | [8 empty] | 0x05c00f00
SS1PMMPhase3Current30_med60in80 | DIGITAL | IOD_SS1_disk | D241 | [8 empty] | 0x05c00f10
SS1PMMPhase3Current31_med60in80 | DIGITAL | IOD_SS1_disk | D242 | [8 empty] | 0x05c00f20
SS1PMMPhase3Current32_med60in80 | DIGITAL | IOD_SS1_disk | D243 | [8 empty] | 0x05c00f30
SS1PMMPhase3Current33_med60in80 | DIGITAL | IOD_SS1_disk | D244 | [8 empty] | 0x05c00f40
SS1PMMPhase3Current34_med60in80 | DIGITAL | IOD_SS1_disk | D245 | [8 empty] | 0x05c00f50
SS1PMMPhase3Current35_med60in80 | DIGITAL | IOD_SS1_disk | D246 | [8 empty] | 0x05c00f60
SS1PMMPhase3Current36_med60in80 | DIGITAL | IOD_SS1_disk | D247 | [8 empty] | 0x05c00f70
SS1PMMPhase3Current37_med60in80 | DIGITAL | IOD_SS1_disk | D248 | [8 empty] | 0x05c00f80
SS1PMMPhase3Current38_med60in80 | DIGITAL | IOD_SS1_disk | D249 | [8 empty] | 0x05c00f90
SS1PMMPhase3Current39_med60in80 | DIGITAL | IOD_SS1_disk | D250 | [8 empty] | 0x05c00fa0
SS1PMMPhase3Current40_med60in80 | DIGITAL | IOD_SS1_disk | D251 | [8 empty] | 0x05c00fb0
SS1PMMPhase3Current41_med60in80 | DIGITAL | IOD_SS1_disk | D252 | [8 empty] | 0x05c00fc0
SS1PMMPhase3Current42_med60in80 | DIGITAL | IOD_SS1_disk | D253 | [8 empty] | 0x05c00fd0
SS1UserloggedIn_mem | DIGITAL | IOD_SS1_disk | D254 | [8 empty] | 0x05c00fe0
SS1PMMPoljeFazaATok1_16_nad80 | DIGITAL | IOD_SS1_disk | D2000[16] | [8 empty] | 0x05c00ff0
SS1PMMPoljeFazaATok17_32_nad80 | DIGITAL | IOD_SS1_disk | D2017[16] | [8 empty] | 0x05c01000
SS1PMMPoljeFazaATok33_42_nad80 | DIGITAL | IOD_SS1_disk | D2034[16] | [8 empty] | 0x05c01010
SS1PMMPoljeFazaBTok1_16_nad80 | DIGITAL | IOD_SS1_disk | D2051[16] | [8 empty] | 0x05c01020
SS1PMMPoljeFazaBTok17_32_nad80 | DIGITAL | IOD_SS1_disk | D2068[16] | [8 empty] | 0x05c01030
SS1PMMPoljeFazaBTok33_42_nad80 | DIGITAL | IOD_SS1_disk | D2085[16] | [8 empty] | 0x05c01040
SS1PMMPoljeFazaCTok1_16_nad80 | DIGITAL | IOD_SS1_disk | D2102[16] | [8 empty] | 0x05c01050
SS1PMMPoljeFazaCTok17_32_nad80 | DIGITAL | IOD_SS1_disk | D2119[16] | [8 empty] | 0x05c01060
SS1PMMPoljeFazaCTok33_42_nad80 | DIGITAL | IOD_SS1_disk | D2136[16] | [8 empty] | 0x05c01070
SS1PMMPoljeFazaATok1_16_med60_80 | DIGITAL | IOD_SS1_disk | D2153[16] | [8 empty] | 0x05c01080
SS1PMMPoljeFazaATok17_32_med60_80 | DIGITAL | IOD_SS1_disk | D2170[16] | [8 empty] | 0x05c01090
SS1PMMPoljeFazaATok33_42_med60_80 | DIGITAL | IOD_SS1_disk | D2187[16] | [8 empty] | 0x05c010a0
SS1PMMPoljeFazaBTok1_16_med60_80 | DIGITAL | IOD_SS1_disk | D2204[16] | [8 empty] | 0x05c010b0
SS1PMMPoljeFazaBTok17_32_med60_80 | DIGITAL | IOD_SS1_disk | D2221[16] | [8 empty] | 0x05c010c0
SS1PMMPoljeFazaBTok33_42_med60_80 | DIGITAL | IOD_SS1_disk | D2238[16] | [8 empty] | 0x05c010d0
SS1PMMPoljeFazaCTok1_16_med60_80 | DIGITAL | IOD_SS1_disk | D2255[16] | [8 empty] | 0x05c010e0
SS1PMMPoljeFazaCTok17_32_med60_80 | DIGITAL | IOD_SS1_disk | D2272[16] | [8 empty] | 0x05c010f0
SS1PMMPoljeFazaCTok33_42_med60_80 | DIGITAL | IOD_SS1_disk | D2289[16] | [8 empty] | 0x05c01100
ASS1_omogoci_sms | DIGITAL | IOD_SS1_disk | D500[200] | [8 empty] | 0x05c01110
SS1PrikaziPMM | DIGITAL | IOD_SS1_disk | D300 | [8 empty] | 0x05c01120
SS1PrikaziSP1 | DIGITAL | IOD_SS1_disk | D301 | [8 empty] | 0x05c01130
SS1PrikaziSP2 | DIGITAL | IOD_SS1_disk | D302 | [8 empty] | 0x05c01140
SS1PrikaziSP3 | DIGITAL | IOD_SS1_disk | D303 | [8 empty] | 0x05c01150
SS1PrikaziSP4 | DIGITAL | IOD_SS1_disk | D304 | [8 empty] | 0x05c01160
SS1PrikaziSP5 | DIGITAL | IOD_SS1_disk | D305 | [8 empty] | 0x05c01170
SS1PrikaziKlimat1 | DIGITAL | IOD_SS1_disk | D306 | [8 empty] | 0x05c01180
SS1PrikaziKlimat2 | DIGITAL | IOD_SS1_disk | D307 | [8 empty] | 0x05c01190
SS1PrikaziKlimat3 | DIGITAL | IOD_SS1_disk | D308 | [8 empty] | 0x05c011a0
SS1PMM_2x63_VirB_zavihek | DIGITAL | IOD_SS1_disk | D309 | [8 empty] | 0x05c011b0
SS1PMM_2x63_VirA_zavihek | DIGITAL | IOD_SS1_disk | D310 | [8 empty] | 0x05c011c0
SS1AlarmKlimat1_Napaka_Omogoci | DIGITAL | IOD_SS1_disk | D3000 | [8 empty] | 0x05c011d0
SS1AlarmKlimat2_Napaka_Omogoci | DIGITAL | IOD_SS1_disk | D3001 | [8 empty] | 0x05c011e0
SS1AlarmKlimat3_Napaka_Omogoci | DIGITAL | IOD_SS1_disk | D3002 | [8 empty] | 0x05c011f0
SS1AlarmSP1_Napaka_Omogoci | DIGITAL | IOD_SS1_disk | D3003 | [8 empty] | 0x05c01200
SS1AlarmSP2_Napaka_Omogoci | DIGITAL | IOD_SS1_disk | D3004 | [8 empty] | 0x05c01210
SS1AlarmSP3_Napaka_Omogoci | DIGITAL | IOD_SS1_disk | D3005 | [8 empty] | 0x05c01220
SS1AlarmSP4_Napaka_Omogoci | DIGITAL | IOD_SS1_disk | D3006 | [8 empty] | 0x05c01230
SS1AlarmSP5_Napaka_Omogoci | DIGITAL | IOD_SS1_disk | D3007 | [8 empty] | 0x05c01240
SS1NapakaSenzorTemp1_Omogoci | DIGITAL | IOD_SS1_disk | D3008 | [8 empty] | 0x05c01250
SS1NapakaSenzorTemp2_Omogoci | DIGITAL | IOD_SS1_disk | D3009 | [8 empty] | 0x05c01260
SS1NapakaSenzorTemp3_Omogoci | DIGITAL | IOD_SS1_disk | D3010 | [8 empty] | 0x05c01270
SS1NapakaSenzorTempKontrSoba_Omogoci | DIGITAL | IOD_SS1_disk | D3011 | [8 empty] | 0x05c01280
SS1NapakaSenzorTempLinkProstor_Omogoci | DIGITAL | IOD_SS1_disk | D3012 | [8 empty] | 0x05c01290
SS1NapakaSenzorVlaga1_Omogoci | DIGITAL | IOD_SS1_disk | D3013 | [8 empty] | 0x05c012a0
SS1NapakaSenzorVlaga2_Omogoci | DIGITAL | IOD_SS1_disk | D3014 | [8 empty] | 0x05c012b0
SS1NapakaSenzorVlaga3_Omogoci | DIGITAL | IOD_SS1_disk | D3015 | [8 empty] | 0x05c012c0
SS1NapakaSenzorVlagaKontrSoba_Omogoci | DIGITAL | IOD_SS1_disk | D3016 | [8 empty] | 0x05c012d0
SS1NapakaSenzorVlagaLinkProstor_Omogoci | DIGITAL | IOD_SS1_disk | D3017 | [8 empty] | 0x05c012e0
SS1OpozoriloBaterijaPLC_Omogoci | DIGITAL | IOD_SS1_disk | D3018 | [8 empty] | 0x05c012f0
SS1PMMOverCurrentBetw1_VirB_Omogoci | DIGITAL | IOD_SS1_disk | D3019 | [8 empty] | 0x05c01300
SS1PMMOverCurrentBetw2_VirB_Omogoci | DIGITAL | IOD_SS1_disk | D3020 | [8 empty] | 0x05c01310
SS1PMMOverCurrentBetw3_VirB_Omogoci | DIGITAL | IOD_SS1_disk | D3021 | [8 empty] | 0x05c01320
SS1PMMOverCurrentBetw1_VirA_Omogoci | DIGITAL | IOD_SS1_disk | D3022 | [8 empty] | 0x05c01330
SS1PMMOverCurrentBetw2_VirA_Omogoci | DIGITAL | IOD_SS1_disk | D3023 | [8 empty] | 0x05c01340
SS1PMMOverCurrentBetw3_VirA_Omogoci | DIGITAL | IOD_SS1_disk | D3024 | [8 empty] | 0x05c01350
SS1PMMOverCurrentOver1_VirB_Omogoci | DIGITAL | IOD_SS1_disk | D3025 | [8 empty] | 0x05c01360
SS1PMMOverCurrentOver2_VirB_Omogoci | DIGITAL | IOD_SS1_disk | D3026 | [8 empty] | 0x05c01370
SS1PMMOverCurrentOver3_VirB_Omogoci | DIGITAL | IOD_SS1_disk | D3027 | [8 empty] | 0x05c01380
SS1PMMOverCurrentOver1_VirA_Omogoci | DIGITAL | IOD_SS1_disk | D3028 | [8 empty] | 0x05c01390
SS1PMMOverCurrentOver2_VirA_Omogoci | DIGITAL | IOD_SS1_disk | D3029 | [8 empty] | 0x05c013a0
SS1PMMOverCurrentOver3_VirA_Omogoci | DIGITAL | IOD_SS1_disk | D3030 | [8 empty] | 0x05c013b0
SS1PMM1OverVoltage_Omogoci | DIGITAL | IOD_SS1_disk | D3031 | [8 empty] | 0x05c013c0
SS1AlarmUPSKrmOmara_Alarm_Omogoci | DIGITAL | IOD_SS1_disk | D3032 | [8 empty] | 0x05c013d0
SS1StanjeUPSKrmOmara_BaterijskiNacin_Omogoci | DIGITAL | IOD_SS1_disk | D3033 | [8 empty] | 0x05c013e0
SS1StanjeUPSKrmOmara_Polnenje_Omogoci | DIGITAL | IOD_SS1_disk | D3034 | [8 empty] | 0x05c013f0
SS1AlarmLAH1_RazlitjeVode_Omogoci | DIGITAL | IOD_SS1_disk | D3035 | [8 empty] | 0x05c01400
SS1AlarmLAH2_RazlitjeVode_Omogoci | DIGITAL | IOD_SS1_disk | D3036 | [8 empty] | 0x05c01410
SS1ErrComPort2_Omogoci | DIGITAL | IOD_SS1_disk | D3037 | [8 empty] | 0x05c01420
SS1ErrComPanelPLC_Omogoci | DIGITAL | IOD_SS1_disk | D3038 | [8 empty] | 0x05c01430
SS1ErrComKlima1_Omogoci | DIGITAL | IOD_SS1_disk | D3039 | [8 empty] | 0x05c01440
SS1ErrComKlima2_Omogoci | DIGITAL | IOD_SS1_disk | D3040 | [8 empty] | 0x05c01450
SS1ErrComKlima3_Omogoci | DIGITAL | IOD_SS1_disk | D3041 | [8 empty] | 0x05c01460
SS1ErrComPMM_Omogoci | DIGITAL | IOD_SS1_disk | D3042 | [8 empty] | 0x05c01470
SS1KlimaError1AlarmKompresor1_Omogoci | DIGITAL | IOD_SS1_disk | D3043 | [8 empty] | 0x05c01480
SS1KlimaError1AlarmKompresor2_Omogoci | DIGITAL | IOD_SS1_disk | D3044 | [8 empty] | 0x05c01490
SS1KlimaError1NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS1_disk | D3045 | [8 empty] | 0x05c014a0
SS1KlimaError1NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS1_disk | D3046 | [8 empty] | 0x05c014b0
SS1KlimaError1NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS1_disk | D3047 | [8 empty] | 0x05c014c0
SS1KlimaError1FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3048 | [8 empty] | 0x05c014d0
SS1KlimaError1ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS1_disk | D3049 | [8 empty] | 0x05c014e0
SS1KlimaError1ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS1_disk | D3050 | [8 empty] | 0x05c014f0
SS1KlimaError1PozarniAlarm_Omogoci | DIGITAL | IOD_SS1_disk | D3051 | [8 empty] | 0x05c01500
SS1KlimaError1ZamasenFilter_Omogoci | DIGITAL | IOD_SS1_disk | D3052 | [8 empty] | 0x05c01510
SS1KlimaError1VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS1_disk | D3053 | [8 empty] | 0x05c01520
SS1KlimaError1NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS1_disk | D3054 | [8 empty] | 0x05c01530
SS1KlimaError1VisokaVlaznost_Omogoci | DIGITAL | IOD_SS1_disk | D3055 | [8 empty] | 0x05c01540
SS1KlimaError1NizkaVlaznost_Omogoci | DIGITAL | IOD_SS1_disk | D3056 | [8 empty] | 0x05c01550
SS1KlimaError1Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3057 | [8 empty] | 0x05c01560
SS1KlimaError1Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3058 | [8 empty] | 0x05c01570
SS1KlimaError1VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3059 | [8 empty] | 0x05c01580
SS1KlimaError1NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS1_disk | D3060 | [8 empty] | 0x05c01590
SS1KlimaError1NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS1_disk | D3061 | [8 empty] | 0x05c015a0
SS1KlimaError1NapakaSenzorPritiska_Omogoci | DIGITAL | IOD_SS1_disk | D3062 | [8 empty] | 0x05c015b0
SS1KlimaError1VisokTokVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3063 | [8 empty] | 0x05c015c0
SS1KlimaError1NiVodeVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3064 | [8 empty] | 0x05c015d0
SS1KlimaError1NiTokaVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3065 | [8 empty] | 0x05c015e0
SS1KlimaError1VisokPritiskVKrogu1_Omogoci | DIGITAL | IOD_SS1_disk | D3066 | [8 empty] | 0x05c015f0
SS1KlimaError1VisokPritiskVKrogu2_Omogoci | DIGITAL | IOD_SS1_disk | D3067 | [8 empty] | 0x05c01600
SS1KlimaError1IzlivVode_Omogoci | DIGITAL | IOD_SS1_disk | D3068 | [8 empty] | 0x05c01610
SS1KlimaError1TermZascInVisokPritiskKompr1_Omogoci | DIGITAL | IOD_SS1_disk | D3069 | [8 empty] | 0x05c01620
SS1KlimaError1VlazilecnaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3070 | [8 empty] | 0x05c01630
SS1KlimaError1TermZascInVisokPritiskKompr2_Omogoci | DIGITAL | IOD_SS1_disk | D3071 | [8 empty] | 0x05c01640
SS1KlimaError1NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS1_disk | D3072 | [8 empty] | 0x05c01650
SS1KlimaError1Kond1FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3073 | [8 empty] | 0x05c01660
SS1KlimaError1Kond2FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3074 | [8 empty] | 0x05c01670
SS1KlimaError1ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS1_disk | D3075 | [8 empty] | 0x05c01680
SS1KlimaError2AlarmKompresor1_Omogoci | DIGITAL | IOD_SS1_disk | D3076 | [8 empty] | 0x05c01690
SS1KlimaError2AlarmKompresor2_Omogoci | DIGITAL | IOD_SS1_disk | D3077 | [8 empty] | 0x05c016a0
SS1KlimaError2NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS1_disk | D3078 | [8 empty] | 0x05c016b0
SS1KlimaError2NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS1_disk | D3079 | [8 empty] | 0x05c016c0
SS1KlimaError2NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS1_disk | D3080 | [8 empty] | 0x05c016d0
SS1KlimaError2FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3081 | [8 empty] | 0x05c016e0
SS1KlimaError2ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS1_disk | D3082 | [8 empty] | 0x05c016f0
SS1KlimaError2ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS1_disk | D3083 | [8 empty] | 0x05c01700
SS1KlimaError2PozarniAlarm_Omogoci | DIGITAL | IOD_SS1_disk | D3084 | [8 empty] | 0x05c01710
SS1KlimaError2ZamasenFilter_Omogoci | DIGITAL | IOD_SS1_disk | D3085 | [8 empty] | 0x05c01720
SS1KlimaError2VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS1_disk | D3086 | [8 empty] | 0x05c01730
SS1KlimaError2NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS1_disk | D3087 | [8 empty] | 0x05c01740
SS1KlimaError2VisokaVlaznost_Omogoci | DIGITAL | IOD_SS1_disk | D3088 | [8 empty] | 0x05c01750
SS1KlimaError2NizkaVlaznost_Omogoci | DIGITAL | IOD_SS1_disk | D3089 | [8 empty] | 0x05c01760
SS1KlimaError2Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3090 | [8 empty] | 0x05c01770
SS1KlimaError2Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3091 | [8 empty] | 0x05c01780
SS1KlimaError2VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3092 | [8 empty] | 0x05c01790
SS1KlimaError2NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS1_disk | D3093 | [8 empty] | 0x05c017a0
SS1KlimaError2NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS1_disk | D3094 | [8 empty] | 0x05c017b0
SS1KlimaError2NapakaSenzorPritiska_Omogoci | DIGITAL | IOD_SS1_disk | D3095 | [8 empty] | 0x05c017c0
SS1KlimaError2VisokTokVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3096 | [8 empty] | 0x05c017d0
SS1KlimaError2NiVodeVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3097 | [8 empty] | 0x05c017e0
SS1KlimaError2NiTokaVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3098 | [8 empty] | 0x05c017f0
SS1KlimaError2VisokPritiskVKrogu1_Omogoci | DIGITAL | IOD_SS1_disk | D3099 | [8 empty] | 0x05c01800
SS1KlimaError2VisokPritiskVKrogu2_Omogoci | DIGITAL | IOD_SS1_disk | D3100 | [8 empty] | 0x05c01810
SS1KlimaError2IzlivVode_Omogoci | DIGITAL | IOD_SS1_disk | D3101 | [8 empty] | 0x05c01820
SS1KlimaError2TermZascInVisokPritiskKompr1_Omogoci | DIGITAL | IOD_SS1_disk | D3102 | [8 empty] | 0x05c01830
SS1KlimaError2VlazilecnaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3103 | [8 empty] | 0x05c01840
SS1KlimaError2TermZascInVisokPritiskKompr2_Omogoci | DIGITAL | IOD_SS1_disk | D3104 | [8 empty] | 0x05c01850
SS1KlimaError2NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS1_disk | D3105 | [8 empty] | 0x05c01860
SS1KlimaError2Kond1FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3106 | [8 empty] | 0x05c01870
SS1KlimaError2Kond2FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3107 | [8 empty] | 0x05c01880
SS1KlimaError2ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS1_disk | D3108 | [8 empty] | 0x05c01890
SS1KlimaError3AlarmKompresor1_Omogoci | DIGITAL | IOD_SS1_disk | D3109 | [8 empty] | 0x05c018a0
SS1KlimaError3AlarmKompresor2_Omogoci | DIGITAL | IOD_SS1_disk | D3110 | [8 empty] | 0x05c018b0
SS1KlimaError3NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS1_disk | D3111 | [8 empty] | 0x05c018c0
SS1KlimaError3NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS1_disk | D3112 | [8 empty] | 0x05c018d0
SS1KlimaError3NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS1_disk | D3113 | [8 empty] | 0x05c018e0
SS1KlimaError3FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3114 | [8 empty] | 0x05c018f0
SS1KlimaError3ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS1_disk | D3115 | [8 empty] | 0x05c01900
SS1KlimaError3ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS1_disk | D3116 | [8 empty] | 0x05c01910
SS1KlimaError3PozarniAlarm_Omogoci | DIGITAL | IOD_SS1_disk | D3117 | [8 empty] | 0x05c01920
SS1KlimaError3ZamasenFilter_Omogoci | DIGITAL | IOD_SS1_disk | D3118 | [8 empty] | 0x05c01930
SS1KlimaError3VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS1_disk | D3119 | [8 empty] | 0x05c01940
SS1KlimaError3NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS1_disk | D3120 | [8 empty] | 0x05c01950
SS1KlimaError3VisokaVlaznost_Omogoci | DIGITAL | IOD_SS1_disk | D3121 | [8 empty] | 0x05c01960
SS1KlimaError3NizkaVlaznost_Omogoci | DIGITAL | IOD_SS1_disk | D3122 | [8 empty] | 0x05c01970
SS1KlimaError3Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3123 | [8 empty] | 0x05c01980
SS1KlimaError3Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3124 | [8 empty] | 0x05c01990
SS1KlimaError3VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3125 | [8 empty] | 0x05c019a0
SS1KlimaError3NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS1_disk | D3126 | [8 empty] | 0x05c019b0
SS1KlimaError3NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS1_disk | D3127 | [8 empty] | 0x05c019c0
SS1KlimaError3NapakaSenzorPritiska_Omogoci | DIGITAL | IOD_SS1_disk | D3128 | [8 empty] | 0x05c019d0
SS1KlimaError3VisokTokVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3129 | [8 empty] | 0x05c019e0
SS1KlimaError3NiVodeVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3130 | [8 empty] | 0x05c019f0
SS1KlimaError3NiTokaVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3131 | [8 empty] | 0x05c01a00
SS1KlimaError3VisokPritiskVKrogu1_Omogoci | DIGITAL | IOD_SS1_disk | D3132 | [8 empty] | 0x05c01a10
SS1KlimaError3VisokPritiskVKrogu2_Omogoci | DIGITAL | IOD_SS1_disk | D3133 | [8 empty] | 0x05c01a20
SS1KlimaError3IzlivVode_Omogoci | DIGITAL | IOD_SS1_disk | D3134 | [8 empty] | 0x05c01a30
SS1KlimaError3TermZascInVisokPritiskKompr1_Omogoci | DIGITAL | IOD_SS1_disk | D3135 | [8 empty] | 0x05c01a40
SS1KlimaError3VlazilecnaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3136 | [8 empty] | 0x05c01a50
SS1KlimaError3TermZascInVisokPritiskKompr2_Omogoci | DIGITAL | IOD_SS1_disk | D3137 | [8 empty] | 0x05c01a60
SS1KlimaError3NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS1_disk | D3138 | [8 empty] | 0x05c01a70
SS1KlimaError3Kond1FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3139 | [8 empty] | 0x05c01a80
SS1KlimaError3Kond2FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3140 | [8 empty] | 0x05c01a90
SS1KlimaError3ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS1_disk | D3141 | [8 empty] | 0x05c01aa0
SS1PMMPhase1Current1_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3142 | [8 empty] | 0x05c01ab0
SS1PMMPhase1Current2_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3143 | [8 empty] | 0x05c01ac0
SS1PMMPhase1Current3_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3144 | [8 empty] | 0x05c01ad0
SS1PMMPhase1Current4_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3145 | [8 empty] | 0x05c01ae0
SS1PMMPhase1Current5_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3146 | [8 empty] | 0x05c01af0
SS1PMMPhase1Current6_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3147 | [8 empty] | 0x05c01b00
SS1PMMPhase1Current7_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3148 | [8 empty] | 0x05c01b10
SS1PMMPhase1Current8_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3149 | [8 empty] | 0x05c01b20
SS1PMMPhase1Current9_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3150 | [8 empty] | 0x05c01b30
SS1PMMPhase1Current10_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3151 | [8 empty] | 0x05c01b40
SS1PMMPhase1Current11_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3152 | [8 empty] | 0x05c01b50
SS1PMMPhase1Current12_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3153 | [8 empty] | 0x05c01b60
SS1PMMPhase1Current13_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3154 | [8 empty] | 0x05c01b70
SS1PMMPhase1Current14_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3155 | [8 empty] | 0x05c01b80
SS1PMMPhase1Current15_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3156 | [8 empty] | 0x05c01b90
SS1PMMPhase1Current16_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3157 | [8 empty] | 0x05c01ba0
SS1PMMPhase1Current17_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3158 | [8 empty] | 0x05c01bb0
SS1PMMPhase1Current18_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3159 | [8 empty] | 0x05c01bc0
SS1PMMPhase1Current19_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3160 | [8 empty] | 0x05c01bd0
SS1PMMPhase1Current20_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3161 | [8 empty] | 0x05c01be0
SS1PMMPhase1Current21_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3162 | [8 empty] | 0x05c01bf0
SS1PMMPhase1Current22_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3163 | [8 empty] | 0x05c01c00
SS1PMMPhase1Current23_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3164 | [8 empty] | 0x05c01c10
SS1PMMPhase1Current24_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3165 | [8 empty] | 0x05c01c20
SS1PMMPhase1Current25_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3166 | [8 empty] | 0x05c01c30
SS1PMMPhase1Current26_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3167 | [8 empty] | 0x05c01c40
SS1PMMPhase1Current27_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3168 | [8 empty] | 0x05c01c50
SS1PMMPhase1Current28_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3169 | [8 empty] | 0x05c01c60
SS1PMMPhase1Current29_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3170 | [8 empty] | 0x05c01c70
SS1PMMPhase1Current30_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3171 | [8 empty] | 0x05c01c80
SS1PMMPhase1Current31_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3172 | [8 empty] | 0x05c01c90
SS1PMMPhase1Current32_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3173 | [8 empty] | 0x05c01ca0
SS1PMMPhase1Current33_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3174 | [8 empty] | 0x05c01cb0
SS1PMMPhase1Current34_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3175 | [8 empty] | 0x05c01cc0
SS1PMMPhase1Current35_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3176 | [8 empty] | 0x05c01cd0
SS1PMMPhase1Current36_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3177 | [8 empty] | 0x05c01ce0
SS1PMMPhase1Current37_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3178 | [8 empty] | 0x05c01cf0
SS1PMMPhase1Current38_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3179 | [8 empty] | 0x05c01d00
SS1PMMPhase1Current39_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3180 | [8 empty] | 0x05c01d10
SS1PMMPhase1Current40_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3181 | [8 empty] | 0x05c01d20
SS1PMMPhase1Current41_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3182 | [8 empty] | 0x05c01d30
SS1PMMPhase1Current42_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3183 | [8 empty] | 0x05c01d40
SS1PMMPhase2Current1_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3184 | [8 empty] | 0x05c01d50
SS1PMMPhase2Current2_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3185 | [8 empty] | 0x05c01d60
SS1PMMPhase2Current3_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3186 | [8 empty] | 0x05c01d70
SS1PMMPhase2Current4_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3187 | [8 empty] | 0x05c01d80
SS1PMMPhase2Current5_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3188 | [8 empty] | 0x05c01d90
SS1PMMPhase2Current6_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3189 | [8 empty] | 0x05c01da0
SS1PMMPhase2Current7_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3190 | [8 empty] | 0x05c01db0
SS1PMMPhase2Current8_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3191 | [8 empty] | 0x05c01dc0
SS1PMMPhase2Current9_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3192 | [8 empty] | 0x05c01dd0
SS1PMMPhase2Current10_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3193 | [8 empty] | 0x05c01de0
SS1PMMPhase2Current11_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3194 | [8 empty] | 0x05c01df0
SS1PMMPhase2Current12_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3195 | [8 empty] | 0x05c01e00
SS1PMMPhase2Current13_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3196 | [8 empty] | 0x05c01e10
SS1PMMPhase2Current14_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3197 | [8 empty] | 0x05c01e20
SS1PMMPhase2Current15_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3198 | [8 empty] | 0x05c01e30
SS1PMMPhase2Current16_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3199 | [8 empty] | 0x05c01e40
SS1PMMPhase2Current17_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3200 | [8 empty] | 0x05c01e50
SS1PMMPhase2Current18_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3201 | [8 empty] | 0x05c01e60
SS1PMMPhase2Current19_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3202 | [8 empty] | 0x05c01e70
SS1PMMPhase2Current20_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3203 | [8 empty] | 0x05c01e80
SS1PMMPhase2Current21_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3204 | [8 empty] | 0x05c01e90
SS1PMMPhase2Current22_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3205 | [8 empty] | 0x05c01ea0
SS1PMMPhase2Current23_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3206 | [8 empty] | 0x05c01eb0
SS1PMMPhase2Current24_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3207 | [8 empty] | 0x05c01ec0
SS1PMMPhase2Current25_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3208 | [8 empty] | 0x05c01ed0
SS1PMMPhase2Current26_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3209 | [8 empty] | 0x05c01ee0
SS1PMMPhase2Current27_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3210 | [8 empty] | 0x05c01ef0
SS1PMMPhase2Current28_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3211 | [8 empty] | 0x05c01f00
SS1PMMPhase2Current29_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3212 | [8 empty] | 0x05c01f10
SS1PMMPhase2Current30_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3213 | [8 empty] | 0x05c01f20
SS1PMMPhase2Current31_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3214 | [8 empty] | 0x05c01f30
SS1PMMPhase2Current32_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3215 | [8 empty] | 0x05c01f40
SS1PMMPhase2Current33_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3216 | [8 empty] | 0x05c01f50
SS1PMMPhase2Current34_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3217 | [8 empty] | 0x05c01f60
SS1PMMPhase2Current35_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3218 | [8 empty] | 0x05c01f70
SS1PMMPhase2Current36_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3219 | [8 empty] | 0x05c01f80
SS1PMMPhase2Current37_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3220 | [8 empty] | 0x05c01f90
SS1PMMPhase2Current38_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3221 | [8 empty] | 0x05c01fa0
SS1PMMPhase2Current39_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3222 | [8 empty] | 0x05c01fb0
SS1PMMPhase2Current40_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3223 | [8 empty] | 0x05c01fc0
SS1PMMPhase2Current41_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3224 | [8 empty] | 0x05c01fd0
SS1PMMPhase2Current42_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3225 | [8 empty] | 0x05c01fe0
SS1PMMPhase3Current1_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3226 | [8 empty] | 0x05c01ff0
SS1PMMPhase3Current2_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3227 | [8 empty] | 0x05c02000
SS1PMMPhase3Current3_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3228 | [8 empty] | 0x05c02010
SS1PMMPhase3Current4_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3229 | [8 empty] | 0x05c02020
SS1PMMPhase3Current5_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3230 | [8 empty] | 0x05c02030
SS1PMMPhase3Current6_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3231 | [8 empty] | 0x05c02040
SS1PMMPhase3Current7_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3232 | [8 empty] | 0x05c02050
SS1PMMPhase3Current8_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3233 | [8 empty] | 0x05c02060
SS1PMMPhase3Current9_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3234 | [8 empty] | 0x05c02070
SS1PMMPhase3Current10_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3235 | [8 empty] | 0x05c02080
SS1PMMPhase3Current11_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3236 | [8 empty] | 0x05c02090
SS1PMMPhase3Current12_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3237 | [8 empty] | 0x05c020a0
SS1PMMPhase3Current13_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3238 | [8 empty] | 0x05c020b0
SS1PMMPhase3Current14_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3239 | [8 empty] | 0x05c020c0
SS1PMMPhase3Current15_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3240 | [8 empty] | 0x05c020d0
SS1PMMPhase3Current16_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3241 | [8 empty] | 0x05c020e0
SS1PMMPhase3Current17_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3242 | [8 empty] | 0x05c020f0
SS1PMMPhase3Current18_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3243 | [8 empty] | 0x05c02100
SS1PMMPhase3Current19_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3244 | [8 empty] | 0x05c02110
SS1PMMPhase3Current20_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3245 | [8 empty] | 0x05c02120
SS1PMMPhase3Current21_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3246 | [8 empty] | 0x05c02130
SS1PMMPhase3Current22_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3247 | [8 empty] | 0x05c02140
SS1PMMPhase3Current23_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3248 | [8 empty] | 0x05c02150
SS1PMMPhase3Current24_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3249 | [8 empty] | 0x05c02160
SS1PMMPhase3Current25_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3250 | [8 empty] | 0x05c02170
SS1PMMPhase3Current26_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3251 | [8 empty] | 0x05c02180
SS1PMMPhase3Current27_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3252 | [8 empty] | 0x05c02190
SS1PMMPhase3Current28_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3253 | [8 empty] | 0x05c021a0
SS1PMMPhase3Current29_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3254 | [8 empty] | 0x05c021b0
SS1PMMPhase3Current30_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3255 | [8 empty] | 0x05c021c0
SS1PMMPhase3Current31_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3256 | [8 empty] | 0x05c021d0
SS1PMMPhase3Current32_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3257 | [8 empty] | 0x05c021e0
SS1PMMPhase3Current33_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3258 | [8 empty] | 0x05c021f0
SS1PMMPhase3Current34_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3259 | [8 empty] | 0x05c02200
SS1PMMPhase3Current35_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3260 | [8 empty] | 0x05c02210
SS1PMMPhase3Current36_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3261 | [8 empty] | 0x05c02220
SS1PMMPhase3Current37_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3262 | [8 empty] | 0x05c02230
SS1PMMPhase3Current38_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3263 | [8 empty] | 0x05c02240
SS1PMMPhase3Current39_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3264 | [8 empty] | 0x05c02250
SS1PMMPhase3Current40_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3265 | [8 empty] | 0x05c02260
SS1PMMPhase3Current41_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3266 | [8 empty] | 0x05c02270
SS1PMMPhase3Current42_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3267 | [8 empty] | 0x05c02280
SS1PMMPhase1Current1_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3268 | [8 empty] | 0x05c02290
SS1PMMPhase1Current2_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3269 | [8 empty] | 0x05c022a0
SS1PMMPhase1Current3_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3270 | [8 empty] | 0x05c022b0
SS1PMMPhase1Current4_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3271 | [8 empty] | 0x05c022c0
SS1PMMPhase1Current5_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3272 | [8 empty] | 0x05c022d0
SS1PMMPhase1Current6_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3273 | [8 empty] | 0x05c022e0
SS1PMMPhase1Current7_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3274 | [8 empty] | 0x05c022f0
SS1PMMPhase1Current8_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3275 | [8 empty] | 0x05c02300
SS1PMMPhase1Current9_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3276 | [8 empty] | 0x05c02310
SS1PMMPhase1Current10_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3277 | [8 empty] | 0x05c02320
SS1PMMPhase1Current11_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3278 | [8 empty] | 0x05c02330
SS1PMMPhase1Current12_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3279 | [8 empty] | 0x05c02340
SS1PMMPhase1Current13_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3280 | [8 empty] | 0x05c02350
SS1PMMPhase1Current14_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3281 | [8 empty] | 0x05c02360
SS1PMMPhase1Current15_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3282 | [8 empty] | 0x05c02370
SS1PMMPhase1Current16_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3283 | [8 empty] | 0x05c02380
SS1PMMPhase1Current17_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3284 | [8 empty] | 0x05c02390
SS1PMMPhase1Current18_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3285 | [8 empty] | 0x05c023a0
SS1PMMPhase1Current19_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3286 | [8 empty] | 0x05c023b0
SS1PMMPhase1Current20_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3287 | [8 empty] | 0x05c023c0
SS1PMMPhase1Current21_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3288 | [8 empty] | 0x05c023d0
SS1PMMPhase1Current22_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3289 | [8 empty] | 0x05c023e0
SS1PMMPhase1Current23_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3290 | [8 empty] | 0x05c023f0
SS1PMMPhase1Current24_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3291 | [8 empty] | 0x05c02400
SS1PMMPhase1Current25_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3292 | [8 empty] | 0x05c02410
SS1PMMPhase1Current26_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3293 | [8 empty] | 0x05c02420
SS1PMMPhase1Current27_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3294 | [8 empty] | 0x05c02430
SS1PMMPhase1Current28_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3295 | [8 empty] | 0x05c02440
SS1PMMPhase1Current29_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3296 | [8 empty] | 0x05c02450
SS1PMMPhase1Current30_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3297 | [8 empty] | 0x05c02460
SS1PMMPhase1Current31_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3298 | [8 empty] | 0x05c02470
SS1PMMPhase1Current32_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3299 | [8 empty] | 0x05c02480
SS1PMMPhase1Current33_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3300 | [8 empty] | 0x05c02490
SS1PMMPhase1Current34_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3301 | [8 empty] | 0x05c024a0
SS1PMMPhase1Current35_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3302 | [8 empty] | 0x05c024b0
SS1PMMPhase1Current36_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3303 | [8 empty] | 0x05c024c0
SS1PMMPhase1Current37_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3304 | [8 empty] | 0x05c024d0
SS1PMMPhase1Current38_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3305 | [8 empty] | 0x05c024e0
SS1PMMPhase1Current39_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3306 | [8 empty] | 0x05c024f0
SS1PMMPhase1Current40_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3307 | [8 empty] | 0x05c02500
SS1PMMPhase1Current41_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3308 | [8 empty] | 0x05c02510
SS1PMMPhase1Current42_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3309 | [8 empty] | 0x05c02520
SS1PMMPhase2Current1_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3310 | [8 empty] | 0x05c02530
SS1PMMPhase2Current2_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3311 | [8 empty] | 0x05c02540
SS1PMMPhase2Current3_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3312 | [8 empty] | 0x05c02550
SS1PMMPhase2Current4_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3313 | [8 empty] | 0x05c02560
SS1PMMPhase2Current5_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3314 | [8 empty] | 0x05c02570
SS1PMMPhase2Current6_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3315 | [8 empty] | 0x05c02580
SS1PMMPhase2Current7_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3316 | [8 empty] | 0x05c02590
SS1PMMPhase2Current8_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3317 | [8 empty] | 0x05c025a0
SS1PMMPhase2Current9_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3318 | [8 empty] | 0x05c025b0
SS1PMMPhase2Current10_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3319 | [8 empty] | 0x05c025c0
SS1PMMPhase2Current11_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3320 | [8 empty] | 0x05c025d0
SS1PMMPhase2Current12_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3321 | [8 empty] | 0x05c025e0
SS1PMMPhase2Current13_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3322 | [8 empty] | 0x05c025f0
SS1PMMPhase2Current14_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3323 | [8 empty] | 0x05c02600
SS1PMMPhase2Current15_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3324 | [8 empty] | 0x05c02610
SS1PMMPhase2Current16_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3325 | [8 empty] | 0x05c02620
SS1PMMPhase2Current17_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3326 | [8 empty] | 0x05c02630
SS1PMMPhase2Current18_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3327 | [8 empty] | 0x05c02640
SS1PMMPhase2Current19_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3328 | [8 empty] | 0x05c02650
SS1PMMPhase2Current20_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3329 | [8 empty] | 0x05c02660
SS1PMMPhase2Current21_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3330 | [8 empty] | 0x05c02670
SS1PMMPhase2Current22_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3331 | [8 empty] | 0x05c02680
SS1PMMPhase2Current23_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3332 | [8 empty] | 0x05c02690
SS1PMMPhase2Current24_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3333 | [8 empty] | 0x05c026a0
SS1PMMPhase2Current25_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3334 | [8 empty] | 0x05c026b0
SS1PMMPhase2Current26_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3335 | [8 empty] | 0x05c026c0
SS1PMMPhase2Current27_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3336 | [8 empty] | 0x05c026d0
SS1PMMPhase2Current28_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3337 | [8 empty] | 0x05c026e0
SS1PMMPhase2Current29_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3338 | [8 empty] | 0x05c026f0
SS1PMMPhase2Current30_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3339 | [8 empty] | 0x05c02700
SS1PMMPhase2Current31_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3340 | [8 empty] | 0x05c02710
SS1PMMPhase2Current32_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3341 | [8 empty] | 0x05c02720
SS1PMMPhase2Current33_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3342 | [8 empty] | 0x05c02730
SS1PMMPhase2Current34_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3343 | [8 empty] | 0x05c02740
SS1PMMPhase2Current35_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3344 | [8 empty] | 0x05c02750
SS1PMMPhase2Current36_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3345 | [8 empty] | 0x05c02760
SS1PMMPhase2Current37_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3346 | [8 empty] | 0x05c02770
SS1PMMPhase2Current38_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3347 | [8 empty] | 0x05c02780
SS1PMMPhase2Current39_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3348 | [8 empty] | 0x05c02790
SS1PMMPhase2Current40_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3349 | [8 empty] | 0x05c027a0
SS1PMMPhase2Current41_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3350 | [8 empty] | 0x05c027b0
SS1PMMPhase2Current42_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3351 | [8 empty] | 0x05c027c0
SS1PMMPhase3Current1_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3352 | [8 empty] | 0x05c027d0
SS1PMMPhase3Current2_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3353 | [8 empty] | 0x05c027e0
SS1PMMPhase3Current3_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3354 | [8 empty] | 0x05c027f0
SS1PMMPhase3Current4_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3355 | [8 empty] | 0x05c02800
SS1PMMPhase3Current5_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3356 | [8 empty] | 0x05c02810
SS1PMMPhase3Current6_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3357 | [8 empty] | 0x05c02820
SS1PMMPhase3Current7_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3358 | [8 empty] | 0x05c02830
SS1PMMPhase3Current8_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3359 | [8 empty] | 0x05c02840
SS1PMMPhase3Current9_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3360 | [8 empty] | 0x05c02850
SS1PMMPhase3Current10_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3361 | [8 empty] | 0x05c02860
SS1PMMPhase3Current11_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3362 | [8 empty] | 0x05c02870
SS1PMMPhase3Current12_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3363 | [8 empty] | 0x05c02880
SS1PMMPhase3Current13_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3364 | [8 empty] | 0x05c02890
SS1PMMPhase3Current14_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3365 | [8 empty] | 0x05c028a0
SS1PMMPhase3Current15_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3366 | [8 empty] | 0x05c028b0
SS1PMMPhase3Current16_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3367 | [8 empty] | 0x05c028c0
SS1PMMPhase3Current17_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3368 | [8 empty] | 0x05c028d0
SS1PMMPhase3Current18_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3369 | [8 empty] | 0x05c028e0
SS1PMMPhase3Current19_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3370 | [8 empty] | 0x05c028f0
SS1PMMPhase3Current20_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3371 | [8 empty] | 0x05c02900
SS1PMMPhase3Current21_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3372 | [8 empty] | 0x05c02910
SS1PMMPhase3Current22_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3373 | [8 empty] | 0x05c02920
SS1PMMPhase3Current23_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3374 | [8 empty] | 0x05c02930
SS1PMMPhase3Current24_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3375 | [8 empty] | 0x05c02940
SS1PMMPhase3Current25_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3376 | [8 empty] | 0x05c02950
SS1PMMPhase3Current26_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3377 | [8 empty] | 0x05c02960
SS1PMMPhase3Current27_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3378 | [8 empty] | 0x05c02970
SS1PMMPhase3Current28_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3379 | [8 empty] | 0x05c02980
SS1PMMPhase3Current29_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3380 | [8 empty] | 0x05c02990
SS1PMMPhase3Current30_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3381 | [8 empty] | 0x05c029a0
SS1PMMPhase3Current31_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3382 | [8 empty] | 0x05c029b0
SS1PMMPhase3Current32_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3383 | [8 empty] | 0x05c029c0
SS1PMMPhase3Current33_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3384 | [8 empty] | 0x05c029d0
SS1PMMPhase3Current34_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3385 | [8 empty] | 0x05c029e0
SS1PMMPhase3Current35_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3386 | [8 empty] | 0x05c029f0
SS1PMMPhase3Current36_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3387 | [8 empty] | 0x05c02a00
SS1PMMPhase3Current37_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3388 | [8 empty] | 0x05c02a10
SS1PMMPhase3Current38_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3389 | [8 empty] | 0x05c02a20
SS1PMMPhase3Current39_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3390 | [8 empty] | 0x05c02a30
SS1PMMPhase3Current40_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3391 | [8 empty] | 0x05c02a40
SS1PMMPhase3Current41_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3392 | [8 empty] | 0x05c02a50
SS1PMMPhase3Current42_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3393 | [8 empty] | 0x05c02a60
SS1AlarmTempTIA123Previsoka_Omogoci | DIGITAL | IOD_SS1_disk | D3394 | [8 empty] | 0x05c02a70
SS1AlarmTempTIA4Previsoka_Omogoci | DIGITAL | IOD_SS1_disk | D3395 | [8 empty] | 0x05c02a80
SS1AlarmTempTIA5Previsoka_Omogoci | DIGITAL | IOD_SS1_disk | D3396 | [8 empty] | 0x05c02a90
SS1PMMOverCurrentBetw1_VirB | DIGITAL | IOD_SS1_disk | D3397 | [8 empty] | 0x05c02aa0
SS1PMMOverCurrentBetw2_VirB | DIGITAL | IOD_SS1_disk | D3398 | [8 empty] | 0x05c02ab0
SS1PMMOverCurrentBetw3_VirB | DIGITAL | IOD_SS1_disk | D3399 | [8 empty] | 0x05c02ac0
SS1PMMOverCurrentBetw1_VirA | DIGITAL | IOD_SS1_disk | D3400 | [8 empty] | 0x05c02ad0
SS1PMMOverCurrentBetw2_VirA | DIGITAL | IOD_SS1_disk | D3401 | [8 empty] | 0x05c02ae0
SS1PMMOverCurrentBetw3_VirA | DIGITAL | IOD_SS1_disk | D3402 | [8 empty] | 0x05c02af0
SS1PMMOverCurrentOver1_VirB | DIGITAL | IOD_SS1_disk | D3403 | [8 empty] | 0x05c02b00
SS1PMMOverCurrentOver2_VirB | DIGITAL | IOD_SS1_disk | D3404 | [8 empty] | 0x05c02b10
SS1PMMOverCurrentOver3_VirB | DIGITAL | IOD_SS1_disk | D3405 | [8 empty] | 0x05c02b20
SS1PMMOverCurrentOver1_VirA | DIGITAL | IOD_SS1_disk | D3406 | [8 empty] | 0x05c02b30
SS1PMMOverCurrentOver2_VirA | DIGITAL | IOD_SS1_disk | D3407 | [8 empty] | 0x05c02b40
SS1PMMOverCurrentOver3_VirA | DIGITAL | IOD_SS1_disk | D3408 | [8 empty] | 0x05c02b50
SS1PMMOverCurrentBetw1_VirB_1_2 | DIGITAL | IOD_SS1_disk | D3409 | [8 empty] | 0x05c02b60
SS1PMMOverCurrentBetw1_VirB_2_2 | DIGITAL | IOD_SS1_disk | D3410 | [8 empty] | 0x05c02b70
SS1PMMOverCurrentBetw1_VirA_1_2 | DIGITAL | IOD_SS1_disk | D3411 | [8 empty] | 0x05c02b80
SS1PMMOverCurrentBetw1_VirA_2_2 | DIGITAL | IOD_SS1_disk | D3412 | [8 empty] | 0x05c02b90
SS1PMMOverCurrentBetw2_VirB_1_2 | DIGITAL | IOD_SS1_disk | D3413 | [8 empty] | 0x05c02ba0
SS1PMMOverCurrentBetw2_VirB_2_2 | DIGITAL | IOD_SS1_disk | D3414 | [8 empty] | 0x05c02bb0
SS1PMMOverCurrentBetw2_VirA_1_2 | DIGITAL | IOD_SS1_disk | D3415 | [8 empty] | 0x05c02bc0
SS1PMMOverCurrentBetw2_VirA_2_2 | DIGITAL | IOD_SS1_disk | D3416 | [8 empty] | 0x05c02bd0
SS1PMMOverCurrentBetw3_VirB_1_2 | DIGITAL | IOD_SS1_disk | D3417 | [8 empty] | 0x05c02be0
SS1PMMOverCurrentBetw3_VirB_2_2 | DIGITAL | IOD_SS1_disk | D3418 | [8 empty] | 0x05c02bf0
SS1PMMOverCurrentBetw3_VirA_1_2 | DIGITAL | IOD_SS1_disk | D3419 | [8 empty] | 0x05c02c00
SS1PMMOverCurrentBetw3_VirA_2_2 | DIGITAL | IOD_SS1_disk | D3420 | [8 empty] | 0x05c02c10
SS1PMMOverCurrentOver1_VirB_1_2 | DIGITAL | IOD_SS1_disk | D3421 | [8 empty] | 0x05c02c20
SS1PMMOverCurrentOver1_VirB_2_2 | DIGITAL | IOD_SS1_disk | D3422 | [8 empty] | 0x05c02c30
SS1PMMOverCurrentOver1_VirA_1_2 | DIGITAL | IOD_SS1_disk | D3423 | [8 empty] | 0x05c02c40
SS1PMMOverCurrentOver1_VirA_2_2 | DIGITAL | IOD_SS1_disk | D3424 | [8 empty] | 0x05c02c50
SS1PMMOverCurrentOver2_VirB_1_2 | DIGITAL | IOD_SS1_disk | D3425 | [8 empty] | 0x05c02c60
SS1PMMOverCurrentOver2_VirB_2_2 | DIGITAL | IOD_SS1_disk | D3426 | [8 empty] | 0x05c02c70
SS1PMMOverCurrentOver2_VirA_1_2 | DIGITAL | IOD_SS1_disk | D3427 | [8 empty] | 0x05c02c80
SS1PMMOverCurrentOver2_VirA_2_2 | DIGITAL | IOD_SS1_disk | D3428 | [8 empty] | 0x05c02c90
SS1PMMOverCurrentOver3_VirB_1_2 | DIGITAL | IOD_SS1_disk | D3429 | [8 empty] | 0x05c02ca0
SS1PMMOverCurrentOver3_VirB_2_2 | DIGITAL | IOD_SS1_disk | D3430 | [8 empty] | 0x05c02cb0
SS1PMMOverCurrentOver3_VirA_1_2 | DIGITAL | IOD_SS1_disk | D3431 | [8 empty] | 0x05c02cc0
SS1PMMOverCurrentOver3_VirA_2_2 | DIGITAL | IOD_SS1_disk | D3432 | [8 empty] | 0x05c02cd0
SS1AlarmSinhronizacijaNOK_Omogoci | DIGITAL | IOD_SS1_disk | D3433 | [8 empty] | 0x05c02ce0
SS1VsotaF1_1_16B | INT | IOD_SS1_disk | I3 | [8 empty] | 0x05c02cf0
SS1VsotaF1_17_32B | INT | IOD_SS1_disk | I4 | [8 empty] | 0x05c02cf1
SS1VsotaF1_33_42B | INT | IOD_SS1_disk | I5 | [8 empty] | 0x05c02cf2
SS1VsotaF1_1_16A | INT | IOD_SS1_disk | I6 | [8 empty] | 0x05c02cf3
SS1VsotaF1_17_32A | INT | IOD_SS1_disk | I7 | [8 empty] | 0x05c02cf4
SS1VsotaF1_33_42A | INT | IOD_SS1_disk | I8 | [8 empty] | 0x05c02cf5
SS1VsotaF2_1_16B | INT | IOD_SS1_disk | I9 | [8 empty] | 0x05c02cf6
SS1VsotaF2_17_32B | INT | IOD_SS1_disk | I10 | [8 empty] | 0x05c02cf7
SS1VsotaF2_33_42B | INT | IOD_SS1_disk | I11 | [8 empty] | 0x05c02cf8
SS1VsotaF2_1_16A | INT | IOD_SS1_disk | I12 | [8 empty] | 0x05c02cf9
SS1VsotaF2_17_32A | INT | IOD_SS1_disk | I13 | [8 empty] | 0x05c02cfa
SS1VsotaF2_33_42A | INT | IOD_SS1_disk | I14 | [8 empty] | 0x05c02cfb
SS1VsotaF3_1_16B | INT | IOD_SS1_disk | I15 | [8 empty] | 0x05c02cfc
SS1VsotaF3_17_32B | INT | IOD_SS1_disk | I16 | [8 empty] | 0x05c02cfd
SS1VsotaF3_33_42B | INT | IOD_SS1_disk | I17 | [8 empty] | 0x05c02cfe
SS1VsotaF3_1_16A | INT | IOD_SS1_disk | I18 | [8 empty] | 0x05c02cff
SS1VsotaF3_17_32A | INT | IOD_SS1_disk | I19 | [8 empty] | 0x05c02d00
SS1VsotaF3_33_42A | INT | IOD_SS1_disk | I20 | [8 empty] | 0x05c02d01
SS1ComSCADA_stevec2 | INT | IOD_SS1_mem | I1 | [8 empty] | 0x05c02d02
SS1ComSCADA_stevec1 | INT | IOD_SS1_mem | I2 | [8 empty] | 0x05c02d03
SS1AktualniSetPointTemp | REAL | IOD_SS1 | SS1:.AktualniSetPointTemp | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c02d04
SS1AktualniSetPointVlaga | REAL | IOD_SS1 | SS1:.AktualniSetPointVlaga | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c02d05
SS1AlarmKlimat1_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmKlimat1_Napaka | [6 empty] | 6157 | 0 | 0x05c02d10
SS1AlarmKlimat2_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmKlimat2_Napaka | [6 empty] | 6157 | 0 | 0x05c02d20
SS1AlarmKlimat3_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmKlimat3_Napaka | [6 empty] | 6157 | 0 | 0x05c02d30
SS1AlarmLAH1_RazlitjeVode | DIGITAL | IOD_SS1 | SS1:.AlarmLAH1_RazlitjeVode | [6 empty] | 6157 | 0 | 0x05c02d40
SS1AlarmLAH2_RazlitjeVode | DIGITAL | IOD_SS1 | SS1:.AlarmLAH2_RazlitjeVode | [6 empty] | 6157 | 0 | 0x05c02d50
SS1AlarmSinhronizacijaNOK | DIGITAL | IOD_SS1 | SS1:.AlarmSinhronizacijaNOK | [6 empty] | 6157 | 0 | 0x05c02d60
SS1AlarmSP1_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmSP1_Napaka | [6 empty] | 6157 | 0 | 0x05c02d70
SS1AlarmSP2_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmSP2_Napaka | [6 empty] | 6157 | 0 | 0x05c02d80
SS1AlarmSP3_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmSP3_Napaka | [6 empty] | 6157 | 0 | 0x05c02d90
SS1AlarmSP4_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmSP4_Napaka | [6 empty] | 6157 | 0 | 0x05c02da0
SS1AlarmSP5_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmSP5_Napaka | [6 empty] | 6157 | 0 | 0x05c02db0
SS1AlarmTempTIA123Previsoka | DIGITAL | IOD_SS1 | SS1:.AlarmTempTIA123Previsoka | [6 empty] | 6157 | 0 | 0x05c02dc0
SS1AlarmTempTIA4Previsoka | DIGITAL | IOD_SS1 | SS1:.AlarmTempTIA4Previsoka | [6 empty] | 6157 | 0 | 0x05c02dd0
SS1AlarmTempTIA5Previsoka | DIGITAL | IOD_SS1 | SS1:.AlarmTempTIA5Previsoka | [6 empty] | 6157 | 0 | 0x05c02de0
SS1AlarmTSTempPrevisoka | DIGITAL | IOD_SS1 | SS1:.AlarmTSTempPrevisoka | [6 empty] | 6157 | 0 | 0x05c02df0
SS1AlarmUPSKrmOmara_Alarm | DIGITAL | IOD_SS1 | SS1:.AlarmUPSKrmOmara_Alarm | [6 empty] | 6157 | 0 | 0x05c02e00
SS1ComSCADA | DIGITAL | IOD_SS1 | SS1:.ComSCADA | [6 empty] | 6157 | 0 | 0x05c02e10
SS1ComSCADA1 | DIGITAL | IOD_SS1 | SS1:.ComSCADA1 | [6 empty] | 6157 | 0 | 0x05c02e20
SS1DatumCasDan | BYTE | IOD_SS1 | SS1:.DatumCas.Dan | [6 empty] | 6157 | 0 | 0x05c02e30
SS1DatumCasLeto | BYTE | IOD_SS1 | SS1:.DatumCas.Leto | [6 empty] | 6157 | 0 | 0x05c02e31
SS1DatumCasLeto2 | INT | IOD_SS1 | SS1:.DatumCas.Leto2 | [6 empty] | 6157 | 0 | 0x05c02e32
SS1DatumCasMesec | BYTE | IOD_SS1 | SS1:.DatumCas.Mesec | [6 empty] | 6157 | 0 | 0x05c02e33
SS1DatumCasMinuta | BYTE | IOD_SS1 | SS1:.DatumCas.Minuta | [6 empty] | 6157 | 0 | 0x05c02e34
SS1DatumCasSekunda | BYTE | IOD_SS1 | SS1:.DatumCas.Sekunda | [6 empty] | 6157 | 0 | 0x05c02e35
SS1DatumCasUra | BYTE | IOD_SS1 | SS1:.DatumCas.Ura | [6 empty] | 6157 | 0 | 0x05c02e36
SS1ErrComKlima1 | DIGITAL | IOD_SS1 | SS1:.ErrComKlima[1] | [6 empty] | 6157 | 0 | 0x05c02e40
SS1ErrComKlima2 | DIGITAL | IOD_SS1 | SS1:.ErrComKlima[2] | [6 empty] | 6157 | 0 | 0x05c02e50
SS1ErrComKlima3 | DIGITAL | IOD_SS1 | SS1:.ErrComKlima[3] | [6 empty] | 6157 | 0 | 0x05c02e60
SS1ErrCommScada | DIGITAL | IOD_SS1 | SS1:.ErrCommScada | [6 empty] | 6157 | 0 | 0x05c02e70
SS1ErrComPanelPLC | DIGITAL | IOD_SS1 | SS1:.ErrComPanelPLC | [6 empty] | 6157 | 0 | 0x05c02e80
SS1ErrComPMM | DIGITAL | IOD_SS1 | SS1:.ErrComPMM | [6 empty] | 6157 | 0 | 0x05c02e90
SS1ErrComPort2 | DIGITAL | IOD_SS1 | SS1:.ErrComPort2 | [6 empty] | 6157 | 0 | 0x05c02ea0
SS1Klima1_Onemogocena | DIGITAL | IOD_SS1 | SS1:.Klima1_Onemogocena | [6 empty] | 6157 | 0 | 0x05c02eb0
SS1Klima2_Onemogocena | DIGITAL | IOD_SS1 | SS1:.Klima2_Onemogocena | [6 empty] | 6157 | 0 | 0x05c02ec0
SS1Klima3_Onemogocena | DIGITAL | IOD_SS1 | SS1:.Klima3_Onemogocena | [6 empty] | 6157 | 0 | 0x05c02ed0
SS1Klima1IzhodniVentilator | DIGITAL | IOD_SS1 | SS1:.Klima[1].IzhodniVentilator | [6 empty] | 6157 | 0 | 0x05c02ee0
SS1Klima1Kompresor1 | DIGITAL | IOD_SS1 | SS1:.Klima[1].Kompresor1 | [6 empty] | 6157 | 0 | 0x05c02ef0
SS1Klima1Kompresor2 | DIGITAL | IOD_SS1 | SS1:.Klima[1].Kompresor2 | [6 empty] | 6157 | 0 | 0x05c02f00
SS1Klima1NastMaxTemp | REAL | IOD_SS1 | SS1:.Klima[1].NastMaxTemp | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c02f10
SS1Klima1NastMaxVlaznost | REAL | IOD_SS1 | SS1:.Klima[1].NastMaxVlaznost | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c02f11
SS1Klima1NastMinTemp | REAL | IOD_SS1 | SS1:.Klima[1].NastMinTemp | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c02f12
SS1Klima1NastMinVlaznost | REAL | IOD_SS1 | SS1:.Klima[1].NastMinVlaznost | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c02f13
SS1Klima1NastTempProstora | REAL | IOD_SS1 | SS1:.Klima[1].NastTempProstora | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c02f14
SS1Klima1NastVlaznost | REAL | IOD_SS1 | SS1:.Klima[1].NastVlaznost | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c02f15
SS1Klima1Pritisk | REAL | IOD_SS1 | SS1:.Klima[1].Pritisk | 0 | 5 | 0 | 5 | bar | ##.# | 6157 | 0 | 0x05c02f16
SS1Klima1Razvlazevanje | DIGITAL | IOD_SS1 | SS1:.Klima[1].Razvlazevanje | [6 empty] | 6157 | 0 | 0x05c02f20
SS1Klima1TemperaturaProstora | REAL | IOD_SS1 | SS1:.Klima[1].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c02f30
SS1Klima1VentilGretjeOdpiranje | DIGITAL | IOD_SS1 | SS1:.Klima[1].VentilGretjeOdpiranje | [6 empty] | 6157 | 0 | 0x05c02f40
SS1Klima1VentilGretjeZapiranje | DIGITAL | IOD_SS1 | SS1:.Klima[1].VentilGretjeZapiranje | [6 empty] | 6157 | 0 | 0x05c02f50
SS1Klima1Vlazenje | DIGITAL | IOD_SS1 | SS1:.Klima[1].Vlazenje | [6 empty] | 6157 | 0 | 0x05c02f60
SS1Klima1Vlazilec_Stanja | BYTE | IOD_SS1 | SS1:.Klima[1].Vlazilec_Stanja | [6 empty] | 6157 | 0 | 0x05c02f70
SS1Klima1VlaznostProstora | REAL | IOD_SS1 | SS1:.Klima[1].VlaznostProstora | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c02f71
SS1Klima2IzhodniVentilator | DIGITAL | IOD_SS1 | SS1:.Klima[2].IzhodniVentilator | [6 empty] | 6157 | 0 | 0x05c02f80
SS1Klima2Kompresor1 | DIGITAL | IOD_SS1 | SS1:.Klima[2].Kompresor1 | [6 empty] | 6157 | 0 | 0x05c02f90
SS1Klima2Kompresor2 | DIGITAL | IOD_SS1 | SS1:.Klima[2].Kompresor2 | [6 empty] | 6157 | 0 | 0x05c02fa0
SS1Klima2NastMaxTemp | REAL | IOD_SS1 | SS1:.Klima[2].NastMaxTemp | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c02fb0
SS1Klima2NastMaxVlaznost | REAL | IOD_SS1 | SS1:.Klima[2].NastMaxVlaznost | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c02fb1
SS1Klima2NastMinTemp | REAL | IOD_SS1 | SS1:.Klima[2].NastMinTemp | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c02fb2
SS1Klima2NastMinVlaznost | REAL | IOD_SS1 | SS1:.Klima[2].NastMinVlaznost | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c02fb3
SS1Klima2NastTempProstora | REAL | IOD_SS1 | SS1:.Klima[2].NastTempProstora | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c02fb4
SS1Klima2NastVlaznost | REAL | IOD_SS1 | SS1:.Klima[2].NastVlaznost | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c02fb5
SS1Klima2Pritisk | REAL | IOD_SS1 | SS1:.Klima[2].Pritisk | 0 | 5 | 0 | 5 | bar | ##.# | 6157 | 0 | 0x05c02fb6
SS1Klima2Razvlazevanje | DIGITAL | IOD_SS1 | SS1:.Klima[2].Razvlazevanje | [6 empty] | 6157 | 0 | 0x05c02fc0
SS1Klima2TemperaturaProstora | REAL | IOD_SS1 | SS1:.Klima[2].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c02fd0
SS1Klima2VentilGretjeOdpiranje | DIGITAL | IOD_SS1 | SS1:.Klima[2].VentilGretjeOdpiranje | [6 empty] | 6157 | 0 | 0x05c02fe0
SS1Klima2VentilGretjeZapiranje | DIGITAL | IOD_SS1 | SS1:.Klima[2].VentilGretjeZapiranje | [6 empty] | 6157 | 0 | 0x05c02ff0
SS1Klima2Vlazenje | DIGITAL | IOD_SS1 | SS1:.Klima[2].Vlazenje | [6 empty] | 6157 | 0 | 0x05c03000
SS1Klima2Vlazilec_Stanja | BYTE | IOD_SS1 | SS1:.Klima[2].Vlazilec_Stanja | [6 empty] | 6157 | 0 | 0x05c03010
SS1Klima2VlaznostProstora | REAL | IOD_SS1 | SS1:.Klima[2].VlaznostProstora | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c03011
SS1Klima3IzhodniVentilator | DIGITAL | IOD_SS1 | SS1:.Klima[3].IzhodniVentilator | [6 empty] | 6157 | 0 | 0x05c03020
SS1Klima3Kompresor1 | DIGITAL | IOD_SS1 | SS1:.Klima[3].Kompresor1 | [6 empty] | 6157 | 0 | 0x05c03030
SS1Klima3Kompresor2 | DIGITAL | IOD_SS1 | SS1:.Klima[3].Kompresor2 | [6 empty] | 6157 | 0 | 0x05c03040
SS1Klima3NastMaxTemp | REAL | IOD_SS1 | SS1:.Klima[3].NastMaxTemp | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c03050
SS1Klima3NastMaxVlaznost | REAL | IOD_SS1 | SS1:.Klima[3].NastMaxVlaznost | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c03051
SS1Klima3NastMinTemp | REAL | IOD_SS1 | SS1:.Klima[3].NastMinTemp | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c03052
SS1Klima3NastMinVlaznost | REAL | IOD_SS1 | SS1:.Klima[3].NastMinVlaznost | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c03053
SS1Klima3NastTempProstora | REAL | IOD_SS1 | SS1:.Klima[3].NastTempProstora | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c03054
SS1Klima3NastVlaznost | REAL | IOD_SS1 | SS1:.Klima[3].NastVlaznost | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c03055
SS1Klima3Pritisk | REAL | IOD_SS1 | SS1:.Klima[3].Pritisk | 0 | 5 | 0 | 5 | bar | ##.# | 6157 | 0 | 0x05c03056
SS1Klima3Razvlazevanje | DIGITAL | IOD_SS1 | SS1:.Klima[3].Razvlazevanje | [6 empty] | 6157 | 0 | 0x05c03060
SS1Klima3TemperaturaProstora | REAL | IOD_SS1 | SS1:.Klima[3].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c03070
SS1Klima3VentilGretjeOdpiranje | DIGITAL | IOD_SS1 | SS1:.Klima[3].VentilGretjeOdpiranje | [6 empty] | 6157 | 0 | 0x05c03080
SS1Klima3VentilGretjeZapiranje | DIGITAL | IOD_SS1 | SS1:.Klima[3].VentilGretjeZapiranje | [6 empty] | 6157 | 0 | 0x05c03090
SS1Klima3Vlazenje | DIGITAL | IOD_SS1 | SS1:.Klima[3].Vlazenje | [6 empty] | 6157 | 0 | 0x05c030a0
SS1Klima3Vlazilec_Stanja | BYTE | IOD_SS1 | SS1:.Klima[3].Vlazilec_Stanja | [6 empty] | 6157 | 0 | 0x05c030b0
SS1Klima3VlaznostProstora | REAL | IOD_SS1 | SS1:.Klima[3].VlaznostProstora | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c030b1
SS1KlimaError1AlarmKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].AlarmKompresor1 | [6 empty] | 6157 | 0 | 0x05c030c0
SS1KlimaError1AlarmKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].AlarmKompresor2 | [6 empty] | 6157 | 0 | 0x05c030d0
SS1KlimaError1FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].FenThermalCutout | [6 empty] | 6157 | 0 | 0x05c030e0
SS1KlimaError1IzlivVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].IzlivVode | [6 empty] | 6157 | 0 | 0x05c030f0
SS1KlimaError1Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].Kompresor1naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x05c03100
SS1KlimaError1Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].Kompresor2naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x05c03110
SS1KlimaError1Kond1FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].Kond1FenThermalCutout | [6 empty] | 6157 | 0 | 0x05c03120
SS1KlimaError1Kond2FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].Kond2FenThermalCutout | [6 empty] | 6157 | 0 | 0x05c03130
SS1KlimaError1NapakaPriPretokuVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NapakaPriPretokuVode | [6 empty] | 6157 | 0 | 0x05c03140
SS1KlimaError1NapakaPriPretokuZraka | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NapakaPriPretokuZraka | [6 empty] | 6157 | 0 | 0x05c03150
SS1KlimaError1NapakaSenzorPritiska | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NapakaSenzorPritiska | [6 empty] | 6157 | 0 | 0x05c03160
SS1KlimaError1NapakaSenzorVlaznosti | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NapakaSenzorVlaznosti | [6 empty] | 6157 | 0 | 0x05c03170
SS1KlimaError1NapakaTSTemperaturaProstora | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NapakaTSTemperaturaProstora | [6 empty] | 6157 | 0 | 0x05c03180
SS1KlimaError1NiTokaVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NiTokaVVlazilcu | [6 empty] | 6157 | 0 | 0x05c03190
SS1KlimaError1NiVodeVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NiVodeVVlazilcu | [6 empty] | 6157 | 0 | 0x05c031a0
SS1KlimaError1NizekPritiskKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NizekPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x05c031b0
SS1KlimaError1NizekPritiskKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NizekPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x05c031c0
SS1KlimaError1NizkaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NizkaTempVProstoru | [6 empty] | 6157 | 0 | 0x05c031d0
SS1KlimaError1NizkaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NizkaVlaznost | [6 empty] | 6157 | 0 | 0x05c031e0
SS1KlimaError1PozarniAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].PozarniAlarm | [6 empty] | 6157 | 0 | 0x05c031f0
SS1KlimaError1TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].TermZascInVisokPritiskKompr1 | [6 empty] | 6157 | 0 | 0x05c03200
SS1KlimaError1TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].TermZascInVisokPritiskKompr2 | [6 empty] | 6157 | 0 | 0x05c03210
SS1KlimaError1ThermalCutoutHeater1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].ThermalCutoutHeater1 | [6 empty] | 6157 | 0 | 0x05c03220
SS1KlimaError1ThermalCutoutHeater2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].ThermalCutoutHeater2 | [6 empty] | 6157 | 0 | 0x05c03230
SS1KlimaError1VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VentilatorNaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x05c03240
SS1KlimaError1VisokaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VisokaTempVProstoru | [6 empty] | 6157 | 0 | 0x05c03250
SS1KlimaError1VisokaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VisokaVlaznost | [6 empty] | 6157 | 0 | 0x05c03260
SS1KlimaError1VisokPritiskVKrogu1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VisokPritiskVKrogu1 | [6 empty] | 6157 | 0 | 0x05c03270
SS1KlimaError1VisokPritiskVKrogu2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VisokPritiskVKrogu2 | [6 empty] | 6157 | 0 | 0x05c03280
SS1KlimaError1VisokTokVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VisokTokVVlazilcu | [6 empty] | 6157 | 0 | 0x05c03290
SS1KlimaError1VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VlazilecnaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x05c032a0
SS1KlimaError1ZamasenFilter | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].ZamasenFilter | [6 empty] | 6157 | 0 | 0x05c032b0
SS1KlimaError1ZunanjiAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].ZunanjiAlarm | [6 empty] | 6157 | 0 | 0x05c032c0
SS1KlimaError2AlarmKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].AlarmKompresor1 | [6 empty] | 6157 | 0 | 0x05c032d0
SS1KlimaError2AlarmKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].AlarmKompresor2 | [6 empty] | 6157 | 0 | 0x05c032e0
SS1KlimaError2FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].FenThermalCutout | [6 empty] | 6157 | 0 | 0x05c032f0
SS1KlimaError2IzlivVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].IzlivVode | [6 empty] | 6157 | 0 | 0x05c03300
SS1KlimaError2Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].Kompresor1naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x05c03310
SS1KlimaError2Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].Kompresor2naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x05c03320
SS1KlimaError2Kond1FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].Kond1FenThermalCutout | [6 empty] | 6157 | 0 | 0x05c03330
SS1KlimaError2Kond2FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].Kond2FenThermalCutout | [6 empty] | 6157 | 0 | 0x05c03340
SS1KlimaError2NapakaPriPretokuVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NapakaPriPretokuVode | [6 empty] | 6157 | 0 | 0x05c03350
SS1KlimaError2NapakaPriPretokuZraka | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NapakaPriPretokuZraka | [6 empty] | 6157 | 0 | 0x05c03360
SS1KlimaError2NapakaSenzorPritiska | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NapakaSenzorPritiska | [6 empty] | 6157 | 0 | 0x05c03370
SS1KlimaError2NapakaSenzorVlaznosti | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NapakaSenzorVlaznosti | [6 empty] | 6157 | 0 | 0x05c03380
SS1KlimaError2NapakaTSTemperaturaProstora | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NapakaTSTemperaturaProstora | [6 empty] | 6157 | 0 | 0x05c03390
SS1KlimaError2NiTokaVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NiTokaVVlazilcu | [6 empty] | 6157 | 0 | 0x05c033a0
SS1KlimaError2NiVodeVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NiVodeVVlazilcu | [6 empty] | 6157 | 0 | 0x05c033b0
SS1KlimaError2NizekPritiskKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NizekPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x05c033c0
SS1KlimaError2NizekPritiskKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NizekPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x05c033d0
SS1KlimaError2NizkaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NizkaTempVProstoru | [6 empty] | 6157 | 0 | 0x05c033e0
SS1KlimaError2NizkaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NizkaVlaznost | [6 empty] | 6157 | 0 | 0x05c033f0
SS1KlimaError2PozarniAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].PozarniAlarm | [6 empty] | 6157 | 0 | 0x05c03400
SS1KlimaError2TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].TermZascInVisokPritiskKompr1 | [6 empty] | 6157 | 0 | 0x05c03410
SS1KlimaError2TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].TermZascInVisokPritiskKompr2 | [6 empty] | 6157 | 0 | 0x05c03420
SS1KlimaError2ThermalCutoutHeater1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].ThermalCutoutHeater1 | [6 empty] | 6157 | 0 | 0x05c03430
SS1KlimaError2ThermalCutoutHeater2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].ThermalCutoutHeater2 | [6 empty] | 6157 | 0 | 0x05c03440
SS1KlimaError2VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VentilatorNaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x05c03450
SS1KlimaError2VisokaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VisokaTempVProstoru | [6 empty] | 6157 | 0 | 0x05c03460
SS1KlimaError2VisokaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VisokaVlaznost | [6 empty] | 6157 | 0 | 0x05c03470
SS1KlimaError2VisokPritiskVKrogu1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VisokPritiskVKrogu1 | [6 empty] | 6157 | 0 | 0x05c03480
SS1KlimaError2VisokPritiskVKrogu2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VisokPritiskVKrogu2 | [6 empty] | 6157 | 0 | 0x05c03490
SS1KlimaError2VisokTokVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VisokTokVVlazilcu | [6 empty] | 6157 | 0 | 0x05c034a0
SS1KlimaError2VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VlazilecnaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x05c034b0
SS1KlimaError2ZamasenFilter | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].ZamasenFilter | [6 empty] | 6157 | 0 | 0x05c034c0
SS1KlimaError2ZunanjiAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].ZunanjiAlarm | [6 empty] | 6157 | 0 | 0x05c034d0
SS1KlimaError3AlarmKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].AlarmKompresor1 | [6 empty] | 6157 | 0 | 0x05c034e0
SS1KlimaError3AlarmKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].AlarmKompresor2 | [6 empty] | 6157 | 0 | 0x05c034f0
SS1KlimaError3FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].FenThermalCutout | [6 empty] | 6157 | 0 | 0x05c03500
SS1KlimaError3IzlivVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].IzlivVode | [6 empty] | 6157 | 0 | 0x05c03510
SS1KlimaError3Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].Kompresor1naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x05c03520
SS1KlimaError3Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].Kompresor2naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x05c03530
SS1KlimaError3Kond1FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].Kond1FenThermalCutout | [6 empty] | 6157 | 0 | 0x05c03540
SS1KlimaError3Kond2FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].Kond2FenThermalCutout | [6 empty] | 6157 | 0 | 0x05c03550
SS1KlimaError3NapakaPriPretokuVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NapakaPriPretokuVode | [6 empty] | 6157 | 0 | 0x05c03560
SS1KlimaError3NapakaPriPretokuZraka | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NapakaPriPretokuZraka | [6 empty] | 6157 | 0 | 0x05c03570
SS1KlimaError3NapakaSenzorPritiska | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NapakaSenzorPritiska | [6 empty] | 6157 | 0 | 0x05c03580
SS1KlimaError3NapakaSenzorVlaznosti | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NapakaSenzorVlaznosti | [6 empty] | 6157 | 0 | 0x05c03590
SS1KlimaError3NapakaTSTemperaturaProstora | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NapakaTSTemperaturaProstora | [6 empty] | 6157 | 0 | 0x05c035a0
SS1KlimaError3NiTokaVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NiTokaVVlazilcu | [6 empty] | 6157 | 0 | 0x05c035b0
SS1KlimaError3NiVodeVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NiVodeVVlazilcu | [6 empty] | 6157 | 0 | 0x05c035c0
SS1KlimaError3NizekPritiskKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NizekPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x05c035d0
SS1KlimaError3NizekPritiskKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NizekPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x05c035e0
SS1KlimaError3NizkaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NizkaTempVProstoru | [6 empty] | 6157 | 0 | 0x05c035f0
SS1KlimaError3NizkaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NizkaVlaznost | [6 empty] | 6157 | 0 | 0x05c03600
SS1KlimaError3PozarniAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].PozarniAlarm | [6 empty] | 6157 | 0 | 0x05c03610
SS1KlimaError3TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].TermZascInVisokPritiskKompr1 | [6 empty] | 6157 | 0 | 0x05c03620
SS1KlimaError3TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].TermZascInVisokPritiskKompr2 | [6 empty] | 6157 | 0 | 0x05c03630
SS1KlimaError3ThermalCutoutHeater1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].ThermalCutoutHeater1 | [6 empty] | 6157 | 0 | 0x05c03640
SS1KlimaError3ThermalCutoutHeater2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].ThermalCutoutHeater2 | [6 empty] | 6157 | 0 | 0x05c03650
SS1KlimaError3VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VentilatorNaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x05c03660
SS1KlimaError3VisokaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VisokaTempVProstoru | [6 empty] | 6157 | 0 | 0x05c03670
SS1KlimaError3VisokaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VisokaVlaznost | [6 empty] | 6157 | 0 | 0x05c03680
SS1KlimaError3VisokPritiskVKrogu1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VisokPritiskVKrogu1 | [6 empty] | 6157 | 0 | 0x05c03690
SS1KlimaError3VisokPritiskVKrogu2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VisokPritiskVKrogu2 | [6 empty] | 6157 | 0 | 0x05c036a0
SS1KlimaError3VisokTokVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VisokTokVVlazilcu | [6 empty] | 6157 | 0 | 0x05c036b0
SS1KlimaError3VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VlazilecnaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x05c036c0
SS1KlimaError3ZamasenFilter | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].ZamasenFilter | [6 empty] | 6157 | 0 | 0x05c036d0
SS1KlimaError3ZunanjiAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].ZunanjiAlarm | [6 empty] | 6157 | 0 | 0x05c036e0
SS1NacDelovanjaKlime1_Avtomatsko | DIGITAL | IOD_SS1 | SS1:.NacDelovanjaKlime1_Avtomatsko | [6 empty] | 6157 | 0 | 0x05c036f0
SS1NacDelovanjaKlime2_3Avtomatsko | DIGITAL | IOD_SS1 | SS1:.NacDelovanjaKlime2_3Avtomatsko | [6 empty] | 6157 | 0 | 0x05c03700
SS1NapakaSenzorTemp1 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorTemp1 | [6 empty] | 6157 | 0 | 0x05c03710
SS1NapakaSenzorTemp2 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorTemp2 | [6 empty] | 6157 | 0 | 0x05c03720
SS1NapakaSenzorTemp3 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorTemp3 | [6 empty] | 6157 | 0 | 0x05c03730
SS1NapakaSenzorTempKontrSoba | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorTempKontrSoba | [6 empty] | 6157 | 0 | 0x05c03740
SS1NapakaSenzorTempLinkProstor | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorTempLinkProstor | [6 empty] | 6157 | 0 | 0x05c03750
SS1NapakaSenzorVlaga1 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorVlaga1 | [6 empty] | 6157 | 0 | 0x05c03760
SS1NapakaSenzorVlaga2 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorVlaga2 | [6 empty] | 6157 | 0 | 0x05c03770
SS1NapakaSenzorVlaga3 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorVlaga3 | [6 empty] | 6157 | 0 | 0x05c03780
SS1NapakaSenzorVlagaKontrSoba | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorVlagaKontrSoba | [6 empty] | 6157 | 0 | 0x05c03790
SS1NapakaSenzorVlagaLinkProstor | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorVlagaLinkProstor | [6 empty] | 6157 | 0 | 0x05c037a0
SS1NastaviCasNaKrmilniku | DIGITAL | IOD_SS1 | SS1:.NastaviCasNaKrmilniku | [6 empty] | 6157 | 0 | 0x05c037b0
SS1NastavitevUreKrUspesna | DIGITAL | IOD_SS1 | SS1:.NastavitevUreKrUspesna | [6 empty] | 6157 | 0 | 0x05c037c0
SS1ObratUreKlim1 | REAL | IOD_SS1 | SS1:.ObratUreKlim[1] | [6 empty] | 6157 | 0 | 0x05c037d0
SS1ObratUreKlim2 | REAL | IOD_SS1 | SS1:.ObratUreKlim[2] | [6 empty] | 6157 | 0 | 0x05c037d1
SS1ObratUreKlim3 | REAL | IOD_SS1 | SS1:.ObratUreKlim[3] | [6 empty] | 6157 | 0 | 0x05c037d2
SS1OpozoriloBaterijaPLC | DIGITAL | IOD_SS1 | SS1:.OpozoriloBaterijaPLC | [6 empty] | 6157 | 0 | 0x05c037e0
SS1PMMActiveEnergyConsumed_kWh | REAL | IOD_SS1 | SS1:.PMM.ActiveEnergyConsumed_kWh | [6 empty] | 6157 | 0 | 0x05c037f0
SS1PMMActivePowerPhaseA_kW | REAL | IOD_SS1 | SS1:.PMM.ActivePowerPhaseA_kW | [6 empty] | 6157 | 0 | 0x05c037f1
SS1PMMActivePowerPhaseB_kW | REAL | IOD_SS1 | SS1:.PMM.ActivePowerPhaseB_kW | [6 empty] | 6157 | 0 | 0x05c037f2
SS1PMMActivePowerPhaseC_kW | REAL | IOD_SS1 | SS1:.PMM.ActivePowerPhaseC_kW | [6 empty] | 6157 | 0 | 0x05c037f3
SS1PMMAlarmPhase1C01_16_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C01_16_60to80 | [6 empty] | 6157 | 0 | 0x05c037f4
SS1PMMAlarmPhase1C01_16_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C01_16_over80 | [6 empty] | 6157 | 0 | 0x05c037f5
SS1PMMAlarmPhase1C17_32_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C17_32_60to80 | [6 empty] | 6157 | 0 | 0x05c037f6
SS1PMMAlarmPhase1C17_32_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C17_32_over80 | [6 empty] | 6157 | 0 | 0x05c037f7
SS1PMMAlarmPhase1C33_42_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C33_42_60to80 | [6 empty] | 6157 | 0 | 0x05c037f8
SS1PMMAlarmPhase1C33_42_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C33_42_over80 | [6 empty] | 6157 | 0 | 0x05c037f9
SS1PMMAlarmPhase2C01_16_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C01_16_60to80 | [6 empty] | 6157 | 0 | 0x05c037fa
SS1PMMAlarmPhase2C01_16_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C01_16_over80 | [6 empty] | 6157 | 0 | 0x05c037fb
SS1PMMAlarmPhase2C17_32_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C17_32_60to80 | [6 empty] | 6157 | 0 | 0x05c037fc
SS1PMMAlarmPhase2C17_32_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C17_32_over80 | [6 empty] | 6157 | 0 | 0x05c037fd
SS1PMMAlarmPhase2C33_42_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C33_42_60to80 | [6 empty] | 6157 | 0 | 0x05c037fe
SS1PMMAlarmPhase2C33_42_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C33_42_over80 | [6 empty] | 6157 | 0 | 0x05c037ff
SS1PMMAlarmPhase3C01_16_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C01_16_60to80 | [6 empty] | 6157 | 0 | 0x05c03800
SS1PMMAlarmPhase3C01_16_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C01_16_over80 | [6 empty] | 6157 | 0 | 0x05c03801
SS1PMMAlarmPhase3C17_32_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C17_32_60to80 | [6 empty] | 6157 | 0 | 0x05c03802
SS1PMMAlarmPhase3C17_32_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C17_32_over80 | [6 empty] | 6157 | 0 | 0x05c03803
SS1PMMAlarmPhase3C33_42_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C33_42_60to80 | [6 empty] | 6157 | 0 | 0x05c03804
SS1PMMAlarmPhase3C33_42_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C33_42_over80 | [6 empty] | 6157 | 0 | 0x05c03805
SS1PMMAparentPowerPhaseA | REAL | IOD_SS1 | SS1:.PMM.AparentPowerPhaseA | [6 empty] | 6157 | 0 | 0x05c03806
SS1PMMAparentPowerPhaseB | REAL | IOD_SS1 | SS1:.PMM.AparentPowerPhaseB | [6 empty] | 6157 | 0 | 0x05c03807
SS1PMMAparentPowerPhaseC | REAL | IOD_SS1 | SS1:.PMM.AparentPowerPhaseC | [6 empty] | 6157 | 0 | 0x05c03808
SS1PMMAverageCurrent_A | REAL | IOD_SS1 | SS1:.PMM.AverageCurrent_A | [6 empty] | 6157 | 0 | 0x05c03809
SS1PMMAveragePhaseToNeutral_V | REAL | IOD_SS1 | SS1:.PMM.AveragePhaseToNeutral_V | 0 | 270.0 | 0 | 270.0 | V | ###.# | 6157 | 0 | 0x05c0380a
SS1PMMAveragePhaseToPhase_V | REAL | IOD_SS1 | SS1:.PMM.AveragePhaseToPhase_V | 0 | 450.0 | 0 | 450.0 | V | ###.# | 6157 | 0 | 0x05c0380b
SS1PMMCurrentInPhaseA_A | REAL | IOD_SS1 | SS1:.PMM.CurrentInPhaseA_A | 0 | 250.0 | 0 | 250.0 | A | ###.# | 6157 | 0 | 0x05c0380c
SS1PMMCurrentInPhaseB_A | REAL | IOD_SS1 | SS1:.PMM.CurrentInPhaseB_A | 0 | 250.0 | 0 | 250.0 | A | ###.# | 6157 | 0 | 0x05c0380d
SS1PMMCurrentInPhaseC_A | REAL | IOD_SS1 | SS1:.PMM.CurrentInPhaseC_A | 0 | 250.0 | 0 | 250.0 | A | ###.# | 6157 | 0 | 0x05c0380e
SS1PMMFrequency_Hz | REAL | IOD_SS1 | SS1:.PMM.Frequency_Hz | 0 | 60.00 | 0 | 60.00 | Hz | ##.# | 6157 | 0 | 0x05c0380f
SS1PMMPhase1Current10 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[10] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03810
SS1PMMPhase1Current11 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[11] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03811
SS1PMMPhase1Current12 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[12] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03812
SS1PMMPhase1Current13 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[13] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03813
SS1PMMPhase1Current14 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[14] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03814
SS1PMMPhase1Current15 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[15] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03815
SS1PMMPhase1Current16 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[16] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03816
SS1PMMPhase1Current17 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[17] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03817
SS1PMMPhase1Current18 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[18] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03818
SS1PMMPhase1Current19 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[19] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03819
SS1PMMPhase1Current1 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[1] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0381a
SS1PMMPhase1Current20 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[20] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0381b
SS1PMMPhase1Current21 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[21] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0381c
SS1PMMPhase1Current22 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[22] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0381d
SS1PMMPhase1Current23 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[23] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0381e
SS1PMMPhase1Current24 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[24] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0381f
SS1PMMPhase1Current25 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[25] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03820
SS1PMMPhase1Current26 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[26] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03821
SS1PMMPhase1Current27 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[27] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03822
SS1PMMPhase1Current28 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[28] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03823
SS1PMMPhase1Current29 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[29] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03824
SS1PMMPhase1Current2 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[2] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03825
SS1PMMPhase1Current30 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[30] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03826
SS1PMMPhase1Current31 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[31] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03827
SS1PMMPhase1Current32 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[32] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03828
SS1PMMPhase1Current33 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[33] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03829
SS1PMMPhase1Current34 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[34] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0382a
SS1PMMPhase1Current35 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[35] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0382b
SS1PMMPhase1Current36 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[36] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0382c
SS1PMMPhase1Current37 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[37] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0382d
SS1PMMPhase1Current38 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[38] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0382e
SS1PMMPhase1Current39 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[39] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0382f
SS1PMMPhase1Current3 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[3] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03830
SS1PMMPhase1Current40 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[40] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03831
SS1PMMPhase1Current41 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[41] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03832
SS1PMMPhase1Current42 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[42] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03833
SS1PMMPhase1Current4 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[4] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03834
SS1PMMPhase1Current5 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[5] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03835
SS1PMMPhase1Current6 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[6] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03836
SS1PMMPhase1Current7 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[7] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03837
SS1PMMPhase1Current8 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[8] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03838
SS1PMMPhase1Current9 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[9] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03839
SS1PMMPhase2Current10 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[10] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0383a
SS1PMMPhase2Current11 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[11] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0383b
SS1PMMPhase2Current12 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[12] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0383c
SS1PMMPhase2Current13 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[13] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0383d
SS1PMMPhase2Current14 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[14] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0383e
SS1PMMPhase2Current15 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[15] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0383f
SS1PMMPhase2Current16 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[16] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03840
SS1PMMPhase2Current17 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[17] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03841
SS1PMMPhase2Current18 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[18] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03842
SS1PMMPhase2Current19 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[19] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03843
SS1PMMPhase2Current1 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[1] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03844
SS1PMMPhase2Current20 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[20] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03845
SS1PMMPhase2Current21 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[21] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03846
SS1PMMPhase2Current22 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[22] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03847
SS1PMMPhase2Current23 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[23] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03848
SS1PMMPhase2Current24 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[24] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03849
SS1PMMPhase2Current25 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[25] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0384a
SS1PMMPhase2Current26 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[26] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0384b
SS1PMMPhase2Current27 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[27] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0384c
SS1PMMPhase2Current28 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[28] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0384d
SS1PMMPhase2Current29 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[29] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0384e
SS1PMMPhase2Current2 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[2] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0384f
SS1PMMPhase2Current30 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[30] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03850
SS1PMMPhase2Current31 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[31] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03851
SS1PMMPhase2Current32 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[32] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03852
SS1PMMPhase2Current33 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[33] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03853
SS1PMMPhase2Current34 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[34] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03854
SS1PMMPhase2Current35 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[35] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03855
SS1PMMPhase2Current36 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[36] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03856
SS1PMMPhase2Current37 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[37] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03857
SS1PMMPhase2Current38 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[38] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03858
SS1PMMPhase2Current39 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[39] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03859
SS1PMMPhase2Current3 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[3] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0385a
SS1PMMPhase2Current40 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[40] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0385b
SS1PMMPhase2Current41 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[41] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0385c
SS1PMMPhase2Current42 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[42] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0385d
SS1PMMPhase2Current4 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[4] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0385e
SS1PMMPhase2Current5 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[5] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0385f
SS1PMMPhase2Current6 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[6] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03860
SS1PMMPhase2Current7 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[7] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03861
SS1PMMPhase2Current8 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[8] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03862
SS1PMMPhase2Current9 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[9] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03863
SS1PMMPhase3Current10 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[10] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03864
SS1PMMPhase3Current11 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[11] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03865
SS1PMMPhase3Current12 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[12] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03866
SS1PMMPhase3Current13 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[13] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03867
SS1PMMPhase3Current14 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[14] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03868
SS1PMMPhase3Current15 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[15] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03869
SS1PMMPhase3Current16 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[16] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0386a
SS1PMMPhase3Current17 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[17] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0386b
SS1PMMPhase3Current18 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[18] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0386c
SS1PMMPhase3Current19 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[19] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0386d
SS1PMMPhase3Current1 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[1] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0386e
SS1PMMPhase3Current20 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[20] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0386f
SS1PMMPhase3Current21 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[21] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03870
SS1PMMPhase3Current22 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[22] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03871
SS1PMMPhase3Current23 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[23] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03872
SS1PMMPhase3Current24 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[24] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03873
SS1PMMPhase3Current25 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[25] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03874
SS1PMMPhase3Current26 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[26] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03875
SS1PMMPhase3Current27 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[27] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03876
SS1PMMPhase3Current28 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[28] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03877
SS1PMMPhase3Current29 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[29] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03878
SS1PMMPhase3Current2 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[2] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03879
SS1PMMPhase3Current30 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[30] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0387a
SS1PMMPhase3Current31 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[31] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0387b
SS1PMMPhase3Current32 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[32] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0387c
SS1PMMPhase3Current33 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[33] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0387d
SS1PMMPhase3Current34 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[34] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0387e
SS1PMMPhase3Current35 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[35] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0387f
SS1PMMPhase3Current36 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[36] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03880
SS1PMMPhase3Current37 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[37] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03881
SS1PMMPhase3Current38 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[38] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03882
SS1PMMPhase3Current39 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[39] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03883
SS1PMMPhase3Current3 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[3] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03884
SS1PMMPhase3Current40 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[40] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03885
SS1PMMPhase3Current41 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[41] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03886
SS1PMMPhase3Current42 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[42] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03887
SS1PMMPhase3Current4 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[4] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03888
SS1PMMPhase3Current5 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[5] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c03889
SS1PMMPhase3Current6 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[6] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0388a
SS1PMMPhase3Current7 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[7] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0388b
SS1PMMPhase3Current8 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[8] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0388c
SS1PMMPhase3Current9 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[9] | 0 | 16.00 | 0 | 16.00 | A | ##.# | 6157 | 0 | 0x05c0388d
SS1PMMPowerFactorSys | REAL | IOD_SS1 | SS1:.PMM.PowerFactorSys | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.# | 6157 | 0 | 0x05c0388e
SS1PMMReactiveEnergyConsumed_kVARh | REAL | IOD_SS1 | SS1:.PMM.ReactiveEnergyConsumed_kVARh |  |  |  |  | kVArh | ####.# | 6157 | 0 | 0x05c0388f
SS1PMMReactivePowerPhaseA | REAL | IOD_SS1 | SS1:.PMM.ReactivePowerPhaseA | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x05c03890
SS1PMMReactivePowerPhaseB | REAL | IOD_SS1 | SS1:.PMM.ReactivePowerPhaseB | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x05c03891
SS1PMMReactivePowerPhaseC | REAL | IOD_SS1 | SS1:.PMM.ReactivePowerPhaseC | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x05c03892
SS1PMMTotalActivePower_kW | REAL | IOD_SS1 | SS1:.PMM.TotalActivePower_kW | 0 | 300 | 0 | 300 | kW | ####.# | 6157 | 0 | 0x05c03893
SS1PMMTotalAparentPower_kVA | REAL | IOD_SS1 | SS1:.PMM.TotalAparentPower_kVA | 0 | 300 | 0 | 300 | kVA | ####.# | 6157 | 0 | 0x05c03894
SS1PMMTotalPowerFactor | REAL | IOD_SS1 | SS1:.PMM.TotalPowerFactor | 0 | 1 | 0 | 1 |  | ####.# | 6157 | 0 | 0x05c03895
SS1PMMTotalReactivePower_kVAR | REAL | IOD_SS1 | SS1:.PMM.TotalReactivePower_kVAR | 0 | 300 | 0 | 300 | kVAr | ####.# | 6157 | 0 | 0x05c03896
SS1PMMVirA_fsys | REAL | IOD_SS1 | SS1:.PMM.VirA_fsys | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 0 | 0x05c03897
SS1PMMVirA_Isys | REAL | IOD_SS1 | SS1:.PMM.VirA_Isys | 0 | 1000 | 0 | 1000 | A | ####.# | 6157 | 0 | 0x05c03898
SS1PMMVirA_PFsys | REAL | IOD_SS1 | SS1:.PMM.VirA_PFsys | 0 | 1 | 0 | 0 | 1 | ####.# | 6157 | 0 | 0x05c03899
SS1PMMVirA_Psys | REAL | IOD_SS1 | SS1:.PMM.VirA_Psys | 0 | 300 | 0 | 300 | kW | ####.# | 6157 | 0 | 0x05c0389a
SS1PMMVirA_Qsys | REAL | IOD_SS1 | SS1:.PMM.VirA_Qsys | 0 | 300 | 0 | 300 | kVAr | ####.# | 6157 | 0 | 0x05c0389b
SS1PMMVirA_Ssys | REAL | IOD_SS1 | SS1:.PMM.VirA_Ssys | 0 | 300 | 0 | 300 | kVA | ####.# | 6157 | 0 | 0x05c0389c
SS1PMMVirA_Usys | REAL | IOD_SS1 | SS1:.PMM.VirA_Usys | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x05c0389d
SS1PMMVirB_fsys | REAL | IOD_SS1 | SS1:.PMM.VirB_fsys | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 0 | 0x05c0389e
SS1PMMVirB_Isys | REAL | IOD_SS1 | SS1:.PMM.VirB_Isys | 0 | 1000 | 0 | 1000 | A | ####.# | 6157 | 0 | 0x05c0389f
SS1PMMVirB_PFsys | REAL | IOD_SS1 | SS1:.PMM.VirB_PFsys | 0 | 1 | 0 | 0 | 1 | ####.# | 6157 | 0 | 0x05c038a0
SS1PMMVirB_Psys | REAL | IOD_SS1 | SS1:.PMM.VirB_Psys | 0 | 300 | 0 | 300 | kW | ####.# | 6157 | 0 | 0x05c038a1
SS1PMMVirB_Qsys | REAL | IOD_SS1 | SS1:.PMM.VirB_Qsys | 0 | 300 | 0 | 300 | kVAr | ####.# | 6157 | 0 | 0x05c038a2
SS1PMMVirB_Ssys | REAL | IOD_SS1 | SS1:.PMM.VirB_Ssys | 0 | 300 | 0 | 300 | kVA | ####.# | 6157 | 0 | 0x05c038a3
SS1PMMVirB_Usys | REAL | IOD_SS1 | SS1:.PMM.VirB_Usys | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x05c038a4
SS1PMMVirBActiveEnergyConsumed_kWh | REAL | IOD_SS1 | SS1:.PMM.VirBActiveEnergyConsumed_kWh |  |  |  |  | kVArh | ####.# | 6157 | 0 | 0x05c038a5
SS1PMMVirBActivePowerPhaseA_kW | REAL | IOD_SS1 | SS1:.PMM.VirBActivePowerPhaseA_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 0 | 0x05c038a6
SS1PMMVirBActivePowerPhaseB_kW | REAL | IOD_SS1 | SS1:.PMM.VirBActivePowerPhaseB_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 0 | 0x05c038a7
SS1PMMVirBActivePowerPhaseC_kW | REAL | IOD_SS1 | SS1:.PMM.VirBActivePowerPhaseC_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 0 | 0x05c038a8
SS1PMMVirBAparentPowerPhaseA | REAL | IOD_SS1 | SS1:.PMM.VirBAparentPowerPhaseA | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x05c038a9
SS1PMMVirBAparentPowerPhaseB | REAL | IOD_SS1 | SS1:.PMM.VirBAparentPowerPhaseB | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x05c038aa
SS1PMMVirBAparentPowerPhaseC | REAL | IOD_SS1 | SS1:.PMM.VirBAparentPowerPhaseC | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x05c038ab
SS1PMMVirBAverageCurrent_A | REAL | IOD_SS1 | SS1:.PMM.VirBAverageCurrent_A | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 0 | 0x05c038ac
SS1PMMVirBAveragePhaseToNeutral_V | REAL | IOD_SS1 | SS1:.PMM.VirBAveragePhaseToNeutral_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x05c038ad
SS1PMMVirBAveragePhaseToPhase_V | REAL | IOD_SS1 | SS1:.PMM.VirBAveragePhaseToPhase_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x05c038ae
SS1PMMVirBCurrentInPhaseA_A | REAL | IOD_SS1 | SS1:.PMM.VirBCurrentInPhaseA_A | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 0 | 0x05c038af
SS1PMMVirBCurrentInPhaseB_A | REAL | IOD_SS1 | SS1:.PMM.VirBCurrentInPhaseB_A | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 0 | 0x05c038b0
SS1PMMVirBCurrentInPhaseC_A | REAL | IOD_SS1 | SS1:.PMM.VirBCurrentInPhaseC_A | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 0 | 0x05c038b1
SS1PMMVirBFrequency_Hz | REAL | IOD_SS1 | SS1:.PMM.VirBFrequency_Hz | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 0 | 0x05c038b2
SS1PMMVirBPowerFactorSys | REAL | IOD_SS1 | SS1:.PMM.VirBPowerFactorSys | 0 | 1 | 0 | 1 |  | ####.# | 6157 | 0 | 0x05c038b3
SS1PMMVirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS1 | SS1:.PMM.VirBReactiveEnergyConsumed_kWh |  |  |  |  | kVArh | ####.# | 6157 | 0 | 0x05c038b4
SS1PMMVirBReactivePowerPhaseA | REAL | IOD_SS1 | SS1:.PMM.VirBReactivePowerPhaseA | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x05c038b5
SS1PMMVirBReactivePowerPhaseB | REAL | IOD_SS1 | SS1:.PMM.VirBReactivePowerPhaseB | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x05c038b6
SS1PMMVirBReactivePowerPhaseC | REAL | IOD_SS1 | SS1:.PMM.VirBReactivePowerPhaseC | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x05c038b7
SS1PMMVirBTotalActivePower_kW | REAL | IOD_SS1 | SS1:.PMM.VirBTotalActivePower_kW | 0 | 300 | 0 | 300 | kW | ####.# | 6157 | 0 | 0x05c038b8
SS1PMMVirBTotalAparentPower_kVA | REAL | IOD_SS1 | SS1:.PMM.VirBTotalAparentPower_kVA | 0 | 300 | 0 | 300 | kVA | ####.# | 6157 | 0 | 0x05c038b9
SS1PMMVirBTotalPowerFactor | REAL | IOD_SS1 | SS1:.PMM.VirBTotalPowerFactor | 0 | 1 | 0 | 1 |  | ####.# | 6157 | 0 | 0x05c038ba
SS1PMMVirBTotalReactivePower_kVAR | REAL | IOD_SS1 | SS1:.PMM.VirBTotalReactivePower_kVAR | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x05c038bb
SS1PMMVirBVoltageBetweenPhaseAB_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseAB_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x05c038bc
SS1PMMVirBVoltageBetweenPhaseAN_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseAN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x05c038bd
SS1PMMVirBVoltageBetweenPhaseBC_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseBC_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x05c038be
SS1PMMVirBVoltageBetweenPhaseBN_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseBN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x05c038bf
SS1PMMVirBVoltageBetweenPhaseCA_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseCA_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x05c038c0
SS1PMMVirBVoltageBetweenPhaseCN_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseCN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x05c038c1
SS1PMMVoltageBetweenPhaseAB_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseAB_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x05c038c2
SS1PMMVoltageBetweenPhaseAN_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseAN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x05c038c3
SS1PMMVoltageBetweenPhaseBC_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseBC_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x05c038c4
SS1PMMVoltageBetweenPhaseBN_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseBN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x05c038c5
SS1PMMVoltageBetweenPhaseCA_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseCA_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x05c038c6
SS1PMMVoltageBetweenPhaseCN_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseCN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x05c038c7
SS1PMM1OverCurrentBetw1 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentBetw[1] | [6 empty] | 6157 | 0 | 0x05c038d0
SS1PMM1OverCurrentBetw2 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentBetw[2] | [6 empty] | 6157 | 0 | 0x05c038e0
SS1PMM1OverCurrentBetw3 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentBetw[3] | [6 empty] | 6157 | 0 | 0x05c038f0
SS1PMM1OverCurrentOver1 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentOver[1] | [6 empty] | 6157 | 0 | 0x05c03900
SS1PMM1OverCurrentOver2 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentOver[2] | [6 empty] | 6157 | 0 | 0x05c03910
SS1PMM1OverCurrentOver3 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentOver[3] | [6 empty] | 6157 | 0 | 0x05c03920
SS1PMM1OverVoltage | DIGITAL | IOD_SS1 | SS1:.PMM1OverVoltage | [6 empty] | 6157 | 0 | 0x05c03930
SS1RocniVklopKlima1 | DIGITAL | IOD_SS1 | SS1:.RocniVklopKlima1 | [6 empty] | 6157 | 0 | 0x05c03940
SS1RocniVklopKlima2 | DIGITAL | IOD_SS1 | SS1:.RocniVklopKlima2 | [6 empty] | 6157 | 0 | 0x05c03950
SS1RocniVklopKlima3 | DIGITAL | IOD_SS1 | SS1:.RocniVklopKlima3 | [6 empty] | 6157 | 0 | 0x05c03960
SS1SinhronizacijaPanelOK | DIGITAL | IOD_SS1 | SS1:.SinhronizacijaPanelOK | [6 empty] | 6157 | 0 | 0x05c03970
SS1SinhronizirajCas_Panel | DIGITAL | IOD_SS1 | SS1:.SinhronizirajCas_Panel | [6 empty] | 6157 | 0 | 0x05c03980
SS1SKTemp1 | REAL | IOD_SS1 | SS1:.SKTemp1 | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c03990
SS1SKTemp2 | REAL | IOD_SS1 | SS1:.SKTemp2 | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c03991
SS1SKTemp3 | REAL | IOD_SS1 | SS1:.SKTemp3 | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c03992
SS1SKTempKontrSoba | REAL | IOD_SS1 | SS1:.SKTempKontrSoba | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c03993
SS1SKTempLinkProstor | REAL | IOD_SS1 | SS1:.SKTempLinkProstor | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c03994
SS1SKTempServSoba1Povpr | REAL | IOD_SS1 | SS1:.SKTempServSoba1Povpr | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c03995
SS1SkupneNapakeNaprav_Klima1 | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_Klima1 | [6 empty] | 6157 | 0 | 0x05c039a0
SS1SkupneNapakeNaprav_Klima2 | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_Klima2 | [6 empty] | 6157 | 0 | 0x05c039b0
SS1SkupneNapakeNaprav_Klima3 | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_Klima3 | [6 empty] | 6157 | 0 | 0x05c039c0
SS1SkupneNapakeNaprav_Komunikacija | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_Komunikacija | [6 empty] | 6157 | 0 | 0x05c039d0
SS1SkupneNapakeNaprav_PMMVirA | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_PMMVirA | [6 empty] | 6157 | 0 | 0x05c039e0
SS1SkupneNapakeNaprav_PMMVirB | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_PMMVirB | [6 empty] | 6157 | 0 | 0x05c039f0
SS1SkupneNapakeNaprav_PMMVirBVirA | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_PMMVirBVirA | [6 empty] | 6157 | 0 | 0x05c03a00
SS1SkupneNapakeNaprav_TempVlaga | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_TempVlaga | [6 empty] | 6157 | 0 | 0x05c03a10
SS1SKVlaga1 | REAL | IOD_SS1 | SS1:.SKVlaga1 | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c03a20
SS1SKVlaga2 | REAL | IOD_SS1 | SS1:.SKVlaga2 | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c03a21
SS1SKVlaga3 | REAL | IOD_SS1 | SS1:.SKVlaga3 | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c03a22
SS1SKVlagaKontrSoba | REAL | IOD_SS1 | SS1:.SKVlagaKontrSoba | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c03a23
SS1SKVlagaLinkProstor | REAL | IOD_SS1 | SS1:.SKVlagaLinkProstor | 0 | 100 | 0 | 100 | % | ##.# | 6157 | 0 | 0x05c03a24
SS1StanjeKlimat1_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeKlimat1_Delovanje | [6 empty] | 6157 | 0 | 0x05c03a30
SS1StanjeKlimat2_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeKlimat2_Delovanje | [6 empty] | 6157 | 0 | 0x05c03a40
SS1StanjeKlimat3_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeKlimat3_Delovanje | [6 empty] | 6157 | 0 | 0x05c03a50
SS1StanjeSP1_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeSP1_Delovanje | [6 empty] | 6157 | 0 | 0x05c03a60
SS1StanjeSP2_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeSP2_Delovanje | [6 empty] | 6157 | 0 | 0x05c03a70
SS1StanjeSP3_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeSP3_Delovanje | [6 empty] | 6157 | 0 | 0x05c03a80
SS1StanjeSP4_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeSP4_Delovanje | [6 empty] | 6157 | 0 | 0x05c03a90
SS1StanjeSP5_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeSP5_Delovanje | [6 empty] | 6157 | 0 | 0x05c03aa0
SS1StanjeUPSKrmOmara_BaterijskiNacin | DIGITAL | IOD_SS1 | SS1:.StanjeUPSKrmOmara_BaterijskiNacin | [6 empty] | 6157 | 0 | 0x05c03ab0
SS1StanjeUPSKrmOmara_Polnenje | DIGITAL | IOD_SS1 | SS1:.StanjeUPSKrmOmara_Polnenje | [6 empty] | 6157 | 0 | 0x05c03ac0
SS1StUrZaPreklopKlim | INT | IOD_SS1 | SS1:.StUrZaPreklopKlim | [6 empty] | 6157 | 0 | 0x05c03ad0
SS1TempZaAlarmTIA123 | REAL | IOD_SS1 | SS1:.TempZaAlarmTIA123 | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c03ad1
SS1TempZaAlarmTIA4 | REAL | IOD_SS1 | SS1:.TempZaAlarmTIA4 | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c03ad2
SS1TempZaAlarmTIA5 | REAL | IOD_SS1 | SS1:.TempZaAlarmTIA5 | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c03ad3
SS1TempZaVklopObehKlim | REAL | IOD_SS1 | SS1:.TempZaVklopObehKlim | 0 | 60 | 0 | 60 | °C | ##.# | 6157 | 0 | 0x05c03ad4
SS1UPSstatus_Prikaz_PanelSCADA | BYTE | IOD_SS1 | SS1:.UPSstatus_Prikaz_PanelSCADA | [6 empty] | 6157 | 0 | 0x05c03ad5
SS1UserCurrentLevel | BYTE | IOD_SS1 | SS1:.UserCurrentLevel | [6 empty] | 6157 | 0 | 0x05c03ad6
SS1UserLoggedIn | DIGITAL | IOD_SS1 | SS1:.UserLoggedIn | [6 empty] | 6157 | 0 | 0x05c03ae0
SS1UserName | STRING | IOD_SS1 | SS1:.UserName | [6 empty] | 6157 | 0 | 0x05c03af0
SS1XVH_AlarmOn | DIGITAL | IOD_SS1 | SS1:.XVH_AlarmOn | [6 empty] | 6157 | 0 | 0x05c03b00
SS1OnemAlarmPon | DIGITAL | IOD_SS1_disk | D325 | [8 empty] | 0x05c03b10
SS1OmogociVseAlarme | DIGITAL | IOD_SS1_disk | D328 | [8 empty] | 0x05c03b20
SS1OmogociVseSMSAlarme | DIGITAL | IOD_SS1_disk | D321 | [8 empty] | 0x05c03b30
SS1OmogociVseDogodke_DO | DIGITAL | IOD_SS1_disk | D322 | [8 empty] | 0x05c03b40
SS1OmogociVseDogodke_DI | DIGITAL | IOD_SS1_disk | D323 | [8 empty] | 0x05c03b50
SS1OmogociVseDogodke_COM | DIGITAL | IOD_SS1_disk | D324 | [8 empty] | 0x05c03b60
SS1PricetekSMSAlarmov1 | INT | IOD_SS1_disk | I21 | [5 empty] | ## |  |  | 0x05c03b70
SS1KonecSMSAlarmov1 | INT | IOD_SS1_disk | I22 | [5 empty] | ## |  |  | 0x05c03b71
SS1ErrCommScada_Omogoci | DIGITAL | IOD_SS1_disk | D326 | [8 empty] | 0x05c03b80
Test | INT | IOD_SS1_disk | I23 | [8 empty] | 0x05c03b90
SS1Klimat1_Vklop | DIGITAL | IOD_SS1 | SS1:.Klimat1_Vklop | [8 empty] | 0x05c03ba0
SS1Klimat2_Vklop | DIGITAL | IOD_SS1 | SS1:.Klimat2_Vklop | [8 empty] | 0x05c03bb0
SS1Klimat3_Vklop | DIGITAL | IOD_SS1 | SS1:.Klimat3_Vklop | [8 empty] | 0x05c03bc0
SS1PricetekSMSAlarmov2 | INT | IOD_SS1_disk | I24 | [5 empty] | ## |  |  | 0x05c03bd0
SS1KonecSMSAlarmov2 | INT | IOD_SS1_disk | I25 | [5 empty] | ## |  |  | 0x05c03bd1
SS1OnemAlarmPon2 | DIGITAL | IOD_SS1_disk | D327 | [8 empty] | 0x05c03be0
SS1ErrCommScada2 | DIGITAL | IOD_SS1 | SS1:.ErrCommScada2 | [8 empty] | 0x05c03bf0
SS1ComSCADA2 | DIGITAL | IOD_SS1 | SS1:.ComSCADA2 | [8 empty] | 0x05c03c00
SS1ErrCommScada_Omogoci2 | DIGITAL | IOD_SS1_disk | D330 | [8 empty] | 0x05c03c10
SS1Server_A_Izpad | DIGITAL | IOD_SS1_disk | D331 | [8 empty] | 0x05c03c20
SS1Server_B_Izpad | DIGITAL | IOD_SS1_disk | D332 | [8 empty] | 0x05c03c30
SS1ComSCADA_stevec3 | INT | IOD_SS1_mem | I3450 | [8 empty] | 0x05c03c40
SS1ComSCADA_stevec | INT | IOD_SS1_mem | I3452 | [8 empty] | 0x05c03c41
SS1ComSCADA3 | DIGITAL | IOD_SS1 | SS1:.ComSCADA3 | [8 empty] | 0x05c03c50
SS1kom_nast_cas_izpada | UINT | IOD_SS1 | SS1:.kom_nast_cas_izpada | [8 empty] | 0x05c03c60
BSS1_omogoci_sms | DIGITAL | IOD_SS1_disk | D4000[200] | [8 empty] | 0x05c03c70

## variable_1
SS1AktualniSetPointTemp | REAL | IOD_SS1 | SS1:.AktualniSetPointTemp
SS1AktualniSetPointVlaga | REAL | IOD_SS1 | SS1:.AktualniSetPointVlaga
SS1AlarmKlimat1_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmKlimat1_Napaka
SS1AlarmKlimat2_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmKlimat2_Napaka
SS1AlarmKlimat3_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmKlimat3_Napaka
SS1AlarmLAH1_RazlitjeVode | DIGITAL | IOD_SS1 | SS1:.AlarmLAH1_RazlitjeVode
SS1AlarmLAH2_RazlitjeVode | DIGITAL | IOD_SS1 | SS1:.AlarmLAH2_RazlitjeVode
SS1AlarmSinhronizacijaNOK | DIGITAL | IOD_SS1 | SS1:.AlarmSinhronizacijaNOK
SS1AlarmSP1_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmSP1_Napaka
SS1AlarmSP2_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmSP2_Napaka
SS1AlarmSP3_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmSP3_Napaka
SS1AlarmSP4_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmSP4_Napaka
SS1AlarmSP5_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmSP5_Napaka
SS1AlarmTempTIA123Previsoka | DIGITAL | IOD_SS1 | SS1:.AlarmTempTIA123Previsoka
SS1AlarmTempTIA4Previsoka | DIGITAL | IOD_SS1 | SS1:.AlarmTempTIA4Previsoka
SS1AlarmTempTIA5Previsoka | DIGITAL | IOD_SS1 | SS1:.AlarmTempTIA5Previsoka
SS1AlarmTSTempPrevisoka | DIGITAL | IOD_SS1 | SS1:.AlarmTSTempPrevisoka
SS1AlarmUPSKrmOmara_Alarm | DIGITAL | IOD_SS1 | SS1:.AlarmUPSKrmOmara_Alarm
SS1ComSCADA | DIGITAL | IOD_SS1 | SS1:.ComSCADA
SS1ComSCADA1 | DIGITAL | IOD_SS1 | SS1:.ComSCADA1
SS1DatumCasDan | INT | IOD_SS1 | SS1:.DatumCas.Dan | BYTE
SS1DatumCasLeto | INT | IOD_SS1 | SS1:.DatumCas.Leto | BYTE
SS1DatumCasLeto2 | INT | IOD_SS1 | SS1:.DatumCas.Leto2
SS1DatumCasMesec | INT | IOD_SS1 | SS1:.DatumCas.Mesec | BYTE
SS1DatumCasMinuta | INT | IOD_SS1 | SS1:.DatumCas.Minuta | BYTE
SS1DatumCasSekunda | INT | IOD_SS1 | SS1:.DatumCas.Sekunda | BYTE
SS1DatumCasUra | INT | IOD_SS1 | SS1:.DatumCas.Ura | BYTE
SS1ErrComKlima1 | DIGITAL | IOD_SS1 | SS1:.ErrComKlima[1]
SS1ErrComKlima2 | DIGITAL | IOD_SS1 | SS1:.ErrComKlima[2]
SS1ErrComKlima3 | DIGITAL | IOD_SS1 | SS1:.ErrComKlima[3]
SS1ErrCommScada | DIGITAL | IOD_SS1 | SS1:.ErrCommScada
SS1ErrComPanelPLC | DIGITAL | IOD_SS1 | SS1:.ErrComPanelPLC
SS1ErrComPMM | DIGITAL | IOD_SS1 | SS1:.ErrComPMM
SS1ErrComPort2 | DIGITAL | IOD_SS1 | SS1:.ErrComPort2
SS1Klima1_Onemogocena | DIGITAL | IOD_SS1 | SS1:.Klima1_Onemogocena
SS1Klima2_Onemogocena | DIGITAL | IOD_SS1 | SS1:.Klima2_Onemogocena
SS1Klima3_Onemogocena | DIGITAL | IOD_SS1 | SS1:.Klima3_Onemogocena
SS1Klima1IzhodniVentilator | DIGITAL | IOD_SS1 | SS1:.Klima[1].IzhodniVentilator
SS1Klima1Kompresor1 | DIGITAL | IOD_SS1 | SS1:.Klima[1].Kompresor1
SS1Klima1Kompresor2 | DIGITAL | IOD_SS1 | SS1:.Klima[1].Kompresor2
SS1Klima1NastMaxTemp | REAL | IOD_SS1 | SS1:.Klima[1].NastMaxTemp
SS1Klima1NastMaxVlaznost | REAL | IOD_SS1 | SS1:.Klima[1].NastMaxVlaznost
SS1Klima1NastMinTemp | REAL | IOD_SS1 | SS1:.Klima[1].NastMinTemp
SS1Klima1NastMinVlaznost | REAL | IOD_SS1 | SS1:.Klima[1].NastMinVlaznost
SS1Klima1NastTempProstora | REAL | IOD_SS1 | SS1:.Klima[1].NastTempProstora
SS1Klima1NastVlaznost | REAL | IOD_SS1 | SS1:.Klima[1].NastVlaznost
SS1Klima1Pritisk | REAL | IOD_SS1 | SS1:.Klima[1].Pritisk
SS1Klima1Razvlazevanje | DIGITAL | IOD_SS1 | SS1:.Klima[1].Razvlazevanje
SS1Klima1TemperaturaProstora | REAL | IOD_SS1 | SS1:.Klima[1].TemperaturaProstora
SS1Klima1VentilGretjeOdpiranje | DIGITAL | IOD_SS1 | SS1:.Klima[1].VentilGretjeOdpiranje
SS1Klima1VentilGretjeZapiranje | DIGITAL | IOD_SS1 | SS1:.Klima[1].VentilGretjeZapiranje
SS1Klima1Vlazenje | DIGITAL | IOD_SS1 | SS1:.Klima[1].Vlazenje
SS1Klima1Vlazilec_Stanja | INT | IOD_SS1 | SS1:.Klima[1].Vlazilec_Stanja | BYTE
SS1Klima1VlaznostProstora | REAL | IOD_SS1 | SS1:.Klima[1].VlaznostProstora
SS1Klima2IzhodniVentilator | DIGITAL | IOD_SS1 | SS1:.Klima[2].IzhodniVentilator
SS1Klima2Kompresor1 | DIGITAL | IOD_SS1 | SS1:.Klima[2].Kompresor1
SS1Klima2Kompresor2 | DIGITAL | IOD_SS1 | SS1:.Klima[2].Kompresor2
SS1Klima2NastMaxTemp | REAL | IOD_SS1 | SS1:.Klima[2].NastMaxTemp
SS1Klima2NastMaxVlaznost | REAL | IOD_SS1 | SS1:.Klima[2].NastMaxVlaznost
SS1Klima2NastMinTemp | REAL | IOD_SS1 | SS1:.Klima[2].NastMinTemp
SS1Klima2NastMinVlaznost | REAL | IOD_SS1 | SS1:.Klima[2].NastMinVlaznost
SS1Klima2NastTempProstora | REAL | IOD_SS1 | SS1:.Klima[2].NastTempProstora
SS1Klima2NastVlaznost | REAL | IOD_SS1 | SS1:.Klima[2].NastVlaznost
SS1Klima2Pritisk | REAL | IOD_SS1 | SS1:.Klima[2].Pritisk
SS1Klima2Razvlazevanje | DIGITAL | IOD_SS1 | SS1:.Klima[2].Razvlazevanje
SS1Klima2TemperaturaProstora | REAL | IOD_SS1 | SS1:.Klima[2].TemperaturaProstora
SS1Klima2VentilGretjeOdpiranje | DIGITAL | IOD_SS1 | SS1:.Klima[2].VentilGretjeOdpiranje
SS1Klima2VentilGretjeZapiranje | DIGITAL | IOD_SS1 | SS1:.Klima[2].VentilGretjeZapiranje
SS1Klima2Vlazenje | DIGITAL | IOD_SS1 | SS1:.Klima[2].Vlazenje
SS1Klima2Vlazilec_Stanja | INT | IOD_SS1 | SS1:.Klima[2].Vlazilec_Stanja | BYTE
SS1Klima2VlaznostProstora | REAL | IOD_SS1 | SS1:.Klima[2].VlaznostProstora
SS1Klima3IzhodniVentilator | DIGITAL | IOD_SS1 | SS1:.Klima[3].IzhodniVentilator
SS1Klima3Kompresor1 | DIGITAL | IOD_SS1 | SS1:.Klima[3].Kompresor1
SS1Klima3Kompresor2 | DIGITAL | IOD_SS1 | SS1:.Klima[3].Kompresor2
SS1Klima3NastMaxTemp | REAL | IOD_SS1 | SS1:.Klima[3].NastMaxTemp
SS1Klima3NastMaxVlaznost | REAL | IOD_SS1 | SS1:.Klima[3].NastMaxVlaznost
SS1Klima3NastMinTemp | REAL | IOD_SS1 | SS1:.Klima[3].NastMinTemp
SS1Klima3NastMinVlaznost | REAL | IOD_SS1 | SS1:.Klima[3].NastMinVlaznost
SS1Klima3NastTempProstora | REAL | IOD_SS1 | SS1:.Klima[3].NastTempProstora
SS1Klima3NastVlaznost | REAL | IOD_SS1 | SS1:.Klima[3].NastVlaznost
SS1Klima3Pritisk | REAL | IOD_SS1 | SS1:.Klima[3].Pritisk
SS1Klima3Razvlazevanje | DIGITAL | IOD_SS1 | SS1:.Klima[3].Razvlazevanje
SS1Klima3TemperaturaProstora | REAL | IOD_SS1 | SS1:.Klima[3].TemperaturaProstora
SS1Klima3VentilGretjeOdpiranje | DIGITAL | IOD_SS1 | SS1:.Klima[3].VentilGretjeOdpiranje
SS1Klima3VentilGretjeZapiranje | DIGITAL | IOD_SS1 | SS1:.Klima[3].VentilGretjeZapiranje
SS1Klima3Vlazenje | DIGITAL | IOD_SS1 | SS1:.Klima[3].Vlazenje
SS1Klima3Vlazilec_Stanja | INT | IOD_SS1 | SS1:.Klima[3].Vlazilec_Stanja | BYTE
SS1Klima3VlaznostProstora | REAL | IOD_SS1 | SS1:.Klima[3].VlaznostProstora
SS1KlimaError1AlarmKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].AlarmKompresor1
SS1KlimaError1AlarmKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].AlarmKompresor2
SS1KlimaError1FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].FenThermalCutout
SS1KlimaError1IzlivVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].IzlivVode
SS1KlimaError1Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].Kompresor1naMejiStevilaObrUr
SS1KlimaError1Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].Kompresor2naMejiStevilaObrUr
SS1KlimaError1Kond1FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].Kond1FenThermalCutout
SS1KlimaError1Kond2FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].Kond2FenThermalCutout
SS1KlimaError1NapakaPriPretokuVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NapakaPriPretokuVode
SS1KlimaError1NapakaPriPretokuZraka | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NapakaPriPretokuZraka
SS1KlimaError1NapakaSenzorPritiska | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NapakaSenzorPritiska
SS1KlimaError1NapakaSenzorVlaznosti | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NapakaSenzorVlaznosti
SS1KlimaError1NapakaTSTemperaturaProstora | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NapakaTSTemperaturaProstora
SS1KlimaError1NiTokaVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NiTokaVVlazilcu
SS1KlimaError1NiVodeVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NiVodeVVlazilcu
SS1KlimaError1NizekPritiskKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NizekPritiskKompresor1
SS1KlimaError1NizekPritiskKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NizekPritiskKompresor2
SS1KlimaError1NizkaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NizkaTempVProstoru
SS1KlimaError1NizkaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NizkaVlaznost
SS1KlimaError1PozarniAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].PozarniAlarm
SS1KlimaError1TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].TermZascInVisokPritiskKompr1
SS1KlimaError1TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].TermZascInVisokPritiskKompr2
SS1KlimaError1ThermalCutoutHeater1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].ThermalCutoutHeater1
SS1KlimaError1ThermalCutoutHeater2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].ThermalCutoutHeater2
SS1KlimaError1VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VentilatorNaMejiStevilaObrUr
SS1KlimaError1VisokaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VisokaTempVProstoru
SS1KlimaError1VisokaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VisokaVlaznost
SS1KlimaError1VisokPritiskVKrogu1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VisokPritiskVKrogu1
SS1KlimaError1VisokPritiskVKrogu2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VisokPritiskVKrogu2
SS1KlimaError1VisokTokVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VisokTokVVlazilcu
SS1KlimaError1VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VlazilecnaMejiStevilaObrUr
SS1KlimaError1ZamasenFilter | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].ZamasenFilter
SS1KlimaError1ZunanjiAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].ZunanjiAlarm
SS1KlimaError2AlarmKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].AlarmKompresor1
SS1KlimaError2AlarmKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].AlarmKompresor2
SS1KlimaError2FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].FenThermalCutout
SS1KlimaError2IzlivVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].IzlivVode
SS1KlimaError2Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].Kompresor1naMejiStevilaObrUr
SS1KlimaError2Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].Kompresor2naMejiStevilaObrUr
SS1KlimaError2Kond1FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].Kond1FenThermalCutout
SS1KlimaError2Kond2FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].Kond2FenThermalCutout
SS1KlimaError2NapakaPriPretokuVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NapakaPriPretokuVode
SS1KlimaError2NapakaPriPretokuZraka | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NapakaPriPretokuZraka
SS1KlimaError2NapakaSenzorPritiska | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NapakaSenzorPritiska
SS1KlimaError2NapakaSenzorVlaznosti | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NapakaSenzorVlaznosti
SS1KlimaError2NapakaTSTemperaturaProstora | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NapakaTSTemperaturaProstora
SS1KlimaError2NiTokaVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NiTokaVVlazilcu
SS1KlimaError2NiVodeVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NiVodeVVlazilcu
SS1KlimaError2NizekPritiskKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NizekPritiskKompresor1
SS1KlimaError2NizekPritiskKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NizekPritiskKompresor2
SS1KlimaError2NizkaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NizkaTempVProstoru
SS1KlimaError2NizkaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NizkaVlaznost
SS1KlimaError2PozarniAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].PozarniAlarm
SS1KlimaError2TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].TermZascInVisokPritiskKompr1
SS1KlimaError2TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].TermZascInVisokPritiskKompr2
SS1KlimaError2ThermalCutoutHeater1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].ThermalCutoutHeater1
SS1KlimaError2ThermalCutoutHeater2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].ThermalCutoutHeater2
SS1KlimaError2VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VentilatorNaMejiStevilaObrUr
SS1KlimaError2VisokaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VisokaTempVProstoru
SS1KlimaError2VisokaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VisokaVlaznost
SS1KlimaError2VisokPritiskVKrogu1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VisokPritiskVKrogu1
SS1KlimaError2VisokPritiskVKrogu2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VisokPritiskVKrogu2
SS1KlimaError2VisokTokVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VisokTokVVlazilcu
SS1KlimaError2VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VlazilecnaMejiStevilaObrUr
SS1KlimaError2ZamasenFilter | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].ZamasenFilter
SS1KlimaError2ZunanjiAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].ZunanjiAlarm
SS1KlimaError3AlarmKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].AlarmKompresor1
SS1KlimaError3AlarmKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].AlarmKompresor2
SS1KlimaError3FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].FenThermalCutout
SS1KlimaError3IzlivVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].IzlivVode
SS1KlimaError3Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].Kompresor1naMejiStevilaObrUr
SS1KlimaError3Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].Kompresor2naMejiStevilaObrUr
SS1KlimaError3Kond1FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].Kond1FenThermalCutout
SS1KlimaError3Kond2FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].Kond2FenThermalCutout
SS1KlimaError3NapakaPriPretokuVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NapakaPriPretokuVode
SS1KlimaError3NapakaPriPretokuZraka | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NapakaPriPretokuZraka
SS1KlimaError3NapakaSenzorPritiska | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NapakaSenzorPritiska
SS1KlimaError3NapakaSenzorVlaznosti | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NapakaSenzorVlaznosti
SS1KlimaError3NapakaTSTemperaturaProstora | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NapakaTSTemperaturaProstora
SS1KlimaError3NiTokaVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NiTokaVVlazilcu
SS1KlimaError3NiVodeVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NiVodeVVlazilcu
SS1KlimaError3NizekPritiskKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NizekPritiskKompresor1
SS1KlimaError3NizekPritiskKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NizekPritiskKompresor2
SS1KlimaError3NizkaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NizkaTempVProstoru
SS1KlimaError3NizkaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NizkaVlaznost
SS1KlimaError3PozarniAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].PozarniAlarm
SS1KlimaError3TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].TermZascInVisokPritiskKompr1
SS1KlimaError3TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].TermZascInVisokPritiskKompr2
SS1KlimaError3ThermalCutoutHeater1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].ThermalCutoutHeater1
SS1KlimaError3ThermalCutoutHeater2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].ThermalCutoutHeater2
SS1KlimaError3VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VentilatorNaMejiStevilaObrUr
SS1KlimaError3VisokaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VisokaTempVProstoru
SS1KlimaError3VisokaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VisokaVlaznost
SS1KlimaError3VisokPritiskVKrogu1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VisokPritiskVKrogu1
SS1KlimaError3VisokPritiskVKrogu2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VisokPritiskVKrogu2
SS1KlimaError3VisokTokVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VisokTokVVlazilcu
SS1KlimaError3VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VlazilecnaMejiStevilaObrUr
SS1KlimaError3ZamasenFilter | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].ZamasenFilter
SS1KlimaError3ZunanjiAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].ZunanjiAlarm
SS1NacDelovanjaKlime1_Avtomatsko | DIGITAL | IOD_SS1 | SS1:.NacDelovanjaKlime1_Avtomatsko
SS1NacDelovanjaKlime2_3Avtomatsko | DIGITAL | IOD_SS1 | SS1:.NacDelovanjaKlime2_3Avtomatsko
SS1NapakaSenzorTemp1 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorTemp1
SS1NapakaSenzorTemp2 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorTemp2
SS1NapakaSenzorTemp3 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorTemp3
SS1NapakaSenzorTempKontrSoba | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorTempKontrSoba
SS1NapakaSenzorTempLinkProstor | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorTempLinkProstor
SS1NapakaSenzorVlaga1 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorVlaga1
SS1NapakaSenzorVlaga2 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorVlaga2
SS1NapakaSenzorVlaga3 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorVlaga3
SS1NapakaSenzorVlagaKontrSoba | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorVlagaKontrSoba
SS1NapakaSenzorVlagaLinkProstor | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorVlagaLinkProstor
SS1NastaviCasNaKrmilniku | DIGITAL | IOD_SS1 | SS1:.NastaviCasNaKrmilniku
SS1NastavitevUreKrUspesna | DIGITAL | IOD_SS1 | SS1:.NastavitevUreKrUspesna
SS1ObratUreKlim1 | REAL | IOD_SS1 | SS1:.ObratUreKlim[1]
SS1ObratUreKlim2 | REAL | IOD_SS1 | SS1:.ObratUreKlim[2]
SS1ObratUreKlim3 | REAL | IOD_SS1 | SS1:.ObratUreKlim[3]
SS1OpozoriloBaterijaPLC | DIGITAL | IOD_SS1 | SS1:.OpozoriloBaterijaPLC
SS1PMMActiveEnergyConsumed_kWh | REAL | IOD_SS1 | SS1:.PMM.ActiveEnergyConsumed_kWh
SS1PMMActivePowerPhaseA_kW | REAL | IOD_SS1 | SS1:.PMM.ActivePowerPhaseA_kW
SS1PMMActivePowerPhaseB_kW | REAL | IOD_SS1 | SS1:.PMM.ActivePowerPhaseB_kW
SS1PMMActivePowerPhaseC_kW | REAL | IOD_SS1 | SS1:.PMM.ActivePowerPhaseC_kW
SS1PMMAlarmPhase1C01_16_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C01_16_60to80
SS1PMMAlarmPhase1C01_16_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C01_16_over80
SS1PMMAlarmPhase1C17_32_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C17_32_60to80
SS1PMMAlarmPhase1C17_32_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C17_32_over80
SS1PMMAlarmPhase1C33_42_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C33_42_60to80
SS1PMMAlarmPhase1C33_42_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C33_42_over80
SS1PMMAlarmPhase2C01_16_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C01_16_60to80
SS1PMMAlarmPhase2C01_16_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C01_16_over80
SS1PMMAlarmPhase2C17_32_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C17_32_60to80
SS1PMMAlarmPhase2C17_32_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C17_32_over80
SS1PMMAlarmPhase2C33_42_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C33_42_60to80
SS1PMMAlarmPhase2C33_42_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C33_42_over80
SS1PMMAlarmPhase3C01_16_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C01_16_60to80
SS1PMMAlarmPhase3C01_16_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C01_16_over80
SS1PMMAlarmPhase3C17_32_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C17_32_60to80
SS1PMMAlarmPhase3C17_32_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C17_32_over80
SS1PMMAlarmPhase3C33_42_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C33_42_60to80
SS1PMMAlarmPhase3C33_42_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C33_42_over80
SS1PMMAparentPowerPhaseA | REAL | IOD_SS1 | SS1:.PMM.AparentPowerPhaseA
SS1PMMAparentPowerPhaseB | REAL | IOD_SS1 | SS1:.PMM.AparentPowerPhaseB
SS1PMMAparentPowerPhaseC | REAL | IOD_SS1 | SS1:.PMM.AparentPowerPhaseC
SS1PMMAverageCurrent_A | REAL | IOD_SS1 | SS1:.PMM.AverageCurrent_A
SS1PMMAveragePhaseToNeutral_V | REAL | IOD_SS1 | SS1:.PMM.AveragePhaseToNeutral_V
SS1PMMAveragePhaseToPhase_V | REAL | IOD_SS1 | SS1:.PMM.AveragePhaseToPhase_V
SS1PMMCurrentInPhaseA_A | REAL | IOD_SS1 | SS1:.PMM.CurrentInPhaseA_A
SS1PMMCurrentInPhaseB_A | REAL | IOD_SS1 | SS1:.PMM.CurrentInPhaseB_A
SS1PMMCurrentInPhaseC_A | REAL | IOD_SS1 | SS1:.PMM.CurrentInPhaseC_A
SS1PMMFrequency_Hz | REAL | IOD_SS1 | SS1:.PMM.Frequency_Hz
SS1PMMPhase1Current10 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[10]
SS1PMMPhase1Current11 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[11]
SS1PMMPhase1Current12 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[12]
SS1PMMPhase1Current13 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[13]
SS1PMMPhase1Current14 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[14]
SS1PMMPhase1Current15 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[15]
SS1PMMPhase1Current16 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[16]
SS1PMMPhase1Current17 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[17]
SS1PMMPhase1Current18 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[18]
SS1PMMPhase1Current19 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[19]
SS1PMMPhase1Current1 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[1]
SS1PMMPhase1Current20 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[20]
SS1PMMPhase1Current21 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[21]
SS1PMMPhase1Current22 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[22]
SS1PMMPhase1Current23 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[23]
SS1PMMPhase1Current24 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[24]
SS1PMMPhase1Current25 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[25]
SS1PMMPhase1Current26 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[26]
SS1PMMPhase1Current27 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[27]
SS1PMMPhase1Current28 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[28]
SS1PMMPhase1Current29 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[29]
SS1PMMPhase1Current2 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[2]
SS1PMMPhase1Current30 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[30]
SS1PMMPhase1Current31 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[31]
SS1PMMPhase1Current32 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[32]
SS1PMMPhase1Current33 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[33]
SS1PMMPhase1Current34 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[34]
SS1PMMPhase1Current35 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[35]
SS1PMMPhase1Current36 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[36]
SS1PMMPhase1Current37 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[37]
SS1PMMPhase1Current38 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[38]
SS1PMMPhase1Current39 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[39]
SS1PMMPhase1Current3 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[3]
SS1PMMPhase1Current40 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[40]
SS1PMMPhase1Current41 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[41]
SS1PMMPhase1Current42 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[42]
SS1PMMPhase1Current4 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[4]
SS1PMMPhase1Current5 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[5]
SS1PMMPhase1Current6 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[6]
SS1PMMPhase1Current7 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[7]
SS1PMMPhase1Current8 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[8]
SS1PMMPhase1Current9 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[9]
SS1PMMPhase2Current10 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[10]
SS1PMMPhase2Current11 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[11]
SS1PMMPhase2Current12 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[12]
SS1PMMPhase2Current13 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[13]
SS1PMMPhase2Current14 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[14]
SS1PMMPhase2Current15 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[15]
SS1PMMPhase2Current16 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[16]
SS1PMMPhase2Current17 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[17]
SS1PMMPhase2Current18 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[18]
SS1PMMPhase2Current19 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[19]
SS1PMMPhase2Current1 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[1]
SS1PMMPhase2Current20 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[20]
SS1PMMPhase2Current21 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[21]
SS1PMMPhase2Current22 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[22]
SS1PMMPhase2Current23 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[23]
SS1PMMPhase2Current24 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[24]
SS1PMMPhase2Current25 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[25]
SS1PMMPhase2Current26 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[26]
SS1PMMPhase2Current27 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[27]
SS1PMMPhase2Current28 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[28]
SS1PMMPhase2Current29 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[29]
SS1PMMPhase2Current2 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[2]
SS1PMMPhase2Current30 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[30]
SS1PMMPhase2Current31 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[31]
SS1PMMPhase2Current32 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[32]
SS1PMMPhase2Current33 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[33]
SS1PMMPhase2Current34 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[34]
SS1PMMPhase2Current35 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[35]
SS1PMMPhase2Current36 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[36]
SS1PMMPhase2Current37 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[37]
SS1PMMPhase2Current38 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[38]
SS1PMMPhase2Current39 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[39]
SS1PMMPhase2Current3 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[3]
SS1PMMPhase2Current40 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[40]
SS1PMMPhase2Current41 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[41]
SS1PMMPhase2Current42 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[42]
SS1PMMPhase2Current4 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[4]
SS1PMMPhase2Current5 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[5]
SS1PMMPhase2Current6 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[6]
SS1PMMPhase2Current7 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[7]
SS1PMMPhase2Current8 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[8]
SS1PMMPhase2Current9 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[9]
SS1PMMPhase3Current10 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[10]
SS1PMMPhase3Current11 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[11]
SS1PMMPhase3Current12 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[12]
SS1PMMPhase3Current13 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[13]
SS1PMMPhase3Current14 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[14]
SS1PMMPhase3Current15 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[15]
SS1PMMPhase3Current16 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[16]
SS1PMMPhase3Current17 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[17]
SS1PMMPhase3Current18 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[18]
SS1PMMPhase3Current19 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[19]
SS1PMMPhase3Current1 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[1]
SS1PMMPhase3Current20 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[20]
SS1PMMPhase3Current21 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[21]
SS1PMMPhase3Current22 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[22]
SS1PMMPhase3Current23 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[23]
SS1PMMPhase3Current24 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[24]
SS1PMMPhase3Current25 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[25]
SS1PMMPhase3Current26 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[26]
SS1PMMPhase3Current27 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[27]
SS1PMMPhase3Current28 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[28]
SS1PMMPhase3Current29 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[29]
SS1PMMPhase3Current2 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[2]
SS1PMMPhase3Current30 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[30]
SS1PMMPhase3Current31 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[31]
SS1PMMPhase3Current32 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[32]
SS1PMMPhase3Current33 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[33]
SS1PMMPhase3Current34 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[34]
SS1PMMPhase3Current35 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[35]
SS1PMMPhase3Current36 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[36]
SS1PMMPhase3Current37 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[37]
SS1PMMPhase3Current38 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[38]
SS1PMMPhase3Current39 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[39]
SS1PMMPhase3Current3 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[3]
SS1PMMPhase3Current40 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[40]
SS1PMMPhase3Current41 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[41]
SS1PMMPhase3Current42 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[42]
SS1PMMPhase3Current4 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[4]
SS1PMMPhase3Current5 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[5]
SS1PMMPhase3Current6 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[6]
SS1PMMPhase3Current7 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[7]
SS1PMMPhase3Current8 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[8]
SS1PMMPhase3Current9 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[9]
SS1PMMPowerFactorSys | REAL | IOD_SS1 | SS1:.PMM.PowerFactorSys
SS1PMMReactiveEnergyConsumed_kVARh | REAL | IOD_SS1 | SS1:.PMM.ReactiveEnergyConsumed_kVARh
SS1PMMReactivePowerPhaseA | REAL | IOD_SS1 | SS1:.PMM.ReactivePowerPhaseA
SS1PMMReactivePowerPhaseB | REAL | IOD_SS1 | SS1:.PMM.ReactivePowerPhaseB
SS1PMMReactivePowerPhaseC | REAL | IOD_SS1 | SS1:.PMM.ReactivePowerPhaseC
SS1PMMTotalActivePower_kW | REAL | IOD_SS1 | SS1:.PMM.TotalActivePower_kW
SS1PMMTotalAparentPower_kVA | REAL | IOD_SS1 | SS1:.PMM.TotalAparentPower_kVA
SS1PMMTotalPowerFactor | REAL | IOD_SS1 | SS1:.PMM.TotalPowerFactor
SS1PMMTotalReactivePower_kVAR | REAL | IOD_SS1 | SS1:.PMM.TotalReactivePower_kVAR
SS1PMMVirA_fsys | REAL | IOD_SS1 | SS1:.PMM.VirA_fsys
SS1PMMVirA_Isys | REAL | IOD_SS1 | SS1:.PMM.VirA_Isys
SS1PMMVirA_PFsys | REAL | IOD_SS1 | SS1:.PMM.VirA_PFsys
SS1PMMVirA_Psys | REAL | IOD_SS1 | SS1:.PMM.VirA_Psys
SS1PMMVirA_Qsys | REAL | IOD_SS1 | SS1:.PMM.VirA_Qsys
SS1PMMVirA_Ssys | REAL | IOD_SS1 | SS1:.PMM.VirA_Ssys
SS1PMMVirA_Usys | REAL | IOD_SS1 | SS1:.PMM.VirA_Usys
SS1PMMVirB_fsys | REAL | IOD_SS1 | SS1:.PMM.VirB_fsys
SS1PMMVirB_Isys | REAL | IOD_SS1 | SS1:.PMM.VirB_Isys
SS1PMMVirB_PFsys | REAL | IOD_SS1 | SS1:.PMM.VirB_PFsys
SS1PMMVirB_Psys | REAL | IOD_SS1 | SS1:.PMM.VirB_Psys
SS1PMMVirB_Qsys | REAL | IOD_SS1 | SS1:.PMM.VirB_Qsys
SS1PMMVirB_Ssys | REAL | IOD_SS1 | SS1:.PMM.VirB_Ssys
SS1PMMVirB_Usys | REAL | IOD_SS1 | SS1:.PMM.VirB_Usys
SS1PMMVirBActiveEnergyConsumed_kWh | REAL | IOD_SS1 | SS1:.PMM.VirBActiveEnergyConsumed_kWh
SS1PMMVirBActivePowerPhaseA_kW | REAL | IOD_SS1 | SS1:.PMM.VirBActivePowerPhaseA_kW
SS1PMMVirBActivePowerPhaseB_kW | REAL | IOD_SS1 | SS1:.PMM.VirBActivePowerPhaseB_kW
SS1PMMVirBActivePowerPhaseC_kW | REAL | IOD_SS1 | SS1:.PMM.VirBActivePowerPhaseC_kW
SS1PMMVirBAparentPowerPhaseA | REAL | IOD_SS1 | SS1:.PMM.VirBAparentPowerPhaseA
SS1PMMVirBAparentPowerPhaseB | REAL | IOD_SS1 | SS1:.PMM.VirBAparentPowerPhaseB
SS1PMMVirBAparentPowerPhaseC | REAL | IOD_SS1 | SS1:.PMM.VirBAparentPowerPhaseC
SS1PMMVirBAverageCurrent_A | REAL | IOD_SS1 | SS1:.PMM.VirBAverageCurrent_A
SS1PMMVirBAveragePhaseToNeutral_V | REAL | IOD_SS1 | SS1:.PMM.VirBAveragePhaseToNeutral_V
SS1PMMVirBAveragePhaseToPhase_V | REAL | IOD_SS1 | SS1:.PMM.VirBAveragePhaseToPhase_V
SS1PMMVirBCurrentInPhaseA_A | REAL | IOD_SS1 | SS1:.PMM.VirBCurrentInPhaseA_A
SS1PMMVirBCurrentInPhaseB_A | REAL | IOD_SS1 | SS1:.PMM.VirBCurrentInPhaseB_A
SS1PMMVirBCurrentInPhaseC_A | REAL | IOD_SS1 | SS1:.PMM.VirBCurrentInPhaseC_A
SS1PMMVirBFrequency_Hz | REAL | IOD_SS1 | SS1:.PMM.VirBFrequency_Hz
SS1PMMVirBPowerFactorSys | REAL | IOD_SS1 | SS1:.PMM.VirBPowerFactorSys
SS1PMMVirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS1 | SS1:.PMM.VirBReactiveEnergyConsumed_kWh
SS1PMMVirBReactivePowerPhaseA | REAL | IOD_SS1 | SS1:.PMM.VirBReactivePowerPhaseA
SS1PMMVirBReactivePowerPhaseB | REAL | IOD_SS1 | SS1:.PMM.VirBReactivePowerPhaseB
SS1PMMVirBReactivePowerPhaseC | REAL | IOD_SS1 | SS1:.PMM.VirBReactivePowerPhaseC
SS1PMMVirBTotalActivePower_kW | REAL | IOD_SS1 | SS1:.PMM.VirBTotalActivePower_kW
SS1PMMVirBTotalAparentPower_kVA | REAL | IOD_SS1 | SS1:.PMM.VirBTotalAparentPower_kVA
SS1PMMVirBTotalPowerFactor | REAL | IOD_SS1 | SS1:.PMM.VirBTotalPowerFactor
SS1PMMVirBTotalReactivePower_kVAR | REAL | IOD_SS1 | SS1:.PMM.VirBTotalReactivePower_kVAR
SS1PMMVirBVoltageBetweenPhaseAB_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseAB_V
SS1PMMVirBVoltageBetweenPhaseAN_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseAN_V
SS1PMMVirBVoltageBetweenPhaseBC_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseBC_V
SS1PMMVirBVoltageBetweenPhaseBN_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseBN_V
SS1PMMVirBVoltageBetweenPhaseCA_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseCA_V
SS1PMMVirBVoltageBetweenPhaseCN_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseCN_V
SS1PMMVoltageBetweenPhaseAB_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseAB_V
SS1PMMVoltageBetweenPhaseAN_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseAN_V
SS1PMMVoltageBetweenPhaseBC_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseBC_V
SS1PMMVoltageBetweenPhaseBN_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseBN_V
SS1PMMVoltageBetweenPhaseCA_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseCA_V
SS1PMMVoltageBetweenPhaseCN_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseCN_V
SS1PMM1OverCurrentBetw1 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentBetw[1]
SS1PMM1OverCurrentBetw2 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentBetw[2]
SS1PMM1OverCurrentBetw3 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentBetw[3]
SS1PMM1OverCurrentOver1 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentOver[1]
SS1PMM1OverCurrentOver2 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentOver[2]
SS1PMM1OverCurrentOver3 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentOver[3]
SS1PMM1OverVoltage | DIGITAL | IOD_SS1 | SS1:.PMM1OverVoltage
SS1RocniVklopKlima1 | DIGITAL | IOD_SS1 | SS1:.RocniVklopKlima1
SS1RocniVklopKlima2 | DIGITAL | IOD_SS1 | SS1:.RocniVklopKlima2
SS1RocniVklopKlima3 | DIGITAL | IOD_SS1 | SS1:.RocniVklopKlima3
SS1SinhronizacijaPanelOK | DIGITAL | IOD_SS1 | SS1:.SinhronizacijaPanelOK
SS1SinhronizirajCas_Panel | DIGITAL | IOD_SS1 | SS1:.SinhronizirajCas_Panel
SS1SKTemp1 | REAL | IOD_SS1 | SS1:.SKTemp1
SS1SKTemp2 | REAL | IOD_SS1 | SS1:.SKTemp2
SS1SKTemp3 | REAL | IOD_SS1 | SS1:.SKTemp3
SS1SKTempKontrSoba | REAL | IOD_SS1 | SS1:.SKTempKontrSoba
SS1SKTempLinkProstor | REAL | IOD_SS1 | SS1:.SKTempLinkProstor
SS1SKTempServSoba1Povpr | REAL | IOD_SS1 | SS1:.SKTempServSoba1Povpr
SS1SkupneNapakeNaprav_Klima1 | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_Klima1
SS1SkupneNapakeNaprav_Klima2 | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_Klima2
SS1SkupneNapakeNaprav_Klima3 | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_Klima3
SS1SkupneNapakeNaprav_Komunikacija | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_Komunikacija
SS1SkupneNapakeNaprav_PMMVirA | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_PMMVirA
SS1SkupneNapakeNaprav_PMMVirB | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_PMMVirB
SS1SkupneNapakeNaprav_PMMVirBVirA | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_PMMVirBVirA
SS1SkupneNapakeNaprav_TempVlaga | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_TempVlaga
SS1SKVlaga1 | REAL | IOD_SS1 | SS1:.SKVlaga1
SS1SKVlaga2 | REAL | IOD_SS1 | SS1:.SKVlaga2
SS1SKVlaga3 | REAL | IOD_SS1 | SS1:.SKVlaga3
SS1SKVlagaKontrSoba | REAL | IOD_SS1 | SS1:.SKVlagaKontrSoba
SS1SKVlagaLinkProstor | REAL | IOD_SS1 | SS1:.SKVlagaLinkProstor
SS1StanjeKlimat1_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeKlimat1_Delovanje
SS1StanjeKlimat2_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeKlimat2_Delovanje
SS1StanjeKlimat3_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeKlimat3_Delovanje
SS1StanjeSP1_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeSP1_Delovanje
SS1StanjeSP2_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeSP2_Delovanje
SS1StanjeSP3_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeSP3_Delovanje
SS1StanjeSP4_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeSP4_Delovanje
SS1StanjeSP5_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeSP5_Delovanje
SS1StanjeUPSKrmOmara_BaterijskiNacin | DIGITAL | IOD_SS1 | SS1:.StanjeUPSKrmOmara_BaterijskiNacin
SS1StanjeUPSKrmOmara_Polnenje | DIGITAL | IOD_SS1 | SS1:.StanjeUPSKrmOmara_Polnenje
SS1StUrZaPreklopKlim | INT | IOD_SS1 | SS1:.StUrZaPreklopKlim
SS1TempZaAlarmTIA123 | REAL | IOD_SS1 | SS1:.TempZaAlarmTIA123
SS1TempZaAlarmTIA4 | REAL | IOD_SS1 | SS1:.TempZaAlarmTIA4
SS1TempZaAlarmTIA5 | REAL | IOD_SS1 | SS1:.TempZaAlarmTIA5
SS1TempZaVklopObehKlim | REAL | IOD_SS1 | SS1:.TempZaVklopObehKlim
SS1UPSstatus_Prikaz_PanelSCADA | INT | IOD_SS1 | SS1:.UPSstatus_Prikaz_PanelSCADA | BYTE
SS1UserCurrentLevel | INT | IOD_SS1 | SS1:.UserCurrentLevel | BYTE
SS1UserLoggedIn | DIGITAL | IOD_SS1 | SS1:.UserLoggedIn
SS1UserName | STRING | IOD_SS1 | SS1:.UserName
SS1XVH_AlarmOn | DIGITAL | IOD_SS1 | SS1:.XVH_AlarmOn
SS1Klimat1_Vklop | DIGITAL | IOD_SS1 | SS1:.Klimat1_Vklop
SS1Klimat2_Vklop | DIGITAL | IOD_SS1 | SS1:.Klimat2_Vklop
SS1Klimat3_Vklop | DIGITAL | IOD_SS1 | SS1:.Klimat3_Vklop
SS1ErrCommScada2 | DIGITAL | IOD_SS1 | SS1:.ErrCommScada2
SS1ComSCADA2 | DIGITAL | IOD_SS1 | SS1:.ComSCADA2
SS1ComSCADA3 | DIGITAL | IOD_SS1 | SS1:.ComSCADA3
SS1kom_nast_cas_izpada | UINT | IOD_SS1 | SS1:.kom_nast_cas_izpada

## variable_2
SS1AlarmKlimat1_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmKlimat1_Napaka
SS1AlarmKlimat2_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmKlimat2_Napaka
SS1AlarmKlimat3_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmKlimat3_Napaka
SS1AlarmLAH1_RazlitjeVode | DIGITAL | IOD_SS1 | SS1:.AlarmLAH1_RazlitjeVode
SS1AlarmLAH2_RazlitjeVode | DIGITAL | IOD_SS1 | SS1:.AlarmLAH2_RazlitjeVode
SS1AlarmSinhronizacijaNOK | DIGITAL | IOD_SS1 | SS1:.AlarmSinhronizacijaNOK
SS1AlarmSP1_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmSP1_Napaka
SS1AlarmSP2_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmSP2_Napaka
SS1AlarmSP3_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmSP3_Napaka
SS1AlarmSP4_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmSP4_Napaka
SS1AlarmSP5_Napaka | DIGITAL | IOD_SS1 | SS1:.AlarmSP5_Napaka
SS1AlarmTempTIA123Previsoka | DIGITAL | IOD_SS1 | SS1:.AlarmTempTIA123Previsoka
SS1AlarmTempTIA4Previsoka | DIGITAL | IOD_SS1 | SS1:.AlarmTempTIA4Previsoka
SS1AlarmTempTIA5Previsoka | DIGITAL | IOD_SS1 | SS1:.AlarmTempTIA5Previsoka
SS1AlarmTSTempPrevisoka | DIGITAL | IOD_SS1 | SS1:.AlarmTSTempPrevisoka
SS1AlarmUPSKrmOmara_Alarm | DIGITAL | IOD_SS1 | SS1:.AlarmUPSKrmOmara_Alarm
SS1ComSCADA | DIGITAL | IOD_SS1 | SS1:.ComSCADA
SS1ComSCADA1 | DIGITAL | IOD_SS1 | SS1:.ComSCADA1
SS1ErrComKlima1 | DIGITAL | IOD_SS1 | SS1:.ErrComKlima[1]
SS1ErrComKlima2 | DIGITAL | IOD_SS1 | SS1:.ErrComKlima[2]
SS1ErrComKlima3 | DIGITAL | IOD_SS1 | SS1:.ErrComKlima[3]
SS1ErrCommScada | DIGITAL | IOD_SS1 | SS1:.ErrCommScada
SS1ErrComPanelPLC | DIGITAL | IOD_SS1 | SS1:.ErrComPanelPLC
SS1ErrComPMM | DIGITAL | IOD_SS1 | SS1:.ErrComPMM
SS1ErrComPort2 | DIGITAL | IOD_SS1 | SS1:.ErrComPort2
SS1Klima1_Onemogocena | DIGITAL | IOD_SS1 | SS1:.Klima1_Onemogocena
SS1Klima2_Onemogocena | DIGITAL | IOD_SS1 | SS1:.Klima2_Onemogocena
SS1Klima3_Onemogocena | DIGITAL | IOD_SS1 | SS1:.Klima3_Onemogocena
SS1Klima1IzhodniVentilator | DIGITAL | IOD_SS1 | SS1:.Klima[1].IzhodniVentilator
SS1Klima1Kompresor1 | DIGITAL | IOD_SS1 | SS1:.Klima[1].Kompresor1
SS1Klima1Kompresor2 | DIGITAL | IOD_SS1 | SS1:.Klima[1].Kompresor2
SS1Klima1Razvlazevanje | DIGITAL | IOD_SS1 | SS1:.Klima[1].Razvlazevanje
SS1Klima1VentilGretjeOdpiranje | DIGITAL | IOD_SS1 | SS1:.Klima[1].VentilGretjeOdpiranje
SS1Klima1VentilGretjeZapiranje | DIGITAL | IOD_SS1 | SS1:.Klima[1].VentilGretjeZapiranje
SS1Klima1Vlazenje | DIGITAL | IOD_SS1 | SS1:.Klima[1].Vlazenje
SS1Klima2IzhodniVentilator | DIGITAL | IOD_SS1 | SS1:.Klima[2].IzhodniVentilator
SS1Klima2Kompresor1 | DIGITAL | IOD_SS1 | SS1:.Klima[2].Kompresor1
SS1Klima2Kompresor2 | DIGITAL | IOD_SS1 | SS1:.Klima[2].Kompresor2
SS1Klima2Razvlazevanje | DIGITAL | IOD_SS1 | SS1:.Klima[2].Razvlazevanje
SS1Klima2VentilGretjeOdpiranje | DIGITAL | IOD_SS1 | SS1:.Klima[2].VentilGretjeOdpiranje
SS1Klima2VentilGretjeZapiranje | DIGITAL | IOD_SS1 | SS1:.Klima[2].VentilGretjeZapiranje
SS1Klima2Vlazenje | DIGITAL | IOD_SS1 | SS1:.Klima[2].Vlazenje
SS1Klima3IzhodniVentilator | DIGITAL | IOD_SS1 | SS1:.Klima[3].IzhodniVentilator
SS1Klima3Kompresor1 | DIGITAL | IOD_SS1 | SS1:.Klima[3].Kompresor1
SS1Klima3Kompresor2 | DIGITAL | IOD_SS1 | SS1:.Klima[3].Kompresor2
SS1Klima3Razvlazevanje | DIGITAL | IOD_SS1 | SS1:.Klima[3].Razvlazevanje
SS1Klima3VentilGretjeOdpiranje | DIGITAL | IOD_SS1 | SS1:.Klima[3].VentilGretjeOdpiranje
SS1Klima3VentilGretjeZapiranje | DIGITAL | IOD_SS1 | SS1:.Klima[3].VentilGretjeZapiranje
SS1Klima3Vlazenje | DIGITAL | IOD_SS1 | SS1:.Klima[3].Vlazenje
SS1KlimaError1AlarmKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].AlarmKompresor1
SS1KlimaError1AlarmKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].AlarmKompresor2
SS1KlimaError1FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].FenThermalCutout
SS1KlimaError1IzlivVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].IzlivVode
SS1KlimaError1Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].Kompresor1naMejiStevilaObrUr
SS1KlimaError1Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].Kompresor2naMejiStevilaObrUr
SS1KlimaError1Kond1FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].Kond1FenThermalCutout
SS1KlimaError1Kond2FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].Kond2FenThermalCutout
SS1KlimaError1NapakaPriPretokuVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NapakaPriPretokuVode
SS1KlimaError1NapakaPriPretokuZraka | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NapakaPriPretokuZraka
SS1KlimaError1NapakaSenzorPritiska | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NapakaSenzorPritiska
SS1KlimaError1NapakaSenzorVlaznosti | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NapakaSenzorVlaznosti
SS1KlimaError1NapakaTSTemperaturaProstora | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NapakaTSTemperaturaProstora
SS1KlimaError1NiTokaVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NiTokaVVlazilcu
SS1KlimaError1NiVodeVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NiVodeVVlazilcu
SS1KlimaError1NizekPritiskKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NizekPritiskKompresor1
SS1KlimaError1NizekPritiskKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NizekPritiskKompresor2
SS1KlimaError1NizkaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NizkaTempVProstoru
SS1KlimaError1NizkaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].NizkaVlaznost
SS1KlimaError1PozarniAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].PozarniAlarm
SS1KlimaError1TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].TermZascInVisokPritiskKompr1
SS1KlimaError1TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].TermZascInVisokPritiskKompr2
SS1KlimaError1ThermalCutoutHeater1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].ThermalCutoutHeater1
SS1KlimaError1ThermalCutoutHeater2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].ThermalCutoutHeater2
SS1KlimaError1VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VentilatorNaMejiStevilaObrUr
SS1KlimaError1VisokaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VisokaTempVProstoru
SS1KlimaError1VisokaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VisokaVlaznost
SS1KlimaError1VisokPritiskVKrogu1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VisokPritiskVKrogu1
SS1KlimaError1VisokPritiskVKrogu2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VisokPritiskVKrogu2
SS1KlimaError1VisokTokVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VisokTokVVlazilcu
SS1KlimaError1VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].VlazilecnaMejiStevilaObrUr
SS1KlimaError1ZamasenFilter | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].ZamasenFilter
SS1KlimaError1ZunanjiAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[1].ZunanjiAlarm
SS1KlimaError2AlarmKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].AlarmKompresor1
SS1KlimaError2AlarmKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].AlarmKompresor2
SS1KlimaError2FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].FenThermalCutout
SS1KlimaError2IzlivVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].IzlivVode
SS1KlimaError2Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].Kompresor1naMejiStevilaObrUr
SS1KlimaError2Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].Kompresor2naMejiStevilaObrUr
SS1KlimaError2Kond1FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].Kond1FenThermalCutout
SS1KlimaError2Kond2FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].Kond2FenThermalCutout
SS1KlimaError2NapakaPriPretokuVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NapakaPriPretokuVode
SS1KlimaError2NapakaPriPretokuZraka | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NapakaPriPretokuZraka
SS1KlimaError2NapakaSenzorPritiska | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NapakaSenzorPritiska
SS1KlimaError2NapakaSenzorVlaznosti | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NapakaSenzorVlaznosti
SS1KlimaError2NapakaTSTemperaturaProstora | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NapakaTSTemperaturaProstora
SS1KlimaError2NiTokaVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NiTokaVVlazilcu
SS1KlimaError2NiVodeVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NiVodeVVlazilcu
SS1KlimaError2NizekPritiskKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NizekPritiskKompresor1
SS1KlimaError2NizekPritiskKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NizekPritiskKompresor2
SS1KlimaError2NizkaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NizkaTempVProstoru
SS1KlimaError2NizkaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].NizkaVlaznost
SS1KlimaError2PozarniAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].PozarniAlarm
SS1KlimaError2TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].TermZascInVisokPritiskKompr1
SS1KlimaError2TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].TermZascInVisokPritiskKompr2
SS1KlimaError2ThermalCutoutHeater1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].ThermalCutoutHeater1
SS1KlimaError2ThermalCutoutHeater2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].ThermalCutoutHeater2
SS1KlimaError2VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VentilatorNaMejiStevilaObrUr
SS1KlimaError2VisokaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VisokaTempVProstoru
SS1KlimaError2VisokaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VisokaVlaznost
SS1KlimaError2VisokPritiskVKrogu1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VisokPritiskVKrogu1
SS1KlimaError2VisokPritiskVKrogu2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VisokPritiskVKrogu2
SS1KlimaError2VisokTokVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VisokTokVVlazilcu
SS1KlimaError2VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].VlazilecnaMejiStevilaObrUr
SS1KlimaError2ZamasenFilter | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].ZamasenFilter
SS1KlimaError2ZunanjiAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[2].ZunanjiAlarm
SS1KlimaError3AlarmKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].AlarmKompresor1
SS1KlimaError3AlarmKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].AlarmKompresor2
SS1KlimaError3FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].FenThermalCutout
SS1KlimaError3IzlivVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].IzlivVode
SS1KlimaError3Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].Kompresor1naMejiStevilaObrUr
SS1KlimaError3Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].Kompresor2naMejiStevilaObrUr
SS1KlimaError3Kond1FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].Kond1FenThermalCutout
SS1KlimaError3Kond2FenThermalCutout | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].Kond2FenThermalCutout
SS1KlimaError3NapakaPriPretokuVode | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NapakaPriPretokuVode
SS1KlimaError3NapakaPriPretokuZraka | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NapakaPriPretokuZraka
SS1KlimaError3NapakaSenzorPritiska | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NapakaSenzorPritiska
SS1KlimaError3NapakaSenzorVlaznosti | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NapakaSenzorVlaznosti
SS1KlimaError3NapakaTSTemperaturaProstora | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NapakaTSTemperaturaProstora
SS1KlimaError3NiTokaVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NiTokaVVlazilcu
SS1KlimaError3NiVodeVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NiVodeVVlazilcu
SS1KlimaError3NizekPritiskKompresor1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NizekPritiskKompresor1
SS1KlimaError3NizekPritiskKompresor2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NizekPritiskKompresor2
SS1KlimaError3NizkaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NizkaTempVProstoru
SS1KlimaError3NizkaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].NizkaVlaznost
SS1KlimaError3PozarniAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].PozarniAlarm
SS1KlimaError3TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].TermZascInVisokPritiskKompr1
SS1KlimaError3TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].TermZascInVisokPritiskKompr2
SS1KlimaError3ThermalCutoutHeater1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].ThermalCutoutHeater1
SS1KlimaError3ThermalCutoutHeater2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].ThermalCutoutHeater2
SS1KlimaError3VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VentilatorNaMejiStevilaObrUr
SS1KlimaError3VisokaTempVProstoru | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VisokaTempVProstoru
SS1KlimaError3VisokaVlaznost | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VisokaVlaznost
SS1KlimaError3VisokPritiskVKrogu1 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VisokPritiskVKrogu1
SS1KlimaError3VisokPritiskVKrogu2 | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VisokPritiskVKrogu2
SS1KlimaError3VisokTokVVlazilcu | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VisokTokVVlazilcu
SS1KlimaError3VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].VlazilecnaMejiStevilaObrUr
SS1KlimaError3ZamasenFilter | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].ZamasenFilter
SS1KlimaError3ZunanjiAlarm | DIGITAL | IOD_SS1 | SS1:.KlimaError[3].ZunanjiAlarm
SS1NacDelovanjaKlime1_Avtomatsko | DIGITAL | IOD_SS1 | SS1:.NacDelovanjaKlime1_Avtomatsko
SS1NacDelovanjaKlime2_3Avtomatsko | DIGITAL | IOD_SS1 | SS1:.NacDelovanjaKlime2_3Avtomatsko
SS1NapakaSenzorTemp1 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorTemp1
SS1NapakaSenzorTemp2 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorTemp2
SS1NapakaSenzorTemp3 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorTemp3
SS1NapakaSenzorTempKontrSoba | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorTempKontrSoba
SS1NapakaSenzorTempLinkProstor | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorTempLinkProstor
SS1NapakaSenzorVlaga1 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorVlaga1
SS1NapakaSenzorVlaga2 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorVlaga2
SS1NapakaSenzorVlaga3 | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorVlaga3
SS1NapakaSenzorVlagaKontrSoba | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorVlagaKontrSoba
SS1NapakaSenzorVlagaLinkProstor | DIGITAL | IOD_SS1 | SS1:.NapakaSenzorVlagaLinkProstor
SS1NastaviCasNaKrmilniku | DIGITAL | IOD_SS1 | SS1:.NastaviCasNaKrmilniku
SS1NastavitevUreKrUspesna | DIGITAL | IOD_SS1 | SS1:.NastavitevUreKrUspesna
SS1OpozoriloBaterijaPLC | DIGITAL | IOD_SS1 | SS1:.OpozoriloBaterijaPLC
SS1PMM1OverCurrentBetw1 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentBetw[1]
SS1PMM1OverCurrentBetw2 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentBetw[2]
SS1PMM1OverCurrentBetw3 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentBetw[3]
SS1PMM1OverCurrentOver1 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentOver[1]
SS1PMM1OverCurrentOver2 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentOver[2]
SS1PMM1OverCurrentOver3 | DIGITAL | IOD_SS1 | SS1:.PMM1OverCurrentOver[3]
SS1PMM1OverVoltage | DIGITAL | IOD_SS1 | SS1:.PMM1OverVoltage
SS1RocniVklopKlima1 | DIGITAL | IOD_SS1 | SS1:.RocniVklopKlima1
SS1RocniVklopKlima2 | DIGITAL | IOD_SS1 | SS1:.RocniVklopKlima2
SS1RocniVklopKlima3 | DIGITAL | IOD_SS1 | SS1:.RocniVklopKlima3
SS1SinhronizacijaPanelOK | DIGITAL | IOD_SS1 | SS1:.SinhronizacijaPanelOK
SS1SinhronizirajCas_Panel | DIGITAL | IOD_SS1 | SS1:.SinhronizirajCas_Panel
SS1SkupneNapakeNaprav_Klima1 | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_Klima1
SS1SkupneNapakeNaprav_Klima2 | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_Klima2
SS1SkupneNapakeNaprav_Klima3 | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_Klima3
SS1SkupneNapakeNaprav_Komunikacija | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_Komunikacija
SS1SkupneNapakeNaprav_PMMVirA | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_PMMVirA
SS1SkupneNapakeNaprav_PMMVirB | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_PMMVirB
SS1SkupneNapakeNaprav_PMMVirBVirA | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_PMMVirBVirA
SS1SkupneNapakeNaprav_TempVlaga | DIGITAL | IOD_SS1 | SS1:.SkupneNapakeNaprav_TempVlaga
SS1StanjeKlimat1_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeKlimat1_Delovanje
SS1StanjeKlimat2_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeKlimat2_Delovanje
SS1StanjeKlimat3_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeKlimat3_Delovanje
SS1StanjeSP1_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeSP1_Delovanje
SS1StanjeSP2_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeSP2_Delovanje
SS1StanjeSP3_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeSP3_Delovanje
SS1StanjeSP4_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeSP4_Delovanje
SS1StanjeSP5_Delovanje | DIGITAL | IOD_SS1 | SS1:.StanjeSP5_Delovanje
SS1StanjeUPSKrmOmara_BaterijskiNacin | DIGITAL | IOD_SS1 | SS1:.StanjeUPSKrmOmara_BaterijskiNacin
SS1StanjeUPSKrmOmara_Polnenje | DIGITAL | IOD_SS1 | SS1:.StanjeUPSKrmOmara_Polnenje
SS1UserLoggedIn | DIGITAL | IOD_SS1 | SS1:.UserLoggedIn
SS1XVH_AlarmOn | DIGITAL | IOD_SS1 | SS1:.XVH_AlarmOn
SS1Klimat1_Vklop | DIGITAL | IOD_SS1 | SS1:.Klimat1_Vklop
SS1Klimat2_Vklop | DIGITAL | IOD_SS1 | SS1:.Klimat2_Vklop
SS1Klimat3_Vklop | DIGITAL | IOD_SS1 | SS1:.Klimat3_Vklop
SS1ErrCommScada2 | DIGITAL | IOD_SS1 | SS1:.ErrCommScada2
SS1ComSCADA2 | DIGITAL | IOD_SS1 | SS1:.ComSCADA2
SS1ComSCADA3 | DIGITAL | IOD_SS1 | SS1:.ComSCADA3
SS1DatumCasDan | INT | IOD_SS1 | SS1:.DatumCas.Dan | BYTE
SS1DatumCasLeto | INT | IOD_SS1 | SS1:.DatumCas.Leto | BYTE
SS1DatumCasLeto2 | INT | IOD_SS1 | SS1:.DatumCas.Leto2
SS1DatumCasMesec | INT | IOD_SS1 | SS1:.DatumCas.Mesec | BYTE
SS1DatumCasMinuta | INT | IOD_SS1 | SS1:.DatumCas.Minuta | BYTE
SS1DatumCasSekunda | INT | IOD_SS1 | SS1:.DatumCas.Sekunda | BYTE
SS1DatumCasUra | INT | IOD_SS1 | SS1:.DatumCas.Ura | BYTE
SS1Klima1Vlazilec_Stanja | INT | IOD_SS1 | SS1:.Klima[1].Vlazilec_Stanja | BYTE
SS1Klima2Vlazilec_Stanja | INT | IOD_SS1 | SS1:.Klima[2].Vlazilec_Stanja | BYTE
SS1Klima3Vlazilec_Stanja | INT | IOD_SS1 | SS1:.Klima[3].Vlazilec_Stanja | BYTE
SS1StUrZaPreklopKlim | INT | IOD_SS1 | SS1:.StUrZaPreklopKlim
SS1UPSstatus_Prikaz_PanelSCADA | INT | IOD_SS1 | SS1:.UPSstatus_Prikaz_PanelSCADA | BYTE
SS1UserCurrentLevel | INT | IOD_SS1 | SS1:.UserCurrentLevel | BYTE
SS1AktualniSetPointTemp | REAL | IOD_SS1 | SS1:.AktualniSetPointTemp
SS1AktualniSetPointVlaga | REAL | IOD_SS1 | SS1:.AktualniSetPointVlaga
SS1Klima1NastMaxTemp | REAL | IOD_SS1 | SS1:.Klima[1].NastMaxTemp
SS1Klima1NastMaxVlaznost | REAL | IOD_SS1 | SS1:.Klima[1].NastMaxVlaznost
SS1Klima1NastMinTemp | REAL | IOD_SS1 | SS1:.Klima[1].NastMinTemp
SS1Klima1NastMinVlaznost | REAL | IOD_SS1 | SS1:.Klima[1].NastMinVlaznost
SS1Klima1NastTempProstora | REAL | IOD_SS1 | SS1:.Klima[1].NastTempProstora
SS1Klima1NastVlaznost | REAL | IOD_SS1 | SS1:.Klima[1].NastVlaznost
SS1Klima1Pritisk | REAL | IOD_SS1 | SS1:.Klima[1].Pritisk
SS1Klima1TemperaturaProstora | REAL | IOD_SS1 | SS1:.Klima[1].TemperaturaProstora
SS1Klima1VlaznostProstora | REAL | IOD_SS1 | SS1:.Klima[1].VlaznostProstora
SS1Klima2NastMaxTemp | REAL | IOD_SS1 | SS1:.Klima[2].NastMaxTemp
SS1Klima2NastMaxVlaznost | REAL | IOD_SS1 | SS1:.Klima[2].NastMaxVlaznost
SS1Klima2NastMinTemp | REAL | IOD_SS1 | SS1:.Klima[2].NastMinTemp
SS1Klima2NastMinVlaznost | REAL | IOD_SS1 | SS1:.Klima[2].NastMinVlaznost
SS1Klima2NastTempProstora | REAL | IOD_SS1 | SS1:.Klima[2].NastTempProstora
SS1Klima2NastVlaznost | REAL | IOD_SS1 | SS1:.Klima[2].NastVlaznost
SS1Klima2Pritisk | REAL | IOD_SS1 | SS1:.Klima[2].Pritisk
SS1Klima2TemperaturaProstora | REAL | IOD_SS1 | SS1:.Klima[2].TemperaturaProstora
SS1Klima2VlaznostProstora | REAL | IOD_SS1 | SS1:.Klima[2].VlaznostProstora
SS1Klima3NastMaxTemp | REAL | IOD_SS1 | SS1:.Klima[3].NastMaxTemp
SS1Klima3NastMaxVlaznost | REAL | IOD_SS1 | SS1:.Klima[3].NastMaxVlaznost
SS1Klima3NastMinTemp | REAL | IOD_SS1 | SS1:.Klima[3].NastMinTemp
SS1Klima3NastMinVlaznost | REAL | IOD_SS1 | SS1:.Klima[3].NastMinVlaznost
SS1Klima3NastTempProstora | REAL | IOD_SS1 | SS1:.Klima[3].NastTempProstora
SS1Klima3NastVlaznost | REAL | IOD_SS1 | SS1:.Klima[3].NastVlaznost
SS1Klima3Pritisk | REAL | IOD_SS1 | SS1:.Klima[3].Pritisk
SS1Klima3TemperaturaProstora | REAL | IOD_SS1 | SS1:.Klima[3].TemperaturaProstora
SS1Klima3VlaznostProstora | REAL | IOD_SS1 | SS1:.Klima[3].VlaznostProstora
SS1ObratUreKlim1 | REAL | IOD_SS1 | SS1:.ObratUreKlim[1]
SS1ObratUreKlim2 | REAL | IOD_SS1 | SS1:.ObratUreKlim[2]
SS1ObratUreKlim3 | REAL | IOD_SS1 | SS1:.ObratUreKlim[3]
SS1PMMActiveEnergyConsumed_kWh | REAL | IOD_SS1 | SS1:.PMM.ActiveEnergyConsumed_kWh
SS1PMMActivePowerPhaseA_kW | REAL | IOD_SS1 | SS1:.PMM.ActivePowerPhaseA_kW
SS1PMMActivePowerPhaseB_kW | REAL | IOD_SS1 | SS1:.PMM.ActivePowerPhaseB_kW
SS1PMMActivePowerPhaseC_kW | REAL | IOD_SS1 | SS1:.PMM.ActivePowerPhaseC_kW
SS1PMMAparentPowerPhaseA | REAL | IOD_SS1 | SS1:.PMM.AparentPowerPhaseA
SS1PMMAparentPowerPhaseB | REAL | IOD_SS1 | SS1:.PMM.AparentPowerPhaseB
SS1PMMAparentPowerPhaseC | REAL | IOD_SS1 | SS1:.PMM.AparentPowerPhaseC
SS1PMMAverageCurrent_A | REAL | IOD_SS1 | SS1:.PMM.AverageCurrent_A
SS1PMMAveragePhaseToNeutral_V | REAL | IOD_SS1 | SS1:.PMM.AveragePhaseToNeutral_V
SS1PMMAveragePhaseToPhase_V | REAL | IOD_SS1 | SS1:.PMM.AveragePhaseToPhase_V
SS1PMMCurrentInPhaseA_A | REAL | IOD_SS1 | SS1:.PMM.CurrentInPhaseA_A
SS1PMMCurrentInPhaseB_A | REAL | IOD_SS1 | SS1:.PMM.CurrentInPhaseB_A
SS1PMMCurrentInPhaseC_A | REAL | IOD_SS1 | SS1:.PMM.CurrentInPhaseC_A
SS1PMMFrequency_Hz | REAL | IOD_SS1 | SS1:.PMM.Frequency_Hz
SS1PMMPhase1Current10 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[10]
SS1PMMPhase1Current11 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[11]
SS1PMMPhase1Current12 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[12]
SS1PMMPhase1Current13 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[13]
SS1PMMPhase1Current14 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[14]
SS1PMMPhase1Current15 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[15]
SS1PMMPhase1Current16 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[16]
SS1PMMPhase1Current17 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[17]
SS1PMMPhase1Current18 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[18]
SS1PMMPhase1Current19 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[19]
SS1PMMPhase1Current1 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[1]
SS1PMMPhase1Current20 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[20]
SS1PMMPhase1Current21 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[21]
SS1PMMPhase1Current22 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[22]
SS1PMMPhase1Current23 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[23]
SS1PMMPhase1Current24 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[24]
SS1PMMPhase1Current25 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[25]
SS1PMMPhase1Current26 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[26]
SS1PMMPhase1Current27 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[27]
SS1PMMPhase1Current28 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[28]
SS1PMMPhase1Current29 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[29]
SS1PMMPhase1Current2 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[2]
SS1PMMPhase1Current30 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[30]
SS1PMMPhase1Current31 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[31]
SS1PMMPhase1Current32 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[32]
SS1PMMPhase1Current33 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[33]
SS1PMMPhase1Current34 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[34]
SS1PMMPhase1Current35 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[35]
SS1PMMPhase1Current36 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[36]
SS1PMMPhase1Current37 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[37]
SS1PMMPhase1Current38 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[38]
SS1PMMPhase1Current39 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[39]
SS1PMMPhase1Current3 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[3]
SS1PMMPhase1Current40 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[40]
SS1PMMPhase1Current41 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[41]
SS1PMMPhase1Current42 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[42]
SS1PMMPhase1Current4 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[4]
SS1PMMPhase1Current5 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[5]
SS1PMMPhase1Current6 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[6]
SS1PMMPhase1Current7 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[7]
SS1PMMPhase1Current8 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[8]
SS1PMMPhase1Current9 | REAL | IOD_SS1 | SS1:.PMM.Phase[1].Current[9]
SS1PMMPhase2Current10 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[10]
SS1PMMPhase2Current11 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[11]
SS1PMMPhase2Current12 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[12]
SS1PMMPhase2Current13 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[13]
SS1PMMPhase2Current14 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[14]
SS1PMMPhase2Current15 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[15]
SS1PMMPhase2Current16 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[16]
SS1PMMPhase2Current17 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[17]
SS1PMMPhase2Current18 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[18]
SS1PMMPhase2Current19 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[19]
SS1PMMPhase2Current1 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[1]
SS1PMMPhase2Current20 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[20]
SS1PMMPhase2Current21 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[21]
SS1PMMPhase2Current22 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[22]
SS1PMMPhase2Current23 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[23]
SS1PMMPhase2Current24 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[24]
SS1PMMPhase2Current25 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[25]
SS1PMMPhase2Current26 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[26]
SS1PMMPhase2Current27 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[27]
SS1PMMPhase2Current28 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[28]
SS1PMMPhase2Current29 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[29]
SS1PMMPhase2Current2 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[2]
SS1PMMPhase2Current30 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[30]
SS1PMMPhase2Current31 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[31]
SS1PMMPhase2Current32 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[32]
SS1PMMPhase2Current33 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[33]
SS1PMMPhase2Current34 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[34]
SS1PMMPhase2Current35 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[35]
SS1PMMPhase2Current36 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[36]
SS1PMMPhase2Current37 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[37]
SS1PMMPhase2Current38 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[38]
SS1PMMPhase2Current39 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[39]
SS1PMMPhase2Current3 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[3]
SS1PMMPhase2Current40 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[40]
SS1PMMPhase2Current41 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[41]
SS1PMMPhase2Current42 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[42]
SS1PMMPhase2Current4 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[4]
SS1PMMPhase2Current5 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[5]
SS1PMMPhase2Current6 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[6]
SS1PMMPhase2Current7 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[7]
SS1PMMPhase2Current8 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[8]
SS1PMMPhase2Current9 | REAL | IOD_SS1 | SS1:.PMM.Phase[2].Current[9]
SS1PMMPhase3Current10 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[10]
SS1PMMPhase3Current11 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[11]
SS1PMMPhase3Current12 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[12]
SS1PMMPhase3Current13 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[13]
SS1PMMPhase3Current14 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[14]
SS1PMMPhase3Current15 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[15]
SS1PMMPhase3Current16 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[16]
SS1PMMPhase3Current17 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[17]
SS1PMMPhase3Current18 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[18]
SS1PMMPhase3Current19 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[19]
SS1PMMPhase3Current1 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[1]
SS1PMMPhase3Current20 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[20]
SS1PMMPhase3Current21 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[21]
SS1PMMPhase3Current22 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[22]
SS1PMMPhase3Current23 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[23]
SS1PMMPhase3Current24 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[24]
SS1PMMPhase3Current25 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[25]
SS1PMMPhase3Current26 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[26]
SS1PMMPhase3Current27 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[27]
SS1PMMPhase3Current28 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[28]
SS1PMMPhase3Current29 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[29]
SS1PMMPhase3Current2 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[2]
SS1PMMPhase3Current30 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[30]
SS1PMMPhase3Current31 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[31]
SS1PMMPhase3Current32 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[32]
SS1PMMPhase3Current33 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[33]
SS1PMMPhase3Current34 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[34]
SS1PMMPhase3Current35 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[35]
SS1PMMPhase3Current36 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[36]
SS1PMMPhase3Current37 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[37]
SS1PMMPhase3Current38 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[38]
SS1PMMPhase3Current39 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[39]
SS1PMMPhase3Current3 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[3]
SS1PMMPhase3Current40 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[40]
SS1PMMPhase3Current41 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[41]
SS1PMMPhase3Current42 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[42]
SS1PMMPhase3Current4 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[4]
SS1PMMPhase3Current5 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[5]
SS1PMMPhase3Current6 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[6]
SS1PMMPhase3Current7 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[7]
SS1PMMPhase3Current8 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[8]
SS1PMMPhase3Current9 | REAL | IOD_SS1 | SS1:.PMM.Phase[3].Current[9]
SS1PMMPowerFactorSys | REAL | IOD_SS1 | SS1:.PMM.PowerFactorSys
SS1PMMReactiveEnergyConsumed_kVARh | REAL | IOD_SS1 | SS1:.PMM.ReactiveEnergyConsumed_kVARh
SS1PMMReactivePowerPhaseA | REAL | IOD_SS1 | SS1:.PMM.ReactivePowerPhaseA
SS1PMMReactivePowerPhaseB | REAL | IOD_SS1 | SS1:.PMM.ReactivePowerPhaseB
SS1PMMReactivePowerPhaseC | REAL | IOD_SS1 | SS1:.PMM.ReactivePowerPhaseC
SS1PMMTotalActivePower_kW | REAL | IOD_SS1 | SS1:.PMM.TotalActivePower_kW
SS1PMMTotalAparentPower_kVA | REAL | IOD_SS1 | SS1:.PMM.TotalAparentPower_kVA
SS1PMMTotalPowerFactor | REAL | IOD_SS1 | SS1:.PMM.TotalPowerFactor
SS1PMMTotalReactivePower_kVAR | REAL | IOD_SS1 | SS1:.PMM.TotalReactivePower_kVAR
SS1PMMVirA_fsys | REAL | IOD_SS1 | SS1:.PMM.VirA_fsys
SS1PMMVirA_Isys | REAL | IOD_SS1 | SS1:.PMM.VirA_Isys
SS1PMMVirA_PFsys | REAL | IOD_SS1 | SS1:.PMM.VirA_PFsys
SS1PMMVirA_Psys | REAL | IOD_SS1 | SS1:.PMM.VirA_Psys
SS1PMMVirA_Qsys | REAL | IOD_SS1 | SS1:.PMM.VirA_Qsys
SS1PMMVirA_Ssys | REAL | IOD_SS1 | SS1:.PMM.VirA_Ssys
SS1PMMVirA_Usys | REAL | IOD_SS1 | SS1:.PMM.VirA_Usys
SS1PMMVirB_fsys | REAL | IOD_SS1 | SS1:.PMM.VirB_fsys
SS1PMMVirB_Isys | REAL | IOD_SS1 | SS1:.PMM.VirB_Isys
SS1PMMVirB_PFsys | REAL | IOD_SS1 | SS1:.PMM.VirB_PFsys
SS1PMMVirB_Psys | REAL | IOD_SS1 | SS1:.PMM.VirB_Psys
SS1PMMVirB_Qsys | REAL | IOD_SS1 | SS1:.PMM.VirB_Qsys
SS1PMMVirB_Ssys | REAL | IOD_SS1 | SS1:.PMM.VirB_Ssys
SS1PMMVirB_Usys | REAL | IOD_SS1 | SS1:.PMM.VirB_Usys
SS1PMMVirBActiveEnergyConsumed_kWh | REAL | IOD_SS1 | SS1:.PMM.VirBActiveEnergyConsumed_kWh
SS1PMMVirBActivePowerPhaseA_kW | REAL | IOD_SS1 | SS1:.PMM.VirBActivePowerPhaseA_kW
SS1PMMVirBActivePowerPhaseB_kW | REAL | IOD_SS1 | SS1:.PMM.VirBActivePowerPhaseB_kW
SS1PMMVirBActivePowerPhaseC_kW | REAL | IOD_SS1 | SS1:.PMM.VirBActivePowerPhaseC_kW
SS1PMMVirBAparentPowerPhaseA | REAL | IOD_SS1 | SS1:.PMM.VirBAparentPowerPhaseA
SS1PMMVirBAparentPowerPhaseB | REAL | IOD_SS1 | SS1:.PMM.VirBAparentPowerPhaseB
SS1PMMVirBAparentPowerPhaseC | REAL | IOD_SS1 | SS1:.PMM.VirBAparentPowerPhaseC
SS1PMMVirBAverageCurrent_A | REAL | IOD_SS1 | SS1:.PMM.VirBAverageCurrent_A
SS1PMMVirBAveragePhaseToNeutral_V | REAL | IOD_SS1 | SS1:.PMM.VirBAveragePhaseToNeutral_V
SS1PMMVirBAveragePhaseToPhase_V | REAL | IOD_SS1 | SS1:.PMM.VirBAveragePhaseToPhase_V
SS1PMMVirBCurrentInPhaseA_A | REAL | IOD_SS1 | SS1:.PMM.VirBCurrentInPhaseA_A
SS1PMMVirBCurrentInPhaseB_A | REAL | IOD_SS1 | SS1:.PMM.VirBCurrentInPhaseB_A
SS1PMMVirBCurrentInPhaseC_A | REAL | IOD_SS1 | SS1:.PMM.VirBCurrentInPhaseC_A
SS1PMMVirBFrequency_Hz | REAL | IOD_SS1 | SS1:.PMM.VirBFrequency_Hz
SS1PMMVirBPowerFactorSys | REAL | IOD_SS1 | SS1:.PMM.VirBPowerFactorSys
SS1PMMVirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS1 | SS1:.PMM.VirBReactiveEnergyConsumed_kWh
SS1PMMVirBReactivePowerPhaseA | REAL | IOD_SS1 | SS1:.PMM.VirBReactivePowerPhaseA
SS1PMMVirBReactivePowerPhaseB | REAL | IOD_SS1 | SS1:.PMM.VirBReactivePowerPhaseB
SS1PMMVirBReactivePowerPhaseC | REAL | IOD_SS1 | SS1:.PMM.VirBReactivePowerPhaseC
SS1PMMVirBTotalActivePower_kW | REAL | IOD_SS1 | SS1:.PMM.VirBTotalActivePower_kW
SS1PMMVirBTotalAparentPower_kVA | REAL | IOD_SS1 | SS1:.PMM.VirBTotalAparentPower_kVA
SS1PMMVirBTotalPowerFactor | REAL | IOD_SS1 | SS1:.PMM.VirBTotalPowerFactor
SS1PMMVirBTotalReactivePower_kVAR | REAL | IOD_SS1 | SS1:.PMM.VirBTotalReactivePower_kVAR
SS1PMMVirBVoltageBetweenPhaseAB_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseAB_V
SS1PMMVirBVoltageBetweenPhaseAN_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseAN_V
SS1PMMVirBVoltageBetweenPhaseBC_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseBC_V
SS1PMMVirBVoltageBetweenPhaseBN_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseBN_V
SS1PMMVirBVoltageBetweenPhaseCA_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseCA_V
SS1PMMVirBVoltageBetweenPhaseCN_V | REAL | IOD_SS1 | SS1:.PMM.VirBVoltageBetweenPhaseCN_V
SS1PMMVoltageBetweenPhaseAB_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseAB_V
SS1PMMVoltageBetweenPhaseAN_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseAN_V
SS1PMMVoltageBetweenPhaseBC_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseBC_V
SS1PMMVoltageBetweenPhaseBN_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseBN_V
SS1PMMVoltageBetweenPhaseCA_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseCA_V
SS1PMMVoltageBetweenPhaseCN_V | REAL | IOD_SS1 | SS1:.PMM.VoltageBetweenPhaseCN_V
SS1SKTemp1 | REAL | IOD_SS1 | SS1:.SKTemp1
SS1SKTemp2 | REAL | IOD_SS1 | SS1:.SKTemp2
SS1SKTemp3 | REAL | IOD_SS1 | SS1:.SKTemp3
SS1SKTempKontrSoba | REAL | IOD_SS1 | SS1:.SKTempKontrSoba
SS1SKTempLinkProstor | REAL | IOD_SS1 | SS1:.SKTempLinkProstor
SS1SKTempServSoba1Povpr | REAL | IOD_SS1 | SS1:.SKTempServSoba1Povpr
SS1SKVlaga1 | REAL | IOD_SS1 | SS1:.SKVlaga1
SS1SKVlaga2 | REAL | IOD_SS1 | SS1:.SKVlaga2
SS1SKVlaga3 | REAL | IOD_SS1 | SS1:.SKVlaga3
SS1SKVlagaKontrSoba | REAL | IOD_SS1 | SS1:.SKVlagaKontrSoba
SS1SKVlagaLinkProstor | REAL | IOD_SS1 | SS1:.SKVlagaLinkProstor
SS1TempZaAlarmTIA123 | REAL | IOD_SS1 | SS1:.TempZaAlarmTIA123
SS1TempZaAlarmTIA4 | REAL | IOD_SS1 | SS1:.TempZaAlarmTIA4
SS1TempZaAlarmTIA5 | REAL | IOD_SS1 | SS1:.TempZaAlarmTIA5
SS1TempZaVklopObehKlim | REAL | IOD_SS1 | SS1:.TempZaVklopObehKlim
SS1UserName | STRING | IOD_SS1 | SS1:.UserName
SS1PMMAlarmPhase1C01_16_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C01_16_60to80
SS1PMMAlarmPhase1C01_16_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C01_16_over80
SS1PMMAlarmPhase1C17_32_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C17_32_60to80
SS1PMMAlarmPhase1C17_32_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C17_32_over80
SS1PMMAlarmPhase1C33_42_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C33_42_60to80
SS1PMMAlarmPhase1C33_42_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[1].C33_42_over80
SS1PMMAlarmPhase2C01_16_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C01_16_60to80
SS1PMMAlarmPhase2C01_16_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C01_16_over80
SS1PMMAlarmPhase2C17_32_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C17_32_60to80
SS1PMMAlarmPhase2C17_32_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C17_32_over80
SS1PMMAlarmPhase2C33_42_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C33_42_60to80
SS1PMMAlarmPhase2C33_42_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[2].C33_42_over80
SS1PMMAlarmPhase3C01_16_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C01_16_60to80
SS1PMMAlarmPhase3C01_16_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C01_16_over80
SS1PMMAlarmPhase3C17_32_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C17_32_60to80
SS1PMMAlarmPhase3C17_32_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C17_32_over80
SS1PMMAlarmPhase3C33_42_60to80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C33_42_60to80
SS1PMMAlarmPhase3C33_42_over80 | UINT | IOD_SS1 | SS1:.PMM.AlarmPhase[3].C33_42_over80
SS1kom_nast_cas_izpada | UINT | IOD_SS1 | SS1:.kom_nast_cas_izpada

## variable_3
SS1AlarmKlimat1_Napaka | DIGITAL | IOD_SS1_TCP | 1 | 00001 | AlarmKlimat1_Napaka
SS1AlarmKlimat2_Napaka | DIGITAL | IOD_SS1_TCP | 2 | 00002 | AlarmKlimat2_Napaka
SS1AlarmKlimat3_Napaka | DIGITAL | IOD_SS1_TCP | 3 | 00003 | AlarmKlimat3_Napaka
SS1AlarmLAH1_RazlitjeVode | DIGITAL | IOD_SS1_TCP | 4 | 00004 | AlarmLAH1_RazlitjeVode
SS1AlarmLAH2_RazlitjeVode | DIGITAL | IOD_SS1_TCP | 5 | 00005 | AlarmLAH2_RazlitjeVode
SS1AlarmSinhronizacijaNOK | DIGITAL | IOD_SS1_TCP | 6 | 00006 | AlarmSinhronizacijaNOK
SS1AlarmSP1_Napaka | DIGITAL | IOD_SS1_TCP | 7 | 00007 | AlarmSP1_Napaka
SS1AlarmSP2_Napaka | DIGITAL | IOD_SS1_TCP | 8 | 00008 | AlarmSP2_Napaka
SS1AlarmSP3_Napaka | DIGITAL | IOD_SS1_TCP | 9 | 00009 | AlarmSP3_Napaka
SS1AlarmSP4_Napaka | DIGITAL | IOD_SS1_TCP | 10 | 00010 | AlarmSP4_Napaka
SS1AlarmSP5_Napaka | DIGITAL | IOD_SS1_TCP | 11 | 00011 | AlarmSP5_Napaka
SS1AlarmTempTIA123Previsoka | DIGITAL | IOD_SS1_TCP | 12 | 00012 | AlarmTempTIA123Previsoka
SS1AlarmTempTIA4Previsoka | DIGITAL | IOD_SS1_TCP | 13 | 00013 | AlarmTempTIA4Previsoka
SS1AlarmTempTIA5Previsoka | DIGITAL | IOD_SS1_TCP | 14 | 00014 | AlarmTempTIA5Previsoka
SS1AlarmTSTempPrevisoka | DIGITAL | IOD_SS1_TCP | 15 | 00015 | AlarmTSTempPrevisoka
SS1AlarmUPSKrmOmara_Alarm | DIGITAL | IOD_SS1_TCP | 16 | 00016 | AlarmUPSKrmOmara_Alarm
SS1ComSCADA | DIGITAL | IOD_SS1_TCP | 17 | 00017 | ComSCADA
SS1ComSCADA1 | DIGITAL | IOD_SS1_TCP | 18 | 00018 | ComSCADA1
SS1ErrComKlima1 | DIGITAL | IOD_SS1_TCP | 19 | 00019 | ErrComKlima[1]
SS1ErrComKlima2 | DIGITAL | IOD_SS1_TCP | 20 | 00020 | ErrComKlima[2]
SS1ErrComKlima3 | DIGITAL | IOD_SS1_TCP | 21 | 00021 | ErrComKlima[3]
SS1ErrCommScada | DIGITAL | IOD_SS1_TCP | 22 | 00022 | ErrCommScada
SS1ErrComPanelPLC | DIGITAL | IOD_SS1_TCP | 23 | 00023 | ErrComPanelPLC
SS1ErrComPMM | DIGITAL | IOD_SS1_TCP | 24 | 00024 | ErrComPMM
SS1ErrComPort2 | DIGITAL | IOD_SS1_TCP | 25 | 00025 | ErrComPort2
SS1Klima1_Onemogocena | DIGITAL | IOD_SS1_TCP | 26 | 00026 | Klima1_Onemogocena
SS1Klima2_Onemogocena | DIGITAL | IOD_SS1_TCP | 27 | 00027 | Klima2_Onemogocena
SS1Klima3_Onemogocena | DIGITAL | IOD_SS1_TCP | 28 | 00028 | Klima3_Onemogocena
SS1Klima1IzhodniVentilator | DIGITAL | IOD_SS1_TCP | 29 | 00029 | Klima[1].IzhodniVentilator
SS1Klima1Kompresor1 | DIGITAL | IOD_SS1_TCP | 30 | 00030 | Klima[1].Kompresor1
SS1Klima1Kompresor2 | DIGITAL | IOD_SS1_TCP | 31 | 00031 | Klima[1].Kompresor2
SS1Klima1Razvlazevanje | DIGITAL | IOD_SS1_TCP | 32 | 00032 | Klima[1].Razvlazevanje
SS1Klima1VentilGretjeOdpiranje | DIGITAL | IOD_SS1_TCP | 33 | 00033 | Klima[1].VentilGretjeOdpiranje
SS1Klima1VentilGretjeZapiranje | DIGITAL | IOD_SS1_TCP | 34 | 00034 | Klima[1].VentilGretjeZapiranje
SS1Klima1Vlazenje | DIGITAL | IOD_SS1_TCP | 35 | 00035 | Klima[1].Vlazenje
SS1Klima2IzhodniVentilator | DIGITAL | IOD_SS1_TCP | 36 | 00036 | Klima[2].IzhodniVentilator
SS1Klima2Kompresor1 | DIGITAL | IOD_SS1_TCP | 37 | 00037 | Klima[2].Kompresor1
SS1Klima2Kompresor2 | DIGITAL | IOD_SS1_TCP | 38 | 00038 | Klima[2].Kompresor2
SS1Klima2Razvlazevanje | DIGITAL | IOD_SS1_TCP | 39 | 00039 | Klima[2].Razvlazevanje
SS1Klima2VentilGretjeOdpiranje | DIGITAL | IOD_SS1_TCP | 40 | 00040 | Klima[2].VentilGretjeOdpiranje
SS1Klima2VentilGretjeZapiranje | DIGITAL | IOD_SS1_TCP | 41 | 00041 | Klima[2].VentilGretjeZapiranje
SS1Klima2Vlazenje | DIGITAL | IOD_SS1_TCP | 42 | 00042 | Klima[2].Vlazenje
SS1Klima3IzhodniVentilator | DIGITAL | IOD_SS1_TCP | 43 | 00043 | Klima[3].IzhodniVentilator
SS1Klima3Kompresor1 | DIGITAL | IOD_SS1_TCP | 44 | 00044 | Klima[3].Kompresor1
SS1Klima3Kompresor2 | DIGITAL | IOD_SS1_TCP | 45 | 00045 | Klima[3].Kompresor2
SS1Klima3Razvlazevanje | DIGITAL | IOD_SS1_TCP | 46 | 00046 | Klima[3].Razvlazevanje
SS1Klima3VentilGretjeOdpiranje | DIGITAL | IOD_SS1_TCP | 47 | 00047 | Klima[3].VentilGretjeOdpiranje
SS1Klima3VentilGretjeZapiranje | DIGITAL | IOD_SS1_TCP | 48 | 00048 | Klima[3].VentilGretjeZapiranje
SS1Klima3Vlazenje | DIGITAL | IOD_SS1_TCP | 49 | 00049 | Klima[3].Vlazenje
SS1KlimaError1AlarmKompresor1 | DIGITAL | IOD_SS1_TCP | 50 | 00050 | KlimaError[1].AlarmKompresor1
SS1KlimaError1AlarmKompresor2 | DIGITAL | IOD_SS1_TCP | 51 | 00051 | KlimaError[1].AlarmKompresor2
SS1KlimaError1FenThermalCutout | DIGITAL | IOD_SS1_TCP | 52 | 00052 | KlimaError[1].FenThermalCutout
SS1KlimaError1IzlivVode | DIGITAL | IOD_SS1_TCP | 53 | 00053 | KlimaError[1].IzlivVode
SS1KlimaError1Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 54 | 00054 | KlimaError[1].Kompresor1naMejiStevilaObrUr
SS1KlimaError1Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 55 | 00055 | KlimaError[1].Kompresor2naMejiStevilaObrUr
SS1KlimaError1Kond1FenThermalCutout | DIGITAL | IOD_SS1_TCP | 56 | 00056 | KlimaError[1].Kond1FenThermalCutout
SS1KlimaError1Kond2FenThermalCutout | DIGITAL | IOD_SS1_TCP | 57 | 00057 | KlimaError[1].Kond2FenThermalCutout
SS1KlimaError1NapakaPriPretokuVode | DIGITAL | IOD_SS1_TCP | 58 | 00058 | KlimaError[1].NapakaPriPretokuVode
SS1KlimaError1NapakaPriPretokuZraka | DIGITAL | IOD_SS1_TCP | 59 | 00059 | KlimaError[1].NapakaPriPretokuZraka
SS1KlimaError1NapakaSenzorPritiska | DIGITAL | IOD_SS1_TCP | 60 | 00060 | KlimaError[1].NapakaSenzorPritiska
SS1KlimaError1NapakaSenzorVlaznosti | DIGITAL | IOD_SS1_TCP | 61 | 00061 | KlimaError[1].NapakaSenzorVlaznosti
SS1KlimaError1NapakaTSTemperaturaProstora | DIGITAL | IOD_SS1_TCP | 62 | 00062 | KlimaError[1].NapakaTSTemperaturaProstora
SS1KlimaError1NiTokaVVlazilcu | DIGITAL | IOD_SS1_TCP | 63 | 00063 | KlimaError[1].NiTokaVVlazilcu
SS1KlimaError1NiVodeVVlazilcu | DIGITAL | IOD_SS1_TCP | 64 | 00064 | KlimaError[1].NiVodeVVlazilcu
SS1KlimaError1NizekPritiskKompresor1 | DIGITAL | IOD_SS1_TCP | 65 | 00065 | KlimaError[1].NizekPritiskKompresor1
SS1KlimaError1NizekPritiskKompresor2 | DIGITAL | IOD_SS1_TCP | 66 | 00066 | KlimaError[1].NizekPritiskKompresor2
SS1KlimaError1NizkaTempVProstoru | DIGITAL | IOD_SS1_TCP | 67 | 00067 | KlimaError[1].NizkaTempVProstoru
SS1KlimaError1NizkaVlaznost | DIGITAL | IOD_SS1_TCP | 68 | 00068 | KlimaError[1].NizkaVlaznost
SS1KlimaError1PozarniAlarm | DIGITAL | IOD_SS1_TCP | 69 | 00069 | KlimaError[1].PozarniAlarm
SS1KlimaError1TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS1_TCP | 70 | 00070 | KlimaError[1].TermZascInVisokPritiskKompr1
SS1KlimaError1TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS1_TCP | 71 | 00071 | KlimaError[1].TermZascInVisokPritiskKompr2
SS1KlimaError1ThermalCutoutHeater1 | DIGITAL | IOD_SS1_TCP | 72 | 00072 | KlimaError[1].ThermalCutoutHeater1
SS1KlimaError1ThermalCutoutHeater2 | DIGITAL | IOD_SS1_TCP | 73 | 00073 | KlimaError[1].ThermalCutoutHeater2
SS1KlimaError1VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 74 | 00074 | KlimaError[1].VentilatorNaMejiStevilaObrUr
SS1KlimaError1VisokaTempVProstoru | DIGITAL | IOD_SS1_TCP | 75 | 00075 | KlimaError[1].VisokaTempVProstoru
SS1KlimaError1VisokaVlaznost | DIGITAL | IOD_SS1_TCP | 76 | 00076 | KlimaError[1].VisokaVlaznost
SS1KlimaError1VisokPritiskVKrogu1 | DIGITAL | IOD_SS1_TCP | 77 | 00077 | KlimaError[1].VisokPritiskVKrogu1
SS1KlimaError1VisokPritiskVKrogu2 | DIGITAL | IOD_SS1_TCP | 78 | 00078 | KlimaError[1].VisokPritiskVKrogu2
SS1KlimaError1VisokTokVVlazilcu | DIGITAL | IOD_SS1_TCP | 79 | 00079 | KlimaError[1].VisokTokVVlazilcu
SS1KlimaError1VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 80 | 00080 | KlimaError[1].VlazilecnaMejiStevilaObrUr
SS1KlimaError1ZamasenFilter | DIGITAL | IOD_SS1_TCP | 81 | 00081 | KlimaError[1].ZamasenFilter
SS1KlimaError1ZunanjiAlarm | DIGITAL | IOD_SS1_TCP | 82 | 00082 | KlimaError[1].ZunanjiAlarm
SS1KlimaError2AlarmKompresor1 | DIGITAL | IOD_SS1_TCP | 83 | 00083 | KlimaError[2].AlarmKompresor1
SS1KlimaError2AlarmKompresor2 | DIGITAL | IOD_SS1_TCP | 84 | 00084 | KlimaError[2].AlarmKompresor2
SS1KlimaError2FenThermalCutout | DIGITAL | IOD_SS1_TCP | 85 | 00085 | KlimaError[2].FenThermalCutout
SS1KlimaError2IzlivVode | DIGITAL | IOD_SS1_TCP | 86 | 00086 | KlimaError[2].IzlivVode
SS1KlimaError2Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 87 | 00087 | KlimaError[2].Kompresor1naMejiStevilaObrUr
SS1KlimaError2Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 88 | 00088 | KlimaError[2].Kompresor2naMejiStevilaObrUr
SS1KlimaError2Kond1FenThermalCutout | DIGITAL | IOD_SS1_TCP | 89 | 00089 | KlimaError[2].Kond1FenThermalCutout
SS1KlimaError2Kond2FenThermalCutout | DIGITAL | IOD_SS1_TCP | 90 | 00090 | KlimaError[2].Kond2FenThermalCutout
SS1KlimaError2NapakaPriPretokuVode | DIGITAL | IOD_SS1_TCP | 91 | 00091 | KlimaError[2].NapakaPriPretokuVode
SS1KlimaError2NapakaPriPretokuZraka | DIGITAL | IOD_SS1_TCP | 92 | 00092 | KlimaError[2].NapakaPriPretokuZraka
SS1KlimaError2NapakaSenzorPritiska | DIGITAL | IOD_SS1_TCP | 93 | 00093 | KlimaError[2].NapakaSenzorPritiska
SS1KlimaError2NapakaSenzorVlaznosti | DIGITAL | IOD_SS1_TCP | 94 | 00094 | KlimaError[2].NapakaSenzorVlaznosti
SS1KlimaError2NapakaTSTemperaturaProstora | DIGITAL | IOD_SS1_TCP | 95 | 00095 | KlimaError[2].NapakaTSTemperaturaProstora
SS1KlimaError2NiTokaVVlazilcu | DIGITAL | IOD_SS1_TCP | 96 | 00096 | KlimaError[2].NiTokaVVlazilcu
SS1KlimaError2NiVodeVVlazilcu | DIGITAL | IOD_SS1_TCP | 97 | 00097 | KlimaError[2].NiVodeVVlazilcu
SS1KlimaError2NizekPritiskKompresor1 | DIGITAL | IOD_SS1_TCP | 98 | 00098 | KlimaError[2].NizekPritiskKompresor1
SS1KlimaError2NizekPritiskKompresor2 | DIGITAL | IOD_SS1_TCP | 99 | 00099 | KlimaError[2].NizekPritiskKompresor2
SS1KlimaError2NizkaTempVProstoru | DIGITAL | IOD_SS1_TCP | 100 | 00100 | KlimaError[2].NizkaTempVProstoru
SS1KlimaError2NizkaVlaznost | DIGITAL | IOD_SS1_TCP | 101 | 00101 | KlimaError[2].NizkaVlaznost
SS1KlimaError2PozarniAlarm | DIGITAL | IOD_SS1_TCP | 102 | 00102 | KlimaError[2].PozarniAlarm
SS1KlimaError2TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS1_TCP | 103 | 00103 | KlimaError[2].TermZascInVisokPritiskKompr1
SS1KlimaError2TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS1_TCP | 104 | 00104 | KlimaError[2].TermZascInVisokPritiskKompr2
SS1KlimaError2ThermalCutoutHeater1 | DIGITAL | IOD_SS1_TCP | 105 | 00105 | KlimaError[2].ThermalCutoutHeater1
SS1KlimaError2ThermalCutoutHeater2 | DIGITAL | IOD_SS1_TCP | 106 | 00106 | KlimaError[2].ThermalCutoutHeater2
SS1KlimaError2VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 107 | 00107 | KlimaError[2].VentilatorNaMejiStevilaObrUr
SS1KlimaError2VisokaTempVProstoru | DIGITAL | IOD_SS1_TCP | 108 | 00108 | KlimaError[2].VisokaTempVProstoru
SS1KlimaError2VisokaVlaznost | DIGITAL | IOD_SS1_TCP | 109 | 00109 | KlimaError[2].VisokaVlaznost
SS1KlimaError2VisokPritiskVKrogu1 | DIGITAL | IOD_SS1_TCP | 110 | 00110 | KlimaError[2].VisokPritiskVKrogu1
SS1KlimaError2VisokPritiskVKrogu2 | DIGITAL | IOD_SS1_TCP | 111 | 00111 | KlimaError[2].VisokPritiskVKrogu2
SS1KlimaError2VisokTokVVlazilcu | DIGITAL | IOD_SS1_TCP | 112 | 00112 | KlimaError[2].VisokTokVVlazilcu
SS1KlimaError2VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 113 | 00113 | KlimaError[2].VlazilecnaMejiStevilaObrUr
SS1KlimaError2ZamasenFilter | DIGITAL | IOD_SS1_TCP | 114 | 00114 | KlimaError[2].ZamasenFilter
SS1KlimaError2ZunanjiAlarm | DIGITAL | IOD_SS1_TCP | 115 | 00115 | KlimaError[2].ZunanjiAlarm
SS1KlimaError3AlarmKompresor1 | DIGITAL | IOD_SS1_TCP | 116 | 00116 | KlimaError[3].AlarmKompresor1
SS1KlimaError3AlarmKompresor2 | DIGITAL | IOD_SS1_TCP | 117 | 00117 | KlimaError[3].AlarmKompresor2
SS1KlimaError3FenThermalCutout | DIGITAL | IOD_SS1_TCP | 118 | 00118 | KlimaError[3].FenThermalCutout
SS1KlimaError3IzlivVode | DIGITAL | IOD_SS1_TCP | 119 | 00119 | KlimaError[3].IzlivVode
SS1KlimaError3Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 120 | 00120 | KlimaError[3].Kompresor1naMejiStevilaObrUr
SS1KlimaError3Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 121 | 00121 | KlimaError[3].Kompresor2naMejiStevilaObrUr
SS1KlimaError3Kond1FenThermalCutout | DIGITAL | IOD_SS1_TCP | 122 | 00122 | KlimaError[3].Kond1FenThermalCutout
SS1KlimaError3Kond2FenThermalCutout | DIGITAL | IOD_SS1_TCP | 123 | 00123 | KlimaError[3].Kond2FenThermalCutout
SS1KlimaError3NapakaPriPretokuVode | DIGITAL | IOD_SS1_TCP | 124 | 00124 | KlimaError[3].NapakaPriPretokuVode
SS1KlimaError3NapakaPriPretokuZraka | DIGITAL | IOD_SS1_TCP | 125 | 00125 | KlimaError[3].NapakaPriPretokuZraka
SS1KlimaError3NapakaSenzorPritiska | DIGITAL | IOD_SS1_TCP | 126 | 00126 | KlimaError[3].NapakaSenzorPritiska
SS1KlimaError3NapakaSenzorVlaznosti | DIGITAL | IOD_SS1_TCP | 127 | 00127 | KlimaError[3].NapakaSenzorVlaznosti
SS1KlimaError3NapakaTSTemperaturaProstora | DIGITAL | IOD_SS1_TCP | 128 | 00128 | KlimaError[3].NapakaTSTemperaturaProstora
SS1KlimaError3NiTokaVVlazilcu | DIGITAL | IOD_SS1_TCP | 129 | 00129 | KlimaError[3].NiTokaVVlazilcu
SS1KlimaError3NiVodeVVlazilcu | DIGITAL | IOD_SS1_TCP | 130 | 00130 | KlimaError[3].NiVodeVVlazilcu
SS1KlimaError3NizekPritiskKompresor1 | DIGITAL | IOD_SS1_TCP | 131 | 00131 | KlimaError[3].NizekPritiskKompresor1
SS1KlimaError3NizekPritiskKompresor2 | DIGITAL | IOD_SS1_TCP | 132 | 00132 | KlimaError[3].NizekPritiskKompresor2
SS1KlimaError3NizkaTempVProstoru | DIGITAL | IOD_SS1_TCP | 133 | 00133 | KlimaError[3].NizkaTempVProstoru
SS1KlimaError3NizkaVlaznost | DIGITAL | IOD_SS1_TCP | 134 | 00134 | KlimaError[3].NizkaVlaznost
SS1KlimaError3PozarniAlarm | DIGITAL | IOD_SS1_TCP | 135 | 00135 | KlimaError[3].PozarniAlarm
SS1KlimaError3TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS1_TCP | 136 | 00136 | KlimaError[3].TermZascInVisokPritiskKompr1
SS1KlimaError3TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS1_TCP | 137 | 00137 | KlimaError[3].TermZascInVisokPritiskKompr2
SS1KlimaError3ThermalCutoutHeater1 | DIGITAL | IOD_SS1_TCP | 138 | 00138 | KlimaError[3].ThermalCutoutHeater1
SS1KlimaError3ThermalCutoutHeater2 | DIGITAL | IOD_SS1_TCP | 139 | 00139 | KlimaError[3].ThermalCutoutHeater2
SS1KlimaError3VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 140 | 00140 | KlimaError[3].VentilatorNaMejiStevilaObrUr
SS1KlimaError3VisokaTempVProstoru | DIGITAL | IOD_SS1_TCP | 141 | 00141 | KlimaError[3].VisokaTempVProstoru
SS1KlimaError3VisokaVlaznost | DIGITAL | IOD_SS1_TCP | 142 | 00142 | KlimaError[3].VisokaVlaznost
SS1KlimaError3VisokPritiskVKrogu1 | DIGITAL | IOD_SS1_TCP | 143 | 00143 | KlimaError[3].VisokPritiskVKrogu1
SS1KlimaError3VisokPritiskVKrogu2 | DIGITAL | IOD_SS1_TCP | 144 | 00144 | KlimaError[3].VisokPritiskVKrogu2
SS1KlimaError3VisokTokVVlazilcu | DIGITAL | IOD_SS1_TCP | 145 | 00145 | KlimaError[3].VisokTokVVlazilcu
SS1KlimaError3VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 146 | 00146 | KlimaError[3].VlazilecnaMejiStevilaObrUr
SS1KlimaError3ZamasenFilter | DIGITAL | IOD_SS1_TCP | 147 | 00147 | KlimaError[3].ZamasenFilter
SS1KlimaError3ZunanjiAlarm | DIGITAL | IOD_SS1_TCP | 148 | 00148 | KlimaError[3].ZunanjiAlarm
SS1NacDelovanjaKlime1_Avtomatsko | DIGITAL | IOD_SS1_TCP | 149 | 00149 | NacDelovanjaKlime1_Avtomatsko
SS1NacDelovanjaKlime2_3Avtomatsko | DIGITAL | IOD_SS1_TCP | 150 | 00150 | NacDelovanjaKlime2_3Avtomatsko
SS1NapakaSenzorTemp1 | DIGITAL | IOD_SS1_TCP | 151 | 00151 | NapakaSenzorTemp1
SS1NapakaSenzorTemp2 | DIGITAL | IOD_SS1_TCP | 152 | 00152 | NapakaSenzorTemp2
SS1NapakaSenzorTemp3 | DIGITAL | IOD_SS1_TCP | 153 | 00153 | NapakaSenzorTemp3
SS1NapakaSenzorTempKontrSoba | DIGITAL | IOD_SS1_TCP | 154 | 00154 | NapakaSenzorTempKontrSoba
SS1NapakaSenzorTempLinkProstor | DIGITAL | IOD_SS1_TCP | 155 | 00155 | NapakaSenzorTempLinkProstor
SS1NapakaSenzorVlaga1 | DIGITAL | IOD_SS1_TCP | 156 | 00156 | NapakaSenzorVlaga1
SS1NapakaSenzorVlaga2 | DIGITAL | IOD_SS1_TCP | 157 | 00157 | NapakaSenzorVlaga2
SS1NapakaSenzorVlaga3 | DIGITAL | IOD_SS1_TCP | 158 | 00158 | NapakaSenzorVlaga3
SS1NapakaSenzorVlagaKontrSoba | DIGITAL | IOD_SS1_TCP | 159 | 00159 | NapakaSenzorVlagaKontrSoba
SS1NapakaSenzorVlagaLinkProstor | DIGITAL | IOD_SS1_TCP | 160 | 00160 | NapakaSenzorVlagaLinkProstor
SS1NastaviCasNaKrmilniku | DIGITAL | IOD_SS1_TCP | 161 | 00161 | NastaviCasNaKrmilniku
SS1NastavitevUreKrUspesna | DIGITAL | IOD_SS1_TCP | 162 | 00162 | NastavitevUreKrUspesna
SS1OpozoriloBaterijaPLC | DIGITAL | IOD_SS1_TCP | 163 | 00163 | OpozoriloBaterijaPLC
SS1PMM1OverCurrentBetw1 | DIGITAL | IOD_SS1_TCP | 164 | 00164 | PMM1OverCurrentBetw[1]
SS1PMM1OverCurrentBetw2 | DIGITAL | IOD_SS1_TCP | 165 | 00165 | PMM1OverCurrentBetw[2]
SS1PMM1OverCurrentBetw3 | DIGITAL | IOD_SS1_TCP | 166 | 00166 | PMM1OverCurrentBetw[3]
SS1PMM1OverCurrentOver1 | DIGITAL | IOD_SS1_TCP | 167 | 00167 | PMM1OverCurrentOver[1]
SS1PMM1OverCurrentOver2 | DIGITAL | IOD_SS1_TCP | 168 | 00168 | PMM1OverCurrentOver[2]
SS1PMM1OverCurrentOver3 | DIGITAL | IOD_SS1_TCP | 169 | 00169 | PMM1OverCurrentOver[3]
SS1PMM1OverVoltage | DIGITAL | IOD_SS1_TCP | 170 | 00170 | PMM1OverVoltage
SS1RocniVklopKlima1 | DIGITAL | IOD_SS1_TCP | 171 | 00171 | RocniVklopKlima1
SS1RocniVklopKlima2 | DIGITAL | IOD_SS1_TCP | 172 | 00172 | RocniVklopKlima2
SS1RocniVklopKlima3 | DIGITAL | IOD_SS1_TCP | 173 | 00173 | RocniVklopKlima3
SS1SinhronizacijaPanelOK | DIGITAL | IOD_SS1_TCP | 174 | 00174 | SinhronizacijaPanelOK
SS1SinhronizirajCas_Panel | DIGITAL | IOD_SS1_TCP | 175 | 00175 | SinhronizirajCas_Panel
SS1SkupneNapakeNaprav_Klima1 | DIGITAL | IOD_SS1_TCP | 176 | 00176 | SkupneNapakeNaprav_Klima1
SS1SkupneNapakeNaprav_Klima2 | DIGITAL | IOD_SS1_TCP | 177 | 00177 | SkupneNapakeNaprav_Klima2
SS1SkupneNapakeNaprav_Klima3 | DIGITAL | IOD_SS1_TCP | 178 | 00178 | SkupneNapakeNaprav_Klima3
SS1SkupneNapakeNaprav_Komunikacija | DIGITAL | IOD_SS1_TCP | 179 | 00179 | SkupneNapakeNaprav_Komunikacija
SS1SkupneNapakeNaprav_PMMVirA | DIGITAL | IOD_SS1_TCP | 180 | 00180 | SkupneNapakeNaprav_PMMVirA
SS1SkupneNapakeNaprav_PMMVirB | DIGITAL | IOD_SS1_TCP | 181 | 00181 | SkupneNapakeNaprav_PMMVirB
SS1SkupneNapakeNaprav_PMMVirBVirA | DIGITAL | IOD_SS1_TCP | 182 | 00182 | SkupneNapakeNaprav_PMMVirBVirA
SS1SkupneNapakeNaprav_TempVlaga | DIGITAL | IOD_SS1_TCP | 183 | 00183 | SkupneNapakeNaprav_TempVlaga
SS1StanjeKlimat1_Delovanje | DIGITAL | IOD_SS1_TCP | 184 | 00184 | StanjeKlimat1_Delovanje
SS1StanjeKlimat2_Delovanje | DIGITAL | IOD_SS1_TCP | 185 | 00185 | StanjeKlimat2_Delovanje
SS1StanjeKlimat3_Delovanje | DIGITAL | IOD_SS1_TCP | 186 | 00186 | StanjeKlimat3_Delovanje
SS1StanjeSP1_Delovanje | DIGITAL | IOD_SS1_TCP | 187 | 00187 | StanjeSP1_Delovanje
SS1StanjeSP2_Delovanje | DIGITAL | IOD_SS1_TCP | 188 | 00188 | StanjeSP2_Delovanje
SS1StanjeSP3_Delovanje | DIGITAL | IOD_SS1_TCP | 189 | 00189 | StanjeSP3_Delovanje
SS1StanjeSP4_Delovanje | DIGITAL | IOD_SS1_TCP | 190 | 00190 | StanjeSP4_Delovanje
SS1StanjeSP5_Delovanje | DIGITAL | IOD_SS1_TCP | 191 | 00191 | StanjeSP5_Delovanje
SS1StanjeUPSKrmOmara_BaterijskiNacin | DIGITAL | IOD_SS1_TCP | 192 | 00192 | StanjeUPSKrmOmara_BaterijskiNacin
SS1StanjeUPSKrmOmara_Polnenje | DIGITAL | IOD_SS1_TCP | 193 | 00193 | StanjeUPSKrmOmara_Polnenje
SS1UserLoggedIn | DIGITAL | IOD_SS1_TCP | 194 | 00194 | UserLoggedIn
SS1XVH_AlarmOn | DIGITAL | IOD_SS1_TCP | 195 | 00195 | XVH_AlarmOn
SS1Klimat1_Vklop | DIGITAL | IOD_SS1_TCP | 196 | 00196 | Klimat1_Vklop
SS1Klimat2_Vklop | DIGITAL | IOD_SS1_TCP | 197 | 00197 | Klimat2_Vklop
SS1Klimat3_Vklop | DIGITAL | IOD_SS1_TCP | 198 | 00198 | Klimat3_Vklop
SS1ErrCommScada2 | DIGITAL | IOD_SS1_TCP | 199 | 00199 | ErrCommScada2
SS1ComSCADA2 | DIGITAL | IOD_SS1_TCP | 200 | 00200 | ComSCADA2
SS1ComSCADA3 | DIGITAL | IOD_SS1_TCP | 201 | 00201 | ComSCADA3
SS1DatumCasDan | INT | IOD_SS1_TCP | 1 | 40001 | DatumCas.Dan | BYTE
SS1DatumCasLeto | INT | IOD_SS1_TCP | 2 | 40002 | DatumCas.Leto | BYTE
SS1DatumCasLeto2 | INT | IOD_SS1_TCP | 3 | 40003 | DatumCas.Leto2
SS1DatumCasMesec | INT | IOD_SS1_TCP | 4 | 40004 | DatumCas.Mesec | BYTE
SS1DatumCasMinuta | INT | IOD_SS1_TCP | 5 | 40005 | DatumCas.Minuta | BYTE
SS1DatumCasSekunda | INT | IOD_SS1_TCP | 6 | 40006 | DatumCas.Sekunda | BYTE
SS1DatumCasUra | INT | IOD_SS1_TCP | 7 | 40007 | DatumCas.Ura | BYTE
SS1Klima1Vlazilec_Stanja | INT | IOD_SS1_TCP | 8 | 40008 | Klima[1].Vlazilec_Stanja | BYTE
SS1Klima2Vlazilec_Stanja | INT | IOD_SS1_TCP | 9 | 40009 | Klima[2].Vlazilec_Stanja | BYTE
SS1Klima3Vlazilec_Stanja | INT | IOD_SS1_TCP | 10 | 40010 | Klima[3].Vlazilec_Stanja | BYTE
SS1StUrZaPreklopKlim | INT | IOD_SS1_TCP | 11 | 40011 | StUrZaPreklopKlim
SS1UPSstatus_Prikaz_PanelSCADA | INT | IOD_SS1_TCP | 12 | 40012 | UPSstatus_Prikaz_PanelSCADA | BYTE
SS1UserCurrentLevel | INT | IOD_SS1_TCP | 13 | 40013 | UserCurrentLevel | BYTE
SS1AktualniSetPointTemp | REAL | IOD_SS1_TCP | 4001 | 44001 | AktualniSetPointTemp
SS1AktualniSetPointVlaga | REAL | IOD_SS1_TCP | 4003 | 44003 | AktualniSetPointVlaga
SS1Klima1NastMaxTemp | REAL | IOD_SS1_TCP | 4005 | 44005 | Klima[1].NastMaxTemp
SS1Klima1NastMaxVlaznost | REAL | IOD_SS1_TCP | 4007 | 44007 | Klima[1].NastMaxVlaznost
SS1Klima1NastMinTemp | REAL | IOD_SS1_TCP | 4009 | 44009 | Klima[1].NastMinTemp
SS1Klima1NastMinVlaznost | REAL | IOD_SS1_TCP | 4011 | 44011 | Klima[1].NastMinVlaznost
SS1Klima1NastTempProstora | REAL | IOD_SS1_TCP | 4013 | 44013 | Klima[1].NastTempProstora
SS1Klima1NastVlaznost | REAL | IOD_SS1_TCP | 4015 | 44015 | Klima[1].NastVlaznost
SS1Klima1Pritisk | REAL | IOD_SS1_TCP | 4017 | 44017 | Klima[1].Pritisk
SS1Klima1TemperaturaProstora | REAL | IOD_SS1_TCP | 4019 | 44019 | Klima[1].TemperaturaProstora
SS1Klima1VlaznostProstora | REAL | IOD_SS1_TCP | 4021 | 44021 | Klima[1].VlaznostProstora
SS1Klima2NastMaxTemp | REAL | IOD_SS1_TCP | 4023 | 44023 | Klima[2].NastMaxTemp
SS1Klima2NastMaxVlaznost | REAL | IOD_SS1_TCP | 4025 | 44025 | Klima[2].NastMaxVlaznost
SS1Klima2NastMinTemp | REAL | IOD_SS1_TCP | 4027 | 44027 | Klima[2].NastMinTemp
SS1Klima2NastMinVlaznost | REAL | IOD_SS1_TCP | 4029 | 44029 | Klima[2].NastMinVlaznost
SS1Klima2NastTempProstora | REAL | IOD_SS1_TCP | 4031 | 44031 | Klima[2].NastTempProstora
SS1Klima2NastVlaznost | REAL | IOD_SS1_TCP | 4033 | 44033 | Klima[2].NastVlaznost
SS1Klima2Pritisk | REAL | IOD_SS1_TCP | 4035 | 44035 | Klima[2].Pritisk
SS1Klima2TemperaturaProstora | REAL | IOD_SS1_TCP | 4037 | 44037 | Klima[2].TemperaturaProstora
SS1Klima2VlaznostProstora | REAL | IOD_SS1_TCP | 4039 | 44039 | Klima[2].VlaznostProstora
SS1Klima3NastMaxTemp | REAL | IOD_SS1_TCP | 4041 | 44041 | Klima[3].NastMaxTemp
SS1Klima3NastMaxVlaznost | REAL | IOD_SS1_TCP | 4043 | 44043 | Klima[3].NastMaxVlaznost
SS1Klima3NastMinTemp | REAL | IOD_SS1_TCP | 4045 | 44045 | Klima[3].NastMinTemp
SS1Klima3NastMinVlaznost | REAL | IOD_SS1_TCP | 4047 | 44047 | Klima[3].NastMinVlaznost
SS1Klima3NastTempProstora | REAL | IOD_SS1_TCP | 4049 | 44049 | Klima[3].NastTempProstora
SS1Klima3NastVlaznost | REAL | IOD_SS1_TCP | 4051 | 44051 | Klima[3].NastVlaznost
SS1Klima3Pritisk | REAL | IOD_SS1_TCP | 4053 | 44053 | Klima[3].Pritisk
SS1Klima3TemperaturaProstora | REAL | IOD_SS1_TCP | 4055 | 44055 | Klima[3].TemperaturaProstora
SS1Klima3VlaznostProstora | REAL | IOD_SS1_TCP | 4057 | 44057 | Klima[3].VlaznostProstora
SS1ObratUreKlim1 | REAL | IOD_SS1_TCP | 4059 | 44059 | ObratUreKlim[1]
SS1ObratUreKlim2 | REAL | IOD_SS1_TCP | 4061 | 44061 | ObratUreKlim[2]
SS1ObratUreKlim3 | REAL | IOD_SS1_TCP | 4063 | 44063 | ObratUreKlim[3]
SS1PMMActiveEnergyConsumed_kWh | REAL | IOD_SS1_TCP | 4065 | 44065 | PMM.ActiveEnergyConsumed_kWh
SS1PMMActivePowerPhaseA_kW | REAL | IOD_SS1_TCP | 4067 | 44067 | PMM.ActivePowerPhaseA_kW
SS1PMMActivePowerPhaseB_kW | REAL | IOD_SS1_TCP | 4069 | 44069 | PMM.ActivePowerPhaseB_kW
SS1PMMActivePowerPhaseC_kW | REAL | IOD_SS1_TCP | 4071 | 44071 | PMM.ActivePowerPhaseC_kW
SS1PMMAparentPowerPhaseA | REAL | IOD_SS1_TCP | 4073 | 44073 | PMM.AparentPowerPhaseA
SS1PMMAparentPowerPhaseB | REAL | IOD_SS1_TCP | 4075 | 44075 | PMM.AparentPowerPhaseB
SS1PMMAparentPowerPhaseC | REAL | IOD_SS1_TCP | 4077 | 44077 | PMM.AparentPowerPhaseC
SS1PMMAverageCurrent_A | REAL | IOD_SS1_TCP | 4079 | 44079 | PMM.AverageCurrent_A
SS1PMMAveragePhaseToNeutral_V | REAL | IOD_SS1_TCP | 4081 | 44081 | PMM.AveragePhaseToNeutral_V
SS1PMMAveragePhaseToPhase_V | REAL | IOD_SS1_TCP | 4083 | 44083 | PMM.AveragePhaseToPhase_V
SS1PMMCurrentInPhaseA_A | REAL | IOD_SS1_TCP | 4085 | 44085 | PMM.CurrentInPhaseA_A
SS1PMMCurrentInPhaseB_A | REAL | IOD_SS1_TCP | 4087 | 44087 | PMM.CurrentInPhaseB_A
SS1PMMCurrentInPhaseC_A | REAL | IOD_SS1_TCP | 4089 | 44089 | PMM.CurrentInPhaseC_A
SS1PMMFrequency_Hz | REAL | IOD_SS1_TCP | 4091 | 44091 | PMM.Frequency_Hz
SS1PMMPhase1Current10 | REAL | IOD_SS1_TCP | 4093 | 44093 | PMM.Phase[1].Current[10]
SS1PMMPhase1Current11 | REAL | IOD_SS1_TCP | 4095 | 44095 | PMM.Phase[1].Current[11]
SS1PMMPhase1Current12 | REAL | IOD_SS1_TCP | 4097 | 44097 | PMM.Phase[1].Current[12]
SS1PMMPhase1Current13 | REAL | IOD_SS1_TCP | 4099 | 44099 | PMM.Phase[1].Current[13]
SS1PMMPhase1Current14 | REAL | IOD_SS1_TCP | 4101 | 44101 | PMM.Phase[1].Current[14]
SS1PMMPhase1Current15 | REAL | IOD_SS1_TCP | 4103 | 44103 | PMM.Phase[1].Current[15]
SS1PMMPhase1Current16 | REAL | IOD_SS1_TCP | 4105 | 44105 | PMM.Phase[1].Current[16]
SS1PMMPhase1Current17 | REAL | IOD_SS1_TCP | 4107 | 44107 | PMM.Phase[1].Current[17]
SS1PMMPhase1Current18 | REAL | IOD_SS1_TCP | 4109 | 44109 | PMM.Phase[1].Current[18]
SS1PMMPhase1Current19 | REAL | IOD_SS1_TCP | 4111 | 44111 | PMM.Phase[1].Current[19]
SS1PMMPhase1Current1 | REAL | IOD_SS1_TCP | 4113 | 44113 | PMM.Phase[1].Current[1]
SS1PMMPhase1Current20 | REAL | IOD_SS1_TCP | 4115 | 44115 | PMM.Phase[1].Current[20]
SS1PMMPhase1Current21 | REAL | IOD_SS1_TCP | 4117 | 44117 | PMM.Phase[1].Current[21]
SS1PMMPhase1Current22 | REAL | IOD_SS1_TCP | 4119 | 44119 | PMM.Phase[1].Current[22]
SS1PMMPhase1Current23 | REAL | IOD_SS1_TCP | 4121 | 44121 | PMM.Phase[1].Current[23]
SS1PMMPhase1Current24 | REAL | IOD_SS1_TCP | 4123 | 44123 | PMM.Phase[1].Current[24]
SS1PMMPhase1Current25 | REAL | IOD_SS1_TCP | 4125 | 44125 | PMM.Phase[1].Current[25]
SS1PMMPhase1Current26 | REAL | IOD_SS1_TCP | 4127 | 44127 | PMM.Phase[1].Current[26]
SS1PMMPhase1Current27 | REAL | IOD_SS1_TCP | 4129 | 44129 | PMM.Phase[1].Current[27]
SS1PMMPhase1Current28 | REAL | IOD_SS1_TCP | 4131 | 44131 | PMM.Phase[1].Current[28]
SS1PMMPhase1Current29 | REAL | IOD_SS1_TCP | 4133 | 44133 | PMM.Phase[1].Current[29]
SS1PMMPhase1Current2 | REAL | IOD_SS1_TCP | 4135 | 44135 | PMM.Phase[1].Current[2]
SS1PMMPhase1Current30 | REAL | IOD_SS1_TCP | 4137 | 44137 | PMM.Phase[1].Current[30]
SS1PMMPhase1Current31 | REAL | IOD_SS1_TCP | 4139 | 44139 | PMM.Phase[1].Current[31]
SS1PMMPhase1Current32 | REAL | IOD_SS1_TCP | 4141 | 44141 | PMM.Phase[1].Current[32]
SS1PMMPhase1Current33 | REAL | IOD_SS1_TCP | 4143 | 44143 | PMM.Phase[1].Current[33]
SS1PMMPhase1Current34 | REAL | IOD_SS1_TCP | 4145 | 44145 | PMM.Phase[1].Current[34]
SS1PMMPhase1Current35 | REAL | IOD_SS1_TCP | 4147 | 44147 | PMM.Phase[1].Current[35]
SS1PMMPhase1Current36 | REAL | IOD_SS1_TCP | 4149 | 44149 | PMM.Phase[1].Current[36]
SS1PMMPhase1Current37 | REAL | IOD_SS1_TCP | 4151 | 44151 | PMM.Phase[1].Current[37]
SS1PMMPhase1Current38 | REAL | IOD_SS1_TCP | 4153 | 44153 | PMM.Phase[1].Current[38]
SS1PMMPhase1Current39 | REAL | IOD_SS1_TCP | 4155 | 44155 | PMM.Phase[1].Current[39]
SS1PMMPhase1Current3 | REAL | IOD_SS1_TCP | 4157 | 44157 | PMM.Phase[1].Current[3]
SS1PMMPhase1Current40 | REAL | IOD_SS1_TCP | 4159 | 44159 | PMM.Phase[1].Current[40]
SS1PMMPhase1Current41 | REAL | IOD_SS1_TCP | 4161 | 44161 | PMM.Phase[1].Current[41]
SS1PMMPhase1Current42 | REAL | IOD_SS1_TCP | 4163 | 44163 | PMM.Phase[1].Current[42]
SS1PMMPhase1Current4 | REAL | IOD_SS1_TCP | 4165 | 44165 | PMM.Phase[1].Current[4]
SS1PMMPhase1Current5 | REAL | IOD_SS1_TCP | 4167 | 44167 | PMM.Phase[1].Current[5]
SS1PMMPhase1Current6 | REAL | IOD_SS1_TCP | 4169 | 44169 | PMM.Phase[1].Current[6]
SS1PMMPhase1Current7 | REAL | IOD_SS1_TCP | 4171 | 44171 | PMM.Phase[1].Current[7]
SS1PMMPhase1Current8 | REAL | IOD_SS1_TCP | 4173 | 44173 | PMM.Phase[1].Current[8]
SS1PMMPhase1Current9 | REAL | IOD_SS1_TCP | 4175 | 44175 | PMM.Phase[1].Current[9]
SS1PMMPhase2Current10 | REAL | IOD_SS1_TCP | 4177 | 44177 | PMM.Phase[2].Current[10]
SS1PMMPhase2Current11 | REAL | IOD_SS1_TCP | 4179 | 44179 | PMM.Phase[2].Current[11]
SS1PMMPhase2Current12 | REAL | IOD_SS1_TCP | 4181 | 44181 | PMM.Phase[2].Current[12]
SS1PMMPhase2Current13 | REAL | IOD_SS1_TCP | 4183 | 44183 | PMM.Phase[2].Current[13]
SS1PMMPhase2Current14 | REAL | IOD_SS1_TCP | 4185 | 44185 | PMM.Phase[2].Current[14]
SS1PMMPhase2Current15 | REAL | IOD_SS1_TCP | 4187 | 44187 | PMM.Phase[2].Current[15]
SS1PMMPhase2Current16 | REAL | IOD_SS1_TCP | 4189 | 44189 | PMM.Phase[2].Current[16]
SS1PMMPhase2Current17 | REAL | IOD_SS1_TCP | 4191 | 44191 | PMM.Phase[2].Current[17]
SS1PMMPhase2Current18 | REAL | IOD_SS1_TCP | 4193 | 44193 | PMM.Phase[2].Current[18]
SS1PMMPhase2Current19 | REAL | IOD_SS1_TCP | 4195 | 44195 | PMM.Phase[2].Current[19]
SS1PMMPhase2Current1 | REAL | IOD_SS1_TCP | 4197 | 44197 | PMM.Phase[2].Current[1]
SS1PMMPhase2Current20 | REAL | IOD_SS1_TCP | 4199 | 44199 | PMM.Phase[2].Current[20]
SS1PMMPhase2Current21 | REAL | IOD_SS1_TCP | 4201 | 44201 | PMM.Phase[2].Current[21]
SS1PMMPhase2Current22 | REAL | IOD_SS1_TCP | 4203 | 44203 | PMM.Phase[2].Current[22]
SS1PMMPhase2Current23 | REAL | IOD_SS1_TCP | 4205 | 44205 | PMM.Phase[2].Current[23]
SS1PMMPhase2Current24 | REAL | IOD_SS1_TCP | 4207 | 44207 | PMM.Phase[2].Current[24]
SS1PMMPhase2Current25 | REAL | IOD_SS1_TCP | 4209 | 44209 | PMM.Phase[2].Current[25]
SS1PMMPhase2Current26 | REAL | IOD_SS1_TCP | 4211 | 44211 | PMM.Phase[2].Current[26]
SS1PMMPhase2Current27 | REAL | IOD_SS1_TCP | 4213 | 44213 | PMM.Phase[2].Current[27]
SS1PMMPhase2Current28 | REAL | IOD_SS1_TCP | 4215 | 44215 | PMM.Phase[2].Current[28]
SS1PMMPhase2Current29 | REAL | IOD_SS1_TCP | 4217 | 44217 | PMM.Phase[2].Current[29]
SS1PMMPhase2Current2 | REAL | IOD_SS1_TCP | 4219 | 44219 | PMM.Phase[2].Current[2]
SS1PMMPhase2Current30 | REAL | IOD_SS1_TCP | 4221 | 44221 | PMM.Phase[2].Current[30]
SS1PMMPhase2Current31 | REAL | IOD_SS1_TCP | 4223 | 44223 | PMM.Phase[2].Current[31]
SS1PMMPhase2Current32 | REAL | IOD_SS1_TCP | 4225 | 44225 | PMM.Phase[2].Current[32]
SS1PMMPhase2Current33 | REAL | IOD_SS1_TCP | 4227 | 44227 | PMM.Phase[2].Current[33]
SS1PMMPhase2Current34 | REAL | IOD_SS1_TCP | 4229 | 44229 | PMM.Phase[2].Current[34]
SS1PMMPhase2Current35 | REAL | IOD_SS1_TCP | 4231 | 44231 | PMM.Phase[2].Current[35]
SS1PMMPhase2Current36 | REAL | IOD_SS1_TCP | 4233 | 44233 | PMM.Phase[2].Current[36]
SS1PMMPhase2Current37 | REAL | IOD_SS1_TCP | 4235 | 44235 | PMM.Phase[2].Current[37]
SS1PMMPhase2Current38 | REAL | IOD_SS1_TCP | 4237 | 44237 | PMM.Phase[2].Current[38]
SS1PMMPhase2Current39 | REAL | IOD_SS1_TCP | 4239 | 44239 | PMM.Phase[2].Current[39]
SS1PMMPhase2Current3 | REAL | IOD_SS1_TCP | 4241 | 44241 | PMM.Phase[2].Current[3]
SS1PMMPhase2Current40 | REAL | IOD_SS1_TCP | 4243 | 44243 | PMM.Phase[2].Current[40]
SS1PMMPhase2Current41 | REAL | IOD_SS1_TCP | 4245 | 44245 | PMM.Phase[2].Current[41]
SS1PMMPhase2Current42 | REAL | IOD_SS1_TCP | 4247 | 44247 | PMM.Phase[2].Current[42]
SS1PMMPhase2Current4 | REAL | IOD_SS1_TCP | 4249 | 44249 | PMM.Phase[2].Current[4]
SS1PMMPhase2Current5 | REAL | IOD_SS1_TCP | 4251 | 44251 | PMM.Phase[2].Current[5]
SS1PMMPhase2Current6 | REAL | IOD_SS1_TCP | 4253 | 44253 | PMM.Phase[2].Current[6]
SS1PMMPhase2Current7 | REAL | IOD_SS1_TCP | 4255 | 44255 | PMM.Phase[2].Current[7]
SS1PMMPhase2Current8 | REAL | IOD_SS1_TCP | 4257 | 44257 | PMM.Phase[2].Current[8]
SS1PMMPhase2Current9 | REAL | IOD_SS1_TCP | 4259 | 44259 | PMM.Phase[2].Current[9]
SS1PMMPhase3Current10 | REAL | IOD_SS1_TCP | 4261 | 44261 | PMM.Phase[3].Current[10]
SS1PMMPhase3Current11 | REAL | IOD_SS1_TCP | 4263 | 44263 | PMM.Phase[3].Current[11]
SS1PMMPhase3Current12 | REAL | IOD_SS1_TCP | 4265 | 44265 | PMM.Phase[3].Current[12]
SS1PMMPhase3Current13 | REAL | IOD_SS1_TCP | 4267 | 44267 | PMM.Phase[3].Current[13]
SS1PMMPhase3Current14 | REAL | IOD_SS1_TCP | 4269 | 44269 | PMM.Phase[3].Current[14]
SS1PMMPhase3Current15 | REAL | IOD_SS1_TCP | 4271 | 44271 | PMM.Phase[3].Current[15]
SS1PMMPhase3Current16 | REAL | IOD_SS1_TCP | 4273 | 44273 | PMM.Phase[3].Current[16]
SS1PMMPhase3Current17 | REAL | IOD_SS1_TCP | 4275 | 44275 | PMM.Phase[3].Current[17]
SS1PMMPhase3Current18 | REAL | IOD_SS1_TCP | 4277 | 44277 | PMM.Phase[3].Current[18]
SS1PMMPhase3Current19 | REAL | IOD_SS1_TCP | 4279 | 44279 | PMM.Phase[3].Current[19]
SS1PMMPhase3Current1 | REAL | IOD_SS1_TCP | 4281 | 44281 | PMM.Phase[3].Current[1]
SS1PMMPhase3Current20 | REAL | IOD_SS1_TCP | 4283 | 44283 | PMM.Phase[3].Current[20]
SS1PMMPhase3Current21 | REAL | IOD_SS1_TCP | 4285 | 44285 | PMM.Phase[3].Current[21]
SS1PMMPhase3Current22 | REAL | IOD_SS1_TCP | 4287 | 44287 | PMM.Phase[3].Current[22]
SS1PMMPhase3Current23 | REAL | IOD_SS1_TCP | 4289 | 44289 | PMM.Phase[3].Current[23]
SS1PMMPhase3Current24 | REAL | IOD_SS1_TCP | 4291 | 44291 | PMM.Phase[3].Current[24]
SS1PMMPhase3Current25 | REAL | IOD_SS1_TCP | 4293 | 44293 | PMM.Phase[3].Current[25]
SS1PMMPhase3Current26 | REAL | IOD_SS1_TCP | 4295 | 44295 | PMM.Phase[3].Current[26]
SS1PMMPhase3Current27 | REAL | IOD_SS1_TCP | 4297 | 44297 | PMM.Phase[3].Current[27]
SS1PMMPhase3Current28 | REAL | IOD_SS1_TCP | 4299 | 44299 | PMM.Phase[3].Current[28]
SS1PMMPhase3Current29 | REAL | IOD_SS1_TCP | 4301 | 44301 | PMM.Phase[3].Current[29]
SS1PMMPhase3Current2 | REAL | IOD_SS1_TCP | 4303 | 44303 | PMM.Phase[3].Current[2]
SS1PMMPhase3Current30 | REAL | IOD_SS1_TCP | 4305 | 44305 | PMM.Phase[3].Current[30]
SS1PMMPhase3Current31 | REAL | IOD_SS1_TCP | 4307 | 44307 | PMM.Phase[3].Current[31]
SS1PMMPhase3Current32 | REAL | IOD_SS1_TCP | 4309 | 44309 | PMM.Phase[3].Current[32]
SS1PMMPhase3Current33 | REAL | IOD_SS1_TCP | 4311 | 44311 | PMM.Phase[3].Current[33]
SS1PMMPhase3Current34 | REAL | IOD_SS1_TCP | 4313 | 44313 | PMM.Phase[3].Current[34]
SS1PMMPhase3Current35 | REAL | IOD_SS1_TCP | 4315 | 44315 | PMM.Phase[3].Current[35]
SS1PMMPhase3Current36 | REAL | IOD_SS1_TCP | 4317 | 44317 | PMM.Phase[3].Current[36]
SS1PMMPhase3Current37 | REAL | IOD_SS1_TCP | 4319 | 44319 | PMM.Phase[3].Current[37]
SS1PMMPhase3Current38 | REAL | IOD_SS1_TCP | 4321 | 44321 | PMM.Phase[3].Current[38]
SS1PMMPhase3Current39 | REAL | IOD_SS1_TCP | 4323 | 44323 | PMM.Phase[3].Current[39]
SS1PMMPhase3Current3 | REAL | IOD_SS1_TCP | 4325 | 44325 | PMM.Phase[3].Current[3]
SS1PMMPhase3Current40 | REAL | IOD_SS1_TCP | 4327 | 44327 | PMM.Phase[3].Current[40]
SS1PMMPhase3Current41 | REAL | IOD_SS1_TCP | 4329 | 44329 | PMM.Phase[3].Current[41]
SS1PMMPhase3Current42 | REAL | IOD_SS1_TCP | 4331 | 44331 | PMM.Phase[3].Current[42]
SS1PMMPhase3Current4 | REAL | IOD_SS1_TCP | 4333 | 44333 | PMM.Phase[3].Current[4]
SS1PMMPhase3Current5 | REAL | IOD_SS1_TCP | 4335 | 44335 | PMM.Phase[3].Current[5]
SS1PMMPhase3Current6 | REAL | IOD_SS1_TCP | 4337 | 44337 | PMM.Phase[3].Current[6]
SS1PMMPhase3Current7 | REAL | IOD_SS1_TCP | 4339 | 44339 | PMM.Phase[3].Current[7]
SS1PMMPhase3Current8 | REAL | IOD_SS1_TCP | 4341 | 44341 | PMM.Phase[3].Current[8]
SS1PMMPhase3Current9 | REAL | IOD_SS1_TCP | 4343 | 44343 | PMM.Phase[3].Current[9]
SS1PMMPowerFactorSys | REAL | IOD_SS1_TCP | 4345 | 44345 | PMM.PowerFactorSys
SS1PMMReactiveEnergyConsumed_kVARh | REAL | IOD_SS1_TCP | 4347 | 44347 | PMM.ReactiveEnergyConsumed_kVARh
SS1PMMReactivePowerPhaseA | REAL | IOD_SS1_TCP | 4349 | 44349 | PMM.ReactivePowerPhaseA
SS1PMMReactivePowerPhaseB | REAL | IOD_SS1_TCP | 4351 | 44351 | PMM.ReactivePowerPhaseB
SS1PMMReactivePowerPhaseC | REAL | IOD_SS1_TCP | 4353 | 44353 | PMM.ReactivePowerPhaseC
SS1PMMTotalActivePower_kW | REAL | IOD_SS1_TCP | 4355 | 44355 | PMM.TotalActivePower_kW
SS1PMMTotalAparentPower_kVA | REAL | IOD_SS1_TCP | 4357 | 44357 | PMM.TotalAparentPower_kVA
SS1PMMTotalPowerFactor | REAL | IOD_SS1_TCP | 4359 | 44359 | PMM.TotalPowerFactor
SS1PMMTotalReactivePower_kVAR | REAL | IOD_SS1_TCP | 4361 | 44361 | PMM.TotalReactivePower_kVAR
SS1PMMVirA_fsys | REAL | IOD_SS1_TCP | 4363 | 44363 | PMM.VirA_fsys
SS1PMMVirA_Isys | REAL | IOD_SS1_TCP | 4365 | 44365 | PMM.VirA_Isys
SS1PMMVirA_PFsys | REAL | IOD_SS1_TCP | 4367 | 44367 | PMM.VirA_PFsys
SS1PMMVirA_Psys | REAL | IOD_SS1_TCP | 4369 | 44369 | PMM.VirA_Psys
SS1PMMVirA_Qsys | REAL | IOD_SS1_TCP | 4371 | 44371 | PMM.VirA_Qsys
SS1PMMVirA_Ssys | REAL | IOD_SS1_TCP | 4373 | 44373 | PMM.VirA_Ssys
SS1PMMVirA_Usys | REAL | IOD_SS1_TCP | 4375 | 44375 | PMM.VirA_Usys
SS1PMMVirB_fsys | REAL | IOD_SS1_TCP | 4377 | 44377 | PMM.VirB_fsys
SS1PMMVirB_Isys | REAL | IOD_SS1_TCP | 4379 | 44379 | PMM.VirB_Isys
SS1PMMVirB_PFsys | REAL | IOD_SS1_TCP | 4381 | 44381 | PMM.VirB_PFsys
SS1PMMVirB_Psys | REAL | IOD_SS1_TCP | 4383 | 44383 | PMM.VirB_Psys
SS1PMMVirB_Qsys | REAL | IOD_SS1_TCP | 4385 | 44385 | PMM.VirB_Qsys
SS1PMMVirB_Ssys | REAL | IOD_SS1_TCP | 4387 | 44387 | PMM.VirB_Ssys
SS1PMMVirB_Usys | REAL | IOD_SS1_TCP | 4389 | 44389 | PMM.VirB_Usys
SS1PMMVirBActiveEnergyConsumed_kWh | REAL | IOD_SS1_TCP | 4391 | 44391 | PMM.VirBActiveEnergyConsumed_kWh
SS1PMMVirBActivePowerPhaseA_kW | REAL | IOD_SS1_TCP | 4393 | 44393 | PMM.VirBActivePowerPhaseA_kW
SS1PMMVirBActivePowerPhaseB_kW | REAL | IOD_SS1_TCP | 4395 | 44395 | PMM.VirBActivePowerPhaseB_kW
SS1PMMVirBActivePowerPhaseC_kW | REAL | IOD_SS1_TCP | 4397 | 44397 | PMM.VirBActivePowerPhaseC_kW
SS1PMMVirBAparentPowerPhaseA | REAL | IOD_SS1_TCP | 4399 | 44399 | PMM.VirBAparentPowerPhaseA
SS1PMMVirBAparentPowerPhaseB | REAL | IOD_SS1_TCP | 4401 | 44401 | PMM.VirBAparentPowerPhaseB
SS1PMMVirBAparentPowerPhaseC | REAL | IOD_SS1_TCP | 4403 | 44403 | PMM.VirBAparentPowerPhaseC
SS1PMMVirBAverageCurrent_A | REAL | IOD_SS1_TCP | 4405 | 44405 | PMM.VirBAverageCurrent_A
SS1PMMVirBAveragePhaseToNeutral_V | REAL | IOD_SS1_TCP | 4407 | 44407 | PMM.VirBAveragePhaseToNeutral_V
SS1PMMVirBAveragePhaseToPhase_V | REAL | IOD_SS1_TCP | 4409 | 44409 | PMM.VirBAveragePhaseToPhase_V
SS1PMMVirBCurrentInPhaseA_A | REAL | IOD_SS1_TCP | 4411 | 44411 | PMM.VirBCurrentInPhaseA_A
SS1PMMVirBCurrentInPhaseB_A | REAL | IOD_SS1_TCP | 4413 | 44413 | PMM.VirBCurrentInPhaseB_A
SS1PMMVirBCurrentInPhaseC_A | REAL | IOD_SS1_TCP | 4415 | 44415 | PMM.VirBCurrentInPhaseC_A
SS1PMMVirBFrequency_Hz | REAL | IOD_SS1_TCP | 4417 | 44417 | PMM.VirBFrequency_Hz
SS1PMMVirBPowerFactorSys | REAL | IOD_SS1_TCP | 4419 | 44419 | PMM.VirBPowerFactorSys
SS1PMMVirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS1_TCP | 4421 | 44421 | PMM.VirBReactiveEnergyConsumed_kWh
SS1PMMVirBReactivePowerPhaseA | REAL | IOD_SS1_TCP | 4423 | 44423 | PMM.VirBReactivePowerPhaseA
SS1PMMVirBReactivePowerPhaseB | REAL | IOD_SS1_TCP | 4425 | 44425 | PMM.VirBReactivePowerPhaseB
SS1PMMVirBReactivePowerPhaseC | REAL | IOD_SS1_TCP | 4427 | 44427 | PMM.VirBReactivePowerPhaseC
SS1PMMVirBTotalActivePower_kW | REAL | IOD_SS1_TCP | 4429 | 44429 | PMM.VirBTotalActivePower_kW
SS1PMMVirBTotalAparentPower_kVA | REAL | IOD_SS1_TCP | 4431 | 44431 | PMM.VirBTotalAparentPower_kVA
SS1PMMVirBTotalPowerFactor | REAL | IOD_SS1_TCP | 4433 | 44433 | PMM.VirBTotalPowerFactor
SS1PMMVirBTotalReactivePower_kVAR | REAL | IOD_SS1_TCP | 4435 | 44435 | PMM.VirBTotalReactivePower_kVAR
SS1PMMVirBVoltageBetweenPhaseAB_V | REAL | IOD_SS1_TCP | 4437 | 44437 | PMM.VirBVoltageBetweenPhaseAB_V
SS1PMMVirBVoltageBetweenPhaseAN_V | REAL | IOD_SS1_TCP | 4439 | 44439 | PMM.VirBVoltageBetweenPhaseAN_V
SS1PMMVirBVoltageBetweenPhaseBC_V | REAL | IOD_SS1_TCP | 4441 | 44441 | PMM.VirBVoltageBetweenPhaseBC_V
SS1PMMVirBVoltageBetweenPhaseBN_V | REAL | IOD_SS1_TCP | 4443 | 44443 | PMM.VirBVoltageBetweenPhaseBN_V
SS1PMMVirBVoltageBetweenPhaseCA_V | REAL | IOD_SS1_TCP | 4445 | 44445 | PMM.VirBVoltageBetweenPhaseCA_V
SS1PMMVirBVoltageBetweenPhaseCN_V | REAL | IOD_SS1_TCP | 4447 | 44447 | PMM.VirBVoltageBetweenPhaseCN_V
SS1PMMVoltageBetweenPhaseAB_V | REAL | IOD_SS1_TCP | 4449 | 44449 | PMM.VoltageBetweenPhaseAB_V
SS1PMMVoltageBetweenPhaseAN_V | REAL | IOD_SS1_TCP | 4451 | 44451 | PMM.VoltageBetweenPhaseAN_V
SS1PMMVoltageBetweenPhaseBC_V | REAL | IOD_SS1_TCP | 4453 | 44453 | PMM.VoltageBetweenPhaseBC_V
SS1PMMVoltageBetweenPhaseBN_V | REAL | IOD_SS1_TCP | 4455 | 44455 | PMM.VoltageBetweenPhaseBN_V
SS1PMMVoltageBetweenPhaseCA_V | REAL | IOD_SS1_TCP | 4457 | 44457 | PMM.VoltageBetweenPhaseCA_V
SS1PMMVoltageBetweenPhaseCN_V | REAL | IOD_SS1_TCP | 4459 | 44459 | PMM.VoltageBetweenPhaseCN_V
SS1SKTemp1 | REAL | IOD_SS1_TCP | 4461 | 44461 | SKTemp1
SS1SKTemp2 | REAL | IOD_SS1_TCP | 4463 | 44463 | SKTemp2
SS1SKTemp3 | REAL | IOD_SS1_TCP | 4465 | 44465 | SKTemp3
SS1SKTempKontrSoba | REAL | IOD_SS1_TCP | 4467 | 44467 | SKTempKontrSoba
SS1SKTempLinkProstor | REAL | IOD_SS1_TCP | 4469 | 44469 | SKTempLinkProstor
SS1SKTempServSoba1Povpr | REAL | IOD_SS1_TCP | 4471 | 44471 | SKTempServSoba1Povpr
SS1SKVlaga1 | REAL | IOD_SS1_TCP | 4473 | 44473 | SKVlaga1
SS1SKVlaga2 | REAL | IOD_SS1_TCP | 4475 | 44475 | SKVlaga2
SS1SKVlaga3 | REAL | IOD_SS1_TCP | 4477 | 44477 | SKVlaga3
SS1SKVlagaKontrSoba | REAL | IOD_SS1_TCP | 4479 | 44479 | SKVlagaKontrSoba
SS1SKVlagaLinkProstor | REAL | IOD_SS1_TCP | 4481 | 44481 | SKVlagaLinkProstor
SS1TempZaAlarmTIA123 | REAL | IOD_SS1_TCP | 4483 | 44483 | TempZaAlarmTIA123
SS1TempZaAlarmTIA4 | REAL | IOD_SS1_TCP | 4485 | 44485 | TempZaAlarmTIA4
SS1TempZaAlarmTIA5 | REAL | IOD_SS1_TCP | 4487 | 44487 | TempZaAlarmTIA5
SS1TempZaVklopObehKlim | REAL | IOD_SS1_TCP | 4489 | 44489 | TempZaVklopObehKlim
SS1UserName | STRING | IOD_SS1_TCP | 5001 | 45001[15] | UserName
SS1PMMAlarmPhase1C01_16_60to80 | UINT | IOD_SS1_TCP | 6001 | 46001 | PMM.AlarmPhase[1].C01_16_60to80
SS1PMMAlarmPhase1C01_16_over80 | UINT | IOD_SS1_TCP | 6002 | 46002 | PMM.AlarmPhase[1].C01_16_over80
SS1PMMAlarmPhase1C17_32_60to80 | UINT | IOD_SS1_TCP | 6003 | 46003 | PMM.AlarmPhase[1].C17_32_60to80
SS1PMMAlarmPhase1C17_32_over80 | UINT | IOD_SS1_TCP | 6004 | 46004 | PMM.AlarmPhase[1].C17_32_over80
SS1PMMAlarmPhase1C33_42_60to80 | UINT | IOD_SS1_TCP | 6005 | 46005 | PMM.AlarmPhase[1].C33_42_60to80
SS1PMMAlarmPhase1C33_42_over80 | UINT | IOD_SS1_TCP | 6006 | 46006 | PMM.AlarmPhase[1].C33_42_over80
SS1PMMAlarmPhase2C01_16_60to80 | UINT | IOD_SS1_TCP | 6007 | 46007 | PMM.AlarmPhase[2].C01_16_60to80
SS1PMMAlarmPhase2C01_16_over80 | UINT | IOD_SS1_TCP | 6008 | 46008 | PMM.AlarmPhase[2].C01_16_over80
SS1PMMAlarmPhase2C17_32_60to80 | UINT | IOD_SS1_TCP | 6009 | 46009 | PMM.AlarmPhase[2].C17_32_60to80
SS1PMMAlarmPhase2C17_32_over80 | UINT | IOD_SS1_TCP | 6010 | 46010 | PMM.AlarmPhase[2].C17_32_over80
SS1PMMAlarmPhase2C33_42_60to80 | UINT | IOD_SS1_TCP | 6011 | 46011 | PMM.AlarmPhase[2].C33_42_60to80
SS1PMMAlarmPhase2C33_42_over80 | UINT | IOD_SS1_TCP | 6012 | 46012 | PMM.AlarmPhase[2].C33_42_over80
SS1PMMAlarmPhase3C01_16_60to80 | UINT | IOD_SS1_TCP | 6013 | 46013 | PMM.AlarmPhase[3].C01_16_60to80
SS1PMMAlarmPhase3C01_16_over80 | UINT | IOD_SS1_TCP | 6014 | 46014 | PMM.AlarmPhase[3].C01_16_over80
SS1PMMAlarmPhase3C17_32_60to80 | UINT | IOD_SS1_TCP | 6015 | 46015 | PMM.AlarmPhase[3].C17_32_60to80
SS1PMMAlarmPhase3C17_32_over80 | UINT | IOD_SS1_TCP | 6016 | 46016 | PMM.AlarmPhase[3].C17_32_over80
SS1PMMAlarmPhase3C33_42_60to80 | UINT | IOD_SS1_TCP | 6017 | 46017 | PMM.AlarmPhase[3].C33_42_60to80
SS1PMMAlarmPhase3C33_42_over80 | UINT | IOD_SS1_TCP | 6018 | 46018 | PMM.AlarmPhase[3].C33_42_over80
SS1kom_nast_cas_izpada | UINT | IOD_SS1_TCP | 6019 | 46019 | kom_nast_cas_izpada

## variable_new
SS1Pulzi1s | DIGITAL | IOD_SS1_disk | D1
SS1PMMPhase1Current1_med60in80 | DIGITAL | IOD_SS1_disk | D2
SS1PMMPhase1Current2_med60in80 | DIGITAL | IOD_SS1_disk | D3
SS1PMMPhase1Current3_med60in80 | DIGITAL | IOD_SS1_disk | D4
SS1PMMPhase1Current4_med60in80 | DIGITAL | IOD_SS1_disk | D5
SS1PMMPhase1Current5_med60in80 | DIGITAL | IOD_SS1_disk | D6
SS1PMMPhase1Current6_med60in80 | DIGITAL | IOD_SS1_disk | D7
SS1PMMPhase1Current7_med60in80 | DIGITAL | IOD_SS1_disk | D8
SS1PMMPhase1Current8_med60in80 | DIGITAL | IOD_SS1_disk | D9
SS1PMMPhase1Current9_med60in80 | DIGITAL | IOD_SS1_disk | D10
SS1PMMPhase1Current10_med60in80 | DIGITAL | IOD_SS1_disk | D11
SS1PMMPhase1Current11_med60in80 | DIGITAL | IOD_SS1_disk | D12
SS1PMMPhase1Current12_med60in80 | DIGITAL | IOD_SS1_disk | D13
SS1PMMPhase1Current13_med60in80 | DIGITAL | IOD_SS1_disk | D14
SS1PMMPhase1Current14_med60in80 | DIGITAL | IOD_SS1_disk | D15
SS1PMMPhase1Current15_med60in80 | DIGITAL | IOD_SS1_disk | D16
SS1PMMPhase1Current16_med60in80 | DIGITAL | IOD_SS1_disk | D17
SS1PMMPhase1Current17_med60in80 | DIGITAL | IOD_SS1_disk | D18
SS1PMMPhase1Current18_med60in80 | DIGITAL | IOD_SS1_disk | D19
SS1PMMPhase1Current19_med60in80 | DIGITAL | IOD_SS1_disk | D20
SS1PMMPhase1Current20_med60in80 | DIGITAL | IOD_SS1_disk | D21
SS1PMMPhase1Current21_med60in80 | DIGITAL | IOD_SS1_disk | D22
SS1PMMPhase1Current22_med60in80 | DIGITAL | IOD_SS1_disk | D23
SS1PMMPhase1Current23_med60in80 | DIGITAL | IOD_SS1_disk | D24
SS1PMMPhase1Current24_med60in80 | DIGITAL | IOD_SS1_disk | D25
SS1PMMPhase1Current25_med60in80 | DIGITAL | IOD_SS1_disk | D26
SS1PMMPhase1Current26_med60in80 | DIGITAL | IOD_SS1_disk | D27
SS1PMMPhase1Current27_med60in80 | DIGITAL | IOD_SS1_disk | D28
SS1PMMPhase1Current28_med60in80 | DIGITAL | IOD_SS1_disk | D29
SS1PMMPhase1Current29_med60in80 | DIGITAL | IOD_SS1_disk | D30
SS1PMMPhase1Current30_med60in80 | DIGITAL | IOD_SS1_disk | D31
SS1PMMPhase1Current31_med60in80 | DIGITAL | IOD_SS1_disk | D32
SS1PMMPhase1Current32_med60in80 | DIGITAL | IOD_SS1_disk | D33
SS1PMMPhase1Current33_med60in80 | DIGITAL | IOD_SS1_disk | D34
SS1PMMPhase1Current34_med60in80 | DIGITAL | IOD_SS1_disk | D35
SS1PMMPhase1Current35_med60in80 | DIGITAL | IOD_SS1_disk | D36
SS1PMMPhase1Current36_med60in80 | DIGITAL | IOD_SS1_disk | D37
SS1PMMPhase1Current37_med60in80 | DIGITAL | IOD_SS1_disk | D38
SS1PMMPhase1Current38_med60in80 | DIGITAL | IOD_SS1_disk | D39
SS1PMMPhase1Current39_med60in80 | DIGITAL | IOD_SS1_disk | D40
SS1PMMPhase1Current40_med60in80 | DIGITAL | IOD_SS1_disk | D41
SS1PMMPhase1Current41_med60in80 | DIGITAL | IOD_SS1_disk | D42
SS1PMMPhase1Current42_med60in80 | DIGITAL | IOD_SS1_disk | D43
SS1PMMPhase1Current1_nad80 | DIGITAL | IOD_SS1_disk | D44
SS1PMMPhase1Current2_nad80 | DIGITAL | IOD_SS1_disk | D45
SS1PMMPhase1Current3_nad80 | DIGITAL | IOD_SS1_disk | D46
SS1PMMPhase1Current4_nad80 | DIGITAL | IOD_SS1_disk | D47
SS1PMMPhase1Current5_nad80 | DIGITAL | IOD_SS1_disk | D48
SS1PMMPhase1Current6_nad80 | DIGITAL | IOD_SS1_disk | D49
SS1PMMPhase1Current7_nad80 | DIGITAL | IOD_SS1_disk | D50
SS1PMMPhase1Current8_nad80 | DIGITAL | IOD_SS1_disk | D51
SS1PMMPhase1Current9_nad80 | DIGITAL | IOD_SS1_disk | D52
SS1PMMPhase1Current10_nad80 | DIGITAL | IOD_SS1_disk | D53
SS1PMMPhase1Current11_nad80 | DIGITAL | IOD_SS1_disk | D54
SS1PMMPhase1Current12_nad80 | DIGITAL | IOD_SS1_disk | D55
SS1PMMPhase1Current13_nad80 | DIGITAL | IOD_SS1_disk | D56
SS1PMMPhase1Current14_nad80 | DIGITAL | IOD_SS1_disk | D57
SS1PMMPhase1Current15_nad80 | DIGITAL | IOD_SS1_disk | D58
SS1PMMPhase1Current16_nad80 | DIGITAL | IOD_SS1_disk | D59
SS1PMMPhase1Current17_nad80 | DIGITAL | IOD_SS1_disk | D60
SS1PMMPhase1Current18_nad80 | DIGITAL | IOD_SS1_disk | D61
SS1PMMPhase1Current19_nad80 | DIGITAL | IOD_SS1_disk | D62
SS1PMMPhase1Current20_nad80 | DIGITAL | IOD_SS1_disk | D63
SS1PMMPhase1Current21_nad80 | DIGITAL | IOD_SS1_disk | D64
SS1PMMPhase1Current22_nad80 | DIGITAL | IOD_SS1_disk | D65
SS1PMMPhase1Current23_nad80 | DIGITAL | IOD_SS1_disk | D66
SS1PMMPhase1Current24_nad80 | DIGITAL | IOD_SS1_disk | D67
SS1PMMPhase1Current25_nad80 | DIGITAL | IOD_SS1_disk | D68
SS1PMMPhase1Current26_nad80 | DIGITAL | IOD_SS1_disk | D69
SS1PMMPhase1Current27_nad80 | DIGITAL | IOD_SS1_disk | D70
SS1PMMPhase1Current28_nad80 | DIGITAL | IOD_SS1_disk | D71
SS1PMMPhase1Current29_nad80 | DIGITAL | IOD_SS1_disk | D72
SS1PMMPhase1Current30_nad80 | DIGITAL | IOD_SS1_disk | D73
SS1PMMPhase1Current31_nad80 | DIGITAL | IOD_SS1_disk | D74
SS1PMMPhase1Current32_nad80 | DIGITAL | IOD_SS1_disk | D75
SS1PMMPhase1Current33_nad80 | DIGITAL | IOD_SS1_disk | D76
SS1PMMPhase1Current34_nad80 | DIGITAL | IOD_SS1_disk | D77
SS1PMMPhase1Current35_nad80 | DIGITAL | IOD_SS1_disk | D78
SS1PMMPhase1Current36_nad80 | DIGITAL | IOD_SS1_disk | D79
SS1PMMPhase1Current37_nad80 | DIGITAL | IOD_SS1_disk | D80
SS1PMMPhase1Current38_nad80 | DIGITAL | IOD_SS1_disk | D81
SS1PMMPhase1Current39_nad80 | DIGITAL | IOD_SS1_disk | D82
SS1PMMPhase1Current40_nad80 | DIGITAL | IOD_SS1_disk | D83
SS1PMMPhase1Current41_nad80 | DIGITAL | IOD_SS1_disk | D84
SS1PMMPhase1Current42_nad80 | DIGITAL | IOD_SS1_disk | D85
SS1PMMPhase2Current1_nad80 | DIGITAL | IOD_SS1_disk | D86
SS1PMMPhase2Current2_nad80 | DIGITAL | IOD_SS1_disk | D87
SS1PMMPhase2Current3_nad80 | DIGITAL | IOD_SS1_disk | D88
SS1PMMPhase2Current4_nad80 | DIGITAL | IOD_SS1_disk | D89
SS1PMMPhase2Current5_nad80 | DIGITAL | IOD_SS1_disk | D90
SS1PMMPhase2Current6_nad80 | DIGITAL | IOD_SS1_disk | D91
SS1PMMPhase2Current7_nad80 | DIGITAL | IOD_SS1_disk | D92
SS1PMMPhase2Current8_nad80 | DIGITAL | IOD_SS1_disk | D93
SS1PMMPhase2Current9_nad80 | DIGITAL | IOD_SS1_disk | D94
SS1PMMPhase2Current10_nad80 | DIGITAL | IOD_SS1_disk | D95
SS1PMMPhase2Current11_nad80 | DIGITAL | IOD_SS1_disk | D96
SS1PMMPhase2Current12_nad80 | DIGITAL | IOD_SS1_disk | D97
SS1PMMPhase2Current13_nad80 | DIGITAL | IOD_SS1_disk | D98
SS1PMMPhase2Current14_nad80 | DIGITAL | IOD_SS1_disk | D99
SS1PMMPhase2Current15_nad80 | DIGITAL | IOD_SS1_disk | D100
SS1PMMPhase2Current16_nad80 | DIGITAL | IOD_SS1_disk | D101
SS1PMMPhase2Current17_nad80 | DIGITAL | IOD_SS1_disk | D102
SS1PMMPhase2Current18_nad80 | DIGITAL | IOD_SS1_disk | D103
SS1PMMPhase2Current19_nad80 | DIGITAL | IOD_SS1_disk | D104
SS1PMMPhase2Current20_nad80 | DIGITAL | IOD_SS1_disk | D105
SS1PMMPhase2Current21_nad80 | DIGITAL | IOD_SS1_disk | D106
SS1PMMPhase2Current22_nad80 | DIGITAL | IOD_SS1_disk | D107
SS1PMMPhase2Current23_nad80 | DIGITAL | IOD_SS1_disk | D108
SS1PMMPhase2Current24_nad80 | DIGITAL | IOD_SS1_disk | D109
SS1PMMPhase2Current25_nad80 | DIGITAL | IOD_SS1_disk | D110
SS1PMMPhase2Current26_nad80 | DIGITAL | IOD_SS1_disk | D111
SS1PMMPhase2Current27_nad80 | DIGITAL | IOD_SS1_disk | D112
SS1PMMPhase2Current28_nad80 | DIGITAL | IOD_SS1_disk | D113
SS1PMMPhase2Current29_nad80 | DIGITAL | IOD_SS1_disk | D114
SS1PMMPhase2Current30_nad80 | DIGITAL | IOD_SS1_disk | D115
SS1PMMPhase2Current31_nad80 | DIGITAL | IOD_SS1_disk | D116
SS1PMMPhase2Current32_nad80 | DIGITAL | IOD_SS1_disk | D117
SS1PMMPhase2Current33_nad80 | DIGITAL | IOD_SS1_disk | D118
SS1PMMPhase2Current34_nad80 | DIGITAL | IOD_SS1_disk | D119
SS1PMMPhase2Current35_nad80 | DIGITAL | IOD_SS1_disk | D120
SS1PMMPhase2Current36_nad80 | DIGITAL | IOD_SS1_disk | D121
SS1PMMPhase2Current37_nad80 | DIGITAL | IOD_SS1_disk | D122
SS1PMMPhase2Current38_nad80 | DIGITAL | IOD_SS1_disk | D123
SS1PMMPhase2Current39_nad80 | DIGITAL | IOD_SS1_disk | D124
SS1PMMPhase2Current40_nad80 | DIGITAL | IOD_SS1_disk | D125
SS1PMMPhase2Current41_nad80 | DIGITAL | IOD_SS1_disk | D126
SS1PMMPhase2Current42_nad80 | DIGITAL | IOD_SS1_disk | D127
SS1PMMPhase3Current1_nad80 | DIGITAL | IOD_SS1_disk | D128
SS1PMMPhase3Current2_nad80 | DIGITAL | IOD_SS1_disk | D129
SS1PMMPhase3Current3_nad80 | DIGITAL | IOD_SS1_disk | D130
SS1PMMPhase3Current4_nad80 | DIGITAL | IOD_SS1_disk | D131
SS1PMMPhase3Current5_nad80 | DIGITAL | IOD_SS1_disk | D132
SS1PMMPhase3Current6_nad80 | DIGITAL | IOD_SS1_disk | D133
SS1PMMPhase3Current7_nad80 | DIGITAL | IOD_SS1_disk | D134
SS1PMMPhase3Current8_nad80 | DIGITAL | IOD_SS1_disk | D135
SS1PMMPhase3Current9_nad80 | DIGITAL | IOD_SS1_disk | D136
SS1PMMPhase3Current10_nad80 | DIGITAL | IOD_SS1_disk | D137
SS1PMMPhase3Current11_nad80 | DIGITAL | IOD_SS1_disk | D138
SS1PMMPhase3Current12_nad80 | DIGITAL | IOD_SS1_disk | D139
SS1PMMPhase3Current13_nad80 | DIGITAL | IOD_SS1_disk | D140
SS1PMMPhase3Current14_nad80 | DIGITAL | IOD_SS1_disk | D141
SS1PMMPhase3Current15_nad80 | DIGITAL | IOD_SS1_disk | D142
SS1PMMPhase3Current16_nad80 | DIGITAL | IOD_SS1_disk | D143
SS1PMMPhase3Current17_nad80 | DIGITAL | IOD_SS1_disk | D144
SS1PMMPhase3Current18_nad80 | DIGITAL | IOD_SS1_disk | D145
SS1PMMPhase3Current19_nad80 | DIGITAL | IOD_SS1_disk | D146
SS1PMMPhase3Current20_nad80 | DIGITAL | IOD_SS1_disk | D147
SS1PMMPhase3Current21_nad80 | DIGITAL | IOD_SS1_disk | D148
SS1PMMPhase3Current22_nad80 | DIGITAL | IOD_SS1_disk | D149
SS1PMMPhase3Current23_nad80 | DIGITAL | IOD_SS1_disk | D150
SS1PMMPhase3Current24_nad80 | DIGITAL | IOD_SS1_disk | D151
SS1PMMPhase3Current25_nad80 | DIGITAL | IOD_SS1_disk | D152
SS1PMMPhase3Current26_nad80 | DIGITAL | IOD_SS1_disk | D153
SS1PMMPhase3Current27_nad80 | DIGITAL | IOD_SS1_disk | D154
SS1PMMPhase3Current28_nad80 | DIGITAL | IOD_SS1_disk | D155
SS1PMMPhase3Current29_nad80 | DIGITAL | IOD_SS1_disk | D156
SS1PMMPhase3Current30_nad80 | DIGITAL | IOD_SS1_disk | D157
SS1PMMPhase3Current31_nad80 | DIGITAL | IOD_SS1_disk | D158
SS1PMMPhase3Current32_nad80 | DIGITAL | IOD_SS1_disk | D159
SS1PMMPhase3Current33_nad80 | DIGITAL | IOD_SS1_disk | D160
SS1PMMPhase3Current34_nad80 | DIGITAL | IOD_SS1_disk | D161
SS1PMMPhase3Current35_nad80 | DIGITAL | IOD_SS1_disk | D162
SS1PMMPhase3Current36_nad80 | DIGITAL | IOD_SS1_disk | D163
SS1PMMPhase3Current37_nad80 | DIGITAL | IOD_SS1_disk | D164
SS1PMMPhase3Current38_nad80 | DIGITAL | IOD_SS1_disk | D165
SS1PMMPhase3Current39_nad80 | DIGITAL | IOD_SS1_disk | D166
SS1PMMPhase3Current40_nad80 | DIGITAL | IOD_SS1_disk | D167
SS1PMMPhase3Current41_nad80 | DIGITAL | IOD_SS1_disk | D168
SS1PMMPhase3Current42_nad80 | DIGITAL | IOD_SS1_disk | D169
SS1PMMPhase2Current1_med60in80 | DIGITAL | IOD_SS1_disk | D170
SS1PMMPhase2Current2_med60in80 | DIGITAL | IOD_SS1_disk | D171
SS1PMMPhase2Current3_med60in80 | DIGITAL | IOD_SS1_disk | D172
SS1PMMPhase2Current4_med60in80 | DIGITAL | IOD_SS1_disk | D173
SS1PMMPhase2Current5_med60in80 | DIGITAL | IOD_SS1_disk | D174
SS1PMMPhase2Current6_med60in80 | DIGITAL | IOD_SS1_disk | D175
SS1PMMPhase2Current7_med60in80 | DIGITAL | IOD_SS1_disk | D176
SS1PMMPhase2Current8_med60in80 | DIGITAL | IOD_SS1_disk | D177
SS1PMMPhase2Current9_med60in80 | DIGITAL | IOD_SS1_disk | D178
SS1PMMPhase2Current10_med60in80 | DIGITAL | IOD_SS1_disk | D179
SS1PMMPhase2Current11_med60in80 | DIGITAL | IOD_SS1_disk | D180
SS1PMMPhase2Current12_med60in80 | DIGITAL | IOD_SS1_disk | D181
SS1PMMPhase2Current13_med60in80 | DIGITAL | IOD_SS1_disk | D182
SS1PMMPhase2Current14_med60in80 | DIGITAL | IOD_SS1_disk | D183
SS1PMMPhase2Current15_med60in80 | DIGITAL | IOD_SS1_disk | D184
SS1PMMPhase2Current16_med60in80 | DIGITAL | IOD_SS1_disk | D185
SS1PMMPhase2Current17_med60in80 | DIGITAL | IOD_SS1_disk | D186
SS1PMMPhase2Current18_med60in80 | DIGITAL | IOD_SS1_disk | D187
SS1PMMPhase2Current19_med60in80 | DIGITAL | IOD_SS1_disk | D188
SS1PMMPhase2Current20_med60in80 | DIGITAL | IOD_SS1_disk | D189
SS1PMMPhase2Current21_med60in80 | DIGITAL | IOD_SS1_disk | D190
SS1PMMPhase2Current22_med60in80 | DIGITAL | IOD_SS1_disk | D191
SS1PMMPhase2Current23_med60in80 | DIGITAL | IOD_SS1_disk | D192
SS1PMMPhase2Current24_med60in80 | DIGITAL | IOD_SS1_disk | D193
SS1PMMPhase2Current25_med60in80 | DIGITAL | IOD_SS1_disk | D194
SS1PMMPhase2Current26_med60in80 | DIGITAL | IOD_SS1_disk | D195
SS1PMMPhase2Current27_med60in80 | DIGITAL | IOD_SS1_disk | D196
SS1PMMPhase2Current28_med60in80 | DIGITAL | IOD_SS1_disk | D197
SS1PMMPhase2Current29_med60in80 | DIGITAL | IOD_SS1_disk | D198
SS1PMMPhase2Current30_med60in80 | DIGITAL | IOD_SS1_disk | D199
SS1PMMPhase2Current31_med60in80 | DIGITAL | IOD_SS1_disk | D200
SS1PMMPhase2Current32_med60in80 | DIGITAL | IOD_SS1_disk | D201
SS1PMMPhase2Current33_med60in80 | DIGITAL | IOD_SS1_disk | D202
SS1PMMPhase2Current34_med60in80 | DIGITAL | IOD_SS1_disk | D203
SS1PMMPhase2Current35_med60in80 | DIGITAL | IOD_SS1_disk | D204
SS1PMMPhase2Current36_med60in80 | DIGITAL | IOD_SS1_disk | D205
SS1PMMPhase2Current37_med60in80 | DIGITAL | IOD_SS1_disk | D206
SS1PMMPhase2Current38_med60in80 | DIGITAL | IOD_SS1_disk | D207
SS1PMMPhase2Current39_med60in80 | DIGITAL | IOD_SS1_disk | D208
SS1PMMPhase2Current40_med60in80 | DIGITAL | IOD_SS1_disk | D209
SS1PMMPhase2Current41_med60in80 | DIGITAL | IOD_SS1_disk | D210
SS1PMMPhase2Current42_med60in80 | DIGITAL | IOD_SS1_disk | D211
SS1PMMPhase3Current1_med60in80 | DIGITAL | IOD_SS1_disk | D212
SS1PMMPhase3Current2_med60in80 | DIGITAL | IOD_SS1_disk | D213
SS1PMMPhase3Current3_med60in80 | DIGITAL | IOD_SS1_disk | D214
SS1PMMPhase3Current4_med60in80 | DIGITAL | IOD_SS1_disk | D215
SS1PMMPhase3Current5_med60in80 | DIGITAL | IOD_SS1_disk | D216
SS1PMMPhase3Current6_med60in80 | DIGITAL | IOD_SS1_disk | D217
SS1PMMPhase3Current7_med60in80 | DIGITAL | IOD_SS1_disk | D218
SS1PMMPhase3Current8_med60in80 | DIGITAL | IOD_SS1_disk | D219
SS1PMMPhase3Current9_med60in80 | DIGITAL | IOD_SS1_disk | D220
SS1PMMPhase3Current10_med60in80 | DIGITAL | IOD_SS1_disk | D221
SS1PMMPhase3Current11_med60in80 | DIGITAL | IOD_SS1_disk | D222
SS1PMMPhase3Current12_med60in80 | DIGITAL | IOD_SS1_disk | D223
SS1PMMPhase3Current13_med60in80 | DIGITAL | IOD_SS1_disk | D224
SS1PMMPhase3Current14_med60in80 | DIGITAL | IOD_SS1_disk | D225
SS1PMMPhase3Current15_med60in80 | DIGITAL | IOD_SS1_disk | D226
SS1PMMPhase3Current16_med60in80 | DIGITAL | IOD_SS1_disk | D227
SS1PMMPhase3Current17_med60in80 | DIGITAL | IOD_SS1_disk | D228
SS1PMMPhase3Current18_med60in80 | DIGITAL | IOD_SS1_disk | D229
SS1PMMPhase3Current19_med60in80 | DIGITAL | IOD_SS1_disk | D230
SS1PMMPhase3Current20_med60in80 | DIGITAL | IOD_SS1_disk | D231
SS1PMMPhase3Current21_med60in80 | DIGITAL | IOD_SS1_disk | D232
SS1PMMPhase3Current22_med60in80 | DIGITAL | IOD_SS1_disk | D233
SS1PMMPhase3Current23_med60in80 | DIGITAL | IOD_SS1_disk | D234
SS1PMMPhase3Current24_med60in80 | DIGITAL | IOD_SS1_disk | D235
SS1PMMPhase3Current25_med60in80 | DIGITAL | IOD_SS1_disk | D236
SS1PMMPhase3Current26_med60in80 | DIGITAL | IOD_SS1_disk | D237
SS1PMMPhase3Current27_med60in80 | DIGITAL | IOD_SS1_disk | D238
SS1PMMPhase3Current28_med60in80 | DIGITAL | IOD_SS1_disk | D239
SS1PMMPhase3Current29_med60in80 | DIGITAL | IOD_SS1_disk | D240
SS1PMMPhase3Current30_med60in80 | DIGITAL | IOD_SS1_disk | D241
SS1PMMPhase3Current31_med60in80 | DIGITAL | IOD_SS1_disk | D242
SS1PMMPhase3Current32_med60in80 | DIGITAL | IOD_SS1_disk | D243
SS1PMMPhase3Current33_med60in80 | DIGITAL | IOD_SS1_disk | D244
SS1PMMPhase3Current34_med60in80 | DIGITAL | IOD_SS1_disk | D245
SS1PMMPhase3Current35_med60in80 | DIGITAL | IOD_SS1_disk | D246
SS1PMMPhase3Current36_med60in80 | DIGITAL | IOD_SS1_disk | D247
SS1PMMPhase3Current37_med60in80 | DIGITAL | IOD_SS1_disk | D248
SS1PMMPhase3Current38_med60in80 | DIGITAL | IOD_SS1_disk | D249
SS1PMMPhase3Current39_med60in80 | DIGITAL | IOD_SS1_disk | D250
SS1PMMPhase3Current40_med60in80 | DIGITAL | IOD_SS1_disk | D251
SS1PMMPhase3Current41_med60in80 | DIGITAL | IOD_SS1_disk | D252
SS1PMMPhase3Current42_med60in80 | DIGITAL | IOD_SS1_disk | D253
SS1UserloggedIn_mem | DIGITAL | IOD_SS1_disk | D254
SS1PMMPoljeFazaATok1_16_nad80 | DIGITAL | IOD_SS1_disk | D2000[16]
SS1PMMPoljeFazaATok17_32_nad80 | DIGITAL | IOD_SS1_disk | D2017[16]
SS1PMMPoljeFazaATok33_42_nad80 | DIGITAL | IOD_SS1_disk | D2034[16]
SS1PMMPoljeFazaBTok1_16_nad80 | DIGITAL | IOD_SS1_disk | D2051[16]
SS1PMMPoljeFazaBTok17_32_nad80 | DIGITAL | IOD_SS1_disk | D2068[16]
SS1PMMPoljeFazaBTok33_42_nad80 | DIGITAL | IOD_SS1_disk | D2085[16]
SS1PMMPoljeFazaCTok1_16_nad80 | DIGITAL | IOD_SS1_disk | D2102[16]
SS1PMMPoljeFazaCTok17_32_nad80 | DIGITAL | IOD_SS1_disk | D2119[16]
SS1PMMPoljeFazaCTok33_42_nad80 | DIGITAL | IOD_SS1_disk | D2136[16]
SS1PMMPoljeFazaATok1_16_med60_80 | DIGITAL | IOD_SS1_disk | D2153[16]
SS1PMMPoljeFazaATok17_32_med60_80 | DIGITAL | IOD_SS1_disk | D2170[16]
SS1PMMPoljeFazaATok33_42_med60_80 | DIGITAL | IOD_SS1_disk | D2187[16]
SS1PMMPoljeFazaBTok1_16_med60_80 | DIGITAL | IOD_SS1_disk | D2204[16]
SS1PMMPoljeFazaBTok17_32_med60_80 | DIGITAL | IOD_SS1_disk | D2221[16]
SS1PMMPoljeFazaBTok33_42_med60_80 | DIGITAL | IOD_SS1_disk | D2238[16]
SS1PMMPoljeFazaCTok1_16_med60_80 | DIGITAL | IOD_SS1_disk | D2255[16]
SS1PMMPoljeFazaCTok17_32_med60_80 | DIGITAL | IOD_SS1_disk | D2272[16]
SS1PMMPoljeFazaCTok33_42_med60_80 | DIGITAL | IOD_SS1_disk | D2289[16]
ASS1_omogoci_sms | DIGITAL | IOD_SS1_disk | D500[200]
SS1PrikaziPMM | DIGITAL | IOD_SS1_disk | D300
SS1PrikaziSP1 | DIGITAL | IOD_SS1_disk | D301
SS1PrikaziSP2 | DIGITAL | IOD_SS1_disk | D302
SS1PrikaziSP3 | DIGITAL | IOD_SS1_disk | D303
SS1PrikaziSP4 | DIGITAL | IOD_SS1_disk | D304
SS1PrikaziSP5 | DIGITAL | IOD_SS1_disk | D305
SS1PrikaziKlimat1 | DIGITAL | IOD_SS1_disk | D306
SS1PrikaziKlimat2 | DIGITAL | IOD_SS1_disk | D307
SS1PrikaziKlimat3 | DIGITAL | IOD_SS1_disk | D308
SS1PMM_2x63_VirB_zavihek | DIGITAL | IOD_SS1_disk | D309
SS1PMM_2x63_VirA_zavihek | DIGITAL | IOD_SS1_disk | D310
SS1AlarmKlimat1_Napaka_Omogoci | DIGITAL | IOD_SS1_disk | D3000
SS1AlarmKlimat2_Napaka_Omogoci | DIGITAL | IOD_SS1_disk | D3001
SS1AlarmKlimat3_Napaka_Omogoci | DIGITAL | IOD_SS1_disk | D3002
SS1AlarmSP1_Napaka_Omogoci | DIGITAL | IOD_SS1_disk | D3003
SS1AlarmSP2_Napaka_Omogoci | DIGITAL | IOD_SS1_disk | D3004
SS1AlarmSP3_Napaka_Omogoci | DIGITAL | IOD_SS1_disk | D3005
SS1AlarmSP4_Napaka_Omogoci | DIGITAL | IOD_SS1_disk | D3006
SS1AlarmSP5_Napaka_Omogoci | DIGITAL | IOD_SS1_disk | D3007
SS1NapakaSenzorTemp1_Omogoci | DIGITAL | IOD_SS1_disk | D3008
SS1NapakaSenzorTemp2_Omogoci | DIGITAL | IOD_SS1_disk | D3009
SS1NapakaSenzorTemp3_Omogoci | DIGITAL | IOD_SS1_disk | D3010
SS1NapakaSenzorTempKontrSoba_Omogoci | DIGITAL | IOD_SS1_disk | D3011
SS1NapakaSenzorTempLinkProstor_Omogoci | DIGITAL | IOD_SS1_disk | D3012
SS1NapakaSenzorVlaga1_Omogoci | DIGITAL | IOD_SS1_disk | D3013
SS1NapakaSenzorVlaga2_Omogoci | DIGITAL | IOD_SS1_disk | D3014
SS1NapakaSenzorVlaga3_Omogoci | DIGITAL | IOD_SS1_disk | D3015
SS1NapakaSenzorVlagaKontrSoba_Omogoci | DIGITAL | IOD_SS1_disk | D3016
SS1NapakaSenzorVlagaLinkProstor_Omogoci | DIGITAL | IOD_SS1_disk | D3017
SS1OpozoriloBaterijaPLC_Omogoci | DIGITAL | IOD_SS1_disk | D3018
SS1PMMOverCurrentBetw1_VirB_Omogoci | DIGITAL | IOD_SS1_disk | D3019
SS1PMMOverCurrentBetw2_VirB_Omogoci | DIGITAL | IOD_SS1_disk | D3020
SS1PMMOverCurrentBetw3_VirB_Omogoci | DIGITAL | IOD_SS1_disk | D3021
SS1PMMOverCurrentBetw1_VirA_Omogoci | DIGITAL | IOD_SS1_disk | D3022
SS1PMMOverCurrentBetw2_VirA_Omogoci | DIGITAL | IOD_SS1_disk | D3023
SS1PMMOverCurrentBetw3_VirA_Omogoci | DIGITAL | IOD_SS1_disk | D3024
SS1PMMOverCurrentOver1_VirB_Omogoci | DIGITAL | IOD_SS1_disk | D3025
SS1PMMOverCurrentOver2_VirB_Omogoci | DIGITAL | IOD_SS1_disk | D3026
SS1PMMOverCurrentOver3_VirB_Omogoci | DIGITAL | IOD_SS1_disk | D3027
SS1PMMOverCurrentOver1_VirA_Omogoci | DIGITAL | IOD_SS1_disk | D3028
SS1PMMOverCurrentOver2_VirA_Omogoci | DIGITAL | IOD_SS1_disk | D3029
SS1PMMOverCurrentOver3_VirA_Omogoci | DIGITAL | IOD_SS1_disk | D3030
SS1PMM1OverVoltage_Omogoci | DIGITAL | IOD_SS1_disk | D3031
SS1AlarmUPSKrmOmara_Alarm_Omogoci | DIGITAL | IOD_SS1_disk | D3032
SS1StanjeUPSKrmOmara_BaterijskiNacin_Omogoci | DIGITAL | IOD_SS1_disk | D3033
SS1StanjeUPSKrmOmara_Polnenje_Omogoci | DIGITAL | IOD_SS1_disk | D3034
SS1AlarmLAH1_RazlitjeVode_Omogoci | DIGITAL | IOD_SS1_disk | D3035
SS1AlarmLAH2_RazlitjeVode_Omogoci | DIGITAL | IOD_SS1_disk | D3036
SS1ErrComPort2_Omogoci | DIGITAL | IOD_SS1_disk | D3037
SS1ErrComPanelPLC_Omogoci | DIGITAL | IOD_SS1_disk | D3038
SS1ErrComKlima1_Omogoci | DIGITAL | IOD_SS1_disk | D3039
SS1ErrComKlima2_Omogoci | DIGITAL | IOD_SS1_disk | D3040
SS1ErrComKlima3_Omogoci | DIGITAL | IOD_SS1_disk | D3041
SS1ErrComPMM_Omogoci | DIGITAL | IOD_SS1_disk | D3042
SS1KlimaError1AlarmKompresor1_Omogoci | DIGITAL | IOD_SS1_disk | D3043
SS1KlimaError1AlarmKompresor2_Omogoci | DIGITAL | IOD_SS1_disk | D3044
SS1KlimaError1NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS1_disk | D3045
SS1KlimaError1NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS1_disk | D3046
SS1KlimaError1NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS1_disk | D3047
SS1KlimaError1FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3048
SS1KlimaError1ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS1_disk | D3049
SS1KlimaError1ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS1_disk | D3050
SS1KlimaError1PozarniAlarm_Omogoci | DIGITAL | IOD_SS1_disk | D3051
SS1KlimaError1ZamasenFilter_Omogoci | DIGITAL | IOD_SS1_disk | D3052
SS1KlimaError1VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS1_disk | D3053
SS1KlimaError1NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS1_disk | D3054
SS1KlimaError1VisokaVlaznost_Omogoci | DIGITAL | IOD_SS1_disk | D3055
SS1KlimaError1NizkaVlaznost_Omogoci | DIGITAL | IOD_SS1_disk | D3056
SS1KlimaError1Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3057
SS1KlimaError1Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3058
SS1KlimaError1VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3059
SS1KlimaError1NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS1_disk | D3060
SS1KlimaError1NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS1_disk | D3061
SS1KlimaError1NapakaSenzorPritiska_Omogoci | DIGITAL | IOD_SS1_disk | D3062
SS1KlimaError1VisokTokVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3063
SS1KlimaError1NiVodeVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3064
SS1KlimaError1NiTokaVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3065
SS1KlimaError1VisokPritiskVKrogu1_Omogoci | DIGITAL | IOD_SS1_disk | D3066
SS1KlimaError1VisokPritiskVKrogu2_Omogoci | DIGITAL | IOD_SS1_disk | D3067
SS1KlimaError1IzlivVode_Omogoci | DIGITAL | IOD_SS1_disk | D3068
SS1KlimaError1TermZascInVisokPritiskKompr1_Omogoci | DIGITAL | IOD_SS1_disk | D3069
SS1KlimaError1VlazilecnaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3070
SS1KlimaError1TermZascInVisokPritiskKompr2_Omogoci | DIGITAL | IOD_SS1_disk | D3071
SS1KlimaError1NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS1_disk | D3072
SS1KlimaError1Kond1FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3073
SS1KlimaError1Kond2FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3074
SS1KlimaError1ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS1_disk | D3075
SS1KlimaError2AlarmKompresor1_Omogoci | DIGITAL | IOD_SS1_disk | D3076
SS1KlimaError2AlarmKompresor2_Omogoci | DIGITAL | IOD_SS1_disk | D3077
SS1KlimaError2NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS1_disk | D3078
SS1KlimaError2NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS1_disk | D3079
SS1KlimaError2NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS1_disk | D3080
SS1KlimaError2FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3081
SS1KlimaError2ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS1_disk | D3082
SS1KlimaError2ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS1_disk | D3083
SS1KlimaError2PozarniAlarm_Omogoci | DIGITAL | IOD_SS1_disk | D3084
SS1KlimaError2ZamasenFilter_Omogoci | DIGITAL | IOD_SS1_disk | D3085
SS1KlimaError2VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS1_disk | D3086
SS1KlimaError2NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS1_disk | D3087
SS1KlimaError2VisokaVlaznost_Omogoci | DIGITAL | IOD_SS1_disk | D3088
SS1KlimaError2NizkaVlaznost_Omogoci | DIGITAL | IOD_SS1_disk | D3089
SS1KlimaError2Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3090
SS1KlimaError2Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3091
SS1KlimaError2VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3092
SS1KlimaError2NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS1_disk | D3093
SS1KlimaError2NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS1_disk | D3094
SS1KlimaError2NapakaSenzorPritiska_Omogoci | DIGITAL | IOD_SS1_disk | D3095
SS1KlimaError2VisokTokVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3096
SS1KlimaError2NiVodeVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3097
SS1KlimaError2NiTokaVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3098
SS1KlimaError2VisokPritiskVKrogu1_Omogoci | DIGITAL | IOD_SS1_disk | D3099
SS1KlimaError2VisokPritiskVKrogu2_Omogoci | DIGITAL | IOD_SS1_disk | D3100
SS1KlimaError2IzlivVode_Omogoci | DIGITAL | IOD_SS1_disk | D3101
SS1KlimaError2TermZascInVisokPritiskKompr1_Omogoci | DIGITAL | IOD_SS1_disk | D3102
SS1KlimaError2VlazilecnaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3103
SS1KlimaError2TermZascInVisokPritiskKompr2_Omogoci | DIGITAL | IOD_SS1_disk | D3104
SS1KlimaError2NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS1_disk | D3105
SS1KlimaError2Kond1FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3106
SS1KlimaError2Kond2FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3107
SS1KlimaError2ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS1_disk | D3108
SS1KlimaError3AlarmKompresor1_Omogoci | DIGITAL | IOD_SS1_disk | D3109
SS1KlimaError3AlarmKompresor2_Omogoci | DIGITAL | IOD_SS1_disk | D3110
SS1KlimaError3NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS1_disk | D3111
SS1KlimaError3NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS1_disk | D3112
SS1KlimaError3NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS1_disk | D3113
SS1KlimaError3FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3114
SS1KlimaError3ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS1_disk | D3115
SS1KlimaError3ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS1_disk | D3116
SS1KlimaError3PozarniAlarm_Omogoci | DIGITAL | IOD_SS1_disk | D3117
SS1KlimaError3ZamasenFilter_Omogoci | DIGITAL | IOD_SS1_disk | D3118
SS1KlimaError3VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS1_disk | D3119
SS1KlimaError3NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS1_disk | D3120
SS1KlimaError3VisokaVlaznost_Omogoci | DIGITAL | IOD_SS1_disk | D3121
SS1KlimaError3NizkaVlaznost_Omogoci | DIGITAL | IOD_SS1_disk | D3122
SS1KlimaError3Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3123
SS1KlimaError3Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3124
SS1KlimaError3VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3125
SS1KlimaError3NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS1_disk | D3126
SS1KlimaError3NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS1_disk | D3127
SS1KlimaError3NapakaSenzorPritiska_Omogoci | DIGITAL | IOD_SS1_disk | D3128
SS1KlimaError3VisokTokVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3129
SS1KlimaError3NiVodeVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3130
SS1KlimaError3NiTokaVVlazilcu_Omogoci | DIGITAL | IOD_SS1_disk | D3131
SS1KlimaError3VisokPritiskVKrogu1_Omogoci | DIGITAL | IOD_SS1_disk | D3132
SS1KlimaError3VisokPritiskVKrogu2_Omogoci | DIGITAL | IOD_SS1_disk | D3133
SS1KlimaError3IzlivVode_Omogoci | DIGITAL | IOD_SS1_disk | D3134
SS1KlimaError3TermZascInVisokPritiskKompr1_Omogoci | DIGITAL | IOD_SS1_disk | D3135
SS1KlimaError3VlazilecnaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS1_disk | D3136
SS1KlimaError3TermZascInVisokPritiskKompr2_Omogoci | DIGITAL | IOD_SS1_disk | D3137
SS1KlimaError3NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS1_disk | D3138
SS1KlimaError3Kond1FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3139
SS1KlimaError3Kond2FenThermalCutout_Omogoci | DIGITAL | IOD_SS1_disk | D3140
SS1KlimaError3ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS1_disk | D3141
SS1PMMPhase1Current1_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3142
SS1PMMPhase1Current2_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3143
SS1PMMPhase1Current3_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3144
SS1PMMPhase1Current4_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3145
SS1PMMPhase1Current5_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3146
SS1PMMPhase1Current6_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3147
SS1PMMPhase1Current7_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3148
SS1PMMPhase1Current8_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3149
SS1PMMPhase1Current9_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3150
SS1PMMPhase1Current10_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3151
SS1PMMPhase1Current11_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3152
SS1PMMPhase1Current12_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3153
SS1PMMPhase1Current13_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3154
SS1PMMPhase1Current14_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3155
SS1PMMPhase1Current15_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3156
SS1PMMPhase1Current16_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3157
SS1PMMPhase1Current17_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3158
SS1PMMPhase1Current18_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3159
SS1PMMPhase1Current19_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3160
SS1PMMPhase1Current20_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3161
SS1PMMPhase1Current21_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3162
SS1PMMPhase1Current22_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3163
SS1PMMPhase1Current23_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3164
SS1PMMPhase1Current24_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3165
SS1PMMPhase1Current25_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3166
SS1PMMPhase1Current26_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3167
SS1PMMPhase1Current27_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3168
SS1PMMPhase1Current28_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3169
SS1PMMPhase1Current29_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3170
SS1PMMPhase1Current30_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3171
SS1PMMPhase1Current31_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3172
SS1PMMPhase1Current32_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3173
SS1PMMPhase1Current33_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3174
SS1PMMPhase1Current34_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3175
SS1PMMPhase1Current35_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3176
SS1PMMPhase1Current36_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3177
SS1PMMPhase1Current37_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3178
SS1PMMPhase1Current38_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3179
SS1PMMPhase1Current39_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3180
SS1PMMPhase1Current40_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3181
SS1PMMPhase1Current41_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3182
SS1PMMPhase1Current42_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3183
SS1PMMPhase2Current1_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3184
SS1PMMPhase2Current2_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3185
SS1PMMPhase2Current3_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3186
SS1PMMPhase2Current4_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3187
SS1PMMPhase2Current5_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3188
SS1PMMPhase2Current6_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3189
SS1PMMPhase2Current7_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3190
SS1PMMPhase2Current8_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3191
SS1PMMPhase2Current9_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3192
SS1PMMPhase2Current10_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3193
SS1PMMPhase2Current11_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3194
SS1PMMPhase2Current12_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3195
SS1PMMPhase2Current13_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3196
SS1PMMPhase2Current14_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3197
SS1PMMPhase2Current15_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3198
SS1PMMPhase2Current16_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3199
SS1PMMPhase2Current17_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3200
SS1PMMPhase2Current18_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3201
SS1PMMPhase2Current19_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3202
SS1PMMPhase2Current20_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3203
SS1PMMPhase2Current21_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3204
SS1PMMPhase2Current22_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3205
SS1PMMPhase2Current23_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3206
SS1PMMPhase2Current24_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3207
SS1PMMPhase2Current25_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3208
SS1PMMPhase2Current26_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3209
SS1PMMPhase2Current27_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3210
SS1PMMPhase2Current28_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3211
SS1PMMPhase2Current29_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3212
SS1PMMPhase2Current30_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3213
SS1PMMPhase2Current31_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3214
SS1PMMPhase2Current32_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3215
SS1PMMPhase2Current33_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3216
SS1PMMPhase2Current34_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3217
SS1PMMPhase2Current35_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3218
SS1PMMPhase2Current36_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3219
SS1PMMPhase2Current37_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3220
SS1PMMPhase2Current38_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3221
SS1PMMPhase2Current39_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3222
SS1PMMPhase2Current40_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3223
SS1PMMPhase2Current41_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3224
SS1PMMPhase2Current42_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3225
SS1PMMPhase3Current1_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3226
SS1PMMPhase3Current2_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3227
SS1PMMPhase3Current3_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3228
SS1PMMPhase3Current4_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3229
SS1PMMPhase3Current5_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3230
SS1PMMPhase3Current6_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3231
SS1PMMPhase3Current7_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3232
SS1PMMPhase3Current8_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3233
SS1PMMPhase3Current9_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3234
SS1PMMPhase3Current10_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3235
SS1PMMPhase3Current11_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3236
SS1PMMPhase3Current12_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3237
SS1PMMPhase3Current13_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3238
SS1PMMPhase3Current14_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3239
SS1PMMPhase3Current15_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3240
SS1PMMPhase3Current16_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3241
SS1PMMPhase3Current17_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3242
SS1PMMPhase3Current18_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3243
SS1PMMPhase3Current19_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3244
SS1PMMPhase3Current20_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3245
SS1PMMPhase3Current21_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3246
SS1PMMPhase3Current22_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3247
SS1PMMPhase3Current23_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3248
SS1PMMPhase3Current24_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3249
SS1PMMPhase3Current25_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3250
SS1PMMPhase3Current26_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3251
SS1PMMPhase3Current27_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3252
SS1PMMPhase3Current28_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3253
SS1PMMPhase3Current29_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3254
SS1PMMPhase3Current30_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3255
SS1PMMPhase3Current31_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3256
SS1PMMPhase3Current32_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3257
SS1PMMPhase3Current33_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3258
SS1PMMPhase3Current34_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3259
SS1PMMPhase3Current35_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3260
SS1PMMPhase3Current36_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3261
SS1PMMPhase3Current37_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3262
SS1PMMPhase3Current38_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3263
SS1PMMPhase3Current39_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3264
SS1PMMPhase3Current40_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3265
SS1PMMPhase3Current41_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3266
SS1PMMPhase3Current42_med60in80_Omogoci | DIGITAL | IOD_SS1_disk | D3267
SS1PMMPhase1Current1_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3268
SS1PMMPhase1Current2_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3269
SS1PMMPhase1Current3_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3270
SS1PMMPhase1Current4_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3271
SS1PMMPhase1Current5_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3272
SS1PMMPhase1Current6_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3273
SS1PMMPhase1Current7_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3274
SS1PMMPhase1Current8_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3275
SS1PMMPhase1Current9_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3276
SS1PMMPhase1Current10_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3277
SS1PMMPhase1Current11_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3278
SS1PMMPhase1Current12_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3279
SS1PMMPhase1Current13_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3280
SS1PMMPhase1Current14_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3281
SS1PMMPhase1Current15_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3282
SS1PMMPhase1Current16_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3283
SS1PMMPhase1Current17_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3284
SS1PMMPhase1Current18_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3285
SS1PMMPhase1Current19_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3286
SS1PMMPhase1Current20_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3287
SS1PMMPhase1Current21_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3288
SS1PMMPhase1Current22_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3289
SS1PMMPhase1Current23_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3290
SS1PMMPhase1Current24_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3291
SS1PMMPhase1Current25_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3292
SS1PMMPhase1Current26_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3293
SS1PMMPhase1Current27_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3294
SS1PMMPhase1Current28_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3295
SS1PMMPhase1Current29_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3296
SS1PMMPhase1Current30_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3297
SS1PMMPhase1Current31_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3298
SS1PMMPhase1Current32_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3299
SS1PMMPhase1Current33_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3300
SS1PMMPhase1Current34_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3301
SS1PMMPhase1Current35_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3302
SS1PMMPhase1Current36_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3303
SS1PMMPhase1Current37_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3304
SS1PMMPhase1Current38_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3305
SS1PMMPhase1Current39_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3306
SS1PMMPhase1Current40_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3307
SS1PMMPhase1Current41_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3308
SS1PMMPhase1Current42_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3309
SS1PMMPhase2Current1_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3310
SS1PMMPhase2Current2_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3311
SS1PMMPhase2Current3_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3312
SS1PMMPhase2Current4_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3313
SS1PMMPhase2Current5_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3314
SS1PMMPhase2Current6_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3315
SS1PMMPhase2Current7_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3316
SS1PMMPhase2Current8_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3317
SS1PMMPhase2Current9_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3318
SS1PMMPhase2Current10_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3319
SS1PMMPhase2Current11_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3320
SS1PMMPhase2Current12_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3321
SS1PMMPhase2Current13_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3322
SS1PMMPhase2Current14_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3323
SS1PMMPhase2Current15_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3324
SS1PMMPhase2Current16_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3325
SS1PMMPhase2Current17_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3326
SS1PMMPhase2Current18_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3327
SS1PMMPhase2Current19_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3328
SS1PMMPhase2Current20_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3329
SS1PMMPhase2Current21_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3330
SS1PMMPhase2Current22_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3331
SS1PMMPhase2Current23_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3332
SS1PMMPhase2Current24_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3333
SS1PMMPhase2Current25_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3334
SS1PMMPhase2Current26_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3335
SS1PMMPhase2Current27_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3336
SS1PMMPhase2Current28_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3337
SS1PMMPhase2Current29_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3338
SS1PMMPhase2Current30_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3339
SS1PMMPhase2Current31_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3340
SS1PMMPhase2Current32_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3341
SS1PMMPhase2Current33_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3342
SS1PMMPhase2Current34_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3343
SS1PMMPhase2Current35_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3344
SS1PMMPhase2Current36_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3345
SS1PMMPhase2Current37_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3346
SS1PMMPhase2Current38_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3347
SS1PMMPhase2Current39_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3348
SS1PMMPhase2Current40_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3349
SS1PMMPhase2Current41_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3350
SS1PMMPhase2Current42_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3351
SS1PMMPhase3Current1_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3352
SS1PMMPhase3Current2_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3353
SS1PMMPhase3Current3_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3354
SS1PMMPhase3Current4_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3355
SS1PMMPhase3Current5_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3356
SS1PMMPhase3Current6_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3357
SS1PMMPhase3Current7_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3358
SS1PMMPhase3Current8_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3359
SS1PMMPhase3Current9_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3360
SS1PMMPhase3Current10_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3361
SS1PMMPhase3Current11_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3362
SS1PMMPhase3Current12_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3363
SS1PMMPhase3Current13_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3364
SS1PMMPhase3Current14_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3365
SS1PMMPhase3Current15_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3366
SS1PMMPhase3Current16_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3367
SS1PMMPhase3Current17_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3368
SS1PMMPhase3Current18_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3369
SS1PMMPhase3Current19_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3370
SS1PMMPhase3Current20_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3371
SS1PMMPhase3Current21_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3372
SS1PMMPhase3Current22_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3373
SS1PMMPhase3Current23_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3374
SS1PMMPhase3Current24_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3375
SS1PMMPhase3Current25_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3376
SS1PMMPhase3Current26_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3377
SS1PMMPhase3Current27_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3378
SS1PMMPhase3Current28_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3379
SS1PMMPhase3Current29_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3380
SS1PMMPhase3Current30_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3381
SS1PMMPhase3Current31_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3382
SS1PMMPhase3Current32_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3383
SS1PMMPhase3Current33_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3384
SS1PMMPhase3Current34_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3385
SS1PMMPhase3Current35_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3386
SS1PMMPhase3Current36_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3387
SS1PMMPhase3Current37_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3388
SS1PMMPhase3Current38_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3389
SS1PMMPhase3Current39_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3390
SS1PMMPhase3Current40_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3391
SS1PMMPhase3Current41_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3392
SS1PMMPhase3Current42_nad80_Omogoci | DIGITAL | IOD_SS1_disk | D3393
SS1AlarmTempTIA123Previsoka_Omogoci | DIGITAL | IOD_SS1_disk | D3394
SS1AlarmTempTIA4Previsoka_Omogoci | DIGITAL | IOD_SS1_disk | D3395
SS1AlarmTempTIA5Previsoka_Omogoci | DIGITAL | IOD_SS1_disk | D3396
SS1PMMOverCurrentBetw1_VirB | DIGITAL | IOD_SS1_disk | D3397
SS1PMMOverCurrentBetw2_VirB | DIGITAL | IOD_SS1_disk | D3398
SS1PMMOverCurrentBetw3_VirB | DIGITAL | IOD_SS1_disk | D3399
SS1PMMOverCurrentBetw1_VirA | DIGITAL | IOD_SS1_disk | D3400
SS1PMMOverCurrentBetw2_VirA | DIGITAL | IOD_SS1_disk | D3401
SS1PMMOverCurrentBetw3_VirA | DIGITAL | IOD_SS1_disk | D3402
SS1PMMOverCurrentOver1_VirB | DIGITAL | IOD_SS1_disk | D3403
SS1PMMOverCurrentOver2_VirB | DIGITAL | IOD_SS1_disk | D3404
SS1PMMOverCurrentOver3_VirB | DIGITAL | IOD_SS1_disk | D3405
SS1PMMOverCurrentOver1_VirA | DIGITAL | IOD_SS1_disk | D3406
SS1PMMOverCurrentOver2_VirA | DIGITAL | IOD_SS1_disk | D3407
SS1PMMOverCurrentOver3_VirA | DIGITAL | IOD_SS1_disk | D3408
SS1PMMOverCurrentBetw1_VirB_1_2 | DIGITAL | IOD_SS1_disk | D3409
SS1PMMOverCurrentBetw1_VirB_2_2 | DIGITAL | IOD_SS1_disk | D3410
SS1PMMOverCurrentBetw1_VirA_1_2 | DIGITAL | IOD_SS1_disk | D3411
SS1PMMOverCurrentBetw1_VirA_2_2 | DIGITAL | IOD_SS1_disk | D3412
SS1PMMOverCurrentBetw2_VirB_1_2 | DIGITAL | IOD_SS1_disk | D3413
SS1PMMOverCurrentBetw2_VirB_2_2 | DIGITAL | IOD_SS1_disk | D3414
SS1PMMOverCurrentBetw2_VirA_1_2 | DIGITAL | IOD_SS1_disk | D3415
SS1PMMOverCurrentBetw2_VirA_2_2 | DIGITAL | IOD_SS1_disk | D3416
SS1PMMOverCurrentBetw3_VirB_1_2 | DIGITAL | IOD_SS1_disk | D3417
SS1PMMOverCurrentBetw3_VirB_2_2 | DIGITAL | IOD_SS1_disk | D3418
SS1PMMOverCurrentBetw3_VirA_1_2 | DIGITAL | IOD_SS1_disk | D3419
SS1PMMOverCurrentBetw3_VirA_2_2 | DIGITAL | IOD_SS1_disk | D3420
SS1PMMOverCurrentOver1_VirB_1_2 | DIGITAL | IOD_SS1_disk | D3421
SS1PMMOverCurrentOver1_VirB_2_2 | DIGITAL | IOD_SS1_disk | D3422
SS1PMMOverCurrentOver1_VirA_1_2 | DIGITAL | IOD_SS1_disk | D3423
SS1PMMOverCurrentOver1_VirA_2_2 | DIGITAL | IOD_SS1_disk | D3424
SS1PMMOverCurrentOver2_VirB_1_2 | DIGITAL | IOD_SS1_disk | D3425
SS1PMMOverCurrentOver2_VirB_2_2 | DIGITAL | IOD_SS1_disk | D3426
SS1PMMOverCurrentOver2_VirA_1_2 | DIGITAL | IOD_SS1_disk | D3427
SS1PMMOverCurrentOver2_VirA_2_2 | DIGITAL | IOD_SS1_disk | D3428
SS1PMMOverCurrentOver3_VirB_1_2 | DIGITAL | IOD_SS1_disk | D3429
SS1PMMOverCurrentOver3_VirB_2_2 | DIGITAL | IOD_SS1_disk | D3430
SS1PMMOverCurrentOver3_VirA_1_2 | DIGITAL | IOD_SS1_disk | D3431
SS1PMMOverCurrentOver3_VirA_2_2 | DIGITAL | IOD_SS1_disk | D3432
SS1AlarmSinhronizacijaNOK_Omogoci | DIGITAL | IOD_SS1_disk | D3433
SS1VsotaF1_1_16B | INT | IOD_SS1_disk | I3
SS1VsotaF1_17_32B | INT | IOD_SS1_disk | I4
SS1VsotaF1_33_42B | INT | IOD_SS1_disk | I5
SS1VsotaF1_1_16A | INT | IOD_SS1_disk | I6
SS1VsotaF1_17_32A | INT | IOD_SS1_disk | I7
SS1VsotaF1_33_42A | INT | IOD_SS1_disk | I8
SS1VsotaF2_1_16B | INT | IOD_SS1_disk | I9
SS1VsotaF2_17_32B | INT | IOD_SS1_disk | I10
SS1VsotaF2_33_42B | INT | IOD_SS1_disk | I11
SS1VsotaF2_1_16A | INT | IOD_SS1_disk | I12
SS1VsotaF2_17_32A | INT | IOD_SS1_disk | I13
SS1VsotaF2_33_42A | INT | IOD_SS1_disk | I14
SS1VsotaF3_1_16B | INT | IOD_SS1_disk | I15
SS1VsotaF3_17_32B | INT | IOD_SS1_disk | I16
SS1VsotaF3_33_42B | INT | IOD_SS1_disk | I17
SS1VsotaF3_1_16A | INT | IOD_SS1_disk | I18
SS1VsotaF3_17_32A | INT | IOD_SS1_disk | I19
SS1VsotaF3_33_42A | INT | IOD_SS1_disk | I20
SS1ComSCADA_stevec2 | INT | IOD_SS1_mem | I1
SS1ComSCADA_stevec1 | INT | IOD_SS1_mem | I2
SS1AktualniSetPointTemp | REAL | IOD_SS1_TCP | 44001 | 0 | 60 | 0 | 60 | °C | ##.#
SS1AktualniSetPointVlaga | REAL | IOD_SS1_TCP | 44003 | 0 | 100 | 0 | 100 | % | ##.#
SS1AlarmKlimat1_Napaka | DIGITAL | IOD_SS1_TCP | 00001
SS1AlarmKlimat2_Napaka | DIGITAL | IOD_SS1_TCP | 00002
SS1AlarmKlimat3_Napaka | DIGITAL | IOD_SS1_TCP | 00003
SS1AlarmLAH1_RazlitjeVode | DIGITAL | IOD_SS1_TCP | 00004
SS1AlarmLAH2_RazlitjeVode | DIGITAL | IOD_SS1_TCP | 00005
SS1AlarmSinhronizacijaNOK | DIGITAL | IOD_SS1_TCP | 00006
SS1AlarmSP1_Napaka | DIGITAL | IOD_SS1_TCP | 00007
SS1AlarmSP2_Napaka | DIGITAL | IOD_SS1_TCP | 00008
SS1AlarmSP3_Napaka | DIGITAL | IOD_SS1_TCP | 00009
SS1AlarmSP4_Napaka | DIGITAL | IOD_SS1_TCP | 00010
SS1AlarmSP5_Napaka | DIGITAL | IOD_SS1_TCP | 00011
SS1AlarmTempTIA123Previsoka | DIGITAL | IOD_SS1_TCP | 00012
SS1AlarmTempTIA4Previsoka | DIGITAL | IOD_SS1_TCP | 00013
SS1AlarmTempTIA5Previsoka | DIGITAL | IOD_SS1_TCP | 00014
SS1AlarmTSTempPrevisoka | DIGITAL | IOD_SS1_TCP | 00015
SS1AlarmUPSKrmOmara_Alarm | DIGITAL | IOD_SS1_TCP | 00016
SS1ComSCADA | DIGITAL | IOD_SS1_TCP | 00017
SS1ComSCADA1 | DIGITAL | IOD_SS1_TCP | 00018
SS1DatumCasDan | INT | IOD_SS1_TCP | 40001
SS1DatumCasLeto | INT | IOD_SS1_TCP | 40002
SS1DatumCasLeto2 | INT | IOD_SS1_TCP | 40003
SS1DatumCasMesec | INT | IOD_SS1_TCP | 40004
SS1DatumCasMinuta | INT | IOD_SS1_TCP | 40005
SS1DatumCasSekunda | INT | IOD_SS1_TCP | 40006
SS1DatumCasUra | INT | IOD_SS1_TCP | 40007
SS1ErrComKlima1 | DIGITAL | IOD_SS1_TCP | 00019
SS1ErrComKlima2 | DIGITAL | IOD_SS1_TCP | 00020
SS1ErrComKlima3 | DIGITAL | IOD_SS1_TCP | 00021
SS1ErrCommScada | DIGITAL | IOD_SS1_TCP | 00022
SS1ErrComPanelPLC | DIGITAL | IOD_SS1_TCP | 00023
SS1ErrComPMM | DIGITAL | IOD_SS1_TCP | 00024
SS1ErrComPort2 | DIGITAL | IOD_SS1_TCP | 00025
SS1Klima1_Onemogocena | DIGITAL | IOD_SS1_TCP | 00026
SS1Klima2_Onemogocena | DIGITAL | IOD_SS1_TCP | 00027
SS1Klima3_Onemogocena | DIGITAL | IOD_SS1_TCP | 00028
SS1Klima1IzhodniVentilator | DIGITAL | IOD_SS1_TCP | 00029
SS1Klima1Kompresor1 | DIGITAL | IOD_SS1_TCP | 00030
SS1Klima1Kompresor2 | DIGITAL | IOD_SS1_TCP | 00031
SS1Klima1NastMaxTemp | REAL | IOD_SS1_TCP | 44005 | 0 | 60 | 0 | 60 | °C | ##.#
SS1Klima1NastMaxVlaznost | REAL | IOD_SS1_TCP | 44007 | 0 | 100 | 0 | 100 | % | ##.#
SS1Klima1NastMinTemp | REAL | IOD_SS1_TCP | 44009 | 0 | 60 | 0 | 60 | °C | ##.#
SS1Klima1NastMinVlaznost | REAL | IOD_SS1_TCP | 44011 | 0 | 100 | 0 | 100 | % | ##.#
SS1Klima1NastTempProstora | REAL | IOD_SS1_TCP | 44013 | 0 | 60 | 0 | 60 | °C | ##.#
SS1Klima1NastVlaznost | REAL | IOD_SS1_TCP | 44015 | 0 | 100 | 0 | 100 | % | ##.#
SS1Klima1Pritisk | REAL | IOD_SS1_TCP | 44017 | 0 | 5 | 0 | 5 | bar | ##.#
SS1Klima1Razvlazevanje | DIGITAL | IOD_SS1_TCP | 00032
SS1Klima1TemperaturaProstora | REAL | IOD_SS1_TCP | 44019 | 0 | 60 | 0 | 60 | °C | ##.#
SS1Klima1VentilGretjeOdpiranje | DIGITAL | IOD_SS1_TCP | 00033
SS1Klima1VentilGretjeZapiranje | DIGITAL | IOD_SS1_TCP | 00034
SS1Klima1Vlazenje | DIGITAL | IOD_SS1_TCP | 00035
SS1Klima1Vlazilec_Stanja | INT | IOD_SS1_TCP | 40008
SS1Klima1VlaznostProstora | REAL | IOD_SS1_TCP | 44021 | 0 | 100 | 0 | 100 | % | ##.#
SS1Klima2IzhodniVentilator | DIGITAL | IOD_SS1_TCP | 00036
SS1Klima2Kompresor1 | DIGITAL | IOD_SS1_TCP | 00037
SS1Klima2Kompresor2 | DIGITAL | IOD_SS1_TCP | 00038
SS1Klima2NastMaxTemp | REAL | IOD_SS1_TCP | 44023 | 0 | 60 | 0 | 60 | °C | ##.#
SS1Klima2NastMaxVlaznost | REAL | IOD_SS1_TCP | 44025 | 0 | 100 | 0 | 100 | % | ##.#
SS1Klima2NastMinTemp | REAL | IOD_SS1_TCP | 44027 | 0 | 60 | 0 | 60 | °C | ##.#
SS1Klima2NastMinVlaznost | REAL | IOD_SS1_TCP | 44029 | 0 | 100 | 0 | 100 | % | ##.#
SS1Klima2NastTempProstora | REAL | IOD_SS1_TCP | 44031 | 0 | 60 | 0 | 60 | °C | ##.#
SS1Klima2NastVlaznost | REAL | IOD_SS1_TCP | 44033 | 0 | 100 | 0 | 100 | % | ##.#
SS1Klima2Pritisk | REAL | IOD_SS1_TCP | 44035 | 0 | 5 | 0 | 5 | bar | ##.#
SS1Klima2Razvlazevanje | DIGITAL | IOD_SS1_TCP | 00039
SS1Klima2TemperaturaProstora | REAL | IOD_SS1_TCP | 44037 | 0 | 60 | 0 | 60 | °C | ##.#
SS1Klima2VentilGretjeOdpiranje | DIGITAL | IOD_SS1_TCP | 00040
SS1Klima2VentilGretjeZapiranje | DIGITAL | IOD_SS1_TCP | 00041
SS1Klima2Vlazenje | DIGITAL | IOD_SS1_TCP | 00042
SS1Klima2Vlazilec_Stanja | INT | IOD_SS1_TCP | 40009
SS1Klima2VlaznostProstora | REAL | IOD_SS1_TCP | 44039 | 0 | 100 | 0 | 100 | % | ##.#
SS1Klima3IzhodniVentilator | DIGITAL | IOD_SS1_TCP | 00043
SS1Klima3Kompresor1 | DIGITAL | IOD_SS1_TCP | 00044
SS1Klima3Kompresor2 | DIGITAL | IOD_SS1_TCP | 00045
SS1Klima3NastMaxTemp | REAL | IOD_SS1_TCP | 44041 | 0 | 60 | 0 | 60 | °C | ##.#
SS1Klima3NastMaxVlaznost | REAL | IOD_SS1_TCP | 44043 | 0 | 100 | 0 | 100 | % | ##.#
SS1Klima3NastMinTemp | REAL | IOD_SS1_TCP | 44045 | 0 | 60 | 0 | 60 | °C | ##.#
SS1Klima3NastMinVlaznost | REAL | IOD_SS1_TCP | 44047 | 0 | 100 | 0 | 100 | % | ##.#
SS1Klima3NastTempProstora | REAL | IOD_SS1_TCP | 44049 | 0 | 60 | 0 | 60 | °C | ##.#
SS1Klima3NastVlaznost | REAL | IOD_SS1_TCP | 44051 | 0 | 100 | 0 | 100 | % | ##.#
SS1Klima3Pritisk | REAL | IOD_SS1_TCP | 44053 | 0 | 5 | 0 | 5 | bar | ##.#
SS1Klima3Razvlazevanje | DIGITAL | IOD_SS1_TCP | 00046
SS1Klima3TemperaturaProstora | REAL | IOD_SS1_TCP | 44055 | 0 | 60 | 0 | 60 | °C | ##.#
SS1Klima3VentilGretjeOdpiranje | DIGITAL | IOD_SS1_TCP | 00047
SS1Klima3VentilGretjeZapiranje | DIGITAL | IOD_SS1_TCP | 00048
SS1Klima3Vlazenje | DIGITAL | IOD_SS1_TCP | 00049
SS1Klima3Vlazilec_Stanja | INT | IOD_SS1_TCP | 40010
SS1Klima3VlaznostProstora | REAL | IOD_SS1_TCP | 44057 | 0 | 100 | 0 | 100 | % | ##.#
SS1KlimaError1AlarmKompresor1 | DIGITAL | IOD_SS1_TCP | 00050
SS1KlimaError1AlarmKompresor2 | DIGITAL | IOD_SS1_TCP | 00051
SS1KlimaError1FenThermalCutout | DIGITAL | IOD_SS1_TCP | 00052
SS1KlimaError1IzlivVode | DIGITAL | IOD_SS1_TCP | 00053
SS1KlimaError1Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 00054
SS1KlimaError1Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 00055
SS1KlimaError1Kond1FenThermalCutout | DIGITAL | IOD_SS1_TCP | 00056
SS1KlimaError1Kond2FenThermalCutout | DIGITAL | IOD_SS1_TCP | 00057
SS1KlimaError1NapakaPriPretokuVode | DIGITAL | IOD_SS1_TCP | 00058
SS1KlimaError1NapakaPriPretokuZraka | DIGITAL | IOD_SS1_TCP | 00059
SS1KlimaError1NapakaSenzorPritiska | DIGITAL | IOD_SS1_TCP | 00060
SS1KlimaError1NapakaSenzorVlaznosti | DIGITAL | IOD_SS1_TCP | 00061
SS1KlimaError1NapakaTSTemperaturaProstora | DIGITAL | IOD_SS1_TCP | 00062
SS1KlimaError1NiTokaVVlazilcu | DIGITAL | IOD_SS1_TCP | 00063
SS1KlimaError1NiVodeVVlazilcu | DIGITAL | IOD_SS1_TCP | 00064
SS1KlimaError1NizekPritiskKompresor1 | DIGITAL | IOD_SS1_TCP | 00065
SS1KlimaError1NizekPritiskKompresor2 | DIGITAL | IOD_SS1_TCP | 00066
SS1KlimaError1NizkaTempVProstoru | DIGITAL | IOD_SS1_TCP | 00067
SS1KlimaError1NizkaVlaznost | DIGITAL | IOD_SS1_TCP | 00068
SS1KlimaError1PozarniAlarm | DIGITAL | IOD_SS1_TCP | 00069
SS1KlimaError1TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS1_TCP | 00070
SS1KlimaError1TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS1_TCP | 00071
SS1KlimaError1ThermalCutoutHeater1 | DIGITAL | IOD_SS1_TCP | 00072
SS1KlimaError1ThermalCutoutHeater2 | DIGITAL | IOD_SS1_TCP | 00073
SS1KlimaError1VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 00074
SS1KlimaError1VisokaTempVProstoru | DIGITAL | IOD_SS1_TCP | 00075
SS1KlimaError1VisokaVlaznost | DIGITAL | IOD_SS1_TCP | 00076
SS1KlimaError1VisokPritiskVKrogu1 | DIGITAL | IOD_SS1_TCP | 00077
SS1KlimaError1VisokPritiskVKrogu2 | DIGITAL | IOD_SS1_TCP | 00078
SS1KlimaError1VisokTokVVlazilcu | DIGITAL | IOD_SS1_TCP | 00079
SS1KlimaError1VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 00080
SS1KlimaError1ZamasenFilter | DIGITAL | IOD_SS1_TCP | 00081
SS1KlimaError1ZunanjiAlarm | DIGITAL | IOD_SS1_TCP | 00082
SS1KlimaError2AlarmKompresor1 | DIGITAL | IOD_SS1_TCP | 00083
SS1KlimaError2AlarmKompresor2 | DIGITAL | IOD_SS1_TCP | 00084
SS1KlimaError2FenThermalCutout | DIGITAL | IOD_SS1_TCP | 00085
SS1KlimaError2IzlivVode | DIGITAL | IOD_SS1_TCP | 00086
SS1KlimaError2Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 00087
SS1KlimaError2Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 00088
SS1KlimaError2Kond1FenThermalCutout | DIGITAL | IOD_SS1_TCP | 00089
SS1KlimaError2Kond2FenThermalCutout | DIGITAL | IOD_SS1_TCP | 00090
SS1KlimaError2NapakaPriPretokuVode | DIGITAL | IOD_SS1_TCP | 00091
SS1KlimaError2NapakaPriPretokuZraka | DIGITAL | IOD_SS1_TCP | 00092
SS1KlimaError2NapakaSenzorPritiska | DIGITAL | IOD_SS1_TCP | 00093
SS1KlimaError2NapakaSenzorVlaznosti | DIGITAL | IOD_SS1_TCP | 00094
SS1KlimaError2NapakaTSTemperaturaProstora | DIGITAL | IOD_SS1_TCP | 00095
SS1KlimaError2NiTokaVVlazilcu | DIGITAL | IOD_SS1_TCP | 00096
SS1KlimaError2NiVodeVVlazilcu | DIGITAL | IOD_SS1_TCP | 00097
SS1KlimaError2NizekPritiskKompresor1 | DIGITAL | IOD_SS1_TCP | 00098
SS1KlimaError2NizekPritiskKompresor2 | DIGITAL | IOD_SS1_TCP | 00099
SS1KlimaError2NizkaTempVProstoru | DIGITAL | IOD_SS1_TCP | 00100
SS1KlimaError2NizkaVlaznost | DIGITAL | IOD_SS1_TCP | 00101
SS1KlimaError2PozarniAlarm | DIGITAL | IOD_SS1_TCP | 00102
SS1KlimaError2TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS1_TCP | 00103
SS1KlimaError2TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS1_TCP | 00104
SS1KlimaError2ThermalCutoutHeater1 | DIGITAL | IOD_SS1_TCP | 00105
SS1KlimaError2ThermalCutoutHeater2 | DIGITAL | IOD_SS1_TCP | 00106
SS1KlimaError2VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 00107
SS1KlimaError2VisokaTempVProstoru | DIGITAL | IOD_SS1_TCP | 00108
SS1KlimaError2VisokaVlaznost | DIGITAL | IOD_SS1_TCP | 00109
SS1KlimaError2VisokPritiskVKrogu1 | DIGITAL | IOD_SS1_TCP | 00110
SS1KlimaError2VisokPritiskVKrogu2 | DIGITAL | IOD_SS1_TCP | 00111
SS1KlimaError2VisokTokVVlazilcu | DIGITAL | IOD_SS1_TCP | 00112
SS1KlimaError2VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 00113
SS1KlimaError2ZamasenFilter | DIGITAL | IOD_SS1_TCP | 00114
SS1KlimaError2ZunanjiAlarm | DIGITAL | IOD_SS1_TCP | 00115
SS1KlimaError3AlarmKompresor1 | DIGITAL | IOD_SS1_TCP | 00116
SS1KlimaError3AlarmKompresor2 | DIGITAL | IOD_SS1_TCP | 00117
SS1KlimaError3FenThermalCutout | DIGITAL | IOD_SS1_TCP | 00118
SS1KlimaError3IzlivVode | DIGITAL | IOD_SS1_TCP | 00119
SS1KlimaError3Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 00120
SS1KlimaError3Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 00121
SS1KlimaError3Kond1FenThermalCutout | DIGITAL | IOD_SS1_TCP | 00122
SS1KlimaError3Kond2FenThermalCutout | DIGITAL | IOD_SS1_TCP | 00123
SS1KlimaError3NapakaPriPretokuVode | DIGITAL | IOD_SS1_TCP | 00124
SS1KlimaError3NapakaPriPretokuZraka | DIGITAL | IOD_SS1_TCP | 00125
SS1KlimaError3NapakaSenzorPritiska | DIGITAL | IOD_SS1_TCP | 00126
SS1KlimaError3NapakaSenzorVlaznosti | DIGITAL | IOD_SS1_TCP | 00127
SS1KlimaError3NapakaTSTemperaturaProstora | DIGITAL | IOD_SS1_TCP | 00128
SS1KlimaError3NiTokaVVlazilcu | DIGITAL | IOD_SS1_TCP | 00129
SS1KlimaError3NiVodeVVlazilcu | DIGITAL | IOD_SS1_TCP | 00130
SS1KlimaError3NizekPritiskKompresor1 | DIGITAL | IOD_SS1_TCP | 00131
SS1KlimaError3NizekPritiskKompresor2 | DIGITAL | IOD_SS1_TCP | 00132
SS1KlimaError3NizkaTempVProstoru | DIGITAL | IOD_SS1_TCP | 00133
SS1KlimaError3NizkaVlaznost | DIGITAL | IOD_SS1_TCP | 00134
SS1KlimaError3PozarniAlarm | DIGITAL | IOD_SS1_TCP | 00135
SS1KlimaError3TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS1_TCP | 00136
SS1KlimaError3TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS1_TCP | 00137
SS1KlimaError3ThermalCutoutHeater1 | DIGITAL | IOD_SS1_TCP | 00138
SS1KlimaError3ThermalCutoutHeater2 | DIGITAL | IOD_SS1_TCP | 00139
SS1KlimaError3VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 00140
SS1KlimaError3VisokaTempVProstoru | DIGITAL | IOD_SS1_TCP | 00141
SS1KlimaError3VisokaVlaznost | DIGITAL | IOD_SS1_TCP | 00142
SS1KlimaError3VisokPritiskVKrogu1 | DIGITAL | IOD_SS1_TCP | 00143
SS1KlimaError3VisokPritiskVKrogu2 | DIGITAL | IOD_SS1_TCP | 00144
SS1KlimaError3VisokTokVVlazilcu | DIGITAL | IOD_SS1_TCP | 00145
SS1KlimaError3VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS1_TCP | 00146
SS1KlimaError3ZamasenFilter | DIGITAL | IOD_SS1_TCP | 00147
SS1KlimaError3ZunanjiAlarm | DIGITAL | IOD_SS1_TCP | 00148
SS1NacDelovanjaKlime1_Avtomatsko | DIGITAL | IOD_SS1_TCP | 00149
SS1NacDelovanjaKlime2_3Avtomatsko | DIGITAL | IOD_SS1_TCP | 00150
SS1NapakaSenzorTemp1 | DIGITAL | IOD_SS1_TCP | 00151
SS1NapakaSenzorTemp2 | DIGITAL | IOD_SS1_TCP | 00152
SS1NapakaSenzorTemp3 | DIGITAL | IOD_SS1_TCP | 00153
SS1NapakaSenzorTempKontrSoba | DIGITAL | IOD_SS1_TCP | 00154
SS1NapakaSenzorTempLinkProstor | DIGITAL | IOD_SS1_TCP | 00155
SS1NapakaSenzorVlaga1 | DIGITAL | IOD_SS1_TCP | 00156
SS1NapakaSenzorVlaga2 | DIGITAL | IOD_SS1_TCP | 00157
SS1NapakaSenzorVlaga3 | DIGITAL | IOD_SS1_TCP | 00158
SS1NapakaSenzorVlagaKontrSoba | DIGITAL | IOD_SS1_TCP | 00159
SS1NapakaSenzorVlagaLinkProstor | DIGITAL | IOD_SS1_TCP | 00160
SS1NastaviCasNaKrmilniku | DIGITAL | IOD_SS1_TCP | 00161
SS1NastavitevUreKrUspesna | DIGITAL | IOD_SS1_TCP | 00162
SS1ObratUreKlim1 | REAL | IOD_SS1_TCP | 44059
SS1ObratUreKlim2 | REAL | IOD_SS1_TCP | 44061
SS1ObratUreKlim3 | REAL | IOD_SS1_TCP | 44063
SS1OpozoriloBaterijaPLC | DIGITAL | IOD_SS1_TCP | 00163
SS1PMMActiveEnergyConsumed_kWh | REAL | IOD_SS1_TCP | 44065
SS1PMMActivePowerPhaseA_kW | REAL | IOD_SS1_TCP | 44067
SS1PMMActivePowerPhaseB_kW | REAL | IOD_SS1_TCP | 44069
SS1PMMActivePowerPhaseC_kW | REAL | IOD_SS1_TCP | 44071
SS1PMMAlarmPhase1C01_16_60to80 | UINT | IOD_SS1_TCP | 46001
SS1PMMAlarmPhase1C01_16_over80 | UINT | IOD_SS1_TCP | 46002
SS1PMMAlarmPhase1C17_32_60to80 | UINT | IOD_SS1_TCP | 46003
SS1PMMAlarmPhase1C17_32_over80 | UINT | IOD_SS1_TCP | 46004
SS1PMMAlarmPhase1C33_42_60to80 | UINT | IOD_SS1_TCP | 46005
SS1PMMAlarmPhase1C33_42_over80 | UINT | IOD_SS1_TCP | 46006
SS1PMMAlarmPhase2C01_16_60to80 | UINT | IOD_SS1_TCP | 46007
SS1PMMAlarmPhase2C01_16_over80 | UINT | IOD_SS1_TCP | 46008
SS1PMMAlarmPhase2C17_32_60to80 | UINT | IOD_SS1_TCP | 46009
SS1PMMAlarmPhase2C17_32_over80 | UINT | IOD_SS1_TCP | 46010
SS1PMMAlarmPhase2C33_42_60to80 | UINT | IOD_SS1_TCP | 46011
SS1PMMAlarmPhase2C33_42_over80 | UINT | IOD_SS1_TCP | 46012
SS1PMMAlarmPhase3C01_16_60to80 | UINT | IOD_SS1_TCP | 46013
SS1PMMAlarmPhase3C01_16_over80 | UINT | IOD_SS1_TCP | 46014
SS1PMMAlarmPhase3C17_32_60to80 | UINT | IOD_SS1_TCP | 46015
SS1PMMAlarmPhase3C17_32_over80 | UINT | IOD_SS1_TCP | 46016
SS1PMMAlarmPhase3C33_42_60to80 | UINT | IOD_SS1_TCP | 46017
SS1PMMAlarmPhase3C33_42_over80 | UINT | IOD_SS1_TCP | 46018
SS1PMMAparentPowerPhaseA | REAL | IOD_SS1_TCP | 44073
SS1PMMAparentPowerPhaseB | REAL | IOD_SS1_TCP | 44075
SS1PMMAparentPowerPhaseC | REAL | IOD_SS1_TCP | 44077
SS1PMMAverageCurrent_A | REAL | IOD_SS1_TCP | 44079
SS1PMMAveragePhaseToNeutral_V | REAL | IOD_SS1_TCP | 44081 | 0 | 270 | 0 | 270 | V | ###.#
SS1PMMAveragePhaseToPhase_V | REAL | IOD_SS1_TCP | 44083 | 0 | 450 | 0 | 450 | V | ###.#
SS1PMMCurrentInPhaseA_A | REAL | IOD_SS1_TCP | 44085 | 0 | 250 | 0 | 250 | A | ###.#
SS1PMMCurrentInPhaseB_A | REAL | IOD_SS1_TCP | 44087 | 0 | 250 | 0 | 250 | A | ###.#
SS1PMMCurrentInPhaseC_A | REAL | IOD_SS1_TCP | 44089 | 0 | 250 | 0 | 250 | A | ###.#
SS1PMMFrequency_Hz | REAL | IOD_SS1_TCP | 44091 | 0 | 60 | 0 | 60 | Hz | ##.#
SS1PMMPhase1Current10 | REAL | IOD_SS1_TCP | 44093 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current11 | REAL | IOD_SS1_TCP | 44095 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current12 | REAL | IOD_SS1_TCP | 44097 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current13 | REAL | IOD_SS1_TCP | 44099 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current14 | REAL | IOD_SS1_TCP | 44101 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current15 | REAL | IOD_SS1_TCP | 44103 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current16 | REAL | IOD_SS1_TCP | 44105 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current17 | REAL | IOD_SS1_TCP | 44107 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current18 | REAL | IOD_SS1_TCP | 44109 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current19 | REAL | IOD_SS1_TCP | 44111 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current1 | REAL | IOD_SS1_TCP | 44113 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current20 | REAL | IOD_SS1_TCP | 44115 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current21 | REAL | IOD_SS1_TCP | 44117 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current22 | REAL | IOD_SS1_TCP | 44119 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current23 | REAL | IOD_SS1_TCP | 44121 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current24 | REAL | IOD_SS1_TCP | 44123 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current25 | REAL | IOD_SS1_TCP | 44125 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current26 | REAL | IOD_SS1_TCP | 44127 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current27 | REAL | IOD_SS1_TCP | 44129 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current28 | REAL | IOD_SS1_TCP | 44131 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current29 | REAL | IOD_SS1_TCP | 44133 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current2 | REAL | IOD_SS1_TCP | 44135 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current30 | REAL | IOD_SS1_TCP | 44137 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current31 | REAL | IOD_SS1_TCP | 44139 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current32 | REAL | IOD_SS1_TCP | 44141 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current33 | REAL | IOD_SS1_TCP | 44143 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current34 | REAL | IOD_SS1_TCP | 44145 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current35 | REAL | IOD_SS1_TCP | 44147 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current36 | REAL | IOD_SS1_TCP | 44149 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current37 | REAL | IOD_SS1_TCP | 44151 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current38 | REAL | IOD_SS1_TCP | 44153 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current39 | REAL | IOD_SS1_TCP | 44155 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current3 | REAL | IOD_SS1_TCP | 44157 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current40 | REAL | IOD_SS1_TCP | 44159 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current41 | REAL | IOD_SS1_TCP | 44161 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current42 | REAL | IOD_SS1_TCP | 44163 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current4 | REAL | IOD_SS1_TCP | 44165 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current5 | REAL | IOD_SS1_TCP | 44167 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current6 | REAL | IOD_SS1_TCP | 44169 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current7 | REAL | IOD_SS1_TCP | 44171 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current8 | REAL | IOD_SS1_TCP | 44173 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase1Current9 | REAL | IOD_SS1_TCP | 44175 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current10 | REAL | IOD_SS1_TCP | 44177 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current11 | REAL | IOD_SS1_TCP | 44179 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current12 | REAL | IOD_SS1_TCP | 44181 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current13 | REAL | IOD_SS1_TCP | 44183 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current14 | REAL | IOD_SS1_TCP | 44185 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current15 | REAL | IOD_SS1_TCP | 44187 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current16 | REAL | IOD_SS1_TCP | 44189 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current17 | REAL | IOD_SS1_TCP | 44191 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current18 | REAL | IOD_SS1_TCP | 44193 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current19 | REAL | IOD_SS1_TCP | 44195 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current1 | REAL | IOD_SS1_TCP | 44197 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current20 | REAL | IOD_SS1_TCP | 44199 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current21 | REAL | IOD_SS1_TCP | 44201 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current22 | REAL | IOD_SS1_TCP | 44203 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current23 | REAL | IOD_SS1_TCP | 44205 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current24 | REAL | IOD_SS1_TCP | 44207 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current25 | REAL | IOD_SS1_TCP | 44209 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current26 | REAL | IOD_SS1_TCP | 44211 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current27 | REAL | IOD_SS1_TCP | 44213 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current28 | REAL | IOD_SS1_TCP | 44215 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current29 | REAL | IOD_SS1_TCP | 44217 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current2 | REAL | IOD_SS1_TCP | 44219 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current30 | REAL | IOD_SS1_TCP | 44221 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current31 | REAL | IOD_SS1_TCP | 44223 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current32 | REAL | IOD_SS1_TCP | 44225 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current33 | REAL | IOD_SS1_TCP | 44227 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current34 | REAL | IOD_SS1_TCP | 44229 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current35 | REAL | IOD_SS1_TCP | 44231 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current36 | REAL | IOD_SS1_TCP | 44233 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current37 | REAL | IOD_SS1_TCP | 44235 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current38 | REAL | IOD_SS1_TCP | 44237 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current39 | REAL | IOD_SS1_TCP | 44239 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current3 | REAL | IOD_SS1_TCP | 44241 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current40 | REAL | IOD_SS1_TCP | 44243 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current41 | REAL | IOD_SS1_TCP | 44245 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current42 | REAL | IOD_SS1_TCP | 44247 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current4 | REAL | IOD_SS1_TCP | 44249 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current5 | REAL | IOD_SS1_TCP | 44251 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current6 | REAL | IOD_SS1_TCP | 44253 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current7 | REAL | IOD_SS1_TCP | 44255 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current8 | REAL | IOD_SS1_TCP | 44257 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase2Current9 | REAL | IOD_SS1_TCP | 44259 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current10 | REAL | IOD_SS1_TCP | 44261 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current11 | REAL | IOD_SS1_TCP | 44263 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current12 | REAL | IOD_SS1_TCP | 44265 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current13 | REAL | IOD_SS1_TCP | 44267 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current14 | REAL | IOD_SS1_TCP | 44269 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current15 | REAL | IOD_SS1_TCP | 44271 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current16 | REAL | IOD_SS1_TCP | 44273 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current17 | REAL | IOD_SS1_TCP | 44275 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current18 | REAL | IOD_SS1_TCP | 44277 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current19 | REAL | IOD_SS1_TCP | 44279 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current1 | REAL | IOD_SS1_TCP | 44281 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current20 | REAL | IOD_SS1_TCP | 44283 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current21 | REAL | IOD_SS1_TCP | 44285 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current22 | REAL | IOD_SS1_TCP | 44287 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current23 | REAL | IOD_SS1_TCP | 44289 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current24 | REAL | IOD_SS1_TCP | 44291 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current25 | REAL | IOD_SS1_TCP | 44293 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current26 | REAL | IOD_SS1_TCP | 44295 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current27 | REAL | IOD_SS1_TCP | 44297 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current28 | REAL | IOD_SS1_TCP | 44299 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current29 | REAL | IOD_SS1_TCP | 44301 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current2 | REAL | IOD_SS1_TCP | 44303 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current30 | REAL | IOD_SS1_TCP | 44305 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current31 | REAL | IOD_SS1_TCP | 44307 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current32 | REAL | IOD_SS1_TCP | 44309 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current33 | REAL | IOD_SS1_TCP | 44311 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current34 | REAL | IOD_SS1_TCP | 44313 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current35 | REAL | IOD_SS1_TCP | 44315 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current36 | REAL | IOD_SS1_TCP | 44317 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current37 | REAL | IOD_SS1_TCP | 44319 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current38 | REAL | IOD_SS1_TCP | 44321 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current39 | REAL | IOD_SS1_TCP | 44323 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current3 | REAL | IOD_SS1_TCP | 44325 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current40 | REAL | IOD_SS1_TCP | 44327 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current41 | REAL | IOD_SS1_TCP | 44329 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current42 | REAL | IOD_SS1_TCP | 44331 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current4 | REAL | IOD_SS1_TCP | 44333 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current5 | REAL | IOD_SS1_TCP | 44335 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current6 | REAL | IOD_SS1_TCP | 44337 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current7 | REAL | IOD_SS1_TCP | 44339 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current8 | REAL | IOD_SS1_TCP | 44341 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPhase3Current9 | REAL | IOD_SS1_TCP | 44343 | 0 | 16 | 0 | 16 | A | ##.#
SS1PMMPowerFactorSys | REAL | IOD_SS1_TCP | 44345 | -1 | 1 | -1 | 1 |  | ##.#
SS1PMMReactiveEnergyConsumed_kVARh | REAL | IOD_SS1_TCP | 44347 |  |  |  |  | kVArh | ####.#
SS1PMMReactivePowerPhaseA | REAL | IOD_SS1_TCP | 44349 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS1PMMReactivePowerPhaseB | REAL | IOD_SS1_TCP | 44351 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS1PMMReactivePowerPhaseC | REAL | IOD_SS1_TCP | 44353 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS1PMMTotalActivePower_kW | REAL | IOD_SS1_TCP | 44355 | 0 | 300 | 0 | 300 | kW | ####.#
SS1PMMTotalAparentPower_kVA | REAL | IOD_SS1_TCP | 44357 | 0 | 300 | 0 | 300 | kVA | ####.#
SS1PMMTotalPowerFactor | REAL | IOD_SS1_TCP | 44359 | 0 | 1 | 0 | 1 |  | ####.#
SS1PMMTotalReactivePower_kVAR | REAL | IOD_SS1_TCP | 44361 | 0 | 300 | 0 | 300 | kVAr | ####.#
SS1PMMVirA_fsys | REAL | IOD_SS1_TCP | 44363 | 0 | 70 | 0 | 70 | Hz | ####.#
SS1PMMVirA_Isys | REAL | IOD_SS1_TCP | 44365 | 0 | 1000 | 0 | 1000 | A | ####.#
SS1PMMVirA_PFsys | REAL | IOD_SS1_TCP | 44367 | 0 | 1 | 0 | 0 | 1 | ####.#
SS1PMMVirA_Psys | REAL | IOD_SS1_TCP | 44369 | 0 | 300 | 0 | 300 | kW | ####.#
SS1PMMVirA_Qsys | REAL | IOD_SS1_TCP | 44371 | 0 | 300 | 0 | 300 | kVAr | ####.#
SS1PMMVirA_Ssys | REAL | IOD_SS1_TCP | 44373 | 0 | 300 | 0 | 300 | kVA | ####.#
SS1PMMVirA_Usys | REAL | IOD_SS1_TCP | 44375 | 0 | 450 | 0 | 450 | V | ####.#
SS1PMMVirB_fsys | REAL | IOD_SS1_TCP | 44377 | 0 | 70 | 0 | 70 | Hz | ####.#
SS1PMMVirB_Isys | REAL | IOD_SS1_TCP | 44379 | 0 | 1000 | 0 | 1000 | A | ####.#
SS1PMMVirB_PFsys | REAL | IOD_SS1_TCP | 44381 | 0 | 1 | 0 | 0 | 1 | ####.#
SS1PMMVirB_Psys | REAL | IOD_SS1_TCP | 44383 | 0 | 300 | 0 | 300 | kW | ####.#
SS1PMMVirB_Qsys | REAL | IOD_SS1_TCP | 44385 | 0 | 300 | 0 | 300 | kVAr | ####.#
SS1PMMVirB_Ssys | REAL | IOD_SS1_TCP | 44387 | 0 | 300 | 0 | 300 | kVA | ####.#
SS1PMMVirB_Usys | REAL | IOD_SS1_TCP | 44389 | 0 | 450 | 0 | 450 | V | ####.#
SS1PMMVirBActiveEnergyConsumed_kWh | REAL | IOD_SS1_TCP | 44391 |  |  |  |  | kVArh | ####.#
SS1PMMVirBActivePowerPhaseA_kW | REAL | IOD_SS1_TCP | 44393 | 0 | 100 | 0 | 100 | kW | ####.#
SS1PMMVirBActivePowerPhaseB_kW | REAL | IOD_SS1_TCP | 44395 | 0 | 100 | 0 | 100 | kW | ####.#
SS1PMMVirBActivePowerPhaseC_kW | REAL | IOD_SS1_TCP | 44397 | 0 | 100 | 0 | 100 | kW | ####.#
SS1PMMVirBAparentPowerPhaseA | REAL | IOD_SS1_TCP | 44399 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS1PMMVirBAparentPowerPhaseB | REAL | IOD_SS1_TCP | 44401 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS1PMMVirBAparentPowerPhaseC | REAL | IOD_SS1_TCP | 44403 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS1PMMVirBAverageCurrent_A | REAL | IOD_SS1_TCP | 44405 | 0 | 100 | 0 | 100 | A | ####.#
SS1PMMVirBAveragePhaseToNeutral_V | REAL | IOD_SS1_TCP | 44407 | 0 | 270 | 0 | 270 | V | ####.#
SS1PMMVirBAveragePhaseToPhase_V | REAL | IOD_SS1_TCP | 44409 | 0 | 270 | 0 | 270 | V | ####.#
SS1PMMVirBCurrentInPhaseA_A | REAL | IOD_SS1_TCP | 44411 | 0 | 100 | 0 | 100 | A | ####.#
SS1PMMVirBCurrentInPhaseB_A | REAL | IOD_SS1_TCP | 44413 | 0 | 100 | 0 | 100 | A | ####.#
SS1PMMVirBCurrentInPhaseC_A | REAL | IOD_SS1_TCP | 44415 | 0 | 100 | 0 | 100 | A | ####.#
SS1PMMVirBFrequency_Hz | REAL | IOD_SS1_TCP | 44417 | 0 | 70 | 0 | 70 | Hz | ####.#
SS1PMMVirBPowerFactorSys | REAL | IOD_SS1_TCP | 44419 | 0 | 1 | 0 | 1 |  | ####.#
SS1PMMVirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS1_TCP | 44421 |  |  |  |  | kVArh | ####.#
SS1PMMVirBReactivePowerPhaseA | REAL | IOD_SS1_TCP | 44423 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS1PMMVirBReactivePowerPhaseB | REAL | IOD_SS1_TCP | 44425 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS1PMMVirBReactivePowerPhaseC | REAL | IOD_SS1_TCP | 44427 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS1PMMVirBTotalActivePower_kW | REAL | IOD_SS1_TCP | 44429 | 0 | 300 | 0 | 300 | kW | ####.#
SS1PMMVirBTotalAparentPower_kVA | REAL | IOD_SS1_TCP | 44431 | 0 | 300 | 0 | 300 | kVA | ####.#
SS1PMMVirBTotalPowerFactor | REAL | IOD_SS1_TCP | 44433 | 0 | 1 | 0 | 1 |  | ####.#
SS1PMMVirBTotalReactivePower_kVAR | REAL | IOD_SS1_TCP | 44435 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS1PMMVirBVoltageBetweenPhaseAB_V | REAL | IOD_SS1_TCP | 44437 | 0 | 450 | 0 | 450 | V | ####.#
SS1PMMVirBVoltageBetweenPhaseAN_V | REAL | IOD_SS1_TCP | 44439 | 0 | 270 | 0 | 270 | V | ####.#
SS1PMMVirBVoltageBetweenPhaseBC_V | REAL | IOD_SS1_TCP | 44441 | 0 | 450 | 0 | 450 | V | ####.#
SS1PMMVirBVoltageBetweenPhaseBN_V | REAL | IOD_SS1_TCP | 44443 | 0 | 270 | 0 | 270 | V | ####.#
SS1PMMVirBVoltageBetweenPhaseCA_V | REAL | IOD_SS1_TCP | 44445 | 0 | 450 | 0 | 450 | V | ####.#
SS1PMMVirBVoltageBetweenPhaseCN_V | REAL | IOD_SS1_TCP | 44447 | 0 | 270 | 0 | 270 | V | ####.#
SS1PMMVoltageBetweenPhaseAB_V | REAL | IOD_SS1_TCP | 44449 | 0 | 450 | 0 | 450 | V | ####.#
SS1PMMVoltageBetweenPhaseAN_V | REAL | IOD_SS1_TCP | 44451 | 0 | 270 | 0 | 270 | V | ####.#
SS1PMMVoltageBetweenPhaseBC_V | REAL | IOD_SS1_TCP | 44453 | 0 | 450 | 0 | 450 | V | ####.#
SS1PMMVoltageBetweenPhaseBN_V | REAL | IOD_SS1_TCP | 44455 | 0 | 270 | 0 | 270 | V | ####.#
SS1PMMVoltageBetweenPhaseCA_V | REAL | IOD_SS1_TCP | 44457 | 0 | 450 | 0 | 450 | V | ####.#
SS1PMMVoltageBetweenPhaseCN_V | REAL | IOD_SS1_TCP | 44459 | 0 | 270 | 0 | 270 | V | ####.#
SS1PMM1OverCurrentBetw1 | DIGITAL | IOD_SS1_TCP | 00164
SS1PMM1OverCurrentBetw2 | DIGITAL | IOD_SS1_TCP | 00165
SS1PMM1OverCurrentBetw3 | DIGITAL | IOD_SS1_TCP | 00166
SS1PMM1OverCurrentOver1 | DIGITAL | IOD_SS1_TCP | 00167
SS1PMM1OverCurrentOver2 | DIGITAL | IOD_SS1_TCP | 00168
SS1PMM1OverCurrentOver3 | DIGITAL | IOD_SS1_TCP | 00169
SS1PMM1OverVoltage | DIGITAL | IOD_SS1_TCP | 00170
SS1RocniVklopKlima1 | DIGITAL | IOD_SS1_TCP | 00171
SS1RocniVklopKlima2 | DIGITAL | IOD_SS1_TCP | 00172
SS1RocniVklopKlima3 | DIGITAL | IOD_SS1_TCP | 00173
SS1SinhronizacijaPanelOK | DIGITAL | IOD_SS1_TCP | 00174
SS1SinhronizirajCas_Panel | DIGITAL | IOD_SS1_TCP | 00175
SS1SKTemp1 | REAL | IOD_SS1_TCP | 44461 | 0 | 60 | 0 | 60 | °C | ##.#
SS1SKTemp2 | REAL | IOD_SS1_TCP | 44463 | 0 | 60 | 0 | 60 | °C | ##.#
SS1SKTemp3 | REAL | IOD_SS1_TCP | 44465 | 0 | 60 | 0 | 60 | °C | ##.#
SS1SKTempKontrSoba | REAL | IOD_SS1_TCP | 44467 | 0 | 60 | 0 | 60 | °C | ##.#
SS1SKTempLinkProstor | REAL | IOD_SS1_TCP | 44469 | 0 | 60 | 0 | 60 | °C | ##.#
SS1SKTempServSoba1Povpr | REAL | IOD_SS1_TCP | 44471 | 0 | 60 | 0 | 60 | °C | ##.#
SS1SkupneNapakeNaprav_Klima1 | DIGITAL | IOD_SS1_TCP | 00176
SS1SkupneNapakeNaprav_Klima2 | DIGITAL | IOD_SS1_TCP | 00177
SS1SkupneNapakeNaprav_Klima3 | DIGITAL | IOD_SS1_TCP | 00178
SS1SkupneNapakeNaprav_Komunikacija | DIGITAL | IOD_SS1_TCP | 00179
SS1SkupneNapakeNaprav_PMMVirA | DIGITAL | IOD_SS1_TCP | 00180
SS1SkupneNapakeNaprav_PMMVirB | DIGITAL | IOD_SS1_TCP | 00181
SS1SkupneNapakeNaprav_PMMVirBVirA | DIGITAL | IOD_SS1_TCP | 00182
SS1SkupneNapakeNaprav_TempVlaga | DIGITAL | IOD_SS1_TCP | 00183
SS1SKVlaga1 | REAL | IOD_SS1_TCP | 44473 | 0 | 100 | 0 | 100 | % | ##.#
SS1SKVlaga2 | REAL | IOD_SS1_TCP | 44475 | 0 | 100 | 0 | 100 | % | ##.#
SS1SKVlaga3 | REAL | IOD_SS1_TCP | 44477 | 0 | 100 | 0 | 100 | % | ##.#
SS1SKVlagaKontrSoba | REAL | IOD_SS1_TCP | 44479 | 0 | 100 | 0 | 100 | % | ##.#
SS1SKVlagaLinkProstor | REAL | IOD_SS1_TCP | 44481 | 0 | 100 | 0 | 100 | % | ##.#
SS1StanjeKlimat1_Delovanje | DIGITAL | IOD_SS1_TCP | 00184
SS1StanjeKlimat2_Delovanje | DIGITAL | IOD_SS1_TCP | 00185
SS1StanjeKlimat3_Delovanje | DIGITAL | IOD_SS1_TCP | 00186
SS1StanjeSP1_Delovanje | DIGITAL | IOD_SS1_TCP | 00187
SS1StanjeSP2_Delovanje | DIGITAL | IOD_SS1_TCP | 00188
SS1StanjeSP3_Delovanje | DIGITAL | IOD_SS1_TCP | 00189
SS1StanjeSP4_Delovanje | DIGITAL | IOD_SS1_TCP | 00190
SS1StanjeSP5_Delovanje | DIGITAL | IOD_SS1_TCP | 00191
SS1StanjeUPSKrmOmara_BaterijskiNacin | DIGITAL | IOD_SS1_TCP | 00192
SS1StanjeUPSKrmOmara_Polnenje | DIGITAL | IOD_SS1_TCP | 00193
SS1StUrZaPreklopKlim | INT | IOD_SS1_TCP | 40011
SS1TempZaAlarmTIA123 | REAL | IOD_SS1_TCP | 44483 | 0 | 60 | 0 | 60 | °C | ##.#
SS1TempZaAlarmTIA4 | REAL | IOD_SS1_TCP | 44485 | 0 | 60 | 0 | 60 | °C | ##.#
SS1TempZaAlarmTIA5 | REAL | IOD_SS1_TCP | 44487 | 0 | 60 | 0 | 60 | °C | ##.#
SS1TempZaVklopObehKlim | REAL | IOD_SS1_TCP | 44489 | 0 | 60 | 0 | 60 | °C | ##.#
SS1UPSstatus_Prikaz_PanelSCADA | INT | IOD_SS1_TCP | 40012
SS1UserCurrentLevel | INT | IOD_SS1_TCP | 40013
SS1UserLoggedIn | DIGITAL | IOD_SS1_TCP | 00194
SS1UserName | STRING | IOD_SS1_TCP | 45001[15]
SS1XVH_AlarmOn | DIGITAL | IOD_SS1_TCP | 00195
SS1OnemAlarmPon | DIGITAL | IOD_SS1_disk | D325
SS1OmogociVseAlarme | DIGITAL | IOD_SS1_disk | D328
SS1OmogociVseSMSAlarme | DIGITAL | IOD_SS1_disk | D321
SS1OmogociVseDogodke_DO | DIGITAL | IOD_SS1_disk | D322
SS1OmogociVseDogodke_DI | DIGITAL | IOD_SS1_disk | D323
SS1OmogociVseDogodke_COM | DIGITAL | IOD_SS1_disk | D324
SS1PricetekSMSAlarmov1 | INT | IOD_SS1_disk | I21 | [5 empty] | ##
SS1KonecSMSAlarmov1 | INT | IOD_SS1_disk | I22 | [5 empty] | ##
SS1ErrCommScada_Omogoci | DIGITAL | IOD_SS1_disk | D326
Test | INT | IOD_SS1_disk | I23
SS1Klimat1_Vklop | DIGITAL | IOD_SS1_TCP | 00196
SS1Klimat2_Vklop | DIGITAL | IOD_SS1_TCP | 00197
SS1Klimat3_Vklop | DIGITAL | IOD_SS1_TCP | 00198
SS1PricetekSMSAlarmov2 | INT | IOD_SS1_disk | I24 | [5 empty] | ##
SS1KonecSMSAlarmov2 | INT | IOD_SS1_disk | I25 | [5 empty] | ##
SS1OnemAlarmPon2 | DIGITAL | IOD_SS1_disk | D327
SS1ErrCommScada2 | DIGITAL | IOD_SS1_TCP | 00199
SS1ComSCADA2 | DIGITAL | IOD_SS1_TCP | 00200
SS1ErrCommScada_Omogoci2 | DIGITAL | IOD_SS1_disk | D330
SS1Server_A_Izpad | DIGITAL | IOD_SS1_disk | D331
SS1Server_B_Izpad | DIGITAL | IOD_SS1_disk | D332
SS1ComSCADA_stevec3 | INT | IOD_SS1_mem | I3450
SS1ComSCADA_stevec | INT | IOD_SS1_mem | I3452
SS1ComSCADA3 | DIGITAL | IOD_SS1_TCP | 00201
SS1kom_nast_cas_izpada | UINT | IOD_SS1_TCP | 46019
BSS1_omogoci_sms | DIGITAL | IOD_SS1_disk | D4000[200]

## XSoft
mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Write_BOOL(FC) | mod_Write_Word(FC) | mod_Write_Word(FC) | mod_Write_dWord(FC) | mod_Write_dWord(FC) | mod_Write_String(FC)
(*Branje BOOL*) | (*Branje INT*) | (*Branje UINT*) | (*Branje LONG*) | (*Branje REAL*) | (*Branje STRING*) | (*Pisanje BOOL*) | (*Pisanje INT*) | (*Pisanje UINT*) | (*Pisanje LONG*) | (*Pisanje REAL*) | (*Pisanje STRING*)
(**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**)
mind_bool[0]:=AlarmKlimat1_Napaka; | mind[0]:=DatumCas.Dan; | mind[6000]:=PMM.AlarmPhase[1].C01_16_60to80; |  | Read_Real(rVar:=AktualniSetPointTemp,lo:=4000,hi:=4001); | Read_String(sVar:=UserName,start:=5000); | 0:AlarmKlimat1_Napaka:=Bit_0; | 0:DatumCas.Dan:=Byte_0; | 6000:PMM.AlarmPhase[1].C01_16_60to80:=Word_01; |  | 4001:AktualniSetPointTemp:=Real_0; | 5000:UserName:=String_0;
mind_bool[1]:=AlarmKlimat2_Napaka; | mind[1]:=DatumCas.Leto; | mind[6001]:=PMM.AlarmPhase[1].C01_16_over80; |  | Read_Real(rVar:=AktualniSetPointVlaga,lo:=4002,hi:=4003); |  | 1:AlarmKlimat2_Napaka:=Bit_0; | 1:DatumCas.Leto:=Byte_0; | 6001:PMM.AlarmPhase[1].C01_16_over80:=Word_01; |  | 4003:AktualniSetPointVlaga:=Real_0;
mind_bool[2]:=AlarmKlimat3_Napaka; | mind[2]:=DatumCas.Leto2; | mind[6002]:=PMM.AlarmPhase[1].C17_32_60to80; |  | Read_Real(rVar:=Klima[1].NastMaxTemp,lo:=4004,hi:=4005); |  | 2:AlarmKlimat3_Napaka:=Bit_0; | 2:DatumCas.Leto2:=Word_01; | 6002:PMM.AlarmPhase[1].C17_32_60to80:=Word_01; |  | 4005:Klima[1].NastMaxTemp:=Real_0;
mind_bool[3]:=AlarmLAH1_RazlitjeVode; | mind[3]:=DatumCas.Mesec; | mind[6003]:=PMM.AlarmPhase[1].C17_32_over80; |  | Read_Real(rVar:=Klima[1].NastMaxVlaznost,lo:=4006,hi:=4007); |  | 3:AlarmLAH1_RazlitjeVode:=Bit_0; | 3:DatumCas.Mesec:=Byte_0; | 6003:PMM.AlarmPhase[1].C17_32_over80:=Word_01; |  | 4007:Klima[1].NastMaxVlaznost:=Real_0;
mind_bool[4]:=AlarmLAH2_RazlitjeVode; | mind[4]:=DatumCas.Minuta; | mind[6004]:=PMM.AlarmPhase[1].C33_42_60to80; |  | Read_Real(rVar:=Klima[1].NastMinTemp,lo:=4008,hi:=4009); |  | 4:AlarmLAH2_RazlitjeVode:=Bit_0; | 4:DatumCas.Minuta:=Byte_0; | 6004:PMM.AlarmPhase[1].C33_42_60to80:=Word_01; |  | 4009:Klima[1].NastMinTemp:=Real_0;
mind_bool[5]:=AlarmSinhronizacijaNOK; | mind[5]:=DatumCas.Sekunda; | mind[6005]:=PMM.AlarmPhase[1].C33_42_over80; |  | Read_Real(rVar:=Klima[1].NastMinVlaznost,lo:=4010,hi:=4011); |  | 5:AlarmSinhronizacijaNOK:=Bit_0; | 5:DatumCas.Sekunda:=Byte_0; | 6005:PMM.AlarmPhase[1].C33_42_over80:=Word_01; |  | 4011:Klima[1].NastMinVlaznost:=Real_0;
mind_bool[6]:=AlarmSP1_Napaka; | mind[6]:=DatumCas.Ura; | mind[6006]:=PMM.AlarmPhase[2].C01_16_60to80; |  | Read_Real(rVar:=Klima[1].NastTempProstora,lo:=4012,hi:=4013); |  | 6:AlarmSP1_Napaka:=Bit_0; | 6:DatumCas.Ura:=Byte_0; | 6006:PMM.AlarmPhase[2].C01_16_60to80:=Word_01; |  | 4013:Klima[1].NastTempProstora:=Real_0;
mind_bool[7]:=AlarmSP2_Napaka; | mind[7]:=Klima[1].Vlazilec_Stanja; | mind[6007]:=PMM.AlarmPhase[2].C01_16_over80; |  | Read_Real(rVar:=Klima[1].NastVlaznost,lo:=4014,hi:=4015); |  | 7:AlarmSP2_Napaka:=Bit_0; | 7:Klima[1].Vlazilec_Stanja:=Byte_0; | 6007:PMM.AlarmPhase[2].C01_16_over80:=Word_01; |  | 4015:Klima[1].NastVlaznost:=Real_0;
mind_bool[8]:=AlarmSP3_Napaka; | mind[8]:=Klima[2].Vlazilec_Stanja; | mind[6008]:=PMM.AlarmPhase[2].C17_32_60to80; |  | Read_Real(rVar:=Klima[1].Pritisk,lo:=4016,hi:=4017); |  | 8:AlarmSP3_Napaka:=Bit_0; | 8:Klima[2].Vlazilec_Stanja:=Byte_0; | 6008:PMM.AlarmPhase[2].C17_32_60to80:=Word_01; |  | 4017:Klima[1].Pritisk:=Real_0;
mind_bool[9]:=AlarmSP4_Napaka; | mind[9]:=Klima[3].Vlazilec_Stanja; | mind[6009]:=PMM.AlarmPhase[2].C17_32_over80; |  | Read_Real(rVar:=Klima[1].TemperaturaProstora,lo:=4018,hi:=4019); |  | 9:AlarmSP4_Napaka:=Bit_0; | 9:Klima[3].Vlazilec_Stanja:=Byte_0; | 6009:PMM.AlarmPhase[2].C17_32_over80:=Word_01; |  | 4019:Klima[1].TemperaturaProstora:=Real_0;
mind_bool[10]:=AlarmSP5_Napaka; | mind[10]:=StUrZaPreklopKlim; | mind[6010]:=PMM.AlarmPhase[2].C33_42_60to80; |  | Read_Real(rVar:=Klima[1].VlaznostProstora,lo:=4020,hi:=4021); |  | 10:AlarmSP5_Napaka:=Bit_0; | 10:StUrZaPreklopKlim:=Word_01; | 6010:PMM.AlarmPhase[2].C33_42_60to80:=Word_01; |  | 4021:Klima[1].VlaznostProstora:=Real_0;
mind_bool[11]:=AlarmTempTIA123Previsoka; | mind[11]:=UPSstatus_Prikaz_PanelSCADA; | mind[6011]:=PMM.AlarmPhase[2].C33_42_over80; |  | Read_Real(rVar:=Klima[2].NastMaxTemp,lo:=4022,hi:=4023); |  | 11:AlarmTempTIA123Previsoka:=Bit_0; | 11:UPSstatus_Prikaz_PanelSCADA:=Byte_0; | 6011:PMM.AlarmPhase[2].C33_42_over80:=Word_01; |  | 4023:Klima[2].NastMaxTemp:=Real_0;
mind_bool[12]:=AlarmTempTIA4Previsoka; | mind[12]:=UserCurrentLevel; | mind[6012]:=PMM.AlarmPhase[3].C01_16_60to80; |  | Read_Real(rVar:=Klima[2].NastMaxVlaznost,lo:=4024,hi:=4025); |  | 12:AlarmTempTIA4Previsoka:=Bit_0; | 12:UserCurrentLevel:=Byte_0; | 6012:PMM.AlarmPhase[3].C01_16_60to80:=Word_01; |  | 4025:Klima[2].NastMaxVlaznost:=Real_0;
mind_bool[13]:=AlarmTempTIA5Previsoka; |  | mind[6013]:=PMM.AlarmPhase[3].C01_16_over80; |  | Read_Real(rVar:=Klima[2].NastMinTemp,lo:=4026,hi:=4027); |  | 13:AlarmTempTIA5Previsoka:=Bit_0; |  | 6013:PMM.AlarmPhase[3].C01_16_over80:=Word_01; |  | 4027:Klima[2].NastMinTemp:=Real_0;
mind_bool[14]:=AlarmTSTempPrevisoka; |  | mind[6014]:=PMM.AlarmPhase[3].C17_32_60to80; |  | Read_Real(rVar:=Klima[2].NastMinVlaznost,lo:=4028,hi:=4029); |  | 14:AlarmTSTempPrevisoka:=Bit_0; |  | 6014:PMM.AlarmPhase[3].C17_32_60to80:=Word_01; |  | 4029:Klima[2].NastMinVlaznost:=Real_0;
mind_bool[15]:=AlarmUPSKrmOmara_Alarm; |  | mind[6015]:=PMM.AlarmPhase[3].C17_32_over80; |  | Read_Real(rVar:=Klima[2].NastTempProstora,lo:=4030,hi:=4031); |  | 15:AlarmUPSKrmOmara_Alarm:=Bit_0; |  | 6015:PMM.AlarmPhase[3].C17_32_over80:=Word_01; |  | 4031:Klima[2].NastTempProstora:=Real_0;
mind_bool[16]:=ComSCADA; |  | mind[6016]:=PMM.AlarmPhase[3].C33_42_60to80; |  | Read_Real(rVar:=Klima[2].NastVlaznost,lo:=4032,hi:=4033); |  | 16:ComSCADA:=Bit_0; |  | 6016:PMM.AlarmPhase[3].C33_42_60to80:=Word_01; |  | 4033:Klima[2].NastVlaznost:=Real_0;
mind_bool[17]:=ComSCADA1; |  | mind[6017]:=PMM.AlarmPhase[3].C33_42_over80; |  | Read_Real(rVar:=Klima[2].Pritisk,lo:=4034,hi:=4035); |  | 17:ComSCADA1:=Bit_0; |  | 6017:PMM.AlarmPhase[3].C33_42_over80:=Word_01; |  | 4035:Klima[2].Pritisk:=Real_0;
mind_bool[18]:=ErrComKlima[1]; |  | mind[6018]:=kom_nast_cas_izpada; |  | Read_Real(rVar:=Klima[2].TemperaturaProstora,lo:=4036,hi:=4037); |  | 18:ErrComKlima[1]:=Bit_0; |  | 6018:kom_nast_cas_izpada:=Word_01; |  | 4037:Klima[2].TemperaturaProstora:=Real_0;
mind_bool[19]:=ErrComKlima[2]; |  |  |  | Read_Real(rVar:=Klima[2].VlaznostProstora,lo:=4038,hi:=4039); |  | 19:ErrComKlima[2]:=Bit_0; |  |  |  | 4039:Klima[2].VlaznostProstora:=Real_0;
mind_bool[20]:=ErrComKlima[3]; |  |  |  | Read_Real(rVar:=Klima[3].NastMaxTemp,lo:=4040,hi:=4041); |  | 20:ErrComKlima[3]:=Bit_0; |  |  |  | 4041:Klima[3].NastMaxTemp:=Real_0;
mind_bool[21]:=ErrCommScada; |  |  |  | Read_Real(rVar:=Klima[3].NastMaxVlaznost,lo:=4042,hi:=4043); |  | 21:ErrCommScada:=Bit_0; |  |  |  | 4043:Klima[3].NastMaxVlaznost:=Real_0;
mind_bool[22]:=ErrComPanelPLC; |  |  |  | Read_Real(rVar:=Klima[3].NastMinTemp,lo:=4044,hi:=4045); |  | 22:ErrComPanelPLC:=Bit_0; |  |  |  | 4045:Klima[3].NastMinTemp:=Real_0;
mind_bool[23]:=ErrComPMM; |  |  |  | Read_Real(rVar:=Klima[3].NastMinVlaznost,lo:=4046,hi:=4047); |  | 23:ErrComPMM:=Bit_0; |  |  |  | 4047:Klima[3].NastMinVlaznost:=Real_0;
mind_bool[24]:=ErrComPort2; |  |  |  | Read_Real(rVar:=Klima[3].NastTempProstora,lo:=4048,hi:=4049); |  | 24:ErrComPort2:=Bit_0; |  |  |  | 4049:Klima[3].NastTempProstora:=Real_0;
mind_bool[25]:=Klima1_Onemogocena; |  |  |  | Read_Real(rVar:=Klima[3].NastVlaznost,lo:=4050,hi:=4051); |  | 25:Klima1_Onemogocena:=Bit_0; |  |  |  | 4051:Klima[3].NastVlaznost:=Real_0;
mind_bool[26]:=Klima2_Onemogocena; |  |  |  | Read_Real(rVar:=Klima[3].Pritisk,lo:=4052,hi:=4053); |  | 26:Klima2_Onemogocena:=Bit_0; |  |  |  | 4053:Klima[3].Pritisk:=Real_0;
mind_bool[27]:=Klima3_Onemogocena; |  |  |  | Read_Real(rVar:=Klima[3].TemperaturaProstora,lo:=4054,hi:=4055); |  | 27:Klima3_Onemogocena:=Bit_0; |  |  |  | 4055:Klima[3].TemperaturaProstora:=Real_0;
mind_bool[28]:=Klima[1].IzhodniVentilator; |  |  |  | Read_Real(rVar:=Klima[3].VlaznostProstora,lo:=4056,hi:=4057); |  | 28:Klima[1].IzhodniVentilator:=Bit_0; |  |  |  | 4057:Klima[3].VlaznostProstora:=Real_0;
mind_bool[29]:=Klima[1].Kompresor1; |  |  |  | Read_Real(rVar:=ObratUreKlim[1],lo:=4058,hi:=4059); |  | 29:Klima[1].Kompresor1:=Bit_0; |  |  |  | 4059:ObratUreKlim[1]:=Real_0;
mind_bool[30]:=Klima[1].Kompresor2; |  |  |  | Read_Real(rVar:=ObratUreKlim[2],lo:=4060,hi:=4061); |  | 30:Klima[1].Kompresor2:=Bit_0; |  |  |  | 4061:ObratUreKlim[2]:=Real_0;
mind_bool[31]:=Klima[1].Razvlazevanje; |  |  |  | Read_Real(rVar:=ObratUreKlim[3],lo:=4062,hi:=4063); |  | 31:Klima[1].Razvlazevanje:=Bit_0; |  |  |  | 4063:ObratUreKlim[3]:=Real_0;
mind_bool[32]:=Klima[1].VentilGretjeOdpiranje; |  |  |  | Read_Real(rVar:=PMM.ActiveEnergyConsumed_kWh,lo:=4064,hi:=4065); |  | 32:Klima[1].VentilGretjeOdpiranje:=Bit_0; |  |  |  | 4065:PMM.ActiveEnergyConsumed_kWh:=Real_0;
mind_bool[33]:=Klima[1].VentilGretjeZapiranje; |  |  |  | Read_Real(rVar:=PMM.ActivePowerPhaseA_kW,lo:=4066,hi:=4067); |  | 33:Klima[1].VentilGretjeZapiranje:=Bit_0; |  |  |  | 4067:PMM.ActivePowerPhaseA_kW:=Real_0;
mind_bool[34]:=Klima[1].Vlazenje; |  |  |  | Read_Real(rVar:=PMM.ActivePowerPhaseB_kW,lo:=4068,hi:=4069); |  | 34:Klima[1].Vlazenje:=Bit_0; |  |  |  | 4069:PMM.ActivePowerPhaseB_kW:=Real_0;
mind_bool[35]:=Klima[2].IzhodniVentilator; |  |  |  | Read_Real(rVar:=PMM.ActivePowerPhaseC_kW,lo:=4070,hi:=4071); |  | 35:Klima[2].IzhodniVentilator:=Bit_0; |  |  |  | 4071:PMM.ActivePowerPhaseC_kW:=Real_0;
mind_bool[36]:=Klima[2].Kompresor1; |  |  |  | Read_Real(rVar:=PMM.AparentPowerPhaseA,lo:=4072,hi:=4073); |  | 36:Klima[2].Kompresor1:=Bit_0; |  |  |  | 4073:PMM.AparentPowerPhaseA:=Real_0;
mind_bool[37]:=Klima[2].Kompresor2; |  |  |  | Read_Real(rVar:=PMM.AparentPowerPhaseB,lo:=4074,hi:=4075); |  | 37:Klima[2].Kompresor2:=Bit_0; |  |  |  | 4075:PMM.AparentPowerPhaseB:=Real_0;
mind_bool[38]:=Klima[2].Razvlazevanje; |  |  |  | Read_Real(rVar:=PMM.AparentPowerPhaseC,lo:=4076,hi:=4077); |  | 38:Klima[2].Razvlazevanje:=Bit_0; |  |  |  | 4077:PMM.AparentPowerPhaseC:=Real_0;
mind_bool[39]:=Klima[2].VentilGretjeOdpiranje; |  |  |  | Read_Real(rVar:=PMM.AverageCurrent_A,lo:=4078,hi:=4079); |  | 39:Klima[2].VentilGretjeOdpiranje:=Bit_0; |  |  |  | 4079:PMM.AverageCurrent_A:=Real_0;
mind_bool[40]:=Klima[2].VentilGretjeZapiranje; |  |  |  | Read_Real(rVar:=PMM.AveragePhaseToNeutral_V,lo:=4080,hi:=4081); |  | 40:Klima[2].VentilGretjeZapiranje:=Bit_0; |  |  |  | 4081:PMM.AveragePhaseToNeutral_V:=Real_0;
mind_bool[41]:=Klima[2].Vlazenje; |  |  |  | Read_Real(rVar:=PMM.AveragePhaseToPhase_V,lo:=4082,hi:=4083); |  | 41:Klima[2].Vlazenje:=Bit_0; |  |  |  | 4083:PMM.AveragePhaseToPhase_V:=Real_0;
mind_bool[42]:=Klima[3].IzhodniVentilator; |  |  |  | Read_Real(rVar:=PMM.CurrentInPhaseA_A,lo:=4084,hi:=4085); |  | 42:Klima[3].IzhodniVentilator:=Bit_0; |  |  |  | 4085:PMM.CurrentInPhaseA_A:=Real_0;
mind_bool[43]:=Klima[3].Kompresor1; |  |  |  | Read_Real(rVar:=PMM.CurrentInPhaseB_A,lo:=4086,hi:=4087); |  | 43:Klima[3].Kompresor1:=Bit_0; |  |  |  | 4087:PMM.CurrentInPhaseB_A:=Real_0;
mind_bool[44]:=Klima[3].Kompresor2; |  |  |  | Read_Real(rVar:=PMM.CurrentInPhaseC_A,lo:=4088,hi:=4089); |  | 44:Klima[3].Kompresor2:=Bit_0; |  |  |  | 4089:PMM.CurrentInPhaseC_A:=Real_0;
mind_bool[45]:=Klima[3].Razvlazevanje; |  |  |  | Read_Real(rVar:=PMM.Frequency_Hz,lo:=4090,hi:=4091); |  | 45:Klima[3].Razvlazevanje:=Bit_0; |  |  |  | 4091:PMM.Frequency_Hz:=Real_0;
mind_bool[46]:=Klima[3].VentilGretjeOdpiranje; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[10],lo:=4092,hi:=4093); |  | 46:Klima[3].VentilGretjeOdpiranje:=Bit_0; |  |  |  | 4093:PMM.Phase[1].Current[10]:=Real_0;
mind_bool[47]:=Klima[3].VentilGretjeZapiranje; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[11],lo:=4094,hi:=4095); |  | 47:Klima[3].VentilGretjeZapiranje:=Bit_0; |  |  |  | 4095:PMM.Phase[1].Current[11]:=Real_0;
mind_bool[48]:=Klima[3].Vlazenje; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[12],lo:=4096,hi:=4097); |  | 48:Klima[3].Vlazenje:=Bit_0; |  |  |  | 4097:PMM.Phase[1].Current[12]:=Real_0;
mind_bool[49]:=KlimaError[1].AlarmKompresor1; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[13],lo:=4098,hi:=4099); |  | 49:KlimaError[1].AlarmKompresor1:=Bit_0; |  |  |  | 4099:PMM.Phase[1].Current[13]:=Real_0;
mind_bool[50]:=KlimaError[1].AlarmKompresor2; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[14],lo:=4100,hi:=4101); |  | 50:KlimaError[1].AlarmKompresor2:=Bit_0; |  |  |  | 4101:PMM.Phase[1].Current[14]:=Real_0;
mind_bool[51]:=KlimaError[1].FenThermalCutout; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[15],lo:=4102,hi:=4103); |  | 51:KlimaError[1].FenThermalCutout:=Bit_0; |  |  |  | 4103:PMM.Phase[1].Current[15]:=Real_0;
mind_bool[52]:=KlimaError[1].IzlivVode; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[16],lo:=4104,hi:=4105); |  | 52:KlimaError[1].IzlivVode:=Bit_0; |  |  |  | 4105:PMM.Phase[1].Current[16]:=Real_0;
mind_bool[53]:=KlimaError[1].Kompresor1naMejiStevilaObrUr; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[17],lo:=4106,hi:=4107); |  | 53:KlimaError[1].Kompresor1naMejiStevilaObrUr:=Bit_0; |  |  |  | 4107:PMM.Phase[1].Current[17]:=Real_0;
mind_bool[54]:=KlimaError[1].Kompresor2naMejiStevilaObrUr; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[18],lo:=4108,hi:=4109); |  | 54:KlimaError[1].Kompresor2naMejiStevilaObrUr:=Bit_0; |  |  |  | 4109:PMM.Phase[1].Current[18]:=Real_0;
mind_bool[55]:=KlimaError[1].Kond1FenThermalCutout; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[19],lo:=4110,hi:=4111); |  | 55:KlimaError[1].Kond1FenThermalCutout:=Bit_0; |  |  |  | 4111:PMM.Phase[1].Current[19]:=Real_0;
mind_bool[56]:=KlimaError[1].Kond2FenThermalCutout; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[1],lo:=4112,hi:=4113); |  | 56:KlimaError[1].Kond2FenThermalCutout:=Bit_0; |  |  |  | 4113:PMM.Phase[1].Current[1]:=Real_0;
mind_bool[57]:=KlimaError[1].NapakaPriPretokuVode; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[20],lo:=4114,hi:=4115); |  | 57:KlimaError[1].NapakaPriPretokuVode:=Bit_0; |  |  |  | 4115:PMM.Phase[1].Current[20]:=Real_0;
mind_bool[58]:=KlimaError[1].NapakaPriPretokuZraka; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[21],lo:=4116,hi:=4117); |  | 58:KlimaError[1].NapakaPriPretokuZraka:=Bit_0; |  |  |  | 4117:PMM.Phase[1].Current[21]:=Real_0;
mind_bool[59]:=KlimaError[1].NapakaSenzorPritiska; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[22],lo:=4118,hi:=4119); |  | 59:KlimaError[1].NapakaSenzorPritiska:=Bit_0; |  |  |  | 4119:PMM.Phase[1].Current[22]:=Real_0;
mind_bool[60]:=KlimaError[1].NapakaSenzorVlaznosti; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[23],lo:=4120,hi:=4121); |  | 60:KlimaError[1].NapakaSenzorVlaznosti:=Bit_0; |  |  |  | 4121:PMM.Phase[1].Current[23]:=Real_0;
mind_bool[61]:=KlimaError[1].NapakaTSTemperaturaProstora; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[24],lo:=4122,hi:=4123); |  | 61:KlimaError[1].NapakaTSTemperaturaProstora:=Bit_0; |  |  |  | 4123:PMM.Phase[1].Current[24]:=Real_0;
mind_bool[62]:=KlimaError[1].NiTokaVVlazilcu; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[25],lo:=4124,hi:=4125); |  | 62:KlimaError[1].NiTokaVVlazilcu:=Bit_0; |  |  |  | 4125:PMM.Phase[1].Current[25]:=Real_0;
mind_bool[63]:=KlimaError[1].NiVodeVVlazilcu; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[26],lo:=4126,hi:=4127); |  | 63:KlimaError[1].NiVodeVVlazilcu:=Bit_0; |  |  |  | 4127:PMM.Phase[1].Current[26]:=Real_0;
mind_bool[64]:=KlimaError[1].NizekPritiskKompresor1; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[27],lo:=4128,hi:=4129); |  | 64:KlimaError[1].NizekPritiskKompresor1:=Bit_0; |  |  |  | 4129:PMM.Phase[1].Current[27]:=Real_0;
mind_bool[65]:=KlimaError[1].NizekPritiskKompresor2; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[28],lo:=4130,hi:=4131); |  | 65:KlimaError[1].NizekPritiskKompresor2:=Bit_0; |  |  |  | 4131:PMM.Phase[1].Current[28]:=Real_0;
mind_bool[66]:=KlimaError[1].NizkaTempVProstoru; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[29],lo:=4132,hi:=4133); |  | 66:KlimaError[1].NizkaTempVProstoru:=Bit_0; |  |  |  | 4133:PMM.Phase[1].Current[29]:=Real_0;
mind_bool[67]:=KlimaError[1].NizkaVlaznost; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[2],lo:=4134,hi:=4135); |  | 67:KlimaError[1].NizkaVlaznost:=Bit_0; |  |  |  | 4135:PMM.Phase[1].Current[2]:=Real_0;
mind_bool[68]:=KlimaError[1].PozarniAlarm; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[30],lo:=4136,hi:=4137); |  | 68:KlimaError[1].PozarniAlarm:=Bit_0; |  |  |  | 4137:PMM.Phase[1].Current[30]:=Real_0;
mind_bool[69]:=KlimaError[1].TermZascInVisokPritiskKompr1; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[31],lo:=4138,hi:=4139); |  | 69:KlimaError[1].TermZascInVisokPritiskKompr1:=Bit_0; |  |  |  | 4139:PMM.Phase[1].Current[31]:=Real_0;
mind_bool[70]:=KlimaError[1].TermZascInVisokPritiskKompr2; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[32],lo:=4140,hi:=4141); |  | 70:KlimaError[1].TermZascInVisokPritiskKompr2:=Bit_0; |  |  |  | 4141:PMM.Phase[1].Current[32]:=Real_0;
mind_bool[71]:=KlimaError[1].ThermalCutoutHeater1; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[33],lo:=4142,hi:=4143); |  | 71:KlimaError[1].ThermalCutoutHeater1:=Bit_0; |  |  |  | 4143:PMM.Phase[1].Current[33]:=Real_0;
mind_bool[72]:=KlimaError[1].ThermalCutoutHeater2; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[34],lo:=4144,hi:=4145); |  | 72:KlimaError[1].ThermalCutoutHeater2:=Bit_0; |  |  |  | 4145:PMM.Phase[1].Current[34]:=Real_0;
mind_bool[73]:=KlimaError[1].VentilatorNaMejiStevilaObrUr; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[35],lo:=4146,hi:=4147); |  | 73:KlimaError[1].VentilatorNaMejiStevilaObrUr:=Bit_0; |  |  |  | 4147:PMM.Phase[1].Current[35]:=Real_0;
mind_bool[74]:=KlimaError[1].VisokaTempVProstoru; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[36],lo:=4148,hi:=4149); |  | 74:KlimaError[1].VisokaTempVProstoru:=Bit_0; |  |  |  | 4149:PMM.Phase[1].Current[36]:=Real_0;
mind_bool[75]:=KlimaError[1].VisokaVlaznost; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[37],lo:=4150,hi:=4151); |  | 75:KlimaError[1].VisokaVlaznost:=Bit_0; |  |  |  | 4151:PMM.Phase[1].Current[37]:=Real_0;
mind_bool[76]:=KlimaError[1].VisokPritiskVKrogu1; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[38],lo:=4152,hi:=4153); |  | 76:KlimaError[1].VisokPritiskVKrogu1:=Bit_0; |  |  |  | 4153:PMM.Phase[1].Current[38]:=Real_0;
mind_bool[77]:=KlimaError[1].VisokPritiskVKrogu2; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[39],lo:=4154,hi:=4155); |  | 77:KlimaError[1].VisokPritiskVKrogu2:=Bit_0; |  |  |  | 4155:PMM.Phase[1].Current[39]:=Real_0;
mind_bool[78]:=KlimaError[1].VisokTokVVlazilcu; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[3],lo:=4156,hi:=4157); |  | 78:KlimaError[1].VisokTokVVlazilcu:=Bit_0; |  |  |  | 4157:PMM.Phase[1].Current[3]:=Real_0;
mind_bool[79]:=KlimaError[1].VlazilecnaMejiStevilaObrUr; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[40],lo:=4158,hi:=4159); |  | 79:KlimaError[1].VlazilecnaMejiStevilaObrUr:=Bit_0; |  |  |  | 4159:PMM.Phase[1].Current[40]:=Real_0;
mind_bool[80]:=KlimaError[1].ZamasenFilter; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[41],lo:=4160,hi:=4161); |  | 80:KlimaError[1].ZamasenFilter:=Bit_0; |  |  |  | 4161:PMM.Phase[1].Current[41]:=Real_0;
mind_bool[81]:=KlimaError[1].ZunanjiAlarm; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[42],lo:=4162,hi:=4163); |  | 81:KlimaError[1].ZunanjiAlarm:=Bit_0; |  |  |  | 4163:PMM.Phase[1].Current[42]:=Real_0;
mind_bool[82]:=KlimaError[2].AlarmKompresor1; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[4],lo:=4164,hi:=4165); |  | 82:KlimaError[2].AlarmKompresor1:=Bit_0; |  |  |  | 4165:PMM.Phase[1].Current[4]:=Real_0;
mind_bool[83]:=KlimaError[2].AlarmKompresor2; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[5],lo:=4166,hi:=4167); |  | 83:KlimaError[2].AlarmKompresor2:=Bit_0; |  |  |  | 4167:PMM.Phase[1].Current[5]:=Real_0;
mind_bool[84]:=KlimaError[2].FenThermalCutout; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[6],lo:=4168,hi:=4169); |  | 84:KlimaError[2].FenThermalCutout:=Bit_0; |  |  |  | 4169:PMM.Phase[1].Current[6]:=Real_0;
mind_bool[85]:=KlimaError[2].IzlivVode; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[7],lo:=4170,hi:=4171); |  | 85:KlimaError[2].IzlivVode:=Bit_0; |  |  |  | 4171:PMM.Phase[1].Current[7]:=Real_0;
mind_bool[86]:=KlimaError[2].Kompresor1naMejiStevilaObrUr; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[8],lo:=4172,hi:=4173); |  | 86:KlimaError[2].Kompresor1naMejiStevilaObrUr:=Bit_0; |  |  |  | 4173:PMM.Phase[1].Current[8]:=Real_0;
mind_bool[87]:=KlimaError[2].Kompresor2naMejiStevilaObrUr; |  |  |  | Read_Real(rVar:=PMM.Phase[1].Current[9],lo:=4174,hi:=4175); |  | 87:KlimaError[2].Kompresor2naMejiStevilaObrUr:=Bit_0; |  |  |  | 4175:PMM.Phase[1].Current[9]:=Real_0;
mind_bool[88]:=KlimaError[2].Kond1FenThermalCutout; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[10],lo:=4176,hi:=4177); |  | 88:KlimaError[2].Kond1FenThermalCutout:=Bit_0; |  |  |  | 4177:PMM.Phase[2].Current[10]:=Real_0;
mind_bool[89]:=KlimaError[2].Kond2FenThermalCutout; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[11],lo:=4178,hi:=4179); |  | 89:KlimaError[2].Kond2FenThermalCutout:=Bit_0; |  |  |  | 4179:PMM.Phase[2].Current[11]:=Real_0;
mind_bool[90]:=KlimaError[2].NapakaPriPretokuVode; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[12],lo:=4180,hi:=4181); |  | 90:KlimaError[2].NapakaPriPretokuVode:=Bit_0; |  |  |  | 4181:PMM.Phase[2].Current[12]:=Real_0;
mind_bool[91]:=KlimaError[2].NapakaPriPretokuZraka; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[13],lo:=4182,hi:=4183); |  | 91:KlimaError[2].NapakaPriPretokuZraka:=Bit_0; |  |  |  | 4183:PMM.Phase[2].Current[13]:=Real_0;
mind_bool[92]:=KlimaError[2].NapakaSenzorPritiska; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[14],lo:=4184,hi:=4185); |  | 92:KlimaError[2].NapakaSenzorPritiska:=Bit_0; |  |  |  | 4185:PMM.Phase[2].Current[14]:=Real_0;
mind_bool[93]:=KlimaError[2].NapakaSenzorVlaznosti; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[15],lo:=4186,hi:=4187); |  | 93:KlimaError[2].NapakaSenzorVlaznosti:=Bit_0; |  |  |  | 4187:PMM.Phase[2].Current[15]:=Real_0;
mind_bool[94]:=KlimaError[2].NapakaTSTemperaturaProstora; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[16],lo:=4188,hi:=4189); |  | 94:KlimaError[2].NapakaTSTemperaturaProstora:=Bit_0; |  |  |  | 4189:PMM.Phase[2].Current[16]:=Real_0;
mind_bool[95]:=KlimaError[2].NiTokaVVlazilcu; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[17],lo:=4190,hi:=4191); |  | 95:KlimaError[2].NiTokaVVlazilcu:=Bit_0; |  |  |  | 4191:PMM.Phase[2].Current[17]:=Real_0;
mind_bool[96]:=KlimaError[2].NiVodeVVlazilcu; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[18],lo:=4192,hi:=4193); |  | 96:KlimaError[2].NiVodeVVlazilcu:=Bit_0; |  |  |  | 4193:PMM.Phase[2].Current[18]:=Real_0;
mind_bool[97]:=KlimaError[2].NizekPritiskKompresor1; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[19],lo:=4194,hi:=4195); |  | 97:KlimaError[2].NizekPritiskKompresor1:=Bit_0; |  |  |  | 4195:PMM.Phase[2].Current[19]:=Real_0;
mind_bool[98]:=KlimaError[2].NizekPritiskKompresor2; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[1],lo:=4196,hi:=4197); |  | 98:KlimaError[2].NizekPritiskKompresor2:=Bit_0; |  |  |  | 4197:PMM.Phase[2].Current[1]:=Real_0;
mind_bool[99]:=KlimaError[2].NizkaTempVProstoru; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[20],lo:=4198,hi:=4199); |  | 99:KlimaError[2].NizkaTempVProstoru:=Bit_0; |  |  |  | 4199:PMM.Phase[2].Current[20]:=Real_0;
mind_bool[100]:=KlimaError[2].NizkaVlaznost; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[21],lo:=4200,hi:=4201); |  | 100:KlimaError[2].NizkaVlaznost:=Bit_0; |  |  |  | 4201:PMM.Phase[2].Current[21]:=Real_0;
mind_bool[101]:=KlimaError[2].PozarniAlarm; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[22],lo:=4202,hi:=4203); |  | 101:KlimaError[2].PozarniAlarm:=Bit_0; |  |  |  | 4203:PMM.Phase[2].Current[22]:=Real_0;
mind_bool[102]:=KlimaError[2].TermZascInVisokPritiskKompr1; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[23],lo:=4204,hi:=4205); |  | 102:KlimaError[2].TermZascInVisokPritiskKompr1:=Bit_0; |  |  |  | 4205:PMM.Phase[2].Current[23]:=Real_0;
mind_bool[103]:=KlimaError[2].TermZascInVisokPritiskKompr2; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[24],lo:=4206,hi:=4207); |  | 103:KlimaError[2].TermZascInVisokPritiskKompr2:=Bit_0; |  |  |  | 4207:PMM.Phase[2].Current[24]:=Real_0;
mind_bool[104]:=KlimaError[2].ThermalCutoutHeater1; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[25],lo:=4208,hi:=4209); |  | 104:KlimaError[2].ThermalCutoutHeater1:=Bit_0; |  |  |  | 4209:PMM.Phase[2].Current[25]:=Real_0;
mind_bool[105]:=KlimaError[2].ThermalCutoutHeater2; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[26],lo:=4210,hi:=4211); |  | 105:KlimaError[2].ThermalCutoutHeater2:=Bit_0; |  |  |  | 4211:PMM.Phase[2].Current[26]:=Real_0;
mind_bool[106]:=KlimaError[2].VentilatorNaMejiStevilaObrUr; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[27],lo:=4212,hi:=4213); |  | 106:KlimaError[2].VentilatorNaMejiStevilaObrUr:=Bit_0; |  |  |  | 4213:PMM.Phase[2].Current[27]:=Real_0;
mind_bool[107]:=KlimaError[2].VisokaTempVProstoru; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[28],lo:=4214,hi:=4215); |  | 107:KlimaError[2].VisokaTempVProstoru:=Bit_0; |  |  |  | 4215:PMM.Phase[2].Current[28]:=Real_0;
mind_bool[108]:=KlimaError[2].VisokaVlaznost; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[29],lo:=4216,hi:=4217); |  | 108:KlimaError[2].VisokaVlaznost:=Bit_0; |  |  |  | 4217:PMM.Phase[2].Current[29]:=Real_0;
mind_bool[109]:=KlimaError[2].VisokPritiskVKrogu1; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[2],lo:=4218,hi:=4219); |  | 109:KlimaError[2].VisokPritiskVKrogu1:=Bit_0; |  |  |  | 4219:PMM.Phase[2].Current[2]:=Real_0;
mind_bool[110]:=KlimaError[2].VisokPritiskVKrogu2; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[30],lo:=4220,hi:=4221); |  | 110:KlimaError[2].VisokPritiskVKrogu2:=Bit_0; |  |  |  | 4221:PMM.Phase[2].Current[30]:=Real_0;
mind_bool[111]:=KlimaError[2].VisokTokVVlazilcu; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[31],lo:=4222,hi:=4223); |  | 111:KlimaError[2].VisokTokVVlazilcu:=Bit_0; |  |  |  | 4223:PMM.Phase[2].Current[31]:=Real_0;
mind_bool[112]:=KlimaError[2].VlazilecnaMejiStevilaObrUr; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[32],lo:=4224,hi:=4225); |  | 112:KlimaError[2].VlazilecnaMejiStevilaObrUr:=Bit_0; |  |  |  | 4225:PMM.Phase[2].Current[32]:=Real_0;
mind_bool[113]:=KlimaError[2].ZamasenFilter; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[33],lo:=4226,hi:=4227); |  | 113:KlimaError[2].ZamasenFilter:=Bit_0; |  |  |  | 4227:PMM.Phase[2].Current[33]:=Real_0;
mind_bool[114]:=KlimaError[2].ZunanjiAlarm; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[34],lo:=4228,hi:=4229); |  | 114:KlimaError[2].ZunanjiAlarm:=Bit_0; |  |  |  | 4229:PMM.Phase[2].Current[34]:=Real_0;
mind_bool[115]:=KlimaError[3].AlarmKompresor1; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[35],lo:=4230,hi:=4231); |  | 115:KlimaError[3].AlarmKompresor1:=Bit_0; |  |  |  | 4231:PMM.Phase[2].Current[35]:=Real_0;
mind_bool[116]:=KlimaError[3].AlarmKompresor2; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[36],lo:=4232,hi:=4233); |  | 116:KlimaError[3].AlarmKompresor2:=Bit_0; |  |  |  | 4233:PMM.Phase[2].Current[36]:=Real_0;
mind_bool[117]:=KlimaError[3].FenThermalCutout; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[37],lo:=4234,hi:=4235); |  | 117:KlimaError[3].FenThermalCutout:=Bit_0; |  |  |  | 4235:PMM.Phase[2].Current[37]:=Real_0;
mind_bool[118]:=KlimaError[3].IzlivVode; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[38],lo:=4236,hi:=4237); |  | 118:KlimaError[3].IzlivVode:=Bit_0; |  |  |  | 4237:PMM.Phase[2].Current[38]:=Real_0;
mind_bool[119]:=KlimaError[3].Kompresor1naMejiStevilaObrUr; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[39],lo:=4238,hi:=4239); |  | 119:KlimaError[3].Kompresor1naMejiStevilaObrUr:=Bit_0; |  |  |  | 4239:PMM.Phase[2].Current[39]:=Real_0;
mind_bool[120]:=KlimaError[3].Kompresor2naMejiStevilaObrUr; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[3],lo:=4240,hi:=4241); |  | 120:KlimaError[3].Kompresor2naMejiStevilaObrUr:=Bit_0; |  |  |  | 4241:PMM.Phase[2].Current[3]:=Real_0;
mind_bool[121]:=KlimaError[3].Kond1FenThermalCutout; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[40],lo:=4242,hi:=4243); |  | 121:KlimaError[3].Kond1FenThermalCutout:=Bit_0; |  |  |  | 4243:PMM.Phase[2].Current[40]:=Real_0;
mind_bool[122]:=KlimaError[3].Kond2FenThermalCutout; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[41],lo:=4244,hi:=4245); |  | 122:KlimaError[3].Kond2FenThermalCutout:=Bit_0; |  |  |  | 4245:PMM.Phase[2].Current[41]:=Real_0;
mind_bool[123]:=KlimaError[3].NapakaPriPretokuVode; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[42],lo:=4246,hi:=4247); |  | 123:KlimaError[3].NapakaPriPretokuVode:=Bit_0; |  |  |  | 4247:PMM.Phase[2].Current[42]:=Real_0;
mind_bool[124]:=KlimaError[3].NapakaPriPretokuZraka; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[4],lo:=4248,hi:=4249); |  | 124:KlimaError[3].NapakaPriPretokuZraka:=Bit_0; |  |  |  | 4249:PMM.Phase[2].Current[4]:=Real_0;
mind_bool[125]:=KlimaError[3].NapakaSenzorPritiska; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[5],lo:=4250,hi:=4251); |  | 125:KlimaError[3].NapakaSenzorPritiska:=Bit_0; |  |  |  | 4251:PMM.Phase[2].Current[5]:=Real_0;
mind_bool[126]:=KlimaError[3].NapakaSenzorVlaznosti; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[6],lo:=4252,hi:=4253); |  | 126:KlimaError[3].NapakaSenzorVlaznosti:=Bit_0; |  |  |  | 4253:PMM.Phase[2].Current[6]:=Real_0;
mind_bool[127]:=KlimaError[3].NapakaTSTemperaturaProstora; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[7],lo:=4254,hi:=4255); |  | 127:KlimaError[3].NapakaTSTemperaturaProstora:=Bit_0; |  |  |  | 4255:PMM.Phase[2].Current[7]:=Real_0;
mind_bool[128]:=KlimaError[3].NiTokaVVlazilcu; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[8],lo:=4256,hi:=4257); |  | 128:KlimaError[3].NiTokaVVlazilcu:=Bit_0; |  |  |  | 4257:PMM.Phase[2].Current[8]:=Real_0;
mind_bool[129]:=KlimaError[3].NiVodeVVlazilcu; |  |  |  | Read_Real(rVar:=PMM.Phase[2].Current[9],lo:=4258,hi:=4259); |  | 129:KlimaError[3].NiVodeVVlazilcu:=Bit_0; |  |  |  | 4259:PMM.Phase[2].Current[9]:=Real_0;
mind_bool[130]:=KlimaError[3].NizekPritiskKompresor1; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[10],lo:=4260,hi:=4261); |  | 130:KlimaError[3].NizekPritiskKompresor1:=Bit_0; |  |  |  | 4261:PMM.Phase[3].Current[10]:=Real_0;
mind_bool[131]:=KlimaError[3].NizekPritiskKompresor2; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[11],lo:=4262,hi:=4263); |  | 131:KlimaError[3].NizekPritiskKompresor2:=Bit_0; |  |  |  | 4263:PMM.Phase[3].Current[11]:=Real_0;
mind_bool[132]:=KlimaError[3].NizkaTempVProstoru; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[12],lo:=4264,hi:=4265); |  | 132:KlimaError[3].NizkaTempVProstoru:=Bit_0; |  |  |  | 4265:PMM.Phase[3].Current[12]:=Real_0;
mind_bool[133]:=KlimaError[3].NizkaVlaznost; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[13],lo:=4266,hi:=4267); |  | 133:KlimaError[3].NizkaVlaznost:=Bit_0; |  |  |  | 4267:PMM.Phase[3].Current[13]:=Real_0;
mind_bool[134]:=KlimaError[3].PozarniAlarm; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[14],lo:=4268,hi:=4269); |  | 134:KlimaError[3].PozarniAlarm:=Bit_0; |  |  |  | 4269:PMM.Phase[3].Current[14]:=Real_0;
mind_bool[135]:=KlimaError[3].TermZascInVisokPritiskKompr1; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[15],lo:=4270,hi:=4271); |  | 135:KlimaError[3].TermZascInVisokPritiskKompr1:=Bit_0; |  |  |  | 4271:PMM.Phase[3].Current[15]:=Real_0;
mind_bool[136]:=KlimaError[3].TermZascInVisokPritiskKompr2; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[16],lo:=4272,hi:=4273); |  | 136:KlimaError[3].TermZascInVisokPritiskKompr2:=Bit_0; |  |  |  | 4273:PMM.Phase[3].Current[16]:=Real_0;
mind_bool[137]:=KlimaError[3].ThermalCutoutHeater1; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[17],lo:=4274,hi:=4275); |  | 137:KlimaError[3].ThermalCutoutHeater1:=Bit_0; |  |  |  | 4275:PMM.Phase[3].Current[17]:=Real_0;
mind_bool[138]:=KlimaError[3].ThermalCutoutHeater2; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[18],lo:=4276,hi:=4277); |  | 138:KlimaError[3].ThermalCutoutHeater2:=Bit_0; |  |  |  | 4277:PMM.Phase[3].Current[18]:=Real_0;
mind_bool[139]:=KlimaError[3].VentilatorNaMejiStevilaObrUr; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[19],lo:=4278,hi:=4279); |  | 139:KlimaError[3].VentilatorNaMejiStevilaObrUr:=Bit_0; |  |  |  | 4279:PMM.Phase[3].Current[19]:=Real_0;
mind_bool[140]:=KlimaError[3].VisokaTempVProstoru; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[1],lo:=4280,hi:=4281); |  | 140:KlimaError[3].VisokaTempVProstoru:=Bit_0; |  |  |  | 4281:PMM.Phase[3].Current[1]:=Real_0;
mind_bool[141]:=KlimaError[3].VisokaVlaznost; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[20],lo:=4282,hi:=4283); |  | 141:KlimaError[3].VisokaVlaznost:=Bit_0; |  |  |  | 4283:PMM.Phase[3].Current[20]:=Real_0;
mind_bool[142]:=KlimaError[3].VisokPritiskVKrogu1; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[21],lo:=4284,hi:=4285); |  | 142:KlimaError[3].VisokPritiskVKrogu1:=Bit_0; |  |  |  | 4285:PMM.Phase[3].Current[21]:=Real_0;
mind_bool[143]:=KlimaError[3].VisokPritiskVKrogu2; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[22],lo:=4286,hi:=4287); |  | 143:KlimaError[3].VisokPritiskVKrogu2:=Bit_0; |  |  |  | 4287:PMM.Phase[3].Current[22]:=Real_0;
mind_bool[144]:=KlimaError[3].VisokTokVVlazilcu; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[23],lo:=4288,hi:=4289); |  | 144:KlimaError[3].VisokTokVVlazilcu:=Bit_0; |  |  |  | 4289:PMM.Phase[3].Current[23]:=Real_0;
mind_bool[145]:=KlimaError[3].VlazilecnaMejiStevilaObrUr; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[24],lo:=4290,hi:=4291); |  | 145:KlimaError[3].VlazilecnaMejiStevilaObrUr:=Bit_0; |  |  |  | 4291:PMM.Phase[3].Current[24]:=Real_0;
mind_bool[146]:=KlimaError[3].ZamasenFilter; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[25],lo:=4292,hi:=4293); |  | 146:KlimaError[3].ZamasenFilter:=Bit_0; |  |  |  | 4293:PMM.Phase[3].Current[25]:=Real_0;
mind_bool[147]:=KlimaError[3].ZunanjiAlarm; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[26],lo:=4294,hi:=4295); |  | 147:KlimaError[3].ZunanjiAlarm:=Bit_0; |  |  |  | 4295:PMM.Phase[3].Current[26]:=Real_0;
mind_bool[148]:=NacDelovanjaKlime1_Avtomatsko; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[27],lo:=4296,hi:=4297); |  | 148:NacDelovanjaKlime1_Avtomatsko:=Bit_0; |  |  |  | 4297:PMM.Phase[3].Current[27]:=Real_0;
mind_bool[149]:=NacDelovanjaKlime2_3Avtomatsko; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[28],lo:=4298,hi:=4299); |  | 149:NacDelovanjaKlime2_3Avtomatsko:=Bit_0; |  |  |  | 4299:PMM.Phase[3].Current[28]:=Real_0;
mind_bool[150]:=NapakaSenzorTemp1; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[29],lo:=4300,hi:=4301); |  | 150:NapakaSenzorTemp1:=Bit_0; |  |  |  | 4301:PMM.Phase[3].Current[29]:=Real_0;
mind_bool[151]:=NapakaSenzorTemp2; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[2],lo:=4302,hi:=4303); |  | 151:NapakaSenzorTemp2:=Bit_0; |  |  |  | 4303:PMM.Phase[3].Current[2]:=Real_0;
mind_bool[152]:=NapakaSenzorTemp3; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[30],lo:=4304,hi:=4305); |  | 152:NapakaSenzorTemp3:=Bit_0; |  |  |  | 4305:PMM.Phase[3].Current[30]:=Real_0;
mind_bool[153]:=NapakaSenzorTempKontrSoba; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[31],lo:=4306,hi:=4307); |  | 153:NapakaSenzorTempKontrSoba:=Bit_0; |  |  |  | 4307:PMM.Phase[3].Current[31]:=Real_0;
mind_bool[154]:=NapakaSenzorTempLinkProstor; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[32],lo:=4308,hi:=4309); |  | 154:NapakaSenzorTempLinkProstor:=Bit_0; |  |  |  | 4309:PMM.Phase[3].Current[32]:=Real_0;
mind_bool[155]:=NapakaSenzorVlaga1; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[33],lo:=4310,hi:=4311); |  | 155:NapakaSenzorVlaga1:=Bit_0; |  |  |  | 4311:PMM.Phase[3].Current[33]:=Real_0;
mind_bool[156]:=NapakaSenzorVlaga2; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[34],lo:=4312,hi:=4313); |  | 156:NapakaSenzorVlaga2:=Bit_0; |  |  |  | 4313:PMM.Phase[3].Current[34]:=Real_0;
mind_bool[157]:=NapakaSenzorVlaga3; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[35],lo:=4314,hi:=4315); |  | 157:NapakaSenzorVlaga3:=Bit_0; |  |  |  | 4315:PMM.Phase[3].Current[35]:=Real_0;
mind_bool[158]:=NapakaSenzorVlagaKontrSoba; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[36],lo:=4316,hi:=4317); |  | 158:NapakaSenzorVlagaKontrSoba:=Bit_0; |  |  |  | 4317:PMM.Phase[3].Current[36]:=Real_0;
mind_bool[159]:=NapakaSenzorVlagaLinkProstor; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[37],lo:=4318,hi:=4319); |  | 159:NapakaSenzorVlagaLinkProstor:=Bit_0; |  |  |  | 4319:PMM.Phase[3].Current[37]:=Real_0;
mind_bool[160]:=NastaviCasNaKrmilniku; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[38],lo:=4320,hi:=4321); |  | 160:NastaviCasNaKrmilniku:=Bit_0; |  |  |  | 4321:PMM.Phase[3].Current[38]:=Real_0;
mind_bool[161]:=NastavitevUreKrUspesna; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[39],lo:=4322,hi:=4323); |  | 161:NastavitevUreKrUspesna:=Bit_0; |  |  |  | 4323:PMM.Phase[3].Current[39]:=Real_0;
mind_bool[162]:=OpozoriloBaterijaPLC; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[3],lo:=4324,hi:=4325); |  | 162:OpozoriloBaterijaPLC:=Bit_0; |  |  |  | 4325:PMM.Phase[3].Current[3]:=Real_0;
mind_bool[163]:=PMM1OverCurrentBetw[1]; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[40],lo:=4326,hi:=4327); |  | 163:PMM1OverCurrentBetw[1]:=Bit_0; |  |  |  | 4327:PMM.Phase[3].Current[40]:=Real_0;
mind_bool[164]:=PMM1OverCurrentBetw[2]; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[41],lo:=4328,hi:=4329); |  | 164:PMM1OverCurrentBetw[2]:=Bit_0; |  |  |  | 4329:PMM.Phase[3].Current[41]:=Real_0;
mind_bool[165]:=PMM1OverCurrentBetw[3]; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[42],lo:=4330,hi:=4331); |  | 165:PMM1OverCurrentBetw[3]:=Bit_0; |  |  |  | 4331:PMM.Phase[3].Current[42]:=Real_0;
mind_bool[166]:=PMM1OverCurrentOver[1]; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[4],lo:=4332,hi:=4333); |  | 166:PMM1OverCurrentOver[1]:=Bit_0; |  |  |  | 4333:PMM.Phase[3].Current[4]:=Real_0;
mind_bool[167]:=PMM1OverCurrentOver[2]; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[5],lo:=4334,hi:=4335); |  | 167:PMM1OverCurrentOver[2]:=Bit_0; |  |  |  | 4335:PMM.Phase[3].Current[5]:=Real_0;
mind_bool[168]:=PMM1OverCurrentOver[3]; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[6],lo:=4336,hi:=4337); |  | 168:PMM1OverCurrentOver[3]:=Bit_0; |  |  |  | 4337:PMM.Phase[3].Current[6]:=Real_0;
mind_bool[169]:=PMM1OverVoltage; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[7],lo:=4338,hi:=4339); |  | 169:PMM1OverVoltage:=Bit_0; |  |  |  | 4339:PMM.Phase[3].Current[7]:=Real_0;
mind_bool[170]:=RocniVklopKlima1; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[8],lo:=4340,hi:=4341); |  | 170:RocniVklopKlima1:=Bit_0; |  |  |  | 4341:PMM.Phase[3].Current[8]:=Real_0;
mind_bool[171]:=RocniVklopKlima2; |  |  |  | Read_Real(rVar:=PMM.Phase[3].Current[9],lo:=4342,hi:=4343); |  | 171:RocniVklopKlima2:=Bit_0; |  |  |  | 4343:PMM.Phase[3].Current[9]:=Real_0;
mind_bool[172]:=RocniVklopKlima3; |  |  |  | Read_Real(rVar:=PMM.PowerFactorSys,lo:=4344,hi:=4345); |  | 172:RocniVklopKlima3:=Bit_0; |  |  |  | 4345:PMM.PowerFactorSys:=Real_0;
mind_bool[173]:=SinhronizacijaPanelOK; |  |  |  | Read_Real(rVar:=PMM.ReactiveEnergyConsumed_kVARh,lo:=4346,hi:=4347); |  | 173:SinhronizacijaPanelOK:=Bit_0; |  |  |  | 4347:PMM.ReactiveEnergyConsumed_kVARh:=Real_0;
mind_bool[174]:=SinhronizirajCas_Panel; |  |  |  | Read_Real(rVar:=PMM.ReactivePowerPhaseA,lo:=4348,hi:=4349); |  | 174:SinhronizirajCas_Panel:=Bit_0; |  |  |  | 4349:PMM.ReactivePowerPhaseA:=Real_0;
mind_bool[175]:=SkupneNapakeNaprav_Klima1; |  |  |  | Read_Real(rVar:=PMM.ReactivePowerPhaseB,lo:=4350,hi:=4351); |  | 175:SkupneNapakeNaprav_Klima1:=Bit_0; |  |  |  | 4351:PMM.ReactivePowerPhaseB:=Real_0;
mind_bool[176]:=SkupneNapakeNaprav_Klima2; |  |  |  | Read_Real(rVar:=PMM.ReactivePowerPhaseC,lo:=4352,hi:=4353); |  | 176:SkupneNapakeNaprav_Klima2:=Bit_0; |  |  |  | 4353:PMM.ReactivePowerPhaseC:=Real_0;
mind_bool[177]:=SkupneNapakeNaprav_Klima3; |  |  |  | Read_Real(rVar:=PMM.TotalActivePower_kW,lo:=4354,hi:=4355); |  | 177:SkupneNapakeNaprav_Klima3:=Bit_0; |  |  |  | 4355:PMM.TotalActivePower_kW:=Real_0;
mind_bool[178]:=SkupneNapakeNaprav_Komunikacija; |  |  |  | Read_Real(rVar:=PMM.TotalAparentPower_kVA,lo:=4356,hi:=4357); |  | 178:SkupneNapakeNaprav_Komunikacija:=Bit_0; |  |  |  | 4357:PMM.TotalAparentPower_kVA:=Real_0;
mind_bool[179]:=SkupneNapakeNaprav_PMMVirA; |  |  |  | Read_Real(rVar:=PMM.TotalPowerFactor,lo:=4358,hi:=4359); |  | 179:SkupneNapakeNaprav_PMMVirA:=Bit_0; |  |  |  | 4359:PMM.TotalPowerFactor:=Real_0;
mind_bool[180]:=SkupneNapakeNaprav_PMMVirB; |  |  |  | Read_Real(rVar:=PMM.TotalReactivePower_kVAR,lo:=4360,hi:=4361); |  | 180:SkupneNapakeNaprav_PMMVirB:=Bit_0; |  |  |  | 4361:PMM.TotalReactivePower_kVAR:=Real_0;
mind_bool[181]:=SkupneNapakeNaprav_PMMVirBVirA; |  |  |  | Read_Real(rVar:=PMM.VirA_fsys,lo:=4362,hi:=4363); |  | 181:SkupneNapakeNaprav_PMMVirBVirA:=Bit_0; |  |  |  | 4363:PMM.VirA_fsys:=Real_0;
mind_bool[182]:=SkupneNapakeNaprav_TempVlaga; |  |  |  | Read_Real(rVar:=PMM.VirA_Isys,lo:=4364,hi:=4365); |  | 182:SkupneNapakeNaprav_TempVlaga:=Bit_0; |  |  |  | 4365:PMM.VirA_Isys:=Real_0;
mind_bool[183]:=StanjeKlimat1_Delovanje; |  |  |  | Read_Real(rVar:=PMM.VirA_PFsys,lo:=4366,hi:=4367); |  | 183:StanjeKlimat1_Delovanje:=Bit_0; |  |  |  | 4367:PMM.VirA_PFsys:=Real_0;
mind_bool[184]:=StanjeKlimat2_Delovanje; |  |  |  | Read_Real(rVar:=PMM.VirA_Psys,lo:=4368,hi:=4369); |  | 184:StanjeKlimat2_Delovanje:=Bit_0; |  |  |  | 4369:PMM.VirA_Psys:=Real_0;
mind_bool[185]:=StanjeKlimat3_Delovanje; |  |  |  | Read_Real(rVar:=PMM.VirA_Qsys,lo:=4370,hi:=4371); |  | 185:StanjeKlimat3_Delovanje:=Bit_0; |  |  |  | 4371:PMM.VirA_Qsys:=Real_0;
mind_bool[186]:=StanjeSP1_Delovanje; |  |  |  | Read_Real(rVar:=PMM.VirA_Ssys,lo:=4372,hi:=4373); |  | 186:StanjeSP1_Delovanje:=Bit_0; |  |  |  | 4373:PMM.VirA_Ssys:=Real_0;
mind_bool[187]:=StanjeSP2_Delovanje; |  |  |  | Read_Real(rVar:=PMM.VirA_Usys,lo:=4374,hi:=4375); |  | 187:StanjeSP2_Delovanje:=Bit_0; |  |  |  | 4375:PMM.VirA_Usys:=Real_0;
mind_bool[188]:=StanjeSP3_Delovanje; |  |  |  | Read_Real(rVar:=PMM.VirB_fsys,lo:=4376,hi:=4377); |  | 188:StanjeSP3_Delovanje:=Bit_0; |  |  |  | 4377:PMM.VirB_fsys:=Real_0;
mind_bool[189]:=StanjeSP4_Delovanje; |  |  |  | Read_Real(rVar:=PMM.VirB_Isys,lo:=4378,hi:=4379); |  | 189:StanjeSP4_Delovanje:=Bit_0; |  |  |  | 4379:PMM.VirB_Isys:=Real_0;
mind_bool[190]:=StanjeSP5_Delovanje; |  |  |  | Read_Real(rVar:=PMM.VirB_PFsys,lo:=4380,hi:=4381); |  | 190:StanjeSP5_Delovanje:=Bit_0; |  |  |  | 4381:PMM.VirB_PFsys:=Real_0;
mind_bool[191]:=StanjeUPSKrmOmara_BaterijskiNacin; |  |  |  | Read_Real(rVar:=PMM.VirB_Psys,lo:=4382,hi:=4383); |  | 191:StanjeUPSKrmOmara_BaterijskiNacin:=Bit_0; |  |  |  | 4383:PMM.VirB_Psys:=Real_0;
mind_bool[192]:=StanjeUPSKrmOmara_Polnenje; |  |  |  | Read_Real(rVar:=PMM.VirB_Qsys,lo:=4384,hi:=4385); |  | 192:StanjeUPSKrmOmara_Polnenje:=Bit_0; |  |  |  | 4385:PMM.VirB_Qsys:=Real_0;
mind_bool[193]:=UserLoggedIn; |  |  |  | Read_Real(rVar:=PMM.VirB_Ssys,lo:=4386,hi:=4387); |  | 193:UserLoggedIn:=Bit_0; |  |  |  | 4387:PMM.VirB_Ssys:=Real_0;
mind_bool[194]:=XVH_AlarmOn; |  |  |  | Read_Real(rVar:=PMM.VirB_Usys,lo:=4388,hi:=4389); |  | 194:XVH_AlarmOn:=Bit_0; |  |  |  | 4389:PMM.VirB_Usys:=Real_0;
mind_bool[195]:=Klimat1_Vklop; |  |  |  | Read_Real(rVar:=PMM.VirBActiveEnergyConsumed_kWh,lo:=4390,hi:=4391); |  | 195:Klimat1_Vklop:=Bit_0; |  |  |  | 4391:PMM.VirBActiveEnergyConsumed_kWh:=Real_0;
mind_bool[196]:=Klimat2_Vklop; |  |  |  | Read_Real(rVar:=PMM.VirBActivePowerPhaseA_kW,lo:=4392,hi:=4393); |  | 196:Klimat2_Vklop:=Bit_0; |  |  |  | 4393:PMM.VirBActivePowerPhaseA_kW:=Real_0;
mind_bool[197]:=Klimat3_Vklop; |  |  |  | Read_Real(rVar:=PMM.VirBActivePowerPhaseB_kW,lo:=4394,hi:=4395); |  | 197:Klimat3_Vklop:=Bit_0; |  |  |  | 4395:PMM.VirBActivePowerPhaseB_kW:=Real_0;
mind_bool[198]:=ErrCommScada2; |  |  |  | Read_Real(rVar:=PMM.VirBActivePowerPhaseC_kW,lo:=4396,hi:=4397); |  | 198:ErrCommScada2:=Bit_0; |  |  |  | 4397:PMM.VirBActivePowerPhaseC_kW:=Real_0;
mind_bool[199]:=ComSCADA2; |  |  |  | Read_Real(rVar:=PMM.VirBAparentPowerPhaseA,lo:=4398,hi:=4399); |  | 199:ComSCADA2:=Bit_0; |  |  |  | 4399:PMM.VirBAparentPowerPhaseA:=Real_0;
mind_bool[200]:=ComSCADA3; |  |  |  | Read_Real(rVar:=PMM.VirBAparentPowerPhaseB,lo:=4400,hi:=4401); |  | 200:ComSCADA3:=Bit_0; |  |  |  | 4401:PMM.VirBAparentPowerPhaseB:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBAparentPowerPhaseC,lo:=4402,hi:=4403); | [5 empty] | 4403:PMM.VirBAparentPowerPhaseC:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBAverageCurrent_A,lo:=4404,hi:=4405); | [5 empty] | 4405:PMM.VirBAverageCurrent_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBAveragePhaseToNeutral_V,lo:=4406,hi:=4407); | [5 empty] | 4407:PMM.VirBAveragePhaseToNeutral_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBAveragePhaseToPhase_V,lo:=4408,hi:=4409); | [5 empty] | 4409:PMM.VirBAveragePhaseToPhase_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBCurrentInPhaseA_A,lo:=4410,hi:=4411); | [5 empty] | 4411:PMM.VirBCurrentInPhaseA_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBCurrentInPhaseB_A,lo:=4412,hi:=4413); | [5 empty] | 4413:PMM.VirBCurrentInPhaseB_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBCurrentInPhaseC_A,lo:=4414,hi:=4415); | [5 empty] | 4415:PMM.VirBCurrentInPhaseC_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBFrequency_Hz,lo:=4416,hi:=4417); | [5 empty] | 4417:PMM.VirBFrequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBPowerFactorSys,lo:=4418,hi:=4419); | [5 empty] | 4419:PMM.VirBPowerFactorSys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBReactiveEnergyConsumed_kWh,lo:=4420,hi:=4421); | [5 empty] | 4421:PMM.VirBReactiveEnergyConsumed_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBReactivePowerPhaseA,lo:=4422,hi:=4423); | [5 empty] | 4423:PMM.VirBReactivePowerPhaseA:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBReactivePowerPhaseB,lo:=4424,hi:=4425); | [5 empty] | 4425:PMM.VirBReactivePowerPhaseB:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBReactivePowerPhaseC,lo:=4426,hi:=4427); | [5 empty] | 4427:PMM.VirBReactivePowerPhaseC:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBTotalActivePower_kW,lo:=4428,hi:=4429); | [5 empty] | 4429:PMM.VirBTotalActivePower_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBTotalAparentPower_kVA,lo:=4430,hi:=4431); | [5 empty] | 4431:PMM.VirBTotalAparentPower_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBTotalPowerFactor,lo:=4432,hi:=4433); | [5 empty] | 4433:PMM.VirBTotalPowerFactor:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBTotalReactivePower_kVAR,lo:=4434,hi:=4435); | [5 empty] | 4435:PMM.VirBTotalReactivePower_kVAR:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseAB_V,lo:=4436,hi:=4437); | [5 empty] | 4437:PMM.VirBVoltageBetweenPhaseAB_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseAN_V,lo:=4438,hi:=4439); | [5 empty] | 4439:PMM.VirBVoltageBetweenPhaseAN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseBC_V,lo:=4440,hi:=4441); | [5 empty] | 4441:PMM.VirBVoltageBetweenPhaseBC_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseBN_V,lo:=4442,hi:=4443); | [5 empty] | 4443:PMM.VirBVoltageBetweenPhaseBN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseCA_V,lo:=4444,hi:=4445); | [5 empty] | 4445:PMM.VirBVoltageBetweenPhaseCA_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseCN_V,lo:=4446,hi:=4447); | [5 empty] | 4447:PMM.VirBVoltageBetweenPhaseCN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VoltageBetweenPhaseAB_V,lo:=4448,hi:=4449); | [5 empty] | 4449:PMM.VoltageBetweenPhaseAB_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VoltageBetweenPhaseAN_V,lo:=4450,hi:=4451); | [5 empty] | 4451:PMM.VoltageBetweenPhaseAN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VoltageBetweenPhaseBC_V,lo:=4452,hi:=4453); | [5 empty] | 4453:PMM.VoltageBetweenPhaseBC_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VoltageBetweenPhaseBN_V,lo:=4454,hi:=4455); | [5 empty] | 4455:PMM.VoltageBetweenPhaseBN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VoltageBetweenPhaseCA_V,lo:=4456,hi:=4457); | [5 empty] | 4457:PMM.VoltageBetweenPhaseCA_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM.VoltageBetweenPhaseCN_V,lo:=4458,hi:=4459); | [5 empty] | 4459:PMM.VoltageBetweenPhaseCN_V:=Real_0;
|  |  |  | Read_Real(rVar:=SKTemp1,lo:=4460,hi:=4461); | [5 empty] | 4461:SKTemp1:=Real_0;
|  |  |  | Read_Real(rVar:=SKTemp2,lo:=4462,hi:=4463); | [5 empty] | 4463:SKTemp2:=Real_0;
|  |  |  | Read_Real(rVar:=SKTemp3,lo:=4464,hi:=4465); | [5 empty] | 4465:SKTemp3:=Real_0;
|  |  |  | Read_Real(rVar:=SKTempKontrSoba,lo:=4466,hi:=4467); | [5 empty] | 4467:SKTempKontrSoba:=Real_0;
|  |  |  | Read_Real(rVar:=SKTempLinkProstor,lo:=4468,hi:=4469); | [5 empty] | 4469:SKTempLinkProstor:=Real_0;
|  |  |  | Read_Real(rVar:=SKTempServSoba1Povpr,lo:=4470,hi:=4471); | [5 empty] | 4471:SKTempServSoba1Povpr:=Real_0;
|  |  |  | Read_Real(rVar:=SKVlaga1,lo:=4472,hi:=4473); | [5 empty] | 4473:SKVlaga1:=Real_0;
|  |  |  | Read_Real(rVar:=SKVlaga2,lo:=4474,hi:=4475); | [5 empty] | 4475:SKVlaga2:=Real_0;
|  |  |  | Read_Real(rVar:=SKVlaga3,lo:=4476,hi:=4477); | [5 empty] | 4477:SKVlaga3:=Real_0;
|  |  |  | Read_Real(rVar:=SKVlagaKontrSoba,lo:=4478,hi:=4479); | [5 empty] | 4479:SKVlagaKontrSoba:=Real_0;
|  |  |  | Read_Real(rVar:=SKVlagaLinkProstor,lo:=4480,hi:=4481); | [5 empty] | 4481:SKVlagaLinkProstor:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaAlarmTIA123,lo:=4482,hi:=4483); | [5 empty] | 4483:TempZaAlarmTIA123:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaAlarmTIA4,lo:=4484,hi:=4485); | [5 empty] | 4485:TempZaAlarmTIA4:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaAlarmTIA5,lo:=4486,hi:=4487); | [5 empty] | 4487:TempZaAlarmTIA5:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaVklopObehKlim,lo:=4488,hi:=4489); | [5 empty] | 4489:TempZaVklopObehKlim:=Real_0;

## XSoft_EXP
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
PROGRAM mod_Read
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*Branje BOOL*)
(**)
mind_bool[0]:=AlarmKlimat1_Napaka;
mind_bool[1]:=AlarmKlimat2_Napaka;
mind_bool[2]:=AlarmKlimat3_Napaka;
mind_bool[3]:=AlarmLAH1_RazlitjeVode;
mind_bool[4]:=AlarmLAH2_RazlitjeVode;
mind_bool[5]:=AlarmSinhronizacijaNOK;
mind_bool[6]:=AlarmSP1_Napaka;
mind_bool[7]:=AlarmSP2_Napaka;
mind_bool[8]:=AlarmSP3_Napaka;
mind_bool[9]:=AlarmSP4_Napaka;
mind_bool[10]:=AlarmSP5_Napaka;
mind_bool[11]:=AlarmTempTIA123Previsoka;
mind_bool[12]:=AlarmTempTIA4Previsoka;
mind_bool[13]:=AlarmTempTIA5Previsoka;
mind_bool[14]:=AlarmTSTempPrevisoka;
mind_bool[15]:=AlarmUPSKrmOmara_Alarm;
mind_bool[16]:=ComSCADA;
mind_bool[17]:=ComSCADA1;
mind_bool[18]:=ErrComKlima[1];
mind_bool[19]:=ErrComKlima[2];
mind_bool[20]:=ErrComKlima[3];
mind_bool[21]:=ErrCommScada;
mind_bool[22]:=ErrComPanelPLC;
mind_bool[23]:=ErrComPMM;
mind_bool[24]:=ErrComPort2;
mind_bool[25]:=Klima1_Onemogocena;
mind_bool[26]:=Klima2_Onemogocena;
mind_bool[27]:=Klima3_Onemogocena;
mind_bool[28]:=Klima[1].IzhodniVentilator;
mind_bool[29]:=Klima[1].Kompresor1;
mind_bool[30]:=Klima[1].Kompresor2;
mind_bool[31]:=Klima[1].Razvlazevanje;
mind_bool[32]:=Klima[1].VentilGretjeOdpiranje;
mind_bool[33]:=Klima[1].VentilGretjeZapiranje;
mind_bool[34]:=Klima[1].Vlazenje;
mind_bool[35]:=Klima[2].IzhodniVentilator;
mind_bool[36]:=Klima[2].Kompresor1;
mind_bool[37]:=Klima[2].Kompresor2;
mind_bool[38]:=Klima[2].Razvlazevanje;
mind_bool[39]:=Klima[2].VentilGretjeOdpiranje;
mind_bool[40]:=Klima[2].VentilGretjeZapiranje;
mind_bool[41]:=Klima[2].Vlazenje;
mind_bool[42]:=Klima[3].IzhodniVentilator;
mind_bool[43]:=Klima[3].Kompresor1;
mind_bool[44]:=Klima[3].Kompresor2;
mind_bool[45]:=Klima[3].Razvlazevanje;
mind_bool[46]:=Klima[3].VentilGretjeOdpiranje;
mind_bool[47]:=Klima[3].VentilGretjeZapiranje;
mind_bool[48]:=Klima[3].Vlazenje;
mind_bool[49]:=KlimaError[1].AlarmKompresor1;
mind_bool[50]:=KlimaError[1].AlarmKompresor2;
mind_bool[51]:=KlimaError[1].FenThermalCutout;
mind_bool[52]:=KlimaError[1].IzlivVode;
mind_bool[53]:=KlimaError[1].Kompresor1naMejiStevilaObrUr;
mind_bool[54]:=KlimaError[1].Kompresor2naMejiStevilaObrUr;
mind_bool[55]:=KlimaError[1].Kond1FenThermalCutout;
mind_bool[56]:=KlimaError[1].Kond2FenThermalCutout;
mind_bool[57]:=KlimaError[1].NapakaPriPretokuVode;
mind_bool[58]:=KlimaError[1].NapakaPriPretokuZraka;
mind_bool[59]:=KlimaError[1].NapakaSenzorPritiska;
mind_bool[60]:=KlimaError[1].NapakaSenzorVlaznosti;
mind_bool[61]:=KlimaError[1].NapakaTSTemperaturaProstora;
mind_bool[62]:=KlimaError[1].NiTokaVVlazilcu;
mind_bool[63]:=KlimaError[1].NiVodeVVlazilcu;
mind_bool[64]:=KlimaError[1].NizekPritiskKompresor1;
mind_bool[65]:=KlimaError[1].NizekPritiskKompresor2;
mind_bool[66]:=KlimaError[1].NizkaTempVProstoru;
mind_bool[67]:=KlimaError[1].NizkaVlaznost;
mind_bool[68]:=KlimaError[1].PozarniAlarm;
mind_bool[69]:=KlimaError[1].TermZascInVisokPritiskKompr1;
mind_bool[70]:=KlimaError[1].TermZascInVisokPritiskKompr2;
mind_bool[71]:=KlimaError[1].ThermalCutoutHeater1;
mind_bool[72]:=KlimaError[1].ThermalCutoutHeater2;
mind_bool[73]:=KlimaError[1].VentilatorNaMejiStevilaObrUr;
mind_bool[74]:=KlimaError[1].VisokaTempVProstoru;
mind_bool[75]:=KlimaError[1].VisokaVlaznost;
mind_bool[76]:=KlimaError[1].VisokPritiskVKrogu1;
mind_bool[77]:=KlimaError[1].VisokPritiskVKrogu2;
mind_bool[78]:=KlimaError[1].VisokTokVVlazilcu;
mind_bool[79]:=KlimaError[1].VlazilecnaMejiStevilaObrUr;
mind_bool[80]:=KlimaError[1].ZamasenFilter;
mind_bool[81]:=KlimaError[1].ZunanjiAlarm;
mind_bool[82]:=KlimaError[2].AlarmKompresor1;
mind_bool[83]:=KlimaError[2].AlarmKompresor2;
mind_bool[84]:=KlimaError[2].FenThermalCutout;
mind_bool[85]:=KlimaError[2].IzlivVode;
mind_bool[86]:=KlimaError[2].Kompresor1naMejiStevilaObrUr;
mind_bool[87]:=KlimaError[2].Kompresor2naMejiStevilaObrUr;
mind_bool[88]:=KlimaError[2].Kond1FenThermalCutout;
mind_bool[89]:=KlimaError[2].Kond2FenThermalCutout;
mind_bool[90]:=KlimaError[2].NapakaPriPretokuVode;
mind_bool[91]:=KlimaError[2].NapakaPriPretokuZraka;
mind_bool[92]:=KlimaError[2].NapakaSenzorPritiska;
mind_bool[93]:=KlimaError[2].NapakaSenzorVlaznosti;
mind_bool[94]:=KlimaError[2].NapakaTSTemperaturaProstora;
mind_bool[95]:=KlimaError[2].NiTokaVVlazilcu;
mind_bool[96]:=KlimaError[2].NiVodeVVlazilcu;
mind_bool[97]:=KlimaError[2].NizekPritiskKompresor1;
mind_bool[98]:=KlimaError[2].NizekPritiskKompresor2;
mind_bool[99]:=KlimaError[2].NizkaTempVProstoru;
mind_bool[100]:=KlimaError[2].NizkaVlaznost;
mind_bool[101]:=KlimaError[2].PozarniAlarm;
mind_bool[102]:=KlimaError[2].TermZascInVisokPritiskKompr1;
mind_bool[103]:=KlimaError[2].TermZascInVisokPritiskKompr2;
mind_bool[104]:=KlimaError[2].ThermalCutoutHeater1;
mind_bool[105]:=KlimaError[2].ThermalCutoutHeater2;
mind_bool[106]:=KlimaError[2].VentilatorNaMejiStevilaObrUr;
mind_bool[107]:=KlimaError[2].VisokaTempVProstoru;
mind_bool[108]:=KlimaError[2].VisokaVlaznost;
mind_bool[109]:=KlimaError[2].VisokPritiskVKrogu1;
mind_bool[110]:=KlimaError[2].VisokPritiskVKrogu2;
mind_bool[111]:=KlimaError[2].VisokTokVVlazilcu;
mind_bool[112]:=KlimaError[2].VlazilecnaMejiStevilaObrUr;
mind_bool[113]:=KlimaError[2].ZamasenFilter;
mind_bool[114]:=KlimaError[2].ZunanjiAlarm;
mind_bool[115]:=KlimaError[3].AlarmKompresor1;
mind_bool[116]:=KlimaError[3].AlarmKompresor2;
mind_bool[117]:=KlimaError[3].FenThermalCutout;
mind_bool[118]:=KlimaError[3].IzlivVode;
mind_bool[119]:=KlimaError[3].Kompresor1naMejiStevilaObrUr;
mind_bool[120]:=KlimaError[3].Kompresor2naMejiStevilaObrUr;
mind_bool[121]:=KlimaError[3].Kond1FenThermalCutout;
mind_bool[122]:=KlimaError[3].Kond2FenThermalCutout;
mind_bool[123]:=KlimaError[3].NapakaPriPretokuVode;
mind_bool[124]:=KlimaError[3].NapakaPriPretokuZraka;
mind_bool[125]:=KlimaError[3].NapakaSenzorPritiska;
mind_bool[126]:=KlimaError[3].NapakaSenzorVlaznosti;
mind_bool[127]:=KlimaError[3].NapakaTSTemperaturaProstora;
mind_bool[128]:=KlimaError[3].NiTokaVVlazilcu;
mind_bool[129]:=KlimaError[3].NiVodeVVlazilcu;
mind_bool[130]:=KlimaError[3].NizekPritiskKompresor1;
mind_bool[131]:=KlimaError[3].NizekPritiskKompresor2;
mind_bool[132]:=KlimaError[3].NizkaTempVProstoru;
mind_bool[133]:=KlimaError[3].NizkaVlaznost;
mind_bool[134]:=KlimaError[3].PozarniAlarm;
mind_bool[135]:=KlimaError[3].TermZascInVisokPritiskKompr1;
mind_bool[136]:=KlimaError[3].TermZascInVisokPritiskKompr2;
mind_bool[137]:=KlimaError[3].ThermalCutoutHeater1;
mind_bool[138]:=KlimaError[3].ThermalCutoutHeater2;
mind_bool[139]:=KlimaError[3].VentilatorNaMejiStevilaObrUr;
mind_bool[140]:=KlimaError[3].VisokaTempVProstoru;
mind_bool[141]:=KlimaError[3].VisokaVlaznost;
mind_bool[142]:=KlimaError[3].VisokPritiskVKrogu1;
mind_bool[143]:=KlimaError[3].VisokPritiskVKrogu2;
mind_bool[144]:=KlimaError[3].VisokTokVVlazilcu;
mind_bool[145]:=KlimaError[3].VlazilecnaMejiStevilaObrUr;
mind_bool[146]:=KlimaError[3].ZamasenFilter;
mind_bool[147]:=KlimaError[3].ZunanjiAlarm;
mind_bool[148]:=NacDelovanjaKlime1_Avtomatsko;
mind_bool[149]:=NacDelovanjaKlime2_3Avtomatsko;
mind_bool[150]:=NapakaSenzorTemp1;
mind_bool[151]:=NapakaSenzorTemp2;
mind_bool[152]:=NapakaSenzorTemp3;
mind_bool[153]:=NapakaSenzorTempKontrSoba;
mind_bool[154]:=NapakaSenzorTempLinkProstor;
mind_bool[155]:=NapakaSenzorVlaga1;
mind_bool[156]:=NapakaSenzorVlaga2;
mind_bool[157]:=NapakaSenzorVlaga3;
mind_bool[158]:=NapakaSenzorVlagaKontrSoba;
mind_bool[159]:=NapakaSenzorVlagaLinkProstor;
mind_bool[160]:=NastaviCasNaKrmilniku;
mind_bool[161]:=NastavitevUreKrUspesna;
mind_bool[162]:=OpozoriloBaterijaPLC;
mind_bool[163]:=PMM1OverCurrentBetw[1];
mind_bool[164]:=PMM1OverCurrentBetw[2];
mind_bool[165]:=PMM1OverCurrentBetw[3];
mind_bool[166]:=PMM1OverCurrentOver[1];
mind_bool[167]:=PMM1OverCurrentOver[2];
mind_bool[168]:=PMM1OverCurrentOver[3];
mind_bool[169]:=PMM1OverVoltage;
mind_bool[170]:=RocniVklopKlima1;
mind_bool[171]:=RocniVklopKlima2;
mind_bool[172]:=RocniVklopKlima3;
mind_bool[173]:=SinhronizacijaPanelOK;
mind_bool[174]:=SinhronizirajCas_Panel;
mind_bool[175]:=SkupneNapakeNaprav_Klima1;
mind_bool[176]:=SkupneNapakeNaprav_Klima2;
mind_bool[177]:=SkupneNapakeNaprav_Klima3;
mind_bool[178]:=SkupneNapakeNaprav_Komunikacija;
mind_bool[179]:=SkupneNapakeNaprav_PMMVirA;
mind_bool[180]:=SkupneNapakeNaprav_PMMVirB;
mind_bool[181]:=SkupneNapakeNaprav_PMMVirBVirA;
mind_bool[182]:=SkupneNapakeNaprav_TempVlaga;
mind_bool[183]:=StanjeKlimat1_Delovanje;
mind_bool[184]:=StanjeKlimat2_Delovanje;
mind_bool[185]:=StanjeKlimat3_Delovanje;
mind_bool[186]:=StanjeSP1_Delovanje;
mind_bool[187]:=StanjeSP2_Delovanje;
mind_bool[188]:=StanjeSP3_Delovanje;
mind_bool[189]:=StanjeSP4_Delovanje;
mind_bool[190]:=StanjeSP5_Delovanje;
mind_bool[191]:=StanjeUPSKrmOmara_BaterijskiNacin;
mind_bool[192]:=StanjeUPSKrmOmara_Polnenje;
mind_bool[193]:=UserLoggedIn;
mind_bool[194]:=XVH_AlarmOn;
mind_bool[195]:=Klimat1_Vklop;
mind_bool[196]:=Klimat2_Vklop;
mind_bool[197]:=Klimat3_Vklop;
mind_bool[198]:=ErrCommScada2;
mind_bool[199]:=ComSCADA2;
mind_bool[200]:=ComSCADA3;
(*Branje INT*)
(**)
mind[0]:=DatumCas.Dan;
mind[1]:=DatumCas.Leto;
mind[2]:=DatumCas.Leto2;
mind[3]:=DatumCas.Mesec;
mind[4]:=DatumCas.Minuta;
mind[5]:=DatumCas.Sekunda;
mind[6]:=DatumCas.Ura;
mind[7]:=Klima[1].Vlazilec_Stanja;
mind[8]:=Klima[2].Vlazilec_Stanja;
mind[9]:=Klima[3].Vlazilec_Stanja;
mind[10]:=StUrZaPreklopKlim;
mind[11]:=UPSstatus_Prikaz_PanelSCADA;
mind[12]:=UserCurrentLevel;
(*Branje UINT*)
(**)
mind[6000]:=PMM.AlarmPhase[1].C01_16_60to80;
mind[6001]:=PMM.AlarmPhase[1].C01_16_over80;
mind[6002]:=PMM.AlarmPhase[1].C17_32_60to80;
mind[6003]:=PMM.AlarmPhase[1].C17_32_over80;
mind[6004]:=PMM.AlarmPhase[1].C33_42_60to80;
mind[6005]:=PMM.AlarmPhase[1].C33_42_over80;
mind[6006]:=PMM.AlarmPhase[2].C01_16_60to80;
mind[6007]:=PMM.AlarmPhase[2].C01_16_over80;
mind[6008]:=PMM.AlarmPhase[2].C17_32_60to80;
mind[6009]:=PMM.AlarmPhase[2].C17_32_over80;
mind[6010]:=PMM.AlarmPhase[2].C33_42_60to80;
mind[6011]:=PMM.AlarmPhase[2].C33_42_over80;
mind[6012]:=PMM.AlarmPhase[3].C01_16_60to80;
mind[6013]:=PMM.AlarmPhase[3].C01_16_over80;
mind[6014]:=PMM.AlarmPhase[3].C17_32_60to80;
mind[6015]:=PMM.AlarmPhase[3].C17_32_over80;
mind[6016]:=PMM.AlarmPhase[3].C33_42_60to80;
mind[6017]:=PMM.AlarmPhase[3].C33_42_over80;
mind[6018]:=kom_nast_cas_izpada;
(*Branje LONG*)
(**)
(*Branje REAL*)
(**)
Read_Real(rVar:=AktualniSetPointTemp,lo:=4000,hi:=4001);
Read_Real(rVar:=AktualniSetPointVlaga,lo:=4002,hi:=4003);
Read_Real(rVar:=Klima[1].NastMaxTemp,lo:=4004,hi:=4005);
Read_Real(rVar:=Klima[1].NastMaxVlaznost,lo:=4006,hi:=4007);
Read_Real(rVar:=Klima[1].NastMinTemp,lo:=4008,hi:=4009);
Read_Real(rVar:=Klima[1].NastMinVlaznost,lo:=4010,hi:=4011);
Read_Real(rVar:=Klima[1].NastTempProstora,lo:=4012,hi:=4013);
Read_Real(rVar:=Klima[1].NastVlaznost,lo:=4014,hi:=4015);
Read_Real(rVar:=Klima[1].Pritisk,lo:=4016,hi:=4017);
Read_Real(rVar:=Klima[1].TemperaturaProstora,lo:=4018,hi:=4019);
Read_Real(rVar:=Klima[1].VlaznostProstora,lo:=4020,hi:=4021);
Read_Real(rVar:=Klima[2].NastMaxTemp,lo:=4022,hi:=4023);
Read_Real(rVar:=Klima[2].NastMaxVlaznost,lo:=4024,hi:=4025);
Read_Real(rVar:=Klima[2].NastMinTemp,lo:=4026,hi:=4027);
Read_Real(rVar:=Klima[2].NastMinVlaznost,lo:=4028,hi:=4029);
Read_Real(rVar:=Klima[2].NastTempProstora,lo:=4030,hi:=4031);
Read_Real(rVar:=Klima[2].NastVlaznost,lo:=4032,hi:=4033);
Read_Real(rVar:=Klima[2].Pritisk,lo:=4034,hi:=4035);
Read_Real(rVar:=Klima[2].TemperaturaProstora,lo:=4036,hi:=4037);
Read_Real(rVar:=Klima[2].VlaznostProstora,lo:=4038,hi:=4039);
Read_Real(rVar:=Klima[3].NastMaxTemp,lo:=4040,hi:=4041);
Read_Real(rVar:=Klima[3].NastMaxVlaznost,lo:=4042,hi:=4043);
Read_Real(rVar:=Klima[3].NastMinTemp,lo:=4044,hi:=4045);
Read_Real(rVar:=Klima[3].NastMinVlaznost,lo:=4046,hi:=4047);
Read_Real(rVar:=Klima[3].NastTempProstora,lo:=4048,hi:=4049);
Read_Real(rVar:=Klima[3].NastVlaznost,lo:=4050,hi:=4051);
Read_Real(rVar:=Klima[3].Pritisk,lo:=4052,hi:=4053);
Read_Real(rVar:=Klima[3].TemperaturaProstora,lo:=4054,hi:=4055);
Read_Real(rVar:=Klima[3].VlaznostProstora,lo:=4056,hi:=4057);
Read_Real(rVar:=ObratUreKlim[1],lo:=4058,hi:=4059);
Read_Real(rVar:=ObratUreKlim[2],lo:=4060,hi:=4061);
Read_Real(rVar:=ObratUreKlim[3],lo:=4062,hi:=4063);
Read_Real(rVar:=PMM.ActiveEnergyConsumed_kWh,lo:=4064,hi:=4065);
Read_Real(rVar:=PMM.ActivePowerPhaseA_kW,lo:=4066,hi:=4067);
Read_Real(rVar:=PMM.ActivePowerPhaseB_kW,lo:=4068,hi:=4069);
Read_Real(rVar:=PMM.ActivePowerPhaseC_kW,lo:=4070,hi:=4071);
Read_Real(rVar:=PMM.AparentPowerPhaseA,lo:=4072,hi:=4073);
Read_Real(rVar:=PMM.AparentPowerPhaseB,lo:=4074,hi:=4075);
Read_Real(rVar:=PMM.AparentPowerPhaseC,lo:=4076,hi:=4077);
Read_Real(rVar:=PMM.AverageCurrent_A,lo:=4078,hi:=4079);
Read_Real(rVar:=PMM.AveragePhaseToNeutral_V,lo:=4080,hi:=4081);
Read_Real(rVar:=PMM.AveragePhaseToPhase_V,lo:=4082,hi:=4083);
Read_Real(rVar:=PMM.CurrentInPhaseA_A,lo:=4084,hi:=4085);
Read_Real(rVar:=PMM.CurrentInPhaseB_A,lo:=4086,hi:=4087);
Read_Real(rVar:=PMM.CurrentInPhaseC_A,lo:=4088,hi:=4089);
Read_Real(rVar:=PMM.Frequency_Hz,lo:=4090,hi:=4091);
Read_Real(rVar:=PMM.Phase[1].Current[10],lo:=4092,hi:=4093);
Read_Real(rVar:=PMM.Phase[1].Current[11],lo:=4094,hi:=4095);
Read_Real(rVar:=PMM.Phase[1].Current[12],lo:=4096,hi:=4097);
Read_Real(rVar:=PMM.Phase[1].Current[13],lo:=4098,hi:=4099);
Read_Real(rVar:=PMM.Phase[1].Current[14],lo:=4100,hi:=4101);
Read_Real(rVar:=PMM.Phase[1].Current[15],lo:=4102,hi:=4103);
Read_Real(rVar:=PMM.Phase[1].Current[16],lo:=4104,hi:=4105);
Read_Real(rVar:=PMM.Phase[1].Current[17],lo:=4106,hi:=4107);
Read_Real(rVar:=PMM.Phase[1].Current[18],lo:=4108,hi:=4109);
Read_Real(rVar:=PMM.Phase[1].Current[19],lo:=4110,hi:=4111);
Read_Real(rVar:=PMM.Phase[1].Current[1],lo:=4112,hi:=4113);
Read_Real(rVar:=PMM.Phase[1].Current[20],lo:=4114,hi:=4115);
Read_Real(rVar:=PMM.Phase[1].Current[21],lo:=4116,hi:=4117);
Read_Real(rVar:=PMM.Phase[1].Current[22],lo:=4118,hi:=4119);
Read_Real(rVar:=PMM.Phase[1].Current[23],lo:=4120,hi:=4121);
Read_Real(rVar:=PMM.Phase[1].Current[24],lo:=4122,hi:=4123);
Read_Real(rVar:=PMM.Phase[1].Current[25],lo:=4124,hi:=4125);
Read_Real(rVar:=PMM.Phase[1].Current[26],lo:=4126,hi:=4127);
Read_Real(rVar:=PMM.Phase[1].Current[27],lo:=4128,hi:=4129);
Read_Real(rVar:=PMM.Phase[1].Current[28],lo:=4130,hi:=4131);
Read_Real(rVar:=PMM.Phase[1].Current[29],lo:=4132,hi:=4133);
Read_Real(rVar:=PMM.Phase[1].Current[2],lo:=4134,hi:=4135);
Read_Real(rVar:=PMM.Phase[1].Current[30],lo:=4136,hi:=4137);
Read_Real(rVar:=PMM.Phase[1].Current[31],lo:=4138,hi:=4139);
Read_Real(rVar:=PMM.Phase[1].Current[32],lo:=4140,hi:=4141);
Read_Real(rVar:=PMM.Phase[1].Current[33],lo:=4142,hi:=4143);
Read_Real(rVar:=PMM.Phase[1].Current[34],lo:=4144,hi:=4145);
Read_Real(rVar:=PMM.Phase[1].Current[35],lo:=4146,hi:=4147);
Read_Real(rVar:=PMM.Phase[1].Current[36],lo:=4148,hi:=4149);
Read_Real(rVar:=PMM.Phase[1].Current[37],lo:=4150,hi:=4151);
Read_Real(rVar:=PMM.Phase[1].Current[38],lo:=4152,hi:=4153);
Read_Real(rVar:=PMM.Phase[1].Current[39],lo:=4154,hi:=4155);
Read_Real(rVar:=PMM.Phase[1].Current[3],lo:=4156,hi:=4157);
Read_Real(rVar:=PMM.Phase[1].Current[40],lo:=4158,hi:=4159);
Read_Real(rVar:=PMM.Phase[1].Current[41],lo:=4160,hi:=4161);
Read_Real(rVar:=PMM.Phase[1].Current[42],lo:=4162,hi:=4163);
Read_Real(rVar:=PMM.Phase[1].Current[4],lo:=4164,hi:=4165);
Read_Real(rVar:=PMM.Phase[1].Current[5],lo:=4166,hi:=4167);
Read_Real(rVar:=PMM.Phase[1].Current[6],lo:=4168,hi:=4169);
Read_Real(rVar:=PMM.Phase[1].Current[7],lo:=4170,hi:=4171);
Read_Real(rVar:=PMM.Phase[1].Current[8],lo:=4172,hi:=4173);
Read_Real(rVar:=PMM.Phase[1].Current[9],lo:=4174,hi:=4175);
Read_Real(rVar:=PMM.Phase[2].Current[10],lo:=4176,hi:=4177);
Read_Real(rVar:=PMM.Phase[2].Current[11],lo:=4178,hi:=4179);
Read_Real(rVar:=PMM.Phase[2].Current[12],lo:=4180,hi:=4181);
Read_Real(rVar:=PMM.Phase[2].Current[13],lo:=4182,hi:=4183);
Read_Real(rVar:=PMM.Phase[2].Current[14],lo:=4184,hi:=4185);
Read_Real(rVar:=PMM.Phase[2].Current[15],lo:=4186,hi:=4187);
Read_Real(rVar:=PMM.Phase[2].Current[16],lo:=4188,hi:=4189);
Read_Real(rVar:=PMM.Phase[2].Current[17],lo:=4190,hi:=4191);
Read_Real(rVar:=PMM.Phase[2].Current[18],lo:=4192,hi:=4193);
Read_Real(rVar:=PMM.Phase[2].Current[19],lo:=4194,hi:=4195);
Read_Real(rVar:=PMM.Phase[2].Current[1],lo:=4196,hi:=4197);
Read_Real(rVar:=PMM.Phase[2].Current[20],lo:=4198,hi:=4199);
Read_Real(rVar:=PMM.Phase[2].Current[21],lo:=4200,hi:=4201);
Read_Real(rVar:=PMM.Phase[2].Current[22],lo:=4202,hi:=4203);
Read_Real(rVar:=PMM.Phase[2].Current[23],lo:=4204,hi:=4205);
Read_Real(rVar:=PMM.Phase[2].Current[24],lo:=4206,hi:=4207);
Read_Real(rVar:=PMM.Phase[2].Current[25],lo:=4208,hi:=4209);
Read_Real(rVar:=PMM.Phase[2].Current[26],lo:=4210,hi:=4211);
Read_Real(rVar:=PMM.Phase[2].Current[27],lo:=4212,hi:=4213);
Read_Real(rVar:=PMM.Phase[2].Current[28],lo:=4214,hi:=4215);
Read_Real(rVar:=PMM.Phase[2].Current[29],lo:=4216,hi:=4217);
Read_Real(rVar:=PMM.Phase[2].Current[2],lo:=4218,hi:=4219);
Read_Real(rVar:=PMM.Phase[2].Current[30],lo:=4220,hi:=4221);
Read_Real(rVar:=PMM.Phase[2].Current[31],lo:=4222,hi:=4223);
Read_Real(rVar:=PMM.Phase[2].Current[32],lo:=4224,hi:=4225);
Read_Real(rVar:=PMM.Phase[2].Current[33],lo:=4226,hi:=4227);
Read_Real(rVar:=PMM.Phase[2].Current[34],lo:=4228,hi:=4229);
Read_Real(rVar:=PMM.Phase[2].Current[35],lo:=4230,hi:=4231);
Read_Real(rVar:=PMM.Phase[2].Current[36],lo:=4232,hi:=4233);
Read_Real(rVar:=PMM.Phase[2].Current[37],lo:=4234,hi:=4235);
Read_Real(rVar:=PMM.Phase[2].Current[38],lo:=4236,hi:=4237);
Read_Real(rVar:=PMM.Phase[2].Current[39],lo:=4238,hi:=4239);
Read_Real(rVar:=PMM.Phase[2].Current[3],lo:=4240,hi:=4241);
Read_Real(rVar:=PMM.Phase[2].Current[40],lo:=4242,hi:=4243);
Read_Real(rVar:=PMM.Phase[2].Current[41],lo:=4244,hi:=4245);
Read_Real(rVar:=PMM.Phase[2].Current[42],lo:=4246,hi:=4247);
Read_Real(rVar:=PMM.Phase[2].Current[4],lo:=4248,hi:=4249);
Read_Real(rVar:=PMM.Phase[2].Current[5],lo:=4250,hi:=4251);
Read_Real(rVar:=PMM.Phase[2].Current[6],lo:=4252,hi:=4253);
Read_Real(rVar:=PMM.Phase[2].Current[7],lo:=4254,hi:=4255);
Read_Real(rVar:=PMM.Phase[2].Current[8],lo:=4256,hi:=4257);
Read_Real(rVar:=PMM.Phase[2].Current[9],lo:=4258,hi:=4259);
Read_Real(rVar:=PMM.Phase[3].Current[10],lo:=4260,hi:=4261);
Read_Real(rVar:=PMM.Phase[3].Current[11],lo:=4262,hi:=4263);
Read_Real(rVar:=PMM.Phase[3].Current[12],lo:=4264,hi:=4265);
Read_Real(rVar:=PMM.Phase[3].Current[13],lo:=4266,hi:=4267);
Read_Real(rVar:=PMM.Phase[3].Current[14],lo:=4268,hi:=4269);
Read_Real(rVar:=PMM.Phase[3].Current[15],lo:=4270,hi:=4271);
Read_Real(rVar:=PMM.Phase[3].Current[16],lo:=4272,hi:=4273);
Read_Real(rVar:=PMM.Phase[3].Current[17],lo:=4274,hi:=4275);
Read_Real(rVar:=PMM.Phase[3].Current[18],lo:=4276,hi:=4277);
Read_Real(rVar:=PMM.Phase[3].Current[19],lo:=4278,hi:=4279);
Read_Real(rVar:=PMM.Phase[3].Current[1],lo:=4280,hi:=4281);
Read_Real(rVar:=PMM.Phase[3].Current[20],lo:=4282,hi:=4283);
Read_Real(rVar:=PMM.Phase[3].Current[21],lo:=4284,hi:=4285);
Read_Real(rVar:=PMM.Phase[3].Current[22],lo:=4286,hi:=4287);
Read_Real(rVar:=PMM.Phase[3].Current[23],lo:=4288,hi:=4289);
Read_Real(rVar:=PMM.Phase[3].Current[24],lo:=4290,hi:=4291);
Read_Real(rVar:=PMM.Phase[3].Current[25],lo:=4292,hi:=4293);
Read_Real(rVar:=PMM.Phase[3].Current[26],lo:=4294,hi:=4295);
Read_Real(rVar:=PMM.Phase[3].Current[27],lo:=4296,hi:=4297);
Read_Real(rVar:=PMM.Phase[3].Current[28],lo:=4298,hi:=4299);
Read_Real(rVar:=PMM.Phase[3].Current[29],lo:=4300,hi:=4301);
Read_Real(rVar:=PMM.Phase[3].Current[2],lo:=4302,hi:=4303);
Read_Real(rVar:=PMM.Phase[3].Current[30],lo:=4304,hi:=4305);
Read_Real(rVar:=PMM.Phase[3].Current[31],lo:=4306,hi:=4307);
Read_Real(rVar:=PMM.Phase[3].Current[32],lo:=4308,hi:=4309);
Read_Real(rVar:=PMM.Phase[3].Current[33],lo:=4310,hi:=4311);
Read_Real(rVar:=PMM.Phase[3].Current[34],lo:=4312,hi:=4313);
Read_Real(rVar:=PMM.Phase[3].Current[35],lo:=4314,hi:=4315);
Read_Real(rVar:=PMM.Phase[3].Current[36],lo:=4316,hi:=4317);
Read_Real(rVar:=PMM.Phase[3].Current[37],lo:=4318,hi:=4319);
Read_Real(rVar:=PMM.Phase[3].Current[38],lo:=4320,hi:=4321);
Read_Real(rVar:=PMM.Phase[3].Current[39],lo:=4322,hi:=4323);
Read_Real(rVar:=PMM.Phase[3].Current[3],lo:=4324,hi:=4325);
Read_Real(rVar:=PMM.Phase[3].Current[40],lo:=4326,hi:=4327);
Read_Real(rVar:=PMM.Phase[3].Current[41],lo:=4328,hi:=4329);
Read_Real(rVar:=PMM.Phase[3].Current[42],lo:=4330,hi:=4331);
Read_Real(rVar:=PMM.Phase[3].Current[4],lo:=4332,hi:=4333);
Read_Real(rVar:=PMM.Phase[3].Current[5],lo:=4334,hi:=4335);
Read_Real(rVar:=PMM.Phase[3].Current[6],lo:=4336,hi:=4337);
Read_Real(rVar:=PMM.Phase[3].Current[7],lo:=4338,hi:=4339);
Read_Real(rVar:=PMM.Phase[3].Current[8],lo:=4340,hi:=4341);
Read_Real(rVar:=PMM.Phase[3].Current[9],lo:=4342,hi:=4343);
Read_Real(rVar:=PMM.PowerFactorSys,lo:=4344,hi:=4345);
Read_Real(rVar:=PMM.ReactiveEnergyConsumed_kVARh,lo:=4346,hi:=4347);
Read_Real(rVar:=PMM.ReactivePowerPhaseA,lo:=4348,hi:=4349);
Read_Real(rVar:=PMM.ReactivePowerPhaseB,lo:=4350,hi:=4351);
Read_Real(rVar:=PMM.ReactivePowerPhaseC,lo:=4352,hi:=4353);
Read_Real(rVar:=PMM.TotalActivePower_kW,lo:=4354,hi:=4355);
Read_Real(rVar:=PMM.TotalAparentPower_kVA,lo:=4356,hi:=4357);
Read_Real(rVar:=PMM.TotalPowerFactor,lo:=4358,hi:=4359);
Read_Real(rVar:=PMM.TotalReactivePower_kVAR,lo:=4360,hi:=4361);
Read_Real(rVar:=PMM.VirA_fsys,lo:=4362,hi:=4363);
Read_Real(rVar:=PMM.VirA_Isys,lo:=4364,hi:=4365);
Read_Real(rVar:=PMM.VirA_PFsys,lo:=4366,hi:=4367);
Read_Real(rVar:=PMM.VirA_Psys,lo:=4368,hi:=4369);
Read_Real(rVar:=PMM.VirA_Qsys,lo:=4370,hi:=4371);
Read_Real(rVar:=PMM.VirA_Ssys,lo:=4372,hi:=4373);
Read_Real(rVar:=PMM.VirA_Usys,lo:=4374,hi:=4375);
Read_Real(rVar:=PMM.VirB_fsys,lo:=4376,hi:=4377);
Read_Real(rVar:=PMM.VirB_Isys,lo:=4378,hi:=4379);
Read_Real(rVar:=PMM.VirB_PFsys,lo:=4380,hi:=4381);
Read_Real(rVar:=PMM.VirB_Psys,lo:=4382,hi:=4383);
Read_Real(rVar:=PMM.VirB_Qsys,lo:=4384,hi:=4385);
Read_Real(rVar:=PMM.VirB_Ssys,lo:=4386,hi:=4387);
Read_Real(rVar:=PMM.VirB_Usys,lo:=4388,hi:=4389);
Read_Real(rVar:=PMM.VirBActiveEnergyConsumed_kWh,lo:=4390,hi:=4391);
Read_Real(rVar:=PMM.VirBActivePowerPhaseA_kW,lo:=4392,hi:=4393);
Read_Real(rVar:=PMM.VirBActivePowerPhaseB_kW,lo:=4394,hi:=4395);
Read_Real(rVar:=PMM.VirBActivePowerPhaseC_kW,lo:=4396,hi:=4397);
Read_Real(rVar:=PMM.VirBAparentPowerPhaseA,lo:=4398,hi:=4399);
Read_Real(rVar:=PMM.VirBAparentPowerPhaseB,lo:=4400,hi:=4401);
Read_Real(rVar:=PMM.VirBAparentPowerPhaseC,lo:=4402,hi:=4403);
Read_Real(rVar:=PMM.VirBAverageCurrent_A,lo:=4404,hi:=4405);
Read_Real(rVar:=PMM.VirBAveragePhaseToNeutral_V,lo:=4406,hi:=4407);
Read_Real(rVar:=PMM.VirBAveragePhaseToPhase_V,lo:=4408,hi:=4409);
Read_Real(rVar:=PMM.VirBCurrentInPhaseA_A,lo:=4410,hi:=4411);
Read_Real(rVar:=PMM.VirBCurrentInPhaseB_A,lo:=4412,hi:=4413);
Read_Real(rVar:=PMM.VirBCurrentInPhaseC_A,lo:=4414,hi:=4415);
Read_Real(rVar:=PMM.VirBFrequency_Hz,lo:=4416,hi:=4417);
Read_Real(rVar:=PMM.VirBPowerFactorSys,lo:=4418,hi:=4419);
Read_Real(rVar:=PMM.VirBReactiveEnergyConsumed_kWh,lo:=4420,hi:=4421);
Read_Real(rVar:=PMM.VirBReactivePowerPhaseA,lo:=4422,hi:=4423);
Read_Real(rVar:=PMM.VirBReactivePowerPhaseB,lo:=4424,hi:=4425);
Read_Real(rVar:=PMM.VirBReactivePowerPhaseC,lo:=4426,hi:=4427);
Read_Real(rVar:=PMM.VirBTotalActivePower_kW,lo:=4428,hi:=4429);
Read_Real(rVar:=PMM.VirBTotalAparentPower_kVA,lo:=4430,hi:=4431);
Read_Real(rVar:=PMM.VirBTotalPowerFactor,lo:=4432,hi:=4433);
Read_Real(rVar:=PMM.VirBTotalReactivePower_kVAR,lo:=4434,hi:=4435);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseAB_V,lo:=4436,hi:=4437);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseAN_V,lo:=4438,hi:=4439);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseBC_V,lo:=4440,hi:=4441);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseBN_V,lo:=4442,hi:=4443);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseCA_V,lo:=4444,hi:=4445);
Read_Real(rVar:=PMM.VirBVoltageBetweenPhaseCN_V,lo:=4446,hi:=4447);
Read_Real(rVar:=PMM.VoltageBetweenPhaseAB_V,lo:=4448,hi:=4449);
Read_Real(rVar:=PMM.VoltageBetweenPhaseAN_V,lo:=4450,hi:=4451);
Read_Real(rVar:=PMM.VoltageBetweenPhaseBC_V,lo:=4452,hi:=4453);
Read_Real(rVar:=PMM.VoltageBetweenPhaseBN_V,lo:=4454,hi:=4455);
Read_Real(rVar:=PMM.VoltageBetweenPhaseCA_V,lo:=4456,hi:=4457);
Read_Real(rVar:=PMM.VoltageBetweenPhaseCN_V,lo:=4458,hi:=4459);
Read_Real(rVar:=SKTemp1,lo:=4460,hi:=4461);
Read_Real(rVar:=SKTemp2,lo:=4462,hi:=4463);
Read_Real(rVar:=SKTemp3,lo:=4464,hi:=4465);
Read_Real(rVar:=SKTempKontrSoba,lo:=4466,hi:=4467);
Read_Real(rVar:=SKTempLinkProstor,lo:=4468,hi:=4469);
Read_Real(rVar:=SKTempServSoba1Povpr,lo:=4470,hi:=4471);
Read_Real(rVar:=SKVlaga1,lo:=4472,hi:=4473);
Read_Real(rVar:=SKVlaga2,lo:=4474,hi:=4475);
Read_Real(rVar:=SKVlaga3,lo:=4476,hi:=4477);
Read_Real(rVar:=SKVlagaKontrSoba,lo:=4478,hi:=4479);
Read_Real(rVar:=SKVlagaLinkProstor,lo:=4480,hi:=4481);
Read_Real(rVar:=TempZaAlarmTIA123,lo:=4482,hi:=4483);
Read_Real(rVar:=TempZaAlarmTIA4,lo:=4484,hi:=4485);
Read_Real(rVar:=TempZaAlarmTIA5,lo:=4486,hi:=4487);
Read_Real(rVar:=TempZaVklopObehKlim,lo:=4488,hi:=4489);
(*Branje STRING*)
(**)
Read_String(sVar:=UserName,start:=5000);
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Bool : BOOL
VAR_INPUT
index: INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje BOOL*)
(**)
0:AlarmKlimat1_Napaka:=Bit_0;
1:AlarmKlimat2_Napaka:=Bit_0;
2:AlarmKlimat3_Napaka:=Bit_0;
3:AlarmLAH1_RazlitjeVode:=Bit_0;
4:AlarmLAH2_RazlitjeVode:=Bit_0;
5:AlarmSinhronizacijaNOK:=Bit_0;
6:AlarmSP1_Napaka:=Bit_0;
7:AlarmSP2_Napaka:=Bit_0;
8:AlarmSP3_Napaka:=Bit_0;
9:AlarmSP4_Napaka:=Bit_0;
10:AlarmSP5_Napaka:=Bit_0;
11:AlarmTempTIA123Previsoka:=Bit_0;
12:AlarmTempTIA4Previsoka:=Bit_0;
13:AlarmTempTIA5Previsoka:=Bit_0;
14:AlarmTSTempPrevisoka:=Bit_0;
15:AlarmUPSKrmOmara_Alarm:=Bit_0;
16:ComSCADA:=Bit_0;
17:ComSCADA1:=Bit_0;
18:ErrComKlima[1]:=Bit_0;
19:ErrComKlima[2]:=Bit_0;
20:ErrComKlima[3]:=Bit_0;
21:ErrCommScada:=Bit_0;
22:ErrComPanelPLC:=Bit_0;
23:ErrComPMM:=Bit_0;
24:ErrComPort2:=Bit_0;
25:Klima1_Onemogocena:=Bit_0;
26:Klima2_Onemogocena:=Bit_0;
27:Klima3_Onemogocena:=Bit_0;
28:Klima[1].IzhodniVentilator:=Bit_0;
29:Klima[1].Kompresor1:=Bit_0;
30:Klima[1].Kompresor2:=Bit_0;
31:Klima[1].Razvlazevanje:=Bit_0;
32:Klima[1].VentilGretjeOdpiranje:=Bit_0;
33:Klima[1].VentilGretjeZapiranje:=Bit_0;
34:Klima[1].Vlazenje:=Bit_0;
35:Klima[2].IzhodniVentilator:=Bit_0;
36:Klima[2].Kompresor1:=Bit_0;
37:Klima[2].Kompresor2:=Bit_0;
38:Klima[2].Razvlazevanje:=Bit_0;
39:Klima[2].VentilGretjeOdpiranje:=Bit_0;
40:Klima[2].VentilGretjeZapiranje:=Bit_0;
41:Klima[2].Vlazenje:=Bit_0;
42:Klima[3].IzhodniVentilator:=Bit_0;
43:Klima[3].Kompresor1:=Bit_0;
44:Klima[3].Kompresor2:=Bit_0;
45:Klima[3].Razvlazevanje:=Bit_0;
46:Klima[3].VentilGretjeOdpiranje:=Bit_0;
47:Klima[3].VentilGretjeZapiranje:=Bit_0;
48:Klima[3].Vlazenje:=Bit_0;
49:KlimaError[1].AlarmKompresor1:=Bit_0;
50:KlimaError[1].AlarmKompresor2:=Bit_0;
51:KlimaError[1].FenThermalCutout:=Bit_0;
52:KlimaError[1].IzlivVode:=Bit_0;
53:KlimaError[1].Kompresor1naMejiStevilaObrUr:=Bit_0;
54:KlimaError[1].Kompresor2naMejiStevilaObrUr:=Bit_0;
55:KlimaError[1].Kond1FenThermalCutout:=Bit_0;
56:KlimaError[1].Kond2FenThermalCutout:=Bit_0;
57:KlimaError[1].NapakaPriPretokuVode:=Bit_0;
58:KlimaError[1].NapakaPriPretokuZraka:=Bit_0;
59:KlimaError[1].NapakaSenzorPritiska:=Bit_0;
60:KlimaError[1].NapakaSenzorVlaznosti:=Bit_0;
61:KlimaError[1].NapakaTSTemperaturaProstora:=Bit_0;
62:KlimaError[1].NiTokaVVlazilcu:=Bit_0;
63:KlimaError[1].NiVodeVVlazilcu:=Bit_0;
64:KlimaError[1].NizekPritiskKompresor1:=Bit_0;
65:KlimaError[1].NizekPritiskKompresor2:=Bit_0;
66:KlimaError[1].NizkaTempVProstoru:=Bit_0;
67:KlimaError[1].NizkaVlaznost:=Bit_0;
68:KlimaError[1].PozarniAlarm:=Bit_0;
69:KlimaError[1].TermZascInVisokPritiskKompr1:=Bit_0;
70:KlimaError[1].TermZascInVisokPritiskKompr2:=Bit_0;
71:KlimaError[1].ThermalCutoutHeater1:=Bit_0;
72:KlimaError[1].ThermalCutoutHeater2:=Bit_0;
73:KlimaError[1].VentilatorNaMejiStevilaObrUr:=Bit_0;
74:KlimaError[1].VisokaTempVProstoru:=Bit_0;
75:KlimaError[1].VisokaVlaznost:=Bit_0;
76:KlimaError[1].VisokPritiskVKrogu1:=Bit_0;
77:KlimaError[1].VisokPritiskVKrogu2:=Bit_0;
78:KlimaError[1].VisokTokVVlazilcu:=Bit_0;
79:KlimaError[1].VlazilecnaMejiStevilaObrUr:=Bit_0;
80:KlimaError[1].ZamasenFilter:=Bit_0;
81:KlimaError[1].ZunanjiAlarm:=Bit_0;
82:KlimaError[2].AlarmKompresor1:=Bit_0;
83:KlimaError[2].AlarmKompresor2:=Bit_0;
84:KlimaError[2].FenThermalCutout:=Bit_0;
85:KlimaError[2].IzlivVode:=Bit_0;
86:KlimaError[2].Kompresor1naMejiStevilaObrUr:=Bit_0;
87:KlimaError[2].Kompresor2naMejiStevilaObrUr:=Bit_0;
88:KlimaError[2].Kond1FenThermalCutout:=Bit_0;
89:KlimaError[2].Kond2FenThermalCutout:=Bit_0;
90:KlimaError[2].NapakaPriPretokuVode:=Bit_0;
91:KlimaError[2].NapakaPriPretokuZraka:=Bit_0;
92:KlimaError[2].NapakaSenzorPritiska:=Bit_0;
93:KlimaError[2].NapakaSenzorVlaznosti:=Bit_0;
94:KlimaError[2].NapakaTSTemperaturaProstora:=Bit_0;
95:KlimaError[2].NiTokaVVlazilcu:=Bit_0;
96:KlimaError[2].NiVodeVVlazilcu:=Bit_0;
97:KlimaError[2].NizekPritiskKompresor1:=Bit_0;
98:KlimaError[2].NizekPritiskKompresor2:=Bit_0;
99:KlimaError[2].NizkaTempVProstoru:=Bit_0;
100:KlimaError[2].NizkaVlaznost:=Bit_0;
101:KlimaError[2].PozarniAlarm:=Bit_0;
102:KlimaError[2].TermZascInVisokPritiskKompr1:=Bit_0;
103:KlimaError[2].TermZascInVisokPritiskKompr2:=Bit_0;
104:KlimaError[2].ThermalCutoutHeater1:=Bit_0;
105:KlimaError[2].ThermalCutoutHeater2:=Bit_0;
106:KlimaError[2].VentilatorNaMejiStevilaObrUr:=Bit_0;
107:KlimaError[2].VisokaTempVProstoru:=Bit_0;
108:KlimaError[2].VisokaVlaznost:=Bit_0;
109:KlimaError[2].VisokPritiskVKrogu1:=Bit_0;
110:KlimaError[2].VisokPritiskVKrogu2:=Bit_0;
111:KlimaError[2].VisokTokVVlazilcu:=Bit_0;
112:KlimaError[2].VlazilecnaMejiStevilaObrUr:=Bit_0;
113:KlimaError[2].ZamasenFilter:=Bit_0;
114:KlimaError[2].ZunanjiAlarm:=Bit_0;
115:KlimaError[3].AlarmKompresor1:=Bit_0;
116:KlimaError[3].AlarmKompresor2:=Bit_0;
117:KlimaError[3].FenThermalCutout:=Bit_0;
118:KlimaError[3].IzlivVode:=Bit_0;
119:KlimaError[3].Kompresor1naMejiStevilaObrUr:=Bit_0;
120:KlimaError[3].Kompresor2naMejiStevilaObrUr:=Bit_0;
121:KlimaError[3].Kond1FenThermalCutout:=Bit_0;
122:KlimaError[3].Kond2FenThermalCutout:=Bit_0;
123:KlimaError[3].NapakaPriPretokuVode:=Bit_0;
124:KlimaError[3].NapakaPriPretokuZraka:=Bit_0;
125:KlimaError[3].NapakaSenzorPritiska:=Bit_0;
126:KlimaError[3].NapakaSenzorVlaznosti:=Bit_0;
127:KlimaError[3].NapakaTSTemperaturaProstora:=Bit_0;
128:KlimaError[3].NiTokaVVlazilcu:=Bit_0;
129:KlimaError[3].NiVodeVVlazilcu:=Bit_0;
130:KlimaError[3].NizekPritiskKompresor1:=Bit_0;
131:KlimaError[3].NizekPritiskKompresor2:=Bit_0;
132:KlimaError[3].NizkaTempVProstoru:=Bit_0;
133:KlimaError[3].NizkaVlaznost:=Bit_0;
134:KlimaError[3].PozarniAlarm:=Bit_0;
135:KlimaError[3].TermZascInVisokPritiskKompr1:=Bit_0;
136:KlimaError[3].TermZascInVisokPritiskKompr2:=Bit_0;
137:KlimaError[3].ThermalCutoutHeater1:=Bit_0;
138:KlimaError[3].ThermalCutoutHeater2:=Bit_0;
139:KlimaError[3].VentilatorNaMejiStevilaObrUr:=Bit_0;
140:KlimaError[3].VisokaTempVProstoru:=Bit_0;
141:KlimaError[3].VisokaVlaznost:=Bit_0;
142:KlimaError[3].VisokPritiskVKrogu1:=Bit_0;
143:KlimaError[3].VisokPritiskVKrogu2:=Bit_0;
144:KlimaError[3].VisokTokVVlazilcu:=Bit_0;
145:KlimaError[3].VlazilecnaMejiStevilaObrUr:=Bit_0;
146:KlimaError[3].ZamasenFilter:=Bit_0;
147:KlimaError[3].ZunanjiAlarm:=Bit_0;
148:NacDelovanjaKlime1_Avtomatsko:=Bit_0;
149:NacDelovanjaKlime2_3Avtomatsko:=Bit_0;
150:NapakaSenzorTemp1:=Bit_0;
151:NapakaSenzorTemp2:=Bit_0;
152:NapakaSenzorTemp3:=Bit_0;
153:NapakaSenzorTempKontrSoba:=Bit_0;
154:NapakaSenzorTempLinkProstor:=Bit_0;
155:NapakaSenzorVlaga1:=Bit_0;
156:NapakaSenzorVlaga2:=Bit_0;
157:NapakaSenzorVlaga3:=Bit_0;
158:NapakaSenzorVlagaKontrSoba:=Bit_0;
159:NapakaSenzorVlagaLinkProstor:=Bit_0;
160:NastaviCasNaKrmilniku:=Bit_0;
161:NastavitevUreKrUspesna:=Bit_0;
162:OpozoriloBaterijaPLC:=Bit_0;
163:PMM1OverCurrentBetw[1]:=Bit_0;
164:PMM1OverCurrentBetw[2]:=Bit_0;
165:PMM1OverCurrentBetw[3]:=Bit_0;
166:PMM1OverCurrentOver[1]:=Bit_0;
167:PMM1OverCurrentOver[2]:=Bit_0;
168:PMM1OverCurrentOver[3]:=Bit_0;
169:PMM1OverVoltage:=Bit_0;
170:RocniVklopKlima1:=Bit_0;
171:RocniVklopKlima2:=Bit_0;
172:RocniVklopKlima3:=Bit_0;
173:SinhronizacijaPanelOK:=Bit_0;
174:SinhronizirajCas_Panel:=Bit_0;
175:SkupneNapakeNaprav_Klima1:=Bit_0;
176:SkupneNapakeNaprav_Klima2:=Bit_0;
177:SkupneNapakeNaprav_Klima3:=Bit_0;
178:SkupneNapakeNaprav_Komunikacija:=Bit_0;
179:SkupneNapakeNaprav_PMMVirA:=Bit_0;
180:SkupneNapakeNaprav_PMMVirB:=Bit_0;
181:SkupneNapakeNaprav_PMMVirBVirA:=Bit_0;
182:SkupneNapakeNaprav_TempVlaga:=Bit_0;
183:StanjeKlimat1_Delovanje:=Bit_0;
184:StanjeKlimat2_Delovanje:=Bit_0;
185:StanjeKlimat3_Delovanje:=Bit_0;
186:StanjeSP1_Delovanje:=Bit_0;
187:StanjeSP2_Delovanje:=Bit_0;
188:StanjeSP3_Delovanje:=Bit_0;
189:StanjeSP4_Delovanje:=Bit_0;
190:StanjeSP5_Delovanje:=Bit_0;
191:StanjeUPSKrmOmara_BaterijskiNacin:=Bit_0;
192:StanjeUPSKrmOmara_Polnenje:=Bit_0;
193:UserLoggedIn:=Bit_0;
194:XVH_AlarmOn:=Bit_0;
195:Klimat1_Vklop:=Bit_0;
196:Klimat2_Vklop:=Bit_0;
197:Klimat3_Vklop:=Bit_0;
198:ErrCommScada2:=Bit_0;
199:ComSCADA2:=Bit_0;
200:ComSCADA3:=Bit_0;
(*BOOL*)
END_CASE
END_FUNCTION
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_dWord : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje LONG*)
(**)
(*Pisanje REAL*)
(**)
4001:AktualniSetPointTemp:=Real_0;
4003:AktualniSetPointVlaga:=Real_0;
4005:Klima[1].NastMaxTemp:=Real_0;
4007:Klima[1].NastMaxVlaznost:=Real_0;
4009:Klima[1].NastMinTemp:=Real_0;
4011:Klima[1].NastMinVlaznost:=Real_0;
4013:Klima[1].NastTempProstora:=Real_0;
4015:Klima[1].NastVlaznost:=Real_0;
4017:Klima[1].Pritisk:=Real_0;
4019:Klima[1].TemperaturaProstora:=Real_0;
4021:Klima[1].VlaznostProstora:=Real_0;
4023:Klima[2].NastMaxTemp:=Real_0;
4025:Klima[2].NastMaxVlaznost:=Real_0;
4027:Klima[2].NastMinTemp:=Real_0;
4029:Klima[2].NastMinVlaznost:=Real_0;
4031:Klima[2].NastTempProstora:=Real_0;
4033:Klima[2].NastVlaznost:=Real_0;
4035:Klima[2].Pritisk:=Real_0;
4037:Klima[2].TemperaturaProstora:=Real_0;
4039:Klima[2].VlaznostProstora:=Real_0;
4041:Klima[3].NastMaxTemp:=Real_0;
4043:Klima[3].NastMaxVlaznost:=Real_0;
4045:Klima[3].NastMinTemp:=Real_0;
4047:Klima[3].NastMinVlaznost:=Real_0;
4049:Klima[3].NastTempProstora:=Real_0;
4051:Klima[3].NastVlaznost:=Real_0;
4053:Klima[3].Pritisk:=Real_0;
4055:Klima[3].TemperaturaProstora:=Real_0;
4057:Klima[3].VlaznostProstora:=Real_0;
4059:ObratUreKlim[1]:=Real_0;
4061:ObratUreKlim[2]:=Real_0;
4063:ObratUreKlim[3]:=Real_0;
4065:PMM.ActiveEnergyConsumed_kWh:=Real_0;
4067:PMM.ActivePowerPhaseA_kW:=Real_0;
4069:PMM.ActivePowerPhaseB_kW:=Real_0;
4071:PMM.ActivePowerPhaseC_kW:=Real_0;
4073:PMM.AparentPowerPhaseA:=Real_0;
4075:PMM.AparentPowerPhaseB:=Real_0;
4077:PMM.AparentPowerPhaseC:=Real_0;
4079:PMM.AverageCurrent_A:=Real_0;
4081:PMM.AveragePhaseToNeutral_V:=Real_0;
4083:PMM.AveragePhaseToPhase_V:=Real_0;
4085:PMM.CurrentInPhaseA_A:=Real_0;
4087:PMM.CurrentInPhaseB_A:=Real_0;
4089:PMM.CurrentInPhaseC_A:=Real_0;
4091:PMM.Frequency_Hz:=Real_0;
4093:PMM.Phase[1].Current[10]:=Real_0;
4095:PMM.Phase[1].Current[11]:=Real_0;
4097:PMM.Phase[1].Current[12]:=Real_0;
4099:PMM.Phase[1].Current[13]:=Real_0;
4101:PMM.Phase[1].Current[14]:=Real_0;
4103:PMM.Phase[1].Current[15]:=Real_0;
4105:PMM.Phase[1].Current[16]:=Real_0;
4107:PMM.Phase[1].Current[17]:=Real_0;
4109:PMM.Phase[1].Current[18]:=Real_0;
4111:PMM.Phase[1].Current[19]:=Real_0;
4113:PMM.Phase[1].Current[1]:=Real_0;
4115:PMM.Phase[1].Current[20]:=Real_0;
4117:PMM.Phase[1].Current[21]:=Real_0;
4119:PMM.Phase[1].Current[22]:=Real_0;
4121:PMM.Phase[1].Current[23]:=Real_0;
4123:PMM.Phase[1].Current[24]:=Real_0;
4125:PMM.Phase[1].Current[25]:=Real_0;
4127:PMM.Phase[1].Current[26]:=Real_0;
4129:PMM.Phase[1].Current[27]:=Real_0;
4131:PMM.Phase[1].Current[28]:=Real_0;
4133:PMM.Phase[1].Current[29]:=Real_0;
4135:PMM.Phase[1].Current[2]:=Real_0;
4137:PMM.Phase[1].Current[30]:=Real_0;
4139:PMM.Phase[1].Current[31]:=Real_0;
4141:PMM.Phase[1].Current[32]:=Real_0;
4143:PMM.Phase[1].Current[33]:=Real_0;
4145:PMM.Phase[1].Current[34]:=Real_0;
4147:PMM.Phase[1].Current[35]:=Real_0;
4149:PMM.Phase[1].Current[36]:=Real_0;
4151:PMM.Phase[1].Current[37]:=Real_0;
4153:PMM.Phase[1].Current[38]:=Real_0;
4155:PMM.Phase[1].Current[39]:=Real_0;
4157:PMM.Phase[1].Current[3]:=Real_0;
4159:PMM.Phase[1].Current[40]:=Real_0;
4161:PMM.Phase[1].Current[41]:=Real_0;
4163:PMM.Phase[1].Current[42]:=Real_0;
4165:PMM.Phase[1].Current[4]:=Real_0;
4167:PMM.Phase[1].Current[5]:=Real_0;
4169:PMM.Phase[1].Current[6]:=Real_0;
4171:PMM.Phase[1].Current[7]:=Real_0;
4173:PMM.Phase[1].Current[8]:=Real_0;
4175:PMM.Phase[1].Current[9]:=Real_0;
4177:PMM.Phase[2].Current[10]:=Real_0;
4179:PMM.Phase[2].Current[11]:=Real_0;
4181:PMM.Phase[2].Current[12]:=Real_0;
4183:PMM.Phase[2].Current[13]:=Real_0;
4185:PMM.Phase[2].Current[14]:=Real_0;
4187:PMM.Phase[2].Current[15]:=Real_0;
4189:PMM.Phase[2].Current[16]:=Real_0;
4191:PMM.Phase[2].Current[17]:=Real_0;
4193:PMM.Phase[2].Current[18]:=Real_0;
4195:PMM.Phase[2].Current[19]:=Real_0;
4197:PMM.Phase[2].Current[1]:=Real_0;
4199:PMM.Phase[2].Current[20]:=Real_0;
4201:PMM.Phase[2].Current[21]:=Real_0;
4203:PMM.Phase[2].Current[22]:=Real_0;
4205:PMM.Phase[2].Current[23]:=Real_0;
4207:PMM.Phase[2].Current[24]:=Real_0;
4209:PMM.Phase[2].Current[25]:=Real_0;
4211:PMM.Phase[2].Current[26]:=Real_0;
4213:PMM.Phase[2].Current[27]:=Real_0;
4215:PMM.Phase[2].Current[28]:=Real_0;
4217:PMM.Phase[2].Current[29]:=Real_0;
4219:PMM.Phase[2].Current[2]:=Real_0;
4221:PMM.Phase[2].Current[30]:=Real_0;
4223:PMM.Phase[2].Current[31]:=Real_0;
4225:PMM.Phase[2].Current[32]:=Real_0;
4227:PMM.Phase[2].Current[33]:=Real_0;
4229:PMM.Phase[2].Current[34]:=Real_0;
4231:PMM.Phase[2].Current[35]:=Real_0;
4233:PMM.Phase[2].Current[36]:=Real_0;
4235:PMM.Phase[2].Current[37]:=Real_0;
4237:PMM.Phase[2].Current[38]:=Real_0;
4239:PMM.Phase[2].Current[39]:=Real_0;
4241:PMM.Phase[2].Current[3]:=Real_0;
4243:PMM.Phase[2].Current[40]:=Real_0;
4245:PMM.Phase[2].Current[41]:=Real_0;
4247:PMM.Phase[2].Current[42]:=Real_0;
4249:PMM.Phase[2].Current[4]:=Real_0;
4251:PMM.Phase[2].Current[5]:=Real_0;
4253:PMM.Phase[2].Current[6]:=Real_0;
4255:PMM.Phase[2].Current[7]:=Real_0;
4257:PMM.Phase[2].Current[8]:=Real_0;
4259:PMM.Phase[2].Current[9]:=Real_0;
4261:PMM.Phase[3].Current[10]:=Real_0;
4263:PMM.Phase[3].Current[11]:=Real_0;
4265:PMM.Phase[3].Current[12]:=Real_0;
4267:PMM.Phase[3].Current[13]:=Real_0;
4269:PMM.Phase[3].Current[14]:=Real_0;
4271:PMM.Phase[3].Current[15]:=Real_0;
4273:PMM.Phase[3].Current[16]:=Real_0;
4275:PMM.Phase[3].Current[17]:=Real_0;
4277:PMM.Phase[3].Current[18]:=Real_0;
4279:PMM.Phase[3].Current[19]:=Real_0;
4281:PMM.Phase[3].Current[1]:=Real_0;
4283:PMM.Phase[3].Current[20]:=Real_0;
4285:PMM.Phase[3].Current[21]:=Real_0;
4287:PMM.Phase[3].Current[22]:=Real_0;
4289:PMM.Phase[3].Current[23]:=Real_0;
4291:PMM.Phase[3].Current[24]:=Real_0;
4293:PMM.Phase[3].Current[25]:=Real_0;
4295:PMM.Phase[3].Current[26]:=Real_0;
4297:PMM.Phase[3].Current[27]:=Real_0;
4299:PMM.Phase[3].Current[28]:=Real_0;
4301:PMM.Phase[3].Current[29]:=Real_0;
4303:PMM.Phase[3].Current[2]:=Real_0;
4305:PMM.Phase[3].Current[30]:=Real_0;
4307:PMM.Phase[3].Current[31]:=Real_0;
4309:PMM.Phase[3].Current[32]:=Real_0;
4311:PMM.Phase[3].Current[33]:=Real_0;
4313:PMM.Phase[3].Current[34]:=Real_0;
4315:PMM.Phase[3].Current[35]:=Real_0;
4317:PMM.Phase[3].Current[36]:=Real_0;
4319:PMM.Phase[3].Current[37]:=Real_0;
4321:PMM.Phase[3].Current[38]:=Real_0;
4323:PMM.Phase[3].Current[39]:=Real_0;
4325:PMM.Phase[3].Current[3]:=Real_0;
4327:PMM.Phase[3].Current[40]:=Real_0;
4329:PMM.Phase[3].Current[41]:=Real_0;
4331:PMM.Phase[3].Current[42]:=Real_0;
4333:PMM.Phase[3].Current[4]:=Real_0;
4335:PMM.Phase[3].Current[5]:=Real_0;
4337:PMM.Phase[3].Current[6]:=Real_0;
4339:PMM.Phase[3].Current[7]:=Real_0;
4341:PMM.Phase[3].Current[8]:=Real_0;
4343:PMM.Phase[3].Current[9]:=Real_0;
4345:PMM.PowerFactorSys:=Real_0;
4347:PMM.ReactiveEnergyConsumed_kVARh:=Real_0;
4349:PMM.ReactivePowerPhaseA:=Real_0;
4351:PMM.ReactivePowerPhaseB:=Real_0;
4353:PMM.ReactivePowerPhaseC:=Real_0;
4355:PMM.TotalActivePower_kW:=Real_0;
4357:PMM.TotalAparentPower_kVA:=Real_0;
4359:PMM.TotalPowerFactor:=Real_0;
4361:PMM.TotalReactivePower_kVAR:=Real_0;
4363:PMM.VirA_fsys:=Real_0;
4365:PMM.VirA_Isys:=Real_0;
4367:PMM.VirA_PFsys:=Real_0;
4369:PMM.VirA_Psys:=Real_0;
4371:PMM.VirA_Qsys:=Real_0;
4373:PMM.VirA_Ssys:=Real_0;
4375:PMM.VirA_Usys:=Real_0;
4377:PMM.VirB_fsys:=Real_0;
4379:PMM.VirB_Isys:=Real_0;
4381:PMM.VirB_PFsys:=Real_0;
4383:PMM.VirB_Psys:=Real_0;
4385:PMM.VirB_Qsys:=Real_0;
4387:PMM.VirB_Ssys:=Real_0;
4389:PMM.VirB_Usys:=Real_0;
4391:PMM.VirBActiveEnergyConsumed_kWh:=Real_0;
4393:PMM.VirBActivePowerPhaseA_kW:=Real_0;
4395:PMM.VirBActivePowerPhaseB_kW:=Real_0;
4397:PMM.VirBActivePowerPhaseC_kW:=Real_0;
4399:PMM.VirBAparentPowerPhaseA:=Real_0;
4401:PMM.VirBAparentPowerPhaseB:=Real_0;
4403:PMM.VirBAparentPowerPhaseC:=Real_0;
4405:PMM.VirBAverageCurrent_A:=Real_0;
4407:PMM.VirBAveragePhaseToNeutral_V:=Real_0;
4409:PMM.VirBAveragePhaseToPhase_V:=Real_0;
4411:PMM.VirBCurrentInPhaseA_A:=Real_0;
4413:PMM.VirBCurrentInPhaseB_A:=Real_0;
4415:PMM.VirBCurrentInPhaseC_A:=Real_0;
4417:PMM.VirBFrequency_Hz:=Real_0;
4419:PMM.VirBPowerFactorSys:=Real_0;
4421:PMM.VirBReactiveEnergyConsumed_kWh:=Real_0;
4423:PMM.VirBReactivePowerPhaseA:=Real_0;
4425:PMM.VirBReactivePowerPhaseB:=Real_0;
4427:PMM.VirBReactivePowerPhaseC:=Real_0;
4429:PMM.VirBTotalActivePower_kW:=Real_0;
4431:PMM.VirBTotalAparentPower_kVA:=Real_0;
4433:PMM.VirBTotalPowerFactor:=Real_0;
4435:PMM.VirBTotalReactivePower_kVAR:=Real_0;
4437:PMM.VirBVoltageBetweenPhaseAB_V:=Real_0;
4439:PMM.VirBVoltageBetweenPhaseAN_V:=Real_0;
4441:PMM.VirBVoltageBetweenPhaseBC_V:=Real_0;
4443:PMM.VirBVoltageBetweenPhaseBN_V:=Real_0;
4445:PMM.VirBVoltageBetweenPhaseCA_V:=Real_0;
4447:PMM.VirBVoltageBetweenPhaseCN_V:=Real_0;
4449:PMM.VoltageBetweenPhaseAB_V:=Real_0;
4451:PMM.VoltageBetweenPhaseAN_V:=Real_0;
4453:PMM.VoltageBetweenPhaseBC_V:=Real_0;
4455:PMM.VoltageBetweenPhaseBN_V:=Real_0;
4457:PMM.VoltageBetweenPhaseCA_V:=Real_0;
4459:PMM.VoltageBetweenPhaseCN_V:=Real_0;
4461:SKTemp1:=Real_0;
4463:SKTemp2:=Real_0;
4465:SKTemp3:=Real_0;
4467:SKTempKontrSoba:=Real_0;
4469:SKTempLinkProstor:=Real_0;
4471:SKTempServSoba1Povpr:=Real_0;
4473:SKVlaga1:=Real_0;
4475:SKVlaga2:=Real_0;
4477:SKVlaga3:=Real_0;
4479:SKVlagaKontrSoba:=Real_0;
4481:SKVlagaLinkProstor:=Real_0;
4483:TempZaAlarmTIA123:=Real_0;
4485:TempZaAlarmTIA4:=Real_0;
4487:TempZaAlarmTIA5:=Real_0;
4489:TempZaVklopObehKlim:=Real_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_String : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje STRING*)
(**)
5000:UserName:=String_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Word : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje INT*)
(**)
0:DatumCas.Dan:=Byte_0;
1:DatumCas.Leto:=Byte_0;
2:DatumCas.Leto2:=Word_01;
3:DatumCas.Mesec:=Byte_0;
4:DatumCas.Minuta:=Byte_0;
5:DatumCas.Sekunda:=Byte_0;
6:DatumCas.Ura:=Byte_0;
7:Klima[1].Vlazilec_Stanja:=Byte_0;
8:Klima[2].Vlazilec_Stanja:=Byte_0;
9:Klima[3].Vlazilec_Stanja:=Byte_0;
10:StUrZaPreklopKlim:=Word_01;
11:UPSstatus_Prikaz_PanelSCADA:=Byte_0;
12:UserCurrentLevel:=Byte_0;
(*Pisanje UINT*)
(**)
6000:PMM.AlarmPhase[1].C01_16_60to80:=Word_01;
6001:PMM.AlarmPhase[1].C01_16_over80:=Word_01;
6002:PMM.AlarmPhase[1].C17_32_60to80:=Word_01;
6003:PMM.AlarmPhase[1].C17_32_over80:=Word_01;
6004:PMM.AlarmPhase[1].C33_42_60to80:=Word_01;
6005:PMM.AlarmPhase[1].C33_42_over80:=Word_01;
6006:PMM.AlarmPhase[2].C01_16_60to80:=Word_01;
6007:PMM.AlarmPhase[2].C01_16_over80:=Word_01;
6008:PMM.AlarmPhase[2].C17_32_60to80:=Word_01;
6009:PMM.AlarmPhase[2].C17_32_over80:=Word_01;
6010:PMM.AlarmPhase[2].C33_42_60to80:=Word_01;
6011:PMM.AlarmPhase[2].C33_42_over80:=Word_01;
6012:PMM.AlarmPhase[3].C01_16_60to80:=Word_01;
6013:PMM.AlarmPhase[3].C01_16_over80:=Word_01;
6014:PMM.AlarmPhase[3].C17_32_60to80:=Word_01;
6015:PMM.AlarmPhase[3].C17_32_over80:=Word_01;
6016:PMM.AlarmPhase[3].C33_42_60to80:=Word_01;
6017:PMM.AlarmPhase[3].C33_42_over80:=Word_01;
6018:kom_nast_cas_izpada:=Word_01;
;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
(*Modbus Slave Example*)
PROGRAM PLC_PRG_modnet
VAR
Slave_Adresa:BYTE:=2;
Slave_Port:INT:=502;
SlaveSetup:MBS_Setup;
SlavePoll:MBS_Poll;
SlaveAnswer:MBS_Answer;
step: USINT;
end :BOOL;
i: INT;
cycle :BOOL := FALSE; (* First cycle *)
OpenDefaultPort: BOOL;
Write_16: BOOL;
Write_15: BOOL;
Write_5: BOOL;
j: INT;
slavepollwOffset_temp: INT;
slaveanswerwCount_temp: INT;
slaveanswerwoffset_temp: INT;
END_VAR
(* @END_DECLARATION := '0' *)
(*Modbus Slave Example*)
IF Write_16=TRUE THEN (**)
FOR j := 0 TO (slaveanswerwCount_temp-1)/15 BY 1 DO (*vpiše se dword, real*)
wStr_0:=mind[slaveanswerwoffset_temp+j];
wStr_1:=mind[slaveanswerwoffset_temp+j+1];
wStr_2 :=mind[slaveanswerwoffset_temp+j+2];
wStr_3:=mind[slaveanswerwoffset_temp+j+3];
wStr_4:=mind[slaveanswerwoffset_temp+j+4];
wStr_5 :=mind[slaveanswerwoffset_temp+j+5];
wStr_6:=mind[slaveanswerwoffset_temp+j+6];
wStr_7:=mind[slaveanswerwoffset_temp+j+7];
wStr_8:=mind[slaveanswerwoffset_temp+j+8];
wStr_9:=mind[slaveanswerwoffset_temp+j+9];
wStr_10:=mind[slaveanswerwoffset_temp+j+10];
wStr_11:=mind[slaveanswerwoffset_temp+j+11];
wStr_12:=mind[slaveanswerwoffset_temp+j+12];
wStr_13:=mind[slaveanswerwoffset_temp+j+13];
wStr_14:=mind[slaveanswerwoffset_temp+j+14];
bStr_29:=0;
mod_Write_String(index:=slaveanswerwoffset_temp+j); (*vpis real in string*)
END_FOR;
FOR j := 1 TO slaveanswerwCount_temp-1 BY 2 DO (*vpiše se dword, real*)
Word_01:=mind[slaveanswerwoffset_temp+j-1];
Word_23:=mind[slaveanswerwoffset_temp+j];
mod_Write_dWord(index:=slaveanswerwoffset_temp+j); (*vpis real in dword*)
END_FOR;
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO (*vpiše se word*)
Word_01:=mind[slaveanswerwoffset_temp+j];
mod_Write_Word(index:=slaveanswerwoffset_temp+j); (*vpis word*)
END_FOR;
Write_16:=FALSE;
END_IF;
IF Write_5=TRUE OR Write_15=TRUE THEN (**)
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO
Bit_0:=mind_bool[slaveanswerwoffset_temp+j];
mod_Write_Bool(index:=slaveanswerwoffset_temp+j); (*vpis spremembe v spremenljivko*)
END_FOR;
Write_5:=FALSE;
Write_15:=FALSE;
END_IF;
(*iz scade ni komande za branje*)
IF Write_16=FALSE AND Write_5=FALSE AND Write_15=FALSE THEN
mod_Read();(*branje spremenljivk za scado*)
END_IF
(*Close all sockets on corresponding event*)
IF cycle = FALSE THEN
SysCallbackRegister(INDEXOF(Callback_Stop),event_stop);
SysCallbackRegister(INDEXOF(Callback_Reset),event_before_reset);
SysCallbackRegister(INDEXOF(Callback_Reset),event_shutdown);
cycle := TRUE;
END_IF
(*Close all connections via application *)
IF end = TRUE THEN
MBS_CloseAllConnections();
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=FALSE); (*Close port*)
step := 0;
END_IF
IF OpenDefaultPort=TRUE THEN
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=TRUE); (*Close port*)
step := 0;
OpenDefaultPort:=FALSE;
END_IF
(* State machine for setup, poll and answer *)
CASE step OF
0:(**)
SlaveSetup.bUnitIdentifier:=Slave_Adresa;(*Subunitnumber*)
slavesetup.wDefaultPort:=Slave_Port;(*Standartport *)
SlaveSetup.xAdditionalPortActive:=FALSE;(*Port opened or closed*)
SlaveSetup.xSecureMode:=FALSE;(*If TRUE only preset IPs are accepted*)
SlaveSetup.tTimeout:=T#3m;(*Timeout if no communication with slave established*)
SlaveSetup(xStrobe:=TRUE);(*Strobe starts function*)
IF slavesetup.xBusy = FALSE THEN
slavesetup(xstrobe := FALSE);
step := 1 ;
END_IF;
1:(**)
SlavePoll(xStrobe:=TRUE);(*Searching for master commands*)
IF NOT SlavePoll.xBusy THEN
step:=2;
SlavePoll(xStrobe:=FALSE);
END_IF;
2:(**)
step:= 1;
CASE SlavePoll.bFunctionCode OF (*Connect accepted pollparameters with answerparameters*)
8:(**)(*Poll answers*)
;
15:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind_bool[slaveanswer.woffset+i] := slavepoll.xarData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.xarData:=slavepoll.xarData;
Write_15:=TRUE;
16:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind[slaveanswer.woffset+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.wardata := slavepoll.warData;
Write_16:=TRUE;
1,2:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slavepoll.wcount-1 BY 1 DO
slaveanswer.xarData[i]:=mind_bool[slavepoll.woffset+i]; (*Read from Data-array*)
END_FOR
3,4:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slaveanswer.wCount-1 BY 1 DO
slaveanswer.warData[i]:=mind[slavepoll.woffset+i];(*Read from Data-array*)
END_FOR
5:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
mind_bool[slavepoll.woffset]:=slavepoll.xarData[0];(*Write to Data-array*)
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.xarData := slavepoll.xardata;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
Write_5:=TRUE;
6:
slaveanswer.bFunctionCode:= slavepoll.bFunctionCode;
mind[slavepoll.woffset]:= slavepoll.warData[0];(*Write to Data-array*)
slaveanswer.wOffset:= slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wardata := slavepoll.wardata;
23:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
FOR i:= 0 TO slavepoll.wCountAdd-1 BY 1 DO
mind[slavepoll.woffsetadd+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
FOR i := 0 TO slavepoll.wCount BY 1 DO
slaveanswer.warData[i] := mind[1+slavepoll.woffset+i];(*Read from Data-array*)
END_FOR;
END_CASE;
IF slavepoll.xAvailable = TRUE THEN
slaveanswer();(*When Data ready, send answer*)
END_IF
END_CASE;
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_dWord : BOOL
VAR_INPUT
dVAR: DWORD;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
DWord_0:=dVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_Real : BOOL
VAR_INPUT
rVAR: REAL;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
Real_0:=rVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_String : BOOL
VAR_INPUT
sVar: STRING;
start:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
String_0:=LEFT (sVar,29);
mind[start]:=wStr_0;
mind[start+1]:=wStr_1;
mind[start+2]:=wStr_2;
mind[start+3]:=wStr_3;
mind[start+4]:=wStr_4;
mind[start+5]:=wStr_5;
mind[start+6]:=wStr_6;
mind[start+7]:=wStr_7;
mind[start+8]:=wStr_8;
mind[start+9]:=wStr_9;
mind[start+10]:=wStr_10;
mind[start+11]:=wStr_11;
mind[start+12]:=wStr_12;
mind[start+13]:=wStr_13;
bStr_29:=0;
mind[start+14]:=wStr_14;
END_FUNCTION
(* @GLOBAL_VARIABLE_LIST := 'Global_Variables_Modnet' *)
(* @PATH := '' *)
(* @SYMFILEFLAGS := '2048' *)
VAR_GLOBAL
(*delovno polje za modnet komunikacijo*)
mind :ARRAY [0..9999] OF WORD;
mind_bool :ARRAY [0..9999] OF BOOL; (*Buffer-Array*)
(*Delovni markerji //*)
Bit_0 AT %MX0.0 : BOOL;
Byte_0 AT %MB0 : BYTE;
Byte_1 AT %MB1 : BYTE;
Byte_2 AT %MB2 : BYTE;
Byte_3 AT %MB3 : BYTE;
Real_0 AT %MR0:REAL;
DWord_0 AT %MD0:DWORD;
Word_01 AT %MW0:WORD;
Word_23 AT %MW2:WORD;
String_0 AT %MW10:STRING;
wStr_0 AT %MW10:WORD;
wStr_1 AT %MW12:WORD;
wStr_2 AT %MW14:WORD;
wStr_3 AT %MW16:WORD;
wStr_4 AT %MW18:WORD;
wStr_5 AT %MW20:WORD;
wStr_6 AT %MW22:WORD;
wStr_7 AT %MW24:WORD;
wStr_8 AT %MW26:WORD;
wStr_9 AT %MW28:WORD;
wStr_10 AT %MW30:WORD;
wStr_11 AT %MW32:WORD;
wStr_12 AT %MW34:WORD;
wStr_13 AT %MW36:WORD;
wStr_14 AT %MW38:WORD;
bStr_00 AT %MB10:BYTE;
bStr_01 AT %MB11:BYTE;
bStr_02 AT %MB12:BYTE;
bStr_03 AT %MB13:BYTE;
bStr_04 AT %MB14:BYTE;
bStr_05 AT %MB15:BYTE;
bStr_06 AT %MB16:BYTE;
bStr_07 AT %MB17:BYTE;
bStr_08 AT %MB18:BYTE;
bStr_09 AT %MB19:BYTE;
bStr_10 AT %MB20:BYTE;
bStr_11 AT %MB21:BYTE;
bStr_12 AT %MB22:BYTE;
bStr_13 AT %MB23:BYTE;
bStr_14 AT %MB24:BYTE;
bStr_15 AT %MB25:BYTE;
bStr_16 AT %MB26:BYTE;
bStr_17 AT %MB27:BYTE;
bStr_18 AT %MB28:BYTE;
bStr_19 AT %MB29:BYTE;
bStr_20 AT %MB30:BYTE;
bStr_21 AT %MB31:BYTE;
bStr_22 AT %MB32:BYTE;
bStr_23 AT %MB33:BYTE;
bStr_24 AT %MB34:BYTE;
bStr_25 AT %MB35:BYTE;
bStr_26 AT %MB36:BYTE;
bStr_27 AT %MB37:BYTE;
bStr_28 AT %MB38:BYTE;
bStr_29 AT %MB39:BYTE;
(********************************************)
END_VAR
(* @OBJECT_END := 'Global_Variables_Modnet' *)
(* @CONNECTIONS := Global_Variables_Modnet
FILENAME : ''
FILETIME : 0
EXPORT : 0
NUMOFCONNECTIONS : 0
*)
(*KONEC_KODA*)