## Prva stran
variable | 2437 | 1.KORAK | variable_1 | 2.KORAK | KORAKI!
Device name | Tip | število spremenljivk | Tip (izbrani) | Zamenjaj z | 1.V Sheet "variable" skopiraj vsebino iz variable.dbf - iz Citect SCAD-a projekta, ki ga želiš pretvoriti.
IOD_SS2 | BCD | 0 | BCD | INT | 2.V polje A3 vpiši Device ime spremenljivk ki se bodo prenašale preko Modnet protokola
| BYTE | 229 | BYTE | BYTE | 3.V polje A6 vpiši ime krmilnika (npr.:PLC1, če je adresa v spremenljivkah PLC1:.NapakaKoncnega_stikala, drugače pusti polje prazno)
OPC name | DIGITAL | 409 | DIGITAL | DIGITAL | 4. Pritisni gumb 1.KORAK (V poljih C3:C10 se izpiše število spremenljivk, ki imajo Device enak tistemu v polju A3)
SS2 | INT | 28 | INT | INT | 5. Pritisni gumb 2.KORAK (V Sheet-u variable_1 se naredi seznam spremenljivk, ki se bodo prenačale preko Modnet protokola)
| LONG | 0 | LONG | LONG | 6. Pritisni gumb 3.KORAK (V poljih C15:C24 se izpiše število spremnljiv po tipih, v poljih F15:F24 se izpiše število potrebni wordow/coilov za prenos spremnljivk)
| REAL | 579 | REAL | REAL | 7. 4.KORAK: V polja C29:C38 je potrebno ročno vpisati začetne naslove spremnljivk. Potrebno je paziti na:
| STRING | 5 | UINT | UINT | *naslov se morajo začeti z lihim številom npr.:1, 101, 551
| UINT | 0 | STRING | STRING | *naslove je potrebno nastaviti tako, da se naslovi sremenljivk ne more prekrivati (naslovi spremenjivk gredo od (začetnega naslova) do (začetnega naslova+število potrebnih wordow))
8. Pritisni gumb 5.KORAK (V Sheet-u variable_2 se naredi seznam spremenljivk, ki so tokrat sortirana po tipih)
9. Pritisni gumb 6.KORAK (V Sheet-u variable_3 se naredi seznam spremenljivk, katerih Device se zamenja z devicom v polju C41)
Trajanje makroja | variable_1 |  |  | 3.KORAK | 10. Pritisni gumb 7.KORAK (V Sheet-u variable_new se generira seznam spremenljivk. To vsebino je potrebno skopirati v variable.dbf)
0 | Tip | število spremenljivk | TIP | št.potrebnih coilov/wordov | *ta korak traja nekoliko dalj časa (odvisno od števila spremenljivk)
| BCD | 0 | BCD | 0 | *če se pojavi težava z adresami ki se začnejo z 0000 (npr.: "00001" se spremeni na "1") je potrebno uporabiti priloženo (prazno) variable.dbf ali v
| BYTE | 0 | BYTE | 0 | ProjectEditoju/VariableTags na poljubni spremenljki nastaviti adreso" 00001"
| DIGITAL | 409 | DIGITAL | 409 (Coil) | 11. Pritisni gumb 8.KORAK in 9.KORAK (V Sheet-u Xsoft se generira koda)
| INT | 257 | INT | 257 (word) | 12. S pritiskom na gumb 10.KORAK se zgenerira EXP koda za Xsoft (Xsoft_EXP)
| LONG | 0 | LONG | 0 (word) | 13. S pritiskom na gumb Save*.EXP se avtomatsko generira datoka *.EXP
| REAL | 579 | REAL | 1158 (word)
| STRING | 5 | STRING | 75 (word)
| UINT | 0 | UINT | 0 (word)
POZOR!
*V Sheet-u variable mora biti vsebina skopirana od polja A1 naprej (če je katera vrstica prazna makroji ne bodo delovali pravilno)
*Ena "STRING" spremenljivka zasede 15wordow (to pomeni 29 znakov, 1BYTE=1STRING)
|  | 4.KORAK(vpiši ročno) | variable_2 | 5.KORAK | *Dolžina "STRING" spremenljivk je 29 znakov (lahko tudi več vendar ne z uporabno tega dokumenta in XSoft programa,potrebna je modifikacija makrojev in Xsoft programa)
| Tip | Začetni naslov |  | Sortiraj | *Vsi stringi so enake dolžine (29)
| BCD |  |  | BCD | *"BYTE" spremenljivke se v variable.dbf spremenijo v "INT" (prenašanje posameznih bytov ni mogoče, niti naslavaljanje v citectscadi)
| BYTE |  |  | DIGITAL | *Naslovi spremenljivk se morajo obvezno začeti z lihim naslovom (preizkušeno je z začetnimi naslovi, ki se izpišejo po pritisku na gumb Ponastavi)
| DIGITAL | 1 |  | BYTE | *Z pritiskom na gumb RESET se pobriše vsebina vseh Sheet-ov razen Sheet-a variable (makor reset se izvaja precej časa)
| INT | 1 |  | INT | *makroji ne delujejo pravilno,če je v Sheet-u variable več kot 9999 vrstic oz. spremenljivk (število vseh spremnljivk je prikazano v polju B1)
| LONG | 3001 |  | LONG | *če se vsebine iz variable_new ne gre skpirat v variable.dbf datotek, vsebino skopirajte najprej v *.txt datoteko in nato v variable.dbf
| REAL | 4001 |  | REAL | *v polju A14 na Sheet-u Prva stran se prikazuje število ciklop do konca izvedbe makroja (samo za gumb 7.KORAK)
| STRING | 6001 |  | STRING
| UINT | 7001 |  | UINT
| variable_3 | 6.KORAK | variable_new | 7.KORAK
| New Device name | IOD_SS2_TCP |  | Nova variable dbf
|  |  | xSoft | 8.KORAK in 9.KORAK
xSoft koda
xSoft_EXP
Izvoz*.EXP
1.KORAK
2.KORAK
3.KORAK
5.KORAK
6.KORAK
7.KORAK
8.KORAK
9.KORAK
RESET
Ponastavi
10.KORAK
Save*.EXP

## variable
SS2PrikazKlimat2 | DIGITAL | IOD_SS2_disk | D3 | [8 empty] | 0x0fc00010
SS2PrikazKlimat3 | DIGITAL | IOD_SS2_disk | D4 | [8 empty] | 0x0fc00020
SS2PrikazKlimat4 | DIGITAL | IOD_SS2_disk | D5 | [8 empty] | 0x0fc00030
SS2PrikazKlimat5 | DIGITAL | IOD_SS2_disk | D6 | [8 empty] | 0x0fc00040
SS2PrikazKlimat6 | DIGITAL | IOD_SS2_disk | D7 | [8 empty] | 0x0fc00050
SS2PrikazPMM1 | DIGITAL | IOD_SS2_disk | D8 | [8 empty] | 0x0fc00060
SS2PrikazPMM2 | DIGITAL | IOD_SS2_disk | D9 | [8 empty] | 0x0fc00070
SS2PrikazUPSKrmOm | DIGITAL | IOD_SS2_disk | D10 | [8 empty] | 0x0fc00080
SS2PrikazNastTemp1 | DIGITAL | IOD_SS2_disk | D11 | [8 empty] | 0x0fc00090
SS2PrikazNastTemp2 | DIGITAL | IOD_SS2_disk | D12 | [8 empty] | 0x0fc000a0
SS2PrikazNastTemp3 | DIGITAL | IOD_SS2_disk | D13 | [8 empty] | 0x0fc000b0
SS2PrikazNastTemp4 | DIGITAL | IOD_SS2_disk | D14 | [8 empty] | 0x0fc000c0
SS2Pulz1s | DIGITAL | IOD_SS2_disk | D1 | [8 empty] | 0x0fc000d0
SS2PrikazKlimat1 | DIGITAL | IOD_SS2_disk | D2 | [8 empty] | 0x0fc000e0
SS2OmogociVseAlarme | DIGITAL | IOD_SS2_disk | D3950 | [8 empty] | 0x0fc000f0
SS2OmogociVseSMSAlarme | DIGITAL | IOD_SS2_disk | D3951 | [8 empty] | 0x0fc00100
SS2PMM1Phase1Current1_med60in80 | DIGITAL | IOD_SS2_disk | D15 | [8 empty] | 0x0fc00110
SS2PMM1Phase1Current2_med60in80 | DIGITAL | IOD_SS2_disk | D16 | [8 empty] | 0x0fc00120
SS2PMM1Phase1Current3_med60in80 | DIGITAL | IOD_SS2_disk | D17 | [8 empty] | 0x0fc00130
SS2PMM1Phase1Current4_med60in80 | DIGITAL | IOD_SS2_disk | D18 | [8 empty] | 0x0fc00140
SS2PMM1Phase1Current5_med60in80 | DIGITAL | IOD_SS2_disk | D19 | [8 empty] | 0x0fc00150
SS2PMM1Phase1Current6_med60in80 | DIGITAL | IOD_SS2_disk | D20 | [8 empty] | 0x0fc00160
SS2PMM1Phase1Current7_med60in80 | DIGITAL | IOD_SS2_disk | D21 | [8 empty] | 0x0fc00170
SS2PMM1Phase1Current8_med60in80 | DIGITAL | IOD_SS2_disk | D22 | [8 empty] | 0x0fc00180
SS2PMM1Phase1Current9_med60in80 | DIGITAL | IOD_SS2_disk | D23 | [8 empty] | 0x0fc00190
SS2PMM1Phase1Current10_med60in80 | DIGITAL | IOD_SS2_disk | D24 | [8 empty] | 0x0fc001a0
SS2PMM1Phase1Current11_med60in80 | DIGITAL | IOD_SS2_disk | D25 | [8 empty] | 0x0fc001b0
SS2PMM1Phase1Current12_med60in80 | DIGITAL | IOD_SS2_disk | D26 | [8 empty] | 0x0fc001c0
SS2PMM1Phase1Current13_med60in80 | DIGITAL | IOD_SS2_disk | D27 | [8 empty] | 0x0fc001d0
SS2PMM1Phase1Current14_med60in80 | DIGITAL | IOD_SS2_disk | D28 | [8 empty] | 0x0fc001e0
SS2PMM1Phase1Current15_med60in80 | DIGITAL | IOD_SS2_disk | D29 | [8 empty] | 0x0fc001f0
SS2PMM1Phase1Current16_med60in80 | DIGITAL | IOD_SS2_disk | D30 | [8 empty] | 0x0fc00200
SS2PMM1Phase1Current17_med60in80 | DIGITAL | IOD_SS2_disk | D31 | [8 empty] | 0x0fc00210
SS2PMM1Phase1Current18_med60in80 | DIGITAL | IOD_SS2_disk | D32 | [8 empty] | 0x0fc00220
SS2PMM1Phase1Current19_med60in80 | DIGITAL | IOD_SS2_disk | D33 | [8 empty] | 0x0fc00230
SS2PMM1Phase1Current20_med60in80 | DIGITAL | IOD_SS2_disk | D34 | [8 empty] | 0x0fc00240
SS2PMM1Phase1Current21_med60in80 | DIGITAL | IOD_SS2_disk | D35 | [8 empty] | 0x0fc00250
SS2PMM1Phase1Current22_med60in80 | DIGITAL | IOD_SS2_disk | D36 | [8 empty] | 0x0fc00260
SS2PMM1Phase1Current23_med60in80 | DIGITAL | IOD_SS2_disk | D37 | [8 empty] | 0x0fc00270
SS2PMM1Phase1Current24_med60in80 | DIGITAL | IOD_SS2_disk | D38 | [8 empty] | 0x0fc00280
SS2PMM1Phase1Current25_med60in80 | DIGITAL | IOD_SS2_disk | D39 | [8 empty] | 0x0fc00290
SS2PMM1Phase1Current26_med60in80 | DIGITAL | IOD_SS2_disk | D40 | [8 empty] | 0x0fc002a0
SS2PMM1Phase1Current27_med60in80 | DIGITAL | IOD_SS2_disk | D41 | [8 empty] | 0x0fc002b0
SS2PMM1Phase1Current28_med60in80 | DIGITAL | IOD_SS2_disk | D42 | [8 empty] | 0x0fc002c0
SS2PMM1Phase1Current29_med60in80 | DIGITAL | IOD_SS2_disk | D43 | [8 empty] | 0x0fc002d0
SS2PMM1Phase1Current30_med60in80 | DIGITAL | IOD_SS2_disk | D44 | [8 empty] | 0x0fc002e0
SS2PMM1Phase1Current31_med60in80 | DIGITAL | IOD_SS2_disk | D45 | [8 empty] | 0x0fc002f0
SS2PMM1Phase1Current32_med60in80 | DIGITAL | IOD_SS2_disk | D46 | [8 empty] | 0x0fc00300
SS2PMM1Phase1Current33_med60in80 | DIGITAL | IOD_SS2_disk | D47 | [8 empty] | 0x0fc00310
SS2PMM1Phase1Current34_med60in80 | DIGITAL | IOD_SS2_disk | D48 | [8 empty] | 0x0fc00320
SS2PMM1Phase1Current35_med60in80 | DIGITAL | IOD_SS2_disk | D49 | [8 empty] | 0x0fc00330
SS2PMM1Phase1Current36_med60in80 | DIGITAL | IOD_SS2_disk | D50 | [8 empty] | 0x0fc00340
SS2PMM1Phase1Current37_med60in80 | DIGITAL | IOD_SS2_disk | D51 | [8 empty] | 0x0fc00350
SS2PMM1Phase1Current38_med60in80 | DIGITAL | IOD_SS2_disk | D52 | [8 empty] | 0x0fc00360
SS2PMM1Phase1Current39_med60in80 | DIGITAL | IOD_SS2_disk | D53 | [8 empty] | 0x0fc00370
SS2PMM1Phase1Current40_med60in80 | DIGITAL | IOD_SS2_disk | D54 | [8 empty] | 0x0fc00380
SS2PMM1Phase1Current41_med60in80 | DIGITAL | IOD_SS2_disk | D55 | [8 empty] | 0x0fc00390
SS2PMM1Phase1Current42_med60in80 | DIGITAL | IOD_SS2_disk | D56 | [8 empty] | 0x0fc003a0
SS2PMM1Phase1Current1_nad80 | DIGITAL | IOD_SS2_disk | D57 | [8 empty] | 0x0fc003b0
SS2PMM1Phase1Current2_nad80 | DIGITAL | IOD_SS2_disk | D58 | [8 empty] | 0x0fc003c0
SS2PMM1Phase1Current3_nad80 | DIGITAL | IOD_SS2_disk | D59 | [8 empty] | 0x0fc003d0
SS2PMM1Phase1Current4_nad80 | DIGITAL | IOD_SS2_disk | D60 | [8 empty] | 0x0fc003e0
SS2PMM1Phase1Current5_nad80 | DIGITAL | IOD_SS2_disk | D61 | [8 empty] | 0x0fc003f0
SS2PMM1Phase1Current6_nad80 | DIGITAL | IOD_SS2_disk | D62 | [8 empty] | 0x0fc00400
SS2PMM1Phase1Current7_nad80 | DIGITAL | IOD_SS2_disk | D63 | [8 empty] | 0x0fc00410
SS2PMM1Phase1Current8_nad80 | DIGITAL | IOD_SS2_disk | D64 | [8 empty] | 0x0fc00420
SS2PMM1Phase1Current9_nad80 | DIGITAL | IOD_SS2_disk | D65 | [8 empty] | 0x0fc00430
SS2PMM1Phase1Current10_nad80 | DIGITAL | IOD_SS2_disk | D66 | [8 empty] | 0x0fc00440
SS2PMM1Phase1Current11_nad80 | DIGITAL | IOD_SS2_disk | D67 | [8 empty] | 0x0fc00450
SS2PMM1Phase1Current12_nad80 | DIGITAL | IOD_SS2_disk | D68 | [8 empty] | 0x0fc00460
SS2PMM1Phase1Current13_nad80 | DIGITAL | IOD_SS2_disk | D69 | [8 empty] | 0x0fc00470
SS2PMM1Phase1Current14_nad80 | DIGITAL | IOD_SS2_disk | D70 | [8 empty] | 0x0fc00480
SS2PMM1Phase1Current15_nad80 | DIGITAL | IOD_SS2_disk | D71 | [8 empty] | 0x0fc00490
SS2PMM1Phase1Current16_nad80 | DIGITAL | IOD_SS2_disk | D72 | [8 empty] | 0x0fc004a0
SS2PMM1Phase1Current17_nad80 | DIGITAL | IOD_SS2_disk | D73 | [8 empty] | 0x0fc004b0
SS2PMM1Phase1Current18_nad80 | DIGITAL | IOD_SS2_disk | D74 | [8 empty] | 0x0fc004c0
SS2PMM1Phase1Current19_nad80 | DIGITAL | IOD_SS2_disk | D75 | [8 empty] | 0x0fc004d0
SS2PMM1Phase1Current20_nad80 | DIGITAL | IOD_SS2_disk | D76 | [8 empty] | 0x0fc004e0
SS2PMM1Phase1Current21_nad80 | DIGITAL | IOD_SS2_disk | D77 | [8 empty] | 0x0fc004f0
SS2PMM1Phase1Current22_nad80 | DIGITAL | IOD_SS2_disk | D78 | [8 empty] | 0x0fc00500
SS2PMM1Phase1Current23_nad80 | DIGITAL | IOD_SS2_disk | D79 | [8 empty] | 0x0fc00510
SS2PMM1Phase1Current24_nad80 | DIGITAL | IOD_SS2_disk | D80 | [8 empty] | 0x0fc00520
SS2PMM1Phase1Current25_nad80 | DIGITAL | IOD_SS2_disk | D81 | [8 empty] | 0x0fc00530
SS2PMM1Phase1Current26_nad80 | DIGITAL | IOD_SS2_disk | D82 | [8 empty] | 0x0fc00540
SS2PMM1Phase1Current27_nad80 | DIGITAL | IOD_SS2_disk | D83 | [8 empty] | 0x0fc00550
SS2PMM1Phase1Current28_nad80 | DIGITAL | IOD_SS2_disk | D84 | [8 empty] | 0x0fc00560
SS2PMM1Phase1Current29_nad80 | DIGITAL | IOD_SS2_disk | D85 | [8 empty] | 0x0fc00570
SS2PMM1Phase1Current30_nad80 | DIGITAL | IOD_SS2_disk | D86 | [8 empty] | 0x0fc00580
SS2PMM1Phase1Current31_nad80 | DIGITAL | IOD_SS2_disk | D87 | [8 empty] | 0x0fc00590
SS2PMM1Phase1Current32_nad80 | DIGITAL | IOD_SS2_disk | D88 | [8 empty] | 0x0fc005a0
SS2PMM1Phase1Current33_nad80 | DIGITAL | IOD_SS2_disk | D89 | [8 empty] | 0x0fc005b0
SS2PMM1Phase1Current34_nad80 | DIGITAL | IOD_SS2_disk | D90 | [8 empty] | 0x0fc005c0
SS2PMM1Phase1Current35_nad80 | DIGITAL | IOD_SS2_disk | D91 | [8 empty] | 0x0fc005d0
SS2PMM1Phase1Current36_nad80 | DIGITAL | IOD_SS2_disk | D92 | [8 empty] | 0x0fc005e0
SS2PMM1Phase1Current37_nad80 | DIGITAL | IOD_SS2_disk | D93 | [8 empty] | 0x0fc005f0
SS2PMM1Phase1Current38_nad80 | DIGITAL | IOD_SS2_disk | D94 | [8 empty] | 0x0fc00600
SS2PMM1Phase1Current39_nad80 | DIGITAL | IOD_SS2_disk | D95 | [8 empty] | 0x0fc00610
SS2PMM1Phase1Current40_nad80 | DIGITAL | IOD_SS2_disk | D96 | [8 empty] | 0x0fc00620
SS2PMM1Phase1Current41_nad80 | DIGITAL | IOD_SS2_disk | D97 | [8 empty] | 0x0fc00630
SS2PMM1Phase1Current42_nad80 | DIGITAL | IOD_SS2_disk | D98 | [8 empty] | 0x0fc00640
SS2PMM1Phase2Current1_nad80 | DIGITAL | IOD_SS2_disk | D99 | [8 empty] | 0x0fc00650
SS2PMM1Phase2Current2_nad80 | DIGITAL | IOD_SS2_disk | D100 | [8 empty] | 0x0fc00660
SS2PMM1Phase2Current3_nad80 | DIGITAL | IOD_SS2_disk | D101 | [8 empty] | 0x0fc00670
SS2PMM1Phase2Current4_nad80 | DIGITAL | IOD_SS2_disk | D102 | [8 empty] | 0x0fc00680
SS2PMM1Phase2Current5_nad80 | DIGITAL | IOD_SS2_disk | D103 | [8 empty] | 0x0fc00690
SS2PMM1Phase2Current6_nad80 | DIGITAL | IOD_SS2_disk | D104 | [8 empty] | 0x0fc006a0
SS2PMM1Phase2Current7_nad80 | DIGITAL | IOD_SS2_disk | D105 | [8 empty] | 0x0fc006b0
SS2PMM1Phase2Current8_nad80 | DIGITAL | IOD_SS2_disk | D106 | [8 empty] | 0x0fc006c0
SS2PMM1Phase2Current9_nad80 | DIGITAL | IOD_SS2_disk | D107 | [8 empty] | 0x0fc006d0
SS2PMM1Phase2Current10_nad80 | DIGITAL | IOD_SS2_disk | D108 | [8 empty] | 0x0fc006e0
SS2PMM1Phase2Current11_nad80 | DIGITAL | IOD_SS2_disk | D109 | [8 empty] | 0x0fc006f0
SS2PMM1Phase2Current12_nad80 | DIGITAL | IOD_SS2_disk | D110 | [8 empty] | 0x0fc00700
SS2PMM1Phase2Current13_nad80 | DIGITAL | IOD_SS2_disk | D111 | [8 empty] | 0x0fc00710
SS2PMM1Phase2Current14_nad80 | DIGITAL | IOD_SS2_disk | D112 | [8 empty] | 0x0fc00720
SS2PMM1Phase2Current15_nad80 | DIGITAL | IOD_SS2_disk | D113 | [8 empty] | 0x0fc00730
SS2PMM1Phase2Current16_nad80 | DIGITAL | IOD_SS2_disk | D114 | [8 empty] | 0x0fc00740
SS2PMM1Phase2Current17_nad80 | DIGITAL | IOD_SS2_disk | D115 | [8 empty] | 0x0fc00750
SS2PMM1Phase2Current18_nad80 | DIGITAL | IOD_SS2_disk | D116 | [8 empty] | 0x0fc00760
SS2PMM1Phase2Current19_nad80 | DIGITAL | IOD_SS2_disk | D117 | [8 empty] | 0x0fc00770
SS2PMM1Phase2Current20_nad80 | DIGITAL | IOD_SS2_disk | D118 | [8 empty] | 0x0fc00780
SS2PMM1Phase2Current21_nad80 | DIGITAL | IOD_SS2_disk | D119 | [8 empty] | 0x0fc00790
SS2PMM1Phase2Current22_nad80 | DIGITAL | IOD_SS2_disk | D120 | [8 empty] | 0x0fc007a0
SS2PMM1Phase2Current23_nad80 | DIGITAL | IOD_SS2_disk | D121 | [8 empty] | 0x0fc007b0
SS2PMM1Phase2Current24_nad80 | DIGITAL | IOD_SS2_disk | D122 | [8 empty] | 0x0fc007c0
SS2PMM1Phase2Current25_nad80 | DIGITAL | IOD_SS2_disk | D123 | [8 empty] | 0x0fc007d0
SS2PMM1Phase2Current26_nad80 | DIGITAL | IOD_SS2_disk | D124 | [8 empty] | 0x0fc007e0
SS2PMM1Phase2Current27_nad80 | DIGITAL | IOD_SS2_disk | D125 | [8 empty] | 0x0fc007f0
SS2PMM1Phase2Current28_nad80 | DIGITAL | IOD_SS2_disk | D126 | [8 empty] | 0x0fc00800
SS2PMM1Phase2Current29_nad80 | DIGITAL | IOD_SS2_disk | D127 | [8 empty] | 0x0fc00810
SS2PMM1Phase2Current30_nad80 | DIGITAL | IOD_SS2_disk | D128 | [8 empty] | 0x0fc00820
SS2PMM1Phase2Current31_nad80 | DIGITAL | IOD_SS2_disk | D129 | [8 empty] | 0x0fc00830
SS2PMM1Phase2Current32_nad80 | DIGITAL | IOD_SS2_disk | D130 | [8 empty] | 0x0fc00840
SS2PMM1Phase2Current33_nad80 | DIGITAL | IOD_SS2_disk | D131 | [8 empty] | 0x0fc00850
SS2PMM1Phase2Current34_nad80 | DIGITAL | IOD_SS2_disk | D132 | [8 empty] | 0x0fc00860
SS2PMM1Phase2Current35_nad80 | DIGITAL | IOD_SS2_disk | D133 | [8 empty] | 0x0fc00870
SS2PMM1Phase2Current36_nad80 | DIGITAL | IOD_SS2_disk | D134 | [8 empty] | 0x0fc00880
SS2PMM1Phase2Current37_nad80 | DIGITAL | IOD_SS2_disk | D135 | [8 empty] | 0x0fc00890
SS2PMM1Phase2Current38_nad80 | DIGITAL | IOD_SS2_disk | D136 | [8 empty] | 0x0fc008a0
SS2PMM1Phase2Current39_nad80 | DIGITAL | IOD_SS2_disk | D137 | [8 empty] | 0x0fc008b0
SS2PMM1Phase2Current40_nad80 | DIGITAL | IOD_SS2_disk | D138 | [8 empty] | 0x0fc008c0
SS2PMM1Phase2Current41_nad80 | DIGITAL | IOD_SS2_disk | D139 | [8 empty] | 0x0fc008d0
SS2PMM1Phase2Current42_nad80 | DIGITAL | IOD_SS2_disk | D140 | [8 empty] | 0x0fc008e0
SS2PMM1Phase3Current1_nad80 | DIGITAL | IOD_SS2_disk | D141 | [8 empty] | 0x0fc008f0
SS2PMM1Phase3Current2_nad80 | DIGITAL | IOD_SS2_disk | D142 | [8 empty] | 0x0fc00900
SS2PMM1Phase3Current3_nad80 | DIGITAL | IOD_SS2_disk | D143 | [8 empty] | 0x0fc00910
SS2PMM1Phase3Current4_nad80 | DIGITAL | IOD_SS2_disk | D144 | [8 empty] | 0x0fc00920
SS2PMM1Phase3Current5_nad80 | DIGITAL | IOD_SS2_disk | D145 | [8 empty] | 0x0fc00930
SS2PMM1Phase3Current6_nad80 | DIGITAL | IOD_SS2_disk | D146 | [8 empty] | 0x0fc00940
SS2PMM1Phase3Current7_nad80 | DIGITAL | IOD_SS2_disk | D147 | [8 empty] | 0x0fc00950
SS2PMM1Phase3Current8_nad80 | DIGITAL | IOD_SS2_disk | D148 | [8 empty] | 0x0fc00960
SS2PMM1Phase3Current9_nad80 | DIGITAL | IOD_SS2_disk | D149 | [8 empty] | 0x0fc00970
SS2PMM1Phase3Current10_nad80 | DIGITAL | IOD_SS2_disk | D150 | [8 empty] | 0x0fc00980
SS2PMM1Phase3Current11_nad80 | DIGITAL | IOD_SS2_disk | D151 | [8 empty] | 0x0fc00990
SS2PMM1Phase3Current12_nad80 | DIGITAL | IOD_SS2_disk | D152 | [8 empty] | 0x0fc009a0
SS2PMM1Phase3Current13_nad80 | DIGITAL | IOD_SS2_disk | D153 | [8 empty] | 0x0fc009b0
SS2PMM1Phase3Current14_nad80 | DIGITAL | IOD_SS2_disk | D154 | [8 empty] | 0x0fc009c0
SS2PMM1Phase3Current15_nad80 | DIGITAL | IOD_SS2_disk | D155 | [8 empty] | 0x0fc009d0
SS2PMM1Phase3Current16_nad80 | DIGITAL | IOD_SS2_disk | D156 | [8 empty] | 0x0fc009e0
SS2PMM1Phase3Current17_nad80 | DIGITAL | IOD_SS2_disk | D157 | [8 empty] | 0x0fc009f0
SS2PMM1Phase3Current18_nad80 | DIGITAL | IOD_SS2_disk | D158 | [8 empty] | 0x0fc00a00
SS2PMM1Phase3Current19_nad80 | DIGITAL | IOD_SS2_disk | D159 | [8 empty] | 0x0fc00a10
SS2PMM1Phase3Current20_nad80 | DIGITAL | IOD_SS2_disk | D160 | [8 empty] | 0x0fc00a20
SS2PMM1Phase3Current21_nad80 | DIGITAL | IOD_SS2_disk | D161 | [8 empty] | 0x0fc00a30
SS2PMM1Phase3Current22_nad80 | DIGITAL | IOD_SS2_disk | D162 | [8 empty] | 0x0fc00a40
SS2PMM1Phase3Current23_nad80 | DIGITAL | IOD_SS2_disk | D163 | [8 empty] | 0x0fc00a50
SS2PMM1Phase3Current24_nad80 | DIGITAL | IOD_SS2_disk | D164 | [8 empty] | 0x0fc00a60
SS2PMM1Phase3Current25_nad80 | DIGITAL | IOD_SS2_disk | D165 | [8 empty] | 0x0fc00a70
SS2PMM1Phase3Current26_nad80 | DIGITAL | IOD_SS2_disk | D166 | [8 empty] | 0x0fc00a80
SS2PMM1Phase3Current27_nad80 | DIGITAL | IOD_SS2_disk | D167 | [8 empty] | 0x0fc00a90
SS2PMM1Phase3Current28_nad80 | DIGITAL | IOD_SS2_disk | D168 | [8 empty] | 0x0fc00aa0
SS2PMM1Phase3Current29_nad80 | DIGITAL | IOD_SS2_disk | D169 | [8 empty] | 0x0fc00ab0
SS2PMM1Phase3Current30_nad80 | DIGITAL | IOD_SS2_disk | D170 | [8 empty] | 0x0fc00ac0
SS2PMM1Phase3Current31_nad80 | DIGITAL | IOD_SS2_disk | D171 | [8 empty] | 0x0fc00ad0
SS2PMM1Phase3Current32_nad80 | DIGITAL | IOD_SS2_disk | D172 | [8 empty] | 0x0fc00ae0
SS2PMM1Phase3Current33_nad80 | DIGITAL | IOD_SS2_disk | D173 | [8 empty] | 0x0fc00af0
SS2PMM1Phase3Current34_nad80 | DIGITAL | IOD_SS2_disk | D174 | [8 empty] | 0x0fc00b00
SS2PMM1Phase3Current35_nad80 | DIGITAL | IOD_SS2_disk | D175 | [8 empty] | 0x0fc00b10
SS2PMM1Phase3Current36_nad80 | DIGITAL | IOD_SS2_disk | D176 | [8 empty] | 0x0fc00b20
SS2PMM1Phase3Current37_nad80 | DIGITAL | IOD_SS2_disk | D177 | [8 empty] | 0x0fc00b30
SS2PMM1Phase3Current38_nad80 | DIGITAL | IOD_SS2_disk | D178 | [8 empty] | 0x0fc00b40
SS2PMM1Phase3Current39_nad80 | DIGITAL | IOD_SS2_disk | D179 | [8 empty] | 0x0fc00b50
SS2PMM1Phase3Current40_nad80 | DIGITAL | IOD_SS2_disk | D180 | [8 empty] | 0x0fc00b60
SS2PMM1Phase3Current41_nad80 | DIGITAL | IOD_SS2_disk | D181 | [8 empty] | 0x0fc00b70
SS2PMM1Phase3Current42_nad80 | DIGITAL | IOD_SS2_disk | D182 | [8 empty] | 0x0fc00b80
SS2PMM1Phase2Current1_med60in80 | DIGITAL | IOD_SS2_disk | D183 | [8 empty] | 0x0fc00b90
SS2PMM1Phase2Current2_med60in80 | DIGITAL | IOD_SS2_disk | D184 | [8 empty] | 0x0fc00ba0
SS2PMM1Phase2Current3_med60in80 | DIGITAL | IOD_SS2_disk | D185 | [8 empty] | 0x0fc00bb0
SS2PMM1Phase2Current4_med60in80 | DIGITAL | IOD_SS2_disk | D186 | [8 empty] | 0x0fc00bc0
SS2PMM1Phase2Current5_med60in80 | DIGITAL | IOD_SS2_disk | D187 | [8 empty] | 0x0fc00bd0
SS2PMM1Phase2Current6_med60in80 | DIGITAL | IOD_SS2_disk | D188 | [8 empty] | 0x0fc00be0
SS2PMM1Phase2Current7_med60in80 | DIGITAL | IOD_SS2_disk | D189 | [8 empty] | 0x0fc00bf0
SS2PMM1Phase2Current8_med60in80 | DIGITAL | IOD_SS2_disk | D190 | [8 empty] | 0x0fc00c00
SS2PMM1Phase2Current9_med60in80 | DIGITAL | IOD_SS2_disk | D191 | [8 empty] | 0x0fc00c10
SS2PMM1Phase2Current10_med60in80 | DIGITAL | IOD_SS2_disk | D192 | [8 empty] | 0x0fc00c20
SS2PMM1Phase2Current11_med60in80 | DIGITAL | IOD_SS2_disk | D193 | [8 empty] | 0x0fc00c30
SS2PMM1Phase2Current12_med60in80 | DIGITAL | IOD_SS2_disk | D194 | [8 empty] | 0x0fc00c40
SS2PMM1Phase2Current13_med60in80 | DIGITAL | IOD_SS2_disk | D195 | [8 empty] | 0x0fc00c50
SS2PMM1Phase2Current14_med60in80 | DIGITAL | IOD_SS2_disk | D196 | [8 empty] | 0x0fc00c60
SS2PMM1Phase2Current15_med60in80 | DIGITAL | IOD_SS2_disk | D197 | [8 empty] | 0x0fc00c70
SS2PMM1Phase2Current16_med60in80 | DIGITAL | IOD_SS2_disk | D198 | [8 empty] | 0x0fc00c80
SS2PMM1Phase2Current17_med60in80 | DIGITAL | IOD_SS2_disk | D199 | [8 empty] | 0x0fc00c90
SS2PMM1Phase2Current18_med60in80 | DIGITAL | IOD_SS2_disk | D200 | [8 empty] | 0x0fc00ca0
SS2PMM1Phase2Current19_med60in80 | DIGITAL | IOD_SS2_disk | D201 | [8 empty] | 0x0fc00cb0
SS2PMM1Phase2Current20_med60in80 | DIGITAL | IOD_SS2_disk | D202 | [8 empty] | 0x0fc00cc0
SS2PMM1Phase2Current21_med60in80 | DIGITAL | IOD_SS2_disk | D203 | [8 empty] | 0x0fc00cd0
SS2PMM1Phase2Current22_med60in80 | DIGITAL | IOD_SS2_disk | D204 | [8 empty] | 0x0fc00ce0
SS2PMM1Phase2Current23_med60in80 | DIGITAL | IOD_SS2_disk | D205 | [8 empty] | 0x0fc00cf0
SS2PMM1Phase2Current24_med60in80 | DIGITAL | IOD_SS2_disk | D206 | [8 empty] | 0x0fc00d00
SS2PMM1Phase2Current25_med60in80 | DIGITAL | IOD_SS2_disk | D207 | [8 empty] | 0x0fc00d10
SS2PMM1Phase2Current26_med60in80 | DIGITAL | IOD_SS2_disk | D208 | [8 empty] | 0x0fc00d20
SS2PMM1Phase2Current27_med60in80 | DIGITAL | IOD_SS2_disk | D209 | [8 empty] | 0x0fc00d30
SS2PMM1Phase2Current28_med60in80 | DIGITAL | IOD_SS2_disk | D210 | [8 empty] | 0x0fc00d40
SS2PMM1Phase2Current29_med60in80 | DIGITAL | IOD_SS2_disk | D211 | [8 empty] | 0x0fc00d50
SS2PMM1Phase2Current30_med60in80 | DIGITAL | IOD_SS2_disk | D212 | [8 empty] | 0x0fc00d60
SS2PMM1Phase2Current31_med60in80 | DIGITAL | IOD_SS2_disk | D213 | [8 empty] | 0x0fc00d70
SS2PMM1Phase2Current32_med60in80 | DIGITAL | IOD_SS2_disk | D214 | [8 empty] | 0x0fc00d80
SS2PMM1Phase2Current33_med60in80 | DIGITAL | IOD_SS2_disk | D215 | [8 empty] | 0x0fc00d90
SS2PMM1Phase2Current34_med60in80 | DIGITAL | IOD_SS2_disk | D216 | [8 empty] | 0x0fc00da0
SS2PMM1Phase2Current35_med60in80 | DIGITAL | IOD_SS2_disk | D217 | [8 empty] | 0x0fc00db0
SS2PMM1Phase2Current36_med60in80 | DIGITAL | IOD_SS2_disk | D218 | [8 empty] | 0x0fc00dc0
SS2PMM1Phase2Current37_med60in80 | DIGITAL | IOD_SS2_disk | D219 | [8 empty] | 0x0fc00dd0
SS2PMM1Phase2Current38_med60in80 | DIGITAL | IOD_SS2_disk | D220 | [8 empty] | 0x0fc00de0
SS2PMM1Phase2Current39_med60in80 | DIGITAL | IOD_SS2_disk | D221 | [8 empty] | 0x0fc00df0
SS2PMM1Phase2Current40_med60in80 | DIGITAL | IOD_SS2_disk | D222 | [8 empty] | 0x0fc00e00
SS2PMM1Phase2Current41_med60in80 | DIGITAL | IOD_SS2_disk | D223 | [8 empty] | 0x0fc00e10
SS2PMM1Phase2Current42_med60in80 | DIGITAL | IOD_SS2_disk | D224 | [8 empty] | 0x0fc00e20
SS2PMM1Phase3Current1_med60in80 | DIGITAL | IOD_SS2_disk | D225 | [8 empty] | 0x0fc00e30
SS2PMM1Phase3Current2_med60in80 | DIGITAL | IOD_SS2_disk | D226 | [8 empty] | 0x0fc00e40
SS2PMM1Phase3Current3_med60in80 | DIGITAL | IOD_SS2_disk | D227 | [8 empty] | 0x0fc00e50
SS2PMM1Phase3Current4_med60in80 | DIGITAL | IOD_SS2_disk | D228 | [8 empty] | 0x0fc00e60
SS2PMM1Phase3Current5_med60in80 | DIGITAL | IOD_SS2_disk | D229 | [8 empty] | 0x0fc00e70
SS2PMM1Phase3Current6_med60in80 | DIGITAL | IOD_SS2_disk | D230 | [8 empty] | 0x0fc00e80
SS2PMM1Phase3Current7_med60in80 | DIGITAL | IOD_SS2_disk | D231 | [8 empty] | 0x0fc00e90
SS2PMM1Phase3Current8_med60in80 | DIGITAL | IOD_SS2_disk | D232 | [8 empty] | 0x0fc00ea0
SS2PMM1Phase3Current9_med60in80 | DIGITAL | IOD_SS2_disk | D233 | [8 empty] | 0x0fc00eb0
SS2PMM1Phase3Current10_med60in80 | DIGITAL | IOD_SS2_disk | D234 | [8 empty] | 0x0fc00ec0
SS2PMM1Phase3Current11_med60in80 | DIGITAL | IOD_SS2_disk | D235 | [8 empty] | 0x0fc00ed0
SS2PMM1Phase3Current12_med60in80 | DIGITAL | IOD_SS2_disk | D236 | [8 empty] | 0x0fc00ee0
SS2PMM1Phase3Current13_med60in80 | DIGITAL | IOD_SS2_disk | D237 | [8 empty] | 0x0fc00ef0
SS2PMM1Phase3Current14_med60in80 | DIGITAL | IOD_SS2_disk | D238 | [8 empty] | 0x0fc00f00
SS2PMM1Phase3Current15_med60in80 | DIGITAL | IOD_SS2_disk | D239 | [8 empty] | 0x0fc00f10
SS2PMM1Phase3Current16_med60in80 | DIGITAL | IOD_SS2_disk | D240 | [8 empty] | 0x0fc00f20
SS2PMM1Phase3Current17_med60in80 | DIGITAL | IOD_SS2_disk | D241 | [8 empty] | 0x0fc00f30
SS2PMM1Phase3Current18_med60in80 | DIGITAL | IOD_SS2_disk | D242 | [8 empty] | 0x0fc00f40
SS2PMM1Phase3Current19_med60in80 | DIGITAL | IOD_SS2_disk | D243 | [8 empty] | 0x0fc00f50
SS2PMM1Phase3Current20_med60in80 | DIGITAL | IOD_SS2_disk | D244 | [8 empty] | 0x0fc00f60
SS2PMM1Phase3Current21_med60in80 | DIGITAL | IOD_SS2_disk | D245 | [8 empty] | 0x0fc00f70
SS2PMM1Phase3Current22_med60in80 | DIGITAL | IOD_SS2_disk | D246 | [8 empty] | 0x0fc00f80
SS2PMM1Phase3Current23_med60in80 | DIGITAL | IOD_SS2_disk | D247 | [8 empty] | 0x0fc00f90
SS2PMM1Phase3Current24_med60in80 | DIGITAL | IOD_SS2_disk | D248 | [8 empty] | 0x0fc00fa0
SS2PMM1Phase3Current25_med60in80 | DIGITAL | IOD_SS2_disk | D249 | [8 empty] | 0x0fc00fb0
SS2PMM1Phase3Current26_med60in80 | DIGITAL | IOD_SS2_disk | D250 | [8 empty] | 0x0fc00fc0
SS2PMM1Phase3Current27_med60in80 | DIGITAL | IOD_SS2_disk | D251 | [8 empty] | 0x0fc00fd0
SS2PMM1Phase3Current28_med60in80 | DIGITAL | IOD_SS2_disk | D252 | [8 empty] | 0x0fc00fe0
SS2PMM1Phase3Current29_med60in80 | DIGITAL | IOD_SS2_disk | D252 | [8 empty] | 0x0fc00ff0
SS2PMM1Phase3Current30_med60in80 | DIGITAL | IOD_SS2_disk | D253 | [8 empty] | 0x0fc01000
SS2PMM1Phase3Current31_med60in80 | DIGITAL | IOD_SS2_disk | D254 | [8 empty] | 0x0fc01010
SS2PMM1Phase3Current32_med60in80 | DIGITAL | IOD_SS2_disk | D255 | [8 empty] | 0x0fc01020
SS2PMM1Phase3Current33_med60in80 | DIGITAL | IOD_SS2_disk | D256 | [8 empty] | 0x0fc01030
SS2PMM1Phase3Current34_med60in80 | DIGITAL | IOD_SS2_disk | D257 | [8 empty] | 0x0fc01040
SS2PMM1Phase3Current35_med60in80 | DIGITAL | IOD_SS2_disk | D258 | [8 empty] | 0x0fc01050
SS2PMM1Phase3Current36_med60in80 | DIGITAL | IOD_SS2_disk | D259 | [8 empty] | 0x0fc01060
SS2PMM1Phase3Current37_med60in80 | DIGITAL | IOD_SS2_disk | D260 | [8 empty] | 0x0fc01070
SS2PMM1Phase3Current38_med60in80 | DIGITAL | IOD_SS2_disk | D261 | [8 empty] | 0x0fc01080
SS2PMM1Phase3Current39_med60in80 | DIGITAL | IOD_SS2_disk | D262 | [8 empty] | 0x0fc01090
SS2PMM1Phase3Current40_med60in80 | DIGITAL | IOD_SS2_disk | D263 | [8 empty] | 0x0fc010a0
SS2PMM1Phase3Current41_med60in80 | DIGITAL | IOD_SS2_disk | D264 | [8 empty] | 0x0fc010b0
SS2PMM1Phase3Current42_med60in80 | DIGITAL | IOD_SS2_disk | D265 | [8 empty] | 0x0fc010c0
SS2PMM2Phase1Current1_med60in80 | DIGITAL | IOD_SS2_disk | D285 | [8 empty] | 0x0fc010d0
SS2PMM2Phase1Current2_med60in80 | DIGITAL | IOD_SS2_disk | D286 | [8 empty] | 0x0fc010e0
SS2PMM2Phase1Current3_med60in80 | DIGITAL | IOD_SS2_disk | D287 | [8 empty] | 0x0fc010f0
SS2PMM2Phase1Current4_med60in80 | DIGITAL | IOD_SS2_disk | D288 | [8 empty] | 0x0fc01100
SS2PMM2Phase1Current5_med60in80 | DIGITAL | IOD_SS2_disk | D289 | [8 empty] | 0x0fc01110
SS2PMM2Phase1Current6_med60in80 | DIGITAL | IOD_SS2_disk | D290 | [8 empty] | 0x0fc01120
SS2PMM2Phase1Current7_med60in80 | DIGITAL | IOD_SS2_disk | D291 | [8 empty] | 0x0fc01130
SS2PMM2Phase1Current8_med60in80 | DIGITAL | IOD_SS2_disk | D292 | [8 empty] | 0x0fc01140
SS2PMM2Phase1Current9_med60in80 | DIGITAL | IOD_SS2_disk | D293 | [8 empty] | 0x0fc01150
SS2PMM2Phase1Current10_med60in80 | DIGITAL | IOD_SS2_disk | D294 | [8 empty] | 0x0fc01160
SS2PMM2Phase1Current11_med60in80 | DIGITAL | IOD_SS2_disk | D295 | [8 empty] | 0x0fc01170
SS2PMM2Phase1Current12_med60in80 | DIGITAL | IOD_SS2_disk | D296 | [8 empty] | 0x0fc01180
SS2PMM2Phase1Current13_med60in80 | DIGITAL | IOD_SS2_disk | D297 | [8 empty] | 0x0fc01190
SS2PMM2Phase1Current14_med60in80 | DIGITAL | IOD_SS2_disk | D298 | [8 empty] | 0x0fc011a0
SS2PMM2Phase1Current15_med60in80 | DIGITAL | IOD_SS2_disk | D299 | [8 empty] | 0x0fc011b0
SS2PMM2Phase1Current16_med60in80 | DIGITAL | IOD_SS2_disk | D300 | [8 empty] | 0x0fc011c0
SS2PMM2Phase1Current17_med60in80 | DIGITAL | IOD_SS2_disk | D301 | [8 empty] | 0x0fc011d0
SS2PMM2Phase1Current18_med60in80 | DIGITAL | IOD_SS2_disk | D302 | [8 empty] | 0x0fc011e0
SS2PMM2Phase1Current19_med60in80 | DIGITAL | IOD_SS2_disk | D303 | [8 empty] | 0x0fc011f0
SS2PMM2Phase1Current20_med60in80 | DIGITAL | IOD_SS2_disk | D304 | [8 empty] | 0x0fc01200
SS2PMM2Phase1Current21_med60in80 | DIGITAL | IOD_SS2_disk | D305 | [8 empty] | 0x0fc01210
SS2PMM2Phase1Current22_med60in80 | DIGITAL | IOD_SS2_disk | D306 | [8 empty] | 0x0fc01220
SS2PMM2Phase1Current23_med60in80 | DIGITAL | IOD_SS2_disk | D307 | [8 empty] | 0x0fc01230
SS2PMM2Phase1Current24_med60in80 | DIGITAL | IOD_SS2_disk | D308 | [8 empty] | 0x0fc01240
SS2PMM2Phase1Current25_med60in80 | DIGITAL | IOD_SS2_disk | D309 | [8 empty] | 0x0fc01250
SS2PMM2Phase1Current26_med60in80 | DIGITAL | IOD_SS2_disk | D310 | [8 empty] | 0x0fc01260
SS2PMM2Phase1Current27_med60in80 | DIGITAL | IOD_SS2_disk | D311 | [8 empty] | 0x0fc01270
SS2PMM2Phase1Current28_med60in80 | DIGITAL | IOD_SS2_disk | D312 | [8 empty] | 0x0fc01280
SS2PMM2Phase1Current29_med60in80 | DIGITAL | IOD_SS2_disk | D313 | [8 empty] | 0x0fc01290
SS2PMM2Phase1Current30_med60in80 | DIGITAL | IOD_SS2_disk | D314 | [8 empty] | 0x0fc012a0
SS2PMM2Phase1Current31_med60in80 | DIGITAL | IOD_SS2_disk | D315 | [8 empty] | 0x0fc012b0
SS2PMM2Phase1Current32_med60in80 | DIGITAL | IOD_SS2_disk | D316 | [8 empty] | 0x0fc012c0
SS2PMM2Phase1Current33_med60in80 | DIGITAL | IOD_SS2_disk | D317 | [8 empty] | 0x0fc012d0
SS2PMM2Phase1Current34_med60in80 | DIGITAL | IOD_SS2_disk | D318 | [8 empty] | 0x0fc012e0
SS2PMM2Phase1Current35_med60in80 | DIGITAL | IOD_SS2_disk | D319 | [8 empty] | 0x0fc012f0
SS2PMM2Phase1Current36_med60in80 | DIGITAL | IOD_SS2_disk | D320 | [8 empty] | 0x0fc01300
SS2PMM2Phase1Current37_med60in80 | DIGITAL | IOD_SS2_disk | D321 | [8 empty] | 0x0fc01310
SS2PMM2Phase1Current38_med60in80 | DIGITAL | IOD_SS2_disk | D322 | [8 empty] | 0x0fc01320
SS2PMM2Phase1Current39_med60in80 | DIGITAL | IOD_SS2_disk | D323 | [8 empty] | 0x0fc01330
SS2PMM2Phase1Current40_med60in80 | DIGITAL | IOD_SS2_disk | D324 | [8 empty] | 0x0fc01340
SS2PMM2Phase1Current41_med60in80 | DIGITAL | IOD_SS2_disk | D325 | [8 empty] | 0x0fc01350
SS2PMM2Phase1Current42_med60in80 | DIGITAL | IOD_SS2_disk | D326 | [8 empty] | 0x0fc01360
SS2PMM2Phase1Current1_nad80 | DIGITAL | IOD_SS2_disk | D327 | [8 empty] | 0x0fc01370
SS2PMM2Phase1Current2_nad80 | DIGITAL | IOD_SS2_disk | D328 | [8 empty] | 0x0fc01380
SS2PMM2Phase1Current3_nad80 | DIGITAL | IOD_SS2_disk | D329 | [8 empty] | 0x0fc01390
SS2PMM2Phase1Current4_nad80 | DIGITAL | IOD_SS2_disk | D330 | [8 empty] | 0x0fc013a0
SS2PMM2Phase1Current5_nad80 | DIGITAL | IOD_SS2_disk | D331 | [8 empty] | 0x0fc013b0
SS2PMM2Phase1Current6_nad80 | DIGITAL | IOD_SS2_disk | D332 | [8 empty] | 0x0fc013c0
SS2PMM2Phase1Current7_nad80 | DIGITAL | IOD_SS2_disk | D333 | [8 empty] | 0x0fc013d0
SS2PMM2Phase1Current8_nad80 | DIGITAL | IOD_SS2_disk | D334 | [8 empty] | 0x0fc013e0
SS2PMM2Phase1Current9_nad80 | DIGITAL | IOD_SS2_disk | D335 | [8 empty] | 0x0fc013f0
SS2PMM2Phase1Current10_nad80 | DIGITAL | IOD_SS2_disk | D336 | [8 empty] | 0x0fc01400
SS2PMM2Phase1Current11_nad80 | DIGITAL | IOD_SS2_disk | D337 | [8 empty] | 0x0fc01410
SS2PMM2Phase1Current12_nad80 | DIGITAL | IOD_SS2_disk | D338 | [8 empty] | 0x0fc01420
SS2PMM2Phase1Current13_nad80 | DIGITAL | IOD_SS2_disk | D339 | [8 empty] | 0x0fc01430
SS2PMM2Phase1Current14_nad80 | DIGITAL | IOD_SS2_disk | D340 | [8 empty] | 0x0fc01440
SS2PMM2Phase1Current15_nad80 | DIGITAL | IOD_SS2_disk | D341 | [8 empty] | 0x0fc01450
SS2PMM2Phase1Current16_nad80 | DIGITAL | IOD_SS2_disk | D342 | [8 empty] | 0x0fc01460
SS2PMM2Phase1Current17_nad80 | DIGITAL | IOD_SS2_disk | D343 | [8 empty] | 0x0fc01470
SS2PMM2Phase1Current18_nad80 | DIGITAL | IOD_SS2_disk | D344 | [8 empty] | 0x0fc01480
SS2PMM2Phase1Current19_nad80 | DIGITAL | IOD_SS2_disk | D345 | [8 empty] | 0x0fc01490
SS2PMM2Phase1Current20_nad80 | DIGITAL | IOD_SS2_disk | D346 | [8 empty] | 0x0fc014a0
SS2PMM2Phase1Current21_nad80 | DIGITAL | IOD_SS2_disk | D347 | [8 empty] | 0x0fc014b0
SS2PMM2Phase1Current22_nad80 | DIGITAL | IOD_SS2_disk | D348 | [8 empty] | 0x0fc014c0
SS2PMM2Phase1Current23_nad80 | DIGITAL | IOD_SS2_disk | D349 | [8 empty] | 0x0fc014d0
SS2PMM2Phase1Current24_nad80 | DIGITAL | IOD_SS2_disk | D350 | [8 empty] | 0x0fc014e0
SS2PMM2Phase1Current25_nad80 | DIGITAL | IOD_SS2_disk | D351 | [8 empty] | 0x0fc014f0
SS2PMM2Phase1Current26_nad80 | DIGITAL | IOD_SS2_disk | D352 | [8 empty] | 0x0fc01500
SS2PMM2Phase1Current27_nad80 | DIGITAL | IOD_SS2_disk | D353 | [8 empty] | 0x0fc01510
SS2PMM2Phase1Current28_nad80 | DIGITAL | IOD_SS2_disk | D354 | [8 empty] | 0x0fc01520
SS2PMM2Phase1Current29_nad80 | DIGITAL | IOD_SS2_disk | D355 | [8 empty] | 0x0fc01530
SS2PMM2Phase1Current30_nad80 | DIGITAL | IOD_SS2_disk | D356 | [8 empty] | 0x0fc01540
SS2PMM2Phase1Current31_nad80 | DIGITAL | IOD_SS2_disk | D357 | [8 empty] | 0x0fc01550
SS2PMM2Phase1Current32_nad80 | DIGITAL | IOD_SS2_disk | D358 | [8 empty] | 0x0fc01560
SS2PMM2Phase1Current33_nad80 | DIGITAL | IOD_SS2_disk | D359 | [8 empty] | 0x0fc01570
SS2PMM2Phase1Current34_nad80 | DIGITAL | IOD_SS2_disk | D360 | [8 empty] | 0x0fc01580
SS2PMM2Phase1Current35_nad80 | DIGITAL | IOD_SS2_disk | D361 | [8 empty] | 0x0fc01590
SS2PMM2Phase1Current36_nad80 | DIGITAL | IOD_SS2_disk | D362 | [8 empty] | 0x0fc015a0
SS2PMM2Phase1Current37_nad80 | DIGITAL | IOD_SS2_disk | D363 | [8 empty] | 0x0fc015b0
SS2PMM2Phase1Current38_nad80 | DIGITAL | IOD_SS2_disk | D364 | [8 empty] | 0x0fc015c0
SS2PMM2Phase1Current39_nad80 | DIGITAL | IOD_SS2_disk | D365 | [8 empty] | 0x0fc015d0
SS2PMM2Phase1Current40_nad80 | DIGITAL | IOD_SS2_disk | D366 | [8 empty] | 0x0fc015e0
SS2PMM2Phase1Current41_nad80 | DIGITAL | IOD_SS2_disk | D367 | [8 empty] | 0x0fc015f0
SS2PMM2Phase1Current42_nad80 | DIGITAL | IOD_SS2_disk | D368 | [8 empty] | 0x0fc01600
SS2PMM2PoljeFazaATok1_16_nad80 | DIGITAL | IOD_SS2_disk | D537 | [8 empty] | 0x0fc01610
SS2PMM2PoljeFazaATok17_32_nad80 | DIGITAL | IOD_SS2_disk | D538 | [8 empty] | 0x0fc01620
SS2PMM2PoljeFazaATok33_42_nad80 | DIGITAL | IOD_SS2_disk | D539 | [8 empty] | 0x0fc01630
SS2PMM2PoljeFazaBTok1_16_nad80 | DIGITAL | IOD_SS2_disk | D540 | [8 empty] | 0x0fc01640
SS2PMM2PoljeFazaBTok17_32_nad80 | DIGITAL | IOD_SS2_disk | D541 | [8 empty] | 0x0fc01650
SS2PMM2PoljeFazaBTok33_42_nad80 | DIGITAL | IOD_SS2_disk | D542 | [8 empty] | 0x0fc01660
SS2PMM2PoljeFazaCTok1_16_nad80 | DIGITAL | IOD_SS2_disk | D543 | [8 empty] | 0x0fc01670
SS2PMM2PoljeFazaCTok17_32_nad80 | DIGITAL | IOD_SS2_disk | D544 | [8 empty] | 0x0fc01680
SS2PMM2PoljeFazaCTok33_42_nad80 | DIGITAL | IOD_SS2_disk | D545 | [8 empty] | 0x0fc01690
SS2PMM2PoljeFazaATok1_16_med60_80 | DIGITAL | IOD_SS2_disk | D546 | [8 empty] | 0x0fc016a0
SS2PMM2PoljeFazaATok17_32_med60_80 | DIGITAL | IOD_SS2_disk | D547 | [8 empty] | 0x0fc016b0
SS2PMM2PoljeFazaATok33_42_med60_80 | DIGITAL | IOD_SS2_disk | D548 | [8 empty] | 0x0fc016c0
SS2PMM2PoljeFazaBTok1_16_med60_80 | DIGITAL | IOD_SS2_disk | D549 | [8 empty] | 0x0fc016d0
SS2PMM2PoljeFazaBTok17_32_med60_80 | DIGITAL | IOD_SS2_disk | D550 | [8 empty] | 0x0fc016e0
SS2PMM2PoljeFazaBTok33_42_med60_80 | DIGITAL | IOD_SS2_disk | D551 | [8 empty] | 0x0fc016f0
SS2PMM2PoljeFazaCTok1_16_med60_80 | DIGITAL | IOD_SS2_disk | D552 | [8 empty] | 0x0fc01700
SS2PMM2PoljeFazaCTok17_32_med60_80 | DIGITAL | IOD_SS2_disk | D553 | [8 empty] | 0x0fc01710
SS2PMM2PoljeFazaCTok33_42_med60_80 | DIGITAL | IOD_SS2_disk | D554 | [8 empty] | 0x0fc01720
SS2PMM_2x63_VirA_zavihek | DIGITAL | IOD_SS2_disk | D555 | [8 empty] | 0x0fc01730
SS2PMM_2x63_VirB_zavihek | DIGITAL | IOD_SS2_disk | D556 | [8 empty] | 0x0fc01740
SS2PMM_2x17_VirA_zavihek | DIGITAL | IOD_SS2_disk | D557 | [8 empty] | 0x0fc01750
SS2PMM_2x17_VirB_zavihek | DIGITAL | IOD_SS2_disk | D558 | [8 empty] | 0x0fc01760
ASS2_Omogoci_SMS_Alarm | DIGITAL | IOD_SS2_disk | D600[299] | [8 empty] | 0x0fc01770
BSS2_Omogoci_SMS_Alarm | DIGITAL | IOD_SS2_disk | D900[299] | [8 empty] | 0x0fc01780
CSS2_Omogoci_SMS_Alarm | DIGITAL | IOD_SS2_disk | D1200[299] | [8 empty] | 0x0fc01790
DSS2_Omogoci_SMS_Alarm | DIGITAL | IOD_SS2_disk | D1500[299] | [8 empty] | 0x0fc017a0
ESS2_Omogoci_SMS_Alarm | DIGITAL | IOD_SS2_disk | D1800[299] | [8 empty] | 0x0fc017b0
FSS2_Omogoci_SMS_Alarm | DIGITAL | IOD_SS2_disk | D2100[299] | [8 empty] | 0x0fc017c0
SS2AlarmUPSKrmOmara_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D2500 | [8 empty] | 0x0fc017d0
SS2StanjeUPSKrmOmara_BaterijskiNacin_Omogoci | DIGITAL | IOD_SS2_disk | D2501 | [8 empty] | 0x0fc017e0
SS2StanjeUPSKrmOmara_Polnjenje_Omogoci | DIGITAL | IOD_SS2_disk | D2502 | [8 empty] | 0x0fc017f0
SS2NapakaSenzorTemp1_Omogoci | DIGITAL | IOD_SS2_disk | D2503 | [8 empty] | 0x0fc01800
SS2NapakaSenzorTemp2_Omogoci | DIGITAL | IOD_SS2_disk | D2504 | [8 empty] | 0x0fc01810
SS2NapakaSenzorTemp3_Omogoci | DIGITAL | IOD_SS2_disk | D2505 | [8 empty] | 0x0fc01820
SS2NapakaSenzorTemp4_Omogoci | DIGITAL | IOD_SS2_disk | D2506 | [8 empty] | 0x0fc01830
SS2NapakaSenzorVlaga1_Omogoci | DIGITAL | IOD_SS2_disk | D2507 | [8 empty] | 0x0fc01840
SS2NapakaSenzorVlaga2_Omogoci | DIGITAL | IOD_SS2_disk | D2508 | [8 empty] | 0x0fc01850
SS2NapakaSenzorVlaga3_Omogoci | DIGITAL | IOD_SS2_disk | D2509 | [8 empty] | 0x0fc01860
SS2NapakaSenzorVlaga4_Omogoci | DIGITAL | IOD_SS2_disk | D2510 | [8 empty] | 0x0fc01870
SS2AlarmLAH1RazlitjeVode_Omogoci | DIGITAL | IOD_SS2_disk | D2511 | [8 empty] | 0x0fc01880
SS2AlarmLAH2RazlitjeVode_Omogoci | DIGITAL | IOD_SS2_disk | D2512 | [8 empty] | 0x0fc01890
SS2AlarmLAH3RazlitjeVode_Omogoci | DIGITAL | IOD_SS2_disk | D2513 | [8 empty] | 0x0fc018a0
SS2AlarmKlimat2_1_Napaka_Omogoci | DIGITAL | IOD_SS2_disk | D2514 | [8 empty] | 0x0fc018b0
SS2AlarmKlimat2_2_Napaka_Omogoci | DIGITAL | IOD_SS2_disk | D2515 | [8 empty] | 0x0fc018c0
SS2AlarmKlimat2_3_Napaka_Omogoci | DIGITAL | IOD_SS2_disk | D2516 | [8 empty] | 0x0fc018d0
SS2AlarmKlimat2_4_Napaka_Omogoci | DIGITAL | IOD_SS2_disk | D2517 | [8 empty] | 0x0fc018e0
SS2AlarmKlimat2_5_Napaka_Omogoci | DIGITAL | IOD_SS2_disk | D2518 | [8 empty] | 0x0fc018f0
SS2AlarmKlimat2_6_Napaka_Omogoci | DIGITAL | IOD_SS2_disk | D2519 | [8 empty] | 0x0fc01900
SS2PMM1OverCurrentBetw1_Omogoci | DIGITAL | IOD_SS2_disk | D2521 | [8 empty] | 0x0fc01910
SS2PMM1OverCurrentBetw2_Omogoci | DIGITAL | IOD_SS2_disk | D2522 | [8 empty] | 0x0fc01920
SS2PMM1OverCurrentBetw3_Omogoci | DIGITAL | IOD_SS2_disk | D2523 | [8 empty] | 0x0fc01930
SS2PMM1OverCurrentOver1_Omogoci | DIGITAL | IOD_SS2_disk | D2524 | [8 empty] | 0x0fc01940
SS2PMM1OverCurrentOver2_Omogoci | DIGITAL | IOD_SS2_disk | D2525 | [8 empty] | 0x0fc01950
SS2PMM1OverCurrentOver3_Omogoci | DIGITAL | IOD_SS2_disk | D2526 | [8 empty] | 0x0fc01960
SS2PMM2OverCurrentBetw1_Omogoci | DIGITAL | IOD_SS2_disk | D2528 | [8 empty] | 0x0fc01970
SS2PMM2OverCurrentBetw2_Omogoci | DIGITAL | IOD_SS2_disk | D2529 | [8 empty] | 0x0fc01980
SS2PMM2OverCurrentBetw3_Omogoci | DIGITAL | IOD_SS2_disk | D2530 | [8 empty] | 0x0fc01990
SS2PMM2OverCurrentOver1_Omogoci | DIGITAL | IOD_SS2_disk | D2531 | [8 empty] | 0x0fc019a0
SS2PMM2OverCurrentOver2_Omogoci | DIGITAL | IOD_SS2_disk | D2532 | [8 empty] | 0x0fc019b0
SS2PMM2OverCurrentOver3_Omogoci | DIGITAL | IOD_SS2_disk | D2533 | [8 empty] | 0x0fc019c0
SS2ErrComPMM1_Omogoci | DIGITAL | IOD_SS2_disk | D2534 | [8 empty] | 0x0fc019d0
SS2ErrComPMM2_Omogoci | DIGITAL | IOD_SS2_disk | D2535 | [8 empty] | 0x0fc019e0
SS2ErrComKlima1_Omogoci | DIGITAL | IOD_SS2_disk | D2536 | [8 empty] | 0x0fc019f0
SS2ErrComKlima2_Omogoci | DIGITAL | IOD_SS2_disk | D2537 | [8 empty] | 0x0fc01a00
SS2ErrComKlima3_Omogoci | DIGITAL | IOD_SS2_disk | D2538 | [8 empty] | 0x0fc01a10
SS2ErrComKlima4_Omogoci | DIGITAL | IOD_SS2_disk | D2539 | [8 empty] | 0x0fc01a20
SS2ErrComKlima5_Omogoci | DIGITAL | IOD_SS2_disk | D2540 | [8 empty] | 0x0fc01a30
SS2ErrComKlima6_Omogoci | DIGITAL | IOD_SS2_disk | D2541 | [8 empty] | 0x0fc01a40
SS2ErrComPanelPLC_Omogoci | DIGITAL | IOD_SS2_disk | D2542 | [8 empty] | 0x0fc01a50
SS2ErrCommScada_Omogoci | DIGITAL | IOD_SS2_disk | D2543 | [8 empty] | 0x0fc01a60
SS2OpozoriloBaterijaPLC_Omogoci | DIGITAL | IOD_SS2_disk | D2544 | [8 empty] | 0x0fc01a70
SS2KlimaError1AlarmKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2545 | [8 empty] | 0x0fc01a80
SS2KlimaError1AlarmKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2546 | [8 empty] | 0x0fc01a90
SS2KlimaError1FenThermalCutout_Omogoci | DIGITAL | IOD_SS2_disk | D2547 | [8 empty] | 0x0fc01aa0
SS2KlimaError1IzlivVode_Omogoci | DIGITAL | IOD_SS2_disk | D2548 | [8 empty] | 0x0fc01ab0
SS2KlimaError1Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2549 | [8 empty] | 0x0fc01ac0
SS2KlimaError1Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2550 | [8 empty] | 0x0fc01ad0
SS2KlimaError1NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS2_disk | D2553 | [8 empty] | 0x0fc01ae0
SS2KlimaError1NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS2_disk | D2554 | [8 empty] | 0x0fc01af0
SS2KlimaError1NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS2_disk | D2556 | [8 empty] | 0x0fc01b00
SS2KlimaError1NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS2_disk | D2557 | [8 empty] | 0x0fc01b10
SS2KlimaError1NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2560 | [8 empty] | 0x0fc01b20
SS2KlimaError1NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2561 | [8 empty] | 0x0fc01b30
SS2KlimaError1NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2562 | [8 empty] | 0x0fc01b40
SS2KlimaError1NizkaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2563 | [8 empty] | 0x0fc01b50
SS2KlimaError1PozarniAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2564 | [8 empty] | 0x0fc01b60
SS2KlimaError1ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS2_disk | D2567 | [8 empty] | 0x0fc01b70
SS2KlimaError1ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS2_disk | D2568 | [8 empty] | 0x0fc01b80
SS2KlimaError1VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2569 | [8 empty] | 0x0fc01b90
SS2KlimaError1VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2570 | [8 empty] | 0x0fc01ba0
SS2KlimaError1VisokaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2571 | [8 empty] | 0x0fc01bb0
SS2KlimaError1VisokPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2572 | [8 empty] | 0x0fc01bc0
SS2KlimaError1VisokPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2573 | [8 empty] | 0x0fc01bd0
SS2KlimaError1NapakaVlazilca_Omogoci | DIGITAL | IOD_SS2_disk | D2574 | [8 empty] | 0x0fc01be0
SS2KlimaError1ZamasenFilter_Omogoci | DIGITAL | IOD_SS2_disk | D2576 | [8 empty] | 0x0fc01bf0
SS2KlimaError1ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2577 | [8 empty] | 0x0fc01c00
SS2KlimaError2AlarmKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2578 | [8 empty] | 0x0fc01c10
SS2KlimaError2AlarmKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2579 | [8 empty] | 0x0fc01c20
SS2KlimaError2FenThermalCutout_Omogoci | DIGITAL | IOD_SS2_disk | D2580 | [8 empty] | 0x0fc01c30
SS2KlimaError2IzlivVode_Omogoci | DIGITAL | IOD_SS2_disk | D2581 | [8 empty] | 0x0fc01c40
SS2KlimaError2Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2582 | [8 empty] | 0x0fc01c50
SS2KlimaError2Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2583 | [8 empty] | 0x0fc01c60
SS2KlimaError2NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS2_disk | D2586 | [8 empty] | 0x0fc01c70
SS2KlimaError2NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS2_disk | D2587 | [8 empty] | 0x0fc01c80
SS2KlimaError2NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS2_disk | D2589 | [8 empty] | 0x0fc01c90
SS2KlimaError2NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS2_disk | D2590 | [8 empty] | 0x0fc01ca0
SS2KlimaError2NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2593 | [8 empty] | 0x0fc01cb0
SS2KlimaError2NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2594 | [8 empty] | 0x0fc01cc0
SS2KlimaError2NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2595 | [8 empty] | 0x0fc01cd0
SS2KlimaError2NizkaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2596 | [8 empty] | 0x0fc01ce0
SS2KlimaError2PozarniAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2597 | [8 empty] | 0x0fc01cf0
SS2KlimaError2ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS2_disk | D2600 | [8 empty] | 0x0fc01d00
SS2KlimaError2ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS2_disk | D2601 | [8 empty] | 0x0fc01d10
SS2KlimaError2VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2602 | [8 empty] | 0x0fc01d20
SS2KlimaError2VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2603 | [8 empty] | 0x0fc01d30
SS2KlimaError2VisokaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2604 | [8 empty] | 0x0fc01d40
SS2KlimaError2VisokPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2605 | [8 empty] | 0x0fc01d50
SS2KlimaError2VisokPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2606 | [8 empty] | 0x0fc01d60
SS2KlimaError2NapakaVlazilca_Omogoci | DIGITAL | IOD_SS2_disk | D2607 | [8 empty] | 0x0fc01d70
SS2KlimaError2ZamasenFilter_Omogoci | DIGITAL | IOD_SS2_disk | D2609 | [8 empty] | 0x0fc01d80
SS2KlimaError2ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2610 | [8 empty] | 0x0fc01d90
SS2KlimaError3AlarmKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2611 | [8 empty] | 0x0fc01da0
SS2KlimaError3AlarmKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2612 | [8 empty] | 0x0fc01db0
SS2KlimaError3FenThermalCutout_Omogoci | DIGITAL | IOD_SS2_disk | D2613 | [8 empty] | 0x0fc01dc0
SS2KlimaError3IzlivVode_Omogoci | DIGITAL | IOD_SS2_disk | D2614 | [8 empty] | 0x0fc01dd0
SS2KlimaError3Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2615 | [8 empty] | 0x0fc01de0
SS2KlimaError3Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2616 | [8 empty] | 0x0fc01df0
SS2KlimaError3NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS2_disk | D2619 | [8 empty] | 0x0fc01e00
SS2KlimaError3NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS2_disk | D2620 | [8 empty] | 0x0fc01e10
SS2KlimaError3NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS2_disk | D2622 | [8 empty] | 0x0fc01e20
SS2KlimaError3NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS2_disk | D2623 | [8 empty] | 0x0fc01e30
SS2KlimaError3NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2626 | [8 empty] | 0x0fc01e40
SS2KlimaError3NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2627 | [8 empty] | 0x0fc01e50
SS2KlimaError3NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2628 | [8 empty] | 0x0fc01e60
SS2KlimaError3NizkaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2629 | [8 empty] | 0x0fc01e70
SS2KlimaError3PozarniAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2630 | [8 empty] | 0x0fc01e80
SS2KlimaError3ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS2_disk | D2633 | [8 empty] | 0x0fc01e90
SS2KlimaError3ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS2_disk | D2634 | [8 empty] | 0x0fc01ea0
SS2KlimaError3VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2635 | [8 empty] | 0x0fc01eb0
SS2KlimaError3VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2636 | [8 empty] | 0x0fc01ec0
SS2KlimaError3VisokaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2637 | [8 empty] | 0x0fc01ed0
SS2KlimaError3VisokPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2638 | [8 empty] | 0x0fc01ee0
SS2KlimaError3VisokPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2639 | [8 empty] | 0x0fc01ef0
SS2KlimaError3NapakaVlazilca_Omogoci | DIGITAL | IOD_SS2_disk | D2640 | [8 empty] | 0x0fc01f00
SS2KlimaError3ZamasenFilter_Omogoci | DIGITAL | IOD_SS2_disk | D2642 | [8 empty] | 0x0fc01f10
SS2KlimaError3ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2643 | [8 empty] | 0x0fc01f20
SS2KlimaError4AlarmKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2644 | [8 empty] | 0x0fc01f30
SS2KlimaError4AlarmKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2645 | [8 empty] | 0x0fc01f40
SS2KlimaError4FenThermalCutout_Omogoci | DIGITAL | IOD_SS2_disk | D2646 | [8 empty] | 0x0fc01f50
SS2KlimaError4IzlivVode_Omogoci | DIGITAL | IOD_SS2_disk | D2647 | [8 empty] | 0x0fc01f60
SS2KlimaError4Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2648 | [8 empty] | 0x0fc01f70
SS2KlimaError4Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2649 | [8 empty] | 0x0fc01f80
SS2KlimaError4NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS2_disk | D2652 | [8 empty] | 0x0fc01f90
SS2KlimaError4NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS2_disk | D2653 | [8 empty] | 0x0fc01fa0
SS2KlimaError4NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS2_disk | D2655 | [8 empty] | 0x0fc01fb0
SS2KlimaError4NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS2_disk | D2656 | [8 empty] | 0x0fc01fc0
SS2KlimaError4NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2659 | [8 empty] | 0x0fc01fd0
SS2KlimaError4NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2660 | [8 empty] | 0x0fc01fe0
SS2KlimaError4NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2661 | [8 empty] | 0x0fc01ff0
SS2KlimaError4NizkaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2662 | [8 empty] | 0x0fc02000
SS2KlimaError4PozarniAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2663 | [8 empty] | 0x0fc02010
SS2KlimaError4ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS2_disk | D2666 | [8 empty] | 0x0fc02020
SS2KlimaError4ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS2_disk | D2667 | [8 empty] | 0x0fc02030
SS2KlimaError4VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2668 | [8 empty] | 0x0fc02040
SS2KlimaError4VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2669 | [8 empty] | 0x0fc02050
SS2KlimaError4VisokaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2670 | [8 empty] | 0x0fc02060
SS2KlimaError4VisokPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2671 | [8 empty] | 0x0fc02070
SS2KlimaError4VisokPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2672 | [8 empty] | 0x0fc02080
SS2KlimaError4NapakaVlazilca_Omogoci | DIGITAL | IOD_SS2_disk | D2673 | [8 empty] | 0x0fc02090
SS2KlimaError4ZamasenFilter_Omogoci | DIGITAL | IOD_SS2_disk | D2675 | [8 empty] | 0x0fc020a0
SS2KlimaError4ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2676 | [8 empty] | 0x0fc020b0
SS2KlimaError5AlarmKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2677 | [8 empty] | 0x0fc020c0
SS2KlimaError5AlarmKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2678 | [8 empty] | 0x0fc020d0
SS2KlimaError5FenThermalCutout_Omogoci | DIGITAL | IOD_SS2_disk | D2679 | [8 empty] | 0x0fc020e0
SS2KlimaError5IzlivVode_Omogoci | DIGITAL | IOD_SS2_disk | D2680 | [8 empty] | 0x0fc020f0
SS2KlimaError5Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2681 | [8 empty] | 0x0fc02100
SS2KlimaError5Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2682 | [8 empty] | 0x0fc02110
SS2KlimaError5NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS2_disk | D2685 | [8 empty] | 0x0fc02120
SS2KlimaError5NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS2_disk | D2686 | [8 empty] | 0x0fc02130
SS2KlimaError5NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS2_disk | D2688 | [8 empty] | 0x0fc02140
SS2KlimaError5NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS2_disk | D2689 | [8 empty] | 0x0fc02150
SS2KlimaError5NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2692 | [8 empty] | 0x0fc02160
SS2KlimaError5NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2693 | [8 empty] | 0x0fc02170
SS2KlimaError5NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2694 | [8 empty] | 0x0fc02180
SS2KlimaError5NizkaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2695 | [8 empty] | 0x0fc02190
SS2KlimaError5PozarniAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2696 | [8 empty] | 0x0fc021a0
SS2KlimaError5ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS2_disk | D2699 | [8 empty] | 0x0fc021b0
SS2KlimaError5ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS2_disk | D2700 | [8 empty] | 0x0fc021c0
SS2KlimaError5VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2701 | [8 empty] | 0x0fc021d0
SS2KlimaError5VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2702 | [8 empty] | 0x0fc021e0
SS2KlimaError5VisokaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2703 | [8 empty] | 0x0fc021f0
SS2KlimaError5VisokPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2704 | [8 empty] | 0x0fc02200
SS2KlimaError5VisokPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2705 | [8 empty] | 0x0fc02210
SS2KlimaError5NapakaVlazilca_Omogoci | DIGITAL | IOD_SS2_disk | D2706 | [8 empty] | 0x0fc02220
SS2KlimaError5ZamasenFilter_Omogoci | DIGITAL | IOD_SS2_disk | D2708 | [8 empty] | 0x0fc02230
SS2KlimaError5ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2709 | [8 empty] | 0x0fc02240
SS2KlimaError6AlarmKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2710 | [8 empty] | 0x0fc02250
SS2KlimaError6AlarmKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2711 | [8 empty] | 0x0fc02260
SS2KlimaError6FenThermalCutout_Omogoci | DIGITAL | IOD_SS2_disk | D2712 | [8 empty] | 0x0fc02270
SS2KlimaError6IzlivVode_Omogoci | DIGITAL | IOD_SS2_disk | D2713 | [8 empty] | 0x0fc02280
SS2KlimaError6Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2714 | [8 empty] | 0x0fc02290
SS2KlimaError6Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2715 | [8 empty] | 0x0fc022a0
SS2KlimaError6NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS2_disk | D2718 | [8 empty] | 0x0fc022b0
SS2KlimaError6NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS2_disk | D2719 | [8 empty] | 0x0fc022c0
SS2KlimaError6NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS2_disk | D2721 | [8 empty] | 0x0fc022d0
SS2KlimaError6NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS2_disk | D2722 | [8 empty] | 0x0fc022e0
SS2KlimaError6NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2725 | [8 empty] | 0x0fc022f0
SS2KlimaError6NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2726 | [8 empty] | 0x0fc02300
SS2KlimaError6NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2727 | [8 empty] | 0x0fc02310
SS2KlimaError6NizkaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2728 | [8 empty] | 0x0fc02320
SS2KlimaError6PozarniAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2729 | [8 empty] | 0x0fc02330
SS2KlimaError6ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS2_disk | D2732 | [8 empty] | 0x0fc02340
SS2KlimaError6ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS2_disk | D2733 | [8 empty] | 0x0fc02350
SS2KlimaError6VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2734 | [8 empty] | 0x0fc02360
SS2KlimaError6VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2735 | [8 empty] | 0x0fc02370
SS2KlimaError6VisokaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2736 | [8 empty] | 0x0fc02380
SS2KlimaError6VisokPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2737 | [8 empty] | 0x0fc02390
SS2KlimaError6VisokPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2738 | [8 empty] | 0x0fc023a0
SS2KlimaError6NapakaVlazilca_Omogoci | DIGITAL | IOD_SS2_disk | D2739 | [8 empty] | 0x0fc023b0
SS2KlimaError6ZamasenFilter_Omogoci | DIGITAL | IOD_SS2_disk | D2741 | [8 empty] | 0x0fc023c0
SS2KlimaError6ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2742 | [8 empty] | 0x0fc023d0
SS2PMM1Phase1Current1_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2743 | [8 empty] | 0x0fc023e0
SS2PMM1Phase1Current2_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2744 | [8 empty] | 0x0fc023f0
SS2PMM1Phase1Current3_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2745 | [8 empty] | 0x0fc02400
SS2PMM1Phase1Current4_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2746 | [8 empty] | 0x0fc02410
SS2PMM1Phase1Current5_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2747 | [8 empty] | 0x0fc02420
SS2PMM1Phase1Current6_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2748 | [8 empty] | 0x0fc02430
SS2PMM1Phase1Current7_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2749 | [8 empty] | 0x0fc02440
SS2PMM1Phase1Current8_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2750 | [8 empty] | 0x0fc02450
SS2PMM1Phase1Current9_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2751 | [8 empty] | 0x0fc02460
SS2PMM1Phase1Current10_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2752 | [8 empty] | 0x0fc02470
SS2PMM1Phase1Current11_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2753 | [8 empty] | 0x0fc02480
SS2PMM1Phase1Current12_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2754 | [8 empty] | 0x0fc02490
SS2PMM1Phase1Current13_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2755 | [8 empty] | 0x0fc024a0
SS2PMM1Phase1Current14_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2756 | [8 empty] | 0x0fc024b0
SS2PMM1Phase1Current15_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2757 | [8 empty] | 0x0fc024c0
SS2PMM1Phase1Current16_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2758 | [8 empty] | 0x0fc024d0
SS2PMM1Phase1Current17_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2759 | [8 empty] | 0x0fc024e0
SS2PMM1Phase1Current18_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2760 | [8 empty] | 0x0fc024f0
SS2PMM1Phase1Current19_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2761 | [8 empty] | 0x0fc02500
SS2PMM1Phase1Current20_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2762 | [8 empty] | 0x0fc02510
SS2PMM1Phase1Current21_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2763 | [8 empty] | 0x0fc02520
SS2PMM1Phase1Current22_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2764 | [8 empty] | 0x0fc02530
SS2PMM1Phase1Current23_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2765 | [8 empty] | 0x0fc02540
SS2PMM1Phase1Current24_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2766 | [8 empty] | 0x0fc02550
SS2PMM1Phase1Current25_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2767 | [8 empty] | 0x0fc02560
SS2PMM1Phase1Current26_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2768 | [8 empty] | 0x0fc02570
SS2PMM1Phase1Current27_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2769 | [8 empty] | 0x0fc02580
SS2PMM1Phase1Current28_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2770 | [8 empty] | 0x0fc02590
SS2PMM1Phase1Current29_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2771 | [8 empty] | 0x0fc025a0
SS2PMM1Phase1Current30_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2772 | [8 empty] | 0x0fc025b0
SS2PMM1Phase1Current31_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2773 | [8 empty] | 0x0fc025c0
SS2PMM1Phase1Current32_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2774 | [8 empty] | 0x0fc025d0
SS2PMM1Phase1Current33_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2775 | [8 empty] | 0x0fc025e0
SS2PMM1Phase1Current34_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2776 | [8 empty] | 0x0fc025f0
SS2PMM1Phase1Current35_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2777 | [8 empty] | 0x0fc02600
SS2PMM1Phase1Current36_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2778 | [8 empty] | 0x0fc02610
SS2PMM1Phase1Current37_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2779 | [8 empty] | 0x0fc02620
SS2PMM1Phase1Current38_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2780 | [8 empty] | 0x0fc02630
SS2PMM1Phase1Current39_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2781 | [8 empty] | 0x0fc02640
SS2PMM1Phase1Current40_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2782 | [8 empty] | 0x0fc02650
SS2PMM1Phase1Current41_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2783 | [8 empty] | 0x0fc02660
SS2PMM1Phase1Current42_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2784 | [8 empty] | 0x0fc02670
SS2PMM1Phase2Current1_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2785 | [8 empty] | 0x0fc02680
SS2PMM1Phase2Current2_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2786 | [8 empty] | 0x0fc02690
SS2PMM1Phase2Current3_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2787 | [8 empty] | 0x0fc026a0
SS2PMM1Phase2Current4_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2788 | [8 empty] | 0x0fc026b0
SS2PMM1Phase2Current5_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2789 | [8 empty] | 0x0fc026c0
SS2PMM1Phase2Current6_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2790 | [8 empty] | 0x0fc026d0
SS2PMM1Phase2Current7_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2791 | [8 empty] | 0x0fc026e0
SS2PMM1Phase2Current8_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2792 | [8 empty] | 0x0fc026f0
SS2PMM1Phase2Current9_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2793 | [8 empty] | 0x0fc02700
SS2PMM1Phase2Current10_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2794 | [8 empty] | 0x0fc02710
SS2PMM1Phase2Current11_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2795 | [8 empty] | 0x0fc02720
SS2PMM1Phase2Current12_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2796 | [8 empty] | 0x0fc02730
SS2PMM1Phase2Current13_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2797 | [8 empty] | 0x0fc02740
SS2PMM1Phase2Current14_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2798 | [8 empty] | 0x0fc02750
SS2PMM1Phase2Current15_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2799 | [8 empty] | 0x0fc02760
SS2PMM1Phase2Current16_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2800 | [8 empty] | 0x0fc02770
SS2PMM1Phase2Current17_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2801 | [8 empty] | 0x0fc02780
SS2PMM1Phase2Current18_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2802 | [8 empty] | 0x0fc02790
SS2PMM1Phase2Current19_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2803 | [8 empty] | 0x0fc027a0
SS2PMM1Phase2Current20_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2804 | [8 empty] | 0x0fc027b0
SS2PMM1Phase2Current21_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2805 | [8 empty] | 0x0fc027c0
SS2PMM1Phase2Current22_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2806 | [8 empty] | 0x0fc027d0
SS2PMM1Phase2Current23_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2807 | [8 empty] | 0x0fc027e0
SS2PMM1Phase2Current24_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2808 | [8 empty] | 0x0fc027f0
SS2PMM1Phase2Current25_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2809 | [8 empty] | 0x0fc02800
SS2PMM1Phase2Current26_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2810 | [8 empty] | 0x0fc02810
SS2PMM1Phase2Current27_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2811 | [8 empty] | 0x0fc02820
SS2PMM1Phase2Current28_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2812 | [8 empty] | 0x0fc02830
SS2PMM1Phase2Current29_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2813 | [8 empty] | 0x0fc02840
SS2PMM1Phase2Current30_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2814 | [8 empty] | 0x0fc02850
SS2PMM1Phase2Current31_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2815 | [8 empty] | 0x0fc02860
SS2PMM1Phase2Current32_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2816 | [8 empty] | 0x0fc02870
SS2PMM1Phase2Current33_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2817 | [8 empty] | 0x0fc02880
SS2PMM1Phase2Current34_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2818 | [8 empty] | 0x0fc02890
SS2PMM1Phase2Current35_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2819 | [8 empty] | 0x0fc028a0
SS2PMM1Phase2Current36_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2820 | [8 empty] | 0x0fc028b0
SS2PMM1Phase2Current37_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2821 | [8 empty] | 0x0fc028c0
SS2PMM1Phase2Current38_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2822 | [8 empty] | 0x0fc028d0
SS2PMM1Phase2Current39_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2823 | [8 empty] | 0x0fc028e0
SS2PMM1Phase2Current40_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2824 | [8 empty] | 0x0fc028f0
SS2PMM1Phase2Current41_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2825 | [8 empty] | 0x0fc02900
SS2PMM1Phase2Current42_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2826 | [8 empty] | 0x0fc02910
SS2PMM1Phase3Current1_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2827 | [8 empty] | 0x0fc02920
SS2PMM1Phase3Current2_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2828 | [8 empty] | 0x0fc02930
SS2PMM1Phase3Current3_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2829 | [8 empty] | 0x0fc02940
SS2PMM1Phase3Current4_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2830 | [8 empty] | 0x0fc02950
SS2PMM1Phase3Current5_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2831 | [8 empty] | 0x0fc02960
SS2PMM1Phase3Current6_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2832 | [8 empty] | 0x0fc02970
SS2PMM1Phase3Current7_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2833 | [8 empty] | 0x0fc02980
SS2PMM1Phase3Current8_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2834 | [8 empty] | 0x0fc02990
SS2PMM1Phase3Current9_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2835 | [8 empty] | 0x0fc029a0
SS2PMM1Phase3Current10_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2836 | [8 empty] | 0x0fc029b0
SS2PMM1Phase3Current11_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2837 | [8 empty] | 0x0fc029c0
SS2PMM1Phase3Current12_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2838 | [8 empty] | 0x0fc029d0
SS2PMM1Phase3Current13_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2839 | [8 empty] | 0x0fc029e0
SS2PMM1Phase3Current14_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2840 | [8 empty] | 0x0fc029f0
SS2PMM1Phase3Current15_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2841 | [8 empty] | 0x0fc02a00
SS2PMM1Phase3Current16_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2842 | [8 empty] | 0x0fc02a10
SS2PMM1Phase3Current17_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2843 | [8 empty] | 0x0fc02a20
SS2PMM1Phase3Current18_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2844 | [8 empty] | 0x0fc02a30
SS2PMM1Phase3Current19_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2845 | [8 empty] | 0x0fc02a40
SS2PMM1Phase3Current20_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2846 | [8 empty] | 0x0fc02a50
SS2PMM1Phase3Current21_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2847 | [8 empty] | 0x0fc02a60
SS2PMM1Phase3Current22_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2848 | [8 empty] | 0x0fc02a70
SS2PMM1Phase3Current23_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2849 | [8 empty] | 0x0fc02a80
SS2PMM1Phase3Current24_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2850 | [8 empty] | 0x0fc02a90
SS2PMM1Phase3Current25_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2851 | [8 empty] | 0x0fc02aa0
SS2PMM1Phase3Current26_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2852 | [8 empty] | 0x0fc02ab0
SS2PMM1Phase3Current27_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2853 | [8 empty] | 0x0fc02ac0
SS2PMM1Phase3Current28_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2854 | [8 empty] | 0x0fc02ad0
SS2PMM1Phase3Current29_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2855 | [8 empty] | 0x0fc02ae0
SS2PMM1Phase3Current30_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2856 | [8 empty] | 0x0fc02af0
SS2PMM1Phase3Current31_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2857 | [8 empty] | 0x0fc02b00
SS2PMM1Phase3Current32_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2858 | [8 empty] | 0x0fc02b10
SS2PMM1Phase3Current33_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2859 | [8 empty] | 0x0fc02b20
SS2PMM1Phase3Current34_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2860 | [8 empty] | 0x0fc02b30
SS2PMM1Phase3Current35_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2861 | [8 empty] | 0x0fc02b40
SS2PMM1Phase3Current36_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2862 | [8 empty] | 0x0fc02b50
SS2PMM1Phase3Current37_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2863 | [8 empty] | 0x0fc02b60
SS2PMM1Phase3Current38_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2864 | [8 empty] | 0x0fc02b70
SS2PMM1Phase3Current39_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2865 | [8 empty] | 0x0fc02b80
SS2PMM1Phase3Current40_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2866 | [8 empty] | 0x0fc02b90
SS2PMM1Phase3Current41_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2867 | [8 empty] | 0x0fc02ba0
SS2PMM1Phase3Current42_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2868 | [8 empty] | 0x0fc02bb0
SS2PMM2Phase1Current1_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2869 | [8 empty] | 0x0fc02bc0
SS2PMM2Phase1Current2_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2870 | [8 empty] | 0x0fc02bd0
SS2PMM2Phase1Current3_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2871 | [8 empty] | 0x0fc02be0
SS2PMM2Phase1Current4_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2872 | [8 empty] | 0x0fc02bf0
SS2PMM2Phase1Current5_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2873 | [8 empty] | 0x0fc02c00
SS2PMM2Phase1Current6_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2874 | [8 empty] | 0x0fc02c10
SS2PMM2Phase1Current7_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2875 | [8 empty] | 0x0fc02c20
SS2PMM2Phase1Current8_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2876 | [8 empty] | 0x0fc02c30
SS2PMM2Phase1Current9_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2877 | [8 empty] | 0x0fc02c40
SS2PMM2Phase1Current10_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2878 | [8 empty] | 0x0fc02c50
SS2PMM2Phase1Current11_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2879 | [8 empty] | 0x0fc02c60
SS2PMM2Phase1Current12_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2880 | [8 empty] | 0x0fc02c70
SS2PMM2Phase1Current13_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2881 | [8 empty] | 0x0fc02c80
SS2PMM2Phase1Current14_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2882 | [8 empty] | 0x0fc02c90
SS2PMM2Phase1Current15_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2883 | [8 empty] | 0x0fc02ca0
SS2PMM2Phase1Current16_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2884 | [8 empty] | 0x0fc02cb0
SS2PMM2Phase1Current17_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2885 | [8 empty] | 0x0fc02cc0
SS2PMM2Phase1Current18_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2886 | [8 empty] | 0x0fc02cd0
SS2PMM2Phase1Current19_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2887 | [8 empty] | 0x0fc02ce0
SS2PMM2Phase1Current20_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2888 | [8 empty] | 0x0fc02cf0
SS2PMM2Phase1Current21_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2889 | [8 empty] | 0x0fc02d00
SS2PMM2Phase1Current22_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2890 | [8 empty] | 0x0fc02d10
SS2PMM2Phase1Current23_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2891 | [8 empty] | 0x0fc02d20
SS2PMM2Phase1Current24_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2892 | [8 empty] | 0x0fc02d30
SS2PMM2Phase1Current25_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2893 | [8 empty] | 0x0fc02d40
SS2PMM2Phase1Current26_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2894 | [8 empty] | 0x0fc02d50
SS2PMM2Phase1Current27_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2895 | [8 empty] | 0x0fc02d60
SS2PMM2Phase1Current28_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2896 | [8 empty] | 0x0fc02d70
SS2PMM2Phase1Current29_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2897 | [8 empty] | 0x0fc02d80
SS2PMM2Phase1Current30_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2898 | [8 empty] | 0x0fc02d90
SS2PMM2Phase1Current31_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2899 | [8 empty] | 0x0fc02da0
SS2PMM2Phase1Current32_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2900 | [8 empty] | 0x0fc02db0
SS2PMM2Phase1Current33_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2901 | [8 empty] | 0x0fc02dc0
SS2PMM2Phase1Current34_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2902 | [8 empty] | 0x0fc02dd0
SS2PMM2Phase1Current35_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2903 | [8 empty] | 0x0fc02de0
SS2PMM2Phase1Current36_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2904 | [8 empty] | 0x0fc02df0
SS2PMM2Phase1Current37_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2905 | [8 empty] | 0x0fc02e00
SS2PMM2Phase1Current38_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2906 | [8 empty] | 0x0fc02e10
SS2PMM2Phase1Current39_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2907 | [8 empty] | 0x0fc02e20
SS2PMM2Phase1Current40_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2908 | [8 empty] | 0x0fc02e30
SS2PMM2Phase1Current41_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2909 | [8 empty] | 0x0fc02e40
SS2PMM2Phase1Current42_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2910 | [8 empty] | 0x0fc02e50
SS2PMM1Phase1Current1_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D2995 | [8 empty] | 0x0fc02e60
SS2PMM1Phase1Current2_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D2996 | [8 empty] | 0x0fc02e70
SS2PMM1Phase1Current3_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D2997 | [8 empty] | 0x0fc02e80
SS2PMM1Phase1Current4_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D2998 | [8 empty] | 0x0fc02e90
SS2PMM1Phase1Current5_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D2999 | [8 empty] | 0x0fc02ea0
SS2PMM1Phase1Current6_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3000 | [8 empty] | 0x0fc02eb0
SS2PMM1Phase1Current7_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3001 | [8 empty] | 0x0fc02ec0
SS2PMM1Phase1Current8_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3002 | [8 empty] | 0x0fc02ed0
SS2PMM1Phase1Current9_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3003 | [8 empty] | 0x0fc02ee0
SS2PMM1Phase1Current10_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3004 | [8 empty] | 0x0fc02ef0
SS2PMM1Phase1Current11_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3005 | [8 empty] | 0x0fc02f00
SS2PMM1Phase1Current12_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3006 | [8 empty] | 0x0fc02f10
SS2PMM1Phase1Current13_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3007 | [8 empty] | 0x0fc02f20
SS2PMM1Phase1Current14_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3008 | [8 empty] | 0x0fc02f30
SS2PMM1Phase1Current15_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3009 | [8 empty] | 0x0fc02f40
SS2PMM1Phase1Current16_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3010 | [8 empty] | 0x0fc02f50
SS2PMM1Phase1Current17_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3011 | [8 empty] | 0x0fc02f60
SS2PMM1Phase1Current18_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3012 | [8 empty] | 0x0fc02f70
SS2PMM1Phase1Current19_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3013 | [8 empty] | 0x0fc02f80
SS2PMM1Phase1Current20_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3014 | [8 empty] | 0x0fc02f90
SS2PMM1Phase1Current21_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3015 | [8 empty] | 0x0fc02fa0
SS2PMM1Phase1Current22_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3016 | [8 empty] | 0x0fc02fb0
SS2PMM1Phase1Current23_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3017 | [8 empty] | 0x0fc02fc0
SS2PMM1Phase1Current24_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3018 | [8 empty] | 0x0fc02fd0
SS2PMM1Phase1Current25_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3019 | [8 empty] | 0x0fc02fe0
SS2PMM1Phase1Current26_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3020 | [8 empty] | 0x0fc02ff0
SS2PMM1Phase1Current27_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3021 | [8 empty] | 0x0fc03000
SS2PMM1Phase1Current28_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3022 | [8 empty] | 0x0fc03010
SS2PMM1Phase1Current29_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3023 | [8 empty] | 0x0fc03020
SS2PMM1Phase1Current30_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3024 | [8 empty] | 0x0fc03030
SS2PMM1Phase1Current31_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3025 | [8 empty] | 0x0fc03040
SS2PMM1Phase1Current32_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3026 | [8 empty] | 0x0fc03050
SS2PMM1Phase1Current33_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3027 | [8 empty] | 0x0fc03060
SS2PMM1Phase1Current34_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3028 | [8 empty] | 0x0fc03070
SS2PMM1Phase1Current35_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3029 | [8 empty] | 0x0fc03080
SS2PMM1Phase1Current36_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3030 | [8 empty] | 0x0fc03090
SS2PMM1Phase1Current37_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3031 | [8 empty] | 0x0fc030a0
SS2PMM1Phase1Current38_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3032 | [8 empty] | 0x0fc030b0
SS2PMM1Phase1Current39_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3033 | [8 empty] | 0x0fc030c0
SS2PMM1Phase1Current40_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3034 | [8 empty] | 0x0fc030d0
SS2PMM1Phase1Current41_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3035 | [8 empty] | 0x0fc030e0
SS2PMM1Phase1Current42_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3036 | [8 empty] | 0x0fc030f0
SS2PMM1Phase2Current1_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3037 | [8 empty] | 0x0fc03100
SS2PMM1Phase2Current2_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3038 | [8 empty] | 0x0fc03110
SS2PMM1Phase2Current3_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3039 | [8 empty] | 0x0fc03120
SS2PMM1Phase2Current4_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3040 | [8 empty] | 0x0fc03130
SS2PMM1Phase2Current5_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3041 | [8 empty] | 0x0fc03140
SS2PMM1Phase2Current6_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3042 | [8 empty] | 0x0fc03150
SS2PMM1Phase2Current7_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3043 | [8 empty] | 0x0fc03160
SS2PMM1Phase2Current8_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3044 | [8 empty] | 0x0fc03170
SS2PMM1Phase2Current9_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3045 | [8 empty] | 0x0fc03180
SS2PMM1Phase2Current10_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3046 | [8 empty] | 0x0fc03190
SS2PMM1Phase2Current11_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3047 | [8 empty] | 0x0fc031a0
SS2PMM1Phase2Current12_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3048 | [8 empty] | 0x0fc031b0
SS2PMM1Phase2Current13_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3049 | [8 empty] | 0x0fc031c0
SS2PMM1Phase2Current14_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3050 | [8 empty] | 0x0fc031d0
SS2PMM1Phase2Current15_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3051 | [8 empty] | 0x0fc031e0
SS2PMM1Phase2Current16_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3052 | [8 empty] | 0x0fc031f0
SS2PMM1Phase2Current17_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3053 | [8 empty] | 0x0fc03200
SS2PMM1Phase2Current18_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3054 | [8 empty] | 0x0fc03210
SS2PMM1Phase2Current19_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3055 | [8 empty] | 0x0fc03220
SS2PMM1Phase2Current20_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3056 | [8 empty] | 0x0fc03230
SS2PMM1Phase2Current21_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3057 | [8 empty] | 0x0fc03240
SS2PMM1Phase2Current22_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3058 | [8 empty] | 0x0fc03250
SS2PMM1Phase2Current23_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3059 | [8 empty] | 0x0fc03260
SS2PMM1Phase2Current24_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3060 | [8 empty] | 0x0fc03270
SS2PMM1Phase2Current25_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3061 | [8 empty] | 0x0fc03280
SS2PMM1Phase2Current26_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3062 | [8 empty] | 0x0fc03290
SS2PMM1Phase2Current27_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3063 | [8 empty] | 0x0fc032a0
SS2PMM1Phase2Current28_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3064 | [8 empty] | 0x0fc032b0
SS2PMM1Phase2Current29_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3065 | [8 empty] | 0x0fc032c0
SS2PMM1Phase2Current30_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3066 | [8 empty] | 0x0fc032d0
SS2PMM1Phase2Current31_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3067 | [8 empty] | 0x0fc032e0
SS2PMM1Phase2Current32_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3068 | [8 empty] | 0x0fc032f0
SS2PMM1Phase2Current33_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3069 | [8 empty] | 0x0fc03300
SS2PMM1Phase2Current34_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3070 | [8 empty] | 0x0fc03310
SS2PMM1Phase2Current35_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3071 | [8 empty] | 0x0fc03320
SS2PMM1Phase2Current36_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3072 | [8 empty] | 0x0fc03330
SS2PMM1Phase2Current37_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3073 | [8 empty] | 0x0fc03340
SS2PMM1Phase2Current38_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3074 | [8 empty] | 0x0fc03350
SS2PMM1Phase2Current39_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3075 | [8 empty] | 0x0fc03360
SS2PMM1Phase2Current40_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3076 | [8 empty] | 0x0fc03370
SS2PMM1Phase2Current41_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3077 | [8 empty] | 0x0fc03380
SS2PMM1Phase2Current42_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3078 | [8 empty] | 0x0fc03390
SS2PMM1Phase3Current1_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3079 | [8 empty] | 0x0fc033a0
SS2PMM1Phase3Current2_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3080 | [8 empty] | 0x0fc033b0
SS2PMM1Phase3Current3_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3081 | [8 empty] | 0x0fc033c0
SS2PMM1Phase3Current4_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3082 | [8 empty] | 0x0fc033d0
SS2PMM1Phase3Current5_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3083 | [8 empty] | 0x0fc033e0
SS2PMM1Phase3Current6_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3084 | [8 empty] | 0x0fc033f0
SS2PMM1Phase3Current7_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3085 | [8 empty] | 0x0fc03400
SS2PMM1Phase3Current8_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3086 | [8 empty] | 0x0fc03410
SS2PMM1Phase3Current9_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3087 | [8 empty] | 0x0fc03420
SS2PMM1Phase3Current10_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3088 | [8 empty] | 0x0fc03430
SS2PMM1Phase3Current11_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3089 | [8 empty] | 0x0fc03440
SS2PMM1Phase3Current12_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3090 | [8 empty] | 0x0fc03450
SS2PMM1Phase3Current13_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3091 | [8 empty] | 0x0fc03460
SS2PMM1Phase3Current14_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3092 | [8 empty] | 0x0fc03470
SS2PMM1Phase3Current15_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3093 | [8 empty] | 0x0fc03480
SS2PMM1Phase3Current16_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3094 | [8 empty] | 0x0fc03490
SS2PMM1Phase3Current17_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3095 | [8 empty] | 0x0fc034a0
SS2PMM1Phase3Current18_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3096 | [8 empty] | 0x0fc034b0
SS2PMM1Phase3Current19_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3097 | [8 empty] | 0x0fc034c0
SS2PMM1Phase3Current20_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3098 | [8 empty] | 0x0fc034d0
SS2PMM1Phase3Current21_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3099 | [8 empty] | 0x0fc034e0
SS2PMM1Phase3Current22_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3100 | [8 empty] | 0x0fc034f0
SS2PMM1Phase3Current23_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3101 | [8 empty] | 0x0fc03500
SS2PMM1Phase3Current24_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3102 | [8 empty] | 0x0fc03510
SS2PMM1Phase3Current25_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3103 | [8 empty] | 0x0fc03520
SS2PMM1Phase3Current26_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3104 | [8 empty] | 0x0fc03530
SS2PMM1Phase3Current27_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3105 | [8 empty] | 0x0fc03540
SS2PMM1Phase3Current28_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3106 | [8 empty] | 0x0fc03550
SS2PMM1Phase3Current29_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3107 | [8 empty] | 0x0fc03560
SS2PMM1Phase3Current30_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3108 | [8 empty] | 0x0fc03570
SS2PMM1Phase3Current31_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3109 | [8 empty] | 0x0fc03580
SS2PMM1Phase3Current32_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3110 | [8 empty] | 0x0fc03590
SS2PMM1Phase3Current33_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3111 | [8 empty] | 0x0fc035a0
SS2PMM1Phase3Current34_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3112 | [8 empty] | 0x0fc035b0
SS2PMM1Phase3Current35_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3113 | [8 empty] | 0x0fc035c0
SS2PMM1Phase3Current36_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3114 | [8 empty] | 0x0fc035d0
SS2PMM1Phase3Current37_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3115 | [8 empty] | 0x0fc035e0
SS2PMM1Phase3Current38_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3116 | [8 empty] | 0x0fc035f0
SS2PMM1Phase3Current39_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3117 | [8 empty] | 0x0fc03600
SS2PMM1Phase3Current40_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3118 | [8 empty] | 0x0fc03610
SS2PMM1Phase3Current41_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3119 | [8 empty] | 0x0fc03620
SS2PMM1Phase3Current42_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3120 | [8 empty] | 0x0fc03630
SS2PMM2Phase1Current1_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3121 | [8 empty] | 0x0fc03640
SS2PMM2Phase1Current2_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3122 | [8 empty] | 0x0fc03650
SS2PMM2Phase1Current3_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3123 | [8 empty] | 0x0fc03660
SS2PMM2Phase1Current4_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3124 | [8 empty] | 0x0fc03670
SS2PMM2Phase1Current5_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3125 | [8 empty] | 0x0fc03680
SS2PMM2Phase1Current6_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3126 | [8 empty] | 0x0fc03690
SS2PMM2Phase1Current7_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3127 | [8 empty] | 0x0fc036a0
SS2PMM2Phase1Current8_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3128 | [8 empty] | 0x0fc036b0
SS2PMM2Phase1Current9_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3129 | [8 empty] | 0x0fc036c0
SS2PMM2Phase1Current10_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3130 | [8 empty] | 0x0fc036d0
SS2PMM2Phase1Current11_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3131 | [8 empty] | 0x0fc036e0
SS2PMM2Phase1Current12_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3132 | [8 empty] | 0x0fc036f0
SS2PMM2Phase1Current13_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3133 | [8 empty] | 0x0fc03700
SS2PMM2Phase1Current14_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3134 | [8 empty] | 0x0fc03710
SS2PMM2Phase1Current15_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3135 | [8 empty] | 0x0fc03720
SS2PMM2Phase1Current16_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3136 | [8 empty] | 0x0fc03730
SS2PMM2Phase1Current17_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3137 | [8 empty] | 0x0fc03740
SS2PMM2Phase1Current18_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3138 | [8 empty] | 0x0fc03750
SS2PMM2Phase1Current19_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3139 | [8 empty] | 0x0fc03760
SS2PMM2Phase1Current20_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3140 | [8 empty] | 0x0fc03770
SS2PMM2Phase1Current21_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3141 | [8 empty] | 0x0fc03780
SS2PMM2Phase1Current22_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3142 | [8 empty] | 0x0fc03790
SS2PMM2Phase1Current23_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3143 | [8 empty] | 0x0fc037a0
SS2PMM2Phase1Current24_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3144 | [8 empty] | 0x0fc037b0
SS2PMM2Phase1Current25_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3145 | [8 empty] | 0x0fc037c0
SS2PMM2Phase1Current26_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3146 | [8 empty] | 0x0fc037d0
SS2PMM2Phase1Current27_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3147 | [8 empty] | 0x0fc037e0
SS2PMM2Phase1Current28_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3148 | [8 empty] | 0x0fc037f0
SS2PMM2Phase1Current29_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3149 | [8 empty] | 0x0fc03800
SS2PMM2Phase1Current30_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3150 | [8 empty] | 0x0fc03810
SS2PMM2Phase1Current31_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3151 | [8 empty] | 0x0fc03820
SS2PMM2Phase1Current32_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3152 | [8 empty] | 0x0fc03830
SS2PMM2Phase1Current33_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3153 | [8 empty] | 0x0fc03840
SS2PMM2Phase1Current34_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3154 | [8 empty] | 0x0fc03850
SS2PMM2Phase1Current35_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3155 | [8 empty] | 0x0fc03860
SS2PMM2Phase1Current36_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3156 | [8 empty] | 0x0fc03870
SS2PMM2Phase1Current37_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3157 | [8 empty] | 0x0fc03880
SS2PMM2Phase1Current38_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3158 | [8 empty] | 0x0fc03890
SS2PMM2Phase1Current39_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3159 | [8 empty] | 0x0fc038a0
SS2PMM2Phase1Current40_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3160 | [8 empty] | 0x0fc038b0
SS2PMM2Phase1Current41_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3161 | [8 empty] | 0x0fc038c0
SS2PMM2Phase1Current42_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3162 | [8 empty] | 0x0fc038d0
SS2SKTemp1_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R1 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc038e0
SS2SKTemp1_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R2 | 0 | 60 | 0 | 60 | °C | ####.# |  |  | 0x0fc038e1
SS2SKTemp1_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D3249 | [8 empty] | 0x0fc038f0
SS2SKTemp1_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D3250 | [8 empty] | 0x0fc03900
SS2SKVlaga1_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R3 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc03910
SS2SKVlaga1_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R4 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc03911
SS2SKVlaga1_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D3253 | [8 empty] | 0x0fc03920
SS2SKVlaga1_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D3254 | [8 empty] | 0x0fc03930
SS2SKTemp2_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R5 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc03940
SS2SKTemp2_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R6 | 0 | 60 | 0 | 60 | °C | ####.# |  |  | 0x0fc03941
SS2SKTemp2_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D3257 | [8 empty] | 0x0fc03950
SS2SKTemp2_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D3258 | [8 empty] | 0x0fc03960
SS2SKVlaga2_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R7 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc03970
SS2SKVlaga2_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R8 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc03971
SS2SKVlaga2_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D3261 | [8 empty] | 0x0fc03980
SS2SKVlaga2_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D3262 | [8 empty] | 0x0fc03990
SS2SKTemp3_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R9 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc039a0
SS2SKTemp3_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R10 | 0 | 60 | 0 | 60 | °C | ####.# |  |  | 0x0fc039a1
SS2SKTemp3_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D3265 | [8 empty] | 0x0fc039b0
SS2SKTemp3_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D3266 | [8 empty] | 0x0fc039c0
SS2SKVlaga3_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R11 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc039d0
SS2SKVlaga3_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R12 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc039d1
SS2SKVlaga3_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D3269 | [8 empty] | 0x0fc039e0
SS2SKVlaga3_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D3270 | [8 empty] | 0x0fc039f0
SS2SKTemp4_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R13 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc03a00
SS2SKTemp4_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R14 | 0 | 60 | 0 | 60 | °C | ####.# |  |  | 0x0fc03a01
SS2SKTemp4_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D3273 | [8 empty] | 0x0fc03a10
SS2SKTemp4_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D3274 | [8 empty] | 0x0fc03a20
SS2SKVlaga4_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R15 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc03a30
SS2SKVlaga4_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R16 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc03a31
SS2SKVlaga4_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D3277 | [8 empty] | 0x0fc03a40
SS2SKVlaga4_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D3278 | [8 empty] | 0x0fc03a50
SS2ComSCADA_stevec2 | INT | IOD_SS2_mem | I1 | [8 empty] | 0x0fc03a60
SS2ComSCADA_stevec1 | INT | IOD_SS2_mem | I2 | [8 empty] | 0x0fc03a61
SS2PMM2x63_VirA_Faza1_Med60in80 | REAL | IOD_SS2_disk | R30[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x0fc03a62
SS2PMM2x63_VirB_Faza1_Med60in80 | REAL | IOD_SS2_disk | R60[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x0fc03a63
SS2PMM2x63_VirA_Faza1_Nad80 | REAL | IOD_SS2_disk | R90[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x0fc03a64
SS2PMM2x63_VirB_Faza1_Mad80 | REAL | IOD_SS2_disk | R120[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x0fc03a65
SS2PMM2x63_VirA_Faza2_Med60in80 | REAL | IOD_SS2_disk | R150[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x0fc03a66
SS2PMM2x63_VirB_Faza2_Med60in80 | REAL | IOD_SS2_disk | R180[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x0fc03a67
SS2PMM2x63_VirA_Faza2_Nad80 | REAL | IOD_SS2_disk | R210[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x0fc03a68
SS2PMM2x63_VirB_Faza2_Mad80 | REAL | IOD_SS2_disk | R240[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x0fc03a69
SS2PMM2x63_VirA_Faza3_Med60in80 | REAL | IOD_SS2_disk | R270[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x0fc03a6a
SS2PMM2x63_VirB_Faza3_Med60in80 | REAL | IOD_SS2_disk | R300[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x0fc03a6b
SS2PMM2x63_VirA_Faza3_Nad80 | REAL | IOD_SS2_disk | R330[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x0fc03a6c
SS2PMM2x63_VirB_Faza3_Mad80 | REAL | IOD_SS2_disk | R360[21] | 0 | 16 | 0 | 16 | A | ####.# |  |  | 0x0fc03a6d
SS2PMM1PoljeFazaATok1_16_nad80 | DIGITAL | IOD_SS2_disk | D3500[16] | [8 empty] | 0x0fc03a70
SS2PMM1PoljeFazaATok17_32_nad80 | DIGITAL | IOD_SS2_disk | D3517[16] | [8 empty] | 0x0fc03a80
SS2PMM1PoljeFazaATok33_42_nad80 | DIGITAL | IOD_SS2_disk | D3534[16] | [8 empty] | 0x0fc03a90
SS2PMM1PoljeFazaBTok1_16_nad80 | DIGITAL | IOD_SS2_disk | D3551[16] | [8 empty] | 0x0fc03aa0
SS2PMM1PoljeFazaBTok17_32_nad80 | DIGITAL | IOD_SS2_disk | D3568[16] | [8 empty] | 0x0fc03ab0
SS2PMM1PoljeFazaBTok33_42_nad80 | DIGITAL | IOD_SS2_disk | D3585[16] | [8 empty] | 0x0fc03ac0
SS2PMM1PoljeFazaCTok1_16_nad80 | DIGITAL | IOD_SS2_disk | D3602[16] | [8 empty] | 0x0fc03ad0
SS2PMM1PoljeFazaCTok17_32_nad80 | DIGITAL | IOD_SS2_disk | D3619[16] | [8 empty] | 0x0fc03ae0
SS2PMM1PoljeFazaCTok33_42_nad80 | DIGITAL | IOD_SS2_disk | D3636[16] | [8 empty] | 0x0fc03af0
SS2PMM1PoljeFazaATok1_16_med60_80 | DIGITAL | IOD_SS2_disk | D3653[16] | [8 empty] | 0x0fc03b00
SS2PMM1PoljeFazaATok17_32_med60_80 | DIGITAL | IOD_SS2_disk | D3670[16] | [8 empty] | 0x0fc03b10
SS2PMM1PoljeFazaATok33_42_med60_80 | DIGITAL | IOD_SS2_disk | D3687[16] | [8 empty] | 0x0fc03b20
SS2PMM1PoljeFazaBTok1_16_med60_80 | DIGITAL | IOD_SS2_disk | D3704[16] | [8 empty] | 0x0fc03b30
SS2PMM1PoljeFazaBTok17_32_med60_80 | DIGITAL | IOD_SS2_disk | D3721[16] | [8 empty] | 0x0fc03b40
SS2PMM1PoljeFazaBTok33_42_med60_80 | DIGITAL | IOD_SS2_disk | D3738[16] | [8 empty] | 0x0fc03b50
SS2PMM1PoljeFazaCTok1_16_med60_80 | DIGITAL | IOD_SS2_disk | D3755[16] | [8 empty] | 0x0fc03b60
SS2PMM1PoljeFazaCTok17_32_med60_80 | DIGITAL | IOD_SS2_disk | D3772[16] | [8 empty] | 0x0fc03b70
SS2PMM1PoljeFazaCTok33_42_med60_80 | DIGITAL | IOD_SS2_disk | D3789[16] | [8 empty] | 0x0fc03b80
SS2ErrComPort2_Omogoci | DIGITAL | IOD_SS2_disk | D3810 | [8 empty] | 0x0fc03b90
SS2PMM1OverCurrentBetw1_VirB_Omogoci | DIGITAL | IOD_SS2_disk | D3811 | [8 empty] | 0x0fc03ba0
SS2PMM1OverCurrentBetw1_VirA_Omogoci | DIGITAL | IOD_SS2_disk | D3812 | [8 empty] | 0x0fc03bb0
SS2PMM1OverCurrentBetw2_VirB_Omogoci | DIGITAL | IOD_SS2_disk | D3813 | [8 empty] | 0x0fc03bc0
SS2PMM1OverCurrentBetw2_VirA_Omogoci | DIGITAL | IOD_SS2_disk | D3814 | [8 empty] | 0x0fc03bd0
SS2PMM1OverCurrentBetw3_VirB_Omogoci | DIGITAL | IOD_SS2_disk | D3815 | [8 empty] | 0x0fc03be0
SS2PMM1OverCurrentBetw3_VirA_Omogoci | DIGITAL | IOD_SS2_disk | D3816 | [8 empty] | 0x0fc03bf0
SS2PMM1OverCurrentBetw1_VirB | DIGITAL | IOD_SS2_disk | D3817 | [8 empty] | 0x0fc03c00
SS2PMM1OverCurrentBetw1_VirA | DIGITAL | IOD_SS2_disk | D3818 | [8 empty] | 0x0fc03c10
SS2PMM1OverCurrentBetw2_VirB | DIGITAL | IOD_SS2_disk | D3819 | [8 empty] | 0x0fc03c20
SS2PMM1OverCurrentBetw2_VirA | DIGITAL | IOD_SS2_disk | D3820 | [8 empty] | 0x0fc03c30
SS2PMM1OverCurrentBetw3_VirB | DIGITAL | IOD_SS2_disk | D3821 | [8 empty] | 0x0fc03c40
SS2PMM1OverCurrentBetw3_VirA | DIGITAL | IOD_SS2_disk | D3822 | [8 empty] | 0x0fc03c50
SS2Test | DIGITAL | IOD_SS2_disk | D3823 | [8 empty] | 0x0fc03c60
SS2Temp1 | INT | IOD_SS2_disk | I34 | [8 empty] | 0x0fc03c70
SS2Temp2 | INT | IOD_SS2_disk | I35 | [8 empty] | 0x0fc03c71
SS2Prikaz | DIGITAL | IOD_SS2_disk | D3824 | [8 empty] | 0x0fc03c80
SS2PMM1OverCurrentBetw1_VirB_1_2 | INT | IOD_SS2_disk | I10 | [8 empty] | 0x0fc03c90
SS2PMM1OverCurrentBetw1_VirA_1_2 | INT | IOD_SS2_disk | I11 | [8 empty] | 0x0fc03c91
SS2PMM1OverCurrentBetw1_VirB_2_2 | INT | IOD_SS2_disk | I12 | [8 empty] | 0x0fc03c92
SS2PMM1OverCurrentBetw1_VirA_2_2 | INT | IOD_SS2_disk | I13 | [8 empty] | 0x0fc03c93
SS2PMM1OverCurrentBetw2_VirB_1_2 | INT | IOD_SS2_disk | I14 | [8 empty] | 0x0fc03c94
SS2PMM1OverCurrentBetw2_VirA_1_2 | INT | IOD_SS2_disk | I15 | [8 empty] | 0x0fc03c95
SS2PMM1OverCurrentBetw2_VirB_2_2 | INT | IOD_SS2_disk | I16 | [8 empty] | 0x0fc03c96
SS2PMM1OverCurrentBetw2_VirA_2_2 | INT | IOD_SS2_disk | I17 | [8 empty] | 0x0fc03c97
SS2PMM1OverCurrentBetw3_VirB_1_2 | INT | IOD_SS2_disk | I18 | [8 empty] | 0x0fc03c98
SS2PMM1OverCurrentBetw3_VirA_1_2 | INT | IOD_SS2_disk | I19 | [8 empty] | 0x0fc03c99
SS2PMM1OverCurrentBetw3_VirB_2_2 | INT | IOD_SS2_disk | I20 | [8 empty] | 0x0fc03c9a
SS2PMM1OverCurrentBetw3_VirA_2_2 | INT | IOD_SS2_disk | I21 | [8 empty] | 0x0fc03c9b
SS2PMM1OverCurrentOver1_VirB_Omogoci | DIGITAL | IOD_SS2_disk | D3825 | [8 empty] | 0x0fc03ca0
SS2PMM1OverCurrentOver1_VirA_Omogoci | DIGITAL | IOD_SS2_disk | D3826 | [8 empty] | 0x0fc03cb0
SS2PMM1OverCurrentOver2_VirB_Omogoci | DIGITAL | IOD_SS2_disk | D3827 | [8 empty] | 0x0fc03cc0
SS2PMM1OverCurrentOver2_VirA_Omogoci | DIGITAL | IOD_SS2_disk | D3828 | [8 empty] | 0x0fc03cd0
SS2PMM1OverCurrentOver3_VirB_Omogoci | DIGITAL | IOD_SS2_disk | D3829 | [8 empty] | 0x0fc03ce0
SS2PMM1OverCurrentOver3_VirA_Omogoci | DIGITAL | IOD_SS2_disk | D3830 | [8 empty] | 0x0fc03cf0
SS2PMM1OverCurrentOver1_VirB | DIGITAL | IOD_SS2_disk | D3831 | [8 empty] | 0x0fc03d00
SS2PMM1OverCurrentOver1_VirA | DIGITAL | IOD_SS2_disk | D3832 | [8 empty] | 0x0fc03d10
SS2PMM1OverCurrentOver2_VirB | DIGITAL | IOD_SS2_disk | D3833 | [8 empty] | 0x0fc03d20
SS2PMM1OverCurrentOver2_VirA | DIGITAL | IOD_SS2_disk | D3834 | [8 empty] | 0x0fc03d30
SS2PMM1OverCurrentOver3_VirB | DIGITAL | IOD_SS2_disk | D3835 | [8 empty] | 0x0fc03d40
SS2PMM1OverCurrentOver3_VirA | DIGITAL | IOD_SS2_disk | D3836 | [8 empty] | 0x0fc03d50
SS2PMM1OverCurrentOver1_VirB_1_2 | INT | IOD_SS2_disk | I22 | [8 empty] | 0x0fc03d60
SS2PMM1OverCurrentOver1_VirA_1_2 | INT | IOD_SS2_disk | I23 | [8 empty] | 0x0fc03d61
SS2PMM1OverCurrentOver1_VirB_2_2 | INT | IOD_SS2_disk | I24 | [8 empty] | 0x0fc03d62
SS2PMM1OverCurrentOver1_VirA_2_2 | INT | IOD_SS2_disk | I25 | [8 empty] | 0x0fc03d63
SS2PMM1OverCurrentOver2_VirB_1_2 | INT | IOD_SS2_disk | I26 | [8 empty] | 0x0fc03d64
SS2PMM1OverCurrentOver2_VirA_1_2 | INT | IOD_SS2_disk | I27 | [8 empty] | 0x0fc03d65
SS2PMM1OverCurrentOver2_VirB_2_2 | INT | IOD_SS2_disk | I28 | [8 empty] | 0x0fc03d66
SS2PMM1OverCurrentOver2_VirA_2_2 | INT | IOD_SS2_disk | I29 | [8 empty] | 0x0fc03d67
SS2PMM1OverCurrentOver3_VirB_1_2 | INT | IOD_SS2_disk | I30 | [8 empty] | 0x0fc03d68
SS2PMM1OverCurrentOver3_VirA_1_2 | INT | IOD_SS2_disk | I31 | [8 empty] | 0x0fc03d69
SS2PMM1OverCurrentOver3_VirB_2_2 | INT | IOD_SS2_disk | I32 | [8 empty] | 0x0fc03d6a
SS2PMM1OverCurrentOver3_VirA_2_2 | INT | IOD_SS2_disk | I33 | [8 empty] | 0x0fc03d6b
SS2VsotaF1_1_16B | INT | IOD_SS2_disk | I40 | [8 empty] | 0x0fc03d6c
SS2VsotaF1_17_32B | INT | IOD_SS2_disk | I41 | [8 empty] | 0x0fc03d6d
SS2VsotaF1_33_42B | INT | IOD_SS2_disk | I42 | [8 empty] | 0x0fc03d6e
SS2VsotaF2_1_16B | INT | IOD_SS2_disk | I43 | [8 empty] | 0x0fc03d6f
SS2VsotaF2_17_32B | INT | IOD_SS2_disk | I44 | [8 empty] | 0x0fc03d70
SS2VsotaF2_33_42B | INT | IOD_SS2_disk | I45 | [8 empty] | 0x0fc03d71
SS2VsotaF3_1_16B | INT | IOD_SS2_disk | I46 | [8 empty] | 0x0fc03d72
SS2VsotaF3_17_32B | INT | IOD_SS2_disk | I47 | [8 empty] | 0x0fc03d73
SS2VsotaF3_33_42B | INT | IOD_SS2_disk | I48 | [8 empty] | 0x0fc03d74
SS2VsotaF1_1_16A | INT | IOD_SS2_disk | I49 | [8 empty] | 0x0fc03d75
SS2VsotaF1_17_32A | INT | IOD_SS2_disk | I50 | [8 empty] | 0x0fc03d76
SS2VsotaF1_33_42A | INT | IOD_SS2_disk | I51 | [8 empty] | 0x0fc03d77
SS2VsotaF2_1_16A | INT | IOD_SS2_disk | I52 | [8 empty] | 0x0fc03d78
SS2VsotaF2_17_32A | INT | IOD_SS2_disk | I53 | [8 empty] | 0x0fc03d79
SS2VsotaF2_33_42A | INT | IOD_SS2_disk | I54 | [8 empty] | 0x0fc03d7a
SS2VsotaF3_1_16A | INT | IOD_SS2_disk | I55 | [8 empty] | 0x0fc03d7b
SS2VsotaF3_17_32A | INT | IOD_SS2_disk | I56 | [8 empty] | 0x0fc03d7c
SS2VsotaF3_33_42A | INT | IOD_SS2_disk | I57 | [8 empty] | 0x0fc03d7d
SS2OpozoriloPMM2x17med60in801_Omogoci | DIGITAL | IOD_SS2_disk | D3850 | [8 empty] | 0x0fc03d80
SS2OpozoriloPMM2x17med60in802_Omogoci | DIGITAL | IOD_SS2_disk | D3851 | [8 empty] | 0x0fc03d90
SS2OpozoriloPMM2x17med60in803_Omogoci | DIGITAL | IOD_SS2_disk | D3852 | [8 empty] | 0x0fc03da0
SS2OpozoriloPMM2x17med60in804_Omogoci | DIGITAL | IOD_SS2_disk | D3853 | [8 empty] | 0x0fc03db0
SS2OpozoriloPMM2x17med60in805_Omogoci | DIGITAL | IOD_SS2_disk | D3854 | [8 empty] | 0x0fc03dc0
SS2OpozoriloPMM2x17med60in806_Omogoci | DIGITAL | IOD_SS2_disk | D3855 | [8 empty] | 0x0fc03dd0
SS2OpozoriloPMM2x17med60in807_Omogoci | DIGITAL | IOD_SS2_disk | D3856 | [8 empty] | 0x0fc03de0
SS2OpozoriloPMM2x17med60in808_Omogoci | DIGITAL | IOD_SS2_disk | D3857 | [8 empty] | 0x0fc03df0
SS2OpozoriloPMM2x17med60in809_Omogoci | DIGITAL | IOD_SS2_disk | D3858 | [8 empty] | 0x0fc03e00
SS2OpozoriloPMM2x17med60in8010_Omogoci | DIGITAL | IOD_SS2_disk | D3859 | [8 empty] | 0x0fc03e10
SS2OpozoriloPMM2x17med60in8011_Omogoci | DIGITAL | IOD_SS2_disk | D3860 | [8 empty] | 0x0fc03e20
SS2OpozoriloPMM2x17med60in8012_Omogoci | DIGITAL | IOD_SS2_disk | D3861 | [8 empty] | 0x0fc03e30
SS2OpozoriloPMM2x17med60in8013_Omogoci | DIGITAL | IOD_SS2_disk | D3862 | [8 empty] | 0x0fc03e40
SS2OpozoriloPMM2x17med60in8014_Omogoci | DIGITAL | IOD_SS2_disk | D3863 | [8 empty] | 0x0fc03e50
SS2OpozoriloPMM2x17med60in8015_Omogoci | DIGITAL | IOD_SS2_disk | D3864 | [8 empty] | 0x0fc03e60
SS2OpozoriloPMM2x17med60in8016_Omogoci | DIGITAL | IOD_SS2_disk | D3865 | [8 empty] | 0x0fc03e70
SS2OpozoriloPMM2x17med60in8017_Omogoci | DIGITAL | IOD_SS2_disk | D3866 | [8 empty] | 0x0fc03e80
SS2OpozoriloPMM2x17med60in8018_Omogoci | DIGITAL | IOD_SS2_disk | D3867 | [8 empty] | 0x0fc03e90
SS2OpozoriloPMM2x17med60in8019_Omogoci | DIGITAL | IOD_SS2_disk | D3868 | [8 empty] | 0x0fc03ea0
SS2OpozoriloPMM2x17med60in8020_Omogoci | DIGITAL | IOD_SS2_disk | D3869 | [8 empty] | 0x0fc03eb0
SS2OpozoriloPMM2x17med60in8021_Omogoci | DIGITAL | IOD_SS2_disk | D3870 | [8 empty] | 0x0fc03ec0
SS2OpozoriloPMM2x17med60in8022_Omogoci | DIGITAL | IOD_SS2_disk | D3871 | [8 empty] | 0x0fc03ed0
SS2OpozoriloPMM2x17med60in8023_Omogoci | DIGITAL | IOD_SS2_disk | D3872 | [8 empty] | 0x0fc03ee0
SS2OpozoriloPMM2x17med60in8024_Omogoci | DIGITAL | IOD_SS2_disk | D3873 | [8 empty] | 0x0fc03ef0
SS2OpozoriloPMM2x17med60in8025_Omogoci | DIGITAL | IOD_SS2_disk | D3874 | [8 empty] | 0x0fc03f00
SS2OpozoriloPMM2x17med60in8026_Omogoci | DIGITAL | IOD_SS2_disk | D3875 | [8 empty] | 0x0fc03f10
SS2OpozoriloPMM2x17med60in8027_Omogoci | DIGITAL | IOD_SS2_disk | D3876 | [8 empty] | 0x0fc03f20
SS2OpozoriloPMM2x17med60in8028_Omogoci | DIGITAL | IOD_SS2_disk | D3877 | [8 empty] | 0x0fc03f30
SS2OpozoriloPMM2x17med60in8029_Omogoci | DIGITAL | IOD_SS2_disk | D3878 | [8 empty] | 0x0fc03f40
SS2OpozoriloPMM2x17med60in8030_Omogoci | DIGITAL | IOD_SS2_disk | D3879 | [8 empty] | 0x0fc03f50
SS2OpozoriloPMM2x17med60in8031_Omogoci | DIGITAL | IOD_SS2_disk | D3880 | [8 empty] | 0x0fc03f60
SS2OpozoriloPMM2x17med60in8032_Omogoci | DIGITAL | IOD_SS2_disk | D3881 | [8 empty] | 0x0fc03f70
SS2OpozoriloPMM2x17med60in8033_Omogoci | DIGITAL | IOD_SS2_disk | D3882 | [8 empty] | 0x0fc03f80
SS2OpozoriloPMM2x17med60in8034_Omogoci | DIGITAL | IOD_SS2_disk | D3883 | [8 empty] | 0x0fc03f90
SS2OpozoriloPMM2x17med60in8035_Omogoci | DIGITAL | IOD_SS2_disk | D3884 | [8 empty] | 0x0fc03fa0
SS2OpozoriloPMM2x17med60in8036_Omogoci | DIGITAL | IOD_SS2_disk | D3885 | [8 empty] | 0x0fc03fb0
SS2OpozoriloPMM2x17med60in8037_Omogoci | DIGITAL | IOD_SS2_disk | D3886 | [8 empty] | 0x0fc03fc0
SS2OpozoriloPMM2x17med60in8038_Omogoci | DIGITAL | IOD_SS2_disk | D3887 | [8 empty] | 0x0fc03fd0
SS2OpozoriloPMM2x17med60in8039_Omogoci | DIGITAL | IOD_SS2_disk | D3888 | [8 empty] | 0x0fc03fe0
SS2OpozoriloPMM2x17med60in8040_Omogoci | DIGITAL | IOD_SS2_disk | D3889 | [8 empty] | 0x0fc03ff0
SS2OpozoriloPMM2x17med60in8041_Omogoci | DIGITAL | IOD_SS2_disk | D3890 | [8 empty] | 0x0fc04000
SS2OpozoriloPMM2x17med60in8042_Omogoci | DIGITAL | IOD_SS2_disk | D3891 | [8 empty] | 0x0fc04010
SS2AlarmPMM2x17nad801_Omogoci | DIGITAL | IOD_SS2_disk | D3892 | [8 empty] | 0x0fc04020
SS2AlarmPMM2x17nad802_Omogoci | DIGITAL | IOD_SS2_disk | D3893 | [8 empty] | 0x0fc04030
SS2AlarmPMM2x17nad803_Omogoci | DIGITAL | IOD_SS2_disk | D3894 | [8 empty] | 0x0fc04040
SS2AlarmPMM2x17nad804_Omogoci | DIGITAL | IOD_SS2_disk | D3895 | [8 empty] | 0x0fc04050
SS2AlarmPMM2x17nad805_Omogoci | DIGITAL | IOD_SS2_disk | D3896 | [8 empty] | 0x0fc04060
SS2AlarmPMM2x17nad806_Omogoci | DIGITAL | IOD_SS2_disk | D3897 | [8 empty] | 0x0fc04070
SS2AlarmPMM2x17nad807_Omogoci | DIGITAL | IOD_SS2_disk | D3898 | [8 empty] | 0x0fc04080
SS2AlarmPMM2x17nad808_Omogoci | DIGITAL | IOD_SS2_disk | D3899 | [8 empty] | 0x0fc04090
SS2AlarmPMM2x17nad809_Omogoci | DIGITAL | IOD_SS2_disk | D3900 | [8 empty] | 0x0fc040a0
SS2AlarmPMM2x17nad8010_Omogoci | DIGITAL | IOD_SS2_disk | D3901 | [8 empty] | 0x0fc040b0
SS2AlarmPMM2x17nad8011_Omogoci | DIGITAL | IOD_SS2_disk | D3902 | [8 empty] | 0x0fc040c0
SS2AlarmPMM2x17nad8012_Omogoci | DIGITAL | IOD_SS2_disk | D3903 | [8 empty] | 0x0fc040d0
SS2AlarmPMM2x17nad8013_Omogoci | DIGITAL | IOD_SS2_disk | D3904 | [8 empty] | 0x0fc040e0
SS2AlarmPMM2x17nad8014_Omogoci | DIGITAL | IOD_SS2_disk | D3905 | [8 empty] | 0x0fc040f0
SS2AlarmPMM2x17nad8015_Omogoci | DIGITAL | IOD_SS2_disk | D3906 | [8 empty] | 0x0fc04100
SS2AlarmPMM2x17nad8016_Omogoci | DIGITAL | IOD_SS2_disk | D3907 | [8 empty] | 0x0fc04110
SS2AlarmPMM2x17nad8017_Omogoci | DIGITAL | IOD_SS2_disk | D3908 | [8 empty] | 0x0fc04120
SS2AlarmPMM2x17nad8018_Omogoci | DIGITAL | IOD_SS2_disk | D3909 | [8 empty] | 0x0fc04130
SS2AlarmPMM2x17nad8019_Omogoci | DIGITAL | IOD_SS2_disk | D3910 | [8 empty] | 0x0fc04140
SS2AlarmPMM2x17nad8020_Omogoci | DIGITAL | IOD_SS2_disk | D3911 | [8 empty] | 0x0fc04150
SS2AlarmPMM2x17nad8021_Omogoci | DIGITAL | IOD_SS2_disk | D3912 | [8 empty] | 0x0fc04160
SS2AlarmPMM2x17nad8022_Omogoci | DIGITAL | IOD_SS2_disk | D3913 | [8 empty] | 0x0fc04170
SS2AlarmPMM2x17nad8023_Omogoci | DIGITAL | IOD_SS2_disk | D3914 | [8 empty] | 0x0fc04180
SS2AlarmPMM2x17nad8024_Omogoci | DIGITAL | IOD_SS2_disk | D3915 | [8 empty] | 0x0fc04190
SS2AlarmPMM2x17nad8025_Omogoci | DIGITAL | IOD_SS2_disk | D3916 | [8 empty] | 0x0fc041a0
SS2AlarmPMM2x17nad8026_Omogoci | DIGITAL | IOD_SS2_disk | D3917 | [8 empty] | 0x0fc041b0
SS2AlarmPMM2x17nad8027_Omogoci | DIGITAL | IOD_SS2_disk | D3918 | [8 empty] | 0x0fc041c0
SS2AlarmPMM2x17nad8028_Omogoci | DIGITAL | IOD_SS2_disk | D3919 | [8 empty] | 0x0fc041d0
SS2AlarmPMM2x17nad8029_Omogoci | DIGITAL | IOD_SS2_disk | D3920 | [8 empty] | 0x0fc041e0
SS2AlarmPMM2x17nad8030_Omogoci | DIGITAL | IOD_SS2_disk | D3921 | [8 empty] | 0x0fc041f0
SS2AlarmPMM2x17nad8031_Omogoci | DIGITAL | IOD_SS2_disk | D3922 | [8 empty] | 0x0fc04200
SS2AlarmPMM2x17nad8032_Omogoci | DIGITAL | IOD_SS2_disk | D3923 | [8 empty] | 0x0fc04210
SS2AlarmPMM2x17nad8033_Omogoci | DIGITAL | IOD_SS2_disk | D3924 | [8 empty] | 0x0fc04220
SS2AlarmPMM2x17nad8034_Omogoci | DIGITAL | IOD_SS2_disk | D3925 | [8 empty] | 0x0fc04230
SS2AlarmPMM2x17nad8035_Omogoci | DIGITAL | IOD_SS2_disk | D3926 | [8 empty] | 0x0fc04240
SS2AlarmPMM2x17nad8036_Omogoci | DIGITAL | IOD_SS2_disk | D3927 | [8 empty] | 0x0fc04250
SS2AlarmPMM2x17nad8037_Omogoci | DIGITAL | IOD_SS2_disk | D3928 | [8 empty] | 0x0fc04260
SS2AlarmPMM2x17nad8038_Omogoci | DIGITAL | IOD_SS2_disk | D3929 | [8 empty] | 0x0fc04270
SS2AlarmPMM2x17nad8039_Omogoci | DIGITAL | IOD_SS2_disk | D3930 | [8 empty] | 0x0fc04280
SS2AlarmPMM2x17nad8040_Omogoci | DIGITAL | IOD_SS2_disk | D3931 | [8 empty] | 0x0fc04290
SS2AlarmPMM2x17nad8041_Omogoci | DIGITAL | IOD_SS2_disk | D3932 | [8 empty] | 0x0fc042a0
SS2AlarmPMM2x17nad8042_Omogoci | DIGITAL | IOD_SS2_disk | D3933 | [8 empty] | 0x0fc042b0
SS2PMM2OverCurrentOver_VirB | DIGITAL | IOD_SS2_disk | D3940 | [8 empty] | 0x0fc042c0
SS2PMM2OverCurrentOver_VirA | DIGITAL | IOD_SS2_disk | D3941 | [8 empty] | 0x0fc042d0
SS2PMM2OverCurrentBetw_VirB | DIGITAL | IOD_SS2_disk | D3942 | [8 empty] | 0x0fc042e0
SS2PMM2OverCurrentBetw_VirA | DIGITAL | IOD_SS2_disk | D3943 | [8 empty] | 0x0fc042f0
SS2PMM2OverCurrentOver_VirB_Omogoci | DIGITAL | IOD_SS2_disk | D3944 | [8 empty] | 0x0fc04300
SS2PMM2OverCurrentOver_VirA_Omogoci | DIGITAL | IOD_SS2_disk | D3945 | [8 empty] | 0x0fc04310
SS2PMM2OverCurrentBetw_VirB_Omogoci | DIGITAL | IOD_SS2_disk | D3946 | [8 empty] | 0x0fc04320
SS2PMM2OverCurrentBetw_VirA_Omogoci | DIGITAL | IOD_SS2_disk | D3947 | [8 empty] | 0x0fc04330
SS2NapakaKlimat1_Klimat2 | DIGITAL | IOD_SS2_disk | D3955 | [8 empty] | 0x0fc04340
SS2NapakaKlimat3_Klimat4 | DIGITAL | IOD_SS2_disk | D3956 | [8 empty] | 0x0fc04350
SS2NapakaKlimat5_Klimat6 | DIGITAL | IOD_SS2_disk | D3957 | [8 empty] | 0x0fc04360
SS2AlarmTempTIA1Previsoka_Omogoci | DIGITAL | IOD_SS2_disk | D3958 | [8 empty] | 0x0fc04370
SS2AlarmTempTIA2Previsoka_Omogoci | DIGITAL | IOD_SS2_disk | D3959 | [8 empty] | 0x0fc04380
SS2AlarmTempTIA3Previsoka_Omogoci | DIGITAL | IOD_SS2_disk | D3960 | [8 empty] | 0x0fc04390
SS2AlarmTempTIA4Previsoka_Omogoci | DIGITAL | IOD_SS2_disk | D3961 | [8 empty] | 0x0fc043a0
SS2SMS_Rezerva | DIGITAL | IOD_SS2_disk | D3962 | [8 empty] | 0x0fc043b0
SS2OnemAlarmPon | DIGITAL | IOD_SS2_disk | D3963 | [8 empty] | 0x0fc043c0
SS2UserloggedIn_mem | DIGITAL | IOD_SS2_disk | D3964 | [8 empty] | 0x0fc043d0
SS2AktualniSetPointTemp1_2 | REAL | IOD_SS2 | SS2:.AktualniSetPointTemp1_2 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc043e0
SS2AktualniSetPointTemp3_4 | REAL | IOD_SS2 | SS2:.AktualniSetPointTemp3_4 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc043e1
SS2AktualniSetPointTemp5_6 | REAL | IOD_SS2 | SS2:.AktualniSetPointTemp5_6 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc043e2
SS2AlarmKlimat2_1_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_1_Napaka | [6 empty] | 6157 | 0 | 0x0fc043f0
SS2AlarmKlimat2_2_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_2_Napaka | [6 empty] | 6157 | 0 | 0x0fc04400
SS2AlarmKlimat2_3_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_3_Napaka | [6 empty] | 6157 | 0 | 0x0fc04410
SS2AlarmKlimat2_4_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_4_Napaka | [6 empty] | 6157 | 0 | 0x0fc04420
SS2AlarmKlimat2_5_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_5_Napaka | [6 empty] | 6157 | 0 | 0x0fc04430
SS2AlarmKlimat2_6_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_6_Napaka | [6 empty] | 6157 | 0 | 0x0fc04440
SS2AlarmLAH1RazlitjeVode | DIGITAL | IOD_SS2 | SS2:.AlarmLAH1RazlitjeVode | [6 empty] | 6157 | 0 | 0x0fc04450
SS2AlarmLAH2RazlitjeVode | DIGITAL | IOD_SS2 | SS2:.AlarmLAH2RazlitjeVode | [6 empty] | 6157 | 0 | 0x0fc04460
SS2AlarmLAH3RazlitjeVode | DIGITAL | IOD_SS2 | SS2:.AlarmLAH3RazlitjeVode | [6 empty] | 6157 | 0 | 0x0fc04470
SS2AlarmPMM2x17nad8010 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[10] | [6 empty] | 6157 | 0 | 0x0fc04480
SS2AlarmPMM2x17nad8011 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[11] | [6 empty] | 6157 | 0 | 0x0fc04490
SS2AlarmPMM2x17nad8012 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[12] | [6 empty] | 6157 | 0 | 0x0fc044a0
SS2AlarmPMM2x17nad8013 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[13] | [6 empty] | 6157 | 0 | 0x0fc044b0
SS2AlarmPMM2x17nad8014 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[14] | [6 empty] | 6157 | 0 | 0x0fc044c0
SS2AlarmPMM2x17nad8015 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[15] | [6 empty] | 6157 | 0 | 0x0fc044d0
SS2AlarmPMM2x17nad8016 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[16] | [6 empty] | 6157 | 0 | 0x0fc044e0
SS2AlarmPMM2x17nad8017 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[17] | [6 empty] | 6157 | 0 | 0x0fc044f0
SS2AlarmPMM2x17nad8018 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[18] | [6 empty] | 6157 | 0 | 0x0fc04500
SS2AlarmPMM2x17nad8019 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[19] | [6 empty] | 6157 | 0 | 0x0fc04510
SS2AlarmPMM2x17nad801 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[1] | [6 empty] | 6157 | 0 | 0x0fc04520
SS2AlarmPMM2x17nad8020 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[20] | [6 empty] | 6157 | 0 | 0x0fc04530
SS2AlarmPMM2x17nad8021 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[21] | [6 empty] | 6157 | 0 | 0x0fc04540
SS2AlarmPMM2x17nad8022 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[22] | [6 empty] | 6157 | 0 | 0x0fc04550
SS2AlarmPMM2x17nad8023 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[23] | [6 empty] | 6157 | 0 | 0x0fc04560
SS2AlarmPMM2x17nad8024 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[24] | [6 empty] | 6157 | 0 | 0x0fc04570
SS2AlarmPMM2x17nad8025 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[25] | [6 empty] | 6157 | 0 | 0x0fc04580
SS2AlarmPMM2x17nad8026 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[26] | [6 empty] | 6157 | 0 | 0x0fc04590
SS2AlarmPMM2x17nad8027 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[27] | [6 empty] | 6157 | 0 | 0x0fc045a0
SS2AlarmPMM2x17nad8028 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[28] | [6 empty] | 6157 | 0 | 0x0fc045b0
SS2AlarmPMM2x17nad8029 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[29] | [6 empty] | 6157 | 0 | 0x0fc045c0
SS2AlarmPMM2x17nad802 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[2] | [6 empty] | 6157 | 0 | 0x0fc045d0
SS2AlarmPMM2x17nad8030 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[30] | [6 empty] | 6157 | 0 | 0x0fc045e0
SS2AlarmPMM2x17nad8031 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[31] | [6 empty] | 6157 | 0 | 0x0fc045f0
SS2AlarmPMM2x17nad8032 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[32] | [6 empty] | 6157 | 0 | 0x0fc04600
SS2AlarmPMM2x17nad8033 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[33] | [6 empty] | 6157 | 0 | 0x0fc04610
SS2AlarmPMM2x17nad8034 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[34] | [6 empty] | 6157 | 0 | 0x0fc04620
SS2AlarmPMM2x17nad8035 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[35] | [6 empty] | 6157 | 0 | 0x0fc04630
SS2AlarmPMM2x17nad8036 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[36] | [6 empty] | 6157 | 0 | 0x0fc04640
SS2AlarmPMM2x17nad8037 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[37] | [6 empty] | 6157 | 0 | 0x0fc04650
SS2AlarmPMM2x17nad8038 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[38] | [6 empty] | 6157 | 0 | 0x0fc04660
SS2AlarmPMM2x17nad8039 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[39] | [6 empty] | 6157 | 0 | 0x0fc04670
SS2AlarmPMM2x17nad803 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[3] | [6 empty] | 6157 | 0 | 0x0fc04680
SS2AlarmPMM2x17nad8040 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[40] | [6 empty] | 6157 | 0 | 0x0fc04690
SS2AlarmPMM2x17nad8041 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[41] | [6 empty] | 6157 | 0 | 0x0fc046a0
SS2AlarmPMM2x17nad8042 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[42] | [6 empty] | 6157 | 0 | 0x0fc046b0
SS2AlarmPMM2x17nad804 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[4] | [6 empty] | 6157 | 0 | 0x0fc046c0
SS2AlarmPMM2x17nad805 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[5] | [6 empty] | 6157 | 0 | 0x0fc046d0
SS2AlarmPMM2x17nad806 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[6] | [6 empty] | 6157 | 0 | 0x0fc046e0
SS2AlarmPMM2x17nad807 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[7] | [6 empty] | 6157 | 0 | 0x0fc046f0
SS2AlarmPMM2x17nad808 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[8] | [6 empty] | 6157 | 0 | 0x0fc04700
SS2AlarmPMM2x17nad809 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[9] | [6 empty] | 6157 | 0 | 0x0fc04710
SS2AlarmSinhronizacijaNOK | DIGITAL | IOD_SS2 | SS2:.AlarmSinhronizacijaNOK | [6 empty] | 6157 | 0 | 0x0fc04720
SS2AlarmSKTemp1_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp1_Previsoka | [6 empty] | 6157 | 0 | 0x0fc04730
SS2AlarmSKTemp2_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp2_Previsoka | [6 empty] | 6157 | 0 | 0x0fc04740
SS2AlarmSKTemp3_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp3_Previsoka | [6 empty] | 6157 | 0 | 0x0fc04750
SS2AlarmSKTemp4_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp4_Previsoka | [6 empty] | 6157 | 0 | 0x0fc04760
SS2AlarmTempTIA1Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA1Previsoka | [6 empty] | 6157 | 0 | 0x0fc04770
SS2AlarmTempTIA2Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA2Previsoka | [6 empty] | 6157 | 0 | 0x0fc04780
SS2AlarmTempTIA3Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA3Previsoka | [6 empty] | 6157 | 0 | 0x0fc04790
SS2AlarmTempTIA4Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA4Previsoka | [6 empty] | 6157 | 0 | 0x0fc047a0
SS2AlarmUPSKrmOmara_Alarm | DIGITAL | IOD_SS2 | SS2:.AlarmUPSKrmOmara_Alarm | [6 empty] | 6157 | 0 | 0x0fc047b0
SS2ComSCADA | DIGITAL | IOD_SS2 | SS2:.ComSCADA | [6 empty] | 6157 | 0 | 0x0fc047c0
SS2ComSCADA1 | DIGITAL | IOD_SS2 | SS2:.ComSCADA1 | [6 empty] | 6157 | 0 | 0x0fc047d0
SS2Date_Time0 | STRING | IOD_SS2 | SS2:.Date_Time[0] | [6 empty] | 6157 | 0 | 0x0fc047e0
SS2Date_Time1 | STRING | IOD_SS2 | SS2:.Date_Time[1] | [6 empty] | 6157 | 0 | 0x0fc047e1
SS2Date_Time2 | STRING | IOD_SS2 | SS2:.Date_Time[2] | [6 empty] | 6157 | 0 | 0x0fc047e2
SS2Date_Time3 | STRING | IOD_SS2 | SS2:.Date_Time[3] | [6 empty] | 6157 | 0 | 0x0fc047e3
SS2DatumCasDan | BYTE | IOD_SS2 | SS2:.DatumCas.Dan | [6 empty] | 6157 | 0 | 0x0fc047e4
SS2DatumCasLeto | BYTE | IOD_SS2 | SS2:.DatumCas.Leto | [6 empty] | 6157 | 0 | 0x0fc047e5
SS2DatumCasLeto2 | INT | IOD_SS2 | SS2:.DatumCas.Leto2 | [6 empty] | 6157 | 0 | 0x0fc047e6
SS2DatumCasMesec | BYTE | IOD_SS2 | SS2:.DatumCas.Mesec | [6 empty] | 6157 | 0 | 0x0fc047e7
SS2DatumCasMinuta | BYTE | IOD_SS2 | SS2:.DatumCas.Minuta | [6 empty] | 6157 | 0 | 0x0fc047e8
SS2DatumCasSekunda | BYTE | IOD_SS2 | SS2:.DatumCas.Sekunda | [6 empty] | 6157 | 0 | 0x0fc047e9
SS2DatumCasUra | BYTE | IOD_SS2 | SS2:.DatumCas.Ura | [6 empty] | 6157 | 0 | 0x0fc047ea
SS2ErrComKlima1 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[1] | [6 empty] | 6157 | 0 | 0x0fc047f0
SS2ErrComKlima2 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[2] | [6 empty] | 6157 | 0 | 0x0fc04800
SS2ErrComKlima3 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[3] | [6 empty] | 6157 | 0 | 0x0fc04810
SS2ErrComKlima4 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[4] | [6 empty] | 6157 | 0 | 0x0fc04820
SS2ErrComKlima5 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[5] | [6 empty] | 6157 | 0 | 0x0fc04830
SS2ErrComKlima6 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[6] | [6 empty] | 6157 | 0 | 0x0fc04840
SS2ErrCommScada | DIGITAL | IOD_SS2 | SS2:.ErrCommScada | [6 empty] | 6157 | 0 | 0x0fc04850
SS2ErrComPanelPLC | DIGITAL | IOD_SS2 | SS2:.ErrComPanelPLC | [6 empty] | 6157 | 0 | 0x0fc04860
SS2ErrComPMM1 | DIGITAL | IOD_SS2 | SS2:.ErrComPMM[1] | [6 empty] | 6157 | 0 | 0x0fc04870
SS2ErrComPMM2 | DIGITAL | IOD_SS2 | SS2:.ErrComPMM[2] | [6 empty] | 6157 | 0 | 0x0fc04880
SS2ErrComPort2 | DIGITAL | IOD_SS2 | SS2:.ErrComPort2 | [6 empty] | 6157 | 0 | 0x0fc04890
SS2ErrorComKlima1Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[1].Error | [6 empty] | 6157 | 0 | 0x0fc048a0
SS2ErrorComKlima1Status | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Status | [6 empty] | 6157 | 0 | 0x0fc048b0
SS2ErrorComKlima2Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[2].Error | [6 empty] | 6157 | 0 | 0x0fc048c0
SS2ErrorComKlima2Status | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Status | [6 empty] | 6157 | 0 | 0x0fc048d0
SS2ErrorComKlima3Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[3].Error | [6 empty] | 6157 | 0 | 0x0fc048e0
SS2ErrorComKlima3Status | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Status | [6 empty] | 6157 | 0 | 0x0fc048f0
SS2ErrorComKlima4Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[4].Error | [6 empty] | 6157 | 0 | 0x0fc04900
SS2ErrorComKlima4Status | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Status | [6 empty] | 6157 | 0 | 0x0fc04910
SS2ErrorComKlima5Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[5].Error | [6 empty] | 6157 | 0 | 0x0fc04920
SS2ErrorComKlima5Status | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Status | [6 empty] | 6157 | 0 | 0x0fc04930
SS2ErrorComKlima6Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[6].Error | [6 empty] | 6157 | 0 | 0x0fc04940
SS2ErrorComKlima6Status | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Status | [6 empty] | 6157 | 0 | 0x0fc04950
SS2ErrorComPMM1Error | DIGITAL | IOD_SS2 | SS2:.ErrorComPMM[1].Error | [6 empty] | 6157 | 0 | 0x0fc04960
SS2ErrorComPMM1Status | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Status | [6 empty] | 6157 | 0 | 0x0fc04970
SS2ErrorComPMM2Error | DIGITAL | IOD_SS2 | SS2:.ErrorComPMM[2].Error | [6 empty] | 6157 | 0 | 0x0fc04980
SS2ErrorComPMM2Status | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Status | [6 empty] | 6157 | 0 | 0x0fc04990
SS2Klima1ure | REAL | IOD_SS2 | SS2:.Klima1ure |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04991
SS2Klima2_1_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_1_Onemogocena | [6 empty] | 6157 | 0 | 0x0fc049a0
SS2Klima2_2_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_2_Onemogocena | [6 empty] | 6157 | 0 | 0x0fc049b0
SS2Klima2_3_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_3_Onemogocena | [6 empty] | 6157 | 0 | 0x0fc049c0
SS2Klima2_4_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_4_Onemogocena | [6 empty] | 6157 | 0 | 0x0fc049d0
SS2Klima2_5_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_5_Onemogocena | [6 empty] | 6157 | 0 | 0x0fc049e0
SS2Klima2_6_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_6_Onemogocena | [6 empty] | 6157 | 0 | 0x0fc049f0
SS2Klima2ure | REAL | IOD_SS2 | SS2:.Klima2ure |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04a00
SS2Klima3ure | REAL | IOD_SS2 | SS2:.Klima3ure |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04a01
SS2Klima4ure | REAL | IOD_SS2 | SS2:.Klima4ure |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04a02
SS2Klima5ure | REAL | IOD_SS2 | SS2:.Klima5ure |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04a03
SS2Klima6ure | REAL | IOD_SS2 | SS2:.Klima6ure |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04a04
SS2Klima1GrelecStatus | BYTE | IOD_SS2 | SS2:.Klima[1].GrelecStatus | [6 empty] | 6157 | 0 | 0x0fc04a05
SS2Klima1IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[1].IzhodniVentilator | [6 empty] | 6157 | 0 | 0x0fc04a10
SS2Klima1IzhodniVentStatus | BYTE | IOD_SS2 | SS2:.Klima[1].IzhodniVentStatus | [6 empty] | 6157 | 0 | 0x0fc04a20
SS2Klima1Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[1].Kompresor1 | [6 empty] | 6157 | 0 | 0x0fc04a30
SS2Klima1Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[1].Kompresor2 | [6 empty] | 6157 | 0 | 0x0fc04a40
SS2Klima1KompresorStatus | BYTE | IOD_SS2 | SS2:.Klima[1].KompresorStatus | [6 empty] | 6157 | 0 | 0x0fc04a50
SS2Klima1NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[1].NacinRazvlaz | [6 empty] | 6157 | 0 | 0x0fc04a51
SS2Klima1NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[1].NastMaxTemp | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04a52
SS2Klima1NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[1].NastMaxVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04a53
SS2Klima1NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[1].NastMinTemp | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04a54
SS2Klima1NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[1].NastMinVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04a55
SS2Klima1NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[1].NastTempProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04a56
SS2Klima1NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[1].NastVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04a57
SS2Klima1ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[1].ObratUreFilter |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04a58
SS2Klima1ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[1].ObratUreKompresor1 |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04a59
SS2Klima1ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[1].ObratUreKompresor2 |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04a5a
SS2Klima1ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[1].ObratUreVent |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04a5b
SS2Klima1Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[1].Razvlazevanje | [6 empty] | 6157 | 0 | 0x0fc04a60
SS2Klima1SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[1].SenzorjiStatus | [6 empty] | 6157 | 0 | 0x0fc04a70
SS2Klima1TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[1].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04a80
SS2Klima1VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[1].VentilGretjeOdpiranje | [6 empty] | 6157 | 0 | 0x0fc04a90
SS2Klima1VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[1].VentilGretjeZapiranje | [6 empty] | 6157 | 0 | 0x0fc04aa0
SS2Klima1Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[1].Vlazenje | [6 empty] | 6157 | 0 | 0x0fc04ab0
SS2Klima1VlazilecStatus | BYTE | IOD_SS2 | SS2:.Klima[1].VlazilecStatus | [6 empty] | 6157 | 0 | 0x0fc04ac0
SS2Klima1VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[1].VlaznostProstora | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04ac1
SS2Klima2GrelecStatus | BYTE | IOD_SS2 | SS2:.Klima[2].GrelecStatus | [6 empty] | 6157 | 0 | 0x0fc04ac2
SS2Klima2IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[2].IzhodniVentilator | [6 empty] | 6157 | 0 | 0x0fc04ad0
SS2Klima2IzhodniVentStatus | BYTE | IOD_SS2 | SS2:.Klima[2].IzhodniVentStatus | [6 empty] | 6157 | 0 | 0x0fc04ae0
SS2Klima2Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[2].Kompresor1 | [6 empty] | 6157 | 0 | 0x0fc04af0
SS2Klima2Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[2].Kompresor2 | [6 empty] | 6157 | 0 | 0x0fc04b00
SS2Klima2KompresorStatus | BYTE | IOD_SS2 | SS2:.Klima[2].KompresorStatus | [6 empty] | 6157 | 0 | 0x0fc04b10
SS2Klima2NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[2].NacinRazvlaz | [6 empty] | 6157 | 0 | 0x0fc04b11
SS2Klima2NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[2].NastMaxTemp | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04b12
SS2Klima2NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[2].NastMaxVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04b13
SS2Klima2NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[2].NastMinTemp | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04b14
SS2Klima2NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[2].NastMinVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04b15
SS2Klima2NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[2].NastTempProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04b16
SS2Klima2NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[2].NastVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04b17
SS2Klima2ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[2].ObratUreFilter |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04b18
SS2Klima2ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[2].ObratUreKompresor1 |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04b19
SS2Klima2ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[2].ObratUreKompresor2 |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04b1a
SS2Klima2ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[2].ObratUreVent |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04b1b
SS2Klima2Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[2].Razvlazevanje | [6 empty] | 6157 | 0 | 0x0fc04b20
SS2Klima2SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[2].SenzorjiStatus | [6 empty] | 6157 | 0 | 0x0fc04b30
SS2Klima2TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[2].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04b40
SS2Klima2VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[2].VentilGretjeOdpiranje | [6 empty] | 6157 | 0 | 0x0fc04b50
SS2Klima2VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[2].VentilGretjeZapiranje | [6 empty] | 6157 | 0 | 0x0fc04b60
SS2Klima2Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[2].Vlazenje | [6 empty] | 6157 | 0 | 0x0fc04b70
SS2Klima2VlazilecStatus | BYTE | IOD_SS2 | SS2:.Klima[2].VlazilecStatus | [6 empty] | 6157 | 0 | 0x0fc04b80
SS2Klima2VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[2].VlaznostProstora | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04b81
SS2Klima3GrelecStatus | BYTE | IOD_SS2 | SS2:.Klima[3].GrelecStatus | [6 empty] | 6157 | 0 | 0x0fc04b82
SS2Klima3IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[3].IzhodniVentilator | [6 empty] | 6157 | 0 | 0x0fc04b90
SS2Klima3IzhodniVentStatus | BYTE | IOD_SS2 | SS2:.Klima[3].IzhodniVentStatus | [6 empty] | 6157 | 0 | 0x0fc04ba0
SS2Klima3Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[3].Kompresor1 | [6 empty] | 6157 | 0 | 0x0fc04bb0
SS2Klima3Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[3].Kompresor2 | [6 empty] | 6157 | 0 | 0x0fc04bc0
SS2Klima3KompresorStatus | BYTE | IOD_SS2 | SS2:.Klima[3].KompresorStatus | [6 empty] | 6157 | 0 | 0x0fc04bd0
SS2Klima3NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[3].NacinRazvlaz | [6 empty] | 6157 | 0 | 0x0fc04bd1
SS2Klima3NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[3].NastMaxTemp | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04bd2
SS2Klima3NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[3].NastMaxVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04bd3
SS2Klima3NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[3].NastMinTemp | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04bd4
SS2Klima3NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[3].NastMinVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04bd5
SS2Klima3NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[3].NastTempProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04bd6
SS2Klima3NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[3].NastVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04bd7
SS2Klima3ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[3].ObratUreFilter |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04bd8
SS2Klima3ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[3].ObratUreKompresor1 |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04bd9
SS2Klima3ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[3].ObratUreKompresor2 |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04bda
SS2Klima3ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[3].ObratUreVent |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04bdb
SS2Klima3Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[3].Razvlazevanje | [6 empty] | 6157 | 0 | 0x0fc04be0
SS2Klima3SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[3].SenzorjiStatus | [6 empty] | 6157 | 0 | 0x0fc04bf0
SS2Klima3TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[3].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04c00
SS2Klima3VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[3].VentilGretjeOdpiranje | [6 empty] | 6157 | 0 | 0x0fc04c10
SS2Klima3VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[3].VentilGretjeZapiranje | [6 empty] | 6157 | 0 | 0x0fc04c20
SS2Klima3Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[3].Vlazenje | [6 empty] | 6157 | 0 | 0x0fc04c30
SS2Klima3VlazilecStatus | BYTE | IOD_SS2 | SS2:.Klima[3].VlazilecStatus | [6 empty] | 6157 | 0 | 0x0fc04c40
SS2Klima3VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[3].VlaznostProstora | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04c41
SS2Klima4GrelecStatus | BYTE | IOD_SS2 | SS2:.Klima[4].GrelecStatus | [6 empty] | 6157 | 0 | 0x0fc04c42
SS2Klima4IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[4].IzhodniVentilator | [6 empty] | 6157 | 0 | 0x0fc04c50
SS2Klima4IzhodniVentStatus | BYTE | IOD_SS2 | SS2:.Klima[4].IzhodniVentStatus | [6 empty] | 6157 | 0 | 0x0fc04c60
SS2Klima4Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[4].Kompresor1 | [6 empty] | 6157 | 0 | 0x0fc04c70
SS2Klima4Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[4].Kompresor2 | [6 empty] | 6157 | 0 | 0x0fc04c80
SS2Klima4KompresorStatus | BYTE | IOD_SS2 | SS2:.Klima[4].KompresorStatus | [6 empty] | 6157 | 0 | 0x0fc04c90
SS2Klima4NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[4].NacinRazvlaz | [6 empty] | 6157 | 0 | 0x0fc04c91
SS2Klima4NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[4].NastMaxTemp | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04c92
SS2Klima4NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[4].NastMaxVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04c93
SS2Klima4NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[4].NastMinTemp | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04c94
SS2Klima4NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[4].NastMinVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04c95
SS2Klima4NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[4].NastTempProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04c96
SS2Klima4NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[4].NastVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04c97
SS2Klima4ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[4].ObratUreFilter |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04c98
SS2Klima4ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[4].ObratUreKompresor1 |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04c99
SS2Klima4ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[4].ObratUreKompresor2 |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04c9a
SS2Klima4ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[4].ObratUreVent |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04c9b
SS2Klima4Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[4].Razvlazevanje | [6 empty] | 6157 | 0 | 0x0fc04ca0
SS2Klima4SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[4].SenzorjiStatus | [6 empty] | 6157 | 0 | 0x0fc04cb0
SS2Klima4TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[4].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04cc0
SS2Klima4VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[4].VentilGretjeOdpiranje | [6 empty] | 6157 | 0 | 0x0fc04cd0
SS2Klima4VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[4].VentilGretjeZapiranje | [6 empty] | 6157 | 0 | 0x0fc04ce0
SS2Klima4Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[4].Vlazenje | [6 empty] | 6157 | 0 | 0x0fc04cf0
SS2Klima4VlazilecStatus | BYTE | IOD_SS2 | SS2:.Klima[4].VlazilecStatus | [6 empty] | 6157 | 0 | 0x0fc04d00
SS2Klima4VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[4].VlaznostProstora | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04d01
SS2Klima5GrelecStatus | BYTE | IOD_SS2 | SS2:.Klima[5].GrelecStatus | [6 empty] | 6157 | 0 | 0x0fc04d02
SS2Klima5IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[5].IzhodniVentilator | [6 empty] | 6157 | 0 | 0x0fc04d10
SS2Klima5IzhodniVentStatus | BYTE | IOD_SS2 | SS2:.Klima[5].IzhodniVentStatus | [6 empty] | 6157 | 0 | 0x0fc04d20
SS2Klima5Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[5].Kompresor1 | [6 empty] | 6157 | 0 | 0x0fc04d30
SS2Klima5Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[5].Kompresor2 | [6 empty] | 6157 | 0 | 0x0fc04d40
SS2Klima5KompresorStatus | BYTE | IOD_SS2 | SS2:.Klima[5].KompresorStatus | [6 empty] | 6157 | 0 | 0x0fc04d50
SS2Klima5NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[5].NacinRazvlaz | [6 empty] | 6157 | 0 | 0x0fc04d51
SS2Klima5NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[5].NastMaxTemp | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04d52
SS2Klima5NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[5].NastMaxVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04d53
SS2Klima5NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[5].NastMinTemp | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04d54
SS2Klima5NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[5].NastMinVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04d55
SS2Klima5NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[5].NastTempProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04d56
SS2Klima5NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[5].NastVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04d57
SS2Klima5ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[5].ObratUreFilter |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04d58
SS2Klima5ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[5].ObratUreKompresor1 |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04d59
SS2Klima5ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[5].ObratUreKompresor2 |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04d5a
SS2Klima5ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[5].ObratUreVent |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04d5b
SS2Klima5Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[5].Razvlazevanje | [6 empty] | 6157 | 0 | 0x0fc04d60
SS2Klima5SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[5].SenzorjiStatus | [6 empty] | 6157 | 0 | 0x0fc04d70
SS2Klima5TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[5].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04d80
SS2Klima5VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[5].VentilGretjeOdpiranje | [6 empty] | 6157 | 0 | 0x0fc04d90
SS2Klima5VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[5].VentilGretjeZapiranje | [6 empty] | 6157 | 0 | 0x0fc04da0
SS2Klima5Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[5].Vlazenje | [6 empty] | 6157 | 0 | 0x0fc04db0
SS2Klima5VlazilecStatus | BYTE | IOD_SS2 | SS2:.Klima[5].VlazilecStatus | [6 empty] | 6157 | 0 | 0x0fc04dc0
SS2Klima5VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[5].VlaznostProstora | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04dc1
SS2Klima6GrelecStatus | BYTE | IOD_SS2 | SS2:.Klima[6].GrelecStatus | [6 empty] | 6157 | 0 | 0x0fc04dc2
SS2Klima6IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[6].IzhodniVentilator | [6 empty] | 6157 | 0 | 0x0fc04dd0
SS2Klima6IzhodniVentStatus | BYTE | IOD_SS2 | SS2:.Klima[6].IzhodniVentStatus | [6 empty] | 6157 | 0 | 0x0fc04de0
SS2Klima6Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[6].Kompresor1 | [6 empty] | 6157 | 0 | 0x0fc04df0
SS2Klima6Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[6].Kompresor2 | [6 empty] | 6157 | 0 | 0x0fc04e00
SS2Klima6KompresorStatus | BYTE | IOD_SS2 | SS2:.Klima[6].KompresorStatus | [6 empty] | 6157 | 0 | 0x0fc04e10
SS2Klima6NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[6].NacinRazvlaz | [6 empty] | 6157 | 0 | 0x0fc04e11
SS2Klima6NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[6].NastMaxTemp | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04e12
SS2Klima6NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[6].NastMaxVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04e13
SS2Klima6NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[6].NastMinTemp | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04e14
SS2Klima6NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[6].NastMinVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04e15
SS2Klima6NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[6].NastTempProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04e16
SS2Klima6NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[6].NastVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04e17
SS2Klima6ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[6].ObratUreFilter |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04e18
SS2Klima6ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[6].ObratUreKompresor1 |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04e19
SS2Klima6ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[6].ObratUreKompresor2 |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04e1a
SS2Klima6ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[6].ObratUreVent |  |  |  |  | h | #### | 6157 | 0 | 0x0fc04e1b
SS2Klima6Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[6].Razvlazevanje | [6 empty] | 6157 | 0 | 0x0fc04e20
SS2Klima6SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[6].SenzorjiStatus | [6 empty] | 6157 | 0 | 0x0fc04e30
SS2Klima6TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[6].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc04e40
SS2Klima6VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[6].VentilGretjeOdpiranje | [6 empty] | 6157 | 0 | 0x0fc04e50
SS2Klima6VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[6].VentilGretjeZapiranje | [6 empty] | 6157 | 0 | 0x0fc04e60
SS2Klima6Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[6].Vlazenje | [6 empty] | 6157 | 0 | 0x0fc04e70
SS2Klima6VlazilecStatus | BYTE | IOD_SS2 | SS2:.Klima[6].VlazilecStatus | [6 empty] | 6157 | 0 | 0x0fc04e80
SS2Klima6VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[6].VlaznostProstora | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc04e81
SS2KlimaError1AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].AlarmKompresor1 | [6 empty] | 6157 | 0 | 0x0fc04e90
SS2KlimaError1AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].AlarmKompresor2 | [6 empty] | 6157 | 0 | 0x0fc04ea0
SS2KlimaError1FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].FenThermalCutout | [6 empty] | 6157 | 0 | 0x0fc04eb0
SS2KlimaError1IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].IzlivVode | [6 empty] | 6157 | 0 | 0x0fc04ec0
SS2KlimaError1Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].Kompresor1naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc04ed0
SS2KlimaError1Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].Kompresor2naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc04ee0
SS2KlimaError1NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NapakaPriPretokuVode | [6 empty] | 6157 | 0 | 0x0fc04ef0
SS2KlimaError1NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NapakaPriPretokuZraka | [6 empty] | 6157 | 0 | 0x0fc04f00
SS2KlimaError1NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NapakaSenzorVlaznosti | [6 empty] | 6157 | 0 | 0x0fc04f10
SS2KlimaError1NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NapakaTSTemperaturaProstora | [6 empty] | 6157 | 0 | 0x0fc04f20
SS2KlimaError1NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NapakaVlazilca | [6 empty] | 6157 | 0 | 0x0fc04f30
SS2KlimaError1NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NizekPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x0fc04f40
SS2KlimaError1NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NizekPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x0fc04f50
SS2KlimaError1NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NizkaTempVProstoru | [6 empty] | 6157 | 0 | 0x0fc04f60
SS2KlimaError1NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NizkaVlaznost | [6 empty] | 6157 | 0 | 0x0fc04f70
SS2KlimaError1PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].PozarniAlarm | [6 empty] | 6157 | 0 | 0x0fc04f80
SS2KlimaError1ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].ThermalCutoutHeater1 | [6 empty] | 6157 | 0 | 0x0fc04f90
SS2KlimaError1ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].ThermalCutoutHeater2 | [6 empty] | 6157 | 0 | 0x0fc04fa0
SS2KlimaError1VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].VentilatorNaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc04fb0
SS2KlimaError1VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].VisokaTempVProstoru | [6 empty] | 6157 | 0 | 0x0fc04fc0
SS2KlimaError1VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].VisokaVlaznost | [6 empty] | 6157 | 0 | 0x0fc04fd0
SS2KlimaError1VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].VisokPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x0fc04fe0
SS2KlimaError1VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].VisokPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x0fc04ff0
SS2KlimaError1ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].ZamasenFilter | [6 empty] | 6157 | 0 | 0x0fc05000
SS2KlimaError1ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].ZunanjiAlarm | [6 empty] | 6157 | 0 | 0x0fc05010
SS2KlimaError2AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].AlarmKompresor1 | [6 empty] | 6157 | 0 | 0x0fc05020
SS2KlimaError2AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].AlarmKompresor2 | [6 empty] | 6157 | 0 | 0x0fc05030
SS2KlimaError2FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].FenThermalCutout | [6 empty] | 6157 | 0 | 0x0fc05040
SS2KlimaError2IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].IzlivVode | [6 empty] | 6157 | 0 | 0x0fc05050
SS2KlimaError2Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].Kompresor1naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc05060
SS2KlimaError2Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].Kompresor2naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc05070
SS2KlimaError2NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NapakaPriPretokuVode | [6 empty] | 6157 | 0 | 0x0fc05080
SS2KlimaError2NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NapakaPriPretokuZraka | [6 empty] | 6157 | 0 | 0x0fc05090
SS2KlimaError2NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NapakaSenzorVlaznosti | [6 empty] | 6157 | 0 | 0x0fc050a0
SS2KlimaError2NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NapakaTSTemperaturaProstora | [6 empty] | 6157 | 0 | 0x0fc050b0
SS2KlimaError2NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NapakaVlazilca | [6 empty] | 6157 | 0 | 0x0fc050c0
SS2KlimaError2NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NizekPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x0fc050d0
SS2KlimaError2NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NizekPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x0fc050e0
SS2KlimaError2NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NizkaTempVProstoru | [6 empty] | 6157 | 0 | 0x0fc050f0
SS2KlimaError2NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NizkaVlaznost | [6 empty] | 6157 | 0 | 0x0fc05100
SS2KlimaError2PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].PozarniAlarm | [6 empty] | 6157 | 0 | 0x0fc05110
SS2KlimaError2ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].ThermalCutoutHeater1 | [6 empty] | 6157 | 0 | 0x0fc05120
SS2KlimaError2ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].ThermalCutoutHeater2 | [6 empty] | 6157 | 0 | 0x0fc05130
SS2KlimaError2VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].VentilatorNaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc05140
SS2KlimaError2VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].VisokaTempVProstoru | [6 empty] | 6157 | 0 | 0x0fc05150
SS2KlimaError2VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].VisokaVlaznost | [6 empty] | 6157 | 0 | 0x0fc05160
SS2KlimaError2VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].VisokPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x0fc05170
SS2KlimaError2VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].VisokPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x0fc05180
SS2KlimaError2ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].ZamasenFilter | [6 empty] | 6157 | 0 | 0x0fc05190
SS2KlimaError2ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].ZunanjiAlarm | [6 empty] | 6157 | 0 | 0x0fc051a0
SS2KlimaError3AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].AlarmKompresor1 | [6 empty] | 6157 | 0 | 0x0fc051b0
SS2KlimaError3AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].AlarmKompresor2 | [6 empty] | 6157 | 0 | 0x0fc051c0
SS2KlimaError3FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].FenThermalCutout | [6 empty] | 6157 | 0 | 0x0fc051d0
SS2KlimaError3IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].IzlivVode | [6 empty] | 6157 | 0 | 0x0fc051e0
SS2KlimaError3Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].Kompresor1naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc051f0
SS2KlimaError3Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].Kompresor2naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc05200
SS2KlimaError3NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NapakaPriPretokuVode | [6 empty] | 6157 | 0 | 0x0fc05210
SS2KlimaError3NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NapakaPriPretokuZraka | [6 empty] | 6157 | 0 | 0x0fc05220
SS2KlimaError3NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NapakaSenzorVlaznosti | [6 empty] | 6157 | 0 | 0x0fc05230
SS2KlimaError3NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NapakaTSTemperaturaProstora | [6 empty] | 6157 | 0 | 0x0fc05240
SS2KlimaError3NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NapakaVlazilca | [6 empty] | 6157 | 0 | 0x0fc05250
SS2KlimaError3NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NizekPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x0fc05260
SS2KlimaError3NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NizekPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x0fc05270
SS2KlimaError3NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NizkaTempVProstoru | [6 empty] | 6157 | 0 | 0x0fc05280
SS2KlimaError3NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NizkaVlaznost | [6 empty] | 6157 | 0 | 0x0fc05290
SS2KlimaError3PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].PozarniAlarm | [6 empty] | 6157 | 0 | 0x0fc052a0
SS2KlimaError3ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].ThermalCutoutHeater1 | [6 empty] | 6157 | 0 | 0x0fc052b0
SS2KlimaError3ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].ThermalCutoutHeater2 | [6 empty] | 6157 | 0 | 0x0fc052c0
SS2KlimaError3VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].VentilatorNaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc052d0
SS2KlimaError3VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].VisokaTempVProstoru | [6 empty] | 6157 | 0 | 0x0fc052e0
SS2KlimaError3VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].VisokaVlaznost | [6 empty] | 6157 | 0 | 0x0fc052f0
SS2KlimaError3VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].VisokPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x0fc05300
SS2KlimaError3VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].VisokPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x0fc05310
SS2KlimaError3ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].ZamasenFilter | [6 empty] | 6157 | 0 | 0x0fc05320
SS2KlimaError3ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].ZunanjiAlarm | [6 empty] | 6157 | 0 | 0x0fc05330
SS2KlimaError4AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].AlarmKompresor1 | [6 empty] | 6157 | 0 | 0x0fc05340
SS2KlimaError4AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].AlarmKompresor2 | [6 empty] | 6157 | 0 | 0x0fc05350
SS2KlimaError4FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].FenThermalCutout | [6 empty] | 6157 | 0 | 0x0fc05360
SS2KlimaError4IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].IzlivVode | [6 empty] | 6157 | 0 | 0x0fc05370
SS2KlimaError4Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].Kompresor1naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc05380
SS2KlimaError4Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].Kompresor2naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc05390
SS2KlimaError4NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NapakaPriPretokuVode | [6 empty] | 6157 | 0 | 0x0fc053a0
SS2KlimaError4NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NapakaPriPretokuZraka | [6 empty] | 6157 | 0 | 0x0fc053b0
SS2KlimaError4NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NapakaSenzorVlaznosti | [6 empty] | 6157 | 0 | 0x0fc053c0
SS2KlimaError4NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NapakaTSTemperaturaProstora | [6 empty] | 6157 | 0 | 0x0fc053d0
SS2KlimaError4NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NapakaVlazilca | [6 empty] | 6157 | 0 | 0x0fc053e0
SS2KlimaError4NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NizekPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x0fc053f0
SS2KlimaError4NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NizekPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x0fc05400
SS2KlimaError4NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NizkaTempVProstoru | [6 empty] | 6157 | 0 | 0x0fc05410
SS2KlimaError4NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NizkaVlaznost | [6 empty] | 6157 | 0 | 0x0fc05420
SS2KlimaError4PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].PozarniAlarm | [6 empty] | 6157 | 0 | 0x0fc05430
SS2KlimaError4ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].ThermalCutoutHeater1 | [6 empty] | 6157 | 0 | 0x0fc05440
SS2KlimaError4ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].ThermalCutoutHeater2 | [6 empty] | 6157 | 0 | 0x0fc05450
SS2KlimaError4VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].VentilatorNaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc05460
SS2KlimaError4VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].VisokaTempVProstoru | [6 empty] | 6157 | 0 | 0x0fc05470
SS2KlimaError4VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].VisokaVlaznost | [6 empty] | 6157 | 0 | 0x0fc05480
SS2KlimaError4VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].VisokPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x0fc05490
SS2KlimaError4VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].VisokPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x0fc054a0
SS2KlimaError4ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].ZamasenFilter | [6 empty] | 6157 | 0 | 0x0fc054b0
SS2KlimaError4ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].ZunanjiAlarm | [6 empty] | 6157 | 0 | 0x0fc054c0
SS2KlimaError5AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].AlarmKompresor1 | [6 empty] | 6157 | 0 | 0x0fc054d0
SS2KlimaError5AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].AlarmKompresor2 | [6 empty] | 6157 | 0 | 0x0fc054e0
SS2KlimaError5FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].FenThermalCutout | [6 empty] | 6157 | 0 | 0x0fc054f0
SS2KlimaError5IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].IzlivVode | [6 empty] | 6157 | 0 | 0x0fc05500
SS2KlimaError5Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].Kompresor1naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc05510
SS2KlimaError5Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].Kompresor2naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc05520
SS2KlimaError5NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NapakaPriPretokuVode | [6 empty] | 6157 | 0 | 0x0fc05530
SS2KlimaError5NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NapakaPriPretokuZraka | [6 empty] | 6157 | 0 | 0x0fc05540
SS2KlimaError5NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NapakaSenzorVlaznosti | [6 empty] | 6157 | 0 | 0x0fc05550
SS2KlimaError5NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NapakaTSTemperaturaProstora | [6 empty] | 6157 | 0 | 0x0fc05560
SS2KlimaError5NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NapakaVlazilca | [6 empty] | 6157 | 0 | 0x0fc05570
SS2KlimaError5NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NizekPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x0fc05580
SS2KlimaError5NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NizekPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x0fc05590
SS2KlimaError5NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NizkaTempVProstoru | [6 empty] | 6157 | 0 | 0x0fc055a0
SS2KlimaError5NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NizkaVlaznost | [6 empty] | 6157 | 0 | 0x0fc055b0
SS2KlimaError5PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].PozarniAlarm | [6 empty] | 6157 | 0 | 0x0fc055c0
SS2KlimaError5ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].ThermalCutoutHeater1 | [6 empty] | 6157 | 0 | 0x0fc055d0
SS2KlimaError5ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].ThermalCutoutHeater2 | [6 empty] | 6157 | 0 | 0x0fc055e0
SS2KlimaError5VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].VentilatorNaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc055f0
SS2KlimaError5VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].VisokaTempVProstoru | [6 empty] | 6157 | 0 | 0x0fc05600
SS2KlimaError5VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].VisokaVlaznost | [6 empty] | 6157 | 0 | 0x0fc05610
SS2KlimaError5VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].VisokPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x0fc05620
SS2KlimaError5VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].VisokPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x0fc05630
SS2KlimaError5ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].ZamasenFilter | [6 empty] | 6157 | 0 | 0x0fc05640
SS2KlimaError5ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].ZunanjiAlarm | [6 empty] | 6157 | 0 | 0x0fc05650
SS2KlimaError6AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].AlarmKompresor1 | [6 empty] | 6157 | 0 | 0x0fc05660
SS2KlimaError6AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].AlarmKompresor2 | [6 empty] | 6157 | 0 | 0x0fc05670
SS2KlimaError6FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].FenThermalCutout | [6 empty] | 6157 | 0 | 0x0fc05680
SS2KlimaError6IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].IzlivVode | [6 empty] | 6157 | 0 | 0x0fc05690
SS2KlimaError6Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].Kompresor1naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc056a0
SS2KlimaError6Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].Kompresor2naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc056b0
SS2KlimaError6NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NapakaPriPretokuVode | [6 empty] | 6157 | 0 | 0x0fc056c0
SS2KlimaError6NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NapakaPriPretokuZraka | [6 empty] | 6157 | 0 | 0x0fc056d0
SS2KlimaError6NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NapakaSenzorVlaznosti | [6 empty] | 6157 | 0 | 0x0fc056e0
SS2KlimaError6NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NapakaTSTemperaturaProstora | [6 empty] | 6157 | 0 | 0x0fc056f0
SS2KlimaError6NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NapakaVlazilca | [6 empty] | 6157 | 0 | 0x0fc05700
SS2KlimaError6NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NizekPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x0fc05710
SS2KlimaError6NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NizekPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x0fc05720
SS2KlimaError6NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NizkaTempVProstoru | [6 empty] | 6157 | 0 | 0x0fc05730
SS2KlimaError6NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NizkaVlaznost | [6 empty] | 6157 | 0 | 0x0fc05740
SS2KlimaError6PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].PozarniAlarm | [6 empty] | 6157 | 0 | 0x0fc05750
SS2KlimaError6ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].ThermalCutoutHeater1 | [6 empty] | 6157 | 0 | 0x0fc05760
SS2KlimaError6ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].ThermalCutoutHeater2 | [6 empty] | 6157 | 0 | 0x0fc05770
SS2KlimaError6VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].VentilatorNaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x0fc05780
SS2KlimaError6VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].VisokaTempVProstoru | [6 empty] | 6157 | 0 | 0x0fc05790
SS2KlimaError6VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].VisokaVlaznost | [6 empty] | 6157 | 0 | 0x0fc057a0
SS2KlimaError6VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].VisokPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x0fc057b0
SS2KlimaError6VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].VisokPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x0fc057c0
SS2KlimaError6ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].ZamasenFilter | [6 empty] | 6157 | 0 | 0x0fc057d0
SS2KlimaError6ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].ZunanjiAlarm | [6 empty] | 6157 | 0 | 0x0fc057e0
SS2NacDeloKlima1_2Avtom | DIGITAL | IOD_SS2 | SS2:.NacDeloKlima1_2Avtom | [6 empty] | 6157 | 0 | 0x0fc057f0
SS2NacDeloKlima3_4Avtom | DIGITAL | IOD_SS2 | SS2:.NacDeloKlima3_4Avtom | [6 empty] | 6157 | 0 | 0x0fc05800
SS2NacDeloKlima5_6Avtom | DIGITAL | IOD_SS2 | SS2:.NacDeloKlima5_6Avtom | [6 empty] | 6157 | 0 | 0x0fc05810
SS2NapakaSenzorTemp1 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp1 | [6 empty] | 6157 |  | 0x0fc05820
SS2NapakaSenzorTemp2 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp2 | [6 empty] | 6157 | 0 | 0x0fc05830
SS2NapakaSenzorTemp3 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp3 | [6 empty] | 6157 | 0 | 0x0fc05840
SS2NapakaSenzorTemp4 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp4 | [6 empty] | 6157 | 0 | 0x0fc05850
SS2NapakaSenzorVlaga1 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga1 | [6 empty] | 6157 | 0 | 0x0fc05860
SS2NapakaSenzorVlaga2 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga2 | [6 empty] | 6157 | 0 | 0x0fc05870
SS2NapakaSenzorVlaga3 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga3 | [6 empty] | 6157 | 0 | 0x0fc05880
SS2NapakaSenzorVlaga4 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga4 | [6 empty] | 6157 | 0 | 0x0fc05890
SS2NastaviCasNaKrmilniku | DIGITAL | IOD_SS2 | SS2:.NastaviCasNaKrmilniku | [6 empty] | 6157 | 0 | 0x0fc058a0
SS2NastavitevUreKrUspesna | DIGITAL | IOD_SS2 | SS2:.NastavitevUreKrUspesna | [6 empty] | 6157 | 0 | 0x0fc058b0
SS2OpozoriloBaterijaPLC | DIGITAL | IOD_SS2 | SS2:.OpozoriloBaterijaPLC | [6 empty] | 6157 | 0 | 0x0fc058c0
SS2OpozoriloPMM2x17med60in8010 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[10] | [6 empty] | 6157 | 0 | 0x0fc058d0
SS2OpozoriloPMM2x17med60in8011 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[11] | [6 empty] | 6157 | 0 | 0x0fc058e0
SS2OpozoriloPMM2x17med60in8012 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[12] | [6 empty] | 6157 | 0 | 0x0fc058f0
SS2OpozoriloPMM2x17med60in8013 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[13] | [6 empty] | 6157 | 0 | 0x0fc05900
SS2OpozoriloPMM2x17med60in8014 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[14] | [6 empty] | 6157 | 0 | 0x0fc05910
SS2OpozoriloPMM2x17med60in8015 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[15] | [6 empty] | 6157 | 0 | 0x0fc05920
SS2OpozoriloPMM2x17med60in8016 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[16] | [6 empty] | 6157 | 0 | 0x0fc05930
SS2OpozoriloPMM2x17med60in8017 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[17] | [6 empty] | 6157 | 0 | 0x0fc05940
SS2OpozoriloPMM2x17med60in8018 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[18] | [6 empty] | 6157 | 0 | 0x0fc05950
SS2OpozoriloPMM2x17med60in8019 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[19] | [6 empty] | 6157 | 0 | 0x0fc05960
SS2OpozoriloPMM2x17med60in801 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[1] | [6 empty] | 6157 | 0 | 0x0fc05970
SS2OpozoriloPMM2x17med60in8020 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[20] | [6 empty] | 6157 | 0 | 0x0fc05980
SS2OpozoriloPMM2x17med60in8021 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[21] | [6 empty] | 6157 | 0 | 0x0fc05990
SS2OpozoriloPMM2x17med60in8022 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[22] | [6 empty] | 6157 | 0 | 0x0fc059a0
SS2OpozoriloPMM2x17med60in8023 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[23] | [6 empty] | 6157 | 0 | 0x0fc059b0
SS2OpozoriloPMM2x17med60in8024 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[24] | [6 empty] | 6157 | 0 | 0x0fc059c0
SS2OpozoriloPMM2x17med60in8025 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[25] | [6 empty] | 6157 | 0 | 0x0fc059d0
SS2OpozoriloPMM2x17med60in8026 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[26] | [6 empty] | 6157 | 0 | 0x0fc059e0
SS2OpozoriloPMM2x17med60in8027 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[27] | [6 empty] | 6157 | 0 | 0x0fc059f0
SS2OpozoriloPMM2x17med60in8028 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[28] | [6 empty] | 6157 | 0 | 0x0fc05a00
SS2OpozoriloPMM2x17med60in8029 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[29] | [6 empty] | 6157 | 0 | 0x0fc05a10
SS2OpozoriloPMM2x17med60in802 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[2] | [6 empty] | 6157 | 0 | 0x0fc05a20
SS2OpozoriloPMM2x17med60in8030 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[30] | [6 empty] | 6157 | 0 | 0x0fc05a30
SS2OpozoriloPMM2x17med60in8031 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[31] | [6 empty] | 6157 | 0 | 0x0fc05a40
SS2OpozoriloPMM2x17med60in8032 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[32] | [6 empty] | 6157 | 0 | 0x0fc05a50
SS2OpozoriloPMM2x17med60in8033 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[33] | [6 empty] | 6157 | 0 | 0x0fc05a60
SS2OpozoriloPMM2x17med60in8034 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[34] | [6 empty] | 6157 | 0 | 0x0fc05a70
SS2OpozoriloPMM2x17med60in8035 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[35] | [6 empty] | 6157 | 0 | 0x0fc05a80
SS2OpozoriloPMM2x17med60in8036 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[36] | [6 empty] | 6157 | 0 | 0x0fc05a90
SS2OpozoriloPMM2x17med60in8037 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[37] | [6 empty] | 6157 | 0 | 0x0fc05aa0
SS2OpozoriloPMM2x17med60in8038 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[38] | [6 empty] | 6157 | 0 | 0x0fc05ab0
SS2OpozoriloPMM2x17med60in8039 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[39] | [6 empty] | 6157 | 0 | 0x0fc05ac0
SS2OpozoriloPMM2x17med60in803 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[3] | [6 empty] | 6157 | 0 | 0x0fc05ad0
SS2OpozoriloPMM2x17med60in8040 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[40] | [6 empty] | 6157 | 0 | 0x0fc05ae0
SS2OpozoriloPMM2x17med60in8041 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[41] | [6 empty] | 6157 | 0 | 0x0fc05af0
SS2OpozoriloPMM2x17med60in8042 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[42] | [6 empty] | 6157 | 0 | 0x0fc05b00
SS2OpozoriloPMM2x17med60in804 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[4] | [6 empty] | 6157 | 0 | 0x0fc05b10
SS2OpozoriloPMM2x17med60in805 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[5] | [6 empty] | 6157 | 0 | 0x0fc05b20
SS2OpozoriloPMM2x17med60in806 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[6] | [6 empty] | 6157 | 0 | 0x0fc05b30
SS2OpozoriloPMM2x17med60in807 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[7] | [6 empty] | 6157 | 0 | 0x0fc05b40
SS2OpozoriloPMM2x17med60in808 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[8] | [6 empty] | 6157 | 0 | 0x0fc05b50
SS2OpozoriloPMM2x17med60in809 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[9] | [6 empty] | 6157 | 0 | 0x0fc05b60
SS2OznakeFaz10 | BYTE | IOD_SS2 | SS2:.OznakeFaz[10] | [6 empty] | 6157 | 0 | 0x0fc05b70
SS2OznakeFaz11 | BYTE | IOD_SS2 | SS2:.OznakeFaz[11] | [6 empty] | 6157 | 0 | 0x0fc05b71
SS2OznakeFaz12 | BYTE | IOD_SS2 | SS2:.OznakeFaz[12] | [6 empty] | 6157 | 0 | 0x0fc05b72
SS2OznakeFaz13 | BYTE | IOD_SS2 | SS2:.OznakeFaz[13] | [6 empty] | 6157 | 0 | 0x0fc05b73
SS2OznakeFaz14 | BYTE | IOD_SS2 | SS2:.OznakeFaz[14] | [6 empty] | 6157 | 0 | 0x0fc05b74
SS2OznakeFaz1 | BYTE | IOD_SS2 | SS2:.OznakeFaz[1] | [6 empty] | 6157 | 0 | 0x0fc05b75
SS2OznakeFaz2 | BYTE | IOD_SS2 | SS2:.OznakeFaz[2] | [6 empty] | 6157 | 0 | 0x0fc05b76
SS2OznakeFaz3 | BYTE | IOD_SS2 | SS2:.OznakeFaz[3] | [6 empty] | 6157 | 0 | 0x0fc05b77
SS2OznakeFaz4 | BYTE | IOD_SS2 | SS2:.OznakeFaz[4] | [6 empty] | 6157 | 0 | 0x0fc05b78
SS2OznakeFaz5 | BYTE | IOD_SS2 | SS2:.OznakeFaz[5] | [6 empty] | 6157 | 0 | 0x0fc05b79
SS2OznakeFaz6 | BYTE | IOD_SS2 | SS2:.OznakeFaz[6] | [6 empty] | 6157 | 0 | 0x0fc05b7a
SS2OznakeFaz7 | BYTE | IOD_SS2 | SS2:.OznakeFaz[7] | [6 empty] | 6157 | 0 | 0x0fc05b7b
SS2OznakeFaz8 | BYTE | IOD_SS2 | SS2:.OznakeFaz[8] | [6 empty] | 6157 | 0 | 0x0fc05b7c
SS2OznakeFaz9 | BYTE | IOD_SS2 | SS2:.OznakeFaz[9] | [6 empty] | 6157 | 0 | 0x0fc05b7d
SS2PhaseBool0 | DIGITAL | IOD_SS2 | SS2:.PhaseBool[0] | [6 empty] | 6157 | 0 | 0x0fc05b80
SS2PhaseBool1 | DIGITAL | IOD_SS2 | SS2:.PhaseBool[1] | [6 empty] | 6157 | 0 | 0x0fc05b90
SS2PhaseBool2 | DIGITAL | IOD_SS2 | SS2:.PhaseBool[2] | [6 empty] | 6157 | 0 | 0x0fc05ba0
SS2PhaseNext | DIGITAL | IOD_SS2 | SS2:.PhaseNext | [6 empty] | 6157 | 0 | 0x0fc05bb0
SS2PhaseNo | BYTE | IOD_SS2 | SS2:.PhaseNo | [6 empty] | 6157 | 0 | 0x0fc05bc0
SS2PhasePrev | DIGITAL | IOD_SS2 | SS2:.PhasePrev | [6 empty] | 6157 | 0 | 0x0fc05bd0
SS2PMM1OverCurrentBetw1 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentBetw[1] | [6 empty] | 6157 | 0 | 0x0fc05be0
SS2PMM1OverCurrentBetw2 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentBetw[2] | [6 empty] | 6157 | 0 | 0x0fc05bf0
SS2PMM1OverCurrentBetw3 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentBetw[3] | [6 empty] | 6157 | 0 | 0x0fc05c00
SS2PMM1OverCurrentOver1 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentOver[1] | [6 empty] | 6157 | 0 | 0x0fc05c10
SS2PMM1OverCurrentOver2 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentOver[2] | [6 empty] | 6157 | 0 | 0x0fc05c20
SS2PMM1OverCurrentOver3 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentOver[3] | [6 empty] | 6157 | 0 | 0x0fc05c30
SS2PMM1OverVoltage | DIGITAL | IOD_SS2 | SS2:.PMM1OverVoltage | [6 empty] | 6157 | 0 | 0x0fc05c40
SS2PMM2OverCurrentBetw1 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentBetw[1] | [6 empty] | 6157 | 0 | 0x0fc05c50
SS2PMM2OverCurrentBetw2 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentBetw[2] | [6 empty] | 6157 | 0 | 0x0fc05c60
SS2PMM2OverCurrentBetw3 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentBetw[3] | [6 empty] | 6157 | 0 | 0x0fc05c70
SS2PMM2OverCurrentOver1 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentOver[1] | [6 empty] | 6157 | 0 | 0x0fc05c80
SS2PMM2OverCurrentOver2 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentOver[2] | [6 empty] | 6157 | 0 | 0x0fc05c90
SS2PMM2OverCurrentOver3 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentOver[3] | [6 empty] | 6157 | 0 | 0x0fc05ca0
SS2PMM2OverVoltage | DIGITAL | IOD_SS2 | SS2:.PMM2OverVoltage | [6 empty] | 6157 | 0 | 0x0fc05cb0
SS2PMM2x17 | DIGITAL | IOD_SS2 | SS2:.PMM2x17 | [6 empty] | 6157 | 0 | 0x0fc05cc0
SS2PMM1ActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMM[1].ActiveEnergyConsumed_kWh |  |  |  |  | kVAr | #### | 6157 | 0 | 0x0fc05cd0
SS2PMM1ActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMM[1].ActivePowerPhaseA_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 0 | 0x0fc05cd1
SS2PMM1ActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMM[1].ActivePowerPhaseB_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 0 | 0x0fc05cd2
SS2PMM1ActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMM[1].ActivePowerPhaseC_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 0 | 0x0fc05cd3
SS2PMM1AlarmPhase1C01_16_60to80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C01_16_60to80 | [6 empty] | 6157 | 0 | 0x0fc05cd4
SS2PMM1AlarmPhase1C01_16_over80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C01_16_over80 | [6 empty] | 6157 | 0 | 0x0fc05cd5
SS2PMM1AlarmPhase1C17_32_60to80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C17_32_60to80 | [6 empty] | 6157 | 0 | 0x0fc05cd6
SS2PMM1AlarmPhase1C17_32_over80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C17_32_over80 | [6 empty] | 6157 | 0 | 0x0fc05cd7
SS2PMM1AlarmPhase1C33_42_60to80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C33_42_60to80 | [6 empty] | 6157 | 0 | 0x0fc05cd8
SS2PMM1AlarmPhase1C33_42_over80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C33_42_over80 | [6 empty] | 6157 | 0 | 0x0fc05cd9
SS2PMM1AlarmPhase1GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].GlobalAlarmReg | [6 empty] | 6157 | 0 | 0x0fc05cda
SS2PMM1AlarmPhase2C01_16_60to80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C01_16_60to80 | [6 empty] | 6157 | 0 | 0x0fc05cdb
SS2PMM1AlarmPhase2C01_16_over80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C01_16_over80 | [6 empty] | 6157 | 0 | 0x0fc05cdc
SS2PMM1AlarmPhase2C17_32_60to80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C17_32_60to80 | [6 empty] | 6157 | 0 | 0x0fc05cdd
SS2PMM1AlarmPhase2C17_32_over80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C17_32_over80 | [6 empty] | 6157 | 0 | 0x0fc05cde
SS2PMM1AlarmPhase2C33_42_60to80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C33_42_60to80 | [6 empty] | 6157 | 0 | 0x0fc05cdf
SS2PMM1AlarmPhase2C33_42_over80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C33_42_over80 | [6 empty] | 6157 | 0 | 0x0fc05ce0
SS2PMM1AlarmPhase2GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].GlobalAlarmReg | [6 empty] | 6157 | 0 | 0x0fc05ce1
SS2PMM1AlarmPhase3C01_16_60to80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C01_16_60to80 | [6 empty] | 6157 | 0 | 0x0fc05ce2
SS2PMM1AlarmPhase3C01_16_over80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C01_16_over80 | [6 empty] | 6157 | 0 | 0x0fc05ce3
SS2PMM1AlarmPhase3C17_32_60to80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C17_32_60to80 | [6 empty] | 6157 | 0 | 0x0fc05ce4
SS2PMM1AlarmPhase3C17_32_over80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C17_32_over80 | [6 empty] | 6157 | 0 | 0x0fc05ce5
SS2PMM1AlarmPhase3C33_42_60to80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C33_42_60to80 | [6 empty] | 6157 | 0 | 0x0fc05ce6
SS2PMM1AlarmPhase3C33_42_over80 | BYTE | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C33_42_over80 | [6 empty] | 6157 | 0 | 0x0fc05ce7
SS2PMM1AlarmPhase3GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].GlobalAlarmReg | [6 empty] | 6157 | 0 | 0x0fc05ce8
SS2PMM1AparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[1].AparentPowerPhaseA | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05ce9
SS2PMM1AparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[1].AparentPowerPhaseB | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05cea
SS2PMM1AparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[1].AparentPowerPhaseC | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05ceb
SS2PMM1AverageCurrent_A | REAL | IOD_SS2 | SS2:.PMM[1].AverageCurrent_A | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05cec
SS2PMM1AveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMM[1].AveragePhaseToNeutral_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05ced
SS2PMM1AveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMM[1].AveragePhaseToPhase_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05cee
SS2PMM1CurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMM[1].CurrentInPhaseA_A | 0 | 500 | 0 | 500 | A | ####.# | 6157 | 0 | 0x0fc05cef
SS2PMM1CurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMM[1].CurrentInPhaseB_A | 0 | 500 | 0 | 500 | A | ####.# | 6157 | 0 | 0x0fc05cf0
SS2PMM1CurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMM[1].CurrentInPhaseC_A | 0 | 500 | 0 | 500 | A | ####.# | 6157 | 0 | 0x0fc05cf1
SS2PMM1Frequency_Hz | REAL | IOD_SS2 | SS2:.PMM[1].Frequency_Hz | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 0 | 0x0fc05cf2
SS2PMM1Phase1Current10 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[10] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05cf3
SS2PMM1Phase1Current11 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[11] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05cf4
SS2PMM1Phase1Current12 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[12] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05cf5
SS2PMM1Phase1Current13 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[13] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05cf6
SS2PMM1Phase1Current14 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[14] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05cf7
SS2PMM1Phase1Current15 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[15] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05cf8
SS2PMM1Phase1Current16 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[16] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05cf9
SS2PMM1Phase1Current17 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[17] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05cfa
SS2PMM1Phase1Current18 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[18] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05cfb
SS2PMM1Phase1Current19 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[19] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05cfc
SS2PMM1Phase1Current1 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[1] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05cfd
SS2PMM1Phase1Current20 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[20] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05cfe
SS2PMM1Phase1Current21 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[21] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05cff
SS2PMM1Phase1Current22 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[22] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d00
SS2PMM1Phase1Current23 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[23] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d01
SS2PMM1Phase1Current24 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[24] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d02
SS2PMM1Phase1Current25 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[25] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d03
SS2PMM1Phase1Current26 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[26] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d04
SS2PMM1Phase1Current27 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[27] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d05
SS2PMM1Phase1Current28 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[28] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d06
SS2PMM1Phase1Current29 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[29] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d07
SS2PMM1Phase1Current2 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[2] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d08
SS2PMM1Phase1Current30 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[30] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d09
SS2PMM1Phase1Current31 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[31] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d0a
SS2PMM1Phase1Current32 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[32] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d0b
SS2PMM1Phase1Current33 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[33] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d0c
SS2PMM1Phase1Current34 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[34] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d0d
SS2PMM1Phase1Current35 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[35] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d0e
SS2PMM1Phase1Current36 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[36] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d0f
SS2PMM1Phase1Current37 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[37] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d10
SS2PMM1Phase1Current38 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[38] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d11
SS2PMM1Phase1Current39 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[39] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d12
SS2PMM1Phase1Current3 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[3] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d13
SS2PMM1Phase1Current40 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[40] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d14
SS2PMM1Phase1Current41 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[41] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d15
SS2PMM1Phase1Current42 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[42] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d16
SS2PMM1Phase1Current4 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[4] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d17
SS2PMM1Phase1Current5 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[5] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d18
SS2PMM1Phase1Current6 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[6] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d19
SS2PMM1Phase1Current7 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[7] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d1a
SS2PMM1Phase1Current8 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[8] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d1b
SS2PMM1Phase1Current9 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[9] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d1c
SS2PMM1Phase2Current10 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[10] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d1d
SS2PMM1Phase2Current11 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[11] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d1e
SS2PMM1Phase2Current12 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[12] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d1f
SS2PMM1Phase2Current13 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[13] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d20
SS2PMM1Phase2Current14 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[14] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d21
SS2PMM1Phase2Current15 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[15] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d22
SS2PMM1Phase2Current16 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[16] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d23
SS2PMM1Phase2Current17 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[17] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d24
SS2PMM1Phase2Current18 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[18] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d25
SS2PMM1Phase2Current19 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[19] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d26
SS2PMM1Phase2Current1 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[1] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d27
SS2PMM1Phase2Current20 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[20] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d28
SS2PMM1Phase2Current21 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[21] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d29
SS2PMM1Phase2Current22 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[22] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d2a
SS2PMM1Phase2Current23 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[23] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d2b
SS2PMM1Phase2Current24 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[24] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d2c
SS2PMM1Phase2Current25 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[25] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d2d
SS2PMM1Phase2Current26 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[26] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d2e
SS2PMM1Phase2Current27 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[27] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d2f
SS2PMM1Phase2Current28 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[28] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d30
SS2PMM1Phase2Current29 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[29] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d31
SS2PMM1Phase2Current2 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[2] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d32
SS2PMM1Phase2Current30 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[30] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d33
SS2PMM1Phase2Current31 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[31] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d34
SS2PMM1Phase2Current32 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[32] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d35
SS2PMM1Phase2Current33 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[33] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d36
SS2PMM1Phase2Current34 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[34] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d37
SS2PMM1Phase2Current35 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[35] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d38
SS2PMM1Phase2Current36 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[36] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d39
SS2PMM1Phase2Current37 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[37] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d3a
SS2PMM1Phase2Current38 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[38] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d3b
SS2PMM1Phase2Current39 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[39] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d3c
SS2PMM1Phase2Current3 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[3] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d3d
SS2PMM1Phase2Current40 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[40] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d3e
SS2PMM1Phase2Current41 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[41] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d3f
SS2PMM1Phase2Current42 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[42] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d40
SS2PMM1Phase2Current4 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[4] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d41
SS2PMM1Phase2Current5 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[5] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d42
SS2PMM1Phase2Current6 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[6] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d43
SS2PMM1Phase2Current7 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[7] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d44
SS2PMM1Phase2Current8 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[8] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d45
SS2PMM1Phase2Current9 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[9] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d46
SS2PMM1Phase3Current10 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[10] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d47
SS2PMM1Phase3Current11 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[11] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d48
SS2PMM1Phase3Current12 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[12] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d49
SS2PMM1Phase3Current13 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[13] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d4a
SS2PMM1Phase3Current14 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[14] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d4b
SS2PMM1Phase3Current15 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[15] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d4c
SS2PMM1Phase3Current16 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[16] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d4d
SS2PMM1Phase3Current17 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[17] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d4e
SS2PMM1Phase3Current18 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[18] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d4f
SS2PMM1Phase3Current19 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[19] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d50
SS2PMM1Phase3Current1 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[1] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d51
SS2PMM1Phase3Current20 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[20] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d52
SS2PMM1Phase3Current21 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[21] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d53
SS2PMM1Phase3Current22 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[22] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d54
SS2PMM1Phase3Current23 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[23] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d55
SS2PMM1Phase3Current24 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[24] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d56
SS2PMM1Phase3Current25 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[25] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d57
SS2PMM1Phase3Current26 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[26] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d58
SS2PMM1Phase3Current27 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[27] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d59
SS2PMM1Phase3Current28 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[28] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d5a
SS2PMM1Phase3Current29 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[29] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d5b
SS2PMM1Phase3Current2 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[2] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d5c
SS2PMM1Phase3Current30 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[30] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d5d
SS2PMM1Phase3Current31 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[31] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d5e
SS2PMM1Phase3Current32 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[32] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d5f
SS2PMM1Phase3Current33 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[33] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d60
SS2PMM1Phase3Current34 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[34] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d61
SS2PMM1Phase3Current35 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[35] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d62
SS2PMM1Phase3Current36 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[36] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d63
SS2PMM1Phase3Current37 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[37] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d64
SS2PMM1Phase3Current38 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[38] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d65
SS2PMM1Phase3Current39 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[39] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d66
SS2PMM1Phase3Current3 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[3] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d67
SS2PMM1Phase3Current40 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[40] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d68
SS2PMM1Phase3Current41 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[41] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d69
SS2PMM1Phase3Current42 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[42] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d6a
SS2PMM1Phase3Current4 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[4] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d6b
SS2PMM1Phase3Current5 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[5] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d6c
SS2PMM1Phase3Current6 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[6] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d6d
SS2PMM1Phase3Current7 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[7] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d6e
SS2PMM1Phase3Current8 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[8] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d6f
SS2PMM1Phase3Current9 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[9] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05d70
SS2PMM1PowerFactorSys | REAL | IOD_SS2 | SS2:.PMM[1].PowerFactorSys | 0 | 1 | 0 | 1 |  | ####.# | 6157 | 0 | 0x0fc05d71
SS2PMM1ReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMM[1].ReactiveEnergyConsumed_kVARh |  |  |  |  | kVArh | ####.# | 6157 | 0 | 0x0fc05d72
SS2PMM1ReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[1].ReactivePowerPhaseA | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05d73
SS2PMM1ReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[1].ReactivePowerPhaseB | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05d74
SS2PMM1ReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[1].ReactivePowerPhaseC | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05d75
SS2PMM1TotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMM[1].TotalActivePower_kW | 0 | 300 | 0 | 300 | kW | ####.# | 6157 | 0 | 0x0fc05d76
SS2PMM1TotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMM[1].TotalAparentPower_kVA | 0 | 300 | 0 | 300 | kVA | ####.# | 6157 | 0 | 0x0fc05d77
SS2PMM1TotalPowerFactor | REAL | IOD_SS2 | SS2:.PMM[1].TotalPowerFactor | 0 | 1 | 0 | 1 |  | ####.# | 6157 | 0 | 0x0fc05d78
SS2PMM1TotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMM[1].TotalReactivePower_kVAR | 0 | 300 | 0 | 300 | kVAr | ####.# | 6157 | 0 | 0x0fc05d79
SS2PMM1VirA_fsys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_fsys | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 0 | 0x0fc05d7a
SS2PMM1VirA_Isys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_Isys | 0 | 1000 | 0 | 1000 | A | ####.# | 6157 | 0 | 0x0fc05d7b
SS2PMM1VirA_PFsys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_PFsys | 0 | 1 | 0 | 0 | 1 | ####.# | 6157 | 0 | 0x0fc05d7c
SS2PMM1VirA_Psys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_Psys | 0 | 300 | 0 | 300 | kW | ####.# | 6157 | 0 | 0x0fc05d7d
SS2PMM1VirA_Qsys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_Qsys | 0 | 300 | 0 | 300 | kVAr | ####.# | 6157 | 0 | 0x0fc05d7e
SS2PMM1VirA_Ssys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_Ssys | 0 | 300 | 0 | 300 | kVA | ####.# | 6157 | 0 | 0x0fc05d7f
SS2PMM1VirA_Usys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_Usys | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05d80
SS2PMM1VirB_fsys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_fsys | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 0 | 0x0fc05d81
SS2PMM1VirB_Isys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_Isys | 0 | 1000 | 0 | 1000 | A | ####.# | 6157 | 0 | 0x0fc05d82
SS2PMM1VirB_PFsys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_PFsys | 0 | 1 | 0 | 0 | 1 | ####.# | 6157 | 0 | 0x0fc05d83
SS2PMM1VirB_Psys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_Psys | 0 | 300 | 0 | 300 | kW | ####.# | 6157 | 0 | 0x0fc05d84
SS2PMM1VirB_Qsys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_Qsys | 0 | 300 | 0 | 300 | kVAr | ####.# | 6157 | 0 | 0x0fc05d85
SS2PMM1VirB_Ssys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_Ssys | 0 | 300 | 0 | 300 | kVA | ####.# | 6157 | 0 | 0x0fc05d86
SS2PMM1VirB_Usys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_Usys | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05d87
SS2PMM1VirBActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMM[1].VirBActiveEnergyConsumed_kWh |  |  |  |  | kVArh | ####.# | 6157 | 0 | 0x0fc05d88
SS2PMM1VirBActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMM[1].VirBActivePowerPhaseA_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 0 | 0x0fc05d89
SS2PMM1VirBActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMM[1].VirBActivePowerPhaseB_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 0 | 0x0fc05d8a
SS2PMM1VirBActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMM[1].VirBActivePowerPhaseC_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 0 | 0x0fc05d8b
SS2PMM1VirBAparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[1].VirBAparentPowerPhaseA | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05d8c
SS2PMM1VirBAparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[1].VirBAparentPowerPhaseB | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05d8d
SS2PMM1VirBAparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[1].VirBAparentPowerPhaseC | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05d8e
SS2PMM1VirBAverageCurrent_A | REAL | IOD_SS2 | SS2:.PMM[1].VirBAverageCurrent_A | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 0 | 0x0fc05d8f
SS2PMM1VirBAveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBAveragePhaseToNeutral_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05d90
SS2PMM1VirBAveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBAveragePhaseToPhase_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05d91
SS2PMM1VirBCurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMM[1].VirBCurrentInPhaseA_A | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 0 | 0x0fc05d92
SS2PMM1VirBCurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMM[1].VirBCurrentInPhaseB_A | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 0 | 0x0fc05d93
SS2PMM1VirBCurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMM[1].VirBCurrentInPhaseC_A | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 0 | 0x0fc05d94
SS2PMM1VirBFrequency_Hz | REAL | IOD_SS2 | SS2:.PMM[1].VirBFrequency_Hz | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 0 | 0x0fc05d95
SS2PMM1VirBPowerFactorSys | REAL | IOD_SS2 | SS2:.PMM[1].VirBPowerFactorSys | 0 | 1 | 0 | 1 |  | ####.# | 6157 | 0 | 0x0fc05d96
SS2PMM1VirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMM[1].VirBReactiveEnergyConsumed_kVARh |  |  |  |  | kVArh | ####.# | 6157 | 0 | 0x0fc05d97
SS2PMM1VirBReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[1].VirBReactivePowerPhaseA | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05d98
SS2PMM1VirBReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[1].VirBReactivePowerPhaseB | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05d99
SS2PMM1VirBReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[1].VirBReactivePowerPhaseC | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05d9a
SS2PMM1VirBTotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMM[1].VirBTotalActivePower_kW | 0 | 300 | 0 | 300 | kW | ####.# | 6157 | 0 | 0x0fc05d9b
SS2PMM1VirBTotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMM[1].VirBTotalAparentPower_kVA | 0 | 300 | 0 | 300 | kVA | ####.# | 6157 | 0 | 0x0fc05d9c
SS2PMM1VirBTotalPowerFactor | REAL | IOD_SS2 | SS2:.PMM[1].VirBTotalPowerFactor | 0 | 1 | 0 | 1 |  | ####.# | 6157 | 0 | 0x0fc05d9d
SS2PMM1VirBTotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMM[1].VirBTotalReactivePower_kVAR | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05d9e
SS2PMM1VirBVoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseAB_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05d9f
SS2PMM1VirBVoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseAN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05da0
SS2PMM1VirBVoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseBC_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05da1
SS2PMM1VirBVoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseBN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05da2
SS2PMM1VirBVoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseCA_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05da3
SS2PMM1VirBVoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseCN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05da4
SS2PMM1VoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseAB_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05da5
SS2PMM1VoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseAN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05da6
SS2PMM1VoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseBC_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05da7
SS2PMM1VoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseBN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05da8
SS2PMM1VoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseCA_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05da9
SS2PMM1VoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseCN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05daa
SS2PMM2ActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMM[2].ActiveEnergyConsumed_kWh |  |  |  |  | kVAr | ####.# | 6157 | 0 | 0x0fc05dab
SS2PMM2ActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMM[2].ActivePowerPhaseA_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 0 | 0x0fc05dac
SS2PMM2ActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMM[2].ActivePowerPhaseB_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 0 | 0x0fc05dad
SS2PMM2ActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMM[2].ActivePowerPhaseC_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 0 | 0x0fc05dae
SS2PMM2AlarmPhase1C01_16_60to80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C01_16_60to80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05daf
SS2PMM2AlarmPhase1C01_16_over80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C01_16_over80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05db0
SS2PMM2AlarmPhase1C17_32_60to80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C17_32_60to80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05db1
SS2PMM2AlarmPhase1C17_32_over80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C17_32_over80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05db2
SS2PMM2AlarmPhase1C33_42_60to80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C33_42_60to80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05db3
SS2PMM2AlarmPhase1C33_42_over80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C33_42_over80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05db4
SS2PMM2AlarmPhase1GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].GlobalAlarmReg | [5 empty] | ####.# | 6157 | 0 | 0x0fc05db5
SS2PMM2AlarmPhase2C01_16_60to80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C01_16_60to80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05db6
SS2PMM2AlarmPhase2C01_16_over80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C01_16_over80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05db7
SS2PMM2AlarmPhase2C17_32_60to80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C17_32_60to80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05db8
SS2PMM2AlarmPhase2C17_32_over80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C17_32_over80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05db9
SS2PMM2AlarmPhase2C33_42_60to80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C33_42_60to80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05dba
SS2PMM2AlarmPhase2C33_42_over80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C33_42_over80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05dbb
SS2PMM2AlarmPhase2GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].GlobalAlarmReg | [5 empty] | ####.# | 6157 | 0 | 0x0fc05dbc
SS2PMM2AlarmPhase3C01_16_60to80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C01_16_60to80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05dbd
SS2PMM2AlarmPhase3C01_16_over80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C01_16_over80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05dbe
SS2PMM2AlarmPhase3C17_32_60to80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C17_32_60to80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05dbf
SS2PMM2AlarmPhase3C17_32_over80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C17_32_over80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05dc0
SS2PMM2AlarmPhase3C33_42_60to80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C33_42_60to80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05dc1
SS2PMM2AlarmPhase3C33_42_over80 | BYTE | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C33_42_over80 | [5 empty] | ####.# | 6157 | 0 | 0x0fc05dc2
SS2PMM2AlarmPhase3GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].GlobalAlarmReg | [5 empty] | ####.# | 6157 | 0 | 0x0fc05dc3
SS2PMM2AparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[2].AparentPowerPhaseA | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05dc4
SS2PMM2AparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[2].AparentPowerPhaseB | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05dc5
SS2PMM2AparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[2].AparentPowerPhaseC | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05dc6
SS2PMM2AverageCurrent_A | REAL | IOD_SS2 | SS2:.PMM[2].AverageCurrent_A | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05dc7
SS2PMM2AveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMM[2].AveragePhaseToNeutral_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05dc8
SS2PMM2AveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMM[2].AveragePhaseToPhase_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05dc9
SS2PMM2CurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMM[2].CurrentInPhaseA_A | 0 | 500 | 0 | 500 | A | ####.# | 6157 | 0 | 0x0fc05dca
SS2PMM2CurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMM[2].CurrentInPhaseB_A | 0 | 500 | 0 | 500 | A | ####.# | 6157 | 0 | 0x0fc05dcb
SS2PMM2CurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMM[2].CurrentInPhaseC_A | 0 | 500 | 0 | 500 | A | ####.# | 6157 | 0 | 0x0fc05dcc
SS2PMM2Frequency_Hz | REAL | IOD_SS2 | SS2:.PMM[2].Frequency_Hz | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 0 | 0x0fc05dcd
SS2PMM2Phase1Current1 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[1] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05dce
SS2PMM2Phase1Current2 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[2] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05dcf
SS2PMM2Phase1Current3 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[3] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05dd0
SS2PMM2Phase1Current4 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[4] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05dd1
SS2PMM2Phase1Current5 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[5] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05dd2
SS2PMM2Phase1Current6 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[6] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05dd3
SS2PMM2Phase1Current7 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[7] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05dd4
SS2PMM2Phase1Current8 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[8] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05dd5
SS2PMM2Phase1Current9 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[9] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05dd6
SS2PMM2Phase1Current10 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[10] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05dd7
SS2PMM2Phase1Current11 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[11] | 0 | 50 | 0 | 50 | A | ####.# | 6157 | 0 | 0x0fc05dd8
SS2PMM2Phase1Current12 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[12] | 0 | 50 | 0 | 50 | A | ####.# | 6157 | 0 | 0x0fc05dd9
SS2PMM2Phase1Current13 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[13] | 0 | 50 | 0 | 50 | A | ####.# | 6157 | 0 | 0x0fc05dda
SS2PMM2Phase1Current14 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[14] | 0 | 50 | 0 | 50 | A | ####.# | 6157 | 0 | 0x0fc05ddb
SS2PMM2Phase1Current15 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[15] | 0 | 50 | 0 | 50 | A | ####.# | 6157 | 0 | 0x0fc05ddc
SS2PMM2Phase1Current16 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[16] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05ddd
SS2PMM2Phase1Current17 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[17] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05dde
SS2PMM2Phase1Current18 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[18] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05ddf
SS2PMM2Phase1Current19 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[19] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05de0
SS2PMM2Phase1Current20 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[20] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05de1
SS2PMM2Phase1Current21 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[21] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05de2
SS2PMM2Phase1Current22 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[22] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05de3
SS2PMM2Phase1Current23 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[23] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05de4
SS2PMM2Phase1Current24 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[24] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05de5
SS2PMM2Phase1Current25 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[25] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05de6
SS2PMM2Phase1Current26 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[26] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05de7
SS2PMM2Phase1Current27 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[27] | 0 | 16 | 0 | 16 | A | ####.# | 6157 | 0 | 0x0fc05de8
SS2PMM2Phase1Current28 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[28] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05de9
SS2PMM2Phase1Current29 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[29] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05dea
SS2PMM2Phase1Current30 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[30] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05deb
SS2PMM2Phase1Current31 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[31] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05dec
SS2PMM2Phase1Current32 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[32] | 0 | 50 | 0 | 50 | A | ####.# | 6157 | 0 | 0x0fc05ded
SS2PMM2Phase1Current33 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[33] | 0 | 50 | 0 | 50 | A | ####.# | 6157 | 0 | 0x0fc05dee
SS2PMM2Phase1Current34 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[34] | 0 | 50 | 0 | 50 | A | ####.# | 6157 | 0 | 0x0fc05def
SS2PMM2Phase1Current35 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[35] | 0 | 50 | 0 | 50 | A | ####.# | 6157 | 0 | 0x0fc05df0
SS2PMM2Phase1Current36 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[36] | 0 | 50 | 0 | 50 | A | ####.# | 6157 | 0 | 0x0fc05df1
SS2PMM2Phase1Current37 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[37] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05df2
SS2PMM2Phase1Current38 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[38] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05df3
SS2PMM2Phase1Current39 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[39] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05df4
SS2PMM2Phase1Current40 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[40] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05df5
SS2PMM2Phase1Current41 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[41] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05df6
SS2PMM2Phase1Current42 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[42] | 0 | 32 | 0 | 32 | A | ####.# | 6157 | 0 | 0x0fc05df7
SS2PMM2Phase2Current10 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[10] | [6 empty] | 6157 | 0 | 0x0fc05df8
SS2PMM2Phase2Current11 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[11] | [6 empty] | 6157 | 0 | 0x0fc05df9
SS2PMM2Phase2Current12 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[12] | [6 empty] | 6157 | 0 | 0x0fc05dfa
SS2PMM2Phase2Current13 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[13] | [6 empty] | 6157 | 0 | 0x0fc05dfb
SS2PMM2Phase2Current14 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[14] | [6 empty] | 6157 | 0 | 0x0fc05dfc
SS2PMM2Phase2Current15 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[15] | [6 empty] | 6157 | 0 | 0x0fc05dfd
SS2PMM2Phase2Current16 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[16] | [6 empty] | 6157 | 0 | 0x0fc05dfe
SS2PMM2Phase2Current17 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[17] | [6 empty] | 6157 | 0 | 0x0fc05dff
SS2PMM2Phase2Current18 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[18] | [6 empty] | 6157 | 0 | 0x0fc05e00
SS2PMM2Phase2Current19 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[19] | [6 empty] | 6157 | 0 | 0x0fc05e01
SS2PMM2Phase2Current1 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[1] | [6 empty] | 6157 | 0 | 0x0fc05e02
SS2PMM2Phase2Current20 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[20] | [6 empty] | 6157 | 0 | 0x0fc05e03
SS2PMM2Phase2Current21 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[21] | [6 empty] | 6157 | 0 | 0x0fc05e04
SS2PMM2Phase2Current22 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[22] | [6 empty] | 6157 | 0 | 0x0fc05e05
SS2PMM2Phase2Current23 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[23] | [6 empty] | 6157 | 0 | 0x0fc05e06
SS2PMM2Phase2Current24 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[24] | [6 empty] | 6157 | 0 | 0x0fc05e07
SS2PMM2Phase2Current25 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[25] | [6 empty] | 6157 | 0 | 0x0fc05e08
SS2PMM2Phase2Current26 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[26] | [6 empty] | 6157 | 0 | 0x0fc05e09
SS2PMM2Phase2Current27 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[27] | [6 empty] | 6157 | 0 | 0x0fc05e0a
SS2PMM2Phase2Current28 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[28] | [6 empty] | 6157 | 0 | 0x0fc05e0b
SS2PMM2Phase2Current29 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[29] | [6 empty] | 6157 | 0 | 0x0fc05e0c
SS2PMM2Phase2Current2 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[2] | [6 empty] | 6157 | 0 | 0x0fc05e0d
SS2PMM2Phase2Current30 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[30] | [6 empty] | 6157 | 0 | 0x0fc05e0e
SS2PMM2Phase2Current31 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[31] | [6 empty] | 6157 | 0 | 0x0fc05e0f
SS2PMM2Phase2Current32 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[32] | [6 empty] | 6157 | 0 | 0x0fc05e10
SS2PMM2Phase2Current33 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[33] | [6 empty] | 6157 | 0 | 0x0fc05e11
SS2PMM2Phase2Current34 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[34] | [6 empty] | 6157 | 0 | 0x0fc05e12
SS2PMM2Phase2Current35 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[35] | [6 empty] | 6157 | 0 | 0x0fc05e13
SS2PMM2Phase2Current36 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[36] | [6 empty] | 6157 | 0 | 0x0fc05e14
SS2PMM2Phase2Current37 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[37] | [6 empty] | 6157 | 0 | 0x0fc05e15
SS2PMM2Phase2Current38 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[38] | [6 empty] | 6157 | 0 | 0x0fc05e16
SS2PMM2Phase2Current39 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[39] | [6 empty] | 6157 | 0 | 0x0fc05e17
SS2PMM2Phase2Current3 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[3] | [6 empty] | 6157 | 0 | 0x0fc05e18
SS2PMM2Phase2Current40 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[40] | [6 empty] | 6157 | 0 | 0x0fc05e19
SS2PMM2Phase2Current41 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[41] | [6 empty] | 6157 | 0 | 0x0fc05e1a
SS2PMM2Phase2Current42 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[42] | [6 empty] | 6157 | 0 | 0x0fc05e1b
SS2PMM2Phase2Current4 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[4] | [6 empty] | 6157 | 0 | 0x0fc05e1c
SS2PMM2Phase2Current5 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[5] | [6 empty] | 6157 | 0 | 0x0fc05e1d
SS2PMM2Phase2Current6 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[6] | [6 empty] | 6157 | 0 | 0x0fc05e1e
SS2PMM2Phase2Current7 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[7] | [6 empty] | 6157 | 0 | 0x0fc05e1f
SS2PMM2Phase2Current8 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[8] | [6 empty] | 6157 | 0 | 0x0fc05e20
SS2PMM2Phase2Current9 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[9] | [6 empty] | 6157 | 0 | 0x0fc05e21
SS2PMM2Phase3Current10 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[10] | [6 empty] | 6157 | 0 | 0x0fc05e22
SS2PMM2Phase3Current11 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[11] | [6 empty] | 6157 | 0 | 0x0fc05e23
SS2PMM2Phase3Current12 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[12] | [6 empty] | 6157 | 0 | 0x0fc05e24
SS2PMM2Phase3Current13 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[13] | [6 empty] | 6157 | 0 | 0x0fc05e25
SS2PMM2Phase3Current14 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[14] | [6 empty] | 6157 | 0 | 0x0fc05e26
SS2PMM2Phase3Current15 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[15] | [6 empty] | 6157 | 0 | 0x0fc05e27
SS2PMM2Phase3Current16 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[16] | [6 empty] | 6157 | 0 | 0x0fc05e28
SS2PMM2Phase3Current17 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[17] | [6 empty] | 6157 | 0 | 0x0fc05e29
SS2PMM2Phase3Current18 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[18] | [6 empty] | 6157 | 0 | 0x0fc05e2a
SS2PMM2Phase3Current19 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[19] | [6 empty] | 6157 | 0 | 0x0fc05e2b
SS2PMM2Phase3Current1 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[1] | [6 empty] | 6157 | 0 | 0x0fc05e2c
SS2PMM2Phase3Current20 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[20] | [6 empty] | 6157 | 0 | 0x0fc05e2d
SS2PMM2Phase3Current21 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[21] | [6 empty] | 6157 | 0 | 0x0fc05e2e
SS2PMM2Phase3Current22 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[22] | [6 empty] | 6157 | 0 | 0x0fc05e2f
SS2PMM2Phase3Current23 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[23] | [6 empty] | 6157 | 0 | 0x0fc05e30
SS2PMM2Phase3Current24 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[24] | [6 empty] | 6157 | 0 | 0x0fc05e31
SS2PMM2Phase3Current25 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[25] | [6 empty] | 6157 | 0 | 0x0fc05e32
SS2PMM2Phase3Current26 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[26] | [6 empty] | 6157 | 0 | 0x0fc05e33
SS2PMM2Phase3Current27 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[27] | [6 empty] | 6157 | 0 | 0x0fc05e34
SS2PMM2Phase3Current28 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[28] | [6 empty] | 6157 | 0 | 0x0fc05e35
SS2PMM2Phase3Current29 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[29] | [6 empty] | 6157 | 0 | 0x0fc05e36
SS2PMM2Phase3Current2 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[2] | [6 empty] | 6157 | 0 | 0x0fc05e37
SS2PMM2Phase3Current30 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[30] | [6 empty] | 6157 | 0 | 0x0fc05e38
SS2PMM2Phase3Current31 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[31] | [6 empty] | 6157 | 0 | 0x0fc05e39
SS2PMM2Phase3Current32 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[32] | [6 empty] | 6157 | 0 | 0x0fc05e3a
SS2PMM2Phase3Current33 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[33] | [6 empty] | 6157 | 0 | 0x0fc05e3b
SS2PMM2Phase3Current34 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[34] | [6 empty] | 6157 | 0 | 0x0fc05e3c
SS2PMM2Phase3Current35 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[35] | [6 empty] | 6157 | 0 | 0x0fc05e3d
SS2PMM2Phase3Current36 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[36] | [6 empty] | 6157 | 0 | 0x0fc05e3e
SS2PMM2Phase3Current37 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[37] | [6 empty] | 6157 | 0 | 0x0fc05e3f
SS2PMM2Phase3Current38 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[38] | [6 empty] | 6157 | 0 | 0x0fc05e40
SS2PMM2Phase3Current39 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[39] | [6 empty] | 6157 | 0 | 0x0fc05e41
SS2PMM2Phase3Current3 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[3] | [6 empty] | 6157 | 0 | 0x0fc05e42
SS2PMM2Phase3Current40 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[40] | [6 empty] | 6157 | 0 | 0x0fc05e43
SS2PMM2Phase3Current41 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[41] | [6 empty] | 6157 | 0 | 0x0fc05e44
SS2PMM2Phase3Current42 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[42] | [6 empty] | 6157 | 0 | 0x0fc05e45
SS2PMM2Phase3Current4 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[4] | [6 empty] | 6157 | 0 | 0x0fc05e46
SS2PMM2Phase3Current5 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[5] | [6 empty] | 6157 | 0 | 0x0fc05e47
SS2PMM2Phase3Current6 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[6] | [6 empty] | 6157 | 0 | 0x0fc05e48
SS2PMM2Phase3Current7 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[7] | [6 empty] | 6157 | 0 | 0x0fc05e49
SS2PMM2Phase3Current8 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[8] | [6 empty] | 6157 | 0 | 0x0fc05e4a
SS2PMM2Phase3Current9 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[9] | [6 empty] | 6157 | 0 | 0x0fc05e4b
SS2PMM2PowerFactorSys | REAL | IOD_SS2 | SS2:.PMM[2].PowerFactorSys | 0 | 1 | 0 | 1 |  | ####.# | 6157 | 0 | 0x0fc05e4c
SS2PMM2ReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMM[2].ReactiveEnergyConsumed_kVARh |  |  |  |  | kVArh | ### | 6157 | 0 | 0x0fc05e4d
SS2PMM2ReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[2].ReactivePowerPhaseA | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05e4e
SS2PMM2ReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[2].ReactivePowerPhaseB | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05e4f
SS2PMM2ReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[2].ReactivePowerPhaseC | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05e50
SS2PMM2TotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMM[2].TotalActivePower_kW | 0 | 300 | 0 | 300 | kW | ####.# | 6157 | 0 | 0x0fc05e51
SS2PMM2TotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMM[2].TotalAparentPower_kVA | 0 | 300 | 0 | 300 | kVA | ####.# | 6157 | 0 | 0x0fc05e52
SS2PMM2TotalPowerFactor | REAL | IOD_SS2 | SS2:.PMM[2].TotalPowerFactor | 0 | 1 | 0 | 1 |  | ####.# | 6157 | 0 | 0x0fc05e53
SS2PMM2TotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMM[2].TotalReactivePower_kVAR | 0 | 300 | 0 | 300 | kVAr | ####.# | 6157 | 0 | 0x0fc05e54
SS2PMM2VirA_fsys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_fsys | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 0 | 0x0fc05e55
SS2PMM2VirA_Isys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_Isys | 0 | 1000 | 0 | 1000 | A | ####.# | 6157 | 0 | 0x0fc05e56
SS2PMM2VirA_PFsys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_PFsys | 0 | 1 | 0 | 1 |  | ####.# | 6157 | 0 | 0x0fc05e57
SS2PMM2VirA_Psys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_Psys | 0 | 300 | 0 | 300 | kW | ####.# | 6157 | 0 | 0x0fc05e58
SS2PMM2VirA_Qsys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_Qsys | 0 | 300 | 0 | 300 | kVAr | ####.# | 6157 | 0 | 0x0fc05e59
SS2PMM2VirA_Ssys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_Ssys | 0 | 300 | 0 | 300 | kVA | ####.# | 6157 | 0 | 0x0fc05e5a
SS2PMM2VirA_Usys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_Usys | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05e5b
SS2PMM2VirB_fsys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_fsys | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 0 | 0x0fc05e5c
SS2PMM2VirB_Isys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_Isys | 0 | 1000 | 0 | 1000 | A | ####.# | 6157 | 0 | 0x0fc05e5d
SS2PMM2VirB_PFsys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_PFsys | 0 | 1 | 0 | 1 |  | ####.# | 6157 | 0 | 0x0fc05e5e
SS2PMM2VirB_Psys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_Psys | 0 | 300 | 0 | 300 | kW | ####.# | 6157 | 0 | 0x0fc05e5f
SS2PMM2VirB_Qsys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_Qsys | 0 | 300 | 0 | 300 | kVAr | ####.# | 6157 | 0 | 0x0fc05e60
SS2PMM2VirB_Ssys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_Ssys | 0 | 300 | 0 | 300 | kVA | ####.# | 6157 | 0 | 0x0fc05e61
SS2PMM2VirB_Usys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_Usys | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05e62
SS2PMM2VirBActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMM[2].VirBActiveEnergyConsumed_kWh |  |  |  |  | kVArh | ####.# | 6157 | 0 | 0x0fc05e63
SS2PMM2VirBActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMM[2].VirBActivePowerPhaseA_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 0 | 0x0fc05e64
SS2PMM2VirBActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMM[2].VirBActivePowerPhaseB_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 0 | 0x0fc05e65
SS2PMM2VirBActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMM[2].VirBActivePowerPhaseC_kW | 0 | 100 | 0 | 100 | kW | ####.# | 6157 | 0 | 0x0fc05e66
SS2PMM2VirBAparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[2].VirBAparentPowerPhaseA | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05e67
SS2PMM2VirBAparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[2].VirBAparentPowerPhaseB | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05e68
SS2PMM2VirBAparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[2].VirBAparentPowerPhaseC | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05e69
SS2PMM2VirBAverageCurrent_A | REAL | IOD_SS2 | SS2:.PMM[2].VirBAverageCurrent_A | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 0 | 0x0fc05e6a
SS2PMM2VirBAveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBAveragePhaseToNeutral_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05e6b
SS2PMM2VirBAveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBAveragePhaseToPhase_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05e6c
SS2PMM2VirBCurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMM[2].VirBCurrentInPhaseA_A | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 0 | 0x0fc05e6d
SS2PMM2VirBCurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMM[2].VirBCurrentInPhaseB_A | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 0 | 0x0fc05e6e
SS2PMM2VirBCurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMM[2].VirBCurrentInPhaseC_A | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 0 | 0x0fc05e6f
SS2PMM2VirBFrequency_Hz | REAL | IOD_SS2 | SS2:.PMM[2].VirBFrequency_Hz | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 0 | 0x0fc05e70
SS2PMM2VirBPowerFactorSys | REAL | IOD_SS2 | SS2:.PMM[2].VirBPowerFactorSys | 0 | 1 | 0 | 1 |  | ####.# | 6157 | 0 | 0x0fc05e71
SS2PMM2VirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMM[2].VirBReactiveEnergyConsumed_kVARh |  |  |  |  | kVArh | ####.# | 6157 | 0 | 0x0fc05e72
SS2PMM2VirBReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[2].VirBReactivePowerPhaseA | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05e73
SS2PMM2VirBReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[2].VirBReactivePowerPhaseB | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05e74
SS2PMM2VirBReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[2].VirBReactivePowerPhaseC | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05e75
SS2PMM2VirBTotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMM[2].VirBTotalActivePower_kW | 0 | 300 | 0 | 300 | kW | ####.# | 6157 | 0 | 0x0fc05e76
SS2PMM2VirBTotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMM[2].VirBTotalAparentPower_kVA | 0 | 300 | 0 | 300 | kVA | ####.# | 6157 | 0 | 0x0fc05e77
SS2PMM2VirBTotalPowerFactor | REAL | IOD_SS2 | SS2:.PMM[2].VirBTotalPowerFactor | 0 | 1 | 0 | 1 |  | ####.# | 6157 | 0 | 0x0fc05e78
SS2PMM2VirBTotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMM[2].VirBTotalReactivePower_kVAR | 0 | 100 | 0 | 100 | kVAr | ####.# | 6157 | 0 | 0x0fc05e79
SS2PMM2VirBVoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseAB_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05e7a
SS2PMM2VirBVoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseAN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05e7b
SS2PMM2VirBVoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseBC_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05e7c
SS2PMM2VirBVoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseBN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05e7d
SS2PMM2VirBVoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseCA_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05e7e
SS2PMM2VirBVoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseCN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05e7f
SS2PMM2VoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseAB_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05e80
SS2PMM2VoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseAN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05e81
SS2PMM2VoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseBC_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05e82
SS2PMM2VoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseBN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05e83
SS2PMM2VoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseCA_V | 0 | 450 | 0 | 450 | V | ####.# | 6157 | 0 | 0x0fc05e84
SS2PMM2VoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseCN_V | 0 | 270 | 0 | 270 | V | ####.# | 6157 | 0 | 0x0fc05e85
SS2PMMPanelActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMMPanel.ActiveEnergyConsumed_kWh | [6 empty] | 6157 | 0 | 0x0fc05e86
SS2PMMPanelActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMMPanel.ActivePowerPhaseA_kW | [6 empty] | 6157 | 0 | 0x0fc05e87
SS2PMMPanelActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMMPanel.ActivePowerPhaseB_kW | [6 empty] | 6157 | 0 | 0x0fc05e88
SS2PMMPanelActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMMPanel.ActivePowerPhaseC_kW | [6 empty] | 6157 | 0 | 0x0fc05e89
SS2PMMPanelAlarmPhase1C01_16_60to80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C01_16_60to80 | [6 empty] | 6157 | 0 | 0x0fc05e8a
SS2PMMPanelAlarmPhase1C01_16_over80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C01_16_over80 | [6 empty] | 6157 | 0 | 0x0fc05e8b
SS2PMMPanelAlarmPhase1C17_32_60to80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C17_32_60to80 | [6 empty] | 6157 | 0 | 0x0fc05e8c
SS2PMMPanelAlarmPhase1C17_32_over80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C17_32_over80 | [6 empty] | 6157 | 0 | 0x0fc05e8d
SS2PMMPanelAlarmPhase1C33_42_60to80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C33_42_60to80 | [6 empty] | 6157 | 0 | 0x0fc05e8e
SS2PMMPanelAlarmPhase1C33_42_over80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C33_42_over80 | [6 empty] | 6157 | 0 | 0x0fc05e8f
SS2PMMPanelAlarmPhase1GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].GlobalAlarmReg | [6 empty] | 6157 | 0 | 0x0fc05e90
SS2PMMPanelAlarmPhase2C01_16_60to80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C01_16_60to80 | [6 empty] | 6157 | 0 | 0x0fc05e91
SS2PMMPanelAlarmPhase2C01_16_over80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C01_16_over80 | [6 empty] | 6157 | 0 | 0x0fc05e92
SS2PMMPanelAlarmPhase2C17_32_60to80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C17_32_60to80 | [6 empty] | 6157 | 0 | 0x0fc05e93
SS2PMMPanelAlarmPhase2C17_32_over80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C17_32_over80 | [6 empty] | 6157 | 0 | 0x0fc05e94
SS2PMMPanelAlarmPhase2C33_42_60to80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C33_42_60to80 | [6 empty] | 6157 | 0 | 0x0fc05e95
SS2PMMPanelAlarmPhase2C33_42_over80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C33_42_over80 | [6 empty] | 6157 | 0 | 0x0fc05e96
SS2PMMPanelAlarmPhase2GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].GlobalAlarmReg | [6 empty] | 6157 | 0 | 0x0fc05e97
SS2PMMPanelAlarmPhase3C01_16_60to80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C01_16_60to80 | [6 empty] | 6157 | 0 | 0x0fc05e98
SS2PMMPanelAlarmPhase3C01_16_over80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C01_16_over80 | [6 empty] | 6157 | 0 | 0x0fc05e99
SS2PMMPanelAlarmPhase3C17_32_60to80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C17_32_60to80 | [6 empty] | 6157 | 0 | 0x0fc05e9a
SS2PMMPanelAlarmPhase3C17_32_over80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C17_32_over80 | [6 empty] | 6157 | 0 | 0x0fc05e9b
SS2PMMPanelAlarmPhase3C33_42_60to80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C33_42_60to80 | [6 empty] | 6157 | 0 | 0x0fc05e9c
SS2PMMPanelAlarmPhase3C33_42_over80 | BYTE | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C33_42_over80 | [6 empty] | 6157 | 0 | 0x0fc05e9d
SS2PMMPanelAlarmPhase3GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].GlobalAlarmReg | [6 empty] | 6157 | 0 | 0x0fc05e9e
SS2PMMPanelAparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMMPanel.AparentPowerPhaseA | [6 empty] | 6157 | 0 | 0x0fc05e9f
SS2PMMPanelAparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMMPanel.AparentPowerPhaseB | [6 empty] | 6157 | 0 | 0x0fc05ea0
SS2PMMPanelAparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMMPanel.AparentPowerPhaseC | [6 empty] | 6157 | 0 | 0x0fc05ea1
SS2PMMPanelAverageCurrent_A | REAL | IOD_SS2 | SS2:.PMMPanel.AverageCurrent_A | [6 empty] | 6157 | 0 | 0x0fc05ea2
SS2PMMPanelAveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMMPanel.AveragePhaseToNeutral_V | [6 empty] | 6157 | 0 | 0x0fc05ea3
SS2PMMPanelAveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMMPanel.AveragePhaseToPhase_V | [6 empty] | 6157 | 0 | 0x0fc05ea4
SS2PMMPanelCurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMMPanel.CurrentInPhaseA_A | [6 empty] | 6157 | 0 | 0x0fc05ea5
SS2PMMPanelCurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMMPanel.CurrentInPhaseB_A | [6 empty] | 6157 | 0 | 0x0fc05ea6
SS2PMMPanelCurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMMPanel.CurrentInPhaseC_A | [6 empty] | 6157 | 0 | 0x0fc05ea7
SS2PMMPanelFrequency_Hz | REAL | IOD_SS2 | SS2:.PMMPanel.Frequency_Hz | [6 empty] | 6157 | 0 | 0x0fc05ea8
SS2PMMPanelPowerFactorSys | REAL | IOD_SS2 | SS2:.PMMPanel.PowerFactorSys | [6 empty] | 6157 | 0 | 0x0fc05ea9
SS2PMMPanelReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMMPanel.ReactiveEnergyConsumed_kVARh | [6 empty] | 6157 | 0 | 0x0fc05eaa
SS2PMMPanelReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMMPanel.ReactivePowerPhaseA | [6 empty] | 6157 | 0 | 0x0fc05eab
SS2PMMPanelReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMMPanel.ReactivePowerPhaseB | [6 empty] | 6157 | 0 | 0x0fc05eac
SS2PMMPanelReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMMPanel.ReactivePowerPhaseC | [6 empty] | 6157 | 0 | 0x0fc05ead
SS2PMMPanelTotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMMPanel.TotalActivePower_kW | [6 empty] | 6157 | 0 | 0x0fc05eae
SS2PMMPanelTotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMMPanel.TotalAparentPower_kVA | [6 empty] | 6157 | 0 | 0x0fc05eaf
SS2PMMPanelTotalPowerFactor | REAL | IOD_SS2 | SS2:.PMMPanel.TotalPowerFactor | [6 empty] | 6157 | 0 | 0x0fc05eb0
SS2PMMPanelTotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMMPanel.TotalReactivePower_kVAR | [6 empty] | 6157 | 0 | 0x0fc05eb1
SS2PMMPanelVirA_fsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_fsys | [6 empty] | 6157 | 0 | 0x0fc05eb2
SS2PMMPanelVirA_Isys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_Isys | [6 empty] | 6157 | 0 | 0x0fc05eb3
SS2PMMPanelVirA_PFsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_PFsys | [6 empty] | 6157 | 0 | 0x0fc05eb4
SS2PMMPanelVirA_Psys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_Psys | [6 empty] | 6157 | 0 | 0x0fc05eb5
SS2PMMPanelVirA_Qsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_Qsys | [6 empty] | 6157 | 0 | 0x0fc05eb6
SS2PMMPanelVirA_Ssys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_Ssys | [6 empty] | 6157 | 0 | 0x0fc05eb7
SS2PMMPanelVirA_Usys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_Usys | [6 empty] | 6157 | 0 | 0x0fc05eb8
SS2PMMPanelVirB_fsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_fsys | [6 empty] | 6157 | 0 | 0x0fc05eb9
SS2PMMPanelVirB_Isys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_Isys | [6 empty] | 6157 | 0 | 0x0fc05eba
SS2PMMPanelVirB_PFsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_PFsys | [6 empty] | 6157 | 0 | 0x0fc05ebb
SS2PMMPanelVirB_Psys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_Psys | [6 empty] | 6157 | 0 | 0x0fc05ebc
SS2PMMPanelVirB_Qsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_Qsys | [6 empty] | 6157 | 0 | 0x0fc05ebd
SS2PMMPanelVirB_Ssys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_Ssys | [6 empty] | 6157 | 0 | 0x0fc05ebe
SS2PMMPanelVirB_Usys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_Usys | [6 empty] | 6157 | 0 | 0x0fc05ebf
SS2PMMPanelVirBActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMMPanel.VirBActiveEnergyConsumed_kWh | [6 empty] | 6157 | 0 | 0x0fc05ec0
SS2PMMPanelVirBActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMMPanel.VirBActivePowerPhaseA_kW | [6 empty] | 6157 | 0 | 0x0fc05ec1
SS2PMMPanelVirBActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMMPanel.VirBActivePowerPhaseB_kW | [6 empty] | 6157 | 0 | 0x0fc05ec2
SS2PMMPanelVirBActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMMPanel.VirBActivePowerPhaseC_kW | [6 empty] | 6157 | 0 | 0x0fc05ec3
SS2PMMPanelVirBAparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAparentPowerPhaseA | [6 empty] | 6157 | 0 | 0x0fc05ec4
SS2PMMPanelVirBAparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAparentPowerPhaseB | [6 empty] | 6157 | 0 | 0x0fc05ec5
SS2PMMPanelVirBAparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAparentPowerPhaseC | [6 empty] | 6157 | 0 | 0x0fc05ec6
SS2PMMPanelVirBAverageCurrent_A | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAverageCurrent_A | [6 empty] | 6157 | 0 | 0x0fc05ec7
SS2PMMPanelVirBAveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAveragePhaseToNeutral_V | [6 empty] | 6157 | 0 | 0x0fc05ec8
SS2PMMPanelVirBAveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAveragePhaseToPhase_V | [6 empty] | 6157 | 0 | 0x0fc05ec9
SS2PMMPanelVirBCurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMMPanel.VirBCurrentInPhaseA_A | [6 empty] | 6157 | 0 | 0x0fc05eca
SS2PMMPanelVirBCurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMMPanel.VirBCurrentInPhaseB_A | [6 empty] | 6157 | 0 | 0x0fc05ecb
SS2PMMPanelVirBCurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMMPanel.VirBCurrentInPhaseC_A | [6 empty] | 6157 | 0 | 0x0fc05ecc
SS2PMMPanelVirBFrequency_Hz | REAL | IOD_SS2 | SS2:.PMMPanel.VirBFrequency_Hz | [6 empty] | 6157 | 0 | 0x0fc05ecd
SS2PMMPanelVirBPowerFactorSys | REAL | IOD_SS2 | SS2:.PMMPanel.VirBPowerFactorSys | [6 empty] | 6157 | 0 | 0x0fc05ece
SS2PMMPanelVirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMMPanel.VirBReactiveEnergyConsumed_kVARh | [6 empty] | 6157 | 0 | 0x0fc05ecf
SS2PMMPanelVirBReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMMPanel.VirBReactivePowerPhaseA | [6 empty] | 6157 | 0 | 0x0fc05ed0
SS2PMMPanelVirBReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMMPanel.VirBReactivePowerPhaseB | [6 empty] | 6157 | 0 | 0x0fc05ed1
SS2PMMPanelVirBReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMMPanel.VirBReactivePowerPhaseC | [6 empty] | 6157 | 0 | 0x0fc05ed2
SS2PMMPanelVirBTotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMMPanel.VirBTotalActivePower_kW | [6 empty] | 6157 | 0 | 0x0fc05ed3
SS2PMMPanelVirBTotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMMPanel.VirBTotalAparentPower_kVA | [6 empty] | 6157 | 0 | 0x0fc05ed4
SS2PMMPanelVirBTotalPowerFactor | REAL | IOD_SS2 | SS2:.PMMPanel.VirBTotalPowerFactor | [6 empty] | 6157 | 0 | 0x0fc05ed5
SS2PMMPanelVirBTotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMMPanel.VirBTotalReactivePower_kVAR | [6 empty] | 6157 | 0 | 0x0fc05ed6
SS2PMMPanelVirBVoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseAB_V | [6 empty] | 6157 | 0 | 0x0fc05ed7
SS2PMMPanelVirBVoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseAN_V | [6 empty] | 6157 | 0 | 0x0fc05ed8
SS2PMMPanelVirBVoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseBC_V | [6 empty] | 6157 | 0 | 0x0fc05ed9
SS2PMMPanelVirBVoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseBN_V | [6 empty] | 6157 | 0 | 0x0fc05eda
SS2PMMPanelVirBVoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseCA_V | [6 empty] | 6157 | 0 | 0x0fc05edb
SS2PMMPanelVirBVoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseCN_V | [6 empty] | 6157 | 0 | 0x0fc05edc
SS2PMMPanelVoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseAB_V | [6 empty] | 6157 | 0 | 0x0fc05edd
SS2PMMPanelVoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseAN_V | [6 empty] | 6157 | 0 | 0x0fc05ede
SS2PMMPanelVoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseBC_V | [6 empty] | 6157 | 0 | 0x0fc05edf
SS2PMMPanelVoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseBN_V | [6 empty] | 6157 | 0 | 0x0fc05ee0
SS2PMMPanelVoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseCA_V | [6 empty] | 6157 | 0 | 0x0fc05ee1
SS2PMMPanelVoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseCN_V | [6 empty] | 6157 | 0 | 0x0fc05ee2
SS2RocniVklopKlima1 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima1 | [6 empty] | 6157 | 0 | 0x0fc05ef0
SS2RocniVklopKlima2 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima2 | [6 empty] | 6157 | 0 | 0x0fc05f00
SS2RocniVklopKlima3 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima3 | [6 empty] | 6157 | 0 | 0x0fc05f10
SS2RocniVklopKlima4 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima4 | [6 empty] | 6157 | 0 | 0x0fc05f20
SS2RocniVklopKlima5 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima5 | [6 empty] | 6157 | 0 | 0x0fc05f30
SS2RocniVklopKlima6 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima6 | [6 empty] | 6157 | 0 | 0x0fc05f40
SS2SinhronizacijaPanelOK | DIGITAL | IOD_SS2 | SS2:.SinhronizacijaPanelOK | [6 empty] | 6157 | 0 | 0x0fc05f50
SS2SinhronizirajCas_Panel | DIGITAL | IOD_SS2 | SS2:.SinhronizirajCas_Panel | [6 empty] | 6157 | 0 | 0x0fc05f60
SS2SKTemp1 | REAL | IOD_SS2 | SS2:.SKTemp1 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc05f70
SS2SKTemp2 | REAL | IOD_SS2 | SS2:.SKTemp2 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc05f71
SS2SKTemp3 | REAL | IOD_SS2 | SS2:.SKTemp3 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc05f72
SS2SKTemp4 | REAL | IOD_SS2 | SS2:.SKTemp4 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc05f73
SS2SkupneNapakeNaprav_Klima1 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima1 | [6 empty] | 6157 | 0 | 0x0fc05f80
SS2SkupneNapakeNaprav_Klima2 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima2 | [6 empty] | 6157 | 0 | 0x0fc05f90
SS2SkupneNapakeNaprav_Klima3 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima3 | [6 empty] | 6157 | 0 | 0x0fc05fa0
SS2SkupneNapakeNaprav_Klima4 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima4 | [6 empty] | 6157 | 0 | 0x0fc05fb0
SS2SkupneNapakeNaprav_Klima5 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima5 | [6 empty] | 6157 | 0 | 0x0fc05fc0
SS2SkupneNapakeNaprav_Klima6 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima6 | [6 empty] | 6157 | 0 | 0x0fc05fd0
SS2SkupneNapakeNaprav_Komunikacija | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Komunikacija | [6 empty] | 6157 | 0 | 0x0fc05fe0
SS2SkupneNapakeNaprav_PMM17VirBVirA | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_PMM17VirBVirA | [6 empty] | 6157 | 0 | 0x0fc05ff0
SS2SkupneNapakeNaprav_PMM63VirBVirA | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_PMM63VirBVirA | [6 empty] | 6157 | 0 | 0x0fc06000
SS2SkupneNapakeNaprav_TempVlaga | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_TempVlaga | [6 empty] | 6157 | 0 | 0x0fc06010
SS2SKVlaga1 | REAL | IOD_SS2 | SS2:.SKVlaga1 | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc06020
SS2SKVlaga2 | REAL | IOD_SS2 | SS2:.SKVlaga2 | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc06021
SS2SKVlaga3 | REAL | IOD_SS2 | SS2:.SKVlaga3 | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc06022
SS2SKVlaga4 | REAL | IOD_SS2 | SS2:.SKVlaga4 | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc06023
SS2StanjeKlimat2_1_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_1_Delovanje | [6 empty] | 6157 | 0 | 0x0fc06030
SS2StanjeKlimat2_2_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_2_Delovanje | [6 empty] | 6157 | 0 | 0x0fc06040
SS2StanjeKlimat2_3_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_3_Delovanje | [6 empty] | 6157 | 0 | 0x0fc06050
SS2StanjeKlimat2_4_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_4_Delovanje | [6 empty] | 6157 | 0 | 0x0fc06060
SS2StanjeKlimat2_5_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_5_Delovanje | [6 empty] | 6157 | 0 | 0x0fc06070
SS2StanjeKlimat2_6_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_6_Delovanje | [6 empty] | 6157 | 0 | 0x0fc06080
SS2StanjeUPSKrmOmara_BaterijskiNacin | DIGITAL | IOD_SS2 | SS2:.StanjeUPSKrmOmara_BaterijskiNacin | [6 empty] | 6157 | 0 | 0x0fc06090
SS2StanjeUPSKrmOmara_Polnjenje | DIGITAL | IOD_SS2 | SS2:.StanjeUPSKrmOmara_Polnjenje | [6 empty] | 6157 | 0 | 0x0fc060a0
SS2StUrZaPreklopKlim1_2 | INT | IOD_SS2 | SS2:.StUrZaPreklopKlim1_2 | [6 empty] | 6157 | 0 | 0x0fc060b0
SS2StUrZaPreklopKlim3_4 | INT | IOD_SS2 | SS2:.StUrZaPreklopKlim3_4 | [6 empty] | 6157 | 0 | 0x0fc060b1
SS2StUrZaPreklopKlim5_6 | INT | IOD_SS2 | SS2:.StUrZaPreklopKlim5_6 | [6 empty] | 6157 | 0 | 0x0fc060b2
SS2TempZaAlarm1_2 | REAL | IOD_SS2 | SS2:.TempZaAlarm1_2 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc060b3
SS2TempZaAlarm3_4 | REAL | IOD_SS2 | SS2:.TempZaAlarm3_4 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc060b4
SS2TempZaAlarm5_6 | REAL | IOD_SS2 | SS2:.TempZaAlarm5_6 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc060b5
SS2TempZaAlarmTIA1 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA1 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc060b6
SS2TempZaAlarmTIA2 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA2 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc060b7
SS2TempZaAlarmTIA3 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA3 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc060b8
SS2TempZaAlarmTIA4 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA4 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc060b9
SS2TempZaVklopObehKlim1_2 | REAL | IOD_SS2 | SS2:.TempZaVklopObehKlim1_2 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc060ba
SS2TempZaVklopObehKlim3_4 | REAL | IOD_SS2 | SS2:.TempZaVklopObehKlim3_4 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc060bb
SS2TempZaVklopObehKlim3_4TIA3 | REAL | IOD_SS2 | SS2:.TempZaVklopObehKlim3_4TIA3 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc060bc
SS2TempZaVklopObehKlim5_6 | REAL | IOD_SS2 | SS2:.TempZaVklopObehKlim5_6 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc060bd
SS2TempZaVklopObehKlim5_6TIA3 | REAL | IOD_SS2 | SS2:.TempZaVklopObehKlim5_6TIA3 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc060be
SS2UPSstatus_Prikaz_PanelSCADA | BYTE | IOD_SS2 | SS2:.UPSstatus_Prikaz_PanelSCADA | [6 empty] | 6157 | 0 | 0x0fc060bf
SS2UserCurrentLevel | BYTE | IOD_SS2 | SS2:.UserCurrentLevel | [6 empty] | 6157 | 0 | 0x0fc060c0
SS2UserLoggedIn | DIGITAL | IOD_SS2 | SS2:.UserLoggedIn | [6 empty] | 6157 | 0 | 0x0fc060d0
SS2UserName | STRING | IOD_SS2 | SS2:.UserName | [6 empty] | 6157 | 0 | 0x0fc060e0
SS2XVH_AlarmOn | DIGITAL | IOD_SS2 | SS2:.XVH_AlarmOn | [6 empty] | 6157 | 0 | 0x0fc060f0
SS2OmogociVseDogodke_DO | DIGITAL | IOD_SS2_disk | D559 | [8 empty] | 0x0fc06100
SS2OmogociVseDogodke_DI | DIGITAL | IOD_SS2_disk | D560 | [8 empty] | 0x0fc06110
SS2OmogociVseDogodke_COM | DIGITAL | IOD_SS2_disk | D567 | [8 empty] | 0x0fc06120
SS2Klimat2_1_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_1_Vklop | [6 empty] | 6157 |  | 0x0fc06130
SS2Klimat2_2_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_2_Vklop | [6 empty] | 6157 |  | 0x0fc06140
SS2Klimat2_3_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_3_Vklop | [6 empty] | 6157 |  | 0x0fc06150
SS2Klimat2_4_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_4_Vklop | [6 empty] | 6157 |  | 0x0fc06160
SS2Klimat2_5_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_5_Vklop | [6 empty] | 6157 |  | 0x0fc06170
SS2Klimat2_6_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_6_Vklop | [6 empty] | 6157 |  | 0x0fc06180
SS2ErrorComKlima1Code0 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[1].Code[0] | [6 empty] | 6157 | 0 | 0x0fc06190
SS2ErrorComKlima1Code10 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[1].Code[10] | [6 empty] | 6157 | 0 | 0x0fc06191
SS2ErrorComKlima1Code11 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[1].Code[11] | [6 empty] | 6157 | 0 | 0x0fc06192
SS2ErrorComKlima1Code12 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[1].Code[12] | [6 empty] | 6157 | 0 | 0x0fc06193
SS2ErrorComKlima1Code13 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[1].Code[13] | [6 empty] | 6157 | 0 | 0x0fc06194
SS2ErrorComKlima1Code14 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[1].Code[14] | [6 empty] | 6157 | 0 | 0x0fc06195
SS2ErrorComKlima1Code15 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[1].Code[15] | [6 empty] | 6157 | 0 | 0x0fc06196
SS2ErrorComKlima1Code1 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[1].Code[1] | [6 empty] | 6157 | 0 | 0x0fc06197
SS2ErrorComKlima1Code2 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[1].Code[2] | [6 empty] | 6157 | 0 | 0x0fc06198
SS2ErrorComKlima1Code3 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[1].Code[3] | [6 empty] | 6157 | 0 | 0x0fc06199
SS2ErrorComKlima1Code4 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[1].Code[4] | [6 empty] | 6157 | 0 | 0x0fc0619a
SS2ErrorComKlima1Code5 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[1].Code[5] | [6 empty] | 6157 | 0 | 0x0fc0619b
SS2ErrorComKlima1Code6 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[1].Code[6] | [6 empty] | 6157 | 0 | 0x0fc0619c
SS2ErrorComKlima1Code7 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[1].Code[7] | [6 empty] | 6157 | 0 | 0x0fc0619d
SS2ErrorComKlima1Code8 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[1].Code[8] | [6 empty] | 6157 | 0 | 0x0fc0619e
SS2ErrorComKlima1Code9 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[1].Code[9] | [6 empty] | 6157 | 0 | 0x0fc0619f
SS2ErrorComKlima2Code0 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[2].Code[0] | [6 empty] | 6157 | 0 | 0x0fc061a0
SS2ErrorComKlima2Code10 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[2].Code[10] | [6 empty] | 6157 | 0 | 0x0fc061a1
SS2ErrorComKlima2Code11 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[2].Code[11] | [6 empty] | 6157 | 0 | 0x0fc061a2
SS2ErrorComKlima2Code12 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[2].Code[12] | [6 empty] | 6157 | 0 | 0x0fc061a3
SS2ErrorComKlima2Code13 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[2].Code[13] | [6 empty] | 6157 | 0 | 0x0fc061a4
SS2ErrorComKlima2Code14 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[2].Code[14] | [6 empty] | 6157 | 0 | 0x0fc061a5
SS2ErrorComKlima2Code15 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[2].Code[15] | [6 empty] | 6157 | 0 | 0x0fc061a6
SS2ErrorComKlima2Code1 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[2].Code[1] | [6 empty] | 6157 | 0 | 0x0fc061a7
SS2ErrorComKlima2Code2 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[2].Code[2] | [6 empty] | 6157 | 0 | 0x0fc061a8
SS2ErrorComKlima2Code3 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[2].Code[3] | [6 empty] | 6157 | 0 | 0x0fc061a9
SS2ErrorComKlima2Code4 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[2].Code[4] | [6 empty] | 6157 | 0 | 0x0fc061aa
SS2ErrorComKlima2Code5 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[2].Code[5] | [6 empty] | 6157 | 0 | 0x0fc061ab
SS2ErrorComKlima2Code6 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[2].Code[6] | [6 empty] | 6157 | 0 | 0x0fc061ac
SS2ErrorComKlima2Code7 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[2].Code[7] | [6 empty] | 6157 | 0 | 0x0fc061ad
SS2ErrorComKlima2Code8 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[2].Code[8] | [6 empty] | 6157 | 0 | 0x0fc061ae
SS2ErrorComKlima2Code9 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[2].Code[9] | [6 empty] | 6157 | 0 | 0x0fc061af
SS2ErrorComKlima3Code0 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[3].Code[0] | [6 empty] | 6157 | 0 | 0x0fc061b0
SS2ErrorComKlima3Code10 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[3].Code[10] | [6 empty] | 6157 | 0 | 0x0fc061b1
SS2ErrorComKlima3Code11 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[3].Code[11] | [6 empty] | 6157 | 0 | 0x0fc061b2
SS2ErrorComKlima3Code12 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[3].Code[12] | [6 empty] | 6157 | 0 | 0x0fc061b3
SS2ErrorComKlima3Code13 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[3].Code[13] | [6 empty] | 6157 | 0 | 0x0fc061b4
SS2ErrorComKlima3Code14 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[3].Code[14] | [6 empty] | 6157 | 0 | 0x0fc061b5
SS2ErrorComKlima3Code15 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[3].Code[15] | [6 empty] | 6157 | 0 | 0x0fc061b6
SS2ErrorComKlima3Code1 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[3].Code[1] | [6 empty] | 6157 | 0 | 0x0fc061b7
SS2ErrorComKlima3Code2 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[3].Code[2] | [6 empty] | 6157 | 0 | 0x0fc061b8
SS2ErrorComKlima3Code3 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[3].Code[3] | [6 empty] | 6157 | 0 | 0x0fc061b9
SS2ErrorComKlima3Code4 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[3].Code[4] | [6 empty] | 6157 | 0 | 0x0fc061ba
SS2ErrorComKlima3Code5 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[3].Code[5] | [6 empty] | 6157 | 0 | 0x0fc061bb
SS2ErrorComKlima3Code6 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[3].Code[6] | [6 empty] | 6157 | 0 | 0x0fc061bc
SS2ErrorComKlima3Code7 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[3].Code[7] | [6 empty] | 6157 | 0 | 0x0fc061bd
SS2ErrorComKlima3Code8 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[3].Code[8] | [6 empty] | 6157 | 0 | 0x0fc061be
SS2ErrorComKlima3Code9 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[3].Code[9] | [6 empty] | 6157 | 0 | 0x0fc061bf
SS2ErrorComKlima4Code0 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[4].Code[0] | [6 empty] | 6157 | 0 | 0x0fc061c0
SS2ErrorComKlima4Code10 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[4].Code[10] | [6 empty] | 6157 | 0 | 0x0fc061c1
SS2ErrorComKlima4Code11 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[4].Code[11] | [6 empty] | 6157 | 0 | 0x0fc061c2
SS2ErrorComKlima4Code12 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[4].Code[12] | [6 empty] | 6157 | 0 | 0x0fc061c3
SS2ErrorComKlima4Code13 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[4].Code[13] | [6 empty] | 6157 | 0 | 0x0fc061c4
SS2ErrorComKlima4Code14 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[4].Code[14] | [6 empty] | 6157 | 0 | 0x0fc061c5
SS2ErrorComKlima4Code15 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[4].Code[15] | [6 empty] | 6157 | 0 | 0x0fc061c6
SS2ErrorComKlima4Code1 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[4].Code[1] | [6 empty] | 6157 | 0 | 0x0fc061c7
SS2ErrorComKlima4Code2 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[4].Code[2] | [6 empty] | 6157 | 0 | 0x0fc061c8
SS2ErrorComKlima4Code3 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[4].Code[3] | [6 empty] | 6157 | 0 | 0x0fc061c9
SS2ErrorComKlima4Code4 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[4].Code[4] | [6 empty] | 6157 | 0 | 0x0fc061ca
SS2ErrorComKlima4Code5 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[4].Code[5] | [6 empty] | 6157 | 0 | 0x0fc061cb
SS2ErrorComKlima4Code6 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[4].Code[6] | [6 empty] | 6157 | 0 | 0x0fc061cc
SS2ErrorComKlima4Code7 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[4].Code[7] | [6 empty] | 6157 | 0 | 0x0fc061cd
SS2ErrorComKlima4Code8 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[4].Code[8] | [6 empty] | 6157 | 0 | 0x0fc061ce
SS2ErrorComKlima4Code9 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[4].Code[9] | [6 empty] | 6157 | 0 | 0x0fc061cf
SS2ErrorComKlima5Code0 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[5].Code[0] | [6 empty] | 6157 | 0 | 0x0fc061d0
SS2ErrorComKlima5Code10 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[5].Code[10] | [6 empty] | 6157 | 0 | 0x0fc061d1
SS2ErrorComKlima5Code11 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[5].Code[11] | [6 empty] | 6157 | 0 | 0x0fc061d2
SS2ErrorComKlima5Code12 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[5].Code[12] | [6 empty] | 6157 | 0 | 0x0fc061d3
SS2ErrorComKlima5Code13 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[5].Code[13] | [6 empty] | 6157 | 0 | 0x0fc061d4
SS2ErrorComKlima5Code14 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[5].Code[14] | [6 empty] | 6157 | 0 | 0x0fc061d5
SS2ErrorComKlima5Code15 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[5].Code[15] | [6 empty] | 6157 | 0 | 0x0fc061d6
SS2ErrorComKlima5Code1 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[5].Code[1] | [6 empty] | 6157 | 0 | 0x0fc061d7
SS2ErrorComKlima5Code2 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[5].Code[2] | [6 empty] | 6157 | 0 | 0x0fc061d8
SS2ErrorComKlima5Code3 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[5].Code[3] | [6 empty] | 6157 | 0 | 0x0fc061d9
SS2ErrorComKlima5Code4 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[5].Code[4] | [6 empty] | 6157 | 0 | 0x0fc061da
SS2ErrorComKlima5Code5 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[5].Code[5] | [6 empty] | 6157 | 0 | 0x0fc061db
SS2ErrorComKlima5Code6 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[5].Code[6] | [6 empty] | 6157 | 0 | 0x0fc061dc
SS2ErrorComKlima5Code7 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[5].Code[7] | [6 empty] | 6157 | 0 | 0x0fc061dd
SS2ErrorComKlima5Code8 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[5].Code[8] | [6 empty] | 6157 | 0 | 0x0fc061de
SS2ErrorComKlima5Code9 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[5].Code[9] | [6 empty] | 6157 | 0 | 0x0fc061df
SS2ErrorComKlima6Code0 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[6].Code[0] | [6 empty] | 6157 | 0 | 0x0fc061e0
SS2ErrorComKlima6Code10 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[6].Code[10] | [6 empty] | 6157 | 0 | 0x0fc061e1
SS2ErrorComKlima6Code11 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[6].Code[11] | [6 empty] | 6157 | 0 | 0x0fc061e2
SS2ErrorComKlima6Code12 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[6].Code[12] | [6 empty] | 6157 | 0 | 0x0fc061e3
SS2ErrorComKlima6Code13 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[6].Code[13] | [6 empty] | 6157 | 0 | 0x0fc061e4
SS2ErrorComKlima6Code14 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[6].Code[14] | [6 empty] | 6157 | 0 | 0x0fc061e5
SS2ErrorComKlima6Code15 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[6].Code[15] | [6 empty] | 6157 | 0 | 0x0fc061e6
SS2ErrorComKlima6Code1 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[6].Code[1] | [6 empty] | 6157 | 0 | 0x0fc061e7
SS2ErrorComKlima6Code2 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[6].Code[2] | [6 empty] | 6157 | 0 | 0x0fc061e8
SS2ErrorComKlima6Code3 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[6].Code[3] | [6 empty] | 6157 | 0 | 0x0fc061e9
SS2ErrorComKlima6Code4 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[6].Code[4] | [6 empty] | 6157 | 0 | 0x0fc061ea
SS2ErrorComKlima6Code5 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[6].Code[5] | [6 empty] | 6157 | 0 | 0x0fc061eb
SS2ErrorComKlima6Code6 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[6].Code[6] | [6 empty] | 6157 | 0 | 0x0fc061ec
SS2ErrorComKlima6Code7 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[6].Code[7] | [6 empty] | 6157 | 0 | 0x0fc061ed
SS2ErrorComKlima6Code8 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[6].Code[8] | [6 empty] | 6157 | 0 | 0x0fc061ee
SS2ErrorComKlima6Code9 | BYTE | IOD_SS2 | SS2:.ErrorComKlima[6].Code[9] | [6 empty] | 6157 | 0 | 0x0fc061ef
SS2ErrorComPMM1Code0 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[1].Code[0] | [6 empty] | 6157 | 0 | 0x0fc061f0
SS2ErrorComPMM1Code10 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[1].Code[10] | [6 empty] | 6157 | 0 | 0x0fc061f1
SS2ErrorComPMM1Code11 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[1].Code[11] | [6 empty] | 6157 | 0 | 0x0fc061f2
SS2ErrorComPMM1Code12 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[1].Code[12] | [6 empty] | 6157 | 0 | 0x0fc061f3
SS2ErrorComPMM1Code13 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[1].Code[13] | [6 empty] | 6157 | 0 | 0x0fc061f4
SS2ErrorComPMM1Code14 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[1].Code[14] | [6 empty] | 6157 | 0 | 0x0fc061f5
SS2ErrorComPMM1Code15 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[1].Code[15] | [6 empty] | 6157 | 0 | 0x0fc061f6
SS2ErrorComPMM1Code1 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[1].Code[1] | [6 empty] | 6157 | 0 | 0x0fc061f7
SS2ErrorComPMM1Code2 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[1].Code[2] | [6 empty] | 6157 | 0 | 0x0fc061f8
SS2ErrorComPMM1Code3 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[1].Code[3] | [6 empty] | 6157 | 0 | 0x0fc061f9
SS2ErrorComPMM1Code4 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[1].Code[4] | [6 empty] | 6157 | 0 | 0x0fc061fa
SS2ErrorComPMM1Code5 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[1].Code[5] | [6 empty] | 6157 | 0 | 0x0fc061fb
SS2ErrorComPMM1Code6 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[1].Code[6] | [6 empty] | 6157 | 0 | 0x0fc061fc
SS2ErrorComPMM1Code7 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[1].Code[7] | [6 empty] | 6157 | 0 | 0x0fc061fd
SS2ErrorComPMM1Code8 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[1].Code[8] | [6 empty] | 6157 | 0 | 0x0fc061fe
SS2ErrorComPMM1Code9 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[1].Code[9] | [6 empty] | 6157 | 0 | 0x0fc061ff
SS2ErrorComPMM2Code0 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[2].Code[0] | [6 empty] | 6157 | 0 | 0x0fc06200
SS2ErrorComPMM2Code10 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[2].Code[10] | [6 empty] | 6157 | 0 | 0x0fc06201
SS2ErrorComPMM2Code11 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[2].Code[11] | [6 empty] | 6157 | 0 | 0x0fc06202
SS2ErrorComPMM2Code12 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[2].Code[12] | [6 empty] | 6157 | 0 | 0x0fc06203
SS2ErrorComPMM2Code13 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[2].Code[13] | [6 empty] | 6157 | 0 | 0x0fc06204
SS2ErrorComPMM2Code14 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[2].Code[14] | [6 empty] | 6157 | 0 | 0x0fc06205
SS2ErrorComPMM2Code15 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[2].Code[15] | [6 empty] | 6157 | 0 | 0x0fc06206
SS2ErrorComPMM2Code1 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[2].Code[1] | [6 empty] | 6157 | 0 | 0x0fc06207
SS2ErrorComPMM2Code2 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[2].Code[2] | [6 empty] | 6157 | 0 | 0x0fc06208
SS2ErrorComPMM2Code3 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[2].Code[3] | [6 empty] | 6157 | 0 | 0x0fc06209
SS2ErrorComPMM2Code4 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[2].Code[4] | [6 empty] | 6157 | 0 | 0x0fc0620a
SS2ErrorComPMM2Code5 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[2].Code[5] | [6 empty] | 6157 | 0 | 0x0fc0620b
SS2ErrorComPMM2Code6 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[2].Code[6] | [6 empty] | 6157 | 0 | 0x0fc0620c
SS2ErrorComPMM2Code7 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[2].Code[7] | [6 empty] | 6157 | 0 | 0x0fc0620d
SS2ErrorComPMM2Code8 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[2].Code[8] | [6 empty] | 6157 | 0 | 0x0fc0620e
SS2ErrorComPMM2Code9 | BYTE | IOD_SS2 | SS2:.ErrorComPMM[2].Code[9] | [6 empty] | 6157 | 0 | 0x0fc0620f
SS2PricetekSMSAlarmov1 | INT | IOD_SS2_disk | I60 | [8 empty] | 0x0fc06210
SS2KonecSMSAlarmov1 | INT | IOD_SS2_disk | I61 | [8 empty] | 0x0fc06211
SS2PricetekSMSAlarmov2 | INT | IOD_SS2_disk | I62 | [8 empty] | 0x0fc06212
SS2KonecSMSAlarmov2 | INT | IOD_SS2_disk | I63 | [8 empty] | 0x0fc06213
SS2PricetekSMSAlarmov3 | INT | IOD_SS2_disk | I64 | [8 empty] | 0x0fc06214
SS2KonecSMSAlarmov3 | INT | IOD_SS2_disk | I65 | [8 empty] | 0x0fc06215
SS2AlarmSinhronizacijaNOK_Omogoci | DIGITAL | IOD_SS2_disk | D3965 | [8 empty] | 0x0fc06220
SS2ErrCommScada2 | DIGITAL | IOD_SS2 | SS2:.ErrCommScada2 | [8 empty] | 0x0fc06230
SS2ComSCADA2 | DIGITAL | IOD_SS2 | SS2:.ComSCADA2 | [8 empty] | 0x0fc06240
SS2ErrCommScada_Omogoci2 | DIGITAL | IOD_SS2_disk | D3968 | [8 empty] | 0x0fc06250
SS2Server_A_Izpad | DIGITAL | IOD_SS2_disk | D3969 | [8 empty] | 0x0fc06260
SS2Server_B_Izpad | DIGITAL | IOD_SS2_disk | D3970 | [8 empty] | 0x0fc06270
SS2ComSCADA_stevec3 | INT | IOD_SS2_mem | I3972 | [8 empty] | 0x0fc06280
SS2ComSCADA_stevec | INT | IOD_SS2_mem | I3974 | [8 empty] | 0x0fc06281
SS2ComSCADA3 | DIGITAL | IOD_SS2 | SS2:.ComSCADA3 | [8 empty] | 0x0fc06290
SS2kom_nast_cas_izpada | INT | IOD_SS2 | SS2:.kom_nast_cas_izpada | [8 empty] | 0x0fc062a0
SS2AlarmSKTemp5_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp5_Previsoka | [6 empty] | 6157 | 0 | 0x0fc062b0
SS2AlarmSKTemp6_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp6_Previsoka | [6 empty] | 6157 | 0 | 0x0fc062c0
SS2AlarmTempTIA5Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA5Previsoka | [6 empty] | 6157 | 0 | 0x0fc062d0
SS2AlarmTempTIA6Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA6Previsoka | [6 empty] | 6157 | 0 | 0x0fc062e0
SS2NapakaSenzorTemp5 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp5 | [6 empty] | 6157 | 0 | 0x0fc062f0
SS2NapakaSenzorTemp6 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp6 | [6 empty] | 6157 | 0 | 0x0fc06300
SS2NapakaSenzorVlaga5 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga5 | [6 empty] | 6157 | 0 | 0x0fc06310
SS2NapakaSenzorVlaga6 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga6 | [6 empty] | 6157 | 0 | 0x0fc06320
SS2SKTemp5 | REAL | IOD_SS2 | SS2:.SKTemp5 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc06330
SS2SKTemp6 | REAL | IOD_SS2 | SS2:.SKTemp6 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc06331
SS2SKVlaga5 | REAL | IOD_SS2 | SS2:.SKVlaga5 | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc06332
SS2SKVlaga6 | REAL | IOD_SS2 | SS2:.SKVlaga6 | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x0fc06333
SS2TempZaAlarmTIA5 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA5 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc06334
SS2TempZaAlarmTIA6 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA6 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc06335
SS2PrikazNastTemp5 | DIGITAL | IOD_SS2_disk | D5000 | [8 empty] | 0x0fc06340
SS2PrikazNastTemp6 | DIGITAL | IOD_SS2_disk | D5001 | [8 empty] | 0x0fc06350
SS2NapakaSenzorTemp5_Omogoci | DIGITAL | IOD_SS2_disk | D5002 | [8 empty] | 0x0fc06360
SS2NapakaSenzorTemp6_Omogoci | DIGITAL | IOD_SS2_disk | D5003 | [8 empty] | 0x0fc06370
SS2NapakaSenzorVlaga5_Omogoci | DIGITAL | IOD_SS2_disk | D5004 | [8 empty] | 0x0fc06380
SS2NapakaSenzorVlaga6_Omogoci | DIGITAL | IOD_SS2_disk | D5005 | [8 empty] | 0x0fc06390
SS2SKTemp5_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R17 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc063a0
SS2SKTemp5_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R18 | 0 | 60 | 0 | 60 | °C | ####.# |  |  | 0x0fc063a1
SS2SKTemp5_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D5006 | [8 empty] | 0x0fc063b0
SS2SKTemp5_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D5007 | [8 empty] | 0x0fc063c0
SS2SKVlaga5_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R19 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc063d0
SS2SKVlaga5_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R20 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc063d1
SS2SKVlaga5_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D5008 | [8 empty] | 0x0fc063e0
SS2SKVlaga5_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D5009 | [8 empty] | 0x0fc063f0
SS2SKTemp6_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R21 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc06400
SS2SKTemp6_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R22 | 0 | 60 | 0 | 60 | °C | ####.# |  |  | 0x0fc06401
SS2SKTemp6_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D5010 | [8 empty] | 0x0fc06410
SS2SKTemp6_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D5011 | [8 empty] | 0x0fc06420
SS2SKVlaga6_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R23 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc06430
SS2SKVlaga6_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R24 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x0fc06431
SS2SKVlaga6_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D5012 | [8 empty] | 0x0fc06440
SS2SKVlaga6_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D5013 | [8 empty] | 0x0fc06450
SS2AlarmTempTIA5Previsoka_Omogoci | DIGITAL | IOD_SS2_disk | D5014 | [8 empty] | 0x0fc06460
SS2AlarmTempTIA6Previsoka_Omogoci | DIGITAL | IOD_SS2_disk | D5015 | [8 empty] | 0x0fc06470
SS2SKTempServSoba1Povpr | REAL | IOD_SS2 | SS2:.SKTempServSoba1Povpr | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc06480
SS2SKTempServSoba2Povpr | REAL | IOD_SS2 | SS2:.SKTempServSoba2Povpr | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc06481
SS2TempZaAlarmTIA235 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA235 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc06482
SS2TempZaAlarmTIA46 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA46 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x0fc06483
SS2AlarmTempTIA235Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA235Previsoka | [6 empty] | 6157 | 0 | 0x0fc06490
SS2AlarmTempTIA46Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA46Previsoka | [6 empty] | 6157 | 0 | 0x0fc064a0
SS2AlarmTempTIA235Previsoka_Omogoci | DIGITAL | IOD_SS2_disk | D5016 | [8 empty] | 0x0fc064b0
SS2AlarmTempTIA46Previsoka_Omogoci | DIGITAL | IOD_SS2_disk | D5017 | [8 empty] | 0x0fc064c0

## variable_1
SS2AktualniSetPointTemp1_2 | REAL | IOD_SS2 | SS2:.AktualniSetPointTemp1_2
SS2AktualniSetPointTemp3_4 | REAL | IOD_SS2 | SS2:.AktualniSetPointTemp3_4
SS2AktualniSetPointTemp5_6 | REAL | IOD_SS2 | SS2:.AktualniSetPointTemp5_6
SS2AlarmKlimat2_1_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_1_Napaka
SS2AlarmKlimat2_2_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_2_Napaka
SS2AlarmKlimat2_3_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_3_Napaka
SS2AlarmKlimat2_4_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_4_Napaka
SS2AlarmKlimat2_5_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_5_Napaka
SS2AlarmKlimat2_6_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_6_Napaka
SS2AlarmLAH1RazlitjeVode | DIGITAL | IOD_SS2 | SS2:.AlarmLAH1RazlitjeVode
SS2AlarmLAH2RazlitjeVode | DIGITAL | IOD_SS2 | SS2:.AlarmLAH2RazlitjeVode
SS2AlarmLAH3RazlitjeVode | DIGITAL | IOD_SS2 | SS2:.AlarmLAH3RazlitjeVode
SS2AlarmPMM2x17nad8010 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[10]
SS2AlarmPMM2x17nad8011 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[11]
SS2AlarmPMM2x17nad8012 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[12]
SS2AlarmPMM2x17nad8013 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[13]
SS2AlarmPMM2x17nad8014 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[14]
SS2AlarmPMM2x17nad8015 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[15]
SS2AlarmPMM2x17nad8016 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[16]
SS2AlarmPMM2x17nad8017 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[17]
SS2AlarmPMM2x17nad8018 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[18]
SS2AlarmPMM2x17nad8019 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[19]
SS2AlarmPMM2x17nad801 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[1]
SS2AlarmPMM2x17nad8020 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[20]
SS2AlarmPMM2x17nad8021 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[21]
SS2AlarmPMM2x17nad8022 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[22]
SS2AlarmPMM2x17nad8023 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[23]
SS2AlarmPMM2x17nad8024 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[24]
SS2AlarmPMM2x17nad8025 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[25]
SS2AlarmPMM2x17nad8026 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[26]
SS2AlarmPMM2x17nad8027 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[27]
SS2AlarmPMM2x17nad8028 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[28]
SS2AlarmPMM2x17nad8029 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[29]
SS2AlarmPMM2x17nad802 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[2]
SS2AlarmPMM2x17nad8030 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[30]
SS2AlarmPMM2x17nad8031 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[31]
SS2AlarmPMM2x17nad8032 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[32]
SS2AlarmPMM2x17nad8033 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[33]
SS2AlarmPMM2x17nad8034 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[34]
SS2AlarmPMM2x17nad8035 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[35]
SS2AlarmPMM2x17nad8036 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[36]
SS2AlarmPMM2x17nad8037 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[37]
SS2AlarmPMM2x17nad8038 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[38]
SS2AlarmPMM2x17nad8039 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[39]
SS2AlarmPMM2x17nad803 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[3]
SS2AlarmPMM2x17nad8040 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[40]
SS2AlarmPMM2x17nad8041 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[41]
SS2AlarmPMM2x17nad8042 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[42]
SS2AlarmPMM2x17nad804 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[4]
SS2AlarmPMM2x17nad805 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[5]
SS2AlarmPMM2x17nad806 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[6]
SS2AlarmPMM2x17nad807 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[7]
SS2AlarmPMM2x17nad808 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[8]
SS2AlarmPMM2x17nad809 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[9]
SS2AlarmSinhronizacijaNOK | DIGITAL | IOD_SS2 | SS2:.AlarmSinhronizacijaNOK
SS2AlarmSKTemp1_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp1_Previsoka
SS2AlarmSKTemp2_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp2_Previsoka
SS2AlarmSKTemp3_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp3_Previsoka
SS2AlarmSKTemp4_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp4_Previsoka
SS2AlarmTempTIA1Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA1Previsoka
SS2AlarmTempTIA2Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA2Previsoka
SS2AlarmTempTIA3Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA3Previsoka
SS2AlarmTempTIA4Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA4Previsoka
SS2AlarmUPSKrmOmara_Alarm | DIGITAL | IOD_SS2 | SS2:.AlarmUPSKrmOmara_Alarm
SS2ComSCADA | DIGITAL | IOD_SS2 | SS2:.ComSCADA
SS2ComSCADA1 | DIGITAL | IOD_SS2 | SS2:.ComSCADA1
SS2Date_Time0 | STRING | IOD_SS2 | SS2:.Date_Time[0]
SS2Date_Time1 | STRING | IOD_SS2 | SS2:.Date_Time[1]
SS2Date_Time2 | STRING | IOD_SS2 | SS2:.Date_Time[2]
SS2Date_Time3 | STRING | IOD_SS2 | SS2:.Date_Time[3]
SS2DatumCasDan | INT | IOD_SS2 | SS2:.DatumCas.Dan | BYTE
SS2DatumCasLeto | INT | IOD_SS2 | SS2:.DatumCas.Leto | BYTE
SS2DatumCasLeto2 | INT | IOD_SS2 | SS2:.DatumCas.Leto2
SS2DatumCasMesec | INT | IOD_SS2 | SS2:.DatumCas.Mesec | BYTE
SS2DatumCasMinuta | INT | IOD_SS2 | SS2:.DatumCas.Minuta | BYTE
SS2DatumCasSekunda | INT | IOD_SS2 | SS2:.DatumCas.Sekunda | BYTE
SS2DatumCasUra | INT | IOD_SS2 | SS2:.DatumCas.Ura | BYTE
SS2ErrComKlima1 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[1]
SS2ErrComKlima2 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[2]
SS2ErrComKlima3 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[3]
SS2ErrComKlima4 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[4]
SS2ErrComKlima5 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[5]
SS2ErrComKlima6 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[6]
SS2ErrCommScada | DIGITAL | IOD_SS2 | SS2:.ErrCommScada
SS2ErrComPanelPLC | DIGITAL | IOD_SS2 | SS2:.ErrComPanelPLC
SS2ErrComPMM1 | DIGITAL | IOD_SS2 | SS2:.ErrComPMM[1]
SS2ErrComPMM2 | DIGITAL | IOD_SS2 | SS2:.ErrComPMM[2]
SS2ErrComPort2 | DIGITAL | IOD_SS2 | SS2:.ErrComPort2
SS2ErrorComKlima1Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[1].Error
SS2ErrorComKlima1Status | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Status
SS2ErrorComKlima2Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[2].Error
SS2ErrorComKlima2Status | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Status
SS2ErrorComKlima3Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[3].Error
SS2ErrorComKlima3Status | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Status
SS2ErrorComKlima4Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[4].Error
SS2ErrorComKlima4Status | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Status
SS2ErrorComKlima5Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[5].Error
SS2ErrorComKlima5Status | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Status
SS2ErrorComKlima6Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[6].Error
SS2ErrorComKlima6Status | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Status
SS2ErrorComPMM1Error | DIGITAL | IOD_SS2 | SS2:.ErrorComPMM[1].Error
SS2ErrorComPMM1Status | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Status
SS2ErrorComPMM2Error | DIGITAL | IOD_SS2 | SS2:.ErrorComPMM[2].Error
SS2ErrorComPMM2Status | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Status
SS2Klima1ure | REAL | IOD_SS2 | SS2:.Klima1ure
SS2Klima2_1_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_1_Onemogocena
SS2Klima2_2_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_2_Onemogocena
SS2Klima2_3_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_3_Onemogocena
SS2Klima2_4_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_4_Onemogocena
SS2Klima2_5_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_5_Onemogocena
SS2Klima2_6_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_6_Onemogocena
SS2Klima2ure | REAL | IOD_SS2 | SS2:.Klima2ure
SS2Klima3ure | REAL | IOD_SS2 | SS2:.Klima3ure
SS2Klima4ure | REAL | IOD_SS2 | SS2:.Klima4ure
SS2Klima5ure | REAL | IOD_SS2 | SS2:.Klima5ure
SS2Klima6ure | REAL | IOD_SS2 | SS2:.Klima6ure
SS2Klima1GrelecStatus | INT | IOD_SS2 | SS2:.Klima[1].GrelecStatus | BYTE
SS2Klima1IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[1].IzhodniVentilator
SS2Klima1IzhodniVentStatus | INT | IOD_SS2 | SS2:.Klima[1].IzhodniVentStatus | BYTE
SS2Klima1Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[1].Kompresor1
SS2Klima1Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[1].Kompresor2
SS2Klima1KompresorStatus | INT | IOD_SS2 | SS2:.Klima[1].KompresorStatus | BYTE
SS2Klima1NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[1].NacinRazvlaz
SS2Klima1NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[1].NastMaxTemp
SS2Klima1NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[1].NastMaxVlaznost
SS2Klima1NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[1].NastMinTemp
SS2Klima1NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[1].NastMinVlaznost
SS2Klima1NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[1].NastTempProstora
SS2Klima1NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[1].NastVlaznost
SS2Klima1ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[1].ObratUreFilter
SS2Klima1ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[1].ObratUreKompresor1
SS2Klima1ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[1].ObratUreKompresor2
SS2Klima1ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[1].ObratUreVent
SS2Klima1Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[1].Razvlazevanje
SS2Klima1SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[1].SenzorjiStatus
SS2Klima1TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[1].TemperaturaProstora
SS2Klima1VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[1].VentilGretjeOdpiranje
SS2Klima1VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[1].VentilGretjeZapiranje
SS2Klima1Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[1].Vlazenje
SS2Klima1VlazilecStatus | INT | IOD_SS2 | SS2:.Klima[1].VlazilecStatus | BYTE
SS2Klima1VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[1].VlaznostProstora
SS2Klima2GrelecStatus | INT | IOD_SS2 | SS2:.Klima[2].GrelecStatus | BYTE
SS2Klima2IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[2].IzhodniVentilator
SS2Klima2IzhodniVentStatus | INT | IOD_SS2 | SS2:.Klima[2].IzhodniVentStatus | BYTE
SS2Klima2Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[2].Kompresor1
SS2Klima2Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[2].Kompresor2
SS2Klima2KompresorStatus | INT | IOD_SS2 | SS2:.Klima[2].KompresorStatus | BYTE
SS2Klima2NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[2].NacinRazvlaz
SS2Klima2NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[2].NastMaxTemp
SS2Klima2NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[2].NastMaxVlaznost
SS2Klima2NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[2].NastMinTemp
SS2Klima2NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[2].NastMinVlaznost
SS2Klima2NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[2].NastTempProstora
SS2Klima2NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[2].NastVlaznost
SS2Klima2ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[2].ObratUreFilter
SS2Klima2ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[2].ObratUreKompresor1
SS2Klima2ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[2].ObratUreKompresor2
SS2Klima2ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[2].ObratUreVent
SS2Klima2Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[2].Razvlazevanje
SS2Klima2SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[2].SenzorjiStatus
SS2Klima2TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[2].TemperaturaProstora
SS2Klima2VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[2].VentilGretjeOdpiranje
SS2Klima2VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[2].VentilGretjeZapiranje
SS2Klima2Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[2].Vlazenje
SS2Klima2VlazilecStatus | INT | IOD_SS2 | SS2:.Klima[2].VlazilecStatus | BYTE
SS2Klima2VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[2].VlaznostProstora
SS2Klima3GrelecStatus | INT | IOD_SS2 | SS2:.Klima[3].GrelecStatus | BYTE
SS2Klima3IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[3].IzhodniVentilator
SS2Klima3IzhodniVentStatus | INT | IOD_SS2 | SS2:.Klima[3].IzhodniVentStatus | BYTE
SS2Klima3Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[3].Kompresor1
SS2Klima3Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[3].Kompresor2
SS2Klima3KompresorStatus | INT | IOD_SS2 | SS2:.Klima[3].KompresorStatus | BYTE
SS2Klima3NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[3].NacinRazvlaz
SS2Klima3NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[3].NastMaxTemp
SS2Klima3NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[3].NastMaxVlaznost
SS2Klima3NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[3].NastMinTemp
SS2Klima3NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[3].NastMinVlaznost
SS2Klima3NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[3].NastTempProstora
SS2Klima3NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[3].NastVlaznost
SS2Klima3ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[3].ObratUreFilter
SS2Klima3ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[3].ObratUreKompresor1
SS2Klima3ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[3].ObratUreKompresor2
SS2Klima3ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[3].ObratUreVent
SS2Klima3Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[3].Razvlazevanje
SS2Klima3SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[3].SenzorjiStatus
SS2Klima3TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[3].TemperaturaProstora
SS2Klima3VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[3].VentilGretjeOdpiranje
SS2Klima3VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[3].VentilGretjeZapiranje
SS2Klima3Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[3].Vlazenje
SS2Klima3VlazilecStatus | INT | IOD_SS2 | SS2:.Klima[3].VlazilecStatus | BYTE
SS2Klima3VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[3].VlaznostProstora
SS2Klima4GrelecStatus | INT | IOD_SS2 | SS2:.Klima[4].GrelecStatus | BYTE
SS2Klima4IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[4].IzhodniVentilator
SS2Klima4IzhodniVentStatus | INT | IOD_SS2 | SS2:.Klima[4].IzhodniVentStatus | BYTE
SS2Klima4Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[4].Kompresor1
SS2Klima4Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[4].Kompresor2
SS2Klima4KompresorStatus | INT | IOD_SS2 | SS2:.Klima[4].KompresorStatus | BYTE
SS2Klima4NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[4].NacinRazvlaz
SS2Klima4NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[4].NastMaxTemp
SS2Klima4NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[4].NastMaxVlaznost
SS2Klima4NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[4].NastMinTemp
SS2Klima4NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[4].NastMinVlaznost
SS2Klima4NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[4].NastTempProstora
SS2Klima4NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[4].NastVlaznost
SS2Klima4ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[4].ObratUreFilter
SS2Klima4ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[4].ObratUreKompresor1
SS2Klima4ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[4].ObratUreKompresor2
SS2Klima4ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[4].ObratUreVent
SS2Klima4Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[4].Razvlazevanje
SS2Klima4SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[4].SenzorjiStatus
SS2Klima4TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[4].TemperaturaProstora
SS2Klima4VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[4].VentilGretjeOdpiranje
SS2Klima4VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[4].VentilGretjeZapiranje
SS2Klima4Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[4].Vlazenje
SS2Klima4VlazilecStatus | INT | IOD_SS2 | SS2:.Klima[4].VlazilecStatus | BYTE
SS2Klima4VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[4].VlaznostProstora
SS2Klima5GrelecStatus | INT | IOD_SS2 | SS2:.Klima[5].GrelecStatus | BYTE
SS2Klima5IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[5].IzhodniVentilator
SS2Klima5IzhodniVentStatus | INT | IOD_SS2 | SS2:.Klima[5].IzhodniVentStatus | BYTE
SS2Klima5Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[5].Kompresor1
SS2Klima5Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[5].Kompresor2
SS2Klima5KompresorStatus | INT | IOD_SS2 | SS2:.Klima[5].KompresorStatus | BYTE
SS2Klima5NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[5].NacinRazvlaz
SS2Klima5NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[5].NastMaxTemp
SS2Klima5NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[5].NastMaxVlaznost
SS2Klima5NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[5].NastMinTemp
SS2Klima5NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[5].NastMinVlaznost
SS2Klima5NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[5].NastTempProstora
SS2Klima5NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[5].NastVlaznost
SS2Klima5ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[5].ObratUreFilter
SS2Klima5ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[5].ObratUreKompresor1
SS2Klima5ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[5].ObratUreKompresor2
SS2Klima5ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[5].ObratUreVent
SS2Klima5Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[5].Razvlazevanje
SS2Klima5SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[5].SenzorjiStatus
SS2Klima5TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[5].TemperaturaProstora
SS2Klima5VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[5].VentilGretjeOdpiranje
SS2Klima5VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[5].VentilGretjeZapiranje
SS2Klima5Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[5].Vlazenje
SS2Klima5VlazilecStatus | INT | IOD_SS2 | SS2:.Klima[5].VlazilecStatus | BYTE
SS2Klima5VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[5].VlaznostProstora
SS2Klima6GrelecStatus | INT | IOD_SS2 | SS2:.Klima[6].GrelecStatus | BYTE
SS2Klima6IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[6].IzhodniVentilator
SS2Klima6IzhodniVentStatus | INT | IOD_SS2 | SS2:.Klima[6].IzhodniVentStatus | BYTE
SS2Klima6Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[6].Kompresor1
SS2Klima6Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[6].Kompresor2
SS2Klima6KompresorStatus | INT | IOD_SS2 | SS2:.Klima[6].KompresorStatus | BYTE
SS2Klima6NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[6].NacinRazvlaz
SS2Klima6NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[6].NastMaxTemp
SS2Klima6NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[6].NastMaxVlaznost
SS2Klima6NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[6].NastMinTemp
SS2Klima6NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[6].NastMinVlaznost
SS2Klima6NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[6].NastTempProstora
SS2Klima6NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[6].NastVlaznost
SS2Klima6ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[6].ObratUreFilter
SS2Klima6ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[6].ObratUreKompresor1
SS2Klima6ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[6].ObratUreKompresor2
SS2Klima6ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[6].ObratUreVent
SS2Klima6Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[6].Razvlazevanje
SS2Klima6SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[6].SenzorjiStatus
SS2Klima6TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[6].TemperaturaProstora
SS2Klima6VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[6].VentilGretjeOdpiranje
SS2Klima6VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[6].VentilGretjeZapiranje
SS2Klima6Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[6].Vlazenje
SS2Klima6VlazilecStatus | INT | IOD_SS2 | SS2:.Klima[6].VlazilecStatus | BYTE
SS2Klima6VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[6].VlaznostProstora
SS2KlimaError1AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].AlarmKompresor1
SS2KlimaError1AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].AlarmKompresor2
SS2KlimaError1FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].FenThermalCutout
SS2KlimaError1IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].IzlivVode
SS2KlimaError1Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].Kompresor1naMejiStevilaObrUr
SS2KlimaError1Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].Kompresor2naMejiStevilaObrUr
SS2KlimaError1NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NapakaPriPretokuVode
SS2KlimaError1NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NapakaPriPretokuZraka
SS2KlimaError1NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NapakaSenzorVlaznosti
SS2KlimaError1NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NapakaTSTemperaturaProstora
SS2KlimaError1NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NapakaVlazilca
SS2KlimaError1NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NizekPritiskKompresor1
SS2KlimaError1NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NizekPritiskKompresor2
SS2KlimaError1NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NizkaTempVProstoru
SS2KlimaError1NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NizkaVlaznost
SS2KlimaError1PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].PozarniAlarm
SS2KlimaError1ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].ThermalCutoutHeater1
SS2KlimaError1ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].ThermalCutoutHeater2
SS2KlimaError1VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].VentilatorNaMejiStevilaObrUr
SS2KlimaError1VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].VisokaTempVProstoru
SS2KlimaError1VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].VisokaVlaznost
SS2KlimaError1VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].VisokPritiskKompresor1
SS2KlimaError1VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].VisokPritiskKompresor2
SS2KlimaError1ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].ZamasenFilter
SS2KlimaError1ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].ZunanjiAlarm
SS2KlimaError2AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].AlarmKompresor1
SS2KlimaError2AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].AlarmKompresor2
SS2KlimaError2FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].FenThermalCutout
SS2KlimaError2IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].IzlivVode
SS2KlimaError2Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].Kompresor1naMejiStevilaObrUr
SS2KlimaError2Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].Kompresor2naMejiStevilaObrUr
SS2KlimaError2NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NapakaPriPretokuVode
SS2KlimaError2NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NapakaPriPretokuZraka
SS2KlimaError2NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NapakaSenzorVlaznosti
SS2KlimaError2NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NapakaTSTemperaturaProstora
SS2KlimaError2NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NapakaVlazilca
SS2KlimaError2NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NizekPritiskKompresor1
SS2KlimaError2NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NizekPritiskKompresor2
SS2KlimaError2NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NizkaTempVProstoru
SS2KlimaError2NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NizkaVlaznost
SS2KlimaError2PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].PozarniAlarm
SS2KlimaError2ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].ThermalCutoutHeater1
SS2KlimaError2ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].ThermalCutoutHeater2
SS2KlimaError2VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].VentilatorNaMejiStevilaObrUr
SS2KlimaError2VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].VisokaTempVProstoru
SS2KlimaError2VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].VisokaVlaznost
SS2KlimaError2VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].VisokPritiskKompresor1
SS2KlimaError2VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].VisokPritiskKompresor2
SS2KlimaError2ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].ZamasenFilter
SS2KlimaError2ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].ZunanjiAlarm
SS2KlimaError3AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].AlarmKompresor1
SS2KlimaError3AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].AlarmKompresor2
SS2KlimaError3FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].FenThermalCutout
SS2KlimaError3IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].IzlivVode
SS2KlimaError3Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].Kompresor1naMejiStevilaObrUr
SS2KlimaError3Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].Kompresor2naMejiStevilaObrUr
SS2KlimaError3NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NapakaPriPretokuVode
SS2KlimaError3NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NapakaPriPretokuZraka
SS2KlimaError3NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NapakaSenzorVlaznosti
SS2KlimaError3NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NapakaTSTemperaturaProstora
SS2KlimaError3NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NapakaVlazilca
SS2KlimaError3NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NizekPritiskKompresor1
SS2KlimaError3NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NizekPritiskKompresor2
SS2KlimaError3NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NizkaTempVProstoru
SS2KlimaError3NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NizkaVlaznost
SS2KlimaError3PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].PozarniAlarm
SS2KlimaError3ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].ThermalCutoutHeater1
SS2KlimaError3ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].ThermalCutoutHeater2
SS2KlimaError3VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].VentilatorNaMejiStevilaObrUr
SS2KlimaError3VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].VisokaTempVProstoru
SS2KlimaError3VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].VisokaVlaznost
SS2KlimaError3VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].VisokPritiskKompresor1
SS2KlimaError3VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].VisokPritiskKompresor2
SS2KlimaError3ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].ZamasenFilter
SS2KlimaError3ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].ZunanjiAlarm
SS2KlimaError4AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].AlarmKompresor1
SS2KlimaError4AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].AlarmKompresor2
SS2KlimaError4FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].FenThermalCutout
SS2KlimaError4IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].IzlivVode
SS2KlimaError4Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].Kompresor1naMejiStevilaObrUr
SS2KlimaError4Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].Kompresor2naMejiStevilaObrUr
SS2KlimaError4NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NapakaPriPretokuVode
SS2KlimaError4NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NapakaPriPretokuZraka
SS2KlimaError4NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NapakaSenzorVlaznosti
SS2KlimaError4NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NapakaTSTemperaturaProstora
SS2KlimaError4NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NapakaVlazilca
SS2KlimaError4NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NizekPritiskKompresor1
SS2KlimaError4NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NizekPritiskKompresor2
SS2KlimaError4NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NizkaTempVProstoru
SS2KlimaError4NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NizkaVlaznost
SS2KlimaError4PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].PozarniAlarm
SS2KlimaError4ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].ThermalCutoutHeater1
SS2KlimaError4ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].ThermalCutoutHeater2
SS2KlimaError4VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].VentilatorNaMejiStevilaObrUr
SS2KlimaError4VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].VisokaTempVProstoru
SS2KlimaError4VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].VisokaVlaznost
SS2KlimaError4VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].VisokPritiskKompresor1
SS2KlimaError4VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].VisokPritiskKompresor2
SS2KlimaError4ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].ZamasenFilter
SS2KlimaError4ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].ZunanjiAlarm
SS2KlimaError5AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].AlarmKompresor1
SS2KlimaError5AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].AlarmKompresor2
SS2KlimaError5FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].FenThermalCutout
SS2KlimaError5IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].IzlivVode
SS2KlimaError5Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].Kompresor1naMejiStevilaObrUr
SS2KlimaError5Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].Kompresor2naMejiStevilaObrUr
SS2KlimaError5NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NapakaPriPretokuVode
SS2KlimaError5NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NapakaPriPretokuZraka
SS2KlimaError5NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NapakaSenzorVlaznosti
SS2KlimaError5NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NapakaTSTemperaturaProstora
SS2KlimaError5NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NapakaVlazilca
SS2KlimaError5NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NizekPritiskKompresor1
SS2KlimaError5NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NizekPritiskKompresor2
SS2KlimaError5NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NizkaTempVProstoru
SS2KlimaError5NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NizkaVlaznost
SS2KlimaError5PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].PozarniAlarm
SS2KlimaError5ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].ThermalCutoutHeater1
SS2KlimaError5ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].ThermalCutoutHeater2
SS2KlimaError5VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].VentilatorNaMejiStevilaObrUr
SS2KlimaError5VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].VisokaTempVProstoru
SS2KlimaError5VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].VisokaVlaznost
SS2KlimaError5VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].VisokPritiskKompresor1
SS2KlimaError5VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].VisokPritiskKompresor2
SS2KlimaError5ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].ZamasenFilter
SS2KlimaError5ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].ZunanjiAlarm
SS2KlimaError6AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].AlarmKompresor1
SS2KlimaError6AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].AlarmKompresor2
SS2KlimaError6FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].FenThermalCutout
SS2KlimaError6IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].IzlivVode
SS2KlimaError6Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].Kompresor1naMejiStevilaObrUr
SS2KlimaError6Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].Kompresor2naMejiStevilaObrUr
SS2KlimaError6NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NapakaPriPretokuVode
SS2KlimaError6NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NapakaPriPretokuZraka
SS2KlimaError6NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NapakaSenzorVlaznosti
SS2KlimaError6NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NapakaTSTemperaturaProstora
SS2KlimaError6NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NapakaVlazilca
SS2KlimaError6NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NizekPritiskKompresor1
SS2KlimaError6NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NizekPritiskKompresor2
SS2KlimaError6NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NizkaTempVProstoru
SS2KlimaError6NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NizkaVlaznost
SS2KlimaError6PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].PozarniAlarm
SS2KlimaError6ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].ThermalCutoutHeater1
SS2KlimaError6ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].ThermalCutoutHeater2
SS2KlimaError6VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].VentilatorNaMejiStevilaObrUr
SS2KlimaError6VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].VisokaTempVProstoru
SS2KlimaError6VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].VisokaVlaznost
SS2KlimaError6VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].VisokPritiskKompresor1
SS2KlimaError6VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].VisokPritiskKompresor2
SS2KlimaError6ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].ZamasenFilter
SS2KlimaError6ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].ZunanjiAlarm
SS2NacDeloKlima1_2Avtom | DIGITAL | IOD_SS2 | SS2:.NacDeloKlima1_2Avtom
SS2NacDeloKlima3_4Avtom | DIGITAL | IOD_SS2 | SS2:.NacDeloKlima3_4Avtom
SS2NacDeloKlima5_6Avtom | DIGITAL | IOD_SS2 | SS2:.NacDeloKlima5_6Avtom
SS2NapakaSenzorTemp1 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp1
SS2NapakaSenzorTemp2 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp2
SS2NapakaSenzorTemp3 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp3
SS2NapakaSenzorTemp4 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp4
SS2NapakaSenzorVlaga1 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga1
SS2NapakaSenzorVlaga2 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga2
SS2NapakaSenzorVlaga3 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga3
SS2NapakaSenzorVlaga4 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga4
SS2NastaviCasNaKrmilniku | DIGITAL | IOD_SS2 | SS2:.NastaviCasNaKrmilniku
SS2NastavitevUreKrUspesna | DIGITAL | IOD_SS2 | SS2:.NastavitevUreKrUspesna
SS2OpozoriloBaterijaPLC | DIGITAL | IOD_SS2 | SS2:.OpozoriloBaterijaPLC
SS2OpozoriloPMM2x17med60in8010 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[10]
SS2OpozoriloPMM2x17med60in8011 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[11]
SS2OpozoriloPMM2x17med60in8012 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[12]
SS2OpozoriloPMM2x17med60in8013 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[13]
SS2OpozoriloPMM2x17med60in8014 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[14]
SS2OpozoriloPMM2x17med60in8015 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[15]
SS2OpozoriloPMM2x17med60in8016 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[16]
SS2OpozoriloPMM2x17med60in8017 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[17]
SS2OpozoriloPMM2x17med60in8018 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[18]
SS2OpozoriloPMM2x17med60in8019 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[19]
SS2OpozoriloPMM2x17med60in801 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[1]
SS2OpozoriloPMM2x17med60in8020 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[20]
SS2OpozoriloPMM2x17med60in8021 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[21]
SS2OpozoriloPMM2x17med60in8022 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[22]
SS2OpozoriloPMM2x17med60in8023 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[23]
SS2OpozoriloPMM2x17med60in8024 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[24]
SS2OpozoriloPMM2x17med60in8025 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[25]
SS2OpozoriloPMM2x17med60in8026 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[26]
SS2OpozoriloPMM2x17med60in8027 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[27]
SS2OpozoriloPMM2x17med60in8028 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[28]
SS2OpozoriloPMM2x17med60in8029 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[29]
SS2OpozoriloPMM2x17med60in802 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[2]
SS2OpozoriloPMM2x17med60in8030 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[30]
SS2OpozoriloPMM2x17med60in8031 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[31]
SS2OpozoriloPMM2x17med60in8032 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[32]
SS2OpozoriloPMM2x17med60in8033 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[33]
SS2OpozoriloPMM2x17med60in8034 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[34]
SS2OpozoriloPMM2x17med60in8035 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[35]
SS2OpozoriloPMM2x17med60in8036 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[36]
SS2OpozoriloPMM2x17med60in8037 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[37]
SS2OpozoriloPMM2x17med60in8038 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[38]
SS2OpozoriloPMM2x17med60in8039 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[39]
SS2OpozoriloPMM2x17med60in803 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[3]
SS2OpozoriloPMM2x17med60in8040 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[40]
SS2OpozoriloPMM2x17med60in8041 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[41]
SS2OpozoriloPMM2x17med60in8042 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[42]
SS2OpozoriloPMM2x17med60in804 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[4]
SS2OpozoriloPMM2x17med60in805 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[5]
SS2OpozoriloPMM2x17med60in806 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[6]
SS2OpozoriloPMM2x17med60in807 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[7]
SS2OpozoriloPMM2x17med60in808 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[8]
SS2OpozoriloPMM2x17med60in809 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[9]
SS2OznakeFaz10 | INT | IOD_SS2 | SS2:.OznakeFaz[10] | BYTE
SS2OznakeFaz11 | INT | IOD_SS2 | SS2:.OznakeFaz[11] | BYTE
SS2OznakeFaz12 | INT | IOD_SS2 | SS2:.OznakeFaz[12] | BYTE
SS2OznakeFaz13 | INT | IOD_SS2 | SS2:.OznakeFaz[13] | BYTE
SS2OznakeFaz14 | INT | IOD_SS2 | SS2:.OznakeFaz[14] | BYTE
SS2OznakeFaz1 | INT | IOD_SS2 | SS2:.OznakeFaz[1] | BYTE
SS2OznakeFaz2 | INT | IOD_SS2 | SS2:.OznakeFaz[2] | BYTE
SS2OznakeFaz3 | INT | IOD_SS2 | SS2:.OznakeFaz[3] | BYTE
SS2OznakeFaz4 | INT | IOD_SS2 | SS2:.OznakeFaz[4] | BYTE
SS2OznakeFaz5 | INT | IOD_SS2 | SS2:.OznakeFaz[5] | BYTE
SS2OznakeFaz6 | INT | IOD_SS2 | SS2:.OznakeFaz[6] | BYTE
SS2OznakeFaz7 | INT | IOD_SS2 | SS2:.OznakeFaz[7] | BYTE
SS2OznakeFaz8 | INT | IOD_SS2 | SS2:.OznakeFaz[8] | BYTE
SS2OznakeFaz9 | INT | IOD_SS2 | SS2:.OznakeFaz[9] | BYTE
SS2PhaseBool0 | DIGITAL | IOD_SS2 | SS2:.PhaseBool[0]
SS2PhaseBool1 | DIGITAL | IOD_SS2 | SS2:.PhaseBool[1]
SS2PhaseBool2 | DIGITAL | IOD_SS2 | SS2:.PhaseBool[2]
SS2PhaseNext | DIGITAL | IOD_SS2 | SS2:.PhaseNext
SS2PhaseNo | INT | IOD_SS2 | SS2:.PhaseNo | BYTE
SS2PhasePrev | DIGITAL | IOD_SS2 | SS2:.PhasePrev
SS2PMM1OverCurrentBetw1 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentBetw[1]
SS2PMM1OverCurrentBetw2 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentBetw[2]
SS2PMM1OverCurrentBetw3 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentBetw[3]
SS2PMM1OverCurrentOver1 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentOver[1]
SS2PMM1OverCurrentOver2 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentOver[2]
SS2PMM1OverCurrentOver3 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentOver[3]
SS2PMM1OverVoltage | DIGITAL | IOD_SS2 | SS2:.PMM1OverVoltage
SS2PMM2OverCurrentBetw1 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentBetw[1]
SS2PMM2OverCurrentBetw2 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentBetw[2]
SS2PMM2OverCurrentBetw3 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentBetw[3]
SS2PMM2OverCurrentOver1 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentOver[1]
SS2PMM2OverCurrentOver2 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentOver[2]
SS2PMM2OverCurrentOver3 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentOver[3]
SS2PMM2OverVoltage | DIGITAL | IOD_SS2 | SS2:.PMM2OverVoltage
SS2PMM2x17 | DIGITAL | IOD_SS2 | SS2:.PMM2x17
SS2PMM1ActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMM[1].ActiveEnergyConsumed_kWh
SS2PMM1ActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMM[1].ActivePowerPhaseA_kW
SS2PMM1ActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMM[1].ActivePowerPhaseB_kW
SS2PMM1ActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMM[1].ActivePowerPhaseC_kW
SS2PMM1AlarmPhase1C01_16_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C01_16_60to80 | BYTE
SS2PMM1AlarmPhase1C01_16_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C01_16_over80 | BYTE
SS2PMM1AlarmPhase1C17_32_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C17_32_60to80 | BYTE
SS2PMM1AlarmPhase1C17_32_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C17_32_over80 | BYTE
SS2PMM1AlarmPhase1C33_42_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C33_42_60to80 | BYTE
SS2PMM1AlarmPhase1C33_42_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C33_42_over80 | BYTE
SS2PMM1AlarmPhase1GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].GlobalAlarmReg
SS2PMM1AlarmPhase2C01_16_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C01_16_60to80 | BYTE
SS2PMM1AlarmPhase2C01_16_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C01_16_over80 | BYTE
SS2PMM1AlarmPhase2C17_32_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C17_32_60to80 | BYTE
SS2PMM1AlarmPhase2C17_32_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C17_32_over80 | BYTE
SS2PMM1AlarmPhase2C33_42_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C33_42_60to80 | BYTE
SS2PMM1AlarmPhase2C33_42_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C33_42_over80 | BYTE
SS2PMM1AlarmPhase2GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].GlobalAlarmReg
SS2PMM1AlarmPhase3C01_16_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C01_16_60to80 | BYTE
SS2PMM1AlarmPhase3C01_16_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C01_16_over80 | BYTE
SS2PMM1AlarmPhase3C17_32_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C17_32_60to80 | BYTE
SS2PMM1AlarmPhase3C17_32_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C17_32_over80 | BYTE
SS2PMM1AlarmPhase3C33_42_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C33_42_60to80 | BYTE
SS2PMM1AlarmPhase3C33_42_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C33_42_over80 | BYTE
SS2PMM1AlarmPhase3GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].GlobalAlarmReg
SS2PMM1AparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[1].AparentPowerPhaseA
SS2PMM1AparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[1].AparentPowerPhaseB
SS2PMM1AparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[1].AparentPowerPhaseC
SS2PMM1AverageCurrent_A | REAL | IOD_SS2 | SS2:.PMM[1].AverageCurrent_A
SS2PMM1AveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMM[1].AveragePhaseToNeutral_V
SS2PMM1AveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMM[1].AveragePhaseToPhase_V
SS2PMM1CurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMM[1].CurrentInPhaseA_A
SS2PMM1CurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMM[1].CurrentInPhaseB_A
SS2PMM1CurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMM[1].CurrentInPhaseC_A
SS2PMM1Frequency_Hz | REAL | IOD_SS2 | SS2:.PMM[1].Frequency_Hz
SS2PMM1Phase1Current10 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[10]
SS2PMM1Phase1Current11 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[11]
SS2PMM1Phase1Current12 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[12]
SS2PMM1Phase1Current13 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[13]
SS2PMM1Phase1Current14 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[14]
SS2PMM1Phase1Current15 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[15]
SS2PMM1Phase1Current16 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[16]
SS2PMM1Phase1Current17 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[17]
SS2PMM1Phase1Current18 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[18]
SS2PMM1Phase1Current19 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[19]
SS2PMM1Phase1Current1 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[1]
SS2PMM1Phase1Current20 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[20]
SS2PMM1Phase1Current21 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[21]
SS2PMM1Phase1Current22 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[22]
SS2PMM1Phase1Current23 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[23]
SS2PMM1Phase1Current24 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[24]
SS2PMM1Phase1Current25 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[25]
SS2PMM1Phase1Current26 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[26]
SS2PMM1Phase1Current27 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[27]
SS2PMM1Phase1Current28 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[28]
SS2PMM1Phase1Current29 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[29]
SS2PMM1Phase1Current2 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[2]
SS2PMM1Phase1Current30 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[30]
SS2PMM1Phase1Current31 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[31]
SS2PMM1Phase1Current32 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[32]
SS2PMM1Phase1Current33 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[33]
SS2PMM1Phase1Current34 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[34]
SS2PMM1Phase1Current35 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[35]
SS2PMM1Phase1Current36 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[36]
SS2PMM1Phase1Current37 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[37]
SS2PMM1Phase1Current38 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[38]
SS2PMM1Phase1Current39 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[39]
SS2PMM1Phase1Current3 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[3]
SS2PMM1Phase1Current40 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[40]
SS2PMM1Phase1Current41 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[41]
SS2PMM1Phase1Current42 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[42]
SS2PMM1Phase1Current4 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[4]
SS2PMM1Phase1Current5 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[5]
SS2PMM1Phase1Current6 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[6]
SS2PMM1Phase1Current7 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[7]
SS2PMM1Phase1Current8 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[8]
SS2PMM1Phase1Current9 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[9]
SS2PMM1Phase2Current10 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[10]
SS2PMM1Phase2Current11 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[11]
SS2PMM1Phase2Current12 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[12]
SS2PMM1Phase2Current13 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[13]
SS2PMM1Phase2Current14 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[14]
SS2PMM1Phase2Current15 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[15]
SS2PMM1Phase2Current16 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[16]
SS2PMM1Phase2Current17 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[17]
SS2PMM1Phase2Current18 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[18]
SS2PMM1Phase2Current19 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[19]
SS2PMM1Phase2Current1 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[1]
SS2PMM1Phase2Current20 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[20]
SS2PMM1Phase2Current21 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[21]
SS2PMM1Phase2Current22 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[22]
SS2PMM1Phase2Current23 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[23]
SS2PMM1Phase2Current24 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[24]
SS2PMM1Phase2Current25 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[25]
SS2PMM1Phase2Current26 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[26]
SS2PMM1Phase2Current27 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[27]
SS2PMM1Phase2Current28 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[28]
SS2PMM1Phase2Current29 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[29]
SS2PMM1Phase2Current2 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[2]
SS2PMM1Phase2Current30 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[30]
SS2PMM1Phase2Current31 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[31]
SS2PMM1Phase2Current32 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[32]
SS2PMM1Phase2Current33 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[33]
SS2PMM1Phase2Current34 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[34]
SS2PMM1Phase2Current35 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[35]
SS2PMM1Phase2Current36 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[36]
SS2PMM1Phase2Current37 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[37]
SS2PMM1Phase2Current38 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[38]
SS2PMM1Phase2Current39 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[39]
SS2PMM1Phase2Current3 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[3]
SS2PMM1Phase2Current40 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[40]
SS2PMM1Phase2Current41 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[41]
SS2PMM1Phase2Current42 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[42]
SS2PMM1Phase2Current4 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[4]
SS2PMM1Phase2Current5 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[5]
SS2PMM1Phase2Current6 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[6]
SS2PMM1Phase2Current7 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[7]
SS2PMM1Phase2Current8 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[8]
SS2PMM1Phase2Current9 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[9]
SS2PMM1Phase3Current10 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[10]
SS2PMM1Phase3Current11 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[11]
SS2PMM1Phase3Current12 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[12]
SS2PMM1Phase3Current13 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[13]
SS2PMM1Phase3Current14 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[14]
SS2PMM1Phase3Current15 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[15]
SS2PMM1Phase3Current16 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[16]
SS2PMM1Phase3Current17 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[17]
SS2PMM1Phase3Current18 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[18]
SS2PMM1Phase3Current19 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[19]
SS2PMM1Phase3Current1 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[1]
SS2PMM1Phase3Current20 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[20]
SS2PMM1Phase3Current21 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[21]
SS2PMM1Phase3Current22 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[22]
SS2PMM1Phase3Current23 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[23]
SS2PMM1Phase3Current24 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[24]
SS2PMM1Phase3Current25 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[25]
SS2PMM1Phase3Current26 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[26]
SS2PMM1Phase3Current27 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[27]
SS2PMM1Phase3Current28 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[28]
SS2PMM1Phase3Current29 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[29]
SS2PMM1Phase3Current2 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[2]
SS2PMM1Phase3Current30 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[30]
SS2PMM1Phase3Current31 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[31]
SS2PMM1Phase3Current32 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[32]
SS2PMM1Phase3Current33 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[33]
SS2PMM1Phase3Current34 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[34]
SS2PMM1Phase3Current35 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[35]
SS2PMM1Phase3Current36 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[36]
SS2PMM1Phase3Current37 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[37]
SS2PMM1Phase3Current38 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[38]
SS2PMM1Phase3Current39 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[39]
SS2PMM1Phase3Current3 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[3]
SS2PMM1Phase3Current40 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[40]
SS2PMM1Phase3Current41 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[41]
SS2PMM1Phase3Current42 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[42]
SS2PMM1Phase3Current4 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[4]
SS2PMM1Phase3Current5 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[5]
SS2PMM1Phase3Current6 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[6]
SS2PMM1Phase3Current7 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[7]
SS2PMM1Phase3Current8 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[8]
SS2PMM1Phase3Current9 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[9]
SS2PMM1PowerFactorSys | REAL | IOD_SS2 | SS2:.PMM[1].PowerFactorSys
SS2PMM1ReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMM[1].ReactiveEnergyConsumed_kVARh
SS2PMM1ReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[1].ReactivePowerPhaseA
SS2PMM1ReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[1].ReactivePowerPhaseB
SS2PMM1ReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[1].ReactivePowerPhaseC
SS2PMM1TotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMM[1].TotalActivePower_kW
SS2PMM1TotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMM[1].TotalAparentPower_kVA
SS2PMM1TotalPowerFactor | REAL | IOD_SS2 | SS2:.PMM[1].TotalPowerFactor
SS2PMM1TotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMM[1].TotalReactivePower_kVAR
SS2PMM1VirA_fsys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_fsys
SS2PMM1VirA_Isys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_Isys
SS2PMM1VirA_PFsys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_PFsys
SS2PMM1VirA_Psys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_Psys
SS2PMM1VirA_Qsys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_Qsys
SS2PMM1VirA_Ssys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_Ssys
SS2PMM1VirA_Usys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_Usys
SS2PMM1VirB_fsys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_fsys
SS2PMM1VirB_Isys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_Isys
SS2PMM1VirB_PFsys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_PFsys
SS2PMM1VirB_Psys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_Psys
SS2PMM1VirB_Qsys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_Qsys
SS2PMM1VirB_Ssys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_Ssys
SS2PMM1VirB_Usys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_Usys
SS2PMM1VirBActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMM[1].VirBActiveEnergyConsumed_kWh
SS2PMM1VirBActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMM[1].VirBActivePowerPhaseA_kW
SS2PMM1VirBActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMM[1].VirBActivePowerPhaseB_kW
SS2PMM1VirBActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMM[1].VirBActivePowerPhaseC_kW
SS2PMM1VirBAparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[1].VirBAparentPowerPhaseA
SS2PMM1VirBAparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[1].VirBAparentPowerPhaseB
SS2PMM1VirBAparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[1].VirBAparentPowerPhaseC
SS2PMM1VirBAverageCurrent_A | REAL | IOD_SS2 | SS2:.PMM[1].VirBAverageCurrent_A
SS2PMM1VirBAveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBAveragePhaseToNeutral_V
SS2PMM1VirBAveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBAveragePhaseToPhase_V
SS2PMM1VirBCurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMM[1].VirBCurrentInPhaseA_A
SS2PMM1VirBCurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMM[1].VirBCurrentInPhaseB_A
SS2PMM1VirBCurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMM[1].VirBCurrentInPhaseC_A
SS2PMM1VirBFrequency_Hz | REAL | IOD_SS2 | SS2:.PMM[1].VirBFrequency_Hz
SS2PMM1VirBPowerFactorSys | REAL | IOD_SS2 | SS2:.PMM[1].VirBPowerFactorSys
SS2PMM1VirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMM[1].VirBReactiveEnergyConsumed_kVARh
SS2PMM1VirBReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[1].VirBReactivePowerPhaseA
SS2PMM1VirBReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[1].VirBReactivePowerPhaseB
SS2PMM1VirBReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[1].VirBReactivePowerPhaseC
SS2PMM1VirBTotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMM[1].VirBTotalActivePower_kW
SS2PMM1VirBTotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMM[1].VirBTotalAparentPower_kVA
SS2PMM1VirBTotalPowerFactor | REAL | IOD_SS2 | SS2:.PMM[1].VirBTotalPowerFactor
SS2PMM1VirBTotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMM[1].VirBTotalReactivePower_kVAR
SS2PMM1VirBVoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseAB_V
SS2PMM1VirBVoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseAN_V
SS2PMM1VirBVoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseBC_V
SS2PMM1VirBVoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseBN_V
SS2PMM1VirBVoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseCA_V
SS2PMM1VirBVoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseCN_V
SS2PMM1VoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseAB_V
SS2PMM1VoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseAN_V
SS2PMM1VoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseBC_V
SS2PMM1VoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseBN_V
SS2PMM1VoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseCA_V
SS2PMM1VoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseCN_V
SS2PMM2ActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMM[2].ActiveEnergyConsumed_kWh
SS2PMM2ActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMM[2].ActivePowerPhaseA_kW
SS2PMM2ActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMM[2].ActivePowerPhaseB_kW
SS2PMM2ActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMM[2].ActivePowerPhaseC_kW
SS2PMM2AlarmPhase1C01_16_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C01_16_60to80 | BYTE
SS2PMM2AlarmPhase1C01_16_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C01_16_over80 | BYTE
SS2PMM2AlarmPhase1C17_32_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C17_32_60to80 | BYTE
SS2PMM2AlarmPhase1C17_32_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C17_32_over80 | BYTE
SS2PMM2AlarmPhase1C33_42_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C33_42_60to80 | BYTE
SS2PMM2AlarmPhase1C33_42_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C33_42_over80 | BYTE
SS2PMM2AlarmPhase1GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].GlobalAlarmReg
SS2PMM2AlarmPhase2C01_16_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C01_16_60to80 | BYTE
SS2PMM2AlarmPhase2C01_16_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C01_16_over80 | BYTE
SS2PMM2AlarmPhase2C17_32_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C17_32_60to80 | BYTE
SS2PMM2AlarmPhase2C17_32_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C17_32_over80 | BYTE
SS2PMM2AlarmPhase2C33_42_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C33_42_60to80 | BYTE
SS2PMM2AlarmPhase2C33_42_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C33_42_over80 | BYTE
SS2PMM2AlarmPhase2GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].GlobalAlarmReg
SS2PMM2AlarmPhase3C01_16_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C01_16_60to80 | BYTE
SS2PMM2AlarmPhase3C01_16_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C01_16_over80 | BYTE
SS2PMM2AlarmPhase3C17_32_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C17_32_60to80 | BYTE
SS2PMM2AlarmPhase3C17_32_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C17_32_over80 | BYTE
SS2PMM2AlarmPhase3C33_42_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C33_42_60to80 | BYTE
SS2PMM2AlarmPhase3C33_42_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C33_42_over80 | BYTE
SS2PMM2AlarmPhase3GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].GlobalAlarmReg
SS2PMM2AparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[2].AparentPowerPhaseA
SS2PMM2AparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[2].AparentPowerPhaseB
SS2PMM2AparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[2].AparentPowerPhaseC
SS2PMM2AverageCurrent_A | REAL | IOD_SS2 | SS2:.PMM[2].AverageCurrent_A
SS2PMM2AveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMM[2].AveragePhaseToNeutral_V
SS2PMM2AveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMM[2].AveragePhaseToPhase_V
SS2PMM2CurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMM[2].CurrentInPhaseA_A
SS2PMM2CurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMM[2].CurrentInPhaseB_A
SS2PMM2CurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMM[2].CurrentInPhaseC_A
SS2PMM2Frequency_Hz | REAL | IOD_SS2 | SS2:.PMM[2].Frequency_Hz
SS2PMM2Phase1Current1 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[1]
SS2PMM2Phase1Current2 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[2]
SS2PMM2Phase1Current3 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[3]
SS2PMM2Phase1Current4 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[4]
SS2PMM2Phase1Current5 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[5]
SS2PMM2Phase1Current6 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[6]
SS2PMM2Phase1Current7 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[7]
SS2PMM2Phase1Current8 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[8]
SS2PMM2Phase1Current9 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[9]
SS2PMM2Phase1Current10 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[10]
SS2PMM2Phase1Current11 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[11]
SS2PMM2Phase1Current12 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[12]
SS2PMM2Phase1Current13 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[13]
SS2PMM2Phase1Current14 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[14]
SS2PMM2Phase1Current15 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[15]
SS2PMM2Phase1Current16 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[16]
SS2PMM2Phase1Current17 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[17]
SS2PMM2Phase1Current18 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[18]
SS2PMM2Phase1Current19 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[19]
SS2PMM2Phase1Current20 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[20]
SS2PMM2Phase1Current21 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[21]
SS2PMM2Phase1Current22 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[22]
SS2PMM2Phase1Current23 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[23]
SS2PMM2Phase1Current24 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[24]
SS2PMM2Phase1Current25 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[25]
SS2PMM2Phase1Current26 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[26]
SS2PMM2Phase1Current27 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[27]
SS2PMM2Phase1Current28 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[28]
SS2PMM2Phase1Current29 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[29]
SS2PMM2Phase1Current30 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[30]
SS2PMM2Phase1Current31 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[31]
SS2PMM2Phase1Current32 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[32]
SS2PMM2Phase1Current33 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[33]
SS2PMM2Phase1Current34 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[34]
SS2PMM2Phase1Current35 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[35]
SS2PMM2Phase1Current36 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[36]
SS2PMM2Phase1Current37 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[37]
SS2PMM2Phase1Current38 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[38]
SS2PMM2Phase1Current39 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[39]
SS2PMM2Phase1Current40 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[40]
SS2PMM2Phase1Current41 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[41]
SS2PMM2Phase1Current42 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[42]
SS2PMM2Phase2Current10 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[10]
SS2PMM2Phase2Current11 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[11]
SS2PMM2Phase2Current12 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[12]
SS2PMM2Phase2Current13 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[13]
SS2PMM2Phase2Current14 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[14]
SS2PMM2Phase2Current15 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[15]
SS2PMM2Phase2Current16 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[16]
SS2PMM2Phase2Current17 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[17]
SS2PMM2Phase2Current18 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[18]
SS2PMM2Phase2Current19 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[19]
SS2PMM2Phase2Current1 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[1]
SS2PMM2Phase2Current20 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[20]
SS2PMM2Phase2Current21 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[21]
SS2PMM2Phase2Current22 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[22]
SS2PMM2Phase2Current23 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[23]
SS2PMM2Phase2Current24 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[24]
SS2PMM2Phase2Current25 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[25]
SS2PMM2Phase2Current26 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[26]
SS2PMM2Phase2Current27 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[27]
SS2PMM2Phase2Current28 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[28]
SS2PMM2Phase2Current29 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[29]
SS2PMM2Phase2Current2 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[2]
SS2PMM2Phase2Current30 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[30]
SS2PMM2Phase2Current31 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[31]
SS2PMM2Phase2Current32 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[32]
SS2PMM2Phase2Current33 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[33]
SS2PMM2Phase2Current34 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[34]
SS2PMM2Phase2Current35 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[35]
SS2PMM2Phase2Current36 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[36]
SS2PMM2Phase2Current37 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[37]
SS2PMM2Phase2Current38 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[38]
SS2PMM2Phase2Current39 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[39]
SS2PMM2Phase2Current3 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[3]
SS2PMM2Phase2Current40 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[40]
SS2PMM2Phase2Current41 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[41]
SS2PMM2Phase2Current42 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[42]
SS2PMM2Phase2Current4 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[4]
SS2PMM2Phase2Current5 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[5]
SS2PMM2Phase2Current6 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[6]
SS2PMM2Phase2Current7 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[7]
SS2PMM2Phase2Current8 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[8]
SS2PMM2Phase2Current9 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[9]
SS2PMM2Phase3Current10 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[10]
SS2PMM2Phase3Current11 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[11]
SS2PMM2Phase3Current12 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[12]
SS2PMM2Phase3Current13 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[13]
SS2PMM2Phase3Current14 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[14]
SS2PMM2Phase3Current15 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[15]
SS2PMM2Phase3Current16 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[16]
SS2PMM2Phase3Current17 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[17]
SS2PMM2Phase3Current18 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[18]
SS2PMM2Phase3Current19 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[19]
SS2PMM2Phase3Current1 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[1]
SS2PMM2Phase3Current20 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[20]
SS2PMM2Phase3Current21 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[21]
SS2PMM2Phase3Current22 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[22]
SS2PMM2Phase3Current23 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[23]
SS2PMM2Phase3Current24 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[24]
SS2PMM2Phase3Current25 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[25]
SS2PMM2Phase3Current26 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[26]
SS2PMM2Phase3Current27 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[27]
SS2PMM2Phase3Current28 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[28]
SS2PMM2Phase3Current29 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[29]
SS2PMM2Phase3Current2 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[2]
SS2PMM2Phase3Current30 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[30]
SS2PMM2Phase3Current31 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[31]
SS2PMM2Phase3Current32 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[32]
SS2PMM2Phase3Current33 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[33]
SS2PMM2Phase3Current34 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[34]
SS2PMM2Phase3Current35 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[35]
SS2PMM2Phase3Current36 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[36]
SS2PMM2Phase3Current37 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[37]
SS2PMM2Phase3Current38 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[38]
SS2PMM2Phase3Current39 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[39]
SS2PMM2Phase3Current3 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[3]
SS2PMM2Phase3Current40 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[40]
SS2PMM2Phase3Current41 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[41]
SS2PMM2Phase3Current42 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[42]
SS2PMM2Phase3Current4 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[4]
SS2PMM2Phase3Current5 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[5]
SS2PMM2Phase3Current6 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[6]
SS2PMM2Phase3Current7 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[7]
SS2PMM2Phase3Current8 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[8]
SS2PMM2Phase3Current9 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[9]
SS2PMM2PowerFactorSys | REAL | IOD_SS2 | SS2:.PMM[2].PowerFactorSys
SS2PMM2ReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMM[2].ReactiveEnergyConsumed_kVARh
SS2PMM2ReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[2].ReactivePowerPhaseA
SS2PMM2ReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[2].ReactivePowerPhaseB
SS2PMM2ReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[2].ReactivePowerPhaseC
SS2PMM2TotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMM[2].TotalActivePower_kW
SS2PMM2TotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMM[2].TotalAparentPower_kVA
SS2PMM2TotalPowerFactor | REAL | IOD_SS2 | SS2:.PMM[2].TotalPowerFactor
SS2PMM2TotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMM[2].TotalReactivePower_kVAR
SS2PMM2VirA_fsys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_fsys
SS2PMM2VirA_Isys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_Isys
SS2PMM2VirA_PFsys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_PFsys
SS2PMM2VirA_Psys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_Psys
SS2PMM2VirA_Qsys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_Qsys
SS2PMM2VirA_Ssys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_Ssys
SS2PMM2VirA_Usys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_Usys
SS2PMM2VirB_fsys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_fsys
SS2PMM2VirB_Isys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_Isys
SS2PMM2VirB_PFsys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_PFsys
SS2PMM2VirB_Psys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_Psys
SS2PMM2VirB_Qsys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_Qsys
SS2PMM2VirB_Ssys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_Ssys
SS2PMM2VirB_Usys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_Usys
SS2PMM2VirBActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMM[2].VirBActiveEnergyConsumed_kWh
SS2PMM2VirBActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMM[2].VirBActivePowerPhaseA_kW
SS2PMM2VirBActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMM[2].VirBActivePowerPhaseB_kW
SS2PMM2VirBActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMM[2].VirBActivePowerPhaseC_kW
SS2PMM2VirBAparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[2].VirBAparentPowerPhaseA
SS2PMM2VirBAparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[2].VirBAparentPowerPhaseB
SS2PMM2VirBAparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[2].VirBAparentPowerPhaseC
SS2PMM2VirBAverageCurrent_A | REAL | IOD_SS2 | SS2:.PMM[2].VirBAverageCurrent_A
SS2PMM2VirBAveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBAveragePhaseToNeutral_V
SS2PMM2VirBAveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBAveragePhaseToPhase_V
SS2PMM2VirBCurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMM[2].VirBCurrentInPhaseA_A
SS2PMM2VirBCurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMM[2].VirBCurrentInPhaseB_A
SS2PMM2VirBCurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMM[2].VirBCurrentInPhaseC_A
SS2PMM2VirBFrequency_Hz | REAL | IOD_SS2 | SS2:.PMM[2].VirBFrequency_Hz
SS2PMM2VirBPowerFactorSys | REAL | IOD_SS2 | SS2:.PMM[2].VirBPowerFactorSys
SS2PMM2VirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMM[2].VirBReactiveEnergyConsumed_kVARh
SS2PMM2VirBReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[2].VirBReactivePowerPhaseA
SS2PMM2VirBReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[2].VirBReactivePowerPhaseB
SS2PMM2VirBReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[2].VirBReactivePowerPhaseC
SS2PMM2VirBTotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMM[2].VirBTotalActivePower_kW
SS2PMM2VirBTotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMM[2].VirBTotalAparentPower_kVA
SS2PMM2VirBTotalPowerFactor | REAL | IOD_SS2 | SS2:.PMM[2].VirBTotalPowerFactor
SS2PMM2VirBTotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMM[2].VirBTotalReactivePower_kVAR
SS2PMM2VirBVoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseAB_V
SS2PMM2VirBVoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseAN_V
SS2PMM2VirBVoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseBC_V
SS2PMM2VirBVoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseBN_V
SS2PMM2VirBVoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseCA_V
SS2PMM2VirBVoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseCN_V
SS2PMM2VoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseAB_V
SS2PMM2VoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseAN_V
SS2PMM2VoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseBC_V
SS2PMM2VoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseBN_V
SS2PMM2VoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseCA_V
SS2PMM2VoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseCN_V
SS2PMMPanelActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMMPanel.ActiveEnergyConsumed_kWh
SS2PMMPanelActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMMPanel.ActivePowerPhaseA_kW
SS2PMMPanelActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMMPanel.ActivePowerPhaseB_kW
SS2PMMPanelActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMMPanel.ActivePowerPhaseC_kW
SS2PMMPanelAlarmPhase1C01_16_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C01_16_60to80 | BYTE
SS2PMMPanelAlarmPhase1C01_16_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C01_16_over80 | BYTE
SS2PMMPanelAlarmPhase1C17_32_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C17_32_60to80 | BYTE
SS2PMMPanelAlarmPhase1C17_32_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C17_32_over80 | BYTE
SS2PMMPanelAlarmPhase1C33_42_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C33_42_60to80 | BYTE
SS2PMMPanelAlarmPhase1C33_42_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C33_42_over80 | BYTE
SS2PMMPanelAlarmPhase1GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].GlobalAlarmReg
SS2PMMPanelAlarmPhase2C01_16_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C01_16_60to80 | BYTE
SS2PMMPanelAlarmPhase2C01_16_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C01_16_over80 | BYTE
SS2PMMPanelAlarmPhase2C17_32_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C17_32_60to80 | BYTE
SS2PMMPanelAlarmPhase2C17_32_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C17_32_over80 | BYTE
SS2PMMPanelAlarmPhase2C33_42_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C33_42_60to80 | BYTE
SS2PMMPanelAlarmPhase2C33_42_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C33_42_over80 | BYTE
SS2PMMPanelAlarmPhase2GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].GlobalAlarmReg
SS2PMMPanelAlarmPhase3C01_16_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C01_16_60to80 | BYTE
SS2PMMPanelAlarmPhase3C01_16_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C01_16_over80 | BYTE
SS2PMMPanelAlarmPhase3C17_32_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C17_32_60to80 | BYTE
SS2PMMPanelAlarmPhase3C17_32_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C17_32_over80 | BYTE
SS2PMMPanelAlarmPhase3C33_42_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C33_42_60to80 | BYTE
SS2PMMPanelAlarmPhase3C33_42_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C33_42_over80 | BYTE
SS2PMMPanelAlarmPhase3GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].GlobalAlarmReg
SS2PMMPanelAparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMMPanel.AparentPowerPhaseA
SS2PMMPanelAparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMMPanel.AparentPowerPhaseB
SS2PMMPanelAparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMMPanel.AparentPowerPhaseC
SS2PMMPanelAverageCurrent_A | REAL | IOD_SS2 | SS2:.PMMPanel.AverageCurrent_A
SS2PMMPanelAveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMMPanel.AveragePhaseToNeutral_V
SS2PMMPanelAveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMMPanel.AveragePhaseToPhase_V
SS2PMMPanelCurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMMPanel.CurrentInPhaseA_A
SS2PMMPanelCurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMMPanel.CurrentInPhaseB_A
SS2PMMPanelCurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMMPanel.CurrentInPhaseC_A
SS2PMMPanelFrequency_Hz | REAL | IOD_SS2 | SS2:.PMMPanel.Frequency_Hz
SS2PMMPanelPowerFactorSys | REAL | IOD_SS2 | SS2:.PMMPanel.PowerFactorSys
SS2PMMPanelReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMMPanel.ReactiveEnergyConsumed_kVARh
SS2PMMPanelReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMMPanel.ReactivePowerPhaseA
SS2PMMPanelReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMMPanel.ReactivePowerPhaseB
SS2PMMPanelReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMMPanel.ReactivePowerPhaseC
SS2PMMPanelTotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMMPanel.TotalActivePower_kW
SS2PMMPanelTotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMMPanel.TotalAparentPower_kVA
SS2PMMPanelTotalPowerFactor | REAL | IOD_SS2 | SS2:.PMMPanel.TotalPowerFactor
SS2PMMPanelTotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMMPanel.TotalReactivePower_kVAR
SS2PMMPanelVirA_fsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_fsys
SS2PMMPanelVirA_Isys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_Isys
SS2PMMPanelVirA_PFsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_PFsys
SS2PMMPanelVirA_Psys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_Psys
SS2PMMPanelVirA_Qsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_Qsys
SS2PMMPanelVirA_Ssys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_Ssys
SS2PMMPanelVirA_Usys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_Usys
SS2PMMPanelVirB_fsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_fsys
SS2PMMPanelVirB_Isys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_Isys
SS2PMMPanelVirB_PFsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_PFsys
SS2PMMPanelVirB_Psys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_Psys
SS2PMMPanelVirB_Qsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_Qsys
SS2PMMPanelVirB_Ssys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_Ssys
SS2PMMPanelVirB_Usys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_Usys
SS2PMMPanelVirBActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMMPanel.VirBActiveEnergyConsumed_kWh
SS2PMMPanelVirBActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMMPanel.VirBActivePowerPhaseA_kW
SS2PMMPanelVirBActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMMPanel.VirBActivePowerPhaseB_kW
SS2PMMPanelVirBActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMMPanel.VirBActivePowerPhaseC_kW
SS2PMMPanelVirBAparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAparentPowerPhaseA
SS2PMMPanelVirBAparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAparentPowerPhaseB
SS2PMMPanelVirBAparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAparentPowerPhaseC
SS2PMMPanelVirBAverageCurrent_A | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAverageCurrent_A
SS2PMMPanelVirBAveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAveragePhaseToNeutral_V
SS2PMMPanelVirBAveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAveragePhaseToPhase_V
SS2PMMPanelVirBCurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMMPanel.VirBCurrentInPhaseA_A
SS2PMMPanelVirBCurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMMPanel.VirBCurrentInPhaseB_A
SS2PMMPanelVirBCurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMMPanel.VirBCurrentInPhaseC_A
SS2PMMPanelVirBFrequency_Hz | REAL | IOD_SS2 | SS2:.PMMPanel.VirBFrequency_Hz
SS2PMMPanelVirBPowerFactorSys | REAL | IOD_SS2 | SS2:.PMMPanel.VirBPowerFactorSys
SS2PMMPanelVirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMMPanel.VirBReactiveEnergyConsumed_kVARh
SS2PMMPanelVirBReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMMPanel.VirBReactivePowerPhaseA
SS2PMMPanelVirBReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMMPanel.VirBReactivePowerPhaseB
SS2PMMPanelVirBReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMMPanel.VirBReactivePowerPhaseC
SS2PMMPanelVirBTotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMMPanel.VirBTotalActivePower_kW
SS2PMMPanelVirBTotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMMPanel.VirBTotalAparentPower_kVA
SS2PMMPanelVirBTotalPowerFactor | REAL | IOD_SS2 | SS2:.PMMPanel.VirBTotalPowerFactor
SS2PMMPanelVirBTotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMMPanel.VirBTotalReactivePower_kVAR
SS2PMMPanelVirBVoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseAB_V
SS2PMMPanelVirBVoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseAN_V
SS2PMMPanelVirBVoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseBC_V
SS2PMMPanelVirBVoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseBN_V
SS2PMMPanelVirBVoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseCA_V
SS2PMMPanelVirBVoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseCN_V
SS2PMMPanelVoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseAB_V
SS2PMMPanelVoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseAN_V
SS2PMMPanelVoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseBC_V
SS2PMMPanelVoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseBN_V
SS2PMMPanelVoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseCA_V
SS2PMMPanelVoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseCN_V
SS2RocniVklopKlima1 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima1
SS2RocniVklopKlima2 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima2
SS2RocniVklopKlima3 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima3
SS2RocniVklopKlima4 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima4
SS2RocniVklopKlima5 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima5
SS2RocniVklopKlima6 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima6
SS2SinhronizacijaPanelOK | DIGITAL | IOD_SS2 | SS2:.SinhronizacijaPanelOK
SS2SinhronizirajCas_Panel | DIGITAL | IOD_SS2 | SS2:.SinhronizirajCas_Panel
SS2SKTemp1 | REAL | IOD_SS2 | SS2:.SKTemp1
SS2SKTemp2 | REAL | IOD_SS2 | SS2:.SKTemp2
SS2SKTemp3 | REAL | IOD_SS2 | SS2:.SKTemp3
SS2SKTemp4 | REAL | IOD_SS2 | SS2:.SKTemp4
SS2SkupneNapakeNaprav_Klima1 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima1
SS2SkupneNapakeNaprav_Klima2 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima2
SS2SkupneNapakeNaprav_Klima3 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima3
SS2SkupneNapakeNaprav_Klima4 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima4
SS2SkupneNapakeNaprav_Klima5 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima5
SS2SkupneNapakeNaprav_Klima6 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima6
SS2SkupneNapakeNaprav_Komunikacija | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Komunikacija
SS2SkupneNapakeNaprav_PMM17VirBVirA | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_PMM17VirBVirA
SS2SkupneNapakeNaprav_PMM63VirBVirA | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_PMM63VirBVirA
SS2SkupneNapakeNaprav_TempVlaga | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_TempVlaga
SS2SKVlaga1 | REAL | IOD_SS2 | SS2:.SKVlaga1
SS2SKVlaga2 | REAL | IOD_SS2 | SS2:.SKVlaga2
SS2SKVlaga3 | REAL | IOD_SS2 | SS2:.SKVlaga3
SS2SKVlaga4 | REAL | IOD_SS2 | SS2:.SKVlaga4
SS2StanjeKlimat2_1_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_1_Delovanje
SS2StanjeKlimat2_2_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_2_Delovanje
SS2StanjeKlimat2_3_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_3_Delovanje
SS2StanjeKlimat2_4_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_4_Delovanje
SS2StanjeKlimat2_5_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_5_Delovanje
SS2StanjeKlimat2_6_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_6_Delovanje
SS2StanjeUPSKrmOmara_BaterijskiNacin | DIGITAL | IOD_SS2 | SS2:.StanjeUPSKrmOmara_BaterijskiNacin
SS2StanjeUPSKrmOmara_Polnjenje | DIGITAL | IOD_SS2 | SS2:.StanjeUPSKrmOmara_Polnjenje
SS2StUrZaPreklopKlim1_2 | INT | IOD_SS2 | SS2:.StUrZaPreklopKlim1_2
SS2StUrZaPreklopKlim3_4 | INT | IOD_SS2 | SS2:.StUrZaPreklopKlim3_4
SS2StUrZaPreklopKlim5_6 | INT | IOD_SS2 | SS2:.StUrZaPreklopKlim5_6
SS2TempZaAlarm1_2 | REAL | IOD_SS2 | SS2:.TempZaAlarm1_2
SS2TempZaAlarm3_4 | REAL | IOD_SS2 | SS2:.TempZaAlarm3_4
SS2TempZaAlarm5_6 | REAL | IOD_SS2 | SS2:.TempZaAlarm5_6
SS2TempZaAlarmTIA1 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA1
SS2TempZaAlarmTIA2 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA2
SS2TempZaAlarmTIA3 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA3
SS2TempZaAlarmTIA4 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA4
SS2TempZaVklopObehKlim1_2 | REAL | IOD_SS2 | SS2:.TempZaVklopObehKlim1_2
SS2TempZaVklopObehKlim3_4 | REAL | IOD_SS2 | SS2:.TempZaVklopObehKlim3_4
SS2TempZaVklopObehKlim3_4TIA3 | REAL | IOD_SS2 | SS2:.TempZaVklopObehKlim3_4TIA3
SS2TempZaVklopObehKlim5_6 | REAL | IOD_SS2 | SS2:.TempZaVklopObehKlim5_6
SS2TempZaVklopObehKlim5_6TIA3 | REAL | IOD_SS2 | SS2:.TempZaVklopObehKlim5_6TIA3
SS2UPSstatus_Prikaz_PanelSCADA | INT | IOD_SS2 | SS2:.UPSstatus_Prikaz_PanelSCADA | BYTE
SS2UserCurrentLevel | INT | IOD_SS2 | SS2:.UserCurrentLevel | BYTE
SS2UserLoggedIn | DIGITAL | IOD_SS2 | SS2:.UserLoggedIn
SS2UserName | STRING | IOD_SS2 | SS2:.UserName
SS2XVH_AlarmOn | DIGITAL | IOD_SS2 | SS2:.XVH_AlarmOn
SS2Klimat2_1_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_1_Vklop
SS2Klimat2_2_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_2_Vklop
SS2Klimat2_3_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_3_Vklop
SS2Klimat2_4_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_4_Vklop
SS2Klimat2_5_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_5_Vklop
SS2Klimat2_6_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_6_Vklop
SS2ErrorComKlima1Code0 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[0] | BYTE
SS2ErrorComKlima1Code10 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[10] | BYTE
SS2ErrorComKlima1Code11 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[11] | BYTE
SS2ErrorComKlima1Code12 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[12] | BYTE
SS2ErrorComKlima1Code13 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[13] | BYTE
SS2ErrorComKlima1Code14 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[14] | BYTE
SS2ErrorComKlima1Code15 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[15] | BYTE
SS2ErrorComKlima1Code1 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[1] | BYTE
SS2ErrorComKlima1Code2 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[2] | BYTE
SS2ErrorComKlima1Code3 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[3] | BYTE
SS2ErrorComKlima1Code4 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[4] | BYTE
SS2ErrorComKlima1Code5 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[5] | BYTE
SS2ErrorComKlima1Code6 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[6] | BYTE
SS2ErrorComKlima1Code7 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[7] | BYTE
SS2ErrorComKlima1Code8 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[8] | BYTE
SS2ErrorComKlima1Code9 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[9] | BYTE
SS2ErrorComKlima2Code0 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[0] | BYTE
SS2ErrorComKlima2Code10 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[10] | BYTE
SS2ErrorComKlima2Code11 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[11] | BYTE
SS2ErrorComKlima2Code12 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[12] | BYTE
SS2ErrorComKlima2Code13 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[13] | BYTE
SS2ErrorComKlima2Code14 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[14] | BYTE
SS2ErrorComKlima2Code15 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[15] | BYTE
SS2ErrorComKlima2Code1 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[1] | BYTE
SS2ErrorComKlima2Code2 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[2] | BYTE
SS2ErrorComKlima2Code3 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[3] | BYTE
SS2ErrorComKlima2Code4 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[4] | BYTE
SS2ErrorComKlima2Code5 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[5] | BYTE
SS2ErrorComKlima2Code6 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[6] | BYTE
SS2ErrorComKlima2Code7 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[7] | BYTE
SS2ErrorComKlima2Code8 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[8] | BYTE
SS2ErrorComKlima2Code9 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[9] | BYTE
SS2ErrorComKlima3Code0 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[0] | BYTE
SS2ErrorComKlima3Code10 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[10] | BYTE
SS2ErrorComKlima3Code11 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[11] | BYTE
SS2ErrorComKlima3Code12 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[12] | BYTE
SS2ErrorComKlima3Code13 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[13] | BYTE
SS2ErrorComKlima3Code14 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[14] | BYTE
SS2ErrorComKlima3Code15 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[15] | BYTE
SS2ErrorComKlima3Code1 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[1] | BYTE
SS2ErrorComKlima3Code2 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[2] | BYTE
SS2ErrorComKlima3Code3 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[3] | BYTE
SS2ErrorComKlima3Code4 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[4] | BYTE
SS2ErrorComKlima3Code5 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[5] | BYTE
SS2ErrorComKlima3Code6 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[6] | BYTE
SS2ErrorComKlima3Code7 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[7] | BYTE
SS2ErrorComKlima3Code8 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[8] | BYTE
SS2ErrorComKlima3Code9 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[9] | BYTE
SS2ErrorComKlima4Code0 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[0] | BYTE
SS2ErrorComKlima4Code10 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[10] | BYTE
SS2ErrorComKlima4Code11 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[11] | BYTE
SS2ErrorComKlima4Code12 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[12] | BYTE
SS2ErrorComKlima4Code13 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[13] | BYTE
SS2ErrorComKlima4Code14 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[14] | BYTE
SS2ErrorComKlima4Code15 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[15] | BYTE
SS2ErrorComKlima4Code1 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[1] | BYTE
SS2ErrorComKlima4Code2 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[2] | BYTE
SS2ErrorComKlima4Code3 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[3] | BYTE
SS2ErrorComKlima4Code4 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[4] | BYTE
SS2ErrorComKlima4Code5 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[5] | BYTE
SS2ErrorComKlima4Code6 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[6] | BYTE
SS2ErrorComKlima4Code7 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[7] | BYTE
SS2ErrorComKlima4Code8 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[8] | BYTE
SS2ErrorComKlima4Code9 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[9] | BYTE
SS2ErrorComKlima5Code0 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[0] | BYTE
SS2ErrorComKlima5Code10 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[10] | BYTE
SS2ErrorComKlima5Code11 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[11] | BYTE
SS2ErrorComKlima5Code12 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[12] | BYTE
SS2ErrorComKlima5Code13 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[13] | BYTE
SS2ErrorComKlima5Code14 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[14] | BYTE
SS2ErrorComKlima5Code15 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[15] | BYTE
SS2ErrorComKlima5Code1 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[1] | BYTE
SS2ErrorComKlima5Code2 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[2] | BYTE
SS2ErrorComKlima5Code3 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[3] | BYTE
SS2ErrorComKlima5Code4 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[4] | BYTE
SS2ErrorComKlima5Code5 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[5] | BYTE
SS2ErrorComKlima5Code6 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[6] | BYTE
SS2ErrorComKlima5Code7 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[7] | BYTE
SS2ErrorComKlima5Code8 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[8] | BYTE
SS2ErrorComKlima5Code9 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[9] | BYTE
SS2ErrorComKlima6Code0 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[0] | BYTE
SS2ErrorComKlima6Code10 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[10] | BYTE
SS2ErrorComKlima6Code11 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[11] | BYTE
SS2ErrorComKlima6Code12 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[12] | BYTE
SS2ErrorComKlima6Code13 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[13] | BYTE
SS2ErrorComKlima6Code14 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[14] | BYTE
SS2ErrorComKlima6Code15 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[15] | BYTE
SS2ErrorComKlima6Code1 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[1] | BYTE
SS2ErrorComKlima6Code2 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[2] | BYTE
SS2ErrorComKlima6Code3 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[3] | BYTE
SS2ErrorComKlima6Code4 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[4] | BYTE
SS2ErrorComKlima6Code5 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[5] | BYTE
SS2ErrorComKlima6Code6 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[6] | BYTE
SS2ErrorComKlima6Code7 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[7] | BYTE
SS2ErrorComKlima6Code8 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[8] | BYTE
SS2ErrorComKlima6Code9 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[9] | BYTE
SS2ErrorComPMM1Code0 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[0] | BYTE
SS2ErrorComPMM1Code10 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[10] | BYTE
SS2ErrorComPMM1Code11 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[11] | BYTE
SS2ErrorComPMM1Code12 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[12] | BYTE
SS2ErrorComPMM1Code13 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[13] | BYTE
SS2ErrorComPMM1Code14 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[14] | BYTE
SS2ErrorComPMM1Code15 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[15] | BYTE
SS2ErrorComPMM1Code1 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[1] | BYTE
SS2ErrorComPMM1Code2 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[2] | BYTE
SS2ErrorComPMM1Code3 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[3] | BYTE
SS2ErrorComPMM1Code4 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[4] | BYTE
SS2ErrorComPMM1Code5 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[5] | BYTE
SS2ErrorComPMM1Code6 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[6] | BYTE
SS2ErrorComPMM1Code7 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[7] | BYTE
SS2ErrorComPMM1Code8 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[8] | BYTE
SS2ErrorComPMM1Code9 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[9] | BYTE
SS2ErrorComPMM2Code0 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[0] | BYTE
SS2ErrorComPMM2Code10 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[10] | BYTE
SS2ErrorComPMM2Code11 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[11] | BYTE
SS2ErrorComPMM2Code12 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[12] | BYTE
SS2ErrorComPMM2Code13 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[13] | BYTE
SS2ErrorComPMM2Code14 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[14] | BYTE
SS2ErrorComPMM2Code15 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[15] | BYTE
SS2ErrorComPMM2Code1 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[1] | BYTE
SS2ErrorComPMM2Code2 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[2] | BYTE
SS2ErrorComPMM2Code3 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[3] | BYTE
SS2ErrorComPMM2Code4 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[4] | BYTE
SS2ErrorComPMM2Code5 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[5] | BYTE
SS2ErrorComPMM2Code6 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[6] | BYTE
SS2ErrorComPMM2Code7 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[7] | BYTE
SS2ErrorComPMM2Code8 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[8] | BYTE
SS2ErrorComPMM2Code9 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[9] | BYTE
SS2ErrCommScada2 | DIGITAL | IOD_SS2 | SS2:.ErrCommScada2
SS2ComSCADA2 | DIGITAL | IOD_SS2 | SS2:.ComSCADA2
SS2ComSCADA3 | DIGITAL | IOD_SS2 | SS2:.ComSCADA3
SS2kom_nast_cas_izpada | INT | IOD_SS2 | SS2:.kom_nast_cas_izpada
SS2AlarmSKTemp5_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp5_Previsoka
SS2AlarmSKTemp6_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp6_Previsoka
SS2AlarmTempTIA5Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA5Previsoka
SS2AlarmTempTIA6Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA6Previsoka
SS2NapakaSenzorTemp5 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp5
SS2NapakaSenzorTemp6 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp6
SS2NapakaSenzorVlaga5 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga5
SS2NapakaSenzorVlaga6 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga6
SS2SKTemp5 | REAL | IOD_SS2 | SS2:.SKTemp5
SS2SKTemp6 | REAL | IOD_SS2 | SS2:.SKTemp6
SS2SKVlaga5 | REAL | IOD_SS2 | SS2:.SKVlaga5
SS2SKVlaga6 | REAL | IOD_SS2 | SS2:.SKVlaga6
SS2TempZaAlarmTIA5 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA5
SS2TempZaAlarmTIA6 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA6
SS2SKTempServSoba1Povpr | REAL | IOD_SS2 | SS2:.SKTempServSoba1Povpr
SS2SKTempServSoba2Povpr | REAL | IOD_SS2 | SS2:.SKTempServSoba2Povpr
SS2TempZaAlarmTIA235 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA235
SS2TempZaAlarmTIA46 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA46
SS2AlarmTempTIA235Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA235Previsoka
SS2AlarmTempTIA46Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA46Previsoka

## variable_2
SS2AlarmKlimat2_1_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_1_Napaka
SS2AlarmKlimat2_2_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_2_Napaka
SS2AlarmKlimat2_3_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_3_Napaka
SS2AlarmKlimat2_4_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_4_Napaka
SS2AlarmKlimat2_5_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_5_Napaka
SS2AlarmKlimat2_6_Napaka | DIGITAL | IOD_SS2 | SS2:.AlarmKlimat2_6_Napaka
SS2AlarmLAH1RazlitjeVode | DIGITAL | IOD_SS2 | SS2:.AlarmLAH1RazlitjeVode
SS2AlarmLAH2RazlitjeVode | DIGITAL | IOD_SS2 | SS2:.AlarmLAH2RazlitjeVode
SS2AlarmLAH3RazlitjeVode | DIGITAL | IOD_SS2 | SS2:.AlarmLAH3RazlitjeVode
SS2AlarmPMM2x17nad8010 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[10]
SS2AlarmPMM2x17nad8011 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[11]
SS2AlarmPMM2x17nad8012 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[12]
SS2AlarmPMM2x17nad8013 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[13]
SS2AlarmPMM2x17nad8014 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[14]
SS2AlarmPMM2x17nad8015 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[15]
SS2AlarmPMM2x17nad8016 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[16]
SS2AlarmPMM2x17nad8017 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[17]
SS2AlarmPMM2x17nad8018 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[18]
SS2AlarmPMM2x17nad8019 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[19]
SS2AlarmPMM2x17nad801 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[1]
SS2AlarmPMM2x17nad8020 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[20]
SS2AlarmPMM2x17nad8021 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[21]
SS2AlarmPMM2x17nad8022 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[22]
SS2AlarmPMM2x17nad8023 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[23]
SS2AlarmPMM2x17nad8024 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[24]
SS2AlarmPMM2x17nad8025 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[25]
SS2AlarmPMM2x17nad8026 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[26]
SS2AlarmPMM2x17nad8027 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[27]
SS2AlarmPMM2x17nad8028 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[28]
SS2AlarmPMM2x17nad8029 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[29]
SS2AlarmPMM2x17nad802 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[2]
SS2AlarmPMM2x17nad8030 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[30]
SS2AlarmPMM2x17nad8031 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[31]
SS2AlarmPMM2x17nad8032 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[32]
SS2AlarmPMM2x17nad8033 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[33]
SS2AlarmPMM2x17nad8034 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[34]
SS2AlarmPMM2x17nad8035 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[35]
SS2AlarmPMM2x17nad8036 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[36]
SS2AlarmPMM2x17nad8037 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[37]
SS2AlarmPMM2x17nad8038 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[38]
SS2AlarmPMM2x17nad8039 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[39]
SS2AlarmPMM2x17nad803 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[3]
SS2AlarmPMM2x17nad8040 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[40]
SS2AlarmPMM2x17nad8041 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[41]
SS2AlarmPMM2x17nad8042 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[42]
SS2AlarmPMM2x17nad804 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[4]
SS2AlarmPMM2x17nad805 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[5]
SS2AlarmPMM2x17nad806 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[6]
SS2AlarmPMM2x17nad807 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[7]
SS2AlarmPMM2x17nad808 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[8]
SS2AlarmPMM2x17nad809 | DIGITAL | IOD_SS2 | SS2:.AlarmPMM2x17nad80[9]
SS2AlarmSinhronizacijaNOK | DIGITAL | IOD_SS2 | SS2:.AlarmSinhronizacijaNOK
SS2AlarmSKTemp1_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp1_Previsoka
SS2AlarmSKTemp2_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp2_Previsoka
SS2AlarmSKTemp3_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp3_Previsoka
SS2AlarmSKTemp4_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp4_Previsoka
SS2AlarmTempTIA1Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA1Previsoka
SS2AlarmTempTIA2Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA2Previsoka
SS2AlarmTempTIA3Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA3Previsoka
SS2AlarmTempTIA4Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA4Previsoka
SS2AlarmUPSKrmOmara_Alarm | DIGITAL | IOD_SS2 | SS2:.AlarmUPSKrmOmara_Alarm
SS2ComSCADA | DIGITAL | IOD_SS2 | SS2:.ComSCADA
SS2ComSCADA1 | DIGITAL | IOD_SS2 | SS2:.ComSCADA1
SS2ErrComKlima1 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[1]
SS2ErrComKlima2 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[2]
SS2ErrComKlima3 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[3]
SS2ErrComKlima4 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[4]
SS2ErrComKlima5 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[5]
SS2ErrComKlima6 | DIGITAL | IOD_SS2 | SS2:.ErrComKlima[6]
SS2ErrCommScada | DIGITAL | IOD_SS2 | SS2:.ErrCommScada
SS2ErrComPanelPLC | DIGITAL | IOD_SS2 | SS2:.ErrComPanelPLC
SS2ErrComPMM1 | DIGITAL | IOD_SS2 | SS2:.ErrComPMM[1]
SS2ErrComPMM2 | DIGITAL | IOD_SS2 | SS2:.ErrComPMM[2]
SS2ErrComPort2 | DIGITAL | IOD_SS2 | SS2:.ErrComPort2
SS2ErrorComKlima1Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[1].Error
SS2ErrorComKlima2Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[2].Error
SS2ErrorComKlima3Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[3].Error
SS2ErrorComKlima4Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[4].Error
SS2ErrorComKlima5Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[5].Error
SS2ErrorComKlima6Error | DIGITAL | IOD_SS2 | SS2:.ErrorComKlima[6].Error
SS2ErrorComPMM1Error | DIGITAL | IOD_SS2 | SS2:.ErrorComPMM[1].Error
SS2ErrorComPMM2Error | DIGITAL | IOD_SS2 | SS2:.ErrorComPMM[2].Error
SS2Klima2_1_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_1_Onemogocena
SS2Klima2_2_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_2_Onemogocena
SS2Klima2_3_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_3_Onemogocena
SS2Klima2_4_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_4_Onemogocena
SS2Klima2_5_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_5_Onemogocena
SS2Klima2_6_Onemogocena | DIGITAL | IOD_SS2 | SS2:.Klima2_6_Onemogocena
SS2Klima1IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[1].IzhodniVentilator
SS2Klima1Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[1].Kompresor1
SS2Klima1Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[1].Kompresor2
SS2Klima1Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[1].Razvlazevanje
SS2Klima1SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[1].SenzorjiStatus
SS2Klima1VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[1].VentilGretjeOdpiranje
SS2Klima1VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[1].VentilGretjeZapiranje
SS2Klima1Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[1].Vlazenje
SS2Klima2IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[2].IzhodniVentilator
SS2Klima2Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[2].Kompresor1
SS2Klima2Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[2].Kompresor2
SS2Klima2Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[2].Razvlazevanje
SS2Klima2SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[2].SenzorjiStatus
SS2Klima2VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[2].VentilGretjeOdpiranje
SS2Klima2VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[2].VentilGretjeZapiranje
SS2Klima2Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[2].Vlazenje
SS2Klima3IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[3].IzhodniVentilator
SS2Klima3Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[3].Kompresor1
SS2Klima3Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[3].Kompresor2
SS2Klima3Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[3].Razvlazevanje
SS2Klima3SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[3].SenzorjiStatus
SS2Klima3VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[3].VentilGretjeOdpiranje
SS2Klima3VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[3].VentilGretjeZapiranje
SS2Klima3Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[3].Vlazenje
SS2Klima4IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[4].IzhodniVentilator
SS2Klima4Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[4].Kompresor1
SS2Klima4Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[4].Kompresor2
SS2Klima4Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[4].Razvlazevanje
SS2Klima4SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[4].SenzorjiStatus
SS2Klima4VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[4].VentilGretjeOdpiranje
SS2Klima4VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[4].VentilGretjeZapiranje
SS2Klima4Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[4].Vlazenje
SS2Klima5IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[5].IzhodniVentilator
SS2Klima5Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[5].Kompresor1
SS2Klima5Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[5].Kompresor2
SS2Klima5Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[5].Razvlazevanje
SS2Klima5SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[5].SenzorjiStatus
SS2Klima5VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[5].VentilGretjeOdpiranje
SS2Klima5VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[5].VentilGretjeZapiranje
SS2Klima5Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[5].Vlazenje
SS2Klima6IzhodniVentilator | DIGITAL | IOD_SS2 | SS2:.Klima[6].IzhodniVentilator
SS2Klima6Kompresor1 | DIGITAL | IOD_SS2 | SS2:.Klima[6].Kompresor1
SS2Klima6Kompresor2 | DIGITAL | IOD_SS2 | SS2:.Klima[6].Kompresor2
SS2Klima6Razvlazevanje | DIGITAL | IOD_SS2 | SS2:.Klima[6].Razvlazevanje
SS2Klima6SenzorjiStatus | DIGITAL | IOD_SS2 | SS2:.Klima[6].SenzorjiStatus
SS2Klima6VentilGretjeOdpiranje | DIGITAL | IOD_SS2 | SS2:.Klima[6].VentilGretjeOdpiranje
SS2Klima6VentilGretjeZapiranje | DIGITAL | IOD_SS2 | SS2:.Klima[6].VentilGretjeZapiranje
SS2Klima6Vlazenje | DIGITAL | IOD_SS2 | SS2:.Klima[6].Vlazenje
SS2KlimaError1AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].AlarmKompresor1
SS2KlimaError1AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].AlarmKompresor2
SS2KlimaError1FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].FenThermalCutout
SS2KlimaError1IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].IzlivVode
SS2KlimaError1Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].Kompresor1naMejiStevilaObrUr
SS2KlimaError1Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].Kompresor2naMejiStevilaObrUr
SS2KlimaError1NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NapakaPriPretokuVode
SS2KlimaError1NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NapakaPriPretokuZraka
SS2KlimaError1NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NapakaSenzorVlaznosti
SS2KlimaError1NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NapakaTSTemperaturaProstora
SS2KlimaError1NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NapakaVlazilca
SS2KlimaError1NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NizekPritiskKompresor1
SS2KlimaError1NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NizekPritiskKompresor2
SS2KlimaError1NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NizkaTempVProstoru
SS2KlimaError1NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].NizkaVlaznost
SS2KlimaError1PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].PozarniAlarm
SS2KlimaError1ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].ThermalCutoutHeater1
SS2KlimaError1ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].ThermalCutoutHeater2
SS2KlimaError1VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].VentilatorNaMejiStevilaObrUr
SS2KlimaError1VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].VisokaTempVProstoru
SS2KlimaError1VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].VisokaVlaznost
SS2KlimaError1VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].VisokPritiskKompresor1
SS2KlimaError1VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].VisokPritiskKompresor2
SS2KlimaError1ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].ZamasenFilter
SS2KlimaError1ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[1].ZunanjiAlarm
SS2KlimaError2AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].AlarmKompresor1
SS2KlimaError2AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].AlarmKompresor2
SS2KlimaError2FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].FenThermalCutout
SS2KlimaError2IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].IzlivVode
SS2KlimaError2Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].Kompresor1naMejiStevilaObrUr
SS2KlimaError2Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].Kompresor2naMejiStevilaObrUr
SS2KlimaError2NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NapakaPriPretokuVode
SS2KlimaError2NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NapakaPriPretokuZraka
SS2KlimaError2NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NapakaSenzorVlaznosti
SS2KlimaError2NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NapakaTSTemperaturaProstora
SS2KlimaError2NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NapakaVlazilca
SS2KlimaError2NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NizekPritiskKompresor1
SS2KlimaError2NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NizekPritiskKompresor2
SS2KlimaError2NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NizkaTempVProstoru
SS2KlimaError2NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].NizkaVlaznost
SS2KlimaError2PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].PozarniAlarm
SS2KlimaError2ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].ThermalCutoutHeater1
SS2KlimaError2ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].ThermalCutoutHeater2
SS2KlimaError2VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].VentilatorNaMejiStevilaObrUr
SS2KlimaError2VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].VisokaTempVProstoru
SS2KlimaError2VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].VisokaVlaznost
SS2KlimaError2VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].VisokPritiskKompresor1
SS2KlimaError2VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].VisokPritiskKompresor2
SS2KlimaError2ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].ZamasenFilter
SS2KlimaError2ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[2].ZunanjiAlarm
SS2KlimaError3AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].AlarmKompresor1
SS2KlimaError3AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].AlarmKompresor2
SS2KlimaError3FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].FenThermalCutout
SS2KlimaError3IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].IzlivVode
SS2KlimaError3Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].Kompresor1naMejiStevilaObrUr
SS2KlimaError3Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].Kompresor2naMejiStevilaObrUr
SS2KlimaError3NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NapakaPriPretokuVode
SS2KlimaError3NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NapakaPriPretokuZraka
SS2KlimaError3NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NapakaSenzorVlaznosti
SS2KlimaError3NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NapakaTSTemperaturaProstora
SS2KlimaError3NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NapakaVlazilca
SS2KlimaError3NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NizekPritiskKompresor1
SS2KlimaError3NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NizekPritiskKompresor2
SS2KlimaError3NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NizkaTempVProstoru
SS2KlimaError3NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].NizkaVlaznost
SS2KlimaError3PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].PozarniAlarm
SS2KlimaError3ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].ThermalCutoutHeater1
SS2KlimaError3ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].ThermalCutoutHeater2
SS2KlimaError3VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].VentilatorNaMejiStevilaObrUr
SS2KlimaError3VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].VisokaTempVProstoru
SS2KlimaError3VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].VisokaVlaznost
SS2KlimaError3VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].VisokPritiskKompresor1
SS2KlimaError3VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].VisokPritiskKompresor2
SS2KlimaError3ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].ZamasenFilter
SS2KlimaError3ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[3].ZunanjiAlarm
SS2KlimaError4AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].AlarmKompresor1
SS2KlimaError4AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].AlarmKompresor2
SS2KlimaError4FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].FenThermalCutout
SS2KlimaError4IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].IzlivVode
SS2KlimaError4Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].Kompresor1naMejiStevilaObrUr
SS2KlimaError4Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].Kompresor2naMejiStevilaObrUr
SS2KlimaError4NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NapakaPriPretokuVode
SS2KlimaError4NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NapakaPriPretokuZraka
SS2KlimaError4NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NapakaSenzorVlaznosti
SS2KlimaError4NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NapakaTSTemperaturaProstora
SS2KlimaError4NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NapakaVlazilca
SS2KlimaError4NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NizekPritiskKompresor1
SS2KlimaError4NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NizekPritiskKompresor2
SS2KlimaError4NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NizkaTempVProstoru
SS2KlimaError4NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].NizkaVlaznost
SS2KlimaError4PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].PozarniAlarm
SS2KlimaError4ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].ThermalCutoutHeater1
SS2KlimaError4ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].ThermalCutoutHeater2
SS2KlimaError4VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].VentilatorNaMejiStevilaObrUr
SS2KlimaError4VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].VisokaTempVProstoru
SS2KlimaError4VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].VisokaVlaznost
SS2KlimaError4VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].VisokPritiskKompresor1
SS2KlimaError4VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].VisokPritiskKompresor2
SS2KlimaError4ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].ZamasenFilter
SS2KlimaError4ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[4].ZunanjiAlarm
SS2KlimaError5AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].AlarmKompresor1
SS2KlimaError5AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].AlarmKompresor2
SS2KlimaError5FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].FenThermalCutout
SS2KlimaError5IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].IzlivVode
SS2KlimaError5Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].Kompresor1naMejiStevilaObrUr
SS2KlimaError5Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].Kompresor2naMejiStevilaObrUr
SS2KlimaError5NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NapakaPriPretokuVode
SS2KlimaError5NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NapakaPriPretokuZraka
SS2KlimaError5NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NapakaSenzorVlaznosti
SS2KlimaError5NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NapakaTSTemperaturaProstora
SS2KlimaError5NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NapakaVlazilca
SS2KlimaError5NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NizekPritiskKompresor1
SS2KlimaError5NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NizekPritiskKompresor2
SS2KlimaError5NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NizkaTempVProstoru
SS2KlimaError5NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].NizkaVlaznost
SS2KlimaError5PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].PozarniAlarm
SS2KlimaError5ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].ThermalCutoutHeater1
SS2KlimaError5ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].ThermalCutoutHeater2
SS2KlimaError5VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].VentilatorNaMejiStevilaObrUr
SS2KlimaError5VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].VisokaTempVProstoru
SS2KlimaError5VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].VisokaVlaznost
SS2KlimaError5VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].VisokPritiskKompresor1
SS2KlimaError5VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].VisokPritiskKompresor2
SS2KlimaError5ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].ZamasenFilter
SS2KlimaError5ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[5].ZunanjiAlarm
SS2KlimaError6AlarmKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].AlarmKompresor1
SS2KlimaError6AlarmKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].AlarmKompresor2
SS2KlimaError6FenThermalCutout | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].FenThermalCutout
SS2KlimaError6IzlivVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].IzlivVode
SS2KlimaError6Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].Kompresor1naMejiStevilaObrUr
SS2KlimaError6Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].Kompresor2naMejiStevilaObrUr
SS2KlimaError6NapakaPriPretokuVode | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NapakaPriPretokuVode
SS2KlimaError6NapakaPriPretokuZraka | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NapakaPriPretokuZraka
SS2KlimaError6NapakaSenzorVlaznosti | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NapakaSenzorVlaznosti
SS2KlimaError6NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NapakaTSTemperaturaProstora
SS2KlimaError6NapakaVlazilca | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NapakaVlazilca
SS2KlimaError6NizekPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NizekPritiskKompresor1
SS2KlimaError6NizekPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NizekPritiskKompresor2
SS2KlimaError6NizkaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NizkaTempVProstoru
SS2KlimaError6NizkaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].NizkaVlaznost
SS2KlimaError6PozarniAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].PozarniAlarm
SS2KlimaError6ThermalCutoutHeater1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].ThermalCutoutHeater1
SS2KlimaError6ThermalCutoutHeater2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].ThermalCutoutHeater2
SS2KlimaError6VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].VentilatorNaMejiStevilaObrUr
SS2KlimaError6VisokaTempVProstoru | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].VisokaTempVProstoru
SS2KlimaError6VisokaVlaznost | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].VisokaVlaznost
SS2KlimaError6VisokPritiskKompresor1 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].VisokPritiskKompresor1
SS2KlimaError6VisokPritiskKompresor2 | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].VisokPritiskKompresor2
SS2KlimaError6ZamasenFilter | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].ZamasenFilter
SS2KlimaError6ZunanjiAlarm | DIGITAL | IOD_SS2 | SS2:.KlimaError[6].ZunanjiAlarm
SS2NacDeloKlima1_2Avtom | DIGITAL | IOD_SS2 | SS2:.NacDeloKlima1_2Avtom
SS2NacDeloKlima3_4Avtom | DIGITAL | IOD_SS2 | SS2:.NacDeloKlima3_4Avtom
SS2NacDeloKlima5_6Avtom | DIGITAL | IOD_SS2 | SS2:.NacDeloKlima5_6Avtom
SS2NapakaSenzorTemp1 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp1
SS2NapakaSenzorTemp2 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp2
SS2NapakaSenzorTemp3 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp3
SS2NapakaSenzorTemp4 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp4
SS2NapakaSenzorVlaga1 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga1
SS2NapakaSenzorVlaga2 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga2
SS2NapakaSenzorVlaga3 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga3
SS2NapakaSenzorVlaga4 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga4
SS2NastaviCasNaKrmilniku | DIGITAL | IOD_SS2 | SS2:.NastaviCasNaKrmilniku
SS2NastavitevUreKrUspesna | DIGITAL | IOD_SS2 | SS2:.NastavitevUreKrUspesna
SS2OpozoriloBaterijaPLC | DIGITAL | IOD_SS2 | SS2:.OpozoriloBaterijaPLC
SS2OpozoriloPMM2x17med60in8010 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[10]
SS2OpozoriloPMM2x17med60in8011 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[11]
SS2OpozoriloPMM2x17med60in8012 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[12]
SS2OpozoriloPMM2x17med60in8013 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[13]
SS2OpozoriloPMM2x17med60in8014 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[14]
SS2OpozoriloPMM2x17med60in8015 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[15]
SS2OpozoriloPMM2x17med60in8016 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[16]
SS2OpozoriloPMM2x17med60in8017 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[17]
SS2OpozoriloPMM2x17med60in8018 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[18]
SS2OpozoriloPMM2x17med60in8019 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[19]
SS2OpozoriloPMM2x17med60in801 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[1]
SS2OpozoriloPMM2x17med60in8020 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[20]
SS2OpozoriloPMM2x17med60in8021 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[21]
SS2OpozoriloPMM2x17med60in8022 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[22]
SS2OpozoriloPMM2x17med60in8023 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[23]
SS2OpozoriloPMM2x17med60in8024 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[24]
SS2OpozoriloPMM2x17med60in8025 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[25]
SS2OpozoriloPMM2x17med60in8026 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[26]
SS2OpozoriloPMM2x17med60in8027 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[27]
SS2OpozoriloPMM2x17med60in8028 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[28]
SS2OpozoriloPMM2x17med60in8029 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[29]
SS2OpozoriloPMM2x17med60in802 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[2]
SS2OpozoriloPMM2x17med60in8030 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[30]
SS2OpozoriloPMM2x17med60in8031 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[31]
SS2OpozoriloPMM2x17med60in8032 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[32]
SS2OpozoriloPMM2x17med60in8033 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[33]
SS2OpozoriloPMM2x17med60in8034 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[34]
SS2OpozoriloPMM2x17med60in8035 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[35]
SS2OpozoriloPMM2x17med60in8036 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[36]
SS2OpozoriloPMM2x17med60in8037 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[37]
SS2OpozoriloPMM2x17med60in8038 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[38]
SS2OpozoriloPMM2x17med60in8039 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[39]
SS2OpozoriloPMM2x17med60in803 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[3]
SS2OpozoriloPMM2x17med60in8040 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[40]
SS2OpozoriloPMM2x17med60in8041 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[41]
SS2OpozoriloPMM2x17med60in8042 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[42]
SS2OpozoriloPMM2x17med60in804 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[4]
SS2OpozoriloPMM2x17med60in805 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[5]
SS2OpozoriloPMM2x17med60in806 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[6]
SS2OpozoriloPMM2x17med60in807 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[7]
SS2OpozoriloPMM2x17med60in808 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[8]
SS2OpozoriloPMM2x17med60in809 | DIGITAL | IOD_SS2 | SS2:.OpozoriloPMM2x17med60in80[9]
SS2PhaseBool0 | DIGITAL | IOD_SS2 | SS2:.PhaseBool[0]
SS2PhaseBool1 | DIGITAL | IOD_SS2 | SS2:.PhaseBool[1]
SS2PhaseBool2 | DIGITAL | IOD_SS2 | SS2:.PhaseBool[2]
SS2PhaseNext | DIGITAL | IOD_SS2 | SS2:.PhaseNext
SS2PhasePrev | DIGITAL | IOD_SS2 | SS2:.PhasePrev
SS2PMM1OverCurrentBetw1 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentBetw[1]
SS2PMM1OverCurrentBetw2 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentBetw[2]
SS2PMM1OverCurrentBetw3 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentBetw[3]
SS2PMM1OverCurrentOver1 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentOver[1]
SS2PMM1OverCurrentOver2 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentOver[2]
SS2PMM1OverCurrentOver3 | DIGITAL | IOD_SS2 | SS2:.PMM1OverCurrentOver[3]
SS2PMM1OverVoltage | DIGITAL | IOD_SS2 | SS2:.PMM1OverVoltage
SS2PMM2OverCurrentBetw1 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentBetw[1]
SS2PMM2OverCurrentBetw2 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentBetw[2]
SS2PMM2OverCurrentBetw3 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentBetw[3]
SS2PMM2OverCurrentOver1 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentOver[1]
SS2PMM2OverCurrentOver2 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentOver[2]
SS2PMM2OverCurrentOver3 | DIGITAL | IOD_SS2 | SS2:.PMM2OverCurrentOver[3]
SS2PMM2OverVoltage | DIGITAL | IOD_SS2 | SS2:.PMM2OverVoltage
SS2PMM2x17 | DIGITAL | IOD_SS2 | SS2:.PMM2x17
SS2RocniVklopKlima1 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima1
SS2RocniVklopKlima2 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima2
SS2RocniVklopKlima3 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima3
SS2RocniVklopKlima4 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima4
SS2RocniVklopKlima5 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima5
SS2RocniVklopKlima6 | DIGITAL | IOD_SS2 | SS2:.RocniVklopKlima6
SS2SinhronizacijaPanelOK | DIGITAL | IOD_SS2 | SS2:.SinhronizacijaPanelOK
SS2SinhronizirajCas_Panel | DIGITAL | IOD_SS2 | SS2:.SinhronizirajCas_Panel
SS2SkupneNapakeNaprav_Klima1 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima1
SS2SkupneNapakeNaprav_Klima2 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima2
SS2SkupneNapakeNaprav_Klima3 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima3
SS2SkupneNapakeNaprav_Klima4 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima4
SS2SkupneNapakeNaprav_Klima5 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima5
SS2SkupneNapakeNaprav_Klima6 | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Klima6
SS2SkupneNapakeNaprav_Komunikacija | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_Komunikacija
SS2SkupneNapakeNaprav_PMM17VirBVirA | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_PMM17VirBVirA
SS2SkupneNapakeNaprav_PMM63VirBVirA | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_PMM63VirBVirA
SS2SkupneNapakeNaprav_TempVlaga | DIGITAL | IOD_SS2 | SS2:.SkupneNapakeNaprav_TempVlaga
SS2StanjeKlimat2_1_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_1_Delovanje
SS2StanjeKlimat2_2_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_2_Delovanje
SS2StanjeKlimat2_3_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_3_Delovanje
SS2StanjeKlimat2_4_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_4_Delovanje
SS2StanjeKlimat2_5_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_5_Delovanje
SS2StanjeKlimat2_6_Delovanje | DIGITAL | IOD_SS2 | SS2:.StanjeKlimat2_6_Delovanje
SS2StanjeUPSKrmOmara_BaterijskiNacin | DIGITAL | IOD_SS2 | SS2:.StanjeUPSKrmOmara_BaterijskiNacin
SS2StanjeUPSKrmOmara_Polnjenje | DIGITAL | IOD_SS2 | SS2:.StanjeUPSKrmOmara_Polnjenje
SS2UserLoggedIn | DIGITAL | IOD_SS2 | SS2:.UserLoggedIn
SS2XVH_AlarmOn | DIGITAL | IOD_SS2 | SS2:.XVH_AlarmOn
SS2Klimat2_1_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_1_Vklop
SS2Klimat2_2_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_2_Vklop
SS2Klimat2_3_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_3_Vklop
SS2Klimat2_4_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_4_Vklop
SS2Klimat2_5_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_5_Vklop
SS2Klimat2_6_Vklop | DIGITAL | IOD_SS2 | SS2:.Klimat2_6_Vklop
SS2ErrCommScada2 | DIGITAL | IOD_SS2 | SS2:.ErrCommScada2
SS2ComSCADA2 | DIGITAL | IOD_SS2 | SS2:.ComSCADA2
SS2ComSCADA3 | DIGITAL | IOD_SS2 | SS2:.ComSCADA3
SS2AlarmSKTemp5_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp5_Previsoka
SS2AlarmSKTemp6_Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmSKTemp6_Previsoka
SS2AlarmTempTIA5Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA5Previsoka
SS2AlarmTempTIA6Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA6Previsoka
SS2NapakaSenzorTemp5 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp5
SS2NapakaSenzorTemp6 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorTemp6
SS2NapakaSenzorVlaga5 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga5
SS2NapakaSenzorVlaga6 | DIGITAL | IOD_SS2 | SS2:.NapakaSenzorVlaga6
SS2AlarmTempTIA235Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA235Previsoka
SS2AlarmTempTIA46Previsoka | DIGITAL | IOD_SS2 | SS2:.AlarmTempTIA46Previsoka
SS2DatumCasDan | INT | IOD_SS2 | SS2:.DatumCas.Dan | BYTE
SS2DatumCasLeto | INT | IOD_SS2 | SS2:.DatumCas.Leto | BYTE
SS2DatumCasLeto2 | INT | IOD_SS2 | SS2:.DatumCas.Leto2
SS2DatumCasMesec | INT | IOD_SS2 | SS2:.DatumCas.Mesec | BYTE
SS2DatumCasMinuta | INT | IOD_SS2 | SS2:.DatumCas.Minuta | BYTE
SS2DatumCasSekunda | INT | IOD_SS2 | SS2:.DatumCas.Sekunda | BYTE
SS2DatumCasUra | INT | IOD_SS2 | SS2:.DatumCas.Ura | BYTE
SS2ErrorComKlima1Status | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Status
SS2ErrorComKlima2Status | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Status
SS2ErrorComKlima3Status | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Status
SS2ErrorComKlima4Status | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Status
SS2ErrorComKlima5Status | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Status
SS2ErrorComKlima6Status | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Status
SS2ErrorComPMM1Status | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Status
SS2ErrorComPMM2Status | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Status
SS2Klima1GrelecStatus | INT | IOD_SS2 | SS2:.Klima[1].GrelecStatus | BYTE
SS2Klima1IzhodniVentStatus | INT | IOD_SS2 | SS2:.Klima[1].IzhodniVentStatus | BYTE
SS2Klima1KompresorStatus | INT | IOD_SS2 | SS2:.Klima[1].KompresorStatus | BYTE
SS2Klima1NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[1].NacinRazvlaz
SS2Klima1VlazilecStatus | INT | IOD_SS2 | SS2:.Klima[1].VlazilecStatus | BYTE
SS2Klima2GrelecStatus | INT | IOD_SS2 | SS2:.Klima[2].GrelecStatus | BYTE
SS2Klima2IzhodniVentStatus | INT | IOD_SS2 | SS2:.Klima[2].IzhodniVentStatus | BYTE
SS2Klima2KompresorStatus | INT | IOD_SS2 | SS2:.Klima[2].KompresorStatus | BYTE
SS2Klima2NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[2].NacinRazvlaz
SS2Klima2VlazilecStatus | INT | IOD_SS2 | SS2:.Klima[2].VlazilecStatus | BYTE
SS2Klima3GrelecStatus | INT | IOD_SS2 | SS2:.Klima[3].GrelecStatus | BYTE
SS2Klima3IzhodniVentStatus | INT | IOD_SS2 | SS2:.Klima[3].IzhodniVentStatus | BYTE
SS2Klima3KompresorStatus | INT | IOD_SS2 | SS2:.Klima[3].KompresorStatus | BYTE
SS2Klima3NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[3].NacinRazvlaz
SS2Klima3VlazilecStatus | INT | IOD_SS2 | SS2:.Klima[3].VlazilecStatus | BYTE
SS2Klima4GrelecStatus | INT | IOD_SS2 | SS2:.Klima[4].GrelecStatus | BYTE
SS2Klima4IzhodniVentStatus | INT | IOD_SS2 | SS2:.Klima[4].IzhodniVentStatus | BYTE
SS2Klima4KompresorStatus | INT | IOD_SS2 | SS2:.Klima[4].KompresorStatus | BYTE
SS2Klima4NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[4].NacinRazvlaz
SS2Klima4VlazilecStatus | INT | IOD_SS2 | SS2:.Klima[4].VlazilecStatus | BYTE
SS2Klima5GrelecStatus | INT | IOD_SS2 | SS2:.Klima[5].GrelecStatus | BYTE
SS2Klima5IzhodniVentStatus | INT | IOD_SS2 | SS2:.Klima[5].IzhodniVentStatus | BYTE
SS2Klima5KompresorStatus | INT | IOD_SS2 | SS2:.Klima[5].KompresorStatus | BYTE
SS2Klima5NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[5].NacinRazvlaz
SS2Klima5VlazilecStatus | INT | IOD_SS2 | SS2:.Klima[5].VlazilecStatus | BYTE
SS2Klima6GrelecStatus | INT | IOD_SS2 | SS2:.Klima[6].GrelecStatus | BYTE
SS2Klima6IzhodniVentStatus | INT | IOD_SS2 | SS2:.Klima[6].IzhodniVentStatus | BYTE
SS2Klima6KompresorStatus | INT | IOD_SS2 | SS2:.Klima[6].KompresorStatus | BYTE
SS2Klima6NacinRazvlaz | INT | IOD_SS2 | SS2:.Klima[6].NacinRazvlaz
SS2Klima6VlazilecStatus | INT | IOD_SS2 | SS2:.Klima[6].VlazilecStatus | BYTE
SS2OznakeFaz10 | INT | IOD_SS2 | SS2:.OznakeFaz[10] | BYTE
SS2OznakeFaz11 | INT | IOD_SS2 | SS2:.OznakeFaz[11] | BYTE
SS2OznakeFaz12 | INT | IOD_SS2 | SS2:.OznakeFaz[12] | BYTE
SS2OznakeFaz13 | INT | IOD_SS2 | SS2:.OznakeFaz[13] | BYTE
SS2OznakeFaz14 | INT | IOD_SS2 | SS2:.OznakeFaz[14] | BYTE
SS2OznakeFaz1 | INT | IOD_SS2 | SS2:.OznakeFaz[1] | BYTE
SS2OznakeFaz2 | INT | IOD_SS2 | SS2:.OznakeFaz[2] | BYTE
SS2OznakeFaz3 | INT | IOD_SS2 | SS2:.OznakeFaz[3] | BYTE
SS2OznakeFaz4 | INT | IOD_SS2 | SS2:.OznakeFaz[4] | BYTE
SS2OznakeFaz5 | INT | IOD_SS2 | SS2:.OznakeFaz[5] | BYTE
SS2OznakeFaz6 | INT | IOD_SS2 | SS2:.OznakeFaz[6] | BYTE
SS2OznakeFaz7 | INT | IOD_SS2 | SS2:.OznakeFaz[7] | BYTE
SS2OznakeFaz8 | INT | IOD_SS2 | SS2:.OznakeFaz[8] | BYTE
SS2OznakeFaz9 | INT | IOD_SS2 | SS2:.OznakeFaz[9] | BYTE
SS2PhaseNo | INT | IOD_SS2 | SS2:.PhaseNo | BYTE
SS2PMM1AlarmPhase1C01_16_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C01_16_60to80 | BYTE
SS2PMM1AlarmPhase1C01_16_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C01_16_over80 | BYTE
SS2PMM1AlarmPhase1C17_32_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C17_32_60to80 | BYTE
SS2PMM1AlarmPhase1C17_32_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C17_32_over80 | BYTE
SS2PMM1AlarmPhase1C33_42_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C33_42_60to80 | BYTE
SS2PMM1AlarmPhase1C33_42_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].C33_42_over80 | BYTE
SS2PMM1AlarmPhase1GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[1].GlobalAlarmReg
SS2PMM1AlarmPhase2C01_16_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C01_16_60to80 | BYTE
SS2PMM1AlarmPhase2C01_16_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C01_16_over80 | BYTE
SS2PMM1AlarmPhase2C17_32_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C17_32_60to80 | BYTE
SS2PMM1AlarmPhase2C17_32_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C17_32_over80 | BYTE
SS2PMM1AlarmPhase2C33_42_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C33_42_60to80 | BYTE
SS2PMM1AlarmPhase2C33_42_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].C33_42_over80 | BYTE
SS2PMM1AlarmPhase2GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[2].GlobalAlarmReg
SS2PMM1AlarmPhase3C01_16_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C01_16_60to80 | BYTE
SS2PMM1AlarmPhase3C01_16_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C01_16_over80 | BYTE
SS2PMM1AlarmPhase3C17_32_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C17_32_60to80 | BYTE
SS2PMM1AlarmPhase3C17_32_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C17_32_over80 | BYTE
SS2PMM1AlarmPhase3C33_42_60to80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C33_42_60to80 | BYTE
SS2PMM1AlarmPhase3C33_42_over80 | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].C33_42_over80 | BYTE
SS2PMM1AlarmPhase3GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[1].AlarmPhase[3].GlobalAlarmReg
SS2PMM2AlarmPhase1C01_16_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C01_16_60to80 | BYTE
SS2PMM2AlarmPhase1C01_16_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C01_16_over80 | BYTE
SS2PMM2AlarmPhase1C17_32_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C17_32_60to80 | BYTE
SS2PMM2AlarmPhase1C17_32_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C17_32_over80 | BYTE
SS2PMM2AlarmPhase1C33_42_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C33_42_60to80 | BYTE
SS2PMM2AlarmPhase1C33_42_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].C33_42_over80 | BYTE
SS2PMM2AlarmPhase1GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[1].GlobalAlarmReg
SS2PMM2AlarmPhase2C01_16_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C01_16_60to80 | BYTE
SS2PMM2AlarmPhase2C01_16_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C01_16_over80 | BYTE
SS2PMM2AlarmPhase2C17_32_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C17_32_60to80 | BYTE
SS2PMM2AlarmPhase2C17_32_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C17_32_over80 | BYTE
SS2PMM2AlarmPhase2C33_42_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C33_42_60to80 | BYTE
SS2PMM2AlarmPhase2C33_42_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].C33_42_over80 | BYTE
SS2PMM2AlarmPhase2GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[2].GlobalAlarmReg
SS2PMM2AlarmPhase3C01_16_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C01_16_60to80 | BYTE
SS2PMM2AlarmPhase3C01_16_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C01_16_over80 | BYTE
SS2PMM2AlarmPhase3C17_32_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C17_32_60to80 | BYTE
SS2PMM2AlarmPhase3C17_32_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C17_32_over80 | BYTE
SS2PMM2AlarmPhase3C33_42_60to80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C33_42_60to80 | BYTE
SS2PMM2AlarmPhase3C33_42_over80 | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].C33_42_over80 | BYTE
SS2PMM2AlarmPhase3GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMM[2].AlarmPhase[3].GlobalAlarmReg
SS2PMMPanelAlarmPhase1C01_16_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C01_16_60to80 | BYTE
SS2PMMPanelAlarmPhase1C01_16_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C01_16_over80 | BYTE
SS2PMMPanelAlarmPhase1C17_32_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C17_32_60to80 | BYTE
SS2PMMPanelAlarmPhase1C17_32_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C17_32_over80 | BYTE
SS2PMMPanelAlarmPhase1C33_42_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C33_42_60to80 | BYTE
SS2PMMPanelAlarmPhase1C33_42_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].C33_42_over80 | BYTE
SS2PMMPanelAlarmPhase1GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[1].GlobalAlarmReg
SS2PMMPanelAlarmPhase2C01_16_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C01_16_60to80 | BYTE
SS2PMMPanelAlarmPhase2C01_16_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C01_16_over80 | BYTE
SS2PMMPanelAlarmPhase2C17_32_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C17_32_60to80 | BYTE
SS2PMMPanelAlarmPhase2C17_32_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C17_32_over80 | BYTE
SS2PMMPanelAlarmPhase2C33_42_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C33_42_60to80 | BYTE
SS2PMMPanelAlarmPhase2C33_42_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].C33_42_over80 | BYTE
SS2PMMPanelAlarmPhase2GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[2].GlobalAlarmReg
SS2PMMPanelAlarmPhase3C01_16_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C01_16_60to80 | BYTE
SS2PMMPanelAlarmPhase3C01_16_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C01_16_over80 | BYTE
SS2PMMPanelAlarmPhase3C17_32_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C17_32_60to80 | BYTE
SS2PMMPanelAlarmPhase3C17_32_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C17_32_over80 | BYTE
SS2PMMPanelAlarmPhase3C33_42_60to80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C33_42_60to80 | BYTE
SS2PMMPanelAlarmPhase3C33_42_over80 | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].C33_42_over80 | BYTE
SS2PMMPanelAlarmPhase3GlobalAlarmReg | INT | IOD_SS2 | SS2:.PMMPanel.AlarmPhase[3].GlobalAlarmReg
SS2StUrZaPreklopKlim1_2 | INT | IOD_SS2 | SS2:.StUrZaPreklopKlim1_2
SS2StUrZaPreklopKlim3_4 | INT | IOD_SS2 | SS2:.StUrZaPreklopKlim3_4
SS2StUrZaPreklopKlim5_6 | INT | IOD_SS2 | SS2:.StUrZaPreklopKlim5_6
SS2UPSstatus_Prikaz_PanelSCADA | INT | IOD_SS2 | SS2:.UPSstatus_Prikaz_PanelSCADA | BYTE
SS2UserCurrentLevel | INT | IOD_SS2 | SS2:.UserCurrentLevel | BYTE
SS2ErrorComKlima1Code0 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[0] | BYTE
SS2ErrorComKlima1Code10 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[10] | BYTE
SS2ErrorComKlima1Code11 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[11] | BYTE
SS2ErrorComKlima1Code12 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[12] | BYTE
SS2ErrorComKlima1Code13 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[13] | BYTE
SS2ErrorComKlima1Code14 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[14] | BYTE
SS2ErrorComKlima1Code15 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[15] | BYTE
SS2ErrorComKlima1Code1 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[1] | BYTE
SS2ErrorComKlima1Code2 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[2] | BYTE
SS2ErrorComKlima1Code3 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[3] | BYTE
SS2ErrorComKlima1Code4 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[4] | BYTE
SS2ErrorComKlima1Code5 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[5] | BYTE
SS2ErrorComKlima1Code6 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[6] | BYTE
SS2ErrorComKlima1Code7 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[7] | BYTE
SS2ErrorComKlima1Code8 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[8] | BYTE
SS2ErrorComKlima1Code9 | INT | IOD_SS2 | SS2:.ErrorComKlima[1].Code[9] | BYTE
SS2ErrorComKlima2Code0 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[0] | BYTE
SS2ErrorComKlima2Code10 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[10] | BYTE
SS2ErrorComKlima2Code11 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[11] | BYTE
SS2ErrorComKlima2Code12 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[12] | BYTE
SS2ErrorComKlima2Code13 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[13] | BYTE
SS2ErrorComKlima2Code14 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[14] | BYTE
SS2ErrorComKlima2Code15 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[15] | BYTE
SS2ErrorComKlima2Code1 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[1] | BYTE
SS2ErrorComKlima2Code2 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[2] | BYTE
SS2ErrorComKlima2Code3 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[3] | BYTE
SS2ErrorComKlima2Code4 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[4] | BYTE
SS2ErrorComKlima2Code5 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[5] | BYTE
SS2ErrorComKlima2Code6 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[6] | BYTE
SS2ErrorComKlima2Code7 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[7] | BYTE
SS2ErrorComKlima2Code8 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[8] | BYTE
SS2ErrorComKlima2Code9 | INT | IOD_SS2 | SS2:.ErrorComKlima[2].Code[9] | BYTE
SS2ErrorComKlima3Code0 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[0] | BYTE
SS2ErrorComKlima3Code10 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[10] | BYTE
SS2ErrorComKlima3Code11 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[11] | BYTE
SS2ErrorComKlima3Code12 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[12] | BYTE
SS2ErrorComKlima3Code13 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[13] | BYTE
SS2ErrorComKlima3Code14 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[14] | BYTE
SS2ErrorComKlima3Code15 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[15] | BYTE
SS2ErrorComKlima3Code1 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[1] | BYTE
SS2ErrorComKlima3Code2 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[2] | BYTE
SS2ErrorComKlima3Code3 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[3] | BYTE
SS2ErrorComKlima3Code4 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[4] | BYTE
SS2ErrorComKlima3Code5 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[5] | BYTE
SS2ErrorComKlima3Code6 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[6] | BYTE
SS2ErrorComKlima3Code7 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[7] | BYTE
SS2ErrorComKlima3Code8 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[8] | BYTE
SS2ErrorComKlima3Code9 | INT | IOD_SS2 | SS2:.ErrorComKlima[3].Code[9] | BYTE
SS2ErrorComKlima4Code0 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[0] | BYTE
SS2ErrorComKlima4Code10 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[10] | BYTE
SS2ErrorComKlima4Code11 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[11] | BYTE
SS2ErrorComKlima4Code12 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[12] | BYTE
SS2ErrorComKlima4Code13 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[13] | BYTE
SS2ErrorComKlima4Code14 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[14] | BYTE
SS2ErrorComKlima4Code15 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[15] | BYTE
SS2ErrorComKlima4Code1 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[1] | BYTE
SS2ErrorComKlima4Code2 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[2] | BYTE
SS2ErrorComKlima4Code3 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[3] | BYTE
SS2ErrorComKlima4Code4 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[4] | BYTE
SS2ErrorComKlima4Code5 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[5] | BYTE
SS2ErrorComKlima4Code6 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[6] | BYTE
SS2ErrorComKlima4Code7 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[7] | BYTE
SS2ErrorComKlima4Code8 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[8] | BYTE
SS2ErrorComKlima4Code9 | INT | IOD_SS2 | SS2:.ErrorComKlima[4].Code[9] | BYTE
SS2ErrorComKlima5Code0 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[0] | BYTE
SS2ErrorComKlima5Code10 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[10] | BYTE
SS2ErrorComKlima5Code11 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[11] | BYTE
SS2ErrorComKlima5Code12 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[12] | BYTE
SS2ErrorComKlima5Code13 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[13] | BYTE
SS2ErrorComKlima5Code14 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[14] | BYTE
SS2ErrorComKlima5Code15 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[15] | BYTE
SS2ErrorComKlima5Code1 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[1] | BYTE
SS2ErrorComKlima5Code2 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[2] | BYTE
SS2ErrorComKlima5Code3 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[3] | BYTE
SS2ErrorComKlima5Code4 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[4] | BYTE
SS2ErrorComKlima5Code5 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[5] | BYTE
SS2ErrorComKlima5Code6 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[6] | BYTE
SS2ErrorComKlima5Code7 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[7] | BYTE
SS2ErrorComKlima5Code8 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[8] | BYTE
SS2ErrorComKlima5Code9 | INT | IOD_SS2 | SS2:.ErrorComKlima[5].Code[9] | BYTE
SS2ErrorComKlima6Code0 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[0] | BYTE
SS2ErrorComKlima6Code10 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[10] | BYTE
SS2ErrorComKlima6Code11 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[11] | BYTE
SS2ErrorComKlima6Code12 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[12] | BYTE
SS2ErrorComKlima6Code13 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[13] | BYTE
SS2ErrorComKlima6Code14 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[14] | BYTE
SS2ErrorComKlima6Code15 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[15] | BYTE
SS2ErrorComKlima6Code1 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[1] | BYTE
SS2ErrorComKlima6Code2 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[2] | BYTE
SS2ErrorComKlima6Code3 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[3] | BYTE
SS2ErrorComKlima6Code4 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[4] | BYTE
SS2ErrorComKlima6Code5 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[5] | BYTE
SS2ErrorComKlima6Code6 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[6] | BYTE
SS2ErrorComKlima6Code7 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[7] | BYTE
SS2ErrorComKlima6Code8 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[8] | BYTE
SS2ErrorComKlima6Code9 | INT | IOD_SS2 | SS2:.ErrorComKlima[6].Code[9] | BYTE
SS2ErrorComPMM1Code0 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[0] | BYTE
SS2ErrorComPMM1Code10 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[10] | BYTE
SS2ErrorComPMM1Code11 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[11] | BYTE
SS2ErrorComPMM1Code12 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[12] | BYTE
SS2ErrorComPMM1Code13 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[13] | BYTE
SS2ErrorComPMM1Code14 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[14] | BYTE
SS2ErrorComPMM1Code15 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[15] | BYTE
SS2ErrorComPMM1Code1 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[1] | BYTE
SS2ErrorComPMM1Code2 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[2] | BYTE
SS2ErrorComPMM1Code3 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[3] | BYTE
SS2ErrorComPMM1Code4 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[4] | BYTE
SS2ErrorComPMM1Code5 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[5] | BYTE
SS2ErrorComPMM1Code6 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[6] | BYTE
SS2ErrorComPMM1Code7 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[7] | BYTE
SS2ErrorComPMM1Code8 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[8] | BYTE
SS2ErrorComPMM1Code9 | INT | IOD_SS2 | SS2:.ErrorComPMM[1].Code[9] | BYTE
SS2ErrorComPMM2Code0 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[0] | BYTE
SS2ErrorComPMM2Code10 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[10] | BYTE
SS2ErrorComPMM2Code11 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[11] | BYTE
SS2ErrorComPMM2Code12 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[12] | BYTE
SS2ErrorComPMM2Code13 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[13] | BYTE
SS2ErrorComPMM2Code14 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[14] | BYTE
SS2ErrorComPMM2Code15 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[15] | BYTE
SS2ErrorComPMM2Code1 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[1] | BYTE
SS2ErrorComPMM2Code2 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[2] | BYTE
SS2ErrorComPMM2Code3 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[3] | BYTE
SS2ErrorComPMM2Code4 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[4] | BYTE
SS2ErrorComPMM2Code5 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[5] | BYTE
SS2ErrorComPMM2Code6 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[6] | BYTE
SS2ErrorComPMM2Code7 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[7] | BYTE
SS2ErrorComPMM2Code8 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[8] | BYTE
SS2ErrorComPMM2Code9 | INT | IOD_SS2 | SS2:.ErrorComPMM[2].Code[9] | BYTE
SS2kom_nast_cas_izpada | INT | IOD_SS2 | SS2:.kom_nast_cas_izpada
SS2AktualniSetPointTemp1_2 | REAL | IOD_SS2 | SS2:.AktualniSetPointTemp1_2
SS2AktualniSetPointTemp3_4 | REAL | IOD_SS2 | SS2:.AktualniSetPointTemp3_4
SS2AktualniSetPointTemp5_6 | REAL | IOD_SS2 | SS2:.AktualniSetPointTemp5_6
SS2Klima1ure | REAL | IOD_SS2 | SS2:.Klima1ure
SS2Klima2ure | REAL | IOD_SS2 | SS2:.Klima2ure
SS2Klima3ure | REAL | IOD_SS2 | SS2:.Klima3ure
SS2Klima4ure | REAL | IOD_SS2 | SS2:.Klima4ure
SS2Klima5ure | REAL | IOD_SS2 | SS2:.Klima5ure
SS2Klima6ure | REAL | IOD_SS2 | SS2:.Klima6ure
SS2Klima1NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[1].NastMaxTemp
SS2Klima1NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[1].NastMaxVlaznost
SS2Klima1NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[1].NastMinTemp
SS2Klima1NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[1].NastMinVlaznost
SS2Klima1NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[1].NastTempProstora
SS2Klima1NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[1].NastVlaznost
SS2Klima1ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[1].ObratUreFilter
SS2Klima1ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[1].ObratUreKompresor1
SS2Klima1ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[1].ObratUreKompresor2
SS2Klima1ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[1].ObratUreVent
SS2Klima1TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[1].TemperaturaProstora
SS2Klima1VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[1].VlaznostProstora
SS2Klima2NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[2].NastMaxTemp
SS2Klima2NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[2].NastMaxVlaznost
SS2Klima2NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[2].NastMinTemp
SS2Klima2NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[2].NastMinVlaznost
SS2Klima2NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[2].NastTempProstora
SS2Klima2NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[2].NastVlaznost
SS2Klima2ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[2].ObratUreFilter
SS2Klima2ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[2].ObratUreKompresor1
SS2Klima2ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[2].ObratUreKompresor2
SS2Klima2ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[2].ObratUreVent
SS2Klima2TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[2].TemperaturaProstora
SS2Klima2VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[2].VlaznostProstora
SS2Klima3NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[3].NastMaxTemp
SS2Klima3NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[3].NastMaxVlaznost
SS2Klima3NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[3].NastMinTemp
SS2Klima3NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[3].NastMinVlaznost
SS2Klima3NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[3].NastTempProstora
SS2Klima3NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[3].NastVlaznost
SS2Klima3ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[3].ObratUreFilter
SS2Klima3ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[3].ObratUreKompresor1
SS2Klima3ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[3].ObratUreKompresor2
SS2Klima3ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[3].ObratUreVent
SS2Klima3TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[3].TemperaturaProstora
SS2Klima3VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[3].VlaznostProstora
SS2Klima4NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[4].NastMaxTemp
SS2Klima4NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[4].NastMaxVlaznost
SS2Klima4NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[4].NastMinTemp
SS2Klima4NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[4].NastMinVlaznost
SS2Klima4NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[4].NastTempProstora
SS2Klima4NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[4].NastVlaznost
SS2Klima4ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[4].ObratUreFilter
SS2Klima4ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[4].ObratUreKompresor1
SS2Klima4ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[4].ObratUreKompresor2
SS2Klima4ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[4].ObratUreVent
SS2Klima4TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[4].TemperaturaProstora
SS2Klima4VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[4].VlaznostProstora
SS2Klima5NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[5].NastMaxTemp
SS2Klima5NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[5].NastMaxVlaznost
SS2Klima5NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[5].NastMinTemp
SS2Klima5NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[5].NastMinVlaznost
SS2Klima5NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[5].NastTempProstora
SS2Klima5NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[5].NastVlaznost
SS2Klima5ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[5].ObratUreFilter
SS2Klima5ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[5].ObratUreKompresor1
SS2Klima5ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[5].ObratUreKompresor2
SS2Klima5ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[5].ObratUreVent
SS2Klima5TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[5].TemperaturaProstora
SS2Klima5VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[5].VlaznostProstora
SS2Klima6NastMaxTemp | REAL | IOD_SS2 | SS2:.Klima[6].NastMaxTemp
SS2Klima6NastMaxVlaznost | REAL | IOD_SS2 | SS2:.Klima[6].NastMaxVlaznost
SS2Klima6NastMinTemp | REAL | IOD_SS2 | SS2:.Klima[6].NastMinTemp
SS2Klima6NastMinVlaznost | REAL | IOD_SS2 | SS2:.Klima[6].NastMinVlaznost
SS2Klima6NastTempProstora | REAL | IOD_SS2 | SS2:.Klima[6].NastTempProstora
SS2Klima6NastVlaznost | REAL | IOD_SS2 | SS2:.Klima[6].NastVlaznost
SS2Klima6ObratUreFilter | REAL | IOD_SS2 | SS2:.Klima[6].ObratUreFilter
SS2Klima6ObratUreKompresor1 | REAL | IOD_SS2 | SS2:.Klima[6].ObratUreKompresor1
SS2Klima6ObratUreKompresor2 | REAL | IOD_SS2 | SS2:.Klima[6].ObratUreKompresor2
SS2Klima6ObratUreVent | REAL | IOD_SS2 | SS2:.Klima[6].ObratUreVent
SS2Klima6TemperaturaProstora | REAL | IOD_SS2 | SS2:.Klima[6].TemperaturaProstora
SS2Klima6VlaznostProstora | REAL | IOD_SS2 | SS2:.Klima[6].VlaznostProstora
SS2PMM1ActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMM[1].ActiveEnergyConsumed_kWh
SS2PMM1ActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMM[1].ActivePowerPhaseA_kW
SS2PMM1ActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMM[1].ActivePowerPhaseB_kW
SS2PMM1ActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMM[1].ActivePowerPhaseC_kW
SS2PMM1AparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[1].AparentPowerPhaseA
SS2PMM1AparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[1].AparentPowerPhaseB
SS2PMM1AparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[1].AparentPowerPhaseC
SS2PMM1AverageCurrent_A | REAL | IOD_SS2 | SS2:.PMM[1].AverageCurrent_A
SS2PMM1AveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMM[1].AveragePhaseToNeutral_V
SS2PMM1AveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMM[1].AveragePhaseToPhase_V
SS2PMM1CurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMM[1].CurrentInPhaseA_A
SS2PMM1CurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMM[1].CurrentInPhaseB_A
SS2PMM1CurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMM[1].CurrentInPhaseC_A
SS2PMM1Frequency_Hz | REAL | IOD_SS2 | SS2:.PMM[1].Frequency_Hz
SS2PMM1Phase1Current10 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[10]
SS2PMM1Phase1Current11 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[11]
SS2PMM1Phase1Current12 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[12]
SS2PMM1Phase1Current13 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[13]
SS2PMM1Phase1Current14 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[14]
SS2PMM1Phase1Current15 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[15]
SS2PMM1Phase1Current16 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[16]
SS2PMM1Phase1Current17 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[17]
SS2PMM1Phase1Current18 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[18]
SS2PMM1Phase1Current19 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[19]
SS2PMM1Phase1Current1 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[1]
SS2PMM1Phase1Current20 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[20]
SS2PMM1Phase1Current21 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[21]
SS2PMM1Phase1Current22 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[22]
SS2PMM1Phase1Current23 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[23]
SS2PMM1Phase1Current24 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[24]
SS2PMM1Phase1Current25 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[25]
SS2PMM1Phase1Current26 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[26]
SS2PMM1Phase1Current27 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[27]
SS2PMM1Phase1Current28 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[28]
SS2PMM1Phase1Current29 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[29]
SS2PMM1Phase1Current2 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[2]
SS2PMM1Phase1Current30 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[30]
SS2PMM1Phase1Current31 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[31]
SS2PMM1Phase1Current32 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[32]
SS2PMM1Phase1Current33 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[33]
SS2PMM1Phase1Current34 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[34]
SS2PMM1Phase1Current35 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[35]
SS2PMM1Phase1Current36 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[36]
SS2PMM1Phase1Current37 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[37]
SS2PMM1Phase1Current38 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[38]
SS2PMM1Phase1Current39 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[39]
SS2PMM1Phase1Current3 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[3]
SS2PMM1Phase1Current40 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[40]
SS2PMM1Phase1Current41 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[41]
SS2PMM1Phase1Current42 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[42]
SS2PMM1Phase1Current4 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[4]
SS2PMM1Phase1Current5 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[5]
SS2PMM1Phase1Current6 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[6]
SS2PMM1Phase1Current7 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[7]
SS2PMM1Phase1Current8 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[8]
SS2PMM1Phase1Current9 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[1].Current[9]
SS2PMM1Phase2Current10 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[10]
SS2PMM1Phase2Current11 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[11]
SS2PMM1Phase2Current12 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[12]
SS2PMM1Phase2Current13 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[13]
SS2PMM1Phase2Current14 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[14]
SS2PMM1Phase2Current15 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[15]
SS2PMM1Phase2Current16 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[16]
SS2PMM1Phase2Current17 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[17]
SS2PMM1Phase2Current18 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[18]
SS2PMM1Phase2Current19 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[19]
SS2PMM1Phase2Current1 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[1]
SS2PMM1Phase2Current20 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[20]
SS2PMM1Phase2Current21 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[21]
SS2PMM1Phase2Current22 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[22]
SS2PMM1Phase2Current23 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[23]
SS2PMM1Phase2Current24 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[24]
SS2PMM1Phase2Current25 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[25]
SS2PMM1Phase2Current26 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[26]
SS2PMM1Phase2Current27 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[27]
SS2PMM1Phase2Current28 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[28]
SS2PMM1Phase2Current29 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[29]
SS2PMM1Phase2Current2 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[2]
SS2PMM1Phase2Current30 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[30]
SS2PMM1Phase2Current31 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[31]
SS2PMM1Phase2Current32 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[32]
SS2PMM1Phase2Current33 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[33]
SS2PMM1Phase2Current34 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[34]
SS2PMM1Phase2Current35 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[35]
SS2PMM1Phase2Current36 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[36]
SS2PMM1Phase2Current37 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[37]
SS2PMM1Phase2Current38 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[38]
SS2PMM1Phase2Current39 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[39]
SS2PMM1Phase2Current3 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[3]
SS2PMM1Phase2Current40 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[40]
SS2PMM1Phase2Current41 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[41]
SS2PMM1Phase2Current42 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[42]
SS2PMM1Phase2Current4 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[4]
SS2PMM1Phase2Current5 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[5]
SS2PMM1Phase2Current6 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[6]
SS2PMM1Phase2Current7 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[7]
SS2PMM1Phase2Current8 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[8]
SS2PMM1Phase2Current9 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[2].Current[9]
SS2PMM1Phase3Current10 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[10]
SS2PMM1Phase3Current11 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[11]
SS2PMM1Phase3Current12 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[12]
SS2PMM1Phase3Current13 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[13]
SS2PMM1Phase3Current14 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[14]
SS2PMM1Phase3Current15 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[15]
SS2PMM1Phase3Current16 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[16]
SS2PMM1Phase3Current17 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[17]
SS2PMM1Phase3Current18 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[18]
SS2PMM1Phase3Current19 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[19]
SS2PMM1Phase3Current1 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[1]
SS2PMM1Phase3Current20 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[20]
SS2PMM1Phase3Current21 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[21]
SS2PMM1Phase3Current22 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[22]
SS2PMM1Phase3Current23 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[23]
SS2PMM1Phase3Current24 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[24]
SS2PMM1Phase3Current25 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[25]
SS2PMM1Phase3Current26 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[26]
SS2PMM1Phase3Current27 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[27]
SS2PMM1Phase3Current28 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[28]
SS2PMM1Phase3Current29 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[29]
SS2PMM1Phase3Current2 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[2]
SS2PMM1Phase3Current30 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[30]
SS2PMM1Phase3Current31 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[31]
SS2PMM1Phase3Current32 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[32]
SS2PMM1Phase3Current33 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[33]
SS2PMM1Phase3Current34 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[34]
SS2PMM1Phase3Current35 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[35]
SS2PMM1Phase3Current36 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[36]
SS2PMM1Phase3Current37 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[37]
SS2PMM1Phase3Current38 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[38]
SS2PMM1Phase3Current39 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[39]
SS2PMM1Phase3Current3 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[3]
SS2PMM1Phase3Current40 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[40]
SS2PMM1Phase3Current41 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[41]
SS2PMM1Phase3Current42 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[42]
SS2PMM1Phase3Current4 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[4]
SS2PMM1Phase3Current5 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[5]
SS2PMM1Phase3Current6 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[6]
SS2PMM1Phase3Current7 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[7]
SS2PMM1Phase3Current8 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[8]
SS2PMM1Phase3Current9 | REAL | IOD_SS2 | SS2:.PMM[1].Phase[3].Current[9]
SS2PMM1PowerFactorSys | REAL | IOD_SS2 | SS2:.PMM[1].PowerFactorSys
SS2PMM1ReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMM[1].ReactiveEnergyConsumed_kVARh
SS2PMM1ReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[1].ReactivePowerPhaseA
SS2PMM1ReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[1].ReactivePowerPhaseB
SS2PMM1ReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[1].ReactivePowerPhaseC
SS2PMM1TotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMM[1].TotalActivePower_kW
SS2PMM1TotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMM[1].TotalAparentPower_kVA
SS2PMM1TotalPowerFactor | REAL | IOD_SS2 | SS2:.PMM[1].TotalPowerFactor
SS2PMM1TotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMM[1].TotalReactivePower_kVAR
SS2PMM1VirA_fsys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_fsys
SS2PMM1VirA_Isys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_Isys
SS2PMM1VirA_PFsys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_PFsys
SS2PMM1VirA_Psys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_Psys
SS2PMM1VirA_Qsys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_Qsys
SS2PMM1VirA_Ssys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_Ssys
SS2PMM1VirA_Usys | REAL | IOD_SS2 | SS2:.PMM[1].VirA_Usys
SS2PMM1VirB_fsys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_fsys
SS2PMM1VirB_Isys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_Isys
SS2PMM1VirB_PFsys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_PFsys
SS2PMM1VirB_Psys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_Psys
SS2PMM1VirB_Qsys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_Qsys
SS2PMM1VirB_Ssys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_Ssys
SS2PMM1VirB_Usys | REAL | IOD_SS2 | SS2:.PMM[1].VirB_Usys
SS2PMM1VirBActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMM[1].VirBActiveEnergyConsumed_kWh
SS2PMM1VirBActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMM[1].VirBActivePowerPhaseA_kW
SS2PMM1VirBActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMM[1].VirBActivePowerPhaseB_kW
SS2PMM1VirBActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMM[1].VirBActivePowerPhaseC_kW
SS2PMM1VirBAparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[1].VirBAparentPowerPhaseA
SS2PMM1VirBAparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[1].VirBAparentPowerPhaseB
SS2PMM1VirBAparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[1].VirBAparentPowerPhaseC
SS2PMM1VirBAverageCurrent_A | REAL | IOD_SS2 | SS2:.PMM[1].VirBAverageCurrent_A
SS2PMM1VirBAveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBAveragePhaseToNeutral_V
SS2PMM1VirBAveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBAveragePhaseToPhase_V
SS2PMM1VirBCurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMM[1].VirBCurrentInPhaseA_A
SS2PMM1VirBCurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMM[1].VirBCurrentInPhaseB_A
SS2PMM1VirBCurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMM[1].VirBCurrentInPhaseC_A
SS2PMM1VirBFrequency_Hz | REAL | IOD_SS2 | SS2:.PMM[1].VirBFrequency_Hz
SS2PMM1VirBPowerFactorSys | REAL | IOD_SS2 | SS2:.PMM[1].VirBPowerFactorSys
SS2PMM1VirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMM[1].VirBReactiveEnergyConsumed_kVARh
SS2PMM1VirBReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[1].VirBReactivePowerPhaseA
SS2PMM1VirBReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[1].VirBReactivePowerPhaseB
SS2PMM1VirBReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[1].VirBReactivePowerPhaseC
SS2PMM1VirBTotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMM[1].VirBTotalActivePower_kW
SS2PMM1VirBTotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMM[1].VirBTotalAparentPower_kVA
SS2PMM1VirBTotalPowerFactor | REAL | IOD_SS2 | SS2:.PMM[1].VirBTotalPowerFactor
SS2PMM1VirBTotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMM[1].VirBTotalReactivePower_kVAR
SS2PMM1VirBVoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseAB_V
SS2PMM1VirBVoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseAN_V
SS2PMM1VirBVoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseBC_V
SS2PMM1VirBVoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseBN_V
SS2PMM1VirBVoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseCA_V
SS2PMM1VirBVoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMM[1].VirBVoltageBetweenPhaseCN_V
SS2PMM1VoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseAB_V
SS2PMM1VoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseAN_V
SS2PMM1VoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseBC_V
SS2PMM1VoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseBN_V
SS2PMM1VoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseCA_V
SS2PMM1VoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMM[1].VoltageBetweenPhaseCN_V
SS2PMM2ActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMM[2].ActiveEnergyConsumed_kWh
SS2PMM2ActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMM[2].ActivePowerPhaseA_kW
SS2PMM2ActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMM[2].ActivePowerPhaseB_kW
SS2PMM2ActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMM[2].ActivePowerPhaseC_kW
SS2PMM2AparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[2].AparentPowerPhaseA
SS2PMM2AparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[2].AparentPowerPhaseB
SS2PMM2AparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[2].AparentPowerPhaseC
SS2PMM2AverageCurrent_A | REAL | IOD_SS2 | SS2:.PMM[2].AverageCurrent_A
SS2PMM2AveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMM[2].AveragePhaseToNeutral_V
SS2PMM2AveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMM[2].AveragePhaseToPhase_V
SS2PMM2CurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMM[2].CurrentInPhaseA_A
SS2PMM2CurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMM[2].CurrentInPhaseB_A
SS2PMM2CurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMM[2].CurrentInPhaseC_A
SS2PMM2Frequency_Hz | REAL | IOD_SS2 | SS2:.PMM[2].Frequency_Hz
SS2PMM2Phase1Current1 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[1]
SS2PMM2Phase1Current2 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[2]
SS2PMM2Phase1Current3 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[3]
SS2PMM2Phase1Current4 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[4]
SS2PMM2Phase1Current5 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[5]
SS2PMM2Phase1Current6 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[6]
SS2PMM2Phase1Current7 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[7]
SS2PMM2Phase1Current8 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[8]
SS2PMM2Phase1Current9 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[9]
SS2PMM2Phase1Current10 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[10]
SS2PMM2Phase1Current11 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[11]
SS2PMM2Phase1Current12 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[12]
SS2PMM2Phase1Current13 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[13]
SS2PMM2Phase1Current14 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[14]
SS2PMM2Phase1Current15 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[15]
SS2PMM2Phase1Current16 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[16]
SS2PMM2Phase1Current17 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[17]
SS2PMM2Phase1Current18 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[18]
SS2PMM2Phase1Current19 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[19]
SS2PMM2Phase1Current20 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[20]
SS2PMM2Phase1Current21 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[21]
SS2PMM2Phase1Current22 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[22]
SS2PMM2Phase1Current23 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[23]
SS2PMM2Phase1Current24 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[24]
SS2PMM2Phase1Current25 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[25]
SS2PMM2Phase1Current26 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[26]
SS2PMM2Phase1Current27 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[27]
SS2PMM2Phase1Current28 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[28]
SS2PMM2Phase1Current29 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[29]
SS2PMM2Phase1Current30 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[30]
SS2PMM2Phase1Current31 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[31]
SS2PMM2Phase1Current32 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[32]
SS2PMM2Phase1Current33 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[33]
SS2PMM2Phase1Current34 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[34]
SS2PMM2Phase1Current35 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[35]
SS2PMM2Phase1Current36 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[36]
SS2PMM2Phase1Current37 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[37]
SS2PMM2Phase1Current38 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[38]
SS2PMM2Phase1Current39 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[39]
SS2PMM2Phase1Current40 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[40]
SS2PMM2Phase1Current41 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[41]
SS2PMM2Phase1Current42 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[1].Current[42]
SS2PMM2Phase2Current10 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[10]
SS2PMM2Phase2Current11 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[11]
SS2PMM2Phase2Current12 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[12]
SS2PMM2Phase2Current13 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[13]
SS2PMM2Phase2Current14 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[14]
SS2PMM2Phase2Current15 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[15]
SS2PMM2Phase2Current16 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[16]
SS2PMM2Phase2Current17 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[17]
SS2PMM2Phase2Current18 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[18]
SS2PMM2Phase2Current19 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[19]
SS2PMM2Phase2Current1 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[1]
SS2PMM2Phase2Current20 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[20]
SS2PMM2Phase2Current21 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[21]
SS2PMM2Phase2Current22 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[22]
SS2PMM2Phase2Current23 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[23]
SS2PMM2Phase2Current24 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[24]
SS2PMM2Phase2Current25 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[25]
SS2PMM2Phase2Current26 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[26]
SS2PMM2Phase2Current27 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[27]
SS2PMM2Phase2Current28 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[28]
SS2PMM2Phase2Current29 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[29]
SS2PMM2Phase2Current2 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[2]
SS2PMM2Phase2Current30 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[30]
SS2PMM2Phase2Current31 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[31]
SS2PMM2Phase2Current32 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[32]
SS2PMM2Phase2Current33 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[33]
SS2PMM2Phase2Current34 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[34]
SS2PMM2Phase2Current35 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[35]
SS2PMM2Phase2Current36 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[36]
SS2PMM2Phase2Current37 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[37]
SS2PMM2Phase2Current38 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[38]
SS2PMM2Phase2Current39 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[39]
SS2PMM2Phase2Current3 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[3]
SS2PMM2Phase2Current40 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[40]
SS2PMM2Phase2Current41 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[41]
SS2PMM2Phase2Current42 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[42]
SS2PMM2Phase2Current4 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[4]
SS2PMM2Phase2Current5 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[5]
SS2PMM2Phase2Current6 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[6]
SS2PMM2Phase2Current7 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[7]
SS2PMM2Phase2Current8 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[8]
SS2PMM2Phase2Current9 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[2].Current[9]
SS2PMM2Phase3Current10 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[10]
SS2PMM2Phase3Current11 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[11]
SS2PMM2Phase3Current12 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[12]
SS2PMM2Phase3Current13 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[13]
SS2PMM2Phase3Current14 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[14]
SS2PMM2Phase3Current15 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[15]
SS2PMM2Phase3Current16 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[16]
SS2PMM2Phase3Current17 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[17]
SS2PMM2Phase3Current18 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[18]
SS2PMM2Phase3Current19 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[19]
SS2PMM2Phase3Current1 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[1]
SS2PMM2Phase3Current20 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[20]
SS2PMM2Phase3Current21 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[21]
SS2PMM2Phase3Current22 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[22]
SS2PMM2Phase3Current23 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[23]
SS2PMM2Phase3Current24 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[24]
SS2PMM2Phase3Current25 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[25]
SS2PMM2Phase3Current26 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[26]
SS2PMM2Phase3Current27 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[27]
SS2PMM2Phase3Current28 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[28]
SS2PMM2Phase3Current29 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[29]
SS2PMM2Phase3Current2 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[2]
SS2PMM2Phase3Current30 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[30]
SS2PMM2Phase3Current31 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[31]
SS2PMM2Phase3Current32 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[32]
SS2PMM2Phase3Current33 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[33]
SS2PMM2Phase3Current34 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[34]
SS2PMM2Phase3Current35 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[35]
SS2PMM2Phase3Current36 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[36]
SS2PMM2Phase3Current37 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[37]
SS2PMM2Phase3Current38 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[38]
SS2PMM2Phase3Current39 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[39]
SS2PMM2Phase3Current3 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[3]
SS2PMM2Phase3Current40 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[40]
SS2PMM2Phase3Current41 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[41]
SS2PMM2Phase3Current42 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[42]
SS2PMM2Phase3Current4 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[4]
SS2PMM2Phase3Current5 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[5]
SS2PMM2Phase3Current6 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[6]
SS2PMM2Phase3Current7 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[7]
SS2PMM2Phase3Current8 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[8]
SS2PMM2Phase3Current9 | REAL | IOD_SS2 | SS2:.PMM[2].Phase[3].Current[9]
SS2PMM2PowerFactorSys | REAL | IOD_SS2 | SS2:.PMM[2].PowerFactorSys
SS2PMM2ReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMM[2].ReactiveEnergyConsumed_kVARh
SS2PMM2ReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[2].ReactivePowerPhaseA
SS2PMM2ReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[2].ReactivePowerPhaseB
SS2PMM2ReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[2].ReactivePowerPhaseC
SS2PMM2TotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMM[2].TotalActivePower_kW
SS2PMM2TotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMM[2].TotalAparentPower_kVA
SS2PMM2TotalPowerFactor | REAL | IOD_SS2 | SS2:.PMM[2].TotalPowerFactor
SS2PMM2TotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMM[2].TotalReactivePower_kVAR
SS2PMM2VirA_fsys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_fsys
SS2PMM2VirA_Isys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_Isys
SS2PMM2VirA_PFsys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_PFsys
SS2PMM2VirA_Psys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_Psys
SS2PMM2VirA_Qsys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_Qsys
SS2PMM2VirA_Ssys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_Ssys
SS2PMM2VirA_Usys | REAL | IOD_SS2 | SS2:.PMM[2].VirA_Usys
SS2PMM2VirB_fsys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_fsys
SS2PMM2VirB_Isys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_Isys
SS2PMM2VirB_PFsys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_PFsys
SS2PMM2VirB_Psys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_Psys
SS2PMM2VirB_Qsys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_Qsys
SS2PMM2VirB_Ssys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_Ssys
SS2PMM2VirB_Usys | REAL | IOD_SS2 | SS2:.PMM[2].VirB_Usys
SS2PMM2VirBActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMM[2].VirBActiveEnergyConsumed_kWh
SS2PMM2VirBActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMM[2].VirBActivePowerPhaseA_kW
SS2PMM2VirBActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMM[2].VirBActivePowerPhaseB_kW
SS2PMM2VirBActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMM[2].VirBActivePowerPhaseC_kW
SS2PMM2VirBAparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[2].VirBAparentPowerPhaseA
SS2PMM2VirBAparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[2].VirBAparentPowerPhaseB
SS2PMM2VirBAparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[2].VirBAparentPowerPhaseC
SS2PMM2VirBAverageCurrent_A | REAL | IOD_SS2 | SS2:.PMM[2].VirBAverageCurrent_A
SS2PMM2VirBAveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBAveragePhaseToNeutral_V
SS2PMM2VirBAveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBAveragePhaseToPhase_V
SS2PMM2VirBCurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMM[2].VirBCurrentInPhaseA_A
SS2PMM2VirBCurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMM[2].VirBCurrentInPhaseB_A
SS2PMM2VirBCurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMM[2].VirBCurrentInPhaseC_A
SS2PMM2VirBFrequency_Hz | REAL | IOD_SS2 | SS2:.PMM[2].VirBFrequency_Hz
SS2PMM2VirBPowerFactorSys | REAL | IOD_SS2 | SS2:.PMM[2].VirBPowerFactorSys
SS2PMM2VirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMM[2].VirBReactiveEnergyConsumed_kVARh
SS2PMM2VirBReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMM[2].VirBReactivePowerPhaseA
SS2PMM2VirBReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMM[2].VirBReactivePowerPhaseB
SS2PMM2VirBReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMM[2].VirBReactivePowerPhaseC
SS2PMM2VirBTotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMM[2].VirBTotalActivePower_kW
SS2PMM2VirBTotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMM[2].VirBTotalAparentPower_kVA
SS2PMM2VirBTotalPowerFactor | REAL | IOD_SS2 | SS2:.PMM[2].VirBTotalPowerFactor
SS2PMM2VirBTotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMM[2].VirBTotalReactivePower_kVAR
SS2PMM2VirBVoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseAB_V
SS2PMM2VirBVoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseAN_V
SS2PMM2VirBVoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseBC_V
SS2PMM2VirBVoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseBN_V
SS2PMM2VirBVoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseCA_V
SS2PMM2VirBVoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMM[2].VirBVoltageBetweenPhaseCN_V
SS2PMM2VoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseAB_V
SS2PMM2VoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseAN_V
SS2PMM2VoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseBC_V
SS2PMM2VoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseBN_V
SS2PMM2VoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseCA_V
SS2PMM2VoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMM[2].VoltageBetweenPhaseCN_V
SS2PMMPanelActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMMPanel.ActiveEnergyConsumed_kWh
SS2PMMPanelActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMMPanel.ActivePowerPhaseA_kW
SS2PMMPanelActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMMPanel.ActivePowerPhaseB_kW
SS2PMMPanelActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMMPanel.ActivePowerPhaseC_kW
SS2PMMPanelAparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMMPanel.AparentPowerPhaseA
SS2PMMPanelAparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMMPanel.AparentPowerPhaseB
SS2PMMPanelAparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMMPanel.AparentPowerPhaseC
SS2PMMPanelAverageCurrent_A | REAL | IOD_SS2 | SS2:.PMMPanel.AverageCurrent_A
SS2PMMPanelAveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMMPanel.AveragePhaseToNeutral_V
SS2PMMPanelAveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMMPanel.AveragePhaseToPhase_V
SS2PMMPanelCurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMMPanel.CurrentInPhaseA_A
SS2PMMPanelCurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMMPanel.CurrentInPhaseB_A
SS2PMMPanelCurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMMPanel.CurrentInPhaseC_A
SS2PMMPanelFrequency_Hz | REAL | IOD_SS2 | SS2:.PMMPanel.Frequency_Hz
SS2PMMPanelPowerFactorSys | REAL | IOD_SS2 | SS2:.PMMPanel.PowerFactorSys
SS2PMMPanelReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMMPanel.ReactiveEnergyConsumed_kVARh
SS2PMMPanelReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMMPanel.ReactivePowerPhaseA
SS2PMMPanelReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMMPanel.ReactivePowerPhaseB
SS2PMMPanelReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMMPanel.ReactivePowerPhaseC
SS2PMMPanelTotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMMPanel.TotalActivePower_kW
SS2PMMPanelTotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMMPanel.TotalAparentPower_kVA
SS2PMMPanelTotalPowerFactor | REAL | IOD_SS2 | SS2:.PMMPanel.TotalPowerFactor
SS2PMMPanelTotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMMPanel.TotalReactivePower_kVAR
SS2PMMPanelVirA_fsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_fsys
SS2PMMPanelVirA_Isys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_Isys
SS2PMMPanelVirA_PFsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_PFsys
SS2PMMPanelVirA_Psys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_Psys
SS2PMMPanelVirA_Qsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_Qsys
SS2PMMPanelVirA_Ssys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_Ssys
SS2PMMPanelVirA_Usys | REAL | IOD_SS2 | SS2:.PMMPanel.VirA_Usys
SS2PMMPanelVirB_fsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_fsys
SS2PMMPanelVirB_Isys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_Isys
SS2PMMPanelVirB_PFsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_PFsys
SS2PMMPanelVirB_Psys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_Psys
SS2PMMPanelVirB_Qsys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_Qsys
SS2PMMPanelVirB_Ssys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_Ssys
SS2PMMPanelVirB_Usys | REAL | IOD_SS2 | SS2:.PMMPanel.VirB_Usys
SS2PMMPanelVirBActiveEnergyConsumed_kWh | REAL | IOD_SS2 | SS2:.PMMPanel.VirBActiveEnergyConsumed_kWh
SS2PMMPanelVirBActivePowerPhaseA_kW | REAL | IOD_SS2 | SS2:.PMMPanel.VirBActivePowerPhaseA_kW
SS2PMMPanelVirBActivePowerPhaseB_kW | REAL | IOD_SS2 | SS2:.PMMPanel.VirBActivePowerPhaseB_kW
SS2PMMPanelVirBActivePowerPhaseC_kW | REAL | IOD_SS2 | SS2:.PMMPanel.VirBActivePowerPhaseC_kW
SS2PMMPanelVirBAparentPowerPhaseA | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAparentPowerPhaseA
SS2PMMPanelVirBAparentPowerPhaseB | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAparentPowerPhaseB
SS2PMMPanelVirBAparentPowerPhaseC | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAparentPowerPhaseC
SS2PMMPanelVirBAverageCurrent_A | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAverageCurrent_A
SS2PMMPanelVirBAveragePhaseToNeutral_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAveragePhaseToNeutral_V
SS2PMMPanelVirBAveragePhaseToPhase_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBAveragePhaseToPhase_V
SS2PMMPanelVirBCurrentInPhaseA_A | REAL | IOD_SS2 | SS2:.PMMPanel.VirBCurrentInPhaseA_A
SS2PMMPanelVirBCurrentInPhaseB_A | REAL | IOD_SS2 | SS2:.PMMPanel.VirBCurrentInPhaseB_A
SS2PMMPanelVirBCurrentInPhaseC_A | REAL | IOD_SS2 | SS2:.PMMPanel.VirBCurrentInPhaseC_A
SS2PMMPanelVirBFrequency_Hz | REAL | IOD_SS2 | SS2:.PMMPanel.VirBFrequency_Hz
SS2PMMPanelVirBPowerFactorSys | REAL | IOD_SS2 | SS2:.PMMPanel.VirBPowerFactorSys
SS2PMMPanelVirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS2 | SS2:.PMMPanel.VirBReactiveEnergyConsumed_kVARh
SS2PMMPanelVirBReactivePowerPhaseA | REAL | IOD_SS2 | SS2:.PMMPanel.VirBReactivePowerPhaseA
SS2PMMPanelVirBReactivePowerPhaseB | REAL | IOD_SS2 | SS2:.PMMPanel.VirBReactivePowerPhaseB
SS2PMMPanelVirBReactivePowerPhaseC | REAL | IOD_SS2 | SS2:.PMMPanel.VirBReactivePowerPhaseC
SS2PMMPanelVirBTotalActivePower_kW | REAL | IOD_SS2 | SS2:.PMMPanel.VirBTotalActivePower_kW
SS2PMMPanelVirBTotalAparentPower_kVA | REAL | IOD_SS2 | SS2:.PMMPanel.VirBTotalAparentPower_kVA
SS2PMMPanelVirBTotalPowerFactor | REAL | IOD_SS2 | SS2:.PMMPanel.VirBTotalPowerFactor
SS2PMMPanelVirBTotalReactivePower_kVAR | REAL | IOD_SS2 | SS2:.PMMPanel.VirBTotalReactivePower_kVAR
SS2PMMPanelVirBVoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseAB_V
SS2PMMPanelVirBVoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseAN_V
SS2PMMPanelVirBVoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseBC_V
SS2PMMPanelVirBVoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseBN_V
SS2PMMPanelVirBVoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseCA_V
SS2PMMPanelVirBVoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VirBVoltageBetweenPhaseCN_V
SS2PMMPanelVoltageBetweenPhaseAB_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseAB_V
SS2PMMPanelVoltageBetweenPhaseAN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseAN_V
SS2PMMPanelVoltageBetweenPhaseBC_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseBC_V
SS2PMMPanelVoltageBetweenPhaseBN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseBN_V
SS2PMMPanelVoltageBetweenPhaseCA_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseCA_V
SS2PMMPanelVoltageBetweenPhaseCN_V | REAL | IOD_SS2 | SS2:.PMMPanel.VoltageBetweenPhaseCN_V
SS2SKTemp1 | REAL | IOD_SS2 | SS2:.SKTemp1
SS2SKTemp2 | REAL | IOD_SS2 | SS2:.SKTemp2
SS2SKTemp3 | REAL | IOD_SS2 | SS2:.SKTemp3
SS2SKTemp4 | REAL | IOD_SS2 | SS2:.SKTemp4
SS2SKVlaga1 | REAL | IOD_SS2 | SS2:.SKVlaga1
SS2SKVlaga2 | REAL | IOD_SS2 | SS2:.SKVlaga2
SS2SKVlaga3 | REAL | IOD_SS2 | SS2:.SKVlaga3
SS2SKVlaga4 | REAL | IOD_SS2 | SS2:.SKVlaga4
SS2TempZaAlarm1_2 | REAL | IOD_SS2 | SS2:.TempZaAlarm1_2
SS2TempZaAlarm3_4 | REAL | IOD_SS2 | SS2:.TempZaAlarm3_4
SS2TempZaAlarm5_6 | REAL | IOD_SS2 | SS2:.TempZaAlarm5_6
SS2TempZaAlarmTIA1 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA1
SS2TempZaAlarmTIA2 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA2
SS2TempZaAlarmTIA3 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA3
SS2TempZaAlarmTIA4 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA4
SS2TempZaVklopObehKlim1_2 | REAL | IOD_SS2 | SS2:.TempZaVklopObehKlim1_2
SS2TempZaVklopObehKlim3_4 | REAL | IOD_SS2 | SS2:.TempZaVklopObehKlim3_4
SS2TempZaVklopObehKlim3_4TIA3 | REAL | IOD_SS2 | SS2:.TempZaVklopObehKlim3_4TIA3
SS2TempZaVklopObehKlim5_6 | REAL | IOD_SS2 | SS2:.TempZaVklopObehKlim5_6
SS2TempZaVklopObehKlim5_6TIA3 | REAL | IOD_SS2 | SS2:.TempZaVklopObehKlim5_6TIA3
SS2SKTemp5 | REAL | IOD_SS2 | SS2:.SKTemp5
SS2SKTemp6 | REAL | IOD_SS2 | SS2:.SKTemp6
SS2SKVlaga5 | REAL | IOD_SS2 | SS2:.SKVlaga5
SS2SKVlaga6 | REAL | IOD_SS2 | SS2:.SKVlaga6
SS2TempZaAlarmTIA5 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA5
SS2TempZaAlarmTIA6 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA6
SS2SKTempServSoba1Povpr | REAL | IOD_SS2 | SS2:.SKTempServSoba1Povpr
SS2SKTempServSoba2Povpr | REAL | IOD_SS2 | SS2:.SKTempServSoba2Povpr
SS2TempZaAlarmTIA235 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA235
SS2TempZaAlarmTIA46 | REAL | IOD_SS2 | SS2:.TempZaAlarmTIA46
SS2Date_Time0 | STRING | IOD_SS2 | SS2:.Date_Time[0]
SS2Date_Time1 | STRING | IOD_SS2 | SS2:.Date_Time[1]
SS2Date_Time2 | STRING | IOD_SS2 | SS2:.Date_Time[2]
SS2Date_Time3 | STRING | IOD_SS2 | SS2:.Date_Time[3]
SS2UserName | STRING | IOD_SS2 | SS2:.UserName

## variable_3
SS2AlarmKlimat2_1_Napaka | DIGITAL | IOD_SS2_TCP | 1 | 00001 | AlarmKlimat2_1_Napaka
SS2AlarmKlimat2_2_Napaka | DIGITAL | IOD_SS2_TCP | 2 | 00002 | AlarmKlimat2_2_Napaka
SS2AlarmKlimat2_3_Napaka | DIGITAL | IOD_SS2_TCP | 3 | 00003 | AlarmKlimat2_3_Napaka
SS2AlarmKlimat2_4_Napaka | DIGITAL | IOD_SS2_TCP | 4 | 00004 | AlarmKlimat2_4_Napaka
SS2AlarmKlimat2_5_Napaka | DIGITAL | IOD_SS2_TCP | 5 | 00005 | AlarmKlimat2_5_Napaka
SS2AlarmKlimat2_6_Napaka | DIGITAL | IOD_SS2_TCP | 6 | 00006 | AlarmKlimat2_6_Napaka
SS2AlarmLAH1RazlitjeVode | DIGITAL | IOD_SS2_TCP | 7 | 00007 | AlarmLAH1RazlitjeVode
SS2AlarmLAH2RazlitjeVode | DIGITAL | IOD_SS2_TCP | 8 | 00008 | AlarmLAH2RazlitjeVode
SS2AlarmLAH3RazlitjeVode | DIGITAL | IOD_SS2_TCP | 9 | 00009 | AlarmLAH3RazlitjeVode
SS2AlarmPMM2x17nad8010 | DIGITAL | IOD_SS2_TCP | 10 | 00010 | AlarmPMM2x17nad80[10]
SS2AlarmPMM2x17nad8011 | DIGITAL | IOD_SS2_TCP | 11 | 00011 | AlarmPMM2x17nad80[11]
SS2AlarmPMM2x17nad8012 | DIGITAL | IOD_SS2_TCP | 12 | 00012 | AlarmPMM2x17nad80[12]
SS2AlarmPMM2x17nad8013 | DIGITAL | IOD_SS2_TCP | 13 | 00013 | AlarmPMM2x17nad80[13]
SS2AlarmPMM2x17nad8014 | DIGITAL | IOD_SS2_TCP | 14 | 00014 | AlarmPMM2x17nad80[14]
SS2AlarmPMM2x17nad8015 | DIGITAL | IOD_SS2_TCP | 15 | 00015 | AlarmPMM2x17nad80[15]
SS2AlarmPMM2x17nad8016 | DIGITAL | IOD_SS2_TCP | 16 | 00016 | AlarmPMM2x17nad80[16]
SS2AlarmPMM2x17nad8017 | DIGITAL | IOD_SS2_TCP | 17 | 00017 | AlarmPMM2x17nad80[17]
SS2AlarmPMM2x17nad8018 | DIGITAL | IOD_SS2_TCP | 18 | 00018 | AlarmPMM2x17nad80[18]
SS2AlarmPMM2x17nad8019 | DIGITAL | IOD_SS2_TCP | 19 | 00019 | AlarmPMM2x17nad80[19]
SS2AlarmPMM2x17nad801 | DIGITAL | IOD_SS2_TCP | 20 | 00020 | AlarmPMM2x17nad80[1]
SS2AlarmPMM2x17nad8020 | DIGITAL | IOD_SS2_TCP | 21 | 00021 | AlarmPMM2x17nad80[20]
SS2AlarmPMM2x17nad8021 | DIGITAL | IOD_SS2_TCP | 22 | 00022 | AlarmPMM2x17nad80[21]
SS2AlarmPMM2x17nad8022 | DIGITAL | IOD_SS2_TCP | 23 | 00023 | AlarmPMM2x17nad80[22]
SS2AlarmPMM2x17nad8023 | DIGITAL | IOD_SS2_TCP | 24 | 00024 | AlarmPMM2x17nad80[23]
SS2AlarmPMM2x17nad8024 | DIGITAL | IOD_SS2_TCP | 25 | 00025 | AlarmPMM2x17nad80[24]
SS2AlarmPMM2x17nad8025 | DIGITAL | IOD_SS2_TCP | 26 | 00026 | AlarmPMM2x17nad80[25]
SS2AlarmPMM2x17nad8026 | DIGITAL | IOD_SS2_TCP | 27 | 00027 | AlarmPMM2x17nad80[26]
SS2AlarmPMM2x17nad8027 | DIGITAL | IOD_SS2_TCP | 28 | 00028 | AlarmPMM2x17nad80[27]
SS2AlarmPMM2x17nad8028 | DIGITAL | IOD_SS2_TCP | 29 | 00029 | AlarmPMM2x17nad80[28]
SS2AlarmPMM2x17nad8029 | DIGITAL | IOD_SS2_TCP | 30 | 00030 | AlarmPMM2x17nad80[29]
SS2AlarmPMM2x17nad802 | DIGITAL | IOD_SS2_TCP | 31 | 00031 | AlarmPMM2x17nad80[2]
SS2AlarmPMM2x17nad8030 | DIGITAL | IOD_SS2_TCP | 32 | 00032 | AlarmPMM2x17nad80[30]
SS2AlarmPMM2x17nad8031 | DIGITAL | IOD_SS2_TCP | 33 | 00033 | AlarmPMM2x17nad80[31]
SS2AlarmPMM2x17nad8032 | DIGITAL | IOD_SS2_TCP | 34 | 00034 | AlarmPMM2x17nad80[32]
SS2AlarmPMM2x17nad8033 | DIGITAL | IOD_SS2_TCP | 35 | 00035 | AlarmPMM2x17nad80[33]
SS2AlarmPMM2x17nad8034 | DIGITAL | IOD_SS2_TCP | 36 | 00036 | AlarmPMM2x17nad80[34]
SS2AlarmPMM2x17nad8035 | DIGITAL | IOD_SS2_TCP | 37 | 00037 | AlarmPMM2x17nad80[35]
SS2AlarmPMM2x17nad8036 | DIGITAL | IOD_SS2_TCP | 38 | 00038 | AlarmPMM2x17nad80[36]
SS2AlarmPMM2x17nad8037 | DIGITAL | IOD_SS2_TCP | 39 | 00039 | AlarmPMM2x17nad80[37]
SS2AlarmPMM2x17nad8038 | DIGITAL | IOD_SS2_TCP | 40 | 00040 | AlarmPMM2x17nad80[38]
SS2AlarmPMM2x17nad8039 | DIGITAL | IOD_SS2_TCP | 41 | 00041 | AlarmPMM2x17nad80[39]
SS2AlarmPMM2x17nad803 | DIGITAL | IOD_SS2_TCP | 42 | 00042 | AlarmPMM2x17nad80[3]
SS2AlarmPMM2x17nad8040 | DIGITAL | IOD_SS2_TCP | 43 | 00043 | AlarmPMM2x17nad80[40]
SS2AlarmPMM2x17nad8041 | DIGITAL | IOD_SS2_TCP | 44 | 00044 | AlarmPMM2x17nad80[41]
SS2AlarmPMM2x17nad8042 | DIGITAL | IOD_SS2_TCP | 45 | 00045 | AlarmPMM2x17nad80[42]
SS2AlarmPMM2x17nad804 | DIGITAL | IOD_SS2_TCP | 46 | 00046 | AlarmPMM2x17nad80[4]
SS2AlarmPMM2x17nad805 | DIGITAL | IOD_SS2_TCP | 47 | 00047 | AlarmPMM2x17nad80[5]
SS2AlarmPMM2x17nad806 | DIGITAL | IOD_SS2_TCP | 48 | 00048 | AlarmPMM2x17nad80[6]
SS2AlarmPMM2x17nad807 | DIGITAL | IOD_SS2_TCP | 49 | 00049 | AlarmPMM2x17nad80[7]
SS2AlarmPMM2x17nad808 | DIGITAL | IOD_SS2_TCP | 50 | 00050 | AlarmPMM2x17nad80[8]
SS2AlarmPMM2x17nad809 | DIGITAL | IOD_SS2_TCP | 51 | 00051 | AlarmPMM2x17nad80[9]
SS2AlarmSinhronizacijaNOK | DIGITAL | IOD_SS2_TCP | 52 | 00052 | AlarmSinhronizacijaNOK
SS2AlarmSKTemp1_Previsoka | DIGITAL | IOD_SS2_TCP | 53 | 00053 | AlarmSKTemp1_Previsoka
SS2AlarmSKTemp2_Previsoka | DIGITAL | IOD_SS2_TCP | 54 | 00054 | AlarmSKTemp2_Previsoka
SS2AlarmSKTemp3_Previsoka | DIGITAL | IOD_SS2_TCP | 55 | 00055 | AlarmSKTemp3_Previsoka
SS2AlarmSKTemp4_Previsoka | DIGITAL | IOD_SS2_TCP | 56 | 00056 | AlarmSKTemp4_Previsoka
SS2AlarmTempTIA1Previsoka | DIGITAL | IOD_SS2_TCP | 57 | 00057 | AlarmTempTIA1Previsoka
SS2AlarmTempTIA2Previsoka | DIGITAL | IOD_SS2_TCP | 58 | 00058 | AlarmTempTIA2Previsoka
SS2AlarmTempTIA3Previsoka | DIGITAL | IOD_SS2_TCP | 59 | 00059 | AlarmTempTIA3Previsoka
SS2AlarmTempTIA4Previsoka | DIGITAL | IOD_SS2_TCP | 60 | 00060 | AlarmTempTIA4Previsoka
SS2AlarmUPSKrmOmara_Alarm | DIGITAL | IOD_SS2_TCP | 61 | 00061 | AlarmUPSKrmOmara_Alarm
SS2ComSCADA | DIGITAL | IOD_SS2_TCP | 62 | 00062 | ComSCADA
SS2ComSCADA1 | DIGITAL | IOD_SS2_TCP | 63 | 00063 | ComSCADA1
SS2ErrComKlima1 | DIGITAL | IOD_SS2_TCP | 64 | 00064 | ErrComKlima[1]
SS2ErrComKlima2 | DIGITAL | IOD_SS2_TCP | 65 | 00065 | ErrComKlima[2]
SS2ErrComKlima3 | DIGITAL | IOD_SS2_TCP | 66 | 00066 | ErrComKlima[3]
SS2ErrComKlima4 | DIGITAL | IOD_SS2_TCP | 67 | 00067 | ErrComKlima[4]
SS2ErrComKlima5 | DIGITAL | IOD_SS2_TCP | 68 | 00068 | ErrComKlima[5]
SS2ErrComKlima6 | DIGITAL | IOD_SS2_TCP | 69 | 00069 | ErrComKlima[6]
SS2ErrCommScada | DIGITAL | IOD_SS2_TCP | 70 | 00070 | ErrCommScada
SS2ErrComPanelPLC | DIGITAL | IOD_SS2_TCP | 71 | 00071 | ErrComPanelPLC
SS2ErrComPMM1 | DIGITAL | IOD_SS2_TCP | 72 | 00072 | ErrComPMM[1]
SS2ErrComPMM2 | DIGITAL | IOD_SS2_TCP | 73 | 00073 | ErrComPMM[2]
SS2ErrComPort2 | DIGITAL | IOD_SS2_TCP | 74 | 00074 | ErrComPort2
SS2ErrorComKlima1Error | DIGITAL | IOD_SS2_TCP | 75 | 00075 | ErrorComKlima[1].Error
SS2ErrorComKlima2Error | DIGITAL | IOD_SS2_TCP | 76 | 00076 | ErrorComKlima[2].Error
SS2ErrorComKlima3Error | DIGITAL | IOD_SS2_TCP | 77 | 00077 | ErrorComKlima[3].Error
SS2ErrorComKlima4Error | DIGITAL | IOD_SS2_TCP | 78 | 00078 | ErrorComKlima[4].Error
SS2ErrorComKlima5Error | DIGITAL | IOD_SS2_TCP | 79 | 00079 | ErrorComKlima[5].Error
SS2ErrorComKlima6Error | DIGITAL | IOD_SS2_TCP | 80 | 00080 | ErrorComKlima[6].Error
SS2ErrorComPMM1Error | DIGITAL | IOD_SS2_TCP | 81 | 00081 | ErrorComPMM[1].Error
SS2ErrorComPMM2Error | DIGITAL | IOD_SS2_TCP | 82 | 00082 | ErrorComPMM[2].Error
SS2Klima2_1_Onemogocena | DIGITAL | IOD_SS2_TCP | 83 | 00083 | Klima2_1_Onemogocena
SS2Klima2_2_Onemogocena | DIGITAL | IOD_SS2_TCP | 84 | 00084 | Klima2_2_Onemogocena
SS2Klima2_3_Onemogocena | DIGITAL | IOD_SS2_TCP | 85 | 00085 | Klima2_3_Onemogocena
SS2Klima2_4_Onemogocena | DIGITAL | IOD_SS2_TCP | 86 | 00086 | Klima2_4_Onemogocena
SS2Klima2_5_Onemogocena | DIGITAL | IOD_SS2_TCP | 87 | 00087 | Klima2_5_Onemogocena
SS2Klima2_6_Onemogocena | DIGITAL | IOD_SS2_TCP | 88 | 00088 | Klima2_6_Onemogocena
SS2Klima1IzhodniVentilator | DIGITAL | IOD_SS2_TCP | 89 | 00089 | Klima[1].IzhodniVentilator
SS2Klima1Kompresor1 | DIGITAL | IOD_SS2_TCP | 90 | 00090 | Klima[1].Kompresor1
SS2Klima1Kompresor2 | DIGITAL | IOD_SS2_TCP | 91 | 00091 | Klima[1].Kompresor2
SS2Klima1Razvlazevanje | DIGITAL | IOD_SS2_TCP | 92 | 00092 | Klima[1].Razvlazevanje
SS2Klima1SenzorjiStatus | DIGITAL | IOD_SS2_TCP | 93 | 00093 | Klima[1].SenzorjiStatus
SS2Klima1VentilGretjeOdpiranje | DIGITAL | IOD_SS2_TCP | 94 | 00094 | Klima[1].VentilGretjeOdpiranje
SS2Klima1VentilGretjeZapiranje | DIGITAL | IOD_SS2_TCP | 95 | 00095 | Klima[1].VentilGretjeZapiranje
SS2Klima1Vlazenje | DIGITAL | IOD_SS2_TCP | 96 | 00096 | Klima[1].Vlazenje
SS2Klima2IzhodniVentilator | DIGITAL | IOD_SS2_TCP | 97 | 00097 | Klima[2].IzhodniVentilator
SS2Klima2Kompresor1 | DIGITAL | IOD_SS2_TCP | 98 | 00098 | Klima[2].Kompresor1
SS2Klima2Kompresor2 | DIGITAL | IOD_SS2_TCP | 99 | 00099 | Klima[2].Kompresor2
SS2Klima2Razvlazevanje | DIGITAL | IOD_SS2_TCP | 100 | 00100 | Klima[2].Razvlazevanje
SS2Klima2SenzorjiStatus | DIGITAL | IOD_SS2_TCP | 101 | 00101 | Klima[2].SenzorjiStatus
SS2Klima2VentilGretjeOdpiranje | DIGITAL | IOD_SS2_TCP | 102 | 00102 | Klima[2].VentilGretjeOdpiranje
SS2Klima2VentilGretjeZapiranje | DIGITAL | IOD_SS2_TCP | 103 | 00103 | Klima[2].VentilGretjeZapiranje
SS2Klima2Vlazenje | DIGITAL | IOD_SS2_TCP | 104 | 00104 | Klima[2].Vlazenje
SS2Klima3IzhodniVentilator | DIGITAL | IOD_SS2_TCP | 105 | 00105 | Klima[3].IzhodniVentilator
SS2Klima3Kompresor1 | DIGITAL | IOD_SS2_TCP | 106 | 00106 | Klima[3].Kompresor1
SS2Klima3Kompresor2 | DIGITAL | IOD_SS2_TCP | 107 | 00107 | Klima[3].Kompresor2
SS2Klima3Razvlazevanje | DIGITAL | IOD_SS2_TCP | 108 | 00108 | Klima[3].Razvlazevanje
SS2Klima3SenzorjiStatus | DIGITAL | IOD_SS2_TCP | 109 | 00109 | Klima[3].SenzorjiStatus
SS2Klima3VentilGretjeOdpiranje | DIGITAL | IOD_SS2_TCP | 110 | 00110 | Klima[3].VentilGretjeOdpiranje
SS2Klima3VentilGretjeZapiranje | DIGITAL | IOD_SS2_TCP | 111 | 00111 | Klima[3].VentilGretjeZapiranje
SS2Klima3Vlazenje | DIGITAL | IOD_SS2_TCP | 112 | 00112 | Klima[3].Vlazenje
SS2Klima4IzhodniVentilator | DIGITAL | IOD_SS2_TCP | 113 | 00113 | Klima[4].IzhodniVentilator
SS2Klima4Kompresor1 | DIGITAL | IOD_SS2_TCP | 114 | 00114 | Klima[4].Kompresor1
SS2Klima4Kompresor2 | DIGITAL | IOD_SS2_TCP | 115 | 00115 | Klima[4].Kompresor2
SS2Klima4Razvlazevanje | DIGITAL | IOD_SS2_TCP | 116 | 00116 | Klima[4].Razvlazevanje
SS2Klima4SenzorjiStatus | DIGITAL | IOD_SS2_TCP | 117 | 00117 | Klima[4].SenzorjiStatus
SS2Klima4VentilGretjeOdpiranje | DIGITAL | IOD_SS2_TCP | 118 | 00118 | Klima[4].VentilGretjeOdpiranje
SS2Klima4VentilGretjeZapiranje | DIGITAL | IOD_SS2_TCP | 119 | 00119 | Klima[4].VentilGretjeZapiranje
SS2Klima4Vlazenje | DIGITAL | IOD_SS2_TCP | 120 | 00120 | Klima[4].Vlazenje
SS2Klima5IzhodniVentilator | DIGITAL | IOD_SS2_TCP | 121 | 00121 | Klima[5].IzhodniVentilator
SS2Klima5Kompresor1 | DIGITAL | IOD_SS2_TCP | 122 | 00122 | Klima[5].Kompresor1
SS2Klima5Kompresor2 | DIGITAL | IOD_SS2_TCP | 123 | 00123 | Klima[5].Kompresor2
SS2Klima5Razvlazevanje | DIGITAL | IOD_SS2_TCP | 124 | 00124 | Klima[5].Razvlazevanje
SS2Klima5SenzorjiStatus | DIGITAL | IOD_SS2_TCP | 125 | 00125 | Klima[5].SenzorjiStatus
SS2Klima5VentilGretjeOdpiranje | DIGITAL | IOD_SS2_TCP | 126 | 00126 | Klima[5].VentilGretjeOdpiranje
SS2Klima5VentilGretjeZapiranje | DIGITAL | IOD_SS2_TCP | 127 | 00127 | Klima[5].VentilGretjeZapiranje
SS2Klima5Vlazenje | DIGITAL | IOD_SS2_TCP | 128 | 00128 | Klima[5].Vlazenje
SS2Klima6IzhodniVentilator | DIGITAL | IOD_SS2_TCP | 129 | 00129 | Klima[6].IzhodniVentilator
SS2Klima6Kompresor1 | DIGITAL | IOD_SS2_TCP | 130 | 00130 | Klima[6].Kompresor1
SS2Klima6Kompresor2 | DIGITAL | IOD_SS2_TCP | 131 | 00131 | Klima[6].Kompresor2
SS2Klima6Razvlazevanje | DIGITAL | IOD_SS2_TCP | 132 | 00132 | Klima[6].Razvlazevanje
SS2Klima6SenzorjiStatus | DIGITAL | IOD_SS2_TCP | 133 | 00133 | Klima[6].SenzorjiStatus
SS2Klima6VentilGretjeOdpiranje | DIGITAL | IOD_SS2_TCP | 134 | 00134 | Klima[6].VentilGretjeOdpiranje
SS2Klima6VentilGretjeZapiranje | DIGITAL | IOD_SS2_TCP | 135 | 00135 | Klima[6].VentilGretjeZapiranje
SS2Klima6Vlazenje | DIGITAL | IOD_SS2_TCP | 136 | 00136 | Klima[6].Vlazenje
SS2KlimaError1AlarmKompresor1 | DIGITAL | IOD_SS2_TCP | 137 | 00137 | KlimaError[1].AlarmKompresor1
SS2KlimaError1AlarmKompresor2 | DIGITAL | IOD_SS2_TCP | 138 | 00138 | KlimaError[1].AlarmKompresor2
SS2KlimaError1FenThermalCutout | DIGITAL | IOD_SS2_TCP | 139 | 00139 | KlimaError[1].FenThermalCutout
SS2KlimaError1IzlivVode | DIGITAL | IOD_SS2_TCP | 140 | 00140 | KlimaError[1].IzlivVode
SS2KlimaError1Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 141 | 00141 | KlimaError[1].Kompresor1naMejiStevilaObrUr
SS2KlimaError1Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 142 | 00142 | KlimaError[1].Kompresor2naMejiStevilaObrUr
SS2KlimaError1NapakaPriPretokuVode | DIGITAL | IOD_SS2_TCP | 143 | 00143 | KlimaError[1].NapakaPriPretokuVode
SS2KlimaError1NapakaPriPretokuZraka | DIGITAL | IOD_SS2_TCP | 144 | 00144 | KlimaError[1].NapakaPriPretokuZraka
SS2KlimaError1NapakaSenzorVlaznosti | DIGITAL | IOD_SS2_TCP | 145 | 00145 | KlimaError[1].NapakaSenzorVlaznosti
SS2KlimaError1NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2_TCP | 146 | 00146 | KlimaError[1].NapakaTSTemperaturaProstora
SS2KlimaError1NapakaVlazilca | DIGITAL | IOD_SS2_TCP | 147 | 00147 | KlimaError[1].NapakaVlazilca
SS2KlimaError1NizekPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 148 | 00148 | KlimaError[1].NizekPritiskKompresor1
SS2KlimaError1NizekPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 149 | 00149 | KlimaError[1].NizekPritiskKompresor2
SS2KlimaError1NizkaTempVProstoru | DIGITAL | IOD_SS2_TCP | 150 | 00150 | KlimaError[1].NizkaTempVProstoru
SS2KlimaError1NizkaVlaznost | DIGITAL | IOD_SS2_TCP | 151 | 00151 | KlimaError[1].NizkaVlaznost
SS2KlimaError1PozarniAlarm | DIGITAL | IOD_SS2_TCP | 152 | 00152 | KlimaError[1].PozarniAlarm
SS2KlimaError1ThermalCutoutHeater1 | DIGITAL | IOD_SS2_TCP | 153 | 00153 | KlimaError[1].ThermalCutoutHeater1
SS2KlimaError1ThermalCutoutHeater2 | DIGITAL | IOD_SS2_TCP | 154 | 00154 | KlimaError[1].ThermalCutoutHeater2
SS2KlimaError1VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 155 | 00155 | KlimaError[1].VentilatorNaMejiStevilaObrUr
SS2KlimaError1VisokaTempVProstoru | DIGITAL | IOD_SS2_TCP | 156 | 00156 | KlimaError[1].VisokaTempVProstoru
SS2KlimaError1VisokaVlaznost | DIGITAL | IOD_SS2_TCP | 157 | 00157 | KlimaError[1].VisokaVlaznost
SS2KlimaError1VisokPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 158 | 00158 | KlimaError[1].VisokPritiskKompresor1
SS2KlimaError1VisokPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 159 | 00159 | KlimaError[1].VisokPritiskKompresor2
SS2KlimaError1ZamasenFilter | DIGITAL | IOD_SS2_TCP | 160 | 00160 | KlimaError[1].ZamasenFilter
SS2KlimaError1ZunanjiAlarm | DIGITAL | IOD_SS2_TCP | 161 | 00161 | KlimaError[1].ZunanjiAlarm
SS2KlimaError2AlarmKompresor1 | DIGITAL | IOD_SS2_TCP | 162 | 00162 | KlimaError[2].AlarmKompresor1
SS2KlimaError2AlarmKompresor2 | DIGITAL | IOD_SS2_TCP | 163 | 00163 | KlimaError[2].AlarmKompresor2
SS2KlimaError2FenThermalCutout | DIGITAL | IOD_SS2_TCP | 164 | 00164 | KlimaError[2].FenThermalCutout
SS2KlimaError2IzlivVode | DIGITAL | IOD_SS2_TCP | 165 | 00165 | KlimaError[2].IzlivVode
SS2KlimaError2Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 166 | 00166 | KlimaError[2].Kompresor1naMejiStevilaObrUr
SS2KlimaError2Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 167 | 00167 | KlimaError[2].Kompresor2naMejiStevilaObrUr
SS2KlimaError2NapakaPriPretokuVode | DIGITAL | IOD_SS2_TCP | 168 | 00168 | KlimaError[2].NapakaPriPretokuVode
SS2KlimaError2NapakaPriPretokuZraka | DIGITAL | IOD_SS2_TCP | 169 | 00169 | KlimaError[2].NapakaPriPretokuZraka
SS2KlimaError2NapakaSenzorVlaznosti | DIGITAL | IOD_SS2_TCP | 170 | 00170 | KlimaError[2].NapakaSenzorVlaznosti
SS2KlimaError2NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2_TCP | 171 | 00171 | KlimaError[2].NapakaTSTemperaturaProstora
SS2KlimaError2NapakaVlazilca | DIGITAL | IOD_SS2_TCP | 172 | 00172 | KlimaError[2].NapakaVlazilca
SS2KlimaError2NizekPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 173 | 00173 | KlimaError[2].NizekPritiskKompresor1
SS2KlimaError2NizekPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 174 | 00174 | KlimaError[2].NizekPritiskKompresor2
SS2KlimaError2NizkaTempVProstoru | DIGITAL | IOD_SS2_TCP | 175 | 00175 | KlimaError[2].NizkaTempVProstoru
SS2KlimaError2NizkaVlaznost | DIGITAL | IOD_SS2_TCP | 176 | 00176 | KlimaError[2].NizkaVlaznost
SS2KlimaError2PozarniAlarm | DIGITAL | IOD_SS2_TCP | 177 | 00177 | KlimaError[2].PozarniAlarm
SS2KlimaError2ThermalCutoutHeater1 | DIGITAL | IOD_SS2_TCP | 178 | 00178 | KlimaError[2].ThermalCutoutHeater1
SS2KlimaError2ThermalCutoutHeater2 | DIGITAL | IOD_SS2_TCP | 179 | 00179 | KlimaError[2].ThermalCutoutHeater2
SS2KlimaError2VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 180 | 00180 | KlimaError[2].VentilatorNaMejiStevilaObrUr
SS2KlimaError2VisokaTempVProstoru | DIGITAL | IOD_SS2_TCP | 181 | 00181 | KlimaError[2].VisokaTempVProstoru
SS2KlimaError2VisokaVlaznost | DIGITAL | IOD_SS2_TCP | 182 | 00182 | KlimaError[2].VisokaVlaznost
SS2KlimaError2VisokPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 183 | 00183 | KlimaError[2].VisokPritiskKompresor1
SS2KlimaError2VisokPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 184 | 00184 | KlimaError[2].VisokPritiskKompresor2
SS2KlimaError2ZamasenFilter | DIGITAL | IOD_SS2_TCP | 185 | 00185 | KlimaError[2].ZamasenFilter
SS2KlimaError2ZunanjiAlarm | DIGITAL | IOD_SS2_TCP | 186 | 00186 | KlimaError[2].ZunanjiAlarm
SS2KlimaError3AlarmKompresor1 | DIGITAL | IOD_SS2_TCP | 187 | 00187 | KlimaError[3].AlarmKompresor1
SS2KlimaError3AlarmKompresor2 | DIGITAL | IOD_SS2_TCP | 188 | 00188 | KlimaError[3].AlarmKompresor2
SS2KlimaError3FenThermalCutout | DIGITAL | IOD_SS2_TCP | 189 | 00189 | KlimaError[3].FenThermalCutout
SS2KlimaError3IzlivVode | DIGITAL | IOD_SS2_TCP | 190 | 00190 | KlimaError[3].IzlivVode
SS2KlimaError3Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 191 | 00191 | KlimaError[3].Kompresor1naMejiStevilaObrUr
SS2KlimaError3Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 192 | 00192 | KlimaError[3].Kompresor2naMejiStevilaObrUr
SS2KlimaError3NapakaPriPretokuVode | DIGITAL | IOD_SS2_TCP | 193 | 00193 | KlimaError[3].NapakaPriPretokuVode
SS2KlimaError3NapakaPriPretokuZraka | DIGITAL | IOD_SS2_TCP | 194 | 00194 | KlimaError[3].NapakaPriPretokuZraka
SS2KlimaError3NapakaSenzorVlaznosti | DIGITAL | IOD_SS2_TCP | 195 | 00195 | KlimaError[3].NapakaSenzorVlaznosti
SS2KlimaError3NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2_TCP | 196 | 00196 | KlimaError[3].NapakaTSTemperaturaProstora
SS2KlimaError3NapakaVlazilca | DIGITAL | IOD_SS2_TCP | 197 | 00197 | KlimaError[3].NapakaVlazilca
SS2KlimaError3NizekPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 198 | 00198 | KlimaError[3].NizekPritiskKompresor1
SS2KlimaError3NizekPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 199 | 00199 | KlimaError[3].NizekPritiskKompresor2
SS2KlimaError3NizkaTempVProstoru | DIGITAL | IOD_SS2_TCP | 200 | 00200 | KlimaError[3].NizkaTempVProstoru
SS2KlimaError3NizkaVlaznost | DIGITAL | IOD_SS2_TCP | 201 | 00201 | KlimaError[3].NizkaVlaznost
SS2KlimaError3PozarniAlarm | DIGITAL | IOD_SS2_TCP | 202 | 00202 | KlimaError[3].PozarniAlarm
SS2KlimaError3ThermalCutoutHeater1 | DIGITAL | IOD_SS2_TCP | 203 | 00203 | KlimaError[3].ThermalCutoutHeater1
SS2KlimaError3ThermalCutoutHeater2 | DIGITAL | IOD_SS2_TCP | 204 | 00204 | KlimaError[3].ThermalCutoutHeater2
SS2KlimaError3VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 205 | 00205 | KlimaError[3].VentilatorNaMejiStevilaObrUr
SS2KlimaError3VisokaTempVProstoru | DIGITAL | IOD_SS2_TCP | 206 | 00206 | KlimaError[3].VisokaTempVProstoru
SS2KlimaError3VisokaVlaznost | DIGITAL | IOD_SS2_TCP | 207 | 00207 | KlimaError[3].VisokaVlaznost
SS2KlimaError3VisokPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 208 | 00208 | KlimaError[3].VisokPritiskKompresor1
SS2KlimaError3VisokPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 209 | 00209 | KlimaError[3].VisokPritiskKompresor2
SS2KlimaError3ZamasenFilter | DIGITAL | IOD_SS2_TCP | 210 | 00210 | KlimaError[3].ZamasenFilter
SS2KlimaError3ZunanjiAlarm | DIGITAL | IOD_SS2_TCP | 211 | 00211 | KlimaError[3].ZunanjiAlarm
SS2KlimaError4AlarmKompresor1 | DIGITAL | IOD_SS2_TCP | 212 | 00212 | KlimaError[4].AlarmKompresor1
SS2KlimaError4AlarmKompresor2 | DIGITAL | IOD_SS2_TCP | 213 | 00213 | KlimaError[4].AlarmKompresor2
SS2KlimaError4FenThermalCutout | DIGITAL | IOD_SS2_TCP | 214 | 00214 | KlimaError[4].FenThermalCutout
SS2KlimaError4IzlivVode | DIGITAL | IOD_SS2_TCP | 215 | 00215 | KlimaError[4].IzlivVode
SS2KlimaError4Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 216 | 00216 | KlimaError[4].Kompresor1naMejiStevilaObrUr
SS2KlimaError4Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 217 | 00217 | KlimaError[4].Kompresor2naMejiStevilaObrUr
SS2KlimaError4NapakaPriPretokuVode | DIGITAL | IOD_SS2_TCP | 218 | 00218 | KlimaError[4].NapakaPriPretokuVode
SS2KlimaError4NapakaPriPretokuZraka | DIGITAL | IOD_SS2_TCP | 219 | 00219 | KlimaError[4].NapakaPriPretokuZraka
SS2KlimaError4NapakaSenzorVlaznosti | DIGITAL | IOD_SS2_TCP | 220 | 00220 | KlimaError[4].NapakaSenzorVlaznosti
SS2KlimaError4NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2_TCP | 221 | 00221 | KlimaError[4].NapakaTSTemperaturaProstora
SS2KlimaError4NapakaVlazilca | DIGITAL | IOD_SS2_TCP | 222 | 00222 | KlimaError[4].NapakaVlazilca
SS2KlimaError4NizekPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 223 | 00223 | KlimaError[4].NizekPritiskKompresor1
SS2KlimaError4NizekPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 224 | 00224 | KlimaError[4].NizekPritiskKompresor2
SS2KlimaError4NizkaTempVProstoru | DIGITAL | IOD_SS2_TCP | 225 | 00225 | KlimaError[4].NizkaTempVProstoru
SS2KlimaError4NizkaVlaznost | DIGITAL | IOD_SS2_TCP | 226 | 00226 | KlimaError[4].NizkaVlaznost
SS2KlimaError4PozarniAlarm | DIGITAL | IOD_SS2_TCP | 227 | 00227 | KlimaError[4].PozarniAlarm
SS2KlimaError4ThermalCutoutHeater1 | DIGITAL | IOD_SS2_TCP | 228 | 00228 | KlimaError[4].ThermalCutoutHeater1
SS2KlimaError4ThermalCutoutHeater2 | DIGITAL | IOD_SS2_TCP | 229 | 00229 | KlimaError[4].ThermalCutoutHeater2
SS2KlimaError4VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 230 | 00230 | KlimaError[4].VentilatorNaMejiStevilaObrUr
SS2KlimaError4VisokaTempVProstoru | DIGITAL | IOD_SS2_TCP | 231 | 00231 | KlimaError[4].VisokaTempVProstoru
SS2KlimaError4VisokaVlaznost | DIGITAL | IOD_SS2_TCP | 232 | 00232 | KlimaError[4].VisokaVlaznost
SS2KlimaError4VisokPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 233 | 00233 | KlimaError[4].VisokPritiskKompresor1
SS2KlimaError4VisokPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 234 | 00234 | KlimaError[4].VisokPritiskKompresor2
SS2KlimaError4ZamasenFilter | DIGITAL | IOD_SS2_TCP | 235 | 00235 | KlimaError[4].ZamasenFilter
SS2KlimaError4ZunanjiAlarm | DIGITAL | IOD_SS2_TCP | 236 | 00236 | KlimaError[4].ZunanjiAlarm
SS2KlimaError5AlarmKompresor1 | DIGITAL | IOD_SS2_TCP | 237 | 00237 | KlimaError[5].AlarmKompresor1
SS2KlimaError5AlarmKompresor2 | DIGITAL | IOD_SS2_TCP | 238 | 00238 | KlimaError[5].AlarmKompresor2
SS2KlimaError5FenThermalCutout | DIGITAL | IOD_SS2_TCP | 239 | 00239 | KlimaError[5].FenThermalCutout
SS2KlimaError5IzlivVode | DIGITAL | IOD_SS2_TCP | 240 | 00240 | KlimaError[5].IzlivVode
SS2KlimaError5Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 241 | 00241 | KlimaError[5].Kompresor1naMejiStevilaObrUr
SS2KlimaError5Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 242 | 00242 | KlimaError[5].Kompresor2naMejiStevilaObrUr
SS2KlimaError5NapakaPriPretokuVode | DIGITAL | IOD_SS2_TCP | 243 | 00243 | KlimaError[5].NapakaPriPretokuVode
SS2KlimaError5NapakaPriPretokuZraka | DIGITAL | IOD_SS2_TCP | 244 | 00244 | KlimaError[5].NapakaPriPretokuZraka
SS2KlimaError5NapakaSenzorVlaznosti | DIGITAL | IOD_SS2_TCP | 245 | 00245 | KlimaError[5].NapakaSenzorVlaznosti
SS2KlimaError5NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2_TCP | 246 | 00246 | KlimaError[5].NapakaTSTemperaturaProstora
SS2KlimaError5NapakaVlazilca | DIGITAL | IOD_SS2_TCP | 247 | 00247 | KlimaError[5].NapakaVlazilca
SS2KlimaError5NizekPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 248 | 00248 | KlimaError[5].NizekPritiskKompresor1
SS2KlimaError5NizekPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 249 | 00249 | KlimaError[5].NizekPritiskKompresor2
SS2KlimaError5NizkaTempVProstoru | DIGITAL | IOD_SS2_TCP | 250 | 00250 | KlimaError[5].NizkaTempVProstoru
SS2KlimaError5NizkaVlaznost | DIGITAL | IOD_SS2_TCP | 251 | 00251 | KlimaError[5].NizkaVlaznost
SS2KlimaError5PozarniAlarm | DIGITAL | IOD_SS2_TCP | 252 | 00252 | KlimaError[5].PozarniAlarm
SS2KlimaError5ThermalCutoutHeater1 | DIGITAL | IOD_SS2_TCP | 253 | 00253 | KlimaError[5].ThermalCutoutHeater1
SS2KlimaError5ThermalCutoutHeater2 | DIGITAL | IOD_SS2_TCP | 254 | 00254 | KlimaError[5].ThermalCutoutHeater2
SS2KlimaError5VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 255 | 00255 | KlimaError[5].VentilatorNaMejiStevilaObrUr
SS2KlimaError5VisokaTempVProstoru | DIGITAL | IOD_SS2_TCP | 256 | 00256 | KlimaError[5].VisokaTempVProstoru
SS2KlimaError5VisokaVlaznost | DIGITAL | IOD_SS2_TCP | 257 | 00257 | KlimaError[5].VisokaVlaznost
SS2KlimaError5VisokPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 258 | 00258 | KlimaError[5].VisokPritiskKompresor1
SS2KlimaError5VisokPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 259 | 00259 | KlimaError[5].VisokPritiskKompresor2
SS2KlimaError5ZamasenFilter | DIGITAL | IOD_SS2_TCP | 260 | 00260 | KlimaError[5].ZamasenFilter
SS2KlimaError5ZunanjiAlarm | DIGITAL | IOD_SS2_TCP | 261 | 00261 | KlimaError[5].ZunanjiAlarm
SS2KlimaError6AlarmKompresor1 | DIGITAL | IOD_SS2_TCP | 262 | 00262 | KlimaError[6].AlarmKompresor1
SS2KlimaError6AlarmKompresor2 | DIGITAL | IOD_SS2_TCP | 263 | 00263 | KlimaError[6].AlarmKompresor2
SS2KlimaError6FenThermalCutout | DIGITAL | IOD_SS2_TCP | 264 | 00264 | KlimaError[6].FenThermalCutout
SS2KlimaError6IzlivVode | DIGITAL | IOD_SS2_TCP | 265 | 00265 | KlimaError[6].IzlivVode
SS2KlimaError6Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 266 | 00266 | KlimaError[6].Kompresor1naMejiStevilaObrUr
SS2KlimaError6Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 267 | 00267 | KlimaError[6].Kompresor2naMejiStevilaObrUr
SS2KlimaError6NapakaPriPretokuVode | DIGITAL | IOD_SS2_TCP | 268 | 00268 | KlimaError[6].NapakaPriPretokuVode
SS2KlimaError6NapakaPriPretokuZraka | DIGITAL | IOD_SS2_TCP | 269 | 00269 | KlimaError[6].NapakaPriPretokuZraka
SS2KlimaError6NapakaSenzorVlaznosti | DIGITAL | IOD_SS2_TCP | 270 | 00270 | KlimaError[6].NapakaSenzorVlaznosti
SS2KlimaError6NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2_TCP | 271 | 00271 | KlimaError[6].NapakaTSTemperaturaProstora
SS2KlimaError6NapakaVlazilca | DIGITAL | IOD_SS2_TCP | 272 | 00272 | KlimaError[6].NapakaVlazilca
SS2KlimaError6NizekPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 273 | 00273 | KlimaError[6].NizekPritiskKompresor1
SS2KlimaError6NizekPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 274 | 00274 | KlimaError[6].NizekPritiskKompresor2
SS2KlimaError6NizkaTempVProstoru | DIGITAL | IOD_SS2_TCP | 275 | 00275 | KlimaError[6].NizkaTempVProstoru
SS2KlimaError6NizkaVlaznost | DIGITAL | IOD_SS2_TCP | 276 | 00276 | KlimaError[6].NizkaVlaznost
SS2KlimaError6PozarniAlarm | DIGITAL | IOD_SS2_TCP | 277 | 00277 | KlimaError[6].PozarniAlarm
SS2KlimaError6ThermalCutoutHeater1 | DIGITAL | IOD_SS2_TCP | 278 | 00278 | KlimaError[6].ThermalCutoutHeater1
SS2KlimaError6ThermalCutoutHeater2 | DIGITAL | IOD_SS2_TCP | 279 | 00279 | KlimaError[6].ThermalCutoutHeater2
SS2KlimaError6VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 280 | 00280 | KlimaError[6].VentilatorNaMejiStevilaObrUr
SS2KlimaError6VisokaTempVProstoru | DIGITAL | IOD_SS2_TCP | 281 | 00281 | KlimaError[6].VisokaTempVProstoru
SS2KlimaError6VisokaVlaznost | DIGITAL | IOD_SS2_TCP | 282 | 00282 | KlimaError[6].VisokaVlaznost
SS2KlimaError6VisokPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 283 | 00283 | KlimaError[6].VisokPritiskKompresor1
SS2KlimaError6VisokPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 284 | 00284 | KlimaError[6].VisokPritiskKompresor2
SS2KlimaError6ZamasenFilter | DIGITAL | IOD_SS2_TCP | 285 | 00285 | KlimaError[6].ZamasenFilter
SS2KlimaError6ZunanjiAlarm | DIGITAL | IOD_SS2_TCP | 286 | 00286 | KlimaError[6].ZunanjiAlarm
SS2NacDeloKlima1_2Avtom | DIGITAL | IOD_SS2_TCP | 287 | 00287 | NacDeloKlima1_2Avtom
SS2NacDeloKlima3_4Avtom | DIGITAL | IOD_SS2_TCP | 288 | 00288 | NacDeloKlima3_4Avtom
SS2NacDeloKlima5_6Avtom | DIGITAL | IOD_SS2_TCP | 289 | 00289 | NacDeloKlima5_6Avtom
SS2NapakaSenzorTemp1 | DIGITAL | IOD_SS2_TCP | 290 | 00290 | NapakaSenzorTemp1
SS2NapakaSenzorTemp2 | DIGITAL | IOD_SS2_TCP | 291 | 00291 | NapakaSenzorTemp2
SS2NapakaSenzorTemp3 | DIGITAL | IOD_SS2_TCP | 292 | 00292 | NapakaSenzorTemp3
SS2NapakaSenzorTemp4 | DIGITAL | IOD_SS2_TCP | 293 | 00293 | NapakaSenzorTemp4
SS2NapakaSenzorVlaga1 | DIGITAL | IOD_SS2_TCP | 294 | 00294 | NapakaSenzorVlaga1
SS2NapakaSenzorVlaga2 | DIGITAL | IOD_SS2_TCP | 295 | 00295 | NapakaSenzorVlaga2
SS2NapakaSenzorVlaga3 | DIGITAL | IOD_SS2_TCP | 296 | 00296 | NapakaSenzorVlaga3
SS2NapakaSenzorVlaga4 | DIGITAL | IOD_SS2_TCP | 297 | 00297 | NapakaSenzorVlaga4
SS2NastaviCasNaKrmilniku | DIGITAL | IOD_SS2_TCP | 298 | 00298 | NastaviCasNaKrmilniku
SS2NastavitevUreKrUspesna | DIGITAL | IOD_SS2_TCP | 299 | 00299 | NastavitevUreKrUspesna
SS2OpozoriloBaterijaPLC | DIGITAL | IOD_SS2_TCP | 300 | 00300 | OpozoriloBaterijaPLC
SS2OpozoriloPMM2x17med60in8010 | DIGITAL | IOD_SS2_TCP | 301 | 00301 | OpozoriloPMM2x17med60in80[10]
SS2OpozoriloPMM2x17med60in8011 | DIGITAL | IOD_SS2_TCP | 302 | 00302 | OpozoriloPMM2x17med60in80[11]
SS2OpozoriloPMM2x17med60in8012 | DIGITAL | IOD_SS2_TCP | 303 | 00303 | OpozoriloPMM2x17med60in80[12]
SS2OpozoriloPMM2x17med60in8013 | DIGITAL | IOD_SS2_TCP | 304 | 00304 | OpozoriloPMM2x17med60in80[13]
SS2OpozoriloPMM2x17med60in8014 | DIGITAL | IOD_SS2_TCP | 305 | 00305 | OpozoriloPMM2x17med60in80[14]
SS2OpozoriloPMM2x17med60in8015 | DIGITAL | IOD_SS2_TCP | 306 | 00306 | OpozoriloPMM2x17med60in80[15]
SS2OpozoriloPMM2x17med60in8016 | DIGITAL | IOD_SS2_TCP | 307 | 00307 | OpozoriloPMM2x17med60in80[16]
SS2OpozoriloPMM2x17med60in8017 | DIGITAL | IOD_SS2_TCP | 308 | 00308 | OpozoriloPMM2x17med60in80[17]
SS2OpozoriloPMM2x17med60in8018 | DIGITAL | IOD_SS2_TCP | 309 | 00309 | OpozoriloPMM2x17med60in80[18]
SS2OpozoriloPMM2x17med60in8019 | DIGITAL | IOD_SS2_TCP | 310 | 00310 | OpozoriloPMM2x17med60in80[19]
SS2OpozoriloPMM2x17med60in801 | DIGITAL | IOD_SS2_TCP | 311 | 00311 | OpozoriloPMM2x17med60in80[1]
SS2OpozoriloPMM2x17med60in8020 | DIGITAL | IOD_SS2_TCP | 312 | 00312 | OpozoriloPMM2x17med60in80[20]
SS2OpozoriloPMM2x17med60in8021 | DIGITAL | IOD_SS2_TCP | 313 | 00313 | OpozoriloPMM2x17med60in80[21]
SS2OpozoriloPMM2x17med60in8022 | DIGITAL | IOD_SS2_TCP | 314 | 00314 | OpozoriloPMM2x17med60in80[22]
SS2OpozoriloPMM2x17med60in8023 | DIGITAL | IOD_SS2_TCP | 315 | 00315 | OpozoriloPMM2x17med60in80[23]
SS2OpozoriloPMM2x17med60in8024 | DIGITAL | IOD_SS2_TCP | 316 | 00316 | OpozoriloPMM2x17med60in80[24]
SS2OpozoriloPMM2x17med60in8025 | DIGITAL | IOD_SS2_TCP | 317 | 00317 | OpozoriloPMM2x17med60in80[25]
SS2OpozoriloPMM2x17med60in8026 | DIGITAL | IOD_SS2_TCP | 318 | 00318 | OpozoriloPMM2x17med60in80[26]
SS2OpozoriloPMM2x17med60in8027 | DIGITAL | IOD_SS2_TCP | 319 | 00319 | OpozoriloPMM2x17med60in80[27]
SS2OpozoriloPMM2x17med60in8028 | DIGITAL | IOD_SS2_TCP | 320 | 00320 | OpozoriloPMM2x17med60in80[28]
SS2OpozoriloPMM2x17med60in8029 | DIGITAL | IOD_SS2_TCP | 321 | 00321 | OpozoriloPMM2x17med60in80[29]
SS2OpozoriloPMM2x17med60in802 | DIGITAL | IOD_SS2_TCP | 322 | 00322 | OpozoriloPMM2x17med60in80[2]
SS2OpozoriloPMM2x17med60in8030 | DIGITAL | IOD_SS2_TCP | 323 | 00323 | OpozoriloPMM2x17med60in80[30]
SS2OpozoriloPMM2x17med60in8031 | DIGITAL | IOD_SS2_TCP | 324 | 00324 | OpozoriloPMM2x17med60in80[31]
SS2OpozoriloPMM2x17med60in8032 | DIGITAL | IOD_SS2_TCP | 325 | 00325 | OpozoriloPMM2x17med60in80[32]
SS2OpozoriloPMM2x17med60in8033 | DIGITAL | IOD_SS2_TCP | 326 | 00326 | OpozoriloPMM2x17med60in80[33]
SS2OpozoriloPMM2x17med60in8034 | DIGITAL | IOD_SS2_TCP | 327 | 00327 | OpozoriloPMM2x17med60in80[34]
SS2OpozoriloPMM2x17med60in8035 | DIGITAL | IOD_SS2_TCP | 328 | 00328 | OpozoriloPMM2x17med60in80[35]
SS2OpozoriloPMM2x17med60in8036 | DIGITAL | IOD_SS2_TCP | 329 | 00329 | OpozoriloPMM2x17med60in80[36]
SS2OpozoriloPMM2x17med60in8037 | DIGITAL | IOD_SS2_TCP | 330 | 00330 | OpozoriloPMM2x17med60in80[37]
SS2OpozoriloPMM2x17med60in8038 | DIGITAL | IOD_SS2_TCP | 331 | 00331 | OpozoriloPMM2x17med60in80[38]
SS2OpozoriloPMM2x17med60in8039 | DIGITAL | IOD_SS2_TCP | 332 | 00332 | OpozoriloPMM2x17med60in80[39]
SS2OpozoriloPMM2x17med60in803 | DIGITAL | IOD_SS2_TCP | 333 | 00333 | OpozoriloPMM2x17med60in80[3]
SS2OpozoriloPMM2x17med60in8040 | DIGITAL | IOD_SS2_TCP | 334 | 00334 | OpozoriloPMM2x17med60in80[40]
SS2OpozoriloPMM2x17med60in8041 | DIGITAL | IOD_SS2_TCP | 335 | 00335 | OpozoriloPMM2x17med60in80[41]
SS2OpozoriloPMM2x17med60in8042 | DIGITAL | IOD_SS2_TCP | 336 | 00336 | OpozoriloPMM2x17med60in80[42]
SS2OpozoriloPMM2x17med60in804 | DIGITAL | IOD_SS2_TCP | 337 | 00337 | OpozoriloPMM2x17med60in80[4]
SS2OpozoriloPMM2x17med60in805 | DIGITAL | IOD_SS2_TCP | 338 | 00338 | OpozoriloPMM2x17med60in80[5]
SS2OpozoriloPMM2x17med60in806 | DIGITAL | IOD_SS2_TCP | 339 | 00339 | OpozoriloPMM2x17med60in80[6]
SS2OpozoriloPMM2x17med60in807 | DIGITAL | IOD_SS2_TCP | 340 | 00340 | OpozoriloPMM2x17med60in80[7]
SS2OpozoriloPMM2x17med60in808 | DIGITAL | IOD_SS2_TCP | 341 | 00341 | OpozoriloPMM2x17med60in80[8]
SS2OpozoriloPMM2x17med60in809 | DIGITAL | IOD_SS2_TCP | 342 | 00342 | OpozoriloPMM2x17med60in80[9]
SS2PhaseBool0 | DIGITAL | IOD_SS2_TCP | 343 | 00343 | PhaseBool[0]
SS2PhaseBool1 | DIGITAL | IOD_SS2_TCP | 344 | 00344 | PhaseBool[1]
SS2PhaseBool2 | DIGITAL | IOD_SS2_TCP | 345 | 00345 | PhaseBool[2]
SS2PhaseNext | DIGITAL | IOD_SS2_TCP | 346 | 00346 | PhaseNext
SS2PhasePrev | DIGITAL | IOD_SS2_TCP | 347 | 00347 | PhasePrev
SS2PMM1OverCurrentBetw1 | DIGITAL | IOD_SS2_TCP | 348 | 00348 | PMM1OverCurrentBetw[1]
SS2PMM1OverCurrentBetw2 | DIGITAL | IOD_SS2_TCP | 349 | 00349 | PMM1OverCurrentBetw[2]
SS2PMM1OverCurrentBetw3 | DIGITAL | IOD_SS2_TCP | 350 | 00350 | PMM1OverCurrentBetw[3]
SS2PMM1OverCurrentOver1 | DIGITAL | IOD_SS2_TCP | 351 | 00351 | PMM1OverCurrentOver[1]
SS2PMM1OverCurrentOver2 | DIGITAL | IOD_SS2_TCP | 352 | 00352 | PMM1OverCurrentOver[2]
SS2PMM1OverCurrentOver3 | DIGITAL | IOD_SS2_TCP | 353 | 00353 | PMM1OverCurrentOver[3]
SS2PMM1OverVoltage | DIGITAL | IOD_SS2_TCP | 354 | 00354 | PMM1OverVoltage
SS2PMM2OverCurrentBetw1 | DIGITAL | IOD_SS2_TCP | 355 | 00355 | PMM2OverCurrentBetw[1]
SS2PMM2OverCurrentBetw2 | DIGITAL | IOD_SS2_TCP | 356 | 00356 | PMM2OverCurrentBetw[2]
SS2PMM2OverCurrentBetw3 | DIGITAL | IOD_SS2_TCP | 357 | 00357 | PMM2OverCurrentBetw[3]
SS2PMM2OverCurrentOver1 | DIGITAL | IOD_SS2_TCP | 358 | 00358 | PMM2OverCurrentOver[1]
SS2PMM2OverCurrentOver2 | DIGITAL | IOD_SS2_TCP | 359 | 00359 | PMM2OverCurrentOver[2]
SS2PMM2OverCurrentOver3 | DIGITAL | IOD_SS2_TCP | 360 | 00360 | PMM2OverCurrentOver[3]
SS2PMM2OverVoltage | DIGITAL | IOD_SS2_TCP | 361 | 00361 | PMM2OverVoltage
SS2PMM2x17 | DIGITAL | IOD_SS2_TCP | 362 | 00362 | PMM2x17
SS2RocniVklopKlima1 | DIGITAL | IOD_SS2_TCP | 363 | 00363 | RocniVklopKlima1
SS2RocniVklopKlima2 | DIGITAL | IOD_SS2_TCP | 364 | 00364 | RocniVklopKlima2
SS2RocniVklopKlima3 | DIGITAL | IOD_SS2_TCP | 365 | 00365 | RocniVklopKlima3
SS2RocniVklopKlima4 | DIGITAL | IOD_SS2_TCP | 366 | 00366 | RocniVklopKlima4
SS2RocniVklopKlima5 | DIGITAL | IOD_SS2_TCP | 367 | 00367 | RocniVklopKlima5
SS2RocniVklopKlima6 | DIGITAL | IOD_SS2_TCP | 368 | 00368 | RocniVklopKlima6
SS2SinhronizacijaPanelOK | DIGITAL | IOD_SS2_TCP | 369 | 00369 | SinhronizacijaPanelOK
SS2SinhronizirajCas_Panel | DIGITAL | IOD_SS2_TCP | 370 | 00370 | SinhronizirajCas_Panel
SS2SkupneNapakeNaprav_Klima1 | DIGITAL | IOD_SS2_TCP | 371 | 00371 | SkupneNapakeNaprav_Klima1
SS2SkupneNapakeNaprav_Klima2 | DIGITAL | IOD_SS2_TCP | 372 | 00372 | SkupneNapakeNaprav_Klima2
SS2SkupneNapakeNaprav_Klima3 | DIGITAL | IOD_SS2_TCP | 373 | 00373 | SkupneNapakeNaprav_Klima3
SS2SkupneNapakeNaprav_Klima4 | DIGITAL | IOD_SS2_TCP | 374 | 00374 | SkupneNapakeNaprav_Klima4
SS2SkupneNapakeNaprav_Klima5 | DIGITAL | IOD_SS2_TCP | 375 | 00375 | SkupneNapakeNaprav_Klima5
SS2SkupneNapakeNaprav_Klima6 | DIGITAL | IOD_SS2_TCP | 376 | 00376 | SkupneNapakeNaprav_Klima6
SS2SkupneNapakeNaprav_Komunikacija | DIGITAL | IOD_SS2_TCP | 377 | 00377 | SkupneNapakeNaprav_Komunikacija
SS2SkupneNapakeNaprav_PMM17VirBVirA | DIGITAL | IOD_SS2_TCP | 378 | 00378 | SkupneNapakeNaprav_PMM17VirBVirA
SS2SkupneNapakeNaprav_PMM63VirBVirA | DIGITAL | IOD_SS2_TCP | 379 | 00379 | SkupneNapakeNaprav_PMM63VirBVirA
SS2SkupneNapakeNaprav_TempVlaga | DIGITAL | IOD_SS2_TCP | 380 | 00380 | SkupneNapakeNaprav_TempVlaga
SS2StanjeKlimat2_1_Delovanje | DIGITAL | IOD_SS2_TCP | 381 | 00381 | StanjeKlimat2_1_Delovanje
SS2StanjeKlimat2_2_Delovanje | DIGITAL | IOD_SS2_TCP | 382 | 00382 | StanjeKlimat2_2_Delovanje
SS2StanjeKlimat2_3_Delovanje | DIGITAL | IOD_SS2_TCP | 383 | 00383 | StanjeKlimat2_3_Delovanje
SS2StanjeKlimat2_4_Delovanje | DIGITAL | IOD_SS2_TCP | 384 | 00384 | StanjeKlimat2_4_Delovanje
SS2StanjeKlimat2_5_Delovanje | DIGITAL | IOD_SS2_TCP | 385 | 00385 | StanjeKlimat2_5_Delovanje
SS2StanjeKlimat2_6_Delovanje | DIGITAL | IOD_SS2_TCP | 386 | 00386 | StanjeKlimat2_6_Delovanje
SS2StanjeUPSKrmOmara_BaterijskiNacin | DIGITAL | IOD_SS2_TCP | 387 | 00387 | StanjeUPSKrmOmara_BaterijskiNacin
SS2StanjeUPSKrmOmara_Polnjenje | DIGITAL | IOD_SS2_TCP | 388 | 00388 | StanjeUPSKrmOmara_Polnjenje
SS2UserLoggedIn | DIGITAL | IOD_SS2_TCP | 389 | 00389 | UserLoggedIn
SS2XVH_AlarmOn | DIGITAL | IOD_SS2_TCP | 390 | 00390 | XVH_AlarmOn
SS2Klimat2_1_Vklop | DIGITAL | IOD_SS2_TCP | 391 | 00391 | Klimat2_1_Vklop
SS2Klimat2_2_Vklop | DIGITAL | IOD_SS2_TCP | 392 | 00392 | Klimat2_2_Vklop
SS2Klimat2_3_Vklop | DIGITAL | IOD_SS2_TCP | 393 | 00393 | Klimat2_3_Vklop
SS2Klimat2_4_Vklop | DIGITAL | IOD_SS2_TCP | 394 | 00394 | Klimat2_4_Vklop
SS2Klimat2_5_Vklop | DIGITAL | IOD_SS2_TCP | 395 | 00395 | Klimat2_5_Vklop
SS2Klimat2_6_Vklop | DIGITAL | IOD_SS2_TCP | 396 | 00396 | Klimat2_6_Vklop
SS2ErrCommScada2 | DIGITAL | IOD_SS2_TCP | 397 | 00397 | ErrCommScada2
SS2ComSCADA2 | DIGITAL | IOD_SS2_TCP | 398 | 00398 | ComSCADA2
SS2ComSCADA3 | DIGITAL | IOD_SS2_TCP | 399 | 00399 | ComSCADA3
SS2AlarmSKTemp5_Previsoka | DIGITAL | IOD_SS2_TCP | 400 | 00400 | AlarmSKTemp5_Previsoka
SS2AlarmSKTemp6_Previsoka | DIGITAL | IOD_SS2_TCP | 401 | 00401 | AlarmSKTemp6_Previsoka
SS2AlarmTempTIA5Previsoka | DIGITAL | IOD_SS2_TCP | 402 | 00402 | AlarmTempTIA5Previsoka
SS2AlarmTempTIA6Previsoka | DIGITAL | IOD_SS2_TCP | 403 | 00403 | AlarmTempTIA6Previsoka
SS2NapakaSenzorTemp5 | DIGITAL | IOD_SS2_TCP | 404 | 00404 | NapakaSenzorTemp5
SS2NapakaSenzorTemp6 | DIGITAL | IOD_SS2_TCP | 405 | 00405 | NapakaSenzorTemp6
SS2NapakaSenzorVlaga5 | DIGITAL | IOD_SS2_TCP | 406 | 00406 | NapakaSenzorVlaga5
SS2NapakaSenzorVlaga6 | DIGITAL | IOD_SS2_TCP | 407 | 00407 | NapakaSenzorVlaga6
SS2AlarmTempTIA235Previsoka | DIGITAL | IOD_SS2_TCP | 408 | 00408 | AlarmTempTIA235Previsoka
SS2AlarmTempTIA46Previsoka | DIGITAL | IOD_SS2_TCP | 409 | 00409 | AlarmTempTIA46Previsoka
SS2DatumCasDan | INT | IOD_SS2_TCP | 1 | 40001 | DatumCas.Dan | BYTE
SS2DatumCasLeto | INT | IOD_SS2_TCP | 2 | 40002 | DatumCas.Leto | BYTE
SS2DatumCasLeto2 | INT | IOD_SS2_TCP | 3 | 40003 | DatumCas.Leto2
SS2DatumCasMesec | INT | IOD_SS2_TCP | 4 | 40004 | DatumCas.Mesec | BYTE
SS2DatumCasMinuta | INT | IOD_SS2_TCP | 5 | 40005 | DatumCas.Minuta | BYTE
SS2DatumCasSekunda | INT | IOD_SS2_TCP | 6 | 40006 | DatumCas.Sekunda | BYTE
SS2DatumCasUra | INT | IOD_SS2_TCP | 7 | 40007 | DatumCas.Ura | BYTE
SS2ErrorComKlima1Status | INT | IOD_SS2_TCP | 8 | 40008 | ErrorComKlima[1].Status
SS2ErrorComKlima2Status | INT | IOD_SS2_TCP | 9 | 40009 | ErrorComKlima[2].Status
SS2ErrorComKlima3Status | INT | IOD_SS2_TCP | 10 | 40010 | ErrorComKlima[3].Status
SS2ErrorComKlima4Status | INT | IOD_SS2_TCP | 11 | 40011 | ErrorComKlima[4].Status
SS2ErrorComKlima5Status | INT | IOD_SS2_TCP | 12 | 40012 | ErrorComKlima[5].Status
SS2ErrorComKlima6Status | INT | IOD_SS2_TCP | 13 | 40013 | ErrorComKlima[6].Status
SS2ErrorComPMM1Status | INT | IOD_SS2_TCP | 14 | 40014 | ErrorComPMM[1].Status
SS2ErrorComPMM2Status | INT | IOD_SS2_TCP | 15 | 40015 | ErrorComPMM[2].Status
SS2Klima1GrelecStatus | INT | IOD_SS2_TCP | 16 | 40016 | Klima[1].GrelecStatus | BYTE
SS2Klima1IzhodniVentStatus | INT | IOD_SS2_TCP | 17 | 40017 | Klima[1].IzhodniVentStatus | BYTE
SS2Klima1KompresorStatus | INT | IOD_SS2_TCP | 18 | 40018 | Klima[1].KompresorStatus | BYTE
SS2Klima1NacinRazvlaz | INT | IOD_SS2_TCP | 19 | 40019 | Klima[1].NacinRazvlaz
SS2Klima1VlazilecStatus | INT | IOD_SS2_TCP | 20 | 40020 | Klima[1].VlazilecStatus | BYTE
SS2Klima2GrelecStatus | INT | IOD_SS2_TCP | 21 | 40021 | Klima[2].GrelecStatus | BYTE
SS2Klima2IzhodniVentStatus | INT | IOD_SS2_TCP | 22 | 40022 | Klima[2].IzhodniVentStatus | BYTE
SS2Klima2KompresorStatus | INT | IOD_SS2_TCP | 23 | 40023 | Klima[2].KompresorStatus | BYTE
SS2Klima2NacinRazvlaz | INT | IOD_SS2_TCP | 24 | 40024 | Klima[2].NacinRazvlaz
SS2Klima2VlazilecStatus | INT | IOD_SS2_TCP | 25 | 40025 | Klima[2].VlazilecStatus | BYTE
SS2Klima3GrelecStatus | INT | IOD_SS2_TCP | 26 | 40026 | Klima[3].GrelecStatus | BYTE
SS2Klima3IzhodniVentStatus | INT | IOD_SS2_TCP | 27 | 40027 | Klima[3].IzhodniVentStatus | BYTE
SS2Klima3KompresorStatus | INT | IOD_SS2_TCP | 28 | 40028 | Klima[3].KompresorStatus | BYTE
SS2Klima3NacinRazvlaz | INT | IOD_SS2_TCP | 29 | 40029 | Klima[3].NacinRazvlaz
SS2Klima3VlazilecStatus | INT | IOD_SS2_TCP | 30 | 40030 | Klima[3].VlazilecStatus | BYTE
SS2Klima4GrelecStatus | INT | IOD_SS2_TCP | 31 | 40031 | Klima[4].GrelecStatus | BYTE
SS2Klima4IzhodniVentStatus | INT | IOD_SS2_TCP | 32 | 40032 | Klima[4].IzhodniVentStatus | BYTE
SS2Klima4KompresorStatus | INT | IOD_SS2_TCP | 33 | 40033 | Klima[4].KompresorStatus | BYTE
SS2Klima4NacinRazvlaz | INT | IOD_SS2_TCP | 34 | 40034 | Klima[4].NacinRazvlaz
SS2Klima4VlazilecStatus | INT | IOD_SS2_TCP | 35 | 40035 | Klima[4].VlazilecStatus | BYTE
SS2Klima5GrelecStatus | INT | IOD_SS2_TCP | 36 | 40036 | Klima[5].GrelecStatus | BYTE
SS2Klima5IzhodniVentStatus | INT | IOD_SS2_TCP | 37 | 40037 | Klima[5].IzhodniVentStatus | BYTE
SS2Klima5KompresorStatus | INT | IOD_SS2_TCP | 38 | 40038 | Klima[5].KompresorStatus | BYTE
SS2Klima5NacinRazvlaz | INT | IOD_SS2_TCP | 39 | 40039 | Klima[5].NacinRazvlaz
SS2Klima5VlazilecStatus | INT | IOD_SS2_TCP | 40 | 40040 | Klima[5].VlazilecStatus | BYTE
SS2Klima6GrelecStatus | INT | IOD_SS2_TCP | 41 | 40041 | Klima[6].GrelecStatus | BYTE
SS2Klima6IzhodniVentStatus | INT | IOD_SS2_TCP | 42 | 40042 | Klima[6].IzhodniVentStatus | BYTE
SS2Klima6KompresorStatus | INT | IOD_SS2_TCP | 43 | 40043 | Klima[6].KompresorStatus | BYTE
SS2Klima6NacinRazvlaz | INT | IOD_SS2_TCP | 44 | 40044 | Klima[6].NacinRazvlaz
SS2Klima6VlazilecStatus | INT | IOD_SS2_TCP | 45 | 40045 | Klima[6].VlazilecStatus | BYTE
SS2OznakeFaz10 | INT | IOD_SS2_TCP | 46 | 40046 | OznakeFaz[10] | BYTE
SS2OznakeFaz11 | INT | IOD_SS2_TCP | 47 | 40047 | OznakeFaz[11] | BYTE
SS2OznakeFaz12 | INT | IOD_SS2_TCP | 48 | 40048 | OznakeFaz[12] | BYTE
SS2OznakeFaz13 | INT | IOD_SS2_TCP | 49 | 40049 | OznakeFaz[13] | BYTE
SS2OznakeFaz14 | INT | IOD_SS2_TCP | 50 | 40050 | OznakeFaz[14] | BYTE
SS2OznakeFaz1 | INT | IOD_SS2_TCP | 51 | 40051 | OznakeFaz[1] | BYTE
SS2OznakeFaz2 | INT | IOD_SS2_TCP | 52 | 40052 | OznakeFaz[2] | BYTE
SS2OznakeFaz3 | INT | IOD_SS2_TCP | 53 | 40053 | OznakeFaz[3] | BYTE
SS2OznakeFaz4 | INT | IOD_SS2_TCP | 54 | 40054 | OznakeFaz[4] | BYTE
SS2OznakeFaz5 | INT | IOD_SS2_TCP | 55 | 40055 | OznakeFaz[5] | BYTE
SS2OznakeFaz6 | INT | IOD_SS2_TCP | 56 | 40056 | OznakeFaz[6] | BYTE
SS2OznakeFaz7 | INT | IOD_SS2_TCP | 57 | 40057 | OznakeFaz[7] | BYTE
SS2OznakeFaz8 | INT | IOD_SS2_TCP | 58 | 40058 | OznakeFaz[8] | BYTE
SS2OznakeFaz9 | INT | IOD_SS2_TCP | 59 | 40059 | OznakeFaz[9] | BYTE
SS2PhaseNo | INT | IOD_SS2_TCP | 60 | 40060 | PhaseNo | BYTE
SS2PMM1AlarmPhase1C01_16_60to80 | INT | IOD_SS2_TCP | 61 | 40061 | PMM[1].AlarmPhase[1].C01_16_60to80 | BYTE
SS2PMM1AlarmPhase1C01_16_over80 | INT | IOD_SS2_TCP | 62 | 40062 | PMM[1].AlarmPhase[1].C01_16_over80 | BYTE
SS2PMM1AlarmPhase1C17_32_60to80 | INT | IOD_SS2_TCP | 63 | 40063 | PMM[1].AlarmPhase[1].C17_32_60to80 | BYTE
SS2PMM1AlarmPhase1C17_32_over80 | INT | IOD_SS2_TCP | 64 | 40064 | PMM[1].AlarmPhase[1].C17_32_over80 | BYTE
SS2PMM1AlarmPhase1C33_42_60to80 | INT | IOD_SS2_TCP | 65 | 40065 | PMM[1].AlarmPhase[1].C33_42_60to80 | BYTE
SS2PMM1AlarmPhase1C33_42_over80 | INT | IOD_SS2_TCP | 66 | 40066 | PMM[1].AlarmPhase[1].C33_42_over80 | BYTE
SS2PMM1AlarmPhase1GlobalAlarmReg | INT | IOD_SS2_TCP | 67 | 40067 | PMM[1].AlarmPhase[1].GlobalAlarmReg
SS2PMM1AlarmPhase2C01_16_60to80 | INT | IOD_SS2_TCP | 68 | 40068 | PMM[1].AlarmPhase[2].C01_16_60to80 | BYTE
SS2PMM1AlarmPhase2C01_16_over80 | INT | IOD_SS2_TCP | 69 | 40069 | PMM[1].AlarmPhase[2].C01_16_over80 | BYTE
SS2PMM1AlarmPhase2C17_32_60to80 | INT | IOD_SS2_TCP | 70 | 40070 | PMM[1].AlarmPhase[2].C17_32_60to80 | BYTE
SS2PMM1AlarmPhase2C17_32_over80 | INT | IOD_SS2_TCP | 71 | 40071 | PMM[1].AlarmPhase[2].C17_32_over80 | BYTE
SS2PMM1AlarmPhase2C33_42_60to80 | INT | IOD_SS2_TCP | 72 | 40072 | PMM[1].AlarmPhase[2].C33_42_60to80 | BYTE
SS2PMM1AlarmPhase2C33_42_over80 | INT | IOD_SS2_TCP | 73 | 40073 | PMM[1].AlarmPhase[2].C33_42_over80 | BYTE
SS2PMM1AlarmPhase2GlobalAlarmReg | INT | IOD_SS2_TCP | 74 | 40074 | PMM[1].AlarmPhase[2].GlobalAlarmReg
SS2PMM1AlarmPhase3C01_16_60to80 | INT | IOD_SS2_TCP | 75 | 40075 | PMM[1].AlarmPhase[3].C01_16_60to80 | BYTE
SS2PMM1AlarmPhase3C01_16_over80 | INT | IOD_SS2_TCP | 76 | 40076 | PMM[1].AlarmPhase[3].C01_16_over80 | BYTE
SS2PMM1AlarmPhase3C17_32_60to80 | INT | IOD_SS2_TCP | 77 | 40077 | PMM[1].AlarmPhase[3].C17_32_60to80 | BYTE
SS2PMM1AlarmPhase3C17_32_over80 | INT | IOD_SS2_TCP | 78 | 40078 | PMM[1].AlarmPhase[3].C17_32_over80 | BYTE
SS2PMM1AlarmPhase3C33_42_60to80 | INT | IOD_SS2_TCP | 79 | 40079 | PMM[1].AlarmPhase[3].C33_42_60to80 | BYTE
SS2PMM1AlarmPhase3C33_42_over80 | INT | IOD_SS2_TCP | 80 | 40080 | PMM[1].AlarmPhase[3].C33_42_over80 | BYTE
SS2PMM1AlarmPhase3GlobalAlarmReg | INT | IOD_SS2_TCP | 81 | 40081 | PMM[1].AlarmPhase[3].GlobalAlarmReg
SS2PMM2AlarmPhase1C01_16_60to80 | INT | IOD_SS2_TCP | 82 | 40082 | PMM[2].AlarmPhase[1].C01_16_60to80 | BYTE
SS2PMM2AlarmPhase1C01_16_over80 | INT | IOD_SS2_TCP | 83 | 40083 | PMM[2].AlarmPhase[1].C01_16_over80 | BYTE
SS2PMM2AlarmPhase1C17_32_60to80 | INT | IOD_SS2_TCP | 84 | 40084 | PMM[2].AlarmPhase[1].C17_32_60to80 | BYTE
SS2PMM2AlarmPhase1C17_32_over80 | INT | IOD_SS2_TCP | 85 | 40085 | PMM[2].AlarmPhase[1].C17_32_over80 | BYTE
SS2PMM2AlarmPhase1C33_42_60to80 | INT | IOD_SS2_TCP | 86 | 40086 | PMM[2].AlarmPhase[1].C33_42_60to80 | BYTE
SS2PMM2AlarmPhase1C33_42_over80 | INT | IOD_SS2_TCP | 87 | 40087 | PMM[2].AlarmPhase[1].C33_42_over80 | BYTE
SS2PMM2AlarmPhase1GlobalAlarmReg | INT | IOD_SS2_TCP | 88 | 40088 | PMM[2].AlarmPhase[1].GlobalAlarmReg
SS2PMM2AlarmPhase2C01_16_60to80 | INT | IOD_SS2_TCP | 89 | 40089 | PMM[2].AlarmPhase[2].C01_16_60to80 | BYTE
SS2PMM2AlarmPhase2C01_16_over80 | INT | IOD_SS2_TCP | 90 | 40090 | PMM[2].AlarmPhase[2].C01_16_over80 | BYTE
SS2PMM2AlarmPhase2C17_32_60to80 | INT | IOD_SS2_TCP | 91 | 40091 | PMM[2].AlarmPhase[2].C17_32_60to80 | BYTE
SS2PMM2AlarmPhase2C17_32_over80 | INT | IOD_SS2_TCP | 92 | 40092 | PMM[2].AlarmPhase[2].C17_32_over80 | BYTE
SS2PMM2AlarmPhase2C33_42_60to80 | INT | IOD_SS2_TCP | 93 | 40093 | PMM[2].AlarmPhase[2].C33_42_60to80 | BYTE
SS2PMM2AlarmPhase2C33_42_over80 | INT | IOD_SS2_TCP | 94 | 40094 | PMM[2].AlarmPhase[2].C33_42_over80 | BYTE
SS2PMM2AlarmPhase2GlobalAlarmReg | INT | IOD_SS2_TCP | 95 | 40095 | PMM[2].AlarmPhase[2].GlobalAlarmReg
SS2PMM2AlarmPhase3C01_16_60to80 | INT | IOD_SS2_TCP | 96 | 40096 | PMM[2].AlarmPhase[3].C01_16_60to80 | BYTE
SS2PMM2AlarmPhase3C01_16_over80 | INT | IOD_SS2_TCP | 97 | 40097 | PMM[2].AlarmPhase[3].C01_16_over80 | BYTE
SS2PMM2AlarmPhase3C17_32_60to80 | INT | IOD_SS2_TCP | 98 | 40098 | PMM[2].AlarmPhase[3].C17_32_60to80 | BYTE
SS2PMM2AlarmPhase3C17_32_over80 | INT | IOD_SS2_TCP | 99 | 40099 | PMM[2].AlarmPhase[3].C17_32_over80 | BYTE
SS2PMM2AlarmPhase3C33_42_60to80 | INT | IOD_SS2_TCP | 100 | 40100 | PMM[2].AlarmPhase[3].C33_42_60to80 | BYTE
SS2PMM2AlarmPhase3C33_42_over80 | INT | IOD_SS2_TCP | 101 | 40101 | PMM[2].AlarmPhase[3].C33_42_over80 | BYTE
SS2PMM2AlarmPhase3GlobalAlarmReg | INT | IOD_SS2_TCP | 102 | 40102 | PMM[2].AlarmPhase[3].GlobalAlarmReg
SS2PMMPanelAlarmPhase1C01_16_60to80 | INT | IOD_SS2_TCP | 103 | 40103 | PMMPanel.AlarmPhase[1].C01_16_60to80 | BYTE
SS2PMMPanelAlarmPhase1C01_16_over80 | INT | IOD_SS2_TCP | 104 | 40104 | PMMPanel.AlarmPhase[1].C01_16_over80 | BYTE
SS2PMMPanelAlarmPhase1C17_32_60to80 | INT | IOD_SS2_TCP | 105 | 40105 | PMMPanel.AlarmPhase[1].C17_32_60to80 | BYTE
SS2PMMPanelAlarmPhase1C17_32_over80 | INT | IOD_SS2_TCP | 106 | 40106 | PMMPanel.AlarmPhase[1].C17_32_over80 | BYTE
SS2PMMPanelAlarmPhase1C33_42_60to80 | INT | IOD_SS2_TCP | 107 | 40107 | PMMPanel.AlarmPhase[1].C33_42_60to80 | BYTE
SS2PMMPanelAlarmPhase1C33_42_over80 | INT | IOD_SS2_TCP | 108 | 40108 | PMMPanel.AlarmPhase[1].C33_42_over80 | BYTE
SS2PMMPanelAlarmPhase1GlobalAlarmReg | INT | IOD_SS2_TCP | 109 | 40109 | PMMPanel.AlarmPhase[1].GlobalAlarmReg
SS2PMMPanelAlarmPhase2C01_16_60to80 | INT | IOD_SS2_TCP | 110 | 40110 | PMMPanel.AlarmPhase[2].C01_16_60to80 | BYTE
SS2PMMPanelAlarmPhase2C01_16_over80 | INT | IOD_SS2_TCP | 111 | 40111 | PMMPanel.AlarmPhase[2].C01_16_over80 | BYTE
SS2PMMPanelAlarmPhase2C17_32_60to80 | INT | IOD_SS2_TCP | 112 | 40112 | PMMPanel.AlarmPhase[2].C17_32_60to80 | BYTE
SS2PMMPanelAlarmPhase2C17_32_over80 | INT | IOD_SS2_TCP | 113 | 40113 | PMMPanel.AlarmPhase[2].C17_32_over80 | BYTE
SS2PMMPanelAlarmPhase2C33_42_60to80 | INT | IOD_SS2_TCP | 114 | 40114 | PMMPanel.AlarmPhase[2].C33_42_60to80 | BYTE
SS2PMMPanelAlarmPhase2C33_42_over80 | INT | IOD_SS2_TCP | 115 | 40115 | PMMPanel.AlarmPhase[2].C33_42_over80 | BYTE
SS2PMMPanelAlarmPhase2GlobalAlarmReg | INT | IOD_SS2_TCP | 116 | 40116 | PMMPanel.AlarmPhase[2].GlobalAlarmReg
SS2PMMPanelAlarmPhase3C01_16_60to80 | INT | IOD_SS2_TCP | 117 | 40117 | PMMPanel.AlarmPhase[3].C01_16_60to80 | BYTE
SS2PMMPanelAlarmPhase3C01_16_over80 | INT | IOD_SS2_TCP | 118 | 40118 | PMMPanel.AlarmPhase[3].C01_16_over80 | BYTE
SS2PMMPanelAlarmPhase3C17_32_60to80 | INT | IOD_SS2_TCP | 119 | 40119 | PMMPanel.AlarmPhase[3].C17_32_60to80 | BYTE
SS2PMMPanelAlarmPhase3C17_32_over80 | INT | IOD_SS2_TCP | 120 | 40120 | PMMPanel.AlarmPhase[3].C17_32_over80 | BYTE
SS2PMMPanelAlarmPhase3C33_42_60to80 | INT | IOD_SS2_TCP | 121 | 40121 | PMMPanel.AlarmPhase[3].C33_42_60to80 | BYTE
SS2PMMPanelAlarmPhase3C33_42_over80 | INT | IOD_SS2_TCP | 122 | 40122 | PMMPanel.AlarmPhase[3].C33_42_over80 | BYTE
SS2PMMPanelAlarmPhase3GlobalAlarmReg | INT | IOD_SS2_TCP | 123 | 40123 | PMMPanel.AlarmPhase[3].GlobalAlarmReg
SS2StUrZaPreklopKlim1_2 | INT | IOD_SS2_TCP | 124 | 40124 | StUrZaPreklopKlim1_2
SS2StUrZaPreklopKlim3_4 | INT | IOD_SS2_TCP | 125 | 40125 | StUrZaPreklopKlim3_4
SS2StUrZaPreklopKlim5_6 | INT | IOD_SS2_TCP | 126 | 40126 | StUrZaPreklopKlim5_6
SS2UPSstatus_Prikaz_PanelSCADA | INT | IOD_SS2_TCP | 127 | 40127 | UPSstatus_Prikaz_PanelSCADA | BYTE
SS2UserCurrentLevel | INT | IOD_SS2_TCP | 128 | 40128 | UserCurrentLevel | BYTE
SS2ErrorComKlima1Code0 | INT | IOD_SS2_TCP | 129 | 40129 | ErrorComKlima[1].Code[0] | BYTE
SS2ErrorComKlima1Code10 | INT | IOD_SS2_TCP | 130 | 40130 | ErrorComKlima[1].Code[10] | BYTE
SS2ErrorComKlima1Code11 | INT | IOD_SS2_TCP | 131 | 40131 | ErrorComKlima[1].Code[11] | BYTE
SS2ErrorComKlima1Code12 | INT | IOD_SS2_TCP | 132 | 40132 | ErrorComKlima[1].Code[12] | BYTE
SS2ErrorComKlima1Code13 | INT | IOD_SS2_TCP | 133 | 40133 | ErrorComKlima[1].Code[13] | BYTE
SS2ErrorComKlima1Code14 | INT | IOD_SS2_TCP | 134 | 40134 | ErrorComKlima[1].Code[14] | BYTE
SS2ErrorComKlima1Code15 | INT | IOD_SS2_TCP | 135 | 40135 | ErrorComKlima[1].Code[15] | BYTE
SS2ErrorComKlima1Code1 | INT | IOD_SS2_TCP | 136 | 40136 | ErrorComKlima[1].Code[1] | BYTE
SS2ErrorComKlima1Code2 | INT | IOD_SS2_TCP | 137 | 40137 | ErrorComKlima[1].Code[2] | BYTE
SS2ErrorComKlima1Code3 | INT | IOD_SS2_TCP | 138 | 40138 | ErrorComKlima[1].Code[3] | BYTE
SS2ErrorComKlima1Code4 | INT | IOD_SS2_TCP | 139 | 40139 | ErrorComKlima[1].Code[4] | BYTE
SS2ErrorComKlima1Code5 | INT | IOD_SS2_TCP | 140 | 40140 | ErrorComKlima[1].Code[5] | BYTE
SS2ErrorComKlima1Code6 | INT | IOD_SS2_TCP | 141 | 40141 | ErrorComKlima[1].Code[6] | BYTE
SS2ErrorComKlima1Code7 | INT | IOD_SS2_TCP | 142 | 40142 | ErrorComKlima[1].Code[7] | BYTE
SS2ErrorComKlima1Code8 | INT | IOD_SS2_TCP | 143 | 40143 | ErrorComKlima[1].Code[8] | BYTE
SS2ErrorComKlima1Code9 | INT | IOD_SS2_TCP | 144 | 40144 | ErrorComKlima[1].Code[9] | BYTE
SS2ErrorComKlima2Code0 | INT | IOD_SS2_TCP | 145 | 40145 | ErrorComKlima[2].Code[0] | BYTE
SS2ErrorComKlima2Code10 | INT | IOD_SS2_TCP | 146 | 40146 | ErrorComKlima[2].Code[10] | BYTE
SS2ErrorComKlima2Code11 | INT | IOD_SS2_TCP | 147 | 40147 | ErrorComKlima[2].Code[11] | BYTE
SS2ErrorComKlima2Code12 | INT | IOD_SS2_TCP | 148 | 40148 | ErrorComKlima[2].Code[12] | BYTE
SS2ErrorComKlima2Code13 | INT | IOD_SS2_TCP | 149 | 40149 | ErrorComKlima[2].Code[13] | BYTE
SS2ErrorComKlima2Code14 | INT | IOD_SS2_TCP | 150 | 40150 | ErrorComKlima[2].Code[14] | BYTE
SS2ErrorComKlima2Code15 | INT | IOD_SS2_TCP | 151 | 40151 | ErrorComKlima[2].Code[15] | BYTE
SS2ErrorComKlima2Code1 | INT | IOD_SS2_TCP | 152 | 40152 | ErrorComKlima[2].Code[1] | BYTE
SS2ErrorComKlima2Code2 | INT | IOD_SS2_TCP | 153 | 40153 | ErrorComKlima[2].Code[2] | BYTE
SS2ErrorComKlima2Code3 | INT | IOD_SS2_TCP | 154 | 40154 | ErrorComKlima[2].Code[3] | BYTE
SS2ErrorComKlima2Code4 | INT | IOD_SS2_TCP | 155 | 40155 | ErrorComKlima[2].Code[4] | BYTE
SS2ErrorComKlima2Code5 | INT | IOD_SS2_TCP | 156 | 40156 | ErrorComKlima[2].Code[5] | BYTE
SS2ErrorComKlima2Code6 | INT | IOD_SS2_TCP | 157 | 40157 | ErrorComKlima[2].Code[6] | BYTE
SS2ErrorComKlima2Code7 | INT | IOD_SS2_TCP | 158 | 40158 | ErrorComKlima[2].Code[7] | BYTE
SS2ErrorComKlima2Code8 | INT | IOD_SS2_TCP | 159 | 40159 | ErrorComKlima[2].Code[8] | BYTE
SS2ErrorComKlima2Code9 | INT | IOD_SS2_TCP | 160 | 40160 | ErrorComKlima[2].Code[9] | BYTE
SS2ErrorComKlima3Code0 | INT | IOD_SS2_TCP | 161 | 40161 | ErrorComKlima[3].Code[0] | BYTE
SS2ErrorComKlima3Code10 | INT | IOD_SS2_TCP | 162 | 40162 | ErrorComKlima[3].Code[10] | BYTE
SS2ErrorComKlima3Code11 | INT | IOD_SS2_TCP | 163 | 40163 | ErrorComKlima[3].Code[11] | BYTE
SS2ErrorComKlima3Code12 | INT | IOD_SS2_TCP | 164 | 40164 | ErrorComKlima[3].Code[12] | BYTE
SS2ErrorComKlima3Code13 | INT | IOD_SS2_TCP | 165 | 40165 | ErrorComKlima[3].Code[13] | BYTE
SS2ErrorComKlima3Code14 | INT | IOD_SS2_TCP | 166 | 40166 | ErrorComKlima[3].Code[14] | BYTE
SS2ErrorComKlima3Code15 | INT | IOD_SS2_TCP | 167 | 40167 | ErrorComKlima[3].Code[15] | BYTE
SS2ErrorComKlima3Code1 | INT | IOD_SS2_TCP | 168 | 40168 | ErrorComKlima[3].Code[1] | BYTE
SS2ErrorComKlima3Code2 | INT | IOD_SS2_TCP | 169 | 40169 | ErrorComKlima[3].Code[2] | BYTE
SS2ErrorComKlima3Code3 | INT | IOD_SS2_TCP | 170 | 40170 | ErrorComKlima[3].Code[3] | BYTE
SS2ErrorComKlima3Code4 | INT | IOD_SS2_TCP | 171 | 40171 | ErrorComKlima[3].Code[4] | BYTE
SS2ErrorComKlima3Code5 | INT | IOD_SS2_TCP | 172 | 40172 | ErrorComKlima[3].Code[5] | BYTE
SS2ErrorComKlima3Code6 | INT | IOD_SS2_TCP | 173 | 40173 | ErrorComKlima[3].Code[6] | BYTE
SS2ErrorComKlima3Code7 | INT | IOD_SS2_TCP | 174 | 40174 | ErrorComKlima[3].Code[7] | BYTE
SS2ErrorComKlima3Code8 | INT | IOD_SS2_TCP | 175 | 40175 | ErrorComKlima[3].Code[8] | BYTE
SS2ErrorComKlima3Code9 | INT | IOD_SS2_TCP | 176 | 40176 | ErrorComKlima[3].Code[9] | BYTE
SS2ErrorComKlima4Code0 | INT | IOD_SS2_TCP | 177 | 40177 | ErrorComKlima[4].Code[0] | BYTE
SS2ErrorComKlima4Code10 | INT | IOD_SS2_TCP | 178 | 40178 | ErrorComKlima[4].Code[10] | BYTE
SS2ErrorComKlima4Code11 | INT | IOD_SS2_TCP | 179 | 40179 | ErrorComKlima[4].Code[11] | BYTE
SS2ErrorComKlima4Code12 | INT | IOD_SS2_TCP | 180 | 40180 | ErrorComKlima[4].Code[12] | BYTE
SS2ErrorComKlima4Code13 | INT | IOD_SS2_TCP | 181 | 40181 | ErrorComKlima[4].Code[13] | BYTE
SS2ErrorComKlima4Code14 | INT | IOD_SS2_TCP | 182 | 40182 | ErrorComKlima[4].Code[14] | BYTE
SS2ErrorComKlima4Code15 | INT | IOD_SS2_TCP | 183 | 40183 | ErrorComKlima[4].Code[15] | BYTE
SS2ErrorComKlima4Code1 | INT | IOD_SS2_TCP | 184 | 40184 | ErrorComKlima[4].Code[1] | BYTE
SS2ErrorComKlima4Code2 | INT | IOD_SS2_TCP | 185 | 40185 | ErrorComKlima[4].Code[2] | BYTE
SS2ErrorComKlima4Code3 | INT | IOD_SS2_TCP | 186 | 40186 | ErrorComKlima[4].Code[3] | BYTE
SS2ErrorComKlima4Code4 | INT | IOD_SS2_TCP | 187 | 40187 | ErrorComKlima[4].Code[4] | BYTE
SS2ErrorComKlima4Code5 | INT | IOD_SS2_TCP | 188 | 40188 | ErrorComKlima[4].Code[5] | BYTE
SS2ErrorComKlima4Code6 | INT | IOD_SS2_TCP | 189 | 40189 | ErrorComKlima[4].Code[6] | BYTE
SS2ErrorComKlima4Code7 | INT | IOD_SS2_TCP | 190 | 40190 | ErrorComKlima[4].Code[7] | BYTE
SS2ErrorComKlima4Code8 | INT | IOD_SS2_TCP | 191 | 40191 | ErrorComKlima[4].Code[8] | BYTE
SS2ErrorComKlima4Code9 | INT | IOD_SS2_TCP | 192 | 40192 | ErrorComKlima[4].Code[9] | BYTE
SS2ErrorComKlima5Code0 | INT | IOD_SS2_TCP | 193 | 40193 | ErrorComKlima[5].Code[0] | BYTE
SS2ErrorComKlima5Code10 | INT | IOD_SS2_TCP | 194 | 40194 | ErrorComKlima[5].Code[10] | BYTE
SS2ErrorComKlima5Code11 | INT | IOD_SS2_TCP | 195 | 40195 | ErrorComKlima[5].Code[11] | BYTE
SS2ErrorComKlima5Code12 | INT | IOD_SS2_TCP | 196 | 40196 | ErrorComKlima[5].Code[12] | BYTE
SS2ErrorComKlima5Code13 | INT | IOD_SS2_TCP | 197 | 40197 | ErrorComKlima[5].Code[13] | BYTE
SS2ErrorComKlima5Code14 | INT | IOD_SS2_TCP | 198 | 40198 | ErrorComKlima[5].Code[14] | BYTE
SS2ErrorComKlima5Code15 | INT | IOD_SS2_TCP | 199 | 40199 | ErrorComKlima[5].Code[15] | BYTE
SS2ErrorComKlima5Code1 | INT | IOD_SS2_TCP | 200 | 40200 | ErrorComKlima[5].Code[1] | BYTE
SS2ErrorComKlima5Code2 | INT | IOD_SS2_TCP | 201 | 40201 | ErrorComKlima[5].Code[2] | BYTE
SS2ErrorComKlima5Code3 | INT | IOD_SS2_TCP | 202 | 40202 | ErrorComKlima[5].Code[3] | BYTE
SS2ErrorComKlima5Code4 | INT | IOD_SS2_TCP | 203 | 40203 | ErrorComKlima[5].Code[4] | BYTE
SS2ErrorComKlima5Code5 | INT | IOD_SS2_TCP | 204 | 40204 | ErrorComKlima[5].Code[5] | BYTE
SS2ErrorComKlima5Code6 | INT | IOD_SS2_TCP | 205 | 40205 | ErrorComKlima[5].Code[6] | BYTE
SS2ErrorComKlima5Code7 | INT | IOD_SS2_TCP | 206 | 40206 | ErrorComKlima[5].Code[7] | BYTE
SS2ErrorComKlima5Code8 | INT | IOD_SS2_TCP | 207 | 40207 | ErrorComKlima[5].Code[8] | BYTE
SS2ErrorComKlima5Code9 | INT | IOD_SS2_TCP | 208 | 40208 | ErrorComKlima[5].Code[9] | BYTE
SS2ErrorComKlima6Code0 | INT | IOD_SS2_TCP | 209 | 40209 | ErrorComKlima[6].Code[0] | BYTE
SS2ErrorComKlima6Code10 | INT | IOD_SS2_TCP | 210 | 40210 | ErrorComKlima[6].Code[10] | BYTE
SS2ErrorComKlima6Code11 | INT | IOD_SS2_TCP | 211 | 40211 | ErrorComKlima[6].Code[11] | BYTE
SS2ErrorComKlima6Code12 | INT | IOD_SS2_TCP | 212 | 40212 | ErrorComKlima[6].Code[12] | BYTE
SS2ErrorComKlima6Code13 | INT | IOD_SS2_TCP | 213 | 40213 | ErrorComKlima[6].Code[13] | BYTE
SS2ErrorComKlima6Code14 | INT | IOD_SS2_TCP | 214 | 40214 | ErrorComKlima[6].Code[14] | BYTE
SS2ErrorComKlima6Code15 | INT | IOD_SS2_TCP | 215 | 40215 | ErrorComKlima[6].Code[15] | BYTE
SS2ErrorComKlima6Code1 | INT | IOD_SS2_TCP | 216 | 40216 | ErrorComKlima[6].Code[1] | BYTE
SS2ErrorComKlima6Code2 | INT | IOD_SS2_TCP | 217 | 40217 | ErrorComKlima[6].Code[2] | BYTE
SS2ErrorComKlima6Code3 | INT | IOD_SS2_TCP | 218 | 40218 | ErrorComKlima[6].Code[3] | BYTE
SS2ErrorComKlima6Code4 | INT | IOD_SS2_TCP | 219 | 40219 | ErrorComKlima[6].Code[4] | BYTE
SS2ErrorComKlima6Code5 | INT | IOD_SS2_TCP | 220 | 40220 | ErrorComKlima[6].Code[5] | BYTE
SS2ErrorComKlima6Code6 | INT | IOD_SS2_TCP | 221 | 40221 | ErrorComKlima[6].Code[6] | BYTE
SS2ErrorComKlima6Code7 | INT | IOD_SS2_TCP | 222 | 40222 | ErrorComKlima[6].Code[7] | BYTE
SS2ErrorComKlima6Code8 | INT | IOD_SS2_TCP | 223 | 40223 | ErrorComKlima[6].Code[8] | BYTE
SS2ErrorComKlima6Code9 | INT | IOD_SS2_TCP | 224 | 40224 | ErrorComKlima[6].Code[9] | BYTE
SS2ErrorComPMM1Code0 | INT | IOD_SS2_TCP | 225 | 40225 | ErrorComPMM[1].Code[0] | BYTE
SS2ErrorComPMM1Code10 | INT | IOD_SS2_TCP | 226 | 40226 | ErrorComPMM[1].Code[10] | BYTE
SS2ErrorComPMM1Code11 | INT | IOD_SS2_TCP | 227 | 40227 | ErrorComPMM[1].Code[11] | BYTE
SS2ErrorComPMM1Code12 | INT | IOD_SS2_TCP | 228 | 40228 | ErrorComPMM[1].Code[12] | BYTE
SS2ErrorComPMM1Code13 | INT | IOD_SS2_TCP | 229 | 40229 | ErrorComPMM[1].Code[13] | BYTE
SS2ErrorComPMM1Code14 | INT | IOD_SS2_TCP | 230 | 40230 | ErrorComPMM[1].Code[14] | BYTE
SS2ErrorComPMM1Code15 | INT | IOD_SS2_TCP | 231 | 40231 | ErrorComPMM[1].Code[15] | BYTE
SS2ErrorComPMM1Code1 | INT | IOD_SS2_TCP | 232 | 40232 | ErrorComPMM[1].Code[1] | BYTE
SS2ErrorComPMM1Code2 | INT | IOD_SS2_TCP | 233 | 40233 | ErrorComPMM[1].Code[2] | BYTE
SS2ErrorComPMM1Code3 | INT | IOD_SS2_TCP | 234 | 40234 | ErrorComPMM[1].Code[3] | BYTE
SS2ErrorComPMM1Code4 | INT | IOD_SS2_TCP | 235 | 40235 | ErrorComPMM[1].Code[4] | BYTE
SS2ErrorComPMM1Code5 | INT | IOD_SS2_TCP | 236 | 40236 | ErrorComPMM[1].Code[5] | BYTE
SS2ErrorComPMM1Code6 | INT | IOD_SS2_TCP | 237 | 40237 | ErrorComPMM[1].Code[6] | BYTE
SS2ErrorComPMM1Code7 | INT | IOD_SS2_TCP | 238 | 40238 | ErrorComPMM[1].Code[7] | BYTE
SS2ErrorComPMM1Code8 | INT | IOD_SS2_TCP | 239 | 40239 | ErrorComPMM[1].Code[8] | BYTE
SS2ErrorComPMM1Code9 | INT | IOD_SS2_TCP | 240 | 40240 | ErrorComPMM[1].Code[9] | BYTE
SS2ErrorComPMM2Code0 | INT | IOD_SS2_TCP | 241 | 40241 | ErrorComPMM[2].Code[0] | BYTE
SS2ErrorComPMM2Code10 | INT | IOD_SS2_TCP | 242 | 40242 | ErrorComPMM[2].Code[10] | BYTE
SS2ErrorComPMM2Code11 | INT | IOD_SS2_TCP | 243 | 40243 | ErrorComPMM[2].Code[11] | BYTE
SS2ErrorComPMM2Code12 | INT | IOD_SS2_TCP | 244 | 40244 | ErrorComPMM[2].Code[12] | BYTE
SS2ErrorComPMM2Code13 | INT | IOD_SS2_TCP | 245 | 40245 | ErrorComPMM[2].Code[13] | BYTE
SS2ErrorComPMM2Code14 | INT | IOD_SS2_TCP | 246 | 40246 | ErrorComPMM[2].Code[14] | BYTE
SS2ErrorComPMM2Code15 | INT | IOD_SS2_TCP | 247 | 40247 | ErrorComPMM[2].Code[15] | BYTE
SS2ErrorComPMM2Code1 | INT | IOD_SS2_TCP | 248 | 40248 | ErrorComPMM[2].Code[1] | BYTE
SS2ErrorComPMM2Code2 | INT | IOD_SS2_TCP | 249 | 40249 | ErrorComPMM[2].Code[2] | BYTE
SS2ErrorComPMM2Code3 | INT | IOD_SS2_TCP | 250 | 40250 | ErrorComPMM[2].Code[3] | BYTE
SS2ErrorComPMM2Code4 | INT | IOD_SS2_TCP | 251 | 40251 | ErrorComPMM[2].Code[4] | BYTE
SS2ErrorComPMM2Code5 | INT | IOD_SS2_TCP | 252 | 40252 | ErrorComPMM[2].Code[5] | BYTE
SS2ErrorComPMM2Code6 | INT | IOD_SS2_TCP | 253 | 40253 | ErrorComPMM[2].Code[6] | BYTE
SS2ErrorComPMM2Code7 | INT | IOD_SS2_TCP | 254 | 40254 | ErrorComPMM[2].Code[7] | BYTE
SS2ErrorComPMM2Code8 | INT | IOD_SS2_TCP | 255 | 40255 | ErrorComPMM[2].Code[8] | BYTE
SS2ErrorComPMM2Code9 | INT | IOD_SS2_TCP | 256 | 40256 | ErrorComPMM[2].Code[9] | BYTE
SS2kom_nast_cas_izpada | INT | IOD_SS2_TCP | 257 | 40257 | kom_nast_cas_izpada
SS2AktualniSetPointTemp1_2 | REAL | IOD_SS2_TCP | 4001 | 44001 | AktualniSetPointTemp1_2
SS2AktualniSetPointTemp3_4 | REAL | IOD_SS2_TCP | 4003 | 44003 | AktualniSetPointTemp3_4
SS2AktualniSetPointTemp5_6 | REAL | IOD_SS2_TCP | 4005 | 44005 | AktualniSetPointTemp5_6
SS2Klima1ure | REAL | IOD_SS2_TCP | 4007 | 44007 | Klima1ure
SS2Klima2ure | REAL | IOD_SS2_TCP | 4009 | 44009 | Klima2ure
SS2Klima3ure | REAL | IOD_SS2_TCP | 4011 | 44011 | Klima3ure
SS2Klima4ure | REAL | IOD_SS2_TCP | 4013 | 44013 | Klima4ure
SS2Klima5ure | REAL | IOD_SS2_TCP | 4015 | 44015 | Klima5ure
SS2Klima6ure | REAL | IOD_SS2_TCP | 4017 | 44017 | Klima6ure
SS2Klima1NastMaxTemp | REAL | IOD_SS2_TCP | 4019 | 44019 | Klima[1].NastMaxTemp
SS2Klima1NastMaxVlaznost | REAL | IOD_SS2_TCP | 4021 | 44021 | Klima[1].NastMaxVlaznost
SS2Klima1NastMinTemp | REAL | IOD_SS2_TCP | 4023 | 44023 | Klima[1].NastMinTemp
SS2Klima1NastMinVlaznost | REAL | IOD_SS2_TCP | 4025 | 44025 | Klima[1].NastMinVlaznost
SS2Klima1NastTempProstora | REAL | IOD_SS2_TCP | 4027 | 44027 | Klima[1].NastTempProstora
SS2Klima1NastVlaznost | REAL | IOD_SS2_TCP | 4029 | 44029 | Klima[1].NastVlaznost
SS2Klima1ObratUreFilter | REAL | IOD_SS2_TCP | 4031 | 44031 | Klima[1].ObratUreFilter
SS2Klima1ObratUreKompresor1 | REAL | IOD_SS2_TCP | 4033 | 44033 | Klima[1].ObratUreKompresor1
SS2Klima1ObratUreKompresor2 | REAL | IOD_SS2_TCP | 4035 | 44035 | Klima[1].ObratUreKompresor2
SS2Klima1ObratUreVent | REAL | IOD_SS2_TCP | 4037 | 44037 | Klima[1].ObratUreVent
SS2Klima1TemperaturaProstora | REAL | IOD_SS2_TCP | 4039 | 44039 | Klima[1].TemperaturaProstora
SS2Klima1VlaznostProstora | REAL | IOD_SS2_TCP | 4041 | 44041 | Klima[1].VlaznostProstora
SS2Klima2NastMaxTemp | REAL | IOD_SS2_TCP | 4043 | 44043 | Klima[2].NastMaxTemp
SS2Klima2NastMaxVlaznost | REAL | IOD_SS2_TCP | 4045 | 44045 | Klima[2].NastMaxVlaznost
SS2Klima2NastMinTemp | REAL | IOD_SS2_TCP | 4047 | 44047 | Klima[2].NastMinTemp
SS2Klima2NastMinVlaznost | REAL | IOD_SS2_TCP | 4049 | 44049 | Klima[2].NastMinVlaznost
SS2Klima2NastTempProstora | REAL | IOD_SS2_TCP | 4051 | 44051 | Klima[2].NastTempProstora
SS2Klima2NastVlaznost | REAL | IOD_SS2_TCP | 4053 | 44053 | Klima[2].NastVlaznost
SS2Klima2ObratUreFilter | REAL | IOD_SS2_TCP | 4055 | 44055 | Klima[2].ObratUreFilter
SS2Klima2ObratUreKompresor1 | REAL | IOD_SS2_TCP | 4057 | 44057 | Klima[2].ObratUreKompresor1
SS2Klima2ObratUreKompresor2 | REAL | IOD_SS2_TCP | 4059 | 44059 | Klima[2].ObratUreKompresor2
SS2Klima2ObratUreVent | REAL | IOD_SS2_TCP | 4061 | 44061 | Klima[2].ObratUreVent
SS2Klima2TemperaturaProstora | REAL | IOD_SS2_TCP | 4063 | 44063 | Klima[2].TemperaturaProstora
SS2Klima2VlaznostProstora | REAL | IOD_SS2_TCP | 4065 | 44065 | Klima[2].VlaznostProstora
SS2Klima3NastMaxTemp | REAL | IOD_SS2_TCP | 4067 | 44067 | Klima[3].NastMaxTemp
SS2Klima3NastMaxVlaznost | REAL | IOD_SS2_TCP | 4069 | 44069 | Klima[3].NastMaxVlaznost
SS2Klima3NastMinTemp | REAL | IOD_SS2_TCP | 4071 | 44071 | Klima[3].NastMinTemp
SS2Klima3NastMinVlaznost | REAL | IOD_SS2_TCP | 4073 | 44073 | Klima[3].NastMinVlaznost
SS2Klima3NastTempProstora | REAL | IOD_SS2_TCP | 4075 | 44075 | Klima[3].NastTempProstora
SS2Klima3NastVlaznost | REAL | IOD_SS2_TCP | 4077 | 44077 | Klima[3].NastVlaznost
SS2Klima3ObratUreFilter | REAL | IOD_SS2_TCP | 4079 | 44079 | Klima[3].ObratUreFilter
SS2Klima3ObratUreKompresor1 | REAL | IOD_SS2_TCP | 4081 | 44081 | Klima[3].ObratUreKompresor1
SS2Klima3ObratUreKompresor2 | REAL | IOD_SS2_TCP | 4083 | 44083 | Klima[3].ObratUreKompresor2
SS2Klima3ObratUreVent | REAL | IOD_SS2_TCP | 4085 | 44085 | Klima[3].ObratUreVent
SS2Klima3TemperaturaProstora | REAL | IOD_SS2_TCP | 4087 | 44087 | Klima[3].TemperaturaProstora
SS2Klima3VlaznostProstora | REAL | IOD_SS2_TCP | 4089 | 44089 | Klima[3].VlaznostProstora
SS2Klima4NastMaxTemp | REAL | IOD_SS2_TCP | 4091 | 44091 | Klima[4].NastMaxTemp
SS2Klima4NastMaxVlaznost | REAL | IOD_SS2_TCP | 4093 | 44093 | Klima[4].NastMaxVlaznost
SS2Klima4NastMinTemp | REAL | IOD_SS2_TCP | 4095 | 44095 | Klima[4].NastMinTemp
SS2Klima4NastMinVlaznost | REAL | IOD_SS2_TCP | 4097 | 44097 | Klima[4].NastMinVlaznost
SS2Klima4NastTempProstora | REAL | IOD_SS2_TCP | 4099 | 44099 | Klima[4].NastTempProstora
SS2Klima4NastVlaznost | REAL | IOD_SS2_TCP | 4101 | 44101 | Klima[4].NastVlaznost
SS2Klima4ObratUreFilter | REAL | IOD_SS2_TCP | 4103 | 44103 | Klima[4].ObratUreFilter
SS2Klima4ObratUreKompresor1 | REAL | IOD_SS2_TCP | 4105 | 44105 | Klima[4].ObratUreKompresor1
SS2Klima4ObratUreKompresor2 | REAL | IOD_SS2_TCP | 4107 | 44107 | Klima[4].ObratUreKompresor2
SS2Klima4ObratUreVent | REAL | IOD_SS2_TCP | 4109 | 44109 | Klima[4].ObratUreVent
SS2Klima4TemperaturaProstora | REAL | IOD_SS2_TCP | 4111 | 44111 | Klima[4].TemperaturaProstora
SS2Klima4VlaznostProstora | REAL | IOD_SS2_TCP | 4113 | 44113 | Klima[4].VlaznostProstora
SS2Klima5NastMaxTemp | REAL | IOD_SS2_TCP | 4115 | 44115 | Klima[5].NastMaxTemp
SS2Klima5NastMaxVlaznost | REAL | IOD_SS2_TCP | 4117 | 44117 | Klima[5].NastMaxVlaznost
SS2Klima5NastMinTemp | REAL | IOD_SS2_TCP | 4119 | 44119 | Klima[5].NastMinTemp
SS2Klima5NastMinVlaznost | REAL | IOD_SS2_TCP | 4121 | 44121 | Klima[5].NastMinVlaznost
SS2Klima5NastTempProstora | REAL | IOD_SS2_TCP | 4123 | 44123 | Klima[5].NastTempProstora
SS2Klima5NastVlaznost | REAL | IOD_SS2_TCP | 4125 | 44125 | Klima[5].NastVlaznost
SS2Klima5ObratUreFilter | REAL | IOD_SS2_TCP | 4127 | 44127 | Klima[5].ObratUreFilter
SS2Klima5ObratUreKompresor1 | REAL | IOD_SS2_TCP | 4129 | 44129 | Klima[5].ObratUreKompresor1
SS2Klima5ObratUreKompresor2 | REAL | IOD_SS2_TCP | 4131 | 44131 | Klima[5].ObratUreKompresor2
SS2Klima5ObratUreVent | REAL | IOD_SS2_TCP | 4133 | 44133 | Klima[5].ObratUreVent
SS2Klima5TemperaturaProstora | REAL | IOD_SS2_TCP | 4135 | 44135 | Klima[5].TemperaturaProstora
SS2Klima5VlaznostProstora | REAL | IOD_SS2_TCP | 4137 | 44137 | Klima[5].VlaznostProstora
SS2Klima6NastMaxTemp | REAL | IOD_SS2_TCP | 4139 | 44139 | Klima[6].NastMaxTemp
SS2Klima6NastMaxVlaznost | REAL | IOD_SS2_TCP | 4141 | 44141 | Klima[6].NastMaxVlaznost
SS2Klima6NastMinTemp | REAL | IOD_SS2_TCP | 4143 | 44143 | Klima[6].NastMinTemp
SS2Klima6NastMinVlaznost | REAL | IOD_SS2_TCP | 4145 | 44145 | Klima[6].NastMinVlaznost
SS2Klima6NastTempProstora | REAL | IOD_SS2_TCP | 4147 | 44147 | Klima[6].NastTempProstora
SS2Klima6NastVlaznost | REAL | IOD_SS2_TCP | 4149 | 44149 | Klima[6].NastVlaznost
SS2Klima6ObratUreFilter | REAL | IOD_SS2_TCP | 4151 | 44151 | Klima[6].ObratUreFilter
SS2Klima6ObratUreKompresor1 | REAL | IOD_SS2_TCP | 4153 | 44153 | Klima[6].ObratUreKompresor1
SS2Klima6ObratUreKompresor2 | REAL | IOD_SS2_TCP | 4155 | 44155 | Klima[6].ObratUreKompresor2
SS2Klima6ObratUreVent | REAL | IOD_SS2_TCP | 4157 | 44157 | Klima[6].ObratUreVent
SS2Klima6TemperaturaProstora | REAL | IOD_SS2_TCP | 4159 | 44159 | Klima[6].TemperaturaProstora
SS2Klima6VlaznostProstora | REAL | IOD_SS2_TCP | 4161 | 44161 | Klima[6].VlaznostProstora
SS2PMM1ActiveEnergyConsumed_kWh | REAL | IOD_SS2_TCP | 4163 | 44163 | PMM[1].ActiveEnergyConsumed_kWh
SS2PMM1ActivePowerPhaseA_kW | REAL | IOD_SS2_TCP | 4165 | 44165 | PMM[1].ActivePowerPhaseA_kW
SS2PMM1ActivePowerPhaseB_kW | REAL | IOD_SS2_TCP | 4167 | 44167 | PMM[1].ActivePowerPhaseB_kW
SS2PMM1ActivePowerPhaseC_kW | REAL | IOD_SS2_TCP | 4169 | 44169 | PMM[1].ActivePowerPhaseC_kW
SS2PMM1AparentPowerPhaseA | REAL | IOD_SS2_TCP | 4171 | 44171 | PMM[1].AparentPowerPhaseA
SS2PMM1AparentPowerPhaseB | REAL | IOD_SS2_TCP | 4173 | 44173 | PMM[1].AparentPowerPhaseB
SS2PMM1AparentPowerPhaseC | REAL | IOD_SS2_TCP | 4175 | 44175 | PMM[1].AparentPowerPhaseC
SS2PMM1AverageCurrent_A | REAL | IOD_SS2_TCP | 4177 | 44177 | PMM[1].AverageCurrent_A
SS2PMM1AveragePhaseToNeutral_V | REAL | IOD_SS2_TCP | 4179 | 44179 | PMM[1].AveragePhaseToNeutral_V
SS2PMM1AveragePhaseToPhase_V | REAL | IOD_SS2_TCP | 4181 | 44181 | PMM[1].AveragePhaseToPhase_V
SS2PMM1CurrentInPhaseA_A | REAL | IOD_SS2_TCP | 4183 | 44183 | PMM[1].CurrentInPhaseA_A
SS2PMM1CurrentInPhaseB_A | REAL | IOD_SS2_TCP | 4185 | 44185 | PMM[1].CurrentInPhaseB_A
SS2PMM1CurrentInPhaseC_A | REAL | IOD_SS2_TCP | 4187 | 44187 | PMM[1].CurrentInPhaseC_A
SS2PMM1Frequency_Hz | REAL | IOD_SS2_TCP | 4189 | 44189 | PMM[1].Frequency_Hz
SS2PMM1Phase1Current10 | REAL | IOD_SS2_TCP | 4191 | 44191 | PMM[1].Phase[1].Current[10]
SS2PMM1Phase1Current11 | REAL | IOD_SS2_TCP | 4193 | 44193 | PMM[1].Phase[1].Current[11]
SS2PMM1Phase1Current12 | REAL | IOD_SS2_TCP | 4195 | 44195 | PMM[1].Phase[1].Current[12]
SS2PMM1Phase1Current13 | REAL | IOD_SS2_TCP | 4197 | 44197 | PMM[1].Phase[1].Current[13]
SS2PMM1Phase1Current14 | REAL | IOD_SS2_TCP | 4199 | 44199 | PMM[1].Phase[1].Current[14]
SS2PMM1Phase1Current15 | REAL | IOD_SS2_TCP | 4201 | 44201 | PMM[1].Phase[1].Current[15]
SS2PMM1Phase1Current16 | REAL | IOD_SS2_TCP | 4203 | 44203 | PMM[1].Phase[1].Current[16]
SS2PMM1Phase1Current17 | REAL | IOD_SS2_TCP | 4205 | 44205 | PMM[1].Phase[1].Current[17]
SS2PMM1Phase1Current18 | REAL | IOD_SS2_TCP | 4207 | 44207 | PMM[1].Phase[1].Current[18]
SS2PMM1Phase1Current19 | REAL | IOD_SS2_TCP | 4209 | 44209 | PMM[1].Phase[1].Current[19]
SS2PMM1Phase1Current1 | REAL | IOD_SS2_TCP | 4211 | 44211 | PMM[1].Phase[1].Current[1]
SS2PMM1Phase1Current20 | REAL | IOD_SS2_TCP | 4213 | 44213 | PMM[1].Phase[1].Current[20]
SS2PMM1Phase1Current21 | REAL | IOD_SS2_TCP | 4215 | 44215 | PMM[1].Phase[1].Current[21]
SS2PMM1Phase1Current22 | REAL | IOD_SS2_TCP | 4217 | 44217 | PMM[1].Phase[1].Current[22]
SS2PMM1Phase1Current23 | REAL | IOD_SS2_TCP | 4219 | 44219 | PMM[1].Phase[1].Current[23]
SS2PMM1Phase1Current24 | REAL | IOD_SS2_TCP | 4221 | 44221 | PMM[1].Phase[1].Current[24]
SS2PMM1Phase1Current25 | REAL | IOD_SS2_TCP | 4223 | 44223 | PMM[1].Phase[1].Current[25]
SS2PMM1Phase1Current26 | REAL | IOD_SS2_TCP | 4225 | 44225 | PMM[1].Phase[1].Current[26]
SS2PMM1Phase1Current27 | REAL | IOD_SS2_TCP | 4227 | 44227 | PMM[1].Phase[1].Current[27]
SS2PMM1Phase1Current28 | REAL | IOD_SS2_TCP | 4229 | 44229 | PMM[1].Phase[1].Current[28]
SS2PMM1Phase1Current29 | REAL | IOD_SS2_TCP | 4231 | 44231 | PMM[1].Phase[1].Current[29]
SS2PMM1Phase1Current2 | REAL | IOD_SS2_TCP | 4233 | 44233 | PMM[1].Phase[1].Current[2]
SS2PMM1Phase1Current30 | REAL | IOD_SS2_TCP | 4235 | 44235 | PMM[1].Phase[1].Current[30]
SS2PMM1Phase1Current31 | REAL | IOD_SS2_TCP | 4237 | 44237 | PMM[1].Phase[1].Current[31]
SS2PMM1Phase1Current32 | REAL | IOD_SS2_TCP | 4239 | 44239 | PMM[1].Phase[1].Current[32]
SS2PMM1Phase1Current33 | REAL | IOD_SS2_TCP | 4241 | 44241 | PMM[1].Phase[1].Current[33]
SS2PMM1Phase1Current34 | REAL | IOD_SS2_TCP | 4243 | 44243 | PMM[1].Phase[1].Current[34]
SS2PMM1Phase1Current35 | REAL | IOD_SS2_TCP | 4245 | 44245 | PMM[1].Phase[1].Current[35]
SS2PMM1Phase1Current36 | REAL | IOD_SS2_TCP | 4247 | 44247 | PMM[1].Phase[1].Current[36]
SS2PMM1Phase1Current37 | REAL | IOD_SS2_TCP | 4249 | 44249 | PMM[1].Phase[1].Current[37]
SS2PMM1Phase1Current38 | REAL | IOD_SS2_TCP | 4251 | 44251 | PMM[1].Phase[1].Current[38]
SS2PMM1Phase1Current39 | REAL | IOD_SS2_TCP | 4253 | 44253 | PMM[1].Phase[1].Current[39]
SS2PMM1Phase1Current3 | REAL | IOD_SS2_TCP | 4255 | 44255 | PMM[1].Phase[1].Current[3]
SS2PMM1Phase1Current40 | REAL | IOD_SS2_TCP | 4257 | 44257 | PMM[1].Phase[1].Current[40]
SS2PMM1Phase1Current41 | REAL | IOD_SS2_TCP | 4259 | 44259 | PMM[1].Phase[1].Current[41]
SS2PMM1Phase1Current42 | REAL | IOD_SS2_TCP | 4261 | 44261 | PMM[1].Phase[1].Current[42]
SS2PMM1Phase1Current4 | REAL | IOD_SS2_TCP | 4263 | 44263 | PMM[1].Phase[1].Current[4]
SS2PMM1Phase1Current5 | REAL | IOD_SS2_TCP | 4265 | 44265 | PMM[1].Phase[1].Current[5]
SS2PMM1Phase1Current6 | REAL | IOD_SS2_TCP | 4267 | 44267 | PMM[1].Phase[1].Current[6]
SS2PMM1Phase1Current7 | REAL | IOD_SS2_TCP | 4269 | 44269 | PMM[1].Phase[1].Current[7]
SS2PMM1Phase1Current8 | REAL | IOD_SS2_TCP | 4271 | 44271 | PMM[1].Phase[1].Current[8]
SS2PMM1Phase1Current9 | REAL | IOD_SS2_TCP | 4273 | 44273 | PMM[1].Phase[1].Current[9]
SS2PMM1Phase2Current10 | REAL | IOD_SS2_TCP | 4275 | 44275 | PMM[1].Phase[2].Current[10]
SS2PMM1Phase2Current11 | REAL | IOD_SS2_TCP | 4277 | 44277 | PMM[1].Phase[2].Current[11]
SS2PMM1Phase2Current12 | REAL | IOD_SS2_TCP | 4279 | 44279 | PMM[1].Phase[2].Current[12]
SS2PMM1Phase2Current13 | REAL | IOD_SS2_TCP | 4281 | 44281 | PMM[1].Phase[2].Current[13]
SS2PMM1Phase2Current14 | REAL | IOD_SS2_TCP | 4283 | 44283 | PMM[1].Phase[2].Current[14]
SS2PMM1Phase2Current15 | REAL | IOD_SS2_TCP | 4285 | 44285 | PMM[1].Phase[2].Current[15]
SS2PMM1Phase2Current16 | REAL | IOD_SS2_TCP | 4287 | 44287 | PMM[1].Phase[2].Current[16]
SS2PMM1Phase2Current17 | REAL | IOD_SS2_TCP | 4289 | 44289 | PMM[1].Phase[2].Current[17]
SS2PMM1Phase2Current18 | REAL | IOD_SS2_TCP | 4291 | 44291 | PMM[1].Phase[2].Current[18]
SS2PMM1Phase2Current19 | REAL | IOD_SS2_TCP | 4293 | 44293 | PMM[1].Phase[2].Current[19]
SS2PMM1Phase2Current1 | REAL | IOD_SS2_TCP | 4295 | 44295 | PMM[1].Phase[2].Current[1]
SS2PMM1Phase2Current20 | REAL | IOD_SS2_TCP | 4297 | 44297 | PMM[1].Phase[2].Current[20]
SS2PMM1Phase2Current21 | REAL | IOD_SS2_TCP | 4299 | 44299 | PMM[1].Phase[2].Current[21]
SS2PMM1Phase2Current22 | REAL | IOD_SS2_TCP | 4301 | 44301 | PMM[1].Phase[2].Current[22]
SS2PMM1Phase2Current23 | REAL | IOD_SS2_TCP | 4303 | 44303 | PMM[1].Phase[2].Current[23]
SS2PMM1Phase2Current24 | REAL | IOD_SS2_TCP | 4305 | 44305 | PMM[1].Phase[2].Current[24]
SS2PMM1Phase2Current25 | REAL | IOD_SS2_TCP | 4307 | 44307 | PMM[1].Phase[2].Current[25]
SS2PMM1Phase2Current26 | REAL | IOD_SS2_TCP | 4309 | 44309 | PMM[1].Phase[2].Current[26]
SS2PMM1Phase2Current27 | REAL | IOD_SS2_TCP | 4311 | 44311 | PMM[1].Phase[2].Current[27]
SS2PMM1Phase2Current28 | REAL | IOD_SS2_TCP | 4313 | 44313 | PMM[1].Phase[2].Current[28]
SS2PMM1Phase2Current29 | REAL | IOD_SS2_TCP | 4315 | 44315 | PMM[1].Phase[2].Current[29]
SS2PMM1Phase2Current2 | REAL | IOD_SS2_TCP | 4317 | 44317 | PMM[1].Phase[2].Current[2]
SS2PMM1Phase2Current30 | REAL | IOD_SS2_TCP | 4319 | 44319 | PMM[1].Phase[2].Current[30]
SS2PMM1Phase2Current31 | REAL | IOD_SS2_TCP | 4321 | 44321 | PMM[1].Phase[2].Current[31]
SS2PMM1Phase2Current32 | REAL | IOD_SS2_TCP | 4323 | 44323 | PMM[1].Phase[2].Current[32]
SS2PMM1Phase2Current33 | REAL | IOD_SS2_TCP | 4325 | 44325 | PMM[1].Phase[2].Current[33]
SS2PMM1Phase2Current34 | REAL | IOD_SS2_TCP | 4327 | 44327 | PMM[1].Phase[2].Current[34]
SS2PMM1Phase2Current35 | REAL | IOD_SS2_TCP | 4329 | 44329 | PMM[1].Phase[2].Current[35]
SS2PMM1Phase2Current36 | REAL | IOD_SS2_TCP | 4331 | 44331 | PMM[1].Phase[2].Current[36]
SS2PMM1Phase2Current37 | REAL | IOD_SS2_TCP | 4333 | 44333 | PMM[1].Phase[2].Current[37]
SS2PMM1Phase2Current38 | REAL | IOD_SS2_TCP | 4335 | 44335 | PMM[1].Phase[2].Current[38]
SS2PMM1Phase2Current39 | REAL | IOD_SS2_TCP | 4337 | 44337 | PMM[1].Phase[2].Current[39]
SS2PMM1Phase2Current3 | REAL | IOD_SS2_TCP | 4339 | 44339 | PMM[1].Phase[2].Current[3]
SS2PMM1Phase2Current40 | REAL | IOD_SS2_TCP | 4341 | 44341 | PMM[1].Phase[2].Current[40]
SS2PMM1Phase2Current41 | REAL | IOD_SS2_TCP | 4343 | 44343 | PMM[1].Phase[2].Current[41]
SS2PMM1Phase2Current42 | REAL | IOD_SS2_TCP | 4345 | 44345 | PMM[1].Phase[2].Current[42]
SS2PMM1Phase2Current4 | REAL | IOD_SS2_TCP | 4347 | 44347 | PMM[1].Phase[2].Current[4]
SS2PMM1Phase2Current5 | REAL | IOD_SS2_TCP | 4349 | 44349 | PMM[1].Phase[2].Current[5]
SS2PMM1Phase2Current6 | REAL | IOD_SS2_TCP | 4351 | 44351 | PMM[1].Phase[2].Current[6]
SS2PMM1Phase2Current7 | REAL | IOD_SS2_TCP | 4353 | 44353 | PMM[1].Phase[2].Current[7]
SS2PMM1Phase2Current8 | REAL | IOD_SS2_TCP | 4355 | 44355 | PMM[1].Phase[2].Current[8]
SS2PMM1Phase2Current9 | REAL | IOD_SS2_TCP | 4357 | 44357 | PMM[1].Phase[2].Current[9]
SS2PMM1Phase3Current10 | REAL | IOD_SS2_TCP | 4359 | 44359 | PMM[1].Phase[3].Current[10]
SS2PMM1Phase3Current11 | REAL | IOD_SS2_TCP | 4361 | 44361 | PMM[1].Phase[3].Current[11]
SS2PMM1Phase3Current12 | REAL | IOD_SS2_TCP | 4363 | 44363 | PMM[1].Phase[3].Current[12]
SS2PMM1Phase3Current13 | REAL | IOD_SS2_TCP | 4365 | 44365 | PMM[1].Phase[3].Current[13]
SS2PMM1Phase3Current14 | REAL | IOD_SS2_TCP | 4367 | 44367 | PMM[1].Phase[3].Current[14]
SS2PMM1Phase3Current15 | REAL | IOD_SS2_TCP | 4369 | 44369 | PMM[1].Phase[3].Current[15]
SS2PMM1Phase3Current16 | REAL | IOD_SS2_TCP | 4371 | 44371 | PMM[1].Phase[3].Current[16]
SS2PMM1Phase3Current17 | REAL | IOD_SS2_TCP | 4373 | 44373 | PMM[1].Phase[3].Current[17]
SS2PMM1Phase3Current18 | REAL | IOD_SS2_TCP | 4375 | 44375 | PMM[1].Phase[3].Current[18]
SS2PMM1Phase3Current19 | REAL | IOD_SS2_TCP | 4377 | 44377 | PMM[1].Phase[3].Current[19]
SS2PMM1Phase3Current1 | REAL | IOD_SS2_TCP | 4379 | 44379 | PMM[1].Phase[3].Current[1]
SS2PMM1Phase3Current20 | REAL | IOD_SS2_TCP | 4381 | 44381 | PMM[1].Phase[3].Current[20]
SS2PMM1Phase3Current21 | REAL | IOD_SS2_TCP | 4383 | 44383 | PMM[1].Phase[3].Current[21]
SS2PMM1Phase3Current22 | REAL | IOD_SS2_TCP | 4385 | 44385 | PMM[1].Phase[3].Current[22]
SS2PMM1Phase3Current23 | REAL | IOD_SS2_TCP | 4387 | 44387 | PMM[1].Phase[3].Current[23]
SS2PMM1Phase3Current24 | REAL | IOD_SS2_TCP | 4389 | 44389 | PMM[1].Phase[3].Current[24]
SS2PMM1Phase3Current25 | REAL | IOD_SS2_TCP | 4391 | 44391 | PMM[1].Phase[3].Current[25]
SS2PMM1Phase3Current26 | REAL | IOD_SS2_TCP | 4393 | 44393 | PMM[1].Phase[3].Current[26]
SS2PMM1Phase3Current27 | REAL | IOD_SS2_TCP | 4395 | 44395 | PMM[1].Phase[3].Current[27]
SS2PMM1Phase3Current28 | REAL | IOD_SS2_TCP | 4397 | 44397 | PMM[1].Phase[3].Current[28]
SS2PMM1Phase3Current29 | REAL | IOD_SS2_TCP | 4399 | 44399 | PMM[1].Phase[3].Current[29]
SS2PMM1Phase3Current2 | REAL | IOD_SS2_TCP | 4401 | 44401 | PMM[1].Phase[3].Current[2]
SS2PMM1Phase3Current30 | REAL | IOD_SS2_TCP | 4403 | 44403 | PMM[1].Phase[3].Current[30]
SS2PMM1Phase3Current31 | REAL | IOD_SS2_TCP | 4405 | 44405 | PMM[1].Phase[3].Current[31]
SS2PMM1Phase3Current32 | REAL | IOD_SS2_TCP | 4407 | 44407 | PMM[1].Phase[3].Current[32]
SS2PMM1Phase3Current33 | REAL | IOD_SS2_TCP | 4409 | 44409 | PMM[1].Phase[3].Current[33]
SS2PMM1Phase3Current34 | REAL | IOD_SS2_TCP | 4411 | 44411 | PMM[1].Phase[3].Current[34]
SS2PMM1Phase3Current35 | REAL | IOD_SS2_TCP | 4413 | 44413 | PMM[1].Phase[3].Current[35]
SS2PMM1Phase3Current36 | REAL | IOD_SS2_TCP | 4415 | 44415 | PMM[1].Phase[3].Current[36]
SS2PMM1Phase3Current37 | REAL | IOD_SS2_TCP | 4417 | 44417 | PMM[1].Phase[3].Current[37]
SS2PMM1Phase3Current38 | REAL | IOD_SS2_TCP | 4419 | 44419 | PMM[1].Phase[3].Current[38]
SS2PMM1Phase3Current39 | REAL | IOD_SS2_TCP | 4421 | 44421 | PMM[1].Phase[3].Current[39]
SS2PMM1Phase3Current3 | REAL | IOD_SS2_TCP | 4423 | 44423 | PMM[1].Phase[3].Current[3]
SS2PMM1Phase3Current40 | REAL | IOD_SS2_TCP | 4425 | 44425 | PMM[1].Phase[3].Current[40]
SS2PMM1Phase3Current41 | REAL | IOD_SS2_TCP | 4427 | 44427 | PMM[1].Phase[3].Current[41]
SS2PMM1Phase3Current42 | REAL | IOD_SS2_TCP | 4429 | 44429 | PMM[1].Phase[3].Current[42]
SS2PMM1Phase3Current4 | REAL | IOD_SS2_TCP | 4431 | 44431 | PMM[1].Phase[3].Current[4]
SS2PMM1Phase3Current5 | REAL | IOD_SS2_TCP | 4433 | 44433 | PMM[1].Phase[3].Current[5]
SS2PMM1Phase3Current6 | REAL | IOD_SS2_TCP | 4435 | 44435 | PMM[1].Phase[3].Current[6]
SS2PMM1Phase3Current7 | REAL | IOD_SS2_TCP | 4437 | 44437 | PMM[1].Phase[3].Current[7]
SS2PMM1Phase3Current8 | REAL | IOD_SS2_TCP | 4439 | 44439 | PMM[1].Phase[3].Current[8]
SS2PMM1Phase3Current9 | REAL | IOD_SS2_TCP | 4441 | 44441 | PMM[1].Phase[3].Current[9]
SS2PMM1PowerFactorSys | REAL | IOD_SS2_TCP | 4443 | 44443 | PMM[1].PowerFactorSys
SS2PMM1ReactiveEnergyConsumed_kVARh | REAL | IOD_SS2_TCP | 4445 | 44445 | PMM[1].ReactiveEnergyConsumed_kVARh
SS2PMM1ReactivePowerPhaseA | REAL | IOD_SS2_TCP | 4447 | 44447 | PMM[1].ReactivePowerPhaseA
SS2PMM1ReactivePowerPhaseB | REAL | IOD_SS2_TCP | 4449 | 44449 | PMM[1].ReactivePowerPhaseB
SS2PMM1ReactivePowerPhaseC | REAL | IOD_SS2_TCP | 4451 | 44451 | PMM[1].ReactivePowerPhaseC
SS2PMM1TotalActivePower_kW | REAL | IOD_SS2_TCP | 4453 | 44453 | PMM[1].TotalActivePower_kW
SS2PMM1TotalAparentPower_kVA | REAL | IOD_SS2_TCP | 4455 | 44455 | PMM[1].TotalAparentPower_kVA
SS2PMM1TotalPowerFactor | REAL | IOD_SS2_TCP | 4457 | 44457 | PMM[1].TotalPowerFactor
SS2PMM1TotalReactivePower_kVAR | REAL | IOD_SS2_TCP | 4459 | 44459 | PMM[1].TotalReactivePower_kVAR
SS2PMM1VirA_fsys | REAL | IOD_SS2_TCP | 4461 | 44461 | PMM[1].VirA_fsys
SS2PMM1VirA_Isys | REAL | IOD_SS2_TCP | 4463 | 44463 | PMM[1].VirA_Isys
SS2PMM1VirA_PFsys | REAL | IOD_SS2_TCP | 4465 | 44465 | PMM[1].VirA_PFsys
SS2PMM1VirA_Psys | REAL | IOD_SS2_TCP | 4467 | 44467 | PMM[1].VirA_Psys
SS2PMM1VirA_Qsys | REAL | IOD_SS2_TCP | 4469 | 44469 | PMM[1].VirA_Qsys
SS2PMM1VirA_Ssys | REAL | IOD_SS2_TCP | 4471 | 44471 | PMM[1].VirA_Ssys
SS2PMM1VirA_Usys | REAL | IOD_SS2_TCP | 4473 | 44473 | PMM[1].VirA_Usys
SS2PMM1VirB_fsys | REAL | IOD_SS2_TCP | 4475 | 44475 | PMM[1].VirB_fsys
SS2PMM1VirB_Isys | REAL | IOD_SS2_TCP | 4477 | 44477 | PMM[1].VirB_Isys
SS2PMM1VirB_PFsys | REAL | IOD_SS2_TCP | 4479 | 44479 | PMM[1].VirB_PFsys
SS2PMM1VirB_Psys | REAL | IOD_SS2_TCP | 4481 | 44481 | PMM[1].VirB_Psys
SS2PMM1VirB_Qsys | REAL | IOD_SS2_TCP | 4483 | 44483 | PMM[1].VirB_Qsys
SS2PMM1VirB_Ssys | REAL | IOD_SS2_TCP | 4485 | 44485 | PMM[1].VirB_Ssys
SS2PMM1VirB_Usys | REAL | IOD_SS2_TCP | 4487 | 44487 | PMM[1].VirB_Usys
SS2PMM1VirBActiveEnergyConsumed_kWh | REAL | IOD_SS2_TCP | 4489 | 44489 | PMM[1].VirBActiveEnergyConsumed_kWh
SS2PMM1VirBActivePowerPhaseA_kW | REAL | IOD_SS2_TCP | 4491 | 44491 | PMM[1].VirBActivePowerPhaseA_kW
SS2PMM1VirBActivePowerPhaseB_kW | REAL | IOD_SS2_TCP | 4493 | 44493 | PMM[1].VirBActivePowerPhaseB_kW
SS2PMM1VirBActivePowerPhaseC_kW | REAL | IOD_SS2_TCP | 4495 | 44495 | PMM[1].VirBActivePowerPhaseC_kW
SS2PMM1VirBAparentPowerPhaseA | REAL | IOD_SS2_TCP | 4497 | 44497 | PMM[1].VirBAparentPowerPhaseA
SS2PMM1VirBAparentPowerPhaseB | REAL | IOD_SS2_TCP | 4499 | 44499 | PMM[1].VirBAparentPowerPhaseB
SS2PMM1VirBAparentPowerPhaseC | REAL | IOD_SS2_TCP | 4501 | 44501 | PMM[1].VirBAparentPowerPhaseC
SS2PMM1VirBAverageCurrent_A | REAL | IOD_SS2_TCP | 4503 | 44503 | PMM[1].VirBAverageCurrent_A
SS2PMM1VirBAveragePhaseToNeutral_V | REAL | IOD_SS2_TCP | 4505 | 44505 | PMM[1].VirBAveragePhaseToNeutral_V
SS2PMM1VirBAveragePhaseToPhase_V | REAL | IOD_SS2_TCP | 4507 | 44507 | PMM[1].VirBAveragePhaseToPhase_V
SS2PMM1VirBCurrentInPhaseA_A | REAL | IOD_SS2_TCP | 4509 | 44509 | PMM[1].VirBCurrentInPhaseA_A
SS2PMM1VirBCurrentInPhaseB_A | REAL | IOD_SS2_TCP | 4511 | 44511 | PMM[1].VirBCurrentInPhaseB_A
SS2PMM1VirBCurrentInPhaseC_A | REAL | IOD_SS2_TCP | 4513 | 44513 | PMM[1].VirBCurrentInPhaseC_A
SS2PMM1VirBFrequency_Hz | REAL | IOD_SS2_TCP | 4515 | 44515 | PMM[1].VirBFrequency_Hz
SS2PMM1VirBPowerFactorSys | REAL | IOD_SS2_TCP | 4517 | 44517 | PMM[1].VirBPowerFactorSys
SS2PMM1VirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS2_TCP | 4519 | 44519 | PMM[1].VirBReactiveEnergyConsumed_kVARh
SS2PMM1VirBReactivePowerPhaseA | REAL | IOD_SS2_TCP | 4521 | 44521 | PMM[1].VirBReactivePowerPhaseA
SS2PMM1VirBReactivePowerPhaseB | REAL | IOD_SS2_TCP | 4523 | 44523 | PMM[1].VirBReactivePowerPhaseB
SS2PMM1VirBReactivePowerPhaseC | REAL | IOD_SS2_TCP | 4525 | 44525 | PMM[1].VirBReactivePowerPhaseC
SS2PMM1VirBTotalActivePower_kW | REAL | IOD_SS2_TCP | 4527 | 44527 | PMM[1].VirBTotalActivePower_kW
SS2PMM1VirBTotalAparentPower_kVA | REAL | IOD_SS2_TCP | 4529 | 44529 | PMM[1].VirBTotalAparentPower_kVA
SS2PMM1VirBTotalPowerFactor | REAL | IOD_SS2_TCP | 4531 | 44531 | PMM[1].VirBTotalPowerFactor
SS2PMM1VirBTotalReactivePower_kVAR | REAL | IOD_SS2_TCP | 4533 | 44533 | PMM[1].VirBTotalReactivePower_kVAR
SS2PMM1VirBVoltageBetweenPhaseAB_V | REAL | IOD_SS2_TCP | 4535 | 44535 | PMM[1].VirBVoltageBetweenPhaseAB_V
SS2PMM1VirBVoltageBetweenPhaseAN_V | REAL | IOD_SS2_TCP | 4537 | 44537 | PMM[1].VirBVoltageBetweenPhaseAN_V
SS2PMM1VirBVoltageBetweenPhaseBC_V | REAL | IOD_SS2_TCP | 4539 | 44539 | PMM[1].VirBVoltageBetweenPhaseBC_V
SS2PMM1VirBVoltageBetweenPhaseBN_V | REAL | IOD_SS2_TCP | 4541 | 44541 | PMM[1].VirBVoltageBetweenPhaseBN_V
SS2PMM1VirBVoltageBetweenPhaseCA_V | REAL | IOD_SS2_TCP | 4543 | 44543 | PMM[1].VirBVoltageBetweenPhaseCA_V
SS2PMM1VirBVoltageBetweenPhaseCN_V | REAL | IOD_SS2_TCP | 4545 | 44545 | PMM[1].VirBVoltageBetweenPhaseCN_V
SS2PMM1VoltageBetweenPhaseAB_V | REAL | IOD_SS2_TCP | 4547 | 44547 | PMM[1].VoltageBetweenPhaseAB_V
SS2PMM1VoltageBetweenPhaseAN_V | REAL | IOD_SS2_TCP | 4549 | 44549 | PMM[1].VoltageBetweenPhaseAN_V
SS2PMM1VoltageBetweenPhaseBC_V | REAL | IOD_SS2_TCP | 4551 | 44551 | PMM[1].VoltageBetweenPhaseBC_V
SS2PMM1VoltageBetweenPhaseBN_V | REAL | IOD_SS2_TCP | 4553 | 44553 | PMM[1].VoltageBetweenPhaseBN_V
SS2PMM1VoltageBetweenPhaseCA_V | REAL | IOD_SS2_TCP | 4555 | 44555 | PMM[1].VoltageBetweenPhaseCA_V
SS2PMM1VoltageBetweenPhaseCN_V | REAL | IOD_SS2_TCP | 4557 | 44557 | PMM[1].VoltageBetweenPhaseCN_V
SS2PMM2ActiveEnergyConsumed_kWh | REAL | IOD_SS2_TCP | 4559 | 44559 | PMM[2].ActiveEnergyConsumed_kWh
SS2PMM2ActivePowerPhaseA_kW | REAL | IOD_SS2_TCP | 4561 | 44561 | PMM[2].ActivePowerPhaseA_kW
SS2PMM2ActivePowerPhaseB_kW | REAL | IOD_SS2_TCP | 4563 | 44563 | PMM[2].ActivePowerPhaseB_kW
SS2PMM2ActivePowerPhaseC_kW | REAL | IOD_SS2_TCP | 4565 | 44565 | PMM[2].ActivePowerPhaseC_kW
SS2PMM2AparentPowerPhaseA | REAL | IOD_SS2_TCP | 4567 | 44567 | PMM[2].AparentPowerPhaseA
SS2PMM2AparentPowerPhaseB | REAL | IOD_SS2_TCP | 4569 | 44569 | PMM[2].AparentPowerPhaseB
SS2PMM2AparentPowerPhaseC | REAL | IOD_SS2_TCP | 4571 | 44571 | PMM[2].AparentPowerPhaseC
SS2PMM2AverageCurrent_A | REAL | IOD_SS2_TCP | 4573 | 44573 | PMM[2].AverageCurrent_A
SS2PMM2AveragePhaseToNeutral_V | REAL | IOD_SS2_TCP | 4575 | 44575 | PMM[2].AveragePhaseToNeutral_V
SS2PMM2AveragePhaseToPhase_V | REAL | IOD_SS2_TCP | 4577 | 44577 | PMM[2].AveragePhaseToPhase_V
SS2PMM2CurrentInPhaseA_A | REAL | IOD_SS2_TCP | 4579 | 44579 | PMM[2].CurrentInPhaseA_A
SS2PMM2CurrentInPhaseB_A | REAL | IOD_SS2_TCP | 4581 | 44581 | PMM[2].CurrentInPhaseB_A
SS2PMM2CurrentInPhaseC_A | REAL | IOD_SS2_TCP | 4583 | 44583 | PMM[2].CurrentInPhaseC_A
SS2PMM2Frequency_Hz | REAL | IOD_SS2_TCP | 4585 | 44585 | PMM[2].Frequency_Hz
SS2PMM2Phase1Current1 | REAL | IOD_SS2_TCP | 4587 | 44587 | PMM[2].Phase[1].Current[1]
SS2PMM2Phase1Current2 | REAL | IOD_SS2_TCP | 4589 | 44589 | PMM[2].Phase[1].Current[2]
SS2PMM2Phase1Current3 | REAL | IOD_SS2_TCP | 4591 | 44591 | PMM[2].Phase[1].Current[3]
SS2PMM2Phase1Current4 | REAL | IOD_SS2_TCP | 4593 | 44593 | PMM[2].Phase[1].Current[4]
SS2PMM2Phase1Current5 | REAL | IOD_SS2_TCP | 4595 | 44595 | PMM[2].Phase[1].Current[5]
SS2PMM2Phase1Current6 | REAL | IOD_SS2_TCP | 4597 | 44597 | PMM[2].Phase[1].Current[6]
SS2PMM2Phase1Current7 | REAL | IOD_SS2_TCP | 4599 | 44599 | PMM[2].Phase[1].Current[7]
SS2PMM2Phase1Current8 | REAL | IOD_SS2_TCP | 4601 | 44601 | PMM[2].Phase[1].Current[8]
SS2PMM2Phase1Current9 | REAL | IOD_SS2_TCP | 4603 | 44603 | PMM[2].Phase[1].Current[9]
SS2PMM2Phase1Current10 | REAL | IOD_SS2_TCP | 4605 | 44605 | PMM[2].Phase[1].Current[10]
SS2PMM2Phase1Current11 | REAL | IOD_SS2_TCP | 4607 | 44607 | PMM[2].Phase[1].Current[11]
SS2PMM2Phase1Current12 | REAL | IOD_SS2_TCP | 4609 | 44609 | PMM[2].Phase[1].Current[12]
SS2PMM2Phase1Current13 | REAL | IOD_SS2_TCP | 4611 | 44611 | PMM[2].Phase[1].Current[13]
SS2PMM2Phase1Current14 | REAL | IOD_SS2_TCP | 4613 | 44613 | PMM[2].Phase[1].Current[14]
SS2PMM2Phase1Current15 | REAL | IOD_SS2_TCP | 4615 | 44615 | PMM[2].Phase[1].Current[15]
SS2PMM2Phase1Current16 | REAL | IOD_SS2_TCP | 4617 | 44617 | PMM[2].Phase[1].Current[16]
SS2PMM2Phase1Current17 | REAL | IOD_SS2_TCP | 4619 | 44619 | PMM[2].Phase[1].Current[17]
SS2PMM2Phase1Current18 | REAL | IOD_SS2_TCP | 4621 | 44621 | PMM[2].Phase[1].Current[18]
SS2PMM2Phase1Current19 | REAL | IOD_SS2_TCP | 4623 | 44623 | PMM[2].Phase[1].Current[19]
SS2PMM2Phase1Current20 | REAL | IOD_SS2_TCP | 4625 | 44625 | PMM[2].Phase[1].Current[20]
SS2PMM2Phase1Current21 | REAL | IOD_SS2_TCP | 4627 | 44627 | PMM[2].Phase[1].Current[21]
SS2PMM2Phase1Current22 | REAL | IOD_SS2_TCP | 4629 | 44629 | PMM[2].Phase[1].Current[22]
SS2PMM2Phase1Current23 | REAL | IOD_SS2_TCP | 4631 | 44631 | PMM[2].Phase[1].Current[23]
SS2PMM2Phase1Current24 | REAL | IOD_SS2_TCP | 4633 | 44633 | PMM[2].Phase[1].Current[24]
SS2PMM2Phase1Current25 | REAL | IOD_SS2_TCP | 4635 | 44635 | PMM[2].Phase[1].Current[25]
SS2PMM2Phase1Current26 | REAL | IOD_SS2_TCP | 4637 | 44637 | PMM[2].Phase[1].Current[26]
SS2PMM2Phase1Current27 | REAL | IOD_SS2_TCP | 4639 | 44639 | PMM[2].Phase[1].Current[27]
SS2PMM2Phase1Current28 | REAL | IOD_SS2_TCP | 4641 | 44641 | PMM[2].Phase[1].Current[28]
SS2PMM2Phase1Current29 | REAL | IOD_SS2_TCP | 4643 | 44643 | PMM[2].Phase[1].Current[29]
SS2PMM2Phase1Current30 | REAL | IOD_SS2_TCP | 4645 | 44645 | PMM[2].Phase[1].Current[30]
SS2PMM2Phase1Current31 | REAL | IOD_SS2_TCP | 4647 | 44647 | PMM[2].Phase[1].Current[31]
SS2PMM2Phase1Current32 | REAL | IOD_SS2_TCP | 4649 | 44649 | PMM[2].Phase[1].Current[32]
SS2PMM2Phase1Current33 | REAL | IOD_SS2_TCP | 4651 | 44651 | PMM[2].Phase[1].Current[33]
SS2PMM2Phase1Current34 | REAL | IOD_SS2_TCP | 4653 | 44653 | PMM[2].Phase[1].Current[34]
SS2PMM2Phase1Current35 | REAL | IOD_SS2_TCP | 4655 | 44655 | PMM[2].Phase[1].Current[35]
SS2PMM2Phase1Current36 | REAL | IOD_SS2_TCP | 4657 | 44657 | PMM[2].Phase[1].Current[36]
SS2PMM2Phase1Current37 | REAL | IOD_SS2_TCP | 4659 | 44659 | PMM[2].Phase[1].Current[37]
SS2PMM2Phase1Current38 | REAL | IOD_SS2_TCP | 4661 | 44661 | PMM[2].Phase[1].Current[38]
SS2PMM2Phase1Current39 | REAL | IOD_SS2_TCP | 4663 | 44663 | PMM[2].Phase[1].Current[39]
SS2PMM2Phase1Current40 | REAL | IOD_SS2_TCP | 4665 | 44665 | PMM[2].Phase[1].Current[40]
SS2PMM2Phase1Current41 | REAL | IOD_SS2_TCP | 4667 | 44667 | PMM[2].Phase[1].Current[41]
SS2PMM2Phase1Current42 | REAL | IOD_SS2_TCP | 4669 | 44669 | PMM[2].Phase[1].Current[42]
SS2PMM2Phase2Current10 | REAL | IOD_SS2_TCP | 4671 | 44671 | PMM[2].Phase[2].Current[10]
SS2PMM2Phase2Current11 | REAL | IOD_SS2_TCP | 4673 | 44673 | PMM[2].Phase[2].Current[11]
SS2PMM2Phase2Current12 | REAL | IOD_SS2_TCP | 4675 | 44675 | PMM[2].Phase[2].Current[12]
SS2PMM2Phase2Current13 | REAL | IOD_SS2_TCP | 4677 | 44677 | PMM[2].Phase[2].Current[13]
SS2PMM2Phase2Current14 | REAL | IOD_SS2_TCP | 4679 | 44679 | PMM[2].Phase[2].Current[14]
SS2PMM2Phase2Current15 | REAL | IOD_SS2_TCP | 4681 | 44681 | PMM[2].Phase[2].Current[15]
SS2PMM2Phase2Current16 | REAL | IOD_SS2_TCP | 4683 | 44683 | PMM[2].Phase[2].Current[16]
SS2PMM2Phase2Current17 | REAL | IOD_SS2_TCP | 4685 | 44685 | PMM[2].Phase[2].Current[17]
SS2PMM2Phase2Current18 | REAL | IOD_SS2_TCP | 4687 | 44687 | PMM[2].Phase[2].Current[18]
SS2PMM2Phase2Current19 | REAL | IOD_SS2_TCP | 4689 | 44689 | PMM[2].Phase[2].Current[19]
SS2PMM2Phase2Current1 | REAL | IOD_SS2_TCP | 4691 | 44691 | PMM[2].Phase[2].Current[1]
SS2PMM2Phase2Current20 | REAL | IOD_SS2_TCP | 4693 | 44693 | PMM[2].Phase[2].Current[20]
SS2PMM2Phase2Current21 | REAL | IOD_SS2_TCP | 4695 | 44695 | PMM[2].Phase[2].Current[21]
SS2PMM2Phase2Current22 | REAL | IOD_SS2_TCP | 4697 | 44697 | PMM[2].Phase[2].Current[22]
SS2PMM2Phase2Current23 | REAL | IOD_SS2_TCP | 4699 | 44699 | PMM[2].Phase[2].Current[23]
SS2PMM2Phase2Current24 | REAL | IOD_SS2_TCP | 4701 | 44701 | PMM[2].Phase[2].Current[24]
SS2PMM2Phase2Current25 | REAL | IOD_SS2_TCP | 4703 | 44703 | PMM[2].Phase[2].Current[25]
SS2PMM2Phase2Current26 | REAL | IOD_SS2_TCP | 4705 | 44705 | PMM[2].Phase[2].Current[26]
SS2PMM2Phase2Current27 | REAL | IOD_SS2_TCP | 4707 | 44707 | PMM[2].Phase[2].Current[27]
SS2PMM2Phase2Current28 | REAL | IOD_SS2_TCP | 4709 | 44709 | PMM[2].Phase[2].Current[28]
SS2PMM2Phase2Current29 | REAL | IOD_SS2_TCP | 4711 | 44711 | PMM[2].Phase[2].Current[29]
SS2PMM2Phase2Current2 | REAL | IOD_SS2_TCP | 4713 | 44713 | PMM[2].Phase[2].Current[2]
SS2PMM2Phase2Current30 | REAL | IOD_SS2_TCP | 4715 | 44715 | PMM[2].Phase[2].Current[30]
SS2PMM2Phase2Current31 | REAL | IOD_SS2_TCP | 4717 | 44717 | PMM[2].Phase[2].Current[31]
SS2PMM2Phase2Current32 | REAL | IOD_SS2_TCP | 4719 | 44719 | PMM[2].Phase[2].Current[32]
SS2PMM2Phase2Current33 | REAL | IOD_SS2_TCP | 4721 | 44721 | PMM[2].Phase[2].Current[33]
SS2PMM2Phase2Current34 | REAL | IOD_SS2_TCP | 4723 | 44723 | PMM[2].Phase[2].Current[34]
SS2PMM2Phase2Current35 | REAL | IOD_SS2_TCP | 4725 | 44725 | PMM[2].Phase[2].Current[35]
SS2PMM2Phase2Current36 | REAL | IOD_SS2_TCP | 4727 | 44727 | PMM[2].Phase[2].Current[36]
SS2PMM2Phase2Current37 | REAL | IOD_SS2_TCP | 4729 | 44729 | PMM[2].Phase[2].Current[37]
SS2PMM2Phase2Current38 | REAL | IOD_SS2_TCP | 4731 | 44731 | PMM[2].Phase[2].Current[38]
SS2PMM2Phase2Current39 | REAL | IOD_SS2_TCP | 4733 | 44733 | PMM[2].Phase[2].Current[39]
SS2PMM2Phase2Current3 | REAL | IOD_SS2_TCP | 4735 | 44735 | PMM[2].Phase[2].Current[3]
SS2PMM2Phase2Current40 | REAL | IOD_SS2_TCP | 4737 | 44737 | PMM[2].Phase[2].Current[40]
SS2PMM2Phase2Current41 | REAL | IOD_SS2_TCP | 4739 | 44739 | PMM[2].Phase[2].Current[41]
SS2PMM2Phase2Current42 | REAL | IOD_SS2_TCP | 4741 | 44741 | PMM[2].Phase[2].Current[42]
SS2PMM2Phase2Current4 | REAL | IOD_SS2_TCP | 4743 | 44743 | PMM[2].Phase[2].Current[4]
SS2PMM2Phase2Current5 | REAL | IOD_SS2_TCP | 4745 | 44745 | PMM[2].Phase[2].Current[5]
SS2PMM2Phase2Current6 | REAL | IOD_SS2_TCP | 4747 | 44747 | PMM[2].Phase[2].Current[6]
SS2PMM2Phase2Current7 | REAL | IOD_SS2_TCP | 4749 | 44749 | PMM[2].Phase[2].Current[7]
SS2PMM2Phase2Current8 | REAL | IOD_SS2_TCP | 4751 | 44751 | PMM[2].Phase[2].Current[8]
SS2PMM2Phase2Current9 | REAL | IOD_SS2_TCP | 4753 | 44753 | PMM[2].Phase[2].Current[9]
SS2PMM2Phase3Current10 | REAL | IOD_SS2_TCP | 4755 | 44755 | PMM[2].Phase[3].Current[10]
SS2PMM2Phase3Current11 | REAL | IOD_SS2_TCP | 4757 | 44757 | PMM[2].Phase[3].Current[11]
SS2PMM2Phase3Current12 | REAL | IOD_SS2_TCP | 4759 | 44759 | PMM[2].Phase[3].Current[12]
SS2PMM2Phase3Current13 | REAL | IOD_SS2_TCP | 4761 | 44761 | PMM[2].Phase[3].Current[13]
SS2PMM2Phase3Current14 | REAL | IOD_SS2_TCP | 4763 | 44763 | PMM[2].Phase[3].Current[14]
SS2PMM2Phase3Current15 | REAL | IOD_SS2_TCP | 4765 | 44765 | PMM[2].Phase[3].Current[15]
SS2PMM2Phase3Current16 | REAL | IOD_SS2_TCP | 4767 | 44767 | PMM[2].Phase[3].Current[16]
SS2PMM2Phase3Current17 | REAL | IOD_SS2_TCP | 4769 | 44769 | PMM[2].Phase[3].Current[17]
SS2PMM2Phase3Current18 | REAL | IOD_SS2_TCP | 4771 | 44771 | PMM[2].Phase[3].Current[18]
SS2PMM2Phase3Current19 | REAL | IOD_SS2_TCP | 4773 | 44773 | PMM[2].Phase[3].Current[19]
SS2PMM2Phase3Current1 | REAL | IOD_SS2_TCP | 4775 | 44775 | PMM[2].Phase[3].Current[1]
SS2PMM2Phase3Current20 | REAL | IOD_SS2_TCP | 4777 | 44777 | PMM[2].Phase[3].Current[20]
SS2PMM2Phase3Current21 | REAL | IOD_SS2_TCP | 4779 | 44779 | PMM[2].Phase[3].Current[21]
SS2PMM2Phase3Current22 | REAL | IOD_SS2_TCP | 4781 | 44781 | PMM[2].Phase[3].Current[22]
SS2PMM2Phase3Current23 | REAL | IOD_SS2_TCP | 4783 | 44783 | PMM[2].Phase[3].Current[23]
SS2PMM2Phase3Current24 | REAL | IOD_SS2_TCP | 4785 | 44785 | PMM[2].Phase[3].Current[24]
SS2PMM2Phase3Current25 | REAL | IOD_SS2_TCP | 4787 | 44787 | PMM[2].Phase[3].Current[25]
SS2PMM2Phase3Current26 | REAL | IOD_SS2_TCP | 4789 | 44789 | PMM[2].Phase[3].Current[26]
SS2PMM2Phase3Current27 | REAL | IOD_SS2_TCP | 4791 | 44791 | PMM[2].Phase[3].Current[27]
SS2PMM2Phase3Current28 | REAL | IOD_SS2_TCP | 4793 | 44793 | PMM[2].Phase[3].Current[28]
SS2PMM2Phase3Current29 | REAL | IOD_SS2_TCP | 4795 | 44795 | PMM[2].Phase[3].Current[29]
SS2PMM2Phase3Current2 | REAL | IOD_SS2_TCP | 4797 | 44797 | PMM[2].Phase[3].Current[2]
SS2PMM2Phase3Current30 | REAL | IOD_SS2_TCP | 4799 | 44799 | PMM[2].Phase[3].Current[30]
SS2PMM2Phase3Current31 | REAL | IOD_SS2_TCP | 4801 | 44801 | PMM[2].Phase[3].Current[31]
SS2PMM2Phase3Current32 | REAL | IOD_SS2_TCP | 4803 | 44803 | PMM[2].Phase[3].Current[32]
SS2PMM2Phase3Current33 | REAL | IOD_SS2_TCP | 4805 | 44805 | PMM[2].Phase[3].Current[33]
SS2PMM2Phase3Current34 | REAL | IOD_SS2_TCP | 4807 | 44807 | PMM[2].Phase[3].Current[34]
SS2PMM2Phase3Current35 | REAL | IOD_SS2_TCP | 4809 | 44809 | PMM[2].Phase[3].Current[35]
SS2PMM2Phase3Current36 | REAL | IOD_SS2_TCP | 4811 | 44811 | PMM[2].Phase[3].Current[36]
SS2PMM2Phase3Current37 | REAL | IOD_SS2_TCP | 4813 | 44813 | PMM[2].Phase[3].Current[37]
SS2PMM2Phase3Current38 | REAL | IOD_SS2_TCP | 4815 | 44815 | PMM[2].Phase[3].Current[38]
SS2PMM2Phase3Current39 | REAL | IOD_SS2_TCP | 4817 | 44817 | PMM[2].Phase[3].Current[39]
SS2PMM2Phase3Current3 | REAL | IOD_SS2_TCP | 4819 | 44819 | PMM[2].Phase[3].Current[3]
SS2PMM2Phase3Current40 | REAL | IOD_SS2_TCP | 4821 | 44821 | PMM[2].Phase[3].Current[40]
SS2PMM2Phase3Current41 | REAL | IOD_SS2_TCP | 4823 | 44823 | PMM[2].Phase[3].Current[41]
SS2PMM2Phase3Current42 | REAL | IOD_SS2_TCP | 4825 | 44825 | PMM[2].Phase[3].Current[42]
SS2PMM2Phase3Current4 | REAL | IOD_SS2_TCP | 4827 | 44827 | PMM[2].Phase[3].Current[4]
SS2PMM2Phase3Current5 | REAL | IOD_SS2_TCP | 4829 | 44829 | PMM[2].Phase[3].Current[5]
SS2PMM2Phase3Current6 | REAL | IOD_SS2_TCP | 4831 | 44831 | PMM[2].Phase[3].Current[6]
SS2PMM2Phase3Current7 | REAL | IOD_SS2_TCP | 4833 | 44833 | PMM[2].Phase[3].Current[7]
SS2PMM2Phase3Current8 | REAL | IOD_SS2_TCP | 4835 | 44835 | PMM[2].Phase[3].Current[8]
SS2PMM2Phase3Current9 | REAL | IOD_SS2_TCP | 4837 | 44837 | PMM[2].Phase[3].Current[9]
SS2PMM2PowerFactorSys | REAL | IOD_SS2_TCP | 4839 | 44839 | PMM[2].PowerFactorSys
SS2PMM2ReactiveEnergyConsumed_kVARh | REAL | IOD_SS2_TCP | 4841 | 44841 | PMM[2].ReactiveEnergyConsumed_kVARh
SS2PMM2ReactivePowerPhaseA | REAL | IOD_SS2_TCP | 4843 | 44843 | PMM[2].ReactivePowerPhaseA
SS2PMM2ReactivePowerPhaseB | REAL | IOD_SS2_TCP | 4845 | 44845 | PMM[2].ReactivePowerPhaseB
SS2PMM2ReactivePowerPhaseC | REAL | IOD_SS2_TCP | 4847 | 44847 | PMM[2].ReactivePowerPhaseC
SS2PMM2TotalActivePower_kW | REAL | IOD_SS2_TCP | 4849 | 44849 | PMM[2].TotalActivePower_kW
SS2PMM2TotalAparentPower_kVA | REAL | IOD_SS2_TCP | 4851 | 44851 | PMM[2].TotalAparentPower_kVA
SS2PMM2TotalPowerFactor | REAL | IOD_SS2_TCP | 4853 | 44853 | PMM[2].TotalPowerFactor
SS2PMM2TotalReactivePower_kVAR | REAL | IOD_SS2_TCP | 4855 | 44855 | PMM[2].TotalReactivePower_kVAR
SS2PMM2VirA_fsys | REAL | IOD_SS2_TCP | 4857 | 44857 | PMM[2].VirA_fsys
SS2PMM2VirA_Isys | REAL | IOD_SS2_TCP | 4859 | 44859 | PMM[2].VirA_Isys
SS2PMM2VirA_PFsys | REAL | IOD_SS2_TCP | 4861 | 44861 | PMM[2].VirA_PFsys
SS2PMM2VirA_Psys | REAL | IOD_SS2_TCP | 4863 | 44863 | PMM[2].VirA_Psys
SS2PMM2VirA_Qsys | REAL | IOD_SS2_TCP | 4865 | 44865 | PMM[2].VirA_Qsys
SS2PMM2VirA_Ssys | REAL | IOD_SS2_TCP | 4867 | 44867 | PMM[2].VirA_Ssys
SS2PMM2VirA_Usys | REAL | IOD_SS2_TCP | 4869 | 44869 | PMM[2].VirA_Usys
SS2PMM2VirB_fsys | REAL | IOD_SS2_TCP | 4871 | 44871 | PMM[2].VirB_fsys
SS2PMM2VirB_Isys | REAL | IOD_SS2_TCP | 4873 | 44873 | PMM[2].VirB_Isys
SS2PMM2VirB_PFsys | REAL | IOD_SS2_TCP | 4875 | 44875 | PMM[2].VirB_PFsys
SS2PMM2VirB_Psys | REAL | IOD_SS2_TCP | 4877 | 44877 | PMM[2].VirB_Psys
SS2PMM2VirB_Qsys | REAL | IOD_SS2_TCP | 4879 | 44879 | PMM[2].VirB_Qsys
SS2PMM2VirB_Ssys | REAL | IOD_SS2_TCP | 4881 | 44881 | PMM[2].VirB_Ssys
SS2PMM2VirB_Usys | REAL | IOD_SS2_TCP | 4883 | 44883 | PMM[2].VirB_Usys
SS2PMM2VirBActiveEnergyConsumed_kWh | REAL | IOD_SS2_TCP | 4885 | 44885 | PMM[2].VirBActiveEnergyConsumed_kWh
SS2PMM2VirBActivePowerPhaseA_kW | REAL | IOD_SS2_TCP | 4887 | 44887 | PMM[2].VirBActivePowerPhaseA_kW
SS2PMM2VirBActivePowerPhaseB_kW | REAL | IOD_SS2_TCP | 4889 | 44889 | PMM[2].VirBActivePowerPhaseB_kW
SS2PMM2VirBActivePowerPhaseC_kW | REAL | IOD_SS2_TCP | 4891 | 44891 | PMM[2].VirBActivePowerPhaseC_kW
SS2PMM2VirBAparentPowerPhaseA | REAL | IOD_SS2_TCP | 4893 | 44893 | PMM[2].VirBAparentPowerPhaseA
SS2PMM2VirBAparentPowerPhaseB | REAL | IOD_SS2_TCP | 4895 | 44895 | PMM[2].VirBAparentPowerPhaseB
SS2PMM2VirBAparentPowerPhaseC | REAL | IOD_SS2_TCP | 4897 | 44897 | PMM[2].VirBAparentPowerPhaseC
SS2PMM2VirBAverageCurrent_A | REAL | IOD_SS2_TCP | 4899 | 44899 | PMM[2].VirBAverageCurrent_A
SS2PMM2VirBAveragePhaseToNeutral_V | REAL | IOD_SS2_TCP | 4901 | 44901 | PMM[2].VirBAveragePhaseToNeutral_V
SS2PMM2VirBAveragePhaseToPhase_V | REAL | IOD_SS2_TCP | 4903 | 44903 | PMM[2].VirBAveragePhaseToPhase_V
SS2PMM2VirBCurrentInPhaseA_A | REAL | IOD_SS2_TCP | 4905 | 44905 | PMM[2].VirBCurrentInPhaseA_A
SS2PMM2VirBCurrentInPhaseB_A | REAL | IOD_SS2_TCP | 4907 | 44907 | PMM[2].VirBCurrentInPhaseB_A
SS2PMM2VirBCurrentInPhaseC_A | REAL | IOD_SS2_TCP | 4909 | 44909 | PMM[2].VirBCurrentInPhaseC_A
SS2PMM2VirBFrequency_Hz | REAL | IOD_SS2_TCP | 4911 | 44911 | PMM[2].VirBFrequency_Hz
SS2PMM2VirBPowerFactorSys | REAL | IOD_SS2_TCP | 4913 | 44913 | PMM[2].VirBPowerFactorSys
SS2PMM2VirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS2_TCP | 4915 | 44915 | PMM[2].VirBReactiveEnergyConsumed_kVARh
SS2PMM2VirBReactivePowerPhaseA | REAL | IOD_SS2_TCP | 4917 | 44917 | PMM[2].VirBReactivePowerPhaseA
SS2PMM2VirBReactivePowerPhaseB | REAL | IOD_SS2_TCP | 4919 | 44919 | PMM[2].VirBReactivePowerPhaseB
SS2PMM2VirBReactivePowerPhaseC | REAL | IOD_SS2_TCP | 4921 | 44921 | PMM[2].VirBReactivePowerPhaseC
SS2PMM2VirBTotalActivePower_kW | REAL | IOD_SS2_TCP | 4923 | 44923 | PMM[2].VirBTotalActivePower_kW
SS2PMM2VirBTotalAparentPower_kVA | REAL | IOD_SS2_TCP | 4925 | 44925 | PMM[2].VirBTotalAparentPower_kVA
SS2PMM2VirBTotalPowerFactor | REAL | IOD_SS2_TCP | 4927 | 44927 | PMM[2].VirBTotalPowerFactor
SS2PMM2VirBTotalReactivePower_kVAR | REAL | IOD_SS2_TCP | 4929 | 44929 | PMM[2].VirBTotalReactivePower_kVAR
SS2PMM2VirBVoltageBetweenPhaseAB_V | REAL | IOD_SS2_TCP | 4931 | 44931 | PMM[2].VirBVoltageBetweenPhaseAB_V
SS2PMM2VirBVoltageBetweenPhaseAN_V | REAL | IOD_SS2_TCP | 4933 | 44933 | PMM[2].VirBVoltageBetweenPhaseAN_V
SS2PMM2VirBVoltageBetweenPhaseBC_V | REAL | IOD_SS2_TCP | 4935 | 44935 | PMM[2].VirBVoltageBetweenPhaseBC_V
SS2PMM2VirBVoltageBetweenPhaseBN_V | REAL | IOD_SS2_TCP | 4937 | 44937 | PMM[2].VirBVoltageBetweenPhaseBN_V
SS2PMM2VirBVoltageBetweenPhaseCA_V | REAL | IOD_SS2_TCP | 4939 | 44939 | PMM[2].VirBVoltageBetweenPhaseCA_V
SS2PMM2VirBVoltageBetweenPhaseCN_V | REAL | IOD_SS2_TCP | 4941 | 44941 | PMM[2].VirBVoltageBetweenPhaseCN_V
SS2PMM2VoltageBetweenPhaseAB_V | REAL | IOD_SS2_TCP | 4943 | 44943 | PMM[2].VoltageBetweenPhaseAB_V
SS2PMM2VoltageBetweenPhaseAN_V | REAL | IOD_SS2_TCP | 4945 | 44945 | PMM[2].VoltageBetweenPhaseAN_V
SS2PMM2VoltageBetweenPhaseBC_V | REAL | IOD_SS2_TCP | 4947 | 44947 | PMM[2].VoltageBetweenPhaseBC_V
SS2PMM2VoltageBetweenPhaseBN_V | REAL | IOD_SS2_TCP | 4949 | 44949 | PMM[2].VoltageBetweenPhaseBN_V
SS2PMM2VoltageBetweenPhaseCA_V | REAL | IOD_SS2_TCP | 4951 | 44951 | PMM[2].VoltageBetweenPhaseCA_V
SS2PMM2VoltageBetweenPhaseCN_V | REAL | IOD_SS2_TCP | 4953 | 44953 | PMM[2].VoltageBetweenPhaseCN_V
SS2PMMPanelActiveEnergyConsumed_kWh | REAL | IOD_SS2_TCP | 4955 | 44955 | PMMPanel.ActiveEnergyConsumed_kWh
SS2PMMPanelActivePowerPhaseA_kW | REAL | IOD_SS2_TCP | 4957 | 44957 | PMMPanel.ActivePowerPhaseA_kW
SS2PMMPanelActivePowerPhaseB_kW | REAL | IOD_SS2_TCP | 4959 | 44959 | PMMPanel.ActivePowerPhaseB_kW
SS2PMMPanelActivePowerPhaseC_kW | REAL | IOD_SS2_TCP | 4961 | 44961 | PMMPanel.ActivePowerPhaseC_kW
SS2PMMPanelAparentPowerPhaseA | REAL | IOD_SS2_TCP | 4963 | 44963 | PMMPanel.AparentPowerPhaseA
SS2PMMPanelAparentPowerPhaseB | REAL | IOD_SS2_TCP | 4965 | 44965 | PMMPanel.AparentPowerPhaseB
SS2PMMPanelAparentPowerPhaseC | REAL | IOD_SS2_TCP | 4967 | 44967 | PMMPanel.AparentPowerPhaseC
SS2PMMPanelAverageCurrent_A | REAL | IOD_SS2_TCP | 4969 | 44969 | PMMPanel.AverageCurrent_A
SS2PMMPanelAveragePhaseToNeutral_V | REAL | IOD_SS2_TCP | 4971 | 44971 | PMMPanel.AveragePhaseToNeutral_V
SS2PMMPanelAveragePhaseToPhase_V | REAL | IOD_SS2_TCP | 4973 | 44973 | PMMPanel.AveragePhaseToPhase_V
SS2PMMPanelCurrentInPhaseA_A | REAL | IOD_SS2_TCP | 4975 | 44975 | PMMPanel.CurrentInPhaseA_A
SS2PMMPanelCurrentInPhaseB_A | REAL | IOD_SS2_TCP | 4977 | 44977 | PMMPanel.CurrentInPhaseB_A
SS2PMMPanelCurrentInPhaseC_A | REAL | IOD_SS2_TCP | 4979 | 44979 | PMMPanel.CurrentInPhaseC_A
SS2PMMPanelFrequency_Hz | REAL | IOD_SS2_TCP | 4981 | 44981 | PMMPanel.Frequency_Hz
SS2PMMPanelPowerFactorSys | REAL | IOD_SS2_TCP | 4983 | 44983 | PMMPanel.PowerFactorSys
SS2PMMPanelReactiveEnergyConsumed_kVARh | REAL | IOD_SS2_TCP | 4985 | 44985 | PMMPanel.ReactiveEnergyConsumed_kVARh
SS2PMMPanelReactivePowerPhaseA | REAL | IOD_SS2_TCP | 4987 | 44987 | PMMPanel.ReactivePowerPhaseA
SS2PMMPanelReactivePowerPhaseB | REAL | IOD_SS2_TCP | 4989 | 44989 | PMMPanel.ReactivePowerPhaseB
SS2PMMPanelReactivePowerPhaseC | REAL | IOD_SS2_TCP | 4991 | 44991 | PMMPanel.ReactivePowerPhaseC
SS2PMMPanelTotalActivePower_kW | REAL | IOD_SS2_TCP | 4993 | 44993 | PMMPanel.TotalActivePower_kW
SS2PMMPanelTotalAparentPower_kVA | REAL | IOD_SS2_TCP | 4995 | 44995 | PMMPanel.TotalAparentPower_kVA
SS2PMMPanelTotalPowerFactor | REAL | IOD_SS2_TCP | 4997 | 44997 | PMMPanel.TotalPowerFactor
SS2PMMPanelTotalReactivePower_kVAR | REAL | IOD_SS2_TCP | 4999 | 44999 | PMMPanel.TotalReactivePower_kVAR
SS2PMMPanelVirA_fsys | REAL | IOD_SS2_TCP | 5001 | 45001 | PMMPanel.VirA_fsys
SS2PMMPanelVirA_Isys | REAL | IOD_SS2_TCP | 5003 | 45003 | PMMPanel.VirA_Isys
SS2PMMPanelVirA_PFsys | REAL | IOD_SS2_TCP | 5005 | 45005 | PMMPanel.VirA_PFsys
SS2PMMPanelVirA_Psys | REAL | IOD_SS2_TCP | 5007 | 45007 | PMMPanel.VirA_Psys
SS2PMMPanelVirA_Qsys | REAL | IOD_SS2_TCP | 5009 | 45009 | PMMPanel.VirA_Qsys
SS2PMMPanelVirA_Ssys | REAL | IOD_SS2_TCP | 5011 | 45011 | PMMPanel.VirA_Ssys
SS2PMMPanelVirA_Usys | REAL | IOD_SS2_TCP | 5013 | 45013 | PMMPanel.VirA_Usys
SS2PMMPanelVirB_fsys | REAL | IOD_SS2_TCP | 5015 | 45015 | PMMPanel.VirB_fsys
SS2PMMPanelVirB_Isys | REAL | IOD_SS2_TCP | 5017 | 45017 | PMMPanel.VirB_Isys
SS2PMMPanelVirB_PFsys | REAL | IOD_SS2_TCP | 5019 | 45019 | PMMPanel.VirB_PFsys
SS2PMMPanelVirB_Psys | REAL | IOD_SS2_TCP | 5021 | 45021 | PMMPanel.VirB_Psys
SS2PMMPanelVirB_Qsys | REAL | IOD_SS2_TCP | 5023 | 45023 | PMMPanel.VirB_Qsys
SS2PMMPanelVirB_Ssys | REAL | IOD_SS2_TCP | 5025 | 45025 | PMMPanel.VirB_Ssys
SS2PMMPanelVirB_Usys | REAL | IOD_SS2_TCP | 5027 | 45027 | PMMPanel.VirB_Usys
SS2PMMPanelVirBActiveEnergyConsumed_kWh | REAL | IOD_SS2_TCP | 5029 | 45029 | PMMPanel.VirBActiveEnergyConsumed_kWh
SS2PMMPanelVirBActivePowerPhaseA_kW | REAL | IOD_SS2_TCP | 5031 | 45031 | PMMPanel.VirBActivePowerPhaseA_kW
SS2PMMPanelVirBActivePowerPhaseB_kW | REAL | IOD_SS2_TCP | 5033 | 45033 | PMMPanel.VirBActivePowerPhaseB_kW
SS2PMMPanelVirBActivePowerPhaseC_kW | REAL | IOD_SS2_TCP | 5035 | 45035 | PMMPanel.VirBActivePowerPhaseC_kW
SS2PMMPanelVirBAparentPowerPhaseA | REAL | IOD_SS2_TCP | 5037 | 45037 | PMMPanel.VirBAparentPowerPhaseA
SS2PMMPanelVirBAparentPowerPhaseB | REAL | IOD_SS2_TCP | 5039 | 45039 | PMMPanel.VirBAparentPowerPhaseB
SS2PMMPanelVirBAparentPowerPhaseC | REAL | IOD_SS2_TCP | 5041 | 45041 | PMMPanel.VirBAparentPowerPhaseC
SS2PMMPanelVirBAverageCurrent_A | REAL | IOD_SS2_TCP | 5043 | 45043 | PMMPanel.VirBAverageCurrent_A
SS2PMMPanelVirBAveragePhaseToNeutral_V | REAL | IOD_SS2_TCP | 5045 | 45045 | PMMPanel.VirBAveragePhaseToNeutral_V
SS2PMMPanelVirBAveragePhaseToPhase_V | REAL | IOD_SS2_TCP | 5047 | 45047 | PMMPanel.VirBAveragePhaseToPhase_V
SS2PMMPanelVirBCurrentInPhaseA_A | REAL | IOD_SS2_TCP | 5049 | 45049 | PMMPanel.VirBCurrentInPhaseA_A
SS2PMMPanelVirBCurrentInPhaseB_A | REAL | IOD_SS2_TCP | 5051 | 45051 | PMMPanel.VirBCurrentInPhaseB_A
SS2PMMPanelVirBCurrentInPhaseC_A | REAL | IOD_SS2_TCP | 5053 | 45053 | PMMPanel.VirBCurrentInPhaseC_A
SS2PMMPanelVirBFrequency_Hz | REAL | IOD_SS2_TCP | 5055 | 45055 | PMMPanel.VirBFrequency_Hz
SS2PMMPanelVirBPowerFactorSys | REAL | IOD_SS2_TCP | 5057 | 45057 | PMMPanel.VirBPowerFactorSys
SS2PMMPanelVirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS2_TCP | 5059 | 45059 | PMMPanel.VirBReactiveEnergyConsumed_kVARh
SS2PMMPanelVirBReactivePowerPhaseA | REAL | IOD_SS2_TCP | 5061 | 45061 | PMMPanel.VirBReactivePowerPhaseA
SS2PMMPanelVirBReactivePowerPhaseB | REAL | IOD_SS2_TCP | 5063 | 45063 | PMMPanel.VirBReactivePowerPhaseB
SS2PMMPanelVirBReactivePowerPhaseC | REAL | IOD_SS2_TCP | 5065 | 45065 | PMMPanel.VirBReactivePowerPhaseC
SS2PMMPanelVirBTotalActivePower_kW | REAL | IOD_SS2_TCP | 5067 | 45067 | PMMPanel.VirBTotalActivePower_kW
SS2PMMPanelVirBTotalAparentPower_kVA | REAL | IOD_SS2_TCP | 5069 | 45069 | PMMPanel.VirBTotalAparentPower_kVA
SS2PMMPanelVirBTotalPowerFactor | REAL | IOD_SS2_TCP | 5071 | 45071 | PMMPanel.VirBTotalPowerFactor
SS2PMMPanelVirBTotalReactivePower_kVAR | REAL | IOD_SS2_TCP | 5073 | 45073 | PMMPanel.VirBTotalReactivePower_kVAR
SS2PMMPanelVirBVoltageBetweenPhaseAB_V | REAL | IOD_SS2_TCP | 5075 | 45075 | PMMPanel.VirBVoltageBetweenPhaseAB_V
SS2PMMPanelVirBVoltageBetweenPhaseAN_V | REAL | IOD_SS2_TCP | 5077 | 45077 | PMMPanel.VirBVoltageBetweenPhaseAN_V
SS2PMMPanelVirBVoltageBetweenPhaseBC_V | REAL | IOD_SS2_TCP | 5079 | 45079 | PMMPanel.VirBVoltageBetweenPhaseBC_V
SS2PMMPanelVirBVoltageBetweenPhaseBN_V | REAL | IOD_SS2_TCP | 5081 | 45081 | PMMPanel.VirBVoltageBetweenPhaseBN_V
SS2PMMPanelVirBVoltageBetweenPhaseCA_V | REAL | IOD_SS2_TCP | 5083 | 45083 | PMMPanel.VirBVoltageBetweenPhaseCA_V
SS2PMMPanelVirBVoltageBetweenPhaseCN_V | REAL | IOD_SS2_TCP | 5085 | 45085 | PMMPanel.VirBVoltageBetweenPhaseCN_V
SS2PMMPanelVoltageBetweenPhaseAB_V | REAL | IOD_SS2_TCP | 5087 | 45087 | PMMPanel.VoltageBetweenPhaseAB_V
SS2PMMPanelVoltageBetweenPhaseAN_V | REAL | IOD_SS2_TCP | 5089 | 45089 | PMMPanel.VoltageBetweenPhaseAN_V
SS2PMMPanelVoltageBetweenPhaseBC_V | REAL | IOD_SS2_TCP | 5091 | 45091 | PMMPanel.VoltageBetweenPhaseBC_V
SS2PMMPanelVoltageBetweenPhaseBN_V | REAL | IOD_SS2_TCP | 5093 | 45093 | PMMPanel.VoltageBetweenPhaseBN_V
SS2PMMPanelVoltageBetweenPhaseCA_V | REAL | IOD_SS2_TCP | 5095 | 45095 | PMMPanel.VoltageBetweenPhaseCA_V
SS2PMMPanelVoltageBetweenPhaseCN_V | REAL | IOD_SS2_TCP | 5097 | 45097 | PMMPanel.VoltageBetweenPhaseCN_V
SS2SKTemp1 | REAL | IOD_SS2_TCP | 5099 | 45099 | SKTemp1
SS2SKTemp2 | REAL | IOD_SS2_TCP | 5101 | 45101 | SKTemp2
SS2SKTemp3 | REAL | IOD_SS2_TCP | 5103 | 45103 | SKTemp3
SS2SKTemp4 | REAL | IOD_SS2_TCP | 5105 | 45105 | SKTemp4
SS2SKVlaga1 | REAL | IOD_SS2_TCP | 5107 | 45107 | SKVlaga1
SS2SKVlaga2 | REAL | IOD_SS2_TCP | 5109 | 45109 | SKVlaga2
SS2SKVlaga3 | REAL | IOD_SS2_TCP | 5111 | 45111 | SKVlaga3
SS2SKVlaga4 | REAL | IOD_SS2_TCP | 5113 | 45113 | SKVlaga4
SS2TempZaAlarm1_2 | REAL | IOD_SS2_TCP | 5115 | 45115 | TempZaAlarm1_2
SS2TempZaAlarm3_4 | REAL | IOD_SS2_TCP | 5117 | 45117 | TempZaAlarm3_4
SS2TempZaAlarm5_6 | REAL | IOD_SS2_TCP | 5119 | 45119 | TempZaAlarm5_6
SS2TempZaAlarmTIA1 | REAL | IOD_SS2_TCP | 5121 | 45121 | TempZaAlarmTIA1
SS2TempZaAlarmTIA2 | REAL | IOD_SS2_TCP | 5123 | 45123 | TempZaAlarmTIA2
SS2TempZaAlarmTIA3 | REAL | IOD_SS2_TCP | 5125 | 45125 | TempZaAlarmTIA3
SS2TempZaAlarmTIA4 | REAL | IOD_SS2_TCP | 5127 | 45127 | TempZaAlarmTIA4
SS2TempZaVklopObehKlim1_2 | REAL | IOD_SS2_TCP | 5129 | 45129 | TempZaVklopObehKlim1_2
SS2TempZaVklopObehKlim3_4 | REAL | IOD_SS2_TCP | 5131 | 45131 | TempZaVklopObehKlim3_4
SS2TempZaVklopObehKlim3_4TIA3 | REAL | IOD_SS2_TCP | 5133 | 45133 | TempZaVklopObehKlim3_4TIA3
SS2TempZaVklopObehKlim5_6 | REAL | IOD_SS2_TCP | 5135 | 45135 | TempZaVklopObehKlim5_6
SS2TempZaVklopObehKlim5_6TIA3 | REAL | IOD_SS2_TCP | 5137 | 45137 | TempZaVklopObehKlim5_6TIA3
SS2SKTemp5 | REAL | IOD_SS2_TCP | 5139 | 45139 | SKTemp5
SS2SKTemp6 | REAL | IOD_SS2_TCP | 5141 | 45141 | SKTemp6
SS2SKVlaga5 | REAL | IOD_SS2_TCP | 5143 | 45143 | SKVlaga5
SS2SKVlaga6 | REAL | IOD_SS2_TCP | 5145 | 45145 | SKVlaga6
SS2TempZaAlarmTIA5 | REAL | IOD_SS2_TCP | 5147 | 45147 | TempZaAlarmTIA5
SS2TempZaAlarmTIA6 | REAL | IOD_SS2_TCP | 5149 | 45149 | TempZaAlarmTIA6
SS2SKTempServSoba1Povpr | REAL | IOD_SS2_TCP | 5151 | 45151 | SKTempServSoba1Povpr
SS2SKTempServSoba2Povpr | REAL | IOD_SS2_TCP | 5153 | 45153 | SKTempServSoba2Povpr
SS2TempZaAlarmTIA235 | REAL | IOD_SS2_TCP | 5155 | 45155 | TempZaAlarmTIA235
SS2TempZaAlarmTIA46 | REAL | IOD_SS2_TCP | 5157 | 45157 | TempZaAlarmTIA46
SS2Date_Time0 | STRING | IOD_SS2_TCP | 6001 | 46001[15] | Date_Time[0]
SS2Date_Time1 | STRING | IOD_SS2_TCP | 6016 | 46016[15] | Date_Time[1]
SS2Date_Time2 | STRING | IOD_SS2_TCP | 6031 | 46031[15] | Date_Time[2]
SS2Date_Time3 | STRING | IOD_SS2_TCP | 6046 | 46046[15] | Date_Time[3]
SS2UserName | STRING | IOD_SS2_TCP | 6061 | 46061[15] | UserName

## variable_new
SS2PrikazKlimat2 | DIGITAL | IOD_SS2_disk | D3
SS2PrikazKlimat3 | DIGITAL | IOD_SS2_disk | D4
SS2PrikazKlimat4 | DIGITAL | IOD_SS2_disk | D5
SS2PrikazKlimat5 | DIGITAL | IOD_SS2_disk | D6
SS2PrikazKlimat6 | DIGITAL | IOD_SS2_disk | D7
SS2PrikazPMM1 | DIGITAL | IOD_SS2_disk | D8
SS2PrikazPMM2 | DIGITAL | IOD_SS2_disk | D9
SS2PrikazUPSKrmOm | DIGITAL | IOD_SS2_disk | D10
SS2PrikazNastTemp1 | DIGITAL | IOD_SS2_disk | D11
SS2PrikazNastTemp2 | DIGITAL | IOD_SS2_disk | D12
SS2PrikazNastTemp3 | DIGITAL | IOD_SS2_disk | D13
SS2PrikazNastTemp4 | DIGITAL | IOD_SS2_disk | D14
SS2Pulz1s | DIGITAL | IOD_SS2_disk | D1
SS2PrikazKlimat1 | DIGITAL | IOD_SS2_disk | D2
SS2OmogociVseAlarme | DIGITAL | IOD_SS2_disk | D3950
SS2OmogociVseSMSAlarme | DIGITAL | IOD_SS2_disk | D3951
SS2PMM1Phase1Current1_med60in80 | DIGITAL | IOD_SS2_disk | D15
SS2PMM1Phase1Current2_med60in80 | DIGITAL | IOD_SS2_disk | D16
SS2PMM1Phase1Current3_med60in80 | DIGITAL | IOD_SS2_disk | D17
SS2PMM1Phase1Current4_med60in80 | DIGITAL | IOD_SS2_disk | D18
SS2PMM1Phase1Current5_med60in80 | DIGITAL | IOD_SS2_disk | D19
SS2PMM1Phase1Current6_med60in80 | DIGITAL | IOD_SS2_disk | D20
SS2PMM1Phase1Current7_med60in80 | DIGITAL | IOD_SS2_disk | D21
SS2PMM1Phase1Current8_med60in80 | DIGITAL | IOD_SS2_disk | D22
SS2PMM1Phase1Current9_med60in80 | DIGITAL | IOD_SS2_disk | D23
SS2PMM1Phase1Current10_med60in80 | DIGITAL | IOD_SS2_disk | D24
SS2PMM1Phase1Current11_med60in80 | DIGITAL | IOD_SS2_disk | D25
SS2PMM1Phase1Current12_med60in80 | DIGITAL | IOD_SS2_disk | D26
SS2PMM1Phase1Current13_med60in80 | DIGITAL | IOD_SS2_disk | D27
SS2PMM1Phase1Current14_med60in80 | DIGITAL | IOD_SS2_disk | D28
SS2PMM1Phase1Current15_med60in80 | DIGITAL | IOD_SS2_disk | D29
SS2PMM1Phase1Current16_med60in80 | DIGITAL | IOD_SS2_disk | D30
SS2PMM1Phase1Current17_med60in80 | DIGITAL | IOD_SS2_disk | D31
SS2PMM1Phase1Current18_med60in80 | DIGITAL | IOD_SS2_disk | D32
SS2PMM1Phase1Current19_med60in80 | DIGITAL | IOD_SS2_disk | D33
SS2PMM1Phase1Current20_med60in80 | DIGITAL | IOD_SS2_disk | D34
SS2PMM1Phase1Current21_med60in80 | DIGITAL | IOD_SS2_disk | D35
SS2PMM1Phase1Current22_med60in80 | DIGITAL | IOD_SS2_disk | D36
SS2PMM1Phase1Current23_med60in80 | DIGITAL | IOD_SS2_disk | D37
SS2PMM1Phase1Current24_med60in80 | DIGITAL | IOD_SS2_disk | D38
SS2PMM1Phase1Current25_med60in80 | DIGITAL | IOD_SS2_disk | D39
SS2PMM1Phase1Current26_med60in80 | DIGITAL | IOD_SS2_disk | D40
SS2PMM1Phase1Current27_med60in80 | DIGITAL | IOD_SS2_disk | D41
SS2PMM1Phase1Current28_med60in80 | DIGITAL | IOD_SS2_disk | D42
SS2PMM1Phase1Current29_med60in80 | DIGITAL | IOD_SS2_disk | D43
SS2PMM1Phase1Current30_med60in80 | DIGITAL | IOD_SS2_disk | D44
SS2PMM1Phase1Current31_med60in80 | DIGITAL | IOD_SS2_disk | D45
SS2PMM1Phase1Current32_med60in80 | DIGITAL | IOD_SS2_disk | D46
SS2PMM1Phase1Current33_med60in80 | DIGITAL | IOD_SS2_disk | D47
SS2PMM1Phase1Current34_med60in80 | DIGITAL | IOD_SS2_disk | D48
SS2PMM1Phase1Current35_med60in80 | DIGITAL | IOD_SS2_disk | D49
SS2PMM1Phase1Current36_med60in80 | DIGITAL | IOD_SS2_disk | D50
SS2PMM1Phase1Current37_med60in80 | DIGITAL | IOD_SS2_disk | D51
SS2PMM1Phase1Current38_med60in80 | DIGITAL | IOD_SS2_disk | D52
SS2PMM1Phase1Current39_med60in80 | DIGITAL | IOD_SS2_disk | D53
SS2PMM1Phase1Current40_med60in80 | DIGITAL | IOD_SS2_disk | D54
SS2PMM1Phase1Current41_med60in80 | DIGITAL | IOD_SS2_disk | D55
SS2PMM1Phase1Current42_med60in80 | DIGITAL | IOD_SS2_disk | D56
SS2PMM1Phase1Current1_nad80 | DIGITAL | IOD_SS2_disk | D57
SS2PMM1Phase1Current2_nad80 | DIGITAL | IOD_SS2_disk | D58
SS2PMM1Phase1Current3_nad80 | DIGITAL | IOD_SS2_disk | D59
SS2PMM1Phase1Current4_nad80 | DIGITAL | IOD_SS2_disk | D60
SS2PMM1Phase1Current5_nad80 | DIGITAL | IOD_SS2_disk | D61
SS2PMM1Phase1Current6_nad80 | DIGITAL | IOD_SS2_disk | D62
SS2PMM1Phase1Current7_nad80 | DIGITAL | IOD_SS2_disk | D63
SS2PMM1Phase1Current8_nad80 | DIGITAL | IOD_SS2_disk | D64
SS2PMM1Phase1Current9_nad80 | DIGITAL | IOD_SS2_disk | D65
SS2PMM1Phase1Current10_nad80 | DIGITAL | IOD_SS2_disk | D66
SS2PMM1Phase1Current11_nad80 | DIGITAL | IOD_SS2_disk | D67
SS2PMM1Phase1Current12_nad80 | DIGITAL | IOD_SS2_disk | D68
SS2PMM1Phase1Current13_nad80 | DIGITAL | IOD_SS2_disk | D69
SS2PMM1Phase1Current14_nad80 | DIGITAL | IOD_SS2_disk | D70
SS2PMM1Phase1Current15_nad80 | DIGITAL | IOD_SS2_disk | D71
SS2PMM1Phase1Current16_nad80 | DIGITAL | IOD_SS2_disk | D72
SS2PMM1Phase1Current17_nad80 | DIGITAL | IOD_SS2_disk | D73
SS2PMM1Phase1Current18_nad80 | DIGITAL | IOD_SS2_disk | D74
SS2PMM1Phase1Current19_nad80 | DIGITAL | IOD_SS2_disk | D75
SS2PMM1Phase1Current20_nad80 | DIGITAL | IOD_SS2_disk | D76
SS2PMM1Phase1Current21_nad80 | DIGITAL | IOD_SS2_disk | D77
SS2PMM1Phase1Current22_nad80 | DIGITAL | IOD_SS2_disk | D78
SS2PMM1Phase1Current23_nad80 | DIGITAL | IOD_SS2_disk | D79
SS2PMM1Phase1Current24_nad80 | DIGITAL | IOD_SS2_disk | D80
SS2PMM1Phase1Current25_nad80 | DIGITAL | IOD_SS2_disk | D81
SS2PMM1Phase1Current26_nad80 | DIGITAL | IOD_SS2_disk | D82
SS2PMM1Phase1Current27_nad80 | DIGITAL | IOD_SS2_disk | D83
SS2PMM1Phase1Current28_nad80 | DIGITAL | IOD_SS2_disk | D84
SS2PMM1Phase1Current29_nad80 | DIGITAL | IOD_SS2_disk | D85
SS2PMM1Phase1Current30_nad80 | DIGITAL | IOD_SS2_disk | D86
SS2PMM1Phase1Current31_nad80 | DIGITAL | IOD_SS2_disk | D87
SS2PMM1Phase1Current32_nad80 | DIGITAL | IOD_SS2_disk | D88
SS2PMM1Phase1Current33_nad80 | DIGITAL | IOD_SS2_disk | D89
SS2PMM1Phase1Current34_nad80 | DIGITAL | IOD_SS2_disk | D90
SS2PMM1Phase1Current35_nad80 | DIGITAL | IOD_SS2_disk | D91
SS2PMM1Phase1Current36_nad80 | DIGITAL | IOD_SS2_disk | D92
SS2PMM1Phase1Current37_nad80 | DIGITAL | IOD_SS2_disk | D93
SS2PMM1Phase1Current38_nad80 | DIGITAL | IOD_SS2_disk | D94
SS2PMM1Phase1Current39_nad80 | DIGITAL | IOD_SS2_disk | D95
SS2PMM1Phase1Current40_nad80 | DIGITAL | IOD_SS2_disk | D96
SS2PMM1Phase1Current41_nad80 | DIGITAL | IOD_SS2_disk | D97
SS2PMM1Phase1Current42_nad80 | DIGITAL | IOD_SS2_disk | D98
SS2PMM1Phase2Current1_nad80 | DIGITAL | IOD_SS2_disk | D99
SS2PMM1Phase2Current2_nad80 | DIGITAL | IOD_SS2_disk | D100
SS2PMM1Phase2Current3_nad80 | DIGITAL | IOD_SS2_disk | D101
SS2PMM1Phase2Current4_nad80 | DIGITAL | IOD_SS2_disk | D102
SS2PMM1Phase2Current5_nad80 | DIGITAL | IOD_SS2_disk | D103
SS2PMM1Phase2Current6_nad80 | DIGITAL | IOD_SS2_disk | D104
SS2PMM1Phase2Current7_nad80 | DIGITAL | IOD_SS2_disk | D105
SS2PMM1Phase2Current8_nad80 | DIGITAL | IOD_SS2_disk | D106
SS2PMM1Phase2Current9_nad80 | DIGITAL | IOD_SS2_disk | D107
SS2PMM1Phase2Current10_nad80 | DIGITAL | IOD_SS2_disk | D108
SS2PMM1Phase2Current11_nad80 | DIGITAL | IOD_SS2_disk | D109
SS2PMM1Phase2Current12_nad80 | DIGITAL | IOD_SS2_disk | D110
SS2PMM1Phase2Current13_nad80 | DIGITAL | IOD_SS2_disk | D111
SS2PMM1Phase2Current14_nad80 | DIGITAL | IOD_SS2_disk | D112
SS2PMM1Phase2Current15_nad80 | DIGITAL | IOD_SS2_disk | D113
SS2PMM1Phase2Current16_nad80 | DIGITAL | IOD_SS2_disk | D114
SS2PMM1Phase2Current17_nad80 | DIGITAL | IOD_SS2_disk | D115
SS2PMM1Phase2Current18_nad80 | DIGITAL | IOD_SS2_disk | D116
SS2PMM1Phase2Current19_nad80 | DIGITAL | IOD_SS2_disk | D117
SS2PMM1Phase2Current20_nad80 | DIGITAL | IOD_SS2_disk | D118
SS2PMM1Phase2Current21_nad80 | DIGITAL | IOD_SS2_disk | D119
SS2PMM1Phase2Current22_nad80 | DIGITAL | IOD_SS2_disk | D120
SS2PMM1Phase2Current23_nad80 | DIGITAL | IOD_SS2_disk | D121
SS2PMM1Phase2Current24_nad80 | DIGITAL | IOD_SS2_disk | D122
SS2PMM1Phase2Current25_nad80 | DIGITAL | IOD_SS2_disk | D123
SS2PMM1Phase2Current26_nad80 | DIGITAL | IOD_SS2_disk | D124
SS2PMM1Phase2Current27_nad80 | DIGITAL | IOD_SS2_disk | D125
SS2PMM1Phase2Current28_nad80 | DIGITAL | IOD_SS2_disk | D126
SS2PMM1Phase2Current29_nad80 | DIGITAL | IOD_SS2_disk | D127
SS2PMM1Phase2Current30_nad80 | DIGITAL | IOD_SS2_disk | D128
SS2PMM1Phase2Current31_nad80 | DIGITAL | IOD_SS2_disk | D129
SS2PMM1Phase2Current32_nad80 | DIGITAL | IOD_SS2_disk | D130
SS2PMM1Phase2Current33_nad80 | DIGITAL | IOD_SS2_disk | D131
SS2PMM1Phase2Current34_nad80 | DIGITAL | IOD_SS2_disk | D132
SS2PMM1Phase2Current35_nad80 | DIGITAL | IOD_SS2_disk | D133
SS2PMM1Phase2Current36_nad80 | DIGITAL | IOD_SS2_disk | D134
SS2PMM1Phase2Current37_nad80 | DIGITAL | IOD_SS2_disk | D135
SS2PMM1Phase2Current38_nad80 | DIGITAL | IOD_SS2_disk | D136
SS2PMM1Phase2Current39_nad80 | DIGITAL | IOD_SS2_disk | D137
SS2PMM1Phase2Current40_nad80 | DIGITAL | IOD_SS2_disk | D138
SS2PMM1Phase2Current41_nad80 | DIGITAL | IOD_SS2_disk | D139
SS2PMM1Phase2Current42_nad80 | DIGITAL | IOD_SS2_disk | D140
SS2PMM1Phase3Current1_nad80 | DIGITAL | IOD_SS2_disk | D141
SS2PMM1Phase3Current2_nad80 | DIGITAL | IOD_SS2_disk | D142
SS2PMM1Phase3Current3_nad80 | DIGITAL | IOD_SS2_disk | D143
SS2PMM1Phase3Current4_nad80 | DIGITAL | IOD_SS2_disk | D144
SS2PMM1Phase3Current5_nad80 | DIGITAL | IOD_SS2_disk | D145
SS2PMM1Phase3Current6_nad80 | DIGITAL | IOD_SS2_disk | D146
SS2PMM1Phase3Current7_nad80 | DIGITAL | IOD_SS2_disk | D147
SS2PMM1Phase3Current8_nad80 | DIGITAL | IOD_SS2_disk | D148
SS2PMM1Phase3Current9_nad80 | DIGITAL | IOD_SS2_disk | D149
SS2PMM1Phase3Current10_nad80 | DIGITAL | IOD_SS2_disk | D150
SS2PMM1Phase3Current11_nad80 | DIGITAL | IOD_SS2_disk | D151
SS2PMM1Phase3Current12_nad80 | DIGITAL | IOD_SS2_disk | D152
SS2PMM1Phase3Current13_nad80 | DIGITAL | IOD_SS2_disk | D153
SS2PMM1Phase3Current14_nad80 | DIGITAL | IOD_SS2_disk | D154
SS2PMM1Phase3Current15_nad80 | DIGITAL | IOD_SS2_disk | D155
SS2PMM1Phase3Current16_nad80 | DIGITAL | IOD_SS2_disk | D156
SS2PMM1Phase3Current17_nad80 | DIGITAL | IOD_SS2_disk | D157
SS2PMM1Phase3Current18_nad80 | DIGITAL | IOD_SS2_disk | D158
SS2PMM1Phase3Current19_nad80 | DIGITAL | IOD_SS2_disk | D159
SS2PMM1Phase3Current20_nad80 | DIGITAL | IOD_SS2_disk | D160
SS2PMM1Phase3Current21_nad80 | DIGITAL | IOD_SS2_disk | D161
SS2PMM1Phase3Current22_nad80 | DIGITAL | IOD_SS2_disk | D162
SS2PMM1Phase3Current23_nad80 | DIGITAL | IOD_SS2_disk | D163
SS2PMM1Phase3Current24_nad80 | DIGITAL | IOD_SS2_disk | D164
SS2PMM1Phase3Current25_nad80 | DIGITAL | IOD_SS2_disk | D165
SS2PMM1Phase3Current26_nad80 | DIGITAL | IOD_SS2_disk | D166
SS2PMM1Phase3Current27_nad80 | DIGITAL | IOD_SS2_disk | D167
SS2PMM1Phase3Current28_nad80 | DIGITAL | IOD_SS2_disk | D168
SS2PMM1Phase3Current29_nad80 | DIGITAL | IOD_SS2_disk | D169
SS2PMM1Phase3Current30_nad80 | DIGITAL | IOD_SS2_disk | D170
SS2PMM1Phase3Current31_nad80 | DIGITAL | IOD_SS2_disk | D171
SS2PMM1Phase3Current32_nad80 | DIGITAL | IOD_SS2_disk | D172
SS2PMM1Phase3Current33_nad80 | DIGITAL | IOD_SS2_disk | D173
SS2PMM1Phase3Current34_nad80 | DIGITAL | IOD_SS2_disk | D174
SS2PMM1Phase3Current35_nad80 | DIGITAL | IOD_SS2_disk | D175
SS2PMM1Phase3Current36_nad80 | DIGITAL | IOD_SS2_disk | D176
SS2PMM1Phase3Current37_nad80 | DIGITAL | IOD_SS2_disk | D177
SS2PMM1Phase3Current38_nad80 | DIGITAL | IOD_SS2_disk | D178
SS2PMM1Phase3Current39_nad80 | DIGITAL | IOD_SS2_disk | D179
SS2PMM1Phase3Current40_nad80 | DIGITAL | IOD_SS2_disk | D180
SS2PMM1Phase3Current41_nad80 | DIGITAL | IOD_SS2_disk | D181
SS2PMM1Phase3Current42_nad80 | DIGITAL | IOD_SS2_disk | D182
SS2PMM1Phase2Current1_med60in80 | DIGITAL | IOD_SS2_disk | D183
SS2PMM1Phase2Current2_med60in80 | DIGITAL | IOD_SS2_disk | D184
SS2PMM1Phase2Current3_med60in80 | DIGITAL | IOD_SS2_disk | D185
SS2PMM1Phase2Current4_med60in80 | DIGITAL | IOD_SS2_disk | D186
SS2PMM1Phase2Current5_med60in80 | DIGITAL | IOD_SS2_disk | D187
SS2PMM1Phase2Current6_med60in80 | DIGITAL | IOD_SS2_disk | D188
SS2PMM1Phase2Current7_med60in80 | DIGITAL | IOD_SS2_disk | D189
SS2PMM1Phase2Current8_med60in80 | DIGITAL | IOD_SS2_disk | D190
SS2PMM1Phase2Current9_med60in80 | DIGITAL | IOD_SS2_disk | D191
SS2PMM1Phase2Current10_med60in80 | DIGITAL | IOD_SS2_disk | D192
SS2PMM1Phase2Current11_med60in80 | DIGITAL | IOD_SS2_disk | D193
SS2PMM1Phase2Current12_med60in80 | DIGITAL | IOD_SS2_disk | D194
SS2PMM1Phase2Current13_med60in80 | DIGITAL | IOD_SS2_disk | D195
SS2PMM1Phase2Current14_med60in80 | DIGITAL | IOD_SS2_disk | D196
SS2PMM1Phase2Current15_med60in80 | DIGITAL | IOD_SS2_disk | D197
SS2PMM1Phase2Current16_med60in80 | DIGITAL | IOD_SS2_disk | D198
SS2PMM1Phase2Current17_med60in80 | DIGITAL | IOD_SS2_disk | D199
SS2PMM1Phase2Current18_med60in80 | DIGITAL | IOD_SS2_disk | D200
SS2PMM1Phase2Current19_med60in80 | DIGITAL | IOD_SS2_disk | D201
SS2PMM1Phase2Current20_med60in80 | DIGITAL | IOD_SS2_disk | D202
SS2PMM1Phase2Current21_med60in80 | DIGITAL | IOD_SS2_disk | D203
SS2PMM1Phase2Current22_med60in80 | DIGITAL | IOD_SS2_disk | D204
SS2PMM1Phase2Current23_med60in80 | DIGITAL | IOD_SS2_disk | D205
SS2PMM1Phase2Current24_med60in80 | DIGITAL | IOD_SS2_disk | D206
SS2PMM1Phase2Current25_med60in80 | DIGITAL | IOD_SS2_disk | D207
SS2PMM1Phase2Current26_med60in80 | DIGITAL | IOD_SS2_disk | D208
SS2PMM1Phase2Current27_med60in80 | DIGITAL | IOD_SS2_disk | D209
SS2PMM1Phase2Current28_med60in80 | DIGITAL | IOD_SS2_disk | D210
SS2PMM1Phase2Current29_med60in80 | DIGITAL | IOD_SS2_disk | D211
SS2PMM1Phase2Current30_med60in80 | DIGITAL | IOD_SS2_disk | D212
SS2PMM1Phase2Current31_med60in80 | DIGITAL | IOD_SS2_disk | D213
SS2PMM1Phase2Current32_med60in80 | DIGITAL | IOD_SS2_disk | D214
SS2PMM1Phase2Current33_med60in80 | DIGITAL | IOD_SS2_disk | D215
SS2PMM1Phase2Current34_med60in80 | DIGITAL | IOD_SS2_disk | D216
SS2PMM1Phase2Current35_med60in80 | DIGITAL | IOD_SS2_disk | D217
SS2PMM1Phase2Current36_med60in80 | DIGITAL | IOD_SS2_disk | D218
SS2PMM1Phase2Current37_med60in80 | DIGITAL | IOD_SS2_disk | D219
SS2PMM1Phase2Current38_med60in80 | DIGITAL | IOD_SS2_disk | D220
SS2PMM1Phase2Current39_med60in80 | DIGITAL | IOD_SS2_disk | D221
SS2PMM1Phase2Current40_med60in80 | DIGITAL | IOD_SS2_disk | D222
SS2PMM1Phase2Current41_med60in80 | DIGITAL | IOD_SS2_disk | D223
SS2PMM1Phase2Current42_med60in80 | DIGITAL | IOD_SS2_disk | D224
SS2PMM1Phase3Current1_med60in80 | DIGITAL | IOD_SS2_disk | D225
SS2PMM1Phase3Current2_med60in80 | DIGITAL | IOD_SS2_disk | D226
SS2PMM1Phase3Current3_med60in80 | DIGITAL | IOD_SS2_disk | D227
SS2PMM1Phase3Current4_med60in80 | DIGITAL | IOD_SS2_disk | D228
SS2PMM1Phase3Current5_med60in80 | DIGITAL | IOD_SS2_disk | D229
SS2PMM1Phase3Current6_med60in80 | DIGITAL | IOD_SS2_disk | D230
SS2PMM1Phase3Current7_med60in80 | DIGITAL | IOD_SS2_disk | D231
SS2PMM1Phase3Current8_med60in80 | DIGITAL | IOD_SS2_disk | D232
SS2PMM1Phase3Current9_med60in80 | DIGITAL | IOD_SS2_disk | D233
SS2PMM1Phase3Current10_med60in80 | DIGITAL | IOD_SS2_disk | D234
SS2PMM1Phase3Current11_med60in80 | DIGITAL | IOD_SS2_disk | D235
SS2PMM1Phase3Current12_med60in80 | DIGITAL | IOD_SS2_disk | D236
SS2PMM1Phase3Current13_med60in80 | DIGITAL | IOD_SS2_disk | D237
SS2PMM1Phase3Current14_med60in80 | DIGITAL | IOD_SS2_disk | D238
SS2PMM1Phase3Current15_med60in80 | DIGITAL | IOD_SS2_disk | D239
SS2PMM1Phase3Current16_med60in80 | DIGITAL | IOD_SS2_disk | D240
SS2PMM1Phase3Current17_med60in80 | DIGITAL | IOD_SS2_disk | D241
SS2PMM1Phase3Current18_med60in80 | DIGITAL | IOD_SS2_disk | D242
SS2PMM1Phase3Current19_med60in80 | DIGITAL | IOD_SS2_disk | D243
SS2PMM1Phase3Current20_med60in80 | DIGITAL | IOD_SS2_disk | D244
SS2PMM1Phase3Current21_med60in80 | DIGITAL | IOD_SS2_disk | D245
SS2PMM1Phase3Current22_med60in80 | DIGITAL | IOD_SS2_disk | D246
SS2PMM1Phase3Current23_med60in80 | DIGITAL | IOD_SS2_disk | D247
SS2PMM1Phase3Current24_med60in80 | DIGITAL | IOD_SS2_disk | D248
SS2PMM1Phase3Current25_med60in80 | DIGITAL | IOD_SS2_disk | D249
SS2PMM1Phase3Current26_med60in80 | DIGITAL | IOD_SS2_disk | D250
SS2PMM1Phase3Current27_med60in80 | DIGITAL | IOD_SS2_disk | D251
SS2PMM1Phase3Current28_med60in80 | DIGITAL | IOD_SS2_disk | D252
SS2PMM1Phase3Current29_med60in80 | DIGITAL | IOD_SS2_disk | D252
SS2PMM1Phase3Current30_med60in80 | DIGITAL | IOD_SS2_disk | D253
SS2PMM1Phase3Current31_med60in80 | DIGITAL | IOD_SS2_disk | D254
SS2PMM1Phase3Current32_med60in80 | DIGITAL | IOD_SS2_disk | D255
SS2PMM1Phase3Current33_med60in80 | DIGITAL | IOD_SS2_disk | D256
SS2PMM1Phase3Current34_med60in80 | DIGITAL | IOD_SS2_disk | D257
SS2PMM1Phase3Current35_med60in80 | DIGITAL | IOD_SS2_disk | D258
SS2PMM1Phase3Current36_med60in80 | DIGITAL | IOD_SS2_disk | D259
SS2PMM1Phase3Current37_med60in80 | DIGITAL | IOD_SS2_disk | D260
SS2PMM1Phase3Current38_med60in80 | DIGITAL | IOD_SS2_disk | D261
SS2PMM1Phase3Current39_med60in80 | DIGITAL | IOD_SS2_disk | D262
SS2PMM1Phase3Current40_med60in80 | DIGITAL | IOD_SS2_disk | D263
SS2PMM1Phase3Current41_med60in80 | DIGITAL | IOD_SS2_disk | D264
SS2PMM1Phase3Current42_med60in80 | DIGITAL | IOD_SS2_disk | D265
SS2PMM2Phase1Current1_med60in80 | DIGITAL | IOD_SS2_disk | D285
SS2PMM2Phase1Current2_med60in80 | DIGITAL | IOD_SS2_disk | D286
SS2PMM2Phase1Current3_med60in80 | DIGITAL | IOD_SS2_disk | D287
SS2PMM2Phase1Current4_med60in80 | DIGITAL | IOD_SS2_disk | D288
SS2PMM2Phase1Current5_med60in80 | DIGITAL | IOD_SS2_disk | D289
SS2PMM2Phase1Current6_med60in80 | DIGITAL | IOD_SS2_disk | D290
SS2PMM2Phase1Current7_med60in80 | DIGITAL | IOD_SS2_disk | D291
SS2PMM2Phase1Current8_med60in80 | DIGITAL | IOD_SS2_disk | D292
SS2PMM2Phase1Current9_med60in80 | DIGITAL | IOD_SS2_disk | D293
SS2PMM2Phase1Current10_med60in80 | DIGITAL | IOD_SS2_disk | D294
SS2PMM2Phase1Current11_med60in80 | DIGITAL | IOD_SS2_disk | D295
SS2PMM2Phase1Current12_med60in80 | DIGITAL | IOD_SS2_disk | D296
SS2PMM2Phase1Current13_med60in80 | DIGITAL | IOD_SS2_disk | D297
SS2PMM2Phase1Current14_med60in80 | DIGITAL | IOD_SS2_disk | D298
SS2PMM2Phase1Current15_med60in80 | DIGITAL | IOD_SS2_disk | D299
SS2PMM2Phase1Current16_med60in80 | DIGITAL | IOD_SS2_disk | D300
SS2PMM2Phase1Current17_med60in80 | DIGITAL | IOD_SS2_disk | D301
SS2PMM2Phase1Current18_med60in80 | DIGITAL | IOD_SS2_disk | D302
SS2PMM2Phase1Current19_med60in80 | DIGITAL | IOD_SS2_disk | D303
SS2PMM2Phase1Current20_med60in80 | DIGITAL | IOD_SS2_disk | D304
SS2PMM2Phase1Current21_med60in80 | DIGITAL | IOD_SS2_disk | D305
SS2PMM2Phase1Current22_med60in80 | DIGITAL | IOD_SS2_disk | D306
SS2PMM2Phase1Current23_med60in80 | DIGITAL | IOD_SS2_disk | D307
SS2PMM2Phase1Current24_med60in80 | DIGITAL | IOD_SS2_disk | D308
SS2PMM2Phase1Current25_med60in80 | DIGITAL | IOD_SS2_disk | D309
SS2PMM2Phase1Current26_med60in80 | DIGITAL | IOD_SS2_disk | D310
SS2PMM2Phase1Current27_med60in80 | DIGITAL | IOD_SS2_disk | D311
SS2PMM2Phase1Current28_med60in80 | DIGITAL | IOD_SS2_disk | D312
SS2PMM2Phase1Current29_med60in80 | DIGITAL | IOD_SS2_disk | D313
SS2PMM2Phase1Current30_med60in80 | DIGITAL | IOD_SS2_disk | D314
SS2PMM2Phase1Current31_med60in80 | DIGITAL | IOD_SS2_disk | D315
SS2PMM2Phase1Current32_med60in80 | DIGITAL | IOD_SS2_disk | D316
SS2PMM2Phase1Current33_med60in80 | DIGITAL | IOD_SS2_disk | D317
SS2PMM2Phase1Current34_med60in80 | DIGITAL | IOD_SS2_disk | D318
SS2PMM2Phase1Current35_med60in80 | DIGITAL | IOD_SS2_disk | D319
SS2PMM2Phase1Current36_med60in80 | DIGITAL | IOD_SS2_disk | D320
SS2PMM2Phase1Current37_med60in80 | DIGITAL | IOD_SS2_disk | D321
SS2PMM2Phase1Current38_med60in80 | DIGITAL | IOD_SS2_disk | D322
SS2PMM2Phase1Current39_med60in80 | DIGITAL | IOD_SS2_disk | D323
SS2PMM2Phase1Current40_med60in80 | DIGITAL | IOD_SS2_disk | D324
SS2PMM2Phase1Current41_med60in80 | DIGITAL | IOD_SS2_disk | D325
SS2PMM2Phase1Current42_med60in80 | DIGITAL | IOD_SS2_disk | D326
SS2PMM2Phase1Current1_nad80 | DIGITAL | IOD_SS2_disk | D327
SS2PMM2Phase1Current2_nad80 | DIGITAL | IOD_SS2_disk | D328
SS2PMM2Phase1Current3_nad80 | DIGITAL | IOD_SS2_disk | D329
SS2PMM2Phase1Current4_nad80 | DIGITAL | IOD_SS2_disk | D330
SS2PMM2Phase1Current5_nad80 | DIGITAL | IOD_SS2_disk | D331
SS2PMM2Phase1Current6_nad80 | DIGITAL | IOD_SS2_disk | D332
SS2PMM2Phase1Current7_nad80 | DIGITAL | IOD_SS2_disk | D333
SS2PMM2Phase1Current8_nad80 | DIGITAL | IOD_SS2_disk | D334
SS2PMM2Phase1Current9_nad80 | DIGITAL | IOD_SS2_disk | D335
SS2PMM2Phase1Current10_nad80 | DIGITAL | IOD_SS2_disk | D336
SS2PMM2Phase1Current11_nad80 | DIGITAL | IOD_SS2_disk | D337
SS2PMM2Phase1Current12_nad80 | DIGITAL | IOD_SS2_disk | D338
SS2PMM2Phase1Current13_nad80 | DIGITAL | IOD_SS2_disk | D339
SS2PMM2Phase1Current14_nad80 | DIGITAL | IOD_SS2_disk | D340
SS2PMM2Phase1Current15_nad80 | DIGITAL | IOD_SS2_disk | D341
SS2PMM2Phase1Current16_nad80 | DIGITAL | IOD_SS2_disk | D342
SS2PMM2Phase1Current17_nad80 | DIGITAL | IOD_SS2_disk | D343
SS2PMM2Phase1Current18_nad80 | DIGITAL | IOD_SS2_disk | D344
SS2PMM2Phase1Current19_nad80 | DIGITAL | IOD_SS2_disk | D345
SS2PMM2Phase1Current20_nad80 | DIGITAL | IOD_SS2_disk | D346
SS2PMM2Phase1Current21_nad80 | DIGITAL | IOD_SS2_disk | D347
SS2PMM2Phase1Current22_nad80 | DIGITAL | IOD_SS2_disk | D348
SS2PMM2Phase1Current23_nad80 | DIGITAL | IOD_SS2_disk | D349
SS2PMM2Phase1Current24_nad80 | DIGITAL | IOD_SS2_disk | D350
SS2PMM2Phase1Current25_nad80 | DIGITAL | IOD_SS2_disk | D351
SS2PMM2Phase1Current26_nad80 | DIGITAL | IOD_SS2_disk | D352
SS2PMM2Phase1Current27_nad80 | DIGITAL | IOD_SS2_disk | D353
SS2PMM2Phase1Current28_nad80 | DIGITAL | IOD_SS2_disk | D354
SS2PMM2Phase1Current29_nad80 | DIGITAL | IOD_SS2_disk | D355
SS2PMM2Phase1Current30_nad80 | DIGITAL | IOD_SS2_disk | D356
SS2PMM2Phase1Current31_nad80 | DIGITAL | IOD_SS2_disk | D357
SS2PMM2Phase1Current32_nad80 | DIGITAL | IOD_SS2_disk | D358
SS2PMM2Phase1Current33_nad80 | DIGITAL | IOD_SS2_disk | D359
SS2PMM2Phase1Current34_nad80 | DIGITAL | IOD_SS2_disk | D360
SS2PMM2Phase1Current35_nad80 | DIGITAL | IOD_SS2_disk | D361
SS2PMM2Phase1Current36_nad80 | DIGITAL | IOD_SS2_disk | D362
SS2PMM2Phase1Current37_nad80 | DIGITAL | IOD_SS2_disk | D363
SS2PMM2Phase1Current38_nad80 | DIGITAL | IOD_SS2_disk | D364
SS2PMM2Phase1Current39_nad80 | DIGITAL | IOD_SS2_disk | D365
SS2PMM2Phase1Current40_nad80 | DIGITAL | IOD_SS2_disk | D366
SS2PMM2Phase1Current41_nad80 | DIGITAL | IOD_SS2_disk | D367
SS2PMM2Phase1Current42_nad80 | DIGITAL | IOD_SS2_disk | D368
SS2PMM2PoljeFazaATok1_16_nad80 | DIGITAL | IOD_SS2_disk | D537
SS2PMM2PoljeFazaATok17_32_nad80 | DIGITAL | IOD_SS2_disk | D538
SS2PMM2PoljeFazaATok33_42_nad80 | DIGITAL | IOD_SS2_disk | D539
SS2PMM2PoljeFazaBTok1_16_nad80 | DIGITAL | IOD_SS2_disk | D540
SS2PMM2PoljeFazaBTok17_32_nad80 | DIGITAL | IOD_SS2_disk | D541
SS2PMM2PoljeFazaBTok33_42_nad80 | DIGITAL | IOD_SS2_disk | D542
SS2PMM2PoljeFazaCTok1_16_nad80 | DIGITAL | IOD_SS2_disk | D543
SS2PMM2PoljeFazaCTok17_32_nad80 | DIGITAL | IOD_SS2_disk | D544
SS2PMM2PoljeFazaCTok33_42_nad80 | DIGITAL | IOD_SS2_disk | D545
SS2PMM2PoljeFazaATok1_16_med60_80 | DIGITAL | IOD_SS2_disk | D546
SS2PMM2PoljeFazaATok17_32_med60_80 | DIGITAL | IOD_SS2_disk | D547
SS2PMM2PoljeFazaATok33_42_med60_80 | DIGITAL | IOD_SS2_disk | D548
SS2PMM2PoljeFazaBTok1_16_med60_80 | DIGITAL | IOD_SS2_disk | D549
SS2PMM2PoljeFazaBTok17_32_med60_80 | DIGITAL | IOD_SS2_disk | D550
SS2PMM2PoljeFazaBTok33_42_med60_80 | DIGITAL | IOD_SS2_disk | D551
SS2PMM2PoljeFazaCTok1_16_med60_80 | DIGITAL | IOD_SS2_disk | D552
SS2PMM2PoljeFazaCTok17_32_med60_80 | DIGITAL | IOD_SS2_disk | D553
SS2PMM2PoljeFazaCTok33_42_med60_80 | DIGITAL | IOD_SS2_disk | D554
SS2PMM_2x63_VirA_zavihek | DIGITAL | IOD_SS2_disk | D555
SS2PMM_2x63_VirB_zavihek | DIGITAL | IOD_SS2_disk | D556
SS2PMM_2x17_VirA_zavihek | DIGITAL | IOD_SS2_disk | D557
SS2PMM_2x17_VirB_zavihek | DIGITAL | IOD_SS2_disk | D558
ASS2_Omogoci_SMS_Alarm | DIGITAL | IOD_SS2_disk | D600[299]
BSS2_Omogoci_SMS_Alarm | DIGITAL | IOD_SS2_disk | D900[299]
CSS2_Omogoci_SMS_Alarm | DIGITAL | IOD_SS2_disk | D1200[299]
DSS2_Omogoci_SMS_Alarm | DIGITAL | IOD_SS2_disk | D1500[299]
ESS2_Omogoci_SMS_Alarm | DIGITAL | IOD_SS2_disk | D1800[299]
FSS2_Omogoci_SMS_Alarm | DIGITAL | IOD_SS2_disk | D2100[299]
SS2AlarmUPSKrmOmara_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D2500
SS2StanjeUPSKrmOmara_BaterijskiNacin_Omogoci | DIGITAL | IOD_SS2_disk | D2501
SS2StanjeUPSKrmOmara_Polnjenje_Omogoci | DIGITAL | IOD_SS2_disk | D2502
SS2NapakaSenzorTemp1_Omogoci | DIGITAL | IOD_SS2_disk | D2503
SS2NapakaSenzorTemp2_Omogoci | DIGITAL | IOD_SS2_disk | D2504
SS2NapakaSenzorTemp3_Omogoci | DIGITAL | IOD_SS2_disk | D2505
SS2NapakaSenzorTemp4_Omogoci | DIGITAL | IOD_SS2_disk | D2506
SS2NapakaSenzorVlaga1_Omogoci | DIGITAL | IOD_SS2_disk | D2507
SS2NapakaSenzorVlaga2_Omogoci | DIGITAL | IOD_SS2_disk | D2508
SS2NapakaSenzorVlaga3_Omogoci | DIGITAL | IOD_SS2_disk | D2509
SS2NapakaSenzorVlaga4_Omogoci | DIGITAL | IOD_SS2_disk | D2510
SS2AlarmLAH1RazlitjeVode_Omogoci | DIGITAL | IOD_SS2_disk | D2511
SS2AlarmLAH2RazlitjeVode_Omogoci | DIGITAL | IOD_SS2_disk | D2512
SS2AlarmLAH3RazlitjeVode_Omogoci | DIGITAL | IOD_SS2_disk | D2513
SS2AlarmKlimat2_1_Napaka_Omogoci | DIGITAL | IOD_SS2_disk | D2514
SS2AlarmKlimat2_2_Napaka_Omogoci | DIGITAL | IOD_SS2_disk | D2515
SS2AlarmKlimat2_3_Napaka_Omogoci | DIGITAL | IOD_SS2_disk | D2516
SS2AlarmKlimat2_4_Napaka_Omogoci | DIGITAL | IOD_SS2_disk | D2517
SS2AlarmKlimat2_5_Napaka_Omogoci | DIGITAL | IOD_SS2_disk | D2518
SS2AlarmKlimat2_6_Napaka_Omogoci | DIGITAL | IOD_SS2_disk | D2519
SS2PMM1OverCurrentBetw1_Omogoci | DIGITAL | IOD_SS2_disk | D2521
SS2PMM1OverCurrentBetw2_Omogoci | DIGITAL | IOD_SS2_disk | D2522
SS2PMM1OverCurrentBetw3_Omogoci | DIGITAL | IOD_SS2_disk | D2523
SS2PMM1OverCurrentOver1_Omogoci | DIGITAL | IOD_SS2_disk | D2524
SS2PMM1OverCurrentOver2_Omogoci | DIGITAL | IOD_SS2_disk | D2525
SS2PMM1OverCurrentOver3_Omogoci | DIGITAL | IOD_SS2_disk | D2526
SS2PMM2OverCurrentBetw1_Omogoci | DIGITAL | IOD_SS2_disk | D2528
SS2PMM2OverCurrentBetw2_Omogoci | DIGITAL | IOD_SS2_disk | D2529
SS2PMM2OverCurrentBetw3_Omogoci | DIGITAL | IOD_SS2_disk | D2530
SS2PMM2OverCurrentOver1_Omogoci | DIGITAL | IOD_SS2_disk | D2531
SS2PMM2OverCurrentOver2_Omogoci | DIGITAL | IOD_SS2_disk | D2532
SS2PMM2OverCurrentOver3_Omogoci | DIGITAL | IOD_SS2_disk | D2533
SS2ErrComPMM1_Omogoci | DIGITAL | IOD_SS2_disk | D2534
SS2ErrComPMM2_Omogoci | DIGITAL | IOD_SS2_disk | D2535
SS2ErrComKlima1_Omogoci | DIGITAL | IOD_SS2_disk | D2536
SS2ErrComKlima2_Omogoci | DIGITAL | IOD_SS2_disk | D2537
SS2ErrComKlima3_Omogoci | DIGITAL | IOD_SS2_disk | D2538
SS2ErrComKlima4_Omogoci | DIGITAL | IOD_SS2_disk | D2539
SS2ErrComKlima5_Omogoci | DIGITAL | IOD_SS2_disk | D2540
SS2ErrComKlima6_Omogoci | DIGITAL | IOD_SS2_disk | D2541
SS2ErrComPanelPLC_Omogoci | DIGITAL | IOD_SS2_disk | D2542
SS2ErrCommScada_Omogoci | DIGITAL | IOD_SS2_disk | D2543
SS2OpozoriloBaterijaPLC_Omogoci | DIGITAL | IOD_SS2_disk | D2544
SS2KlimaError1AlarmKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2545
SS2KlimaError1AlarmKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2546
SS2KlimaError1FenThermalCutout_Omogoci | DIGITAL | IOD_SS2_disk | D2547
SS2KlimaError1IzlivVode_Omogoci | DIGITAL | IOD_SS2_disk | D2548
SS2KlimaError1Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2549
SS2KlimaError1Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2550
SS2KlimaError1NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS2_disk | D2553
SS2KlimaError1NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS2_disk | D2554
SS2KlimaError1NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS2_disk | D2556
SS2KlimaError1NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS2_disk | D2557
SS2KlimaError1NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2560
SS2KlimaError1NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2561
SS2KlimaError1NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2562
SS2KlimaError1NizkaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2563
SS2KlimaError1PozarniAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2564
SS2KlimaError1ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS2_disk | D2567
SS2KlimaError1ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS2_disk | D2568
SS2KlimaError1VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2569
SS2KlimaError1VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2570
SS2KlimaError1VisokaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2571
SS2KlimaError1VisokPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2572
SS2KlimaError1VisokPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2573
SS2KlimaError1NapakaVlazilca_Omogoci | DIGITAL | IOD_SS2_disk | D2574
SS2KlimaError1ZamasenFilter_Omogoci | DIGITAL | IOD_SS2_disk | D2576
SS2KlimaError1ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2577
SS2KlimaError2AlarmKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2578
SS2KlimaError2AlarmKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2579
SS2KlimaError2FenThermalCutout_Omogoci | DIGITAL | IOD_SS2_disk | D2580
SS2KlimaError2IzlivVode_Omogoci | DIGITAL | IOD_SS2_disk | D2581
SS2KlimaError2Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2582
SS2KlimaError2Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2583
SS2KlimaError2NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS2_disk | D2586
SS2KlimaError2NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS2_disk | D2587
SS2KlimaError2NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS2_disk | D2589
SS2KlimaError2NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS2_disk | D2590
SS2KlimaError2NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2593
SS2KlimaError2NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2594
SS2KlimaError2NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2595
SS2KlimaError2NizkaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2596
SS2KlimaError2PozarniAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2597
SS2KlimaError2ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS2_disk | D2600
SS2KlimaError2ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS2_disk | D2601
SS2KlimaError2VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2602
SS2KlimaError2VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2603
SS2KlimaError2VisokaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2604
SS2KlimaError2VisokPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2605
SS2KlimaError2VisokPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2606
SS2KlimaError2NapakaVlazilca_Omogoci | DIGITAL | IOD_SS2_disk | D2607
SS2KlimaError2ZamasenFilter_Omogoci | DIGITAL | IOD_SS2_disk | D2609
SS2KlimaError2ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2610
SS2KlimaError3AlarmKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2611
SS2KlimaError3AlarmKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2612
SS2KlimaError3FenThermalCutout_Omogoci | DIGITAL | IOD_SS2_disk | D2613
SS2KlimaError3IzlivVode_Omogoci | DIGITAL | IOD_SS2_disk | D2614
SS2KlimaError3Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2615
SS2KlimaError3Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2616
SS2KlimaError3NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS2_disk | D2619
SS2KlimaError3NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS2_disk | D2620
SS2KlimaError3NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS2_disk | D2622
SS2KlimaError3NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS2_disk | D2623
SS2KlimaError3NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2626
SS2KlimaError3NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2627
SS2KlimaError3NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2628
SS2KlimaError3NizkaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2629
SS2KlimaError3PozarniAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2630
SS2KlimaError3ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS2_disk | D2633
SS2KlimaError3ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS2_disk | D2634
SS2KlimaError3VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2635
SS2KlimaError3VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2636
SS2KlimaError3VisokaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2637
SS2KlimaError3VisokPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2638
SS2KlimaError3VisokPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2639
SS2KlimaError3NapakaVlazilca_Omogoci | DIGITAL | IOD_SS2_disk | D2640
SS2KlimaError3ZamasenFilter_Omogoci | DIGITAL | IOD_SS2_disk | D2642
SS2KlimaError3ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2643
SS2KlimaError4AlarmKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2644
SS2KlimaError4AlarmKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2645
SS2KlimaError4FenThermalCutout_Omogoci | DIGITAL | IOD_SS2_disk | D2646
SS2KlimaError4IzlivVode_Omogoci | DIGITAL | IOD_SS2_disk | D2647
SS2KlimaError4Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2648
SS2KlimaError4Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2649
SS2KlimaError4NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS2_disk | D2652
SS2KlimaError4NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS2_disk | D2653
SS2KlimaError4NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS2_disk | D2655
SS2KlimaError4NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS2_disk | D2656
SS2KlimaError4NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2659
SS2KlimaError4NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2660
SS2KlimaError4NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2661
SS2KlimaError4NizkaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2662
SS2KlimaError4PozarniAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2663
SS2KlimaError4ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS2_disk | D2666
SS2KlimaError4ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS2_disk | D2667
SS2KlimaError4VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2668
SS2KlimaError4VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2669
SS2KlimaError4VisokaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2670
SS2KlimaError4VisokPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2671
SS2KlimaError4VisokPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2672
SS2KlimaError4NapakaVlazilca_Omogoci | DIGITAL | IOD_SS2_disk | D2673
SS2KlimaError4ZamasenFilter_Omogoci | DIGITAL | IOD_SS2_disk | D2675
SS2KlimaError4ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2676
SS2KlimaError5AlarmKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2677
SS2KlimaError5AlarmKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2678
SS2KlimaError5FenThermalCutout_Omogoci | DIGITAL | IOD_SS2_disk | D2679
SS2KlimaError5IzlivVode_Omogoci | DIGITAL | IOD_SS2_disk | D2680
SS2KlimaError5Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2681
SS2KlimaError5Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2682
SS2KlimaError5NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS2_disk | D2685
SS2KlimaError5NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS2_disk | D2686
SS2KlimaError5NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS2_disk | D2688
SS2KlimaError5NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS2_disk | D2689
SS2KlimaError5NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2692
SS2KlimaError5NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2693
SS2KlimaError5NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2694
SS2KlimaError5NizkaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2695
SS2KlimaError5PozarniAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2696
SS2KlimaError5ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS2_disk | D2699
SS2KlimaError5ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS2_disk | D2700
SS2KlimaError5VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2701
SS2KlimaError5VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2702
SS2KlimaError5VisokaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2703
SS2KlimaError5VisokPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2704
SS2KlimaError5VisokPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2705
SS2KlimaError5NapakaVlazilca_Omogoci | DIGITAL | IOD_SS2_disk | D2706
SS2KlimaError5ZamasenFilter_Omogoci | DIGITAL | IOD_SS2_disk | D2708
SS2KlimaError5ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2709
SS2KlimaError6AlarmKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2710
SS2KlimaError6AlarmKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2711
SS2KlimaError6FenThermalCutout_Omogoci | DIGITAL | IOD_SS2_disk | D2712
SS2KlimaError6IzlivVode_Omogoci | DIGITAL | IOD_SS2_disk | D2713
SS2KlimaError6Kompresor1naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2714
SS2KlimaError6Kompresor2naMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2715
SS2KlimaError6NapakaPriPretokuVode_Omogoci | DIGITAL | IOD_SS2_disk | D2718
SS2KlimaError6NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_SS2_disk | D2719
SS2KlimaError6NapakaSenzorVlaznosti_Omogoci | DIGITAL | IOD_SS2_disk | D2721
SS2KlimaError6NapakaTSTemperaturaProstora_Omogoci | DIGITAL | IOD_SS2_disk | D2722
SS2KlimaError6NizekPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2725
SS2KlimaError6NizekPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2726
SS2KlimaError6NizkaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2727
SS2KlimaError6NizkaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2728
SS2KlimaError6PozarniAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2729
SS2KlimaError6ThermalCutoutHeater1_Omogoci | DIGITAL | IOD_SS2_disk | D2732
SS2KlimaError6ThermalCutoutHeater2_Omogoci | DIGITAL | IOD_SS2_disk | D2733
SS2KlimaError6VentilatorNaMejiStevilaObrUr_Omogoci | DIGITAL | IOD_SS2_disk | D2734
SS2KlimaError6VisokaTempVProstoru_Omogoci | DIGITAL | IOD_SS2_disk | D2735
SS2KlimaError6VisokaVlaznost_Omogoci | DIGITAL | IOD_SS2_disk | D2736
SS2KlimaError6VisokPritiskKompresor1_Omogoci | DIGITAL | IOD_SS2_disk | D2737
SS2KlimaError6VisokPritiskKompresor2_Omogoci | DIGITAL | IOD_SS2_disk | D2738
SS2KlimaError6NapakaVlazilca_Omogoci | DIGITAL | IOD_SS2_disk | D2739
SS2KlimaError6ZamasenFilter_Omogoci | DIGITAL | IOD_SS2_disk | D2741
SS2KlimaError6ZunanjiAlarm_Omogoci | DIGITAL | IOD_SS2_disk | D2742
SS2PMM1Phase1Current1_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2743
SS2PMM1Phase1Current2_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2744
SS2PMM1Phase1Current3_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2745
SS2PMM1Phase1Current4_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2746
SS2PMM1Phase1Current5_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2747
SS2PMM1Phase1Current6_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2748
SS2PMM1Phase1Current7_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2749
SS2PMM1Phase1Current8_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2750
SS2PMM1Phase1Current9_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2751
SS2PMM1Phase1Current10_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2752
SS2PMM1Phase1Current11_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2753
SS2PMM1Phase1Current12_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2754
SS2PMM1Phase1Current13_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2755
SS2PMM1Phase1Current14_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2756
SS2PMM1Phase1Current15_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2757
SS2PMM1Phase1Current16_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2758
SS2PMM1Phase1Current17_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2759
SS2PMM1Phase1Current18_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2760
SS2PMM1Phase1Current19_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2761
SS2PMM1Phase1Current20_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2762
SS2PMM1Phase1Current21_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2763
SS2PMM1Phase1Current22_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2764
SS2PMM1Phase1Current23_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2765
SS2PMM1Phase1Current24_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2766
SS2PMM1Phase1Current25_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2767
SS2PMM1Phase1Current26_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2768
SS2PMM1Phase1Current27_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2769
SS2PMM1Phase1Current28_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2770
SS2PMM1Phase1Current29_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2771
SS2PMM1Phase1Current30_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2772
SS2PMM1Phase1Current31_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2773
SS2PMM1Phase1Current32_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2774
SS2PMM1Phase1Current33_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2775
SS2PMM1Phase1Current34_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2776
SS2PMM1Phase1Current35_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2777
SS2PMM1Phase1Current36_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2778
SS2PMM1Phase1Current37_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2779
SS2PMM1Phase1Current38_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2780
SS2PMM1Phase1Current39_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2781
SS2PMM1Phase1Current40_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2782
SS2PMM1Phase1Current41_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2783
SS2PMM1Phase1Current42_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2784
SS2PMM1Phase2Current1_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2785
SS2PMM1Phase2Current2_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2786
SS2PMM1Phase2Current3_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2787
SS2PMM1Phase2Current4_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2788
SS2PMM1Phase2Current5_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2789
SS2PMM1Phase2Current6_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2790
SS2PMM1Phase2Current7_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2791
SS2PMM1Phase2Current8_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2792
SS2PMM1Phase2Current9_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2793
SS2PMM1Phase2Current10_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2794
SS2PMM1Phase2Current11_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2795
SS2PMM1Phase2Current12_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2796
SS2PMM1Phase2Current13_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2797
SS2PMM1Phase2Current14_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2798
SS2PMM1Phase2Current15_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2799
SS2PMM1Phase2Current16_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2800
SS2PMM1Phase2Current17_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2801
SS2PMM1Phase2Current18_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2802
SS2PMM1Phase2Current19_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2803
SS2PMM1Phase2Current20_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2804
SS2PMM1Phase2Current21_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2805
SS2PMM1Phase2Current22_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2806
SS2PMM1Phase2Current23_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2807
SS2PMM1Phase2Current24_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2808
SS2PMM1Phase2Current25_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2809
SS2PMM1Phase2Current26_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2810
SS2PMM1Phase2Current27_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2811
SS2PMM1Phase2Current28_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2812
SS2PMM1Phase2Current29_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2813
SS2PMM1Phase2Current30_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2814
SS2PMM1Phase2Current31_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2815
SS2PMM1Phase2Current32_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2816
SS2PMM1Phase2Current33_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2817
SS2PMM1Phase2Current34_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2818
SS2PMM1Phase2Current35_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2819
SS2PMM1Phase2Current36_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2820
SS2PMM1Phase2Current37_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2821
SS2PMM1Phase2Current38_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2822
SS2PMM1Phase2Current39_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2823
SS2PMM1Phase2Current40_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2824
SS2PMM1Phase2Current41_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2825
SS2PMM1Phase2Current42_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2826
SS2PMM1Phase3Current1_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2827
SS2PMM1Phase3Current2_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2828
SS2PMM1Phase3Current3_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2829
SS2PMM1Phase3Current4_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2830
SS2PMM1Phase3Current5_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2831
SS2PMM1Phase3Current6_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2832
SS2PMM1Phase3Current7_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2833
SS2PMM1Phase3Current8_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2834
SS2PMM1Phase3Current9_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2835
SS2PMM1Phase3Current10_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2836
SS2PMM1Phase3Current11_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2837
SS2PMM1Phase3Current12_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2838
SS2PMM1Phase3Current13_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2839
SS2PMM1Phase3Current14_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2840
SS2PMM1Phase3Current15_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2841
SS2PMM1Phase3Current16_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2842
SS2PMM1Phase3Current17_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2843
SS2PMM1Phase3Current18_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2844
SS2PMM1Phase3Current19_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2845
SS2PMM1Phase3Current20_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2846
SS2PMM1Phase3Current21_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2847
SS2PMM1Phase3Current22_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2848
SS2PMM1Phase3Current23_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2849
SS2PMM1Phase3Current24_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2850
SS2PMM1Phase3Current25_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2851
SS2PMM1Phase3Current26_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2852
SS2PMM1Phase3Current27_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2853
SS2PMM1Phase3Current28_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2854
SS2PMM1Phase3Current29_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2855
SS2PMM1Phase3Current30_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2856
SS2PMM1Phase3Current31_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2857
SS2PMM1Phase3Current32_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2858
SS2PMM1Phase3Current33_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2859
SS2PMM1Phase3Current34_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2860
SS2PMM1Phase3Current35_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2861
SS2PMM1Phase3Current36_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2862
SS2PMM1Phase3Current37_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2863
SS2PMM1Phase3Current38_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2864
SS2PMM1Phase3Current39_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2865
SS2PMM1Phase3Current40_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2866
SS2PMM1Phase3Current41_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2867
SS2PMM1Phase3Current42_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2868
SS2PMM2Phase1Current1_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2869
SS2PMM2Phase1Current2_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2870
SS2PMM2Phase1Current3_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2871
SS2PMM2Phase1Current4_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2872
SS2PMM2Phase1Current5_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2873
SS2PMM2Phase1Current6_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2874
SS2PMM2Phase1Current7_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2875
SS2PMM2Phase1Current8_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2876
SS2PMM2Phase1Current9_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2877
SS2PMM2Phase1Current10_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2878
SS2PMM2Phase1Current11_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2879
SS2PMM2Phase1Current12_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2880
SS2PMM2Phase1Current13_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2881
SS2PMM2Phase1Current14_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2882
SS2PMM2Phase1Current15_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2883
SS2PMM2Phase1Current16_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2884
SS2PMM2Phase1Current17_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2885
SS2PMM2Phase1Current18_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2886
SS2PMM2Phase1Current19_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2887
SS2PMM2Phase1Current20_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2888
SS2PMM2Phase1Current21_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2889
SS2PMM2Phase1Current22_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2890
SS2PMM2Phase1Current23_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2891
SS2PMM2Phase1Current24_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2892
SS2PMM2Phase1Current25_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2893
SS2PMM2Phase1Current26_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2894
SS2PMM2Phase1Current27_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2895
SS2PMM2Phase1Current28_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2896
SS2PMM2Phase1Current29_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2897
SS2PMM2Phase1Current30_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2898
SS2PMM2Phase1Current31_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2899
SS2PMM2Phase1Current32_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2900
SS2PMM2Phase1Current33_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2901
SS2PMM2Phase1Current34_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2902
SS2PMM2Phase1Current35_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2903
SS2PMM2Phase1Current36_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2904
SS2PMM2Phase1Current37_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2905
SS2PMM2Phase1Current38_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2906
SS2PMM2Phase1Current39_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2907
SS2PMM2Phase1Current40_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2908
SS2PMM2Phase1Current41_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2909
SS2PMM2Phase1Current42_med60in80_Omogoci | DIGITAL | IOD_SS2_disk | D2910
SS2PMM1Phase1Current1_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D2995
SS2PMM1Phase1Current2_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D2996
SS2PMM1Phase1Current3_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D2997
SS2PMM1Phase1Current4_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D2998
SS2PMM1Phase1Current5_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D2999
SS2PMM1Phase1Current6_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3000
SS2PMM1Phase1Current7_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3001
SS2PMM1Phase1Current8_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3002
SS2PMM1Phase1Current9_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3003
SS2PMM1Phase1Current10_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3004
SS2PMM1Phase1Current11_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3005
SS2PMM1Phase1Current12_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3006
SS2PMM1Phase1Current13_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3007
SS2PMM1Phase1Current14_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3008
SS2PMM1Phase1Current15_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3009
SS2PMM1Phase1Current16_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3010
SS2PMM1Phase1Current17_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3011
SS2PMM1Phase1Current18_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3012
SS2PMM1Phase1Current19_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3013
SS2PMM1Phase1Current20_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3014
SS2PMM1Phase1Current21_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3015
SS2PMM1Phase1Current22_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3016
SS2PMM1Phase1Current23_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3017
SS2PMM1Phase1Current24_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3018
SS2PMM1Phase1Current25_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3019
SS2PMM1Phase1Current26_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3020
SS2PMM1Phase1Current27_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3021
SS2PMM1Phase1Current28_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3022
SS2PMM1Phase1Current29_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3023
SS2PMM1Phase1Current30_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3024
SS2PMM1Phase1Current31_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3025
SS2PMM1Phase1Current32_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3026
SS2PMM1Phase1Current33_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3027
SS2PMM1Phase1Current34_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3028
SS2PMM1Phase1Current35_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3029
SS2PMM1Phase1Current36_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3030
SS2PMM1Phase1Current37_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3031
SS2PMM1Phase1Current38_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3032
SS2PMM1Phase1Current39_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3033
SS2PMM1Phase1Current40_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3034
SS2PMM1Phase1Current41_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3035
SS2PMM1Phase1Current42_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3036
SS2PMM1Phase2Current1_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3037
SS2PMM1Phase2Current2_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3038
SS2PMM1Phase2Current3_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3039
SS2PMM1Phase2Current4_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3040
SS2PMM1Phase2Current5_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3041
SS2PMM1Phase2Current6_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3042
SS2PMM1Phase2Current7_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3043
SS2PMM1Phase2Current8_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3044
SS2PMM1Phase2Current9_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3045
SS2PMM1Phase2Current10_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3046
SS2PMM1Phase2Current11_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3047
SS2PMM1Phase2Current12_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3048
SS2PMM1Phase2Current13_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3049
SS2PMM1Phase2Current14_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3050
SS2PMM1Phase2Current15_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3051
SS2PMM1Phase2Current16_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3052
SS2PMM1Phase2Current17_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3053
SS2PMM1Phase2Current18_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3054
SS2PMM1Phase2Current19_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3055
SS2PMM1Phase2Current20_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3056
SS2PMM1Phase2Current21_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3057
SS2PMM1Phase2Current22_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3058
SS2PMM1Phase2Current23_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3059
SS2PMM1Phase2Current24_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3060
SS2PMM1Phase2Current25_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3061
SS2PMM1Phase2Current26_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3062
SS2PMM1Phase2Current27_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3063
SS2PMM1Phase2Current28_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3064
SS2PMM1Phase2Current29_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3065
SS2PMM1Phase2Current30_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3066
SS2PMM1Phase2Current31_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3067
SS2PMM1Phase2Current32_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3068
SS2PMM1Phase2Current33_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3069
SS2PMM1Phase2Current34_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3070
SS2PMM1Phase2Current35_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3071
SS2PMM1Phase2Current36_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3072
SS2PMM1Phase2Current37_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3073
SS2PMM1Phase2Current38_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3074
SS2PMM1Phase2Current39_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3075
SS2PMM1Phase2Current40_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3076
SS2PMM1Phase2Current41_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3077
SS2PMM1Phase2Current42_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3078
SS2PMM1Phase3Current1_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3079
SS2PMM1Phase3Current2_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3080
SS2PMM1Phase3Current3_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3081
SS2PMM1Phase3Current4_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3082
SS2PMM1Phase3Current5_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3083
SS2PMM1Phase3Current6_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3084
SS2PMM1Phase3Current7_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3085
SS2PMM1Phase3Current8_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3086
SS2PMM1Phase3Current9_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3087
SS2PMM1Phase3Current10_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3088
SS2PMM1Phase3Current11_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3089
SS2PMM1Phase3Current12_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3090
SS2PMM1Phase3Current13_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3091
SS2PMM1Phase3Current14_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3092
SS2PMM1Phase3Current15_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3093
SS2PMM1Phase3Current16_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3094
SS2PMM1Phase3Current17_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3095
SS2PMM1Phase3Current18_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3096
SS2PMM1Phase3Current19_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3097
SS2PMM1Phase3Current20_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3098
SS2PMM1Phase3Current21_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3099
SS2PMM1Phase3Current22_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3100
SS2PMM1Phase3Current23_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3101
SS2PMM1Phase3Current24_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3102
SS2PMM1Phase3Current25_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3103
SS2PMM1Phase3Current26_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3104
SS2PMM1Phase3Current27_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3105
SS2PMM1Phase3Current28_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3106
SS2PMM1Phase3Current29_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3107
SS2PMM1Phase3Current30_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3108
SS2PMM1Phase3Current31_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3109
SS2PMM1Phase3Current32_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3110
SS2PMM1Phase3Current33_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3111
SS2PMM1Phase3Current34_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3112
SS2PMM1Phase3Current35_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3113
SS2PMM1Phase3Current36_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3114
SS2PMM1Phase3Current37_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3115
SS2PMM1Phase3Current38_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3116
SS2PMM1Phase3Current39_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3117
SS2PMM1Phase3Current40_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3118
SS2PMM1Phase3Current41_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3119
SS2PMM1Phase3Current42_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3120
SS2PMM2Phase1Current1_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3121
SS2PMM2Phase1Current2_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3122
SS2PMM2Phase1Current3_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3123
SS2PMM2Phase1Current4_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3124
SS2PMM2Phase1Current5_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3125
SS2PMM2Phase1Current6_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3126
SS2PMM2Phase1Current7_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3127
SS2PMM2Phase1Current8_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3128
SS2PMM2Phase1Current9_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3129
SS2PMM2Phase1Current10_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3130
SS2PMM2Phase1Current11_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3131
SS2PMM2Phase1Current12_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3132
SS2PMM2Phase1Current13_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3133
SS2PMM2Phase1Current14_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3134
SS2PMM2Phase1Current15_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3135
SS2PMM2Phase1Current16_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3136
SS2PMM2Phase1Current17_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3137
SS2PMM2Phase1Current18_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3138
SS2PMM2Phase1Current19_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3139
SS2PMM2Phase1Current20_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3140
SS2PMM2Phase1Current21_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3141
SS2PMM2Phase1Current22_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3142
SS2PMM2Phase1Current23_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3143
SS2PMM2Phase1Current24_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3144
SS2PMM2Phase1Current25_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3145
SS2PMM2Phase1Current26_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3146
SS2PMM2Phase1Current27_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3147
SS2PMM2Phase1Current28_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3148
SS2PMM2Phase1Current29_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3149
SS2PMM2Phase1Current30_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3150
SS2PMM2Phase1Current31_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3151
SS2PMM2Phase1Current32_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3152
SS2PMM2Phase1Current33_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3153
SS2PMM2Phase1Current34_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3154
SS2PMM2Phase1Current35_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3155
SS2PMM2Phase1Current36_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3156
SS2PMM2Phase1Current37_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3157
SS2PMM2Phase1Current38_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3158
SS2PMM2Phase1Current39_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3159
SS2PMM2Phase1Current40_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3160
SS2PMM2Phase1Current41_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3161
SS2PMM2Phase1Current42_nad80_Omogoci | DIGITAL | IOD_SS2_disk | D3162
SS2SKTemp1_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R1 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKTemp1_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R2 | 0 | 60 | 0 | 60 | °C | ####.#
SS2SKTemp1_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D3249
SS2SKTemp1_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D3250
SS2SKVlaga1_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R3 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKVlaga1_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R4 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKVlaga1_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D3253
SS2SKVlaga1_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D3254
SS2SKTemp2_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R5 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKTemp2_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R6 | 0 | 60 | 0 | 60 | °C | ####.#
SS2SKTemp2_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D3257
SS2SKTemp2_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D3258
SS2SKVlaga2_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R7 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKVlaga2_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R8 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKVlaga2_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D3261
SS2SKVlaga2_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D3262
SS2SKTemp3_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R9 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKTemp3_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R10 | 0 | 60 | 0 | 60 | °C | ####.#
SS2SKTemp3_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D3265
SS2SKTemp3_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D3266
SS2SKVlaga3_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R11 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKVlaga3_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R12 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKVlaga3_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D3269
SS2SKVlaga3_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D3270
SS2SKTemp4_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R13 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKTemp4_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R14 | 0 | 60 | 0 | 60 | °C | ####.#
SS2SKTemp4_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D3273
SS2SKTemp4_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D3274
SS2SKVlaga4_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R15 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKVlaga4_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R16 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKVlaga4_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D3277
SS2SKVlaga4_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D3278
SS2ComSCADA_stevec2 | INT | IOD_SS2_mem | I1
SS2ComSCADA_stevec1 | INT | IOD_SS2_mem | I2
SS2PMM2x63_VirA_Faza1_Med60in80 | REAL | IOD_SS2_disk | R30[21] | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2x63_VirB_Faza1_Med60in80 | REAL | IOD_SS2_disk | R60[21] | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2x63_VirA_Faza1_Nad80 | REAL | IOD_SS2_disk | R90[21] | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2x63_VirB_Faza1_Mad80 | REAL | IOD_SS2_disk | R120[21] | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2x63_VirA_Faza2_Med60in80 | REAL | IOD_SS2_disk | R150[21] | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2x63_VirB_Faza2_Med60in80 | REAL | IOD_SS2_disk | R180[21] | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2x63_VirA_Faza2_Nad80 | REAL | IOD_SS2_disk | R210[21] | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2x63_VirB_Faza2_Mad80 | REAL | IOD_SS2_disk | R240[21] | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2x63_VirA_Faza3_Med60in80 | REAL | IOD_SS2_disk | R270[21] | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2x63_VirB_Faza3_Med60in80 | REAL | IOD_SS2_disk | R300[21] | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2x63_VirA_Faza3_Nad80 | REAL | IOD_SS2_disk | R330[21] | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2x63_VirB_Faza3_Mad80 | REAL | IOD_SS2_disk | R360[21] | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1PoljeFazaATok1_16_nad80 | DIGITAL | IOD_SS2_disk | D3500[16]
SS2PMM1PoljeFazaATok17_32_nad80 | DIGITAL | IOD_SS2_disk | D3517[16]
SS2PMM1PoljeFazaATok33_42_nad80 | DIGITAL | IOD_SS2_disk | D3534[16]
SS2PMM1PoljeFazaBTok1_16_nad80 | DIGITAL | IOD_SS2_disk | D3551[16]
SS2PMM1PoljeFazaBTok17_32_nad80 | DIGITAL | IOD_SS2_disk | D3568[16]
SS2PMM1PoljeFazaBTok33_42_nad80 | DIGITAL | IOD_SS2_disk | D3585[16]
SS2PMM1PoljeFazaCTok1_16_nad80 | DIGITAL | IOD_SS2_disk | D3602[16]
SS2PMM1PoljeFazaCTok17_32_nad80 | DIGITAL | IOD_SS2_disk | D3619[16]
SS2PMM1PoljeFazaCTok33_42_nad80 | DIGITAL | IOD_SS2_disk | D3636[16]
SS2PMM1PoljeFazaATok1_16_med60_80 | DIGITAL | IOD_SS2_disk | D3653[16]
SS2PMM1PoljeFazaATok17_32_med60_80 | DIGITAL | IOD_SS2_disk | D3670[16]
SS2PMM1PoljeFazaATok33_42_med60_80 | DIGITAL | IOD_SS2_disk | D3687[16]
SS2PMM1PoljeFazaBTok1_16_med60_80 | DIGITAL | IOD_SS2_disk | D3704[16]
SS2PMM1PoljeFazaBTok17_32_med60_80 | DIGITAL | IOD_SS2_disk | D3721[16]
SS2PMM1PoljeFazaBTok33_42_med60_80 | DIGITAL | IOD_SS2_disk | D3738[16]
SS2PMM1PoljeFazaCTok1_16_med60_80 | DIGITAL | IOD_SS2_disk | D3755[16]
SS2PMM1PoljeFazaCTok17_32_med60_80 | DIGITAL | IOD_SS2_disk | D3772[16]
SS2PMM1PoljeFazaCTok33_42_med60_80 | DIGITAL | IOD_SS2_disk | D3789[16]
SS2ErrComPort2_Omogoci | DIGITAL | IOD_SS2_disk | D3810
SS2PMM1OverCurrentBetw1_VirB_Omogoci | DIGITAL | IOD_SS2_disk | D3811
SS2PMM1OverCurrentBetw1_VirA_Omogoci | DIGITAL | IOD_SS2_disk | D3812
SS2PMM1OverCurrentBetw2_VirB_Omogoci | DIGITAL | IOD_SS2_disk | D3813
SS2PMM1OverCurrentBetw2_VirA_Omogoci | DIGITAL | IOD_SS2_disk | D3814
SS2PMM1OverCurrentBetw3_VirB_Omogoci | DIGITAL | IOD_SS2_disk | D3815
SS2PMM1OverCurrentBetw3_VirA_Omogoci | DIGITAL | IOD_SS2_disk | D3816
SS2PMM1OverCurrentBetw1_VirB | DIGITAL | IOD_SS2_disk | D3817
SS2PMM1OverCurrentBetw1_VirA | DIGITAL | IOD_SS2_disk | D3818
SS2PMM1OverCurrentBetw2_VirB | DIGITAL | IOD_SS2_disk | D3819
SS2PMM1OverCurrentBetw2_VirA | DIGITAL | IOD_SS2_disk | D3820
SS2PMM1OverCurrentBetw3_VirB | DIGITAL | IOD_SS2_disk | D3821
SS2PMM1OverCurrentBetw3_VirA | DIGITAL | IOD_SS2_disk | D3822
SS2Test | DIGITAL | IOD_SS2_disk | D3823
SS2Temp1 | INT | IOD_SS2_disk | I34
SS2Temp2 | INT | IOD_SS2_disk | I35
SS2Prikaz | DIGITAL | IOD_SS2_disk | D3824
SS2PMM1OverCurrentBetw1_VirB_1_2 | INT | IOD_SS2_disk | I10
SS2PMM1OverCurrentBetw1_VirA_1_2 | INT | IOD_SS2_disk | I11
SS2PMM1OverCurrentBetw1_VirB_2_2 | INT | IOD_SS2_disk | I12
SS2PMM1OverCurrentBetw1_VirA_2_2 | INT | IOD_SS2_disk | I13
SS2PMM1OverCurrentBetw2_VirB_1_2 | INT | IOD_SS2_disk | I14
SS2PMM1OverCurrentBetw2_VirA_1_2 | INT | IOD_SS2_disk | I15
SS2PMM1OverCurrentBetw2_VirB_2_2 | INT | IOD_SS2_disk | I16
SS2PMM1OverCurrentBetw2_VirA_2_2 | INT | IOD_SS2_disk | I17
SS2PMM1OverCurrentBetw3_VirB_1_2 | INT | IOD_SS2_disk | I18
SS2PMM1OverCurrentBetw3_VirA_1_2 | INT | IOD_SS2_disk | I19
SS2PMM1OverCurrentBetw3_VirB_2_2 | INT | IOD_SS2_disk | I20
SS2PMM1OverCurrentBetw3_VirA_2_2 | INT | IOD_SS2_disk | I21
SS2PMM1OverCurrentOver1_VirB_Omogoci | DIGITAL | IOD_SS2_disk | D3825
SS2PMM1OverCurrentOver1_VirA_Omogoci | DIGITAL | IOD_SS2_disk | D3826
SS2PMM1OverCurrentOver2_VirB_Omogoci | DIGITAL | IOD_SS2_disk | D3827
SS2PMM1OverCurrentOver2_VirA_Omogoci | DIGITAL | IOD_SS2_disk | D3828
SS2PMM1OverCurrentOver3_VirB_Omogoci | DIGITAL | IOD_SS2_disk | D3829
SS2PMM1OverCurrentOver3_VirA_Omogoci | DIGITAL | IOD_SS2_disk | D3830
SS2PMM1OverCurrentOver1_VirB | DIGITAL | IOD_SS2_disk | D3831
SS2PMM1OverCurrentOver1_VirA | DIGITAL | IOD_SS2_disk | D3832
SS2PMM1OverCurrentOver2_VirB | DIGITAL | IOD_SS2_disk | D3833
SS2PMM1OverCurrentOver2_VirA | DIGITAL | IOD_SS2_disk | D3834
SS2PMM1OverCurrentOver3_VirB | DIGITAL | IOD_SS2_disk | D3835
SS2PMM1OverCurrentOver3_VirA | DIGITAL | IOD_SS2_disk | D3836
SS2PMM1OverCurrentOver1_VirB_1_2 | INT | IOD_SS2_disk | I22
SS2PMM1OverCurrentOver1_VirA_1_2 | INT | IOD_SS2_disk | I23
SS2PMM1OverCurrentOver1_VirB_2_2 | INT | IOD_SS2_disk | I24
SS2PMM1OverCurrentOver1_VirA_2_2 | INT | IOD_SS2_disk | I25
SS2PMM1OverCurrentOver2_VirB_1_2 | INT | IOD_SS2_disk | I26
SS2PMM1OverCurrentOver2_VirA_1_2 | INT | IOD_SS2_disk | I27
SS2PMM1OverCurrentOver2_VirB_2_2 | INT | IOD_SS2_disk | I28
SS2PMM1OverCurrentOver2_VirA_2_2 | INT | IOD_SS2_disk | I29
SS2PMM1OverCurrentOver3_VirB_1_2 | INT | IOD_SS2_disk | I30
SS2PMM1OverCurrentOver3_VirA_1_2 | INT | IOD_SS2_disk | I31
SS2PMM1OverCurrentOver3_VirB_2_2 | INT | IOD_SS2_disk | I32
SS2PMM1OverCurrentOver3_VirA_2_2 | INT | IOD_SS2_disk | I33
SS2VsotaF1_1_16B | INT | IOD_SS2_disk | I40
SS2VsotaF1_17_32B | INT | IOD_SS2_disk | I41
SS2VsotaF1_33_42B | INT | IOD_SS2_disk | I42
SS2VsotaF2_1_16B | INT | IOD_SS2_disk | I43
SS2VsotaF2_17_32B | INT | IOD_SS2_disk | I44
SS2VsotaF2_33_42B | INT | IOD_SS2_disk | I45
SS2VsotaF3_1_16B | INT | IOD_SS2_disk | I46
SS2VsotaF3_17_32B | INT | IOD_SS2_disk | I47
SS2VsotaF3_33_42B | INT | IOD_SS2_disk | I48
SS2VsotaF1_1_16A | INT | IOD_SS2_disk | I49
SS2VsotaF1_17_32A | INT | IOD_SS2_disk | I50
SS2VsotaF1_33_42A | INT | IOD_SS2_disk | I51
SS2VsotaF2_1_16A | INT | IOD_SS2_disk | I52
SS2VsotaF2_17_32A | INT | IOD_SS2_disk | I53
SS2VsotaF2_33_42A | INT | IOD_SS2_disk | I54
SS2VsotaF3_1_16A | INT | IOD_SS2_disk | I55
SS2VsotaF3_17_32A | INT | IOD_SS2_disk | I56
SS2VsotaF3_33_42A | INT | IOD_SS2_disk | I57
SS2OpozoriloPMM2x17med60in801_Omogoci | DIGITAL | IOD_SS2_disk | D3850
SS2OpozoriloPMM2x17med60in802_Omogoci | DIGITAL | IOD_SS2_disk | D3851
SS2OpozoriloPMM2x17med60in803_Omogoci | DIGITAL | IOD_SS2_disk | D3852
SS2OpozoriloPMM2x17med60in804_Omogoci | DIGITAL | IOD_SS2_disk | D3853
SS2OpozoriloPMM2x17med60in805_Omogoci | DIGITAL | IOD_SS2_disk | D3854
SS2OpozoriloPMM2x17med60in806_Omogoci | DIGITAL | IOD_SS2_disk | D3855
SS2OpozoriloPMM2x17med60in807_Omogoci | DIGITAL | IOD_SS2_disk | D3856
SS2OpozoriloPMM2x17med60in808_Omogoci | DIGITAL | IOD_SS2_disk | D3857
SS2OpozoriloPMM2x17med60in809_Omogoci | DIGITAL | IOD_SS2_disk | D3858
SS2OpozoriloPMM2x17med60in8010_Omogoci | DIGITAL | IOD_SS2_disk | D3859
SS2OpozoriloPMM2x17med60in8011_Omogoci | DIGITAL | IOD_SS2_disk | D3860
SS2OpozoriloPMM2x17med60in8012_Omogoci | DIGITAL | IOD_SS2_disk | D3861
SS2OpozoriloPMM2x17med60in8013_Omogoci | DIGITAL | IOD_SS2_disk | D3862
SS2OpozoriloPMM2x17med60in8014_Omogoci | DIGITAL | IOD_SS2_disk | D3863
SS2OpozoriloPMM2x17med60in8015_Omogoci | DIGITAL | IOD_SS2_disk | D3864
SS2OpozoriloPMM2x17med60in8016_Omogoci | DIGITAL | IOD_SS2_disk | D3865
SS2OpozoriloPMM2x17med60in8017_Omogoci | DIGITAL | IOD_SS2_disk | D3866
SS2OpozoriloPMM2x17med60in8018_Omogoci | DIGITAL | IOD_SS2_disk | D3867
SS2OpozoriloPMM2x17med60in8019_Omogoci | DIGITAL | IOD_SS2_disk | D3868
SS2OpozoriloPMM2x17med60in8020_Omogoci | DIGITAL | IOD_SS2_disk | D3869
SS2OpozoriloPMM2x17med60in8021_Omogoci | DIGITAL | IOD_SS2_disk | D3870
SS2OpozoriloPMM2x17med60in8022_Omogoci | DIGITAL | IOD_SS2_disk | D3871
SS2OpozoriloPMM2x17med60in8023_Omogoci | DIGITAL | IOD_SS2_disk | D3872
SS2OpozoriloPMM2x17med60in8024_Omogoci | DIGITAL | IOD_SS2_disk | D3873
SS2OpozoriloPMM2x17med60in8025_Omogoci | DIGITAL | IOD_SS2_disk | D3874
SS2OpozoriloPMM2x17med60in8026_Omogoci | DIGITAL | IOD_SS2_disk | D3875
SS2OpozoriloPMM2x17med60in8027_Omogoci | DIGITAL | IOD_SS2_disk | D3876
SS2OpozoriloPMM2x17med60in8028_Omogoci | DIGITAL | IOD_SS2_disk | D3877
SS2OpozoriloPMM2x17med60in8029_Omogoci | DIGITAL | IOD_SS2_disk | D3878
SS2OpozoriloPMM2x17med60in8030_Omogoci | DIGITAL | IOD_SS2_disk | D3879
SS2OpozoriloPMM2x17med60in8031_Omogoci | DIGITAL | IOD_SS2_disk | D3880
SS2OpozoriloPMM2x17med60in8032_Omogoci | DIGITAL | IOD_SS2_disk | D3881
SS2OpozoriloPMM2x17med60in8033_Omogoci | DIGITAL | IOD_SS2_disk | D3882
SS2OpozoriloPMM2x17med60in8034_Omogoci | DIGITAL | IOD_SS2_disk | D3883
SS2OpozoriloPMM2x17med60in8035_Omogoci | DIGITAL | IOD_SS2_disk | D3884
SS2OpozoriloPMM2x17med60in8036_Omogoci | DIGITAL | IOD_SS2_disk | D3885
SS2OpozoriloPMM2x17med60in8037_Omogoci | DIGITAL | IOD_SS2_disk | D3886
SS2OpozoriloPMM2x17med60in8038_Omogoci | DIGITAL | IOD_SS2_disk | D3887
SS2OpozoriloPMM2x17med60in8039_Omogoci | DIGITAL | IOD_SS2_disk | D3888
SS2OpozoriloPMM2x17med60in8040_Omogoci | DIGITAL | IOD_SS2_disk | D3889
SS2OpozoriloPMM2x17med60in8041_Omogoci | DIGITAL | IOD_SS2_disk | D3890
SS2OpozoriloPMM2x17med60in8042_Omogoci | DIGITAL | IOD_SS2_disk | D3891
SS2AlarmPMM2x17nad801_Omogoci | DIGITAL | IOD_SS2_disk | D3892
SS2AlarmPMM2x17nad802_Omogoci | DIGITAL | IOD_SS2_disk | D3893
SS2AlarmPMM2x17nad803_Omogoci | DIGITAL | IOD_SS2_disk | D3894
SS2AlarmPMM2x17nad804_Omogoci | DIGITAL | IOD_SS2_disk | D3895
SS2AlarmPMM2x17nad805_Omogoci | DIGITAL | IOD_SS2_disk | D3896
SS2AlarmPMM2x17nad806_Omogoci | DIGITAL | IOD_SS2_disk | D3897
SS2AlarmPMM2x17nad807_Omogoci | DIGITAL | IOD_SS2_disk | D3898
SS2AlarmPMM2x17nad808_Omogoci | DIGITAL | IOD_SS2_disk | D3899
SS2AlarmPMM2x17nad809_Omogoci | DIGITAL | IOD_SS2_disk | D3900
SS2AlarmPMM2x17nad8010_Omogoci | DIGITAL | IOD_SS2_disk | D3901
SS2AlarmPMM2x17nad8011_Omogoci | DIGITAL | IOD_SS2_disk | D3902
SS2AlarmPMM2x17nad8012_Omogoci | DIGITAL | IOD_SS2_disk | D3903
SS2AlarmPMM2x17nad8013_Omogoci | DIGITAL | IOD_SS2_disk | D3904
SS2AlarmPMM2x17nad8014_Omogoci | DIGITAL | IOD_SS2_disk | D3905
SS2AlarmPMM2x17nad8015_Omogoci | DIGITAL | IOD_SS2_disk | D3906
SS2AlarmPMM2x17nad8016_Omogoci | DIGITAL | IOD_SS2_disk | D3907
SS2AlarmPMM2x17nad8017_Omogoci | DIGITAL | IOD_SS2_disk | D3908
SS2AlarmPMM2x17nad8018_Omogoci | DIGITAL | IOD_SS2_disk | D3909
SS2AlarmPMM2x17nad8019_Omogoci | DIGITAL | IOD_SS2_disk | D3910
SS2AlarmPMM2x17nad8020_Omogoci | DIGITAL | IOD_SS2_disk | D3911
SS2AlarmPMM2x17nad8021_Omogoci | DIGITAL | IOD_SS2_disk | D3912
SS2AlarmPMM2x17nad8022_Omogoci | DIGITAL | IOD_SS2_disk | D3913
SS2AlarmPMM2x17nad8023_Omogoci | DIGITAL | IOD_SS2_disk | D3914
SS2AlarmPMM2x17nad8024_Omogoci | DIGITAL | IOD_SS2_disk | D3915
SS2AlarmPMM2x17nad8025_Omogoci | DIGITAL | IOD_SS2_disk | D3916
SS2AlarmPMM2x17nad8026_Omogoci | DIGITAL | IOD_SS2_disk | D3917
SS2AlarmPMM2x17nad8027_Omogoci | DIGITAL | IOD_SS2_disk | D3918
SS2AlarmPMM2x17nad8028_Omogoci | DIGITAL | IOD_SS2_disk | D3919
SS2AlarmPMM2x17nad8029_Omogoci | DIGITAL | IOD_SS2_disk | D3920
SS2AlarmPMM2x17nad8030_Omogoci | DIGITAL | IOD_SS2_disk | D3921
SS2AlarmPMM2x17nad8031_Omogoci | DIGITAL | IOD_SS2_disk | D3922
SS2AlarmPMM2x17nad8032_Omogoci | DIGITAL | IOD_SS2_disk | D3923
SS2AlarmPMM2x17nad8033_Omogoci | DIGITAL | IOD_SS2_disk | D3924
SS2AlarmPMM2x17nad8034_Omogoci | DIGITAL | IOD_SS2_disk | D3925
SS2AlarmPMM2x17nad8035_Omogoci | DIGITAL | IOD_SS2_disk | D3926
SS2AlarmPMM2x17nad8036_Omogoci | DIGITAL | IOD_SS2_disk | D3927
SS2AlarmPMM2x17nad8037_Omogoci | DIGITAL | IOD_SS2_disk | D3928
SS2AlarmPMM2x17nad8038_Omogoci | DIGITAL | IOD_SS2_disk | D3929
SS2AlarmPMM2x17nad8039_Omogoci | DIGITAL | IOD_SS2_disk | D3930
SS2AlarmPMM2x17nad8040_Omogoci | DIGITAL | IOD_SS2_disk | D3931
SS2AlarmPMM2x17nad8041_Omogoci | DIGITAL | IOD_SS2_disk | D3932
SS2AlarmPMM2x17nad8042_Omogoci | DIGITAL | IOD_SS2_disk | D3933
SS2PMM2OverCurrentOver_VirB | DIGITAL | IOD_SS2_disk | D3940
SS2PMM2OverCurrentOver_VirA | DIGITAL | IOD_SS2_disk | D3941
SS2PMM2OverCurrentBetw_VirB | DIGITAL | IOD_SS2_disk | D3942
SS2PMM2OverCurrentBetw_VirA | DIGITAL | IOD_SS2_disk | D3943
SS2PMM2OverCurrentOver_VirB_Omogoci | DIGITAL | IOD_SS2_disk | D3944
SS2PMM2OverCurrentOver_VirA_Omogoci | DIGITAL | IOD_SS2_disk | D3945
SS2PMM2OverCurrentBetw_VirB_Omogoci | DIGITAL | IOD_SS2_disk | D3946
SS2PMM2OverCurrentBetw_VirA_Omogoci | DIGITAL | IOD_SS2_disk | D3947
SS2NapakaKlimat1_Klimat2 | DIGITAL | IOD_SS2_disk | D3955
SS2NapakaKlimat3_Klimat4 | DIGITAL | IOD_SS2_disk | D3956
SS2NapakaKlimat5_Klimat6 | DIGITAL | IOD_SS2_disk | D3957
SS2AlarmTempTIA1Previsoka_Omogoci | DIGITAL | IOD_SS2_disk | D3958
SS2AlarmTempTIA2Previsoka_Omogoci | DIGITAL | IOD_SS2_disk | D3959
SS2AlarmTempTIA3Previsoka_Omogoci | DIGITAL | IOD_SS2_disk | D3960
SS2AlarmTempTIA4Previsoka_Omogoci | DIGITAL | IOD_SS2_disk | D3961
SS2SMS_Rezerva | DIGITAL | IOD_SS2_disk | D3962
SS2OnemAlarmPon | DIGITAL | IOD_SS2_disk | D3963
SS2UserloggedIn_mem | DIGITAL | IOD_SS2_disk | D3964
SS2AktualniSetPointTemp1_2 | REAL | IOD_SS2_TCP | 44001 | 0 | 60 | 0 | 60 | °C | ####.#
SS2AktualniSetPointTemp3_4 | REAL | IOD_SS2_TCP | 44003 | 0 | 60 | 0 | 60 | °C | ####.#
SS2AktualniSetPointTemp5_6 | REAL | IOD_SS2_TCP | 44005 | 0 | 60 | 0 | 60 | °C | ####.#
SS2AlarmKlimat2_1_Napaka | DIGITAL | IOD_SS2_TCP | 00001
SS2AlarmKlimat2_2_Napaka | DIGITAL | IOD_SS2_TCP | 00002
SS2AlarmKlimat2_3_Napaka | DIGITAL | IOD_SS2_TCP | 00003
SS2AlarmKlimat2_4_Napaka | DIGITAL | IOD_SS2_TCP | 00004
SS2AlarmKlimat2_5_Napaka | DIGITAL | IOD_SS2_TCP | 00005
SS2AlarmKlimat2_6_Napaka | DIGITAL | IOD_SS2_TCP | 00006
SS2AlarmLAH1RazlitjeVode | DIGITAL | IOD_SS2_TCP | 00007
SS2AlarmLAH2RazlitjeVode | DIGITAL | IOD_SS2_TCP | 00008
SS2AlarmLAH3RazlitjeVode | DIGITAL | IOD_SS2_TCP | 00009
SS2AlarmPMM2x17nad8010 | DIGITAL | IOD_SS2_TCP | 00010
SS2AlarmPMM2x17nad8011 | DIGITAL | IOD_SS2_TCP | 00011
SS2AlarmPMM2x17nad8012 | DIGITAL | IOD_SS2_TCP | 00012
SS2AlarmPMM2x17nad8013 | DIGITAL | IOD_SS2_TCP | 00013
SS2AlarmPMM2x17nad8014 | DIGITAL | IOD_SS2_TCP | 00014
SS2AlarmPMM2x17nad8015 | DIGITAL | IOD_SS2_TCP | 00015
SS2AlarmPMM2x17nad8016 | DIGITAL | IOD_SS2_TCP | 00016
SS2AlarmPMM2x17nad8017 | DIGITAL | IOD_SS2_TCP | 00017
SS2AlarmPMM2x17nad8018 | DIGITAL | IOD_SS2_TCP | 00018
SS2AlarmPMM2x17nad8019 | DIGITAL | IOD_SS2_TCP | 00019
SS2AlarmPMM2x17nad801 | DIGITAL | IOD_SS2_TCP | 00020
SS2AlarmPMM2x17nad8020 | DIGITAL | IOD_SS2_TCP | 00021
SS2AlarmPMM2x17nad8021 | DIGITAL | IOD_SS2_TCP | 00022
SS2AlarmPMM2x17nad8022 | DIGITAL | IOD_SS2_TCP | 00023
SS2AlarmPMM2x17nad8023 | DIGITAL | IOD_SS2_TCP | 00024
SS2AlarmPMM2x17nad8024 | DIGITAL | IOD_SS2_TCP | 00025
SS2AlarmPMM2x17nad8025 | DIGITAL | IOD_SS2_TCP | 00026
SS2AlarmPMM2x17nad8026 | DIGITAL | IOD_SS2_TCP | 00027
SS2AlarmPMM2x17nad8027 | DIGITAL | IOD_SS2_TCP | 00028
SS2AlarmPMM2x17nad8028 | DIGITAL | IOD_SS2_TCP | 00029
SS2AlarmPMM2x17nad8029 | DIGITAL | IOD_SS2_TCP | 00030
SS2AlarmPMM2x17nad802 | DIGITAL | IOD_SS2_TCP | 00031
SS2AlarmPMM2x17nad8030 | DIGITAL | IOD_SS2_TCP | 00032
SS2AlarmPMM2x17nad8031 | DIGITAL | IOD_SS2_TCP | 00033
SS2AlarmPMM2x17nad8032 | DIGITAL | IOD_SS2_TCP | 00034
SS2AlarmPMM2x17nad8033 | DIGITAL | IOD_SS2_TCP | 00035
SS2AlarmPMM2x17nad8034 | DIGITAL | IOD_SS2_TCP | 00036
SS2AlarmPMM2x17nad8035 | DIGITAL | IOD_SS2_TCP | 00037
SS2AlarmPMM2x17nad8036 | DIGITAL | IOD_SS2_TCP | 00038
SS2AlarmPMM2x17nad8037 | DIGITAL | IOD_SS2_TCP | 00039
SS2AlarmPMM2x17nad8038 | DIGITAL | IOD_SS2_TCP | 00040
SS2AlarmPMM2x17nad8039 | DIGITAL | IOD_SS2_TCP | 00041
SS2AlarmPMM2x17nad803 | DIGITAL | IOD_SS2_TCP | 00042
SS2AlarmPMM2x17nad8040 | DIGITAL | IOD_SS2_TCP | 00043
SS2AlarmPMM2x17nad8041 | DIGITAL | IOD_SS2_TCP | 00044
SS2AlarmPMM2x17nad8042 | DIGITAL | IOD_SS2_TCP | 00045
SS2AlarmPMM2x17nad804 | DIGITAL | IOD_SS2_TCP | 00046
SS2AlarmPMM2x17nad805 | DIGITAL | IOD_SS2_TCP | 00047
SS2AlarmPMM2x17nad806 | DIGITAL | IOD_SS2_TCP | 00048
SS2AlarmPMM2x17nad807 | DIGITAL | IOD_SS2_TCP | 00049
SS2AlarmPMM2x17nad808 | DIGITAL | IOD_SS2_TCP | 00050
SS2AlarmPMM2x17nad809 | DIGITAL | IOD_SS2_TCP | 00051
SS2AlarmSinhronizacijaNOK | DIGITAL | IOD_SS2_TCP | 00052
SS2AlarmSKTemp1_Previsoka | DIGITAL | IOD_SS2_TCP | 00053
SS2AlarmSKTemp2_Previsoka | DIGITAL | IOD_SS2_TCP | 00054
SS2AlarmSKTemp3_Previsoka | DIGITAL | IOD_SS2_TCP | 00055
SS2AlarmSKTemp4_Previsoka | DIGITAL | IOD_SS2_TCP | 00056
SS2AlarmTempTIA1Previsoka | DIGITAL | IOD_SS2_TCP | 00057
SS2AlarmTempTIA2Previsoka | DIGITAL | IOD_SS2_TCP | 00058
SS2AlarmTempTIA3Previsoka | DIGITAL | IOD_SS2_TCP | 00059
SS2AlarmTempTIA4Previsoka | DIGITAL | IOD_SS2_TCP | 00060
SS2AlarmUPSKrmOmara_Alarm | DIGITAL | IOD_SS2_TCP | 00061
SS2ComSCADA | DIGITAL | IOD_SS2_TCP | 00062
SS2ComSCADA1 | DIGITAL | IOD_SS2_TCP | 00063
SS2Date_Time0 | STRING | IOD_SS2_TCP | 46001[15]
SS2Date_Time1 | STRING | IOD_SS2_TCP | 46016[15]
SS2Date_Time2 | STRING | IOD_SS2_TCP | 46031[15]
SS2Date_Time3 | STRING | IOD_SS2_TCP | 46046[15]
SS2DatumCasDan | INT | IOD_SS2_TCP | 40001
SS2DatumCasLeto | INT | IOD_SS2_TCP | 40002
SS2DatumCasLeto2 | INT | IOD_SS2_TCP | 40003
SS2DatumCasMesec | INT | IOD_SS2_TCP | 40004
SS2DatumCasMinuta | INT | IOD_SS2_TCP | 40005
SS2DatumCasSekunda | INT | IOD_SS2_TCP | 40006
SS2DatumCasUra | INT | IOD_SS2_TCP | 40007
SS2ErrComKlima1 | DIGITAL | IOD_SS2_TCP | 00064
SS2ErrComKlima2 | DIGITAL | IOD_SS2_TCP | 00065
SS2ErrComKlima3 | DIGITAL | IOD_SS2_TCP | 00066
SS2ErrComKlima4 | DIGITAL | IOD_SS2_TCP | 00067
SS2ErrComKlima5 | DIGITAL | IOD_SS2_TCP | 00068
SS2ErrComKlima6 | DIGITAL | IOD_SS2_TCP | 00069
SS2ErrCommScada | DIGITAL | IOD_SS2_TCP | 00070
SS2ErrComPanelPLC | DIGITAL | IOD_SS2_TCP | 00071
SS2ErrComPMM1 | DIGITAL | IOD_SS2_TCP | 00072
SS2ErrComPMM2 | DIGITAL | IOD_SS2_TCP | 00073
SS2ErrComPort2 | DIGITAL | IOD_SS2_TCP | 00074
SS2ErrorComKlima1Error | DIGITAL | IOD_SS2_TCP | 00075
SS2ErrorComKlima1Status | INT | IOD_SS2_TCP | 40008
SS2ErrorComKlima2Error | DIGITAL | IOD_SS2_TCP | 00076
SS2ErrorComKlima2Status | INT | IOD_SS2_TCP | 40009
SS2ErrorComKlima3Error | DIGITAL | IOD_SS2_TCP | 00077
SS2ErrorComKlima3Status | INT | IOD_SS2_TCP | 40010
SS2ErrorComKlima4Error | DIGITAL | IOD_SS2_TCP | 00078
SS2ErrorComKlima4Status | INT | IOD_SS2_TCP | 40011
SS2ErrorComKlima5Error | DIGITAL | IOD_SS2_TCP | 00079
SS2ErrorComKlima5Status | INT | IOD_SS2_TCP | 40012
SS2ErrorComKlima6Error | DIGITAL | IOD_SS2_TCP | 00080
SS2ErrorComKlima6Status | INT | IOD_SS2_TCP | 40013
SS2ErrorComPMM1Error | DIGITAL | IOD_SS2_TCP | 00081
SS2ErrorComPMM1Status | INT | IOD_SS2_TCP | 40014
SS2ErrorComPMM2Error | DIGITAL | IOD_SS2_TCP | 00082
SS2ErrorComPMM2Status | INT | IOD_SS2_TCP | 40015
SS2Klima1ure | REAL | IOD_SS2_TCP | 44007 |  |  |  |  | h | ####
SS2Klima2_1_Onemogocena | DIGITAL | IOD_SS2_TCP | 00083
SS2Klima2_2_Onemogocena | DIGITAL | IOD_SS2_TCP | 00084
SS2Klima2_3_Onemogocena | DIGITAL | IOD_SS2_TCP | 00085
SS2Klima2_4_Onemogocena | DIGITAL | IOD_SS2_TCP | 00086
SS2Klima2_5_Onemogocena | DIGITAL | IOD_SS2_TCP | 00087
SS2Klima2_6_Onemogocena | DIGITAL | IOD_SS2_TCP | 00088
SS2Klima2ure | REAL | IOD_SS2_TCP | 44009 |  |  |  |  | h | ####
SS2Klima3ure | REAL | IOD_SS2_TCP | 44011 |  |  |  |  | h | ####
SS2Klima4ure | REAL | IOD_SS2_TCP | 44013 |  |  |  |  | h | ####
SS2Klima5ure | REAL | IOD_SS2_TCP | 44015 |  |  |  |  | h | ####
SS2Klima6ure | REAL | IOD_SS2_TCP | 44017 |  |  |  |  | h | ####
SS2Klima1GrelecStatus | INT | IOD_SS2_TCP | 40016
SS2Klima1IzhodniVentilator | DIGITAL | IOD_SS2_TCP | 00089
SS2Klima1IzhodniVentStatus | INT | IOD_SS2_TCP | 40017
SS2Klima1Kompresor1 | DIGITAL | IOD_SS2_TCP | 00090
SS2Klima1Kompresor2 | DIGITAL | IOD_SS2_TCP | 00091
SS2Klima1KompresorStatus | INT | IOD_SS2_TCP | 40018
SS2Klima1NacinRazvlaz | INT | IOD_SS2_TCP | 40019
SS2Klima1NastMaxTemp | REAL | IOD_SS2_TCP | 44019 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima1NastMaxVlaznost | REAL | IOD_SS2_TCP | 44021 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima1NastMinTemp | REAL | IOD_SS2_TCP | 44023 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima1NastMinVlaznost | REAL | IOD_SS2_TCP | 44025 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima1NastTempProstora | REAL | IOD_SS2_TCP | 44027 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima1NastVlaznost | REAL | IOD_SS2_TCP | 44029 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima1ObratUreFilter | REAL | IOD_SS2_TCP | 44031 |  |  |  |  | h | ####
SS2Klima1ObratUreKompresor1 | REAL | IOD_SS2_TCP | 44033 |  |  |  |  | h | ####
SS2Klima1ObratUreKompresor2 | REAL | IOD_SS2_TCP | 44035 |  |  |  |  | h | ####
SS2Klima1ObratUreVent | REAL | IOD_SS2_TCP | 44037 |  |  |  |  | h | ####
SS2Klima1Razvlazevanje | DIGITAL | IOD_SS2_TCP | 00092
SS2Klima1SenzorjiStatus | DIGITAL | IOD_SS2_TCP | 00093
SS2Klima1TemperaturaProstora | REAL | IOD_SS2_TCP | 44039 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima1VentilGretjeOdpiranje | DIGITAL | IOD_SS2_TCP | 00094
SS2Klima1VentilGretjeZapiranje | DIGITAL | IOD_SS2_TCP | 00095
SS2Klima1Vlazenje | DIGITAL | IOD_SS2_TCP | 00096
SS2Klima1VlazilecStatus | INT | IOD_SS2_TCP | 40020
SS2Klima1VlaznostProstora | REAL | IOD_SS2_TCP | 44041 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima2GrelecStatus | INT | IOD_SS2_TCP | 40021
SS2Klima2IzhodniVentilator | DIGITAL | IOD_SS2_TCP | 00097
SS2Klima2IzhodniVentStatus | INT | IOD_SS2_TCP | 40022
SS2Klima2Kompresor1 | DIGITAL | IOD_SS2_TCP | 00098
SS2Klima2Kompresor2 | DIGITAL | IOD_SS2_TCP | 00099
SS2Klima2KompresorStatus | INT | IOD_SS2_TCP | 40023
SS2Klima2NacinRazvlaz | INT | IOD_SS2_TCP | 40024
SS2Klima2NastMaxTemp | REAL | IOD_SS2_TCP | 44043 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima2NastMaxVlaznost | REAL | IOD_SS2_TCP | 44045 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima2NastMinTemp | REAL | IOD_SS2_TCP | 44047 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima2NastMinVlaznost | REAL | IOD_SS2_TCP | 44049 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima2NastTempProstora | REAL | IOD_SS2_TCP | 44051 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima2NastVlaznost | REAL | IOD_SS2_TCP | 44053 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima2ObratUreFilter | REAL | IOD_SS2_TCP | 44055 |  |  |  |  | h | ####
SS2Klima2ObratUreKompresor1 | REAL | IOD_SS2_TCP | 44057 |  |  |  |  | h | ####
SS2Klima2ObratUreKompresor2 | REAL | IOD_SS2_TCP | 44059 |  |  |  |  | h | ####
SS2Klima2ObratUreVent | REAL | IOD_SS2_TCP | 44061 |  |  |  |  | h | ####
SS2Klima2Razvlazevanje | DIGITAL | IOD_SS2_TCP | 00100
SS2Klima2SenzorjiStatus | DIGITAL | IOD_SS2_TCP | 00101
SS2Klima2TemperaturaProstora | REAL | IOD_SS2_TCP | 44063 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima2VentilGretjeOdpiranje | DIGITAL | IOD_SS2_TCP | 00102
SS2Klima2VentilGretjeZapiranje | DIGITAL | IOD_SS2_TCP | 00103
SS2Klima2Vlazenje | DIGITAL | IOD_SS2_TCP | 00104
SS2Klima2VlazilecStatus | INT | IOD_SS2_TCP | 40025
SS2Klima2VlaznostProstora | REAL | IOD_SS2_TCP | 44065 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima3GrelecStatus | INT | IOD_SS2_TCP | 40026
SS2Klima3IzhodniVentilator | DIGITAL | IOD_SS2_TCP | 00105
SS2Klima3IzhodniVentStatus | INT | IOD_SS2_TCP | 40027
SS2Klima3Kompresor1 | DIGITAL | IOD_SS2_TCP | 00106
SS2Klima3Kompresor2 | DIGITAL | IOD_SS2_TCP | 00107
SS2Klima3KompresorStatus | INT | IOD_SS2_TCP | 40028
SS2Klima3NacinRazvlaz | INT | IOD_SS2_TCP | 40029
SS2Klima3NastMaxTemp | REAL | IOD_SS2_TCP | 44067 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima3NastMaxVlaznost | REAL | IOD_SS2_TCP | 44069 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima3NastMinTemp | REAL | IOD_SS2_TCP | 44071 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima3NastMinVlaznost | REAL | IOD_SS2_TCP | 44073 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima3NastTempProstora | REAL | IOD_SS2_TCP | 44075 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima3NastVlaznost | REAL | IOD_SS2_TCP | 44077 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima3ObratUreFilter | REAL | IOD_SS2_TCP | 44079 |  |  |  |  | h | ####
SS2Klima3ObratUreKompresor1 | REAL | IOD_SS2_TCP | 44081 |  |  |  |  | h | ####
SS2Klima3ObratUreKompresor2 | REAL | IOD_SS2_TCP | 44083 |  |  |  |  | h | ####
SS2Klima3ObratUreVent | REAL | IOD_SS2_TCP | 44085 |  |  |  |  | h | ####
SS2Klima3Razvlazevanje | DIGITAL | IOD_SS2_TCP | 00108
SS2Klima3SenzorjiStatus | DIGITAL | IOD_SS2_TCP | 00109
SS2Klima3TemperaturaProstora | REAL | IOD_SS2_TCP | 44087 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima3VentilGretjeOdpiranje | DIGITAL | IOD_SS2_TCP | 00110
SS2Klima3VentilGretjeZapiranje | DIGITAL | IOD_SS2_TCP | 00111
SS2Klima3Vlazenje | DIGITAL | IOD_SS2_TCP | 00112
SS2Klima3VlazilecStatus | INT | IOD_SS2_TCP | 40030
SS2Klima3VlaznostProstora | REAL | IOD_SS2_TCP | 44089 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima4GrelecStatus | INT | IOD_SS2_TCP | 40031
SS2Klima4IzhodniVentilator | DIGITAL | IOD_SS2_TCP | 00113
SS2Klima4IzhodniVentStatus | INT | IOD_SS2_TCP | 40032
SS2Klima4Kompresor1 | DIGITAL | IOD_SS2_TCP | 00114
SS2Klima4Kompresor2 | DIGITAL | IOD_SS2_TCP | 00115
SS2Klima4KompresorStatus | INT | IOD_SS2_TCP | 40033
SS2Klima4NacinRazvlaz | INT | IOD_SS2_TCP | 40034
SS2Klima4NastMaxTemp | REAL | IOD_SS2_TCP | 44091 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima4NastMaxVlaznost | REAL | IOD_SS2_TCP | 44093 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima4NastMinTemp | REAL | IOD_SS2_TCP | 44095 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima4NastMinVlaznost | REAL | IOD_SS2_TCP | 44097 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima4NastTempProstora | REAL | IOD_SS2_TCP | 44099 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima4NastVlaznost | REAL | IOD_SS2_TCP | 44101 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima4ObratUreFilter | REAL | IOD_SS2_TCP | 44103 |  |  |  |  | h | ####
SS2Klima4ObratUreKompresor1 | REAL | IOD_SS2_TCP | 44105 |  |  |  |  | h | ####
SS2Klima4ObratUreKompresor2 | REAL | IOD_SS2_TCP | 44107 |  |  |  |  | h | ####
SS2Klima4ObratUreVent | REAL | IOD_SS2_TCP | 44109 |  |  |  |  | h | ####
SS2Klima4Razvlazevanje | DIGITAL | IOD_SS2_TCP | 00116
SS2Klima4SenzorjiStatus | DIGITAL | IOD_SS2_TCP | 00117
SS2Klima4TemperaturaProstora | REAL | IOD_SS2_TCP | 44111 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima4VentilGretjeOdpiranje | DIGITAL | IOD_SS2_TCP | 00118
SS2Klima4VentilGretjeZapiranje | DIGITAL | IOD_SS2_TCP | 00119
SS2Klima4Vlazenje | DIGITAL | IOD_SS2_TCP | 00120
SS2Klima4VlazilecStatus | INT | IOD_SS2_TCP | 40035
SS2Klima4VlaznostProstora | REAL | IOD_SS2_TCP | 44113 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima5GrelecStatus | INT | IOD_SS2_TCP | 40036
SS2Klima5IzhodniVentilator | DIGITAL | IOD_SS2_TCP | 00121
SS2Klima5IzhodniVentStatus | INT | IOD_SS2_TCP | 40037
SS2Klima5Kompresor1 | DIGITAL | IOD_SS2_TCP | 00122
SS2Klima5Kompresor2 | DIGITAL | IOD_SS2_TCP | 00123
SS2Klima5KompresorStatus | INT | IOD_SS2_TCP | 40038
SS2Klima5NacinRazvlaz | INT | IOD_SS2_TCP | 40039
SS2Klima5NastMaxTemp | REAL | IOD_SS2_TCP | 44115 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima5NastMaxVlaznost | REAL | IOD_SS2_TCP | 44117 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima5NastMinTemp | REAL | IOD_SS2_TCP | 44119 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima5NastMinVlaznost | REAL | IOD_SS2_TCP | 44121 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima5NastTempProstora | REAL | IOD_SS2_TCP | 44123 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima5NastVlaznost | REAL | IOD_SS2_TCP | 44125 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima5ObratUreFilter | REAL | IOD_SS2_TCP | 44127 |  |  |  |  | h | ####
SS2Klima5ObratUreKompresor1 | REAL | IOD_SS2_TCP | 44129 |  |  |  |  | h | ####
SS2Klima5ObratUreKompresor2 | REAL | IOD_SS2_TCP | 44131 |  |  |  |  | h | ####
SS2Klima5ObratUreVent | REAL | IOD_SS2_TCP | 44133 |  |  |  |  | h | ####
SS2Klima5Razvlazevanje | DIGITAL | IOD_SS2_TCP | 00124
SS2Klima5SenzorjiStatus | DIGITAL | IOD_SS2_TCP | 00125
SS2Klima5TemperaturaProstora | REAL | IOD_SS2_TCP | 44135 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima5VentilGretjeOdpiranje | DIGITAL | IOD_SS2_TCP | 00126
SS2Klima5VentilGretjeZapiranje | DIGITAL | IOD_SS2_TCP | 00127
SS2Klima5Vlazenje | DIGITAL | IOD_SS2_TCP | 00128
SS2Klima5VlazilecStatus | INT | IOD_SS2_TCP | 40040
SS2Klima5VlaznostProstora | REAL | IOD_SS2_TCP | 44137 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima6GrelecStatus | INT | IOD_SS2_TCP | 40041
SS2Klima6IzhodniVentilator | DIGITAL | IOD_SS2_TCP | 00129
SS2Klima6IzhodniVentStatus | INT | IOD_SS2_TCP | 40042
SS2Klima6Kompresor1 | DIGITAL | IOD_SS2_TCP | 00130
SS2Klima6Kompresor2 | DIGITAL | IOD_SS2_TCP | 00131
SS2Klima6KompresorStatus | INT | IOD_SS2_TCP | 40043
SS2Klima6NacinRazvlaz | INT | IOD_SS2_TCP | 40044
SS2Klima6NastMaxTemp | REAL | IOD_SS2_TCP | 44139 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima6NastMaxVlaznost | REAL | IOD_SS2_TCP | 44141 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima6NastMinTemp | REAL | IOD_SS2_TCP | 44143 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima6NastMinVlaznost | REAL | IOD_SS2_TCP | 44145 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima6NastTempProstora | REAL | IOD_SS2_TCP | 44147 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima6NastVlaznost | REAL | IOD_SS2_TCP | 44149 | 0 | 100 | 0 | 100 | % | ####.#
SS2Klima6ObratUreFilter | REAL | IOD_SS2_TCP | 44151 |  |  |  |  | h | ####
SS2Klima6ObratUreKompresor1 | REAL | IOD_SS2_TCP | 44153 |  |  |  |  | h | ####
SS2Klima6ObratUreKompresor2 | REAL | IOD_SS2_TCP | 44155 |  |  |  |  | h | ####
SS2Klima6ObratUreVent | REAL | IOD_SS2_TCP | 44157 |  |  |  |  | h | ####
SS2Klima6Razvlazevanje | DIGITAL | IOD_SS2_TCP | 00132
SS2Klima6SenzorjiStatus | DIGITAL | IOD_SS2_TCP | 00133
SS2Klima6TemperaturaProstora | REAL | IOD_SS2_TCP | 44159 | 0 | 60 | 0 | 60 | °C | ####.#
SS2Klima6VentilGretjeOdpiranje | DIGITAL | IOD_SS2_TCP | 00134
SS2Klima6VentilGretjeZapiranje | DIGITAL | IOD_SS2_TCP | 00135
SS2Klima6Vlazenje | DIGITAL | IOD_SS2_TCP | 00136
SS2Klima6VlazilecStatus | INT | IOD_SS2_TCP | 40045
SS2Klima6VlaznostProstora | REAL | IOD_SS2_TCP | 44161 | 0 | 100 | 0 | 100 | % | ####.#
SS2KlimaError1AlarmKompresor1 | DIGITAL | IOD_SS2_TCP | 00137
SS2KlimaError1AlarmKompresor2 | DIGITAL | IOD_SS2_TCP | 00138
SS2KlimaError1FenThermalCutout | DIGITAL | IOD_SS2_TCP | 00139
SS2KlimaError1IzlivVode | DIGITAL | IOD_SS2_TCP | 00140
SS2KlimaError1Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00141
SS2KlimaError1Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00142
SS2KlimaError1NapakaPriPretokuVode | DIGITAL | IOD_SS2_TCP | 00143
SS2KlimaError1NapakaPriPretokuZraka | DIGITAL | IOD_SS2_TCP | 00144
SS2KlimaError1NapakaSenzorVlaznosti | DIGITAL | IOD_SS2_TCP | 00145
SS2KlimaError1NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2_TCP | 00146
SS2KlimaError1NapakaVlazilca | DIGITAL | IOD_SS2_TCP | 00147
SS2KlimaError1NizekPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 00148
SS2KlimaError1NizekPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 00149
SS2KlimaError1NizkaTempVProstoru | DIGITAL | IOD_SS2_TCP | 00150
SS2KlimaError1NizkaVlaznost | DIGITAL | IOD_SS2_TCP | 00151
SS2KlimaError1PozarniAlarm | DIGITAL | IOD_SS2_TCP | 00152
SS2KlimaError1ThermalCutoutHeater1 | DIGITAL | IOD_SS2_TCP | 00153
SS2KlimaError1ThermalCutoutHeater2 | DIGITAL | IOD_SS2_TCP | 00154
SS2KlimaError1VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00155
SS2KlimaError1VisokaTempVProstoru | DIGITAL | IOD_SS2_TCP | 00156
SS2KlimaError1VisokaVlaznost | DIGITAL | IOD_SS2_TCP | 00157
SS2KlimaError1VisokPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 00158
SS2KlimaError1VisokPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 00159
SS2KlimaError1ZamasenFilter | DIGITAL | IOD_SS2_TCP | 00160
SS2KlimaError1ZunanjiAlarm | DIGITAL | IOD_SS2_TCP | 00161
SS2KlimaError2AlarmKompresor1 | DIGITAL | IOD_SS2_TCP | 00162
SS2KlimaError2AlarmKompresor2 | DIGITAL | IOD_SS2_TCP | 00163
SS2KlimaError2FenThermalCutout | DIGITAL | IOD_SS2_TCP | 00164
SS2KlimaError2IzlivVode | DIGITAL | IOD_SS2_TCP | 00165
SS2KlimaError2Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00166
SS2KlimaError2Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00167
SS2KlimaError2NapakaPriPretokuVode | DIGITAL | IOD_SS2_TCP | 00168
SS2KlimaError2NapakaPriPretokuZraka | DIGITAL | IOD_SS2_TCP | 00169
SS2KlimaError2NapakaSenzorVlaznosti | DIGITAL | IOD_SS2_TCP | 00170
SS2KlimaError2NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2_TCP | 00171
SS2KlimaError2NapakaVlazilca | DIGITAL | IOD_SS2_TCP | 00172
SS2KlimaError2NizekPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 00173
SS2KlimaError2NizekPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 00174
SS2KlimaError2NizkaTempVProstoru | DIGITAL | IOD_SS2_TCP | 00175
SS2KlimaError2NizkaVlaznost | DIGITAL | IOD_SS2_TCP | 00176
SS2KlimaError2PozarniAlarm | DIGITAL | IOD_SS2_TCP | 00177
SS2KlimaError2ThermalCutoutHeater1 | DIGITAL | IOD_SS2_TCP | 00178
SS2KlimaError2ThermalCutoutHeater2 | DIGITAL | IOD_SS2_TCP | 00179
SS2KlimaError2VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00180
SS2KlimaError2VisokaTempVProstoru | DIGITAL | IOD_SS2_TCP | 00181
SS2KlimaError2VisokaVlaznost | DIGITAL | IOD_SS2_TCP | 00182
SS2KlimaError2VisokPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 00183
SS2KlimaError2VisokPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 00184
SS2KlimaError2ZamasenFilter | DIGITAL | IOD_SS2_TCP | 00185
SS2KlimaError2ZunanjiAlarm | DIGITAL | IOD_SS2_TCP | 00186
SS2KlimaError3AlarmKompresor1 | DIGITAL | IOD_SS2_TCP | 00187
SS2KlimaError3AlarmKompresor2 | DIGITAL | IOD_SS2_TCP | 00188
SS2KlimaError3FenThermalCutout | DIGITAL | IOD_SS2_TCP | 00189
SS2KlimaError3IzlivVode | DIGITAL | IOD_SS2_TCP | 00190
SS2KlimaError3Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00191
SS2KlimaError3Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00192
SS2KlimaError3NapakaPriPretokuVode | DIGITAL | IOD_SS2_TCP | 00193
SS2KlimaError3NapakaPriPretokuZraka | DIGITAL | IOD_SS2_TCP | 00194
SS2KlimaError3NapakaSenzorVlaznosti | DIGITAL | IOD_SS2_TCP | 00195
SS2KlimaError3NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2_TCP | 00196
SS2KlimaError3NapakaVlazilca | DIGITAL | IOD_SS2_TCP | 00197
SS2KlimaError3NizekPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 00198
SS2KlimaError3NizekPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 00199
SS2KlimaError3NizkaTempVProstoru | DIGITAL | IOD_SS2_TCP | 00200
SS2KlimaError3NizkaVlaznost | DIGITAL | IOD_SS2_TCP | 00201
SS2KlimaError3PozarniAlarm | DIGITAL | IOD_SS2_TCP | 00202
SS2KlimaError3ThermalCutoutHeater1 | DIGITAL | IOD_SS2_TCP | 00203
SS2KlimaError3ThermalCutoutHeater2 | DIGITAL | IOD_SS2_TCP | 00204
SS2KlimaError3VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00205
SS2KlimaError3VisokaTempVProstoru | DIGITAL | IOD_SS2_TCP | 00206
SS2KlimaError3VisokaVlaznost | DIGITAL | IOD_SS2_TCP | 00207
SS2KlimaError3VisokPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 00208
SS2KlimaError3VisokPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 00209
SS2KlimaError3ZamasenFilter | DIGITAL | IOD_SS2_TCP | 00210
SS2KlimaError3ZunanjiAlarm | DIGITAL | IOD_SS2_TCP | 00211
SS2KlimaError4AlarmKompresor1 | DIGITAL | IOD_SS2_TCP | 00212
SS2KlimaError4AlarmKompresor2 | DIGITAL | IOD_SS2_TCP | 00213
SS2KlimaError4FenThermalCutout | DIGITAL | IOD_SS2_TCP | 00214
SS2KlimaError4IzlivVode | DIGITAL | IOD_SS2_TCP | 00215
SS2KlimaError4Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00216
SS2KlimaError4Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00217
SS2KlimaError4NapakaPriPretokuVode | DIGITAL | IOD_SS2_TCP | 00218
SS2KlimaError4NapakaPriPretokuZraka | DIGITAL | IOD_SS2_TCP | 00219
SS2KlimaError4NapakaSenzorVlaznosti | DIGITAL | IOD_SS2_TCP | 00220
SS2KlimaError4NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2_TCP | 00221
SS2KlimaError4NapakaVlazilca | DIGITAL | IOD_SS2_TCP | 00222
SS2KlimaError4NizekPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 00223
SS2KlimaError4NizekPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 00224
SS2KlimaError4NizkaTempVProstoru | DIGITAL | IOD_SS2_TCP | 00225
SS2KlimaError4NizkaVlaznost | DIGITAL | IOD_SS2_TCP | 00226
SS2KlimaError4PozarniAlarm | DIGITAL | IOD_SS2_TCP | 00227
SS2KlimaError4ThermalCutoutHeater1 | DIGITAL | IOD_SS2_TCP | 00228
SS2KlimaError4ThermalCutoutHeater2 | DIGITAL | IOD_SS2_TCP | 00229
SS2KlimaError4VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00230
SS2KlimaError4VisokaTempVProstoru | DIGITAL | IOD_SS2_TCP | 00231
SS2KlimaError4VisokaVlaznost | DIGITAL | IOD_SS2_TCP | 00232
SS2KlimaError4VisokPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 00233
SS2KlimaError4VisokPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 00234
SS2KlimaError4ZamasenFilter | DIGITAL | IOD_SS2_TCP | 00235
SS2KlimaError4ZunanjiAlarm | DIGITAL | IOD_SS2_TCP | 00236
SS2KlimaError5AlarmKompresor1 | DIGITAL | IOD_SS2_TCP | 00237
SS2KlimaError5AlarmKompresor2 | DIGITAL | IOD_SS2_TCP | 00238
SS2KlimaError5FenThermalCutout | DIGITAL | IOD_SS2_TCP | 00239
SS2KlimaError5IzlivVode | DIGITAL | IOD_SS2_TCP | 00240
SS2KlimaError5Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00241
SS2KlimaError5Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00242
SS2KlimaError5NapakaPriPretokuVode | DIGITAL | IOD_SS2_TCP | 00243
SS2KlimaError5NapakaPriPretokuZraka | DIGITAL | IOD_SS2_TCP | 00244
SS2KlimaError5NapakaSenzorVlaznosti | DIGITAL | IOD_SS2_TCP | 00245
SS2KlimaError5NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2_TCP | 00246
SS2KlimaError5NapakaVlazilca | DIGITAL | IOD_SS2_TCP | 00247
SS2KlimaError5NizekPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 00248
SS2KlimaError5NizekPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 00249
SS2KlimaError5NizkaTempVProstoru | DIGITAL | IOD_SS2_TCP | 00250
SS2KlimaError5NizkaVlaznost | DIGITAL | IOD_SS2_TCP | 00251
SS2KlimaError5PozarniAlarm | DIGITAL | IOD_SS2_TCP | 00252
SS2KlimaError5ThermalCutoutHeater1 | DIGITAL | IOD_SS2_TCP | 00253
SS2KlimaError5ThermalCutoutHeater2 | DIGITAL | IOD_SS2_TCP | 00254
SS2KlimaError5VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00255
SS2KlimaError5VisokaTempVProstoru | DIGITAL | IOD_SS2_TCP | 00256
SS2KlimaError5VisokaVlaznost | DIGITAL | IOD_SS2_TCP | 00257
SS2KlimaError5VisokPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 00258
SS2KlimaError5VisokPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 00259
SS2KlimaError5ZamasenFilter | DIGITAL | IOD_SS2_TCP | 00260
SS2KlimaError5ZunanjiAlarm | DIGITAL | IOD_SS2_TCP | 00261
SS2KlimaError6AlarmKompresor1 | DIGITAL | IOD_SS2_TCP | 00262
SS2KlimaError6AlarmKompresor2 | DIGITAL | IOD_SS2_TCP | 00263
SS2KlimaError6FenThermalCutout | DIGITAL | IOD_SS2_TCP | 00264
SS2KlimaError6IzlivVode | DIGITAL | IOD_SS2_TCP | 00265
SS2KlimaError6Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00266
SS2KlimaError6Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00267
SS2KlimaError6NapakaPriPretokuVode | DIGITAL | IOD_SS2_TCP | 00268
SS2KlimaError6NapakaPriPretokuZraka | DIGITAL | IOD_SS2_TCP | 00269
SS2KlimaError6NapakaSenzorVlaznosti | DIGITAL | IOD_SS2_TCP | 00270
SS2KlimaError6NapakaTSTemperaturaProstora | DIGITAL | IOD_SS2_TCP | 00271
SS2KlimaError6NapakaVlazilca | DIGITAL | IOD_SS2_TCP | 00272
SS2KlimaError6NizekPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 00273
SS2KlimaError6NizekPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 00274
SS2KlimaError6NizkaTempVProstoru | DIGITAL | IOD_SS2_TCP | 00275
SS2KlimaError6NizkaVlaznost | DIGITAL | IOD_SS2_TCP | 00276
SS2KlimaError6PozarniAlarm | DIGITAL | IOD_SS2_TCP | 00277
SS2KlimaError6ThermalCutoutHeater1 | DIGITAL | IOD_SS2_TCP | 00278
SS2KlimaError6ThermalCutoutHeater2 | DIGITAL | IOD_SS2_TCP | 00279
SS2KlimaError6VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS2_TCP | 00280
SS2KlimaError6VisokaTempVProstoru | DIGITAL | IOD_SS2_TCP | 00281
SS2KlimaError6VisokaVlaznost | DIGITAL | IOD_SS2_TCP | 00282
SS2KlimaError6VisokPritiskKompresor1 | DIGITAL | IOD_SS2_TCP | 00283
SS2KlimaError6VisokPritiskKompresor2 | DIGITAL | IOD_SS2_TCP | 00284
SS2KlimaError6ZamasenFilter | DIGITAL | IOD_SS2_TCP | 00285
SS2KlimaError6ZunanjiAlarm | DIGITAL | IOD_SS2_TCP | 00286
SS2NacDeloKlima1_2Avtom | DIGITAL | IOD_SS2_TCP | 00287
SS2NacDeloKlima3_4Avtom | DIGITAL | IOD_SS2_TCP | 00288
SS2NacDeloKlima5_6Avtom | DIGITAL | IOD_SS2_TCP | 00289
SS2NapakaSenzorTemp1 | DIGITAL | IOD_SS2_TCP | 00290
SS2NapakaSenzorTemp2 | DIGITAL | IOD_SS2_TCP | 00291
SS2NapakaSenzorTemp3 | DIGITAL | IOD_SS2_TCP | 00292
SS2NapakaSenzorTemp4 | DIGITAL | IOD_SS2_TCP | 00293
SS2NapakaSenzorVlaga1 | DIGITAL | IOD_SS2_TCP | 00294
SS2NapakaSenzorVlaga2 | DIGITAL | IOD_SS2_TCP | 00295
SS2NapakaSenzorVlaga3 | DIGITAL | IOD_SS2_TCP | 00296
SS2NapakaSenzorVlaga4 | DIGITAL | IOD_SS2_TCP | 00297
SS2NastaviCasNaKrmilniku | DIGITAL | IOD_SS2_TCP | 00298
SS2NastavitevUreKrUspesna | DIGITAL | IOD_SS2_TCP | 00299
SS2OpozoriloBaterijaPLC | DIGITAL | IOD_SS2_TCP | 00300
SS2OpozoriloPMM2x17med60in8010 | DIGITAL | IOD_SS2_TCP | 00301
SS2OpozoriloPMM2x17med60in8011 | DIGITAL | IOD_SS2_TCP | 00302
SS2OpozoriloPMM2x17med60in8012 | DIGITAL | IOD_SS2_TCP | 00303
SS2OpozoriloPMM2x17med60in8013 | DIGITAL | IOD_SS2_TCP | 00304
SS2OpozoriloPMM2x17med60in8014 | DIGITAL | IOD_SS2_TCP | 00305
SS2OpozoriloPMM2x17med60in8015 | DIGITAL | IOD_SS2_TCP | 00306
SS2OpozoriloPMM2x17med60in8016 | DIGITAL | IOD_SS2_TCP | 00307
SS2OpozoriloPMM2x17med60in8017 | DIGITAL | IOD_SS2_TCP | 00308
SS2OpozoriloPMM2x17med60in8018 | DIGITAL | IOD_SS2_TCP | 00309
SS2OpozoriloPMM2x17med60in8019 | DIGITAL | IOD_SS2_TCP | 00310
SS2OpozoriloPMM2x17med60in801 | DIGITAL | IOD_SS2_TCP | 00311
SS2OpozoriloPMM2x17med60in8020 | DIGITAL | IOD_SS2_TCP | 00312
SS2OpozoriloPMM2x17med60in8021 | DIGITAL | IOD_SS2_TCP | 00313
SS2OpozoriloPMM2x17med60in8022 | DIGITAL | IOD_SS2_TCP | 00314
SS2OpozoriloPMM2x17med60in8023 | DIGITAL | IOD_SS2_TCP | 00315
SS2OpozoriloPMM2x17med60in8024 | DIGITAL | IOD_SS2_TCP | 00316
SS2OpozoriloPMM2x17med60in8025 | DIGITAL | IOD_SS2_TCP | 00317
SS2OpozoriloPMM2x17med60in8026 | DIGITAL | IOD_SS2_TCP | 00318
SS2OpozoriloPMM2x17med60in8027 | DIGITAL | IOD_SS2_TCP | 00319
SS2OpozoriloPMM2x17med60in8028 | DIGITAL | IOD_SS2_TCP | 00320
SS2OpozoriloPMM2x17med60in8029 | DIGITAL | IOD_SS2_TCP | 00321
SS2OpozoriloPMM2x17med60in802 | DIGITAL | IOD_SS2_TCP | 00322
SS2OpozoriloPMM2x17med60in8030 | DIGITAL | IOD_SS2_TCP | 00323
SS2OpozoriloPMM2x17med60in8031 | DIGITAL | IOD_SS2_TCP | 00324
SS2OpozoriloPMM2x17med60in8032 | DIGITAL | IOD_SS2_TCP | 00325
SS2OpozoriloPMM2x17med60in8033 | DIGITAL | IOD_SS2_TCP | 00326
SS2OpozoriloPMM2x17med60in8034 | DIGITAL | IOD_SS2_TCP | 00327
SS2OpozoriloPMM2x17med60in8035 | DIGITAL | IOD_SS2_TCP | 00328
SS2OpozoriloPMM2x17med60in8036 | DIGITAL | IOD_SS2_TCP | 00329
SS2OpozoriloPMM2x17med60in8037 | DIGITAL | IOD_SS2_TCP | 00330
SS2OpozoriloPMM2x17med60in8038 | DIGITAL | IOD_SS2_TCP | 00331
SS2OpozoriloPMM2x17med60in8039 | DIGITAL | IOD_SS2_TCP | 00332
SS2OpozoriloPMM2x17med60in803 | DIGITAL | IOD_SS2_TCP | 00333
SS2OpozoriloPMM2x17med60in8040 | DIGITAL | IOD_SS2_TCP | 00334
SS2OpozoriloPMM2x17med60in8041 | DIGITAL | IOD_SS2_TCP | 00335
SS2OpozoriloPMM2x17med60in8042 | DIGITAL | IOD_SS2_TCP | 00336
SS2OpozoriloPMM2x17med60in804 | DIGITAL | IOD_SS2_TCP | 00337
SS2OpozoriloPMM2x17med60in805 | DIGITAL | IOD_SS2_TCP | 00338
SS2OpozoriloPMM2x17med60in806 | DIGITAL | IOD_SS2_TCP | 00339
SS2OpozoriloPMM2x17med60in807 | DIGITAL | IOD_SS2_TCP | 00340
SS2OpozoriloPMM2x17med60in808 | DIGITAL | IOD_SS2_TCP | 00341
SS2OpozoriloPMM2x17med60in809 | DIGITAL | IOD_SS2_TCP | 00342
SS2OznakeFaz10 | INT | IOD_SS2_TCP | 40046
SS2OznakeFaz11 | INT | IOD_SS2_TCP | 40047
SS2OznakeFaz12 | INT | IOD_SS2_TCP | 40048
SS2OznakeFaz13 | INT | IOD_SS2_TCP | 40049
SS2OznakeFaz14 | INT | IOD_SS2_TCP | 40050
SS2OznakeFaz1 | INT | IOD_SS2_TCP | 40051
SS2OznakeFaz2 | INT | IOD_SS2_TCP | 40052
SS2OznakeFaz3 | INT | IOD_SS2_TCP | 40053
SS2OznakeFaz4 | INT | IOD_SS2_TCP | 40054
SS2OznakeFaz5 | INT | IOD_SS2_TCP | 40055
SS2OznakeFaz6 | INT | IOD_SS2_TCP | 40056
SS2OznakeFaz7 | INT | IOD_SS2_TCP | 40057
SS2OznakeFaz8 | INT | IOD_SS2_TCP | 40058
SS2OznakeFaz9 | INT | IOD_SS2_TCP | 40059
SS2PhaseBool0 | DIGITAL | IOD_SS2_TCP | 00343
SS2PhaseBool1 | DIGITAL | IOD_SS2_TCP | 00344
SS2PhaseBool2 | DIGITAL | IOD_SS2_TCP | 00345
SS2PhaseNext | DIGITAL | IOD_SS2_TCP | 00346
SS2PhaseNo | INT | IOD_SS2_TCP | 40060
SS2PhasePrev | DIGITAL | IOD_SS2_TCP | 00347
SS2PMM1OverCurrentBetw1 | DIGITAL | IOD_SS2_TCP | 00348
SS2PMM1OverCurrentBetw2 | DIGITAL | IOD_SS2_TCP | 00349
SS2PMM1OverCurrentBetw3 | DIGITAL | IOD_SS2_TCP | 00350
SS2PMM1OverCurrentOver1 | DIGITAL | IOD_SS2_TCP | 00351
SS2PMM1OverCurrentOver2 | DIGITAL | IOD_SS2_TCP | 00352
SS2PMM1OverCurrentOver3 | DIGITAL | IOD_SS2_TCP | 00353
SS2PMM1OverVoltage | DIGITAL | IOD_SS2_TCP | 00354
SS2PMM2OverCurrentBetw1 | DIGITAL | IOD_SS2_TCP | 00355
SS2PMM2OverCurrentBetw2 | DIGITAL | IOD_SS2_TCP | 00356
SS2PMM2OverCurrentBetw3 | DIGITAL | IOD_SS2_TCP | 00357
SS2PMM2OverCurrentOver1 | DIGITAL | IOD_SS2_TCP | 00358
SS2PMM2OverCurrentOver2 | DIGITAL | IOD_SS2_TCP | 00359
SS2PMM2OverCurrentOver3 | DIGITAL | IOD_SS2_TCP | 00360
SS2PMM2OverVoltage | DIGITAL | IOD_SS2_TCP | 00361
SS2PMM2x17 | DIGITAL | IOD_SS2_TCP | 00362
SS2PMM1ActiveEnergyConsumed_kWh | REAL | IOD_SS2_TCP | 44163 |  |  |  |  | kVAr | ####
SS2PMM1ActivePowerPhaseA_kW | REAL | IOD_SS2_TCP | 44165 | 0 | 100 | 0 | 100 | kW | ####.#
SS2PMM1ActivePowerPhaseB_kW | REAL | IOD_SS2_TCP | 44167 | 0 | 100 | 0 | 100 | kW | ####.#
SS2PMM1ActivePowerPhaseC_kW | REAL | IOD_SS2_TCP | 44169 | 0 | 100 | 0 | 100 | kW | ####.#
SS2PMM1AlarmPhase1C01_16_60to80 | INT | IOD_SS2_TCP | 40061
SS2PMM1AlarmPhase1C01_16_over80 | INT | IOD_SS2_TCP | 40062
SS2PMM1AlarmPhase1C17_32_60to80 | INT | IOD_SS2_TCP | 40063
SS2PMM1AlarmPhase1C17_32_over80 | INT | IOD_SS2_TCP | 40064
SS2PMM1AlarmPhase1C33_42_60to80 | INT | IOD_SS2_TCP | 40065
SS2PMM1AlarmPhase1C33_42_over80 | INT | IOD_SS2_TCP | 40066
SS2PMM1AlarmPhase1GlobalAlarmReg | INT | IOD_SS2_TCP | 40067
SS2PMM1AlarmPhase2C01_16_60to80 | INT | IOD_SS2_TCP | 40068
SS2PMM1AlarmPhase2C01_16_over80 | INT | IOD_SS2_TCP | 40069
SS2PMM1AlarmPhase2C17_32_60to80 | INT | IOD_SS2_TCP | 40070
SS2PMM1AlarmPhase2C17_32_over80 | INT | IOD_SS2_TCP | 40071
SS2PMM1AlarmPhase2C33_42_60to80 | INT | IOD_SS2_TCP | 40072
SS2PMM1AlarmPhase2C33_42_over80 | INT | IOD_SS2_TCP | 40073
SS2PMM1AlarmPhase2GlobalAlarmReg | INT | IOD_SS2_TCP | 40074
SS2PMM1AlarmPhase3C01_16_60to80 | INT | IOD_SS2_TCP | 40075
SS2PMM1AlarmPhase3C01_16_over80 | INT | IOD_SS2_TCP | 40076
SS2PMM1AlarmPhase3C17_32_60to80 | INT | IOD_SS2_TCP | 40077
SS2PMM1AlarmPhase3C17_32_over80 | INT | IOD_SS2_TCP | 40078
SS2PMM1AlarmPhase3C33_42_60to80 | INT | IOD_SS2_TCP | 40079
SS2PMM1AlarmPhase3C33_42_over80 | INT | IOD_SS2_TCP | 40080
SS2PMM1AlarmPhase3GlobalAlarmReg | INT | IOD_SS2_TCP | 40081
SS2PMM1AparentPowerPhaseA | REAL | IOD_SS2_TCP | 44171 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM1AparentPowerPhaseB | REAL | IOD_SS2_TCP | 44173 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM1AparentPowerPhaseC | REAL | IOD_SS2_TCP | 44175 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM1AverageCurrent_A | REAL | IOD_SS2_TCP | 44177 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1AveragePhaseToNeutral_V | REAL | IOD_SS2_TCP | 44179 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMM1AveragePhaseToPhase_V | REAL | IOD_SS2_TCP | 44181 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM1CurrentInPhaseA_A | REAL | IOD_SS2_TCP | 44183 | 0 | 500 | 0 | 500 | A | ####.#
SS2PMM1CurrentInPhaseB_A | REAL | IOD_SS2_TCP | 44185 | 0 | 500 | 0 | 500 | A | ####.#
SS2PMM1CurrentInPhaseC_A | REAL | IOD_SS2_TCP | 44187 | 0 | 500 | 0 | 500 | A | ####.#
SS2PMM1Frequency_Hz | REAL | IOD_SS2_TCP | 44189 | 0 | 70 | 0 | 70 | Hz | ####.#
SS2PMM1Phase1Current10 | REAL | IOD_SS2_TCP | 44191 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current11 | REAL | IOD_SS2_TCP | 44193 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current12 | REAL | IOD_SS2_TCP | 44195 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current13 | REAL | IOD_SS2_TCP | 44197 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current14 | REAL | IOD_SS2_TCP | 44199 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current15 | REAL | IOD_SS2_TCP | 44201 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current16 | REAL | IOD_SS2_TCP | 44203 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current17 | REAL | IOD_SS2_TCP | 44205 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current18 | REAL | IOD_SS2_TCP | 44207 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current19 | REAL | IOD_SS2_TCP | 44209 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current1 | REAL | IOD_SS2_TCP | 44211 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current20 | REAL | IOD_SS2_TCP | 44213 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current21 | REAL | IOD_SS2_TCP | 44215 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current22 | REAL | IOD_SS2_TCP | 44217 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current23 | REAL | IOD_SS2_TCP | 44219 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current24 | REAL | IOD_SS2_TCP | 44221 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current25 | REAL | IOD_SS2_TCP | 44223 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current26 | REAL | IOD_SS2_TCP | 44225 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current27 | REAL | IOD_SS2_TCP | 44227 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current28 | REAL | IOD_SS2_TCP | 44229 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current29 | REAL | IOD_SS2_TCP | 44231 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current2 | REAL | IOD_SS2_TCP | 44233 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current30 | REAL | IOD_SS2_TCP | 44235 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current31 | REAL | IOD_SS2_TCP | 44237 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current32 | REAL | IOD_SS2_TCP | 44239 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current33 | REAL | IOD_SS2_TCP | 44241 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current34 | REAL | IOD_SS2_TCP | 44243 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current35 | REAL | IOD_SS2_TCP | 44245 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current36 | REAL | IOD_SS2_TCP | 44247 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current37 | REAL | IOD_SS2_TCP | 44249 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current38 | REAL | IOD_SS2_TCP | 44251 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current39 | REAL | IOD_SS2_TCP | 44253 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current3 | REAL | IOD_SS2_TCP | 44255 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current40 | REAL | IOD_SS2_TCP | 44257 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current41 | REAL | IOD_SS2_TCP | 44259 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current42 | REAL | IOD_SS2_TCP | 44261 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current4 | REAL | IOD_SS2_TCP | 44263 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current5 | REAL | IOD_SS2_TCP | 44265 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current6 | REAL | IOD_SS2_TCP | 44267 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current7 | REAL | IOD_SS2_TCP | 44269 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current8 | REAL | IOD_SS2_TCP | 44271 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase1Current9 | REAL | IOD_SS2_TCP | 44273 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current10 | REAL | IOD_SS2_TCP | 44275 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current11 | REAL | IOD_SS2_TCP | 44277 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current12 | REAL | IOD_SS2_TCP | 44279 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current13 | REAL | IOD_SS2_TCP | 44281 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current14 | REAL | IOD_SS2_TCP | 44283 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current15 | REAL | IOD_SS2_TCP | 44285 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current16 | REAL | IOD_SS2_TCP | 44287 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current17 | REAL | IOD_SS2_TCP | 44289 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current18 | REAL | IOD_SS2_TCP | 44291 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current19 | REAL | IOD_SS2_TCP | 44293 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current1 | REAL | IOD_SS2_TCP | 44295 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current20 | REAL | IOD_SS2_TCP | 44297 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current21 | REAL | IOD_SS2_TCP | 44299 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current22 | REAL | IOD_SS2_TCP | 44301 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current23 | REAL | IOD_SS2_TCP | 44303 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current24 | REAL | IOD_SS2_TCP | 44305 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current25 | REAL | IOD_SS2_TCP | 44307 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current26 | REAL | IOD_SS2_TCP | 44309 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current27 | REAL | IOD_SS2_TCP | 44311 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current28 | REAL | IOD_SS2_TCP | 44313 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current29 | REAL | IOD_SS2_TCP | 44315 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current2 | REAL | IOD_SS2_TCP | 44317 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current30 | REAL | IOD_SS2_TCP | 44319 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current31 | REAL | IOD_SS2_TCP | 44321 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current32 | REAL | IOD_SS2_TCP | 44323 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current33 | REAL | IOD_SS2_TCP | 44325 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current34 | REAL | IOD_SS2_TCP | 44327 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current35 | REAL | IOD_SS2_TCP | 44329 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current36 | REAL | IOD_SS2_TCP | 44331 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current37 | REAL | IOD_SS2_TCP | 44333 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current38 | REAL | IOD_SS2_TCP | 44335 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current39 | REAL | IOD_SS2_TCP | 44337 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current3 | REAL | IOD_SS2_TCP | 44339 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current40 | REAL | IOD_SS2_TCP | 44341 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current41 | REAL | IOD_SS2_TCP | 44343 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current42 | REAL | IOD_SS2_TCP | 44345 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current4 | REAL | IOD_SS2_TCP | 44347 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current5 | REAL | IOD_SS2_TCP | 44349 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current6 | REAL | IOD_SS2_TCP | 44351 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current7 | REAL | IOD_SS2_TCP | 44353 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current8 | REAL | IOD_SS2_TCP | 44355 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase2Current9 | REAL | IOD_SS2_TCP | 44357 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current10 | REAL | IOD_SS2_TCP | 44359 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current11 | REAL | IOD_SS2_TCP | 44361 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current12 | REAL | IOD_SS2_TCP | 44363 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current13 | REAL | IOD_SS2_TCP | 44365 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current14 | REAL | IOD_SS2_TCP | 44367 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current15 | REAL | IOD_SS2_TCP | 44369 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current16 | REAL | IOD_SS2_TCP | 44371 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current17 | REAL | IOD_SS2_TCP | 44373 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current18 | REAL | IOD_SS2_TCP | 44375 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current19 | REAL | IOD_SS2_TCP | 44377 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current1 | REAL | IOD_SS2_TCP | 44379 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current20 | REAL | IOD_SS2_TCP | 44381 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current21 | REAL | IOD_SS2_TCP | 44383 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current22 | REAL | IOD_SS2_TCP | 44385 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current23 | REAL | IOD_SS2_TCP | 44387 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current24 | REAL | IOD_SS2_TCP | 44389 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current25 | REAL | IOD_SS2_TCP | 44391 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current26 | REAL | IOD_SS2_TCP | 44393 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current27 | REAL | IOD_SS2_TCP | 44395 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current28 | REAL | IOD_SS2_TCP | 44397 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current29 | REAL | IOD_SS2_TCP | 44399 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current2 | REAL | IOD_SS2_TCP | 44401 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current30 | REAL | IOD_SS2_TCP | 44403 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current31 | REAL | IOD_SS2_TCP | 44405 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current32 | REAL | IOD_SS2_TCP | 44407 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current33 | REAL | IOD_SS2_TCP | 44409 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current34 | REAL | IOD_SS2_TCP | 44411 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current35 | REAL | IOD_SS2_TCP | 44413 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current36 | REAL | IOD_SS2_TCP | 44415 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current37 | REAL | IOD_SS2_TCP | 44417 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current38 | REAL | IOD_SS2_TCP | 44419 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current39 | REAL | IOD_SS2_TCP | 44421 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current3 | REAL | IOD_SS2_TCP | 44423 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current40 | REAL | IOD_SS2_TCP | 44425 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current41 | REAL | IOD_SS2_TCP | 44427 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current42 | REAL | IOD_SS2_TCP | 44429 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current4 | REAL | IOD_SS2_TCP | 44431 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current5 | REAL | IOD_SS2_TCP | 44433 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current6 | REAL | IOD_SS2_TCP | 44435 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current7 | REAL | IOD_SS2_TCP | 44437 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current8 | REAL | IOD_SS2_TCP | 44439 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1Phase3Current9 | REAL | IOD_SS2_TCP | 44441 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM1PowerFactorSys | REAL | IOD_SS2_TCP | 44443 | 0 | 1 | 0 | 1 |  | ####.#
SS2PMM1ReactiveEnergyConsumed_kVARh | REAL | IOD_SS2_TCP | 44445 |  |  |  |  | kVArh | ####.#
SS2PMM1ReactivePowerPhaseA | REAL | IOD_SS2_TCP | 44447 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM1ReactivePowerPhaseB | REAL | IOD_SS2_TCP | 44449 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM1ReactivePowerPhaseC | REAL | IOD_SS2_TCP | 44451 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM1TotalActivePower_kW | REAL | IOD_SS2_TCP | 44453 | 0 | 300 | 0 | 300 | kW | ####.#
SS2PMM1TotalAparentPower_kVA | REAL | IOD_SS2_TCP | 44455 | 0 | 300 | 0 | 300 | kVA | ####.#
SS2PMM1TotalPowerFactor | REAL | IOD_SS2_TCP | 44457 | 0 | 1 | 0 | 1 |  | ####.#
SS2PMM1TotalReactivePower_kVAR | REAL | IOD_SS2_TCP | 44459 | 0 | 300 | 0 | 300 | kVAr | ####.#
SS2PMM1VirA_fsys | REAL | IOD_SS2_TCP | 44461 | 0 | 70 | 0 | 70 | Hz | ####.#
SS2PMM1VirA_Isys | REAL | IOD_SS2_TCP | 44463 | 0 | 1000 | 0 | 1000 | A | ####.#
SS2PMM1VirA_PFsys | REAL | IOD_SS2_TCP | 44465 | 0 | 1 | 0 | 0 | 1 | ####.#
SS2PMM1VirA_Psys | REAL | IOD_SS2_TCP | 44467 | 0 | 300 | 0 | 300 | kW | ####.#
SS2PMM1VirA_Qsys | REAL | IOD_SS2_TCP | 44469 | 0 | 300 | 0 | 300 | kVAr | ####.#
SS2PMM1VirA_Ssys | REAL | IOD_SS2_TCP | 44471 | 0 | 300 | 0 | 300 | kVA | ####.#
SS2PMM1VirA_Usys | REAL | IOD_SS2_TCP | 44473 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM1VirB_fsys | REAL | IOD_SS2_TCP | 44475 | 0 | 70 | 0 | 70 | Hz | ####.#
SS2PMM1VirB_Isys | REAL | IOD_SS2_TCP | 44477 | 0 | 1000 | 0 | 1000 | A | ####.#
SS2PMM1VirB_PFsys | REAL | IOD_SS2_TCP | 44479 | 0 | 1 | 0 | 0 | 1 | ####.#
SS2PMM1VirB_Psys | REAL | IOD_SS2_TCP | 44481 | 0 | 300 | 0 | 300 | kW | ####.#
SS2PMM1VirB_Qsys | REAL | IOD_SS2_TCP | 44483 | 0 | 300 | 0 | 300 | kVAr | ####.#
SS2PMM1VirB_Ssys | REAL | IOD_SS2_TCP | 44485 | 0 | 300 | 0 | 300 | kVA | ####.#
SS2PMM1VirB_Usys | REAL | IOD_SS2_TCP | 44487 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM1VirBActiveEnergyConsumed_kWh | REAL | IOD_SS2_TCP | 44489 |  |  |  |  | kVArh | ####.#
SS2PMM1VirBActivePowerPhaseA_kW | REAL | IOD_SS2_TCP | 44491 | 0 | 100 | 0 | 100 | kW | ####.#
SS2PMM1VirBActivePowerPhaseB_kW | REAL | IOD_SS2_TCP | 44493 | 0 | 100 | 0 | 100 | kW | ####.#
SS2PMM1VirBActivePowerPhaseC_kW | REAL | IOD_SS2_TCP | 44495 | 0 | 100 | 0 | 100 | kW | ####.#
SS2PMM1VirBAparentPowerPhaseA | REAL | IOD_SS2_TCP | 44497 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM1VirBAparentPowerPhaseB | REAL | IOD_SS2_TCP | 44499 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM1VirBAparentPowerPhaseC | REAL | IOD_SS2_TCP | 44501 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM1VirBAverageCurrent_A | REAL | IOD_SS2_TCP | 44503 | 0 | 100 | 0 | 100 | A | ####.#
SS2PMM1VirBAveragePhaseToNeutral_V | REAL | IOD_SS2_TCP | 44505 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMM1VirBAveragePhaseToPhase_V | REAL | IOD_SS2_TCP | 44507 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMM1VirBCurrentInPhaseA_A | REAL | IOD_SS2_TCP | 44509 | 0 | 100 | 0 | 100 | A | ####.#
SS2PMM1VirBCurrentInPhaseB_A | REAL | IOD_SS2_TCP | 44511 | 0 | 100 | 0 | 100 | A | ####.#
SS2PMM1VirBCurrentInPhaseC_A | REAL | IOD_SS2_TCP | 44513 | 0 | 100 | 0 | 100 | A | ####.#
SS2PMM1VirBFrequency_Hz | REAL | IOD_SS2_TCP | 44515 | 0 | 70 | 0 | 70 | Hz | ####.#
SS2PMM1VirBPowerFactorSys | REAL | IOD_SS2_TCP | 44517 | 0 | 1 | 0 | 1 |  | ####.#
SS2PMM1VirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS2_TCP | 44519 |  |  |  |  | kVArh | ####.#
SS2PMM1VirBReactivePowerPhaseA | REAL | IOD_SS2_TCP | 44521 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM1VirBReactivePowerPhaseB | REAL | IOD_SS2_TCP | 44523 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM1VirBReactivePowerPhaseC | REAL | IOD_SS2_TCP | 44525 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM1VirBTotalActivePower_kW | REAL | IOD_SS2_TCP | 44527 | 0 | 300 | 0 | 300 | kW | ####.#
SS2PMM1VirBTotalAparentPower_kVA | REAL | IOD_SS2_TCP | 44529 | 0 | 300 | 0 | 300 | kVA | ####.#
SS2PMM1VirBTotalPowerFactor | REAL | IOD_SS2_TCP | 44531 | 0 | 1 | 0 | 1 |  | ####.#
SS2PMM1VirBTotalReactivePower_kVAR | REAL | IOD_SS2_TCP | 44533 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM1VirBVoltageBetweenPhaseAB_V | REAL | IOD_SS2_TCP | 44535 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM1VirBVoltageBetweenPhaseAN_V | REAL | IOD_SS2_TCP | 44537 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMM1VirBVoltageBetweenPhaseBC_V | REAL | IOD_SS2_TCP | 44539 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM1VirBVoltageBetweenPhaseBN_V | REAL | IOD_SS2_TCP | 44541 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMM1VirBVoltageBetweenPhaseCA_V | REAL | IOD_SS2_TCP | 44543 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM1VirBVoltageBetweenPhaseCN_V | REAL | IOD_SS2_TCP | 44545 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMM1VoltageBetweenPhaseAB_V | REAL | IOD_SS2_TCP | 44547 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM1VoltageBetweenPhaseAN_V | REAL | IOD_SS2_TCP | 44549 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMM1VoltageBetweenPhaseBC_V | REAL | IOD_SS2_TCP | 44551 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM1VoltageBetweenPhaseBN_V | REAL | IOD_SS2_TCP | 44553 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMM1VoltageBetweenPhaseCA_V | REAL | IOD_SS2_TCP | 44555 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM1VoltageBetweenPhaseCN_V | REAL | IOD_SS2_TCP | 44557 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMM2ActiveEnergyConsumed_kWh | REAL | IOD_SS2_TCP | 44559 |  |  |  |  | kVAr | ####.#
SS2PMM2ActivePowerPhaseA_kW | REAL | IOD_SS2_TCP | 44561 | 0 | 100 | 0 | 100 | kW | ####.#
SS2PMM2ActivePowerPhaseB_kW | REAL | IOD_SS2_TCP | 44563 | 0 | 100 | 0 | 100 | kW | ####.#
SS2PMM2ActivePowerPhaseC_kW | REAL | IOD_SS2_TCP | 44565 | 0 | 100 | 0 | 100 | kW | ####.#
SS2PMM2AlarmPhase1C01_16_60to80 | INT | IOD_SS2_TCP | 40082 | [5 empty] | ####.#
SS2PMM2AlarmPhase1C01_16_over80 | INT | IOD_SS2_TCP | 40083 | [5 empty] | ####.#
SS2PMM2AlarmPhase1C17_32_60to80 | INT | IOD_SS2_TCP | 40084 | [5 empty] | ####.#
SS2PMM2AlarmPhase1C17_32_over80 | INT | IOD_SS2_TCP | 40085 | [5 empty] | ####.#
SS2PMM2AlarmPhase1C33_42_60to80 | INT | IOD_SS2_TCP | 40086 | [5 empty] | ####.#
SS2PMM2AlarmPhase1C33_42_over80 | INT | IOD_SS2_TCP | 40087 | [5 empty] | ####.#
SS2PMM2AlarmPhase1GlobalAlarmReg | INT | IOD_SS2_TCP | 40088 | [5 empty] | ####.#
SS2PMM2AlarmPhase2C01_16_60to80 | INT | IOD_SS2_TCP | 40089 | [5 empty] | ####.#
SS2PMM2AlarmPhase2C01_16_over80 | INT | IOD_SS2_TCP | 40090 | [5 empty] | ####.#
SS2PMM2AlarmPhase2C17_32_60to80 | INT | IOD_SS2_TCP | 40091 | [5 empty] | ####.#
SS2PMM2AlarmPhase2C17_32_over80 | INT | IOD_SS2_TCP | 40092 | [5 empty] | ####.#
SS2PMM2AlarmPhase2C33_42_60to80 | INT | IOD_SS2_TCP | 40093 | [5 empty] | ####.#
SS2PMM2AlarmPhase2C33_42_over80 | INT | IOD_SS2_TCP | 40094 | [5 empty] | ####.#
SS2PMM2AlarmPhase2GlobalAlarmReg | INT | IOD_SS2_TCP | 40095 | [5 empty] | ####.#
SS2PMM2AlarmPhase3C01_16_60to80 | INT | IOD_SS2_TCP | 40096 | [5 empty] | ####.#
SS2PMM2AlarmPhase3C01_16_over80 | INT | IOD_SS2_TCP | 40097 | [5 empty] | ####.#
SS2PMM2AlarmPhase3C17_32_60to80 | INT | IOD_SS2_TCP | 40098 | [5 empty] | ####.#
SS2PMM2AlarmPhase3C17_32_over80 | INT | IOD_SS2_TCP | 40099 | [5 empty] | ####.#
SS2PMM2AlarmPhase3C33_42_60to80 | INT | IOD_SS2_TCP | 40100 | [5 empty] | ####.#
SS2PMM2AlarmPhase3C33_42_over80 | INT | IOD_SS2_TCP | 40101 | [5 empty] | ####.#
SS2PMM2AlarmPhase3GlobalAlarmReg | INT | IOD_SS2_TCP | 40102 | [5 empty] | ####.#
SS2PMM2AparentPowerPhaseA | REAL | IOD_SS2_TCP | 44567 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM2AparentPowerPhaseB | REAL | IOD_SS2_TCP | 44569 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM2AparentPowerPhaseC | REAL | IOD_SS2_TCP | 44571 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM2AverageCurrent_A | REAL | IOD_SS2_TCP | 44573 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2AveragePhaseToNeutral_V | REAL | IOD_SS2_TCP | 44575 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMM2AveragePhaseToPhase_V | REAL | IOD_SS2_TCP | 44577 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM2CurrentInPhaseA_A | REAL | IOD_SS2_TCP | 44579 | 0 | 500 | 0 | 500 | A | ####.#
SS2PMM2CurrentInPhaseB_A | REAL | IOD_SS2_TCP | 44581 | 0 | 500 | 0 | 500 | A | ####.#
SS2PMM2CurrentInPhaseC_A | REAL | IOD_SS2_TCP | 44583 | 0 | 500 | 0 | 500 | A | ####.#
SS2PMM2Frequency_Hz | REAL | IOD_SS2_TCP | 44585 | 0 | 70 | 0 | 70 | Hz | ####.#
SS2PMM2Phase1Current1 | REAL | IOD_SS2_TCP | 44587 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2Phase1Current2 | REAL | IOD_SS2_TCP | 44589 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2Phase1Current3 | REAL | IOD_SS2_TCP | 44591 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2Phase1Current4 | REAL | IOD_SS2_TCP | 44593 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2Phase1Current5 | REAL | IOD_SS2_TCP | 44595 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2Phase1Current6 | REAL | IOD_SS2_TCP | 44597 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2Phase1Current7 | REAL | IOD_SS2_TCP | 44599 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current8 | REAL | IOD_SS2_TCP | 44601 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current9 | REAL | IOD_SS2_TCP | 44603 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current10 | REAL | IOD_SS2_TCP | 44605 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current11 | REAL | IOD_SS2_TCP | 44607 | 0 | 50 | 0 | 50 | A | ####.#
SS2PMM2Phase1Current12 | REAL | IOD_SS2_TCP | 44609 | 0 | 50 | 0 | 50 | A | ####.#
SS2PMM2Phase1Current13 | REAL | IOD_SS2_TCP | 44611 | 0 | 50 | 0 | 50 | A | ####.#
SS2PMM2Phase1Current14 | REAL | IOD_SS2_TCP | 44613 | 0 | 50 | 0 | 50 | A | ####.#
SS2PMM2Phase1Current15 | REAL | IOD_SS2_TCP | 44615 | 0 | 50 | 0 | 50 | A | ####.#
SS2PMM2Phase1Current16 | REAL | IOD_SS2_TCP | 44617 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current17 | REAL | IOD_SS2_TCP | 44619 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current18 | REAL | IOD_SS2_TCP | 44621 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current19 | REAL | IOD_SS2_TCP | 44623 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current20 | REAL | IOD_SS2_TCP | 44625 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current21 | REAL | IOD_SS2_TCP | 44627 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current22 | REAL | IOD_SS2_TCP | 44629 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2Phase1Current23 | REAL | IOD_SS2_TCP | 44631 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2Phase1Current24 | REAL | IOD_SS2_TCP | 44633 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2Phase1Current25 | REAL | IOD_SS2_TCP | 44635 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2Phase1Current26 | REAL | IOD_SS2_TCP | 44637 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2Phase1Current27 | REAL | IOD_SS2_TCP | 44639 | 0 | 16 | 0 | 16 | A | ####.#
SS2PMM2Phase1Current28 | REAL | IOD_SS2_TCP | 44641 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current29 | REAL | IOD_SS2_TCP | 44643 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current30 | REAL | IOD_SS2_TCP | 44645 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current31 | REAL | IOD_SS2_TCP | 44647 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current32 | REAL | IOD_SS2_TCP | 44649 | 0 | 50 | 0 | 50 | A | ####.#
SS2PMM2Phase1Current33 | REAL | IOD_SS2_TCP | 44651 | 0 | 50 | 0 | 50 | A | ####.#
SS2PMM2Phase1Current34 | REAL | IOD_SS2_TCP | 44653 | 0 | 50 | 0 | 50 | A | ####.#
SS2PMM2Phase1Current35 | REAL | IOD_SS2_TCP | 44655 | 0 | 50 | 0 | 50 | A | ####.#
SS2PMM2Phase1Current36 | REAL | IOD_SS2_TCP | 44657 | 0 | 50 | 0 | 50 | A | ####.#
SS2PMM2Phase1Current37 | REAL | IOD_SS2_TCP | 44659 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current38 | REAL | IOD_SS2_TCP | 44661 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current39 | REAL | IOD_SS2_TCP | 44663 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current40 | REAL | IOD_SS2_TCP | 44665 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current41 | REAL | IOD_SS2_TCP | 44667 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase1Current42 | REAL | IOD_SS2_TCP | 44669 | 0 | 32 | 0 | 32 | A | ####.#
SS2PMM2Phase2Current10 | REAL | IOD_SS2_TCP | 44671
SS2PMM2Phase2Current11 | REAL | IOD_SS2_TCP | 44673
SS2PMM2Phase2Current12 | REAL | IOD_SS2_TCP | 44675
SS2PMM2Phase2Current13 | REAL | IOD_SS2_TCP | 44677
SS2PMM2Phase2Current14 | REAL | IOD_SS2_TCP | 44679
SS2PMM2Phase2Current15 | REAL | IOD_SS2_TCP | 44681
SS2PMM2Phase2Current16 | REAL | IOD_SS2_TCP | 44683
SS2PMM2Phase2Current17 | REAL | IOD_SS2_TCP | 44685
SS2PMM2Phase2Current18 | REAL | IOD_SS2_TCP | 44687
SS2PMM2Phase2Current19 | REAL | IOD_SS2_TCP | 44689
SS2PMM2Phase2Current1 | REAL | IOD_SS2_TCP | 44691
SS2PMM2Phase2Current20 | REAL | IOD_SS2_TCP | 44693
SS2PMM2Phase2Current21 | REAL | IOD_SS2_TCP | 44695
SS2PMM2Phase2Current22 | REAL | IOD_SS2_TCP | 44697
SS2PMM2Phase2Current23 | REAL | IOD_SS2_TCP | 44699
SS2PMM2Phase2Current24 | REAL | IOD_SS2_TCP | 44701
SS2PMM2Phase2Current25 | REAL | IOD_SS2_TCP | 44703
SS2PMM2Phase2Current26 | REAL | IOD_SS2_TCP | 44705
SS2PMM2Phase2Current27 | REAL | IOD_SS2_TCP | 44707
SS2PMM2Phase2Current28 | REAL | IOD_SS2_TCP | 44709
SS2PMM2Phase2Current29 | REAL | IOD_SS2_TCP | 44711
SS2PMM2Phase2Current2 | REAL | IOD_SS2_TCP | 44713
SS2PMM2Phase2Current30 | REAL | IOD_SS2_TCP | 44715
SS2PMM2Phase2Current31 | REAL | IOD_SS2_TCP | 44717
SS2PMM2Phase2Current32 | REAL | IOD_SS2_TCP | 44719
SS2PMM2Phase2Current33 | REAL | IOD_SS2_TCP | 44721
SS2PMM2Phase2Current34 | REAL | IOD_SS2_TCP | 44723
SS2PMM2Phase2Current35 | REAL | IOD_SS2_TCP | 44725
SS2PMM2Phase2Current36 | REAL | IOD_SS2_TCP | 44727
SS2PMM2Phase2Current37 | REAL | IOD_SS2_TCP | 44729
SS2PMM2Phase2Current38 | REAL | IOD_SS2_TCP | 44731
SS2PMM2Phase2Current39 | REAL | IOD_SS2_TCP | 44733
SS2PMM2Phase2Current3 | REAL | IOD_SS2_TCP | 44735
SS2PMM2Phase2Current40 | REAL | IOD_SS2_TCP | 44737
SS2PMM2Phase2Current41 | REAL | IOD_SS2_TCP | 44739
SS2PMM2Phase2Current42 | REAL | IOD_SS2_TCP | 44741
SS2PMM2Phase2Current4 | REAL | IOD_SS2_TCP | 44743
SS2PMM2Phase2Current5 | REAL | IOD_SS2_TCP | 44745
SS2PMM2Phase2Current6 | REAL | IOD_SS2_TCP | 44747
SS2PMM2Phase2Current7 | REAL | IOD_SS2_TCP | 44749
SS2PMM2Phase2Current8 | REAL | IOD_SS2_TCP | 44751
SS2PMM2Phase2Current9 | REAL | IOD_SS2_TCP | 44753
SS2PMM2Phase3Current10 | REAL | IOD_SS2_TCP | 44755
SS2PMM2Phase3Current11 | REAL | IOD_SS2_TCP | 44757
SS2PMM2Phase3Current12 | REAL | IOD_SS2_TCP | 44759
SS2PMM2Phase3Current13 | REAL | IOD_SS2_TCP | 44761
SS2PMM2Phase3Current14 | REAL | IOD_SS2_TCP | 44763
SS2PMM2Phase3Current15 | REAL | IOD_SS2_TCP | 44765
SS2PMM2Phase3Current16 | REAL | IOD_SS2_TCP | 44767
SS2PMM2Phase3Current17 | REAL | IOD_SS2_TCP | 44769
SS2PMM2Phase3Current18 | REAL | IOD_SS2_TCP | 44771
SS2PMM2Phase3Current19 | REAL | IOD_SS2_TCP | 44773
SS2PMM2Phase3Current1 | REAL | IOD_SS2_TCP | 44775
SS2PMM2Phase3Current20 | REAL | IOD_SS2_TCP | 44777
SS2PMM2Phase3Current21 | REAL | IOD_SS2_TCP | 44779
SS2PMM2Phase3Current22 | REAL | IOD_SS2_TCP | 44781
SS2PMM2Phase3Current23 | REAL | IOD_SS2_TCP | 44783
SS2PMM2Phase3Current24 | REAL | IOD_SS2_TCP | 44785
SS2PMM2Phase3Current25 | REAL | IOD_SS2_TCP | 44787
SS2PMM2Phase3Current26 | REAL | IOD_SS2_TCP | 44789
SS2PMM2Phase3Current27 | REAL | IOD_SS2_TCP | 44791
SS2PMM2Phase3Current28 | REAL | IOD_SS2_TCP | 44793
SS2PMM2Phase3Current29 | REAL | IOD_SS2_TCP | 44795
SS2PMM2Phase3Current2 | REAL | IOD_SS2_TCP | 44797
SS2PMM2Phase3Current30 | REAL | IOD_SS2_TCP | 44799
SS2PMM2Phase3Current31 | REAL | IOD_SS2_TCP | 44801
SS2PMM2Phase3Current32 | REAL | IOD_SS2_TCP | 44803
SS2PMM2Phase3Current33 | REAL | IOD_SS2_TCP | 44805
SS2PMM2Phase3Current34 | REAL | IOD_SS2_TCP | 44807
SS2PMM2Phase3Current35 | REAL | IOD_SS2_TCP | 44809
SS2PMM2Phase3Current36 | REAL | IOD_SS2_TCP | 44811
SS2PMM2Phase3Current37 | REAL | IOD_SS2_TCP | 44813
SS2PMM2Phase3Current38 | REAL | IOD_SS2_TCP | 44815
SS2PMM2Phase3Current39 | REAL | IOD_SS2_TCP | 44817
SS2PMM2Phase3Current3 | REAL | IOD_SS2_TCP | 44819
SS2PMM2Phase3Current40 | REAL | IOD_SS2_TCP | 44821
SS2PMM2Phase3Current41 | REAL | IOD_SS2_TCP | 44823
SS2PMM2Phase3Current42 | REAL | IOD_SS2_TCP | 44825
SS2PMM2Phase3Current4 | REAL | IOD_SS2_TCP | 44827
SS2PMM2Phase3Current5 | REAL | IOD_SS2_TCP | 44829
SS2PMM2Phase3Current6 | REAL | IOD_SS2_TCP | 44831
SS2PMM2Phase3Current7 | REAL | IOD_SS2_TCP | 44833
SS2PMM2Phase3Current8 | REAL | IOD_SS2_TCP | 44835
SS2PMM2Phase3Current9 | REAL | IOD_SS2_TCP | 44837
SS2PMM2PowerFactorSys | REAL | IOD_SS2_TCP | 44839 | 0 | 1 | 0 | 1 |  | ####.#
SS2PMM2ReactiveEnergyConsumed_kVARh | REAL | IOD_SS2_TCP | 44841 |  |  |  |  | kVArh | ###
SS2PMM2ReactivePowerPhaseA | REAL | IOD_SS2_TCP | 44843 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM2ReactivePowerPhaseB | REAL | IOD_SS2_TCP | 44845 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM2ReactivePowerPhaseC | REAL | IOD_SS2_TCP | 44847 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM2TotalActivePower_kW | REAL | IOD_SS2_TCP | 44849 | 0 | 300 | 0 | 300 | kW | ####.#
SS2PMM2TotalAparentPower_kVA | REAL | IOD_SS2_TCP | 44851 | 0 | 300 | 0 | 300 | kVA | ####.#
SS2PMM2TotalPowerFactor | REAL | IOD_SS2_TCP | 44853 | 0 | 1 | 0 | 1 |  | ####.#
SS2PMM2TotalReactivePower_kVAR | REAL | IOD_SS2_TCP | 44855 | 0 | 300 | 0 | 300 | kVAr | ####.#
SS2PMM2VirA_fsys | REAL | IOD_SS2_TCP | 44857 | 0 | 70 | 0 | 70 | Hz | ####.#
SS2PMM2VirA_Isys | REAL | IOD_SS2_TCP | 44859 | 0 | 1000 | 0 | 1000 | A | ####.#
SS2PMM2VirA_PFsys | REAL | IOD_SS2_TCP | 44861 | 0 | 1 | 0 | 1 |  | ####.#
SS2PMM2VirA_Psys | REAL | IOD_SS2_TCP | 44863 | 0 | 300 | 0 | 300 | kW | ####.#
SS2PMM2VirA_Qsys | REAL | IOD_SS2_TCP | 44865 | 0 | 300 | 0 | 300 | kVAr | ####.#
SS2PMM2VirA_Ssys | REAL | IOD_SS2_TCP | 44867 | 0 | 300 | 0 | 300 | kVA | ####.#
SS2PMM2VirA_Usys | REAL | IOD_SS2_TCP | 44869 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM2VirB_fsys | REAL | IOD_SS2_TCP | 44871 | 0 | 70 | 0 | 70 | Hz | ####.#
SS2PMM2VirB_Isys | REAL | IOD_SS2_TCP | 44873 | 0 | 1000 | 0 | 1000 | A | ####.#
SS2PMM2VirB_PFsys | REAL | IOD_SS2_TCP | 44875 | 0 | 1 | 0 | 1 |  | ####.#
SS2PMM2VirB_Psys | REAL | IOD_SS2_TCP | 44877 | 0 | 300 | 0 | 300 | kW | ####.#
SS2PMM2VirB_Qsys | REAL | IOD_SS2_TCP | 44879 | 0 | 300 | 0 | 300 | kVAr | ####.#
SS2PMM2VirB_Ssys | REAL | IOD_SS2_TCP | 44881 | 0 | 300 | 0 | 300 | kVA | ####.#
SS2PMM2VirB_Usys | REAL | IOD_SS2_TCP | 44883 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM2VirBActiveEnergyConsumed_kWh | REAL | IOD_SS2_TCP | 44885 |  |  |  |  | kVArh | ####.#
SS2PMM2VirBActivePowerPhaseA_kW | REAL | IOD_SS2_TCP | 44887 | 0 | 100 | 0 | 100 | kW | ####.#
SS2PMM2VirBActivePowerPhaseB_kW | REAL | IOD_SS2_TCP | 44889 | 0 | 100 | 0 | 100 | kW | ####.#
SS2PMM2VirBActivePowerPhaseC_kW | REAL | IOD_SS2_TCP | 44891 | 0 | 100 | 0 | 100 | kW | ####.#
SS2PMM2VirBAparentPowerPhaseA | REAL | IOD_SS2_TCP | 44893 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM2VirBAparentPowerPhaseB | REAL | IOD_SS2_TCP | 44895 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM2VirBAparentPowerPhaseC | REAL | IOD_SS2_TCP | 44897 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM2VirBAverageCurrent_A | REAL | IOD_SS2_TCP | 44899 | 0 | 100 | 0 | 100 | A | ####.#
SS2PMM2VirBAveragePhaseToNeutral_V | REAL | IOD_SS2_TCP | 44901 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMM2VirBAveragePhaseToPhase_V | REAL | IOD_SS2_TCP | 44903 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMM2VirBCurrentInPhaseA_A | REAL | IOD_SS2_TCP | 44905 | 0 | 100 | 0 | 100 | A | ####.#
SS2PMM2VirBCurrentInPhaseB_A | REAL | IOD_SS2_TCP | 44907 | 0 | 100 | 0 | 100 | A | ####.#
SS2PMM2VirBCurrentInPhaseC_A | REAL | IOD_SS2_TCP | 44909 | 0 | 100 | 0 | 100 | A | ####.#
SS2PMM2VirBFrequency_Hz | REAL | IOD_SS2_TCP | 44911 | 0 | 70 | 0 | 70 | Hz | ####.#
SS2PMM2VirBPowerFactorSys | REAL | IOD_SS2_TCP | 44913 | 0 | 1 | 0 | 1 |  | ####.#
SS2PMM2VirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS2_TCP | 44915 |  |  |  |  | kVArh | ####.#
SS2PMM2VirBReactivePowerPhaseA | REAL | IOD_SS2_TCP | 44917 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM2VirBReactivePowerPhaseB | REAL | IOD_SS2_TCP | 44919 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM2VirBReactivePowerPhaseC | REAL | IOD_SS2_TCP | 44921 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM2VirBTotalActivePower_kW | REAL | IOD_SS2_TCP | 44923 | 0 | 300 | 0 | 300 | kW | ####.#
SS2PMM2VirBTotalAparentPower_kVA | REAL | IOD_SS2_TCP | 44925 | 0 | 300 | 0 | 300 | kVA | ####.#
SS2PMM2VirBTotalPowerFactor | REAL | IOD_SS2_TCP | 44927 | 0 | 1 | 0 | 1 |  | ####.#
SS2PMM2VirBTotalReactivePower_kVAR | REAL | IOD_SS2_TCP | 44929 | 0 | 100 | 0 | 100 | kVAr | ####.#
SS2PMM2VirBVoltageBetweenPhaseAB_V | REAL | IOD_SS2_TCP | 44931 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM2VirBVoltageBetweenPhaseAN_V | REAL | IOD_SS2_TCP | 44933 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMM2VirBVoltageBetweenPhaseBC_V | REAL | IOD_SS2_TCP | 44935 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM2VirBVoltageBetweenPhaseBN_V | REAL | IOD_SS2_TCP | 44937 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMM2VirBVoltageBetweenPhaseCA_V | REAL | IOD_SS2_TCP | 44939 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM2VirBVoltageBetweenPhaseCN_V | REAL | IOD_SS2_TCP | 44941 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMM2VoltageBetweenPhaseAB_V | REAL | IOD_SS2_TCP | 44943 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM2VoltageBetweenPhaseAN_V | REAL | IOD_SS2_TCP | 44945 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMM2VoltageBetweenPhaseBC_V | REAL | IOD_SS2_TCP | 44947 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM2VoltageBetweenPhaseBN_V | REAL | IOD_SS2_TCP | 44949 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMM2VoltageBetweenPhaseCA_V | REAL | IOD_SS2_TCP | 44951 | 0 | 450 | 0 | 450 | V | ####.#
SS2PMM2VoltageBetweenPhaseCN_V | REAL | IOD_SS2_TCP | 44953 | 0 | 270 | 0 | 270 | V | ####.#
SS2PMMPanelActiveEnergyConsumed_kWh | REAL | IOD_SS2_TCP | 44955
SS2PMMPanelActivePowerPhaseA_kW | REAL | IOD_SS2_TCP | 44957
SS2PMMPanelActivePowerPhaseB_kW | REAL | IOD_SS2_TCP | 44959
SS2PMMPanelActivePowerPhaseC_kW | REAL | IOD_SS2_TCP | 44961
SS2PMMPanelAlarmPhase1C01_16_60to80 | INT | IOD_SS2_TCP | 40103
SS2PMMPanelAlarmPhase1C01_16_over80 | INT | IOD_SS2_TCP | 40104
SS2PMMPanelAlarmPhase1C17_32_60to80 | INT | IOD_SS2_TCP | 40105
SS2PMMPanelAlarmPhase1C17_32_over80 | INT | IOD_SS2_TCP | 40106
SS2PMMPanelAlarmPhase1C33_42_60to80 | INT | IOD_SS2_TCP | 40107
SS2PMMPanelAlarmPhase1C33_42_over80 | INT | IOD_SS2_TCP | 40108
SS2PMMPanelAlarmPhase1GlobalAlarmReg | INT | IOD_SS2_TCP | 40109
SS2PMMPanelAlarmPhase2C01_16_60to80 | INT | IOD_SS2_TCP | 40110
SS2PMMPanelAlarmPhase2C01_16_over80 | INT | IOD_SS2_TCP | 40111
SS2PMMPanelAlarmPhase2C17_32_60to80 | INT | IOD_SS2_TCP | 40112
SS2PMMPanelAlarmPhase2C17_32_over80 | INT | IOD_SS2_TCP | 40113
SS2PMMPanelAlarmPhase2C33_42_60to80 | INT | IOD_SS2_TCP | 40114
SS2PMMPanelAlarmPhase2C33_42_over80 | INT | IOD_SS2_TCP | 40115
SS2PMMPanelAlarmPhase2GlobalAlarmReg | INT | IOD_SS2_TCP | 40116
SS2PMMPanelAlarmPhase3C01_16_60to80 | INT | IOD_SS2_TCP | 40117
SS2PMMPanelAlarmPhase3C01_16_over80 | INT | IOD_SS2_TCP | 40118
SS2PMMPanelAlarmPhase3C17_32_60to80 | INT | IOD_SS2_TCP | 40119
SS2PMMPanelAlarmPhase3C17_32_over80 | INT | IOD_SS2_TCP | 40120
SS2PMMPanelAlarmPhase3C33_42_60to80 | INT | IOD_SS2_TCP | 40121
SS2PMMPanelAlarmPhase3C33_42_over80 | INT | IOD_SS2_TCP | 40122
SS2PMMPanelAlarmPhase3GlobalAlarmReg | INT | IOD_SS2_TCP | 40123
SS2PMMPanelAparentPowerPhaseA | REAL | IOD_SS2_TCP | 44963
SS2PMMPanelAparentPowerPhaseB | REAL | IOD_SS2_TCP | 44965
SS2PMMPanelAparentPowerPhaseC | REAL | IOD_SS2_TCP | 44967
SS2PMMPanelAverageCurrent_A | REAL | IOD_SS2_TCP | 44969
SS2PMMPanelAveragePhaseToNeutral_V | REAL | IOD_SS2_TCP | 44971
SS2PMMPanelAveragePhaseToPhase_V | REAL | IOD_SS2_TCP | 44973
SS2PMMPanelCurrentInPhaseA_A | REAL | IOD_SS2_TCP | 44975
SS2PMMPanelCurrentInPhaseB_A | REAL | IOD_SS2_TCP | 44977
SS2PMMPanelCurrentInPhaseC_A | REAL | IOD_SS2_TCP | 44979
SS2PMMPanelFrequency_Hz | REAL | IOD_SS2_TCP | 44981
SS2PMMPanelPowerFactorSys | REAL | IOD_SS2_TCP | 44983
SS2PMMPanelReactiveEnergyConsumed_kVARh | REAL | IOD_SS2_TCP | 44985
SS2PMMPanelReactivePowerPhaseA | REAL | IOD_SS2_TCP | 44987
SS2PMMPanelReactivePowerPhaseB | REAL | IOD_SS2_TCP | 44989
SS2PMMPanelReactivePowerPhaseC | REAL | IOD_SS2_TCP | 44991
SS2PMMPanelTotalActivePower_kW | REAL | IOD_SS2_TCP | 44993
SS2PMMPanelTotalAparentPower_kVA | REAL | IOD_SS2_TCP | 44995
SS2PMMPanelTotalPowerFactor | REAL | IOD_SS2_TCP | 44997
SS2PMMPanelTotalReactivePower_kVAR | REAL | IOD_SS2_TCP | 44999
SS2PMMPanelVirA_fsys | REAL | IOD_SS2_TCP | 45001
SS2PMMPanelVirA_Isys | REAL | IOD_SS2_TCP | 45003
SS2PMMPanelVirA_PFsys | REAL | IOD_SS2_TCP | 45005
SS2PMMPanelVirA_Psys | REAL | IOD_SS2_TCP | 45007
SS2PMMPanelVirA_Qsys | REAL | IOD_SS2_TCP | 45009
SS2PMMPanelVirA_Ssys | REAL | IOD_SS2_TCP | 45011
SS2PMMPanelVirA_Usys | REAL | IOD_SS2_TCP | 45013
SS2PMMPanelVirB_fsys | REAL | IOD_SS2_TCP | 45015
SS2PMMPanelVirB_Isys | REAL | IOD_SS2_TCP | 45017
SS2PMMPanelVirB_PFsys | REAL | IOD_SS2_TCP | 45019
SS2PMMPanelVirB_Psys | REAL | IOD_SS2_TCP | 45021
SS2PMMPanelVirB_Qsys | REAL | IOD_SS2_TCP | 45023
SS2PMMPanelVirB_Ssys | REAL | IOD_SS2_TCP | 45025
SS2PMMPanelVirB_Usys | REAL | IOD_SS2_TCP | 45027
SS2PMMPanelVirBActiveEnergyConsumed_kWh | REAL | IOD_SS2_TCP | 45029
SS2PMMPanelVirBActivePowerPhaseA_kW | REAL | IOD_SS2_TCP | 45031
SS2PMMPanelVirBActivePowerPhaseB_kW | REAL | IOD_SS2_TCP | 45033
SS2PMMPanelVirBActivePowerPhaseC_kW | REAL | IOD_SS2_TCP | 45035
SS2PMMPanelVirBAparentPowerPhaseA | REAL | IOD_SS2_TCP | 45037
SS2PMMPanelVirBAparentPowerPhaseB | REAL | IOD_SS2_TCP | 45039
SS2PMMPanelVirBAparentPowerPhaseC | REAL | IOD_SS2_TCP | 45041
SS2PMMPanelVirBAverageCurrent_A | REAL | IOD_SS2_TCP | 45043
SS2PMMPanelVirBAveragePhaseToNeutral_V | REAL | IOD_SS2_TCP | 45045
SS2PMMPanelVirBAveragePhaseToPhase_V | REAL | IOD_SS2_TCP | 45047
SS2PMMPanelVirBCurrentInPhaseA_A | REAL | IOD_SS2_TCP | 45049
SS2PMMPanelVirBCurrentInPhaseB_A | REAL | IOD_SS2_TCP | 45051
SS2PMMPanelVirBCurrentInPhaseC_A | REAL | IOD_SS2_TCP | 45053
SS2PMMPanelVirBFrequency_Hz | REAL | IOD_SS2_TCP | 45055
SS2PMMPanelVirBPowerFactorSys | REAL | IOD_SS2_TCP | 45057
SS2PMMPanelVirBReactiveEnergyConsumed_kVARh | REAL | IOD_SS2_TCP | 45059
SS2PMMPanelVirBReactivePowerPhaseA | REAL | IOD_SS2_TCP | 45061
SS2PMMPanelVirBReactivePowerPhaseB | REAL | IOD_SS2_TCP | 45063
SS2PMMPanelVirBReactivePowerPhaseC | REAL | IOD_SS2_TCP | 45065
SS2PMMPanelVirBTotalActivePower_kW | REAL | IOD_SS2_TCP | 45067
SS2PMMPanelVirBTotalAparentPower_kVA | REAL | IOD_SS2_TCP | 45069
SS2PMMPanelVirBTotalPowerFactor | REAL | IOD_SS2_TCP | 45071
SS2PMMPanelVirBTotalReactivePower_kVAR | REAL | IOD_SS2_TCP | 45073
SS2PMMPanelVirBVoltageBetweenPhaseAB_V | REAL | IOD_SS2_TCP | 45075
SS2PMMPanelVirBVoltageBetweenPhaseAN_V | REAL | IOD_SS2_TCP | 45077
SS2PMMPanelVirBVoltageBetweenPhaseBC_V | REAL | IOD_SS2_TCP | 45079
SS2PMMPanelVirBVoltageBetweenPhaseBN_V | REAL | IOD_SS2_TCP | 45081
SS2PMMPanelVirBVoltageBetweenPhaseCA_V | REAL | IOD_SS2_TCP | 45083
SS2PMMPanelVirBVoltageBetweenPhaseCN_V | REAL | IOD_SS2_TCP | 45085
SS2PMMPanelVoltageBetweenPhaseAB_V | REAL | IOD_SS2_TCP | 45087
SS2PMMPanelVoltageBetweenPhaseAN_V | REAL | IOD_SS2_TCP | 45089
SS2PMMPanelVoltageBetweenPhaseBC_V | REAL | IOD_SS2_TCP | 45091
SS2PMMPanelVoltageBetweenPhaseBN_V | REAL | IOD_SS2_TCP | 45093
SS2PMMPanelVoltageBetweenPhaseCA_V | REAL | IOD_SS2_TCP | 45095
SS2PMMPanelVoltageBetweenPhaseCN_V | REAL | IOD_SS2_TCP | 45097
SS2RocniVklopKlima1 | DIGITAL | IOD_SS2_TCP | 00363
SS2RocniVklopKlima2 | DIGITAL | IOD_SS2_TCP | 00364
SS2RocniVklopKlima3 | DIGITAL | IOD_SS2_TCP | 00365
SS2RocniVklopKlima4 | DIGITAL | IOD_SS2_TCP | 00366
SS2RocniVklopKlima5 | DIGITAL | IOD_SS2_TCP | 00367
SS2RocniVklopKlima6 | DIGITAL | IOD_SS2_TCP | 00368
SS2SinhronizacijaPanelOK | DIGITAL | IOD_SS2_TCP | 00369
SS2SinhronizirajCas_Panel | DIGITAL | IOD_SS2_TCP | 00370
SS2SKTemp1 | REAL | IOD_SS2_TCP | 45099 | 0 | 60 | 0 | 60 | °C | ####.#
SS2SKTemp2 | REAL | IOD_SS2_TCP | 45101 | 0 | 60 | 0 | 60 | °C | ####.#
SS2SKTemp3 | REAL | IOD_SS2_TCP | 45103 | 0 | 60 | 0 | 60 | °C | ####.#
SS2SKTemp4 | REAL | IOD_SS2_TCP | 45105 | 0 | 60 | 0 | 60 | °C | ####.#
SS2SkupneNapakeNaprav_Klima1 | DIGITAL | IOD_SS2_TCP | 00371
SS2SkupneNapakeNaprav_Klima2 | DIGITAL | IOD_SS2_TCP | 00372
SS2SkupneNapakeNaprav_Klima3 | DIGITAL | IOD_SS2_TCP | 00373
SS2SkupneNapakeNaprav_Klima4 | DIGITAL | IOD_SS2_TCP | 00374
SS2SkupneNapakeNaprav_Klima5 | DIGITAL | IOD_SS2_TCP | 00375
SS2SkupneNapakeNaprav_Klima6 | DIGITAL | IOD_SS2_TCP | 00376
SS2SkupneNapakeNaprav_Komunikacija | DIGITAL | IOD_SS2_TCP | 00377
SS2SkupneNapakeNaprav_PMM17VirBVirA | DIGITAL | IOD_SS2_TCP | 00378
SS2SkupneNapakeNaprav_PMM63VirBVirA | DIGITAL | IOD_SS2_TCP | 00379
SS2SkupneNapakeNaprav_TempVlaga | DIGITAL | IOD_SS2_TCP | 00380
SS2SKVlaga1 | REAL | IOD_SS2_TCP | 45107 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKVlaga2 | REAL | IOD_SS2_TCP | 45109 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKVlaga3 | REAL | IOD_SS2_TCP | 45111 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKVlaga4 | REAL | IOD_SS2_TCP | 45113 | 0 | 100 | 0 | 100 | % | ####.#
SS2StanjeKlimat2_1_Delovanje | DIGITAL | IOD_SS2_TCP | 00381
SS2StanjeKlimat2_2_Delovanje | DIGITAL | IOD_SS2_TCP | 00382
SS2StanjeKlimat2_3_Delovanje | DIGITAL | IOD_SS2_TCP | 00383
SS2StanjeKlimat2_4_Delovanje | DIGITAL | IOD_SS2_TCP | 00384
SS2StanjeKlimat2_5_Delovanje | DIGITAL | IOD_SS2_TCP | 00385
SS2StanjeKlimat2_6_Delovanje | DIGITAL | IOD_SS2_TCP | 00386
SS2StanjeUPSKrmOmara_BaterijskiNacin | DIGITAL | IOD_SS2_TCP | 00387
SS2StanjeUPSKrmOmara_Polnjenje | DIGITAL | IOD_SS2_TCP | 00388
SS2StUrZaPreklopKlim1_2 | INT | IOD_SS2_TCP | 40124
SS2StUrZaPreklopKlim3_4 | INT | IOD_SS2_TCP | 40125
SS2StUrZaPreklopKlim5_6 | INT | IOD_SS2_TCP | 40126
SS2TempZaAlarm1_2 | REAL | IOD_SS2_TCP | 45115 | 0 | 60 | 0 | 60 | °C | ####.#
SS2TempZaAlarm3_4 | REAL | IOD_SS2_TCP | 45117 | 0 | 60 | 0 | 60 | °C | ####.#
SS2TempZaAlarm5_6 | REAL | IOD_SS2_TCP | 45119 | 0 | 60 | 0 | 60 | °C | ####.#
SS2TempZaAlarmTIA1 | REAL | IOD_SS2_TCP | 45121 | 0 | 60 | 0 | 60 | °C | ####.#
SS2TempZaAlarmTIA2 | REAL | IOD_SS2_TCP | 45123 | 0 | 60 | 0 | 60 | °C | ####.#
SS2TempZaAlarmTIA3 | REAL | IOD_SS2_TCP | 45125 | 0 | 60 | 0 | 60 | °C | ####.#
SS2TempZaAlarmTIA4 | REAL | IOD_SS2_TCP | 45127 | 0 | 60 | 0 | 60 | °C | ####.#
SS2TempZaVklopObehKlim1_2 | REAL | IOD_SS2_TCP | 45129 | 0 | 60 | 0 | 60 | °C | ####.#
SS2TempZaVklopObehKlim3_4 | REAL | IOD_SS2_TCP | 45131 | 0 | 60 | 0 | 60 | °C | ####.#
SS2TempZaVklopObehKlim3_4TIA3 | REAL | IOD_SS2_TCP | 45133 | 0 | 60 | 0 | 60 | °C | ####.#
SS2TempZaVklopObehKlim5_6 | REAL | IOD_SS2_TCP | 45135 | 0 | 60 | 0 | 60 | °C | ####.#
SS2TempZaVklopObehKlim5_6TIA3 | REAL | IOD_SS2_TCP | 45137 | 0 | 60 | 0 | 60 | °C | ####.#
SS2UPSstatus_Prikaz_PanelSCADA | INT | IOD_SS2_TCP | 40127
SS2UserCurrentLevel | INT | IOD_SS2_TCP | 40128
SS2UserLoggedIn | DIGITAL | IOD_SS2_TCP | 00389
SS2UserName | STRING | IOD_SS2_TCP | 46061[15]
SS2XVH_AlarmOn | DIGITAL | IOD_SS2_TCP | 00390
SS2OmogociVseDogodke_DO | DIGITAL | IOD_SS2_disk | D559
SS2OmogociVseDogodke_DI | DIGITAL | IOD_SS2_disk | D560
SS2OmogociVseDogodke_COM | DIGITAL | IOD_SS2_disk | D567
SS2Klimat2_1_Vklop | DIGITAL | IOD_SS2_TCP | 00391
SS2Klimat2_2_Vklop | DIGITAL | IOD_SS2_TCP | 00392
SS2Klimat2_3_Vklop | DIGITAL | IOD_SS2_TCP | 00393
SS2Klimat2_4_Vklop | DIGITAL | IOD_SS2_TCP | 00394
SS2Klimat2_5_Vklop | DIGITAL | IOD_SS2_TCP | 00395
SS2Klimat2_6_Vklop | DIGITAL | IOD_SS2_TCP | 00396
SS2ErrorComKlima1Code0 | INT | IOD_SS2_TCP | 40129
SS2ErrorComKlima1Code10 | INT | IOD_SS2_TCP | 40130
SS2ErrorComKlima1Code11 | INT | IOD_SS2_TCP | 40131
SS2ErrorComKlima1Code12 | INT | IOD_SS2_TCP | 40132
SS2ErrorComKlima1Code13 | INT | IOD_SS2_TCP | 40133
SS2ErrorComKlima1Code14 | INT | IOD_SS2_TCP | 40134
SS2ErrorComKlima1Code15 | INT | IOD_SS2_TCP | 40135
SS2ErrorComKlima1Code1 | INT | IOD_SS2_TCP | 40136
SS2ErrorComKlima1Code2 | INT | IOD_SS2_TCP | 40137
SS2ErrorComKlima1Code3 | INT | IOD_SS2_TCP | 40138
SS2ErrorComKlima1Code4 | INT | IOD_SS2_TCP | 40139
SS2ErrorComKlima1Code5 | INT | IOD_SS2_TCP | 40140
SS2ErrorComKlima1Code6 | INT | IOD_SS2_TCP | 40141
SS2ErrorComKlima1Code7 | INT | IOD_SS2_TCP | 40142
SS2ErrorComKlima1Code8 | INT | IOD_SS2_TCP | 40143
SS2ErrorComKlima1Code9 | INT | IOD_SS2_TCP | 40144
SS2ErrorComKlima2Code0 | INT | IOD_SS2_TCP | 40145
SS2ErrorComKlima2Code10 | INT | IOD_SS2_TCP | 40146
SS2ErrorComKlima2Code11 | INT | IOD_SS2_TCP | 40147
SS2ErrorComKlima2Code12 | INT | IOD_SS2_TCP | 40148
SS2ErrorComKlima2Code13 | INT | IOD_SS2_TCP | 40149
SS2ErrorComKlima2Code14 | INT | IOD_SS2_TCP | 40150
SS2ErrorComKlima2Code15 | INT | IOD_SS2_TCP | 40151
SS2ErrorComKlima2Code1 | INT | IOD_SS2_TCP | 40152
SS2ErrorComKlima2Code2 | INT | IOD_SS2_TCP | 40153
SS2ErrorComKlima2Code3 | INT | IOD_SS2_TCP | 40154
SS2ErrorComKlima2Code4 | INT | IOD_SS2_TCP | 40155
SS2ErrorComKlima2Code5 | INT | IOD_SS2_TCP | 40156
SS2ErrorComKlima2Code6 | INT | IOD_SS2_TCP | 40157
SS2ErrorComKlima2Code7 | INT | IOD_SS2_TCP | 40158
SS2ErrorComKlima2Code8 | INT | IOD_SS2_TCP | 40159
SS2ErrorComKlima2Code9 | INT | IOD_SS2_TCP | 40160
SS2ErrorComKlima3Code0 | INT | IOD_SS2_TCP | 40161
SS2ErrorComKlima3Code10 | INT | IOD_SS2_TCP | 40162
SS2ErrorComKlima3Code11 | INT | IOD_SS2_TCP | 40163
SS2ErrorComKlima3Code12 | INT | IOD_SS2_TCP | 40164
SS2ErrorComKlima3Code13 | INT | IOD_SS2_TCP | 40165
SS2ErrorComKlima3Code14 | INT | IOD_SS2_TCP | 40166
SS2ErrorComKlima3Code15 | INT | IOD_SS2_TCP | 40167
SS2ErrorComKlima3Code1 | INT | IOD_SS2_TCP | 40168
SS2ErrorComKlima3Code2 | INT | IOD_SS2_TCP | 40169
SS2ErrorComKlima3Code3 | INT | IOD_SS2_TCP | 40170
SS2ErrorComKlima3Code4 | INT | IOD_SS2_TCP | 40171
SS2ErrorComKlima3Code5 | INT | IOD_SS2_TCP | 40172
SS2ErrorComKlima3Code6 | INT | IOD_SS2_TCP | 40173
SS2ErrorComKlima3Code7 | INT | IOD_SS2_TCP | 40174
SS2ErrorComKlima3Code8 | INT | IOD_SS2_TCP | 40175
SS2ErrorComKlima3Code9 | INT | IOD_SS2_TCP | 40176
SS2ErrorComKlima4Code0 | INT | IOD_SS2_TCP | 40177
SS2ErrorComKlima4Code10 | INT | IOD_SS2_TCP | 40178
SS2ErrorComKlima4Code11 | INT | IOD_SS2_TCP | 40179
SS2ErrorComKlima4Code12 | INT | IOD_SS2_TCP | 40180
SS2ErrorComKlima4Code13 | INT | IOD_SS2_TCP | 40181
SS2ErrorComKlima4Code14 | INT | IOD_SS2_TCP | 40182
SS2ErrorComKlima4Code15 | INT | IOD_SS2_TCP | 40183
SS2ErrorComKlima4Code1 | INT | IOD_SS2_TCP | 40184
SS2ErrorComKlima4Code2 | INT | IOD_SS2_TCP | 40185
SS2ErrorComKlima4Code3 | INT | IOD_SS2_TCP | 40186
SS2ErrorComKlima4Code4 | INT | IOD_SS2_TCP | 40187
SS2ErrorComKlima4Code5 | INT | IOD_SS2_TCP | 40188
SS2ErrorComKlima4Code6 | INT | IOD_SS2_TCP | 40189
SS2ErrorComKlima4Code7 | INT | IOD_SS2_TCP | 40190
SS2ErrorComKlima4Code8 | INT | IOD_SS2_TCP | 40191
SS2ErrorComKlima4Code9 | INT | IOD_SS2_TCP | 40192
SS2ErrorComKlima5Code0 | INT | IOD_SS2_TCP | 40193
SS2ErrorComKlima5Code10 | INT | IOD_SS2_TCP | 40194
SS2ErrorComKlima5Code11 | INT | IOD_SS2_TCP | 40195
SS2ErrorComKlima5Code12 | INT | IOD_SS2_TCP | 40196
SS2ErrorComKlima5Code13 | INT | IOD_SS2_TCP | 40197
SS2ErrorComKlima5Code14 | INT | IOD_SS2_TCP | 40198
SS2ErrorComKlima5Code15 | INT | IOD_SS2_TCP | 40199
SS2ErrorComKlima5Code1 | INT | IOD_SS2_TCP | 40200
SS2ErrorComKlima5Code2 | INT | IOD_SS2_TCP | 40201
SS2ErrorComKlima5Code3 | INT | IOD_SS2_TCP | 40202
SS2ErrorComKlima5Code4 | INT | IOD_SS2_TCP | 40203
SS2ErrorComKlima5Code5 | INT | IOD_SS2_TCP | 40204
SS2ErrorComKlima5Code6 | INT | IOD_SS2_TCP | 40205
SS2ErrorComKlima5Code7 | INT | IOD_SS2_TCP | 40206
SS2ErrorComKlima5Code8 | INT | IOD_SS2_TCP | 40207
SS2ErrorComKlima5Code9 | INT | IOD_SS2_TCP | 40208
SS2ErrorComKlima6Code0 | INT | IOD_SS2_TCP | 40209
SS2ErrorComKlima6Code10 | INT | IOD_SS2_TCP | 40210
SS2ErrorComKlima6Code11 | INT | IOD_SS2_TCP | 40211
SS2ErrorComKlima6Code12 | INT | IOD_SS2_TCP | 40212
SS2ErrorComKlima6Code13 | INT | IOD_SS2_TCP | 40213
SS2ErrorComKlima6Code14 | INT | IOD_SS2_TCP | 40214
SS2ErrorComKlima6Code15 | INT | IOD_SS2_TCP | 40215
SS2ErrorComKlima6Code1 | INT | IOD_SS2_TCP | 40216
SS2ErrorComKlima6Code2 | INT | IOD_SS2_TCP | 40217
SS2ErrorComKlima6Code3 | INT | IOD_SS2_TCP | 40218
SS2ErrorComKlima6Code4 | INT | IOD_SS2_TCP | 40219
SS2ErrorComKlima6Code5 | INT | IOD_SS2_TCP | 40220
SS2ErrorComKlima6Code6 | INT | IOD_SS2_TCP | 40221
SS2ErrorComKlima6Code7 | INT | IOD_SS2_TCP | 40222
SS2ErrorComKlima6Code8 | INT | IOD_SS2_TCP | 40223
SS2ErrorComKlima6Code9 | INT | IOD_SS2_TCP | 40224
SS2ErrorComPMM1Code0 | INT | IOD_SS2_TCP | 40225
SS2ErrorComPMM1Code10 | INT | IOD_SS2_TCP | 40226
SS2ErrorComPMM1Code11 | INT | IOD_SS2_TCP | 40227
SS2ErrorComPMM1Code12 | INT | IOD_SS2_TCP | 40228
SS2ErrorComPMM1Code13 | INT | IOD_SS2_TCP | 40229
SS2ErrorComPMM1Code14 | INT | IOD_SS2_TCP | 40230
SS2ErrorComPMM1Code15 | INT | IOD_SS2_TCP | 40231
SS2ErrorComPMM1Code1 | INT | IOD_SS2_TCP | 40232
SS2ErrorComPMM1Code2 | INT | IOD_SS2_TCP | 40233
SS2ErrorComPMM1Code3 | INT | IOD_SS2_TCP | 40234
SS2ErrorComPMM1Code4 | INT | IOD_SS2_TCP | 40235
SS2ErrorComPMM1Code5 | INT | IOD_SS2_TCP | 40236
SS2ErrorComPMM1Code6 | INT | IOD_SS2_TCP | 40237
SS2ErrorComPMM1Code7 | INT | IOD_SS2_TCP | 40238
SS2ErrorComPMM1Code8 | INT | IOD_SS2_TCP | 40239
SS2ErrorComPMM1Code9 | INT | IOD_SS2_TCP | 40240
SS2ErrorComPMM2Code0 | INT | IOD_SS2_TCP | 40241
SS2ErrorComPMM2Code10 | INT | IOD_SS2_TCP | 40242
SS2ErrorComPMM2Code11 | INT | IOD_SS2_TCP | 40243
SS2ErrorComPMM2Code12 | INT | IOD_SS2_TCP | 40244
SS2ErrorComPMM2Code13 | INT | IOD_SS2_TCP | 40245
SS2ErrorComPMM2Code14 | INT | IOD_SS2_TCP | 40246
SS2ErrorComPMM2Code15 | INT | IOD_SS2_TCP | 40247
SS2ErrorComPMM2Code1 | INT | IOD_SS2_TCP | 40248
SS2ErrorComPMM2Code2 | INT | IOD_SS2_TCP | 40249
SS2ErrorComPMM2Code3 | INT | IOD_SS2_TCP | 40250
SS2ErrorComPMM2Code4 | INT | IOD_SS2_TCP | 40251
SS2ErrorComPMM2Code5 | INT | IOD_SS2_TCP | 40252
SS2ErrorComPMM2Code6 | INT | IOD_SS2_TCP | 40253
SS2ErrorComPMM2Code7 | INT | IOD_SS2_TCP | 40254
SS2ErrorComPMM2Code8 | INT | IOD_SS2_TCP | 40255
SS2ErrorComPMM2Code9 | INT | IOD_SS2_TCP | 40256
SS2PricetekSMSAlarmov1 | INT | IOD_SS2_disk | I60
SS2KonecSMSAlarmov1 | INT | IOD_SS2_disk | I61
SS2PricetekSMSAlarmov2 | INT | IOD_SS2_disk | I62
SS2KonecSMSAlarmov2 | INT | IOD_SS2_disk | I63
SS2PricetekSMSAlarmov3 | INT | IOD_SS2_disk | I64
SS2KonecSMSAlarmov3 | INT | IOD_SS2_disk | I65
SS2AlarmSinhronizacijaNOK_Omogoci | DIGITAL | IOD_SS2_disk | D3965
SS2ErrCommScada2 | DIGITAL | IOD_SS2_TCP | 00397
SS2ComSCADA2 | DIGITAL | IOD_SS2_TCP | 00398
SS2ErrCommScada_Omogoci2 | DIGITAL | IOD_SS2_disk | D3968
SS2Server_A_Izpad | DIGITAL | IOD_SS2_disk | D3969
SS2Server_B_Izpad | DIGITAL | IOD_SS2_disk | D3970
SS2ComSCADA_stevec3 | INT | IOD_SS2_mem | I3972
SS2ComSCADA_stevec | INT | IOD_SS2_mem | I3974
SS2ComSCADA3 | DIGITAL | IOD_SS2_TCP | 00399
SS2kom_nast_cas_izpada | INT | IOD_SS2_TCP | 40257
SS2AlarmSKTemp5_Previsoka | DIGITAL | IOD_SS2_TCP | 00400
SS2AlarmSKTemp6_Previsoka | DIGITAL | IOD_SS2_TCP | 00401
SS2AlarmTempTIA5Previsoka | DIGITAL | IOD_SS2_TCP | 00402
SS2AlarmTempTIA6Previsoka | DIGITAL | IOD_SS2_TCP | 00403
SS2NapakaSenzorTemp5 | DIGITAL | IOD_SS2_TCP | 00404
SS2NapakaSenzorTemp6 | DIGITAL | IOD_SS2_TCP | 00405
SS2NapakaSenzorVlaga5 | DIGITAL | IOD_SS2_TCP | 00406
SS2NapakaSenzorVlaga6 | DIGITAL | IOD_SS2_TCP | 00407
SS2SKTemp5 | REAL | IOD_SS2_TCP | 45139 | 0 | 60 | 0 | 60 | °C | ####.#
SS2SKTemp6 | REAL | IOD_SS2_TCP | 45141 | 0 | 60 | 0 | 60 | °C | ####.#
SS2SKVlaga5 | REAL | IOD_SS2_TCP | 45143 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKVlaga6 | REAL | IOD_SS2_TCP | 45145 | 0 | 100 | 0 | 100 | % | ####.#
SS2TempZaAlarmTIA5 | REAL | IOD_SS2_TCP | 45147 | 0 | 60 | 0 | 60 | °C | ####.#
SS2TempZaAlarmTIA6 | REAL | IOD_SS2_TCP | 45149 | 0 | 60 | 0 | 60 | °C | ####.#
SS2PrikazNastTemp5 | DIGITAL | IOD_SS2_disk | D5000
SS2PrikazNastTemp6 | DIGITAL | IOD_SS2_disk | D5001
SS2NapakaSenzorTemp5_Omogoci | DIGITAL | IOD_SS2_disk | D5002
SS2NapakaSenzorTemp6_Omogoci | DIGITAL | IOD_SS2_disk | D5003
SS2NapakaSenzorVlaga5_Omogoci | DIGITAL | IOD_SS2_disk | D5004
SS2NapakaSenzorVlaga6_Omogoci | DIGITAL | IOD_SS2_disk | D5005
SS2SKTemp5_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R17 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKTemp5_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R18 | 0 | 60 | 0 | 60 | °C | ####.#
SS2SKTemp5_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D5006
SS2SKTemp5_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D5007
SS2SKVlaga5_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R19 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKVlaga5_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R20 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKVlaga5_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D5008
SS2SKVlaga5_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D5009
SS2SKTemp6_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R21 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKTemp6_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R22 | 0 | 60 | 0 | 60 | °C | ####.#
SS2SKTemp6_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D5010
SS2SKTemp6_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D5011
SS2SKVlaga6_Opozorilo_Zgornja_Meja | REAL | IOD_SS2_disk | R23 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKVlaga6_Alarm_Zgornja_Meja | REAL | IOD_SS2_disk | R24 | 0 | 100 | 0 | 100 | % | ####.#
SS2SKVlaga6_Opozorilo_Omogoci | DIGITAL | IOD_SS2_disk | D5012
SS2SKVlaga6_Alarm_Omogoci | DIGITAL | IOD_SS2_disk | D5013
SS2AlarmTempTIA5Previsoka_Omogoci | DIGITAL | IOD_SS2_disk | D5014
SS2AlarmTempTIA6Previsoka_Omogoci | DIGITAL | IOD_SS2_disk | D5015
SS2SKTempServSoba1Povpr | REAL | IOD_SS2_TCP | 45151 | 0 | 60 | 0 | 60 | °C | ####.#
SS2SKTempServSoba2Povpr | REAL | IOD_SS2_TCP | 45153 | 0 | 60 | 0 | 60 | °C | ####.#
SS2TempZaAlarmTIA235 | REAL | IOD_SS2_TCP | 45155 | 0 | 60 | 0 | 60 | °C | ####.#
SS2TempZaAlarmTIA46 | REAL | IOD_SS2_TCP | 45157 | 0 | 60 | 0 | 60 | °C | ####.#
SS2AlarmTempTIA235Previsoka | DIGITAL | IOD_SS2_TCP | 00408
SS2AlarmTempTIA46Previsoka | DIGITAL | IOD_SS2_TCP | 00409
SS2AlarmTempTIA235Previsoka_Omogoci | DIGITAL | IOD_SS2_disk | D5016
SS2AlarmTempTIA46Previsoka_Omogoci | DIGITAL | IOD_SS2_disk | D5017

## XSoft
mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Write_BOOL(FC) | mod_Write_Word(FC) | mod_Write_Word(FC) | mod_Write_dWord(FC) | mod_Write_dWord(FC) | mod_Write_String(FC)
(*Branje BOOL*) | (*Branje INT*) | (*Branje UINT*) | (*Branje LONG*) | (*Branje REAL*) | (*Branje STRING*) | (*Pisanje BOOL*) | (*Pisanje INT*) | (*Pisanje UINT*) | (*Pisanje LONG*) | (*Pisanje REAL*) | (*Pisanje STRING*)
(**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**)
mind_bool[0]:=AlarmKlimat2_1_Napaka; | mind[0]:=DatumCas.Dan; |  |  | Read_Real(rVar:=AktualniSetPointTemp1_2,lo:=4000,hi:=4001); | Read_String(sVar:=Date_Time[0],start:=6000); | 0:AlarmKlimat2_1_Napaka:=Bit_0; | 0:DatumCas.Dan:=Byte_0; |  |  | 4001:AktualniSetPointTemp1_2:=Real_0; | 6000:Date_Time[0]:=String_0;
mind_bool[1]:=AlarmKlimat2_2_Napaka; | mind[1]:=DatumCas.Leto; |  |  | Read_Real(rVar:=AktualniSetPointTemp3_4,lo:=4002,hi:=4003); | Read_String(sVar:=Date_Time[1],start:=6015); | 1:AlarmKlimat2_2_Napaka:=Bit_0; | 1:DatumCas.Leto:=Byte_0; |  |  | 4003:AktualniSetPointTemp3_4:=Real_0; | 6015:Date_Time[1]:=String_0;
mind_bool[2]:=AlarmKlimat2_3_Napaka; | mind[2]:=DatumCas.Leto2; |  |  | Read_Real(rVar:=AktualniSetPointTemp5_6,lo:=4004,hi:=4005); | Read_String(sVar:=Date_Time[2],start:=6030); | 2:AlarmKlimat2_3_Napaka:=Bit_0; | 2:DatumCas.Leto2:=Word_01; |  |  | 4005:AktualniSetPointTemp5_6:=Real_0; | 6030:Date_Time[2]:=String_0;
mind_bool[3]:=AlarmKlimat2_4_Napaka; | mind[3]:=DatumCas.Mesec; |  |  | Read_Real(rVar:=Klima1ure,lo:=4006,hi:=4007); | Read_String(sVar:=Date_Time[3],start:=6045); | 3:AlarmKlimat2_4_Napaka:=Bit_0; | 3:DatumCas.Mesec:=Byte_0; |  |  | 4007:Klima1ure:=Real_0; | 6045:Date_Time[3]:=String_0;
mind_bool[4]:=AlarmKlimat2_5_Napaka; | mind[4]:=DatumCas.Minuta; |  |  | Read_Real(rVar:=Klima2ure,lo:=4008,hi:=4009); | Read_String(sVar:=UserName,start:=6060); | 4:AlarmKlimat2_5_Napaka:=Bit_0; | 4:DatumCas.Minuta:=Byte_0; |  |  | 4009:Klima2ure:=Real_0; | 6060:UserName:=String_0;
mind_bool[5]:=AlarmKlimat2_6_Napaka; | mind[5]:=DatumCas.Sekunda; |  |  | Read_Real(rVar:=Klima3ure,lo:=4010,hi:=4011); |  | 5:AlarmKlimat2_6_Napaka:=Bit_0; | 5:DatumCas.Sekunda:=Byte_0; |  |  | 4011:Klima3ure:=Real_0;
mind_bool[6]:=AlarmLAH1RazlitjeVode; | mind[6]:=DatumCas.Ura; |  |  | Read_Real(rVar:=Klima4ure,lo:=4012,hi:=4013); |  | 6:AlarmLAH1RazlitjeVode:=Bit_0; | 6:DatumCas.Ura:=Byte_0; |  |  | 4013:Klima4ure:=Real_0;
mind_bool[7]:=AlarmLAH2RazlitjeVode; | mind[7]:=ErrorComKlima[1].Status; |  |  | Read_Real(rVar:=Klima5ure,lo:=4014,hi:=4015); |  | 7:AlarmLAH2RazlitjeVode:=Bit_0; | 7:ErrorComKlima[1].Status:=Word_01; |  |  | 4015:Klima5ure:=Real_0;
mind_bool[8]:=AlarmLAH3RazlitjeVode; | mind[8]:=ErrorComKlima[2].Status; |  |  | Read_Real(rVar:=Klima6ure,lo:=4016,hi:=4017); |  | 8:AlarmLAH3RazlitjeVode:=Bit_0; | 8:ErrorComKlima[2].Status:=Word_01; |  |  | 4017:Klima6ure:=Real_0;
mind_bool[9]:=AlarmPMM2x17nad80[10]; | mind[9]:=ErrorComKlima[3].Status; |  |  | Read_Real(rVar:=Klima[1].NastMaxTemp,lo:=4018,hi:=4019); |  | 9:AlarmPMM2x17nad80[10]:=Bit_0; | 9:ErrorComKlima[3].Status:=Word_01; |  |  | 4019:Klima[1].NastMaxTemp:=Real_0;
mind_bool[10]:=AlarmPMM2x17nad80[11]; | mind[10]:=ErrorComKlima[4].Status; |  |  | Read_Real(rVar:=Klima[1].NastMaxVlaznost,lo:=4020,hi:=4021); |  | 10:AlarmPMM2x17nad80[11]:=Bit_0; | 10:ErrorComKlima[4].Status:=Word_01; |  |  | 4021:Klima[1].NastMaxVlaznost:=Real_0;
mind_bool[11]:=AlarmPMM2x17nad80[12]; | mind[11]:=ErrorComKlima[5].Status; |  |  | Read_Real(rVar:=Klima[1].NastMinTemp,lo:=4022,hi:=4023); |  | 11:AlarmPMM2x17nad80[12]:=Bit_0; | 11:ErrorComKlima[5].Status:=Word_01; |  |  | 4023:Klima[1].NastMinTemp:=Real_0;
mind_bool[12]:=AlarmPMM2x17nad80[13]; | mind[12]:=ErrorComKlima[6].Status; |  |  | Read_Real(rVar:=Klima[1].NastMinVlaznost,lo:=4024,hi:=4025); |  | 12:AlarmPMM2x17nad80[13]:=Bit_0; | 12:ErrorComKlima[6].Status:=Word_01; |  |  | 4025:Klima[1].NastMinVlaznost:=Real_0;
mind_bool[13]:=AlarmPMM2x17nad80[14]; | mind[13]:=ErrorComPMM[1].Status; |  |  | Read_Real(rVar:=Klima[1].NastTempProstora,lo:=4026,hi:=4027); |  | 13:AlarmPMM2x17nad80[14]:=Bit_0; | 13:ErrorComPMM[1].Status:=Word_01; |  |  | 4027:Klima[1].NastTempProstora:=Real_0;
mind_bool[14]:=AlarmPMM2x17nad80[15]; | mind[14]:=ErrorComPMM[2].Status; |  |  | Read_Real(rVar:=Klima[1].NastVlaznost,lo:=4028,hi:=4029); |  | 14:AlarmPMM2x17nad80[15]:=Bit_0; | 14:ErrorComPMM[2].Status:=Word_01; |  |  | 4029:Klima[1].NastVlaznost:=Real_0;
mind_bool[15]:=AlarmPMM2x17nad80[16]; | mind[15]:=Klima[1].GrelecStatus; |  |  | Read_Real(rVar:=Klima[1].ObratUreFilter,lo:=4030,hi:=4031); |  | 15:AlarmPMM2x17nad80[16]:=Bit_0; | 15:Klima[1].GrelecStatus:=Byte_0; |  |  | 4031:Klima[1].ObratUreFilter:=Real_0;
mind_bool[16]:=AlarmPMM2x17nad80[17]; | mind[16]:=Klima[1].IzhodniVentStatus; |  |  | Read_Real(rVar:=Klima[1].ObratUreKompresor1,lo:=4032,hi:=4033); |  | 16:AlarmPMM2x17nad80[17]:=Bit_0; | 16:Klima[1].IzhodniVentStatus:=Byte_0; |  |  | 4033:Klima[1].ObratUreKompresor1:=Real_0;
mind_bool[17]:=AlarmPMM2x17nad80[18]; | mind[17]:=Klima[1].KompresorStatus; |  |  | Read_Real(rVar:=Klima[1].ObratUreKompresor2,lo:=4034,hi:=4035); |  | 17:AlarmPMM2x17nad80[18]:=Bit_0; | 17:Klima[1].KompresorStatus:=Byte_0; |  |  | 4035:Klima[1].ObratUreKompresor2:=Real_0;
mind_bool[18]:=AlarmPMM2x17nad80[19]; | mind[18]:=Klima[1].NacinRazvlaz; |  |  | Read_Real(rVar:=Klima[1].ObratUreVent,lo:=4036,hi:=4037); |  | 18:AlarmPMM2x17nad80[19]:=Bit_0; | 18:Klima[1].NacinRazvlaz:=Word_01; |  |  | 4037:Klima[1].ObratUreVent:=Real_0;
mind_bool[19]:=AlarmPMM2x17nad80[1]; | mind[19]:=Klima[1].VlazilecStatus; |  |  | Read_Real(rVar:=Klima[1].TemperaturaProstora,lo:=4038,hi:=4039); |  | 19:AlarmPMM2x17nad80[1]:=Bit_0; | 19:Klima[1].VlazilecStatus:=Byte_0; |  |  | 4039:Klima[1].TemperaturaProstora:=Real_0;
mind_bool[20]:=AlarmPMM2x17nad80[20]; | mind[20]:=Klima[2].GrelecStatus; |  |  | Read_Real(rVar:=Klima[1].VlaznostProstora,lo:=4040,hi:=4041); |  | 20:AlarmPMM2x17nad80[20]:=Bit_0; | 20:Klima[2].GrelecStatus:=Byte_0; |  |  | 4041:Klima[1].VlaznostProstora:=Real_0;
mind_bool[21]:=AlarmPMM2x17nad80[21]; | mind[21]:=Klima[2].IzhodniVentStatus; |  |  | Read_Real(rVar:=Klima[2].NastMaxTemp,lo:=4042,hi:=4043); |  | 21:AlarmPMM2x17nad80[21]:=Bit_0; | 21:Klima[2].IzhodniVentStatus:=Byte_0; |  |  | 4043:Klima[2].NastMaxTemp:=Real_0;
mind_bool[22]:=AlarmPMM2x17nad80[22]; | mind[22]:=Klima[2].KompresorStatus; |  |  | Read_Real(rVar:=Klima[2].NastMaxVlaznost,lo:=4044,hi:=4045); |  | 22:AlarmPMM2x17nad80[22]:=Bit_0; | 22:Klima[2].KompresorStatus:=Byte_0; |  |  | 4045:Klima[2].NastMaxVlaznost:=Real_0;
mind_bool[23]:=AlarmPMM2x17nad80[23]; | mind[23]:=Klima[2].NacinRazvlaz; |  |  | Read_Real(rVar:=Klima[2].NastMinTemp,lo:=4046,hi:=4047); |  | 23:AlarmPMM2x17nad80[23]:=Bit_0; | 23:Klima[2].NacinRazvlaz:=Word_01; |  |  | 4047:Klima[2].NastMinTemp:=Real_0;
mind_bool[24]:=AlarmPMM2x17nad80[24]; | mind[24]:=Klima[2].VlazilecStatus; |  |  | Read_Real(rVar:=Klima[2].NastMinVlaznost,lo:=4048,hi:=4049); |  | 24:AlarmPMM2x17nad80[24]:=Bit_0; | 24:Klima[2].VlazilecStatus:=Byte_0; |  |  | 4049:Klima[2].NastMinVlaznost:=Real_0;
mind_bool[25]:=AlarmPMM2x17nad80[25]; | mind[25]:=Klima[3].GrelecStatus; |  |  | Read_Real(rVar:=Klima[2].NastTempProstora,lo:=4050,hi:=4051); |  | 25:AlarmPMM2x17nad80[25]:=Bit_0; | 25:Klima[3].GrelecStatus:=Byte_0; |  |  | 4051:Klima[2].NastTempProstora:=Real_0;
mind_bool[26]:=AlarmPMM2x17nad80[26]; | mind[26]:=Klima[3].IzhodniVentStatus; |  |  | Read_Real(rVar:=Klima[2].NastVlaznost,lo:=4052,hi:=4053); |  | 26:AlarmPMM2x17nad80[26]:=Bit_0; | 26:Klima[3].IzhodniVentStatus:=Byte_0; |  |  | 4053:Klima[2].NastVlaznost:=Real_0;
mind_bool[27]:=AlarmPMM2x17nad80[27]; | mind[27]:=Klima[3].KompresorStatus; |  |  | Read_Real(rVar:=Klima[2].ObratUreFilter,lo:=4054,hi:=4055); |  | 27:AlarmPMM2x17nad80[27]:=Bit_0; | 27:Klima[3].KompresorStatus:=Byte_0; |  |  | 4055:Klima[2].ObratUreFilter:=Real_0;
mind_bool[28]:=AlarmPMM2x17nad80[28]; | mind[28]:=Klima[3].NacinRazvlaz; |  |  | Read_Real(rVar:=Klima[2].ObratUreKompresor1,lo:=4056,hi:=4057); |  | 28:AlarmPMM2x17nad80[28]:=Bit_0; | 28:Klima[3].NacinRazvlaz:=Word_01; |  |  | 4057:Klima[2].ObratUreKompresor1:=Real_0;
mind_bool[29]:=AlarmPMM2x17nad80[29]; | mind[29]:=Klima[3].VlazilecStatus; |  |  | Read_Real(rVar:=Klima[2].ObratUreKompresor2,lo:=4058,hi:=4059); |  | 29:AlarmPMM2x17nad80[29]:=Bit_0; | 29:Klima[3].VlazilecStatus:=Byte_0; |  |  | 4059:Klima[2].ObratUreKompresor2:=Real_0;
mind_bool[30]:=AlarmPMM2x17nad80[2]; | mind[30]:=Klima[4].GrelecStatus; |  |  | Read_Real(rVar:=Klima[2].ObratUreVent,lo:=4060,hi:=4061); |  | 30:AlarmPMM2x17nad80[2]:=Bit_0; | 30:Klima[4].GrelecStatus:=Byte_0; |  |  | 4061:Klima[2].ObratUreVent:=Real_0;
mind_bool[31]:=AlarmPMM2x17nad80[30]; | mind[31]:=Klima[4].IzhodniVentStatus; |  |  | Read_Real(rVar:=Klima[2].TemperaturaProstora,lo:=4062,hi:=4063); |  | 31:AlarmPMM2x17nad80[30]:=Bit_0; | 31:Klima[4].IzhodniVentStatus:=Byte_0; |  |  | 4063:Klima[2].TemperaturaProstora:=Real_0;
mind_bool[32]:=AlarmPMM2x17nad80[31]; | mind[32]:=Klima[4].KompresorStatus; |  |  | Read_Real(rVar:=Klima[2].VlaznostProstora,lo:=4064,hi:=4065); |  | 32:AlarmPMM2x17nad80[31]:=Bit_0; | 32:Klima[4].KompresorStatus:=Byte_0; |  |  | 4065:Klima[2].VlaznostProstora:=Real_0;
mind_bool[33]:=AlarmPMM2x17nad80[32]; | mind[33]:=Klima[4].NacinRazvlaz; |  |  | Read_Real(rVar:=Klima[3].NastMaxTemp,lo:=4066,hi:=4067); |  | 33:AlarmPMM2x17nad80[32]:=Bit_0; | 33:Klima[4].NacinRazvlaz:=Word_01; |  |  | 4067:Klima[3].NastMaxTemp:=Real_0;
mind_bool[34]:=AlarmPMM2x17nad80[33]; | mind[34]:=Klima[4].VlazilecStatus; |  |  | Read_Real(rVar:=Klima[3].NastMaxVlaznost,lo:=4068,hi:=4069); |  | 34:AlarmPMM2x17nad80[33]:=Bit_0; | 34:Klima[4].VlazilecStatus:=Byte_0; |  |  | 4069:Klima[3].NastMaxVlaznost:=Real_0;
mind_bool[35]:=AlarmPMM2x17nad80[34]; | mind[35]:=Klima[5].GrelecStatus; |  |  | Read_Real(rVar:=Klima[3].NastMinTemp,lo:=4070,hi:=4071); |  | 35:AlarmPMM2x17nad80[34]:=Bit_0; | 35:Klima[5].GrelecStatus:=Byte_0; |  |  | 4071:Klima[3].NastMinTemp:=Real_0;
mind_bool[36]:=AlarmPMM2x17nad80[35]; | mind[36]:=Klima[5].IzhodniVentStatus; |  |  | Read_Real(rVar:=Klima[3].NastMinVlaznost,lo:=4072,hi:=4073); |  | 36:AlarmPMM2x17nad80[35]:=Bit_0; | 36:Klima[5].IzhodniVentStatus:=Byte_0; |  |  | 4073:Klima[3].NastMinVlaznost:=Real_0;
mind_bool[37]:=AlarmPMM2x17nad80[36]; | mind[37]:=Klima[5].KompresorStatus; |  |  | Read_Real(rVar:=Klima[3].NastTempProstora,lo:=4074,hi:=4075); |  | 37:AlarmPMM2x17nad80[36]:=Bit_0; | 37:Klima[5].KompresorStatus:=Byte_0; |  |  | 4075:Klima[3].NastTempProstora:=Real_0;
mind_bool[38]:=AlarmPMM2x17nad80[37]; | mind[38]:=Klima[5].NacinRazvlaz; |  |  | Read_Real(rVar:=Klima[3].NastVlaznost,lo:=4076,hi:=4077); |  | 38:AlarmPMM2x17nad80[37]:=Bit_0; | 38:Klima[5].NacinRazvlaz:=Word_01; |  |  | 4077:Klima[3].NastVlaznost:=Real_0;
mind_bool[39]:=AlarmPMM2x17nad80[38]; | mind[39]:=Klima[5].VlazilecStatus; |  |  | Read_Real(rVar:=Klima[3].ObratUreFilter,lo:=4078,hi:=4079); |  | 39:AlarmPMM2x17nad80[38]:=Bit_0; | 39:Klima[5].VlazilecStatus:=Byte_0; |  |  | 4079:Klima[3].ObratUreFilter:=Real_0;
mind_bool[40]:=AlarmPMM2x17nad80[39]; | mind[40]:=Klima[6].GrelecStatus; |  |  | Read_Real(rVar:=Klima[3].ObratUreKompresor1,lo:=4080,hi:=4081); |  | 40:AlarmPMM2x17nad80[39]:=Bit_0; | 40:Klima[6].GrelecStatus:=Byte_0; |  |  | 4081:Klima[3].ObratUreKompresor1:=Real_0;
mind_bool[41]:=AlarmPMM2x17nad80[3]; | mind[41]:=Klima[6].IzhodniVentStatus; |  |  | Read_Real(rVar:=Klima[3].ObratUreKompresor2,lo:=4082,hi:=4083); |  | 41:AlarmPMM2x17nad80[3]:=Bit_0; | 41:Klima[6].IzhodniVentStatus:=Byte_0; |  |  | 4083:Klima[3].ObratUreKompresor2:=Real_0;
mind_bool[42]:=AlarmPMM2x17nad80[40]; | mind[42]:=Klima[6].KompresorStatus; |  |  | Read_Real(rVar:=Klima[3].ObratUreVent,lo:=4084,hi:=4085); |  | 42:AlarmPMM2x17nad80[40]:=Bit_0; | 42:Klima[6].KompresorStatus:=Byte_0; |  |  | 4085:Klima[3].ObratUreVent:=Real_0;
mind_bool[43]:=AlarmPMM2x17nad80[41]; | mind[43]:=Klima[6].NacinRazvlaz; |  |  | Read_Real(rVar:=Klima[3].TemperaturaProstora,lo:=4086,hi:=4087); |  | 43:AlarmPMM2x17nad80[41]:=Bit_0; | 43:Klima[6].NacinRazvlaz:=Word_01; |  |  | 4087:Klima[3].TemperaturaProstora:=Real_0;
mind_bool[44]:=AlarmPMM2x17nad80[42]; | mind[44]:=Klima[6].VlazilecStatus; |  |  | Read_Real(rVar:=Klima[3].VlaznostProstora,lo:=4088,hi:=4089); |  | 44:AlarmPMM2x17nad80[42]:=Bit_0; | 44:Klima[6].VlazilecStatus:=Byte_0; |  |  | 4089:Klima[3].VlaznostProstora:=Real_0;
mind_bool[45]:=AlarmPMM2x17nad80[4]; | mind[45]:=OznakeFaz[10]; |  |  | Read_Real(rVar:=Klima[4].NastMaxTemp,lo:=4090,hi:=4091); |  | 45:AlarmPMM2x17nad80[4]:=Bit_0; | 45:OznakeFaz[10]:=Byte_0; |  |  | 4091:Klima[4].NastMaxTemp:=Real_0;
mind_bool[46]:=AlarmPMM2x17nad80[5]; | mind[46]:=OznakeFaz[11]; |  |  | Read_Real(rVar:=Klima[4].NastMaxVlaznost,lo:=4092,hi:=4093); |  | 46:AlarmPMM2x17nad80[5]:=Bit_0; | 46:OznakeFaz[11]:=Byte_0; |  |  | 4093:Klima[4].NastMaxVlaznost:=Real_0;
mind_bool[47]:=AlarmPMM2x17nad80[6]; | mind[47]:=OznakeFaz[12]; |  |  | Read_Real(rVar:=Klima[4].NastMinTemp,lo:=4094,hi:=4095); |  | 47:AlarmPMM2x17nad80[6]:=Bit_0; | 47:OznakeFaz[12]:=Byte_0; |  |  | 4095:Klima[4].NastMinTemp:=Real_0;
mind_bool[48]:=AlarmPMM2x17nad80[7]; | mind[48]:=OznakeFaz[13]; |  |  | Read_Real(rVar:=Klima[4].NastMinVlaznost,lo:=4096,hi:=4097); |  | 48:AlarmPMM2x17nad80[7]:=Bit_0; | 48:OznakeFaz[13]:=Byte_0; |  |  | 4097:Klima[4].NastMinVlaznost:=Real_0;
mind_bool[49]:=AlarmPMM2x17nad80[8]; | mind[49]:=OznakeFaz[14]; |  |  | Read_Real(rVar:=Klima[4].NastTempProstora,lo:=4098,hi:=4099); |  | 49:AlarmPMM2x17nad80[8]:=Bit_0; | 49:OznakeFaz[14]:=Byte_0; |  |  | 4099:Klima[4].NastTempProstora:=Real_0;
mind_bool[50]:=AlarmPMM2x17nad80[9]; | mind[50]:=OznakeFaz[1]; |  |  | Read_Real(rVar:=Klima[4].NastVlaznost,lo:=4100,hi:=4101); |  | 50:AlarmPMM2x17nad80[9]:=Bit_0; | 50:OznakeFaz[1]:=Byte_0; |  |  | 4101:Klima[4].NastVlaznost:=Real_0;
mind_bool[51]:=AlarmSinhronizacijaNOK; | mind[51]:=OznakeFaz[2]; |  |  | Read_Real(rVar:=Klima[4].ObratUreFilter,lo:=4102,hi:=4103); |  | 51:AlarmSinhronizacijaNOK:=Bit_0; | 51:OznakeFaz[2]:=Byte_0; |  |  | 4103:Klima[4].ObratUreFilter:=Real_0;
mind_bool[52]:=AlarmSKTemp1_Previsoka; | mind[52]:=OznakeFaz[3]; |  |  | Read_Real(rVar:=Klima[4].ObratUreKompresor1,lo:=4104,hi:=4105); |  | 52:AlarmSKTemp1_Previsoka:=Bit_0; | 52:OznakeFaz[3]:=Byte_0; |  |  | 4105:Klima[4].ObratUreKompresor1:=Real_0;
mind_bool[53]:=AlarmSKTemp2_Previsoka; | mind[53]:=OznakeFaz[4]; |  |  | Read_Real(rVar:=Klima[4].ObratUreKompresor2,lo:=4106,hi:=4107); |  | 53:AlarmSKTemp2_Previsoka:=Bit_0; | 53:OznakeFaz[4]:=Byte_0; |  |  | 4107:Klima[4].ObratUreKompresor2:=Real_0;
mind_bool[54]:=AlarmSKTemp3_Previsoka; | mind[54]:=OznakeFaz[5]; |  |  | Read_Real(rVar:=Klima[4].ObratUreVent,lo:=4108,hi:=4109); |  | 54:AlarmSKTemp3_Previsoka:=Bit_0; | 54:OznakeFaz[5]:=Byte_0; |  |  | 4109:Klima[4].ObratUreVent:=Real_0;
mind_bool[55]:=AlarmSKTemp4_Previsoka; | mind[55]:=OznakeFaz[6]; |  |  | Read_Real(rVar:=Klima[4].TemperaturaProstora,lo:=4110,hi:=4111); |  | 55:AlarmSKTemp4_Previsoka:=Bit_0; | 55:OznakeFaz[6]:=Byte_0; |  |  | 4111:Klima[4].TemperaturaProstora:=Real_0;
mind_bool[56]:=AlarmTempTIA1Previsoka; | mind[56]:=OznakeFaz[7]; |  |  | Read_Real(rVar:=Klima[4].VlaznostProstora,lo:=4112,hi:=4113); |  | 56:AlarmTempTIA1Previsoka:=Bit_0; | 56:OznakeFaz[7]:=Byte_0; |  |  | 4113:Klima[4].VlaznostProstora:=Real_0;
mind_bool[57]:=AlarmTempTIA2Previsoka; | mind[57]:=OznakeFaz[8]; |  |  | Read_Real(rVar:=Klima[5].NastMaxTemp,lo:=4114,hi:=4115); |  | 57:AlarmTempTIA2Previsoka:=Bit_0; | 57:OznakeFaz[8]:=Byte_0; |  |  | 4115:Klima[5].NastMaxTemp:=Real_0;
mind_bool[58]:=AlarmTempTIA3Previsoka; | mind[58]:=OznakeFaz[9]; |  |  | Read_Real(rVar:=Klima[5].NastMaxVlaznost,lo:=4116,hi:=4117); |  | 58:AlarmTempTIA3Previsoka:=Bit_0; | 58:OznakeFaz[9]:=Byte_0; |  |  | 4117:Klima[5].NastMaxVlaznost:=Real_0;
mind_bool[59]:=AlarmTempTIA4Previsoka; | mind[59]:=PhaseNo; |  |  | Read_Real(rVar:=Klima[5].NastMinTemp,lo:=4118,hi:=4119); |  | 59:AlarmTempTIA4Previsoka:=Bit_0; | 59:PhaseNo:=Byte_0; |  |  | 4119:Klima[5].NastMinTemp:=Real_0;
mind_bool[60]:=AlarmUPSKrmOmara_Alarm; | mind[60]:=PMM[1].AlarmPhase[1].C01_16_60to80; |  |  | Read_Real(rVar:=Klima[5].NastMinVlaznost,lo:=4120,hi:=4121); |  | 60:AlarmUPSKrmOmara_Alarm:=Bit_0; | 60:PMM[1].AlarmPhase[1].C01_16_60to80:=Byte_0; |  |  | 4121:Klima[5].NastMinVlaznost:=Real_0;
mind_bool[61]:=ComSCADA; | mind[61]:=PMM[1].AlarmPhase[1].C01_16_over80; |  |  | Read_Real(rVar:=Klima[5].NastTempProstora,lo:=4122,hi:=4123); |  | 61:ComSCADA:=Bit_0; | 61:PMM[1].AlarmPhase[1].C01_16_over80:=Byte_0; |  |  | 4123:Klima[5].NastTempProstora:=Real_0;
mind_bool[62]:=ComSCADA1; | mind[62]:=PMM[1].AlarmPhase[1].C17_32_60to80; |  |  | Read_Real(rVar:=Klima[5].NastVlaznost,lo:=4124,hi:=4125); |  | 62:ComSCADA1:=Bit_0; | 62:PMM[1].AlarmPhase[1].C17_32_60to80:=Byte_0; |  |  | 4125:Klima[5].NastVlaznost:=Real_0;
mind_bool[63]:=ErrComKlima[1]; | mind[63]:=PMM[1].AlarmPhase[1].C17_32_over80; |  |  | Read_Real(rVar:=Klima[5].ObratUreFilter,lo:=4126,hi:=4127); |  | 63:ErrComKlima[1]:=Bit_0; | 63:PMM[1].AlarmPhase[1].C17_32_over80:=Byte_0; |  |  | 4127:Klima[5].ObratUreFilter:=Real_0;
mind_bool[64]:=ErrComKlima[2]; | mind[64]:=PMM[1].AlarmPhase[1].C33_42_60to80; |  |  | Read_Real(rVar:=Klima[5].ObratUreKompresor1,lo:=4128,hi:=4129); |  | 64:ErrComKlima[2]:=Bit_0; | 64:PMM[1].AlarmPhase[1].C33_42_60to80:=Byte_0; |  |  | 4129:Klima[5].ObratUreKompresor1:=Real_0;
mind_bool[65]:=ErrComKlima[3]; | mind[65]:=PMM[1].AlarmPhase[1].C33_42_over80; |  |  | Read_Real(rVar:=Klima[5].ObratUreKompresor2,lo:=4130,hi:=4131); |  | 65:ErrComKlima[3]:=Bit_0; | 65:PMM[1].AlarmPhase[1].C33_42_over80:=Byte_0; |  |  | 4131:Klima[5].ObratUreKompresor2:=Real_0;
mind_bool[66]:=ErrComKlima[4]; | mind[66]:=PMM[1].AlarmPhase[1].GlobalAlarmReg; |  |  | Read_Real(rVar:=Klima[5].ObratUreVent,lo:=4132,hi:=4133); |  | 66:ErrComKlima[4]:=Bit_0; | 66:PMM[1].AlarmPhase[1].GlobalAlarmReg:=Word_01; |  |  | 4133:Klima[5].ObratUreVent:=Real_0;
mind_bool[67]:=ErrComKlima[5]; | mind[67]:=PMM[1].AlarmPhase[2].C01_16_60to80; |  |  | Read_Real(rVar:=Klima[5].TemperaturaProstora,lo:=4134,hi:=4135); |  | 67:ErrComKlima[5]:=Bit_0; | 67:PMM[1].AlarmPhase[2].C01_16_60to80:=Byte_0; |  |  | 4135:Klima[5].TemperaturaProstora:=Real_0;
mind_bool[68]:=ErrComKlima[6]; | mind[68]:=PMM[1].AlarmPhase[2].C01_16_over80; |  |  | Read_Real(rVar:=Klima[5].VlaznostProstora,lo:=4136,hi:=4137); |  | 68:ErrComKlima[6]:=Bit_0; | 68:PMM[1].AlarmPhase[2].C01_16_over80:=Byte_0; |  |  | 4137:Klima[5].VlaznostProstora:=Real_0;
mind_bool[69]:=ErrCommScada; | mind[69]:=PMM[1].AlarmPhase[2].C17_32_60to80; |  |  | Read_Real(rVar:=Klima[6].NastMaxTemp,lo:=4138,hi:=4139); |  | 69:ErrCommScada:=Bit_0; | 69:PMM[1].AlarmPhase[2].C17_32_60to80:=Byte_0; |  |  | 4139:Klima[6].NastMaxTemp:=Real_0;
mind_bool[70]:=ErrComPanelPLC; | mind[70]:=PMM[1].AlarmPhase[2].C17_32_over80; |  |  | Read_Real(rVar:=Klima[6].NastMaxVlaznost,lo:=4140,hi:=4141); |  | 70:ErrComPanelPLC:=Bit_0; | 70:PMM[1].AlarmPhase[2].C17_32_over80:=Byte_0; |  |  | 4141:Klima[6].NastMaxVlaznost:=Real_0;
mind_bool[71]:=ErrComPMM[1]; | mind[71]:=PMM[1].AlarmPhase[2].C33_42_60to80; |  |  | Read_Real(rVar:=Klima[6].NastMinTemp,lo:=4142,hi:=4143); |  | 71:ErrComPMM[1]:=Bit_0; | 71:PMM[1].AlarmPhase[2].C33_42_60to80:=Byte_0; |  |  | 4143:Klima[6].NastMinTemp:=Real_0;
mind_bool[72]:=ErrComPMM[2]; | mind[72]:=PMM[1].AlarmPhase[2].C33_42_over80; |  |  | Read_Real(rVar:=Klima[6].NastMinVlaznost,lo:=4144,hi:=4145); |  | 72:ErrComPMM[2]:=Bit_0; | 72:PMM[1].AlarmPhase[2].C33_42_over80:=Byte_0; |  |  | 4145:Klima[6].NastMinVlaznost:=Real_0;
mind_bool[73]:=ErrComPort2; | mind[73]:=PMM[1].AlarmPhase[2].GlobalAlarmReg; |  |  | Read_Real(rVar:=Klima[6].NastTempProstora,lo:=4146,hi:=4147); |  | 73:ErrComPort2:=Bit_0; | 73:PMM[1].AlarmPhase[2].GlobalAlarmReg:=Word_01; |  |  | 4147:Klima[6].NastTempProstora:=Real_0;
mind_bool[74]:=ErrorComKlima[1].Error; | mind[74]:=PMM[1].AlarmPhase[3].C01_16_60to80; |  |  | Read_Real(rVar:=Klima[6].NastVlaznost,lo:=4148,hi:=4149); |  | 74:ErrorComKlima[1].Error:=Bit_0; | 74:PMM[1].AlarmPhase[3].C01_16_60to80:=Byte_0; |  |  | 4149:Klima[6].NastVlaznost:=Real_0;
mind_bool[75]:=ErrorComKlima[2].Error; | mind[75]:=PMM[1].AlarmPhase[3].C01_16_over80; |  |  | Read_Real(rVar:=Klima[6].ObratUreFilter,lo:=4150,hi:=4151); |  | 75:ErrorComKlima[2].Error:=Bit_0; | 75:PMM[1].AlarmPhase[3].C01_16_over80:=Byte_0; |  |  | 4151:Klima[6].ObratUreFilter:=Real_0;
mind_bool[76]:=ErrorComKlima[3].Error; | mind[76]:=PMM[1].AlarmPhase[3].C17_32_60to80; |  |  | Read_Real(rVar:=Klima[6].ObratUreKompresor1,lo:=4152,hi:=4153); |  | 76:ErrorComKlima[3].Error:=Bit_0; | 76:PMM[1].AlarmPhase[3].C17_32_60to80:=Byte_0; |  |  | 4153:Klima[6].ObratUreKompresor1:=Real_0;
mind_bool[77]:=ErrorComKlima[4].Error; | mind[77]:=PMM[1].AlarmPhase[3].C17_32_over80; |  |  | Read_Real(rVar:=Klima[6].ObratUreKompresor2,lo:=4154,hi:=4155); |  | 77:ErrorComKlima[4].Error:=Bit_0; | 77:PMM[1].AlarmPhase[3].C17_32_over80:=Byte_0; |  |  | 4155:Klima[6].ObratUreKompresor2:=Real_0;
mind_bool[78]:=ErrorComKlima[5].Error; | mind[78]:=PMM[1].AlarmPhase[3].C33_42_60to80; |  |  | Read_Real(rVar:=Klima[6].ObratUreVent,lo:=4156,hi:=4157); |  | 78:ErrorComKlima[5].Error:=Bit_0; | 78:PMM[1].AlarmPhase[3].C33_42_60to80:=Byte_0; |  |  | 4157:Klima[6].ObratUreVent:=Real_0;
mind_bool[79]:=ErrorComKlima[6].Error; | mind[79]:=PMM[1].AlarmPhase[3].C33_42_over80; |  |  | Read_Real(rVar:=Klima[6].TemperaturaProstora,lo:=4158,hi:=4159); |  | 79:ErrorComKlima[6].Error:=Bit_0; | 79:PMM[1].AlarmPhase[3].C33_42_over80:=Byte_0; |  |  | 4159:Klima[6].TemperaturaProstora:=Real_0;
mind_bool[80]:=ErrorComPMM[1].Error; | mind[80]:=PMM[1].AlarmPhase[3].GlobalAlarmReg; |  |  | Read_Real(rVar:=Klima[6].VlaznostProstora,lo:=4160,hi:=4161); |  | 80:ErrorComPMM[1].Error:=Bit_0; | 80:PMM[1].AlarmPhase[3].GlobalAlarmReg:=Word_01; |  |  | 4161:Klima[6].VlaznostProstora:=Real_0;
mind_bool[81]:=ErrorComPMM[2].Error; | mind[81]:=PMM[2].AlarmPhase[1].C01_16_60to80; |  |  | Read_Real(rVar:=PMM[1].ActiveEnergyConsumed_kWh,lo:=4162,hi:=4163); |  | 81:ErrorComPMM[2].Error:=Bit_0; | 81:PMM[2].AlarmPhase[1].C01_16_60to80:=Byte_0; |  |  | 4163:PMM[1].ActiveEnergyConsumed_kWh:=Real_0;
mind_bool[82]:=Klima2_1_Onemogocena; | mind[82]:=PMM[2].AlarmPhase[1].C01_16_over80; |  |  | Read_Real(rVar:=PMM[1].ActivePowerPhaseA_kW,lo:=4164,hi:=4165); |  | 82:Klima2_1_Onemogocena:=Bit_0; | 82:PMM[2].AlarmPhase[1].C01_16_over80:=Byte_0; |  |  | 4165:PMM[1].ActivePowerPhaseA_kW:=Real_0;
mind_bool[83]:=Klima2_2_Onemogocena; | mind[83]:=PMM[2].AlarmPhase[1].C17_32_60to80; |  |  | Read_Real(rVar:=PMM[1].ActivePowerPhaseB_kW,lo:=4166,hi:=4167); |  | 83:Klima2_2_Onemogocena:=Bit_0; | 83:PMM[2].AlarmPhase[1].C17_32_60to80:=Byte_0; |  |  | 4167:PMM[1].ActivePowerPhaseB_kW:=Real_0;
mind_bool[84]:=Klima2_3_Onemogocena; | mind[84]:=PMM[2].AlarmPhase[1].C17_32_over80; |  |  | Read_Real(rVar:=PMM[1].ActivePowerPhaseC_kW,lo:=4168,hi:=4169); |  | 84:Klima2_3_Onemogocena:=Bit_0; | 84:PMM[2].AlarmPhase[1].C17_32_over80:=Byte_0; |  |  | 4169:PMM[1].ActivePowerPhaseC_kW:=Real_0;
mind_bool[85]:=Klima2_4_Onemogocena; | mind[85]:=PMM[2].AlarmPhase[1].C33_42_60to80; |  |  | Read_Real(rVar:=PMM[1].AparentPowerPhaseA,lo:=4170,hi:=4171); |  | 85:Klima2_4_Onemogocena:=Bit_0; | 85:PMM[2].AlarmPhase[1].C33_42_60to80:=Byte_0; |  |  | 4171:PMM[1].AparentPowerPhaseA:=Real_0;
mind_bool[86]:=Klima2_5_Onemogocena; | mind[86]:=PMM[2].AlarmPhase[1].C33_42_over80; |  |  | Read_Real(rVar:=PMM[1].AparentPowerPhaseB,lo:=4172,hi:=4173); |  | 86:Klima2_5_Onemogocena:=Bit_0; | 86:PMM[2].AlarmPhase[1].C33_42_over80:=Byte_0; |  |  | 4173:PMM[1].AparentPowerPhaseB:=Real_0;
mind_bool[87]:=Klima2_6_Onemogocena; | mind[87]:=PMM[2].AlarmPhase[1].GlobalAlarmReg; |  |  | Read_Real(rVar:=PMM[1].AparentPowerPhaseC,lo:=4174,hi:=4175); |  | 87:Klima2_6_Onemogocena:=Bit_0; | 87:PMM[2].AlarmPhase[1].GlobalAlarmReg:=Word_01; |  |  | 4175:PMM[1].AparentPowerPhaseC:=Real_0;
mind_bool[88]:=Klima[1].IzhodniVentilator; | mind[88]:=PMM[2].AlarmPhase[2].C01_16_60to80; |  |  | Read_Real(rVar:=PMM[1].AverageCurrent_A,lo:=4176,hi:=4177); |  | 88:Klima[1].IzhodniVentilator:=Bit_0; | 88:PMM[2].AlarmPhase[2].C01_16_60to80:=Byte_0; |  |  | 4177:PMM[1].AverageCurrent_A:=Real_0;
mind_bool[89]:=Klima[1].Kompresor1; | mind[89]:=PMM[2].AlarmPhase[2].C01_16_over80; |  |  | Read_Real(rVar:=PMM[1].AveragePhaseToNeutral_V,lo:=4178,hi:=4179); |  | 89:Klima[1].Kompresor1:=Bit_0; | 89:PMM[2].AlarmPhase[2].C01_16_over80:=Byte_0; |  |  | 4179:PMM[1].AveragePhaseToNeutral_V:=Real_0;
mind_bool[90]:=Klima[1].Kompresor2; | mind[90]:=PMM[2].AlarmPhase[2].C17_32_60to80; |  |  | Read_Real(rVar:=PMM[1].AveragePhaseToPhase_V,lo:=4180,hi:=4181); |  | 90:Klima[1].Kompresor2:=Bit_0; | 90:PMM[2].AlarmPhase[2].C17_32_60to80:=Byte_0; |  |  | 4181:PMM[1].AveragePhaseToPhase_V:=Real_0;
mind_bool[91]:=Klima[1].Razvlazevanje; | mind[91]:=PMM[2].AlarmPhase[2].C17_32_over80; |  |  | Read_Real(rVar:=PMM[1].CurrentInPhaseA_A,lo:=4182,hi:=4183); |  | 91:Klima[1].Razvlazevanje:=Bit_0; | 91:PMM[2].AlarmPhase[2].C17_32_over80:=Byte_0; |  |  | 4183:PMM[1].CurrentInPhaseA_A:=Real_0;
mind_bool[92]:=Klima[1].SenzorjiStatus; | mind[92]:=PMM[2].AlarmPhase[2].C33_42_60to80; |  |  | Read_Real(rVar:=PMM[1].CurrentInPhaseB_A,lo:=4184,hi:=4185); |  | 92:Klima[1].SenzorjiStatus:=Bit_0; | 92:PMM[2].AlarmPhase[2].C33_42_60to80:=Byte_0; |  |  | 4185:PMM[1].CurrentInPhaseB_A:=Real_0;
mind_bool[93]:=Klima[1].VentilGretjeOdpiranje; | mind[93]:=PMM[2].AlarmPhase[2].C33_42_over80; |  |  | Read_Real(rVar:=PMM[1].CurrentInPhaseC_A,lo:=4186,hi:=4187); |  | 93:Klima[1].VentilGretjeOdpiranje:=Bit_0; | 93:PMM[2].AlarmPhase[2].C33_42_over80:=Byte_0; |  |  | 4187:PMM[1].CurrentInPhaseC_A:=Real_0;
mind_bool[94]:=Klima[1].VentilGretjeZapiranje; | mind[94]:=PMM[2].AlarmPhase[2].GlobalAlarmReg; |  |  | Read_Real(rVar:=PMM[1].Frequency_Hz,lo:=4188,hi:=4189); |  | 94:Klima[1].VentilGretjeZapiranje:=Bit_0; | 94:PMM[2].AlarmPhase[2].GlobalAlarmReg:=Word_01; |  |  | 4189:PMM[1].Frequency_Hz:=Real_0;
mind_bool[95]:=Klima[1].Vlazenje; | mind[95]:=PMM[2].AlarmPhase[3].C01_16_60to80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[10],lo:=4190,hi:=4191); |  | 95:Klima[1].Vlazenje:=Bit_0; | 95:PMM[2].AlarmPhase[3].C01_16_60to80:=Byte_0; |  |  | 4191:PMM[1].Phase[1].Current[10]:=Real_0;
mind_bool[96]:=Klima[2].IzhodniVentilator; | mind[96]:=PMM[2].AlarmPhase[3].C01_16_over80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[11],lo:=4192,hi:=4193); |  | 96:Klima[2].IzhodniVentilator:=Bit_0; | 96:PMM[2].AlarmPhase[3].C01_16_over80:=Byte_0; |  |  | 4193:PMM[1].Phase[1].Current[11]:=Real_0;
mind_bool[97]:=Klima[2].Kompresor1; | mind[97]:=PMM[2].AlarmPhase[3].C17_32_60to80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[12],lo:=4194,hi:=4195); |  | 97:Klima[2].Kompresor1:=Bit_0; | 97:PMM[2].AlarmPhase[3].C17_32_60to80:=Byte_0; |  |  | 4195:PMM[1].Phase[1].Current[12]:=Real_0;
mind_bool[98]:=Klima[2].Kompresor2; | mind[98]:=PMM[2].AlarmPhase[3].C17_32_over80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[13],lo:=4196,hi:=4197); |  | 98:Klima[2].Kompresor2:=Bit_0; | 98:PMM[2].AlarmPhase[3].C17_32_over80:=Byte_0; |  |  | 4197:PMM[1].Phase[1].Current[13]:=Real_0;
mind_bool[99]:=Klima[2].Razvlazevanje; | mind[99]:=PMM[2].AlarmPhase[3].C33_42_60to80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[14],lo:=4198,hi:=4199); |  | 99:Klima[2].Razvlazevanje:=Bit_0; | 99:PMM[2].AlarmPhase[3].C33_42_60to80:=Byte_0; |  |  | 4199:PMM[1].Phase[1].Current[14]:=Real_0;
mind_bool[100]:=Klima[2].SenzorjiStatus; | mind[100]:=PMM[2].AlarmPhase[3].C33_42_over80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[15],lo:=4200,hi:=4201); |  | 100:Klima[2].SenzorjiStatus:=Bit_0; | 100:PMM[2].AlarmPhase[3].C33_42_over80:=Byte_0; |  |  | 4201:PMM[1].Phase[1].Current[15]:=Real_0;
mind_bool[101]:=Klima[2].VentilGretjeOdpiranje; | mind[101]:=PMM[2].AlarmPhase[3].GlobalAlarmReg; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[16],lo:=4202,hi:=4203); |  | 101:Klima[2].VentilGretjeOdpiranje:=Bit_0; | 101:PMM[2].AlarmPhase[3].GlobalAlarmReg:=Word_01; |  |  | 4203:PMM[1].Phase[1].Current[16]:=Real_0;
mind_bool[102]:=Klima[2].VentilGretjeZapiranje; | mind[102]:=PMMPanel.AlarmPhase[1].C01_16_60to80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[17],lo:=4204,hi:=4205); |  | 102:Klima[2].VentilGretjeZapiranje:=Bit_0; | 102:PMMPanel.AlarmPhase[1].C01_16_60to80:=Byte_0; |  |  | 4205:PMM[1].Phase[1].Current[17]:=Real_0;
mind_bool[103]:=Klima[2].Vlazenje; | mind[103]:=PMMPanel.AlarmPhase[1].C01_16_over80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[18],lo:=4206,hi:=4207); |  | 103:Klima[2].Vlazenje:=Bit_0; | 103:PMMPanel.AlarmPhase[1].C01_16_over80:=Byte_0; |  |  | 4207:PMM[1].Phase[1].Current[18]:=Real_0;
mind_bool[104]:=Klima[3].IzhodniVentilator; | mind[104]:=PMMPanel.AlarmPhase[1].C17_32_60to80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[19],lo:=4208,hi:=4209); |  | 104:Klima[3].IzhodniVentilator:=Bit_0; | 104:PMMPanel.AlarmPhase[1].C17_32_60to80:=Byte_0; |  |  | 4209:PMM[1].Phase[1].Current[19]:=Real_0;
mind_bool[105]:=Klima[3].Kompresor1; | mind[105]:=PMMPanel.AlarmPhase[1].C17_32_over80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[1],lo:=4210,hi:=4211); |  | 105:Klima[3].Kompresor1:=Bit_0; | 105:PMMPanel.AlarmPhase[1].C17_32_over80:=Byte_0; |  |  | 4211:PMM[1].Phase[1].Current[1]:=Real_0;
mind_bool[106]:=Klima[3].Kompresor2; | mind[106]:=PMMPanel.AlarmPhase[1].C33_42_60to80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[20],lo:=4212,hi:=4213); |  | 106:Klima[3].Kompresor2:=Bit_0; | 106:PMMPanel.AlarmPhase[1].C33_42_60to80:=Byte_0; |  |  | 4213:PMM[1].Phase[1].Current[20]:=Real_0;
mind_bool[107]:=Klima[3].Razvlazevanje; | mind[107]:=PMMPanel.AlarmPhase[1].C33_42_over80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[21],lo:=4214,hi:=4215); |  | 107:Klima[3].Razvlazevanje:=Bit_0; | 107:PMMPanel.AlarmPhase[1].C33_42_over80:=Byte_0; |  |  | 4215:PMM[1].Phase[1].Current[21]:=Real_0;
mind_bool[108]:=Klima[3].SenzorjiStatus; | mind[108]:=PMMPanel.AlarmPhase[1].GlobalAlarmReg; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[22],lo:=4216,hi:=4217); |  | 108:Klima[3].SenzorjiStatus:=Bit_0; | 108:PMMPanel.AlarmPhase[1].GlobalAlarmReg:=Word_01; |  |  | 4217:PMM[1].Phase[1].Current[22]:=Real_0;
mind_bool[109]:=Klima[3].VentilGretjeOdpiranje; | mind[109]:=PMMPanel.AlarmPhase[2].C01_16_60to80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[23],lo:=4218,hi:=4219); |  | 109:Klima[3].VentilGretjeOdpiranje:=Bit_0; | 109:PMMPanel.AlarmPhase[2].C01_16_60to80:=Byte_0; |  |  | 4219:PMM[1].Phase[1].Current[23]:=Real_0;
mind_bool[110]:=Klima[3].VentilGretjeZapiranje; | mind[110]:=PMMPanel.AlarmPhase[2].C01_16_over80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[24],lo:=4220,hi:=4221); |  | 110:Klima[3].VentilGretjeZapiranje:=Bit_0; | 110:PMMPanel.AlarmPhase[2].C01_16_over80:=Byte_0; |  |  | 4221:PMM[1].Phase[1].Current[24]:=Real_0;
mind_bool[111]:=Klima[3].Vlazenje; | mind[111]:=PMMPanel.AlarmPhase[2].C17_32_60to80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[25],lo:=4222,hi:=4223); |  | 111:Klima[3].Vlazenje:=Bit_0; | 111:PMMPanel.AlarmPhase[2].C17_32_60to80:=Byte_0; |  |  | 4223:PMM[1].Phase[1].Current[25]:=Real_0;
mind_bool[112]:=Klima[4].IzhodniVentilator; | mind[112]:=PMMPanel.AlarmPhase[2].C17_32_over80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[26],lo:=4224,hi:=4225); |  | 112:Klima[4].IzhodniVentilator:=Bit_0; | 112:PMMPanel.AlarmPhase[2].C17_32_over80:=Byte_0; |  |  | 4225:PMM[1].Phase[1].Current[26]:=Real_0;
mind_bool[113]:=Klima[4].Kompresor1; | mind[113]:=PMMPanel.AlarmPhase[2].C33_42_60to80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[27],lo:=4226,hi:=4227); |  | 113:Klima[4].Kompresor1:=Bit_0; | 113:PMMPanel.AlarmPhase[2].C33_42_60to80:=Byte_0; |  |  | 4227:PMM[1].Phase[1].Current[27]:=Real_0;
mind_bool[114]:=Klima[4].Kompresor2; | mind[114]:=PMMPanel.AlarmPhase[2].C33_42_over80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[28],lo:=4228,hi:=4229); |  | 114:Klima[4].Kompresor2:=Bit_0; | 114:PMMPanel.AlarmPhase[2].C33_42_over80:=Byte_0; |  |  | 4229:PMM[1].Phase[1].Current[28]:=Real_0;
mind_bool[115]:=Klima[4].Razvlazevanje; | mind[115]:=PMMPanel.AlarmPhase[2].GlobalAlarmReg; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[29],lo:=4230,hi:=4231); |  | 115:Klima[4].Razvlazevanje:=Bit_0; | 115:PMMPanel.AlarmPhase[2].GlobalAlarmReg:=Word_01; |  |  | 4231:PMM[1].Phase[1].Current[29]:=Real_0;
mind_bool[116]:=Klima[4].SenzorjiStatus; | mind[116]:=PMMPanel.AlarmPhase[3].C01_16_60to80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[2],lo:=4232,hi:=4233); |  | 116:Klima[4].SenzorjiStatus:=Bit_0; | 116:PMMPanel.AlarmPhase[3].C01_16_60to80:=Byte_0; |  |  | 4233:PMM[1].Phase[1].Current[2]:=Real_0;
mind_bool[117]:=Klima[4].VentilGretjeOdpiranje; | mind[117]:=PMMPanel.AlarmPhase[3].C01_16_over80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[30],lo:=4234,hi:=4235); |  | 117:Klima[4].VentilGretjeOdpiranje:=Bit_0; | 117:PMMPanel.AlarmPhase[3].C01_16_over80:=Byte_0; |  |  | 4235:PMM[1].Phase[1].Current[30]:=Real_0;
mind_bool[118]:=Klima[4].VentilGretjeZapiranje; | mind[118]:=PMMPanel.AlarmPhase[3].C17_32_60to80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[31],lo:=4236,hi:=4237); |  | 118:Klima[4].VentilGretjeZapiranje:=Bit_0; | 118:PMMPanel.AlarmPhase[3].C17_32_60to80:=Byte_0; |  |  | 4237:PMM[1].Phase[1].Current[31]:=Real_0;
mind_bool[119]:=Klima[4].Vlazenje; | mind[119]:=PMMPanel.AlarmPhase[3].C17_32_over80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[32],lo:=4238,hi:=4239); |  | 119:Klima[4].Vlazenje:=Bit_0; | 119:PMMPanel.AlarmPhase[3].C17_32_over80:=Byte_0; |  |  | 4239:PMM[1].Phase[1].Current[32]:=Real_0;
mind_bool[120]:=Klima[5].IzhodniVentilator; | mind[120]:=PMMPanel.AlarmPhase[3].C33_42_60to80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[33],lo:=4240,hi:=4241); |  | 120:Klima[5].IzhodniVentilator:=Bit_0; | 120:PMMPanel.AlarmPhase[3].C33_42_60to80:=Byte_0; |  |  | 4241:PMM[1].Phase[1].Current[33]:=Real_0;
mind_bool[121]:=Klima[5].Kompresor1; | mind[121]:=PMMPanel.AlarmPhase[3].C33_42_over80; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[34],lo:=4242,hi:=4243); |  | 121:Klima[5].Kompresor1:=Bit_0; | 121:PMMPanel.AlarmPhase[3].C33_42_over80:=Byte_0; |  |  | 4243:PMM[1].Phase[1].Current[34]:=Real_0;
mind_bool[122]:=Klima[5].Kompresor2; | mind[122]:=PMMPanel.AlarmPhase[3].GlobalAlarmReg; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[35],lo:=4244,hi:=4245); |  | 122:Klima[5].Kompresor2:=Bit_0; | 122:PMMPanel.AlarmPhase[3].GlobalAlarmReg:=Word_01; |  |  | 4245:PMM[1].Phase[1].Current[35]:=Real_0;
mind_bool[123]:=Klima[5].Razvlazevanje; | mind[123]:=StUrZaPreklopKlim1_2; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[36],lo:=4246,hi:=4247); |  | 123:Klima[5].Razvlazevanje:=Bit_0; | 123:StUrZaPreklopKlim1_2:=Word_01; |  |  | 4247:PMM[1].Phase[1].Current[36]:=Real_0;
mind_bool[124]:=Klima[5].SenzorjiStatus; | mind[124]:=StUrZaPreklopKlim3_4; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[37],lo:=4248,hi:=4249); |  | 124:Klima[5].SenzorjiStatus:=Bit_0; | 124:StUrZaPreklopKlim3_4:=Word_01; |  |  | 4249:PMM[1].Phase[1].Current[37]:=Real_0;
mind_bool[125]:=Klima[5].VentilGretjeOdpiranje; | mind[125]:=StUrZaPreklopKlim5_6; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[38],lo:=4250,hi:=4251); |  | 125:Klima[5].VentilGretjeOdpiranje:=Bit_0; | 125:StUrZaPreklopKlim5_6:=Word_01; |  |  | 4251:PMM[1].Phase[1].Current[38]:=Real_0;
mind_bool[126]:=Klima[5].VentilGretjeZapiranje; | mind[126]:=UPSstatus_Prikaz_PanelSCADA; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[39],lo:=4252,hi:=4253); |  | 126:Klima[5].VentilGretjeZapiranje:=Bit_0; | 126:UPSstatus_Prikaz_PanelSCADA:=Byte_0; |  |  | 4253:PMM[1].Phase[1].Current[39]:=Real_0;
mind_bool[127]:=Klima[5].Vlazenje; | mind[127]:=UserCurrentLevel; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[3],lo:=4254,hi:=4255); |  | 127:Klima[5].Vlazenje:=Bit_0; | 127:UserCurrentLevel:=Byte_0; |  |  | 4255:PMM[1].Phase[1].Current[3]:=Real_0;
mind_bool[128]:=Klima[6].IzhodniVentilator; | mind[128]:=ErrorComKlima[1].Code[0]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[40],lo:=4256,hi:=4257); |  | 128:Klima[6].IzhodniVentilator:=Bit_0; | 128:ErrorComKlima[1].Code[0]:=Byte_0; |  |  | 4257:PMM[1].Phase[1].Current[40]:=Real_0;
mind_bool[129]:=Klima[6].Kompresor1; | mind[129]:=ErrorComKlima[1].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[41],lo:=4258,hi:=4259); |  | 129:Klima[6].Kompresor1:=Bit_0; | 129:ErrorComKlima[1].Code[10]:=Byte_0; |  |  | 4259:PMM[1].Phase[1].Current[41]:=Real_0;
mind_bool[130]:=Klima[6].Kompresor2; | mind[130]:=ErrorComKlima[1].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[42],lo:=4260,hi:=4261); |  | 130:Klima[6].Kompresor2:=Bit_0; | 130:ErrorComKlima[1].Code[11]:=Byte_0; |  |  | 4261:PMM[1].Phase[1].Current[42]:=Real_0;
mind_bool[131]:=Klima[6].Razvlazevanje; | mind[131]:=ErrorComKlima[1].Code[12]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[4],lo:=4262,hi:=4263); |  | 131:Klima[6].Razvlazevanje:=Bit_0; | 131:ErrorComKlima[1].Code[12]:=Byte_0; |  |  | 4263:PMM[1].Phase[1].Current[4]:=Real_0;
mind_bool[132]:=Klima[6].SenzorjiStatus; | mind[132]:=ErrorComKlima[1].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[5],lo:=4264,hi:=4265); |  | 132:Klima[6].SenzorjiStatus:=Bit_0; | 132:ErrorComKlima[1].Code[13]:=Byte_0; |  |  | 4265:PMM[1].Phase[1].Current[5]:=Real_0;
mind_bool[133]:=Klima[6].VentilGretjeOdpiranje; | mind[133]:=ErrorComKlima[1].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[6],lo:=4266,hi:=4267); |  | 133:Klima[6].VentilGretjeOdpiranje:=Bit_0; | 133:ErrorComKlima[1].Code[14]:=Byte_0; |  |  | 4267:PMM[1].Phase[1].Current[6]:=Real_0;
mind_bool[134]:=Klima[6].VentilGretjeZapiranje; | mind[134]:=ErrorComKlima[1].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[7],lo:=4268,hi:=4269); |  | 134:Klima[6].VentilGretjeZapiranje:=Bit_0; | 134:ErrorComKlima[1].Code[15]:=Byte_0; |  |  | 4269:PMM[1].Phase[1].Current[7]:=Real_0;
mind_bool[135]:=Klima[6].Vlazenje; | mind[135]:=ErrorComKlima[1].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[8],lo:=4270,hi:=4271); |  | 135:Klima[6].Vlazenje:=Bit_0; | 135:ErrorComKlima[1].Code[1]:=Byte_0; |  |  | 4271:PMM[1].Phase[1].Current[8]:=Real_0;
mind_bool[136]:=KlimaError[1].AlarmKompresor1; | mind[136]:=ErrorComKlima[1].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[9],lo:=4272,hi:=4273); |  | 136:KlimaError[1].AlarmKompresor1:=Bit_0; | 136:ErrorComKlima[1].Code[2]:=Byte_0; |  |  | 4273:PMM[1].Phase[1].Current[9]:=Real_0;
mind_bool[137]:=KlimaError[1].AlarmKompresor2; | mind[137]:=ErrorComKlima[1].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[10],lo:=4274,hi:=4275); |  | 137:KlimaError[1].AlarmKompresor2:=Bit_0; | 137:ErrorComKlima[1].Code[3]:=Byte_0; |  |  | 4275:PMM[1].Phase[2].Current[10]:=Real_0;
mind_bool[138]:=KlimaError[1].FenThermalCutout; | mind[138]:=ErrorComKlima[1].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[11],lo:=4276,hi:=4277); |  | 138:KlimaError[1].FenThermalCutout:=Bit_0; | 138:ErrorComKlima[1].Code[4]:=Byte_0; |  |  | 4277:PMM[1].Phase[2].Current[11]:=Real_0;
mind_bool[139]:=KlimaError[1].IzlivVode; | mind[139]:=ErrorComKlima[1].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[12],lo:=4278,hi:=4279); |  | 139:KlimaError[1].IzlivVode:=Bit_0; | 139:ErrorComKlima[1].Code[5]:=Byte_0; |  |  | 4279:PMM[1].Phase[2].Current[12]:=Real_0;
mind_bool[140]:=KlimaError[1].Kompresor1naMejiStevilaObrUr; | mind[140]:=ErrorComKlima[1].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[13],lo:=4280,hi:=4281); |  | 140:KlimaError[1].Kompresor1naMejiStevilaObrUr:=Bit_0; | 140:ErrorComKlima[1].Code[6]:=Byte_0; |  |  | 4281:PMM[1].Phase[2].Current[13]:=Real_0;
mind_bool[141]:=KlimaError[1].Kompresor2naMejiStevilaObrUr; | mind[141]:=ErrorComKlima[1].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[14],lo:=4282,hi:=4283); |  | 141:KlimaError[1].Kompresor2naMejiStevilaObrUr:=Bit_0; | 141:ErrorComKlima[1].Code[7]:=Byte_0; |  |  | 4283:PMM[1].Phase[2].Current[14]:=Real_0;
mind_bool[142]:=KlimaError[1].NapakaPriPretokuVode; | mind[142]:=ErrorComKlima[1].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[15],lo:=4284,hi:=4285); |  | 142:KlimaError[1].NapakaPriPretokuVode:=Bit_0; | 142:ErrorComKlima[1].Code[8]:=Byte_0; |  |  | 4285:PMM[1].Phase[2].Current[15]:=Real_0;
mind_bool[143]:=KlimaError[1].NapakaPriPretokuZraka; | mind[143]:=ErrorComKlima[1].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[16],lo:=4286,hi:=4287); |  | 143:KlimaError[1].NapakaPriPretokuZraka:=Bit_0; | 143:ErrorComKlima[1].Code[9]:=Byte_0; |  |  | 4287:PMM[1].Phase[2].Current[16]:=Real_0;
mind_bool[144]:=KlimaError[1].NapakaSenzorVlaznosti; | mind[144]:=ErrorComKlima[2].Code[0]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[17],lo:=4288,hi:=4289); |  | 144:KlimaError[1].NapakaSenzorVlaznosti:=Bit_0; | 144:ErrorComKlima[2].Code[0]:=Byte_0; |  |  | 4289:PMM[1].Phase[2].Current[17]:=Real_0;
mind_bool[145]:=KlimaError[1].NapakaTSTemperaturaProstora; | mind[145]:=ErrorComKlima[2].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[18],lo:=4290,hi:=4291); |  | 145:KlimaError[1].NapakaTSTemperaturaProstora:=Bit_0; | 145:ErrorComKlima[2].Code[10]:=Byte_0; |  |  | 4291:PMM[1].Phase[2].Current[18]:=Real_0;
mind_bool[146]:=KlimaError[1].NapakaVlazilca; | mind[146]:=ErrorComKlima[2].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[19],lo:=4292,hi:=4293); |  | 146:KlimaError[1].NapakaVlazilca:=Bit_0; | 146:ErrorComKlima[2].Code[11]:=Byte_0; |  |  | 4293:PMM[1].Phase[2].Current[19]:=Real_0;
mind_bool[147]:=KlimaError[1].NizekPritiskKompresor1; | mind[147]:=ErrorComKlima[2].Code[12]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[1],lo:=4294,hi:=4295); |  | 147:KlimaError[1].NizekPritiskKompresor1:=Bit_0; | 147:ErrorComKlima[2].Code[12]:=Byte_0; |  |  | 4295:PMM[1].Phase[2].Current[1]:=Real_0;
mind_bool[148]:=KlimaError[1].NizekPritiskKompresor2; | mind[148]:=ErrorComKlima[2].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[20],lo:=4296,hi:=4297); |  | 148:KlimaError[1].NizekPritiskKompresor2:=Bit_0; | 148:ErrorComKlima[2].Code[13]:=Byte_0; |  |  | 4297:PMM[1].Phase[2].Current[20]:=Real_0;
mind_bool[149]:=KlimaError[1].NizkaTempVProstoru; | mind[149]:=ErrorComKlima[2].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[21],lo:=4298,hi:=4299); |  | 149:KlimaError[1].NizkaTempVProstoru:=Bit_0; | 149:ErrorComKlima[2].Code[14]:=Byte_0; |  |  | 4299:PMM[1].Phase[2].Current[21]:=Real_0;
mind_bool[150]:=KlimaError[1].NizkaVlaznost; | mind[150]:=ErrorComKlima[2].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[22],lo:=4300,hi:=4301); |  | 150:KlimaError[1].NizkaVlaznost:=Bit_0; | 150:ErrorComKlima[2].Code[15]:=Byte_0; |  |  | 4301:PMM[1].Phase[2].Current[22]:=Real_0;
mind_bool[151]:=KlimaError[1].PozarniAlarm; | mind[151]:=ErrorComKlima[2].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[23],lo:=4302,hi:=4303); |  | 151:KlimaError[1].PozarniAlarm:=Bit_0; | 151:ErrorComKlima[2].Code[1]:=Byte_0; |  |  | 4303:PMM[1].Phase[2].Current[23]:=Real_0;
mind_bool[152]:=KlimaError[1].ThermalCutoutHeater1; | mind[152]:=ErrorComKlima[2].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[24],lo:=4304,hi:=4305); |  | 152:KlimaError[1].ThermalCutoutHeater1:=Bit_0; | 152:ErrorComKlima[2].Code[2]:=Byte_0; |  |  | 4305:PMM[1].Phase[2].Current[24]:=Real_0;
mind_bool[153]:=KlimaError[1].ThermalCutoutHeater2; | mind[153]:=ErrorComKlima[2].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[25],lo:=4306,hi:=4307); |  | 153:KlimaError[1].ThermalCutoutHeater2:=Bit_0; | 153:ErrorComKlima[2].Code[3]:=Byte_0; |  |  | 4307:PMM[1].Phase[2].Current[25]:=Real_0;
mind_bool[154]:=KlimaError[1].VentilatorNaMejiStevilaObrUr; | mind[154]:=ErrorComKlima[2].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[26],lo:=4308,hi:=4309); |  | 154:KlimaError[1].VentilatorNaMejiStevilaObrUr:=Bit_0; | 154:ErrorComKlima[2].Code[4]:=Byte_0; |  |  | 4309:PMM[1].Phase[2].Current[26]:=Real_0;
mind_bool[155]:=KlimaError[1].VisokaTempVProstoru; | mind[155]:=ErrorComKlima[2].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[27],lo:=4310,hi:=4311); |  | 155:KlimaError[1].VisokaTempVProstoru:=Bit_0; | 155:ErrorComKlima[2].Code[5]:=Byte_0; |  |  | 4311:PMM[1].Phase[2].Current[27]:=Real_0;
mind_bool[156]:=KlimaError[1].VisokaVlaznost; | mind[156]:=ErrorComKlima[2].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[28],lo:=4312,hi:=4313); |  | 156:KlimaError[1].VisokaVlaznost:=Bit_0; | 156:ErrorComKlima[2].Code[6]:=Byte_0; |  |  | 4313:PMM[1].Phase[2].Current[28]:=Real_0;
mind_bool[157]:=KlimaError[1].VisokPritiskKompresor1; | mind[157]:=ErrorComKlima[2].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[29],lo:=4314,hi:=4315); |  | 157:KlimaError[1].VisokPritiskKompresor1:=Bit_0; | 157:ErrorComKlima[2].Code[7]:=Byte_0; |  |  | 4315:PMM[1].Phase[2].Current[29]:=Real_0;
mind_bool[158]:=KlimaError[1].VisokPritiskKompresor2; | mind[158]:=ErrorComKlima[2].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[2],lo:=4316,hi:=4317); |  | 158:KlimaError[1].VisokPritiskKompresor2:=Bit_0; | 158:ErrorComKlima[2].Code[8]:=Byte_0; |  |  | 4317:PMM[1].Phase[2].Current[2]:=Real_0;
mind_bool[159]:=KlimaError[1].ZamasenFilter; | mind[159]:=ErrorComKlima[2].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[30],lo:=4318,hi:=4319); |  | 159:KlimaError[1].ZamasenFilter:=Bit_0; | 159:ErrorComKlima[2].Code[9]:=Byte_0; |  |  | 4319:PMM[1].Phase[2].Current[30]:=Real_0;
mind_bool[160]:=KlimaError[1].ZunanjiAlarm; | mind[160]:=ErrorComKlima[3].Code[0]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[31],lo:=4320,hi:=4321); |  | 160:KlimaError[1].ZunanjiAlarm:=Bit_0; | 160:ErrorComKlima[3].Code[0]:=Byte_0; |  |  | 4321:PMM[1].Phase[2].Current[31]:=Real_0;
mind_bool[161]:=KlimaError[2].AlarmKompresor1; | mind[161]:=ErrorComKlima[3].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[32],lo:=4322,hi:=4323); |  | 161:KlimaError[2].AlarmKompresor1:=Bit_0; | 161:ErrorComKlima[3].Code[10]:=Byte_0; |  |  | 4323:PMM[1].Phase[2].Current[32]:=Real_0;
mind_bool[162]:=KlimaError[2].AlarmKompresor2; | mind[162]:=ErrorComKlima[3].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[33],lo:=4324,hi:=4325); |  | 162:KlimaError[2].AlarmKompresor2:=Bit_0; | 162:ErrorComKlima[3].Code[11]:=Byte_0; |  |  | 4325:PMM[1].Phase[2].Current[33]:=Real_0;
mind_bool[163]:=KlimaError[2].FenThermalCutout; | mind[163]:=ErrorComKlima[3].Code[12]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[34],lo:=4326,hi:=4327); |  | 163:KlimaError[2].FenThermalCutout:=Bit_0; | 163:ErrorComKlima[3].Code[12]:=Byte_0; |  |  | 4327:PMM[1].Phase[2].Current[34]:=Real_0;
mind_bool[164]:=KlimaError[2].IzlivVode; | mind[164]:=ErrorComKlima[3].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[35],lo:=4328,hi:=4329); |  | 164:KlimaError[2].IzlivVode:=Bit_0; | 164:ErrorComKlima[3].Code[13]:=Byte_0; |  |  | 4329:PMM[1].Phase[2].Current[35]:=Real_0;
mind_bool[165]:=KlimaError[2].Kompresor1naMejiStevilaObrUr; | mind[165]:=ErrorComKlima[3].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[36],lo:=4330,hi:=4331); |  | 165:KlimaError[2].Kompresor1naMejiStevilaObrUr:=Bit_0; | 165:ErrorComKlima[3].Code[14]:=Byte_0; |  |  | 4331:PMM[1].Phase[2].Current[36]:=Real_0;
mind_bool[166]:=KlimaError[2].Kompresor2naMejiStevilaObrUr; | mind[166]:=ErrorComKlima[3].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[37],lo:=4332,hi:=4333); |  | 166:KlimaError[2].Kompresor2naMejiStevilaObrUr:=Bit_0; | 166:ErrorComKlima[3].Code[15]:=Byte_0; |  |  | 4333:PMM[1].Phase[2].Current[37]:=Real_0;
mind_bool[167]:=KlimaError[2].NapakaPriPretokuVode; | mind[167]:=ErrorComKlima[3].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[38],lo:=4334,hi:=4335); |  | 167:KlimaError[2].NapakaPriPretokuVode:=Bit_0; | 167:ErrorComKlima[3].Code[1]:=Byte_0; |  |  | 4335:PMM[1].Phase[2].Current[38]:=Real_0;
mind_bool[168]:=KlimaError[2].NapakaPriPretokuZraka; | mind[168]:=ErrorComKlima[3].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[39],lo:=4336,hi:=4337); |  | 168:KlimaError[2].NapakaPriPretokuZraka:=Bit_0; | 168:ErrorComKlima[3].Code[2]:=Byte_0; |  |  | 4337:PMM[1].Phase[2].Current[39]:=Real_0;
mind_bool[169]:=KlimaError[2].NapakaSenzorVlaznosti; | mind[169]:=ErrorComKlima[3].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[3],lo:=4338,hi:=4339); |  | 169:KlimaError[2].NapakaSenzorVlaznosti:=Bit_0; | 169:ErrorComKlima[3].Code[3]:=Byte_0; |  |  | 4339:PMM[1].Phase[2].Current[3]:=Real_0;
mind_bool[170]:=KlimaError[2].NapakaTSTemperaturaProstora; | mind[170]:=ErrorComKlima[3].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[40],lo:=4340,hi:=4341); |  | 170:KlimaError[2].NapakaTSTemperaturaProstora:=Bit_0; | 170:ErrorComKlima[3].Code[4]:=Byte_0; |  |  | 4341:PMM[1].Phase[2].Current[40]:=Real_0;
mind_bool[171]:=KlimaError[2].NapakaVlazilca; | mind[171]:=ErrorComKlima[3].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[41],lo:=4342,hi:=4343); |  | 171:KlimaError[2].NapakaVlazilca:=Bit_0; | 171:ErrorComKlima[3].Code[5]:=Byte_0; |  |  | 4343:PMM[1].Phase[2].Current[41]:=Real_0;
mind_bool[172]:=KlimaError[2].NizekPritiskKompresor1; | mind[172]:=ErrorComKlima[3].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[42],lo:=4344,hi:=4345); |  | 172:KlimaError[2].NizekPritiskKompresor1:=Bit_0; | 172:ErrorComKlima[3].Code[6]:=Byte_0; |  |  | 4345:PMM[1].Phase[2].Current[42]:=Real_0;
mind_bool[173]:=KlimaError[2].NizekPritiskKompresor2; | mind[173]:=ErrorComKlima[3].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[4],lo:=4346,hi:=4347); |  | 173:KlimaError[2].NizekPritiskKompresor2:=Bit_0; | 173:ErrorComKlima[3].Code[7]:=Byte_0; |  |  | 4347:PMM[1].Phase[2].Current[4]:=Real_0;
mind_bool[174]:=KlimaError[2].NizkaTempVProstoru; | mind[174]:=ErrorComKlima[3].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[5],lo:=4348,hi:=4349); |  | 174:KlimaError[2].NizkaTempVProstoru:=Bit_0; | 174:ErrorComKlima[3].Code[8]:=Byte_0; |  |  | 4349:PMM[1].Phase[2].Current[5]:=Real_0;
mind_bool[175]:=KlimaError[2].NizkaVlaznost; | mind[175]:=ErrorComKlima[3].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[6],lo:=4350,hi:=4351); |  | 175:KlimaError[2].NizkaVlaznost:=Bit_0; | 175:ErrorComKlima[3].Code[9]:=Byte_0; |  |  | 4351:PMM[1].Phase[2].Current[6]:=Real_0;
mind_bool[176]:=KlimaError[2].PozarniAlarm; | mind[176]:=ErrorComKlima[4].Code[0]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[7],lo:=4352,hi:=4353); |  | 176:KlimaError[2].PozarniAlarm:=Bit_0; | 176:ErrorComKlima[4].Code[0]:=Byte_0; |  |  | 4353:PMM[1].Phase[2].Current[7]:=Real_0;
mind_bool[177]:=KlimaError[2].ThermalCutoutHeater1; | mind[177]:=ErrorComKlima[4].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[8],lo:=4354,hi:=4355); |  | 177:KlimaError[2].ThermalCutoutHeater1:=Bit_0; | 177:ErrorComKlima[4].Code[10]:=Byte_0; |  |  | 4355:PMM[1].Phase[2].Current[8]:=Real_0;
mind_bool[178]:=KlimaError[2].ThermalCutoutHeater2; | mind[178]:=ErrorComKlima[4].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[9],lo:=4356,hi:=4357); |  | 178:KlimaError[2].ThermalCutoutHeater2:=Bit_0; | 178:ErrorComKlima[4].Code[11]:=Byte_0; |  |  | 4357:PMM[1].Phase[2].Current[9]:=Real_0;
mind_bool[179]:=KlimaError[2].VentilatorNaMejiStevilaObrUr; | mind[179]:=ErrorComKlima[4].Code[12]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[10],lo:=4358,hi:=4359); |  | 179:KlimaError[2].VentilatorNaMejiStevilaObrUr:=Bit_0; | 179:ErrorComKlima[4].Code[12]:=Byte_0; |  |  | 4359:PMM[1].Phase[3].Current[10]:=Real_0;
mind_bool[180]:=KlimaError[2].VisokaTempVProstoru; | mind[180]:=ErrorComKlima[4].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[11],lo:=4360,hi:=4361); |  | 180:KlimaError[2].VisokaTempVProstoru:=Bit_0; | 180:ErrorComKlima[4].Code[13]:=Byte_0; |  |  | 4361:PMM[1].Phase[3].Current[11]:=Real_0;
mind_bool[181]:=KlimaError[2].VisokaVlaznost; | mind[181]:=ErrorComKlima[4].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[12],lo:=4362,hi:=4363); |  | 181:KlimaError[2].VisokaVlaznost:=Bit_0; | 181:ErrorComKlima[4].Code[14]:=Byte_0; |  |  | 4363:PMM[1].Phase[3].Current[12]:=Real_0;
mind_bool[182]:=KlimaError[2].VisokPritiskKompresor1; | mind[182]:=ErrorComKlima[4].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[13],lo:=4364,hi:=4365); |  | 182:KlimaError[2].VisokPritiskKompresor1:=Bit_0; | 182:ErrorComKlima[4].Code[15]:=Byte_0; |  |  | 4365:PMM[1].Phase[3].Current[13]:=Real_0;
mind_bool[183]:=KlimaError[2].VisokPritiskKompresor2; | mind[183]:=ErrorComKlima[4].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[14],lo:=4366,hi:=4367); |  | 183:KlimaError[2].VisokPritiskKompresor2:=Bit_0; | 183:ErrorComKlima[4].Code[1]:=Byte_0; |  |  | 4367:PMM[1].Phase[3].Current[14]:=Real_0;
mind_bool[184]:=KlimaError[2].ZamasenFilter; | mind[184]:=ErrorComKlima[4].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[15],lo:=4368,hi:=4369); |  | 184:KlimaError[2].ZamasenFilter:=Bit_0; | 184:ErrorComKlima[4].Code[2]:=Byte_0; |  |  | 4369:PMM[1].Phase[3].Current[15]:=Real_0;
mind_bool[185]:=KlimaError[2].ZunanjiAlarm; | mind[185]:=ErrorComKlima[4].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[16],lo:=4370,hi:=4371); |  | 185:KlimaError[2].ZunanjiAlarm:=Bit_0; | 185:ErrorComKlima[4].Code[3]:=Byte_0; |  |  | 4371:PMM[1].Phase[3].Current[16]:=Real_0;
mind_bool[186]:=KlimaError[3].AlarmKompresor1; | mind[186]:=ErrorComKlima[4].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[17],lo:=4372,hi:=4373); |  | 186:KlimaError[3].AlarmKompresor1:=Bit_0; | 186:ErrorComKlima[4].Code[4]:=Byte_0; |  |  | 4373:PMM[1].Phase[3].Current[17]:=Real_0;
mind_bool[187]:=KlimaError[3].AlarmKompresor2; | mind[187]:=ErrorComKlima[4].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[18],lo:=4374,hi:=4375); |  | 187:KlimaError[3].AlarmKompresor2:=Bit_0; | 187:ErrorComKlima[4].Code[5]:=Byte_0; |  |  | 4375:PMM[1].Phase[3].Current[18]:=Real_0;
mind_bool[188]:=KlimaError[3].FenThermalCutout; | mind[188]:=ErrorComKlima[4].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[19],lo:=4376,hi:=4377); |  | 188:KlimaError[3].FenThermalCutout:=Bit_0; | 188:ErrorComKlima[4].Code[6]:=Byte_0; |  |  | 4377:PMM[1].Phase[3].Current[19]:=Real_0;
mind_bool[189]:=KlimaError[3].IzlivVode; | mind[189]:=ErrorComKlima[4].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[1],lo:=4378,hi:=4379); |  | 189:KlimaError[3].IzlivVode:=Bit_0; | 189:ErrorComKlima[4].Code[7]:=Byte_0; |  |  | 4379:PMM[1].Phase[3].Current[1]:=Real_0;
mind_bool[190]:=KlimaError[3].Kompresor1naMejiStevilaObrUr; | mind[190]:=ErrorComKlima[4].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[20],lo:=4380,hi:=4381); |  | 190:KlimaError[3].Kompresor1naMejiStevilaObrUr:=Bit_0; | 190:ErrorComKlima[4].Code[8]:=Byte_0; |  |  | 4381:PMM[1].Phase[3].Current[20]:=Real_0;
mind_bool[191]:=KlimaError[3].Kompresor2naMejiStevilaObrUr; | mind[191]:=ErrorComKlima[4].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[21],lo:=4382,hi:=4383); |  | 191:KlimaError[3].Kompresor2naMejiStevilaObrUr:=Bit_0; | 191:ErrorComKlima[4].Code[9]:=Byte_0; |  |  | 4383:PMM[1].Phase[3].Current[21]:=Real_0;
mind_bool[192]:=KlimaError[3].NapakaPriPretokuVode; | mind[192]:=ErrorComKlima[5].Code[0]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[22],lo:=4384,hi:=4385); |  | 192:KlimaError[3].NapakaPriPretokuVode:=Bit_0; | 192:ErrorComKlima[5].Code[0]:=Byte_0; |  |  | 4385:PMM[1].Phase[3].Current[22]:=Real_0;
mind_bool[193]:=KlimaError[3].NapakaPriPretokuZraka; | mind[193]:=ErrorComKlima[5].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[23],lo:=4386,hi:=4387); |  | 193:KlimaError[3].NapakaPriPretokuZraka:=Bit_0; | 193:ErrorComKlima[5].Code[10]:=Byte_0; |  |  | 4387:PMM[1].Phase[3].Current[23]:=Real_0;
mind_bool[194]:=KlimaError[3].NapakaSenzorVlaznosti; | mind[194]:=ErrorComKlima[5].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[24],lo:=4388,hi:=4389); |  | 194:KlimaError[3].NapakaSenzorVlaznosti:=Bit_0; | 194:ErrorComKlima[5].Code[11]:=Byte_0; |  |  | 4389:PMM[1].Phase[3].Current[24]:=Real_0;
mind_bool[195]:=KlimaError[3].NapakaTSTemperaturaProstora; | mind[195]:=ErrorComKlima[5].Code[12]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[25],lo:=4390,hi:=4391); |  | 195:KlimaError[3].NapakaTSTemperaturaProstora:=Bit_0; | 195:ErrorComKlima[5].Code[12]:=Byte_0; |  |  | 4391:PMM[1].Phase[3].Current[25]:=Real_0;
mind_bool[196]:=KlimaError[3].NapakaVlazilca; | mind[196]:=ErrorComKlima[5].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[26],lo:=4392,hi:=4393); |  | 196:KlimaError[3].NapakaVlazilca:=Bit_0; | 196:ErrorComKlima[5].Code[13]:=Byte_0; |  |  | 4393:PMM[1].Phase[3].Current[26]:=Real_0;
mind_bool[197]:=KlimaError[3].NizekPritiskKompresor1; | mind[197]:=ErrorComKlima[5].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[27],lo:=4394,hi:=4395); |  | 197:KlimaError[3].NizekPritiskKompresor1:=Bit_0; | 197:ErrorComKlima[5].Code[14]:=Byte_0; |  |  | 4395:PMM[1].Phase[3].Current[27]:=Real_0;
mind_bool[198]:=KlimaError[3].NizekPritiskKompresor2; | mind[198]:=ErrorComKlima[5].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[28],lo:=4396,hi:=4397); |  | 198:KlimaError[3].NizekPritiskKompresor2:=Bit_0; | 198:ErrorComKlima[5].Code[15]:=Byte_0; |  |  | 4397:PMM[1].Phase[3].Current[28]:=Real_0;
mind_bool[199]:=KlimaError[3].NizkaTempVProstoru; | mind[199]:=ErrorComKlima[5].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[29],lo:=4398,hi:=4399); |  | 199:KlimaError[3].NizkaTempVProstoru:=Bit_0; | 199:ErrorComKlima[5].Code[1]:=Byte_0; |  |  | 4399:PMM[1].Phase[3].Current[29]:=Real_0;
mind_bool[200]:=KlimaError[3].NizkaVlaznost; | mind[200]:=ErrorComKlima[5].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[2],lo:=4400,hi:=4401); |  | 200:KlimaError[3].NizkaVlaznost:=Bit_0; | 200:ErrorComKlima[5].Code[2]:=Byte_0; |  |  | 4401:PMM[1].Phase[3].Current[2]:=Real_0;
mind_bool[201]:=KlimaError[3].PozarniAlarm; | mind[201]:=ErrorComKlima[5].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[30],lo:=4402,hi:=4403); |  | 201:KlimaError[3].PozarniAlarm:=Bit_0; | 201:ErrorComKlima[5].Code[3]:=Byte_0; |  |  | 4403:PMM[1].Phase[3].Current[30]:=Real_0;
mind_bool[202]:=KlimaError[3].ThermalCutoutHeater1; | mind[202]:=ErrorComKlima[5].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[31],lo:=4404,hi:=4405); |  | 202:KlimaError[3].ThermalCutoutHeater1:=Bit_0; | 202:ErrorComKlima[5].Code[4]:=Byte_0; |  |  | 4405:PMM[1].Phase[3].Current[31]:=Real_0;
mind_bool[203]:=KlimaError[3].ThermalCutoutHeater2; | mind[203]:=ErrorComKlima[5].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[32],lo:=4406,hi:=4407); |  | 203:KlimaError[3].ThermalCutoutHeater2:=Bit_0; | 203:ErrorComKlima[5].Code[5]:=Byte_0; |  |  | 4407:PMM[1].Phase[3].Current[32]:=Real_0;
mind_bool[204]:=KlimaError[3].VentilatorNaMejiStevilaObrUr; | mind[204]:=ErrorComKlima[5].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[33],lo:=4408,hi:=4409); |  | 204:KlimaError[3].VentilatorNaMejiStevilaObrUr:=Bit_0; | 204:ErrorComKlima[5].Code[6]:=Byte_0; |  |  | 4409:PMM[1].Phase[3].Current[33]:=Real_0;
mind_bool[205]:=KlimaError[3].VisokaTempVProstoru; | mind[205]:=ErrorComKlima[5].Code[7]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[34],lo:=4410,hi:=4411); |  | 205:KlimaError[3].VisokaTempVProstoru:=Bit_0; | 205:ErrorComKlima[5].Code[7]:=Byte_0; |  |  | 4411:PMM[1].Phase[3].Current[34]:=Real_0;
mind_bool[206]:=KlimaError[3].VisokaVlaznost; | mind[206]:=ErrorComKlima[5].Code[8]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[35],lo:=4412,hi:=4413); |  | 206:KlimaError[3].VisokaVlaznost:=Bit_0; | 206:ErrorComKlima[5].Code[8]:=Byte_0; |  |  | 4413:PMM[1].Phase[3].Current[35]:=Real_0;
mind_bool[207]:=KlimaError[3].VisokPritiskKompresor1; | mind[207]:=ErrorComKlima[5].Code[9]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[36],lo:=4414,hi:=4415); |  | 207:KlimaError[3].VisokPritiskKompresor1:=Bit_0; | 207:ErrorComKlima[5].Code[9]:=Byte_0; |  |  | 4415:PMM[1].Phase[3].Current[36]:=Real_0;
mind_bool[208]:=KlimaError[3].VisokPritiskKompresor2; | mind[208]:=ErrorComKlima[6].Code[0]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[37],lo:=4416,hi:=4417); |  | 208:KlimaError[3].VisokPritiskKompresor2:=Bit_0; | 208:ErrorComKlima[6].Code[0]:=Byte_0; |  |  | 4417:PMM[1].Phase[3].Current[37]:=Real_0;
mind_bool[209]:=KlimaError[3].ZamasenFilter; | mind[209]:=ErrorComKlima[6].Code[10]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[38],lo:=4418,hi:=4419); |  | 209:KlimaError[3].ZamasenFilter:=Bit_0; | 209:ErrorComKlima[6].Code[10]:=Byte_0; |  |  | 4419:PMM[1].Phase[3].Current[38]:=Real_0;
mind_bool[210]:=KlimaError[3].ZunanjiAlarm; | mind[210]:=ErrorComKlima[6].Code[11]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[39],lo:=4420,hi:=4421); |  | 210:KlimaError[3].ZunanjiAlarm:=Bit_0; | 210:ErrorComKlima[6].Code[11]:=Byte_0; |  |  | 4421:PMM[1].Phase[3].Current[39]:=Real_0;
mind_bool[211]:=KlimaError[4].AlarmKompresor1; | mind[211]:=ErrorComKlima[6].Code[12]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[3],lo:=4422,hi:=4423); |  | 211:KlimaError[4].AlarmKompresor1:=Bit_0; | 211:ErrorComKlima[6].Code[12]:=Byte_0; |  |  | 4423:PMM[1].Phase[3].Current[3]:=Real_0;
mind_bool[212]:=KlimaError[4].AlarmKompresor2; | mind[212]:=ErrorComKlima[6].Code[13]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[40],lo:=4424,hi:=4425); |  | 212:KlimaError[4].AlarmKompresor2:=Bit_0; | 212:ErrorComKlima[6].Code[13]:=Byte_0; |  |  | 4425:PMM[1].Phase[3].Current[40]:=Real_0;
mind_bool[213]:=KlimaError[4].FenThermalCutout; | mind[213]:=ErrorComKlima[6].Code[14]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[41],lo:=4426,hi:=4427); |  | 213:KlimaError[4].FenThermalCutout:=Bit_0; | 213:ErrorComKlima[6].Code[14]:=Byte_0; |  |  | 4427:PMM[1].Phase[3].Current[41]:=Real_0;
mind_bool[214]:=KlimaError[4].IzlivVode; | mind[214]:=ErrorComKlima[6].Code[15]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[42],lo:=4428,hi:=4429); |  | 214:KlimaError[4].IzlivVode:=Bit_0; | 214:ErrorComKlima[6].Code[15]:=Byte_0; |  |  | 4429:PMM[1].Phase[3].Current[42]:=Real_0;
mind_bool[215]:=KlimaError[4].Kompresor1naMejiStevilaObrUr; | mind[215]:=ErrorComKlima[6].Code[1]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[4],lo:=4430,hi:=4431); |  | 215:KlimaError[4].Kompresor1naMejiStevilaObrUr:=Bit_0; | 215:ErrorComKlima[6].Code[1]:=Byte_0; |  |  | 4431:PMM[1].Phase[3].Current[4]:=Real_0;
mind_bool[216]:=KlimaError[4].Kompresor2naMejiStevilaObrUr; | mind[216]:=ErrorComKlima[6].Code[2]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[5],lo:=4432,hi:=4433); |  | 216:KlimaError[4].Kompresor2naMejiStevilaObrUr:=Bit_0; | 216:ErrorComKlima[6].Code[2]:=Byte_0; |  |  | 4433:PMM[1].Phase[3].Current[5]:=Real_0;
mind_bool[217]:=KlimaError[4].NapakaPriPretokuVode; | mind[217]:=ErrorComKlima[6].Code[3]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[6],lo:=4434,hi:=4435); |  | 217:KlimaError[4].NapakaPriPretokuVode:=Bit_0; | 217:ErrorComKlima[6].Code[3]:=Byte_0; |  |  | 4435:PMM[1].Phase[3].Current[6]:=Real_0;
mind_bool[218]:=KlimaError[4].NapakaPriPretokuZraka; | mind[218]:=ErrorComKlima[6].Code[4]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[7],lo:=4436,hi:=4437); |  | 218:KlimaError[4].NapakaPriPretokuZraka:=Bit_0; | 218:ErrorComKlima[6].Code[4]:=Byte_0; |  |  | 4437:PMM[1].Phase[3].Current[7]:=Real_0;
mind_bool[219]:=KlimaError[4].NapakaSenzorVlaznosti; | mind[219]:=ErrorComKlima[6].Code[5]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[8],lo:=4438,hi:=4439); |  | 219:KlimaError[4].NapakaSenzorVlaznosti:=Bit_0; | 219:ErrorComKlima[6].Code[5]:=Byte_0; |  |  | 4439:PMM[1].Phase[3].Current[8]:=Real_0;
mind_bool[220]:=KlimaError[4].NapakaTSTemperaturaProstora; | mind[220]:=ErrorComKlima[6].Code[6]; |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[9],lo:=4440,hi:=4441); |  | 220:KlimaError[4].NapakaTSTemperaturaProstora:=Bit_0; | 220:ErrorComKlima[6].Code[6]:=Byte_0; |  |  | 4441:PMM[1].Phase[3].Current[9]:=Real_0;
mind_bool[221]:=KlimaError[4].NapakaVlazilca; | mind[221]:=ErrorComKlima[6].Code[7]; |  |  | Read_Real(rVar:=PMM[1].PowerFactorSys,lo:=4442,hi:=4443); |  | 221:KlimaError[4].NapakaVlazilca:=Bit_0; | 221:ErrorComKlima[6].Code[7]:=Byte_0; |  |  | 4443:PMM[1].PowerFactorSys:=Real_0;
mind_bool[222]:=KlimaError[4].NizekPritiskKompresor1; | mind[222]:=ErrorComKlima[6].Code[8]; |  |  | Read_Real(rVar:=PMM[1].ReactiveEnergyConsumed_kVARh,lo:=4444,hi:=4445); |  | 222:KlimaError[4].NizekPritiskKompresor1:=Bit_0; | 222:ErrorComKlima[6].Code[8]:=Byte_0; |  |  | 4445:PMM[1].ReactiveEnergyConsumed_kVARh:=Real_0;
mind_bool[223]:=KlimaError[4].NizekPritiskKompresor2; | mind[223]:=ErrorComKlima[6].Code[9]; |  |  | Read_Real(rVar:=PMM[1].ReactivePowerPhaseA,lo:=4446,hi:=4447); |  | 223:KlimaError[4].NizekPritiskKompresor2:=Bit_0; | 223:ErrorComKlima[6].Code[9]:=Byte_0; |  |  | 4447:PMM[1].ReactivePowerPhaseA:=Real_0;
mind_bool[224]:=KlimaError[4].NizkaTempVProstoru; | mind[224]:=ErrorComPMM[1].Code[0]; |  |  | Read_Real(rVar:=PMM[1].ReactivePowerPhaseB,lo:=4448,hi:=4449); |  | 224:KlimaError[4].NizkaTempVProstoru:=Bit_0; | 224:ErrorComPMM[1].Code[0]:=Byte_0; |  |  | 4449:PMM[1].ReactivePowerPhaseB:=Real_0;
mind_bool[225]:=KlimaError[4].NizkaVlaznost; | mind[225]:=ErrorComPMM[1].Code[10]; |  |  | Read_Real(rVar:=PMM[1].ReactivePowerPhaseC,lo:=4450,hi:=4451); |  | 225:KlimaError[4].NizkaVlaznost:=Bit_0; | 225:ErrorComPMM[1].Code[10]:=Byte_0; |  |  | 4451:PMM[1].ReactivePowerPhaseC:=Real_0;
mind_bool[226]:=KlimaError[4].PozarniAlarm; | mind[226]:=ErrorComPMM[1].Code[11]; |  |  | Read_Real(rVar:=PMM[1].TotalActivePower_kW,lo:=4452,hi:=4453); |  | 226:KlimaError[4].PozarniAlarm:=Bit_0; | 226:ErrorComPMM[1].Code[11]:=Byte_0; |  |  | 4453:PMM[1].TotalActivePower_kW:=Real_0;
mind_bool[227]:=KlimaError[4].ThermalCutoutHeater1; | mind[227]:=ErrorComPMM[1].Code[12]; |  |  | Read_Real(rVar:=PMM[1].TotalAparentPower_kVA,lo:=4454,hi:=4455); |  | 227:KlimaError[4].ThermalCutoutHeater1:=Bit_0; | 227:ErrorComPMM[1].Code[12]:=Byte_0; |  |  | 4455:PMM[1].TotalAparentPower_kVA:=Real_0;
mind_bool[228]:=KlimaError[4].ThermalCutoutHeater2; | mind[228]:=ErrorComPMM[1].Code[13]; |  |  | Read_Real(rVar:=PMM[1].TotalPowerFactor,lo:=4456,hi:=4457); |  | 228:KlimaError[4].ThermalCutoutHeater2:=Bit_0; | 228:ErrorComPMM[1].Code[13]:=Byte_0; |  |  | 4457:PMM[1].TotalPowerFactor:=Real_0;
mind_bool[229]:=KlimaError[4].VentilatorNaMejiStevilaObrUr; | mind[229]:=ErrorComPMM[1].Code[14]; |  |  | Read_Real(rVar:=PMM[1].TotalReactivePower_kVAR,lo:=4458,hi:=4459); |  | 229:KlimaError[4].VentilatorNaMejiStevilaObrUr:=Bit_0; | 229:ErrorComPMM[1].Code[14]:=Byte_0; |  |  | 4459:PMM[1].TotalReactivePower_kVAR:=Real_0;
mind_bool[230]:=KlimaError[4].VisokaTempVProstoru; | mind[230]:=ErrorComPMM[1].Code[15]; |  |  | Read_Real(rVar:=PMM[1].VirA_fsys,lo:=4460,hi:=4461); |  | 230:KlimaError[4].VisokaTempVProstoru:=Bit_0; | 230:ErrorComPMM[1].Code[15]:=Byte_0; |  |  | 4461:PMM[1].VirA_fsys:=Real_0;
mind_bool[231]:=KlimaError[4].VisokaVlaznost; | mind[231]:=ErrorComPMM[1].Code[1]; |  |  | Read_Real(rVar:=PMM[1].VirA_Isys,lo:=4462,hi:=4463); |  | 231:KlimaError[4].VisokaVlaznost:=Bit_0; | 231:ErrorComPMM[1].Code[1]:=Byte_0; |  |  | 4463:PMM[1].VirA_Isys:=Real_0;
mind_bool[232]:=KlimaError[4].VisokPritiskKompresor1; | mind[232]:=ErrorComPMM[1].Code[2]; |  |  | Read_Real(rVar:=PMM[1].VirA_PFsys,lo:=4464,hi:=4465); |  | 232:KlimaError[4].VisokPritiskKompresor1:=Bit_0; | 232:ErrorComPMM[1].Code[2]:=Byte_0; |  |  | 4465:PMM[1].VirA_PFsys:=Real_0;
mind_bool[233]:=KlimaError[4].VisokPritiskKompresor2; | mind[233]:=ErrorComPMM[1].Code[3]; |  |  | Read_Real(rVar:=PMM[1].VirA_Psys,lo:=4466,hi:=4467); |  | 233:KlimaError[4].VisokPritiskKompresor2:=Bit_0; | 233:ErrorComPMM[1].Code[3]:=Byte_0; |  |  | 4467:PMM[1].VirA_Psys:=Real_0;
mind_bool[234]:=KlimaError[4].ZamasenFilter; | mind[234]:=ErrorComPMM[1].Code[4]; |  |  | Read_Real(rVar:=PMM[1].VirA_Qsys,lo:=4468,hi:=4469); |  | 234:KlimaError[4].ZamasenFilter:=Bit_0; | 234:ErrorComPMM[1].Code[4]:=Byte_0; |  |  | 4469:PMM[1].VirA_Qsys:=Real_0;
mind_bool[235]:=KlimaError[4].ZunanjiAlarm; | mind[235]:=ErrorComPMM[1].Code[5]; |  |  | Read_Real(rVar:=PMM[1].VirA_Ssys,lo:=4470,hi:=4471); |  | 235:KlimaError[4].ZunanjiAlarm:=Bit_0; | 235:ErrorComPMM[1].Code[5]:=Byte_0; |  |  | 4471:PMM[1].VirA_Ssys:=Real_0;
mind_bool[236]:=KlimaError[5].AlarmKompresor1; | mind[236]:=ErrorComPMM[1].Code[6]; |  |  | Read_Real(rVar:=PMM[1].VirA_Usys,lo:=4472,hi:=4473); |  | 236:KlimaError[5].AlarmKompresor1:=Bit_0; | 236:ErrorComPMM[1].Code[6]:=Byte_0; |  |  | 4473:PMM[1].VirA_Usys:=Real_0;
mind_bool[237]:=KlimaError[5].AlarmKompresor2; | mind[237]:=ErrorComPMM[1].Code[7]; |  |  | Read_Real(rVar:=PMM[1].VirB_fsys,lo:=4474,hi:=4475); |  | 237:KlimaError[5].AlarmKompresor2:=Bit_0; | 237:ErrorComPMM[1].Code[7]:=Byte_0; |  |  | 4475:PMM[1].VirB_fsys:=Real_0;
mind_bool[238]:=KlimaError[5].FenThermalCutout; | mind[238]:=ErrorComPMM[1].Code[8]; |  |  | Read_Real(rVar:=PMM[1].VirB_Isys,lo:=4476,hi:=4477); |  | 238:KlimaError[5].FenThermalCutout:=Bit_0; | 238:ErrorComPMM[1].Code[8]:=Byte_0; |  |  | 4477:PMM[1].VirB_Isys:=Real_0;
mind_bool[239]:=KlimaError[5].IzlivVode; | mind[239]:=ErrorComPMM[1].Code[9]; |  |  | Read_Real(rVar:=PMM[1].VirB_PFsys,lo:=4478,hi:=4479); |  | 239:KlimaError[5].IzlivVode:=Bit_0; | 239:ErrorComPMM[1].Code[9]:=Byte_0; |  |  | 4479:PMM[1].VirB_PFsys:=Real_0;
mind_bool[240]:=KlimaError[5].Kompresor1naMejiStevilaObrUr; | mind[240]:=ErrorComPMM[2].Code[0]; |  |  | Read_Real(rVar:=PMM[1].VirB_Psys,lo:=4480,hi:=4481); |  | 240:KlimaError[5].Kompresor1naMejiStevilaObrUr:=Bit_0; | 240:ErrorComPMM[2].Code[0]:=Byte_0; |  |  | 4481:PMM[1].VirB_Psys:=Real_0;
mind_bool[241]:=KlimaError[5].Kompresor2naMejiStevilaObrUr; | mind[241]:=ErrorComPMM[2].Code[10]; |  |  | Read_Real(rVar:=PMM[1].VirB_Qsys,lo:=4482,hi:=4483); |  | 241:KlimaError[5].Kompresor2naMejiStevilaObrUr:=Bit_0; | 241:ErrorComPMM[2].Code[10]:=Byte_0; |  |  | 4483:PMM[1].VirB_Qsys:=Real_0;
mind_bool[242]:=KlimaError[5].NapakaPriPretokuVode; | mind[242]:=ErrorComPMM[2].Code[11]; |  |  | Read_Real(rVar:=PMM[1].VirB_Ssys,lo:=4484,hi:=4485); |  | 242:KlimaError[5].NapakaPriPretokuVode:=Bit_0; | 242:ErrorComPMM[2].Code[11]:=Byte_0; |  |  | 4485:PMM[1].VirB_Ssys:=Real_0;
mind_bool[243]:=KlimaError[5].NapakaPriPretokuZraka; | mind[243]:=ErrorComPMM[2].Code[12]; |  |  | Read_Real(rVar:=PMM[1].VirB_Usys,lo:=4486,hi:=4487); |  | 243:KlimaError[5].NapakaPriPretokuZraka:=Bit_0; | 243:ErrorComPMM[2].Code[12]:=Byte_0; |  |  | 4487:PMM[1].VirB_Usys:=Real_0;
mind_bool[244]:=KlimaError[5].NapakaSenzorVlaznosti; | mind[244]:=ErrorComPMM[2].Code[13]; |  |  | Read_Real(rVar:=PMM[1].VirBActiveEnergyConsumed_kWh,lo:=4488,hi:=4489); |  | 244:KlimaError[5].NapakaSenzorVlaznosti:=Bit_0; | 244:ErrorComPMM[2].Code[13]:=Byte_0; |  |  | 4489:PMM[1].VirBActiveEnergyConsumed_kWh:=Real_0;
mind_bool[245]:=KlimaError[5].NapakaTSTemperaturaProstora; | mind[245]:=ErrorComPMM[2].Code[14]; |  |  | Read_Real(rVar:=PMM[1].VirBActivePowerPhaseA_kW,lo:=4490,hi:=4491); |  | 245:KlimaError[5].NapakaTSTemperaturaProstora:=Bit_0; | 245:ErrorComPMM[2].Code[14]:=Byte_0; |  |  | 4491:PMM[1].VirBActivePowerPhaseA_kW:=Real_0;
mind_bool[246]:=KlimaError[5].NapakaVlazilca; | mind[246]:=ErrorComPMM[2].Code[15]; |  |  | Read_Real(rVar:=PMM[1].VirBActivePowerPhaseB_kW,lo:=4492,hi:=4493); |  | 246:KlimaError[5].NapakaVlazilca:=Bit_0; | 246:ErrorComPMM[2].Code[15]:=Byte_0; |  |  | 4493:PMM[1].VirBActivePowerPhaseB_kW:=Real_0;
mind_bool[247]:=KlimaError[5].NizekPritiskKompresor1; | mind[247]:=ErrorComPMM[2].Code[1]; |  |  | Read_Real(rVar:=PMM[1].VirBActivePowerPhaseC_kW,lo:=4494,hi:=4495); |  | 247:KlimaError[5].NizekPritiskKompresor1:=Bit_0; | 247:ErrorComPMM[2].Code[1]:=Byte_0; |  |  | 4495:PMM[1].VirBActivePowerPhaseC_kW:=Real_0;
mind_bool[248]:=KlimaError[5].NizekPritiskKompresor2; | mind[248]:=ErrorComPMM[2].Code[2]; |  |  | Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseA,lo:=4496,hi:=4497); |  | 248:KlimaError[5].NizekPritiskKompresor2:=Bit_0; | 248:ErrorComPMM[2].Code[2]:=Byte_0; |  |  | 4497:PMM[1].VirBAparentPowerPhaseA:=Real_0;
mind_bool[249]:=KlimaError[5].NizkaTempVProstoru; | mind[249]:=ErrorComPMM[2].Code[3]; |  |  | Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseB,lo:=4498,hi:=4499); |  | 249:KlimaError[5].NizkaTempVProstoru:=Bit_0; | 249:ErrorComPMM[2].Code[3]:=Byte_0; |  |  | 4499:PMM[1].VirBAparentPowerPhaseB:=Real_0;
mind_bool[250]:=KlimaError[5].NizkaVlaznost; | mind[250]:=ErrorComPMM[2].Code[4]; |  |  | Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseC,lo:=4500,hi:=4501); |  | 250:KlimaError[5].NizkaVlaznost:=Bit_0; | 250:ErrorComPMM[2].Code[4]:=Byte_0; |  |  | 4501:PMM[1].VirBAparentPowerPhaseC:=Real_0;
mind_bool[251]:=KlimaError[5].PozarniAlarm; | mind[251]:=ErrorComPMM[2].Code[5]; |  |  | Read_Real(rVar:=PMM[1].VirBAverageCurrent_A,lo:=4502,hi:=4503); |  | 251:KlimaError[5].PozarniAlarm:=Bit_0; | 251:ErrorComPMM[2].Code[5]:=Byte_0; |  |  | 4503:PMM[1].VirBAverageCurrent_A:=Real_0;
mind_bool[252]:=KlimaError[5].ThermalCutoutHeater1; | mind[252]:=ErrorComPMM[2].Code[6]; |  |  | Read_Real(rVar:=PMM[1].VirBAveragePhaseToNeutral_V,lo:=4504,hi:=4505); |  | 252:KlimaError[5].ThermalCutoutHeater1:=Bit_0; | 252:ErrorComPMM[2].Code[6]:=Byte_0; |  |  | 4505:PMM[1].VirBAveragePhaseToNeutral_V:=Real_0;
mind_bool[253]:=KlimaError[5].ThermalCutoutHeater2; | mind[253]:=ErrorComPMM[2].Code[7]; |  |  | Read_Real(rVar:=PMM[1].VirBAveragePhaseToPhase_V,lo:=4506,hi:=4507); |  | 253:KlimaError[5].ThermalCutoutHeater2:=Bit_0; | 253:ErrorComPMM[2].Code[7]:=Byte_0; |  |  | 4507:PMM[1].VirBAveragePhaseToPhase_V:=Real_0;
mind_bool[254]:=KlimaError[5].VentilatorNaMejiStevilaObrUr; | mind[254]:=ErrorComPMM[2].Code[8]; |  |  | Read_Real(rVar:=PMM[1].VirBCurrentInPhaseA_A,lo:=4508,hi:=4509); |  | 254:KlimaError[5].VentilatorNaMejiStevilaObrUr:=Bit_0; | 254:ErrorComPMM[2].Code[8]:=Byte_0; |  |  | 4509:PMM[1].VirBCurrentInPhaseA_A:=Real_0;
mind_bool[255]:=KlimaError[5].VisokaTempVProstoru; | mind[255]:=ErrorComPMM[2].Code[9]; |  |  | Read_Real(rVar:=PMM[1].VirBCurrentInPhaseB_A,lo:=4510,hi:=4511); |  | 255:KlimaError[5].VisokaTempVProstoru:=Bit_0; | 255:ErrorComPMM[2].Code[9]:=Byte_0; |  |  | 4511:PMM[1].VirBCurrentInPhaseB_A:=Real_0;
mind_bool[256]:=KlimaError[5].VisokaVlaznost; | mind[256]:=kom_nast_cas_izpada; |  |  | Read_Real(rVar:=PMM[1].VirBCurrentInPhaseC_A,lo:=4512,hi:=4513); |  | 256:KlimaError[5].VisokaVlaznost:=Bit_0; | 256:kom_nast_cas_izpada:=Word_01; |  |  | 4513:PMM[1].VirBCurrentInPhaseC_A:=Real_0;
mind_bool[257]:=KlimaError[5].VisokPritiskKompresor1; |  |  |  | Read_Real(rVar:=PMM[1].VirBFrequency_Hz,lo:=4514,hi:=4515); |  | 257:KlimaError[5].VisokPritiskKompresor1:=Bit_0; |  |  |  | 4515:PMM[1].VirBFrequency_Hz:=Real_0;
mind_bool[258]:=KlimaError[5].VisokPritiskKompresor2; |  |  |  | Read_Real(rVar:=PMM[1].VirBPowerFactorSys,lo:=4516,hi:=4517); |  | 258:KlimaError[5].VisokPritiskKompresor2:=Bit_0; |  |  |  | 4517:PMM[1].VirBPowerFactorSys:=Real_0;
mind_bool[259]:=KlimaError[5].ZamasenFilter; |  |  |  | Read_Real(rVar:=PMM[1].VirBReactiveEnergyConsumed_kVARh,lo:=4518,hi:=4519); |  | 259:KlimaError[5].ZamasenFilter:=Bit_0; |  |  |  | 4519:PMM[1].VirBReactiveEnergyConsumed_kVARh:=Real_0;
mind_bool[260]:=KlimaError[5].ZunanjiAlarm; |  |  |  | Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseA,lo:=4520,hi:=4521); |  | 260:KlimaError[5].ZunanjiAlarm:=Bit_0; |  |  |  | 4521:PMM[1].VirBReactivePowerPhaseA:=Real_0;
mind_bool[261]:=KlimaError[6].AlarmKompresor1; |  |  |  | Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseB,lo:=4522,hi:=4523); |  | 261:KlimaError[6].AlarmKompresor1:=Bit_0; |  |  |  | 4523:PMM[1].VirBReactivePowerPhaseB:=Real_0;
mind_bool[262]:=KlimaError[6].AlarmKompresor2; |  |  |  | Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseC,lo:=4524,hi:=4525); |  | 262:KlimaError[6].AlarmKompresor2:=Bit_0; |  |  |  | 4525:PMM[1].VirBReactivePowerPhaseC:=Real_0;
mind_bool[263]:=KlimaError[6].FenThermalCutout; |  |  |  | Read_Real(rVar:=PMM[1].VirBTotalActivePower_kW,lo:=4526,hi:=4527); |  | 263:KlimaError[6].FenThermalCutout:=Bit_0; |  |  |  | 4527:PMM[1].VirBTotalActivePower_kW:=Real_0;
mind_bool[264]:=KlimaError[6].IzlivVode; |  |  |  | Read_Real(rVar:=PMM[1].VirBTotalAparentPower_kVA,lo:=4528,hi:=4529); |  | 264:KlimaError[6].IzlivVode:=Bit_0; |  |  |  | 4529:PMM[1].VirBTotalAparentPower_kVA:=Real_0;
mind_bool[265]:=KlimaError[6].Kompresor1naMejiStevilaObrUr; |  |  |  | Read_Real(rVar:=PMM[1].VirBTotalPowerFactor,lo:=4530,hi:=4531); |  | 265:KlimaError[6].Kompresor1naMejiStevilaObrUr:=Bit_0; |  |  |  | 4531:PMM[1].VirBTotalPowerFactor:=Real_0;
mind_bool[266]:=KlimaError[6].Kompresor2naMejiStevilaObrUr; |  |  |  | Read_Real(rVar:=PMM[1].VirBTotalReactivePower_kVAR,lo:=4532,hi:=4533); |  | 266:KlimaError[6].Kompresor2naMejiStevilaObrUr:=Bit_0; |  |  |  | 4533:PMM[1].VirBTotalReactivePower_kVAR:=Real_0;
mind_bool[267]:=KlimaError[6].NapakaPriPretokuVode; |  |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseAB_V,lo:=4534,hi:=4535); |  | 267:KlimaError[6].NapakaPriPretokuVode:=Bit_0; |  |  |  | 4535:PMM[1].VirBVoltageBetweenPhaseAB_V:=Real_0;
mind_bool[268]:=KlimaError[6].NapakaPriPretokuZraka; |  |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseAN_V,lo:=4536,hi:=4537); |  | 268:KlimaError[6].NapakaPriPretokuZraka:=Bit_0; |  |  |  | 4537:PMM[1].VirBVoltageBetweenPhaseAN_V:=Real_0;
mind_bool[269]:=KlimaError[6].NapakaSenzorVlaznosti; |  |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseBC_V,lo:=4538,hi:=4539); |  | 269:KlimaError[6].NapakaSenzorVlaznosti:=Bit_0; |  |  |  | 4539:PMM[1].VirBVoltageBetweenPhaseBC_V:=Real_0;
mind_bool[270]:=KlimaError[6].NapakaTSTemperaturaProstora; |  |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseBN_V,lo:=4540,hi:=4541); |  | 270:KlimaError[6].NapakaTSTemperaturaProstora:=Bit_0; |  |  |  | 4541:PMM[1].VirBVoltageBetweenPhaseBN_V:=Real_0;
mind_bool[271]:=KlimaError[6].NapakaVlazilca; |  |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseCA_V,lo:=4542,hi:=4543); |  | 271:KlimaError[6].NapakaVlazilca:=Bit_0; |  |  |  | 4543:PMM[1].VirBVoltageBetweenPhaseCA_V:=Real_0;
mind_bool[272]:=KlimaError[6].NizekPritiskKompresor1; |  |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseCN_V,lo:=4544,hi:=4545); |  | 272:KlimaError[6].NizekPritiskKompresor1:=Bit_0; |  |  |  | 4545:PMM[1].VirBVoltageBetweenPhaseCN_V:=Real_0;
mind_bool[273]:=KlimaError[6].NizekPritiskKompresor2; |  |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseAB_V,lo:=4546,hi:=4547); |  | 273:KlimaError[6].NizekPritiskKompresor2:=Bit_0; |  |  |  | 4547:PMM[1].VoltageBetweenPhaseAB_V:=Real_0;
mind_bool[274]:=KlimaError[6].NizkaTempVProstoru; |  |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseAN_V,lo:=4548,hi:=4549); |  | 274:KlimaError[6].NizkaTempVProstoru:=Bit_0; |  |  |  | 4549:PMM[1].VoltageBetweenPhaseAN_V:=Real_0;
mind_bool[275]:=KlimaError[6].NizkaVlaznost; |  |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseBC_V,lo:=4550,hi:=4551); |  | 275:KlimaError[6].NizkaVlaznost:=Bit_0; |  |  |  | 4551:PMM[1].VoltageBetweenPhaseBC_V:=Real_0;
mind_bool[276]:=KlimaError[6].PozarniAlarm; |  |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseBN_V,lo:=4552,hi:=4553); |  | 276:KlimaError[6].PozarniAlarm:=Bit_0; |  |  |  | 4553:PMM[1].VoltageBetweenPhaseBN_V:=Real_0;
mind_bool[277]:=KlimaError[6].ThermalCutoutHeater1; |  |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseCA_V,lo:=4554,hi:=4555); |  | 277:KlimaError[6].ThermalCutoutHeater1:=Bit_0; |  |  |  | 4555:PMM[1].VoltageBetweenPhaseCA_V:=Real_0;
mind_bool[278]:=KlimaError[6].ThermalCutoutHeater2; |  |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseCN_V,lo:=4556,hi:=4557); |  | 278:KlimaError[6].ThermalCutoutHeater2:=Bit_0; |  |  |  | 4557:PMM[1].VoltageBetweenPhaseCN_V:=Real_0;
mind_bool[279]:=KlimaError[6].VentilatorNaMejiStevilaObrUr; |  |  |  | Read_Real(rVar:=PMM[2].ActiveEnergyConsumed_kWh,lo:=4558,hi:=4559); |  | 279:KlimaError[6].VentilatorNaMejiStevilaObrUr:=Bit_0; |  |  |  | 4559:PMM[2].ActiveEnergyConsumed_kWh:=Real_0;
mind_bool[280]:=KlimaError[6].VisokaTempVProstoru; |  |  |  | Read_Real(rVar:=PMM[2].ActivePowerPhaseA_kW,lo:=4560,hi:=4561); |  | 280:KlimaError[6].VisokaTempVProstoru:=Bit_0; |  |  |  | 4561:PMM[2].ActivePowerPhaseA_kW:=Real_0;
mind_bool[281]:=KlimaError[6].VisokaVlaznost; |  |  |  | Read_Real(rVar:=PMM[2].ActivePowerPhaseB_kW,lo:=4562,hi:=4563); |  | 281:KlimaError[6].VisokaVlaznost:=Bit_0; |  |  |  | 4563:PMM[2].ActivePowerPhaseB_kW:=Real_0;
mind_bool[282]:=KlimaError[6].VisokPritiskKompresor1; |  |  |  | Read_Real(rVar:=PMM[2].ActivePowerPhaseC_kW,lo:=4564,hi:=4565); |  | 282:KlimaError[6].VisokPritiskKompresor1:=Bit_0; |  |  |  | 4565:PMM[2].ActivePowerPhaseC_kW:=Real_0;
mind_bool[283]:=KlimaError[6].VisokPritiskKompresor2; |  |  |  | Read_Real(rVar:=PMM[2].AparentPowerPhaseA,lo:=4566,hi:=4567); |  | 283:KlimaError[6].VisokPritiskKompresor2:=Bit_0; |  |  |  | 4567:PMM[2].AparentPowerPhaseA:=Real_0;
mind_bool[284]:=KlimaError[6].ZamasenFilter; |  |  |  | Read_Real(rVar:=PMM[2].AparentPowerPhaseB,lo:=4568,hi:=4569); |  | 284:KlimaError[6].ZamasenFilter:=Bit_0; |  |  |  | 4569:PMM[2].AparentPowerPhaseB:=Real_0;
mind_bool[285]:=KlimaError[6].ZunanjiAlarm; |  |  |  | Read_Real(rVar:=PMM[2].AparentPowerPhaseC,lo:=4570,hi:=4571); |  | 285:KlimaError[6].ZunanjiAlarm:=Bit_0; |  |  |  | 4571:PMM[2].AparentPowerPhaseC:=Real_0;
mind_bool[286]:=NacDeloKlima1_2Avtom; |  |  |  | Read_Real(rVar:=PMM[2].AverageCurrent_A,lo:=4572,hi:=4573); |  | 286:NacDeloKlima1_2Avtom:=Bit_0; |  |  |  | 4573:PMM[2].AverageCurrent_A:=Real_0;
mind_bool[287]:=NacDeloKlima3_4Avtom; |  |  |  | Read_Real(rVar:=PMM[2].AveragePhaseToNeutral_V,lo:=4574,hi:=4575); |  | 287:NacDeloKlima3_4Avtom:=Bit_0; |  |  |  | 4575:PMM[2].AveragePhaseToNeutral_V:=Real_0;
mind_bool[288]:=NacDeloKlima5_6Avtom; |  |  |  | Read_Real(rVar:=PMM[2].AveragePhaseToPhase_V,lo:=4576,hi:=4577); |  | 288:NacDeloKlima5_6Avtom:=Bit_0; |  |  |  | 4577:PMM[2].AveragePhaseToPhase_V:=Real_0;
mind_bool[289]:=NapakaSenzorTemp1; |  |  |  | Read_Real(rVar:=PMM[2].CurrentInPhaseA_A,lo:=4578,hi:=4579); |  | 289:NapakaSenzorTemp1:=Bit_0; |  |  |  | 4579:PMM[2].CurrentInPhaseA_A:=Real_0;
mind_bool[290]:=NapakaSenzorTemp2; |  |  |  | Read_Real(rVar:=PMM[2].CurrentInPhaseB_A,lo:=4580,hi:=4581); |  | 290:NapakaSenzorTemp2:=Bit_0; |  |  |  | 4581:PMM[2].CurrentInPhaseB_A:=Real_0;
mind_bool[291]:=NapakaSenzorTemp3; |  |  |  | Read_Real(rVar:=PMM[2].CurrentInPhaseC_A,lo:=4582,hi:=4583); |  | 291:NapakaSenzorTemp3:=Bit_0; |  |  |  | 4583:PMM[2].CurrentInPhaseC_A:=Real_0;
mind_bool[292]:=NapakaSenzorTemp4; |  |  |  | Read_Real(rVar:=PMM[2].Frequency_Hz,lo:=4584,hi:=4585); |  | 292:NapakaSenzorTemp4:=Bit_0; |  |  |  | 4585:PMM[2].Frequency_Hz:=Real_0;
mind_bool[293]:=NapakaSenzorVlaga1; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[1],lo:=4586,hi:=4587); |  | 293:NapakaSenzorVlaga1:=Bit_0; |  |  |  | 4587:PMM[2].Phase[1].Current[1]:=Real_0;
mind_bool[294]:=NapakaSenzorVlaga2; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[2],lo:=4588,hi:=4589); |  | 294:NapakaSenzorVlaga2:=Bit_0; |  |  |  | 4589:PMM[2].Phase[1].Current[2]:=Real_0;
mind_bool[295]:=NapakaSenzorVlaga3; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[3],lo:=4590,hi:=4591); |  | 295:NapakaSenzorVlaga3:=Bit_0; |  |  |  | 4591:PMM[2].Phase[1].Current[3]:=Real_0;
mind_bool[296]:=NapakaSenzorVlaga4; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[4],lo:=4592,hi:=4593); |  | 296:NapakaSenzorVlaga4:=Bit_0; |  |  |  | 4593:PMM[2].Phase[1].Current[4]:=Real_0;
mind_bool[297]:=NastaviCasNaKrmilniku; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[5],lo:=4594,hi:=4595); |  | 297:NastaviCasNaKrmilniku:=Bit_0; |  |  |  | 4595:PMM[2].Phase[1].Current[5]:=Real_0;
mind_bool[298]:=NastavitevUreKrUspesna; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[6],lo:=4596,hi:=4597); |  | 298:NastavitevUreKrUspesna:=Bit_0; |  |  |  | 4597:PMM[2].Phase[1].Current[6]:=Real_0;
mind_bool[299]:=OpozoriloBaterijaPLC; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[7],lo:=4598,hi:=4599); |  | 299:OpozoriloBaterijaPLC:=Bit_0; |  |  |  | 4599:PMM[2].Phase[1].Current[7]:=Real_0;
mind_bool[300]:=OpozoriloPMM2x17med60in80[10]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[8],lo:=4600,hi:=4601); |  | 300:OpozoriloPMM2x17med60in80[10]:=Bit_0; |  |  |  | 4601:PMM[2].Phase[1].Current[8]:=Real_0;
mind_bool[301]:=OpozoriloPMM2x17med60in80[11]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[9],lo:=4602,hi:=4603); |  | 301:OpozoriloPMM2x17med60in80[11]:=Bit_0; |  |  |  | 4603:PMM[2].Phase[1].Current[9]:=Real_0;
mind_bool[302]:=OpozoriloPMM2x17med60in80[12]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[10],lo:=4604,hi:=4605); |  | 302:OpozoriloPMM2x17med60in80[12]:=Bit_0; |  |  |  | 4605:PMM[2].Phase[1].Current[10]:=Real_0;
mind_bool[303]:=OpozoriloPMM2x17med60in80[13]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[11],lo:=4606,hi:=4607); |  | 303:OpozoriloPMM2x17med60in80[13]:=Bit_0; |  |  |  | 4607:PMM[2].Phase[1].Current[11]:=Real_0;
mind_bool[304]:=OpozoriloPMM2x17med60in80[14]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[12],lo:=4608,hi:=4609); |  | 304:OpozoriloPMM2x17med60in80[14]:=Bit_0; |  |  |  | 4609:PMM[2].Phase[1].Current[12]:=Real_0;
mind_bool[305]:=OpozoriloPMM2x17med60in80[15]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[13],lo:=4610,hi:=4611); |  | 305:OpozoriloPMM2x17med60in80[15]:=Bit_0; |  |  |  | 4611:PMM[2].Phase[1].Current[13]:=Real_0;
mind_bool[306]:=OpozoriloPMM2x17med60in80[16]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[14],lo:=4612,hi:=4613); |  | 306:OpozoriloPMM2x17med60in80[16]:=Bit_0; |  |  |  | 4613:PMM[2].Phase[1].Current[14]:=Real_0;
mind_bool[307]:=OpozoriloPMM2x17med60in80[17]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[15],lo:=4614,hi:=4615); |  | 307:OpozoriloPMM2x17med60in80[17]:=Bit_0; |  |  |  | 4615:PMM[2].Phase[1].Current[15]:=Real_0;
mind_bool[308]:=OpozoriloPMM2x17med60in80[18]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[16],lo:=4616,hi:=4617); |  | 308:OpozoriloPMM2x17med60in80[18]:=Bit_0; |  |  |  | 4617:PMM[2].Phase[1].Current[16]:=Real_0;
mind_bool[309]:=OpozoriloPMM2x17med60in80[19]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[17],lo:=4618,hi:=4619); |  | 309:OpozoriloPMM2x17med60in80[19]:=Bit_0; |  |  |  | 4619:PMM[2].Phase[1].Current[17]:=Real_0;
mind_bool[310]:=OpozoriloPMM2x17med60in80[1]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[18],lo:=4620,hi:=4621); |  | 310:OpozoriloPMM2x17med60in80[1]:=Bit_0; |  |  |  | 4621:PMM[2].Phase[1].Current[18]:=Real_0;
mind_bool[311]:=OpozoriloPMM2x17med60in80[20]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[19],lo:=4622,hi:=4623); |  | 311:OpozoriloPMM2x17med60in80[20]:=Bit_0; |  |  |  | 4623:PMM[2].Phase[1].Current[19]:=Real_0;
mind_bool[312]:=OpozoriloPMM2x17med60in80[21]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[20],lo:=4624,hi:=4625); |  | 312:OpozoriloPMM2x17med60in80[21]:=Bit_0; |  |  |  | 4625:PMM[2].Phase[1].Current[20]:=Real_0;
mind_bool[313]:=OpozoriloPMM2x17med60in80[22]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[21],lo:=4626,hi:=4627); |  | 313:OpozoriloPMM2x17med60in80[22]:=Bit_0; |  |  |  | 4627:PMM[2].Phase[1].Current[21]:=Real_0;
mind_bool[314]:=OpozoriloPMM2x17med60in80[23]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[22],lo:=4628,hi:=4629); |  | 314:OpozoriloPMM2x17med60in80[23]:=Bit_0; |  |  |  | 4629:PMM[2].Phase[1].Current[22]:=Real_0;
mind_bool[315]:=OpozoriloPMM2x17med60in80[24]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[23],lo:=4630,hi:=4631); |  | 315:OpozoriloPMM2x17med60in80[24]:=Bit_0; |  |  |  | 4631:PMM[2].Phase[1].Current[23]:=Real_0;
mind_bool[316]:=OpozoriloPMM2x17med60in80[25]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[24],lo:=4632,hi:=4633); |  | 316:OpozoriloPMM2x17med60in80[25]:=Bit_0; |  |  |  | 4633:PMM[2].Phase[1].Current[24]:=Real_0;
mind_bool[317]:=OpozoriloPMM2x17med60in80[26]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[25],lo:=4634,hi:=4635); |  | 317:OpozoriloPMM2x17med60in80[26]:=Bit_0; |  |  |  | 4635:PMM[2].Phase[1].Current[25]:=Real_0;
mind_bool[318]:=OpozoriloPMM2x17med60in80[27]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[26],lo:=4636,hi:=4637); |  | 318:OpozoriloPMM2x17med60in80[27]:=Bit_0; |  |  |  | 4637:PMM[2].Phase[1].Current[26]:=Real_0;
mind_bool[319]:=OpozoriloPMM2x17med60in80[28]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[27],lo:=4638,hi:=4639); |  | 319:OpozoriloPMM2x17med60in80[28]:=Bit_0; |  |  |  | 4639:PMM[2].Phase[1].Current[27]:=Real_0;
mind_bool[320]:=OpozoriloPMM2x17med60in80[29]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[28],lo:=4640,hi:=4641); |  | 320:OpozoriloPMM2x17med60in80[29]:=Bit_0; |  |  |  | 4641:PMM[2].Phase[1].Current[28]:=Real_0;
mind_bool[321]:=OpozoriloPMM2x17med60in80[2]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[29],lo:=4642,hi:=4643); |  | 321:OpozoriloPMM2x17med60in80[2]:=Bit_0; |  |  |  | 4643:PMM[2].Phase[1].Current[29]:=Real_0;
mind_bool[322]:=OpozoriloPMM2x17med60in80[30]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[30],lo:=4644,hi:=4645); |  | 322:OpozoriloPMM2x17med60in80[30]:=Bit_0; |  |  |  | 4645:PMM[2].Phase[1].Current[30]:=Real_0;
mind_bool[323]:=OpozoriloPMM2x17med60in80[31]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[31],lo:=4646,hi:=4647); |  | 323:OpozoriloPMM2x17med60in80[31]:=Bit_0; |  |  |  | 4647:PMM[2].Phase[1].Current[31]:=Real_0;
mind_bool[324]:=OpozoriloPMM2x17med60in80[32]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[32],lo:=4648,hi:=4649); |  | 324:OpozoriloPMM2x17med60in80[32]:=Bit_0; |  |  |  | 4649:PMM[2].Phase[1].Current[32]:=Real_0;
mind_bool[325]:=OpozoriloPMM2x17med60in80[33]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[33],lo:=4650,hi:=4651); |  | 325:OpozoriloPMM2x17med60in80[33]:=Bit_0; |  |  |  | 4651:PMM[2].Phase[1].Current[33]:=Real_0;
mind_bool[326]:=OpozoriloPMM2x17med60in80[34]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[34],lo:=4652,hi:=4653); |  | 326:OpozoriloPMM2x17med60in80[34]:=Bit_0; |  |  |  | 4653:PMM[2].Phase[1].Current[34]:=Real_0;
mind_bool[327]:=OpozoriloPMM2x17med60in80[35]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[35],lo:=4654,hi:=4655); |  | 327:OpozoriloPMM2x17med60in80[35]:=Bit_0; |  |  |  | 4655:PMM[2].Phase[1].Current[35]:=Real_0;
mind_bool[328]:=OpozoriloPMM2x17med60in80[36]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[36],lo:=4656,hi:=4657); |  | 328:OpozoriloPMM2x17med60in80[36]:=Bit_0; |  |  |  | 4657:PMM[2].Phase[1].Current[36]:=Real_0;
mind_bool[329]:=OpozoriloPMM2x17med60in80[37]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[37],lo:=4658,hi:=4659); |  | 329:OpozoriloPMM2x17med60in80[37]:=Bit_0; |  |  |  | 4659:PMM[2].Phase[1].Current[37]:=Real_0;
mind_bool[330]:=OpozoriloPMM2x17med60in80[38]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[38],lo:=4660,hi:=4661); |  | 330:OpozoriloPMM2x17med60in80[38]:=Bit_0; |  |  |  | 4661:PMM[2].Phase[1].Current[38]:=Real_0;
mind_bool[331]:=OpozoriloPMM2x17med60in80[39]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[39],lo:=4662,hi:=4663); |  | 331:OpozoriloPMM2x17med60in80[39]:=Bit_0; |  |  |  | 4663:PMM[2].Phase[1].Current[39]:=Real_0;
mind_bool[332]:=OpozoriloPMM2x17med60in80[3]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[40],lo:=4664,hi:=4665); |  | 332:OpozoriloPMM2x17med60in80[3]:=Bit_0; |  |  |  | 4665:PMM[2].Phase[1].Current[40]:=Real_0;
mind_bool[333]:=OpozoriloPMM2x17med60in80[40]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[41],lo:=4666,hi:=4667); |  | 333:OpozoriloPMM2x17med60in80[40]:=Bit_0; |  |  |  | 4667:PMM[2].Phase[1].Current[41]:=Real_0;
mind_bool[334]:=OpozoriloPMM2x17med60in80[41]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[1].Current[42],lo:=4668,hi:=4669); |  | 334:OpozoriloPMM2x17med60in80[41]:=Bit_0; |  |  |  | 4669:PMM[2].Phase[1].Current[42]:=Real_0;
mind_bool[335]:=OpozoriloPMM2x17med60in80[42]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[10],lo:=4670,hi:=4671); |  | 335:OpozoriloPMM2x17med60in80[42]:=Bit_0; |  |  |  | 4671:PMM[2].Phase[2].Current[10]:=Real_0;
mind_bool[336]:=OpozoriloPMM2x17med60in80[4]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[11],lo:=4672,hi:=4673); |  | 336:OpozoriloPMM2x17med60in80[4]:=Bit_0; |  |  |  | 4673:PMM[2].Phase[2].Current[11]:=Real_0;
mind_bool[337]:=OpozoriloPMM2x17med60in80[5]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[12],lo:=4674,hi:=4675); |  | 337:OpozoriloPMM2x17med60in80[5]:=Bit_0; |  |  |  | 4675:PMM[2].Phase[2].Current[12]:=Real_0;
mind_bool[338]:=OpozoriloPMM2x17med60in80[6]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[13],lo:=4676,hi:=4677); |  | 338:OpozoriloPMM2x17med60in80[6]:=Bit_0; |  |  |  | 4677:PMM[2].Phase[2].Current[13]:=Real_0;
mind_bool[339]:=OpozoriloPMM2x17med60in80[7]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[14],lo:=4678,hi:=4679); |  | 339:OpozoriloPMM2x17med60in80[7]:=Bit_0; |  |  |  | 4679:PMM[2].Phase[2].Current[14]:=Real_0;
mind_bool[340]:=OpozoriloPMM2x17med60in80[8]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[15],lo:=4680,hi:=4681); |  | 340:OpozoriloPMM2x17med60in80[8]:=Bit_0; |  |  |  | 4681:PMM[2].Phase[2].Current[15]:=Real_0;
mind_bool[341]:=OpozoriloPMM2x17med60in80[9]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[16],lo:=4682,hi:=4683); |  | 341:OpozoriloPMM2x17med60in80[9]:=Bit_0; |  |  |  | 4683:PMM[2].Phase[2].Current[16]:=Real_0;
mind_bool[342]:=PhaseBool[0]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[17],lo:=4684,hi:=4685); |  | 342:PhaseBool[0]:=Bit_0; |  |  |  | 4685:PMM[2].Phase[2].Current[17]:=Real_0;
mind_bool[343]:=PhaseBool[1]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[18],lo:=4686,hi:=4687); |  | 343:PhaseBool[1]:=Bit_0; |  |  |  | 4687:PMM[2].Phase[2].Current[18]:=Real_0;
mind_bool[344]:=PhaseBool[2]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[19],lo:=4688,hi:=4689); |  | 344:PhaseBool[2]:=Bit_0; |  |  |  | 4689:PMM[2].Phase[2].Current[19]:=Real_0;
mind_bool[345]:=PhaseNext; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[1],lo:=4690,hi:=4691); |  | 345:PhaseNext:=Bit_0; |  |  |  | 4691:PMM[2].Phase[2].Current[1]:=Real_0;
mind_bool[346]:=PhasePrev; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[20],lo:=4692,hi:=4693); |  | 346:PhasePrev:=Bit_0; |  |  |  | 4693:PMM[2].Phase[2].Current[20]:=Real_0;
mind_bool[347]:=PMM1OverCurrentBetw[1]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[21],lo:=4694,hi:=4695); |  | 347:PMM1OverCurrentBetw[1]:=Bit_0; |  |  |  | 4695:PMM[2].Phase[2].Current[21]:=Real_0;
mind_bool[348]:=PMM1OverCurrentBetw[2]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[22],lo:=4696,hi:=4697); |  | 348:PMM1OverCurrentBetw[2]:=Bit_0; |  |  |  | 4697:PMM[2].Phase[2].Current[22]:=Real_0;
mind_bool[349]:=PMM1OverCurrentBetw[3]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[23],lo:=4698,hi:=4699); |  | 349:PMM1OverCurrentBetw[3]:=Bit_0; |  |  |  | 4699:PMM[2].Phase[2].Current[23]:=Real_0;
mind_bool[350]:=PMM1OverCurrentOver[1]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[24],lo:=4700,hi:=4701); |  | 350:PMM1OverCurrentOver[1]:=Bit_0; |  |  |  | 4701:PMM[2].Phase[2].Current[24]:=Real_0;
mind_bool[351]:=PMM1OverCurrentOver[2]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[25],lo:=4702,hi:=4703); |  | 351:PMM1OverCurrentOver[2]:=Bit_0; |  |  |  | 4703:PMM[2].Phase[2].Current[25]:=Real_0;
mind_bool[352]:=PMM1OverCurrentOver[3]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[26],lo:=4704,hi:=4705); |  | 352:PMM1OverCurrentOver[3]:=Bit_0; |  |  |  | 4705:PMM[2].Phase[2].Current[26]:=Real_0;
mind_bool[353]:=PMM1OverVoltage; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[27],lo:=4706,hi:=4707); |  | 353:PMM1OverVoltage:=Bit_0; |  |  |  | 4707:PMM[2].Phase[2].Current[27]:=Real_0;
mind_bool[354]:=PMM2OverCurrentBetw[1]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[28],lo:=4708,hi:=4709); |  | 354:PMM2OverCurrentBetw[1]:=Bit_0; |  |  |  | 4709:PMM[2].Phase[2].Current[28]:=Real_0;
mind_bool[355]:=PMM2OverCurrentBetw[2]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[29],lo:=4710,hi:=4711); |  | 355:PMM2OverCurrentBetw[2]:=Bit_0; |  |  |  | 4711:PMM[2].Phase[2].Current[29]:=Real_0;
mind_bool[356]:=PMM2OverCurrentBetw[3]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[2],lo:=4712,hi:=4713); |  | 356:PMM2OverCurrentBetw[3]:=Bit_0; |  |  |  | 4713:PMM[2].Phase[2].Current[2]:=Real_0;
mind_bool[357]:=PMM2OverCurrentOver[1]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[30],lo:=4714,hi:=4715); |  | 357:PMM2OverCurrentOver[1]:=Bit_0; |  |  |  | 4715:PMM[2].Phase[2].Current[30]:=Real_0;
mind_bool[358]:=PMM2OverCurrentOver[2]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[31],lo:=4716,hi:=4717); |  | 358:PMM2OverCurrentOver[2]:=Bit_0; |  |  |  | 4717:PMM[2].Phase[2].Current[31]:=Real_0;
mind_bool[359]:=PMM2OverCurrentOver[3]; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[32],lo:=4718,hi:=4719); |  | 359:PMM2OverCurrentOver[3]:=Bit_0; |  |  |  | 4719:PMM[2].Phase[2].Current[32]:=Real_0;
mind_bool[360]:=PMM2OverVoltage; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[33],lo:=4720,hi:=4721); |  | 360:PMM2OverVoltage:=Bit_0; |  |  |  | 4721:PMM[2].Phase[2].Current[33]:=Real_0;
mind_bool[361]:=PMM2x17; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[34],lo:=4722,hi:=4723); |  | 361:PMM2x17:=Bit_0; |  |  |  | 4723:PMM[2].Phase[2].Current[34]:=Real_0;
mind_bool[362]:=RocniVklopKlima1; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[35],lo:=4724,hi:=4725); |  | 362:RocniVklopKlima1:=Bit_0; |  |  |  | 4725:PMM[2].Phase[2].Current[35]:=Real_0;
mind_bool[363]:=RocniVklopKlima2; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[36],lo:=4726,hi:=4727); |  | 363:RocniVklopKlima2:=Bit_0; |  |  |  | 4727:PMM[2].Phase[2].Current[36]:=Real_0;
mind_bool[364]:=RocniVklopKlima3; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[37],lo:=4728,hi:=4729); |  | 364:RocniVklopKlima3:=Bit_0; |  |  |  | 4729:PMM[2].Phase[2].Current[37]:=Real_0;
mind_bool[365]:=RocniVklopKlima4; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[38],lo:=4730,hi:=4731); |  | 365:RocniVklopKlima4:=Bit_0; |  |  |  | 4731:PMM[2].Phase[2].Current[38]:=Real_0;
mind_bool[366]:=RocniVklopKlima5; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[39],lo:=4732,hi:=4733); |  | 366:RocniVklopKlima5:=Bit_0; |  |  |  | 4733:PMM[2].Phase[2].Current[39]:=Real_0;
mind_bool[367]:=RocniVklopKlima6; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[3],lo:=4734,hi:=4735); |  | 367:RocniVklopKlima6:=Bit_0; |  |  |  | 4735:PMM[2].Phase[2].Current[3]:=Real_0;
mind_bool[368]:=SinhronizacijaPanelOK; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[40],lo:=4736,hi:=4737); |  | 368:SinhronizacijaPanelOK:=Bit_0; |  |  |  | 4737:PMM[2].Phase[2].Current[40]:=Real_0;
mind_bool[369]:=SinhronizirajCas_Panel; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[41],lo:=4738,hi:=4739); |  | 369:SinhronizirajCas_Panel:=Bit_0; |  |  |  | 4739:PMM[2].Phase[2].Current[41]:=Real_0;
mind_bool[370]:=SkupneNapakeNaprav_Klima1; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[42],lo:=4740,hi:=4741); |  | 370:SkupneNapakeNaprav_Klima1:=Bit_0; |  |  |  | 4741:PMM[2].Phase[2].Current[42]:=Real_0;
mind_bool[371]:=SkupneNapakeNaprav_Klima2; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[4],lo:=4742,hi:=4743); |  | 371:SkupneNapakeNaprav_Klima2:=Bit_0; |  |  |  | 4743:PMM[2].Phase[2].Current[4]:=Real_0;
mind_bool[372]:=SkupneNapakeNaprav_Klima3; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[5],lo:=4744,hi:=4745); |  | 372:SkupneNapakeNaprav_Klima3:=Bit_0; |  |  |  | 4745:PMM[2].Phase[2].Current[5]:=Real_0;
mind_bool[373]:=SkupneNapakeNaprav_Klima4; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[6],lo:=4746,hi:=4747); |  | 373:SkupneNapakeNaprav_Klima4:=Bit_0; |  |  |  | 4747:PMM[2].Phase[2].Current[6]:=Real_0;
mind_bool[374]:=SkupneNapakeNaprav_Klima5; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[7],lo:=4748,hi:=4749); |  | 374:SkupneNapakeNaprav_Klima5:=Bit_0; |  |  |  | 4749:PMM[2].Phase[2].Current[7]:=Real_0;
mind_bool[375]:=SkupneNapakeNaprav_Klima6; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[8],lo:=4750,hi:=4751); |  | 375:SkupneNapakeNaprav_Klima6:=Bit_0; |  |  |  | 4751:PMM[2].Phase[2].Current[8]:=Real_0;
mind_bool[376]:=SkupneNapakeNaprav_Komunikacija; |  |  |  | Read_Real(rVar:=PMM[2].Phase[2].Current[9],lo:=4752,hi:=4753); |  | 376:SkupneNapakeNaprav_Komunikacija:=Bit_0; |  |  |  | 4753:PMM[2].Phase[2].Current[9]:=Real_0;
mind_bool[377]:=SkupneNapakeNaprav_PMM17VirBVirA; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[10],lo:=4754,hi:=4755); |  | 377:SkupneNapakeNaprav_PMM17VirBVirA:=Bit_0; |  |  |  | 4755:PMM[2].Phase[3].Current[10]:=Real_0;
mind_bool[378]:=SkupneNapakeNaprav_PMM63VirBVirA; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[11],lo:=4756,hi:=4757); |  | 378:SkupneNapakeNaprav_PMM63VirBVirA:=Bit_0; |  |  |  | 4757:PMM[2].Phase[3].Current[11]:=Real_0;
mind_bool[379]:=SkupneNapakeNaprav_TempVlaga; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[12],lo:=4758,hi:=4759); |  | 379:SkupneNapakeNaprav_TempVlaga:=Bit_0; |  |  |  | 4759:PMM[2].Phase[3].Current[12]:=Real_0;
mind_bool[380]:=StanjeKlimat2_1_Delovanje; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[13],lo:=4760,hi:=4761); |  | 380:StanjeKlimat2_1_Delovanje:=Bit_0; |  |  |  | 4761:PMM[2].Phase[3].Current[13]:=Real_0;
mind_bool[381]:=StanjeKlimat2_2_Delovanje; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[14],lo:=4762,hi:=4763); |  | 381:StanjeKlimat2_2_Delovanje:=Bit_0; |  |  |  | 4763:PMM[2].Phase[3].Current[14]:=Real_0;
mind_bool[382]:=StanjeKlimat2_3_Delovanje; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[15],lo:=4764,hi:=4765); |  | 382:StanjeKlimat2_3_Delovanje:=Bit_0; |  |  |  | 4765:PMM[2].Phase[3].Current[15]:=Real_0;
mind_bool[383]:=StanjeKlimat2_4_Delovanje; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[16],lo:=4766,hi:=4767); |  | 383:StanjeKlimat2_4_Delovanje:=Bit_0; |  |  |  | 4767:PMM[2].Phase[3].Current[16]:=Real_0;
mind_bool[384]:=StanjeKlimat2_5_Delovanje; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[17],lo:=4768,hi:=4769); |  | 384:StanjeKlimat2_5_Delovanje:=Bit_0; |  |  |  | 4769:PMM[2].Phase[3].Current[17]:=Real_0;
mind_bool[385]:=StanjeKlimat2_6_Delovanje; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[18],lo:=4770,hi:=4771); |  | 385:StanjeKlimat2_6_Delovanje:=Bit_0; |  |  |  | 4771:PMM[2].Phase[3].Current[18]:=Real_0;
mind_bool[386]:=StanjeUPSKrmOmara_BaterijskiNacin; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[19],lo:=4772,hi:=4773); |  | 386:StanjeUPSKrmOmara_BaterijskiNacin:=Bit_0; |  |  |  | 4773:PMM[2].Phase[3].Current[19]:=Real_0;
mind_bool[387]:=StanjeUPSKrmOmara_Polnjenje; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[1],lo:=4774,hi:=4775); |  | 387:StanjeUPSKrmOmara_Polnjenje:=Bit_0; |  |  |  | 4775:PMM[2].Phase[3].Current[1]:=Real_0;
mind_bool[388]:=UserLoggedIn; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[20],lo:=4776,hi:=4777); |  | 388:UserLoggedIn:=Bit_0; |  |  |  | 4777:PMM[2].Phase[3].Current[20]:=Real_0;
mind_bool[389]:=XVH_AlarmOn; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[21],lo:=4778,hi:=4779); |  | 389:XVH_AlarmOn:=Bit_0; |  |  |  | 4779:PMM[2].Phase[3].Current[21]:=Real_0;
mind_bool[390]:=Klimat2_1_Vklop; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[22],lo:=4780,hi:=4781); |  | 390:Klimat2_1_Vklop:=Bit_0; |  |  |  | 4781:PMM[2].Phase[3].Current[22]:=Real_0;
mind_bool[391]:=Klimat2_2_Vklop; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[23],lo:=4782,hi:=4783); |  | 391:Klimat2_2_Vklop:=Bit_0; |  |  |  | 4783:PMM[2].Phase[3].Current[23]:=Real_0;
mind_bool[392]:=Klimat2_3_Vklop; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[24],lo:=4784,hi:=4785); |  | 392:Klimat2_3_Vklop:=Bit_0; |  |  |  | 4785:PMM[2].Phase[3].Current[24]:=Real_0;
mind_bool[393]:=Klimat2_4_Vklop; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[25],lo:=4786,hi:=4787); |  | 393:Klimat2_4_Vklop:=Bit_0; |  |  |  | 4787:PMM[2].Phase[3].Current[25]:=Real_0;
mind_bool[394]:=Klimat2_5_Vklop; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[26],lo:=4788,hi:=4789); |  | 394:Klimat2_5_Vklop:=Bit_0; |  |  |  | 4789:PMM[2].Phase[3].Current[26]:=Real_0;
mind_bool[395]:=Klimat2_6_Vklop; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[27],lo:=4790,hi:=4791); |  | 395:Klimat2_6_Vklop:=Bit_0; |  |  |  | 4791:PMM[2].Phase[3].Current[27]:=Real_0;
mind_bool[396]:=ErrCommScada2; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[28],lo:=4792,hi:=4793); |  | 396:ErrCommScada2:=Bit_0; |  |  |  | 4793:PMM[2].Phase[3].Current[28]:=Real_0;
mind_bool[397]:=ComSCADA2; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[29],lo:=4794,hi:=4795); |  | 397:ComSCADA2:=Bit_0; |  |  |  | 4795:PMM[2].Phase[3].Current[29]:=Real_0;
mind_bool[398]:=ComSCADA3; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[2],lo:=4796,hi:=4797); |  | 398:ComSCADA3:=Bit_0; |  |  |  | 4797:PMM[2].Phase[3].Current[2]:=Real_0;
mind_bool[399]:=AlarmSKTemp5_Previsoka; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[30],lo:=4798,hi:=4799); |  | 399:AlarmSKTemp5_Previsoka:=Bit_0; |  |  |  | 4799:PMM[2].Phase[3].Current[30]:=Real_0;
mind_bool[400]:=AlarmSKTemp6_Previsoka; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[31],lo:=4800,hi:=4801); |  | 400:AlarmSKTemp6_Previsoka:=Bit_0; |  |  |  | 4801:PMM[2].Phase[3].Current[31]:=Real_0;
mind_bool[401]:=AlarmTempTIA5Previsoka; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[32],lo:=4802,hi:=4803); |  | 401:AlarmTempTIA5Previsoka:=Bit_0; |  |  |  | 4803:PMM[2].Phase[3].Current[32]:=Real_0;
mind_bool[402]:=AlarmTempTIA6Previsoka; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[33],lo:=4804,hi:=4805); |  | 402:AlarmTempTIA6Previsoka:=Bit_0; |  |  |  | 4805:PMM[2].Phase[3].Current[33]:=Real_0;
mind_bool[403]:=NapakaSenzorTemp5; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[34],lo:=4806,hi:=4807); |  | 403:NapakaSenzorTemp5:=Bit_0; |  |  |  | 4807:PMM[2].Phase[3].Current[34]:=Real_0;
mind_bool[404]:=NapakaSenzorTemp6; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[35],lo:=4808,hi:=4809); |  | 404:NapakaSenzorTemp6:=Bit_0; |  |  |  | 4809:PMM[2].Phase[3].Current[35]:=Real_0;
mind_bool[405]:=NapakaSenzorVlaga5; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[36],lo:=4810,hi:=4811); |  | 405:NapakaSenzorVlaga5:=Bit_0; |  |  |  | 4811:PMM[2].Phase[3].Current[36]:=Real_0;
mind_bool[406]:=NapakaSenzorVlaga6; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[37],lo:=4812,hi:=4813); |  | 406:NapakaSenzorVlaga6:=Bit_0; |  |  |  | 4813:PMM[2].Phase[3].Current[37]:=Real_0;
mind_bool[407]:=AlarmTempTIA235Previsoka; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[38],lo:=4814,hi:=4815); |  | 407:AlarmTempTIA235Previsoka:=Bit_0; |  |  |  | 4815:PMM[2].Phase[3].Current[38]:=Real_0;
mind_bool[408]:=AlarmTempTIA46Previsoka; |  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[39],lo:=4816,hi:=4817); |  | 408:AlarmTempTIA46Previsoka:=Bit_0; |  |  |  | 4817:PMM[2].Phase[3].Current[39]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[3],lo:=4818,hi:=4819); | [5 empty] | 4819:PMM[2].Phase[3].Current[3]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[40],lo:=4820,hi:=4821); | [5 empty] | 4821:PMM[2].Phase[3].Current[40]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[41],lo:=4822,hi:=4823); | [5 empty] | 4823:PMM[2].Phase[3].Current[41]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[42],lo:=4824,hi:=4825); | [5 empty] | 4825:PMM[2].Phase[3].Current[42]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[4],lo:=4826,hi:=4827); | [5 empty] | 4827:PMM[2].Phase[3].Current[4]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[5],lo:=4828,hi:=4829); | [5 empty] | 4829:PMM[2].Phase[3].Current[5]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[6],lo:=4830,hi:=4831); | [5 empty] | 4831:PMM[2].Phase[3].Current[6]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[7],lo:=4832,hi:=4833); | [5 empty] | 4833:PMM[2].Phase[3].Current[7]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[8],lo:=4834,hi:=4835); | [5 empty] | 4835:PMM[2].Phase[3].Current[8]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].Phase[3].Current[9],lo:=4836,hi:=4837); | [5 empty] | 4837:PMM[2].Phase[3].Current[9]:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].PowerFactorSys,lo:=4838,hi:=4839); | [5 empty] | 4839:PMM[2].PowerFactorSys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].ReactiveEnergyConsumed_kVARh,lo:=4840,hi:=4841); | [5 empty] | 4841:PMM[2].ReactiveEnergyConsumed_kVARh:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].ReactivePowerPhaseA,lo:=4842,hi:=4843); | [5 empty] | 4843:PMM[2].ReactivePowerPhaseA:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].ReactivePowerPhaseB,lo:=4844,hi:=4845); | [5 empty] | 4845:PMM[2].ReactivePowerPhaseB:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].ReactivePowerPhaseC,lo:=4846,hi:=4847); | [5 empty] | 4847:PMM[2].ReactivePowerPhaseC:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].TotalActivePower_kW,lo:=4848,hi:=4849); | [5 empty] | 4849:PMM[2].TotalActivePower_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].TotalAparentPower_kVA,lo:=4850,hi:=4851); | [5 empty] | 4851:PMM[2].TotalAparentPower_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].TotalPowerFactor,lo:=4852,hi:=4853); | [5 empty] | 4853:PMM[2].TotalPowerFactor:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].TotalReactivePower_kVAR,lo:=4854,hi:=4855); | [5 empty] | 4855:PMM[2].TotalReactivePower_kVAR:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirA_fsys,lo:=4856,hi:=4857); | [5 empty] | 4857:PMM[2].VirA_fsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirA_Isys,lo:=4858,hi:=4859); | [5 empty] | 4859:PMM[2].VirA_Isys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirA_PFsys,lo:=4860,hi:=4861); | [5 empty] | 4861:PMM[2].VirA_PFsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirA_Psys,lo:=4862,hi:=4863); | [5 empty] | 4863:PMM[2].VirA_Psys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirA_Qsys,lo:=4864,hi:=4865); | [5 empty] | 4865:PMM[2].VirA_Qsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirA_Ssys,lo:=4866,hi:=4867); | [5 empty] | 4867:PMM[2].VirA_Ssys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirA_Usys,lo:=4868,hi:=4869); | [5 empty] | 4869:PMM[2].VirA_Usys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirB_fsys,lo:=4870,hi:=4871); | [5 empty] | 4871:PMM[2].VirB_fsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirB_Isys,lo:=4872,hi:=4873); | [5 empty] | 4873:PMM[2].VirB_Isys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirB_PFsys,lo:=4874,hi:=4875); | [5 empty] | 4875:PMM[2].VirB_PFsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirB_Psys,lo:=4876,hi:=4877); | [5 empty] | 4877:PMM[2].VirB_Psys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirB_Qsys,lo:=4878,hi:=4879); | [5 empty] | 4879:PMM[2].VirB_Qsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirB_Ssys,lo:=4880,hi:=4881); | [5 empty] | 4881:PMM[2].VirB_Ssys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirB_Usys,lo:=4882,hi:=4883); | [5 empty] | 4883:PMM[2].VirB_Usys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBActiveEnergyConsumed_kWh,lo:=4884,hi:=4885); | [5 empty] | 4885:PMM[2].VirBActiveEnergyConsumed_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBActivePowerPhaseA_kW,lo:=4886,hi:=4887); | [5 empty] | 4887:PMM[2].VirBActivePowerPhaseA_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBActivePowerPhaseB_kW,lo:=4888,hi:=4889); | [5 empty] | 4889:PMM[2].VirBActivePowerPhaseB_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBActivePowerPhaseC_kW,lo:=4890,hi:=4891); | [5 empty] | 4891:PMM[2].VirBActivePowerPhaseC_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBAparentPowerPhaseA,lo:=4892,hi:=4893); | [5 empty] | 4893:PMM[2].VirBAparentPowerPhaseA:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBAparentPowerPhaseB,lo:=4894,hi:=4895); | [5 empty] | 4895:PMM[2].VirBAparentPowerPhaseB:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBAparentPowerPhaseC,lo:=4896,hi:=4897); | [5 empty] | 4897:PMM[2].VirBAparentPowerPhaseC:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBAverageCurrent_A,lo:=4898,hi:=4899); | [5 empty] | 4899:PMM[2].VirBAverageCurrent_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBAveragePhaseToNeutral_V,lo:=4900,hi:=4901); | [5 empty] | 4901:PMM[2].VirBAveragePhaseToNeutral_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBAveragePhaseToPhase_V,lo:=4902,hi:=4903); | [5 empty] | 4903:PMM[2].VirBAveragePhaseToPhase_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBCurrentInPhaseA_A,lo:=4904,hi:=4905); | [5 empty] | 4905:PMM[2].VirBCurrentInPhaseA_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBCurrentInPhaseB_A,lo:=4906,hi:=4907); | [5 empty] | 4907:PMM[2].VirBCurrentInPhaseB_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBCurrentInPhaseC_A,lo:=4908,hi:=4909); | [5 empty] | 4909:PMM[2].VirBCurrentInPhaseC_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBFrequency_Hz,lo:=4910,hi:=4911); | [5 empty] | 4911:PMM[2].VirBFrequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBPowerFactorSys,lo:=4912,hi:=4913); | [5 empty] | 4913:PMM[2].VirBPowerFactorSys:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBReactiveEnergyConsumed_kVARh,lo:=4914,hi:=4915); | [5 empty] | 4915:PMM[2].VirBReactiveEnergyConsumed_kVARh:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBReactivePowerPhaseA,lo:=4916,hi:=4917); | [5 empty] | 4917:PMM[2].VirBReactivePowerPhaseA:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBReactivePowerPhaseB,lo:=4918,hi:=4919); | [5 empty] | 4919:PMM[2].VirBReactivePowerPhaseB:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBReactivePowerPhaseC,lo:=4920,hi:=4921); | [5 empty] | 4921:PMM[2].VirBReactivePowerPhaseC:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBTotalActivePower_kW,lo:=4922,hi:=4923); | [5 empty] | 4923:PMM[2].VirBTotalActivePower_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBTotalAparentPower_kVA,lo:=4924,hi:=4925); | [5 empty] | 4925:PMM[2].VirBTotalAparentPower_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBTotalPowerFactor,lo:=4926,hi:=4927); | [5 empty] | 4927:PMM[2].VirBTotalPowerFactor:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBTotalReactivePower_kVAR,lo:=4928,hi:=4929); | [5 empty] | 4929:PMM[2].VirBTotalReactivePower_kVAR:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBVoltageBetweenPhaseAB_V,lo:=4930,hi:=4931); | [5 empty] | 4931:PMM[2].VirBVoltageBetweenPhaseAB_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBVoltageBetweenPhaseAN_V,lo:=4932,hi:=4933); | [5 empty] | 4933:PMM[2].VirBVoltageBetweenPhaseAN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBVoltageBetweenPhaseBC_V,lo:=4934,hi:=4935); | [5 empty] | 4935:PMM[2].VirBVoltageBetweenPhaseBC_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBVoltageBetweenPhaseBN_V,lo:=4936,hi:=4937); | [5 empty] | 4937:PMM[2].VirBVoltageBetweenPhaseBN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBVoltageBetweenPhaseCA_V,lo:=4938,hi:=4939); | [5 empty] | 4939:PMM[2].VirBVoltageBetweenPhaseCA_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VirBVoltageBetweenPhaseCN_V,lo:=4940,hi:=4941); | [5 empty] | 4941:PMM[2].VirBVoltageBetweenPhaseCN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VoltageBetweenPhaseAB_V,lo:=4942,hi:=4943); | [5 empty] | 4943:PMM[2].VoltageBetweenPhaseAB_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VoltageBetweenPhaseAN_V,lo:=4944,hi:=4945); | [5 empty] | 4945:PMM[2].VoltageBetweenPhaseAN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VoltageBetweenPhaseBC_V,lo:=4946,hi:=4947); | [5 empty] | 4947:PMM[2].VoltageBetweenPhaseBC_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VoltageBetweenPhaseBN_V,lo:=4948,hi:=4949); | [5 empty] | 4949:PMM[2].VoltageBetweenPhaseBN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VoltageBetweenPhaseCA_V,lo:=4950,hi:=4951); | [5 empty] | 4951:PMM[2].VoltageBetweenPhaseCA_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMM[2].VoltageBetweenPhaseCN_V,lo:=4952,hi:=4953); | [5 empty] | 4953:PMM[2].VoltageBetweenPhaseCN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.ActiveEnergyConsumed_kWh,lo:=4954,hi:=4955); | [5 empty] | 4955:PMMPanel.ActiveEnergyConsumed_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.ActivePowerPhaseA_kW,lo:=4956,hi:=4957); | [5 empty] | 4957:PMMPanel.ActivePowerPhaseA_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.ActivePowerPhaseB_kW,lo:=4958,hi:=4959); | [5 empty] | 4959:PMMPanel.ActivePowerPhaseB_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.ActivePowerPhaseC_kW,lo:=4960,hi:=4961); | [5 empty] | 4961:PMMPanel.ActivePowerPhaseC_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.AparentPowerPhaseA,lo:=4962,hi:=4963); | [5 empty] | 4963:PMMPanel.AparentPowerPhaseA:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.AparentPowerPhaseB,lo:=4964,hi:=4965); | [5 empty] | 4965:PMMPanel.AparentPowerPhaseB:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.AparentPowerPhaseC,lo:=4966,hi:=4967); | [5 empty] | 4967:PMMPanel.AparentPowerPhaseC:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.AverageCurrent_A,lo:=4968,hi:=4969); | [5 empty] | 4969:PMMPanel.AverageCurrent_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.AveragePhaseToNeutral_V,lo:=4970,hi:=4971); | [5 empty] | 4971:PMMPanel.AveragePhaseToNeutral_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.AveragePhaseToPhase_V,lo:=4972,hi:=4973); | [5 empty] | 4973:PMMPanel.AveragePhaseToPhase_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.CurrentInPhaseA_A,lo:=4974,hi:=4975); | [5 empty] | 4975:PMMPanel.CurrentInPhaseA_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.CurrentInPhaseB_A,lo:=4976,hi:=4977); | [5 empty] | 4977:PMMPanel.CurrentInPhaseB_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.CurrentInPhaseC_A,lo:=4978,hi:=4979); | [5 empty] | 4979:PMMPanel.CurrentInPhaseC_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.Frequency_Hz,lo:=4980,hi:=4981); | [5 empty] | 4981:PMMPanel.Frequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.PowerFactorSys,lo:=4982,hi:=4983); | [5 empty] | 4983:PMMPanel.PowerFactorSys:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.ReactiveEnergyConsumed_kVARh,lo:=4984,hi:=4985); | [5 empty] | 4985:PMMPanel.ReactiveEnergyConsumed_kVARh:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.ReactivePowerPhaseA,lo:=4986,hi:=4987); | [5 empty] | 4987:PMMPanel.ReactivePowerPhaseA:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.ReactivePowerPhaseB,lo:=4988,hi:=4989); | [5 empty] | 4989:PMMPanel.ReactivePowerPhaseB:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.ReactivePowerPhaseC,lo:=4990,hi:=4991); | [5 empty] | 4991:PMMPanel.ReactivePowerPhaseC:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.TotalActivePower_kW,lo:=4992,hi:=4993); | [5 empty] | 4993:PMMPanel.TotalActivePower_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.TotalAparentPower_kVA,lo:=4994,hi:=4995); | [5 empty] | 4995:PMMPanel.TotalAparentPower_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.TotalPowerFactor,lo:=4996,hi:=4997); | [5 empty] | 4997:PMMPanel.TotalPowerFactor:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.TotalReactivePower_kVAR,lo:=4998,hi:=4999); | [5 empty] | 4999:PMMPanel.TotalReactivePower_kVAR:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirA_fsys,lo:=5000,hi:=5001); | [5 empty] | 5001:PMMPanel.VirA_fsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirA_Isys,lo:=5002,hi:=5003); | [5 empty] | 5003:PMMPanel.VirA_Isys:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirA_PFsys,lo:=5004,hi:=5005); | [5 empty] | 5005:PMMPanel.VirA_PFsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirA_Psys,lo:=5006,hi:=5007); | [5 empty] | 5007:PMMPanel.VirA_Psys:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirA_Qsys,lo:=5008,hi:=5009); | [5 empty] | 5009:PMMPanel.VirA_Qsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirA_Ssys,lo:=5010,hi:=5011); | [5 empty] | 5011:PMMPanel.VirA_Ssys:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirA_Usys,lo:=5012,hi:=5013); | [5 empty] | 5013:PMMPanel.VirA_Usys:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirB_fsys,lo:=5014,hi:=5015); | [5 empty] | 5015:PMMPanel.VirB_fsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirB_Isys,lo:=5016,hi:=5017); | [5 empty] | 5017:PMMPanel.VirB_Isys:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirB_PFsys,lo:=5018,hi:=5019); | [5 empty] | 5019:PMMPanel.VirB_PFsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirB_Psys,lo:=5020,hi:=5021); | [5 empty] | 5021:PMMPanel.VirB_Psys:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirB_Qsys,lo:=5022,hi:=5023); | [5 empty] | 5023:PMMPanel.VirB_Qsys:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirB_Ssys,lo:=5024,hi:=5025); | [5 empty] | 5025:PMMPanel.VirB_Ssys:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirB_Usys,lo:=5026,hi:=5027); | [5 empty] | 5027:PMMPanel.VirB_Usys:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBActiveEnergyConsumed_kWh,lo:=5028,hi:=5029); | [5 empty] | 5029:PMMPanel.VirBActiveEnergyConsumed_kWh:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBActivePowerPhaseA_kW,lo:=5030,hi:=5031); | [5 empty] | 5031:PMMPanel.VirBActivePowerPhaseA_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBActivePowerPhaseB_kW,lo:=5032,hi:=5033); | [5 empty] | 5033:PMMPanel.VirBActivePowerPhaseB_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBActivePowerPhaseC_kW,lo:=5034,hi:=5035); | [5 empty] | 5035:PMMPanel.VirBActivePowerPhaseC_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBAparentPowerPhaseA,lo:=5036,hi:=5037); | [5 empty] | 5037:PMMPanel.VirBAparentPowerPhaseA:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBAparentPowerPhaseB,lo:=5038,hi:=5039); | [5 empty] | 5039:PMMPanel.VirBAparentPowerPhaseB:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBAparentPowerPhaseC,lo:=5040,hi:=5041); | [5 empty] | 5041:PMMPanel.VirBAparentPowerPhaseC:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBAverageCurrent_A,lo:=5042,hi:=5043); | [5 empty] | 5043:PMMPanel.VirBAverageCurrent_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBAveragePhaseToNeutral_V,lo:=5044,hi:=5045); | [5 empty] | 5045:PMMPanel.VirBAveragePhaseToNeutral_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBAveragePhaseToPhase_V,lo:=5046,hi:=5047); | [5 empty] | 5047:PMMPanel.VirBAveragePhaseToPhase_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBCurrentInPhaseA_A,lo:=5048,hi:=5049); | [5 empty] | 5049:PMMPanel.VirBCurrentInPhaseA_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBCurrentInPhaseB_A,lo:=5050,hi:=5051); | [5 empty] | 5051:PMMPanel.VirBCurrentInPhaseB_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBCurrentInPhaseC_A,lo:=5052,hi:=5053); | [5 empty] | 5053:PMMPanel.VirBCurrentInPhaseC_A:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBFrequency_Hz,lo:=5054,hi:=5055); | [5 empty] | 5055:PMMPanel.VirBFrequency_Hz:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBPowerFactorSys,lo:=5056,hi:=5057); | [5 empty] | 5057:PMMPanel.VirBPowerFactorSys:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBReactiveEnergyConsumed_kVARh,lo:=5058,hi:=5059); | [5 empty] | 5059:PMMPanel.VirBReactiveEnergyConsumed_kVARh:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBReactivePowerPhaseA,lo:=5060,hi:=5061); | [5 empty] | 5061:PMMPanel.VirBReactivePowerPhaseA:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBReactivePowerPhaseB,lo:=5062,hi:=5063); | [5 empty] | 5063:PMMPanel.VirBReactivePowerPhaseB:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBReactivePowerPhaseC,lo:=5064,hi:=5065); | [5 empty] | 5065:PMMPanel.VirBReactivePowerPhaseC:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBTotalActivePower_kW,lo:=5066,hi:=5067); | [5 empty] | 5067:PMMPanel.VirBTotalActivePower_kW:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBTotalAparentPower_kVA,lo:=5068,hi:=5069); | [5 empty] | 5069:PMMPanel.VirBTotalAparentPower_kVA:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBTotalPowerFactor,lo:=5070,hi:=5071); | [5 empty] | 5071:PMMPanel.VirBTotalPowerFactor:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBTotalReactivePower_kVAR,lo:=5072,hi:=5073); | [5 empty] | 5073:PMMPanel.VirBTotalReactivePower_kVAR:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBVoltageBetweenPhaseAB_V,lo:=5074,hi:=5075); | [5 empty] | 5075:PMMPanel.VirBVoltageBetweenPhaseAB_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBVoltageBetweenPhaseAN_V,lo:=5076,hi:=5077); | [5 empty] | 5077:PMMPanel.VirBVoltageBetweenPhaseAN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBVoltageBetweenPhaseBC_V,lo:=5078,hi:=5079); | [5 empty] | 5079:PMMPanel.VirBVoltageBetweenPhaseBC_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBVoltageBetweenPhaseBN_V,lo:=5080,hi:=5081); | [5 empty] | 5081:PMMPanel.VirBVoltageBetweenPhaseBN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBVoltageBetweenPhaseCA_V,lo:=5082,hi:=5083); | [5 empty] | 5083:PMMPanel.VirBVoltageBetweenPhaseCA_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VirBVoltageBetweenPhaseCN_V,lo:=5084,hi:=5085); | [5 empty] | 5085:PMMPanel.VirBVoltageBetweenPhaseCN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VoltageBetweenPhaseAB_V,lo:=5086,hi:=5087); | [5 empty] | 5087:PMMPanel.VoltageBetweenPhaseAB_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VoltageBetweenPhaseAN_V,lo:=5088,hi:=5089); | [5 empty] | 5089:PMMPanel.VoltageBetweenPhaseAN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VoltageBetweenPhaseBC_V,lo:=5090,hi:=5091); | [5 empty] | 5091:PMMPanel.VoltageBetweenPhaseBC_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VoltageBetweenPhaseBN_V,lo:=5092,hi:=5093); | [5 empty] | 5093:PMMPanel.VoltageBetweenPhaseBN_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VoltageBetweenPhaseCA_V,lo:=5094,hi:=5095); | [5 empty] | 5095:PMMPanel.VoltageBetweenPhaseCA_V:=Real_0;
|  |  |  | Read_Real(rVar:=PMMPanel.VoltageBetweenPhaseCN_V,lo:=5096,hi:=5097); | [5 empty] | 5097:PMMPanel.VoltageBetweenPhaseCN_V:=Real_0;
|  |  |  | Read_Real(rVar:=SKTemp1,lo:=5098,hi:=5099); | [5 empty] | 5099:SKTemp1:=Real_0;
|  |  |  | Read_Real(rVar:=SKTemp2,lo:=5100,hi:=5101); | [5 empty] | 5101:SKTemp2:=Real_0;
|  |  |  | Read_Real(rVar:=SKTemp3,lo:=5102,hi:=5103); | [5 empty] | 5103:SKTemp3:=Real_0;
|  |  |  | Read_Real(rVar:=SKTemp4,lo:=5104,hi:=5105); | [5 empty] | 5105:SKTemp4:=Real_0;
|  |  |  | Read_Real(rVar:=SKVlaga1,lo:=5106,hi:=5107); | [5 empty] | 5107:SKVlaga1:=Real_0;
|  |  |  | Read_Real(rVar:=SKVlaga2,lo:=5108,hi:=5109); | [5 empty] | 5109:SKVlaga2:=Real_0;
|  |  |  | Read_Real(rVar:=SKVlaga3,lo:=5110,hi:=5111); | [5 empty] | 5111:SKVlaga3:=Real_0;
|  |  |  | Read_Real(rVar:=SKVlaga4,lo:=5112,hi:=5113); | [5 empty] | 5113:SKVlaga4:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaAlarm1_2,lo:=5114,hi:=5115); | [5 empty] | 5115:TempZaAlarm1_2:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaAlarm3_4,lo:=5116,hi:=5117); | [5 empty] | 5117:TempZaAlarm3_4:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaAlarm5_6,lo:=5118,hi:=5119); | [5 empty] | 5119:TempZaAlarm5_6:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaAlarmTIA1,lo:=5120,hi:=5121); | [5 empty] | 5121:TempZaAlarmTIA1:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaAlarmTIA2,lo:=5122,hi:=5123); | [5 empty] | 5123:TempZaAlarmTIA2:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaAlarmTIA3,lo:=5124,hi:=5125); | [5 empty] | 5125:TempZaAlarmTIA3:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaAlarmTIA4,lo:=5126,hi:=5127); | [5 empty] | 5127:TempZaAlarmTIA4:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaVklopObehKlim1_2,lo:=5128,hi:=5129); | [5 empty] | 5129:TempZaVklopObehKlim1_2:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaVklopObehKlim3_4,lo:=5130,hi:=5131); | [5 empty] | 5131:TempZaVklopObehKlim3_4:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaVklopObehKlim3_4TIA3,lo:=5132,hi:=5133); | [5 empty] | 5133:TempZaVklopObehKlim3_4TIA3:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaVklopObehKlim5_6,lo:=5134,hi:=5135); | [5 empty] | 5135:TempZaVklopObehKlim5_6:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaVklopObehKlim5_6TIA3,lo:=5136,hi:=5137); | [5 empty] | 5137:TempZaVklopObehKlim5_6TIA3:=Real_0;
|  |  |  | Read_Real(rVar:=SKTemp5,lo:=5138,hi:=5139); | [5 empty] | 5139:SKTemp5:=Real_0;
|  |  |  | Read_Real(rVar:=SKTemp6,lo:=5140,hi:=5141); | [5 empty] | 5141:SKTemp6:=Real_0;
|  |  |  | Read_Real(rVar:=SKVlaga5,lo:=5142,hi:=5143); | [5 empty] | 5143:SKVlaga5:=Real_0;
|  |  |  | Read_Real(rVar:=SKVlaga6,lo:=5144,hi:=5145); | [5 empty] | 5145:SKVlaga6:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaAlarmTIA5,lo:=5146,hi:=5147); | [5 empty] | 5147:TempZaAlarmTIA5:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaAlarmTIA6,lo:=5148,hi:=5149); | [5 empty] | 5149:TempZaAlarmTIA6:=Real_0;
|  |  |  | Read_Real(rVar:=SKTempServSoba1Povpr,lo:=5150,hi:=5151); | [5 empty] | 5151:SKTempServSoba1Povpr:=Real_0;
|  |  |  | Read_Real(rVar:=SKTempServSoba2Povpr,lo:=5152,hi:=5153); | [5 empty] | 5153:SKTempServSoba2Povpr:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaAlarmTIA235,lo:=5154,hi:=5155); | [5 empty] | 5155:TempZaAlarmTIA235:=Real_0;
|  |  |  | Read_Real(rVar:=TempZaAlarmTIA46,lo:=5156,hi:=5157); | [5 empty] | 5157:TempZaAlarmTIA46:=Real_0;

## XSoft_EXP
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
PROGRAM mod_Read
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*Branje BOOL*)
(**)
mind_bool[0]:=AlarmKlimat2_1_Napaka;
mind_bool[1]:=AlarmKlimat2_2_Napaka;
mind_bool[2]:=AlarmKlimat2_3_Napaka;
mind_bool[3]:=AlarmKlimat2_4_Napaka;
mind_bool[4]:=AlarmKlimat2_5_Napaka;
mind_bool[5]:=AlarmKlimat2_6_Napaka;
mind_bool[6]:=AlarmLAH1RazlitjeVode;
mind_bool[7]:=AlarmLAH2RazlitjeVode;
mind_bool[8]:=AlarmLAH3RazlitjeVode;
mind_bool[9]:=AlarmPMM2x17nad80[10];
mind_bool[10]:=AlarmPMM2x17nad80[11];
mind_bool[11]:=AlarmPMM2x17nad80[12];
mind_bool[12]:=AlarmPMM2x17nad80[13];
mind_bool[13]:=AlarmPMM2x17nad80[14];
mind_bool[14]:=AlarmPMM2x17nad80[15];
mind_bool[15]:=AlarmPMM2x17nad80[16];
mind_bool[16]:=AlarmPMM2x17nad80[17];
mind_bool[17]:=AlarmPMM2x17nad80[18];
mind_bool[18]:=AlarmPMM2x17nad80[19];
mind_bool[19]:=AlarmPMM2x17nad80[1];
mind_bool[20]:=AlarmPMM2x17nad80[20];
mind_bool[21]:=AlarmPMM2x17nad80[21];
mind_bool[22]:=AlarmPMM2x17nad80[22];
mind_bool[23]:=AlarmPMM2x17nad80[23];
mind_bool[24]:=AlarmPMM2x17nad80[24];
mind_bool[25]:=AlarmPMM2x17nad80[25];
mind_bool[26]:=AlarmPMM2x17nad80[26];
mind_bool[27]:=AlarmPMM2x17nad80[27];
mind_bool[28]:=AlarmPMM2x17nad80[28];
mind_bool[29]:=AlarmPMM2x17nad80[29];
mind_bool[30]:=AlarmPMM2x17nad80[2];
mind_bool[31]:=AlarmPMM2x17nad80[30];
mind_bool[32]:=AlarmPMM2x17nad80[31];
mind_bool[33]:=AlarmPMM2x17nad80[32];
mind_bool[34]:=AlarmPMM2x17nad80[33];
mind_bool[35]:=AlarmPMM2x17nad80[34];
mind_bool[36]:=AlarmPMM2x17nad80[35];
mind_bool[37]:=AlarmPMM2x17nad80[36];
mind_bool[38]:=AlarmPMM2x17nad80[37];
mind_bool[39]:=AlarmPMM2x17nad80[38];
mind_bool[40]:=AlarmPMM2x17nad80[39];
mind_bool[41]:=AlarmPMM2x17nad80[3];
mind_bool[42]:=AlarmPMM2x17nad80[40];
mind_bool[43]:=AlarmPMM2x17nad80[41];
mind_bool[44]:=AlarmPMM2x17nad80[42];
mind_bool[45]:=AlarmPMM2x17nad80[4];
mind_bool[46]:=AlarmPMM2x17nad80[5];
mind_bool[47]:=AlarmPMM2x17nad80[6];
mind_bool[48]:=AlarmPMM2x17nad80[7];
mind_bool[49]:=AlarmPMM2x17nad80[8];
mind_bool[50]:=AlarmPMM2x17nad80[9];
mind_bool[51]:=AlarmSinhronizacijaNOK;
mind_bool[52]:=AlarmSKTemp1_Previsoka;
mind_bool[53]:=AlarmSKTemp2_Previsoka;
mind_bool[54]:=AlarmSKTemp3_Previsoka;
mind_bool[55]:=AlarmSKTemp4_Previsoka;
mind_bool[56]:=AlarmTempTIA1Previsoka;
mind_bool[57]:=AlarmTempTIA2Previsoka;
mind_bool[58]:=AlarmTempTIA3Previsoka;
mind_bool[59]:=AlarmTempTIA4Previsoka;
mind_bool[60]:=AlarmUPSKrmOmara_Alarm;
mind_bool[61]:=ComSCADA;
mind_bool[62]:=ComSCADA1;
mind_bool[63]:=ErrComKlima[1];
mind_bool[64]:=ErrComKlima[2];
mind_bool[65]:=ErrComKlima[3];
mind_bool[66]:=ErrComKlima[4];
mind_bool[67]:=ErrComKlima[5];
mind_bool[68]:=ErrComKlima[6];
mind_bool[69]:=ErrCommScada;
mind_bool[70]:=ErrComPanelPLC;
mind_bool[71]:=ErrComPMM[1];
mind_bool[72]:=ErrComPMM[2];
mind_bool[73]:=ErrComPort2;
mind_bool[74]:=ErrorComKlima[1].Error;
mind_bool[75]:=ErrorComKlima[2].Error;
mind_bool[76]:=ErrorComKlima[3].Error;
mind_bool[77]:=ErrorComKlima[4].Error;
mind_bool[78]:=ErrorComKlima[5].Error;
mind_bool[79]:=ErrorComKlima[6].Error;
mind_bool[80]:=ErrorComPMM[1].Error;
mind_bool[81]:=ErrorComPMM[2].Error;
mind_bool[82]:=Klima2_1_Onemogocena;
mind_bool[83]:=Klima2_2_Onemogocena;
mind_bool[84]:=Klima2_3_Onemogocena;
mind_bool[85]:=Klima2_4_Onemogocena;
mind_bool[86]:=Klima2_5_Onemogocena;
mind_bool[87]:=Klima2_6_Onemogocena;
mind_bool[88]:=Klima[1].IzhodniVentilator;
mind_bool[89]:=Klima[1].Kompresor1;
mind_bool[90]:=Klima[1].Kompresor2;
mind_bool[91]:=Klima[1].Razvlazevanje;
mind_bool[92]:=Klima[1].SenzorjiStatus;
mind_bool[93]:=Klima[1].VentilGretjeOdpiranje;
mind_bool[94]:=Klima[1].VentilGretjeZapiranje;
mind_bool[95]:=Klima[1].Vlazenje;
mind_bool[96]:=Klima[2].IzhodniVentilator;
mind_bool[97]:=Klima[2].Kompresor1;
mind_bool[98]:=Klima[2].Kompresor2;
mind_bool[99]:=Klima[2].Razvlazevanje;
mind_bool[100]:=Klima[2].SenzorjiStatus;
mind_bool[101]:=Klima[2].VentilGretjeOdpiranje;
mind_bool[102]:=Klima[2].VentilGretjeZapiranje;
mind_bool[103]:=Klima[2].Vlazenje;
mind_bool[104]:=Klima[3].IzhodniVentilator;
mind_bool[105]:=Klima[3].Kompresor1;
mind_bool[106]:=Klima[3].Kompresor2;
mind_bool[107]:=Klima[3].Razvlazevanje;
mind_bool[108]:=Klima[3].SenzorjiStatus;
mind_bool[109]:=Klima[3].VentilGretjeOdpiranje;
mind_bool[110]:=Klima[3].VentilGretjeZapiranje;
mind_bool[111]:=Klima[3].Vlazenje;
mind_bool[112]:=Klima[4].IzhodniVentilator;
mind_bool[113]:=Klima[4].Kompresor1;
mind_bool[114]:=Klima[4].Kompresor2;
mind_bool[115]:=Klima[4].Razvlazevanje;
mind_bool[116]:=Klima[4].SenzorjiStatus;
mind_bool[117]:=Klima[4].VentilGretjeOdpiranje;
mind_bool[118]:=Klima[4].VentilGretjeZapiranje;
mind_bool[119]:=Klima[4].Vlazenje;
mind_bool[120]:=Klima[5].IzhodniVentilator;
mind_bool[121]:=Klima[5].Kompresor1;
mind_bool[122]:=Klima[5].Kompresor2;
mind_bool[123]:=Klima[5].Razvlazevanje;
mind_bool[124]:=Klima[5].SenzorjiStatus;
mind_bool[125]:=Klima[5].VentilGretjeOdpiranje;
mind_bool[126]:=Klima[5].VentilGretjeZapiranje;
mind_bool[127]:=Klima[5].Vlazenje;
mind_bool[128]:=Klima[6].IzhodniVentilator;
mind_bool[129]:=Klima[6].Kompresor1;
mind_bool[130]:=Klima[6].Kompresor2;
mind_bool[131]:=Klima[6].Razvlazevanje;
mind_bool[132]:=Klima[6].SenzorjiStatus;
mind_bool[133]:=Klima[6].VentilGretjeOdpiranje;
mind_bool[134]:=Klima[6].VentilGretjeZapiranje;
mind_bool[135]:=Klima[6].Vlazenje;
mind_bool[136]:=KlimaError[1].AlarmKompresor1;
mind_bool[137]:=KlimaError[1].AlarmKompresor2;
mind_bool[138]:=KlimaError[1].FenThermalCutout;
mind_bool[139]:=KlimaError[1].IzlivVode;
mind_bool[140]:=KlimaError[1].Kompresor1naMejiStevilaObrUr;
mind_bool[141]:=KlimaError[1].Kompresor2naMejiStevilaObrUr;
mind_bool[142]:=KlimaError[1].NapakaPriPretokuVode;
mind_bool[143]:=KlimaError[1].NapakaPriPretokuZraka;
mind_bool[144]:=KlimaError[1].NapakaSenzorVlaznosti;
mind_bool[145]:=KlimaError[1].NapakaTSTemperaturaProstora;
mind_bool[146]:=KlimaError[1].NapakaVlazilca;
mind_bool[147]:=KlimaError[1].NizekPritiskKompresor1;
mind_bool[148]:=KlimaError[1].NizekPritiskKompresor2;
mind_bool[149]:=KlimaError[1].NizkaTempVProstoru;
mind_bool[150]:=KlimaError[1].NizkaVlaznost;
mind_bool[151]:=KlimaError[1].PozarniAlarm;
mind_bool[152]:=KlimaError[1].ThermalCutoutHeater1;
mind_bool[153]:=KlimaError[1].ThermalCutoutHeater2;
mind_bool[154]:=KlimaError[1].VentilatorNaMejiStevilaObrUr;
mind_bool[155]:=KlimaError[1].VisokaTempVProstoru;
mind_bool[156]:=KlimaError[1].VisokaVlaznost;
mind_bool[157]:=KlimaError[1].VisokPritiskKompresor1;
mind_bool[158]:=KlimaError[1].VisokPritiskKompresor2;
mind_bool[159]:=KlimaError[1].ZamasenFilter;
mind_bool[160]:=KlimaError[1].ZunanjiAlarm;
mind_bool[161]:=KlimaError[2].AlarmKompresor1;
mind_bool[162]:=KlimaError[2].AlarmKompresor2;
mind_bool[163]:=KlimaError[2].FenThermalCutout;
mind_bool[164]:=KlimaError[2].IzlivVode;
mind_bool[165]:=KlimaError[2].Kompresor1naMejiStevilaObrUr;
mind_bool[166]:=KlimaError[2].Kompresor2naMejiStevilaObrUr;
mind_bool[167]:=KlimaError[2].NapakaPriPretokuVode;
mind_bool[168]:=KlimaError[2].NapakaPriPretokuZraka;
mind_bool[169]:=KlimaError[2].NapakaSenzorVlaznosti;
mind_bool[170]:=KlimaError[2].NapakaTSTemperaturaProstora;
mind_bool[171]:=KlimaError[2].NapakaVlazilca;
mind_bool[172]:=KlimaError[2].NizekPritiskKompresor1;
mind_bool[173]:=KlimaError[2].NizekPritiskKompresor2;
mind_bool[174]:=KlimaError[2].NizkaTempVProstoru;
mind_bool[175]:=KlimaError[2].NizkaVlaznost;
mind_bool[176]:=KlimaError[2].PozarniAlarm;
mind_bool[177]:=KlimaError[2].ThermalCutoutHeater1;
mind_bool[178]:=KlimaError[2].ThermalCutoutHeater2;
mind_bool[179]:=KlimaError[2].VentilatorNaMejiStevilaObrUr;
mind_bool[180]:=KlimaError[2].VisokaTempVProstoru;
mind_bool[181]:=KlimaError[2].VisokaVlaznost;
mind_bool[182]:=KlimaError[2].VisokPritiskKompresor1;
mind_bool[183]:=KlimaError[2].VisokPritiskKompresor2;
mind_bool[184]:=KlimaError[2].ZamasenFilter;
mind_bool[185]:=KlimaError[2].ZunanjiAlarm;
mind_bool[186]:=KlimaError[3].AlarmKompresor1;
mind_bool[187]:=KlimaError[3].AlarmKompresor2;
mind_bool[188]:=KlimaError[3].FenThermalCutout;
mind_bool[189]:=KlimaError[3].IzlivVode;
mind_bool[190]:=KlimaError[3].Kompresor1naMejiStevilaObrUr;
mind_bool[191]:=KlimaError[3].Kompresor2naMejiStevilaObrUr;
mind_bool[192]:=KlimaError[3].NapakaPriPretokuVode;
mind_bool[193]:=KlimaError[3].NapakaPriPretokuZraka;
mind_bool[194]:=KlimaError[3].NapakaSenzorVlaznosti;
mind_bool[195]:=KlimaError[3].NapakaTSTemperaturaProstora;
mind_bool[196]:=KlimaError[3].NapakaVlazilca;
mind_bool[197]:=KlimaError[3].NizekPritiskKompresor1;
mind_bool[198]:=KlimaError[3].NizekPritiskKompresor2;
mind_bool[199]:=KlimaError[3].NizkaTempVProstoru;
mind_bool[200]:=KlimaError[3].NizkaVlaznost;
mind_bool[201]:=KlimaError[3].PozarniAlarm;
mind_bool[202]:=KlimaError[3].ThermalCutoutHeater1;
mind_bool[203]:=KlimaError[3].ThermalCutoutHeater2;
mind_bool[204]:=KlimaError[3].VentilatorNaMejiStevilaObrUr;
mind_bool[205]:=KlimaError[3].VisokaTempVProstoru;
mind_bool[206]:=KlimaError[3].VisokaVlaznost;
mind_bool[207]:=KlimaError[3].VisokPritiskKompresor1;
mind_bool[208]:=KlimaError[3].VisokPritiskKompresor2;
mind_bool[209]:=KlimaError[3].ZamasenFilter;
mind_bool[210]:=KlimaError[3].ZunanjiAlarm;
mind_bool[211]:=KlimaError[4].AlarmKompresor1;
mind_bool[212]:=KlimaError[4].AlarmKompresor2;
mind_bool[213]:=KlimaError[4].FenThermalCutout;
mind_bool[214]:=KlimaError[4].IzlivVode;
mind_bool[215]:=KlimaError[4].Kompresor1naMejiStevilaObrUr;
mind_bool[216]:=KlimaError[4].Kompresor2naMejiStevilaObrUr;
mind_bool[217]:=KlimaError[4].NapakaPriPretokuVode;
mind_bool[218]:=KlimaError[4].NapakaPriPretokuZraka;
mind_bool[219]:=KlimaError[4].NapakaSenzorVlaznosti;
mind_bool[220]:=KlimaError[4].NapakaTSTemperaturaProstora;
mind_bool[221]:=KlimaError[4].NapakaVlazilca;
mind_bool[222]:=KlimaError[4].NizekPritiskKompresor1;
mind_bool[223]:=KlimaError[4].NizekPritiskKompresor2;
mind_bool[224]:=KlimaError[4].NizkaTempVProstoru;
mind_bool[225]:=KlimaError[4].NizkaVlaznost;
mind_bool[226]:=KlimaError[4].PozarniAlarm;
mind_bool[227]:=KlimaError[4].ThermalCutoutHeater1;
mind_bool[228]:=KlimaError[4].ThermalCutoutHeater2;
mind_bool[229]:=KlimaError[4].VentilatorNaMejiStevilaObrUr;
mind_bool[230]:=KlimaError[4].VisokaTempVProstoru;
mind_bool[231]:=KlimaError[4].VisokaVlaznost;
mind_bool[232]:=KlimaError[4].VisokPritiskKompresor1;
mind_bool[233]:=KlimaError[4].VisokPritiskKompresor2;
mind_bool[234]:=KlimaError[4].ZamasenFilter;
mind_bool[235]:=KlimaError[4].ZunanjiAlarm;
mind_bool[236]:=KlimaError[5].AlarmKompresor1;
mind_bool[237]:=KlimaError[5].AlarmKompresor2;
mind_bool[238]:=KlimaError[5].FenThermalCutout;
mind_bool[239]:=KlimaError[5].IzlivVode;
mind_bool[240]:=KlimaError[5].Kompresor1naMejiStevilaObrUr;
mind_bool[241]:=KlimaError[5].Kompresor2naMejiStevilaObrUr;
mind_bool[242]:=KlimaError[5].NapakaPriPretokuVode;
mind_bool[243]:=KlimaError[5].NapakaPriPretokuZraka;
mind_bool[244]:=KlimaError[5].NapakaSenzorVlaznosti;
mind_bool[245]:=KlimaError[5].NapakaTSTemperaturaProstora;
mind_bool[246]:=KlimaError[5].NapakaVlazilca;
mind_bool[247]:=KlimaError[5].NizekPritiskKompresor1;
mind_bool[248]:=KlimaError[5].NizekPritiskKompresor2;
mind_bool[249]:=KlimaError[5].NizkaTempVProstoru;
mind_bool[250]:=KlimaError[5].NizkaVlaznost;
mind_bool[251]:=KlimaError[5].PozarniAlarm;
mind_bool[252]:=KlimaError[5].ThermalCutoutHeater1;
mind_bool[253]:=KlimaError[5].ThermalCutoutHeater2;
mind_bool[254]:=KlimaError[5].VentilatorNaMejiStevilaObrUr;
mind_bool[255]:=KlimaError[5].VisokaTempVProstoru;
mind_bool[256]:=KlimaError[5].VisokaVlaznost;
mind_bool[257]:=KlimaError[5].VisokPritiskKompresor1;
mind_bool[258]:=KlimaError[5].VisokPritiskKompresor2;
mind_bool[259]:=KlimaError[5].ZamasenFilter;
mind_bool[260]:=KlimaError[5].ZunanjiAlarm;
mind_bool[261]:=KlimaError[6].AlarmKompresor1;
mind_bool[262]:=KlimaError[6].AlarmKompresor2;
mind_bool[263]:=KlimaError[6].FenThermalCutout;
mind_bool[264]:=KlimaError[6].IzlivVode;
mind_bool[265]:=KlimaError[6].Kompresor1naMejiStevilaObrUr;
mind_bool[266]:=KlimaError[6].Kompresor2naMejiStevilaObrUr;
mind_bool[267]:=KlimaError[6].NapakaPriPretokuVode;
mind_bool[268]:=KlimaError[6].NapakaPriPretokuZraka;
mind_bool[269]:=KlimaError[6].NapakaSenzorVlaznosti;
mind_bool[270]:=KlimaError[6].NapakaTSTemperaturaProstora;
mind_bool[271]:=KlimaError[6].NapakaVlazilca;
mind_bool[272]:=KlimaError[6].NizekPritiskKompresor1;
mind_bool[273]:=KlimaError[6].NizekPritiskKompresor2;
mind_bool[274]:=KlimaError[6].NizkaTempVProstoru;
mind_bool[275]:=KlimaError[6].NizkaVlaznost;
mind_bool[276]:=KlimaError[6].PozarniAlarm;
mind_bool[277]:=KlimaError[6].ThermalCutoutHeater1;
mind_bool[278]:=KlimaError[6].ThermalCutoutHeater2;
mind_bool[279]:=KlimaError[6].VentilatorNaMejiStevilaObrUr;
mind_bool[280]:=KlimaError[6].VisokaTempVProstoru;
mind_bool[281]:=KlimaError[6].VisokaVlaznost;
mind_bool[282]:=KlimaError[6].VisokPritiskKompresor1;
mind_bool[283]:=KlimaError[6].VisokPritiskKompresor2;
mind_bool[284]:=KlimaError[6].ZamasenFilter;
mind_bool[285]:=KlimaError[6].ZunanjiAlarm;
mind_bool[286]:=NacDeloKlima1_2Avtom;
mind_bool[287]:=NacDeloKlima3_4Avtom;
mind_bool[288]:=NacDeloKlima5_6Avtom;
mind_bool[289]:=NapakaSenzorTemp1;
mind_bool[290]:=NapakaSenzorTemp2;
mind_bool[291]:=NapakaSenzorTemp3;
mind_bool[292]:=NapakaSenzorTemp4;
mind_bool[293]:=NapakaSenzorVlaga1;
mind_bool[294]:=NapakaSenzorVlaga2;
mind_bool[295]:=NapakaSenzorVlaga3;
mind_bool[296]:=NapakaSenzorVlaga4;
mind_bool[297]:=NastaviCasNaKrmilniku;
mind_bool[298]:=NastavitevUreKrUspesna;
mind_bool[299]:=OpozoriloBaterijaPLC;
mind_bool[300]:=OpozoriloPMM2x17med60in80[10];
mind_bool[301]:=OpozoriloPMM2x17med60in80[11];
mind_bool[302]:=OpozoriloPMM2x17med60in80[12];
mind_bool[303]:=OpozoriloPMM2x17med60in80[13];
mind_bool[304]:=OpozoriloPMM2x17med60in80[14];
mind_bool[305]:=OpozoriloPMM2x17med60in80[15];
mind_bool[306]:=OpozoriloPMM2x17med60in80[16];
mind_bool[307]:=OpozoriloPMM2x17med60in80[17];
mind_bool[308]:=OpozoriloPMM2x17med60in80[18];
mind_bool[309]:=OpozoriloPMM2x17med60in80[19];
mind_bool[310]:=OpozoriloPMM2x17med60in80[1];
mind_bool[311]:=OpozoriloPMM2x17med60in80[20];
mind_bool[312]:=OpozoriloPMM2x17med60in80[21];
mind_bool[313]:=OpozoriloPMM2x17med60in80[22];
mind_bool[314]:=OpozoriloPMM2x17med60in80[23];
mind_bool[315]:=OpozoriloPMM2x17med60in80[24];
mind_bool[316]:=OpozoriloPMM2x17med60in80[25];
mind_bool[317]:=OpozoriloPMM2x17med60in80[26];
mind_bool[318]:=OpozoriloPMM2x17med60in80[27];
mind_bool[319]:=OpozoriloPMM2x17med60in80[28];
mind_bool[320]:=OpozoriloPMM2x17med60in80[29];
mind_bool[321]:=OpozoriloPMM2x17med60in80[2];
mind_bool[322]:=OpozoriloPMM2x17med60in80[30];
mind_bool[323]:=OpozoriloPMM2x17med60in80[31];
mind_bool[324]:=OpozoriloPMM2x17med60in80[32];
mind_bool[325]:=OpozoriloPMM2x17med60in80[33];
mind_bool[326]:=OpozoriloPMM2x17med60in80[34];
mind_bool[327]:=OpozoriloPMM2x17med60in80[35];
mind_bool[328]:=OpozoriloPMM2x17med60in80[36];
mind_bool[329]:=OpozoriloPMM2x17med60in80[37];
mind_bool[330]:=OpozoriloPMM2x17med60in80[38];
mind_bool[331]:=OpozoriloPMM2x17med60in80[39];
mind_bool[332]:=OpozoriloPMM2x17med60in80[3];
mind_bool[333]:=OpozoriloPMM2x17med60in80[40];
mind_bool[334]:=OpozoriloPMM2x17med60in80[41];
mind_bool[335]:=OpozoriloPMM2x17med60in80[42];
mind_bool[336]:=OpozoriloPMM2x17med60in80[4];
mind_bool[337]:=OpozoriloPMM2x17med60in80[5];
mind_bool[338]:=OpozoriloPMM2x17med60in80[6];
mind_bool[339]:=OpozoriloPMM2x17med60in80[7];
mind_bool[340]:=OpozoriloPMM2x17med60in80[8];
mind_bool[341]:=OpozoriloPMM2x17med60in80[9];
mind_bool[342]:=PhaseBool[0];
mind_bool[343]:=PhaseBool[1];
mind_bool[344]:=PhaseBool[2];
mind_bool[345]:=PhaseNext;
mind_bool[346]:=PhasePrev;
mind_bool[347]:=PMM1OverCurrentBetw[1];
mind_bool[348]:=PMM1OverCurrentBetw[2];
mind_bool[349]:=PMM1OverCurrentBetw[3];
mind_bool[350]:=PMM1OverCurrentOver[1];
mind_bool[351]:=PMM1OverCurrentOver[2];
mind_bool[352]:=PMM1OverCurrentOver[3];
mind_bool[353]:=PMM1OverVoltage;
mind_bool[354]:=PMM2OverCurrentBetw[1];
mind_bool[355]:=PMM2OverCurrentBetw[2];
mind_bool[356]:=PMM2OverCurrentBetw[3];
mind_bool[357]:=PMM2OverCurrentOver[1];
mind_bool[358]:=PMM2OverCurrentOver[2];
mind_bool[359]:=PMM2OverCurrentOver[3];
mind_bool[360]:=PMM2OverVoltage;
mind_bool[361]:=PMM2x17;
mind_bool[362]:=RocniVklopKlima1;
mind_bool[363]:=RocniVklopKlima2;
mind_bool[364]:=RocniVklopKlima3;
mind_bool[365]:=RocniVklopKlima4;
mind_bool[366]:=RocniVklopKlima5;
mind_bool[367]:=RocniVklopKlima6;
mind_bool[368]:=SinhronizacijaPanelOK;
mind_bool[369]:=SinhronizirajCas_Panel;
mind_bool[370]:=SkupneNapakeNaprav_Klima1;
mind_bool[371]:=SkupneNapakeNaprav_Klima2;
mind_bool[372]:=SkupneNapakeNaprav_Klima3;
mind_bool[373]:=SkupneNapakeNaprav_Klima4;
mind_bool[374]:=SkupneNapakeNaprav_Klima5;
mind_bool[375]:=SkupneNapakeNaprav_Klima6;
mind_bool[376]:=SkupneNapakeNaprav_Komunikacija;
mind_bool[377]:=SkupneNapakeNaprav_PMM17VirBVirA;
mind_bool[378]:=SkupneNapakeNaprav_PMM63VirBVirA;
mind_bool[379]:=SkupneNapakeNaprav_TempVlaga;
mind_bool[380]:=StanjeKlimat2_1_Delovanje;
mind_bool[381]:=StanjeKlimat2_2_Delovanje;
mind_bool[382]:=StanjeKlimat2_3_Delovanje;
mind_bool[383]:=StanjeKlimat2_4_Delovanje;
mind_bool[384]:=StanjeKlimat2_5_Delovanje;
mind_bool[385]:=StanjeKlimat2_6_Delovanje;
mind_bool[386]:=StanjeUPSKrmOmara_BaterijskiNacin;
mind_bool[387]:=StanjeUPSKrmOmara_Polnjenje;
mind_bool[388]:=UserLoggedIn;
mind_bool[389]:=XVH_AlarmOn;
mind_bool[390]:=Klimat2_1_Vklop;
mind_bool[391]:=Klimat2_2_Vklop;
mind_bool[392]:=Klimat2_3_Vklop;
mind_bool[393]:=Klimat2_4_Vklop;
mind_bool[394]:=Klimat2_5_Vklop;
mind_bool[395]:=Klimat2_6_Vklop;
mind_bool[396]:=ErrCommScada2;
mind_bool[397]:=ComSCADA2;
mind_bool[398]:=ComSCADA3;
mind_bool[399]:=AlarmSKTemp5_Previsoka;
mind_bool[400]:=AlarmSKTemp6_Previsoka;
mind_bool[401]:=AlarmTempTIA5Previsoka;
mind_bool[402]:=AlarmTempTIA6Previsoka;
mind_bool[403]:=NapakaSenzorTemp5;
mind_bool[404]:=NapakaSenzorTemp6;
mind_bool[405]:=NapakaSenzorVlaga5;
mind_bool[406]:=NapakaSenzorVlaga6;
mind_bool[407]:=AlarmTempTIA235Previsoka;
mind_bool[408]:=AlarmTempTIA46Previsoka;
(*Branje INT*)
(**)
mind[0]:=DatumCas.Dan;
mind[1]:=DatumCas.Leto;
mind[2]:=DatumCas.Leto2;
mind[3]:=DatumCas.Mesec;
mind[4]:=DatumCas.Minuta;
mind[5]:=DatumCas.Sekunda;
mind[6]:=DatumCas.Ura;
mind[7]:=ErrorComKlima[1].Status;
mind[8]:=ErrorComKlima[2].Status;
mind[9]:=ErrorComKlima[3].Status;
mind[10]:=ErrorComKlima[4].Status;
mind[11]:=ErrorComKlima[5].Status;
mind[12]:=ErrorComKlima[6].Status;
mind[13]:=ErrorComPMM[1].Status;
mind[14]:=ErrorComPMM[2].Status;
mind[15]:=Klima[1].GrelecStatus;
mind[16]:=Klima[1].IzhodniVentStatus;
mind[17]:=Klima[1].KompresorStatus;
mind[18]:=Klima[1].NacinRazvlaz;
mind[19]:=Klima[1].VlazilecStatus;
mind[20]:=Klima[2].GrelecStatus;
mind[21]:=Klima[2].IzhodniVentStatus;
mind[22]:=Klima[2].KompresorStatus;
mind[23]:=Klima[2].NacinRazvlaz;
mind[24]:=Klima[2].VlazilecStatus;
mind[25]:=Klima[3].GrelecStatus;
mind[26]:=Klima[3].IzhodniVentStatus;
mind[27]:=Klima[3].KompresorStatus;
mind[28]:=Klima[3].NacinRazvlaz;
mind[29]:=Klima[3].VlazilecStatus;
mind[30]:=Klima[4].GrelecStatus;
mind[31]:=Klima[4].IzhodniVentStatus;
mind[32]:=Klima[4].KompresorStatus;
mind[33]:=Klima[4].NacinRazvlaz;
mind[34]:=Klima[4].VlazilecStatus;
mind[35]:=Klima[5].GrelecStatus;
mind[36]:=Klima[5].IzhodniVentStatus;
mind[37]:=Klima[5].KompresorStatus;
mind[38]:=Klima[5].NacinRazvlaz;
mind[39]:=Klima[5].VlazilecStatus;
mind[40]:=Klima[6].GrelecStatus;
mind[41]:=Klima[6].IzhodniVentStatus;
mind[42]:=Klima[6].KompresorStatus;
mind[43]:=Klima[6].NacinRazvlaz;
mind[44]:=Klima[6].VlazilecStatus;
mind[45]:=OznakeFaz[10];
mind[46]:=OznakeFaz[11];
mind[47]:=OznakeFaz[12];
mind[48]:=OznakeFaz[13];
mind[49]:=OznakeFaz[14];
mind[50]:=OznakeFaz[1];
mind[51]:=OznakeFaz[2];
mind[52]:=OznakeFaz[3];
mind[53]:=OznakeFaz[4];
mind[54]:=OznakeFaz[5];
mind[55]:=OznakeFaz[6];
mind[56]:=OznakeFaz[7];
mind[57]:=OznakeFaz[8];
mind[58]:=OznakeFaz[9];
mind[59]:=PhaseNo;
mind[60]:=PMM[1].AlarmPhase[1].C01_16_60to80;
mind[61]:=PMM[1].AlarmPhase[1].C01_16_over80;
mind[62]:=PMM[1].AlarmPhase[1].C17_32_60to80;
mind[63]:=PMM[1].AlarmPhase[1].C17_32_over80;
mind[64]:=PMM[1].AlarmPhase[1].C33_42_60to80;
mind[65]:=PMM[1].AlarmPhase[1].C33_42_over80;
mind[66]:=PMM[1].AlarmPhase[1].GlobalAlarmReg;
mind[67]:=PMM[1].AlarmPhase[2].C01_16_60to80;
mind[68]:=PMM[1].AlarmPhase[2].C01_16_over80;
mind[69]:=PMM[1].AlarmPhase[2].C17_32_60to80;
mind[70]:=PMM[1].AlarmPhase[2].C17_32_over80;
mind[71]:=PMM[1].AlarmPhase[2].C33_42_60to80;
mind[72]:=PMM[1].AlarmPhase[2].C33_42_over80;
mind[73]:=PMM[1].AlarmPhase[2].GlobalAlarmReg;
mind[74]:=PMM[1].AlarmPhase[3].C01_16_60to80;
mind[75]:=PMM[1].AlarmPhase[3].C01_16_over80;
mind[76]:=PMM[1].AlarmPhase[3].C17_32_60to80;
mind[77]:=PMM[1].AlarmPhase[3].C17_32_over80;
mind[78]:=PMM[1].AlarmPhase[3].C33_42_60to80;
mind[79]:=PMM[1].AlarmPhase[3].C33_42_over80;
mind[80]:=PMM[1].AlarmPhase[3].GlobalAlarmReg;
mind[81]:=PMM[2].AlarmPhase[1].C01_16_60to80;
mind[82]:=PMM[2].AlarmPhase[1].C01_16_over80;
mind[83]:=PMM[2].AlarmPhase[1].C17_32_60to80;
mind[84]:=PMM[2].AlarmPhase[1].C17_32_over80;
mind[85]:=PMM[2].AlarmPhase[1].C33_42_60to80;
mind[86]:=PMM[2].AlarmPhase[1].C33_42_over80;
mind[87]:=PMM[2].AlarmPhase[1].GlobalAlarmReg;
mind[88]:=PMM[2].AlarmPhase[2].C01_16_60to80;
mind[89]:=PMM[2].AlarmPhase[2].C01_16_over80;
mind[90]:=PMM[2].AlarmPhase[2].C17_32_60to80;
mind[91]:=PMM[2].AlarmPhase[2].C17_32_over80;
mind[92]:=PMM[2].AlarmPhase[2].C33_42_60to80;
mind[93]:=PMM[2].AlarmPhase[2].C33_42_over80;
mind[94]:=PMM[2].AlarmPhase[2].GlobalAlarmReg;
mind[95]:=PMM[2].AlarmPhase[3].C01_16_60to80;
mind[96]:=PMM[2].AlarmPhase[3].C01_16_over80;
mind[97]:=PMM[2].AlarmPhase[3].C17_32_60to80;
mind[98]:=PMM[2].AlarmPhase[3].C17_32_over80;
mind[99]:=PMM[2].AlarmPhase[3].C33_42_60to80;
mind[100]:=PMM[2].AlarmPhase[3].C33_42_over80;
mind[101]:=PMM[2].AlarmPhase[3].GlobalAlarmReg;
mind[102]:=PMMPanel.AlarmPhase[1].C01_16_60to80;
mind[103]:=PMMPanel.AlarmPhase[1].C01_16_over80;
mind[104]:=PMMPanel.AlarmPhase[1].C17_32_60to80;
mind[105]:=PMMPanel.AlarmPhase[1].C17_32_over80;
mind[106]:=PMMPanel.AlarmPhase[1].C33_42_60to80;
mind[107]:=PMMPanel.AlarmPhase[1].C33_42_over80;
mind[108]:=PMMPanel.AlarmPhase[1].GlobalAlarmReg;
mind[109]:=PMMPanel.AlarmPhase[2].C01_16_60to80;
mind[110]:=PMMPanel.AlarmPhase[2].C01_16_over80;
mind[111]:=PMMPanel.AlarmPhase[2].C17_32_60to80;
mind[112]:=PMMPanel.AlarmPhase[2].C17_32_over80;
mind[113]:=PMMPanel.AlarmPhase[2].C33_42_60to80;
mind[114]:=PMMPanel.AlarmPhase[2].C33_42_over80;
mind[115]:=PMMPanel.AlarmPhase[2].GlobalAlarmReg;
mind[116]:=PMMPanel.AlarmPhase[3].C01_16_60to80;
mind[117]:=PMMPanel.AlarmPhase[3].C01_16_over80;
mind[118]:=PMMPanel.AlarmPhase[3].C17_32_60to80;
mind[119]:=PMMPanel.AlarmPhase[3].C17_32_over80;
mind[120]:=PMMPanel.AlarmPhase[3].C33_42_60to80;
mind[121]:=PMMPanel.AlarmPhase[3].C33_42_over80;
mind[122]:=PMMPanel.AlarmPhase[3].GlobalAlarmReg;
mind[123]:=StUrZaPreklopKlim1_2;
mind[124]:=StUrZaPreklopKlim3_4;
mind[125]:=StUrZaPreklopKlim5_6;
mind[126]:=UPSstatus_Prikaz_PanelSCADA;
mind[127]:=UserCurrentLevel;
mind[128]:=ErrorComKlima[1].Code[0];
mind[129]:=ErrorComKlima[1].Code[10];
mind[130]:=ErrorComKlima[1].Code[11];
mind[131]:=ErrorComKlima[1].Code[12];
mind[132]:=ErrorComKlima[1].Code[13];
mind[133]:=ErrorComKlima[1].Code[14];
mind[134]:=ErrorComKlima[1].Code[15];
mind[135]:=ErrorComKlima[1].Code[1];
mind[136]:=ErrorComKlima[1].Code[2];
mind[137]:=ErrorComKlima[1].Code[3];
mind[138]:=ErrorComKlima[1].Code[4];
mind[139]:=ErrorComKlima[1].Code[5];
mind[140]:=ErrorComKlima[1].Code[6];
mind[141]:=ErrorComKlima[1].Code[7];
mind[142]:=ErrorComKlima[1].Code[8];
mind[143]:=ErrorComKlima[1].Code[9];
mind[144]:=ErrorComKlima[2].Code[0];
mind[145]:=ErrorComKlima[2].Code[10];
mind[146]:=ErrorComKlima[2].Code[11];
mind[147]:=ErrorComKlima[2].Code[12];
mind[148]:=ErrorComKlima[2].Code[13];
mind[149]:=ErrorComKlima[2].Code[14];
mind[150]:=ErrorComKlima[2].Code[15];
mind[151]:=ErrorComKlima[2].Code[1];
mind[152]:=ErrorComKlima[2].Code[2];
mind[153]:=ErrorComKlima[2].Code[3];
mind[154]:=ErrorComKlima[2].Code[4];
mind[155]:=ErrorComKlima[2].Code[5];
mind[156]:=ErrorComKlima[2].Code[6];
mind[157]:=ErrorComKlima[2].Code[7];
mind[158]:=ErrorComKlima[2].Code[8];
mind[159]:=ErrorComKlima[2].Code[9];
mind[160]:=ErrorComKlima[3].Code[0];
mind[161]:=ErrorComKlima[3].Code[10];
mind[162]:=ErrorComKlima[3].Code[11];
mind[163]:=ErrorComKlima[3].Code[12];
mind[164]:=ErrorComKlima[3].Code[13];
mind[165]:=ErrorComKlima[3].Code[14];
mind[166]:=ErrorComKlima[3].Code[15];
mind[167]:=ErrorComKlima[3].Code[1];
mind[168]:=ErrorComKlima[3].Code[2];
mind[169]:=ErrorComKlima[3].Code[3];
mind[170]:=ErrorComKlima[3].Code[4];
mind[171]:=ErrorComKlima[3].Code[5];
mind[172]:=ErrorComKlima[3].Code[6];
mind[173]:=ErrorComKlima[3].Code[7];
mind[174]:=ErrorComKlima[3].Code[8];
mind[175]:=ErrorComKlima[3].Code[9];
mind[176]:=ErrorComKlima[4].Code[0];
mind[177]:=ErrorComKlima[4].Code[10];
mind[178]:=ErrorComKlima[4].Code[11];
mind[179]:=ErrorComKlima[4].Code[12];
mind[180]:=ErrorComKlima[4].Code[13];
mind[181]:=ErrorComKlima[4].Code[14];
mind[182]:=ErrorComKlima[4].Code[15];
mind[183]:=ErrorComKlima[4].Code[1];
mind[184]:=ErrorComKlima[4].Code[2];
mind[185]:=ErrorComKlima[4].Code[3];
mind[186]:=ErrorComKlima[4].Code[4];
mind[187]:=ErrorComKlima[4].Code[5];
mind[188]:=ErrorComKlima[4].Code[6];
mind[189]:=ErrorComKlima[4].Code[7];
mind[190]:=ErrorComKlima[4].Code[8];
mind[191]:=ErrorComKlima[4].Code[9];
mind[192]:=ErrorComKlima[5].Code[0];
mind[193]:=ErrorComKlima[5].Code[10];
mind[194]:=ErrorComKlima[5].Code[11];
mind[195]:=ErrorComKlima[5].Code[12];
mind[196]:=ErrorComKlima[5].Code[13];
mind[197]:=ErrorComKlima[5].Code[14];
mind[198]:=ErrorComKlima[5].Code[15];
mind[199]:=ErrorComKlima[5].Code[1];
mind[200]:=ErrorComKlima[5].Code[2];
mind[201]:=ErrorComKlima[5].Code[3];
mind[202]:=ErrorComKlima[5].Code[4];
mind[203]:=ErrorComKlima[5].Code[5];
mind[204]:=ErrorComKlima[5].Code[6];
mind[205]:=ErrorComKlima[5].Code[7];
mind[206]:=ErrorComKlima[5].Code[8];
mind[207]:=ErrorComKlima[5].Code[9];
mind[208]:=ErrorComKlima[6].Code[0];
mind[209]:=ErrorComKlima[6].Code[10];
mind[210]:=ErrorComKlima[6].Code[11];
mind[211]:=ErrorComKlima[6].Code[12];
mind[212]:=ErrorComKlima[6].Code[13];
mind[213]:=ErrorComKlima[6].Code[14];
mind[214]:=ErrorComKlima[6].Code[15];
mind[215]:=ErrorComKlima[6].Code[1];
mind[216]:=ErrorComKlima[6].Code[2];
mind[217]:=ErrorComKlima[6].Code[3];
mind[218]:=ErrorComKlima[6].Code[4];
mind[219]:=ErrorComKlima[6].Code[5];
mind[220]:=ErrorComKlima[6].Code[6];
mind[221]:=ErrorComKlima[6].Code[7];
mind[222]:=ErrorComKlima[6].Code[8];
mind[223]:=ErrorComKlima[6].Code[9];
mind[224]:=ErrorComPMM[1].Code[0];
mind[225]:=ErrorComPMM[1].Code[10];
mind[226]:=ErrorComPMM[1].Code[11];
mind[227]:=ErrorComPMM[1].Code[12];
mind[228]:=ErrorComPMM[1].Code[13];
mind[229]:=ErrorComPMM[1].Code[14];
mind[230]:=ErrorComPMM[1].Code[15];
mind[231]:=ErrorComPMM[1].Code[1];
mind[232]:=ErrorComPMM[1].Code[2];
mind[233]:=ErrorComPMM[1].Code[3];
mind[234]:=ErrorComPMM[1].Code[4];
mind[235]:=ErrorComPMM[1].Code[5];
mind[236]:=ErrorComPMM[1].Code[6];
mind[237]:=ErrorComPMM[1].Code[7];
mind[238]:=ErrorComPMM[1].Code[8];
mind[239]:=ErrorComPMM[1].Code[9];
mind[240]:=ErrorComPMM[2].Code[0];
mind[241]:=ErrorComPMM[2].Code[10];
mind[242]:=ErrorComPMM[2].Code[11];
mind[243]:=ErrorComPMM[2].Code[12];
mind[244]:=ErrorComPMM[2].Code[13];
mind[245]:=ErrorComPMM[2].Code[14];
mind[246]:=ErrorComPMM[2].Code[15];
mind[247]:=ErrorComPMM[2].Code[1];
mind[248]:=ErrorComPMM[2].Code[2];
mind[249]:=ErrorComPMM[2].Code[3];
mind[250]:=ErrorComPMM[2].Code[4];
mind[251]:=ErrorComPMM[2].Code[5];
mind[252]:=ErrorComPMM[2].Code[6];
mind[253]:=ErrorComPMM[2].Code[7];
mind[254]:=ErrorComPMM[2].Code[8];
mind[255]:=ErrorComPMM[2].Code[9];
mind[256]:=kom_nast_cas_izpada;
(*Branje UINT*)
(**)
(*Branje LONG*)
(**)
(*Branje REAL*)
(**)
Read_Real(rVar:=AktualniSetPointTemp1_2,lo:=4000,hi:=4001);
Read_Real(rVar:=AktualniSetPointTemp3_4,lo:=4002,hi:=4003);
Read_Real(rVar:=AktualniSetPointTemp5_6,lo:=4004,hi:=4005);
Read_Real(rVar:=Klima1ure,lo:=4006,hi:=4007);
Read_Real(rVar:=Klima2ure,lo:=4008,hi:=4009);
Read_Real(rVar:=Klima3ure,lo:=4010,hi:=4011);
Read_Real(rVar:=Klima4ure,lo:=4012,hi:=4013);
Read_Real(rVar:=Klima5ure,lo:=4014,hi:=4015);
Read_Real(rVar:=Klima6ure,lo:=4016,hi:=4017);
Read_Real(rVar:=Klima[1].NastMaxTemp,lo:=4018,hi:=4019);
Read_Real(rVar:=Klima[1].NastMaxVlaznost,lo:=4020,hi:=4021);
Read_Real(rVar:=Klima[1].NastMinTemp,lo:=4022,hi:=4023);
Read_Real(rVar:=Klima[1].NastMinVlaznost,lo:=4024,hi:=4025);
Read_Real(rVar:=Klima[1].NastTempProstora,lo:=4026,hi:=4027);
Read_Real(rVar:=Klima[1].NastVlaznost,lo:=4028,hi:=4029);
Read_Real(rVar:=Klima[1].ObratUreFilter,lo:=4030,hi:=4031);
Read_Real(rVar:=Klima[1].ObratUreKompresor1,lo:=4032,hi:=4033);
Read_Real(rVar:=Klima[1].ObratUreKompresor2,lo:=4034,hi:=4035);
Read_Real(rVar:=Klima[1].ObratUreVent,lo:=4036,hi:=4037);
Read_Real(rVar:=Klima[1].TemperaturaProstora,lo:=4038,hi:=4039);
Read_Real(rVar:=Klima[1].VlaznostProstora,lo:=4040,hi:=4041);
Read_Real(rVar:=Klima[2].NastMaxTemp,lo:=4042,hi:=4043);
Read_Real(rVar:=Klima[2].NastMaxVlaznost,lo:=4044,hi:=4045);
Read_Real(rVar:=Klima[2].NastMinTemp,lo:=4046,hi:=4047);
Read_Real(rVar:=Klima[2].NastMinVlaznost,lo:=4048,hi:=4049);
Read_Real(rVar:=Klima[2].NastTempProstora,lo:=4050,hi:=4051);
Read_Real(rVar:=Klima[2].NastVlaznost,lo:=4052,hi:=4053);
Read_Real(rVar:=Klima[2].ObratUreFilter,lo:=4054,hi:=4055);
Read_Real(rVar:=Klima[2].ObratUreKompresor1,lo:=4056,hi:=4057);
Read_Real(rVar:=Klima[2].ObratUreKompresor2,lo:=4058,hi:=4059);
Read_Real(rVar:=Klima[2].ObratUreVent,lo:=4060,hi:=4061);
Read_Real(rVar:=Klima[2].TemperaturaProstora,lo:=4062,hi:=4063);
Read_Real(rVar:=Klima[2].VlaznostProstora,lo:=4064,hi:=4065);
Read_Real(rVar:=Klima[3].NastMaxTemp,lo:=4066,hi:=4067);
Read_Real(rVar:=Klima[3].NastMaxVlaznost,lo:=4068,hi:=4069);
Read_Real(rVar:=Klima[3].NastMinTemp,lo:=4070,hi:=4071);
Read_Real(rVar:=Klima[3].NastMinVlaznost,lo:=4072,hi:=4073);
Read_Real(rVar:=Klima[3].NastTempProstora,lo:=4074,hi:=4075);
Read_Real(rVar:=Klima[3].NastVlaznost,lo:=4076,hi:=4077);
Read_Real(rVar:=Klima[3].ObratUreFilter,lo:=4078,hi:=4079);
Read_Real(rVar:=Klima[3].ObratUreKompresor1,lo:=4080,hi:=4081);
Read_Real(rVar:=Klima[3].ObratUreKompresor2,lo:=4082,hi:=4083);
Read_Real(rVar:=Klima[3].ObratUreVent,lo:=4084,hi:=4085);
Read_Real(rVar:=Klima[3].TemperaturaProstora,lo:=4086,hi:=4087);
Read_Real(rVar:=Klima[3].VlaznostProstora,lo:=4088,hi:=4089);
Read_Real(rVar:=Klima[4].NastMaxTemp,lo:=4090,hi:=4091);
Read_Real(rVar:=Klima[4].NastMaxVlaznost,lo:=4092,hi:=4093);
Read_Real(rVar:=Klima[4].NastMinTemp,lo:=4094,hi:=4095);
Read_Real(rVar:=Klima[4].NastMinVlaznost,lo:=4096,hi:=4097);
Read_Real(rVar:=Klima[4].NastTempProstora,lo:=4098,hi:=4099);
Read_Real(rVar:=Klima[4].NastVlaznost,lo:=4100,hi:=4101);
Read_Real(rVar:=Klima[4].ObratUreFilter,lo:=4102,hi:=4103);
Read_Real(rVar:=Klima[4].ObratUreKompresor1,lo:=4104,hi:=4105);
Read_Real(rVar:=Klima[4].ObratUreKompresor2,lo:=4106,hi:=4107);
Read_Real(rVar:=Klima[4].ObratUreVent,lo:=4108,hi:=4109);
Read_Real(rVar:=Klima[4].TemperaturaProstora,lo:=4110,hi:=4111);
Read_Real(rVar:=Klima[4].VlaznostProstora,lo:=4112,hi:=4113);
Read_Real(rVar:=Klima[5].NastMaxTemp,lo:=4114,hi:=4115);
Read_Real(rVar:=Klima[5].NastMaxVlaznost,lo:=4116,hi:=4117);
Read_Real(rVar:=Klima[5].NastMinTemp,lo:=4118,hi:=4119);
Read_Real(rVar:=Klima[5].NastMinVlaznost,lo:=4120,hi:=4121);
Read_Real(rVar:=Klima[5].NastTempProstora,lo:=4122,hi:=4123);
Read_Real(rVar:=Klima[5].NastVlaznost,lo:=4124,hi:=4125);
Read_Real(rVar:=Klima[5].ObratUreFilter,lo:=4126,hi:=4127);
Read_Real(rVar:=Klima[5].ObratUreKompresor1,lo:=4128,hi:=4129);
Read_Real(rVar:=Klima[5].ObratUreKompresor2,lo:=4130,hi:=4131);
Read_Real(rVar:=Klima[5].ObratUreVent,lo:=4132,hi:=4133);
Read_Real(rVar:=Klima[5].TemperaturaProstora,lo:=4134,hi:=4135);
Read_Real(rVar:=Klima[5].VlaznostProstora,lo:=4136,hi:=4137);
Read_Real(rVar:=Klima[6].NastMaxTemp,lo:=4138,hi:=4139);
Read_Real(rVar:=Klima[6].NastMaxVlaznost,lo:=4140,hi:=4141);
Read_Real(rVar:=Klima[6].NastMinTemp,lo:=4142,hi:=4143);
Read_Real(rVar:=Klima[6].NastMinVlaznost,lo:=4144,hi:=4145);
Read_Real(rVar:=Klima[6].NastTempProstora,lo:=4146,hi:=4147);
Read_Real(rVar:=Klima[6].NastVlaznost,lo:=4148,hi:=4149);
Read_Real(rVar:=Klima[6].ObratUreFilter,lo:=4150,hi:=4151);
Read_Real(rVar:=Klima[6].ObratUreKompresor1,lo:=4152,hi:=4153);
Read_Real(rVar:=Klima[6].ObratUreKompresor2,lo:=4154,hi:=4155);
Read_Real(rVar:=Klima[6].ObratUreVent,lo:=4156,hi:=4157);
Read_Real(rVar:=Klima[6].TemperaturaProstora,lo:=4158,hi:=4159);
Read_Real(rVar:=Klima[6].VlaznostProstora,lo:=4160,hi:=4161);
Read_Real(rVar:=PMM[1].ActiveEnergyConsumed_kWh,lo:=4162,hi:=4163);
Read_Real(rVar:=PMM[1].ActivePowerPhaseA_kW,lo:=4164,hi:=4165);
Read_Real(rVar:=PMM[1].ActivePowerPhaseB_kW,lo:=4166,hi:=4167);
Read_Real(rVar:=PMM[1].ActivePowerPhaseC_kW,lo:=4168,hi:=4169);
Read_Real(rVar:=PMM[1].AparentPowerPhaseA,lo:=4170,hi:=4171);
Read_Real(rVar:=PMM[1].AparentPowerPhaseB,lo:=4172,hi:=4173);
Read_Real(rVar:=PMM[1].AparentPowerPhaseC,lo:=4174,hi:=4175);
Read_Real(rVar:=PMM[1].AverageCurrent_A,lo:=4176,hi:=4177);
Read_Real(rVar:=PMM[1].AveragePhaseToNeutral_V,lo:=4178,hi:=4179);
Read_Real(rVar:=PMM[1].AveragePhaseToPhase_V,lo:=4180,hi:=4181);
Read_Real(rVar:=PMM[1].CurrentInPhaseA_A,lo:=4182,hi:=4183);
Read_Real(rVar:=PMM[1].CurrentInPhaseB_A,lo:=4184,hi:=4185);
Read_Real(rVar:=PMM[1].CurrentInPhaseC_A,lo:=4186,hi:=4187);
Read_Real(rVar:=PMM[1].Frequency_Hz,lo:=4188,hi:=4189);
Read_Real(rVar:=PMM[1].Phase[1].Current[10],lo:=4190,hi:=4191);
Read_Real(rVar:=PMM[1].Phase[1].Current[11],lo:=4192,hi:=4193);
Read_Real(rVar:=PMM[1].Phase[1].Current[12],lo:=4194,hi:=4195);
Read_Real(rVar:=PMM[1].Phase[1].Current[13],lo:=4196,hi:=4197);
Read_Real(rVar:=PMM[1].Phase[1].Current[14],lo:=4198,hi:=4199);
Read_Real(rVar:=PMM[1].Phase[1].Current[15],lo:=4200,hi:=4201);
Read_Real(rVar:=PMM[1].Phase[1].Current[16],lo:=4202,hi:=4203);
Read_Real(rVar:=PMM[1].Phase[1].Current[17],lo:=4204,hi:=4205);
Read_Real(rVar:=PMM[1].Phase[1].Current[18],lo:=4206,hi:=4207);
Read_Real(rVar:=PMM[1].Phase[1].Current[19],lo:=4208,hi:=4209);
Read_Real(rVar:=PMM[1].Phase[1].Current[1],lo:=4210,hi:=4211);
Read_Real(rVar:=PMM[1].Phase[1].Current[20],lo:=4212,hi:=4213);
Read_Real(rVar:=PMM[1].Phase[1].Current[21],lo:=4214,hi:=4215);
Read_Real(rVar:=PMM[1].Phase[1].Current[22],lo:=4216,hi:=4217);
Read_Real(rVar:=PMM[1].Phase[1].Current[23],lo:=4218,hi:=4219);
Read_Real(rVar:=PMM[1].Phase[1].Current[24],lo:=4220,hi:=4221);
Read_Real(rVar:=PMM[1].Phase[1].Current[25],lo:=4222,hi:=4223);
Read_Real(rVar:=PMM[1].Phase[1].Current[26],lo:=4224,hi:=4225);
Read_Real(rVar:=PMM[1].Phase[1].Current[27],lo:=4226,hi:=4227);
Read_Real(rVar:=PMM[1].Phase[1].Current[28],lo:=4228,hi:=4229);
Read_Real(rVar:=PMM[1].Phase[1].Current[29],lo:=4230,hi:=4231);
Read_Real(rVar:=PMM[1].Phase[1].Current[2],lo:=4232,hi:=4233);
Read_Real(rVar:=PMM[1].Phase[1].Current[30],lo:=4234,hi:=4235);
Read_Real(rVar:=PMM[1].Phase[1].Current[31],lo:=4236,hi:=4237);
Read_Real(rVar:=PMM[1].Phase[1].Current[32],lo:=4238,hi:=4239);
Read_Real(rVar:=PMM[1].Phase[1].Current[33],lo:=4240,hi:=4241);
Read_Real(rVar:=PMM[1].Phase[1].Current[34],lo:=4242,hi:=4243);
Read_Real(rVar:=PMM[1].Phase[1].Current[35],lo:=4244,hi:=4245);
Read_Real(rVar:=PMM[1].Phase[1].Current[36],lo:=4246,hi:=4247);
Read_Real(rVar:=PMM[1].Phase[1].Current[37],lo:=4248,hi:=4249);
Read_Real(rVar:=PMM[1].Phase[1].Current[38],lo:=4250,hi:=4251);
Read_Real(rVar:=PMM[1].Phase[1].Current[39],lo:=4252,hi:=4253);
Read_Real(rVar:=PMM[1].Phase[1].Current[3],lo:=4254,hi:=4255);
Read_Real(rVar:=PMM[1].Phase[1].Current[40],lo:=4256,hi:=4257);
Read_Real(rVar:=PMM[1].Phase[1].Current[41],lo:=4258,hi:=4259);
Read_Real(rVar:=PMM[1].Phase[1].Current[42],lo:=4260,hi:=4261);
Read_Real(rVar:=PMM[1].Phase[1].Current[4],lo:=4262,hi:=4263);
Read_Real(rVar:=PMM[1].Phase[1].Current[5],lo:=4264,hi:=4265);
Read_Real(rVar:=PMM[1].Phase[1].Current[6],lo:=4266,hi:=4267);
Read_Real(rVar:=PMM[1].Phase[1].Current[7],lo:=4268,hi:=4269);
Read_Real(rVar:=PMM[1].Phase[1].Current[8],lo:=4270,hi:=4271);
Read_Real(rVar:=PMM[1].Phase[1].Current[9],lo:=4272,hi:=4273);
Read_Real(rVar:=PMM[1].Phase[2].Current[10],lo:=4274,hi:=4275);
Read_Real(rVar:=PMM[1].Phase[2].Current[11],lo:=4276,hi:=4277);
Read_Real(rVar:=PMM[1].Phase[2].Current[12],lo:=4278,hi:=4279);
Read_Real(rVar:=PMM[1].Phase[2].Current[13],lo:=4280,hi:=4281);
Read_Real(rVar:=PMM[1].Phase[2].Current[14],lo:=4282,hi:=4283);
Read_Real(rVar:=PMM[1].Phase[2].Current[15],lo:=4284,hi:=4285);
Read_Real(rVar:=PMM[1].Phase[2].Current[16],lo:=4286,hi:=4287);
Read_Real(rVar:=PMM[1].Phase[2].Current[17],lo:=4288,hi:=4289);
Read_Real(rVar:=PMM[1].Phase[2].Current[18],lo:=4290,hi:=4291);
Read_Real(rVar:=PMM[1].Phase[2].Current[19],lo:=4292,hi:=4293);
Read_Real(rVar:=PMM[1].Phase[2].Current[1],lo:=4294,hi:=4295);
Read_Real(rVar:=PMM[1].Phase[2].Current[20],lo:=4296,hi:=4297);
Read_Real(rVar:=PMM[1].Phase[2].Current[21],lo:=4298,hi:=4299);
Read_Real(rVar:=PMM[1].Phase[2].Current[22],lo:=4300,hi:=4301);
Read_Real(rVar:=PMM[1].Phase[2].Current[23],lo:=4302,hi:=4303);
Read_Real(rVar:=PMM[1].Phase[2].Current[24],lo:=4304,hi:=4305);
Read_Real(rVar:=PMM[1].Phase[2].Current[25],lo:=4306,hi:=4307);
Read_Real(rVar:=PMM[1].Phase[2].Current[26],lo:=4308,hi:=4309);
Read_Real(rVar:=PMM[1].Phase[2].Current[27],lo:=4310,hi:=4311);
Read_Real(rVar:=PMM[1].Phase[2].Current[28],lo:=4312,hi:=4313);
Read_Real(rVar:=PMM[1].Phase[2].Current[29],lo:=4314,hi:=4315);
Read_Real(rVar:=PMM[1].Phase[2].Current[2],lo:=4316,hi:=4317);
Read_Real(rVar:=PMM[1].Phase[2].Current[30],lo:=4318,hi:=4319);
Read_Real(rVar:=PMM[1].Phase[2].Current[31],lo:=4320,hi:=4321);
Read_Real(rVar:=PMM[1].Phase[2].Current[32],lo:=4322,hi:=4323);
Read_Real(rVar:=PMM[1].Phase[2].Current[33],lo:=4324,hi:=4325);
Read_Real(rVar:=PMM[1].Phase[2].Current[34],lo:=4326,hi:=4327);
Read_Real(rVar:=PMM[1].Phase[2].Current[35],lo:=4328,hi:=4329);
Read_Real(rVar:=PMM[1].Phase[2].Current[36],lo:=4330,hi:=4331);
Read_Real(rVar:=PMM[1].Phase[2].Current[37],lo:=4332,hi:=4333);
Read_Real(rVar:=PMM[1].Phase[2].Current[38],lo:=4334,hi:=4335);
Read_Real(rVar:=PMM[1].Phase[2].Current[39],lo:=4336,hi:=4337);
Read_Real(rVar:=PMM[1].Phase[2].Current[3],lo:=4338,hi:=4339);
Read_Real(rVar:=PMM[1].Phase[2].Current[40],lo:=4340,hi:=4341);
Read_Real(rVar:=PMM[1].Phase[2].Current[41],lo:=4342,hi:=4343);
Read_Real(rVar:=PMM[1].Phase[2].Current[42],lo:=4344,hi:=4345);
Read_Real(rVar:=PMM[1].Phase[2].Current[4],lo:=4346,hi:=4347);
Read_Real(rVar:=PMM[1].Phase[2].Current[5],lo:=4348,hi:=4349);
Read_Real(rVar:=PMM[1].Phase[2].Current[6],lo:=4350,hi:=4351);
Read_Real(rVar:=PMM[1].Phase[2].Current[7],lo:=4352,hi:=4353);
Read_Real(rVar:=PMM[1].Phase[2].Current[8],lo:=4354,hi:=4355);
Read_Real(rVar:=PMM[1].Phase[2].Current[9],lo:=4356,hi:=4357);
Read_Real(rVar:=PMM[1].Phase[3].Current[10],lo:=4358,hi:=4359);
Read_Real(rVar:=PMM[1].Phase[3].Current[11],lo:=4360,hi:=4361);
Read_Real(rVar:=PMM[1].Phase[3].Current[12],lo:=4362,hi:=4363);
Read_Real(rVar:=PMM[1].Phase[3].Current[13],lo:=4364,hi:=4365);
Read_Real(rVar:=PMM[1].Phase[3].Current[14],lo:=4366,hi:=4367);
Read_Real(rVar:=PMM[1].Phase[3].Current[15],lo:=4368,hi:=4369);
Read_Real(rVar:=PMM[1].Phase[3].Current[16],lo:=4370,hi:=4371);
Read_Real(rVar:=PMM[1].Phase[3].Current[17],lo:=4372,hi:=4373);
Read_Real(rVar:=PMM[1].Phase[3].Current[18],lo:=4374,hi:=4375);
Read_Real(rVar:=PMM[1].Phase[3].Current[19],lo:=4376,hi:=4377);
Read_Real(rVar:=PMM[1].Phase[3].Current[1],lo:=4378,hi:=4379);
Read_Real(rVar:=PMM[1].Phase[3].Current[20],lo:=4380,hi:=4381);
Read_Real(rVar:=PMM[1].Phase[3].Current[21],lo:=4382,hi:=4383);
Read_Real(rVar:=PMM[1].Phase[3].Current[22],lo:=4384,hi:=4385);
Read_Real(rVar:=PMM[1].Phase[3].Current[23],lo:=4386,hi:=4387);
Read_Real(rVar:=PMM[1].Phase[3].Current[24],lo:=4388,hi:=4389);
Read_Real(rVar:=PMM[1].Phase[3].Current[25],lo:=4390,hi:=4391);
Read_Real(rVar:=PMM[1].Phase[3].Current[26],lo:=4392,hi:=4393);
Read_Real(rVar:=PMM[1].Phase[3].Current[27],lo:=4394,hi:=4395);
Read_Real(rVar:=PMM[1].Phase[3].Current[28],lo:=4396,hi:=4397);
Read_Real(rVar:=PMM[1].Phase[3].Current[29],lo:=4398,hi:=4399);
Read_Real(rVar:=PMM[1].Phase[3].Current[2],lo:=4400,hi:=4401);
Read_Real(rVar:=PMM[1].Phase[3].Current[30],lo:=4402,hi:=4403);
Read_Real(rVar:=PMM[1].Phase[3].Current[31],lo:=4404,hi:=4405);
Read_Real(rVar:=PMM[1].Phase[3].Current[32],lo:=4406,hi:=4407);
Read_Real(rVar:=PMM[1].Phase[3].Current[33],lo:=4408,hi:=4409);
Read_Real(rVar:=PMM[1].Phase[3].Current[34],lo:=4410,hi:=4411);
Read_Real(rVar:=PMM[1].Phase[3].Current[35],lo:=4412,hi:=4413);
Read_Real(rVar:=PMM[1].Phase[3].Current[36],lo:=4414,hi:=4415);
Read_Real(rVar:=PMM[1].Phase[3].Current[37],lo:=4416,hi:=4417);
Read_Real(rVar:=PMM[1].Phase[3].Current[38],lo:=4418,hi:=4419);
Read_Real(rVar:=PMM[1].Phase[3].Current[39],lo:=4420,hi:=4421);
Read_Real(rVar:=PMM[1].Phase[3].Current[3],lo:=4422,hi:=4423);
Read_Real(rVar:=PMM[1].Phase[3].Current[40],lo:=4424,hi:=4425);
Read_Real(rVar:=PMM[1].Phase[3].Current[41],lo:=4426,hi:=4427);
Read_Real(rVar:=PMM[1].Phase[3].Current[42],lo:=4428,hi:=4429);
Read_Real(rVar:=PMM[1].Phase[3].Current[4],lo:=4430,hi:=4431);
Read_Real(rVar:=PMM[1].Phase[3].Current[5],lo:=4432,hi:=4433);
Read_Real(rVar:=PMM[1].Phase[3].Current[6],lo:=4434,hi:=4435);
Read_Real(rVar:=PMM[1].Phase[3].Current[7],lo:=4436,hi:=4437);
Read_Real(rVar:=PMM[1].Phase[3].Current[8],lo:=4438,hi:=4439);
Read_Real(rVar:=PMM[1].Phase[3].Current[9],lo:=4440,hi:=4441);
Read_Real(rVar:=PMM[1].PowerFactorSys,lo:=4442,hi:=4443);
Read_Real(rVar:=PMM[1].ReactiveEnergyConsumed_kVARh,lo:=4444,hi:=4445);
Read_Real(rVar:=PMM[1].ReactivePowerPhaseA,lo:=4446,hi:=4447);
Read_Real(rVar:=PMM[1].ReactivePowerPhaseB,lo:=4448,hi:=4449);
Read_Real(rVar:=PMM[1].ReactivePowerPhaseC,lo:=4450,hi:=4451);
Read_Real(rVar:=PMM[1].TotalActivePower_kW,lo:=4452,hi:=4453);
Read_Real(rVar:=PMM[1].TotalAparentPower_kVA,lo:=4454,hi:=4455);
Read_Real(rVar:=PMM[1].TotalPowerFactor,lo:=4456,hi:=4457);
Read_Real(rVar:=PMM[1].TotalReactivePower_kVAR,lo:=4458,hi:=4459);
Read_Real(rVar:=PMM[1].VirA_fsys,lo:=4460,hi:=4461);
Read_Real(rVar:=PMM[1].VirA_Isys,lo:=4462,hi:=4463);
Read_Real(rVar:=PMM[1].VirA_PFsys,lo:=4464,hi:=4465);
Read_Real(rVar:=PMM[1].VirA_Psys,lo:=4466,hi:=4467);
Read_Real(rVar:=PMM[1].VirA_Qsys,lo:=4468,hi:=4469);
Read_Real(rVar:=PMM[1].VirA_Ssys,lo:=4470,hi:=4471);
Read_Real(rVar:=PMM[1].VirA_Usys,lo:=4472,hi:=4473);
Read_Real(rVar:=PMM[1].VirB_fsys,lo:=4474,hi:=4475);
Read_Real(rVar:=PMM[1].VirB_Isys,lo:=4476,hi:=4477);
Read_Real(rVar:=PMM[1].VirB_PFsys,lo:=4478,hi:=4479);
Read_Real(rVar:=PMM[1].VirB_Psys,lo:=4480,hi:=4481);
Read_Real(rVar:=PMM[1].VirB_Qsys,lo:=4482,hi:=4483);
Read_Real(rVar:=PMM[1].VirB_Ssys,lo:=4484,hi:=4485);
Read_Real(rVar:=PMM[1].VirB_Usys,lo:=4486,hi:=4487);
Read_Real(rVar:=PMM[1].VirBActiveEnergyConsumed_kWh,lo:=4488,hi:=4489);
Read_Real(rVar:=PMM[1].VirBActivePowerPhaseA_kW,lo:=4490,hi:=4491);
Read_Real(rVar:=PMM[1].VirBActivePowerPhaseB_kW,lo:=4492,hi:=4493);
Read_Real(rVar:=PMM[1].VirBActivePowerPhaseC_kW,lo:=4494,hi:=4495);
Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseA,lo:=4496,hi:=4497);
Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseB,lo:=4498,hi:=4499);
Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseC,lo:=4500,hi:=4501);
Read_Real(rVar:=PMM[1].VirBAverageCurrent_A,lo:=4502,hi:=4503);
Read_Real(rVar:=PMM[1].VirBAveragePhaseToNeutral_V,lo:=4504,hi:=4505);
Read_Real(rVar:=PMM[1].VirBAveragePhaseToPhase_V,lo:=4506,hi:=4507);
Read_Real(rVar:=PMM[1].VirBCurrentInPhaseA_A,lo:=4508,hi:=4509);
Read_Real(rVar:=PMM[1].VirBCurrentInPhaseB_A,lo:=4510,hi:=4511);
Read_Real(rVar:=PMM[1].VirBCurrentInPhaseC_A,lo:=4512,hi:=4513);
Read_Real(rVar:=PMM[1].VirBFrequency_Hz,lo:=4514,hi:=4515);
Read_Real(rVar:=PMM[1].VirBPowerFactorSys,lo:=4516,hi:=4517);
Read_Real(rVar:=PMM[1].VirBReactiveEnergyConsumed_kVARh,lo:=4518,hi:=4519);
Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseA,lo:=4520,hi:=4521);
Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseB,lo:=4522,hi:=4523);
Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseC,lo:=4524,hi:=4525);
Read_Real(rVar:=PMM[1].VirBTotalActivePower_kW,lo:=4526,hi:=4527);
Read_Real(rVar:=PMM[1].VirBTotalAparentPower_kVA,lo:=4528,hi:=4529);
Read_Real(rVar:=PMM[1].VirBTotalPowerFactor,lo:=4530,hi:=4531);
Read_Real(rVar:=PMM[1].VirBTotalReactivePower_kVAR,lo:=4532,hi:=4533);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseAB_V,lo:=4534,hi:=4535);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseAN_V,lo:=4536,hi:=4537);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseBC_V,lo:=4538,hi:=4539);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseBN_V,lo:=4540,hi:=4541);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseCA_V,lo:=4542,hi:=4543);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseCN_V,lo:=4544,hi:=4545);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseAB_V,lo:=4546,hi:=4547);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseAN_V,lo:=4548,hi:=4549);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseBC_V,lo:=4550,hi:=4551);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseBN_V,lo:=4552,hi:=4553);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseCA_V,lo:=4554,hi:=4555);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseCN_V,lo:=4556,hi:=4557);
Read_Real(rVar:=PMM[2].ActiveEnergyConsumed_kWh,lo:=4558,hi:=4559);
Read_Real(rVar:=PMM[2].ActivePowerPhaseA_kW,lo:=4560,hi:=4561);
Read_Real(rVar:=PMM[2].ActivePowerPhaseB_kW,lo:=4562,hi:=4563);
Read_Real(rVar:=PMM[2].ActivePowerPhaseC_kW,lo:=4564,hi:=4565);
Read_Real(rVar:=PMM[2].AparentPowerPhaseA,lo:=4566,hi:=4567);
Read_Real(rVar:=PMM[2].AparentPowerPhaseB,lo:=4568,hi:=4569);
Read_Real(rVar:=PMM[2].AparentPowerPhaseC,lo:=4570,hi:=4571);
Read_Real(rVar:=PMM[2].AverageCurrent_A,lo:=4572,hi:=4573);
Read_Real(rVar:=PMM[2].AveragePhaseToNeutral_V,lo:=4574,hi:=4575);
Read_Real(rVar:=PMM[2].AveragePhaseToPhase_V,lo:=4576,hi:=4577);
Read_Real(rVar:=PMM[2].CurrentInPhaseA_A,lo:=4578,hi:=4579);
Read_Real(rVar:=PMM[2].CurrentInPhaseB_A,lo:=4580,hi:=4581);
Read_Real(rVar:=PMM[2].CurrentInPhaseC_A,lo:=4582,hi:=4583);
Read_Real(rVar:=PMM[2].Frequency_Hz,lo:=4584,hi:=4585);
Read_Real(rVar:=PMM[2].Phase[1].Current[1],lo:=4586,hi:=4587);
Read_Real(rVar:=PMM[2].Phase[1].Current[2],lo:=4588,hi:=4589);
Read_Real(rVar:=PMM[2].Phase[1].Current[3],lo:=4590,hi:=4591);
Read_Real(rVar:=PMM[2].Phase[1].Current[4],lo:=4592,hi:=4593);
Read_Real(rVar:=PMM[2].Phase[1].Current[5],lo:=4594,hi:=4595);
Read_Real(rVar:=PMM[2].Phase[1].Current[6],lo:=4596,hi:=4597);
Read_Real(rVar:=PMM[2].Phase[1].Current[7],lo:=4598,hi:=4599);
Read_Real(rVar:=PMM[2].Phase[1].Current[8],lo:=4600,hi:=4601);
Read_Real(rVar:=PMM[2].Phase[1].Current[9],lo:=4602,hi:=4603);
Read_Real(rVar:=PMM[2].Phase[1].Current[10],lo:=4604,hi:=4605);
Read_Real(rVar:=PMM[2].Phase[1].Current[11],lo:=4606,hi:=4607);
Read_Real(rVar:=PMM[2].Phase[1].Current[12],lo:=4608,hi:=4609);
Read_Real(rVar:=PMM[2].Phase[1].Current[13],lo:=4610,hi:=4611);
Read_Real(rVar:=PMM[2].Phase[1].Current[14],lo:=4612,hi:=4613);
Read_Real(rVar:=PMM[2].Phase[1].Current[15],lo:=4614,hi:=4615);
Read_Real(rVar:=PMM[2].Phase[1].Current[16],lo:=4616,hi:=4617);
Read_Real(rVar:=PMM[2].Phase[1].Current[17],lo:=4618,hi:=4619);
Read_Real(rVar:=PMM[2].Phase[1].Current[18],lo:=4620,hi:=4621);
Read_Real(rVar:=PMM[2].Phase[1].Current[19],lo:=4622,hi:=4623);
Read_Real(rVar:=PMM[2].Phase[1].Current[20],lo:=4624,hi:=4625);
Read_Real(rVar:=PMM[2].Phase[1].Current[21],lo:=4626,hi:=4627);
Read_Real(rVar:=PMM[2].Phase[1].Current[22],lo:=4628,hi:=4629);
Read_Real(rVar:=PMM[2].Phase[1].Current[23],lo:=4630,hi:=4631);
Read_Real(rVar:=PMM[2].Phase[1].Current[24],lo:=4632,hi:=4633);
Read_Real(rVar:=PMM[2].Phase[1].Current[25],lo:=4634,hi:=4635);
Read_Real(rVar:=PMM[2].Phase[1].Current[26],lo:=4636,hi:=4637);
Read_Real(rVar:=PMM[2].Phase[1].Current[27],lo:=4638,hi:=4639);
Read_Real(rVar:=PMM[2].Phase[1].Current[28],lo:=4640,hi:=4641);
Read_Real(rVar:=PMM[2].Phase[1].Current[29],lo:=4642,hi:=4643);
Read_Real(rVar:=PMM[2].Phase[1].Current[30],lo:=4644,hi:=4645);
Read_Real(rVar:=PMM[2].Phase[1].Current[31],lo:=4646,hi:=4647);
Read_Real(rVar:=PMM[2].Phase[1].Current[32],lo:=4648,hi:=4649);
Read_Real(rVar:=PMM[2].Phase[1].Current[33],lo:=4650,hi:=4651);
Read_Real(rVar:=PMM[2].Phase[1].Current[34],lo:=4652,hi:=4653);
Read_Real(rVar:=PMM[2].Phase[1].Current[35],lo:=4654,hi:=4655);
Read_Real(rVar:=PMM[2].Phase[1].Current[36],lo:=4656,hi:=4657);
Read_Real(rVar:=PMM[2].Phase[1].Current[37],lo:=4658,hi:=4659);
Read_Real(rVar:=PMM[2].Phase[1].Current[38],lo:=4660,hi:=4661);
Read_Real(rVar:=PMM[2].Phase[1].Current[39],lo:=4662,hi:=4663);
Read_Real(rVar:=PMM[2].Phase[1].Current[40],lo:=4664,hi:=4665);
Read_Real(rVar:=PMM[2].Phase[1].Current[41],lo:=4666,hi:=4667);
Read_Real(rVar:=PMM[2].Phase[1].Current[42],lo:=4668,hi:=4669);
Read_Real(rVar:=PMM[2].Phase[2].Current[10],lo:=4670,hi:=4671);
Read_Real(rVar:=PMM[2].Phase[2].Current[11],lo:=4672,hi:=4673);
Read_Real(rVar:=PMM[2].Phase[2].Current[12],lo:=4674,hi:=4675);
Read_Real(rVar:=PMM[2].Phase[2].Current[13],lo:=4676,hi:=4677);
Read_Real(rVar:=PMM[2].Phase[2].Current[14],lo:=4678,hi:=4679);
Read_Real(rVar:=PMM[2].Phase[2].Current[15],lo:=4680,hi:=4681);
Read_Real(rVar:=PMM[2].Phase[2].Current[16],lo:=4682,hi:=4683);
Read_Real(rVar:=PMM[2].Phase[2].Current[17],lo:=4684,hi:=4685);
Read_Real(rVar:=PMM[2].Phase[2].Current[18],lo:=4686,hi:=4687);
Read_Real(rVar:=PMM[2].Phase[2].Current[19],lo:=4688,hi:=4689);
Read_Real(rVar:=PMM[2].Phase[2].Current[1],lo:=4690,hi:=4691);
Read_Real(rVar:=PMM[2].Phase[2].Current[20],lo:=4692,hi:=4693);
Read_Real(rVar:=PMM[2].Phase[2].Current[21],lo:=4694,hi:=4695);
Read_Real(rVar:=PMM[2].Phase[2].Current[22],lo:=4696,hi:=4697);
Read_Real(rVar:=PMM[2].Phase[2].Current[23],lo:=4698,hi:=4699);
Read_Real(rVar:=PMM[2].Phase[2].Current[24],lo:=4700,hi:=4701);
Read_Real(rVar:=PMM[2].Phase[2].Current[25],lo:=4702,hi:=4703);
Read_Real(rVar:=PMM[2].Phase[2].Current[26],lo:=4704,hi:=4705);
Read_Real(rVar:=PMM[2].Phase[2].Current[27],lo:=4706,hi:=4707);
Read_Real(rVar:=PMM[2].Phase[2].Current[28],lo:=4708,hi:=4709);
Read_Real(rVar:=PMM[2].Phase[2].Current[29],lo:=4710,hi:=4711);
Read_Real(rVar:=PMM[2].Phase[2].Current[2],lo:=4712,hi:=4713);
Read_Real(rVar:=PMM[2].Phase[2].Current[30],lo:=4714,hi:=4715);
Read_Real(rVar:=PMM[2].Phase[2].Current[31],lo:=4716,hi:=4717);
Read_Real(rVar:=PMM[2].Phase[2].Current[32],lo:=4718,hi:=4719);
Read_Real(rVar:=PMM[2].Phase[2].Current[33],lo:=4720,hi:=4721);
Read_Real(rVar:=PMM[2].Phase[2].Current[34],lo:=4722,hi:=4723);
Read_Real(rVar:=PMM[2].Phase[2].Current[35],lo:=4724,hi:=4725);
Read_Real(rVar:=PMM[2].Phase[2].Current[36],lo:=4726,hi:=4727);
Read_Real(rVar:=PMM[2].Phase[2].Current[37],lo:=4728,hi:=4729);
Read_Real(rVar:=PMM[2].Phase[2].Current[38],lo:=4730,hi:=4731);
Read_Real(rVar:=PMM[2].Phase[2].Current[39],lo:=4732,hi:=4733);
Read_Real(rVar:=PMM[2].Phase[2].Current[3],lo:=4734,hi:=4735);
Read_Real(rVar:=PMM[2].Phase[2].Current[40],lo:=4736,hi:=4737);
Read_Real(rVar:=PMM[2].Phase[2].Current[41],lo:=4738,hi:=4739);
Read_Real(rVar:=PMM[2].Phase[2].Current[42],lo:=4740,hi:=4741);
Read_Real(rVar:=PMM[2].Phase[2].Current[4],lo:=4742,hi:=4743);
Read_Real(rVar:=PMM[2].Phase[2].Current[5],lo:=4744,hi:=4745);
Read_Real(rVar:=PMM[2].Phase[2].Current[6],lo:=4746,hi:=4747);
Read_Real(rVar:=PMM[2].Phase[2].Current[7],lo:=4748,hi:=4749);
Read_Real(rVar:=PMM[2].Phase[2].Current[8],lo:=4750,hi:=4751);
Read_Real(rVar:=PMM[2].Phase[2].Current[9],lo:=4752,hi:=4753);
Read_Real(rVar:=PMM[2].Phase[3].Current[10],lo:=4754,hi:=4755);
Read_Real(rVar:=PMM[2].Phase[3].Current[11],lo:=4756,hi:=4757);
Read_Real(rVar:=PMM[2].Phase[3].Current[12],lo:=4758,hi:=4759);
Read_Real(rVar:=PMM[2].Phase[3].Current[13],lo:=4760,hi:=4761);
Read_Real(rVar:=PMM[2].Phase[3].Current[14],lo:=4762,hi:=4763);
Read_Real(rVar:=PMM[2].Phase[3].Current[15],lo:=4764,hi:=4765);
Read_Real(rVar:=PMM[2].Phase[3].Current[16],lo:=4766,hi:=4767);
Read_Real(rVar:=PMM[2].Phase[3].Current[17],lo:=4768,hi:=4769);
Read_Real(rVar:=PMM[2].Phase[3].Current[18],lo:=4770,hi:=4771);
Read_Real(rVar:=PMM[2].Phase[3].Current[19],lo:=4772,hi:=4773);
Read_Real(rVar:=PMM[2].Phase[3].Current[1],lo:=4774,hi:=4775);
Read_Real(rVar:=PMM[2].Phase[3].Current[20],lo:=4776,hi:=4777);
Read_Real(rVar:=PMM[2].Phase[3].Current[21],lo:=4778,hi:=4779);
Read_Real(rVar:=PMM[2].Phase[3].Current[22],lo:=4780,hi:=4781);
Read_Real(rVar:=PMM[2].Phase[3].Current[23],lo:=4782,hi:=4783);
Read_Real(rVar:=PMM[2].Phase[3].Current[24],lo:=4784,hi:=4785);
Read_Real(rVar:=PMM[2].Phase[3].Current[25],lo:=4786,hi:=4787);
Read_Real(rVar:=PMM[2].Phase[3].Current[26],lo:=4788,hi:=4789);
Read_Real(rVar:=PMM[2].Phase[3].Current[27],lo:=4790,hi:=4791);
Read_Real(rVar:=PMM[2].Phase[3].Current[28],lo:=4792,hi:=4793);
Read_Real(rVar:=PMM[2].Phase[3].Current[29],lo:=4794,hi:=4795);
Read_Real(rVar:=PMM[2].Phase[3].Current[2],lo:=4796,hi:=4797);
Read_Real(rVar:=PMM[2].Phase[3].Current[30],lo:=4798,hi:=4799);
Read_Real(rVar:=PMM[2].Phase[3].Current[31],lo:=4800,hi:=4801);
Read_Real(rVar:=PMM[2].Phase[3].Current[32],lo:=4802,hi:=4803);
Read_Real(rVar:=PMM[2].Phase[3].Current[33],lo:=4804,hi:=4805);
Read_Real(rVar:=PMM[2].Phase[3].Current[34],lo:=4806,hi:=4807);
Read_Real(rVar:=PMM[2].Phase[3].Current[35],lo:=4808,hi:=4809);
Read_Real(rVar:=PMM[2].Phase[3].Current[36],lo:=4810,hi:=4811);
Read_Real(rVar:=PMM[2].Phase[3].Current[37],lo:=4812,hi:=4813);
Read_Real(rVar:=PMM[2].Phase[3].Current[38],lo:=4814,hi:=4815);
Read_Real(rVar:=PMM[2].Phase[3].Current[39],lo:=4816,hi:=4817);
Read_Real(rVar:=PMM[2].Phase[3].Current[3],lo:=4818,hi:=4819);
Read_Real(rVar:=PMM[2].Phase[3].Current[40],lo:=4820,hi:=4821);
Read_Real(rVar:=PMM[2].Phase[3].Current[41],lo:=4822,hi:=4823);
Read_Real(rVar:=PMM[2].Phase[3].Current[42],lo:=4824,hi:=4825);
Read_Real(rVar:=PMM[2].Phase[3].Current[4],lo:=4826,hi:=4827);
Read_Real(rVar:=PMM[2].Phase[3].Current[5],lo:=4828,hi:=4829);
Read_Real(rVar:=PMM[2].Phase[3].Current[6],lo:=4830,hi:=4831);
Read_Real(rVar:=PMM[2].Phase[3].Current[7],lo:=4832,hi:=4833);
Read_Real(rVar:=PMM[2].Phase[3].Current[8],lo:=4834,hi:=4835);
Read_Real(rVar:=PMM[2].Phase[3].Current[9],lo:=4836,hi:=4837);
Read_Real(rVar:=PMM[2].PowerFactorSys,lo:=4838,hi:=4839);
Read_Real(rVar:=PMM[2].ReactiveEnergyConsumed_kVARh,lo:=4840,hi:=4841);
Read_Real(rVar:=PMM[2].ReactivePowerPhaseA,lo:=4842,hi:=4843);
Read_Real(rVar:=PMM[2].ReactivePowerPhaseB,lo:=4844,hi:=4845);
Read_Real(rVar:=PMM[2].ReactivePowerPhaseC,lo:=4846,hi:=4847);
Read_Real(rVar:=PMM[2].TotalActivePower_kW,lo:=4848,hi:=4849);
Read_Real(rVar:=PMM[2].TotalAparentPower_kVA,lo:=4850,hi:=4851);
Read_Real(rVar:=PMM[2].TotalPowerFactor,lo:=4852,hi:=4853);
Read_Real(rVar:=PMM[2].TotalReactivePower_kVAR,lo:=4854,hi:=4855);
Read_Real(rVar:=PMM[2].VirA_fsys,lo:=4856,hi:=4857);
Read_Real(rVar:=PMM[2].VirA_Isys,lo:=4858,hi:=4859);
Read_Real(rVar:=PMM[2].VirA_PFsys,lo:=4860,hi:=4861);
Read_Real(rVar:=PMM[2].VirA_Psys,lo:=4862,hi:=4863);
Read_Real(rVar:=PMM[2].VirA_Qsys,lo:=4864,hi:=4865);
Read_Real(rVar:=PMM[2].VirA_Ssys,lo:=4866,hi:=4867);
Read_Real(rVar:=PMM[2].VirA_Usys,lo:=4868,hi:=4869);
Read_Real(rVar:=PMM[2].VirB_fsys,lo:=4870,hi:=4871);
Read_Real(rVar:=PMM[2].VirB_Isys,lo:=4872,hi:=4873);
Read_Real(rVar:=PMM[2].VirB_PFsys,lo:=4874,hi:=4875);
Read_Real(rVar:=PMM[2].VirB_Psys,lo:=4876,hi:=4877);
Read_Real(rVar:=PMM[2].VirB_Qsys,lo:=4878,hi:=4879);
Read_Real(rVar:=PMM[2].VirB_Ssys,lo:=4880,hi:=4881);
Read_Real(rVar:=PMM[2].VirB_Usys,lo:=4882,hi:=4883);
Read_Real(rVar:=PMM[2].VirBActiveEnergyConsumed_kWh,lo:=4884,hi:=4885);
Read_Real(rVar:=PMM[2].VirBActivePowerPhaseA_kW,lo:=4886,hi:=4887);
Read_Real(rVar:=PMM[2].VirBActivePowerPhaseB_kW,lo:=4888,hi:=4889);
Read_Real(rVar:=PMM[2].VirBActivePowerPhaseC_kW,lo:=4890,hi:=4891);
Read_Real(rVar:=PMM[2].VirBAparentPowerPhaseA,lo:=4892,hi:=4893);
Read_Real(rVar:=PMM[2].VirBAparentPowerPhaseB,lo:=4894,hi:=4895);
Read_Real(rVar:=PMM[2].VirBAparentPowerPhaseC,lo:=4896,hi:=4897);
Read_Real(rVar:=PMM[2].VirBAverageCurrent_A,lo:=4898,hi:=4899);
Read_Real(rVar:=PMM[2].VirBAveragePhaseToNeutral_V,lo:=4900,hi:=4901);
Read_Real(rVar:=PMM[2].VirBAveragePhaseToPhase_V,lo:=4902,hi:=4903);
Read_Real(rVar:=PMM[2].VirBCurrentInPhaseA_A,lo:=4904,hi:=4905);
Read_Real(rVar:=PMM[2].VirBCurrentInPhaseB_A,lo:=4906,hi:=4907);
Read_Real(rVar:=PMM[2].VirBCurrentInPhaseC_A,lo:=4908,hi:=4909);
Read_Real(rVar:=PMM[2].VirBFrequency_Hz,lo:=4910,hi:=4911);
Read_Real(rVar:=PMM[2].VirBPowerFactorSys,lo:=4912,hi:=4913);
Read_Real(rVar:=PMM[2].VirBReactiveEnergyConsumed_kVARh,lo:=4914,hi:=4915);
Read_Real(rVar:=PMM[2].VirBReactivePowerPhaseA,lo:=4916,hi:=4917);
Read_Real(rVar:=PMM[2].VirBReactivePowerPhaseB,lo:=4918,hi:=4919);
Read_Real(rVar:=PMM[2].VirBReactivePowerPhaseC,lo:=4920,hi:=4921);
Read_Real(rVar:=PMM[2].VirBTotalActivePower_kW,lo:=4922,hi:=4923);
Read_Real(rVar:=PMM[2].VirBTotalAparentPower_kVA,lo:=4924,hi:=4925);
Read_Real(rVar:=PMM[2].VirBTotalPowerFactor,lo:=4926,hi:=4927);
Read_Real(rVar:=PMM[2].VirBTotalReactivePower_kVAR,lo:=4928,hi:=4929);
Read_Real(rVar:=PMM[2].VirBVoltageBetweenPhaseAB_V,lo:=4930,hi:=4931);
Read_Real(rVar:=PMM[2].VirBVoltageBetweenPhaseAN_V,lo:=4932,hi:=4933);
Read_Real(rVar:=PMM[2].VirBVoltageBetweenPhaseBC_V,lo:=4934,hi:=4935);
Read_Real(rVar:=PMM[2].VirBVoltageBetweenPhaseBN_V,lo:=4936,hi:=4937);
Read_Real(rVar:=PMM[2].VirBVoltageBetweenPhaseCA_V,lo:=4938,hi:=4939);
Read_Real(rVar:=PMM[2].VirBVoltageBetweenPhaseCN_V,lo:=4940,hi:=4941);
Read_Real(rVar:=PMM[2].VoltageBetweenPhaseAB_V,lo:=4942,hi:=4943);
Read_Real(rVar:=PMM[2].VoltageBetweenPhaseAN_V,lo:=4944,hi:=4945);
Read_Real(rVar:=PMM[2].VoltageBetweenPhaseBC_V,lo:=4946,hi:=4947);
Read_Real(rVar:=PMM[2].VoltageBetweenPhaseBN_V,lo:=4948,hi:=4949);
Read_Real(rVar:=PMM[2].VoltageBetweenPhaseCA_V,lo:=4950,hi:=4951);
Read_Real(rVar:=PMM[2].VoltageBetweenPhaseCN_V,lo:=4952,hi:=4953);
Read_Real(rVar:=PMMPanel.ActiveEnergyConsumed_kWh,lo:=4954,hi:=4955);
Read_Real(rVar:=PMMPanel.ActivePowerPhaseA_kW,lo:=4956,hi:=4957);
Read_Real(rVar:=PMMPanel.ActivePowerPhaseB_kW,lo:=4958,hi:=4959);
Read_Real(rVar:=PMMPanel.ActivePowerPhaseC_kW,lo:=4960,hi:=4961);
Read_Real(rVar:=PMMPanel.AparentPowerPhaseA,lo:=4962,hi:=4963);
Read_Real(rVar:=PMMPanel.AparentPowerPhaseB,lo:=4964,hi:=4965);
Read_Real(rVar:=PMMPanel.AparentPowerPhaseC,lo:=4966,hi:=4967);
Read_Real(rVar:=PMMPanel.AverageCurrent_A,lo:=4968,hi:=4969);
Read_Real(rVar:=PMMPanel.AveragePhaseToNeutral_V,lo:=4970,hi:=4971);
Read_Real(rVar:=PMMPanel.AveragePhaseToPhase_V,lo:=4972,hi:=4973);
Read_Real(rVar:=PMMPanel.CurrentInPhaseA_A,lo:=4974,hi:=4975);
Read_Real(rVar:=PMMPanel.CurrentInPhaseB_A,lo:=4976,hi:=4977);
Read_Real(rVar:=PMMPanel.CurrentInPhaseC_A,lo:=4978,hi:=4979);
Read_Real(rVar:=PMMPanel.Frequency_Hz,lo:=4980,hi:=4981);
Read_Real(rVar:=PMMPanel.PowerFactorSys,lo:=4982,hi:=4983);
Read_Real(rVar:=PMMPanel.ReactiveEnergyConsumed_kVARh,lo:=4984,hi:=4985);
Read_Real(rVar:=PMMPanel.ReactivePowerPhaseA,lo:=4986,hi:=4987);
Read_Real(rVar:=PMMPanel.ReactivePowerPhaseB,lo:=4988,hi:=4989);
Read_Real(rVar:=PMMPanel.ReactivePowerPhaseC,lo:=4990,hi:=4991);
Read_Real(rVar:=PMMPanel.TotalActivePower_kW,lo:=4992,hi:=4993);
Read_Real(rVar:=PMMPanel.TotalAparentPower_kVA,lo:=4994,hi:=4995);
Read_Real(rVar:=PMMPanel.TotalPowerFactor,lo:=4996,hi:=4997);
Read_Real(rVar:=PMMPanel.TotalReactivePower_kVAR,lo:=4998,hi:=4999);
Read_Real(rVar:=PMMPanel.VirA_fsys,lo:=5000,hi:=5001);
Read_Real(rVar:=PMMPanel.VirA_Isys,lo:=5002,hi:=5003);
Read_Real(rVar:=PMMPanel.VirA_PFsys,lo:=5004,hi:=5005);
Read_Real(rVar:=PMMPanel.VirA_Psys,lo:=5006,hi:=5007);
Read_Real(rVar:=PMMPanel.VirA_Qsys,lo:=5008,hi:=5009);
Read_Real(rVar:=PMMPanel.VirA_Ssys,lo:=5010,hi:=5011);
Read_Real(rVar:=PMMPanel.VirA_Usys,lo:=5012,hi:=5013);
Read_Real(rVar:=PMMPanel.VirB_fsys,lo:=5014,hi:=5015);
Read_Real(rVar:=PMMPanel.VirB_Isys,lo:=5016,hi:=5017);
Read_Real(rVar:=PMMPanel.VirB_PFsys,lo:=5018,hi:=5019);
Read_Real(rVar:=PMMPanel.VirB_Psys,lo:=5020,hi:=5021);
Read_Real(rVar:=PMMPanel.VirB_Qsys,lo:=5022,hi:=5023);
Read_Real(rVar:=PMMPanel.VirB_Ssys,lo:=5024,hi:=5025);
Read_Real(rVar:=PMMPanel.VirB_Usys,lo:=5026,hi:=5027);
Read_Real(rVar:=PMMPanel.VirBActiveEnergyConsumed_kWh,lo:=5028,hi:=5029);
Read_Real(rVar:=PMMPanel.VirBActivePowerPhaseA_kW,lo:=5030,hi:=5031);
Read_Real(rVar:=PMMPanel.VirBActivePowerPhaseB_kW,lo:=5032,hi:=5033);
Read_Real(rVar:=PMMPanel.VirBActivePowerPhaseC_kW,lo:=5034,hi:=5035);
Read_Real(rVar:=PMMPanel.VirBAparentPowerPhaseA,lo:=5036,hi:=5037);
Read_Real(rVar:=PMMPanel.VirBAparentPowerPhaseB,lo:=5038,hi:=5039);
Read_Real(rVar:=PMMPanel.VirBAparentPowerPhaseC,lo:=5040,hi:=5041);
Read_Real(rVar:=PMMPanel.VirBAverageCurrent_A,lo:=5042,hi:=5043);
Read_Real(rVar:=PMMPanel.VirBAveragePhaseToNeutral_V,lo:=5044,hi:=5045);
Read_Real(rVar:=PMMPanel.VirBAveragePhaseToPhase_V,lo:=5046,hi:=5047);
Read_Real(rVar:=PMMPanel.VirBCurrentInPhaseA_A,lo:=5048,hi:=5049);
Read_Real(rVar:=PMMPanel.VirBCurrentInPhaseB_A,lo:=5050,hi:=5051);
Read_Real(rVar:=PMMPanel.VirBCurrentInPhaseC_A,lo:=5052,hi:=5053);
Read_Real(rVar:=PMMPanel.VirBFrequency_Hz,lo:=5054,hi:=5055);
Read_Real(rVar:=PMMPanel.VirBPowerFactorSys,lo:=5056,hi:=5057);
Read_Real(rVar:=PMMPanel.VirBReactiveEnergyConsumed_kVARh,lo:=5058,hi:=5059);
Read_Real(rVar:=PMMPanel.VirBReactivePowerPhaseA,lo:=5060,hi:=5061);
Read_Real(rVar:=PMMPanel.VirBReactivePowerPhaseB,lo:=5062,hi:=5063);
Read_Real(rVar:=PMMPanel.VirBReactivePowerPhaseC,lo:=5064,hi:=5065);
Read_Real(rVar:=PMMPanel.VirBTotalActivePower_kW,lo:=5066,hi:=5067);
Read_Real(rVar:=PMMPanel.VirBTotalAparentPower_kVA,lo:=5068,hi:=5069);
Read_Real(rVar:=PMMPanel.VirBTotalPowerFactor,lo:=5070,hi:=5071);
Read_Real(rVar:=PMMPanel.VirBTotalReactivePower_kVAR,lo:=5072,hi:=5073);
Read_Real(rVar:=PMMPanel.VirBVoltageBetweenPhaseAB_V,lo:=5074,hi:=5075);
Read_Real(rVar:=PMMPanel.VirBVoltageBetweenPhaseAN_V,lo:=5076,hi:=5077);
Read_Real(rVar:=PMMPanel.VirBVoltageBetweenPhaseBC_V,lo:=5078,hi:=5079);
Read_Real(rVar:=PMMPanel.VirBVoltageBetweenPhaseBN_V,lo:=5080,hi:=5081);
Read_Real(rVar:=PMMPanel.VirBVoltageBetweenPhaseCA_V,lo:=5082,hi:=5083);
Read_Real(rVar:=PMMPanel.VirBVoltageBetweenPhaseCN_V,lo:=5084,hi:=5085);
Read_Real(rVar:=PMMPanel.VoltageBetweenPhaseAB_V,lo:=5086,hi:=5087);
Read_Real(rVar:=PMMPanel.VoltageBetweenPhaseAN_V,lo:=5088,hi:=5089);
Read_Real(rVar:=PMMPanel.VoltageBetweenPhaseBC_V,lo:=5090,hi:=5091);
Read_Real(rVar:=PMMPanel.VoltageBetweenPhaseBN_V,lo:=5092,hi:=5093);
Read_Real(rVar:=PMMPanel.VoltageBetweenPhaseCA_V,lo:=5094,hi:=5095);
Read_Real(rVar:=PMMPanel.VoltageBetweenPhaseCN_V,lo:=5096,hi:=5097);
Read_Real(rVar:=SKTemp1,lo:=5098,hi:=5099);
Read_Real(rVar:=SKTemp2,lo:=5100,hi:=5101);
Read_Real(rVar:=SKTemp3,lo:=5102,hi:=5103);
Read_Real(rVar:=SKTemp4,lo:=5104,hi:=5105);
Read_Real(rVar:=SKVlaga1,lo:=5106,hi:=5107);
Read_Real(rVar:=SKVlaga2,lo:=5108,hi:=5109);
Read_Real(rVar:=SKVlaga3,lo:=5110,hi:=5111);
Read_Real(rVar:=SKVlaga4,lo:=5112,hi:=5113);
Read_Real(rVar:=TempZaAlarm1_2,lo:=5114,hi:=5115);
Read_Real(rVar:=TempZaAlarm3_4,lo:=5116,hi:=5117);
Read_Real(rVar:=TempZaAlarm5_6,lo:=5118,hi:=5119);
Read_Real(rVar:=TempZaAlarmTIA1,lo:=5120,hi:=5121);
Read_Real(rVar:=TempZaAlarmTIA2,lo:=5122,hi:=5123);
Read_Real(rVar:=TempZaAlarmTIA3,lo:=5124,hi:=5125);
Read_Real(rVar:=TempZaAlarmTIA4,lo:=5126,hi:=5127);
Read_Real(rVar:=TempZaVklopObehKlim1_2,lo:=5128,hi:=5129);
Read_Real(rVar:=TempZaVklopObehKlim3_4,lo:=5130,hi:=5131);
Read_Real(rVar:=TempZaVklopObehKlim3_4TIA3,lo:=5132,hi:=5133);
Read_Real(rVar:=TempZaVklopObehKlim5_6,lo:=5134,hi:=5135);
Read_Real(rVar:=TempZaVklopObehKlim5_6TIA3,lo:=5136,hi:=5137);
Read_Real(rVar:=SKTemp5,lo:=5138,hi:=5139);
Read_Real(rVar:=SKTemp6,lo:=5140,hi:=5141);
Read_Real(rVar:=SKVlaga5,lo:=5142,hi:=5143);
Read_Real(rVar:=SKVlaga6,lo:=5144,hi:=5145);
Read_Real(rVar:=TempZaAlarmTIA5,lo:=5146,hi:=5147);
Read_Real(rVar:=TempZaAlarmTIA6,lo:=5148,hi:=5149);
Read_Real(rVar:=SKTempServSoba1Povpr,lo:=5150,hi:=5151);
Read_Real(rVar:=SKTempServSoba2Povpr,lo:=5152,hi:=5153);
Read_Real(rVar:=TempZaAlarmTIA235,lo:=5154,hi:=5155);
Read_Real(rVar:=TempZaAlarmTIA46,lo:=5156,hi:=5157);
(*Branje STRING*)
(**)
Read_String(sVar:=Date_Time[0],start:=6000);
Read_String(sVar:=Date_Time[1],start:=6015);
Read_String(sVar:=Date_Time[2],start:=6030);
Read_String(sVar:=Date_Time[3],start:=6045);
Read_String(sVar:=UserName,start:=6060);
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Bool : BOOL
VAR_INPUT
index: INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje BOOL*)
(**)
0:AlarmKlimat2_1_Napaka:=Bit_0;
1:AlarmKlimat2_2_Napaka:=Bit_0;
2:AlarmKlimat2_3_Napaka:=Bit_0;
3:AlarmKlimat2_4_Napaka:=Bit_0;
4:AlarmKlimat2_5_Napaka:=Bit_0;
5:AlarmKlimat2_6_Napaka:=Bit_0;
6:AlarmLAH1RazlitjeVode:=Bit_0;
7:AlarmLAH2RazlitjeVode:=Bit_0;
8:AlarmLAH3RazlitjeVode:=Bit_0;
9:AlarmPMM2x17nad80[10]:=Bit_0;
10:AlarmPMM2x17nad80[11]:=Bit_0;
11:AlarmPMM2x17nad80[12]:=Bit_0;
12:AlarmPMM2x17nad80[13]:=Bit_0;
13:AlarmPMM2x17nad80[14]:=Bit_0;
14:AlarmPMM2x17nad80[15]:=Bit_0;
15:AlarmPMM2x17nad80[16]:=Bit_0;
16:AlarmPMM2x17nad80[17]:=Bit_0;
17:AlarmPMM2x17nad80[18]:=Bit_0;
18:AlarmPMM2x17nad80[19]:=Bit_0;
19:AlarmPMM2x17nad80[1]:=Bit_0;
20:AlarmPMM2x17nad80[20]:=Bit_0;
21:AlarmPMM2x17nad80[21]:=Bit_0;
22:AlarmPMM2x17nad80[22]:=Bit_0;
23:AlarmPMM2x17nad80[23]:=Bit_0;
24:AlarmPMM2x17nad80[24]:=Bit_0;
25:AlarmPMM2x17nad80[25]:=Bit_0;
26:AlarmPMM2x17nad80[26]:=Bit_0;
27:AlarmPMM2x17nad80[27]:=Bit_0;
28:AlarmPMM2x17nad80[28]:=Bit_0;
29:AlarmPMM2x17nad80[29]:=Bit_0;
30:AlarmPMM2x17nad80[2]:=Bit_0;
31:AlarmPMM2x17nad80[30]:=Bit_0;
32:AlarmPMM2x17nad80[31]:=Bit_0;
33:AlarmPMM2x17nad80[32]:=Bit_0;
34:AlarmPMM2x17nad80[33]:=Bit_0;
35:AlarmPMM2x17nad80[34]:=Bit_0;
36:AlarmPMM2x17nad80[35]:=Bit_0;
37:AlarmPMM2x17nad80[36]:=Bit_0;
38:AlarmPMM2x17nad80[37]:=Bit_0;
39:AlarmPMM2x17nad80[38]:=Bit_0;
40:AlarmPMM2x17nad80[39]:=Bit_0;
41:AlarmPMM2x17nad80[3]:=Bit_0;
42:AlarmPMM2x17nad80[40]:=Bit_0;
43:AlarmPMM2x17nad80[41]:=Bit_0;
44:AlarmPMM2x17nad80[42]:=Bit_0;
45:AlarmPMM2x17nad80[4]:=Bit_0;
46:AlarmPMM2x17nad80[5]:=Bit_0;
47:AlarmPMM2x17nad80[6]:=Bit_0;
48:AlarmPMM2x17nad80[7]:=Bit_0;
49:AlarmPMM2x17nad80[8]:=Bit_0;
50:AlarmPMM2x17nad80[9]:=Bit_0;
51:AlarmSinhronizacijaNOK:=Bit_0;
52:AlarmSKTemp1_Previsoka:=Bit_0;
53:AlarmSKTemp2_Previsoka:=Bit_0;
54:AlarmSKTemp3_Previsoka:=Bit_0;
55:AlarmSKTemp4_Previsoka:=Bit_0;
56:AlarmTempTIA1Previsoka:=Bit_0;
57:AlarmTempTIA2Previsoka:=Bit_0;
58:AlarmTempTIA3Previsoka:=Bit_0;
59:AlarmTempTIA4Previsoka:=Bit_0;
60:AlarmUPSKrmOmara_Alarm:=Bit_0;
61:ComSCADA:=Bit_0;
62:ComSCADA1:=Bit_0;
63:ErrComKlima[1]:=Bit_0;
64:ErrComKlima[2]:=Bit_0;
65:ErrComKlima[3]:=Bit_0;
66:ErrComKlima[4]:=Bit_0;
67:ErrComKlima[5]:=Bit_0;
68:ErrComKlima[6]:=Bit_0;
69:ErrCommScada:=Bit_0;
70:ErrComPanelPLC:=Bit_0;
71:ErrComPMM[1]:=Bit_0;
72:ErrComPMM[2]:=Bit_0;
73:ErrComPort2:=Bit_0;
74:ErrorComKlima[1].Error:=Bit_0;
75:ErrorComKlima[2].Error:=Bit_0;
76:ErrorComKlima[3].Error:=Bit_0;
77:ErrorComKlima[4].Error:=Bit_0;
78:ErrorComKlima[5].Error:=Bit_0;
79:ErrorComKlima[6].Error:=Bit_0;
80:ErrorComPMM[1].Error:=Bit_0;
81:ErrorComPMM[2].Error:=Bit_0;
82:Klima2_1_Onemogocena:=Bit_0;
83:Klima2_2_Onemogocena:=Bit_0;
84:Klima2_3_Onemogocena:=Bit_0;
85:Klima2_4_Onemogocena:=Bit_0;
86:Klima2_5_Onemogocena:=Bit_0;
87:Klima2_6_Onemogocena:=Bit_0;
88:Klima[1].IzhodniVentilator:=Bit_0;
89:Klima[1].Kompresor1:=Bit_0;
90:Klima[1].Kompresor2:=Bit_0;
91:Klima[1].Razvlazevanje:=Bit_0;
92:Klima[1].SenzorjiStatus:=Bit_0;
93:Klima[1].VentilGretjeOdpiranje:=Bit_0;
94:Klima[1].VentilGretjeZapiranje:=Bit_0;
95:Klima[1].Vlazenje:=Bit_0;
96:Klima[2].IzhodniVentilator:=Bit_0;
97:Klima[2].Kompresor1:=Bit_0;
98:Klima[2].Kompresor2:=Bit_0;
99:Klima[2].Razvlazevanje:=Bit_0;
100:Klima[2].SenzorjiStatus:=Bit_0;
101:Klima[2].VentilGretjeOdpiranje:=Bit_0;
102:Klima[2].VentilGretjeZapiranje:=Bit_0;
103:Klima[2].Vlazenje:=Bit_0;
104:Klima[3].IzhodniVentilator:=Bit_0;
105:Klima[3].Kompresor1:=Bit_0;
106:Klima[3].Kompresor2:=Bit_0;
107:Klima[3].Razvlazevanje:=Bit_0;
108:Klima[3].SenzorjiStatus:=Bit_0;
109:Klima[3].VentilGretjeOdpiranje:=Bit_0;
110:Klima[3].VentilGretjeZapiranje:=Bit_0;
111:Klima[3].Vlazenje:=Bit_0;
112:Klima[4].IzhodniVentilator:=Bit_0;
113:Klima[4].Kompresor1:=Bit_0;
114:Klima[4].Kompresor2:=Bit_0;
115:Klima[4].Razvlazevanje:=Bit_0;
116:Klima[4].SenzorjiStatus:=Bit_0;
117:Klima[4].VentilGretjeOdpiranje:=Bit_0;
118:Klima[4].VentilGretjeZapiranje:=Bit_0;
119:Klima[4].Vlazenje:=Bit_0;
120:Klima[5].IzhodniVentilator:=Bit_0;
121:Klima[5].Kompresor1:=Bit_0;
122:Klima[5].Kompresor2:=Bit_0;
123:Klima[5].Razvlazevanje:=Bit_0;
124:Klima[5].SenzorjiStatus:=Bit_0;
125:Klima[5].VentilGretjeOdpiranje:=Bit_0;
126:Klima[5].VentilGretjeZapiranje:=Bit_0;
127:Klima[5].Vlazenje:=Bit_0;
128:Klima[6].IzhodniVentilator:=Bit_0;
129:Klima[6].Kompresor1:=Bit_0;
130:Klima[6].Kompresor2:=Bit_0;
131:Klima[6].Razvlazevanje:=Bit_0;
132:Klima[6].SenzorjiStatus:=Bit_0;
133:Klima[6].VentilGretjeOdpiranje:=Bit_0;
134:Klima[6].VentilGretjeZapiranje:=Bit_0;
135:Klima[6].Vlazenje:=Bit_0;
136:KlimaError[1].AlarmKompresor1:=Bit_0;
137:KlimaError[1].AlarmKompresor2:=Bit_0;
138:KlimaError[1].FenThermalCutout:=Bit_0;
139:KlimaError[1].IzlivVode:=Bit_0;
140:KlimaError[1].Kompresor1naMejiStevilaObrUr:=Bit_0;
141:KlimaError[1].Kompresor2naMejiStevilaObrUr:=Bit_0;
142:KlimaError[1].NapakaPriPretokuVode:=Bit_0;
143:KlimaError[1].NapakaPriPretokuZraka:=Bit_0;
144:KlimaError[1].NapakaSenzorVlaznosti:=Bit_0;
145:KlimaError[1].NapakaTSTemperaturaProstora:=Bit_0;
146:KlimaError[1].NapakaVlazilca:=Bit_0;
147:KlimaError[1].NizekPritiskKompresor1:=Bit_0;
148:KlimaError[1].NizekPritiskKompresor2:=Bit_0;
149:KlimaError[1].NizkaTempVProstoru:=Bit_0;
150:KlimaError[1].NizkaVlaznost:=Bit_0;
151:KlimaError[1].PozarniAlarm:=Bit_0;
152:KlimaError[1].ThermalCutoutHeater1:=Bit_0;
153:KlimaError[1].ThermalCutoutHeater2:=Bit_0;
154:KlimaError[1].VentilatorNaMejiStevilaObrUr:=Bit_0;
155:KlimaError[1].VisokaTempVProstoru:=Bit_0;
156:KlimaError[1].VisokaVlaznost:=Bit_0;
157:KlimaError[1].VisokPritiskKompresor1:=Bit_0;
158:KlimaError[1].VisokPritiskKompresor2:=Bit_0;
159:KlimaError[1].ZamasenFilter:=Bit_0;
160:KlimaError[1].ZunanjiAlarm:=Bit_0;
161:KlimaError[2].AlarmKompresor1:=Bit_0;
162:KlimaError[2].AlarmKompresor2:=Bit_0;
163:KlimaError[2].FenThermalCutout:=Bit_0;
164:KlimaError[2].IzlivVode:=Bit_0;
165:KlimaError[2].Kompresor1naMejiStevilaObrUr:=Bit_0;
166:KlimaError[2].Kompresor2naMejiStevilaObrUr:=Bit_0;
167:KlimaError[2].NapakaPriPretokuVode:=Bit_0;
168:KlimaError[2].NapakaPriPretokuZraka:=Bit_0;
169:KlimaError[2].NapakaSenzorVlaznosti:=Bit_0;
170:KlimaError[2].NapakaTSTemperaturaProstora:=Bit_0;
171:KlimaError[2].NapakaVlazilca:=Bit_0;
172:KlimaError[2].NizekPritiskKompresor1:=Bit_0;
173:KlimaError[2].NizekPritiskKompresor2:=Bit_0;
174:KlimaError[2].NizkaTempVProstoru:=Bit_0;
175:KlimaError[2].NizkaVlaznost:=Bit_0;
176:KlimaError[2].PozarniAlarm:=Bit_0;
177:KlimaError[2].ThermalCutoutHeater1:=Bit_0;
178:KlimaError[2].ThermalCutoutHeater2:=Bit_0;
179:KlimaError[2].VentilatorNaMejiStevilaObrUr:=Bit_0;
180:KlimaError[2].VisokaTempVProstoru:=Bit_0;
181:KlimaError[2].VisokaVlaznost:=Bit_0;
182:KlimaError[2].VisokPritiskKompresor1:=Bit_0;
183:KlimaError[2].VisokPritiskKompresor2:=Bit_0;
184:KlimaError[2].ZamasenFilter:=Bit_0;
185:KlimaError[2].ZunanjiAlarm:=Bit_0;
186:KlimaError[3].AlarmKompresor1:=Bit_0;
187:KlimaError[3].AlarmKompresor2:=Bit_0;
188:KlimaError[3].FenThermalCutout:=Bit_0;
189:KlimaError[3].IzlivVode:=Bit_0;
190:KlimaError[3].Kompresor1naMejiStevilaObrUr:=Bit_0;
191:KlimaError[3].Kompresor2naMejiStevilaObrUr:=Bit_0;
192:KlimaError[3].NapakaPriPretokuVode:=Bit_0;
193:KlimaError[3].NapakaPriPretokuZraka:=Bit_0;
194:KlimaError[3].NapakaSenzorVlaznosti:=Bit_0;
195:KlimaError[3].NapakaTSTemperaturaProstora:=Bit_0;
196:KlimaError[3].NapakaVlazilca:=Bit_0;
197:KlimaError[3].NizekPritiskKompresor1:=Bit_0;
198:KlimaError[3].NizekPritiskKompresor2:=Bit_0;
199:KlimaError[3].NizkaTempVProstoru:=Bit_0;
200:KlimaError[3].NizkaVlaznost:=Bit_0;
201:KlimaError[3].PozarniAlarm:=Bit_0;
202:KlimaError[3].ThermalCutoutHeater1:=Bit_0;
203:KlimaError[3].ThermalCutoutHeater2:=Bit_0;
204:KlimaError[3].VentilatorNaMejiStevilaObrUr:=Bit_0;
205:KlimaError[3].VisokaTempVProstoru:=Bit_0;
206:KlimaError[3].VisokaVlaznost:=Bit_0;
207:KlimaError[3].VisokPritiskKompresor1:=Bit_0;
208:KlimaError[3].VisokPritiskKompresor2:=Bit_0;
209:KlimaError[3].ZamasenFilter:=Bit_0;
210:KlimaError[3].ZunanjiAlarm:=Bit_0;
211:KlimaError[4].AlarmKompresor1:=Bit_0;
212:KlimaError[4].AlarmKompresor2:=Bit_0;
213:KlimaError[4].FenThermalCutout:=Bit_0;
214:KlimaError[4].IzlivVode:=Bit_0;
215:KlimaError[4].Kompresor1naMejiStevilaObrUr:=Bit_0;
216:KlimaError[4].Kompresor2naMejiStevilaObrUr:=Bit_0;
217:KlimaError[4].NapakaPriPretokuVode:=Bit_0;
218:KlimaError[4].NapakaPriPretokuZraka:=Bit_0;
219:KlimaError[4].NapakaSenzorVlaznosti:=Bit_0;
220:KlimaError[4].NapakaTSTemperaturaProstora:=Bit_0;
221:KlimaError[4].NapakaVlazilca:=Bit_0;
222:KlimaError[4].NizekPritiskKompresor1:=Bit_0;
223:KlimaError[4].NizekPritiskKompresor2:=Bit_0;
224:KlimaError[4].NizkaTempVProstoru:=Bit_0;
225:KlimaError[4].NizkaVlaznost:=Bit_0;
226:KlimaError[4].PozarniAlarm:=Bit_0;
227:KlimaError[4].ThermalCutoutHeater1:=Bit_0;
228:KlimaError[4].ThermalCutoutHeater2:=Bit_0;
229:KlimaError[4].VentilatorNaMejiStevilaObrUr:=Bit_0;
230:KlimaError[4].VisokaTempVProstoru:=Bit_0;
231:KlimaError[4].VisokaVlaznost:=Bit_0;
232:KlimaError[4].VisokPritiskKompresor1:=Bit_0;
233:KlimaError[4].VisokPritiskKompresor2:=Bit_0;
234:KlimaError[4].ZamasenFilter:=Bit_0;
235:KlimaError[4].ZunanjiAlarm:=Bit_0;
236:KlimaError[5].AlarmKompresor1:=Bit_0;
237:KlimaError[5].AlarmKompresor2:=Bit_0;
238:KlimaError[5].FenThermalCutout:=Bit_0;
239:KlimaError[5].IzlivVode:=Bit_0;
240:KlimaError[5].Kompresor1naMejiStevilaObrUr:=Bit_0;
241:KlimaError[5].Kompresor2naMejiStevilaObrUr:=Bit_0;
242:KlimaError[5].NapakaPriPretokuVode:=Bit_0;
243:KlimaError[5].NapakaPriPretokuZraka:=Bit_0;
244:KlimaError[5].NapakaSenzorVlaznosti:=Bit_0;
245:KlimaError[5].NapakaTSTemperaturaProstora:=Bit_0;
246:KlimaError[5].NapakaVlazilca:=Bit_0;
247:KlimaError[5].NizekPritiskKompresor1:=Bit_0;
248:KlimaError[5].NizekPritiskKompresor2:=Bit_0;
249:KlimaError[5].NizkaTempVProstoru:=Bit_0;
250:KlimaError[5].NizkaVlaznost:=Bit_0;
251:KlimaError[5].PozarniAlarm:=Bit_0;
252:KlimaError[5].ThermalCutoutHeater1:=Bit_0;
253:KlimaError[5].ThermalCutoutHeater2:=Bit_0;
254:KlimaError[5].VentilatorNaMejiStevilaObrUr:=Bit_0;
255:KlimaError[5].VisokaTempVProstoru:=Bit_0;
256:KlimaError[5].VisokaVlaznost:=Bit_0;
257:KlimaError[5].VisokPritiskKompresor1:=Bit_0;
258:KlimaError[5].VisokPritiskKompresor2:=Bit_0;
259:KlimaError[5].ZamasenFilter:=Bit_0;
260:KlimaError[5].ZunanjiAlarm:=Bit_0;
261:KlimaError[6].AlarmKompresor1:=Bit_0;
262:KlimaError[6].AlarmKompresor2:=Bit_0;
263:KlimaError[6].FenThermalCutout:=Bit_0;
264:KlimaError[6].IzlivVode:=Bit_0;
265:KlimaError[6].Kompresor1naMejiStevilaObrUr:=Bit_0;
266:KlimaError[6].Kompresor2naMejiStevilaObrUr:=Bit_0;
267:KlimaError[6].NapakaPriPretokuVode:=Bit_0;
268:KlimaError[6].NapakaPriPretokuZraka:=Bit_0;
269:KlimaError[6].NapakaSenzorVlaznosti:=Bit_0;
270:KlimaError[6].NapakaTSTemperaturaProstora:=Bit_0;
271:KlimaError[6].NapakaVlazilca:=Bit_0;
272:KlimaError[6].NizekPritiskKompresor1:=Bit_0;
273:KlimaError[6].NizekPritiskKompresor2:=Bit_0;
274:KlimaError[6].NizkaTempVProstoru:=Bit_0;
275:KlimaError[6].NizkaVlaznost:=Bit_0;
276:KlimaError[6].PozarniAlarm:=Bit_0;
277:KlimaError[6].ThermalCutoutHeater1:=Bit_0;
278:KlimaError[6].ThermalCutoutHeater2:=Bit_0;
279:KlimaError[6].VentilatorNaMejiStevilaObrUr:=Bit_0;
280:KlimaError[6].VisokaTempVProstoru:=Bit_0;
281:KlimaError[6].VisokaVlaznost:=Bit_0;
282:KlimaError[6].VisokPritiskKompresor1:=Bit_0;
283:KlimaError[6].VisokPritiskKompresor2:=Bit_0;
284:KlimaError[6].ZamasenFilter:=Bit_0;
285:KlimaError[6].ZunanjiAlarm:=Bit_0;
286:NacDeloKlima1_2Avtom:=Bit_0;
287:NacDeloKlima3_4Avtom:=Bit_0;
288:NacDeloKlima5_6Avtom:=Bit_0;
289:NapakaSenzorTemp1:=Bit_0;
290:NapakaSenzorTemp2:=Bit_0;
291:NapakaSenzorTemp3:=Bit_0;
292:NapakaSenzorTemp4:=Bit_0;
293:NapakaSenzorVlaga1:=Bit_0;
294:NapakaSenzorVlaga2:=Bit_0;
295:NapakaSenzorVlaga3:=Bit_0;
296:NapakaSenzorVlaga4:=Bit_0;
297:NastaviCasNaKrmilniku:=Bit_0;
298:NastavitevUreKrUspesna:=Bit_0;
299:OpozoriloBaterijaPLC:=Bit_0;
300:OpozoriloPMM2x17med60in80[10]:=Bit_0;
301:OpozoriloPMM2x17med60in80[11]:=Bit_0;
302:OpozoriloPMM2x17med60in80[12]:=Bit_0;
303:OpozoriloPMM2x17med60in80[13]:=Bit_0;
304:OpozoriloPMM2x17med60in80[14]:=Bit_0;
305:OpozoriloPMM2x17med60in80[15]:=Bit_0;
306:OpozoriloPMM2x17med60in80[16]:=Bit_0;
307:OpozoriloPMM2x17med60in80[17]:=Bit_0;
308:OpozoriloPMM2x17med60in80[18]:=Bit_0;
309:OpozoriloPMM2x17med60in80[19]:=Bit_0;
310:OpozoriloPMM2x17med60in80[1]:=Bit_0;
311:OpozoriloPMM2x17med60in80[20]:=Bit_0;
312:OpozoriloPMM2x17med60in80[21]:=Bit_0;
313:OpozoriloPMM2x17med60in80[22]:=Bit_0;
314:OpozoriloPMM2x17med60in80[23]:=Bit_0;
315:OpozoriloPMM2x17med60in80[24]:=Bit_0;
316:OpozoriloPMM2x17med60in80[25]:=Bit_0;
317:OpozoriloPMM2x17med60in80[26]:=Bit_0;
318:OpozoriloPMM2x17med60in80[27]:=Bit_0;
319:OpozoriloPMM2x17med60in80[28]:=Bit_0;
320:OpozoriloPMM2x17med60in80[29]:=Bit_0;
321:OpozoriloPMM2x17med60in80[2]:=Bit_0;
322:OpozoriloPMM2x17med60in80[30]:=Bit_0;
323:OpozoriloPMM2x17med60in80[31]:=Bit_0;
324:OpozoriloPMM2x17med60in80[32]:=Bit_0;
325:OpozoriloPMM2x17med60in80[33]:=Bit_0;
326:OpozoriloPMM2x17med60in80[34]:=Bit_0;
327:OpozoriloPMM2x17med60in80[35]:=Bit_0;
328:OpozoriloPMM2x17med60in80[36]:=Bit_0;
329:OpozoriloPMM2x17med60in80[37]:=Bit_0;
330:OpozoriloPMM2x17med60in80[38]:=Bit_0;
331:OpozoriloPMM2x17med60in80[39]:=Bit_0;
332:OpozoriloPMM2x17med60in80[3]:=Bit_0;
333:OpozoriloPMM2x17med60in80[40]:=Bit_0;
334:OpozoriloPMM2x17med60in80[41]:=Bit_0;
335:OpozoriloPMM2x17med60in80[42]:=Bit_0;
336:OpozoriloPMM2x17med60in80[4]:=Bit_0;
337:OpozoriloPMM2x17med60in80[5]:=Bit_0;
338:OpozoriloPMM2x17med60in80[6]:=Bit_0;
339:OpozoriloPMM2x17med60in80[7]:=Bit_0;
340:OpozoriloPMM2x17med60in80[8]:=Bit_0;
341:OpozoriloPMM2x17med60in80[9]:=Bit_0;
342:PhaseBool[0]:=Bit_0;
343:PhaseBool[1]:=Bit_0;
344:PhaseBool[2]:=Bit_0;
345:PhaseNext:=Bit_0;
346:PhasePrev:=Bit_0;
347:PMM1OverCurrentBetw[1]:=Bit_0;
348:PMM1OverCurrentBetw[2]:=Bit_0;
349:PMM1OverCurrentBetw[3]:=Bit_0;
350:PMM1OverCurrentOver[1]:=Bit_0;
351:PMM1OverCurrentOver[2]:=Bit_0;
352:PMM1OverCurrentOver[3]:=Bit_0;
353:PMM1OverVoltage:=Bit_0;
354:PMM2OverCurrentBetw[1]:=Bit_0;
355:PMM2OverCurrentBetw[2]:=Bit_0;
356:PMM2OverCurrentBetw[3]:=Bit_0;
357:PMM2OverCurrentOver[1]:=Bit_0;
358:PMM2OverCurrentOver[2]:=Bit_0;
359:PMM2OverCurrentOver[3]:=Bit_0;
360:PMM2OverVoltage:=Bit_0;
361:PMM2x17:=Bit_0;
362:RocniVklopKlima1:=Bit_0;
363:RocniVklopKlima2:=Bit_0;
364:RocniVklopKlima3:=Bit_0;
365:RocniVklopKlima4:=Bit_0;
366:RocniVklopKlima5:=Bit_0;
367:RocniVklopKlima6:=Bit_0;
368:SinhronizacijaPanelOK:=Bit_0;
369:SinhronizirajCas_Panel:=Bit_0;
370:SkupneNapakeNaprav_Klima1:=Bit_0;
371:SkupneNapakeNaprav_Klima2:=Bit_0;
372:SkupneNapakeNaprav_Klima3:=Bit_0;
373:SkupneNapakeNaprav_Klima4:=Bit_0;
374:SkupneNapakeNaprav_Klima5:=Bit_0;
375:SkupneNapakeNaprav_Klima6:=Bit_0;
376:SkupneNapakeNaprav_Komunikacija:=Bit_0;
377:SkupneNapakeNaprav_PMM17VirBVirA:=Bit_0;
378:SkupneNapakeNaprav_PMM63VirBVirA:=Bit_0;
379:SkupneNapakeNaprav_TempVlaga:=Bit_0;
380:StanjeKlimat2_1_Delovanje:=Bit_0;
381:StanjeKlimat2_2_Delovanje:=Bit_0;
382:StanjeKlimat2_3_Delovanje:=Bit_0;
383:StanjeKlimat2_4_Delovanje:=Bit_0;
384:StanjeKlimat2_5_Delovanje:=Bit_0;
385:StanjeKlimat2_6_Delovanje:=Bit_0;
386:StanjeUPSKrmOmara_BaterijskiNacin:=Bit_0;
387:StanjeUPSKrmOmara_Polnjenje:=Bit_0;
388:UserLoggedIn:=Bit_0;
389:XVH_AlarmOn:=Bit_0;
390:Klimat2_1_Vklop:=Bit_0;
391:Klimat2_2_Vklop:=Bit_0;
392:Klimat2_3_Vklop:=Bit_0;
393:Klimat2_4_Vklop:=Bit_0;
394:Klimat2_5_Vklop:=Bit_0;
395:Klimat2_6_Vklop:=Bit_0;
396:ErrCommScada2:=Bit_0;
397:ComSCADA2:=Bit_0;
398:ComSCADA3:=Bit_0;
399:AlarmSKTemp5_Previsoka:=Bit_0;
400:AlarmSKTemp6_Previsoka:=Bit_0;
401:AlarmTempTIA5Previsoka:=Bit_0;
402:AlarmTempTIA6Previsoka:=Bit_0;
403:NapakaSenzorTemp5:=Bit_0;
404:NapakaSenzorTemp6:=Bit_0;
405:NapakaSenzorVlaga5:=Bit_0;
406:NapakaSenzorVlaga6:=Bit_0;
407:AlarmTempTIA235Previsoka:=Bit_0;
408:AlarmTempTIA46Previsoka:=Bit_0;
(*BOOL*)
END_CASE
END_FUNCTION
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_dWord : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje LONG*)
(**)
(*Pisanje REAL*)
(**)
4001:AktualniSetPointTemp1_2:=Real_0;
4003:AktualniSetPointTemp3_4:=Real_0;
4005:AktualniSetPointTemp5_6:=Real_0;
4007:Klima1ure:=Real_0;
4009:Klima2ure:=Real_0;
4011:Klima3ure:=Real_0;
4013:Klima4ure:=Real_0;
4015:Klima5ure:=Real_0;
4017:Klima6ure:=Real_0;
4019:Klima[1].NastMaxTemp:=Real_0;
4021:Klima[1].NastMaxVlaznost:=Real_0;
4023:Klima[1].NastMinTemp:=Real_0;
4025:Klima[1].NastMinVlaznost:=Real_0;
4027:Klima[1].NastTempProstora:=Real_0;
4029:Klima[1].NastVlaznost:=Real_0;
4031:Klima[1].ObratUreFilter:=Real_0;
4033:Klima[1].ObratUreKompresor1:=Real_0;
4035:Klima[1].ObratUreKompresor2:=Real_0;
4037:Klima[1].ObratUreVent:=Real_0;
4039:Klima[1].TemperaturaProstora:=Real_0;
4041:Klima[1].VlaznostProstora:=Real_0;
4043:Klima[2].NastMaxTemp:=Real_0;
4045:Klima[2].NastMaxVlaznost:=Real_0;
4047:Klima[2].NastMinTemp:=Real_0;
4049:Klima[2].NastMinVlaznost:=Real_0;
4051:Klima[2].NastTempProstora:=Real_0;
4053:Klima[2].NastVlaznost:=Real_0;
4055:Klima[2].ObratUreFilter:=Real_0;
4057:Klima[2].ObratUreKompresor1:=Real_0;
4059:Klima[2].ObratUreKompresor2:=Real_0;
4061:Klima[2].ObratUreVent:=Real_0;
4063:Klima[2].TemperaturaProstora:=Real_0;
4065:Klima[2].VlaznostProstora:=Real_0;
4067:Klima[3].NastMaxTemp:=Real_0;
4069:Klima[3].NastMaxVlaznost:=Real_0;
4071:Klima[3].NastMinTemp:=Real_0;
4073:Klima[3].NastMinVlaznost:=Real_0;
4075:Klima[3].NastTempProstora:=Real_0;
4077:Klima[3].NastVlaznost:=Real_0;
4079:Klima[3].ObratUreFilter:=Real_0;
4081:Klima[3].ObratUreKompresor1:=Real_0;
4083:Klima[3].ObratUreKompresor2:=Real_0;
4085:Klima[3].ObratUreVent:=Real_0;
4087:Klima[3].TemperaturaProstora:=Real_0;
4089:Klima[3].VlaznostProstora:=Real_0;
4091:Klima[4].NastMaxTemp:=Real_0;
4093:Klima[4].NastMaxVlaznost:=Real_0;
4095:Klima[4].NastMinTemp:=Real_0;
4097:Klima[4].NastMinVlaznost:=Real_0;
4099:Klima[4].NastTempProstora:=Real_0;
4101:Klima[4].NastVlaznost:=Real_0;
4103:Klima[4].ObratUreFilter:=Real_0;
4105:Klima[4].ObratUreKompresor1:=Real_0;
4107:Klima[4].ObratUreKompresor2:=Real_0;
4109:Klima[4].ObratUreVent:=Real_0;
4111:Klima[4].TemperaturaProstora:=Real_0;
4113:Klima[4].VlaznostProstora:=Real_0;
4115:Klima[5].NastMaxTemp:=Real_0;
4117:Klima[5].NastMaxVlaznost:=Real_0;
4119:Klima[5].NastMinTemp:=Real_0;
4121:Klima[5].NastMinVlaznost:=Real_0;
4123:Klima[5].NastTempProstora:=Real_0;
4125:Klima[5].NastVlaznost:=Real_0;
4127:Klima[5].ObratUreFilter:=Real_0;
4129:Klima[5].ObratUreKompresor1:=Real_0;
4131:Klima[5].ObratUreKompresor2:=Real_0;
4133:Klima[5].ObratUreVent:=Real_0;
4135:Klima[5].TemperaturaProstora:=Real_0;
4137:Klima[5].VlaznostProstora:=Real_0;
4139:Klima[6].NastMaxTemp:=Real_0;
4141:Klima[6].NastMaxVlaznost:=Real_0;
4143:Klima[6].NastMinTemp:=Real_0;
4145:Klima[6].NastMinVlaznost:=Real_0;
4147:Klima[6].NastTempProstora:=Real_0;
4149:Klima[6].NastVlaznost:=Real_0;
4151:Klima[6].ObratUreFilter:=Real_0;
4153:Klima[6].ObratUreKompresor1:=Real_0;
4155:Klima[6].ObratUreKompresor2:=Real_0;
4157:Klima[6].ObratUreVent:=Real_0;
4159:Klima[6].TemperaturaProstora:=Real_0;
4161:Klima[6].VlaznostProstora:=Real_0;
4163:PMM[1].ActiveEnergyConsumed_kWh:=Real_0;
4165:PMM[1].ActivePowerPhaseA_kW:=Real_0;
4167:PMM[1].ActivePowerPhaseB_kW:=Real_0;
4169:PMM[1].ActivePowerPhaseC_kW:=Real_0;
4171:PMM[1].AparentPowerPhaseA:=Real_0;
4173:PMM[1].AparentPowerPhaseB:=Real_0;
4175:PMM[1].AparentPowerPhaseC:=Real_0;
4177:PMM[1].AverageCurrent_A:=Real_0;
4179:PMM[1].AveragePhaseToNeutral_V:=Real_0;
4181:PMM[1].AveragePhaseToPhase_V:=Real_0;
4183:PMM[1].CurrentInPhaseA_A:=Real_0;
4185:PMM[1].CurrentInPhaseB_A:=Real_0;
4187:PMM[1].CurrentInPhaseC_A:=Real_0;
4189:PMM[1].Frequency_Hz:=Real_0;
4191:PMM[1].Phase[1].Current[10]:=Real_0;
4193:PMM[1].Phase[1].Current[11]:=Real_0;
4195:PMM[1].Phase[1].Current[12]:=Real_0;
4197:PMM[1].Phase[1].Current[13]:=Real_0;
4199:PMM[1].Phase[1].Current[14]:=Real_0;
4201:PMM[1].Phase[1].Current[15]:=Real_0;
4203:PMM[1].Phase[1].Current[16]:=Real_0;
4205:PMM[1].Phase[1].Current[17]:=Real_0;
4207:PMM[1].Phase[1].Current[18]:=Real_0;
4209:PMM[1].Phase[1].Current[19]:=Real_0;
4211:PMM[1].Phase[1].Current[1]:=Real_0;
4213:PMM[1].Phase[1].Current[20]:=Real_0;
4215:PMM[1].Phase[1].Current[21]:=Real_0;
4217:PMM[1].Phase[1].Current[22]:=Real_0;
4219:PMM[1].Phase[1].Current[23]:=Real_0;
4221:PMM[1].Phase[1].Current[24]:=Real_0;
4223:PMM[1].Phase[1].Current[25]:=Real_0;
4225:PMM[1].Phase[1].Current[26]:=Real_0;
4227:PMM[1].Phase[1].Current[27]:=Real_0;
4229:PMM[1].Phase[1].Current[28]:=Real_0;
4231:PMM[1].Phase[1].Current[29]:=Real_0;
4233:PMM[1].Phase[1].Current[2]:=Real_0;
4235:PMM[1].Phase[1].Current[30]:=Real_0;
4237:PMM[1].Phase[1].Current[31]:=Real_0;
4239:PMM[1].Phase[1].Current[32]:=Real_0;
4241:PMM[1].Phase[1].Current[33]:=Real_0;
4243:PMM[1].Phase[1].Current[34]:=Real_0;
4245:PMM[1].Phase[1].Current[35]:=Real_0;
4247:PMM[1].Phase[1].Current[36]:=Real_0;
4249:PMM[1].Phase[1].Current[37]:=Real_0;
4251:PMM[1].Phase[1].Current[38]:=Real_0;
4253:PMM[1].Phase[1].Current[39]:=Real_0;
4255:PMM[1].Phase[1].Current[3]:=Real_0;
4257:PMM[1].Phase[1].Current[40]:=Real_0;
4259:PMM[1].Phase[1].Current[41]:=Real_0;
4261:PMM[1].Phase[1].Current[42]:=Real_0;
4263:PMM[1].Phase[1].Current[4]:=Real_0;
4265:PMM[1].Phase[1].Current[5]:=Real_0;
4267:PMM[1].Phase[1].Current[6]:=Real_0;
4269:PMM[1].Phase[1].Current[7]:=Real_0;
4271:PMM[1].Phase[1].Current[8]:=Real_0;
4273:PMM[1].Phase[1].Current[9]:=Real_0;
4275:PMM[1].Phase[2].Current[10]:=Real_0;
4277:PMM[1].Phase[2].Current[11]:=Real_0;
4279:PMM[1].Phase[2].Current[12]:=Real_0;
4281:PMM[1].Phase[2].Current[13]:=Real_0;
4283:PMM[1].Phase[2].Current[14]:=Real_0;
4285:PMM[1].Phase[2].Current[15]:=Real_0;
4287:PMM[1].Phase[2].Current[16]:=Real_0;
4289:PMM[1].Phase[2].Current[17]:=Real_0;
4291:PMM[1].Phase[2].Current[18]:=Real_0;
4293:PMM[1].Phase[2].Current[19]:=Real_0;
4295:PMM[1].Phase[2].Current[1]:=Real_0;
4297:PMM[1].Phase[2].Current[20]:=Real_0;
4299:PMM[1].Phase[2].Current[21]:=Real_0;
4301:PMM[1].Phase[2].Current[22]:=Real_0;
4303:PMM[1].Phase[2].Current[23]:=Real_0;
4305:PMM[1].Phase[2].Current[24]:=Real_0;
4307:PMM[1].Phase[2].Current[25]:=Real_0;
4309:PMM[1].Phase[2].Current[26]:=Real_0;
4311:PMM[1].Phase[2].Current[27]:=Real_0;
4313:PMM[1].Phase[2].Current[28]:=Real_0;
4315:PMM[1].Phase[2].Current[29]:=Real_0;
4317:PMM[1].Phase[2].Current[2]:=Real_0;
4319:PMM[1].Phase[2].Current[30]:=Real_0;
4321:PMM[1].Phase[2].Current[31]:=Real_0;
4323:PMM[1].Phase[2].Current[32]:=Real_0;
4325:PMM[1].Phase[2].Current[33]:=Real_0;
4327:PMM[1].Phase[2].Current[34]:=Real_0;
4329:PMM[1].Phase[2].Current[35]:=Real_0;
4331:PMM[1].Phase[2].Current[36]:=Real_0;
4333:PMM[1].Phase[2].Current[37]:=Real_0;
4335:PMM[1].Phase[2].Current[38]:=Real_0;
4337:PMM[1].Phase[2].Current[39]:=Real_0;
4339:PMM[1].Phase[2].Current[3]:=Real_0;
4341:PMM[1].Phase[2].Current[40]:=Real_0;
4343:PMM[1].Phase[2].Current[41]:=Real_0;
4345:PMM[1].Phase[2].Current[42]:=Real_0;
4347:PMM[1].Phase[2].Current[4]:=Real_0;
4349:PMM[1].Phase[2].Current[5]:=Real_0;
4351:PMM[1].Phase[2].Current[6]:=Real_0;
4353:PMM[1].Phase[2].Current[7]:=Real_0;
4355:PMM[1].Phase[2].Current[8]:=Real_0;
4357:PMM[1].Phase[2].Current[9]:=Real_0;
4359:PMM[1].Phase[3].Current[10]:=Real_0;
4361:PMM[1].Phase[3].Current[11]:=Real_0;
4363:PMM[1].Phase[3].Current[12]:=Real_0;
4365:PMM[1].Phase[3].Current[13]:=Real_0;
4367:PMM[1].Phase[3].Current[14]:=Real_0;
4369:PMM[1].Phase[3].Current[15]:=Real_0;
4371:PMM[1].Phase[3].Current[16]:=Real_0;
4373:PMM[1].Phase[3].Current[17]:=Real_0;
4375:PMM[1].Phase[3].Current[18]:=Real_0;
4377:PMM[1].Phase[3].Current[19]:=Real_0;
4379:PMM[1].Phase[3].Current[1]:=Real_0;
4381:PMM[1].Phase[3].Current[20]:=Real_0;
4383:PMM[1].Phase[3].Current[21]:=Real_0;
4385:PMM[1].Phase[3].Current[22]:=Real_0;
4387:PMM[1].Phase[3].Current[23]:=Real_0;
4389:PMM[1].Phase[3].Current[24]:=Real_0;
4391:PMM[1].Phase[3].Current[25]:=Real_0;
4393:PMM[1].Phase[3].Current[26]:=Real_0;
4395:PMM[1].Phase[3].Current[27]:=Real_0;
4397:PMM[1].Phase[3].Current[28]:=Real_0;
4399:PMM[1].Phase[3].Current[29]:=Real_0;
4401:PMM[1].Phase[3].Current[2]:=Real_0;
4403:PMM[1].Phase[3].Current[30]:=Real_0;
4405:PMM[1].Phase[3].Current[31]:=Real_0;
4407:PMM[1].Phase[3].Current[32]:=Real_0;
4409:PMM[1].Phase[3].Current[33]:=Real_0;
4411:PMM[1].Phase[3].Current[34]:=Real_0;
4413:PMM[1].Phase[3].Current[35]:=Real_0;
4415:PMM[1].Phase[3].Current[36]:=Real_0;
4417:PMM[1].Phase[3].Current[37]:=Real_0;
4419:PMM[1].Phase[3].Current[38]:=Real_0;
4421:PMM[1].Phase[3].Current[39]:=Real_0;
4423:PMM[1].Phase[3].Current[3]:=Real_0;
4425:PMM[1].Phase[3].Current[40]:=Real_0;
4427:PMM[1].Phase[3].Current[41]:=Real_0;
4429:PMM[1].Phase[3].Current[42]:=Real_0;
4431:PMM[1].Phase[3].Current[4]:=Real_0;
4433:PMM[1].Phase[3].Current[5]:=Real_0;
4435:PMM[1].Phase[3].Current[6]:=Real_0;
4437:PMM[1].Phase[3].Current[7]:=Real_0;
4439:PMM[1].Phase[3].Current[8]:=Real_0;
4441:PMM[1].Phase[3].Current[9]:=Real_0;
4443:PMM[1].PowerFactorSys:=Real_0;
4445:PMM[1].ReactiveEnergyConsumed_kVARh:=Real_0;
4447:PMM[1].ReactivePowerPhaseA:=Real_0;
4449:PMM[1].ReactivePowerPhaseB:=Real_0;
4451:PMM[1].ReactivePowerPhaseC:=Real_0;
4453:PMM[1].TotalActivePower_kW:=Real_0;
4455:PMM[1].TotalAparentPower_kVA:=Real_0;
4457:PMM[1].TotalPowerFactor:=Real_0;
4459:PMM[1].TotalReactivePower_kVAR:=Real_0;
4461:PMM[1].VirA_fsys:=Real_0;
4463:PMM[1].VirA_Isys:=Real_0;
4465:PMM[1].VirA_PFsys:=Real_0;
4467:PMM[1].VirA_Psys:=Real_0;
4469:PMM[1].VirA_Qsys:=Real_0;
4471:PMM[1].VirA_Ssys:=Real_0;
4473:PMM[1].VirA_Usys:=Real_0;
4475:PMM[1].VirB_fsys:=Real_0;
4477:PMM[1].VirB_Isys:=Real_0;
4479:PMM[1].VirB_PFsys:=Real_0;
4481:PMM[1].VirB_Psys:=Real_0;
4483:PMM[1].VirB_Qsys:=Real_0;
4485:PMM[1].VirB_Ssys:=Real_0;
4487:PMM[1].VirB_Usys:=Real_0;
4489:PMM[1].VirBActiveEnergyConsumed_kWh:=Real_0;
4491:PMM[1].VirBActivePowerPhaseA_kW:=Real_0;
4493:PMM[1].VirBActivePowerPhaseB_kW:=Real_0;
4495:PMM[1].VirBActivePowerPhaseC_kW:=Real_0;
4497:PMM[1].VirBAparentPowerPhaseA:=Real_0;
4499:PMM[1].VirBAparentPowerPhaseB:=Real_0;
4501:PMM[1].VirBAparentPowerPhaseC:=Real_0;
4503:PMM[1].VirBAverageCurrent_A:=Real_0;
4505:PMM[1].VirBAveragePhaseToNeutral_V:=Real_0;
4507:PMM[1].VirBAveragePhaseToPhase_V:=Real_0;
4509:PMM[1].VirBCurrentInPhaseA_A:=Real_0;
4511:PMM[1].VirBCurrentInPhaseB_A:=Real_0;
4513:PMM[1].VirBCurrentInPhaseC_A:=Real_0;
4515:PMM[1].VirBFrequency_Hz:=Real_0;
4517:PMM[1].VirBPowerFactorSys:=Real_0;
4519:PMM[1].VirBReactiveEnergyConsumed_kVARh:=Real_0;
4521:PMM[1].VirBReactivePowerPhaseA:=Real_0;
4523:PMM[1].VirBReactivePowerPhaseB:=Real_0;
4525:PMM[1].VirBReactivePowerPhaseC:=Real_0;
4527:PMM[1].VirBTotalActivePower_kW:=Real_0;
4529:PMM[1].VirBTotalAparentPower_kVA:=Real_0;
4531:PMM[1].VirBTotalPowerFactor:=Real_0;
4533:PMM[1].VirBTotalReactivePower_kVAR:=Real_0;
4535:PMM[1].VirBVoltageBetweenPhaseAB_V:=Real_0;
4537:PMM[1].VirBVoltageBetweenPhaseAN_V:=Real_0;
4539:PMM[1].VirBVoltageBetweenPhaseBC_V:=Real_0;
4541:PMM[1].VirBVoltageBetweenPhaseBN_V:=Real_0;
4543:PMM[1].VirBVoltageBetweenPhaseCA_V:=Real_0;
4545:PMM[1].VirBVoltageBetweenPhaseCN_V:=Real_0;
4547:PMM[1].VoltageBetweenPhaseAB_V:=Real_0;
4549:PMM[1].VoltageBetweenPhaseAN_V:=Real_0;
4551:PMM[1].VoltageBetweenPhaseBC_V:=Real_0;
4553:PMM[1].VoltageBetweenPhaseBN_V:=Real_0;
4555:PMM[1].VoltageBetweenPhaseCA_V:=Real_0;
4557:PMM[1].VoltageBetweenPhaseCN_V:=Real_0;
4559:PMM[2].ActiveEnergyConsumed_kWh:=Real_0;
4561:PMM[2].ActivePowerPhaseA_kW:=Real_0;
4563:PMM[2].ActivePowerPhaseB_kW:=Real_0;
4565:PMM[2].ActivePowerPhaseC_kW:=Real_0;
4567:PMM[2].AparentPowerPhaseA:=Real_0;
4569:PMM[2].AparentPowerPhaseB:=Real_0;
4571:PMM[2].AparentPowerPhaseC:=Real_0;
4573:PMM[2].AverageCurrent_A:=Real_0;
4575:PMM[2].AveragePhaseToNeutral_V:=Real_0;
4577:PMM[2].AveragePhaseToPhase_V:=Real_0;
4579:PMM[2].CurrentInPhaseA_A:=Real_0;
4581:PMM[2].CurrentInPhaseB_A:=Real_0;
4583:PMM[2].CurrentInPhaseC_A:=Real_0;
4585:PMM[2].Frequency_Hz:=Real_0;
4587:PMM[2].Phase[1].Current[1]:=Real_0;
4589:PMM[2].Phase[1].Current[2]:=Real_0;
4591:PMM[2].Phase[1].Current[3]:=Real_0;
4593:PMM[2].Phase[1].Current[4]:=Real_0;
4595:PMM[2].Phase[1].Current[5]:=Real_0;
4597:PMM[2].Phase[1].Current[6]:=Real_0;
4599:PMM[2].Phase[1].Current[7]:=Real_0;
4601:PMM[2].Phase[1].Current[8]:=Real_0;
4603:PMM[2].Phase[1].Current[9]:=Real_0;
4605:PMM[2].Phase[1].Current[10]:=Real_0;
4607:PMM[2].Phase[1].Current[11]:=Real_0;
4609:PMM[2].Phase[1].Current[12]:=Real_0;
4611:PMM[2].Phase[1].Current[13]:=Real_0;
4613:PMM[2].Phase[1].Current[14]:=Real_0;
4615:PMM[2].Phase[1].Current[15]:=Real_0;
4617:PMM[2].Phase[1].Current[16]:=Real_0;
4619:PMM[2].Phase[1].Current[17]:=Real_0;
4621:PMM[2].Phase[1].Current[18]:=Real_0;
4623:PMM[2].Phase[1].Current[19]:=Real_0;
4625:PMM[2].Phase[1].Current[20]:=Real_0;
4627:PMM[2].Phase[1].Current[21]:=Real_0;
4629:PMM[2].Phase[1].Current[22]:=Real_0;
4631:PMM[2].Phase[1].Current[23]:=Real_0;
4633:PMM[2].Phase[1].Current[24]:=Real_0;
4635:PMM[2].Phase[1].Current[25]:=Real_0;
4637:PMM[2].Phase[1].Current[26]:=Real_0;
4639:PMM[2].Phase[1].Current[27]:=Real_0;
4641:PMM[2].Phase[1].Current[28]:=Real_0;
4643:PMM[2].Phase[1].Current[29]:=Real_0;
4645:PMM[2].Phase[1].Current[30]:=Real_0;
4647:PMM[2].Phase[1].Current[31]:=Real_0;
4649:PMM[2].Phase[1].Current[32]:=Real_0;
4651:PMM[2].Phase[1].Current[33]:=Real_0;
4653:PMM[2].Phase[1].Current[34]:=Real_0;
4655:PMM[2].Phase[1].Current[35]:=Real_0;
4657:PMM[2].Phase[1].Current[36]:=Real_0;
4659:PMM[2].Phase[1].Current[37]:=Real_0;
4661:PMM[2].Phase[1].Current[38]:=Real_0;
4663:PMM[2].Phase[1].Current[39]:=Real_0;
4665:PMM[2].Phase[1].Current[40]:=Real_0;
4667:PMM[2].Phase[1].Current[41]:=Real_0;
4669:PMM[2].Phase[1].Current[42]:=Real_0;
4671:PMM[2].Phase[2].Current[10]:=Real_0;
4673:PMM[2].Phase[2].Current[11]:=Real_0;
4675:PMM[2].Phase[2].Current[12]:=Real_0;
4677:PMM[2].Phase[2].Current[13]:=Real_0;
4679:PMM[2].Phase[2].Current[14]:=Real_0;
4681:PMM[2].Phase[2].Current[15]:=Real_0;
4683:PMM[2].Phase[2].Current[16]:=Real_0;
4685:PMM[2].Phase[2].Current[17]:=Real_0;
4687:PMM[2].Phase[2].Current[18]:=Real_0;
4689:PMM[2].Phase[2].Current[19]:=Real_0;
4691:PMM[2].Phase[2].Current[1]:=Real_0;
4693:PMM[2].Phase[2].Current[20]:=Real_0;
4695:PMM[2].Phase[2].Current[21]:=Real_0;
4697:PMM[2].Phase[2].Current[22]:=Real_0;
4699:PMM[2].Phase[2].Current[23]:=Real_0;
4701:PMM[2].Phase[2].Current[24]:=Real_0;
4703:PMM[2].Phase[2].Current[25]:=Real_0;
4705:PMM[2].Phase[2].Current[26]:=Real_0;
4707:PMM[2].Phase[2].Current[27]:=Real_0;
4709:PMM[2].Phase[2].Current[28]:=Real_0;
4711:PMM[2].Phase[2].Current[29]:=Real_0;
4713:PMM[2].Phase[2].Current[2]:=Real_0;
4715:PMM[2].Phase[2].Current[30]:=Real_0;
4717:PMM[2].Phase[2].Current[31]:=Real_0;
4719:PMM[2].Phase[2].Current[32]:=Real_0;
4721:PMM[2].Phase[2].Current[33]:=Real_0;
4723:PMM[2].Phase[2].Current[34]:=Real_0;
4725:PMM[2].Phase[2].Current[35]:=Real_0;
4727:PMM[2].Phase[2].Current[36]:=Real_0;
4729:PMM[2].Phase[2].Current[37]:=Real_0;
4731:PMM[2].Phase[2].Current[38]:=Real_0;
4733:PMM[2].Phase[2].Current[39]:=Real_0;
4735:PMM[2].Phase[2].Current[3]:=Real_0;
4737:PMM[2].Phase[2].Current[40]:=Real_0;
4739:PMM[2].Phase[2].Current[41]:=Real_0;
4741:PMM[2].Phase[2].Current[42]:=Real_0;
4743:PMM[2].Phase[2].Current[4]:=Real_0;
4745:PMM[2].Phase[2].Current[5]:=Real_0;
4747:PMM[2].Phase[2].Current[6]:=Real_0;
4749:PMM[2].Phase[2].Current[7]:=Real_0;
4751:PMM[2].Phase[2].Current[8]:=Real_0;
4753:PMM[2].Phase[2].Current[9]:=Real_0;
4755:PMM[2].Phase[3].Current[10]:=Real_0;
4757:PMM[2].Phase[3].Current[11]:=Real_0;
4759:PMM[2].Phase[3].Current[12]:=Real_0;
4761:PMM[2].Phase[3].Current[13]:=Real_0;
4763:PMM[2].Phase[3].Current[14]:=Real_0;
4765:PMM[2].Phase[3].Current[15]:=Real_0;
4767:PMM[2].Phase[3].Current[16]:=Real_0;
4769:PMM[2].Phase[3].Current[17]:=Real_0;
4771:PMM[2].Phase[3].Current[18]:=Real_0;
4773:PMM[2].Phase[3].Current[19]:=Real_0;
4775:PMM[2].Phase[3].Current[1]:=Real_0;
4777:PMM[2].Phase[3].Current[20]:=Real_0;
4779:PMM[2].Phase[3].Current[21]:=Real_0;
4781:PMM[2].Phase[3].Current[22]:=Real_0;
4783:PMM[2].Phase[3].Current[23]:=Real_0;
4785:PMM[2].Phase[3].Current[24]:=Real_0;
4787:PMM[2].Phase[3].Current[25]:=Real_0;
4789:PMM[2].Phase[3].Current[26]:=Real_0;
4791:PMM[2].Phase[3].Current[27]:=Real_0;
4793:PMM[2].Phase[3].Current[28]:=Real_0;
4795:PMM[2].Phase[3].Current[29]:=Real_0;
4797:PMM[2].Phase[3].Current[2]:=Real_0;
4799:PMM[2].Phase[3].Current[30]:=Real_0;
4801:PMM[2].Phase[3].Current[31]:=Real_0;
4803:PMM[2].Phase[3].Current[32]:=Real_0;
4805:PMM[2].Phase[3].Current[33]:=Real_0;
4807:PMM[2].Phase[3].Current[34]:=Real_0;
4809:PMM[2].Phase[3].Current[35]:=Real_0;
4811:PMM[2].Phase[3].Current[36]:=Real_0;
4813:PMM[2].Phase[3].Current[37]:=Real_0;
4815:PMM[2].Phase[3].Current[38]:=Real_0;
4817:PMM[2].Phase[3].Current[39]:=Real_0;
4819:PMM[2].Phase[3].Current[3]:=Real_0;
4821:PMM[2].Phase[3].Current[40]:=Real_0;
4823:PMM[2].Phase[3].Current[41]:=Real_0;
4825:PMM[2].Phase[3].Current[42]:=Real_0;
4827:PMM[2].Phase[3].Current[4]:=Real_0;
4829:PMM[2].Phase[3].Current[5]:=Real_0;
4831:PMM[2].Phase[3].Current[6]:=Real_0;
4833:PMM[2].Phase[3].Current[7]:=Real_0;
4835:PMM[2].Phase[3].Current[8]:=Real_0;
4837:PMM[2].Phase[3].Current[9]:=Real_0;
4839:PMM[2].PowerFactorSys:=Real_0;
4841:PMM[2].ReactiveEnergyConsumed_kVARh:=Real_0;
4843:PMM[2].ReactivePowerPhaseA:=Real_0;
4845:PMM[2].ReactivePowerPhaseB:=Real_0;
4847:PMM[2].ReactivePowerPhaseC:=Real_0;
4849:PMM[2].TotalActivePower_kW:=Real_0;
4851:PMM[2].TotalAparentPower_kVA:=Real_0;
4853:PMM[2].TotalPowerFactor:=Real_0;
4855:PMM[2].TotalReactivePower_kVAR:=Real_0;
4857:PMM[2].VirA_fsys:=Real_0;
4859:PMM[2].VirA_Isys:=Real_0;
4861:PMM[2].VirA_PFsys:=Real_0;
4863:PMM[2].VirA_Psys:=Real_0;
4865:PMM[2].VirA_Qsys:=Real_0;
4867:PMM[2].VirA_Ssys:=Real_0;
4869:PMM[2].VirA_Usys:=Real_0;
4871:PMM[2].VirB_fsys:=Real_0;
4873:PMM[2].VirB_Isys:=Real_0;
4875:PMM[2].VirB_PFsys:=Real_0;
4877:PMM[2].VirB_Psys:=Real_0;
4879:PMM[2].VirB_Qsys:=Real_0;
4881:PMM[2].VirB_Ssys:=Real_0;
4883:PMM[2].VirB_Usys:=Real_0;
4885:PMM[2].VirBActiveEnergyConsumed_kWh:=Real_0;
4887:PMM[2].VirBActivePowerPhaseA_kW:=Real_0;
4889:PMM[2].VirBActivePowerPhaseB_kW:=Real_0;
4891:PMM[2].VirBActivePowerPhaseC_kW:=Real_0;
4893:PMM[2].VirBAparentPowerPhaseA:=Real_0;
4895:PMM[2].VirBAparentPowerPhaseB:=Real_0;
4897:PMM[2].VirBAparentPowerPhaseC:=Real_0;
4899:PMM[2].VirBAverageCurrent_A:=Real_0;
4901:PMM[2].VirBAveragePhaseToNeutral_V:=Real_0;
4903:PMM[2].VirBAveragePhaseToPhase_V:=Real_0;
4905:PMM[2].VirBCurrentInPhaseA_A:=Real_0;
4907:PMM[2].VirBCurrentInPhaseB_A:=Real_0;
4909:PMM[2].VirBCurrentInPhaseC_A:=Real_0;
4911:PMM[2].VirBFrequency_Hz:=Real_0;
4913:PMM[2].VirBPowerFactorSys:=Real_0;
4915:PMM[2].VirBReactiveEnergyConsumed_kVARh:=Real_0;
4917:PMM[2].VirBReactivePowerPhaseA:=Real_0;
4919:PMM[2].VirBReactivePowerPhaseB:=Real_0;
4921:PMM[2].VirBReactivePowerPhaseC:=Real_0;
4923:PMM[2].VirBTotalActivePower_kW:=Real_0;
4925:PMM[2].VirBTotalAparentPower_kVA:=Real_0;
4927:PMM[2].VirBTotalPowerFactor:=Real_0;
4929:PMM[2].VirBTotalReactivePower_kVAR:=Real_0;
4931:PMM[2].VirBVoltageBetweenPhaseAB_V:=Real_0;
4933:PMM[2].VirBVoltageBetweenPhaseAN_V:=Real_0;
4935:PMM[2].VirBVoltageBetweenPhaseBC_V:=Real_0;
4937:PMM[2].VirBVoltageBetweenPhaseBN_V:=Real_0;
4939:PMM[2].VirBVoltageBetweenPhaseCA_V:=Real_0;
4941:PMM[2].VirBVoltageBetweenPhaseCN_V:=Real_0;
4943:PMM[2].VoltageBetweenPhaseAB_V:=Real_0;
4945:PMM[2].VoltageBetweenPhaseAN_V:=Real_0;
4947:PMM[2].VoltageBetweenPhaseBC_V:=Real_0;
4949:PMM[2].VoltageBetweenPhaseBN_V:=Real_0;
4951:PMM[2].VoltageBetweenPhaseCA_V:=Real_0;
4953:PMM[2].VoltageBetweenPhaseCN_V:=Real_0;
4955:PMMPanel.ActiveEnergyConsumed_kWh:=Real_0;
4957:PMMPanel.ActivePowerPhaseA_kW:=Real_0;
4959:PMMPanel.ActivePowerPhaseB_kW:=Real_0;
4961:PMMPanel.ActivePowerPhaseC_kW:=Real_0;
4963:PMMPanel.AparentPowerPhaseA:=Real_0;
4965:PMMPanel.AparentPowerPhaseB:=Real_0;
4967:PMMPanel.AparentPowerPhaseC:=Real_0;
4969:PMMPanel.AverageCurrent_A:=Real_0;
4971:PMMPanel.AveragePhaseToNeutral_V:=Real_0;
4973:PMMPanel.AveragePhaseToPhase_V:=Real_0;
4975:PMMPanel.CurrentInPhaseA_A:=Real_0;
4977:PMMPanel.CurrentInPhaseB_A:=Real_0;
4979:PMMPanel.CurrentInPhaseC_A:=Real_0;
4981:PMMPanel.Frequency_Hz:=Real_0;
4983:PMMPanel.PowerFactorSys:=Real_0;
4985:PMMPanel.ReactiveEnergyConsumed_kVARh:=Real_0;
4987:PMMPanel.ReactivePowerPhaseA:=Real_0;
4989:PMMPanel.ReactivePowerPhaseB:=Real_0;
4991:PMMPanel.ReactivePowerPhaseC:=Real_0;
4993:PMMPanel.TotalActivePower_kW:=Real_0;
4995:PMMPanel.TotalAparentPower_kVA:=Real_0;
4997:PMMPanel.TotalPowerFactor:=Real_0;
4999:PMMPanel.TotalReactivePower_kVAR:=Real_0;
5001:PMMPanel.VirA_fsys:=Real_0;
5003:PMMPanel.VirA_Isys:=Real_0;
5005:PMMPanel.VirA_PFsys:=Real_0;
5007:PMMPanel.VirA_Psys:=Real_0;
5009:PMMPanel.VirA_Qsys:=Real_0;
5011:PMMPanel.VirA_Ssys:=Real_0;
5013:PMMPanel.VirA_Usys:=Real_0;
5015:PMMPanel.VirB_fsys:=Real_0;
5017:PMMPanel.VirB_Isys:=Real_0;
5019:PMMPanel.VirB_PFsys:=Real_0;
5021:PMMPanel.VirB_Psys:=Real_0;
5023:PMMPanel.VirB_Qsys:=Real_0;
5025:PMMPanel.VirB_Ssys:=Real_0;
5027:PMMPanel.VirB_Usys:=Real_0;
5029:PMMPanel.VirBActiveEnergyConsumed_kWh:=Real_0;
5031:PMMPanel.VirBActivePowerPhaseA_kW:=Real_0;
5033:PMMPanel.VirBActivePowerPhaseB_kW:=Real_0;
5035:PMMPanel.VirBActivePowerPhaseC_kW:=Real_0;
5037:PMMPanel.VirBAparentPowerPhaseA:=Real_0;
5039:PMMPanel.VirBAparentPowerPhaseB:=Real_0;
5041:PMMPanel.VirBAparentPowerPhaseC:=Real_0;
5043:PMMPanel.VirBAverageCurrent_A:=Real_0;
5045:PMMPanel.VirBAveragePhaseToNeutral_V:=Real_0;
5047:PMMPanel.VirBAveragePhaseToPhase_V:=Real_0;
5049:PMMPanel.VirBCurrentInPhaseA_A:=Real_0;
5051:PMMPanel.VirBCurrentInPhaseB_A:=Real_0;
5053:PMMPanel.VirBCurrentInPhaseC_A:=Real_0;
5055:PMMPanel.VirBFrequency_Hz:=Real_0;
5057:PMMPanel.VirBPowerFactorSys:=Real_0;
5059:PMMPanel.VirBReactiveEnergyConsumed_kVARh:=Real_0;
5061:PMMPanel.VirBReactivePowerPhaseA:=Real_0;
5063:PMMPanel.VirBReactivePowerPhaseB:=Real_0;
5065:PMMPanel.VirBReactivePowerPhaseC:=Real_0;
5067:PMMPanel.VirBTotalActivePower_kW:=Real_0;
5069:PMMPanel.VirBTotalAparentPower_kVA:=Real_0;
5071:PMMPanel.VirBTotalPowerFactor:=Real_0;
5073:PMMPanel.VirBTotalReactivePower_kVAR:=Real_0;
5075:PMMPanel.VirBVoltageBetweenPhaseAB_V:=Real_0;
5077:PMMPanel.VirBVoltageBetweenPhaseAN_V:=Real_0;
5079:PMMPanel.VirBVoltageBetweenPhaseBC_V:=Real_0;
5081:PMMPanel.VirBVoltageBetweenPhaseBN_V:=Real_0;
5083:PMMPanel.VirBVoltageBetweenPhaseCA_V:=Real_0;
5085:PMMPanel.VirBVoltageBetweenPhaseCN_V:=Real_0;
5087:PMMPanel.VoltageBetweenPhaseAB_V:=Real_0;
5089:PMMPanel.VoltageBetweenPhaseAN_V:=Real_0;
5091:PMMPanel.VoltageBetweenPhaseBC_V:=Real_0;
5093:PMMPanel.VoltageBetweenPhaseBN_V:=Real_0;
5095:PMMPanel.VoltageBetweenPhaseCA_V:=Real_0;
5097:PMMPanel.VoltageBetweenPhaseCN_V:=Real_0;
5099:SKTemp1:=Real_0;
5101:SKTemp2:=Real_0;
5103:SKTemp3:=Real_0;
5105:SKTemp4:=Real_0;
5107:SKVlaga1:=Real_0;
5109:SKVlaga2:=Real_0;
5111:SKVlaga3:=Real_0;
5113:SKVlaga4:=Real_0;
5115:TempZaAlarm1_2:=Real_0;
5117:TempZaAlarm3_4:=Real_0;
5119:TempZaAlarm5_6:=Real_0;
5121:TempZaAlarmTIA1:=Real_0;
5123:TempZaAlarmTIA2:=Real_0;
5125:TempZaAlarmTIA3:=Real_0;
5127:TempZaAlarmTIA4:=Real_0;
5129:TempZaVklopObehKlim1_2:=Real_0;
5131:TempZaVklopObehKlim3_4:=Real_0;
5133:TempZaVklopObehKlim3_4TIA3:=Real_0;
5135:TempZaVklopObehKlim5_6:=Real_0;
5137:TempZaVklopObehKlim5_6TIA3:=Real_0;
5139:SKTemp5:=Real_0;
5141:SKTemp6:=Real_0;
5143:SKVlaga5:=Real_0;
5145:SKVlaga6:=Real_0;
5147:TempZaAlarmTIA5:=Real_0;
5149:TempZaAlarmTIA6:=Real_0;
5151:SKTempServSoba1Povpr:=Real_0;
5153:SKTempServSoba2Povpr:=Real_0;
5155:TempZaAlarmTIA235:=Real_0;
5157:TempZaAlarmTIA46:=Real_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_String : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje STRING*)
(**)
6000:Date_Time[0]:=String_0;
6015:Date_Time[1]:=String_0;
6030:Date_Time[2]:=String_0;
6045:Date_Time[3]:=String_0;
6060:UserName:=String_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Word : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje INT*)
(**)
0:DatumCas.Dan:=Byte_0;
1:DatumCas.Leto:=Byte_0;
2:DatumCas.Leto2:=Word_01;
3:DatumCas.Mesec:=Byte_0;
4:DatumCas.Minuta:=Byte_0;
5:DatumCas.Sekunda:=Byte_0;
6:DatumCas.Ura:=Byte_0;
7:ErrorComKlima[1].Status:=Word_01;
8:ErrorComKlima[2].Status:=Word_01;
9:ErrorComKlima[3].Status:=Word_01;
10:ErrorComKlima[4].Status:=Word_01;
11:ErrorComKlima[5].Status:=Word_01;
12:ErrorComKlima[6].Status:=Word_01;
13:ErrorComPMM[1].Status:=Word_01;
14:ErrorComPMM[2].Status:=Word_01;
15:Klima[1].GrelecStatus:=Byte_0;
16:Klima[1].IzhodniVentStatus:=Byte_0;
17:Klima[1].KompresorStatus:=Byte_0;
18:Klima[1].NacinRazvlaz:=Word_01;
19:Klima[1].VlazilecStatus:=Byte_0;
20:Klima[2].GrelecStatus:=Byte_0;
21:Klima[2].IzhodniVentStatus:=Byte_0;
22:Klima[2].KompresorStatus:=Byte_0;
23:Klima[2].NacinRazvlaz:=Word_01;
24:Klima[2].VlazilecStatus:=Byte_0;
25:Klima[3].GrelecStatus:=Byte_0;
26:Klima[3].IzhodniVentStatus:=Byte_0;
27:Klima[3].KompresorStatus:=Byte_0;
28:Klima[3].NacinRazvlaz:=Word_01;
29:Klima[3].VlazilecStatus:=Byte_0;
30:Klima[4].GrelecStatus:=Byte_0;
31:Klima[4].IzhodniVentStatus:=Byte_0;
32:Klima[4].KompresorStatus:=Byte_0;
33:Klima[4].NacinRazvlaz:=Word_01;
34:Klima[4].VlazilecStatus:=Byte_0;
35:Klima[5].GrelecStatus:=Byte_0;
36:Klima[5].IzhodniVentStatus:=Byte_0;
37:Klima[5].KompresorStatus:=Byte_0;
38:Klima[5].NacinRazvlaz:=Word_01;
39:Klima[5].VlazilecStatus:=Byte_0;
40:Klima[6].GrelecStatus:=Byte_0;
41:Klima[6].IzhodniVentStatus:=Byte_0;
42:Klima[6].KompresorStatus:=Byte_0;
43:Klima[6].NacinRazvlaz:=Word_01;
44:Klima[6].VlazilecStatus:=Byte_0;
45:OznakeFaz[10]:=Byte_0;
46:OznakeFaz[11]:=Byte_0;
47:OznakeFaz[12]:=Byte_0;
48:OznakeFaz[13]:=Byte_0;
49:OznakeFaz[14]:=Byte_0;
50:OznakeFaz[1]:=Byte_0;
51:OznakeFaz[2]:=Byte_0;
52:OznakeFaz[3]:=Byte_0;
53:OznakeFaz[4]:=Byte_0;
54:OznakeFaz[5]:=Byte_0;
55:OznakeFaz[6]:=Byte_0;
56:OznakeFaz[7]:=Byte_0;
57:OznakeFaz[8]:=Byte_0;
58:OznakeFaz[9]:=Byte_0;
59:PhaseNo:=Byte_0;
60:PMM[1].AlarmPhase[1].C01_16_60to80:=Byte_0;
61:PMM[1].AlarmPhase[1].C01_16_over80:=Byte_0;
62:PMM[1].AlarmPhase[1].C17_32_60to80:=Byte_0;
63:PMM[1].AlarmPhase[1].C17_32_over80:=Byte_0;
64:PMM[1].AlarmPhase[1].C33_42_60to80:=Byte_0;
65:PMM[1].AlarmPhase[1].C33_42_over80:=Byte_0;
66:PMM[1].AlarmPhase[1].GlobalAlarmReg:=Word_01;
67:PMM[1].AlarmPhase[2].C01_16_60to80:=Byte_0;
68:PMM[1].AlarmPhase[2].C01_16_over80:=Byte_0;
69:PMM[1].AlarmPhase[2].C17_32_60to80:=Byte_0;
70:PMM[1].AlarmPhase[2].C17_32_over80:=Byte_0;
71:PMM[1].AlarmPhase[2].C33_42_60to80:=Byte_0;
72:PMM[1].AlarmPhase[2].C33_42_over80:=Byte_0;
73:PMM[1].AlarmPhase[2].GlobalAlarmReg:=Word_01;
74:PMM[1].AlarmPhase[3].C01_16_60to80:=Byte_0;
75:PMM[1].AlarmPhase[3].C01_16_over80:=Byte_0;
76:PMM[1].AlarmPhase[3].C17_32_60to80:=Byte_0;
77:PMM[1].AlarmPhase[3].C17_32_over80:=Byte_0;
78:PMM[1].AlarmPhase[3].C33_42_60to80:=Byte_0;
79:PMM[1].AlarmPhase[3].C33_42_over80:=Byte_0;
80:PMM[1].AlarmPhase[3].GlobalAlarmReg:=Word_01;
81:PMM[2].AlarmPhase[1].C01_16_60to80:=Byte_0;
82:PMM[2].AlarmPhase[1].C01_16_over80:=Byte_0;
83:PMM[2].AlarmPhase[1].C17_32_60to80:=Byte_0;
84:PMM[2].AlarmPhase[1].C17_32_over80:=Byte_0;
85:PMM[2].AlarmPhase[1].C33_42_60to80:=Byte_0;
86:PMM[2].AlarmPhase[1].C33_42_over80:=Byte_0;
87:PMM[2].AlarmPhase[1].GlobalAlarmReg:=Word_01;
88:PMM[2].AlarmPhase[2].C01_16_60to80:=Byte_0;
89:PMM[2].AlarmPhase[2].C01_16_over80:=Byte_0;
90:PMM[2].AlarmPhase[2].C17_32_60to80:=Byte_0;
91:PMM[2].AlarmPhase[2].C17_32_over80:=Byte_0;
92:PMM[2].AlarmPhase[2].C33_42_60to80:=Byte_0;
93:PMM[2].AlarmPhase[2].C33_42_over80:=Byte_0;
94:PMM[2].AlarmPhase[2].GlobalAlarmReg:=Word_01;
95:PMM[2].AlarmPhase[3].C01_16_60to80:=Byte_0;
96:PMM[2].AlarmPhase[3].C01_16_over80:=Byte_0;
97:PMM[2].AlarmPhase[3].C17_32_60to80:=Byte_0;
98:PMM[2].AlarmPhase[3].C17_32_over80:=Byte_0;
99:PMM[2].AlarmPhase[3].C33_42_60to80:=Byte_0;
100:PMM[2].AlarmPhase[3].C33_42_over80:=Byte_0;
101:PMM[2].AlarmPhase[3].GlobalAlarmReg:=Word_01;
102:PMMPanel.AlarmPhase[1].C01_16_60to80:=Byte_0;
103:PMMPanel.AlarmPhase[1].C01_16_over80:=Byte_0;
104:PMMPanel.AlarmPhase[1].C17_32_60to80:=Byte_0;
105:PMMPanel.AlarmPhase[1].C17_32_over80:=Byte_0;
106:PMMPanel.AlarmPhase[1].C33_42_60to80:=Byte_0;
107:PMMPanel.AlarmPhase[1].C33_42_over80:=Byte_0;
108:PMMPanel.AlarmPhase[1].GlobalAlarmReg:=Word_01;
109:PMMPanel.AlarmPhase[2].C01_16_60to80:=Byte_0;
110:PMMPanel.AlarmPhase[2].C01_16_over80:=Byte_0;
111:PMMPanel.AlarmPhase[2].C17_32_60to80:=Byte_0;
112:PMMPanel.AlarmPhase[2].C17_32_over80:=Byte_0;
113:PMMPanel.AlarmPhase[2].C33_42_60to80:=Byte_0;
114:PMMPanel.AlarmPhase[2].C33_42_over80:=Byte_0;
115:PMMPanel.AlarmPhase[2].GlobalAlarmReg:=Word_01;
116:PMMPanel.AlarmPhase[3].C01_16_60to80:=Byte_0;
117:PMMPanel.AlarmPhase[3].C01_16_over80:=Byte_0;
118:PMMPanel.AlarmPhase[3].C17_32_60to80:=Byte_0;
119:PMMPanel.AlarmPhase[3].C17_32_over80:=Byte_0;
120:PMMPanel.AlarmPhase[3].C33_42_60to80:=Byte_0;
121:PMMPanel.AlarmPhase[3].C33_42_over80:=Byte_0;
122:PMMPanel.AlarmPhase[3].GlobalAlarmReg:=Word_01;
123:StUrZaPreklopKlim1_2:=Word_01;
124:StUrZaPreklopKlim3_4:=Word_01;
125:StUrZaPreklopKlim5_6:=Word_01;
126:UPSstatus_Prikaz_PanelSCADA:=Byte_0;
127:UserCurrentLevel:=Byte_0;
128:ErrorComKlima[1].Code[0]:=Byte_0;
129:ErrorComKlima[1].Code[10]:=Byte_0;
130:ErrorComKlima[1].Code[11]:=Byte_0;
131:ErrorComKlima[1].Code[12]:=Byte_0;
132:ErrorComKlima[1].Code[13]:=Byte_0;
133:ErrorComKlima[1].Code[14]:=Byte_0;
134:ErrorComKlima[1].Code[15]:=Byte_0;
135:ErrorComKlima[1].Code[1]:=Byte_0;
136:ErrorComKlima[1].Code[2]:=Byte_0;
137:ErrorComKlima[1].Code[3]:=Byte_0;
138:ErrorComKlima[1].Code[4]:=Byte_0;
139:ErrorComKlima[1].Code[5]:=Byte_0;
140:ErrorComKlima[1].Code[6]:=Byte_0;
141:ErrorComKlima[1].Code[7]:=Byte_0;
142:ErrorComKlima[1].Code[8]:=Byte_0;
143:ErrorComKlima[1].Code[9]:=Byte_0;
144:ErrorComKlima[2].Code[0]:=Byte_0;
145:ErrorComKlima[2].Code[10]:=Byte_0;
146:ErrorComKlima[2].Code[11]:=Byte_0;
147:ErrorComKlima[2].Code[12]:=Byte_0;
148:ErrorComKlima[2].Code[13]:=Byte_0;
149:ErrorComKlima[2].Code[14]:=Byte_0;
150:ErrorComKlima[2].Code[15]:=Byte_0;
151:ErrorComKlima[2].Code[1]:=Byte_0;
152:ErrorComKlima[2].Code[2]:=Byte_0;
153:ErrorComKlima[2].Code[3]:=Byte_0;
154:ErrorComKlima[2].Code[4]:=Byte_0;
155:ErrorComKlima[2].Code[5]:=Byte_0;
156:ErrorComKlima[2].Code[6]:=Byte_0;
157:ErrorComKlima[2].Code[7]:=Byte_0;
158:ErrorComKlima[2].Code[8]:=Byte_0;
159:ErrorComKlima[2].Code[9]:=Byte_0;
160:ErrorComKlima[3].Code[0]:=Byte_0;
161:ErrorComKlima[3].Code[10]:=Byte_0;
162:ErrorComKlima[3].Code[11]:=Byte_0;
163:ErrorComKlima[3].Code[12]:=Byte_0;
164:ErrorComKlima[3].Code[13]:=Byte_0;
165:ErrorComKlima[3].Code[14]:=Byte_0;
166:ErrorComKlima[3].Code[15]:=Byte_0;
167:ErrorComKlima[3].Code[1]:=Byte_0;
168:ErrorComKlima[3].Code[2]:=Byte_0;
169:ErrorComKlima[3].Code[3]:=Byte_0;
170:ErrorComKlima[3].Code[4]:=Byte_0;
171:ErrorComKlima[3].Code[5]:=Byte_0;
172:ErrorComKlima[3].Code[6]:=Byte_0;
173:ErrorComKlima[3].Code[7]:=Byte_0;
174:ErrorComKlima[3].Code[8]:=Byte_0;
175:ErrorComKlima[3].Code[9]:=Byte_0;
176:ErrorComKlima[4].Code[0]:=Byte_0;
177:ErrorComKlima[4].Code[10]:=Byte_0;
178:ErrorComKlima[4].Code[11]:=Byte_0;
179:ErrorComKlima[4].Code[12]:=Byte_0;
180:ErrorComKlima[4].Code[13]:=Byte_0;
181:ErrorComKlima[4].Code[14]:=Byte_0;
182:ErrorComKlima[4].Code[15]:=Byte_0;
183:ErrorComKlima[4].Code[1]:=Byte_0;
184:ErrorComKlima[4].Code[2]:=Byte_0;
185:ErrorComKlima[4].Code[3]:=Byte_0;
186:ErrorComKlima[4].Code[4]:=Byte_0;
187:ErrorComKlima[4].Code[5]:=Byte_0;
188:ErrorComKlima[4].Code[6]:=Byte_0;
189:ErrorComKlima[4].Code[7]:=Byte_0;
190:ErrorComKlima[4].Code[8]:=Byte_0;
191:ErrorComKlima[4].Code[9]:=Byte_0;
192:ErrorComKlima[5].Code[0]:=Byte_0;
193:ErrorComKlima[5].Code[10]:=Byte_0;
194:ErrorComKlima[5].Code[11]:=Byte_0;
195:ErrorComKlima[5].Code[12]:=Byte_0;
196:ErrorComKlima[5].Code[13]:=Byte_0;
197:ErrorComKlima[5].Code[14]:=Byte_0;
198:ErrorComKlima[5].Code[15]:=Byte_0;
199:ErrorComKlima[5].Code[1]:=Byte_0;
200:ErrorComKlima[5].Code[2]:=Byte_0;
201:ErrorComKlima[5].Code[3]:=Byte_0;
202:ErrorComKlima[5].Code[4]:=Byte_0;
203:ErrorComKlima[5].Code[5]:=Byte_0;
204:ErrorComKlima[5].Code[6]:=Byte_0;
205:ErrorComKlima[5].Code[7]:=Byte_0;
206:ErrorComKlima[5].Code[8]:=Byte_0;
207:ErrorComKlima[5].Code[9]:=Byte_0;
208:ErrorComKlima[6].Code[0]:=Byte_0;
209:ErrorComKlima[6].Code[10]:=Byte_0;
210:ErrorComKlima[6].Code[11]:=Byte_0;
211:ErrorComKlima[6].Code[12]:=Byte_0;
212:ErrorComKlima[6].Code[13]:=Byte_0;
213:ErrorComKlima[6].Code[14]:=Byte_0;
214:ErrorComKlima[6].Code[15]:=Byte_0;
215:ErrorComKlima[6].Code[1]:=Byte_0;
216:ErrorComKlima[6].Code[2]:=Byte_0;
217:ErrorComKlima[6].Code[3]:=Byte_0;
218:ErrorComKlima[6].Code[4]:=Byte_0;
219:ErrorComKlima[6].Code[5]:=Byte_0;
220:ErrorComKlima[6].Code[6]:=Byte_0;
221:ErrorComKlima[6].Code[7]:=Byte_0;
222:ErrorComKlima[6].Code[8]:=Byte_0;
223:ErrorComKlima[6].Code[9]:=Byte_0;
224:ErrorComPMM[1].Code[0]:=Byte_0;
225:ErrorComPMM[1].Code[10]:=Byte_0;
226:ErrorComPMM[1].Code[11]:=Byte_0;
227:ErrorComPMM[1].Code[12]:=Byte_0;
228:ErrorComPMM[1].Code[13]:=Byte_0;
229:ErrorComPMM[1].Code[14]:=Byte_0;
230:ErrorComPMM[1].Code[15]:=Byte_0;
231:ErrorComPMM[1].Code[1]:=Byte_0;
232:ErrorComPMM[1].Code[2]:=Byte_0;
233:ErrorComPMM[1].Code[3]:=Byte_0;
234:ErrorComPMM[1].Code[4]:=Byte_0;
235:ErrorComPMM[1].Code[5]:=Byte_0;
236:ErrorComPMM[1].Code[6]:=Byte_0;
237:ErrorComPMM[1].Code[7]:=Byte_0;
238:ErrorComPMM[1].Code[8]:=Byte_0;
239:ErrorComPMM[1].Code[9]:=Byte_0;
240:ErrorComPMM[2].Code[0]:=Byte_0;
241:ErrorComPMM[2].Code[10]:=Byte_0;
242:ErrorComPMM[2].Code[11]:=Byte_0;
243:ErrorComPMM[2].Code[12]:=Byte_0;
244:ErrorComPMM[2].Code[13]:=Byte_0;
245:ErrorComPMM[2].Code[14]:=Byte_0;
246:ErrorComPMM[2].Code[15]:=Byte_0;
247:ErrorComPMM[2].Code[1]:=Byte_0;
248:ErrorComPMM[2].Code[2]:=Byte_0;
249:ErrorComPMM[2].Code[3]:=Byte_0;
250:ErrorComPMM[2].Code[4]:=Byte_0;
251:ErrorComPMM[2].Code[5]:=Byte_0;
252:ErrorComPMM[2].Code[6]:=Byte_0;
253:ErrorComPMM[2].Code[7]:=Byte_0;
254:ErrorComPMM[2].Code[8]:=Byte_0;
255:ErrorComPMM[2].Code[9]:=Byte_0;
256:kom_nast_cas_izpada:=Word_01;
(*Pisanje UINT*)
(**)
;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
(*Modbus Slave Example*)
PROGRAM PLC_PRG_modnet
VAR
Slave_Adresa:BYTE:=2;
Slave_Port:INT:=502;
SlaveSetup:MBS_Setup;
SlavePoll:MBS_Poll;
SlaveAnswer:MBS_Answer;
step: USINT;
end :BOOL;
i: INT;
cycle :BOOL := FALSE; (* First cycle *)
OpenDefaultPort: BOOL;
Write_16: BOOL;
Write_15: BOOL;
Write_5: BOOL;
j: INT;
slavepollwOffset_temp: INT;
slaveanswerwCount_temp: INT;
slaveanswerwoffset_temp: INT;
END_VAR
(* @END_DECLARATION := '0' *)
(*Modbus Slave Example*)
IF Write_16=TRUE THEN (**)
FOR j := 0 TO (slaveanswerwCount_temp-1)/15 BY 1 DO (*vpiše se dword, real*)
wStr_0:=mind[slaveanswerwoffset_temp+j];
wStr_1:=mind[slaveanswerwoffset_temp+j+1];
wStr_2 :=mind[slaveanswerwoffset_temp+j+2];
wStr_3:=mind[slaveanswerwoffset_temp+j+3];
wStr_4:=mind[slaveanswerwoffset_temp+j+4];
wStr_5 :=mind[slaveanswerwoffset_temp+j+5];
wStr_6:=mind[slaveanswerwoffset_temp+j+6];
wStr_7:=mind[slaveanswerwoffset_temp+j+7];
wStr_8:=mind[slaveanswerwoffset_temp+j+8];
wStr_9:=mind[slaveanswerwoffset_temp+j+9];
wStr_10:=mind[slaveanswerwoffset_temp+j+10];
wStr_11:=mind[slaveanswerwoffset_temp+j+11];
wStr_12:=mind[slaveanswerwoffset_temp+j+12];
wStr_13:=mind[slaveanswerwoffset_temp+j+13];
wStr_14:=mind[slaveanswerwoffset_temp+j+14];
bStr_29:=0;
mod_Write_String(index:=slaveanswerwoffset_temp+j); (*vpis real in string*)
END_FOR;
FOR j := 1 TO slaveanswerwCount_temp-1 BY 2 DO (*vpiše se dword, real*)
Word_01:=mind[slaveanswerwoffset_temp+j-1];
Word_23:=mind[slaveanswerwoffset_temp+j];
mod_Write_dWord(index:=slaveanswerwoffset_temp+j); (*vpis real in dword*)
END_FOR;
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO (*vpiše se word*)
Word_01:=mind[slaveanswerwoffset_temp+j];
mod_Write_Word(index:=slaveanswerwoffset_temp+j); (*vpis word*)
END_FOR;
Write_16:=FALSE;
END_IF;
IF Write_5=TRUE OR Write_15=TRUE THEN (**)
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO
Bit_0:=mind_bool[slaveanswerwoffset_temp+j];
mod_Write_Bool(index:=slaveanswerwoffset_temp+j); (*vpis spremembe v spremenljivko*)
END_FOR;
Write_5:=FALSE;
Write_15:=FALSE;
END_IF;
(*iz scade ni komande za branje*)
IF Write_16=FALSE AND Write_5=FALSE AND Write_15=FALSE THEN
mod_Read();(*branje spremenljivk za scado*)
END_IF
(*Close all sockets on corresponding event*)
IF cycle = FALSE THEN
SysCallbackRegister(INDEXOF(Callback_Stop),event_stop);
SysCallbackRegister(INDEXOF(Callback_Reset),event_before_reset);
SysCallbackRegister(INDEXOF(Callback_Reset),event_shutdown);
cycle := TRUE;
END_IF
(*Close all connections via application *)
IF end = TRUE THEN
MBS_CloseAllConnections();
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=FALSE); (*Close port*)
step := 0;
END_IF
IF OpenDefaultPort=TRUE THEN
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=TRUE); (*Close port*)
step := 0;
OpenDefaultPort:=FALSE;
END_IF
(* State machine for setup, poll and answer *)
CASE step OF
0:(**)
SlaveSetup.bUnitIdentifier:=Slave_Adresa;(*Subunitnumber*)
slavesetup.wDefaultPort:=Slave_Port;(*Standartport *)
SlaveSetup.xAdditionalPortActive:=FALSE;(*Port opened or closed*)
SlaveSetup.xSecureMode:=FALSE;(*If TRUE only preset IPs are accepted*)
SlaveSetup.tTimeout:=T#3m;(*Timeout if no communication with slave established*)
SlaveSetup(xStrobe:=TRUE);(*Strobe starts function*)
IF slavesetup.xBusy = FALSE THEN
slavesetup(xstrobe := FALSE);
step := 1 ;
END_IF;
1:(**)
SlavePoll(xStrobe:=TRUE);(*Searching for master commands*)
IF NOT SlavePoll.xBusy THEN
step:=2;
SlavePoll(xStrobe:=FALSE);
END_IF;
2:(**)
step:= 1;
CASE SlavePoll.bFunctionCode OF (*Connect accepted pollparameters with answerparameters*)
8:(**)(*Poll answers*)
;
15:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind_bool[slaveanswer.woffset+i] := slavepoll.xarData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.xarData:=slavepoll.xarData;
Write_15:=TRUE;
16:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind[slaveanswer.woffset+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.wardata := slavepoll.warData;
Write_16:=TRUE;
1,2:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slavepoll.wcount-1 BY 1 DO
slaveanswer.xarData[i]:=mind_bool[slavepoll.woffset+i]; (*Read from Data-array*)
END_FOR
3,4:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slaveanswer.wCount-1 BY 1 DO
slaveanswer.warData[i]:=mind[slavepoll.woffset+i];(*Read from Data-array*)
END_FOR
5:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
mind_bool[slavepoll.woffset]:=slavepoll.xarData[0];(*Write to Data-array*)
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.xarData := slavepoll.xardata;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
Write_5:=TRUE;
6:
slaveanswer.bFunctionCode:= slavepoll.bFunctionCode;
mind[slavepoll.woffset]:= slavepoll.warData[0];(*Write to Data-array*)
slaveanswer.wOffset:= slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wardata := slavepoll.wardata;
23:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
FOR i:= 0 TO slavepoll.wCountAdd-1 BY 1 DO
mind[slavepoll.woffsetadd+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
FOR i := 0 TO slavepoll.wCount BY 1 DO
slaveanswer.warData[i] := mind[1+slavepoll.woffset+i];(*Read from Data-array*)
END_FOR;
END_CASE;
IF slavepoll.xAvailable = TRUE THEN
slaveanswer();(*When Data ready, send answer*)
END_IF
END_CASE;
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_dWord : BOOL
VAR_INPUT
dVAR: DWORD;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
DWord_0:=dVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_Real : BOOL
VAR_INPUT
rVAR: REAL;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
Real_0:=rVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_String : BOOL
VAR_INPUT
sVar: STRING;
start:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
String_0:=LEFT (sVar,29);
mind[start]:=wStr_0;
mind[start+1]:=wStr_1;
mind[start+2]:=wStr_2;
mind[start+3]:=wStr_3;
mind[start+4]:=wStr_4;
mind[start+5]:=wStr_5;
mind[start+6]:=wStr_6;
mind[start+7]:=wStr_7;
mind[start+8]:=wStr_8;
mind[start+9]:=wStr_9;
mind[start+10]:=wStr_10;
mind[start+11]:=wStr_11;
mind[start+12]:=wStr_12;
mind[start+13]:=wStr_13;
bStr_29:=0;
mind[start+14]:=wStr_14;
END_FUNCTION
(* @GLOBAL_VARIABLE_LIST := 'Global_Variables_Modnet' *)
(* @PATH := '' *)
(* @SYMFILEFLAGS := '2048' *)
VAR_GLOBAL
(*delovno polje za modnet komunikacijo*)
mind :ARRAY [0..9999] OF WORD;
mind_bool :ARRAY [0..9999] OF BOOL; (*Buffer-Array*)
(*Delovni markerji //*)
Bit_0 AT %MX0.0 : BOOL;
Byte_0 AT %MB0 : BYTE;
Byte_1 AT %MB1 : BYTE;
Byte_2 AT %MB2 : BYTE;
Byte_3 AT %MB3 : BYTE;
Real_0 AT %MR0:REAL;
DWord_0 AT %MD0:DWORD;
Word_01 AT %MW0:WORD;
Word_23 AT %MW2:WORD;
String_0 AT %MW10:STRING;
wStr_0 AT %MW10:WORD;
wStr_1 AT %MW12:WORD;
wStr_2 AT %MW14:WORD;
wStr_3 AT %MW16:WORD;
wStr_4 AT %MW18:WORD;
wStr_5 AT %MW20:WORD;
wStr_6 AT %MW22:WORD;
wStr_7 AT %MW24:WORD;
wStr_8 AT %MW26:WORD;
wStr_9 AT %MW28:WORD;
wStr_10 AT %MW30:WORD;
wStr_11 AT %MW32:WORD;
wStr_12 AT %MW34:WORD;
wStr_13 AT %MW36:WORD;
wStr_14 AT %MW38:WORD;
bStr_00 AT %MB10:BYTE;
bStr_01 AT %MB11:BYTE;
bStr_02 AT %MB12:BYTE;
bStr_03 AT %MB13:BYTE;
bStr_04 AT %MB14:BYTE;
bStr_05 AT %MB15:BYTE;
bStr_06 AT %MB16:BYTE;
bStr_07 AT %MB17:BYTE;
bStr_08 AT %MB18:BYTE;
bStr_09 AT %MB19:BYTE;
bStr_10 AT %MB20:BYTE;
bStr_11 AT %MB21:BYTE;
bStr_12 AT %MB22:BYTE;
bStr_13 AT %MB23:BYTE;
bStr_14 AT %MB24:BYTE;
bStr_15 AT %MB25:BYTE;
bStr_16 AT %MB26:BYTE;
bStr_17 AT %MB27:BYTE;
bStr_18 AT %MB28:BYTE;
bStr_19 AT %MB29:BYTE;
bStr_20 AT %MB30:BYTE;
bStr_21 AT %MB31:BYTE;
bStr_22 AT %MB32:BYTE;
bStr_23 AT %MB33:BYTE;
bStr_24 AT %MB34:BYTE;
bStr_25 AT %MB35:BYTE;
bStr_26 AT %MB36:BYTE;
bStr_27 AT %MB37:BYTE;
bStr_28 AT %MB38:BYTE;
bStr_29 AT %MB39:BYTE;
(********************************************)
END_VAR
(* @OBJECT_END := 'Global_Variables_Modnet' *)
(* @CONNECTIONS := Global_Variables_Modnet
FILENAME : ''
FILETIME : 0
EXPORT : 0
NUMOFCONNECTIONS : 0
*)
(*KONEC_KODA*)