## Prva stran
variable | 691 | 1.KORAK | variable_1 | 2.KORAK | KORAKI!
Device name | Tip | število spremenljivk | Tip (izbrani) | Zamenjaj z | 1.V Sheet "variable" skopiraj vsebino iz variable.dbf - iz Citect SCAD-a projekta, ki ga želiš pretvoriti.
IOD_SS3 | BCD | 0 | BCD | INT | 2.V polje A3 vpiši Device ime spremenljivk ki se bodo prenašale preko Modnet protokola
| BYTE | 88 | BYTE | BYTE | 3.V polje A6 vpiši ime krmilnika (npr.:PLC1, če je adresa v spremenljivkah PLC1:.NapakaKoncnega_stikala, drugače pusti polje prazno)
OPC name | DIGITAL | 297 | DIGITAL | DIGITAL | 4. Pritisni gumb 1.KORAK (V poljih C3:C10 se izpiše število spremenljivk, ki imajo Device enak tistemu v polju A3)
SS3 | INT | 8 | INT | INT | 5. Pritisni gumb 2.KORAK (V Sheet-u variable_1 se naredi seznam spremenljivk, ki se bodo prenačale preko Modnet protokola)
| LONG | 0 | LONG | LONG | 6. Pritisni gumb 3.KORAK (V poljih C15:C24 se izpiše število spremnljiv po tipih, v poljih F15:F24 se izpiše število potrebni wordow/coilov za prenos spremnljivk)
| REAL | 49 | REAL | REAL | 7. 4.KORAK: V polja C29:C38 je potrebno ročno vpisati začetne naslove spremnljivk. Potrebno je paziti na:
| STRING | 5 | UINT | UINT | *naslov se morajo začeti z lihim številom npr.:1, 101, 551
| UINT | 0 | STRING | STRING | *naslove je potrebno nastaviti tako, da se naslovi sremenljivk ne more prekrivati (naslovi spremenjivk gredo od (začetnega naslova) do (začetnega naslova+število potrebnih wordow))
8. Pritisni gumb 5.KORAK (V Sheet-u variable_2 se naredi seznam spremenljivk, ki so tokrat sortirana po tipih)
9. Pritisni gumb 6.KORAK (V Sheet-u variable_3 se naredi seznam spremenljivk, katerih Device se zamenja z devicom v polju C41)
Trajanje makroja | variable_1 |  |  | 3.KORAK | 10. Pritisni gumb 7.KORAK (V Sheet-u variable_new se generira seznam spremenljivk. To vsebino je potrebno skopirati v variable.dbf)
0 | Tip | število spremenljivk | TIP | št.potrebnih coilov/wordov | *ta korak traja nekoliko dalj časa (odvisno od števila spremenljivk)
| BCD | 0 | BCD | 0 | *če se pojavi težava z adresami ki se začnejo z 0000 (npr.: "00001" se spremeni na "1") je potrebno uporabiti priloženo (prazno) variable.dbf ali v
| BYTE | 0 | BYTE | 0 | ProjectEditoju/VariableTags na poljubni spremenljki nastaviti adreso" 00001"
| DIGITAL | 297 | DIGITAL | 297 (Coil) | 11. Pritisni gumb 8.KORAK in 9.KORAK (V Sheet-u Xsoft se generira koda)
| INT | 96 | INT | 96 (word) | 12. S pritiskom na gumb 10.KORAK se zgenerira EXP koda za Xsoft (Xsoft_EXP)
| LONG | 0 | LONG | 0 (word) | 13. S pritiskom na gumb Save*.EXP se avtomatsko generira datoka *.EXP
| REAL | 49 | REAL | 98 (word)
| STRING | 5 | STRING | 75 (word)
| UINT | 0 | UINT | 0 (word)
POZOR!
*V Sheet-u variable mora biti vsebina skopirana od polja A1 naprej (če je katera vrstica prazna makroji ne bodo delovali pravilno)
*Ena "STRING" spremenljivka zasede 15wordow (to pomeni 29 znakov, 1BYTE=1STRING)
|  | 4.KORAK(vpiši ročno) | variable_2 | 5.KORAK | *Dolžina "STRING" spremenljivk je 29 znakov (lahko tudi več vendar ne z uporabno tega dokumenta in XSoft programa,potrebna je modifikacija makrojev in Xsoft programa)
| Tip | Začetni naslov |  | Sortiraj | *Vsi stringi so enake dolžine (29)
| BCD |  |  | BCD | *"BYTE" spremenljivke se v variable.dbf spremenijo v "INT" (prenašanje posameznih bytov ni mogoče, niti naslavaljanje v citectscadi)
| BYTE |  |  | DIGITAL | *Naslovi spremenljivk se morajo obvezno začeti z lihim naslovom (preizkušeno je z začetnimi naslovi, ki se izpišejo po pritisku na gumb Ponastavi)
| DIGITAL | 1 |  | BYTE | *Z pritiskom na gumb RESET se pobriše vsebina vseh Sheet-ov razen Sheet-a variable (makor reset se izvaja precej časa)
| INT | 1 |  | INT | *makroji ne delujejo pravilno,če je v Sheet-u variable več kot 9999 vrstic oz. spremenljivk (število vseh spremnljivk je prikazano v polju B1)
| LONG | 3001 |  | LONG | *če se vsebine iz variable_new ne gre skpirat v variable.dbf datotek, vsebino skopirajte najprej v *.txt datoteko in nato v variable.dbf
| REAL | 4001 |  | REAL | *v polju A14 na Sheet-u Prva stran se prikazuje število ciklop do konca izvedbe makroja (samo za gumb 7.KORAK)
| STRING | 5001 |  | STRING
| UINT | 6001 |  | UINT
| variable_3 | 6.KORAK | variable_new | 7.KORAK
| New Device name | IOD_SS3_TCP |  | Nova variable dbf
|  |  | xSoft | 8.KORAK in 9.KORAK
xSoft koda
xSoft_EXP
Izvoz*.EXP
1.KORAK
2.KORAK
3.KORAK
5.KORAK
6.KORAK
7.KORAK
8.KORAK
9.KORAK
RESET
Ponastavi
10.KORAK
Save*.EXP

## variable
SS3Pulzi1s | DIGITAL | IOD_SS3_disk | D1 | [8 empty] | 0x06400010
ASS3_omogoci_sms | DIGITAL | IOD_SS3_disk | D202[200] | [8 empty] | 0x06400020
BSS3_omogoci_sms | DIGITAL | IOD_SS3_disk | D402[200] | [8 empty] | 0x06400030
CSS3_omogoci_sms | DIGITAL | IOD_SS3_disk | D602[200] | [8 empty] | 0x06400040
DSS3_omogoci_sms | DIGITAL | IOD_SS3_disk | D802[200] | [8 empty] | 0x06400050
ESS3_omogoci_sms | DIGITAL | IOD_SS3_disk | D1002[200] | [8 empty] | 0x06400060
FSS3_omogoci_sms | DIGITAL | IOD_SS3_disk | D1202[200] | [8 empty] | 0x06400070
SS3AlarmKlimat1_Napaka_Om | DIGITAL | IOD_SS3_disk | D1402 | [8 empty] | 0x06400080
SS3AlarmKlimat2_Napaka_Om | DIGITAL | IOD_SS3_disk | D1403 | [8 empty] | 0x06400090
SS3AlarmKlimat3_Napaka_Om | DIGITAL | IOD_SS3_disk | D1404 | [8 empty] | 0x064000a0
SS3AlarmKlimat4_Napaka_Om | DIGITAL | IOD_SS3_disk | D1405 | [8 empty] | 0x064000b0
SS3NapakaSenzorTemp1_Om | DIGITAL | IOD_SS3_disk | D1406 | [8 empty] | 0x064000c0
SS3NapakaSenzorTemp2_Om | DIGITAL | IOD_SS3_disk | D1407 | [8 empty] | 0x064000d0
SS3NapakaSenzorTemp3_Om | DIGITAL | IOD_SS3_disk | D1408 | [8 empty] | 0x064000e0
SS3NapakaSenzorVlaga1_Om | DIGITAL | IOD_SS3_disk | D1409 | [8 empty] | 0x064000f0
SS3NapakaSenzorVlaga2_Om | DIGITAL | IOD_SS3_disk | D1410 | [8 empty] | 0x06400100
SS3NapakaSenzorVlaga3_Om | DIGITAL | IOD_SS3_disk | D1411 | [8 empty] | 0x06400110
SS3OpozoriloBaterijaPLC_Om | DIGITAL | IOD_SS3_disk | D1412 | [8 empty] | 0x06400120
SS3AlarmUPSKrmOmara_Alarm_Om | DIGITAL | IOD_SS3_disk | D1413 | [8 empty] | 0x06400130
SS3StanjeUPSKrmOmara_BaterijskiNacin_Om | DIGITAL | IOD_SS3_disk | D1414 | [8 empty] | 0x06400140
SS3StanjeUPSKrmOmara_Polnenje_Om | DIGITAL | IOD_SS3_disk | D1415 | [8 empty] | 0x06400150
SS3AlarmLAH1_RazlitjeVode_Om | DIGITAL | IOD_SS3_disk | D1416 | [8 empty] | 0x06400160
SS3AlarmLAH2_RazlitjeVode_Om | DIGITAL | IOD_SS3_disk | D1417 | [8 empty] | 0x06400170
SS3ErrComPort2_Om | DIGITAL | IOD_SS3_disk | D1418 | [8 empty] | 0x06400180
SS3ErrComPanelPLC_Om | DIGITAL | IOD_SS3_disk | D1419 | [8 empty] | 0x06400190
SS3ErrComSCADA_Om | DIGITAL | IOD_SS3_disk | D1420 | [8 empty] | 0x064001a0
SS3ErrComKlima1_Om | DIGITAL | IOD_SS3_disk | D1421 | [8 empty] | 0x064001b0
SS3ErrComKlima2_Om | DIGITAL | IOD_SS3_disk | D1422 | [8 empty] | 0x064001c0
SS3ErrComKlima3_Om | DIGITAL | IOD_SS3_disk | D1423 | [8 empty] | 0x064001d0
SS3ErrComKlima4_Om | DIGITAL | IOD_SS3_disk | D1424 | [8 empty] | 0x064001e0
SS3KlimaError1AlarmKompresor1_Om | DIGITAL | IOD_SS3_disk | D1425 | [8 empty] | 0x064001f0
SS3KlimaError1AlarmKompresor2_Om | DIGITAL | IOD_SS3_disk | D1426 | [8 empty] | 0x06400200
SS3KlimaError1NizekPritiskKompresor1_Om | DIGITAL | IOD_SS3_disk | D1427 | [8 empty] | 0x06400210
SS3KlimaError1NizekPritiskKompresor2_Om | DIGITAL | IOD_SS3_disk | D1428 | [8 empty] | 0x06400220
SS3KlimaError1NapakaPriPretokuZraka_Om | DIGITAL | IOD_SS3_disk | D1429 | [8 empty] | 0x06400230
SS3KlimaError1FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1430 | [8 empty] | 0x06400240
SS3KlimaError1ThermalCutoutHeater1_Om | DIGITAL | IOD_SS3_disk | D1431 | [8 empty] | 0x06400250
SS3KlimaError1ThermalCutoutHeater2_Om | DIGITAL | IOD_SS3_disk | D1432 | [8 empty] | 0x06400260
SS3KlimaError1PozarniAlarm_Om | DIGITAL | IOD_SS3_disk | D1433 | [8 empty] | 0x06400270
SS3KlimaError1ZamasenFilter_Om | DIGITAL | IOD_SS3_disk | D1434 | [8 empty] | 0x06400280
SS3KlimaError1VisokaTempVProstoru_Om | DIGITAL | IOD_SS3_disk | D1435 | [8 empty] | 0x06400290
SS3KlimaError1NizkaTempVProstoru_Om | DIGITAL | IOD_SS3_disk | D1436 | [8 empty] | 0x064002a0
SS3KlimaError1VisokaVlaznost_Om | DIGITAL | IOD_SS3_disk | D1437 | [8 empty] | 0x064002b0
SS3KlimaError1NizkaVlaznost_Om | DIGITAL | IOD_SS3_disk | D1438 | [8 empty] | 0x064002c0
SS3KlimaError1Kompresor1naMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1439 | [8 empty] | 0x064002d0
SS3KlimaError1Kompresor2naMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1440 | [8 empty] | 0x064002e0
SS3KlimaError1VentilatorNaMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1441 | [8 empty] | 0x064002f0
SS3KlimaError1NapakaTSTemperaturaProstora_Om | DIGITAL | IOD_SS3_disk | D1442 | [8 empty] | 0x06400300
SS3KlimaError1NapakaSenzorVlaznosti_Om | DIGITAL | IOD_SS3_disk | D1443 | [8 empty] | 0x06400310
SS3KlimaError1NapakaSenzorPritiska_Om | DIGITAL | IOD_SS3_disk | D1444 | [8 empty] | 0x06400320
SS3KlimaError1VisokTokVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1445 | [8 empty] | 0x06400330
SS3KlimaError1NiVodeVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1446 | [8 empty] | 0x06400340
SS3KlimaError1NiTokaVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1447 | [8 empty] | 0x06400350
SS3KlimaError1VisokPritiskVKrogu1_Om | DIGITAL | IOD_SS3_disk | D1448 | [8 empty] | 0x06400360
SS3KlimaError1VisokPritiskVKrogu2_Om | DIGITAL | IOD_SS3_disk | D1449 | [8 empty] | 0x06400370
SS3KlimaError1IzlivVode_Om | DIGITAL | IOD_SS3_disk | D1450 | [8 empty] | 0x06400380
SS3KlimaError1TermZascInVisokPritiskKompr1_Om | DIGITAL | IOD_SS3_disk | D1451 | [8 empty] | 0x06400390
SS3KlimaError1VlazilecnaMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1452 | [8 empty] | 0x064003a0
SS3KlimaError1TermZascInVisokPritiskKompr2_Om | DIGITAL | IOD_SS3_disk | D1453 | [8 empty] | 0x064003b0
SS3KlimaError1NapakaPriPretokuVode_Om | DIGITAL | IOD_SS3_disk | D1454 | [8 empty] | 0x064003c0
SS3KlimaError1Kond1FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1455 | [8 empty] | 0x064003d0
SS3KlimaError1Kond2FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1456 | [8 empty] | 0x064003e0
SS3KlimaError1ZunanjiAlarm_Om | DIGITAL | IOD_SS3_disk | D1457 | [8 empty] | 0x064003f0
SS3KlimaError1FaultyEprom_Om | DIGITAL | IOD_SS3_disk | D1458 | [8 empty] | 0x06400400
SS3KlimaError1NapakaSenzorTempIzpiha_Om | DIGITAL | IOD_SS3_disk | D1459 | [8 empty] | 0x06400410
SS3KlimaError1NapakaSenzorTempProstora_Om | DIGITAL | IOD_SS3_disk | D1460 | [8 empty] | 0x06400420
SS3KlimaError1NapakaSenzorZunanjeTemp_Om | DIGITAL | IOD_SS3_disk | D1461 | [8 empty] | 0x06400430
SS3KlimaError1NizkaTempPovratneVode_Om | DIGITAL | IOD_SS3_disk | D1462 | [8 empty] | 0x06400440
SS3KlimaError1StoppedByAlarms_Om | DIGITAL | IOD_SS3_disk | D1463 | [8 empty] | 0x06400450
SS3KlimaError1VisokaTempPovratneVode_Om | DIGITAL | IOD_SS3_disk | D1464 | [8 empty] | 0x06400460
SS3KlimaError1GeneralAlarm_Om | DIGITAL | IOD_SS3_disk | D1465 | [8 empty] | 0x06400470
SS3KlimaError1NapakaSenzorPovratVode_Om | DIGITAL | IOD_SS3_disk | D1466 | [8 empty] | 0x06400480
SS3KlimaError2AlarmKompresor1_Om | DIGITAL | IOD_SS3_disk | D1467 | [8 empty] | 0x06400490
SS3KlimaError2AlarmKompresor2_Om | DIGITAL | IOD_SS3_disk | D1468 | [8 empty] | 0x064004a0
SS3KlimaError2NizekPritiskKompresor1_Om | DIGITAL | IOD_SS3_disk | D1469 | [8 empty] | 0x064004b0
SS3KlimaError2NizekPritiskKompresor2_Om | DIGITAL | IOD_SS3_disk | D1470 | [8 empty] | 0x064004c0
SS3KlimaError2NapakaPriPretokuZraka_Om | DIGITAL | IOD_SS3_disk | D1471 | [8 empty] | 0x064004d0
SS3KlimaError2FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1472 | [8 empty] | 0x064004e0
SS3KlimaError2ThermalCutoutHeater1_Om | DIGITAL | IOD_SS3_disk | D1473 | [8 empty] | 0x064004f0
SS3KlimaError2ThermalCutoutHeater2_Om | DIGITAL | IOD_SS3_disk | D1474 | [8 empty] | 0x06400500
SS3KlimaError2PozarniAlarm_Om | DIGITAL | IOD_SS3_disk | D1475 | [8 empty] | 0x06400510
SS3KlimaError2ZamasenFilter_Om | DIGITAL | IOD_SS3_disk | D1476 | [8 empty] | 0x06400520
SS3KlimaError2VisokaTempVProstoru_Om | DIGITAL | IOD_SS3_disk | D1477 | [8 empty] | 0x06400530
SS3KlimaError2NizkaTempVProstoru_Om | DIGITAL | IOD_SS3_disk | D1478 | [8 empty] | 0x06400540
SS3KlimaError2VisokaVlaznost_Om | DIGITAL | IOD_SS3_disk | D1479 | [8 empty] | 0x06400550
SS3KlimaError2NizkaVlaznost_Om | DIGITAL | IOD_SS3_disk | D1480 | [8 empty] | 0x06400560
SS3KlimaError2Kompresor1naMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1481 | [8 empty] | 0x06400570
SS3KlimaError2Kompresor2naMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1482 | [8 empty] | 0x06400580
SS3KlimaError2VentilatorNaMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1483 | [8 empty] | 0x06400590
SS3KlimaError2NapakaTSTemperaturaProstora_Om | DIGITAL | IOD_SS3_disk | D1484 | [8 empty] | 0x064005a0
SS3KlimaError2NapakaSenzorVlaznosti_Om | DIGITAL | IOD_SS3_disk | D1485 | [8 empty] | 0x064005b0
SS3KlimaError2NapakaSenzorPritiska_Om | DIGITAL | IOD_SS3_disk | D1486 | [8 empty] | 0x064005c0
SS3KlimaError2VisokTokVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1487 | [8 empty] | 0x064005d0
SS3KlimaError2NiVodeVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1488 | [8 empty] | 0x064005e0
SS3KlimaError2NiTokaVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1489 | [8 empty] | 0x064005f0
SS3KlimaError2VisokPritiskVKrogu1_Om | DIGITAL | IOD_SS3_disk | D1490 | [8 empty] | 0x06400600
SS3KlimaError2VisokPritiskVKrogu2_Om | DIGITAL | IOD_SS3_disk | D1491 | [8 empty] | 0x06400610
SS3KlimaError2IzlivVode_Om | DIGITAL | IOD_SS3_disk | D1492 | [8 empty] | 0x06400620
SS3KlimaError2TermZascInVisokPritiskKompr1_Om | DIGITAL | IOD_SS3_disk | D1493 | [8 empty] | 0x06400630
SS3KlimaError2VlazilecnaMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1494 | [8 empty] | 0x06400640
SS3KlimaError2TermZascInVisokPritiskKompr2_Om | DIGITAL | IOD_SS3_disk | D1495 | [8 empty] | 0x06400650
SS3KlimaError2NapakaPriPretokuVode_Om | DIGITAL | IOD_SS3_disk | D1496 | [8 empty] | 0x06400660
SS3KlimaError2Kond1FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1497 | [8 empty] | 0x06400670
SS3KlimaError2Kond2FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1498 | [8 empty] | 0x06400680
SS3KlimaError2ZunanjiAlarm_Om | DIGITAL | IOD_SS3_disk | D1499 | [8 empty] | 0x06400690
SS3KlimaError2FaultyEprom_Om | DIGITAL | IOD_SS3_disk | D1500 | [8 empty] | 0x064006a0
SS3KlimaError2NapakaSenzorTempIzpiha_Om | DIGITAL | IOD_SS3_disk | D1501 | [8 empty] | 0x064006b0
SS3KlimaError2NapakaSenzorTempProstora_Om | DIGITAL | IOD_SS3_disk | D1502 | [8 empty] | 0x064006c0
SS3KlimaError2NapakaSenzorZunanjeTemp_Om | DIGITAL | IOD_SS3_disk | D1503 | [8 empty] | 0x064006d0
SS3KlimaError2NizkaTempPovratneVode_Om | DIGITAL | IOD_SS3_disk | D1504 | [8 empty] | 0x064006e0
SS3KlimaError2StoppedByAlarms_Om | DIGITAL | IOD_SS3_disk | D1505 | [8 empty] | 0x064006f0
SS3KlimaError2VisokaTempPovratneVode_Om | DIGITAL | IOD_SS3_disk | D1506 | [8 empty] | 0x06400700
SS3KlimaError2GeneralAlarm_Om | DIGITAL | IOD_SS3_disk | D1507 | [8 empty] | 0x06400710
SS3KlimaError2NapakaSenzorPovratVode_Om | DIGITAL | IOD_SS3_disk | D1508 | [8 empty] | 0x06400720
SS3KlimaError3AlarmKompresor1_Om | DIGITAL | IOD_SS3_disk | D1509 | [8 empty] | 0x06400730
SS3KlimaError3AlarmKompresor2_Om | DIGITAL | IOD_SS3_disk | D1510 | [8 empty] | 0x06400740
SS3KlimaError3NizekPritiskKompresor1_Om | DIGITAL | IOD_SS3_disk | D1511 | [8 empty] | 0x06400750
SS3KlimaError3NizekPritiskKompresor2_Om | DIGITAL | IOD_SS3_disk | D1512 | [8 empty] | 0x06400760
SS3KlimaError3NapakaPriPretokuZraka_Om | DIGITAL | IOD_SS3_disk | D1513 | [8 empty] | 0x06400770
SS3KlimaError3FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1514 | [8 empty] | 0x06400780
SS3KlimaError3ThermalCutoutHeater1_Om | DIGITAL | IOD_SS3_disk | D1515 | [8 empty] | 0x06400790
SS3KlimaError3ThermalCutoutHeater2_Om | DIGITAL | IOD_SS3_disk | D1516 | [8 empty] | 0x064007a0
SS3KlimaError3PozarniAlarm_Om | DIGITAL | IOD_SS3_disk | D1517 | [8 empty] | 0x064007b0
SS3KlimaError3ZamasenFilter_Om | DIGITAL | IOD_SS3_disk | D1518 | [8 empty] | 0x064007c0
SS3KlimaError3VisokaTempVProstoru_Om | DIGITAL | IOD_SS3_disk | D1519 | [8 empty] | 0x064007d0
SS3KlimaError3NizkaTempVProstoru_Om | DIGITAL | IOD_SS3_disk | D1520 | [8 empty] | 0x064007e0
SS3KlimaError3VisokaVlaznost_Om | DIGITAL | IOD_SS3_disk | D1521 | [8 empty] | 0x064007f0
SS3KlimaError3NizkaVlaznost_Om | DIGITAL | IOD_SS3_disk | D1522 | [8 empty] | 0x06400800
SS3KlimaError3Kompresor1naMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1523 | [8 empty] | 0x06400810
SS3KlimaError3Kompresor2naMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1524 | [8 empty] | 0x06400820
SS3KlimaError3VentilatorNaMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1525 | [8 empty] | 0x06400830
SS3KlimaError3NapakaTSTemperaturaProstora_Om | DIGITAL | IOD_SS3_disk | D1526 | [8 empty] | 0x06400840
SS3KlimaError3NapakaSenzorVlaznosti_Om | DIGITAL | IOD_SS3_disk | D1527 | [8 empty] | 0x06400850
SS3KlimaError3NapakaSenzorPritiska_Om | DIGITAL | IOD_SS3_disk | D1528 | [8 empty] | 0x06400860
SS3KlimaError3VisokTokVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1529 | [8 empty] | 0x06400870
SS3KlimaError3NiVodeVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1530 | [8 empty] | 0x06400880
SS3KlimaError3NiTokaVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1531 | [8 empty] | 0x06400890
SS3KlimaError3VisokPritiskVKrogu1_Om | DIGITAL | IOD_SS3_disk | D1532 | [8 empty] | 0x064008a0
SS3KlimaError3VisokPritiskVKrogu2_Om | DIGITAL | IOD_SS3_disk | D1533 | [8 empty] | 0x064008b0
SS3KlimaError3IzlivVode_Om | DIGITAL | IOD_SS3_disk | D1534 | [8 empty] | 0x064008c0
SS3KlimaError3TermZascInVisokPritiskKompr1_Om | DIGITAL | IOD_SS3_disk | D1535 | [8 empty] | 0x064008d0
SS3KlimaError3VlazilecnaMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1536 | [8 empty] | 0x064008e0
SS3KlimaError3TermZascInVisokPritiskKompr2_Om | DIGITAL | IOD_SS3_disk | D1537 | [8 empty] | 0x064008f0
SS3KlimaError3NapakaPriPretokuVode_Om | DIGITAL | IOD_SS3_disk | D1538 | [8 empty] | 0x06400900
SS3KlimaError3Kond1FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1539 | [8 empty] | 0x06400910
SS3KlimaError3Kond2FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1540 | [8 empty] | 0x06400920
SS3KlimaError3ZunanjiAlarm_Om | DIGITAL | IOD_SS3_disk | D1541 | [8 empty] | 0x06400930
SS3KlimaError3FaultyEprom_Om | DIGITAL | IOD_SS3_disk | D1542 | [8 empty] | 0x06400940
SS3KlimaError3NapakaSenzorTempIzpiha_Om | DIGITAL | IOD_SS3_disk | D1543 | [8 empty] | 0x06400950
SS3KlimaError3NapakaSenzorTempProstora_Om | DIGITAL | IOD_SS3_disk | D1544 | [8 empty] | 0x06400960
SS3KlimaError3NapakaSenzorZunanjeTemp_Om | DIGITAL | IOD_SS3_disk | D1545 | [8 empty] | 0x06400970
SS3KlimaError3NizkaTempPovratneVode_Om | DIGITAL | IOD_SS3_disk | D1546 | [8 empty] | 0x06400980
SS3KlimaError3StoppedByAlarms_Om | DIGITAL | IOD_SS3_disk | D1547 | [8 empty] | 0x06400990
SS3KlimaError3VisokaTempPovratneVode_Om | DIGITAL | IOD_SS3_disk | D1548 | [8 empty] | 0x064009a0
SS3KlimaError3GeneralAlarm_Om | DIGITAL | IOD_SS3_disk | D1549 | [8 empty] | 0x064009b0
SS3KlimaError3NapakaSenzorPovratVode_Om | DIGITAL | IOD_SS3_disk | D1550 | [8 empty] | 0x064009c0
SS3KlimaError4AlarmKompresor1_Om | DIGITAL | IOD_SS3_disk | D1551 | [8 empty] | 0x064009d0
SS3KlimaError4AlarmKompresor2_Om | DIGITAL | IOD_SS3_disk | D1552 | [8 empty] | 0x064009e0
SS3KlimaError4NizekPritiskKompresor1_Om | DIGITAL | IOD_SS3_disk | D1553 | [8 empty] | 0x064009f0
SS3KlimaError4NizekPritiskKompresor2_Om | DIGITAL | IOD_SS3_disk | D1554 | [8 empty] | 0x06400a00
SS3KlimaError4NapakaPriPretokuZraka_Om | DIGITAL | IOD_SS3_disk | D1555 | [8 empty] | 0x06400a10
SS3KlimaError4FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1556 | [8 empty] | 0x06400a20
SS3KlimaError4ThermalCutoutHeater1_Om | DIGITAL | IOD_SS3_disk | D1557 | [8 empty] | 0x06400a30
SS3KlimaError4ThermalCutoutHeater2_Om | DIGITAL | IOD_SS3_disk | D1558 | [8 empty] | 0x06400a40
SS3KlimaError4PozarniAlarm_Om | DIGITAL | IOD_SS3_disk | D1559 | [8 empty] | 0x06400a50
SS3KlimaError4ZamasenFilter_Om | DIGITAL | IOD_SS3_disk | D1560 | [8 empty] | 0x06400a60
SS3KlimaError4VisokaTempVProstoru_Om | DIGITAL | IOD_SS3_disk | D1561 | [8 empty] | 0x06400a70
SS3KlimaError4NizkaTempVProstoru_Om | DIGITAL | IOD_SS3_disk | D1562 | [8 empty] | 0x06400a80
SS3KlimaError4VisokaVlaznost_Om | DIGITAL | IOD_SS3_disk | D1563 | [8 empty] | 0x06400a90
SS3KlimaError4NizkaVlaznost_Om | DIGITAL | IOD_SS3_disk | D1564 | [8 empty] | 0x06400aa0
SS3KlimaError4Kompresor1naMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1565 | [8 empty] | 0x06400ab0
SS3KlimaError4Kompresor2naMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1566 | [8 empty] | 0x06400ac0
SS3KlimaError4VentilatorNaMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1567 | [8 empty] | 0x06400ad0
SS3KlimaError4NapakaTSTemperaturaProstora_Om | DIGITAL | IOD_SS3_disk | D1568 | [8 empty] | 0x06400ae0
SS3KlimaError4NapakaSenzorVlaznosti_Om | DIGITAL | IOD_SS3_disk | D1569 | [8 empty] | 0x06400af0
SS3KlimaError4NapakaSenzorPritiska_Om | DIGITAL | IOD_SS3_disk | D1570 | [8 empty] | 0x06400b00
SS3KlimaError4VisokTokVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1571 | [8 empty] | 0x06400b10
SS3KlimaError4NiVodeVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1572 | [8 empty] | 0x06400b20
SS3KlimaError4NiTokaVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1573 | [8 empty] | 0x06400b30
SS3KlimaError4VisokPritiskVKrogu1_Om | DIGITAL | IOD_SS3_disk | D1574 | [8 empty] | 0x06400b40
SS3KlimaError4VisokPritiskVKrogu2_Om | DIGITAL | IOD_SS3_disk | D1575 | [8 empty] | 0x06400b50
SS3KlimaError4IzlivVode_Om | DIGITAL | IOD_SS3_disk | D1576 | [8 empty] | 0x06400b60
SS3KlimaError4TermZascInVisokPritiskKompr1_Om | DIGITAL | IOD_SS3_disk | D1577 | [8 empty] | 0x06400b70
SS3KlimaError4VlazilecnaMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1578 | [8 empty] | 0x06400b80
SS3KlimaError4TermZascInVisokPritiskKompr2_Om | DIGITAL | IOD_SS3_disk | D1579 | [8 empty] | 0x06400b90
SS3KlimaError4NapakaPriPretokuVode_Om | DIGITAL | IOD_SS3_disk | D1580 | [8 empty] | 0x06400ba0
SS3KlimaError4Kond1FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1581 | [8 empty] | 0x06400bb0
SS3KlimaError4Kond2FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1582 | [8 empty] | 0x06400bc0
SS3KlimaError4ZunanjiAlarm_Om | DIGITAL | IOD_SS3_disk | D1583 | [8 empty] | 0x06400bd0
SS3KlimaError4FaultyEprom_Om | DIGITAL | IOD_SS3_disk | D1584 | [8 empty] | 0x06400be0
SS3KlimaError4NapakaSenzorTempIzpiha_Om | DIGITAL | IOD_SS3_disk | D1585 | [8 empty] | 0x06400bf0
SS3KlimaError4NapakaSenzorTempProstora_Om | DIGITAL | IOD_SS3_disk | D1586 | [8 empty] | 0x06400c00
SS3KlimaError4NapakaSenzorZunanjeTemp_Om | DIGITAL | IOD_SS3_disk | D1587 | [8 empty] | 0x06400c10
SS3KlimaError4NizkaTempPovratneVode_Om | DIGITAL | IOD_SS3_disk | D1588 | [8 empty] | 0x06400c20
SS3KlimaError4StoppedByAlarms_Om | DIGITAL | IOD_SS3_disk | D1589 | [8 empty] | 0x06400c30
SS3KlimaError4VisokaTempPovratneVode_Om | DIGITAL | IOD_SS3_disk | D1590 | [8 empty] | 0x06400c40
SS3KlimaError4GeneralAlarm_Om | DIGITAL | IOD_SS3_disk | D1591 | [8 empty] | 0x06400c50
SS3KlimaError4NapakaSenzorPovratVode_Om | DIGITAL | IOD_SS3_disk | D1592 | [8 empty] | 0x06400c60
SS3AlarmTempTIA1Previsoka_Om | DIGITAL | IOD_SS3_disk | D1593 | [8 empty] | 0x06400c70
SS3AlarmTempTIA2Previsoka_Om | DIGITAL | IOD_SS3_disk | D1594 | [8 empty] | 0x06400c80
SS3AlarmTempTIA3Previsoka_Om | DIGITAL | IOD_SS3_disk | D1595 | [8 empty] | 0x06400c90
SS3UserloggedIn_mem | DIGITAL | IOD_SS3_disk | D1596 | [8 empty] | 0x06400ca0
SS3OnemAlarmPon | DIGITAL | IOD_SS3_disk | D1597 | [8 empty] | 0x06400cb0
SS3ComSCADA_stevec2 | INT | IOD_SS3_mem | I1600 | [8 empty] | 0x06400cc0
SS3ComSCADA_stevec1 | INT | IOD_SS3_mem | I1602 | [8 empty] | 0x06400cc1
SS3OmogociVseAlarme | DIGITAL | IOD_SS3_disk | D1598 | [8 empty] | 0x06400cd0
SS3OmogociVseSMSAlarme | DIGITAL | IOD_SS3_disk | D1599 | [8 empty] | 0x06400ce0
SS3AlarmSinhronizacijaNOK_Om | DIGITAL | IOD_SS3_disk | D1600 | [8 empty] | 0x06400cf0
SS3AktualniSetPointTemp1_2 | REAL | IOD_SS3 | SS3:.AktualniSetPointTemp1_2 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06400d00
SS3AktualniSetPointTemp3_4 | REAL | IOD_SS3 | SS3:.AktualniSetPointTemp3_4 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06400d01
SS3AlarmKlimat1_Napaka | DIGITAL | IOD_SS3 | SS3:.AlarmKlimat1_Napaka | [6 empty] | 6157 | 0 | 0x06400d10
SS3AlarmKlimat2_Napaka | DIGITAL | IOD_SS3 | SS3:.AlarmKlimat2_Napaka | [6 empty] | 6157 | 0 | 0x06400d20
SS3AlarmKlimat3_Napaka | DIGITAL | IOD_SS3 | SS3:.AlarmKlimat3_Napaka | [6 empty] | 6157 | 0 | 0x06400d30
SS3AlarmKlimat4_Napaka | DIGITAL | IOD_SS3 | SS3:.AlarmKlimat4_Napaka | [6 empty] | 6157 | 0 | 0x06400d40
SS3AlarmLAH1_RazlitjeVode | DIGITAL | IOD_SS3 | SS3:.AlarmLAH1_RazlitjeVode | [6 empty] | 6157 | 0 | 0x06400d50
SS3AlarmLAH2_RazlitjeVode | DIGITAL | IOD_SS3 | SS3:.AlarmLAH2_RazlitjeVode | [6 empty] | 6157 | 0 | 0x06400d60
SS3AlarmSinhronizacijaNOK | DIGITAL | IOD_SS3 | SS3:.AlarmSinhronizacijaNOK | [6 empty] | 6157 | 0 | 0x06400d70
SS3AlarmTempTIA1Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA1Previsoka | [6 empty] | 6157 | 0 | 0x06400d80
SS3AlarmTempTIA2Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA2Previsoka | [6 empty] | 6157 | 0 | 0x06400d90
SS3AlarmTempTIA3Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA3Previsoka | [6 empty] | 6157 | 0 | 0x06400da0
SS3AlarmTSTemp1Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTSTemp1Previsoka | [6 empty] | 6157 | 0 | 0x06400db0
SS3AlarmTSTemp3Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTSTemp3Previsoka | [6 empty] | 6157 | 0 | 0x06400dc0
SS3AlarmUPSKrmOmara_Alarm | DIGITAL | IOD_SS3 | SS3:.AlarmUPSKrmOmara_Alarm | [6 empty] | 6157 | 0 | 0x06400dd0
SS3ComSCADA | DIGITAL | IOD_SS3 | SS3:.ComSCADA | [6 empty] | 6157 | 0 | 0x06400de0
SS3ComSCADA1 | DIGITAL | IOD_SS3 | SS3:.ComSCADA1 | [6 empty] | 6157 | 0 | 0x06400df0
SS3DatumCasDan | BYTE | IOD_SS3 | SS3:.DatumCas.Dan | [6 empty] | 6157 | 0 | 0x06400e00
SS3DatumCasLeto | BYTE | IOD_SS3 | SS3:.DatumCas.Leto | [6 empty] | 6157 | 0 | 0x06400e01
SS3DatumCasLeto2 | INT | IOD_SS3 | SS3:.DatumCas.Leto2 | [6 empty] | 6157 | 0 | 0x06400e02
SS3DatumCasMesec | BYTE | IOD_SS3 | SS3:.DatumCas.Mesec | [6 empty] | 6157 | 0 | 0x06400e03
SS3DatumCasMinuta | BYTE | IOD_SS3 | SS3:.DatumCas.Minuta | [6 empty] | 6157 | 0 | 0x06400e04
SS3DatumCasSekunda | BYTE | IOD_SS3 | SS3:.DatumCas.Sekunda | [6 empty] | 6157 | 0 | 0x06400e05
SS3DatumCasUra | BYTE | IOD_SS3 | SS3:.DatumCas.Ura | [6 empty] | 6157 | 0 | 0x06400e06
SS3ErrComKlima1 | DIGITAL | IOD_SS3 | SS3:.ErrComKlima[1] | [6 empty] | 6157 | 0 | 0x06400e10
SS3ErrComKlima2 | DIGITAL | IOD_SS3 | SS3:.ErrComKlima[2] | [6 empty] | 6157 | 0 | 0x06400e20
SS3ErrComKlima3 | DIGITAL | IOD_SS3 | SS3:.ErrComKlima[3] | [6 empty] | 6157 | 0 | 0x06400e30
SS3ErrComKlima4 | DIGITAL | IOD_SS3 | SS3:.ErrComKlima[4] | [6 empty] | 6157 | 0 | 0x06400e40
SS3ErrCommScada | DIGITAL | IOD_SS3 | SS3:.ErrCommScada | [6 empty] | 6157 | 0 | 0x06400e50
SS3ErrComPanelPLC | DIGITAL | IOD_SS3 | SS3:.ErrComPanelPLC | [6 empty] | 6157 | 0 | 0x06400e60
SS3ErrComPort2 | DIGITAL | IOD_SS3 | SS3:.ErrComPort2 | [6 empty] | 6157 | 0 | 0x06400e70
SS3ErrorComKlima4Error | DIGITAL | IOD_SS3 | SS3:.ErrorComKlima[4].Error | [6 empty] | 6157 | 0 | 0x06400e80
SS3ErrorComKlima4Status | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Status | [6 empty] | 6157 | 0 | 0x06400e90
SS3Klima1_Onemogocena | DIGITAL | IOD_SS3 | SS3:.Klima1_Onemogocena | [6 empty] | 6157 | 0 | 0x06400ea0
SS3Klima1ure | REAL | IOD_SS3 | SS3:.Klima1ure | [6 empty] | 6157 | 0 | 0x06400eb0
SS3Klima2_Onemogocena | DIGITAL | IOD_SS3 | SS3:.Klima2_Onemogocena | [6 empty] | 6157 | 0 | 0x06400ec0
SS3Klima2ure | REAL | IOD_SS3 | SS3:.Klima2ure | [6 empty] | 6157 | 0 | 0x06400ed0
SS3Klima3_Onemogocena | DIGITAL | IOD_SS3 | SS3:.Klima3_Onemogocena | [6 empty] | 6157 | 0 | 0x06400ee0
SS3Klima3ure | REAL | IOD_SS3 | SS3:.Klima3ure | [6 empty] | 6157 | 0 | 0x06400ef0
SS3Klima4_Onemogocena | DIGITAL | IOD_SS3 | SS3:.Klima4_Onemogocena | [6 empty] | 6157 | 0 | 0x06400f00
SS3Klima4ure | REAL | IOD_SS3 | SS3:.Klima4ure | [6 empty] | 6157 | 0 | 0x06400f10
SS3Klima1Deluje | DIGITAL | IOD_SS3 | SS3:.Klima[1].Deluje | [6 empty] | 6157 | 0 | 0x06400f20
SS3Klima1EnergySaving | DIGITAL | IOD_SS3 | SS3:.Klima[1].EnergySaving | [6 empty] | 6157 | 0 | 0x06400f30
SS3Klima1GrelecStatus | BYTE | IOD_SS3 | SS3:.Klima[1].GrelecStatus | [6 empty] | 6157 | 0 | 0x06400f40
SS3Klima1IzhodniVentStatus | BYTE | IOD_SS3 | SS3:.Klima[1].IzhodniVentStatus | [6 empty] | 6157 | 0 | 0x06400f41
SS3Klima1KompresorStatus | BYTE | IOD_SS3 | SS3:.Klima[1].KompresorStatus | [6 empty] | 6157 | 0 | 0x06400f42
SS3Klima1Napaka | DIGITAL | IOD_SS3 | SS3:.Klima[1].Napaka | [6 empty] | 6157 | 0 | 0x06400f50
SS3Klima1NastTempProstora | REAL | IOD_SS3 | SS3:.Klima[1].NastTempProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06400f60
SS3Klima1NastVlaznost | REAL | IOD_SS3 | SS3:.Klima[1].NastVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x06400f61
SS3Klima1ObratovalneUre | REAL | IOD_SS3 | SS3:.Klima[1].ObratovalneUre | [6 empty] | 6157 | 0 | 0x06400f62
SS3Klima1OnOffEnablingBySupervisor | DIGITAL | IOD_SS3 | SS3:.Klima[1].OnOffEnablingBySupervisor | [6 empty] | 6157 | 0 | 0x06400f70
SS3Klima1Razvlazevanje | DIGITAL | IOD_SS3 | SS3:.Klima[1].Razvlazevanje | [6 empty] | 6157 | 0 | 0x06400f80
SS3Klima1RemoteOFFtoOutput | DIGITAL | IOD_SS3 | SS3:.Klima[1].RemoteOFFtoOutput | [6 empty] | 6157 | 0 | 0x06400f90
SS3Klima1RemoteOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[1].RemoteOnOff | [6 empty] | 6157 | 0 | 0x06400fa0
SS3Klima1RocniIzklop | DIGITAL | IOD_SS3 | SS3:.Klima[1].RocniIzklop | [6 empty] | 6157 | 0 | 0x06400fb0
SS3Klima1SenzorjiStatus | DIGITAL | IOD_SS3 | SS3:.Klima[1].SenzorjiStatus | [6 empty] | 6157 | 0 | 0x06400fc0
SS3Klima1TemperaturaProstora | REAL | IOD_SS3 | SS3:.Klima[1].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06400fd0
SS3Klima1UnitOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[1].UnitOnOff | [6 empty] | 6157 | 0 | 0x06400fe0
SS3Klima1VentilGretjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[1].VentilGretjeOdpiranje | [6 empty] | 6157 | 0 | 0x06400ff0
SS3Klima1VentilGretjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[1].VentilGretjeZapiranje | [6 empty] | 6157 | 0 | 0x06401000
SS3Klima1VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[1].VentilHlajenjeOdpiranje | [6 empty] | 6157 | 0 | 0x06401010
SS3Klima1VentilHlajenjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[1].VentilHlajenjeZapiranje | [6 empty] | 6157 | 0 | 0x06401020
SS3Klima1Vlazenje | DIGITAL | IOD_SS3 | SS3:.Klima[1].Vlazenje | [6 empty] | 6157 | 0 | 0x06401030
SS3Klima1VlazilecStatus | BYTE | IOD_SS3 | SS3:.Klima[1].VlazilecStatus | [6 empty] | 6157 | 0 | 0x06401040
SS3Klima1VlaznostProstora | REAL | IOD_SS3 | SS3:.Klima[1].VlaznostProstora | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x06401041
SS3Klima2Deluje | DIGITAL | IOD_SS3 | SS3:.Klima[2].Deluje | [6 empty] | 6157 | 0 | 0x06401050
SS3Klima2EnergySaving | DIGITAL | IOD_SS3 | SS3:.Klima[2].EnergySaving | [6 empty] | 6157 | 0 | 0x06401060
SS3Klima2GrelecStatus | BYTE | IOD_SS3 | SS3:.Klima[2].GrelecStatus | [6 empty] | 6157 | 0 | 0x06401070
SS3Klima2IzhodniVentStatus | BYTE | IOD_SS3 | SS3:.Klima[2].IzhodniVentStatus | [6 empty] | 6157 | 0 | 0x06401071
SS3Klima2KompresorStatus | BYTE | IOD_SS3 | SS3:.Klima[2].KompresorStatus | [6 empty] | 6157 | 0 | 0x06401072
SS3Klima2Napaka | DIGITAL | IOD_SS3 | SS3:.Klima[2].Napaka | [6 empty] | 6157 | 0 | 0x06401080
SS3Klima2NastTempProstora | REAL | IOD_SS3 | SS3:.Klima[2].NastTempProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06401090
SS3Klima2NastVlaznost | REAL | IOD_SS3 | SS3:.Klima[2].NastVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x06401091
SS3Klima2ObratovalneUre | REAL | IOD_SS3 | SS3:.Klima[2].ObratovalneUre | [6 empty] | 6157 | 0 | 0x06401092
SS3Klima2OnOffEnablingBySupervisor | DIGITAL | IOD_SS3 | SS3:.Klima[2].OnOffEnablingBySupervisor | [6 empty] | 6157 | 0 | 0x064010a0
SS3Klima2Razvlazevanje | DIGITAL | IOD_SS3 | SS3:.Klima[2].Razvlazevanje | [6 empty] | 6157 | 0 | 0x064010b0
SS3Klima2RemoteOFFtoOutput | DIGITAL | IOD_SS3 | SS3:.Klima[2].RemoteOFFtoOutput | [6 empty] | 6157 | 0 | 0x064010c0
SS3Klima2RemoteOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[2].RemoteOnOff | [6 empty] | 6157 | 0 | 0x064010d0
SS3Klima2RocniIzklop | DIGITAL | IOD_SS3 | SS3:.Klima[2].RocniIzklop | [6 empty] | 6157 | 0 | 0x064010e0
SS3Klima2SenzorjiStatus | DIGITAL | IOD_SS3 | SS3:.Klima[2].SenzorjiStatus | [6 empty] | 6157 | 0 | 0x064010f0
SS3Klima2TemperaturaProstora | REAL | IOD_SS3 | SS3:.Klima[2].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06401100
SS3Klima2UnitOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[2].UnitOnOff | [6 empty] | 6157 | 0 | 0x06401110
SS3Klima2VentilGretjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[2].VentilGretjeOdpiranje | [6 empty] | 6157 | 0 | 0x06401120
SS3Klima2VentilGretjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[2].VentilGretjeZapiranje | [6 empty] | 6157 | 0 | 0x06401130
SS3Klima2VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[2].VentilHlajenjeOdpiranje | [6 empty] | 6157 | 0 | 0x06401140
SS3Klima2VentilHlajenjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[2].VentilHlajenjeZapiranje | [6 empty] | 6157 | 0 | 0x06401150
SS3Klima2Vlazenje | DIGITAL | IOD_SS3 | SS3:.Klima[2].Vlazenje | [6 empty] | 6157 | 0 | 0x06401160
SS3Klima2VlazilecStatus | BYTE | IOD_SS3 | SS3:.Klima[2].VlazilecStatus | [6 empty] | 6157 | 0 | 0x06401170
SS3Klima2VlaznostProstora | REAL | IOD_SS3 | SS3:.Klima[2].VlaznostProstora | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x06401171
SS3Klima3Deluje | DIGITAL | IOD_SS3 | SS3:.Klima[3].Deluje | [6 empty] | 6157 | 0 | 0x06401180
SS3Klima3EnergySaving | DIGITAL | IOD_SS3 | SS3:.Klima[3].EnergySaving | [6 empty] | 6157 | 0 | 0x06401190
SS3Klima3GrelecStatus | BYTE | IOD_SS3 | SS3:.Klima[3].GrelecStatus | [6 empty] | 6157 | 0 | 0x064011a0
SS3Klima3IzhodniVentStatus | BYTE | IOD_SS3 | SS3:.Klima[3].IzhodniVentStatus | [6 empty] | 6157 | 0 | 0x064011a1
SS3Klima3KompresorStatus | BYTE | IOD_SS3 | SS3:.Klima[3].KompresorStatus | [6 empty] | 6157 | 0 | 0x064011a2
SS3Klima3Napaka | DIGITAL | IOD_SS3 | SS3:.Klima[3].Napaka | [6 empty] | 6157 | 0 | 0x064011b0
SS3Klima3NastTempProstora | REAL | IOD_SS3 | SS3:.Klima[3].NastTempProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x064011c0
SS3Klima3NastVlaznost | REAL | IOD_SS3 | SS3:.Klima[3].NastVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x064011c1
SS3Klima3ObratovalneUre | REAL | IOD_SS3 | SS3:.Klima[3].ObratovalneUre | [6 empty] | 6157 | 0 | 0x064011c2
SS3Klima3OnOffEnablingBySupervisor | DIGITAL | IOD_SS3 | SS3:.Klima[3].OnOffEnablingBySupervisor | [6 empty] | 6157 | 0 | 0x064011d0
SS3Klima3Razvlazevanje | DIGITAL | IOD_SS3 | SS3:.Klima[3].Razvlazevanje | [6 empty] | 6157 | 0 | 0x064011e0
SS3Klima3RemoteOFFtoOutput | DIGITAL | IOD_SS3 | SS3:.Klima[3].RemoteOFFtoOutput | [6 empty] | 6157 | 0 | 0x064011f0
SS3Klima3RemoteOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[3].RemoteOnOff | [6 empty] | 6157 | 0 | 0x06401200
SS3Klima3RocniIzklop | DIGITAL | IOD_SS3 | SS3:.Klima[3].RocniIzklop | [6 empty] | 6157 | 0 | 0x06401210
SS3Klima3SenzorjiStatus | DIGITAL | IOD_SS3 | SS3:.Klima[3].SenzorjiStatus | [6 empty] | 6157 | 0 | 0x06401220
SS3Klima3TemperaturaProstora | REAL | IOD_SS3 | SS3:.Klima[3].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06401230
SS3Klima3UnitOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[3].UnitOnOff | [6 empty] | 6157 | 0 | 0x06401240
SS3Klima3VentilGretjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[3].VentilGretjeOdpiranje | [6 empty] | 6157 | 0 | 0x06401250
SS3Klima3VentilGretjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[3].VentilGretjeZapiranje | [6 empty] | 6157 | 0 | 0x06401260
SS3Klima3VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[3].VentilHlajenjeOdpiranje | [6 empty] | 6157 | 0 | 0x06401270
SS3Klima3VentilHlajenjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[3].VentilHlajenjeZapiranje | [6 empty] | 6157 | 0 | 0x06401280
SS3Klima3Vlazenje | DIGITAL | IOD_SS3 | SS3:.Klima[3].Vlazenje | [6 empty] | 6157 | 0 | 0x06401290
SS3Klima3VlazilecStatus | BYTE | IOD_SS3 | SS3:.Klima[3].VlazilecStatus | [6 empty] | 6157 | 0 | 0x064012a0
SS3Klima3VlaznostProstora | REAL | IOD_SS3 | SS3:.Klima[3].VlaznostProstora | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x064012a1
SS3Klima4Deluje | DIGITAL | IOD_SS3 | SS3:.Klima[4].Deluje | [6 empty] | 6157 | 0 | 0x064012b0
SS3Klima4EnergySaving | DIGITAL | IOD_SS3 | SS3:.Klima[4].EnergySaving | [6 empty] | 6157 | 0 | 0x064012c0
SS3Klima4GrelecStatus | BYTE | IOD_SS3 | SS3:.Klima[4].GrelecStatus | [6 empty] | 6157 | 0 | 0x064012d0
SS3Klima4IzhodniVentStatus | BYTE | IOD_SS3 | SS3:.Klima[4].IzhodniVentStatus | [6 empty] | 6157 | 0 | 0x064012d1
SS3Klima4KompresorStatus | BYTE | IOD_SS3 | SS3:.Klima[4].KompresorStatus | [6 empty] | 6157 | 0 | 0x064012d2
SS3Klima4Napaka | DIGITAL | IOD_SS3 | SS3:.Klima[4].Napaka | [6 empty] | 6157 | 0 | 0x064012e0
SS3Klima4NastTempProstora | REAL | IOD_SS3 | SS3:.Klima[4].NastTempProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x064012f0
SS3Klima4NastVlaznost | REAL | IOD_SS3 | SS3:.Klima[4].NastVlaznost | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x064012f1
SS3Klima4ObratovalneUre | REAL | IOD_SS3 | SS3:.Klima[4].ObratovalneUre | [6 empty] | 6157 | 0 | 0x064012f2
SS3Klima4OnOffEnablingBySupervisor | DIGITAL | IOD_SS3 | SS3:.Klima[4].OnOffEnablingBySupervisor | [6 empty] | 6157 | 0 | 0x06401300
SS3Klima4Razvlazevanje | DIGITAL | IOD_SS3 | SS3:.Klima[4].Razvlazevanje | [6 empty] | 6157 | 0 | 0x06401310
SS3Klima4RemoteOFFtoOutput | DIGITAL | IOD_SS3 | SS3:.Klima[4].RemoteOFFtoOutput | [6 empty] | 6157 | 0 | 0x06401320
SS3Klima4RemoteOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[4].RemoteOnOff | [6 empty] | 6157 | 0 | 0x06401330
SS3Klima4RocniIzklop | DIGITAL | IOD_SS3 | SS3:.Klima[4].RocniIzklop | [6 empty] | 6157 | 0 | 0x06401340
SS3Klima4SenzorjiStatus | DIGITAL | IOD_SS3 | SS3:.Klima[4].SenzorjiStatus | [6 empty] | 6157 | 0 | 0x06401350
SS3Klima4TemperaturaProstora | REAL | IOD_SS3 | SS3:.Klima[4].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06401360
SS3Klima4UnitOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[4].UnitOnOff | [6 empty] | 6157 | 0 | 0x06401370
SS3Klima4VentilGretjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[4].VentilGretjeOdpiranje | [6 empty] | 6157 | 0 | 0x06401380
SS3Klima4VentilGretjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[4].VentilGretjeZapiranje | [6 empty] | 6157 | 0 | 0x06401390
SS3Klima4VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[4].VentilHlajenjeOdpiranje | [6 empty] | 6157 | 0 | 0x064013a0
SS3Klima4VentilHlajenjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[4].VentilHlajenjeZapiranje | [6 empty] | 6157 | 0 | 0x064013b0
SS3Klima4Vlazenje | DIGITAL | IOD_SS3 | SS3:.Klima[4].Vlazenje | [6 empty] | 6157 | 0 | 0x064013c0
SS3Klima4VlazilecStatus | BYTE | IOD_SS3 | SS3:.Klima[4].VlazilecStatus | [6 empty] | 6157 | 0 | 0x064013d0
SS3Klima4VlaznostProstora | REAL | IOD_SS3 | SS3:.Klima[4].VlaznostProstora | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x064013d1
SS3KlimaError1AlarmKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].AlarmKompresor1 | [6 empty] | 6157 | 0 | 0x064013e0
SS3KlimaError1AlarmKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].AlarmKompresor2 | [6 empty] | 6157 | 0 | 0x064013f0
SS3KlimaError1FaultyEprom | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].FaultyEprom | [6 empty] | 6157 | 0 | 0x06401400
SS3KlimaError1FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].FenThermalCutout | [6 empty] | 6157 | 0 | 0x06401410
SS3KlimaError1GeneralAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].GeneralAlarm | [6 empty] | 6157 | 0 | 0x06401420
SS3KlimaError1Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].Kompresor1naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x06401430
SS3KlimaError1Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].Kompresor2naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x06401440
SS3KlimaError1Kond1FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].Kond1FenThermalCutout | [6 empty] | 6157 | 0 | 0x06401450
SS3KlimaError1Kond2FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].Kond2FenThermalCutout | [6 empty] | 6157 | 0 | 0x06401460
SS3KlimaError1NapakaPriPretokuVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaPriPretokuVode | [6 empty] | 6157 | 0 | 0x06401470
SS3KlimaError1NapakaPriPretokuZraka | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaPriPretokuZraka | [6 empty] | 6157 | 0 | 0x06401480
SS3KlimaError1NapakaSenzorPovratVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorPovratVode | [6 empty] | 6157 | 0 | 0x06401490
SS3KlimaError1NapakaSenzorPritiska | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorPritiska | [6 empty] | 6157 | 0 | 0x064014a0
SS3KlimaError1NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorTempIzpiha | [6 empty] | 6157 | 0 | 0x064014b0
SS3KlimaError1NapakaSenzorTempProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorTempProstora | [6 empty] | 6157 | 0 | 0x064014c0
SS3KlimaError1NapakaSenzorVlaznosti | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorVlaznosti | [6 empty] | 6157 | 0 | 0x064014d0
SS3KlimaError1NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorZunanjeTemp | [6 empty] | 6157 | 0 | 0x064014e0
SS3KlimaError1NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaTSTemperaturaProstora | [6 empty] | 6157 | 0 | 0x064014f0
SS3KlimaError1NiTokaVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NiTokaVVlazilcu | [6 empty] | 6157 | 0 | 0x06401500
SS3KlimaError1NiVodeVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NiVodeVVlazilcu | [6 empty] | 6157 | 0 | 0x06401510
SS3KlimaError1NizekPritiskKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NizekPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x06401520
SS3KlimaError1NizekPritiskKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NizekPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x06401530
SS3KlimaError1NizkaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NizkaTempPovratneVode | [6 empty] | 6157 | 0 | 0x06401540
SS3KlimaError1NizkaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NizkaTempVProstoru | [6 empty] | 6157 | 0 | 0x06401550
SS3KlimaError1NizkaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NizkaVlaznost | [6 empty] | 6157 | 0 | 0x06401560
SS3KlimaError1PozarniAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].PozarniAlarm | [6 empty] | 6157 | 0 | 0x06401570
SS3KlimaError1StoppedByAlarms | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].StoppedByAlarms | [6 empty] | 6157 | 0 | 0x06401580
SS3KlimaError1TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].TermZascInVisokPritiskKompr1 | [6 empty] | 6157 | 0 | 0x06401590
SS3KlimaError1TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].TermZascInVisokPritiskKompr2 | [6 empty] | 6157 | 0 | 0x064015a0
SS3KlimaError1ThermalCutoutHeater1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].ThermalCutoutHeater1 | [6 empty] | 6157 | 0 | 0x064015b0
SS3KlimaError1ThermalCutoutHeater2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].ThermalCutoutHeater2 | [6 empty] | 6157 | 0 | 0x064015c0
SS3KlimaError1VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VentilatorNaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x064015d0
SS3KlimaError1VisokaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokaTempPovratneVode | [6 empty] | 6157 | 0 | 0x064015e0
SS3KlimaError1VisokaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokaTempVProstoru | [6 empty] | 6157 | 0 | 0x064015f0
SS3KlimaError1VisokaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokaVlaznost | [6 empty] | 6157 | 0 | 0x06401600
SS3KlimaError1VisokPritiskVKrogu1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokPritiskVKrogu1 | [6 empty] | 6157 | 0 | 0x06401610
SS3KlimaError1VisokPritiskVKrogu2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokPritiskVKrogu2 | [6 empty] | 6157 | 0 | 0x06401620
SS3KlimaError1VisokTokVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokTokVVlazilcu | [6 empty] | 6157 | 0 | 0x06401630
SS3KlimaError1VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VlazilecnaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x06401640
SS3KlimaError1ZamasenFilter | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].ZamasenFilter | [6 empty] | 6157 | 0 | 0x06401650
SS3KlimaError2AlarmKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].AlarmKompresor1 | [6 empty] | 6157 | 0 | 0x06401660
SS3KlimaError2AlarmKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].AlarmKompresor2 | [6 empty] | 6157 | 0 | 0x06401670
SS3KlimaError2FaultyEprom | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].FaultyEprom | [6 empty] | 6157 | 0 | 0x06401680
SS3KlimaError2FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].FenThermalCutout | [6 empty] | 6157 | 0 | 0x06401690
SS3KlimaError2GeneralAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].GeneralAlarm | [6 empty] | 6157 | 0 | 0x064016a0
SS3KlimaError2Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].Kompresor1naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x064016b0
SS3KlimaError2Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].Kompresor2naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x064016c0
SS3KlimaError2Kond1FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].Kond1FenThermalCutout | [6 empty] | 6157 | 0 | 0x064016d0
SS3KlimaError2Kond2FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].Kond2FenThermalCutout | [6 empty] | 6157 | 0 | 0x064016e0
SS3KlimaError2NapakaPriPretokuVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaPriPretokuVode | [6 empty] | 6157 | 0 | 0x064016f0
SS3KlimaError2NapakaPriPretokuZraka | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaPriPretokuZraka | [6 empty] | 6157 | 0 | 0x06401700
SS3KlimaError2NapakaSenzorPovratVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorPovratVode | [6 empty] | 6157 | 0 | 0x06401710
SS3KlimaError2NapakaSenzorPritiska | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorPritiska | [6 empty] | 6157 | 0 | 0x06401720
SS3KlimaError2NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorTempIzpiha | [6 empty] | 6157 | 0 | 0x06401730
SS3KlimaError2NapakaSenzorTempProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorTempProstora | [6 empty] | 6157 | 0 | 0x06401740
SS3KlimaError2NapakaSenzorVlaznosti | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorVlaznosti | [6 empty] | 6157 | 0 | 0x06401750
SS3KlimaError2NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorZunanjeTemp | [6 empty] | 6157 | 0 | 0x06401760
SS3KlimaError2NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaTSTemperaturaProstora | [6 empty] | 6157 | 0 | 0x06401770
SS3KlimaError2NiTokaVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NiTokaVVlazilcu | [6 empty] | 6157 | 0 | 0x06401780
SS3KlimaError2NiVodeVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NiVodeVVlazilcu | [6 empty] | 6157 | 0 | 0x06401790
SS3KlimaError2NizekPritiskKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NizekPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x064017a0
SS3KlimaError2NizekPritiskKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NizekPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x064017b0
SS3KlimaError2NizkaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NizkaTempPovratneVode | [6 empty] | 6157 | 0 | 0x064017c0
SS3KlimaError2NizkaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NizkaTempVProstoru | [6 empty] | 6157 | 0 | 0x064017d0
SS3KlimaError2NizkaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NizkaVlaznost | [6 empty] | 6157 | 0 | 0x064017e0
SS3KlimaError2PozarniAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].PozarniAlarm | [6 empty] | 6157 | 0 | 0x064017f0
SS3KlimaError2StoppedByAlarms | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].StoppedByAlarms | [6 empty] | 6157 | 0 | 0x06401800
SS3KlimaError2TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].TermZascInVisokPritiskKompr1 | [6 empty] | 6157 | 0 | 0x06401810
SS3KlimaError2TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].TermZascInVisokPritiskKompr2 | [6 empty] | 6157 | 0 | 0x06401820
SS3KlimaError2ThermalCutoutHeater1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].ThermalCutoutHeater1 | [6 empty] | 6157 | 0 | 0x06401830
SS3KlimaError2ThermalCutoutHeater2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].ThermalCutoutHeater2 | [6 empty] | 6157 | 0 | 0x06401840
SS3KlimaError2VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VentilatorNaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x06401850
SS3KlimaError2VisokaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokaTempPovratneVode | [6 empty] | 6157 | 0 | 0x06401860
SS3KlimaError2VisokaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokaTempVProstoru | [6 empty] | 6157 | 0 | 0x06401870
SS3KlimaError2VisokaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokaVlaznost | [6 empty] | 6157 | 0 | 0x06401880
SS3KlimaError2VisokPritiskVKrogu1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokPritiskVKrogu1 | [6 empty] | 6157 | 0 | 0x06401890
SS3KlimaError2VisokPritiskVKrogu2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokPritiskVKrogu2 | [6 empty] | 6157 | 0 | 0x064018a0
SS3KlimaError2VisokTokVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokTokVVlazilcu | [6 empty] | 6157 | 0 | 0x064018b0
SS3KlimaError2VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VlazilecnaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x064018c0
SS3KlimaError2ZamasenFilter | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].ZamasenFilter | [6 empty] | 6157 | 0 | 0x064018d0
SS3KlimaError3AlarmKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].AlarmKompresor1 | [6 empty] | 6157 | 0 | 0x064018e0
SS3KlimaError3AlarmKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].AlarmKompresor2 | [6 empty] | 6157 | 0 | 0x064018f0
SS3KlimaError3FaultyEprom | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].FaultyEprom | [6 empty] | 6157 | 0 | 0x06401900
SS3KlimaError3FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].FenThermalCutout | [6 empty] | 6157 | 0 | 0x06401910
SS3KlimaError3GeneralAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].GeneralAlarm | [6 empty] | 6157 | 0 | 0x06401920
SS3KlimaError3Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].Kompresor1naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x06401930
SS3KlimaError3Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].Kompresor2naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x06401940
SS3KlimaError3Kond1FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].Kond1FenThermalCutout | [6 empty] | 6157 | 0 | 0x06401950
SS3KlimaError3Kond2FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].Kond2FenThermalCutout | [6 empty] | 6157 | 0 | 0x06401960
SS3KlimaError3NapakaPriPretokuVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaPriPretokuVode | [6 empty] | 6157 | 0 | 0x06401970
SS3KlimaError3NapakaPriPretokuZraka | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaPriPretokuZraka | [6 empty] | 6157 | 0 | 0x06401980
SS3KlimaError3NapakaSenzorPovratVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorPovratVode | [6 empty] | 6157 | 0 | 0x06401990
SS3KlimaError3NapakaSenzorPritiska | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorPritiska | [6 empty] | 6157 | 0 | 0x064019a0
SS3KlimaError3NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorTempIzpiha | [6 empty] | 6157 | 0 | 0x064019b0
SS3KlimaError3NapakaSenzorTempProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorTempProstora | [6 empty] | 6157 | 0 | 0x064019c0
SS3KlimaError3NapakaSenzorVlaznosti | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorVlaznosti | [6 empty] | 6157 | 0 | 0x064019d0
SS3KlimaError3NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorZunanjeTemp | [6 empty] | 6157 | 0 | 0x064019e0
SS3KlimaError3NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaTSTemperaturaProstora | [6 empty] | 6157 | 0 | 0x064019f0
SS3KlimaError3NiTokaVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NiTokaVVlazilcu | [6 empty] | 6157 | 0 | 0x06401a00
SS3KlimaError3NiVodeVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NiVodeVVlazilcu | [6 empty] | 6157 | 0 | 0x06401a10
SS3KlimaError3NizekPritiskKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NizekPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x06401a20
SS3KlimaError3NizekPritiskKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NizekPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x06401a30
SS3KlimaError3NizkaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NizkaTempPovratneVode | [6 empty] | 6157 | 0 | 0x06401a40
SS3KlimaError3NizkaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NizkaTempVProstoru | [6 empty] | 6157 | 0 | 0x06401a50
SS3KlimaError3NizkaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NizkaVlaznost | [6 empty] | 6157 | 0 | 0x06401a60
SS3KlimaError3PozarniAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].PozarniAlarm | [6 empty] | 6157 | 0 | 0x06401a70
SS3KlimaError3StoppedByAlarms | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].StoppedByAlarms | [6 empty] | 6157 | 0 | 0x06401a80
SS3KlimaError3TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].TermZascInVisokPritiskKompr1 | [6 empty] | 6157 | 0 | 0x06401a90
SS3KlimaError3TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].TermZascInVisokPritiskKompr2 | [6 empty] | 6157 | 0 | 0x06401aa0
SS3KlimaError3ThermalCutoutHeater1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].ThermalCutoutHeater1 | [6 empty] | 6157 | 0 | 0x06401ab0
SS3KlimaError3ThermalCutoutHeater2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].ThermalCutoutHeater2 | [6 empty] | 6157 | 0 | 0x06401ac0
SS3KlimaError3VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VentilatorNaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x06401ad0
SS3KlimaError3VisokaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokaTempPovratneVode | [6 empty] | 6157 | 0 | 0x06401ae0
SS3KlimaError3VisokaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokaTempVProstoru | [6 empty] | 6157 | 0 | 0x06401af0
SS3KlimaError3VisokaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokaVlaznost | [6 empty] | 6157 | 0 | 0x06401b00
SS3KlimaError3VisokPritiskVKrogu1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokPritiskVKrogu1 | [6 empty] | 6157 | 0 | 0x06401b10
SS3KlimaError3VisokPritiskVKrogu2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokPritiskVKrogu2 | [6 empty] | 6157 | 0 | 0x06401b20
SS3KlimaError3VisokTokVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokTokVVlazilcu | [6 empty] | 6157 | 0 | 0x06401b30
SS3KlimaError3VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VlazilecnaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x06401b40
SS3KlimaError3ZamasenFilter | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].ZamasenFilter | [6 empty] | 6157 | 0 | 0x06401b50
SS3KlimaError4AlarmKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].AlarmKompresor1 | [6 empty] | 6157 | 0 | 0x06401b60
SS3KlimaError4AlarmKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].AlarmKompresor2 | [6 empty] | 6157 | 0 | 0x06401b70
SS3KlimaError4FaultyEprom | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].FaultyEprom | [6 empty] | 6157 | 0 | 0x06401b80
SS3KlimaError4FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].FenThermalCutout | [6 empty] | 6157 | 0 | 0x06401b90
SS3KlimaError4GeneralAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].GeneralAlarm | [6 empty] | 6157 | 0 | 0x06401ba0
SS3KlimaError4Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].Kompresor1naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x06401bb0
SS3KlimaError4Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].Kompresor2naMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x06401bc0
SS3KlimaError4Kond1FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].Kond1FenThermalCutout | [6 empty] | 6157 | 0 | 0x06401bd0
SS3KlimaError4Kond2FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].Kond2FenThermalCutout | [6 empty] | 6157 | 0 | 0x06401be0
SS3KlimaError4NapakaPriPretokuVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaPriPretokuVode | [6 empty] | 6157 | 0 | 0x06401bf0
SS3KlimaError4NapakaPriPretokuZraka | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaPriPretokuZraka | [6 empty] | 6157 | 0 | 0x06401c00
SS3KlimaError4NapakaSenzorPovratVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorPovratVode | [6 empty] | 6157 | 0 | 0x06401c10
SS3KlimaError4NapakaSenzorPritiska | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorPritiska | [6 empty] | 6157 | 0 | 0x06401c20
SS3KlimaError4NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorTempIzpiha | [6 empty] | 6157 | 0 | 0x06401c30
SS3KlimaError4NapakaSenzorTempProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorTempProstora | [6 empty] | 6157 | 0 | 0x06401c40
SS3KlimaError4NapakaSenzorVlaznosti | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorVlaznosti | [6 empty] | 6157 | 0 | 0x06401c50
SS3KlimaError4NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorZunanjeTemp | [6 empty] | 6157 | 0 | 0x06401c60
SS3KlimaError4NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaTSTemperaturaProstora | [6 empty] | 6157 | 0 | 0x06401c70
SS3KlimaError4NiTokaVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NiTokaVVlazilcu | [6 empty] | 6157 | 0 | 0x06401c80
SS3KlimaError4NiVodeVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NiVodeVVlazilcu | [6 empty] | 6157 | 0 | 0x06401c90
SS3KlimaError4NizekPritiskKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NizekPritiskKompresor1 | [6 empty] | 6157 | 0 | 0x06401ca0
SS3KlimaError4NizekPritiskKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NizekPritiskKompresor2 | [6 empty] | 6157 | 0 | 0x06401cb0
SS3KlimaError4NizkaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NizkaTempPovratneVode | [6 empty] | 6157 | 0 | 0x06401cc0
SS3KlimaError4NizkaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NizkaTempVProstoru | [6 empty] | 6157 | 0 | 0x06401cd0
SS3KlimaError4NizkaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NizkaVlaznost | [6 empty] | 6157 | 0 | 0x06401ce0
SS3KlimaError4PozarniAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].PozarniAlarm | [6 empty] | 6157 | 0 | 0x06401cf0
SS3KlimaError4StoppedByAlarms | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].StoppedByAlarms | [6 empty] | 6157 | 0 | 0x06401d00
SS3KlimaError4TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].TermZascInVisokPritiskKompr1 | [6 empty] | 6157 | 0 | 0x06401d10
SS3KlimaError4TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].TermZascInVisokPritiskKompr2 | [6 empty] | 6157 | 0 | 0x06401d20
SS3KlimaError4ThermalCutoutHeater1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].ThermalCutoutHeater1 | [6 empty] | 6157 | 0 | 0x06401d30
SS3KlimaError4ThermalCutoutHeater2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].ThermalCutoutHeater2 | [6 empty] | 6157 | 0 | 0x06401d40
SS3KlimaError4VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VentilatorNaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x06401d50
SS3KlimaError4VisokaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokaTempPovratneVode | [6 empty] | 6157 | 0 | 0x06401d60
SS3KlimaError4VisokaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokaTempVProstoru | [6 empty] | 6157 | 0 | 0x06401d70
SS3KlimaError4VisokaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokaVlaznost | [6 empty] | 6157 | 0 | 0x06401d80
SS3KlimaError4VisokPritiskVKrogu1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokPritiskVKrogu1 | [6 empty] | 6157 | 0 | 0x06401d90
SS3KlimaError4VisokPritiskVKrogu2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokPritiskVKrogu2 | [6 empty] | 6157 | 0 | 0x06401da0
SS3KlimaError4VisokTokVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokTokVVlazilcu | [6 empty] | 6157 | 0 | 0x06401db0
SS3KlimaError4VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VlazilecnaMejiStevilaObrUr | [6 empty] | 6157 | 0 | 0x06401dc0
SS3KlimaError4ZamasenFilter | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].ZamasenFilter | [6 empty] | 6157 | 0 | 0x06401dd0
SS3NacDelovanjaKlime1_2_Avtomatsko | DIGITAL | IOD_SS3 | SS3:.NacDelovanjaKlime1_2_Avtomatsko | [6 empty] | 6157 | 0 | 0x06401de0
SS3NacDelovanjaKlime3_4_Avtomatsko | DIGITAL | IOD_SS3 | SS3:.NacDelovanjaKlime3_4_Avtomatsko | [6 empty] | 6157 | 0 | 0x06401df0
SS3NapakaSenzorTemp1 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorTemp1 | [6 empty] | 6157 | 0 | 0x06401e00
SS3NapakaSenzorTemp2 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorTemp2 | [6 empty] | 6157 | 0 | 0x06401e10
SS3NapakaSenzorTemp3 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorTemp3 | [6 empty] | 6157 | 0 | 0x06401e20
SS3NapakaSenzorVlaga1 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorVlaga1 | [6 empty] | 6157 | 0 | 0x06401e30
SS3NapakaSenzorVlaga2 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorVlaga2 | [6 empty] | 6157 | 0 | 0x06401e40
SS3NapakaSenzorVlaga3 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorVlaga3 | [6 empty] | 6157 | 0 | 0x06401e50
SS3NastaviCasNaKrmilniku | DIGITAL | IOD_SS3 | SS3:.NastaviCasNaKrmilniku | [6 empty] | 6157 | 0 | 0x06401e60
SS3NastavitevUreKrUspesna | DIGITAL | IOD_SS3 | SS3:.NastavitevUreKrUspesna | [6 empty] | 6157 | 0 | 0x06401e70
SS3OpozoriloBaterijaPLC | DIGITAL | IOD_SS3 | SS3:.OpozoriloBaterijaPLC | [6 empty] | 6157 | 0 | 0x06401e80
SS3OsveziAlarmePanel | DIGITAL | IOD_SS3 | SS3:.OsveziAlarmePanel | [6 empty] | 6157 | 0 | 0x06401e90
SS3RocniVklopKlima1 | DIGITAL | IOD_SS3 | SS3:.RocniVklopKlima1 | [6 empty] | 6157 | 0 | 0x06401ea0
SS3RocniVklopKlima2 | DIGITAL | IOD_SS3 | SS3:.RocniVklopKlima2 | [6 empty] | 6157 | 0 | 0x06401eb0
SS3RocniVklopKlima3 | DIGITAL | IOD_SS3 | SS3:.RocniVklopKlima3 | [6 empty] | 6157 | 0 | 0x06401ec0
SS3RocniVklopKlima4 | DIGITAL | IOD_SS3 | SS3:.RocniVklopKlima4 | [6 empty] | 6157 | 0 | 0x06401ed0
SS3SinhronizacijaPanelOK | DIGITAL | IOD_SS3 | SS3:.SinhronizacijaPanelOK | [6 empty] | 6157 | 0 | 0x06401ee0
SS3SinhronizirajCas_Panel | DIGITAL | IOD_SS3 | SS3:.SinhronizirajCas_Panel | [6 empty] | 6157 | 0 | 0x06401ef0
SS3SKTemp1 | REAL | IOD_SS3 | SS3:.SKTemp1 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06401f00
SS3SKTemp2 | REAL | IOD_SS3 | SS3:.SKTemp2 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06401f01
SS3SKTemp3 | REAL | IOD_SS3 | SS3:.SKTemp3 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06401f02
SS3SkupneNapakeNaprav_Klima1 | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_Klima1 | [6 empty] | 6157 | 0 | 0x06401f10
SS3SkupneNapakeNaprav_Klima2 | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_Klima2 | [6 empty] | 6157 | 0 | 0x06401f20
SS3SkupneNapakeNaprav_Klima3 | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_Klima3 | [6 empty] | 6157 | 0 | 0x06401f30
SS3SkupneNapakeNaprav_Klima4 | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_Klima4 | [6 empty] | 6157 | 0 | 0x06401f40
SS3SkupneNapakeNaprav_Komunikacija | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_Komunikacija | [6 empty] | 6157 | 0 | 0x06401f50
SS3SkupneNapakeNaprav_TempVlaga | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_TempVlaga | [6 empty] | 6157 | 0 | 0x06401f60
SS3SKVlaga1 | REAL | IOD_SS3 | SS3:.SKVlaga1 | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x06401f70
SS3SKVlaga2 | REAL | IOD_SS3 | SS3:.SKVlaga2 | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x06401f71
SS3SKVlaga3 | REAL | IOD_SS3 | SS3:.SKVlaga3 | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x06401f72
SS3StanjeKlimat1_Delovanje | DIGITAL | IOD_SS3 | SS3:.StanjeKlimat1_Delovanje | [6 empty] | 6157 | 0 | 0x06401f80
SS3StanjeKlimat2_Delovanje | DIGITAL | IOD_SS3 | SS3:.StanjeKlimat2_Delovanje | [6 empty] | 6157 | 0 | 0x06401f90
SS3StanjeKlimat3_Delovanje | DIGITAL | IOD_SS3 | SS3:.StanjeKlimat3_Delovanje | [6 empty] | 6157 | 0 | 0x06401fa0
SS3StanjeKlimat4_Delovanje | DIGITAL | IOD_SS3 | SS3:.StanjeKlimat4_Delovanje | [6 empty] | 6157 | 0 | 0x06401fb0
SS3StanjeUPSKrmOmara_BaterijskiNacin | DIGITAL | IOD_SS3 | SS3:.StanjeUPSKrmOmara_BaterijskiNacin | [6 empty] | 6157 | 0 | 0x06401fc0
SS3StanjeUPSKrmOmara_Polnjenje | DIGITAL | IOD_SS3 | SS3:.StanjeUPSKrmOmara_Polnjenje | [6 empty] | 6157 | 0 | 0x06401fd0
SS3StUrZaPreklopKlim1_2 | INT | IOD_SS3 | SS3:.StUrZaPreklopKlim1_2 | [6 empty] | 6157 | 0 | 0x06401fe0
SS3StUrZaPreklopKlim3_4 | INT | IOD_SS3 | SS3:.StUrZaPreklopKlim3_4 | [6 empty] | 6157 | 0 | 0x06401fe1
SS3TempZaAlarm1_2 | REAL | IOD_SS3 | SS3:.TempZaAlarm1_2 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06401fe2
SS3TempZaAlarm3_4 | REAL | IOD_SS3 | SS3:.TempZaAlarm3_4 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06401fe3
SS3TempZaAlarmTIA1 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA1 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06401fe4
SS3TempZaAlarmTIA2 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA2 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06401fe5
SS3TempZaAlarmTIA3 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA3 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06401fe6
SS3TempZaVklopObehKlim1_2 | REAL | IOD_SS3 | SS3:.TempZaVklopObehKlim1_2 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06401fe7
SS3TempZaVklopObehKlim3_4 | REAL | IOD_SS3 | SS3:.TempZaVklopObehKlim3_4 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06401fe8
SS3UPSstatus_Prikaz_PanelSCADA | BYTE | IOD_SS3 | SS3:.UPSstatus_Prikaz_PanelSCADA | [6 empty] | 6157 | 0 | 0x06401fe9
SS3UserCurrentLevel | BYTE | IOD_SS3 | SS3:.UserCurrentLevel | [6 empty] | 6157 | 0 | 0x06401fea
SS3UserLoggedIn | DIGITAL | IOD_SS3 | SS3:.UserLoggedIn | [6 empty] | 6157 | 0 | 0x06401ff0
SS3UserName | STRING | IOD_SS3 | SS3:.UserName | [6 empty] | 6157 | 0 | 0x06402000
SS3XVH_AlarmOn | DIGITAL | IOD_SS3 | SS3:.XVH_AlarmOn | [6 empty] | 6157 | 0 | 0x06402010
SS3PricetekSMSAlarmov1 | INT | IOD_SS3_disk | I1 | [8 empty] | 0x06402020
SS3KonecSMSAlarmov1 | INT | IOD_SS3_disk | I2 | [8 empty] | 0x06402021
SS3Klimat1_Vklop | DIGITAL | IOD_SS3 | SS3:.Klimat1_Vklop | [6 empty] | 6157 |  | 0x06402030
SS3Klimat2_Vklop | DIGITAL | IOD_SS3 | SS3:.Klimat2_Vklop | [6 empty] | 6157 |  | 0x06402040
SS3Klimat3_Vklop | DIGITAL | IOD_SS3 | SS3:.Klimat3_Vklop | [6 empty] | 6157 |  | 0x06402050
SS3Klimat4_Vklop | DIGITAL | IOD_SS3 | SS3:.Klimat4_Vklop | [6 empty] | 6157 |  | 0x06402060
SS3OmogociVseDogodke_DO | DIGITAL | IOD_SS3_disk | D2 | [8 empty] | 0x06402070
SS3OmogociVseDogodke_DI | DIGITAL | IOD_SS3_disk | D3 | [8 empty] | 0x06402080
SS3OmogociVseDogodke_COM | DIGITAL | IOD_SS3_disk | D4 | [8 empty] | 0x06402090
SS3Date_Time0 | STRING | IOD_SS3 | SS3:.Date_Time[0] | [6 empty] | 6157 | 0 | 0x064020a8
SS3Date_Time1 | STRING | IOD_SS3 | SS3:.Date_Time[1] | [6 empty] | 6157 | 0 | 0x064020a9
SS3Date_Time2 | STRING | IOD_SS3 | SS3:.Date_Time[2] | [6 empty] | 6157 | 0 | 0x064020aa
SS3Date_Time3 | STRING | IOD_SS3 | SS3:.Date_Time[3] | [6 empty] | 6157 | 0 | 0x064020ab
SS3ErrorComKlima1Code0 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[1].Code[0] | [6 empty] | 6157 | 0 | 0x064020ac
SS3ErrorComKlima1Code10 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[1].Code[10] | [6 empty] | 6157 | 0 | 0x064020ad
SS3ErrorComKlima1Code11 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[1].Code[11] | [6 empty] | 6157 | 0 | 0x064020ae
SS3ErrorComKlima1Code12 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[1].Code[12] | [6 empty] | 6157 | 0 | 0x064020af
SS3ErrorComKlima1Code13 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[1].Code[13] | [6 empty] | 6157 | 0 | 0x064020b0
SS3ErrorComKlima1Code14 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[1].Code[14] | [6 empty] | 6157 | 0 | 0x064020b1
SS3ErrorComKlima1Code15 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[1].Code[15] | [6 empty] | 6157 | 0 | 0x064020b2
SS3ErrorComKlima1Code1 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[1].Code[1] | [6 empty] | 6157 | 0 | 0x064020b3
SS3ErrorComKlima1Code2 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[1].Code[2] | [6 empty] | 6157 | 0 | 0x064020b4
SS3ErrorComKlima1Code3 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[1].Code[3] | [6 empty] | 6157 | 0 | 0x064020b5
SS3ErrorComKlima1Code4 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[1].Code[4] | [6 empty] | 6157 | 0 | 0x064020b6
SS3ErrorComKlima1Code5 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[1].Code[5] | [6 empty] | 6157 | 0 | 0x064020b7
SS3ErrorComKlima1Code6 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[1].Code[6] | [6 empty] | 6157 | 0 | 0x064020b8
SS3ErrorComKlima1Code7 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[1].Code[7] | [6 empty] | 6157 | 0 | 0x064020b9
SS3ErrorComKlima1Code8 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[1].Code[8] | [6 empty] | 6157 | 0 | 0x064020ba
SS3ErrorComKlima1Code9 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[1].Code[9] | [6 empty] | 6157 | 0 | 0x064020bb
SS3ErrorComKlima1Error | DIGITAL | IOD_SS3 | SS3:.ErrorComKlima[1].Error | [6 empty] | 6157 | 0 | 0x064020c0
SS3ErrorComKlima1Status | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Status | [6 empty] | 6157 | 0 | 0x064020d0
SS3ErrorComKlima2Code0 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[2].Code[0] | [6 empty] | 6157 | 0 | 0x064020d1
SS3ErrorComKlima2Code10 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[2].Code[10] | [6 empty] | 6157 | 0 | 0x064020d2
SS3ErrorComKlima2Code11 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[2].Code[11] | [6 empty] | 6157 | 0 | 0x064020d3
SS3ErrorComKlima2Code12 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[2].Code[12] | [6 empty] | 6157 | 0 | 0x064020d4
SS3ErrorComKlima2Code13 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[2].Code[13] | [6 empty] | 6157 | 0 | 0x064020d5
SS3ErrorComKlima2Code14 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[2].Code[14] | [6 empty] | 6157 | 0 | 0x064020d6
SS3ErrorComKlima2Code15 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[2].Code[15] | [6 empty] | 6157 | 0 | 0x064020d7
SS3ErrorComKlima2Code1 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[2].Code[1] | [6 empty] | 6157 | 0 | 0x064020d8
SS3ErrorComKlima2Code2 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[2].Code[2] | [6 empty] | 6157 | 0 | 0x064020d9
SS3ErrorComKlima2Code3 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[2].Code[3] | [6 empty] | 6157 | 0 | 0x064020da
SS3ErrorComKlima2Code4 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[2].Code[4] | [6 empty] | 6157 | 0 | 0x064020db
SS3ErrorComKlima2Code5 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[2].Code[5] | [6 empty] | 6157 | 0 | 0x064020dc
SS3ErrorComKlima2Code6 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[2].Code[6] | [6 empty] | 6157 | 0 | 0x064020dd
SS3ErrorComKlima2Code7 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[2].Code[7] | [6 empty] | 6157 | 0 | 0x064020de
SS3ErrorComKlima2Code8 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[2].Code[8] | [6 empty] | 6157 | 0 | 0x064020df
SS3ErrorComKlima2Code9 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[2].Code[9] | [6 empty] | 6157 | 0 | 0x064020e0
SS3ErrorComKlima2Error | DIGITAL | IOD_SS3 | SS3:.ErrorComKlima[2].Error | [6 empty] | 6157 | 0 | 0x064020f0
SS3ErrorComKlima2Status | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Status | [6 empty] | 6157 | 0 | 0x06402100
SS3ErrorComKlima3Code0 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[3].Code[0] | [6 empty] | 6157 | 0 | 0x06402101
SS3ErrorComKlima3Code10 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[3].Code[10] | [6 empty] | 6157 | 0 | 0x06402102
SS3ErrorComKlima3Code11 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[3].Code[11] | [6 empty] | 6157 | 0 | 0x06402103
SS3ErrorComKlima3Code12 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[3].Code[12] | [6 empty] | 6157 | 0 | 0x06402104
SS3ErrorComKlima3Code13 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[3].Code[13] | [6 empty] | 6157 | 0 | 0x06402105
SS3ErrorComKlima3Code14 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[3].Code[14] | [6 empty] | 6157 | 0 | 0x06402106
SS3ErrorComKlima3Code15 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[3].Code[15] | [6 empty] | 6157 | 0 | 0x06402107
SS3ErrorComKlima3Code1 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[3].Code[1] | [6 empty] | 6157 | 0 | 0x06402108
SS3ErrorComKlima3Code2 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[3].Code[2] | [6 empty] | 6157 | 0 | 0x06402109
SS3ErrorComKlima3Code3 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[3].Code[3] | [6 empty] | 6157 | 0 | 0x0640210a
SS3ErrorComKlima3Code4 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[3].Code[4] | [6 empty] | 6157 | 0 | 0x0640210b
SS3ErrorComKlima3Code5 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[3].Code[5] | [6 empty] | 6157 | 0 | 0x0640210c
SS3ErrorComKlima3Code6 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[3].Code[6] | [6 empty] | 6157 | 0 | 0x0640210d
SS3ErrorComKlima3Code7 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[3].Code[7] | [6 empty] | 6157 | 0 | 0x0640210e
SS3ErrorComKlima3Code8 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[3].Code[8] | [6 empty] | 6157 | 0 | 0x0640210f
SS3ErrorComKlima3Code9 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[3].Code[9] | [6 empty] | 6157 | 0 | 0x06402110
SS3ErrorComKlima3Error | DIGITAL | IOD_SS3 | SS3:.ErrorComKlima[3].Error | [6 empty] | 6157 | 0 | 0x06402120
SS3ErrorComKlima3Status | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Status | [6 empty] | 6157 | 0 | 0x06402130
SS3ErrorComKlima4Code0 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[4].Code[0] | [6 empty] | 6157 | 0 | 0x06402131
SS3ErrorComKlima4Code10 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[4].Code[10] | [6 empty] | 6157 | 0 | 0x06402132
SS3ErrorComKlima4Code11 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[4].Code[11] | [6 empty] | 6157 | 0 | 0x06402133
SS3ErrorComKlima4Code12 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[4].Code[12] | [6 empty] | 6157 | 0 | 0x06402134
SS3ErrorComKlima4Code13 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[4].Code[13] | [6 empty] | 6157 | 0 | 0x06402135
SS3ErrorComKlima4Code14 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[4].Code[14] | [6 empty] | 6157 | 0 | 0x06402136
SS3ErrorComKlima4Code15 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[4].Code[15] | [6 empty] | 6157 | 0 | 0x06402137
SS3ErrorComKlima4Code1 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[4].Code[1] | [6 empty] | 6157 | 0 | 0x06402138
SS3ErrorComKlima4Code2 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[4].Code[2] | [6 empty] | 6157 | 0 | 0x06402139
SS3ErrorComKlima4Code3 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[4].Code[3] | [6 empty] | 6157 | 0 | 0x0640213a
SS3ErrorComKlima4Code4 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[4].Code[4] | [6 empty] | 6157 | 0 | 0x0640213b
SS3ErrorComKlima4Code5 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[4].Code[5] | [6 empty] | 6157 | 0 | 0x0640213c
SS3ErrorComKlima4Code6 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[4].Code[6] | [6 empty] | 6157 | 0 | 0x0640213d
SS3ErrorComKlima4Code7 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[4].Code[7] | [6 empty] | 6157 | 0 | 0x0640213e
SS3ErrorComKlima4Code8 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[4].Code[8] | [6 empty] | 6157 | 0 | 0x0640213f
SS3ErrorComKlima4Code9 | BYTE | IOD_SS3 | SS3:.ErrorComKlima[4].Code[9] | [6 empty] | 6157 | 0 | 0x06402140
SS3ErrCommScada2 | DIGITAL | IOD_SS3 | SS3:.ErrCommScada2 | [8 empty] | 0x06402150
SS3ComSCADA2 | DIGITAL | IOD_SS3 | SS3:.ComSCADA2 | [8 empty] | 0x06402160
SS3ErrComSCADA_Om2 | DIGITAL | IOD_SS3_disk | D2002 | [8 empty] | 0x06402170
SS3Server_A_Izpad | DIGITAL | IOD_SS3_disk | D2003 | [8 empty] | 0x06402180
SS3Server_B_Izpad | DIGITAL | IOD_SS3_disk | D2004 | [8 empty] | 0x06402190
SS3ComSCADA_stevec3 | INT | IOD_SS3_mem | I2006 | [8 empty] | 0x064021a0
SS3ComSCADA_stevec | INT | IOD_SS3_mem | I2008 | [8 empty] | 0x064021a1
SS3kom_nast_cas_izpada | INT | IOD_SS3 | SS3:.kom_nast_cas_izpada | [8 empty] | 0x064021c0
SS3ComSCADA3 | DIGITAL | IOD_SS3 | SS3:.ComSCADA3 | [8 empty] | 0x064021d0
SS3NapakaSenzorTemp4_Om | DIGITAL | IOD_SS3_disk | D5000 | [8 empty] | 0x064021e0
SS3NapakaSenzorTemp5_Om | DIGITAL | IOD_SS3_disk | D5001 | [8 empty] | 0x064021f0
SS3NapakaSenzorVlaga4_Om | DIGITAL | IOD_SS3_disk | D5002 | [8 empty] | 0x06402200
SS3NapakaSenzorVlaga5_Om | DIGITAL | IOD_SS3_disk | D5003 | [8 empty] | 0x06402210
SS3AlarmTempTIA4Previsoka_Om | DIGITAL | IOD_SS3_disk | D5004 | [8 empty] | 0x06402220
SS3AlarmTempTIA5Previsoka_Om | DIGITAL | IOD_SS3_disk | D5005 | [8 empty] | 0x06402230
SS3AlarmTempTIA4Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA4Previsoka | [6 empty] | 6157 | 0 | 0x06402240
SS3AlarmTempTIA5Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA5Previsoka | [6 empty] | 6157 | 0 | 0x06402250
SS3NapakaSenzorTemp4 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorTemp4 | [6 empty] | 6157 | 0 | 0x06402260
SS3NapakaSenzorTemp5 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorTemp5 | [6 empty] | 6157 | 0 | 0x06402270
SS3NapakaSenzorVlaga4 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorVlaga4 | [6 empty] | 6157 | 0 | 0x06402280
SS3NapakaSenzorVlaga5 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorVlaga5 | [6 empty] | 6157 | 0 | 0x06402290
SS3SKTemp4 | REAL | IOD_SS3 | SS3:.SKTemp4 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x064022a0
SS3SKTemp5 | REAL | IOD_SS3 | SS3:.SKTemp5 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x064022a1
SS3SKVlaga4 | REAL | IOD_SS3 | SS3:.SKVlaga4 | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x064022a2
SS3SKVlaga5 | REAL | IOD_SS3 | SS3:.SKVlaga5 | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 0 | 0x064022a3
SS3TempZaAlarmTIA4 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA4 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x064022a4
SS3TempZaAlarmTIA5 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA5 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x064022a5
SS3SKTemp4_Opozorilo_Zgornja_Meja | REAL | IOD_SS3_disk | R17 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x064022a6
SS3SKTemp4_Alarm_Zgornja_Meja | REAL | IOD_SS3_disk | R18 | 0 | 60 | 0 | 60 | °C | ####.# |  |  | 0x064022a7
SS3SKTemp4_Opozorilo_Omogoci | DIGITAL | IOD_SS3_disk | D5006 | [8 empty] | 0x064022b0
SS3SKTemp4_Alarm_Omogoci | DIGITAL | IOD_SS3_disk | D5007 | [8 empty] | 0x064022c0
SS3SKVlaga4_Opozorilo_Zgornja_Meja | REAL | IOD_SS3_disk | R19 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x064022d0
SS3SKVlaga4_Alarm_Zgornja_Meja | REAL | IOD_SS3_disk | R20 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x064022d1
SS3SKVlaga4_Opozorilo_Omogoci | DIGITAL | IOD_SS3_disk | D5008 | [8 empty] | 0x064022e0
SS3SKVlaga4_Alarm_Omogoci | DIGITAL | IOD_SS3_disk | D5009 | [8 empty] | 0x064022f0
SS3SKTemp5_Opozorilo_Zgornja_Meja | REAL | IOD_SS3_disk | R21 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x06402300
SS3SKTemp5_Alarm_Zgornja_Meja | REAL | IOD_SS3_disk | R22 | 0 | 60 | 0 | 60 | °C | ####.# |  |  | 0x06402301
SS3SKTemp5_Opozorilo_Omogoci | DIGITAL | IOD_SS3_disk | D5010 | [8 empty] | 0x06402310
SS3SKTemp5_Alarm_Omogoci | DIGITAL | IOD_SS3_disk | D5011 | [8 empty] | 0x06402320
SS3SKVlaga5_Opozorilo_Zgornja_Meja | REAL | IOD_SS3_disk | R23 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x06402330
SS3SKVlaga5_Alarm_Zgornja_Meja | REAL | IOD_SS3_disk | R24 | 0 | 100 | 0 | 100 | % | ####.# |  |  | 0x06402331
SS3SKVlaga5_Opozorilo_Omogoci | DIGITAL | IOD_SS3_disk | D5012 | [8 empty] | 0x06402340
SS3SKVlaga5_Alarm_Omogoci | DIGITAL | IOD_SS3_disk | D5013 | [8 empty] | 0x06402350
SS3SKTempServSoba1Povpr | REAL | IOD_SS3 | SS3:.SKTempServSoba1Povpr | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06402360
SS3SKTempServSoba2Povpr | REAL | IOD_SS3 | SS3:.SKTempServSoba2Povpr | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06402361
SS3TempZaAlarmTIA124 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA124 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06402362
SS3TempZaAlarmTIA35 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA35 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 0 | 0x06402363
SS3AlarmTempTIA124Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA124Previsoka | [6 empty] | 6157 | 0 | 0x06402370
SS3AlarmTempTIA35Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA35Previsoka | [6 empty] | 6157 | 0 | 0x06402380
SS3AlarmTempTIA124Previsoka_Om | DIGITAL | IOD_SS3_disk | D5014 | [8 empty] | 0x06402390
SS3AlarmTempTIA35Previsoka_Om | DIGITAL | IOD_SS3_disk | D5015 | [8 empty] | 0x064023a0
A2SS3_omogoci_sms | DIGITAL | IOD_SS3_disk | D5020[200] | [8 empty] | 0x064023b0
B2SS3_omogoci_sms | DIGITAL | IOD_SS3_disk | D5220[200] | [8 empty] | 0x064023c0

## variable_1
SS3AktualniSetPointTemp1_2 | REAL | IOD_SS3 | SS3:.AktualniSetPointTemp1_2
SS3AktualniSetPointTemp3_4 | REAL | IOD_SS3 | SS3:.AktualniSetPointTemp3_4
SS3AlarmKlimat1_Napaka | DIGITAL | IOD_SS3 | SS3:.AlarmKlimat1_Napaka
SS3AlarmKlimat2_Napaka | DIGITAL | IOD_SS3 | SS3:.AlarmKlimat2_Napaka
SS3AlarmKlimat3_Napaka | DIGITAL | IOD_SS3 | SS3:.AlarmKlimat3_Napaka
SS3AlarmKlimat4_Napaka | DIGITAL | IOD_SS3 | SS3:.AlarmKlimat4_Napaka
SS3AlarmLAH1_RazlitjeVode | DIGITAL | IOD_SS3 | SS3:.AlarmLAH1_RazlitjeVode
SS3AlarmLAH2_RazlitjeVode | DIGITAL | IOD_SS3 | SS3:.AlarmLAH2_RazlitjeVode
SS3AlarmSinhronizacijaNOK | DIGITAL | IOD_SS3 | SS3:.AlarmSinhronizacijaNOK
SS3AlarmTempTIA1Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA1Previsoka
SS3AlarmTempTIA2Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA2Previsoka
SS3AlarmTempTIA3Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA3Previsoka
SS3AlarmTSTemp1Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTSTemp1Previsoka
SS3AlarmTSTemp3Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTSTemp3Previsoka
SS3AlarmUPSKrmOmara_Alarm | DIGITAL | IOD_SS3 | SS3:.AlarmUPSKrmOmara_Alarm
SS3ComSCADA | DIGITAL | IOD_SS3 | SS3:.ComSCADA
SS3ComSCADA1 | DIGITAL | IOD_SS3 | SS3:.ComSCADA1
SS3DatumCasDan | INT | IOD_SS3 | SS3:.DatumCas.Dan | BYTE
SS3DatumCasLeto | INT | IOD_SS3 | SS3:.DatumCas.Leto | BYTE
SS3DatumCasLeto2 | INT | IOD_SS3 | SS3:.DatumCas.Leto2
SS3DatumCasMesec | INT | IOD_SS3 | SS3:.DatumCas.Mesec | BYTE
SS3DatumCasMinuta | INT | IOD_SS3 | SS3:.DatumCas.Minuta | BYTE
SS3DatumCasSekunda | INT | IOD_SS3 | SS3:.DatumCas.Sekunda | BYTE
SS3DatumCasUra | INT | IOD_SS3 | SS3:.DatumCas.Ura | BYTE
SS3ErrComKlima1 | DIGITAL | IOD_SS3 | SS3:.ErrComKlima[1]
SS3ErrComKlima2 | DIGITAL | IOD_SS3 | SS3:.ErrComKlima[2]
SS3ErrComKlima3 | DIGITAL | IOD_SS3 | SS3:.ErrComKlima[3]
SS3ErrComKlima4 | DIGITAL | IOD_SS3 | SS3:.ErrComKlima[4]
SS3ErrCommScada | DIGITAL | IOD_SS3 | SS3:.ErrCommScada
SS3ErrComPanelPLC | DIGITAL | IOD_SS3 | SS3:.ErrComPanelPLC
SS3ErrComPort2 | DIGITAL | IOD_SS3 | SS3:.ErrComPort2
SS3ErrorComKlima4Error | DIGITAL | IOD_SS3 | SS3:.ErrorComKlima[4].Error
SS3ErrorComKlima4Status | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Status
SS3Klima1_Onemogocena | DIGITAL | IOD_SS3 | SS3:.Klima1_Onemogocena
SS3Klima1ure | REAL | IOD_SS3 | SS3:.Klima1ure
SS3Klima2_Onemogocena | DIGITAL | IOD_SS3 | SS3:.Klima2_Onemogocena
SS3Klima2ure | REAL | IOD_SS3 | SS3:.Klima2ure
SS3Klima3_Onemogocena | DIGITAL | IOD_SS3 | SS3:.Klima3_Onemogocena
SS3Klima3ure | REAL | IOD_SS3 | SS3:.Klima3ure
SS3Klima4_Onemogocena | DIGITAL | IOD_SS3 | SS3:.Klima4_Onemogocena
SS3Klima4ure | REAL | IOD_SS3 | SS3:.Klima4ure
SS3Klima1Deluje | DIGITAL | IOD_SS3 | SS3:.Klima[1].Deluje
SS3Klima1EnergySaving | DIGITAL | IOD_SS3 | SS3:.Klima[1].EnergySaving
SS3Klima1GrelecStatus | INT | IOD_SS3 | SS3:.Klima[1].GrelecStatus | BYTE
SS3Klima1IzhodniVentStatus | INT | IOD_SS3 | SS3:.Klima[1].IzhodniVentStatus | BYTE
SS3Klima1KompresorStatus | INT | IOD_SS3 | SS3:.Klima[1].KompresorStatus | BYTE
SS3Klima1Napaka | DIGITAL | IOD_SS3 | SS3:.Klima[1].Napaka
SS3Klima1NastTempProstora | REAL | IOD_SS3 | SS3:.Klima[1].NastTempProstora
SS3Klima1NastVlaznost | REAL | IOD_SS3 | SS3:.Klima[1].NastVlaznost
SS3Klima1ObratovalneUre | REAL | IOD_SS3 | SS3:.Klima[1].ObratovalneUre
SS3Klima1OnOffEnablingBySupervisor | DIGITAL | IOD_SS3 | SS3:.Klima[1].OnOffEnablingBySupervisor
SS3Klima1Razvlazevanje | DIGITAL | IOD_SS3 | SS3:.Klima[1].Razvlazevanje
SS3Klima1RemoteOFFtoOutput | DIGITAL | IOD_SS3 | SS3:.Klima[1].RemoteOFFtoOutput
SS3Klima1RemoteOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[1].RemoteOnOff
SS3Klima1RocniIzklop | DIGITAL | IOD_SS3 | SS3:.Klima[1].RocniIzklop
SS3Klima1SenzorjiStatus | DIGITAL | IOD_SS3 | SS3:.Klima[1].SenzorjiStatus
SS3Klima1TemperaturaProstora | REAL | IOD_SS3 | SS3:.Klima[1].TemperaturaProstora
SS3Klima1UnitOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[1].UnitOnOff
SS3Klima1VentilGretjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[1].VentilGretjeOdpiranje
SS3Klima1VentilGretjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[1].VentilGretjeZapiranje
SS3Klima1VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[1].VentilHlajenjeOdpiranje
SS3Klima1VentilHlajenjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[1].VentilHlajenjeZapiranje
SS3Klima1Vlazenje | DIGITAL | IOD_SS3 | SS3:.Klima[1].Vlazenje
SS3Klima1VlazilecStatus | INT | IOD_SS3 | SS3:.Klima[1].VlazilecStatus | BYTE
SS3Klima1VlaznostProstora | REAL | IOD_SS3 | SS3:.Klima[1].VlaznostProstora
SS3Klima2Deluje | DIGITAL | IOD_SS3 | SS3:.Klima[2].Deluje
SS3Klima2EnergySaving | DIGITAL | IOD_SS3 | SS3:.Klima[2].EnergySaving
SS3Klima2GrelecStatus | INT | IOD_SS3 | SS3:.Klima[2].GrelecStatus | BYTE
SS3Klima2IzhodniVentStatus | INT | IOD_SS3 | SS3:.Klima[2].IzhodniVentStatus | BYTE
SS3Klima2KompresorStatus | INT | IOD_SS3 | SS3:.Klima[2].KompresorStatus | BYTE
SS3Klima2Napaka | DIGITAL | IOD_SS3 | SS3:.Klima[2].Napaka
SS3Klima2NastTempProstora | REAL | IOD_SS3 | SS3:.Klima[2].NastTempProstora
SS3Klima2NastVlaznost | REAL | IOD_SS3 | SS3:.Klima[2].NastVlaznost
SS3Klima2ObratovalneUre | REAL | IOD_SS3 | SS3:.Klima[2].ObratovalneUre
SS3Klima2OnOffEnablingBySupervisor | DIGITAL | IOD_SS3 | SS3:.Klima[2].OnOffEnablingBySupervisor
SS3Klima2Razvlazevanje | DIGITAL | IOD_SS3 | SS3:.Klima[2].Razvlazevanje
SS3Klima2RemoteOFFtoOutput | DIGITAL | IOD_SS3 | SS3:.Klima[2].RemoteOFFtoOutput
SS3Klima2RemoteOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[2].RemoteOnOff
SS3Klima2RocniIzklop | DIGITAL | IOD_SS3 | SS3:.Klima[2].RocniIzklop
SS3Klima2SenzorjiStatus | DIGITAL | IOD_SS3 | SS3:.Klima[2].SenzorjiStatus
SS3Klima2TemperaturaProstora | REAL | IOD_SS3 | SS3:.Klima[2].TemperaturaProstora
SS3Klima2UnitOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[2].UnitOnOff
SS3Klima2VentilGretjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[2].VentilGretjeOdpiranje
SS3Klima2VentilGretjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[2].VentilGretjeZapiranje
SS3Klima2VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[2].VentilHlajenjeOdpiranje
SS3Klima2VentilHlajenjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[2].VentilHlajenjeZapiranje
SS3Klima2Vlazenje | DIGITAL | IOD_SS3 | SS3:.Klima[2].Vlazenje
SS3Klima2VlazilecStatus | INT | IOD_SS3 | SS3:.Klima[2].VlazilecStatus | BYTE
SS3Klima2VlaznostProstora | REAL | IOD_SS3 | SS3:.Klima[2].VlaznostProstora
SS3Klima3Deluje | DIGITAL | IOD_SS3 | SS3:.Klima[3].Deluje
SS3Klima3EnergySaving | DIGITAL | IOD_SS3 | SS3:.Klima[3].EnergySaving
SS3Klima3GrelecStatus | INT | IOD_SS3 | SS3:.Klima[3].GrelecStatus | BYTE
SS3Klima3IzhodniVentStatus | INT | IOD_SS3 | SS3:.Klima[3].IzhodniVentStatus | BYTE
SS3Klima3KompresorStatus | INT | IOD_SS3 | SS3:.Klima[3].KompresorStatus | BYTE
SS3Klima3Napaka | DIGITAL | IOD_SS3 | SS3:.Klima[3].Napaka
SS3Klima3NastTempProstora | REAL | IOD_SS3 | SS3:.Klima[3].NastTempProstora
SS3Klima3NastVlaznost | REAL | IOD_SS3 | SS3:.Klima[3].NastVlaznost
SS3Klima3ObratovalneUre | REAL | IOD_SS3 | SS3:.Klima[3].ObratovalneUre
SS3Klima3OnOffEnablingBySupervisor | DIGITAL | IOD_SS3 | SS3:.Klima[3].OnOffEnablingBySupervisor
SS3Klima3Razvlazevanje | DIGITAL | IOD_SS3 | SS3:.Klima[3].Razvlazevanje
SS3Klima3RemoteOFFtoOutput | DIGITAL | IOD_SS3 | SS3:.Klima[3].RemoteOFFtoOutput
SS3Klima3RemoteOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[3].RemoteOnOff
SS3Klima3RocniIzklop | DIGITAL | IOD_SS3 | SS3:.Klima[3].RocniIzklop
SS3Klima3SenzorjiStatus | DIGITAL | IOD_SS3 | SS3:.Klima[3].SenzorjiStatus
SS3Klima3TemperaturaProstora | REAL | IOD_SS3 | SS3:.Klima[3].TemperaturaProstora
SS3Klima3UnitOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[3].UnitOnOff
SS3Klima3VentilGretjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[3].VentilGretjeOdpiranje
SS3Klima3VentilGretjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[3].VentilGretjeZapiranje
SS3Klima3VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[3].VentilHlajenjeOdpiranje
SS3Klima3VentilHlajenjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[3].VentilHlajenjeZapiranje
SS3Klima3Vlazenje | DIGITAL | IOD_SS3 | SS3:.Klima[3].Vlazenje
SS3Klima3VlazilecStatus | INT | IOD_SS3 | SS3:.Klima[3].VlazilecStatus | BYTE
SS3Klima3VlaznostProstora | REAL | IOD_SS3 | SS3:.Klima[3].VlaznostProstora
SS3Klima4Deluje | DIGITAL | IOD_SS3 | SS3:.Klima[4].Deluje
SS3Klima4EnergySaving | DIGITAL | IOD_SS3 | SS3:.Klima[4].EnergySaving
SS3Klima4GrelecStatus | INT | IOD_SS3 | SS3:.Klima[4].GrelecStatus | BYTE
SS3Klima4IzhodniVentStatus | INT | IOD_SS3 | SS3:.Klima[4].IzhodniVentStatus | BYTE
SS3Klima4KompresorStatus | INT | IOD_SS3 | SS3:.Klima[4].KompresorStatus | BYTE
SS3Klima4Napaka | DIGITAL | IOD_SS3 | SS3:.Klima[4].Napaka
SS3Klima4NastTempProstora | REAL | IOD_SS3 | SS3:.Klima[4].NastTempProstora
SS3Klima4NastVlaznost | REAL | IOD_SS3 | SS3:.Klima[4].NastVlaznost
SS3Klima4ObratovalneUre | REAL | IOD_SS3 | SS3:.Klima[4].ObratovalneUre
SS3Klima4OnOffEnablingBySupervisor | DIGITAL | IOD_SS3 | SS3:.Klima[4].OnOffEnablingBySupervisor
SS3Klima4Razvlazevanje | DIGITAL | IOD_SS3 | SS3:.Klima[4].Razvlazevanje
SS3Klima4RemoteOFFtoOutput | DIGITAL | IOD_SS3 | SS3:.Klima[4].RemoteOFFtoOutput
SS3Klima4RemoteOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[4].RemoteOnOff
SS3Klima4RocniIzklop | DIGITAL | IOD_SS3 | SS3:.Klima[4].RocniIzklop
SS3Klima4SenzorjiStatus | DIGITAL | IOD_SS3 | SS3:.Klima[4].SenzorjiStatus
SS3Klima4TemperaturaProstora | REAL | IOD_SS3 | SS3:.Klima[4].TemperaturaProstora
SS3Klima4UnitOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[4].UnitOnOff
SS3Klima4VentilGretjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[4].VentilGretjeOdpiranje
SS3Klima4VentilGretjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[4].VentilGretjeZapiranje
SS3Klima4VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[4].VentilHlajenjeOdpiranje
SS3Klima4VentilHlajenjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[4].VentilHlajenjeZapiranje
SS3Klima4Vlazenje | DIGITAL | IOD_SS3 | SS3:.Klima[4].Vlazenje
SS3Klima4VlazilecStatus | INT | IOD_SS3 | SS3:.Klima[4].VlazilecStatus | BYTE
SS3Klima4VlaznostProstora | REAL | IOD_SS3 | SS3:.Klima[4].VlaznostProstora
SS3KlimaError1AlarmKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].AlarmKompresor1
SS3KlimaError1AlarmKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].AlarmKompresor2
SS3KlimaError1FaultyEprom | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].FaultyEprom
SS3KlimaError1FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].FenThermalCutout
SS3KlimaError1GeneralAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].GeneralAlarm
SS3KlimaError1Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].Kompresor1naMejiStevilaObrUr
SS3KlimaError1Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].Kompresor2naMejiStevilaObrUr
SS3KlimaError1Kond1FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].Kond1FenThermalCutout
SS3KlimaError1Kond2FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].Kond2FenThermalCutout
SS3KlimaError1NapakaPriPretokuVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaPriPretokuVode
SS3KlimaError1NapakaPriPretokuZraka | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaPriPretokuZraka
SS3KlimaError1NapakaSenzorPovratVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorPovratVode
SS3KlimaError1NapakaSenzorPritiska | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorPritiska
SS3KlimaError1NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorTempIzpiha
SS3KlimaError1NapakaSenzorTempProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorTempProstora
SS3KlimaError1NapakaSenzorVlaznosti | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorVlaznosti
SS3KlimaError1NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorZunanjeTemp
SS3KlimaError1NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaTSTemperaturaProstora
SS3KlimaError1NiTokaVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NiTokaVVlazilcu
SS3KlimaError1NiVodeVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NiVodeVVlazilcu
SS3KlimaError1NizekPritiskKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NizekPritiskKompresor1
SS3KlimaError1NizekPritiskKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NizekPritiskKompresor2
SS3KlimaError1NizkaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NizkaTempPovratneVode
SS3KlimaError1NizkaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NizkaTempVProstoru
SS3KlimaError1NizkaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NizkaVlaznost
SS3KlimaError1PozarniAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].PozarniAlarm
SS3KlimaError1StoppedByAlarms | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].StoppedByAlarms
SS3KlimaError1TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].TermZascInVisokPritiskKompr1
SS3KlimaError1TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].TermZascInVisokPritiskKompr2
SS3KlimaError1ThermalCutoutHeater1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].ThermalCutoutHeater1
SS3KlimaError1ThermalCutoutHeater2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].ThermalCutoutHeater2
SS3KlimaError1VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VentilatorNaMejiStevilaObrUr
SS3KlimaError1VisokaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokaTempPovratneVode
SS3KlimaError1VisokaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokaTempVProstoru
SS3KlimaError1VisokaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokaVlaznost
SS3KlimaError1VisokPritiskVKrogu1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokPritiskVKrogu1
SS3KlimaError1VisokPritiskVKrogu2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokPritiskVKrogu2
SS3KlimaError1VisokTokVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokTokVVlazilcu
SS3KlimaError1VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VlazilecnaMejiStevilaObrUr
SS3KlimaError1ZamasenFilter | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].ZamasenFilter
SS3KlimaError2AlarmKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].AlarmKompresor1
SS3KlimaError2AlarmKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].AlarmKompresor2
SS3KlimaError2FaultyEprom | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].FaultyEprom
SS3KlimaError2FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].FenThermalCutout
SS3KlimaError2GeneralAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].GeneralAlarm
SS3KlimaError2Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].Kompresor1naMejiStevilaObrUr
SS3KlimaError2Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].Kompresor2naMejiStevilaObrUr
SS3KlimaError2Kond1FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].Kond1FenThermalCutout
SS3KlimaError2Kond2FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].Kond2FenThermalCutout
SS3KlimaError2NapakaPriPretokuVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaPriPretokuVode
SS3KlimaError2NapakaPriPretokuZraka | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaPriPretokuZraka
SS3KlimaError2NapakaSenzorPovratVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorPovratVode
SS3KlimaError2NapakaSenzorPritiska | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorPritiska
SS3KlimaError2NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorTempIzpiha
SS3KlimaError2NapakaSenzorTempProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorTempProstora
SS3KlimaError2NapakaSenzorVlaznosti | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorVlaznosti
SS3KlimaError2NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorZunanjeTemp
SS3KlimaError2NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaTSTemperaturaProstora
SS3KlimaError2NiTokaVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NiTokaVVlazilcu
SS3KlimaError2NiVodeVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NiVodeVVlazilcu
SS3KlimaError2NizekPritiskKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NizekPritiskKompresor1
SS3KlimaError2NizekPritiskKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NizekPritiskKompresor2
SS3KlimaError2NizkaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NizkaTempPovratneVode
SS3KlimaError2NizkaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NizkaTempVProstoru
SS3KlimaError2NizkaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NizkaVlaznost
SS3KlimaError2PozarniAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].PozarniAlarm
SS3KlimaError2StoppedByAlarms | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].StoppedByAlarms
SS3KlimaError2TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].TermZascInVisokPritiskKompr1
SS3KlimaError2TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].TermZascInVisokPritiskKompr2
SS3KlimaError2ThermalCutoutHeater1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].ThermalCutoutHeater1
SS3KlimaError2ThermalCutoutHeater2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].ThermalCutoutHeater2
SS3KlimaError2VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VentilatorNaMejiStevilaObrUr
SS3KlimaError2VisokaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokaTempPovratneVode
SS3KlimaError2VisokaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokaTempVProstoru
SS3KlimaError2VisokaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokaVlaznost
SS3KlimaError2VisokPritiskVKrogu1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokPritiskVKrogu1
SS3KlimaError2VisokPritiskVKrogu2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokPritiskVKrogu2
SS3KlimaError2VisokTokVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokTokVVlazilcu
SS3KlimaError2VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VlazilecnaMejiStevilaObrUr
SS3KlimaError2ZamasenFilter | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].ZamasenFilter
SS3KlimaError3AlarmKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].AlarmKompresor1
SS3KlimaError3AlarmKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].AlarmKompresor2
SS3KlimaError3FaultyEprom | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].FaultyEprom
SS3KlimaError3FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].FenThermalCutout
SS3KlimaError3GeneralAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].GeneralAlarm
SS3KlimaError3Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].Kompresor1naMejiStevilaObrUr
SS3KlimaError3Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].Kompresor2naMejiStevilaObrUr
SS3KlimaError3Kond1FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].Kond1FenThermalCutout
SS3KlimaError3Kond2FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].Kond2FenThermalCutout
SS3KlimaError3NapakaPriPretokuVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaPriPretokuVode
SS3KlimaError3NapakaPriPretokuZraka | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaPriPretokuZraka
SS3KlimaError3NapakaSenzorPovratVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorPovratVode
SS3KlimaError3NapakaSenzorPritiska | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorPritiska
SS3KlimaError3NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorTempIzpiha
SS3KlimaError3NapakaSenzorTempProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorTempProstora
SS3KlimaError3NapakaSenzorVlaznosti | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorVlaznosti
SS3KlimaError3NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorZunanjeTemp
SS3KlimaError3NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaTSTemperaturaProstora
SS3KlimaError3NiTokaVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NiTokaVVlazilcu
SS3KlimaError3NiVodeVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NiVodeVVlazilcu
SS3KlimaError3NizekPritiskKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NizekPritiskKompresor1
SS3KlimaError3NizekPritiskKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NizekPritiskKompresor2
SS3KlimaError3NizkaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NizkaTempPovratneVode
SS3KlimaError3NizkaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NizkaTempVProstoru
SS3KlimaError3NizkaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NizkaVlaznost
SS3KlimaError3PozarniAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].PozarniAlarm
SS3KlimaError3StoppedByAlarms | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].StoppedByAlarms
SS3KlimaError3TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].TermZascInVisokPritiskKompr1
SS3KlimaError3TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].TermZascInVisokPritiskKompr2
SS3KlimaError3ThermalCutoutHeater1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].ThermalCutoutHeater1
SS3KlimaError3ThermalCutoutHeater2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].ThermalCutoutHeater2
SS3KlimaError3VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VentilatorNaMejiStevilaObrUr
SS3KlimaError3VisokaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokaTempPovratneVode
SS3KlimaError3VisokaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokaTempVProstoru
SS3KlimaError3VisokaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokaVlaznost
SS3KlimaError3VisokPritiskVKrogu1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokPritiskVKrogu1
SS3KlimaError3VisokPritiskVKrogu2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokPritiskVKrogu2
SS3KlimaError3VisokTokVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokTokVVlazilcu
SS3KlimaError3VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VlazilecnaMejiStevilaObrUr
SS3KlimaError3ZamasenFilter | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].ZamasenFilter
SS3KlimaError4AlarmKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].AlarmKompresor1
SS3KlimaError4AlarmKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].AlarmKompresor2
SS3KlimaError4FaultyEprom | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].FaultyEprom
SS3KlimaError4FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].FenThermalCutout
SS3KlimaError4GeneralAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].GeneralAlarm
SS3KlimaError4Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].Kompresor1naMejiStevilaObrUr
SS3KlimaError4Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].Kompresor2naMejiStevilaObrUr
SS3KlimaError4Kond1FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].Kond1FenThermalCutout
SS3KlimaError4Kond2FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].Kond2FenThermalCutout
SS3KlimaError4NapakaPriPretokuVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaPriPretokuVode
SS3KlimaError4NapakaPriPretokuZraka | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaPriPretokuZraka
SS3KlimaError4NapakaSenzorPovratVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorPovratVode
SS3KlimaError4NapakaSenzorPritiska | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorPritiska
SS3KlimaError4NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorTempIzpiha
SS3KlimaError4NapakaSenzorTempProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorTempProstora
SS3KlimaError4NapakaSenzorVlaznosti | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorVlaznosti
SS3KlimaError4NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorZunanjeTemp
SS3KlimaError4NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaTSTemperaturaProstora
SS3KlimaError4NiTokaVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NiTokaVVlazilcu
SS3KlimaError4NiVodeVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NiVodeVVlazilcu
SS3KlimaError4NizekPritiskKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NizekPritiskKompresor1
SS3KlimaError4NizekPritiskKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NizekPritiskKompresor2
SS3KlimaError4NizkaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NizkaTempPovratneVode
SS3KlimaError4NizkaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NizkaTempVProstoru
SS3KlimaError4NizkaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NizkaVlaznost
SS3KlimaError4PozarniAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].PozarniAlarm
SS3KlimaError4StoppedByAlarms | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].StoppedByAlarms
SS3KlimaError4TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].TermZascInVisokPritiskKompr1
SS3KlimaError4TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].TermZascInVisokPritiskKompr2
SS3KlimaError4ThermalCutoutHeater1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].ThermalCutoutHeater1
SS3KlimaError4ThermalCutoutHeater2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].ThermalCutoutHeater2
SS3KlimaError4VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VentilatorNaMejiStevilaObrUr
SS3KlimaError4VisokaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokaTempPovratneVode
SS3KlimaError4VisokaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokaTempVProstoru
SS3KlimaError4VisokaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokaVlaznost
SS3KlimaError4VisokPritiskVKrogu1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokPritiskVKrogu1
SS3KlimaError4VisokPritiskVKrogu2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokPritiskVKrogu2
SS3KlimaError4VisokTokVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokTokVVlazilcu
SS3KlimaError4VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VlazilecnaMejiStevilaObrUr
SS3KlimaError4ZamasenFilter | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].ZamasenFilter
SS3NacDelovanjaKlime1_2_Avtomatsko | DIGITAL | IOD_SS3 | SS3:.NacDelovanjaKlime1_2_Avtomatsko
SS3NacDelovanjaKlime3_4_Avtomatsko | DIGITAL | IOD_SS3 | SS3:.NacDelovanjaKlime3_4_Avtomatsko
SS3NapakaSenzorTemp1 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorTemp1
SS3NapakaSenzorTemp2 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorTemp2
SS3NapakaSenzorTemp3 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorTemp3
SS3NapakaSenzorVlaga1 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorVlaga1
SS3NapakaSenzorVlaga2 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorVlaga2
SS3NapakaSenzorVlaga3 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorVlaga3
SS3NastaviCasNaKrmilniku | DIGITAL | IOD_SS3 | SS3:.NastaviCasNaKrmilniku
SS3NastavitevUreKrUspesna | DIGITAL | IOD_SS3 | SS3:.NastavitevUreKrUspesna
SS3OpozoriloBaterijaPLC | DIGITAL | IOD_SS3 | SS3:.OpozoriloBaterijaPLC
SS3OsveziAlarmePanel | DIGITAL | IOD_SS3 | SS3:.OsveziAlarmePanel
SS3RocniVklopKlima1 | DIGITAL | IOD_SS3 | SS3:.RocniVklopKlima1
SS3RocniVklopKlima2 | DIGITAL | IOD_SS3 | SS3:.RocniVklopKlima2
SS3RocniVklopKlima3 | DIGITAL | IOD_SS3 | SS3:.RocniVklopKlima3
SS3RocniVklopKlima4 | DIGITAL | IOD_SS3 | SS3:.RocniVklopKlima4
SS3SinhronizacijaPanelOK | DIGITAL | IOD_SS3 | SS3:.SinhronizacijaPanelOK
SS3SinhronizirajCas_Panel | DIGITAL | IOD_SS3 | SS3:.SinhronizirajCas_Panel
SS3SKTemp1 | REAL | IOD_SS3 | SS3:.SKTemp1
SS3SKTemp2 | REAL | IOD_SS3 | SS3:.SKTemp2
SS3SKTemp3 | REAL | IOD_SS3 | SS3:.SKTemp3
SS3SkupneNapakeNaprav_Klima1 | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_Klima1
SS3SkupneNapakeNaprav_Klima2 | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_Klima2
SS3SkupneNapakeNaprav_Klima3 | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_Klima3
SS3SkupneNapakeNaprav_Klima4 | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_Klima4
SS3SkupneNapakeNaprav_Komunikacija | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_Komunikacija
SS3SkupneNapakeNaprav_TempVlaga | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_TempVlaga
SS3SKVlaga1 | REAL | IOD_SS3 | SS3:.SKVlaga1
SS3SKVlaga2 | REAL | IOD_SS3 | SS3:.SKVlaga2
SS3SKVlaga3 | REAL | IOD_SS3 | SS3:.SKVlaga3
SS3StanjeKlimat1_Delovanje | DIGITAL | IOD_SS3 | SS3:.StanjeKlimat1_Delovanje
SS3StanjeKlimat2_Delovanje | DIGITAL | IOD_SS3 | SS3:.StanjeKlimat2_Delovanje
SS3StanjeKlimat3_Delovanje | DIGITAL | IOD_SS3 | SS3:.StanjeKlimat3_Delovanje
SS3StanjeKlimat4_Delovanje | DIGITAL | IOD_SS3 | SS3:.StanjeKlimat4_Delovanje
SS3StanjeUPSKrmOmara_BaterijskiNacin | DIGITAL | IOD_SS3 | SS3:.StanjeUPSKrmOmara_BaterijskiNacin
SS3StanjeUPSKrmOmara_Polnjenje | DIGITAL | IOD_SS3 | SS3:.StanjeUPSKrmOmara_Polnjenje
SS3StUrZaPreklopKlim1_2 | INT | IOD_SS3 | SS3:.StUrZaPreklopKlim1_2
SS3StUrZaPreklopKlim3_4 | INT | IOD_SS3 | SS3:.StUrZaPreklopKlim3_4
SS3TempZaAlarm1_2 | REAL | IOD_SS3 | SS3:.TempZaAlarm1_2
SS3TempZaAlarm3_4 | REAL | IOD_SS3 | SS3:.TempZaAlarm3_4
SS3TempZaAlarmTIA1 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA1
SS3TempZaAlarmTIA2 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA2
SS3TempZaAlarmTIA3 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA3
SS3TempZaVklopObehKlim1_2 | REAL | IOD_SS3 | SS3:.TempZaVklopObehKlim1_2
SS3TempZaVklopObehKlim3_4 | REAL | IOD_SS3 | SS3:.TempZaVklopObehKlim3_4
SS3UPSstatus_Prikaz_PanelSCADA | INT | IOD_SS3 | SS3:.UPSstatus_Prikaz_PanelSCADA | BYTE
SS3UserCurrentLevel | INT | IOD_SS3 | SS3:.UserCurrentLevel | BYTE
SS3UserLoggedIn | DIGITAL | IOD_SS3 | SS3:.UserLoggedIn
SS3UserName | STRING | IOD_SS3 | SS3:.UserName
SS3XVH_AlarmOn | DIGITAL | IOD_SS3 | SS3:.XVH_AlarmOn
SS3Klimat1_Vklop | DIGITAL | IOD_SS3 | SS3:.Klimat1_Vklop
SS3Klimat2_Vklop | DIGITAL | IOD_SS3 | SS3:.Klimat2_Vklop
SS3Klimat3_Vklop | DIGITAL | IOD_SS3 | SS3:.Klimat3_Vklop
SS3Klimat4_Vklop | DIGITAL | IOD_SS3 | SS3:.Klimat4_Vklop
SS3Date_Time0 | STRING | IOD_SS3 | SS3:.Date_Time[0]
SS3Date_Time1 | STRING | IOD_SS3 | SS3:.Date_Time[1]
SS3Date_Time2 | STRING | IOD_SS3 | SS3:.Date_Time[2]
SS3Date_Time3 | STRING | IOD_SS3 | SS3:.Date_Time[3]
SS3ErrorComKlima1Code0 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[0] | BYTE
SS3ErrorComKlima1Code10 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[10] | BYTE
SS3ErrorComKlima1Code11 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[11] | BYTE
SS3ErrorComKlima1Code12 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[12] | BYTE
SS3ErrorComKlima1Code13 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[13] | BYTE
SS3ErrorComKlima1Code14 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[14] | BYTE
SS3ErrorComKlima1Code15 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[15] | BYTE
SS3ErrorComKlima1Code1 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[1] | BYTE
SS3ErrorComKlima1Code2 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[2] | BYTE
SS3ErrorComKlima1Code3 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[3] | BYTE
SS3ErrorComKlima1Code4 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[4] | BYTE
SS3ErrorComKlima1Code5 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[5] | BYTE
SS3ErrorComKlima1Code6 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[6] | BYTE
SS3ErrorComKlima1Code7 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[7] | BYTE
SS3ErrorComKlima1Code8 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[8] | BYTE
SS3ErrorComKlima1Code9 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[9] | BYTE
SS3ErrorComKlima1Error | DIGITAL | IOD_SS3 | SS3:.ErrorComKlima[1].Error
SS3ErrorComKlima1Status | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Status
SS3ErrorComKlima2Code0 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[0] | BYTE
SS3ErrorComKlima2Code10 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[10] | BYTE
SS3ErrorComKlima2Code11 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[11] | BYTE
SS3ErrorComKlima2Code12 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[12] | BYTE
SS3ErrorComKlima2Code13 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[13] | BYTE
SS3ErrorComKlima2Code14 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[14] | BYTE
SS3ErrorComKlima2Code15 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[15] | BYTE
SS3ErrorComKlima2Code1 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[1] | BYTE
SS3ErrorComKlima2Code2 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[2] | BYTE
SS3ErrorComKlima2Code3 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[3] | BYTE
SS3ErrorComKlima2Code4 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[4] | BYTE
SS3ErrorComKlima2Code5 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[5] | BYTE
SS3ErrorComKlima2Code6 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[6] | BYTE
SS3ErrorComKlima2Code7 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[7] | BYTE
SS3ErrorComKlima2Code8 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[8] | BYTE
SS3ErrorComKlima2Code9 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[9] | BYTE
SS3ErrorComKlima2Error | DIGITAL | IOD_SS3 | SS3:.ErrorComKlima[2].Error
SS3ErrorComKlima2Status | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Status
SS3ErrorComKlima3Code0 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[0] | BYTE
SS3ErrorComKlima3Code10 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[10] | BYTE
SS3ErrorComKlima3Code11 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[11] | BYTE
SS3ErrorComKlima3Code12 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[12] | BYTE
SS3ErrorComKlima3Code13 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[13] | BYTE
SS3ErrorComKlima3Code14 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[14] | BYTE
SS3ErrorComKlima3Code15 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[15] | BYTE
SS3ErrorComKlima3Code1 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[1] | BYTE
SS3ErrorComKlima3Code2 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[2] | BYTE
SS3ErrorComKlima3Code3 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[3] | BYTE
SS3ErrorComKlima3Code4 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[4] | BYTE
SS3ErrorComKlima3Code5 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[5] | BYTE
SS3ErrorComKlima3Code6 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[6] | BYTE
SS3ErrorComKlima3Code7 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[7] | BYTE
SS3ErrorComKlima3Code8 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[8] | BYTE
SS3ErrorComKlima3Code9 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[9] | BYTE
SS3ErrorComKlima3Error | DIGITAL | IOD_SS3 | SS3:.ErrorComKlima[3].Error
SS3ErrorComKlima3Status | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Status
SS3ErrorComKlima4Code0 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[0] | BYTE
SS3ErrorComKlima4Code10 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[10] | BYTE
SS3ErrorComKlima4Code11 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[11] | BYTE
SS3ErrorComKlima4Code12 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[12] | BYTE
SS3ErrorComKlima4Code13 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[13] | BYTE
SS3ErrorComKlima4Code14 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[14] | BYTE
SS3ErrorComKlima4Code15 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[15] | BYTE
SS3ErrorComKlima4Code1 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[1] | BYTE
SS3ErrorComKlima4Code2 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[2] | BYTE
SS3ErrorComKlima4Code3 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[3] | BYTE
SS3ErrorComKlima4Code4 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[4] | BYTE
SS3ErrorComKlima4Code5 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[5] | BYTE
SS3ErrorComKlima4Code6 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[6] | BYTE
SS3ErrorComKlima4Code7 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[7] | BYTE
SS3ErrorComKlima4Code8 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[8] | BYTE
SS3ErrorComKlima4Code9 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[9] | BYTE
SS3ErrCommScada2 | DIGITAL | IOD_SS3 | SS3:.ErrCommScada2
SS3ComSCADA2 | DIGITAL | IOD_SS3 | SS3:.ComSCADA2
SS3kom_nast_cas_izpada | INT | IOD_SS3 | SS3:.kom_nast_cas_izpada
SS3ComSCADA3 | DIGITAL | IOD_SS3 | SS3:.ComSCADA3
SS3AlarmTempTIA4Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA4Previsoka
SS3AlarmTempTIA5Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA5Previsoka
SS3NapakaSenzorTemp4 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorTemp4
SS3NapakaSenzorTemp5 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorTemp5
SS3NapakaSenzorVlaga4 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorVlaga4
SS3NapakaSenzorVlaga5 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorVlaga5
SS3SKTemp4 | REAL | IOD_SS3 | SS3:.SKTemp4
SS3SKTemp5 | REAL | IOD_SS3 | SS3:.SKTemp5
SS3SKVlaga4 | REAL | IOD_SS3 | SS3:.SKVlaga4
SS3SKVlaga5 | REAL | IOD_SS3 | SS3:.SKVlaga5
SS3TempZaAlarmTIA4 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA4
SS3TempZaAlarmTIA5 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA5
SS3SKTempServSoba1Povpr | REAL | IOD_SS3 | SS3:.SKTempServSoba1Povpr
SS3SKTempServSoba2Povpr | REAL | IOD_SS3 | SS3:.SKTempServSoba2Povpr
SS3TempZaAlarmTIA124 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA124
SS3TempZaAlarmTIA35 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA35
SS3AlarmTempTIA124Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA124Previsoka
SS3AlarmTempTIA35Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA35Previsoka

## variable_2
SS3AlarmKlimat1_Napaka | DIGITAL | IOD_SS3 | SS3:.AlarmKlimat1_Napaka
SS3AlarmKlimat2_Napaka | DIGITAL | IOD_SS3 | SS3:.AlarmKlimat2_Napaka
SS3AlarmKlimat3_Napaka | DIGITAL | IOD_SS3 | SS3:.AlarmKlimat3_Napaka
SS3AlarmKlimat4_Napaka | DIGITAL | IOD_SS3 | SS3:.AlarmKlimat4_Napaka
SS3AlarmLAH1_RazlitjeVode | DIGITAL | IOD_SS3 | SS3:.AlarmLAH1_RazlitjeVode
SS3AlarmLAH2_RazlitjeVode | DIGITAL | IOD_SS3 | SS3:.AlarmLAH2_RazlitjeVode
SS3AlarmSinhronizacijaNOK | DIGITAL | IOD_SS3 | SS3:.AlarmSinhronizacijaNOK
SS3AlarmTempTIA1Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA1Previsoka
SS3AlarmTempTIA2Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA2Previsoka
SS3AlarmTempTIA3Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA3Previsoka
SS3AlarmTSTemp1Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTSTemp1Previsoka
SS3AlarmTSTemp3Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTSTemp3Previsoka
SS3AlarmUPSKrmOmara_Alarm | DIGITAL | IOD_SS3 | SS3:.AlarmUPSKrmOmara_Alarm
SS3ComSCADA | DIGITAL | IOD_SS3 | SS3:.ComSCADA
SS3ComSCADA1 | DIGITAL | IOD_SS3 | SS3:.ComSCADA1
SS3ErrComKlima1 | DIGITAL | IOD_SS3 | SS3:.ErrComKlima[1]
SS3ErrComKlima2 | DIGITAL | IOD_SS3 | SS3:.ErrComKlima[2]
SS3ErrComKlima3 | DIGITAL | IOD_SS3 | SS3:.ErrComKlima[3]
SS3ErrComKlima4 | DIGITAL | IOD_SS3 | SS3:.ErrComKlima[4]
SS3ErrCommScada | DIGITAL | IOD_SS3 | SS3:.ErrCommScada
SS3ErrComPanelPLC | DIGITAL | IOD_SS3 | SS3:.ErrComPanelPLC
SS3ErrComPort2 | DIGITAL | IOD_SS3 | SS3:.ErrComPort2
SS3ErrorComKlima4Error | DIGITAL | IOD_SS3 | SS3:.ErrorComKlima[4].Error
SS3Klima1_Onemogocena | DIGITAL | IOD_SS3 | SS3:.Klima1_Onemogocena
SS3Klima2_Onemogocena | DIGITAL | IOD_SS3 | SS3:.Klima2_Onemogocena
SS3Klima3_Onemogocena | DIGITAL | IOD_SS3 | SS3:.Klima3_Onemogocena
SS3Klima4_Onemogocena | DIGITAL | IOD_SS3 | SS3:.Klima4_Onemogocena
SS3Klima1Deluje | DIGITAL | IOD_SS3 | SS3:.Klima[1].Deluje
SS3Klima1EnergySaving | DIGITAL | IOD_SS3 | SS3:.Klima[1].EnergySaving
SS3Klima1Napaka | DIGITAL | IOD_SS3 | SS3:.Klima[1].Napaka
SS3Klima1OnOffEnablingBySupervisor | DIGITAL | IOD_SS3 | SS3:.Klima[1].OnOffEnablingBySupervisor
SS3Klima1Razvlazevanje | DIGITAL | IOD_SS3 | SS3:.Klima[1].Razvlazevanje
SS3Klima1RemoteOFFtoOutput | DIGITAL | IOD_SS3 | SS3:.Klima[1].RemoteOFFtoOutput
SS3Klima1RemoteOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[1].RemoteOnOff
SS3Klima1RocniIzklop | DIGITAL | IOD_SS3 | SS3:.Klima[1].RocniIzklop
SS3Klima1SenzorjiStatus | DIGITAL | IOD_SS3 | SS3:.Klima[1].SenzorjiStatus
SS3Klima1UnitOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[1].UnitOnOff
SS3Klima1VentilGretjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[1].VentilGretjeOdpiranje
SS3Klima1VentilGretjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[1].VentilGretjeZapiranje
SS3Klima1VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[1].VentilHlajenjeOdpiranje
SS3Klima1VentilHlajenjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[1].VentilHlajenjeZapiranje
SS3Klima1Vlazenje | DIGITAL | IOD_SS3 | SS3:.Klima[1].Vlazenje
SS3Klima2Deluje | DIGITAL | IOD_SS3 | SS3:.Klima[2].Deluje
SS3Klima2EnergySaving | DIGITAL | IOD_SS3 | SS3:.Klima[2].EnergySaving
SS3Klima2Napaka | DIGITAL | IOD_SS3 | SS3:.Klima[2].Napaka
SS3Klima2OnOffEnablingBySupervisor | DIGITAL | IOD_SS3 | SS3:.Klima[2].OnOffEnablingBySupervisor
SS3Klima2Razvlazevanje | DIGITAL | IOD_SS3 | SS3:.Klima[2].Razvlazevanje
SS3Klima2RemoteOFFtoOutput | DIGITAL | IOD_SS3 | SS3:.Klima[2].RemoteOFFtoOutput
SS3Klima2RemoteOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[2].RemoteOnOff
SS3Klima2RocniIzklop | DIGITAL | IOD_SS3 | SS3:.Klima[2].RocniIzklop
SS3Klima2SenzorjiStatus | DIGITAL | IOD_SS3 | SS3:.Klima[2].SenzorjiStatus
SS3Klima2UnitOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[2].UnitOnOff
SS3Klima2VentilGretjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[2].VentilGretjeOdpiranje
SS3Klima2VentilGretjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[2].VentilGretjeZapiranje
SS3Klima2VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[2].VentilHlajenjeOdpiranje
SS3Klima2VentilHlajenjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[2].VentilHlajenjeZapiranje
SS3Klima2Vlazenje | DIGITAL | IOD_SS3 | SS3:.Klima[2].Vlazenje
SS3Klima3Deluje | DIGITAL | IOD_SS3 | SS3:.Klima[3].Deluje
SS3Klima3EnergySaving | DIGITAL | IOD_SS3 | SS3:.Klima[3].EnergySaving
SS3Klima3Napaka | DIGITAL | IOD_SS3 | SS3:.Klima[3].Napaka
SS3Klima3OnOffEnablingBySupervisor | DIGITAL | IOD_SS3 | SS3:.Klima[3].OnOffEnablingBySupervisor
SS3Klima3Razvlazevanje | DIGITAL | IOD_SS3 | SS3:.Klima[3].Razvlazevanje
SS3Klima3RemoteOFFtoOutput | DIGITAL | IOD_SS3 | SS3:.Klima[3].RemoteOFFtoOutput
SS3Klima3RemoteOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[3].RemoteOnOff
SS3Klima3RocniIzklop | DIGITAL | IOD_SS3 | SS3:.Klima[3].RocniIzklop
SS3Klima3SenzorjiStatus | DIGITAL | IOD_SS3 | SS3:.Klima[3].SenzorjiStatus
SS3Klima3UnitOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[3].UnitOnOff
SS3Klima3VentilGretjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[3].VentilGretjeOdpiranje
SS3Klima3VentilGretjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[3].VentilGretjeZapiranje
SS3Klima3VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[3].VentilHlajenjeOdpiranje
SS3Klima3VentilHlajenjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[3].VentilHlajenjeZapiranje
SS3Klima3Vlazenje | DIGITAL | IOD_SS3 | SS3:.Klima[3].Vlazenje
SS3Klima4Deluje | DIGITAL | IOD_SS3 | SS3:.Klima[4].Deluje
SS3Klima4EnergySaving | DIGITAL | IOD_SS3 | SS3:.Klima[4].EnergySaving
SS3Klima4Napaka | DIGITAL | IOD_SS3 | SS3:.Klima[4].Napaka
SS3Klima4OnOffEnablingBySupervisor | DIGITAL | IOD_SS3 | SS3:.Klima[4].OnOffEnablingBySupervisor
SS3Klima4Razvlazevanje | DIGITAL | IOD_SS3 | SS3:.Klima[4].Razvlazevanje
SS3Klima4RemoteOFFtoOutput | DIGITAL | IOD_SS3 | SS3:.Klima[4].RemoteOFFtoOutput
SS3Klima4RemoteOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[4].RemoteOnOff
SS3Klima4RocniIzklop | DIGITAL | IOD_SS3 | SS3:.Klima[4].RocniIzklop
SS3Klima4SenzorjiStatus | DIGITAL | IOD_SS3 | SS3:.Klima[4].SenzorjiStatus
SS3Klima4UnitOnOff | DIGITAL | IOD_SS3 | SS3:.Klima[4].UnitOnOff
SS3Klima4VentilGretjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[4].VentilGretjeOdpiranje
SS3Klima4VentilGretjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[4].VentilGretjeZapiranje
SS3Klima4VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3 | SS3:.Klima[4].VentilHlajenjeOdpiranje
SS3Klima4VentilHlajenjeZapiranje | DIGITAL | IOD_SS3 | SS3:.Klima[4].VentilHlajenjeZapiranje
SS3Klima4Vlazenje | DIGITAL | IOD_SS3 | SS3:.Klima[4].Vlazenje
SS3KlimaError1AlarmKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].AlarmKompresor1
SS3KlimaError1AlarmKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].AlarmKompresor2
SS3KlimaError1FaultyEprom | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].FaultyEprom
SS3KlimaError1FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].FenThermalCutout
SS3KlimaError1GeneralAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].GeneralAlarm
SS3KlimaError1Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].Kompresor1naMejiStevilaObrUr
SS3KlimaError1Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].Kompresor2naMejiStevilaObrUr
SS3KlimaError1Kond1FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].Kond1FenThermalCutout
SS3KlimaError1Kond2FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].Kond2FenThermalCutout
SS3KlimaError1NapakaPriPretokuVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaPriPretokuVode
SS3KlimaError1NapakaPriPretokuZraka | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaPriPretokuZraka
SS3KlimaError1NapakaSenzorPovratVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorPovratVode
SS3KlimaError1NapakaSenzorPritiska | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorPritiska
SS3KlimaError1NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorTempIzpiha
SS3KlimaError1NapakaSenzorTempProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorTempProstora
SS3KlimaError1NapakaSenzorVlaznosti | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorVlaznosti
SS3KlimaError1NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaSenzorZunanjeTemp
SS3KlimaError1NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NapakaTSTemperaturaProstora
SS3KlimaError1NiTokaVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NiTokaVVlazilcu
SS3KlimaError1NiVodeVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NiVodeVVlazilcu
SS3KlimaError1NizekPritiskKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NizekPritiskKompresor1
SS3KlimaError1NizekPritiskKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NizekPritiskKompresor2
SS3KlimaError1NizkaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NizkaTempPovratneVode
SS3KlimaError1NizkaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NizkaTempVProstoru
SS3KlimaError1NizkaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].NizkaVlaznost
SS3KlimaError1PozarniAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].PozarniAlarm
SS3KlimaError1StoppedByAlarms | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].StoppedByAlarms
SS3KlimaError1TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].TermZascInVisokPritiskKompr1
SS3KlimaError1TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].TermZascInVisokPritiskKompr2
SS3KlimaError1ThermalCutoutHeater1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].ThermalCutoutHeater1
SS3KlimaError1ThermalCutoutHeater2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].ThermalCutoutHeater2
SS3KlimaError1VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VentilatorNaMejiStevilaObrUr
SS3KlimaError1VisokaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokaTempPovratneVode
SS3KlimaError1VisokaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokaTempVProstoru
SS3KlimaError1VisokaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokaVlaznost
SS3KlimaError1VisokPritiskVKrogu1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokPritiskVKrogu1
SS3KlimaError1VisokPritiskVKrogu2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokPritiskVKrogu2
SS3KlimaError1VisokTokVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VisokTokVVlazilcu
SS3KlimaError1VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].VlazilecnaMejiStevilaObrUr
SS3KlimaError1ZamasenFilter | DIGITAL | IOD_SS3 | SS3:.KlimaError[1].ZamasenFilter
SS3KlimaError2AlarmKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].AlarmKompresor1
SS3KlimaError2AlarmKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].AlarmKompresor2
SS3KlimaError2FaultyEprom | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].FaultyEprom
SS3KlimaError2FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].FenThermalCutout
SS3KlimaError2GeneralAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].GeneralAlarm
SS3KlimaError2Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].Kompresor1naMejiStevilaObrUr
SS3KlimaError2Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].Kompresor2naMejiStevilaObrUr
SS3KlimaError2Kond1FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].Kond1FenThermalCutout
SS3KlimaError2Kond2FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].Kond2FenThermalCutout
SS3KlimaError2NapakaPriPretokuVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaPriPretokuVode
SS3KlimaError2NapakaPriPretokuZraka | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaPriPretokuZraka
SS3KlimaError2NapakaSenzorPovratVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorPovratVode
SS3KlimaError2NapakaSenzorPritiska | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorPritiska
SS3KlimaError2NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorTempIzpiha
SS3KlimaError2NapakaSenzorTempProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorTempProstora
SS3KlimaError2NapakaSenzorVlaznosti | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorVlaznosti
SS3KlimaError2NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaSenzorZunanjeTemp
SS3KlimaError2NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NapakaTSTemperaturaProstora
SS3KlimaError2NiTokaVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NiTokaVVlazilcu
SS3KlimaError2NiVodeVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NiVodeVVlazilcu
SS3KlimaError2NizekPritiskKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NizekPritiskKompresor1
SS3KlimaError2NizekPritiskKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NizekPritiskKompresor2
SS3KlimaError2NizkaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NizkaTempPovratneVode
SS3KlimaError2NizkaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NizkaTempVProstoru
SS3KlimaError2NizkaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].NizkaVlaznost
SS3KlimaError2PozarniAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].PozarniAlarm
SS3KlimaError2StoppedByAlarms | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].StoppedByAlarms
SS3KlimaError2TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].TermZascInVisokPritiskKompr1
SS3KlimaError2TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].TermZascInVisokPritiskKompr2
SS3KlimaError2ThermalCutoutHeater1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].ThermalCutoutHeater1
SS3KlimaError2ThermalCutoutHeater2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].ThermalCutoutHeater2
SS3KlimaError2VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VentilatorNaMejiStevilaObrUr
SS3KlimaError2VisokaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokaTempPovratneVode
SS3KlimaError2VisokaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokaTempVProstoru
SS3KlimaError2VisokaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokaVlaznost
SS3KlimaError2VisokPritiskVKrogu1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokPritiskVKrogu1
SS3KlimaError2VisokPritiskVKrogu2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokPritiskVKrogu2
SS3KlimaError2VisokTokVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VisokTokVVlazilcu
SS3KlimaError2VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].VlazilecnaMejiStevilaObrUr
SS3KlimaError2ZamasenFilter | DIGITAL | IOD_SS3 | SS3:.KlimaError[2].ZamasenFilter
SS3KlimaError3AlarmKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].AlarmKompresor1
SS3KlimaError3AlarmKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].AlarmKompresor2
SS3KlimaError3FaultyEprom | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].FaultyEprom
SS3KlimaError3FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].FenThermalCutout
SS3KlimaError3GeneralAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].GeneralAlarm
SS3KlimaError3Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].Kompresor1naMejiStevilaObrUr
SS3KlimaError3Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].Kompresor2naMejiStevilaObrUr
SS3KlimaError3Kond1FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].Kond1FenThermalCutout
SS3KlimaError3Kond2FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].Kond2FenThermalCutout
SS3KlimaError3NapakaPriPretokuVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaPriPretokuVode
SS3KlimaError3NapakaPriPretokuZraka | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaPriPretokuZraka
SS3KlimaError3NapakaSenzorPovratVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorPovratVode
SS3KlimaError3NapakaSenzorPritiska | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorPritiska
SS3KlimaError3NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorTempIzpiha
SS3KlimaError3NapakaSenzorTempProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorTempProstora
SS3KlimaError3NapakaSenzorVlaznosti | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorVlaznosti
SS3KlimaError3NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaSenzorZunanjeTemp
SS3KlimaError3NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NapakaTSTemperaturaProstora
SS3KlimaError3NiTokaVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NiTokaVVlazilcu
SS3KlimaError3NiVodeVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NiVodeVVlazilcu
SS3KlimaError3NizekPritiskKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NizekPritiskKompresor1
SS3KlimaError3NizekPritiskKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NizekPritiskKompresor2
SS3KlimaError3NizkaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NizkaTempPovratneVode
SS3KlimaError3NizkaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NizkaTempVProstoru
SS3KlimaError3NizkaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].NizkaVlaznost
SS3KlimaError3PozarniAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].PozarniAlarm
SS3KlimaError3StoppedByAlarms | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].StoppedByAlarms
SS3KlimaError3TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].TermZascInVisokPritiskKompr1
SS3KlimaError3TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].TermZascInVisokPritiskKompr2
SS3KlimaError3ThermalCutoutHeater1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].ThermalCutoutHeater1
SS3KlimaError3ThermalCutoutHeater2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].ThermalCutoutHeater2
SS3KlimaError3VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VentilatorNaMejiStevilaObrUr
SS3KlimaError3VisokaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokaTempPovratneVode
SS3KlimaError3VisokaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokaTempVProstoru
SS3KlimaError3VisokaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokaVlaznost
SS3KlimaError3VisokPritiskVKrogu1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokPritiskVKrogu1
SS3KlimaError3VisokPritiskVKrogu2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokPritiskVKrogu2
SS3KlimaError3VisokTokVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VisokTokVVlazilcu
SS3KlimaError3VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].VlazilecnaMejiStevilaObrUr
SS3KlimaError3ZamasenFilter | DIGITAL | IOD_SS3 | SS3:.KlimaError[3].ZamasenFilter
SS3KlimaError4AlarmKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].AlarmKompresor1
SS3KlimaError4AlarmKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].AlarmKompresor2
SS3KlimaError4FaultyEprom | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].FaultyEprom
SS3KlimaError4FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].FenThermalCutout
SS3KlimaError4GeneralAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].GeneralAlarm
SS3KlimaError4Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].Kompresor1naMejiStevilaObrUr
SS3KlimaError4Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].Kompresor2naMejiStevilaObrUr
SS3KlimaError4Kond1FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].Kond1FenThermalCutout
SS3KlimaError4Kond2FenThermalCutout | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].Kond2FenThermalCutout
SS3KlimaError4NapakaPriPretokuVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaPriPretokuVode
SS3KlimaError4NapakaPriPretokuZraka | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaPriPretokuZraka
SS3KlimaError4NapakaSenzorPovratVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorPovratVode
SS3KlimaError4NapakaSenzorPritiska | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorPritiska
SS3KlimaError4NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorTempIzpiha
SS3KlimaError4NapakaSenzorTempProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorTempProstora
SS3KlimaError4NapakaSenzorVlaznosti | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorVlaznosti
SS3KlimaError4NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaSenzorZunanjeTemp
SS3KlimaError4NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NapakaTSTemperaturaProstora
SS3KlimaError4NiTokaVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NiTokaVVlazilcu
SS3KlimaError4NiVodeVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NiVodeVVlazilcu
SS3KlimaError4NizekPritiskKompresor1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NizekPritiskKompresor1
SS3KlimaError4NizekPritiskKompresor2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NizekPritiskKompresor2
SS3KlimaError4NizkaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NizkaTempPovratneVode
SS3KlimaError4NizkaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NizkaTempVProstoru
SS3KlimaError4NizkaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].NizkaVlaznost
SS3KlimaError4PozarniAlarm | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].PozarniAlarm
SS3KlimaError4StoppedByAlarms | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].StoppedByAlarms
SS3KlimaError4TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].TermZascInVisokPritiskKompr1
SS3KlimaError4TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].TermZascInVisokPritiskKompr2
SS3KlimaError4ThermalCutoutHeater1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].ThermalCutoutHeater1
SS3KlimaError4ThermalCutoutHeater2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].ThermalCutoutHeater2
SS3KlimaError4VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VentilatorNaMejiStevilaObrUr
SS3KlimaError4VisokaTempPovratneVode | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokaTempPovratneVode
SS3KlimaError4VisokaTempVProstoru | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokaTempVProstoru
SS3KlimaError4VisokaVlaznost | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokaVlaznost
SS3KlimaError4VisokPritiskVKrogu1 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokPritiskVKrogu1
SS3KlimaError4VisokPritiskVKrogu2 | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokPritiskVKrogu2
SS3KlimaError4VisokTokVVlazilcu | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VisokTokVVlazilcu
SS3KlimaError4VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].VlazilecnaMejiStevilaObrUr
SS3KlimaError4ZamasenFilter | DIGITAL | IOD_SS3 | SS3:.KlimaError[4].ZamasenFilter
SS3NacDelovanjaKlime1_2_Avtomatsko | DIGITAL | IOD_SS3 | SS3:.NacDelovanjaKlime1_2_Avtomatsko
SS3NacDelovanjaKlime3_4_Avtomatsko | DIGITAL | IOD_SS3 | SS3:.NacDelovanjaKlime3_4_Avtomatsko
SS3NapakaSenzorTemp1 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorTemp1
SS3NapakaSenzorTemp2 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorTemp2
SS3NapakaSenzorTemp3 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorTemp3
SS3NapakaSenzorVlaga1 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorVlaga1
SS3NapakaSenzorVlaga2 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorVlaga2
SS3NapakaSenzorVlaga3 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorVlaga3
SS3NastaviCasNaKrmilniku | DIGITAL | IOD_SS3 | SS3:.NastaviCasNaKrmilniku
SS3NastavitevUreKrUspesna | DIGITAL | IOD_SS3 | SS3:.NastavitevUreKrUspesna
SS3OpozoriloBaterijaPLC | DIGITAL | IOD_SS3 | SS3:.OpozoriloBaterijaPLC
SS3OsveziAlarmePanel | DIGITAL | IOD_SS3 | SS3:.OsveziAlarmePanel
SS3RocniVklopKlima1 | DIGITAL | IOD_SS3 | SS3:.RocniVklopKlima1
SS3RocniVklopKlima2 | DIGITAL | IOD_SS3 | SS3:.RocniVklopKlima2
SS3RocniVklopKlima3 | DIGITAL | IOD_SS3 | SS3:.RocniVklopKlima3
SS3RocniVklopKlima4 | DIGITAL | IOD_SS3 | SS3:.RocniVklopKlima4
SS3SinhronizacijaPanelOK | DIGITAL | IOD_SS3 | SS3:.SinhronizacijaPanelOK
SS3SinhronizirajCas_Panel | DIGITAL | IOD_SS3 | SS3:.SinhronizirajCas_Panel
SS3SkupneNapakeNaprav_Klima1 | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_Klima1
SS3SkupneNapakeNaprav_Klima2 | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_Klima2
SS3SkupneNapakeNaprav_Klima3 | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_Klima3
SS3SkupneNapakeNaprav_Klima4 | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_Klima4
SS3SkupneNapakeNaprav_Komunikacija | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_Komunikacija
SS3SkupneNapakeNaprav_TempVlaga | DIGITAL | IOD_SS3 | SS3:.SkupneNapakeNaprav_TempVlaga
SS3StanjeKlimat1_Delovanje | DIGITAL | IOD_SS3 | SS3:.StanjeKlimat1_Delovanje
SS3StanjeKlimat2_Delovanje | DIGITAL | IOD_SS3 | SS3:.StanjeKlimat2_Delovanje
SS3StanjeKlimat3_Delovanje | DIGITAL | IOD_SS3 | SS3:.StanjeKlimat3_Delovanje
SS3StanjeKlimat4_Delovanje | DIGITAL | IOD_SS3 | SS3:.StanjeKlimat4_Delovanje
SS3StanjeUPSKrmOmara_BaterijskiNacin | DIGITAL | IOD_SS3 | SS3:.StanjeUPSKrmOmara_BaterijskiNacin
SS3StanjeUPSKrmOmara_Polnjenje | DIGITAL | IOD_SS3 | SS3:.StanjeUPSKrmOmara_Polnjenje
SS3UserLoggedIn | DIGITAL | IOD_SS3 | SS3:.UserLoggedIn
SS3XVH_AlarmOn | DIGITAL | IOD_SS3 | SS3:.XVH_AlarmOn
SS3Klimat1_Vklop | DIGITAL | IOD_SS3 | SS3:.Klimat1_Vklop
SS3Klimat2_Vklop | DIGITAL | IOD_SS3 | SS3:.Klimat2_Vklop
SS3Klimat3_Vklop | DIGITAL | IOD_SS3 | SS3:.Klimat3_Vklop
SS3Klimat4_Vklop | DIGITAL | IOD_SS3 | SS3:.Klimat4_Vklop
SS3ErrorComKlima1Error | DIGITAL | IOD_SS3 | SS3:.ErrorComKlima[1].Error
SS3ErrorComKlima2Error | DIGITAL | IOD_SS3 | SS3:.ErrorComKlima[2].Error
SS3ErrorComKlima3Error | DIGITAL | IOD_SS3 | SS3:.ErrorComKlima[3].Error
SS3ErrCommScada2 | DIGITAL | IOD_SS3 | SS3:.ErrCommScada2
SS3ComSCADA2 | DIGITAL | IOD_SS3 | SS3:.ComSCADA2
SS3ComSCADA3 | DIGITAL | IOD_SS3 | SS3:.ComSCADA3
SS3AlarmTempTIA4Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA4Previsoka
SS3AlarmTempTIA5Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA5Previsoka
SS3NapakaSenzorTemp4 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorTemp4
SS3NapakaSenzorTemp5 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorTemp5
SS3NapakaSenzorVlaga4 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorVlaga4
SS3NapakaSenzorVlaga5 | DIGITAL | IOD_SS3 | SS3:.NapakaSenzorVlaga5
SS3AlarmTempTIA124Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA124Previsoka
SS3AlarmTempTIA35Previsoka | DIGITAL | IOD_SS3 | SS3:.AlarmTempTIA35Previsoka
SS3DatumCasDan | INT | IOD_SS3 | SS3:.DatumCas.Dan | BYTE
SS3DatumCasLeto | INT | IOD_SS3 | SS3:.DatumCas.Leto | BYTE
SS3DatumCasLeto2 | INT | IOD_SS3 | SS3:.DatumCas.Leto2
SS3DatumCasMesec | INT | IOD_SS3 | SS3:.DatumCas.Mesec | BYTE
SS3DatumCasMinuta | INT | IOD_SS3 | SS3:.DatumCas.Minuta | BYTE
SS3DatumCasSekunda | INT | IOD_SS3 | SS3:.DatumCas.Sekunda | BYTE
SS3DatumCasUra | INT | IOD_SS3 | SS3:.DatumCas.Ura | BYTE
SS3ErrorComKlima4Status | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Status
SS3Klima1GrelecStatus | INT | IOD_SS3 | SS3:.Klima[1].GrelecStatus | BYTE
SS3Klima1IzhodniVentStatus | INT | IOD_SS3 | SS3:.Klima[1].IzhodniVentStatus | BYTE
SS3Klima1KompresorStatus | INT | IOD_SS3 | SS3:.Klima[1].KompresorStatus | BYTE
SS3Klima1VlazilecStatus | INT | IOD_SS3 | SS3:.Klima[1].VlazilecStatus | BYTE
SS3Klima2GrelecStatus | INT | IOD_SS3 | SS3:.Klima[2].GrelecStatus | BYTE
SS3Klima2IzhodniVentStatus | INT | IOD_SS3 | SS3:.Klima[2].IzhodniVentStatus | BYTE
SS3Klima2KompresorStatus | INT | IOD_SS3 | SS3:.Klima[2].KompresorStatus | BYTE
SS3Klima2VlazilecStatus | INT | IOD_SS3 | SS3:.Klima[2].VlazilecStatus | BYTE
SS3Klima3GrelecStatus | INT | IOD_SS3 | SS3:.Klima[3].GrelecStatus | BYTE
SS3Klima3IzhodniVentStatus | INT | IOD_SS3 | SS3:.Klima[3].IzhodniVentStatus | BYTE
SS3Klima3KompresorStatus | INT | IOD_SS3 | SS3:.Klima[3].KompresorStatus | BYTE
SS3Klima3VlazilecStatus | INT | IOD_SS3 | SS3:.Klima[3].VlazilecStatus | BYTE
SS3Klima4GrelecStatus | INT | IOD_SS3 | SS3:.Klima[4].GrelecStatus | BYTE
SS3Klima4IzhodniVentStatus | INT | IOD_SS3 | SS3:.Klima[4].IzhodniVentStatus | BYTE
SS3Klima4KompresorStatus | INT | IOD_SS3 | SS3:.Klima[4].KompresorStatus | BYTE
SS3Klima4VlazilecStatus | INT | IOD_SS3 | SS3:.Klima[4].VlazilecStatus | BYTE
SS3StUrZaPreklopKlim1_2 | INT | IOD_SS3 | SS3:.StUrZaPreklopKlim1_2
SS3StUrZaPreklopKlim3_4 | INT | IOD_SS3 | SS3:.StUrZaPreklopKlim3_4
SS3UPSstatus_Prikaz_PanelSCADA | INT | IOD_SS3 | SS3:.UPSstatus_Prikaz_PanelSCADA | BYTE
SS3UserCurrentLevel | INT | IOD_SS3 | SS3:.UserCurrentLevel | BYTE
SS3ErrorComKlima1Code0 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[0] | BYTE
SS3ErrorComKlima1Code10 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[10] | BYTE
SS3ErrorComKlima1Code11 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[11] | BYTE
SS3ErrorComKlima1Code12 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[12] | BYTE
SS3ErrorComKlima1Code13 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[13] | BYTE
SS3ErrorComKlima1Code14 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[14] | BYTE
SS3ErrorComKlima1Code15 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[15] | BYTE
SS3ErrorComKlima1Code1 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[1] | BYTE
SS3ErrorComKlima1Code2 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[2] | BYTE
SS3ErrorComKlima1Code3 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[3] | BYTE
SS3ErrorComKlima1Code4 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[4] | BYTE
SS3ErrorComKlima1Code5 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[5] | BYTE
SS3ErrorComKlima1Code6 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[6] | BYTE
SS3ErrorComKlima1Code7 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[7] | BYTE
SS3ErrorComKlima1Code8 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[8] | BYTE
SS3ErrorComKlima1Code9 | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Code[9] | BYTE
SS3ErrorComKlima1Status | INT | IOD_SS3 | SS3:.ErrorComKlima[1].Status
SS3ErrorComKlima2Code0 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[0] | BYTE
SS3ErrorComKlima2Code10 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[10] | BYTE
SS3ErrorComKlima2Code11 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[11] | BYTE
SS3ErrorComKlima2Code12 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[12] | BYTE
SS3ErrorComKlima2Code13 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[13] | BYTE
SS3ErrorComKlima2Code14 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[14] | BYTE
SS3ErrorComKlima2Code15 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[15] | BYTE
SS3ErrorComKlima2Code1 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[1] | BYTE
SS3ErrorComKlima2Code2 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[2] | BYTE
SS3ErrorComKlima2Code3 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[3] | BYTE
SS3ErrorComKlima2Code4 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[4] | BYTE
SS3ErrorComKlima2Code5 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[5] | BYTE
SS3ErrorComKlima2Code6 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[6] | BYTE
SS3ErrorComKlima2Code7 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[7] | BYTE
SS3ErrorComKlima2Code8 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[8] | BYTE
SS3ErrorComKlima2Code9 | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Code[9] | BYTE
SS3ErrorComKlima2Status | INT | IOD_SS3 | SS3:.ErrorComKlima[2].Status
SS3ErrorComKlima3Code0 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[0] | BYTE
SS3ErrorComKlima3Code10 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[10] | BYTE
SS3ErrorComKlima3Code11 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[11] | BYTE
SS3ErrorComKlima3Code12 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[12] | BYTE
SS3ErrorComKlima3Code13 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[13] | BYTE
SS3ErrorComKlima3Code14 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[14] | BYTE
SS3ErrorComKlima3Code15 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[15] | BYTE
SS3ErrorComKlima3Code1 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[1] | BYTE
SS3ErrorComKlima3Code2 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[2] | BYTE
SS3ErrorComKlima3Code3 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[3] | BYTE
SS3ErrorComKlima3Code4 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[4] | BYTE
SS3ErrorComKlima3Code5 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[5] | BYTE
SS3ErrorComKlima3Code6 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[6] | BYTE
SS3ErrorComKlima3Code7 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[7] | BYTE
SS3ErrorComKlima3Code8 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[8] | BYTE
SS3ErrorComKlima3Code9 | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Code[9] | BYTE
SS3ErrorComKlima3Status | INT | IOD_SS3 | SS3:.ErrorComKlima[3].Status
SS3ErrorComKlima4Code0 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[0] | BYTE
SS3ErrorComKlima4Code10 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[10] | BYTE
SS3ErrorComKlima4Code11 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[11] | BYTE
SS3ErrorComKlima4Code12 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[12] | BYTE
SS3ErrorComKlima4Code13 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[13] | BYTE
SS3ErrorComKlima4Code14 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[14] | BYTE
SS3ErrorComKlima4Code15 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[15] | BYTE
SS3ErrorComKlima4Code1 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[1] | BYTE
SS3ErrorComKlima4Code2 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[2] | BYTE
SS3ErrorComKlima4Code3 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[3] | BYTE
SS3ErrorComKlima4Code4 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[4] | BYTE
SS3ErrorComKlima4Code5 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[5] | BYTE
SS3ErrorComKlima4Code6 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[6] | BYTE
SS3ErrorComKlima4Code7 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[7] | BYTE
SS3ErrorComKlima4Code8 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[8] | BYTE
SS3ErrorComKlima4Code9 | INT | IOD_SS3 | SS3:.ErrorComKlima[4].Code[9] | BYTE
SS3kom_nast_cas_izpada | INT | IOD_SS3 | SS3:.kom_nast_cas_izpada
SS3AktualniSetPointTemp1_2 | REAL | IOD_SS3 | SS3:.AktualniSetPointTemp1_2
SS3AktualniSetPointTemp3_4 | REAL | IOD_SS3 | SS3:.AktualniSetPointTemp3_4
SS3Klima1ure | REAL | IOD_SS3 | SS3:.Klima1ure
SS3Klima2ure | REAL | IOD_SS3 | SS3:.Klima2ure
SS3Klima3ure | REAL | IOD_SS3 | SS3:.Klima3ure
SS3Klima4ure | REAL | IOD_SS3 | SS3:.Klima4ure
SS3Klima1NastTempProstora | REAL | IOD_SS3 | SS3:.Klima[1].NastTempProstora
SS3Klima1NastVlaznost | REAL | IOD_SS3 | SS3:.Klima[1].NastVlaznost
SS3Klima1ObratovalneUre | REAL | IOD_SS3 | SS3:.Klima[1].ObratovalneUre
SS3Klima1TemperaturaProstora | REAL | IOD_SS3 | SS3:.Klima[1].TemperaturaProstora
SS3Klima1VlaznostProstora | REAL | IOD_SS3 | SS3:.Klima[1].VlaznostProstora
SS3Klima2NastTempProstora | REAL | IOD_SS3 | SS3:.Klima[2].NastTempProstora
SS3Klima2NastVlaznost | REAL | IOD_SS3 | SS3:.Klima[2].NastVlaznost
SS3Klima2ObratovalneUre | REAL | IOD_SS3 | SS3:.Klima[2].ObratovalneUre
SS3Klima2TemperaturaProstora | REAL | IOD_SS3 | SS3:.Klima[2].TemperaturaProstora
SS3Klima2VlaznostProstora | REAL | IOD_SS3 | SS3:.Klima[2].VlaznostProstora
SS3Klima3NastTempProstora | REAL | IOD_SS3 | SS3:.Klima[3].NastTempProstora
SS3Klima3NastVlaznost | REAL | IOD_SS3 | SS3:.Klima[3].NastVlaznost
SS3Klima3ObratovalneUre | REAL | IOD_SS3 | SS3:.Klima[3].ObratovalneUre
SS3Klima3TemperaturaProstora | REAL | IOD_SS3 | SS3:.Klima[3].TemperaturaProstora
SS3Klima3VlaznostProstora | REAL | IOD_SS3 | SS3:.Klima[3].VlaznostProstora
SS3Klima4NastTempProstora | REAL | IOD_SS3 | SS3:.Klima[4].NastTempProstora
SS3Klima4NastVlaznost | REAL | IOD_SS3 | SS3:.Klima[4].NastVlaznost
SS3Klima4ObratovalneUre | REAL | IOD_SS3 | SS3:.Klima[4].ObratovalneUre
SS3Klima4TemperaturaProstora | REAL | IOD_SS3 | SS3:.Klima[4].TemperaturaProstora
SS3Klima4VlaznostProstora | REAL | IOD_SS3 | SS3:.Klima[4].VlaznostProstora
SS3SKTemp1 | REAL | IOD_SS3 | SS3:.SKTemp1
SS3SKTemp2 | REAL | IOD_SS3 | SS3:.SKTemp2
SS3SKTemp3 | REAL | IOD_SS3 | SS3:.SKTemp3
SS3SKVlaga1 | REAL | IOD_SS3 | SS3:.SKVlaga1
SS3SKVlaga2 | REAL | IOD_SS3 | SS3:.SKVlaga2
SS3SKVlaga3 | REAL | IOD_SS3 | SS3:.SKVlaga3
SS3TempZaAlarm1_2 | REAL | IOD_SS3 | SS3:.TempZaAlarm1_2
SS3TempZaAlarm3_4 | REAL | IOD_SS3 | SS3:.TempZaAlarm3_4
SS3TempZaAlarmTIA1 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA1
SS3TempZaAlarmTIA2 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA2
SS3TempZaAlarmTIA3 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA3
SS3TempZaVklopObehKlim1_2 | REAL | IOD_SS3 | SS3:.TempZaVklopObehKlim1_2
SS3TempZaVklopObehKlim3_4 | REAL | IOD_SS3 | SS3:.TempZaVklopObehKlim3_4
SS3SKTemp4 | REAL | IOD_SS3 | SS3:.SKTemp4
SS3SKTemp5 | REAL | IOD_SS3 | SS3:.SKTemp5
SS3SKVlaga4 | REAL | IOD_SS3 | SS3:.SKVlaga4
SS3SKVlaga5 | REAL | IOD_SS3 | SS3:.SKVlaga5
SS3TempZaAlarmTIA4 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA4
SS3TempZaAlarmTIA5 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA5
SS3SKTempServSoba1Povpr | REAL | IOD_SS3 | SS3:.SKTempServSoba1Povpr
SS3SKTempServSoba2Povpr | REAL | IOD_SS3 | SS3:.SKTempServSoba2Povpr
SS3TempZaAlarmTIA124 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA124
SS3TempZaAlarmTIA35 | REAL | IOD_SS3 | SS3:.TempZaAlarmTIA35
SS3UserName | STRING | IOD_SS3 | SS3:.UserName
SS3Date_Time0 | STRING | IOD_SS3 | SS3:.Date_Time[0]
SS3Date_Time1 | STRING | IOD_SS3 | SS3:.Date_Time[1]
SS3Date_Time2 | STRING | IOD_SS3 | SS3:.Date_Time[2]
SS3Date_Time3 | STRING | IOD_SS3 | SS3:.Date_Time[3]

## variable_3
SS3AlarmKlimat1_Napaka | DIGITAL | IOD_SS3_TCP | 1 | 00001 | AlarmKlimat1_Napaka
SS3AlarmKlimat2_Napaka | DIGITAL | IOD_SS3_TCP | 2 | 00002 | AlarmKlimat2_Napaka
SS3AlarmKlimat3_Napaka | DIGITAL | IOD_SS3_TCP | 3 | 00003 | AlarmKlimat3_Napaka
SS3AlarmKlimat4_Napaka | DIGITAL | IOD_SS3_TCP | 4 | 00004 | AlarmKlimat4_Napaka
SS3AlarmLAH1_RazlitjeVode | DIGITAL | IOD_SS3_TCP | 5 | 00005 | AlarmLAH1_RazlitjeVode
SS3AlarmLAH2_RazlitjeVode | DIGITAL | IOD_SS3_TCP | 6 | 00006 | AlarmLAH2_RazlitjeVode
SS3AlarmSinhronizacijaNOK | DIGITAL | IOD_SS3_TCP | 7 | 00007 | AlarmSinhronizacijaNOK
SS3AlarmTempTIA1Previsoka | DIGITAL | IOD_SS3_TCP | 8 | 00008 | AlarmTempTIA1Previsoka
SS3AlarmTempTIA2Previsoka | DIGITAL | IOD_SS3_TCP | 9 | 00009 | AlarmTempTIA2Previsoka
SS3AlarmTempTIA3Previsoka | DIGITAL | IOD_SS3_TCP | 10 | 00010 | AlarmTempTIA3Previsoka
SS3AlarmTSTemp1Previsoka | DIGITAL | IOD_SS3_TCP | 11 | 00011 | AlarmTSTemp1Previsoka
SS3AlarmTSTemp3Previsoka | DIGITAL | IOD_SS3_TCP | 12 | 00012 | AlarmTSTemp3Previsoka
SS3AlarmUPSKrmOmara_Alarm | DIGITAL | IOD_SS3_TCP | 13 | 00013 | AlarmUPSKrmOmara_Alarm
SS3ComSCADA | DIGITAL | IOD_SS3_TCP | 14 | 00014 | ComSCADA
SS3ComSCADA1 | DIGITAL | IOD_SS3_TCP | 15 | 00015 | ComSCADA1
SS3ErrComKlima1 | DIGITAL | IOD_SS3_TCP | 16 | 00016 | ErrComKlima[1]
SS3ErrComKlima2 | DIGITAL | IOD_SS3_TCP | 17 | 00017 | ErrComKlima[2]
SS3ErrComKlima3 | DIGITAL | IOD_SS3_TCP | 18 | 00018 | ErrComKlima[3]
SS3ErrComKlima4 | DIGITAL | IOD_SS3_TCP | 19 | 00019 | ErrComKlima[4]
SS3ErrCommScada | DIGITAL | IOD_SS3_TCP | 20 | 00020 | ErrCommScada
SS3ErrComPanelPLC | DIGITAL | IOD_SS3_TCP | 21 | 00021 | ErrComPanelPLC
SS3ErrComPort2 | DIGITAL | IOD_SS3_TCP | 22 | 00022 | ErrComPort2
SS3ErrorComKlima4Error | DIGITAL | IOD_SS3_TCP | 23 | 00023 | ErrorComKlima[4].Error
SS3Klima1_Onemogocena | DIGITAL | IOD_SS3_TCP | 24 | 00024 | Klima1_Onemogocena
SS3Klima2_Onemogocena | DIGITAL | IOD_SS3_TCP | 25 | 00025 | Klima2_Onemogocena
SS3Klima3_Onemogocena | DIGITAL | IOD_SS3_TCP | 26 | 00026 | Klima3_Onemogocena
SS3Klima4_Onemogocena | DIGITAL | IOD_SS3_TCP | 27 | 00027 | Klima4_Onemogocena
SS3Klima1Deluje | DIGITAL | IOD_SS3_TCP | 28 | 00028 | Klima[1].Deluje
SS3Klima1EnergySaving | DIGITAL | IOD_SS3_TCP | 29 | 00029 | Klima[1].EnergySaving
SS3Klima1Napaka | DIGITAL | IOD_SS3_TCP | 30 | 00030 | Klima[1].Napaka
SS3Klima1OnOffEnablingBySupervisor | DIGITAL | IOD_SS3_TCP | 31 | 00031 | Klima[1].OnOffEnablingBySupervisor
SS3Klima1Razvlazevanje | DIGITAL | IOD_SS3_TCP | 32 | 00032 | Klima[1].Razvlazevanje
SS3Klima1RemoteOFFtoOutput | DIGITAL | IOD_SS3_TCP | 33 | 00033 | Klima[1].RemoteOFFtoOutput
SS3Klima1RemoteOnOff | DIGITAL | IOD_SS3_TCP | 34 | 00034 | Klima[1].RemoteOnOff
SS3Klima1RocniIzklop | DIGITAL | IOD_SS3_TCP | 35 | 00035 | Klima[1].RocniIzklop
SS3Klima1SenzorjiStatus | DIGITAL | IOD_SS3_TCP | 36 | 00036 | Klima[1].SenzorjiStatus
SS3Klima1UnitOnOff | DIGITAL | IOD_SS3_TCP | 37 | 00037 | Klima[1].UnitOnOff
SS3Klima1VentilGretjeOdpiranje | DIGITAL | IOD_SS3_TCP | 38 | 00038 | Klima[1].VentilGretjeOdpiranje
SS3Klima1VentilGretjeZapiranje | DIGITAL | IOD_SS3_TCP | 39 | 00039 | Klima[1].VentilGretjeZapiranje
SS3Klima1VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3_TCP | 40 | 00040 | Klima[1].VentilHlajenjeOdpiranje
SS3Klima1VentilHlajenjeZapiranje | DIGITAL | IOD_SS3_TCP | 41 | 00041 | Klima[1].VentilHlajenjeZapiranje
SS3Klima1Vlazenje | DIGITAL | IOD_SS3_TCP | 42 | 00042 | Klima[1].Vlazenje
SS3Klima2Deluje | DIGITAL | IOD_SS3_TCP | 43 | 00043 | Klima[2].Deluje
SS3Klima2EnergySaving | DIGITAL | IOD_SS3_TCP | 44 | 00044 | Klima[2].EnergySaving
SS3Klima2Napaka | DIGITAL | IOD_SS3_TCP | 45 | 00045 | Klima[2].Napaka
SS3Klima2OnOffEnablingBySupervisor | DIGITAL | IOD_SS3_TCP | 46 | 00046 | Klima[2].OnOffEnablingBySupervisor
SS3Klima2Razvlazevanje | DIGITAL | IOD_SS3_TCP | 47 | 00047 | Klima[2].Razvlazevanje
SS3Klima2RemoteOFFtoOutput | DIGITAL | IOD_SS3_TCP | 48 | 00048 | Klima[2].RemoteOFFtoOutput
SS3Klima2RemoteOnOff | DIGITAL | IOD_SS3_TCP | 49 | 00049 | Klima[2].RemoteOnOff
SS3Klima2RocniIzklop | DIGITAL | IOD_SS3_TCP | 50 | 00050 | Klima[2].RocniIzklop
SS3Klima2SenzorjiStatus | DIGITAL | IOD_SS3_TCP | 51 | 00051 | Klima[2].SenzorjiStatus
SS3Klima2UnitOnOff | DIGITAL | IOD_SS3_TCP | 52 | 00052 | Klima[2].UnitOnOff
SS3Klima2VentilGretjeOdpiranje | DIGITAL | IOD_SS3_TCP | 53 | 00053 | Klima[2].VentilGretjeOdpiranje
SS3Klima2VentilGretjeZapiranje | DIGITAL | IOD_SS3_TCP | 54 | 00054 | Klima[2].VentilGretjeZapiranje
SS3Klima2VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3_TCP | 55 | 00055 | Klima[2].VentilHlajenjeOdpiranje
SS3Klima2VentilHlajenjeZapiranje | DIGITAL | IOD_SS3_TCP | 56 | 00056 | Klima[2].VentilHlajenjeZapiranje
SS3Klima2Vlazenje | DIGITAL | IOD_SS3_TCP | 57 | 00057 | Klima[2].Vlazenje
SS3Klima3Deluje | DIGITAL | IOD_SS3_TCP | 58 | 00058 | Klima[3].Deluje
SS3Klima3EnergySaving | DIGITAL | IOD_SS3_TCP | 59 | 00059 | Klima[3].EnergySaving
SS3Klima3Napaka | DIGITAL | IOD_SS3_TCP | 60 | 00060 | Klima[3].Napaka
SS3Klima3OnOffEnablingBySupervisor | DIGITAL | IOD_SS3_TCP | 61 | 00061 | Klima[3].OnOffEnablingBySupervisor
SS3Klima3Razvlazevanje | DIGITAL | IOD_SS3_TCP | 62 | 00062 | Klima[3].Razvlazevanje
SS3Klima3RemoteOFFtoOutput | DIGITAL | IOD_SS3_TCP | 63 | 00063 | Klima[3].RemoteOFFtoOutput
SS3Klima3RemoteOnOff | DIGITAL | IOD_SS3_TCP | 64 | 00064 | Klima[3].RemoteOnOff
SS3Klima3RocniIzklop | DIGITAL | IOD_SS3_TCP | 65 | 00065 | Klima[3].RocniIzklop
SS3Klima3SenzorjiStatus | DIGITAL | IOD_SS3_TCP | 66 | 00066 | Klima[3].SenzorjiStatus
SS3Klima3UnitOnOff | DIGITAL | IOD_SS3_TCP | 67 | 00067 | Klima[3].UnitOnOff
SS3Klima3VentilGretjeOdpiranje | DIGITAL | IOD_SS3_TCP | 68 | 00068 | Klima[3].VentilGretjeOdpiranje
SS3Klima3VentilGretjeZapiranje | DIGITAL | IOD_SS3_TCP | 69 | 00069 | Klima[3].VentilGretjeZapiranje
SS3Klima3VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3_TCP | 70 | 00070 | Klima[3].VentilHlajenjeOdpiranje
SS3Klima3VentilHlajenjeZapiranje | DIGITAL | IOD_SS3_TCP | 71 | 00071 | Klima[3].VentilHlajenjeZapiranje
SS3Klima3Vlazenje | DIGITAL | IOD_SS3_TCP | 72 | 00072 | Klima[3].Vlazenje
SS3Klima4Deluje | DIGITAL | IOD_SS3_TCP | 73 | 00073 | Klima[4].Deluje
SS3Klima4EnergySaving | DIGITAL | IOD_SS3_TCP | 74 | 00074 | Klima[4].EnergySaving
SS3Klima4Napaka | DIGITAL | IOD_SS3_TCP | 75 | 00075 | Klima[4].Napaka
SS3Klima4OnOffEnablingBySupervisor | DIGITAL | IOD_SS3_TCP | 76 | 00076 | Klima[4].OnOffEnablingBySupervisor
SS3Klima4Razvlazevanje | DIGITAL | IOD_SS3_TCP | 77 | 00077 | Klima[4].Razvlazevanje
SS3Klima4RemoteOFFtoOutput | DIGITAL | IOD_SS3_TCP | 78 | 00078 | Klima[4].RemoteOFFtoOutput
SS3Klima4RemoteOnOff | DIGITAL | IOD_SS3_TCP | 79 | 00079 | Klima[4].RemoteOnOff
SS3Klima4RocniIzklop | DIGITAL | IOD_SS3_TCP | 80 | 00080 | Klima[4].RocniIzklop
SS3Klima4SenzorjiStatus | DIGITAL | IOD_SS3_TCP | 81 | 00081 | Klima[4].SenzorjiStatus
SS3Klima4UnitOnOff | DIGITAL | IOD_SS3_TCP | 82 | 00082 | Klima[4].UnitOnOff
SS3Klima4VentilGretjeOdpiranje | DIGITAL | IOD_SS3_TCP | 83 | 00083 | Klima[4].VentilGretjeOdpiranje
SS3Klima4VentilGretjeZapiranje | DIGITAL | IOD_SS3_TCP | 84 | 00084 | Klima[4].VentilGretjeZapiranje
SS3Klima4VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3_TCP | 85 | 00085 | Klima[4].VentilHlajenjeOdpiranje
SS3Klima4VentilHlajenjeZapiranje | DIGITAL | IOD_SS3_TCP | 86 | 00086 | Klima[4].VentilHlajenjeZapiranje
SS3Klima4Vlazenje | DIGITAL | IOD_SS3_TCP | 87 | 00087 | Klima[4].Vlazenje
SS3KlimaError1AlarmKompresor1 | DIGITAL | IOD_SS3_TCP | 88 | 00088 | KlimaError[1].AlarmKompresor1
SS3KlimaError1AlarmKompresor2 | DIGITAL | IOD_SS3_TCP | 89 | 00089 | KlimaError[1].AlarmKompresor2
SS3KlimaError1FaultyEprom | DIGITAL | IOD_SS3_TCP | 90 | 00090 | KlimaError[1].FaultyEprom
SS3KlimaError1FenThermalCutout | DIGITAL | IOD_SS3_TCP | 91 | 00091 | KlimaError[1].FenThermalCutout
SS3KlimaError1GeneralAlarm | DIGITAL | IOD_SS3_TCP | 92 | 00092 | KlimaError[1].GeneralAlarm
SS3KlimaError1Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 93 | 00093 | KlimaError[1].Kompresor1naMejiStevilaObrUr
SS3KlimaError1Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 94 | 00094 | KlimaError[1].Kompresor2naMejiStevilaObrUr
SS3KlimaError1Kond1FenThermalCutout | DIGITAL | IOD_SS3_TCP | 95 | 00095 | KlimaError[1].Kond1FenThermalCutout
SS3KlimaError1Kond2FenThermalCutout | DIGITAL | IOD_SS3_TCP | 96 | 00096 | KlimaError[1].Kond2FenThermalCutout
SS3KlimaError1NapakaPriPretokuVode | DIGITAL | IOD_SS3_TCP | 97 | 00097 | KlimaError[1].NapakaPriPretokuVode
SS3KlimaError1NapakaPriPretokuZraka | DIGITAL | IOD_SS3_TCP | 98 | 00098 | KlimaError[1].NapakaPriPretokuZraka
SS3KlimaError1NapakaSenzorPovratVode | DIGITAL | IOD_SS3_TCP | 99 | 00099 | KlimaError[1].NapakaSenzorPovratVode
SS3KlimaError1NapakaSenzorPritiska | DIGITAL | IOD_SS3_TCP | 100 | 00100 | KlimaError[1].NapakaSenzorPritiska
SS3KlimaError1NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3_TCP | 101 | 00101 | KlimaError[1].NapakaSenzorTempIzpiha
SS3KlimaError1NapakaSenzorTempProstora | DIGITAL | IOD_SS3_TCP | 102 | 00102 | KlimaError[1].NapakaSenzorTempProstora
SS3KlimaError1NapakaSenzorVlaznosti | DIGITAL | IOD_SS3_TCP | 103 | 00103 | KlimaError[1].NapakaSenzorVlaznosti
SS3KlimaError1NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3_TCP | 104 | 00104 | KlimaError[1].NapakaSenzorZunanjeTemp
SS3KlimaError1NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3_TCP | 105 | 00105 | KlimaError[1].NapakaTSTemperaturaProstora
SS3KlimaError1NiTokaVVlazilcu | DIGITAL | IOD_SS3_TCP | 106 | 00106 | KlimaError[1].NiTokaVVlazilcu
SS3KlimaError1NiVodeVVlazilcu | DIGITAL | IOD_SS3_TCP | 107 | 00107 | KlimaError[1].NiVodeVVlazilcu
SS3KlimaError1NizekPritiskKompresor1 | DIGITAL | IOD_SS3_TCP | 108 | 00108 | KlimaError[1].NizekPritiskKompresor1
SS3KlimaError1NizekPritiskKompresor2 | DIGITAL | IOD_SS3_TCP | 109 | 00109 | KlimaError[1].NizekPritiskKompresor2
SS3KlimaError1NizkaTempPovratneVode | DIGITAL | IOD_SS3_TCP | 110 | 00110 | KlimaError[1].NizkaTempPovratneVode
SS3KlimaError1NizkaTempVProstoru | DIGITAL | IOD_SS3_TCP | 111 | 00111 | KlimaError[1].NizkaTempVProstoru
SS3KlimaError1NizkaVlaznost | DIGITAL | IOD_SS3_TCP | 112 | 00112 | KlimaError[1].NizkaVlaznost
SS3KlimaError1PozarniAlarm | DIGITAL | IOD_SS3_TCP | 113 | 00113 | KlimaError[1].PozarniAlarm
SS3KlimaError1StoppedByAlarms | DIGITAL | IOD_SS3_TCP | 114 | 00114 | KlimaError[1].StoppedByAlarms
SS3KlimaError1TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3_TCP | 115 | 00115 | KlimaError[1].TermZascInVisokPritiskKompr1
SS3KlimaError1TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3_TCP | 116 | 00116 | KlimaError[1].TermZascInVisokPritiskKompr2
SS3KlimaError1ThermalCutoutHeater1 | DIGITAL | IOD_SS3_TCP | 117 | 00117 | KlimaError[1].ThermalCutoutHeater1
SS3KlimaError1ThermalCutoutHeater2 | DIGITAL | IOD_SS3_TCP | 118 | 00118 | KlimaError[1].ThermalCutoutHeater2
SS3KlimaError1VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 119 | 00119 | KlimaError[1].VentilatorNaMejiStevilaObrUr
SS3KlimaError1VisokaTempPovratneVode | DIGITAL | IOD_SS3_TCP | 120 | 00120 | KlimaError[1].VisokaTempPovratneVode
SS3KlimaError1VisokaTempVProstoru | DIGITAL | IOD_SS3_TCP | 121 | 00121 | KlimaError[1].VisokaTempVProstoru
SS3KlimaError1VisokaVlaznost | DIGITAL | IOD_SS3_TCP | 122 | 00122 | KlimaError[1].VisokaVlaznost
SS3KlimaError1VisokPritiskVKrogu1 | DIGITAL | IOD_SS3_TCP | 123 | 00123 | KlimaError[1].VisokPritiskVKrogu1
SS3KlimaError1VisokPritiskVKrogu2 | DIGITAL | IOD_SS3_TCP | 124 | 00124 | KlimaError[1].VisokPritiskVKrogu2
SS3KlimaError1VisokTokVVlazilcu | DIGITAL | IOD_SS3_TCP | 125 | 00125 | KlimaError[1].VisokTokVVlazilcu
SS3KlimaError1VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 126 | 00126 | KlimaError[1].VlazilecnaMejiStevilaObrUr
SS3KlimaError1ZamasenFilter | DIGITAL | IOD_SS3_TCP | 127 | 00127 | KlimaError[1].ZamasenFilter
SS3KlimaError2AlarmKompresor1 | DIGITAL | IOD_SS3_TCP | 128 | 00128 | KlimaError[2].AlarmKompresor1
SS3KlimaError2AlarmKompresor2 | DIGITAL | IOD_SS3_TCP | 129 | 00129 | KlimaError[2].AlarmKompresor2
SS3KlimaError2FaultyEprom | DIGITAL | IOD_SS3_TCP | 130 | 00130 | KlimaError[2].FaultyEprom
SS3KlimaError2FenThermalCutout | DIGITAL | IOD_SS3_TCP | 131 | 00131 | KlimaError[2].FenThermalCutout
SS3KlimaError2GeneralAlarm | DIGITAL | IOD_SS3_TCP | 132 | 00132 | KlimaError[2].GeneralAlarm
SS3KlimaError2Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 133 | 00133 | KlimaError[2].Kompresor1naMejiStevilaObrUr
SS3KlimaError2Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 134 | 00134 | KlimaError[2].Kompresor2naMejiStevilaObrUr
SS3KlimaError2Kond1FenThermalCutout | DIGITAL | IOD_SS3_TCP | 135 | 00135 | KlimaError[2].Kond1FenThermalCutout
SS3KlimaError2Kond2FenThermalCutout | DIGITAL | IOD_SS3_TCP | 136 | 00136 | KlimaError[2].Kond2FenThermalCutout
SS3KlimaError2NapakaPriPretokuVode | DIGITAL | IOD_SS3_TCP | 137 | 00137 | KlimaError[2].NapakaPriPretokuVode
SS3KlimaError2NapakaPriPretokuZraka | DIGITAL | IOD_SS3_TCP | 138 | 00138 | KlimaError[2].NapakaPriPretokuZraka
SS3KlimaError2NapakaSenzorPovratVode | DIGITAL | IOD_SS3_TCP | 139 | 00139 | KlimaError[2].NapakaSenzorPovratVode
SS3KlimaError2NapakaSenzorPritiska | DIGITAL | IOD_SS3_TCP | 140 | 00140 | KlimaError[2].NapakaSenzorPritiska
SS3KlimaError2NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3_TCP | 141 | 00141 | KlimaError[2].NapakaSenzorTempIzpiha
SS3KlimaError2NapakaSenzorTempProstora | DIGITAL | IOD_SS3_TCP | 142 | 00142 | KlimaError[2].NapakaSenzorTempProstora
SS3KlimaError2NapakaSenzorVlaznosti | DIGITAL | IOD_SS3_TCP | 143 | 00143 | KlimaError[2].NapakaSenzorVlaznosti
SS3KlimaError2NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3_TCP | 144 | 00144 | KlimaError[2].NapakaSenzorZunanjeTemp
SS3KlimaError2NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3_TCP | 145 | 00145 | KlimaError[2].NapakaTSTemperaturaProstora
SS3KlimaError2NiTokaVVlazilcu | DIGITAL | IOD_SS3_TCP | 146 | 00146 | KlimaError[2].NiTokaVVlazilcu
SS3KlimaError2NiVodeVVlazilcu | DIGITAL | IOD_SS3_TCP | 147 | 00147 | KlimaError[2].NiVodeVVlazilcu
SS3KlimaError2NizekPritiskKompresor1 | DIGITAL | IOD_SS3_TCP | 148 | 00148 | KlimaError[2].NizekPritiskKompresor1
SS3KlimaError2NizekPritiskKompresor2 | DIGITAL | IOD_SS3_TCP | 149 | 00149 | KlimaError[2].NizekPritiskKompresor2
SS3KlimaError2NizkaTempPovratneVode | DIGITAL | IOD_SS3_TCP | 150 | 00150 | KlimaError[2].NizkaTempPovratneVode
SS3KlimaError2NizkaTempVProstoru | DIGITAL | IOD_SS3_TCP | 151 | 00151 | KlimaError[2].NizkaTempVProstoru
SS3KlimaError2NizkaVlaznost | DIGITAL | IOD_SS3_TCP | 152 | 00152 | KlimaError[2].NizkaVlaznost
SS3KlimaError2PozarniAlarm | DIGITAL | IOD_SS3_TCP | 153 | 00153 | KlimaError[2].PozarniAlarm
SS3KlimaError2StoppedByAlarms | DIGITAL | IOD_SS3_TCP | 154 | 00154 | KlimaError[2].StoppedByAlarms
SS3KlimaError2TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3_TCP | 155 | 00155 | KlimaError[2].TermZascInVisokPritiskKompr1
SS3KlimaError2TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3_TCP | 156 | 00156 | KlimaError[2].TermZascInVisokPritiskKompr2
SS3KlimaError2ThermalCutoutHeater1 | DIGITAL | IOD_SS3_TCP | 157 | 00157 | KlimaError[2].ThermalCutoutHeater1
SS3KlimaError2ThermalCutoutHeater2 | DIGITAL | IOD_SS3_TCP | 158 | 00158 | KlimaError[2].ThermalCutoutHeater2
SS3KlimaError2VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 159 | 00159 | KlimaError[2].VentilatorNaMejiStevilaObrUr
SS3KlimaError2VisokaTempPovratneVode | DIGITAL | IOD_SS3_TCP | 160 | 00160 | KlimaError[2].VisokaTempPovratneVode
SS3KlimaError2VisokaTempVProstoru | DIGITAL | IOD_SS3_TCP | 161 | 00161 | KlimaError[2].VisokaTempVProstoru
SS3KlimaError2VisokaVlaznost | DIGITAL | IOD_SS3_TCP | 162 | 00162 | KlimaError[2].VisokaVlaznost
SS3KlimaError2VisokPritiskVKrogu1 | DIGITAL | IOD_SS3_TCP | 163 | 00163 | KlimaError[2].VisokPritiskVKrogu1
SS3KlimaError2VisokPritiskVKrogu2 | DIGITAL | IOD_SS3_TCP | 164 | 00164 | KlimaError[2].VisokPritiskVKrogu2
SS3KlimaError2VisokTokVVlazilcu | DIGITAL | IOD_SS3_TCP | 165 | 00165 | KlimaError[2].VisokTokVVlazilcu
SS3KlimaError2VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 166 | 00166 | KlimaError[2].VlazilecnaMejiStevilaObrUr
SS3KlimaError2ZamasenFilter | DIGITAL | IOD_SS3_TCP | 167 | 00167 | KlimaError[2].ZamasenFilter
SS3KlimaError3AlarmKompresor1 | DIGITAL | IOD_SS3_TCP | 168 | 00168 | KlimaError[3].AlarmKompresor1
SS3KlimaError3AlarmKompresor2 | DIGITAL | IOD_SS3_TCP | 169 | 00169 | KlimaError[3].AlarmKompresor2
SS3KlimaError3FaultyEprom | DIGITAL | IOD_SS3_TCP | 170 | 00170 | KlimaError[3].FaultyEprom
SS3KlimaError3FenThermalCutout | DIGITAL | IOD_SS3_TCP | 171 | 00171 | KlimaError[3].FenThermalCutout
SS3KlimaError3GeneralAlarm | DIGITAL | IOD_SS3_TCP | 172 | 00172 | KlimaError[3].GeneralAlarm
SS3KlimaError3Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 173 | 00173 | KlimaError[3].Kompresor1naMejiStevilaObrUr
SS3KlimaError3Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 174 | 00174 | KlimaError[3].Kompresor2naMejiStevilaObrUr
SS3KlimaError3Kond1FenThermalCutout | DIGITAL | IOD_SS3_TCP | 175 | 00175 | KlimaError[3].Kond1FenThermalCutout
SS3KlimaError3Kond2FenThermalCutout | DIGITAL | IOD_SS3_TCP | 176 | 00176 | KlimaError[3].Kond2FenThermalCutout
SS3KlimaError3NapakaPriPretokuVode | DIGITAL | IOD_SS3_TCP | 177 | 00177 | KlimaError[3].NapakaPriPretokuVode
SS3KlimaError3NapakaPriPretokuZraka | DIGITAL | IOD_SS3_TCP | 178 | 00178 | KlimaError[3].NapakaPriPretokuZraka
SS3KlimaError3NapakaSenzorPovratVode | DIGITAL | IOD_SS3_TCP | 179 | 00179 | KlimaError[3].NapakaSenzorPovratVode
SS3KlimaError3NapakaSenzorPritiska | DIGITAL | IOD_SS3_TCP | 180 | 00180 | KlimaError[3].NapakaSenzorPritiska
SS3KlimaError3NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3_TCP | 181 | 00181 | KlimaError[3].NapakaSenzorTempIzpiha
SS3KlimaError3NapakaSenzorTempProstora | DIGITAL | IOD_SS3_TCP | 182 | 00182 | KlimaError[3].NapakaSenzorTempProstora
SS3KlimaError3NapakaSenzorVlaznosti | DIGITAL | IOD_SS3_TCP | 183 | 00183 | KlimaError[3].NapakaSenzorVlaznosti
SS3KlimaError3NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3_TCP | 184 | 00184 | KlimaError[3].NapakaSenzorZunanjeTemp
SS3KlimaError3NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3_TCP | 185 | 00185 | KlimaError[3].NapakaTSTemperaturaProstora
SS3KlimaError3NiTokaVVlazilcu | DIGITAL | IOD_SS3_TCP | 186 | 00186 | KlimaError[3].NiTokaVVlazilcu
SS3KlimaError3NiVodeVVlazilcu | DIGITAL | IOD_SS3_TCP | 187 | 00187 | KlimaError[3].NiVodeVVlazilcu
SS3KlimaError3NizekPritiskKompresor1 | DIGITAL | IOD_SS3_TCP | 188 | 00188 | KlimaError[3].NizekPritiskKompresor1
SS3KlimaError3NizekPritiskKompresor2 | DIGITAL | IOD_SS3_TCP | 189 | 00189 | KlimaError[3].NizekPritiskKompresor2
SS3KlimaError3NizkaTempPovratneVode | DIGITAL | IOD_SS3_TCP | 190 | 00190 | KlimaError[3].NizkaTempPovratneVode
SS3KlimaError3NizkaTempVProstoru | DIGITAL | IOD_SS3_TCP | 191 | 00191 | KlimaError[3].NizkaTempVProstoru
SS3KlimaError3NizkaVlaznost | DIGITAL | IOD_SS3_TCP | 192 | 00192 | KlimaError[3].NizkaVlaznost
SS3KlimaError3PozarniAlarm | DIGITAL | IOD_SS3_TCP | 193 | 00193 | KlimaError[3].PozarniAlarm
SS3KlimaError3StoppedByAlarms | DIGITAL | IOD_SS3_TCP | 194 | 00194 | KlimaError[3].StoppedByAlarms
SS3KlimaError3TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3_TCP | 195 | 00195 | KlimaError[3].TermZascInVisokPritiskKompr1
SS3KlimaError3TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3_TCP | 196 | 00196 | KlimaError[3].TermZascInVisokPritiskKompr2
SS3KlimaError3ThermalCutoutHeater1 | DIGITAL | IOD_SS3_TCP | 197 | 00197 | KlimaError[3].ThermalCutoutHeater1
SS3KlimaError3ThermalCutoutHeater2 | DIGITAL | IOD_SS3_TCP | 198 | 00198 | KlimaError[3].ThermalCutoutHeater2
SS3KlimaError3VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 199 | 00199 | KlimaError[3].VentilatorNaMejiStevilaObrUr
SS3KlimaError3VisokaTempPovratneVode | DIGITAL | IOD_SS3_TCP | 200 | 00200 | KlimaError[3].VisokaTempPovratneVode
SS3KlimaError3VisokaTempVProstoru | DIGITAL | IOD_SS3_TCP | 201 | 00201 | KlimaError[3].VisokaTempVProstoru
SS3KlimaError3VisokaVlaznost | DIGITAL | IOD_SS3_TCP | 202 | 00202 | KlimaError[3].VisokaVlaznost
SS3KlimaError3VisokPritiskVKrogu1 | DIGITAL | IOD_SS3_TCP | 203 | 00203 | KlimaError[3].VisokPritiskVKrogu1
SS3KlimaError3VisokPritiskVKrogu2 | DIGITAL | IOD_SS3_TCP | 204 | 00204 | KlimaError[3].VisokPritiskVKrogu2
SS3KlimaError3VisokTokVVlazilcu | DIGITAL | IOD_SS3_TCP | 205 | 00205 | KlimaError[3].VisokTokVVlazilcu
SS3KlimaError3VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 206 | 00206 | KlimaError[3].VlazilecnaMejiStevilaObrUr
SS3KlimaError3ZamasenFilter | DIGITAL | IOD_SS3_TCP | 207 | 00207 | KlimaError[3].ZamasenFilter
SS3KlimaError4AlarmKompresor1 | DIGITAL | IOD_SS3_TCP | 208 | 00208 | KlimaError[4].AlarmKompresor1
SS3KlimaError4AlarmKompresor2 | DIGITAL | IOD_SS3_TCP | 209 | 00209 | KlimaError[4].AlarmKompresor2
SS3KlimaError4FaultyEprom | DIGITAL | IOD_SS3_TCP | 210 | 00210 | KlimaError[4].FaultyEprom
SS3KlimaError4FenThermalCutout | DIGITAL | IOD_SS3_TCP | 211 | 00211 | KlimaError[4].FenThermalCutout
SS3KlimaError4GeneralAlarm | DIGITAL | IOD_SS3_TCP | 212 | 00212 | KlimaError[4].GeneralAlarm
SS3KlimaError4Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 213 | 00213 | KlimaError[4].Kompresor1naMejiStevilaObrUr
SS3KlimaError4Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 214 | 00214 | KlimaError[4].Kompresor2naMejiStevilaObrUr
SS3KlimaError4Kond1FenThermalCutout | DIGITAL | IOD_SS3_TCP | 215 | 00215 | KlimaError[4].Kond1FenThermalCutout
SS3KlimaError4Kond2FenThermalCutout | DIGITAL | IOD_SS3_TCP | 216 | 00216 | KlimaError[4].Kond2FenThermalCutout
SS3KlimaError4NapakaPriPretokuVode | DIGITAL | IOD_SS3_TCP | 217 | 00217 | KlimaError[4].NapakaPriPretokuVode
SS3KlimaError4NapakaPriPretokuZraka | DIGITAL | IOD_SS3_TCP | 218 | 00218 | KlimaError[4].NapakaPriPretokuZraka
SS3KlimaError4NapakaSenzorPovratVode | DIGITAL | IOD_SS3_TCP | 219 | 00219 | KlimaError[4].NapakaSenzorPovratVode
SS3KlimaError4NapakaSenzorPritiska | DIGITAL | IOD_SS3_TCP | 220 | 00220 | KlimaError[4].NapakaSenzorPritiska
SS3KlimaError4NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3_TCP | 221 | 00221 | KlimaError[4].NapakaSenzorTempIzpiha
SS3KlimaError4NapakaSenzorTempProstora | DIGITAL | IOD_SS3_TCP | 222 | 00222 | KlimaError[4].NapakaSenzorTempProstora
SS3KlimaError4NapakaSenzorVlaznosti | DIGITAL | IOD_SS3_TCP | 223 | 00223 | KlimaError[4].NapakaSenzorVlaznosti
SS3KlimaError4NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3_TCP | 224 | 00224 | KlimaError[4].NapakaSenzorZunanjeTemp
SS3KlimaError4NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3_TCP | 225 | 00225 | KlimaError[4].NapakaTSTemperaturaProstora
SS3KlimaError4NiTokaVVlazilcu | DIGITAL | IOD_SS3_TCP | 226 | 00226 | KlimaError[4].NiTokaVVlazilcu
SS3KlimaError4NiVodeVVlazilcu | DIGITAL | IOD_SS3_TCP | 227 | 00227 | KlimaError[4].NiVodeVVlazilcu
SS3KlimaError4NizekPritiskKompresor1 | DIGITAL | IOD_SS3_TCP | 228 | 00228 | KlimaError[4].NizekPritiskKompresor1
SS3KlimaError4NizekPritiskKompresor2 | DIGITAL | IOD_SS3_TCP | 229 | 00229 | KlimaError[4].NizekPritiskKompresor2
SS3KlimaError4NizkaTempPovratneVode | DIGITAL | IOD_SS3_TCP | 230 | 00230 | KlimaError[4].NizkaTempPovratneVode
SS3KlimaError4NizkaTempVProstoru | DIGITAL | IOD_SS3_TCP | 231 | 00231 | KlimaError[4].NizkaTempVProstoru
SS3KlimaError4NizkaVlaznost | DIGITAL | IOD_SS3_TCP | 232 | 00232 | KlimaError[4].NizkaVlaznost
SS3KlimaError4PozarniAlarm | DIGITAL | IOD_SS3_TCP | 233 | 00233 | KlimaError[4].PozarniAlarm
SS3KlimaError4StoppedByAlarms | DIGITAL | IOD_SS3_TCP | 234 | 00234 | KlimaError[4].StoppedByAlarms
SS3KlimaError4TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3_TCP | 235 | 00235 | KlimaError[4].TermZascInVisokPritiskKompr1
SS3KlimaError4TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3_TCP | 236 | 00236 | KlimaError[4].TermZascInVisokPritiskKompr2
SS3KlimaError4ThermalCutoutHeater1 | DIGITAL | IOD_SS3_TCP | 237 | 00237 | KlimaError[4].ThermalCutoutHeater1
SS3KlimaError4ThermalCutoutHeater2 | DIGITAL | IOD_SS3_TCP | 238 | 00238 | KlimaError[4].ThermalCutoutHeater2
SS3KlimaError4VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 239 | 00239 | KlimaError[4].VentilatorNaMejiStevilaObrUr
SS3KlimaError4VisokaTempPovratneVode | DIGITAL | IOD_SS3_TCP | 240 | 00240 | KlimaError[4].VisokaTempPovratneVode
SS3KlimaError4VisokaTempVProstoru | DIGITAL | IOD_SS3_TCP | 241 | 00241 | KlimaError[4].VisokaTempVProstoru
SS3KlimaError4VisokaVlaznost | DIGITAL | IOD_SS3_TCP | 242 | 00242 | KlimaError[4].VisokaVlaznost
SS3KlimaError4VisokPritiskVKrogu1 | DIGITAL | IOD_SS3_TCP | 243 | 00243 | KlimaError[4].VisokPritiskVKrogu1
SS3KlimaError4VisokPritiskVKrogu2 | DIGITAL | IOD_SS3_TCP | 244 | 00244 | KlimaError[4].VisokPritiskVKrogu2
SS3KlimaError4VisokTokVVlazilcu | DIGITAL | IOD_SS3_TCP | 245 | 00245 | KlimaError[4].VisokTokVVlazilcu
SS3KlimaError4VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 246 | 00246 | KlimaError[4].VlazilecnaMejiStevilaObrUr
SS3KlimaError4ZamasenFilter | DIGITAL | IOD_SS3_TCP | 247 | 00247 | KlimaError[4].ZamasenFilter
SS3NacDelovanjaKlime1_2_Avtomatsko | DIGITAL | IOD_SS3_TCP | 248 | 00248 | NacDelovanjaKlime1_2_Avtomatsko
SS3NacDelovanjaKlime3_4_Avtomatsko | DIGITAL | IOD_SS3_TCP | 249 | 00249 | NacDelovanjaKlime3_4_Avtomatsko
SS3NapakaSenzorTemp1 | DIGITAL | IOD_SS3_TCP | 250 | 00250 | NapakaSenzorTemp1
SS3NapakaSenzorTemp2 | DIGITAL | IOD_SS3_TCP | 251 | 00251 | NapakaSenzorTemp2
SS3NapakaSenzorTemp3 | DIGITAL | IOD_SS3_TCP | 252 | 00252 | NapakaSenzorTemp3
SS3NapakaSenzorVlaga1 | DIGITAL | IOD_SS3_TCP | 253 | 00253 | NapakaSenzorVlaga1
SS3NapakaSenzorVlaga2 | DIGITAL | IOD_SS3_TCP | 254 | 00254 | NapakaSenzorVlaga2
SS3NapakaSenzorVlaga3 | DIGITAL | IOD_SS3_TCP | 255 | 00255 | NapakaSenzorVlaga3
SS3NastaviCasNaKrmilniku | DIGITAL | IOD_SS3_TCP | 256 | 00256 | NastaviCasNaKrmilniku
SS3NastavitevUreKrUspesna | DIGITAL | IOD_SS3_TCP | 257 | 00257 | NastavitevUreKrUspesna
SS3OpozoriloBaterijaPLC | DIGITAL | IOD_SS3_TCP | 258 | 00258 | OpozoriloBaterijaPLC
SS3OsveziAlarmePanel | DIGITAL | IOD_SS3_TCP | 259 | 00259 | OsveziAlarmePanel
SS3RocniVklopKlima1 | DIGITAL | IOD_SS3_TCP | 260 | 00260 | RocniVklopKlima1
SS3RocniVklopKlima2 | DIGITAL | IOD_SS3_TCP | 261 | 00261 | RocniVklopKlima2
SS3RocniVklopKlima3 | DIGITAL | IOD_SS3_TCP | 262 | 00262 | RocniVklopKlima3
SS3RocniVklopKlima4 | DIGITAL | IOD_SS3_TCP | 263 | 00263 | RocniVklopKlima4
SS3SinhronizacijaPanelOK | DIGITAL | IOD_SS3_TCP | 264 | 00264 | SinhronizacijaPanelOK
SS3SinhronizirajCas_Panel | DIGITAL | IOD_SS3_TCP | 265 | 00265 | SinhronizirajCas_Panel
SS3SkupneNapakeNaprav_Klima1 | DIGITAL | IOD_SS3_TCP | 266 | 00266 | SkupneNapakeNaprav_Klima1
SS3SkupneNapakeNaprav_Klima2 | DIGITAL | IOD_SS3_TCP | 267 | 00267 | SkupneNapakeNaprav_Klima2
SS3SkupneNapakeNaprav_Klima3 | DIGITAL | IOD_SS3_TCP | 268 | 00268 | SkupneNapakeNaprav_Klima3
SS3SkupneNapakeNaprav_Klima4 | DIGITAL | IOD_SS3_TCP | 269 | 00269 | SkupneNapakeNaprav_Klima4
SS3SkupneNapakeNaprav_Komunikacija | DIGITAL | IOD_SS3_TCP | 270 | 00270 | SkupneNapakeNaprav_Komunikacija
SS3SkupneNapakeNaprav_TempVlaga | DIGITAL | IOD_SS3_TCP | 271 | 00271 | SkupneNapakeNaprav_TempVlaga
SS3StanjeKlimat1_Delovanje | DIGITAL | IOD_SS3_TCP | 272 | 00272 | StanjeKlimat1_Delovanje
SS3StanjeKlimat2_Delovanje | DIGITAL | IOD_SS3_TCP | 273 | 00273 | StanjeKlimat2_Delovanje
SS3StanjeKlimat3_Delovanje | DIGITAL | IOD_SS3_TCP | 274 | 00274 | StanjeKlimat3_Delovanje
SS3StanjeKlimat4_Delovanje | DIGITAL | IOD_SS3_TCP | 275 | 00275 | StanjeKlimat4_Delovanje
SS3StanjeUPSKrmOmara_BaterijskiNacin | DIGITAL | IOD_SS3_TCP | 276 | 00276 | StanjeUPSKrmOmara_BaterijskiNacin
SS3StanjeUPSKrmOmara_Polnjenje | DIGITAL | IOD_SS3_TCP | 277 | 00277 | StanjeUPSKrmOmara_Polnjenje
SS3UserLoggedIn | DIGITAL | IOD_SS3_TCP | 278 | 00278 | UserLoggedIn
SS3XVH_AlarmOn | DIGITAL | IOD_SS3_TCP | 279 | 00279 | XVH_AlarmOn
SS3Klimat1_Vklop | DIGITAL | IOD_SS3_TCP | 280 | 00280 | Klimat1_Vklop
SS3Klimat2_Vklop | DIGITAL | IOD_SS3_TCP | 281 | 00281 | Klimat2_Vklop
SS3Klimat3_Vklop | DIGITAL | IOD_SS3_TCP | 282 | 00282 | Klimat3_Vklop
SS3Klimat4_Vklop | DIGITAL | IOD_SS3_TCP | 283 | 00283 | Klimat4_Vklop
SS3ErrorComKlima1Error | DIGITAL | IOD_SS3_TCP | 284 | 00284 | ErrorComKlima[1].Error
SS3ErrorComKlima2Error | DIGITAL | IOD_SS3_TCP | 285 | 00285 | ErrorComKlima[2].Error
SS3ErrorComKlima3Error | DIGITAL | IOD_SS3_TCP | 286 | 00286 | ErrorComKlima[3].Error
SS3ErrCommScada2 | DIGITAL | IOD_SS3_TCP | 287 | 00287 | ErrCommScada2
SS3ComSCADA2 | DIGITAL | IOD_SS3_TCP | 288 | 00288 | ComSCADA2
SS3ComSCADA3 | DIGITAL | IOD_SS3_TCP | 289 | 00289 | ComSCADA3
SS3AlarmTempTIA4Previsoka | DIGITAL | IOD_SS3_TCP | 290 | 00290 | AlarmTempTIA4Previsoka
SS3AlarmTempTIA5Previsoka | DIGITAL | IOD_SS3_TCP | 291 | 00291 | AlarmTempTIA5Previsoka
SS3NapakaSenzorTemp4 | DIGITAL | IOD_SS3_TCP | 292 | 00292 | NapakaSenzorTemp4
SS3NapakaSenzorTemp5 | DIGITAL | IOD_SS3_TCP | 293 | 00293 | NapakaSenzorTemp5
SS3NapakaSenzorVlaga4 | DIGITAL | IOD_SS3_TCP | 294 | 00294 | NapakaSenzorVlaga4
SS3NapakaSenzorVlaga5 | DIGITAL | IOD_SS3_TCP | 295 | 00295 | NapakaSenzorVlaga5
SS3AlarmTempTIA124Previsoka | DIGITAL | IOD_SS3_TCP | 296 | 00296 | AlarmTempTIA124Previsoka
SS3AlarmTempTIA35Previsoka | DIGITAL | IOD_SS3_TCP | 297 | 00297 | AlarmTempTIA35Previsoka
SS3DatumCasDan | INT | IOD_SS3_TCP | 1 | 40001 | DatumCas.Dan | BYTE
SS3DatumCasLeto | INT | IOD_SS3_TCP | 2 | 40002 | DatumCas.Leto | BYTE
SS3DatumCasLeto2 | INT | IOD_SS3_TCP | 3 | 40003 | DatumCas.Leto2
SS3DatumCasMesec | INT | IOD_SS3_TCP | 4 | 40004 | DatumCas.Mesec | BYTE
SS3DatumCasMinuta | INT | IOD_SS3_TCP | 5 | 40005 | DatumCas.Minuta | BYTE
SS3DatumCasSekunda | INT | IOD_SS3_TCP | 6 | 40006 | DatumCas.Sekunda | BYTE
SS3DatumCasUra | INT | IOD_SS3_TCP | 7 | 40007 | DatumCas.Ura | BYTE
SS3ErrorComKlima4Status | INT | IOD_SS3_TCP | 8 | 40008 | ErrorComKlima[4].Status
SS3Klima1GrelecStatus | INT | IOD_SS3_TCP | 9 | 40009 | Klima[1].GrelecStatus | BYTE
SS3Klima1IzhodniVentStatus | INT | IOD_SS3_TCP | 10 | 40010 | Klima[1].IzhodniVentStatus | BYTE
SS3Klima1KompresorStatus | INT | IOD_SS3_TCP | 11 | 40011 | Klima[1].KompresorStatus | BYTE
SS3Klima1VlazilecStatus | INT | IOD_SS3_TCP | 12 | 40012 | Klima[1].VlazilecStatus | BYTE
SS3Klima2GrelecStatus | INT | IOD_SS3_TCP | 13 | 40013 | Klima[2].GrelecStatus | BYTE
SS3Klima2IzhodniVentStatus | INT | IOD_SS3_TCP | 14 | 40014 | Klima[2].IzhodniVentStatus | BYTE
SS3Klima2KompresorStatus | INT | IOD_SS3_TCP | 15 | 40015 | Klima[2].KompresorStatus | BYTE
SS3Klima2VlazilecStatus | INT | IOD_SS3_TCP | 16 | 40016 | Klima[2].VlazilecStatus | BYTE
SS3Klima3GrelecStatus | INT | IOD_SS3_TCP | 17 | 40017 | Klima[3].GrelecStatus | BYTE
SS3Klima3IzhodniVentStatus | INT | IOD_SS3_TCP | 18 | 40018 | Klima[3].IzhodniVentStatus | BYTE
SS3Klima3KompresorStatus | INT | IOD_SS3_TCP | 19 | 40019 | Klima[3].KompresorStatus | BYTE
SS3Klima3VlazilecStatus | INT | IOD_SS3_TCP | 20 | 40020 | Klima[3].VlazilecStatus | BYTE
SS3Klima4GrelecStatus | INT | IOD_SS3_TCP | 21 | 40021 | Klima[4].GrelecStatus | BYTE
SS3Klima4IzhodniVentStatus | INT | IOD_SS3_TCP | 22 | 40022 | Klima[4].IzhodniVentStatus | BYTE
SS3Klima4KompresorStatus | INT | IOD_SS3_TCP | 23 | 40023 | Klima[4].KompresorStatus | BYTE
SS3Klima4VlazilecStatus | INT | IOD_SS3_TCP | 24 | 40024 | Klima[4].VlazilecStatus | BYTE
SS3StUrZaPreklopKlim1_2 | INT | IOD_SS3_TCP | 25 | 40025 | StUrZaPreklopKlim1_2
SS3StUrZaPreklopKlim3_4 | INT | IOD_SS3_TCP | 26 | 40026 | StUrZaPreklopKlim3_4
SS3UPSstatus_Prikaz_PanelSCADA | INT | IOD_SS3_TCP | 27 | 40027 | UPSstatus_Prikaz_PanelSCADA | BYTE
SS3UserCurrentLevel | INT | IOD_SS3_TCP | 28 | 40028 | UserCurrentLevel | BYTE
SS3ErrorComKlima1Code0 | INT | IOD_SS3_TCP | 29 | 40029 | ErrorComKlima[1].Code[0] | BYTE
SS3ErrorComKlima1Code10 | INT | IOD_SS3_TCP | 30 | 40030 | ErrorComKlima[1].Code[10] | BYTE
SS3ErrorComKlima1Code11 | INT | IOD_SS3_TCP | 31 | 40031 | ErrorComKlima[1].Code[11] | BYTE
SS3ErrorComKlima1Code12 | INT | IOD_SS3_TCP | 32 | 40032 | ErrorComKlima[1].Code[12] | BYTE
SS3ErrorComKlima1Code13 | INT | IOD_SS3_TCP | 33 | 40033 | ErrorComKlima[1].Code[13] | BYTE
SS3ErrorComKlima1Code14 | INT | IOD_SS3_TCP | 34 | 40034 | ErrorComKlima[1].Code[14] | BYTE
SS3ErrorComKlima1Code15 | INT | IOD_SS3_TCP | 35 | 40035 | ErrorComKlima[1].Code[15] | BYTE
SS3ErrorComKlima1Code1 | INT | IOD_SS3_TCP | 36 | 40036 | ErrorComKlima[1].Code[1] | BYTE
SS3ErrorComKlima1Code2 | INT | IOD_SS3_TCP | 37 | 40037 | ErrorComKlima[1].Code[2] | BYTE
SS3ErrorComKlima1Code3 | INT | IOD_SS3_TCP | 38 | 40038 | ErrorComKlima[1].Code[3] | BYTE
SS3ErrorComKlima1Code4 | INT | IOD_SS3_TCP | 39 | 40039 | ErrorComKlima[1].Code[4] | BYTE
SS3ErrorComKlima1Code5 | INT | IOD_SS3_TCP | 40 | 40040 | ErrorComKlima[1].Code[5] | BYTE
SS3ErrorComKlima1Code6 | INT | IOD_SS3_TCP | 41 | 40041 | ErrorComKlima[1].Code[6] | BYTE
SS3ErrorComKlima1Code7 | INT | IOD_SS3_TCP | 42 | 40042 | ErrorComKlima[1].Code[7] | BYTE
SS3ErrorComKlima1Code8 | INT | IOD_SS3_TCP | 43 | 40043 | ErrorComKlima[1].Code[8] | BYTE
SS3ErrorComKlima1Code9 | INT | IOD_SS3_TCP | 44 | 40044 | ErrorComKlima[1].Code[9] | BYTE
SS3ErrorComKlima1Status | INT | IOD_SS3_TCP | 45 | 40045 | ErrorComKlima[1].Status
SS3ErrorComKlima2Code0 | INT | IOD_SS3_TCP | 46 | 40046 | ErrorComKlima[2].Code[0] | BYTE
SS3ErrorComKlima2Code10 | INT | IOD_SS3_TCP | 47 | 40047 | ErrorComKlima[2].Code[10] | BYTE
SS3ErrorComKlima2Code11 | INT | IOD_SS3_TCP | 48 | 40048 | ErrorComKlima[2].Code[11] | BYTE
SS3ErrorComKlima2Code12 | INT | IOD_SS3_TCP | 49 | 40049 | ErrorComKlima[2].Code[12] | BYTE
SS3ErrorComKlima2Code13 | INT | IOD_SS3_TCP | 50 | 40050 | ErrorComKlima[2].Code[13] | BYTE
SS3ErrorComKlima2Code14 | INT | IOD_SS3_TCP | 51 | 40051 | ErrorComKlima[2].Code[14] | BYTE
SS3ErrorComKlima2Code15 | INT | IOD_SS3_TCP | 52 | 40052 | ErrorComKlima[2].Code[15] | BYTE
SS3ErrorComKlima2Code1 | INT | IOD_SS3_TCP | 53 | 40053 | ErrorComKlima[2].Code[1] | BYTE
SS3ErrorComKlima2Code2 | INT | IOD_SS3_TCP | 54 | 40054 | ErrorComKlima[2].Code[2] | BYTE
SS3ErrorComKlima2Code3 | INT | IOD_SS3_TCP | 55 | 40055 | ErrorComKlima[2].Code[3] | BYTE
SS3ErrorComKlima2Code4 | INT | IOD_SS3_TCP | 56 | 40056 | ErrorComKlima[2].Code[4] | BYTE
SS3ErrorComKlima2Code5 | INT | IOD_SS3_TCP | 57 | 40057 | ErrorComKlima[2].Code[5] | BYTE
SS3ErrorComKlima2Code6 | INT | IOD_SS3_TCP | 58 | 40058 | ErrorComKlima[2].Code[6] | BYTE
SS3ErrorComKlima2Code7 | INT | IOD_SS3_TCP | 59 | 40059 | ErrorComKlima[2].Code[7] | BYTE
SS3ErrorComKlima2Code8 | INT | IOD_SS3_TCP | 60 | 40060 | ErrorComKlima[2].Code[8] | BYTE
SS3ErrorComKlima2Code9 | INT | IOD_SS3_TCP | 61 | 40061 | ErrorComKlima[2].Code[9] | BYTE
SS3ErrorComKlima2Status | INT | IOD_SS3_TCP | 62 | 40062 | ErrorComKlima[2].Status
SS3ErrorComKlima3Code0 | INT | IOD_SS3_TCP | 63 | 40063 | ErrorComKlima[3].Code[0] | BYTE
SS3ErrorComKlima3Code10 | INT | IOD_SS3_TCP | 64 | 40064 | ErrorComKlima[3].Code[10] | BYTE
SS3ErrorComKlima3Code11 | INT | IOD_SS3_TCP | 65 | 40065 | ErrorComKlima[3].Code[11] | BYTE
SS3ErrorComKlima3Code12 | INT | IOD_SS3_TCP | 66 | 40066 | ErrorComKlima[3].Code[12] | BYTE
SS3ErrorComKlima3Code13 | INT | IOD_SS3_TCP | 67 | 40067 | ErrorComKlima[3].Code[13] | BYTE
SS3ErrorComKlima3Code14 | INT | IOD_SS3_TCP | 68 | 40068 | ErrorComKlima[3].Code[14] | BYTE
SS3ErrorComKlima3Code15 | INT | IOD_SS3_TCP | 69 | 40069 | ErrorComKlima[3].Code[15] | BYTE
SS3ErrorComKlima3Code1 | INT | IOD_SS3_TCP | 70 | 40070 | ErrorComKlima[3].Code[1] | BYTE
SS3ErrorComKlima3Code2 | INT | IOD_SS3_TCP | 71 | 40071 | ErrorComKlima[3].Code[2] | BYTE
SS3ErrorComKlima3Code3 | INT | IOD_SS3_TCP | 72 | 40072 | ErrorComKlima[3].Code[3] | BYTE
SS3ErrorComKlima3Code4 | INT | IOD_SS3_TCP | 73 | 40073 | ErrorComKlima[3].Code[4] | BYTE
SS3ErrorComKlima3Code5 | INT | IOD_SS3_TCP | 74 | 40074 | ErrorComKlima[3].Code[5] | BYTE
SS3ErrorComKlima3Code6 | INT | IOD_SS3_TCP | 75 | 40075 | ErrorComKlima[3].Code[6] | BYTE
SS3ErrorComKlima3Code7 | INT | IOD_SS3_TCP | 76 | 40076 | ErrorComKlima[3].Code[7] | BYTE
SS3ErrorComKlima3Code8 | INT | IOD_SS3_TCP | 77 | 40077 | ErrorComKlima[3].Code[8] | BYTE
SS3ErrorComKlima3Code9 | INT | IOD_SS3_TCP | 78 | 40078 | ErrorComKlima[3].Code[9] | BYTE
SS3ErrorComKlima3Status | INT | IOD_SS3_TCP | 79 | 40079 | ErrorComKlima[3].Status
SS3ErrorComKlima4Code0 | INT | IOD_SS3_TCP | 80 | 40080 | ErrorComKlima[4].Code[0] | BYTE
SS3ErrorComKlima4Code10 | INT | IOD_SS3_TCP | 81 | 40081 | ErrorComKlima[4].Code[10] | BYTE
SS3ErrorComKlima4Code11 | INT | IOD_SS3_TCP | 82 | 40082 | ErrorComKlima[4].Code[11] | BYTE
SS3ErrorComKlima4Code12 | INT | IOD_SS3_TCP | 83 | 40083 | ErrorComKlima[4].Code[12] | BYTE
SS3ErrorComKlima4Code13 | INT | IOD_SS3_TCP | 84 | 40084 | ErrorComKlima[4].Code[13] | BYTE
SS3ErrorComKlima4Code14 | INT | IOD_SS3_TCP | 85 | 40085 | ErrorComKlima[4].Code[14] | BYTE
SS3ErrorComKlima4Code15 | INT | IOD_SS3_TCP | 86 | 40086 | ErrorComKlima[4].Code[15] | BYTE
SS3ErrorComKlima4Code1 | INT | IOD_SS3_TCP | 87 | 40087 | ErrorComKlima[4].Code[1] | BYTE
SS3ErrorComKlima4Code2 | INT | IOD_SS3_TCP | 88 | 40088 | ErrorComKlima[4].Code[2] | BYTE
SS3ErrorComKlima4Code3 | INT | IOD_SS3_TCP | 89 | 40089 | ErrorComKlima[4].Code[3] | BYTE
SS3ErrorComKlima4Code4 | INT | IOD_SS3_TCP | 90 | 40090 | ErrorComKlima[4].Code[4] | BYTE
SS3ErrorComKlima4Code5 | INT | IOD_SS3_TCP | 91 | 40091 | ErrorComKlima[4].Code[5] | BYTE
SS3ErrorComKlima4Code6 | INT | IOD_SS3_TCP | 92 | 40092 | ErrorComKlima[4].Code[6] | BYTE
SS3ErrorComKlima4Code7 | INT | IOD_SS3_TCP | 93 | 40093 | ErrorComKlima[4].Code[7] | BYTE
SS3ErrorComKlima4Code8 | INT | IOD_SS3_TCP | 94 | 40094 | ErrorComKlima[4].Code[8] | BYTE
SS3ErrorComKlima4Code9 | INT | IOD_SS3_TCP | 95 | 40095 | ErrorComKlima[4].Code[9] | BYTE
SS3kom_nast_cas_izpada | INT | IOD_SS3_TCP | 96 | 40096 | kom_nast_cas_izpada
SS3AktualniSetPointTemp1_2 | REAL | IOD_SS3_TCP | 4001 | 44001 | AktualniSetPointTemp1_2
SS3AktualniSetPointTemp3_4 | REAL | IOD_SS3_TCP | 4003 | 44003 | AktualniSetPointTemp3_4
SS3Klima1ure | REAL | IOD_SS3_TCP | 4005 | 44005 | Klima1ure
SS3Klima2ure | REAL | IOD_SS3_TCP | 4007 | 44007 | Klima2ure
SS3Klima3ure | REAL | IOD_SS3_TCP | 4009 | 44009 | Klima3ure
SS3Klima4ure | REAL | IOD_SS3_TCP | 4011 | 44011 | Klima4ure
SS3Klima1NastTempProstora | REAL | IOD_SS3_TCP | 4013 | 44013 | Klima[1].NastTempProstora
SS3Klima1NastVlaznost | REAL | IOD_SS3_TCP | 4015 | 44015 | Klima[1].NastVlaznost
SS3Klima1ObratovalneUre | REAL | IOD_SS3_TCP | 4017 | 44017 | Klima[1].ObratovalneUre
SS3Klima1TemperaturaProstora | REAL | IOD_SS3_TCP | 4019 | 44019 | Klima[1].TemperaturaProstora
SS3Klima1VlaznostProstora | REAL | IOD_SS3_TCP | 4021 | 44021 | Klima[1].VlaznostProstora
SS3Klima2NastTempProstora | REAL | IOD_SS3_TCP | 4023 | 44023 | Klima[2].NastTempProstora
SS3Klima2NastVlaznost | REAL | IOD_SS3_TCP | 4025 | 44025 | Klima[2].NastVlaznost
SS3Klima2ObratovalneUre | REAL | IOD_SS3_TCP | 4027 | 44027 | Klima[2].ObratovalneUre
SS3Klima2TemperaturaProstora | REAL | IOD_SS3_TCP | 4029 | 44029 | Klima[2].TemperaturaProstora
SS3Klima2VlaznostProstora | REAL | IOD_SS3_TCP | 4031 | 44031 | Klima[2].VlaznostProstora
SS3Klima3NastTempProstora | REAL | IOD_SS3_TCP | 4033 | 44033 | Klima[3].NastTempProstora
SS3Klima3NastVlaznost | REAL | IOD_SS3_TCP | 4035 | 44035 | Klima[3].NastVlaznost
SS3Klima3ObratovalneUre | REAL | IOD_SS3_TCP | 4037 | 44037 | Klima[3].ObratovalneUre
SS3Klima3TemperaturaProstora | REAL | IOD_SS3_TCP | 4039 | 44039 | Klima[3].TemperaturaProstora
SS3Klima3VlaznostProstora | REAL | IOD_SS3_TCP | 4041 | 44041 | Klima[3].VlaznostProstora
SS3Klima4NastTempProstora | REAL | IOD_SS3_TCP | 4043 | 44043 | Klima[4].NastTempProstora
SS3Klima4NastVlaznost | REAL | IOD_SS3_TCP | 4045 | 44045 | Klima[4].NastVlaznost
SS3Klima4ObratovalneUre | REAL | IOD_SS3_TCP | 4047 | 44047 | Klima[4].ObratovalneUre
SS3Klima4TemperaturaProstora | REAL | IOD_SS3_TCP | 4049 | 44049 | Klima[4].TemperaturaProstora
SS3Klima4VlaznostProstora | REAL | IOD_SS3_TCP | 4051 | 44051 | Klima[4].VlaznostProstora
SS3SKTemp1 | REAL | IOD_SS3_TCP | 4053 | 44053 | SKTemp1
SS3SKTemp2 | REAL | IOD_SS3_TCP | 4055 | 44055 | SKTemp2
SS3SKTemp3 | REAL | IOD_SS3_TCP | 4057 | 44057 | SKTemp3
SS3SKVlaga1 | REAL | IOD_SS3_TCP | 4059 | 44059 | SKVlaga1
SS3SKVlaga2 | REAL | IOD_SS3_TCP | 4061 | 44061 | SKVlaga2
SS3SKVlaga3 | REAL | IOD_SS3_TCP | 4063 | 44063 | SKVlaga3
SS3TempZaAlarm1_2 | REAL | IOD_SS3_TCP | 4065 | 44065 | TempZaAlarm1_2
SS3TempZaAlarm3_4 | REAL | IOD_SS3_TCP | 4067 | 44067 | TempZaAlarm3_4
SS3TempZaAlarmTIA1 | REAL | IOD_SS3_TCP | 4069 | 44069 | TempZaAlarmTIA1
SS3TempZaAlarmTIA2 | REAL | IOD_SS3_TCP | 4071 | 44071 | TempZaAlarmTIA2
SS3TempZaAlarmTIA3 | REAL | IOD_SS3_TCP | 4073 | 44073 | TempZaAlarmTIA3
SS3TempZaVklopObehKlim1_2 | REAL | IOD_SS3_TCP | 4075 | 44075 | TempZaVklopObehKlim1_2
SS3TempZaVklopObehKlim3_4 | REAL | IOD_SS3_TCP | 4077 | 44077 | TempZaVklopObehKlim3_4
SS3SKTemp4 | REAL | IOD_SS3_TCP | 4079 | 44079 | SKTemp4
SS3SKTemp5 | REAL | IOD_SS3_TCP | 4081 | 44081 | SKTemp5
SS3SKVlaga4 | REAL | IOD_SS3_TCP | 4083 | 44083 | SKVlaga4
SS3SKVlaga5 | REAL | IOD_SS3_TCP | 4085 | 44085 | SKVlaga5
SS3TempZaAlarmTIA4 | REAL | IOD_SS3_TCP | 4087 | 44087 | TempZaAlarmTIA4
SS3TempZaAlarmTIA5 | REAL | IOD_SS3_TCP | 4089 | 44089 | TempZaAlarmTIA5
SS3SKTempServSoba1Povpr | REAL | IOD_SS3_TCP | 4091 | 44091 | SKTempServSoba1Povpr
SS3SKTempServSoba2Povpr | REAL | IOD_SS3_TCP | 4093 | 44093 | SKTempServSoba2Povpr
SS3TempZaAlarmTIA124 | REAL | IOD_SS3_TCP | 4095 | 44095 | TempZaAlarmTIA124
SS3TempZaAlarmTIA35 | REAL | IOD_SS3_TCP | 4097 | 44097 | TempZaAlarmTIA35
SS3UserName | STRING | IOD_SS3_TCP | 5001 | 45001[15] | UserName
SS3Date_Time0 | STRING | IOD_SS3_TCP | 5016 | 45016[15] | Date_Time[0]
SS3Date_Time1 | STRING | IOD_SS3_TCP | 5031 | 45031[15] | Date_Time[1]
SS3Date_Time2 | STRING | IOD_SS3_TCP | 5046 | 45046[15] | Date_Time[2]
SS3Date_Time3 | STRING | IOD_SS3_TCP | 5061 | 45061[15] | Date_Time[3]

## variable_new
SS3Pulzi1s | DIGITAL | IOD_SS3_disk | D1
ASS3_omogoci_sms | DIGITAL | IOD_SS3_disk | D202[200]
BSS3_omogoci_sms | DIGITAL | IOD_SS3_disk | D402[200]
CSS3_omogoci_sms | DIGITAL | IOD_SS3_disk | D602[200]
DSS3_omogoci_sms | DIGITAL | IOD_SS3_disk | D802[200]
ESS3_omogoci_sms | DIGITAL | IOD_SS3_disk | D1002[200]
FSS3_omogoci_sms | DIGITAL | IOD_SS3_disk | D1202[200]
SS3AlarmKlimat1_Napaka_Om | DIGITAL | IOD_SS3_disk | D1402
SS3AlarmKlimat2_Napaka_Om | DIGITAL | IOD_SS3_disk | D1403
SS3AlarmKlimat3_Napaka_Om | DIGITAL | IOD_SS3_disk | D1404
SS3AlarmKlimat4_Napaka_Om | DIGITAL | IOD_SS3_disk | D1405
SS3NapakaSenzorTemp1_Om | DIGITAL | IOD_SS3_disk | D1406
SS3NapakaSenzorTemp2_Om | DIGITAL | IOD_SS3_disk | D1407
SS3NapakaSenzorTemp3_Om | DIGITAL | IOD_SS3_disk | D1408
SS3NapakaSenzorVlaga1_Om | DIGITAL | IOD_SS3_disk | D1409
SS3NapakaSenzorVlaga2_Om | DIGITAL | IOD_SS3_disk | D1410
SS3NapakaSenzorVlaga3_Om | DIGITAL | IOD_SS3_disk | D1411
SS3OpozoriloBaterijaPLC_Om | DIGITAL | IOD_SS3_disk | D1412
SS3AlarmUPSKrmOmara_Alarm_Om | DIGITAL | IOD_SS3_disk | D1413
SS3StanjeUPSKrmOmara_BaterijskiNacin_Om | DIGITAL | IOD_SS3_disk | D1414
SS3StanjeUPSKrmOmara_Polnenje_Om | DIGITAL | IOD_SS3_disk | D1415
SS3AlarmLAH1_RazlitjeVode_Om | DIGITAL | IOD_SS3_disk | D1416
SS3AlarmLAH2_RazlitjeVode_Om | DIGITAL | IOD_SS3_disk | D1417
SS3ErrComPort2_Om | DIGITAL | IOD_SS3_disk | D1418
SS3ErrComPanelPLC_Om | DIGITAL | IOD_SS3_disk | D1419
SS3ErrComSCADA_Om | DIGITAL | IOD_SS3_disk | D1420
SS3ErrComKlima1_Om | DIGITAL | IOD_SS3_disk | D1421
SS3ErrComKlima2_Om | DIGITAL | IOD_SS3_disk | D1422
SS3ErrComKlima3_Om | DIGITAL | IOD_SS3_disk | D1423
SS3ErrComKlima4_Om | DIGITAL | IOD_SS3_disk | D1424
SS3KlimaError1AlarmKompresor1_Om | DIGITAL | IOD_SS3_disk | D1425
SS3KlimaError1AlarmKompresor2_Om | DIGITAL | IOD_SS3_disk | D1426
SS3KlimaError1NizekPritiskKompresor1_Om | DIGITAL | IOD_SS3_disk | D1427
SS3KlimaError1NizekPritiskKompresor2_Om | DIGITAL | IOD_SS3_disk | D1428
SS3KlimaError1NapakaPriPretokuZraka_Om | DIGITAL | IOD_SS3_disk | D1429
SS3KlimaError1FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1430
SS3KlimaError1ThermalCutoutHeater1_Om | DIGITAL | IOD_SS3_disk | D1431
SS3KlimaError1ThermalCutoutHeater2_Om | DIGITAL | IOD_SS3_disk | D1432
SS3KlimaError1PozarniAlarm_Om | DIGITAL | IOD_SS3_disk | D1433
SS3KlimaError1ZamasenFilter_Om | DIGITAL | IOD_SS3_disk | D1434
SS3KlimaError1VisokaTempVProstoru_Om | DIGITAL | IOD_SS3_disk | D1435
SS3KlimaError1NizkaTempVProstoru_Om | DIGITAL | IOD_SS3_disk | D1436
SS3KlimaError1VisokaVlaznost_Om | DIGITAL | IOD_SS3_disk | D1437
SS3KlimaError1NizkaVlaznost_Om | DIGITAL | IOD_SS3_disk | D1438
SS3KlimaError1Kompresor1naMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1439
SS3KlimaError1Kompresor2naMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1440
SS3KlimaError1VentilatorNaMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1441
SS3KlimaError1NapakaTSTemperaturaProstora_Om | DIGITAL | IOD_SS3_disk | D1442
SS3KlimaError1NapakaSenzorVlaznosti_Om | DIGITAL | IOD_SS3_disk | D1443
SS3KlimaError1NapakaSenzorPritiska_Om | DIGITAL | IOD_SS3_disk | D1444
SS3KlimaError1VisokTokVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1445
SS3KlimaError1NiVodeVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1446
SS3KlimaError1NiTokaVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1447
SS3KlimaError1VisokPritiskVKrogu1_Om | DIGITAL | IOD_SS3_disk | D1448
SS3KlimaError1VisokPritiskVKrogu2_Om | DIGITAL | IOD_SS3_disk | D1449
SS3KlimaError1IzlivVode_Om | DIGITAL | IOD_SS3_disk | D1450
SS3KlimaError1TermZascInVisokPritiskKompr1_Om | DIGITAL | IOD_SS3_disk | D1451
SS3KlimaError1VlazilecnaMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1452
SS3KlimaError1TermZascInVisokPritiskKompr2_Om | DIGITAL | IOD_SS3_disk | D1453
SS3KlimaError1NapakaPriPretokuVode_Om | DIGITAL | IOD_SS3_disk | D1454
SS3KlimaError1Kond1FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1455
SS3KlimaError1Kond2FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1456
SS3KlimaError1ZunanjiAlarm_Om | DIGITAL | IOD_SS3_disk | D1457
SS3KlimaError1FaultyEprom_Om | DIGITAL | IOD_SS3_disk | D1458
SS3KlimaError1NapakaSenzorTempIzpiha_Om | DIGITAL | IOD_SS3_disk | D1459
SS3KlimaError1NapakaSenzorTempProstora_Om | DIGITAL | IOD_SS3_disk | D1460
SS3KlimaError1NapakaSenzorZunanjeTemp_Om | DIGITAL | IOD_SS3_disk | D1461
SS3KlimaError1NizkaTempPovratneVode_Om | DIGITAL | IOD_SS3_disk | D1462
SS3KlimaError1StoppedByAlarms_Om | DIGITAL | IOD_SS3_disk | D1463
SS3KlimaError1VisokaTempPovratneVode_Om | DIGITAL | IOD_SS3_disk | D1464
SS3KlimaError1GeneralAlarm_Om | DIGITAL | IOD_SS3_disk | D1465
SS3KlimaError1NapakaSenzorPovratVode_Om | DIGITAL | IOD_SS3_disk | D1466
SS3KlimaError2AlarmKompresor1_Om | DIGITAL | IOD_SS3_disk | D1467
SS3KlimaError2AlarmKompresor2_Om | DIGITAL | IOD_SS3_disk | D1468
SS3KlimaError2NizekPritiskKompresor1_Om | DIGITAL | IOD_SS3_disk | D1469
SS3KlimaError2NizekPritiskKompresor2_Om | DIGITAL | IOD_SS3_disk | D1470
SS3KlimaError2NapakaPriPretokuZraka_Om | DIGITAL | IOD_SS3_disk | D1471
SS3KlimaError2FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1472
SS3KlimaError2ThermalCutoutHeater1_Om | DIGITAL | IOD_SS3_disk | D1473
SS3KlimaError2ThermalCutoutHeater2_Om | DIGITAL | IOD_SS3_disk | D1474
SS3KlimaError2PozarniAlarm_Om | DIGITAL | IOD_SS3_disk | D1475
SS3KlimaError2ZamasenFilter_Om | DIGITAL | IOD_SS3_disk | D1476
SS3KlimaError2VisokaTempVProstoru_Om | DIGITAL | IOD_SS3_disk | D1477
SS3KlimaError2NizkaTempVProstoru_Om | DIGITAL | IOD_SS3_disk | D1478
SS3KlimaError2VisokaVlaznost_Om | DIGITAL | IOD_SS3_disk | D1479
SS3KlimaError2NizkaVlaznost_Om | DIGITAL | IOD_SS3_disk | D1480
SS3KlimaError2Kompresor1naMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1481
SS3KlimaError2Kompresor2naMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1482
SS3KlimaError2VentilatorNaMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1483
SS3KlimaError2NapakaTSTemperaturaProstora_Om | DIGITAL | IOD_SS3_disk | D1484
SS3KlimaError2NapakaSenzorVlaznosti_Om | DIGITAL | IOD_SS3_disk | D1485
SS3KlimaError2NapakaSenzorPritiska_Om | DIGITAL | IOD_SS3_disk | D1486
SS3KlimaError2VisokTokVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1487
SS3KlimaError2NiVodeVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1488
SS3KlimaError2NiTokaVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1489
SS3KlimaError2VisokPritiskVKrogu1_Om | DIGITAL | IOD_SS3_disk | D1490
SS3KlimaError2VisokPritiskVKrogu2_Om | DIGITAL | IOD_SS3_disk | D1491
SS3KlimaError2IzlivVode_Om | DIGITAL | IOD_SS3_disk | D1492
SS3KlimaError2TermZascInVisokPritiskKompr1_Om | DIGITAL | IOD_SS3_disk | D1493
SS3KlimaError2VlazilecnaMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1494
SS3KlimaError2TermZascInVisokPritiskKompr2_Om | DIGITAL | IOD_SS3_disk | D1495
SS3KlimaError2NapakaPriPretokuVode_Om | DIGITAL | IOD_SS3_disk | D1496
SS3KlimaError2Kond1FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1497
SS3KlimaError2Kond2FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1498
SS3KlimaError2ZunanjiAlarm_Om | DIGITAL | IOD_SS3_disk | D1499
SS3KlimaError2FaultyEprom_Om | DIGITAL | IOD_SS3_disk | D1500
SS3KlimaError2NapakaSenzorTempIzpiha_Om | DIGITAL | IOD_SS3_disk | D1501
SS3KlimaError2NapakaSenzorTempProstora_Om | DIGITAL | IOD_SS3_disk | D1502
SS3KlimaError2NapakaSenzorZunanjeTemp_Om | DIGITAL | IOD_SS3_disk | D1503
SS3KlimaError2NizkaTempPovratneVode_Om | DIGITAL | IOD_SS3_disk | D1504
SS3KlimaError2StoppedByAlarms_Om | DIGITAL | IOD_SS3_disk | D1505
SS3KlimaError2VisokaTempPovratneVode_Om | DIGITAL | IOD_SS3_disk | D1506
SS3KlimaError2GeneralAlarm_Om | DIGITAL | IOD_SS3_disk | D1507
SS3KlimaError2NapakaSenzorPovratVode_Om | DIGITAL | IOD_SS3_disk | D1508
SS3KlimaError3AlarmKompresor1_Om | DIGITAL | IOD_SS3_disk | D1509
SS3KlimaError3AlarmKompresor2_Om | DIGITAL | IOD_SS3_disk | D1510
SS3KlimaError3NizekPritiskKompresor1_Om | DIGITAL | IOD_SS3_disk | D1511
SS3KlimaError3NizekPritiskKompresor2_Om | DIGITAL | IOD_SS3_disk | D1512
SS3KlimaError3NapakaPriPretokuZraka_Om | DIGITAL | IOD_SS3_disk | D1513
SS3KlimaError3FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1514
SS3KlimaError3ThermalCutoutHeater1_Om | DIGITAL | IOD_SS3_disk | D1515
SS3KlimaError3ThermalCutoutHeater2_Om | DIGITAL | IOD_SS3_disk | D1516
SS3KlimaError3PozarniAlarm_Om | DIGITAL | IOD_SS3_disk | D1517
SS3KlimaError3ZamasenFilter_Om | DIGITAL | IOD_SS3_disk | D1518
SS3KlimaError3VisokaTempVProstoru_Om | DIGITAL | IOD_SS3_disk | D1519
SS3KlimaError3NizkaTempVProstoru_Om | DIGITAL | IOD_SS3_disk | D1520
SS3KlimaError3VisokaVlaznost_Om | DIGITAL | IOD_SS3_disk | D1521
SS3KlimaError3NizkaVlaznost_Om | DIGITAL | IOD_SS3_disk | D1522
SS3KlimaError3Kompresor1naMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1523
SS3KlimaError3Kompresor2naMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1524
SS3KlimaError3VentilatorNaMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1525
SS3KlimaError3NapakaTSTemperaturaProstora_Om | DIGITAL | IOD_SS3_disk | D1526
SS3KlimaError3NapakaSenzorVlaznosti_Om | DIGITAL | IOD_SS3_disk | D1527
SS3KlimaError3NapakaSenzorPritiska_Om | DIGITAL | IOD_SS3_disk | D1528
SS3KlimaError3VisokTokVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1529
SS3KlimaError3NiVodeVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1530
SS3KlimaError3NiTokaVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1531
SS3KlimaError3VisokPritiskVKrogu1_Om | DIGITAL | IOD_SS3_disk | D1532
SS3KlimaError3VisokPritiskVKrogu2_Om | DIGITAL | IOD_SS3_disk | D1533
SS3KlimaError3IzlivVode_Om | DIGITAL | IOD_SS3_disk | D1534
SS3KlimaError3TermZascInVisokPritiskKompr1_Om | DIGITAL | IOD_SS3_disk | D1535
SS3KlimaError3VlazilecnaMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1536
SS3KlimaError3TermZascInVisokPritiskKompr2_Om | DIGITAL | IOD_SS3_disk | D1537
SS3KlimaError3NapakaPriPretokuVode_Om | DIGITAL | IOD_SS3_disk | D1538
SS3KlimaError3Kond1FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1539
SS3KlimaError3Kond2FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1540
SS3KlimaError3ZunanjiAlarm_Om | DIGITAL | IOD_SS3_disk | D1541
SS3KlimaError3FaultyEprom_Om | DIGITAL | IOD_SS3_disk | D1542
SS3KlimaError3NapakaSenzorTempIzpiha_Om | DIGITAL | IOD_SS3_disk | D1543
SS3KlimaError3NapakaSenzorTempProstora_Om | DIGITAL | IOD_SS3_disk | D1544
SS3KlimaError3NapakaSenzorZunanjeTemp_Om | DIGITAL | IOD_SS3_disk | D1545
SS3KlimaError3NizkaTempPovratneVode_Om | DIGITAL | IOD_SS3_disk | D1546
SS3KlimaError3StoppedByAlarms_Om | DIGITAL | IOD_SS3_disk | D1547
SS3KlimaError3VisokaTempPovratneVode_Om | DIGITAL | IOD_SS3_disk | D1548
SS3KlimaError3GeneralAlarm_Om | DIGITAL | IOD_SS3_disk | D1549
SS3KlimaError3NapakaSenzorPovratVode_Om | DIGITAL | IOD_SS3_disk | D1550
SS3KlimaError4AlarmKompresor1_Om | DIGITAL | IOD_SS3_disk | D1551
SS3KlimaError4AlarmKompresor2_Om | DIGITAL | IOD_SS3_disk | D1552
SS3KlimaError4NizekPritiskKompresor1_Om | DIGITAL | IOD_SS3_disk | D1553
SS3KlimaError4NizekPritiskKompresor2_Om | DIGITAL | IOD_SS3_disk | D1554
SS3KlimaError4NapakaPriPretokuZraka_Om | DIGITAL | IOD_SS3_disk | D1555
SS3KlimaError4FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1556
SS3KlimaError4ThermalCutoutHeater1_Om | DIGITAL | IOD_SS3_disk | D1557
SS3KlimaError4ThermalCutoutHeater2_Om | DIGITAL | IOD_SS3_disk | D1558
SS3KlimaError4PozarniAlarm_Om | DIGITAL | IOD_SS3_disk | D1559
SS3KlimaError4ZamasenFilter_Om | DIGITAL | IOD_SS3_disk | D1560
SS3KlimaError4VisokaTempVProstoru_Om | DIGITAL | IOD_SS3_disk | D1561
SS3KlimaError4NizkaTempVProstoru_Om | DIGITAL | IOD_SS3_disk | D1562
SS3KlimaError4VisokaVlaznost_Om | DIGITAL | IOD_SS3_disk | D1563
SS3KlimaError4NizkaVlaznost_Om | DIGITAL | IOD_SS3_disk | D1564
SS3KlimaError4Kompresor1naMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1565
SS3KlimaError4Kompresor2naMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1566
SS3KlimaError4VentilatorNaMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1567
SS3KlimaError4NapakaTSTemperaturaProstora_Om | DIGITAL | IOD_SS3_disk | D1568
SS3KlimaError4NapakaSenzorVlaznosti_Om | DIGITAL | IOD_SS3_disk | D1569
SS3KlimaError4NapakaSenzorPritiska_Om | DIGITAL | IOD_SS3_disk | D1570
SS3KlimaError4VisokTokVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1571
SS3KlimaError4NiVodeVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1572
SS3KlimaError4NiTokaVVlazilcu_Om | DIGITAL | IOD_SS3_disk | D1573
SS3KlimaError4VisokPritiskVKrogu1_Om | DIGITAL | IOD_SS3_disk | D1574
SS3KlimaError4VisokPritiskVKrogu2_Om | DIGITAL | IOD_SS3_disk | D1575
SS3KlimaError4IzlivVode_Om | DIGITAL | IOD_SS3_disk | D1576
SS3KlimaError4TermZascInVisokPritiskKompr1_Om | DIGITAL | IOD_SS3_disk | D1577
SS3KlimaError4VlazilecnaMejiStevilaObrUr_Om | DIGITAL | IOD_SS3_disk | D1578
SS3KlimaError4TermZascInVisokPritiskKompr2_Om | DIGITAL | IOD_SS3_disk | D1579
SS3KlimaError4NapakaPriPretokuVode_Om | DIGITAL | IOD_SS3_disk | D1580
SS3KlimaError4Kond1FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1581
SS3KlimaError4Kond2FenThermalCutout_Om | DIGITAL | IOD_SS3_disk | D1582
SS3KlimaError4ZunanjiAlarm_Om | DIGITAL | IOD_SS3_disk | D1583
SS3KlimaError4FaultyEprom_Om | DIGITAL | IOD_SS3_disk | D1584
SS3KlimaError4NapakaSenzorTempIzpiha_Om | DIGITAL | IOD_SS3_disk | D1585
SS3KlimaError4NapakaSenzorTempProstora_Om | DIGITAL | IOD_SS3_disk | D1586
SS3KlimaError4NapakaSenzorZunanjeTemp_Om | DIGITAL | IOD_SS3_disk | D1587
SS3KlimaError4NizkaTempPovratneVode_Om | DIGITAL | IOD_SS3_disk | D1588
SS3KlimaError4StoppedByAlarms_Om | DIGITAL | IOD_SS3_disk | D1589
SS3KlimaError4VisokaTempPovratneVode_Om | DIGITAL | IOD_SS3_disk | D1590
SS3KlimaError4GeneralAlarm_Om | DIGITAL | IOD_SS3_disk | D1591
SS3KlimaError4NapakaSenzorPovratVode_Om | DIGITAL | IOD_SS3_disk | D1592
SS3AlarmTempTIA1Previsoka_Om | DIGITAL | IOD_SS3_disk | D1593
SS3AlarmTempTIA2Previsoka_Om | DIGITAL | IOD_SS3_disk | D1594
SS3AlarmTempTIA3Previsoka_Om | DIGITAL | IOD_SS3_disk | D1595
SS3UserloggedIn_mem | DIGITAL | IOD_SS3_disk | D1596
SS3OnemAlarmPon | DIGITAL | IOD_SS3_disk | D1597
SS3ComSCADA_stevec2 | INT | IOD_SS3_mem | I1600
SS3ComSCADA_stevec1 | INT | IOD_SS3_mem | I1602
SS3OmogociVseAlarme | DIGITAL | IOD_SS3_disk | D1598
SS3OmogociVseSMSAlarme | DIGITAL | IOD_SS3_disk | D1599
SS3AlarmSinhronizacijaNOK_Om | DIGITAL | IOD_SS3_disk | D1600
SS3AktualniSetPointTemp1_2 | REAL | IOD_SS3_TCP | 44001 | 0 | 60 | 0 | 60 | °C | ####.#
SS3AktualniSetPointTemp3_4 | REAL | IOD_SS3_TCP | 44003 | 0 | 60 | 0 | 60 | °C | ####.#
SS3AlarmKlimat1_Napaka | DIGITAL | IOD_SS3_TCP | 00001
SS3AlarmKlimat2_Napaka | DIGITAL | IOD_SS3_TCP | 00002
SS3AlarmKlimat3_Napaka | DIGITAL | IOD_SS3_TCP | 00003
SS3AlarmKlimat4_Napaka | DIGITAL | IOD_SS3_TCP | 00004
SS3AlarmLAH1_RazlitjeVode | DIGITAL | IOD_SS3_TCP | 00005
SS3AlarmLAH2_RazlitjeVode | DIGITAL | IOD_SS3_TCP | 00006
SS3AlarmSinhronizacijaNOK | DIGITAL | IOD_SS3_TCP | 00007
SS3AlarmTempTIA1Previsoka | DIGITAL | IOD_SS3_TCP | 00008
SS3AlarmTempTIA2Previsoka | DIGITAL | IOD_SS3_TCP | 00009
SS3AlarmTempTIA3Previsoka | DIGITAL | IOD_SS3_TCP | 00010
SS3AlarmTSTemp1Previsoka | DIGITAL | IOD_SS3_TCP | 00011
SS3AlarmTSTemp3Previsoka | DIGITAL | IOD_SS3_TCP | 00012
SS3AlarmUPSKrmOmara_Alarm | DIGITAL | IOD_SS3_TCP | 00013
SS3ComSCADA | DIGITAL | IOD_SS3_TCP | 00014
SS3ComSCADA1 | DIGITAL | IOD_SS3_TCP | 00015
SS3DatumCasDan | INT | IOD_SS3_TCP | 40001
SS3DatumCasLeto | INT | IOD_SS3_TCP | 40002
SS3DatumCasLeto2 | INT | IOD_SS3_TCP | 40003
SS3DatumCasMesec | INT | IOD_SS3_TCP | 40004
SS3DatumCasMinuta | INT | IOD_SS3_TCP | 40005
SS3DatumCasSekunda | INT | IOD_SS3_TCP | 40006
SS3DatumCasUra | INT | IOD_SS3_TCP | 40007
SS3ErrComKlima1 | DIGITAL | IOD_SS3_TCP | 00016
SS3ErrComKlima2 | DIGITAL | IOD_SS3_TCP | 00017
SS3ErrComKlima3 | DIGITAL | IOD_SS3_TCP | 00018
SS3ErrComKlima4 | DIGITAL | IOD_SS3_TCP | 00019
SS3ErrCommScada | DIGITAL | IOD_SS3_TCP | 00020
SS3ErrComPanelPLC | DIGITAL | IOD_SS3_TCP | 00021
SS3ErrComPort2 | DIGITAL | IOD_SS3_TCP | 00022
SS3ErrorComKlima4Error | DIGITAL | IOD_SS3_TCP | 00023
SS3ErrorComKlima4Status | INT | IOD_SS3_TCP | 40008
SS3Klima1_Onemogocena | DIGITAL | IOD_SS3_TCP | 00024
SS3Klima1ure | REAL | IOD_SS3_TCP | 44005
SS3Klima2_Onemogocena | DIGITAL | IOD_SS3_TCP | 00025
SS3Klima2ure | REAL | IOD_SS3_TCP | 44007
SS3Klima3_Onemogocena | DIGITAL | IOD_SS3_TCP | 00026
SS3Klima3ure | REAL | IOD_SS3_TCP | 44009
SS3Klima4_Onemogocena | DIGITAL | IOD_SS3_TCP | 00027
SS3Klima4ure | REAL | IOD_SS3_TCP | 44011
SS3Klima1Deluje | DIGITAL | IOD_SS3_TCP | 00028
SS3Klima1EnergySaving | DIGITAL | IOD_SS3_TCP | 00029
SS3Klima1GrelecStatus | INT | IOD_SS3_TCP | 40009
SS3Klima1IzhodniVentStatus | INT | IOD_SS3_TCP | 40010
SS3Klima1KompresorStatus | INT | IOD_SS3_TCP | 40011
SS3Klima1Napaka | DIGITAL | IOD_SS3_TCP | 00030
SS3Klima1NastTempProstora | REAL | IOD_SS3_TCP | 44013 | 0 | 60 | 0 | 60 | °C | ####.#
SS3Klima1NastVlaznost | REAL | IOD_SS3_TCP | 44015 | 0 | 100 | 0 | 100 | % | ####.#
SS3Klima1ObratovalneUre | REAL | IOD_SS3_TCP | 44017
SS3Klima1OnOffEnablingBySupervisor | DIGITAL | IOD_SS3_TCP | 00031
SS3Klima1Razvlazevanje | DIGITAL | IOD_SS3_TCP | 00032
SS3Klima1RemoteOFFtoOutput | DIGITAL | IOD_SS3_TCP | 00033
SS3Klima1RemoteOnOff | DIGITAL | IOD_SS3_TCP | 00034
SS3Klima1RocniIzklop | DIGITAL | IOD_SS3_TCP | 00035
SS3Klima1SenzorjiStatus | DIGITAL | IOD_SS3_TCP | 00036
SS3Klima1TemperaturaProstora | REAL | IOD_SS3_TCP | 44019 | 0 | 60 | 0 | 60 | °C | ####.#
SS3Klima1UnitOnOff | DIGITAL | IOD_SS3_TCP | 00037
SS3Klima1VentilGretjeOdpiranje | DIGITAL | IOD_SS3_TCP | 00038
SS3Klima1VentilGretjeZapiranje | DIGITAL | IOD_SS3_TCP | 00039
SS3Klima1VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3_TCP | 00040
SS3Klima1VentilHlajenjeZapiranje | DIGITAL | IOD_SS3_TCP | 00041
SS3Klima1Vlazenje | DIGITAL | IOD_SS3_TCP | 00042
SS3Klima1VlazilecStatus | INT | IOD_SS3_TCP | 40012
SS3Klima1VlaznostProstora | REAL | IOD_SS3_TCP | 44021 | 0 | 100 | 0 | 100 | % | ####.#
SS3Klima2Deluje | DIGITAL | IOD_SS3_TCP | 00043
SS3Klima2EnergySaving | DIGITAL | IOD_SS3_TCP | 00044
SS3Klima2GrelecStatus | INT | IOD_SS3_TCP | 40013
SS3Klima2IzhodniVentStatus | INT | IOD_SS3_TCP | 40014
SS3Klima2KompresorStatus | INT | IOD_SS3_TCP | 40015
SS3Klima2Napaka | DIGITAL | IOD_SS3_TCP | 00045
SS3Klima2NastTempProstora | REAL | IOD_SS3_TCP | 44023 | 0 | 60 | 0 | 60 | °C | ####.#
SS3Klima2NastVlaznost | REAL | IOD_SS3_TCP | 44025 | 0 | 100 | 0 | 100 | % | ####.#
SS3Klima2ObratovalneUre | REAL | IOD_SS3_TCP | 44027
SS3Klima2OnOffEnablingBySupervisor | DIGITAL | IOD_SS3_TCP | 00046
SS3Klima2Razvlazevanje | DIGITAL | IOD_SS3_TCP | 00047
SS3Klima2RemoteOFFtoOutput | DIGITAL | IOD_SS3_TCP | 00048
SS3Klima2RemoteOnOff | DIGITAL | IOD_SS3_TCP | 00049
SS3Klima2RocniIzklop | DIGITAL | IOD_SS3_TCP | 00050
SS3Klima2SenzorjiStatus | DIGITAL | IOD_SS3_TCP | 00051
SS3Klima2TemperaturaProstora | REAL | IOD_SS3_TCP | 44029 | 0 | 60 | 0 | 60 | °C | ####.#
SS3Klima2UnitOnOff | DIGITAL | IOD_SS3_TCP | 00052
SS3Klima2VentilGretjeOdpiranje | DIGITAL | IOD_SS3_TCP | 00053
SS3Klima2VentilGretjeZapiranje | DIGITAL | IOD_SS3_TCP | 00054
SS3Klima2VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3_TCP | 00055
SS3Klima2VentilHlajenjeZapiranje | DIGITAL | IOD_SS3_TCP | 00056
SS3Klima2Vlazenje | DIGITAL | IOD_SS3_TCP | 00057
SS3Klima2VlazilecStatus | INT | IOD_SS3_TCP | 40016
SS3Klima2VlaznostProstora | REAL | IOD_SS3_TCP | 44031 | 0 | 100 | 0 | 100 | % | ####.#
SS3Klima3Deluje | DIGITAL | IOD_SS3_TCP | 00058
SS3Klima3EnergySaving | DIGITAL | IOD_SS3_TCP | 00059
SS3Klima3GrelecStatus | INT | IOD_SS3_TCP | 40017
SS3Klima3IzhodniVentStatus | INT | IOD_SS3_TCP | 40018
SS3Klima3KompresorStatus | INT | IOD_SS3_TCP | 40019
SS3Klima3Napaka | DIGITAL | IOD_SS3_TCP | 00060
SS3Klima3NastTempProstora | REAL | IOD_SS3_TCP | 44033 | 0 | 60 | 0 | 60 | °C | ####.#
SS3Klima3NastVlaznost | REAL | IOD_SS3_TCP | 44035 | 0 | 100 | 0 | 100 | % | ####.#
SS3Klima3ObratovalneUre | REAL | IOD_SS3_TCP | 44037
SS3Klima3OnOffEnablingBySupervisor | DIGITAL | IOD_SS3_TCP | 00061
SS3Klima3Razvlazevanje | DIGITAL | IOD_SS3_TCP | 00062
SS3Klima3RemoteOFFtoOutput | DIGITAL | IOD_SS3_TCP | 00063
SS3Klima3RemoteOnOff | DIGITAL | IOD_SS3_TCP | 00064
SS3Klima3RocniIzklop | DIGITAL | IOD_SS3_TCP | 00065
SS3Klima3SenzorjiStatus | DIGITAL | IOD_SS3_TCP | 00066
SS3Klima3TemperaturaProstora | REAL | IOD_SS3_TCP | 44039 | 0 | 60 | 0 | 60 | °C | ####.#
SS3Klima3UnitOnOff | DIGITAL | IOD_SS3_TCP | 00067
SS3Klima3VentilGretjeOdpiranje | DIGITAL | IOD_SS3_TCP | 00068
SS3Klima3VentilGretjeZapiranje | DIGITAL | IOD_SS3_TCP | 00069
SS3Klima3VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3_TCP | 00070
SS3Klima3VentilHlajenjeZapiranje | DIGITAL | IOD_SS3_TCP | 00071
SS3Klima3Vlazenje | DIGITAL | IOD_SS3_TCP | 00072
SS3Klima3VlazilecStatus | INT | IOD_SS3_TCP | 40020
SS3Klima3VlaznostProstora | REAL | IOD_SS3_TCP | 44041 | 0 | 100 | 0 | 100 | % | ####.#
SS3Klima4Deluje | DIGITAL | IOD_SS3_TCP | 00073
SS3Klima4EnergySaving | DIGITAL | IOD_SS3_TCP | 00074
SS3Klima4GrelecStatus | INT | IOD_SS3_TCP | 40021
SS3Klima4IzhodniVentStatus | INT | IOD_SS3_TCP | 40022
SS3Klima4KompresorStatus | INT | IOD_SS3_TCP | 40023
SS3Klima4Napaka | DIGITAL | IOD_SS3_TCP | 00075
SS3Klima4NastTempProstora | REAL | IOD_SS3_TCP | 44043 | 0 | 60 | 0 | 60 | °C | ####.#
SS3Klima4NastVlaznost | REAL | IOD_SS3_TCP | 44045 | 0 | 100 | 0 | 100 | % | ####.#
SS3Klima4ObratovalneUre | REAL | IOD_SS3_TCP | 44047
SS3Klima4OnOffEnablingBySupervisor | DIGITAL | IOD_SS3_TCP | 00076
SS3Klima4Razvlazevanje | DIGITAL | IOD_SS3_TCP | 00077
SS3Klima4RemoteOFFtoOutput | DIGITAL | IOD_SS3_TCP | 00078
SS3Klima4RemoteOnOff | DIGITAL | IOD_SS3_TCP | 00079
SS3Klima4RocniIzklop | DIGITAL | IOD_SS3_TCP | 00080
SS3Klima4SenzorjiStatus | DIGITAL | IOD_SS3_TCP | 00081
SS3Klima4TemperaturaProstora | REAL | IOD_SS3_TCP | 44049 | 0 | 60 | 0 | 60 | °C | ####.#
SS3Klima4UnitOnOff | DIGITAL | IOD_SS3_TCP | 00082
SS3Klima4VentilGretjeOdpiranje | DIGITAL | IOD_SS3_TCP | 00083
SS3Klima4VentilGretjeZapiranje | DIGITAL | IOD_SS3_TCP | 00084
SS3Klima4VentilHlajenjeOdpiranje | DIGITAL | IOD_SS3_TCP | 00085
SS3Klima4VentilHlajenjeZapiranje | DIGITAL | IOD_SS3_TCP | 00086
SS3Klima4Vlazenje | DIGITAL | IOD_SS3_TCP | 00087
SS3Klima4VlazilecStatus | INT | IOD_SS3_TCP | 40024
SS3Klima4VlaznostProstora | REAL | IOD_SS3_TCP | 44051 | 0 | 100 | 0 | 100 | % | ####.#
SS3KlimaError1AlarmKompresor1 | DIGITAL | IOD_SS3_TCP | 00088
SS3KlimaError1AlarmKompresor2 | DIGITAL | IOD_SS3_TCP | 00089
SS3KlimaError1FaultyEprom | DIGITAL | IOD_SS3_TCP | 00090
SS3KlimaError1FenThermalCutout | DIGITAL | IOD_SS3_TCP | 00091
SS3KlimaError1GeneralAlarm | DIGITAL | IOD_SS3_TCP | 00092
SS3KlimaError1Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 00093
SS3KlimaError1Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 00094
SS3KlimaError1Kond1FenThermalCutout | DIGITAL | IOD_SS3_TCP | 00095
SS3KlimaError1Kond2FenThermalCutout | DIGITAL | IOD_SS3_TCP | 00096
SS3KlimaError1NapakaPriPretokuVode | DIGITAL | IOD_SS3_TCP | 00097
SS3KlimaError1NapakaPriPretokuZraka | DIGITAL | IOD_SS3_TCP | 00098
SS3KlimaError1NapakaSenzorPovratVode | DIGITAL | IOD_SS3_TCP | 00099
SS3KlimaError1NapakaSenzorPritiska | DIGITAL | IOD_SS3_TCP | 00100
SS3KlimaError1NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3_TCP | 00101
SS3KlimaError1NapakaSenzorTempProstora | DIGITAL | IOD_SS3_TCP | 00102
SS3KlimaError1NapakaSenzorVlaznosti | DIGITAL | IOD_SS3_TCP | 00103
SS3KlimaError1NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3_TCP | 00104
SS3KlimaError1NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3_TCP | 00105
SS3KlimaError1NiTokaVVlazilcu | DIGITAL | IOD_SS3_TCP | 00106
SS3KlimaError1NiVodeVVlazilcu | DIGITAL | IOD_SS3_TCP | 00107
SS3KlimaError1NizekPritiskKompresor1 | DIGITAL | IOD_SS3_TCP | 00108
SS3KlimaError1NizekPritiskKompresor2 | DIGITAL | IOD_SS3_TCP | 00109
SS3KlimaError1NizkaTempPovratneVode | DIGITAL | IOD_SS3_TCP | 00110
SS3KlimaError1NizkaTempVProstoru | DIGITAL | IOD_SS3_TCP | 00111
SS3KlimaError1NizkaVlaznost | DIGITAL | IOD_SS3_TCP | 00112
SS3KlimaError1PozarniAlarm | DIGITAL | IOD_SS3_TCP | 00113
SS3KlimaError1StoppedByAlarms | DIGITAL | IOD_SS3_TCP | 00114
SS3KlimaError1TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3_TCP | 00115
SS3KlimaError1TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3_TCP | 00116
SS3KlimaError1ThermalCutoutHeater1 | DIGITAL | IOD_SS3_TCP | 00117
SS3KlimaError1ThermalCutoutHeater2 | DIGITAL | IOD_SS3_TCP | 00118
SS3KlimaError1VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 00119
SS3KlimaError1VisokaTempPovratneVode | DIGITAL | IOD_SS3_TCP | 00120
SS3KlimaError1VisokaTempVProstoru | DIGITAL | IOD_SS3_TCP | 00121
SS3KlimaError1VisokaVlaznost | DIGITAL | IOD_SS3_TCP | 00122
SS3KlimaError1VisokPritiskVKrogu1 | DIGITAL | IOD_SS3_TCP | 00123
SS3KlimaError1VisokPritiskVKrogu2 | DIGITAL | IOD_SS3_TCP | 00124
SS3KlimaError1VisokTokVVlazilcu | DIGITAL | IOD_SS3_TCP | 00125
SS3KlimaError1VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 00126
SS3KlimaError1ZamasenFilter | DIGITAL | IOD_SS3_TCP | 00127
SS3KlimaError2AlarmKompresor1 | DIGITAL | IOD_SS3_TCP | 00128
SS3KlimaError2AlarmKompresor2 | DIGITAL | IOD_SS3_TCP | 00129
SS3KlimaError2FaultyEprom | DIGITAL | IOD_SS3_TCP | 00130
SS3KlimaError2FenThermalCutout | DIGITAL | IOD_SS3_TCP | 00131
SS3KlimaError2GeneralAlarm | DIGITAL | IOD_SS3_TCP | 00132
SS3KlimaError2Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 00133
SS3KlimaError2Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 00134
SS3KlimaError2Kond1FenThermalCutout | DIGITAL | IOD_SS3_TCP | 00135
SS3KlimaError2Kond2FenThermalCutout | DIGITAL | IOD_SS3_TCP | 00136
SS3KlimaError2NapakaPriPretokuVode | DIGITAL | IOD_SS3_TCP | 00137
SS3KlimaError2NapakaPriPretokuZraka | DIGITAL | IOD_SS3_TCP | 00138
SS3KlimaError2NapakaSenzorPovratVode | DIGITAL | IOD_SS3_TCP | 00139
SS3KlimaError2NapakaSenzorPritiska | DIGITAL | IOD_SS3_TCP | 00140
SS3KlimaError2NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3_TCP | 00141
SS3KlimaError2NapakaSenzorTempProstora | DIGITAL | IOD_SS3_TCP | 00142
SS3KlimaError2NapakaSenzorVlaznosti | DIGITAL | IOD_SS3_TCP | 00143
SS3KlimaError2NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3_TCP | 00144
SS3KlimaError2NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3_TCP | 00145
SS3KlimaError2NiTokaVVlazilcu | DIGITAL | IOD_SS3_TCP | 00146
SS3KlimaError2NiVodeVVlazilcu | DIGITAL | IOD_SS3_TCP | 00147
SS3KlimaError2NizekPritiskKompresor1 | DIGITAL | IOD_SS3_TCP | 00148
SS3KlimaError2NizekPritiskKompresor2 | DIGITAL | IOD_SS3_TCP | 00149
SS3KlimaError2NizkaTempPovratneVode | DIGITAL | IOD_SS3_TCP | 00150
SS3KlimaError2NizkaTempVProstoru | DIGITAL | IOD_SS3_TCP | 00151
SS3KlimaError2NizkaVlaznost | DIGITAL | IOD_SS3_TCP | 00152
SS3KlimaError2PozarniAlarm | DIGITAL | IOD_SS3_TCP | 00153
SS3KlimaError2StoppedByAlarms | DIGITAL | IOD_SS3_TCP | 00154
SS3KlimaError2TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3_TCP | 00155
SS3KlimaError2TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3_TCP | 00156
SS3KlimaError2ThermalCutoutHeater1 | DIGITAL | IOD_SS3_TCP | 00157
SS3KlimaError2ThermalCutoutHeater2 | DIGITAL | IOD_SS3_TCP | 00158
SS3KlimaError2VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 00159
SS3KlimaError2VisokaTempPovratneVode | DIGITAL | IOD_SS3_TCP | 00160
SS3KlimaError2VisokaTempVProstoru | DIGITAL | IOD_SS3_TCP | 00161
SS3KlimaError2VisokaVlaznost | DIGITAL | IOD_SS3_TCP | 00162
SS3KlimaError2VisokPritiskVKrogu1 | DIGITAL | IOD_SS3_TCP | 00163
SS3KlimaError2VisokPritiskVKrogu2 | DIGITAL | IOD_SS3_TCP | 00164
SS3KlimaError2VisokTokVVlazilcu | DIGITAL | IOD_SS3_TCP | 00165
SS3KlimaError2VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 00166
SS3KlimaError2ZamasenFilter | DIGITAL | IOD_SS3_TCP | 00167
SS3KlimaError3AlarmKompresor1 | DIGITAL | IOD_SS3_TCP | 00168
SS3KlimaError3AlarmKompresor2 | DIGITAL | IOD_SS3_TCP | 00169
SS3KlimaError3FaultyEprom | DIGITAL | IOD_SS3_TCP | 00170
SS3KlimaError3FenThermalCutout | DIGITAL | IOD_SS3_TCP | 00171
SS3KlimaError3GeneralAlarm | DIGITAL | IOD_SS3_TCP | 00172
SS3KlimaError3Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 00173
SS3KlimaError3Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 00174
SS3KlimaError3Kond1FenThermalCutout | DIGITAL | IOD_SS3_TCP | 00175
SS3KlimaError3Kond2FenThermalCutout | DIGITAL | IOD_SS3_TCP | 00176
SS3KlimaError3NapakaPriPretokuVode | DIGITAL | IOD_SS3_TCP | 00177
SS3KlimaError3NapakaPriPretokuZraka | DIGITAL | IOD_SS3_TCP | 00178
SS3KlimaError3NapakaSenzorPovratVode | DIGITAL | IOD_SS3_TCP | 00179
SS3KlimaError3NapakaSenzorPritiska | DIGITAL | IOD_SS3_TCP | 00180
SS3KlimaError3NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3_TCP | 00181
SS3KlimaError3NapakaSenzorTempProstora | DIGITAL | IOD_SS3_TCP | 00182
SS3KlimaError3NapakaSenzorVlaznosti | DIGITAL | IOD_SS3_TCP | 00183
SS3KlimaError3NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3_TCP | 00184
SS3KlimaError3NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3_TCP | 00185
SS3KlimaError3NiTokaVVlazilcu | DIGITAL | IOD_SS3_TCP | 00186
SS3KlimaError3NiVodeVVlazilcu | DIGITAL | IOD_SS3_TCP | 00187
SS3KlimaError3NizekPritiskKompresor1 | DIGITAL | IOD_SS3_TCP | 00188
SS3KlimaError3NizekPritiskKompresor2 | DIGITAL | IOD_SS3_TCP | 00189
SS3KlimaError3NizkaTempPovratneVode | DIGITAL | IOD_SS3_TCP | 00190
SS3KlimaError3NizkaTempVProstoru | DIGITAL | IOD_SS3_TCP | 00191
SS3KlimaError3NizkaVlaznost | DIGITAL | IOD_SS3_TCP | 00192
SS3KlimaError3PozarniAlarm | DIGITAL | IOD_SS3_TCP | 00193
SS3KlimaError3StoppedByAlarms | DIGITAL | IOD_SS3_TCP | 00194
SS3KlimaError3TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3_TCP | 00195
SS3KlimaError3TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3_TCP | 00196
SS3KlimaError3ThermalCutoutHeater1 | DIGITAL | IOD_SS3_TCP | 00197
SS3KlimaError3ThermalCutoutHeater2 | DIGITAL | IOD_SS3_TCP | 00198
SS3KlimaError3VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 00199
SS3KlimaError3VisokaTempPovratneVode | DIGITAL | IOD_SS3_TCP | 00200
SS3KlimaError3VisokaTempVProstoru | DIGITAL | IOD_SS3_TCP | 00201
SS3KlimaError3VisokaVlaznost | DIGITAL | IOD_SS3_TCP | 00202
SS3KlimaError3VisokPritiskVKrogu1 | DIGITAL | IOD_SS3_TCP | 00203
SS3KlimaError3VisokPritiskVKrogu2 | DIGITAL | IOD_SS3_TCP | 00204
SS3KlimaError3VisokTokVVlazilcu | DIGITAL | IOD_SS3_TCP | 00205
SS3KlimaError3VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 00206
SS3KlimaError3ZamasenFilter | DIGITAL | IOD_SS3_TCP | 00207
SS3KlimaError4AlarmKompresor1 | DIGITAL | IOD_SS3_TCP | 00208
SS3KlimaError4AlarmKompresor2 | DIGITAL | IOD_SS3_TCP | 00209
SS3KlimaError4FaultyEprom | DIGITAL | IOD_SS3_TCP | 00210
SS3KlimaError4FenThermalCutout | DIGITAL | IOD_SS3_TCP | 00211
SS3KlimaError4GeneralAlarm | DIGITAL | IOD_SS3_TCP | 00212
SS3KlimaError4Kompresor1naMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 00213
SS3KlimaError4Kompresor2naMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 00214
SS3KlimaError4Kond1FenThermalCutout | DIGITAL | IOD_SS3_TCP | 00215
SS3KlimaError4Kond2FenThermalCutout | DIGITAL | IOD_SS3_TCP | 00216
SS3KlimaError4NapakaPriPretokuVode | DIGITAL | IOD_SS3_TCP | 00217
SS3KlimaError4NapakaPriPretokuZraka | DIGITAL | IOD_SS3_TCP | 00218
SS3KlimaError4NapakaSenzorPovratVode | DIGITAL | IOD_SS3_TCP | 00219
SS3KlimaError4NapakaSenzorPritiska | DIGITAL | IOD_SS3_TCP | 00220
SS3KlimaError4NapakaSenzorTempIzpiha | DIGITAL | IOD_SS3_TCP | 00221
SS3KlimaError4NapakaSenzorTempProstora | DIGITAL | IOD_SS3_TCP | 00222
SS3KlimaError4NapakaSenzorVlaznosti | DIGITAL | IOD_SS3_TCP | 00223
SS3KlimaError4NapakaSenzorZunanjeTemp | DIGITAL | IOD_SS3_TCP | 00224
SS3KlimaError4NapakaTSTemperaturaProstora | DIGITAL | IOD_SS3_TCP | 00225
SS3KlimaError4NiTokaVVlazilcu | DIGITAL | IOD_SS3_TCP | 00226
SS3KlimaError4NiVodeVVlazilcu | DIGITAL | IOD_SS3_TCP | 00227
SS3KlimaError4NizekPritiskKompresor1 | DIGITAL | IOD_SS3_TCP | 00228
SS3KlimaError4NizekPritiskKompresor2 | DIGITAL | IOD_SS3_TCP | 00229
SS3KlimaError4NizkaTempPovratneVode | DIGITAL | IOD_SS3_TCP | 00230
SS3KlimaError4NizkaTempVProstoru | DIGITAL | IOD_SS3_TCP | 00231
SS3KlimaError4NizkaVlaznost | DIGITAL | IOD_SS3_TCP | 00232
SS3KlimaError4PozarniAlarm | DIGITAL | IOD_SS3_TCP | 00233
SS3KlimaError4StoppedByAlarms | DIGITAL | IOD_SS3_TCP | 00234
SS3KlimaError4TermZascInVisokPritiskKompr1 | DIGITAL | IOD_SS3_TCP | 00235
SS3KlimaError4TermZascInVisokPritiskKompr2 | DIGITAL | IOD_SS3_TCP | 00236
SS3KlimaError4ThermalCutoutHeater1 | DIGITAL | IOD_SS3_TCP | 00237
SS3KlimaError4ThermalCutoutHeater2 | DIGITAL | IOD_SS3_TCP | 00238
SS3KlimaError4VentilatorNaMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 00239
SS3KlimaError4VisokaTempPovratneVode | DIGITAL | IOD_SS3_TCP | 00240
SS3KlimaError4VisokaTempVProstoru | DIGITAL | IOD_SS3_TCP | 00241
SS3KlimaError4VisokaVlaznost | DIGITAL | IOD_SS3_TCP | 00242
SS3KlimaError4VisokPritiskVKrogu1 | DIGITAL | IOD_SS3_TCP | 00243
SS3KlimaError4VisokPritiskVKrogu2 | DIGITAL | IOD_SS3_TCP | 00244
SS3KlimaError4VisokTokVVlazilcu | DIGITAL | IOD_SS3_TCP | 00245
SS3KlimaError4VlazilecnaMejiStevilaObrUr | DIGITAL | IOD_SS3_TCP | 00246
SS3KlimaError4ZamasenFilter | DIGITAL | IOD_SS3_TCP | 00247
SS3NacDelovanjaKlime1_2_Avtomatsko | DIGITAL | IOD_SS3_TCP | 00248
SS3NacDelovanjaKlime3_4_Avtomatsko | DIGITAL | IOD_SS3_TCP | 00249
SS3NapakaSenzorTemp1 | DIGITAL | IOD_SS3_TCP | 00250
SS3NapakaSenzorTemp2 | DIGITAL | IOD_SS3_TCP | 00251
SS3NapakaSenzorTemp3 | DIGITAL | IOD_SS3_TCP | 00252
SS3NapakaSenzorVlaga1 | DIGITAL | IOD_SS3_TCP | 00253
SS3NapakaSenzorVlaga2 | DIGITAL | IOD_SS3_TCP | 00254
SS3NapakaSenzorVlaga3 | DIGITAL | IOD_SS3_TCP | 00255
SS3NastaviCasNaKrmilniku | DIGITAL | IOD_SS3_TCP | 00256
SS3NastavitevUreKrUspesna | DIGITAL | IOD_SS3_TCP | 00257
SS3OpozoriloBaterijaPLC | DIGITAL | IOD_SS3_TCP | 00258
SS3OsveziAlarmePanel | DIGITAL | IOD_SS3_TCP | 00259
SS3RocniVklopKlima1 | DIGITAL | IOD_SS3_TCP | 00260
SS3RocniVklopKlima2 | DIGITAL | IOD_SS3_TCP | 00261
SS3RocniVklopKlima3 | DIGITAL | IOD_SS3_TCP | 00262
SS3RocniVklopKlima4 | DIGITAL | IOD_SS3_TCP | 00263
SS3SinhronizacijaPanelOK | DIGITAL | IOD_SS3_TCP | 00264
SS3SinhronizirajCas_Panel | DIGITAL | IOD_SS3_TCP | 00265
SS3SKTemp1 | REAL | IOD_SS3_TCP | 44053 | 0 | 60 | 0 | 60 | °C | ####.#
SS3SKTemp2 | REAL | IOD_SS3_TCP | 44055 | 0 | 60 | 0 | 60 | °C | ####.#
SS3SKTemp3 | REAL | IOD_SS3_TCP | 44057 | 0 | 60 | 0 | 60 | °C | ####.#
SS3SkupneNapakeNaprav_Klima1 | DIGITAL | IOD_SS3_TCP | 00266
SS3SkupneNapakeNaprav_Klima2 | DIGITAL | IOD_SS3_TCP | 00267
SS3SkupneNapakeNaprav_Klima3 | DIGITAL | IOD_SS3_TCP | 00268
SS3SkupneNapakeNaprav_Klima4 | DIGITAL | IOD_SS3_TCP | 00269
SS3SkupneNapakeNaprav_Komunikacija | DIGITAL | IOD_SS3_TCP | 00270
SS3SkupneNapakeNaprav_TempVlaga | DIGITAL | IOD_SS3_TCP | 00271
SS3SKVlaga1 | REAL | IOD_SS3_TCP | 44059 | 0 | 100 | 0 | 100 | % | ####.#
SS3SKVlaga2 | REAL | IOD_SS3_TCP | 44061 | 0 | 100 | 0 | 100 | % | ####.#
SS3SKVlaga3 | REAL | IOD_SS3_TCP | 44063 | 0 | 100 | 0 | 100 | % | ####.#
SS3StanjeKlimat1_Delovanje | DIGITAL | IOD_SS3_TCP | 00272
SS3StanjeKlimat2_Delovanje | DIGITAL | IOD_SS3_TCP | 00273
SS3StanjeKlimat3_Delovanje | DIGITAL | IOD_SS3_TCP | 00274
SS3StanjeKlimat4_Delovanje | DIGITAL | IOD_SS3_TCP | 00275
SS3StanjeUPSKrmOmara_BaterijskiNacin | DIGITAL | IOD_SS3_TCP | 00276
SS3StanjeUPSKrmOmara_Polnjenje | DIGITAL | IOD_SS3_TCP | 00277
SS3StUrZaPreklopKlim1_2 | INT | IOD_SS3_TCP | 40025
SS3StUrZaPreklopKlim3_4 | INT | IOD_SS3_TCP | 40026
SS3TempZaAlarm1_2 | REAL | IOD_SS3_TCP | 44065 | 0 | 60 | 0 | 60 | °C | ####.#
SS3TempZaAlarm3_4 | REAL | IOD_SS3_TCP | 44067 | 0 | 60 | 0 | 60 | °C | ####.#
SS3TempZaAlarmTIA1 | REAL | IOD_SS3_TCP | 44069 | 0 | 60 | 0 | 60 | °C | ####.#
SS3TempZaAlarmTIA2 | REAL | IOD_SS3_TCP | 44071 | 0 | 60 | 0 | 60 | °C | ####.#
SS3TempZaAlarmTIA3 | REAL | IOD_SS3_TCP | 44073 | 0 | 60 | 0 | 60 | °C | ####.#
SS3TempZaVklopObehKlim1_2 | REAL | IOD_SS3_TCP | 44075 | 0 | 60 | 0 | 60 | °C | ####.#
SS3TempZaVklopObehKlim3_4 | REAL | IOD_SS3_TCP | 44077 | 0 | 60 | 0 | 60 | °C | ####.#
SS3UPSstatus_Prikaz_PanelSCADA | INT | IOD_SS3_TCP | 40027
SS3UserCurrentLevel | INT | IOD_SS3_TCP | 40028
SS3UserLoggedIn | DIGITAL | IOD_SS3_TCP | 00278
SS3UserName | STRING | IOD_SS3_TCP | 45001[15]
SS3XVH_AlarmOn | DIGITAL | IOD_SS3_TCP | 00279
SS3PricetekSMSAlarmov1 | INT | IOD_SS3_disk | I1
SS3KonecSMSAlarmov1 | INT | IOD_SS3_disk | I2
SS3Klimat1_Vklop | DIGITAL | IOD_SS3_TCP | 00280
SS3Klimat2_Vklop | DIGITAL | IOD_SS3_TCP | 00281
SS3Klimat3_Vklop | DIGITAL | IOD_SS3_TCP | 00282
SS3Klimat4_Vklop | DIGITAL | IOD_SS3_TCP | 00283
SS3OmogociVseDogodke_DO | DIGITAL | IOD_SS3_disk | D2
SS3OmogociVseDogodke_DI | DIGITAL | IOD_SS3_disk | D3
SS3OmogociVseDogodke_COM | DIGITAL | IOD_SS3_disk | D4
SS3Date_Time0 | STRING | IOD_SS3_TCP | 45016[15]
SS3Date_Time1 | STRING | IOD_SS3_TCP | 45031[15]
SS3Date_Time2 | STRING | IOD_SS3_TCP | 45046[15]
SS3Date_Time3 | STRING | IOD_SS3_TCP | 45061[15]
SS3ErrorComKlima1Code0 | INT | IOD_SS3_TCP | 40029
SS3ErrorComKlima1Code10 | INT | IOD_SS3_TCP | 40030
SS3ErrorComKlima1Code11 | INT | IOD_SS3_TCP | 40031
SS3ErrorComKlima1Code12 | INT | IOD_SS3_TCP | 40032
SS3ErrorComKlima1Code13 | INT | IOD_SS3_TCP | 40033
SS3ErrorComKlima1Code14 | INT | IOD_SS3_TCP | 40034
SS3ErrorComKlima1Code15 | INT | IOD_SS3_TCP | 40035
SS3ErrorComKlima1Code1 | INT | IOD_SS3_TCP | 40036
SS3ErrorComKlima1Code2 | INT | IOD_SS3_TCP | 40037
SS3ErrorComKlima1Code3 | INT | IOD_SS3_TCP | 40038
SS3ErrorComKlima1Code4 | INT | IOD_SS3_TCP | 40039
SS3ErrorComKlima1Code5 | INT | IOD_SS3_TCP | 40040
SS3ErrorComKlima1Code6 | INT | IOD_SS3_TCP | 40041
SS3ErrorComKlima1Code7 | INT | IOD_SS3_TCP | 40042
SS3ErrorComKlima1Code8 | INT | IOD_SS3_TCP | 40043
SS3ErrorComKlima1Code9 | INT | IOD_SS3_TCP | 40044
SS3ErrorComKlima1Error | DIGITAL | IOD_SS3_TCP | 00284
SS3ErrorComKlima1Status | INT | IOD_SS3_TCP | 40045
SS3ErrorComKlima2Code0 | INT | IOD_SS3_TCP | 40046
SS3ErrorComKlima2Code10 | INT | IOD_SS3_TCP | 40047
SS3ErrorComKlima2Code11 | INT | IOD_SS3_TCP | 40048
SS3ErrorComKlima2Code12 | INT | IOD_SS3_TCP | 40049
SS3ErrorComKlima2Code13 | INT | IOD_SS3_TCP | 40050
SS3ErrorComKlima2Code14 | INT | IOD_SS3_TCP | 40051
SS3ErrorComKlima2Code15 | INT | IOD_SS3_TCP | 40052
SS3ErrorComKlima2Code1 | INT | IOD_SS3_TCP | 40053
SS3ErrorComKlima2Code2 | INT | IOD_SS3_TCP | 40054
SS3ErrorComKlima2Code3 | INT | IOD_SS3_TCP | 40055
SS3ErrorComKlima2Code4 | INT | IOD_SS3_TCP | 40056
SS3ErrorComKlima2Code5 | INT | IOD_SS3_TCP | 40057
SS3ErrorComKlima2Code6 | INT | IOD_SS3_TCP | 40058
SS3ErrorComKlima2Code7 | INT | IOD_SS3_TCP | 40059
SS3ErrorComKlima2Code8 | INT | IOD_SS3_TCP | 40060
SS3ErrorComKlima2Code9 | INT | IOD_SS3_TCP | 40061
SS3ErrorComKlima2Error | DIGITAL | IOD_SS3_TCP | 00285
SS3ErrorComKlima2Status | INT | IOD_SS3_TCP | 40062
SS3ErrorComKlima3Code0 | INT | IOD_SS3_TCP | 40063
SS3ErrorComKlima3Code10 | INT | IOD_SS3_TCP | 40064
SS3ErrorComKlima3Code11 | INT | IOD_SS3_TCP | 40065
SS3ErrorComKlima3Code12 | INT | IOD_SS3_TCP | 40066
SS3ErrorComKlima3Code13 | INT | IOD_SS3_TCP | 40067
SS3ErrorComKlima3Code14 | INT | IOD_SS3_TCP | 40068
SS3ErrorComKlima3Code15 | INT | IOD_SS3_TCP | 40069
SS3ErrorComKlima3Code1 | INT | IOD_SS3_TCP | 40070
SS3ErrorComKlima3Code2 | INT | IOD_SS3_TCP | 40071
SS3ErrorComKlima3Code3 | INT | IOD_SS3_TCP | 40072
SS3ErrorComKlima3Code4 | INT | IOD_SS3_TCP | 40073
SS3ErrorComKlima3Code5 | INT | IOD_SS3_TCP | 40074
SS3ErrorComKlima3Code6 | INT | IOD_SS3_TCP | 40075
SS3ErrorComKlima3Code7 | INT | IOD_SS3_TCP | 40076
SS3ErrorComKlima3Code8 | INT | IOD_SS3_TCP | 40077
SS3ErrorComKlima3Code9 | INT | IOD_SS3_TCP | 40078
SS3ErrorComKlima3Error | DIGITAL | IOD_SS3_TCP | 00286
SS3ErrorComKlima3Status | INT | IOD_SS3_TCP | 40079
SS3ErrorComKlima4Code0 | INT | IOD_SS3_TCP | 40080
SS3ErrorComKlima4Code10 | INT | IOD_SS3_TCP | 40081
SS3ErrorComKlima4Code11 | INT | IOD_SS3_TCP | 40082
SS3ErrorComKlima4Code12 | INT | IOD_SS3_TCP | 40083
SS3ErrorComKlima4Code13 | INT | IOD_SS3_TCP | 40084
SS3ErrorComKlima4Code14 | INT | IOD_SS3_TCP | 40085
SS3ErrorComKlima4Code15 | INT | IOD_SS3_TCP | 40086
SS3ErrorComKlima4Code1 | INT | IOD_SS3_TCP | 40087
SS3ErrorComKlima4Code2 | INT | IOD_SS3_TCP | 40088
SS3ErrorComKlima4Code3 | INT | IOD_SS3_TCP | 40089
SS3ErrorComKlima4Code4 | INT | IOD_SS3_TCP | 40090
SS3ErrorComKlima4Code5 | INT | IOD_SS3_TCP | 40091
SS3ErrorComKlima4Code6 | INT | IOD_SS3_TCP | 40092
SS3ErrorComKlima4Code7 | INT | IOD_SS3_TCP | 40093
SS3ErrorComKlima4Code8 | INT | IOD_SS3_TCP | 40094
SS3ErrorComKlima4Code9 | INT | IOD_SS3_TCP | 40095
SS3ErrCommScada2 | DIGITAL | IOD_SS3_TCP | 00287
SS3ComSCADA2 | DIGITAL | IOD_SS3_TCP | 00288
SS3ErrComSCADA_Om2 | DIGITAL | IOD_SS3_disk | D2002
SS3Server_A_Izpad | DIGITAL | IOD_SS3_disk | D2003
SS3Server_B_Izpad | DIGITAL | IOD_SS3_disk | D2004
SS3ComSCADA_stevec3 | INT | IOD_SS3_mem | I2006
SS3ComSCADA_stevec | INT | IOD_SS3_mem | I2008
SS3kom_nast_cas_izpada | INT | IOD_SS3_TCP | 40096
SS3ComSCADA3 | DIGITAL | IOD_SS3_TCP | 00289
SS3NapakaSenzorTemp4_Om | DIGITAL | IOD_SS3_disk | D5000
SS3NapakaSenzorTemp5_Om | DIGITAL | IOD_SS3_disk | D5001
SS3NapakaSenzorVlaga4_Om | DIGITAL | IOD_SS3_disk | D5002
SS3NapakaSenzorVlaga5_Om | DIGITAL | IOD_SS3_disk | D5003
SS3AlarmTempTIA4Previsoka_Om | DIGITAL | IOD_SS3_disk | D5004
SS3AlarmTempTIA5Previsoka_Om | DIGITAL | IOD_SS3_disk | D5005
SS3AlarmTempTIA4Previsoka | DIGITAL | IOD_SS3_TCP | 00290
SS3AlarmTempTIA5Previsoka | DIGITAL | IOD_SS3_TCP | 00291
SS3NapakaSenzorTemp4 | DIGITAL | IOD_SS3_TCP | 00292
SS3NapakaSenzorTemp5 | DIGITAL | IOD_SS3_TCP | 00293
SS3NapakaSenzorVlaga4 | DIGITAL | IOD_SS3_TCP | 00294
SS3NapakaSenzorVlaga5 | DIGITAL | IOD_SS3_TCP | 00295
SS3SKTemp4 | REAL | IOD_SS3_TCP | 44079 | 0 | 60 | 0 | 60 | °C | ####.#
SS3SKTemp5 | REAL | IOD_SS3_TCP | 44081 | 0 | 60 | 0 | 60 | °C | ####.#
SS3SKVlaga4 | REAL | IOD_SS3_TCP | 44083 | 0 | 100 | 0 | 100 | % | ####.#
SS3SKVlaga5 | REAL | IOD_SS3_TCP | 44085 | 0 | 100 | 0 | 100 | % | ####.#
SS3TempZaAlarmTIA4 | REAL | IOD_SS3_TCP | 44087 | 0 | 60 | 0 | 60 | °C | ####.#
SS3TempZaAlarmTIA5 | REAL | IOD_SS3_TCP | 44089 | 0 | 60 | 0 | 60 | °C | ####.#
SS3SKTemp4_Opozorilo_Zgornja_Meja | REAL | IOD_SS3_disk | R17 | 0 | 100 | 0 | 100 | % | ####.#
SS3SKTemp4_Alarm_Zgornja_Meja | REAL | IOD_SS3_disk | R18 | 0 | 60 | 0 | 60 | °C | ####.#
SS3SKTemp4_Opozorilo_Omogoci | DIGITAL | IOD_SS3_disk | D5006
SS3SKTemp4_Alarm_Omogoci | DIGITAL | IOD_SS3_disk | D5007
SS3SKVlaga4_Opozorilo_Zgornja_Meja | REAL | IOD_SS3_disk | R19 | 0 | 100 | 0 | 100 | % | ####.#
SS3SKVlaga4_Alarm_Zgornja_Meja | REAL | IOD_SS3_disk | R20 | 0 | 100 | 0 | 100 | % | ####.#
SS3SKVlaga4_Opozorilo_Omogoci | DIGITAL | IOD_SS3_disk | D5008
SS3SKVlaga4_Alarm_Omogoci | DIGITAL | IOD_SS3_disk | D5009
SS3SKTemp5_Opozorilo_Zgornja_Meja | REAL | IOD_SS3_disk | R21 | 0 | 100 | 0 | 100 | % | ####.#
SS3SKTemp5_Alarm_Zgornja_Meja | REAL | IOD_SS3_disk | R22 | 0 | 60 | 0 | 60 | °C | ####.#
SS3SKTemp5_Opozorilo_Omogoci | DIGITAL | IOD_SS3_disk | D5010
SS3SKTemp5_Alarm_Omogoci | DIGITAL | IOD_SS3_disk | D5011
SS3SKVlaga5_Opozorilo_Zgornja_Meja | REAL | IOD_SS3_disk | R23 | 0 | 100 | 0 | 100 | % | ####.#
SS3SKVlaga5_Alarm_Zgornja_Meja | REAL | IOD_SS3_disk | R24 | 0 | 100 | 0 | 100 | % | ####.#
SS3SKVlaga5_Opozorilo_Omogoci | DIGITAL | IOD_SS3_disk | D5012
SS3SKVlaga5_Alarm_Omogoci | DIGITAL | IOD_SS3_disk | D5013
SS3SKTempServSoba1Povpr | REAL | IOD_SS3_TCP | 44091 | 0 | 60 | 0 | 60 | °C | ####.#
SS3SKTempServSoba2Povpr | REAL | IOD_SS3_TCP | 44093 | 0 | 60 | 0 | 60 | °C | ####.#
SS3TempZaAlarmTIA124 | REAL | IOD_SS3_TCP | 44095 | 0 | 60 | 0 | 60 | °C | ####.#
SS3TempZaAlarmTIA35 | REAL | IOD_SS3_TCP | 44097 | 0 | 60 | 0 | 60 | °C | ####.#
SS3AlarmTempTIA124Previsoka | DIGITAL | IOD_SS3_TCP | 00296
SS3AlarmTempTIA35Previsoka | DIGITAL | IOD_SS3_TCP | 00297
SS3AlarmTempTIA124Previsoka_Om | DIGITAL | IOD_SS3_disk | D5014
SS3AlarmTempTIA35Previsoka_Om | DIGITAL | IOD_SS3_disk | D5015
A2SS3_omogoci_sms | DIGITAL | IOD_SS3_disk | D5020[200]
B2SS3_omogoci_sms | DIGITAL | IOD_SS3_disk | D5220[200]

## XSoft
mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Write_BOOL(FC) | mod_Write_Word(FC) | mod_Write_Word(FC) | mod_Write_dWord(FC) | mod_Write_dWord(FC) | mod_Write_String(FC)
(*Branje BOOL*) | (*Branje INT*) | (*Branje UINT*) | (*Branje LONG*) | (*Branje REAL*) | (*Branje STRING*) | (*Pisanje BOOL*) | (*Pisanje INT*) | (*Pisanje UINT*) | (*Pisanje LONG*) | (*Pisanje REAL*) | (*Pisanje STRING*)
(**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**)
mind_bool[0]:=AlarmKlimat1_Napaka; | mind[0]:=DatumCas.Dan; |  |  | Read_Real(rVar:=AktualniSetPointTemp1_2,lo:=4000,hi:=4001); | Read_String(sVar:=UserName,start:=5000); | 0:AlarmKlimat1_Napaka:=Bit_0; | 0:DatumCas.Dan:=Byte_0; |  |  | 4001:AktualniSetPointTemp1_2:=Real_0; | 5000:UserName:=String_0;
mind_bool[1]:=AlarmKlimat2_Napaka; | mind[1]:=DatumCas.Leto; |  |  | Read_Real(rVar:=AktualniSetPointTemp3_4,lo:=4002,hi:=4003); | Read_String(sVar:=Date_Time[0],start:=5015); | 1:AlarmKlimat2_Napaka:=Bit_0; | 1:DatumCas.Leto:=Byte_0; |  |  | 4003:AktualniSetPointTemp3_4:=Real_0; | 5015:Date_Time[0]:=String_0;
mind_bool[2]:=AlarmKlimat3_Napaka; | mind[2]:=DatumCas.Leto2; |  |  | Read_Real(rVar:=Klima1ure,lo:=4004,hi:=4005); | Read_String(sVar:=Date_Time[1],start:=5030); | 2:AlarmKlimat3_Napaka:=Bit_0; | 2:DatumCas.Leto2:=Word_01; |  |  | 4005:Klima1ure:=Real_0; | 5030:Date_Time[1]:=String_0;
mind_bool[3]:=AlarmKlimat4_Napaka; | mind[3]:=DatumCas.Mesec; |  |  | Read_Real(rVar:=Klima2ure,lo:=4006,hi:=4007); | Read_String(sVar:=Date_Time[2],start:=5045); | 3:AlarmKlimat4_Napaka:=Bit_0; | 3:DatumCas.Mesec:=Byte_0; |  |  | 4007:Klima2ure:=Real_0; | 5045:Date_Time[2]:=String_0;
mind_bool[4]:=AlarmLAH1_RazlitjeVode; | mind[4]:=DatumCas.Minuta; |  |  | Read_Real(rVar:=Klima3ure,lo:=4008,hi:=4009); | Read_String(sVar:=Date_Time[3],start:=5060); | 4:AlarmLAH1_RazlitjeVode:=Bit_0; | 4:DatumCas.Minuta:=Byte_0; |  |  | 4009:Klima3ure:=Real_0; | 5060:Date_Time[3]:=String_0;
mind_bool[5]:=AlarmLAH2_RazlitjeVode; | mind[5]:=DatumCas.Sekunda; |  |  | Read_Real(rVar:=Klima4ure,lo:=4010,hi:=4011); |  | 5:AlarmLAH2_RazlitjeVode:=Bit_0; | 5:DatumCas.Sekunda:=Byte_0; |  |  | 4011:Klima4ure:=Real_0;
mind_bool[6]:=AlarmSinhronizacijaNOK; | mind[6]:=DatumCas.Ura; |  |  | Read_Real(rVar:=Klima[1].NastTempProstora,lo:=4012,hi:=4013); |  | 6:AlarmSinhronizacijaNOK:=Bit_0; | 6:DatumCas.Ura:=Byte_0; |  |  | 4013:Klima[1].NastTempProstora:=Real_0;
mind_bool[7]:=AlarmTempTIA1Previsoka; | mind[7]:=ErrorComKlima[4].Status; |  |  | Read_Real(rVar:=Klima[1].NastVlaznost,lo:=4014,hi:=4015); |  | 7:AlarmTempTIA1Previsoka:=Bit_0; | 7:ErrorComKlima[4].Status:=Word_01; |  |  | 4015:Klima[1].NastVlaznost:=Real_0;
mind_bool[8]:=AlarmTempTIA2Previsoka; | mind[8]:=Klima[1].GrelecStatus; |  |  | Read_Real(rVar:=Klima[1].ObratovalneUre,lo:=4016,hi:=4017); |  | 8:AlarmTempTIA2Previsoka:=Bit_0; | 8:Klima[1].GrelecStatus:=Byte_0; |  |  | 4017:Klima[1].ObratovalneUre:=Real_0;
mind_bool[9]:=AlarmTempTIA3Previsoka; | mind[9]:=Klima[1].IzhodniVentStatus; |  |  | Read_Real(rVar:=Klima[1].TemperaturaProstora,lo:=4018,hi:=4019); |  | 9:AlarmTempTIA3Previsoka:=Bit_0; | 9:Klima[1].IzhodniVentStatus:=Byte_0; |  |  | 4019:Klima[1].TemperaturaProstora:=Real_0;
mind_bool[10]:=AlarmTSTemp1Previsoka; | mind[10]:=Klima[1].KompresorStatus; |  |  | Read_Real(rVar:=Klima[1].VlaznostProstora,lo:=4020,hi:=4021); |  | 10:AlarmTSTemp1Previsoka:=Bit_0; | 10:Klima[1].KompresorStatus:=Byte_0; |  |  | 4021:Klima[1].VlaznostProstora:=Real_0;
mind_bool[11]:=AlarmTSTemp3Previsoka; | mind[11]:=Klima[1].VlazilecStatus; |  |  | Read_Real(rVar:=Klima[2].NastTempProstora,lo:=4022,hi:=4023); |  | 11:AlarmTSTemp3Previsoka:=Bit_0; | 11:Klima[1].VlazilecStatus:=Byte_0; |  |  | 4023:Klima[2].NastTempProstora:=Real_0;
mind_bool[12]:=AlarmUPSKrmOmara_Alarm; | mind[12]:=Klima[2].GrelecStatus; |  |  | Read_Real(rVar:=Klima[2].NastVlaznost,lo:=4024,hi:=4025); |  | 12:AlarmUPSKrmOmara_Alarm:=Bit_0; | 12:Klima[2].GrelecStatus:=Byte_0; |  |  | 4025:Klima[2].NastVlaznost:=Real_0;
mind_bool[13]:=ComSCADA; | mind[13]:=Klima[2].IzhodniVentStatus; |  |  | Read_Real(rVar:=Klima[2].ObratovalneUre,lo:=4026,hi:=4027); |  | 13:ComSCADA:=Bit_0; | 13:Klima[2].IzhodniVentStatus:=Byte_0; |  |  | 4027:Klima[2].ObratovalneUre:=Real_0;
mind_bool[14]:=ComSCADA1; | mind[14]:=Klima[2].KompresorStatus; |  |  | Read_Real(rVar:=Klima[2].TemperaturaProstora,lo:=4028,hi:=4029); |  | 14:ComSCADA1:=Bit_0; | 14:Klima[2].KompresorStatus:=Byte_0; |  |  | 4029:Klima[2].TemperaturaProstora:=Real_0;
mind_bool[15]:=ErrComKlima[1]; | mind[15]:=Klima[2].VlazilecStatus; |  |  | Read_Real(rVar:=Klima[2].VlaznostProstora,lo:=4030,hi:=4031); |  | 15:ErrComKlima[1]:=Bit_0; | 15:Klima[2].VlazilecStatus:=Byte_0; |  |  | 4031:Klima[2].VlaznostProstora:=Real_0;
mind_bool[16]:=ErrComKlima[2]; | mind[16]:=Klima[3].GrelecStatus; |  |  | Read_Real(rVar:=Klima[3].NastTempProstora,lo:=4032,hi:=4033); |  | 16:ErrComKlima[2]:=Bit_0; | 16:Klima[3].GrelecStatus:=Byte_0; |  |  | 4033:Klima[3].NastTempProstora:=Real_0;
mind_bool[17]:=ErrComKlima[3]; | mind[17]:=Klima[3].IzhodniVentStatus; |  |  | Read_Real(rVar:=Klima[3].NastVlaznost,lo:=4034,hi:=4035); |  | 17:ErrComKlima[3]:=Bit_0; | 17:Klima[3].IzhodniVentStatus:=Byte_0; |  |  | 4035:Klima[3].NastVlaznost:=Real_0;
mind_bool[18]:=ErrComKlima[4]; | mind[18]:=Klima[3].KompresorStatus; |  |  | Read_Real(rVar:=Klima[3].ObratovalneUre,lo:=4036,hi:=4037); |  | 18:ErrComKlima[4]:=Bit_0; | 18:Klima[3].KompresorStatus:=Byte_0; |  |  | 4037:Klima[3].ObratovalneUre:=Real_0;
mind_bool[19]:=ErrCommScada; | mind[19]:=Klima[3].VlazilecStatus; |  |  | Read_Real(rVar:=Klima[3].TemperaturaProstora,lo:=4038,hi:=4039); |  | 19:ErrCommScada:=Bit_0; | 19:Klima[3].VlazilecStatus:=Byte_0; |  |  | 4039:Klima[3].TemperaturaProstora:=Real_0;
mind_bool[20]:=ErrComPanelPLC; | mind[20]:=Klima[4].GrelecStatus; |  |  | Read_Real(rVar:=Klima[3].VlaznostProstora,lo:=4040,hi:=4041); |  | 20:ErrComPanelPLC:=Bit_0; | 20:Klima[4].GrelecStatus:=Byte_0; |  |  | 4041:Klima[3].VlaznostProstora:=Real_0;
mind_bool[21]:=ErrComPort2; | mind[21]:=Klima[4].IzhodniVentStatus; |  |  | Read_Real(rVar:=Klima[4].NastTempProstora,lo:=4042,hi:=4043); |  | 21:ErrComPort2:=Bit_0; | 21:Klima[4].IzhodniVentStatus:=Byte_0; |  |  | 4043:Klima[4].NastTempProstora:=Real_0;
mind_bool[22]:=ErrorComKlima[4].Error; | mind[22]:=Klima[4].KompresorStatus; |  |  | Read_Real(rVar:=Klima[4].NastVlaznost,lo:=4044,hi:=4045); |  | 22:ErrorComKlima[4].Error:=Bit_0; | 22:Klima[4].KompresorStatus:=Byte_0; |  |  | 4045:Klima[4].NastVlaznost:=Real_0;
mind_bool[23]:=Klima1_Onemogocena; | mind[23]:=Klima[4].VlazilecStatus; |  |  | Read_Real(rVar:=Klima[4].ObratovalneUre,lo:=4046,hi:=4047); |  | 23:Klima1_Onemogocena:=Bit_0; | 23:Klima[4].VlazilecStatus:=Byte_0; |  |  | 4047:Klima[4].ObratovalneUre:=Real_0;
mind_bool[24]:=Klima2_Onemogocena; | mind[24]:=StUrZaPreklopKlim1_2; |  |  | Read_Real(rVar:=Klima[4].TemperaturaProstora,lo:=4048,hi:=4049); |  | 24:Klima2_Onemogocena:=Bit_0; | 24:StUrZaPreklopKlim1_2:=Word_01; |  |  | 4049:Klima[4].TemperaturaProstora:=Real_0;
mind_bool[25]:=Klima3_Onemogocena; | mind[25]:=StUrZaPreklopKlim3_4; |  |  | Read_Real(rVar:=Klima[4].VlaznostProstora,lo:=4050,hi:=4051); |  | 25:Klima3_Onemogocena:=Bit_0; | 25:StUrZaPreklopKlim3_4:=Word_01; |  |  | 4051:Klima[4].VlaznostProstora:=Real_0;
mind_bool[26]:=Klima4_Onemogocena; | mind[26]:=UPSstatus_Prikaz_PanelSCADA; |  |  | Read_Real(rVar:=SKTemp1,lo:=4052,hi:=4053); |  | 26:Klima4_Onemogocena:=Bit_0; | 26:UPSstatus_Prikaz_PanelSCADA:=Byte_0; |  |  | 4053:SKTemp1:=Real_0;
mind_bool[27]:=Klima[1].Deluje; | mind[27]:=UserCurrentLevel; |  |  | Read_Real(rVar:=SKTemp2,lo:=4054,hi:=4055); |  | 27:Klima[1].Deluje:=Bit_0; | 27:UserCurrentLevel:=Byte_0; |  |  | 4055:SKTemp2:=Real_0;
mind_bool[28]:=Klima[1].EnergySaving; | mind[28]:=ErrorComKlima[1].Code[0]; |  |  | Read_Real(rVar:=SKTemp3,lo:=4056,hi:=4057); |  | 28:Klima[1].EnergySaving:=Bit_0; | 28:ErrorComKlima[1].Code[0]:=Byte_0; |  |  | 4057:SKTemp3:=Real_0;
mind_bool[29]:=Klima[1].Napaka; | mind[29]:=ErrorComKlima[1].Code[10]; |  |  | Read_Real(rVar:=SKVlaga1,lo:=4058,hi:=4059); |  | 29:Klima[1].Napaka:=Bit_0; | 29:ErrorComKlima[1].Code[10]:=Byte_0; |  |  | 4059:SKVlaga1:=Real_0;
mind_bool[30]:=Klima[1].OnOffEnablingBySupervisor; | mind[30]:=ErrorComKlima[1].Code[11]; |  |  | Read_Real(rVar:=SKVlaga2,lo:=4060,hi:=4061); |  | 30:Klima[1].OnOffEnablingBySupervisor:=Bit_0; | 30:ErrorComKlima[1].Code[11]:=Byte_0; |  |  | 4061:SKVlaga2:=Real_0;
mind_bool[31]:=Klima[1].Razvlazevanje; | mind[31]:=ErrorComKlima[1].Code[12]; |  |  | Read_Real(rVar:=SKVlaga3,lo:=4062,hi:=4063); |  | 31:Klima[1].Razvlazevanje:=Bit_0; | 31:ErrorComKlima[1].Code[12]:=Byte_0; |  |  | 4063:SKVlaga3:=Real_0;
mind_bool[32]:=Klima[1].RemoteOFFtoOutput; | mind[32]:=ErrorComKlima[1].Code[13]; |  |  | Read_Real(rVar:=TempZaAlarm1_2,lo:=4064,hi:=4065); |  | 32:Klima[1].RemoteOFFtoOutput:=Bit_0; | 32:ErrorComKlima[1].Code[13]:=Byte_0; |  |  | 4065:TempZaAlarm1_2:=Real_0;
mind_bool[33]:=Klima[1].RemoteOnOff; | mind[33]:=ErrorComKlima[1].Code[14]; |  |  | Read_Real(rVar:=TempZaAlarm3_4,lo:=4066,hi:=4067); |  | 33:Klima[1].RemoteOnOff:=Bit_0; | 33:ErrorComKlima[1].Code[14]:=Byte_0; |  |  | 4067:TempZaAlarm3_4:=Real_0;
mind_bool[34]:=Klima[1].RocniIzklop; | mind[34]:=ErrorComKlima[1].Code[15]; |  |  | Read_Real(rVar:=TempZaAlarmTIA1,lo:=4068,hi:=4069); |  | 34:Klima[1].RocniIzklop:=Bit_0; | 34:ErrorComKlima[1].Code[15]:=Byte_0; |  |  | 4069:TempZaAlarmTIA1:=Real_0;
mind_bool[35]:=Klima[1].SenzorjiStatus; | mind[35]:=ErrorComKlima[1].Code[1]; |  |  | Read_Real(rVar:=TempZaAlarmTIA2,lo:=4070,hi:=4071); |  | 35:Klima[1].SenzorjiStatus:=Bit_0; | 35:ErrorComKlima[1].Code[1]:=Byte_0; |  |  | 4071:TempZaAlarmTIA2:=Real_0;
mind_bool[36]:=Klima[1].UnitOnOff; | mind[36]:=ErrorComKlima[1].Code[2]; |  |  | Read_Real(rVar:=TempZaAlarmTIA3,lo:=4072,hi:=4073); |  | 36:Klima[1].UnitOnOff:=Bit_0; | 36:ErrorComKlima[1].Code[2]:=Byte_0; |  |  | 4073:TempZaAlarmTIA3:=Real_0;
mind_bool[37]:=Klima[1].VentilGretjeOdpiranje; | mind[37]:=ErrorComKlima[1].Code[3]; |  |  | Read_Real(rVar:=TempZaVklopObehKlim1_2,lo:=4074,hi:=4075); |  | 37:Klima[1].VentilGretjeOdpiranje:=Bit_0; | 37:ErrorComKlima[1].Code[3]:=Byte_0; |  |  | 4075:TempZaVklopObehKlim1_2:=Real_0;
mind_bool[38]:=Klima[1].VentilGretjeZapiranje; | mind[38]:=ErrorComKlima[1].Code[4]; |  |  | Read_Real(rVar:=TempZaVklopObehKlim3_4,lo:=4076,hi:=4077); |  | 38:Klima[1].VentilGretjeZapiranje:=Bit_0; | 38:ErrorComKlima[1].Code[4]:=Byte_0; |  |  | 4077:TempZaVklopObehKlim3_4:=Real_0;
mind_bool[39]:=Klima[1].VentilHlajenjeOdpiranje; | mind[39]:=ErrorComKlima[1].Code[5]; |  |  | Read_Real(rVar:=SKTemp4,lo:=4078,hi:=4079); |  | 39:Klima[1].VentilHlajenjeOdpiranje:=Bit_0; | 39:ErrorComKlima[1].Code[5]:=Byte_0; |  |  | 4079:SKTemp4:=Real_0;
mind_bool[40]:=Klima[1].VentilHlajenjeZapiranje; | mind[40]:=ErrorComKlima[1].Code[6]; |  |  | Read_Real(rVar:=SKTemp5,lo:=4080,hi:=4081); |  | 40:Klima[1].VentilHlajenjeZapiranje:=Bit_0; | 40:ErrorComKlima[1].Code[6]:=Byte_0; |  |  | 4081:SKTemp5:=Real_0;
mind_bool[41]:=Klima[1].Vlazenje; | mind[41]:=ErrorComKlima[1].Code[7]; |  |  | Read_Real(rVar:=SKVlaga4,lo:=4082,hi:=4083); |  | 41:Klima[1].Vlazenje:=Bit_0; | 41:ErrorComKlima[1].Code[7]:=Byte_0; |  |  | 4083:SKVlaga4:=Real_0;
mind_bool[42]:=Klima[2].Deluje; | mind[42]:=ErrorComKlima[1].Code[8]; |  |  | Read_Real(rVar:=SKVlaga5,lo:=4084,hi:=4085); |  | 42:Klima[2].Deluje:=Bit_0; | 42:ErrorComKlima[1].Code[8]:=Byte_0; |  |  | 4085:SKVlaga5:=Real_0;
mind_bool[43]:=Klima[2].EnergySaving; | mind[43]:=ErrorComKlima[1].Code[9]; |  |  | Read_Real(rVar:=TempZaAlarmTIA4,lo:=4086,hi:=4087); |  | 43:Klima[2].EnergySaving:=Bit_0; | 43:ErrorComKlima[1].Code[9]:=Byte_0; |  |  | 4087:TempZaAlarmTIA4:=Real_0;
mind_bool[44]:=Klima[2].Napaka; | mind[44]:=ErrorComKlima[1].Status; |  |  | Read_Real(rVar:=TempZaAlarmTIA5,lo:=4088,hi:=4089); |  | 44:Klima[2].Napaka:=Bit_0; | 44:ErrorComKlima[1].Status:=Word_01; |  |  | 4089:TempZaAlarmTIA5:=Real_0;
mind_bool[45]:=Klima[2].OnOffEnablingBySupervisor; | mind[45]:=ErrorComKlima[2].Code[0]; |  |  | Read_Real(rVar:=SKTempServSoba1Povpr,lo:=4090,hi:=4091); |  | 45:Klima[2].OnOffEnablingBySupervisor:=Bit_0; | 45:ErrorComKlima[2].Code[0]:=Byte_0; |  |  | 4091:SKTempServSoba1Povpr:=Real_0;
mind_bool[46]:=Klima[2].Razvlazevanje; | mind[46]:=ErrorComKlima[2].Code[10]; |  |  | Read_Real(rVar:=SKTempServSoba2Povpr,lo:=4092,hi:=4093); |  | 46:Klima[2].Razvlazevanje:=Bit_0; | 46:ErrorComKlima[2].Code[10]:=Byte_0; |  |  | 4093:SKTempServSoba2Povpr:=Real_0;
mind_bool[47]:=Klima[2].RemoteOFFtoOutput; | mind[47]:=ErrorComKlima[2].Code[11]; |  |  | Read_Real(rVar:=TempZaAlarmTIA124,lo:=4094,hi:=4095); |  | 47:Klima[2].RemoteOFFtoOutput:=Bit_0; | 47:ErrorComKlima[2].Code[11]:=Byte_0; |  |  | 4095:TempZaAlarmTIA124:=Real_0;
mind_bool[48]:=Klima[2].RemoteOnOff; | mind[48]:=ErrorComKlima[2].Code[12]; |  |  | Read_Real(rVar:=TempZaAlarmTIA35,lo:=4096,hi:=4097); |  | 48:Klima[2].RemoteOnOff:=Bit_0; | 48:ErrorComKlima[2].Code[12]:=Byte_0; |  |  | 4097:TempZaAlarmTIA35:=Real_0;
mind_bool[49]:=Klima[2].RocniIzklop; | mind[49]:=ErrorComKlima[2].Code[13]; |  |  |  |  | 49:Klima[2].RocniIzklop:=Bit_0; | 49:ErrorComKlima[2].Code[13]:=Byte_0;
mind_bool[50]:=Klima[2].SenzorjiStatus; | mind[50]:=ErrorComKlima[2].Code[14]; |  |  |  |  | 50:Klima[2].SenzorjiStatus:=Bit_0; | 50:ErrorComKlima[2].Code[14]:=Byte_0;
mind_bool[51]:=Klima[2].UnitOnOff; | mind[51]:=ErrorComKlima[2].Code[15]; |  |  |  |  | 51:Klima[2].UnitOnOff:=Bit_0; | 51:ErrorComKlima[2].Code[15]:=Byte_0;
mind_bool[52]:=Klima[2].VentilGretjeOdpiranje; | mind[52]:=ErrorComKlima[2].Code[1]; |  |  |  |  | 52:Klima[2].VentilGretjeOdpiranje:=Bit_0; | 52:ErrorComKlima[2].Code[1]:=Byte_0;
mind_bool[53]:=Klima[2].VentilGretjeZapiranje; | mind[53]:=ErrorComKlima[2].Code[2]; |  |  |  |  | 53:Klima[2].VentilGretjeZapiranje:=Bit_0; | 53:ErrorComKlima[2].Code[2]:=Byte_0;
mind_bool[54]:=Klima[2].VentilHlajenjeOdpiranje; | mind[54]:=ErrorComKlima[2].Code[3]; |  |  |  |  | 54:Klima[2].VentilHlajenjeOdpiranje:=Bit_0; | 54:ErrorComKlima[2].Code[3]:=Byte_0;
mind_bool[55]:=Klima[2].VentilHlajenjeZapiranje; | mind[55]:=ErrorComKlima[2].Code[4]; |  |  |  |  | 55:Klima[2].VentilHlajenjeZapiranje:=Bit_0; | 55:ErrorComKlima[2].Code[4]:=Byte_0;
mind_bool[56]:=Klima[2].Vlazenje; | mind[56]:=ErrorComKlima[2].Code[5]; |  |  |  |  | 56:Klima[2].Vlazenje:=Bit_0; | 56:ErrorComKlima[2].Code[5]:=Byte_0;
mind_bool[57]:=Klima[3].Deluje; | mind[57]:=ErrorComKlima[2].Code[6]; |  |  |  |  | 57:Klima[3].Deluje:=Bit_0; | 57:ErrorComKlima[2].Code[6]:=Byte_0;
mind_bool[58]:=Klima[3].EnergySaving; | mind[58]:=ErrorComKlima[2].Code[7]; |  |  |  |  | 58:Klima[3].EnergySaving:=Bit_0; | 58:ErrorComKlima[2].Code[7]:=Byte_0;
mind_bool[59]:=Klima[3].Napaka; | mind[59]:=ErrorComKlima[2].Code[8]; |  |  |  |  | 59:Klima[3].Napaka:=Bit_0; | 59:ErrorComKlima[2].Code[8]:=Byte_0;
mind_bool[60]:=Klima[3].OnOffEnablingBySupervisor; | mind[60]:=ErrorComKlima[2].Code[9]; |  |  |  |  | 60:Klima[3].OnOffEnablingBySupervisor:=Bit_0; | 60:ErrorComKlima[2].Code[9]:=Byte_0;
mind_bool[61]:=Klima[3].Razvlazevanje; | mind[61]:=ErrorComKlima[2].Status; |  |  |  |  | 61:Klima[3].Razvlazevanje:=Bit_0; | 61:ErrorComKlima[2].Status:=Word_01;
mind_bool[62]:=Klima[3].RemoteOFFtoOutput; | mind[62]:=ErrorComKlima[3].Code[0]; |  |  |  |  | 62:Klima[3].RemoteOFFtoOutput:=Bit_0; | 62:ErrorComKlima[3].Code[0]:=Byte_0;
mind_bool[63]:=Klima[3].RemoteOnOff; | mind[63]:=ErrorComKlima[3].Code[10]; |  |  |  |  | 63:Klima[3].RemoteOnOff:=Bit_0; | 63:ErrorComKlima[3].Code[10]:=Byte_0;
mind_bool[64]:=Klima[3].RocniIzklop; | mind[64]:=ErrorComKlima[3].Code[11]; |  |  |  |  | 64:Klima[3].RocniIzklop:=Bit_0; | 64:ErrorComKlima[3].Code[11]:=Byte_0;
mind_bool[65]:=Klima[3].SenzorjiStatus; | mind[65]:=ErrorComKlima[3].Code[12]; |  |  |  |  | 65:Klima[3].SenzorjiStatus:=Bit_0; | 65:ErrorComKlima[3].Code[12]:=Byte_0;
mind_bool[66]:=Klima[3].UnitOnOff; | mind[66]:=ErrorComKlima[3].Code[13]; |  |  |  |  | 66:Klima[3].UnitOnOff:=Bit_0; | 66:ErrorComKlima[3].Code[13]:=Byte_0;
mind_bool[67]:=Klima[3].VentilGretjeOdpiranje; | mind[67]:=ErrorComKlima[3].Code[14]; |  |  |  |  | 67:Klima[3].VentilGretjeOdpiranje:=Bit_0; | 67:ErrorComKlima[3].Code[14]:=Byte_0;
mind_bool[68]:=Klima[3].VentilGretjeZapiranje; | mind[68]:=ErrorComKlima[3].Code[15]; |  |  |  |  | 68:Klima[3].VentilGretjeZapiranje:=Bit_0; | 68:ErrorComKlima[3].Code[15]:=Byte_0;
mind_bool[69]:=Klima[3].VentilHlajenjeOdpiranje; | mind[69]:=ErrorComKlima[3].Code[1]; |  |  |  |  | 69:Klima[3].VentilHlajenjeOdpiranje:=Bit_0; | 69:ErrorComKlima[3].Code[1]:=Byte_0;
mind_bool[70]:=Klima[3].VentilHlajenjeZapiranje; | mind[70]:=ErrorComKlima[3].Code[2]; |  |  |  |  | 70:Klima[3].VentilHlajenjeZapiranje:=Bit_0; | 70:ErrorComKlima[3].Code[2]:=Byte_0;
mind_bool[71]:=Klima[3].Vlazenje; | mind[71]:=ErrorComKlima[3].Code[3]; |  |  |  |  | 71:Klima[3].Vlazenje:=Bit_0; | 71:ErrorComKlima[3].Code[3]:=Byte_0;
mind_bool[72]:=Klima[4].Deluje; | mind[72]:=ErrorComKlima[3].Code[4]; |  |  |  |  | 72:Klima[4].Deluje:=Bit_0; | 72:ErrorComKlima[3].Code[4]:=Byte_0;
mind_bool[73]:=Klima[4].EnergySaving; | mind[73]:=ErrorComKlima[3].Code[5]; |  |  |  |  | 73:Klima[4].EnergySaving:=Bit_0; | 73:ErrorComKlima[3].Code[5]:=Byte_0;
mind_bool[74]:=Klima[4].Napaka; | mind[74]:=ErrorComKlima[3].Code[6]; |  |  |  |  | 74:Klima[4].Napaka:=Bit_0; | 74:ErrorComKlima[3].Code[6]:=Byte_0;
mind_bool[75]:=Klima[4].OnOffEnablingBySupervisor; | mind[75]:=ErrorComKlima[3].Code[7]; |  |  |  |  | 75:Klima[4].OnOffEnablingBySupervisor:=Bit_0; | 75:ErrorComKlima[3].Code[7]:=Byte_0;
mind_bool[76]:=Klima[4].Razvlazevanje; | mind[76]:=ErrorComKlima[3].Code[8]; |  |  |  |  | 76:Klima[4].Razvlazevanje:=Bit_0; | 76:ErrorComKlima[3].Code[8]:=Byte_0;
mind_bool[77]:=Klima[4].RemoteOFFtoOutput; | mind[77]:=ErrorComKlima[3].Code[9]; |  |  |  |  | 77:Klima[4].RemoteOFFtoOutput:=Bit_0; | 77:ErrorComKlima[3].Code[9]:=Byte_0;
mind_bool[78]:=Klima[4].RemoteOnOff; | mind[78]:=ErrorComKlima[3].Status; |  |  |  |  | 78:Klima[4].RemoteOnOff:=Bit_0; | 78:ErrorComKlima[3].Status:=Word_01;
mind_bool[79]:=Klima[4].RocniIzklop; | mind[79]:=ErrorComKlima[4].Code[0]; |  |  |  |  | 79:Klima[4].RocniIzklop:=Bit_0; | 79:ErrorComKlima[4].Code[0]:=Byte_0;
mind_bool[80]:=Klima[4].SenzorjiStatus; | mind[80]:=ErrorComKlima[4].Code[10]; |  |  |  |  | 80:Klima[4].SenzorjiStatus:=Bit_0; | 80:ErrorComKlima[4].Code[10]:=Byte_0;
mind_bool[81]:=Klima[4].UnitOnOff; | mind[81]:=ErrorComKlima[4].Code[11]; |  |  |  |  | 81:Klima[4].UnitOnOff:=Bit_0; | 81:ErrorComKlima[4].Code[11]:=Byte_0;
mind_bool[82]:=Klima[4].VentilGretjeOdpiranje; | mind[82]:=ErrorComKlima[4].Code[12]; |  |  |  |  | 82:Klima[4].VentilGretjeOdpiranje:=Bit_0; | 82:ErrorComKlima[4].Code[12]:=Byte_0;
mind_bool[83]:=Klima[4].VentilGretjeZapiranje; | mind[83]:=ErrorComKlima[4].Code[13]; |  |  |  |  | 83:Klima[4].VentilGretjeZapiranje:=Bit_0; | 83:ErrorComKlima[4].Code[13]:=Byte_0;
mind_bool[84]:=Klima[4].VentilHlajenjeOdpiranje; | mind[84]:=ErrorComKlima[4].Code[14]; |  |  |  |  | 84:Klima[4].VentilHlajenjeOdpiranje:=Bit_0; | 84:ErrorComKlima[4].Code[14]:=Byte_0;
mind_bool[85]:=Klima[4].VentilHlajenjeZapiranje; | mind[85]:=ErrorComKlima[4].Code[15]; |  |  |  |  | 85:Klima[4].VentilHlajenjeZapiranje:=Bit_0; | 85:ErrorComKlima[4].Code[15]:=Byte_0;
mind_bool[86]:=Klima[4].Vlazenje; | mind[86]:=ErrorComKlima[4].Code[1]; |  |  |  |  | 86:Klima[4].Vlazenje:=Bit_0; | 86:ErrorComKlima[4].Code[1]:=Byte_0;
mind_bool[87]:=KlimaError[1].AlarmKompresor1; | mind[87]:=ErrorComKlima[4].Code[2]; |  |  |  |  | 87:KlimaError[1].AlarmKompresor1:=Bit_0; | 87:ErrorComKlima[4].Code[2]:=Byte_0;
mind_bool[88]:=KlimaError[1].AlarmKompresor2; | mind[88]:=ErrorComKlima[4].Code[3]; |  |  |  |  | 88:KlimaError[1].AlarmKompresor2:=Bit_0; | 88:ErrorComKlima[4].Code[3]:=Byte_0;
mind_bool[89]:=KlimaError[1].FaultyEprom; | mind[89]:=ErrorComKlima[4].Code[4]; |  |  |  |  | 89:KlimaError[1].FaultyEprom:=Bit_0; | 89:ErrorComKlima[4].Code[4]:=Byte_0;
mind_bool[90]:=KlimaError[1].FenThermalCutout; | mind[90]:=ErrorComKlima[4].Code[5]; |  |  |  |  | 90:KlimaError[1].FenThermalCutout:=Bit_0; | 90:ErrorComKlima[4].Code[5]:=Byte_0;
mind_bool[91]:=KlimaError[1].GeneralAlarm; | mind[91]:=ErrorComKlima[4].Code[6]; |  |  |  |  | 91:KlimaError[1].GeneralAlarm:=Bit_0; | 91:ErrorComKlima[4].Code[6]:=Byte_0;
mind_bool[92]:=KlimaError[1].Kompresor1naMejiStevilaObrUr; | mind[92]:=ErrorComKlima[4].Code[7]; |  |  |  |  | 92:KlimaError[1].Kompresor1naMejiStevilaObrUr:=Bit_0; | 92:ErrorComKlima[4].Code[7]:=Byte_0;
mind_bool[93]:=KlimaError[1].Kompresor2naMejiStevilaObrUr; | mind[93]:=ErrorComKlima[4].Code[8]; |  |  |  |  | 93:KlimaError[1].Kompresor2naMejiStevilaObrUr:=Bit_0; | 93:ErrorComKlima[4].Code[8]:=Byte_0;
mind_bool[94]:=KlimaError[1].Kond1FenThermalCutout; | mind[94]:=ErrorComKlima[4].Code[9]; |  |  |  |  | 94:KlimaError[1].Kond1FenThermalCutout:=Bit_0; | 94:ErrorComKlima[4].Code[9]:=Byte_0;
mind_bool[95]:=KlimaError[1].Kond2FenThermalCutout; | mind[95]:=kom_nast_cas_izpada; |  |  |  |  | 95:KlimaError[1].Kond2FenThermalCutout:=Bit_0; | 95:kom_nast_cas_izpada:=Word_01;
mind_bool[96]:=KlimaError[1].NapakaPriPretokuVode; | [5 empty] | 96:KlimaError[1].NapakaPriPretokuVode:=Bit_0;
mind_bool[97]:=KlimaError[1].NapakaPriPretokuZraka; | [5 empty] | 97:KlimaError[1].NapakaPriPretokuZraka:=Bit_0;
mind_bool[98]:=KlimaError[1].NapakaSenzorPovratVode; | [5 empty] | 98:KlimaError[1].NapakaSenzorPovratVode:=Bit_0;
mind_bool[99]:=KlimaError[1].NapakaSenzorPritiska; | [5 empty] | 99:KlimaError[1].NapakaSenzorPritiska:=Bit_0;
mind_bool[100]:=KlimaError[1].NapakaSenzorTempIzpiha; | [5 empty] | 100:KlimaError[1].NapakaSenzorTempIzpiha:=Bit_0;
mind_bool[101]:=KlimaError[1].NapakaSenzorTempProstora; | [5 empty] | 101:KlimaError[1].NapakaSenzorTempProstora:=Bit_0;
mind_bool[102]:=KlimaError[1].NapakaSenzorVlaznosti; | [5 empty] | 102:KlimaError[1].NapakaSenzorVlaznosti:=Bit_0;
mind_bool[103]:=KlimaError[1].NapakaSenzorZunanjeTemp; | [5 empty] | 103:KlimaError[1].NapakaSenzorZunanjeTemp:=Bit_0;
mind_bool[104]:=KlimaError[1].NapakaTSTemperaturaProstora; | [5 empty] | 104:KlimaError[1].NapakaTSTemperaturaProstora:=Bit_0;
mind_bool[105]:=KlimaError[1].NiTokaVVlazilcu; | [5 empty] | 105:KlimaError[1].NiTokaVVlazilcu:=Bit_0;
mind_bool[106]:=KlimaError[1].NiVodeVVlazilcu; | [5 empty] | 106:KlimaError[1].NiVodeVVlazilcu:=Bit_0;
mind_bool[107]:=KlimaError[1].NizekPritiskKompresor1; | [5 empty] | 107:KlimaError[1].NizekPritiskKompresor1:=Bit_0;
mind_bool[108]:=KlimaError[1].NizekPritiskKompresor2; | [5 empty] | 108:KlimaError[1].NizekPritiskKompresor2:=Bit_0;
mind_bool[109]:=KlimaError[1].NizkaTempPovratneVode; | [5 empty] | 109:KlimaError[1].NizkaTempPovratneVode:=Bit_0;
mind_bool[110]:=KlimaError[1].NizkaTempVProstoru; | [5 empty] | 110:KlimaError[1].NizkaTempVProstoru:=Bit_0;
mind_bool[111]:=KlimaError[1].NizkaVlaznost; | [5 empty] | 111:KlimaError[1].NizkaVlaznost:=Bit_0;
mind_bool[112]:=KlimaError[1].PozarniAlarm; | [5 empty] | 112:KlimaError[1].PozarniAlarm:=Bit_0;
mind_bool[113]:=KlimaError[1].StoppedByAlarms; | [5 empty] | 113:KlimaError[1].StoppedByAlarms:=Bit_0;
mind_bool[114]:=KlimaError[1].TermZascInVisokPritiskKompr1; | [5 empty] | 114:KlimaError[1].TermZascInVisokPritiskKompr1:=Bit_0;
mind_bool[115]:=KlimaError[1].TermZascInVisokPritiskKompr2; | [5 empty] | 115:KlimaError[1].TermZascInVisokPritiskKompr2:=Bit_0;
mind_bool[116]:=KlimaError[1].ThermalCutoutHeater1; | [5 empty] | 116:KlimaError[1].ThermalCutoutHeater1:=Bit_0;
mind_bool[117]:=KlimaError[1].ThermalCutoutHeater2; | [5 empty] | 117:KlimaError[1].ThermalCutoutHeater2:=Bit_0;
mind_bool[118]:=KlimaError[1].VentilatorNaMejiStevilaObrUr; | [5 empty] | 118:KlimaError[1].VentilatorNaMejiStevilaObrUr:=Bit_0;
mind_bool[119]:=KlimaError[1].VisokaTempPovratneVode; | [5 empty] | 119:KlimaError[1].VisokaTempPovratneVode:=Bit_0;
mind_bool[120]:=KlimaError[1].VisokaTempVProstoru; | [5 empty] | 120:KlimaError[1].VisokaTempVProstoru:=Bit_0;
mind_bool[121]:=KlimaError[1].VisokaVlaznost; | [5 empty] | 121:KlimaError[1].VisokaVlaznost:=Bit_0;
mind_bool[122]:=KlimaError[1].VisokPritiskVKrogu1; | [5 empty] | 122:KlimaError[1].VisokPritiskVKrogu1:=Bit_0;
mind_bool[123]:=KlimaError[1].VisokPritiskVKrogu2; | [5 empty] | 123:KlimaError[1].VisokPritiskVKrogu2:=Bit_0;
mind_bool[124]:=KlimaError[1].VisokTokVVlazilcu; | [5 empty] | 124:KlimaError[1].VisokTokVVlazilcu:=Bit_0;
mind_bool[125]:=KlimaError[1].VlazilecnaMejiStevilaObrUr; | [5 empty] | 125:KlimaError[1].VlazilecnaMejiStevilaObrUr:=Bit_0;
mind_bool[126]:=KlimaError[1].ZamasenFilter; | [5 empty] | 126:KlimaError[1].ZamasenFilter:=Bit_0;
mind_bool[127]:=KlimaError[2].AlarmKompresor1; | [5 empty] | 127:KlimaError[2].AlarmKompresor1:=Bit_0;
mind_bool[128]:=KlimaError[2].AlarmKompresor2; | [5 empty] | 128:KlimaError[2].AlarmKompresor2:=Bit_0;
mind_bool[129]:=KlimaError[2].FaultyEprom; | [5 empty] | 129:KlimaError[2].FaultyEprom:=Bit_0;
mind_bool[130]:=KlimaError[2].FenThermalCutout; | [5 empty] | 130:KlimaError[2].FenThermalCutout:=Bit_0;
mind_bool[131]:=KlimaError[2].GeneralAlarm; | [5 empty] | 131:KlimaError[2].GeneralAlarm:=Bit_0;
mind_bool[132]:=KlimaError[2].Kompresor1naMejiStevilaObrUr; | [5 empty] | 132:KlimaError[2].Kompresor1naMejiStevilaObrUr:=Bit_0;
mind_bool[133]:=KlimaError[2].Kompresor2naMejiStevilaObrUr; | [5 empty] | 133:KlimaError[2].Kompresor2naMejiStevilaObrUr:=Bit_0;
mind_bool[134]:=KlimaError[2].Kond1FenThermalCutout; | [5 empty] | 134:KlimaError[2].Kond1FenThermalCutout:=Bit_0;
mind_bool[135]:=KlimaError[2].Kond2FenThermalCutout; | [5 empty] | 135:KlimaError[2].Kond2FenThermalCutout:=Bit_0;
mind_bool[136]:=KlimaError[2].NapakaPriPretokuVode; | [5 empty] | 136:KlimaError[2].NapakaPriPretokuVode:=Bit_0;
mind_bool[137]:=KlimaError[2].NapakaPriPretokuZraka; | [5 empty] | 137:KlimaError[2].NapakaPriPretokuZraka:=Bit_0;
mind_bool[138]:=KlimaError[2].NapakaSenzorPovratVode; | [5 empty] | 138:KlimaError[2].NapakaSenzorPovratVode:=Bit_0;
mind_bool[139]:=KlimaError[2].NapakaSenzorPritiska; | [5 empty] | 139:KlimaError[2].NapakaSenzorPritiska:=Bit_0;
mind_bool[140]:=KlimaError[2].NapakaSenzorTempIzpiha; | [5 empty] | 140:KlimaError[2].NapakaSenzorTempIzpiha:=Bit_0;
mind_bool[141]:=KlimaError[2].NapakaSenzorTempProstora; | [5 empty] | 141:KlimaError[2].NapakaSenzorTempProstora:=Bit_0;
mind_bool[142]:=KlimaError[2].NapakaSenzorVlaznosti; | [5 empty] | 142:KlimaError[2].NapakaSenzorVlaznosti:=Bit_0;
mind_bool[143]:=KlimaError[2].NapakaSenzorZunanjeTemp; | [5 empty] | 143:KlimaError[2].NapakaSenzorZunanjeTemp:=Bit_0;
mind_bool[144]:=KlimaError[2].NapakaTSTemperaturaProstora; | [5 empty] | 144:KlimaError[2].NapakaTSTemperaturaProstora:=Bit_0;
mind_bool[145]:=KlimaError[2].NiTokaVVlazilcu; | [5 empty] | 145:KlimaError[2].NiTokaVVlazilcu:=Bit_0;
mind_bool[146]:=KlimaError[2].NiVodeVVlazilcu; | [5 empty] | 146:KlimaError[2].NiVodeVVlazilcu:=Bit_0;
mind_bool[147]:=KlimaError[2].NizekPritiskKompresor1; | [5 empty] | 147:KlimaError[2].NizekPritiskKompresor1:=Bit_0;
mind_bool[148]:=KlimaError[2].NizekPritiskKompresor2; | [5 empty] | 148:KlimaError[2].NizekPritiskKompresor2:=Bit_0;
mind_bool[149]:=KlimaError[2].NizkaTempPovratneVode; | [5 empty] | 149:KlimaError[2].NizkaTempPovratneVode:=Bit_0;
mind_bool[150]:=KlimaError[2].NizkaTempVProstoru; | [5 empty] | 150:KlimaError[2].NizkaTempVProstoru:=Bit_0;
mind_bool[151]:=KlimaError[2].NizkaVlaznost; | [5 empty] | 151:KlimaError[2].NizkaVlaznost:=Bit_0;
mind_bool[152]:=KlimaError[2].PozarniAlarm; | [5 empty] | 152:KlimaError[2].PozarniAlarm:=Bit_0;
mind_bool[153]:=KlimaError[2].StoppedByAlarms; | [5 empty] | 153:KlimaError[2].StoppedByAlarms:=Bit_0;
mind_bool[154]:=KlimaError[2].TermZascInVisokPritiskKompr1; | [5 empty] | 154:KlimaError[2].TermZascInVisokPritiskKompr1:=Bit_0;
mind_bool[155]:=KlimaError[2].TermZascInVisokPritiskKompr2; | [5 empty] | 155:KlimaError[2].TermZascInVisokPritiskKompr2:=Bit_0;
mind_bool[156]:=KlimaError[2].ThermalCutoutHeater1; | [5 empty] | 156:KlimaError[2].ThermalCutoutHeater1:=Bit_0;
mind_bool[157]:=KlimaError[2].ThermalCutoutHeater2; | [5 empty] | 157:KlimaError[2].ThermalCutoutHeater2:=Bit_0;
mind_bool[158]:=KlimaError[2].VentilatorNaMejiStevilaObrUr; | [5 empty] | 158:KlimaError[2].VentilatorNaMejiStevilaObrUr:=Bit_0;
mind_bool[159]:=KlimaError[2].VisokaTempPovratneVode; | [5 empty] | 159:KlimaError[2].VisokaTempPovratneVode:=Bit_0;
mind_bool[160]:=KlimaError[2].VisokaTempVProstoru; | [5 empty] | 160:KlimaError[2].VisokaTempVProstoru:=Bit_0;
mind_bool[161]:=KlimaError[2].VisokaVlaznost; | [5 empty] | 161:KlimaError[2].VisokaVlaznost:=Bit_0;
mind_bool[162]:=KlimaError[2].VisokPritiskVKrogu1; | [5 empty] | 162:KlimaError[2].VisokPritiskVKrogu1:=Bit_0;
mind_bool[163]:=KlimaError[2].VisokPritiskVKrogu2; | [5 empty] | 163:KlimaError[2].VisokPritiskVKrogu2:=Bit_0;
mind_bool[164]:=KlimaError[2].VisokTokVVlazilcu; | [5 empty] | 164:KlimaError[2].VisokTokVVlazilcu:=Bit_0;
mind_bool[165]:=KlimaError[2].VlazilecnaMejiStevilaObrUr; | [5 empty] | 165:KlimaError[2].VlazilecnaMejiStevilaObrUr:=Bit_0;
mind_bool[166]:=KlimaError[2].ZamasenFilter; | [5 empty] | 166:KlimaError[2].ZamasenFilter:=Bit_0;
mind_bool[167]:=KlimaError[3].AlarmKompresor1; | [5 empty] | 167:KlimaError[3].AlarmKompresor1:=Bit_0;
mind_bool[168]:=KlimaError[3].AlarmKompresor2; | [5 empty] | 168:KlimaError[3].AlarmKompresor2:=Bit_0;
mind_bool[169]:=KlimaError[3].FaultyEprom; | [5 empty] | 169:KlimaError[3].FaultyEprom:=Bit_0;
mind_bool[170]:=KlimaError[3].FenThermalCutout; | [5 empty] | 170:KlimaError[3].FenThermalCutout:=Bit_0;
mind_bool[171]:=KlimaError[3].GeneralAlarm; | [5 empty] | 171:KlimaError[3].GeneralAlarm:=Bit_0;
mind_bool[172]:=KlimaError[3].Kompresor1naMejiStevilaObrUr; | [5 empty] | 172:KlimaError[3].Kompresor1naMejiStevilaObrUr:=Bit_0;
mind_bool[173]:=KlimaError[3].Kompresor2naMejiStevilaObrUr; | [5 empty] | 173:KlimaError[3].Kompresor2naMejiStevilaObrUr:=Bit_0;
mind_bool[174]:=KlimaError[3].Kond1FenThermalCutout; | [5 empty] | 174:KlimaError[3].Kond1FenThermalCutout:=Bit_0;
mind_bool[175]:=KlimaError[3].Kond2FenThermalCutout; | [5 empty] | 175:KlimaError[3].Kond2FenThermalCutout:=Bit_0;
mind_bool[176]:=KlimaError[3].NapakaPriPretokuVode; | [5 empty] | 176:KlimaError[3].NapakaPriPretokuVode:=Bit_0;
mind_bool[177]:=KlimaError[3].NapakaPriPretokuZraka; | [5 empty] | 177:KlimaError[3].NapakaPriPretokuZraka:=Bit_0;
mind_bool[178]:=KlimaError[3].NapakaSenzorPovratVode; | [5 empty] | 178:KlimaError[3].NapakaSenzorPovratVode:=Bit_0;
mind_bool[179]:=KlimaError[3].NapakaSenzorPritiska; | [5 empty] | 179:KlimaError[3].NapakaSenzorPritiska:=Bit_0;
mind_bool[180]:=KlimaError[3].NapakaSenzorTempIzpiha; | [5 empty] | 180:KlimaError[3].NapakaSenzorTempIzpiha:=Bit_0;
mind_bool[181]:=KlimaError[3].NapakaSenzorTempProstora; | [5 empty] | 181:KlimaError[3].NapakaSenzorTempProstora:=Bit_0;
mind_bool[182]:=KlimaError[3].NapakaSenzorVlaznosti; | [5 empty] | 182:KlimaError[3].NapakaSenzorVlaznosti:=Bit_0;
mind_bool[183]:=KlimaError[3].NapakaSenzorZunanjeTemp; | [5 empty] | 183:KlimaError[3].NapakaSenzorZunanjeTemp:=Bit_0;
mind_bool[184]:=KlimaError[3].NapakaTSTemperaturaProstora; | [5 empty] | 184:KlimaError[3].NapakaTSTemperaturaProstora:=Bit_0;
mind_bool[185]:=KlimaError[3].NiTokaVVlazilcu; | [5 empty] | 185:KlimaError[3].NiTokaVVlazilcu:=Bit_0;
mind_bool[186]:=KlimaError[3].NiVodeVVlazilcu; | [5 empty] | 186:KlimaError[3].NiVodeVVlazilcu:=Bit_0;
mind_bool[187]:=KlimaError[3].NizekPritiskKompresor1; | [5 empty] | 187:KlimaError[3].NizekPritiskKompresor1:=Bit_0;
mind_bool[188]:=KlimaError[3].NizekPritiskKompresor2; | [5 empty] | 188:KlimaError[3].NizekPritiskKompresor2:=Bit_0;
mind_bool[189]:=KlimaError[3].NizkaTempPovratneVode; | [5 empty] | 189:KlimaError[3].NizkaTempPovratneVode:=Bit_0;
mind_bool[190]:=KlimaError[3].NizkaTempVProstoru; | [5 empty] | 190:KlimaError[3].NizkaTempVProstoru:=Bit_0;
mind_bool[191]:=KlimaError[3].NizkaVlaznost; | [5 empty] | 191:KlimaError[3].NizkaVlaznost:=Bit_0;
mind_bool[192]:=KlimaError[3].PozarniAlarm; | [5 empty] | 192:KlimaError[3].PozarniAlarm:=Bit_0;
mind_bool[193]:=KlimaError[3].StoppedByAlarms; | [5 empty] | 193:KlimaError[3].StoppedByAlarms:=Bit_0;
mind_bool[194]:=KlimaError[3].TermZascInVisokPritiskKompr1; | [5 empty] | 194:KlimaError[3].TermZascInVisokPritiskKompr1:=Bit_0;
mind_bool[195]:=KlimaError[3].TermZascInVisokPritiskKompr2; | [5 empty] | 195:KlimaError[3].TermZascInVisokPritiskKompr2:=Bit_0;
mind_bool[196]:=KlimaError[3].ThermalCutoutHeater1; | [5 empty] | 196:KlimaError[3].ThermalCutoutHeater1:=Bit_0;
mind_bool[197]:=KlimaError[3].ThermalCutoutHeater2; | [5 empty] | 197:KlimaError[3].ThermalCutoutHeater2:=Bit_0;
mind_bool[198]:=KlimaError[3].VentilatorNaMejiStevilaObrUr; | [5 empty] | 198:KlimaError[3].VentilatorNaMejiStevilaObrUr:=Bit_0;
mind_bool[199]:=KlimaError[3].VisokaTempPovratneVode; | [5 empty] | 199:KlimaError[3].VisokaTempPovratneVode:=Bit_0;
mind_bool[200]:=KlimaError[3].VisokaTempVProstoru; | [5 empty] | 200:KlimaError[3].VisokaTempVProstoru:=Bit_0;
mind_bool[201]:=KlimaError[3].VisokaVlaznost; | [5 empty] | 201:KlimaError[3].VisokaVlaznost:=Bit_0;
mind_bool[202]:=KlimaError[3].VisokPritiskVKrogu1; | [5 empty] | 202:KlimaError[3].VisokPritiskVKrogu1:=Bit_0;
mind_bool[203]:=KlimaError[3].VisokPritiskVKrogu2; | [5 empty] | 203:KlimaError[3].VisokPritiskVKrogu2:=Bit_0;
mind_bool[204]:=KlimaError[3].VisokTokVVlazilcu; | [5 empty] | 204:KlimaError[3].VisokTokVVlazilcu:=Bit_0;
mind_bool[205]:=KlimaError[3].VlazilecnaMejiStevilaObrUr; | [5 empty] | 205:KlimaError[3].VlazilecnaMejiStevilaObrUr:=Bit_0;
mind_bool[206]:=KlimaError[3].ZamasenFilter; | [5 empty] | 206:KlimaError[3].ZamasenFilter:=Bit_0;
mind_bool[207]:=KlimaError[4].AlarmKompresor1; | [5 empty] | 207:KlimaError[4].AlarmKompresor1:=Bit_0;
mind_bool[208]:=KlimaError[4].AlarmKompresor2; | [5 empty] | 208:KlimaError[4].AlarmKompresor2:=Bit_0;
mind_bool[209]:=KlimaError[4].FaultyEprom; | [5 empty] | 209:KlimaError[4].FaultyEprom:=Bit_0;
mind_bool[210]:=KlimaError[4].FenThermalCutout; | [5 empty] | 210:KlimaError[4].FenThermalCutout:=Bit_0;
mind_bool[211]:=KlimaError[4].GeneralAlarm; | [5 empty] | 211:KlimaError[4].GeneralAlarm:=Bit_0;
mind_bool[212]:=KlimaError[4].Kompresor1naMejiStevilaObrUr; | [5 empty] | 212:KlimaError[4].Kompresor1naMejiStevilaObrUr:=Bit_0;
mind_bool[213]:=KlimaError[4].Kompresor2naMejiStevilaObrUr; | [5 empty] | 213:KlimaError[4].Kompresor2naMejiStevilaObrUr:=Bit_0;
mind_bool[214]:=KlimaError[4].Kond1FenThermalCutout; | [5 empty] | 214:KlimaError[4].Kond1FenThermalCutout:=Bit_0;
mind_bool[215]:=KlimaError[4].Kond2FenThermalCutout; | [5 empty] | 215:KlimaError[4].Kond2FenThermalCutout:=Bit_0;
mind_bool[216]:=KlimaError[4].NapakaPriPretokuVode; | [5 empty] | 216:KlimaError[4].NapakaPriPretokuVode:=Bit_0;
mind_bool[217]:=KlimaError[4].NapakaPriPretokuZraka; | [5 empty] | 217:KlimaError[4].NapakaPriPretokuZraka:=Bit_0;
mind_bool[218]:=KlimaError[4].NapakaSenzorPovratVode; | [5 empty] | 218:KlimaError[4].NapakaSenzorPovratVode:=Bit_0;
mind_bool[219]:=KlimaError[4].NapakaSenzorPritiska; | [5 empty] | 219:KlimaError[4].NapakaSenzorPritiska:=Bit_0;
mind_bool[220]:=KlimaError[4].NapakaSenzorTempIzpiha; | [5 empty] | 220:KlimaError[4].NapakaSenzorTempIzpiha:=Bit_0;
mind_bool[221]:=KlimaError[4].NapakaSenzorTempProstora; | [5 empty] | 221:KlimaError[4].NapakaSenzorTempProstora:=Bit_0;
mind_bool[222]:=KlimaError[4].NapakaSenzorVlaznosti; | [5 empty] | 222:KlimaError[4].NapakaSenzorVlaznosti:=Bit_0;
mind_bool[223]:=KlimaError[4].NapakaSenzorZunanjeTemp; | [5 empty] | 223:KlimaError[4].NapakaSenzorZunanjeTemp:=Bit_0;
mind_bool[224]:=KlimaError[4].NapakaTSTemperaturaProstora; | [5 empty] | 224:KlimaError[4].NapakaTSTemperaturaProstora:=Bit_0;
mind_bool[225]:=KlimaError[4].NiTokaVVlazilcu; | [5 empty] | 225:KlimaError[4].NiTokaVVlazilcu:=Bit_0;
mind_bool[226]:=KlimaError[4].NiVodeVVlazilcu; | [5 empty] | 226:KlimaError[4].NiVodeVVlazilcu:=Bit_0;
mind_bool[227]:=KlimaError[4].NizekPritiskKompresor1; | [5 empty] | 227:KlimaError[4].NizekPritiskKompresor1:=Bit_0;
mind_bool[228]:=KlimaError[4].NizekPritiskKompresor2; | [5 empty] | 228:KlimaError[4].NizekPritiskKompresor2:=Bit_0;
mind_bool[229]:=KlimaError[4].NizkaTempPovratneVode; | [5 empty] | 229:KlimaError[4].NizkaTempPovratneVode:=Bit_0;
mind_bool[230]:=KlimaError[4].NizkaTempVProstoru; | [5 empty] | 230:KlimaError[4].NizkaTempVProstoru:=Bit_0;
mind_bool[231]:=KlimaError[4].NizkaVlaznost; | [5 empty] | 231:KlimaError[4].NizkaVlaznost:=Bit_0;
mind_bool[232]:=KlimaError[4].PozarniAlarm; | [5 empty] | 232:KlimaError[4].PozarniAlarm:=Bit_0;
mind_bool[233]:=KlimaError[4].StoppedByAlarms; | [5 empty] | 233:KlimaError[4].StoppedByAlarms:=Bit_0;
mind_bool[234]:=KlimaError[4].TermZascInVisokPritiskKompr1; | [5 empty] | 234:KlimaError[4].TermZascInVisokPritiskKompr1:=Bit_0;
mind_bool[235]:=KlimaError[4].TermZascInVisokPritiskKompr2; | [5 empty] | 235:KlimaError[4].TermZascInVisokPritiskKompr2:=Bit_0;
mind_bool[236]:=KlimaError[4].ThermalCutoutHeater1; | [5 empty] | 236:KlimaError[4].ThermalCutoutHeater1:=Bit_0;
mind_bool[237]:=KlimaError[4].ThermalCutoutHeater2; | [5 empty] | 237:KlimaError[4].ThermalCutoutHeater2:=Bit_0;
mind_bool[238]:=KlimaError[4].VentilatorNaMejiStevilaObrUr; | [5 empty] | 238:KlimaError[4].VentilatorNaMejiStevilaObrUr:=Bit_0;
mind_bool[239]:=KlimaError[4].VisokaTempPovratneVode; | [5 empty] | 239:KlimaError[4].VisokaTempPovratneVode:=Bit_0;
mind_bool[240]:=KlimaError[4].VisokaTempVProstoru; | [5 empty] | 240:KlimaError[4].VisokaTempVProstoru:=Bit_0;
mind_bool[241]:=KlimaError[4].VisokaVlaznost; | [5 empty] | 241:KlimaError[4].VisokaVlaznost:=Bit_0;
mind_bool[242]:=KlimaError[4].VisokPritiskVKrogu1; | [5 empty] | 242:KlimaError[4].VisokPritiskVKrogu1:=Bit_0;
mind_bool[243]:=KlimaError[4].VisokPritiskVKrogu2; | [5 empty] | 243:KlimaError[4].VisokPritiskVKrogu2:=Bit_0;
mind_bool[244]:=KlimaError[4].VisokTokVVlazilcu; | [5 empty] | 244:KlimaError[4].VisokTokVVlazilcu:=Bit_0;
mind_bool[245]:=KlimaError[4].VlazilecnaMejiStevilaObrUr; | [5 empty] | 245:KlimaError[4].VlazilecnaMejiStevilaObrUr:=Bit_0;
mind_bool[246]:=KlimaError[4].ZamasenFilter; | [5 empty] | 246:KlimaError[4].ZamasenFilter:=Bit_0;
mind_bool[247]:=NacDelovanjaKlime1_2_Avtomatsko; | [5 empty] | 247:NacDelovanjaKlime1_2_Avtomatsko:=Bit_0;
mind_bool[248]:=NacDelovanjaKlime3_4_Avtomatsko; | [5 empty] | 248:NacDelovanjaKlime3_4_Avtomatsko:=Bit_0;
mind_bool[249]:=NapakaSenzorTemp1; | [5 empty] | 249:NapakaSenzorTemp1:=Bit_0;
mind_bool[250]:=NapakaSenzorTemp2; | [5 empty] | 250:NapakaSenzorTemp2:=Bit_0;
mind_bool[251]:=NapakaSenzorTemp3; | [5 empty] | 251:NapakaSenzorTemp3:=Bit_0;
mind_bool[252]:=NapakaSenzorVlaga1; | [5 empty] | 252:NapakaSenzorVlaga1:=Bit_0;
mind_bool[253]:=NapakaSenzorVlaga2; | [5 empty] | 253:NapakaSenzorVlaga2:=Bit_0;
mind_bool[254]:=NapakaSenzorVlaga3; | [5 empty] | 254:NapakaSenzorVlaga3:=Bit_0;
mind_bool[255]:=NastaviCasNaKrmilniku; | [5 empty] | 255:NastaviCasNaKrmilniku:=Bit_0;
mind_bool[256]:=NastavitevUreKrUspesna; | [5 empty] | 256:NastavitevUreKrUspesna:=Bit_0;
mind_bool[257]:=OpozoriloBaterijaPLC; | [5 empty] | 257:OpozoriloBaterijaPLC:=Bit_0;
mind_bool[258]:=OsveziAlarmePanel; | [5 empty] | 258:OsveziAlarmePanel:=Bit_0;
mind_bool[259]:=RocniVklopKlima1; | [5 empty] | 259:RocniVklopKlima1:=Bit_0;
mind_bool[260]:=RocniVklopKlima2; | [5 empty] | 260:RocniVklopKlima2:=Bit_0;
mind_bool[261]:=RocniVklopKlima3; | [5 empty] | 261:RocniVklopKlima3:=Bit_0;
mind_bool[262]:=RocniVklopKlima4; | [5 empty] | 262:RocniVklopKlima4:=Bit_0;
mind_bool[263]:=SinhronizacijaPanelOK; | [5 empty] | 263:SinhronizacijaPanelOK:=Bit_0;
mind_bool[264]:=SinhronizirajCas_Panel; | [5 empty] | 264:SinhronizirajCas_Panel:=Bit_0;
mind_bool[265]:=SkupneNapakeNaprav_Klima1; | [5 empty] | 265:SkupneNapakeNaprav_Klima1:=Bit_0;
mind_bool[266]:=SkupneNapakeNaprav_Klima2; | [5 empty] | 266:SkupneNapakeNaprav_Klima2:=Bit_0;
mind_bool[267]:=SkupneNapakeNaprav_Klima3; | [5 empty] | 267:SkupneNapakeNaprav_Klima3:=Bit_0;
mind_bool[268]:=SkupneNapakeNaprav_Klima4; | [5 empty] | 268:SkupneNapakeNaprav_Klima4:=Bit_0;
mind_bool[269]:=SkupneNapakeNaprav_Komunikacija; | [5 empty] | 269:SkupneNapakeNaprav_Komunikacija:=Bit_0;
mind_bool[270]:=SkupneNapakeNaprav_TempVlaga; | [5 empty] | 270:SkupneNapakeNaprav_TempVlaga:=Bit_0;
mind_bool[271]:=StanjeKlimat1_Delovanje; | [5 empty] | 271:StanjeKlimat1_Delovanje:=Bit_0;
mind_bool[272]:=StanjeKlimat2_Delovanje; | [5 empty] | 272:StanjeKlimat2_Delovanje:=Bit_0;
mind_bool[273]:=StanjeKlimat3_Delovanje; | [5 empty] | 273:StanjeKlimat3_Delovanje:=Bit_0;
mind_bool[274]:=StanjeKlimat4_Delovanje; | [5 empty] | 274:StanjeKlimat4_Delovanje:=Bit_0;
mind_bool[275]:=StanjeUPSKrmOmara_BaterijskiNacin; | [5 empty] | 275:StanjeUPSKrmOmara_BaterijskiNacin:=Bit_0;
mind_bool[276]:=StanjeUPSKrmOmara_Polnjenje; | [5 empty] | 276:StanjeUPSKrmOmara_Polnjenje:=Bit_0;
mind_bool[277]:=UserLoggedIn; | [5 empty] | 277:UserLoggedIn:=Bit_0;
mind_bool[278]:=XVH_AlarmOn; | [5 empty] | 278:XVH_AlarmOn:=Bit_0;
mind_bool[279]:=Klimat1_Vklop; | [5 empty] | 279:Klimat1_Vklop:=Bit_0;
mind_bool[280]:=Klimat2_Vklop; | [5 empty] | 280:Klimat2_Vklop:=Bit_0;
mind_bool[281]:=Klimat3_Vklop; | [5 empty] | 281:Klimat3_Vklop:=Bit_0;
mind_bool[282]:=Klimat4_Vklop; | [5 empty] | 282:Klimat4_Vklop:=Bit_0;
mind_bool[283]:=ErrorComKlima[1].Error; | [5 empty] | 283:ErrorComKlima[1].Error:=Bit_0;
mind_bool[284]:=ErrorComKlima[2].Error; | [5 empty] | 284:ErrorComKlima[2].Error:=Bit_0;
mind_bool[285]:=ErrorComKlima[3].Error; | [5 empty] | 285:ErrorComKlima[3].Error:=Bit_0;
mind_bool[286]:=ErrCommScada2; | [5 empty] | 286:ErrCommScada2:=Bit_0;
mind_bool[287]:=ComSCADA2; | [5 empty] | 287:ComSCADA2:=Bit_0;
mind_bool[288]:=ComSCADA3; | [5 empty] | 288:ComSCADA3:=Bit_0;
mind_bool[289]:=AlarmTempTIA4Previsoka; | [5 empty] | 289:AlarmTempTIA4Previsoka:=Bit_0;
mind_bool[290]:=AlarmTempTIA5Previsoka; | [5 empty] | 290:AlarmTempTIA5Previsoka:=Bit_0;
mind_bool[291]:=NapakaSenzorTemp4; | [5 empty] | 291:NapakaSenzorTemp4:=Bit_0;
mind_bool[292]:=NapakaSenzorTemp5; | [5 empty] | 292:NapakaSenzorTemp5:=Bit_0;
mind_bool[293]:=NapakaSenzorVlaga4; | [5 empty] | 293:NapakaSenzorVlaga4:=Bit_0;
mind_bool[294]:=NapakaSenzorVlaga5; | [5 empty] | 294:NapakaSenzorVlaga5:=Bit_0;
mind_bool[295]:=AlarmTempTIA124Previsoka; | [5 empty] | 295:AlarmTempTIA124Previsoka:=Bit_0;
mind_bool[296]:=AlarmTempTIA35Previsoka; | [5 empty] | 296:AlarmTempTIA35Previsoka:=Bit_0;

## XSoft_EXP
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
PROGRAM mod_Read
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*Branje BOOL*)
(**)
mind_bool[0]:=AlarmKlimat1_Napaka;
mind_bool[1]:=AlarmKlimat2_Napaka;
mind_bool[2]:=AlarmKlimat3_Napaka;
mind_bool[3]:=AlarmKlimat4_Napaka;
mind_bool[4]:=AlarmLAH1_RazlitjeVode;
mind_bool[5]:=AlarmLAH2_RazlitjeVode;
mind_bool[6]:=AlarmSinhronizacijaNOK;
mind_bool[7]:=AlarmTempTIA1Previsoka;
mind_bool[8]:=AlarmTempTIA2Previsoka;
mind_bool[9]:=AlarmTempTIA3Previsoka;
mind_bool[10]:=AlarmTSTemp1Previsoka;
mind_bool[11]:=AlarmTSTemp3Previsoka;
mind_bool[12]:=AlarmUPSKrmOmara_Alarm;
mind_bool[13]:=ComSCADA;
mind_bool[14]:=ComSCADA1;
mind_bool[15]:=ErrComKlima[1];
mind_bool[16]:=ErrComKlima[2];
mind_bool[17]:=ErrComKlima[3];
mind_bool[18]:=ErrComKlima[4];
mind_bool[19]:=ErrCommScada;
mind_bool[20]:=ErrComPanelPLC;
mind_bool[21]:=ErrComPort2;
mind_bool[22]:=ErrorComKlima[4].Error;
mind_bool[23]:=Klima1_Onemogocena;
mind_bool[24]:=Klima2_Onemogocena;
mind_bool[25]:=Klima3_Onemogocena;
mind_bool[26]:=Klima4_Onemogocena;
mind_bool[27]:=Klima[1].Deluje;
mind_bool[28]:=Klima[1].EnergySaving;
mind_bool[29]:=Klima[1].Napaka;
mind_bool[30]:=Klima[1].OnOffEnablingBySupervisor;
mind_bool[31]:=Klima[1].Razvlazevanje;
mind_bool[32]:=Klima[1].RemoteOFFtoOutput;
mind_bool[33]:=Klima[1].RemoteOnOff;
mind_bool[34]:=Klima[1].RocniIzklop;
mind_bool[35]:=Klima[1].SenzorjiStatus;
mind_bool[36]:=Klima[1].UnitOnOff;
mind_bool[37]:=Klima[1].VentilGretjeOdpiranje;
mind_bool[38]:=Klima[1].VentilGretjeZapiranje;
mind_bool[39]:=Klima[1].VentilHlajenjeOdpiranje;
mind_bool[40]:=Klima[1].VentilHlajenjeZapiranje;
mind_bool[41]:=Klima[1].Vlazenje;
mind_bool[42]:=Klima[2].Deluje;
mind_bool[43]:=Klima[2].EnergySaving;
mind_bool[44]:=Klima[2].Napaka;
mind_bool[45]:=Klima[2].OnOffEnablingBySupervisor;
mind_bool[46]:=Klima[2].Razvlazevanje;
mind_bool[47]:=Klima[2].RemoteOFFtoOutput;
mind_bool[48]:=Klima[2].RemoteOnOff;
mind_bool[49]:=Klima[2].RocniIzklop;
mind_bool[50]:=Klima[2].SenzorjiStatus;
mind_bool[51]:=Klima[2].UnitOnOff;
mind_bool[52]:=Klima[2].VentilGretjeOdpiranje;
mind_bool[53]:=Klima[2].VentilGretjeZapiranje;
mind_bool[54]:=Klima[2].VentilHlajenjeOdpiranje;
mind_bool[55]:=Klima[2].VentilHlajenjeZapiranje;
mind_bool[56]:=Klima[2].Vlazenje;
mind_bool[57]:=Klima[3].Deluje;
mind_bool[58]:=Klima[3].EnergySaving;
mind_bool[59]:=Klima[3].Napaka;
mind_bool[60]:=Klima[3].OnOffEnablingBySupervisor;
mind_bool[61]:=Klima[3].Razvlazevanje;
mind_bool[62]:=Klima[3].RemoteOFFtoOutput;
mind_bool[63]:=Klima[3].RemoteOnOff;
mind_bool[64]:=Klima[3].RocniIzklop;
mind_bool[65]:=Klima[3].SenzorjiStatus;
mind_bool[66]:=Klima[3].UnitOnOff;
mind_bool[67]:=Klima[3].VentilGretjeOdpiranje;
mind_bool[68]:=Klima[3].VentilGretjeZapiranje;
mind_bool[69]:=Klima[3].VentilHlajenjeOdpiranje;
mind_bool[70]:=Klima[3].VentilHlajenjeZapiranje;
mind_bool[71]:=Klima[3].Vlazenje;
mind_bool[72]:=Klima[4].Deluje;
mind_bool[73]:=Klima[4].EnergySaving;
mind_bool[74]:=Klima[4].Napaka;
mind_bool[75]:=Klima[4].OnOffEnablingBySupervisor;
mind_bool[76]:=Klima[4].Razvlazevanje;
mind_bool[77]:=Klima[4].RemoteOFFtoOutput;
mind_bool[78]:=Klima[4].RemoteOnOff;
mind_bool[79]:=Klima[4].RocniIzklop;
mind_bool[80]:=Klima[4].SenzorjiStatus;
mind_bool[81]:=Klima[4].UnitOnOff;
mind_bool[82]:=Klima[4].VentilGretjeOdpiranje;
mind_bool[83]:=Klima[4].VentilGretjeZapiranje;
mind_bool[84]:=Klima[4].VentilHlajenjeOdpiranje;
mind_bool[85]:=Klima[4].VentilHlajenjeZapiranje;
mind_bool[86]:=Klima[4].Vlazenje;
mind_bool[87]:=KlimaError[1].AlarmKompresor1;
mind_bool[88]:=KlimaError[1].AlarmKompresor2;
mind_bool[89]:=KlimaError[1].FaultyEprom;
mind_bool[90]:=KlimaError[1].FenThermalCutout;
mind_bool[91]:=KlimaError[1].GeneralAlarm;
mind_bool[92]:=KlimaError[1].Kompresor1naMejiStevilaObrUr;
mind_bool[93]:=KlimaError[1].Kompresor2naMejiStevilaObrUr;
mind_bool[94]:=KlimaError[1].Kond1FenThermalCutout;
mind_bool[95]:=KlimaError[1].Kond2FenThermalCutout;
mind_bool[96]:=KlimaError[1].NapakaPriPretokuVode;
mind_bool[97]:=KlimaError[1].NapakaPriPretokuZraka;
mind_bool[98]:=KlimaError[1].NapakaSenzorPovratVode;
mind_bool[99]:=KlimaError[1].NapakaSenzorPritiska;
mind_bool[100]:=KlimaError[1].NapakaSenzorTempIzpiha;
mind_bool[101]:=KlimaError[1].NapakaSenzorTempProstora;
mind_bool[102]:=KlimaError[1].NapakaSenzorVlaznosti;
mind_bool[103]:=KlimaError[1].NapakaSenzorZunanjeTemp;
mind_bool[104]:=KlimaError[1].NapakaTSTemperaturaProstora;
mind_bool[105]:=KlimaError[1].NiTokaVVlazilcu;
mind_bool[106]:=KlimaError[1].NiVodeVVlazilcu;
mind_bool[107]:=KlimaError[1].NizekPritiskKompresor1;
mind_bool[108]:=KlimaError[1].NizekPritiskKompresor2;
mind_bool[109]:=KlimaError[1].NizkaTempPovratneVode;
mind_bool[110]:=KlimaError[1].NizkaTempVProstoru;
mind_bool[111]:=KlimaError[1].NizkaVlaznost;
mind_bool[112]:=KlimaError[1].PozarniAlarm;
mind_bool[113]:=KlimaError[1].StoppedByAlarms;
mind_bool[114]:=KlimaError[1].TermZascInVisokPritiskKompr1;
mind_bool[115]:=KlimaError[1].TermZascInVisokPritiskKompr2;
mind_bool[116]:=KlimaError[1].ThermalCutoutHeater1;
mind_bool[117]:=KlimaError[1].ThermalCutoutHeater2;
mind_bool[118]:=KlimaError[1].VentilatorNaMejiStevilaObrUr;
mind_bool[119]:=KlimaError[1].VisokaTempPovratneVode;
mind_bool[120]:=KlimaError[1].VisokaTempVProstoru;
mind_bool[121]:=KlimaError[1].VisokaVlaznost;
mind_bool[122]:=KlimaError[1].VisokPritiskVKrogu1;
mind_bool[123]:=KlimaError[1].VisokPritiskVKrogu2;
mind_bool[124]:=KlimaError[1].VisokTokVVlazilcu;
mind_bool[125]:=KlimaError[1].VlazilecnaMejiStevilaObrUr;
mind_bool[126]:=KlimaError[1].ZamasenFilter;
mind_bool[127]:=KlimaError[2].AlarmKompresor1;
mind_bool[128]:=KlimaError[2].AlarmKompresor2;
mind_bool[129]:=KlimaError[2].FaultyEprom;
mind_bool[130]:=KlimaError[2].FenThermalCutout;
mind_bool[131]:=KlimaError[2].GeneralAlarm;
mind_bool[132]:=KlimaError[2].Kompresor1naMejiStevilaObrUr;
mind_bool[133]:=KlimaError[2].Kompresor2naMejiStevilaObrUr;
mind_bool[134]:=KlimaError[2].Kond1FenThermalCutout;
mind_bool[135]:=KlimaError[2].Kond2FenThermalCutout;
mind_bool[136]:=KlimaError[2].NapakaPriPretokuVode;
mind_bool[137]:=KlimaError[2].NapakaPriPretokuZraka;
mind_bool[138]:=KlimaError[2].NapakaSenzorPovratVode;
mind_bool[139]:=KlimaError[2].NapakaSenzorPritiska;
mind_bool[140]:=KlimaError[2].NapakaSenzorTempIzpiha;
mind_bool[141]:=KlimaError[2].NapakaSenzorTempProstora;
mind_bool[142]:=KlimaError[2].NapakaSenzorVlaznosti;
mind_bool[143]:=KlimaError[2].NapakaSenzorZunanjeTemp;
mind_bool[144]:=KlimaError[2].NapakaTSTemperaturaProstora;
mind_bool[145]:=KlimaError[2].NiTokaVVlazilcu;
mind_bool[146]:=KlimaError[2].NiVodeVVlazilcu;
mind_bool[147]:=KlimaError[2].NizekPritiskKompresor1;
mind_bool[148]:=KlimaError[2].NizekPritiskKompresor2;
mind_bool[149]:=KlimaError[2].NizkaTempPovratneVode;
mind_bool[150]:=KlimaError[2].NizkaTempVProstoru;
mind_bool[151]:=KlimaError[2].NizkaVlaznost;
mind_bool[152]:=KlimaError[2].PozarniAlarm;
mind_bool[153]:=KlimaError[2].StoppedByAlarms;
mind_bool[154]:=KlimaError[2].TermZascInVisokPritiskKompr1;
mind_bool[155]:=KlimaError[2].TermZascInVisokPritiskKompr2;
mind_bool[156]:=KlimaError[2].ThermalCutoutHeater1;
mind_bool[157]:=KlimaError[2].ThermalCutoutHeater2;
mind_bool[158]:=KlimaError[2].VentilatorNaMejiStevilaObrUr;
mind_bool[159]:=KlimaError[2].VisokaTempPovratneVode;
mind_bool[160]:=KlimaError[2].VisokaTempVProstoru;
mind_bool[161]:=KlimaError[2].VisokaVlaznost;
mind_bool[162]:=KlimaError[2].VisokPritiskVKrogu1;
mind_bool[163]:=KlimaError[2].VisokPritiskVKrogu2;
mind_bool[164]:=KlimaError[2].VisokTokVVlazilcu;
mind_bool[165]:=KlimaError[2].VlazilecnaMejiStevilaObrUr;
mind_bool[166]:=KlimaError[2].ZamasenFilter;
mind_bool[167]:=KlimaError[3].AlarmKompresor1;
mind_bool[168]:=KlimaError[3].AlarmKompresor2;
mind_bool[169]:=KlimaError[3].FaultyEprom;
mind_bool[170]:=KlimaError[3].FenThermalCutout;
mind_bool[171]:=KlimaError[3].GeneralAlarm;
mind_bool[172]:=KlimaError[3].Kompresor1naMejiStevilaObrUr;
mind_bool[173]:=KlimaError[3].Kompresor2naMejiStevilaObrUr;
mind_bool[174]:=KlimaError[3].Kond1FenThermalCutout;
mind_bool[175]:=KlimaError[3].Kond2FenThermalCutout;
mind_bool[176]:=KlimaError[3].NapakaPriPretokuVode;
mind_bool[177]:=KlimaError[3].NapakaPriPretokuZraka;
mind_bool[178]:=KlimaError[3].NapakaSenzorPovratVode;
mind_bool[179]:=KlimaError[3].NapakaSenzorPritiska;
mind_bool[180]:=KlimaError[3].NapakaSenzorTempIzpiha;
mind_bool[181]:=KlimaError[3].NapakaSenzorTempProstora;
mind_bool[182]:=KlimaError[3].NapakaSenzorVlaznosti;
mind_bool[183]:=KlimaError[3].NapakaSenzorZunanjeTemp;
mind_bool[184]:=KlimaError[3].NapakaTSTemperaturaProstora;
mind_bool[185]:=KlimaError[3].NiTokaVVlazilcu;
mind_bool[186]:=KlimaError[3].NiVodeVVlazilcu;
mind_bool[187]:=KlimaError[3].NizekPritiskKompresor1;
mind_bool[188]:=KlimaError[3].NizekPritiskKompresor2;
mind_bool[189]:=KlimaError[3].NizkaTempPovratneVode;
mind_bool[190]:=KlimaError[3].NizkaTempVProstoru;
mind_bool[191]:=KlimaError[3].NizkaVlaznost;
mind_bool[192]:=KlimaError[3].PozarniAlarm;
mind_bool[193]:=KlimaError[3].StoppedByAlarms;
mind_bool[194]:=KlimaError[3].TermZascInVisokPritiskKompr1;
mind_bool[195]:=KlimaError[3].TermZascInVisokPritiskKompr2;
mind_bool[196]:=KlimaError[3].ThermalCutoutHeater1;
mind_bool[197]:=KlimaError[3].ThermalCutoutHeater2;
mind_bool[198]:=KlimaError[3].VentilatorNaMejiStevilaObrUr;
mind_bool[199]:=KlimaError[3].VisokaTempPovratneVode;
mind_bool[200]:=KlimaError[3].VisokaTempVProstoru;
mind_bool[201]:=KlimaError[3].VisokaVlaznost;
mind_bool[202]:=KlimaError[3].VisokPritiskVKrogu1;
mind_bool[203]:=KlimaError[3].VisokPritiskVKrogu2;
mind_bool[204]:=KlimaError[3].VisokTokVVlazilcu;
mind_bool[205]:=KlimaError[3].VlazilecnaMejiStevilaObrUr;
mind_bool[206]:=KlimaError[3].ZamasenFilter;
mind_bool[207]:=KlimaError[4].AlarmKompresor1;
mind_bool[208]:=KlimaError[4].AlarmKompresor2;
mind_bool[209]:=KlimaError[4].FaultyEprom;
mind_bool[210]:=KlimaError[4].FenThermalCutout;
mind_bool[211]:=KlimaError[4].GeneralAlarm;
mind_bool[212]:=KlimaError[4].Kompresor1naMejiStevilaObrUr;
mind_bool[213]:=KlimaError[4].Kompresor2naMejiStevilaObrUr;
mind_bool[214]:=KlimaError[4].Kond1FenThermalCutout;
mind_bool[215]:=KlimaError[4].Kond2FenThermalCutout;
mind_bool[216]:=KlimaError[4].NapakaPriPretokuVode;
mind_bool[217]:=KlimaError[4].NapakaPriPretokuZraka;
mind_bool[218]:=KlimaError[4].NapakaSenzorPovratVode;
mind_bool[219]:=KlimaError[4].NapakaSenzorPritiska;
mind_bool[220]:=KlimaError[4].NapakaSenzorTempIzpiha;
mind_bool[221]:=KlimaError[4].NapakaSenzorTempProstora;
mind_bool[222]:=KlimaError[4].NapakaSenzorVlaznosti;
mind_bool[223]:=KlimaError[4].NapakaSenzorZunanjeTemp;
mind_bool[224]:=KlimaError[4].NapakaTSTemperaturaProstora;
mind_bool[225]:=KlimaError[4].NiTokaVVlazilcu;
mind_bool[226]:=KlimaError[4].NiVodeVVlazilcu;
mind_bool[227]:=KlimaError[4].NizekPritiskKompresor1;
mind_bool[228]:=KlimaError[4].NizekPritiskKompresor2;
mind_bool[229]:=KlimaError[4].NizkaTempPovratneVode;
mind_bool[230]:=KlimaError[4].NizkaTempVProstoru;
mind_bool[231]:=KlimaError[4].NizkaVlaznost;
mind_bool[232]:=KlimaError[4].PozarniAlarm;
mind_bool[233]:=KlimaError[4].StoppedByAlarms;
mind_bool[234]:=KlimaError[4].TermZascInVisokPritiskKompr1;
mind_bool[235]:=KlimaError[4].TermZascInVisokPritiskKompr2;
mind_bool[236]:=KlimaError[4].ThermalCutoutHeater1;
mind_bool[237]:=KlimaError[4].ThermalCutoutHeater2;
mind_bool[238]:=KlimaError[4].VentilatorNaMejiStevilaObrUr;
mind_bool[239]:=KlimaError[4].VisokaTempPovratneVode;
mind_bool[240]:=KlimaError[4].VisokaTempVProstoru;
mind_bool[241]:=KlimaError[4].VisokaVlaznost;
mind_bool[242]:=KlimaError[4].VisokPritiskVKrogu1;
mind_bool[243]:=KlimaError[4].VisokPritiskVKrogu2;
mind_bool[244]:=KlimaError[4].VisokTokVVlazilcu;
mind_bool[245]:=KlimaError[4].VlazilecnaMejiStevilaObrUr;
mind_bool[246]:=KlimaError[4].ZamasenFilter;
mind_bool[247]:=NacDelovanjaKlime1_2_Avtomatsko;
mind_bool[248]:=NacDelovanjaKlime3_4_Avtomatsko;
mind_bool[249]:=NapakaSenzorTemp1;
mind_bool[250]:=NapakaSenzorTemp2;
mind_bool[251]:=NapakaSenzorTemp3;
mind_bool[252]:=NapakaSenzorVlaga1;
mind_bool[253]:=NapakaSenzorVlaga2;
mind_bool[254]:=NapakaSenzorVlaga3;
mind_bool[255]:=NastaviCasNaKrmilniku;
mind_bool[256]:=NastavitevUreKrUspesna;
mind_bool[257]:=OpozoriloBaterijaPLC;
mind_bool[258]:=OsveziAlarmePanel;
mind_bool[259]:=RocniVklopKlima1;
mind_bool[260]:=RocniVklopKlima2;
mind_bool[261]:=RocniVklopKlima3;
mind_bool[262]:=RocniVklopKlima4;
mind_bool[263]:=SinhronizacijaPanelOK;
mind_bool[264]:=SinhronizirajCas_Panel;
mind_bool[265]:=SkupneNapakeNaprav_Klima1;
mind_bool[266]:=SkupneNapakeNaprav_Klima2;
mind_bool[267]:=SkupneNapakeNaprav_Klima3;
mind_bool[268]:=SkupneNapakeNaprav_Klima4;
mind_bool[269]:=SkupneNapakeNaprav_Komunikacija;
mind_bool[270]:=SkupneNapakeNaprav_TempVlaga;
mind_bool[271]:=StanjeKlimat1_Delovanje;
mind_bool[272]:=StanjeKlimat2_Delovanje;
mind_bool[273]:=StanjeKlimat3_Delovanje;
mind_bool[274]:=StanjeKlimat4_Delovanje;
mind_bool[275]:=StanjeUPSKrmOmara_BaterijskiNacin;
mind_bool[276]:=StanjeUPSKrmOmara_Polnjenje;
mind_bool[277]:=UserLoggedIn;
mind_bool[278]:=XVH_AlarmOn;
mind_bool[279]:=Klimat1_Vklop;
mind_bool[280]:=Klimat2_Vklop;
mind_bool[281]:=Klimat3_Vklop;
mind_bool[282]:=Klimat4_Vklop;
mind_bool[283]:=ErrorComKlima[1].Error;
mind_bool[284]:=ErrorComKlima[2].Error;
mind_bool[285]:=ErrorComKlima[3].Error;
mind_bool[286]:=ErrCommScada2;
mind_bool[287]:=ComSCADA2;
mind_bool[288]:=ComSCADA3;
mind_bool[289]:=AlarmTempTIA4Previsoka;
mind_bool[290]:=AlarmTempTIA5Previsoka;
mind_bool[291]:=NapakaSenzorTemp4;
mind_bool[292]:=NapakaSenzorTemp5;
mind_bool[293]:=NapakaSenzorVlaga4;
mind_bool[294]:=NapakaSenzorVlaga5;
mind_bool[295]:=AlarmTempTIA124Previsoka;
mind_bool[296]:=AlarmTempTIA35Previsoka;
(*Branje INT*)
(**)
mind[0]:=DatumCas.Dan;
mind[1]:=DatumCas.Leto;
mind[2]:=DatumCas.Leto2;
mind[3]:=DatumCas.Mesec;
mind[4]:=DatumCas.Minuta;
mind[5]:=DatumCas.Sekunda;
mind[6]:=DatumCas.Ura;
mind[7]:=ErrorComKlima[4].Status;
mind[8]:=Klima[1].GrelecStatus;
mind[9]:=Klima[1].IzhodniVentStatus;
mind[10]:=Klima[1].KompresorStatus;
mind[11]:=Klima[1].VlazilecStatus;
mind[12]:=Klima[2].GrelecStatus;
mind[13]:=Klima[2].IzhodniVentStatus;
mind[14]:=Klima[2].KompresorStatus;
mind[15]:=Klima[2].VlazilecStatus;
mind[16]:=Klima[3].GrelecStatus;
mind[17]:=Klima[3].IzhodniVentStatus;
mind[18]:=Klima[3].KompresorStatus;
mind[19]:=Klima[3].VlazilecStatus;
mind[20]:=Klima[4].GrelecStatus;
mind[21]:=Klima[4].IzhodniVentStatus;
mind[22]:=Klima[4].KompresorStatus;
mind[23]:=Klima[4].VlazilecStatus;
mind[24]:=StUrZaPreklopKlim1_2;
mind[25]:=StUrZaPreklopKlim3_4;
mind[26]:=UPSstatus_Prikaz_PanelSCADA;
mind[27]:=UserCurrentLevel;
mind[28]:=ErrorComKlima[1].Code[0];
mind[29]:=ErrorComKlima[1].Code[10];
mind[30]:=ErrorComKlima[1].Code[11];
mind[31]:=ErrorComKlima[1].Code[12];
mind[32]:=ErrorComKlima[1].Code[13];
mind[33]:=ErrorComKlima[1].Code[14];
mind[34]:=ErrorComKlima[1].Code[15];
mind[35]:=ErrorComKlima[1].Code[1];
mind[36]:=ErrorComKlima[1].Code[2];
mind[37]:=ErrorComKlima[1].Code[3];
mind[38]:=ErrorComKlima[1].Code[4];
mind[39]:=ErrorComKlima[1].Code[5];
mind[40]:=ErrorComKlima[1].Code[6];
mind[41]:=ErrorComKlima[1].Code[7];
mind[42]:=ErrorComKlima[1].Code[8];
mind[43]:=ErrorComKlima[1].Code[9];
mind[44]:=ErrorComKlima[1].Status;
mind[45]:=ErrorComKlima[2].Code[0];
mind[46]:=ErrorComKlima[2].Code[10];
mind[47]:=ErrorComKlima[2].Code[11];
mind[48]:=ErrorComKlima[2].Code[12];
mind[49]:=ErrorComKlima[2].Code[13];
mind[50]:=ErrorComKlima[2].Code[14];
mind[51]:=ErrorComKlima[2].Code[15];
mind[52]:=ErrorComKlima[2].Code[1];
mind[53]:=ErrorComKlima[2].Code[2];
mind[54]:=ErrorComKlima[2].Code[3];
mind[55]:=ErrorComKlima[2].Code[4];
mind[56]:=ErrorComKlima[2].Code[5];
mind[57]:=ErrorComKlima[2].Code[6];
mind[58]:=ErrorComKlima[2].Code[7];
mind[59]:=ErrorComKlima[2].Code[8];
mind[60]:=ErrorComKlima[2].Code[9];
mind[61]:=ErrorComKlima[2].Status;
mind[62]:=ErrorComKlima[3].Code[0];
mind[63]:=ErrorComKlima[3].Code[10];
mind[64]:=ErrorComKlima[3].Code[11];
mind[65]:=ErrorComKlima[3].Code[12];
mind[66]:=ErrorComKlima[3].Code[13];
mind[67]:=ErrorComKlima[3].Code[14];
mind[68]:=ErrorComKlima[3].Code[15];
mind[69]:=ErrorComKlima[3].Code[1];
mind[70]:=ErrorComKlima[3].Code[2];
mind[71]:=ErrorComKlima[3].Code[3];
mind[72]:=ErrorComKlima[3].Code[4];
mind[73]:=ErrorComKlima[3].Code[5];
mind[74]:=ErrorComKlima[3].Code[6];
mind[75]:=ErrorComKlima[3].Code[7];
mind[76]:=ErrorComKlima[3].Code[8];
mind[77]:=ErrorComKlima[3].Code[9];
mind[78]:=ErrorComKlima[3].Status;
mind[79]:=ErrorComKlima[4].Code[0];
mind[80]:=ErrorComKlima[4].Code[10];
mind[81]:=ErrorComKlima[4].Code[11];
mind[82]:=ErrorComKlima[4].Code[12];
mind[83]:=ErrorComKlima[4].Code[13];
mind[84]:=ErrorComKlima[4].Code[14];
mind[85]:=ErrorComKlima[4].Code[15];
mind[86]:=ErrorComKlima[4].Code[1];
mind[87]:=ErrorComKlima[4].Code[2];
mind[88]:=ErrorComKlima[4].Code[3];
mind[89]:=ErrorComKlima[4].Code[4];
mind[90]:=ErrorComKlima[4].Code[5];
mind[91]:=ErrorComKlima[4].Code[6];
mind[92]:=ErrorComKlima[4].Code[7];
mind[93]:=ErrorComKlima[4].Code[8];
mind[94]:=ErrorComKlima[4].Code[9];
mind[95]:=kom_nast_cas_izpada;
(*Branje UINT*)
(**)
(*Branje LONG*)
(**)
(*Branje REAL*)
(**)
Read_Real(rVar:=AktualniSetPointTemp1_2,lo:=4000,hi:=4001);
Read_Real(rVar:=AktualniSetPointTemp3_4,lo:=4002,hi:=4003);
Read_Real(rVar:=Klima1ure,lo:=4004,hi:=4005);
Read_Real(rVar:=Klima2ure,lo:=4006,hi:=4007);
Read_Real(rVar:=Klima3ure,lo:=4008,hi:=4009);
Read_Real(rVar:=Klima4ure,lo:=4010,hi:=4011);
Read_Real(rVar:=Klima[1].NastTempProstora,lo:=4012,hi:=4013);
Read_Real(rVar:=Klima[1].NastVlaznost,lo:=4014,hi:=4015);
Read_Real(rVar:=Klima[1].ObratovalneUre,lo:=4016,hi:=4017);
Read_Real(rVar:=Klima[1].TemperaturaProstora,lo:=4018,hi:=4019);
Read_Real(rVar:=Klima[1].VlaznostProstora,lo:=4020,hi:=4021);
Read_Real(rVar:=Klima[2].NastTempProstora,lo:=4022,hi:=4023);
Read_Real(rVar:=Klima[2].NastVlaznost,lo:=4024,hi:=4025);
Read_Real(rVar:=Klima[2].ObratovalneUre,lo:=4026,hi:=4027);
Read_Real(rVar:=Klima[2].TemperaturaProstora,lo:=4028,hi:=4029);
Read_Real(rVar:=Klima[2].VlaznostProstora,lo:=4030,hi:=4031);
Read_Real(rVar:=Klima[3].NastTempProstora,lo:=4032,hi:=4033);
Read_Real(rVar:=Klima[3].NastVlaznost,lo:=4034,hi:=4035);
Read_Real(rVar:=Klima[3].ObratovalneUre,lo:=4036,hi:=4037);
Read_Real(rVar:=Klima[3].TemperaturaProstora,lo:=4038,hi:=4039);
Read_Real(rVar:=Klima[3].VlaznostProstora,lo:=4040,hi:=4041);
Read_Real(rVar:=Klima[4].NastTempProstora,lo:=4042,hi:=4043);
Read_Real(rVar:=Klima[4].NastVlaznost,lo:=4044,hi:=4045);
Read_Real(rVar:=Klima[4].ObratovalneUre,lo:=4046,hi:=4047);
Read_Real(rVar:=Klima[4].TemperaturaProstora,lo:=4048,hi:=4049);
Read_Real(rVar:=Klima[4].VlaznostProstora,lo:=4050,hi:=4051);
Read_Real(rVar:=SKTemp1,lo:=4052,hi:=4053);
Read_Real(rVar:=SKTemp2,lo:=4054,hi:=4055);
Read_Real(rVar:=SKTemp3,lo:=4056,hi:=4057);
Read_Real(rVar:=SKVlaga1,lo:=4058,hi:=4059);
Read_Real(rVar:=SKVlaga2,lo:=4060,hi:=4061);
Read_Real(rVar:=SKVlaga3,lo:=4062,hi:=4063);
Read_Real(rVar:=TempZaAlarm1_2,lo:=4064,hi:=4065);
Read_Real(rVar:=TempZaAlarm3_4,lo:=4066,hi:=4067);
Read_Real(rVar:=TempZaAlarmTIA1,lo:=4068,hi:=4069);
Read_Real(rVar:=TempZaAlarmTIA2,lo:=4070,hi:=4071);
Read_Real(rVar:=TempZaAlarmTIA3,lo:=4072,hi:=4073);
Read_Real(rVar:=TempZaVklopObehKlim1_2,lo:=4074,hi:=4075);
Read_Real(rVar:=TempZaVklopObehKlim3_4,lo:=4076,hi:=4077);
Read_Real(rVar:=SKTemp4,lo:=4078,hi:=4079);
Read_Real(rVar:=SKTemp5,lo:=4080,hi:=4081);
Read_Real(rVar:=SKVlaga4,lo:=4082,hi:=4083);
Read_Real(rVar:=SKVlaga5,lo:=4084,hi:=4085);
Read_Real(rVar:=TempZaAlarmTIA4,lo:=4086,hi:=4087);
Read_Real(rVar:=TempZaAlarmTIA5,lo:=4088,hi:=4089);
Read_Real(rVar:=SKTempServSoba1Povpr,lo:=4090,hi:=4091);
Read_Real(rVar:=SKTempServSoba2Povpr,lo:=4092,hi:=4093);
Read_Real(rVar:=TempZaAlarmTIA124,lo:=4094,hi:=4095);
Read_Real(rVar:=TempZaAlarmTIA35,lo:=4096,hi:=4097);
(*Branje STRING*)
(**)
Read_String(sVar:=UserName,start:=5000);
Read_String(sVar:=Date_Time[0],start:=5015);
Read_String(sVar:=Date_Time[1],start:=5030);
Read_String(sVar:=Date_Time[2],start:=5045);
Read_String(sVar:=Date_Time[3],start:=5060);
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Bool : BOOL
VAR_INPUT
index: INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje BOOL*)
(**)
0:AlarmKlimat1_Napaka:=Bit_0;
1:AlarmKlimat2_Napaka:=Bit_0;
2:AlarmKlimat3_Napaka:=Bit_0;
3:AlarmKlimat4_Napaka:=Bit_0;
4:AlarmLAH1_RazlitjeVode:=Bit_0;
5:AlarmLAH2_RazlitjeVode:=Bit_0;
6:AlarmSinhronizacijaNOK:=Bit_0;
7:AlarmTempTIA1Previsoka:=Bit_0;
8:AlarmTempTIA2Previsoka:=Bit_0;
9:AlarmTempTIA3Previsoka:=Bit_0;
10:AlarmTSTemp1Previsoka:=Bit_0;
11:AlarmTSTemp3Previsoka:=Bit_0;
12:AlarmUPSKrmOmara_Alarm:=Bit_0;
13:ComSCADA:=Bit_0;
14:ComSCADA1:=Bit_0;
15:ErrComKlima[1]:=Bit_0;
16:ErrComKlima[2]:=Bit_0;
17:ErrComKlima[3]:=Bit_0;
18:ErrComKlima[4]:=Bit_0;
19:ErrCommScada:=Bit_0;
20:ErrComPanelPLC:=Bit_0;
21:ErrComPort2:=Bit_0;
22:ErrorComKlima[4].Error:=Bit_0;
23:Klima1_Onemogocena:=Bit_0;
24:Klima2_Onemogocena:=Bit_0;
25:Klima3_Onemogocena:=Bit_0;
26:Klima4_Onemogocena:=Bit_0;
27:Klima[1].Deluje:=Bit_0;
28:Klima[1].EnergySaving:=Bit_0;
29:Klima[1].Napaka:=Bit_0;
30:Klima[1].OnOffEnablingBySupervisor:=Bit_0;
31:Klima[1].Razvlazevanje:=Bit_0;
32:Klima[1].RemoteOFFtoOutput:=Bit_0;
33:Klima[1].RemoteOnOff:=Bit_0;
34:Klima[1].RocniIzklop:=Bit_0;
35:Klima[1].SenzorjiStatus:=Bit_0;
36:Klima[1].UnitOnOff:=Bit_0;
37:Klima[1].VentilGretjeOdpiranje:=Bit_0;
38:Klima[1].VentilGretjeZapiranje:=Bit_0;
39:Klima[1].VentilHlajenjeOdpiranje:=Bit_0;
40:Klima[1].VentilHlajenjeZapiranje:=Bit_0;
41:Klima[1].Vlazenje:=Bit_0;
42:Klima[2].Deluje:=Bit_0;
43:Klima[2].EnergySaving:=Bit_0;
44:Klima[2].Napaka:=Bit_0;
45:Klima[2].OnOffEnablingBySupervisor:=Bit_0;
46:Klima[2].Razvlazevanje:=Bit_0;
47:Klima[2].RemoteOFFtoOutput:=Bit_0;
48:Klima[2].RemoteOnOff:=Bit_0;
49:Klima[2].RocniIzklop:=Bit_0;
50:Klima[2].SenzorjiStatus:=Bit_0;
51:Klima[2].UnitOnOff:=Bit_0;
52:Klima[2].VentilGretjeOdpiranje:=Bit_0;
53:Klima[2].VentilGretjeZapiranje:=Bit_0;
54:Klima[2].VentilHlajenjeOdpiranje:=Bit_0;
55:Klima[2].VentilHlajenjeZapiranje:=Bit_0;
56:Klima[2].Vlazenje:=Bit_0;
57:Klima[3].Deluje:=Bit_0;
58:Klima[3].EnergySaving:=Bit_0;
59:Klima[3].Napaka:=Bit_0;
60:Klima[3].OnOffEnablingBySupervisor:=Bit_0;
61:Klima[3].Razvlazevanje:=Bit_0;
62:Klima[3].RemoteOFFtoOutput:=Bit_0;
63:Klima[3].RemoteOnOff:=Bit_0;
64:Klima[3].RocniIzklop:=Bit_0;
65:Klima[3].SenzorjiStatus:=Bit_0;
66:Klima[3].UnitOnOff:=Bit_0;
67:Klima[3].VentilGretjeOdpiranje:=Bit_0;
68:Klima[3].VentilGretjeZapiranje:=Bit_0;
69:Klima[3].VentilHlajenjeOdpiranje:=Bit_0;
70:Klima[3].VentilHlajenjeZapiranje:=Bit_0;
71:Klima[3].Vlazenje:=Bit_0;
72:Klima[4].Deluje:=Bit_0;
73:Klima[4].EnergySaving:=Bit_0;
74:Klima[4].Napaka:=Bit_0;
75:Klima[4].OnOffEnablingBySupervisor:=Bit_0;
76:Klima[4].Razvlazevanje:=Bit_0;
77:Klima[4].RemoteOFFtoOutput:=Bit_0;
78:Klima[4].RemoteOnOff:=Bit_0;
79:Klima[4].RocniIzklop:=Bit_0;
80:Klima[4].SenzorjiStatus:=Bit_0;
81:Klima[4].UnitOnOff:=Bit_0;
82:Klima[4].VentilGretjeOdpiranje:=Bit_0;
83:Klima[4].VentilGretjeZapiranje:=Bit_0;
84:Klima[4].VentilHlajenjeOdpiranje:=Bit_0;
85:Klima[4].VentilHlajenjeZapiranje:=Bit_0;
86:Klima[4].Vlazenje:=Bit_0;
87:KlimaError[1].AlarmKompresor1:=Bit_0;
88:KlimaError[1].AlarmKompresor2:=Bit_0;
89:KlimaError[1].FaultyEprom:=Bit_0;
90:KlimaError[1].FenThermalCutout:=Bit_0;
91:KlimaError[1].GeneralAlarm:=Bit_0;
92:KlimaError[1].Kompresor1naMejiStevilaObrUr:=Bit_0;
93:KlimaError[1].Kompresor2naMejiStevilaObrUr:=Bit_0;
94:KlimaError[1].Kond1FenThermalCutout:=Bit_0;
95:KlimaError[1].Kond2FenThermalCutout:=Bit_0;
96:KlimaError[1].NapakaPriPretokuVode:=Bit_0;
97:KlimaError[1].NapakaPriPretokuZraka:=Bit_0;
98:KlimaError[1].NapakaSenzorPovratVode:=Bit_0;
99:KlimaError[1].NapakaSenzorPritiska:=Bit_0;
100:KlimaError[1].NapakaSenzorTempIzpiha:=Bit_0;
101:KlimaError[1].NapakaSenzorTempProstora:=Bit_0;
102:KlimaError[1].NapakaSenzorVlaznosti:=Bit_0;
103:KlimaError[1].NapakaSenzorZunanjeTemp:=Bit_0;
104:KlimaError[1].NapakaTSTemperaturaProstora:=Bit_0;
105:KlimaError[1].NiTokaVVlazilcu:=Bit_0;
106:KlimaError[1].NiVodeVVlazilcu:=Bit_0;
107:KlimaError[1].NizekPritiskKompresor1:=Bit_0;
108:KlimaError[1].NizekPritiskKompresor2:=Bit_0;
109:KlimaError[1].NizkaTempPovratneVode:=Bit_0;
110:KlimaError[1].NizkaTempVProstoru:=Bit_0;
111:KlimaError[1].NizkaVlaznost:=Bit_0;
112:KlimaError[1].PozarniAlarm:=Bit_0;
113:KlimaError[1].StoppedByAlarms:=Bit_0;
114:KlimaError[1].TermZascInVisokPritiskKompr1:=Bit_0;
115:KlimaError[1].TermZascInVisokPritiskKompr2:=Bit_0;
116:KlimaError[1].ThermalCutoutHeater1:=Bit_0;
117:KlimaError[1].ThermalCutoutHeater2:=Bit_0;
118:KlimaError[1].VentilatorNaMejiStevilaObrUr:=Bit_0;
119:KlimaError[1].VisokaTempPovratneVode:=Bit_0;
120:KlimaError[1].VisokaTempVProstoru:=Bit_0;
121:KlimaError[1].VisokaVlaznost:=Bit_0;
122:KlimaError[1].VisokPritiskVKrogu1:=Bit_0;
123:KlimaError[1].VisokPritiskVKrogu2:=Bit_0;
124:KlimaError[1].VisokTokVVlazilcu:=Bit_0;
125:KlimaError[1].VlazilecnaMejiStevilaObrUr:=Bit_0;
126:KlimaError[1].ZamasenFilter:=Bit_0;
127:KlimaError[2].AlarmKompresor1:=Bit_0;
128:KlimaError[2].AlarmKompresor2:=Bit_0;
129:KlimaError[2].FaultyEprom:=Bit_0;
130:KlimaError[2].FenThermalCutout:=Bit_0;
131:KlimaError[2].GeneralAlarm:=Bit_0;
132:KlimaError[2].Kompresor1naMejiStevilaObrUr:=Bit_0;
133:KlimaError[2].Kompresor2naMejiStevilaObrUr:=Bit_0;
134:KlimaError[2].Kond1FenThermalCutout:=Bit_0;
135:KlimaError[2].Kond2FenThermalCutout:=Bit_0;
136:KlimaError[2].NapakaPriPretokuVode:=Bit_0;
137:KlimaError[2].NapakaPriPretokuZraka:=Bit_0;
138:KlimaError[2].NapakaSenzorPovratVode:=Bit_0;
139:KlimaError[2].NapakaSenzorPritiska:=Bit_0;
140:KlimaError[2].NapakaSenzorTempIzpiha:=Bit_0;
141:KlimaError[2].NapakaSenzorTempProstora:=Bit_0;
142:KlimaError[2].NapakaSenzorVlaznosti:=Bit_0;
143:KlimaError[2].NapakaSenzorZunanjeTemp:=Bit_0;
144:KlimaError[2].NapakaTSTemperaturaProstora:=Bit_0;
145:KlimaError[2].NiTokaVVlazilcu:=Bit_0;
146:KlimaError[2].NiVodeVVlazilcu:=Bit_0;
147:KlimaError[2].NizekPritiskKompresor1:=Bit_0;
148:KlimaError[2].NizekPritiskKompresor2:=Bit_0;
149:KlimaError[2].NizkaTempPovratneVode:=Bit_0;
150:KlimaError[2].NizkaTempVProstoru:=Bit_0;
151:KlimaError[2].NizkaVlaznost:=Bit_0;
152:KlimaError[2].PozarniAlarm:=Bit_0;
153:KlimaError[2].StoppedByAlarms:=Bit_0;
154:KlimaError[2].TermZascInVisokPritiskKompr1:=Bit_0;
155:KlimaError[2].TermZascInVisokPritiskKompr2:=Bit_0;
156:KlimaError[2].ThermalCutoutHeater1:=Bit_0;
157:KlimaError[2].ThermalCutoutHeater2:=Bit_0;
158:KlimaError[2].VentilatorNaMejiStevilaObrUr:=Bit_0;
159:KlimaError[2].VisokaTempPovratneVode:=Bit_0;
160:KlimaError[2].VisokaTempVProstoru:=Bit_0;
161:KlimaError[2].VisokaVlaznost:=Bit_0;
162:KlimaError[2].VisokPritiskVKrogu1:=Bit_0;
163:KlimaError[2].VisokPritiskVKrogu2:=Bit_0;
164:KlimaError[2].VisokTokVVlazilcu:=Bit_0;
165:KlimaError[2].VlazilecnaMejiStevilaObrUr:=Bit_0;
166:KlimaError[2].ZamasenFilter:=Bit_0;
167:KlimaError[3].AlarmKompresor1:=Bit_0;
168:KlimaError[3].AlarmKompresor2:=Bit_0;
169:KlimaError[3].FaultyEprom:=Bit_0;
170:KlimaError[3].FenThermalCutout:=Bit_0;
171:KlimaError[3].GeneralAlarm:=Bit_0;
172:KlimaError[3].Kompresor1naMejiStevilaObrUr:=Bit_0;
173:KlimaError[3].Kompresor2naMejiStevilaObrUr:=Bit_0;
174:KlimaError[3].Kond1FenThermalCutout:=Bit_0;
175:KlimaError[3].Kond2FenThermalCutout:=Bit_0;
176:KlimaError[3].NapakaPriPretokuVode:=Bit_0;
177:KlimaError[3].NapakaPriPretokuZraka:=Bit_0;
178:KlimaError[3].NapakaSenzorPovratVode:=Bit_0;
179:KlimaError[3].NapakaSenzorPritiska:=Bit_0;
180:KlimaError[3].NapakaSenzorTempIzpiha:=Bit_0;
181:KlimaError[3].NapakaSenzorTempProstora:=Bit_0;
182:KlimaError[3].NapakaSenzorVlaznosti:=Bit_0;
183:KlimaError[3].NapakaSenzorZunanjeTemp:=Bit_0;
184:KlimaError[3].NapakaTSTemperaturaProstora:=Bit_0;
185:KlimaError[3].NiTokaVVlazilcu:=Bit_0;
186:KlimaError[3].NiVodeVVlazilcu:=Bit_0;
187:KlimaError[3].NizekPritiskKompresor1:=Bit_0;
188:KlimaError[3].NizekPritiskKompresor2:=Bit_0;
189:KlimaError[3].NizkaTempPovratneVode:=Bit_0;
190:KlimaError[3].NizkaTempVProstoru:=Bit_0;
191:KlimaError[3].NizkaVlaznost:=Bit_0;
192:KlimaError[3].PozarniAlarm:=Bit_0;
193:KlimaError[3].StoppedByAlarms:=Bit_0;
194:KlimaError[3].TermZascInVisokPritiskKompr1:=Bit_0;
195:KlimaError[3].TermZascInVisokPritiskKompr2:=Bit_0;
196:KlimaError[3].ThermalCutoutHeater1:=Bit_0;
197:KlimaError[3].ThermalCutoutHeater2:=Bit_0;
198:KlimaError[3].VentilatorNaMejiStevilaObrUr:=Bit_0;
199:KlimaError[3].VisokaTempPovratneVode:=Bit_0;
200:KlimaError[3].VisokaTempVProstoru:=Bit_0;
201:KlimaError[3].VisokaVlaznost:=Bit_0;
202:KlimaError[3].VisokPritiskVKrogu1:=Bit_0;
203:KlimaError[3].VisokPritiskVKrogu2:=Bit_0;
204:KlimaError[3].VisokTokVVlazilcu:=Bit_0;
205:KlimaError[3].VlazilecnaMejiStevilaObrUr:=Bit_0;
206:KlimaError[3].ZamasenFilter:=Bit_0;
207:KlimaError[4].AlarmKompresor1:=Bit_0;
208:KlimaError[4].AlarmKompresor2:=Bit_0;
209:KlimaError[4].FaultyEprom:=Bit_0;
210:KlimaError[4].FenThermalCutout:=Bit_0;
211:KlimaError[4].GeneralAlarm:=Bit_0;
212:KlimaError[4].Kompresor1naMejiStevilaObrUr:=Bit_0;
213:KlimaError[4].Kompresor2naMejiStevilaObrUr:=Bit_0;
214:KlimaError[4].Kond1FenThermalCutout:=Bit_0;
215:KlimaError[4].Kond2FenThermalCutout:=Bit_0;
216:KlimaError[4].NapakaPriPretokuVode:=Bit_0;
217:KlimaError[4].NapakaPriPretokuZraka:=Bit_0;
218:KlimaError[4].NapakaSenzorPovratVode:=Bit_0;
219:KlimaError[4].NapakaSenzorPritiska:=Bit_0;
220:KlimaError[4].NapakaSenzorTempIzpiha:=Bit_0;
221:KlimaError[4].NapakaSenzorTempProstora:=Bit_0;
222:KlimaError[4].NapakaSenzorVlaznosti:=Bit_0;
223:KlimaError[4].NapakaSenzorZunanjeTemp:=Bit_0;
224:KlimaError[4].NapakaTSTemperaturaProstora:=Bit_0;
225:KlimaError[4].NiTokaVVlazilcu:=Bit_0;
226:KlimaError[4].NiVodeVVlazilcu:=Bit_0;
227:KlimaError[4].NizekPritiskKompresor1:=Bit_0;
228:KlimaError[4].NizekPritiskKompresor2:=Bit_0;
229:KlimaError[4].NizkaTempPovratneVode:=Bit_0;
230:KlimaError[4].NizkaTempVProstoru:=Bit_0;
231:KlimaError[4].NizkaVlaznost:=Bit_0;
232:KlimaError[4].PozarniAlarm:=Bit_0;
233:KlimaError[4].StoppedByAlarms:=Bit_0;
234:KlimaError[4].TermZascInVisokPritiskKompr1:=Bit_0;
235:KlimaError[4].TermZascInVisokPritiskKompr2:=Bit_0;
236:KlimaError[4].ThermalCutoutHeater1:=Bit_0;
237:KlimaError[4].ThermalCutoutHeater2:=Bit_0;
238:KlimaError[4].VentilatorNaMejiStevilaObrUr:=Bit_0;
239:KlimaError[4].VisokaTempPovratneVode:=Bit_0;
240:KlimaError[4].VisokaTempVProstoru:=Bit_0;
241:KlimaError[4].VisokaVlaznost:=Bit_0;
242:KlimaError[4].VisokPritiskVKrogu1:=Bit_0;
243:KlimaError[4].VisokPritiskVKrogu2:=Bit_0;
244:KlimaError[4].VisokTokVVlazilcu:=Bit_0;
245:KlimaError[4].VlazilecnaMejiStevilaObrUr:=Bit_0;
246:KlimaError[4].ZamasenFilter:=Bit_0;
247:NacDelovanjaKlime1_2_Avtomatsko:=Bit_0;
248:NacDelovanjaKlime3_4_Avtomatsko:=Bit_0;
249:NapakaSenzorTemp1:=Bit_0;
250:NapakaSenzorTemp2:=Bit_0;
251:NapakaSenzorTemp3:=Bit_0;
252:NapakaSenzorVlaga1:=Bit_0;
253:NapakaSenzorVlaga2:=Bit_0;
254:NapakaSenzorVlaga3:=Bit_0;
255:NastaviCasNaKrmilniku:=Bit_0;
256:NastavitevUreKrUspesna:=Bit_0;
257:OpozoriloBaterijaPLC:=Bit_0;
258:OsveziAlarmePanel:=Bit_0;
259:RocniVklopKlima1:=Bit_0;
260:RocniVklopKlima2:=Bit_0;
261:RocniVklopKlima3:=Bit_0;
262:RocniVklopKlima4:=Bit_0;
263:SinhronizacijaPanelOK:=Bit_0;
264:SinhronizirajCas_Panel:=Bit_0;
265:SkupneNapakeNaprav_Klima1:=Bit_0;
266:SkupneNapakeNaprav_Klima2:=Bit_0;
267:SkupneNapakeNaprav_Klima3:=Bit_0;
268:SkupneNapakeNaprav_Klima4:=Bit_0;
269:SkupneNapakeNaprav_Komunikacija:=Bit_0;
270:SkupneNapakeNaprav_TempVlaga:=Bit_0;
271:StanjeKlimat1_Delovanje:=Bit_0;
272:StanjeKlimat2_Delovanje:=Bit_0;
273:StanjeKlimat3_Delovanje:=Bit_0;
274:StanjeKlimat4_Delovanje:=Bit_0;
275:StanjeUPSKrmOmara_BaterijskiNacin:=Bit_0;
276:StanjeUPSKrmOmara_Polnjenje:=Bit_0;
277:UserLoggedIn:=Bit_0;
278:XVH_AlarmOn:=Bit_0;
279:Klimat1_Vklop:=Bit_0;
280:Klimat2_Vklop:=Bit_0;
281:Klimat3_Vklop:=Bit_0;
282:Klimat4_Vklop:=Bit_0;
283:ErrorComKlima[1].Error:=Bit_0;
284:ErrorComKlima[2].Error:=Bit_0;
285:ErrorComKlima[3].Error:=Bit_0;
286:ErrCommScada2:=Bit_0;
287:ComSCADA2:=Bit_0;
288:ComSCADA3:=Bit_0;
289:AlarmTempTIA4Previsoka:=Bit_0;
290:AlarmTempTIA5Previsoka:=Bit_0;
291:NapakaSenzorTemp4:=Bit_0;
292:NapakaSenzorTemp5:=Bit_0;
293:NapakaSenzorVlaga4:=Bit_0;
294:NapakaSenzorVlaga5:=Bit_0;
295:AlarmTempTIA124Previsoka:=Bit_0;
296:AlarmTempTIA35Previsoka:=Bit_0;
(*BOOL*)
END_CASE
END_FUNCTION
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_dWord : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje LONG*)
(**)
(*Pisanje REAL*)
(**)
4001:AktualniSetPointTemp1_2:=Real_0;
4003:AktualniSetPointTemp3_4:=Real_0;
4005:Klima1ure:=Real_0;
4007:Klima2ure:=Real_0;
4009:Klima3ure:=Real_0;
4011:Klima4ure:=Real_0;
4013:Klima[1].NastTempProstora:=Real_0;
4015:Klima[1].NastVlaznost:=Real_0;
4017:Klima[1].ObratovalneUre:=Real_0;
4019:Klima[1].TemperaturaProstora:=Real_0;
4021:Klima[1].VlaznostProstora:=Real_0;
4023:Klima[2].NastTempProstora:=Real_0;
4025:Klima[2].NastVlaznost:=Real_0;
4027:Klima[2].ObratovalneUre:=Real_0;
4029:Klima[2].TemperaturaProstora:=Real_0;
4031:Klima[2].VlaznostProstora:=Real_0;
4033:Klima[3].NastTempProstora:=Real_0;
4035:Klima[3].NastVlaznost:=Real_0;
4037:Klima[3].ObratovalneUre:=Real_0;
4039:Klima[3].TemperaturaProstora:=Real_0;
4041:Klima[3].VlaznostProstora:=Real_0;
4043:Klima[4].NastTempProstora:=Real_0;
4045:Klima[4].NastVlaznost:=Real_0;
4047:Klima[4].ObratovalneUre:=Real_0;
4049:Klima[4].TemperaturaProstora:=Real_0;
4051:Klima[4].VlaznostProstora:=Real_0;
4053:SKTemp1:=Real_0;
4055:SKTemp2:=Real_0;
4057:SKTemp3:=Real_0;
4059:SKVlaga1:=Real_0;
4061:SKVlaga2:=Real_0;
4063:SKVlaga3:=Real_0;
4065:TempZaAlarm1_2:=Real_0;
4067:TempZaAlarm3_4:=Real_0;
4069:TempZaAlarmTIA1:=Real_0;
4071:TempZaAlarmTIA2:=Real_0;
4073:TempZaAlarmTIA3:=Real_0;
4075:TempZaVklopObehKlim1_2:=Real_0;
4077:TempZaVklopObehKlim3_4:=Real_0;
4079:SKTemp4:=Real_0;
4081:SKTemp5:=Real_0;
4083:SKVlaga4:=Real_0;
4085:SKVlaga5:=Real_0;
4087:TempZaAlarmTIA4:=Real_0;
4089:TempZaAlarmTIA5:=Real_0;
4091:SKTempServSoba1Povpr:=Real_0;
4093:SKTempServSoba2Povpr:=Real_0;
4095:TempZaAlarmTIA124:=Real_0;
4097:TempZaAlarmTIA35:=Real_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_String : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje STRING*)
(**)
5000:UserName:=String_0;
5015:Date_Time[0]:=String_0;
5030:Date_Time[1]:=String_0;
5045:Date_Time[2]:=String_0;
5060:Date_Time[3]:=String_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Word : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje INT*)
(**)
0:DatumCas.Dan:=Byte_0;
1:DatumCas.Leto:=Byte_0;
2:DatumCas.Leto2:=Word_01;
3:DatumCas.Mesec:=Byte_0;
4:DatumCas.Minuta:=Byte_0;
5:DatumCas.Sekunda:=Byte_0;
6:DatumCas.Ura:=Byte_0;
7:ErrorComKlima[4].Status:=Word_01;
8:Klima[1].GrelecStatus:=Byte_0;
9:Klima[1].IzhodniVentStatus:=Byte_0;
10:Klima[1].KompresorStatus:=Byte_0;
11:Klima[1].VlazilecStatus:=Byte_0;
12:Klima[2].GrelecStatus:=Byte_0;
13:Klima[2].IzhodniVentStatus:=Byte_0;
14:Klima[2].KompresorStatus:=Byte_0;
15:Klima[2].VlazilecStatus:=Byte_0;
16:Klima[3].GrelecStatus:=Byte_0;
17:Klima[3].IzhodniVentStatus:=Byte_0;
18:Klima[3].KompresorStatus:=Byte_0;
19:Klima[3].VlazilecStatus:=Byte_0;
20:Klima[4].GrelecStatus:=Byte_0;
21:Klima[4].IzhodniVentStatus:=Byte_0;
22:Klima[4].KompresorStatus:=Byte_0;
23:Klima[4].VlazilecStatus:=Byte_0;
24:StUrZaPreklopKlim1_2:=Word_01;
25:StUrZaPreklopKlim3_4:=Word_01;
26:UPSstatus_Prikaz_PanelSCADA:=Byte_0;
27:UserCurrentLevel:=Byte_0;
28:ErrorComKlima[1].Code[0]:=Byte_0;
29:ErrorComKlima[1].Code[10]:=Byte_0;
30:ErrorComKlima[1].Code[11]:=Byte_0;
31:ErrorComKlima[1].Code[12]:=Byte_0;
32:ErrorComKlima[1].Code[13]:=Byte_0;
33:ErrorComKlima[1].Code[14]:=Byte_0;
34:ErrorComKlima[1].Code[15]:=Byte_0;
35:ErrorComKlima[1].Code[1]:=Byte_0;
36:ErrorComKlima[1].Code[2]:=Byte_0;
37:ErrorComKlima[1].Code[3]:=Byte_0;
38:ErrorComKlima[1].Code[4]:=Byte_0;
39:ErrorComKlima[1].Code[5]:=Byte_0;
40:ErrorComKlima[1].Code[6]:=Byte_0;
41:ErrorComKlima[1].Code[7]:=Byte_0;
42:ErrorComKlima[1].Code[8]:=Byte_0;
43:ErrorComKlima[1].Code[9]:=Byte_0;
44:ErrorComKlima[1].Status:=Word_01;
45:ErrorComKlima[2].Code[0]:=Byte_0;
46:ErrorComKlima[2].Code[10]:=Byte_0;
47:ErrorComKlima[2].Code[11]:=Byte_0;
48:ErrorComKlima[2].Code[12]:=Byte_0;
49:ErrorComKlima[2].Code[13]:=Byte_0;
50:ErrorComKlima[2].Code[14]:=Byte_0;
51:ErrorComKlima[2].Code[15]:=Byte_0;
52:ErrorComKlima[2].Code[1]:=Byte_0;
53:ErrorComKlima[2].Code[2]:=Byte_0;
54:ErrorComKlima[2].Code[3]:=Byte_0;
55:ErrorComKlima[2].Code[4]:=Byte_0;
56:ErrorComKlima[2].Code[5]:=Byte_0;
57:ErrorComKlima[2].Code[6]:=Byte_0;
58:ErrorComKlima[2].Code[7]:=Byte_0;
59:ErrorComKlima[2].Code[8]:=Byte_0;
60:ErrorComKlima[2].Code[9]:=Byte_0;
61:ErrorComKlima[2].Status:=Word_01;
62:ErrorComKlima[3].Code[0]:=Byte_0;
63:ErrorComKlima[3].Code[10]:=Byte_0;
64:ErrorComKlima[3].Code[11]:=Byte_0;
65:ErrorComKlima[3].Code[12]:=Byte_0;
66:ErrorComKlima[3].Code[13]:=Byte_0;
67:ErrorComKlima[3].Code[14]:=Byte_0;
68:ErrorComKlima[3].Code[15]:=Byte_0;
69:ErrorComKlima[3].Code[1]:=Byte_0;
70:ErrorComKlima[3].Code[2]:=Byte_0;
71:ErrorComKlima[3].Code[3]:=Byte_0;
72:ErrorComKlima[3].Code[4]:=Byte_0;
73:ErrorComKlima[3].Code[5]:=Byte_0;
74:ErrorComKlima[3].Code[6]:=Byte_0;
75:ErrorComKlima[3].Code[7]:=Byte_0;
76:ErrorComKlima[3].Code[8]:=Byte_0;
77:ErrorComKlima[3].Code[9]:=Byte_0;
78:ErrorComKlima[3].Status:=Word_01;
79:ErrorComKlima[4].Code[0]:=Byte_0;
80:ErrorComKlima[4].Code[10]:=Byte_0;
81:ErrorComKlima[4].Code[11]:=Byte_0;
82:ErrorComKlima[4].Code[12]:=Byte_0;
83:ErrorComKlima[4].Code[13]:=Byte_0;
84:ErrorComKlima[4].Code[14]:=Byte_0;
85:ErrorComKlima[4].Code[15]:=Byte_0;
86:ErrorComKlima[4].Code[1]:=Byte_0;
87:ErrorComKlima[4].Code[2]:=Byte_0;
88:ErrorComKlima[4].Code[3]:=Byte_0;
89:ErrorComKlima[4].Code[4]:=Byte_0;
90:ErrorComKlima[4].Code[5]:=Byte_0;
91:ErrorComKlima[4].Code[6]:=Byte_0;
92:ErrorComKlima[4].Code[7]:=Byte_0;
93:ErrorComKlima[4].Code[8]:=Byte_0;
94:ErrorComKlima[4].Code[9]:=Byte_0;
95:kom_nast_cas_izpada:=Word_01;
(*Pisanje UINT*)
(**)
;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
(*Modbus Slave Example*)
PROGRAM PLC_PRG_modnet
VAR
Slave_Adresa:BYTE:=2;
Slave_Port:INT:=502;
SlaveSetup:MBS_Setup;
SlavePoll:MBS_Poll;
SlaveAnswer:MBS_Answer;
step: USINT;
end :BOOL;
i: INT;
cycle :BOOL := FALSE; (* First cycle *)
OpenDefaultPort: BOOL;
Write_16: BOOL;
Write_15: BOOL;
Write_5: BOOL;
j: INT;
slavepollwOffset_temp: INT;
slaveanswerwCount_temp: INT;
slaveanswerwoffset_temp: INT;
END_VAR
(* @END_DECLARATION := '0' *)
(*Modbus Slave Example*)
IF Write_16=TRUE THEN (**)
FOR j := 0 TO (slaveanswerwCount_temp-1)/15 BY 1 DO (*vpiše se dword, real*)
wStr_0:=mind[slaveanswerwoffset_temp+j];
wStr_1:=mind[slaveanswerwoffset_temp+j+1];
wStr_2 :=mind[slaveanswerwoffset_temp+j+2];
wStr_3:=mind[slaveanswerwoffset_temp+j+3];
wStr_4:=mind[slaveanswerwoffset_temp+j+4];
wStr_5 :=mind[slaveanswerwoffset_temp+j+5];
wStr_6:=mind[slaveanswerwoffset_temp+j+6];
wStr_7:=mind[slaveanswerwoffset_temp+j+7];
wStr_8:=mind[slaveanswerwoffset_temp+j+8];
wStr_9:=mind[slaveanswerwoffset_temp+j+9];
wStr_10:=mind[slaveanswerwoffset_temp+j+10];
wStr_11:=mind[slaveanswerwoffset_temp+j+11];
wStr_12:=mind[slaveanswerwoffset_temp+j+12];
wStr_13:=mind[slaveanswerwoffset_temp+j+13];
wStr_14:=mind[slaveanswerwoffset_temp+j+14];
bStr_29:=0;
mod_Write_String(index:=slaveanswerwoffset_temp+j); (*vpis real in string*)
END_FOR;
FOR j := 1 TO slaveanswerwCount_temp-1 BY 2 DO (*vpiše se dword, real*)
Word_01:=mind[slaveanswerwoffset_temp+j-1];
Word_23:=mind[slaveanswerwoffset_temp+j];
mod_Write_dWord(index:=slaveanswerwoffset_temp+j); (*vpis real in dword*)
END_FOR;
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO (*vpiše se word*)
Word_01:=mind[slaveanswerwoffset_temp+j];
mod_Write_Word(index:=slaveanswerwoffset_temp+j); (*vpis word*)
END_FOR;
Write_16:=FALSE;
END_IF;
IF Write_5=TRUE OR Write_15=TRUE THEN (**)
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO
Bit_0:=mind_bool[slaveanswerwoffset_temp+j];
mod_Write_Bool(index:=slaveanswerwoffset_temp+j); (*vpis spremembe v spremenljivko*)
END_FOR;
Write_5:=FALSE;
Write_15:=FALSE;
END_IF;
(*iz scade ni komande za branje*)
IF Write_16=FALSE AND Write_5=FALSE AND Write_15=FALSE THEN
mod_Read();(*branje spremenljivk za scado*)
END_IF
(*Close all sockets on corresponding event*)
IF cycle = FALSE THEN
SysCallbackRegister(INDEXOF(Callback_Stop),event_stop);
SysCallbackRegister(INDEXOF(Callback_Reset),event_before_reset);
SysCallbackRegister(INDEXOF(Callback_Reset),event_shutdown);
cycle := TRUE;
END_IF
(*Close all connections via application *)
IF end = TRUE THEN
MBS_CloseAllConnections();
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=FALSE); (*Close port*)
step := 0;
END_IF
IF OpenDefaultPort=TRUE THEN
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=TRUE); (*Close port*)
step := 0;
OpenDefaultPort:=FALSE;
END_IF
(* State machine for setup, poll and answer *)
CASE step OF
0:(**)
SlaveSetup.bUnitIdentifier:=Slave_Adresa;(*Subunitnumber*)
slavesetup.wDefaultPort:=Slave_Port;(*Standartport *)
SlaveSetup.xAdditionalPortActive:=FALSE;(*Port opened or closed*)
SlaveSetup.xSecureMode:=FALSE;(*If TRUE only preset IPs are accepted*)
SlaveSetup.tTimeout:=T#3m;(*Timeout if no communication with slave established*)
SlaveSetup(xStrobe:=TRUE);(*Strobe starts function*)
IF slavesetup.xBusy = FALSE THEN
slavesetup(xstrobe := FALSE);
step := 1 ;
END_IF;
1:(**)
SlavePoll(xStrobe:=TRUE);(*Searching for master commands*)
IF NOT SlavePoll.xBusy THEN
step:=2;
SlavePoll(xStrobe:=FALSE);
END_IF;
2:(**)
step:= 1;
CASE SlavePoll.bFunctionCode OF (*Connect accepted pollparameters with answerparameters*)
8:(**)(*Poll answers*)
;
15:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind_bool[slaveanswer.woffset+i] := slavepoll.xarData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.xarData:=slavepoll.xarData;
Write_15:=TRUE;
16:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind[slaveanswer.woffset+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.wardata := slavepoll.warData;
Write_16:=TRUE;
1,2:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slavepoll.wcount-1 BY 1 DO
slaveanswer.xarData[i]:=mind_bool[slavepoll.woffset+i]; (*Read from Data-array*)
END_FOR
3,4:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slaveanswer.wCount-1 BY 1 DO
slaveanswer.warData[i]:=mind[slavepoll.woffset+i];(*Read from Data-array*)
END_FOR
5:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
mind_bool[slavepoll.woffset]:=slavepoll.xarData[0];(*Write to Data-array*)
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.xarData := slavepoll.xardata;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
Write_5:=TRUE;
6:
slaveanswer.bFunctionCode:= slavepoll.bFunctionCode;
mind[slavepoll.woffset]:= slavepoll.warData[0];(*Write to Data-array*)
slaveanswer.wOffset:= slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wardata := slavepoll.wardata;
23:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
FOR i:= 0 TO slavepoll.wCountAdd-1 BY 1 DO
mind[slavepoll.woffsetadd+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
FOR i := 0 TO slavepoll.wCount BY 1 DO
slaveanswer.warData[i] := mind[1+slavepoll.woffset+i];(*Read from Data-array*)
END_FOR;
END_CASE;
IF slavepoll.xAvailable = TRUE THEN
slaveanswer();(*When Data ready, send answer*)
END_IF
END_CASE;
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_dWord : BOOL
VAR_INPUT
dVAR: DWORD;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
DWord_0:=dVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_Real : BOOL
VAR_INPUT
rVAR: REAL;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
Real_0:=rVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_String : BOOL
VAR_INPUT
sVar: STRING;
start:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
String_0:=LEFT (sVar,29);
mind[start]:=wStr_0;
mind[start+1]:=wStr_1;
mind[start+2]:=wStr_2;
mind[start+3]:=wStr_3;
mind[start+4]:=wStr_4;
mind[start+5]:=wStr_5;
mind[start+6]:=wStr_6;
mind[start+7]:=wStr_7;
mind[start+8]:=wStr_8;
mind[start+9]:=wStr_9;
mind[start+10]:=wStr_10;
mind[start+11]:=wStr_11;
mind[start+12]:=wStr_12;
mind[start+13]:=wStr_13;
bStr_29:=0;
mind[start+14]:=wStr_14;
END_FUNCTION
(* @GLOBAL_VARIABLE_LIST := 'Global_Variables_Modnet' *)
(* @PATH := '' *)
(* @SYMFILEFLAGS := '2048' *)
VAR_GLOBAL
(*delovno polje za modnet komunikacijo*)
mind :ARRAY [0..9999] OF WORD;
mind_bool :ARRAY [0..9999] OF BOOL; (*Buffer-Array*)
(*Delovni markerji //*)
Bit_0 AT %MX0.0 : BOOL;
Byte_0 AT %MB0 : BYTE;
Byte_1 AT %MB1 : BYTE;
Byte_2 AT %MB2 : BYTE;
Byte_3 AT %MB3 : BYTE;
Real_0 AT %MR0:REAL;
DWord_0 AT %MD0:DWORD;
Word_01 AT %MW0:WORD;
Word_23 AT %MW2:WORD;
String_0 AT %MW10:STRING;
wStr_0 AT %MW10:WORD;
wStr_1 AT %MW12:WORD;
wStr_2 AT %MW14:WORD;
wStr_3 AT %MW16:WORD;
wStr_4 AT %MW18:WORD;
wStr_5 AT %MW20:WORD;
wStr_6 AT %MW22:WORD;
wStr_7 AT %MW24:WORD;
wStr_8 AT %MW26:WORD;
wStr_9 AT %MW28:WORD;
wStr_10 AT %MW30:WORD;
wStr_11 AT %MW32:WORD;
wStr_12 AT %MW34:WORD;
wStr_13 AT %MW36:WORD;
wStr_14 AT %MW38:WORD;
bStr_00 AT %MB10:BYTE;
bStr_01 AT %MB11:BYTE;
bStr_02 AT %MB12:BYTE;
bStr_03 AT %MB13:BYTE;
bStr_04 AT %MB14:BYTE;
bStr_05 AT %MB15:BYTE;
bStr_06 AT %MB16:BYTE;
bStr_07 AT %MB17:BYTE;
bStr_08 AT %MB18:BYTE;
bStr_09 AT %MB19:BYTE;
bStr_10 AT %MB20:BYTE;
bStr_11 AT %MB21:BYTE;
bStr_12 AT %MB22:BYTE;
bStr_13 AT %MB23:BYTE;
bStr_14 AT %MB24:BYTE;
bStr_15 AT %MB25:BYTE;
bStr_16 AT %MB26:BYTE;
bStr_17 AT %MB27:BYTE;
bStr_18 AT %MB28:BYTE;
bStr_19 AT %MB29:BYTE;
bStr_20 AT %MB30:BYTE;
bStr_21 AT %MB31:BYTE;
bStr_22 AT %MB32:BYTE;
bStr_23 AT %MB33:BYTE;
bStr_24 AT %MB34:BYTE;
bStr_25 AT %MB35:BYTE;
bStr_26 AT %MB36:BYTE;
bStr_27 AT %MB37:BYTE;
bStr_28 AT %MB38:BYTE;
bStr_29 AT %MB39:BYTE;
(********************************************)
END_VAR
(* @OBJECT_END := 'Global_Variables_Modnet' *)
(* @CONNECTIONS := Global_Variables_Modnet
FILENAME : ''
FILETIME : 0
EXPORT : 0
NUMOFCONNECTIONS : 0
*)
(*KONEC_KODA*)