## Prva stran
variable | 5506 | 1.KORAK | variable_1 | 2.KORAK | KORAKI!
Device name | Tip | število spremenljivk | Tip (izbrani) | Zamenjaj z | 1.V Sheet "variable" skopiraj vsebino iz variable.dbf - iz Citect SCAD-a projekta, ki ga želiš pretvoriti.
IOD_STR | BCD | 0 | BCD | INT | 2.V polje A3 vpiši Device ime spremenljivk ki se bodo prenašale preko Modnet protokola
| BYTE | 497 | BYTE | BYTE | 3.V polje A6 vpiši ime krmilnika (npr.:PLC1, če je adresa v spremenljivkah PLC1:.NapakaKoncnega_stikala, drugače pusti polje prazno)
OPC name | DIGITAL | 1197 | DIGITAL | DIGITAL | 4. Pritisni gumb 1.KORAK (V poljih C3:C10 se izpiše število spremenljivk, ki imajo Device enak tistemu v polju A3)
STR | INT | 662 | INT | INT | 5. Pritisni gumb 2.KORAK (V Sheet-u variable_1 se naredi seznam spremenljivk, ki se bodo prenačale preko Modnet protokola)
| LONG | 2 | LONG | LONG | 6. Pritisni gumb 3.KORAK (V poljih C15:C24 se izpiše število spremnljiv po tipih, v poljih F15:F24 se izpiše število potrebni wordow/coilov za prenos spremnljivk)
| REAL | 616 | REAL | REAL | 7. 4.KORAK: V polja C29:C38 je potrebno ročno vpisati začetne naslove spremnljivk. Potrebno je paziti na:
| STRING | 5 | UINT | UINT | *naslov se morajo začeti z lihim številom npr.:1, 101, 551
| UINT | 1 | STRING | STRING | *naslove je potrebno nastaviti tako, da se naslovi sremenljivk ne more prekrivati (naslovi spremenjivk gredo od (začetnega naslova) do (začetnega naslova+število potrebnih wordow))
8. Pritisni gumb 5.KORAK (V Sheet-u variable_2 se naredi seznam spremenljivk, ki so tokrat sortirana po tipih)
9. Pritisni gumb 6.KORAK (V Sheet-u variable_3 se naredi seznam spremenljivk, katerih Device se zamenja z devicom v polju C41)
Trajanje makroja | variable_1 |  |  | 3.KORAK | 10. Pritisni gumb 7.KORAK (V Sheet-u variable_new se generira seznam spremenljivk. To vsebino je potrebno skopirati v variable.dbf)
0 | Tip | število spremenljivk | TIP | št.potrebnih coilov/wordov | *ta korak traja nekoliko dalj časa (odvisno od števila spremenljivk)
| BCD | 0 | BCD | 0 | *če se pojavi težava z adresami ki se začnejo z 0000 (npr.: "00001" se spremeni na "1") je potrebno uporabiti priloženo (prazno) variable.dbf ali v
| BYTE | 0 | BYTE | 0 | ProjectEditoju/VariableTags na poljubni spremenljki nastaviti adreso" 00001"
| DIGITAL | 1197 | DIGITAL | 1197 (Coil) | 11. Pritisni gumb 8.KORAK in 9.KORAK (V Sheet-u Xsoft se generira koda)
| INT | 1159 | INT | 1159 (word) | 12. S pritiskom na gumb 10.KORAK se zgenerira EXP koda za Xsoft (Xsoft_EXP)
| LONG | 2 | LONG | 4 (word) | 13. S pritiskom na gumb Save*.EXP se avtomatsko generira datoka *.EXP
| REAL | 616 | REAL | 1232 (word)
| STRING | 5 | STRING | 75 (word)
| UINT | 1 | UINT | 1 (word)
POZOR!
*V Sheet-u variable mora biti vsebina skopirana od polja A1 naprej (če je katera vrstica prazna makroji ne bodo delovali pravilno)
*Ena "STRING" spremenljivka zasede 15wordow (to pomeni 29 znakov, 1BYTE=1STRING)
|  | 4.KORAK(vpiši ročno) | variable_2 | 5.KORAK | *Dolžina "STRING" spremenljivk je 29 znakov (lahko tudi več vendar ne z uporabno tega dokumenta in XSoft programa,potrebna je modifikacija makrojev in Xsoft programa)
| Tip | Začetni naslov |  | Sortiraj | *Vsi stringi so enake dolžine (29)
| BCD |  |  | BCD | *"BYTE" spremenljivke se v variable.dbf spremenijo v "INT" (prenašanje posameznih bytov ni mogoče, niti naslavaljanje v citectscadi)
| BYTE |  |  | DIGITAL | *Naslovi spremenljivk se morajo obvezno začeti z lihim naslovom (preizkušeno je z začetnimi naslovi, ki se izpišejo po pritisku na gumb Ponastavi)
| DIGITAL | 1 |  | BYTE | *Z pritiskom na gumb RESET se pobriše vsebina vseh Sheet-ov razen Sheet-a variable (makor reset se izvaja precej časa)
| INT | 1 |  | INT | *makroji ne delujejo pravilno,če je v Sheet-u variable več kot 9999 vrstic oz. spremenljivk (število vseh spremnljivk je prikazano v polju B1)
| LONG | 4001 |  | LONG | *če se vsebine iz variable_new ne gre skpirat v variable.dbf datotek, vsebino skopirajte najprej v *.txt datoteko in nato v variable.dbf
| REAL | 5001 |  | REAL | *v polju A14 na Sheet-u Prva stran se prikazuje število ciklop do konca izvedbe makroja (samo za gumb 7.KORAK)
| STRING | 7001 |  | STRING
| UINT | 8001 |  | UINT
| variable_3 | 6.KORAK | variable_new | 7.KORAK
| New Device name | IOD_STR_TCP |  | Nova variable dbf
|  |  | xSoft | 8.KORAK in 9.KORAK
xSoft koda
xSoft_EXP
Izvoz*.EXP
1.KORAK
2.KORAK
3.KORAK
5.KORAK
6.KORAK
7.KORAK
8.KORAK
9.KORAK
RESET
Ponastavi
10.KORAK
Save*.EXP

## variable
STRUrnikKopiraj | DIGITAL | IOD_STR_disk | D328 | [8 empty] | 0x034075a0
STRToplPostSkupnaNapaka_Omogoci | DIGITAL | IOD_STR_disk | D1 | [8 empty] | 0x034075b0
STRKlima1OkvaraVlazilne_Omogoci | DIGITAL | IOD_STR_disk | D3 | [8 empty] | 0x034075c0
STRKlima1OkvaraRototerma_Omogoci | DIGITAL | IOD_STR_disk | D4 | [8 empty] | 0x034075d0
STRKlima1PozarniAlarm_Omogoci | DIGITAL | IOD_STR_disk | D5 | [8 empty] | 0x034075e0
STRKlima1NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_STR_disk | D6 | [8 empty] | 0x034075f0
STRKlima1PreobremenitevMotVent_Omogoci | DIGITAL | IOD_STR_disk | D7 | [8 empty] | 0x03407600
STRKlima1PreobremenitevMotCrpGr_Omogoci | DIGITAL | IOD_STR_disk | D8 | [8 empty] | 0x03407610
STRKlima1ProtizmrzAktivna_Omogoci | DIGITAL | IOD_STR_disk | D9 | [8 empty] | 0x03407620
STRKlima1ZamasenFilter_Omogoci | DIGITAL | IOD_STR_disk | D10 | [8 empty] | 0x03407630
STRKlima1SkupniAlarmA_Omogoci | DIGITAL | IOD_STR_disk | D11 | [8 empty] | 0x03407640
STRKlima1SkupniAlarmB_Omogoci | DIGITAL | IOD_STR_disk | D12 | [8 empty] | 0x03407650
STRKlima2OkvaraVlazilne_Omogoci | DIGITAL | IOD_STR_disk | D14 | [8 empty] | 0x03407660
STRKlima2OkvaraRototerma_Omogoci | DIGITAL | IOD_STR_disk | D15 | [8 empty] | 0x03407670
STRKlima2PozarniAlarm_Omogoci | DIGITAL | IOD_STR_disk | D16 | [8 empty] | 0x03407680
STRKlima2NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_STR_disk | D17 | [8 empty] | 0x03407690
STRKlima2PreobremenitevMotVent_Omogoci | DIGITAL | IOD_STR_disk | D18 | [8 empty] | 0x034076a0
STRKlima2PreobremenitevMotCrpGr_Omogoci | DIGITAL | IOD_STR_disk | D19 | [8 empty] | 0x034076b0
STRKlima2ProtizmrzAktivna_Omogoci | DIGITAL | IOD_STR_disk | D20 | [8 empty] | 0x034076c0
STRKlima2ZamasenFilter_Omogoci | DIGITAL | IOD_STR_disk | D21 | [8 empty] | 0x034076d0
STRKlima2SkupniAlarmA_Omogoci | DIGITAL | IOD_STR_disk | D22 | [8 empty] | 0x034076e0
STRKlima2SkupniAlarmB_Omogoci | DIGITAL | IOD_STR_disk | D23 | [8 empty] | 0x034076f0
ASTR_Omogoci_SMS_Alarm | DIGITAL | IOD_STR_disk2 | D1[299] | [8 empty] | 0x03407700
BSTR_Omogoci_SMS_Alarm | DIGITAL | IOD_STR_disk2 | D301[299] | [8 empty] | 0x03407710
CSTR_Omogoci_SMS_Alarm | DIGITAL | IOD_STR_disk2 | D602[299] | [8 empty] | 0x03407720
DSTR_Omogoci_SMS_Alarm | DIGITAL | IOD_STR_disk2 | D903[299] | [8 empty] | 0x03407730
ESTR_Omogoci_SMS_Alarm | DIGITAL | IOD_STR_disk2 | D1204[299] | [8 empty] | 0x03407740
FSTR_Omogoci_SMS_Alarm | DIGITAL | IOD_STR_disk2 | D1505[299] | [8 empty] | 0x03407750
STROmogociVseSMSAlarme | DIGITAL | IOD_STR_disk | D24 | [8 empty] | 0x03407760
STROmogociVseAlarme | DIGITAL | IOD_STR_disk | D25 | [8 empty] | 0x03407770
STROmogociVseDogodke_DO | DIGITAL | IOD_STR_disk | D295 | [8 empty] | 0x03407780
STROmogociVseDogodke_DI | DIGITAL | IOD_STR_disk | D296 | [8 empty] | 0x03407790
STROmogociVseDogodke_COM | DIGITAL | IOD_STR_disk | D297 | [8 empty] | 0x034077a0
STR_meja_tok_opozorilo | LONG | IOD_STR_disk | L1[9] | [8 empty] | 0x034077b0
STR_meja_tok_alarm | LONG | IOD_STR_disk | L10[9] | [8 empty] | 0x034077b1
STR_meja_tok_opozorilo_Omogoci | DIGITAL | IOD_STR_disk | D30[9] | [8 empty] | 0x034077c0
STR_meja_tok_alarm_Omogoci | DIGITAL | IOD_STR_disk | D40[9] | [8 empty] | 0x034077d0
STR_razlika_energ_dan | REAL | IOD_STR_disk | R4000 | [8 empty] | 0x034077e0
STR_razlika_energ_ted | REAL | IOD_STR_disk | R4004 | [8 empty] | 0x034077e1
STR_razlika_energ_mes | REAL | IOD_STR_disk | R4008 | [8 empty] | 0x034077e2
STR_DanEnergCirc | REAL | IOD_STR_disk | R4012[30] | [8 empty] | 0x034077e3
STR_CasDDanEnergCirc | INT | IOD_STR_disk | I0[30] | [8 empty] | 0x034077e4
STR_CasMDanEnergCirc | INT | IOD_STR_disk | I30[30] | [8 empty] | 0x034077e5
STR_TedenEnergCirc | REAL | IOD_STR_disk | R4042[30] | [8 empty] | 0x034077e6
STR_CasDTedenEnergCirc | INT | IOD_STR_disk | I60[30] | [8 empty] | 0x034077e7
STR_CasMTedenEnergCirc | INT | IOD_STR_disk | I90[30] | [8 empty] | 0x034077e8
STR_MesecEnergCirc | REAL | IOD_STR_disk | R4072[30] | [8 empty] | 0x034077e9
STR_CasDMesecEnergCirc | INT | IOD_STR_disk | I120[30] | [8 empty] | 0x034077ea
STR_CasMMesecEnergCirc | INT | IOD_STR_disk | I150[30] | [8 empty] | 0x034077eb
STR_StSt_DanEnergCirc | REAL | IOD_STR_disk | R4102 | [8 empty] | 0x034077ec
STR_StSt_TedenEnergCirc | REAL | IOD_STR_disk | R4106 | [8 empty] | 0x034077ed
STR_StSt_MesecEnergCirc | REAL | IOD_STR_disk | R4110 | [8 empty] | 0x034077ee
STR_StStCasDDanEnergCirc | INT | IOD_STR_disk | I276 | [8 empty] | 0x034077ef
STR_StStCasMDanEnergCirc | INT | IOD_STR_disk | I277 | [8 empty] | 0x034077f0
STR_StStCasDTedenEnergCirc | INT | IOD_STR_disk | I278 | [8 empty] | 0x034077f1
STR_StStCasMTedenEnergCirc | INT | IOD_STR_disk | I279 | [8 empty] | 0x034077f2
STR_StStCasDMesecEnergCirc | INT | IOD_STR_disk | I280 | [8 empty] | 0x034077f3
STR_StStCasMMesecEnergCirc | INT | IOD_STR_disk | I281 | [8 empty] | 0x034077f4
STR_MaxDnevnaEnergija1 | REAL | IOD_STR_disk | R4111 | [5 empty] | ####### |  |  | 0x034077f5
STR_MaxMesecnaEnergija1 | REAL | IOD_STR_disk | R4114 | [5 empty] | ####### |  |  | 0x034077f6
STR_MaxTedenskaEnergija1 | REAL | IOD_STR_disk | R4118 | [5 empty] | ####### |  |  | 0x034077f7
STRComSCADA_stevec1 | INT | IOD_STR_disk | I200 | [8 empty] | 0x034077f8
STRComSCADA_stevec2 | INT | IOD_STR_disk | I201 | [8 empty] | 0x034077f9
STRPulz1s | DIGITAL | IOD_STR_disk | D62 | [8 empty] | 0x03407800
STRHladStrojPretokAlarm_Omogoci | DIGITAL | IOD_STR_disk | D63 | [8 empty] | 0x03407810
STRHladStrojFazeAlarm_Omogoci | DIGITAL | IOD_STR_disk | D64 | [8 empty] | 0x03407820
STRHladStrojVisokPritiskAlarm_Omogoci | DIGITAL | IOD_STR_disk | D65 | [8 empty] | 0x03407830
STRHladStrojTemperaturaAlarm_Omogoci | DIGITAL | IOD_STR_disk | D66 | [8 empty] | 0x03407840
STRHladStrojUraAlarm_Omogoci | DIGITAL | IOD_STR_disk | D67 | [8 empty] | 0x03407850
STRHladStrojSenzorAlarm_Omogoci | DIGITAL | IOD_STR_disk | D68 | [8 empty] | 0x03407860
STRHladStrojKompresorOljeAlarm_Omogoci | DIGITAL | IOD_STR_disk | D69 | [8 empty] | 0x03407870
STRHladStrojZmrzalniAlarm_Omogoci | DIGITAL | IOD_STR_disk | D70 | [8 empty] | 0x03407880
STRHladStrojZmrzalniAlarmB_Omogoci | DIGITAL | IOD_STR_disk | D71 | [8 empty] | 0x03407890
STRHladStrojVisokPritiskOpozorilo_Omogoci | DIGITAL | IOD_STR_disk | D72 | [8 empty] | 0x034078a0
STRHladStrojNizekPritiskAlarm_Omogoci | DIGITAL | IOD_STR_disk | D73 | [8 empty] | 0x034078b0
STRHladStrojLANcarelAlarm_Omogoci | DIGITAL | IOD_STR_disk | D74 | [8 empty] | 0x034078c0
STRHladStrojObratovalneUreOpozorilo_Omogoci | DIGITAL | IOD_STR_disk | D75 | [8 empty] | 0x034078d0
STRNapakaSenzorHIA1_Omogoci | DIGITAL | IOD_STR_disk | D78 | [8 empty] | 0x034078e0
STRNapakaSenzorHIA2_Omogoci | DIGITAL | IOD_STR_disk | D79 | [8 empty] | 0x034078f0
STRNapakaSenzorHIA3_Omogoci | DIGITAL | IOD_STR_disk | D80 | [8 empty] | 0x03407900
STRNapakaSenzorHIA4_Omogoci | DIGITAL | IOD_STR_disk | D81 | [8 empty] | 0x03407910
STRNapakaSenzorTIA1_Omogoci | DIGITAL | IOD_STR_disk | D82 | [8 empty] | 0x03407920
STRNapakaSenzorTIA2_Omogoci | DIGITAL | IOD_STR_disk | D83 | [8 empty] | 0x03407930
STRNapakaSenzorTIA3_Omogoci | DIGITAL | IOD_STR_disk | D84 | [8 empty] | 0x03407940
STRNapakaSenzorTIA4_Omogoci | DIGITAL | IOD_STR_disk | D85 | [8 empty] | 0x03407950
STRDI_HladStERR_Omogoci | DIGITAL | IOD_STR_disk | D100 | [8 empty] | 0x03407960
STRDI_Lop3Y1Zaprta_Omogoci | DIGITAL | IOD_STR_disk | D101 | [8 empty] | 0x03407970
STRDI_Lop3Y1Odprta_Omogoci | DIGITAL | IOD_STR_disk | D102 | [8 empty] | 0x03407980
STRDI_Lop4Y1Zaprta_Omogoci | DIGITAL | IOD_STR_disk | D103 | [8 empty] | 0x03407990
STRDI_Lop4Y1Odprta_Omogoci | DIGITAL | IOD_STR_disk | D104 | [8 empty] | 0x034079a0
STRDI_Lop1PL1Zaprta_Omogoci | DIGITAL | IOD_STR_disk | D105 | [8 empty] | 0x034079b0
STRDI_Lop1PL1Odprta_Omogoci | DIGITAL | IOD_STR_disk | D106 | [8 empty] | 0x034079c0
STRDI_Lop1PL2Zaprta_Omogoci | DIGITAL | IOD_STR_disk | D107 | [8 empty] | 0x034079d0
STRDI_Lop1PL2Odprta_Omogoci | DIGITAL | IOD_STR_disk | D108 | [8 empty] | 0x034079e0
STRDI_Lop1PL3Zaprta_Omogoci | DIGITAL | IOD_STR_disk | D109 | [8 empty] | 0x034079f0
STRDI_Lop1PL3Odprta_Omogoci | DIGITAL | IOD_STR_disk | D110 | [8 empty] | 0x03407a00
STRDI_RazlitjeVodeK1_Omogoci | DIGITAL | IOD_STR_disk | D111 | [8 empty] | 0x03407a10
STRDI_RazlitjeVodeK2_Omogoci | DIGITAL | IOD_STR_disk | D112 | [8 empty] | 0x03407a20
STRDI_RazlitjeVodeHP_Omogoci | DIGITAL | IOD_STR_disk | D113 | [8 empty] | 0x03407a30
STRDI_RazlitjeVodeTP_Omogoci | DIGITAL | IOD_STR_disk | D114 | [8 empty] | 0x03407a40
STRDI_RazlitjeVodeEXP1_Omogoci | DIGITAL | IOD_STR_disk | D115 | [8 empty] | 0x03407a50
STRDI_RazlitjeVodeEXP2_Omogoci | DIGITAL | IOD_STR_disk | D116 | [8 empty] | 0x03407a60
STRDI_ToplPostGenErr_Omogoci | DIGITAL | IOD_STR_disk | D117 | [8 empty] | 0x03407a70
STRCrpalkeGrfs1AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D118 | [8 empty] | 0x03407a80
STRCrpalkeGrfs2AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D119 | [8 empty] | 0x03407a90
STRCrpalkeGrfs3AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D120 | [8 empty] | 0x03407aa0
STRCrpalkeGrfs4AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D121 | [8 empty] | 0x03407ab0
STRCrpalkeGrfs5AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D122 | [8 empty] | 0x03407ac0
STRCrpalkeGrfs6AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D123 | [8 empty] | 0x03407ad0
STRCrpalkeGrfs7AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D124 | [8 empty] | 0x03407ae0
STRCrpalkeGrfs8AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D125 | [8 empty] | 0x03407af0
STRCrpalkeGrfs9AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D126 | [8 empty] | 0x03407b00
STRCrpalkeGrfs10AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D127 | [8 empty] | 0x03407b10
STRCrpalkeGrfs11AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D128 | [8 empty] | 0x03407b20
STRCrpalkeGrfs12AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D129 | [8 empty] | 0x03407b30
STRCrpalkeGrfs13AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D130 | [8 empty] | 0x03407b40
STRCrpalkeGrfs14AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D131 | [8 empty] | 0x03407b50
STRCrpalkeDnfs1AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D132 | [8 empty] | 0x03407b60
STRCrpalkeDnfs2AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D133 | [8 empty] | 0x03407b70
STRCrpalkeDnfs3AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D134 | [8 empty] | 0x03407b80
STRCrpalkeDnfs4AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D135 | [8 empty] | 0x03407b90
STRErrCommScada_Omogoci | DIGITAL | IOD_STR_disk | D136 | [8 empty] | 0x03407ba0
STRErrComPanelPLC_Omogoci | DIGITAL | IOD_STR_disk | D137 | [8 empty] | 0x03407bb0
STRErrComPort2_Omogoci | DIGITAL | IOD_STR_disk | D138 | [8 empty] | 0x03407bc0
STRErrComPort3_Omogoci | DIGITAL | IOD_STR_disk | D139 | [8 empty] | 0x03407bd0
STRErrComPort4_Omogoci | DIGITAL | IOD_STR_disk | D140 | [8 empty] | 0x03407be0
STRErrComCirc1_Omogoci | DIGITAL | IOD_STR_disk | D141 | [8 empty] | 0x03407bf0
STRErrComKlima1_Omogoci | DIGITAL | IOD_STR_disk | D142 | [8 empty] | 0x03407c00
STRErrComKlima2_Omogoci | DIGITAL | IOD_STR_disk | D143 | [8 empty] | 0x03407c10
STRErrComDanfossHM1_Omogoci | DIGITAL | IOD_STR_disk | D144 | [8 empty] | 0x03407c20
STRErrComDanfossHM2_Omogoci | DIGITAL | IOD_STR_disk | D145 | [8 empty] | 0x03407c30
STRErrComDanfossHM3_Omogoci | DIGITAL | IOD_STR_disk | D146 | [8 empty] | 0x03407c40
STRErrComDanfossHM4_Omogoci | DIGITAL | IOD_STR_disk | D147 | [8 empty] | 0x03407c50
STRErrComHladStroj_Omogoci | DIGITAL | IOD_STR_disk | D148 | [8 empty] | 0x03407c60
STRErrComToplPost_Omogoci | DIGITAL | IOD_STR_disk | D149 | [8 empty] | 0x03407c70
STRErrCommXC100_Omogoci | DIGITAL | IOD_STR_disk | D150 | [8 empty] | 0x03407c80
STRErrComGrundfos0_Omogoci | DIGITAL | IOD_STR_disk | D151 | [8 empty] | 0x03407c90
STRErrComGrundfos1_Omogoci | DIGITAL | IOD_STR_disk | D152 | [8 empty] | 0x03407ca0
STRErrComGrundfos2_Omogoci | DIGITAL | IOD_STR_disk | D153 | [8 empty] | 0x03407cb0
STRErrComGrundfos3_Omogoci | DIGITAL | IOD_STR_disk | D154 | [8 empty] | 0x03407cc0
STRErrComGrundfos4_Omogoci | DIGITAL | IOD_STR_disk | D155 | [8 empty] | 0x03407cd0
STRErrComGrundfos5_Omogoci | DIGITAL | IOD_STR_disk | D156 | [8 empty] | 0x03407ce0
STRErrComGrundfos6_Omogoci | DIGITAL | IOD_STR_disk | D157 | [8 empty] | 0x03407cf0
STRErrComGrundfos7_Omogoci | DIGITAL | IOD_STR_disk | D158 | [8 empty] | 0x03407d00
STRErrComGrundfos8_Omogoci | DIGITAL | IOD_STR_disk | D159 | [8 empty] | 0x03407d10
STRErrComGrundfos9_Omogoci | DIGITAL | IOD_STR_disk | D160 | [8 empty] | 0x03407d20
STRErrComGrundfos10_Omogoci | DIGITAL | IOD_STR_disk | D161 | [8 empty] | 0x03407d30
STRErrComGrundfos11_Omogoci | DIGITAL | IOD_STR_disk | D162 | [8 empty] | 0x03407d40
STRErrComGrundfos12_Omogoci | DIGITAL | IOD_STR_disk | D163 | [8 empty] | 0x03407d50
STRErrComGrundfos13_Omogoci | DIGITAL | IOD_STR_disk | D164 | [8 empty] | 0x03407d60
STRErrComGrundfos14_Omogoci | DIGITAL | IOD_STR_disk | D165 | [8 empty] | 0x03407d70
STRDIN_230VAC_OK_Omogoci | DIGITAL | IOD_STR_disk | D166 | [8 empty] | 0x03407d80
STRDIN_24VAC_OK_Omogoci | DIGITAL | IOD_STR_disk | D167 | [8 empty] | 0x03407d90
STRDIN_24VDC_OK_Omogoci | DIGITAL | IOD_STR_disk | D168 | [8 empty] | 0x03407da0
STRDIN_CrpHM1ERR_Omogoci | DIGITAL | IOD_STR_disk | D169 | [8 empty] | 0x03407db0
STRDIN_CrpHM2ERR_Omogoci | DIGITAL | IOD_STR_disk | D170 | [8 empty] | 0x03407dc0
STRDIN_CrpHM3ERR_Omogoci | DIGITAL | IOD_STR_disk | D171 | [8 empty] | 0x03407dd0
STRDIN_CrpHM4ERR_Omogoci | DIGITAL | IOD_STR_disk | D172 | [8 empty] | 0x03407de0
STRDIN_HladStERR_Omogoci | DIGITAL | IOD_STR_disk | D173 | [8 empty] | 0x03407df0
STRDI_HladStFS11_Omogoci | DIGITAL | IOD_STR_disk | D174 | [8 empty] | 0x03407e00
STRDIN_Klima1ERR_Omogoci | DIGITAL | IOD_STR_disk | D175 | [8 empty] | 0x03407e10
STRDIN_Klima1filterZAM_Omogoci | DIGITAL | IOD_STR_disk | D176 | [8 empty] | 0x03407e20
STRDI_Klima1FIRE_Omogoci | DIGITAL | IOD_STR_disk | D177 | [8 empty] | 0x03407e30
STRDIN_Klima2ERR_Omogoci | DIGITAL | IOD_STR_disk | D178 | [8 empty] | 0x03407e40
STRDIN_Klima2filterZAM_Omogoci | DIGITAL | IOD_STR_disk | D179 | [8 empty] | 0x03407e50
STRDI_Klima2FIRE_Omogoci | DIGITAL | IOD_STR_disk | D180 | [8 empty] | 0x03407e60
STRDI_Komp1ERR_Omogoci | DIGITAL | IOD_STR_disk | D181 | [8 empty] | 0x03407e70
STRDI_Komp2ERR_Omogoci | DIGITAL | IOD_STR_disk | D182 | [8 empty] | 0x03407e80
STRDI_Kond1FS1FS2_Omogoci | DIGITAL | IOD_STR_disk | D183 | [8 empty] | 0x03407e90
STRDI_Kond2FS1FS2_Omogoci | DIGITAL | IOD_STR_disk | D184 | [8 empty] | 0x03407ea0
STRDI_Kond3FS1FS2_Omogoci | DIGITAL | IOD_STR_disk | D185 | [8 empty] | 0x03407eb0
STRDIN_Vlaz1ERR_Omogoci | DIGITAL | IOD_STR_disk | D186 | [8 empty] | 0x03407ec0
STRDIN_Vlaz2ERR_Omogoci | DIGITAL | IOD_STR_disk | D187 | [8 empty] | 0x03407ed0
STRDIN_Klima1zascStON_Omogoci | DIGITAL | IOD_STR_disk | D188 | [8 empty] | 0x03407ee0
STRDIN_Klima2zascStON_Omogoci | DIGITAL | IOD_STR_disk | D189 | [8 empty] | 0x03407ef0
STRDIN_Kond1zascStON_Omogoci | DIGITAL | IOD_STR_disk | D190 | [8 empty] | 0x03407f00
STRDIN_Kond2zascStON_Omogoci | DIGITAL | IOD_STR_disk | D191 | [8 empty] | 0x03407f10
STRDIN_Kond3zascStON_Omogoci | DIGITAL | IOD_STR_disk | D192 | [8 empty] | 0x03407f20
STRDI_UPS_Alarm_Omogoci | DIGITAL | IOD_STR_disk | D193 | [8 empty] | 0x03407f30
STRDI_UPS_BatNacin_Omogoci | DIGITAL | IOD_STR_disk | D194 | [8 empty] | 0x03407f40
STRDI_UPS_Polnjenje_Omogoci | DIGITAL | IOD_STR_disk | D195 | [8 empty] | 0x03407f50
STRVklopSCFBNapaka1_Omogoci | DIGITAL | IOD_STR_disk | D196 | [8 empty] | 0x03407f60
STRVklopSCFBNapaka2_Omogoci | DIGITAL | IOD_STR_disk | D197 | [8 empty] | 0x03407f70
STRVklopSCFBNapaka3_Omogoci | DIGITAL | IOD_STR_disk | D198 | [8 empty] | 0x03407f80
STRVklopSCFBNapaka4_Omogoci | DIGITAL | IOD_STR_disk | D199 | [8 empty] | 0x03407f90
STRVklopSCFBNapaka5_Omogoci | DIGITAL | IOD_STR_disk | D200 | [8 empty] | 0x03407fa0
STRVklopSCFBNapaka6_Omogoci | DIGITAL | IOD_STR_disk | D201 | [8 empty] | 0x03407fb0
STRVklopSCFBNapaka7_Omogoci | DIGITAL | IOD_STR_disk | D202 | [8 empty] | 0x03407fc0
STRVklopSCFBNapaka8_Omogoci | DIGITAL | IOD_STR_disk | D203 | [8 empty] | 0x03407fd0
STRVklopSCFBNapaka9_Omogoci | DIGITAL | IOD_STR_disk | D204 | [8 empty] | 0x03407fe0
STRVklopSCFBNapaka10_Omogoci | DIGITAL | IOD_STR_disk | D205 | [8 empty] | 0x03407ff0
STRVklopSCFBNapaka11_Omogoci | DIGITAL | IOD_STR_disk | D206 | [8 empty] | 0x03408000
STRVklopSCFBNapaka12_Omogoci | DIGITAL | IOD_STR_disk | D207 | [8 empty] | 0x03408010
STRVklopSCFBNapaka13_Omogoci | DIGITAL | IOD_STR_disk | D208 | [8 empty] | 0x03408020
STRVklopSCFBNapaka14_Omogoci | DIGITAL | IOD_STR_disk | D209 | [8 empty] | 0x03408030
STRVklopSCFBNapaka15_Omogoci | DIGITAL | IOD_STR_disk | D210 | [8 empty] | 0x03408040
STRVklopSCFBNapaka16_Omogoci | DIGITAL | IOD_STR_disk | D211 | [8 empty] | 0x03408050
STRVklopSCFBNapaka17_Omogoci | DIGITAL | IOD_STR_disk | D212 | [8 empty] | 0x03408060
STRVklopSCFBNapaka18_Omogoci | DIGITAL | IOD_STR_disk | D213 | [8 empty] | 0x03408070
STRVklopSCFBNapaka19_Omogoci | DIGITAL | IOD_STR_disk | D214 | [8 empty] | 0x03408080
STRVklopSCFBNapaka20_Omogoci | DIGITAL | IOD_STR_disk | D215 | [8 empty] | 0x03408090
STRVklopSCFBNapaka21_Omogoci | DIGITAL | IOD_STR_disk | D216 | [8 empty] | 0x034080a0
STRVklopSCFBNapaka22_Omogoci | DIGITAL | IOD_STR_disk | D217 | [8 empty] | 0x034080b0
STRVklopSCFBNapaka23_Omogoci | DIGITAL | IOD_STR_disk | D218 | [8 empty] | 0x034080c0
STRVklopSCFBNapaka24_Omogoci | DIGITAL | IOD_STR_disk | D219 | [8 empty] | 0x034080d0
STRVklopSCFBNapaka25_Omogoci | DIGITAL | IOD_STR_disk | D220 | [8 empty] | 0x034080e0
STRSetDateTimeError_Omogoci | DIGITAL | IOD_STR_disk | D221 | [8 empty] | 0x034080f0
STRSlabaBaterijaPLC_A1_Omogoci | DIGITAL | IOD_STR_disk | D222 | [8 empty] | 0x03408100
STRSlabaBaterijaPLC_A100_Omogoci | DIGITAL | IOD_STR_disk | D223 | [8 empty] | 0x03408110
STRTempTSprevisoka_Omogoci | DIGITAL | IOD_STR_disk | D224 | [8 empty] | 0x03408120
STRPozarnaLoputaOnOffError1_Omogoci | DIGITAL | IOD_STR_disk | D225 | [8 empty] | 0x03408130
STRPozarnaLoputaOnOffError2_Omogoci | DIGITAL | IOD_STR_disk | D226 | [8 empty] | 0x03408140
STRPozarnaLoputaOnOffError3_Omogoci | DIGITAL | IOD_STR_disk | D227 | [8 empty] | 0x03408150
STRPozarnaLoputaOnOffError4_Omogoci | DIGITAL | IOD_STR_disk | D228 | [8 empty] | 0x03408160
STRPozarnaLoputaOnOffError5_Omogoci | DIGITAL | IOD_STR_disk | D229 | [8 empty] | 0x03408170
STRNapakaSenzorAI1_Omogoci | DIGITAL | IOD_STR_disk | D230 | [8 empty] | 0x03408180
STRNapakaSenzorAI2_Omogoci | DIGITAL | IOD_STR_disk | D231 | [8 empty] | 0x03408190
STRNapakaSenzorAI3_Omogoci | DIGITAL | IOD_STR_disk | D232 | [8 empty] | 0x034081a0
STRNapakaSenzorAI4_Omogoci | DIGITAL | IOD_STR_disk | D233 | [8 empty] | 0x034081b0
STRNapakaSenzorAI5_Omogoci | DIGITAL | IOD_STR_disk | D234 | [8 empty] | 0x034081c0
STRNapakaSenzorAI6_Omogoci | DIGITAL | IOD_STR_disk | D235 | [8 empty] | 0x034081d0
STRNapakaSenzorAI7_Omogoci | DIGITAL | IOD_STR_disk | D236 | [8 empty] | 0x034081e0
STRNapakaSenzorAI8_Omogoci | DIGITAL | IOD_STR_disk | D237 | [8 empty] | 0x034081f0
STRNapakaSenzorAI9_Omogoci | DIGITAL | IOD_STR_disk | D238 | [8 empty] | 0x03408200
STRNapakaSenzorAI10_Omogoci | DIGITAL | IOD_STR_disk | D239 | [8 empty] | 0x03408210
STRNapakaSenzorAI11_Omogoci | DIGITAL | IOD_STR_disk | D240 | [8 empty] | 0x03408220
STRNapakaSenzorAI12_Omogoci | DIGITAL | IOD_STR_disk | D241 | [8 empty] | 0x03408230
STRNapakaSenzorAI13_Omogoci | DIGITAL | IOD_STR_disk | D242 | [8 empty] | 0x03408240
STRNapakaSenzorAI14_Omogoci | DIGITAL | IOD_STR_disk | D243 | [8 empty] | 0x03408250
STRNapakaSenzorAI15_Omogoci | DIGITAL | IOD_STR_disk | D244 | [8 empty] | 0x03408260
STRNapakaSenzorAI16_Omogoci | DIGITAL | IOD_STR_disk | D245 | [8 empty] | 0x03408270
STRNapakaSenzorAI17_Omogoci | DIGITAL | IOD_STR_disk | D246 | [8 empty] | 0x03408280
STRNapakaSenzorAI18_Omogoci | DIGITAL | IOD_STR_disk | D247 | [8 empty] | 0x03408290
STRNapakaSenzorAI19_Omogoci | DIGITAL | IOD_STR_disk | D248 | [8 empty] | 0x034082a0
STRNapakaSenzorAI20_Omogoci | DIGITAL | IOD_STR_disk | D249 | [8 empty] | 0x034082b0
STRNapakaSenzorAI21_Omogoci | DIGITAL | IOD_STR_disk | D250 | [8 empty] | 0x034082c0
STRNapakaSenzorAI22_Omogoci | DIGITAL | IOD_STR_disk | D251 | [8 empty] | 0x034082d0
STRNapakaSenzorAI23_Omogoci | DIGITAL | IOD_STR_disk | D252 | [8 empty] | 0x034082e0
STRNapakaSenzorAI24_Omogoci | DIGITAL | IOD_STR_disk | D253 | [8 empty] | 0x034082f0
STRNapakaSenzorAI25_Omogoci | DIGITAL | IOD_STR_disk | D254 | [8 empty] | 0x03408300
STRNapakaSenzorAI26_Omogoci | DIGITAL | IOD_STR_disk | D255 | [8 empty] | 0x03408310
STRNapakaSenzorAI27_Omogoci | DIGITAL | IOD_STR_disk | D256 | [8 empty] | 0x03408320
STRNapakaSenzorAI28_Omogoci | DIGITAL | IOD_STR_disk | D257 | [8 empty] | 0x03408330
STRNapakaSenzorAI29_Omogoci | DIGITAL | IOD_STR_disk | D258 | [8 empty] | 0x03408340
STRCrpGrundfosGenError1_Omogoci | DIGITAL | IOD_STR_disk | D259 | [8 empty] | 0x03408350
STRCrpGrundfosGenError2_Omogoci | DIGITAL | IOD_STR_disk | D260 | [8 empty] | 0x03408360
STRCrpGrundfosGenError3_Omogoci | DIGITAL | IOD_STR_disk | D261 | [8 empty] | 0x03408370
STRCrpGrundfosGenError4_Omogoci | DIGITAL | IOD_STR_disk | D262 | [8 empty] | 0x03408380
STRCrpGrundfosGenError5_Omogoci | DIGITAL | IOD_STR_disk | D263 | [8 empty] | 0x03408390
STRCrpGrundfosGenError6_Omogoci | DIGITAL | IOD_STR_disk | D264 | [8 empty] | 0x034083a0
STRCrpGrundfosGenError7_Omogoci | DIGITAL | IOD_STR_disk | D265 | [8 empty] | 0x034083b0
STRCrpGrundfosGenError8_Omogoci | DIGITAL | IOD_STR_disk | D266 | [8 empty] | 0x034083c0
STRCrpGrundfosGenError9_Omogoci | DIGITAL | IOD_STR_disk | D267 | [8 empty] | 0x034083d0
STRCrpGrundfosGenError10_Omogoci | DIGITAL | IOD_STR_disk | D268 | [8 empty] | 0x034083e0
STRCrpGrundfosGenError11_Omogoci | DIGITAL | IOD_STR_disk | D269 | [8 empty] | 0x034083f0
STRCrpGrundfosGenError12_Omogoci | DIGITAL | IOD_STR_disk | D270 | [8 empty] | 0x03408400
STRCrpGrundfosGenError13_Omogoci | DIGITAL | IOD_STR_disk | D271 | [8 empty] | 0x03408410
STRCrpGrundfosGenError14_Omogoci | DIGITAL | IOD_STR_disk | D272 | [8 empty] | 0x03408420
STRCrpGrundfosStatusError1_Omogoci | DIGITAL | IOD_STR_disk | D273 | [8 empty] | 0x03408430
STRCrpGrundfosStatusError2_Omogoci | DIGITAL | IOD_STR_disk | D274 | [8 empty] | 0x03408440
STRCrpGrundfosStatusError3_Omogoci | DIGITAL | IOD_STR_disk | D275 | [8 empty] | 0x03408450
STRCrpGrundfosStatusError4_Omogoci | DIGITAL | IOD_STR_disk | D276 | [8 empty] | 0x03408460
STRCrpGrundfosStatusError5_Omogoci | DIGITAL | IOD_STR_disk | D277 | [8 empty] | 0x03408470
STRCrpGrundfosStatusError6_Omogoci | DIGITAL | IOD_STR_disk | D278 | [8 empty] | 0x03408480
STRCrpGrundfosStatusError7_Omogoci | DIGITAL | IOD_STR_disk | D279 | [8 empty] | 0x03408490
STRCrpGrundfosStatusError8_Omogoci | DIGITAL | IOD_STR_disk | D280 | [8 empty] | 0x034084a0
STRCrpGrundfosStatusError9_Omogoci | DIGITAL | IOD_STR_disk | D281 | [8 empty] | 0x034084b0
STRCrpGrundfosStatusError10_Omogoci | DIGITAL | IOD_STR_disk | D282 | [8 empty] | 0x034084c0
STRCrpGrundfosStatusError11_Omogoci | DIGITAL | IOD_STR_disk | D283 | [8 empty] | 0x034084d0
STRCrpGrundfosStatusError12_Omogoci | DIGITAL | IOD_STR_disk | D284 | [8 empty] | 0x034084e0
STRCrpGrundfosStatusError13_Omogoci | DIGITAL | IOD_STR_disk | D285 | [8 empty] | 0x034084f0
STRCrpGrundfosStatusError14_Omogoci | DIGITAL | IOD_STR_disk | D286 | [8 empty] | 0x03408500
STRCrpDanfossGenError1_Omogoci | DIGITAL | IOD_STR_disk | D287 | [8 empty] | 0x03408510
STRCrpDanfossGenError2_Omogoci | DIGITAL | IOD_STR_disk | D288 | [8 empty] | 0x03408520
STRCrpDanfossGenError3_Omogoci | DIGITAL | IOD_STR_disk | D289 | [8 empty] | 0x03408530
STRCrpDanfossGenError4_Omogoci | DIGITAL | IOD_STR_disk | D290 | [8 empty] | 0x03408540
STRCrpDanfossStatusError1_Omogoci | DIGITAL | IOD_STR_disk | D291 | [8 empty] | 0x03408550
STRCrpDanfossStatusError2_Omogoci | DIGITAL | IOD_STR_disk | D292 | [8 empty] | 0x03408560
STRCrpDanfossStatusError3_Omogoci | DIGITAL | IOD_STR_disk | D293 | [8 empty] | 0x03408570
STRCrpDanfossStatusError4_Omogoci | DIGITAL | IOD_STR_disk | D294 | [8 empty] | 0x03408580
STRSkupnaNapakaPLC_GENIbus_črpalke | DIGITAL | IOD_STR_disk | D298 | [8 empty] | 0x03408590
STRSkupnaNapakaPLC_GENIbus_črpalke_Omogoci | DIGITAL | IOD_STR_disk | D299 | [8 empty] | 0x034085a0
STRSkupnaNApakaSenzorjevHS | DIGITAL | IOD_STR_disk | D300 | [8 empty] | 0x034085b0
STRSkupnaNApakaSenzorjevTP | DIGITAL | IOD_STR_disk | D301 | [8 empty] | 0x034085c0
STRSkupnaNApakaSenzorjevHS_Omogoci | DIGITAL | IOD_STR_disk | D302 | [8 empty] | 0x034085d0
STRSkupnaNApakaSenzorjevTP_Omogoci | DIGITAL | IOD_STR_disk | D303 | [8 empty] | 0x034085e0
STRSkupnaNApakaSenzorjevKN1 | DIGITAL | IOD_STR_disk | D304 | [8 empty] | 0x034085f0
STRSkupnaNApakaSenzorjevKN2 | DIGITAL | IOD_STR_disk | D305 | [8 empty] | 0x03408600
STRSkupnaNApakaSenzorjevKN1_Omogoci | DIGITAL | IOD_STR_disk | D306 | [8 empty] | 0x03408610
STRSkupnaNApakaSenzorjevKN2_Omogoci | DIGITAL | IOD_STR_disk | D307 | [8 empty] | 0x03408620
STRDIN_Komp1ON_Omogoci | DIGITAL | IOD_STR_disk | D308 | [8 empty] | 0x03408630
STRDIN_Komp2ON_Omogoci | DIGITAL | IOD_STR_disk | D309 | [8 empty] | 0x03408640
STRCrpalkeGrfs1AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D310 | [8 empty] | 0x03408650
STRCrpalkeGrfs2AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D311 | [8 empty] | 0x03408660
STRCrpalkeGrfs3AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D312 | [8 empty] | 0x03408670
STRCrpalkeGrfs4AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D313 | [8 empty] | 0x03408680
STRCrpalkeGrfs5AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D314 | [8 empty] | 0x03408690
STRCrpalkeGrfs6AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D315 | [8 empty] | 0x034086a0
STRCrpalkeGrfs7AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D316 | [8 empty] | 0x034086b0
STRCrpalkeGrfs8AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D317 | [8 empty] | 0x034086c0
STRCrpalkeGrfs9AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D318 | [8 empty] | 0x034086d0
STRCrpalkeGrfs10AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D319 | [8 empty] | 0x034086e0
STRCrpalkeGrfs11AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D320 | [8 empty] | 0x034086f0
STRCrpalkeGrfs12AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D321 | [8 empty] | 0x03408700
STRCrpalkeGrfs13AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D322 | [8 empty] | 0x03408710
STRCrpalkeGrfs14AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D323 | [8 empty] | 0x03408720
STRSkpnaNapakaKondenzEnoteInVlazilcev | DIGITAL | IOD_STR_disk | D324 | [8 empty] | 0x03408730
STRSkpnaNapakaKondenzEnoteInVlazilcev_Omogoci | DIGITAL | IOD_STR_disk | D325 | [8 empty] | 0x03408740
STRHladStrojNapaka_Omogoci | DIGITAL | IOD_STR_disk | D329 | [8 empty] | 0x03408750
STRExp1TlakAlarm_Omogoci | DIGITAL | IOD_STR_disk | D330 | [8 empty] | 0x03408760
STRExp2TlakAlarm_Omogoci | DIGITAL | IOD_STR_disk | D331 | [8 empty] | 0x03408770
STRATVTempPrenizka_Omogoci | DIGITAL | IOD_STR_disk | D332 | [8 empty] | 0x03408780
STRUrnikiUrejaj | DIGITAL | IOD_STR_disk | D326 | [8 empty] | 0x03408790
STRDI_GlStikaloDieselON_Omogoci | DIGITAL | IOD_STR_disk | D400 | [8 empty] | 0x034087a0
STRDIN_GlStikaloDieselON_Omogoci | DIGITAL | IOD_STR_disk | D401 | [8 empty] | 0x034087b0
STRDI_GlStikaloMrezaON_Omogoci | DIGITAL | IOD_STR_disk | D402 | [8 empty] | 0x034087c0
STRDIN_GlStikaloMrezaON_Omogoci | DIGITAL | IOD_STR_disk | D403 | [8 empty] | 0x034087d0
STRDI_GlStikaloUpsON_Omogoci | DIGITAL | IOD_STR_disk | D404 | [8 empty] | 0x034087e0
STRDIN_GlStikaloUpsON_Omogoci | DIGITAL | IOD_STR_disk | D405 | [8 empty] | 0x034087f0
STRIzbiraUrnikaB | INT | IOD_STR_disk | I500 | [8 empty] | 0x03408800
STRUrnikiDelovniSCDan1On1Ura | INT | IOD_STR_disk | I501 | [8 empty] | 0x03408801
STRUrnikiDelovniSCDan1On1Mna | INT | IOD_STR_disk | I502 | [8 empty] | 0x03408802
STRUrnikiDelovniSCDan1Off1Ura | INT | IOD_STR_disk | I503 | [8 empty] | 0x03408803
STRUrnikiDelovniSCDan1Off1Mna | INT | IOD_STR_disk | I504 | [8 empty] | 0x03408804
STRUrnikiDelovniSCDan1On2Ura | INT | IOD_STR_disk | I505 | [8 empty] | 0x03408805
STRUrnikiDelovniSCDan1On2Mna | INT | IOD_STR_disk | I506 | [8 empty] | 0x03408806
STRUrnikiDelovniSCDan1Off2Ura | INT | IOD_STR_disk | I507 | [8 empty] | 0x03408807
STRUrnikiDelovniSCDan1Off2Mna | INT | IOD_STR_disk | I508 | [8 empty] | 0x03408808
STRUrnikiDelovniSCDan1On3Ura | INT | IOD_STR_disk | I509 | [8 empty] | 0x03408809
STRUrnikiDelovniSCDan1On3Mna | INT | IOD_STR_disk | I510 | [8 empty] | 0x0340880a
STRUrnikiDelovniSCDan1Off3Ura | INT | IOD_STR_disk | I511 | [8 empty] | 0x0340880b
STRUrnikiDelovniSCDan1Off3Mna | INT | IOD_STR_disk | I512 | [8 empty] | 0x0340880c
STRUrnikiDelovniSCDan2On1Ura | INT | IOD_STR_disk | I513 | [8 empty] | 0x0340880d
STRUrnikiDelovniSCDan2On1Mna | INT | IOD_STR_disk | I514 | [8 empty] | 0x0340880e
STRUrnikiDelovniSCDan2Off1Ura | INT | IOD_STR_disk | I515 | [8 empty] | 0x0340880f
STRUrnikiDelovniSCDan2Off1Mna | INT | IOD_STR_disk | I516 | [8 empty] | 0x03408810
STRUrnikiDelovniSCDan2On2Ura | INT | IOD_STR_disk | I517 | [8 empty] | 0x03408811
STRUrnikiDelovniSCDan2On2Mna | INT | IOD_STR_disk | I518 | [8 empty] | 0x03408812
STRUrnikiDelovniSCDan2Off2Ura | INT | IOD_STR_disk | I519 | [8 empty] | 0x03408813
STRUrnikiDelovniSCDan2Off2Mna | INT | IOD_STR_disk | I520 | [8 empty] | 0x03408814
STRUrnikiDelovniSCDan2On3Ura | INT | IOD_STR_disk | I521 | [8 empty] | 0x03408815
STRUrnikiDelovniSCDan2On3Mna | INT | IOD_STR_disk | I522 | [8 empty] | 0x03408816
STRUrnikiDelovniSCDan2Off3Ura | INT | IOD_STR_disk | I523 | [8 empty] | 0x03408817
STRUrnikiDelovniSCDan2Off3Mna | INT | IOD_STR_disk | I524 | [8 empty] | 0x03408818
STRUrnikiDelovniSCDan3On1Ura | INT | IOD_STR_disk | I525 | [8 empty] | 0x03408819
STRUrnikiDelovniSCDan3On1Mna | INT | IOD_STR_disk | I526 | [8 empty] | 0x0340881a
STRUrnikiDelovniSCDan3Off1Ura | INT | IOD_STR_disk | I527 | [8 empty] | 0x0340881b
STRUrnikiDelovniSCDan3Off1Mna | INT | IOD_STR_disk | I528 | [8 empty] | 0x0340881c
STRUrnikiDelovniSCDan3On2Ura | INT | IOD_STR_disk | I529 | [8 empty] | 0x0340881d
STRUrnikiDelovniSCDan3On2Mna | INT | IOD_STR_disk | I530 | [8 empty] | 0x0340881e
STRUrnikiDelovniSCDan3Off2Ura | INT | IOD_STR_disk | I531 | [8 empty] | 0x0340881f
STRUrnikiDelovniSCDan3Off2Mna | INT | IOD_STR_disk | I532 | [8 empty] | 0x03408820
STRUrnikiDelovniSCDan3On3Ura | INT | IOD_STR_disk | I533 | [8 empty] | 0x03408821
STRUrnikiDelovniSCDan3On3Mna | INT | IOD_STR_disk | I534 | [8 empty] | 0x03408822
STRUrnikiDelovniSCDan3Off3Ura | INT | IOD_STR_disk | I535 | [8 empty] | 0x03408823
STRUrnikiDelovniSCDan3Off3Mna | INT | IOD_STR_disk | I536 | [8 empty] | 0x03408824
STRUrnikiDelovniSCDan4On1Ura | INT | IOD_STR_disk | I537 | [8 empty] | 0x03408825
STRUrnikiDelovniSCDan4On1Mna | INT | IOD_STR_disk | I538 | [8 empty] | 0x03408826
STRUrnikiDelovniSCDan4Off1Ura | INT | IOD_STR_disk | I539 | [8 empty] | 0x03408827
STRUrnikiDelovniSCDan4Off1Mna | INT | IOD_STR_disk | I540 | [8 empty] | 0x03408828
STRUrnikiDelovniSCDan4On2Ura | INT | IOD_STR_disk | I541 | [8 empty] | 0x03408829
STRUrnikiDelovniSCDan4On2Mna | INT | IOD_STR_disk | I542 | [8 empty] | 0x0340882a
STRUrnikiDelovniSCDan4Off2Ura | INT | IOD_STR_disk | I543 | [8 empty] | 0x0340882b
STRUrnikiDelovniSCDan4Off2Mna | INT | IOD_STR_disk | I544 | [8 empty] | 0x0340882c
STRUrnikiDelovniSCDan4On3Ura | INT | IOD_STR_disk | I545 | [8 empty] | 0x0340882d
STRUrnikiDelovniSCDan4On3Mna | INT | IOD_STR_disk | I546 | [8 empty] | 0x0340882e
STRUrnikiDelovniSCDan4Off3Ura | INT | IOD_STR_disk | I547 | [8 empty] | 0x0340882f
STRUrnikiDelovniSCDan4Off3Mna | INT | IOD_STR_disk | I548 | [8 empty] | 0x03408830
STRUrnikiDelovniSCDan5On1Ura | INT | IOD_STR_disk | I549 | [8 empty] | 0x03408831
STRUrnikiDelovniSCDan5On1Mna | INT | IOD_STR_disk | I550 | [8 empty] | 0x03408832
STRUrnikiDelovniSCDan5Off1Ura | INT | IOD_STR_disk | I551 | [8 empty] | 0x03408833
STRUrnikiDelovniSCDan5Off1Mna | INT | IOD_STR_disk | I552 | [8 empty] | 0x03408834
STRUrnikiDelovniSCDan5On2Ura | INT | IOD_STR_disk | I553 | [8 empty] | 0x03408835
STRUrnikiDelovniSCDan5On2Mna | INT | IOD_STR_disk | I554 | [8 empty] | 0x03408836
STRUrnikiDelovniSCDan5Off2Ura | INT | IOD_STR_disk | I555 | [8 empty] | 0x03408837
STRUrnikiDelovniSCDan5Off2Mna | INT | IOD_STR_disk | I556 | [8 empty] | 0x03408838
STRUrnikiDelovniSCDan5On3Ura | INT | IOD_STR_disk | I557 | [8 empty] | 0x03408839
STRUrnikiDelovniSCDan5On3Mna | INT | IOD_STR_disk | I558 | [8 empty] | 0x0340883a
STRUrnikiDelovniSCDan5Off3Ura | INT | IOD_STR_disk | I559 | [8 empty] | 0x0340883b
STRUrnikiDelovniSCDan5Off3Mna | INT | IOD_STR_disk | I560 | [8 empty] | 0x0340883c
STRUrnikiDelovniSCDan6On1Ura | INT | IOD_STR_disk | I561 | [8 empty] | 0x0340883d
STRUrnikiDelovniSCDan6On1Mna | INT | IOD_STR_disk | I562 | [8 empty] | 0x0340883e
STRUrnikiDelovniSCDan6Off1Ura | INT | IOD_STR_disk | I563 | [8 empty] | 0x0340883f
STRUrnikiDelovniSCDan6Off1Mna | INT | IOD_STR_disk | I564 | [8 empty] | 0x03408840
STRUrnikiDelovniSCDan6On2Ura | INT | IOD_STR_disk | I565 | [8 empty] | 0x03408841
STRUrnikiDelovniSCDan6On2Mna | INT | IOD_STR_disk | I566 | [8 empty] | 0x03408842
STRUrnikiDelovniSCDan6Off2Ura | INT | IOD_STR_disk | I567 | [8 empty] | 0x03408843
STRUrnikiDelovniSCDan6Off2Mna | INT | IOD_STR_disk | I568 | [8 empty] | 0x03408844
STRUrnikiDelovniSCDan6On3Ura | INT | IOD_STR_disk | I569 | [8 empty] | 0x03408845
STRUrnikiDelovniSCDan6On3Mna | INT | IOD_STR_disk | I570 | [8 empty] | 0x03408846
STRUrnikiDelovniSCDan6Off3Ura | INT | IOD_STR_disk | I571 | [8 empty] | 0x03408847
STRUrnikiDelovniSCDan6Off3Mna | INT | IOD_STR_disk | I572 | [8 empty] | 0x03408848
STRUrnikiDelovniSCDan7On1Ura | INT | IOD_STR_disk | I573 | [8 empty] | 0x03408849
STRUrnikiDelovniSCDan7On1Mna | INT | IOD_STR_disk | I574 | [8 empty] | 0x0340884a
STRUrnikiDelovniSCDan7Off1Ura | INT | IOD_STR_disk | I575 | [8 empty] | 0x0340884b
STRUrnikiDelovniSCDan7Off1Mna | INT | IOD_STR_disk | I576 | [8 empty] | 0x0340884c
STRUrnikiDelovniSCDan7On2Ura | INT | IOD_STR_disk | I577 | [8 empty] | 0x0340884d
STRUrnikiDelovniSCDan7On2Mna | INT | IOD_STR_disk | I578 | [8 empty] | 0x0340884e
STRUrnikiDelovniSCDan7Off2Ura | INT | IOD_STR_disk | I579 | [8 empty] | 0x0340884f
STRUrnikiDelovniSCDan7Off2Mna | INT | IOD_STR_disk | I580 | [8 empty] | 0x03408850
STRUrnikiDelovniSCDan7On3Ura | INT | IOD_STR_disk | I581 | [8 empty] | 0x03408851
STRUrnikiDelovniSCDan7On3Mna | INT | IOD_STR_disk | I582 | [8 empty] | 0x03408852
STRUrnikiDelovniSCDan7Off3Ura | INT | IOD_STR_disk | I583 | [8 empty] | 0x03408853
STRUrnikiDelovniSCDan7Off3Mna | INT | IOD_STR_disk | I584 | [8 empty] | 0x03408854
STRUrnikiSC1Dan1Urn1UraON | INT | IOD_STR_disk | I1000 | [8 empty] | 0x03408855
STRUrnikiSC1Dan1Urn2UraON | INT | IOD_STR_disk | I1001 | [8 empty] | 0x03408856
STRUrnikiSC1Dan1Urn3UraON | INT | IOD_STR_disk | I1002 | [8 empty] | 0x03408857
STRUrnikiSC1Dan1Urn1UraOFF | INT | IOD_STR_disk | I1003 | [8 empty] | 0x03408858
STRUrnikiSC1Dan1Urn2UraOFF | INT | IOD_STR_disk | I1004 | [8 empty] | 0x03408859
STRUrnikiSC1Dan1Urn3UraOFF | INT | IOD_STR_disk | I1005 | [8 empty] | 0x0340885a
STRUrnikiSC1Dan1Urn1MinON | INT | IOD_STR_disk | I1006 | [8 empty] | 0x0340885b
STRUrnikiSC1Dan1Urn2MinON | INT | IOD_STR_disk | I1007 | [8 empty] | 0x0340885c
STRUrnikiSC1Dan1Urn3MinON | INT | IOD_STR_disk | I1008 | [8 empty] | 0x0340885d
STRUrnikiSC1Dan1Urn1MinOFF | INT | IOD_STR_disk | I1009 | [8 empty] | 0x0340885e
STRUrnikiSC1Dan1Urn2MinOFF | INT | IOD_STR_disk | I1010 | [8 empty] | 0x0340885f
STRUrnikiSC1Dan1Urn3MinOFF | INT | IOD_STR_disk | I1011 | [8 empty] | 0x03408860
STRUrnikiSC1Dan2Urn1UraON | INT | IOD_STR_disk | I1012 | [8 empty] | 0x03408861
STRUrnikiSC1Dan2Urn2UraON | INT | IOD_STR_disk | I1013 | [8 empty] | 0x03408862
STRUrnikiSC1Dan2Urn3UraON | INT | IOD_STR_disk | I1014 | [8 empty] | 0x03408863
STRUrnikiSC1Dan2Urn1UraOFF | INT | IOD_STR_disk | I1015 | [8 empty] | 0x03408864
STRUrnikiSC1Dan2Urn2UraOFF | INT | IOD_STR_disk | I1016 | [8 empty] | 0x03408865
STRUrnikiSC1Dan2Urn3UraOFF | INT | IOD_STR_disk | I1017 | [8 empty] | 0x03408866
STRUrnikiSC1Dan2Urn1MinON | INT | IOD_STR_disk | I1018 | [8 empty] | 0x03408867
STRUrnikiSC1Dan2Urn2MinON | INT | IOD_STR_disk | I1019 | [8 empty] | 0x03408868
STRUrnikiSC1Dan2Urn3MinON | INT | IOD_STR_disk | I1020 | [8 empty] | 0x03408869
STRUrnikiSC1Dan2Urn1MinOFF | INT | IOD_STR_disk | I1021 | [8 empty] | 0x0340886a
STRUrnikiSC1Dan2Urn2MinOFF | INT | IOD_STR_disk | I1022 | [8 empty] | 0x0340886b
STRUrnikiSC1Dan2Urn3MinOFF | INT | IOD_STR_disk | I1023 | [8 empty] | 0x0340886c
STRUrnikiSC1Dan3Urn1UraON | INT | IOD_STR_disk | I1024 | [8 empty] | 0x0340886d
STRUrnikiSC1Dan3Urn2UraON | INT | IOD_STR_disk | I1025 | [8 empty] | 0x0340886e
STRUrnikiSC1Dan3Urn3UraON | INT | IOD_STR_disk | I1026 | [8 empty] | 0x0340886f
STRUrnikiSC1Dan3Urn1UraOFF | INT | IOD_STR_disk | I1027 | [8 empty] | 0x03408870
STRUrnikiSC1Dan3Urn2UraOFF | INT | IOD_STR_disk | I1028 | [8 empty] | 0x03408871
STRUrnikiSC1Dan3Urn3UraOFF | INT | IOD_STR_disk | I1029 | [8 empty] | 0x03408872
STRUrnikiSC1Dan3Urn1MinON | INT | IOD_STR_disk | I1030 | [8 empty] | 0x03408873
STRUrnikiSC1Dan3Urn2MinON | INT | IOD_STR_disk | I1031 | [8 empty] | 0x03408874
STRUrnikiSC1Dan3Urn3MinON | INT | IOD_STR_disk | I1032 | [8 empty] | 0x03408875
STRUrnikiSC1Dan3Urn1MinOFF | INT | IOD_STR_disk | I1033 | [8 empty] | 0x03408876
STRUrnikiSC1Dan3Urn2MinOFF | INT | IOD_STR_disk | I1034 | [8 empty] | 0x03408877
STRUrnikiSC1Dan3Urn3MinOFF | INT | IOD_STR_disk | I1035 | [8 empty] | 0x03408878
STRUrnikiSC1Dan4Urn1UraON | INT | IOD_STR_disk | I1036 | [8 empty] | 0x03408879
STRUrnikiSC1Dan4Urn2UraON | INT | IOD_STR_disk | I1037 | [8 empty] | 0x0340887a
STRUrnikiSC1Dan4Urn3UraON | INT | IOD_STR_disk | I1038 | [8 empty] | 0x0340887b
STRUrnikiSC1Dan4Urn1UraOFF | INT | IOD_STR_disk | I1039 | [8 empty] | 0x0340887c
STRUrnikiSC1Dan4Urn2UraOFF | INT | IOD_STR_disk | I1040 | [8 empty] | 0x0340887d
STRUrnikiSC1Dan4Urn3UraOFF | INT | IOD_STR_disk | I1041 | [8 empty] | 0x0340887e
STRUrnikiSC1Dan4Urn1MinON | INT | IOD_STR_disk | I1042 | [8 empty] | 0x0340887f
STRUrnikiSC1Dan4Urn2MinON | INT | IOD_STR_disk | I1043 | [8 empty] | 0x03408880
STRUrnikiSC1Dan4Urn3MinON | INT | IOD_STR_disk | I1044 | [8 empty] | 0x03408881
STRUrnikiSC1Dan4Urn1MinOFF | INT | IOD_STR_disk | I1045 | [8 empty] | 0x03408882
STRUrnikiSC1Dan4Urn2MinOFF | INT | IOD_STR_disk | I1046 | [8 empty] | 0x03408883
STRUrnikiSC1Dan4Urn3MinOFF | INT | IOD_STR_disk | I1047 | [8 empty] | 0x03408884
STRUrnikiSC1Dan5Urn1UraON | INT | IOD_STR_disk | I1048 | [8 empty] | 0x03408885
STRUrnikiSC1Dan5Urn2UraON | INT | IOD_STR_disk | I1049 | [8 empty] | 0x03408886
STRUrnikiSC1Dan5Urn3UraON | INT | IOD_STR_disk | I1050 | [8 empty] | 0x03408887
STRUrnikiSC1Dan5Urn1UraOFF | INT | IOD_STR_disk | I1051 | [8 empty] | 0x03408888
STRUrnikiSC1Dan5Urn2UraOFF | INT | IOD_STR_disk | I1052 | [8 empty] | 0x03408889
STRUrnikiSC1Dan5Urn3UraOFF | INT | IOD_STR_disk | I1053 | [8 empty] | 0x0340888a
STRUrnikiSC1Dan5Urn1MinON | INT | IOD_STR_disk | I1054 | [8 empty] | 0x0340888b
STRUrnikiSC1Dan5Urn2MinON | INT | IOD_STR_disk | I1055 | [8 empty] | 0x0340888c
STRUrnikiSC1Dan5Urn3MinON | INT | IOD_STR_disk | I1056 | [8 empty] | 0x0340888d
STRUrnikiSC1Dan5Urn1MinOFF | INT | IOD_STR_disk | I1057 | [8 empty] | 0x0340888e
STRUrnikiSC1Dan5Urn2MinOFF | INT | IOD_STR_disk | I1058 | [8 empty] | 0x0340888f
STRUrnikiSC1Dan5Urn3MinOFF | INT | IOD_STR_disk | I1059 | [8 empty] | 0x03408890
STRUrnikiSC1Dan6Urn1UraON | INT | IOD_STR_disk | I1060 | [8 empty] | 0x03408891
STRUrnikiSC1Dan6Urn2UraON | INT | IOD_STR_disk | I1061 | [8 empty] | 0x03408892
STRUrnikiSC1Dan6Urn3UraON | INT | IOD_STR_disk | I1062 | [8 empty] | 0x03408893
STRUrnikiSC1Dan6Urn1UraOFF | INT | IOD_STR_disk | I1063 | [8 empty] | 0x03408894
STRUrnikiSC1Dan6Urn2UraOFF | INT | IOD_STR_disk | I1064 | [8 empty] | 0x03408895
STRUrnikiSC1Dan6Urn3UraOFF | INT | IOD_STR_disk | I1065 | [8 empty] | 0x03408896
STRUrnikiSC1Dan6Urn1MinON | INT | IOD_STR_disk | I1066 | [8 empty] | 0x03408897
STRUrnikiSC1Dan6Urn2MinON | INT | IOD_STR_disk | I1067 | [8 empty] | 0x03408898
STRUrnikiSC1Dan6Urn3MinON | INT | IOD_STR_disk | I1068 | [8 empty] | 0x03408899
STRUrnikiSC1Dan6Urn1MinOFF | INT | IOD_STR_disk | I1069 | [8 empty] | 0x0340889a
STRUrnikiSC1Dan6Urn2MinOFF | INT | IOD_STR_disk | I1070 | [8 empty] | 0x0340889b
STRUrnikiSC1Dan6Urn3MinOFF | INT | IOD_STR_disk | I1071 | [8 empty] | 0x0340889c
STRUrnikiSC1Dan7Urn1UraON | INT | IOD_STR_disk | I1072 | [8 empty] | 0x0340889d
STRUrnikiSC1Dan7Urn2UraON | INT | IOD_STR_disk | I1073 | [8 empty] | 0x0340889e
STRUrnikiSC1Dan7Urn3UraON | INT | IOD_STR_disk | I1074 | [8 empty] | 0x0340889f
STRUrnikiSC1Dan7Urn1UraOFF | INT | IOD_STR_disk | I1075 | [8 empty] | 0x034088a0
STRUrnikiSC1Dan7Urn2UraOFF | INT | IOD_STR_disk | I1076 | [8 empty] | 0x034088a1
STRUrnikiSC1Dan7Urn3UraOFF | INT | IOD_STR_disk | I1077 | [8 empty] | 0x034088a2
STRUrnikiSC1Dan7Urn1MinON | INT | IOD_STR_disk | I1078 | [8 empty] | 0x034088a3
STRUrnikiSC1Dan7Urn2MinON | INT | IOD_STR_disk | I1079 | [8 empty] | 0x034088a4
STRUrnikiSC1Dan7Urn3MinON | INT | IOD_STR_disk | I1080 | [8 empty] | 0x034088a5
STRUrnikiSC1Dan7Urn1MinOFF | INT | IOD_STR_disk | I1081 | [8 empty] | 0x034088a6
STRUrnikiSC1Dan7Urn2MinOFF | INT | IOD_STR_disk | I1082 | [8 empty] | 0x034088a7
STRUrnikiSC1Dan7Urn3MinOFF | INT | IOD_STR_disk | I1083 | [8 empty] | 0x034088a8
STRUrnikiSC2Dan1Urn1UraON | INT | IOD_STR_disk | I1084 | [8 empty] | 0x034088a9
STRUrnikiSC2Dan1Urn2UraON | INT | IOD_STR_disk | I1085 | [8 empty] | 0x034088aa
STRUrnikiSC2Dan1Urn3UraON | INT | IOD_STR_disk | I1086 | [8 empty] | 0x034088ab
STRUrnikiSC2Dan1Urn1UraOFF | INT | IOD_STR_disk | I1087 | [8 empty] | 0x034088ac
STRUrnikiSC2Dan1Urn2UraOFF | INT | IOD_STR_disk | I1088 | [8 empty] | 0x034088ad
STRUrnikiSC2Dan1Urn3UraOFF | INT | IOD_STR_disk | I1089 | [8 empty] | 0x034088ae
STRUrnikiSC2Dan1Urn1MinON | INT | IOD_STR_disk | I1090 | [8 empty] | 0x034088af
STRUrnikiSC2Dan1Urn2MinON | INT | IOD_STR_disk | I1091 | [8 empty] | 0x034088b0
STRUrnikiSC2Dan1Urn3MinON | INT | IOD_STR_disk | I1092 | [8 empty] | 0x034088b1
STRUrnikiSC2Dan1Urn1MinOFF | INT | IOD_STR_disk | I1093 | [8 empty] | 0x034088b2
STRUrnikiSC2Dan1Urn2MinOFF | INT | IOD_STR_disk | I1094 | [8 empty] | 0x034088b3
STRUrnikiSC2Dan1Urn3MinOFF | INT | IOD_STR_disk | I1095 | [8 empty] | 0x034088b4
STRUrnikiSC2Dan2Urn1UraON | INT | IOD_STR_disk | I1096 | [8 empty] | 0x034088b5
STRUrnikiSC2Dan2Urn2UraON | INT | IOD_STR_disk | I1097 | [8 empty] | 0x034088b6
STRUrnikiSC2Dan2Urn3UraON | INT | IOD_STR_disk | I1098 | [8 empty] | 0x034088b7
STRUrnikiSC2Dan2Urn1UraOFF | INT | IOD_STR_disk | I1099 | [8 empty] | 0x034088b8
STRUrnikiSC2Dan2Urn2UraOFF | INT | IOD_STR_disk | I1100 | [8 empty] | 0x034088b9
STRUrnikiSC2Dan2Urn3UraOFF | INT | IOD_STR_disk | I1101 | [8 empty] | 0x034088ba
STRUrnikiSC2Dan2Urn1MinON | INT | IOD_STR_disk | I1102 | [8 empty] | 0x034088bb
STRUrnikiSC2Dan2Urn2MinON | INT | IOD_STR_disk | I1103 | [8 empty] | 0x034088bc
STRUrnikiSC2Dan2Urn3MinON | INT | IOD_STR_disk | I1104 | [8 empty] | 0x034088bd
STRUrnikiSC2Dan2Urn1MinOFF | INT | IOD_STR_disk | I1105 | [8 empty] | 0x034088be
STRUrnikiSC2Dan2Urn2MinOFF | INT | IOD_STR_disk | I1106 | [8 empty] | 0x034088bf
STRUrnikiSC2Dan2Urn3MinOFF | INT | IOD_STR_disk | I1107 | [8 empty] | 0x034088c0
STRUrnikiSC2Dan3Urn1UraON | INT | IOD_STR_disk | I1108 | [8 empty] | 0x034088c1
STRUrnikiSC2Dan3Urn2UraON | INT | IOD_STR_disk | I1109 | [8 empty] | 0x034088c2
STRUrnikiSC2Dan3Urn3UraON | INT | IOD_STR_disk | I1110 | [8 empty] | 0x034088c3
STRUrnikiSC2Dan3Urn1UraOFF | INT | IOD_STR_disk | I1111 | [8 empty] | 0x034088c4
STRUrnikiSC2Dan3Urn2UraOFF | INT | IOD_STR_disk | I1112 | [8 empty] | 0x034088c5
STRUrnikiSC2Dan3Urn3UraOFF | INT | IOD_STR_disk | I1113 | [8 empty] | 0x034088c6
STRUrnikiSC2Dan3Urn1MinON | INT | IOD_STR_disk | I1114 | [8 empty] | 0x034088c7
STRUrnikiSC2Dan3Urn2MinON | INT | IOD_STR_disk | I1115 | [8 empty] | 0x034088c8
STRUrnikiSC2Dan3Urn3MinON | INT | IOD_STR_disk | I1116 | [8 empty] | 0x034088c9
STRUrnikiSC2Dan3Urn1MinOFF | INT | IOD_STR_disk | I1117 | [8 empty] | 0x034088ca
STRUrnikiSC2Dan3Urn2MinOFF | INT | IOD_STR_disk | I1118 | [8 empty] | 0x034088cb
STRUrnikiSC2Dan3Urn3MinOFF | INT | IOD_STR_disk | I1119 | [8 empty] | 0x034088cc
STRUrnikiSC2Dan4Urn1UraON | INT | IOD_STR_disk | I1120 | [8 empty] | 0x034088cd
STRUrnikiSC2Dan4Urn2UraON | INT | IOD_STR_disk | I1121 | [8 empty] | 0x034088ce
STRUrnikiSC2Dan4Urn3UraON | INT | IOD_STR_disk | I1122 | [8 empty] | 0x034088cf
STRUrnikiSC2Dan4Urn1UraOFF | INT | IOD_STR_disk | I1123 | [8 empty] | 0x034088d0
STRUrnikiSC2Dan4Urn2UraOFF | INT | IOD_STR_disk | I1124 | [8 empty] | 0x034088d1
STRUrnikiSC2Dan4Urn3UraOFF | INT | IOD_STR_disk | I1125 | [8 empty] | 0x034088d2
STRUrnikiSC2Dan4Urn1MinON | INT | IOD_STR_disk | I1126 | [8 empty] | 0x034088d3
STRUrnikiSC2Dan4Urn2MinON | INT | IOD_STR_disk | I1127 | [8 empty] | 0x034088d4
STRUrnikiSC2Dan4Urn3MinON | INT | IOD_STR_disk | I1128 | [8 empty] | 0x034088d5
STRUrnikiSC2Dan4Urn1MinOFF | INT | IOD_STR_disk | I1129 | [8 empty] | 0x034088d6
STRUrnikiSC2Dan4Urn2MinOFF | INT | IOD_STR_disk | I1130 | [8 empty] | 0x034088d7
STRUrnikiSC2Dan4Urn3MinOFF | INT | IOD_STR_disk | I1131 | [8 empty] | 0x034088d8
STRUrnikiSC2Dan5Urn1UraON | INT | IOD_STR_disk | I1132 | [8 empty] | 0x034088d9
STRUrnikiSC2Dan5Urn2UraON | INT | IOD_STR_disk | I1133 | [8 empty] | 0x034088da
STRUrnikiSC2Dan5Urn3UraON | INT | IOD_STR_disk | I1134 | [8 empty] | 0x034088db
STRUrnikiSC2Dan5Urn1UraOFF | INT | IOD_STR_disk | I1135 | [8 empty] | 0x034088dc
STRUrnikiSC2Dan5Urn2UraOFF | INT | IOD_STR_disk | I1136 | [8 empty] | 0x034088dd
STRUrnikiSC2Dan5Urn3UraOFF | INT | IOD_STR_disk | I1137 | [8 empty] | 0x034088de
STRUrnikiSC2Dan5Urn1MinON | INT | IOD_STR_disk | I1138 | [8 empty] | 0x034088df
STRUrnikiSC2Dan5Urn2MinON | INT | IOD_STR_disk | I1139 | [8 empty] | 0x034088e0
STRUrnikiSC2Dan5Urn3MinON | INT | IOD_STR_disk | I1140 | [8 empty] | 0x034088e1
STRUrnikiSC2Dan5Urn1MinOFF | INT | IOD_STR_disk | I1141 | [8 empty] | 0x034088e2
STRUrnikiSC2Dan5Urn2MinOFF | INT | IOD_STR_disk | I1142 | [8 empty] | 0x034088e3
STRUrnikiSC2Dan5Urn3MinOFF | INT | IOD_STR_disk | I1143 | [8 empty] | 0x034088e4
STRUrnikiSC2Dan6Urn1UraON | INT | IOD_STR_disk | I1144 | [8 empty] | 0x034088e5
STRUrnikiSC2Dan6Urn2UraON | INT | IOD_STR_disk | I1145 | [8 empty] | 0x034088e6
STRUrnikiSC2Dan6Urn3UraON | INT | IOD_STR_disk | I1146 | [8 empty] | 0x034088e7
STRUrnikiSC2Dan6Urn1UraOFF | INT | IOD_STR_disk | I1147 | [8 empty] | 0x034088e8
STRUrnikiSC2Dan6Urn2UraOFF | INT | IOD_STR_disk | I1148 | [8 empty] | 0x034088e9
STRUrnikiSC2Dan6Urn3UraOFF | INT | IOD_STR_disk | I1149 | [8 empty] | 0x034088ea
STRUrnikiSC2Dan6Urn1MinON | INT | IOD_STR_disk | I1150 | [8 empty] | 0x034088eb
STRUrnikiSC2Dan6Urn2MinON | INT | IOD_STR_disk | I1151 | [8 empty] | 0x034088ec
STRUrnikiSC2Dan6Urn3MinON | INT | IOD_STR_disk | I1152 | [8 empty] | 0x034088ed
STRUrnikiSC2Dan6Urn1MinOFF | INT | IOD_STR_disk | I1153 | [8 empty] | 0x034088ee
STRUrnikiSC2Dan6Urn2MinOFF | INT | IOD_STR_disk | I1154 | [8 empty] | 0x034088ef
STRUrnikiSC2Dan6Urn3MinOFF | INT | IOD_STR_disk | I1155 | [8 empty] | 0x034088f0
STRUrnikiSC2Dan7Urn1UraON | INT | IOD_STR_disk | I1156 | [8 empty] | 0x034088f1
STRUrnikiSC2Dan7Urn2UraON | INT | IOD_STR_disk | I1157 | [8 empty] | 0x034088f2
STRUrnikiSC2Dan7Urn3UraON | INT | IOD_STR_disk | I1158 | [8 empty] | 0x034088f3
STRUrnikiSC2Dan7Urn1UraOFF | INT | IOD_STR_disk | I1159 | [8 empty] | 0x034088f4
STRUrnikiSC2Dan7Urn2UraOFF | INT | IOD_STR_disk | I1160 | [8 empty] | 0x034088f5
STRUrnikiSC2Dan7Urn3UraOFF | INT | IOD_STR_disk | I1161 | [8 empty] | 0x034088f6
STRUrnikiSC2Dan7Urn1MinON | INT | IOD_STR_disk | I1162 | [8 empty] | 0x034088f7
STRUrnikiSC2Dan7Urn2MinON | INT | IOD_STR_disk | I1163 | [8 empty] | 0x034088f8
STRUrnikiSC2Dan7Urn3MinON | INT | IOD_STR_disk | I1164 | [8 empty] | 0x034088f9
STRUrnikiSC2Dan7Urn1MinOFF | INT | IOD_STR_disk | I1165 | [8 empty] | 0x034088fa
STRUrnikiSC2Dan7Urn2MinOFF | INT | IOD_STR_disk | I1166 | [8 empty] | 0x034088fb
STRUrnikiSC2Dan7Urn3MinOFF | INT | IOD_STR_disk | I1167 | [8 empty] | 0x034088fc
STRUrnikiSC3Dan1Urn1UraON | INT | IOD_STR_disk | I1168 | [8 empty] | 0x034088fd
STRUrnikiSC3Dan1Urn2UraON | INT | IOD_STR_disk | I1169 | [8 empty] | 0x034088fe
STRUrnikiSC3Dan1Urn3UraON | INT | IOD_STR_disk | I1170 | [8 empty] | 0x034088ff
STRUrnikiSC3Dan1Urn1UraOFF | INT | IOD_STR_disk | I1171 | [8 empty] | 0x03408900
STRUrnikiSC3Dan1Urn2UraOFF | INT | IOD_STR_disk | I1172 | [8 empty] | 0x03408901
STRUrnikiSC3Dan1Urn3UraOFF | INT | IOD_STR_disk | I1173 | [8 empty] | 0x03408902
STRUrnikiSC3Dan1Urn1MinON | INT | IOD_STR_disk | I1174 | [8 empty] | 0x03408903
STRUrnikiSC3Dan1Urn2MinON | INT | IOD_STR_disk | I1175 | [8 empty] | 0x03408904
STRUrnikiSC3Dan1Urn3MinON | INT | IOD_STR_disk | I1176 | [8 empty] | 0x03408905
STRUrnikiSC3Dan1Urn1MinOFF | INT | IOD_STR_disk | I1177 | [8 empty] | 0x03408906
STRUrnikiSC3Dan1Urn2MinOFF | INT | IOD_STR_disk | I1178 | [8 empty] | 0x03408907
STRUrnikiSC3Dan1Urn3MinOFF | INT | IOD_STR_disk | I1179 | [8 empty] | 0x03408908
STRUrnikiSC3Dan2Urn1UraON | INT | IOD_STR_disk | I1180 | [8 empty] | 0x03408909
STRUrnikiSC3Dan2Urn2UraON | INT | IOD_STR_disk | I1181 | [8 empty] | 0x0340890a
STRUrnikiSC3Dan2Urn3UraON | INT | IOD_STR_disk | I1182 | [8 empty] | 0x0340890b
STRUrnikiSC3Dan2Urn1UraOFF | INT | IOD_STR_disk | I1183 | [8 empty] | 0x0340890c
STRUrnikiSC3Dan2Urn2UraOFF | INT | IOD_STR_disk | I1184 | [8 empty] | 0x0340890d
STRUrnikiSC3Dan2Urn3UraOFF | INT | IOD_STR_disk | I1185 | [8 empty] | 0x0340890e
STRUrnikiSC3Dan2Urn1MinON | INT | IOD_STR_disk | I1186 | [8 empty] | 0x0340890f
STRUrnikiSC3Dan2Urn2MinON | INT | IOD_STR_disk | I1187 | [8 empty] | 0x03408910
STRUrnikiSC3Dan2Urn3MinON | INT | IOD_STR_disk | I1188 | [8 empty] | 0x03408911
STRUrnikiSC3Dan2Urn1MinOFF | INT | IOD_STR_disk | I1189 | [8 empty] | 0x03408912
STRUrnikiSC3Dan2Urn2MinOFF | INT | IOD_STR_disk | I1190 | [8 empty] | 0x03408913
STRUrnikiSC3Dan2Urn3MinOFF | INT | IOD_STR_disk | I1191 | [8 empty] | 0x03408914
STRUrnikiSC3Dan3Urn1UraON | INT | IOD_STR_disk | I1192 | [8 empty] | 0x03408915
STRUrnikiSC3Dan3Urn2UraON | INT | IOD_STR_disk | I1193 | [8 empty] | 0x03408916
STRUrnikiSC3Dan3Urn3UraON | INT | IOD_STR_disk | I1194 | [8 empty] | 0x03408917
STRUrnikiSC3Dan3Urn1UraOFF | INT | IOD_STR_disk | I1195 | [8 empty] | 0x03408918
STRUrnikiSC3Dan3Urn2UraOFF | INT | IOD_STR_disk | I1196 | [8 empty] | 0x03408919
STRUrnikiSC3Dan3Urn3UraOFF | INT | IOD_STR_disk | I1197 | [8 empty] | 0x0340891a
STRUrnikiSC3Dan3Urn1MinON | INT | IOD_STR_disk | I1198 | [8 empty] | 0x0340891b
STRUrnikiSC3Dan3Urn2MinON | INT | IOD_STR_disk | I1199 | [8 empty] | 0x0340891c
STRUrnikiSC3Dan3Urn3MinON | INT | IOD_STR_disk | I1200 | [8 empty] | 0x0340891d
STRUrnikiSC3Dan3Urn1MinOFF | INT | IOD_STR_disk | I1201 | [8 empty] | 0x0340891e
STRUrnikiSC3Dan3Urn2MinOFF | INT | IOD_STR_disk | I1202 | [8 empty] | 0x0340891f
STRUrnikiSC3Dan3Urn3MinOFF | INT | IOD_STR_disk | I1203 | [8 empty] | 0x03408920
STRUrnikiSC3Dan4Urn1UraON | INT | IOD_STR_disk | I1204 | [8 empty] | 0x03408921
STRUrnikiSC3Dan4Urn2UraON | INT | IOD_STR_disk | I1205 | [8 empty] | 0x03408922
STRUrnikiSC3Dan4Urn3UraON | INT | IOD_STR_disk | I1206 | [8 empty] | 0x03408923
STRUrnikiSC3Dan4Urn1UraOFF | INT | IOD_STR_disk | I1207 | [8 empty] | 0x03408924
STRUrnikiSC3Dan4Urn2UraOFF | INT | IOD_STR_disk | I1208 | [8 empty] | 0x03408925
STRUrnikiSC3Dan4Urn3UraOFF | INT | IOD_STR_disk | I1209 | [8 empty] | 0x03408926
STRUrnikiSC3Dan4Urn1MinON | INT | IOD_STR_disk | I1210 | [8 empty] | 0x03408927
STRUrnikiSC3Dan4Urn2MinON | INT | IOD_STR_disk | I1211 | [8 empty] | 0x03408928
STRUrnikiSC3Dan4Urn3MinON | INT | IOD_STR_disk | I1212 | [8 empty] | 0x03408929
STRUrnikiSC3Dan4Urn1MinOFF | INT | IOD_STR_disk | I1213 | [8 empty] | 0x0340892a
STRUrnikiSC3Dan4Urn2MinOFF | INT | IOD_STR_disk | I1214 | [8 empty] | 0x0340892b
STRUrnikiSC3Dan4Urn3MinOFF | INT | IOD_STR_disk | I1215 | [8 empty] | 0x0340892c
STRUrnikiSC3Dan5Urn1UraON | INT | IOD_STR_disk | I1216 | [8 empty] | 0x0340892d
STRUrnikiSC3Dan5Urn2UraON | INT | IOD_STR_disk | I1217 | [8 empty] | 0x0340892e
STRUrnikiSC3Dan5Urn3UraON | INT | IOD_STR_disk | I1218 | [8 empty] | 0x0340892f
STRUrnikiSC3Dan5Urn1UraOFF | INT | IOD_STR_disk | I1219 | [8 empty] | 0x03408930
STRUrnikiSC3Dan5Urn2UraOFF | INT | IOD_STR_disk | I1220 | [8 empty] | 0x03408931
STRUrnikiSC3Dan5Urn3UraOFF | INT | IOD_STR_disk | I1221 | [8 empty] | 0x03408932
STRUrnikiSC3Dan5Urn1MinON | INT | IOD_STR_disk | I1222 | [8 empty] | 0x03408933
STRUrnikiSC3Dan5Urn2MinON | INT | IOD_STR_disk | I1223 | [8 empty] | 0x03408934
STRUrnikiSC3Dan5Urn3MinON | INT | IOD_STR_disk | I1224 | [8 empty] | 0x03408935
STRUrnikiSC3Dan5Urn1MinOFF | INT | IOD_STR_disk | I1225 | [8 empty] | 0x03408936
STRUrnikiSC3Dan5Urn2MinOFF | INT | IOD_STR_disk | I1226 | [8 empty] | 0x03408937
STRUrnikiSC3Dan5Urn3MinOFF | INT | IOD_STR_disk | I1227 | [8 empty] | 0x03408938
STRUrnikiSC3Dan6Urn1UraON | INT | IOD_STR_disk | I1228 | [8 empty] | 0x03408939
STRUrnikiSC3Dan6Urn2UraON | INT | IOD_STR_disk | I1229 | [8 empty] | 0x0340893a
STRUrnikiSC3Dan6Urn3UraON | INT | IOD_STR_disk | I1230 | [8 empty] | 0x0340893b
STRUrnikiSC3Dan6Urn1UraOFF | INT | IOD_STR_disk | I1231 | [8 empty] | 0x0340893c
STRUrnikiSC3Dan6Urn2UraOFF | INT | IOD_STR_disk | I1232 | [8 empty] | 0x0340893d
STRUrnikiSC3Dan6Urn3UraOFF | INT | IOD_STR_disk | I1233 | [8 empty] | 0x0340893e
STRUrnikiSC3Dan6Urn1MinON | INT | IOD_STR_disk | I1234 | [8 empty] | 0x0340893f
STRUrnikiSC3Dan6Urn2MinON | INT | IOD_STR_disk | I1235 | [8 empty] | 0x03408940
STRUrnikiSC3Dan6Urn3MinON | INT | IOD_STR_disk | I1236 | [8 empty] | 0x03408941
STRUrnikiSC3Dan6Urn1MinOFF | INT | IOD_STR_disk | I1237 | [8 empty] | 0x03408942
STRUrnikiSC3Dan6Urn2MinOFF | INT | IOD_STR_disk | I1238 | [8 empty] | 0x03408943
STRUrnikiSC3Dan6Urn3MinOFF | INT | IOD_STR_disk | I1239 | [8 empty] | 0x03408944
STRUrnikiSC3Dan7Urn1UraON | INT | IOD_STR_disk | I1240 | [8 empty] | 0x03408945
STRUrnikiSC3Dan7Urn2UraON | INT | IOD_STR_disk | I1241 | [8 empty] | 0x03408946
STRUrnikiSC3Dan7Urn3UraON | INT | IOD_STR_disk | I1242 | [8 empty] | 0x03408947
STRUrnikiSC3Dan7Urn1UraOFF | INT | IOD_STR_disk | I1243 | [8 empty] | 0x03408948
STRUrnikiSC3Dan7Urn2UraOFF | INT | IOD_STR_disk | I1244 | [8 empty] | 0x03408949
STRUrnikiSC3Dan7Urn3UraOFF | INT | IOD_STR_disk | I1245 | [8 empty] | 0x0340894a
STRUrnikiSC3Dan7Urn1MinON | INT | IOD_STR_disk | I1246 | [8 empty] | 0x0340894b
STRUrnikiSC3Dan7Urn2MinON | INT | IOD_STR_disk | I1247 | [8 empty] | 0x0340894c
STRUrnikiSC3Dan7Urn3MinON | INT | IOD_STR_disk | I1248 | [8 empty] | 0x0340894d
STRUrnikiSC3Dan7Urn1MinOFF | INT | IOD_STR_disk | I1249 | [8 empty] | 0x0340894e
STRUrnikiSC3Dan7Urn2MinOFF | INT | IOD_STR_disk | I1250 | [8 empty] | 0x0340894f
STRUrnikiSC3Dan7Urn3MinOFF | INT | IOD_STR_disk | I1251 | [8 empty] | 0x03408950
STRUrnikiSC4Dan1Urn1UraON | INT | IOD_STR_disk | I1252 | [8 empty] | 0x03408951
STRUrnikiSC4Dan1Urn2UraON | INT | IOD_STR_disk | I1253 | [8 empty] | 0x03408952
STRUrnikiSC4Dan1Urn3UraON | INT | IOD_STR_disk | I1254 | [8 empty] | 0x03408953
STRUrnikiSC4Dan1Urn1UraOFF | INT | IOD_STR_disk | I1255 | [8 empty] | 0x03408954
STRUrnikiSC4Dan1Urn2UraOFF | INT | IOD_STR_disk | I1256 | [8 empty] | 0x03408955
STRUrnikiSC4Dan1Urn3UraOFF | INT | IOD_STR_disk | I1257 | [8 empty] | 0x03408956
STRUrnikiSC4Dan1Urn1MinON | INT | IOD_STR_disk | I1258 | [8 empty] | 0x03408957
STRUrnikiSC4Dan1Urn2MinON | INT | IOD_STR_disk | I1259 | [8 empty] | 0x03408958
STRUrnikiSC4Dan1Urn3MinON | INT | IOD_STR_disk | I1260 | [8 empty] | 0x03408959
STRUrnikiSC4Dan1Urn1MinOFF | INT | IOD_STR_disk | I1261 | [8 empty] | 0x0340895a
STRUrnikiSC4Dan1Urn2MinOFF | INT | IOD_STR_disk | I1262 | [8 empty] | 0x0340895b
STRUrnikiSC4Dan1Urn3MinOFF | INT | IOD_STR_disk | I1263 | [8 empty] | 0x0340895c
STRUrnikiSC4Dan2Urn1UraON | INT | IOD_STR_disk | I1264 | [8 empty] | 0x0340895d
STRUrnikiSC4Dan2Urn2UraON | INT | IOD_STR_disk | I1265 | [8 empty] | 0x0340895e
STRUrnikiSC4Dan2Urn3UraON | INT | IOD_STR_disk | I1266 | [8 empty] | 0x0340895f
STRUrnikiSC4Dan2Urn1UraOFF | INT | IOD_STR_disk | I1267 | [8 empty] | 0x03408960
STRUrnikiSC4Dan2Urn2UraOFF | INT | IOD_STR_disk | I1268 | [8 empty] | 0x03408961
STRUrnikiSC4Dan2Urn3UraOFF | INT | IOD_STR_disk | I1269 | [8 empty] | 0x03408962
STRUrnikiSC4Dan2Urn1MinON | INT | IOD_STR_disk | I1270 | [8 empty] | 0x03408963
STRUrnikiSC4Dan2Urn2MinON | INT | IOD_STR_disk | I1271 | [8 empty] | 0x03408964
STRUrnikiSC4Dan2Urn3MinON | INT | IOD_STR_disk | I1272 | [8 empty] | 0x03408965
STRUrnikiSC4Dan2Urn1MinOFF | INT | IOD_STR_disk | I1273 | [8 empty] | 0x03408966
STRUrnikiSC4Dan2Urn2MinOFF | INT | IOD_STR_disk | I1274 | [8 empty] | 0x03408967
STRUrnikiSC4Dan2Urn3MinOFF | INT | IOD_STR_disk | I1275 | [8 empty] | 0x03408968
STRUrnikiSC4Dan3Urn1UraON | INT | IOD_STR_disk | I1276 | [8 empty] | 0x03408969
STRUrnikiSC4Dan3Urn2UraON | INT | IOD_STR_disk | I1277 | [8 empty] | 0x0340896a
STRUrnikiSC4Dan3Urn3UraON | INT | IOD_STR_disk | I1278 | [8 empty] | 0x0340896b
STRUrnikiSC4Dan3Urn1UraOFF | INT | IOD_STR_disk | I1279 | [8 empty] | 0x0340896c
STRUrnikiSC4Dan3Urn2UraOFF | INT | IOD_STR_disk | I1280 | [8 empty] | 0x0340896d
STRUrnikiSC4Dan3Urn3UraOFF | INT | IOD_STR_disk | I1281 | [8 empty] | 0x0340896e
STRUrnikiSC4Dan3Urn1MinON | INT | IOD_STR_disk | I1282 | [8 empty] | 0x0340896f
STRUrnikiSC4Dan3Urn2MinON | INT | IOD_STR_disk | I1283 | [8 empty] | 0x03408970
STRUrnikiSC4Dan3Urn3MinON | INT | IOD_STR_disk | I1284 | [8 empty] | 0x03408971
STRUrnikiSC4Dan3Urn1MinOFF | INT | IOD_STR_disk | I1285 | [8 empty] | 0x03408972
STRUrnikiSC4Dan3Urn2MinOFF | INT | IOD_STR_disk | I1286 | [8 empty] | 0x03408973
STRUrnikiSC4Dan3Urn3MinOFF | INT | IOD_STR_disk | I1287 | [8 empty] | 0x03408974
STRUrnikiSC4Dan4Urn1UraON | INT | IOD_STR_disk | I1288 | [8 empty] | 0x03408975
STRUrnikiSC4Dan4Urn2UraON | INT | IOD_STR_disk | I1289 | [8 empty] | 0x03408976
STRUrnikiSC4Dan4Urn3UraON | INT | IOD_STR_disk | I1290 | [8 empty] | 0x03408977
STRUrnikiSC4Dan4Urn1UraOFF | INT | IOD_STR_disk | I1291 | [8 empty] | 0x03408978
STRUrnikiSC4Dan4Urn2UraOFF | INT | IOD_STR_disk | I1292 | [8 empty] | 0x03408979
STRUrnikiSC4Dan4Urn3UraOFF | INT | IOD_STR_disk | I1293 | [8 empty] | 0x0340897a
STRUrnikiSC4Dan4Urn1MinON | INT | IOD_STR_disk | I1294 | [8 empty] | 0x0340897b
STRUrnikiSC4Dan4Urn2MinON | INT | IOD_STR_disk | I1295 | [8 empty] | 0x0340897c
STRUrnikiSC4Dan4Urn3MinON | INT | IOD_STR_disk | I1296 | [8 empty] | 0x0340897d
STRUrnikiSC4Dan4Urn1MinOFF | INT | IOD_STR_disk | I1297 | [8 empty] | 0x0340897e
STRUrnikiSC4Dan4Urn2MinOFF | INT | IOD_STR_disk | I1298 | [8 empty] | 0x0340897f
STRUrnikiSC4Dan4Urn3MinOFF | INT | IOD_STR_disk | I1299 | [8 empty] | 0x03408980
STRUrnikiSC4Dan5Urn1UraON | INT | IOD_STR_disk | I1300 | [8 empty] | 0x03408981
STRUrnikiSC4Dan5Urn2UraON | INT | IOD_STR_disk | I1301 | [8 empty] | 0x03408982
STRUrnikiSC4Dan5Urn3UraON | INT | IOD_STR_disk | I1302 | [8 empty] | 0x03408983
STRUrnikiSC4Dan5Urn1UraOFF | INT | IOD_STR_disk | I1303 | [8 empty] | 0x03408984
STRUrnikiSC4Dan5Urn2UraOFF | INT | IOD_STR_disk | I1304 | [8 empty] | 0x03408985
STRUrnikiSC4Dan5Urn3UraOFF | INT | IOD_STR_disk | I1305 | [8 empty] | 0x03408986
STRUrnikiSC4Dan5Urn1MinON | INT | IOD_STR_disk | I1306 | [8 empty] | 0x03408987
STRUrnikiSC4Dan5Urn2MinON | INT | IOD_STR_disk | I1307 | [8 empty] | 0x03408988
STRUrnikiSC4Dan5Urn3MinON | INT | IOD_STR_disk | I1308 | [8 empty] | 0x03408989
STRUrnikiSC4Dan5Urn1MinOFF | INT | IOD_STR_disk | I1309 | [8 empty] | 0x0340898a
STRUrnikiSC4Dan5Urn2MinOFF | INT | IOD_STR_disk | I1310 | [8 empty] | 0x0340898b
STRUrnikiSC4Dan5Urn3MinOFF | INT | IOD_STR_disk | I1311 | [8 empty] | 0x0340898c
STRUrnikiSC4Dan6Urn1UraON | INT | IOD_STR_disk | I1312 | [8 empty] | 0x0340898d
STRUrnikiSC4Dan6Urn2UraON | INT | IOD_STR_disk | I1313 | [8 empty] | 0x0340898e
STRUrnikiSC4Dan6Urn3UraON | INT | IOD_STR_disk | I1314 | [8 empty] | 0x0340898f
STRUrnikiSC4Dan6Urn1UraOFF | INT | IOD_STR_disk | I1315 | [8 empty] | 0x03408990
STRUrnikiSC4Dan6Urn2UraOFF | INT | IOD_STR_disk | I1316 | [8 empty] | 0x03408991
STRUrnikiSC4Dan6Urn3UraOFF | INT | IOD_STR_disk | I1317 | [8 empty] | 0x03408992
STRUrnikiSC4Dan6Urn1MinON | INT | IOD_STR_disk | I1318 | [8 empty] | 0x03408993
STRUrnikiSC4Dan6Urn2MinON | INT | IOD_STR_disk | I1319 | [8 empty] | 0x03408994
STRUrnikiSC4Dan6Urn3MinON | INT | IOD_STR_disk | I1320 | [8 empty] | 0x03408995
STRUrnikiSC4Dan6Urn1MinOFF | INT | IOD_STR_disk | I1321 | [8 empty] | 0x03408996
STRUrnikiSC4Dan6Urn2MinOFF | INT | IOD_STR_disk | I1322 | [8 empty] | 0x03408997
STRUrnikiSC4Dan6Urn3MinOFF | INT | IOD_STR_disk | I1323 | [8 empty] | 0x03408998
STRUrnikiSC4Dan7Urn1UraON | INT | IOD_STR_disk | I1324 | [8 empty] | 0x03408999
STRUrnikiSC4Dan7Urn2UraON | INT | IOD_STR_disk | I1325 | [8 empty] | 0x0340899a
STRUrnikiSC4Dan7Urn3UraON | INT | IOD_STR_disk | I1326 | [8 empty] | 0x0340899b
STRUrnikiSC4Dan7Urn1UraOFF | INT | IOD_STR_disk | I1327 | [8 empty] | 0x0340899c
STRUrnikiSC4Dan7Urn2UraOFF | INT | IOD_STR_disk | I1328 | [8 empty] | 0x0340899d
STRUrnikiSC4Dan7Urn3UraOFF | INT | IOD_STR_disk | I1329 | [8 empty] | 0x0340899e
STRUrnikiSC4Dan7Urn1MinON | INT | IOD_STR_disk | I1330 | [8 empty] | 0x0340899f
STRUrnikiSC4Dan7Urn2MinON | INT | IOD_STR_disk | I1331 | [8 empty] | 0x034089a0
STRUrnikiSC4Dan7Urn3MinON | INT | IOD_STR_disk | I1332 | [8 empty] | 0x034089a1
STRUrnikiSC4Dan7Urn1MinOFF | INT | IOD_STR_disk | I1333 | [8 empty] | 0x034089a2
STRUrnikiSC4Dan7Urn2MinOFF | INT | IOD_STR_disk | I1334 | [8 empty] | 0x034089a3
STRUrnikiSC4Dan7Urn3MinOFF | INT | IOD_STR_disk | I1335 | [8 empty] | 0x034089a4
STRUrnikiSC5Dan1Urn1UraON | INT | IOD_STR_disk | I1336 | [8 empty] | 0x034089a5
STRUrnikiSC5Dan1Urn2UraON | INT | IOD_STR_disk | I1337 | [8 empty] | 0x034089a6
STRUrnikiSC5Dan1Urn3UraON | INT | IOD_STR_disk | I1338 | [8 empty] | 0x034089a7
STRUrnikiSC5Dan1Urn1UraOFF | INT | IOD_STR_disk | I1339 | [8 empty] | 0x034089a8
STRUrnikiSC5Dan1Urn2UraOFF | INT | IOD_STR_disk | I1340 | [8 empty] | 0x034089a9
STRUrnikiSC5Dan1Urn3UraOFF | INT | IOD_STR_disk | I1341 | [8 empty] | 0x034089aa
STRUrnikiSC5Dan1Urn1MinON | INT | IOD_STR_disk | I1342 | [8 empty] | 0x034089ab
STRUrnikiSC5Dan1Urn2MinON | INT | IOD_STR_disk | I1343 | [8 empty] | 0x034089ac
STRUrnikiSC5Dan1Urn3MinON | INT | IOD_STR_disk | I1344 | [8 empty] | 0x034089ad
STRUrnikiSC5Dan1Urn1MinOFF | INT | IOD_STR_disk | I1345 | [8 empty] | 0x034089ae
STRUrnikiSC5Dan1Urn2MinOFF | INT | IOD_STR_disk | I1346 | [8 empty] | 0x034089af
STRUrnikiSC5Dan1Urn3MinOFF | INT | IOD_STR_disk | I1347 | [8 empty] | 0x034089b0
STRUrnikiSC5Dan2Urn1UraON | INT | IOD_STR_disk | I1348 | [8 empty] | 0x034089b1
STRUrnikiSC5Dan2Urn2UraON | INT | IOD_STR_disk | I1349 | [8 empty] | 0x034089b2
STRUrnikiSC5Dan2Urn3UraON | INT | IOD_STR_disk | I1350 | [8 empty] | 0x034089b3
STRUrnikiSC5Dan2Urn1UraOFF | INT | IOD_STR_disk | I1351 | [8 empty] | 0x034089b4
STRUrnikiSC5Dan2Urn2UraOFF | INT | IOD_STR_disk | I1352 | [8 empty] | 0x034089b5
STRUrnikiSC5Dan2Urn3UraOFF | INT | IOD_STR_disk | I1353 | [8 empty] | 0x034089b6
STRUrnikiSC5Dan2Urn1MinON | INT | IOD_STR_disk | I1354 | [8 empty] | 0x034089b7
STRUrnikiSC5Dan2Urn2MinON | INT | IOD_STR_disk | I1355 | [8 empty] | 0x034089b8
STRUrnikiSC5Dan2Urn3MinON | INT | IOD_STR_disk | I1356 | [8 empty] | 0x034089b9
STRUrnikiSC5Dan2Urn1MinOFF | INT | IOD_STR_disk | I1357 | [8 empty] | 0x034089ba
STRUrnikiSC5Dan2Urn2MinOFF | INT | IOD_STR_disk | I1358 | [8 empty] | 0x034089bb
STRUrnikiSC5Dan2Urn3MinOFF | INT | IOD_STR_disk | I1359 | [8 empty] | 0x034089bc
STRUrnikiSC5Dan3Urn1UraON | INT | IOD_STR_disk | I1360 | [8 empty] | 0x034089bd
STRUrnikiSC5Dan3Urn2UraON | INT | IOD_STR_disk | I1361 | [8 empty] | 0x034089be
STRUrnikiSC5Dan3Urn3UraON | INT | IOD_STR_disk | I1362 | [8 empty] | 0x034089bf
STRUrnikiSC5Dan3Urn1UraOFF | INT | IOD_STR_disk | I1363 | [8 empty] | 0x034089c0
STRUrnikiSC5Dan3Urn2UraOFF | INT | IOD_STR_disk | I1364 | [8 empty] | 0x034089c1
STRUrnikiSC5Dan3Urn3UraOFF | INT | IOD_STR_disk | I1365 | [8 empty] | 0x034089c2
STRUrnikiSC5Dan3Urn1MinON | INT | IOD_STR_disk | I1366 | [8 empty] | 0x034089c3
STRUrnikiSC5Dan3Urn2MinON | INT | IOD_STR_disk | I1367 | [8 empty] | 0x034089c4
STRUrnikiSC5Dan3Urn3MinON | INT | IOD_STR_disk | I1368 | [8 empty] | 0x034089c5
STRUrnikiSC5Dan3Urn1MinOFF | INT | IOD_STR_disk | I1369 | [8 empty] | 0x034089c6
STRUrnikiSC5Dan3Urn2MinOFF | INT | IOD_STR_disk | I1370 | [8 empty] | 0x034089c7
STRUrnikiSC5Dan3Urn3MinOFF | INT | IOD_STR_disk | I1371 | [8 empty] | 0x034089c8
STRUrnikiSC5Dan4Urn1UraON | INT | IOD_STR_disk | I1372 | [8 empty] | 0x034089c9
STRUrnikiSC5Dan4Urn2UraON | INT | IOD_STR_disk | I1373 | [8 empty] | 0x034089ca
STRUrnikiSC5Dan4Urn3UraON | INT | IOD_STR_disk | I1374 | [8 empty] | 0x034089cb
STRUrnikiSC5Dan4Urn1UraOFF | INT | IOD_STR_disk | I1375 | [8 empty] | 0x034089cc
STRUrnikiSC5Dan4Urn2UraOFF | INT | IOD_STR_disk | I1376 | [8 empty] | 0x034089cd
STRUrnikiSC5Dan4Urn3UraOFF | INT | IOD_STR_disk | I1377 | [8 empty] | 0x034089ce
STRUrnikiSC5Dan4Urn1MinON | INT | IOD_STR_disk | I1378 | [8 empty] | 0x034089cf
STRUrnikiSC5Dan4Urn2MinON | INT | IOD_STR_disk | I1379 | [8 empty] | 0x034089d0
STRUrnikiSC5Dan4Urn3MinON | INT | IOD_STR_disk | I1380 | [8 empty] | 0x034089d1
STRUrnikiSC5Dan4Urn1MinOFF | INT | IOD_STR_disk | I1381 | [8 empty] | 0x034089d2
STRUrnikiSC5Dan4Urn2MinOFF | INT | IOD_STR_disk | I1382 | [8 empty] | 0x034089d3
STRUrnikiSC5Dan4Urn3MinOFF | INT | IOD_STR_disk | I1383 | [8 empty] | 0x034089d4
STRUrnikiSC5Dan5Urn1UraON | INT | IOD_STR_disk | I1384 | [8 empty] | 0x034089d5
STRUrnikiSC5Dan5Urn2UraON | INT | IOD_STR_disk | I1385 | [8 empty] | 0x034089d6
STRUrnikiSC5Dan5Urn3UraON | INT | IOD_STR_disk | I1386 | [8 empty] | 0x034089d7
STRUrnikiSC5Dan5Urn1UraOFF | INT | IOD_STR_disk | I1387 | [8 empty] | 0x034089d8
STRUrnikiSC5Dan5Urn2UraOFF | INT | IOD_STR_disk | I1388 | [8 empty] | 0x034089d9
STRUrnikiSC5Dan5Urn3UraOFF | INT | IOD_STR_disk | I1389 | [8 empty] | 0x034089da
STRUrnikiSC5Dan5Urn1MinON | INT | IOD_STR_disk | I1390 | [8 empty] | 0x034089db
STRUrnikiSC5Dan5Urn2MinON | INT | IOD_STR_disk | I1391 | [8 empty] | 0x034089dc
STRUrnikiSC5Dan5Urn3MinON | INT | IOD_STR_disk | I1392 | [8 empty] | 0x034089dd
STRUrnikiSC5Dan5Urn1MinOFF | INT | IOD_STR_disk | I1393 | [8 empty] | 0x034089de
STRUrnikiSC5Dan5Urn2MinOFF | INT | IOD_STR_disk | I1394 | [8 empty] | 0x034089df
STRUrnikiSC5Dan5Urn3MinOFF | INT | IOD_STR_disk | I1395 | [8 empty] | 0x034089e0
STRUrnikiSC5Dan6Urn1UraON | INT | IOD_STR_disk | I1396 | [8 empty] | 0x034089e1
STRUrnikiSC5Dan6Urn2UraON | INT | IOD_STR_disk | I1397 | [8 empty] | 0x034089e2
STRUrnikiSC5Dan6Urn3UraON | INT | IOD_STR_disk | I1398 | [8 empty] | 0x034089e3
STRUrnikiSC5Dan6Urn1UraOFF | INT | IOD_STR_disk | I1399 | [8 empty] | 0x034089e4
STRUrnikiSC5Dan6Urn2UraOFF | INT | IOD_STR_disk | I1400 | [8 empty] | 0x034089e5
STRUrnikiSC5Dan6Urn3UraOFF | INT | IOD_STR_disk | I1401 | [8 empty] | 0x034089e6
STRUrnikiSC5Dan6Urn1MinON | INT | IOD_STR_disk | I1402 | [8 empty] | 0x034089e7
STRUrnikiSC5Dan6Urn2MinON | INT | IOD_STR_disk | I1403 | [8 empty] | 0x034089e8
STRUrnikiSC5Dan6Urn3MinON | INT | IOD_STR_disk | I1404 | [8 empty] | 0x034089e9
STRUrnikiSC5Dan6Urn1MinOFF | INT | IOD_STR_disk | I1405 | [8 empty] | 0x034089ea
STRUrnikiSC5Dan6Urn2MinOFF | INT | IOD_STR_disk | I1406 | [8 empty] | 0x034089eb
STRUrnikiSC5Dan6Urn3MinOFF | INT | IOD_STR_disk | I1407 | [8 empty] | 0x034089ec
STRUrnikiSC5Dan7Urn1UraON | INT | IOD_STR_disk | I1408 | [8 empty] | 0x034089ed
STRUrnikiSC5Dan7Urn2UraON | INT | IOD_STR_disk | I1409 | [8 empty] | 0x034089ee
STRUrnikiSC5Dan7Urn3UraON | INT | IOD_STR_disk | I1410 | [8 empty] | 0x034089ef
STRUrnikiSC5Dan7Urn1UraOFF | INT | IOD_STR_disk | I1411 | [8 empty] | 0x034089f0
STRUrnikiSC5Dan7Urn2UraOFF | INT | IOD_STR_disk | I1412 | [8 empty] | 0x034089f1
STRUrnikiSC5Dan7Urn3UraOFF | INT | IOD_STR_disk | I1413 | [8 empty] | 0x034089f2
STRUrnikiSC5Dan7Urn1MinON | INT | IOD_STR_disk | I1414 | [8 empty] | 0x034089f3
STRUrnikiSC5Dan7Urn2MinON | INT | IOD_STR_disk | I1415 | [8 empty] | 0x034089f4
STRUrnikiSC5Dan7Urn3MinON | INT | IOD_STR_disk | I1416 | [8 empty] | 0x034089f5
STRUrnikiSC5Dan7Urn1MinOFF | INT | IOD_STR_disk | I1417 | [8 empty] | 0x034089f6
STRUrnikiSC5Dan7Urn2MinOFF | INT | IOD_STR_disk | I1418 | [8 empty] | 0x034089f7
STRUrnikiSC5Dan7Urn3MinOFF | INT | IOD_STR_disk | I1419 | [8 empty] | 0x034089f8
STRUrnikiSC6Dan1Urn1UraON | INT | IOD_STR_disk | I1420 | [8 empty] | 0x034089f9
STRUrnikiSC6Dan1Urn2UraON | INT | IOD_STR_disk | I1421 | [8 empty] | 0x034089fa
STRUrnikiSC6Dan1Urn3UraON | INT | IOD_STR_disk | I1422 | [8 empty] | 0x034089fb
STRUrnikiSC6Dan1Urn1UraOFF | INT | IOD_STR_disk | I1423 | [8 empty] | 0x034089fc
STRUrnikiSC6Dan1Urn2UraOFF | INT | IOD_STR_disk | I1424 | [8 empty] | 0x034089fd
STRUrnikiSC6Dan1Urn3UraOFF | INT | IOD_STR_disk | I1425 | [8 empty] | 0x034089fe
STRUrnikiSC6Dan1Urn1MinON | INT | IOD_STR_disk | I1426 | [8 empty] | 0x034089ff
STRUrnikiSC6Dan1Urn2MinON | INT | IOD_STR_disk | I1427 | [8 empty] | 0x03408a00
STRUrnikiSC6Dan1Urn3MinON | INT | IOD_STR_disk | I1428 | [8 empty] | 0x03408a01
STRUrnikiSC6Dan1Urn1MinOFF | INT | IOD_STR_disk | I1429 | [8 empty] | 0x03408a02
STRUrnikiSC6Dan1Urn2MinOFF | INT | IOD_STR_disk | I1430 | [8 empty] | 0x03408a03
STRUrnikiSC6Dan1Urn3MinOFF | INT | IOD_STR_disk | I1431 | [8 empty] | 0x03408a04
STRUrnikiSC6Dan2Urn1UraON | INT | IOD_STR_disk | I1432 | [8 empty] | 0x03408a05
STRUrnikiSC6Dan2Urn2UraON | INT | IOD_STR_disk | I1433 | [8 empty] | 0x03408a06
STRUrnikiSC6Dan2Urn3UraON | INT | IOD_STR_disk | I1434 | [8 empty] | 0x03408a07
STRUrnikiSC6Dan2Urn1UraOFF | INT | IOD_STR_disk | I1435 | [8 empty] | 0x03408a08
STRUrnikiSC6Dan2Urn2UraOFF | INT | IOD_STR_disk | I1436 | [8 empty] | 0x03408a09
STRUrnikiSC6Dan2Urn3UraOFF | INT | IOD_STR_disk | I1437 | [8 empty] | 0x03408a0a
STRUrnikiSC6Dan2Urn1MinON | INT | IOD_STR_disk | I1438 | [8 empty] | 0x03408a0b
STRUrnikiSC6Dan2Urn2MinON | INT | IOD_STR_disk | I1439 | [8 empty] | 0x03408a0c
STRUrnikiSC6Dan2Urn3MinON | INT | IOD_STR_disk | I1440 | [8 empty] | 0x03408a0d
STRUrnikiSC6Dan2Urn1MinOFF | INT | IOD_STR_disk | I1441 | [8 empty] | 0x03408a0e
STRUrnikiSC6Dan2Urn2MinOFF | INT | IOD_STR_disk | I1442 | [8 empty] | 0x03408a0f
STRUrnikiSC6Dan2Urn3MinOFF | INT | IOD_STR_disk | I1443 | [8 empty] | 0x03408a10
STRUrnikiSC6Dan3Urn1UraON | INT | IOD_STR_disk | I1444 | [8 empty] | 0x03408a11
STRUrnikiSC6Dan3Urn2UraON | INT | IOD_STR_disk | I1445 | [8 empty] | 0x03408a12
STRUrnikiSC6Dan3Urn3UraON | INT | IOD_STR_disk | I1446 | [8 empty] | 0x03408a13
STRUrnikiSC6Dan3Urn1UraOFF | INT | IOD_STR_disk | I1447 | [8 empty] | 0x03408a14
STRUrnikiSC6Dan3Urn2UraOFF | INT | IOD_STR_disk | I1448 | [8 empty] | 0x03408a15
STRUrnikiSC6Dan3Urn3UraOFF | INT | IOD_STR_disk | I1449 | [8 empty] | 0x03408a16
STRUrnikiSC6Dan3Urn1MinON | INT | IOD_STR_disk | I1450 | [8 empty] | 0x03408a17
STRUrnikiSC6Dan3Urn2MinON | INT | IOD_STR_disk | I1451 | [8 empty] | 0x03408a18
STRUrnikiSC6Dan3Urn3MinON | INT | IOD_STR_disk | I1452 | [8 empty] | 0x03408a19
STRUrnikiSC6Dan3Urn1MinOFF | INT | IOD_STR_disk | I1453 | [8 empty] | 0x03408a1a
STRUrnikiSC6Dan3Urn2MinOFF | INT | IOD_STR_disk | I1454 | [8 empty] | 0x03408a1b
STRUrnikiSC6Dan3Urn3MinOFF | INT | IOD_STR_disk | I1455 | [8 empty] | 0x03408a1c
STRUrnikiSC6Dan4Urn1UraON | INT | IOD_STR_disk | I1456 | [8 empty] | 0x03408a1d
STRUrnikiSC6Dan4Urn2UraON | INT | IOD_STR_disk | I1457 | [8 empty] | 0x03408a1e
STRUrnikiSC6Dan4Urn3UraON | INT | IOD_STR_disk | I1458 | [8 empty] | 0x03408a1f
STRUrnikiSC6Dan4Urn1UraOFF | INT | IOD_STR_disk | I1459 | [8 empty] | 0x03408a20
STRUrnikiSC6Dan4Urn2UraOFF | INT | IOD_STR_disk | I1460 | [8 empty] | 0x03408a21
STRUrnikiSC6Dan4Urn3UraOFF | INT | IOD_STR_disk | I1461 | [8 empty] | 0x03408a22
STRUrnikiSC6Dan4Urn1MinON | INT | IOD_STR_disk | I1462 | [8 empty] | 0x03408a23
STRUrnikiSC6Dan4Urn2MinON | INT | IOD_STR_disk | I1463 | [8 empty] | 0x03408a24
STRUrnikiSC6Dan4Urn3MinON | INT | IOD_STR_disk | I1464 | [8 empty] | 0x03408a25
STRUrnikiSC6Dan4Urn1MinOFF | INT | IOD_STR_disk | I1465 | [8 empty] | 0x03408a26
STRUrnikiSC6Dan4Urn2MinOFF | INT | IOD_STR_disk | I1466 | [8 empty] | 0x03408a27
STRUrnikiSC6Dan4Urn3MinOFF | INT | IOD_STR_disk | I1467 | [8 empty] | 0x03408a28
STRUrnikiSC6Dan5Urn1UraON | INT | IOD_STR_disk | I1468 | [8 empty] | 0x03408a29
STRUrnikiSC6Dan5Urn2UraON | INT | IOD_STR_disk | I1469 | [8 empty] | 0x03408a2a
STRUrnikiSC6Dan5Urn3UraON | INT | IOD_STR_disk | I1470 | [8 empty] | 0x03408a2b
STRUrnikiSC6Dan5Urn1UraOFF | INT | IOD_STR_disk | I1471 | [8 empty] | 0x03408a2c
STRUrnikiSC6Dan5Urn2UraOFF | INT | IOD_STR_disk | I1472 | [8 empty] | 0x03408a2d
STRUrnikiSC6Dan5Urn3UraOFF | INT | IOD_STR_disk | I1473 | [8 empty] | 0x03408a2e
STRUrnikiSC6Dan5Urn1MinON | INT | IOD_STR_disk | I1474 | [8 empty] | 0x03408a2f
STRUrnikiSC6Dan5Urn2MinON | INT | IOD_STR_disk | I1475 | [8 empty] | 0x03408a30
STRUrnikiSC6Dan5Urn3MinON | INT | IOD_STR_disk | I1476 | [8 empty] | 0x03408a31
STRUrnikiSC6Dan5Urn1MinOFF | INT | IOD_STR_disk | I1477 | [8 empty] | 0x03408a32
STRUrnikiSC6Dan5Urn2MinOFF | INT | IOD_STR_disk | I1478 | [8 empty] | 0x03408a33
STRUrnikiSC6Dan5Urn3MinOFF | INT | IOD_STR_disk | I1479 | [8 empty] | 0x03408a34
STRUrnikiSC6Dan6Urn1UraON | INT | IOD_STR_disk | I1480 | [8 empty] | 0x03408a35
STRUrnikiSC6Dan6Urn2UraON | INT | IOD_STR_disk | I1481 | [8 empty] | 0x03408a36
STRUrnikiSC6Dan6Urn3UraON | INT | IOD_STR_disk | I1482 | [8 empty] | 0x03408a37
STRUrnikiSC6Dan6Urn1UraOFF | INT | IOD_STR_disk | I1483 | [8 empty] | 0x03408a38
STRUrnikiSC6Dan6Urn2UraOFF | INT | IOD_STR_disk | I1484 | [8 empty] | 0x03408a39
STRUrnikiSC6Dan6Urn3UraOFF | INT | IOD_STR_disk | I1485 | [8 empty] | 0x03408a3a
STRUrnikiSC6Dan6Urn1MinON | INT | IOD_STR_disk | I1486 | [8 empty] | 0x03408a3b
STRUrnikiSC6Dan6Urn2MinON | INT | IOD_STR_disk | I1487 | [8 empty] | 0x03408a3c
STRUrnikiSC6Dan6Urn3MinON | INT | IOD_STR_disk | I1488 | [8 empty] | 0x03408a3d
STRUrnikiSC6Dan6Urn1MinOFF | INT | IOD_STR_disk | I1489 | [8 empty] | 0x03408a3e
STRUrnikiSC6Dan6Urn2MinOFF | INT | IOD_STR_disk | I1490 | [8 empty] | 0x03408a3f
STRUrnikiSC6Dan6Urn3MinOFF | INT | IOD_STR_disk | I1491 | [8 empty] | 0x03408a40
STRUrnikiSC6Dan7Urn1UraON | INT | IOD_STR_disk | I1492 | [8 empty] | 0x03408a41
STRUrnikiSC6Dan7Urn2UraON | INT | IOD_STR_disk | I1493 | [8 empty] | 0x03408a42
STRUrnikiSC6Dan7Urn3UraON | INT | IOD_STR_disk | I1494 | [8 empty] | 0x03408a43
STRUrnikiSC6Dan7Urn1UraOFF | INT | IOD_STR_disk | I1495 | [8 empty] | 0x03408a44
STRUrnikiSC6Dan7Urn2UraOFF | INT | IOD_STR_disk | I1496 | [8 empty] | 0x03408a45
STRUrnikiSC6Dan7Urn3UraOFF | INT | IOD_STR_disk | I1497 | [8 empty] | 0x03408a46
STRUrnikiSC6Dan7Urn1MinON | INT | IOD_STR_disk | I1498 | [8 empty] | 0x03408a47
STRUrnikiSC6Dan7Urn2MinON | INT | IOD_STR_disk | I1499 | [8 empty] | 0x03408a48
STRUrnikiSC6Dan7Urn3MinON | INT | IOD_STR_disk | I1500 | [8 empty] | 0x03408a49
STRUrnikiSC6Dan7Urn1MinOFF | INT | IOD_STR_disk | I1501 | [8 empty] | 0x03408a4a
STRUrnikiSC6Dan7Urn2MinOFF | INT | IOD_STR_disk | I1502 | [8 empty] | 0x03408a4b
STRUrnikiSC6Dan7Urn3MinOFF | INT | IOD_STR_disk | I1503 | [8 empty] | 0x03408a4c
STRUrnikiSC7Dan1Urn1UraON | INT | IOD_STR_disk | I1504 | [8 empty] | 0x03408a4d
STRUrnikiSC7Dan1Urn2UraON | INT | IOD_STR_disk | I1505 | [8 empty] | 0x03408a4e
STRUrnikiSC7Dan1Urn3UraON | INT | IOD_STR_disk | I1506 | [8 empty] | 0x03408a4f
STRUrnikiSC7Dan1Urn1UraOFF | INT | IOD_STR_disk | I1507 | [8 empty] | 0x03408a50
STRUrnikiSC7Dan1Urn2UraOFF | INT | IOD_STR_disk | I1508 | [8 empty] | 0x03408a51
STRUrnikiSC7Dan1Urn3UraOFF | INT | IOD_STR_disk | I1509 | [8 empty] | 0x03408a52
STRUrnikiSC7Dan1Urn1MinON | INT | IOD_STR_disk | I1510 | [8 empty] | 0x03408a53
STRUrnikiSC7Dan1Urn2MinON | INT | IOD_STR_disk | I1511 | [8 empty] | 0x03408a54
STRUrnikiSC7Dan1Urn3MinON | INT | IOD_STR_disk | I1512 | [8 empty] | 0x03408a55
STRUrnikiSC7Dan1Urn1MinOFF | INT | IOD_STR_disk | I1513 | [8 empty] | 0x03408a56
STRUrnikiSC7Dan1Urn2MinOFF | INT | IOD_STR_disk | I1514 | [8 empty] | 0x03408a57
STRUrnikiSC7Dan1Urn3MinOFF | INT | IOD_STR_disk | I1515 | [8 empty] | 0x03408a58
STRUrnikiSC7Dan2Urn1UraON | INT | IOD_STR_disk | I1516 | [8 empty] | 0x03408a59
STRUrnikiSC7Dan2Urn2UraON | INT | IOD_STR_disk | I1517 | [8 empty] | 0x03408a5a
STRUrnikiSC7Dan2Urn3UraON | INT | IOD_STR_disk | I1518 | [8 empty] | 0x03408a5b
STRUrnikiSC7Dan2Urn1UraOFF | INT | IOD_STR_disk | I1519 | [8 empty] | 0x03408a5c
STRUrnikiSC7Dan2Urn2UraOFF | INT | IOD_STR_disk | I1520 | [8 empty] | 0x03408a5d
STRUrnikiSC7Dan2Urn3UraOFF | INT | IOD_STR_disk | I1521 | [8 empty] | 0x03408a5e
STRUrnikiSC7Dan2Urn1MinON | INT | IOD_STR_disk | I1522 | [8 empty] | 0x03408a5f
STRUrnikiSC7Dan2Urn2MinON | INT | IOD_STR_disk | I1523 | [8 empty] | 0x03408a60
STRUrnikiSC7Dan2Urn3MinON | INT | IOD_STR_disk | I1524 | [8 empty] | 0x03408a61
STRUrnikiSC7Dan2Urn1MinOFF | INT | IOD_STR_disk | I1525 | [8 empty] | 0x03408a62
STRUrnikiSC7Dan2Urn2MinOFF | INT | IOD_STR_disk | I1526 | [8 empty] | 0x03408a63
STRUrnikiSC7Dan2Urn3MinOFF | INT | IOD_STR_disk | I1527 | [8 empty] | 0x03408a64
STRUrnikiSC7Dan3Urn1UraON | INT | IOD_STR_disk | I1528 | [8 empty] | 0x03408a65
STRUrnikiSC7Dan3Urn2UraON | INT | IOD_STR_disk | I1529 | [8 empty] | 0x03408a66
STRUrnikiSC7Dan3Urn3UraON | INT | IOD_STR_disk | I1530 | [8 empty] | 0x03408a67
STRUrnikiSC7Dan3Urn1UraOFF | INT | IOD_STR_disk | I1531 | [8 empty] | 0x03408a68
STRUrnikiSC7Dan3Urn2UraOFF | INT | IOD_STR_disk | I1532 | [8 empty] | 0x03408a69
STRUrnikiSC7Dan3Urn3UraOFF | INT | IOD_STR_disk | I1533 | [8 empty] | 0x03408a6a
STRUrnikiSC7Dan3Urn1MinON | INT | IOD_STR_disk | I1534 | [8 empty] | 0x03408a6b
STRUrnikiSC7Dan3Urn2MinON | INT | IOD_STR_disk | I1535 | [8 empty] | 0x03408a6c
STRUrnikiSC7Dan3Urn3MinON | INT | IOD_STR_disk | I1536 | [8 empty] | 0x03408a6d
STRUrnikiSC7Dan3Urn1MinOFF | INT | IOD_STR_disk | I1537 | [8 empty] | 0x03408a6e
STRUrnikiSC7Dan3Urn2MinOFF | INT | IOD_STR_disk | I1538 | [8 empty] | 0x03408a6f
STRUrnikiSC7Dan3Urn3MinOFF | INT | IOD_STR_disk | I1539 | [8 empty] | 0x03408a70
STRUrnikiSC7Dan4Urn1UraON | INT | IOD_STR_disk | I1540 | [8 empty] | 0x03408a71
STRUrnikiSC7Dan4Urn2UraON | INT | IOD_STR_disk | I1541 | [8 empty] | 0x03408a72
STRUrnikiSC7Dan4Urn3UraON | INT | IOD_STR_disk | I1542 | [8 empty] | 0x03408a73
STRUrnikiSC7Dan4Urn1UraOFF | INT | IOD_STR_disk | I1543 | [8 empty] | 0x03408a74
STRUrnikiSC7Dan4Urn2UraOFF | INT | IOD_STR_disk | I1544 | [8 empty] | 0x03408a75
STRUrnikiSC7Dan4Urn3UraOFF | INT | IOD_STR_disk | I1545 | [8 empty] | 0x03408a76
STRUrnikiSC7Dan4Urn1MinON | INT | IOD_STR_disk | I1546 | [8 empty] | 0x03408a77
STRUrnikiSC7Dan4Urn2MinON | INT | IOD_STR_disk | I1547 | [8 empty] | 0x03408a78
STRUrnikiSC7Dan4Urn3MinON | INT | IOD_STR_disk | I1548 | [8 empty] | 0x03408a79
STRUrnikiSC7Dan4Urn1MinOFF | INT | IOD_STR_disk | I1549 | [8 empty] | 0x03408a7a
STRUrnikiSC7Dan4Urn2MinOFF | INT | IOD_STR_disk | I1550 | [8 empty] | 0x03408a7b
STRUrnikiSC7Dan4Urn3MinOFF | INT | IOD_STR_disk | I1551 | [8 empty] | 0x03408a7c
STRUrnikiSC7Dan5Urn1UraON | INT | IOD_STR_disk | I1552 | [8 empty] | 0x03408a7d
STRUrnikiSC7Dan5Urn2UraON | INT | IOD_STR_disk | I1553 | [8 empty] | 0x03408a7e
STRUrnikiSC7Dan5Urn3UraON | INT | IOD_STR_disk | I1554 | [8 empty] | 0x03408a7f
STRUrnikiSC7Dan5Urn1UraOFF | INT | IOD_STR_disk | I1555 | [8 empty] | 0x03408a80
STRUrnikiSC7Dan5Urn2UraOFF | INT | IOD_STR_disk | I1556 | [8 empty] | 0x03408a81
STRUrnikiSC7Dan5Urn3UraOFF | INT | IOD_STR_disk | I1557 | [8 empty] | 0x03408a82
STRUrnikiSC7Dan5Urn1MinON | INT | IOD_STR_disk | I1558 | [8 empty] | 0x03408a83
STRUrnikiSC7Dan5Urn2MinON | INT | IOD_STR_disk | I1559 | [8 empty] | 0x03408a84
STRUrnikiSC7Dan5Urn3MinON | INT | IOD_STR_disk | I1560 | [8 empty] | 0x03408a85
STRUrnikiSC7Dan5Urn1MinOFF | INT | IOD_STR_disk | I1561 | [8 empty] | 0x03408a86
STRUrnikiSC7Dan5Urn2MinOFF | INT | IOD_STR_disk | I1562 | [8 empty] | 0x03408a87
STRUrnikiSC7Dan5Urn3MinOFF | INT | IOD_STR_disk | I1563 | [8 empty] | 0x03408a88
STRUrnikiSC7Dan6Urn1UraON | INT | IOD_STR_disk | I1564 | [8 empty] | 0x03408a89
STRUrnikiSC7Dan6Urn2UraON | INT | IOD_STR_disk | I1565 | [8 empty] | 0x03408a8a
STRUrnikiSC7Dan6Urn3UraON | INT | IOD_STR_disk | I1566 | [8 empty] | 0x03408a8b
STRUrnikiSC7Dan6Urn1UraOFF | INT | IOD_STR_disk | I1567 | [8 empty] | 0x03408a8c
STRUrnikiSC7Dan6Urn2UraOFF | INT | IOD_STR_disk | I1568 | [8 empty] | 0x03408a8d
STRUrnikiSC7Dan6Urn3UraOFF | INT | IOD_STR_disk | I1569 | [8 empty] | 0x03408a8e
STRUrnikiSC7Dan6Urn1MinON | INT | IOD_STR_disk | I1570 | [8 empty] | 0x03408a8f
STRUrnikiSC7Dan6Urn2MinON | INT | IOD_STR_disk | I1571 | [8 empty] | 0x03408a90
STRUrnikiSC7Dan6Urn3MinON | INT | IOD_STR_disk | I1572 | [8 empty] | 0x03408a91
STRUrnikiSC7Dan6Urn1MinOFF | INT | IOD_STR_disk | I1573 | [8 empty] | 0x03408a92
STRUrnikiSC7Dan6Urn2MinOFF | INT | IOD_STR_disk | I1574 | [8 empty] | 0x03408a93
STRUrnikiSC7Dan6Urn3MinOFF | INT | IOD_STR_disk | I1575 | [8 empty] | 0x03408a94
STRUrnikiSC7Dan7Urn1UraON | INT | IOD_STR_disk | I1576 | [8 empty] | 0x03408a95
STRUrnikiSC7Dan7Urn2UraON | INT | IOD_STR_disk | I1577 | [8 empty] | 0x03408a96
STRUrnikiSC7Dan7Urn3UraON | INT | IOD_STR_disk | I1578 | [8 empty] | 0x03408a97
STRUrnikiSC7Dan7Urn1UraOFF | INT | IOD_STR_disk | I1579 | [8 empty] | 0x03408a98
STRUrnikiSC7Dan7Urn2UraOFF | INT | IOD_STR_disk | I1580 | [8 empty] | 0x03408a99
STRUrnikiSC7Dan7Urn3UraOFF | INT | IOD_STR_disk | I1581 | [8 empty] | 0x03408a9a
STRUrnikiSC7Dan7Urn1MinON | INT | IOD_STR_disk | I1582 | [8 empty] | 0x03408a9b
STRUrnikiSC7Dan7Urn2MinON | INT | IOD_STR_disk | I1583 | [8 empty] | 0x03408a9c
STRUrnikiSC7Dan7Urn3MinON | INT | IOD_STR_disk | I1584 | [8 empty] | 0x03408a9d
STRUrnikiSC7Dan7Urn1MinOFF | INT | IOD_STR_disk | I1585 | [8 empty] | 0x03408a9e
STRUrnikiSC7Dan7Urn2MinOFF | INT | IOD_STR_disk | I1586 | [8 empty] | 0x03408a9f
STRUrnikiSC7Dan7Urn3MinOFF | INT | IOD_STR_disk | I1587 | [8 empty] | 0x03408aa0
STRUrnikiSC8Dan1Urn1UraON | INT | IOD_STR_disk | I1588 | [8 empty] | 0x03408aa1
STRUrnikiSC8Dan1Urn2UraON | INT | IOD_STR_disk | I1589 | [8 empty] | 0x03408aa2
STRUrnikiSC8Dan1Urn3UraON | INT | IOD_STR_disk | I1590 | [8 empty] | 0x03408aa3
STRUrnikiSC8Dan1Urn1UraOFF | INT | IOD_STR_disk | I1591 | [8 empty] | 0x03408aa4
STRUrnikiSC8Dan1Urn2UraOFF | INT | IOD_STR_disk | I1592 | [8 empty] | 0x03408aa5
STRUrnikiSC8Dan1Urn3UraOFF | INT | IOD_STR_disk | I1593 | [8 empty] | 0x03408aa6
STRUrnikiSC8Dan1Urn1MinON | INT | IOD_STR_disk | I1594 | [8 empty] | 0x03408aa7
STRUrnikiSC8Dan1Urn2MinON | INT | IOD_STR_disk | I1595 | [8 empty] | 0x03408aa8
STRUrnikiSC8Dan1Urn3MinON | INT | IOD_STR_disk | I1596 | [8 empty] | 0x03408aa9
STRUrnikiSC8Dan1Urn1MinOFF | INT | IOD_STR_disk | I1597 | [8 empty] | 0x03408aaa
STRUrnikiSC8Dan1Urn2MinOFF | INT | IOD_STR_disk | I1598 | [8 empty] | 0x03408aab
STRUrnikiSC8Dan1Urn3MinOFF | INT | IOD_STR_disk | I1599 | [8 empty] | 0x03408aac
STRUrnikiSC8Dan2Urn1UraON | INT | IOD_STR_disk | I1600 | [8 empty] | 0x03408aad
STRUrnikiSC8Dan2Urn2UraON | INT | IOD_STR_disk | I1601 | [8 empty] | 0x03408aae
STRUrnikiSC8Dan2Urn3UraON | INT | IOD_STR_disk | I1602 | [8 empty] | 0x03408aaf
STRUrnikiSC8Dan2Urn1UraOFF | INT | IOD_STR_disk | I1603 | [8 empty] | 0x03408ab0
STRUrnikiSC8Dan2Urn2UraOFF | INT | IOD_STR_disk | I1604 | [8 empty] | 0x03408ab1
STRUrnikiSC8Dan2Urn3UraOFF | INT | IOD_STR_disk | I1605 | [8 empty] | 0x03408ab2
STRUrnikiSC8Dan2Urn1MinON | INT | IOD_STR_disk | I1606 | [8 empty] | 0x03408ab3
STRUrnikiSC8Dan2Urn2MinON | INT | IOD_STR_disk | I1607 | [8 empty] | 0x03408ab4
STRUrnikiSC8Dan2Urn3MinON | INT | IOD_STR_disk | I1608 | [8 empty] | 0x03408ab5
STRUrnikiSC8Dan2Urn1MinOFF | INT | IOD_STR_disk | I1609 | [8 empty] | 0x03408ab6
STRUrnikiSC8Dan2Urn2MinOFF | INT | IOD_STR_disk | I1610 | [8 empty] | 0x03408ab7
STRUrnikiSC8Dan2Urn3MinOFF | INT | IOD_STR_disk | I1611 | [8 empty] | 0x03408ab8
STRUrnikiSC8Dan3Urn1UraON | INT | IOD_STR_disk | I1612 | [8 empty] | 0x03408ab9
STRUrnikiSC8Dan3Urn2UraON | INT | IOD_STR_disk | I1613 | [8 empty] | 0x03408aba
STRUrnikiSC8Dan3Urn3UraON | INT | IOD_STR_disk | I1614 | [8 empty] | 0x03408abb
STRUrnikiSC8Dan3Urn1UraOFF | INT | IOD_STR_disk | I1615 | [8 empty] | 0x03408abc
STRUrnikiSC8Dan3Urn2UraOFF | INT | IOD_STR_disk | I1616 | [8 empty] | 0x03408abd
STRUrnikiSC8Dan3Urn3UraOFF | INT | IOD_STR_disk | I1617 | [8 empty] | 0x03408abe
STRUrnikiSC8Dan3Urn1MinON | INT | IOD_STR_disk | I1618 | [8 empty] | 0x03408abf
STRUrnikiSC8Dan3Urn2MinON | INT | IOD_STR_disk | I1619 | [8 empty] | 0x03408ac0
STRUrnikiSC8Dan3Urn3MinON | INT | IOD_STR_disk | I1620 | [8 empty] | 0x03408ac1
STRUrnikiSC8Dan3Urn1MinOFF | INT | IOD_STR_disk | I1621 | [8 empty] | 0x03408ac2
STRUrnikiSC8Dan3Urn2MinOFF | INT | IOD_STR_disk | I1622 | [8 empty] | 0x03408ac3
STRUrnikiSC8Dan3Urn3MinOFF | INT | IOD_STR_disk | I1623 | [8 empty] | 0x03408ac4
STRUrnikiSC8Dan4Urn1UraON | INT | IOD_STR_disk | I1624 | [8 empty] | 0x03408ac5
STRUrnikiSC8Dan4Urn2UraON | INT | IOD_STR_disk | I1625 | [8 empty] | 0x03408ac6
STRUrnikiSC8Dan4Urn3UraON | INT | IOD_STR_disk | I1626 | [8 empty] | 0x03408ac7
STRUrnikiSC8Dan4Urn1UraOFF | INT | IOD_STR_disk | I1627 | [8 empty] | 0x03408ac8
STRUrnikiSC8Dan4Urn2UraOFF | INT | IOD_STR_disk | I1628 | [8 empty] | 0x03408ac9
STRUrnikiSC8Dan4Urn3UraOFF | INT | IOD_STR_disk | I1629 | [8 empty] | 0x03408aca
STRUrnikiSC8Dan4Urn1MinON | INT | IOD_STR_disk | I1630 | [8 empty] | 0x03408acb
STRUrnikiSC8Dan4Urn2MinON | INT | IOD_STR_disk | I1631 | [8 empty] | 0x03408acc
STRUrnikiSC8Dan4Urn3MinON | INT | IOD_STR_disk | I1632 | [8 empty] | 0x03408acd
STRUrnikiSC8Dan4Urn1MinOFF | INT | IOD_STR_disk | I1633 | [8 empty] | 0x03408ace
STRUrnikiSC8Dan4Urn2MinOFF | INT | IOD_STR_disk | I1634 | [8 empty] | 0x03408acf
STRUrnikiSC8Dan4Urn3MinOFF | INT | IOD_STR_disk | I1635 | [8 empty] | 0x03408ad0
STRUrnikiSC8Dan5Urn1UraON | INT | IOD_STR_disk | I1636 | [8 empty] | 0x03408ad1
STRUrnikiSC8Dan5Urn2UraON | INT | IOD_STR_disk | I1637 | [8 empty] | 0x03408ad2
STRUrnikiSC8Dan5Urn3UraON | INT | IOD_STR_disk | I1638 | [8 empty] | 0x03408ad3
STRUrnikiSC8Dan5Urn1UraOFF | INT | IOD_STR_disk | I1639 | [8 empty] | 0x03408ad4
STRUrnikiSC8Dan5Urn2UraOFF | INT | IOD_STR_disk | I1640 | [8 empty] | 0x03408ad5
STRUrnikiSC8Dan5Urn3UraOFF | INT | IOD_STR_disk | I1641 | [8 empty] | 0x03408ad6
STRUrnikiSC8Dan5Urn1MinON | INT | IOD_STR_disk | I1642 | [8 empty] | 0x03408ad7
STRUrnikiSC8Dan5Urn2MinON | INT | IOD_STR_disk | I1643 | [8 empty] | 0x03408ad8
STRUrnikiSC8Dan5Urn3MinON | INT | IOD_STR_disk | I1644 | [8 empty] | 0x03408ad9
STRUrnikiSC8Dan5Urn1MinOFF | INT | IOD_STR_disk | I1645 | [8 empty] | 0x03408ada
STRUrnikiSC8Dan5Urn2MinOFF | INT | IOD_STR_disk | I1646 | [8 empty] | 0x03408adb
STRUrnikiSC8Dan5Urn3MinOFF | INT | IOD_STR_disk | I1647 | [8 empty] | 0x03408adc
STRUrnikiSC8Dan6Urn1UraON | INT | IOD_STR_disk | I1648 | [8 empty] | 0x03408add
STRUrnikiSC8Dan6Urn2UraON | INT | IOD_STR_disk | I1649 | [8 empty] | 0x03408ade
STRUrnikiSC8Dan6Urn3UraON | INT | IOD_STR_disk | I1650 | [8 empty] | 0x03408adf
STRUrnikiSC8Dan6Urn1UraOFF | INT | IOD_STR_disk | I1651 | [8 empty] | 0x03408ae0
STRUrnikiSC8Dan6Urn2UraOFF | INT | IOD_STR_disk | I1652 | [8 empty] | 0x03408ae1
STRUrnikiSC8Dan6Urn3UraOFF | INT | IOD_STR_disk | I1653 | [8 empty] | 0x03408ae2
STRUrnikiSC8Dan6Urn1MinON | INT | IOD_STR_disk | I1654 | [8 empty] | 0x03408ae3
STRUrnikiSC8Dan6Urn2MinON | INT | IOD_STR_disk | I1655 | [8 empty] | 0x03408ae4
STRUrnikiSC8Dan6Urn3MinON | INT | IOD_STR_disk | I1656 | [8 empty] | 0x03408ae5
STRUrnikiSC8Dan6Urn1MinOFF | INT | IOD_STR_disk | I1657 | [8 empty] | 0x03408ae6
STRUrnikiSC8Dan6Urn2MinOFF | INT | IOD_STR_disk | I1658 | [8 empty] | 0x03408ae7
STRUrnikiSC8Dan6Urn3MinOFF | INT | IOD_STR_disk | I1659 | [8 empty] | 0x03408ae8
STRUrnikiSC8Dan7Urn1UraON | INT | IOD_STR_disk | I1660 | [8 empty] | 0x03408ae9
STRUrnikiSC8Dan7Urn2UraON | INT | IOD_STR_disk | I1661 | [8 empty] | 0x03408aea
STRUrnikiSC8Dan7Urn3UraON | INT | IOD_STR_disk | I1662 | [8 empty] | 0x03408aeb
STRUrnikiSC8Dan7Urn1UraOFF | INT | IOD_STR_disk | I1663 | [8 empty] | 0x03408aec
STRUrnikiSC8Dan7Urn2UraOFF | INT | IOD_STR_disk | I1664 | [8 empty] | 0x03408aed
STRUrnikiSC8Dan7Urn3UraOFF | INT | IOD_STR_disk | I1665 | [8 empty] | 0x03408aee
STRUrnikiSC8Dan7Urn1MinON | INT | IOD_STR_disk | I1666 | [8 empty] | 0x03408aef
STRUrnikiSC8Dan7Urn2MinON | INT | IOD_STR_disk | I1667 | [8 empty] | 0x03408af0
STRUrnikiSC8Dan7Urn3MinON | INT | IOD_STR_disk | I1668 | [8 empty] | 0x03408af1
STRUrnikiSC8Dan7Urn1MinOFF | INT | IOD_STR_disk | I1669 | [8 empty] | 0x03408af2
STRUrnikiSC8Dan7Urn2MinOFF | INT | IOD_STR_disk | I1670 | [8 empty] | 0x03408af3
STRUrnikiSC8Dan7Urn3MinOFF | INT | IOD_STR_disk | I1671 | [8 empty] | 0x03408af4
STRUrnikiSC9Dan1Urn1UraON | INT | IOD_STR_disk | I1672 | [8 empty] | 0x03408af5
STRUrnikiSC9Dan1Urn2UraON | INT | IOD_STR_disk | I1673 | [8 empty] | 0x03408af6
STRUrnikiSC9Dan1Urn3UraON | INT | IOD_STR_disk | I1674 | [8 empty] | 0x03408af7
STRUrnikiSC9Dan1Urn1UraOFF | INT | IOD_STR_disk | I1675 | [8 empty] | 0x03408af8
STRUrnikiSC9Dan1Urn2UraOFF | INT | IOD_STR_disk | I1676 | [8 empty] | 0x03408af9
STRUrnikiSC9Dan1Urn3UraOFF | INT | IOD_STR_disk | I1677 | [8 empty] | 0x03408afa
STRUrnikiSC9Dan1Urn1MinON | INT | IOD_STR_disk | I1678 | [8 empty] | 0x03408afb
STRUrnikiSC9Dan1Urn2MinON | INT | IOD_STR_disk | I1679 | [8 empty] | 0x03408afc
STRUrnikiSC9Dan1Urn3MinON | INT | IOD_STR_disk | I1680 | [8 empty] | 0x03408afd
STRUrnikiSC9Dan1Urn1MinOFF | INT | IOD_STR_disk | I1681 | [8 empty] | 0x03408afe
STRUrnikiSC9Dan1Urn2MinOFF | INT | IOD_STR_disk | I1682 | [8 empty] | 0x03408aff
STRUrnikiSC9Dan1Urn3MinOFF | INT | IOD_STR_disk | I1683 | [8 empty] | 0x03408b00
STRUrnikiSC9Dan2Urn1UraON | INT | IOD_STR_disk | I1684 | [8 empty] | 0x03408b01
STRUrnikiSC9Dan2Urn2UraON | INT | IOD_STR_disk | I1685 | [8 empty] | 0x03408b02
STRUrnikiSC9Dan2Urn3UraON | INT | IOD_STR_disk | I1686 | [8 empty] | 0x03408b03
STRUrnikiSC9Dan2Urn1UraOFF | INT | IOD_STR_disk | I1687 | [8 empty] | 0x03408b04
STRUrnikiSC9Dan2Urn2UraOFF | INT | IOD_STR_disk | I1688 | [8 empty] | 0x03408b05
STRUrnikiSC9Dan2Urn3UraOFF | INT | IOD_STR_disk | I1689 | [8 empty] | 0x03408b06
STRUrnikiSC9Dan2Urn1MinON | INT | IOD_STR_disk | I1690 | [8 empty] | 0x03408b07
STRUrnikiSC9Dan2Urn2MinON | INT | IOD_STR_disk | I1691 | [8 empty] | 0x03408b08
STRUrnikiSC9Dan2Urn3MinON | INT | IOD_STR_disk | I1692 | [8 empty] | 0x03408b09
STRUrnikiSC9Dan2Urn1MinOFF | INT | IOD_STR_disk | I1693 | [8 empty] | 0x03408b0a
STRUrnikiSC9Dan2Urn2MinOFF | INT | IOD_STR_disk | I1694 | [8 empty] | 0x03408b0b
STRUrnikiSC9Dan2Urn3MinOFF | INT | IOD_STR_disk | I1695 | [8 empty] | 0x03408b0c
STRUrnikiSC9Dan3Urn1UraON | INT | IOD_STR_disk | I1696 | [8 empty] | 0x03408b0d
STRUrnikiSC9Dan3Urn2UraON | INT | IOD_STR_disk | I1697 | [8 empty] | 0x03408b0e
STRUrnikiSC9Dan3Urn3UraON | INT | IOD_STR_disk | I1698 | [8 empty] | 0x03408b0f
STRUrnikiSC9Dan3Urn1UraOFF | INT | IOD_STR_disk | I1699 | [8 empty] | 0x03408b10
STRUrnikiSC9Dan3Urn2UraOFF | INT | IOD_STR_disk | I1700 | [8 empty] | 0x03408b11
STRUrnikiSC9Dan3Urn3UraOFF | INT | IOD_STR_disk | I1701 | [8 empty] | 0x03408b12
STRUrnikiSC9Dan3Urn1MinON | INT | IOD_STR_disk | I1702 | [8 empty] | 0x03408b13
STRUrnikiSC9Dan3Urn2MinON | INT | IOD_STR_disk | I1703 | [8 empty] | 0x03408b14
STRUrnikiSC9Dan3Urn3MinON | INT | IOD_STR_disk | I1704 | [8 empty] | 0x03408b15
STRUrnikiSC9Dan3Urn1MinOFF | INT | IOD_STR_disk | I1705 | [8 empty] | 0x03408b16
STRUrnikiSC9Dan3Urn2MinOFF | INT | IOD_STR_disk | I1706 | [8 empty] | 0x03408b17
STRUrnikiSC9Dan3Urn3MinOFF | INT | IOD_STR_disk | I1707 | [8 empty] | 0x03408b18
STRUrnikiSC9Dan4Urn1UraON | INT | IOD_STR_disk | I1708 | [8 empty] | 0x03408b19
STRUrnikiSC9Dan4Urn2UraON | INT | IOD_STR_disk | I1709 | [8 empty] | 0x03408b1a
STRUrnikiSC9Dan4Urn3UraON | INT | IOD_STR_disk | I1710 | [8 empty] | 0x03408b1b
STRUrnikiSC9Dan4Urn1UraOFF | INT | IOD_STR_disk | I1711 | [8 empty] | 0x03408b1c
STRUrnikiSC9Dan4Urn2UraOFF | INT | IOD_STR_disk | I1712 | [8 empty] | 0x03408b1d
STRUrnikiSC9Dan4Urn3UraOFF | INT | IOD_STR_disk | I1713 | [8 empty] | 0x03408b1e
STRUrnikiSC9Dan4Urn1MinON | INT | IOD_STR_disk | I1714 | [8 empty] | 0x03408b1f
STRUrnikiSC9Dan4Urn2MinON | INT | IOD_STR_disk | I1715 | [8 empty] | 0x03408b20
STRUrnikiSC9Dan4Urn3MinON | INT | IOD_STR_disk | I1716 | [8 empty] | 0x03408b21
STRUrnikiSC9Dan4Urn1MinOFF | INT | IOD_STR_disk | I1717 | [8 empty] | 0x03408b22
STRUrnikiSC9Dan4Urn2MinOFF | INT | IOD_STR_disk | I1718 | [8 empty] | 0x03408b23
STRUrnikiSC9Dan4Urn3MinOFF | INT | IOD_STR_disk | I1719 | [8 empty] | 0x03408b24
STRUrnikiSC9Dan5Urn1UraON | INT | IOD_STR_disk | I1720 | [8 empty] | 0x03408b25
STRUrnikiSC9Dan5Urn2UraON | INT | IOD_STR_disk | I1721 | [8 empty] | 0x03408b26
STRUrnikiSC9Dan5Urn3UraON | INT | IOD_STR_disk | I1722 | [8 empty] | 0x03408b27
STRUrnikiSC9Dan5Urn1UraOFF | INT | IOD_STR_disk | I1723 | [8 empty] | 0x03408b28
STRUrnikiSC9Dan5Urn2UraOFF | INT | IOD_STR_disk | I1724 | [8 empty] | 0x03408b29
STRUrnikiSC9Dan5Urn3UraOFF | INT | IOD_STR_disk | I1725 | [8 empty] | 0x03408b2a
STRUrnikiSC9Dan5Urn1MinON | INT | IOD_STR_disk | I1726 | [8 empty] | 0x03408b2b
STRUrnikiSC9Dan5Urn2MinON | INT | IOD_STR_disk | I1727 | [8 empty] | 0x03408b2c
STRUrnikiSC9Dan5Urn3MinON | INT | IOD_STR_disk | I1728 | [8 empty] | 0x03408b2d
STRUrnikiSC9Dan5Urn1MinOFF | INT | IOD_STR_disk | I1729 | [8 empty] | 0x03408b2e
STRUrnikiSC9Dan5Urn2MinOFF | INT | IOD_STR_disk | I1730 | [8 empty] | 0x03408b2f
STRUrnikiSC9Dan5Urn3MinOFF | INT | IOD_STR_disk | I1731 | [8 empty] | 0x03408b30
STRUrnikiSC9Dan6Urn1UraON | INT | IOD_STR_disk | I1732 | [8 empty] | 0x03408b31
STRUrnikiSC9Dan6Urn2UraON | INT | IOD_STR_disk | I1733 | [8 empty] | 0x03408b32
STRUrnikiSC9Dan6Urn3UraON | INT | IOD_STR_disk | I1734 | [8 empty] | 0x03408b33
STRUrnikiSC9Dan6Urn1UraOFF | INT | IOD_STR_disk | I1735 | [8 empty] | 0x03408b34
STRUrnikiSC9Dan6Urn2UraOFF | INT | IOD_STR_disk | I1736 | [8 empty] | 0x03408b35
STRUrnikiSC9Dan6Urn3UraOFF | INT | IOD_STR_disk | I1737 | [8 empty] | 0x03408b36
STRUrnikiSC9Dan6Urn1MinON | INT | IOD_STR_disk | I1738 | [8 empty] | 0x03408b37
STRUrnikiSC9Dan6Urn2MinON | INT | IOD_STR_disk | I1739 | [8 empty] | 0x03408b38
STRUrnikiSC9Dan6Urn3MinON | INT | IOD_STR_disk | I1740 | [8 empty] | 0x03408b39
STRUrnikiSC9Dan6Urn1MinOFF | INT | IOD_STR_disk | I1741 | [8 empty] | 0x03408b3a
STRUrnikiSC9Dan6Urn2MinOFF | INT | IOD_STR_disk | I1742 | [8 empty] | 0x03408b3b
STRUrnikiSC9Dan6Urn3MinOFF | INT | IOD_STR_disk | I1743 | [8 empty] | 0x03408b3c
STRUrnikiSC9Dan7Urn1UraON | INT | IOD_STR_disk | I1744 | [8 empty] | 0x03408b3d
STRUrnikiSC9Dan7Urn2UraON | INT | IOD_STR_disk | I1745 | [8 empty] | 0x03408b3e
STRUrnikiSC9Dan7Urn3UraON | INT | IOD_STR_disk | I1746 | [8 empty] | 0x03408b3f
STRUrnikiSC9Dan7Urn1UraOFF | INT | IOD_STR_disk | I1747 | [8 empty] | 0x03408b40
STRUrnikiSC9Dan7Urn2UraOFF | INT | IOD_STR_disk | I1748 | [8 empty] | 0x03408b41
STRUrnikiSC9Dan7Urn3UraOFF | INT | IOD_STR_disk | I1749 | [8 empty] | 0x03408b42
STRUrnikiSC9Dan7Urn1MinON | INT | IOD_STR_disk | I1750 | [8 empty] | 0x03408b43
STRUrnikiSC9Dan7Urn2MinON | INT | IOD_STR_disk | I1751 | [8 empty] | 0x03408b44
STRUrnikiSC9Dan7Urn3MinON | INT | IOD_STR_disk | I1752 | [8 empty] | 0x03408b45
STRUrnikiSC9Dan7Urn1MinOFF | INT | IOD_STR_disk | I1753 | [8 empty] | 0x03408b46
STRUrnikiSC9Dan7Urn2MinOFF | INT | IOD_STR_disk | I1754 | [8 empty] | 0x03408b47
STRUrnikiSC9Dan7Urn3MinOFF | INT | IOD_STR_disk | I1755 | [8 empty] | 0x03408b48
STRUrnikiSC10Dan1Urn1UraON | INT | IOD_STR_disk | I1756 | [8 empty] | 0x03408b49
STRUrnikiSC10Dan1Urn2UraON | INT | IOD_STR_disk | I1757 | [8 empty] | 0x03408b4a
STRUrnikiSC10Dan1Urn3UraON | INT | IOD_STR_disk | I1758 | [8 empty] | 0x03408b4b
STRUrnikiSC10Dan1Urn1UraOFF | INT | IOD_STR_disk | I1759 | [8 empty] | 0x03408b4c
STRUrnikiSC10Dan1Urn2UraOFF | INT | IOD_STR_disk | I1760 | [8 empty] | 0x03408b4d
STRUrnikiSC10Dan1Urn3UraOFF | INT | IOD_STR_disk | I1761 | [8 empty] | 0x03408b4e
STRUrnikiSC10Dan1Urn1MinON | INT | IOD_STR_disk | I1762 | [8 empty] | 0x03408b4f
STRUrnikiSC10Dan1Urn2MinON | INT | IOD_STR_disk | I1763 | [8 empty] | 0x03408b50
STRUrnikiSC10Dan1Urn3MinON | INT | IOD_STR_disk | I1764 | [8 empty] | 0x03408b51
STRUrnikiSC10Dan1Urn1MinOFF | INT | IOD_STR_disk | I1765 | [8 empty] | 0x03408b52
STRUrnikiSC10Dan1Urn2MinOFF | INT | IOD_STR_disk | I1766 | [8 empty] | 0x03408b53
STRUrnikiSC10Dan1Urn3MinOFF | INT | IOD_STR_disk | I1767 | [8 empty] | 0x03408b54
STRUrnikiSC10Dan2Urn1UraON | INT | IOD_STR_disk | I1768 | [8 empty] | 0x03408b55
STRUrnikiSC10Dan2Urn2UraON | INT | IOD_STR_disk | I1769 | [8 empty] | 0x03408b56
STRUrnikiSC10Dan2Urn3UraON | INT | IOD_STR_disk | I1770 | [8 empty] | 0x03408b57
STRUrnikiSC10Dan2Urn1UraOFF | INT | IOD_STR_disk | I1771 | [8 empty] | 0x03408b58
STRUrnikiSC10Dan2Urn2UraOFF | INT | IOD_STR_disk | I1772 | [8 empty] | 0x03408b59
STRUrnikiSC10Dan2Urn3UraOFF | INT | IOD_STR_disk | I1773 | [8 empty] | 0x03408b5a
STRUrnikiSC10Dan2Urn1MinON | INT | IOD_STR_disk | I1774 | [8 empty] | 0x03408b5b
STRUrnikiSC10Dan2Urn2MinON | INT | IOD_STR_disk | I1775 | [8 empty] | 0x03408b5c
STRUrnikiSC10Dan2Urn3MinON | INT | IOD_STR_disk | I1776 | [8 empty] | 0x03408b5d
STRUrnikiSC10Dan2Urn1MinOFF | INT | IOD_STR_disk | I1777 | [8 empty] | 0x03408b5e
STRUrnikiSC10Dan2Urn2MinOFF | INT | IOD_STR_disk | I1778 | [8 empty] | 0x03408b5f
STRUrnikiSC10Dan2Urn3MinOFF | INT | IOD_STR_disk | I1779 | [8 empty] | 0x03408b60
STRUrnikiSC10Dan3Urn1UraON | INT | IOD_STR_disk | I1780 | [8 empty] | 0x03408b61
STRUrnikiSC10Dan3Urn2UraON | INT | IOD_STR_disk | I1781 | [8 empty] | 0x03408b62
STRUrnikiSC10Dan3Urn3UraON | INT | IOD_STR_disk | I1782 | [8 empty] | 0x03408b63
STRUrnikiSC10Dan3Urn1UraOFF | INT | IOD_STR_disk | I1783 | [8 empty] | 0x03408b64
STRUrnikiSC10Dan3Urn2UraOFF | INT | IOD_STR_disk | I1784 | [8 empty] | 0x03408b65
STRUrnikiSC10Dan3Urn3UraOFF | INT | IOD_STR_disk | I1785 | [8 empty] | 0x03408b66
STRUrnikiSC10Dan3Urn1MinON | INT | IOD_STR_disk | I1786 | [8 empty] | 0x03408b67
STRUrnikiSC10Dan3Urn2MinON | INT | IOD_STR_disk | I1787 | [8 empty] | 0x03408b68
STRUrnikiSC10Dan3Urn3MinON | INT | IOD_STR_disk | I1788 | [8 empty] | 0x03408b69
STRUrnikiSC10Dan3Urn1MinOFF | INT | IOD_STR_disk | I1789 | [8 empty] | 0x03408b6a
STRUrnikiSC10Dan3Urn2MinOFF | INT | IOD_STR_disk | I1790 | [8 empty] | 0x03408b6b
STRUrnikiSC10Dan3Urn3MinOFF | INT | IOD_STR_disk | I1791 | [8 empty] | 0x03408b6c
STRUrnikiSC10Dan4Urn1UraON | INT | IOD_STR_disk | I1792 | [8 empty] | 0x03408b6d
STRUrnikiSC10Dan4Urn2UraON | INT | IOD_STR_disk | I1793 | [8 empty] | 0x03408b6e
STRUrnikiSC10Dan4Urn3UraON | INT | IOD_STR_disk | I1794 | [8 empty] | 0x03408b6f
STRUrnikiSC10Dan4Urn1UraOFF | INT | IOD_STR_disk | I1795 | [8 empty] | 0x03408b70
STRUrnikiSC10Dan4Urn2UraOFF | INT | IOD_STR_disk | I1796 | [8 empty] | 0x03408b71
STRUrnikiSC10Dan4Urn3UraOFF | INT | IOD_STR_disk | I1797 | [8 empty] | 0x03408b72
STRUrnikiSC10Dan4Urn1MinON | INT | IOD_STR_disk | I1798 | [8 empty] | 0x03408b73
STRUrnikiSC10Dan4Urn2MinON | INT | IOD_STR_disk | I1799 | [8 empty] | 0x03408b74
STRUrnikiSC10Dan4Urn3MinON | INT | IOD_STR_disk | I1800 | [8 empty] | 0x03408b75
STRUrnikiSC10Dan4Urn1MinOFF | INT | IOD_STR_disk | I1801 | [8 empty] | 0x03408b76
STRUrnikiSC10Dan4Urn2MinOFF | INT | IOD_STR_disk | I1802 | [8 empty] | 0x03408b77
STRUrnikiSC10Dan4Urn3MinOFF | INT | IOD_STR_disk | I1803 | [8 empty] | 0x03408b78
STRUrnikiSC10Dan5Urn1UraON | INT | IOD_STR_disk | I1804 | [8 empty] | 0x03408b79
STRUrnikiSC10Dan5Urn2UraON | INT | IOD_STR_disk | I1805 | [8 empty] | 0x03408b7a
STRUrnikiSC10Dan5Urn3UraON | INT | IOD_STR_disk | I1806 | [8 empty] | 0x03408b7b
STRUrnikiSC10Dan5Urn1UraOFF | INT | IOD_STR_disk | I1807 | [8 empty] | 0x03408b7c
STRUrnikiSC10Dan5Urn2UraOFF | INT | IOD_STR_disk | I1808 | [8 empty] | 0x03408b7d
STRUrnikiSC10Dan5Urn3UraOFF | INT | IOD_STR_disk | I1809 | [8 empty] | 0x03408b7e
STRUrnikiSC10Dan5Urn1MinON | INT | IOD_STR_disk | I1810 | [8 empty] | 0x03408b7f
STRUrnikiSC10Dan5Urn2MinON | INT | IOD_STR_disk | I1811 | [8 empty] | 0x03408b80
STRUrnikiSC10Dan5Urn3MinON | INT | IOD_STR_disk | I1812 | [8 empty] | 0x03408b81
STRUrnikiSC10Dan5Urn1MinOFF | INT | IOD_STR_disk | I1813 | [8 empty] | 0x03408b82
STRUrnikiSC10Dan5Urn2MinOFF | INT | IOD_STR_disk | I1814 | [8 empty] | 0x03408b83
STRUrnikiSC10Dan5Urn3MinOFF | INT | IOD_STR_disk | I1815 | [8 empty] | 0x03408b84
STRUrnikiSC10Dan6Urn1UraON | INT | IOD_STR_disk | I1816 | [8 empty] | 0x03408b85
STRUrnikiSC10Dan6Urn2UraON | INT | IOD_STR_disk | I1817 | [8 empty] | 0x03408b86
STRUrnikiSC10Dan6Urn3UraON | INT | IOD_STR_disk | I1818 | [8 empty] | 0x03408b87
STRUrnikiSC10Dan6Urn1UraOFF | INT | IOD_STR_disk | I1819 | [8 empty] | 0x03408b88
STRUrnikiSC10Dan6Urn2UraOFF | INT | IOD_STR_disk | I1820 | [8 empty] | 0x03408b89
STRUrnikiSC10Dan6Urn3UraOFF | INT | IOD_STR_disk | I1821 | [8 empty] | 0x03408b8a
STRUrnikiSC10Dan6Urn1MinON | INT | IOD_STR_disk | I1822 | [8 empty] | 0x03408b8b
STRUrnikiSC10Dan6Urn2MinON | INT | IOD_STR_disk | I1823 | [8 empty] | 0x03408b8c
STRUrnikiSC10Dan6Urn3MinON | INT | IOD_STR_disk | I1824 | [8 empty] | 0x03408b8d
STRUrnikiSC10Dan6Urn1MinOFF | INT | IOD_STR_disk | I1825 | [8 empty] | 0x03408b8e
STRUrnikiSC10Dan6Urn2MinOFF | INT | IOD_STR_disk | I1826 | [8 empty] | 0x03408b8f
STRUrnikiSC10Dan6Urn3MinOFF | INT | IOD_STR_disk | I1827 | [8 empty] | 0x03408b90
STRUrnikiSC10Dan7Urn1UraON | INT | IOD_STR_disk | I1828 | [8 empty] | 0x03408b91
STRUrnikiSC10Dan7Urn2UraON | INT | IOD_STR_disk | I1829 | [8 empty] | 0x03408b92
STRUrnikiSC10Dan7Urn3UraON | INT | IOD_STR_disk | I1830 | [8 empty] | 0x03408b93
STRUrnikiSC10Dan7Urn1UraOFF | INT | IOD_STR_disk | I1831 | [8 empty] | 0x03408b94
STRUrnikiSC10Dan7Urn2UraOFF | INT | IOD_STR_disk | I1832 | [8 empty] | 0x03408b95
STRUrnikiSC10Dan7Urn3UraOFF | INT | IOD_STR_disk | I1833 | [8 empty] | 0x03408b96
STRUrnikiSC10Dan7Urn1MinON | INT | IOD_STR_disk | I1834 | [8 empty] | 0x03408b97
STRUrnikiSC10Dan7Urn2MinON | INT | IOD_STR_disk | I1835 | [8 empty] | 0x03408b98
STRUrnikiSC10Dan7Urn3MinON | INT | IOD_STR_disk | I1836 | [8 empty] | 0x03408b99
STRUrnikiSC10Dan7Urn1MinOFF | INT | IOD_STR_disk | I1837 | [8 empty] | 0x03408b9a
STRUrnikiSC10Dan7Urn2MinOFF | INT | IOD_STR_disk | I1838 | [8 empty] | 0x03408b9b
STRUrnikiSC10Dan7Urn3MinOFF | INT | IOD_STR_disk | I1839 | [8 empty] | 0x03408b9c
STRUrnikiSC11Dan1Urn1UraON | INT | IOD_STR_disk | I1840 | [8 empty] | 0x03408b9d
STRUrnikiSC11Dan1Urn2UraON | INT | IOD_STR_disk | I1841 | [8 empty] | 0x03408b9e
STRUrnikiSC11Dan1Urn3UraON | INT | IOD_STR_disk | I1842 | [8 empty] | 0x03408b9f
STRUrnikiSC11Dan1Urn1UraOFF | INT | IOD_STR_disk | I1843 | [8 empty] | 0x03408ba0
STRUrnikiSC11Dan1Urn2UraOFF | INT | IOD_STR_disk | I1844 | [8 empty] | 0x03408ba1
STRUrnikiSC11Dan1Urn3UraOFF | INT | IOD_STR_disk | I1845 | [8 empty] | 0x03408ba2
STRUrnikiSC11Dan1Urn1MinON | INT | IOD_STR_disk | I1846 | [8 empty] | 0x03408ba3
STRUrnikiSC11Dan1Urn2MinON | INT | IOD_STR_disk | I1847 | [8 empty] | 0x03408ba4
STRUrnikiSC11Dan1Urn3MinON | INT | IOD_STR_disk | I1848 | [8 empty] | 0x03408ba5
STRUrnikiSC11Dan1Urn1MinOFF | INT | IOD_STR_disk | I1849 | [8 empty] | 0x03408ba6
STRUrnikiSC11Dan1Urn2MinOFF | INT | IOD_STR_disk | I1850 | [8 empty] | 0x03408ba7
STRUrnikiSC11Dan1Urn3MinOFF | INT | IOD_STR_disk | I1851 | [8 empty] | 0x03408ba8
STRUrnikiSC11Dan2Urn1UraON | INT | IOD_STR_disk | I1852 | [8 empty] | 0x03408ba9
STRUrnikiSC11Dan2Urn2UraON | INT | IOD_STR_disk | I1853 | [8 empty] | 0x03408baa
STRUrnikiSC11Dan2Urn3UraON | INT | IOD_STR_disk | I1854 | [8 empty] | 0x03408bab
STRUrnikiSC11Dan2Urn1UraOFF | INT | IOD_STR_disk | I1855 | [8 empty] | 0x03408bac
STRUrnikiSC11Dan2Urn2UraOFF | INT | IOD_STR_disk | I1856 | [8 empty] | 0x03408bad
STRUrnikiSC11Dan2Urn3UraOFF | INT | IOD_STR_disk | I1857 | [8 empty] | 0x03408bae
STRUrnikiSC11Dan2Urn1MinON | INT | IOD_STR_disk | I1858 | [8 empty] | 0x03408baf
STRUrnikiSC11Dan2Urn2MinON | INT | IOD_STR_disk | I1859 | [8 empty] | 0x03408bb0
STRUrnikiSC11Dan2Urn3MinON | INT | IOD_STR_disk | I1860 | [8 empty] | 0x03408bb1
STRUrnikiSC11Dan2Urn1MinOFF | INT | IOD_STR_disk | I1861 | [8 empty] | 0x03408bb2
STRUrnikiSC11Dan2Urn2MinOFF | INT | IOD_STR_disk | I1862 | [8 empty] | 0x03408bb3
STRUrnikiSC11Dan2Urn3MinOFF | INT | IOD_STR_disk | I1863 | [8 empty] | 0x03408bb4
STRUrnikiSC11Dan3Urn1UraON | INT | IOD_STR_disk | I1864 | [8 empty] | 0x03408bb5
STRUrnikiSC11Dan3Urn2UraON | INT | IOD_STR_disk | I1865 | [8 empty] | 0x03408bb6
STRUrnikiSC11Dan3Urn3UraON | INT | IOD_STR_disk | I1866 | [8 empty] | 0x03408bb7
STRUrnikiSC11Dan3Urn1UraOFF | INT | IOD_STR_disk | I1867 | [8 empty] | 0x03408bb8
STRUrnikiSC11Dan3Urn2UraOFF | INT | IOD_STR_disk | I1868 | [8 empty] | 0x03408bb9
STRUrnikiSC11Dan3Urn3UraOFF | INT | IOD_STR_disk | I1869 | [8 empty] | 0x03408bba
STRUrnikiSC11Dan3Urn1MinON | INT | IOD_STR_disk | I1870 | [8 empty] | 0x03408bbb
STRUrnikiSC11Dan3Urn2MinON | INT | IOD_STR_disk | I1871 | [8 empty] | 0x03408bbc
STRUrnikiSC11Dan3Urn3MinON | INT | IOD_STR_disk | I1872 | [8 empty] | 0x03408bbd
STRUrnikiSC11Dan3Urn1MinOFF | INT | IOD_STR_disk | I1873 | [8 empty] | 0x03408bbe
STRUrnikiSC11Dan3Urn2MinOFF | INT | IOD_STR_disk | I1874 | [8 empty] | 0x03408bbf
STRUrnikiSC11Dan3Urn3MinOFF | INT | IOD_STR_disk | I1875 | [8 empty] | 0x03408bc0
STRUrnikiSC11Dan4Urn1UraON | INT | IOD_STR_disk | I1876 | [8 empty] | 0x03408bc1
STRUrnikiSC11Dan4Urn2UraON | INT | IOD_STR_disk | I1877 | [8 empty] | 0x03408bc2
STRUrnikiSC11Dan4Urn3UraON | INT | IOD_STR_disk | I1878 | [8 empty] | 0x03408bc3
STRUrnikiSC11Dan4Urn1UraOFF | INT | IOD_STR_disk | I1879 | [8 empty] | 0x03408bc4
STRUrnikiSC11Dan4Urn2UraOFF | INT | IOD_STR_disk | I1880 | [8 empty] | 0x03408bc5
STRUrnikiSC11Dan4Urn3UraOFF | INT | IOD_STR_disk | I1881 | [8 empty] | 0x03408bc6
STRUrnikiSC11Dan4Urn1MinON | INT | IOD_STR_disk | I1882 | [8 empty] | 0x03408bc7
STRUrnikiSC11Dan4Urn2MinON | INT | IOD_STR_disk | I1883 | [8 empty] | 0x03408bc8
STRUrnikiSC11Dan4Urn3MinON | INT | IOD_STR_disk | I1884 | [8 empty] | 0x03408bc9
STRUrnikiSC11Dan4Urn1MinOFF | INT | IOD_STR_disk | I1885 | [8 empty] | 0x03408bca
STRUrnikiSC11Dan4Urn2MinOFF | INT | IOD_STR_disk | I1886 | [8 empty] | 0x03408bcb
STRUrnikiSC11Dan4Urn3MinOFF | INT | IOD_STR_disk | I1887 | [8 empty] | 0x03408bcc
STRUrnikiSC11Dan5Urn1UraON | INT | IOD_STR_disk | I1888 | [8 empty] | 0x03408bcd
STRUrnikiSC11Dan5Urn2UraON | INT | IOD_STR_disk | I1889 | [8 empty] | 0x03408bce
STRUrnikiSC11Dan5Urn3UraON | INT | IOD_STR_disk | I1890 | [8 empty] | 0x03408bcf
STRUrnikiSC11Dan5Urn1UraOFF | INT | IOD_STR_disk | I1891 | [8 empty] | 0x03408bd0
STRUrnikiSC11Dan5Urn2UraOFF | INT | IOD_STR_disk | I1892 | [8 empty] | 0x03408bd1
STRUrnikiSC11Dan5Urn3UraOFF | INT | IOD_STR_disk | I1893 | [8 empty] | 0x03408bd2
STRUrnikiSC11Dan5Urn1MinON | INT | IOD_STR_disk | I1894 | [8 empty] | 0x03408bd3
STRUrnikiSC11Dan5Urn2MinON | INT | IOD_STR_disk | I1895 | [8 empty] | 0x03408bd4
STRUrnikiSC11Dan5Urn3MinON | INT | IOD_STR_disk | I1896 | [8 empty] | 0x03408bd5
STRUrnikiSC11Dan5Urn1MinOFF | INT | IOD_STR_disk | I1897 | [8 empty] | 0x03408bd6
STRUrnikiSC11Dan5Urn2MinOFF | INT | IOD_STR_disk | I1898 | [8 empty] | 0x03408bd7
STRUrnikiSC11Dan5Urn3MinOFF | INT | IOD_STR_disk | I1899 | [8 empty] | 0x03408bd8
STRUrnikiSC11Dan6Urn1UraON | INT | IOD_STR_disk | I1900 | [8 empty] | 0x03408bd9
STRUrnikiSC11Dan6Urn2UraON | INT | IOD_STR_disk | I1901 | [8 empty] | 0x03408bda
STRUrnikiSC11Dan6Urn3UraON | INT | IOD_STR_disk | I1902 | [8 empty] | 0x03408bdb
STRUrnikiSC11Dan6Urn1UraOFF | INT | IOD_STR_disk | I1903 | [8 empty] | 0x03408bdc
STRUrnikiSC11Dan6Urn2UraOFF | INT | IOD_STR_disk | I1904 | [8 empty] | 0x03408bdd
STRUrnikiSC11Dan6Urn3UraOFF | INT | IOD_STR_disk | I1905 | [8 empty] | 0x03408bde
STRUrnikiSC11Dan6Urn1MinON | INT | IOD_STR_disk | I1906 | [8 empty] | 0x03408bdf
STRUrnikiSC11Dan6Urn2MinON | INT | IOD_STR_disk | I1907 | [8 empty] | 0x03408be0
STRUrnikiSC11Dan6Urn3MinON | INT | IOD_STR_disk | I1908 | [8 empty] | 0x03408be1
STRUrnikiSC11Dan6Urn1MinOFF | INT | IOD_STR_disk | I1909 | [8 empty] | 0x03408be2
STRUrnikiSC11Dan6Urn2MinOFF | INT | IOD_STR_disk | I1910 | [8 empty] | 0x03408be3
STRUrnikiSC11Dan6Urn3MinOFF | INT | IOD_STR_disk | I1911 | [8 empty] | 0x03408be4
STRUrnikiSC11Dan7Urn1UraON | INT | IOD_STR_disk | I1912 | [8 empty] | 0x03408be5
STRUrnikiSC11Dan7Urn2UraON | INT | IOD_STR_disk | I1913 | [8 empty] | 0x03408be6
STRUrnikiSC11Dan7Urn3UraON | INT | IOD_STR_disk | I1914 | [8 empty] | 0x03408be7
STRUrnikiSC11Dan7Urn1UraOFF | INT | IOD_STR_disk | I1915 | [8 empty] | 0x03408be8
STRUrnikiSC11Dan7Urn2UraOFF | INT | IOD_STR_disk | I1916 | [8 empty] | 0x03408be9
STRUrnikiSC11Dan7Urn3UraOFF | INT | IOD_STR_disk | I1917 | [8 empty] | 0x03408bea
STRUrnikiSC11Dan7Urn1MinON | INT | IOD_STR_disk | I1918 | [8 empty] | 0x03408beb
STRUrnikiSC11Dan7Urn2MinON | INT | IOD_STR_disk | I1919 | [8 empty] | 0x03408bec
STRUrnikiSC11Dan7Urn3MinON | INT | IOD_STR_disk | I1920 | [8 empty] | 0x03408bed
STRUrnikiSC11Dan7Urn1MinOFF | INT | IOD_STR_disk | I1921 | [8 empty] | 0x03408bee
STRUrnikiSC11Dan7Urn2MinOFF | INT | IOD_STR_disk | I1922 | [8 empty] | 0x03408bef
STRUrnikiSC11Dan7Urn3MinOFF | INT | IOD_STR_disk | I1923 | [8 empty] | 0x03408bf0
STRUrnikiSC12Dan1Urn1UraON | INT | IOD_STR_disk | I1924 | [8 empty] | 0x03408bf1
STRUrnikiSC12Dan1Urn2UraON | INT | IOD_STR_disk | I1925 | [8 empty] | 0x03408bf2
STRUrnikiSC12Dan1Urn3UraON | INT | IOD_STR_disk | I1926 | [8 empty] | 0x03408bf3
STRUrnikiSC12Dan1Urn1UraOFF | INT | IOD_STR_disk | I1927 | [8 empty] | 0x03408bf4
STRUrnikiSC12Dan1Urn2UraOFF | INT | IOD_STR_disk | I1928 | [8 empty] | 0x03408bf5
STRUrnikiSC12Dan1Urn3UraOFF | INT | IOD_STR_disk | I1929 | [8 empty] | 0x03408bf6
STRUrnikiSC12Dan1Urn1MinON | INT | IOD_STR_disk | I1930 | [8 empty] | 0x03408bf7
STRUrnikiSC12Dan1Urn2MinON | INT | IOD_STR_disk | I1931 | [8 empty] | 0x03408bf8
STRUrnikiSC12Dan1Urn3MinON | INT | IOD_STR_disk | I1932 | [8 empty] | 0x03408bf9
STRUrnikiSC12Dan1Urn1MinOFF | INT | IOD_STR_disk | I1933 | [8 empty] | 0x03408bfa
STRUrnikiSC12Dan1Urn2MinOFF | INT | IOD_STR_disk | I1934 | [8 empty] | 0x03408bfb
STRUrnikiSC12Dan1Urn3MinOFF | INT | IOD_STR_disk | I1935 | [8 empty] | 0x03408bfc
STRUrnikiSC12Dan2Urn1UraON | INT | IOD_STR_disk | I1936 | [8 empty] | 0x03408bfd
STRUrnikiSC12Dan2Urn2UraON | INT | IOD_STR_disk | I1937 | [8 empty] | 0x03408bfe
STRUrnikiSC12Dan2Urn3UraON | INT | IOD_STR_disk | I1938 | [8 empty] | 0x03408bff
STRUrnikiSC12Dan2Urn1UraOFF | INT | IOD_STR_disk | I1939 | [8 empty] | 0x03408c00
STRUrnikiSC12Dan2Urn2UraOFF | INT | IOD_STR_disk | I1940 | [8 empty] | 0x03408c01
STRUrnikiSC12Dan2Urn3UraOFF | INT | IOD_STR_disk | I1941 | [8 empty] | 0x03408c02
STRUrnikiSC12Dan2Urn1MinON | INT | IOD_STR_disk | I1942 | [8 empty] | 0x03408c03
STRUrnikiSC12Dan2Urn2MinON | INT | IOD_STR_disk | I1943 | [8 empty] | 0x03408c04
STRUrnikiSC12Dan2Urn3MinON | INT | IOD_STR_disk | I1944 | [8 empty] | 0x03408c05
STRUrnikiSC12Dan2Urn1MinOFF | INT | IOD_STR_disk | I1945 | [8 empty] | 0x03408c06
STRUrnikiSC12Dan2Urn2MinOFF | INT | IOD_STR_disk | I1946 | [8 empty] | 0x03408c07
STRUrnikiSC12Dan2Urn3MinOFF | INT | IOD_STR_disk | I1947 | [8 empty] | 0x03408c08
STRUrnikiSC12Dan3Urn1UraON | INT | IOD_STR_disk | I1948 | [8 empty] | 0x03408c09
STRUrnikiSC12Dan3Urn2UraON | INT | IOD_STR_disk | I1949 | [8 empty] | 0x03408c0a
STRUrnikiSC12Dan3Urn3UraON | INT | IOD_STR_disk | I1950 | [8 empty] | 0x03408c0b
STRUrnikiSC12Dan3Urn1UraOFF | INT | IOD_STR_disk | I1951 | [8 empty] | 0x03408c0c
STRUrnikiSC12Dan3Urn2UraOFF | INT | IOD_STR_disk | I1952 | [8 empty] | 0x03408c0d
STRUrnikiSC12Dan3Urn3UraOFF | INT | IOD_STR_disk | I1953 | [8 empty] | 0x03408c0e
STRUrnikiSC12Dan3Urn1MinON | INT | IOD_STR_disk | I1954 | [8 empty] | 0x03408c0f
STRUrnikiSC12Dan3Urn2MinON | INT | IOD_STR_disk | I1955 | [8 empty] | 0x03408c10
STRUrnikiSC12Dan3Urn3MinON | INT | IOD_STR_disk | I1956 | [8 empty] | 0x03408c11
STRUrnikiSC12Dan3Urn1MinOFF | INT | IOD_STR_disk | I1957 | [8 empty] | 0x03408c12
STRUrnikiSC12Dan3Urn2MinOFF | INT | IOD_STR_disk | I1958 | [8 empty] | 0x03408c13
STRUrnikiSC12Dan3Urn3MinOFF | INT | IOD_STR_disk | I1959 | [8 empty] | 0x03408c14
STRUrnikiSC12Dan4Urn1UraON | INT | IOD_STR_disk | I1960 | [8 empty] | 0x03408c15
STRUrnikiSC12Dan4Urn2UraON | INT | IOD_STR_disk | I1961 | [8 empty] | 0x03408c16
STRUrnikiSC12Dan4Urn3UraON | INT | IOD_STR_disk | I1962 | [8 empty] | 0x03408c17
STRUrnikiSC12Dan4Urn1UraOFF | INT | IOD_STR_disk | I1963 | [8 empty] | 0x03408c18
STRUrnikiSC12Dan4Urn2UraOFF | INT | IOD_STR_disk | I1964 | [8 empty] | 0x03408c19
STRUrnikiSC12Dan4Urn3UraOFF | INT | IOD_STR_disk | I1965 | [8 empty] | 0x03408c1a
STRUrnikiSC12Dan4Urn1MinON | INT | IOD_STR_disk | I1966 | [8 empty] | 0x03408c1b
STRUrnikiSC12Dan4Urn2MinON | INT | IOD_STR_disk | I1967 | [8 empty] | 0x03408c1c
STRUrnikiSC12Dan4Urn3MinON | INT | IOD_STR_disk | I1968 | [8 empty] | 0x03408c1d
STRUrnikiSC12Dan4Urn1MinOFF | INT | IOD_STR_disk | I1969 | [8 empty] | 0x03408c1e
STRUrnikiSC12Dan4Urn2MinOFF | INT | IOD_STR_disk | I1970 | [8 empty] | 0x03408c1f
STRUrnikiSC12Dan4Urn3MinOFF | INT | IOD_STR_disk | I1971 | [8 empty] | 0x03408c20
STRUrnikiSC12Dan5Urn1UraON | INT | IOD_STR_disk | I1972 | [8 empty] | 0x03408c21
STRUrnikiSC12Dan5Urn2UraON | INT | IOD_STR_disk | I1973 | [8 empty] | 0x03408c22
STRUrnikiSC12Dan5Urn3UraON | INT | IOD_STR_disk | I1974 | [8 empty] | 0x03408c23
STRUrnikiSC12Dan5Urn1UraOFF | INT | IOD_STR_disk | I1975 | [8 empty] | 0x03408c24
STRUrnikiSC12Dan5Urn2UraOFF | INT | IOD_STR_disk | I1976 | [8 empty] | 0x03408c25
STRUrnikiSC12Dan5Urn3UraOFF | INT | IOD_STR_disk | I1977 | [8 empty] | 0x03408c26
STRUrnikiSC12Dan5Urn1MinON | INT | IOD_STR_disk | I1978 | [8 empty] | 0x03408c27
STRUrnikiSC12Dan5Urn2MinON | INT | IOD_STR_disk | I1979 | [8 empty] | 0x03408c28
STRUrnikiSC12Dan5Urn3MinON | INT | IOD_STR_disk | I1980 | [8 empty] | 0x03408c29
STRUrnikiSC12Dan5Urn1MinOFF | INT | IOD_STR_disk | I1981 | [8 empty] | 0x03408c2a
STRUrnikiSC12Dan5Urn2MinOFF | INT | IOD_STR_disk | I1982 | [8 empty] | 0x03408c2b
STRUrnikiSC12Dan5Urn3MinOFF | INT | IOD_STR_disk | I1983 | [8 empty] | 0x03408c2c
STRUrnikiSC12Dan6Urn1UraON | INT | IOD_STR_disk | I1984 | [8 empty] | 0x03408c2d
STRUrnikiSC12Dan6Urn2UraON | INT | IOD_STR_disk | I1985 | [8 empty] | 0x03408c2e
STRUrnikiSC12Dan6Urn3UraON | INT | IOD_STR_disk | I1986 | [8 empty] | 0x03408c2f
STRUrnikiSC12Dan6Urn1UraOFF | INT | IOD_STR_disk | I1987 | [8 empty] | 0x03408c30
STRUrnikiSC12Dan6Urn2UraOFF | INT | IOD_STR_disk | I1988 | [8 empty] | 0x03408c31
STRUrnikiSC12Dan6Urn3UraOFF | INT | IOD_STR_disk | I1989 | [8 empty] | 0x03408c32
STRUrnikiSC12Dan6Urn1MinON | INT | IOD_STR_disk | I1990 | [8 empty] | 0x03408c33
STRUrnikiSC12Dan6Urn2MinON | INT | IOD_STR_disk | I1991 | [8 empty] | 0x03408c34
STRUrnikiSC12Dan6Urn3MinON | INT | IOD_STR_disk | I1992 | [8 empty] | 0x03408c35
STRUrnikiSC12Dan6Urn1MinOFF | INT | IOD_STR_disk | I1993 | [8 empty] | 0x03408c36
STRUrnikiSC12Dan6Urn2MinOFF | INT | IOD_STR_disk | I1994 | [8 empty] | 0x03408c37
STRUrnikiSC12Dan6Urn3MinOFF | INT | IOD_STR_disk | I1995 | [8 empty] | 0x03408c38
STRUrnikiSC12Dan7Urn1UraON | INT | IOD_STR_disk | I1996 | [8 empty] | 0x03408c39
STRUrnikiSC12Dan7Urn2UraON | INT | IOD_STR_disk | I1997 | [8 empty] | 0x03408c3a
STRUrnikiSC12Dan7Urn3UraON | INT | IOD_STR_disk | I1998 | [8 empty] | 0x03408c3b
STRUrnikiSC12Dan7Urn1UraOFF | INT | IOD_STR_disk | I1999 | [8 empty] | 0x03408c3c
STRUrnikiSC12Dan7Urn2UraOFF | INT | IOD_STR_disk | I2000 | [8 empty] | 0x03408c3d
STRUrnikiSC12Dan7Urn3UraOFF | INT | IOD_STR_disk | I2001 | [8 empty] | 0x03408c3e
STRUrnikiSC12Dan7Urn1MinON | INT | IOD_STR_disk | I2002 | [8 empty] | 0x03408c3f
STRUrnikiSC12Dan7Urn2MinON | INT | IOD_STR_disk | I2003 | [8 empty] | 0x03408c40
STRUrnikiSC12Dan7Urn3MinON | INT | IOD_STR_disk | I2004 | [8 empty] | 0x03408c41
STRUrnikiSC12Dan7Urn1MinOFF | INT | IOD_STR_disk | I2005 | [8 empty] | 0x03408c42
STRUrnikiSC12Dan7Urn2MinOFF | INT | IOD_STR_disk | I2006 | [8 empty] | 0x03408c43
STRUrnikiSC12Dan7Urn3MinOFF | INT | IOD_STR_disk | I2007 | [8 empty] | 0x03408c44
STRUrnikiSC13Dan1Urn1UraON | INT | IOD_STR_disk | I2008 | [8 empty] | 0x03408c45
STRUrnikiSC13Dan1Urn2UraON | INT | IOD_STR_disk | I2009 | [8 empty] | 0x03408c46
STRUrnikiSC13Dan1Urn3UraON | INT | IOD_STR_disk | I2010 | [8 empty] | 0x03408c47
STRUrnikiSC13Dan1Urn1UraOFF | INT | IOD_STR_disk | I2011 | [8 empty] | 0x03408c48
STRUrnikiSC13Dan1Urn2UraOFF | INT | IOD_STR_disk | I2012 | [8 empty] | 0x03408c49
STRUrnikiSC13Dan1Urn3UraOFF | INT | IOD_STR_disk | I2013 | [8 empty] | 0x03408c4a
STRUrnikiSC13Dan1Urn1MinON | INT | IOD_STR_disk | I2014 | [8 empty] | 0x03408c4b
STRUrnikiSC13Dan1Urn2MinON | INT | IOD_STR_disk | I2015 | [8 empty] | 0x03408c4c
STRUrnikiSC13Dan1Urn3MinON | INT | IOD_STR_disk | I2016 | [8 empty] | 0x03408c4d
STRUrnikiSC13Dan1Urn1MinOFF | INT | IOD_STR_disk | I2017 | [8 empty] | 0x03408c4e
STRUrnikiSC13Dan1Urn2MinOFF | INT | IOD_STR_disk | I2018 | [8 empty] | 0x03408c4f
STRUrnikiSC13Dan1Urn3MinOFF | INT | IOD_STR_disk | I2019 | [8 empty] | 0x03408c50
STRUrnikiSC13Dan2Urn1UraON | INT | IOD_STR_disk | I2020 | [8 empty] | 0x03408c51
STRUrnikiSC13Dan2Urn2UraON | INT | IOD_STR_disk | I2021 | [8 empty] | 0x03408c52
STRUrnikiSC13Dan2Urn3UraON | INT | IOD_STR_disk | I2022 | [8 empty] | 0x03408c53
STRUrnikiSC13Dan2Urn1UraOFF | INT | IOD_STR_disk | I2023 | [8 empty] | 0x03408c54
STRUrnikiSC13Dan2Urn2UraOFF | INT | IOD_STR_disk | I2024 | [8 empty] | 0x03408c55
STRUrnikiSC13Dan2Urn3UraOFF | INT | IOD_STR_disk | I2025 | [8 empty] | 0x03408c56
STRUrnikiSC13Dan2Urn1MinON | INT | IOD_STR_disk | I2026 | [8 empty] | 0x03408c57
STRUrnikiSC13Dan2Urn2MinON | INT | IOD_STR_disk | I2027 | [8 empty] | 0x03408c58
STRUrnikiSC13Dan2Urn3MinON | INT | IOD_STR_disk | I2028 | [8 empty] | 0x03408c59
STRUrnikiSC13Dan2Urn1MinOFF | INT | IOD_STR_disk | I2029 | [8 empty] | 0x03408c5a
STRUrnikiSC13Dan2Urn2MinOFF | INT | IOD_STR_disk | I2030 | [8 empty] | 0x03408c5b
STRUrnikiSC13Dan2Urn3MinOFF | INT | IOD_STR_disk | I2031 | [8 empty] | 0x03408c5c
STRUrnikiSC13Dan3Urn1UraON | INT | IOD_STR_disk | I2032 | [8 empty] | 0x03408c5d
STRUrnikiSC13Dan3Urn2UraON | INT | IOD_STR_disk | I2033 | [8 empty] | 0x03408c5e
STRUrnikiSC13Dan3Urn3UraON | INT | IOD_STR_disk | I2034 | [8 empty] | 0x03408c5f
STRUrnikiSC13Dan3Urn1UraOFF | INT | IOD_STR_disk | I2035 | [8 empty] | 0x03408c60
STRUrnikiSC13Dan3Urn2UraOFF | INT | IOD_STR_disk | I2036 | [8 empty] | 0x03408c61
STRUrnikiSC13Dan3Urn3UraOFF | INT | IOD_STR_disk | I2037 | [8 empty] | 0x03408c62
STRUrnikiSC13Dan3Urn1MinON | INT | IOD_STR_disk | I2038 | [8 empty] | 0x03408c63
STRUrnikiSC13Dan3Urn2MinON | INT | IOD_STR_disk | I2039 | [8 empty] | 0x03408c64
STRUrnikiSC13Dan3Urn3MinON | INT | IOD_STR_disk | I2040 | [8 empty] | 0x03408c65
STRUrnikiSC13Dan3Urn1MinOFF | INT | IOD_STR_disk | I2041 | [8 empty] | 0x03408c66
STRUrnikiSC13Dan3Urn2MinOFF | INT | IOD_STR_disk | I2042 | [8 empty] | 0x03408c67
STRUrnikiSC13Dan3Urn3MinOFF | INT | IOD_STR_disk | I2043 | [8 empty] | 0x03408c68
STRUrnikiSC13Dan4Urn1UraON | INT | IOD_STR_disk | I2044 | [8 empty] | 0x03408c69
STRUrnikiSC13Dan4Urn2UraON | INT | IOD_STR_disk | I2045 | [8 empty] | 0x03408c6a
STRUrnikiSC13Dan4Urn3UraON | INT | IOD_STR_disk | I2046 | [8 empty] | 0x03408c6b
STRUrnikiSC13Dan4Urn1UraOFF | INT | IOD_STR_disk | I2047 | [8 empty] | 0x03408c6c
STRUrnikiSC13Dan4Urn2UraOFF | INT | IOD_STR_disk | I2048 | [8 empty] | 0x03408c6d
STRUrnikiSC13Dan4Urn3UraOFF | INT | IOD_STR_disk | I2049 | [8 empty] | 0x03408c6e
STRUrnikiSC13Dan4Urn1MinON | INT | IOD_STR_disk | I2050 | [8 empty] | 0x03408c6f
STRUrnikiSC13Dan4Urn2MinON | INT | IOD_STR_disk | I2051 | [8 empty] | 0x03408c70
STRUrnikiSC13Dan4Urn3MinON | INT | IOD_STR_disk | I2052 | [8 empty] | 0x03408c71
STRUrnikiSC13Dan4Urn1MinOFF | INT | IOD_STR_disk | I2053 | [8 empty] | 0x03408c72
STRUrnikiSC13Dan4Urn2MinOFF | INT | IOD_STR_disk | I2054 | [8 empty] | 0x03408c73
STRUrnikiSC13Dan4Urn3MinOFF | INT | IOD_STR_disk | I2055 | [8 empty] | 0x03408c74
STRUrnikiSC13Dan5Urn1UraON | INT | IOD_STR_disk | I2056 | [8 empty] | 0x03408c75
STRUrnikiSC13Dan5Urn2UraON | INT | IOD_STR_disk | I2057 | [8 empty] | 0x03408c76
STRUrnikiSC13Dan5Urn3UraON | INT | IOD_STR_disk | I2058 | [8 empty] | 0x03408c77
STRUrnikiSC13Dan5Urn1UraOFF | INT | IOD_STR_disk | I2059 | [8 empty] | 0x03408c78
STRUrnikiSC13Dan5Urn2UraOFF | INT | IOD_STR_disk | I2060 | [8 empty] | 0x03408c79
STRUrnikiSC13Dan5Urn3UraOFF | INT | IOD_STR_disk | I2061 | [8 empty] | 0x03408c7a
STRUrnikiSC13Dan5Urn1MinON | INT | IOD_STR_disk | I2062 | [8 empty] | 0x03408c7b
STRUrnikiSC13Dan5Urn2MinON | INT | IOD_STR_disk | I2063 | [8 empty] | 0x03408c7c
STRUrnikiSC13Dan5Urn3MinON | INT | IOD_STR_disk | I2064 | [8 empty] | 0x03408c7d
STRUrnikiSC13Dan5Urn1MinOFF | INT | IOD_STR_disk | I2065 | [8 empty] | 0x03408c7e
STRUrnikiSC13Dan5Urn2MinOFF | INT | IOD_STR_disk | I2066 | [8 empty] | 0x03408c7f
STRUrnikiSC13Dan5Urn3MinOFF | INT | IOD_STR_disk | I2067 | [8 empty] | 0x03408c80
STRUrnikiSC13Dan6Urn1UraON | INT | IOD_STR_disk | I2068 | [8 empty] | 0x03408c81
STRUrnikiSC13Dan6Urn2UraON | INT | IOD_STR_disk | I2069 | [8 empty] | 0x03408c82
STRUrnikiSC13Dan6Urn3UraON | INT | IOD_STR_disk | I2070 | [8 empty] | 0x03408c83
STRUrnikiSC13Dan6Urn1UraOFF | INT | IOD_STR_disk | I2071 | [8 empty] | 0x03408c84
STRUrnikiSC13Dan6Urn2UraOFF | INT | IOD_STR_disk | I2072 | [8 empty] | 0x03408c85
STRUrnikiSC13Dan6Urn3UraOFF | INT | IOD_STR_disk | I2073 | [8 empty] | 0x03408c86
STRUrnikiSC13Dan6Urn1MinON | INT | IOD_STR_disk | I2074 | [8 empty] | 0x03408c87
STRUrnikiSC13Dan6Urn2MinON | INT | IOD_STR_disk | I2075 | [8 empty] | 0x03408c88
STRUrnikiSC13Dan6Urn3MinON | INT | IOD_STR_disk | I2076 | [8 empty] | 0x03408c89
STRUrnikiSC13Dan6Urn1MinOFF | INT | IOD_STR_disk | I2077 | [8 empty] | 0x03408c8a
STRUrnikiSC13Dan6Urn2MinOFF | INT | IOD_STR_disk | I2078 | [8 empty] | 0x03408c8b
STRUrnikiSC13Dan6Urn3MinOFF | INT | IOD_STR_disk | I2079 | [8 empty] | 0x03408c8c
STRUrnikiSC13Dan7Urn1UraON | INT | IOD_STR_disk | I2080 | [8 empty] | 0x03408c8d
STRUrnikiSC13Dan7Urn2UraON | INT | IOD_STR_disk | I2081 | [8 empty] | 0x03408c8e
STRUrnikiSC13Dan7Urn3UraON | INT | IOD_STR_disk | I2082 | [8 empty] | 0x03408c8f
STRUrnikiSC13Dan7Urn1UraOFF | INT | IOD_STR_disk | I2083 | [8 empty] | 0x03408c90
STRUrnikiSC13Dan7Urn2UraOFF | INT | IOD_STR_disk | I2084 | [8 empty] | 0x03408c91
STRUrnikiSC13Dan7Urn3UraOFF | INT | IOD_STR_disk | I2085 | [8 empty] | 0x03408c92
STRUrnikiSC13Dan7Urn1MinON | INT | IOD_STR_disk | I2086 | [8 empty] | 0x03408c93
STRUrnikiSC13Dan7Urn2MinON | INT | IOD_STR_disk | I2087 | [8 empty] | 0x03408c94
STRUrnikiSC13Dan7Urn3MinON | INT | IOD_STR_disk | I2088 | [8 empty] | 0x03408c95
STRUrnikiSC13Dan7Urn1MinOFF | INT | IOD_STR_disk | I2089 | [8 empty] | 0x03408c96
STRUrnikiSC13Dan7Urn2MinOFF | INT | IOD_STR_disk | I2090 | [8 empty] | 0x03408c97
STRUrnikiSC13Dan7Urn3MinOFF | INT | IOD_STR_disk | I2091 | [8 empty] | 0x03408c98
STRUrnikiSC14Dan1Urn1UraON | INT | IOD_STR_disk | I2092 | [8 empty] | 0x03408c99
STRUrnikiSC14Dan1Urn2UraON | INT | IOD_STR_disk | I2093 | [8 empty] | 0x03408c9a
STRUrnikiSC14Dan1Urn3UraON | INT | IOD_STR_disk | I2094 | [8 empty] | 0x03408c9b
STRUrnikiSC14Dan1Urn1UraOFF | INT | IOD_STR_disk | I2095 | [8 empty] | 0x03408c9c
STRUrnikiSC14Dan1Urn2UraOFF | INT | IOD_STR_disk | I2096 | [8 empty] | 0x03408c9d
STRUrnikiSC14Dan1Urn3UraOFF | INT | IOD_STR_disk | I2097 | [8 empty] | 0x03408c9e
STRUrnikiSC14Dan1Urn1MinON | INT | IOD_STR_disk | I2098 | [8 empty] | 0x03408c9f
STRUrnikiSC14Dan1Urn2MinON | INT | IOD_STR_disk | I2099 | [8 empty] | 0x03408ca0
STRUrnikiSC14Dan1Urn3MinON | INT | IOD_STR_disk | I2100 | [8 empty] | 0x03408ca1
STRUrnikiSC14Dan1Urn1MinOFF | INT | IOD_STR_disk | I2101 | [8 empty] | 0x03408ca2
STRUrnikiSC14Dan1Urn2MinOFF | INT | IOD_STR_disk | I2102 | [8 empty] | 0x03408ca3
STRUrnikiSC14Dan1Urn3MinOFF | INT | IOD_STR_disk | I2103 | [8 empty] | 0x03408ca4
STRUrnikiSC14Dan2Urn1UraON | INT | IOD_STR_disk | I2104 | [8 empty] | 0x03408ca5
STRUrnikiSC14Dan2Urn2UraON | INT | IOD_STR_disk | I2105 | [8 empty] | 0x03408ca6
STRUrnikiSC14Dan2Urn3UraON | INT | IOD_STR_disk | I2106 | [8 empty] | 0x03408ca7
STRUrnikiSC14Dan2Urn1UraOFF | INT | IOD_STR_disk | I2107 | [8 empty] | 0x03408ca8
STRUrnikiSC14Dan2Urn2UraOFF | INT | IOD_STR_disk | I2108 | [8 empty] | 0x03408ca9
STRUrnikiSC14Dan2Urn3UraOFF | INT | IOD_STR_disk | I2109 | [8 empty] | 0x03408caa
STRUrnikiSC14Dan2Urn1MinON | INT | IOD_STR_disk | I2110 | [8 empty] | 0x03408cab
STRUrnikiSC14Dan2Urn2MinON | INT | IOD_STR_disk | I2111 | [8 empty] | 0x03408cac
STRUrnikiSC14Dan2Urn3MinON | INT | IOD_STR_disk | I2112 | [8 empty] | 0x03408cad
STRUrnikiSC14Dan2Urn1MinOFF | INT | IOD_STR_disk | I2113 | [8 empty] | 0x03408cae
STRUrnikiSC14Dan2Urn2MinOFF | INT | IOD_STR_disk | I2114 | [8 empty] | 0x03408caf
STRUrnikiSC14Dan2Urn3MinOFF | INT | IOD_STR_disk | I2115 | [8 empty] | 0x03408cb0
STRUrnikiSC14Dan3Urn1UraON | INT | IOD_STR_disk | I2116 | [8 empty] | 0x03408cb1
STRUrnikiSC14Dan3Urn2UraON | INT | IOD_STR_disk | I2117 | [8 empty] | 0x03408cb2
STRUrnikiSC14Dan3Urn3UraON | INT | IOD_STR_disk | I2118 | [8 empty] | 0x03408cb3
STRUrnikiSC14Dan3Urn1UraOFF | INT | IOD_STR_disk | I2119 | [8 empty] | 0x03408cb4
STRUrnikiSC14Dan3Urn2UraOFF | INT | IOD_STR_disk | I2120 | [8 empty] | 0x03408cb5
STRUrnikiSC14Dan3Urn3UraOFF | INT | IOD_STR_disk | I2121 | [8 empty] | 0x03408cb6
STRUrnikiSC14Dan3Urn1MinON | INT | IOD_STR_disk | I2122 | [8 empty] | 0x03408cb7
STRUrnikiSC14Dan3Urn2MinON | INT | IOD_STR_disk | I2123 | [8 empty] | 0x03408cb8
STRUrnikiSC14Dan3Urn3MinON | INT | IOD_STR_disk | I2124 | [8 empty] | 0x03408cb9
STRUrnikiSC14Dan3Urn1MinOFF | INT | IOD_STR_disk | I2125 | [8 empty] | 0x03408cba
STRUrnikiSC14Dan3Urn2MinOFF | INT | IOD_STR_disk | I2126 | [8 empty] | 0x03408cbb
STRUrnikiSC14Dan3Urn3MinOFF | INT | IOD_STR_disk | I2127 | [8 empty] | 0x03408cbc
STRUrnikiSC14Dan4Urn1UraON | INT | IOD_STR_disk | I2128 | [8 empty] | 0x03408cbd
STRUrnikiSC14Dan4Urn2UraON | INT | IOD_STR_disk | I2129 | [8 empty] | 0x03408cbe
STRUrnikiSC14Dan4Urn3UraON | INT | IOD_STR_disk | I2130 | [8 empty] | 0x03408cbf
STRUrnikiSC14Dan4Urn1UraOFF | INT | IOD_STR_disk | I2131 | [8 empty] | 0x03408cc0
STRUrnikiSC14Dan4Urn2UraOFF | INT | IOD_STR_disk | I2132 | [8 empty] | 0x03408cc1
STRUrnikiSC14Dan4Urn3UraOFF | INT | IOD_STR_disk | I2133 | [8 empty] | 0x03408cc2
STRUrnikiSC14Dan4Urn1MinON | INT | IOD_STR_disk | I2134 | [8 empty] | 0x03408cc3
STRUrnikiSC14Dan4Urn2MinON | INT | IOD_STR_disk | I2135 | [8 empty] | 0x03408cc4
STRUrnikiSC14Dan4Urn3MinON | INT | IOD_STR_disk | I2136 | [8 empty] | 0x03408cc5
STRUrnikiSC14Dan4Urn1MinOFF | INT | IOD_STR_disk | I2137 | [8 empty] | 0x03408cc6
STRUrnikiSC14Dan4Urn2MinOFF | INT | IOD_STR_disk | I2138 | [8 empty] | 0x03408cc7
STRUrnikiSC14Dan4Urn3MinOFF | INT | IOD_STR_disk | I2139 | [8 empty] | 0x03408cc8
STRUrnikiSC14Dan5Urn1UraON | INT | IOD_STR_disk | I2140 | [8 empty] | 0x03408cc9
STRUrnikiSC14Dan5Urn2UraON | INT | IOD_STR_disk | I2141 | [8 empty] | 0x03408cca
STRUrnikiSC14Dan5Urn3UraON | INT | IOD_STR_disk | I2142 | [8 empty] | 0x03408ccb
STRUrnikiSC14Dan5Urn1UraOFF | INT | IOD_STR_disk | I2143 | [8 empty] | 0x03408ccc
STRUrnikiSC14Dan5Urn2UraOFF | INT | IOD_STR_disk | I2144 | [8 empty] | 0x03408ccd
STRUrnikiSC14Dan5Urn3UraOFF | INT | IOD_STR_disk | I2145 | [8 empty] | 0x03408cce
STRUrnikiSC14Dan5Urn1MinON | INT | IOD_STR_disk | I2146 | [8 empty] | 0x03408ccf
STRUrnikiSC14Dan5Urn2MinON | INT | IOD_STR_disk | I2147 | [8 empty] | 0x03408cd0
STRUrnikiSC14Dan5Urn3MinON | INT | IOD_STR_disk | I2148 | [8 empty] | 0x03408cd1
STRUrnikiSC14Dan5Urn1MinOFF | INT | IOD_STR_disk | I2149 | [8 empty] | 0x03408cd2
STRUrnikiSC14Dan5Urn2MinOFF | INT | IOD_STR_disk | I2150 | [8 empty] | 0x03408cd3
STRUrnikiSC14Dan5Urn3MinOFF | INT | IOD_STR_disk | I2151 | [8 empty] | 0x03408cd4
STRUrnikiSC14Dan6Urn1UraON | INT | IOD_STR_disk | I2152 | [8 empty] | 0x03408cd5
STRUrnikiSC14Dan6Urn2UraON | INT | IOD_STR_disk | I2153 | [8 empty] | 0x03408cd6
STRUrnikiSC14Dan6Urn3UraON | INT | IOD_STR_disk | I2154 | [8 empty] | 0x03408cd7
STRUrnikiSC14Dan6Urn1UraOFF | INT | IOD_STR_disk | I2155 | [8 empty] | 0x03408cd8
STRUrnikiSC14Dan6Urn2UraOFF | INT | IOD_STR_disk | I2156 | [8 empty] | 0x03408cd9
STRUrnikiSC14Dan6Urn3UraOFF | INT | IOD_STR_disk | I2157 | [8 empty] | 0x03408cda
STRUrnikiSC14Dan6Urn1MinON | INT | IOD_STR_disk | I2158 | [8 empty] | 0x03408cdb
STRUrnikiSC14Dan6Urn2MinON | INT | IOD_STR_disk | I2159 | [8 empty] | 0x03408cdc
STRUrnikiSC14Dan6Urn3MinON | INT | IOD_STR_disk | I2160 | [8 empty] | 0x03408cdd
STRUrnikiSC14Dan6Urn1MinOFF | INT | IOD_STR_disk | I2161 | [8 empty] | 0x03408cde
STRUrnikiSC14Dan6Urn2MinOFF | INT | IOD_STR_disk | I2162 | [8 empty] | 0x03408cdf
STRUrnikiSC14Dan6Urn3MinOFF | INT | IOD_STR_disk | I2163 | [8 empty] | 0x03408ce0
STRUrnikiSC14Dan7Urn1UraON | INT | IOD_STR_disk | I2164 | [8 empty] | 0x03408ce1
STRUrnikiSC14Dan7Urn2UraON | INT | IOD_STR_disk | I2165 | [8 empty] | 0x03408ce2
STRUrnikiSC14Dan7Urn3UraON | INT | IOD_STR_disk | I2166 | [8 empty] | 0x03408ce3
STRUrnikiSC14Dan7Urn1UraOFF | INT | IOD_STR_disk | I2167 | [8 empty] | 0x03408ce4
STRUrnikiSC14Dan7Urn2UraOFF | INT | IOD_STR_disk | I2168 | [8 empty] | 0x03408ce5
STRUrnikiSC14Dan7Urn3UraOFF | INT | IOD_STR_disk | I2169 | [8 empty] | 0x03408ce6
STRUrnikiSC14Dan7Urn1MinON | INT | IOD_STR_disk | I2170 | [8 empty] | 0x03408ce7
STRUrnikiSC14Dan7Urn2MinON | INT | IOD_STR_disk | I2171 | [8 empty] | 0x03408ce8
STRUrnikiSC14Dan7Urn3MinON | INT | IOD_STR_disk | I2172 | [8 empty] | 0x03408ce9
STRUrnikiSC14Dan7Urn1MinOFF | INT | IOD_STR_disk | I2173 | [8 empty] | 0x03408cea
STRUrnikiSC14Dan7Urn2MinOFF | INT | IOD_STR_disk | I2174 | [8 empty] | 0x03408ceb
STRUrnikiSC14Dan7Urn3MinOFF | INT | IOD_STR_disk | I2175 | [8 empty] | 0x03408cec
STRUrnikiSC15Dan1Urn1UraON | INT | IOD_STR_disk | I2176 | [8 empty] | 0x03408ced
STRUrnikiSC15Dan1Urn2UraON | INT | IOD_STR_disk | I2177 | [8 empty] | 0x03408cee
STRUrnikiSC15Dan1Urn3UraON | INT | IOD_STR_disk | I2178 | [8 empty] | 0x03408cef
STRUrnikiSC15Dan1Urn1UraOFF | INT | IOD_STR_disk | I2179 | [8 empty] | 0x03408cf0
STRUrnikiSC15Dan1Urn2UraOFF | INT | IOD_STR_disk | I2180 | [8 empty] | 0x03408cf1
STRUrnikiSC15Dan1Urn3UraOFF | INT | IOD_STR_disk | I2181 | [8 empty] | 0x03408cf2
STRUrnikiSC15Dan1Urn1MinON | INT | IOD_STR_disk | I2182 | [8 empty] | 0x03408cf3
STRUrnikiSC15Dan1Urn2MinON | INT | IOD_STR_disk | I2183 | [8 empty] | 0x03408cf4
STRUrnikiSC15Dan1Urn3MinON | INT | IOD_STR_disk | I2184 | [8 empty] | 0x03408cf5
STRUrnikiSC15Dan1Urn1MinOFF | INT | IOD_STR_disk | I2185 | [8 empty] | 0x03408cf6
STRUrnikiSC15Dan1Urn2MinOFF | INT | IOD_STR_disk | I2186 | [8 empty] | 0x03408cf7
STRUrnikiSC15Dan1Urn3MinOFF | INT | IOD_STR_disk | I2187 | [8 empty] | 0x03408cf8
STRUrnikiSC15Dan2Urn1UraON | INT | IOD_STR_disk | I2188 | [8 empty] | 0x03408cf9
STRUrnikiSC15Dan2Urn2UraON | INT | IOD_STR_disk | I2189 | [8 empty] | 0x03408cfa
STRUrnikiSC15Dan2Urn3UraON | INT | IOD_STR_disk | I2190 | [8 empty] | 0x03408cfb
STRUrnikiSC15Dan2Urn1UraOFF | INT | IOD_STR_disk | I2191 | [8 empty] | 0x03408cfc
STRUrnikiSC15Dan2Urn2UraOFF | INT | IOD_STR_disk | I2192 | [8 empty] | 0x03408cfd
STRUrnikiSC15Dan2Urn3UraOFF | INT | IOD_STR_disk | I2193 | [8 empty] | 0x03408cfe
STRUrnikiSC15Dan2Urn1MinON | INT | IOD_STR_disk | I2194 | [8 empty] | 0x03408cff
STRUrnikiSC15Dan2Urn2MinON | INT | IOD_STR_disk | I2195 | [8 empty] | 0x03408d00
STRUrnikiSC15Dan2Urn3MinON | INT | IOD_STR_disk | I2196 | [8 empty] | 0x03408d01
STRUrnikiSC15Dan2Urn1MinOFF | INT | IOD_STR_disk | I2197 | [8 empty] | 0x03408d02
STRUrnikiSC15Dan2Urn2MinOFF | INT | IOD_STR_disk | I2198 | [8 empty] | 0x03408d03
STRUrnikiSC15Dan2Urn3MinOFF | INT | IOD_STR_disk | I2199 | [8 empty] | 0x03408d04
STRUrnikiSC15Dan3Urn1UraON | INT | IOD_STR_disk | I2200 | [8 empty] | 0x03408d05
STRUrnikiSC15Dan3Urn2UraON | INT | IOD_STR_disk | I2201 | [8 empty] | 0x03408d06
STRUrnikiSC15Dan3Urn3UraON | INT | IOD_STR_disk | I2202 | [8 empty] | 0x03408d07
STRUrnikiSC15Dan3Urn1UraOFF | INT | IOD_STR_disk | I2203 | [8 empty] | 0x03408d08
STRUrnikiSC15Dan3Urn2UraOFF | INT | IOD_STR_disk | I2204 | [8 empty] | 0x03408d09
STRUrnikiSC15Dan3Urn3UraOFF | INT | IOD_STR_disk | I2205 | [8 empty] | 0x03408d0a
STRUrnikiSC15Dan3Urn1MinON | INT | IOD_STR_disk | I2206 | [8 empty] | 0x03408d0b
STRUrnikiSC15Dan3Urn2MinON | INT | IOD_STR_disk | I2207 | [8 empty] | 0x03408d0c
STRUrnikiSC15Dan3Urn3MinON | INT | IOD_STR_disk | I2208 | [8 empty] | 0x03408d0d
STRUrnikiSC15Dan3Urn1MinOFF | INT | IOD_STR_disk | I2209 | [8 empty] | 0x03408d0e
STRUrnikiSC15Dan3Urn2MinOFF | INT | IOD_STR_disk | I2210 | [8 empty] | 0x03408d0f
STRUrnikiSC15Dan3Urn3MinOFF | INT | IOD_STR_disk | I2211 | [8 empty] | 0x03408d10
STRUrnikiSC15Dan4Urn1UraON | INT | IOD_STR_disk | I2212 | [8 empty] | 0x03408d11
STRUrnikiSC15Dan4Urn2UraON | INT | IOD_STR_disk | I2213 | [8 empty] | 0x03408d12
STRUrnikiSC15Dan4Urn3UraON | INT | IOD_STR_disk | I2214 | [8 empty] | 0x03408d13
STRUrnikiSC15Dan4Urn1UraOFF | INT | IOD_STR_disk | I2215 | [8 empty] | 0x03408d14
STRUrnikiSC15Dan4Urn2UraOFF | INT | IOD_STR_disk | I2216 | [8 empty] | 0x03408d15
STRUrnikiSC15Dan4Urn3UraOFF | INT | IOD_STR_disk | I2217 | [8 empty] | 0x03408d16
STRUrnikiSC15Dan4Urn1MinON | INT | IOD_STR_disk | I2218 | [8 empty] | 0x03408d17
STRUrnikiSC15Dan4Urn2MinON | INT | IOD_STR_disk | I2219 | [8 empty] | 0x03408d18
STRUrnikiSC15Dan4Urn3MinON | INT | IOD_STR_disk | I2220 | [8 empty] | 0x03408d19
STRUrnikiSC15Dan4Urn1MinOFF | INT | IOD_STR_disk | I2221 | [8 empty] | 0x03408d1a
STRUrnikiSC15Dan4Urn2MinOFF | INT | IOD_STR_disk | I2222 | [8 empty] | 0x03408d1b
STRUrnikiSC15Dan4Urn3MinOFF | INT | IOD_STR_disk | I2223 | [8 empty] | 0x03408d1c
STRUrnikiSC15Dan5Urn1UraON | INT | IOD_STR_disk | I2224 | [8 empty] | 0x03408d1d
STRUrnikiSC15Dan5Urn2UraON | INT | IOD_STR_disk | I2225 | [8 empty] | 0x03408d1e
STRUrnikiSC15Dan5Urn3UraON | INT | IOD_STR_disk | I2226 | [8 empty] | 0x03408d1f
STRUrnikiSC15Dan5Urn1UraOFF | INT | IOD_STR_disk | I2227 | [8 empty] | 0x03408d20
STRUrnikiSC15Dan5Urn2UraOFF | INT | IOD_STR_disk | I2228 | [8 empty] | 0x03408d21
STRUrnikiSC15Dan5Urn3UraOFF | INT | IOD_STR_disk | I2229 | [8 empty] | 0x03408d22
STRUrnikiSC15Dan5Urn1MinON | INT | IOD_STR_disk | I2230 | [8 empty] | 0x03408d23
STRUrnikiSC15Dan5Urn2MinON | INT | IOD_STR_disk | I2231 | [8 empty] | 0x03408d24
STRUrnikiSC15Dan5Urn3MinON | INT | IOD_STR_disk | I2232 | [8 empty] | 0x03408d25
STRUrnikiSC15Dan5Urn1MinOFF | INT | IOD_STR_disk | I2233 | [8 empty] | 0x03408d26
STRUrnikiSC15Dan5Urn2MinOFF | INT | IOD_STR_disk | I2234 | [8 empty] | 0x03408d27
STRUrnikiSC15Dan5Urn3MinOFF | INT | IOD_STR_disk | I2235 | [8 empty] | 0x03408d28
STRUrnikiSC15Dan6Urn1UraON | INT | IOD_STR_disk | I2236 | [8 empty] | 0x03408d29
STRUrnikiSC15Dan6Urn2UraON | INT | IOD_STR_disk | I2237 | [8 empty] | 0x03408d2a
STRUrnikiSC15Dan6Urn3UraON | INT | IOD_STR_disk | I2238 | [8 empty] | 0x03408d2b
STRUrnikiSC15Dan6Urn1UraOFF | INT | IOD_STR_disk | I2239 | [8 empty] | 0x03408d2c
STRUrnikiSC15Dan6Urn2UraOFF | INT | IOD_STR_disk | I2240 | [8 empty] | 0x03408d2d
STRUrnikiSC15Dan6Urn3UraOFF | INT | IOD_STR_disk | I2241 | [8 empty] | 0x03408d2e
STRUrnikiSC15Dan6Urn1MinON | INT | IOD_STR_disk | I2242 | [8 empty] | 0x03408d2f
STRUrnikiSC15Dan6Urn2MinON | INT | IOD_STR_disk | I2243 | [8 empty] | 0x03408d30
STRUrnikiSC15Dan6Urn3MinON | INT | IOD_STR_disk | I2244 | [8 empty] | 0x03408d31
STRUrnikiSC15Dan6Urn1MinOFF | INT | IOD_STR_disk | I2245 | [8 empty] | 0x03408d32
STRUrnikiSC15Dan6Urn2MinOFF | INT | IOD_STR_disk | I2246 | [8 empty] | 0x03408d33
STRUrnikiSC15Dan6Urn3MinOFF | INT | IOD_STR_disk | I2247 | [8 empty] | 0x03408d34
STRUrnikiSC15Dan7Urn1UraON | INT | IOD_STR_disk | I2248 | [8 empty] | 0x03408d35
STRUrnikiSC15Dan7Urn2UraON | INT | IOD_STR_disk | I2249 | [8 empty] | 0x03408d36
STRUrnikiSC15Dan7Urn3UraON | INT | IOD_STR_disk | I2250 | [8 empty] | 0x03408d37
STRUrnikiSC15Dan7Urn1UraOFF | INT | IOD_STR_disk | I2251 | [8 empty] | 0x03408d38
STRUrnikiSC15Dan7Urn2UraOFF | INT | IOD_STR_disk | I2252 | [8 empty] | 0x03408d39
STRUrnikiSC15Dan7Urn3UraOFF | INT | IOD_STR_disk | I2253 | [8 empty] | 0x03408d3a
STRUrnikiSC15Dan7Urn1MinON | INT | IOD_STR_disk | I2254 | [8 empty] | 0x03408d3b
STRUrnikiSC15Dan7Urn2MinON | INT | IOD_STR_disk | I2255 | [8 empty] | 0x03408d3c
STRUrnikiSC15Dan7Urn3MinON | INT | IOD_STR_disk | I2256 | [8 empty] | 0x03408d3d
STRUrnikiSC15Dan7Urn1MinOFF | INT | IOD_STR_disk | I2257 | [8 empty] | 0x03408d3e
STRUrnikiSC15Dan7Urn2MinOFF | INT | IOD_STR_disk | I2258 | [8 empty] | 0x03408d3f
STRUrnikiSC15Dan7Urn3MinOFF | INT | IOD_STR_disk | I2259 | [8 empty] | 0x03408d40
STRUrnikiSC16Dan1Urn1UraON | INT | IOD_STR_disk | I2260 | [8 empty] | 0x03408d41
STRUrnikiSC16Dan1Urn2UraON | INT | IOD_STR_disk | I2261 | [8 empty] | 0x03408d42
STRUrnikiSC16Dan1Urn3UraON | INT | IOD_STR_disk | I2262 | [8 empty] | 0x03408d43
STRUrnikiSC16Dan1Urn1UraOFF | INT | IOD_STR_disk | I2263 | [8 empty] | 0x03408d44
STRUrnikiSC16Dan1Urn2UraOFF | INT | IOD_STR_disk | I2264 | [8 empty] | 0x03408d45
STRUrnikiSC16Dan1Urn3UraOFF | INT | IOD_STR_disk | I2265 | [8 empty] | 0x03408d46
STRUrnikiSC16Dan1Urn1MinON | INT | IOD_STR_disk | I2266 | [8 empty] | 0x03408d47
STRUrnikiSC16Dan1Urn2MinON | INT | IOD_STR_disk | I2267 | [8 empty] | 0x03408d48
STRUrnikiSC16Dan1Urn3MinON | INT | IOD_STR_disk | I2268 | [8 empty] | 0x03408d49
STRUrnikiSC16Dan1Urn1MinOFF | INT | IOD_STR_disk | I2269 | [8 empty] | 0x03408d4a
STRUrnikiSC16Dan1Urn2MinOFF | INT | IOD_STR_disk | I2270 | [8 empty] | 0x03408d4b
STRUrnikiSC16Dan1Urn3MinOFF | INT | IOD_STR_disk | I2271 | [8 empty] | 0x03408d4c
STRUrnikiSC16Dan2Urn1UraON | INT | IOD_STR_disk | I2272 | [8 empty] | 0x03408d4d
STRUrnikiSC16Dan2Urn2UraON | INT | IOD_STR_disk | I2273 | [8 empty] | 0x03408d4e
STRUrnikiSC16Dan2Urn3UraON | INT | IOD_STR_disk | I2274 | [8 empty] | 0x03408d4f
STRUrnikiSC16Dan2Urn1UraOFF | INT | IOD_STR_disk | I2275 | [8 empty] | 0x03408d50
STRUrnikiSC16Dan2Urn2UraOFF | INT | IOD_STR_disk | I2276 | [8 empty] | 0x03408d51
STRUrnikiSC16Dan2Urn3UraOFF | INT | IOD_STR_disk | I2277 | [8 empty] | 0x03408d52
STRUrnikiSC16Dan2Urn1MinON | INT | IOD_STR_disk | I2278 | [8 empty] | 0x03408d53
STRUrnikiSC16Dan2Urn2MinON | INT | IOD_STR_disk | I2279 | [8 empty] | 0x03408d54
STRUrnikiSC16Dan2Urn3MinON | INT | IOD_STR_disk | I2280 | [8 empty] | 0x03408d55
STRUrnikiSC16Dan2Urn1MinOFF | INT | IOD_STR_disk | I2281 | [8 empty] | 0x03408d56
STRUrnikiSC16Dan2Urn2MinOFF | INT | IOD_STR_disk | I2282 | [8 empty] | 0x03408d57
STRUrnikiSC16Dan2Urn3MinOFF | INT | IOD_STR_disk | I2283 | [8 empty] | 0x03408d58
STRUrnikiSC16Dan3Urn1UraON | INT | IOD_STR_disk | I2284 | [8 empty] | 0x03408d59
STRUrnikiSC16Dan3Urn2UraON | INT | IOD_STR_disk | I2285 | [8 empty] | 0x03408d5a
STRUrnikiSC16Dan3Urn3UraON | INT | IOD_STR_disk | I2286 | [8 empty] | 0x03408d5b
STRUrnikiSC16Dan3Urn1UraOFF | INT | IOD_STR_disk | I2287 | [8 empty] | 0x03408d5c
STRUrnikiSC16Dan3Urn2UraOFF | INT | IOD_STR_disk | I2288 | [8 empty] | 0x03408d5d
STRUrnikiSC16Dan3Urn3UraOFF | INT | IOD_STR_disk | I2289 | [8 empty] | 0x03408d5e
STRUrnikiSC16Dan3Urn1MinON | INT | IOD_STR_disk | I2290 | [8 empty] | 0x03408d5f
STRUrnikiSC16Dan3Urn2MinON | INT | IOD_STR_disk | I2291 | [8 empty] | 0x03408d60
STRUrnikiSC16Dan3Urn3MinON | INT | IOD_STR_disk | I2292 | [8 empty] | 0x03408d61
STRUrnikiSC16Dan3Urn1MinOFF | INT | IOD_STR_disk | I2293 | [8 empty] | 0x03408d62
STRUrnikiSC16Dan3Urn2MinOFF | INT | IOD_STR_disk | I2294 | [8 empty] | 0x03408d63
STRUrnikiSC16Dan3Urn3MinOFF | INT | IOD_STR_disk | I2295 | [8 empty] | 0x03408d64
STRUrnikiSC16Dan4Urn1UraON | INT | IOD_STR_disk | I2296 | [8 empty] | 0x03408d65
STRUrnikiSC16Dan4Urn2UraON | INT | IOD_STR_disk | I2297 | [8 empty] | 0x03408d66
STRUrnikiSC16Dan4Urn3UraON | INT | IOD_STR_disk | I2298 | [8 empty] | 0x03408d67
STRUrnikiSC16Dan4Urn1UraOFF | INT | IOD_STR_disk | I2299 | [8 empty] | 0x03408d68
STRUrnikiSC16Dan4Urn2UraOFF | INT | IOD_STR_disk | I2300 | [8 empty] | 0x03408d69
STRUrnikiSC16Dan4Urn3UraOFF | INT | IOD_STR_disk | I2301 | [8 empty] | 0x03408d6a
STRUrnikiSC16Dan4Urn1MinON | INT | IOD_STR_disk | I2302 | [8 empty] | 0x03408d6b
STRUrnikiSC16Dan4Urn2MinON | INT | IOD_STR_disk | I2303 | [8 empty] | 0x03408d6c
STRUrnikiSC16Dan4Urn3MinON | INT | IOD_STR_disk | I2304 | [8 empty] | 0x03408d6d
STRUrnikiSC16Dan4Urn1MinOFF | INT | IOD_STR_disk | I2305 | [8 empty] | 0x03408d6e
STRUrnikiSC16Dan4Urn2MinOFF | INT | IOD_STR_disk | I2306 | [8 empty] | 0x03408d6f
STRUrnikiSC16Dan4Urn3MinOFF | INT | IOD_STR_disk | I2307 | [8 empty] | 0x03408d70
STRUrnikiSC16Dan5Urn1UraON | INT | IOD_STR_disk | I2308 | [8 empty] | 0x03408d71
STRUrnikiSC16Dan5Urn2UraON | INT | IOD_STR_disk | I2309 | [8 empty] | 0x03408d72
STRUrnikiSC16Dan5Urn3UraON | INT | IOD_STR_disk | I2310 | [8 empty] | 0x03408d73
STRUrnikiSC16Dan5Urn1UraOFF | INT | IOD_STR_disk | I2311 | [8 empty] | 0x03408d74
STRUrnikiSC16Dan5Urn2UraOFF | INT | IOD_STR_disk | I2312 | [8 empty] | 0x03408d75
STRUrnikiSC16Dan5Urn3UraOFF | INT | IOD_STR_disk | I2313 | [8 empty] | 0x03408d76
STRUrnikiSC16Dan5Urn1MinON | INT | IOD_STR_disk | I2314 | [8 empty] | 0x03408d77
STRUrnikiSC16Dan5Urn2MinON | INT | IOD_STR_disk | I2315 | [8 empty] | 0x03408d78
STRUrnikiSC16Dan5Urn3MinON | INT | IOD_STR_disk | I2316 | [8 empty] | 0x03408d79
STRUrnikiSC16Dan5Urn1MinOFF | INT | IOD_STR_disk | I2317 | [8 empty] | 0x03408d7a
STRUrnikiSC16Dan5Urn2MinOFF | INT | IOD_STR_disk | I2318 | [8 empty] | 0x03408d7b
STRUrnikiSC16Dan5Urn3MinOFF | INT | IOD_STR_disk | I2319 | [8 empty] | 0x03408d7c
STRUrnikiSC16Dan6Urn1UraON | INT | IOD_STR_disk | I2320 | [8 empty] | 0x03408d7d
STRUrnikiSC16Dan6Urn2UraON | INT | IOD_STR_disk | I2321 | [8 empty] | 0x03408d7e
STRUrnikiSC16Dan6Urn3UraON | INT | IOD_STR_disk | I2322 | [8 empty] | 0x03408d7f
STRUrnikiSC16Dan6Urn1UraOFF | INT | IOD_STR_disk | I2323 | [8 empty] | 0x03408d80
STRUrnikiSC16Dan6Urn2UraOFF | INT | IOD_STR_disk | I2324 | [8 empty] | 0x03408d81
STRUrnikiSC16Dan6Urn3UraOFF | INT | IOD_STR_disk | I2325 | [8 empty] | 0x03408d82
STRUrnikiSC16Dan6Urn1MinON | INT | IOD_STR_disk | I2326 | [8 empty] | 0x03408d83
STRUrnikiSC16Dan6Urn2MinON | INT | IOD_STR_disk | I2327 | [8 empty] | 0x03408d84
STRUrnikiSC16Dan6Urn3MinON | INT | IOD_STR_disk | I2328 | [8 empty] | 0x03408d85
STRUrnikiSC16Dan6Urn1MinOFF | INT | IOD_STR_disk | I2329 | [8 empty] | 0x03408d86
STRUrnikiSC16Dan6Urn2MinOFF | INT | IOD_STR_disk | I2330 | [8 empty] | 0x03408d87
STRUrnikiSC16Dan6Urn3MinOFF | INT | IOD_STR_disk | I2331 | [8 empty] | 0x03408d88
STRUrnikiSC16Dan7Urn1UraON | INT | IOD_STR_disk | I2332 | [8 empty] | 0x03408d89
STRUrnikiSC16Dan7Urn2UraON | INT | IOD_STR_disk | I2333 | [8 empty] | 0x03408d8a
STRUrnikiSC16Dan7Urn3UraON | INT | IOD_STR_disk | I2334 | [8 empty] | 0x03408d8b
STRUrnikiSC16Dan7Urn1UraOFF | INT | IOD_STR_disk | I2335 | [8 empty] | 0x03408d8c
STRUrnikiSC16Dan7Urn2UraOFF | INT | IOD_STR_disk | I2336 | [8 empty] | 0x03408d8d
STRUrnikiSC16Dan7Urn3UraOFF | INT | IOD_STR_disk | I2337 | [8 empty] | 0x03408d8e
STRUrnikiSC16Dan7Urn1MinON | INT | IOD_STR_disk | I2338 | [8 empty] | 0x03408d8f
STRUrnikiSC16Dan7Urn2MinON | INT | IOD_STR_disk | I2339 | [8 empty] | 0x03408d90
STRUrnikiSC16Dan7Urn3MinON | INT | IOD_STR_disk | I2340 | [8 empty] | 0x03408d91
STRUrnikiSC16Dan7Urn1MinOFF | INT | IOD_STR_disk | I2341 | [8 empty] | 0x03408d92
STRUrnikiSC16Dan7Urn2MinOFF | INT | IOD_STR_disk | I2342 | [8 empty] | 0x03408d93
STRUrnikiSC16Dan7Urn3MinOFF | INT | IOD_STR_disk | I2343 | [8 empty] | 0x03408d94
STRUrnikiSC17Dan1Urn1UraON | INT | IOD_STR_disk | I2344 | [8 empty] | 0x03408d95
STRUrnikiSC17Dan1Urn2UraON | INT | IOD_STR_disk | I2345 | [8 empty] | 0x03408d96
STRUrnikiSC17Dan1Urn3UraON | INT | IOD_STR_disk | I2346 | [8 empty] | 0x03408d97
STRUrnikiSC17Dan1Urn1UraOFF | INT | IOD_STR_disk | I2347 | [8 empty] | 0x03408d98
STRUrnikiSC17Dan1Urn2UraOFF | INT | IOD_STR_disk | I2348 | [8 empty] | 0x03408d99
STRUrnikiSC17Dan1Urn3UraOFF | INT | IOD_STR_disk | I2349 | [8 empty] | 0x03408d9a
STRUrnikiSC17Dan1Urn1MinON | INT | IOD_STR_disk | I2350 | [8 empty] | 0x03408d9b
STRUrnikiSC17Dan1Urn2MinON | INT | IOD_STR_disk | I2351 | [8 empty] | 0x03408d9c
STRUrnikiSC17Dan1Urn3MinON | INT | IOD_STR_disk | I2352 | [8 empty] | 0x03408d9d
STRUrnikiSC17Dan1Urn1MinOFF | INT | IOD_STR_disk | I2353 | [8 empty] | 0x03408d9e
STRUrnikiSC17Dan1Urn2MinOFF | INT | IOD_STR_disk | I2354 | [8 empty] | 0x03408d9f
STRUrnikiSC17Dan1Urn3MinOFF | INT | IOD_STR_disk | I2355 | [8 empty] | 0x03408da0
STRUrnikiSC17Dan2Urn1UraON | INT | IOD_STR_disk | I2356 | [8 empty] | 0x03408da1
STRUrnikiSC17Dan2Urn2UraON | INT | IOD_STR_disk | I2357 | [8 empty] | 0x03408da2
STRUrnikiSC17Dan2Urn3UraON | INT | IOD_STR_disk | I2358 | [8 empty] | 0x03408da3
STRUrnikiSC17Dan2Urn1UraOFF | INT | IOD_STR_disk | I2359 | [8 empty] | 0x03408da4
STRUrnikiSC17Dan2Urn2UraOFF | INT | IOD_STR_disk | I2360 | [8 empty] | 0x03408da5
STRUrnikiSC17Dan2Urn3UraOFF | INT | IOD_STR_disk | I2361 | [8 empty] | 0x03408da6
STRUrnikiSC17Dan2Urn1MinON | INT | IOD_STR_disk | I2362 | [8 empty] | 0x03408da7
STRUrnikiSC17Dan2Urn2MinON | INT | IOD_STR_disk | I2363 | [8 empty] | 0x03408da8
STRUrnikiSC17Dan2Urn3MinON | INT | IOD_STR_disk | I2364 | [8 empty] | 0x03408da9
STRUrnikiSC17Dan2Urn1MinOFF | INT | IOD_STR_disk | I2365 | [8 empty] | 0x03408daa
STRUrnikiSC17Dan2Urn2MinOFF | INT | IOD_STR_disk | I2366 | [8 empty] | 0x03408dab
STRUrnikiSC17Dan2Urn3MinOFF | INT | IOD_STR_disk | I2367 | [8 empty] | 0x03408dac
STRUrnikiSC17Dan3Urn1UraON | INT | IOD_STR_disk | I2368 | [8 empty] | 0x03408dad
STRUrnikiSC17Dan3Urn2UraON | INT | IOD_STR_disk | I2369 | [8 empty] | 0x03408dae
STRUrnikiSC17Dan3Urn3UraON | INT | IOD_STR_disk | I2370 | [8 empty] | 0x03408daf
STRUrnikiSC17Dan3Urn1UraOFF | INT | IOD_STR_disk | I2371 | [8 empty] | 0x03408db0
STRUrnikiSC17Dan3Urn2UraOFF | INT | IOD_STR_disk | I2372 | [8 empty] | 0x03408db1
STRUrnikiSC17Dan3Urn3UraOFF | INT | IOD_STR_disk | I2373 | [8 empty] | 0x03408db2
STRUrnikiSC17Dan3Urn1MinON | INT | IOD_STR_disk | I2374 | [8 empty] | 0x03408db3
STRUrnikiSC17Dan3Urn2MinON | INT | IOD_STR_disk | I2375 | [8 empty] | 0x03408db4
STRUrnikiSC17Dan3Urn3MinON | INT | IOD_STR_disk | I2376 | [8 empty] | 0x03408db5
STRUrnikiSC17Dan3Urn1MinOFF | INT | IOD_STR_disk | I2377 | [8 empty] | 0x03408db6
STRUrnikiSC17Dan3Urn2MinOFF | INT | IOD_STR_disk | I2378 | [8 empty] | 0x03408db7
STRUrnikiSC17Dan3Urn3MinOFF | INT | IOD_STR_disk | I2379 | [8 empty] | 0x03408db8
STRUrnikiSC17Dan4Urn1UraON | INT | IOD_STR_disk | I2380 | [8 empty] | 0x03408db9
STRUrnikiSC17Dan4Urn2UraON | INT | IOD_STR_disk | I2381 | [8 empty] | 0x03408dba
STRUrnikiSC17Dan4Urn3UraON | INT | IOD_STR_disk | I2382 | [8 empty] | 0x03408dbb
STRUrnikiSC17Dan4Urn1UraOFF | INT | IOD_STR_disk | I2383 | [8 empty] | 0x03408dbc
STRUrnikiSC17Dan4Urn2UraOFF | INT | IOD_STR_disk | I2384 | [8 empty] | 0x03408dbd
STRUrnikiSC17Dan4Urn3UraOFF | INT | IOD_STR_disk | I2385 | [8 empty] | 0x03408dbe
STRUrnikiSC17Dan4Urn1MinON | INT | IOD_STR_disk | I2386 | [8 empty] | 0x03408dbf
STRUrnikiSC17Dan4Urn2MinON | INT | IOD_STR_disk | I2387 | [8 empty] | 0x03408dc0
STRUrnikiSC17Dan4Urn3MinON | INT | IOD_STR_disk | I2388 | [8 empty] | 0x03408dc1
STRUrnikiSC17Dan4Urn1MinOFF | INT | IOD_STR_disk | I2389 | [8 empty] | 0x03408dc2
STRUrnikiSC17Dan4Urn2MinOFF | INT | IOD_STR_disk | I2390 | [8 empty] | 0x03408dc3
STRUrnikiSC17Dan4Urn3MinOFF | INT | IOD_STR_disk | I2391 | [8 empty] | 0x03408dc4
STRUrnikiSC17Dan5Urn1UraON | INT | IOD_STR_disk | I2392 | [8 empty] | 0x03408dc5
STRUrnikiSC17Dan5Urn2UraON | INT | IOD_STR_disk | I2393 | [8 empty] | 0x03408dc6
STRUrnikiSC17Dan5Urn3UraON | INT | IOD_STR_disk | I2394 | [8 empty] | 0x03408dc7
STRUrnikiSC17Dan5Urn1UraOFF | INT | IOD_STR_disk | I2395 | [8 empty] | 0x03408dc8
STRUrnikiSC17Dan5Urn2UraOFF | INT | IOD_STR_disk | I2396 | [8 empty] | 0x03408dc9
STRUrnikiSC17Dan5Urn3UraOFF | INT | IOD_STR_disk | I2397 | [8 empty] | 0x03408dca
STRUrnikiSC17Dan5Urn1MinON | INT | IOD_STR_disk | I2398 | [8 empty] | 0x03408dcb
STRUrnikiSC17Dan5Urn2MinON | INT | IOD_STR_disk | I2399 | [8 empty] | 0x03408dcc
STRUrnikiSC17Dan5Urn3MinON | INT | IOD_STR_disk | I2400 | [8 empty] | 0x03408dcd
STRUrnikiSC17Dan5Urn1MinOFF | INT | IOD_STR_disk | I2401 | [8 empty] | 0x03408dce
STRUrnikiSC17Dan5Urn2MinOFF | INT | IOD_STR_disk | I2402 | [8 empty] | 0x03408dcf
STRUrnikiSC17Dan5Urn3MinOFF | INT | IOD_STR_disk | I2403 | [8 empty] | 0x03408dd0
STRUrnikiSC17Dan6Urn1UraON | INT | IOD_STR_disk | I2404 | [8 empty] | 0x03408dd1
STRUrnikiSC17Dan6Urn2UraON | INT | IOD_STR_disk | I2405 | [8 empty] | 0x03408dd2
STRUrnikiSC17Dan6Urn3UraON | INT | IOD_STR_disk | I2406 | [8 empty] | 0x03408dd3
STRUrnikiSC17Dan6Urn1UraOFF | INT | IOD_STR_disk | I2407 | [8 empty] | 0x03408dd4
STRUrnikiSC17Dan6Urn2UraOFF | INT | IOD_STR_disk | I2408 | [8 empty] | 0x03408dd5
STRUrnikiSC17Dan6Urn3UraOFF | INT | IOD_STR_disk | I2409 | [8 empty] | 0x03408dd6
STRUrnikiSC17Dan6Urn1MinON | INT | IOD_STR_disk | I2410 | [8 empty] | 0x03408dd7
STRUrnikiSC17Dan6Urn2MinON | INT | IOD_STR_disk | I2411 | [8 empty] | 0x03408dd8
STRUrnikiSC17Dan6Urn3MinON | INT | IOD_STR_disk | I2412 | [8 empty] | 0x03408dd9
STRUrnikiSC17Dan6Urn1MinOFF | INT | IOD_STR_disk | I2413 | [8 empty] | 0x03408dda
STRUrnikiSC17Dan6Urn2MinOFF | INT | IOD_STR_disk | I2414 | [8 empty] | 0x03408ddb
STRUrnikiSC17Dan6Urn3MinOFF | INT | IOD_STR_disk | I2415 | [8 empty] | 0x03408ddc
STRUrnikiSC17Dan7Urn1UraON | INT | IOD_STR_disk | I2416 | [8 empty] | 0x03408ddd
STRUrnikiSC17Dan7Urn2UraON | INT | IOD_STR_disk | I2417 | [8 empty] | 0x03408dde
STRUrnikiSC17Dan7Urn3UraON | INT | IOD_STR_disk | I2418 | [8 empty] | 0x03408ddf
STRUrnikiSC17Dan7Urn1UraOFF | INT | IOD_STR_disk | I2419 | [8 empty] | 0x03408de0
STRUrnikiSC17Dan7Urn2UraOFF | INT | IOD_STR_disk | I2420 | [8 empty] | 0x03408de1
STRUrnikiSC17Dan7Urn3UraOFF | INT | IOD_STR_disk | I2421 | [8 empty] | 0x03408de2
STRUrnikiSC17Dan7Urn1MinON | INT | IOD_STR_disk | I2422 | [8 empty] | 0x03408de3
STRUrnikiSC17Dan7Urn2MinON | INT | IOD_STR_disk | I2423 | [8 empty] | 0x03408de4
STRUrnikiSC17Dan7Urn3MinON | INT | IOD_STR_disk | I2424 | [8 empty] | 0x03408de5
STRUrnikiSC17Dan7Urn1MinOFF | INT | IOD_STR_disk | I2425 | [8 empty] | 0x03408de6
STRUrnikiSC17Dan7Urn2MinOFF | INT | IOD_STR_disk | I2426 | [8 empty] | 0x03408de7
STRUrnikiSC17Dan7Urn3MinOFF | INT | IOD_STR_disk | I2427 | [8 empty] | 0x03408de8
STRUrnikiSC18Dan1Urn1UraON | INT | IOD_STR_disk | I2428 | [8 empty] | 0x03408de9
STRUrnikiSC18Dan1Urn2UraON | INT | IOD_STR_disk | I2429 | [8 empty] | 0x03408dea
STRUrnikiSC18Dan1Urn3UraON | INT | IOD_STR_disk | I2430 | [8 empty] | 0x03408deb
STRUrnikiSC18Dan1Urn1UraOFF | INT | IOD_STR_disk | I2431 | [8 empty] | 0x03408dec
STRUrnikiSC18Dan1Urn2UraOFF | INT | IOD_STR_disk | I2432 | [8 empty] | 0x03408ded
STRUrnikiSC18Dan1Urn3UraOFF | INT | IOD_STR_disk | I2433 | [8 empty] | 0x03408dee
STRUrnikiSC18Dan1Urn1MinON | INT | IOD_STR_disk | I2434 | [8 empty] | 0x03408def
STRUrnikiSC18Dan1Urn2MinON | INT | IOD_STR_disk | I2435 | [8 empty] | 0x03408df0
STRUrnikiSC18Dan1Urn3MinON | INT | IOD_STR_disk | I2436 | [8 empty] | 0x03408df1
STRUrnikiSC18Dan1Urn1MinOFF | INT | IOD_STR_disk | I2437 | [8 empty] | 0x03408df2
STRUrnikiSC18Dan1Urn2MinOFF | INT | IOD_STR_disk | I2438 | [8 empty] | 0x03408df3
STRUrnikiSC18Dan1Urn3MinOFF | INT | IOD_STR_disk | I2439 | [8 empty] | 0x03408df4
STRUrnikiSC18Dan2Urn1UraON | INT | IOD_STR_disk | I2440 | [8 empty] | 0x03408df5
STRUrnikiSC18Dan2Urn2UraON | INT | IOD_STR_disk | I2441 | [8 empty] | 0x03408df6
STRUrnikiSC18Dan2Urn3UraON | INT | IOD_STR_disk | I2442 | [8 empty] | 0x03408df7
STRUrnikiSC18Dan2Urn1UraOFF | INT | IOD_STR_disk | I2443 | [8 empty] | 0x03408df8
STRUrnikiSC18Dan2Urn2UraOFF | INT | IOD_STR_disk | I2444 | [8 empty] | 0x03408df9
STRUrnikiSC18Dan2Urn3UraOFF | INT | IOD_STR_disk | I2445 | [8 empty] | 0x03408dfa
STRUrnikiSC18Dan2Urn1MinON | INT | IOD_STR_disk | I2446 | [8 empty] | 0x03408dfb
STRUrnikiSC18Dan2Urn2MinON | INT | IOD_STR_disk | I2447 | [8 empty] | 0x03408dfc
STRUrnikiSC18Dan2Urn3MinON | INT | IOD_STR_disk | I2448 | [8 empty] | 0x03408dfd
STRUrnikiSC18Dan2Urn1MinOFF | INT | IOD_STR_disk | I2449 | [8 empty] | 0x03408dfe
STRUrnikiSC18Dan2Urn2MinOFF | INT | IOD_STR_disk | I2450 | [8 empty] | 0x03408dff
STRUrnikiSC18Dan2Urn3MinOFF | INT | IOD_STR_disk | I2451 | [8 empty] | 0x03408e00
STRUrnikiSC18Dan3Urn1UraON | INT | IOD_STR_disk | I2452 | [8 empty] | 0x03408e01
STRUrnikiSC18Dan3Urn2UraON | INT | IOD_STR_disk | I2453 | [8 empty] | 0x03408e02
STRUrnikiSC18Dan3Urn3UraON | INT | IOD_STR_disk | I2454 | [8 empty] | 0x03408e03
STRUrnikiSC18Dan3Urn1UraOFF | INT | IOD_STR_disk | I2455 | [8 empty] | 0x03408e04
STRUrnikiSC18Dan3Urn2UraOFF | INT | IOD_STR_disk | I2456 | [8 empty] | 0x03408e05
STRUrnikiSC18Dan3Urn3UraOFF | INT | IOD_STR_disk | I2457 | [8 empty] | 0x03408e06
STRUrnikiSC18Dan3Urn1MinON | INT | IOD_STR_disk | I2458 | [8 empty] | 0x03408e07
STRUrnikiSC18Dan3Urn2MinON | INT | IOD_STR_disk | I2459 | [8 empty] | 0x03408e08
STRUrnikiSC18Dan3Urn3MinON | INT | IOD_STR_disk | I2460 | [8 empty] | 0x03408e09
STRUrnikiSC18Dan3Urn1MinOFF | INT | IOD_STR_disk | I2461 | [8 empty] | 0x03408e0a
STRUrnikiSC18Dan3Urn2MinOFF | INT | IOD_STR_disk | I2462 | [8 empty] | 0x03408e0b
STRUrnikiSC18Dan3Urn3MinOFF | INT | IOD_STR_disk | I2463 | [8 empty] | 0x03408e0c
STRUrnikiSC18Dan4Urn1UraON | INT | IOD_STR_disk | I2464 | [8 empty] | 0x03408e0d
STRUrnikiSC18Dan4Urn2UraON | INT | IOD_STR_disk | I2465 | [8 empty] | 0x03408e0e
STRUrnikiSC18Dan4Urn3UraON | INT | IOD_STR_disk | I2466 | [8 empty] | 0x03408e0f
STRUrnikiSC18Dan4Urn1UraOFF | INT | IOD_STR_disk | I2467 | [8 empty] | 0x03408e10
STRUrnikiSC18Dan4Urn2UraOFF | INT | IOD_STR_disk | I2468 | [8 empty] | 0x03408e11
STRUrnikiSC18Dan4Urn3UraOFF | INT | IOD_STR_disk | I2469 | [8 empty] | 0x03408e12
STRUrnikiSC18Dan4Urn1MinON | INT | IOD_STR_disk | I2470 | [8 empty] | 0x03408e13
STRUrnikiSC18Dan4Urn2MinON | INT | IOD_STR_disk | I2471 | [8 empty] | 0x03408e14
STRUrnikiSC18Dan4Urn3MinON | INT | IOD_STR_disk | I2472 | [8 empty] | 0x03408e15
STRUrnikiSC18Dan4Urn1MinOFF | INT | IOD_STR_disk | I2473 | [8 empty] | 0x03408e16
STRUrnikiSC18Dan4Urn2MinOFF | INT | IOD_STR_disk | I2474 | [8 empty] | 0x03408e17
STRUrnikiSC18Dan4Urn3MinOFF | INT | IOD_STR_disk | I2475 | [8 empty] | 0x03408e18
STRUrnikiSC18Dan5Urn1UraON | INT | IOD_STR_disk | I2476 | [8 empty] | 0x03408e19
STRUrnikiSC18Dan5Urn2UraON | INT | IOD_STR_disk | I2477 | [8 empty] | 0x03408e1a
STRUrnikiSC18Dan5Urn3UraON | INT | IOD_STR_disk | I2478 | [8 empty] | 0x03408e1b
STRUrnikiSC18Dan5Urn1UraOFF | INT | IOD_STR_disk | I2479 | [8 empty] | 0x03408e1c
STRUrnikiSC18Dan5Urn2UraOFF | INT | IOD_STR_disk | I2480 | [8 empty] | 0x03408e1d
STRUrnikiSC18Dan5Urn3UraOFF | INT | IOD_STR_disk | I2481 | [8 empty] | 0x03408e1e
STRUrnikiSC18Dan5Urn1MinON | INT | IOD_STR_disk | I2482 | [8 empty] | 0x03408e1f
STRUrnikiSC18Dan5Urn2MinON | INT | IOD_STR_disk | I2483 | [8 empty] | 0x03408e20
STRUrnikiSC18Dan5Urn3MinON | INT | IOD_STR_disk | I2484 | [8 empty] | 0x03408e21
STRUrnikiSC18Dan5Urn1MinOFF | INT | IOD_STR_disk | I2485 | [8 empty] | 0x03408e22
STRUrnikiSC18Dan5Urn2MinOFF | INT | IOD_STR_disk | I2486 | [8 empty] | 0x03408e23
STRUrnikiSC18Dan5Urn3MinOFF | INT | IOD_STR_disk | I2487 | [8 empty] | 0x03408e24
STRUrnikiSC18Dan6Urn1UraON | INT | IOD_STR_disk | I2488 | [8 empty] | 0x03408e25
STRUrnikiSC18Dan6Urn2UraON | INT | IOD_STR_disk | I2489 | [8 empty] | 0x03408e26
STRUrnikiSC18Dan6Urn3UraON | INT | IOD_STR_disk | I2490 | [8 empty] | 0x03408e27
STRUrnikiSC18Dan6Urn1UraOFF | INT | IOD_STR_disk | I2491 | [8 empty] | 0x03408e28
STRUrnikiSC18Dan6Urn2UraOFF | INT | IOD_STR_disk | I2492 | [8 empty] | 0x03408e29
STRUrnikiSC18Dan6Urn3UraOFF | INT | IOD_STR_disk | I2493 | [8 empty] | 0x03408e2a
STRUrnikiSC18Dan6Urn1MinON | INT | IOD_STR_disk | I2494 | [8 empty] | 0x03408e2b
STRUrnikiSC18Dan6Urn2MinON | INT | IOD_STR_disk | I2495 | [8 empty] | 0x03408e2c
STRUrnikiSC18Dan6Urn3MinON | INT | IOD_STR_disk | I2496 | [8 empty] | 0x03408e2d
STRUrnikiSC18Dan6Urn1MinOFF | INT | IOD_STR_disk | I2497 | [8 empty] | 0x03408e2e
STRUrnikiSC18Dan6Urn2MinOFF | INT | IOD_STR_disk | I2498 | [8 empty] | 0x03408e2f
STRUrnikiSC18Dan6Urn3MinOFF | INT | IOD_STR_disk | I2499 | [8 empty] | 0x03408e30
STRUrnikiSC18Dan7Urn1UraON | INT | IOD_STR_disk | I2500 | [8 empty] | 0x03408e31
STRUrnikiSC18Dan7Urn2UraON | INT | IOD_STR_disk | I2501 | [8 empty] | 0x03408e32
STRUrnikiSC18Dan7Urn3UraON | INT | IOD_STR_disk | I2502 | [8 empty] | 0x03408e33
STRUrnikiSC18Dan7Urn1UraOFF | INT | IOD_STR_disk | I2503 | [8 empty] | 0x03408e34
STRUrnikiSC18Dan7Urn2UraOFF | INT | IOD_STR_disk | I2504 | [8 empty] | 0x03408e35
STRUrnikiSC18Dan7Urn3UraOFF | INT | IOD_STR_disk | I2505 | [8 empty] | 0x03408e36
STRUrnikiSC18Dan7Urn1MinON | INT | IOD_STR_disk | I2506 | [8 empty] | 0x03408e37
STRUrnikiSC18Dan7Urn2MinON | INT | IOD_STR_disk | I2507 | [8 empty] | 0x03408e38
STRUrnikiSC18Dan7Urn3MinON | INT | IOD_STR_disk | I2508 | [8 empty] | 0x03408e39
STRUrnikiSC18Dan7Urn1MinOFF | INT | IOD_STR_disk | I2509 | [8 empty] | 0x03408e3a
STRUrnikiSC18Dan7Urn2MinOFF | INT | IOD_STR_disk | I2510 | [8 empty] | 0x03408e3b
STRUrnikiSC18Dan7Urn3MinOFF | INT | IOD_STR_disk | I2511 | [8 empty] | 0x03408e3c
STRUrnikiSC19Dan1Urn1UraON | INT | IOD_STR_disk | I2512 | [8 empty] | 0x03408e3d
STRUrnikiSC19Dan1Urn2UraON | INT | IOD_STR_disk | I2513 | [8 empty] | 0x03408e3e
STRUrnikiSC19Dan1Urn3UraON | INT | IOD_STR_disk | I2514 | [8 empty] | 0x03408e3f
STRUrnikiSC19Dan1Urn1UraOFF | INT | IOD_STR_disk | I2515 | [8 empty] | 0x03408e40
STRUrnikiSC19Dan1Urn2UraOFF | INT | IOD_STR_disk | I2516 | [8 empty] | 0x03408e41
STRUrnikiSC19Dan1Urn3UraOFF | INT | IOD_STR_disk | I2517 | [8 empty] | 0x03408e42
STRUrnikiSC19Dan1Urn1MinON | INT | IOD_STR_disk | I2518 | [8 empty] | 0x03408e43
STRUrnikiSC19Dan1Urn2MinON | INT | IOD_STR_disk | I2519 | [8 empty] | 0x03408e44
STRUrnikiSC19Dan1Urn3MinON | INT | IOD_STR_disk | I2520 | [8 empty] | 0x03408e45
STRUrnikiSC19Dan1Urn1MinOFF | INT | IOD_STR_disk | I2521 | [8 empty] | 0x03408e46
STRUrnikiSC19Dan1Urn2MinOFF | INT | IOD_STR_disk | I2522 | [8 empty] | 0x03408e47
STRUrnikiSC19Dan1Urn3MinOFF | INT | IOD_STR_disk | I2523 | [8 empty] | 0x03408e48
STRUrnikiSC19Dan2Urn1UraON | INT | IOD_STR_disk | I2524 | [8 empty] | 0x03408e49
STRUrnikiSC19Dan2Urn2UraON | INT | IOD_STR_disk | I2525 | [8 empty] | 0x03408e4a
STRUrnikiSC19Dan2Urn3UraON | INT | IOD_STR_disk | I2526 | [8 empty] | 0x03408e4b
STRUrnikiSC19Dan2Urn1UraOFF | INT | IOD_STR_disk | I2527 | [8 empty] | 0x03408e4c
STRUrnikiSC19Dan2Urn2UraOFF | INT | IOD_STR_disk | I2528 | [8 empty] | 0x03408e4d
STRUrnikiSC19Dan2Urn3UraOFF | INT | IOD_STR_disk | I2529 | [8 empty] | 0x03408e4e
STRUrnikiSC19Dan2Urn1MinON | INT | IOD_STR_disk | I2530 | [8 empty] | 0x03408e4f
STRUrnikiSC19Dan2Urn2MinON | INT | IOD_STR_disk | I2531 | [8 empty] | 0x03408e50
STRUrnikiSC19Dan2Urn3MinON | INT | IOD_STR_disk | I2532 | [8 empty] | 0x03408e51
STRUrnikiSC19Dan2Urn1MinOFF | INT | IOD_STR_disk | I2533 | [8 empty] | 0x03408e52
STRUrnikiSC19Dan2Urn2MinOFF | INT | IOD_STR_disk | I2534 | [8 empty] | 0x03408e53
STRUrnikiSC19Dan2Urn3MinOFF | INT | IOD_STR_disk | I2535 | [8 empty] | 0x03408e54
STRUrnikiSC19Dan3Urn1UraON | INT | IOD_STR_disk | I2536 | [8 empty] | 0x03408e55
STRUrnikiSC19Dan3Urn2UraON | INT | IOD_STR_disk | I2537 | [8 empty] | 0x03408e56
STRUrnikiSC19Dan3Urn3UraON | INT | IOD_STR_disk | I2538 | [8 empty] | 0x03408e57
STRUrnikiSC19Dan3Urn1UraOFF | INT | IOD_STR_disk | I2539 | [8 empty] | 0x03408e58
STRUrnikiSC19Dan3Urn2UraOFF | INT | IOD_STR_disk | I2540 | [8 empty] | 0x03408e59
STRUrnikiSC19Dan3Urn3UraOFF | INT | IOD_STR_disk | I2541 | [8 empty] | 0x03408e5a
STRUrnikiSC19Dan3Urn1MinON | INT | IOD_STR_disk | I2542 | [8 empty] | 0x03408e5b
STRUrnikiSC19Dan3Urn2MinON | INT | IOD_STR_disk | I2543 | [8 empty] | 0x03408e5c
STRUrnikiSC19Dan3Urn3MinON | INT | IOD_STR_disk | I2544 | [8 empty] | 0x03408e5d
STRUrnikiSC19Dan3Urn1MinOFF | INT | IOD_STR_disk | I2545 | [8 empty] | 0x03408e5e
STRUrnikiSC19Dan3Urn2MinOFF | INT | IOD_STR_disk | I2546 | [8 empty] | 0x03408e5f
STRUrnikiSC19Dan3Urn3MinOFF | INT | IOD_STR_disk | I2547 | [8 empty] | 0x03408e60
STRUrnikiSC19Dan4Urn1UraON | INT | IOD_STR_disk | I2548 | [8 empty] | 0x03408e61
STRUrnikiSC19Dan4Urn2UraON | INT | IOD_STR_disk | I2549 | [8 empty] | 0x03408e62
STRUrnikiSC19Dan4Urn3UraON | INT | IOD_STR_disk | I2550 | [8 empty] | 0x03408e63
STRUrnikiSC19Dan4Urn1UraOFF | INT | IOD_STR_disk | I2551 | [8 empty] | 0x03408e64
STRUrnikiSC19Dan4Urn2UraOFF | INT | IOD_STR_disk | I2552 | [8 empty] | 0x03408e65
STRUrnikiSC19Dan4Urn3UraOFF | INT | IOD_STR_disk | I2553 | [8 empty] | 0x03408e66
STRUrnikiSC19Dan4Urn1MinON | INT | IOD_STR_disk | I2554 | [8 empty] | 0x03408e67
STRUrnikiSC19Dan4Urn2MinON | INT | IOD_STR_disk | I2555 | [8 empty] | 0x03408e68
STRUrnikiSC19Dan4Urn3MinON | INT | IOD_STR_disk | I2556 | [8 empty] | 0x03408e69
STRUrnikiSC19Dan4Urn1MinOFF | INT | IOD_STR_disk | I2557 | [8 empty] | 0x03408e6a
STRUrnikiSC19Dan4Urn2MinOFF | INT | IOD_STR_disk | I2558 | [8 empty] | 0x03408e6b
STRUrnikiSC19Dan4Urn3MinOFF | INT | IOD_STR_disk | I2559 | [8 empty] | 0x03408e6c
STRUrnikiSC19Dan5Urn1UraON | INT | IOD_STR_disk | I2560 | [8 empty] | 0x03408e6d
STRUrnikiSC19Dan5Urn2UraON | INT | IOD_STR_disk | I2561 | [8 empty] | 0x03408e6e
STRUrnikiSC19Dan5Urn3UraON | INT | IOD_STR_disk | I2562 | [8 empty] | 0x03408e6f
STRUrnikiSC19Dan5Urn1UraOFF | INT | IOD_STR_disk | I2563 | [8 empty] | 0x03408e70
STRUrnikiSC19Dan5Urn2UraOFF | INT | IOD_STR_disk | I2564 | [8 empty] | 0x03408e71
STRUrnikiSC19Dan5Urn3UraOFF | INT | IOD_STR_disk | I2565 | [8 empty] | 0x03408e72
STRUrnikiSC19Dan5Urn1MinON | INT | IOD_STR_disk | I2566 | [8 empty] | 0x03408e73
STRUrnikiSC19Dan5Urn2MinON | INT | IOD_STR_disk | I2567 | [8 empty] | 0x03408e74
STRUrnikiSC19Dan5Urn3MinON | INT | IOD_STR_disk | I2568 | [8 empty] | 0x03408e75
STRUrnikiSC19Dan5Urn1MinOFF | INT | IOD_STR_disk | I2569 | [8 empty] | 0x03408e76
STRUrnikiSC19Dan5Urn2MinOFF | INT | IOD_STR_disk | I2570 | [8 empty] | 0x03408e77
STRUrnikiSC19Dan5Urn3MinOFF | INT | IOD_STR_disk | I2571 | [8 empty] | 0x03408e78
STRUrnikiSC19Dan6Urn1UraON | INT | IOD_STR_disk | I2572 | [8 empty] | 0x03408e79
STRUrnikiSC19Dan6Urn2UraON | INT | IOD_STR_disk | I2573 | [8 empty] | 0x03408e7a
STRUrnikiSC19Dan6Urn3UraON | INT | IOD_STR_disk | I2574 | [8 empty] | 0x03408e7b
STRUrnikiSC19Dan6Urn1UraOFF | INT | IOD_STR_disk | I2575 | [8 empty] | 0x03408e7c
STRUrnikiSC19Dan6Urn2UraOFF | INT | IOD_STR_disk | I2576 | [8 empty] | 0x03408e7d
STRUrnikiSC19Dan6Urn3UraOFF | INT | IOD_STR_disk | I2577 | [8 empty] | 0x03408e7e
STRUrnikiSC19Dan6Urn1MinON | INT | IOD_STR_disk | I2578 | [8 empty] | 0x03408e7f
STRUrnikiSC19Dan6Urn2MinON | INT | IOD_STR_disk | I2579 | [8 empty] | 0x03408e80
STRUrnikiSC19Dan6Urn3MinON | INT | IOD_STR_disk | I2580 | [8 empty] | 0x03408e81
STRUrnikiSC19Dan6Urn1MinOFF | INT | IOD_STR_disk | I2581 | [8 empty] | 0x03408e82
STRUrnikiSC19Dan6Urn2MinOFF | INT | IOD_STR_disk | I2582 | [8 empty] | 0x03408e83
STRUrnikiSC19Dan6Urn3MinOFF | INT | IOD_STR_disk | I2583 | [8 empty] | 0x03408e84
STRUrnikiSC19Dan7Urn1UraON | INT | IOD_STR_disk | I2584 | [8 empty] | 0x03408e85
STRUrnikiSC19Dan7Urn2UraON | INT | IOD_STR_disk | I2585 | [8 empty] | 0x03408e86
STRUrnikiSC19Dan7Urn3UraON | INT | IOD_STR_disk | I2586 | [8 empty] | 0x03408e87
STRUrnikiSC19Dan7Urn1UraOFF | INT | IOD_STR_disk | I2587 | [8 empty] | 0x03408e88
STRUrnikiSC19Dan7Urn2UraOFF | INT | IOD_STR_disk | I2588 | [8 empty] | 0x03408e89
STRUrnikiSC19Dan7Urn3UraOFF | INT | IOD_STR_disk | I2589 | [8 empty] | 0x03408e8a
STRUrnikiSC19Dan7Urn1MinON | INT | IOD_STR_disk | I2590 | [8 empty] | 0x03408e8b
STRUrnikiSC19Dan7Urn2MinON | INT | IOD_STR_disk | I2591 | [8 empty] | 0x03408e8c
STRUrnikiSC19Dan7Urn3MinON | INT | IOD_STR_disk | I2592 | [8 empty] | 0x03408e8d
STRUrnikiSC19Dan7Urn1MinOFF | INT | IOD_STR_disk | I2593 | [8 empty] | 0x03408e8e
STRUrnikiSC19Dan7Urn2MinOFF | INT | IOD_STR_disk | I2594 | [8 empty] | 0x03408e8f
STRUrnikiSC19Dan7Urn3MinOFF | INT | IOD_STR_disk | I2595 | [8 empty] | 0x03408e90
STRUrnikiSC20Dan1Urn1UraON | INT | IOD_STR_disk | I2596 | [8 empty] | 0x03408e91
STRUrnikiSC20Dan1Urn2UraON | INT | IOD_STR_disk | I2597 | [8 empty] | 0x03408e92
STRUrnikiSC20Dan1Urn3UraON | INT | IOD_STR_disk | I2598 | [8 empty] | 0x03408e93
STRUrnikiSC20Dan1Urn1UraOFF | INT | IOD_STR_disk | I2599 | [8 empty] | 0x03408e94
STRUrnikiSC20Dan1Urn2UraOFF | INT | IOD_STR_disk | I2600 | [8 empty] | 0x03408e95
STRUrnikiSC20Dan1Urn3UraOFF | INT | IOD_STR_disk | I2601 | [8 empty] | 0x03408e96
STRUrnikiSC20Dan1Urn1MinON | INT | IOD_STR_disk | I2602 | [8 empty] | 0x03408e97
STRUrnikiSC20Dan1Urn2MinON | INT | IOD_STR_disk | I2603 | [8 empty] | 0x03408e98
STRUrnikiSC20Dan1Urn3MinON | INT | IOD_STR_disk | I2604 | [8 empty] | 0x03408e99
STRUrnikiSC20Dan1Urn1MinOFF | INT | IOD_STR_disk | I2605 | [8 empty] | 0x03408e9a
STRUrnikiSC20Dan1Urn2MinOFF | INT | IOD_STR_disk | I2606 | [8 empty] | 0x03408e9b
STRUrnikiSC20Dan1Urn3MinOFF | INT | IOD_STR_disk | I2607 | [8 empty] | 0x03408e9c
STRUrnikiSC20Dan2Urn1UraON | INT | IOD_STR_disk | I2608 | [8 empty] | 0x03408e9d
STRUrnikiSC20Dan2Urn2UraON | INT | IOD_STR_disk | I2609 | [8 empty] | 0x03408e9e
STRUrnikiSC20Dan2Urn3UraON | INT | IOD_STR_disk | I2610 | [8 empty] | 0x03408e9f
STRUrnikiSC20Dan2Urn1UraOFF | INT | IOD_STR_disk | I2611 | [8 empty] | 0x03408ea0
STRUrnikiSC20Dan2Urn2UraOFF | INT | IOD_STR_disk | I2612 | [8 empty] | 0x03408ea1
STRUrnikiSC20Dan2Urn3UraOFF | INT | IOD_STR_disk | I2613 | [8 empty] | 0x03408ea2
STRUrnikiSC20Dan2Urn1MinON | INT | IOD_STR_disk | I2614 | [8 empty] | 0x03408ea3
STRUrnikiSC20Dan2Urn2MinON | INT | IOD_STR_disk | I2615 | [8 empty] | 0x03408ea4
STRUrnikiSC20Dan2Urn3MinON | INT | IOD_STR_disk | I2616 | [8 empty] | 0x03408ea5
STRUrnikiSC20Dan2Urn1MinOFF | INT | IOD_STR_disk | I2617 | [8 empty] | 0x03408ea6
STRUrnikiSC20Dan2Urn2MinOFF | INT | IOD_STR_disk | I2618 | [8 empty] | 0x03408ea7
STRUrnikiSC20Dan2Urn3MinOFF | INT | IOD_STR_disk | I2619 | [8 empty] | 0x03408ea8
STRUrnikiSC20Dan3Urn1UraON | INT | IOD_STR_disk | I2620 | [8 empty] | 0x03408ea9
STRUrnikiSC20Dan3Urn2UraON | INT | IOD_STR_disk | I2621 | [8 empty] | 0x03408eaa
STRUrnikiSC20Dan3Urn3UraON | INT | IOD_STR_disk | I2622 | [8 empty] | 0x03408eab
STRUrnikiSC20Dan3Urn1UraOFF | INT | IOD_STR_disk | I2623 | [8 empty] | 0x03408eac
STRUrnikiSC20Dan3Urn2UraOFF | INT | IOD_STR_disk | I2624 | [8 empty] | 0x03408ead
STRUrnikiSC20Dan3Urn3UraOFF | INT | IOD_STR_disk | I2625 | [8 empty] | 0x03408eae
STRUrnikiSC20Dan3Urn1MinON | INT | IOD_STR_disk | I2626 | [8 empty] | 0x03408eaf
STRUrnikiSC20Dan3Urn2MinON | INT | IOD_STR_disk | I2627 | [8 empty] | 0x03408eb0
STRUrnikiSC20Dan3Urn3MinON | INT | IOD_STR_disk | I2628 | [8 empty] | 0x03408eb1
STRUrnikiSC20Dan3Urn1MinOFF | INT | IOD_STR_disk | I2629 | [8 empty] | 0x03408eb2
STRUrnikiSC20Dan3Urn2MinOFF | INT | IOD_STR_disk | I2630 | [8 empty] | 0x03408eb3
STRUrnikiSC20Dan3Urn3MinOFF | INT | IOD_STR_disk | I2631 | [8 empty] | 0x03408eb4
STRUrnikiSC20Dan4Urn1UraON | INT | IOD_STR_disk | I2632 | [8 empty] | 0x03408eb5
STRUrnikiSC20Dan4Urn2UraON | INT | IOD_STR_disk | I2633 | [8 empty] | 0x03408eb6
STRUrnikiSC20Dan4Urn3UraON | INT | IOD_STR_disk | I2634 | [8 empty] | 0x03408eb7
STRUrnikiSC20Dan4Urn1UraOFF | INT | IOD_STR_disk | I2635 | [8 empty] | 0x03408eb8
STRUrnikiSC20Dan4Urn2UraOFF | INT | IOD_STR_disk | I2636 | [8 empty] | 0x03408eb9
STRUrnikiSC20Dan4Urn3UraOFF | INT | IOD_STR_disk | I2637 | [8 empty] | 0x03408eba
STRUrnikiSC20Dan4Urn1MinON | INT | IOD_STR_disk | I2638 | [8 empty] | 0x03408ebb
STRUrnikiSC20Dan4Urn2MinON | INT | IOD_STR_disk | I2639 | [8 empty] | 0x03408ebc
STRUrnikiSC20Dan4Urn3MinON | INT | IOD_STR_disk | I2640 | [8 empty] | 0x03408ebd
STRUrnikiSC20Dan4Urn1MinOFF | INT | IOD_STR_disk | I2641 | [8 empty] | 0x03408ebe
STRUrnikiSC20Dan4Urn2MinOFF | INT | IOD_STR_disk | I2642 | [8 empty] | 0x03408ebf
STRUrnikiSC20Dan4Urn3MinOFF | INT | IOD_STR_disk | I2643 | [8 empty] | 0x03408ec0
STRUrnikiSC20Dan5Urn1UraON | INT | IOD_STR_disk | I2644 | [8 empty] | 0x03408ec1
STRUrnikiSC20Dan5Urn2UraON | INT | IOD_STR_disk | I2645 | [8 empty] | 0x03408ec2
STRUrnikiSC20Dan5Urn3UraON | INT | IOD_STR_disk | I2646 | [8 empty] | 0x03408ec3
STRUrnikiSC20Dan5Urn1UraOFF | INT | IOD_STR_disk | I2647 | [8 empty] | 0x03408ec4
STRUrnikiSC20Dan5Urn2UraOFF | INT | IOD_STR_disk | I2648 | [8 empty] | 0x03408ec5
STRUrnikiSC20Dan5Urn3UraOFF | INT | IOD_STR_disk | I2649 | [8 empty] | 0x03408ec6
STRUrnikiSC20Dan5Urn1MinON | INT | IOD_STR_disk | I2650 | [8 empty] | 0x03408ec7
STRUrnikiSC20Dan5Urn2MinON | INT | IOD_STR_disk | I2651 | [8 empty] | 0x03408ec8
STRUrnikiSC20Dan5Urn3MinON | INT | IOD_STR_disk | I2652 | [8 empty] | 0x03408ec9
STRUrnikiSC20Dan5Urn1MinOFF | INT | IOD_STR_disk | I2653 | [8 empty] | 0x03408eca
STRUrnikiSC20Dan5Urn2MinOFF | INT | IOD_STR_disk | I2654 | [8 empty] | 0x03408ecb
STRUrnikiSC20Dan5Urn3MinOFF | INT | IOD_STR_disk | I2655 | [8 empty] | 0x03408ecc
STRUrnikiSC20Dan6Urn1UraON | INT | IOD_STR_disk | I2656 | [8 empty] | 0x03408ecd
STRUrnikiSC20Dan6Urn2UraON | INT | IOD_STR_disk | I2657 | [8 empty] | 0x03408ece
STRUrnikiSC20Dan6Urn3UraON | INT | IOD_STR_disk | I2658 | [8 empty] | 0x03408ecf
STRUrnikiSC20Dan6Urn1UraOFF | INT | IOD_STR_disk | I2659 | [8 empty] | 0x03408ed0
STRUrnikiSC20Dan6Urn2UraOFF | INT | IOD_STR_disk | I2660 | [8 empty] | 0x03408ed1
STRUrnikiSC20Dan6Urn3UraOFF | INT | IOD_STR_disk | I2661 | [8 empty] | 0x03408ed2
STRUrnikiSC20Dan6Urn1MinON | INT | IOD_STR_disk | I2662 | [8 empty] | 0x03408ed3
STRUrnikiSC20Dan6Urn2MinON | INT | IOD_STR_disk | I2663 | [8 empty] | 0x03408ed4
STRUrnikiSC20Dan6Urn3MinON | INT | IOD_STR_disk | I2664 | [8 empty] | 0x03408ed5
STRUrnikiSC20Dan6Urn1MinOFF | INT | IOD_STR_disk | I2665 | [8 empty] | 0x03408ed6
STRUrnikiSC20Dan6Urn2MinOFF | INT | IOD_STR_disk | I2666 | [8 empty] | 0x03408ed7
STRUrnikiSC20Dan6Urn3MinOFF | INT | IOD_STR_disk | I2667 | [8 empty] | 0x03408ed8
STRUrnikiSC20Dan7Urn1UraON | INT | IOD_STR_disk | I2668 | [8 empty] | 0x03408ed9
STRUrnikiSC20Dan7Urn2UraON | INT | IOD_STR_disk | I2669 | [8 empty] | 0x03408eda
STRUrnikiSC20Dan7Urn3UraON | INT | IOD_STR_disk | I2670 | [8 empty] | 0x03408edb
STRUrnikiSC20Dan7Urn1UraOFF | INT | IOD_STR_disk | I2671 | [8 empty] | 0x03408edc
STRUrnikiSC20Dan7Urn2UraOFF | INT | IOD_STR_disk | I2672 | [8 empty] | 0x03408edd
STRUrnikiSC20Dan7Urn3UraOFF | INT | IOD_STR_disk | I2673 | [8 empty] | 0x03408ede
STRUrnikiSC20Dan7Urn1MinON | INT | IOD_STR_disk | I2674 | [8 empty] | 0x03408edf
STRUrnikiSC20Dan7Urn2MinON | INT | IOD_STR_disk | I2675 | [8 empty] | 0x03408ee0
STRUrnikiSC20Dan7Urn3MinON | INT | IOD_STR_disk | I2676 | [8 empty] | 0x03408ee1
STRUrnikiSC20Dan7Urn1MinOFF | INT | IOD_STR_disk | I2677 | [8 empty] | 0x03408ee2
STRUrnikiSC20Dan7Urn2MinOFF | INT | IOD_STR_disk | I2678 | [8 empty] | 0x03408ee3
STRUrnikiSC20Dan7Urn3MinOFF | INT | IOD_STR_disk | I2679 | [8 empty] | 0x03408ee4
STRUrnikiSC21Dan1Urn1UraON | INT | IOD_STR_disk | I2680 | [8 empty] | 0x03408ee5
STRUrnikiSC21Dan1Urn2UraON | INT | IOD_STR_disk | I2681 | [8 empty] | 0x03408ee6
STRUrnikiSC21Dan1Urn3UraON | INT | IOD_STR_disk | I2682 | [8 empty] | 0x03408ee7
STRUrnikiSC21Dan1Urn1UraOFF | INT | IOD_STR_disk | I2683 | [8 empty] | 0x03408ee8
STRUrnikiSC21Dan1Urn2UraOFF | INT | IOD_STR_disk | I2684 | [8 empty] | 0x03408ee9
STRUrnikiSC21Dan1Urn3UraOFF | INT | IOD_STR_disk | I2685 | [8 empty] | 0x03408eea
STRUrnikiSC21Dan1Urn1MinON | INT | IOD_STR_disk | I2686 | [8 empty] | 0x03408eeb
STRUrnikiSC21Dan1Urn2MinON | INT | IOD_STR_disk | I2687 | [8 empty] | 0x03408eec
STRUrnikiSC21Dan1Urn3MinON | INT | IOD_STR_disk | I2688 | [8 empty] | 0x03408eed
STRUrnikiSC21Dan1Urn1MinOFF | INT | IOD_STR_disk | I2689 | [8 empty] | 0x03408eee
STRUrnikiSC21Dan1Urn2MinOFF | INT | IOD_STR_disk | I2690 | [8 empty] | 0x03408eef
STRUrnikiSC21Dan1Urn3MinOFF | INT | IOD_STR_disk | I2691 | [8 empty] | 0x03408ef0
STRUrnikiSC21Dan2Urn1UraON | INT | IOD_STR_disk | I2692 | [8 empty] | 0x03408ef1
STRUrnikiSC21Dan2Urn2UraON | INT | IOD_STR_disk | I2693 | [8 empty] | 0x03408ef2
STRUrnikiSC21Dan2Urn3UraON | INT | IOD_STR_disk | I2694 | [8 empty] | 0x03408ef3
STRUrnikiSC21Dan2Urn1UraOFF | INT | IOD_STR_disk | I2695 | [8 empty] | 0x03408ef4
STRUrnikiSC21Dan2Urn2UraOFF | INT | IOD_STR_disk | I2696 | [8 empty] | 0x03408ef5
STRUrnikiSC21Dan2Urn3UraOFF | INT | IOD_STR_disk | I2697 | [8 empty] | 0x03408ef6
STRUrnikiSC21Dan2Urn1MinON | INT | IOD_STR_disk | I2698 | [8 empty] | 0x03408ef7
STRUrnikiSC21Dan2Urn2MinON | INT | IOD_STR_disk | I2699 | [8 empty] | 0x03408ef8
STRUrnikiSC21Dan2Urn3MinON | INT | IOD_STR_disk | I2700 | [8 empty] | 0x03408ef9
STRUrnikiSC21Dan2Urn1MinOFF | INT | IOD_STR_disk | I2701 | [8 empty] | 0x03408efa
STRUrnikiSC21Dan2Urn2MinOFF | INT | IOD_STR_disk | I2702 | [8 empty] | 0x03408efb
STRUrnikiSC21Dan2Urn3MinOFF | INT | IOD_STR_disk | I2703 | [8 empty] | 0x03408efc
STRUrnikiSC21Dan3Urn1UraON | INT | IOD_STR_disk | I2704 | [8 empty] | 0x03408efd
STRUrnikiSC21Dan3Urn2UraON | INT | IOD_STR_disk | I2705 | [8 empty] | 0x03408efe
STRUrnikiSC21Dan3Urn3UraON | INT | IOD_STR_disk | I2706 | [8 empty] | 0x03408eff
STRUrnikiSC21Dan3Urn1UraOFF | INT | IOD_STR_disk | I2707 | [8 empty] | 0x03408f00
STRUrnikiSC21Dan3Urn2UraOFF | INT | IOD_STR_disk | I2708 | [8 empty] | 0x03408f01
STRUrnikiSC21Dan3Urn3UraOFF | INT | IOD_STR_disk | I2709 | [8 empty] | 0x03408f02
STRUrnikiSC21Dan3Urn1MinON | INT | IOD_STR_disk | I2710 | [8 empty] | 0x03408f03
STRUrnikiSC21Dan3Urn2MinON | INT | IOD_STR_disk | I2711 | [8 empty] | 0x03408f04
STRUrnikiSC21Dan3Urn3MinON | INT | IOD_STR_disk | I2712 | [8 empty] | 0x03408f05
STRUrnikiSC21Dan3Urn1MinOFF | INT | IOD_STR_disk | I2713 | [8 empty] | 0x03408f06
STRUrnikiSC21Dan3Urn2MinOFF | INT | IOD_STR_disk | I2714 | [8 empty] | 0x03408f07
STRUrnikiSC21Dan3Urn3MinOFF | INT | IOD_STR_disk | I2715 | [8 empty] | 0x03408f08
STRUrnikiSC21Dan4Urn1UraON | INT | IOD_STR_disk | I2716 | [8 empty] | 0x03408f09
STRUrnikiSC21Dan4Urn2UraON | INT | IOD_STR_disk | I2717 | [8 empty] | 0x03408f0a
STRUrnikiSC21Dan4Urn3UraON | INT | IOD_STR_disk | I2718 | [8 empty] | 0x03408f0b
STRUrnikiSC21Dan4Urn1UraOFF | INT | IOD_STR_disk | I2719 | [8 empty] | 0x03408f0c
STRUrnikiSC21Dan4Urn2UraOFF | INT | IOD_STR_disk | I2720 | [8 empty] | 0x03408f0d
STRUrnikiSC21Dan4Urn3UraOFF | INT | IOD_STR_disk | I2721 | [8 empty] | 0x03408f0e
STRUrnikiSC21Dan4Urn1MinON | INT | IOD_STR_disk | I2722 | [8 empty] | 0x03408f0f
STRUrnikiSC21Dan4Urn2MinON | INT | IOD_STR_disk | I2723 | [8 empty] | 0x03408f10
STRUrnikiSC21Dan4Urn3MinON | INT | IOD_STR_disk | I2724 | [8 empty] | 0x03408f11
STRUrnikiSC21Dan4Urn1MinOFF | INT | IOD_STR_disk | I2725 | [8 empty] | 0x03408f12
STRUrnikiSC21Dan4Urn2MinOFF | INT | IOD_STR_disk | I2726 | [8 empty] | 0x03408f13
STRUrnikiSC21Dan4Urn3MinOFF | INT | IOD_STR_disk | I2727 | [8 empty] | 0x03408f14
STRUrnikiSC21Dan5Urn1UraON | INT | IOD_STR_disk | I2728 | [8 empty] | 0x03408f15
STRUrnikiSC21Dan5Urn2UraON | INT | IOD_STR_disk | I2729 | [8 empty] | 0x03408f16
STRUrnikiSC21Dan5Urn3UraON | INT | IOD_STR_disk | I2730 | [8 empty] | 0x03408f17
STRUrnikiSC21Dan5Urn1UraOFF | INT | IOD_STR_disk | I2731 | [8 empty] | 0x03408f18
STRUrnikiSC21Dan5Urn2UraOFF | INT | IOD_STR_disk | I2732 | [8 empty] | 0x03408f19
STRUrnikiSC21Dan5Urn3UraOFF | INT | IOD_STR_disk | I2733 | [8 empty] | 0x03408f1a
STRUrnikiSC21Dan5Urn1MinON | INT | IOD_STR_disk | I2734 | [8 empty] | 0x03408f1b
STRUrnikiSC21Dan5Urn2MinON | INT | IOD_STR_disk | I2735 | [8 empty] | 0x03408f1c
STRUrnikiSC21Dan5Urn3MinON | INT | IOD_STR_disk | I2736 | [8 empty] | 0x03408f1d
STRUrnikiSC21Dan5Urn1MinOFF | INT | IOD_STR_disk | I2737 | [8 empty] | 0x03408f1e
STRUrnikiSC21Dan5Urn2MinOFF | INT | IOD_STR_disk | I2738 | [8 empty] | 0x03408f1f
STRUrnikiSC21Dan5Urn3MinOFF | INT | IOD_STR_disk | I2739 | [8 empty] | 0x03408f20
STRUrnikiSC21Dan6Urn1UraON | INT | IOD_STR_disk | I2740 | [8 empty] | 0x03408f21
STRUrnikiSC21Dan6Urn2UraON | INT | IOD_STR_disk | I2741 | [8 empty] | 0x03408f22
STRUrnikiSC21Dan6Urn3UraON | INT | IOD_STR_disk | I2742 | [8 empty] | 0x03408f23
STRUrnikiSC21Dan6Urn1UraOFF | INT | IOD_STR_disk | I2743 | [8 empty] | 0x03408f24
STRUrnikiSC21Dan6Urn2UraOFF | INT | IOD_STR_disk | I2744 | [8 empty] | 0x03408f25
STRUrnikiSC21Dan6Urn3UraOFF | INT | IOD_STR_disk | I2745 | [8 empty] | 0x03408f26
STRUrnikiSC21Dan6Urn1MinON | INT | IOD_STR_disk | I2746 | [8 empty] | 0x03408f27
STRUrnikiSC21Dan6Urn2MinON | INT | IOD_STR_disk | I2747 | [8 empty] | 0x03408f28
STRUrnikiSC21Dan6Urn3MinON | INT | IOD_STR_disk | I2748 | [8 empty] | 0x03408f29
STRUrnikiSC21Dan6Urn1MinOFF | INT | IOD_STR_disk | I2749 | [8 empty] | 0x03408f2a
STRUrnikiSC21Dan6Urn2MinOFF | INT | IOD_STR_disk | I2750 | [8 empty] | 0x03408f2b
STRUrnikiSC21Dan6Urn3MinOFF | INT | IOD_STR_disk | I2751 | [8 empty] | 0x03408f2c
STRUrnikiSC21Dan7Urn1UraON | INT | IOD_STR_disk | I2752 | [8 empty] | 0x03408f2d
STRUrnikiSC21Dan7Urn2UraON | INT | IOD_STR_disk | I2753 | [8 empty] | 0x03408f2e
STRUrnikiSC21Dan7Urn3UraON | INT | IOD_STR_disk | I2754 | [8 empty] | 0x03408f2f
STRUrnikiSC21Dan7Urn1UraOFF | INT | IOD_STR_disk | I2755 | [8 empty] | 0x03408f30
STRUrnikiSC21Dan7Urn2UraOFF | INT | IOD_STR_disk | I2756 | [8 empty] | 0x03408f31
STRUrnikiSC21Dan7Urn3UraOFF | INT | IOD_STR_disk | I2757 | [8 empty] | 0x03408f32
STRUrnikiSC21Dan7Urn1MinON | INT | IOD_STR_disk | I2758 | [8 empty] | 0x03408f33
STRUrnikiSC21Dan7Urn2MinON | INT | IOD_STR_disk | I2759 | [8 empty] | 0x03408f34
STRUrnikiSC21Dan7Urn3MinON | INT | IOD_STR_disk | I2760 | [8 empty] | 0x03408f35
STRUrnikiSC21Dan7Urn1MinOFF | INT | IOD_STR_disk | I2761 | [8 empty] | 0x03408f36
STRUrnikiSC21Dan7Urn2MinOFF | INT | IOD_STR_disk | I2762 | [8 empty] | 0x03408f37
STRUrnikiSC21Dan7Urn3MinOFF | INT | IOD_STR_disk | I2763 | [8 empty] | 0x03408f38
STRUrnikiSC22Dan1Urn1UraON | INT | IOD_STR_disk | I2764 | [8 empty] | 0x03408f39
STRUrnikiSC22Dan1Urn2UraON | INT | IOD_STR_disk | I2765 | [8 empty] | 0x03408f3a
STRUrnikiSC22Dan1Urn3UraON | INT | IOD_STR_disk | I2766 | [8 empty] | 0x03408f3b
STRUrnikiSC22Dan1Urn1UraOFF | INT | IOD_STR_disk | I2767 | [8 empty] | 0x03408f3c
STRUrnikiSC22Dan1Urn2UraOFF | INT | IOD_STR_disk | I2768 | [8 empty] | 0x03408f3d
STRUrnikiSC22Dan1Urn3UraOFF | INT | IOD_STR_disk | I2769 | [8 empty] | 0x03408f3e
STRUrnikiSC22Dan1Urn1MinON | INT | IOD_STR_disk | I2770 | [8 empty] | 0x03408f3f
STRUrnikiSC22Dan1Urn2MinON | INT | IOD_STR_disk | I2771 | [8 empty] | 0x03408f40
STRUrnikiSC22Dan1Urn3MinON | INT | IOD_STR_disk | I2772 | [8 empty] | 0x03408f41
STRUrnikiSC22Dan1Urn1MinOFF | INT | IOD_STR_disk | I2773 | [8 empty] | 0x03408f42
STRUrnikiSC22Dan1Urn2MinOFF | INT | IOD_STR_disk | I2774 | [8 empty] | 0x03408f43
STRUrnikiSC22Dan1Urn3MinOFF | INT | IOD_STR_disk | I2775 | [8 empty] | 0x03408f44
STRUrnikiSC22Dan2Urn1UraON | INT | IOD_STR_disk | I2776 | [8 empty] | 0x03408f45
STRUrnikiSC22Dan2Urn2UraON | INT | IOD_STR_disk | I2777 | [8 empty] | 0x03408f46
STRUrnikiSC22Dan2Urn3UraON | INT | IOD_STR_disk | I2778 | [8 empty] | 0x03408f47
STRUrnikiSC22Dan2Urn1UraOFF | INT | IOD_STR_disk | I2779 | [8 empty] | 0x03408f48
STRUrnikiSC22Dan2Urn2UraOFF | INT | IOD_STR_disk | I2780 | [8 empty] | 0x03408f49
STRUrnikiSC22Dan2Urn3UraOFF | INT | IOD_STR_disk | I2781 | [8 empty] | 0x03408f4a
STRUrnikiSC22Dan2Urn1MinON | INT | IOD_STR_disk | I2782 | [8 empty] | 0x03408f4b
STRUrnikiSC22Dan2Urn2MinON | INT | IOD_STR_disk | I2783 | [8 empty] | 0x03408f4c
STRUrnikiSC22Dan2Urn3MinON | INT | IOD_STR_disk | I2784 | [8 empty] | 0x03408f4d
STRUrnikiSC22Dan2Urn1MinOFF | INT | IOD_STR_disk | I2785 | [8 empty] | 0x03408f4e
STRUrnikiSC22Dan2Urn2MinOFF | INT | IOD_STR_disk | I2786 | [8 empty] | 0x03408f4f
STRUrnikiSC22Dan2Urn3MinOFF | INT | IOD_STR_disk | I2787 | [8 empty] | 0x03408f50
STRUrnikiSC22Dan3Urn1UraON | INT | IOD_STR_disk | I2788 | [8 empty] | 0x03408f51
STRUrnikiSC22Dan3Urn2UraON | INT | IOD_STR_disk | I2789 | [8 empty] | 0x03408f52
STRUrnikiSC22Dan3Urn3UraON | INT | IOD_STR_disk | I2790 | [8 empty] | 0x03408f53
STRUrnikiSC22Dan3Urn1UraOFF | INT | IOD_STR_disk | I2791 | [8 empty] | 0x03408f54
STRUrnikiSC22Dan3Urn2UraOFF | INT | IOD_STR_disk | I2792 | [8 empty] | 0x03408f55
STRUrnikiSC22Dan3Urn3UraOFF | INT | IOD_STR_disk | I2793 | [8 empty] | 0x03408f56
STRUrnikiSC22Dan3Urn1MinON | INT | IOD_STR_disk | I2794 | [8 empty] | 0x03408f57
STRUrnikiSC22Dan3Urn2MinON | INT | IOD_STR_disk | I2795 | [8 empty] | 0x03408f58
STRUrnikiSC22Dan3Urn3MinON | INT | IOD_STR_disk | I2796 | [8 empty] | 0x03408f59
STRUrnikiSC22Dan3Urn1MinOFF | INT | IOD_STR_disk | I2797 | [8 empty] | 0x03408f5a
STRUrnikiSC22Dan3Urn2MinOFF | INT | IOD_STR_disk | I2798 | [8 empty] | 0x03408f5b
STRUrnikiSC22Dan3Urn3MinOFF | INT | IOD_STR_disk | I2799 | [8 empty] | 0x03408f5c
STRUrnikiSC22Dan4Urn1UraON | INT | IOD_STR_disk | I2800 | [8 empty] | 0x03408f5d
STRUrnikiSC22Dan4Urn2UraON | INT | IOD_STR_disk | I2801 | [8 empty] | 0x03408f5e
STRUrnikiSC22Dan4Urn3UraON | INT | IOD_STR_disk | I2802 | [8 empty] | 0x03408f5f
STRUrnikiSC22Dan4Urn1UraOFF | INT | IOD_STR_disk | I2803 | [8 empty] | 0x03408f60
STRUrnikiSC22Dan4Urn2UraOFF | INT | IOD_STR_disk | I2804 | [8 empty] | 0x03408f61
STRUrnikiSC22Dan4Urn3UraOFF | INT | IOD_STR_disk | I2805 | [8 empty] | 0x03408f62
STRUrnikiSC22Dan4Urn1MinON | INT | IOD_STR_disk | I2806 | [8 empty] | 0x03408f63
STRUrnikiSC22Dan4Urn2MinON | INT | IOD_STR_disk | I2807 | [8 empty] | 0x03408f64
STRUrnikiSC22Dan4Urn3MinON | INT | IOD_STR_disk | I2808 | [8 empty] | 0x03408f65
STRUrnikiSC22Dan4Urn1MinOFF | INT | IOD_STR_disk | I2809 | [8 empty] | 0x03408f66
STRUrnikiSC22Dan4Urn2MinOFF | INT | IOD_STR_disk | I2810 | [8 empty] | 0x03408f67
STRUrnikiSC22Dan4Urn3MinOFF | INT | IOD_STR_disk | I2811 | [8 empty] | 0x03408f68
STRUrnikiSC22Dan5Urn1UraON | INT | IOD_STR_disk | I2812 | [8 empty] | 0x03408f69
STRUrnikiSC22Dan5Urn2UraON | INT | IOD_STR_disk | I2813 | [8 empty] | 0x03408f6a
STRUrnikiSC22Dan5Urn3UraON | INT | IOD_STR_disk | I2814 | [8 empty] | 0x03408f6b
STRUrnikiSC22Dan5Urn1UraOFF | INT | IOD_STR_disk | I2815 | [8 empty] | 0x03408f6c
STRUrnikiSC22Dan5Urn2UraOFF | INT | IOD_STR_disk | I2816 | [8 empty] | 0x03408f6d
STRUrnikiSC22Dan5Urn3UraOFF | INT | IOD_STR_disk | I2817 | [8 empty] | 0x03408f6e
STRUrnikiSC22Dan5Urn1MinON | INT | IOD_STR_disk | I2818 | [8 empty] | 0x03408f6f
STRUrnikiSC22Dan5Urn2MinON | INT | IOD_STR_disk | I2819 | [8 empty] | 0x03408f70
STRUrnikiSC22Dan5Urn3MinON | INT | IOD_STR_disk | I2820 | [8 empty] | 0x03408f71
STRUrnikiSC22Dan5Urn1MinOFF | INT | IOD_STR_disk | I2821 | [8 empty] | 0x03408f72
STRUrnikiSC22Dan5Urn2MinOFF | INT | IOD_STR_disk | I2822 | [8 empty] | 0x03408f73
STRUrnikiSC22Dan5Urn3MinOFF | INT | IOD_STR_disk | I2823 | [8 empty] | 0x03408f74
STRUrnikiSC22Dan6Urn1UraON | INT | IOD_STR_disk | I2824 | [8 empty] | 0x03408f75
STRUrnikiSC22Dan6Urn2UraON | INT | IOD_STR_disk | I2825 | [8 empty] | 0x03408f76
STRUrnikiSC22Dan6Urn3UraON | INT | IOD_STR_disk | I2826 | [8 empty] | 0x03408f77
STRUrnikiSC22Dan6Urn1UraOFF | INT | IOD_STR_disk | I2827 | [8 empty] | 0x03408f78
STRUrnikiSC22Dan6Urn2UraOFF | INT | IOD_STR_disk | I2828 | [8 empty] | 0x03408f79
STRUrnikiSC22Dan6Urn3UraOFF | INT | IOD_STR_disk | I2829 | [8 empty] | 0x03408f7a
STRUrnikiSC22Dan6Urn1MinON | INT | IOD_STR_disk | I2830 | [8 empty] | 0x03408f7b
STRUrnikiSC22Dan6Urn2MinON | INT | IOD_STR_disk | I2831 | [8 empty] | 0x03408f7c
STRUrnikiSC22Dan6Urn3MinON | INT | IOD_STR_disk | I2832 | [8 empty] | 0x03408f7d
STRUrnikiSC22Dan6Urn1MinOFF | INT | IOD_STR_disk | I2833 | [8 empty] | 0x03408f7e
STRUrnikiSC22Dan6Urn2MinOFF | INT | IOD_STR_disk | I2834 | [8 empty] | 0x03408f7f
STRUrnikiSC22Dan6Urn3MinOFF | INT | IOD_STR_disk | I2835 | [8 empty] | 0x03408f80
STRUrnikiSC22Dan7Urn1UraON | INT | IOD_STR_disk | I2836 | [8 empty] | 0x03408f81
STRUrnikiSC22Dan7Urn2UraON | INT | IOD_STR_disk | I2837 | [8 empty] | 0x03408f82
STRUrnikiSC22Dan7Urn3UraON | INT | IOD_STR_disk | I2838 | [8 empty] | 0x03408f83
STRUrnikiSC22Dan7Urn1UraOFF | INT | IOD_STR_disk | I2839 | [8 empty] | 0x03408f84
STRUrnikiSC22Dan7Urn2UraOFF | INT | IOD_STR_disk | I2840 | [8 empty] | 0x03408f85
STRUrnikiSC22Dan7Urn3UraOFF | INT | IOD_STR_disk | I2841 | [8 empty] | 0x03408f86
STRUrnikiSC22Dan7Urn1MinON | INT | IOD_STR_disk | I2842 | [8 empty] | 0x03408f87
STRUrnikiSC22Dan7Urn2MinON | INT | IOD_STR_disk | I2843 | [8 empty] | 0x03408f88
STRUrnikiSC22Dan7Urn3MinON | INT | IOD_STR_disk | I2844 | [8 empty] | 0x03408f89
STRUrnikiSC22Dan7Urn1MinOFF | INT | IOD_STR_disk | I2845 | [8 empty] | 0x03408f8a
STRUrnikiSC22Dan7Urn2MinOFF | INT | IOD_STR_disk | I2846 | [8 empty] | 0x03408f8b
STRUrnikiSC22Dan7Urn3MinOFF | INT | IOD_STR_disk | I2847 | [8 empty] | 0x03408f8c
STRUrnikiSC23Dan1Urn1UraON | INT | IOD_STR_disk | I2848 | [8 empty] | 0x03408f8d
STRUrnikiSC23Dan1Urn2UraON | INT | IOD_STR_disk | I2849 | [8 empty] | 0x03408f8e
STRUrnikiSC23Dan1Urn3UraON | INT | IOD_STR_disk | I2850 | [8 empty] | 0x03408f8f
STRUrnikiSC23Dan1Urn1UraOFF | INT | IOD_STR_disk | I2851 | [8 empty] | 0x03408f90
STRUrnikiSC23Dan1Urn2UraOFF | INT | IOD_STR_disk | I2852 | [8 empty] | 0x03408f91
STRUrnikiSC23Dan1Urn3UraOFF | INT | IOD_STR_disk | I2853 | [8 empty] | 0x03408f92
STRUrnikiSC23Dan1Urn1MinON | INT | IOD_STR_disk | I2854 | [8 empty] | 0x03408f93
STRUrnikiSC23Dan1Urn2MinON | INT | IOD_STR_disk | I2855 | [8 empty] | 0x03408f94
STRUrnikiSC23Dan1Urn3MinON | INT | IOD_STR_disk | I2856 | [8 empty] | 0x03408f95
STRUrnikiSC23Dan1Urn1MinOFF | INT | IOD_STR_disk | I2857 | [8 empty] | 0x03408f96
STRUrnikiSC23Dan1Urn2MinOFF | INT | IOD_STR_disk | I2858 | [8 empty] | 0x03408f97
STRUrnikiSC23Dan1Urn3MinOFF | INT | IOD_STR_disk | I2859 | [8 empty] | 0x03408f98
STRUrnikiSC23Dan2Urn1UraON | INT | IOD_STR_disk | I2860 | [8 empty] | 0x03408f99
STRUrnikiSC23Dan2Urn2UraON | INT | IOD_STR_disk | I2861 | [8 empty] | 0x03408f9a
STRUrnikiSC23Dan2Urn3UraON | INT | IOD_STR_disk | I2862 | [8 empty] | 0x03408f9b
STRUrnikiSC23Dan2Urn1UraOFF | INT | IOD_STR_disk | I2863 | [8 empty] | 0x03408f9c
STRUrnikiSC23Dan2Urn2UraOFF | INT | IOD_STR_disk | I2864 | [8 empty] | 0x03408f9d
STRUrnikiSC23Dan2Urn3UraOFF | INT | IOD_STR_disk | I2865 | [8 empty] | 0x03408f9e
STRUrnikiSC23Dan2Urn1MinON | INT | IOD_STR_disk | I2866 | [8 empty] | 0x03408f9f
STRUrnikiSC23Dan2Urn2MinON | INT | IOD_STR_disk | I2867 | [8 empty] | 0x03408fa0
STRUrnikiSC23Dan2Urn3MinON | INT | IOD_STR_disk | I2868 | [8 empty] | 0x03408fa1
STRUrnikiSC23Dan2Urn1MinOFF | INT | IOD_STR_disk | I2869 | [8 empty] | 0x03408fa2
STRUrnikiSC23Dan2Urn2MinOFF | INT | IOD_STR_disk | I2870 | [8 empty] | 0x03408fa3
STRUrnikiSC23Dan2Urn3MinOFF | INT | IOD_STR_disk | I2871 | [8 empty] | 0x03408fa4
STRUrnikiSC23Dan3Urn1UraON | INT | IOD_STR_disk | I2872 | [8 empty] | 0x03408fa5
STRUrnikiSC23Dan3Urn2UraON | INT | IOD_STR_disk | I2873 | [8 empty] | 0x03408fa6
STRUrnikiSC23Dan3Urn3UraON | INT | IOD_STR_disk | I2874 | [8 empty] | 0x03408fa7
STRUrnikiSC23Dan3Urn1UraOFF | INT | IOD_STR_disk | I2875 | [8 empty] | 0x03408fa8
STRUrnikiSC23Dan3Urn2UraOFF | INT | IOD_STR_disk | I2876 | [8 empty] | 0x03408fa9
STRUrnikiSC23Dan3Urn3UraOFF | INT | IOD_STR_disk | I2877 | [8 empty] | 0x03408faa
STRUrnikiSC23Dan3Urn1MinON | INT | IOD_STR_disk | I2878 | [8 empty] | 0x03408fab
STRUrnikiSC23Dan3Urn2MinON | INT | IOD_STR_disk | I2879 | [8 empty] | 0x03408fac
STRUrnikiSC23Dan3Urn3MinON | INT | IOD_STR_disk | I2880 | [8 empty] | 0x03408fad
STRUrnikiSC23Dan3Urn1MinOFF | INT | IOD_STR_disk | I2881 | [8 empty] | 0x03408fae
STRUrnikiSC23Dan3Urn2MinOFF | INT | IOD_STR_disk | I2882 | [8 empty] | 0x03408faf
STRUrnikiSC23Dan3Urn3MinOFF | INT | IOD_STR_disk | I2883 | [8 empty] | 0x03408fb0
STRUrnikiSC23Dan4Urn1UraON | INT | IOD_STR_disk | I2884 | [8 empty] | 0x03408fb1
STRUrnikiSC23Dan4Urn2UraON | INT | IOD_STR_disk | I2885 | [8 empty] | 0x03408fb2
STRUrnikiSC23Dan4Urn3UraON | INT | IOD_STR_disk | I2886 | [8 empty] | 0x03408fb3
STRUrnikiSC23Dan4Urn1UraOFF | INT | IOD_STR_disk | I2887 | [8 empty] | 0x03408fb4
STRUrnikiSC23Dan4Urn2UraOFF | INT | IOD_STR_disk | I2888 | [8 empty] | 0x03408fb5
STRUrnikiSC23Dan4Urn3UraOFF | INT | IOD_STR_disk | I2889 | [8 empty] | 0x03408fb6
STRUrnikiSC23Dan4Urn1MinON | INT | IOD_STR_disk | I2890 | [8 empty] | 0x03408fb7
STRUrnikiSC23Dan4Urn2MinON | INT | IOD_STR_disk | I2891 | [8 empty] | 0x03408fb8
STRUrnikiSC23Dan4Urn3MinON | INT | IOD_STR_disk | I2892 | [8 empty] | 0x03408fb9
STRUrnikiSC23Dan4Urn1MinOFF | INT | IOD_STR_disk | I2893 | [8 empty] | 0x03408fba
STRUrnikiSC23Dan4Urn2MinOFF | INT | IOD_STR_disk | I2894 | [8 empty] | 0x03408fbb
STRUrnikiSC23Dan4Urn3MinOFF | INT | IOD_STR_disk | I2895 | [8 empty] | 0x03408fbc
STRUrnikiSC23Dan5Urn1UraON | INT | IOD_STR_disk | I2896 | [8 empty] | 0x03408fbd
STRUrnikiSC23Dan5Urn2UraON | INT | IOD_STR_disk | I2897 | [8 empty] | 0x03408fbe
STRUrnikiSC23Dan5Urn3UraON | INT | IOD_STR_disk | I2898 | [8 empty] | 0x03408fbf
STRUrnikiSC23Dan5Urn1UraOFF | INT | IOD_STR_disk | I2899 | [8 empty] | 0x03408fc0
STRUrnikiSC23Dan5Urn2UraOFF | INT | IOD_STR_disk | I2900 | [8 empty] | 0x03408fc1
STRUrnikiSC23Dan5Urn3UraOFF | INT | IOD_STR_disk | I2901 | [8 empty] | 0x03408fc2
STRUrnikiSC23Dan5Urn1MinON | INT | IOD_STR_disk | I2902 | [8 empty] | 0x03408fc3
STRUrnikiSC23Dan5Urn2MinON | INT | IOD_STR_disk | I2903 | [8 empty] | 0x03408fc4
STRUrnikiSC23Dan5Urn3MinON | INT | IOD_STR_disk | I2904 | [8 empty] | 0x03408fc5
STRUrnikiSC23Dan5Urn1MinOFF | INT | IOD_STR_disk | I2905 | [8 empty] | 0x03408fc6
STRUrnikiSC23Dan5Urn2MinOFF | INT | IOD_STR_disk | I2906 | [8 empty] | 0x03408fc7
STRUrnikiSC23Dan5Urn3MinOFF | INT | IOD_STR_disk | I2907 | [8 empty] | 0x03408fc8
STRUrnikiSC23Dan6Urn1UraON | INT | IOD_STR_disk | I2908 | [8 empty] | 0x03408fc9
STRUrnikiSC23Dan6Urn2UraON | INT | IOD_STR_disk | I2909 | [8 empty] | 0x03408fca
STRUrnikiSC23Dan6Urn3UraON | INT | IOD_STR_disk | I2910 | [8 empty] | 0x03408fcb
STRUrnikiSC23Dan6Urn1UraOFF | INT | IOD_STR_disk | I2911 | [8 empty] | 0x03408fcc
STRUrnikiSC23Dan6Urn2UraOFF | INT | IOD_STR_disk | I2912 | [8 empty] | 0x03408fcd
STRUrnikiSC23Dan6Urn3UraOFF | INT | IOD_STR_disk | I2913 | [8 empty] | 0x03408fce
STRUrnikiSC23Dan6Urn1MinON | INT | IOD_STR_disk | I2914 | [8 empty] | 0x03408fcf
STRUrnikiSC23Dan6Urn2MinON | INT | IOD_STR_disk | I2915 | [8 empty] | 0x03408fd0
STRUrnikiSC23Dan6Urn3MinON | INT | IOD_STR_disk | I2916 | [8 empty] | 0x03408fd1
STRUrnikiSC23Dan6Urn1MinOFF | INT | IOD_STR_disk | I2917 | [8 empty] | 0x03408fd2
STRUrnikiSC23Dan6Urn2MinOFF | INT | IOD_STR_disk | I2918 | [8 empty] | 0x03408fd3
STRUrnikiSC23Dan6Urn3MinOFF | INT | IOD_STR_disk | I2919 | [8 empty] | 0x03408fd4
STRUrnikiSC23Dan7Urn1UraON | INT | IOD_STR_disk | I2920 | [8 empty] | 0x03408fd5
STRUrnikiSC23Dan7Urn2UraON | INT | IOD_STR_disk | I2921 | [8 empty] | 0x03408fd6
STRUrnikiSC23Dan7Urn3UraON | INT | IOD_STR_disk | I2922 | [8 empty] | 0x03408fd7
STRUrnikiSC23Dan7Urn1UraOFF | INT | IOD_STR_disk | I2923 | [8 empty] | 0x03408fd8
STRUrnikiSC23Dan7Urn2UraOFF | INT | IOD_STR_disk | I2924 | [8 empty] | 0x03408fd9
STRUrnikiSC23Dan7Urn3UraOFF | INT | IOD_STR_disk | I2925 | [8 empty] | 0x03408fda
STRUrnikiSC23Dan7Urn1MinON | INT | IOD_STR_disk | I2926 | [8 empty] | 0x03408fdb
STRUrnikiSC23Dan7Urn2MinON | INT | IOD_STR_disk | I2927 | [8 empty] | 0x03408fdc
STRUrnikiSC23Dan7Urn3MinON | INT | IOD_STR_disk | I2928 | [8 empty] | 0x03408fdd
STRUrnikiSC23Dan7Urn1MinOFF | INT | IOD_STR_disk | I2929 | [8 empty] | 0x03408fde
STRUrnikiSC23Dan7Urn2MinOFF | INT | IOD_STR_disk | I2930 | [8 empty] | 0x03408fdf
STRUrnikiSC23Dan7Urn3MinOFF | INT | IOD_STR_disk | I2931 | [8 empty] | 0x03408fe0
STRUrnikiSC24Dan1Urn1UraON | INT | IOD_STR_disk | I2932 | [8 empty] | 0x03408fe1
STRUrnikiSC24Dan1Urn2UraON | INT | IOD_STR_disk | I2933 | [8 empty] | 0x03408fe2
STRUrnikiSC24Dan1Urn3UraON | INT | IOD_STR_disk | I2934 | [8 empty] | 0x03408fe3
STRUrnikiSC24Dan1Urn1UraOFF | INT | IOD_STR_disk | I2935 | [8 empty] | 0x03408fe4
STRUrnikiSC24Dan1Urn2UraOFF | INT | IOD_STR_disk | I2936 | [8 empty] | 0x03408fe5
STRUrnikiSC24Dan1Urn3UraOFF | INT | IOD_STR_disk | I2937 | [8 empty] | 0x03408fe6
STRUrnikiSC24Dan1Urn1MinON | INT | IOD_STR_disk | I2938 | [8 empty] | 0x03408fe7
STRUrnikiSC24Dan1Urn2MinON | INT | IOD_STR_disk | I2939 | [8 empty] | 0x03408fe8
STRUrnikiSC24Dan1Urn3MinON | INT | IOD_STR_disk | I2940 | [8 empty] | 0x03408fe9
STRUrnikiSC24Dan1Urn1MinOFF | INT | IOD_STR_disk | I2941 | [8 empty] | 0x03408fea
STRUrnikiSC24Dan1Urn2MinOFF | INT | IOD_STR_disk | I2942 | [8 empty] | 0x03408feb
STRUrnikiSC24Dan1Urn3MinOFF | INT | IOD_STR_disk | I2943 | [8 empty] | 0x03408fec
STRUrnikiSC24Dan2Urn1UraON | INT | IOD_STR_disk | I2944 | [8 empty] | 0x03408fed
STRUrnikiSC24Dan2Urn2UraON | INT | IOD_STR_disk | I2945 | [8 empty] | 0x03408fee
STRUrnikiSC24Dan2Urn3UraON | INT | IOD_STR_disk | I2946 | [8 empty] | 0x03408fef
STRUrnikiSC24Dan2Urn1UraOFF | INT | IOD_STR_disk | I2947 | [8 empty] | 0x03408ff0
STRUrnikiSC24Dan2Urn2UraOFF | INT | IOD_STR_disk | I2948 | [8 empty] | 0x03408ff1
STRUrnikiSC24Dan2Urn3UraOFF | INT | IOD_STR_disk | I2949 | [8 empty] | 0x03408ff2
STRUrnikiSC24Dan2Urn1MinON | INT | IOD_STR_disk | I2950 | [8 empty] | 0x03408ff3
STRUrnikiSC24Dan2Urn2MinON | INT | IOD_STR_disk | I2951 | [8 empty] | 0x03408ff4
STRUrnikiSC24Dan2Urn3MinON | INT | IOD_STR_disk | I2952 | [8 empty] | 0x03408ff5
STRUrnikiSC24Dan2Urn1MinOFF | INT | IOD_STR_disk | I2953 | [8 empty] | 0x03408ff6
STRUrnikiSC24Dan2Urn2MinOFF | INT | IOD_STR_disk | I2954 | [8 empty] | 0x03408ff7
STRUrnikiSC24Dan2Urn3MinOFF | INT | IOD_STR_disk | I2955 | [8 empty] | 0x03408ff8
STRUrnikiSC24Dan3Urn1UraON | INT | IOD_STR_disk | I2956 | [8 empty] | 0x03408ff9
STRUrnikiSC24Dan3Urn2UraON | INT | IOD_STR_disk | I2957 | [8 empty] | 0x03408ffa
STRUrnikiSC24Dan3Urn3UraON | INT | IOD_STR_disk | I2958 | [8 empty] | 0x03408ffb
STRUrnikiSC24Dan3Urn1UraOFF | INT | IOD_STR_disk | I2959 | [8 empty] | 0x03408ffc
STRUrnikiSC24Dan3Urn2UraOFF | INT | IOD_STR_disk | I2960 | [8 empty] | 0x03408ffd
STRUrnikiSC24Dan3Urn3UraOFF | INT | IOD_STR_disk | I2961 | [8 empty] | 0x03408ffe
STRUrnikiSC24Dan3Urn1MinON | INT | IOD_STR_disk | I2962 | [8 empty] | 0x03408fff
STRUrnikiSC24Dan3Urn2MinON | INT | IOD_STR_disk | I2963 | [8 empty] | 0x03409000
STRUrnikiSC24Dan3Urn3MinON | INT | IOD_STR_disk | I2964 | [8 empty] | 0x03409001
STRUrnikiSC24Dan3Urn1MinOFF | INT | IOD_STR_disk | I2965 | [8 empty] | 0x03409002
STRUrnikiSC24Dan3Urn2MinOFF | INT | IOD_STR_disk | I2966 | [8 empty] | 0x03409003
STRUrnikiSC24Dan3Urn3MinOFF | INT | IOD_STR_disk | I2967 | [8 empty] | 0x03409004
STRUrnikiSC24Dan4Urn1UraON | INT | IOD_STR_disk | I2968 | [8 empty] | 0x03409005
STRUrnikiSC24Dan4Urn2UraON | INT | IOD_STR_disk | I2969 | [8 empty] | 0x03409006
STRUrnikiSC24Dan4Urn3UraON | INT | IOD_STR_disk | I2970 | [8 empty] | 0x03409007
STRUrnikiSC24Dan4Urn1UraOFF | INT | IOD_STR_disk | I2971 | [8 empty] | 0x03409008
STRUrnikiSC24Dan4Urn2UraOFF | INT | IOD_STR_disk | I2972 | [8 empty] | 0x03409009
STRUrnikiSC24Dan4Urn3UraOFF | INT | IOD_STR_disk | I2973 | [8 empty] | 0x0340900a
STRUrnikiSC24Dan4Urn1MinON | INT | IOD_STR_disk | I2974 | [8 empty] | 0x0340900b
STRUrnikiSC24Dan4Urn2MinON | INT | IOD_STR_disk | I2975 | [8 empty] | 0x0340900c
STRUrnikiSC24Dan4Urn3MinON | INT | IOD_STR_disk | I2976 | [8 empty] | 0x0340900d
STRUrnikiSC24Dan4Urn1MinOFF | INT | IOD_STR_disk | I2977 | [8 empty] | 0x0340900e
STRUrnikiSC24Dan4Urn2MinOFF | INT | IOD_STR_disk | I2978 | [8 empty] | 0x0340900f
STRUrnikiSC24Dan4Urn3MinOFF | INT | IOD_STR_disk | I2979 | [8 empty] | 0x03409010
STRUrnikiSC24Dan5Urn1UraON | INT | IOD_STR_disk | I2980 | [8 empty] | 0x03409011
STRUrnikiSC24Dan5Urn2UraON | INT | IOD_STR_disk | I2981 | [8 empty] | 0x03409012
STRUrnikiSC24Dan5Urn3UraON | INT | IOD_STR_disk | I2982 | [8 empty] | 0x03409013
STRUrnikiSC24Dan5Urn1UraOFF | INT | IOD_STR_disk | I2983 | [8 empty] | 0x03409014
STRUrnikiSC24Dan5Urn2UraOFF | INT | IOD_STR_disk | I2984 | [8 empty] | 0x03409015
STRUrnikiSC24Dan5Urn3UraOFF | INT | IOD_STR_disk | I2985 | [8 empty] | 0x03409016
STRUrnikiSC24Dan5Urn1MinON | INT | IOD_STR_disk | I2986 | [8 empty] | 0x03409017
STRUrnikiSC24Dan5Urn2MinON | INT | IOD_STR_disk | I2987 | [8 empty] | 0x03409018
STRUrnikiSC24Dan5Urn3MinON | INT | IOD_STR_disk | I2988 | [8 empty] | 0x03409019
STRUrnikiSC24Dan5Urn1MinOFF | INT | IOD_STR_disk | I2989 | [8 empty] | 0x0340901a
STRUrnikiSC24Dan5Urn2MinOFF | INT | IOD_STR_disk | I2990 | [8 empty] | 0x0340901b
STRUrnikiSC24Dan5Urn3MinOFF | INT | IOD_STR_disk | I2991 | [8 empty] | 0x0340901c
STRUrnikiSC24Dan6Urn1UraON | INT | IOD_STR_disk | I2992 | [8 empty] | 0x0340901d
STRUrnikiSC24Dan6Urn2UraON | INT | IOD_STR_disk | I2993 | [8 empty] | 0x0340901e
STRUrnikiSC24Dan6Urn3UraON | INT | IOD_STR_disk | I2994 | [8 empty] | 0x0340901f
STRUrnikiSC24Dan6Urn1UraOFF | INT | IOD_STR_disk | I2995 | [8 empty] | 0x03409020
STRUrnikiSC24Dan6Urn2UraOFF | INT | IOD_STR_disk | I2996 | [8 empty] | 0x03409021
STRUrnikiSC24Dan6Urn3UraOFF | INT | IOD_STR_disk | I2997 | [8 empty] | 0x03409022
STRUrnikiSC24Dan6Urn1MinON | INT | IOD_STR_disk | I2998 | [8 empty] | 0x03409023
STRUrnikiSC24Dan6Urn2MinON | INT | IOD_STR_disk | I2999 | [8 empty] | 0x03409024
STRUrnikiSC24Dan6Urn3MinON | INT | IOD_STR_disk | I3000 | [8 empty] | 0x03409025
STRUrnikiSC24Dan6Urn1MinOFF | INT | IOD_STR_disk | I3001 | [8 empty] | 0x03409026
STRUrnikiSC24Dan6Urn2MinOFF | INT | IOD_STR_disk | I3002 | [8 empty] | 0x03409027
STRUrnikiSC24Dan6Urn3MinOFF | INT | IOD_STR_disk | I3003 | [8 empty] | 0x03409028
STRUrnikiSC24Dan7Urn1UraON | INT | IOD_STR_disk | I3004 | [8 empty] | 0x03409029
STRUrnikiSC24Dan7Urn2UraON | INT | IOD_STR_disk | I3005 | [8 empty] | 0x0340902a
STRUrnikiSC24Dan7Urn3UraON | INT | IOD_STR_disk | I3006 | [8 empty] | 0x0340902b
STRUrnikiSC24Dan7Urn1UraOFF | INT | IOD_STR_disk | I3007 | [8 empty] | 0x0340902c
STRUrnikiSC24Dan7Urn2UraOFF | INT | IOD_STR_disk | I3008 | [8 empty] | 0x0340902d
STRUrnikiSC24Dan7Urn3UraOFF | INT | IOD_STR_disk | I3009 | [8 empty] | 0x0340902e
STRUrnikiSC24Dan7Urn1MinON | INT | IOD_STR_disk | I3010 | [8 empty] | 0x0340902f
STRUrnikiSC24Dan7Urn2MinON | INT | IOD_STR_disk | I3011 | [8 empty] | 0x03409030
STRUrnikiSC24Dan7Urn3MinON | INT | IOD_STR_disk | I3012 | [8 empty] | 0x03409031
STRUrnikiSC24Dan7Urn1MinOFF | INT | IOD_STR_disk | I3013 | [8 empty] | 0x03409032
STRUrnikiSC24Dan7Urn2MinOFF | INT | IOD_STR_disk | I3014 | [8 empty] | 0x03409033
STRUrnikiSC24Dan7Urn3MinOFF | INT | IOD_STR_disk | I3015 | [8 empty] | 0x03409034
STRPotrdiVpisUrnikaSC | DIGITAL | IOD_STR_disk | D327 | [8 empty] | 0x03409040
STRUrnikiSaveSCDan1On1Ura | INT | IOD_STR_disk | I3016 | [8 empty] | 0x03409050
STRUrnikiSaveSCDan1On1Mna | INT | IOD_STR_disk | I3017 | [8 empty] | 0x03409051
STRUrnikiSaveSCDan1Off1Ura | INT | IOD_STR_disk | I3018 | [8 empty] | 0x03409052
STRUrnikiSaveSCDan1Off1Mna | INT | IOD_STR_disk | I3019 | [8 empty] | 0x03409053
STRUrnikiSaveSCDan1On2Ura | INT | IOD_STR_disk | I3020 | [8 empty] | 0x03409054
STRUrnikiSaveSCDan1On2Mna | INT | IOD_STR_disk | I3021 | [8 empty] | 0x03409055
STRUrnikiSaveSCDan1Off2Ura | INT | IOD_STR_disk | I3022 | [8 empty] | 0x03409056
STRUrnikiSaveSCDan1Off2Mna | INT | IOD_STR_disk | I3023 | [8 empty] | 0x03409057
STRUrnikiSaveSCDan1On3Ura | INT | IOD_STR_disk | I3024 | [8 empty] | 0x03409058
STRUrnikiSaveSCDan1On3Mna | INT | IOD_STR_disk | I3025 | [8 empty] | 0x03409059
STRUrnikiSaveSCDan1Off3Ura | INT | IOD_STR_disk | I3026 | [8 empty] | 0x0340905a
STRUrnikiSaveSCDan1Off3Mna | INT | IOD_STR_disk | I3027 | [8 empty] | 0x0340905b
STRUrnikiSaveSCDan2On1Ura | INT | IOD_STR_disk | I3028 | [8 empty] | 0x0340905c
STRUrnikiSaveSCDan2On1Mna | INT | IOD_STR_disk | I3029 | [8 empty] | 0x0340905d
STRUrnikiSaveSCDan2Off1Ura | INT | IOD_STR_disk | I3030 | [8 empty] | 0x0340905e
STRUrnikiSaveSCDan2Off1Mna | INT | IOD_STR_disk | I3031 | [8 empty] | 0x0340905f
STRUrnikiSaveSCDan2On2Ura | INT | IOD_STR_disk | I3032 | [8 empty] | 0x03409060
STRUrnikiSaveSCDan2On2Mna | INT | IOD_STR_disk | I3033 | [8 empty] | 0x03409061
STRUrnikiSaveSCDan2Off2Ura | INT | IOD_STR_disk | I3034 | [8 empty] | 0x03409062
STRUrnikiSaveSCDan2Off2Mna | INT | IOD_STR_disk | I3035 | [8 empty] | 0x03409063
STRUrnikiSaveSCDan2On3Ura | INT | IOD_STR_disk | I3036 | [8 empty] | 0x03409064
STRUrnikiSaveSCDan2On3Mna | INT | IOD_STR_disk | I3037 | [8 empty] | 0x03409065
STRUrnikiSaveSCDan2Off3Ura | INT | IOD_STR_disk | I3038 | [8 empty] | 0x03409066
STRUrnikiSaveSCDan2Off3Mna | INT | IOD_STR_disk | I3039 | [8 empty] | 0x03409067
STRUrnikiSaveSCDan3On1Ura | INT | IOD_STR_disk | I3040 | [8 empty] | 0x03409068
STRUrnikiSaveSCDan3On1Mna | INT | IOD_STR_disk | I3041 | [8 empty] | 0x03409069
STRUrnikiSaveSCDan3Off1Ura | INT | IOD_STR_disk | I3042 | [8 empty] | 0x0340906a
STRUrnikiSaveSCDan3Off1Mna | INT | IOD_STR_disk | I3043 | [8 empty] | 0x0340906b
STRUrnikiSaveSCDan3On2Ura | INT | IOD_STR_disk | I3044 | [8 empty] | 0x0340906c
STRUrnikiSaveSCDan3On2Mna | INT | IOD_STR_disk | I3045 | [8 empty] | 0x0340906d
STRUrnikiSaveSCDan3Off2Ura | INT | IOD_STR_disk | I3046 | [8 empty] | 0x0340906e
STRUrnikiSaveSCDan3Off2Mna | INT | IOD_STR_disk | I3047 | [8 empty] | 0x0340906f
STRUrnikiSaveSCDan3On3Ura | INT | IOD_STR_disk | I3048 | [8 empty] | 0x03409070
STRUrnikiSaveSCDan3On3Mna | INT | IOD_STR_disk | I3049 | [8 empty] | 0x03409071
STRUrnikiSaveSCDan3Off3Ura | INT | IOD_STR_disk | I3050 | [8 empty] | 0x03409072
STRUrnikiSaveSCDan3Off3Mna | INT | IOD_STR_disk | I3051 | [8 empty] | 0x03409073
STRUrnikiSaveSCDan4On1Ura | INT | IOD_STR_disk | I3052 | [8 empty] | 0x03409074
STRUrnikiSaveSCDan4On1Mna | INT | IOD_STR_disk | I3053 | [8 empty] | 0x03409075
STRUrnikiSaveSCDan4Off1Ura | INT | IOD_STR_disk | I3054 | [8 empty] | 0x03409076
STRUrnikiSaveSCDan4Off1Mna | INT | IOD_STR_disk | I3055 | [8 empty] | 0x03409077
STRUrnikiSaveSCDan4On2Ura | INT | IOD_STR_disk | I3056 | [8 empty] | 0x03409078
STRUrnikiSaveSCDan4On2Mna | INT | IOD_STR_disk | I3057 | [8 empty] | 0x03409079
STRUrnikiSaveSCDan4Off2Ura | INT | IOD_STR_disk | I3058 | [8 empty] | 0x0340907a
STRUrnikiSaveSCDan4Off2Mna | INT | IOD_STR_disk | I3059 | [8 empty] | 0x0340907b
STRUrnikiSaveSCDan4On3Ura | INT | IOD_STR_disk | I3060 | [8 empty] | 0x0340907c
STRUrnikiSaveSCDan4On3Mna | INT | IOD_STR_disk | I3061 | [8 empty] | 0x0340907d
STRUrnikiSaveSCDan4Off3Ura | INT | IOD_STR_disk | I3062 | [8 empty] | 0x0340907e
STRUrnikiSaveSCDan4Off3Mna | INT | IOD_STR_disk | I3063 | [8 empty] | 0x0340907f
STRUrnikiSaveSCDan5On1Ura | INT | IOD_STR_disk | I3064 | [8 empty] | 0x03409080
STRUrnikiSaveSCDan5On1Mna | INT | IOD_STR_disk | I3065 | [8 empty] | 0x03409081
STRUrnikiSaveSCDan5Off1Ura | INT | IOD_STR_disk | I3066 | [8 empty] | 0x03409082
STRUrnikiSaveSCDan5Off1Mna | INT | IOD_STR_disk | I3067 | [8 empty] | 0x03409083
STRUrnikiSaveSCDan5On2Ura | INT | IOD_STR_disk | I3068 | [8 empty] | 0x03409084
STRUrnikiSaveSCDan5On2Mna | INT | IOD_STR_disk | I3069 | [8 empty] | 0x03409085
STRUrnikiSaveSCDan5Off2Ura | INT | IOD_STR_disk | I3070 | [8 empty] | 0x03409086
STRUrnikiSaveSCDan5Off2Mna | INT | IOD_STR_disk | I3071 | [8 empty] | 0x03409087
STRUrnikiSaveSCDan5On3Ura | INT | IOD_STR_disk | I3072 | [8 empty] | 0x03409088
STRUrnikiSaveSCDan5On3Mna | INT | IOD_STR_disk | I3073 | [8 empty] | 0x03409089
STRUrnikiSaveSCDan5Off3Ura | INT | IOD_STR_disk | I3074 | [8 empty] | 0x0340908a
STRUrnikiSaveSCDan5Off3Mna | INT | IOD_STR_disk | I3075 | [8 empty] | 0x0340908b
STRUrnikiSaveSCDan6On1Ura | INT | IOD_STR_disk | I3076 | [8 empty] | 0x0340908c
STRUrnikiSaveSCDan6On1Mna | INT | IOD_STR_disk | I3077 | [8 empty] | 0x0340908d
STRUrnikiSaveSCDan6Off1Ura | INT | IOD_STR_disk | I3078 | [8 empty] | 0x0340908e
STRUrnikiSaveSCDan6Off1Mna | INT | IOD_STR_disk | I3079 | [8 empty] | 0x0340908f
STRUrnikiSaveSCDan6On2Ura | INT | IOD_STR_disk | I3080 | [8 empty] | 0x03409090
STRUrnikiSaveSCDan6On2Mna | INT | IOD_STR_disk | I3081 | [8 empty] | 0x03409091
STRUrnikiSaveSCDan6Off2Ura | INT | IOD_STR_disk | I3082 | [8 empty] | 0x03409092
STRUrnikiSaveSCDan6Off2Mna | INT | IOD_STR_disk | I3083 | [8 empty] | 0x03409093
STRUrnikiSaveSCDan6On3Ura | INT | IOD_STR_disk | I3084 | [8 empty] | 0x03409094
STRUrnikiSaveSCDan6On3Mna | INT | IOD_STR_disk | I3085 | [8 empty] | 0x03409095
STRUrnikiSaveSCDan6Off3Ura | INT | IOD_STR_disk | I3086 | [8 empty] | 0x03409096
STRUrnikiSaveSCDan6Off3Mna | INT | IOD_STR_disk | I3087 | [8 empty] | 0x03409097
STRUrnikiSaveSCDan7On1Ura | INT | IOD_STR_disk | I3088 | [8 empty] | 0x03409098
STRUrnikiSaveSCDan7On1Mna | INT | IOD_STR_disk | I3089 | [8 empty] | 0x03409099
STRUrnikiSaveSCDan7Off1Ura | INT | IOD_STR_disk | I3090 | [8 empty] | 0x0340909a
STRUrnikiSaveSCDan7Off1Mna | INT | IOD_STR_disk | I3091 | [8 empty] | 0x0340909b
STRUrnikiSaveSCDan7On2Ura | INT | IOD_STR_disk | I3092 | [8 empty] | 0x0340909c
STRUrnikiSaveSCDan7On2Mna | INT | IOD_STR_disk | I3093 | [8 empty] | 0x0340909d
STRUrnikiSaveSCDan7Off2Ura | INT | IOD_STR_disk | I3094 | [8 empty] | 0x0340909e
STRUrnikiSaveSCDan7Off2Mna | INT | IOD_STR_disk | I3095 | [8 empty] | 0x0340909f
STRUrnikiSaveSCDan7On3Ura | INT | IOD_STR_disk | I3096 | [8 empty] | 0x034090a0
STRUrnikiSaveSCDan7On3Mna | INT | IOD_STR_disk | I3097 | [8 empty] | 0x034090a1
STRUrnikiSaveSCDan7Off3Ura | INT | IOD_STR_disk | I3098 | [8 empty] | 0x034090a2
STRUrnikiSaveSCDan7Off3Mna | INT | IOD_STR_disk | I3099 | [8 empty] | 0x034090a3
STRAkumSanVodeTE1OnOff | DIGITAL | IOD_STR | STR:.AkumSanVodeTE1OnOff | [6 empty] | 6157 | 1 | 0x034090b0
STRAlarmGenCirc1 | DIGITAL | IOD_STR | STR:.AlarmGenCirc1 | [6 empty] | 6157 | 1 | 0x034090c0
STRAlarmGenComm | DIGITAL | IOD_STR | STR:.AlarmGenComm | [6 empty] | 6157 | 1 | 0x034090d0
STRAlarmGenDI | DIGITAL | IOD_STR | STR:.AlarmGenDI | [6 empty] | 6157 | 1 | 0x034090e0
STRAlarmGenHladPost | DIGITAL | IOD_STR | STR:.AlarmGenHladPost | [6 empty] | 6157 | 1 | 0x034090f0
STRAlarmGenKlima1 | DIGITAL | IOD_STR | STR:.AlarmGenKlima1 | [6 empty] | 6157 | 1 | 0x03409100
STRAlarmGenKlima2 | DIGITAL | IOD_STR | STR:.AlarmGenKlima2 | [6 empty] | 6157 | 1 | 0x03409110
STRAlarmGenLopute | DIGITAL | IOD_STR | STR:.AlarmGenLopute | [6 empty] | 6157 | 1 | 0x03409120
STRAlarmGenRest | DIGITAL | IOD_STR | STR:.AlarmGenRest | [6 empty] | 6157 | 1 | 0x03409130
STRAlarmGenSenzor | DIGITAL | IOD_STR | STR:.AlarmGenSenzor | [6 empty] | 6157 | 1 | 0x03409140
STRAlarmGenTemp | DIGITAL | IOD_STR | STR:.AlarmGenTemp | [6 empty] | 6157 | 1 | 0x03409150
STRAlarmGenToplPost | DIGITAL | IOD_STR | STR:.AlarmGenToplPost | [6 empty] | 6157 | 1 | 0x03409160
STRAlarmGenVent | DIGITAL | IOD_STR | STR:.AlarmGenVent | [6 empty] | 6157 | 1 | 0x03409170
STRAlarmGenVTV | DIGITAL | IOD_STR | STR:.AlarmGenVTV | [6 empty] | 6157 | 1 | 0x03409180
STRATVAlarmTemp | REAL | IOD_STR | STR:.ATVAlarmTemp | 0 | 100 | 0 | 100 | °C | ####.# | 6157 | 1 | 0x03409190
STRATVTempPrenizka | DIGITAL | IOD_STR | STR:.ATVTempPrenizka | [6 empty] | 6157 | 1 | 0x034091a0
STRCirc1CosFi_III | REAL | IOD_STR | STR:.Circ[1].CosFi_III | -100 | 100 | -1.00 | 1.00 |  | ##.## | 6157 | 1 | 0x034091b0
STRCirc1DelovnaEnergija | REAL | IOD_STR | STR:.Circ[1].DelovnaEnergija | 0 | 1200 | 0 | 1200 | kW | ###.# | 6157 | 1 | 0x034091b1
STRCirc1DelovnaMoc_III | REAL | IOD_STR | STR:.Circ[1].DelovnaMoc_III | 0 | 1200 | 0 | 1200 | kW | ###.# | 6157 | 1 | 0x034091b2
STRCirc1DelovnaMoc_L1 | REAL | IOD_STR | STR:.Circ[1].DelovnaMoc_L1 | 0 | 1200 | 0 | 1200 | kW | ###.# | 6157 | 1 | 0x034091b3
STRCirc1DelovnaMoc_L2 | REAL | IOD_STR | STR:.Circ[1].DelovnaMoc_L2 | 0 | 1200 | 0 | 1200 | kW | ###.# | 6157 | 1 | 0x034091b4
STRCirc1DelovnaMoc_L3 | REAL | IOD_STR | STR:.Circ[1].DelovnaMoc_L3 | 0 | 1200 | 0 | 1200 | kW | ###.# | 6157 | 1 | 0x034091b5
STRCirc1Frekvenca_L1 | REAL | IOD_STR | STR:.Circ[1].Frekvenca_L1 | 0 | 60 | 0 | 60 | Hz | ##.# | 6157 | 1 | 0x034091b6
STRCirc1InduktivnaEnergija | REAL | IOD_STR | STR:.Circ[1].InduktivnaEnergija | 0 | 1000 | 0 | 1000 | kW | ###.# | 6157 | 1 | 0x034091b7
STRCirc1InduktivnaMoc_III | REAL | IOD_STR | STR:.Circ[1].InduktivnaMoc_III | 0 | 1200 | 0 | 1200 | kVAR | ###.# | 6157 | 1 | 0x034091b8
STRCirc1JalovaMoc_L1 | REAL | IOD_STR | STR:.Circ[1].JalovaMoc_L1 | 0 | 1200 | 0 | 1200 | kVAR | ###.# | 6157 | 1 | 0x034091b9
STRCirc1JalovaMoc_L2 | REAL | IOD_STR | STR:.Circ[1].JalovaMoc_L2 | 0 | 1200 | 0 | 1200 | kVAR | ###.# | 6157 | 1 | 0x034091ba
STRCirc1JalovaMoc_L3 | REAL | IOD_STR | STR:.Circ[1].JalovaMoc_L3 | 0 | 1200 | 0 | 1200 | kVAR | ###.# | 6157 | 1 | 0x034091bb
STRCirc1KapacitivnaEnergija | REAL | IOD_STR | STR:.Circ[1].KapacitivnaEnergija | [6 empty] | 6157 | 1 | 0x034091bc
STRCirc1KapacitivnaMoc_III | REAL | IOD_STR | STR:.Circ[1].KapacitivnaMoc_III | 0 | 1000 | 0 | 1000 | kVAR | ###.# | 6157 | 1 | 0x034091bd
STRCirc1MaximumDemand | REAL | IOD_STR | STR:.Circ[1].MaximumDemand | 0 | 1200 | 0 | 1200 | A | ###.# | 6157 | 1 | 0x034091be
STRCirc1Napetost_L1_L2 | REAL | IOD_STR | STR:.Circ[1].Napetost_L1_L2 | 0 | 450 | 0 | 450 | V | ###.# | 6157 | 1 | 0x034091bf
STRCirc1Napetost_L1_N | REAL | IOD_STR | STR:.Circ[1].Napetost_L1_N | 0 | 270 | 0 | 270 | V | ###.# | 6157 | 1 | 0x034091c0
STRCirc1Napetost_L2_L3 | REAL | IOD_STR | STR:.Circ[1].Napetost_L2_L3 | 0 | 450 | 0 | 450 | V | ###.# | 6157 | 1 | 0x034091c1
STRCirc1Napetost_L2_N | REAL | IOD_STR | STR:.Circ[1].Napetost_L2_N | 0 | 270 | 0 | 270 | V | ###.# | 6157 | 1 | 0x034091c2
STRCirc1Napetost_L3_L1 | REAL | IOD_STR | STR:.Circ[1].Napetost_L3_L1 | 0 | 450 | 0 | 450 | V | ###.# | 6157 | 1 | 0x034091c3
STRCirc1Napetost_L3_N | REAL | IOD_STR | STR:.Circ[1].Napetost_L3_N | 0 | 270 | 0 | 270 | V | ###.# | 6157 | 1 | 0x034091c4
STRCirc1NavideznaMoc_III | REAL | IOD_STR | STR:.Circ[1].NavideznaMoc_III | 0 | 1200 | 0 | 1200 | kVA | ###.# | 6157 | 1 | 0x034091c5
STRCirc1NicelniTok | REAL | IOD_STR | STR:.Circ[1].NicelniTok | 0 | 1200 | 0 | 1200 | A | ###.# | 6157 | 1 | 0x034091c6
STRCirc1PowerFactor_III | REAL | IOD_STR | STR:.Circ[1].PowerFactor_III | -100 | 100 | -1.00 | 1.00 |  | ##.## | 6157 | 1 | 0x034091c7
STRCirc1PowerFactor_L1 | REAL | IOD_STR | STR:.Circ[1].PowerFactor_L1 | -100 | 100 | -1.00 | 1.00 |  | ##.## | 6157 | 1 | 0x034091c8
STRCirc1PowerFactor_L2 | REAL | IOD_STR | STR:.Circ[1].PowerFactor_L2 | -100 | 100 | -1.00 | 1.00 |  | ##.## | 6157 | 1 | 0x034091c9
STRCirc1PowerFactor_L3 | REAL | IOD_STR | STR:.Circ[1].PowerFactor_L3 | -100 | 100 | -1.00 | 1.00 |  | ##.## | 6157 | 1 | 0x034091ca
STRCirc1THDI_L1 | REAL | IOD_STR | STR:.Circ[1].THDI_L1 | 0 | 100 | 0 | 10 | % | ###.# | 6157 | 1 | 0x034091cb
STRCirc1THDI_L2 | REAL | IOD_STR | STR:.Circ[1].THDI_L2 | 0 | 100 | 0 | 10 | % | ###.# | 6157 | 1 | 0x034091cc
STRCirc1THDI_L3 | REAL | IOD_STR | STR:.Circ[1].THDI_L3 | 0 | 100 | 0 | 10 | % | ###.# | 6157 | 1 | 0x034091cd
STRCirc1THDV_L1 | REAL | IOD_STR | STR:.Circ[1].THDV_L1 | 0 | 100 | 0 | 10 | % | ###.# | 6157 | 1 | 0x034091ce
STRCirc1THDV_L2 | REAL | IOD_STR | STR:.Circ[1].THDV_L2 | 0 | 100 | 0 | 10 | % | ###.# | 6157 | 1 | 0x034091cf
STRCirc1THDV_L3 | REAL | IOD_STR | STR:.Circ[1].THDV_L3 | 0 | 100 | 0 | 10 | % | ###.# | 6157 | 1 | 0x034091d0
STRCirc1Tok_L1 | REAL | IOD_STR | STR:.Circ[1].Tok_L1 | 0 | 1200 | 0 | 1200 | A | ###.# | 6157 | 1 | 0x034091d1
STRCirc1Tok_L2 | REAL | IOD_STR | STR:.Circ[1].Tok_L2 | 0 | 1200 | 0 | 1200 | A | ###.# | 6157 | 1 | 0x034091d2
STRCirc1Tok_L3 | REAL | IOD_STR | STR:.Circ[1].Tok_L3 | 0 | 1200 | 0 | 1200 | A | ###.# | 6157 | 1 | 0x034091d3
STRCirc1TokPovprecje_III | REAL | IOD_STR | STR:.Circ[1].TokPovprecje_III | 0 | 1200 | 0 | 1200 | A | ###.# | 6157 | 1 | 0x034091d4
STRComSCADA | DIGITAL | IOD_STR | STR:.ComSCADA | [6 empty] | 6157 | 1 | 0x034091e0
STRComSCADA1 | DIGITAL | IOD_STR | STR:.ComSCADA1 | [6 empty] | 6157 | 1 | 0x034091f0
STRCrpalkaMN1OnOff | DIGITAL | IOD_STR | STR:.CrpalkaMN1OnOff | [6 empty] | 6157 | 1 | 0x03409200
STRCrpalkaTm11TM12OnOff | DIGITAL | IOD_STR | STR:.CrpalkaTm11TM12OnOff | [6 empty] | 6157 | 1 | 0x03409210
STRCrpalkeDnfs1AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].AlarmAktiven | [6 empty] | 6157 | 1 | 0x03409220
STRCrpalkeDnfs1Current | REAL | IOD_STR | STR:.CrpalkeDnfs[1].Current | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409230
STRCrpalkeDnfs1Deluje | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].Deluje | [6 empty] | 6157 | 1 | 0x03409240
STRCrpalkeDnfs1PreklopkaMode | INT | IOD_STR | STR:.CrpalkeDnfs[1].PreklopkaMode | [6 empty] | 6157 | 1 | 0x03409250
STRCrpalkeDnfs1QuickStop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].QuickStop | [6 empty] | 6157 | 1 | 0x03409260
STRCrpalkeDnfs1RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].RemoteON | [6 empty] | 6157 | 1 | 0x03409270
STRCrpalkeDnfs1Reset | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].Reset | [6 empty] | 6157 | 1 | 0x03409280
STRCrpalkeDnfs1Start | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].Start | [6 empty] | 6157 | 1 | 0x03409290
STRCrpalkeDnfs1StarterStatus | REAL | IOD_STR | STR:.CrpalkeDnfs[1].StarterStatus | [6 empty] | 6157 | 1 | 0x034092a0
STRCrpalkeDnfs1StarterStatus0do7 | BYTE | IOD_STR | STR:.CrpalkeDnfs[1].StarterStatus0do7 | [6 empty] | 6157 | 1 | 0x034092a1
STRCrpalkeDnfs1StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeDnfs[1].StatusCrpalke | [6 empty] | 6157 | 1 | 0x034092a2
STRCrpalkeDnfs1StatusKontaktor | INT | IOD_STR | STR:.CrpalkeDnfs[1].StatusKontaktor | [6 empty] | 6157 | 1 | 0x034092a3
STRCrpalkeDnfs1Stop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].Stop | [6 empty] | 6157 | 1 | 0x034092b0
STRCrpalkeDnfs1Temerature | REAL | IOD_STR | STR:.CrpalkeDnfs[1].Temerature | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x034092c0
STRCrpalkeDnfs1TripCode | REAL | IOD_STR | STR:.CrpalkeDnfs[1].TripCode | [6 empty] | 6157 | 1 | 0x034092c1
STRCrpalkeDnfs1UreXC200 | REAL | IOD_STR | STR:.CrpalkeDnfs[1].UreXC200 |  |  |  |  | h | #### | 6157 | 1 | 0x034092c2
STRCrpalkeDnfs2AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].AlarmAktiven | [6 empty] | 6157 | 1 | 0x034092d0
STRCrpalkeDnfs2Current | REAL | IOD_STR | STR:.CrpalkeDnfs[2].Current | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x034092e0
STRCrpalkeDnfs2Deluje | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].Deluje | [6 empty] | 6157 | 1 | 0x034092f0
STRCrpalkeDnfs2PreklopkaMode | INT | IOD_STR | STR:.CrpalkeDnfs[2].PreklopkaMode | [6 empty] | 6157 | 1 | 0x03409300
STRCrpalkeDnfs2QuickStop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].QuickStop | [6 empty] | 6157 | 1 | 0x03409310
STRCrpalkeDnfs2RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].RemoteON | [6 empty] | 6157 | 1 | 0x03409320
STRCrpalkeDnfs2Reset | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].Reset | [6 empty] | 6157 | 1 | 0x03409330
STRCrpalkeDnfs2Start | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].Start | [6 empty] | 6157 | 1 | 0x03409340
STRCrpalkeDnfs2StarterStatus | REAL | IOD_STR | STR:.CrpalkeDnfs[2].StarterStatus | [6 empty] | 6157 | 1 | 0x03409350
STRCrpalkeDnfs2StarterStatus0do7 | BYTE | IOD_STR | STR:.CrpalkeDnfs[2].StarterStatus0do7 | [6 empty] | 6157 | 1 | 0x03409351
STRCrpalkeDnfs2StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeDnfs[2].StatusCrpalke | [6 empty] | 6157 | 1 | 0x03409352
STRCrpalkeDnfs2StatusKontaktor | INT | IOD_STR | STR:.CrpalkeDnfs[2].StatusKontaktor | [6 empty] | 6157 | 1 | 0x03409353
STRCrpalkeDnfs2Stop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].Stop | [6 empty] | 6157 | 1 | 0x03409360
STRCrpalkeDnfs2Temerature | REAL | IOD_STR | STR:.CrpalkeDnfs[2].Temerature | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x03409370
STRCrpalkeDnfs2TripCode | REAL | IOD_STR | STR:.CrpalkeDnfs[2].TripCode | [6 empty] | 6157 | 1 | 0x03409371
STRCrpalkeDnfs2UreXC200 | REAL | IOD_STR | STR:.CrpalkeDnfs[2].UreXC200 |  |  |  |  | h | #### | 6157 | 1 | 0x03409372
STRCrpalkeDnfs3AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].AlarmAktiven | [6 empty] | 6157 | 1 | 0x03409380
STRCrpalkeDnfs3Current | REAL | IOD_STR | STR:.CrpalkeDnfs[3].Current | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409390
STRCrpalkeDnfs3Deluje | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].Deluje | [6 empty] | 6157 | 1 | 0x034093a0
STRCrpalkeDnfs3PreklopkaMode | INT | IOD_STR | STR:.CrpalkeDnfs[3].PreklopkaMode | [6 empty] | 6157 | 1 | 0x034093b0
STRCrpalkeDnfs3QuickStop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].QuickStop | [6 empty] | 6157 | 1 | 0x034093c0
STRCrpalkeDnfs3RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].RemoteON | [6 empty] | 6157 | 1 | 0x034093d0
STRCrpalkeDnfs3Reset | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].Reset | [6 empty] | 6157 | 1 | 0x034093e0
STRCrpalkeDnfs3Start | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].Start | [6 empty] | 6157 | 1 | 0x034093f0
STRCrpalkeDnfs3StarterStatus | REAL | IOD_STR | STR:.CrpalkeDnfs[3].StarterStatus | [6 empty] | 6157 | 1 | 0x03409400
STRCrpalkeDnfs3StarterStatus0do7 | BYTE | IOD_STR | STR:.CrpalkeDnfs[3].StarterStatus0do7 | [6 empty] | 6157 | 1 | 0x03409401
STRCrpalkeDnfs3StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeDnfs[3].StatusCrpalke | [6 empty] | 6157 | 1 | 0x03409402
STRCrpalkeDnfs3StatusKontaktor | INT | IOD_STR | STR:.CrpalkeDnfs[3].StatusKontaktor | [6 empty] | 6157 | 1 | 0x03409403
STRCrpalkeDnfs3Stop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].Stop | [6 empty] | 6157 | 1 | 0x03409410
STRCrpalkeDnfs3Temerature | REAL | IOD_STR | STR:.CrpalkeDnfs[3].Temerature | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x03409420
STRCrpalkeDnfs3TripCode | REAL | IOD_STR | STR:.CrpalkeDnfs[3].TripCode | [6 empty] | 6157 | 1 | 0x03409421
STRCrpalkeDnfs3UreXC200 | REAL | IOD_STR | STR:.CrpalkeDnfs[3].UreXC200 |  |  |  |  | h | #### | 6157 | 1 | 0x03409422
STRCrpalkeDnfs4AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].AlarmAktiven | [6 empty] | 6157 | 1 | 0x03409430
STRCrpalkeDnfs4Current | REAL | IOD_STR | STR:.CrpalkeDnfs[4].Current | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409440
STRCrpalkeDnfs4Deluje | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].Deluje | [6 empty] | 6157 | 1 | 0x03409450
STRCrpalkeDnfs4PreklopkaMode | INT | IOD_STR | STR:.CrpalkeDnfs[4].PreklopkaMode | [6 empty] | 6157 | 1 | 0x03409460
STRCrpalkeDnfs4QuickStop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].QuickStop | [6 empty] | 6157 | 1 | 0x03409470
STRCrpalkeDnfs4RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].RemoteON | [6 empty] | 6157 | 1 | 0x03409480
STRCrpalkeDnfs4Reset | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].Reset | [6 empty] | 6157 | 1 | 0x03409490
STRCrpalkeDnfs4Start | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].Start | [6 empty] | 6157 | 1 | 0x034094a0
STRCrpalkeDnfs4StarterStatus | REAL | IOD_STR | STR:.CrpalkeDnfs[4].StarterStatus | [6 empty] | 6157 | 1 | 0x034094b0
STRCrpalkeDnfs4StarterStatus0do7 | BYTE | IOD_STR | STR:.CrpalkeDnfs[4].StarterStatus0do7 | [6 empty] | 6157 | 1 | 0x034094b1
STRCrpalkeDnfs4StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeDnfs[4].StatusCrpalke | [6 empty] | 6157 | 1 | 0x034094b2
STRCrpalkeDnfs4StatusKontaktor | INT | IOD_STR | STR:.CrpalkeDnfs[4].StatusKontaktor | [6 empty] | 6157 | 1 | 0x034094b3
STRCrpalkeDnfs4Stop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].Stop | [6 empty] | 6157 | 1 | 0x034094c0
STRCrpalkeDnfs4Temerature | REAL | IOD_STR | STR:.CrpalkeDnfs[4].Temerature | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x034094d0
STRCrpalkeDnfs4TripCode | REAL | IOD_STR | STR:.CrpalkeDnfs[4].TripCode | [6 empty] | 6157 | 1 | 0x034094d1
STRCrpalkeDnfs4UreXC200 | REAL | IOD_STR | STR:.CrpalkeDnfs[4].UreXC200 |  |  |  |  | h | #### | 6157 | 1 | 0x034094d2
STRCrpalkeGrfs10AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmActiveCode | [6 empty] | 6157 | 1 | 0x034094d3
STRCrpalkeGrfs10AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].AlarmAktiven | [6 empty] | 6157 | 1 | 0x034094e0
STRCrpalkeGrfs10AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmCodeLog1 | [6 empty] | 6157 | 1 | 0x034094f0
STRCrpalkeGrfs10AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmCodeLog2 | [6 empty] | 6157 | 1 | 0x034094f1
STRCrpalkeGrfs10AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmCodeLog3 | [6 empty] | 6157 | 1 | 0x034094f2
STRCrpalkeGrfs10AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmCodeLog4 | [6 empty] | 6157 | 1 | 0x034094f3
STRCrpalkeGrfs10AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmCodeLog5 | [6 empty] | 6157 | 1 | 0x034094f4
STRCrpalkeGrfs10AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[0] | [6 empty] | 6157 | 1 | 0x034094f5
STRCrpalkeGrfs10AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[10] | [6 empty] | 6157 | 1 | 0x034094f6
STRCrpalkeGrfs10AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[11] | [6 empty] | 6157 | 1 | 0x034094f7
STRCrpalkeGrfs10AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[12] | [6 empty] | 6157 | 1 | 0x034094f8
STRCrpalkeGrfs10AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[13] | [6 empty] | 6157 | 1 | 0x034094f9
STRCrpalkeGrfs10AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[14] | [6 empty] | 6157 | 1 | 0x034094fa
STRCrpalkeGrfs10AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[15] | [6 empty] | 6157 | 1 | 0x034094fb
STRCrpalkeGrfs10AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[16] | [6 empty] | 6157 | 1 | 0x034094fc
STRCrpalkeGrfs10AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[1] | [6 empty] | 6157 | 1 | 0x034094fd
STRCrpalkeGrfs10AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[2] | [6 empty] | 6157 | 1 | 0x034094fe
STRCrpalkeGrfs10AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[3] | [6 empty] | 6157 | 1 | 0x034094ff
STRCrpalkeGrfs10AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[4] | [6 empty] | 6157 | 1 | 0x03409500
STRCrpalkeGrfs10AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[5] | [6 empty] | 6157 | 1 | 0x03409501
STRCrpalkeGrfs10AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[6] | [6 empty] | 6157 | 1 | 0x03409502
STRCrpalkeGrfs10AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[7] | [6 empty] | 6157 | 1 | 0x03409503
STRCrpalkeGrfs10AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[8] | [6 empty] | 6157 | 1 | 0x03409504
STRCrpalkeGrfs10AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[9] | [6 empty] | 6157 | 1 | 0x03409505
STRCrpalkeGrfs10AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmQSD1 | [6 empty] | 6157 | 1 | 0x03409506
STRCrpalkeGrfs10AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmQSD2 | [6 empty] | 6157 | 1 | 0x03409507
STRCrpalkeGrfs10AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmStart1 | [6 empty] | 6157 | 1 | 0x03409508
STRCrpalkeGrfs10AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmStart2 | [6 empty] | 6157 | 1 | 0x03409509
STRCrpalkeGrfs10AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmStop1 | [6 empty] | 6157 | 1 | 0x0340950a
STRCrpalkeGrfs10AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmStop2 | [6 empty] | 6157 | 1 | 0x0340950b
STRCrpalkeGrfs10AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmStop3 | [6 empty] | 6157 | 1 | 0x0340950c
STRCrpalkeGrfs10AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmSurv1 | [6 empty] | 6157 | 1 | 0x0340950d
STRCrpalkeGrfs10AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmSurv2 | [6 empty] | 6157 | 1 | 0x0340950e
STRCrpalkeGrfs10ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[10].ControlSource | [6 empty] | 6157 | 1 | 0x0340950f
STRCrpalkeGrfs10DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[10].DeltaSetPoint | [6 empty] | 6157 | 1 | 0x03409510
STRCrpalkeGrfs10Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].Deluje | [6 empty] | 6157 | 1 | 0x03409520
STRCrpalkeGrfs10EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[10].EnergijaPoraba |  |  |  |  | kWh | ####.# | 6157 | 1 | 0x03409530
STRCrpalkeGrfs10ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[10].ExternInputSetup | [6 empty] | 6157 | 1 | 0x03409531
STRCrpalkeGrfs10ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[10].ExternInputsStatus | [6 empty] | 6157 | 1 | 0x03409532
STRCrpalkeGrfs10FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[10].FrekPretvornikDCNapetost | 0 | 500 | 0 | 500 | V | ####.# | 6157 | 1 | 0x03409533
STRCrpalkeGrfs10FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[10].FrekPretvornikDCTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409534
STRCrpalkeGrfs10FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[10].FreqMax | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409535
STRCrpalkeGrfs10FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[10].FreqMin | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409536
STRCrpalkeGrfs10FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[10].FreqUpper | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409537
STRCrpalkeGrfs10LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].LocalMode | [6 empty] | 6157 | 1 | 0x03409540
STRCrpalkeGrfs10LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].LocalSetupMode1 | [6 empty] | 6157 | 1 | 0x03409550
STRCrpalkeGrfs10MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[10].MocMax | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x03409551
STRCrpalkeGrfs10MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[10].MocTrenutna | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x03409552
STRCrpalkeGrfs10MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[10].MotorHitrost | 0 | 2500 | 0 | 2500 | obr/min | ####.# | 6157 | 1 | 0x03409553
STRCrpalkeGrfs10MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[10].MotorTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409554
STRCrpalkeGrfs10NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[10].NapajanjeTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409555
STRCrpalkeGrfs10NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[10].NastavitevLokalna | [6 empty] | 6157 | 1 | 0x03409556
STRCrpalkeGrfs10NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[10].NastavitevTrenutna | [6 empty] | 6157 | 1 | 0x03409557
STRCrpalkeGrfs10PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[10].PreklopkaMode | [6 empty] | 6157 | 1 | 0x03409558
STRCrpalkeGrfs10PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[10].PretokMax | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x03409559
STRCrpalkeGrfs10PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[10].PretokMin | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340955a
STRCrpalkeGrfs10PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[10].PretokTrenutni | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340955b
STRCrpalkeGrfs10PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[10].PritiskMax | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340955c
STRCrpalkeGrfs10PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[10].PritiskTrenutni | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340955d
STRCrpalkeGrfs10ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[10].ReferencaMotorjaHzV | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340955e
STRCrpalkeGrfs10ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[10].ReferencaRemote | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340955f
STRCrpalkeGrfs10Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[10].Relay1setup | [6 empty] | 6157 | 1 | 0x03409560
STRCrpalkeGrfs10RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].RemoteON | [6 empty] | 6157 | 1 | 0x03409570
STRCrpalkeGrfs10RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].RemoteSetupMode1 | [6 empty] | 6157 | 1 | 0x03409580
STRCrpalkeGrfs10Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].Reset2handkWhValues | [6 empty] | 6157 | 1 | 0x03409590
STRCrpalkeGrfs10ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].ResetAlarm | [6 empty] | 6157 | 1 | 0x034095a0
STRCrpalkeGrfs10ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].ResetAlarmLog | [6 empty] | 6157 | 1 | 0x034095b0
STRCrpalkeGrfs10ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].ResetDevice | [6 empty] | 6157 | 1 | 0x034095c0
STRCrpalkeGrfs10SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetAutomatic | [6 empty] | 6157 | 1 | 0x034095d0
STRCrpalkeGrfs10SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetConstFreqMode | [6 empty] | 6157 | 1 | 0x034095e0
STRCrpalkeGrfs10SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetConstPress | [6 empty] | 6157 | 1 | 0x034095f0
STRCrpalkeGrfs10SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetLocalMode | [6 empty] | 6157 | 1 | 0x03409600
STRCrpalkeGrfs10SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetMaxRunMode | [6 empty] | 6157 | 1 | 0x03409610
STRCrpalkeGrfs10SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetMinRunMode | [6 empty] | 6157 | 1 | 0x03409620
STRCrpalkeGrfs10SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetPropPress | [6 empty] | 6157 | 1 | 0x03409630
STRCrpalkeGrfs10SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetReference | [6 empty] | 6157 | 1 | 0x03409640
STRCrpalkeGrfs10SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetRemoteMode | [6 empty] | 6157 | 1 | 0x03409650
STRCrpalkeGrfs10SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetTwinModeAlt | [6 empty] | 6157 | 1 | 0x03409660
STRCrpalkeGrfs10SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetTwinModeSpare | [6 empty] | 6157 | 1 | 0x03409670
STRCrpalkeGrfs10SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetTwinModeSync | [6 empty] | 6157 | 1 | 0x03409680
STRCrpalkeGrfs10Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].Start | [6 empty] | 6157 | 1 | 0x03409690
STRCrpalkeGrfs10StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeGrfs[10].StatusCrpalke | [6 empty] | 6157 | 1 | 0x034096a0
STRCrpalkeGrfs10StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].StatusMode1 | [6 empty] | 6157 | 1 | 0x034096a1
STRCrpalkeGrfs10StatusMode1co | BYTE | IOD_STR | STR:.CrpalkeGrfs[10].StatusMode1co | [6 empty] | 6157 | 1 | 0x034096a2
STRCrpalkeGrfs10StatusMode1op | BYTE | IOD_STR | STR:.CrpalkeGrfs[10].StatusMode1op | [6 empty] | 6157 | 1 | 0x034096a3
STRCrpalkeGrfs10StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].StatusMode2 | [6 empty] | 6157 | 1 | 0x034096a4
STRCrpalkeGrfs10StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[10].StatusMode3 | [6 empty] | 6157 | 1 | 0x034096a5
STRCrpalkeGrfs10StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[10].StevecUr2h |  |  |  |  | 2h |  | 6157 | 1 | 0x034096a6
STRCrpalkeGrfs10Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].Stop | [6 empty] | 6157 | 1 | 0x034096b0
STRCrpalkeGrfs10SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[10].SystemFeedback | [6 empty] | 6157 | 1 | 0x034096c0
STRCrpalkeGrfs10SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[10].SystemReference | [6 empty] | 6157 | 1 | 0x034096c1
STRCrpalkeGrfs10TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[10].TemperaturaMotorja | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x034096c2
STRCrpalkeGrfs10UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[10].UreXC200 |  |  |  |  | h | ####.# | 6157 | 1 | 0x034096c3
STRCrpalkeGrfs11AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmActiveCode | [6 empty] | 6157 | 1 | 0x034096c4
STRCrpalkeGrfs11AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].AlarmAktiven | [6 empty] | 6157 | 1 | 0x034096d0
STRCrpalkeGrfs11AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmCodeLog1 | [6 empty] | 6157 | 1 | 0x034096e0
STRCrpalkeGrfs11AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmCodeLog2 | [6 empty] | 6157 | 1 | 0x034096e1
STRCrpalkeGrfs11AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmCodeLog3 | [6 empty] | 6157 | 1 | 0x034096e2
STRCrpalkeGrfs11AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmCodeLog4 | [6 empty] | 6157 | 1 | 0x034096e3
STRCrpalkeGrfs11AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmCodeLog5 | [6 empty] | 6157 | 1 | 0x034096e4
STRCrpalkeGrfs11AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[0] | [6 empty] | 6157 | 1 | 0x034096e5
STRCrpalkeGrfs11AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[10] | [6 empty] | 6157 | 1 | 0x034096e6
STRCrpalkeGrfs11AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[11] | [6 empty] | 6157 | 1 | 0x034096e7
STRCrpalkeGrfs11AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[12] | [6 empty] | 6157 | 1 | 0x034096e8
STRCrpalkeGrfs11AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[13] | [6 empty] | 6157 | 1 | 0x034096e9
STRCrpalkeGrfs11AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[14] | [6 empty] | 6157 | 1 | 0x034096ea
STRCrpalkeGrfs11AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[15] | [6 empty] | 6157 | 1 | 0x034096eb
STRCrpalkeGrfs11AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[16] | [6 empty] | 6157 | 1 | 0x034096ec
STRCrpalkeGrfs11AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[1] | [6 empty] | 6157 | 1 | 0x034096ed
STRCrpalkeGrfs11AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[2] | [6 empty] | 6157 | 1 | 0x034096ee
STRCrpalkeGrfs11AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[3] | [6 empty] | 6157 | 1 | 0x034096ef
STRCrpalkeGrfs11AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[4] | [6 empty] | 6157 | 1 | 0x034096f0
STRCrpalkeGrfs11AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[5] | [6 empty] | 6157 | 1 | 0x034096f1
STRCrpalkeGrfs11AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[6] | [6 empty] | 6157 | 1 | 0x034096f2
STRCrpalkeGrfs11AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[7] | [6 empty] | 6157 | 1 | 0x034096f3
STRCrpalkeGrfs11AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[8] | [6 empty] | 6157 | 1 | 0x034096f4
STRCrpalkeGrfs11AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[9] | [6 empty] | 6157 | 1 | 0x034096f5
STRCrpalkeGrfs11AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmQSD1 | [6 empty] | 6157 | 1 | 0x034096f6
STRCrpalkeGrfs11AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmQSD2 | [6 empty] | 6157 | 1 | 0x034096f7
STRCrpalkeGrfs11AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmStart1 | [6 empty] | 6157 | 1 | 0x034096f8
STRCrpalkeGrfs11AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmStart2 | [6 empty] | 6157 | 1 | 0x034096f9
STRCrpalkeGrfs11AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmStop1 | [6 empty] | 6157 | 1 | 0x034096fa
STRCrpalkeGrfs11AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmStop2 | [6 empty] | 6157 | 1 | 0x034096fb
STRCrpalkeGrfs11AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmStop3 | [6 empty] | 6157 | 1 | 0x034096fc
STRCrpalkeGrfs11AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmSurv1 | [6 empty] | 6157 | 1 | 0x034096fd
STRCrpalkeGrfs11AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmSurv2 | [6 empty] | 6157 | 1 | 0x034096fe
STRCrpalkeGrfs11ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[11].ControlSource | [6 empty] | 6157 | 1 | 0x034096ff
STRCrpalkeGrfs11DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[11].DeltaSetPoint | [6 empty] | 6157 | 1 | 0x03409700
STRCrpalkeGrfs11Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].Deluje | [6 empty] | 6157 | 1 | 0x03409710
STRCrpalkeGrfs11EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[11].EnergijaPoraba |  |  |  |  | kWh | ####.# | 6157 | 1 | 0x03409720
STRCrpalkeGrfs11ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[11].ExternInputSetup | [6 empty] | 6157 | 1 | 0x03409721
STRCrpalkeGrfs11ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[11].ExternInputsStatus | [6 empty] | 6157 | 1 | 0x03409722
STRCrpalkeGrfs11FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[11].FrekPretvornikDCNapetost | 0 | 500 | 0 | 500 | V | ####.# | 6157 | 1 | 0x03409723
STRCrpalkeGrfs11FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[11].FrekPretvornikDCTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409724
STRCrpalkeGrfs11FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[11].FreqMax | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409725
STRCrpalkeGrfs11FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[11].FreqMin | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409726
STRCrpalkeGrfs11FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[11].FreqUpper | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409727
STRCrpalkeGrfs11LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].LocalMode | [6 empty] | 6157 | 1 | 0x03409730
STRCrpalkeGrfs11LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].LocalSetupMode1 | [6 empty] | 6157 | 1 | 0x03409740
STRCrpalkeGrfs11MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[11].MocMax | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x03409741
STRCrpalkeGrfs11MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[11].MocTrenutna | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x03409742
STRCrpalkeGrfs11MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[11].MotorHitrost | 0 | 2500 | 0 | 2500 | obr/min | ####.# | 6157 | 1 | 0x03409743
STRCrpalkeGrfs11MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[11].MotorTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409744
STRCrpalkeGrfs11NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[11].NapajanjeTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409745
STRCrpalkeGrfs11NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[11].NastavitevLokalna | [6 empty] | 6157 | 1 | 0x03409746
STRCrpalkeGrfs11NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[11].NastavitevTrenutna | [6 empty] | 6157 | 1 | 0x03409747
STRCrpalkeGrfs11PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[11].PreklopkaMode | [6 empty] | 6157 | 1 | 0x03409748
STRCrpalkeGrfs11PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[11].PretokMax | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x03409749
STRCrpalkeGrfs11PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[11].PretokMin | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340974a
STRCrpalkeGrfs11PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[11].PretokTrenutni | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340974b
STRCrpalkeGrfs11PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[11].PritiskMax | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340974c
STRCrpalkeGrfs11PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[11].PritiskTrenutni | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340974d
STRCrpalkeGrfs11ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[11].ReferencaMotorjaHzV | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340974e
STRCrpalkeGrfs11ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[11].ReferencaRemote | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340974f
STRCrpalkeGrfs11Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[11].Relay1setup | [6 empty] | 6157 | 1 | 0x03409750
STRCrpalkeGrfs11RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].RemoteON | [6 empty] | 6157 | 1 | 0x03409760
STRCrpalkeGrfs11RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].RemoteSetupMode1 | [6 empty] | 6157 | 1 | 0x03409770
STRCrpalkeGrfs11Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].Reset2handkWhValues | [6 empty] | 6157 | 1 | 0x03409780
STRCrpalkeGrfs11ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].ResetAlarm | [6 empty] | 6157 | 1 | 0x03409790
STRCrpalkeGrfs11ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].ResetAlarmLog | [6 empty] | 6157 | 1 | 0x034097a0
STRCrpalkeGrfs11ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].ResetDevice | [6 empty] | 6157 | 1 | 0x034097b0
STRCrpalkeGrfs11SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetAutomatic | [6 empty] | 6157 | 1 | 0x034097c0
STRCrpalkeGrfs11SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetConstFreqMode | [6 empty] | 6157 | 1 | 0x034097d0
STRCrpalkeGrfs11SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetConstPress | [6 empty] | 6157 | 1 | 0x034097e0
STRCrpalkeGrfs11SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetLocalMode | [6 empty] | 6157 | 1 | 0x034097f0
STRCrpalkeGrfs11SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetMaxRunMode | [6 empty] | 6157 | 1 | 0x03409800
STRCrpalkeGrfs11SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetMinRunMode | [6 empty] | 6157 | 1 | 0x03409810
STRCrpalkeGrfs11SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetPropPress | [6 empty] | 6157 | 1 | 0x03409820
STRCrpalkeGrfs11SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetReference | [6 empty] | 6157 | 1 | 0x03409830
STRCrpalkeGrfs11SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetRemoteMode | [6 empty] | 6157 | 1 | 0x03409840
STRCrpalkeGrfs11SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetTwinModeAlt | [6 empty] | 6157 | 1 | 0x03409850
STRCrpalkeGrfs11SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetTwinModeSpare | [6 empty] | 6157 | 1 | 0x03409860
STRCrpalkeGrfs11SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetTwinModeSync | [6 empty] | 6157 | 1 | 0x03409870
STRCrpalkeGrfs11Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].Start | [6 empty] | 6157 | 1 | 0x03409880
STRCrpalkeGrfs11StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeGrfs[11].StatusCrpalke | [6 empty] | 6157 | 1 | 0x03409890
STRCrpalkeGrfs11StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].StatusMode1 | [6 empty] | 6157 | 1 | 0x03409891
STRCrpalkeGrfs11StatusMode1co | BYTE | IOD_STR | STR:.CrpalkeGrfs[11].StatusMode1co | [6 empty] | 6157 | 1 | 0x03409892
STRCrpalkeGrfs11StatusMode1op | BYTE | IOD_STR | STR:.CrpalkeGrfs[11].StatusMode1op | [6 empty] | 6157 | 1 | 0x03409893
STRCrpalkeGrfs11StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].StatusMode2 | [6 empty] | 6157 | 1 | 0x03409894
STRCrpalkeGrfs11StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[11].StatusMode3 | [6 empty] | 6157 | 1 | 0x03409895
STRCrpalkeGrfs11StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[11].StevecUr2h |  |  |  |  | 2h |  | 6157 | 1 | 0x03409896
STRCrpalkeGrfs11Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].Stop | [6 empty] | 6157 | 1 | 0x034098a0
STRCrpalkeGrfs11SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[11].SystemFeedback | [6 empty] | 6157 | 1 | 0x034098b0
STRCrpalkeGrfs11SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[11].SystemReference | [6 empty] | 6157 | 1 | 0x034098b1
STRCrpalkeGrfs11TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[11].TemperaturaMotorja | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x034098b2
STRCrpalkeGrfs11UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[11].UreXC200 |  |  |  |  | h | ####.# | 6157 | 1 | 0x034098b3
STRCrpalkeGrfs12AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmActiveCode | [6 empty] | 6157 | 1 | 0x034098b4
STRCrpalkeGrfs12AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].AlarmAktiven | [6 empty] | 6157 | 1 | 0x034098c0
STRCrpalkeGrfs12AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmCodeLog1 | [6 empty] | 6157 | 1 | 0x034098d0
STRCrpalkeGrfs12AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmCodeLog2 | [6 empty] | 6157 | 1 | 0x034098d1
STRCrpalkeGrfs12AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmCodeLog3 | [6 empty] | 6157 | 1 | 0x034098d2
STRCrpalkeGrfs12AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmCodeLog4 | [6 empty] | 6157 | 1 | 0x034098d3
STRCrpalkeGrfs12AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmCodeLog5 | [6 empty] | 6157 | 1 | 0x034098d4
STRCrpalkeGrfs12AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[0] | [6 empty] | 6157 | 1 | 0x034098d5
STRCrpalkeGrfs12AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[10] | [6 empty] | 6157 | 1 | 0x034098d6
STRCrpalkeGrfs12AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[11] | [6 empty] | 6157 | 1 | 0x034098d7
STRCrpalkeGrfs12AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[12] | [6 empty] | 6157 | 1 | 0x034098d8
STRCrpalkeGrfs12AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[13] | [6 empty] | 6157 | 1 | 0x034098d9
STRCrpalkeGrfs12AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[14] | [6 empty] | 6157 | 1 | 0x034098da
STRCrpalkeGrfs12AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[15] | [6 empty] | 6157 | 1 | 0x034098db
STRCrpalkeGrfs12AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[16] | [6 empty] | 6157 | 1 | 0x034098dc
STRCrpalkeGrfs12AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[1] | [6 empty] | 6157 | 1 | 0x034098dd
STRCrpalkeGrfs12AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[2] | [6 empty] | 6157 | 1 | 0x034098de
STRCrpalkeGrfs12AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[3] | [6 empty] | 6157 | 1 | 0x034098df
STRCrpalkeGrfs12AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[4] | [6 empty] | 6157 | 1 | 0x034098e0
STRCrpalkeGrfs12AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[5] | [6 empty] | 6157 | 1 | 0x034098e1
STRCrpalkeGrfs12AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[6] | [6 empty] | 6157 | 1 | 0x034098e2
STRCrpalkeGrfs12AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[7] | [6 empty] | 6157 | 1 | 0x034098e3
STRCrpalkeGrfs12AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[8] | [6 empty] | 6157 | 1 | 0x034098e4
STRCrpalkeGrfs12AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[9] | [6 empty] | 6157 | 1 | 0x034098e5
STRCrpalkeGrfs12AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmQSD1 | [6 empty] | 6157 | 1 | 0x034098e6
STRCrpalkeGrfs12AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmQSD2 | [6 empty] | 6157 | 1 | 0x034098e7
STRCrpalkeGrfs12AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmStart1 | [6 empty] | 6157 | 1 | 0x034098e8
STRCrpalkeGrfs12AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmStart2 | [6 empty] | 6157 | 1 | 0x034098e9
STRCrpalkeGrfs12AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmStop1 | [6 empty] | 6157 | 1 | 0x034098ea
STRCrpalkeGrfs12AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmStop2 | [6 empty] | 6157 | 1 | 0x034098eb
STRCrpalkeGrfs12AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmStop3 | [6 empty] | 6157 | 1 | 0x034098ec
STRCrpalkeGrfs12AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmSurv1 | [6 empty] | 6157 | 1 | 0x034098ed
STRCrpalkeGrfs12AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmSurv2 | [6 empty] | 6157 | 1 | 0x034098ee
STRCrpalkeGrfs12ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[12].ControlSource | [6 empty] | 6157 | 1 | 0x034098ef
STRCrpalkeGrfs12DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[12].DeltaSetPoint | [6 empty] | 6157 | 1 | 0x034098f0
STRCrpalkeGrfs12Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].Deluje | [6 empty] | 6157 | 1 | 0x03409900
STRCrpalkeGrfs12EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[12].EnergijaPoraba |  |  |  |  | kWh | ####.# | 6157 | 1 | 0x03409910
STRCrpalkeGrfs12ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[12].ExternInputSetup | [6 empty] | 6157 | 1 | 0x03409911
STRCrpalkeGrfs12ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[12].ExternInputsStatus | [6 empty] | 6157 | 1 | 0x03409912
STRCrpalkeGrfs12FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[12].FrekPretvornikDCNapetost | 0 | 500 | 0 | 500 | V | ####.# | 6157 | 1 | 0x03409913
STRCrpalkeGrfs12FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[12].FrekPretvornikDCTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409914
STRCrpalkeGrfs12FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[12].FreqMax | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409915
STRCrpalkeGrfs12FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[12].FreqMin | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409916
STRCrpalkeGrfs12FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[12].FreqUpper | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409917
STRCrpalkeGrfs12LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].LocalMode | [6 empty] | 6157 | 1 | 0x03409920
STRCrpalkeGrfs12LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].LocalSetupMode1 | [6 empty] | 6157 | 1 | 0x03409930
STRCrpalkeGrfs12MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[12].MocMax | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x03409931
STRCrpalkeGrfs12MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[12].MocTrenutna | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x03409932
STRCrpalkeGrfs12MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[12].MotorHitrost | 0 | 2500 | 0 | 2500 | obr/min | ####.# | 6157 | 1 | 0x03409933
STRCrpalkeGrfs12MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[12].MotorTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409934
STRCrpalkeGrfs12NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[12].NapajanjeTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409935
STRCrpalkeGrfs12NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[12].NastavitevLokalna | [6 empty] | 6157 | 1 | 0x03409936
STRCrpalkeGrfs12NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[12].NastavitevTrenutna | [6 empty] | 6157 | 1 | 0x03409937
STRCrpalkeGrfs12PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[12].PreklopkaMode | [6 empty] | 6157 | 1 | 0x03409938
STRCrpalkeGrfs12PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[12].PretokMax | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x03409939
STRCrpalkeGrfs12PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[12].PretokMin | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340993a
STRCrpalkeGrfs12PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[12].PretokTrenutni | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340993b
STRCrpalkeGrfs12PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[12].PritiskMax | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340993c
STRCrpalkeGrfs12PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[12].PritiskTrenutni | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340993d
STRCrpalkeGrfs12ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[12].ReferencaMotorjaHzV | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340993e
STRCrpalkeGrfs12ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[12].ReferencaRemote | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340993f
STRCrpalkeGrfs12Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[12].Relay1setup | [6 empty] | 6157 | 1 | 0x03409940
STRCrpalkeGrfs12RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].RemoteON | [6 empty] | 6157 | 1 | 0x03409950
STRCrpalkeGrfs12RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].RemoteSetupMode1 | [6 empty] | 6157 | 1 | 0x03409960
STRCrpalkeGrfs12Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].Reset2handkWhValues | [6 empty] | 6157 | 1 | 0x03409970
STRCrpalkeGrfs12ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].ResetAlarm | [6 empty] | 6157 | 1 | 0x03409980
STRCrpalkeGrfs12ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].ResetAlarmLog | [6 empty] | 6157 | 1 | 0x03409990
STRCrpalkeGrfs12ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].ResetDevice | [6 empty] | 6157 | 1 | 0x034099a0
STRCrpalkeGrfs12SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetAutomatic | [6 empty] | 6157 | 1 | 0x034099b0
STRCrpalkeGrfs12SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetConstFreqMode | [6 empty] | 6157 | 1 | 0x034099c0
STRCrpalkeGrfs12SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetConstPress | [6 empty] | 6157 | 1 | 0x034099d0
STRCrpalkeGrfs12SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetLocalMode | [6 empty] | 6157 | 1 | 0x034099e0
STRCrpalkeGrfs12SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetMaxRunMode | [6 empty] | 6157 | 1 | 0x034099f0
STRCrpalkeGrfs12SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetMinRunMode | [6 empty] | 6157 | 1 | 0x03409a00
STRCrpalkeGrfs12SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetPropPress | [6 empty] | 6157 | 1 | 0x03409a10
STRCrpalkeGrfs12SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetReference | [6 empty] | 6157 | 1 | 0x03409a20
STRCrpalkeGrfs12SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetRemoteMode | [6 empty] | 6157 | 1 | 0x03409a30
STRCrpalkeGrfs12SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetTwinModeAlt | [6 empty] | 6157 | 1 | 0x03409a40
STRCrpalkeGrfs12SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetTwinModeSpare | [6 empty] | 6157 | 1 | 0x03409a50
STRCrpalkeGrfs12SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetTwinModeSync | [6 empty] | 6157 | 1 | 0x03409a60
STRCrpalkeGrfs12Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].Start | [6 empty] | 6157 | 1 | 0x03409a70
STRCrpalkeGrfs12StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeGrfs[12].StatusCrpalke | [6 empty] | 6157 | 1 | 0x03409a80
STRCrpalkeGrfs12StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].StatusMode1 | [6 empty] | 6157 | 1 | 0x03409a81
STRCrpalkeGrfs12StatusMode1co | BYTE | IOD_STR | STR:.CrpalkeGrfs[12].StatusMode1co | [6 empty] | 6157 | 1 | 0x03409a82
STRCrpalkeGrfs12StatusMode1op | BYTE | IOD_STR | STR:.CrpalkeGrfs[12].StatusMode1op | [6 empty] | 6157 | 1 | 0x03409a83
STRCrpalkeGrfs12StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].StatusMode2 | [6 empty] | 6157 | 1 | 0x03409a84
STRCrpalkeGrfs12StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[12].StatusMode3 | [6 empty] | 6157 | 1 | 0x03409a85
STRCrpalkeGrfs12StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[12].StevecUr2h |  |  |  |  | 2h |  | 6157 | 1 | 0x03409a86
STRCrpalkeGrfs12Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].Stop | [6 empty] | 6157 | 1 | 0x03409a90
STRCrpalkeGrfs12SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[12].SystemFeedback | [6 empty] | 6157 | 1 | 0x03409aa0
STRCrpalkeGrfs12SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[12].SystemReference | [6 empty] | 6157 | 1 | 0x03409aa1
STRCrpalkeGrfs12TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[12].TemperaturaMotorja | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x03409aa2
STRCrpalkeGrfs12UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[12].UreXC200 |  |  |  |  | h | ####.# | 6157 | 1 | 0x03409aa3
STRCrpalkeGrfs13AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmActiveCode | [6 empty] | 6157 | 1 | 0x03409aa4
STRCrpalkeGrfs13AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].AlarmAktiven | [6 empty] | 6157 | 1 | 0x03409ab0
STRCrpalkeGrfs13AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmCodeLog1 | [6 empty] | 6157 | 1 | 0x03409ac0
STRCrpalkeGrfs13AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmCodeLog2 | [6 empty] | 6157 | 1 | 0x03409ac1
STRCrpalkeGrfs13AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmCodeLog3 | [6 empty] | 6157 | 1 | 0x03409ac2
STRCrpalkeGrfs13AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmCodeLog4 | [6 empty] | 6157 | 1 | 0x03409ac3
STRCrpalkeGrfs13AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmCodeLog5 | [6 empty] | 6157 | 1 | 0x03409ac4
STRCrpalkeGrfs13AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[0] | [6 empty] | 6157 | 1 | 0x03409ac5
STRCrpalkeGrfs13AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[10] | [6 empty] | 6157 | 1 | 0x03409ac6
STRCrpalkeGrfs13AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[11] | [6 empty] | 6157 | 1 | 0x03409ac7
STRCrpalkeGrfs13AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[12] | [6 empty] | 6157 | 1 | 0x03409ac8
STRCrpalkeGrfs13AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[13] | [6 empty] | 6157 | 1 | 0x03409ac9
STRCrpalkeGrfs13AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[14] | [6 empty] | 6157 | 1 | 0x03409aca
STRCrpalkeGrfs13AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[15] | [6 empty] | 6157 | 1 | 0x03409acb
STRCrpalkeGrfs13AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[16] | [6 empty] | 6157 | 1 | 0x03409acc
STRCrpalkeGrfs13AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[1] | [6 empty] | 6157 | 1 | 0x03409acd
STRCrpalkeGrfs13AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[2] | [6 empty] | 6157 | 1 | 0x03409ace
STRCrpalkeGrfs13AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[3] | [6 empty] | 6157 | 1 | 0x03409acf
STRCrpalkeGrfs13AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[4] | [6 empty] | 6157 | 1 | 0x03409ad0
STRCrpalkeGrfs13AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[5] | [6 empty] | 6157 | 1 | 0x03409ad1
STRCrpalkeGrfs13AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[6] | [6 empty] | 6157 | 1 | 0x03409ad2
STRCrpalkeGrfs13AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[7] | [6 empty] | 6157 | 1 | 0x03409ad3
STRCrpalkeGrfs13AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[8] | [6 empty] | 6157 | 1 | 0x03409ad4
STRCrpalkeGrfs13AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[9] | [6 empty] | 6157 | 1 | 0x03409ad5
STRCrpalkeGrfs13AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmQSD1 | [6 empty] | 6157 | 1 | 0x03409ad6
STRCrpalkeGrfs13AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmQSD2 | [6 empty] | 6157 | 1 | 0x03409ad7
STRCrpalkeGrfs13AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmStart1 | [6 empty] | 6157 | 1 | 0x03409ad8
STRCrpalkeGrfs13AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmStart2 | [6 empty] | 6157 | 1 | 0x03409ad9
STRCrpalkeGrfs13AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmStop1 | [6 empty] | 6157 | 1 | 0x03409ada
STRCrpalkeGrfs13AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmStop2 | [6 empty] | 6157 | 1 | 0x03409adb
STRCrpalkeGrfs13AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmStop3 | [6 empty] | 6157 | 1 | 0x03409adc
STRCrpalkeGrfs13AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmSurv1 | [6 empty] | 6157 | 1 | 0x03409add
STRCrpalkeGrfs13AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmSurv2 | [6 empty] | 6157 | 1 | 0x03409ade
STRCrpalkeGrfs13ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[13].ControlSource | [6 empty] | 6157 | 1 | 0x03409adf
STRCrpalkeGrfs13DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[13].DeltaSetPoint | [6 empty] | 6157 | 1 | 0x03409ae0
STRCrpalkeGrfs13Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].Deluje | [6 empty] | 6157 | 1 | 0x03409af0
STRCrpalkeGrfs13EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[13].EnergijaPoraba |  |  |  |  | kWh | ####.# | 6157 | 1 | 0x03409b00
STRCrpalkeGrfs13ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[13].ExternInputSetup | [6 empty] | 6157 | 1 | 0x03409b01
STRCrpalkeGrfs13ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[13].ExternInputsStatus | [6 empty] | 6157 | 1 | 0x03409b02
STRCrpalkeGrfs13FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[13].FrekPretvornikDCNapetost | 0 | 500 | 0 | 500 | V | ####.# | 6157 | 1 | 0x03409b03
STRCrpalkeGrfs13FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[13].FrekPretvornikDCTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409b04
STRCrpalkeGrfs13FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[13].FreqMax | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409b05
STRCrpalkeGrfs13FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[13].FreqMin | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409b06
STRCrpalkeGrfs13FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[13].FreqUpper | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409b07
STRCrpalkeGrfs13LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].LocalMode | [6 empty] | 6157 | 1 | 0x03409b10
STRCrpalkeGrfs13LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].LocalSetupMode1 | [6 empty] | 6157 | 1 | 0x03409b20
STRCrpalkeGrfs13MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[13].MocMax | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x03409b21
STRCrpalkeGrfs13MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[13].MocTrenutna | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x03409b22
STRCrpalkeGrfs13MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[13].MotorHitrost | 0 | 2500 | 0 | 2500 | obr/min | ####.# | 6157 | 1 | 0x03409b23
STRCrpalkeGrfs13MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[13].MotorTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409b24
STRCrpalkeGrfs13NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[13].NapajanjeTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409b25
STRCrpalkeGrfs13NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[13].NastavitevLokalna | [6 empty] | 6157 | 1 | 0x03409b26
STRCrpalkeGrfs13NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[13].NastavitevTrenutna | [6 empty] | 6157 | 1 | 0x03409b27
STRCrpalkeGrfs13PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[13].PreklopkaMode | [6 empty] | 6157 | 1 | 0x03409b28
STRCrpalkeGrfs13PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[13].PretokMax | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x03409b29
STRCrpalkeGrfs13PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[13].PretokMin | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x03409b2a
STRCrpalkeGrfs13PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[13].PretokTrenutni | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x03409b2b
STRCrpalkeGrfs13PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[13].PritiskMax | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x03409b2c
STRCrpalkeGrfs13PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[13].PritiskTrenutni | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x03409b2d
STRCrpalkeGrfs13ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[13].ReferencaMotorjaHzV | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409b2e
STRCrpalkeGrfs13ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[13].ReferencaRemote | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x03409b2f
STRCrpalkeGrfs13Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[13].Relay1setup | [6 empty] | 6157 | 1 | 0x03409b30
STRCrpalkeGrfs13RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].RemoteON | [6 empty] | 6157 | 1 | 0x03409b40
STRCrpalkeGrfs13RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].RemoteSetupMode1 | [6 empty] | 6157 | 1 | 0x03409b50
STRCrpalkeGrfs13Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].Reset2handkWhValues | [6 empty] | 6157 | 1 | 0x03409b60
STRCrpalkeGrfs13ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].ResetAlarm | [6 empty] | 6157 | 1 | 0x03409b70
STRCrpalkeGrfs13ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].ResetAlarmLog | [6 empty] | 6157 | 1 | 0x03409b80
STRCrpalkeGrfs13ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].ResetDevice | [6 empty] | 6157 | 1 | 0x03409b90
STRCrpalkeGrfs13SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetAutomatic | [6 empty] | 6157 | 1 | 0x03409ba0
STRCrpalkeGrfs13SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetConstFreqMode | [6 empty] | 6157 | 1 | 0x03409bb0
STRCrpalkeGrfs13SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetConstPress | [6 empty] | 6157 | 1 | 0x03409bc0
STRCrpalkeGrfs13SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetLocalMode | [6 empty] | 6157 | 1 | 0x03409bd0
STRCrpalkeGrfs13SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetMaxRunMode | [6 empty] | 6157 | 1 | 0x03409be0
STRCrpalkeGrfs13SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetMinRunMode | [6 empty] | 6157 | 1 | 0x03409bf0
STRCrpalkeGrfs13SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetPropPress | [6 empty] | 6157 | 1 | 0x03409c00
STRCrpalkeGrfs13SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetReference | [6 empty] | 6157 | 1 | 0x03409c10
STRCrpalkeGrfs13SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetRemoteMode | [6 empty] | 6157 | 1 | 0x03409c20
STRCrpalkeGrfs13SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetTwinModeAlt | [6 empty] | 6157 | 1 | 0x03409c30
STRCrpalkeGrfs13SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetTwinModeSpare | [6 empty] | 6157 | 1 | 0x03409c40
STRCrpalkeGrfs13SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetTwinModeSync | [6 empty] | 6157 | 1 | 0x03409c50
STRCrpalkeGrfs13Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].Start | [6 empty] | 6157 | 1 | 0x03409c60
STRCrpalkeGrfs13StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeGrfs[13].StatusCrpalke | [6 empty] | 6157 | 1 | 0x03409c70
STRCrpalkeGrfs13StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].StatusMode1 | [6 empty] | 6157 | 1 | 0x03409c71
STRCrpalkeGrfs13StatusMode1co | BYTE | IOD_STR | STR:.CrpalkeGrfs[13].StatusMode1co | [6 empty] | 6157 | 1 | 0x03409c72
STRCrpalkeGrfs13StatusMode1op | BYTE | IOD_STR | STR:.CrpalkeGrfs[13].StatusMode1op | [6 empty] | 6157 | 1 | 0x03409c73
STRCrpalkeGrfs13StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].StatusMode2 | [6 empty] | 6157 | 1 | 0x03409c74
STRCrpalkeGrfs13StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[13].StatusMode3 | [6 empty] | 6157 | 1 | 0x03409c75
STRCrpalkeGrfs13StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[13].StevecUr2h |  |  |  |  | 2h |  | 6157 | 1 | 0x03409c76
STRCrpalkeGrfs13Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].Stop | [6 empty] | 6157 | 1 | 0x03409c80
STRCrpalkeGrfs13SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[13].SystemFeedback | [6 empty] | 6157 | 1 | 0x03409c90
STRCrpalkeGrfs13SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[13].SystemReference | [6 empty] | 6157 | 1 | 0x03409c91
STRCrpalkeGrfs13TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[13].TemperaturaMotorja | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x03409c92
STRCrpalkeGrfs13UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[13].UreXC200 |  |  |  |  | h | ####.# | 6157 | 1 | 0x03409c93
STRCrpalkeGrfs14AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmActiveCode | [6 empty] | 6157 | 1 | 0x03409c94
STRCrpalkeGrfs14AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].AlarmAktiven | [6 empty] | 6157 | 1 | 0x03409ca0
STRCrpalkeGrfs14AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmCodeLog1 | [6 empty] | 6157 | 1 | 0x03409cb0
STRCrpalkeGrfs14AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmCodeLog2 | [6 empty] | 6157 | 1 | 0x03409cb1
STRCrpalkeGrfs14AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmCodeLog3 | [6 empty] | 6157 | 1 | 0x03409cb2
STRCrpalkeGrfs14AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmCodeLog4 | [6 empty] | 6157 | 1 | 0x03409cb3
STRCrpalkeGrfs14AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmCodeLog5 | [6 empty] | 6157 | 1 | 0x03409cb4
STRCrpalkeGrfs14AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[0] | [6 empty] | 6157 | 1 | 0x03409cb5
STRCrpalkeGrfs14AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[10] | [6 empty] | 6157 | 1 | 0x03409cb6
STRCrpalkeGrfs14AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[11] | [6 empty] | 6157 | 1 | 0x03409cb7
STRCrpalkeGrfs14AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[12] | [6 empty] | 6157 | 1 | 0x03409cb8
STRCrpalkeGrfs14AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[13] | [6 empty] | 6157 | 1 | 0x03409cb9
STRCrpalkeGrfs14AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[14] | [6 empty] | 6157 | 1 | 0x03409cba
STRCrpalkeGrfs14AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[15] | [6 empty] | 6157 | 1 | 0x03409cbb
STRCrpalkeGrfs14AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[16] | [6 empty] | 6157 | 1 | 0x03409cbc
STRCrpalkeGrfs14AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[1] | [6 empty] | 6157 | 1 | 0x03409cbd
STRCrpalkeGrfs14AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[2] | [6 empty] | 6157 | 1 | 0x03409cbe
STRCrpalkeGrfs14AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[3] | [6 empty] | 6157 | 1 | 0x03409cbf
STRCrpalkeGrfs14AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[4] | [6 empty] | 6157 | 1 | 0x03409cc0
STRCrpalkeGrfs14AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[5] | [6 empty] | 6157 | 1 | 0x03409cc1
STRCrpalkeGrfs14AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[6] | [6 empty] | 6157 | 1 | 0x03409cc2
STRCrpalkeGrfs14AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[7] | [6 empty] | 6157 | 1 | 0x03409cc3
STRCrpalkeGrfs14AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[8] | [6 empty] | 6157 | 1 | 0x03409cc4
STRCrpalkeGrfs14AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[9] | [6 empty] | 6157 | 1 | 0x03409cc5
STRCrpalkeGrfs14AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmQSD1 | [6 empty] | 6157 | 1 | 0x03409cc6
STRCrpalkeGrfs14AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmQSD2 | [6 empty] | 6157 | 1 | 0x03409cc7
STRCrpalkeGrfs14AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmStart1 | [6 empty] | 6157 | 1 | 0x03409cc8
STRCrpalkeGrfs14AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmStart2 | [6 empty] | 6157 | 1 | 0x03409cc9
STRCrpalkeGrfs14AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmStop1 | [6 empty] | 6157 | 1 | 0x03409cca
STRCrpalkeGrfs14AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmStop2 | [6 empty] | 6157 | 1 | 0x03409ccb
STRCrpalkeGrfs14AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmStop3 | [6 empty] | 6157 | 1 | 0x03409ccc
STRCrpalkeGrfs14AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmSurv1 | [6 empty] | 6157 | 1 | 0x03409ccd
STRCrpalkeGrfs14AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmSurv2 | [6 empty] | 6157 | 1 | 0x03409cce
STRCrpalkeGrfs14ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[14].ControlSource | [6 empty] | 6157 | 1 | 0x03409ccf
STRCrpalkeGrfs14DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[14].DeltaSetPoint | [6 empty] | 6157 | 1 | 0x03409cd0
STRCrpalkeGrfs14Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].Deluje | [6 empty] | 6157 | 1 | 0x03409ce0
STRCrpalkeGrfs14EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[14].EnergijaPoraba |  |  |  |  | kWh | ####.# | 6157 | 1 | 0x03409cf0
STRCrpalkeGrfs14ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[14].ExternInputSetup | [6 empty] | 6157 | 1 | 0x03409cf1
STRCrpalkeGrfs14ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[14].ExternInputsStatus | [6 empty] | 6157 | 1 | 0x03409cf2
STRCrpalkeGrfs14FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[14].FrekPretvornikDCNapetost | 0 | 500 | 0 | 500 | V | ####.# | 6157 | 1 | 0x03409cf3
STRCrpalkeGrfs14FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[14].FrekPretvornikDCTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409cf4
STRCrpalkeGrfs14FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[14].FreqMax | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409cf5
STRCrpalkeGrfs14FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[14].FreqMin | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409cf6
STRCrpalkeGrfs14FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[14].FreqUpper | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409cf7
STRCrpalkeGrfs14LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].LocalMode | [6 empty] | 6157 | 1 | 0x03409d00
STRCrpalkeGrfs14LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].LocalSetupMode1 | [6 empty] | 6157 | 1 | 0x03409d10
STRCrpalkeGrfs14MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[14].MocMax | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x03409d11
STRCrpalkeGrfs14MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[14].MocTrenutna | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x03409d12
STRCrpalkeGrfs14MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[14].MotorHitrost | 0 | 2500 | 0 | 2500 | obr/min | ####.# | 6157 | 1 | 0x03409d13
STRCrpalkeGrfs14MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[14].MotorTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409d14
STRCrpalkeGrfs14NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[14].NapajanjeTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409d15
STRCrpalkeGrfs14NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[14].NastavitevLokalna | [6 empty] | 6157 | 1 | 0x03409d16
STRCrpalkeGrfs14NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[14].NastavitevTrenutna | [6 empty] | 6157 | 1 | 0x03409d17
STRCrpalkeGrfs14PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[14].PreklopkaMode | [6 empty] | 6157 | 1 | 0x03409d18
STRCrpalkeGrfs14PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[14].PretokMax | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x03409d19
STRCrpalkeGrfs14PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[14].PretokMin | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x03409d1a
STRCrpalkeGrfs14PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[14].PretokTrenutni | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x03409d1b
STRCrpalkeGrfs14PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[14].PritiskMax | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x03409d1c
STRCrpalkeGrfs14PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[14].PritiskTrenutni | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x03409d1d
STRCrpalkeGrfs14ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[14].ReferencaMotorjaHzV | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409d1e
STRCrpalkeGrfs14ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[14].ReferencaRemote | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x03409d1f
STRCrpalkeGrfs14Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[14].Relay1setup | [6 empty] | 6157 | 1 | 0x03409d20
STRCrpalkeGrfs14RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].RemoteON | [6 empty] | 6157 | 1 | 0x03409d30
STRCrpalkeGrfs14RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].RemoteSetupMode1 | [6 empty] | 6157 | 1 | 0x03409d40
STRCrpalkeGrfs14Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].Reset2handkWhValues | [6 empty] | 6157 | 1 | 0x03409d50
STRCrpalkeGrfs14ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].ResetAlarm | [6 empty] | 6157 | 1 | 0x03409d60
STRCrpalkeGrfs14ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].ResetAlarmLog | [6 empty] | 6157 | 1 | 0x03409d70
STRCrpalkeGrfs14ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].ResetDevice | [6 empty] | 6157 | 1 | 0x03409d80
STRCrpalkeGrfs14SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetAutomatic | [6 empty] | 6157 | 1 | 0x03409d90
STRCrpalkeGrfs14SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetConstFreqMode | [6 empty] | 6157 | 1 | 0x03409da0
STRCrpalkeGrfs14SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetConstPress | [6 empty] | 6157 | 1 | 0x03409db0
STRCrpalkeGrfs14SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetLocalMode | [6 empty] | 6157 | 1 | 0x03409dc0
STRCrpalkeGrfs14SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetMaxRunMode | [6 empty] | 6157 | 1 | 0x03409dd0
STRCrpalkeGrfs14SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetMinRunMode | [6 empty] | 6157 | 1 | 0x03409de0
STRCrpalkeGrfs14SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetPropPress | [6 empty] | 6157 | 1 | 0x03409df0
STRCrpalkeGrfs14SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetReference | [6 empty] | 6157 | 1 | 0x03409e00
STRCrpalkeGrfs14SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetRemoteMode | [6 empty] | 6157 | 1 | 0x03409e10
STRCrpalkeGrfs14SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetTwinModeAlt | [6 empty] | 6157 | 1 | 0x03409e20
STRCrpalkeGrfs14SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetTwinModeSpare | [6 empty] | 6157 | 1 | 0x03409e30
STRCrpalkeGrfs14SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetTwinModeSync | [6 empty] | 6157 | 1 | 0x03409e40
STRCrpalkeGrfs14Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].Start | [6 empty] | 6157 | 1 | 0x03409e50
STRCrpalkeGrfs14StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeGrfs[14].StatusCrpalke | [6 empty] | 6157 | 1 | 0x03409e60
STRCrpalkeGrfs14StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].StatusMode1 | [6 empty] | 6157 | 1 | 0x03409e61
STRCrpalkeGrfs14StatusMode1co | BYTE | IOD_STR | STR:.CrpalkeGrfs[14].StatusMode1co | [6 empty] | 6157 | 1 | 0x03409e62
STRCrpalkeGrfs14StatusMode1op | BYTE | IOD_STR | STR:.CrpalkeGrfs[14].StatusMode1op | [6 empty] | 6157 | 1 | 0x03409e63
STRCrpalkeGrfs14StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].StatusMode2 | [6 empty] | 6157 | 1 | 0x03409e64
STRCrpalkeGrfs14StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[14].StatusMode3 | [6 empty] | 6157 | 1 | 0x03409e65
STRCrpalkeGrfs14StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[14].StevecUr2h |  |  |  |  | 2h |  | 6157 | 1 | 0x03409e66
STRCrpalkeGrfs14Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].Stop | [6 empty] | 6157 | 1 | 0x03409e70
STRCrpalkeGrfs14SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[14].SystemFeedback | [6 empty] | 6157 | 1 | 0x03409e80
STRCrpalkeGrfs14SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[14].SystemReference | [6 empty] | 6157 | 1 | 0x03409e81
STRCrpalkeGrfs14TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[14].TemperaturaMotorja | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x03409e82
STRCrpalkeGrfs14UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[14].UreXC200 |  |  |  |  | h | ####.# | 6157 | 1 | 0x03409e83
STRCrpalkeGrfs1AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmActiveCode | [6 empty] | 6157 | 1 | 0x03409e84
STRCrpalkeGrfs1AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].AlarmAktiven | [6 empty] | 6157 | 1 | 0x03409e90
STRCrpalkeGrfs1AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmCodeLog1 | [6 empty] | 6157 | 1 | 0x03409ea0
STRCrpalkeGrfs1AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmCodeLog2 | [6 empty] | 6157 | 1 | 0x03409ea1
STRCrpalkeGrfs1AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmCodeLog3 | [6 empty] | 6157 | 1 | 0x03409ea2
STRCrpalkeGrfs1AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmCodeLog4 | [6 empty] | 6157 | 1 | 0x03409ea3
STRCrpalkeGrfs1AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmCodeLog5 | [6 empty] | 6157 | 1 | 0x03409ea4
STRCrpalkeGrfs1AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[0] | [6 empty] | 6157 | 1 | 0x03409ea5
STRCrpalkeGrfs1AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[10] | [6 empty] | 6157 | 1 | 0x03409ea6
STRCrpalkeGrfs1AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[11] | [6 empty] | 6157 | 1 | 0x03409ea7
STRCrpalkeGrfs1AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[12] | [6 empty] | 6157 | 1 | 0x03409ea8
STRCrpalkeGrfs1AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[13] | [6 empty] | 6157 | 1 | 0x03409ea9
STRCrpalkeGrfs1AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[14] | [6 empty] | 6157 | 1 | 0x03409eaa
STRCrpalkeGrfs1AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[15] | [6 empty] | 6157 | 1 | 0x03409eab
STRCrpalkeGrfs1AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[16] | [6 empty] | 6157 | 1 | 0x03409eac
STRCrpalkeGrfs1AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[1] | [6 empty] | 6157 | 1 | 0x03409ead
STRCrpalkeGrfs1AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[2] | [6 empty] | 6157 | 1 | 0x03409eae
STRCrpalkeGrfs1AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[3] | [6 empty] | 6157 | 1 | 0x03409eaf
STRCrpalkeGrfs1AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[4] | [6 empty] | 6157 | 1 | 0x03409eb0
STRCrpalkeGrfs1AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[5] | [6 empty] | 6157 | 1 | 0x03409eb1
STRCrpalkeGrfs1AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[6] | [6 empty] | 6157 | 1 | 0x03409eb2
STRCrpalkeGrfs1AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[7] | [6 empty] | 6157 | 1 | 0x03409eb3
STRCrpalkeGrfs1AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[8] | [6 empty] | 6157 | 1 | 0x03409eb4
STRCrpalkeGrfs1AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[9] | [6 empty] | 6157 | 1 | 0x03409eb5
STRCrpalkeGrfs1AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmQSD1 | [6 empty] | 6157 | 1 | 0x03409eb6
STRCrpalkeGrfs1AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmQSD2 | [6 empty] | 6157 | 1 | 0x03409eb7
STRCrpalkeGrfs1AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmStart1 | [6 empty] | 6157 | 1 | 0x03409eb8
STRCrpalkeGrfs1AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmStart2 | [6 empty] | 6157 | 1 | 0x03409eb9
STRCrpalkeGrfs1AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmStop1 | [6 empty] | 6157 | 1 | 0x03409eba
STRCrpalkeGrfs1AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmStop2 | [6 empty] | 6157 | 1 | 0x03409ebb
STRCrpalkeGrfs1AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmStop3 | [6 empty] | 6157 | 1 | 0x03409ebc
STRCrpalkeGrfs1AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmSurv1 | [6 empty] | 6157 | 1 | 0x03409ebd
STRCrpalkeGrfs1AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmSurv2 | [6 empty] | 6157 | 1 | 0x03409ebe
STRCrpalkeGrfs1ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[1].ControlSource | [6 empty] | 6157 | 1 | 0x03409ebf
STRCrpalkeGrfs1DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[1].DeltaSetPoint | [6 empty] | 6157 | 1 | 0x03409ec0
STRCrpalkeGrfs1Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].Deluje | [6 empty] | 6157 | 1 | 0x03409ed0
STRCrpalkeGrfs1EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[1].EnergijaPoraba |  |  |  |  | kWh | ####.# | 6157 | 1 | 0x03409ee0
STRCrpalkeGrfs1ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[1].ExternInputSetup | [6 empty] | 6157 | 1 | 0x03409ee1
STRCrpalkeGrfs1ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[1].ExternInputsStatus | [6 empty] | 6157 | 1 | 0x03409ee2
STRCrpalkeGrfs1FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[1].FrekPretvornikDCNapetost | 0 | 500 | 0 | 500 | V | ####.# | 6157 | 1 | 0x03409ee3
STRCrpalkeGrfs1FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[1].FrekPretvornikDCTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409ee4
STRCrpalkeGrfs1FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[1].FreqMax | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409ee5
STRCrpalkeGrfs1FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[1].FreqMin | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409ee6
STRCrpalkeGrfs1FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[1].FreqUpper | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409ee7
STRCrpalkeGrfs1LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].LocalMode | [6 empty] | 6157 | 1 | 0x03409ef0
STRCrpalkeGrfs1LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].LocalSetupMode1 | [6 empty] | 6157 | 1 | 0x03409f00
STRCrpalkeGrfs1MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[1].MocMax | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x03409f01
STRCrpalkeGrfs1MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[1].MocTrenutna | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x03409f02
STRCrpalkeGrfs1MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[1].MotorHitrost | 0 | 2500 | 0 | 2500 | obr/min | ####.# | 6157 | 1 | 0x03409f03
STRCrpalkeGrfs1MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[1].MotorTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409f04
STRCrpalkeGrfs1NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[1].NapajanjeTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x03409f05
STRCrpalkeGrfs1NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[1].NastavitevLokalna | [6 empty] | 6157 | 1 | 0x03409f06
STRCrpalkeGrfs1NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[1].NastavitevTrenutna | [6 empty] | 6157 | 1 | 0x03409f07
STRCrpalkeGrfs1PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[1].PreklopkaMode | [6 empty] | 6157 | 1 | 0x03409f08
STRCrpalkeGrfs1PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[1].PretokMax | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x03409f09
STRCrpalkeGrfs1PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[1].PretokMin | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x03409f0a
STRCrpalkeGrfs1PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[1].PretokTrenutni | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x03409f0b
STRCrpalkeGrfs1PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[1].PritiskMax | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x03409f0c
STRCrpalkeGrfs1PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[1].PritiskTrenutni | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x03409f0d
STRCrpalkeGrfs1ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[1].ReferencaMotorjaHzV | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x03409f0e
STRCrpalkeGrfs1ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[1].ReferencaRemote | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x03409f0f
STRCrpalkeGrfs1Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[1].Relay1setup | [6 empty] | 6157 | 1 | 0x03409f10
STRCrpalkeGrfs1RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].RemoteON | [6 empty] | 6157 | 1 | 0x03409f20
STRCrpalkeGrfs1RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].RemoteSetupMode1 | [6 empty] | 6157 | 1 | 0x03409f30
STRCrpalkeGrfs1Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].Reset2handkWhValues | [6 empty] | 6157 | 1 | 0x03409f40
STRCrpalkeGrfs1ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].ResetAlarm | [6 empty] | 6157 | 1 | 0x03409f50
STRCrpalkeGrfs1ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].ResetAlarmLog | [6 empty] | 6157 | 1 | 0x03409f60
STRCrpalkeGrfs1ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].ResetDevice | [6 empty] | 6157 | 1 | 0x03409f70
STRCrpalkeGrfs1SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetAutomatic | [6 empty] | 6157 | 1 | 0x03409f80
STRCrpalkeGrfs1SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetConstFreqMode | [6 empty] | 6157 | 1 | 0x03409f90
STRCrpalkeGrfs1SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetConstPress | [6 empty] | 6157 | 1 | 0x03409fa0
STRCrpalkeGrfs1SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetLocalMode | [6 empty] | 6157 | 1 | 0x03409fb0
STRCrpalkeGrfs1SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetMaxRunMode | [6 empty] | 6157 | 1 | 0x03409fc0
STRCrpalkeGrfs1SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetMinRunMode | [6 empty] | 6157 | 1 | 0x03409fd0
STRCrpalkeGrfs1SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetPropPress | [6 empty] | 6157 | 1 | 0x03409fe0
STRCrpalkeGrfs1SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetReference | [6 empty] | 6157 | 1 | 0x03409ff0
STRCrpalkeGrfs1SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetRemoteMode | [6 empty] | 6157 | 1 | 0x0340a000
STRCrpalkeGrfs1SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetTwinModeAlt | [6 empty] | 6157 | 1 | 0x0340a010
STRCrpalkeGrfs1SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetTwinModeSpare | [6 empty] | 6157 | 1 | 0x0340a020
STRCrpalkeGrfs1SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetTwinModeSync | [6 empty] | 6157 | 1 | 0x0340a030
STRCrpalkeGrfs1Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].Start | [6 empty] | 6157 | 1 | 0x0340a040
STRCrpalkeGrfs1StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeGrfs[1].StatusCrpalke | [6 empty] | 6157 | 1 | 0x0340a050
STRCrpalkeGrfs1StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].StatusMode1 | [6 empty] | 6157 | 1 | 0x0340a051
STRCrpalkeGrfs1StatusMode1co | BYTE | IOD_STR | STR:.CrpalkeGrfs[1].StatusMode1co | [6 empty] | 6157 | 1 | 0x0340a052
STRCrpalkeGrfs1StatusMode1op | BYTE | IOD_STR | STR:.CrpalkeGrfs[1].StatusMode1op | [6 empty] | 6157 | 1 | 0x0340a053
STRCrpalkeGrfs1StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].StatusMode2 | [6 empty] | 6157 | 1 | 0x0340a054
STRCrpalkeGrfs1StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[1].StatusMode3 | [6 empty] | 6157 | 1 | 0x0340a055
STRCrpalkeGrfs1StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[1].StevecUr2h |  |  |  |  | 2h |  | 6157 | 1 | 0x0340a056
STRCrpalkeGrfs1Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].Stop | [6 empty] | 6157 | 1 | 0x0340a060
STRCrpalkeGrfs1SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[1].SystemFeedback | [6 empty] | 6157 | 1 | 0x0340a070
STRCrpalkeGrfs1SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[1].SystemReference | [6 empty] | 6157 | 1 | 0x0340a071
STRCrpalkeGrfs1TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[1].TemperaturaMotorja | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x0340a072
STRCrpalkeGrfs1UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[1].UreXC200 |  |  |  |  | h | ####.# | 6157 | 1 | 0x0340a073
STRCrpalkeGrfs2AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmActiveCode | [6 empty] | 6157 | 1 | 0x0340a074
STRCrpalkeGrfs2AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].AlarmAktiven | [6 empty] | 6157 | 1 | 0x0340a080
STRCrpalkeGrfs2AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmCodeLog1 | [6 empty] | 6157 | 1 | 0x0340a090
STRCrpalkeGrfs2AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmCodeLog2 | [6 empty] | 6157 | 1 | 0x0340a091
STRCrpalkeGrfs2AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmCodeLog3 | [6 empty] | 6157 | 1 | 0x0340a092
STRCrpalkeGrfs2AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmCodeLog4 | [6 empty] | 6157 | 1 | 0x0340a093
STRCrpalkeGrfs2AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmCodeLog5 | [6 empty] | 6157 | 1 | 0x0340a094
STRCrpalkeGrfs2AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[0] | [6 empty] | 6157 | 1 | 0x0340a095
STRCrpalkeGrfs2AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[10] | [6 empty] | 6157 | 1 | 0x0340a096
STRCrpalkeGrfs2AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[11] | [6 empty] | 6157 | 1 | 0x0340a097
STRCrpalkeGrfs2AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[12] | [6 empty] | 6157 | 1 | 0x0340a098
STRCrpalkeGrfs2AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[13] | [6 empty] | 6157 | 1 | 0x0340a099
STRCrpalkeGrfs2AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[14] | [6 empty] | 6157 | 1 | 0x0340a09a
STRCrpalkeGrfs2AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[15] | [6 empty] | 6157 | 1 | 0x0340a09b
STRCrpalkeGrfs2AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[16] | [6 empty] | 6157 | 1 | 0x0340a09c
STRCrpalkeGrfs2AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[1] | [6 empty] | 6157 | 1 | 0x0340a09d
STRCrpalkeGrfs2AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[2] | [6 empty] | 6157 | 1 | 0x0340a09e
STRCrpalkeGrfs2AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[3] | [6 empty] | 6157 | 1 | 0x0340a09f
STRCrpalkeGrfs2AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[4] | [6 empty] | 6157 | 1 | 0x0340a0a0
STRCrpalkeGrfs2AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[5] | [6 empty] | 6157 | 1 | 0x0340a0a1
STRCrpalkeGrfs2AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[6] | [6 empty] | 6157 | 1 | 0x0340a0a2
STRCrpalkeGrfs2AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[7] | [6 empty] | 6157 | 1 | 0x0340a0a3
STRCrpalkeGrfs2AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[8] | [6 empty] | 6157 | 1 | 0x0340a0a4
STRCrpalkeGrfs2AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[9] | [6 empty] | 6157 | 1 | 0x0340a0a5
STRCrpalkeGrfs2AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmQSD1 | [6 empty] | 6157 | 1 | 0x0340a0a6
STRCrpalkeGrfs2AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmQSD2 | [6 empty] | 6157 | 1 | 0x0340a0a7
STRCrpalkeGrfs2AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmStart1 | [6 empty] | 6157 | 1 | 0x0340a0a8
STRCrpalkeGrfs2AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmStart2 | [6 empty] | 6157 | 1 | 0x0340a0a9
STRCrpalkeGrfs2AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmStop1 | [6 empty] | 6157 | 1 | 0x0340a0aa
STRCrpalkeGrfs2AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmStop2 | [6 empty] | 6157 | 1 | 0x0340a0ab
STRCrpalkeGrfs2AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmStop3 | [6 empty] | 6157 | 1 | 0x0340a0ac
STRCrpalkeGrfs2AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmSurv1 | [6 empty] | 6157 | 1 | 0x0340a0ad
STRCrpalkeGrfs2AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmSurv2 | [6 empty] | 6157 | 1 | 0x0340a0ae
STRCrpalkeGrfs2ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[2].ControlSource | [6 empty] | 6157 | 1 | 0x0340a0af
STRCrpalkeGrfs2DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[2].DeltaSetPoint | [6 empty] | 6157 | 1 | 0x0340a0b0
STRCrpalkeGrfs2Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].Deluje | [6 empty] | 6157 | 1 | 0x0340a0c0
STRCrpalkeGrfs2EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[2].EnergijaPoraba |  |  |  |  | kWh | ####.# | 6157 | 1 | 0x0340a0d0
STRCrpalkeGrfs2ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[2].ExternInputSetup | [6 empty] | 6157 | 1 | 0x0340a0d1
STRCrpalkeGrfs2ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[2].ExternInputsStatus | [6 empty] | 6157 | 1 | 0x0340a0d2
STRCrpalkeGrfs2FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[2].FrekPretvornikDCNapetost | 0 | 500 | 0 | 500 | V | ####.# | 6157 | 1 | 0x0340a0d3
STRCrpalkeGrfs2FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[2].FrekPretvornikDCTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340a0d4
STRCrpalkeGrfs2FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[2].FreqMax | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a0d5
STRCrpalkeGrfs2FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[2].FreqMin | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a0d6
STRCrpalkeGrfs2FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[2].FreqUpper | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a0d7
STRCrpalkeGrfs2LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].LocalMode | [6 empty] | 6157 | 1 | 0x0340a0e0
STRCrpalkeGrfs2LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].LocalSetupMode1 | [6 empty] | 6157 | 1 | 0x0340a0f0
STRCrpalkeGrfs2MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[2].MocMax | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x0340a0f1
STRCrpalkeGrfs2MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[2].MocTrenutna | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x0340a0f2
STRCrpalkeGrfs2MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[2].MotorHitrost | 0 | 2500 | 0 | 2500 | obr/min | ####.# | 6157 | 1 | 0x0340a0f3
STRCrpalkeGrfs2MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[2].MotorTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340a0f4
STRCrpalkeGrfs2NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[2].NapajanjeTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340a0f5
STRCrpalkeGrfs2NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[2].NastavitevLokalna | [6 empty] | 6157 | 1 | 0x0340a0f6
STRCrpalkeGrfs2NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[2].NastavitevTrenutna | [6 empty] | 6157 | 1 | 0x0340a0f7
STRCrpalkeGrfs2PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[2].PreklopkaMode | [6 empty] | 6157 | 1 | 0x0340a0f8
STRCrpalkeGrfs2PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[2].PretokMax | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340a0f9
STRCrpalkeGrfs2PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[2].PretokMin | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340a0fa
STRCrpalkeGrfs2PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[2].PretokTrenutni | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340a0fb
STRCrpalkeGrfs2PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[2].PritiskMax | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340a0fc
STRCrpalkeGrfs2PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[2].PritiskTrenutni | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340a0fd
STRCrpalkeGrfs2ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[2].ReferencaMotorjaHzV | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a0fe
STRCrpalkeGrfs2ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[2].ReferencaRemote | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340a0ff
STRCrpalkeGrfs2Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[2].Relay1setup | [6 empty] | 6157 | 1 | 0x0340a100
STRCrpalkeGrfs2RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].RemoteON | [6 empty] | 6157 | 1 | 0x0340a110
STRCrpalkeGrfs2RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].RemoteSetupMode1 | [6 empty] | 6157 | 1 | 0x0340a120
STRCrpalkeGrfs2Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].Reset2handkWhValues | [6 empty] | 6157 | 1 | 0x0340a130
STRCrpalkeGrfs2ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].ResetAlarm | [6 empty] | 6157 | 1 | 0x0340a140
STRCrpalkeGrfs2ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].ResetAlarmLog | [6 empty] | 6157 | 1 | 0x0340a150
STRCrpalkeGrfs2ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].ResetDevice | [6 empty] | 6157 | 1 | 0x0340a160
STRCrpalkeGrfs2SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetAutomatic | [6 empty] | 6157 | 1 | 0x0340a170
STRCrpalkeGrfs2SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetConstFreqMode | [6 empty] | 6157 | 1 | 0x0340a180
STRCrpalkeGrfs2SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetConstPress | [6 empty] | 6157 | 1 | 0x0340a190
STRCrpalkeGrfs2SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetLocalMode | [6 empty] | 6157 | 1 | 0x0340a1a0
STRCrpalkeGrfs2SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetMaxRunMode | [6 empty] | 6157 | 1 | 0x0340a1b0
STRCrpalkeGrfs2SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetMinRunMode | [6 empty] | 6157 | 1 | 0x0340a1c0
STRCrpalkeGrfs2SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetPropPress | [6 empty] | 6157 | 1 | 0x0340a1d0
STRCrpalkeGrfs2SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetReference | [6 empty] | 6157 | 1 | 0x0340a1e0
STRCrpalkeGrfs2SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetRemoteMode | [6 empty] | 6157 | 1 | 0x0340a1f0
STRCrpalkeGrfs2SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetTwinModeAlt | [6 empty] | 6157 | 1 | 0x0340a200
STRCrpalkeGrfs2SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetTwinModeSpare | [6 empty] | 6157 | 1 | 0x0340a210
STRCrpalkeGrfs2SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetTwinModeSync | [6 empty] | 6157 | 1 | 0x0340a220
STRCrpalkeGrfs2Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].Start | [6 empty] | 6157 | 1 | 0x0340a230
STRCrpalkeGrfs2StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeGrfs[2].StatusCrpalke | [6 empty] | 6157 | 1 | 0x0340a240
STRCrpalkeGrfs2StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].StatusMode1 | [6 empty] | 6157 | 1 | 0x0340a241
STRCrpalkeGrfs2StatusMode1co | BYTE | IOD_STR | STR:.CrpalkeGrfs[2].StatusMode1co | [6 empty] | 6157 | 1 | 0x0340a242
STRCrpalkeGrfs2StatusMode1op | BYTE | IOD_STR | STR:.CrpalkeGrfs[2].StatusMode1op | [6 empty] | 6157 | 1 | 0x0340a243
STRCrpalkeGrfs2StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].StatusMode2 | [6 empty] | 6157 | 1 | 0x0340a244
STRCrpalkeGrfs2StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[2].StatusMode3 | [6 empty] | 6157 | 1 | 0x0340a245
STRCrpalkeGrfs2StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[2].StevecUr2h |  |  |  |  | 2h |  | 6157 | 1 | 0x0340a246
STRCrpalkeGrfs2Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].Stop | [6 empty] | 6157 | 1 | 0x0340a250
STRCrpalkeGrfs2SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[2].SystemFeedback | [6 empty] | 6157 | 1 | 0x0340a260
STRCrpalkeGrfs2SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[2].SystemReference | [6 empty] | 6157 | 1 | 0x0340a261
STRCrpalkeGrfs2TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[2].TemperaturaMotorja | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x0340a262
STRCrpalkeGrfs2UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[2].UreXC200 |  |  |  |  | h | ####.# | 6157 | 1 | 0x0340a263
STRCrpalkeGrfs3AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmActiveCode | [6 empty] | 6157 | 1 | 0x0340a264
STRCrpalkeGrfs3AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].AlarmAktiven | [6 empty] | 6157 | 1 | 0x0340a270
STRCrpalkeGrfs3AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmCodeLog1 | [6 empty] | 6157 | 1 | 0x0340a280
STRCrpalkeGrfs3AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmCodeLog2 | [6 empty] | 6157 | 1 | 0x0340a281
STRCrpalkeGrfs3AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmCodeLog3 | [6 empty] | 6157 | 1 | 0x0340a282
STRCrpalkeGrfs3AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmCodeLog4 | [6 empty] | 6157 | 1 | 0x0340a283
STRCrpalkeGrfs3AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmCodeLog5 | [6 empty] | 6157 | 1 | 0x0340a284
STRCrpalkeGrfs3AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[0] | [6 empty] | 6157 | 1 | 0x0340a285
STRCrpalkeGrfs3AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[10] | [6 empty] | 6157 | 1 | 0x0340a286
STRCrpalkeGrfs3AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[11] | [6 empty] | 6157 | 1 | 0x0340a287
STRCrpalkeGrfs3AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[12] | [6 empty] | 6157 | 1 | 0x0340a288
STRCrpalkeGrfs3AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[13] | [6 empty] | 6157 | 1 | 0x0340a289
STRCrpalkeGrfs3AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[14] | [6 empty] | 6157 | 1 | 0x0340a28a
STRCrpalkeGrfs3AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[15] | [6 empty] | 6157 | 1 | 0x0340a28b
STRCrpalkeGrfs3AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[16] | [6 empty] | 6157 | 1 | 0x0340a28c
STRCrpalkeGrfs3AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[1] | [6 empty] | 6157 | 1 | 0x0340a28d
STRCrpalkeGrfs3AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[2] | [6 empty] | 6157 | 1 | 0x0340a28e
STRCrpalkeGrfs3AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[3] | [6 empty] | 6157 | 1 | 0x0340a28f
STRCrpalkeGrfs3AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[4] | [6 empty] | 6157 | 1 | 0x0340a290
STRCrpalkeGrfs3AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[5] | [6 empty] | 6157 | 1 | 0x0340a291
STRCrpalkeGrfs3AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[6] | [6 empty] | 6157 | 1 | 0x0340a292
STRCrpalkeGrfs3AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[7] | [6 empty] | 6157 | 1 | 0x0340a293
STRCrpalkeGrfs3AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[8] | [6 empty] | 6157 | 1 | 0x0340a294
STRCrpalkeGrfs3AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[9] | [6 empty] | 6157 | 1 | 0x0340a295
STRCrpalkeGrfs3AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmQSD1 | [6 empty] | 6157 | 1 | 0x0340a296
STRCrpalkeGrfs3AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmQSD2 | [6 empty] | 6157 | 1 | 0x0340a297
STRCrpalkeGrfs3AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmStart1 | [6 empty] | 6157 | 1 | 0x0340a298
STRCrpalkeGrfs3AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmStart2 | [6 empty] | 6157 | 1 | 0x0340a299
STRCrpalkeGrfs3AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmStop1 | [6 empty] | 6157 | 1 | 0x0340a29a
STRCrpalkeGrfs3AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmStop2 | [6 empty] | 6157 | 1 | 0x0340a29b
STRCrpalkeGrfs3AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmStop3 | [6 empty] | 6157 | 1 | 0x0340a29c
STRCrpalkeGrfs3AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmSurv1 | [6 empty] | 6157 | 1 | 0x0340a29d
STRCrpalkeGrfs3AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmSurv2 | [6 empty] | 6157 | 1 | 0x0340a29e
STRCrpalkeGrfs3ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[3].ControlSource | [6 empty] | 6157 | 1 | 0x0340a29f
STRCrpalkeGrfs3DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[3].DeltaSetPoint | [6 empty] | 6157 | 1 | 0x0340a2a0
STRCrpalkeGrfs3Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].Deluje | [6 empty] | 6157 | 1 | 0x0340a2b0
STRCrpalkeGrfs3EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[3].EnergijaPoraba |  |  |  |  | kWh | ####.# | 6157 | 1 | 0x0340a2c0
STRCrpalkeGrfs3ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[3].ExternInputSetup | [6 empty] | 6157 | 1 | 0x0340a2c1
STRCrpalkeGrfs3ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[3].ExternInputsStatus | [6 empty] | 6157 | 1 | 0x0340a2c2
STRCrpalkeGrfs3FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[3].FrekPretvornikDCNapetost | 0 | 500 | 0 | 500 | V | ####.# | 6157 | 1 | 0x0340a2c3
STRCrpalkeGrfs3FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[3].FrekPretvornikDCTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340a2c4
STRCrpalkeGrfs3FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[3].FreqMax | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a2c5
STRCrpalkeGrfs3FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[3].FreqMin | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a2c6
STRCrpalkeGrfs3FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[3].FreqUpper | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a2c7
STRCrpalkeGrfs3LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].LocalMode | [6 empty] | 6157 | 1 | 0x0340a2d0
STRCrpalkeGrfs3LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].LocalSetupMode1 | [6 empty] | 6157 | 1 | 0x0340a2e0
STRCrpalkeGrfs3MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[3].MocMax | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x0340a2e1
STRCrpalkeGrfs3MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[3].MocTrenutna | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x0340a2e2
STRCrpalkeGrfs3MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[3].MotorHitrost | 0 | 2500 | 0 | 2500 | obr/min | ####.# | 6157 | 1 | 0x0340a2e3
STRCrpalkeGrfs3MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[3].MotorTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340a2e4
STRCrpalkeGrfs3NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[3].NapajanjeTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340a2e5
STRCrpalkeGrfs3NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[3].NastavitevLokalna | [6 empty] | 6157 | 1 | 0x0340a2e6
STRCrpalkeGrfs3NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[3].NastavitevTrenutna | [6 empty] | 6157 | 1 | 0x0340a2e7
STRCrpalkeGrfs3PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[3].PreklopkaMode | [6 empty] | 6157 | 1 | 0x0340a2e8
STRCrpalkeGrfs3PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[3].PretokMax | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340a2e9
STRCrpalkeGrfs3PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[3].PretokMin | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340a2ea
STRCrpalkeGrfs3PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[3].PretokTrenutni | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340a2eb
STRCrpalkeGrfs3PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[3].PritiskMax | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340a2ec
STRCrpalkeGrfs3PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[3].PritiskTrenutni | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340a2ed
STRCrpalkeGrfs3ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[3].ReferencaMotorjaHzV | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a2ee
STRCrpalkeGrfs3ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[3].ReferencaRemote | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340a2ef
STRCrpalkeGrfs3Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[3].Relay1setup | [6 empty] | 6157 | 1 | 0x0340a2f0
STRCrpalkeGrfs3RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].RemoteON | [6 empty] | 6157 | 1 | 0x0340a300
STRCrpalkeGrfs3RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].RemoteSetupMode1 | [6 empty] | 6157 | 1 | 0x0340a310
STRCrpalkeGrfs3Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].Reset2handkWhValues | [6 empty] | 6157 | 1 | 0x0340a320
STRCrpalkeGrfs3ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].ResetAlarm | [6 empty] | 6157 | 1 | 0x0340a330
STRCrpalkeGrfs3ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].ResetAlarmLog | [6 empty] | 6157 | 1 | 0x0340a340
STRCrpalkeGrfs3ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].ResetDevice | [6 empty] | 6157 | 1 | 0x0340a350
STRCrpalkeGrfs3SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetAutomatic | [6 empty] | 6157 | 1 | 0x0340a360
STRCrpalkeGrfs3SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetConstFreqMode | [6 empty] | 6157 | 1 | 0x0340a370
STRCrpalkeGrfs3SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetConstPress | [6 empty] | 6157 | 1 | 0x0340a380
STRCrpalkeGrfs3SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetLocalMode | [6 empty] | 6157 | 1 | 0x0340a390
STRCrpalkeGrfs3SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetMaxRunMode | [6 empty] | 6157 | 1 | 0x0340a3a0
STRCrpalkeGrfs3SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetMinRunMode | [6 empty] | 6157 | 1 | 0x0340a3b0
STRCrpalkeGrfs3SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetPropPress | [6 empty] | 6157 | 1 | 0x0340a3c0
STRCrpalkeGrfs3SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetReference | [6 empty] | 6157 | 1 | 0x0340a3d0
STRCrpalkeGrfs3SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetRemoteMode | [6 empty] | 6157 | 1 | 0x0340a3e0
STRCrpalkeGrfs3SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetTwinModeAlt | [6 empty] | 6157 | 1 | 0x0340a3f0
STRCrpalkeGrfs3SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetTwinModeSpare | [6 empty] | 6157 | 1 | 0x0340a400
STRCrpalkeGrfs3SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetTwinModeSync | [6 empty] | 6157 | 1 | 0x0340a410
STRCrpalkeGrfs3Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].Start | [6 empty] | 6157 | 1 | 0x0340a420
STRCrpalkeGrfs3StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeGrfs[3].StatusCrpalke | [6 empty] | 6157 | 1 | 0x0340a430
STRCrpalkeGrfs3StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].StatusMode1 | [6 empty] | 6157 | 1 | 0x0340a431
STRCrpalkeGrfs3StatusMode1co | BYTE | IOD_STR | STR:.CrpalkeGrfs[3].StatusMode1co | [6 empty] | 6157 | 1 | 0x0340a432
STRCrpalkeGrfs3StatusMode1op | BYTE | IOD_STR | STR:.CrpalkeGrfs[3].StatusMode1op | [6 empty] | 6157 | 1 | 0x0340a433
STRCrpalkeGrfs3StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].StatusMode2 | [6 empty] | 6157 | 1 | 0x0340a434
STRCrpalkeGrfs3StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[3].StatusMode3 | [6 empty] | 6157 | 1 | 0x0340a435
STRCrpalkeGrfs3StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[3].StevecUr2h |  |  |  |  | 2h |  | 6157 | 1 | 0x0340a436
STRCrpalkeGrfs3Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].Stop | [6 empty] | 6157 | 1 | 0x0340a440
STRCrpalkeGrfs3SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[3].SystemFeedback | [6 empty] | 6157 | 1 | 0x0340a450
STRCrpalkeGrfs3SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[3].SystemReference | [6 empty] | 6157 | 1 | 0x0340a451
STRCrpalkeGrfs3TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[3].TemperaturaMotorja | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x0340a452
STRCrpalkeGrfs3UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[3].UreXC200 |  |  |  |  | h | ####.# | 6157 | 1 | 0x0340a453
STRCrpalkeGrfs4AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmActiveCode | [6 empty] | 6157 | 1 | 0x0340a454
STRCrpalkeGrfs4AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].AlarmAktiven | [6 empty] | 6157 | 1 | 0x0340a460
STRCrpalkeGrfs4AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmCodeLog1 | [6 empty] | 6157 | 1 | 0x0340a470
STRCrpalkeGrfs4AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmCodeLog2 | [6 empty] | 6157 | 1 | 0x0340a471
STRCrpalkeGrfs4AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmCodeLog3 | [6 empty] | 6157 | 1 | 0x0340a472
STRCrpalkeGrfs4AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmCodeLog4 | [6 empty] | 6157 | 1 | 0x0340a473
STRCrpalkeGrfs4AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmCodeLog5 | [6 empty] | 6157 | 1 | 0x0340a474
STRCrpalkeGrfs4AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[0] | [6 empty] | 6157 | 1 | 0x0340a475
STRCrpalkeGrfs4AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[10] | [6 empty] | 6157 | 1 | 0x0340a476
STRCrpalkeGrfs4AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[11] | [6 empty] | 6157 | 1 | 0x0340a477
STRCrpalkeGrfs4AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[12] | [6 empty] | 6157 | 1 | 0x0340a478
STRCrpalkeGrfs4AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[13] | [6 empty] | 6157 | 1 | 0x0340a479
STRCrpalkeGrfs4AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[14] | [6 empty] | 6157 | 1 | 0x0340a47a
STRCrpalkeGrfs4AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[15] | [6 empty] | 6157 | 1 | 0x0340a47b
STRCrpalkeGrfs4AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[16] | [6 empty] | 6157 | 1 | 0x0340a47c
STRCrpalkeGrfs4AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[1] | [6 empty] | 6157 | 1 | 0x0340a47d
STRCrpalkeGrfs4AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[2] | [6 empty] | 6157 | 1 | 0x0340a47e
STRCrpalkeGrfs4AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[3] | [6 empty] | 6157 | 1 | 0x0340a47f
STRCrpalkeGrfs4AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[4] | [6 empty] | 6157 | 1 | 0x0340a480
STRCrpalkeGrfs4AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[5] | [6 empty] | 6157 | 1 | 0x0340a481
STRCrpalkeGrfs4AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[6] | [6 empty] | 6157 | 1 | 0x0340a482
STRCrpalkeGrfs4AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[7] | [6 empty] | 6157 | 1 | 0x0340a483
STRCrpalkeGrfs4AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[8] | [6 empty] | 6157 | 1 | 0x0340a484
STRCrpalkeGrfs4AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[9] | [6 empty] | 6157 | 1 | 0x0340a485
STRCrpalkeGrfs4AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmQSD1 | [6 empty] | 6157 | 1 | 0x0340a486
STRCrpalkeGrfs4AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmQSD2 | [6 empty] | 6157 | 1 | 0x0340a487
STRCrpalkeGrfs4AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmStart1 | [6 empty] | 6157 | 1 | 0x0340a488
STRCrpalkeGrfs4AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmStart2 | [6 empty] | 6157 | 1 | 0x0340a489
STRCrpalkeGrfs4AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmStop1 | [6 empty] | 6157 | 1 | 0x0340a48a
STRCrpalkeGrfs4AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmStop2 | [6 empty] | 6157 | 1 | 0x0340a48b
STRCrpalkeGrfs4AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmStop3 | [6 empty] | 6157 | 1 | 0x0340a48c
STRCrpalkeGrfs4AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmSurv1 | [6 empty] | 6157 | 1 | 0x0340a48d
STRCrpalkeGrfs4AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmSurv2 | [6 empty] | 6157 | 1 | 0x0340a48e
STRCrpalkeGrfs4ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[4].ControlSource | [6 empty] | 6157 | 1 | 0x0340a48f
STRCrpalkeGrfs4DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[4].DeltaSetPoint | [6 empty] | 6157 | 1 | 0x0340a490
STRCrpalkeGrfs4Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].Deluje | [6 empty] | 6157 | 1 | 0x0340a4a0
STRCrpalkeGrfs4EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[4].EnergijaPoraba |  |  |  |  | kWh | ####.# | 6157 | 1 | 0x0340a4b0
STRCrpalkeGrfs4ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[4].ExternInputSetup | [6 empty] | 6157 | 1 | 0x0340a4b1
STRCrpalkeGrfs4ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[4].ExternInputsStatus | [6 empty] | 6157 | 1 | 0x0340a4b2
STRCrpalkeGrfs4FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[4].FrekPretvornikDCNapetost | 0 | 500 | 0 | 500 | V | ####.# | 6157 | 1 | 0x0340a4b3
STRCrpalkeGrfs4FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[4].FrekPretvornikDCTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340a4b4
STRCrpalkeGrfs4FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[4].FreqMax | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a4b5
STRCrpalkeGrfs4FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[4].FreqMin | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a4b6
STRCrpalkeGrfs4FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[4].FreqUpper | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a4b7
STRCrpalkeGrfs4LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].LocalMode | [6 empty] | 6157 | 1 | 0x0340a4c0
STRCrpalkeGrfs4LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].LocalSetupMode1 | [6 empty] | 6157 | 1 | 0x0340a4d0
STRCrpalkeGrfs4MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[4].MocMax | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x0340a4d1
STRCrpalkeGrfs4MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[4].MocTrenutna | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x0340a4d2
STRCrpalkeGrfs4MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[4].MotorHitrost | 0 | 2500 | 0 | 2500 | obr/min | ####.# | 6157 | 1 | 0x0340a4d3
STRCrpalkeGrfs4MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[4].MotorTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340a4d4
STRCrpalkeGrfs4NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[4].NapajanjeTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340a4d5
STRCrpalkeGrfs4NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[4].NastavitevLokalna | [6 empty] | 6157 | 1 | 0x0340a4d6
STRCrpalkeGrfs4NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[4].NastavitevTrenutna | [6 empty] | 6157 | 1 | 0x0340a4d7
STRCrpalkeGrfs4PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[4].PreklopkaMode | [6 empty] | 6157 | 1 | 0x0340a4d8
STRCrpalkeGrfs4PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[4].PretokMax | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340a4d9
STRCrpalkeGrfs4PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[4].PretokMin | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340a4da
STRCrpalkeGrfs4PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[4].PretokTrenutni | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340a4db
STRCrpalkeGrfs4PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[4].PritiskMax | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340a4dc
STRCrpalkeGrfs4PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[4].PritiskTrenutni | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340a4dd
STRCrpalkeGrfs4ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[4].ReferencaMotorjaHzV | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a4de
STRCrpalkeGrfs4ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[4].ReferencaRemote | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340a4df
STRCrpalkeGrfs4Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[4].Relay1setup | [6 empty] | 6157 | 1 | 0x0340a4e0
STRCrpalkeGrfs4RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].RemoteON | [6 empty] | 6157 | 1 | 0x0340a4f0
STRCrpalkeGrfs4RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].RemoteSetupMode1 | [6 empty] | 6157 | 1 | 0x0340a500
STRCrpalkeGrfs4Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].Reset2handkWhValues | [6 empty] | 6157 | 1 | 0x0340a510
STRCrpalkeGrfs4ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].ResetAlarm | [6 empty] | 6157 | 1 | 0x0340a520
STRCrpalkeGrfs4ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].ResetAlarmLog | [6 empty] | 6157 | 1 | 0x0340a530
STRCrpalkeGrfs4ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].ResetDevice | [6 empty] | 6157 | 1 | 0x0340a540
STRCrpalkeGrfs4SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetAutomatic | [6 empty] | 6157 | 1 | 0x0340a550
STRCrpalkeGrfs4SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetConstFreqMode | [6 empty] | 6157 | 1 | 0x0340a560
STRCrpalkeGrfs4SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetConstPress | [6 empty] | 6157 | 1 | 0x0340a570
STRCrpalkeGrfs4SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetLocalMode | [6 empty] | 6157 | 1 | 0x0340a580
STRCrpalkeGrfs4SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetMaxRunMode | [6 empty] | 6157 | 1 | 0x0340a590
STRCrpalkeGrfs4SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetMinRunMode | [6 empty] | 6157 | 1 | 0x0340a5a0
STRCrpalkeGrfs4SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetPropPress | [6 empty] | 6157 | 1 | 0x0340a5b0
STRCrpalkeGrfs4SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetReference | [6 empty] | 6157 | 1 | 0x0340a5c0
STRCrpalkeGrfs4SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetRemoteMode | [6 empty] | 6157 | 1 | 0x0340a5d0
STRCrpalkeGrfs4SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetTwinModeAlt | [6 empty] | 6157 | 1 | 0x0340a5e0
STRCrpalkeGrfs4SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetTwinModeSpare | [6 empty] | 6157 | 1 | 0x0340a5f0
STRCrpalkeGrfs4SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetTwinModeSync | [6 empty] | 6157 | 1 | 0x0340a600
STRCrpalkeGrfs4Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].Start | [6 empty] | 6157 | 1 | 0x0340a610
STRCrpalkeGrfs4StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeGrfs[4].StatusCrpalke | [6 empty] | 6157 | 1 | 0x0340a620
STRCrpalkeGrfs4StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].StatusMode1 | [6 empty] | 6157 | 1 | 0x0340a621
STRCrpalkeGrfs4StatusMode1co | BYTE | IOD_STR | STR:.CrpalkeGrfs[4].StatusMode1co | [6 empty] | 6157 | 1 | 0x0340a622
STRCrpalkeGrfs4StatusMode1op | BYTE | IOD_STR | STR:.CrpalkeGrfs[4].StatusMode1op | [6 empty] | 6157 | 1 | 0x0340a623
STRCrpalkeGrfs4StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].StatusMode2 | [6 empty] | 6157 | 1 | 0x0340a624
STRCrpalkeGrfs4StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[4].StatusMode3 | [6 empty] | 6157 | 1 | 0x0340a625
STRCrpalkeGrfs4StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[4].StevecUr2h |  |  |  |  | 2h |  | 6157 | 1 | 0x0340a626
STRCrpalkeGrfs4Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].Stop | [6 empty] | 6157 | 1 | 0x0340a630
STRCrpalkeGrfs4SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[4].SystemFeedback | [6 empty] | 6157 | 1 | 0x0340a640
STRCrpalkeGrfs4SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[4].SystemReference | [6 empty] | 6157 | 1 | 0x0340a641
STRCrpalkeGrfs4TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[4].TemperaturaMotorja | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x0340a642
STRCrpalkeGrfs4UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[4].UreXC200 |  |  |  |  | h | ####.# | 6157 | 1 | 0x0340a643
STRCrpalkeGrfs5AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmActiveCode | [6 empty] | 6157 | 1 | 0x0340a644
STRCrpalkeGrfs5AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].AlarmAktiven | [6 empty] | 6157 | 1 | 0x0340a650
STRCrpalkeGrfs5AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmCodeLog1 | [6 empty] | 6157 | 1 | 0x0340a660
STRCrpalkeGrfs5AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmCodeLog2 | [6 empty] | 6157 | 1 | 0x0340a661
STRCrpalkeGrfs5AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmCodeLog3 | [6 empty] | 6157 | 1 | 0x0340a662
STRCrpalkeGrfs5AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmCodeLog4 | [6 empty] | 6157 | 1 | 0x0340a663
STRCrpalkeGrfs5AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmCodeLog5 | [6 empty] | 6157 | 1 | 0x0340a664
STRCrpalkeGrfs5AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[0] | [6 empty] | 6157 | 1 | 0x0340a665
STRCrpalkeGrfs5AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[10] | [6 empty] | 6157 | 1 | 0x0340a666
STRCrpalkeGrfs5AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[11] | [6 empty] | 6157 | 1 | 0x0340a667
STRCrpalkeGrfs5AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[12] | [6 empty] | 6157 | 1 | 0x0340a668
STRCrpalkeGrfs5AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[13] | [6 empty] | 6157 | 1 | 0x0340a669
STRCrpalkeGrfs5AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[14] | [6 empty] | 6157 | 1 | 0x0340a66a
STRCrpalkeGrfs5AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[15] | [6 empty] | 6157 | 1 | 0x0340a66b
STRCrpalkeGrfs5AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[16] | [6 empty] | 6157 | 1 | 0x0340a66c
STRCrpalkeGrfs5AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[1] | [6 empty] | 6157 | 1 | 0x0340a66d
STRCrpalkeGrfs5AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[2] | [6 empty] | 6157 | 1 | 0x0340a66e
STRCrpalkeGrfs5AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[3] | [6 empty] | 6157 | 1 | 0x0340a66f
STRCrpalkeGrfs5AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[4] | [6 empty] | 6157 | 1 | 0x0340a670
STRCrpalkeGrfs5AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[5] | [6 empty] | 6157 | 1 | 0x0340a671
STRCrpalkeGrfs5AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[6] | [6 empty] | 6157 | 1 | 0x0340a672
STRCrpalkeGrfs5AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[7] | [6 empty] | 6157 | 1 | 0x0340a673
STRCrpalkeGrfs5AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[8] | [6 empty] | 6157 | 1 | 0x0340a674
STRCrpalkeGrfs5AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[9] | [6 empty] | 6157 | 1 | 0x0340a675
STRCrpalkeGrfs5AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmQSD1 | [6 empty] | 6157 | 1 | 0x0340a676
STRCrpalkeGrfs5AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmQSD2 | [6 empty] | 6157 | 1 | 0x0340a677
STRCrpalkeGrfs5AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmStart1 | [6 empty] | 6157 | 1 | 0x0340a678
STRCrpalkeGrfs5AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmStart2 | [6 empty] | 6157 | 1 | 0x0340a679
STRCrpalkeGrfs5AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmStop1 | [6 empty] | 6157 | 1 | 0x0340a67a
STRCrpalkeGrfs5AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmStop2 | [6 empty] | 6157 | 1 | 0x0340a67b
STRCrpalkeGrfs5AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmStop3 | [6 empty] | 6157 | 1 | 0x0340a67c
STRCrpalkeGrfs5AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmSurv1 | [6 empty] | 6157 | 1 | 0x0340a67d
STRCrpalkeGrfs5AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmSurv2 | [6 empty] | 6157 | 1 | 0x0340a67e
STRCrpalkeGrfs5ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[5].ControlSource | [6 empty] | 6157 | 1 | 0x0340a67f
STRCrpalkeGrfs5DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[5].DeltaSetPoint | [6 empty] | 6157 | 1 | 0x0340a680
STRCrpalkeGrfs5Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].Deluje | [6 empty] | 6157 | 1 | 0x0340a690
STRCrpalkeGrfs5EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[5].EnergijaPoraba |  |  |  |  | kWh | ####.# | 6157 | 1 | 0x0340a6a0
STRCrpalkeGrfs5ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[5].ExternInputSetup | [6 empty] | 6157 | 1 | 0x0340a6a1
STRCrpalkeGrfs5ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[5].ExternInputsStatus | [6 empty] | 6157 | 1 | 0x0340a6a2
STRCrpalkeGrfs5FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[5].FrekPretvornikDCNapetost | 0 | 500 | 0 | 500 | V | ####.# | 6157 | 1 | 0x0340a6a3
STRCrpalkeGrfs5FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[5].FrekPretvornikDCTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340a6a4
STRCrpalkeGrfs5FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[5].FreqMax | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a6a5
STRCrpalkeGrfs5FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[5].FreqMin | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a6a6
STRCrpalkeGrfs5FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[5].FreqUpper | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a6a7
STRCrpalkeGrfs5LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].LocalMode | [6 empty] | 6157 | 1 | 0x0340a6b0
STRCrpalkeGrfs5LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].LocalSetupMode1 | [6 empty] | 6157 | 1 | 0x0340a6c0
STRCrpalkeGrfs5MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[5].MocMax | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x0340a6c1
STRCrpalkeGrfs5MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[5].MocTrenutna | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x0340a6c2
STRCrpalkeGrfs5MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[5].MotorHitrost | 0 | 2500 | 0 | 2500 | obr/min | ####.# | 6157 | 1 | 0x0340a6c3
STRCrpalkeGrfs5MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[5].MotorTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340a6c4
STRCrpalkeGrfs5NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[5].NapajanjeTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340a6c5
STRCrpalkeGrfs5NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[5].NastavitevLokalna | [6 empty] | 6157 | 1 | 0x0340a6c6
STRCrpalkeGrfs5NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[5].NastavitevTrenutna | [6 empty] | 6157 | 1 | 0x0340a6c7
STRCrpalkeGrfs5PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[5].PreklopkaMode | [6 empty] | 6157 | 1 | 0x0340a6c8
STRCrpalkeGrfs5PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[5].PretokMax | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340a6c9
STRCrpalkeGrfs5PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[5].PretokMin | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340a6ca
STRCrpalkeGrfs5PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[5].PretokTrenutni | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340a6cb
STRCrpalkeGrfs5PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[5].PritiskMax | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340a6cc
STRCrpalkeGrfs5PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[5].PritiskTrenutni | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340a6cd
STRCrpalkeGrfs5ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[5].ReferencaMotorjaHzV | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a6ce
STRCrpalkeGrfs5ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[5].ReferencaRemote | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340a6cf
STRCrpalkeGrfs5Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[5].Relay1setup | [6 empty] | 6157 | 1 | 0x0340a6d0
STRCrpalkeGrfs5RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].RemoteON | [6 empty] | 6157 | 1 | 0x0340a6e0
STRCrpalkeGrfs5RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].RemoteSetupMode1 | [6 empty] | 6157 | 1 | 0x0340a6f0
STRCrpalkeGrfs5Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].Reset2handkWhValues | [6 empty] | 6157 | 1 | 0x0340a700
STRCrpalkeGrfs5ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].ResetAlarm | [6 empty] | 6157 | 1 | 0x0340a710
STRCrpalkeGrfs5ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].ResetAlarmLog | [6 empty] | 6157 | 1 | 0x0340a720
STRCrpalkeGrfs5ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].ResetDevice | [6 empty] | 6157 | 1 | 0x0340a730
STRCrpalkeGrfs5SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetAutomatic | [6 empty] | 6157 | 1 | 0x0340a740
STRCrpalkeGrfs5SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetConstFreqMode | [6 empty] | 6157 | 1 | 0x0340a750
STRCrpalkeGrfs5SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetConstPress | [6 empty] | 6157 | 1 | 0x0340a760
STRCrpalkeGrfs5SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetLocalMode | [6 empty] | 6157 | 1 | 0x0340a770
STRCrpalkeGrfs5SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetMaxRunMode | [6 empty] | 6157 | 1 | 0x0340a780
STRCrpalkeGrfs5SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetMinRunMode | [6 empty] | 6157 | 1 | 0x0340a790
STRCrpalkeGrfs5SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetPropPress | [6 empty] | 6157 | 1 | 0x0340a7a0
STRCrpalkeGrfs5SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetReference | [6 empty] | 6157 | 1 | 0x0340a7b0
STRCrpalkeGrfs5SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetRemoteMode | [6 empty] | 6157 | 1 | 0x0340a7c0
STRCrpalkeGrfs5SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetTwinModeAlt | [6 empty] | 6157 | 1 | 0x0340a7d0
STRCrpalkeGrfs5SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetTwinModeSpare | [6 empty] | 6157 | 1 | 0x0340a7e0
STRCrpalkeGrfs5SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetTwinModeSync | [6 empty] | 6157 | 1 | 0x0340a7f0
STRCrpalkeGrfs5Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].Start | [6 empty] | 6157 | 1 | 0x0340a800
STRCrpalkeGrfs5StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeGrfs[5].StatusCrpalke | [6 empty] | 6157 | 1 | 0x0340a810
STRCrpalkeGrfs5StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].StatusMode1 | [6 empty] | 6157 | 1 | 0x0340a811
STRCrpalkeGrfs5StatusMode1co | BYTE | IOD_STR | STR:.CrpalkeGrfs[5].StatusMode1co | [6 empty] | 6157 | 1 | 0x0340a812
STRCrpalkeGrfs5StatusMode1op | BYTE | IOD_STR | STR:.CrpalkeGrfs[5].StatusMode1op | [6 empty] | 6157 | 1 | 0x0340a813
STRCrpalkeGrfs5StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].StatusMode2 | [6 empty] | 6157 | 1 | 0x0340a814
STRCrpalkeGrfs5StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[5].StatusMode3 | [6 empty] | 6157 | 1 | 0x0340a815
STRCrpalkeGrfs5StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[5].StevecUr2h |  |  |  |  | 2h |  | 6157 | 1 | 0x0340a816
STRCrpalkeGrfs5Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].Stop | [6 empty] | 6157 | 1 | 0x0340a820
STRCrpalkeGrfs5SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[5].SystemFeedback | [6 empty] | 6157 | 1 | 0x0340a830
STRCrpalkeGrfs5SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[5].SystemReference | [6 empty] | 6157 | 1 | 0x0340a831
STRCrpalkeGrfs5TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[5].TemperaturaMotorja | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x0340a832
STRCrpalkeGrfs5UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[5].UreXC200 |  |  |  |  | h | ####.# | 6157 | 1 | 0x0340a833
STRCrpalkeGrfs6AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmActiveCode | [6 empty] | 6157 | 1 | 0x0340a834
STRCrpalkeGrfs6AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].AlarmAktiven | [6 empty] | 6157 | 1 | 0x0340a840
STRCrpalkeGrfs6AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmCodeLog1 | [6 empty] | 6157 | 1 | 0x0340a850
STRCrpalkeGrfs6AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmCodeLog2 | [6 empty] | 6157 | 1 | 0x0340a851
STRCrpalkeGrfs6AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmCodeLog3 | [6 empty] | 6157 | 1 | 0x0340a852
STRCrpalkeGrfs6AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmCodeLog4 | [6 empty] | 6157 | 1 | 0x0340a853
STRCrpalkeGrfs6AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmCodeLog5 | [6 empty] | 6157 | 1 | 0x0340a854
STRCrpalkeGrfs6AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[0] | [6 empty] | 6157 | 1 | 0x0340a855
STRCrpalkeGrfs6AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[10] | [6 empty] | 6157 | 1 | 0x0340a856
STRCrpalkeGrfs6AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[11] | [6 empty] | 6157 | 1 | 0x0340a857
STRCrpalkeGrfs6AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[12] | [6 empty] | 6157 | 1 | 0x0340a858
STRCrpalkeGrfs6AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[13] | [6 empty] | 6157 | 1 | 0x0340a859
STRCrpalkeGrfs6AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[14] | [6 empty] | 6157 | 1 | 0x0340a85a
STRCrpalkeGrfs6AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[15] | [6 empty] | 6157 | 1 | 0x0340a85b
STRCrpalkeGrfs6AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[16] | [6 empty] | 6157 | 1 | 0x0340a85c
STRCrpalkeGrfs6AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[1] | [6 empty] | 6157 | 1 | 0x0340a85d
STRCrpalkeGrfs6AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[2] | [6 empty] | 6157 | 1 | 0x0340a85e
STRCrpalkeGrfs6AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[3] | [6 empty] | 6157 | 1 | 0x0340a85f
STRCrpalkeGrfs6AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[4] | [6 empty] | 6157 | 1 | 0x0340a860
STRCrpalkeGrfs6AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[5] | [6 empty] | 6157 | 1 | 0x0340a861
STRCrpalkeGrfs6AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[6] | [6 empty] | 6157 | 1 | 0x0340a862
STRCrpalkeGrfs6AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[7] | [6 empty] | 6157 | 1 | 0x0340a863
STRCrpalkeGrfs6AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[8] | [6 empty] | 6157 | 1 | 0x0340a864
STRCrpalkeGrfs6AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[9] | [6 empty] | 6157 | 1 | 0x0340a865
STRCrpalkeGrfs6AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmQSD1 | [6 empty] | 6157 | 1 | 0x0340a866
STRCrpalkeGrfs6AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmQSD2 | [6 empty] | 6157 | 1 | 0x0340a867
STRCrpalkeGrfs6AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmStart1 | [6 empty] | 6157 | 1 | 0x0340a868
STRCrpalkeGrfs6AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmStart2 | [6 empty] | 6157 | 1 | 0x0340a869
STRCrpalkeGrfs6AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmStop1 | [6 empty] | 6157 | 1 | 0x0340a86a
STRCrpalkeGrfs6AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmStop2 | [6 empty] | 6157 | 1 | 0x0340a86b
STRCrpalkeGrfs6AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmStop3 | [6 empty] | 6157 | 1 | 0x0340a86c
STRCrpalkeGrfs6AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmSurv1 | [6 empty] | 6157 | 1 | 0x0340a86d
STRCrpalkeGrfs6AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmSurv2 | [6 empty] | 6157 | 1 | 0x0340a86e
STRCrpalkeGrfs6ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[6].ControlSource | [6 empty] | 6157 | 1 | 0x0340a86f
STRCrpalkeGrfs6DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[6].DeltaSetPoint | [6 empty] | 6157 | 1 | 0x0340a870
STRCrpalkeGrfs6Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].Deluje | [6 empty] | 6157 | 1 | 0x0340a880
STRCrpalkeGrfs6EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[6].EnergijaPoraba |  |  |  |  | kWh | ####.# | 6157 | 1 | 0x0340a890
STRCrpalkeGrfs6ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[6].ExternInputSetup | [6 empty] | 6157 | 1 | 0x0340a891
STRCrpalkeGrfs6ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[6].ExternInputsStatus | [6 empty] | 6157 | 1 | 0x0340a892
STRCrpalkeGrfs6FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[6].FrekPretvornikDCNapetost | 0 | 500 | 0 | 500 | V | ####.# | 6157 | 1 | 0x0340a893
STRCrpalkeGrfs6FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[6].FrekPretvornikDCTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340a894
STRCrpalkeGrfs6FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[6].FreqMax | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a895
STRCrpalkeGrfs6FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[6].FreqMin | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a896
STRCrpalkeGrfs6FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[6].FreqUpper | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a897
STRCrpalkeGrfs6LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].LocalMode | [6 empty] | 6157 | 1 | 0x0340a8a0
STRCrpalkeGrfs6LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].LocalSetupMode1 | [6 empty] | 6157 | 1 | 0x0340a8b0
STRCrpalkeGrfs6MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[6].MocMax | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x0340a8b1
STRCrpalkeGrfs6MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[6].MocTrenutna | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x0340a8b2
STRCrpalkeGrfs6MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[6].MotorHitrost | 0 | 2500 | 0 | 2500 | obr/min | ####.# | 6157 | 1 | 0x0340a8b3
STRCrpalkeGrfs6MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[6].MotorTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340a8b4
STRCrpalkeGrfs6NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[6].NapajanjeTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340a8b5
STRCrpalkeGrfs6NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[6].NastavitevLokalna | [6 empty] | 6157 | 1 | 0x0340a8b6
STRCrpalkeGrfs6NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[6].NastavitevTrenutna | [6 empty] | 6157 | 1 | 0x0340a8b7
STRCrpalkeGrfs6PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[6].PreklopkaMode | [6 empty] | 6157 | 1 | 0x0340a8b8
STRCrpalkeGrfs6PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[6].PretokMax | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340a8b9
STRCrpalkeGrfs6PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[6].PretokMin | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340a8ba
STRCrpalkeGrfs6PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[6].PretokTrenutni | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340a8bb
STRCrpalkeGrfs6PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[6].PritiskMax | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340a8bc
STRCrpalkeGrfs6PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[6].PritiskTrenutni | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340a8bd
STRCrpalkeGrfs6ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[6].ReferencaMotorjaHzV | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340a8be
STRCrpalkeGrfs6ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[6].ReferencaRemote | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340a8bf
STRCrpalkeGrfs6Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[6].Relay1setup | [6 empty] | 6157 | 1 | 0x0340a8c0
STRCrpalkeGrfs6RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].RemoteON | [6 empty] | 6157 | 1 | 0x0340a8d0
STRCrpalkeGrfs6RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].RemoteSetupMode1 | [6 empty] | 6157 | 1 | 0x0340a8e0
STRCrpalkeGrfs6Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].Reset2handkWhValues | [6 empty] | 6157 | 1 | 0x0340a8f0
STRCrpalkeGrfs6ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].ResetAlarm | [6 empty] | 6157 | 1 | 0x0340a900
STRCrpalkeGrfs6ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].ResetAlarmLog | [6 empty] | 6157 | 1 | 0x0340a910
STRCrpalkeGrfs6ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].ResetDevice | [6 empty] | 6157 | 1 | 0x0340a920
STRCrpalkeGrfs6SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetAutomatic | [6 empty] | 6157 | 1 | 0x0340a930
STRCrpalkeGrfs6SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetConstFreqMode | [6 empty] | 6157 | 1 | 0x0340a940
STRCrpalkeGrfs6SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetConstPress | [6 empty] | 6157 | 1 | 0x0340a950
STRCrpalkeGrfs6SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetLocalMode | [6 empty] | 6157 | 1 | 0x0340a960
STRCrpalkeGrfs6SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetMaxRunMode | [6 empty] | 6157 | 1 | 0x0340a970
STRCrpalkeGrfs6SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetMinRunMode | [6 empty] | 6157 | 1 | 0x0340a980
STRCrpalkeGrfs6SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetPropPress | [6 empty] | 6157 | 1 | 0x0340a990
STRCrpalkeGrfs6SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetReference | [6 empty] | 6157 | 1 | 0x0340a9a0
STRCrpalkeGrfs6SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetRemoteMode | [6 empty] | 6157 | 1 | 0x0340a9b0
STRCrpalkeGrfs6SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetTwinModeAlt | [6 empty] | 6157 | 1 | 0x0340a9c0
STRCrpalkeGrfs6SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetTwinModeSpare | [6 empty] | 6157 | 1 | 0x0340a9d0
STRCrpalkeGrfs6SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetTwinModeSync | [6 empty] | 6157 | 1 | 0x0340a9e0
STRCrpalkeGrfs6Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].Start | [6 empty] | 6157 | 1 | 0x0340a9f0
STRCrpalkeGrfs6StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeGrfs[6].StatusCrpalke | [6 empty] | 6157 | 1 | 0x0340aa00
STRCrpalkeGrfs6StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].StatusMode1 | [6 empty] | 6157 | 1 | 0x0340aa01
STRCrpalkeGrfs6StatusMode1co | BYTE | IOD_STR | STR:.CrpalkeGrfs[6].StatusMode1co | [6 empty] | 6157 | 1 | 0x0340aa02
STRCrpalkeGrfs6StatusMode1op | BYTE | IOD_STR | STR:.CrpalkeGrfs[6].StatusMode1op | [6 empty] | 6157 | 1 | 0x0340aa03
STRCrpalkeGrfs6StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].StatusMode2 | [6 empty] | 6157 | 1 | 0x0340aa04
STRCrpalkeGrfs6StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[6].StatusMode3 | [6 empty] | 6157 | 1 | 0x0340aa05
STRCrpalkeGrfs6StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[6].StevecUr2h |  |  |  |  | 2h |  | 6157 | 1 | 0x0340aa06
STRCrpalkeGrfs6Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].Stop | [6 empty] | 6157 | 1 | 0x0340aa10
STRCrpalkeGrfs6SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[6].SystemFeedback | [6 empty] | 6157 | 1 | 0x0340aa20
STRCrpalkeGrfs6SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[6].SystemReference | [6 empty] | 6157 | 1 | 0x0340aa21
STRCrpalkeGrfs6TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[6].TemperaturaMotorja | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x0340aa22
STRCrpalkeGrfs6UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[6].UreXC200 |  |  |  |  | h | ####.# | 6157 | 1 | 0x0340aa23
STRCrpalkeGrfs7AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmActiveCode | [6 empty] | 6157 | 1 | 0x0340aa24
STRCrpalkeGrfs7AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].AlarmAktiven | [6 empty] | 6157 | 1 | 0x0340aa30
STRCrpalkeGrfs7AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmCodeLog1 | [6 empty] | 6157 | 1 | 0x0340aa40
STRCrpalkeGrfs7AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmCodeLog2 | [6 empty] | 6157 | 1 | 0x0340aa41
STRCrpalkeGrfs7AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmCodeLog3 | [6 empty] | 6157 | 1 | 0x0340aa42
STRCrpalkeGrfs7AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmCodeLog4 | [6 empty] | 6157 | 1 | 0x0340aa43
STRCrpalkeGrfs7AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmCodeLog5 | [6 empty] | 6157 | 1 | 0x0340aa44
STRCrpalkeGrfs7AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[0] | [6 empty] | 6157 | 1 | 0x0340aa45
STRCrpalkeGrfs7AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[10] | [6 empty] | 6157 | 1 | 0x0340aa46
STRCrpalkeGrfs7AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[11] | [6 empty] | 6157 | 1 | 0x0340aa47
STRCrpalkeGrfs7AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[12] | [6 empty] | 6157 | 1 | 0x0340aa48
STRCrpalkeGrfs7AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[13] | [6 empty] | 6157 | 1 | 0x0340aa49
STRCrpalkeGrfs7AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[14] | [6 empty] | 6157 | 1 | 0x0340aa4a
STRCrpalkeGrfs7AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[15] | [6 empty] | 6157 | 1 | 0x0340aa4b
STRCrpalkeGrfs7AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[16] | [6 empty] | 6157 | 1 | 0x0340aa4c
STRCrpalkeGrfs7AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[1] | [6 empty] | 6157 | 1 | 0x0340aa4d
STRCrpalkeGrfs7AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[2] | [6 empty] | 6157 | 1 | 0x0340aa4e
STRCrpalkeGrfs7AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[3] | [6 empty] | 6157 | 1 | 0x0340aa4f
STRCrpalkeGrfs7AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[4] | [6 empty] | 6157 | 1 | 0x0340aa50
STRCrpalkeGrfs7AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[5] | [6 empty] | 6157 | 1 | 0x0340aa51
STRCrpalkeGrfs7AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[6] | [6 empty] | 6157 | 1 | 0x0340aa52
STRCrpalkeGrfs7AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[7] | [6 empty] | 6157 | 1 | 0x0340aa53
STRCrpalkeGrfs7AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[8] | [6 empty] | 6157 | 1 | 0x0340aa54
STRCrpalkeGrfs7AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[9] | [6 empty] | 6157 | 1 | 0x0340aa55
STRCrpalkeGrfs7AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmQSD1 | [6 empty] | 6157 | 1 | 0x0340aa56
STRCrpalkeGrfs7AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmQSD2 | [6 empty] | 6157 | 1 | 0x0340aa57
STRCrpalkeGrfs7AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmStart1 | [6 empty] | 6157 | 1 | 0x0340aa58
STRCrpalkeGrfs7AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmStart2 | [6 empty] | 6157 | 1 | 0x0340aa59
STRCrpalkeGrfs7AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmStop1 | [6 empty] | 6157 | 1 | 0x0340aa5a
STRCrpalkeGrfs7AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmStop2 | [6 empty] | 6157 | 1 | 0x0340aa5b
STRCrpalkeGrfs7AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmStop3 | [6 empty] | 6157 | 1 | 0x0340aa5c
STRCrpalkeGrfs7AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmSurv1 | [6 empty] | 6157 | 1 | 0x0340aa5d
STRCrpalkeGrfs7AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmSurv2 | [6 empty] | 6157 | 1 | 0x0340aa5e
STRCrpalkeGrfs7ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[7].ControlSource | [6 empty] | 6157 | 1 | 0x0340aa5f
STRCrpalkeGrfs7DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[7].DeltaSetPoint | [6 empty] | 6157 | 1 | 0x0340aa60
STRCrpalkeGrfs7Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].Deluje | [6 empty] | 6157 | 1 | 0x0340aa70
STRCrpalkeGrfs7EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[7].EnergijaPoraba |  |  |  |  | kWh | ####.# | 6157 | 1 | 0x0340aa80
STRCrpalkeGrfs7ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[7].ExternInputSetup | [6 empty] | 6157 | 1 | 0x0340aa81
STRCrpalkeGrfs7ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[7].ExternInputsStatus | [6 empty] | 6157 | 1 | 0x0340aa82
STRCrpalkeGrfs7FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[7].FrekPretvornikDCNapetost | 0 | 500 | 0 | 500 | V | ####.# | 6157 | 1 | 0x0340aa83
STRCrpalkeGrfs7FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[7].FrekPretvornikDCTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340aa84
STRCrpalkeGrfs7FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[7].FreqMax | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340aa85
STRCrpalkeGrfs7FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[7].FreqMin | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340aa86
STRCrpalkeGrfs7FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[7].FreqUpper | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340aa87
STRCrpalkeGrfs7LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].LocalMode | [6 empty] | 6157 | 1 | 0x0340aa90
STRCrpalkeGrfs7LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].LocalSetupMode1 | [6 empty] | 6157 | 1 | 0x0340aaa0
STRCrpalkeGrfs7MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[7].MocMax | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x0340aaa1
STRCrpalkeGrfs7MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[7].MocTrenutna | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x0340aaa2
STRCrpalkeGrfs7MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[7].MotorHitrost | 0 | 2500 | 0 | 2500 | obr/min | ####.# | 6157 | 1 | 0x0340aaa3
STRCrpalkeGrfs7MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[7].MotorTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340aaa4
STRCrpalkeGrfs7NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[7].NapajanjeTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340aaa5
STRCrpalkeGrfs7NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[7].NastavitevLokalna | [6 empty] | 6157 | 1 | 0x0340aaa6
STRCrpalkeGrfs7NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[7].NastavitevTrenutna | [6 empty] | 6157 | 1 | 0x0340aaa7
STRCrpalkeGrfs7PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[7].PreklopkaMode | [6 empty] | 6157 | 1 | 0x0340aaa8
STRCrpalkeGrfs7PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[7].PretokMax | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340aaa9
STRCrpalkeGrfs7PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[7].PretokMin | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340aaaa
STRCrpalkeGrfs7PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[7].PretokTrenutni | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340aaab
STRCrpalkeGrfs7PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[7].PritiskMax | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340aaac
STRCrpalkeGrfs7PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[7].PritiskTrenutni | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340aaad
STRCrpalkeGrfs7ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[7].ReferencaMotorjaHzV | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340aaae
STRCrpalkeGrfs7ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[7].ReferencaRemote | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340aaaf
STRCrpalkeGrfs7Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[7].Relay1setup | [6 empty] | 6157 | 1 | 0x0340aab0
STRCrpalkeGrfs7RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].RemoteON | [6 empty] | 6157 | 1 | 0x0340aac0
STRCrpalkeGrfs7RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].RemoteSetupMode1 | [6 empty] | 6157 | 1 | 0x0340aad0
STRCrpalkeGrfs7Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].Reset2handkWhValues | [6 empty] | 6157 | 1 | 0x0340aae0
STRCrpalkeGrfs7ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].ResetAlarm | [6 empty] | 6157 | 1 | 0x0340aaf0
STRCrpalkeGrfs7ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].ResetAlarmLog | [6 empty] | 6157 | 1 | 0x0340ab00
STRCrpalkeGrfs7ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].ResetDevice | [6 empty] | 6157 | 1 | 0x0340ab10
STRCrpalkeGrfs7SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetAutomatic | [6 empty] | 6157 | 1 | 0x0340ab20
STRCrpalkeGrfs7SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetConstFreqMode | [6 empty] | 6157 | 1 | 0x0340ab30
STRCrpalkeGrfs7SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetConstPress | [6 empty] | 6157 | 1 | 0x0340ab40
STRCrpalkeGrfs7SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetLocalMode | [6 empty] | 6157 | 1 | 0x0340ab50
STRCrpalkeGrfs7SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetMaxRunMode | [6 empty] | 6157 | 1 | 0x0340ab60
STRCrpalkeGrfs7SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetMinRunMode | [6 empty] | 6157 | 1 | 0x0340ab70
STRCrpalkeGrfs7SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetPropPress | [6 empty] | 6157 | 1 | 0x0340ab80
STRCrpalkeGrfs7SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetReference | [6 empty] | 6157 | 1 | 0x0340ab90
STRCrpalkeGrfs7SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetRemoteMode | [6 empty] | 6157 | 1 | 0x0340aba0
STRCrpalkeGrfs7SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetTwinModeAlt | [6 empty] | 6157 | 1 | 0x0340abb0
STRCrpalkeGrfs7SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetTwinModeSpare | [6 empty] | 6157 | 1 | 0x0340abc0
STRCrpalkeGrfs7SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetTwinModeSync | [6 empty] | 6157 | 1 | 0x0340abd0
STRCrpalkeGrfs7Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].Start | [6 empty] | 6157 | 1 | 0x0340abe0
STRCrpalkeGrfs7StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeGrfs[7].StatusCrpalke | [6 empty] | 6157 | 1 | 0x0340abf0
STRCrpalkeGrfs7StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].StatusMode1 | [6 empty] | 6157 | 1 | 0x0340abf1
STRCrpalkeGrfs7StatusMode1co | BYTE | IOD_STR | STR:.CrpalkeGrfs[7].StatusMode1co | [6 empty] | 6157 | 1 | 0x0340abf2
STRCrpalkeGrfs7StatusMode1op | BYTE | IOD_STR | STR:.CrpalkeGrfs[7].StatusMode1op | [6 empty] | 6157 | 1 | 0x0340abf3
STRCrpalkeGrfs7StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].StatusMode2 | [6 empty] | 6157 | 1 | 0x0340abf4
STRCrpalkeGrfs7StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[7].StatusMode3 | [6 empty] | 6157 | 1 | 0x0340abf5
STRCrpalkeGrfs7StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[7].StevecUr2h |  |  |  |  | 2h |  | 6157 | 1 | 0x0340abf6
STRCrpalkeGrfs7Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].Stop | [6 empty] | 6157 | 1 | 0x0340ac00
STRCrpalkeGrfs7SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[7].SystemFeedback | [6 empty] | 6157 | 1 | 0x0340ac10
STRCrpalkeGrfs7SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[7].SystemReference | [6 empty] | 6157 | 1 | 0x0340ac11
STRCrpalkeGrfs7TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[7].TemperaturaMotorja | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x0340ac12
STRCrpalkeGrfs7UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[7].UreXC200 |  |  |  |  | h | ####.# | 6157 | 1 | 0x0340ac13
STRCrpalkeGrfs8AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmActiveCode | [6 empty] | 6157 | 1 | 0x0340ac14
STRCrpalkeGrfs8AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].AlarmAktiven | [6 empty] | 6157 | 1 | 0x0340ac20
STRCrpalkeGrfs8AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmCodeLog1 | [6 empty] | 6157 | 1 | 0x0340ac30
STRCrpalkeGrfs8AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmCodeLog2 | [6 empty] | 6157 | 1 | 0x0340ac31
STRCrpalkeGrfs8AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmCodeLog3 | [6 empty] | 6157 | 1 | 0x0340ac32
STRCrpalkeGrfs8AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmCodeLog4 | [6 empty] | 6157 | 1 | 0x0340ac33
STRCrpalkeGrfs8AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmCodeLog5 | [6 empty] | 6157 | 1 | 0x0340ac34
STRCrpalkeGrfs8AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[0] | [6 empty] | 6157 | 1 | 0x0340ac35
STRCrpalkeGrfs8AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[10] | [6 empty] | 6157 | 1 | 0x0340ac36
STRCrpalkeGrfs8AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[11] | [6 empty] | 6157 | 1 | 0x0340ac37
STRCrpalkeGrfs8AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[12] | [6 empty] | 6157 | 1 | 0x0340ac38
STRCrpalkeGrfs8AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[13] | [6 empty] | 6157 | 1 | 0x0340ac39
STRCrpalkeGrfs8AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[14] | [6 empty] | 6157 | 1 | 0x0340ac3a
STRCrpalkeGrfs8AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[15] | [6 empty] | 6157 | 1 | 0x0340ac3b
STRCrpalkeGrfs8AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[16] | [6 empty] | 6157 | 1 | 0x0340ac3c
STRCrpalkeGrfs8AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[1] | [6 empty] | 6157 | 1 | 0x0340ac3d
STRCrpalkeGrfs8AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[2] | [6 empty] | 6157 | 1 | 0x0340ac3e
STRCrpalkeGrfs8AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[3] | [6 empty] | 6157 | 1 | 0x0340ac3f
STRCrpalkeGrfs8AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[4] | [6 empty] | 6157 | 1 | 0x0340ac40
STRCrpalkeGrfs8AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[5] | [6 empty] | 6157 | 1 | 0x0340ac41
STRCrpalkeGrfs8AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[6] | [6 empty] | 6157 | 1 | 0x0340ac42
STRCrpalkeGrfs8AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[7] | [6 empty] | 6157 | 1 | 0x0340ac43
STRCrpalkeGrfs8AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[8] | [6 empty] | 6157 | 1 | 0x0340ac44
STRCrpalkeGrfs8AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[9] | [6 empty] | 6157 | 1 | 0x0340ac45
STRCrpalkeGrfs8AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmQSD1 | [6 empty] | 6157 | 1 | 0x0340ac46
STRCrpalkeGrfs8AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmQSD2 | [6 empty] | 6157 | 1 | 0x0340ac47
STRCrpalkeGrfs8AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmStart1 | [6 empty] | 6157 | 1 | 0x0340ac48
STRCrpalkeGrfs8AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmStart2 | [6 empty] | 6157 | 1 | 0x0340ac49
STRCrpalkeGrfs8AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmStop1 | [6 empty] | 6157 | 1 | 0x0340ac4a
STRCrpalkeGrfs8AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmStop2 | [6 empty] | 6157 | 1 | 0x0340ac4b
STRCrpalkeGrfs8AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmStop3 | [6 empty] | 6157 | 1 | 0x0340ac4c
STRCrpalkeGrfs8AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmSurv1 | [6 empty] | 6157 | 1 | 0x0340ac4d
STRCrpalkeGrfs8AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmSurv2 | [6 empty] | 6157 | 1 | 0x0340ac4e
STRCrpalkeGrfs8ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[8].ControlSource | [6 empty] | 6157 | 1 | 0x0340ac4f
STRCrpalkeGrfs8DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[8].DeltaSetPoint | [6 empty] | 6157 | 1 | 0x0340ac50
STRCrpalkeGrfs8Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].Deluje | [6 empty] | 6157 | 1 | 0x0340ac60
STRCrpalkeGrfs8EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[8].EnergijaPoraba |  |  |  |  | kWh | ####.# | 6157 | 1 | 0x0340ac70
STRCrpalkeGrfs8ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[8].ExternInputSetup | [6 empty] | 6157 | 1 | 0x0340ac71
STRCrpalkeGrfs8ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[8].ExternInputsStatus | [6 empty] | 6157 | 1 | 0x0340ac72
STRCrpalkeGrfs8FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[8].FrekPretvornikDCNapetost | 0 | 500 | 0 | 500 | V | ####.# | 6157 | 1 | 0x0340ac73
STRCrpalkeGrfs8FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[8].FrekPretvornikDCTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340ac74
STRCrpalkeGrfs8FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[8].FreqMax | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340ac75
STRCrpalkeGrfs8FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[8].FreqMin | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340ac76
STRCrpalkeGrfs8FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[8].FreqUpper | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340ac77
STRCrpalkeGrfs8LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].LocalMode | [6 empty] | 6157 | 1 | 0x0340ac80
STRCrpalkeGrfs8LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].LocalSetupMode1 | [6 empty] | 6157 | 1 | 0x0340ac90
STRCrpalkeGrfs8MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[8].MocMax | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x0340ac91
STRCrpalkeGrfs8MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[8].MocTrenutna | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x0340ac92
STRCrpalkeGrfs8MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[8].MotorHitrost | 0 | 2500 | 0 | 2500 | obr/min | ####.# | 6157 | 1 | 0x0340ac93
STRCrpalkeGrfs8MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[8].MotorTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340ac94
STRCrpalkeGrfs8NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[8].NapajanjeTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340ac95
STRCrpalkeGrfs8NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[8].NastavitevLokalna | [6 empty] | 6157 | 1 | 0x0340ac96
STRCrpalkeGrfs8NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[8].NastavitevTrenutna | [6 empty] | 6157 | 1 | 0x0340ac97
STRCrpalkeGrfs8PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[8].PreklopkaMode | [6 empty] | 6157 | 1 | 0x0340ac98
STRCrpalkeGrfs8PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[8].PretokMax | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340ac99
STRCrpalkeGrfs8PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[8].PretokMin | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340ac9a
STRCrpalkeGrfs8PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[8].PretokTrenutni | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340ac9b
STRCrpalkeGrfs8PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[8].PritiskMax | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340ac9c
STRCrpalkeGrfs8PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[8].PritiskTrenutni | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340ac9d
STRCrpalkeGrfs8ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[8].ReferencaMotorjaHzV | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340ac9e
STRCrpalkeGrfs8ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[8].ReferencaRemote | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340ac9f
STRCrpalkeGrfs8Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[8].Relay1setup | [6 empty] | 6157 | 1 | 0x0340aca0
STRCrpalkeGrfs8RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].RemoteON | [6 empty] | 6157 | 1 | 0x0340acb0
STRCrpalkeGrfs8RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].RemoteSetupMode1 | [6 empty] | 6157 | 1 | 0x0340acc0
STRCrpalkeGrfs8Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].Reset2handkWhValues | [6 empty] | 6157 | 1 | 0x0340acd0
STRCrpalkeGrfs8ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].ResetAlarm | [6 empty] | 6157 | 1 | 0x0340ace0
STRCrpalkeGrfs8ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].ResetAlarmLog | [6 empty] | 6157 | 1 | 0x0340acf0
STRCrpalkeGrfs8ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].ResetDevice | [6 empty] | 6157 | 1 | 0x0340ad00
STRCrpalkeGrfs8SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetAutomatic | [6 empty] | 6157 | 1 | 0x0340ad10
STRCrpalkeGrfs8SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetConstFreqMode | [6 empty] | 6157 | 1 | 0x0340ad20
STRCrpalkeGrfs8SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetConstPress | [6 empty] | 6157 | 1 | 0x0340ad30
STRCrpalkeGrfs8SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetLocalMode | [6 empty] | 6157 | 1 | 0x0340ad40
STRCrpalkeGrfs8SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetMaxRunMode | [6 empty] | 6157 | 1 | 0x0340ad50
STRCrpalkeGrfs8SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetMinRunMode | [6 empty] | 6157 | 1 | 0x0340ad60
STRCrpalkeGrfs8SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetPropPress | [6 empty] | 6157 | 1 | 0x0340ad70
STRCrpalkeGrfs8SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetReference | [6 empty] | 6157 | 1 | 0x0340ad80
STRCrpalkeGrfs8SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetRemoteMode | [6 empty] | 6157 | 1 | 0x0340ad90
STRCrpalkeGrfs8SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetTwinModeAlt | [6 empty] | 6157 | 1 | 0x0340ada0
STRCrpalkeGrfs8SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetTwinModeSpare | [6 empty] | 6157 | 1 | 0x0340adb0
STRCrpalkeGrfs8SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetTwinModeSync | [6 empty] | 6157 | 1 | 0x0340adc0
STRCrpalkeGrfs8Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].Start | [6 empty] | 6157 | 1 | 0x0340add0
STRCrpalkeGrfs8StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeGrfs[8].StatusCrpalke | [6 empty] | 6157 | 1 | 0x0340ade0
STRCrpalkeGrfs8StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].StatusMode1 | [6 empty] | 6157 | 1 | 0x0340ade1
STRCrpalkeGrfs8StatusMode1co | BYTE | IOD_STR | STR:.CrpalkeGrfs[8].StatusMode1co | [6 empty] | 6157 | 1 | 0x0340ade2
STRCrpalkeGrfs8StatusMode1op | BYTE | IOD_STR | STR:.CrpalkeGrfs[8].StatusMode1op | [6 empty] | 6157 | 1 | 0x0340ade3
STRCrpalkeGrfs8StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].StatusMode2 | [6 empty] | 6157 | 1 | 0x0340ade4
STRCrpalkeGrfs8StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[8].StatusMode3 | [6 empty] | 6157 | 1 | 0x0340ade5
STRCrpalkeGrfs8StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[8].StevecUr2h |  |  |  |  | 2h |  | 6157 | 1 | 0x0340ade6
STRCrpalkeGrfs8Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].Stop | [6 empty] | 6157 | 1 | 0x0340adf0
STRCrpalkeGrfs8SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[8].SystemFeedback | [6 empty] | 6157 | 1 | 0x0340ae00
STRCrpalkeGrfs8SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[8].SystemReference | [6 empty] | 6157 | 1 | 0x0340ae01
STRCrpalkeGrfs8TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[8].TemperaturaMotorja | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x0340ae02
STRCrpalkeGrfs8UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[8].UreXC200 |  |  |  |  | h | ####.# | 6157 | 1 | 0x0340ae03
STRCrpalkeGrfs9AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmActiveCode | [6 empty] | 6157 | 1 | 0x0340ae04
STRCrpalkeGrfs9AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].AlarmAktiven | [6 empty] | 6157 | 1 | 0x0340ae10
STRCrpalkeGrfs9AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmCodeLog1 | [6 empty] | 6157 | 1 | 0x0340ae20
STRCrpalkeGrfs9AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmCodeLog2 | [6 empty] | 6157 | 1 | 0x0340ae21
STRCrpalkeGrfs9AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmCodeLog3 | [6 empty] | 6157 | 1 | 0x0340ae22
STRCrpalkeGrfs9AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmCodeLog4 | [6 empty] | 6157 | 1 | 0x0340ae23
STRCrpalkeGrfs9AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmCodeLog5 | [6 empty] | 6157 | 1 | 0x0340ae24
STRCrpalkeGrfs9AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[0] | [6 empty] | 6157 | 1 | 0x0340ae25
STRCrpalkeGrfs9AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[10] | [6 empty] | 6157 | 1 | 0x0340ae26
STRCrpalkeGrfs9AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[11] | [6 empty] | 6157 | 1 | 0x0340ae27
STRCrpalkeGrfs9AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[12] | [6 empty] | 6157 | 1 | 0x0340ae28
STRCrpalkeGrfs9AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[13] | [6 empty] | 6157 | 1 | 0x0340ae29
STRCrpalkeGrfs9AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[14] | [6 empty] | 6157 | 1 | 0x0340ae2a
STRCrpalkeGrfs9AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[15] | [6 empty] | 6157 | 1 | 0x0340ae2b
STRCrpalkeGrfs9AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[16] | [6 empty] | 6157 | 1 | 0x0340ae2c
STRCrpalkeGrfs9AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[1] | [6 empty] | 6157 | 1 | 0x0340ae2d
STRCrpalkeGrfs9AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[2] | [6 empty] | 6157 | 1 | 0x0340ae2e
STRCrpalkeGrfs9AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[3] | [6 empty] | 6157 | 1 | 0x0340ae2f
STRCrpalkeGrfs9AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[4] | [6 empty] | 6157 | 1 | 0x0340ae30
STRCrpalkeGrfs9AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[5] | [6 empty] | 6157 | 1 | 0x0340ae31
STRCrpalkeGrfs9AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[6] | [6 empty] | 6157 | 1 | 0x0340ae32
STRCrpalkeGrfs9AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[7] | [6 empty] | 6157 | 1 | 0x0340ae33
STRCrpalkeGrfs9AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[8] | [6 empty] | 6157 | 1 | 0x0340ae34
STRCrpalkeGrfs9AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[9] | [6 empty] | 6157 | 1 | 0x0340ae35
STRCrpalkeGrfs9AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmQSD1 | [6 empty] | 6157 | 1 | 0x0340ae36
STRCrpalkeGrfs9AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmQSD2 | [6 empty] | 6157 | 1 | 0x0340ae37
STRCrpalkeGrfs9AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmStart1 | [6 empty] | 6157 | 1 | 0x0340ae38
STRCrpalkeGrfs9AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmStart2 | [6 empty] | 6157 | 1 | 0x0340ae39
STRCrpalkeGrfs9AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmStop1 | [6 empty] | 6157 | 1 | 0x0340ae3a
STRCrpalkeGrfs9AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmStop2 | [6 empty] | 6157 | 1 | 0x0340ae3b
STRCrpalkeGrfs9AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmStop3 | [6 empty] | 6157 | 1 | 0x0340ae3c
STRCrpalkeGrfs9AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmSurv1 | [6 empty] | 6157 | 1 | 0x0340ae3d
STRCrpalkeGrfs9AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmSurv2 | [6 empty] | 6157 | 1 | 0x0340ae3e
STRCrpalkeGrfs9ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[9].ControlSource | [6 empty] | 6157 | 1 | 0x0340ae3f
STRCrpalkeGrfs9DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[9].DeltaSetPoint | [6 empty] | 6157 | 1 | 0x0340ae40
STRCrpalkeGrfs9Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].Deluje | [6 empty] | 6157 | 1 | 0x0340ae50
STRCrpalkeGrfs9EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[9].EnergijaPoraba |  |  |  |  | kWh | ####.# | 6157 | 1 | 0x0340ae60
STRCrpalkeGrfs9ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[9].ExternInputSetup | [6 empty] | 6157 | 1 | 0x0340ae61
STRCrpalkeGrfs9ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[9].ExternInputsStatus | [6 empty] | 6157 | 1 | 0x0340ae62
STRCrpalkeGrfs9FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[9].FrekPretvornikDCNapetost | 0 | 500 | 0 | 500 | V | ####.# | 6157 | 1 | 0x0340ae63
STRCrpalkeGrfs9FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[9].FrekPretvornikDCTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340ae64
STRCrpalkeGrfs9FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[9].FreqMax | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340ae65
STRCrpalkeGrfs9FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[9].FreqMin | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340ae66
STRCrpalkeGrfs9FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[9].FreqUpper | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340ae67
STRCrpalkeGrfs9LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].LocalMode | [6 empty] | 6157 | 1 | 0x0340ae70
STRCrpalkeGrfs9LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].LocalSetupMode1 | [6 empty] | 6157 | 1 | 0x0340ae80
STRCrpalkeGrfs9MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[9].MocMax | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x0340ae81
STRCrpalkeGrfs9MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[9].MocTrenutna | 0 | 10000 | 0 | 10000 | W | ####.# | 6157 | 1 | 0x0340ae82
STRCrpalkeGrfs9MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[9].MotorHitrost | 0 | 2500 | 0 | 2500 | obr/min | ####.# | 6157 | 1 | 0x0340ae83
STRCrpalkeGrfs9MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[9].MotorTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340ae84
STRCrpalkeGrfs9NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[9].NapajanjeTok | 0 | 100 | 0 | 100 | A | ####.# | 6157 | 1 | 0x0340ae85
STRCrpalkeGrfs9NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[9].NastavitevLokalna | [6 empty] | 6157 | 1 | 0x0340ae86
STRCrpalkeGrfs9NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[9].NastavitevTrenutna | [6 empty] | 6157 | 1 | 0x0340ae87
STRCrpalkeGrfs9PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[9].PreklopkaMode | [6 empty] | 6157 | 1 | 0x0340ae88
STRCrpalkeGrfs9PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[9].PretokMax | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340ae89
STRCrpalkeGrfs9PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[9].PretokMin | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340ae8a
STRCrpalkeGrfs9PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[9].PretokTrenutni | 0 | 10 | 0 | 10 | m3/h | ####.# | 6157 | 1 | 0x0340ae8b
STRCrpalkeGrfs9PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[9].PritiskMax | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340ae8c
STRCrpalkeGrfs9PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[9].PritiskTrenutni | 0 | 15 | 0 | 15 | bar | ####.# | 6157 | 1 | 0x0340ae8d
STRCrpalkeGrfs9ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[9].ReferencaMotorjaHzV | 0 | 70 | 0 | 70 | Hz | ####.# | 6157 | 1 | 0x0340ae8e
STRCrpalkeGrfs9ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[9].ReferencaRemote | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340ae8f
STRCrpalkeGrfs9Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[9].Relay1setup | [6 empty] | 6157 | 1 | 0x0340ae90
STRCrpalkeGrfs9RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].RemoteON | [6 empty] | 6157 | 1 | 0x0340aea0
STRCrpalkeGrfs9RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].RemoteSetupMode1 | [6 empty] | 6157 | 1 | 0x0340aeb0
STRCrpalkeGrfs9Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].Reset2handkWhValues | [6 empty] | 6157 | 1 | 0x0340aec0
STRCrpalkeGrfs9ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].ResetAlarm | [6 empty] | 6157 | 1 | 0x0340aed0
STRCrpalkeGrfs9ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].ResetAlarmLog | [6 empty] | 6157 | 1 | 0x0340aee0
STRCrpalkeGrfs9ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].ResetDevice | [6 empty] | 6157 | 1 | 0x0340aef0
STRCrpalkeGrfs9SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetAutomatic | [6 empty] | 6157 | 1 | 0x0340af00
STRCrpalkeGrfs9SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetConstFreqMode | [6 empty] | 6157 | 1 | 0x0340af10
STRCrpalkeGrfs9SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetConstPress | [6 empty] | 6157 | 1 | 0x0340af20
STRCrpalkeGrfs9SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetLocalMode | [6 empty] | 6157 | 1 | 0x0340af30
STRCrpalkeGrfs9SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetMaxRunMode | [6 empty] | 6157 | 1 | 0x0340af40
STRCrpalkeGrfs9SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetMinRunMode | [6 empty] | 6157 | 1 | 0x0340af50
STRCrpalkeGrfs9SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetPropPress | [6 empty] | 6157 | 1 | 0x0340af60
STRCrpalkeGrfs9SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetReference | [6 empty] | 6157 | 1 | 0x0340af70
STRCrpalkeGrfs9SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetRemoteMode | [6 empty] | 6157 | 1 | 0x0340af80
STRCrpalkeGrfs9SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetTwinModeAlt | [6 empty] | 6157 | 1 | 0x0340af90
STRCrpalkeGrfs9SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetTwinModeSpare | [6 empty] | 6157 | 1 | 0x0340afa0
STRCrpalkeGrfs9SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetTwinModeSync | [6 empty] | 6157 | 1 | 0x0340afb0
STRCrpalkeGrfs9Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].Start | [6 empty] | 6157 | 1 | 0x0340afc0
STRCrpalkeGrfs9StatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeGrfs[9].StatusCrpalke | [6 empty] | 6157 | 1 | 0x0340afd0
STRCrpalkeGrfs9StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].StatusMode1 | [6 empty] | 6157 | 1 | 0x0340afd1
STRCrpalkeGrfs9StatusMode1co | BYTE | IOD_STR | STR:.CrpalkeGrfs[9].StatusMode1co | [6 empty] | 6157 | 1 | 0x0340afd2
STRCrpalkeGrfs9StatusMode1op | BYTE | IOD_STR | STR:.CrpalkeGrfs[9].StatusMode1op | [6 empty] | 6157 | 1 | 0x0340afd3
STRCrpalkeGrfs9StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].StatusMode2 | [6 empty] | 6157 | 1 | 0x0340afd4
STRCrpalkeGrfs9StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[9].StatusMode3 | [6 empty] | 6157 | 1 | 0x0340afd5
STRCrpalkeGrfs9StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[9].StevecUr2h |  |  |  |  | 2h |  | 6157 | 1 | 0x0340afd6
STRCrpalkeGrfs9Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].Stop | [6 empty] | 6157 | 1 | 0x0340afe0
STRCrpalkeGrfs9SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[9].SystemFeedback | [6 empty] | 6157 | 1 | 0x0340aff0
STRCrpalkeGrfs9SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[9].SystemReference | [6 empty] | 6157 | 1 | 0x0340aff1
STRCrpalkeGrfs9TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[9].TemperaturaMotorja | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x0340aff2
STRCrpalkeGrfs9UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[9].UreXC200 |  |  |  |  | h | ####.# | 6157 | 1 | 0x0340aff3
STRCrpDanfossGenError1 | DIGITAL | IOD_STR | STR:.CrpDanfossGenError[1] | [6 empty] | 6157 | 1 | 0x0340b000
STRCrpDanfossGenError2 | DIGITAL | IOD_STR | STR:.CrpDanfossGenError[2] | [6 empty] | 6157 | 1 | 0x0340b010
STRCrpDanfossGenError3 | DIGITAL | IOD_STR | STR:.CrpDanfossGenError[3] | [6 empty] | 6157 | 1 | 0x0340b020
STRCrpDanfossGenError4 | DIGITAL | IOD_STR | STR:.CrpDanfossGenError[4] | [6 empty] | 6157 | 1 | 0x0340b030
STRCrpDanfossNaCas1 | DIGITAL | IOD_STR | STR:.CrpDanfossNaCas[1] | [6 empty] | 6157 | 1 | 0x0340b040
STRCrpDanfossNaCas2 | DIGITAL | IOD_STR | STR:.CrpDanfossNaCas[2] | [6 empty] | 6157 | 1 | 0x0340b050
STRCrpDanfossON1 | DIGITAL | IOD_STR | STR:.CrpDanfossON[1] | [6 empty] | 6157 | 1 | 0x0340b060
STRCrpDanfossON2 | DIGITAL | IOD_STR | STR:.CrpDanfossON[2] | [6 empty] | 6157 | 1 | 0x0340b070
STRCrpDanfossON3 | DIGITAL | IOD_STR | STR:.CrpDanfossON[3] | [6 empty] | 6157 | 1 | 0x0340b080
STRCrpDanfossON4 | DIGITAL | IOD_STR | STR:.CrpDanfossON[4] | [6 empty] | 6157 | 1 | 0x0340b090
STRCrpDanfossStatusError1 | DIGITAL | IOD_STR | STR:.CrpDanfossStatusError[1] | [6 empty] | 6157 | 1 | 0x0340b0a0
STRCrpDanfossStatusError2 | DIGITAL | IOD_STR | STR:.CrpDanfossStatusError[2] | [6 empty] | 6157 | 1 | 0x0340b0b0
STRCrpDanfossStatusError3 | DIGITAL | IOD_STR | STR:.CrpDanfossStatusError[3] | [6 empty] | 6157 | 1 | 0x0340b0c0
STRCrpDanfossStatusError4 | DIGITAL | IOD_STR | STR:.CrpDanfossStatusError[4] | [6 empty] | 6157 | 1 | 0x0340b0d0
STRCrpGrundfosGenError10 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[10] | [6 empty] | 6157 | 1 | 0x0340b0e0
STRCrpGrundfosGenError11 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[11] | [6 empty] | 6157 | 1 | 0x0340b0f0
STRCrpGrundfosGenError12 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[12] | [6 empty] | 6157 | 1 | 0x0340b100
STRCrpGrundfosGenError13 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[13] | [6 empty] | 6157 | 1 | 0x0340b110
STRCrpGrundfosGenError14 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[14] | [6 empty] | 6157 | 1 | 0x0340b120
STRCrpGrundfosGenError1 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[1] | [6 empty] | 6157 | 1 | 0x0340b130
STRCrpGrundfosGenError2 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[2] | [6 empty] | 6157 | 1 | 0x0340b140
STRCrpGrundfosGenError3 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[3] | [6 empty] | 6157 | 1 | 0x0340b150
STRCrpGrundfosGenError4 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[4] | [6 empty] | 6157 | 1 | 0x0340b160
STRCrpGrundfosGenError5 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[5] | [6 empty] | 6157 | 1 | 0x0340b170
STRCrpGrundfosGenError6 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[6] | [6 empty] | 6157 | 1 | 0x0340b180
STRCrpGrundfosGenError7 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[7] | [6 empty] | 6157 | 1 | 0x0340b190
STRCrpGrundfosGenError8 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[8] | [6 empty] | 6157 | 1 | 0x0340b1a0
STRCrpGrundfosGenError9 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[9] | [6 empty] | 6157 | 1 | 0x0340b1b0
STRCrpGrundfosNaCas1 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[1] | [6 empty] | 6157 | 1 | 0x0340b1c0
STRCrpGrundfosNaCas2 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[2] | [6 empty] | 6157 | 1 | 0x0340b1d0
STRCrpGrundfosNaCas3 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[3] | [6 empty] | 6157 | 1 | 0x0340b1e0
STRCrpGrundfosNaCas4 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[4] | [6 empty] | 6157 | 1 | 0x0340b1f0
STRCrpGrundfosNaCas5 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[5] | [6 empty] | 6157 | 1 | 0x0340b200
STRCrpGrundfosNaCas6 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[6] | [6 empty] | 6157 | 1 | 0x0340b210
STRCrpGrundfosNaCas7 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[7] | [6 empty] | 6157 | 1 | 0x0340b220
STRCrpGrundfosNaTlak1 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[1] | [6 empty] | 6157 | 1 | 0x0340b230
STRCrpGrundfosNaTlak2 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[2] | [6 empty] | 6157 | 1 | 0x0340b240
STRCrpGrundfosNaTlak3 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[3] | [6 empty] | 6157 | 1 | 0x0340b250
STRCrpGrundfosNaTlak4 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[4] | [6 empty] | 6157 | 1 | 0x0340b260
STRCrpGrundfosNaTlak5 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[5] | [6 empty] | 6157 | 1 | 0x0340b270
STRCrpGrundfosNaTlak6 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[6] | [6 empty] | 6157 | 1 | 0x0340b280
STRCrpGrundfosNaTlak7 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[7] | [6 empty] | 6157 | 1 | 0x0340b290
STRCrpGrundfosON10 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[10] | [6 empty] | 6157 | 1 | 0x0340b2a0
STRCrpGrundfosON11 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[11] | [6 empty] | 6157 | 1 | 0x0340b2b0
STRCrpGrundfosON12 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[12] | [6 empty] | 6157 | 1 | 0x0340b2c0
STRCrpGrundfosON13 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[13] | [6 empty] | 6157 | 1 | 0x0340b2d0
STRCrpGrundfosON14 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[14] | [6 empty] | 6157 | 1 | 0x0340b2e0
STRCrpGrundfosON1 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[1] | [6 empty] | 6157 | 1 | 0x0340b2f0
STRCrpGrundfosON2 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[2] | [6 empty] | 6157 | 1 | 0x0340b300
STRCrpGrundfosON3 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[3] | [6 empty] | 6157 | 1 | 0x0340b310
STRCrpGrundfosON4 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[4] | [6 empty] | 6157 | 1 | 0x0340b320
STRCrpGrundfosON5 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[5] | [6 empty] | 6157 | 1 | 0x0340b330
STRCrpGrundfosON6 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[6] | [6 empty] | 6157 | 1 | 0x0340b340
STRCrpGrundfosON7 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[7] | [6 empty] | 6157 | 1 | 0x0340b350
STRCrpGrundfosON8 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[8] | [6 empty] | 6157 | 1 | 0x0340b360
STRCrpGrundfosON9 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[9] | [6 empty] | 6157 | 1 | 0x0340b370
STRCrpGrundfosStatusError10 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[10] | [6 empty] | 6157 | 1 | 0x0340b380
STRCrpGrundfosStatusError11 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[11] | [6 empty] | 6157 | 1 | 0x0340b390
STRCrpGrundfosStatusError12 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[12] | [6 empty] | 6157 | 1 | 0x0340b3a0
STRCrpGrundfosStatusError13 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[13] | [6 empty] | 6157 | 1 | 0x0340b3b0
STRCrpGrundfosStatusError14 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[14] | [6 empty] | 6157 | 1 | 0x0340b3c0
STRCrpGrundfosStatusError1 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[1] | [6 empty] | 6157 | 1 | 0x0340b3d0
STRCrpGrundfosStatusError2 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[2] | [6 empty] | 6157 | 1 | 0x0340b3e0
STRCrpGrundfosStatusError3 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[3] | [6 empty] | 6157 | 1 | 0x0340b3f0
STRCrpGrundfosStatusError4 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[4] | [6 empty] | 6157 | 1 | 0x0340b400
STRCrpGrundfosStatusError5 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[5] | [6 empty] | 6157 | 1 | 0x0340b410
STRCrpGrundfosStatusError6 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[6] | [6 empty] | 6157 | 1 | 0x0340b420
STRCrpGrundfosStatusError7 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[7] | [6 empty] | 6157 | 1 | 0x0340b430
STRCrpGrundfosStatusError8 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[8] | [6 empty] | 6157 | 1 | 0x0340b440
STRCrpGrundfosStatusError9 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[9] | [6 empty] | 6157 | 1 | 0x0340b450
STRCrpGrundfosTlakSP1 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[1] | 0 | 5 | 0 | 5 | bar | ####.# | 6157 | 1 | 0x0340b460
STRCrpGrundfosTlakSP2 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[2] | 0 | 5 | 0 | 5 | bar | ####.# | 6157 | 1 | 0x0340b461
STRCrpGrundfosTlakSP3 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[3] | 0 | 5 | 0 | 5 | bar | ####.# | 6157 | 1 | 0x0340b462
STRCrpGrundfosTlakSP4 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[4] | 0 | 5 | 0 | 5 | bar | ####.# | 6157 | 1 | 0x0340b463
STRCrpGrundfosTlakSP5 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[5] | 0 | 5 | 0 | 5 | bar | ####.# | 6157 | 1 | 0x0340b464
STRCrpGrundfosTlakSP6 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[6] | 0 | 5 | 0 | 5 | bar | ####.# | 6157 | 1 | 0x0340b465
STRCrpGrundfosTlakSP7 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[7] | 0 | 5 | 0 | 5 | bar | ####.# | 6157 | 1 | 0x0340b466
STRDanfossHMKontOnOff1 | DIGITAL | IOD_STR | STR:.DanfossHMKontOnOff[1] | [6 empty] | 6157 | 1 | 0x0340b470
STRDanfossHMKontOnOff2 | DIGITAL | IOD_STR | STR:.DanfossHMKontOnOff[2] | [6 empty] | 6157 | 1 | 0x0340b480
STRDanfossHMKontOnOff3 | DIGITAL | IOD_STR | STR:.DanfossHMKontOnOff[3] | [6 empty] | 6157 | 1 | 0x0340b490
STRDanfossHMKontOnOff4 | DIGITAL | IOD_STR | STR:.DanfossHMKontOnOff[4] | [6 empty] | 6157 | 1 | 0x0340b4a0
STRDateTimeDan | BYTE | IOD_STR | STR:.DateTime.Dan | [6 empty] | 6157 | 1 | 0x0340b4b0
STRDateTimeLeto | BYTE | IOD_STR | STR:.DateTime.Leto | [6 empty] | 6157 | 1 | 0x0340b4b1
STRDateTimeMesec | BYTE | IOD_STR | STR:.DateTime.Mesec | [6 empty] | 6157 | 1 | 0x0340b4b2
STRDateTimeMinuta | BYTE | IOD_STR | STR:.DateTime.Minuta | [6 empty] | 6157 | 1 | 0x0340b4b3
STRDateTimeSekunda | BYTE | IOD_STR | STR:.DateTime.Sekunda | [6 empty] | 6157 | 1 | 0x0340b4b4
STRDateTimeUra | BYTE | IOD_STR | STR:.DateTime.Ura | [6 empty] | 6157 | 1 | 0x0340b4b5
STRDI_230VAC_OK | DIGITAL | IOD_STR | STR:.DI_230VAC_OK | [6 empty] | 6157 | 1 | 0x0340b4c0
STRDI_24VAC_OK | DIGITAL | IOD_STR | STR:.DI_24VAC_OK | [6 empty] | 6157 | 1 | 0x0340b4d0
STRDI_24VDC_OK | DIGITAL | IOD_STR | STR:.DI_24VDC_OK | [6 empty] | 6157 | 1 | 0x0340b4e0
STRDI_AkumTopVodeAUTO | DIGITAL | IOD_STR | STR:.DI_AkumTopVodeAUTO | [6 empty] | 6157 | 1 | 0x0340b4f0
STRDI_AkumTopVodeKontON | DIGITAL | IOD_STR | STR:.DI_AkumTopVodeKontON | [6 empty] | 6157 | 1 | 0x0340b500
STRDI_CrpHM1AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM1AUTO | [6 empty] | 6157 | 1 | 0x0340b510
STRDI_CrpHM1endOFFtoON | DIGITAL | IOD_STR | STR:.DI_CrpHM1endOFFtoON | [6 empty] | 6157 | 1 | 0x0340b520
STRDI_CrpHM1ERR | DIGITAL | IOD_STR | STR:.DI_CrpHM1ERR | [6 empty] | 6157 | 1 | 0x0340b530
STRDI_CrpHM1kontON | DIGITAL | IOD_STR | STR:.DI_CrpHM1kontON | [6 empty] | 6157 | 1 | 0x0340b540
STRDI_CrpHM2AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM2AUTO | [6 empty] | 6157 | 1 | 0x0340b550
STRDI_CrpHM2endOFFtoON | DIGITAL | IOD_STR | STR:.DI_CrpHM2endOFFtoON | [6 empty] | 6157 | 1 | 0x0340b560
STRDI_CrpHM2ERR | DIGITAL | IOD_STR | STR:.DI_CrpHM2ERR | [6 empty] | 6157 | 1 | 0x0340b570
STRDI_CrpHM2kontON | DIGITAL | IOD_STR | STR:.DI_CrpHM2kontON | [6 empty] | 6157 | 1 | 0x0340b580
STRDI_CrpHM3AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM3AUTO | [6 empty] | 6157 | 1 | 0x0340b590
STRDI_CrpHM3endOFFtoON | DIGITAL | IOD_STR | STR:.DI_CrpHM3endOFFtoON | [6 empty] | 6157 | 1 | 0x0340b5a0
STRDI_CrpHM3ERR | DIGITAL | IOD_STR | STR:.DI_CrpHM3ERR | [6 empty] | 6157 | 1 | 0x0340b5b0
STRDI_CrpHM3kontON | DIGITAL | IOD_STR | STR:.DI_CrpHM3kontON | [6 empty] | 6157 | 1 | 0x0340b5c0
STRDI_CrpHM4AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM4AUTO | [6 empty] | 6157 | 1 | 0x0340b5d0
STRDI_CrpHM4endOFFtoON | DIGITAL | IOD_STR | STR:.DI_CrpHM4endOFFtoON | [6 empty] | 6157 | 1 | 0x0340b5e0
STRDI_CrpHM4ERR | DIGITAL | IOD_STR | STR:.DI_CrpHM4ERR | [6 empty] | 6157 | 1 | 0x0340b5f0
STRDI_CrpHM4kontON | DIGITAL | IOD_STR | STR:.DI_CrpHM4kontON | [6 empty] | 6157 | 1 | 0x0340b600
STRDI_CrpHM5AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM5AUTO | [6 empty] | 6157 | 1 | 0x0340b610
STRDI_CrpHM6AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM6AUTO | [6 empty] | 6157 | 1 | 0x0340b620
STRDI_CrpHM7AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM7AUTO | [6 empty] | 6157 | 1 | 0x0340b630
STRDI_CrpHM8AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM8AUTO | [6 empty] | 6157 | 1 | 0x0340b640
STRDI_CrpMN1AUTO | DIGITAL | IOD_STR | STR:.DI_CrpMN1AUTO | [6 empty] | 6157 | 1 | 0x0340b650
STRDI_CrpMN1kontON | DIGITAL | IOD_STR | STR:.DI_CrpMN1kontON | [6 empty] | 6157 | 1 | 0x0340b660
STRDI_CrpTM10AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM10AUTO | [6 empty] | 6157 | 1 | 0x0340b670
STRDI_CrpTM11TM12AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM11TM12AUTO | [6 empty] | 6157 | 1 | 0x0340b680
STRDI_CrpTM11TM12kontON | DIGITAL | IOD_STR | STR:.DI_CrpTM11TM12kontON | [6 empty] | 6157 | 1 | 0x0340b690
STRDI_CrpTM1AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM1AUTO | [6 empty] | 6157 | 1 | 0x0340b6a0
STRDI_CrpTM2AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM2AUTO | [6 empty] | 6157 | 1 | 0x0340b6b0
STRDI_CrpTM3AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM3AUTO | [6 empty] | 6157 | 1 | 0x0340b6c0
STRDI_CrpTM4AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM4AUTO | [6 empty] | 6157 | 1 | 0x0340b6d0
STRDI_CrpTM5AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM5AUTO | [6 empty] | 6157 | 1 | 0x0340b6e0
STRDI_CrpTM6AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM6AUTO | [6 empty] | 6157 | 1 | 0x0340b6f0
STRDI_CrpTM7AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM7AUTO | [6 empty] | 6157 | 1 | 0x0340b700
STRDI_CrpTM8AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM8AUTO | [6 empty] | 6157 | 1 | 0x0340b710
STRDI_CrpTM9AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM9AUTO | [6 empty] | 6157 | 1 | 0x0340b720
STRDI_GlStikaloDieselON | DIGITAL | IOD_STR | STR:.DI_GlStikaloDieselON | [6 empty] | 6157 | 1 | 0x0340b730
STRDI_GlStikaloMrezaON | DIGITAL | IOD_STR | STR:.DI_GlStikaloMrezaON | [6 empty] | 6157 | 1 | 0x0340b740
STRDI_GlStikaloUpsON | DIGITAL | IOD_STR | STR:.DI_GlStikaloUpsON | [6 empty] | 6157 | 1 | 0x0340b750
STRDI_HladStAUTO | DIGITAL | IOD_STR | STR:.DI_HladStAUTO | [6 empty] | 6157 | 1 | 0x0340b760
STRDI_HladStCrpHladH2OON | DIGITAL | IOD_STR | STR:.DI_HladStCrpHladH2OON | [6 empty] | 6157 | 1 | 0x0340b770
STRDI_HladStERR | DIGITAL | IOD_STR | STR:.DI_HladStERR | [6 empty] | 6157 | 1 | 0x0340b780
STRDI_Klima1ERR | DIGITAL | IOD_STR | STR:.DI_Klima1ERR | [6 empty] | 6157 | 1 | 0x0340b790
STRDI_Klima1filterZAM | DIGITAL | IOD_STR | STR:.DI_Klima1filterZAM | [6 empty] | 6157 | 1 | 0x0340b7a0
STRDI_Klima1FIRE | DIGITAL | IOD_STR | STR:.DI_Klima1FIRE | [6 empty] | 6157 | 1 | 0x0340b7b0
STRDI_Klima1OFFtoON | DIGITAL | IOD_STR | STR:.DI_Klima1OFFtoON | [6 empty] | 6157 | 1 | 0x0340b7c0
STRDI_Klima1ON | DIGITAL | IOD_STR | STR:.DI_Klima1ON | [6 empty] | 6157 | 1 | 0x0340b7d0
STRDI_Klima1zascStON | DIGITAL | IOD_STR | STR:.DI_Klima1zascStON | [6 empty] | 6157 | 1 | 0x0340b7e0
STRDI_Klima2ERR | DIGITAL | IOD_STR | STR:.DI_Klima2ERR | [6 empty] | 6157 | 1 | 0x0340b7f0
STRDI_Klima2filterZAM | DIGITAL | IOD_STR | STR:.DI_Klima2filterZAM | [6 empty] | 6157 | 1 | 0x0340b800
STRDI_Klima2FIRE | DIGITAL | IOD_STR | STR:.DI_Klima2FIRE | [6 empty] | 6157 | 1 | 0x0340b810
STRDI_Klima2OFFtoON | DIGITAL | IOD_STR | STR:.DI_Klima2OFFtoON | [6 empty] | 6157 | 1 | 0x0340b820
STRDI_Klima2ON | DIGITAL | IOD_STR | STR:.DI_Klima2ON | [6 empty] | 6157 | 1 | 0x0340b830
STRDI_Klima2zascStON | DIGITAL | IOD_STR | STR:.DI_Klima2zascStON | [6 empty] | 6157 | 1 | 0x0340b840
STRDI_Komp1ERR | DIGITAL | IOD_STR | STR:.DI_Komp1ERR | [6 empty] | 6157 | 1 | 0x0340b850
STRDI_Komp1ON | DIGITAL | IOD_STR | STR:.DI_Komp1ON | [6 empty] | 6157 | 1 | 0x0340b860
STRDI_Komp2ERR | DIGITAL | IOD_STR | STR:.DI_Komp2ERR | [6 empty] | 6157 | 1 | 0x0340b870
STRDI_Komp2ON | DIGITAL | IOD_STR | STR:.DI_Komp2ON | [6 empty] | 6157 | 1 | 0x0340b880
STRDI_Kond1AUTO | DIGITAL | IOD_STR | STR:.DI_Kond1AUTO | [6 empty] | 6157 | 1 | 0x0340b890
STRDI_Kond1FS1FS2 | DIGITAL | IOD_STR | STR:.DI_Kond1FS1FS2 | [6 empty] | 6157 | 1 | 0x0340b8a0
STRDI_Kond1ON | DIGITAL | IOD_STR | STR:.DI_Kond1ON | [6 empty] | 6157 | 1 | 0x0340b8b0
STRDI_Kond1zascStON | DIGITAL | IOD_STR | STR:.DI_Kond1zascStON | [6 empty] | 6157 | 1 | 0x0340b8c0
STRDI_Kond2AUTO | DIGITAL | IOD_STR | STR:.DI_Kond2AUTO | [6 empty] | 6157 | 1 | 0x0340b8d0
STRDI_Kond2FS1FS2 | DIGITAL | IOD_STR | STR:.DI_Kond2FS1FS2 | [6 empty] | 6157 | 1 | 0x0340b8e0
STRDI_Kond2ON | DIGITAL | IOD_STR | STR:.DI_Kond2ON | [6 empty] | 6157 | 1 | 0x0340b8f0
STRDI_Kond2zascStON | DIGITAL | IOD_STR | STR:.DI_Kond2zascStON | [6 empty] | 6157 | 1 | 0x0340b900
STRDI_Kond3AUTO | DIGITAL | IOD_STR | STR:.DI_Kond3AUTO | [6 empty] | 6157 | 1 | 0x0340b910
STRDI_Kond3FS1FS2 | DIGITAL | IOD_STR | STR:.DI_Kond3FS1FS2 | [6 empty] | 6157 | 1 | 0x0340b920
STRDI_Kond3ON | DIGITAL | IOD_STR | STR:.DI_Kond3ON | [6 empty] | 6157 | 1 | 0x0340b930
STRDI_Kond3zascStON | DIGITAL | IOD_STR | STR:.DI_Kond3zascStON | [6 empty] | 6157 | 1 | 0x0340b940
STRDI_Lop1PL1Odprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL1Odprta | [6 empty] | 6157 | 1 | 0x0340b950
STRDI_Lop1PL1Zaprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL1Zaprta | [6 empty] | 6157 | 1 | 0x0340b960
STRDI_Lop1PL2Odprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL2Odprta | [6 empty] | 6157 | 1 | 0x0340b970
STRDI_Lop1PL2Zaprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL2Zaprta | [6 empty] | 6157 | 1 | 0x0340b980
STRDI_Lop1PL3Odprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL3Odprta | [6 empty] | 6157 | 1 | 0x0340b990
STRDI_Lop1PL3Zaprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL3Zaprta | [6 empty] | 6157 | 1 | 0x0340b9a0
STRDI_Lop3Y1Odprta | DIGITAL | IOD_STR | STR:.DI_Lop3Y1Odprta | [6 empty] | 6157 | 1 | 0x0340b9b0
STRDI_Lop3Y1Zaprta | DIGITAL | IOD_STR | STR:.DI_Lop3Y1Zaprta | [6 empty] | 6157 | 1 | 0x0340b9c0
STRDI_Lop4Y1Odprta | DIGITAL | IOD_STR | STR:.DI_Lop4Y1Odprta | [6 empty] | 6157 | 1 | 0x0340b9d0
STRDI_Lop4Y1Zaprta | DIGITAL | IOD_STR | STR:.DI_Lop4Y1Zaprta | [6 empty] | 6157 | 1 | 0x0340b9e0
STRDI_PotrditevAlarmov | DIGITAL | IOD_STR | STR:.DI_PotrditevAlarmov | [6 empty] | 6157 | 1 | 0x0340b9f0
STRDI_RazlitjeVodeEXP1 | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeEXP1 | [6 empty] | 6157 | 1 | 0x0340ba00
STRDI_RazlitjeVodeEXP2 | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeEXP2 | [6 empty] | 6157 | 1 | 0x0340ba10
STRDI_RazlitjeVodeHP | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeHP | [6 empty] | 6157 | 1 | 0x0340ba20
STRDI_RazlitjeVodeK1 | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeK1 | [6 empty] | 6157 | 1 | 0x0340ba30
STRDI_RazlitjeVodeK2 | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeK2 | [6 empty] | 6157 | 1 | 0x0340ba40
STRDI_RazlitjeVodeTP | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeTP | [6 empty] | 6157 | 1 | 0x0340ba50
STRDI_ToplPostGenErr | DIGITAL | IOD_STR | STR:.DI_ToplPostGenErr | [6 empty] | 6157 | 1 | 0x0340ba60
STRDI_UPS_Alarm | DIGITAL | IOD_STR | STR:.DI_UPS_Alarm | [6 empty] | 6157 | 1 | 0x0340ba70
STRDI_UPS_BatNacin | DIGITAL | IOD_STR | STR:.DI_UPS_BatNacin | [6 empty] | 6157 | 1 | 0x0340ba80
STRDI_UPS_Polnjenje | DIGITAL | IOD_STR | STR:.DI_UPS_Polnjenje | [6 empty] | 6157 | 1 | 0x0340ba90
STRDI_Vent1Auto | DIGITAL | IOD_STR | STR:.DI_Vent1Auto | [6 empty] | 6157 | 1 | 0x0340baa0
STRDI_Vent1kontON | DIGITAL | IOD_STR | STR:.DI_Vent1kontON | [6 empty] | 6157 | 1 | 0x0340bab0
STRDI_Vent2Auto | DIGITAL | IOD_STR | STR:.DI_Vent2Auto | [6 empty] | 6157 | 1 | 0x0340bac0
STRDI_Vent2kontON | DIGITAL | IOD_STR | STR:.DI_Vent2kontON | [6 empty] | 6157 | 1 | 0x0340bad0
STRDI_Vent3Auto | DIGITAL | IOD_STR | STR:.DI_Vent3Auto | [6 empty] | 6157 | 1 | 0x0340bae0
STRDI_Vent3kontON | DIGITAL | IOD_STR | STR:.DI_Vent3kontON | [6 empty] | 6157 | 1 | 0x0340baf0
STRDI_Vent4Auto | DIGITAL | IOD_STR | STR:.DI_Vent4Auto | [6 empty] | 6157 | 1 | 0x0340bb00
STRDI_Vent4kontON | DIGITAL | IOD_STR | STR:.DI_Vent4kontON | [6 empty] | 6157 | 1 | 0x0340bb10
STRDI_Vent5Auto | DIGITAL | IOD_STR | STR:.DI_Vent5Auto | [6 empty] | 6157 | 1 | 0x0340bb20
STRDI_Vent5kontON | DIGITAL | IOD_STR | STR:.DI_Vent5kontON | [6 empty] | 6157 | 1 | 0x0340bb30
STRDI_Vent6Auto | DIGITAL | IOD_STR | STR:.DI_Vent6Auto | [6 empty] | 6157 | 1 | 0x0340bb40
STRDI_Vent6kontON | DIGITAL | IOD_STR | STR:.DI_Vent6kontON | [6 empty] | 6157 | 1 | 0x0340bb50
STRDI_Vlaz1ERR | DIGITAL | IOD_STR | STR:.DI_Vlaz1ERR | [6 empty] | 6157 | 1 | 0x0340bb60
STRDI_Vlaz1ON | DIGITAL | IOD_STR | STR:.DI_Vlaz1ON | [6 empty] | 6157 | 1 | 0x0340bb70
STRDI_Vlaz2ERR | DIGITAL | IOD_STR | STR:.DI_Vlaz2ERR | [6 empty] | 6157 | 1 | 0x0340bb80
STRDI_Vlaz2ON | DIGITAL | IOD_STR | STR:.DI_Vlaz2ON | [6 empty] | 6157 | 1 | 0x0340bb90
STRDIN_230VAC_OK | DIGITAL | IOD_STR | STR:.DIN_230VAC_OK | [6 empty] | 6157 | 1 | 0x0340bba0
STRDIN_24VAC_OK | DIGITAL | IOD_STR | STR:.DIN_24VAC_OK | [6 empty] | 6157 | 1 | 0x0340bbb0
STRDIN_24VDC_OK | DIGITAL | IOD_STR | STR:.DIN_24VDC_OK | [6 empty] | 6157 | 1 | 0x0340bbc0
STRDIN_CrpHM1ERR | DIGITAL | IOD_STR | STR:.DIN_CrpHM1ERR | [6 empty] | 6157 | 1 | 0x0340bbd0
STRDIN_CrpHM2ERR | DIGITAL | IOD_STR | STR:.DIN_CrpHM2ERR | [6 empty] | 6157 | 1 | 0x0340bbe0
STRDIN_CrpHM3ERR | DIGITAL | IOD_STR | STR:.DIN_CrpHM3ERR | [6 empty] | 6157 | 1 | 0x0340bbf0
STRDIN_CrpHM4ERR | DIGITAL | IOD_STR | STR:.DIN_CrpHM4ERR | [6 empty] | 6157 | 1 | 0x0340bc00
STRDIN_HladStERR | DIGITAL | IOD_STR | STR:.DIN_HladStERR | [6 empty] | 6157 | 1 | 0x0340bc10
STRDIN_Klima1ERR | DIGITAL | IOD_STR | STR:.DIN_Klima1ERR | [6 empty] | 6157 | 1 | 0x0340bc20
STRDIN_Klima1filterZAM | DIGITAL | IOD_STR | STR:.DIN_Klima1filterZAM | [6 empty] | 6157 | 1 | 0x0340bc30
STRDIN_Klima1zascStON | DIGITAL | IOD_STR | STR:.DIN_Klima1zascStON | [6 empty] | 6157 | 1 | 0x0340bc40
STRDIN_Klima2ERR | DIGITAL | IOD_STR | STR:.DIN_Klima2ERR | [6 empty] | 6157 | 1 | 0x0340bc50
STRDIN_Klima2filterZAM | DIGITAL | IOD_STR | STR:.DIN_Klima2filterZAM | [6 empty] | 6157 | 1 | 0x0340bc60
STRDIN_Klima2zascStON | DIGITAL | IOD_STR | STR:.DIN_Klima2zascStON | [6 empty] | 6157 | 1 | 0x0340bc70
STRDIN_Komp1ERR | DIGITAL | IOD_STR | STR:.DIN_Komp1ERR | [6 empty] | 6157 | 1 | 0x0340bc80
STRDIN_Komp1ON | DIGITAL | IOD_STR | STR:.DIN_Komp1ON | [6 empty] | 6157 | 1 | 0x0340bc90
STRDIN_Komp2ERR | DIGITAL | IOD_STR | STR:.DIN_Komp2ERR | [6 empty] | 6157 | 1 | 0x0340bca0
STRDIN_Komp2ON | DIGITAL | IOD_STR | STR:.DIN_Komp2ON | [6 empty] | 6157 | 1 | 0x0340bcb0
STRDIN_Kond1zascStON | DIGITAL | IOD_STR | STR:.DIN_Kond1zascStON | [6 empty] | 6157 | 1 | 0x0340bcc0
STRDIN_Kond2zascStON | DIGITAL | IOD_STR | STR:.DIN_Kond2zascStON | [6 empty] | 6157 | 1 | 0x0340bcd0
STRDIN_Kond3zascStON | DIGITAL | IOD_STR | STR:.DIN_Kond3zascStON | [6 empty] | 6157 | 1 | 0x0340bce0
STRDIN_Vlaz1ERR | DIGITAL | IOD_STR | STR:.DIN_Vlaz1ERR | [6 empty] | 6157 | 1 | 0x0340bcf0
STRDIN_Vlaz2ERR | DIGITAL | IOD_STR | STR:.DIN_Vlaz2ERR | [6 empty] | 6157 | 1 | 0x0340bd00
STRDO_BojlerTE1Vklop | DIGITAL | IOD_STR | STR:.DO_BojlerTE1Vklop | [6 empty] | 6157 | 1 | 0x0340bd10
STRDO_CrpHM1Vklop | DIGITAL | IOD_STR | STR:.DO_CrpHM1Vklop | [6 empty] | 6157 | 1 | 0x0340bd20
STRDO_CrpHM2Vklop | DIGITAL | IOD_STR | STR:.DO_CrpHM2Vklop | [6 empty] | 6157 | 1 | 0x0340bd30
STRDO_CrpHM3Vklop | DIGITAL | IOD_STR | STR:.DO_CrpHM3Vklop | [6 empty] | 6157 | 1 | 0x0340bd40
STRDO_CrpHM4Vklop | DIGITAL | IOD_STR | STR:.DO_CrpHM4Vklop | [6 empty] | 6157 | 1 | 0x0340bd50
STRDO_CrpMN1Vklop | DIGITAL | IOD_STR | STR:.DO_CrpMN1Vklop | [6 empty] | 6157 | 1 | 0x0340bd60
STRDO_CrpTM11Vklop | DIGITAL | IOD_STR | STR:.DO_CrpTM11Vklop | [6 empty] | 6157 | 1 | 0x0340bd70
STRDO_GrundfosVklopL | DIGITAL | IOD_STR | STR:.DO_GrundfosVklopL | [6 empty] | 6157 | 1 | 0x0340bd80
STRDO_GrundfosVklopN | DIGITAL | IOD_STR | STR:.DO_GrundfosVklopN | [6 empty] | 6157 | 1 | 0x0340bd90
STRDO_HladStrIzklop | DIGITAL | IOD_STR | STR:.DO_HladStrIzklop | [6 empty] | 6157 | 1 | 0x0340bda0
STRDO_KE1Vklop | DIGITAL | IOD_STR | STR:.DO_KE1Vklop | [6 empty] | 6157 | 1 | 0x0340bdb0
STRDO_KE2Vklop | DIGITAL | IOD_STR | STR:.DO_KE2Vklop | [6 empty] | 6157 | 1 | 0x0340bdc0
STRDO_KE3Vklop | DIGITAL | IOD_STR | STR:.DO_KE3Vklop | [6 empty] | 6157 | 1 | 0x0340bdd0
STRDO_Klima1Vklop | DIGITAL | IOD_STR | STR:.DO_Klima1Vklop | [6 empty] | 6157 | 1 | 0x0340bde0
STRDO_Klima2Vklop | DIGITAL | IOD_STR | STR:.DO_Klima2Vklop | [6 empty] | 6157 | 1 | 0x0340bdf0
STRDO_Lop1PL1Vklop | DIGITAL | IOD_STR | STR:.DO_Lop1PL1Vklop | [6 empty] | 6157 | 1 | 0x0340be00
STRDO_Lop1PL2Vklop | DIGITAL | IOD_STR | STR:.DO_Lop1PL2Vklop | [6 empty] | 6157 | 1 | 0x0340be10
STRDO_Lop1PL3Vklop | DIGITAL | IOD_STR | STR:.DO_Lop1PL3Vklop | [6 empty] | 6157 | 1 | 0x0340be20
STRDO_Lop3Y1Vklop | DIGITAL | IOD_STR | STR:.DO_Lop3Y1Vklop | [6 empty] | 6157 | 1 | 0x0340be30
STRDO_Lop4Y1Vklop | DIGITAL | IOD_STR | STR:.DO_Lop4Y1Vklop | [6 empty] | 6157 | 1 | 0x0340be40
STRDO_RazE11_10Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_10Vklop | [6 empty] | 6157 | 1 | 0x0340be50
STRDO_RazE11_11Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_11Vklop | [6 empty] | 6157 | 1 | 0x0340be60
STRDO_RazE11_1Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_1Vklop | [6 empty] | 6157 | 1 | 0x0340be70
STRDO_RazE11_2Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_2Vklop | [6 empty] | 6157 | 1 | 0x0340be80
STRDO_RazE11_3Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_3Vklop | [6 empty] | 6157 | 1 | 0x0340be90
STRDO_RazE11_4Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_4Vklop | [6 empty] | 6157 | 1 | 0x0340bea0
STRDO_RazE11_5Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_5Vklop | [6 empty] | 6157 | 1 | 0x0340beb0
STRDO_RazE11_6Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_6Vklop | [6 empty] | 6157 | 1 | 0x0340bec0
STRDO_RazE11_7Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_7Vklop | [6 empty] | 6157 | 1 | 0x0340bed0
STRDO_RazE11_8Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_8Vklop | [6 empty] | 6157 | 1 | 0x0340bee0
STRDO_RazE11_9Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_9Vklop | [6 empty] | 6157 | 1 | 0x0340bef0
STRDO_RazE12_12Vklop | DIGITAL | IOD_STR | STR:.DO_RazE12_12Vklop | [6 empty] | 6157 | 1 | 0x0340bf00
STRDO_RazE12_13Vklop | DIGITAL | IOD_STR | STR:.DO_RazE12_13Vklop | [6 empty] | 6157 | 1 | 0x0340bf10
STRDO_RazE12_14Vklop | DIGITAL | IOD_STR | STR:.DO_RazE12_14Vklop | [6 empty] | 6157 | 1 | 0x0340bf20
STRDO_RazE12_15Vklop | DIGITAL | IOD_STR | STR:.DO_RazE12_15Vklop | [6 empty] | 6157 | 1 | 0x0340bf30
STRDO_RazE13_16Vklop | DIGITAL | IOD_STR | STR:.DO_RazE13_16Vklop | [6 empty] | 6157 | 1 | 0x0340bf40
STRDO_RazE13_17Vklop | DIGITAL | IOD_STR | STR:.DO_RazE13_17Vklop | [6 empty] | 6157 | 1 | 0x0340bf50
STRDO_RazE13_18Vklop | DIGITAL | IOD_STR | STR:.DO_RazE13_18Vklop | [6 empty] | 6157 | 1 | 0x0340bf60
STRDO_RazE13_19Vklop | DIGITAL | IOD_STR | STR:.DO_RazE13_19Vklop | [6 empty] | 6157 | 1 | 0x0340bf70
STRDO_RazE16_20Vklop | DIGITAL | IOD_STR | STR:.DO_RazE16_20Vklop | [6 empty] | 6157 | 1 | 0x0340bf80
STRDO_RazE16_21Vklop | DIGITAL | IOD_STR | STR:.DO_RazE16_21Vklop | [6 empty] | 6157 | 1 | 0x0340bf90
STRDO_RazE16_22Vklop | DIGITAL | IOD_STR | STR:.DO_RazE16_22Vklop | [6 empty] | 6157 | 1 | 0x0340bfa0
STRDO_RazE16_23Vklop | DIGITAL | IOD_STR | STR:.DO_RazE16_23Vklop | [6 empty] | 6157 | 1 | 0x0340bfb0
STRDO_RazE16_24Vklop | DIGITAL | IOD_STR | STR:.DO_RazE16_24Vklop | [6 empty] | 6157 | 1 | 0x0340bfc0
STRDO_Vent1Vklop | DIGITAL | IOD_STR | STR:.DO_Vent1Vklop | [6 empty] | 6157 | 1 | 0x0340bfd0
STRDO_Vent2Vklop | DIGITAL | IOD_STR | STR:.DO_Vent2Vklop | [6 empty] | 6157 | 1 | 0x0340bfe0
STRDO_Vent3Vklop | DIGITAL | IOD_STR | STR:.DO_Vent3Vklop | [6 empty] | 6157 | 1 | 0x0340bff0
STRDO_Vent4Vklop | DIGITAL | IOD_STR | STR:.DO_Vent4Vklop | [6 empty] | 6157 | 1 | 0x0340c000
STRDO_Vent5Vklop | DIGITAL | IOD_STR | STR:.DO_Vent5Vklop | [6 empty] | 6157 | 1 | 0x0340c010
STRDO_Vent6Vklop | DIGITAL | IOD_STR | STR:.DO_Vent6Vklop | [6 empty] | 6157 | 1 | 0x0340c020
STRErrComCirc1 | DIGITAL | IOD_STR | STR:.ErrComCirc[1] | [6 empty] | 6157 | 1 | 0x0340c030
STRErrComCirc2 | DIGITAL | IOD_STR | STR:.ErrComCirc[2] | [6 empty] | 6157 | 1 | 0x0340c040
STRErrComDanfossHM1 | DIGITAL | IOD_STR | STR:.ErrComDanfossHM[1] | [6 empty] | 6157 | 1 | 0x0340c050
STRErrComDanfossHM2 | DIGITAL | IOD_STR | STR:.ErrComDanfossHM[2] | [6 empty] | 6157 | 1 | 0x0340c060
STRErrComDanfossHM3 | DIGITAL | IOD_STR | STR:.ErrComDanfossHM[3] | [6 empty] | 6157 | 1 | 0x0340c070
STRErrComDanfossHM4 | DIGITAL | IOD_STR | STR:.ErrComDanfossHM[4] | [6 empty] | 6157 | 1 | 0x0340c080
STRErrComGrundfos0 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[0] | [6 empty] | 6157 | 1 | 0x0340c090
STRErrComGrundfos10 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[10] | [6 empty] | 6157 | 1 | 0x0340c0a0
STRErrComGrundfos11 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[11] | [6 empty] | 6157 | 1 | 0x0340c0b0
STRErrComGrundfos12 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[12] | [6 empty] | 6157 | 1 | 0x0340c0c0
STRErrComGrundfos13 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[13] | [6 empty] | 6157 | 1 | 0x0340c0d0
STRErrComGrundfos14 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[14] | [6 empty] | 6157 | 1 | 0x0340c0e0
STRErrComGrundfos1 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[1] | [6 empty] | 6157 | 1 | 0x0340c0f0
STRErrComGrundfos2 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[2] | [6 empty] | 6157 | 1 | 0x0340c100
STRErrComGrundfos3 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[3] | [6 empty] | 6157 | 1 | 0x0340c110
STRErrComGrundfos4 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[4] | [6 empty] | 6157 | 1 | 0x0340c120
STRErrComGrundfos5 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[5] | [6 empty] | 6157 | 1 | 0x0340c130
STRErrComGrundfos6 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[6] | [6 empty] | 6157 | 1 | 0x0340c140
STRErrComGrundfos7 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[7] | [6 empty] | 6157 | 1 | 0x0340c150
STRErrComGrundfos8 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[8] | [6 empty] | 6157 | 1 | 0x0340c160
STRErrComGrundfos9 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[9] | [6 empty] | 6157 | 1 | 0x0340c170
STRErrComHladStroj | DIGITAL | IOD_STR | STR:.ErrComHladStroj | [6 empty] | 6157 | 1 | 0x0340c180
STRErrComKlima1 | DIGITAL | IOD_STR | STR:.ErrComKlima[1] | [6 empty] | 6157 | 1 | 0x0340c190
STRErrComKlima2 | DIGITAL | IOD_STR | STR:.ErrComKlima[2] | [6 empty] | 6157 | 1 | 0x0340c1a0
STRErrCommScada | DIGITAL | IOD_STR | STR:.ErrCommScada | [6 empty] | 6157 | 1 | 0x0340c1b0
STRErrCommXC100 | DIGITAL | IOD_STR | STR:.ErrCommXC100 | [6 empty] | 6157 | 1 | 0x0340c1c0
STRErrComPanelPLC | DIGITAL | IOD_STR | STR:.ErrComPanelPLC | [6 empty] | 6157 | 1 | 0x0340c1d0
STRErrComPort2 | DIGITAL | IOD_STR | STR:.ErrComPort2 | [6 empty] | 6157 | 1 | 0x0340c1e0
STRErrComPort3 | DIGITAL | IOD_STR | STR:.ErrComPort3 | [6 empty] | 6157 | 1 | 0x0340c1f0
STRErrComPort4 | DIGITAL | IOD_STR | STR:.ErrComPort4 | [6 empty] | 6157 | 1 | 0x0340c200
STRErrComToplPost | DIGITAL | IOD_STR | STR:.ErrComToplPost | [6 empty] | 6157 | 1 | 0x0340c210
STRExp1TlakAlarm | DIGITAL | IOD_STR | STR:.Exp1TlakAlarm | [6 empty] | 6157 | 1 | 0x0340c220
STRExp1TlakMin | REAL | IOD_STR | STR:.Exp1TlakMin | 0 | 10 | 0 | 10 | bar | ####.# | 6157 | 1 | 0x0340c230
STRExp2TlakAlarm | DIGITAL | IOD_STR | STR:.Exp2TlakAlarm | [6 empty] | 6157 | 1 | 0x0340c240
STRExp2TlakMin | REAL | IOD_STR | STR:.Exp2TlakMin | 0 | 16 | 0 | 16 | bar | ####.# | 6157 | 1 | 0x0340c250
STRHladilniStrojOnOff | DIGITAL | IOD_STR | STR:.HladilniStrojOnOff | [6 empty] | 6157 | 1 | 0x0340c260
STRHladStrojFazeAlarm | DIGITAL | IOD_STR | STR:.HladStroj.FazeAlarm | [6 empty] | 6157 | 1 | 0x0340c270
STRHladStrojKompresorOljeAlarm | DIGITAL | IOD_STR | STR:.HladStroj.KompresorOljeAlarm | [6 empty] | 6157 | 1 | 0x0340c280
STRHladStrojKompresorOljeAlarmB | BYTE | IOD_STR | STR:.HladStroj.KompresorOljeAlarmB | [6 empty] | 6157 | 1 | 0x0340c290
STRHladStrojLANcarelAlarm | DIGITAL | IOD_STR | STR:.HladStroj.LANcarelAlarm | [6 empty] | 6157 | 1 | 0x0340c2a0
STRHladStrojNapaka | DIGITAL | IOD_STR | STR:.HladStroj.Napaka | [6 empty] | 6157 | 1 | 0x0340c2b0
STRHladStrojNizekPritiskAlarm | DIGITAL | IOD_STR | STR:.HladStroj.NizekPritiskAlarm | [6 empty] | 6157 | 1 | 0x0340c2c0
STRHladStrojNizekPritiskAlarmB | BYTE | IOD_STR | STR:.HladStroj.NizekPritiskAlarmB | [6 empty] | 6157 | 1 | 0x0340c2d0
STRHladStrojObratovalneUre | REAL | IOD_STR | STR:.HladStroj.ObratovalneUre |  |  |  |  | h | #### | 6157 | 1 | 0x0340c2d1
STRHladStrojObratovalneUreOpozorilo | DIGITAL | IOD_STR | STR:.HladStroj.ObratovalneUreOpozorilo | [6 empty] | 6157 | 1 | 0x0340c2e0
STRHladStrojObratovalneUreOpozoriloB | BYTE | IOD_STR | STR:.HladStroj.ObratovalneUreOpozoriloB | [6 empty] | 6157 | 1 | 0x0340c2f0
STRHladStrojOffByAlarms | DIGITAL | IOD_STR | STR:.HladStroj.OffByAlarms | [6 empty] | 6157 | 1 | 0x0340c300
STRHladStrojPretokAlarm | DIGITAL | IOD_STR | STR:.HladStroj.PretokAlarm | [6 empty] | 6157 | 1 | 0x0340c310
STRHladStrojPritiskSonda1 | REAL | IOD_STR | STR:.HladStroj.PritiskSonda1 | 0 | 5 | 0 | 5 | bar | ####.# | 6157 | 1 | 0x0340c320
STRHladStrojPritiskSonda2 | REAL | IOD_STR | STR:.HladStroj.PritiskSonda2 | 0 | 5 | 0 | 5 | bar | ####.# | 6157 | 1 | 0x0340c321
STRHladStrojPritiskSonda3 | REAL | IOD_STR | STR:.HladStroj.PritiskSonda3 | 0 | 5 | 0 | 5 | bar | ####.# | 6157 | 1 | 0x0340c322
STRHladStrojPritiskSonda4 | REAL | IOD_STR | STR:.HladStroj.PritiskSonda4 | 0 | 5 | 0 | 5 | bar | ####.# | 6157 | 1 | 0x0340c323
STRHladStrojRemoteOn | DIGITAL | IOD_STR | STR:.HladStroj.RemoteOn | [6 empty] | 6157 | 1 | 0x0340c330
STRHladStrojSenzorAlarm | DIGITAL | IOD_STR | STR:.HladStroj.SenzorAlarm | [6 empty] | 6157 | 1 | 0x0340c340
STRHladStrojSummerOperation | DIGITAL | IOD_STR | STR:.HladStroj.SummerOperation | [6 empty] | 6157 | 1 | 0x0340c350
STRHladStrojTemperaturaAlarm | DIGITAL | IOD_STR | STR:.HladStroj.TemperaturaAlarm | [6 empty] | 6157 | 1 | 0x0340c360
STRHladStrojTemperaturaAlarmB | BYTE | IOD_STR | STR:.HladStroj.TemperaturaAlarmB | [6 empty] | 6157 | 1 | 0x0340c370
STRHladStrojTempH2OvhodIzparilnika | REAL | IOD_STR | STR:.HladStroj.TempH2OvhodIzparilnika | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x0340c371
STRHladStrojTempIzhodnaSonda1 | REAL | IOD_STR | STR:.HladStroj.TempIzhodnaSonda1 | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x0340c372
STRHladStrojTempIzhodnaSonda3 | REAL | IOD_STR | STR:.HladStroj.TempIzhodnaSonda3 | 0 | 150 | 0 | 150 | °C | ####.# | 6157 | 1 | 0x0340c373
STRHladStrojTempSetPoint | REAL | IOD_STR | STR:.HladStroj.TempSetPoint | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x0340c374
STRHladStrojUnitOn | DIGITAL | IOD_STR | STR:.HladStroj.UnitOn | [6 empty] | 6157 | 1 | 0x0340c380
STRHladStrojUnitStatus | INT | IOD_STR | STR:.HladStroj.UnitStatus | [6 empty] | 6157 | 1 | 0x0340c390
STRHladStrojUraAlarm | DIGITAL | IOD_STR | STR:.HladStroj.UraAlarm | [6 empty] | 6157 | 1 | 0x0340c3a0
STRHladStrojVisokPritiskAlarm | DIGITAL | IOD_STR | STR:.HladStroj.VisokPritiskAlarm | [6 empty] | 6157 | 1 | 0x0340c3b0
STRHladStrojVisokPritiskAlarmB | BYTE | IOD_STR | STR:.HladStroj.VisokPritiskAlarmB | [6 empty] | 6157 | 1 | 0x0340c3c0
STRHladStrojVisokPritiskOpozorilo | DIGITAL | IOD_STR | STR:.HladStroj.VisokPritiskOpozorilo | [6 empty] | 6157 | 1 | 0x0340c3d0
STRHladStrojVisokPritiskOpozoriloB | BYTE | IOD_STR | STR:.HladStroj.VisokPritiskOpozoriloB | [6 empty] | 6157 | 1 | 0x0340c3e0
STRHladStrojZmrzalniAlarm | DIGITAL | IOD_STR | STR:.HladStroj.ZmrzalniAlarm | [6 empty] | 6157 | 1 | 0x0340c3f0
STRHladStrojZmrzalniAlarmB | BYTE | IOD_STR | STR:.HladStroj.ZmrzalniAlarmB | [6 empty] | 6157 | 1 | 0x0340c400
STRHladStrojErrors10 | DIGITAL | IOD_STR | STR:.HladStrojErrors[10] | [6 empty] | 6157 | 1 | 0x0340c410
STRHladStrojErrors11 | DIGITAL | IOD_STR | STR:.HladStrojErrors[11] | [6 empty] | 6157 | 1 | 0x0340c420
STRHladStrojErrors12 | DIGITAL | IOD_STR | STR:.HladStrojErrors[12] | [6 empty] | 6157 | 1 | 0x0340c430
STRHladStrojErrors13 | DIGITAL | IOD_STR | STR:.HladStrojErrors[13] | [6 empty] | 6157 | 1 | 0x0340c440
STRHladStrojErrors14 | DIGITAL | IOD_STR | STR:.HladStrojErrors[14] | [6 empty] | 6157 | 1 | 0x0340c450
STRHladStrojErrors15 | DIGITAL | IOD_STR | STR:.HladStrojErrors[15] | [6 empty] | 6157 | 1 | 0x0340c460
STRHladStrojErrors16 | DIGITAL | IOD_STR | STR:.HladStrojErrors[16] | [6 empty] | 6157 | 1 | 0x0340c470
STRHladStrojErrors1 | DIGITAL | IOD_STR | STR:.HladStrojErrors[1] | [6 empty] | 6157 | 1 | 0x0340c480
STRHladStrojErrors2 | DIGITAL | IOD_STR | STR:.HladStrojErrors[2] | [6 empty] | 6157 | 1 | 0x0340c490
STRHladStrojErrors3 | DIGITAL | IOD_STR | STR:.HladStrojErrors[3] | [6 empty] | 6157 | 1 | 0x0340c4a0
STRHladStrojErrors4 | DIGITAL | IOD_STR | STR:.HladStrojErrors[4] | [6 empty] | 6157 | 1 | 0x0340c4b0
STRHladStrojErrors5 | DIGITAL | IOD_STR | STR:.HladStrojErrors[5] | [6 empty] | 6157 | 1 | 0x0340c4c0
STRHladStrojErrors6 | DIGITAL | IOD_STR | STR:.HladStrojErrors[6] | [6 empty] | 6157 | 1 | 0x0340c4d0
STRHladStrojErrors7 | DIGITAL | IOD_STR | STR:.HladStrojErrors[7] | [6 empty] | 6157 | 1 | 0x0340c4e0
STRHladStrojErrors8 | DIGITAL | IOD_STR | STR:.HladStrojErrors[8] | [6 empty] | 6157 | 1 | 0x0340c4f0
STRHladStrojErrors9 | DIGITAL | IOD_STR | STR:.HladStrojErrors[9] | [6 empty] | 6157 | 1 | 0x0340c500
STRKlima1errors10 | DIGITAL | IOD_STR | STR:.Klima1errors[10] | [6 empty] | 6157 | 1 | 0x0340c510
STRKlima1errors11 | DIGITAL | IOD_STR | STR:.Klima1errors[11] | [6 empty] | 6157 | 1 | 0x0340c520
STRKlima1errors12 | DIGITAL | IOD_STR | STR:.Klima1errors[12] | [6 empty] | 6157 | 1 | 0x0340c530
STRKlima1errors1 | DIGITAL | IOD_STR | STR:.Klima1errors[1] | [6 empty] | 6157 | 1 | 0x0340c540
STRKlima1errors2 | DIGITAL | IOD_STR | STR:.Klima1errors[2] | [6 empty] | 6157 | 1 | 0x0340c550
STRKlima1errors3 | DIGITAL | IOD_STR | STR:.Klima1errors[3] | [6 empty] | 6157 | 1 | 0x0340c560
STRKlima1errors4 | DIGITAL | IOD_STR | STR:.Klima1errors[4] | [6 empty] | 6157 | 1 | 0x0340c570
STRKlima1errors5 | DIGITAL | IOD_STR | STR:.Klima1errors[5] | [6 empty] | 6157 | 1 | 0x0340c580
STRKlima1errors6 | DIGITAL | IOD_STR | STR:.Klima1errors[6] | [6 empty] | 6157 | 1 | 0x0340c590
STRKlima1errors7 | DIGITAL | IOD_STR | STR:.Klima1errors[7] | [6 empty] | 6157 | 1 | 0x0340c5a0
STRKlima1errors8 | DIGITAL | IOD_STR | STR:.Klima1errors[8] | [6 empty] | 6157 | 1 | 0x0340c5b0
STRKlima1errors9 | DIGITAL | IOD_STR | STR:.Klima1errors[9] | [6 empty] | 6157 | 1 | 0x0340c5c0
STRKlima2errors10 | DIGITAL | IOD_STR | STR:.Klima2errors[10] | [6 empty] | 6157 | 1 | 0x0340c5d0
STRKlima2errors11 | DIGITAL | IOD_STR | STR:.Klima2errors[11] | [6 empty] | 6157 | 1 | 0x0340c5e0
STRKlima2errors12 | DIGITAL | IOD_STR | STR:.Klima2errors[12] | [6 empty] | 6157 | 1 | 0x0340c5f0
STRKlima2errors1 | DIGITAL | IOD_STR | STR:.Klima2errors[1] | [6 empty] | 6157 | 1 | 0x0340c600
STRKlima2errors2 | DIGITAL | IOD_STR | STR:.Klima2errors[2] | [6 empty] | 6157 | 1 | 0x0340c610
STRKlima2errors3 | DIGITAL | IOD_STR | STR:.Klima2errors[3] | [6 empty] | 6157 | 1 | 0x0340c620
STRKlima2errors4 | DIGITAL | IOD_STR | STR:.Klima2errors[4] | [6 empty] | 6157 | 1 | 0x0340c630
STRKlima2errors5 | DIGITAL | IOD_STR | STR:.Klima2errors[5] | [6 empty] | 6157 | 1 | 0x0340c640
STRKlima2errors6 | DIGITAL | IOD_STR | STR:.Klima2errors[6] | [6 empty] | 6157 | 1 | 0x0340c650
STRKlima2errors7 | DIGITAL | IOD_STR | STR:.Klima2errors[7] | [6 empty] | 6157 | 1 | 0x0340c660
STRKlima2errors8 | DIGITAL | IOD_STR | STR:.Klima2errors[8] | [6 empty] | 6157 | 1 | 0x0340c670
STRKlima2errors9 | DIGITAL | IOD_STR | STR:.Klima2errors[9] | [6 empty] | 6157 | 1 | 0x0340c680
STRKlima1CrpalkaGrelnika | DIGITAL | IOD_STR | STR:.Klima[1].CrpalkaGrelnika | [6 empty] | 6157 | 1 | 0x0340c690
STRKlima1CrpalkaStatus | BYTE | IOD_STR | STR:.Klima[1].CrpalkaStatus | [6 empty] | 6157 | 1 | 0x0340c6a0
STRKlima1DelovanjeVentH1 | DIGITAL | IOD_STR | STR:.Klima[1].DelovanjeVentH1 | [6 empty] | 6157 | 1 | 0x0340c6b0
STRKlima1DelovanjeVentH2 | DIGITAL | IOD_STR | STR:.Klima[1].DelovanjeVentH2 | [6 empty] | 6157 | 1 | 0x0340c6c0
STRKlima1Deluje | DIGITAL | IOD_STR | STR:.Klima[1].Deluje | [6 empty] | 6157 | 1 | 0x0340c6d0
STRKlima1FilterError | DIGITAL | IOD_STR | STR:.Klima[1].FilterError | [6 empty] | 6157 | 1 | 0x0340c6e0
STRKlima1HitrostVentilatorjev | REAL | IOD_STR | STR:.Klima[1].HitrostVentilatorjev | 0 | 5000 | 0 | 5000 | obt/min | ####.# | 6157 | 1 | 0x0340c6f0
STRKlima1HitrostVentStatus | BYTE | IOD_STR | STR:.Klima[1].HitrostVentStatus | [6 empty] | 6157 | 1 | 0x0340c6f1
STRKlima1IzhodniVentStatus | BYTE | IOD_STR | STR:.Klima[1].IzhodniVentStatus | [6 empty] | 6157 | 1 | 0x0340c6f2
STRKlima1Napaka | DIGITAL | IOD_STR | STR:.Klima[1].Napaka | [6 empty] | 6157 | 1 | 0x0340c700
STRKlima1NapakaPriPretokuZraka | DIGITAL | IOD_STR | STR:.Klima[1].NapakaPriPretokuZraka | [6 empty] | 6157 | 1 | 0x0340c710
STRKlima1NastTempProstora | REAL | IOD_STR | STR:.Klima[1].NastTempProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x0340c720
STRKlima1ObratovalneUre | REAL | IOD_STR | STR:.Klima[1].ObratovalneUre |  |  |  |  | h | #### | 6157 | 1 | 0x0340c721
STRKlima1OkvaraRototerma | DIGITAL | IOD_STR | STR:.Klima[1].OkvaraRototerma | [6 empty] | 6157 | 1 | 0x0340c730
STRKlima1OkvaraVlazilne | DIGITAL | IOD_STR | STR:.Klima[1].OkvaraVlazilne | [6 empty] | 6157 | 1 | 0x0340c740
STRKlima1PozarError | DIGITAL | IOD_STR | STR:.Klima[1].PozarError | [6 empty] | 6157 | 1 | 0x0340c750
STRKlima1PozarniAlarm | DIGITAL | IOD_STR | STR:.Klima[1].PozarniAlarm | [6 empty] | 6157 | 1 | 0x0340c760
STRKlima1PreobremenitevMotCrpGr | DIGITAL | IOD_STR | STR:.Klima[1].PreobremenitevMotCrpGr | [6 empty] | 6157 | 1 | 0x0340c770
STRKlima1PreobremenitevMotVent | DIGITAL | IOD_STR | STR:.Klima[1].PreobremenitevMotVent | [6 empty] | 6157 | 1 | 0x0340c780
STRKlima1ProtizmrzAktivna | DIGITAL | IOD_STR | STR:.Klima[1].ProtizmrzAktivna | [6 empty] | 6157 | 1 | 0x0340c790
STRKlima1ProtizmrzZasc | REAL | IOD_STR | STR:.Klima[1].ProtizmrzZasc | -30 | 60 | -30 | 60 | °C | ####.# | 6157 | 1 | 0x0340c7a0
STRKlima1RezimDelovanja | REAL | IOD_STR | STR:.Klima[1].RezimDelovanja | [6 empty] | 6157 | 1 | 0x0340c7a1
STRKlima1SkupniAlarmA | DIGITAL | IOD_STR | STR:.Klima[1].SkupniAlarmA | [6 empty] | 6157 | 1 | 0x0340c7b0
STRKlima1SkupniAlarmB | DIGITAL | IOD_STR | STR:.Klima[1].SkupniAlarmB | [6 empty] | 6157 | 1 | 0x0340c7c0
STRKlima1TemperaturaDovoda | REAL | IOD_STR | STR:.Klima[1].TemperaturaDovoda | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x0340c7d0
STRKlima1TemperaturaProstora | REAL | IOD_STR | STR:.Klima[1].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x0340c7d1
STRKlima1TempPredRekN2 | REAL | IOD_STR | STR:.Klima[1].TempPredRekN2 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x0340c7d2
STRKlima1TempZaRekN2 | REAL | IOD_STR | STR:.Klima[1].TempZaRekN2 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x0340c7d3
STRKlima1TlakDovKanal | REAL | IOD_STR | STR:.Klima[1].TlakDovKanal | 0 | 5 | 0 | 5 | bar | ####.# | 6157 | 1 | 0x0340c7d4
STRKlima1TlakOdvodKanal | REAL | IOD_STR | STR:.Klima[1].TlakOdvodKanal | 0 | 5 | 0 | 5 | bar | ####.# | 6157 | 1 | 0x0340c7d5
STRKlima1VklopRegulacije | DIGITAL | IOD_STR | STR:.Klima[1].VklopRegulacije | [6 empty] | 6157 | 1 | 0x0340c7e0
STRKlima1VlagaDovoda | REAL | IOD_STR | STR:.Klima[1].VlagaDovoda | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340c7f0
STRKlima1VlagaVprostor | REAL | IOD_STR | STR:.Klima[1].VlagaVprostor | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340c7f1
STRKlima1ZamasenFilter | DIGITAL | IOD_STR | STR:.Klima[1].ZamasenFilter | [6 empty] | 6157 | 1 | 0x0340c800
STRKlima1ZunanjaTemp | REAL | IOD_STR | STR:.Klima[1].ZunanjaTemp | -30 | 60 | -30 | 60 | °C | ####.# | 6157 | 1 | 0x0340c810
STRKlima2CrpalkaGrelnika | DIGITAL | IOD_STR | STR:.Klima[2].CrpalkaGrelnika | [6 empty] | 6157 | 1 | 0x0340c820
STRKlima2CrpalkaStatus | BYTE | IOD_STR | STR:.Klima[2].CrpalkaStatus | [6 empty] | 6157 | 1 | 0x0340c830
STRKlima2DelovanjeVentH1 | DIGITAL | IOD_STR | STR:.Klima[2].DelovanjeVentH1 | [6 empty] | 6157 | 1 | 0x0340c840
STRKlima2DelovanjeVentH2 | DIGITAL | IOD_STR | STR:.Klima[2].DelovanjeVentH2 | [6 empty] | 6157 | 1 | 0x0340c850
STRKlima2Deluje | DIGITAL | IOD_STR | STR:.Klima[2].Deluje | [6 empty] | 6157 | 1 | 0x0340c860
STRKlima2FilterError | DIGITAL | IOD_STR | STR:.Klima[2].FilterError | [6 empty] | 6157 | 1 | 0x0340c870
STRKlima2HitrostVentilatorjev | REAL | IOD_STR | STR:.Klima[2].HitrostVentilatorjev | 0 | 5000 | 0 | 5000 | obt/min | ####.# | 6157 | 1 | 0x0340c880
STRKlima2HitrostVentStatus | BYTE | IOD_STR | STR:.Klima[2].HitrostVentStatus | [6 empty] | 6157 | 1 | 0x0340c881
STRKlima2IzhodniVentStatus | BYTE | IOD_STR | STR:.Klima[2].IzhodniVentStatus | [6 empty] | 6157 | 1 | 0x0340c882
STRKlima2Napaka | DIGITAL | IOD_STR | STR:.Klima[2].Napaka | [6 empty] | 6157 | 1 | 0x0340c890
STRKlima2NapakaPriPretokuZraka | DIGITAL | IOD_STR | STR:.Klima[2].NapakaPriPretokuZraka | [6 empty] | 6157 | 1 | 0x0340c8a0
STRKlima2NastTempProstora | REAL | IOD_STR | STR:.Klima[2].NastTempProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x0340c8b0
STRKlima2ObratovalneUre | REAL | IOD_STR | STR:.Klima[2].ObratovalneUre |  |  |  |  | h | #### | 6157 | 1 | 0x0340c8b1
STRKlima2OkvaraRototerma | DIGITAL | IOD_STR | STR:.Klima[2].OkvaraRototerma | [6 empty] | 6157 | 1 | 0x0340c8c0
STRKlima2OkvaraVlazilne | DIGITAL | IOD_STR | STR:.Klima[2].OkvaraVlazilne | [6 empty] | 6157 | 1 | 0x0340c8d0
STRKlima2PozarError | DIGITAL | IOD_STR | STR:.Klima[2].PozarError | [6 empty] | 6157 | 1 | 0x0340c8e0
STRKlima2PozarniAlarm | DIGITAL | IOD_STR | STR:.Klima[2].PozarniAlarm | [6 empty] | 6157 | 1 | 0x0340c8f0
STRKlima2PreobremenitevMotCrpGr | DIGITAL | IOD_STR | STR:.Klima[2].PreobremenitevMotCrpGr | [6 empty] | 6157 | 1 | 0x0340c900
STRKlima2PreobremenitevMotVent | DIGITAL | IOD_STR | STR:.Klima[2].PreobremenitevMotVent | [6 empty] | 6157 | 1 | 0x0340c910
STRKlima2ProtizmrzAktivna | DIGITAL | IOD_STR | STR:.Klima[2].ProtizmrzAktivna | [6 empty] | 6157 | 1 | 0x0340c920
STRKlima2ProtizmrzZasc | REAL | IOD_STR | STR:.Klima[2].ProtizmrzZasc | -30 | 50 | -30 | 50 | °C | ####.# | 6157 | 1 | 0x0340c930
STRKlima2RezimDelovanja | REAL | IOD_STR | STR:.Klima[2].RezimDelovanja | [6 empty] | 6157 | 1 | 0x0340c931
STRKlima2SkupniAlarmA | DIGITAL | IOD_STR | STR:.Klima[2].SkupniAlarmA | [6 empty] | 6157 | 1 | 0x0340c940
STRKlima2SkupniAlarmB | DIGITAL | IOD_STR | STR:.Klima[2].SkupniAlarmB | [6 empty] | 6157 | 1 | 0x0340c950
STRKlima2TemperaturaDovoda | REAL | IOD_STR | STR:.Klima[2].TemperaturaDovoda | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x0340c960
STRKlima2TemperaturaProstora | REAL | IOD_STR | STR:.Klima[2].TemperaturaProstora | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x0340c961
STRKlima2TempPredRekN2 | REAL | IOD_STR | STR:.Klima[2].TempPredRekN2 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x0340c962
STRKlima2TempZaRekN2 | REAL | IOD_STR | STR:.Klima[2].TempZaRekN2 | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x0340c963
STRKlima2TlakDovKanal | REAL | IOD_STR | STR:.Klima[2].TlakDovKanal | 0 | 5 | 0 | 5 | bar | ####.# | 6157 | 1 | 0x0340c964
STRKlima2TlakOdvodKanal | REAL | IOD_STR | STR:.Klima[2].TlakOdvodKanal | 0 | 5 | 0 | 5 | bar | ####.# | 6157 | 1 | 0x0340c965
STRKlima2VklopRegulacije | DIGITAL | IOD_STR | STR:.Klima[2].VklopRegulacije | [6 empty] | 6157 | 1 | 0x0340c970
STRKlima2VlagaDovoda | REAL | IOD_STR | STR:.Klima[2].VlagaDovoda | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340c980
STRKlima2VlagaVprostor | REAL | IOD_STR | STR:.Klima[2].VlagaVprostor | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340c981
STRKlima2ZamasenFilter | DIGITAL | IOD_STR | STR:.Klima[2].ZamasenFilter | [6 empty] | 6157 | 1 | 0x0340c990
STRKlima2ZunanjaTemp | REAL | IOD_STR | STR:.Klima[2].ZunanjaTemp | -30 | 60 | -30 | 60 | °C | ####.# | 6157 | 1 | 0x0340c9a0
STRKondEnotaOnOff1 | DIGITAL | IOD_STR | STR:.KondEnotaOnOff[1] | [6 empty] | 6157 | 1 | 0x0340c9b0
STRKondEnotaOnOff2 | DIGITAL | IOD_STR | STR:.KondEnotaOnOff[2] | [6 empty] | 6157 | 1 | 0x0340c9c0
STRKondEnotaOnOff3 | DIGITAL | IOD_STR | STR:.KondEnotaOnOff[3] | [6 empty] | 6157 | 1 | 0x0340c9d0
STRKontRezervaOnOff1 | DIGITAL | IOD_STR | STR:.KontRezervaOnOff[1] | [6 empty] | 6157 | 1 | 0x0340c9e0
STRKontRezervaOnOff2 | DIGITAL | IOD_STR | STR:.KontRezervaOnOff[2] | [6 empty] | 6157 | 1 | 0x0340c9f0
STRKontRezervaOnOff3 | DIGITAL | IOD_STR | STR:.KontRezervaOnOff[3] | [6 empty] | 6157 | 1 | 0x0340ca00
STRNapakaSenzorAI10 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[10] | [6 empty] | 6157 | 1 | 0x0340ca10
STRNapakaSenzorAI11 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[11] | [6 empty] | 6157 | 1 | 0x0340ca20
STRNapakaSenzorAI12 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[12] | [6 empty] | 6157 | 1 | 0x0340ca30
STRNapakaSenzorAI13 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[13] | [6 empty] | 6157 | 1 | 0x0340ca40
STRNapakaSenzorAI14 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[14] | [6 empty] | 6157 | 1 | 0x0340ca50
STRNapakaSenzorAI15 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[15] | [6 empty] | 6157 | 1 | 0x0340ca60
STRNapakaSenzorAI16 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[16] | [6 empty] | 6157 | 1 | 0x0340ca70
STRNapakaSenzorAI17 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[17] | [6 empty] | 6157 | 1 | 0x0340ca80
STRNapakaSenzorAI18 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[18] | [6 empty] | 6157 | 1 | 0x0340ca90
STRNapakaSenzorAI19 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[19] | [6 empty] | 6157 | 1 | 0x0340caa0
STRNapakaSenzorAI1 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[1] | [6 empty] | 6157 | 1 | 0x0340cab0
STRNapakaSenzorAI20 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[20] | [6 empty] | 6157 | 1 | 0x0340cac0
STRNapakaSenzorAI21 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[21] | [6 empty] | 6157 | 1 | 0x0340cad0
STRNapakaSenzorAI22 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[22] | [6 empty] | 6157 | 1 | 0x0340cae0
STRNapakaSenzorAI23 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[23] | [6 empty] | 6157 | 1 | 0x0340caf0
STRNapakaSenzorAI24 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[24] | [6 empty] | 6157 | 1 | 0x0340cb00
STRNapakaSenzorAI25 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[25] | [6 empty] | 6157 | 1 | 0x0340cb10
STRNapakaSenzorAI26 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[26] | [6 empty] | 6157 | 1 | 0x0340cb20
STRNapakaSenzorAI27 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[27] | [6 empty] | 6157 | 1 | 0x0340cb30
STRNapakaSenzorAI28 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[28] | [6 empty] | 6157 | 1 | 0x0340cb40
STRNapakaSenzorAI29 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[29] | [6 empty] | 6157 | 1 | 0x0340cb50
STRNapakaSenzorAI2 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[2] | [6 empty] | 6157 | 1 | 0x0340cb60
STRNapakaSenzorAI30 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[30] | [6 empty] | 6157 | 1 | 0x0340cb70
STRNapakaSenzorAI31 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[31] | [6 empty] | 6157 | 1 | 0x0340cb80
STRNapakaSenzorAI32 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[32] | [6 empty] | 6157 | 1 | 0x0340cb90
STRNapakaSenzorAI33 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[33] | [6 empty] | 6157 | 1 | 0x0340cba0
STRNapakaSenzorAI34 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[34] | [6 empty] | 6157 | 1 | 0x0340cbb0
STRNapakaSenzorAI35 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[35] | [6 empty] | 6157 | 1 | 0x0340cbc0
STRNapakaSenzorAI36 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[36] | [6 empty] | 6157 | 1 | 0x0340cbd0
STRNapakaSenzorAI37 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[37] | [6 empty] | 6157 | 1 | 0x0340cbe0
STRNapakaSenzorAI38 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[38] | [6 empty] | 6157 | 1 | 0x0340cbf0
STRNapakaSenzorAI39 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[39] | [6 empty] | 6157 | 1 | 0x0340cc00
STRNapakaSenzorAI3 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[3] | [6 empty] | 6157 | 1 | 0x0340cc10
STRNapakaSenzorAI40 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[40] | [6 empty] | 6157 | 1 | 0x0340cc20
STRNapakaSenzorAI4 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[4] | [6 empty] | 6157 | 1 | 0x0340cc30
STRNapakaSenzorAI5 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[5] | [6 empty] | 6157 | 1 | 0x0340cc40
STRNapakaSenzorAI6 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[6] | [6 empty] | 6157 | 1 | 0x0340cc50
STRNapakaSenzorAI7 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[7] | [6 empty] | 6157 | 1 | 0x0340cc60
STRNapakaSenzorAI8 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[8] | [6 empty] | 6157 | 1 | 0x0340cc70
STRNapakaSenzorAI9 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[9] | [6 empty] | 6157 | 1 | 0x0340cc80
STRNapakaSenzorHIA1 | DIGITAL | IOD_STR | STR:.NapakaSenzorHIA[1] | [6 empty] | 6157 | 1 | 0x0340cc90
STRNapakaSenzorHIA2 | DIGITAL | IOD_STR | STR:.NapakaSenzorHIA[2] | [6 empty] | 6157 | 1 | 0x0340cca0
STRNapakaSenzorHIA3 | DIGITAL | IOD_STR | STR:.NapakaSenzorHIA[3] | [6 empty] | 6157 | 1 | 0x0340ccb0
STRNapakaSenzorHIA4 | DIGITAL | IOD_STR | STR:.NapakaSenzorHIA[4] | [6 empty] | 6157 | 1 | 0x0340ccc0
STRNapakaSenzorTIA1 | DIGITAL | IOD_STR | STR:.NapakaSenzorTIA[1] | [6 empty] | 6157 | 1 | 0x0340ccd0
STRNapakaSenzorTIA2 | DIGITAL | IOD_STR | STR:.NapakaSenzorTIA[2] | [6 empty] | 6157 | 1 | 0x0340cce0
STRNapakaSenzorTIA3 | DIGITAL | IOD_STR | STR:.NapakaSenzorTIA[3] | [6 empty] | 6157 | 1 | 0x0340ccf0
STRNapakaSenzorTIA4 | DIGITAL | IOD_STR | STR:.NapakaSenzorTIA[4] | [6 empty] | 6157 | 1 | 0x0340cd00
STRPozarnaLoputaOnOffError1 | DIGITAL | IOD_STR | STR:.PozarnaLoputaOnOffError[1] | [6 empty] | 6157 | 1 | 0x0340cd10
STRPozarnaLoputaOnOffError2 | DIGITAL | IOD_STR | STR:.PozarnaLoputaOnOffError[2] | [6 empty] | 6157 | 1 | 0x0340cd20
STRPozarnaLoputaOnOffError3 | DIGITAL | IOD_STR | STR:.PozarnaLoputaOnOffError[3] | [6 empty] | 6157 | 1 | 0x0340cd30
STRPozarnaLoputaOnOffError4 | DIGITAL | IOD_STR | STR:.PozarnaLoputaOnOffError[4] | [6 empty] | 6157 | 1 | 0x0340cd40
STRPozarnaLoputaOnOffError5 | DIGITAL | IOD_STR | STR:.PozarnaLoputaOnOffError[5] | [6 empty] | 6157 | 1 | 0x0340cd50
STRPozarnaLoputaStatus1 | BYTE | IOD_STR | STR:.PozarnaLoputaStatus[1] | [6 empty] | 6157 | 1 | 0x0340cd60
STRPozarnaLoputaStatus2 | BYTE | IOD_STR | STR:.PozarnaLoputaStatus[2] | [6 empty] | 6157 | 1 | 0x0340cd61
STRPozarnaLoputaStatus3 | BYTE | IOD_STR | STR:.PozarnaLoputaStatus[3] | [6 empty] | 6157 | 1 | 0x0340cd62
STRPozarnaLoputaStatus4 | BYTE | IOD_STR | STR:.PozarnaLoputaStatus[4] | [6 empty] | 6157 | 1 | 0x0340cd63
STRPozarnaLoputaStatus5 | BYTE | IOD_STR | STR:.PozarnaLoputaStatus[5] | [6 empty] | 6157 | 1 | 0x0340cd64
STRPozarnaLoputOnOff1 | DIGITAL | IOD_STR | STR:.PozarnaLoputOnOff[1] | [6 empty] | 6157 | 1 | 0x0340cd70
STRPozarnaLoputOnOff2 | DIGITAL | IOD_STR | STR:.PozarnaLoputOnOff[2] | [6 empty] | 6157 | 1 | 0x0340cd80
STRPozarnaLoputOnOff3 | DIGITAL | IOD_STR | STR:.PozarnaLoputOnOff[3] | [6 empty] | 6157 | 1 | 0x0340cd90
STRPozarnaLoputOnOff4 | DIGITAL | IOD_STR | STR:.PozarnaLoputOnOff[4] | [6 empty] | 6157 | 1 | 0x0340cda0
STRPozarnaLoputOnOff5 | DIGITAL | IOD_STR | STR:.PozarnaLoputOnOff[5] | [6 empty] | 6157 | 1 | 0x0340cdb0
STRPozarniAlarm | DIGITAL | IOD_STR | STR:.PozarniAlarm | [6 empty] | 6157 | 1 | 0x0340cdc0
STRPrenosUrnika10 | DIGITAL | IOD_STR | STR:.PrenosUrnika[10] | [6 empty] | 6157 | 1 | 0x0340cdd0
STRPrenosUrnika11 | DIGITAL | IOD_STR | STR:.PrenosUrnika[11] | [6 empty] | 6157 | 1 | 0x0340cde0
STRPrenosUrnika12 | DIGITAL | IOD_STR | STR:.PrenosUrnika[12] | [6 empty] | 6157 | 1 | 0x0340cdf0
STRPrenosUrnika13 | DIGITAL | IOD_STR | STR:.PrenosUrnika[13] | [6 empty] | 6157 | 1 | 0x0340ce00
STRPrenosUrnika14 | DIGITAL | IOD_STR | STR:.PrenosUrnika[14] | [6 empty] | 6157 | 1 | 0x0340ce10
STRPrenosUrnika15 | DIGITAL | IOD_STR | STR:.PrenosUrnika[15] | [6 empty] | 6157 | 1 | 0x0340ce20
STRPrenosUrnika16 | DIGITAL | IOD_STR | STR:.PrenosUrnika[16] | [6 empty] | 6157 | 1 | 0x0340ce30
STRPrenosUrnika17 | DIGITAL | IOD_STR | STR:.PrenosUrnika[17] | [6 empty] | 6157 | 1 | 0x0340ce40
STRPrenosUrnika18 | DIGITAL | IOD_STR | STR:.PrenosUrnika[18] | [6 empty] | 6157 | 1 | 0x0340ce50
STRPrenosUrnika19 | DIGITAL | IOD_STR | STR:.PrenosUrnika[19] | [6 empty] | 6157 | 1 | 0x0340ce60
STRPrenosUrnika1 | DIGITAL | IOD_STR | STR:.PrenosUrnika[1] | [6 empty] | 6157 | 1 | 0x0340ce70
STRPrenosUrnika20 | DIGITAL | IOD_STR | STR:.PrenosUrnika[20] | [6 empty] | 6157 | 1 | 0x0340ce80
STRPrenosUrnika21 | DIGITAL | IOD_STR | STR:.PrenosUrnika[21] | [6 empty] | 6157 | 1 | 0x0340ce90
STRPrenosUrnika22 | DIGITAL | IOD_STR | STR:.PrenosUrnika[22] | [6 empty] | 6157 | 1 | 0x0340cea0
STRPrenosUrnika23 | DIGITAL | IOD_STR | STR:.PrenosUrnika[23] | [6 empty] | 6157 | 1 | 0x0340ceb0
STRPrenosUrnika24 | DIGITAL | IOD_STR | STR:.PrenosUrnika[24] | [6 empty] | 6157 | 1 | 0x0340cec0
STRPrenosUrnika25 | DIGITAL | IOD_STR | STR:.PrenosUrnika[25] | [6 empty] | 6157 | 1 | 0x0340ced0
STRPrenosUrnika2 | DIGITAL | IOD_STR | STR:.PrenosUrnika[2] | [6 empty] | 6157 | 1 | 0x0340cee0
STRPrenosUrnika3 | DIGITAL | IOD_STR | STR:.PrenosUrnika[3] | [6 empty] | 6157 | 1 | 0x0340cef0
STRPrenosUrnika4 | DIGITAL | IOD_STR | STR:.PrenosUrnika[4] | [6 empty] | 6157 | 1 | 0x0340cf00
STRPrenosUrnika5 | DIGITAL | IOD_STR | STR:.PrenosUrnika[5] | [6 empty] | 6157 | 1 | 0x0340cf10
STRPrenosUrnika6 | DIGITAL | IOD_STR | STR:.PrenosUrnika[6] | [6 empty] | 6157 | 1 | 0x0340cf20
STRPrenosUrnika7 | DIGITAL | IOD_STR | STR:.PrenosUrnika[7] | [6 empty] | 6157 | 1 | 0x0340cf30
STRPrenosUrnika8 | DIGITAL | IOD_STR | STR:.PrenosUrnika[8] | [6 empty] | 6157 | 1 | 0x0340cf40
STRPrenosUrnika9 | DIGITAL | IOD_STR | STR:.PrenosUrnika[9] | [6 empty] | 6157 | 1 | 0x0340cf50
STRRazsvetljavaOnOff10 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[10] | [6 empty] | 6157 | 1 | 0x0340cf60
STRRazsvetljavaOnOff11 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[11] | [6 empty] | 6157 | 1 | 0x0340cf70
STRRazsvetljavaOnOff12 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[12] | [6 empty] | 6157 | 1 | 0x0340cf80
STRRazsvetljavaOnOff13 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[13] | [6 empty] | 6157 | 1 | 0x0340cf90
STRRazsvetljavaOnOff14 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[14] | [6 empty] | 6157 | 1 | 0x0340cfa0
STRRazsvetljavaOnOff15 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[15] | [6 empty] | 6157 | 1 | 0x0340cfb0
STRRazsvetljavaOnOff16 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[16] | [6 empty] | 6157 | 1 | 0x0340cfc0
STRRazsvetljavaOnOff17 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[17] | [6 empty] | 6157 | 1 | 0x0340cfd0
STRRazsvetljavaOnOff18 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[18] | [6 empty] | 6157 | 1 | 0x0340cfe0
STRRazsvetljavaOnOff19 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[19] | [6 empty] | 6157 | 1 | 0x0340cff0
STRRazsvetljavaOnOff1 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[1] | [6 empty] | 6157 | 1 | 0x0340d000
STRRazsvetljavaOnOff20 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[20] | [6 empty] | 6157 | 1 | 0x0340d010
STRRazsvetljavaOnOff21 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[21] | [6 empty] | 6157 | 1 | 0x0340d020
STRRazsvetljavaOnOff22 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[22] | [6 empty] | 6157 | 1 | 0x0340d030
STRRazsvetljavaOnOff23 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[23] | [6 empty] | 6157 | 1 | 0x0340d040
STRRazsvetljavaOnOff24 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[24] | [6 empty] | 6157 | 1 | 0x0340d050
STRRazsvetljavaOnOff25 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[25] | [6 empty] | 6157 | 1 | 0x0340d060
STRRazsvetljavaOnOff2 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[2] | [6 empty] | 6157 | 1 | 0x0340d070
STRRazsvetljavaOnOff3 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[3] | [6 empty] | 6157 | 1 | 0x0340d080
STRRazsvetljavaOnOff4 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[4] | [6 empty] | 6157 | 1 | 0x0340d090
STRRazsvetljavaOnOff5 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[5] | [6 empty] | 6157 | 1 | 0x0340d0a0
STRRazsvetljavaOnOff6 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[6] | [6 empty] | 6157 | 1 | 0x0340d0b0
STRRazsvetljavaOnOff7 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[7] | [6 empty] | 6157 | 1 | 0x0340d0c0
STRRazsvetljavaOnOff8 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[8] | [6 empty] | 6157 | 1 | 0x0340d0d0
STRRazsvetljavaOnOff9 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[9] | [6 empty] | 6157 | 1 | 0x0340d0e0
STRRazsvetljavaRocno | DIGITAL | IOD_STR | STR:.RazsvetljavaRocno | [6 empty] | 6157 | 1 | 0x0340d0f0
STRrVersion | REAL | IOD_STR | STR:.rVersion | [6 empty] | 6157 | 1 | 0x0340d100
STRSenzorTempTIA1 | REAL | IOD_STR | STR:.SenzorTempTIA[1] | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x0340d101
STRSenzorTempTIA2 | REAL | IOD_STR | STR:.SenzorTempTIA[2] | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x0340d102
STRSenzorTempTIA3 | REAL | IOD_STR | STR:.SenzorTempTIA[3] | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x0340d103
STRSenzorTempTIA4 | REAL | IOD_STR | STR:.SenzorTempTIA[4] | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x0340d104
STRSenzorVlagaHIA1 | REAL | IOD_STR | STR:.SenzorVlagaHIA[1] | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340d105
STRSenzorVlagaHIA2 | REAL | IOD_STR | STR:.SenzorVlagaHIA[2] | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340d106
STRSenzorVlagaHIA3 | REAL | IOD_STR | STR:.SenzorVlagaHIA[3] | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340d107
STRSenzorVlagaHIA4 | REAL | IOD_STR | STR:.SenzorVlagaHIA[4] | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340d108
STRSetDateTime | DIGITAL | IOD_STR | STR:.SetDateTime | [6 empty] | 6157 | 1 | 0x0340d110
STRSetDateTimeDemand | DIGITAL | IOD_STR | STR:.SetDateTimeDemand | [6 empty] | 6157 | 1 | 0x0340d120
STRSetDateTimeError | DIGITAL | IOD_STR | STR:.SetDateTimeError | [6 empty] | 6157 | 1 | 0x0340d130
STRSetDateTimeFinished | DIGITAL | IOD_STR | STR:.SetDateTimeFinished | [6 empty] | 6157 | 1 | 0x0340d140
STRSetRemoteOnOff1 | DIGITAL | IOD_STR | STR:.SetRemoteOnOff[1] | [6 empty] | 6157 | 1 | 0x0340d150
STRSetRemoteOnOff2 | DIGITAL | IOD_STR | STR:.SetRemoteOnOff[2] | [6 empty] | 6157 | 1 | 0x0340d160
STRSlabaBaterijaPLC_A1 | DIGITAL | IOD_STR | STR:.SlabaBaterijaPLC_A1 | [6 empty] | 6157 | 1 | 0x0340d170
STRSlabaBaterijaPLC_A100 | DIGITAL | IOD_STR | STR:.SlabaBaterijaPLC_A100 | [6 empty] | 6157 | 1 | 0x0340d180
STRSO_BojlerTE1Vklop | DIGITAL | IOD_STR | STR:.SO_BojlerTE1Vklop | [6 empty] | 6157 | 1 | 0x0340d190
STRSO_CrpHM1Vklop | DIGITAL | IOD_STR | STR:.SO_CrpHM1Vklop | [6 empty] | 6157 | 1 | 0x0340d1a0
STRSO_CrpHM2Vklop | DIGITAL | IOD_STR | STR:.SO_CrpHM2Vklop | [6 empty] | 6157 | 1 | 0x0340d1b0
STRSO_CrpHM3Vklop | DIGITAL | IOD_STR | STR:.SO_CrpHM3Vklop | [6 empty] | 6157 | 1 | 0x0340d1c0
STRSO_CrpHM4Vklop | DIGITAL | IOD_STR | STR:.SO_CrpHM4Vklop | [6 empty] | 6157 | 1 | 0x0340d1d0
STRSO_CrpMN1Vklop | DIGITAL | IOD_STR | STR:.SO_CrpMN1Vklop | [6 empty] | 6157 | 1 | 0x0340d1e0
STRSO_CrpTM11Vklop | DIGITAL | IOD_STR | STR:.SO_CrpTM11Vklop | [6 empty] | 6157 | 1 | 0x0340d1f0
STRSO_HladStrVklop | DIGITAL | IOD_STR | STR:.SO_HladStrVklop | [6 empty] | 6157 | 1 | 0x0340d200
STRSO_KE1Vklop | DIGITAL | IOD_STR | STR:.SO_KE1Vklop | [6 empty] | 6157 | 1 | 0x0340d210
STRSO_KE2Vklop | DIGITAL | IOD_STR | STR:.SO_KE2Vklop | [6 empty] | 6157 | 1 | 0x0340d220
STRSO_KE3Vklop | DIGITAL | IOD_STR | STR:.SO_KE3Vklop | [6 empty] | 6157 | 1 | 0x0340d230
STRSO_rezerva1_3 | DIGITAL | IOD_STR | STR:.SO_rezerva1_3 | [6 empty] | 6157 | 1 | 0x0340d240
STRSO_rezerva1_4 | DIGITAL | IOD_STR | STR:.SO_rezerva1_4 | [6 empty] | 6157 | 1 | 0x0340d250
STRSO_rezerva1_5 | DIGITAL | IOD_STR | STR:.SO_rezerva1_5 | [6 empty] | 6157 | 1 | 0x0340d260
STRSO_Vent1Vklop | DIGITAL | IOD_STR | STR:.SO_Vent1Vklop | [6 empty] | 6157 | 1 | 0x0340d270
STRSO_Vent2Vklop | DIGITAL | IOD_STR | STR:.SO_Vent2Vklop | [6 empty] | 6157 | 1 | 0x0340d280
STRSO_Vent3Vklop | DIGITAL | IOD_STR | STR:.SO_Vent3Vklop | [6 empty] | 6157 | 1 | 0x0340d290
STRSO_Vent4Vklop | DIGITAL | IOD_STR | STR:.SO_Vent4Vklop | [6 empty] | 6157 | 1 | 0x0340d2a0
STRSO_Vent5Vklop | DIGITAL | IOD_STR | STR:.SO_Vent5Vklop | [6 empty] | 6157 | 1 | 0x0340d2b0
STRSO_Vent6Vklop | DIGITAL | IOD_STR | STR:.SO_Vent6Vklop | [6 empty] | 6157 | 1 | 0x0340d2c0
STRStatusKondenzEnota0 | BYTE | IOD_STR | STR:.StatusKondenzEnota[0] | [6 empty] | 6157 | 1 | 0x0340d2d0
STRStatusKondenzEnota1 | BYTE | IOD_STR | STR:.StatusKondenzEnota[1] | [6 empty] | 6157 | 1 | 0x0340d2d1
STRStatusKondenzEnota2 | BYTE | IOD_STR | STR:.StatusKondenzEnota[2] | [6 empty] | 6157 | 1 | 0x0340d2d2
STRStatusKondenzEnota3 | BYTE | IOD_STR | STR:.StatusKondenzEnota[3] | [6 empty] | 6157 | 1 | 0x0340d2d3
STRStatusKontaktor10 | BYTE | IOD_STR | STR:.StatusKontaktor[10] | [6 empty] | 6157 | 1 | 0x0340d2d4
STRStatusKontaktor11 | BYTE | IOD_STR | STR:.StatusKontaktor[11] | [6 empty] | 6157 | 1 | 0x0340d2d5
STRStatusKontaktor12 | BYTE | IOD_STR | STR:.StatusKontaktor[12] | [6 empty] | 6157 | 1 | 0x0340d2d6
STRStatusKontaktor13 | BYTE | IOD_STR | STR:.StatusKontaktor[13] | [6 empty] | 6157 | 1 | 0x0340d2d7
STRStatusKontaktor14 | BYTE | IOD_STR | STR:.StatusKontaktor[14] | [6 empty] | 6157 | 1 | 0x0340d2d8
STRStatusKontaktor15 | BYTE | IOD_STR | STR:.StatusKontaktor[15] | [6 empty] | 6157 | 1 | 0x0340d2d9
STRStatusKontaktor16 | BYTE | IOD_STR | STR:.StatusKontaktor[16] | [6 empty] | 6157 | 1 | 0x0340d2da
STRStatusKontaktor17 | BYTE | IOD_STR | STR:.StatusKontaktor[17] | [6 empty] | 6157 | 1 | 0x0340d2db
STRStatusKontaktor18 | BYTE | IOD_STR | STR:.StatusKontaktor[18] | [6 empty] | 6157 | 1 | 0x0340d2dc
STRStatusKontaktor19 | BYTE | IOD_STR | STR:.StatusKontaktor[19] | [6 empty] | 6157 | 1 | 0x0340d2dd
STRStatusKontaktor1 | BYTE | IOD_STR | STR:.StatusKontaktor[1] | [6 empty] | 6157 | 1 | 0x0340d2de
STRStatusKontaktor20 | BYTE | IOD_STR | STR:.StatusKontaktor[20] | [6 empty] | 6157 | 1 | 0x0340d2df
STRStatusKontaktor21 | BYTE | IOD_STR | STR:.StatusKontaktor[21] | [6 empty] | 6157 | 1 | 0x0340d2e0
STRStatusKontaktor22 | BYTE | IOD_STR | STR:.StatusKontaktor[22] | [6 empty] | 6157 | 1 | 0x0340d2e1
STRStatusKontaktor23 | BYTE | IOD_STR | STR:.StatusKontaktor[23] | [6 empty] | 6157 | 1 | 0x0340d2e2
STRStatusKontaktor24 | BYTE | IOD_STR | STR:.StatusKontaktor[24] | [6 empty] | 6157 | 1 | 0x0340d2e3
STRStatusKontaktor25 | BYTE | IOD_STR | STR:.StatusKontaktor[25] | [6 empty] | 6157 | 1 | 0x0340d2e4
STRStatusKontaktor2 | BYTE | IOD_STR | STR:.StatusKontaktor[2] | [6 empty] | 6157 | 1 | 0x0340d2e5
STRStatusKontaktor3 | BYTE | IOD_STR | STR:.StatusKontaktor[3] | [6 empty] | 6157 | 1 | 0x0340d2e6
STRStatusKontaktor4 | BYTE | IOD_STR | STR:.StatusKontaktor[4] | [6 empty] | 6157 | 1 | 0x0340d2e7
STRStatusKontaktor5 | BYTE | IOD_STR | STR:.StatusKontaktor[5] | [6 empty] | 6157 | 1 | 0x0340d2e8
STRStatusKontaktor6 | BYTE | IOD_STR | STR:.StatusKontaktor[6] | [6 empty] | 6157 | 1 | 0x0340d2e9
STRStatusKontaktor7 | BYTE | IOD_STR | STR:.StatusKontaktor[7] | [6 empty] | 6157 | 1 | 0x0340d2ea
STRStatusKontaktor8 | BYTE | IOD_STR | STR:.StatusKontaktor[8] | [6 empty] | 6157 | 1 | 0x0340d2eb
STRStatusKontaktor9 | BYTE | IOD_STR | STR:.StatusKontaktor[9] | [6 empty] | 6157 | 1 | 0x0340d2ec
STRStatusPreklopke10 | BYTE | IOD_STR | STR:.StatusPreklopke[10] | [6 empty] | 6157 | 1 | 0x0340d2ed
STRStatusPreklopke11 | BYTE | IOD_STR | STR:.StatusPreklopke[11] | [6 empty] | 6157 | 1 | 0x0340d2ee
STRStatusPreklopke12 | BYTE | IOD_STR | STR:.StatusPreklopke[12] | [6 empty] | 6157 | 1 | 0x0340d2ef
STRStatusPreklopke13 | BYTE | IOD_STR | STR:.StatusPreklopke[13] | [6 empty] | 6157 | 1 | 0x0340d2f0
STRStatusPreklopke14 | BYTE | IOD_STR | STR:.StatusPreklopke[14] | [6 empty] | 6157 | 1 | 0x0340d2f1
STRStatusPreklopke15 | BYTE | IOD_STR | STR:.StatusPreklopke[15] | [6 empty] | 6157 | 1 | 0x0340d2f2
STRStatusPreklopke16 | BYTE | IOD_STR | STR:.StatusPreklopke[16] | [6 empty] | 6157 | 1 | 0x0340d2f3
STRStatusPreklopke17 | BYTE | IOD_STR | STR:.StatusPreklopke[17] | [6 empty] | 6157 | 1 | 0x0340d2f4
STRStatusPreklopke18 | BYTE | IOD_STR | STR:.StatusPreklopke[18] | [6 empty] | 6157 | 1 | 0x0340d2f5
STRStatusPreklopke19 | BYTE | IOD_STR | STR:.StatusPreklopke[19] | [6 empty] | 6157 | 1 | 0x0340d2f6
STRStatusPreklopke1 | BYTE | IOD_STR | STR:.StatusPreklopke[1] | [6 empty] | 6157 | 1 | 0x0340d2f7
STRStatusPreklopke20 | BYTE | IOD_STR | STR:.StatusPreklopke[20] | [6 empty] | 6157 | 1 | 0x0340d2f8
STRStatusPreklopke21 | BYTE | IOD_STR | STR:.StatusPreklopke[21] | [6 empty] | 6157 | 1 | 0x0340d2f9
STRStatusPreklopke22 | BYTE | IOD_STR | STR:.StatusPreklopke[22] | [6 empty] | 6157 | 1 | 0x0340d2fa
STRStatusPreklopke23 | BYTE | IOD_STR | STR:.StatusPreklopke[23] | [6 empty] | 6157 | 1 | 0x0340d2fb
STRStatusPreklopke24 | BYTE | IOD_STR | STR:.StatusPreklopke[24] | [6 empty] | 6157 | 1 | 0x0340d2fc
STRStatusPreklopke25 | BYTE | IOD_STR | STR:.StatusPreklopke[25] | [6 empty] | 6157 | 1 | 0x0340d2fd
STRStatusPreklopke2 | BYTE | IOD_STR | STR:.StatusPreklopke[2] | [6 empty] | 6157 | 1 | 0x0340d2fe
STRStatusPreklopke3 | BYTE | IOD_STR | STR:.StatusPreklopke[3] | [6 empty] | 6157 | 1 | 0x0340d2ff
STRStatusPreklopke4 | BYTE | IOD_STR | STR:.StatusPreklopke[4] | [6 empty] | 6157 | 1 | 0x0340d300
STRStatusPreklopke5 | BYTE | IOD_STR | STR:.StatusPreklopke[5] | [6 empty] | 6157 | 1 | 0x0340d301
STRStatusPreklopke6 | BYTE | IOD_STR | STR:.StatusPreklopke[6] | [6 empty] | 6157 | 1 | 0x0340d302
STRStatusPreklopke7 | BYTE | IOD_STR | STR:.StatusPreklopke[7] | [6 empty] | 6157 | 1 | 0x0340d303
STRStatusPreklopke8 | BYTE | IOD_STR | STR:.StatusPreklopke[8] | [6 empty] | 6157 | 1 | 0x0340d304
STRStatusPreklopke9 | BYTE | IOD_STR | STR:.StatusPreklopke[9] | [6 empty] | 6157 | 1 | 0x0340d305
STRTEgrelecNaTemp | DIGITAL | IOD_STR | STR:.TEgrelecNaTemp | [6 empty] | 6157 | 1 | 0x0340d310
STRTEgrelecTempMAX | REAL | IOD_STR | STR:.TEgrelecTempMAX | 0 | 100 | 0 | 100 | °C | ####.# | 6157 | 1 | 0x0340d320
STRTEgrelecTempMIN | REAL | IOD_STR | STR:.TEgrelecTempMIN | 0 | 100 | 0 | 100 | °C | ####.# | 6157 | 1 | 0x0340d321
STRTEgrelecTempVklop | DIGITAL | IOD_STR | STR:.TEgrelecTempVklop | [6 empty] | 6157 | 1 | 0x0340d330
STRTempAlarmPoint | REAL | IOD_STR | STR:.TempAlarmPoint | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x0340d340
STRTempTIApovprecna | REAL | IOD_STR | STR:.TempTIApovprecna | 0 | 60 | 0 | 60 | °C | ####.# | 6157 | 1 | 0x0340d341
STRTempTSprevisoka | DIGITAL | IOD_STR | STR:.TempTSprevisoka | [6 empty] | 6157 | 1 | 0x0340d350
STRToplPostHKcrpalkaON | DIGITAL | IOD_STR | STR:.ToplPost.HKcrpalkaON | [6 empty] | 6157 | 1 | 0x0340d360
STRToplPostHKcrpDnevniRezim | DIGITAL | IOD_STR | STR:.ToplPost.HKcrpDnevniRezim | [6 empty] | 6157 | 1 | 0x0340d370
STRToplPostHKcrpNocniRezim | DIGITAL | IOD_STR | STR:.ToplPost.HKcrpNocniRezim | [6 empty] | 6157 | 1 | 0x0340d380
STRToplPostHKdotokNastTemp | REAL | IOD_STR | STR:.ToplPost.HKdotokNastTemp | 0 | 100 | 0 | 100 | °C | ####.# | 6157 | 1 | 0x0340d390
STRToplPostHKdotokTemp | REAL | IOD_STR | STR:.ToplPost.HKdotokTemp | 0 | 100 | 0 | 100 | °C | ####.# | 6157 | 1 | 0x0340d391
STRToplPostHKpovtatekTemp | REAL | IOD_STR | STR:.ToplPost.HKpovtatekTemp | 0 | 100 | 0 | 100 | °C | ####.# | 6157 | 1 | 0x0340d392
STRToplPostHKpovtratekNastTemp | REAL | IOD_STR | STR:.ToplPost.HKpovtratekNastTemp | 0 | 100 | 0 | 100 | °C | ####.# | 6157 | 1 | 0x0340d393
STRToplPostHKrocniRezim | DIGITAL | IOD_STR | STR:.ToplPost.HKrocniRezim | [6 empty] | 6157 | 1 | 0x0340d3a0
STRToplPostHKzunanjaTemp | REAL | IOD_STR | STR:.ToplPost.HKzunanjaTemp | -30 | 60 | -30 | 60 | °C | ####.# | 6157 | 1 | 0x0340d3b0
STRToplPostNapakaRegister | INT | IOD_STR | STR:.ToplPost.NapakaRegister | [6 empty] | 6157 | 1 | 0x0340d3b1
STRToplPostSkupnaNapaka | DIGITAL | IOD_STR | STR:.ToplPost.SkupnaNapaka | [6 empty] | 6157 | 1 | 0x0340d3c0
STRToplPostTVcrpalkaON | DIGITAL | IOD_STR | STR:.ToplPost.TVcrpalkaON | [6 empty] | 6157 | 1 | 0x0340d3d0
STRToplPostTVdotokNastTemp | REAL | IOD_STR | STR:.ToplPost.TVdotokNastTemp | 0 | 100 | 0 | 100 | °C | ####.# | 6157 | 1 | 0x0340d3e0
STRToplPostTVdotokTemp | REAL | IOD_STR | STR:.ToplPost.TVdotokTemp | 0 | 100 | 0 | 100 | °C | ####.# | 6157 | 1 | 0x0340d3e1
STRToplPostTVpovratekTemp | REAL | IOD_STR | STR:.ToplPost.TVpovratekTemp | 0 | 100 | 0 | 100 | °C | ####.# | 6157 | 1 | 0x0340d3e2
STRToplPostTVrezervoarTemp | REAL | IOD_STR | STR:.ToplPost.TVrezervoarTemp | 0 | 100 | 0 | 100 | °C | ####.# | 6157 | 1 | 0x0340d3e3
STRToplPostTVrocniRezim | DIGITAL | IOD_STR | STR:.ToplPost.TVrocniRezim | [6 empty] | 6157 | 1 | 0x0340d3f0
STRToplPostErrors0 | DIGITAL | IOD_STR | STR:.ToplPostErrors[0] | [6 empty] | 6157 | 1 | 0x0340d400
STRToplPostErrors10 | DIGITAL | IOD_STR | STR:.ToplPostErrors[10] | [6 empty] | 6157 | 1 | 0x0340d410
STRToplPostErrors11 | DIGITAL | IOD_STR | STR:.ToplPostErrors[11] | [6 empty] | 6157 | 1 | 0x0340d420
STRToplPostErrors12 | DIGITAL | IOD_STR | STR:.ToplPostErrors[12] | [6 empty] | 6157 | 1 | 0x0340d430
STRToplPostErrors13 | DIGITAL | IOD_STR | STR:.ToplPostErrors[13] | [6 empty] | 6157 | 1 | 0x0340d440
STRToplPostErrors14 | DIGITAL | IOD_STR | STR:.ToplPostErrors[14] | [6 empty] | 6157 | 1 | 0x0340d450
STRToplPostErrors15 | DIGITAL | IOD_STR | STR:.ToplPostErrors[15] | [6 empty] | 6157 | 1 | 0x0340d460
STRToplPostErrors16 | DIGITAL | IOD_STR | STR:.ToplPostErrors[16] | [6 empty] | 6157 | 1 | 0x0340d470
STRToplPostErrors17 | DIGITAL | IOD_STR | STR:.ToplPostErrors[17] | [6 empty] | 6157 | 1 | 0x0340d480
STRToplPostErrors1 | DIGITAL | IOD_STR | STR:.ToplPostErrors[1] | [6 empty] | 6157 | 1 | 0x0340d490
STRToplPostErrors2 | DIGITAL | IOD_STR | STR:.ToplPostErrors[2] | [6 empty] | 6157 | 1 | 0x0340d4a0
STRToplPostErrors3 | DIGITAL | IOD_STR | STR:.ToplPostErrors[3] | [6 empty] | 6157 | 1 | 0x0340d4b0
STRToplPostErrors4 | DIGITAL | IOD_STR | STR:.ToplPostErrors[4] | [6 empty] | 6157 | 1 | 0x0340d4c0
STRToplPostErrors5 | DIGITAL | IOD_STR | STR:.ToplPostErrors[5] | [6 empty] | 6157 | 1 | 0x0340d4d0
STRToplPostErrors6 | DIGITAL | IOD_STR | STR:.ToplPostErrors[6] | [6 empty] | 6157 | 1 | 0x0340d4e0
STRToplPostErrors7 | DIGITAL | IOD_STR | STR:.ToplPostErrors[7] | [6 empty] | 6157 | 1 | 0x0340d4f0
STRToplPostErrors8 | DIGITAL | IOD_STR | STR:.ToplPostErrors[8] | [6 empty] | 6157 | 1 | 0x0340d500
STRToplPostErrors9 | DIGITAL | IOD_STR | STR:.ToplPostErrors[9] | [6 empty] | 6157 | 1 | 0x0340d510
STRTYventilMax1 | REAL | IOD_STR | STR:.TYventilMax[1] | 0 | 100 | 0 | 100 | % | ### | 6157 | 1 | 0x0340d520
STRTYventilMax2 | REAL | IOD_STR | STR:.TYventilMax[2] | 0 | 100 | 0 | 100 | % | ### | 6157 | 1 | 0x0340d521
STRTYventilMax3 | REAL | IOD_STR | STR:.TYventilMax[3] | 0 | 100 | 0 | 100 | % | ### | 6157 | 1 | 0x0340d522
STRTYventilMax4 | REAL | IOD_STR | STR:.TYventilMax[4] | 0 | 100 | 0 | 100 | % | ### | 6157 | 1 | 0x0340d523
STRTYventilMin1 | REAL | IOD_STR | STR:.TYventilMin[1] | 0 | 100 | 0 | 100 | % | ### | 6157 | 1 | 0x0340d524
STRTYventilMin2 | REAL | IOD_STR | STR:.TYventilMin[2] | 0 | 100 | 0 | 100 | % | ### | 6157 | 1 | 0x0340d525
STRTYventilMin3 | REAL | IOD_STR | STR:.TYventilMin[3] | 0 | 100 | 0 | 100 | % | ### | 6157 | 1 | 0x0340d526
STRTYventilMin4 | REAL | IOD_STR | STR:.TYventilMin[4] | 0 | 100 | 0 | 100 | % | ### | 6157 | 1 | 0x0340d527
STRTYventilNaTemp1 | DIGITAL | IOD_STR | STR:.TYventilNaTemp[1] | [6 empty] | 6157 | 1 | 0x0340d530
STRTYventilNaTemp2 | DIGITAL | IOD_STR | STR:.TYventilNaTemp[2] | [6 empty] | 6157 | 1 | 0x0340d540
STRTYventilNaTemp3 | DIGITAL | IOD_STR | STR:.TYventilNaTemp[3] | [6 empty] | 6157 | 1 | 0x0340d550
STRTYventilNaTemp4 | DIGITAL | IOD_STR | STR:.TYventilNaTemp[4] | [6 empty] | 6157 | 1 | 0x0340d560
STRTYventilTempRazlika1 | REAL | IOD_STR | STR:.TYventilTempRazlika[1] | 0 | 100 | 0 | 100 | °C | ####.# | 6157 | 1 | 0x0340d570
STRTYventilTempRazlika2 | REAL | IOD_STR | STR:.TYventilTempRazlika[2] | 0 | 100 | 0 | 100 | °C | ####.# | 6157 | 1 | 0x0340d571
STRTYventilTempRazlika3 | REAL | IOD_STR | STR:.TYventilTempRazlika[3] | 0 | 100 | 0 | 100 | °C | ####.# | 6157 | 1 | 0x0340d572
STRTYventilTempRazlika4 | REAL | IOD_STR | STR:.TYventilTempRazlika[4] | 0 | 100 | 0 | 100 | °C | ####.# | 6157 | 1 | 0x0340d573
STRUrnik_SCtoXCpot | INT | IOD_STR | STR:.Urnik_SCtoXCpot | [6 empty] | 6157 | 1 | 0x0340d574
STRUrnik_SCtoXCzah | INT | IOD_STR | STR:.Urnik_SCtoXCzah | [6 empty] | 6157 | 1 | 0x0340d575
STRUrnik_XCtoSCpot | INT | IOD_STR | STR:.Urnik_XCtoSCpot | [6 empty] | 6157 | 1 | 0x0340d576
STRUrnik_XCtoSCzah | INT | IOD_STR | STR:.Urnik_XCtoSCzah | [6 empty] | 6157 | 1 | 0x0340d577
STRUrnikSCtoXCDan1Off1Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340d578
STRUrnikSCtoXCDan1Off1Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340d579
STRUrnikSCtoXCDan1Off2Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340d57a
STRUrnikSCtoXCDan1Off2Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340d57b
STRUrnikSCtoXCDan1Off3Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340d57c
STRUrnikSCtoXCDan1Off3Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340d57d
STRUrnikSCtoXCDan1On1Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340d57e
STRUrnikSCtoXCDan1On1Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340d57f
STRUrnikSCtoXCDan1On2Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340d580
STRUrnikSCtoXCDan1On2Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340d581
STRUrnikSCtoXCDan1On3Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340d582
STRUrnikSCtoXCDan1On3Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340d583
STRUrnikSCtoXCDan2Off1Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340d584
STRUrnikSCtoXCDan2Off1Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340d585
STRUrnikSCtoXCDan2Off2Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340d586
STRUrnikSCtoXCDan2Off2Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340d587
STRUrnikSCtoXCDan2Off3Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340d588
STRUrnikSCtoXCDan2Off3Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340d589
STRUrnikSCtoXCDan2On1Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340d58a
STRUrnikSCtoXCDan2On1Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340d58b
STRUrnikSCtoXCDan2On2Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340d58c
STRUrnikSCtoXCDan2On2Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340d58d
STRUrnikSCtoXCDan2On3Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340d58e
STRUrnikSCtoXCDan2On3Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340d58f
STRUrnikSCtoXCDan3Off1Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340d590
STRUrnikSCtoXCDan3Off1Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340d591
STRUrnikSCtoXCDan3Off2Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340d592
STRUrnikSCtoXCDan3Off2Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340d593
STRUrnikSCtoXCDan3Off3Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340d594
STRUrnikSCtoXCDan3Off3Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340d595
STRUrnikSCtoXCDan3On1Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340d596
STRUrnikSCtoXCDan3On1Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340d597
STRUrnikSCtoXCDan3On2Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340d598
STRUrnikSCtoXCDan3On2Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340d599
STRUrnikSCtoXCDan3On3Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340d59a
STRUrnikSCtoXCDan3On3Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340d59b
STRUrnikSCtoXCDan4Off1Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340d59c
STRUrnikSCtoXCDan4Off1Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340d59d
STRUrnikSCtoXCDan4Off2Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340d59e
STRUrnikSCtoXCDan4Off2Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340d59f
STRUrnikSCtoXCDan4Off3Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340d5a0
STRUrnikSCtoXCDan4Off3Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340d5a1
STRUrnikSCtoXCDan4On1Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340d5a2
STRUrnikSCtoXCDan4On1Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340d5a3
STRUrnikSCtoXCDan4On2Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340d5a4
STRUrnikSCtoXCDan4On2Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340d5a5
STRUrnikSCtoXCDan4On3Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340d5a6
STRUrnikSCtoXCDan4On3Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340d5a7
STRUrnikSCtoXCDan5Off1Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340d5a8
STRUrnikSCtoXCDan5Off1Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340d5a9
STRUrnikSCtoXCDan5Off2Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340d5aa
STRUrnikSCtoXCDan5Off2Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340d5ab
STRUrnikSCtoXCDan5Off3Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340d5ac
STRUrnikSCtoXCDan5Off3Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340d5ad
STRUrnikSCtoXCDan5On1Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340d5ae
STRUrnikSCtoXCDan5On1Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340d5af
STRUrnikSCtoXCDan5On2Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340d5b0
STRUrnikSCtoXCDan5On2Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340d5b1
STRUrnikSCtoXCDan5On3Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340d5b2
STRUrnikSCtoXCDan5On3Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340d5b3
STRUrnikSCtoXCDan6Off1Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340d5b4
STRUrnikSCtoXCDan6Off1Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340d5b5
STRUrnikSCtoXCDan6Off2Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340d5b6
STRUrnikSCtoXCDan6Off2Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340d5b7
STRUrnikSCtoXCDan6Off3Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340d5b8
STRUrnikSCtoXCDan6Off3Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340d5b9
STRUrnikSCtoXCDan6On1Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340d5ba
STRUrnikSCtoXCDan6On1Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340d5bb
STRUrnikSCtoXCDan6On2Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340d5bc
STRUrnikSCtoXCDan6On2Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340d5bd
STRUrnikSCtoXCDan6On3Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340d5be
STRUrnikSCtoXCDan6On3Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340d5bf
STRUrnikSCtoXCDan7Off1Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340d5c0
STRUrnikSCtoXCDan7Off1Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340d5c1
STRUrnikSCtoXCDan7Off2Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340d5c2
STRUrnikSCtoXCDan7Off2Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340d5c3
STRUrnikSCtoXCDan7Off3Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340d5c4
STRUrnikSCtoXCDan7Off3Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340d5c5
STRUrnikSCtoXCDan7On1Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340d5c6
STRUrnikSCtoXCDan7On1Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340d5c7
STRUrnikSCtoXCDan7On2Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340d5c8
STRUrnikSCtoXCDan7On2Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340d5c9
STRUrnikSCtoXCDan7On3Mna | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340d5ca
STRUrnikSCtoXCDan7On3Ura | BYTE | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340d5cb
STRUrnikXCtoSCDan1Off1Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340d5cc
STRUrnikXCtoSCDan1Off1Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340d5cd
STRUrnikXCtoSCDan1Off2Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340d5ce
STRUrnikXCtoSCDan1Off2Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340d5cf
STRUrnikXCtoSCDan1Off3Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340d5d0
STRUrnikXCtoSCDan1Off3Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340d5d1
STRUrnikXCtoSCDan1On1Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340d5d2
STRUrnikXCtoSCDan1On1Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340d5d3
STRUrnikXCtoSCDan1On2Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340d5d4
STRUrnikXCtoSCDan1On2Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340d5d5
STRUrnikXCtoSCDan1On3Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340d5d6
STRUrnikXCtoSCDan1On3Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340d5d7
STRUrnikXCtoSCDan2Off1Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340d5d8
STRUrnikXCtoSCDan2Off1Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340d5d9
STRUrnikXCtoSCDan2Off2Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340d5da
STRUrnikXCtoSCDan2Off2Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340d5db
STRUrnikXCtoSCDan2Off3Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340d5dc
STRUrnikXCtoSCDan2Off3Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340d5dd
STRUrnikXCtoSCDan2On1Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340d5de
STRUrnikXCtoSCDan2On1Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340d5df
STRUrnikXCtoSCDan2On2Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340d5e0
STRUrnikXCtoSCDan2On2Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340d5e1
STRUrnikXCtoSCDan2On3Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340d5e2
STRUrnikXCtoSCDan2On3Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340d5e3
STRUrnikXCtoSCDan3Off1Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340d5e4
STRUrnikXCtoSCDan3Off1Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340d5e5
STRUrnikXCtoSCDan3Off2Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340d5e6
STRUrnikXCtoSCDan3Off2Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340d5e7
STRUrnikXCtoSCDan3Off3Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340d5e8
STRUrnikXCtoSCDan3Off3Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340d5e9
STRUrnikXCtoSCDan3On1Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340d5ea
STRUrnikXCtoSCDan3On1Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340d5eb
STRUrnikXCtoSCDan3On2Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340d5ec
STRUrnikXCtoSCDan3On2Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340d5ed
STRUrnikXCtoSCDan3On3Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340d5ee
STRUrnikXCtoSCDan3On3Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340d5ef
STRUrnikXCtoSCDan4Off1Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340d5f0
STRUrnikXCtoSCDan4Off1Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340d5f1
STRUrnikXCtoSCDan4Off2Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340d5f2
STRUrnikXCtoSCDan4Off2Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340d5f3
STRUrnikXCtoSCDan4Off3Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340d5f4
STRUrnikXCtoSCDan4Off3Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340d5f5
STRUrnikXCtoSCDan4On1Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340d5f6
STRUrnikXCtoSCDan4On1Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340d5f7
STRUrnikXCtoSCDan4On2Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340d5f8
STRUrnikXCtoSCDan4On2Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340d5f9
STRUrnikXCtoSCDan4On3Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340d5fa
STRUrnikXCtoSCDan4On3Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340d5fb
STRUrnikXCtoSCDan5Off1Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340d5fc
STRUrnikXCtoSCDan5Off1Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340d5fd
STRUrnikXCtoSCDan5Off2Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340d5fe
STRUrnikXCtoSCDan5Off2Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340d5ff
STRUrnikXCtoSCDan5Off3Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340d600
STRUrnikXCtoSCDan5Off3Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340d601
STRUrnikXCtoSCDan5On1Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340d602
STRUrnikXCtoSCDan5On1Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340d603
STRUrnikXCtoSCDan5On2Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340d604
STRUrnikXCtoSCDan5On2Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340d605
STRUrnikXCtoSCDan5On3Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340d606
STRUrnikXCtoSCDan5On3Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340d607
STRUrnikXCtoSCDan6Off1Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340d608
STRUrnikXCtoSCDan6Off1Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340d609
STRUrnikXCtoSCDan6Off2Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340d60a
STRUrnikXCtoSCDan6Off2Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340d60b
STRUrnikXCtoSCDan6Off3Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340d60c
STRUrnikXCtoSCDan6Off3Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340d60d
STRUrnikXCtoSCDan6On1Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340d60e
STRUrnikXCtoSCDan6On1Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340d60f
STRUrnikXCtoSCDan6On2Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340d610
STRUrnikXCtoSCDan6On2Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340d611
STRUrnikXCtoSCDan6On3Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340d612
STRUrnikXCtoSCDan6On3Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340d613
STRUrnikXCtoSCDan7Off1Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340d614
STRUrnikXCtoSCDan7Off1Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340d615
STRUrnikXCtoSCDan7Off2Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340d616
STRUrnikXCtoSCDan7Off2Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340d617
STRUrnikXCtoSCDan7Off3Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340d618
STRUrnikXCtoSCDan7Off3Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340d619
STRUrnikXCtoSCDan7On1Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340d61a
STRUrnikXCtoSCDan7On1Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340d61b
STRUrnikXCtoSCDan7On2Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340d61c
STRUrnikXCtoSCDan7On2Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340d61d
STRUrnikXCtoSCDan7On3Mna | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340d61e
STRUrnikXCtoSCDan7On3Ura | BYTE | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340d61f
STRUserCurrentLevel | BYTE | IOD_STR | STR:.UserCurrentLevel | [6 empty] | 6157 | 1 | 0x0340d620
STRUserCurrentName | STRING | IOD_STR | STR:.UserCurrentName | [6 empty] | 6157 | 1 | 0x0340d621
STRUserLoggedIn | DIGITAL | IOD_STR | STR:.UserLoggedIn | [6 empty] | 6157 | 1 | 0x0340d630
STRValAI_Temp1B1 | REAL | IOD_STR | STR:.ValAI_Temp1B1 | -40 | 60 | -40 | 60 | °C | ####.# | 6157 | 1 | 0x0340d640
STRValAI_Temp1B2 | REAL | IOD_STR | STR:.ValAI_Temp1B2 | 0 | 50 | 0 | 50 | °C | ####.# | 6157 | 1 | 0x0340d641
STRValAI_Temp1B3 | REAL | IOD_STR | STR:.ValAI_Temp1B3 | 0 | 50 | 0 | 50 | °C | ####.# | 6157 | 1 | 0x0340d642
STRValAI_Temp2B2 | REAL | IOD_STR | STR:.ValAI_Temp2B2 | 0 | 50 | 0 | 50 | °C | ####.# | 6157 | 1 | 0x0340d643
STRValAI_Temp2B3 | REAL | IOD_STR | STR:.ValAI_Temp2B3 | 0 | 50 | 0 | 50 | °C | ####.# | 6157 | 1 | 0x0340d644
STRValAI_TempHB2 | REAL | IOD_STR | STR:.ValAI_TempHB2 | -10 | 110 | -10 | 110 | °C | ####.# | 6157 | 1 | 0x0340d645
STRValAI_TempHB4 | REAL | IOD_STR | STR:.ValAI_TempHB4 | -10 | 40 | -10 | 40 | °C | ####.# | 6157 | 1 | 0x0340d646
STRValAI_TempHB9 | REAL | IOD_STR | STR:.ValAI_TempHB9 | -10 | 110 | -10 | 110 | °C | ####.# | 6157 | 1 | 0x0340d647
STRValAI_TempTB1 | REAL | IOD_STR | STR:.ValAI_TempTB1 | -10 | 110 | -10 | 110 | °C | ####.# | 6157 | 1 | 0x0340d648
STRValAI_TempTB10 | REAL | IOD_STR | STR:.ValAI_TempTB10 | -40 | 50 | -40 | 50 | °C | ####.# | 6157 | 1 | 0x0340d649
STRValAI_TempTB2 | REAL | IOD_STR | STR:.ValAI_TempTB2 | -10 | 110 | -10 | 110 | °C | ####.# | 6157 | 1 | 0x0340d64a
STRValAI_TempTB3 | REAL | IOD_STR | STR:.ValAI_TempTB3 | -10 | 110 | -10 | 110 | °C | ####.# | 6157 | 1 | 0x0340d64b
STRValAI_TempTB4 | REAL | IOD_STR | STR:.ValAI_TempTB4 | -10 | 110 | -10 | 110 | °C | ####.# | 6157 | 1 | 0x0340d64c
STRValAI_TempTB8 | REAL | IOD_STR | STR:.ValAI_TempTB8 | -10 | 110 | -10 | 110 | °C | ####.# | 6157 | 1 | 0x0340d64d
STRValAI_TlakExp1S1 | REAL | IOD_STR | STR:.ValAI_TlakExp1S1 | 0 | 10 | 0 | 10 | bar | ####.# | 6157 | 1 | 0x0340d64e
STRValAI_TlakExp1S2 | REAL | IOD_STR | STR:.ValAI_TlakExp1S2 | 0 | 10 | 0 | 10 | bar | ####.# | 6157 | 1 | 0x0340d64f
STRValAI_TlakExp2S1 | REAL | IOD_STR | STR:.ValAI_TlakExp2S1 | 0 | 16 | 0 | 16 | bar | ####.# | 6157 | 1 | 0x0340d650
STRValAI_TlakExp2S2 | REAL | IOD_STR | STR:.ValAI_TlakExp2S2 | 0 | 16 | 0 | 16 | bar | ####.# | 6157 | 1 | 0x0340d651
STRValAI_TlakHB15 | REAL | IOD_STR | STR:.ValAI_TlakHB15 | 0 | 16 | 0 | 16 | bar | ####.# | 6157 | 1 | 0x0340d652
STRValAI_TlakHB16 | REAL | IOD_STR | STR:.ValAI_TlakHB16 | 0 | 6 | 0 | 6 | bar | ####.# | 6157 | 1 | 0x0340d653
STRValAI_TlakHB17 | REAL | IOD_STR | STR:.ValAI_TlakHB17 | 0 | 6 | 0 | 6 | bar | ####.# | 6157 | 1 | 0x0340d654
STRValAI_TlakHB3 | REAL | IOD_STR | STR:.ValAI_TlakHB3 | 0 | 6 | 0 | 6 | bar | ####.# | 6157 | 1 | 0x0340d655
STRValAI_TlakTB11 | REAL | IOD_STR | STR:.ValAI_TlakTB11 | 0 | 6 | 0 | 6 | bar | ####.# | 6157 | 1 | 0x0340d656
STRValAI_TlakTB12 | REAL | IOD_STR | STR:.ValAI_TlakTB12 | 0 | 6 | 0 | 6 | bar | ####.# | 6157 | 1 | 0x0340d657
STRValAI_TlakTB13 | REAL | IOD_STR | STR:.ValAI_TlakTB13 | 0 | 6 | 0 | 6 | bar | ####.# | 6157 | 1 | 0x0340d658
STRValAI_TlakTB14 | REAL | IOD_STR | STR:.ValAI_TlakTB14 | 0 | 6 | 0 | 6 | bar | ####.# | 6157 | 1 | 0x0340d659
STRValAI_Vlaga1B4 | REAL | IOD_STR | STR:.ValAI_Vlaga1B4 | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340d65a
STRValAI_Vlaga2B4 | REAL | IOD_STR | STR:.ValAI_Vlaga2B4 | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340d65b
STRValAO_RegVentTY1 | REAL | IOD_STR | STR:.ValAO_RegVentTY[1] | 0 | 100 | 0 | 100 | % | #### | 6157 | 1 | 0x0340d65c
STRValAO_RegVentTY2 | REAL | IOD_STR | STR:.ValAO_RegVentTY[2] | 0 | 100 | 0 | 100 | % | #### | 6157 | 1 | 0x0340d65d
STRValAO_RegVentTY3 | REAL | IOD_STR | STR:.ValAO_RegVentTY[3] | 0 | 100 | 0 | 100 | % | #### | 6157 | 1 | 0x0340d65e
STRValAO_RegVentTY4 | REAL | IOD_STR | STR:.ValAO_RegVentTY[4] | 0 | 100 | 0 | 100 | % | #### | 6157 | 1 | 0x0340d65f
STRVentilatorOnOff1 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[1] | [6 empty] | 6157 | 1 | 0x0340d660
STRVentilatorOnOff2 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[2] | [6 empty] | 6157 | 1 | 0x0340d670
STRVentilatorOnOff3 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[3] | [6 empty] | 6157 | 1 | 0x0340d680
STRVentilatorOnOff4 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[4] | [6 empty] | 6157 | 1 | 0x0340d690
STRVentilatorOnOff5 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[5] | [6 empty] | 6157 | 1 | 0x0340d6a0
STRVentilatorOnOff6 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[6] | [6 empty] | 6157 | 1 | 0x0340d6b0
STRVklopSCFBNapaka10 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[10] | [6 empty] | 6157 | 1 | 0x0340d6c0
STRVklopSCFBNapaka11 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[11] | [6 empty] | 6157 | 1 | 0x0340d6d0
STRVklopSCFBNapaka12 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[12] | [6 empty] | 6157 | 1 | 0x0340d6e0
STRVklopSCFBNapaka13 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[13] | [6 empty] | 6157 | 1 | 0x0340d6f0
STRVklopSCFBNapaka14 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[14] | [6 empty] | 6157 | 1 | 0x0340d700
STRVklopSCFBNapaka15 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[15] | [6 empty] | 6157 | 1 | 0x0340d710
STRVklopSCFBNapaka16 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[16] | [6 empty] | 6157 | 1 | 0x0340d720
STRVklopSCFBNapaka17 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[17] | [6 empty] | 6157 | 1 | 0x0340d730
STRVklopSCFBNapaka18 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[18] | [6 empty] | 6157 | 1 | 0x0340d740
STRVklopSCFBNapaka19 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[19] | [6 empty] | 6157 | 1 | 0x0340d750
STRVklopSCFBNapaka1 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[1] | [6 empty] | 6157 | 1 | 0x0340d760
STRVklopSCFBNapaka20 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[20] | [6 empty] | 6157 | 1 | 0x0340d770
STRVklopSCFBNapaka21 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[21] | [6 empty] | 6157 | 1 | 0x0340d780
STRVklopSCFBNapaka22 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[22] | [6 empty] | 6157 | 1 | 0x0340d790
STRVklopSCFBNapaka23 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[23] | [6 empty] | 6157 | 1 | 0x0340d7a0
STRVklopSCFBNapaka24 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[24] | [6 empty] | 6157 | 1 | 0x0340d7b0
STRVklopSCFBNapaka25 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[25] | [6 empty] | 6157 | 1 | 0x0340d7c0
STRVklopSCFBNapaka2 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[2] | [6 empty] | 6157 | 1 | 0x0340d7d0
STRVklopSCFBNapaka3 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[3] | [6 empty] | 6157 | 1 | 0x0340d7e0
STRVklopSCFBNapaka4 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[4] | [6 empty] | 6157 | 1 | 0x0340d7f0
STRVklopSCFBNapaka5 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[5] | [6 empty] | 6157 | 1 | 0x0340d800
STRVklopSCFBNapaka6 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[6] | [6 empty] | 6157 | 1 | 0x0340d810
STRVklopSCFBNapaka7 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[7] | [6 empty] | 6157 | 1 | 0x0340d820
STRVklopSCFBNapaka8 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[8] | [6 empty] | 6157 | 1 | 0x0340d830
STRVklopSCFBNapaka9 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[9] | [6 empty] | 6157 | 1 | 0x0340d840
STRVlagaHIApovprecna | REAL | IOD_STR | STR:.VlagaHIApovprecna | 0 | 100 | 0 | 100 | % | ####.# | 6157 | 1 | 0x0340d850
STRXVH_AlarmOn | DIGITAL | IOD_STR | STR:.XVH_AlarmOn | [6 empty] | 6157 | 1 | 0x0340d860
STRXVH_CrpalkaGrfsNum | LONG | IOD_STR | STR:.XVH_CrpalkaGrfsNum | [6 empty] | 6157 | 1 | 0x0340d870
STRXVH_StUrnika | LONG | IOD_STR | STR:.XVH_StUrnika | [6 empty] | 6157 | 1 | 0x0340d871
STRXVH_IzklopVsehLuci | DIGITAL | IOD_STR | STR:.XVH_IzklopVsehLuci | [6 empty] | 6157 | 1 | 0x0340d880
STRXVH_VklopVsehLuci | DIGITAL | IOD_STR | STR:.XVH_VklopVsehLuci | [6 empty] | 6157 | 1 | 0x0340d890
STRUserloggedIn_mem | DIGITAL | IOD_STR_disk | D500 | [8 empty] | 0x0340d8a0
STRSkupnaNapakaKomunikacije | DIGITAL | IOD_STR_disk | D333 | [8 empty] | 0x0340d8b0
STRUrnikiLetniCas | INT | IOD_STR_disk | I3099 | [8 empty] | 0x0340d8c0
STRUrnikZaPrenosTemp | INT | IOD_STR_disk | I3100 | [8 empty] | 0x0340d8c1
STRPrenosUrnikaGor | DIGITAL | IOD_STR_disk | D505 | [8 empty] | 0x0340d8d0
STRZapisiUrnikNaXC | DIGITAL | IOD_STR_disk | D506 | [8 empty] | 0x0340d8e0
STRUrnikCopy | DIGITAL | IOD_STR_disk | D507 | [8 empty] | 0x0340d8f0
STRUrnikPaste | DIGITAL | IOD_STR_disk | D508 | [8 empty] | 0x0340d900
STRPomikZaUroPlus | DIGITAL | IOD_STR_disk | D509 | [8 empty] | 0x0340d910
STRPomikZaUroMinus | DIGITAL | IOD_STR_disk | D510 | [8 empty] | 0x0340d920
STRPrenasanjeUrnikovAktivno | DIGITAL | IOD_STR | STR:.PrenasanjeUrnikovAktivno | [8 empty] | 0x0340d930
STRPrenasanjeUrnikovAktivno1 | DIGITAL | IOD_STR | STR:.PrenasanjeUrnikovAktivno1 | [8 empty] | 0x0340d940
STRCircutorCosFi_III | REAL | IOD_STR | STR:.Circutor.CosFi_III | [6 empty] | 6157 | 1 | 0x0340d950
STRCircutorDelovnaEnergija | REAL | IOD_STR | STR:.Circutor.DelovnaEnergija | [6 empty] | 6157 | 1 | 0x0340d951
STRCircutorDelovnaMoc_III | REAL | IOD_STR | STR:.Circutor.DelovnaMoc_III | [6 empty] | 6157 | 1 | 0x0340d952
STRCircutorDelovnaMoc_L1 | REAL | IOD_STR | STR:.Circutor.DelovnaMoc_L1 | [6 empty] | 6157 | 1 | 0x0340d953
STRCircutorDelovnaMoc_L2 | REAL | IOD_STR | STR:.Circutor.DelovnaMoc_L2 | [6 empty] | 6157 | 1 | 0x0340d954
STRCircutorDelovnaMoc_L3 | REAL | IOD_STR | STR:.Circutor.DelovnaMoc_L3 | [6 empty] | 6157 | 1 | 0x0340d955
STRCircutorFrekvenca_L1 | REAL | IOD_STR | STR:.Circutor.Frekvenca_L1 | [6 empty] | 6157 | 1 | 0x0340d956
STRCircutorInduktivnaEnergija | REAL | IOD_STR | STR:.Circutor.InduktivnaEnergija | [6 empty] | 6157 | 1 | 0x0340d957
STRCircutorInduktivnaMoc_III | REAL | IOD_STR | STR:.Circutor.InduktivnaMoc_III | [6 empty] | 6157 | 1 | 0x0340d958
STRCircutorJalovaMoc_L1 | REAL | IOD_STR | STR:.Circutor.JalovaMoc_L1 | [6 empty] | 6157 | 1 | 0x0340d959
STRCircutorJalovaMoc_L2 | REAL | IOD_STR | STR:.Circutor.JalovaMoc_L2 | [6 empty] | 6157 | 1 | 0x0340d95a
STRCircutorJalovaMoc_L3 | REAL | IOD_STR | STR:.Circutor.JalovaMoc_L3 | [6 empty] | 6157 | 1 | 0x0340d95b
STRCircutorKapacitivnaEnergija | REAL | IOD_STR | STR:.Circutor.KapacitivnaEnergija | [6 empty] | 6157 | 1 | 0x0340d95c
STRCircutorKapacitivnaMoc_III | REAL | IOD_STR | STR:.Circutor.KapacitivnaMoc_III | [6 empty] | 6157 | 1 | 0x0340d95d
STRCircutorMaximumDemand | REAL | IOD_STR | STR:.Circutor.MaximumDemand | [6 empty] | 6157 | 1 | 0x0340d95e
STRCircutorNapetost_L1_L2 | REAL | IOD_STR | STR:.Circutor.Napetost_L1_L2 | [6 empty] | 6157 | 1 | 0x0340d95f
STRCircutorNapetost_L1_N | REAL | IOD_STR | STR:.Circutor.Napetost_L1_N | [6 empty] | 6157 | 1 | 0x0340d960
STRCircutorNapetost_L2_L3 | REAL | IOD_STR | STR:.Circutor.Napetost_L2_L3 | [6 empty] | 6157 | 1 | 0x0340d961
STRCircutorNapetost_L2_N | REAL | IOD_STR | STR:.Circutor.Napetost_L2_N | [6 empty] | 6157 | 1 | 0x0340d962
STRCircutorNapetost_L3_L1 | REAL | IOD_STR | STR:.Circutor.Napetost_L3_L1 | [6 empty] | 6157 | 1 | 0x0340d963
STRCircutorNapetost_L3_N | REAL | IOD_STR | STR:.Circutor.Napetost_L3_N | [6 empty] | 6157 | 1 | 0x0340d964
STRCircutorNavideznaMoc_III | REAL | IOD_STR | STR:.Circutor.NavideznaMoc_III | [6 empty] | 6157 | 1 | 0x0340d965
STRCircutorNicelniTok | REAL | IOD_STR | STR:.Circutor.NicelniTok | [6 empty] | 6157 | 1 | 0x0340d966
STRCircutorPowerFactor_III | REAL | IOD_STR | STR:.Circutor.PowerFactor_III | [6 empty] | 6157 | 1 | 0x0340d967
STRCircutorPowerFactor_L1 | REAL | IOD_STR | STR:.Circutor.PowerFactor_L1 | [6 empty] | 6157 | 1 | 0x0340d968
STRCircutorPowerFactor_L2 | REAL | IOD_STR | STR:.Circutor.PowerFactor_L2 | [6 empty] | 6157 | 1 | 0x0340d969
STRCircutorPowerFactor_L3 | REAL | IOD_STR | STR:.Circutor.PowerFactor_L3 | [6 empty] | 6157 | 1 | 0x0340d96a
STRCircutorTHDI_L1 | REAL | IOD_STR | STR:.Circutor.THDI_L1 | [6 empty] | 6157 | 1 | 0x0340d96b
STRCircutorTHDI_L2 | REAL | IOD_STR | STR:.Circutor.THDI_L2 | [6 empty] | 6157 | 1 | 0x0340d96c
STRCircutorTHDI_L3 | REAL | IOD_STR | STR:.Circutor.THDI_L3 | [6 empty] | 6157 | 1 | 0x0340d96d
STRCircutorTHDV_L1 | REAL | IOD_STR | STR:.Circutor.THDV_L1 | [6 empty] | 6157 | 1 | 0x0340d96e
STRCircutorTHDV_L2 | REAL | IOD_STR | STR:.Circutor.THDV_L2 | [6 empty] | 6157 | 1 | 0x0340d96f
STRCircutorTHDV_L3 | REAL | IOD_STR | STR:.Circutor.THDV_L3 | [6 empty] | 6157 | 1 | 0x0340d970
STRCircutorTok_L1 | REAL | IOD_STR | STR:.Circutor.Tok_L1 | [6 empty] | 6157 | 1 | 0x0340d971
STRCircutorTok_L2 | REAL | IOD_STR | STR:.Circutor.Tok_L2 | [6 empty] | 6157 | 1 | 0x0340d972
STRCircutorTok_L3 | REAL | IOD_STR | STR:.Circutor.Tok_L3 | [6 empty] | 6157 | 1 | 0x0340d973
STRCircutorTokPovprecje_III | REAL | IOD_STR | STR:.Circutor.TokPovprecje_III | [6 empty] | 6157 | 1 | 0x0340d974
STRCrpalkeGrfsGalAlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmActiveCode | [6 empty] | 6157 | 1 | 0x0340d97d
STRCrpalkeGrfsGalAlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.AlarmAktiven | [6 empty] | 6157 | 1 | 0x0340d980
STRCrpalkeGrfsGalAlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmCodeLog1 | [6 empty] | 6157 | 1 | 0x0340d990
STRCrpalkeGrfsGalAlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmCodeLog2 | [6 empty] | 6157 | 1 | 0x0340d991
STRCrpalkeGrfsGalAlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmCodeLog3 | [6 empty] | 6157 | 1 | 0x0340d992
STRCrpalkeGrfsGalAlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmCodeLog4 | [6 empty] | 6157 | 1 | 0x0340d993
STRCrpalkeGrfsGalAlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmCodeLog5 | [6 empty] | 6157 | 1 | 0x0340d994
STRCrpalkeGrfsGalAlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[0] | [6 empty] | 6157 | 1 | 0x0340d995
STRCrpalkeGrfsGalAlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[10] | [6 empty] | 6157 | 1 | 0x0340d996
STRCrpalkeGrfsGalAlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[11] | [6 empty] | 6157 | 1 | 0x0340d997
STRCrpalkeGrfsGalAlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[12] | [6 empty] | 6157 | 1 | 0x0340d998
STRCrpalkeGrfsGalAlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[13] | [6 empty] | 6157 | 1 | 0x0340d999
STRCrpalkeGrfsGalAlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[14] | [6 empty] | 6157 | 1 | 0x0340d99a
STRCrpalkeGrfsGalAlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[15] | [6 empty] | 6157 | 1 | 0x0340d99b
STRCrpalkeGrfsGalAlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[16] | [6 empty] | 6157 | 1 | 0x0340d99c
STRCrpalkeGrfsGalAlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[1] | [6 empty] | 6157 | 1 | 0x0340d99d
STRCrpalkeGrfsGalAlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[2] | [6 empty] | 6157 | 1 | 0x0340d99e
STRCrpalkeGrfsGalAlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[3] | [6 empty] | 6157 | 1 | 0x0340d99f
STRCrpalkeGrfsGalAlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[4] | [6 empty] | 6157 | 1 | 0x0340d9a0
STRCrpalkeGrfsGalAlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[5] | [6 empty] | 6157 | 1 | 0x0340d9a1
STRCrpalkeGrfsGalAlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[6] | [6 empty] | 6157 | 1 | 0x0340d9a2
STRCrpalkeGrfsGalAlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[7] | [6 empty] | 6157 | 1 | 0x0340d9a3
STRCrpalkeGrfsGalAlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[8] | [6 empty] | 6157 | 1 | 0x0340d9a4
STRCrpalkeGrfsGalAlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[9] | [6 empty] | 6157 | 1 | 0x0340d9a5
STRCrpalkeGrfsGalAlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmQSD1 | [6 empty] | 6157 | 1 | 0x0340d9a6
STRCrpalkeGrfsGalAlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmQSD2 | [6 empty] | 6157 | 1 | 0x0340d9a7
STRCrpalkeGrfsGalAlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmStart1 | [6 empty] | 6157 | 1 | 0x0340d9a8
STRCrpalkeGrfsGalAlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmStart2 | [6 empty] | 6157 | 1 | 0x0340d9a9
STRCrpalkeGrfsGalAlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmStop1 | [6 empty] | 6157 | 1 | 0x0340d9aa
STRCrpalkeGrfsGalAlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmStop2 | [6 empty] | 6157 | 1 | 0x0340d9ab
STRCrpalkeGrfsGalAlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmStop3 | [6 empty] | 6157 | 1 | 0x0340d9ac
STRCrpalkeGrfsGalAlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmSurv1 | [6 empty] | 6157 | 1 | 0x0340d9ad
STRCrpalkeGrfsGalAlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmSurv2 | [6 empty] | 6157 | 1 | 0x0340d9ae
STRCrpalkeGrfsGalControlSource | INT | IOD_STR | STR:.CrpalkeGrfsGal.ControlSource | [6 empty] | 6157 | 1 | 0x0340d9af
STRCrpalkeGrfsGalDeluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.Deluje | [6 empty] | 6157 | 1 | 0x0340d9b0
STRCrpalkeGrfsGalEnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfsGal.EnergijaPoraba | [6 empty] | 6157 | 1 | 0x0340d9c0
STRCrpalkeGrfsGalExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfsGal.ExternInputSetup | [6 empty] | 6157 | 1 | 0x0340d9c1
STRCrpalkeGrfsGalExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfsGal.ExternInputsStatus | [6 empty] | 6157 | 1 | 0x0340d9c2
STRCrpalkeGrfsGalFrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfsGal.FrekPretvornikDCNapetost | [6 empty] | 6157 | 1 | 0x0340d9c3
STRCrpalkeGrfsGalFrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfsGal.FrekPretvornikDCTok | [6 empty] | 6157 | 1 | 0x0340d9c4
STRCrpalkeGrfsGalFreqMax | REAL | IOD_STR | STR:.CrpalkeGrfsGal.FreqMax | [6 empty] | 6157 | 1 | 0x0340d9c5
STRCrpalkeGrfsGalFreqMin | REAL | IOD_STR | STR:.CrpalkeGrfsGal.FreqMin | [6 empty] | 6157 | 1 | 0x0340d9c6
STRCrpalkeGrfsGalFreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfsGal.FreqUpper | [6 empty] | 6157 | 1 | 0x0340d9c7
STRCrpalkeGrfsGalLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.LocalMode | [6 empty] | 6157 | 1 | 0x0340d9d0
STRCrpalkeGrfsGalLocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.LocalSetupMode1 | [6 empty] | 6157 | 1 | 0x0340d9e0
STRCrpalkeGrfsGalMocMax | REAL | IOD_STR | STR:.CrpalkeGrfsGal.MocMax | [6 empty] | 6157 | 1 | 0x0340d9e1
STRCrpalkeGrfsGalMocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfsGal.MocTrenutna | [6 empty] | 6157 | 1 | 0x0340d9e2
STRCrpalkeGrfsGalMotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfsGal.MotorHitrost | [6 empty] | 6157 | 1 | 0x0340d9e3
STRCrpalkeGrfsGalMotorTok | REAL | IOD_STR | STR:.CrpalkeGrfsGal.MotorTok | [6 empty] | 6157 | 1 | 0x0340d9e4
STRCrpalkeGrfsGalNapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfsGal.NapajanjeTok | [6 empty] | 6157 | 1 | 0x0340d9e5
STRCrpalkeGrfsGalNastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfsGal.NastavitevLokalna | [6 empty] | 6157 | 1 | 0x0340d9e6
STRCrpalkeGrfsGalNastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfsGal.NastavitevTrenutna | [6 empty] | 6157 | 1 | 0x0340d9e7
STRCrpalkeGrfsGalPreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfsGal.PreklopkaMode | [6 empty] | 6157 | 1 | 0x0340d9e8
STRCrpalkeGrfsGalPretokMax | REAL | IOD_STR | STR:.CrpalkeGrfsGal.PretokMax | [6 empty] | 6157 | 1 | 0x0340d9e9
STRCrpalkeGrfsGalPretokMin | REAL | IOD_STR | STR:.CrpalkeGrfsGal.PretokMin | [6 empty] | 6157 | 1 | 0x0340d9ea
STRCrpalkeGrfsGalPretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfsGal.PretokTrenutni | [6 empty] | 6157 | 1 | 0x0340d9eb
STRCrpalkeGrfsGalPritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfsGal.PritiskMax | [6 empty] | 6157 | 1 | 0x0340d9ec
STRCrpalkeGrfsGalPritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfsGal.PritiskTrenutni | [6 empty] | 6157 | 1 | 0x0340d9ed
STRCrpalkeGrfsGalReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfsGal.ReferencaMotorjaHzV | [6 empty] | 6157 | 1 | 0x0340d9ee
STRCrpalkeGrfsGalReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfsGal.ReferencaRemote | [6 empty] | 6157 | 1 | 0x0340d9ef
STRCrpalkeGrfsGalRelay1setup | INT | IOD_STR | STR:.CrpalkeGrfsGal.Relay1setup | [6 empty] | 6157 | 1 | 0x0340d9f0
STRCrpalkeGrfsGalRemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.RemoteON | [6 empty] | 6157 | 1 | 0x0340da00
STRCrpalkeGrfsGalRemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.RemoteSetupMode1 | [6 empty] | 6157 | 1 | 0x0340da10
STRCrpalkeGrfsGalReset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.Reset2handkWhValues | [6 empty] | 6157 | 1 | 0x0340da20
STRCrpalkeGrfsGalResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.ResetAlarm | [6 empty] | 6157 | 1 | 0x0340da30
STRCrpalkeGrfsGalResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.ResetAlarmLog | [6 empty] | 6157 | 1 | 0x0340da40
STRCrpalkeGrfsGalResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.ResetDevice | [6 empty] | 6157 | 1 | 0x0340da50
STRCrpalkeGrfsGalSetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetAutomatic | [6 empty] | 6157 | 1 | 0x0340da60
STRCrpalkeGrfsGalSetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetConstFreqMode | [6 empty] | 6157 | 1 | 0x0340da70
STRCrpalkeGrfsGalSetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetConstPress | [6 empty] | 6157 | 1 | 0x0340da80
STRCrpalkeGrfsGalSetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetLocalMode | [6 empty] | 6157 | 1 | 0x0340da90
STRCrpalkeGrfsGalSetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetMaxRunMode | [6 empty] | 6157 | 1 | 0x0340daa0
STRCrpalkeGrfsGalSetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetMinRunMode | [6 empty] | 6157 | 1 | 0x0340dab0
STRCrpalkeGrfsGalSetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetPropPress | [6 empty] | 6157 | 1 | 0x0340dac0
STRCrpalkeGrfsGalSetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetReference | [6 empty] | 6157 | 1 | 0x0340dad0
STRCrpalkeGrfsGalSetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetRemoteMode | [6 empty] | 6157 | 1 | 0x0340dae0
STRCrpalkeGrfsGalSetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetTwinModeAlt | [6 empty] | 6157 | 1 | 0x0340daf0
STRCrpalkeGrfsGalSetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetTwinModeSpare | [6 empty] | 6157 | 1 | 0x0340db00
STRCrpalkeGrfsGalSetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetTwinModeSync | [6 empty] | 6157 | 1 | 0x0340db10
STRCrpalkeGrfsGalStart | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.Start | [6 empty] | 6157 | 1 | 0x0340db20
STRCrpalkeGrfsGalStatusCrpalke | BYTE | IOD_STR | STR:.CrpalkeGrfsGal.StatusCrpalke | [6 empty] | 6157 | 1 | 0x0340db30
STRCrpalkeGrfsGalStatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.StatusMode1 | [6 empty] | 6157 | 1 | 0x0340db31
STRCrpalkeGrfsGalStatusMode1co | BYTE | IOD_STR | STR:.CrpalkeGrfsGal.StatusMode1co | [6 empty] | 6157 | 1 | 0x0340db32
STRCrpalkeGrfsGalStatusMode1op | BYTE | IOD_STR | STR:.CrpalkeGrfsGal.StatusMode1op | [6 empty] | 6157 | 1 | 0x0340db33
STRCrpalkeGrfsGalStatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.StatusMode2 | [6 empty] | 6157 | 1 | 0x0340db34
STRCrpalkeGrfsGalStatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfsGal.StatusMode3 | [6 empty] | 6157 | 1 | 0x0340db35
STRCrpalkeGrfsGalStevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfsGal.StevecUr2h | [6 empty] | 6157 | 1 | 0x0340db36
STRCrpalkeGrfsGalStop | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.Stop | [6 empty] | 6157 | 1 | 0x0340db40
STRCrpalkeGrfsGalSystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfsGal.SystemFeedback | [6 empty] | 6157 | 1 | 0x0340db50
STRCrpalkeGrfsGalSystemReference | REAL | IOD_STR | STR:.CrpalkeGrfsGal.SystemReference | [6 empty] | 6157 | 1 | 0x0340db51
STRCrpalkeGrfsGalTemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfsGal.TemperaturaMotorja | [6 empty] | 6157 | 1 | 0x0340db52
STRCrpalkeGrfsGalUreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfsGal.UreXC200 | [6 empty] | 6157 | 1 | 0x0340db53
STRCrpGrfsPIDregKP | REAL | IOD_STR | STR:.CrpGrfsPIDregKP | [6 empty] | 6157 | 1 | 0x0340db54
STRCrpGrfsPIDregTN | INT | IOD_STR | STR:.CrpGrfsPIDregTN | [6 empty] | 6157 | 1 | 0x0340db55
STRDate_Time0 | STRING | IOD_STR | STR:.Date_Time[0] | [6 empty] | 6157 | 1 | 0x0340db56
STRDate_Time1 | STRING | IOD_STR | STR:.Date_Time[1] | [6 empty] | 6157 | 1 | 0x0340db57
STRDate_Time2 | STRING | IOD_STR | STR:.Date_Time[2] | [6 empty] | 6157 | 1 | 0x0340db58
STRDate_Time3 | STRING | IOD_STR | STR:.Date_Time[3] | [6 empty] | 6157 | 1 | 0x0340db59
STRDateTimeDanVtednu | BYTE | IOD_STR | STR:.DateTime.DanVtednu | [6 empty] | 6157 | 1 | 0x0340db5a
STRDI_rezerva10_2 | DIGITAL | IOD_STR | STR:.DI_rezerva10_2 | [6 empty] | 6157 | 1 | 0x0340db60
STRDI_rezerva10_7 | DIGITAL | IOD_STR | STR:.DI_rezerva10_7 | [6 empty] | 6157 | 1 | 0x0340db70
STRDI_rezerva11_4 | DIGITAL | IOD_STR | STR:.DI_rezerva11_4 | [6 empty] | 6157 | 1 | 0x0340db80
STRDI_rezerva14_0 | DIGITAL | IOD_STR | STR:.DI_rezerva14_0 | [6 empty] | 6157 | 1 | 0x0340db90
STRDI_rezerva14_2 | DIGITAL | IOD_STR | STR:.DI_rezerva14_2 | [6 empty] | 6157 | 1 | 0x0340dba0
STRDI_rezerva14_3 | DIGITAL | IOD_STR | STR:.DI_rezerva14_3 | [6 empty] | 6157 | 1 | 0x0340dbb0
STRDI_rezerva14_4 | DIGITAL | IOD_STR | STR:.DI_rezerva14_4 | [6 empty] | 6157 | 1 | 0x0340dbc0
STRDI_rezerva14_5 | DIGITAL | IOD_STR | STR:.DI_rezerva14_5 | [6 empty] | 6157 | 1 | 0x0340dbd0
STRDI_rezerva14_7 | DIGITAL | IOD_STR | STR:.DI_rezerva14_7 | [6 empty] | 6157 | 1 | 0x0340dbe0
STRDI_rezerva2_4 | DIGITAL | IOD_STR | STR:.DI_rezerva2_4 | [6 empty] | 6157 | 1 | 0x0340dbf0
STRDI_rezerva3_5 | DIGITAL | IOD_STR | STR:.DI_rezerva3_5 | [6 empty] | 6157 | 1 | 0x0340dc00
STRDIN_AkumTopVodeAUTO | DIGITAL | IOD_STR | STR:.DIN_AkumTopVodeAUTO | [6 empty] | 6157 | 1 | 0x0340dc10
STRDIN_CrpHM1AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM1AUTO | [6 empty] | 6157 | 1 | 0x0340dc20
STRDIN_CrpHM1kontON | DIGITAL | IOD_STR | STR:.DIN_CrpHM1kontON | [6 empty] | 6157 | 1 | 0x0340dc30
STRDIN_CrpHM2AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM2AUTO | [6 empty] | 6157 | 1 | 0x0340dc40
STRDIN_CrpHM2kontON | DIGITAL | IOD_STR | STR:.DIN_CrpHM2kontON | [6 empty] | 6157 | 1 | 0x0340dc50
STRDIN_CrpHM3AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM3AUTO | [6 empty] | 6157 | 1 | 0x0340dc60
STRDIN_CrpHM3kontON | DIGITAL | IOD_STR | STR:.DIN_CrpHM3kontON | [6 empty] | 6157 | 1 | 0x0340dc70
STRDIN_CrpHM4AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM4AUTO | [6 empty] | 6157 | 1 | 0x0340dc80
STRDIN_CrpHM4kontON | DIGITAL | IOD_STR | STR:.DIN_CrpHM4kontON | [6 empty] | 6157 | 1 | 0x0340dc90
STRDIN_CrpHM5AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM5AUTO | [6 empty] | 6157 | 1 | 0x0340dca0
STRDIN_CrpHM6AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM6AUTO | [6 empty] | 6157 | 1 | 0x0340dcb0
STRDIN_CrpHM7AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM7AUTO | [6 empty] | 6157 | 1 | 0x0340dcc0
STRDIN_CrpHM8AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM8AUTO | [6 empty] | 6157 | 1 | 0x0340dcd0
STRDIN_CrpMN1AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpMN1AUTO | [6 empty] | 6157 | 1 | 0x0340dce0
STRDIN_CrpMN1kontON | DIGITAL | IOD_STR | STR:.DIN_CrpMN1kontON | [6 empty] | 6157 | 1 | 0x0340dcf0
STRDIN_CrpTM10AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM10AUTO | [6 empty] | 6157 | 1 | 0x0340dd00
STRDIN_CrpTM11TM12AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM11TM12AUTO | [6 empty] | 6157 | 1 | 0x0340dd10
STRDIN_CrpTM11TM12kontON | DIGITAL | IOD_STR | STR:.DIN_CrpTM11TM12kontON | [6 empty] | 6157 | 1 | 0x0340dd20
STRDIN_CrpTM1AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM1AUTO | [6 empty] | 6157 | 1 | 0x0340dd30
STRDIN_CrpTM2AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM2AUTO | [6 empty] | 6157 | 1 | 0x0340dd40
STRDIN_CrpTM3AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM3AUTO | [6 empty] | 6157 | 1 | 0x0340dd50
STRDIN_CrpTM4AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM4AUTO | [6 empty] | 6157 | 1 | 0x0340dd60
STRDIN_CrpTM5AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM5AUTO | [6 empty] | 6157 | 1 | 0x0340dd70
STRDIN_CrpTM6AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM6AUTO | [6 empty] | 6157 | 1 | 0x0340dd80
STRDIN_CrpTM7AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM7AUTO | [6 empty] | 6157 | 1 | 0x0340dd90
STRDIN_CrpTM8AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM8AUTO | [6 empty] | 6157 | 1 | 0x0340dda0
STRDIN_CrpTM9AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM9AUTO | [6 empty] | 6157 | 1 | 0x0340ddb0
STRDIN_GlStikaloDieselON | DIGITAL | IOD_STR | STR:.DIN_GlStikaloDieselON | [6 empty] | 6157 | 1 | 0x0340ddc0
STRDIN_GlStikaloMrezaON | DIGITAL | IOD_STR | STR:.DIN_GlStikaloMrezaON | [6 empty] | 6157 | 1 | 0x0340ddd0
STRDIN_GlStikaloUpsON | DIGITAL | IOD_STR | STR:.DIN_GlStikaloUpsON | [6 empty] | 6157 | 1 | 0x0340dde0
STRDIN_HladStAUTO | DIGITAL | IOD_STR | STR:.DIN_HladStAUTO | [6 empty] | 6157 | 1 | 0x0340ddf0
STRDIN_Kond1AUTO | DIGITAL | IOD_STR | STR:.DIN_Kond1AUTO | [6 empty] | 6157 | 1 | 0x0340de00
STRDIN_Kond2AUTO | DIGITAL | IOD_STR | STR:.DIN_Kond2AUTO | [6 empty] | 6157 | 1 | 0x0340de10
STRDIN_Kond3AUTO | DIGITAL | IOD_STR | STR:.DIN_Kond3AUTO | [6 empty] | 6157 | 1 | 0x0340de20
STRDIN_Vent1Auto | DIGITAL | IOD_STR | STR:.DIN_Vent1Auto | [6 empty] | 6157 | 1 | 0x0340de30
STRDIN_Vent1kontON | DIGITAL | IOD_STR | STR:.DIN_Vent1kontON | [6 empty] | 6157 | 1 | 0x0340de40
STRDIN_Vent2Auto | DIGITAL | IOD_STR | STR:.DIN_Vent2Auto | [6 empty] | 6157 | 1 | 0x0340de50
STRDIN_Vent2kontON | DIGITAL | IOD_STR | STR:.DIN_Vent2kontON | [6 empty] | 6157 | 1 | 0x0340de60
STRDIN_Vent3Auto | DIGITAL | IOD_STR | STR:.DIN_Vent3Auto | [6 empty] | 6157 | 1 | 0x0340de70
STRDIN_Vent3kontON | DIGITAL | IOD_STR | STR:.DIN_Vent3kontON | [6 empty] | 6157 | 1 | 0x0340de80
STRDIN_Vent4Auto | DIGITAL | IOD_STR | STR:.DIN_Vent4Auto | [6 empty] | 6157 | 1 | 0x0340de90
STRDIN_Vent4kontON | DIGITAL | IOD_STR | STR:.DIN_Vent4kontON | [6 empty] | 6157 | 1 | 0x0340dea0
STRDIN_Vent5Auto | DIGITAL | IOD_STR | STR:.DIN_Vent5Auto | [6 empty] | 6157 | 1 | 0x0340deb0
STRDIN_Vent5kontON | DIGITAL | IOD_STR | STR:.DIN_Vent5kontON | [6 empty] | 6157 | 1 | 0x0340dec0
STRDIN_Vent6Auto | DIGITAL | IOD_STR | STR:.DIN_Vent6Auto | [6 empty] | 6157 | 1 | 0x0340ded0
STRDIN_Vent6kontON | DIGITAL | IOD_STR | STR:.DIN_Vent6kontON | [6 empty] | 6157 | 1 | 0x0340dee0
STRDO_rezerva0_2 | DIGITAL | IOD_STR | STR:.DO_rezerva0_2 | [6 empty] | 6157 | 1 | 0x0340def0
STRDO_rezerva0_3 | DIGITAL | IOD_STR | STR:.DO_rezerva0_3 | [6 empty] | 6157 | 1 | 0x0340df00
STRDO_rezerva0_4 | DIGITAL | IOD_STR | STR:.DO_rezerva0_4 | [6 empty] | 6157 | 1 | 0x0340df10
STRDO_rezerva0_5 | DIGITAL | IOD_STR | STR:.DO_rezerva0_5 | [6 empty] | 6157 | 1 | 0x0340df20
STRDO_rezerva1_3 | DIGITAL | IOD_STR | STR:.DO_rezerva1_3 | [6 empty] | 6157 | 1 | 0x0340df30
STRDO_rezerva1_4 | DIGITAL | IOD_STR | STR:.DO_rezerva1_4 | [6 empty] | 6157 | 1 | 0x0340df40
STRDO_rezerva1_5 | DIGITAL | IOD_STR | STR:.DO_rezerva1_5 | [6 empty] | 6157 | 1 | 0x0340df50
STRDO_rezerva3_4 | DIGITAL | IOD_STR | STR:.DO_rezerva3_4 | [6 empty] | 6157 | 1 | 0x0340df60
STRDO_rezerva3_6 | DIGITAL | IOD_STR | STR:.DO_rezerva3_6 | [6 empty] | 6157 | 1 | 0x0340df70
STRDO_rezerva4_0 | DIGITAL | IOD_STR | STR:.DO_rezerva4_0 | [6 empty] | 6157 | 1 | 0x0340df80
STRLetniCasDatumi111 | INT | IOD_STR | STR:.LetniCasDatumi[1,1,1] | [6 empty] | 6157 | 1 | 0x0340df90
STRLetniCasDatumi112 | INT | IOD_STR | STR:.LetniCasDatumi[1,1,2] | [6 empty] | 6157 | 1 | 0x0340df91
STRLetniCasDatumi121 | INT | IOD_STR | STR:.LetniCasDatumi[1,2,1] | [6 empty] | 6157 | 1 | 0x0340df92
STRLetniCasDatumi122 | INT | IOD_STR | STR:.LetniCasDatumi[1,2,2] | [6 empty] | 6157 | 1 | 0x0340df93
STRLetniCasDatumi131 | INT | IOD_STR | STR:.LetniCasDatumi[1,3,1] | [6 empty] | 6157 | 1 | 0x0340df94
STRLetniCasDatumi132 | INT | IOD_STR | STR:.LetniCasDatumi[1,3,2] | [6 empty] | 6157 | 1 | 0x0340df95
STRLetniCasDatumi141 | INT | IOD_STR | STR:.LetniCasDatumi[1,4,1] | [6 empty] | 6157 | 1 | 0x0340df96
STRLetniCasDatumi142 | INT | IOD_STR | STR:.LetniCasDatumi[1,4,2] | [6 empty] | 6157 | 1 | 0x0340df97
STRLetniCasDatumi211 | INT | IOD_STR | STR:.LetniCasDatumi[2,1,1] | [6 empty] | 6157 | 1 | 0x0340df98
STRLetniCasDatumi212 | INT | IOD_STR | STR:.LetniCasDatumi[2,1,2] | [6 empty] | 6157 | 1 | 0x0340df99
STRLetniCasDatumi221 | INT | IOD_STR | STR:.LetniCasDatumi[2,2,1] | [6 empty] | 6157 | 1 | 0x0340df9a
STRLetniCasDatumi222 | INT | IOD_STR | STR:.LetniCasDatumi[2,2,2] | [6 empty] | 6157 | 1 | 0x0340df9b
STRLetniCasDatumi231 | INT | IOD_STR | STR:.LetniCasDatumi[2,3,1] | [6 empty] | 6157 | 1 | 0x0340df9c
STRLetniCasDatumi232 | INT | IOD_STR | STR:.LetniCasDatumi[2,3,2] | [6 empty] | 6157 | 1 | 0x0340df9d
STRLetniCasDatumi241 | INT | IOD_STR | STR:.LetniCasDatumi[2,4,1] | [6 empty] | 6157 | 1 | 0x0340df9e
STRLetniCasDatumi242 | INT | IOD_STR | STR:.LetniCasDatumi[2,4,2] | [6 empty] | 6157 | 1 | 0x0340df9f
STRPrenosUrnika26 | DIGITAL | IOD_STR | STR:.PrenosUrnika[26] | [6 empty] | 6157 | 1 | 0x0340dfa0
STRPrenosUrnika27 | DIGITAL | IOD_STR | STR:.PrenosUrnika[27] | [6 empty] | 6157 | 1 | 0x0340dfb0
STRPrenosUrnika28 | DIGITAL | IOD_STR | STR:.PrenosUrnika[28] | [6 empty] | 6157 | 1 | 0x0340dfc0
STRPrenosUrnika29 | DIGITAL | IOD_STR | STR:.PrenosUrnika[29] | [6 empty] | 6157 | 1 | 0x0340dfd0
STRPrenosUrnika30 | DIGITAL | IOD_STR | STR:.PrenosUrnika[30] | [6 empty] | 6157 | 1 | 0x0340dfe0
STRPrenosUrnika31 | DIGITAL | IOD_STR | STR:.PrenosUrnika[31] | [6 empty] | 6157 | 1 | 0x0340dff0
STRPrenosUrnika32 | DIGITAL | IOD_STR | STR:.PrenosUrnika[32] | [6 empty] | 6157 | 1 | 0x0340e000
STRPrenosUrnika33 | DIGITAL | IOD_STR | STR:.PrenosUrnika[33] | [6 empty] | 6157 | 1 | 0x0340e010
STRPrenosUrnika34 | DIGITAL | IOD_STR | STR:.PrenosUrnika[34] | [6 empty] | 6157 | 1 | 0x0340e020
STRPrenosUrnika35 | DIGITAL | IOD_STR | STR:.PrenosUrnika[35] | [6 empty] | 6157 | 1 | 0x0340e030
STRPrenosUrnika36 | DIGITAL | IOD_STR | STR:.PrenosUrnika[36] | [6 empty] | 6157 | 1 | 0x0340e040
STRPrenosUrnika37 | DIGITAL | IOD_STR | STR:.PrenosUrnika[37] | [6 empty] | 6157 | 1 | 0x0340e050
STRPrenosUrnika38 | DIGITAL | IOD_STR | STR:.PrenosUrnika[38] | [6 empty] | 6157 | 1 | 0x0340e060
STRPrenosUrnika39 | DIGITAL | IOD_STR | STR:.PrenosUrnika[39] | [6 empty] | 6157 | 1 | 0x0340e070
STRPrenosUrnika40 | DIGITAL | IOD_STR | STR:.PrenosUrnika[40] | [6 empty] | 6157 | 1 | 0x0340e080
STRPrenosUrnika41 | DIGITAL | IOD_STR | STR:.PrenosUrnika[41] | [6 empty] | 6157 | 1 | 0x0340e090
STRPrenosUrnika42 | DIGITAL | IOD_STR | STR:.PrenosUrnika[42] | [6 empty] | 6157 | 1 | 0x0340e0a0
STRPrenosUrnika43 | DIGITAL | IOD_STR | STR:.PrenosUrnika[43] | [6 empty] | 6157 | 1 | 0x0340e0b0
STRPrenosUrnika44 | DIGITAL | IOD_STR | STR:.PrenosUrnika[44] | [6 empty] | 6157 | 1 | 0x0340e0c0
STRPrenosUrnika45 | DIGITAL | IOD_STR | STR:.PrenosUrnika[45] | [6 empty] | 6157 | 1 | 0x0340e0d0
STRPrenosUrnika46 | DIGITAL | IOD_STR | STR:.PrenosUrnika[46] | [6 empty] | 6157 | 1 | 0x0340e0e0
STRPrenosUrnika47 | DIGITAL | IOD_STR | STR:.PrenosUrnika[47] | [6 empty] | 6157 | 1 | 0x0340e0f0
STRPrenosUrnika48 | DIGITAL | IOD_STR | STR:.PrenosUrnika[48] | [6 empty] | 6157 | 1 | 0x0340e100
STRPrenosUrnika49 | DIGITAL | IOD_STR | STR:.PrenosUrnika[49] | [6 empty] | 6157 | 1 | 0x0340e110
STRPrenosUrnika50 | DIGITAL | IOD_STR | STR:.PrenosUrnika[50] | [6 empty] | 6157 | 1 | 0x0340e120
STRPrenosUrnika51 | DIGITAL | IOD_STR | STR:.PrenosUrnika[51] | [6 empty] | 6157 | 1 | 0x0340e130
STRPrenosUrnika52 | DIGITAL | IOD_STR | STR:.PrenosUrnika[52] | [6 empty] | 6157 | 1 | 0x0340e140
STRPrenosUrnika53 | DIGITAL | IOD_STR | STR:.PrenosUrnika[53] | [6 empty] | 6157 | 1 | 0x0340e150
STRPrenosUrnika54 | DIGITAL | IOD_STR | STR:.PrenosUrnika[54] | [6 empty] | 6157 | 1 | 0x0340e160
STRPrenosUrnika55 | DIGITAL | IOD_STR | STR:.PrenosUrnika[55] | [6 empty] | 6157 | 1 | 0x0340e170
STRPrenosUrnika56 | DIGITAL | IOD_STR | STR:.PrenosUrnika[56] | [6 empty] | 6157 | 1 | 0x0340e180
STRPrenosUrnika57 | DIGITAL | IOD_STR | STR:.PrenosUrnika[57] | [6 empty] | 6157 | 1 | 0x0340e190
STRPrenosUrnika58 | DIGITAL | IOD_STR | STR:.PrenosUrnika[58] | [6 empty] | 6157 | 1 | 0x0340e1a0
STRPrenosUrnika59 | DIGITAL | IOD_STR | STR:.PrenosUrnika[59] | [6 empty] | 6157 | 1 | 0x0340e1b0
STRPrenosUrnika60 | DIGITAL | IOD_STR | STR:.PrenosUrnika[60] | [6 empty] | 6157 | 1 | 0x0340e1c0
STRPrenosUrnika61 | DIGITAL | IOD_STR | STR:.PrenosUrnika[61] | [6 empty] | 6157 | 1 | 0x0340e1d0
STRPrenosUrnika62 | DIGITAL | IOD_STR | STR:.PrenosUrnika[62] | [6 empty] | 6157 | 1 | 0x0340e1e0
STRPrenosUrnika63 | DIGITAL | IOD_STR | STR:.PrenosUrnika[63] | [6 empty] | 6157 | 1 | 0x0340e1f0
STRPrenosUrnika64 | DIGITAL | IOD_STR | STR:.PrenosUrnika[64] | [6 empty] | 6157 | 1 | 0x0340e200
STRPrenosUrnika65 | DIGITAL | IOD_STR | STR:.PrenosUrnika[65] | [6 empty] | 6157 | 1 | 0x0340e210
STRPrenosUrnika66 | DIGITAL | IOD_STR | STR:.PrenosUrnika[66] | [6 empty] | 6157 | 1 | 0x0340e220
STRPrenosUrnika67 | DIGITAL | IOD_STR | STR:.PrenosUrnika[67] | [6 empty] | 6157 | 1 | 0x0340e230
STRPrenosUrnika68 | DIGITAL | IOD_STR | STR:.PrenosUrnika[68] | [6 empty] | 6157 | 1 | 0x0340e240
STRPrenosUrnika69 | DIGITAL | IOD_STR | STR:.PrenosUrnika[69] | [6 empty] | 6157 | 1 | 0x0340e250
STRPrenosUrnika70 | DIGITAL | IOD_STR | STR:.PrenosUrnika[70] | [6 empty] | 6157 | 1 | 0x0340e260
STRPrenosUrnika71 | DIGITAL | IOD_STR | STR:.PrenosUrnika[71] | [6 empty] | 6157 | 1 | 0x0340e270
STRPrenosUrnika72 | DIGITAL | IOD_STR | STR:.PrenosUrnika[72] | [6 empty] | 6157 | 1 | 0x0340e280
STRPrenosUrnika73 | DIGITAL | IOD_STR | STR:.PrenosUrnika[73] | [6 empty] | 6157 | 1 | 0x0340e290
STRPrenosUrnika74 | DIGITAL | IOD_STR | STR:.PrenosUrnika[74] | [6 empty] | 6157 | 1 | 0x0340e2a0
STRPrenosUrnika75 | DIGITAL | IOD_STR | STR:.PrenosUrnika[75] | [6 empty] | 6157 | 1 | 0x0340e2b0
STRPrenosUrnika76 | DIGITAL | IOD_STR | STR:.PrenosUrnika[76] | [6 empty] | 6157 | 1 | 0x0340e2c0
STRPrenosUrnika77 | DIGITAL | IOD_STR | STR:.PrenosUrnika[77] | [6 empty] | 6157 | 1 | 0x0340e2d0
STRPrenosUrnika78 | DIGITAL | IOD_STR | STR:.PrenosUrnika[78] | [6 empty] | 6157 | 1 | 0x0340e2e0
STRPrenosUrnika79 | DIGITAL | IOD_STR | STR:.PrenosUrnika[79] | [6 empty] | 6157 | 1 | 0x0340e2f0
STRPrenosUrnika80 | DIGITAL | IOD_STR | STR:.PrenosUrnika[80] | [6 empty] | 6157 | 1 | 0x0340e300
STRPrenosUrnika81 | DIGITAL | IOD_STR | STR:.PrenosUrnika[81] | [6 empty] | 6157 | 1 | 0x0340e310
STRPrenosUrnika82 | DIGITAL | IOD_STR | STR:.PrenosUrnika[82] | [6 empty] | 6157 | 1 | 0x0340e320
STRPrenosUrnika83 | DIGITAL | IOD_STR | STR:.PrenosUrnika[83] | [6 empty] | 6157 | 1 | 0x0340e330
STRPrenosUrnika84 | DIGITAL | IOD_STR | STR:.PrenosUrnika[84] | [6 empty] | 6157 | 1 | 0x0340e340
STRPrenosUrnika85 | DIGITAL | IOD_STR | STR:.PrenosUrnika[85] | [6 empty] | 6157 | 1 | 0x0340e350
STRPrenosUrnika86 | DIGITAL | IOD_STR | STR:.PrenosUrnika[86] | [6 empty] | 6157 | 1 | 0x0340e360
STRPrenosUrnika87 | DIGITAL | IOD_STR | STR:.PrenosUrnika[87] | [6 empty] | 6157 | 1 | 0x0340e370
STRPrenosUrnika88 | DIGITAL | IOD_STR | STR:.PrenosUrnika[88] | [6 empty] | 6157 | 1 | 0x0340e380
STRPrenosUrnika89 | DIGITAL | IOD_STR | STR:.PrenosUrnika[89] | [6 empty] | 6157 | 1 | 0x0340e390
STRPrenosUrnika90 | DIGITAL | IOD_STR | STR:.PrenosUrnika[90] | [6 empty] | 6157 | 1 | 0x0340e3a0
STRPrenosUrnika91 | DIGITAL | IOD_STR | STR:.PrenosUrnika[91] | [6 empty] | 6157 | 1 | 0x0340e3b0
STRPrenosUrnika92 | DIGITAL | IOD_STR | STR:.PrenosUrnika[92] | [6 empty] | 6157 | 1 | 0x0340e3c0
STRPrenosUrnika93 | DIGITAL | IOD_STR | STR:.PrenosUrnika[93] | [6 empty] | 6157 | 1 | 0x0340e3d0
STRPrenosUrnika94 | DIGITAL | IOD_STR | STR:.PrenosUrnika[94] | [6 empty] | 6157 | 1 | 0x0340e3e0
STRPrenosUrnika95 | DIGITAL | IOD_STR | STR:.PrenosUrnika[95] | [6 empty] | 6157 | 1 | 0x0340e3f0
STRPrenosUrnika96 | DIGITAL | IOD_STR | STR:.PrenosUrnika[96] | [6 empty] | 6157 | 1 | 0x0340e400
STRRazsvRocnoEnaLuc10 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[10] | [6 empty] | 6157 | 1 | 0x0340e410
STRRazsvRocnoEnaLuc11 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[11] | [6 empty] | 6157 | 1 | 0x0340e420
STRRazsvRocnoEnaLuc12 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[12] | [6 empty] | 6157 | 1 | 0x0340e430
STRRazsvRocnoEnaLuc13 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[13] | [6 empty] | 6157 | 1 | 0x0340e440
STRRazsvRocnoEnaLuc14 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[14] | [6 empty] | 6157 | 1 | 0x0340e450
STRRazsvRocnoEnaLuc15 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[15] | [6 empty] | 6157 | 1 | 0x0340e460
STRRazsvRocnoEnaLuc16 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[16] | [6 empty] | 6157 | 1 | 0x0340e470
STRRazsvRocnoEnaLuc17 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[17] | [6 empty] | 6157 | 1 | 0x0340e480
STRRazsvRocnoEnaLuc18 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[18] | [6 empty] | 6157 | 1 | 0x0340e490
STRRazsvRocnoEnaLuc19 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[19] | [6 empty] | 6157 | 1 | 0x0340e4a0
STRRazsvRocnoEnaLuc1 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[1] | [6 empty] | 6157 | 1 | 0x0340e4b0
STRRazsvRocnoEnaLuc20 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[20] | [6 empty] | 6157 | 1 | 0x0340e4c0
STRRazsvRocnoEnaLuc21 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[21] | [6 empty] | 6157 | 1 | 0x0340e4d0
STRRazsvRocnoEnaLuc22 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[22] | [6 empty] | 6157 | 1 | 0x0340e4e0
STRRazsvRocnoEnaLuc23 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[23] | [6 empty] | 6157 | 1 | 0x0340e4f0
STRRazsvRocnoEnaLuc24 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[24] | [6 empty] | 6157 | 1 | 0x0340e500
STRRazsvRocnoEnaLuc25 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[25] | [6 empty] | 6157 | 1 | 0x0340e510
STRRazsvRocnoEnaLuc2 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[2] | [6 empty] | 6157 | 1 | 0x0340e520
STRRazsvRocnoEnaLuc3 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[3] | [6 empty] | 6157 | 1 | 0x0340e530
STRRazsvRocnoEnaLuc4 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[4] | [6 empty] | 6157 | 1 | 0x0340e540
STRRazsvRocnoEnaLuc5 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[5] | [6 empty] | 6157 | 1 | 0x0340e550
STRRazsvRocnoEnaLuc6 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[6] | [6 empty] | 6157 | 1 | 0x0340e560
STRRazsvRocnoEnaLuc7 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[7] | [6 empty] | 6157 | 1 | 0x0340e570
STRRazsvRocnoEnaLuc8 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[8] | [6 empty] | 6157 | 1 | 0x0340e580
STRRazsvRocnoEnaLuc9 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[9] | [6 empty] | 6157 | 1 | 0x0340e590
STRUrnikSaveDan1Off1Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[1].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340e5a8
STRUrnikSaveDan1Off1Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[1].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340e5a9
STRUrnikSaveDan1Off2Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[1].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340e5aa
STRUrnikSaveDan1Off2Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[1].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340e5ab
STRUrnikSaveDan1Off3Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[1].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340e5ac
STRUrnikSaveDan1Off3Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[1].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340e5ad
STRUrnikSaveDan1On1Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[1].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340e5ae
STRUrnikSaveDan1On1Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[1].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340e5af
STRUrnikSaveDan1On2Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[1].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340e5b0
STRUrnikSaveDan1On2Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[1].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340e5b1
STRUrnikSaveDan1On3Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[1].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340e5b2
STRUrnikSaveDan1On3Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[1].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340e5b3
STRUrnikSaveDan2Off1Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[2].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340e5b4
STRUrnikSaveDan2Off1Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[2].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340e5b5
STRUrnikSaveDan2Off2Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[2].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340e5b6
STRUrnikSaveDan2Off2Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[2].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340e5b7
STRUrnikSaveDan2Off3Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[2].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340e5b8
STRUrnikSaveDan2Off3Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[2].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340e5b9
STRUrnikSaveDan2On1Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[2].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340e5ba
STRUrnikSaveDan2On1Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[2].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340e5bb
STRUrnikSaveDan2On2Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[2].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340e5bc
STRUrnikSaveDan2On2Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[2].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340e5bd
STRUrnikSaveDan2On3Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[2].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340e5be
STRUrnikSaveDan2On3Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[2].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340e5bf
STRUrnikSaveDan3Off1Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[3].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340e5c0
STRUrnikSaveDan3Off1Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[3].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340e5c1
STRUrnikSaveDan3Off2Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[3].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340e5c2
STRUrnikSaveDan3Off2Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[3].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340e5c3
STRUrnikSaveDan3Off3Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[3].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340e5c4
STRUrnikSaveDan3Off3Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[3].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340e5c5
STRUrnikSaveDan3On1Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[3].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340e5c6
STRUrnikSaveDan3On1Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[3].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340e5c7
STRUrnikSaveDan3On2Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[3].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340e5c8
STRUrnikSaveDan3On2Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[3].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340e5c9
STRUrnikSaveDan3On3Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[3].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340e5ca
STRUrnikSaveDan3On3Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[3].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340e5cb
STRUrnikSaveDan4Off1Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[4].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340e5cc
STRUrnikSaveDan4Off1Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[4].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340e5cd
STRUrnikSaveDan4Off2Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[4].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340e5ce
STRUrnikSaveDan4Off2Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[4].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340e5cf
STRUrnikSaveDan4Off3Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[4].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340e5d0
STRUrnikSaveDan4Off3Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[4].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340e5d1
STRUrnikSaveDan4On1Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[4].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340e5d2
STRUrnikSaveDan4On1Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[4].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340e5d3
STRUrnikSaveDan4On2Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[4].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340e5d4
STRUrnikSaveDan4On2Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[4].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340e5d5
STRUrnikSaveDan4On3Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[4].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340e5d6
STRUrnikSaveDan4On3Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[4].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340e5d7
STRUrnikSaveDan5Off1Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[5].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340e5d8
STRUrnikSaveDan5Off1Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[5].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340e5d9
STRUrnikSaveDan5Off2Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[5].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340e5da
STRUrnikSaveDan5Off2Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[5].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340e5db
STRUrnikSaveDan5Off3Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[5].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340e5dc
STRUrnikSaveDan5Off3Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[5].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340e5dd
STRUrnikSaveDan5On1Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[5].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340e5de
STRUrnikSaveDan5On1Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[5].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340e5df
STRUrnikSaveDan5On2Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[5].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340e5e0
STRUrnikSaveDan5On2Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[5].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340e5e1
STRUrnikSaveDan5On3Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[5].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340e5e2
STRUrnikSaveDan5On3Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[5].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340e5e3
STRUrnikSaveDan6Off1Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[6].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340e5e4
STRUrnikSaveDan6Off1Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[6].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340e5e5
STRUrnikSaveDan6Off2Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[6].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340e5e6
STRUrnikSaveDan6Off2Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[6].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340e5e7
STRUrnikSaveDan6Off3Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[6].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340e5e8
STRUrnikSaveDan6Off3Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[6].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340e5e9
STRUrnikSaveDan6On1Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[6].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340e5ea
STRUrnikSaveDan6On1Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[6].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340e5eb
STRUrnikSaveDan6On2Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[6].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340e5ec
STRUrnikSaveDan6On2Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[6].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340e5ed
STRUrnikSaveDan6On3Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[6].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340e5ee
STRUrnikSaveDan6On3Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[6].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340e5ef
STRUrnikSaveDan7Off1Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[7].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340e5f0
STRUrnikSaveDan7Off1Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[7].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340e5f1
STRUrnikSaveDan7Off2Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[7].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340e5f2
STRUrnikSaveDan7Off2Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[7].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340e5f3
STRUrnikSaveDan7Off3Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[7].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340e5f4
STRUrnikSaveDan7Off3Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[7].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340e5f5
STRUrnikSaveDan7On1Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[7].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340e5f6
STRUrnikSaveDan7On1Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[7].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340e5f7
STRUrnikSaveDan7On2Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[7].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340e5f8
STRUrnikSaveDan7On2Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[7].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340e5f9
STRUrnikSaveDan7On3Mna | BYTE | IOD_STR | STR:.UrnikSave.Dan[7].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340e5fa
STRUrnikSaveDan7On3Ura | BYTE | IOD_STR | STR:.UrnikSave.Dan[7].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340e5fb
STRValAI_TempTB5 | REAL | IOD_STR | STR:.ValAI_TempTB5 | [6 empty] | 6157 | 1 | 0x0340e5fc
STRXVH_CircNumber | BYTE | IOD_STR | STR:.XVH_CircNumber | [6 empty] | 6157 | 1 | 0x0340e5fd
STRXVH_CrpalkaGrfsPair | DIGITAL | IOD_STR | STR:.XVH_CrpalkaGrfsPair | [6 empty] | 6157 | 1 | 0x0340e600
STRXVH_CrpGrfsCommErr | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsCommErr | [6 empty] | 6157 | 1 | 0x0340e610
STRXVH_CrpGrfsON10 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[10] | [6 empty] | 6157 | 1 | 0x0340e620
STRXVH_CrpGrfsON11 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[11] | [6 empty] | 6157 | 1 | 0x0340e630
STRXVH_CrpGrfsON12 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[12] | [6 empty] | 6157 | 1 | 0x0340e640
STRXVH_CrpGrfsON13 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[13] | [6 empty] | 6157 | 1 | 0x0340e650
STRXVH_CrpGrfsON14 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[14] | [6 empty] | 6157 | 1 | 0x0340e660
STRXVH_CrpGrfsON1 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[1] | [6 empty] | 6157 | 1 | 0x0340e670
STRXVH_CrpGrfsON2 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[2] | [6 empty] | 6157 | 1 | 0x0340e680
STRXVH_CrpGrfsON3 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[3] | [6 empty] | 6157 | 1 | 0x0340e690
STRXVH_CrpGrfsON4 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[4] | [6 empty] | 6157 | 1 | 0x0340e6a0
STRXVH_CrpGrfsON5 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[5] | [6 empty] | 6157 | 1 | 0x0340e6b0
STRXVH_CrpGrfsON6 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[6] | [6 empty] | 6157 | 1 | 0x0340e6c0
STRXVH_CrpGrfsON7 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[7] | [6 empty] | 6157 | 1 | 0x0340e6d0
STRXVH_CrpGrfsON8 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[8] | [6 empty] | 6157 | 1 | 0x0340e6e0
STRXVH_CrpGrfsON9 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[9] | [6 empty] | 6157 | 1 | 0x0340e6f0
STRXVH_CrpGrfsPIDreset | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsPIDreset | [6 empty] | 6157 | 1 | 0x0340e700
STRXVH_CrpGrfsVisibleData10 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[10] | [6 empty] | 6157 | 1 | 0x0340e710
STRXVH_CrpGrfsVisibleData11 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[11] | [6 empty] | 6157 | 1 | 0x0340e720
STRXVH_CrpGrfsVisibleData12 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[12] | [6 empty] | 6157 | 1 | 0x0340e730
STRXVH_CrpGrfsVisibleData13 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[13] | [6 empty] | 6157 | 1 | 0x0340e740
STRXVH_CrpGrfsVisibleData14 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[14] | [6 empty] | 6157 | 1 | 0x0340e750
STRXVH_CrpGrfsVisibleData15 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[15] | [6 empty] | 6157 | 1 | 0x0340e760
STRXVH_CrpGrfsVisibleData16 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[16] | [6 empty] | 6157 | 1 | 0x0340e770
STRXVH_CrpGrfsVisibleData1 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[1] | [6 empty] | 6157 | 1 | 0x0340e780
STRXVH_CrpGrfsVisibleData2 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[2] | [6 empty] | 6157 | 1 | 0x0340e790
STRXVH_CrpGrfsVisibleData3 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[3] | [6 empty] | 6157 | 1 | 0x0340e7a0
STRXVH_CrpGrfsVisibleData4 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[4] | [6 empty] | 6157 | 1 | 0x0340e7b0
STRXVH_CrpGrfsVisibleData5 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[5] | [6 empty] | 6157 | 1 | 0x0340e7c0
STRXVH_CrpGrfsVisibleData6 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[6] | [6 empty] | 6157 | 1 | 0x0340e7d0
STRXVH_CrpGrfsVisibleData7 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[7] | [6 empty] | 6157 | 1 | 0x0340e7e0
STRXVH_CrpGrfsVisibleData8 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[8] | [6 empty] | 6157 | 1 | 0x0340e7f0
STRXVH_CrpGrfsVisibleData9 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[9] | [6 empty] | 6157 | 1 | 0x0340e800
STRXVH_CrpGrundfosNaCas | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosNaCas | [6 empty] | 6157 | 1 | 0x0340e810
STRXVH_CrpGrundfosNaTlak | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosNaTlak | [6 empty] | 6157 | 1 | 0x0340e820
STRXVH_CrpGrundfosON | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosON | [6 empty] | 6157 | 1 | 0x0340e830
STRXVH_CrpGrundfosResetAlarm | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosResetAlarm | [6 empty] | 6157 | 1 | 0x0340e840
STRXVH_CrpGrundfosResetAlarmLog | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosResetAlarmLog | [6 empty] | 6157 | 1 | 0x0340e850
STRXVH_CrpGrundfosSetRef | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosSetRef | [6 empty] | 6157 | 1 | 0x0340e860
STRXVH_CrpGrundfosTlakSP | REAL | IOD_STR | STR:.XVH_CrpGrundfosTlakSP | [6 empty] | 6157 | 1 | 0x0340e870
STRXVH_GrafTemp1 | REAL | IOD_STR | STR:.XVH_GrafTemp[1] | [6 empty] | 6157 | 1 | 0x0340e871
STRXVH_GrafTemp2 | REAL | IOD_STR | STR:.XVH_GrafTemp[2] | [6 empty] | 6157 | 1 | 0x0340e872
STRXVH_GrafTemp3 | REAL | IOD_STR | STR:.XVH_GrafTemp[3] | [6 empty] | 6157 | 1 | 0x0340e873
STRXVH_GrafTemp4 | REAL | IOD_STR | STR:.XVH_GrafTemp[4] | [6 empty] | 6157 | 1 | 0x0340e874
STRXVH_GrafTemp5 | REAL | IOD_STR | STR:.XVH_GrafTemp[5] | [6 empty] | 6157 | 1 | 0x0340e875
STRXVH_GrafVlaga1 | REAL | IOD_STR | STR:.XVH_GrafVlaga[1] | [6 empty] | 6157 | 1 | 0x0340e876
STRXVH_GrafVlaga2 | REAL | IOD_STR | STR:.XVH_GrafVlaga[2] | [6 empty] | 6157 | 1 | 0x0340e877
STRXVH_GrafVlaga3 | REAL | IOD_STR | STR:.XVH_GrafVlaga[3] | [6 empty] | 6157 | 1 | 0x0340e878
STRXVH_GrafVlaga4 | REAL | IOD_STR | STR:.XVH_GrafVlaga[4] | [6 empty] | 6157 | 1 | 0x0340e879
STRXVH_GrafVlaga5 | REAL | IOD_STR | STR:.XVH_GrafVlaga[5] | [6 empty] | 6157 | 1 | 0x0340e87a
STRXVH_KompStatus1 | BYTE | IOD_STR | STR:.XVH_KompStatus[1] | [6 empty] | 6157 | 1 | 0x0340e87b
STRXVH_KompStatus2 | BYTE | IOD_STR | STR:.XVH_KompStatus[2] | [6 empty] | 6157 | 1 | 0x0340e87c
STRXVH_RazsvOnOff | DIGITAL | IOD_STR | STR:.XVH_RazsvOnOff | [6 empty] | 6157 | 1 | 0x0340e880
STRXVH_ReferencaUpper | INT | IOD_STR | STR:.XVH_ReferencaUpper | [6 empty] | 6157 | 1 | 0x0340e890
STRXVH_setCircNum1 | DIGITAL | IOD_STR | STR:.XVH_setCircNum[1] | [6 empty] | 6157 | 1 | 0x0340e8a0
STRXVH_setCircNum2 | DIGITAL | IOD_STR | STR:.XVH_setCircNum[2] | [6 empty] | 6157 | 1 | 0x0340e8b0
STRXVH_setCircNum3 | DIGITAL | IOD_STR | STR:.XVH_setCircNum[3] | [6 empty] | 6157 | 1 | 0x0340e8c0
STRXVH_setCircNum4 | DIGITAL | IOD_STR | STR:.XVH_setCircNum[4] | [6 empty] | 6157 | 1 | 0x0340e8d0
STRXVH_setCircNum5 | DIGITAL | IOD_STR | STR:.XVH_setCircNum[5] | [6 empty] | 6157 | 1 | 0x0340e8e0
STRXVH_TlakSenzor | REAL | IOD_STR | STR:.XVH_TlakSenzor | [6 empty] | 6157 | 1 | 0x0340e8f0
STRXVH_UPSstatus | BYTE | IOD_STR | STR:.XVH_UPSstatus | [6 empty] | 6157 | 1 | 0x0340e8f1
STRXVH_UrnikDan1Off1Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340e8f2
STRXVH_UrnikDan1Off1Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340e8f3
STRXVH_UrnikDan1Off2Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340e8f4
STRXVH_UrnikDan1Off2Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340e8f5
STRXVH_UrnikDan1Off3Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340e8f6
STRXVH_UrnikDan1Off3Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340e8f7
STRXVH_UrnikDan1On1Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[1].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340e8f8
STRXVH_UrnikDan1On1Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[1].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340e8f9
STRXVH_UrnikDan1On2Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[1].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340e8fa
STRXVH_UrnikDan1On2Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[1].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340e8fb
STRXVH_UrnikDan1On3Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[1].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340e8fc
STRXVH_UrnikDan1On3Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[1].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340e8fd
STRXVH_UrnikDan2Off1Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340e8fe
STRXVH_UrnikDan2Off1Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340e8ff
STRXVH_UrnikDan2Off2Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340e900
STRXVH_UrnikDan2Off2Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340e901
STRXVH_UrnikDan2Off3Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340e902
STRXVH_UrnikDan2Off3Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340e903
STRXVH_UrnikDan2On1Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[2].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340e904
STRXVH_UrnikDan2On1Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[2].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340e905
STRXVH_UrnikDan2On2Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[2].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340e906
STRXVH_UrnikDan2On2Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[2].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340e907
STRXVH_UrnikDan2On3Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[2].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340e908
STRXVH_UrnikDan2On3Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[2].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340e909
STRXVH_UrnikDan3Off1Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340e90a
STRXVH_UrnikDan3Off1Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340e90b
STRXVH_UrnikDan3Off2Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340e90c
STRXVH_UrnikDan3Off2Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340e90d
STRXVH_UrnikDan3Off3Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340e90e
STRXVH_UrnikDan3Off3Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340e90f
STRXVH_UrnikDan3On1Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[3].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340e910
STRXVH_UrnikDan3On1Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[3].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340e911
STRXVH_UrnikDan3On2Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[3].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340e912
STRXVH_UrnikDan3On2Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[3].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340e913
STRXVH_UrnikDan3On3Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[3].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340e914
STRXVH_UrnikDan3On3Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[3].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340e915
STRXVH_UrnikDan4Off1Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340e916
STRXVH_UrnikDan4Off1Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340e917
STRXVH_UrnikDan4Off2Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340e918
STRXVH_UrnikDan4Off2Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340e919
STRXVH_UrnikDan4Off3Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340e91a
STRXVH_UrnikDan4Off3Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340e91b
STRXVH_UrnikDan4On1Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[4].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340e91c
STRXVH_UrnikDan4On1Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[4].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340e91d
STRXVH_UrnikDan4On2Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[4].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340e91e
STRXVH_UrnikDan4On2Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[4].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340e91f
STRXVH_UrnikDan4On3Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[4].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340e920
STRXVH_UrnikDan4On3Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[4].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340e921
STRXVH_UrnikDan5Off1Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340e922
STRXVH_UrnikDan5Off1Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340e923
STRXVH_UrnikDan5Off2Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340e924
STRXVH_UrnikDan5Off2Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340e925
STRXVH_UrnikDan5Off3Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340e926
STRXVH_UrnikDan5Off3Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340e927
STRXVH_UrnikDan5On1Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[5].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340e928
STRXVH_UrnikDan5On1Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[5].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340e929
STRXVH_UrnikDan5On2Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[5].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340e92a
STRXVH_UrnikDan5On2Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[5].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340e92b
STRXVH_UrnikDan5On3Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[5].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340e92c
STRXVH_UrnikDan5On3Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[5].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340e92d
STRXVH_UrnikDan6Off1Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340e92e
STRXVH_UrnikDan6Off1Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340e92f
STRXVH_UrnikDan6Off2Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340e930
STRXVH_UrnikDan6Off2Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340e931
STRXVH_UrnikDan6Off3Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340e932
STRXVH_UrnikDan6Off3Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340e933
STRXVH_UrnikDan6On1Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[6].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340e934
STRXVH_UrnikDan6On1Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[6].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340e935
STRXVH_UrnikDan6On2Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[6].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340e936
STRXVH_UrnikDan6On2Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[6].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340e937
STRXVH_UrnikDan6On3Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[6].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340e938
STRXVH_UrnikDan6On3Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[6].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340e939
STRXVH_UrnikDan7Off1Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[1].Mna | [6 empty] | 6157 | 1 | 0x0340e93a
STRXVH_UrnikDan7Off1Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[1].Ura | [6 empty] | 6157 | 1 | 0x0340e93b
STRXVH_UrnikDan7Off2Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[2].Mna | [6 empty] | 6157 | 1 | 0x0340e93c
STRXVH_UrnikDan7Off2Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[2].Ura | [6 empty] | 6157 | 1 | 0x0340e93d
STRXVH_UrnikDan7Off3Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[3].Mna | [6 empty] | 6157 | 1 | 0x0340e93e
STRXVH_UrnikDan7Off3Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[3].Ura | [6 empty] | 6157 | 1 | 0x0340e93f
STRXVH_UrnikDan7On1Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[7].On[1].Mna | [6 empty] | 6157 | 1 | 0x0340e940
STRXVH_UrnikDan7On1Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[7].On[1].Ura | [6 empty] | 6157 | 1 | 0x0340e941
STRXVH_UrnikDan7On2Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[7].On[2].Mna | [6 empty] | 6157 | 1 | 0x0340e942
STRXVH_UrnikDan7On2Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[7].On[2].Ura | [6 empty] | 6157 | 1 | 0x0340e943
STRXVH_UrnikDan7On3Mna | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[7].On[3].Mna | [6 empty] | 6157 | 1 | 0x0340e944
STRXVH_UrnikDan7On3Ura | BYTE | IOD_STR | STR:.XVH_Urnik.Dan[7].On[3].Ura | [6 empty] | 6157 | 1 | 0x0340e945
STRXVH_UrnikNalozi | DIGITAL | IOD_STR | STR:.XVH_UrnikNalozi | [6 empty] | 6157 | 1 | 0x0340e950
STRXVH_UrnikNonStop | DIGITAL | IOD_STR | STR:.XVH_UrnikNonStop | [6 empty] | 6157 | 1 | 0x0340e960
STRXVH_UrnikPotrdiVpis | DIGITAL | IOD_STR | STR:.XVH_UrnikPotrdiVpis | [6 empty] | 6157 | 1 | 0x0340e970
STRXVH_UrnikPreklicVpisa | DIGITAL | IOD_STR | STR:.XVH_UrnikPreklicVpisa | [6 empty] | 6157 | 1 | 0x0340e980
STRXVH_UrnikShrani | DIGITAL | IOD_STR | STR:.XVH_UrnikShrani | [6 empty] | 6157 | 1 | 0x0340e990
STRXVH_VentilTYValue11 | BYTE | IOD_STR | STR:.XVH_VentilTYValue[1,1] | [6 empty] | 6157 | 1 | 0x0340e9a7
STRXVH_VentilTYValue12 | BYTE | IOD_STR | STR:.XVH_VentilTYValue[1,2] | [6 empty] | 6157 | 1 | 0x0340e9a8
STRXVH_VentilTYValue21 | BYTE | IOD_STR | STR:.XVH_VentilTYValue[2,1] | [6 empty] | 6157 | 1 | 0x0340e9a9
STRXVH_VentilTYValue22 | BYTE | IOD_STR | STR:.XVH_VentilTYValue[2,2] | [6 empty] | 6157 | 1 | 0x0340e9aa
STRXVH_VentilTYValue31 | BYTE | IOD_STR | STR:.XVH_VentilTYValue[3,1] | [6 empty] | 6157 | 1 | 0x0340e9ab
STRXVH_VentilTYValue32 | BYTE | IOD_STR | STR:.XVH_VentilTYValue[3,2] | [6 empty] | 6157 | 1 | 0x0340e9ac
STRXVH_VentilTYValue41 | BYTE | IOD_STR | STR:.XVH_VentilTYValue[4,1] | [6 empty] | 6157 | 1 | 0x0340e9ad
STRXVH_VentilTYValue42 | BYTE | IOD_STR | STR:.XVH_VentilTYValue[4,2] | [6 empty] | 6157 | 1 | 0x0340e9ae
STRXVH_VlazilecStatus1 | BYTE | IOD_STR | STR:.XVH_VlazilecStatus[1] | [6 empty] | 6157 | 1 | 0x0340e9af
STRXVH_VlazilecStatus2 | BYTE | IOD_STR | STR:.XVH_VlazilecStatus[2] | [6 empty] | 6157 | 1 | 0x0340e9b0
STRXVH_VpisUrnika | DIGITAL | IOD_STR | STR:.XVH_VpisUrnika | [6 empty] | 6157 | 1 | 0x0340e9c0
STRXVHnum10 | BYTE | IOD_STR | STR:.XVHnum[10] | [6 empty] | 6157 | 1 | 0x0340e9d0
STRXVHnum11 | BYTE | IOD_STR | STR:.XVHnum[11] | [6 empty] | 6157 | 1 | 0x0340e9d1
STRXVHnum12 | BYTE | IOD_STR | STR:.XVHnum[12] | [6 empty] | 6157 | 1 | 0x0340e9d2
STRXVHnum13 | BYTE | IOD_STR | STR:.XVHnum[13] | [6 empty] | 6157 | 1 | 0x0340e9d3
STRXVHnum14 | BYTE | IOD_STR | STR:.XVHnum[14] | [6 empty] | 6157 | 1 | 0x0340e9d4
STRXVHnum1 | BYTE | IOD_STR | STR:.XVHnum[1] | [6 empty] | 6157 | 1 | 0x0340e9d5
STRXVHnum2 | BYTE | IOD_STR | STR:.XVHnum[2] | [6 empty] | 6157 | 1 | 0x0340e9d6
STRXVHnum3 | BYTE | IOD_STR | STR:.XVHnum[3] | [6 empty] | 6157 | 1 | 0x0340e9d7
STRXVHnum4 | BYTE | IOD_STR | STR:.XVHnum[4] | [6 empty] | 6157 | 1 | 0x0340e9d8
STRXVHnum5 | BYTE | IOD_STR | STR:.XVHnum[5] | [6 empty] | 6157 | 1 | 0x0340e9d9
STRXVHnum6 | BYTE | IOD_STR | STR:.XVHnum[6] | [6 empty] | 6157 | 1 | 0x0340e9da
STRXVHnum7 | BYTE | IOD_STR | STR:.XVHnum[7] | [6 empty] | 6157 | 1 | 0x0340e9db
STRXVHnum8 | BYTE | IOD_STR | STR:.XVHnum[8] | [6 empty] | 6157 | 1 | 0x0340e9dc
STRXVHnum9 | BYTE | IOD_STR | STR:.XVHnum[9] | [6 empty] | 6157 | 1 | 0x0340e9dd
STRErrCommScada2 | DIGITAL | IOD_STR | STR:.ErrCommScada2 | [6 empty] | 6157 | 1 | 0x0340e9f0
STRComSCADA2 | DIGITAL | IOD_STR | STR:.ComSCADA2 | [6 empty] | 6157 | 1 | 0x0340ea00
STRErrCommScada_Omogoci2 | DIGITAL | IOD_STR_disk | D4202 | [8 empty] | 0x0340ea10
STRServer_A_Izpad | DIGITAL | IOD_STR_disk | D4203 | [8 empty] | 0x0340ea20
STRServer_B_Izpad | DIGITAL | IOD_STR_disk | D4204 | [8 empty] | 0x0340ea30
STRComSCADA_stevec3 | INT | IOD_STR_disk | I4206 | [8 empty] | 0x0340ea40
STRComSCADA_stevec | INT | IOD_STR_disk | I4208 | [8 empty] | 0x0340ea41
STRComSCADA3 | DIGITAL | IOD_STR | STR:.ComSCADA3 | [8 empty] | 0x0340ea50
STRkom_nast_cas_izpada | UINT | IOD_STR | STR:.kom_nast_cas_izpada | [8 empty] | 0x0340ea60
STRCirc1MaximumDemandA2 | REAL | IOD_STR | STR:.Circ[1].MaximumDemandA2 | 0 | 1200 | 0 | 1200 | A | ###.# | 6157 | 1 | 0x0340ea61
STRCirc1MaximumDemandA3 | REAL | IOD_STR | STR:.Circ[1].MaximumDemandA3 | 0 | 1200 | 0 | 1200 | A | ###.# | 6157 | 1 | 0x0340ea62
STRCirc1RazEner_D_SCADA | REAL | IOD_STR | STR:.Circ[1].RazEner_D_SCADA | [6 empty] | 6157 | 1 | 0x0340ea63
STRCirc1RazEner_T_SCADA | REAL | IOD_STR | STR:.Circ[1].RazEner_T_SCADA | [6 empty] | 6157 | 1 | 0x0340ea64
STRCirc1RazEner_M_SCADA | REAL | IOD_STR | STR:.Circ[1].RazEner_M_SCADA | [6 empty] | 6157 | 1 | 0x0340ea65
STRCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Dnevne_energija_scada1 | [6 empty] | 6157 | 1 | 0x0340ea70
STRCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Dnevne_energija_scada2 | [6 empty] | 6157 | 1 | 0x0340ea80
STRCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Tedenska_energija_scada1 | [6 empty] | 6157 | 1 | 0x0340ea90
STRCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Tedenska_energija_scada2 | [6 empty] | 6157 | 1 | 0x0340eaa0
STRCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Mesecna_energija_scada1 | [6 empty] | 6157 | 1 | 0x0340eab0
STRCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Mesecna_energija_scada2 | [6 empty] | 6157 | 1 | 0x0340eac0
STRCirc_Vpis_Dnevne_energija_scada1_mem | DIGITAL | IOD_STR_disk | D4210 | [8 empty] | 0x0340ead0
STRCirc_Vpis_Dnevne_energija_scada2_mem | DIGITAL | IOD_STR_disk | D4211 | [8 empty] | 0x0340eae0
STRCirc_Vpis_Tedenska_energija_scada1_mem | DIGITAL | IOD_STR_disk | D4212 | [8 empty] | 0x0340eaf0
STRCirc_Vpis_Tedenska_energija_scada2_mem | DIGITAL | IOD_STR_disk | D4213 | [8 empty] | 0x0340eb00
STRCirc_Vpis_Mesecna_energija_scada1_mem | DIGITAL | IOD_STR_disk | D4214 | [8 empty] | 0x0340eb10
STRCirc_Vpis_Mesecna_energija_scada2_mem | DIGITAL | IOD_STR_disk | D4215 | [8 empty] | 0x0340eb20

## variable_1
STRAkumSanVodeTE1OnOff | DIGITAL | IOD_STR | STR:.AkumSanVodeTE1OnOff
STRAlarmGenCirc1 | DIGITAL | IOD_STR | STR:.AlarmGenCirc1
STRAlarmGenComm | DIGITAL | IOD_STR | STR:.AlarmGenComm
STRAlarmGenDI | DIGITAL | IOD_STR | STR:.AlarmGenDI
STRAlarmGenHladPost | DIGITAL | IOD_STR | STR:.AlarmGenHladPost
STRAlarmGenKlima1 | DIGITAL | IOD_STR | STR:.AlarmGenKlima1
STRAlarmGenKlima2 | DIGITAL | IOD_STR | STR:.AlarmGenKlima2
STRAlarmGenLopute | DIGITAL | IOD_STR | STR:.AlarmGenLopute
STRAlarmGenRest | DIGITAL | IOD_STR | STR:.AlarmGenRest
STRAlarmGenSenzor | DIGITAL | IOD_STR | STR:.AlarmGenSenzor
STRAlarmGenTemp | DIGITAL | IOD_STR | STR:.AlarmGenTemp
STRAlarmGenToplPost | DIGITAL | IOD_STR | STR:.AlarmGenToplPost
STRAlarmGenVent | DIGITAL | IOD_STR | STR:.AlarmGenVent
STRAlarmGenVTV | DIGITAL | IOD_STR | STR:.AlarmGenVTV
STRATVAlarmTemp | REAL | IOD_STR | STR:.ATVAlarmTemp
STRATVTempPrenizka | DIGITAL | IOD_STR | STR:.ATVTempPrenizka
STRCirc1CosFi_III | REAL | IOD_STR | STR:.Circ[1].CosFi_III
STRCirc1DelovnaEnergija | REAL | IOD_STR | STR:.Circ[1].DelovnaEnergija
STRCirc1DelovnaMoc_III | REAL | IOD_STR | STR:.Circ[1].DelovnaMoc_III
STRCirc1DelovnaMoc_L1 | REAL | IOD_STR | STR:.Circ[1].DelovnaMoc_L1
STRCirc1DelovnaMoc_L2 | REAL | IOD_STR | STR:.Circ[1].DelovnaMoc_L2
STRCirc1DelovnaMoc_L3 | REAL | IOD_STR | STR:.Circ[1].DelovnaMoc_L3
STRCirc1Frekvenca_L1 | REAL | IOD_STR | STR:.Circ[1].Frekvenca_L1
STRCirc1InduktivnaEnergija | REAL | IOD_STR | STR:.Circ[1].InduktivnaEnergija
STRCirc1InduktivnaMoc_III | REAL | IOD_STR | STR:.Circ[1].InduktivnaMoc_III
STRCirc1JalovaMoc_L1 | REAL | IOD_STR | STR:.Circ[1].JalovaMoc_L1
STRCirc1JalovaMoc_L2 | REAL | IOD_STR | STR:.Circ[1].JalovaMoc_L2
STRCirc1JalovaMoc_L3 | REAL | IOD_STR | STR:.Circ[1].JalovaMoc_L3
STRCirc1KapacitivnaEnergija | REAL | IOD_STR | STR:.Circ[1].KapacitivnaEnergija
STRCirc1KapacitivnaMoc_III | REAL | IOD_STR | STR:.Circ[1].KapacitivnaMoc_III
STRCirc1MaximumDemand | REAL | IOD_STR | STR:.Circ[1].MaximumDemand
STRCirc1Napetost_L1_L2 | REAL | IOD_STR | STR:.Circ[1].Napetost_L1_L2
STRCirc1Napetost_L1_N | REAL | IOD_STR | STR:.Circ[1].Napetost_L1_N
STRCirc1Napetost_L2_L3 | REAL | IOD_STR | STR:.Circ[1].Napetost_L2_L3
STRCirc1Napetost_L2_N | REAL | IOD_STR | STR:.Circ[1].Napetost_L2_N
STRCirc1Napetost_L3_L1 | REAL | IOD_STR | STR:.Circ[1].Napetost_L3_L1
STRCirc1Napetost_L3_N | REAL | IOD_STR | STR:.Circ[1].Napetost_L3_N
STRCirc1NavideznaMoc_III | REAL | IOD_STR | STR:.Circ[1].NavideznaMoc_III
STRCirc1NicelniTok | REAL | IOD_STR | STR:.Circ[1].NicelniTok
STRCirc1PowerFactor_III | REAL | IOD_STR | STR:.Circ[1].PowerFactor_III
STRCirc1PowerFactor_L1 | REAL | IOD_STR | STR:.Circ[1].PowerFactor_L1
STRCirc1PowerFactor_L2 | REAL | IOD_STR | STR:.Circ[1].PowerFactor_L2
STRCirc1PowerFactor_L3 | REAL | IOD_STR | STR:.Circ[1].PowerFactor_L3
STRCirc1THDI_L1 | REAL | IOD_STR | STR:.Circ[1].THDI_L1
STRCirc1THDI_L2 | REAL | IOD_STR | STR:.Circ[1].THDI_L2
STRCirc1THDI_L3 | REAL | IOD_STR | STR:.Circ[1].THDI_L3
STRCirc1THDV_L1 | REAL | IOD_STR | STR:.Circ[1].THDV_L1
STRCirc1THDV_L2 | REAL | IOD_STR | STR:.Circ[1].THDV_L2
STRCirc1THDV_L3 | REAL | IOD_STR | STR:.Circ[1].THDV_L3
STRCirc1Tok_L1 | REAL | IOD_STR | STR:.Circ[1].Tok_L1
STRCirc1Tok_L2 | REAL | IOD_STR | STR:.Circ[1].Tok_L2
STRCirc1Tok_L3 | REAL | IOD_STR | STR:.Circ[1].Tok_L3
STRCirc1TokPovprecje_III | REAL | IOD_STR | STR:.Circ[1].TokPovprecje_III
STRComSCADA | DIGITAL | IOD_STR | STR:.ComSCADA
STRComSCADA1 | DIGITAL | IOD_STR | STR:.ComSCADA1
STRCrpalkaMN1OnOff | DIGITAL | IOD_STR | STR:.CrpalkaMN1OnOff
STRCrpalkaTm11TM12OnOff | DIGITAL | IOD_STR | STR:.CrpalkaTm11TM12OnOff
STRCrpalkeDnfs1AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].AlarmAktiven
STRCrpalkeDnfs1Current | REAL | IOD_STR | STR:.CrpalkeDnfs[1].Current
STRCrpalkeDnfs1Deluje | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].Deluje
STRCrpalkeDnfs1PreklopkaMode | INT | IOD_STR | STR:.CrpalkeDnfs[1].PreklopkaMode
STRCrpalkeDnfs1QuickStop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].QuickStop
STRCrpalkeDnfs1RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].RemoteON
STRCrpalkeDnfs1Reset | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].Reset
STRCrpalkeDnfs1Start | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].Start
STRCrpalkeDnfs1StarterStatus | REAL | IOD_STR | STR:.CrpalkeDnfs[1].StarterStatus
STRCrpalkeDnfs1StarterStatus0do7 | INT | IOD_STR | STR:.CrpalkeDnfs[1].StarterStatus0do7 | BYTE
STRCrpalkeDnfs1StatusCrpalke | INT | IOD_STR | STR:.CrpalkeDnfs[1].StatusCrpalke | BYTE
STRCrpalkeDnfs1StatusKontaktor | INT | IOD_STR | STR:.CrpalkeDnfs[1].StatusKontaktor
STRCrpalkeDnfs1Stop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].Stop
STRCrpalkeDnfs1Temerature | REAL | IOD_STR | STR:.CrpalkeDnfs[1].Temerature
STRCrpalkeDnfs1TripCode | REAL | IOD_STR | STR:.CrpalkeDnfs[1].TripCode
STRCrpalkeDnfs1UreXC200 | REAL | IOD_STR | STR:.CrpalkeDnfs[1].UreXC200
STRCrpalkeDnfs2AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].AlarmAktiven
STRCrpalkeDnfs2Current | REAL | IOD_STR | STR:.CrpalkeDnfs[2].Current
STRCrpalkeDnfs2Deluje | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].Deluje
STRCrpalkeDnfs2PreklopkaMode | INT | IOD_STR | STR:.CrpalkeDnfs[2].PreklopkaMode
STRCrpalkeDnfs2QuickStop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].QuickStop
STRCrpalkeDnfs2RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].RemoteON
STRCrpalkeDnfs2Reset | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].Reset
STRCrpalkeDnfs2Start | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].Start
STRCrpalkeDnfs2StarterStatus | REAL | IOD_STR | STR:.CrpalkeDnfs[2].StarterStatus
STRCrpalkeDnfs2StarterStatus0do7 | INT | IOD_STR | STR:.CrpalkeDnfs[2].StarterStatus0do7 | BYTE
STRCrpalkeDnfs2StatusCrpalke | INT | IOD_STR | STR:.CrpalkeDnfs[2].StatusCrpalke | BYTE
STRCrpalkeDnfs2StatusKontaktor | INT | IOD_STR | STR:.CrpalkeDnfs[2].StatusKontaktor
STRCrpalkeDnfs2Stop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].Stop
STRCrpalkeDnfs2Temerature | REAL | IOD_STR | STR:.CrpalkeDnfs[2].Temerature
STRCrpalkeDnfs2TripCode | REAL | IOD_STR | STR:.CrpalkeDnfs[2].TripCode
STRCrpalkeDnfs2UreXC200 | REAL | IOD_STR | STR:.CrpalkeDnfs[2].UreXC200
STRCrpalkeDnfs3AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].AlarmAktiven
STRCrpalkeDnfs3Current | REAL | IOD_STR | STR:.CrpalkeDnfs[3].Current
STRCrpalkeDnfs3Deluje | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].Deluje
STRCrpalkeDnfs3PreklopkaMode | INT | IOD_STR | STR:.CrpalkeDnfs[3].PreklopkaMode
STRCrpalkeDnfs3QuickStop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].QuickStop
STRCrpalkeDnfs3RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].RemoteON
STRCrpalkeDnfs3Reset | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].Reset
STRCrpalkeDnfs3Start | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].Start
STRCrpalkeDnfs3StarterStatus | REAL | IOD_STR | STR:.CrpalkeDnfs[3].StarterStatus
STRCrpalkeDnfs3StarterStatus0do7 | INT | IOD_STR | STR:.CrpalkeDnfs[3].StarterStatus0do7 | BYTE
STRCrpalkeDnfs3StatusCrpalke | INT | IOD_STR | STR:.CrpalkeDnfs[3].StatusCrpalke | BYTE
STRCrpalkeDnfs3StatusKontaktor | INT | IOD_STR | STR:.CrpalkeDnfs[3].StatusKontaktor
STRCrpalkeDnfs3Stop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].Stop
STRCrpalkeDnfs3Temerature | REAL | IOD_STR | STR:.CrpalkeDnfs[3].Temerature
STRCrpalkeDnfs3TripCode | REAL | IOD_STR | STR:.CrpalkeDnfs[3].TripCode
STRCrpalkeDnfs3UreXC200 | REAL | IOD_STR | STR:.CrpalkeDnfs[3].UreXC200
STRCrpalkeDnfs4AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].AlarmAktiven
STRCrpalkeDnfs4Current | REAL | IOD_STR | STR:.CrpalkeDnfs[4].Current
STRCrpalkeDnfs4Deluje | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].Deluje
STRCrpalkeDnfs4PreklopkaMode | INT | IOD_STR | STR:.CrpalkeDnfs[4].PreklopkaMode
STRCrpalkeDnfs4QuickStop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].QuickStop
STRCrpalkeDnfs4RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].RemoteON
STRCrpalkeDnfs4Reset | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].Reset
STRCrpalkeDnfs4Start | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].Start
STRCrpalkeDnfs4StarterStatus | REAL | IOD_STR | STR:.CrpalkeDnfs[4].StarterStatus
STRCrpalkeDnfs4StarterStatus0do7 | INT | IOD_STR | STR:.CrpalkeDnfs[4].StarterStatus0do7 | BYTE
STRCrpalkeDnfs4StatusCrpalke | INT | IOD_STR | STR:.CrpalkeDnfs[4].StatusCrpalke | BYTE
STRCrpalkeDnfs4StatusKontaktor | INT | IOD_STR | STR:.CrpalkeDnfs[4].StatusKontaktor
STRCrpalkeDnfs4Stop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].Stop
STRCrpalkeDnfs4Temerature | REAL | IOD_STR | STR:.CrpalkeDnfs[4].Temerature
STRCrpalkeDnfs4TripCode | REAL | IOD_STR | STR:.CrpalkeDnfs[4].TripCode
STRCrpalkeDnfs4UreXC200 | REAL | IOD_STR | STR:.CrpalkeDnfs[4].UreXC200
STRCrpalkeGrfs10AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmActiveCode
STRCrpalkeGrfs10AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].AlarmAktiven
STRCrpalkeGrfs10AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmCodeLog1
STRCrpalkeGrfs10AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmCodeLog2
STRCrpalkeGrfs10AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmCodeLog3
STRCrpalkeGrfs10AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmCodeLog4
STRCrpalkeGrfs10AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmCodeLog5
STRCrpalkeGrfs10AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[0]
STRCrpalkeGrfs10AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[10]
STRCrpalkeGrfs10AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[11]
STRCrpalkeGrfs10AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[12]
STRCrpalkeGrfs10AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[13]
STRCrpalkeGrfs10AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[14]
STRCrpalkeGrfs10AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[15]
STRCrpalkeGrfs10AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[16]
STRCrpalkeGrfs10AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[1]
STRCrpalkeGrfs10AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[2]
STRCrpalkeGrfs10AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[3]
STRCrpalkeGrfs10AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[4]
STRCrpalkeGrfs10AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[5]
STRCrpalkeGrfs10AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[6]
STRCrpalkeGrfs10AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[7]
STRCrpalkeGrfs10AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[8]
STRCrpalkeGrfs10AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[9]
STRCrpalkeGrfs10AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmQSD1
STRCrpalkeGrfs10AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmQSD2
STRCrpalkeGrfs10AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmStart1
STRCrpalkeGrfs10AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmStart2
STRCrpalkeGrfs10AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmStop1
STRCrpalkeGrfs10AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmStop2
STRCrpalkeGrfs10AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmStop3
STRCrpalkeGrfs10AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmSurv1
STRCrpalkeGrfs10AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmSurv2
STRCrpalkeGrfs10ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[10].ControlSource
STRCrpalkeGrfs10DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[10].DeltaSetPoint
STRCrpalkeGrfs10Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].Deluje
STRCrpalkeGrfs10EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[10].EnergijaPoraba
STRCrpalkeGrfs10ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[10].ExternInputSetup
STRCrpalkeGrfs10ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[10].ExternInputsStatus
STRCrpalkeGrfs10FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[10].FrekPretvornikDCNapetost
STRCrpalkeGrfs10FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[10].FrekPretvornikDCTok
STRCrpalkeGrfs10FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[10].FreqMax
STRCrpalkeGrfs10FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[10].FreqMin
STRCrpalkeGrfs10FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[10].FreqUpper
STRCrpalkeGrfs10LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].LocalMode
STRCrpalkeGrfs10LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].LocalSetupMode1
STRCrpalkeGrfs10MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[10].MocMax
STRCrpalkeGrfs10MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[10].MocTrenutna
STRCrpalkeGrfs10MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[10].MotorHitrost
STRCrpalkeGrfs10MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[10].MotorTok
STRCrpalkeGrfs10NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[10].NapajanjeTok
STRCrpalkeGrfs10NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[10].NastavitevLokalna
STRCrpalkeGrfs10NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[10].NastavitevTrenutna
STRCrpalkeGrfs10PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[10].PreklopkaMode
STRCrpalkeGrfs10PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[10].PretokMax
STRCrpalkeGrfs10PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[10].PretokMin
STRCrpalkeGrfs10PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[10].PretokTrenutni
STRCrpalkeGrfs10PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[10].PritiskMax
STRCrpalkeGrfs10PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[10].PritiskTrenutni
STRCrpalkeGrfs10ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[10].ReferencaMotorjaHzV
STRCrpalkeGrfs10ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[10].ReferencaRemote
STRCrpalkeGrfs10Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[10].Relay1setup
STRCrpalkeGrfs10RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].RemoteON
STRCrpalkeGrfs10RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].RemoteSetupMode1
STRCrpalkeGrfs10Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].Reset2handkWhValues
STRCrpalkeGrfs10ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].ResetAlarm
STRCrpalkeGrfs10ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].ResetAlarmLog
STRCrpalkeGrfs10ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].ResetDevice
STRCrpalkeGrfs10SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetAutomatic
STRCrpalkeGrfs10SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetConstFreqMode
STRCrpalkeGrfs10SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetConstPress
STRCrpalkeGrfs10SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetLocalMode
STRCrpalkeGrfs10SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetMaxRunMode
STRCrpalkeGrfs10SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetMinRunMode
STRCrpalkeGrfs10SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetPropPress
STRCrpalkeGrfs10SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetReference
STRCrpalkeGrfs10SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetRemoteMode
STRCrpalkeGrfs10SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetTwinModeAlt
STRCrpalkeGrfs10SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetTwinModeSpare
STRCrpalkeGrfs10SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetTwinModeSync
STRCrpalkeGrfs10Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].Start
STRCrpalkeGrfs10StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[10].StatusCrpalke | BYTE
STRCrpalkeGrfs10StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].StatusMode1
STRCrpalkeGrfs10StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[10].StatusMode1co | BYTE
STRCrpalkeGrfs10StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[10].StatusMode1op | BYTE
STRCrpalkeGrfs10StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].StatusMode2
STRCrpalkeGrfs10StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[10].StatusMode3
STRCrpalkeGrfs10StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[10].StevecUr2h
STRCrpalkeGrfs10Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].Stop
STRCrpalkeGrfs10SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[10].SystemFeedback
STRCrpalkeGrfs10SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[10].SystemReference
STRCrpalkeGrfs10TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[10].TemperaturaMotorja
STRCrpalkeGrfs10UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[10].UreXC200
STRCrpalkeGrfs11AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmActiveCode
STRCrpalkeGrfs11AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].AlarmAktiven
STRCrpalkeGrfs11AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmCodeLog1
STRCrpalkeGrfs11AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmCodeLog2
STRCrpalkeGrfs11AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmCodeLog3
STRCrpalkeGrfs11AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmCodeLog4
STRCrpalkeGrfs11AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmCodeLog5
STRCrpalkeGrfs11AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[0]
STRCrpalkeGrfs11AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[10]
STRCrpalkeGrfs11AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[11]
STRCrpalkeGrfs11AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[12]
STRCrpalkeGrfs11AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[13]
STRCrpalkeGrfs11AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[14]
STRCrpalkeGrfs11AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[15]
STRCrpalkeGrfs11AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[16]
STRCrpalkeGrfs11AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[1]
STRCrpalkeGrfs11AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[2]
STRCrpalkeGrfs11AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[3]
STRCrpalkeGrfs11AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[4]
STRCrpalkeGrfs11AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[5]
STRCrpalkeGrfs11AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[6]
STRCrpalkeGrfs11AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[7]
STRCrpalkeGrfs11AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[8]
STRCrpalkeGrfs11AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[9]
STRCrpalkeGrfs11AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmQSD1
STRCrpalkeGrfs11AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmQSD2
STRCrpalkeGrfs11AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmStart1
STRCrpalkeGrfs11AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmStart2
STRCrpalkeGrfs11AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmStop1
STRCrpalkeGrfs11AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmStop2
STRCrpalkeGrfs11AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmStop3
STRCrpalkeGrfs11AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmSurv1
STRCrpalkeGrfs11AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmSurv2
STRCrpalkeGrfs11ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[11].ControlSource
STRCrpalkeGrfs11DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[11].DeltaSetPoint
STRCrpalkeGrfs11Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].Deluje
STRCrpalkeGrfs11EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[11].EnergijaPoraba
STRCrpalkeGrfs11ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[11].ExternInputSetup
STRCrpalkeGrfs11ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[11].ExternInputsStatus
STRCrpalkeGrfs11FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[11].FrekPretvornikDCNapetost
STRCrpalkeGrfs11FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[11].FrekPretvornikDCTok
STRCrpalkeGrfs11FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[11].FreqMax
STRCrpalkeGrfs11FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[11].FreqMin
STRCrpalkeGrfs11FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[11].FreqUpper
STRCrpalkeGrfs11LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].LocalMode
STRCrpalkeGrfs11LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].LocalSetupMode1
STRCrpalkeGrfs11MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[11].MocMax
STRCrpalkeGrfs11MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[11].MocTrenutna
STRCrpalkeGrfs11MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[11].MotorHitrost
STRCrpalkeGrfs11MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[11].MotorTok
STRCrpalkeGrfs11NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[11].NapajanjeTok
STRCrpalkeGrfs11NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[11].NastavitevLokalna
STRCrpalkeGrfs11NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[11].NastavitevTrenutna
STRCrpalkeGrfs11PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[11].PreklopkaMode
STRCrpalkeGrfs11PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[11].PretokMax
STRCrpalkeGrfs11PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[11].PretokMin
STRCrpalkeGrfs11PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[11].PretokTrenutni
STRCrpalkeGrfs11PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[11].PritiskMax
STRCrpalkeGrfs11PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[11].PritiskTrenutni
STRCrpalkeGrfs11ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[11].ReferencaMotorjaHzV
STRCrpalkeGrfs11ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[11].ReferencaRemote
STRCrpalkeGrfs11Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[11].Relay1setup
STRCrpalkeGrfs11RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].RemoteON
STRCrpalkeGrfs11RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].RemoteSetupMode1
STRCrpalkeGrfs11Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].Reset2handkWhValues
STRCrpalkeGrfs11ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].ResetAlarm
STRCrpalkeGrfs11ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].ResetAlarmLog
STRCrpalkeGrfs11ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].ResetDevice
STRCrpalkeGrfs11SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetAutomatic
STRCrpalkeGrfs11SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetConstFreqMode
STRCrpalkeGrfs11SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetConstPress
STRCrpalkeGrfs11SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetLocalMode
STRCrpalkeGrfs11SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetMaxRunMode
STRCrpalkeGrfs11SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetMinRunMode
STRCrpalkeGrfs11SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetPropPress
STRCrpalkeGrfs11SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetReference
STRCrpalkeGrfs11SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetRemoteMode
STRCrpalkeGrfs11SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetTwinModeAlt
STRCrpalkeGrfs11SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetTwinModeSpare
STRCrpalkeGrfs11SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetTwinModeSync
STRCrpalkeGrfs11Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].Start
STRCrpalkeGrfs11StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[11].StatusCrpalke | BYTE
STRCrpalkeGrfs11StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].StatusMode1
STRCrpalkeGrfs11StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[11].StatusMode1co | BYTE
STRCrpalkeGrfs11StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[11].StatusMode1op | BYTE
STRCrpalkeGrfs11StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].StatusMode2
STRCrpalkeGrfs11StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[11].StatusMode3
STRCrpalkeGrfs11StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[11].StevecUr2h
STRCrpalkeGrfs11Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].Stop
STRCrpalkeGrfs11SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[11].SystemFeedback
STRCrpalkeGrfs11SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[11].SystemReference
STRCrpalkeGrfs11TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[11].TemperaturaMotorja
STRCrpalkeGrfs11UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[11].UreXC200
STRCrpalkeGrfs12AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmActiveCode
STRCrpalkeGrfs12AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].AlarmAktiven
STRCrpalkeGrfs12AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmCodeLog1
STRCrpalkeGrfs12AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmCodeLog2
STRCrpalkeGrfs12AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmCodeLog3
STRCrpalkeGrfs12AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmCodeLog4
STRCrpalkeGrfs12AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmCodeLog5
STRCrpalkeGrfs12AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[0]
STRCrpalkeGrfs12AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[10]
STRCrpalkeGrfs12AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[11]
STRCrpalkeGrfs12AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[12]
STRCrpalkeGrfs12AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[13]
STRCrpalkeGrfs12AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[14]
STRCrpalkeGrfs12AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[15]
STRCrpalkeGrfs12AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[16]
STRCrpalkeGrfs12AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[1]
STRCrpalkeGrfs12AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[2]
STRCrpalkeGrfs12AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[3]
STRCrpalkeGrfs12AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[4]
STRCrpalkeGrfs12AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[5]
STRCrpalkeGrfs12AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[6]
STRCrpalkeGrfs12AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[7]
STRCrpalkeGrfs12AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[8]
STRCrpalkeGrfs12AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[9]
STRCrpalkeGrfs12AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmQSD1
STRCrpalkeGrfs12AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmQSD2
STRCrpalkeGrfs12AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmStart1
STRCrpalkeGrfs12AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmStart2
STRCrpalkeGrfs12AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmStop1
STRCrpalkeGrfs12AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmStop2
STRCrpalkeGrfs12AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmStop3
STRCrpalkeGrfs12AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmSurv1
STRCrpalkeGrfs12AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmSurv2
STRCrpalkeGrfs12ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[12].ControlSource
STRCrpalkeGrfs12DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[12].DeltaSetPoint
STRCrpalkeGrfs12Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].Deluje
STRCrpalkeGrfs12EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[12].EnergijaPoraba
STRCrpalkeGrfs12ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[12].ExternInputSetup
STRCrpalkeGrfs12ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[12].ExternInputsStatus
STRCrpalkeGrfs12FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[12].FrekPretvornikDCNapetost
STRCrpalkeGrfs12FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[12].FrekPretvornikDCTok
STRCrpalkeGrfs12FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[12].FreqMax
STRCrpalkeGrfs12FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[12].FreqMin
STRCrpalkeGrfs12FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[12].FreqUpper
STRCrpalkeGrfs12LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].LocalMode
STRCrpalkeGrfs12LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].LocalSetupMode1
STRCrpalkeGrfs12MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[12].MocMax
STRCrpalkeGrfs12MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[12].MocTrenutna
STRCrpalkeGrfs12MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[12].MotorHitrost
STRCrpalkeGrfs12MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[12].MotorTok
STRCrpalkeGrfs12NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[12].NapajanjeTok
STRCrpalkeGrfs12NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[12].NastavitevLokalna
STRCrpalkeGrfs12NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[12].NastavitevTrenutna
STRCrpalkeGrfs12PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[12].PreklopkaMode
STRCrpalkeGrfs12PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[12].PretokMax
STRCrpalkeGrfs12PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[12].PretokMin
STRCrpalkeGrfs12PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[12].PretokTrenutni
STRCrpalkeGrfs12PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[12].PritiskMax
STRCrpalkeGrfs12PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[12].PritiskTrenutni
STRCrpalkeGrfs12ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[12].ReferencaMotorjaHzV
STRCrpalkeGrfs12ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[12].ReferencaRemote
STRCrpalkeGrfs12Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[12].Relay1setup
STRCrpalkeGrfs12RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].RemoteON
STRCrpalkeGrfs12RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].RemoteSetupMode1
STRCrpalkeGrfs12Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].Reset2handkWhValues
STRCrpalkeGrfs12ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].ResetAlarm
STRCrpalkeGrfs12ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].ResetAlarmLog
STRCrpalkeGrfs12ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].ResetDevice
STRCrpalkeGrfs12SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetAutomatic
STRCrpalkeGrfs12SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetConstFreqMode
STRCrpalkeGrfs12SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetConstPress
STRCrpalkeGrfs12SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetLocalMode
STRCrpalkeGrfs12SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetMaxRunMode
STRCrpalkeGrfs12SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetMinRunMode
STRCrpalkeGrfs12SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetPropPress
STRCrpalkeGrfs12SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetReference
STRCrpalkeGrfs12SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetRemoteMode
STRCrpalkeGrfs12SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetTwinModeAlt
STRCrpalkeGrfs12SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetTwinModeSpare
STRCrpalkeGrfs12SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetTwinModeSync
STRCrpalkeGrfs12Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].Start
STRCrpalkeGrfs12StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[12].StatusCrpalke | BYTE
STRCrpalkeGrfs12StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].StatusMode1
STRCrpalkeGrfs12StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[12].StatusMode1co | BYTE
STRCrpalkeGrfs12StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[12].StatusMode1op | BYTE
STRCrpalkeGrfs12StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].StatusMode2
STRCrpalkeGrfs12StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[12].StatusMode3
STRCrpalkeGrfs12StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[12].StevecUr2h
STRCrpalkeGrfs12Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].Stop
STRCrpalkeGrfs12SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[12].SystemFeedback
STRCrpalkeGrfs12SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[12].SystemReference
STRCrpalkeGrfs12TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[12].TemperaturaMotorja
STRCrpalkeGrfs12UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[12].UreXC200
STRCrpalkeGrfs13AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmActiveCode
STRCrpalkeGrfs13AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].AlarmAktiven
STRCrpalkeGrfs13AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmCodeLog1
STRCrpalkeGrfs13AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmCodeLog2
STRCrpalkeGrfs13AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmCodeLog3
STRCrpalkeGrfs13AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmCodeLog4
STRCrpalkeGrfs13AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmCodeLog5
STRCrpalkeGrfs13AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[0]
STRCrpalkeGrfs13AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[10]
STRCrpalkeGrfs13AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[11]
STRCrpalkeGrfs13AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[12]
STRCrpalkeGrfs13AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[13]
STRCrpalkeGrfs13AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[14]
STRCrpalkeGrfs13AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[15]
STRCrpalkeGrfs13AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[16]
STRCrpalkeGrfs13AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[1]
STRCrpalkeGrfs13AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[2]
STRCrpalkeGrfs13AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[3]
STRCrpalkeGrfs13AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[4]
STRCrpalkeGrfs13AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[5]
STRCrpalkeGrfs13AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[6]
STRCrpalkeGrfs13AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[7]
STRCrpalkeGrfs13AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[8]
STRCrpalkeGrfs13AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[9]
STRCrpalkeGrfs13AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmQSD1
STRCrpalkeGrfs13AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmQSD2
STRCrpalkeGrfs13AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmStart1
STRCrpalkeGrfs13AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmStart2
STRCrpalkeGrfs13AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmStop1
STRCrpalkeGrfs13AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmStop2
STRCrpalkeGrfs13AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmStop3
STRCrpalkeGrfs13AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmSurv1
STRCrpalkeGrfs13AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmSurv2
STRCrpalkeGrfs13ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[13].ControlSource
STRCrpalkeGrfs13DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[13].DeltaSetPoint
STRCrpalkeGrfs13Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].Deluje
STRCrpalkeGrfs13EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[13].EnergijaPoraba
STRCrpalkeGrfs13ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[13].ExternInputSetup
STRCrpalkeGrfs13ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[13].ExternInputsStatus
STRCrpalkeGrfs13FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[13].FrekPretvornikDCNapetost
STRCrpalkeGrfs13FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[13].FrekPretvornikDCTok
STRCrpalkeGrfs13FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[13].FreqMax
STRCrpalkeGrfs13FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[13].FreqMin
STRCrpalkeGrfs13FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[13].FreqUpper
STRCrpalkeGrfs13LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].LocalMode
STRCrpalkeGrfs13LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].LocalSetupMode1
STRCrpalkeGrfs13MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[13].MocMax
STRCrpalkeGrfs13MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[13].MocTrenutna
STRCrpalkeGrfs13MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[13].MotorHitrost
STRCrpalkeGrfs13MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[13].MotorTok
STRCrpalkeGrfs13NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[13].NapajanjeTok
STRCrpalkeGrfs13NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[13].NastavitevLokalna
STRCrpalkeGrfs13NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[13].NastavitevTrenutna
STRCrpalkeGrfs13PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[13].PreklopkaMode
STRCrpalkeGrfs13PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[13].PretokMax
STRCrpalkeGrfs13PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[13].PretokMin
STRCrpalkeGrfs13PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[13].PretokTrenutni
STRCrpalkeGrfs13PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[13].PritiskMax
STRCrpalkeGrfs13PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[13].PritiskTrenutni
STRCrpalkeGrfs13ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[13].ReferencaMotorjaHzV
STRCrpalkeGrfs13ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[13].ReferencaRemote
STRCrpalkeGrfs13Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[13].Relay1setup
STRCrpalkeGrfs13RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].RemoteON
STRCrpalkeGrfs13RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].RemoteSetupMode1
STRCrpalkeGrfs13Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].Reset2handkWhValues
STRCrpalkeGrfs13ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].ResetAlarm
STRCrpalkeGrfs13ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].ResetAlarmLog
STRCrpalkeGrfs13ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].ResetDevice
STRCrpalkeGrfs13SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetAutomatic
STRCrpalkeGrfs13SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetConstFreqMode
STRCrpalkeGrfs13SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetConstPress
STRCrpalkeGrfs13SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetLocalMode
STRCrpalkeGrfs13SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetMaxRunMode
STRCrpalkeGrfs13SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetMinRunMode
STRCrpalkeGrfs13SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetPropPress
STRCrpalkeGrfs13SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetReference
STRCrpalkeGrfs13SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetRemoteMode
STRCrpalkeGrfs13SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetTwinModeAlt
STRCrpalkeGrfs13SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetTwinModeSpare
STRCrpalkeGrfs13SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetTwinModeSync
STRCrpalkeGrfs13Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].Start
STRCrpalkeGrfs13StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[13].StatusCrpalke | BYTE
STRCrpalkeGrfs13StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].StatusMode1
STRCrpalkeGrfs13StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[13].StatusMode1co | BYTE
STRCrpalkeGrfs13StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[13].StatusMode1op | BYTE
STRCrpalkeGrfs13StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].StatusMode2
STRCrpalkeGrfs13StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[13].StatusMode3
STRCrpalkeGrfs13StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[13].StevecUr2h
STRCrpalkeGrfs13Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].Stop
STRCrpalkeGrfs13SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[13].SystemFeedback
STRCrpalkeGrfs13SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[13].SystemReference
STRCrpalkeGrfs13TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[13].TemperaturaMotorja
STRCrpalkeGrfs13UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[13].UreXC200
STRCrpalkeGrfs14AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmActiveCode
STRCrpalkeGrfs14AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].AlarmAktiven
STRCrpalkeGrfs14AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmCodeLog1
STRCrpalkeGrfs14AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmCodeLog2
STRCrpalkeGrfs14AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmCodeLog3
STRCrpalkeGrfs14AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmCodeLog4
STRCrpalkeGrfs14AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmCodeLog5
STRCrpalkeGrfs14AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[0]
STRCrpalkeGrfs14AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[10]
STRCrpalkeGrfs14AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[11]
STRCrpalkeGrfs14AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[12]
STRCrpalkeGrfs14AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[13]
STRCrpalkeGrfs14AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[14]
STRCrpalkeGrfs14AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[15]
STRCrpalkeGrfs14AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[16]
STRCrpalkeGrfs14AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[1]
STRCrpalkeGrfs14AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[2]
STRCrpalkeGrfs14AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[3]
STRCrpalkeGrfs14AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[4]
STRCrpalkeGrfs14AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[5]
STRCrpalkeGrfs14AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[6]
STRCrpalkeGrfs14AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[7]
STRCrpalkeGrfs14AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[8]
STRCrpalkeGrfs14AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[9]
STRCrpalkeGrfs14AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmQSD1
STRCrpalkeGrfs14AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmQSD2
STRCrpalkeGrfs14AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmStart1
STRCrpalkeGrfs14AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmStart2
STRCrpalkeGrfs14AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmStop1
STRCrpalkeGrfs14AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmStop2
STRCrpalkeGrfs14AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmStop3
STRCrpalkeGrfs14AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmSurv1
STRCrpalkeGrfs14AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmSurv2
STRCrpalkeGrfs14ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[14].ControlSource
STRCrpalkeGrfs14DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[14].DeltaSetPoint
STRCrpalkeGrfs14Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].Deluje
STRCrpalkeGrfs14EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[14].EnergijaPoraba
STRCrpalkeGrfs14ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[14].ExternInputSetup
STRCrpalkeGrfs14ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[14].ExternInputsStatus
STRCrpalkeGrfs14FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[14].FrekPretvornikDCNapetost
STRCrpalkeGrfs14FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[14].FrekPretvornikDCTok
STRCrpalkeGrfs14FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[14].FreqMax
STRCrpalkeGrfs14FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[14].FreqMin
STRCrpalkeGrfs14FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[14].FreqUpper
STRCrpalkeGrfs14LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].LocalMode
STRCrpalkeGrfs14LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].LocalSetupMode1
STRCrpalkeGrfs14MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[14].MocMax
STRCrpalkeGrfs14MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[14].MocTrenutna
STRCrpalkeGrfs14MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[14].MotorHitrost
STRCrpalkeGrfs14MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[14].MotorTok
STRCrpalkeGrfs14NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[14].NapajanjeTok
STRCrpalkeGrfs14NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[14].NastavitevLokalna
STRCrpalkeGrfs14NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[14].NastavitevTrenutna
STRCrpalkeGrfs14PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[14].PreklopkaMode
STRCrpalkeGrfs14PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[14].PretokMax
STRCrpalkeGrfs14PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[14].PretokMin
STRCrpalkeGrfs14PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[14].PretokTrenutni
STRCrpalkeGrfs14PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[14].PritiskMax
STRCrpalkeGrfs14PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[14].PritiskTrenutni
STRCrpalkeGrfs14ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[14].ReferencaMotorjaHzV
STRCrpalkeGrfs14ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[14].ReferencaRemote
STRCrpalkeGrfs14Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[14].Relay1setup
STRCrpalkeGrfs14RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].RemoteON
STRCrpalkeGrfs14RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].RemoteSetupMode1
STRCrpalkeGrfs14Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].Reset2handkWhValues
STRCrpalkeGrfs14ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].ResetAlarm
STRCrpalkeGrfs14ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].ResetAlarmLog
STRCrpalkeGrfs14ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].ResetDevice
STRCrpalkeGrfs14SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetAutomatic
STRCrpalkeGrfs14SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetConstFreqMode
STRCrpalkeGrfs14SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetConstPress
STRCrpalkeGrfs14SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetLocalMode
STRCrpalkeGrfs14SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetMaxRunMode
STRCrpalkeGrfs14SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetMinRunMode
STRCrpalkeGrfs14SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetPropPress
STRCrpalkeGrfs14SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetReference
STRCrpalkeGrfs14SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetRemoteMode
STRCrpalkeGrfs14SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetTwinModeAlt
STRCrpalkeGrfs14SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetTwinModeSpare
STRCrpalkeGrfs14SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetTwinModeSync
STRCrpalkeGrfs14Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].Start
STRCrpalkeGrfs14StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[14].StatusCrpalke | BYTE
STRCrpalkeGrfs14StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].StatusMode1
STRCrpalkeGrfs14StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[14].StatusMode1co | BYTE
STRCrpalkeGrfs14StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[14].StatusMode1op | BYTE
STRCrpalkeGrfs14StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].StatusMode2
STRCrpalkeGrfs14StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[14].StatusMode3
STRCrpalkeGrfs14StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[14].StevecUr2h
STRCrpalkeGrfs14Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].Stop
STRCrpalkeGrfs14SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[14].SystemFeedback
STRCrpalkeGrfs14SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[14].SystemReference
STRCrpalkeGrfs14TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[14].TemperaturaMotorja
STRCrpalkeGrfs14UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[14].UreXC200
STRCrpalkeGrfs1AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmActiveCode
STRCrpalkeGrfs1AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].AlarmAktiven
STRCrpalkeGrfs1AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmCodeLog1
STRCrpalkeGrfs1AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmCodeLog2
STRCrpalkeGrfs1AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmCodeLog3
STRCrpalkeGrfs1AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmCodeLog4
STRCrpalkeGrfs1AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmCodeLog5
STRCrpalkeGrfs1AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[0]
STRCrpalkeGrfs1AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[10]
STRCrpalkeGrfs1AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[11]
STRCrpalkeGrfs1AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[12]
STRCrpalkeGrfs1AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[13]
STRCrpalkeGrfs1AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[14]
STRCrpalkeGrfs1AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[15]
STRCrpalkeGrfs1AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[16]
STRCrpalkeGrfs1AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[1]
STRCrpalkeGrfs1AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[2]
STRCrpalkeGrfs1AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[3]
STRCrpalkeGrfs1AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[4]
STRCrpalkeGrfs1AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[5]
STRCrpalkeGrfs1AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[6]
STRCrpalkeGrfs1AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[7]
STRCrpalkeGrfs1AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[8]
STRCrpalkeGrfs1AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[9]
STRCrpalkeGrfs1AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmQSD1
STRCrpalkeGrfs1AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmQSD2
STRCrpalkeGrfs1AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmStart1
STRCrpalkeGrfs1AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmStart2
STRCrpalkeGrfs1AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmStop1
STRCrpalkeGrfs1AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmStop2
STRCrpalkeGrfs1AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmStop3
STRCrpalkeGrfs1AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmSurv1
STRCrpalkeGrfs1AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmSurv2
STRCrpalkeGrfs1ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[1].ControlSource
STRCrpalkeGrfs1DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[1].DeltaSetPoint
STRCrpalkeGrfs1Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].Deluje
STRCrpalkeGrfs1EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[1].EnergijaPoraba
STRCrpalkeGrfs1ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[1].ExternInputSetup
STRCrpalkeGrfs1ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[1].ExternInputsStatus
STRCrpalkeGrfs1FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[1].FrekPretvornikDCNapetost
STRCrpalkeGrfs1FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[1].FrekPretvornikDCTok
STRCrpalkeGrfs1FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[1].FreqMax
STRCrpalkeGrfs1FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[1].FreqMin
STRCrpalkeGrfs1FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[1].FreqUpper
STRCrpalkeGrfs1LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].LocalMode
STRCrpalkeGrfs1LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].LocalSetupMode1
STRCrpalkeGrfs1MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[1].MocMax
STRCrpalkeGrfs1MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[1].MocTrenutna
STRCrpalkeGrfs1MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[1].MotorHitrost
STRCrpalkeGrfs1MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[1].MotorTok
STRCrpalkeGrfs1NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[1].NapajanjeTok
STRCrpalkeGrfs1NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[1].NastavitevLokalna
STRCrpalkeGrfs1NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[1].NastavitevTrenutna
STRCrpalkeGrfs1PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[1].PreklopkaMode
STRCrpalkeGrfs1PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[1].PretokMax
STRCrpalkeGrfs1PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[1].PretokMin
STRCrpalkeGrfs1PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[1].PretokTrenutni
STRCrpalkeGrfs1PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[1].PritiskMax
STRCrpalkeGrfs1PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[1].PritiskTrenutni
STRCrpalkeGrfs1ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[1].ReferencaMotorjaHzV
STRCrpalkeGrfs1ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[1].ReferencaRemote
STRCrpalkeGrfs1Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[1].Relay1setup
STRCrpalkeGrfs1RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].RemoteON
STRCrpalkeGrfs1RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].RemoteSetupMode1
STRCrpalkeGrfs1Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].Reset2handkWhValues
STRCrpalkeGrfs1ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].ResetAlarm
STRCrpalkeGrfs1ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].ResetAlarmLog
STRCrpalkeGrfs1ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].ResetDevice
STRCrpalkeGrfs1SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetAutomatic
STRCrpalkeGrfs1SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetConstFreqMode
STRCrpalkeGrfs1SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetConstPress
STRCrpalkeGrfs1SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetLocalMode
STRCrpalkeGrfs1SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetMaxRunMode
STRCrpalkeGrfs1SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetMinRunMode
STRCrpalkeGrfs1SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetPropPress
STRCrpalkeGrfs1SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetReference
STRCrpalkeGrfs1SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetRemoteMode
STRCrpalkeGrfs1SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetTwinModeAlt
STRCrpalkeGrfs1SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetTwinModeSpare
STRCrpalkeGrfs1SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetTwinModeSync
STRCrpalkeGrfs1Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].Start
STRCrpalkeGrfs1StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[1].StatusCrpalke | BYTE
STRCrpalkeGrfs1StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].StatusMode1
STRCrpalkeGrfs1StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[1].StatusMode1co | BYTE
STRCrpalkeGrfs1StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[1].StatusMode1op | BYTE
STRCrpalkeGrfs1StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].StatusMode2
STRCrpalkeGrfs1StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[1].StatusMode3
STRCrpalkeGrfs1StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[1].StevecUr2h
STRCrpalkeGrfs1Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].Stop
STRCrpalkeGrfs1SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[1].SystemFeedback
STRCrpalkeGrfs1SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[1].SystemReference
STRCrpalkeGrfs1TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[1].TemperaturaMotorja
STRCrpalkeGrfs1UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[1].UreXC200
STRCrpalkeGrfs2AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmActiveCode
STRCrpalkeGrfs2AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].AlarmAktiven
STRCrpalkeGrfs2AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmCodeLog1
STRCrpalkeGrfs2AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmCodeLog2
STRCrpalkeGrfs2AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmCodeLog3
STRCrpalkeGrfs2AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmCodeLog4
STRCrpalkeGrfs2AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmCodeLog5
STRCrpalkeGrfs2AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[0]
STRCrpalkeGrfs2AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[10]
STRCrpalkeGrfs2AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[11]
STRCrpalkeGrfs2AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[12]
STRCrpalkeGrfs2AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[13]
STRCrpalkeGrfs2AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[14]
STRCrpalkeGrfs2AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[15]
STRCrpalkeGrfs2AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[16]
STRCrpalkeGrfs2AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[1]
STRCrpalkeGrfs2AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[2]
STRCrpalkeGrfs2AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[3]
STRCrpalkeGrfs2AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[4]
STRCrpalkeGrfs2AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[5]
STRCrpalkeGrfs2AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[6]
STRCrpalkeGrfs2AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[7]
STRCrpalkeGrfs2AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[8]
STRCrpalkeGrfs2AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[9]
STRCrpalkeGrfs2AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmQSD1
STRCrpalkeGrfs2AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmQSD2
STRCrpalkeGrfs2AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmStart1
STRCrpalkeGrfs2AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmStart2
STRCrpalkeGrfs2AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmStop1
STRCrpalkeGrfs2AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmStop2
STRCrpalkeGrfs2AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmStop3
STRCrpalkeGrfs2AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmSurv1
STRCrpalkeGrfs2AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmSurv2
STRCrpalkeGrfs2ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[2].ControlSource
STRCrpalkeGrfs2DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[2].DeltaSetPoint
STRCrpalkeGrfs2Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].Deluje
STRCrpalkeGrfs2EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[2].EnergijaPoraba
STRCrpalkeGrfs2ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[2].ExternInputSetup
STRCrpalkeGrfs2ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[2].ExternInputsStatus
STRCrpalkeGrfs2FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[2].FrekPretvornikDCNapetost
STRCrpalkeGrfs2FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[2].FrekPretvornikDCTok
STRCrpalkeGrfs2FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[2].FreqMax
STRCrpalkeGrfs2FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[2].FreqMin
STRCrpalkeGrfs2FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[2].FreqUpper
STRCrpalkeGrfs2LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].LocalMode
STRCrpalkeGrfs2LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].LocalSetupMode1
STRCrpalkeGrfs2MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[2].MocMax
STRCrpalkeGrfs2MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[2].MocTrenutna
STRCrpalkeGrfs2MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[2].MotorHitrost
STRCrpalkeGrfs2MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[2].MotorTok
STRCrpalkeGrfs2NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[2].NapajanjeTok
STRCrpalkeGrfs2NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[2].NastavitevLokalna
STRCrpalkeGrfs2NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[2].NastavitevTrenutna
STRCrpalkeGrfs2PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[2].PreklopkaMode
STRCrpalkeGrfs2PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[2].PretokMax
STRCrpalkeGrfs2PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[2].PretokMin
STRCrpalkeGrfs2PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[2].PretokTrenutni
STRCrpalkeGrfs2PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[2].PritiskMax
STRCrpalkeGrfs2PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[2].PritiskTrenutni
STRCrpalkeGrfs2ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[2].ReferencaMotorjaHzV
STRCrpalkeGrfs2ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[2].ReferencaRemote
STRCrpalkeGrfs2Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[2].Relay1setup
STRCrpalkeGrfs2RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].RemoteON
STRCrpalkeGrfs2RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].RemoteSetupMode1
STRCrpalkeGrfs2Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].Reset2handkWhValues
STRCrpalkeGrfs2ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].ResetAlarm
STRCrpalkeGrfs2ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].ResetAlarmLog
STRCrpalkeGrfs2ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].ResetDevice
STRCrpalkeGrfs2SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetAutomatic
STRCrpalkeGrfs2SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetConstFreqMode
STRCrpalkeGrfs2SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetConstPress
STRCrpalkeGrfs2SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetLocalMode
STRCrpalkeGrfs2SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetMaxRunMode
STRCrpalkeGrfs2SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetMinRunMode
STRCrpalkeGrfs2SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetPropPress
STRCrpalkeGrfs2SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetReference
STRCrpalkeGrfs2SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetRemoteMode
STRCrpalkeGrfs2SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetTwinModeAlt
STRCrpalkeGrfs2SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetTwinModeSpare
STRCrpalkeGrfs2SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetTwinModeSync
STRCrpalkeGrfs2Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].Start
STRCrpalkeGrfs2StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[2].StatusCrpalke | BYTE
STRCrpalkeGrfs2StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].StatusMode1
STRCrpalkeGrfs2StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[2].StatusMode1co | BYTE
STRCrpalkeGrfs2StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[2].StatusMode1op | BYTE
STRCrpalkeGrfs2StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].StatusMode2
STRCrpalkeGrfs2StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[2].StatusMode3
STRCrpalkeGrfs2StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[2].StevecUr2h
STRCrpalkeGrfs2Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].Stop
STRCrpalkeGrfs2SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[2].SystemFeedback
STRCrpalkeGrfs2SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[2].SystemReference
STRCrpalkeGrfs2TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[2].TemperaturaMotorja
STRCrpalkeGrfs2UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[2].UreXC200
STRCrpalkeGrfs3AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmActiveCode
STRCrpalkeGrfs3AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].AlarmAktiven
STRCrpalkeGrfs3AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmCodeLog1
STRCrpalkeGrfs3AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmCodeLog2
STRCrpalkeGrfs3AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmCodeLog3
STRCrpalkeGrfs3AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmCodeLog4
STRCrpalkeGrfs3AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmCodeLog5
STRCrpalkeGrfs3AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[0]
STRCrpalkeGrfs3AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[10]
STRCrpalkeGrfs3AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[11]
STRCrpalkeGrfs3AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[12]
STRCrpalkeGrfs3AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[13]
STRCrpalkeGrfs3AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[14]
STRCrpalkeGrfs3AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[15]
STRCrpalkeGrfs3AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[16]
STRCrpalkeGrfs3AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[1]
STRCrpalkeGrfs3AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[2]
STRCrpalkeGrfs3AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[3]
STRCrpalkeGrfs3AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[4]
STRCrpalkeGrfs3AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[5]
STRCrpalkeGrfs3AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[6]
STRCrpalkeGrfs3AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[7]
STRCrpalkeGrfs3AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[8]
STRCrpalkeGrfs3AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[9]
STRCrpalkeGrfs3AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmQSD1
STRCrpalkeGrfs3AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmQSD2
STRCrpalkeGrfs3AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmStart1
STRCrpalkeGrfs3AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmStart2
STRCrpalkeGrfs3AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmStop1
STRCrpalkeGrfs3AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmStop2
STRCrpalkeGrfs3AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmStop3
STRCrpalkeGrfs3AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmSurv1
STRCrpalkeGrfs3AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmSurv2
STRCrpalkeGrfs3ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[3].ControlSource
STRCrpalkeGrfs3DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[3].DeltaSetPoint
STRCrpalkeGrfs3Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].Deluje
STRCrpalkeGrfs3EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[3].EnergijaPoraba
STRCrpalkeGrfs3ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[3].ExternInputSetup
STRCrpalkeGrfs3ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[3].ExternInputsStatus
STRCrpalkeGrfs3FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[3].FrekPretvornikDCNapetost
STRCrpalkeGrfs3FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[3].FrekPretvornikDCTok
STRCrpalkeGrfs3FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[3].FreqMax
STRCrpalkeGrfs3FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[3].FreqMin
STRCrpalkeGrfs3FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[3].FreqUpper
STRCrpalkeGrfs3LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].LocalMode
STRCrpalkeGrfs3LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].LocalSetupMode1
STRCrpalkeGrfs3MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[3].MocMax
STRCrpalkeGrfs3MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[3].MocTrenutna
STRCrpalkeGrfs3MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[3].MotorHitrost
STRCrpalkeGrfs3MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[3].MotorTok
STRCrpalkeGrfs3NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[3].NapajanjeTok
STRCrpalkeGrfs3NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[3].NastavitevLokalna
STRCrpalkeGrfs3NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[3].NastavitevTrenutna
STRCrpalkeGrfs3PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[3].PreklopkaMode
STRCrpalkeGrfs3PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[3].PretokMax
STRCrpalkeGrfs3PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[3].PretokMin
STRCrpalkeGrfs3PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[3].PretokTrenutni
STRCrpalkeGrfs3PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[3].PritiskMax
STRCrpalkeGrfs3PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[3].PritiskTrenutni
STRCrpalkeGrfs3ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[3].ReferencaMotorjaHzV
STRCrpalkeGrfs3ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[3].ReferencaRemote
STRCrpalkeGrfs3Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[3].Relay1setup
STRCrpalkeGrfs3RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].RemoteON
STRCrpalkeGrfs3RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].RemoteSetupMode1
STRCrpalkeGrfs3Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].Reset2handkWhValues
STRCrpalkeGrfs3ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].ResetAlarm
STRCrpalkeGrfs3ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].ResetAlarmLog
STRCrpalkeGrfs3ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].ResetDevice
STRCrpalkeGrfs3SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetAutomatic
STRCrpalkeGrfs3SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetConstFreqMode
STRCrpalkeGrfs3SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetConstPress
STRCrpalkeGrfs3SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetLocalMode
STRCrpalkeGrfs3SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetMaxRunMode
STRCrpalkeGrfs3SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetMinRunMode
STRCrpalkeGrfs3SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetPropPress
STRCrpalkeGrfs3SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetReference
STRCrpalkeGrfs3SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetRemoteMode
STRCrpalkeGrfs3SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetTwinModeAlt
STRCrpalkeGrfs3SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetTwinModeSpare
STRCrpalkeGrfs3SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetTwinModeSync
STRCrpalkeGrfs3Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].Start
STRCrpalkeGrfs3StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[3].StatusCrpalke | BYTE
STRCrpalkeGrfs3StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].StatusMode1
STRCrpalkeGrfs3StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[3].StatusMode1co | BYTE
STRCrpalkeGrfs3StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[3].StatusMode1op | BYTE
STRCrpalkeGrfs3StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].StatusMode2
STRCrpalkeGrfs3StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[3].StatusMode3
STRCrpalkeGrfs3StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[3].StevecUr2h
STRCrpalkeGrfs3Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].Stop
STRCrpalkeGrfs3SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[3].SystemFeedback
STRCrpalkeGrfs3SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[3].SystemReference
STRCrpalkeGrfs3TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[3].TemperaturaMotorja
STRCrpalkeGrfs3UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[3].UreXC200
STRCrpalkeGrfs4AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmActiveCode
STRCrpalkeGrfs4AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].AlarmAktiven
STRCrpalkeGrfs4AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmCodeLog1
STRCrpalkeGrfs4AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmCodeLog2
STRCrpalkeGrfs4AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmCodeLog3
STRCrpalkeGrfs4AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmCodeLog4
STRCrpalkeGrfs4AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmCodeLog5
STRCrpalkeGrfs4AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[0]
STRCrpalkeGrfs4AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[10]
STRCrpalkeGrfs4AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[11]
STRCrpalkeGrfs4AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[12]
STRCrpalkeGrfs4AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[13]
STRCrpalkeGrfs4AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[14]
STRCrpalkeGrfs4AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[15]
STRCrpalkeGrfs4AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[16]
STRCrpalkeGrfs4AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[1]
STRCrpalkeGrfs4AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[2]
STRCrpalkeGrfs4AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[3]
STRCrpalkeGrfs4AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[4]
STRCrpalkeGrfs4AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[5]
STRCrpalkeGrfs4AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[6]
STRCrpalkeGrfs4AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[7]
STRCrpalkeGrfs4AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[8]
STRCrpalkeGrfs4AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[9]
STRCrpalkeGrfs4AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmQSD1
STRCrpalkeGrfs4AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmQSD2
STRCrpalkeGrfs4AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmStart1
STRCrpalkeGrfs4AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmStart2
STRCrpalkeGrfs4AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmStop1
STRCrpalkeGrfs4AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmStop2
STRCrpalkeGrfs4AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmStop3
STRCrpalkeGrfs4AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmSurv1
STRCrpalkeGrfs4AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmSurv2
STRCrpalkeGrfs4ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[4].ControlSource
STRCrpalkeGrfs4DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[4].DeltaSetPoint
STRCrpalkeGrfs4Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].Deluje
STRCrpalkeGrfs4EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[4].EnergijaPoraba
STRCrpalkeGrfs4ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[4].ExternInputSetup
STRCrpalkeGrfs4ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[4].ExternInputsStatus
STRCrpalkeGrfs4FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[4].FrekPretvornikDCNapetost
STRCrpalkeGrfs4FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[4].FrekPretvornikDCTok
STRCrpalkeGrfs4FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[4].FreqMax
STRCrpalkeGrfs4FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[4].FreqMin
STRCrpalkeGrfs4FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[4].FreqUpper
STRCrpalkeGrfs4LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].LocalMode
STRCrpalkeGrfs4LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].LocalSetupMode1
STRCrpalkeGrfs4MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[4].MocMax
STRCrpalkeGrfs4MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[4].MocTrenutna
STRCrpalkeGrfs4MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[4].MotorHitrost
STRCrpalkeGrfs4MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[4].MotorTok
STRCrpalkeGrfs4NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[4].NapajanjeTok
STRCrpalkeGrfs4NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[4].NastavitevLokalna
STRCrpalkeGrfs4NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[4].NastavitevTrenutna
STRCrpalkeGrfs4PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[4].PreklopkaMode
STRCrpalkeGrfs4PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[4].PretokMax
STRCrpalkeGrfs4PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[4].PretokMin
STRCrpalkeGrfs4PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[4].PretokTrenutni
STRCrpalkeGrfs4PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[4].PritiskMax
STRCrpalkeGrfs4PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[4].PritiskTrenutni
STRCrpalkeGrfs4ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[4].ReferencaMotorjaHzV
STRCrpalkeGrfs4ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[4].ReferencaRemote
STRCrpalkeGrfs4Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[4].Relay1setup
STRCrpalkeGrfs4RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].RemoteON
STRCrpalkeGrfs4RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].RemoteSetupMode1
STRCrpalkeGrfs4Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].Reset2handkWhValues
STRCrpalkeGrfs4ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].ResetAlarm
STRCrpalkeGrfs4ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].ResetAlarmLog
STRCrpalkeGrfs4ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].ResetDevice
STRCrpalkeGrfs4SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetAutomatic
STRCrpalkeGrfs4SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetConstFreqMode
STRCrpalkeGrfs4SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetConstPress
STRCrpalkeGrfs4SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetLocalMode
STRCrpalkeGrfs4SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetMaxRunMode
STRCrpalkeGrfs4SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetMinRunMode
STRCrpalkeGrfs4SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetPropPress
STRCrpalkeGrfs4SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetReference
STRCrpalkeGrfs4SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetRemoteMode
STRCrpalkeGrfs4SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetTwinModeAlt
STRCrpalkeGrfs4SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetTwinModeSpare
STRCrpalkeGrfs4SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetTwinModeSync
STRCrpalkeGrfs4Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].Start
STRCrpalkeGrfs4StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[4].StatusCrpalke | BYTE
STRCrpalkeGrfs4StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].StatusMode1
STRCrpalkeGrfs4StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[4].StatusMode1co | BYTE
STRCrpalkeGrfs4StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[4].StatusMode1op | BYTE
STRCrpalkeGrfs4StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].StatusMode2
STRCrpalkeGrfs4StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[4].StatusMode3
STRCrpalkeGrfs4StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[4].StevecUr2h
STRCrpalkeGrfs4Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].Stop
STRCrpalkeGrfs4SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[4].SystemFeedback
STRCrpalkeGrfs4SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[4].SystemReference
STRCrpalkeGrfs4TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[4].TemperaturaMotorja
STRCrpalkeGrfs4UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[4].UreXC200
STRCrpalkeGrfs5AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmActiveCode
STRCrpalkeGrfs5AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].AlarmAktiven
STRCrpalkeGrfs5AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmCodeLog1
STRCrpalkeGrfs5AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmCodeLog2
STRCrpalkeGrfs5AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmCodeLog3
STRCrpalkeGrfs5AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmCodeLog4
STRCrpalkeGrfs5AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmCodeLog5
STRCrpalkeGrfs5AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[0]
STRCrpalkeGrfs5AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[10]
STRCrpalkeGrfs5AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[11]
STRCrpalkeGrfs5AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[12]
STRCrpalkeGrfs5AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[13]
STRCrpalkeGrfs5AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[14]
STRCrpalkeGrfs5AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[15]
STRCrpalkeGrfs5AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[16]
STRCrpalkeGrfs5AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[1]
STRCrpalkeGrfs5AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[2]
STRCrpalkeGrfs5AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[3]
STRCrpalkeGrfs5AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[4]
STRCrpalkeGrfs5AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[5]
STRCrpalkeGrfs5AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[6]
STRCrpalkeGrfs5AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[7]
STRCrpalkeGrfs5AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[8]
STRCrpalkeGrfs5AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[9]
STRCrpalkeGrfs5AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmQSD1
STRCrpalkeGrfs5AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmQSD2
STRCrpalkeGrfs5AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmStart1
STRCrpalkeGrfs5AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmStart2
STRCrpalkeGrfs5AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmStop1
STRCrpalkeGrfs5AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmStop2
STRCrpalkeGrfs5AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmStop3
STRCrpalkeGrfs5AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmSurv1
STRCrpalkeGrfs5AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmSurv2
STRCrpalkeGrfs5ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[5].ControlSource
STRCrpalkeGrfs5DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[5].DeltaSetPoint
STRCrpalkeGrfs5Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].Deluje
STRCrpalkeGrfs5EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[5].EnergijaPoraba
STRCrpalkeGrfs5ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[5].ExternInputSetup
STRCrpalkeGrfs5ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[5].ExternInputsStatus
STRCrpalkeGrfs5FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[5].FrekPretvornikDCNapetost
STRCrpalkeGrfs5FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[5].FrekPretvornikDCTok
STRCrpalkeGrfs5FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[5].FreqMax
STRCrpalkeGrfs5FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[5].FreqMin
STRCrpalkeGrfs5FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[5].FreqUpper
STRCrpalkeGrfs5LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].LocalMode
STRCrpalkeGrfs5LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].LocalSetupMode1
STRCrpalkeGrfs5MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[5].MocMax
STRCrpalkeGrfs5MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[5].MocTrenutna
STRCrpalkeGrfs5MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[5].MotorHitrost
STRCrpalkeGrfs5MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[5].MotorTok
STRCrpalkeGrfs5NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[5].NapajanjeTok
STRCrpalkeGrfs5NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[5].NastavitevLokalna
STRCrpalkeGrfs5NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[5].NastavitevTrenutna
STRCrpalkeGrfs5PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[5].PreklopkaMode
STRCrpalkeGrfs5PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[5].PretokMax
STRCrpalkeGrfs5PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[5].PretokMin
STRCrpalkeGrfs5PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[5].PretokTrenutni
STRCrpalkeGrfs5PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[5].PritiskMax
STRCrpalkeGrfs5PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[5].PritiskTrenutni
STRCrpalkeGrfs5ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[5].ReferencaMotorjaHzV
STRCrpalkeGrfs5ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[5].ReferencaRemote
STRCrpalkeGrfs5Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[5].Relay1setup
STRCrpalkeGrfs5RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].RemoteON
STRCrpalkeGrfs5RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].RemoteSetupMode1
STRCrpalkeGrfs5Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].Reset2handkWhValues
STRCrpalkeGrfs5ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].ResetAlarm
STRCrpalkeGrfs5ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].ResetAlarmLog
STRCrpalkeGrfs5ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].ResetDevice
STRCrpalkeGrfs5SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetAutomatic
STRCrpalkeGrfs5SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetConstFreqMode
STRCrpalkeGrfs5SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetConstPress
STRCrpalkeGrfs5SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetLocalMode
STRCrpalkeGrfs5SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetMaxRunMode
STRCrpalkeGrfs5SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetMinRunMode
STRCrpalkeGrfs5SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetPropPress
STRCrpalkeGrfs5SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetReference
STRCrpalkeGrfs5SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetRemoteMode
STRCrpalkeGrfs5SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetTwinModeAlt
STRCrpalkeGrfs5SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetTwinModeSpare
STRCrpalkeGrfs5SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetTwinModeSync
STRCrpalkeGrfs5Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].Start
STRCrpalkeGrfs5StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[5].StatusCrpalke | BYTE
STRCrpalkeGrfs5StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].StatusMode1
STRCrpalkeGrfs5StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[5].StatusMode1co | BYTE
STRCrpalkeGrfs5StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[5].StatusMode1op | BYTE
STRCrpalkeGrfs5StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].StatusMode2
STRCrpalkeGrfs5StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[5].StatusMode3
STRCrpalkeGrfs5StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[5].StevecUr2h
STRCrpalkeGrfs5Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].Stop
STRCrpalkeGrfs5SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[5].SystemFeedback
STRCrpalkeGrfs5SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[5].SystemReference
STRCrpalkeGrfs5TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[5].TemperaturaMotorja
STRCrpalkeGrfs5UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[5].UreXC200
STRCrpalkeGrfs6AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmActiveCode
STRCrpalkeGrfs6AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].AlarmAktiven
STRCrpalkeGrfs6AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmCodeLog1
STRCrpalkeGrfs6AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmCodeLog2
STRCrpalkeGrfs6AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmCodeLog3
STRCrpalkeGrfs6AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmCodeLog4
STRCrpalkeGrfs6AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmCodeLog5
STRCrpalkeGrfs6AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[0]
STRCrpalkeGrfs6AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[10]
STRCrpalkeGrfs6AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[11]
STRCrpalkeGrfs6AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[12]
STRCrpalkeGrfs6AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[13]
STRCrpalkeGrfs6AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[14]
STRCrpalkeGrfs6AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[15]
STRCrpalkeGrfs6AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[16]
STRCrpalkeGrfs6AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[1]
STRCrpalkeGrfs6AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[2]
STRCrpalkeGrfs6AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[3]
STRCrpalkeGrfs6AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[4]
STRCrpalkeGrfs6AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[5]
STRCrpalkeGrfs6AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[6]
STRCrpalkeGrfs6AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[7]
STRCrpalkeGrfs6AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[8]
STRCrpalkeGrfs6AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[9]
STRCrpalkeGrfs6AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmQSD1
STRCrpalkeGrfs6AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmQSD2
STRCrpalkeGrfs6AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmStart1
STRCrpalkeGrfs6AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmStart2
STRCrpalkeGrfs6AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmStop1
STRCrpalkeGrfs6AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmStop2
STRCrpalkeGrfs6AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmStop3
STRCrpalkeGrfs6AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmSurv1
STRCrpalkeGrfs6AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmSurv2
STRCrpalkeGrfs6ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[6].ControlSource
STRCrpalkeGrfs6DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[6].DeltaSetPoint
STRCrpalkeGrfs6Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].Deluje
STRCrpalkeGrfs6EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[6].EnergijaPoraba
STRCrpalkeGrfs6ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[6].ExternInputSetup
STRCrpalkeGrfs6ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[6].ExternInputsStatus
STRCrpalkeGrfs6FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[6].FrekPretvornikDCNapetost
STRCrpalkeGrfs6FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[6].FrekPretvornikDCTok
STRCrpalkeGrfs6FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[6].FreqMax
STRCrpalkeGrfs6FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[6].FreqMin
STRCrpalkeGrfs6FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[6].FreqUpper
STRCrpalkeGrfs6LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].LocalMode
STRCrpalkeGrfs6LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].LocalSetupMode1
STRCrpalkeGrfs6MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[6].MocMax
STRCrpalkeGrfs6MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[6].MocTrenutna
STRCrpalkeGrfs6MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[6].MotorHitrost
STRCrpalkeGrfs6MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[6].MotorTok
STRCrpalkeGrfs6NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[6].NapajanjeTok
STRCrpalkeGrfs6NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[6].NastavitevLokalna
STRCrpalkeGrfs6NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[6].NastavitevTrenutna
STRCrpalkeGrfs6PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[6].PreklopkaMode
STRCrpalkeGrfs6PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[6].PretokMax
STRCrpalkeGrfs6PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[6].PretokMin
STRCrpalkeGrfs6PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[6].PretokTrenutni
STRCrpalkeGrfs6PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[6].PritiskMax
STRCrpalkeGrfs6PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[6].PritiskTrenutni
STRCrpalkeGrfs6ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[6].ReferencaMotorjaHzV
STRCrpalkeGrfs6ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[6].ReferencaRemote
STRCrpalkeGrfs6Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[6].Relay1setup
STRCrpalkeGrfs6RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].RemoteON
STRCrpalkeGrfs6RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].RemoteSetupMode1
STRCrpalkeGrfs6Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].Reset2handkWhValues
STRCrpalkeGrfs6ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].ResetAlarm
STRCrpalkeGrfs6ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].ResetAlarmLog
STRCrpalkeGrfs6ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].ResetDevice
STRCrpalkeGrfs6SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetAutomatic
STRCrpalkeGrfs6SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetConstFreqMode
STRCrpalkeGrfs6SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetConstPress
STRCrpalkeGrfs6SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetLocalMode
STRCrpalkeGrfs6SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetMaxRunMode
STRCrpalkeGrfs6SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetMinRunMode
STRCrpalkeGrfs6SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetPropPress
STRCrpalkeGrfs6SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetReference
STRCrpalkeGrfs6SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetRemoteMode
STRCrpalkeGrfs6SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetTwinModeAlt
STRCrpalkeGrfs6SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetTwinModeSpare
STRCrpalkeGrfs6SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetTwinModeSync
STRCrpalkeGrfs6Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].Start
STRCrpalkeGrfs6StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[6].StatusCrpalke | BYTE
STRCrpalkeGrfs6StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].StatusMode1
STRCrpalkeGrfs6StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[6].StatusMode1co | BYTE
STRCrpalkeGrfs6StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[6].StatusMode1op | BYTE
STRCrpalkeGrfs6StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].StatusMode2
STRCrpalkeGrfs6StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[6].StatusMode3
STRCrpalkeGrfs6StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[6].StevecUr2h
STRCrpalkeGrfs6Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].Stop
STRCrpalkeGrfs6SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[6].SystemFeedback
STRCrpalkeGrfs6SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[6].SystemReference
STRCrpalkeGrfs6TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[6].TemperaturaMotorja
STRCrpalkeGrfs6UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[6].UreXC200
STRCrpalkeGrfs7AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmActiveCode
STRCrpalkeGrfs7AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].AlarmAktiven
STRCrpalkeGrfs7AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmCodeLog1
STRCrpalkeGrfs7AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmCodeLog2
STRCrpalkeGrfs7AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmCodeLog3
STRCrpalkeGrfs7AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmCodeLog4
STRCrpalkeGrfs7AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmCodeLog5
STRCrpalkeGrfs7AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[0]
STRCrpalkeGrfs7AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[10]
STRCrpalkeGrfs7AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[11]
STRCrpalkeGrfs7AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[12]
STRCrpalkeGrfs7AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[13]
STRCrpalkeGrfs7AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[14]
STRCrpalkeGrfs7AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[15]
STRCrpalkeGrfs7AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[16]
STRCrpalkeGrfs7AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[1]
STRCrpalkeGrfs7AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[2]
STRCrpalkeGrfs7AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[3]
STRCrpalkeGrfs7AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[4]
STRCrpalkeGrfs7AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[5]
STRCrpalkeGrfs7AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[6]
STRCrpalkeGrfs7AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[7]
STRCrpalkeGrfs7AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[8]
STRCrpalkeGrfs7AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[9]
STRCrpalkeGrfs7AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmQSD1
STRCrpalkeGrfs7AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmQSD2
STRCrpalkeGrfs7AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmStart1
STRCrpalkeGrfs7AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmStart2
STRCrpalkeGrfs7AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmStop1
STRCrpalkeGrfs7AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmStop2
STRCrpalkeGrfs7AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmStop3
STRCrpalkeGrfs7AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmSurv1
STRCrpalkeGrfs7AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmSurv2
STRCrpalkeGrfs7ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[7].ControlSource
STRCrpalkeGrfs7DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[7].DeltaSetPoint
STRCrpalkeGrfs7Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].Deluje
STRCrpalkeGrfs7EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[7].EnergijaPoraba
STRCrpalkeGrfs7ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[7].ExternInputSetup
STRCrpalkeGrfs7ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[7].ExternInputsStatus
STRCrpalkeGrfs7FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[7].FrekPretvornikDCNapetost
STRCrpalkeGrfs7FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[7].FrekPretvornikDCTok
STRCrpalkeGrfs7FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[7].FreqMax
STRCrpalkeGrfs7FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[7].FreqMin
STRCrpalkeGrfs7FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[7].FreqUpper
STRCrpalkeGrfs7LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].LocalMode
STRCrpalkeGrfs7LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].LocalSetupMode1
STRCrpalkeGrfs7MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[7].MocMax
STRCrpalkeGrfs7MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[7].MocTrenutna
STRCrpalkeGrfs7MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[7].MotorHitrost
STRCrpalkeGrfs7MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[7].MotorTok
STRCrpalkeGrfs7NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[7].NapajanjeTok
STRCrpalkeGrfs7NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[7].NastavitevLokalna
STRCrpalkeGrfs7NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[7].NastavitevTrenutna
STRCrpalkeGrfs7PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[7].PreklopkaMode
STRCrpalkeGrfs7PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[7].PretokMax
STRCrpalkeGrfs7PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[7].PretokMin
STRCrpalkeGrfs7PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[7].PretokTrenutni
STRCrpalkeGrfs7PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[7].PritiskMax
STRCrpalkeGrfs7PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[7].PritiskTrenutni
STRCrpalkeGrfs7ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[7].ReferencaMotorjaHzV
STRCrpalkeGrfs7ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[7].ReferencaRemote
STRCrpalkeGrfs7Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[7].Relay1setup
STRCrpalkeGrfs7RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].RemoteON
STRCrpalkeGrfs7RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].RemoteSetupMode1
STRCrpalkeGrfs7Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].Reset2handkWhValues
STRCrpalkeGrfs7ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].ResetAlarm
STRCrpalkeGrfs7ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].ResetAlarmLog
STRCrpalkeGrfs7ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].ResetDevice
STRCrpalkeGrfs7SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetAutomatic
STRCrpalkeGrfs7SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetConstFreqMode
STRCrpalkeGrfs7SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetConstPress
STRCrpalkeGrfs7SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetLocalMode
STRCrpalkeGrfs7SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetMaxRunMode
STRCrpalkeGrfs7SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetMinRunMode
STRCrpalkeGrfs7SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetPropPress
STRCrpalkeGrfs7SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetReference
STRCrpalkeGrfs7SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetRemoteMode
STRCrpalkeGrfs7SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetTwinModeAlt
STRCrpalkeGrfs7SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetTwinModeSpare
STRCrpalkeGrfs7SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetTwinModeSync
STRCrpalkeGrfs7Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].Start
STRCrpalkeGrfs7StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[7].StatusCrpalke | BYTE
STRCrpalkeGrfs7StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].StatusMode1
STRCrpalkeGrfs7StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[7].StatusMode1co | BYTE
STRCrpalkeGrfs7StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[7].StatusMode1op | BYTE
STRCrpalkeGrfs7StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].StatusMode2
STRCrpalkeGrfs7StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[7].StatusMode3
STRCrpalkeGrfs7StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[7].StevecUr2h
STRCrpalkeGrfs7Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].Stop
STRCrpalkeGrfs7SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[7].SystemFeedback
STRCrpalkeGrfs7SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[7].SystemReference
STRCrpalkeGrfs7TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[7].TemperaturaMotorja
STRCrpalkeGrfs7UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[7].UreXC200
STRCrpalkeGrfs8AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmActiveCode
STRCrpalkeGrfs8AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].AlarmAktiven
STRCrpalkeGrfs8AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmCodeLog1
STRCrpalkeGrfs8AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmCodeLog2
STRCrpalkeGrfs8AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmCodeLog3
STRCrpalkeGrfs8AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmCodeLog4
STRCrpalkeGrfs8AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmCodeLog5
STRCrpalkeGrfs8AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[0]
STRCrpalkeGrfs8AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[10]
STRCrpalkeGrfs8AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[11]
STRCrpalkeGrfs8AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[12]
STRCrpalkeGrfs8AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[13]
STRCrpalkeGrfs8AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[14]
STRCrpalkeGrfs8AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[15]
STRCrpalkeGrfs8AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[16]
STRCrpalkeGrfs8AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[1]
STRCrpalkeGrfs8AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[2]
STRCrpalkeGrfs8AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[3]
STRCrpalkeGrfs8AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[4]
STRCrpalkeGrfs8AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[5]
STRCrpalkeGrfs8AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[6]
STRCrpalkeGrfs8AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[7]
STRCrpalkeGrfs8AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[8]
STRCrpalkeGrfs8AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[9]
STRCrpalkeGrfs8AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmQSD1
STRCrpalkeGrfs8AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmQSD2
STRCrpalkeGrfs8AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmStart1
STRCrpalkeGrfs8AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmStart2
STRCrpalkeGrfs8AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmStop1
STRCrpalkeGrfs8AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmStop2
STRCrpalkeGrfs8AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmStop3
STRCrpalkeGrfs8AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmSurv1
STRCrpalkeGrfs8AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmSurv2
STRCrpalkeGrfs8ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[8].ControlSource
STRCrpalkeGrfs8DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[8].DeltaSetPoint
STRCrpalkeGrfs8Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].Deluje
STRCrpalkeGrfs8EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[8].EnergijaPoraba
STRCrpalkeGrfs8ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[8].ExternInputSetup
STRCrpalkeGrfs8ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[8].ExternInputsStatus
STRCrpalkeGrfs8FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[8].FrekPretvornikDCNapetost
STRCrpalkeGrfs8FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[8].FrekPretvornikDCTok
STRCrpalkeGrfs8FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[8].FreqMax
STRCrpalkeGrfs8FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[8].FreqMin
STRCrpalkeGrfs8FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[8].FreqUpper
STRCrpalkeGrfs8LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].LocalMode
STRCrpalkeGrfs8LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].LocalSetupMode1
STRCrpalkeGrfs8MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[8].MocMax
STRCrpalkeGrfs8MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[8].MocTrenutna
STRCrpalkeGrfs8MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[8].MotorHitrost
STRCrpalkeGrfs8MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[8].MotorTok
STRCrpalkeGrfs8NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[8].NapajanjeTok
STRCrpalkeGrfs8NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[8].NastavitevLokalna
STRCrpalkeGrfs8NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[8].NastavitevTrenutna
STRCrpalkeGrfs8PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[8].PreklopkaMode
STRCrpalkeGrfs8PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[8].PretokMax
STRCrpalkeGrfs8PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[8].PretokMin
STRCrpalkeGrfs8PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[8].PretokTrenutni
STRCrpalkeGrfs8PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[8].PritiskMax
STRCrpalkeGrfs8PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[8].PritiskTrenutni
STRCrpalkeGrfs8ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[8].ReferencaMotorjaHzV
STRCrpalkeGrfs8ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[8].ReferencaRemote
STRCrpalkeGrfs8Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[8].Relay1setup
STRCrpalkeGrfs8RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].RemoteON
STRCrpalkeGrfs8RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].RemoteSetupMode1
STRCrpalkeGrfs8Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].Reset2handkWhValues
STRCrpalkeGrfs8ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].ResetAlarm
STRCrpalkeGrfs8ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].ResetAlarmLog
STRCrpalkeGrfs8ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].ResetDevice
STRCrpalkeGrfs8SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetAutomatic
STRCrpalkeGrfs8SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetConstFreqMode
STRCrpalkeGrfs8SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetConstPress
STRCrpalkeGrfs8SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetLocalMode
STRCrpalkeGrfs8SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetMaxRunMode
STRCrpalkeGrfs8SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetMinRunMode
STRCrpalkeGrfs8SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetPropPress
STRCrpalkeGrfs8SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetReference
STRCrpalkeGrfs8SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetRemoteMode
STRCrpalkeGrfs8SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetTwinModeAlt
STRCrpalkeGrfs8SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetTwinModeSpare
STRCrpalkeGrfs8SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetTwinModeSync
STRCrpalkeGrfs8Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].Start
STRCrpalkeGrfs8StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[8].StatusCrpalke | BYTE
STRCrpalkeGrfs8StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].StatusMode1
STRCrpalkeGrfs8StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[8].StatusMode1co | BYTE
STRCrpalkeGrfs8StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[8].StatusMode1op | BYTE
STRCrpalkeGrfs8StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].StatusMode2
STRCrpalkeGrfs8StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[8].StatusMode3
STRCrpalkeGrfs8StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[8].StevecUr2h
STRCrpalkeGrfs8Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].Stop
STRCrpalkeGrfs8SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[8].SystemFeedback
STRCrpalkeGrfs8SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[8].SystemReference
STRCrpalkeGrfs8TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[8].TemperaturaMotorja
STRCrpalkeGrfs8UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[8].UreXC200
STRCrpalkeGrfs9AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmActiveCode
STRCrpalkeGrfs9AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].AlarmAktiven
STRCrpalkeGrfs9AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmCodeLog1
STRCrpalkeGrfs9AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmCodeLog2
STRCrpalkeGrfs9AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmCodeLog3
STRCrpalkeGrfs9AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmCodeLog4
STRCrpalkeGrfs9AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmCodeLog5
STRCrpalkeGrfs9AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[0]
STRCrpalkeGrfs9AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[10]
STRCrpalkeGrfs9AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[11]
STRCrpalkeGrfs9AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[12]
STRCrpalkeGrfs9AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[13]
STRCrpalkeGrfs9AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[14]
STRCrpalkeGrfs9AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[15]
STRCrpalkeGrfs9AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[16]
STRCrpalkeGrfs9AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[1]
STRCrpalkeGrfs9AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[2]
STRCrpalkeGrfs9AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[3]
STRCrpalkeGrfs9AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[4]
STRCrpalkeGrfs9AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[5]
STRCrpalkeGrfs9AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[6]
STRCrpalkeGrfs9AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[7]
STRCrpalkeGrfs9AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[8]
STRCrpalkeGrfs9AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[9]
STRCrpalkeGrfs9AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmQSD1
STRCrpalkeGrfs9AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmQSD2
STRCrpalkeGrfs9AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmStart1
STRCrpalkeGrfs9AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmStart2
STRCrpalkeGrfs9AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmStop1
STRCrpalkeGrfs9AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmStop2
STRCrpalkeGrfs9AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmStop3
STRCrpalkeGrfs9AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmSurv1
STRCrpalkeGrfs9AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmSurv2
STRCrpalkeGrfs9ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[9].ControlSource
STRCrpalkeGrfs9DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[9].DeltaSetPoint
STRCrpalkeGrfs9Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].Deluje
STRCrpalkeGrfs9EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[9].EnergijaPoraba
STRCrpalkeGrfs9ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[9].ExternInputSetup
STRCrpalkeGrfs9ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[9].ExternInputsStatus
STRCrpalkeGrfs9FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[9].FrekPretvornikDCNapetost
STRCrpalkeGrfs9FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[9].FrekPretvornikDCTok
STRCrpalkeGrfs9FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[9].FreqMax
STRCrpalkeGrfs9FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[9].FreqMin
STRCrpalkeGrfs9FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[9].FreqUpper
STRCrpalkeGrfs9LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].LocalMode
STRCrpalkeGrfs9LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].LocalSetupMode1
STRCrpalkeGrfs9MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[9].MocMax
STRCrpalkeGrfs9MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[9].MocTrenutna
STRCrpalkeGrfs9MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[9].MotorHitrost
STRCrpalkeGrfs9MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[9].MotorTok
STRCrpalkeGrfs9NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[9].NapajanjeTok
STRCrpalkeGrfs9NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[9].NastavitevLokalna
STRCrpalkeGrfs9NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[9].NastavitevTrenutna
STRCrpalkeGrfs9PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[9].PreklopkaMode
STRCrpalkeGrfs9PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[9].PretokMax
STRCrpalkeGrfs9PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[9].PretokMin
STRCrpalkeGrfs9PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[9].PretokTrenutni
STRCrpalkeGrfs9PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[9].PritiskMax
STRCrpalkeGrfs9PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[9].PritiskTrenutni
STRCrpalkeGrfs9ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[9].ReferencaMotorjaHzV
STRCrpalkeGrfs9ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[9].ReferencaRemote
STRCrpalkeGrfs9Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[9].Relay1setup
STRCrpalkeGrfs9RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].RemoteON
STRCrpalkeGrfs9RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].RemoteSetupMode1
STRCrpalkeGrfs9Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].Reset2handkWhValues
STRCrpalkeGrfs9ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].ResetAlarm
STRCrpalkeGrfs9ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].ResetAlarmLog
STRCrpalkeGrfs9ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].ResetDevice
STRCrpalkeGrfs9SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetAutomatic
STRCrpalkeGrfs9SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetConstFreqMode
STRCrpalkeGrfs9SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetConstPress
STRCrpalkeGrfs9SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetLocalMode
STRCrpalkeGrfs9SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetMaxRunMode
STRCrpalkeGrfs9SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetMinRunMode
STRCrpalkeGrfs9SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetPropPress
STRCrpalkeGrfs9SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetReference
STRCrpalkeGrfs9SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetRemoteMode
STRCrpalkeGrfs9SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetTwinModeAlt
STRCrpalkeGrfs9SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetTwinModeSpare
STRCrpalkeGrfs9SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetTwinModeSync
STRCrpalkeGrfs9Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].Start
STRCrpalkeGrfs9StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[9].StatusCrpalke | BYTE
STRCrpalkeGrfs9StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].StatusMode1
STRCrpalkeGrfs9StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[9].StatusMode1co | BYTE
STRCrpalkeGrfs9StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[9].StatusMode1op | BYTE
STRCrpalkeGrfs9StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].StatusMode2
STRCrpalkeGrfs9StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[9].StatusMode3
STRCrpalkeGrfs9StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[9].StevecUr2h
STRCrpalkeGrfs9Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].Stop
STRCrpalkeGrfs9SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[9].SystemFeedback
STRCrpalkeGrfs9SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[9].SystemReference
STRCrpalkeGrfs9TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[9].TemperaturaMotorja
STRCrpalkeGrfs9UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[9].UreXC200
STRCrpDanfossGenError1 | DIGITAL | IOD_STR | STR:.CrpDanfossGenError[1]
STRCrpDanfossGenError2 | DIGITAL | IOD_STR | STR:.CrpDanfossGenError[2]
STRCrpDanfossGenError3 | DIGITAL | IOD_STR | STR:.CrpDanfossGenError[3]
STRCrpDanfossGenError4 | DIGITAL | IOD_STR | STR:.CrpDanfossGenError[4]
STRCrpDanfossNaCas1 | DIGITAL | IOD_STR | STR:.CrpDanfossNaCas[1]
STRCrpDanfossNaCas2 | DIGITAL | IOD_STR | STR:.CrpDanfossNaCas[2]
STRCrpDanfossON1 | DIGITAL | IOD_STR | STR:.CrpDanfossON[1]
STRCrpDanfossON2 | DIGITAL | IOD_STR | STR:.CrpDanfossON[2]
STRCrpDanfossON3 | DIGITAL | IOD_STR | STR:.CrpDanfossON[3]
STRCrpDanfossON4 | DIGITAL | IOD_STR | STR:.CrpDanfossON[4]
STRCrpDanfossStatusError1 | DIGITAL | IOD_STR | STR:.CrpDanfossStatusError[1]
STRCrpDanfossStatusError2 | DIGITAL | IOD_STR | STR:.CrpDanfossStatusError[2]
STRCrpDanfossStatusError3 | DIGITAL | IOD_STR | STR:.CrpDanfossStatusError[3]
STRCrpDanfossStatusError4 | DIGITAL | IOD_STR | STR:.CrpDanfossStatusError[4]
STRCrpGrundfosGenError10 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[10]
STRCrpGrundfosGenError11 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[11]
STRCrpGrundfosGenError12 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[12]
STRCrpGrundfosGenError13 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[13]
STRCrpGrundfosGenError14 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[14]
STRCrpGrundfosGenError1 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[1]
STRCrpGrundfosGenError2 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[2]
STRCrpGrundfosGenError3 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[3]
STRCrpGrundfosGenError4 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[4]
STRCrpGrundfosGenError5 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[5]
STRCrpGrundfosGenError6 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[6]
STRCrpGrundfosGenError7 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[7]
STRCrpGrundfosGenError8 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[8]
STRCrpGrundfosGenError9 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[9]
STRCrpGrundfosNaCas1 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[1]
STRCrpGrundfosNaCas2 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[2]
STRCrpGrundfosNaCas3 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[3]
STRCrpGrundfosNaCas4 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[4]
STRCrpGrundfosNaCas5 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[5]
STRCrpGrundfosNaCas6 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[6]
STRCrpGrundfosNaCas7 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[7]
STRCrpGrundfosNaTlak1 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[1]
STRCrpGrundfosNaTlak2 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[2]
STRCrpGrundfosNaTlak3 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[3]
STRCrpGrundfosNaTlak4 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[4]
STRCrpGrundfosNaTlak5 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[5]
STRCrpGrundfosNaTlak6 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[6]
STRCrpGrundfosNaTlak7 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[7]
STRCrpGrundfosON10 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[10]
STRCrpGrundfosON11 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[11]
STRCrpGrundfosON12 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[12]
STRCrpGrundfosON13 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[13]
STRCrpGrundfosON14 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[14]
STRCrpGrundfosON1 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[1]
STRCrpGrundfosON2 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[2]
STRCrpGrundfosON3 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[3]
STRCrpGrundfosON4 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[4]
STRCrpGrundfosON5 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[5]
STRCrpGrundfosON6 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[6]
STRCrpGrundfosON7 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[7]
STRCrpGrundfosON8 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[8]
STRCrpGrundfosON9 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[9]
STRCrpGrundfosStatusError10 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[10]
STRCrpGrundfosStatusError11 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[11]
STRCrpGrundfosStatusError12 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[12]
STRCrpGrundfosStatusError13 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[13]
STRCrpGrundfosStatusError14 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[14]
STRCrpGrundfosStatusError1 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[1]
STRCrpGrundfosStatusError2 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[2]
STRCrpGrundfosStatusError3 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[3]
STRCrpGrundfosStatusError4 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[4]
STRCrpGrundfosStatusError5 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[5]
STRCrpGrundfosStatusError6 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[6]
STRCrpGrundfosStatusError7 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[7]
STRCrpGrundfosStatusError8 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[8]
STRCrpGrundfosStatusError9 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[9]
STRCrpGrundfosTlakSP1 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[1]
STRCrpGrundfosTlakSP2 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[2]
STRCrpGrundfosTlakSP3 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[3]
STRCrpGrundfosTlakSP4 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[4]
STRCrpGrundfosTlakSP5 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[5]
STRCrpGrundfosTlakSP6 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[6]
STRCrpGrundfosTlakSP7 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[7]
STRDanfossHMKontOnOff1 | DIGITAL | IOD_STR | STR:.DanfossHMKontOnOff[1]
STRDanfossHMKontOnOff2 | DIGITAL | IOD_STR | STR:.DanfossHMKontOnOff[2]
STRDanfossHMKontOnOff3 | DIGITAL | IOD_STR | STR:.DanfossHMKontOnOff[3]
STRDanfossHMKontOnOff4 | DIGITAL | IOD_STR | STR:.DanfossHMKontOnOff[4]
STRDateTimeDan | INT | IOD_STR | STR:.DateTime.Dan | BYTE
STRDateTimeLeto | INT | IOD_STR | STR:.DateTime.Leto | BYTE
STRDateTimeMesec | INT | IOD_STR | STR:.DateTime.Mesec | BYTE
STRDateTimeMinuta | INT | IOD_STR | STR:.DateTime.Minuta | BYTE
STRDateTimeSekunda | INT | IOD_STR | STR:.DateTime.Sekunda | BYTE
STRDateTimeUra | INT | IOD_STR | STR:.DateTime.Ura | BYTE
STRDI_230VAC_OK | DIGITAL | IOD_STR | STR:.DI_230VAC_OK
STRDI_24VAC_OK | DIGITAL | IOD_STR | STR:.DI_24VAC_OK
STRDI_24VDC_OK | DIGITAL | IOD_STR | STR:.DI_24VDC_OK
STRDI_AkumTopVodeAUTO | DIGITAL | IOD_STR | STR:.DI_AkumTopVodeAUTO
STRDI_AkumTopVodeKontON | DIGITAL | IOD_STR | STR:.DI_AkumTopVodeKontON
STRDI_CrpHM1AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM1AUTO
STRDI_CrpHM1endOFFtoON | DIGITAL | IOD_STR | STR:.DI_CrpHM1endOFFtoON
STRDI_CrpHM1ERR | DIGITAL | IOD_STR | STR:.DI_CrpHM1ERR
STRDI_CrpHM1kontON | DIGITAL | IOD_STR | STR:.DI_CrpHM1kontON
STRDI_CrpHM2AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM2AUTO
STRDI_CrpHM2endOFFtoON | DIGITAL | IOD_STR | STR:.DI_CrpHM2endOFFtoON
STRDI_CrpHM2ERR | DIGITAL | IOD_STR | STR:.DI_CrpHM2ERR
STRDI_CrpHM2kontON | DIGITAL | IOD_STR | STR:.DI_CrpHM2kontON
STRDI_CrpHM3AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM3AUTO
STRDI_CrpHM3endOFFtoON | DIGITAL | IOD_STR | STR:.DI_CrpHM3endOFFtoON
STRDI_CrpHM3ERR | DIGITAL | IOD_STR | STR:.DI_CrpHM3ERR
STRDI_CrpHM3kontON | DIGITAL | IOD_STR | STR:.DI_CrpHM3kontON
STRDI_CrpHM4AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM4AUTO
STRDI_CrpHM4endOFFtoON | DIGITAL | IOD_STR | STR:.DI_CrpHM4endOFFtoON
STRDI_CrpHM4ERR | DIGITAL | IOD_STR | STR:.DI_CrpHM4ERR
STRDI_CrpHM4kontON | DIGITAL | IOD_STR | STR:.DI_CrpHM4kontON
STRDI_CrpHM5AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM5AUTO
STRDI_CrpHM6AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM6AUTO
STRDI_CrpHM7AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM7AUTO
STRDI_CrpHM8AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM8AUTO
STRDI_CrpMN1AUTO | DIGITAL | IOD_STR | STR:.DI_CrpMN1AUTO
STRDI_CrpMN1kontON | DIGITAL | IOD_STR | STR:.DI_CrpMN1kontON
STRDI_CrpTM10AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM10AUTO
STRDI_CrpTM11TM12AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM11TM12AUTO
STRDI_CrpTM11TM12kontON | DIGITAL | IOD_STR | STR:.DI_CrpTM11TM12kontON
STRDI_CrpTM1AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM1AUTO
STRDI_CrpTM2AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM2AUTO
STRDI_CrpTM3AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM3AUTO
STRDI_CrpTM4AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM4AUTO
STRDI_CrpTM5AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM5AUTO
STRDI_CrpTM6AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM6AUTO
STRDI_CrpTM7AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM7AUTO
STRDI_CrpTM8AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM8AUTO
STRDI_CrpTM9AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM9AUTO
STRDI_GlStikaloDieselON | DIGITAL | IOD_STR | STR:.DI_GlStikaloDieselON
STRDI_GlStikaloMrezaON | DIGITAL | IOD_STR | STR:.DI_GlStikaloMrezaON
STRDI_GlStikaloUpsON | DIGITAL | IOD_STR | STR:.DI_GlStikaloUpsON
STRDI_HladStAUTO | DIGITAL | IOD_STR | STR:.DI_HladStAUTO
STRDI_HladStCrpHladH2OON | DIGITAL | IOD_STR | STR:.DI_HladStCrpHladH2OON
STRDI_HladStERR | DIGITAL | IOD_STR | STR:.DI_HladStERR
STRDI_Klima1ERR | DIGITAL | IOD_STR | STR:.DI_Klima1ERR
STRDI_Klima1filterZAM | DIGITAL | IOD_STR | STR:.DI_Klima1filterZAM
STRDI_Klima1FIRE | DIGITAL | IOD_STR | STR:.DI_Klima1FIRE
STRDI_Klima1OFFtoON | DIGITAL | IOD_STR | STR:.DI_Klima1OFFtoON
STRDI_Klima1ON | DIGITAL | IOD_STR | STR:.DI_Klima1ON
STRDI_Klima1zascStON | DIGITAL | IOD_STR | STR:.DI_Klima1zascStON
STRDI_Klima2ERR | DIGITAL | IOD_STR | STR:.DI_Klima2ERR
STRDI_Klima2filterZAM | DIGITAL | IOD_STR | STR:.DI_Klima2filterZAM
STRDI_Klima2FIRE | DIGITAL | IOD_STR | STR:.DI_Klima2FIRE
STRDI_Klima2OFFtoON | DIGITAL | IOD_STR | STR:.DI_Klima2OFFtoON
STRDI_Klima2ON | DIGITAL | IOD_STR | STR:.DI_Klima2ON
STRDI_Klima2zascStON | DIGITAL | IOD_STR | STR:.DI_Klima2zascStON
STRDI_Komp1ERR | DIGITAL | IOD_STR | STR:.DI_Komp1ERR
STRDI_Komp1ON | DIGITAL | IOD_STR | STR:.DI_Komp1ON
STRDI_Komp2ERR | DIGITAL | IOD_STR | STR:.DI_Komp2ERR
STRDI_Komp2ON | DIGITAL | IOD_STR | STR:.DI_Komp2ON
STRDI_Kond1AUTO | DIGITAL | IOD_STR | STR:.DI_Kond1AUTO
STRDI_Kond1FS1FS2 | DIGITAL | IOD_STR | STR:.DI_Kond1FS1FS2
STRDI_Kond1ON | DIGITAL | IOD_STR | STR:.DI_Kond1ON
STRDI_Kond1zascStON | DIGITAL | IOD_STR | STR:.DI_Kond1zascStON
STRDI_Kond2AUTO | DIGITAL | IOD_STR | STR:.DI_Kond2AUTO
STRDI_Kond2FS1FS2 | DIGITAL | IOD_STR | STR:.DI_Kond2FS1FS2
STRDI_Kond2ON | DIGITAL | IOD_STR | STR:.DI_Kond2ON
STRDI_Kond2zascStON | DIGITAL | IOD_STR | STR:.DI_Kond2zascStON
STRDI_Kond3AUTO | DIGITAL | IOD_STR | STR:.DI_Kond3AUTO
STRDI_Kond3FS1FS2 | DIGITAL | IOD_STR | STR:.DI_Kond3FS1FS2
STRDI_Kond3ON | DIGITAL | IOD_STR | STR:.DI_Kond3ON
STRDI_Kond3zascStON | DIGITAL | IOD_STR | STR:.DI_Kond3zascStON
STRDI_Lop1PL1Odprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL1Odprta
STRDI_Lop1PL1Zaprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL1Zaprta
STRDI_Lop1PL2Odprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL2Odprta
STRDI_Lop1PL2Zaprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL2Zaprta
STRDI_Lop1PL3Odprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL3Odprta
STRDI_Lop1PL3Zaprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL3Zaprta
STRDI_Lop3Y1Odprta | DIGITAL | IOD_STR | STR:.DI_Lop3Y1Odprta
STRDI_Lop3Y1Zaprta | DIGITAL | IOD_STR | STR:.DI_Lop3Y1Zaprta
STRDI_Lop4Y1Odprta | DIGITAL | IOD_STR | STR:.DI_Lop4Y1Odprta
STRDI_Lop4Y1Zaprta | DIGITAL | IOD_STR | STR:.DI_Lop4Y1Zaprta
STRDI_PotrditevAlarmov | DIGITAL | IOD_STR | STR:.DI_PotrditevAlarmov
STRDI_RazlitjeVodeEXP1 | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeEXP1
STRDI_RazlitjeVodeEXP2 | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeEXP2
STRDI_RazlitjeVodeHP | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeHP
STRDI_RazlitjeVodeK1 | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeK1
STRDI_RazlitjeVodeK2 | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeK2
STRDI_RazlitjeVodeTP | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeTP
STRDI_ToplPostGenErr | DIGITAL | IOD_STR | STR:.DI_ToplPostGenErr
STRDI_UPS_Alarm | DIGITAL | IOD_STR | STR:.DI_UPS_Alarm
STRDI_UPS_BatNacin | DIGITAL | IOD_STR | STR:.DI_UPS_BatNacin
STRDI_UPS_Polnjenje | DIGITAL | IOD_STR | STR:.DI_UPS_Polnjenje
STRDI_Vent1Auto | DIGITAL | IOD_STR | STR:.DI_Vent1Auto
STRDI_Vent1kontON | DIGITAL | IOD_STR | STR:.DI_Vent1kontON
STRDI_Vent2Auto | DIGITAL | IOD_STR | STR:.DI_Vent2Auto
STRDI_Vent2kontON | DIGITAL | IOD_STR | STR:.DI_Vent2kontON
STRDI_Vent3Auto | DIGITAL | IOD_STR | STR:.DI_Vent3Auto
STRDI_Vent3kontON | DIGITAL | IOD_STR | STR:.DI_Vent3kontON
STRDI_Vent4Auto | DIGITAL | IOD_STR | STR:.DI_Vent4Auto
STRDI_Vent4kontON | DIGITAL | IOD_STR | STR:.DI_Vent4kontON
STRDI_Vent5Auto | DIGITAL | IOD_STR | STR:.DI_Vent5Auto
STRDI_Vent5kontON | DIGITAL | IOD_STR | STR:.DI_Vent5kontON
STRDI_Vent6Auto | DIGITAL | IOD_STR | STR:.DI_Vent6Auto
STRDI_Vent6kontON | DIGITAL | IOD_STR | STR:.DI_Vent6kontON
STRDI_Vlaz1ERR | DIGITAL | IOD_STR | STR:.DI_Vlaz1ERR
STRDI_Vlaz1ON | DIGITAL | IOD_STR | STR:.DI_Vlaz1ON
STRDI_Vlaz2ERR | DIGITAL | IOD_STR | STR:.DI_Vlaz2ERR
STRDI_Vlaz2ON | DIGITAL | IOD_STR | STR:.DI_Vlaz2ON
STRDIN_230VAC_OK | DIGITAL | IOD_STR | STR:.DIN_230VAC_OK
STRDIN_24VAC_OK | DIGITAL | IOD_STR | STR:.DIN_24VAC_OK
STRDIN_24VDC_OK | DIGITAL | IOD_STR | STR:.DIN_24VDC_OK
STRDIN_CrpHM1ERR | DIGITAL | IOD_STR | STR:.DIN_CrpHM1ERR
STRDIN_CrpHM2ERR | DIGITAL | IOD_STR | STR:.DIN_CrpHM2ERR
STRDIN_CrpHM3ERR | DIGITAL | IOD_STR | STR:.DIN_CrpHM3ERR
STRDIN_CrpHM4ERR | DIGITAL | IOD_STR | STR:.DIN_CrpHM4ERR
STRDIN_HladStERR | DIGITAL | IOD_STR | STR:.DIN_HladStERR
STRDIN_Klima1ERR | DIGITAL | IOD_STR | STR:.DIN_Klima1ERR
STRDIN_Klima1filterZAM | DIGITAL | IOD_STR | STR:.DIN_Klima1filterZAM
STRDIN_Klima1zascStON | DIGITAL | IOD_STR | STR:.DIN_Klima1zascStON
STRDIN_Klima2ERR | DIGITAL | IOD_STR | STR:.DIN_Klima2ERR
STRDIN_Klima2filterZAM | DIGITAL | IOD_STR | STR:.DIN_Klima2filterZAM
STRDIN_Klima2zascStON | DIGITAL | IOD_STR | STR:.DIN_Klima2zascStON
STRDIN_Komp1ERR | DIGITAL | IOD_STR | STR:.DIN_Komp1ERR
STRDIN_Komp1ON | DIGITAL | IOD_STR | STR:.DIN_Komp1ON
STRDIN_Komp2ERR | DIGITAL | IOD_STR | STR:.DIN_Komp2ERR
STRDIN_Komp2ON | DIGITAL | IOD_STR | STR:.DIN_Komp2ON
STRDIN_Kond1zascStON | DIGITAL | IOD_STR | STR:.DIN_Kond1zascStON
STRDIN_Kond2zascStON | DIGITAL | IOD_STR | STR:.DIN_Kond2zascStON
STRDIN_Kond3zascStON | DIGITAL | IOD_STR | STR:.DIN_Kond3zascStON
STRDIN_Vlaz1ERR | DIGITAL | IOD_STR | STR:.DIN_Vlaz1ERR
STRDIN_Vlaz2ERR | DIGITAL | IOD_STR | STR:.DIN_Vlaz2ERR
STRDO_BojlerTE1Vklop | DIGITAL | IOD_STR | STR:.DO_BojlerTE1Vklop
STRDO_CrpHM1Vklop | DIGITAL | IOD_STR | STR:.DO_CrpHM1Vklop
STRDO_CrpHM2Vklop | DIGITAL | IOD_STR | STR:.DO_CrpHM2Vklop
STRDO_CrpHM3Vklop | DIGITAL | IOD_STR | STR:.DO_CrpHM3Vklop
STRDO_CrpHM4Vklop | DIGITAL | IOD_STR | STR:.DO_CrpHM4Vklop
STRDO_CrpMN1Vklop | DIGITAL | IOD_STR | STR:.DO_CrpMN1Vklop
STRDO_CrpTM11Vklop | DIGITAL | IOD_STR | STR:.DO_CrpTM11Vklop
STRDO_GrundfosVklopL | DIGITAL | IOD_STR | STR:.DO_GrundfosVklopL
STRDO_GrundfosVklopN | DIGITAL | IOD_STR | STR:.DO_GrundfosVklopN
STRDO_HladStrIzklop | DIGITAL | IOD_STR | STR:.DO_HladStrIzklop
STRDO_KE1Vklop | DIGITAL | IOD_STR | STR:.DO_KE1Vklop
STRDO_KE2Vklop | DIGITAL | IOD_STR | STR:.DO_KE2Vklop
STRDO_KE3Vklop | DIGITAL | IOD_STR | STR:.DO_KE3Vklop
STRDO_Klima1Vklop | DIGITAL | IOD_STR | STR:.DO_Klima1Vklop
STRDO_Klima2Vklop | DIGITAL | IOD_STR | STR:.DO_Klima2Vklop
STRDO_Lop1PL1Vklop | DIGITAL | IOD_STR | STR:.DO_Lop1PL1Vklop
STRDO_Lop1PL2Vklop | DIGITAL | IOD_STR | STR:.DO_Lop1PL2Vklop
STRDO_Lop1PL3Vklop | DIGITAL | IOD_STR | STR:.DO_Lop1PL3Vklop
STRDO_Lop3Y1Vklop | DIGITAL | IOD_STR | STR:.DO_Lop3Y1Vklop
STRDO_Lop4Y1Vklop | DIGITAL | IOD_STR | STR:.DO_Lop4Y1Vklop
STRDO_RazE11_10Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_10Vklop
STRDO_RazE11_11Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_11Vklop
STRDO_RazE11_1Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_1Vklop
STRDO_RazE11_2Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_2Vklop
STRDO_RazE11_3Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_3Vklop
STRDO_RazE11_4Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_4Vklop
STRDO_RazE11_5Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_5Vklop
STRDO_RazE11_6Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_6Vklop
STRDO_RazE11_7Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_7Vklop
STRDO_RazE11_8Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_8Vklop
STRDO_RazE11_9Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_9Vklop
STRDO_RazE12_12Vklop | DIGITAL | IOD_STR | STR:.DO_RazE12_12Vklop
STRDO_RazE12_13Vklop | DIGITAL | IOD_STR | STR:.DO_RazE12_13Vklop
STRDO_RazE12_14Vklop | DIGITAL | IOD_STR | STR:.DO_RazE12_14Vklop
STRDO_RazE12_15Vklop | DIGITAL | IOD_STR | STR:.DO_RazE12_15Vklop
STRDO_RazE13_16Vklop | DIGITAL | IOD_STR | STR:.DO_RazE13_16Vklop
STRDO_RazE13_17Vklop | DIGITAL | IOD_STR | STR:.DO_RazE13_17Vklop
STRDO_RazE13_18Vklop | DIGITAL | IOD_STR | STR:.DO_RazE13_18Vklop
STRDO_RazE13_19Vklop | DIGITAL | IOD_STR | STR:.DO_RazE13_19Vklop
STRDO_RazE16_20Vklop | DIGITAL | IOD_STR | STR:.DO_RazE16_20Vklop
STRDO_RazE16_21Vklop | DIGITAL | IOD_STR | STR:.DO_RazE16_21Vklop
STRDO_RazE16_22Vklop | DIGITAL | IOD_STR | STR:.DO_RazE16_22Vklop
STRDO_RazE16_23Vklop | DIGITAL | IOD_STR | STR:.DO_RazE16_23Vklop
STRDO_RazE16_24Vklop | DIGITAL | IOD_STR | STR:.DO_RazE16_24Vklop
STRDO_Vent1Vklop | DIGITAL | IOD_STR | STR:.DO_Vent1Vklop
STRDO_Vent2Vklop | DIGITAL | IOD_STR | STR:.DO_Vent2Vklop
STRDO_Vent3Vklop | DIGITAL | IOD_STR | STR:.DO_Vent3Vklop
STRDO_Vent4Vklop | DIGITAL | IOD_STR | STR:.DO_Vent4Vklop
STRDO_Vent5Vklop | DIGITAL | IOD_STR | STR:.DO_Vent5Vklop
STRDO_Vent6Vklop | DIGITAL | IOD_STR | STR:.DO_Vent6Vklop
STRErrComCirc1 | DIGITAL | IOD_STR | STR:.ErrComCirc[1]
STRErrComCirc2 | DIGITAL | IOD_STR | STR:.ErrComCirc[2]
STRErrComDanfossHM1 | DIGITAL | IOD_STR | STR:.ErrComDanfossHM[1]
STRErrComDanfossHM2 | DIGITAL | IOD_STR | STR:.ErrComDanfossHM[2]
STRErrComDanfossHM3 | DIGITAL | IOD_STR | STR:.ErrComDanfossHM[3]
STRErrComDanfossHM4 | DIGITAL | IOD_STR | STR:.ErrComDanfossHM[4]
STRErrComGrundfos0 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[0]
STRErrComGrundfos10 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[10]
STRErrComGrundfos11 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[11]
STRErrComGrundfos12 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[12]
STRErrComGrundfos13 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[13]
STRErrComGrundfos14 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[14]
STRErrComGrundfos1 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[1]
STRErrComGrundfos2 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[2]
STRErrComGrundfos3 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[3]
STRErrComGrundfos4 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[4]
STRErrComGrundfos5 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[5]
STRErrComGrundfos6 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[6]
STRErrComGrundfos7 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[7]
STRErrComGrundfos8 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[8]
STRErrComGrundfos9 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[9]
STRErrComHladStroj | DIGITAL | IOD_STR | STR:.ErrComHladStroj
STRErrComKlima1 | DIGITAL | IOD_STR | STR:.ErrComKlima[1]
STRErrComKlima2 | DIGITAL | IOD_STR | STR:.ErrComKlima[2]
STRErrCommScada | DIGITAL | IOD_STR | STR:.ErrCommScada
STRErrCommXC100 | DIGITAL | IOD_STR | STR:.ErrCommXC100
STRErrComPanelPLC | DIGITAL | IOD_STR | STR:.ErrComPanelPLC
STRErrComPort2 | DIGITAL | IOD_STR | STR:.ErrComPort2
STRErrComPort3 | DIGITAL | IOD_STR | STR:.ErrComPort3
STRErrComPort4 | DIGITAL | IOD_STR | STR:.ErrComPort4
STRErrComToplPost | DIGITAL | IOD_STR | STR:.ErrComToplPost
STRExp1TlakAlarm | DIGITAL | IOD_STR | STR:.Exp1TlakAlarm
STRExp1TlakMin | REAL | IOD_STR | STR:.Exp1TlakMin
STRExp2TlakAlarm | DIGITAL | IOD_STR | STR:.Exp2TlakAlarm
STRExp2TlakMin | REAL | IOD_STR | STR:.Exp2TlakMin
STRHladilniStrojOnOff | DIGITAL | IOD_STR | STR:.HladilniStrojOnOff
STRHladStrojFazeAlarm | DIGITAL | IOD_STR | STR:.HladStroj.FazeAlarm
STRHladStrojKompresorOljeAlarm | DIGITAL | IOD_STR | STR:.HladStroj.KompresorOljeAlarm
STRHladStrojKompresorOljeAlarmB | INT | IOD_STR | STR:.HladStroj.KompresorOljeAlarmB | BYTE
STRHladStrojLANcarelAlarm | DIGITAL | IOD_STR | STR:.HladStroj.LANcarelAlarm
STRHladStrojNapaka | DIGITAL | IOD_STR | STR:.HladStroj.Napaka
STRHladStrojNizekPritiskAlarm | DIGITAL | IOD_STR | STR:.HladStroj.NizekPritiskAlarm
STRHladStrojNizekPritiskAlarmB | INT | IOD_STR | STR:.HladStroj.NizekPritiskAlarmB | BYTE
STRHladStrojObratovalneUre | REAL | IOD_STR | STR:.HladStroj.ObratovalneUre
STRHladStrojObratovalneUreOpozorilo | DIGITAL | IOD_STR | STR:.HladStroj.ObratovalneUreOpozorilo
STRHladStrojObratovalneUreOpozoriloB | INT | IOD_STR | STR:.HladStroj.ObratovalneUreOpozoriloB | BYTE
STRHladStrojOffByAlarms | DIGITAL | IOD_STR | STR:.HladStroj.OffByAlarms
STRHladStrojPretokAlarm | DIGITAL | IOD_STR | STR:.HladStroj.PretokAlarm
STRHladStrojPritiskSonda1 | REAL | IOD_STR | STR:.HladStroj.PritiskSonda1
STRHladStrojPritiskSonda2 | REAL | IOD_STR | STR:.HladStroj.PritiskSonda2
STRHladStrojPritiskSonda3 | REAL | IOD_STR | STR:.HladStroj.PritiskSonda3
STRHladStrojPritiskSonda4 | REAL | IOD_STR | STR:.HladStroj.PritiskSonda4
STRHladStrojRemoteOn | DIGITAL | IOD_STR | STR:.HladStroj.RemoteOn
STRHladStrojSenzorAlarm | DIGITAL | IOD_STR | STR:.HladStroj.SenzorAlarm
STRHladStrojSummerOperation | DIGITAL | IOD_STR | STR:.HladStroj.SummerOperation
STRHladStrojTemperaturaAlarm | DIGITAL | IOD_STR | STR:.HladStroj.TemperaturaAlarm
STRHladStrojTemperaturaAlarmB | INT | IOD_STR | STR:.HladStroj.TemperaturaAlarmB | BYTE
STRHladStrojTempH2OvhodIzparilnika | REAL | IOD_STR | STR:.HladStroj.TempH2OvhodIzparilnika
STRHladStrojTempIzhodnaSonda1 | REAL | IOD_STR | STR:.HladStroj.TempIzhodnaSonda1
STRHladStrojTempIzhodnaSonda3 | REAL | IOD_STR | STR:.HladStroj.TempIzhodnaSonda3
STRHladStrojTempSetPoint | REAL | IOD_STR | STR:.HladStroj.TempSetPoint
STRHladStrojUnitOn | DIGITAL | IOD_STR | STR:.HladStroj.UnitOn
STRHladStrojUnitStatus | INT | IOD_STR | STR:.HladStroj.UnitStatus
STRHladStrojUraAlarm | DIGITAL | IOD_STR | STR:.HladStroj.UraAlarm
STRHladStrojVisokPritiskAlarm | DIGITAL | IOD_STR | STR:.HladStroj.VisokPritiskAlarm
STRHladStrojVisokPritiskAlarmB | INT | IOD_STR | STR:.HladStroj.VisokPritiskAlarmB | BYTE
STRHladStrojVisokPritiskOpozorilo | DIGITAL | IOD_STR | STR:.HladStroj.VisokPritiskOpozorilo
STRHladStrojVisokPritiskOpozoriloB | INT | IOD_STR | STR:.HladStroj.VisokPritiskOpozoriloB | BYTE
STRHladStrojZmrzalniAlarm | DIGITAL | IOD_STR | STR:.HladStroj.ZmrzalniAlarm
STRHladStrojZmrzalniAlarmB | INT | IOD_STR | STR:.HladStroj.ZmrzalniAlarmB | BYTE
STRHladStrojErrors10 | DIGITAL | IOD_STR | STR:.HladStrojErrors[10]
STRHladStrojErrors11 | DIGITAL | IOD_STR | STR:.HladStrojErrors[11]
STRHladStrojErrors12 | DIGITAL | IOD_STR | STR:.HladStrojErrors[12]
STRHladStrojErrors13 | DIGITAL | IOD_STR | STR:.HladStrojErrors[13]
STRHladStrojErrors14 | DIGITAL | IOD_STR | STR:.HladStrojErrors[14]
STRHladStrojErrors15 | DIGITAL | IOD_STR | STR:.HladStrojErrors[15]
STRHladStrojErrors16 | DIGITAL | IOD_STR | STR:.HladStrojErrors[16]
STRHladStrojErrors1 | DIGITAL | IOD_STR | STR:.HladStrojErrors[1]
STRHladStrojErrors2 | DIGITAL | IOD_STR | STR:.HladStrojErrors[2]
STRHladStrojErrors3 | DIGITAL | IOD_STR | STR:.HladStrojErrors[3]
STRHladStrojErrors4 | DIGITAL | IOD_STR | STR:.HladStrojErrors[4]
STRHladStrojErrors5 | DIGITAL | IOD_STR | STR:.HladStrojErrors[5]
STRHladStrojErrors6 | DIGITAL | IOD_STR | STR:.HladStrojErrors[6]
STRHladStrojErrors7 | DIGITAL | IOD_STR | STR:.HladStrojErrors[7]
STRHladStrojErrors8 | DIGITAL | IOD_STR | STR:.HladStrojErrors[8]
STRHladStrojErrors9 | DIGITAL | IOD_STR | STR:.HladStrojErrors[9]
STRKlima1errors10 | DIGITAL | IOD_STR | STR:.Klima1errors[10]
STRKlima1errors11 | DIGITAL | IOD_STR | STR:.Klima1errors[11]
STRKlima1errors12 | DIGITAL | IOD_STR | STR:.Klima1errors[12]
STRKlima1errors1 | DIGITAL | IOD_STR | STR:.Klima1errors[1]
STRKlima1errors2 | DIGITAL | IOD_STR | STR:.Klima1errors[2]
STRKlima1errors3 | DIGITAL | IOD_STR | STR:.Klima1errors[3]
STRKlima1errors4 | DIGITAL | IOD_STR | STR:.Klima1errors[4]
STRKlima1errors5 | DIGITAL | IOD_STR | STR:.Klima1errors[5]
STRKlima1errors6 | DIGITAL | IOD_STR | STR:.Klima1errors[6]
STRKlima1errors7 | DIGITAL | IOD_STR | STR:.Klima1errors[7]
STRKlima1errors8 | DIGITAL | IOD_STR | STR:.Klima1errors[8]
STRKlima1errors9 | DIGITAL | IOD_STR | STR:.Klima1errors[9]
STRKlima2errors10 | DIGITAL | IOD_STR | STR:.Klima2errors[10]
STRKlima2errors11 | DIGITAL | IOD_STR | STR:.Klima2errors[11]
STRKlima2errors12 | DIGITAL | IOD_STR | STR:.Klima2errors[12]
STRKlima2errors1 | DIGITAL | IOD_STR | STR:.Klima2errors[1]
STRKlima2errors2 | DIGITAL | IOD_STR | STR:.Klima2errors[2]
STRKlima2errors3 | DIGITAL | IOD_STR | STR:.Klima2errors[3]
STRKlima2errors4 | DIGITAL | IOD_STR | STR:.Klima2errors[4]
STRKlima2errors5 | DIGITAL | IOD_STR | STR:.Klima2errors[5]
STRKlima2errors6 | DIGITAL | IOD_STR | STR:.Klima2errors[6]
STRKlima2errors7 | DIGITAL | IOD_STR | STR:.Klima2errors[7]
STRKlima2errors8 | DIGITAL | IOD_STR | STR:.Klima2errors[8]
STRKlima2errors9 | DIGITAL | IOD_STR | STR:.Klima2errors[9]
STRKlima1CrpalkaGrelnika | DIGITAL | IOD_STR | STR:.Klima[1].CrpalkaGrelnika
STRKlima1CrpalkaStatus | INT | IOD_STR | STR:.Klima[1].CrpalkaStatus | BYTE
STRKlima1DelovanjeVentH1 | DIGITAL | IOD_STR | STR:.Klima[1].DelovanjeVentH1
STRKlima1DelovanjeVentH2 | DIGITAL | IOD_STR | STR:.Klima[1].DelovanjeVentH2
STRKlima1Deluje | DIGITAL | IOD_STR | STR:.Klima[1].Deluje
STRKlima1FilterError | DIGITAL | IOD_STR | STR:.Klima[1].FilterError
STRKlima1HitrostVentilatorjev | REAL | IOD_STR | STR:.Klima[1].HitrostVentilatorjev
STRKlima1HitrostVentStatus | INT | IOD_STR | STR:.Klima[1].HitrostVentStatus | BYTE
STRKlima1IzhodniVentStatus | INT | IOD_STR | STR:.Klima[1].IzhodniVentStatus | BYTE
STRKlima1Napaka | DIGITAL | IOD_STR | STR:.Klima[1].Napaka
STRKlima1NapakaPriPretokuZraka | DIGITAL | IOD_STR | STR:.Klima[1].NapakaPriPretokuZraka
STRKlima1NastTempProstora | REAL | IOD_STR | STR:.Klima[1].NastTempProstora
STRKlima1ObratovalneUre | REAL | IOD_STR | STR:.Klima[1].ObratovalneUre
STRKlima1OkvaraRototerma | DIGITAL | IOD_STR | STR:.Klima[1].OkvaraRototerma
STRKlima1OkvaraVlazilne | DIGITAL | IOD_STR | STR:.Klima[1].OkvaraVlazilne
STRKlima1PozarError | DIGITAL | IOD_STR | STR:.Klima[1].PozarError
STRKlima1PozarniAlarm | DIGITAL | IOD_STR | STR:.Klima[1].PozarniAlarm
STRKlima1PreobremenitevMotCrpGr | DIGITAL | IOD_STR | STR:.Klima[1].PreobremenitevMotCrpGr
STRKlima1PreobremenitevMotVent | DIGITAL | IOD_STR | STR:.Klima[1].PreobremenitevMotVent
STRKlima1ProtizmrzAktivna | DIGITAL | IOD_STR | STR:.Klima[1].ProtizmrzAktivna
STRKlima1ProtizmrzZasc | REAL | IOD_STR | STR:.Klima[1].ProtizmrzZasc
STRKlima1RezimDelovanja | REAL | IOD_STR | STR:.Klima[1].RezimDelovanja
STRKlima1SkupniAlarmA | DIGITAL | IOD_STR | STR:.Klima[1].SkupniAlarmA
STRKlima1SkupniAlarmB | DIGITAL | IOD_STR | STR:.Klima[1].SkupniAlarmB
STRKlima1TemperaturaDovoda | REAL | IOD_STR | STR:.Klima[1].TemperaturaDovoda
STRKlima1TemperaturaProstora | REAL | IOD_STR | STR:.Klima[1].TemperaturaProstora
STRKlima1TempPredRekN2 | REAL | IOD_STR | STR:.Klima[1].TempPredRekN2
STRKlima1TempZaRekN2 | REAL | IOD_STR | STR:.Klima[1].TempZaRekN2
STRKlima1TlakDovKanal | REAL | IOD_STR | STR:.Klima[1].TlakDovKanal
STRKlima1TlakOdvodKanal | REAL | IOD_STR | STR:.Klima[1].TlakOdvodKanal
STRKlima1VklopRegulacije | DIGITAL | IOD_STR | STR:.Klima[1].VklopRegulacije
STRKlima1VlagaDovoda | REAL | IOD_STR | STR:.Klima[1].VlagaDovoda
STRKlima1VlagaVprostor | REAL | IOD_STR | STR:.Klima[1].VlagaVprostor
STRKlima1ZamasenFilter | DIGITAL | IOD_STR | STR:.Klima[1].ZamasenFilter
STRKlima1ZunanjaTemp | REAL | IOD_STR | STR:.Klima[1].ZunanjaTemp
STRKlima2CrpalkaGrelnika | DIGITAL | IOD_STR | STR:.Klima[2].CrpalkaGrelnika
STRKlima2CrpalkaStatus | INT | IOD_STR | STR:.Klima[2].CrpalkaStatus | BYTE
STRKlima2DelovanjeVentH1 | DIGITAL | IOD_STR | STR:.Klima[2].DelovanjeVentH1
STRKlima2DelovanjeVentH2 | DIGITAL | IOD_STR | STR:.Klima[2].DelovanjeVentH2
STRKlima2Deluje | DIGITAL | IOD_STR | STR:.Klima[2].Deluje
STRKlima2FilterError | DIGITAL | IOD_STR | STR:.Klima[2].FilterError
STRKlima2HitrostVentilatorjev | REAL | IOD_STR | STR:.Klima[2].HitrostVentilatorjev
STRKlima2HitrostVentStatus | INT | IOD_STR | STR:.Klima[2].HitrostVentStatus | BYTE
STRKlima2IzhodniVentStatus | INT | IOD_STR | STR:.Klima[2].IzhodniVentStatus | BYTE
STRKlima2Napaka | DIGITAL | IOD_STR | STR:.Klima[2].Napaka
STRKlima2NapakaPriPretokuZraka | DIGITAL | IOD_STR | STR:.Klima[2].NapakaPriPretokuZraka
STRKlima2NastTempProstora | REAL | IOD_STR | STR:.Klima[2].NastTempProstora
STRKlima2ObratovalneUre | REAL | IOD_STR | STR:.Klima[2].ObratovalneUre
STRKlima2OkvaraRototerma | DIGITAL | IOD_STR | STR:.Klima[2].OkvaraRototerma
STRKlima2OkvaraVlazilne | DIGITAL | IOD_STR | STR:.Klima[2].OkvaraVlazilne
STRKlima2PozarError | DIGITAL | IOD_STR | STR:.Klima[2].PozarError
STRKlima2PozarniAlarm | DIGITAL | IOD_STR | STR:.Klima[2].PozarniAlarm
STRKlima2PreobremenitevMotCrpGr | DIGITAL | IOD_STR | STR:.Klima[2].PreobremenitevMotCrpGr
STRKlima2PreobremenitevMotVent | DIGITAL | IOD_STR | STR:.Klima[2].PreobremenitevMotVent
STRKlima2ProtizmrzAktivna | DIGITAL | IOD_STR | STR:.Klima[2].ProtizmrzAktivna
STRKlima2ProtizmrzZasc | REAL | IOD_STR | STR:.Klima[2].ProtizmrzZasc
STRKlima2RezimDelovanja | REAL | IOD_STR | STR:.Klima[2].RezimDelovanja
STRKlima2SkupniAlarmA | DIGITAL | IOD_STR | STR:.Klima[2].SkupniAlarmA
STRKlima2SkupniAlarmB | DIGITAL | IOD_STR | STR:.Klima[2].SkupniAlarmB
STRKlima2TemperaturaDovoda | REAL | IOD_STR | STR:.Klima[2].TemperaturaDovoda
STRKlima2TemperaturaProstora | REAL | IOD_STR | STR:.Klima[2].TemperaturaProstora
STRKlima2TempPredRekN2 | REAL | IOD_STR | STR:.Klima[2].TempPredRekN2
STRKlima2TempZaRekN2 | REAL | IOD_STR | STR:.Klima[2].TempZaRekN2
STRKlima2TlakDovKanal | REAL | IOD_STR | STR:.Klima[2].TlakDovKanal
STRKlima2TlakOdvodKanal | REAL | IOD_STR | STR:.Klima[2].TlakOdvodKanal
STRKlima2VklopRegulacije | DIGITAL | IOD_STR | STR:.Klima[2].VklopRegulacije
STRKlima2VlagaDovoda | REAL | IOD_STR | STR:.Klima[2].VlagaDovoda
STRKlima2VlagaVprostor | REAL | IOD_STR | STR:.Klima[2].VlagaVprostor
STRKlima2ZamasenFilter | DIGITAL | IOD_STR | STR:.Klima[2].ZamasenFilter
STRKlima2ZunanjaTemp | REAL | IOD_STR | STR:.Klima[2].ZunanjaTemp
STRKondEnotaOnOff1 | DIGITAL | IOD_STR | STR:.KondEnotaOnOff[1]
STRKondEnotaOnOff2 | DIGITAL | IOD_STR | STR:.KondEnotaOnOff[2]
STRKondEnotaOnOff3 | DIGITAL | IOD_STR | STR:.KondEnotaOnOff[3]
STRKontRezervaOnOff1 | DIGITAL | IOD_STR | STR:.KontRezervaOnOff[1]
STRKontRezervaOnOff2 | DIGITAL | IOD_STR | STR:.KontRezervaOnOff[2]
STRKontRezervaOnOff3 | DIGITAL | IOD_STR | STR:.KontRezervaOnOff[3]
STRNapakaSenzorAI10 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[10]
STRNapakaSenzorAI11 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[11]
STRNapakaSenzorAI12 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[12]
STRNapakaSenzorAI13 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[13]
STRNapakaSenzorAI14 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[14]
STRNapakaSenzorAI15 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[15]
STRNapakaSenzorAI16 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[16]
STRNapakaSenzorAI17 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[17]
STRNapakaSenzorAI18 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[18]
STRNapakaSenzorAI19 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[19]
STRNapakaSenzorAI1 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[1]
STRNapakaSenzorAI20 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[20]
STRNapakaSenzorAI21 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[21]
STRNapakaSenzorAI22 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[22]
STRNapakaSenzorAI23 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[23]
STRNapakaSenzorAI24 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[24]
STRNapakaSenzorAI25 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[25]
STRNapakaSenzorAI26 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[26]
STRNapakaSenzorAI27 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[27]
STRNapakaSenzorAI28 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[28]
STRNapakaSenzorAI29 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[29]
STRNapakaSenzorAI2 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[2]
STRNapakaSenzorAI30 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[30]
STRNapakaSenzorAI31 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[31]
STRNapakaSenzorAI32 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[32]
STRNapakaSenzorAI33 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[33]
STRNapakaSenzorAI34 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[34]
STRNapakaSenzorAI35 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[35]
STRNapakaSenzorAI36 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[36]
STRNapakaSenzorAI37 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[37]
STRNapakaSenzorAI38 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[38]
STRNapakaSenzorAI39 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[39]
STRNapakaSenzorAI3 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[3]
STRNapakaSenzorAI40 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[40]
STRNapakaSenzorAI4 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[4]
STRNapakaSenzorAI5 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[5]
STRNapakaSenzorAI6 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[6]
STRNapakaSenzorAI7 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[7]
STRNapakaSenzorAI8 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[8]
STRNapakaSenzorAI9 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[9]
STRNapakaSenzorHIA1 | DIGITAL | IOD_STR | STR:.NapakaSenzorHIA[1]
STRNapakaSenzorHIA2 | DIGITAL | IOD_STR | STR:.NapakaSenzorHIA[2]
STRNapakaSenzorHIA3 | DIGITAL | IOD_STR | STR:.NapakaSenzorHIA[3]
STRNapakaSenzorHIA4 | DIGITAL | IOD_STR | STR:.NapakaSenzorHIA[4]
STRNapakaSenzorTIA1 | DIGITAL | IOD_STR | STR:.NapakaSenzorTIA[1]
STRNapakaSenzorTIA2 | DIGITAL | IOD_STR | STR:.NapakaSenzorTIA[2]
STRNapakaSenzorTIA3 | DIGITAL | IOD_STR | STR:.NapakaSenzorTIA[3]
STRNapakaSenzorTIA4 | DIGITAL | IOD_STR | STR:.NapakaSenzorTIA[4]
STRPozarnaLoputaOnOffError1 | DIGITAL | IOD_STR | STR:.PozarnaLoputaOnOffError[1]
STRPozarnaLoputaOnOffError2 | DIGITAL | IOD_STR | STR:.PozarnaLoputaOnOffError[2]
STRPozarnaLoputaOnOffError3 | DIGITAL | IOD_STR | STR:.PozarnaLoputaOnOffError[3]
STRPozarnaLoputaOnOffError4 | DIGITAL | IOD_STR | STR:.PozarnaLoputaOnOffError[4]
STRPozarnaLoputaOnOffError5 | DIGITAL | IOD_STR | STR:.PozarnaLoputaOnOffError[5]
STRPozarnaLoputaStatus1 | INT | IOD_STR | STR:.PozarnaLoputaStatus[1] | BYTE
STRPozarnaLoputaStatus2 | INT | IOD_STR | STR:.PozarnaLoputaStatus[2] | BYTE
STRPozarnaLoputaStatus3 | INT | IOD_STR | STR:.PozarnaLoputaStatus[3] | BYTE
STRPozarnaLoputaStatus4 | INT | IOD_STR | STR:.PozarnaLoputaStatus[4] | BYTE
STRPozarnaLoputaStatus5 | INT | IOD_STR | STR:.PozarnaLoputaStatus[5] | BYTE
STRPozarnaLoputOnOff1 | DIGITAL | IOD_STR | STR:.PozarnaLoputOnOff[1]
STRPozarnaLoputOnOff2 | DIGITAL | IOD_STR | STR:.PozarnaLoputOnOff[2]
STRPozarnaLoputOnOff3 | DIGITAL | IOD_STR | STR:.PozarnaLoputOnOff[3]
STRPozarnaLoputOnOff4 | DIGITAL | IOD_STR | STR:.PozarnaLoputOnOff[4]
STRPozarnaLoputOnOff5 | DIGITAL | IOD_STR | STR:.PozarnaLoputOnOff[5]
STRPozarniAlarm | DIGITAL | IOD_STR | STR:.PozarniAlarm
STRPrenosUrnika10 | DIGITAL | IOD_STR | STR:.PrenosUrnika[10]
STRPrenosUrnika11 | DIGITAL | IOD_STR | STR:.PrenosUrnika[11]
STRPrenosUrnika12 | DIGITAL | IOD_STR | STR:.PrenosUrnika[12]
STRPrenosUrnika13 | DIGITAL | IOD_STR | STR:.PrenosUrnika[13]
STRPrenosUrnika14 | DIGITAL | IOD_STR | STR:.PrenosUrnika[14]
STRPrenosUrnika15 | DIGITAL | IOD_STR | STR:.PrenosUrnika[15]
STRPrenosUrnika16 | DIGITAL | IOD_STR | STR:.PrenosUrnika[16]
STRPrenosUrnika17 | DIGITAL | IOD_STR | STR:.PrenosUrnika[17]
STRPrenosUrnika18 | DIGITAL | IOD_STR | STR:.PrenosUrnika[18]
STRPrenosUrnika19 | DIGITAL | IOD_STR | STR:.PrenosUrnika[19]
STRPrenosUrnika1 | DIGITAL | IOD_STR | STR:.PrenosUrnika[1]
STRPrenosUrnika20 | DIGITAL | IOD_STR | STR:.PrenosUrnika[20]
STRPrenosUrnika21 | DIGITAL | IOD_STR | STR:.PrenosUrnika[21]
STRPrenosUrnika22 | DIGITAL | IOD_STR | STR:.PrenosUrnika[22]
STRPrenosUrnika23 | DIGITAL | IOD_STR | STR:.PrenosUrnika[23]
STRPrenosUrnika24 | DIGITAL | IOD_STR | STR:.PrenosUrnika[24]
STRPrenosUrnika25 | DIGITAL | IOD_STR | STR:.PrenosUrnika[25]
STRPrenosUrnika2 | DIGITAL | IOD_STR | STR:.PrenosUrnika[2]
STRPrenosUrnika3 | DIGITAL | IOD_STR | STR:.PrenosUrnika[3]
STRPrenosUrnika4 | DIGITAL | IOD_STR | STR:.PrenosUrnika[4]
STRPrenosUrnika5 | DIGITAL | IOD_STR | STR:.PrenosUrnika[5]
STRPrenosUrnika6 | DIGITAL | IOD_STR | STR:.PrenosUrnika[6]
STRPrenosUrnika7 | DIGITAL | IOD_STR | STR:.PrenosUrnika[7]
STRPrenosUrnika8 | DIGITAL | IOD_STR | STR:.PrenosUrnika[8]
STRPrenosUrnika9 | DIGITAL | IOD_STR | STR:.PrenosUrnika[9]
STRRazsvetljavaOnOff10 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[10]
STRRazsvetljavaOnOff11 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[11]
STRRazsvetljavaOnOff12 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[12]
STRRazsvetljavaOnOff13 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[13]
STRRazsvetljavaOnOff14 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[14]
STRRazsvetljavaOnOff15 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[15]
STRRazsvetljavaOnOff16 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[16]
STRRazsvetljavaOnOff17 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[17]
STRRazsvetljavaOnOff18 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[18]
STRRazsvetljavaOnOff19 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[19]
STRRazsvetljavaOnOff1 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[1]
STRRazsvetljavaOnOff20 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[20]
STRRazsvetljavaOnOff21 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[21]
STRRazsvetljavaOnOff22 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[22]
STRRazsvetljavaOnOff23 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[23]
STRRazsvetljavaOnOff24 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[24]
STRRazsvetljavaOnOff25 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[25]
STRRazsvetljavaOnOff2 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[2]
STRRazsvetljavaOnOff3 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[3]
STRRazsvetljavaOnOff4 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[4]
STRRazsvetljavaOnOff5 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[5]
STRRazsvetljavaOnOff6 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[6]
STRRazsvetljavaOnOff7 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[7]
STRRazsvetljavaOnOff8 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[8]
STRRazsvetljavaOnOff9 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[9]
STRRazsvetljavaRocno | DIGITAL | IOD_STR | STR:.RazsvetljavaRocno
STRrVersion | REAL | IOD_STR | STR:.rVersion
STRSenzorTempTIA1 | REAL | IOD_STR | STR:.SenzorTempTIA[1]
STRSenzorTempTIA2 | REAL | IOD_STR | STR:.SenzorTempTIA[2]
STRSenzorTempTIA3 | REAL | IOD_STR | STR:.SenzorTempTIA[3]
STRSenzorTempTIA4 | REAL | IOD_STR | STR:.SenzorTempTIA[4]
STRSenzorVlagaHIA1 | REAL | IOD_STR | STR:.SenzorVlagaHIA[1]
STRSenzorVlagaHIA2 | REAL | IOD_STR | STR:.SenzorVlagaHIA[2]
STRSenzorVlagaHIA3 | REAL | IOD_STR | STR:.SenzorVlagaHIA[3]
STRSenzorVlagaHIA4 | REAL | IOD_STR | STR:.SenzorVlagaHIA[4]
STRSetDateTime | DIGITAL | IOD_STR | STR:.SetDateTime
STRSetDateTimeDemand | DIGITAL | IOD_STR | STR:.SetDateTimeDemand
STRSetDateTimeError | DIGITAL | IOD_STR | STR:.SetDateTimeError
STRSetDateTimeFinished | DIGITAL | IOD_STR | STR:.SetDateTimeFinished
STRSetRemoteOnOff1 | DIGITAL | IOD_STR | STR:.SetRemoteOnOff[1]
STRSetRemoteOnOff2 | DIGITAL | IOD_STR | STR:.SetRemoteOnOff[2]
STRSlabaBaterijaPLC_A1 | DIGITAL | IOD_STR | STR:.SlabaBaterijaPLC_A1
STRSlabaBaterijaPLC_A100 | DIGITAL | IOD_STR | STR:.SlabaBaterijaPLC_A100
STRSO_BojlerTE1Vklop | DIGITAL | IOD_STR | STR:.SO_BojlerTE1Vklop
STRSO_CrpHM1Vklop | DIGITAL | IOD_STR | STR:.SO_CrpHM1Vklop
STRSO_CrpHM2Vklop | DIGITAL | IOD_STR | STR:.SO_CrpHM2Vklop
STRSO_CrpHM3Vklop | DIGITAL | IOD_STR | STR:.SO_CrpHM3Vklop
STRSO_CrpHM4Vklop | DIGITAL | IOD_STR | STR:.SO_CrpHM4Vklop
STRSO_CrpMN1Vklop | DIGITAL | IOD_STR | STR:.SO_CrpMN1Vklop
STRSO_CrpTM11Vklop | DIGITAL | IOD_STR | STR:.SO_CrpTM11Vklop
STRSO_HladStrVklop | DIGITAL | IOD_STR | STR:.SO_HladStrVklop
STRSO_KE1Vklop | DIGITAL | IOD_STR | STR:.SO_KE1Vklop
STRSO_KE2Vklop | DIGITAL | IOD_STR | STR:.SO_KE2Vklop
STRSO_KE3Vklop | DIGITAL | IOD_STR | STR:.SO_KE3Vklop
STRSO_rezerva1_3 | DIGITAL | IOD_STR | STR:.SO_rezerva1_3
STRSO_rezerva1_4 | DIGITAL | IOD_STR | STR:.SO_rezerva1_4
STRSO_rezerva1_5 | DIGITAL | IOD_STR | STR:.SO_rezerva1_5
STRSO_Vent1Vklop | DIGITAL | IOD_STR | STR:.SO_Vent1Vklop
STRSO_Vent2Vklop | DIGITAL | IOD_STR | STR:.SO_Vent2Vklop
STRSO_Vent3Vklop | DIGITAL | IOD_STR | STR:.SO_Vent3Vklop
STRSO_Vent4Vklop | DIGITAL | IOD_STR | STR:.SO_Vent4Vklop
STRSO_Vent5Vklop | DIGITAL | IOD_STR | STR:.SO_Vent5Vklop
STRSO_Vent6Vklop | DIGITAL | IOD_STR | STR:.SO_Vent6Vklop
STRStatusKondenzEnota0 | INT | IOD_STR | STR:.StatusKondenzEnota[0] | BYTE
STRStatusKondenzEnota1 | INT | IOD_STR | STR:.StatusKondenzEnota[1] | BYTE
STRStatusKondenzEnota2 | INT | IOD_STR | STR:.StatusKondenzEnota[2] | BYTE
STRStatusKondenzEnota3 | INT | IOD_STR | STR:.StatusKondenzEnota[3] | BYTE
STRStatusKontaktor10 | INT | IOD_STR | STR:.StatusKontaktor[10] | BYTE
STRStatusKontaktor11 | INT | IOD_STR | STR:.StatusKontaktor[11] | BYTE
STRStatusKontaktor12 | INT | IOD_STR | STR:.StatusKontaktor[12] | BYTE
STRStatusKontaktor13 | INT | IOD_STR | STR:.StatusKontaktor[13] | BYTE
STRStatusKontaktor14 | INT | IOD_STR | STR:.StatusKontaktor[14] | BYTE
STRStatusKontaktor15 | INT | IOD_STR | STR:.StatusKontaktor[15] | BYTE
STRStatusKontaktor16 | INT | IOD_STR | STR:.StatusKontaktor[16] | BYTE
STRStatusKontaktor17 | INT | IOD_STR | STR:.StatusKontaktor[17] | BYTE
STRStatusKontaktor18 | INT | IOD_STR | STR:.StatusKontaktor[18] | BYTE
STRStatusKontaktor19 | INT | IOD_STR | STR:.StatusKontaktor[19] | BYTE
STRStatusKontaktor1 | INT | IOD_STR | STR:.StatusKontaktor[1] | BYTE
STRStatusKontaktor20 | INT | IOD_STR | STR:.StatusKontaktor[20] | BYTE
STRStatusKontaktor21 | INT | IOD_STR | STR:.StatusKontaktor[21] | BYTE
STRStatusKontaktor22 | INT | IOD_STR | STR:.StatusKontaktor[22] | BYTE
STRStatusKontaktor23 | INT | IOD_STR | STR:.StatusKontaktor[23] | BYTE
STRStatusKontaktor24 | INT | IOD_STR | STR:.StatusKontaktor[24] | BYTE
STRStatusKontaktor25 | INT | IOD_STR | STR:.StatusKontaktor[25] | BYTE
STRStatusKontaktor2 | INT | IOD_STR | STR:.StatusKontaktor[2] | BYTE
STRStatusKontaktor3 | INT | IOD_STR | STR:.StatusKontaktor[3] | BYTE
STRStatusKontaktor4 | INT | IOD_STR | STR:.StatusKontaktor[4] | BYTE
STRStatusKontaktor5 | INT | IOD_STR | STR:.StatusKontaktor[5] | BYTE
STRStatusKontaktor6 | INT | IOD_STR | STR:.StatusKontaktor[6] | BYTE
STRStatusKontaktor7 | INT | IOD_STR | STR:.StatusKontaktor[7] | BYTE
STRStatusKontaktor8 | INT | IOD_STR | STR:.StatusKontaktor[8] | BYTE
STRStatusKontaktor9 | INT | IOD_STR | STR:.StatusKontaktor[9] | BYTE
STRStatusPreklopke10 | INT | IOD_STR | STR:.StatusPreklopke[10] | BYTE
STRStatusPreklopke11 | INT | IOD_STR | STR:.StatusPreklopke[11] | BYTE
STRStatusPreklopke12 | INT | IOD_STR | STR:.StatusPreklopke[12] | BYTE
STRStatusPreklopke13 | INT | IOD_STR | STR:.StatusPreklopke[13] | BYTE
STRStatusPreklopke14 | INT | IOD_STR | STR:.StatusPreklopke[14] | BYTE
STRStatusPreklopke15 | INT | IOD_STR | STR:.StatusPreklopke[15] | BYTE
STRStatusPreklopke16 | INT | IOD_STR | STR:.StatusPreklopke[16] | BYTE
STRStatusPreklopke17 | INT | IOD_STR | STR:.StatusPreklopke[17] | BYTE
STRStatusPreklopke18 | INT | IOD_STR | STR:.StatusPreklopke[18] | BYTE
STRStatusPreklopke19 | INT | IOD_STR | STR:.StatusPreklopke[19] | BYTE
STRStatusPreklopke1 | INT | IOD_STR | STR:.StatusPreklopke[1] | BYTE
STRStatusPreklopke20 | INT | IOD_STR | STR:.StatusPreklopke[20] | BYTE
STRStatusPreklopke21 | INT | IOD_STR | STR:.StatusPreklopke[21] | BYTE
STRStatusPreklopke22 | INT | IOD_STR | STR:.StatusPreklopke[22] | BYTE
STRStatusPreklopke23 | INT | IOD_STR | STR:.StatusPreklopke[23] | BYTE
STRStatusPreklopke24 | INT | IOD_STR | STR:.StatusPreklopke[24] | BYTE
STRStatusPreklopke25 | INT | IOD_STR | STR:.StatusPreklopke[25] | BYTE
STRStatusPreklopke2 | INT | IOD_STR | STR:.StatusPreklopke[2] | BYTE
STRStatusPreklopke3 | INT | IOD_STR | STR:.StatusPreklopke[3] | BYTE
STRStatusPreklopke4 | INT | IOD_STR | STR:.StatusPreklopke[4] | BYTE
STRStatusPreklopke5 | INT | IOD_STR | STR:.StatusPreklopke[5] | BYTE
STRStatusPreklopke6 | INT | IOD_STR | STR:.StatusPreklopke[6] | BYTE
STRStatusPreklopke7 | INT | IOD_STR | STR:.StatusPreklopke[7] | BYTE
STRStatusPreklopke8 | INT | IOD_STR | STR:.StatusPreklopke[8] | BYTE
STRStatusPreklopke9 | INT | IOD_STR | STR:.StatusPreklopke[9] | BYTE
STRTEgrelecNaTemp | DIGITAL | IOD_STR | STR:.TEgrelecNaTemp
STRTEgrelecTempMAX | REAL | IOD_STR | STR:.TEgrelecTempMAX
STRTEgrelecTempMIN | REAL | IOD_STR | STR:.TEgrelecTempMIN
STRTEgrelecTempVklop | DIGITAL | IOD_STR | STR:.TEgrelecTempVklop
STRTempAlarmPoint | REAL | IOD_STR | STR:.TempAlarmPoint
STRTempTIApovprecna | REAL | IOD_STR | STR:.TempTIApovprecna
STRTempTSprevisoka | DIGITAL | IOD_STR | STR:.TempTSprevisoka
STRToplPostHKcrpalkaON | DIGITAL | IOD_STR | STR:.ToplPost.HKcrpalkaON
STRToplPostHKcrpDnevniRezim | DIGITAL | IOD_STR | STR:.ToplPost.HKcrpDnevniRezim
STRToplPostHKcrpNocniRezim | DIGITAL | IOD_STR | STR:.ToplPost.HKcrpNocniRezim
STRToplPostHKdotokNastTemp | REAL | IOD_STR | STR:.ToplPost.HKdotokNastTemp
STRToplPostHKdotokTemp | REAL | IOD_STR | STR:.ToplPost.HKdotokTemp
STRToplPostHKpovtatekTemp | REAL | IOD_STR | STR:.ToplPost.HKpovtatekTemp
STRToplPostHKpovtratekNastTemp | REAL | IOD_STR | STR:.ToplPost.HKpovtratekNastTemp
STRToplPostHKrocniRezim | DIGITAL | IOD_STR | STR:.ToplPost.HKrocniRezim
STRToplPostHKzunanjaTemp | REAL | IOD_STR | STR:.ToplPost.HKzunanjaTemp
STRToplPostNapakaRegister | INT | IOD_STR | STR:.ToplPost.NapakaRegister
STRToplPostSkupnaNapaka | DIGITAL | IOD_STR | STR:.ToplPost.SkupnaNapaka
STRToplPostTVcrpalkaON | DIGITAL | IOD_STR | STR:.ToplPost.TVcrpalkaON
STRToplPostTVdotokNastTemp | REAL | IOD_STR | STR:.ToplPost.TVdotokNastTemp
STRToplPostTVdotokTemp | REAL | IOD_STR | STR:.ToplPost.TVdotokTemp
STRToplPostTVpovratekTemp | REAL | IOD_STR | STR:.ToplPost.TVpovratekTemp
STRToplPostTVrezervoarTemp | REAL | IOD_STR | STR:.ToplPost.TVrezervoarTemp
STRToplPostTVrocniRezim | DIGITAL | IOD_STR | STR:.ToplPost.TVrocniRezim
STRToplPostErrors0 | DIGITAL | IOD_STR | STR:.ToplPostErrors[0]
STRToplPostErrors10 | DIGITAL | IOD_STR | STR:.ToplPostErrors[10]
STRToplPostErrors11 | DIGITAL | IOD_STR | STR:.ToplPostErrors[11]
STRToplPostErrors12 | DIGITAL | IOD_STR | STR:.ToplPostErrors[12]
STRToplPostErrors13 | DIGITAL | IOD_STR | STR:.ToplPostErrors[13]
STRToplPostErrors14 | DIGITAL | IOD_STR | STR:.ToplPostErrors[14]
STRToplPostErrors15 | DIGITAL | IOD_STR | STR:.ToplPostErrors[15]
STRToplPostErrors16 | DIGITAL | IOD_STR | STR:.ToplPostErrors[16]
STRToplPostErrors17 | DIGITAL | IOD_STR | STR:.ToplPostErrors[17]
STRToplPostErrors1 | DIGITAL | IOD_STR | STR:.ToplPostErrors[1]
STRToplPostErrors2 | DIGITAL | IOD_STR | STR:.ToplPostErrors[2]
STRToplPostErrors3 | DIGITAL | IOD_STR | STR:.ToplPostErrors[3]
STRToplPostErrors4 | DIGITAL | IOD_STR | STR:.ToplPostErrors[4]
STRToplPostErrors5 | DIGITAL | IOD_STR | STR:.ToplPostErrors[5]
STRToplPostErrors6 | DIGITAL | IOD_STR | STR:.ToplPostErrors[6]
STRToplPostErrors7 | DIGITAL | IOD_STR | STR:.ToplPostErrors[7]
STRToplPostErrors8 | DIGITAL | IOD_STR | STR:.ToplPostErrors[8]
STRToplPostErrors9 | DIGITAL | IOD_STR | STR:.ToplPostErrors[9]
STRTYventilMax1 | REAL | IOD_STR | STR:.TYventilMax[1]
STRTYventilMax2 | REAL | IOD_STR | STR:.TYventilMax[2]
STRTYventilMax3 | REAL | IOD_STR | STR:.TYventilMax[3]
STRTYventilMax4 | REAL | IOD_STR | STR:.TYventilMax[4]
STRTYventilMin1 | REAL | IOD_STR | STR:.TYventilMin[1]
STRTYventilMin2 | REAL | IOD_STR | STR:.TYventilMin[2]
STRTYventilMin3 | REAL | IOD_STR | STR:.TYventilMin[3]
STRTYventilMin4 | REAL | IOD_STR | STR:.TYventilMin[4]
STRTYventilNaTemp1 | DIGITAL | IOD_STR | STR:.TYventilNaTemp[1]
STRTYventilNaTemp2 | DIGITAL | IOD_STR | STR:.TYventilNaTemp[2]
STRTYventilNaTemp3 | DIGITAL | IOD_STR | STR:.TYventilNaTemp[3]
STRTYventilNaTemp4 | DIGITAL | IOD_STR | STR:.TYventilNaTemp[4]
STRTYventilTempRazlika1 | REAL | IOD_STR | STR:.TYventilTempRazlika[1]
STRTYventilTempRazlika2 | REAL | IOD_STR | STR:.TYventilTempRazlika[2]
STRTYventilTempRazlika3 | REAL | IOD_STR | STR:.TYventilTempRazlika[3]
STRTYventilTempRazlika4 | REAL | IOD_STR | STR:.TYventilTempRazlika[4]
STRUrnik_SCtoXCpot | INT | IOD_STR | STR:.Urnik_SCtoXCpot
STRUrnik_SCtoXCzah | INT | IOD_STR | STR:.Urnik_SCtoXCzah
STRUrnik_XCtoSCpot | INT | IOD_STR | STR:.Urnik_XCtoSCpot
STRUrnik_XCtoSCzah | INT | IOD_STR | STR:.Urnik_XCtoSCzah
STRUrnikSCtoXCDan1Off1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[1].Mna | BYTE
STRUrnikSCtoXCDan1Off1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[1].Ura | BYTE
STRUrnikSCtoXCDan1Off2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[2].Mna | BYTE
STRUrnikSCtoXCDan1Off2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[2].Ura | BYTE
STRUrnikSCtoXCDan1Off3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[3].Mna | BYTE
STRUrnikSCtoXCDan1Off3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[3].Ura | BYTE
STRUrnikSCtoXCDan1On1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[1].Mna | BYTE
STRUrnikSCtoXCDan1On1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[1].Ura | BYTE
STRUrnikSCtoXCDan1On2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[2].Mna | BYTE
STRUrnikSCtoXCDan1On2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[2].Ura | BYTE
STRUrnikSCtoXCDan1On3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[3].Mna | BYTE
STRUrnikSCtoXCDan1On3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[3].Ura | BYTE
STRUrnikSCtoXCDan2Off1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[1].Mna | BYTE
STRUrnikSCtoXCDan2Off1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[1].Ura | BYTE
STRUrnikSCtoXCDan2Off2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[2].Mna | BYTE
STRUrnikSCtoXCDan2Off2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[2].Ura | BYTE
STRUrnikSCtoXCDan2Off3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[3].Mna | BYTE
STRUrnikSCtoXCDan2Off3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[3].Ura | BYTE
STRUrnikSCtoXCDan2On1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[1].Mna | BYTE
STRUrnikSCtoXCDan2On1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[1].Ura | BYTE
STRUrnikSCtoXCDan2On2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[2].Mna | BYTE
STRUrnikSCtoXCDan2On2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[2].Ura | BYTE
STRUrnikSCtoXCDan2On3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[3].Mna | BYTE
STRUrnikSCtoXCDan2On3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[3].Ura | BYTE
STRUrnikSCtoXCDan3Off1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[1].Mna | BYTE
STRUrnikSCtoXCDan3Off1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[1].Ura | BYTE
STRUrnikSCtoXCDan3Off2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[2].Mna | BYTE
STRUrnikSCtoXCDan3Off2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[2].Ura | BYTE
STRUrnikSCtoXCDan3Off3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[3].Mna | BYTE
STRUrnikSCtoXCDan3Off3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[3].Ura | BYTE
STRUrnikSCtoXCDan3On1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[1].Mna | BYTE
STRUrnikSCtoXCDan3On1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[1].Ura | BYTE
STRUrnikSCtoXCDan3On2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[2].Mna | BYTE
STRUrnikSCtoXCDan3On2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[2].Ura | BYTE
STRUrnikSCtoXCDan3On3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[3].Mna | BYTE
STRUrnikSCtoXCDan3On3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[3].Ura | BYTE
STRUrnikSCtoXCDan4Off1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[1].Mna | BYTE
STRUrnikSCtoXCDan4Off1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[1].Ura | BYTE
STRUrnikSCtoXCDan4Off2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[2].Mna | BYTE
STRUrnikSCtoXCDan4Off2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[2].Ura | BYTE
STRUrnikSCtoXCDan4Off3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[3].Mna | BYTE
STRUrnikSCtoXCDan4Off3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[3].Ura | BYTE
STRUrnikSCtoXCDan4On1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[1].Mna | BYTE
STRUrnikSCtoXCDan4On1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[1].Ura | BYTE
STRUrnikSCtoXCDan4On2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[2].Mna | BYTE
STRUrnikSCtoXCDan4On2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[2].Ura | BYTE
STRUrnikSCtoXCDan4On3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[3].Mna | BYTE
STRUrnikSCtoXCDan4On3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[3].Ura | BYTE
STRUrnikSCtoXCDan5Off1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[1].Mna | BYTE
STRUrnikSCtoXCDan5Off1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[1].Ura | BYTE
STRUrnikSCtoXCDan5Off2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[2].Mna | BYTE
STRUrnikSCtoXCDan5Off2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[2].Ura | BYTE
STRUrnikSCtoXCDan5Off3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[3].Mna | BYTE
STRUrnikSCtoXCDan5Off3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[3].Ura | BYTE
STRUrnikSCtoXCDan5On1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[1].Mna | BYTE
STRUrnikSCtoXCDan5On1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[1].Ura | BYTE
STRUrnikSCtoXCDan5On2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[2].Mna | BYTE
STRUrnikSCtoXCDan5On2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[2].Ura | BYTE
STRUrnikSCtoXCDan5On3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[3].Mna | BYTE
STRUrnikSCtoXCDan5On3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[3].Ura | BYTE
STRUrnikSCtoXCDan6Off1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[1].Mna | BYTE
STRUrnikSCtoXCDan6Off1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[1].Ura | BYTE
STRUrnikSCtoXCDan6Off2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[2].Mna | BYTE
STRUrnikSCtoXCDan6Off2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[2].Ura | BYTE
STRUrnikSCtoXCDan6Off3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[3].Mna | BYTE
STRUrnikSCtoXCDan6Off3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[3].Ura | BYTE
STRUrnikSCtoXCDan6On1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[1].Mna | BYTE
STRUrnikSCtoXCDan6On1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[1].Ura | BYTE
STRUrnikSCtoXCDan6On2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[2].Mna | BYTE
STRUrnikSCtoXCDan6On2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[2].Ura | BYTE
STRUrnikSCtoXCDan6On3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[3].Mna | BYTE
STRUrnikSCtoXCDan6On3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[3].Ura | BYTE
STRUrnikSCtoXCDan7Off1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[1].Mna | BYTE
STRUrnikSCtoXCDan7Off1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[1].Ura | BYTE
STRUrnikSCtoXCDan7Off2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[2].Mna | BYTE
STRUrnikSCtoXCDan7Off2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[2].Ura | BYTE
STRUrnikSCtoXCDan7Off3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[3].Mna | BYTE
STRUrnikSCtoXCDan7Off3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[3].Ura | BYTE
STRUrnikSCtoXCDan7On1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[1].Mna | BYTE
STRUrnikSCtoXCDan7On1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[1].Ura | BYTE
STRUrnikSCtoXCDan7On2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[2].Mna | BYTE
STRUrnikSCtoXCDan7On2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[2].Ura | BYTE
STRUrnikSCtoXCDan7On3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[3].Mna | BYTE
STRUrnikSCtoXCDan7On3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[3].Ura | BYTE
STRUrnikXCtoSCDan1Off1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[1].Mna | BYTE
STRUrnikXCtoSCDan1Off1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[1].Ura | BYTE
STRUrnikXCtoSCDan1Off2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[2].Mna | BYTE
STRUrnikXCtoSCDan1Off2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[2].Ura | BYTE
STRUrnikXCtoSCDan1Off3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[3].Mna | BYTE
STRUrnikXCtoSCDan1Off3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[3].Ura | BYTE
STRUrnikXCtoSCDan1On1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[1].Mna | BYTE
STRUrnikXCtoSCDan1On1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[1].Ura | BYTE
STRUrnikXCtoSCDan1On2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[2].Mna | BYTE
STRUrnikXCtoSCDan1On2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[2].Ura | BYTE
STRUrnikXCtoSCDan1On3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[3].Mna | BYTE
STRUrnikXCtoSCDan1On3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[3].Ura | BYTE
STRUrnikXCtoSCDan2Off1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[1].Mna | BYTE
STRUrnikXCtoSCDan2Off1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[1].Ura | BYTE
STRUrnikXCtoSCDan2Off2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[2].Mna | BYTE
STRUrnikXCtoSCDan2Off2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[2].Ura | BYTE
STRUrnikXCtoSCDan2Off3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[3].Mna | BYTE
STRUrnikXCtoSCDan2Off3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[3].Ura | BYTE
STRUrnikXCtoSCDan2On1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[1].Mna | BYTE
STRUrnikXCtoSCDan2On1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[1].Ura | BYTE
STRUrnikXCtoSCDan2On2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[2].Mna | BYTE
STRUrnikXCtoSCDan2On2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[2].Ura | BYTE
STRUrnikXCtoSCDan2On3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[3].Mna | BYTE
STRUrnikXCtoSCDan2On3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[3].Ura | BYTE
STRUrnikXCtoSCDan3Off1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[1].Mna | BYTE
STRUrnikXCtoSCDan3Off1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[1].Ura | BYTE
STRUrnikXCtoSCDan3Off2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[2].Mna | BYTE
STRUrnikXCtoSCDan3Off2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[2].Ura | BYTE
STRUrnikXCtoSCDan3Off3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[3].Mna | BYTE
STRUrnikXCtoSCDan3Off3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[3].Ura | BYTE
STRUrnikXCtoSCDan3On1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[1].Mna | BYTE
STRUrnikXCtoSCDan3On1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[1].Ura | BYTE
STRUrnikXCtoSCDan3On2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[2].Mna | BYTE
STRUrnikXCtoSCDan3On2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[2].Ura | BYTE
STRUrnikXCtoSCDan3On3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[3].Mna | BYTE
STRUrnikXCtoSCDan3On3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[3].Ura | BYTE
STRUrnikXCtoSCDan4Off1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[1].Mna | BYTE
STRUrnikXCtoSCDan4Off1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[1].Ura | BYTE
STRUrnikXCtoSCDan4Off2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[2].Mna | BYTE
STRUrnikXCtoSCDan4Off2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[2].Ura | BYTE
STRUrnikXCtoSCDan4Off3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[3].Mna | BYTE
STRUrnikXCtoSCDan4Off3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[3].Ura | BYTE
STRUrnikXCtoSCDan4On1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[1].Mna | BYTE
STRUrnikXCtoSCDan4On1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[1].Ura | BYTE
STRUrnikXCtoSCDan4On2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[2].Mna | BYTE
STRUrnikXCtoSCDan4On2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[2].Ura | BYTE
STRUrnikXCtoSCDan4On3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[3].Mna | BYTE
STRUrnikXCtoSCDan4On3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[3].Ura | BYTE
STRUrnikXCtoSCDan5Off1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[1].Mna | BYTE
STRUrnikXCtoSCDan5Off1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[1].Ura | BYTE
STRUrnikXCtoSCDan5Off2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[2].Mna | BYTE
STRUrnikXCtoSCDan5Off2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[2].Ura | BYTE
STRUrnikXCtoSCDan5Off3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[3].Mna | BYTE
STRUrnikXCtoSCDan5Off3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[3].Ura | BYTE
STRUrnikXCtoSCDan5On1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[1].Mna | BYTE
STRUrnikXCtoSCDan5On1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[1].Ura | BYTE
STRUrnikXCtoSCDan5On2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[2].Mna | BYTE
STRUrnikXCtoSCDan5On2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[2].Ura | BYTE
STRUrnikXCtoSCDan5On3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[3].Mna | BYTE
STRUrnikXCtoSCDan5On3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[3].Ura | BYTE
STRUrnikXCtoSCDan6Off1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[1].Mna | BYTE
STRUrnikXCtoSCDan6Off1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[1].Ura | BYTE
STRUrnikXCtoSCDan6Off2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[2].Mna | BYTE
STRUrnikXCtoSCDan6Off2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[2].Ura | BYTE
STRUrnikXCtoSCDan6Off3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[3].Mna | BYTE
STRUrnikXCtoSCDan6Off3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[3].Ura | BYTE
STRUrnikXCtoSCDan6On1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[1].Mna | BYTE
STRUrnikXCtoSCDan6On1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[1].Ura | BYTE
STRUrnikXCtoSCDan6On2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[2].Mna | BYTE
STRUrnikXCtoSCDan6On2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[2].Ura | BYTE
STRUrnikXCtoSCDan6On3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[3].Mna | BYTE
STRUrnikXCtoSCDan6On3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[3].Ura | BYTE
STRUrnikXCtoSCDan7Off1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[1].Mna | BYTE
STRUrnikXCtoSCDan7Off1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[1].Ura | BYTE
STRUrnikXCtoSCDan7Off2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[2].Mna | BYTE
STRUrnikXCtoSCDan7Off2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[2].Ura | BYTE
STRUrnikXCtoSCDan7Off3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[3].Mna | BYTE
STRUrnikXCtoSCDan7Off3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[3].Ura | BYTE
STRUrnikXCtoSCDan7On1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[1].Mna | BYTE
STRUrnikXCtoSCDan7On1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[1].Ura | BYTE
STRUrnikXCtoSCDan7On2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[2].Mna | BYTE
STRUrnikXCtoSCDan7On2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[2].Ura | BYTE
STRUrnikXCtoSCDan7On3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[3].Mna | BYTE
STRUrnikXCtoSCDan7On3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[3].Ura | BYTE
STRUserCurrentLevel | INT | IOD_STR | STR:.UserCurrentLevel | BYTE
STRUserCurrentName | STRING | IOD_STR | STR:.UserCurrentName
STRUserLoggedIn | DIGITAL | IOD_STR | STR:.UserLoggedIn
STRValAI_Temp1B1 | REAL | IOD_STR | STR:.ValAI_Temp1B1
STRValAI_Temp1B2 | REAL | IOD_STR | STR:.ValAI_Temp1B2
STRValAI_Temp1B3 | REAL | IOD_STR | STR:.ValAI_Temp1B3
STRValAI_Temp2B2 | REAL | IOD_STR | STR:.ValAI_Temp2B2
STRValAI_Temp2B3 | REAL | IOD_STR | STR:.ValAI_Temp2B3
STRValAI_TempHB2 | REAL | IOD_STR | STR:.ValAI_TempHB2
STRValAI_TempHB4 | REAL | IOD_STR | STR:.ValAI_TempHB4
STRValAI_TempHB9 | REAL | IOD_STR | STR:.ValAI_TempHB9
STRValAI_TempTB1 | REAL | IOD_STR | STR:.ValAI_TempTB1
STRValAI_TempTB10 | REAL | IOD_STR | STR:.ValAI_TempTB10
STRValAI_TempTB2 | REAL | IOD_STR | STR:.ValAI_TempTB2
STRValAI_TempTB3 | REAL | IOD_STR | STR:.ValAI_TempTB3
STRValAI_TempTB4 | REAL | IOD_STR | STR:.ValAI_TempTB4
STRValAI_TempTB8 | REAL | IOD_STR | STR:.ValAI_TempTB8
STRValAI_TlakExp1S1 | REAL | IOD_STR | STR:.ValAI_TlakExp1S1
STRValAI_TlakExp1S2 | REAL | IOD_STR | STR:.ValAI_TlakExp1S2
STRValAI_TlakExp2S1 | REAL | IOD_STR | STR:.ValAI_TlakExp2S1
STRValAI_TlakExp2S2 | REAL | IOD_STR | STR:.ValAI_TlakExp2S2
STRValAI_TlakHB15 | REAL | IOD_STR | STR:.ValAI_TlakHB15
STRValAI_TlakHB16 | REAL | IOD_STR | STR:.ValAI_TlakHB16
STRValAI_TlakHB17 | REAL | IOD_STR | STR:.ValAI_TlakHB17
STRValAI_TlakHB3 | REAL | IOD_STR | STR:.ValAI_TlakHB3
STRValAI_TlakTB11 | REAL | IOD_STR | STR:.ValAI_TlakTB11
STRValAI_TlakTB12 | REAL | IOD_STR | STR:.ValAI_TlakTB12
STRValAI_TlakTB13 | REAL | IOD_STR | STR:.ValAI_TlakTB13
STRValAI_TlakTB14 | REAL | IOD_STR | STR:.ValAI_TlakTB14
STRValAI_Vlaga1B4 | REAL | IOD_STR | STR:.ValAI_Vlaga1B4
STRValAI_Vlaga2B4 | REAL | IOD_STR | STR:.ValAI_Vlaga2B4
STRValAO_RegVentTY1 | REAL | IOD_STR | STR:.ValAO_RegVentTY[1]
STRValAO_RegVentTY2 | REAL | IOD_STR | STR:.ValAO_RegVentTY[2]
STRValAO_RegVentTY3 | REAL | IOD_STR | STR:.ValAO_RegVentTY[3]
STRValAO_RegVentTY4 | REAL | IOD_STR | STR:.ValAO_RegVentTY[4]
STRVentilatorOnOff1 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[1]
STRVentilatorOnOff2 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[2]
STRVentilatorOnOff3 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[3]
STRVentilatorOnOff4 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[4]
STRVentilatorOnOff5 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[5]
STRVentilatorOnOff6 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[6]
STRVklopSCFBNapaka10 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[10]
STRVklopSCFBNapaka11 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[11]
STRVklopSCFBNapaka12 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[12]
STRVklopSCFBNapaka13 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[13]
STRVklopSCFBNapaka14 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[14]
STRVklopSCFBNapaka15 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[15]
STRVklopSCFBNapaka16 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[16]
STRVklopSCFBNapaka17 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[17]
STRVklopSCFBNapaka18 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[18]
STRVklopSCFBNapaka19 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[19]
STRVklopSCFBNapaka1 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[1]
STRVklopSCFBNapaka20 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[20]
STRVklopSCFBNapaka21 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[21]
STRVklopSCFBNapaka22 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[22]
STRVklopSCFBNapaka23 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[23]
STRVklopSCFBNapaka24 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[24]
STRVklopSCFBNapaka25 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[25]
STRVklopSCFBNapaka2 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[2]
STRVklopSCFBNapaka3 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[3]
STRVklopSCFBNapaka4 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[4]
STRVklopSCFBNapaka5 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[5]
STRVklopSCFBNapaka6 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[6]
STRVklopSCFBNapaka7 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[7]
STRVklopSCFBNapaka8 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[8]
STRVklopSCFBNapaka9 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[9]
STRVlagaHIApovprecna | REAL | IOD_STR | STR:.VlagaHIApovprecna
STRXVH_AlarmOn | DIGITAL | IOD_STR | STR:.XVH_AlarmOn
STRXVH_CrpalkaGrfsNum | LONG | IOD_STR | STR:.XVH_CrpalkaGrfsNum
STRXVH_StUrnika | LONG | IOD_STR | STR:.XVH_StUrnika
STRXVH_IzklopVsehLuci | DIGITAL | IOD_STR | STR:.XVH_IzklopVsehLuci
STRXVH_VklopVsehLuci | DIGITAL | IOD_STR | STR:.XVH_VklopVsehLuci
STRPrenasanjeUrnikovAktivno | DIGITAL | IOD_STR | STR:.PrenasanjeUrnikovAktivno
STRPrenasanjeUrnikovAktivno1 | DIGITAL | IOD_STR | STR:.PrenasanjeUrnikovAktivno1
STRCircutorCosFi_III | REAL | IOD_STR | STR:.Circutor.CosFi_III
STRCircutorDelovnaEnergija | REAL | IOD_STR | STR:.Circutor.DelovnaEnergija
STRCircutorDelovnaMoc_III | REAL | IOD_STR | STR:.Circutor.DelovnaMoc_III
STRCircutorDelovnaMoc_L1 | REAL | IOD_STR | STR:.Circutor.DelovnaMoc_L1
STRCircutorDelovnaMoc_L2 | REAL | IOD_STR | STR:.Circutor.DelovnaMoc_L2
STRCircutorDelovnaMoc_L3 | REAL | IOD_STR | STR:.Circutor.DelovnaMoc_L3
STRCircutorFrekvenca_L1 | REAL | IOD_STR | STR:.Circutor.Frekvenca_L1
STRCircutorInduktivnaEnergija | REAL | IOD_STR | STR:.Circutor.InduktivnaEnergija
STRCircutorInduktivnaMoc_III | REAL | IOD_STR | STR:.Circutor.InduktivnaMoc_III
STRCircutorJalovaMoc_L1 | REAL | IOD_STR | STR:.Circutor.JalovaMoc_L1
STRCircutorJalovaMoc_L2 | REAL | IOD_STR | STR:.Circutor.JalovaMoc_L2
STRCircutorJalovaMoc_L3 | REAL | IOD_STR | STR:.Circutor.JalovaMoc_L3
STRCircutorKapacitivnaEnergija | REAL | IOD_STR | STR:.Circutor.KapacitivnaEnergija
STRCircutorKapacitivnaMoc_III | REAL | IOD_STR | STR:.Circutor.KapacitivnaMoc_III
STRCircutorMaximumDemand | REAL | IOD_STR | STR:.Circutor.MaximumDemand
STRCircutorNapetost_L1_L2 | REAL | IOD_STR | STR:.Circutor.Napetost_L1_L2
STRCircutorNapetost_L1_N | REAL | IOD_STR | STR:.Circutor.Napetost_L1_N
STRCircutorNapetost_L2_L3 | REAL | IOD_STR | STR:.Circutor.Napetost_L2_L3
STRCircutorNapetost_L2_N | REAL | IOD_STR | STR:.Circutor.Napetost_L2_N
STRCircutorNapetost_L3_L1 | REAL | IOD_STR | STR:.Circutor.Napetost_L3_L1
STRCircutorNapetost_L3_N | REAL | IOD_STR | STR:.Circutor.Napetost_L3_N
STRCircutorNavideznaMoc_III | REAL | IOD_STR | STR:.Circutor.NavideznaMoc_III
STRCircutorNicelniTok | REAL | IOD_STR | STR:.Circutor.NicelniTok
STRCircutorPowerFactor_III | REAL | IOD_STR | STR:.Circutor.PowerFactor_III
STRCircutorPowerFactor_L1 | REAL | IOD_STR | STR:.Circutor.PowerFactor_L1
STRCircutorPowerFactor_L2 | REAL | IOD_STR | STR:.Circutor.PowerFactor_L2
STRCircutorPowerFactor_L3 | REAL | IOD_STR | STR:.Circutor.PowerFactor_L3
STRCircutorTHDI_L1 | REAL | IOD_STR | STR:.Circutor.THDI_L1
STRCircutorTHDI_L2 | REAL | IOD_STR | STR:.Circutor.THDI_L2
STRCircutorTHDI_L3 | REAL | IOD_STR | STR:.Circutor.THDI_L3
STRCircutorTHDV_L1 | REAL | IOD_STR | STR:.Circutor.THDV_L1
STRCircutorTHDV_L2 | REAL | IOD_STR | STR:.Circutor.THDV_L2
STRCircutorTHDV_L3 | REAL | IOD_STR | STR:.Circutor.THDV_L3
STRCircutorTok_L1 | REAL | IOD_STR | STR:.Circutor.Tok_L1
STRCircutorTok_L2 | REAL | IOD_STR | STR:.Circutor.Tok_L2
STRCircutorTok_L3 | REAL | IOD_STR | STR:.Circutor.Tok_L3
STRCircutorTokPovprecje_III | REAL | IOD_STR | STR:.Circutor.TokPovprecje_III
STRCrpalkeGrfsGalAlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmActiveCode
STRCrpalkeGrfsGalAlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.AlarmAktiven
STRCrpalkeGrfsGalAlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmCodeLog1
STRCrpalkeGrfsGalAlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmCodeLog2
STRCrpalkeGrfsGalAlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmCodeLog3
STRCrpalkeGrfsGalAlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmCodeLog4
STRCrpalkeGrfsGalAlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmCodeLog5
STRCrpalkeGrfsGalAlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[0]
STRCrpalkeGrfsGalAlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[10]
STRCrpalkeGrfsGalAlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[11]
STRCrpalkeGrfsGalAlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[12]
STRCrpalkeGrfsGalAlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[13]
STRCrpalkeGrfsGalAlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[14]
STRCrpalkeGrfsGalAlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[15]
STRCrpalkeGrfsGalAlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[16]
STRCrpalkeGrfsGalAlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[1]
STRCrpalkeGrfsGalAlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[2]
STRCrpalkeGrfsGalAlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[3]
STRCrpalkeGrfsGalAlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[4]
STRCrpalkeGrfsGalAlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[5]
STRCrpalkeGrfsGalAlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[6]
STRCrpalkeGrfsGalAlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[7]
STRCrpalkeGrfsGalAlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[8]
STRCrpalkeGrfsGalAlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[9]
STRCrpalkeGrfsGalAlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmQSD1
STRCrpalkeGrfsGalAlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmQSD2
STRCrpalkeGrfsGalAlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmStart1
STRCrpalkeGrfsGalAlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmStart2
STRCrpalkeGrfsGalAlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmStop1
STRCrpalkeGrfsGalAlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmStop2
STRCrpalkeGrfsGalAlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmStop3
STRCrpalkeGrfsGalAlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmSurv1
STRCrpalkeGrfsGalAlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmSurv2
STRCrpalkeGrfsGalControlSource | INT | IOD_STR | STR:.CrpalkeGrfsGal.ControlSource
STRCrpalkeGrfsGalDeluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.Deluje
STRCrpalkeGrfsGalEnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfsGal.EnergijaPoraba
STRCrpalkeGrfsGalExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfsGal.ExternInputSetup
STRCrpalkeGrfsGalExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfsGal.ExternInputsStatus
STRCrpalkeGrfsGalFrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfsGal.FrekPretvornikDCNapetost
STRCrpalkeGrfsGalFrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfsGal.FrekPretvornikDCTok
STRCrpalkeGrfsGalFreqMax | REAL | IOD_STR | STR:.CrpalkeGrfsGal.FreqMax
STRCrpalkeGrfsGalFreqMin | REAL | IOD_STR | STR:.CrpalkeGrfsGal.FreqMin
STRCrpalkeGrfsGalFreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfsGal.FreqUpper
STRCrpalkeGrfsGalLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.LocalMode
STRCrpalkeGrfsGalLocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.LocalSetupMode1
STRCrpalkeGrfsGalMocMax | REAL | IOD_STR | STR:.CrpalkeGrfsGal.MocMax
STRCrpalkeGrfsGalMocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfsGal.MocTrenutna
STRCrpalkeGrfsGalMotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfsGal.MotorHitrost
STRCrpalkeGrfsGalMotorTok | REAL | IOD_STR | STR:.CrpalkeGrfsGal.MotorTok
STRCrpalkeGrfsGalNapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfsGal.NapajanjeTok
STRCrpalkeGrfsGalNastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfsGal.NastavitevLokalna
STRCrpalkeGrfsGalNastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfsGal.NastavitevTrenutna
STRCrpalkeGrfsGalPreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfsGal.PreklopkaMode
STRCrpalkeGrfsGalPretokMax | REAL | IOD_STR | STR:.CrpalkeGrfsGal.PretokMax
STRCrpalkeGrfsGalPretokMin | REAL | IOD_STR | STR:.CrpalkeGrfsGal.PretokMin
STRCrpalkeGrfsGalPretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfsGal.PretokTrenutni
STRCrpalkeGrfsGalPritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfsGal.PritiskMax
STRCrpalkeGrfsGalPritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfsGal.PritiskTrenutni
STRCrpalkeGrfsGalReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfsGal.ReferencaMotorjaHzV
STRCrpalkeGrfsGalReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfsGal.ReferencaRemote
STRCrpalkeGrfsGalRelay1setup | INT | IOD_STR | STR:.CrpalkeGrfsGal.Relay1setup
STRCrpalkeGrfsGalRemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.RemoteON
STRCrpalkeGrfsGalRemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.RemoteSetupMode1
STRCrpalkeGrfsGalReset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.Reset2handkWhValues
STRCrpalkeGrfsGalResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.ResetAlarm
STRCrpalkeGrfsGalResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.ResetAlarmLog
STRCrpalkeGrfsGalResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.ResetDevice
STRCrpalkeGrfsGalSetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetAutomatic
STRCrpalkeGrfsGalSetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetConstFreqMode
STRCrpalkeGrfsGalSetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetConstPress
STRCrpalkeGrfsGalSetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetLocalMode
STRCrpalkeGrfsGalSetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetMaxRunMode
STRCrpalkeGrfsGalSetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetMinRunMode
STRCrpalkeGrfsGalSetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetPropPress
STRCrpalkeGrfsGalSetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetReference
STRCrpalkeGrfsGalSetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetRemoteMode
STRCrpalkeGrfsGalSetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetTwinModeAlt
STRCrpalkeGrfsGalSetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetTwinModeSpare
STRCrpalkeGrfsGalSetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetTwinModeSync
STRCrpalkeGrfsGalStart | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.Start
STRCrpalkeGrfsGalStatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfsGal.StatusCrpalke | BYTE
STRCrpalkeGrfsGalStatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.StatusMode1
STRCrpalkeGrfsGalStatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfsGal.StatusMode1co | BYTE
STRCrpalkeGrfsGalStatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfsGal.StatusMode1op | BYTE
STRCrpalkeGrfsGalStatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.StatusMode2
STRCrpalkeGrfsGalStatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfsGal.StatusMode3
STRCrpalkeGrfsGalStevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfsGal.StevecUr2h
STRCrpalkeGrfsGalStop | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.Stop
STRCrpalkeGrfsGalSystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfsGal.SystemFeedback
STRCrpalkeGrfsGalSystemReference | REAL | IOD_STR | STR:.CrpalkeGrfsGal.SystemReference
STRCrpalkeGrfsGalTemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfsGal.TemperaturaMotorja
STRCrpalkeGrfsGalUreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfsGal.UreXC200
STRCrpGrfsPIDregKP | REAL | IOD_STR | STR:.CrpGrfsPIDregKP
STRCrpGrfsPIDregTN | INT | IOD_STR | STR:.CrpGrfsPIDregTN
STRDate_Time0 | STRING | IOD_STR | STR:.Date_Time[0]
STRDate_Time1 | STRING | IOD_STR | STR:.Date_Time[1]
STRDate_Time2 | STRING | IOD_STR | STR:.Date_Time[2]
STRDate_Time3 | STRING | IOD_STR | STR:.Date_Time[3]
STRDateTimeDanVtednu | INT | IOD_STR | STR:.DateTime.DanVtednu | BYTE
STRDI_rezerva10_2 | DIGITAL | IOD_STR | STR:.DI_rezerva10_2
STRDI_rezerva10_7 | DIGITAL | IOD_STR | STR:.DI_rezerva10_7
STRDI_rezerva11_4 | DIGITAL | IOD_STR | STR:.DI_rezerva11_4
STRDI_rezerva14_0 | DIGITAL | IOD_STR | STR:.DI_rezerva14_0
STRDI_rezerva14_2 | DIGITAL | IOD_STR | STR:.DI_rezerva14_2
STRDI_rezerva14_3 | DIGITAL | IOD_STR | STR:.DI_rezerva14_3
STRDI_rezerva14_4 | DIGITAL | IOD_STR | STR:.DI_rezerva14_4
STRDI_rezerva14_5 | DIGITAL | IOD_STR | STR:.DI_rezerva14_5
STRDI_rezerva14_7 | DIGITAL | IOD_STR | STR:.DI_rezerva14_7
STRDI_rezerva2_4 | DIGITAL | IOD_STR | STR:.DI_rezerva2_4
STRDI_rezerva3_5 | DIGITAL | IOD_STR | STR:.DI_rezerva3_5
STRDIN_AkumTopVodeAUTO | DIGITAL | IOD_STR | STR:.DIN_AkumTopVodeAUTO
STRDIN_CrpHM1AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM1AUTO
STRDIN_CrpHM1kontON | DIGITAL | IOD_STR | STR:.DIN_CrpHM1kontON
STRDIN_CrpHM2AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM2AUTO
STRDIN_CrpHM2kontON | DIGITAL | IOD_STR | STR:.DIN_CrpHM2kontON
STRDIN_CrpHM3AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM3AUTO
STRDIN_CrpHM3kontON | DIGITAL | IOD_STR | STR:.DIN_CrpHM3kontON
STRDIN_CrpHM4AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM4AUTO
STRDIN_CrpHM4kontON | DIGITAL | IOD_STR | STR:.DIN_CrpHM4kontON
STRDIN_CrpHM5AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM5AUTO
STRDIN_CrpHM6AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM6AUTO
STRDIN_CrpHM7AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM7AUTO
STRDIN_CrpHM8AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM8AUTO
STRDIN_CrpMN1AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpMN1AUTO
STRDIN_CrpMN1kontON | DIGITAL | IOD_STR | STR:.DIN_CrpMN1kontON
STRDIN_CrpTM10AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM10AUTO
STRDIN_CrpTM11TM12AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM11TM12AUTO
STRDIN_CrpTM11TM12kontON | DIGITAL | IOD_STR | STR:.DIN_CrpTM11TM12kontON
STRDIN_CrpTM1AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM1AUTO
STRDIN_CrpTM2AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM2AUTO
STRDIN_CrpTM3AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM3AUTO
STRDIN_CrpTM4AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM4AUTO
STRDIN_CrpTM5AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM5AUTO
STRDIN_CrpTM6AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM6AUTO
STRDIN_CrpTM7AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM7AUTO
STRDIN_CrpTM8AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM8AUTO
STRDIN_CrpTM9AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM9AUTO
STRDIN_GlStikaloDieselON | DIGITAL | IOD_STR | STR:.DIN_GlStikaloDieselON
STRDIN_GlStikaloMrezaON | DIGITAL | IOD_STR | STR:.DIN_GlStikaloMrezaON
STRDIN_GlStikaloUpsON | DIGITAL | IOD_STR | STR:.DIN_GlStikaloUpsON
STRDIN_HladStAUTO | DIGITAL | IOD_STR | STR:.DIN_HladStAUTO
STRDIN_Kond1AUTO | DIGITAL | IOD_STR | STR:.DIN_Kond1AUTO
STRDIN_Kond2AUTO | DIGITAL | IOD_STR | STR:.DIN_Kond2AUTO
STRDIN_Kond3AUTO | DIGITAL | IOD_STR | STR:.DIN_Kond3AUTO
STRDIN_Vent1Auto | DIGITAL | IOD_STR | STR:.DIN_Vent1Auto
STRDIN_Vent1kontON | DIGITAL | IOD_STR | STR:.DIN_Vent1kontON
STRDIN_Vent2Auto | DIGITAL | IOD_STR | STR:.DIN_Vent2Auto
STRDIN_Vent2kontON | DIGITAL | IOD_STR | STR:.DIN_Vent2kontON
STRDIN_Vent3Auto | DIGITAL | IOD_STR | STR:.DIN_Vent3Auto
STRDIN_Vent3kontON | DIGITAL | IOD_STR | STR:.DIN_Vent3kontON
STRDIN_Vent4Auto | DIGITAL | IOD_STR | STR:.DIN_Vent4Auto
STRDIN_Vent4kontON | DIGITAL | IOD_STR | STR:.DIN_Vent4kontON
STRDIN_Vent5Auto | DIGITAL | IOD_STR | STR:.DIN_Vent5Auto
STRDIN_Vent5kontON | DIGITAL | IOD_STR | STR:.DIN_Vent5kontON
STRDIN_Vent6Auto | DIGITAL | IOD_STR | STR:.DIN_Vent6Auto
STRDIN_Vent6kontON | DIGITAL | IOD_STR | STR:.DIN_Vent6kontON
STRDO_rezerva0_2 | DIGITAL | IOD_STR | STR:.DO_rezerva0_2
STRDO_rezerva0_3 | DIGITAL | IOD_STR | STR:.DO_rezerva0_3
STRDO_rezerva0_4 | DIGITAL | IOD_STR | STR:.DO_rezerva0_4
STRDO_rezerva0_5 | DIGITAL | IOD_STR | STR:.DO_rezerva0_5
STRDO_rezerva1_3 | DIGITAL | IOD_STR | STR:.DO_rezerva1_3
STRDO_rezerva1_4 | DIGITAL | IOD_STR | STR:.DO_rezerva1_4
STRDO_rezerva1_5 | DIGITAL | IOD_STR | STR:.DO_rezerva1_5
STRDO_rezerva3_4 | DIGITAL | IOD_STR | STR:.DO_rezerva3_4
STRDO_rezerva3_6 | DIGITAL | IOD_STR | STR:.DO_rezerva3_6
STRDO_rezerva4_0 | DIGITAL | IOD_STR | STR:.DO_rezerva4_0
STRLetniCasDatumi111 | INT | IOD_STR | STR:.LetniCasDatumi[1,1,1]
STRLetniCasDatumi112 | INT | IOD_STR | STR:.LetniCasDatumi[1,1,2]
STRLetniCasDatumi121 | INT | IOD_STR | STR:.LetniCasDatumi[1,2,1]
STRLetniCasDatumi122 | INT | IOD_STR | STR:.LetniCasDatumi[1,2,2]
STRLetniCasDatumi131 | INT | IOD_STR | STR:.LetniCasDatumi[1,3,1]
STRLetniCasDatumi132 | INT | IOD_STR | STR:.LetniCasDatumi[1,3,2]
STRLetniCasDatumi141 | INT | IOD_STR | STR:.LetniCasDatumi[1,4,1]
STRLetniCasDatumi142 | INT | IOD_STR | STR:.LetniCasDatumi[1,4,2]
STRLetniCasDatumi211 | INT | IOD_STR | STR:.LetniCasDatumi[2,1,1]
STRLetniCasDatumi212 | INT | IOD_STR | STR:.LetniCasDatumi[2,1,2]
STRLetniCasDatumi221 | INT | IOD_STR | STR:.LetniCasDatumi[2,2,1]
STRLetniCasDatumi222 | INT | IOD_STR | STR:.LetniCasDatumi[2,2,2]
STRLetniCasDatumi231 | INT | IOD_STR | STR:.LetniCasDatumi[2,3,1]
STRLetniCasDatumi232 | INT | IOD_STR | STR:.LetniCasDatumi[2,3,2]
STRLetniCasDatumi241 | INT | IOD_STR | STR:.LetniCasDatumi[2,4,1]
STRLetniCasDatumi242 | INT | IOD_STR | STR:.LetniCasDatumi[2,4,2]
STRPrenosUrnika26 | DIGITAL | IOD_STR | STR:.PrenosUrnika[26]
STRPrenosUrnika27 | DIGITAL | IOD_STR | STR:.PrenosUrnika[27]
STRPrenosUrnika28 | DIGITAL | IOD_STR | STR:.PrenosUrnika[28]
STRPrenosUrnika29 | DIGITAL | IOD_STR | STR:.PrenosUrnika[29]
STRPrenosUrnika30 | DIGITAL | IOD_STR | STR:.PrenosUrnika[30]
STRPrenosUrnika31 | DIGITAL | IOD_STR | STR:.PrenosUrnika[31]
STRPrenosUrnika32 | DIGITAL | IOD_STR | STR:.PrenosUrnika[32]
STRPrenosUrnika33 | DIGITAL | IOD_STR | STR:.PrenosUrnika[33]
STRPrenosUrnika34 | DIGITAL | IOD_STR | STR:.PrenosUrnika[34]
STRPrenosUrnika35 | DIGITAL | IOD_STR | STR:.PrenosUrnika[35]
STRPrenosUrnika36 | DIGITAL | IOD_STR | STR:.PrenosUrnika[36]
STRPrenosUrnika37 | DIGITAL | IOD_STR | STR:.PrenosUrnika[37]
STRPrenosUrnika38 | DIGITAL | IOD_STR | STR:.PrenosUrnika[38]
STRPrenosUrnika39 | DIGITAL | IOD_STR | STR:.PrenosUrnika[39]
STRPrenosUrnika40 | DIGITAL | IOD_STR | STR:.PrenosUrnika[40]
STRPrenosUrnika41 | DIGITAL | IOD_STR | STR:.PrenosUrnika[41]
STRPrenosUrnika42 | DIGITAL | IOD_STR | STR:.PrenosUrnika[42]
STRPrenosUrnika43 | DIGITAL | IOD_STR | STR:.PrenosUrnika[43]
STRPrenosUrnika44 | DIGITAL | IOD_STR | STR:.PrenosUrnika[44]
STRPrenosUrnika45 | DIGITAL | IOD_STR | STR:.PrenosUrnika[45]
STRPrenosUrnika46 | DIGITAL | IOD_STR | STR:.PrenosUrnika[46]
STRPrenosUrnika47 | DIGITAL | IOD_STR | STR:.PrenosUrnika[47]
STRPrenosUrnika48 | DIGITAL | IOD_STR | STR:.PrenosUrnika[48]
STRPrenosUrnika49 | DIGITAL | IOD_STR | STR:.PrenosUrnika[49]
STRPrenosUrnika50 | DIGITAL | IOD_STR | STR:.PrenosUrnika[50]
STRPrenosUrnika51 | DIGITAL | IOD_STR | STR:.PrenosUrnika[51]
STRPrenosUrnika52 | DIGITAL | IOD_STR | STR:.PrenosUrnika[52]
STRPrenosUrnika53 | DIGITAL | IOD_STR | STR:.PrenosUrnika[53]
STRPrenosUrnika54 | DIGITAL | IOD_STR | STR:.PrenosUrnika[54]
STRPrenosUrnika55 | DIGITAL | IOD_STR | STR:.PrenosUrnika[55]
STRPrenosUrnika56 | DIGITAL | IOD_STR | STR:.PrenosUrnika[56]
STRPrenosUrnika57 | DIGITAL | IOD_STR | STR:.PrenosUrnika[57]
STRPrenosUrnika58 | DIGITAL | IOD_STR | STR:.PrenosUrnika[58]
STRPrenosUrnika59 | DIGITAL | IOD_STR | STR:.PrenosUrnika[59]
STRPrenosUrnika60 | DIGITAL | IOD_STR | STR:.PrenosUrnika[60]
STRPrenosUrnika61 | DIGITAL | IOD_STR | STR:.PrenosUrnika[61]
STRPrenosUrnika62 | DIGITAL | IOD_STR | STR:.PrenosUrnika[62]
STRPrenosUrnika63 | DIGITAL | IOD_STR | STR:.PrenosUrnika[63]
STRPrenosUrnika64 | DIGITAL | IOD_STR | STR:.PrenosUrnika[64]
STRPrenosUrnika65 | DIGITAL | IOD_STR | STR:.PrenosUrnika[65]
STRPrenosUrnika66 | DIGITAL | IOD_STR | STR:.PrenosUrnika[66]
STRPrenosUrnika67 | DIGITAL | IOD_STR | STR:.PrenosUrnika[67]
STRPrenosUrnika68 | DIGITAL | IOD_STR | STR:.PrenosUrnika[68]
STRPrenosUrnika69 | DIGITAL | IOD_STR | STR:.PrenosUrnika[69]
STRPrenosUrnika70 | DIGITAL | IOD_STR | STR:.PrenosUrnika[70]
STRPrenosUrnika71 | DIGITAL | IOD_STR | STR:.PrenosUrnika[71]
STRPrenosUrnika72 | DIGITAL | IOD_STR | STR:.PrenosUrnika[72]
STRPrenosUrnika73 | DIGITAL | IOD_STR | STR:.PrenosUrnika[73]
STRPrenosUrnika74 | DIGITAL | IOD_STR | STR:.PrenosUrnika[74]
STRPrenosUrnika75 | DIGITAL | IOD_STR | STR:.PrenosUrnika[75]
STRPrenosUrnika76 | DIGITAL | IOD_STR | STR:.PrenosUrnika[76]
STRPrenosUrnika77 | DIGITAL | IOD_STR | STR:.PrenosUrnika[77]
STRPrenosUrnika78 | DIGITAL | IOD_STR | STR:.PrenosUrnika[78]
STRPrenosUrnika79 | DIGITAL | IOD_STR | STR:.PrenosUrnika[79]
STRPrenosUrnika80 | DIGITAL | IOD_STR | STR:.PrenosUrnika[80]
STRPrenosUrnika81 | DIGITAL | IOD_STR | STR:.PrenosUrnika[81]
STRPrenosUrnika82 | DIGITAL | IOD_STR | STR:.PrenosUrnika[82]
STRPrenosUrnika83 | DIGITAL | IOD_STR | STR:.PrenosUrnika[83]
STRPrenosUrnika84 | DIGITAL | IOD_STR | STR:.PrenosUrnika[84]
STRPrenosUrnika85 | DIGITAL | IOD_STR | STR:.PrenosUrnika[85]
STRPrenosUrnika86 | DIGITAL | IOD_STR | STR:.PrenosUrnika[86]
STRPrenosUrnika87 | DIGITAL | IOD_STR | STR:.PrenosUrnika[87]
STRPrenosUrnika88 | DIGITAL | IOD_STR | STR:.PrenosUrnika[88]
STRPrenosUrnika89 | DIGITAL | IOD_STR | STR:.PrenosUrnika[89]
STRPrenosUrnika90 | DIGITAL | IOD_STR | STR:.PrenosUrnika[90]
STRPrenosUrnika91 | DIGITAL | IOD_STR | STR:.PrenosUrnika[91]
STRPrenosUrnika92 | DIGITAL | IOD_STR | STR:.PrenosUrnika[92]
STRPrenosUrnika93 | DIGITAL | IOD_STR | STR:.PrenosUrnika[93]
STRPrenosUrnika94 | DIGITAL | IOD_STR | STR:.PrenosUrnika[94]
STRPrenosUrnika95 | DIGITAL | IOD_STR | STR:.PrenosUrnika[95]
STRPrenosUrnika96 | DIGITAL | IOD_STR | STR:.PrenosUrnika[96]
STRRazsvRocnoEnaLuc10 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[10]
STRRazsvRocnoEnaLuc11 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[11]
STRRazsvRocnoEnaLuc12 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[12]
STRRazsvRocnoEnaLuc13 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[13]
STRRazsvRocnoEnaLuc14 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[14]
STRRazsvRocnoEnaLuc15 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[15]
STRRazsvRocnoEnaLuc16 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[16]
STRRazsvRocnoEnaLuc17 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[17]
STRRazsvRocnoEnaLuc18 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[18]
STRRazsvRocnoEnaLuc19 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[19]
STRRazsvRocnoEnaLuc1 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[1]
STRRazsvRocnoEnaLuc20 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[20]
STRRazsvRocnoEnaLuc21 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[21]
STRRazsvRocnoEnaLuc22 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[22]
STRRazsvRocnoEnaLuc23 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[23]
STRRazsvRocnoEnaLuc24 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[24]
STRRazsvRocnoEnaLuc25 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[25]
STRRazsvRocnoEnaLuc2 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[2]
STRRazsvRocnoEnaLuc3 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[3]
STRRazsvRocnoEnaLuc4 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[4]
STRRazsvRocnoEnaLuc5 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[5]
STRRazsvRocnoEnaLuc6 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[6]
STRRazsvRocnoEnaLuc7 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[7]
STRRazsvRocnoEnaLuc8 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[8]
STRRazsvRocnoEnaLuc9 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[9]
STRUrnikSaveDan1Off1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[1].Off[1].Mna | BYTE
STRUrnikSaveDan1Off1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[1].Off[1].Ura | BYTE
STRUrnikSaveDan1Off2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[1].Off[2].Mna | BYTE
STRUrnikSaveDan1Off2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[1].Off[2].Ura | BYTE
STRUrnikSaveDan1Off3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[1].Off[3].Mna | BYTE
STRUrnikSaveDan1Off3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[1].Off[3].Ura | BYTE
STRUrnikSaveDan1On1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[1].On[1].Mna | BYTE
STRUrnikSaveDan1On1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[1].On[1].Ura | BYTE
STRUrnikSaveDan1On2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[1].On[2].Mna | BYTE
STRUrnikSaveDan1On2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[1].On[2].Ura | BYTE
STRUrnikSaveDan1On3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[1].On[3].Mna | BYTE
STRUrnikSaveDan1On3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[1].On[3].Ura | BYTE
STRUrnikSaveDan2Off1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[2].Off[1].Mna | BYTE
STRUrnikSaveDan2Off1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[2].Off[1].Ura | BYTE
STRUrnikSaveDan2Off2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[2].Off[2].Mna | BYTE
STRUrnikSaveDan2Off2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[2].Off[2].Ura | BYTE
STRUrnikSaveDan2Off3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[2].Off[3].Mna | BYTE
STRUrnikSaveDan2Off3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[2].Off[3].Ura | BYTE
STRUrnikSaveDan2On1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[2].On[1].Mna | BYTE
STRUrnikSaveDan2On1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[2].On[1].Ura | BYTE
STRUrnikSaveDan2On2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[2].On[2].Mna | BYTE
STRUrnikSaveDan2On2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[2].On[2].Ura | BYTE
STRUrnikSaveDan2On3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[2].On[3].Mna | BYTE
STRUrnikSaveDan2On3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[2].On[3].Ura | BYTE
STRUrnikSaveDan3Off1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[3].Off[1].Mna | BYTE
STRUrnikSaveDan3Off1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[3].Off[1].Ura | BYTE
STRUrnikSaveDan3Off2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[3].Off[2].Mna | BYTE
STRUrnikSaveDan3Off2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[3].Off[2].Ura | BYTE
STRUrnikSaveDan3Off3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[3].Off[3].Mna | BYTE
STRUrnikSaveDan3Off3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[3].Off[3].Ura | BYTE
STRUrnikSaveDan3On1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[3].On[1].Mna | BYTE
STRUrnikSaveDan3On1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[3].On[1].Ura | BYTE
STRUrnikSaveDan3On2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[3].On[2].Mna | BYTE
STRUrnikSaveDan3On2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[3].On[2].Ura | BYTE
STRUrnikSaveDan3On3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[3].On[3].Mna | BYTE
STRUrnikSaveDan3On3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[3].On[3].Ura | BYTE
STRUrnikSaveDan4Off1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[4].Off[1].Mna | BYTE
STRUrnikSaveDan4Off1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[4].Off[1].Ura | BYTE
STRUrnikSaveDan4Off2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[4].Off[2].Mna | BYTE
STRUrnikSaveDan4Off2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[4].Off[2].Ura | BYTE
STRUrnikSaveDan4Off3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[4].Off[3].Mna | BYTE
STRUrnikSaveDan4Off3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[4].Off[3].Ura | BYTE
STRUrnikSaveDan4On1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[4].On[1].Mna | BYTE
STRUrnikSaveDan4On1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[4].On[1].Ura | BYTE
STRUrnikSaveDan4On2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[4].On[2].Mna | BYTE
STRUrnikSaveDan4On2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[4].On[2].Ura | BYTE
STRUrnikSaveDan4On3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[4].On[3].Mna | BYTE
STRUrnikSaveDan4On3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[4].On[3].Ura | BYTE
STRUrnikSaveDan5Off1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[5].Off[1].Mna | BYTE
STRUrnikSaveDan5Off1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[5].Off[1].Ura | BYTE
STRUrnikSaveDan5Off2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[5].Off[2].Mna | BYTE
STRUrnikSaveDan5Off2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[5].Off[2].Ura | BYTE
STRUrnikSaveDan5Off3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[5].Off[3].Mna | BYTE
STRUrnikSaveDan5Off3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[5].Off[3].Ura | BYTE
STRUrnikSaveDan5On1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[5].On[1].Mna | BYTE
STRUrnikSaveDan5On1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[5].On[1].Ura | BYTE
STRUrnikSaveDan5On2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[5].On[2].Mna | BYTE
STRUrnikSaveDan5On2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[5].On[2].Ura | BYTE
STRUrnikSaveDan5On3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[5].On[3].Mna | BYTE
STRUrnikSaveDan5On3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[5].On[3].Ura | BYTE
STRUrnikSaveDan6Off1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[6].Off[1].Mna | BYTE
STRUrnikSaveDan6Off1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[6].Off[1].Ura | BYTE
STRUrnikSaveDan6Off2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[6].Off[2].Mna | BYTE
STRUrnikSaveDan6Off2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[6].Off[2].Ura | BYTE
STRUrnikSaveDan6Off3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[6].Off[3].Mna | BYTE
STRUrnikSaveDan6Off3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[6].Off[3].Ura | BYTE
STRUrnikSaveDan6On1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[6].On[1].Mna | BYTE
STRUrnikSaveDan6On1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[6].On[1].Ura | BYTE
STRUrnikSaveDan6On2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[6].On[2].Mna | BYTE
STRUrnikSaveDan6On2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[6].On[2].Ura | BYTE
STRUrnikSaveDan6On3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[6].On[3].Mna | BYTE
STRUrnikSaveDan6On3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[6].On[3].Ura | BYTE
STRUrnikSaveDan7Off1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[7].Off[1].Mna | BYTE
STRUrnikSaveDan7Off1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[7].Off[1].Ura | BYTE
STRUrnikSaveDan7Off2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[7].Off[2].Mna | BYTE
STRUrnikSaveDan7Off2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[7].Off[2].Ura | BYTE
STRUrnikSaveDan7Off3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[7].Off[3].Mna | BYTE
STRUrnikSaveDan7Off3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[7].Off[3].Ura | BYTE
STRUrnikSaveDan7On1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[7].On[1].Mna | BYTE
STRUrnikSaveDan7On1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[7].On[1].Ura | BYTE
STRUrnikSaveDan7On2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[7].On[2].Mna | BYTE
STRUrnikSaveDan7On2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[7].On[2].Ura | BYTE
STRUrnikSaveDan7On3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[7].On[3].Mna | BYTE
STRUrnikSaveDan7On3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[7].On[3].Ura | BYTE
STRValAI_TempTB5 | REAL | IOD_STR | STR:.ValAI_TempTB5
STRXVH_CircNumber | INT | IOD_STR | STR:.XVH_CircNumber | BYTE
STRXVH_CrpalkaGrfsPair | DIGITAL | IOD_STR | STR:.XVH_CrpalkaGrfsPair
STRXVH_CrpGrfsCommErr | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsCommErr
STRXVH_CrpGrfsON10 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[10]
STRXVH_CrpGrfsON11 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[11]
STRXVH_CrpGrfsON12 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[12]
STRXVH_CrpGrfsON13 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[13]
STRXVH_CrpGrfsON14 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[14]
STRXVH_CrpGrfsON1 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[1]
STRXVH_CrpGrfsON2 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[2]
STRXVH_CrpGrfsON3 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[3]
STRXVH_CrpGrfsON4 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[4]
STRXVH_CrpGrfsON5 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[5]
STRXVH_CrpGrfsON6 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[6]
STRXVH_CrpGrfsON7 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[7]
STRXVH_CrpGrfsON8 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[8]
STRXVH_CrpGrfsON9 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[9]
STRXVH_CrpGrfsPIDreset | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsPIDreset
STRXVH_CrpGrfsVisibleData10 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[10]
STRXVH_CrpGrfsVisibleData11 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[11]
STRXVH_CrpGrfsVisibleData12 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[12]
STRXVH_CrpGrfsVisibleData13 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[13]
STRXVH_CrpGrfsVisibleData14 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[14]
STRXVH_CrpGrfsVisibleData15 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[15]
STRXVH_CrpGrfsVisibleData16 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[16]
STRXVH_CrpGrfsVisibleData1 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[1]
STRXVH_CrpGrfsVisibleData2 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[2]
STRXVH_CrpGrfsVisibleData3 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[3]
STRXVH_CrpGrfsVisibleData4 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[4]
STRXVH_CrpGrfsVisibleData5 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[5]
STRXVH_CrpGrfsVisibleData6 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[6]
STRXVH_CrpGrfsVisibleData7 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[7]
STRXVH_CrpGrfsVisibleData8 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[8]
STRXVH_CrpGrfsVisibleData9 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[9]
STRXVH_CrpGrundfosNaCas | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosNaCas
STRXVH_CrpGrundfosNaTlak | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosNaTlak
STRXVH_CrpGrundfosON | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosON
STRXVH_CrpGrundfosResetAlarm | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosResetAlarm
STRXVH_CrpGrundfosResetAlarmLog | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosResetAlarmLog
STRXVH_CrpGrundfosSetRef | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosSetRef
STRXVH_CrpGrundfosTlakSP | REAL | IOD_STR | STR:.XVH_CrpGrundfosTlakSP
STRXVH_GrafTemp1 | REAL | IOD_STR | STR:.XVH_GrafTemp[1]
STRXVH_GrafTemp2 | REAL | IOD_STR | STR:.XVH_GrafTemp[2]
STRXVH_GrafTemp3 | REAL | IOD_STR | STR:.XVH_GrafTemp[3]
STRXVH_GrafTemp4 | REAL | IOD_STR | STR:.XVH_GrafTemp[4]
STRXVH_GrafTemp5 | REAL | IOD_STR | STR:.XVH_GrafTemp[5]
STRXVH_GrafVlaga1 | REAL | IOD_STR | STR:.XVH_GrafVlaga[1]
STRXVH_GrafVlaga2 | REAL | IOD_STR | STR:.XVH_GrafVlaga[2]
STRXVH_GrafVlaga3 | REAL | IOD_STR | STR:.XVH_GrafVlaga[3]
STRXVH_GrafVlaga4 | REAL | IOD_STR | STR:.XVH_GrafVlaga[4]
STRXVH_GrafVlaga5 | REAL | IOD_STR | STR:.XVH_GrafVlaga[5]
STRXVH_KompStatus1 | INT | IOD_STR | STR:.XVH_KompStatus[1] | BYTE
STRXVH_KompStatus2 | INT | IOD_STR | STR:.XVH_KompStatus[2] | BYTE
STRXVH_RazsvOnOff | DIGITAL | IOD_STR | STR:.XVH_RazsvOnOff
STRXVH_ReferencaUpper | INT | IOD_STR | STR:.XVH_ReferencaUpper
STRXVH_setCircNum1 | DIGITAL | IOD_STR | STR:.XVH_setCircNum[1]
STRXVH_setCircNum2 | DIGITAL | IOD_STR | STR:.XVH_setCircNum[2]
STRXVH_setCircNum3 | DIGITAL | IOD_STR | STR:.XVH_setCircNum[3]
STRXVH_setCircNum4 | DIGITAL | IOD_STR | STR:.XVH_setCircNum[4]
STRXVH_setCircNum5 | DIGITAL | IOD_STR | STR:.XVH_setCircNum[5]
STRXVH_TlakSenzor | REAL | IOD_STR | STR:.XVH_TlakSenzor
STRXVH_UPSstatus | INT | IOD_STR | STR:.XVH_UPSstatus | BYTE
STRXVH_UrnikDan1Off1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[1].Mna | BYTE
STRXVH_UrnikDan1Off1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[1].Ura | BYTE
STRXVH_UrnikDan1Off2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[2].Mna | BYTE
STRXVH_UrnikDan1Off2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[2].Ura | BYTE
STRXVH_UrnikDan1Off3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[3].Mna | BYTE
STRXVH_UrnikDan1Off3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[3].Ura | BYTE
STRXVH_UrnikDan1On1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].On[1].Mna | BYTE
STRXVH_UrnikDan1On1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].On[1].Ura | BYTE
STRXVH_UrnikDan1On2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].On[2].Mna | BYTE
STRXVH_UrnikDan1On2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].On[2].Ura | BYTE
STRXVH_UrnikDan1On3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].On[3].Mna | BYTE
STRXVH_UrnikDan1On3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].On[3].Ura | BYTE
STRXVH_UrnikDan2Off1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[1].Mna | BYTE
STRXVH_UrnikDan2Off1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[1].Ura | BYTE
STRXVH_UrnikDan2Off2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[2].Mna | BYTE
STRXVH_UrnikDan2Off2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[2].Ura | BYTE
STRXVH_UrnikDan2Off3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[3].Mna | BYTE
STRXVH_UrnikDan2Off3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[3].Ura | BYTE
STRXVH_UrnikDan2On1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].On[1].Mna | BYTE
STRXVH_UrnikDan2On1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].On[1].Ura | BYTE
STRXVH_UrnikDan2On2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].On[2].Mna | BYTE
STRXVH_UrnikDan2On2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].On[2].Ura | BYTE
STRXVH_UrnikDan2On3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].On[3].Mna | BYTE
STRXVH_UrnikDan2On3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].On[3].Ura | BYTE
STRXVH_UrnikDan3Off1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[1].Mna | BYTE
STRXVH_UrnikDan3Off1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[1].Ura | BYTE
STRXVH_UrnikDan3Off2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[2].Mna | BYTE
STRXVH_UrnikDan3Off2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[2].Ura | BYTE
STRXVH_UrnikDan3Off3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[3].Mna | BYTE
STRXVH_UrnikDan3Off3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[3].Ura | BYTE
STRXVH_UrnikDan3On1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].On[1].Mna | BYTE
STRXVH_UrnikDan3On1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].On[1].Ura | BYTE
STRXVH_UrnikDan3On2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].On[2].Mna | BYTE
STRXVH_UrnikDan3On2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].On[2].Ura | BYTE
STRXVH_UrnikDan3On3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].On[3].Mna | BYTE
STRXVH_UrnikDan3On3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].On[3].Ura | BYTE
STRXVH_UrnikDan4Off1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[1].Mna | BYTE
STRXVH_UrnikDan4Off1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[1].Ura | BYTE
STRXVH_UrnikDan4Off2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[2].Mna | BYTE
STRXVH_UrnikDan4Off2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[2].Ura | BYTE
STRXVH_UrnikDan4Off3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[3].Mna | BYTE
STRXVH_UrnikDan4Off3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[3].Ura | BYTE
STRXVH_UrnikDan4On1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].On[1].Mna | BYTE
STRXVH_UrnikDan4On1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].On[1].Ura | BYTE
STRXVH_UrnikDan4On2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].On[2].Mna | BYTE
STRXVH_UrnikDan4On2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].On[2].Ura | BYTE
STRXVH_UrnikDan4On3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].On[3].Mna | BYTE
STRXVH_UrnikDan4On3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].On[3].Ura | BYTE
STRXVH_UrnikDan5Off1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[1].Mna | BYTE
STRXVH_UrnikDan5Off1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[1].Ura | BYTE
STRXVH_UrnikDan5Off2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[2].Mna | BYTE
STRXVH_UrnikDan5Off2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[2].Ura | BYTE
STRXVH_UrnikDan5Off3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[3].Mna | BYTE
STRXVH_UrnikDan5Off3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[3].Ura | BYTE
STRXVH_UrnikDan5On1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].On[1].Mna | BYTE
STRXVH_UrnikDan5On1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].On[1].Ura | BYTE
STRXVH_UrnikDan5On2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].On[2].Mna | BYTE
STRXVH_UrnikDan5On2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].On[2].Ura | BYTE
STRXVH_UrnikDan5On3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].On[3].Mna | BYTE
STRXVH_UrnikDan5On3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].On[3].Ura | BYTE
STRXVH_UrnikDan6Off1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[1].Mna | BYTE
STRXVH_UrnikDan6Off1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[1].Ura | BYTE
STRXVH_UrnikDan6Off2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[2].Mna | BYTE
STRXVH_UrnikDan6Off2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[2].Ura | BYTE
STRXVH_UrnikDan6Off3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[3].Mna | BYTE
STRXVH_UrnikDan6Off3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[3].Ura | BYTE
STRXVH_UrnikDan6On1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].On[1].Mna | BYTE
STRXVH_UrnikDan6On1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].On[1].Ura | BYTE
STRXVH_UrnikDan6On2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].On[2].Mna | BYTE
STRXVH_UrnikDan6On2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].On[2].Ura | BYTE
STRXVH_UrnikDan6On3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].On[3].Mna | BYTE
STRXVH_UrnikDan6On3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].On[3].Ura | BYTE
STRXVH_UrnikDan7Off1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[1].Mna | BYTE
STRXVH_UrnikDan7Off1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[1].Ura | BYTE
STRXVH_UrnikDan7Off2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[2].Mna | BYTE
STRXVH_UrnikDan7Off2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[2].Ura | BYTE
STRXVH_UrnikDan7Off3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[3].Mna | BYTE
STRXVH_UrnikDan7Off3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[3].Ura | BYTE
STRXVH_UrnikDan7On1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].On[1].Mna | BYTE
STRXVH_UrnikDan7On1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].On[1].Ura | BYTE
STRXVH_UrnikDan7On2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].On[2].Mna | BYTE
STRXVH_UrnikDan7On2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].On[2].Ura | BYTE
STRXVH_UrnikDan7On3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].On[3].Mna | BYTE
STRXVH_UrnikDan7On3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].On[3].Ura | BYTE
STRXVH_UrnikNalozi | DIGITAL | IOD_STR | STR:.XVH_UrnikNalozi
STRXVH_UrnikNonStop | DIGITAL | IOD_STR | STR:.XVH_UrnikNonStop
STRXVH_UrnikPotrdiVpis | DIGITAL | IOD_STR | STR:.XVH_UrnikPotrdiVpis
STRXVH_UrnikPreklicVpisa | DIGITAL | IOD_STR | STR:.XVH_UrnikPreklicVpisa
STRXVH_UrnikShrani | DIGITAL | IOD_STR | STR:.XVH_UrnikShrani
STRXVH_VentilTYValue11 | INT | IOD_STR | STR:.XVH_VentilTYValue[1,1] | BYTE
STRXVH_VentilTYValue12 | INT | IOD_STR | STR:.XVH_VentilTYValue[1,2] | BYTE
STRXVH_VentilTYValue21 | INT | IOD_STR | STR:.XVH_VentilTYValue[2,1] | BYTE
STRXVH_VentilTYValue22 | INT | IOD_STR | STR:.XVH_VentilTYValue[2,2] | BYTE
STRXVH_VentilTYValue31 | INT | IOD_STR | STR:.XVH_VentilTYValue[3,1] | BYTE
STRXVH_VentilTYValue32 | INT | IOD_STR | STR:.XVH_VentilTYValue[3,2] | BYTE
STRXVH_VentilTYValue41 | INT | IOD_STR | STR:.XVH_VentilTYValue[4,1] | BYTE
STRXVH_VentilTYValue42 | INT | IOD_STR | STR:.XVH_VentilTYValue[4,2] | BYTE
STRXVH_VlazilecStatus1 | INT | IOD_STR | STR:.XVH_VlazilecStatus[1] | BYTE
STRXVH_VlazilecStatus2 | INT | IOD_STR | STR:.XVH_VlazilecStatus[2] | BYTE
STRXVH_VpisUrnika | DIGITAL | IOD_STR | STR:.XVH_VpisUrnika
STRXVHnum10 | INT | IOD_STR | STR:.XVHnum[10] | BYTE
STRXVHnum11 | INT | IOD_STR | STR:.XVHnum[11] | BYTE
STRXVHnum12 | INT | IOD_STR | STR:.XVHnum[12] | BYTE
STRXVHnum13 | INT | IOD_STR | STR:.XVHnum[13] | BYTE
STRXVHnum14 | INT | IOD_STR | STR:.XVHnum[14] | BYTE
STRXVHnum1 | INT | IOD_STR | STR:.XVHnum[1] | BYTE
STRXVHnum2 | INT | IOD_STR | STR:.XVHnum[2] | BYTE
STRXVHnum3 | INT | IOD_STR | STR:.XVHnum[3] | BYTE
STRXVHnum4 | INT | IOD_STR | STR:.XVHnum[4] | BYTE
STRXVHnum5 | INT | IOD_STR | STR:.XVHnum[5] | BYTE
STRXVHnum6 | INT | IOD_STR | STR:.XVHnum[6] | BYTE
STRXVHnum7 | INT | IOD_STR | STR:.XVHnum[7] | BYTE
STRXVHnum8 | INT | IOD_STR | STR:.XVHnum[8] | BYTE
STRXVHnum9 | INT | IOD_STR | STR:.XVHnum[9] | BYTE
STRErrCommScada2 | DIGITAL | IOD_STR | STR:.ErrCommScada2
STRComSCADA2 | DIGITAL | IOD_STR | STR:.ComSCADA2
STRComSCADA3 | DIGITAL | IOD_STR | STR:.ComSCADA3
STRkom_nast_cas_izpada | UINT | IOD_STR | STR:.kom_nast_cas_izpada
STRCirc1MaximumDemandA2 | REAL | IOD_STR | STR:.Circ[1].MaximumDemandA2
STRCirc1MaximumDemandA3 | REAL | IOD_STR | STR:.Circ[1].MaximumDemandA3
STRCirc1RazEner_D_SCADA | REAL | IOD_STR | STR:.Circ[1].RazEner_D_SCADA
STRCirc1RazEner_T_SCADA | REAL | IOD_STR | STR:.Circ[1].RazEner_T_SCADA
STRCirc1RazEner_M_SCADA | REAL | IOD_STR | STR:.Circ[1].RazEner_M_SCADA
STRCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Dnevne_energija_scada1
STRCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Dnevne_energija_scada2
STRCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Tedenska_energija_scada1
STRCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Tedenska_energija_scada2
STRCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Mesecna_energija_scada1
STRCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Mesecna_energija_scada2

## variable_2
STRAkumSanVodeTE1OnOff | DIGITAL | IOD_STR | STR:.AkumSanVodeTE1OnOff
STRAlarmGenCirc1 | DIGITAL | IOD_STR | STR:.AlarmGenCirc1
STRAlarmGenComm | DIGITAL | IOD_STR | STR:.AlarmGenComm
STRAlarmGenDI | DIGITAL | IOD_STR | STR:.AlarmGenDI
STRAlarmGenHladPost | DIGITAL | IOD_STR | STR:.AlarmGenHladPost
STRAlarmGenKlima1 | DIGITAL | IOD_STR | STR:.AlarmGenKlima1
STRAlarmGenKlima2 | DIGITAL | IOD_STR | STR:.AlarmGenKlima2
STRAlarmGenLopute | DIGITAL | IOD_STR | STR:.AlarmGenLopute
STRAlarmGenRest | DIGITAL | IOD_STR | STR:.AlarmGenRest
STRAlarmGenSenzor | DIGITAL | IOD_STR | STR:.AlarmGenSenzor
STRAlarmGenTemp | DIGITAL | IOD_STR | STR:.AlarmGenTemp
STRAlarmGenToplPost | DIGITAL | IOD_STR | STR:.AlarmGenToplPost
STRAlarmGenVent | DIGITAL | IOD_STR | STR:.AlarmGenVent
STRAlarmGenVTV | DIGITAL | IOD_STR | STR:.AlarmGenVTV
STRATVTempPrenizka | DIGITAL | IOD_STR | STR:.ATVTempPrenizka
STRComSCADA | DIGITAL | IOD_STR | STR:.ComSCADA
STRComSCADA1 | DIGITAL | IOD_STR | STR:.ComSCADA1
STRCrpalkaMN1OnOff | DIGITAL | IOD_STR | STR:.CrpalkaMN1OnOff
STRCrpalkaTm11TM12OnOff | DIGITAL | IOD_STR | STR:.CrpalkaTm11TM12OnOff
STRCrpalkeDnfs1AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].AlarmAktiven
STRCrpalkeDnfs1Deluje | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].Deluje
STRCrpalkeDnfs1QuickStop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].QuickStop
STRCrpalkeDnfs1RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].RemoteON
STRCrpalkeDnfs1Reset | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].Reset
STRCrpalkeDnfs1Start | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].Start
STRCrpalkeDnfs1Stop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[1].Stop
STRCrpalkeDnfs2AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].AlarmAktiven
STRCrpalkeDnfs2Deluje | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].Deluje
STRCrpalkeDnfs2QuickStop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].QuickStop
STRCrpalkeDnfs2RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].RemoteON
STRCrpalkeDnfs2Reset | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].Reset
STRCrpalkeDnfs2Start | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].Start
STRCrpalkeDnfs2Stop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[2].Stop
STRCrpalkeDnfs3AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].AlarmAktiven
STRCrpalkeDnfs3Deluje | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].Deluje
STRCrpalkeDnfs3QuickStop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].QuickStop
STRCrpalkeDnfs3RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].RemoteON
STRCrpalkeDnfs3Reset | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].Reset
STRCrpalkeDnfs3Start | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].Start
STRCrpalkeDnfs3Stop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[3].Stop
STRCrpalkeDnfs4AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].AlarmAktiven
STRCrpalkeDnfs4Deluje | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].Deluje
STRCrpalkeDnfs4QuickStop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].QuickStop
STRCrpalkeDnfs4RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].RemoteON
STRCrpalkeDnfs4Reset | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].Reset
STRCrpalkeDnfs4Start | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].Start
STRCrpalkeDnfs4Stop | DIGITAL | IOD_STR | STR:.CrpalkeDnfs[4].Stop
STRCrpalkeGrfs10AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].AlarmAktiven
STRCrpalkeGrfs10Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].Deluje
STRCrpalkeGrfs10LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].LocalMode
STRCrpalkeGrfs10RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].RemoteON
STRCrpalkeGrfs10Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].Reset2handkWhValues
STRCrpalkeGrfs10ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].ResetAlarm
STRCrpalkeGrfs10ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].ResetAlarmLog
STRCrpalkeGrfs10ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].ResetDevice
STRCrpalkeGrfs10SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetAutomatic
STRCrpalkeGrfs10SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetConstFreqMode
STRCrpalkeGrfs10SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetConstPress
STRCrpalkeGrfs10SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetLocalMode
STRCrpalkeGrfs10SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetMaxRunMode
STRCrpalkeGrfs10SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetMinRunMode
STRCrpalkeGrfs10SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetPropPress
STRCrpalkeGrfs10SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetReference
STRCrpalkeGrfs10SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetRemoteMode
STRCrpalkeGrfs10SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetTwinModeAlt
STRCrpalkeGrfs10SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetTwinModeSpare
STRCrpalkeGrfs10SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].SetTwinModeSync
STRCrpalkeGrfs10Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].Start
STRCrpalkeGrfs10Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[10].Stop
STRCrpalkeGrfs11AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].AlarmAktiven
STRCrpalkeGrfs11Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].Deluje
STRCrpalkeGrfs11LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].LocalMode
STRCrpalkeGrfs11RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].RemoteON
STRCrpalkeGrfs11Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].Reset2handkWhValues
STRCrpalkeGrfs11ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].ResetAlarm
STRCrpalkeGrfs11ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].ResetAlarmLog
STRCrpalkeGrfs11ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].ResetDevice
STRCrpalkeGrfs11SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetAutomatic
STRCrpalkeGrfs11SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetConstFreqMode
STRCrpalkeGrfs11SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetConstPress
STRCrpalkeGrfs11SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetLocalMode
STRCrpalkeGrfs11SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetMaxRunMode
STRCrpalkeGrfs11SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetMinRunMode
STRCrpalkeGrfs11SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetPropPress
STRCrpalkeGrfs11SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetReference
STRCrpalkeGrfs11SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetRemoteMode
STRCrpalkeGrfs11SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetTwinModeAlt
STRCrpalkeGrfs11SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetTwinModeSpare
STRCrpalkeGrfs11SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].SetTwinModeSync
STRCrpalkeGrfs11Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].Start
STRCrpalkeGrfs11Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[11].Stop
STRCrpalkeGrfs12AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].AlarmAktiven
STRCrpalkeGrfs12Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].Deluje
STRCrpalkeGrfs12LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].LocalMode
STRCrpalkeGrfs12RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].RemoteON
STRCrpalkeGrfs12Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].Reset2handkWhValues
STRCrpalkeGrfs12ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].ResetAlarm
STRCrpalkeGrfs12ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].ResetAlarmLog
STRCrpalkeGrfs12ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].ResetDevice
STRCrpalkeGrfs12SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetAutomatic
STRCrpalkeGrfs12SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetConstFreqMode
STRCrpalkeGrfs12SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetConstPress
STRCrpalkeGrfs12SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetLocalMode
STRCrpalkeGrfs12SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetMaxRunMode
STRCrpalkeGrfs12SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetMinRunMode
STRCrpalkeGrfs12SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetPropPress
STRCrpalkeGrfs12SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetReference
STRCrpalkeGrfs12SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetRemoteMode
STRCrpalkeGrfs12SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetTwinModeAlt
STRCrpalkeGrfs12SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetTwinModeSpare
STRCrpalkeGrfs12SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].SetTwinModeSync
STRCrpalkeGrfs12Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].Start
STRCrpalkeGrfs12Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[12].Stop
STRCrpalkeGrfs13AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].AlarmAktiven
STRCrpalkeGrfs13Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].Deluje
STRCrpalkeGrfs13LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].LocalMode
STRCrpalkeGrfs13RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].RemoteON
STRCrpalkeGrfs13Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].Reset2handkWhValues
STRCrpalkeGrfs13ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].ResetAlarm
STRCrpalkeGrfs13ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].ResetAlarmLog
STRCrpalkeGrfs13ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].ResetDevice
STRCrpalkeGrfs13SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetAutomatic
STRCrpalkeGrfs13SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetConstFreqMode
STRCrpalkeGrfs13SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetConstPress
STRCrpalkeGrfs13SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetLocalMode
STRCrpalkeGrfs13SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetMaxRunMode
STRCrpalkeGrfs13SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetMinRunMode
STRCrpalkeGrfs13SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetPropPress
STRCrpalkeGrfs13SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetReference
STRCrpalkeGrfs13SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetRemoteMode
STRCrpalkeGrfs13SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetTwinModeAlt
STRCrpalkeGrfs13SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetTwinModeSpare
STRCrpalkeGrfs13SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].SetTwinModeSync
STRCrpalkeGrfs13Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].Start
STRCrpalkeGrfs13Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[13].Stop
STRCrpalkeGrfs14AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].AlarmAktiven
STRCrpalkeGrfs14Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].Deluje
STRCrpalkeGrfs14LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].LocalMode
STRCrpalkeGrfs14RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].RemoteON
STRCrpalkeGrfs14Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].Reset2handkWhValues
STRCrpalkeGrfs14ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].ResetAlarm
STRCrpalkeGrfs14ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].ResetAlarmLog
STRCrpalkeGrfs14ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].ResetDevice
STRCrpalkeGrfs14SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetAutomatic
STRCrpalkeGrfs14SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetConstFreqMode
STRCrpalkeGrfs14SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetConstPress
STRCrpalkeGrfs14SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetLocalMode
STRCrpalkeGrfs14SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetMaxRunMode
STRCrpalkeGrfs14SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetMinRunMode
STRCrpalkeGrfs14SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetPropPress
STRCrpalkeGrfs14SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetReference
STRCrpalkeGrfs14SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetRemoteMode
STRCrpalkeGrfs14SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetTwinModeAlt
STRCrpalkeGrfs14SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetTwinModeSpare
STRCrpalkeGrfs14SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].SetTwinModeSync
STRCrpalkeGrfs14Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].Start
STRCrpalkeGrfs14Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[14].Stop
STRCrpalkeGrfs1AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].AlarmAktiven
STRCrpalkeGrfs1Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].Deluje
STRCrpalkeGrfs1LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].LocalMode
STRCrpalkeGrfs1RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].RemoteON
STRCrpalkeGrfs1Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].Reset2handkWhValues
STRCrpalkeGrfs1ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].ResetAlarm
STRCrpalkeGrfs1ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].ResetAlarmLog
STRCrpalkeGrfs1ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].ResetDevice
STRCrpalkeGrfs1SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetAutomatic
STRCrpalkeGrfs1SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetConstFreqMode
STRCrpalkeGrfs1SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetConstPress
STRCrpalkeGrfs1SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetLocalMode
STRCrpalkeGrfs1SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetMaxRunMode
STRCrpalkeGrfs1SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetMinRunMode
STRCrpalkeGrfs1SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetPropPress
STRCrpalkeGrfs1SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetReference
STRCrpalkeGrfs1SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetRemoteMode
STRCrpalkeGrfs1SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetTwinModeAlt
STRCrpalkeGrfs1SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetTwinModeSpare
STRCrpalkeGrfs1SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].SetTwinModeSync
STRCrpalkeGrfs1Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].Start
STRCrpalkeGrfs1Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[1].Stop
STRCrpalkeGrfs2AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].AlarmAktiven
STRCrpalkeGrfs2Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].Deluje
STRCrpalkeGrfs2LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].LocalMode
STRCrpalkeGrfs2RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].RemoteON
STRCrpalkeGrfs2Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].Reset2handkWhValues
STRCrpalkeGrfs2ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].ResetAlarm
STRCrpalkeGrfs2ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].ResetAlarmLog
STRCrpalkeGrfs2ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].ResetDevice
STRCrpalkeGrfs2SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetAutomatic
STRCrpalkeGrfs2SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetConstFreqMode
STRCrpalkeGrfs2SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetConstPress
STRCrpalkeGrfs2SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetLocalMode
STRCrpalkeGrfs2SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetMaxRunMode
STRCrpalkeGrfs2SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetMinRunMode
STRCrpalkeGrfs2SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetPropPress
STRCrpalkeGrfs2SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetReference
STRCrpalkeGrfs2SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetRemoteMode
STRCrpalkeGrfs2SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetTwinModeAlt
STRCrpalkeGrfs2SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetTwinModeSpare
STRCrpalkeGrfs2SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].SetTwinModeSync
STRCrpalkeGrfs2Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].Start
STRCrpalkeGrfs2Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[2].Stop
STRCrpalkeGrfs3AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].AlarmAktiven
STRCrpalkeGrfs3Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].Deluje
STRCrpalkeGrfs3LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].LocalMode
STRCrpalkeGrfs3RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].RemoteON
STRCrpalkeGrfs3Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].Reset2handkWhValues
STRCrpalkeGrfs3ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].ResetAlarm
STRCrpalkeGrfs3ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].ResetAlarmLog
STRCrpalkeGrfs3ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].ResetDevice
STRCrpalkeGrfs3SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetAutomatic
STRCrpalkeGrfs3SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetConstFreqMode
STRCrpalkeGrfs3SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetConstPress
STRCrpalkeGrfs3SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetLocalMode
STRCrpalkeGrfs3SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetMaxRunMode
STRCrpalkeGrfs3SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetMinRunMode
STRCrpalkeGrfs3SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetPropPress
STRCrpalkeGrfs3SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetReference
STRCrpalkeGrfs3SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetRemoteMode
STRCrpalkeGrfs3SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetTwinModeAlt
STRCrpalkeGrfs3SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetTwinModeSpare
STRCrpalkeGrfs3SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].SetTwinModeSync
STRCrpalkeGrfs3Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].Start
STRCrpalkeGrfs3Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[3].Stop
STRCrpalkeGrfs4AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].AlarmAktiven
STRCrpalkeGrfs4Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].Deluje
STRCrpalkeGrfs4LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].LocalMode
STRCrpalkeGrfs4RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].RemoteON
STRCrpalkeGrfs4Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].Reset2handkWhValues
STRCrpalkeGrfs4ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].ResetAlarm
STRCrpalkeGrfs4ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].ResetAlarmLog
STRCrpalkeGrfs4ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].ResetDevice
STRCrpalkeGrfs4SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetAutomatic
STRCrpalkeGrfs4SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetConstFreqMode
STRCrpalkeGrfs4SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetConstPress
STRCrpalkeGrfs4SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetLocalMode
STRCrpalkeGrfs4SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetMaxRunMode
STRCrpalkeGrfs4SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetMinRunMode
STRCrpalkeGrfs4SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetPropPress
STRCrpalkeGrfs4SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetReference
STRCrpalkeGrfs4SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetRemoteMode
STRCrpalkeGrfs4SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetTwinModeAlt
STRCrpalkeGrfs4SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetTwinModeSpare
STRCrpalkeGrfs4SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].SetTwinModeSync
STRCrpalkeGrfs4Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].Start
STRCrpalkeGrfs4Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[4].Stop
STRCrpalkeGrfs5AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].AlarmAktiven
STRCrpalkeGrfs5Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].Deluje
STRCrpalkeGrfs5LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].LocalMode
STRCrpalkeGrfs5RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].RemoteON
STRCrpalkeGrfs5Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].Reset2handkWhValues
STRCrpalkeGrfs5ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].ResetAlarm
STRCrpalkeGrfs5ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].ResetAlarmLog
STRCrpalkeGrfs5ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].ResetDevice
STRCrpalkeGrfs5SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetAutomatic
STRCrpalkeGrfs5SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetConstFreqMode
STRCrpalkeGrfs5SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetConstPress
STRCrpalkeGrfs5SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetLocalMode
STRCrpalkeGrfs5SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetMaxRunMode
STRCrpalkeGrfs5SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetMinRunMode
STRCrpalkeGrfs5SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetPropPress
STRCrpalkeGrfs5SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetReference
STRCrpalkeGrfs5SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetRemoteMode
STRCrpalkeGrfs5SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetTwinModeAlt
STRCrpalkeGrfs5SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetTwinModeSpare
STRCrpalkeGrfs5SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].SetTwinModeSync
STRCrpalkeGrfs5Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].Start
STRCrpalkeGrfs5Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[5].Stop
STRCrpalkeGrfs6AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].AlarmAktiven
STRCrpalkeGrfs6Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].Deluje
STRCrpalkeGrfs6LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].LocalMode
STRCrpalkeGrfs6RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].RemoteON
STRCrpalkeGrfs6Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].Reset2handkWhValues
STRCrpalkeGrfs6ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].ResetAlarm
STRCrpalkeGrfs6ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].ResetAlarmLog
STRCrpalkeGrfs6ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].ResetDevice
STRCrpalkeGrfs6SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetAutomatic
STRCrpalkeGrfs6SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetConstFreqMode
STRCrpalkeGrfs6SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetConstPress
STRCrpalkeGrfs6SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetLocalMode
STRCrpalkeGrfs6SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetMaxRunMode
STRCrpalkeGrfs6SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetMinRunMode
STRCrpalkeGrfs6SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetPropPress
STRCrpalkeGrfs6SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetReference
STRCrpalkeGrfs6SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetRemoteMode
STRCrpalkeGrfs6SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetTwinModeAlt
STRCrpalkeGrfs6SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetTwinModeSpare
STRCrpalkeGrfs6SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].SetTwinModeSync
STRCrpalkeGrfs6Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].Start
STRCrpalkeGrfs6Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[6].Stop
STRCrpalkeGrfs7AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].AlarmAktiven
STRCrpalkeGrfs7Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].Deluje
STRCrpalkeGrfs7LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].LocalMode
STRCrpalkeGrfs7RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].RemoteON
STRCrpalkeGrfs7Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].Reset2handkWhValues
STRCrpalkeGrfs7ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].ResetAlarm
STRCrpalkeGrfs7ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].ResetAlarmLog
STRCrpalkeGrfs7ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].ResetDevice
STRCrpalkeGrfs7SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetAutomatic
STRCrpalkeGrfs7SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetConstFreqMode
STRCrpalkeGrfs7SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetConstPress
STRCrpalkeGrfs7SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetLocalMode
STRCrpalkeGrfs7SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetMaxRunMode
STRCrpalkeGrfs7SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetMinRunMode
STRCrpalkeGrfs7SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetPropPress
STRCrpalkeGrfs7SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetReference
STRCrpalkeGrfs7SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetRemoteMode
STRCrpalkeGrfs7SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetTwinModeAlt
STRCrpalkeGrfs7SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetTwinModeSpare
STRCrpalkeGrfs7SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].SetTwinModeSync
STRCrpalkeGrfs7Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].Start
STRCrpalkeGrfs7Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[7].Stop
STRCrpalkeGrfs8AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].AlarmAktiven
STRCrpalkeGrfs8Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].Deluje
STRCrpalkeGrfs8LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].LocalMode
STRCrpalkeGrfs8RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].RemoteON
STRCrpalkeGrfs8Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].Reset2handkWhValues
STRCrpalkeGrfs8ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].ResetAlarm
STRCrpalkeGrfs8ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].ResetAlarmLog
STRCrpalkeGrfs8ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].ResetDevice
STRCrpalkeGrfs8SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetAutomatic
STRCrpalkeGrfs8SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetConstFreqMode
STRCrpalkeGrfs8SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetConstPress
STRCrpalkeGrfs8SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetLocalMode
STRCrpalkeGrfs8SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetMaxRunMode
STRCrpalkeGrfs8SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetMinRunMode
STRCrpalkeGrfs8SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetPropPress
STRCrpalkeGrfs8SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetReference
STRCrpalkeGrfs8SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetRemoteMode
STRCrpalkeGrfs8SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetTwinModeAlt
STRCrpalkeGrfs8SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetTwinModeSpare
STRCrpalkeGrfs8SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].SetTwinModeSync
STRCrpalkeGrfs8Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].Start
STRCrpalkeGrfs8Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[8].Stop
STRCrpalkeGrfs9AlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].AlarmAktiven
STRCrpalkeGrfs9Deluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].Deluje
STRCrpalkeGrfs9LocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].LocalMode
STRCrpalkeGrfs9RemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].RemoteON
STRCrpalkeGrfs9Reset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].Reset2handkWhValues
STRCrpalkeGrfs9ResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].ResetAlarm
STRCrpalkeGrfs9ResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].ResetAlarmLog
STRCrpalkeGrfs9ResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].ResetDevice
STRCrpalkeGrfs9SetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetAutomatic
STRCrpalkeGrfs9SetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetConstFreqMode
STRCrpalkeGrfs9SetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetConstPress
STRCrpalkeGrfs9SetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetLocalMode
STRCrpalkeGrfs9SetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetMaxRunMode
STRCrpalkeGrfs9SetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetMinRunMode
STRCrpalkeGrfs9SetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetPropPress
STRCrpalkeGrfs9SetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetReference
STRCrpalkeGrfs9SetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetRemoteMode
STRCrpalkeGrfs9SetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetTwinModeAlt
STRCrpalkeGrfs9SetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetTwinModeSpare
STRCrpalkeGrfs9SetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].SetTwinModeSync
STRCrpalkeGrfs9Start | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].Start
STRCrpalkeGrfs9Stop | DIGITAL | IOD_STR | STR:.CrpalkeGrfs[9].Stop
STRCrpDanfossGenError1 | DIGITAL | IOD_STR | STR:.CrpDanfossGenError[1]
STRCrpDanfossGenError2 | DIGITAL | IOD_STR | STR:.CrpDanfossGenError[2]
STRCrpDanfossGenError3 | DIGITAL | IOD_STR | STR:.CrpDanfossGenError[3]
STRCrpDanfossGenError4 | DIGITAL | IOD_STR | STR:.CrpDanfossGenError[4]
STRCrpDanfossNaCas1 | DIGITAL | IOD_STR | STR:.CrpDanfossNaCas[1]
STRCrpDanfossNaCas2 | DIGITAL | IOD_STR | STR:.CrpDanfossNaCas[2]
STRCrpDanfossON1 | DIGITAL | IOD_STR | STR:.CrpDanfossON[1]
STRCrpDanfossON2 | DIGITAL | IOD_STR | STR:.CrpDanfossON[2]
STRCrpDanfossON3 | DIGITAL | IOD_STR | STR:.CrpDanfossON[3]
STRCrpDanfossON4 | DIGITAL | IOD_STR | STR:.CrpDanfossON[4]
STRCrpDanfossStatusError1 | DIGITAL | IOD_STR | STR:.CrpDanfossStatusError[1]
STRCrpDanfossStatusError2 | DIGITAL | IOD_STR | STR:.CrpDanfossStatusError[2]
STRCrpDanfossStatusError3 | DIGITAL | IOD_STR | STR:.CrpDanfossStatusError[3]
STRCrpDanfossStatusError4 | DIGITAL | IOD_STR | STR:.CrpDanfossStatusError[4]
STRCrpGrundfosGenError10 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[10]
STRCrpGrundfosGenError11 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[11]
STRCrpGrundfosGenError12 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[12]
STRCrpGrundfosGenError13 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[13]
STRCrpGrundfosGenError14 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[14]
STRCrpGrundfosGenError1 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[1]
STRCrpGrundfosGenError2 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[2]
STRCrpGrundfosGenError3 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[3]
STRCrpGrundfosGenError4 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[4]
STRCrpGrundfosGenError5 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[5]
STRCrpGrundfosGenError6 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[6]
STRCrpGrundfosGenError7 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[7]
STRCrpGrundfosGenError8 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[8]
STRCrpGrundfosGenError9 | DIGITAL | IOD_STR | STR:.CrpGrundfosGenError[9]
STRCrpGrundfosNaCas1 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[1]
STRCrpGrundfosNaCas2 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[2]
STRCrpGrundfosNaCas3 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[3]
STRCrpGrundfosNaCas4 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[4]
STRCrpGrundfosNaCas5 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[5]
STRCrpGrundfosNaCas6 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[6]
STRCrpGrundfosNaCas7 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaCas[7]
STRCrpGrundfosNaTlak1 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[1]
STRCrpGrundfosNaTlak2 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[2]
STRCrpGrundfosNaTlak3 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[3]
STRCrpGrundfosNaTlak4 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[4]
STRCrpGrundfosNaTlak5 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[5]
STRCrpGrundfosNaTlak6 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[6]
STRCrpGrundfosNaTlak7 | DIGITAL | IOD_STR | STR:.CrpGrundfosNaTlak[7]
STRCrpGrundfosON10 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[10]
STRCrpGrundfosON11 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[11]
STRCrpGrundfosON12 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[12]
STRCrpGrundfosON13 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[13]
STRCrpGrundfosON14 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[14]
STRCrpGrundfosON1 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[1]
STRCrpGrundfosON2 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[2]
STRCrpGrundfosON3 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[3]
STRCrpGrundfosON4 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[4]
STRCrpGrundfosON5 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[5]
STRCrpGrundfosON6 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[6]
STRCrpGrundfosON7 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[7]
STRCrpGrundfosON8 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[8]
STRCrpGrundfosON9 | DIGITAL | IOD_STR | STR:.CrpGrundfosON[9]
STRCrpGrundfosStatusError10 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[10]
STRCrpGrundfosStatusError11 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[11]
STRCrpGrundfosStatusError12 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[12]
STRCrpGrundfosStatusError13 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[13]
STRCrpGrundfosStatusError14 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[14]
STRCrpGrundfosStatusError1 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[1]
STRCrpGrundfosStatusError2 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[2]
STRCrpGrundfosStatusError3 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[3]
STRCrpGrundfosStatusError4 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[4]
STRCrpGrundfosStatusError5 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[5]
STRCrpGrundfosStatusError6 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[6]
STRCrpGrundfosStatusError7 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[7]
STRCrpGrundfosStatusError8 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[8]
STRCrpGrundfosStatusError9 | DIGITAL | IOD_STR | STR:.CrpGrundfosStatusError[9]
STRDanfossHMKontOnOff1 | DIGITAL | IOD_STR | STR:.DanfossHMKontOnOff[1]
STRDanfossHMKontOnOff2 | DIGITAL | IOD_STR | STR:.DanfossHMKontOnOff[2]
STRDanfossHMKontOnOff3 | DIGITAL | IOD_STR | STR:.DanfossHMKontOnOff[3]
STRDanfossHMKontOnOff4 | DIGITAL | IOD_STR | STR:.DanfossHMKontOnOff[4]
STRDI_230VAC_OK | DIGITAL | IOD_STR | STR:.DI_230VAC_OK
STRDI_24VAC_OK | DIGITAL | IOD_STR | STR:.DI_24VAC_OK
STRDI_24VDC_OK | DIGITAL | IOD_STR | STR:.DI_24VDC_OK
STRDI_AkumTopVodeAUTO | DIGITAL | IOD_STR | STR:.DI_AkumTopVodeAUTO
STRDI_AkumTopVodeKontON | DIGITAL | IOD_STR | STR:.DI_AkumTopVodeKontON
STRDI_CrpHM1AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM1AUTO
STRDI_CrpHM1endOFFtoON | DIGITAL | IOD_STR | STR:.DI_CrpHM1endOFFtoON
STRDI_CrpHM1ERR | DIGITAL | IOD_STR | STR:.DI_CrpHM1ERR
STRDI_CrpHM1kontON | DIGITAL | IOD_STR | STR:.DI_CrpHM1kontON
STRDI_CrpHM2AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM2AUTO
STRDI_CrpHM2endOFFtoON | DIGITAL | IOD_STR | STR:.DI_CrpHM2endOFFtoON
STRDI_CrpHM2ERR | DIGITAL | IOD_STR | STR:.DI_CrpHM2ERR
STRDI_CrpHM2kontON | DIGITAL | IOD_STR | STR:.DI_CrpHM2kontON
STRDI_CrpHM3AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM3AUTO
STRDI_CrpHM3endOFFtoON | DIGITAL | IOD_STR | STR:.DI_CrpHM3endOFFtoON
STRDI_CrpHM3ERR | DIGITAL | IOD_STR | STR:.DI_CrpHM3ERR
STRDI_CrpHM3kontON | DIGITAL | IOD_STR | STR:.DI_CrpHM3kontON
STRDI_CrpHM4AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM4AUTO
STRDI_CrpHM4endOFFtoON | DIGITAL | IOD_STR | STR:.DI_CrpHM4endOFFtoON
STRDI_CrpHM4ERR | DIGITAL | IOD_STR | STR:.DI_CrpHM4ERR
STRDI_CrpHM4kontON | DIGITAL | IOD_STR | STR:.DI_CrpHM4kontON
STRDI_CrpHM5AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM5AUTO
STRDI_CrpHM6AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM6AUTO
STRDI_CrpHM7AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM7AUTO
STRDI_CrpHM8AUTO | DIGITAL | IOD_STR | STR:.DI_CrpHM8AUTO
STRDI_CrpMN1AUTO | DIGITAL | IOD_STR | STR:.DI_CrpMN1AUTO
STRDI_CrpMN1kontON | DIGITAL | IOD_STR | STR:.DI_CrpMN1kontON
STRDI_CrpTM10AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM10AUTO
STRDI_CrpTM11TM12AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM11TM12AUTO
STRDI_CrpTM11TM12kontON | DIGITAL | IOD_STR | STR:.DI_CrpTM11TM12kontON
STRDI_CrpTM1AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM1AUTO
STRDI_CrpTM2AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM2AUTO
STRDI_CrpTM3AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM3AUTO
STRDI_CrpTM4AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM4AUTO
STRDI_CrpTM5AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM5AUTO
STRDI_CrpTM6AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM6AUTO
STRDI_CrpTM7AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM7AUTO
STRDI_CrpTM8AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM8AUTO
STRDI_CrpTM9AUTO | DIGITAL | IOD_STR | STR:.DI_CrpTM9AUTO
STRDI_GlStikaloDieselON | DIGITAL | IOD_STR | STR:.DI_GlStikaloDieselON
STRDI_GlStikaloMrezaON | DIGITAL | IOD_STR | STR:.DI_GlStikaloMrezaON
STRDI_GlStikaloUpsON | DIGITAL | IOD_STR | STR:.DI_GlStikaloUpsON
STRDI_HladStAUTO | DIGITAL | IOD_STR | STR:.DI_HladStAUTO
STRDI_HladStCrpHladH2OON | DIGITAL | IOD_STR | STR:.DI_HladStCrpHladH2OON
STRDI_HladStERR | DIGITAL | IOD_STR | STR:.DI_HladStERR
STRDI_Klima1ERR | DIGITAL | IOD_STR | STR:.DI_Klima1ERR
STRDI_Klima1filterZAM | DIGITAL | IOD_STR | STR:.DI_Klima1filterZAM
STRDI_Klima1FIRE | DIGITAL | IOD_STR | STR:.DI_Klima1FIRE
STRDI_Klima1OFFtoON | DIGITAL | IOD_STR | STR:.DI_Klima1OFFtoON
STRDI_Klima1ON | DIGITAL | IOD_STR | STR:.DI_Klima1ON
STRDI_Klima1zascStON | DIGITAL | IOD_STR | STR:.DI_Klima1zascStON
STRDI_Klima2ERR | DIGITAL | IOD_STR | STR:.DI_Klima2ERR
STRDI_Klima2filterZAM | DIGITAL | IOD_STR | STR:.DI_Klima2filterZAM
STRDI_Klima2FIRE | DIGITAL | IOD_STR | STR:.DI_Klima2FIRE
STRDI_Klima2OFFtoON | DIGITAL | IOD_STR | STR:.DI_Klima2OFFtoON
STRDI_Klima2ON | DIGITAL | IOD_STR | STR:.DI_Klima2ON
STRDI_Klima2zascStON | DIGITAL | IOD_STR | STR:.DI_Klima2zascStON
STRDI_Komp1ERR | DIGITAL | IOD_STR | STR:.DI_Komp1ERR
STRDI_Komp1ON | DIGITAL | IOD_STR | STR:.DI_Komp1ON
STRDI_Komp2ERR | DIGITAL | IOD_STR | STR:.DI_Komp2ERR
STRDI_Komp2ON | DIGITAL | IOD_STR | STR:.DI_Komp2ON
STRDI_Kond1AUTO | DIGITAL | IOD_STR | STR:.DI_Kond1AUTO
STRDI_Kond1FS1FS2 | DIGITAL | IOD_STR | STR:.DI_Kond1FS1FS2
STRDI_Kond1ON | DIGITAL | IOD_STR | STR:.DI_Kond1ON
STRDI_Kond1zascStON | DIGITAL | IOD_STR | STR:.DI_Kond1zascStON
STRDI_Kond2AUTO | DIGITAL | IOD_STR | STR:.DI_Kond2AUTO
STRDI_Kond2FS1FS2 | DIGITAL | IOD_STR | STR:.DI_Kond2FS1FS2
STRDI_Kond2ON | DIGITAL | IOD_STR | STR:.DI_Kond2ON
STRDI_Kond2zascStON | DIGITAL | IOD_STR | STR:.DI_Kond2zascStON
STRDI_Kond3AUTO | DIGITAL | IOD_STR | STR:.DI_Kond3AUTO
STRDI_Kond3FS1FS2 | DIGITAL | IOD_STR | STR:.DI_Kond3FS1FS2
STRDI_Kond3ON | DIGITAL | IOD_STR | STR:.DI_Kond3ON
STRDI_Kond3zascStON | DIGITAL | IOD_STR | STR:.DI_Kond3zascStON
STRDI_Lop1PL1Odprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL1Odprta
STRDI_Lop1PL1Zaprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL1Zaprta
STRDI_Lop1PL2Odprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL2Odprta
STRDI_Lop1PL2Zaprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL2Zaprta
STRDI_Lop1PL3Odprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL3Odprta
STRDI_Lop1PL3Zaprta | DIGITAL | IOD_STR | STR:.DI_Lop1PL3Zaprta
STRDI_Lop3Y1Odprta | DIGITAL | IOD_STR | STR:.DI_Lop3Y1Odprta
STRDI_Lop3Y1Zaprta | DIGITAL | IOD_STR | STR:.DI_Lop3Y1Zaprta
STRDI_Lop4Y1Odprta | DIGITAL | IOD_STR | STR:.DI_Lop4Y1Odprta
STRDI_Lop4Y1Zaprta | DIGITAL | IOD_STR | STR:.DI_Lop4Y1Zaprta
STRDI_PotrditevAlarmov | DIGITAL | IOD_STR | STR:.DI_PotrditevAlarmov
STRDI_RazlitjeVodeEXP1 | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeEXP1
STRDI_RazlitjeVodeEXP2 | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeEXP2
STRDI_RazlitjeVodeHP | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeHP
STRDI_RazlitjeVodeK1 | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeK1
STRDI_RazlitjeVodeK2 | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeK2
STRDI_RazlitjeVodeTP | DIGITAL | IOD_STR | STR:.DI_RazlitjeVodeTP
STRDI_ToplPostGenErr | DIGITAL | IOD_STR | STR:.DI_ToplPostGenErr
STRDI_UPS_Alarm | DIGITAL | IOD_STR | STR:.DI_UPS_Alarm
STRDI_UPS_BatNacin | DIGITAL | IOD_STR | STR:.DI_UPS_BatNacin
STRDI_UPS_Polnjenje | DIGITAL | IOD_STR | STR:.DI_UPS_Polnjenje
STRDI_Vent1Auto | DIGITAL | IOD_STR | STR:.DI_Vent1Auto
STRDI_Vent1kontON | DIGITAL | IOD_STR | STR:.DI_Vent1kontON
STRDI_Vent2Auto | DIGITAL | IOD_STR | STR:.DI_Vent2Auto
STRDI_Vent2kontON | DIGITAL | IOD_STR | STR:.DI_Vent2kontON
STRDI_Vent3Auto | DIGITAL | IOD_STR | STR:.DI_Vent3Auto
STRDI_Vent3kontON | DIGITAL | IOD_STR | STR:.DI_Vent3kontON
STRDI_Vent4Auto | DIGITAL | IOD_STR | STR:.DI_Vent4Auto
STRDI_Vent4kontON | DIGITAL | IOD_STR | STR:.DI_Vent4kontON
STRDI_Vent5Auto | DIGITAL | IOD_STR | STR:.DI_Vent5Auto
STRDI_Vent5kontON | DIGITAL | IOD_STR | STR:.DI_Vent5kontON
STRDI_Vent6Auto | DIGITAL | IOD_STR | STR:.DI_Vent6Auto
STRDI_Vent6kontON | DIGITAL | IOD_STR | STR:.DI_Vent6kontON
STRDI_Vlaz1ERR | DIGITAL | IOD_STR | STR:.DI_Vlaz1ERR
STRDI_Vlaz1ON | DIGITAL | IOD_STR | STR:.DI_Vlaz1ON
STRDI_Vlaz2ERR | DIGITAL | IOD_STR | STR:.DI_Vlaz2ERR
STRDI_Vlaz2ON | DIGITAL | IOD_STR | STR:.DI_Vlaz2ON
STRDIN_230VAC_OK | DIGITAL | IOD_STR | STR:.DIN_230VAC_OK
STRDIN_24VAC_OK | DIGITAL | IOD_STR | STR:.DIN_24VAC_OK
STRDIN_24VDC_OK | DIGITAL | IOD_STR | STR:.DIN_24VDC_OK
STRDIN_CrpHM1ERR | DIGITAL | IOD_STR | STR:.DIN_CrpHM1ERR
STRDIN_CrpHM2ERR | DIGITAL | IOD_STR | STR:.DIN_CrpHM2ERR
STRDIN_CrpHM3ERR | DIGITAL | IOD_STR | STR:.DIN_CrpHM3ERR
STRDIN_CrpHM4ERR | DIGITAL | IOD_STR | STR:.DIN_CrpHM4ERR
STRDIN_HladStERR | DIGITAL | IOD_STR | STR:.DIN_HladStERR
STRDIN_Klima1ERR | DIGITAL | IOD_STR | STR:.DIN_Klima1ERR
STRDIN_Klima1filterZAM | DIGITAL | IOD_STR | STR:.DIN_Klima1filterZAM
STRDIN_Klima1zascStON | DIGITAL | IOD_STR | STR:.DIN_Klima1zascStON
STRDIN_Klima2ERR | DIGITAL | IOD_STR | STR:.DIN_Klima2ERR
STRDIN_Klima2filterZAM | DIGITAL | IOD_STR | STR:.DIN_Klima2filterZAM
STRDIN_Klima2zascStON | DIGITAL | IOD_STR | STR:.DIN_Klima2zascStON
STRDIN_Komp1ERR | DIGITAL | IOD_STR | STR:.DIN_Komp1ERR
STRDIN_Komp1ON | DIGITAL | IOD_STR | STR:.DIN_Komp1ON
STRDIN_Komp2ERR | DIGITAL | IOD_STR | STR:.DIN_Komp2ERR
STRDIN_Komp2ON | DIGITAL | IOD_STR | STR:.DIN_Komp2ON
STRDIN_Kond1zascStON | DIGITAL | IOD_STR | STR:.DIN_Kond1zascStON
STRDIN_Kond2zascStON | DIGITAL | IOD_STR | STR:.DIN_Kond2zascStON
STRDIN_Kond3zascStON | DIGITAL | IOD_STR | STR:.DIN_Kond3zascStON
STRDIN_Vlaz1ERR | DIGITAL | IOD_STR | STR:.DIN_Vlaz1ERR
STRDIN_Vlaz2ERR | DIGITAL | IOD_STR | STR:.DIN_Vlaz2ERR
STRDO_BojlerTE1Vklop | DIGITAL | IOD_STR | STR:.DO_BojlerTE1Vklop
STRDO_CrpHM1Vklop | DIGITAL | IOD_STR | STR:.DO_CrpHM1Vklop
STRDO_CrpHM2Vklop | DIGITAL | IOD_STR | STR:.DO_CrpHM2Vklop
STRDO_CrpHM3Vklop | DIGITAL | IOD_STR | STR:.DO_CrpHM3Vklop
STRDO_CrpHM4Vklop | DIGITAL | IOD_STR | STR:.DO_CrpHM4Vklop
STRDO_CrpMN1Vklop | DIGITAL | IOD_STR | STR:.DO_CrpMN1Vklop
STRDO_CrpTM11Vklop | DIGITAL | IOD_STR | STR:.DO_CrpTM11Vklop
STRDO_GrundfosVklopL | DIGITAL | IOD_STR | STR:.DO_GrundfosVklopL
STRDO_GrundfosVklopN | DIGITAL | IOD_STR | STR:.DO_GrundfosVklopN
STRDO_HladStrIzklop | DIGITAL | IOD_STR | STR:.DO_HladStrIzklop
STRDO_KE1Vklop | DIGITAL | IOD_STR | STR:.DO_KE1Vklop
STRDO_KE2Vklop | DIGITAL | IOD_STR | STR:.DO_KE2Vklop
STRDO_KE3Vklop | DIGITAL | IOD_STR | STR:.DO_KE3Vklop
STRDO_Klima1Vklop | DIGITAL | IOD_STR | STR:.DO_Klima1Vklop
STRDO_Klima2Vklop | DIGITAL | IOD_STR | STR:.DO_Klima2Vklop
STRDO_Lop1PL1Vklop | DIGITAL | IOD_STR | STR:.DO_Lop1PL1Vklop
STRDO_Lop1PL2Vklop | DIGITAL | IOD_STR | STR:.DO_Lop1PL2Vklop
STRDO_Lop1PL3Vklop | DIGITAL | IOD_STR | STR:.DO_Lop1PL3Vklop
STRDO_Lop3Y1Vklop | DIGITAL | IOD_STR | STR:.DO_Lop3Y1Vklop
STRDO_Lop4Y1Vklop | DIGITAL | IOD_STR | STR:.DO_Lop4Y1Vklop
STRDO_RazE11_10Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_10Vklop
STRDO_RazE11_11Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_11Vklop
STRDO_RazE11_1Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_1Vklop
STRDO_RazE11_2Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_2Vklop
STRDO_RazE11_3Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_3Vklop
STRDO_RazE11_4Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_4Vklop
STRDO_RazE11_5Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_5Vklop
STRDO_RazE11_6Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_6Vklop
STRDO_RazE11_7Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_7Vklop
STRDO_RazE11_8Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_8Vklop
STRDO_RazE11_9Vklop | DIGITAL | IOD_STR | STR:.DO_RazE11_9Vklop
STRDO_RazE12_12Vklop | DIGITAL | IOD_STR | STR:.DO_RazE12_12Vklop
STRDO_RazE12_13Vklop | DIGITAL | IOD_STR | STR:.DO_RazE12_13Vklop
STRDO_RazE12_14Vklop | DIGITAL | IOD_STR | STR:.DO_RazE12_14Vklop
STRDO_RazE12_15Vklop | DIGITAL | IOD_STR | STR:.DO_RazE12_15Vklop
STRDO_RazE13_16Vklop | DIGITAL | IOD_STR | STR:.DO_RazE13_16Vklop
STRDO_RazE13_17Vklop | DIGITAL | IOD_STR | STR:.DO_RazE13_17Vklop
STRDO_RazE13_18Vklop | DIGITAL | IOD_STR | STR:.DO_RazE13_18Vklop
STRDO_RazE13_19Vklop | DIGITAL | IOD_STR | STR:.DO_RazE13_19Vklop
STRDO_RazE16_20Vklop | DIGITAL | IOD_STR | STR:.DO_RazE16_20Vklop
STRDO_RazE16_21Vklop | DIGITAL | IOD_STR | STR:.DO_RazE16_21Vklop
STRDO_RazE16_22Vklop | DIGITAL | IOD_STR | STR:.DO_RazE16_22Vklop
STRDO_RazE16_23Vklop | DIGITAL | IOD_STR | STR:.DO_RazE16_23Vklop
STRDO_RazE16_24Vklop | DIGITAL | IOD_STR | STR:.DO_RazE16_24Vklop
STRDO_Vent1Vklop | DIGITAL | IOD_STR | STR:.DO_Vent1Vklop
STRDO_Vent2Vklop | DIGITAL | IOD_STR | STR:.DO_Vent2Vklop
STRDO_Vent3Vklop | DIGITAL | IOD_STR | STR:.DO_Vent3Vklop
STRDO_Vent4Vklop | DIGITAL | IOD_STR | STR:.DO_Vent4Vklop
STRDO_Vent5Vklop | DIGITAL | IOD_STR | STR:.DO_Vent5Vklop
STRDO_Vent6Vklop | DIGITAL | IOD_STR | STR:.DO_Vent6Vklop
STRErrComCirc1 | DIGITAL | IOD_STR | STR:.ErrComCirc[1]
STRErrComCirc2 | DIGITAL | IOD_STR | STR:.ErrComCirc[2]
STRErrComDanfossHM1 | DIGITAL | IOD_STR | STR:.ErrComDanfossHM[1]
STRErrComDanfossHM2 | DIGITAL | IOD_STR | STR:.ErrComDanfossHM[2]
STRErrComDanfossHM3 | DIGITAL | IOD_STR | STR:.ErrComDanfossHM[3]
STRErrComDanfossHM4 | DIGITAL | IOD_STR | STR:.ErrComDanfossHM[4]
STRErrComGrundfos0 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[0]
STRErrComGrundfos10 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[10]
STRErrComGrundfos11 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[11]
STRErrComGrundfos12 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[12]
STRErrComGrundfos13 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[13]
STRErrComGrundfos14 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[14]
STRErrComGrundfos1 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[1]
STRErrComGrundfos2 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[2]
STRErrComGrundfos3 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[3]
STRErrComGrundfos4 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[4]
STRErrComGrundfos5 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[5]
STRErrComGrundfos6 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[6]
STRErrComGrundfos7 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[7]
STRErrComGrundfos8 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[8]
STRErrComGrundfos9 | DIGITAL | IOD_STR | STR:.ErrComGrundfos[9]
STRErrComHladStroj | DIGITAL | IOD_STR | STR:.ErrComHladStroj
STRErrComKlima1 | DIGITAL | IOD_STR | STR:.ErrComKlima[1]
STRErrComKlima2 | DIGITAL | IOD_STR | STR:.ErrComKlima[2]
STRErrCommScada | DIGITAL | IOD_STR | STR:.ErrCommScada
STRErrCommXC100 | DIGITAL | IOD_STR | STR:.ErrCommXC100
STRErrComPanelPLC | DIGITAL | IOD_STR | STR:.ErrComPanelPLC
STRErrComPort2 | DIGITAL | IOD_STR | STR:.ErrComPort2
STRErrComPort3 | DIGITAL | IOD_STR | STR:.ErrComPort3
STRErrComPort4 | DIGITAL | IOD_STR | STR:.ErrComPort4
STRErrComToplPost | DIGITAL | IOD_STR | STR:.ErrComToplPost
STRExp1TlakAlarm | DIGITAL | IOD_STR | STR:.Exp1TlakAlarm
STRExp2TlakAlarm | DIGITAL | IOD_STR | STR:.Exp2TlakAlarm
STRHladilniStrojOnOff | DIGITAL | IOD_STR | STR:.HladilniStrojOnOff
STRHladStrojFazeAlarm | DIGITAL | IOD_STR | STR:.HladStroj.FazeAlarm
STRHladStrojKompresorOljeAlarm | DIGITAL | IOD_STR | STR:.HladStroj.KompresorOljeAlarm
STRHladStrojLANcarelAlarm | DIGITAL | IOD_STR | STR:.HladStroj.LANcarelAlarm
STRHladStrojNapaka | DIGITAL | IOD_STR | STR:.HladStroj.Napaka
STRHladStrojNizekPritiskAlarm | DIGITAL | IOD_STR | STR:.HladStroj.NizekPritiskAlarm
STRHladStrojObratovalneUreOpozorilo | DIGITAL | IOD_STR | STR:.HladStroj.ObratovalneUreOpozorilo
STRHladStrojOffByAlarms | DIGITAL | IOD_STR | STR:.HladStroj.OffByAlarms
STRHladStrojPretokAlarm | DIGITAL | IOD_STR | STR:.HladStroj.PretokAlarm
STRHladStrojRemoteOn | DIGITAL | IOD_STR | STR:.HladStroj.RemoteOn
STRHladStrojSenzorAlarm | DIGITAL | IOD_STR | STR:.HladStroj.SenzorAlarm
STRHladStrojSummerOperation | DIGITAL | IOD_STR | STR:.HladStroj.SummerOperation
STRHladStrojTemperaturaAlarm | DIGITAL | IOD_STR | STR:.HladStroj.TemperaturaAlarm
STRHladStrojUnitOn | DIGITAL | IOD_STR | STR:.HladStroj.UnitOn
STRHladStrojUraAlarm | DIGITAL | IOD_STR | STR:.HladStroj.UraAlarm
STRHladStrojVisokPritiskAlarm | DIGITAL | IOD_STR | STR:.HladStroj.VisokPritiskAlarm
STRHladStrojVisokPritiskOpozorilo | DIGITAL | IOD_STR | STR:.HladStroj.VisokPritiskOpozorilo
STRHladStrojZmrzalniAlarm | DIGITAL | IOD_STR | STR:.HladStroj.ZmrzalniAlarm
STRHladStrojErrors10 | DIGITAL | IOD_STR | STR:.HladStrojErrors[10]
STRHladStrojErrors11 | DIGITAL | IOD_STR | STR:.HladStrojErrors[11]
STRHladStrojErrors12 | DIGITAL | IOD_STR | STR:.HladStrojErrors[12]
STRHladStrojErrors13 | DIGITAL | IOD_STR | STR:.HladStrojErrors[13]
STRHladStrojErrors14 | DIGITAL | IOD_STR | STR:.HladStrojErrors[14]
STRHladStrojErrors15 | DIGITAL | IOD_STR | STR:.HladStrojErrors[15]
STRHladStrojErrors16 | DIGITAL | IOD_STR | STR:.HladStrojErrors[16]
STRHladStrojErrors1 | DIGITAL | IOD_STR | STR:.HladStrojErrors[1]
STRHladStrojErrors2 | DIGITAL | IOD_STR | STR:.HladStrojErrors[2]
STRHladStrojErrors3 | DIGITAL | IOD_STR | STR:.HladStrojErrors[3]
STRHladStrojErrors4 | DIGITAL | IOD_STR | STR:.HladStrojErrors[4]
STRHladStrojErrors5 | DIGITAL | IOD_STR | STR:.HladStrojErrors[5]
STRHladStrojErrors6 | DIGITAL | IOD_STR | STR:.HladStrojErrors[6]
STRHladStrojErrors7 | DIGITAL | IOD_STR | STR:.HladStrojErrors[7]
STRHladStrojErrors8 | DIGITAL | IOD_STR | STR:.HladStrojErrors[8]
STRHladStrojErrors9 | DIGITAL | IOD_STR | STR:.HladStrojErrors[9]
STRKlima1errors10 | DIGITAL | IOD_STR | STR:.Klima1errors[10]
STRKlima1errors11 | DIGITAL | IOD_STR | STR:.Klima1errors[11]
STRKlima1errors12 | DIGITAL | IOD_STR | STR:.Klima1errors[12]
STRKlima1errors1 | DIGITAL | IOD_STR | STR:.Klima1errors[1]
STRKlima1errors2 | DIGITAL | IOD_STR | STR:.Klima1errors[2]
STRKlima1errors3 | DIGITAL | IOD_STR | STR:.Klima1errors[3]
STRKlima1errors4 | DIGITAL | IOD_STR | STR:.Klima1errors[4]
STRKlima1errors5 | DIGITAL | IOD_STR | STR:.Klima1errors[5]
STRKlima1errors6 | DIGITAL | IOD_STR | STR:.Klima1errors[6]
STRKlima1errors7 | DIGITAL | IOD_STR | STR:.Klima1errors[7]
STRKlima1errors8 | DIGITAL | IOD_STR | STR:.Klima1errors[8]
STRKlima1errors9 | DIGITAL | IOD_STR | STR:.Klima1errors[9]
STRKlima2errors10 | DIGITAL | IOD_STR | STR:.Klima2errors[10]
STRKlima2errors11 | DIGITAL | IOD_STR | STR:.Klima2errors[11]
STRKlima2errors12 | DIGITAL | IOD_STR | STR:.Klima2errors[12]
STRKlima2errors1 | DIGITAL | IOD_STR | STR:.Klima2errors[1]
STRKlima2errors2 | DIGITAL | IOD_STR | STR:.Klima2errors[2]
STRKlima2errors3 | DIGITAL | IOD_STR | STR:.Klima2errors[3]
STRKlima2errors4 | DIGITAL | IOD_STR | STR:.Klima2errors[4]
STRKlima2errors5 | DIGITAL | IOD_STR | STR:.Klima2errors[5]
STRKlima2errors6 | DIGITAL | IOD_STR | STR:.Klima2errors[6]
STRKlima2errors7 | DIGITAL | IOD_STR | STR:.Klima2errors[7]
STRKlima2errors8 | DIGITAL | IOD_STR | STR:.Klima2errors[8]
STRKlima2errors9 | DIGITAL | IOD_STR | STR:.Klima2errors[9]
STRKlima1CrpalkaGrelnika | DIGITAL | IOD_STR | STR:.Klima[1].CrpalkaGrelnika
STRKlima1DelovanjeVentH1 | DIGITAL | IOD_STR | STR:.Klima[1].DelovanjeVentH1
STRKlima1DelovanjeVentH2 | DIGITAL | IOD_STR | STR:.Klima[1].DelovanjeVentH2
STRKlima1Deluje | DIGITAL | IOD_STR | STR:.Klima[1].Deluje
STRKlima1FilterError | DIGITAL | IOD_STR | STR:.Klima[1].FilterError
STRKlima1Napaka | DIGITAL | IOD_STR | STR:.Klima[1].Napaka
STRKlima1NapakaPriPretokuZraka | DIGITAL | IOD_STR | STR:.Klima[1].NapakaPriPretokuZraka
STRKlima1OkvaraRototerma | DIGITAL | IOD_STR | STR:.Klima[1].OkvaraRototerma
STRKlima1OkvaraVlazilne | DIGITAL | IOD_STR | STR:.Klima[1].OkvaraVlazilne
STRKlima1PozarError | DIGITAL | IOD_STR | STR:.Klima[1].PozarError
STRKlima1PozarniAlarm | DIGITAL | IOD_STR | STR:.Klima[1].PozarniAlarm
STRKlima1PreobremenitevMotCrpGr | DIGITAL | IOD_STR | STR:.Klima[1].PreobremenitevMotCrpGr
STRKlima1PreobremenitevMotVent | DIGITAL | IOD_STR | STR:.Klima[1].PreobremenitevMotVent
STRKlima1ProtizmrzAktivna | DIGITAL | IOD_STR | STR:.Klima[1].ProtizmrzAktivna
STRKlima1SkupniAlarmA | DIGITAL | IOD_STR | STR:.Klima[1].SkupniAlarmA
STRKlima1SkupniAlarmB | DIGITAL | IOD_STR | STR:.Klima[1].SkupniAlarmB
STRKlima1VklopRegulacije | DIGITAL | IOD_STR | STR:.Klima[1].VklopRegulacije
STRKlima1ZamasenFilter | DIGITAL | IOD_STR | STR:.Klima[1].ZamasenFilter
STRKlima2CrpalkaGrelnika | DIGITAL | IOD_STR | STR:.Klima[2].CrpalkaGrelnika
STRKlima2DelovanjeVentH1 | DIGITAL | IOD_STR | STR:.Klima[2].DelovanjeVentH1
STRKlima2DelovanjeVentH2 | DIGITAL | IOD_STR | STR:.Klima[2].DelovanjeVentH2
STRKlima2Deluje | DIGITAL | IOD_STR | STR:.Klima[2].Deluje
STRKlima2FilterError | DIGITAL | IOD_STR | STR:.Klima[2].FilterError
STRKlima2Napaka | DIGITAL | IOD_STR | STR:.Klima[2].Napaka
STRKlima2NapakaPriPretokuZraka | DIGITAL | IOD_STR | STR:.Klima[2].NapakaPriPretokuZraka
STRKlima2OkvaraRototerma | DIGITAL | IOD_STR | STR:.Klima[2].OkvaraRototerma
STRKlima2OkvaraVlazilne | DIGITAL | IOD_STR | STR:.Klima[2].OkvaraVlazilne
STRKlima2PozarError | DIGITAL | IOD_STR | STR:.Klima[2].PozarError
STRKlima2PozarniAlarm | DIGITAL | IOD_STR | STR:.Klima[2].PozarniAlarm
STRKlima2PreobremenitevMotCrpGr | DIGITAL | IOD_STR | STR:.Klima[2].PreobremenitevMotCrpGr
STRKlima2PreobremenitevMotVent | DIGITAL | IOD_STR | STR:.Klima[2].PreobremenitevMotVent
STRKlima2ProtizmrzAktivna | DIGITAL | IOD_STR | STR:.Klima[2].ProtizmrzAktivna
STRKlima2SkupniAlarmA | DIGITAL | IOD_STR | STR:.Klima[2].SkupniAlarmA
STRKlima2SkupniAlarmB | DIGITAL | IOD_STR | STR:.Klima[2].SkupniAlarmB
STRKlima2VklopRegulacije | DIGITAL | IOD_STR | STR:.Klima[2].VklopRegulacije
STRKlima2ZamasenFilter | DIGITAL | IOD_STR | STR:.Klima[2].ZamasenFilter
STRKondEnotaOnOff1 | DIGITAL | IOD_STR | STR:.KondEnotaOnOff[1]
STRKondEnotaOnOff2 | DIGITAL | IOD_STR | STR:.KondEnotaOnOff[2]
STRKondEnotaOnOff3 | DIGITAL | IOD_STR | STR:.KondEnotaOnOff[3]
STRKontRezervaOnOff1 | DIGITAL | IOD_STR | STR:.KontRezervaOnOff[1]
STRKontRezervaOnOff2 | DIGITAL | IOD_STR | STR:.KontRezervaOnOff[2]
STRKontRezervaOnOff3 | DIGITAL | IOD_STR | STR:.KontRezervaOnOff[3]
STRNapakaSenzorAI10 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[10]
STRNapakaSenzorAI11 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[11]
STRNapakaSenzorAI12 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[12]
STRNapakaSenzorAI13 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[13]
STRNapakaSenzorAI14 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[14]
STRNapakaSenzorAI15 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[15]
STRNapakaSenzorAI16 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[16]
STRNapakaSenzorAI17 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[17]
STRNapakaSenzorAI18 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[18]
STRNapakaSenzorAI19 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[19]
STRNapakaSenzorAI1 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[1]
STRNapakaSenzorAI20 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[20]
STRNapakaSenzorAI21 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[21]
STRNapakaSenzorAI22 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[22]
STRNapakaSenzorAI23 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[23]
STRNapakaSenzorAI24 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[24]
STRNapakaSenzorAI25 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[25]
STRNapakaSenzorAI26 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[26]
STRNapakaSenzorAI27 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[27]
STRNapakaSenzorAI28 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[28]
STRNapakaSenzorAI29 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[29]
STRNapakaSenzorAI2 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[2]
STRNapakaSenzorAI30 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[30]
STRNapakaSenzorAI31 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[31]
STRNapakaSenzorAI32 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[32]
STRNapakaSenzorAI33 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[33]
STRNapakaSenzorAI34 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[34]
STRNapakaSenzorAI35 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[35]
STRNapakaSenzorAI36 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[36]
STRNapakaSenzorAI37 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[37]
STRNapakaSenzorAI38 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[38]
STRNapakaSenzorAI39 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[39]
STRNapakaSenzorAI3 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[3]
STRNapakaSenzorAI40 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[40]
STRNapakaSenzorAI4 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[4]
STRNapakaSenzorAI5 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[5]
STRNapakaSenzorAI6 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[6]
STRNapakaSenzorAI7 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[7]
STRNapakaSenzorAI8 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[8]
STRNapakaSenzorAI9 | DIGITAL | IOD_STR | STR:.NapakaSenzorAI[9]
STRNapakaSenzorHIA1 | DIGITAL | IOD_STR | STR:.NapakaSenzorHIA[1]
STRNapakaSenzorHIA2 | DIGITAL | IOD_STR | STR:.NapakaSenzorHIA[2]
STRNapakaSenzorHIA3 | DIGITAL | IOD_STR | STR:.NapakaSenzorHIA[3]
STRNapakaSenzorHIA4 | DIGITAL | IOD_STR | STR:.NapakaSenzorHIA[4]
STRNapakaSenzorTIA1 | DIGITAL | IOD_STR | STR:.NapakaSenzorTIA[1]
STRNapakaSenzorTIA2 | DIGITAL | IOD_STR | STR:.NapakaSenzorTIA[2]
STRNapakaSenzorTIA3 | DIGITAL | IOD_STR | STR:.NapakaSenzorTIA[3]
STRNapakaSenzorTIA4 | DIGITAL | IOD_STR | STR:.NapakaSenzorTIA[4]
STRPozarnaLoputaOnOffError1 | DIGITAL | IOD_STR | STR:.PozarnaLoputaOnOffError[1]
STRPozarnaLoputaOnOffError2 | DIGITAL | IOD_STR | STR:.PozarnaLoputaOnOffError[2]
STRPozarnaLoputaOnOffError3 | DIGITAL | IOD_STR | STR:.PozarnaLoputaOnOffError[3]
STRPozarnaLoputaOnOffError4 | DIGITAL | IOD_STR | STR:.PozarnaLoputaOnOffError[4]
STRPozarnaLoputaOnOffError5 | DIGITAL | IOD_STR | STR:.PozarnaLoputaOnOffError[5]
STRPozarnaLoputOnOff1 | DIGITAL | IOD_STR | STR:.PozarnaLoputOnOff[1]
STRPozarnaLoputOnOff2 | DIGITAL | IOD_STR | STR:.PozarnaLoputOnOff[2]
STRPozarnaLoputOnOff3 | DIGITAL | IOD_STR | STR:.PozarnaLoputOnOff[3]
STRPozarnaLoputOnOff4 | DIGITAL | IOD_STR | STR:.PozarnaLoputOnOff[4]
STRPozarnaLoputOnOff5 | DIGITAL | IOD_STR | STR:.PozarnaLoputOnOff[5]
STRPozarniAlarm | DIGITAL | IOD_STR | STR:.PozarniAlarm
STRPrenosUrnika10 | DIGITAL | IOD_STR | STR:.PrenosUrnika[10]
STRPrenosUrnika11 | DIGITAL | IOD_STR | STR:.PrenosUrnika[11]
STRPrenosUrnika12 | DIGITAL | IOD_STR | STR:.PrenosUrnika[12]
STRPrenosUrnika13 | DIGITAL | IOD_STR | STR:.PrenosUrnika[13]
STRPrenosUrnika14 | DIGITAL | IOD_STR | STR:.PrenosUrnika[14]
STRPrenosUrnika15 | DIGITAL | IOD_STR | STR:.PrenosUrnika[15]
STRPrenosUrnika16 | DIGITAL | IOD_STR | STR:.PrenosUrnika[16]
STRPrenosUrnika17 | DIGITAL | IOD_STR | STR:.PrenosUrnika[17]
STRPrenosUrnika18 | DIGITAL | IOD_STR | STR:.PrenosUrnika[18]
STRPrenosUrnika19 | DIGITAL | IOD_STR | STR:.PrenosUrnika[19]
STRPrenosUrnika1 | DIGITAL | IOD_STR | STR:.PrenosUrnika[1]
STRPrenosUrnika20 | DIGITAL | IOD_STR | STR:.PrenosUrnika[20]
STRPrenosUrnika21 | DIGITAL | IOD_STR | STR:.PrenosUrnika[21]
STRPrenosUrnika22 | DIGITAL | IOD_STR | STR:.PrenosUrnika[22]
STRPrenosUrnika23 | DIGITAL | IOD_STR | STR:.PrenosUrnika[23]
STRPrenosUrnika24 | DIGITAL | IOD_STR | STR:.PrenosUrnika[24]
STRPrenosUrnika25 | DIGITAL | IOD_STR | STR:.PrenosUrnika[25]
STRPrenosUrnika2 | DIGITAL | IOD_STR | STR:.PrenosUrnika[2]
STRPrenosUrnika3 | DIGITAL | IOD_STR | STR:.PrenosUrnika[3]
STRPrenosUrnika4 | DIGITAL | IOD_STR | STR:.PrenosUrnika[4]
STRPrenosUrnika5 | DIGITAL | IOD_STR | STR:.PrenosUrnika[5]
STRPrenosUrnika6 | DIGITAL | IOD_STR | STR:.PrenosUrnika[6]
STRPrenosUrnika7 | DIGITAL | IOD_STR | STR:.PrenosUrnika[7]
STRPrenosUrnika8 | DIGITAL | IOD_STR | STR:.PrenosUrnika[8]
STRPrenosUrnika9 | DIGITAL | IOD_STR | STR:.PrenosUrnika[9]
STRRazsvetljavaOnOff10 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[10]
STRRazsvetljavaOnOff11 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[11]
STRRazsvetljavaOnOff12 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[12]
STRRazsvetljavaOnOff13 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[13]
STRRazsvetljavaOnOff14 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[14]
STRRazsvetljavaOnOff15 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[15]
STRRazsvetljavaOnOff16 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[16]
STRRazsvetljavaOnOff17 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[17]
STRRazsvetljavaOnOff18 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[18]
STRRazsvetljavaOnOff19 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[19]
STRRazsvetljavaOnOff1 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[1]
STRRazsvetljavaOnOff20 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[20]
STRRazsvetljavaOnOff21 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[21]
STRRazsvetljavaOnOff22 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[22]
STRRazsvetljavaOnOff23 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[23]
STRRazsvetljavaOnOff24 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[24]
STRRazsvetljavaOnOff25 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[25]
STRRazsvetljavaOnOff2 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[2]
STRRazsvetljavaOnOff3 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[3]
STRRazsvetljavaOnOff4 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[4]
STRRazsvetljavaOnOff5 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[5]
STRRazsvetljavaOnOff6 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[6]
STRRazsvetljavaOnOff7 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[7]
STRRazsvetljavaOnOff8 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[8]
STRRazsvetljavaOnOff9 | DIGITAL | IOD_STR | STR:.RazsvetljavaOnOff[9]
STRRazsvetljavaRocno | DIGITAL | IOD_STR | STR:.RazsvetljavaRocno
STRSetDateTime | DIGITAL | IOD_STR | STR:.SetDateTime
STRSetDateTimeDemand | DIGITAL | IOD_STR | STR:.SetDateTimeDemand
STRSetDateTimeError | DIGITAL | IOD_STR | STR:.SetDateTimeError
STRSetDateTimeFinished | DIGITAL | IOD_STR | STR:.SetDateTimeFinished
STRSetRemoteOnOff1 | DIGITAL | IOD_STR | STR:.SetRemoteOnOff[1]
STRSetRemoteOnOff2 | DIGITAL | IOD_STR | STR:.SetRemoteOnOff[2]
STRSlabaBaterijaPLC_A1 | DIGITAL | IOD_STR | STR:.SlabaBaterijaPLC_A1
STRSlabaBaterijaPLC_A100 | DIGITAL | IOD_STR | STR:.SlabaBaterijaPLC_A100
STRSO_BojlerTE1Vklop | DIGITAL | IOD_STR | STR:.SO_BojlerTE1Vklop
STRSO_CrpHM1Vklop | DIGITAL | IOD_STR | STR:.SO_CrpHM1Vklop
STRSO_CrpHM2Vklop | DIGITAL | IOD_STR | STR:.SO_CrpHM2Vklop
STRSO_CrpHM3Vklop | DIGITAL | IOD_STR | STR:.SO_CrpHM3Vklop
STRSO_CrpHM4Vklop | DIGITAL | IOD_STR | STR:.SO_CrpHM4Vklop
STRSO_CrpMN1Vklop | DIGITAL | IOD_STR | STR:.SO_CrpMN1Vklop
STRSO_CrpTM11Vklop | DIGITAL | IOD_STR | STR:.SO_CrpTM11Vklop
STRSO_HladStrVklop | DIGITAL | IOD_STR | STR:.SO_HladStrVklop
STRSO_KE1Vklop | DIGITAL | IOD_STR | STR:.SO_KE1Vklop
STRSO_KE2Vklop | DIGITAL | IOD_STR | STR:.SO_KE2Vklop
STRSO_KE3Vklop | DIGITAL | IOD_STR | STR:.SO_KE3Vklop
STRSO_rezerva1_3 | DIGITAL | IOD_STR | STR:.SO_rezerva1_3
STRSO_rezerva1_4 | DIGITAL | IOD_STR | STR:.SO_rezerva1_4
STRSO_rezerva1_5 | DIGITAL | IOD_STR | STR:.SO_rezerva1_5
STRSO_Vent1Vklop | DIGITAL | IOD_STR | STR:.SO_Vent1Vklop
STRSO_Vent2Vklop | DIGITAL | IOD_STR | STR:.SO_Vent2Vklop
STRSO_Vent3Vklop | DIGITAL | IOD_STR | STR:.SO_Vent3Vklop
STRSO_Vent4Vklop | DIGITAL | IOD_STR | STR:.SO_Vent4Vklop
STRSO_Vent5Vklop | DIGITAL | IOD_STR | STR:.SO_Vent5Vklop
STRSO_Vent6Vklop | DIGITAL | IOD_STR | STR:.SO_Vent6Vklop
STRTEgrelecNaTemp | DIGITAL | IOD_STR | STR:.TEgrelecNaTemp
STRTEgrelecTempVklop | DIGITAL | IOD_STR | STR:.TEgrelecTempVklop
STRTempTSprevisoka | DIGITAL | IOD_STR | STR:.TempTSprevisoka
STRToplPostHKcrpalkaON | DIGITAL | IOD_STR | STR:.ToplPost.HKcrpalkaON
STRToplPostHKcrpDnevniRezim | DIGITAL | IOD_STR | STR:.ToplPost.HKcrpDnevniRezim
STRToplPostHKcrpNocniRezim | DIGITAL | IOD_STR | STR:.ToplPost.HKcrpNocniRezim
STRToplPostHKrocniRezim | DIGITAL | IOD_STR | STR:.ToplPost.HKrocniRezim
STRToplPostSkupnaNapaka | DIGITAL | IOD_STR | STR:.ToplPost.SkupnaNapaka
STRToplPostTVcrpalkaON | DIGITAL | IOD_STR | STR:.ToplPost.TVcrpalkaON
STRToplPostTVrocniRezim | DIGITAL | IOD_STR | STR:.ToplPost.TVrocniRezim
STRToplPostErrors0 | DIGITAL | IOD_STR | STR:.ToplPostErrors[0]
STRToplPostErrors10 | DIGITAL | IOD_STR | STR:.ToplPostErrors[10]
STRToplPostErrors11 | DIGITAL | IOD_STR | STR:.ToplPostErrors[11]
STRToplPostErrors12 | DIGITAL | IOD_STR | STR:.ToplPostErrors[12]
STRToplPostErrors13 | DIGITAL | IOD_STR | STR:.ToplPostErrors[13]
STRToplPostErrors14 | DIGITAL | IOD_STR | STR:.ToplPostErrors[14]
STRToplPostErrors15 | DIGITAL | IOD_STR | STR:.ToplPostErrors[15]
STRToplPostErrors16 | DIGITAL | IOD_STR | STR:.ToplPostErrors[16]
STRToplPostErrors17 | DIGITAL | IOD_STR | STR:.ToplPostErrors[17]
STRToplPostErrors1 | DIGITAL | IOD_STR | STR:.ToplPostErrors[1]
STRToplPostErrors2 | DIGITAL | IOD_STR | STR:.ToplPostErrors[2]
STRToplPostErrors3 | DIGITAL | IOD_STR | STR:.ToplPostErrors[3]
STRToplPostErrors4 | DIGITAL | IOD_STR | STR:.ToplPostErrors[4]
STRToplPostErrors5 | DIGITAL | IOD_STR | STR:.ToplPostErrors[5]
STRToplPostErrors6 | DIGITAL | IOD_STR | STR:.ToplPostErrors[6]
STRToplPostErrors7 | DIGITAL | IOD_STR | STR:.ToplPostErrors[7]
STRToplPostErrors8 | DIGITAL | IOD_STR | STR:.ToplPostErrors[8]
STRToplPostErrors9 | DIGITAL | IOD_STR | STR:.ToplPostErrors[9]
STRTYventilNaTemp1 | DIGITAL | IOD_STR | STR:.TYventilNaTemp[1]
STRTYventilNaTemp2 | DIGITAL | IOD_STR | STR:.TYventilNaTemp[2]
STRTYventilNaTemp3 | DIGITAL | IOD_STR | STR:.TYventilNaTemp[3]
STRTYventilNaTemp4 | DIGITAL | IOD_STR | STR:.TYventilNaTemp[4]
STRUserLoggedIn | DIGITAL | IOD_STR | STR:.UserLoggedIn
STRVentilatorOnOff1 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[1]
STRVentilatorOnOff2 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[2]
STRVentilatorOnOff3 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[3]
STRVentilatorOnOff4 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[4]
STRVentilatorOnOff5 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[5]
STRVentilatorOnOff6 | DIGITAL | IOD_STR | STR:.VentilatorOnOff[6]
STRVklopSCFBNapaka10 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[10]
STRVklopSCFBNapaka11 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[11]
STRVklopSCFBNapaka12 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[12]
STRVklopSCFBNapaka13 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[13]
STRVklopSCFBNapaka14 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[14]
STRVklopSCFBNapaka15 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[15]
STRVklopSCFBNapaka16 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[16]
STRVklopSCFBNapaka17 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[17]
STRVklopSCFBNapaka18 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[18]
STRVklopSCFBNapaka19 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[19]
STRVklopSCFBNapaka1 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[1]
STRVklopSCFBNapaka20 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[20]
STRVklopSCFBNapaka21 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[21]
STRVklopSCFBNapaka22 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[22]
STRVklopSCFBNapaka23 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[23]
STRVklopSCFBNapaka24 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[24]
STRVklopSCFBNapaka25 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[25]
STRVklopSCFBNapaka2 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[2]
STRVklopSCFBNapaka3 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[3]
STRVklopSCFBNapaka4 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[4]
STRVklopSCFBNapaka5 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[5]
STRVklopSCFBNapaka6 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[6]
STRVklopSCFBNapaka7 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[7]
STRVklopSCFBNapaka8 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[8]
STRVklopSCFBNapaka9 | DIGITAL | IOD_STR | STR:.VklopSCFBNapaka[9]
STRXVH_AlarmOn | DIGITAL | IOD_STR | STR:.XVH_AlarmOn
STRXVH_IzklopVsehLuci | DIGITAL | IOD_STR | STR:.XVH_IzklopVsehLuci
STRXVH_VklopVsehLuci | DIGITAL | IOD_STR | STR:.XVH_VklopVsehLuci
STRPrenasanjeUrnikovAktivno | DIGITAL | IOD_STR | STR:.PrenasanjeUrnikovAktivno
STRPrenasanjeUrnikovAktivno1 | DIGITAL | IOD_STR | STR:.PrenasanjeUrnikovAktivno1
STRCrpalkeGrfsGalAlarmAktiven | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.AlarmAktiven
STRCrpalkeGrfsGalDeluje | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.Deluje
STRCrpalkeGrfsGalLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.LocalMode
STRCrpalkeGrfsGalRemoteON | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.RemoteON
STRCrpalkeGrfsGalReset2handkWhValues | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.Reset2handkWhValues
STRCrpalkeGrfsGalResetAlarm | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.ResetAlarm
STRCrpalkeGrfsGalResetAlarmLog | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.ResetAlarmLog
STRCrpalkeGrfsGalResetDevice | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.ResetDevice
STRCrpalkeGrfsGalSetAutomatic | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetAutomatic
STRCrpalkeGrfsGalSetConstFreqMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetConstFreqMode
STRCrpalkeGrfsGalSetConstPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetConstPress
STRCrpalkeGrfsGalSetLocalMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetLocalMode
STRCrpalkeGrfsGalSetMaxRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetMaxRunMode
STRCrpalkeGrfsGalSetMinRunMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetMinRunMode
STRCrpalkeGrfsGalSetPropPress | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetPropPress
STRCrpalkeGrfsGalSetReference | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetReference
STRCrpalkeGrfsGalSetRemoteMode | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetRemoteMode
STRCrpalkeGrfsGalSetTwinModeAlt | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetTwinModeAlt
STRCrpalkeGrfsGalSetTwinModeSpare | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetTwinModeSpare
STRCrpalkeGrfsGalSetTwinModeSync | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.SetTwinModeSync
STRCrpalkeGrfsGalStart | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.Start
STRCrpalkeGrfsGalStop | DIGITAL | IOD_STR | STR:.CrpalkeGrfsGal.Stop
STRDI_rezerva10_2 | DIGITAL | IOD_STR | STR:.DI_rezerva10_2
STRDI_rezerva10_7 | DIGITAL | IOD_STR | STR:.DI_rezerva10_7
STRDI_rezerva11_4 | DIGITAL | IOD_STR | STR:.DI_rezerva11_4
STRDI_rezerva14_0 | DIGITAL | IOD_STR | STR:.DI_rezerva14_0
STRDI_rezerva14_2 | DIGITAL | IOD_STR | STR:.DI_rezerva14_2
STRDI_rezerva14_3 | DIGITAL | IOD_STR | STR:.DI_rezerva14_3
STRDI_rezerva14_4 | DIGITAL | IOD_STR | STR:.DI_rezerva14_4
STRDI_rezerva14_5 | DIGITAL | IOD_STR | STR:.DI_rezerva14_5
STRDI_rezerva14_7 | DIGITAL | IOD_STR | STR:.DI_rezerva14_7
STRDI_rezerva2_4 | DIGITAL | IOD_STR | STR:.DI_rezerva2_4
STRDI_rezerva3_5 | DIGITAL | IOD_STR | STR:.DI_rezerva3_5
STRDIN_AkumTopVodeAUTO | DIGITAL | IOD_STR | STR:.DIN_AkumTopVodeAUTO
STRDIN_CrpHM1AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM1AUTO
STRDIN_CrpHM1kontON | DIGITAL | IOD_STR | STR:.DIN_CrpHM1kontON
STRDIN_CrpHM2AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM2AUTO
STRDIN_CrpHM2kontON | DIGITAL | IOD_STR | STR:.DIN_CrpHM2kontON
STRDIN_CrpHM3AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM3AUTO
STRDIN_CrpHM3kontON | DIGITAL | IOD_STR | STR:.DIN_CrpHM3kontON
STRDIN_CrpHM4AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM4AUTO
STRDIN_CrpHM4kontON | DIGITAL | IOD_STR | STR:.DIN_CrpHM4kontON
STRDIN_CrpHM5AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM5AUTO
STRDIN_CrpHM6AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM6AUTO
STRDIN_CrpHM7AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM7AUTO
STRDIN_CrpHM8AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpHM8AUTO
STRDIN_CrpMN1AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpMN1AUTO
STRDIN_CrpMN1kontON | DIGITAL | IOD_STR | STR:.DIN_CrpMN1kontON
STRDIN_CrpTM10AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM10AUTO
STRDIN_CrpTM11TM12AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM11TM12AUTO
STRDIN_CrpTM11TM12kontON | DIGITAL | IOD_STR | STR:.DIN_CrpTM11TM12kontON
STRDIN_CrpTM1AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM1AUTO
STRDIN_CrpTM2AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM2AUTO
STRDIN_CrpTM3AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM3AUTO
STRDIN_CrpTM4AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM4AUTO
STRDIN_CrpTM5AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM5AUTO
STRDIN_CrpTM6AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM6AUTO
STRDIN_CrpTM7AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM7AUTO
STRDIN_CrpTM8AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM8AUTO
STRDIN_CrpTM9AUTO | DIGITAL | IOD_STR | STR:.DIN_CrpTM9AUTO
STRDIN_GlStikaloDieselON | DIGITAL | IOD_STR | STR:.DIN_GlStikaloDieselON
STRDIN_GlStikaloMrezaON | DIGITAL | IOD_STR | STR:.DIN_GlStikaloMrezaON
STRDIN_GlStikaloUpsON | DIGITAL | IOD_STR | STR:.DIN_GlStikaloUpsON
STRDIN_HladStAUTO | DIGITAL | IOD_STR | STR:.DIN_HladStAUTO
STRDIN_Kond1AUTO | DIGITAL | IOD_STR | STR:.DIN_Kond1AUTO
STRDIN_Kond2AUTO | DIGITAL | IOD_STR | STR:.DIN_Kond2AUTO
STRDIN_Kond3AUTO | DIGITAL | IOD_STR | STR:.DIN_Kond3AUTO
STRDIN_Vent1Auto | DIGITAL | IOD_STR | STR:.DIN_Vent1Auto
STRDIN_Vent1kontON | DIGITAL | IOD_STR | STR:.DIN_Vent1kontON
STRDIN_Vent2Auto | DIGITAL | IOD_STR | STR:.DIN_Vent2Auto
STRDIN_Vent2kontON | DIGITAL | IOD_STR | STR:.DIN_Vent2kontON
STRDIN_Vent3Auto | DIGITAL | IOD_STR | STR:.DIN_Vent3Auto
STRDIN_Vent3kontON | DIGITAL | IOD_STR | STR:.DIN_Vent3kontON
STRDIN_Vent4Auto | DIGITAL | IOD_STR | STR:.DIN_Vent4Auto
STRDIN_Vent4kontON | DIGITAL | IOD_STR | STR:.DIN_Vent4kontON
STRDIN_Vent5Auto | DIGITAL | IOD_STR | STR:.DIN_Vent5Auto
STRDIN_Vent5kontON | DIGITAL | IOD_STR | STR:.DIN_Vent5kontON
STRDIN_Vent6Auto | DIGITAL | IOD_STR | STR:.DIN_Vent6Auto
STRDIN_Vent6kontON | DIGITAL | IOD_STR | STR:.DIN_Vent6kontON
STRDO_rezerva0_2 | DIGITAL | IOD_STR | STR:.DO_rezerva0_2
STRDO_rezerva0_3 | DIGITAL | IOD_STR | STR:.DO_rezerva0_3
STRDO_rezerva0_4 | DIGITAL | IOD_STR | STR:.DO_rezerva0_4
STRDO_rezerva0_5 | DIGITAL | IOD_STR | STR:.DO_rezerva0_5
STRDO_rezerva1_3 | DIGITAL | IOD_STR | STR:.DO_rezerva1_3
STRDO_rezerva1_4 | DIGITAL | IOD_STR | STR:.DO_rezerva1_4
STRDO_rezerva1_5 | DIGITAL | IOD_STR | STR:.DO_rezerva1_5
STRDO_rezerva3_4 | DIGITAL | IOD_STR | STR:.DO_rezerva3_4
STRDO_rezerva3_6 | DIGITAL | IOD_STR | STR:.DO_rezerva3_6
STRDO_rezerva4_0 | DIGITAL | IOD_STR | STR:.DO_rezerva4_0
STRPrenosUrnika26 | DIGITAL | IOD_STR | STR:.PrenosUrnika[26]
STRPrenosUrnika27 | DIGITAL | IOD_STR | STR:.PrenosUrnika[27]
STRPrenosUrnika28 | DIGITAL | IOD_STR | STR:.PrenosUrnika[28]
STRPrenosUrnika29 | DIGITAL | IOD_STR | STR:.PrenosUrnika[29]
STRPrenosUrnika30 | DIGITAL | IOD_STR | STR:.PrenosUrnika[30]
STRPrenosUrnika31 | DIGITAL | IOD_STR | STR:.PrenosUrnika[31]
STRPrenosUrnika32 | DIGITAL | IOD_STR | STR:.PrenosUrnika[32]
STRPrenosUrnika33 | DIGITAL | IOD_STR | STR:.PrenosUrnika[33]
STRPrenosUrnika34 | DIGITAL | IOD_STR | STR:.PrenosUrnika[34]
STRPrenosUrnika35 | DIGITAL | IOD_STR | STR:.PrenosUrnika[35]
STRPrenosUrnika36 | DIGITAL | IOD_STR | STR:.PrenosUrnika[36]
STRPrenosUrnika37 | DIGITAL | IOD_STR | STR:.PrenosUrnika[37]
STRPrenosUrnika38 | DIGITAL | IOD_STR | STR:.PrenosUrnika[38]
STRPrenosUrnika39 | DIGITAL | IOD_STR | STR:.PrenosUrnika[39]
STRPrenosUrnika40 | DIGITAL | IOD_STR | STR:.PrenosUrnika[40]
STRPrenosUrnika41 | DIGITAL | IOD_STR | STR:.PrenosUrnika[41]
STRPrenosUrnika42 | DIGITAL | IOD_STR | STR:.PrenosUrnika[42]
STRPrenosUrnika43 | DIGITAL | IOD_STR | STR:.PrenosUrnika[43]
STRPrenosUrnika44 | DIGITAL | IOD_STR | STR:.PrenosUrnika[44]
STRPrenosUrnika45 | DIGITAL | IOD_STR | STR:.PrenosUrnika[45]
STRPrenosUrnika46 | DIGITAL | IOD_STR | STR:.PrenosUrnika[46]
STRPrenosUrnika47 | DIGITAL | IOD_STR | STR:.PrenosUrnika[47]
STRPrenosUrnika48 | DIGITAL | IOD_STR | STR:.PrenosUrnika[48]
STRPrenosUrnika49 | DIGITAL | IOD_STR | STR:.PrenosUrnika[49]
STRPrenosUrnika50 | DIGITAL | IOD_STR | STR:.PrenosUrnika[50]
STRPrenosUrnika51 | DIGITAL | IOD_STR | STR:.PrenosUrnika[51]
STRPrenosUrnika52 | DIGITAL | IOD_STR | STR:.PrenosUrnika[52]
STRPrenosUrnika53 | DIGITAL | IOD_STR | STR:.PrenosUrnika[53]
STRPrenosUrnika54 | DIGITAL | IOD_STR | STR:.PrenosUrnika[54]
STRPrenosUrnika55 | DIGITAL | IOD_STR | STR:.PrenosUrnika[55]
STRPrenosUrnika56 | DIGITAL | IOD_STR | STR:.PrenosUrnika[56]
STRPrenosUrnika57 | DIGITAL | IOD_STR | STR:.PrenosUrnika[57]
STRPrenosUrnika58 | DIGITAL | IOD_STR | STR:.PrenosUrnika[58]
STRPrenosUrnika59 | DIGITAL | IOD_STR | STR:.PrenosUrnika[59]
STRPrenosUrnika60 | DIGITAL | IOD_STR | STR:.PrenosUrnika[60]
STRPrenosUrnika61 | DIGITAL | IOD_STR | STR:.PrenosUrnika[61]
STRPrenosUrnika62 | DIGITAL | IOD_STR | STR:.PrenosUrnika[62]
STRPrenosUrnika63 | DIGITAL | IOD_STR | STR:.PrenosUrnika[63]
STRPrenosUrnika64 | DIGITAL | IOD_STR | STR:.PrenosUrnika[64]
STRPrenosUrnika65 | DIGITAL | IOD_STR | STR:.PrenosUrnika[65]
STRPrenosUrnika66 | DIGITAL | IOD_STR | STR:.PrenosUrnika[66]
STRPrenosUrnika67 | DIGITAL | IOD_STR | STR:.PrenosUrnika[67]
STRPrenosUrnika68 | DIGITAL | IOD_STR | STR:.PrenosUrnika[68]
STRPrenosUrnika69 | DIGITAL | IOD_STR | STR:.PrenosUrnika[69]
STRPrenosUrnika70 | DIGITAL | IOD_STR | STR:.PrenosUrnika[70]
STRPrenosUrnika71 | DIGITAL | IOD_STR | STR:.PrenosUrnika[71]
STRPrenosUrnika72 | DIGITAL | IOD_STR | STR:.PrenosUrnika[72]
STRPrenosUrnika73 | DIGITAL | IOD_STR | STR:.PrenosUrnika[73]
STRPrenosUrnika74 | DIGITAL | IOD_STR | STR:.PrenosUrnika[74]
STRPrenosUrnika75 | DIGITAL | IOD_STR | STR:.PrenosUrnika[75]
STRPrenosUrnika76 | DIGITAL | IOD_STR | STR:.PrenosUrnika[76]
STRPrenosUrnika77 | DIGITAL | IOD_STR | STR:.PrenosUrnika[77]
STRPrenosUrnika78 | DIGITAL | IOD_STR | STR:.PrenosUrnika[78]
STRPrenosUrnika79 | DIGITAL | IOD_STR | STR:.PrenosUrnika[79]
STRPrenosUrnika80 | DIGITAL | IOD_STR | STR:.PrenosUrnika[80]
STRPrenosUrnika81 | DIGITAL | IOD_STR | STR:.PrenosUrnika[81]
STRPrenosUrnika82 | DIGITAL | IOD_STR | STR:.PrenosUrnika[82]
STRPrenosUrnika83 | DIGITAL | IOD_STR | STR:.PrenosUrnika[83]
STRPrenosUrnika84 | DIGITAL | IOD_STR | STR:.PrenosUrnika[84]
STRPrenosUrnika85 | DIGITAL | IOD_STR | STR:.PrenosUrnika[85]
STRPrenosUrnika86 | DIGITAL | IOD_STR | STR:.PrenosUrnika[86]
STRPrenosUrnika87 | DIGITAL | IOD_STR | STR:.PrenosUrnika[87]
STRPrenosUrnika88 | DIGITAL | IOD_STR | STR:.PrenosUrnika[88]
STRPrenosUrnika89 | DIGITAL | IOD_STR | STR:.PrenosUrnika[89]
STRPrenosUrnika90 | DIGITAL | IOD_STR | STR:.PrenosUrnika[90]
STRPrenosUrnika91 | DIGITAL | IOD_STR | STR:.PrenosUrnika[91]
STRPrenosUrnika92 | DIGITAL | IOD_STR | STR:.PrenosUrnika[92]
STRPrenosUrnika93 | DIGITAL | IOD_STR | STR:.PrenosUrnika[93]
STRPrenosUrnika94 | DIGITAL | IOD_STR | STR:.PrenosUrnika[94]
STRPrenosUrnika95 | DIGITAL | IOD_STR | STR:.PrenosUrnika[95]
STRPrenosUrnika96 | DIGITAL | IOD_STR | STR:.PrenosUrnika[96]
STRRazsvRocnoEnaLuc10 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[10]
STRRazsvRocnoEnaLuc11 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[11]
STRRazsvRocnoEnaLuc12 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[12]
STRRazsvRocnoEnaLuc13 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[13]
STRRazsvRocnoEnaLuc14 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[14]
STRRazsvRocnoEnaLuc15 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[15]
STRRazsvRocnoEnaLuc16 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[16]
STRRazsvRocnoEnaLuc17 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[17]
STRRazsvRocnoEnaLuc18 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[18]
STRRazsvRocnoEnaLuc19 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[19]
STRRazsvRocnoEnaLuc1 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[1]
STRRazsvRocnoEnaLuc20 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[20]
STRRazsvRocnoEnaLuc21 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[21]
STRRazsvRocnoEnaLuc22 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[22]
STRRazsvRocnoEnaLuc23 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[23]
STRRazsvRocnoEnaLuc24 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[24]
STRRazsvRocnoEnaLuc25 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[25]
STRRazsvRocnoEnaLuc2 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[2]
STRRazsvRocnoEnaLuc3 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[3]
STRRazsvRocnoEnaLuc4 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[4]
STRRazsvRocnoEnaLuc5 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[5]
STRRazsvRocnoEnaLuc6 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[6]
STRRazsvRocnoEnaLuc7 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[7]
STRRazsvRocnoEnaLuc8 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[8]
STRRazsvRocnoEnaLuc9 | DIGITAL | IOD_STR | STR:.RazsvRocnoEnaLuc[9]
STRXVH_CrpalkaGrfsPair | DIGITAL | IOD_STR | STR:.XVH_CrpalkaGrfsPair
STRXVH_CrpGrfsCommErr | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsCommErr
STRXVH_CrpGrfsON10 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[10]
STRXVH_CrpGrfsON11 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[11]
STRXVH_CrpGrfsON12 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[12]
STRXVH_CrpGrfsON13 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[13]
STRXVH_CrpGrfsON14 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[14]
STRXVH_CrpGrfsON1 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[1]
STRXVH_CrpGrfsON2 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[2]
STRXVH_CrpGrfsON3 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[3]
STRXVH_CrpGrfsON4 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[4]
STRXVH_CrpGrfsON5 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[5]
STRXVH_CrpGrfsON6 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[6]
STRXVH_CrpGrfsON7 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[7]
STRXVH_CrpGrfsON8 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[8]
STRXVH_CrpGrfsON9 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsON[9]
STRXVH_CrpGrfsPIDreset | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsPIDreset
STRXVH_CrpGrfsVisibleData10 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[10]
STRXVH_CrpGrfsVisibleData11 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[11]
STRXVH_CrpGrfsVisibleData12 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[12]
STRXVH_CrpGrfsVisibleData13 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[13]
STRXVH_CrpGrfsVisibleData14 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[14]
STRXVH_CrpGrfsVisibleData15 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[15]
STRXVH_CrpGrfsVisibleData16 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[16]
STRXVH_CrpGrfsVisibleData1 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[1]
STRXVH_CrpGrfsVisibleData2 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[2]
STRXVH_CrpGrfsVisibleData3 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[3]
STRXVH_CrpGrfsVisibleData4 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[4]
STRXVH_CrpGrfsVisibleData5 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[5]
STRXVH_CrpGrfsVisibleData6 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[6]
STRXVH_CrpGrfsVisibleData7 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[7]
STRXVH_CrpGrfsVisibleData8 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[8]
STRXVH_CrpGrfsVisibleData9 | DIGITAL | IOD_STR | STR:.XVH_CrpGrfsVisibleData[9]
STRXVH_CrpGrundfosNaCas | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosNaCas
STRXVH_CrpGrundfosNaTlak | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosNaTlak
STRXVH_CrpGrundfosON | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosON
STRXVH_CrpGrundfosResetAlarm | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosResetAlarm
STRXVH_CrpGrundfosResetAlarmLog | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosResetAlarmLog
STRXVH_CrpGrundfosSetRef | DIGITAL | IOD_STR | STR:.XVH_CrpGrundfosSetRef
STRXVH_RazsvOnOff | DIGITAL | IOD_STR | STR:.XVH_RazsvOnOff
STRXVH_setCircNum1 | DIGITAL | IOD_STR | STR:.XVH_setCircNum[1]
STRXVH_setCircNum2 | DIGITAL | IOD_STR | STR:.XVH_setCircNum[2]
STRXVH_setCircNum3 | DIGITAL | IOD_STR | STR:.XVH_setCircNum[3]
STRXVH_setCircNum4 | DIGITAL | IOD_STR | STR:.XVH_setCircNum[4]
STRXVH_setCircNum5 | DIGITAL | IOD_STR | STR:.XVH_setCircNum[5]
STRXVH_UrnikNalozi | DIGITAL | IOD_STR | STR:.XVH_UrnikNalozi
STRXVH_UrnikNonStop | DIGITAL | IOD_STR | STR:.XVH_UrnikNonStop
STRXVH_UrnikPotrdiVpis | DIGITAL | IOD_STR | STR:.XVH_UrnikPotrdiVpis
STRXVH_UrnikPreklicVpisa | DIGITAL | IOD_STR | STR:.XVH_UrnikPreklicVpisa
STRXVH_UrnikShrani | DIGITAL | IOD_STR | STR:.XVH_UrnikShrani
STRXVH_VpisUrnika | DIGITAL | IOD_STR | STR:.XVH_VpisUrnika
STRErrCommScada2 | DIGITAL | IOD_STR | STR:.ErrCommScada2
STRComSCADA2 | DIGITAL | IOD_STR | STR:.ComSCADA2
STRComSCADA3 | DIGITAL | IOD_STR | STR:.ComSCADA3
STRCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Dnevne_energija_scada1
STRCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Dnevne_energija_scada2
STRCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Tedenska_energija_scada1
STRCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Tedenska_energija_scada2
STRCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Mesecna_energija_scada1
STRCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_STR | STR:.Circ_Vpis_Mesecna_energija_scada2
STRCrpalkeDnfs1PreklopkaMode | INT | IOD_STR | STR:.CrpalkeDnfs[1].PreklopkaMode
STRCrpalkeDnfs1StarterStatus0do7 | INT | IOD_STR | STR:.CrpalkeDnfs[1].StarterStatus0do7 | BYTE
STRCrpalkeDnfs1StatusCrpalke | INT | IOD_STR | STR:.CrpalkeDnfs[1].StatusCrpalke | BYTE
STRCrpalkeDnfs1StatusKontaktor | INT | IOD_STR | STR:.CrpalkeDnfs[1].StatusKontaktor
STRCrpalkeDnfs2PreklopkaMode | INT | IOD_STR | STR:.CrpalkeDnfs[2].PreklopkaMode
STRCrpalkeDnfs2StarterStatus0do7 | INT | IOD_STR | STR:.CrpalkeDnfs[2].StarterStatus0do7 | BYTE
STRCrpalkeDnfs2StatusCrpalke | INT | IOD_STR | STR:.CrpalkeDnfs[2].StatusCrpalke | BYTE
STRCrpalkeDnfs2StatusKontaktor | INT | IOD_STR | STR:.CrpalkeDnfs[2].StatusKontaktor
STRCrpalkeDnfs3PreklopkaMode | INT | IOD_STR | STR:.CrpalkeDnfs[3].PreklopkaMode
STRCrpalkeDnfs3StarterStatus0do7 | INT | IOD_STR | STR:.CrpalkeDnfs[3].StarterStatus0do7 | BYTE
STRCrpalkeDnfs3StatusCrpalke | INT | IOD_STR | STR:.CrpalkeDnfs[3].StatusCrpalke | BYTE
STRCrpalkeDnfs3StatusKontaktor | INT | IOD_STR | STR:.CrpalkeDnfs[3].StatusKontaktor
STRCrpalkeDnfs4PreklopkaMode | INT | IOD_STR | STR:.CrpalkeDnfs[4].PreklopkaMode
STRCrpalkeDnfs4StarterStatus0do7 | INT | IOD_STR | STR:.CrpalkeDnfs[4].StarterStatus0do7 | BYTE
STRCrpalkeDnfs4StatusCrpalke | INT | IOD_STR | STR:.CrpalkeDnfs[4].StatusCrpalke | BYTE
STRCrpalkeDnfs4StatusKontaktor | INT | IOD_STR | STR:.CrpalkeDnfs[4].StatusKontaktor
STRCrpalkeGrfs10AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmActiveCode
STRCrpalkeGrfs10AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmCodeLog1
STRCrpalkeGrfs10AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmCodeLog2
STRCrpalkeGrfs10AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmCodeLog3
STRCrpalkeGrfs10AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmCodeLog4
STRCrpalkeGrfs10AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmCodeLog5
STRCrpalkeGrfs10AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[0]
STRCrpalkeGrfs10AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[10]
STRCrpalkeGrfs10AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[11]
STRCrpalkeGrfs10AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[12]
STRCrpalkeGrfs10AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[13]
STRCrpalkeGrfs10AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[14]
STRCrpalkeGrfs10AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[15]
STRCrpalkeGrfs10AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[16]
STRCrpalkeGrfs10AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[1]
STRCrpalkeGrfs10AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[2]
STRCrpalkeGrfs10AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[3]
STRCrpalkeGrfs10AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[4]
STRCrpalkeGrfs10AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[5]
STRCrpalkeGrfs10AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[6]
STRCrpalkeGrfs10AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[7]
STRCrpalkeGrfs10AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[8]
STRCrpalkeGrfs10AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmGroupXVH[9]
STRCrpalkeGrfs10AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmQSD1
STRCrpalkeGrfs10AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmQSD2
STRCrpalkeGrfs10AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmStart1
STRCrpalkeGrfs10AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmStart2
STRCrpalkeGrfs10AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmStop1
STRCrpalkeGrfs10AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmStop2
STRCrpalkeGrfs10AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmStop3
STRCrpalkeGrfs10AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmSurv1
STRCrpalkeGrfs10AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].AlarmSurv2
STRCrpalkeGrfs10ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[10].ControlSource
STRCrpalkeGrfs10ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[10].ExternInputSetup
STRCrpalkeGrfs10ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[10].ExternInputsStatus
STRCrpalkeGrfs10LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].LocalSetupMode1
STRCrpalkeGrfs10PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[10].PreklopkaMode
STRCrpalkeGrfs10Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[10].Relay1setup
STRCrpalkeGrfs10RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].RemoteSetupMode1
STRCrpalkeGrfs10StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[10].StatusCrpalke | BYTE
STRCrpalkeGrfs10StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[10].StatusMode1
STRCrpalkeGrfs10StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[10].StatusMode1co | BYTE
STRCrpalkeGrfs10StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[10].StatusMode1op | BYTE
STRCrpalkeGrfs10StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[10].StatusMode2
STRCrpalkeGrfs10StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[10].StatusMode3
STRCrpalkeGrfs11AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmActiveCode
STRCrpalkeGrfs11AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmCodeLog1
STRCrpalkeGrfs11AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmCodeLog2
STRCrpalkeGrfs11AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmCodeLog3
STRCrpalkeGrfs11AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmCodeLog4
STRCrpalkeGrfs11AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmCodeLog5
STRCrpalkeGrfs11AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[0]
STRCrpalkeGrfs11AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[10]
STRCrpalkeGrfs11AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[11]
STRCrpalkeGrfs11AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[12]
STRCrpalkeGrfs11AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[13]
STRCrpalkeGrfs11AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[14]
STRCrpalkeGrfs11AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[15]
STRCrpalkeGrfs11AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[16]
STRCrpalkeGrfs11AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[1]
STRCrpalkeGrfs11AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[2]
STRCrpalkeGrfs11AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[3]
STRCrpalkeGrfs11AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[4]
STRCrpalkeGrfs11AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[5]
STRCrpalkeGrfs11AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[6]
STRCrpalkeGrfs11AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[7]
STRCrpalkeGrfs11AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[8]
STRCrpalkeGrfs11AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmGroupXVH[9]
STRCrpalkeGrfs11AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmQSD1
STRCrpalkeGrfs11AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmQSD2
STRCrpalkeGrfs11AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmStart1
STRCrpalkeGrfs11AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmStart2
STRCrpalkeGrfs11AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmStop1
STRCrpalkeGrfs11AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmStop2
STRCrpalkeGrfs11AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmStop3
STRCrpalkeGrfs11AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmSurv1
STRCrpalkeGrfs11AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].AlarmSurv2
STRCrpalkeGrfs11ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[11].ControlSource
STRCrpalkeGrfs11ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[11].ExternInputSetup
STRCrpalkeGrfs11ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[11].ExternInputsStatus
STRCrpalkeGrfs11LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].LocalSetupMode1
STRCrpalkeGrfs11PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[11].PreklopkaMode
STRCrpalkeGrfs11Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[11].Relay1setup
STRCrpalkeGrfs11RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].RemoteSetupMode1
STRCrpalkeGrfs11StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[11].StatusCrpalke | BYTE
STRCrpalkeGrfs11StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[11].StatusMode1
STRCrpalkeGrfs11StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[11].StatusMode1co | BYTE
STRCrpalkeGrfs11StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[11].StatusMode1op | BYTE
STRCrpalkeGrfs11StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[11].StatusMode2
STRCrpalkeGrfs11StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[11].StatusMode3
STRCrpalkeGrfs12AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmActiveCode
STRCrpalkeGrfs12AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmCodeLog1
STRCrpalkeGrfs12AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmCodeLog2
STRCrpalkeGrfs12AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmCodeLog3
STRCrpalkeGrfs12AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmCodeLog4
STRCrpalkeGrfs12AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmCodeLog5
STRCrpalkeGrfs12AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[0]
STRCrpalkeGrfs12AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[10]
STRCrpalkeGrfs12AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[11]
STRCrpalkeGrfs12AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[12]
STRCrpalkeGrfs12AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[13]
STRCrpalkeGrfs12AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[14]
STRCrpalkeGrfs12AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[15]
STRCrpalkeGrfs12AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[16]
STRCrpalkeGrfs12AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[1]
STRCrpalkeGrfs12AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[2]
STRCrpalkeGrfs12AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[3]
STRCrpalkeGrfs12AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[4]
STRCrpalkeGrfs12AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[5]
STRCrpalkeGrfs12AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[6]
STRCrpalkeGrfs12AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[7]
STRCrpalkeGrfs12AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[8]
STRCrpalkeGrfs12AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmGroupXVH[9]
STRCrpalkeGrfs12AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmQSD1
STRCrpalkeGrfs12AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmQSD2
STRCrpalkeGrfs12AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmStart1
STRCrpalkeGrfs12AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmStart2
STRCrpalkeGrfs12AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmStop1
STRCrpalkeGrfs12AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmStop2
STRCrpalkeGrfs12AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmStop3
STRCrpalkeGrfs12AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmSurv1
STRCrpalkeGrfs12AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].AlarmSurv2
STRCrpalkeGrfs12ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[12].ControlSource
STRCrpalkeGrfs12ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[12].ExternInputSetup
STRCrpalkeGrfs12ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[12].ExternInputsStatus
STRCrpalkeGrfs12LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].LocalSetupMode1
STRCrpalkeGrfs12PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[12].PreklopkaMode
STRCrpalkeGrfs12Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[12].Relay1setup
STRCrpalkeGrfs12RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].RemoteSetupMode1
STRCrpalkeGrfs12StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[12].StatusCrpalke | BYTE
STRCrpalkeGrfs12StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[12].StatusMode1
STRCrpalkeGrfs12StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[12].StatusMode1co | BYTE
STRCrpalkeGrfs12StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[12].StatusMode1op | BYTE
STRCrpalkeGrfs12StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[12].StatusMode2
STRCrpalkeGrfs12StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[12].StatusMode3
STRCrpalkeGrfs13AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmActiveCode
STRCrpalkeGrfs13AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmCodeLog1
STRCrpalkeGrfs13AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmCodeLog2
STRCrpalkeGrfs13AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmCodeLog3
STRCrpalkeGrfs13AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmCodeLog4
STRCrpalkeGrfs13AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmCodeLog5
STRCrpalkeGrfs13AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[0]
STRCrpalkeGrfs13AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[10]
STRCrpalkeGrfs13AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[11]
STRCrpalkeGrfs13AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[12]
STRCrpalkeGrfs13AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[13]
STRCrpalkeGrfs13AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[14]
STRCrpalkeGrfs13AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[15]
STRCrpalkeGrfs13AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[16]
STRCrpalkeGrfs13AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[1]
STRCrpalkeGrfs13AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[2]
STRCrpalkeGrfs13AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[3]
STRCrpalkeGrfs13AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[4]
STRCrpalkeGrfs13AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[5]
STRCrpalkeGrfs13AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[6]
STRCrpalkeGrfs13AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[7]
STRCrpalkeGrfs13AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[8]
STRCrpalkeGrfs13AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmGroupXVH[9]
STRCrpalkeGrfs13AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmQSD1
STRCrpalkeGrfs13AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmQSD2
STRCrpalkeGrfs13AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmStart1
STRCrpalkeGrfs13AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmStart2
STRCrpalkeGrfs13AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmStop1
STRCrpalkeGrfs13AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmStop2
STRCrpalkeGrfs13AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmStop3
STRCrpalkeGrfs13AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmSurv1
STRCrpalkeGrfs13AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].AlarmSurv2
STRCrpalkeGrfs13ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[13].ControlSource
STRCrpalkeGrfs13ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[13].ExternInputSetup
STRCrpalkeGrfs13ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[13].ExternInputsStatus
STRCrpalkeGrfs13LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].LocalSetupMode1
STRCrpalkeGrfs13PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[13].PreklopkaMode
STRCrpalkeGrfs13Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[13].Relay1setup
STRCrpalkeGrfs13RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].RemoteSetupMode1
STRCrpalkeGrfs13StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[13].StatusCrpalke | BYTE
STRCrpalkeGrfs13StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[13].StatusMode1
STRCrpalkeGrfs13StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[13].StatusMode1co | BYTE
STRCrpalkeGrfs13StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[13].StatusMode1op | BYTE
STRCrpalkeGrfs13StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[13].StatusMode2
STRCrpalkeGrfs13StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[13].StatusMode3
STRCrpalkeGrfs14AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmActiveCode
STRCrpalkeGrfs14AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmCodeLog1
STRCrpalkeGrfs14AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmCodeLog2
STRCrpalkeGrfs14AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmCodeLog3
STRCrpalkeGrfs14AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmCodeLog4
STRCrpalkeGrfs14AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmCodeLog5
STRCrpalkeGrfs14AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[0]
STRCrpalkeGrfs14AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[10]
STRCrpalkeGrfs14AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[11]
STRCrpalkeGrfs14AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[12]
STRCrpalkeGrfs14AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[13]
STRCrpalkeGrfs14AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[14]
STRCrpalkeGrfs14AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[15]
STRCrpalkeGrfs14AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[16]
STRCrpalkeGrfs14AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[1]
STRCrpalkeGrfs14AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[2]
STRCrpalkeGrfs14AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[3]
STRCrpalkeGrfs14AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[4]
STRCrpalkeGrfs14AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[5]
STRCrpalkeGrfs14AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[6]
STRCrpalkeGrfs14AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[7]
STRCrpalkeGrfs14AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[8]
STRCrpalkeGrfs14AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmGroupXVH[9]
STRCrpalkeGrfs14AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmQSD1
STRCrpalkeGrfs14AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmQSD2
STRCrpalkeGrfs14AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmStart1
STRCrpalkeGrfs14AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmStart2
STRCrpalkeGrfs14AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmStop1
STRCrpalkeGrfs14AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmStop2
STRCrpalkeGrfs14AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmStop3
STRCrpalkeGrfs14AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmSurv1
STRCrpalkeGrfs14AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].AlarmSurv2
STRCrpalkeGrfs14ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[14].ControlSource
STRCrpalkeGrfs14ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[14].ExternInputSetup
STRCrpalkeGrfs14ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[14].ExternInputsStatus
STRCrpalkeGrfs14LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].LocalSetupMode1
STRCrpalkeGrfs14PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[14].PreklopkaMode
STRCrpalkeGrfs14Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[14].Relay1setup
STRCrpalkeGrfs14RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].RemoteSetupMode1
STRCrpalkeGrfs14StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[14].StatusCrpalke | BYTE
STRCrpalkeGrfs14StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[14].StatusMode1
STRCrpalkeGrfs14StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[14].StatusMode1co | BYTE
STRCrpalkeGrfs14StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[14].StatusMode1op | BYTE
STRCrpalkeGrfs14StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[14].StatusMode2
STRCrpalkeGrfs14StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[14].StatusMode3
STRCrpalkeGrfs1AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmActiveCode
STRCrpalkeGrfs1AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmCodeLog1
STRCrpalkeGrfs1AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmCodeLog2
STRCrpalkeGrfs1AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmCodeLog3
STRCrpalkeGrfs1AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmCodeLog4
STRCrpalkeGrfs1AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmCodeLog5
STRCrpalkeGrfs1AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[0]
STRCrpalkeGrfs1AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[10]
STRCrpalkeGrfs1AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[11]
STRCrpalkeGrfs1AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[12]
STRCrpalkeGrfs1AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[13]
STRCrpalkeGrfs1AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[14]
STRCrpalkeGrfs1AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[15]
STRCrpalkeGrfs1AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[16]
STRCrpalkeGrfs1AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[1]
STRCrpalkeGrfs1AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[2]
STRCrpalkeGrfs1AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[3]
STRCrpalkeGrfs1AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[4]
STRCrpalkeGrfs1AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[5]
STRCrpalkeGrfs1AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[6]
STRCrpalkeGrfs1AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[7]
STRCrpalkeGrfs1AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[8]
STRCrpalkeGrfs1AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmGroupXVH[9]
STRCrpalkeGrfs1AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmQSD1
STRCrpalkeGrfs1AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmQSD2
STRCrpalkeGrfs1AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmStart1
STRCrpalkeGrfs1AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmStart2
STRCrpalkeGrfs1AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmStop1
STRCrpalkeGrfs1AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmStop2
STRCrpalkeGrfs1AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmStop3
STRCrpalkeGrfs1AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmSurv1
STRCrpalkeGrfs1AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].AlarmSurv2
STRCrpalkeGrfs1ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[1].ControlSource
STRCrpalkeGrfs1ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[1].ExternInputSetup
STRCrpalkeGrfs1ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[1].ExternInputsStatus
STRCrpalkeGrfs1LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].LocalSetupMode1
STRCrpalkeGrfs1PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[1].PreklopkaMode
STRCrpalkeGrfs1Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[1].Relay1setup
STRCrpalkeGrfs1RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].RemoteSetupMode1
STRCrpalkeGrfs1StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[1].StatusCrpalke | BYTE
STRCrpalkeGrfs1StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[1].StatusMode1
STRCrpalkeGrfs1StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[1].StatusMode1co | BYTE
STRCrpalkeGrfs1StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[1].StatusMode1op | BYTE
STRCrpalkeGrfs1StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[1].StatusMode2
STRCrpalkeGrfs1StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[1].StatusMode3
STRCrpalkeGrfs2AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmActiveCode
STRCrpalkeGrfs2AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmCodeLog1
STRCrpalkeGrfs2AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmCodeLog2
STRCrpalkeGrfs2AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmCodeLog3
STRCrpalkeGrfs2AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmCodeLog4
STRCrpalkeGrfs2AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmCodeLog5
STRCrpalkeGrfs2AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[0]
STRCrpalkeGrfs2AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[10]
STRCrpalkeGrfs2AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[11]
STRCrpalkeGrfs2AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[12]
STRCrpalkeGrfs2AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[13]
STRCrpalkeGrfs2AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[14]
STRCrpalkeGrfs2AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[15]
STRCrpalkeGrfs2AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[16]
STRCrpalkeGrfs2AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[1]
STRCrpalkeGrfs2AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[2]
STRCrpalkeGrfs2AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[3]
STRCrpalkeGrfs2AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[4]
STRCrpalkeGrfs2AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[5]
STRCrpalkeGrfs2AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[6]
STRCrpalkeGrfs2AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[7]
STRCrpalkeGrfs2AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[8]
STRCrpalkeGrfs2AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmGroupXVH[9]
STRCrpalkeGrfs2AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmQSD1
STRCrpalkeGrfs2AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmQSD2
STRCrpalkeGrfs2AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmStart1
STRCrpalkeGrfs2AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmStart2
STRCrpalkeGrfs2AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmStop1
STRCrpalkeGrfs2AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmStop2
STRCrpalkeGrfs2AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmStop3
STRCrpalkeGrfs2AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmSurv1
STRCrpalkeGrfs2AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].AlarmSurv2
STRCrpalkeGrfs2ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[2].ControlSource
STRCrpalkeGrfs2ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[2].ExternInputSetup
STRCrpalkeGrfs2ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[2].ExternInputsStatus
STRCrpalkeGrfs2LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].LocalSetupMode1
STRCrpalkeGrfs2PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[2].PreklopkaMode
STRCrpalkeGrfs2Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[2].Relay1setup
STRCrpalkeGrfs2RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].RemoteSetupMode1
STRCrpalkeGrfs2StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[2].StatusCrpalke | BYTE
STRCrpalkeGrfs2StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[2].StatusMode1
STRCrpalkeGrfs2StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[2].StatusMode1co | BYTE
STRCrpalkeGrfs2StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[2].StatusMode1op | BYTE
STRCrpalkeGrfs2StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[2].StatusMode2
STRCrpalkeGrfs2StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[2].StatusMode3
STRCrpalkeGrfs3AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmActiveCode
STRCrpalkeGrfs3AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmCodeLog1
STRCrpalkeGrfs3AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmCodeLog2
STRCrpalkeGrfs3AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmCodeLog3
STRCrpalkeGrfs3AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmCodeLog4
STRCrpalkeGrfs3AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmCodeLog5
STRCrpalkeGrfs3AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[0]
STRCrpalkeGrfs3AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[10]
STRCrpalkeGrfs3AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[11]
STRCrpalkeGrfs3AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[12]
STRCrpalkeGrfs3AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[13]
STRCrpalkeGrfs3AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[14]
STRCrpalkeGrfs3AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[15]
STRCrpalkeGrfs3AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[16]
STRCrpalkeGrfs3AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[1]
STRCrpalkeGrfs3AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[2]
STRCrpalkeGrfs3AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[3]
STRCrpalkeGrfs3AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[4]
STRCrpalkeGrfs3AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[5]
STRCrpalkeGrfs3AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[6]
STRCrpalkeGrfs3AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[7]
STRCrpalkeGrfs3AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[8]
STRCrpalkeGrfs3AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmGroupXVH[9]
STRCrpalkeGrfs3AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmQSD1
STRCrpalkeGrfs3AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmQSD2
STRCrpalkeGrfs3AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmStart1
STRCrpalkeGrfs3AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmStart2
STRCrpalkeGrfs3AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmStop1
STRCrpalkeGrfs3AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmStop2
STRCrpalkeGrfs3AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmStop3
STRCrpalkeGrfs3AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmSurv1
STRCrpalkeGrfs3AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].AlarmSurv2
STRCrpalkeGrfs3ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[3].ControlSource
STRCrpalkeGrfs3ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[3].ExternInputSetup
STRCrpalkeGrfs3ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[3].ExternInputsStatus
STRCrpalkeGrfs3LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].LocalSetupMode1
STRCrpalkeGrfs3PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[3].PreklopkaMode
STRCrpalkeGrfs3Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[3].Relay1setup
STRCrpalkeGrfs3RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].RemoteSetupMode1
STRCrpalkeGrfs3StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[3].StatusCrpalke | BYTE
STRCrpalkeGrfs3StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[3].StatusMode1
STRCrpalkeGrfs3StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[3].StatusMode1co | BYTE
STRCrpalkeGrfs3StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[3].StatusMode1op | BYTE
STRCrpalkeGrfs3StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[3].StatusMode2
STRCrpalkeGrfs3StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[3].StatusMode3
STRCrpalkeGrfs4AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmActiveCode
STRCrpalkeGrfs4AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmCodeLog1
STRCrpalkeGrfs4AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmCodeLog2
STRCrpalkeGrfs4AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmCodeLog3
STRCrpalkeGrfs4AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmCodeLog4
STRCrpalkeGrfs4AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmCodeLog5
STRCrpalkeGrfs4AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[0]
STRCrpalkeGrfs4AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[10]
STRCrpalkeGrfs4AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[11]
STRCrpalkeGrfs4AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[12]
STRCrpalkeGrfs4AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[13]
STRCrpalkeGrfs4AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[14]
STRCrpalkeGrfs4AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[15]
STRCrpalkeGrfs4AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[16]
STRCrpalkeGrfs4AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[1]
STRCrpalkeGrfs4AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[2]
STRCrpalkeGrfs4AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[3]
STRCrpalkeGrfs4AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[4]
STRCrpalkeGrfs4AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[5]
STRCrpalkeGrfs4AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[6]
STRCrpalkeGrfs4AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[7]
STRCrpalkeGrfs4AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[8]
STRCrpalkeGrfs4AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmGroupXVH[9]
STRCrpalkeGrfs4AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmQSD1
STRCrpalkeGrfs4AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmQSD2
STRCrpalkeGrfs4AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmStart1
STRCrpalkeGrfs4AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmStart2
STRCrpalkeGrfs4AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmStop1
STRCrpalkeGrfs4AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmStop2
STRCrpalkeGrfs4AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmStop3
STRCrpalkeGrfs4AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmSurv1
STRCrpalkeGrfs4AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].AlarmSurv2
STRCrpalkeGrfs4ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[4].ControlSource
STRCrpalkeGrfs4ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[4].ExternInputSetup
STRCrpalkeGrfs4ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[4].ExternInputsStatus
STRCrpalkeGrfs4LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].LocalSetupMode1
STRCrpalkeGrfs4PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[4].PreklopkaMode
STRCrpalkeGrfs4Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[4].Relay1setup
STRCrpalkeGrfs4RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].RemoteSetupMode1
STRCrpalkeGrfs4StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[4].StatusCrpalke | BYTE
STRCrpalkeGrfs4StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[4].StatusMode1
STRCrpalkeGrfs4StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[4].StatusMode1co | BYTE
STRCrpalkeGrfs4StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[4].StatusMode1op | BYTE
STRCrpalkeGrfs4StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[4].StatusMode2
STRCrpalkeGrfs4StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[4].StatusMode3
STRCrpalkeGrfs5AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmActiveCode
STRCrpalkeGrfs5AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmCodeLog1
STRCrpalkeGrfs5AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmCodeLog2
STRCrpalkeGrfs5AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmCodeLog3
STRCrpalkeGrfs5AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmCodeLog4
STRCrpalkeGrfs5AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmCodeLog5
STRCrpalkeGrfs5AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[0]
STRCrpalkeGrfs5AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[10]
STRCrpalkeGrfs5AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[11]
STRCrpalkeGrfs5AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[12]
STRCrpalkeGrfs5AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[13]
STRCrpalkeGrfs5AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[14]
STRCrpalkeGrfs5AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[15]
STRCrpalkeGrfs5AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[16]
STRCrpalkeGrfs5AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[1]
STRCrpalkeGrfs5AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[2]
STRCrpalkeGrfs5AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[3]
STRCrpalkeGrfs5AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[4]
STRCrpalkeGrfs5AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[5]
STRCrpalkeGrfs5AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[6]
STRCrpalkeGrfs5AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[7]
STRCrpalkeGrfs5AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[8]
STRCrpalkeGrfs5AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmGroupXVH[9]
STRCrpalkeGrfs5AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmQSD1
STRCrpalkeGrfs5AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmQSD2
STRCrpalkeGrfs5AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmStart1
STRCrpalkeGrfs5AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmStart2
STRCrpalkeGrfs5AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmStop1
STRCrpalkeGrfs5AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmStop2
STRCrpalkeGrfs5AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmStop3
STRCrpalkeGrfs5AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmSurv1
STRCrpalkeGrfs5AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].AlarmSurv2
STRCrpalkeGrfs5ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[5].ControlSource
STRCrpalkeGrfs5ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[5].ExternInputSetup
STRCrpalkeGrfs5ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[5].ExternInputsStatus
STRCrpalkeGrfs5LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].LocalSetupMode1
STRCrpalkeGrfs5PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[5].PreklopkaMode
STRCrpalkeGrfs5Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[5].Relay1setup
STRCrpalkeGrfs5RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].RemoteSetupMode1
STRCrpalkeGrfs5StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[5].StatusCrpalke | BYTE
STRCrpalkeGrfs5StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[5].StatusMode1
STRCrpalkeGrfs5StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[5].StatusMode1co | BYTE
STRCrpalkeGrfs5StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[5].StatusMode1op | BYTE
STRCrpalkeGrfs5StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[5].StatusMode2
STRCrpalkeGrfs5StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[5].StatusMode3
STRCrpalkeGrfs6AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmActiveCode
STRCrpalkeGrfs6AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmCodeLog1
STRCrpalkeGrfs6AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmCodeLog2
STRCrpalkeGrfs6AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmCodeLog3
STRCrpalkeGrfs6AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmCodeLog4
STRCrpalkeGrfs6AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmCodeLog5
STRCrpalkeGrfs6AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[0]
STRCrpalkeGrfs6AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[10]
STRCrpalkeGrfs6AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[11]
STRCrpalkeGrfs6AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[12]
STRCrpalkeGrfs6AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[13]
STRCrpalkeGrfs6AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[14]
STRCrpalkeGrfs6AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[15]
STRCrpalkeGrfs6AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[16]
STRCrpalkeGrfs6AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[1]
STRCrpalkeGrfs6AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[2]
STRCrpalkeGrfs6AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[3]
STRCrpalkeGrfs6AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[4]
STRCrpalkeGrfs6AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[5]
STRCrpalkeGrfs6AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[6]
STRCrpalkeGrfs6AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[7]
STRCrpalkeGrfs6AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[8]
STRCrpalkeGrfs6AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmGroupXVH[9]
STRCrpalkeGrfs6AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmQSD1
STRCrpalkeGrfs6AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmQSD2
STRCrpalkeGrfs6AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmStart1
STRCrpalkeGrfs6AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmStart2
STRCrpalkeGrfs6AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmStop1
STRCrpalkeGrfs6AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmStop2
STRCrpalkeGrfs6AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmStop3
STRCrpalkeGrfs6AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmSurv1
STRCrpalkeGrfs6AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].AlarmSurv2
STRCrpalkeGrfs6ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[6].ControlSource
STRCrpalkeGrfs6ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[6].ExternInputSetup
STRCrpalkeGrfs6ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[6].ExternInputsStatus
STRCrpalkeGrfs6LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].LocalSetupMode1
STRCrpalkeGrfs6PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[6].PreklopkaMode
STRCrpalkeGrfs6Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[6].Relay1setup
STRCrpalkeGrfs6RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].RemoteSetupMode1
STRCrpalkeGrfs6StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[6].StatusCrpalke | BYTE
STRCrpalkeGrfs6StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[6].StatusMode1
STRCrpalkeGrfs6StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[6].StatusMode1co | BYTE
STRCrpalkeGrfs6StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[6].StatusMode1op | BYTE
STRCrpalkeGrfs6StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[6].StatusMode2
STRCrpalkeGrfs6StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[6].StatusMode3
STRCrpalkeGrfs7AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmActiveCode
STRCrpalkeGrfs7AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmCodeLog1
STRCrpalkeGrfs7AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmCodeLog2
STRCrpalkeGrfs7AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmCodeLog3
STRCrpalkeGrfs7AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmCodeLog4
STRCrpalkeGrfs7AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmCodeLog5
STRCrpalkeGrfs7AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[0]
STRCrpalkeGrfs7AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[10]
STRCrpalkeGrfs7AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[11]
STRCrpalkeGrfs7AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[12]
STRCrpalkeGrfs7AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[13]
STRCrpalkeGrfs7AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[14]
STRCrpalkeGrfs7AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[15]
STRCrpalkeGrfs7AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[16]
STRCrpalkeGrfs7AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[1]
STRCrpalkeGrfs7AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[2]
STRCrpalkeGrfs7AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[3]
STRCrpalkeGrfs7AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[4]
STRCrpalkeGrfs7AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[5]
STRCrpalkeGrfs7AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[6]
STRCrpalkeGrfs7AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[7]
STRCrpalkeGrfs7AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[8]
STRCrpalkeGrfs7AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmGroupXVH[9]
STRCrpalkeGrfs7AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmQSD1
STRCrpalkeGrfs7AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmQSD2
STRCrpalkeGrfs7AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmStart1
STRCrpalkeGrfs7AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmStart2
STRCrpalkeGrfs7AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmStop1
STRCrpalkeGrfs7AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmStop2
STRCrpalkeGrfs7AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmStop3
STRCrpalkeGrfs7AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmSurv1
STRCrpalkeGrfs7AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].AlarmSurv2
STRCrpalkeGrfs7ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[7].ControlSource
STRCrpalkeGrfs7ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[7].ExternInputSetup
STRCrpalkeGrfs7ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[7].ExternInputsStatus
STRCrpalkeGrfs7LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].LocalSetupMode1
STRCrpalkeGrfs7PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[7].PreklopkaMode
STRCrpalkeGrfs7Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[7].Relay1setup
STRCrpalkeGrfs7RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].RemoteSetupMode1
STRCrpalkeGrfs7StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[7].StatusCrpalke | BYTE
STRCrpalkeGrfs7StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[7].StatusMode1
STRCrpalkeGrfs7StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[7].StatusMode1co | BYTE
STRCrpalkeGrfs7StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[7].StatusMode1op | BYTE
STRCrpalkeGrfs7StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[7].StatusMode2
STRCrpalkeGrfs7StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[7].StatusMode3
STRCrpalkeGrfs8AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmActiveCode
STRCrpalkeGrfs8AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmCodeLog1
STRCrpalkeGrfs8AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmCodeLog2
STRCrpalkeGrfs8AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmCodeLog3
STRCrpalkeGrfs8AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmCodeLog4
STRCrpalkeGrfs8AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmCodeLog5
STRCrpalkeGrfs8AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[0]
STRCrpalkeGrfs8AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[10]
STRCrpalkeGrfs8AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[11]
STRCrpalkeGrfs8AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[12]
STRCrpalkeGrfs8AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[13]
STRCrpalkeGrfs8AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[14]
STRCrpalkeGrfs8AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[15]
STRCrpalkeGrfs8AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[16]
STRCrpalkeGrfs8AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[1]
STRCrpalkeGrfs8AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[2]
STRCrpalkeGrfs8AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[3]
STRCrpalkeGrfs8AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[4]
STRCrpalkeGrfs8AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[5]
STRCrpalkeGrfs8AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[6]
STRCrpalkeGrfs8AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[7]
STRCrpalkeGrfs8AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[8]
STRCrpalkeGrfs8AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmGroupXVH[9]
STRCrpalkeGrfs8AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmQSD1
STRCrpalkeGrfs8AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmQSD2
STRCrpalkeGrfs8AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmStart1
STRCrpalkeGrfs8AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmStart2
STRCrpalkeGrfs8AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmStop1
STRCrpalkeGrfs8AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmStop2
STRCrpalkeGrfs8AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmStop3
STRCrpalkeGrfs8AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmSurv1
STRCrpalkeGrfs8AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].AlarmSurv2
STRCrpalkeGrfs8ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[8].ControlSource
STRCrpalkeGrfs8ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[8].ExternInputSetup
STRCrpalkeGrfs8ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[8].ExternInputsStatus
STRCrpalkeGrfs8LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].LocalSetupMode1
STRCrpalkeGrfs8PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[8].PreklopkaMode
STRCrpalkeGrfs8Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[8].Relay1setup
STRCrpalkeGrfs8RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].RemoteSetupMode1
STRCrpalkeGrfs8StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[8].StatusCrpalke | BYTE
STRCrpalkeGrfs8StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[8].StatusMode1
STRCrpalkeGrfs8StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[8].StatusMode1co | BYTE
STRCrpalkeGrfs8StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[8].StatusMode1op | BYTE
STRCrpalkeGrfs8StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[8].StatusMode2
STRCrpalkeGrfs8StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[8].StatusMode3
STRCrpalkeGrfs9AlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmActiveCode
STRCrpalkeGrfs9AlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmCodeLog1
STRCrpalkeGrfs9AlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmCodeLog2
STRCrpalkeGrfs9AlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmCodeLog3
STRCrpalkeGrfs9AlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmCodeLog4
STRCrpalkeGrfs9AlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmCodeLog5
STRCrpalkeGrfs9AlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[0]
STRCrpalkeGrfs9AlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[10]
STRCrpalkeGrfs9AlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[11]
STRCrpalkeGrfs9AlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[12]
STRCrpalkeGrfs9AlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[13]
STRCrpalkeGrfs9AlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[14]
STRCrpalkeGrfs9AlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[15]
STRCrpalkeGrfs9AlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[16]
STRCrpalkeGrfs9AlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[1]
STRCrpalkeGrfs9AlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[2]
STRCrpalkeGrfs9AlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[3]
STRCrpalkeGrfs9AlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[4]
STRCrpalkeGrfs9AlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[5]
STRCrpalkeGrfs9AlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[6]
STRCrpalkeGrfs9AlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[7]
STRCrpalkeGrfs9AlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[8]
STRCrpalkeGrfs9AlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmGroupXVH[9]
STRCrpalkeGrfs9AlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmQSD1
STRCrpalkeGrfs9AlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmQSD2
STRCrpalkeGrfs9AlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmStart1
STRCrpalkeGrfs9AlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmStart2
STRCrpalkeGrfs9AlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmStop1
STRCrpalkeGrfs9AlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmStop2
STRCrpalkeGrfs9AlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmStop3
STRCrpalkeGrfs9AlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmSurv1
STRCrpalkeGrfs9AlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].AlarmSurv2
STRCrpalkeGrfs9ControlSource | INT | IOD_STR | STR:.CrpalkeGrfs[9].ControlSource
STRCrpalkeGrfs9ExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfs[9].ExternInputSetup
STRCrpalkeGrfs9ExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfs[9].ExternInputsStatus
STRCrpalkeGrfs9LocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].LocalSetupMode1
STRCrpalkeGrfs9PreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfs[9].PreklopkaMode
STRCrpalkeGrfs9Relay1setup | INT | IOD_STR | STR:.CrpalkeGrfs[9].Relay1setup
STRCrpalkeGrfs9RemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].RemoteSetupMode1
STRCrpalkeGrfs9StatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfs[9].StatusCrpalke | BYTE
STRCrpalkeGrfs9StatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfs[9].StatusMode1
STRCrpalkeGrfs9StatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfs[9].StatusMode1co | BYTE
STRCrpalkeGrfs9StatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfs[9].StatusMode1op | BYTE
STRCrpalkeGrfs9StatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfs[9].StatusMode2
STRCrpalkeGrfs9StatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfs[9].StatusMode3
STRDateTimeDan | INT | IOD_STR | STR:.DateTime.Dan | BYTE
STRDateTimeLeto | INT | IOD_STR | STR:.DateTime.Leto | BYTE
STRDateTimeMesec | INT | IOD_STR | STR:.DateTime.Mesec | BYTE
STRDateTimeMinuta | INT | IOD_STR | STR:.DateTime.Minuta | BYTE
STRDateTimeSekunda | INT | IOD_STR | STR:.DateTime.Sekunda | BYTE
STRDateTimeUra | INT | IOD_STR | STR:.DateTime.Ura | BYTE
STRHladStrojKompresorOljeAlarmB | INT | IOD_STR | STR:.HladStroj.KompresorOljeAlarmB | BYTE
STRHladStrojNizekPritiskAlarmB | INT | IOD_STR | STR:.HladStroj.NizekPritiskAlarmB | BYTE
STRHladStrojObratovalneUreOpozoriloB | INT | IOD_STR | STR:.HladStroj.ObratovalneUreOpozoriloB | BYTE
STRHladStrojTemperaturaAlarmB | INT | IOD_STR | STR:.HladStroj.TemperaturaAlarmB | BYTE
STRHladStrojUnitStatus | INT | IOD_STR | STR:.HladStroj.UnitStatus
STRHladStrojVisokPritiskAlarmB | INT | IOD_STR | STR:.HladStroj.VisokPritiskAlarmB | BYTE
STRHladStrojVisokPritiskOpozoriloB | INT | IOD_STR | STR:.HladStroj.VisokPritiskOpozoriloB | BYTE
STRHladStrojZmrzalniAlarmB | INT | IOD_STR | STR:.HladStroj.ZmrzalniAlarmB | BYTE
STRKlima1CrpalkaStatus | INT | IOD_STR | STR:.Klima[1].CrpalkaStatus | BYTE
STRKlima1HitrostVentStatus | INT | IOD_STR | STR:.Klima[1].HitrostVentStatus | BYTE
STRKlima1IzhodniVentStatus | INT | IOD_STR | STR:.Klima[1].IzhodniVentStatus | BYTE
STRKlima2CrpalkaStatus | INT | IOD_STR | STR:.Klima[2].CrpalkaStatus | BYTE
STRKlima2HitrostVentStatus | INT | IOD_STR | STR:.Klima[2].HitrostVentStatus | BYTE
STRKlima2IzhodniVentStatus | INT | IOD_STR | STR:.Klima[2].IzhodniVentStatus | BYTE
STRPozarnaLoputaStatus1 | INT | IOD_STR | STR:.PozarnaLoputaStatus[1] | BYTE
STRPozarnaLoputaStatus2 | INT | IOD_STR | STR:.PozarnaLoputaStatus[2] | BYTE
STRPozarnaLoputaStatus3 | INT | IOD_STR | STR:.PozarnaLoputaStatus[3] | BYTE
STRPozarnaLoputaStatus4 | INT | IOD_STR | STR:.PozarnaLoputaStatus[4] | BYTE
STRPozarnaLoputaStatus5 | INT | IOD_STR | STR:.PozarnaLoputaStatus[5] | BYTE
STRStatusKondenzEnota0 | INT | IOD_STR | STR:.StatusKondenzEnota[0] | BYTE
STRStatusKondenzEnota1 | INT | IOD_STR | STR:.StatusKondenzEnota[1] | BYTE
STRStatusKondenzEnota2 | INT | IOD_STR | STR:.StatusKondenzEnota[2] | BYTE
STRStatusKondenzEnota3 | INT | IOD_STR | STR:.StatusKondenzEnota[3] | BYTE
STRStatusKontaktor10 | INT | IOD_STR | STR:.StatusKontaktor[10] | BYTE
STRStatusKontaktor11 | INT | IOD_STR | STR:.StatusKontaktor[11] | BYTE
STRStatusKontaktor12 | INT | IOD_STR | STR:.StatusKontaktor[12] | BYTE
STRStatusKontaktor13 | INT | IOD_STR | STR:.StatusKontaktor[13] | BYTE
STRStatusKontaktor14 | INT | IOD_STR | STR:.StatusKontaktor[14] | BYTE
STRStatusKontaktor15 | INT | IOD_STR | STR:.StatusKontaktor[15] | BYTE
STRStatusKontaktor16 | INT | IOD_STR | STR:.StatusKontaktor[16] | BYTE
STRStatusKontaktor17 | INT | IOD_STR | STR:.StatusKontaktor[17] | BYTE
STRStatusKontaktor18 | INT | IOD_STR | STR:.StatusKontaktor[18] | BYTE
STRStatusKontaktor19 | INT | IOD_STR | STR:.StatusKontaktor[19] | BYTE
STRStatusKontaktor1 | INT | IOD_STR | STR:.StatusKontaktor[1] | BYTE
STRStatusKontaktor20 | INT | IOD_STR | STR:.StatusKontaktor[20] | BYTE
STRStatusKontaktor21 | INT | IOD_STR | STR:.StatusKontaktor[21] | BYTE
STRStatusKontaktor22 | INT | IOD_STR | STR:.StatusKontaktor[22] | BYTE
STRStatusKontaktor23 | INT | IOD_STR | STR:.StatusKontaktor[23] | BYTE
STRStatusKontaktor24 | INT | IOD_STR | STR:.StatusKontaktor[24] | BYTE
STRStatusKontaktor25 | INT | IOD_STR | STR:.StatusKontaktor[25] | BYTE
STRStatusKontaktor2 | INT | IOD_STR | STR:.StatusKontaktor[2] | BYTE
STRStatusKontaktor3 | INT | IOD_STR | STR:.StatusKontaktor[3] | BYTE
STRStatusKontaktor4 | INT | IOD_STR | STR:.StatusKontaktor[4] | BYTE
STRStatusKontaktor5 | INT | IOD_STR | STR:.StatusKontaktor[5] | BYTE
STRStatusKontaktor6 | INT | IOD_STR | STR:.StatusKontaktor[6] | BYTE
STRStatusKontaktor7 | INT | IOD_STR | STR:.StatusKontaktor[7] | BYTE
STRStatusKontaktor8 | INT | IOD_STR | STR:.StatusKontaktor[8] | BYTE
STRStatusKontaktor9 | INT | IOD_STR | STR:.StatusKontaktor[9] | BYTE
STRStatusPreklopke10 | INT | IOD_STR | STR:.StatusPreklopke[10] | BYTE
STRStatusPreklopke11 | INT | IOD_STR | STR:.StatusPreklopke[11] | BYTE
STRStatusPreklopke12 | INT | IOD_STR | STR:.StatusPreklopke[12] | BYTE
STRStatusPreklopke13 | INT | IOD_STR | STR:.StatusPreklopke[13] | BYTE
STRStatusPreklopke14 | INT | IOD_STR | STR:.StatusPreklopke[14] | BYTE
STRStatusPreklopke15 | INT | IOD_STR | STR:.StatusPreklopke[15] | BYTE
STRStatusPreklopke16 | INT | IOD_STR | STR:.StatusPreklopke[16] | BYTE
STRStatusPreklopke17 | INT | IOD_STR | STR:.StatusPreklopke[17] | BYTE
STRStatusPreklopke18 | INT | IOD_STR | STR:.StatusPreklopke[18] | BYTE
STRStatusPreklopke19 | INT | IOD_STR | STR:.StatusPreklopke[19] | BYTE
STRStatusPreklopke1 | INT | IOD_STR | STR:.StatusPreklopke[1] | BYTE
STRStatusPreklopke20 | INT | IOD_STR | STR:.StatusPreklopke[20] | BYTE
STRStatusPreklopke21 | INT | IOD_STR | STR:.StatusPreklopke[21] | BYTE
STRStatusPreklopke22 | INT | IOD_STR | STR:.StatusPreklopke[22] | BYTE
STRStatusPreklopke23 | INT | IOD_STR | STR:.StatusPreklopke[23] | BYTE
STRStatusPreklopke24 | INT | IOD_STR | STR:.StatusPreklopke[24] | BYTE
STRStatusPreklopke25 | INT | IOD_STR | STR:.StatusPreklopke[25] | BYTE
STRStatusPreklopke2 | INT | IOD_STR | STR:.StatusPreklopke[2] | BYTE
STRStatusPreklopke3 | INT | IOD_STR | STR:.StatusPreklopke[3] | BYTE
STRStatusPreklopke4 | INT | IOD_STR | STR:.StatusPreklopke[4] | BYTE
STRStatusPreklopke5 | INT | IOD_STR | STR:.StatusPreklopke[5] | BYTE
STRStatusPreklopke6 | INT | IOD_STR | STR:.StatusPreklopke[6] | BYTE
STRStatusPreklopke7 | INT | IOD_STR | STR:.StatusPreklopke[7] | BYTE
STRStatusPreklopke8 | INT | IOD_STR | STR:.StatusPreklopke[8] | BYTE
STRStatusPreklopke9 | INT | IOD_STR | STR:.StatusPreklopke[9] | BYTE
STRToplPostNapakaRegister | INT | IOD_STR | STR:.ToplPost.NapakaRegister
STRUrnik_SCtoXCpot | INT | IOD_STR | STR:.Urnik_SCtoXCpot
STRUrnik_SCtoXCzah | INT | IOD_STR | STR:.Urnik_SCtoXCzah
STRUrnik_XCtoSCpot | INT | IOD_STR | STR:.Urnik_XCtoSCpot
STRUrnik_XCtoSCzah | INT | IOD_STR | STR:.Urnik_XCtoSCzah
STRUrnikSCtoXCDan1Off1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[1].Mna | BYTE
STRUrnikSCtoXCDan1Off1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[1].Ura | BYTE
STRUrnikSCtoXCDan1Off2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[2].Mna | BYTE
STRUrnikSCtoXCDan1Off2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[2].Ura | BYTE
STRUrnikSCtoXCDan1Off3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[3].Mna | BYTE
STRUrnikSCtoXCDan1Off3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].Off[3].Ura | BYTE
STRUrnikSCtoXCDan1On1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[1].Mna | BYTE
STRUrnikSCtoXCDan1On1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[1].Ura | BYTE
STRUrnikSCtoXCDan1On2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[2].Mna | BYTE
STRUrnikSCtoXCDan1On2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[2].Ura | BYTE
STRUrnikSCtoXCDan1On3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[3].Mna | BYTE
STRUrnikSCtoXCDan1On3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[1].On[3].Ura | BYTE
STRUrnikSCtoXCDan2Off1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[1].Mna | BYTE
STRUrnikSCtoXCDan2Off1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[1].Ura | BYTE
STRUrnikSCtoXCDan2Off2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[2].Mna | BYTE
STRUrnikSCtoXCDan2Off2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[2].Ura | BYTE
STRUrnikSCtoXCDan2Off3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[3].Mna | BYTE
STRUrnikSCtoXCDan2Off3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].Off[3].Ura | BYTE
STRUrnikSCtoXCDan2On1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[1].Mna | BYTE
STRUrnikSCtoXCDan2On1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[1].Ura | BYTE
STRUrnikSCtoXCDan2On2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[2].Mna | BYTE
STRUrnikSCtoXCDan2On2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[2].Ura | BYTE
STRUrnikSCtoXCDan2On3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[3].Mna | BYTE
STRUrnikSCtoXCDan2On3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[2].On[3].Ura | BYTE
STRUrnikSCtoXCDan3Off1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[1].Mna | BYTE
STRUrnikSCtoXCDan3Off1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[1].Ura | BYTE
STRUrnikSCtoXCDan3Off2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[2].Mna | BYTE
STRUrnikSCtoXCDan3Off2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[2].Ura | BYTE
STRUrnikSCtoXCDan3Off3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[3].Mna | BYTE
STRUrnikSCtoXCDan3Off3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].Off[3].Ura | BYTE
STRUrnikSCtoXCDan3On1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[1].Mna | BYTE
STRUrnikSCtoXCDan3On1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[1].Ura | BYTE
STRUrnikSCtoXCDan3On2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[2].Mna | BYTE
STRUrnikSCtoXCDan3On2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[2].Ura | BYTE
STRUrnikSCtoXCDan3On3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[3].Mna | BYTE
STRUrnikSCtoXCDan3On3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[3].On[3].Ura | BYTE
STRUrnikSCtoXCDan4Off1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[1].Mna | BYTE
STRUrnikSCtoXCDan4Off1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[1].Ura | BYTE
STRUrnikSCtoXCDan4Off2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[2].Mna | BYTE
STRUrnikSCtoXCDan4Off2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[2].Ura | BYTE
STRUrnikSCtoXCDan4Off3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[3].Mna | BYTE
STRUrnikSCtoXCDan4Off3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].Off[3].Ura | BYTE
STRUrnikSCtoXCDan4On1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[1].Mna | BYTE
STRUrnikSCtoXCDan4On1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[1].Ura | BYTE
STRUrnikSCtoXCDan4On2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[2].Mna | BYTE
STRUrnikSCtoXCDan4On2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[2].Ura | BYTE
STRUrnikSCtoXCDan4On3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[3].Mna | BYTE
STRUrnikSCtoXCDan4On3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[4].On[3].Ura | BYTE
STRUrnikSCtoXCDan5Off1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[1].Mna | BYTE
STRUrnikSCtoXCDan5Off1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[1].Ura | BYTE
STRUrnikSCtoXCDan5Off2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[2].Mna | BYTE
STRUrnikSCtoXCDan5Off2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[2].Ura | BYTE
STRUrnikSCtoXCDan5Off3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[3].Mna | BYTE
STRUrnikSCtoXCDan5Off3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].Off[3].Ura | BYTE
STRUrnikSCtoXCDan5On1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[1].Mna | BYTE
STRUrnikSCtoXCDan5On1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[1].Ura | BYTE
STRUrnikSCtoXCDan5On2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[2].Mna | BYTE
STRUrnikSCtoXCDan5On2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[2].Ura | BYTE
STRUrnikSCtoXCDan5On3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[3].Mna | BYTE
STRUrnikSCtoXCDan5On3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[5].On[3].Ura | BYTE
STRUrnikSCtoXCDan6Off1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[1].Mna | BYTE
STRUrnikSCtoXCDan6Off1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[1].Ura | BYTE
STRUrnikSCtoXCDan6Off2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[2].Mna | BYTE
STRUrnikSCtoXCDan6Off2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[2].Ura | BYTE
STRUrnikSCtoXCDan6Off3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[3].Mna | BYTE
STRUrnikSCtoXCDan6Off3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].Off[3].Ura | BYTE
STRUrnikSCtoXCDan6On1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[1].Mna | BYTE
STRUrnikSCtoXCDan6On1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[1].Ura | BYTE
STRUrnikSCtoXCDan6On2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[2].Mna | BYTE
STRUrnikSCtoXCDan6On2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[2].Ura | BYTE
STRUrnikSCtoXCDan6On3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[3].Mna | BYTE
STRUrnikSCtoXCDan6On3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[6].On[3].Ura | BYTE
STRUrnikSCtoXCDan7Off1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[1].Mna | BYTE
STRUrnikSCtoXCDan7Off1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[1].Ura | BYTE
STRUrnikSCtoXCDan7Off2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[2].Mna | BYTE
STRUrnikSCtoXCDan7Off2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[2].Ura | BYTE
STRUrnikSCtoXCDan7Off3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[3].Mna | BYTE
STRUrnikSCtoXCDan7Off3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].Off[3].Ura | BYTE
STRUrnikSCtoXCDan7On1Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[1].Mna | BYTE
STRUrnikSCtoXCDan7On1Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[1].Ura | BYTE
STRUrnikSCtoXCDan7On2Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[2].Mna | BYTE
STRUrnikSCtoXCDan7On2Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[2].Ura | BYTE
STRUrnikSCtoXCDan7On3Mna | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[3].Mna | BYTE
STRUrnikSCtoXCDan7On3Ura | INT | IOD_STR | STR:.UrnikSCtoXC.Dan[7].On[3].Ura | BYTE
STRUrnikXCtoSCDan1Off1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[1].Mna | BYTE
STRUrnikXCtoSCDan1Off1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[1].Ura | BYTE
STRUrnikXCtoSCDan1Off2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[2].Mna | BYTE
STRUrnikXCtoSCDan1Off2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[2].Ura | BYTE
STRUrnikXCtoSCDan1Off3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[3].Mna | BYTE
STRUrnikXCtoSCDan1Off3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].Off[3].Ura | BYTE
STRUrnikXCtoSCDan1On1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[1].Mna | BYTE
STRUrnikXCtoSCDan1On1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[1].Ura | BYTE
STRUrnikXCtoSCDan1On2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[2].Mna | BYTE
STRUrnikXCtoSCDan1On2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[2].Ura | BYTE
STRUrnikXCtoSCDan1On3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[3].Mna | BYTE
STRUrnikXCtoSCDan1On3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[1].On[3].Ura | BYTE
STRUrnikXCtoSCDan2Off1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[1].Mna | BYTE
STRUrnikXCtoSCDan2Off1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[1].Ura | BYTE
STRUrnikXCtoSCDan2Off2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[2].Mna | BYTE
STRUrnikXCtoSCDan2Off2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[2].Ura | BYTE
STRUrnikXCtoSCDan2Off3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[3].Mna | BYTE
STRUrnikXCtoSCDan2Off3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].Off[3].Ura | BYTE
STRUrnikXCtoSCDan2On1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[1].Mna | BYTE
STRUrnikXCtoSCDan2On1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[1].Ura | BYTE
STRUrnikXCtoSCDan2On2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[2].Mna | BYTE
STRUrnikXCtoSCDan2On2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[2].Ura | BYTE
STRUrnikXCtoSCDan2On3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[3].Mna | BYTE
STRUrnikXCtoSCDan2On3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[2].On[3].Ura | BYTE
STRUrnikXCtoSCDan3Off1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[1].Mna | BYTE
STRUrnikXCtoSCDan3Off1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[1].Ura | BYTE
STRUrnikXCtoSCDan3Off2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[2].Mna | BYTE
STRUrnikXCtoSCDan3Off2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[2].Ura | BYTE
STRUrnikXCtoSCDan3Off3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[3].Mna | BYTE
STRUrnikXCtoSCDan3Off3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].Off[3].Ura | BYTE
STRUrnikXCtoSCDan3On1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[1].Mna | BYTE
STRUrnikXCtoSCDan3On1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[1].Ura | BYTE
STRUrnikXCtoSCDan3On2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[2].Mna | BYTE
STRUrnikXCtoSCDan3On2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[2].Ura | BYTE
STRUrnikXCtoSCDan3On3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[3].Mna | BYTE
STRUrnikXCtoSCDan3On3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[3].On[3].Ura | BYTE
STRUrnikXCtoSCDan4Off1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[1].Mna | BYTE
STRUrnikXCtoSCDan4Off1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[1].Ura | BYTE
STRUrnikXCtoSCDan4Off2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[2].Mna | BYTE
STRUrnikXCtoSCDan4Off2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[2].Ura | BYTE
STRUrnikXCtoSCDan4Off3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[3].Mna | BYTE
STRUrnikXCtoSCDan4Off3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].Off[3].Ura | BYTE
STRUrnikXCtoSCDan4On1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[1].Mna | BYTE
STRUrnikXCtoSCDan4On1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[1].Ura | BYTE
STRUrnikXCtoSCDan4On2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[2].Mna | BYTE
STRUrnikXCtoSCDan4On2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[2].Ura | BYTE
STRUrnikXCtoSCDan4On3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[3].Mna | BYTE
STRUrnikXCtoSCDan4On3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[4].On[3].Ura | BYTE
STRUrnikXCtoSCDan5Off1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[1].Mna | BYTE
STRUrnikXCtoSCDan5Off1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[1].Ura | BYTE
STRUrnikXCtoSCDan5Off2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[2].Mna | BYTE
STRUrnikXCtoSCDan5Off2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[2].Ura | BYTE
STRUrnikXCtoSCDan5Off3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[3].Mna | BYTE
STRUrnikXCtoSCDan5Off3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].Off[3].Ura | BYTE
STRUrnikXCtoSCDan5On1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[1].Mna | BYTE
STRUrnikXCtoSCDan5On1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[1].Ura | BYTE
STRUrnikXCtoSCDan5On2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[2].Mna | BYTE
STRUrnikXCtoSCDan5On2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[2].Ura | BYTE
STRUrnikXCtoSCDan5On3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[3].Mna | BYTE
STRUrnikXCtoSCDan5On3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[5].On[3].Ura | BYTE
STRUrnikXCtoSCDan6Off1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[1].Mna | BYTE
STRUrnikXCtoSCDan6Off1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[1].Ura | BYTE
STRUrnikXCtoSCDan6Off2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[2].Mna | BYTE
STRUrnikXCtoSCDan6Off2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[2].Ura | BYTE
STRUrnikXCtoSCDan6Off3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[3].Mna | BYTE
STRUrnikXCtoSCDan6Off3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].Off[3].Ura | BYTE
STRUrnikXCtoSCDan6On1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[1].Mna | BYTE
STRUrnikXCtoSCDan6On1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[1].Ura | BYTE
STRUrnikXCtoSCDan6On2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[2].Mna | BYTE
STRUrnikXCtoSCDan6On2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[2].Ura | BYTE
STRUrnikXCtoSCDan6On3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[3].Mna | BYTE
STRUrnikXCtoSCDan6On3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[6].On[3].Ura | BYTE
STRUrnikXCtoSCDan7Off1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[1].Mna | BYTE
STRUrnikXCtoSCDan7Off1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[1].Ura | BYTE
STRUrnikXCtoSCDan7Off2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[2].Mna | BYTE
STRUrnikXCtoSCDan7Off2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[2].Ura | BYTE
STRUrnikXCtoSCDan7Off3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[3].Mna | BYTE
STRUrnikXCtoSCDan7Off3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].Off[3].Ura | BYTE
STRUrnikXCtoSCDan7On1Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[1].Mna | BYTE
STRUrnikXCtoSCDan7On1Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[1].Ura | BYTE
STRUrnikXCtoSCDan7On2Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[2].Mna | BYTE
STRUrnikXCtoSCDan7On2Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[2].Ura | BYTE
STRUrnikXCtoSCDan7On3Mna | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[3].Mna | BYTE
STRUrnikXCtoSCDan7On3Ura | INT | IOD_STR | STR:.UrnikXCtoSC.Dan[7].On[3].Ura | BYTE
STRUserCurrentLevel | INT | IOD_STR | STR:.UserCurrentLevel | BYTE
STRCrpalkeGrfsGalAlarmActiveCode | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmActiveCode
STRCrpalkeGrfsGalAlarmCodeLog1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmCodeLog1
STRCrpalkeGrfsGalAlarmCodeLog2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmCodeLog2
STRCrpalkeGrfsGalAlarmCodeLog3 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmCodeLog3
STRCrpalkeGrfsGalAlarmCodeLog4 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmCodeLog4
STRCrpalkeGrfsGalAlarmCodeLog5 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmCodeLog5
STRCrpalkeGrfsGalAlarmGroupXVH0 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[0]
STRCrpalkeGrfsGalAlarmGroupXVH10 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[10]
STRCrpalkeGrfsGalAlarmGroupXVH11 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[11]
STRCrpalkeGrfsGalAlarmGroupXVH12 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[12]
STRCrpalkeGrfsGalAlarmGroupXVH13 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[13]
STRCrpalkeGrfsGalAlarmGroupXVH14 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[14]
STRCrpalkeGrfsGalAlarmGroupXVH15 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[15]
STRCrpalkeGrfsGalAlarmGroupXVH16 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[16]
STRCrpalkeGrfsGalAlarmGroupXVH1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[1]
STRCrpalkeGrfsGalAlarmGroupXVH2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[2]
STRCrpalkeGrfsGalAlarmGroupXVH3 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[3]
STRCrpalkeGrfsGalAlarmGroupXVH4 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[4]
STRCrpalkeGrfsGalAlarmGroupXVH5 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[5]
STRCrpalkeGrfsGalAlarmGroupXVH6 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[6]
STRCrpalkeGrfsGalAlarmGroupXVH7 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[7]
STRCrpalkeGrfsGalAlarmGroupXVH8 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[8]
STRCrpalkeGrfsGalAlarmGroupXVH9 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmGroupXVH[9]
STRCrpalkeGrfsGalAlarmQSD1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmQSD1
STRCrpalkeGrfsGalAlarmQSD2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmQSD2
STRCrpalkeGrfsGalAlarmStart1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmStart1
STRCrpalkeGrfsGalAlarmStart2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmStart2
STRCrpalkeGrfsGalAlarmStop1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmStop1
STRCrpalkeGrfsGalAlarmStop2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmStop2
STRCrpalkeGrfsGalAlarmStop3 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmStop3
STRCrpalkeGrfsGalAlarmSurv1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmSurv1
STRCrpalkeGrfsGalAlarmSurv2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.AlarmSurv2
STRCrpalkeGrfsGalControlSource | INT | IOD_STR | STR:.CrpalkeGrfsGal.ControlSource
STRCrpalkeGrfsGalExternInputSetup | INT | IOD_STR | STR:.CrpalkeGrfsGal.ExternInputSetup
STRCrpalkeGrfsGalExternInputsStatus | INT | IOD_STR | STR:.CrpalkeGrfsGal.ExternInputsStatus
STRCrpalkeGrfsGalLocalSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.LocalSetupMode1
STRCrpalkeGrfsGalPreklopkaMode | INT | IOD_STR | STR:.CrpalkeGrfsGal.PreklopkaMode
STRCrpalkeGrfsGalRelay1setup | INT | IOD_STR | STR:.CrpalkeGrfsGal.Relay1setup
STRCrpalkeGrfsGalRemoteSetupMode1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.RemoteSetupMode1
STRCrpalkeGrfsGalStatusCrpalke | INT | IOD_STR | STR:.CrpalkeGrfsGal.StatusCrpalke | BYTE
STRCrpalkeGrfsGalStatusMode1 | INT | IOD_STR | STR:.CrpalkeGrfsGal.StatusMode1
STRCrpalkeGrfsGalStatusMode1co | INT | IOD_STR | STR:.CrpalkeGrfsGal.StatusMode1co | BYTE
STRCrpalkeGrfsGalStatusMode1op | INT | IOD_STR | STR:.CrpalkeGrfsGal.StatusMode1op | BYTE
STRCrpalkeGrfsGalStatusMode2 | INT | IOD_STR | STR:.CrpalkeGrfsGal.StatusMode2
STRCrpalkeGrfsGalStatusMode3 | INT | IOD_STR | STR:.CrpalkeGrfsGal.StatusMode3
STRCrpGrfsPIDregTN | INT | IOD_STR | STR:.CrpGrfsPIDregTN
STRDateTimeDanVtednu | INT | IOD_STR | STR:.DateTime.DanVtednu | BYTE
STRLetniCasDatumi111 | INT | IOD_STR | STR:.LetniCasDatumi[1,1,1]
STRLetniCasDatumi112 | INT | IOD_STR | STR:.LetniCasDatumi[1,1,2]
STRLetniCasDatumi121 | INT | IOD_STR | STR:.LetniCasDatumi[1,2,1]
STRLetniCasDatumi122 | INT | IOD_STR | STR:.LetniCasDatumi[1,2,2]
STRLetniCasDatumi131 | INT | IOD_STR | STR:.LetniCasDatumi[1,3,1]
STRLetniCasDatumi132 | INT | IOD_STR | STR:.LetniCasDatumi[1,3,2]
STRLetniCasDatumi141 | INT | IOD_STR | STR:.LetniCasDatumi[1,4,1]
STRLetniCasDatumi142 | INT | IOD_STR | STR:.LetniCasDatumi[1,4,2]
STRLetniCasDatumi211 | INT | IOD_STR | STR:.LetniCasDatumi[2,1,1]
STRLetniCasDatumi212 | INT | IOD_STR | STR:.LetniCasDatumi[2,1,2]
STRLetniCasDatumi221 | INT | IOD_STR | STR:.LetniCasDatumi[2,2,1]
STRLetniCasDatumi222 | INT | IOD_STR | STR:.LetniCasDatumi[2,2,2]
STRLetniCasDatumi231 | INT | IOD_STR | STR:.LetniCasDatumi[2,3,1]
STRLetniCasDatumi232 | INT | IOD_STR | STR:.LetniCasDatumi[2,3,2]
STRLetniCasDatumi241 | INT | IOD_STR | STR:.LetniCasDatumi[2,4,1]
STRLetniCasDatumi242 | INT | IOD_STR | STR:.LetniCasDatumi[2,4,2]
STRUrnikSaveDan1Off1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[1].Off[1].Mna | BYTE
STRUrnikSaveDan1Off1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[1].Off[1].Ura | BYTE
STRUrnikSaveDan1Off2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[1].Off[2].Mna | BYTE
STRUrnikSaveDan1Off2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[1].Off[2].Ura | BYTE
STRUrnikSaveDan1Off3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[1].Off[3].Mna | BYTE
STRUrnikSaveDan1Off3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[1].Off[3].Ura | BYTE
STRUrnikSaveDan1On1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[1].On[1].Mna | BYTE
STRUrnikSaveDan1On1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[1].On[1].Ura | BYTE
STRUrnikSaveDan1On2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[1].On[2].Mna | BYTE
STRUrnikSaveDan1On2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[1].On[2].Ura | BYTE
STRUrnikSaveDan1On3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[1].On[3].Mna | BYTE
STRUrnikSaveDan1On3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[1].On[3].Ura | BYTE
STRUrnikSaveDan2Off1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[2].Off[1].Mna | BYTE
STRUrnikSaveDan2Off1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[2].Off[1].Ura | BYTE
STRUrnikSaveDan2Off2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[2].Off[2].Mna | BYTE
STRUrnikSaveDan2Off2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[2].Off[2].Ura | BYTE
STRUrnikSaveDan2Off3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[2].Off[3].Mna | BYTE
STRUrnikSaveDan2Off3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[2].Off[3].Ura | BYTE
STRUrnikSaveDan2On1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[2].On[1].Mna | BYTE
STRUrnikSaveDan2On1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[2].On[1].Ura | BYTE
STRUrnikSaveDan2On2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[2].On[2].Mna | BYTE
STRUrnikSaveDan2On2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[2].On[2].Ura | BYTE
STRUrnikSaveDan2On3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[2].On[3].Mna | BYTE
STRUrnikSaveDan2On3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[2].On[3].Ura | BYTE
STRUrnikSaveDan3Off1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[3].Off[1].Mna | BYTE
STRUrnikSaveDan3Off1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[3].Off[1].Ura | BYTE
STRUrnikSaveDan3Off2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[3].Off[2].Mna | BYTE
STRUrnikSaveDan3Off2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[3].Off[2].Ura | BYTE
STRUrnikSaveDan3Off3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[3].Off[3].Mna | BYTE
STRUrnikSaveDan3Off3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[3].Off[3].Ura | BYTE
STRUrnikSaveDan3On1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[3].On[1].Mna | BYTE
STRUrnikSaveDan3On1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[3].On[1].Ura | BYTE
STRUrnikSaveDan3On2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[3].On[2].Mna | BYTE
STRUrnikSaveDan3On2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[3].On[2].Ura | BYTE
STRUrnikSaveDan3On3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[3].On[3].Mna | BYTE
STRUrnikSaveDan3On3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[3].On[3].Ura | BYTE
STRUrnikSaveDan4Off1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[4].Off[1].Mna | BYTE
STRUrnikSaveDan4Off1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[4].Off[1].Ura | BYTE
STRUrnikSaveDan4Off2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[4].Off[2].Mna | BYTE
STRUrnikSaveDan4Off2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[4].Off[2].Ura | BYTE
STRUrnikSaveDan4Off3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[4].Off[3].Mna | BYTE
STRUrnikSaveDan4Off3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[4].Off[3].Ura | BYTE
STRUrnikSaveDan4On1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[4].On[1].Mna | BYTE
STRUrnikSaveDan4On1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[4].On[1].Ura | BYTE
STRUrnikSaveDan4On2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[4].On[2].Mna | BYTE
STRUrnikSaveDan4On2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[4].On[2].Ura | BYTE
STRUrnikSaveDan4On3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[4].On[3].Mna | BYTE
STRUrnikSaveDan4On3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[4].On[3].Ura | BYTE
STRUrnikSaveDan5Off1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[5].Off[1].Mna | BYTE
STRUrnikSaveDan5Off1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[5].Off[1].Ura | BYTE
STRUrnikSaveDan5Off2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[5].Off[2].Mna | BYTE
STRUrnikSaveDan5Off2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[5].Off[2].Ura | BYTE
STRUrnikSaveDan5Off3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[5].Off[3].Mna | BYTE
STRUrnikSaveDan5Off3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[5].Off[3].Ura | BYTE
STRUrnikSaveDan5On1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[5].On[1].Mna | BYTE
STRUrnikSaveDan5On1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[5].On[1].Ura | BYTE
STRUrnikSaveDan5On2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[5].On[2].Mna | BYTE
STRUrnikSaveDan5On2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[5].On[2].Ura | BYTE
STRUrnikSaveDan5On3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[5].On[3].Mna | BYTE
STRUrnikSaveDan5On3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[5].On[3].Ura | BYTE
STRUrnikSaveDan6Off1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[6].Off[1].Mna | BYTE
STRUrnikSaveDan6Off1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[6].Off[1].Ura | BYTE
STRUrnikSaveDan6Off2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[6].Off[2].Mna | BYTE
STRUrnikSaveDan6Off2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[6].Off[2].Ura | BYTE
STRUrnikSaveDan6Off3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[6].Off[3].Mna | BYTE
STRUrnikSaveDan6Off3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[6].Off[3].Ura | BYTE
STRUrnikSaveDan6On1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[6].On[1].Mna | BYTE
STRUrnikSaveDan6On1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[6].On[1].Ura | BYTE
STRUrnikSaveDan6On2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[6].On[2].Mna | BYTE
STRUrnikSaveDan6On2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[6].On[2].Ura | BYTE
STRUrnikSaveDan6On3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[6].On[3].Mna | BYTE
STRUrnikSaveDan6On3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[6].On[3].Ura | BYTE
STRUrnikSaveDan7Off1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[7].Off[1].Mna | BYTE
STRUrnikSaveDan7Off1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[7].Off[1].Ura | BYTE
STRUrnikSaveDan7Off2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[7].Off[2].Mna | BYTE
STRUrnikSaveDan7Off2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[7].Off[2].Ura | BYTE
STRUrnikSaveDan7Off3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[7].Off[3].Mna | BYTE
STRUrnikSaveDan7Off3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[7].Off[3].Ura | BYTE
STRUrnikSaveDan7On1Mna | INT | IOD_STR | STR:.UrnikSave.Dan[7].On[1].Mna | BYTE
STRUrnikSaveDan7On1Ura | INT | IOD_STR | STR:.UrnikSave.Dan[7].On[1].Ura | BYTE
STRUrnikSaveDan7On2Mna | INT | IOD_STR | STR:.UrnikSave.Dan[7].On[2].Mna | BYTE
STRUrnikSaveDan7On2Ura | INT | IOD_STR | STR:.UrnikSave.Dan[7].On[2].Ura | BYTE
STRUrnikSaveDan7On3Mna | INT | IOD_STR | STR:.UrnikSave.Dan[7].On[3].Mna | BYTE
STRUrnikSaveDan7On3Ura | INT | IOD_STR | STR:.UrnikSave.Dan[7].On[3].Ura | BYTE
STRXVH_CircNumber | INT | IOD_STR | STR:.XVH_CircNumber | BYTE
STRXVH_KompStatus1 | INT | IOD_STR | STR:.XVH_KompStatus[1] | BYTE
STRXVH_KompStatus2 | INT | IOD_STR | STR:.XVH_KompStatus[2] | BYTE
STRXVH_ReferencaUpper | INT | IOD_STR | STR:.XVH_ReferencaUpper
STRXVH_UPSstatus | INT | IOD_STR | STR:.XVH_UPSstatus | BYTE
STRXVH_UrnikDan1Off1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[1].Mna | BYTE
STRXVH_UrnikDan1Off1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[1].Ura | BYTE
STRXVH_UrnikDan1Off2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[2].Mna | BYTE
STRXVH_UrnikDan1Off2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[2].Ura | BYTE
STRXVH_UrnikDan1Off3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[3].Mna | BYTE
STRXVH_UrnikDan1Off3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].Off[3].Ura | BYTE
STRXVH_UrnikDan1On1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].On[1].Mna | BYTE
STRXVH_UrnikDan1On1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].On[1].Ura | BYTE
STRXVH_UrnikDan1On2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].On[2].Mna | BYTE
STRXVH_UrnikDan1On2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].On[2].Ura | BYTE
STRXVH_UrnikDan1On3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].On[3].Mna | BYTE
STRXVH_UrnikDan1On3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[1].On[3].Ura | BYTE
STRXVH_UrnikDan2Off1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[1].Mna | BYTE
STRXVH_UrnikDan2Off1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[1].Ura | BYTE
STRXVH_UrnikDan2Off2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[2].Mna | BYTE
STRXVH_UrnikDan2Off2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[2].Ura | BYTE
STRXVH_UrnikDan2Off3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[3].Mna | BYTE
STRXVH_UrnikDan2Off3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].Off[3].Ura | BYTE
STRXVH_UrnikDan2On1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].On[1].Mna | BYTE
STRXVH_UrnikDan2On1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].On[1].Ura | BYTE
STRXVH_UrnikDan2On2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].On[2].Mna | BYTE
STRXVH_UrnikDan2On2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].On[2].Ura | BYTE
STRXVH_UrnikDan2On3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].On[3].Mna | BYTE
STRXVH_UrnikDan2On3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[2].On[3].Ura | BYTE
STRXVH_UrnikDan3Off1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[1].Mna | BYTE
STRXVH_UrnikDan3Off1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[1].Ura | BYTE
STRXVH_UrnikDan3Off2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[2].Mna | BYTE
STRXVH_UrnikDan3Off2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[2].Ura | BYTE
STRXVH_UrnikDan3Off3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[3].Mna | BYTE
STRXVH_UrnikDan3Off3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].Off[3].Ura | BYTE
STRXVH_UrnikDan3On1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].On[1].Mna | BYTE
STRXVH_UrnikDan3On1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].On[1].Ura | BYTE
STRXVH_UrnikDan3On2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].On[2].Mna | BYTE
STRXVH_UrnikDan3On2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].On[2].Ura | BYTE
STRXVH_UrnikDan3On3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].On[3].Mna | BYTE
STRXVH_UrnikDan3On3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[3].On[3].Ura | BYTE
STRXVH_UrnikDan4Off1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[1].Mna | BYTE
STRXVH_UrnikDan4Off1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[1].Ura | BYTE
STRXVH_UrnikDan4Off2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[2].Mna | BYTE
STRXVH_UrnikDan4Off2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[2].Ura | BYTE
STRXVH_UrnikDan4Off3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[3].Mna | BYTE
STRXVH_UrnikDan4Off3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].Off[3].Ura | BYTE
STRXVH_UrnikDan4On1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].On[1].Mna | BYTE
STRXVH_UrnikDan4On1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].On[1].Ura | BYTE
STRXVH_UrnikDan4On2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].On[2].Mna | BYTE
STRXVH_UrnikDan4On2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].On[2].Ura | BYTE
STRXVH_UrnikDan4On3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].On[3].Mna | BYTE
STRXVH_UrnikDan4On3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[4].On[3].Ura | BYTE
STRXVH_UrnikDan5Off1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[1].Mna | BYTE
STRXVH_UrnikDan5Off1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[1].Ura | BYTE
STRXVH_UrnikDan5Off2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[2].Mna | BYTE
STRXVH_UrnikDan5Off2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[2].Ura | BYTE
STRXVH_UrnikDan5Off3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[3].Mna | BYTE
STRXVH_UrnikDan5Off3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].Off[3].Ura | BYTE
STRXVH_UrnikDan5On1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].On[1].Mna | BYTE
STRXVH_UrnikDan5On1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].On[1].Ura | BYTE
STRXVH_UrnikDan5On2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].On[2].Mna | BYTE
STRXVH_UrnikDan5On2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].On[2].Ura | BYTE
STRXVH_UrnikDan5On3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].On[3].Mna | BYTE
STRXVH_UrnikDan5On3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[5].On[3].Ura | BYTE
STRXVH_UrnikDan6Off1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[1].Mna | BYTE
STRXVH_UrnikDan6Off1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[1].Ura | BYTE
STRXVH_UrnikDan6Off2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[2].Mna | BYTE
STRXVH_UrnikDan6Off2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[2].Ura | BYTE
STRXVH_UrnikDan6Off3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[3].Mna | BYTE
STRXVH_UrnikDan6Off3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].Off[3].Ura | BYTE
STRXVH_UrnikDan6On1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].On[1].Mna | BYTE
STRXVH_UrnikDan6On1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].On[1].Ura | BYTE
STRXVH_UrnikDan6On2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].On[2].Mna | BYTE
STRXVH_UrnikDan6On2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].On[2].Ura | BYTE
STRXVH_UrnikDan6On3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].On[3].Mna | BYTE
STRXVH_UrnikDan6On3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[6].On[3].Ura | BYTE
STRXVH_UrnikDan7Off1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[1].Mna | BYTE
STRXVH_UrnikDan7Off1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[1].Ura | BYTE
STRXVH_UrnikDan7Off2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[2].Mna | BYTE
STRXVH_UrnikDan7Off2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[2].Ura | BYTE
STRXVH_UrnikDan7Off3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[3].Mna | BYTE
STRXVH_UrnikDan7Off3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].Off[3].Ura | BYTE
STRXVH_UrnikDan7On1Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].On[1].Mna | BYTE
STRXVH_UrnikDan7On1Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].On[1].Ura | BYTE
STRXVH_UrnikDan7On2Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].On[2].Mna | BYTE
STRXVH_UrnikDan7On2Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].On[2].Ura | BYTE
STRXVH_UrnikDan7On3Mna | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].On[3].Mna | BYTE
STRXVH_UrnikDan7On3Ura | INT | IOD_STR | STR:.XVH_Urnik.Dan[7].On[3].Ura | BYTE
STRXVH_VentilTYValue11 | INT | IOD_STR | STR:.XVH_VentilTYValue[1,1] | BYTE
STRXVH_VentilTYValue12 | INT | IOD_STR | STR:.XVH_VentilTYValue[1,2] | BYTE
STRXVH_VentilTYValue21 | INT | IOD_STR | STR:.XVH_VentilTYValue[2,1] | BYTE
STRXVH_VentilTYValue22 | INT | IOD_STR | STR:.XVH_VentilTYValue[2,2] | BYTE
STRXVH_VentilTYValue31 | INT | IOD_STR | STR:.XVH_VentilTYValue[3,1] | BYTE
STRXVH_VentilTYValue32 | INT | IOD_STR | STR:.XVH_VentilTYValue[3,2] | BYTE
STRXVH_VentilTYValue41 | INT | IOD_STR | STR:.XVH_VentilTYValue[4,1] | BYTE
STRXVH_VentilTYValue42 | INT | IOD_STR | STR:.XVH_VentilTYValue[4,2] | BYTE
STRXVH_VlazilecStatus1 | INT | IOD_STR | STR:.XVH_VlazilecStatus[1] | BYTE
STRXVH_VlazilecStatus2 | INT | IOD_STR | STR:.XVH_VlazilecStatus[2] | BYTE
STRXVHnum10 | INT | IOD_STR | STR:.XVHnum[10] | BYTE
STRXVHnum11 | INT | IOD_STR | STR:.XVHnum[11] | BYTE
STRXVHnum12 | INT | IOD_STR | STR:.XVHnum[12] | BYTE
STRXVHnum13 | INT | IOD_STR | STR:.XVHnum[13] | BYTE
STRXVHnum14 | INT | IOD_STR | STR:.XVHnum[14] | BYTE
STRXVHnum1 | INT | IOD_STR | STR:.XVHnum[1] | BYTE
STRXVHnum2 | INT | IOD_STR | STR:.XVHnum[2] | BYTE
STRXVHnum3 | INT | IOD_STR | STR:.XVHnum[3] | BYTE
STRXVHnum4 | INT | IOD_STR | STR:.XVHnum[4] | BYTE
STRXVHnum5 | INT | IOD_STR | STR:.XVHnum[5] | BYTE
STRXVHnum6 | INT | IOD_STR | STR:.XVHnum[6] | BYTE
STRXVHnum7 | INT | IOD_STR | STR:.XVHnum[7] | BYTE
STRXVHnum8 | INT | IOD_STR | STR:.XVHnum[8] | BYTE
STRXVHnum9 | INT | IOD_STR | STR:.XVHnum[9] | BYTE
STRXVH_CrpalkaGrfsNum | LONG | IOD_STR | STR:.XVH_CrpalkaGrfsNum
STRXVH_StUrnika | LONG | IOD_STR | STR:.XVH_StUrnika
STRATVAlarmTemp | REAL | IOD_STR | STR:.ATVAlarmTemp
STRCirc1CosFi_III | REAL | IOD_STR | STR:.Circ[1].CosFi_III
STRCirc1DelovnaEnergija | REAL | IOD_STR | STR:.Circ[1].DelovnaEnergija
STRCirc1DelovnaMoc_III | REAL | IOD_STR | STR:.Circ[1].DelovnaMoc_III
STRCirc1DelovnaMoc_L1 | REAL | IOD_STR | STR:.Circ[1].DelovnaMoc_L1
STRCirc1DelovnaMoc_L2 | REAL | IOD_STR | STR:.Circ[1].DelovnaMoc_L2
STRCirc1DelovnaMoc_L3 | REAL | IOD_STR | STR:.Circ[1].DelovnaMoc_L3
STRCirc1Frekvenca_L1 | REAL | IOD_STR | STR:.Circ[1].Frekvenca_L1
STRCirc1InduktivnaEnergija | REAL | IOD_STR | STR:.Circ[1].InduktivnaEnergija
STRCirc1InduktivnaMoc_III | REAL | IOD_STR | STR:.Circ[1].InduktivnaMoc_III
STRCirc1JalovaMoc_L1 | REAL | IOD_STR | STR:.Circ[1].JalovaMoc_L1
STRCirc1JalovaMoc_L2 | REAL | IOD_STR | STR:.Circ[1].JalovaMoc_L2
STRCirc1JalovaMoc_L3 | REAL | IOD_STR | STR:.Circ[1].JalovaMoc_L3
STRCirc1KapacitivnaEnergija | REAL | IOD_STR | STR:.Circ[1].KapacitivnaEnergija
STRCirc1KapacitivnaMoc_III | REAL | IOD_STR | STR:.Circ[1].KapacitivnaMoc_III
STRCirc1MaximumDemand | REAL | IOD_STR | STR:.Circ[1].MaximumDemand
STRCirc1Napetost_L1_L2 | REAL | IOD_STR | STR:.Circ[1].Napetost_L1_L2
STRCirc1Napetost_L1_N | REAL | IOD_STR | STR:.Circ[1].Napetost_L1_N
STRCirc1Napetost_L2_L3 | REAL | IOD_STR | STR:.Circ[1].Napetost_L2_L3
STRCirc1Napetost_L2_N | REAL | IOD_STR | STR:.Circ[1].Napetost_L2_N
STRCirc1Napetost_L3_L1 | REAL | IOD_STR | STR:.Circ[1].Napetost_L3_L1
STRCirc1Napetost_L3_N | REAL | IOD_STR | STR:.Circ[1].Napetost_L3_N
STRCirc1NavideznaMoc_III | REAL | IOD_STR | STR:.Circ[1].NavideznaMoc_III
STRCirc1NicelniTok | REAL | IOD_STR | STR:.Circ[1].NicelniTok
STRCirc1PowerFactor_III | REAL | IOD_STR | STR:.Circ[1].PowerFactor_III
STRCirc1PowerFactor_L1 | REAL | IOD_STR | STR:.Circ[1].PowerFactor_L1
STRCirc1PowerFactor_L2 | REAL | IOD_STR | STR:.Circ[1].PowerFactor_L2
STRCirc1PowerFactor_L3 | REAL | IOD_STR | STR:.Circ[1].PowerFactor_L3
STRCirc1THDI_L1 | REAL | IOD_STR | STR:.Circ[1].THDI_L1
STRCirc1THDI_L2 | REAL | IOD_STR | STR:.Circ[1].THDI_L2
STRCirc1THDI_L3 | REAL | IOD_STR | STR:.Circ[1].THDI_L3
STRCirc1THDV_L1 | REAL | IOD_STR | STR:.Circ[1].THDV_L1
STRCirc1THDV_L2 | REAL | IOD_STR | STR:.Circ[1].THDV_L2
STRCirc1THDV_L3 | REAL | IOD_STR | STR:.Circ[1].THDV_L3
STRCirc1Tok_L1 | REAL | IOD_STR | STR:.Circ[1].Tok_L1
STRCirc1Tok_L2 | REAL | IOD_STR | STR:.Circ[1].Tok_L2
STRCirc1Tok_L3 | REAL | IOD_STR | STR:.Circ[1].Tok_L3
STRCirc1TokPovprecje_III | REAL | IOD_STR | STR:.Circ[1].TokPovprecje_III
STRCrpalkeDnfs1Current | REAL | IOD_STR | STR:.CrpalkeDnfs[1].Current
STRCrpalkeDnfs1StarterStatus | REAL | IOD_STR | STR:.CrpalkeDnfs[1].StarterStatus
STRCrpalkeDnfs1Temerature | REAL | IOD_STR | STR:.CrpalkeDnfs[1].Temerature
STRCrpalkeDnfs1TripCode | REAL | IOD_STR | STR:.CrpalkeDnfs[1].TripCode
STRCrpalkeDnfs1UreXC200 | REAL | IOD_STR | STR:.CrpalkeDnfs[1].UreXC200
STRCrpalkeDnfs2Current | REAL | IOD_STR | STR:.CrpalkeDnfs[2].Current
STRCrpalkeDnfs2StarterStatus | REAL | IOD_STR | STR:.CrpalkeDnfs[2].StarterStatus
STRCrpalkeDnfs2Temerature | REAL | IOD_STR | STR:.CrpalkeDnfs[2].Temerature
STRCrpalkeDnfs2TripCode | REAL | IOD_STR | STR:.CrpalkeDnfs[2].TripCode
STRCrpalkeDnfs2UreXC200 | REAL | IOD_STR | STR:.CrpalkeDnfs[2].UreXC200
STRCrpalkeDnfs3Current | REAL | IOD_STR | STR:.CrpalkeDnfs[3].Current
STRCrpalkeDnfs3StarterStatus | REAL | IOD_STR | STR:.CrpalkeDnfs[3].StarterStatus
STRCrpalkeDnfs3Temerature | REAL | IOD_STR | STR:.CrpalkeDnfs[3].Temerature
STRCrpalkeDnfs3TripCode | REAL | IOD_STR | STR:.CrpalkeDnfs[3].TripCode
STRCrpalkeDnfs3UreXC200 | REAL | IOD_STR | STR:.CrpalkeDnfs[3].UreXC200
STRCrpalkeDnfs4Current | REAL | IOD_STR | STR:.CrpalkeDnfs[4].Current
STRCrpalkeDnfs4StarterStatus | REAL | IOD_STR | STR:.CrpalkeDnfs[4].StarterStatus
STRCrpalkeDnfs4Temerature | REAL | IOD_STR | STR:.CrpalkeDnfs[4].Temerature
STRCrpalkeDnfs4TripCode | REAL | IOD_STR | STR:.CrpalkeDnfs[4].TripCode
STRCrpalkeDnfs4UreXC200 | REAL | IOD_STR | STR:.CrpalkeDnfs[4].UreXC200
STRCrpalkeGrfs10DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[10].DeltaSetPoint
STRCrpalkeGrfs10EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[10].EnergijaPoraba
STRCrpalkeGrfs10FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[10].FrekPretvornikDCNapetost
STRCrpalkeGrfs10FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[10].FrekPretvornikDCTok
STRCrpalkeGrfs10FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[10].FreqMax
STRCrpalkeGrfs10FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[10].FreqMin
STRCrpalkeGrfs10FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[10].FreqUpper
STRCrpalkeGrfs10MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[10].MocMax
STRCrpalkeGrfs10MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[10].MocTrenutna
STRCrpalkeGrfs10MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[10].MotorHitrost
STRCrpalkeGrfs10MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[10].MotorTok
STRCrpalkeGrfs10NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[10].NapajanjeTok
STRCrpalkeGrfs10NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[10].NastavitevLokalna
STRCrpalkeGrfs10NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[10].NastavitevTrenutna
STRCrpalkeGrfs10PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[10].PretokMax
STRCrpalkeGrfs10PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[10].PretokMin
STRCrpalkeGrfs10PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[10].PretokTrenutni
STRCrpalkeGrfs10PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[10].PritiskMax
STRCrpalkeGrfs10PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[10].PritiskTrenutni
STRCrpalkeGrfs10ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[10].ReferencaMotorjaHzV
STRCrpalkeGrfs10ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[10].ReferencaRemote
STRCrpalkeGrfs10StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[10].StevecUr2h
STRCrpalkeGrfs10SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[10].SystemFeedback
STRCrpalkeGrfs10SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[10].SystemReference
STRCrpalkeGrfs10TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[10].TemperaturaMotorja
STRCrpalkeGrfs10UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[10].UreXC200
STRCrpalkeGrfs11DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[11].DeltaSetPoint
STRCrpalkeGrfs11EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[11].EnergijaPoraba
STRCrpalkeGrfs11FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[11].FrekPretvornikDCNapetost
STRCrpalkeGrfs11FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[11].FrekPretvornikDCTok
STRCrpalkeGrfs11FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[11].FreqMax
STRCrpalkeGrfs11FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[11].FreqMin
STRCrpalkeGrfs11FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[11].FreqUpper
STRCrpalkeGrfs11MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[11].MocMax
STRCrpalkeGrfs11MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[11].MocTrenutna
STRCrpalkeGrfs11MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[11].MotorHitrost
STRCrpalkeGrfs11MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[11].MotorTok
STRCrpalkeGrfs11NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[11].NapajanjeTok
STRCrpalkeGrfs11NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[11].NastavitevLokalna
STRCrpalkeGrfs11NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[11].NastavitevTrenutna
STRCrpalkeGrfs11PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[11].PretokMax
STRCrpalkeGrfs11PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[11].PretokMin
STRCrpalkeGrfs11PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[11].PretokTrenutni
STRCrpalkeGrfs11PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[11].PritiskMax
STRCrpalkeGrfs11PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[11].PritiskTrenutni
STRCrpalkeGrfs11ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[11].ReferencaMotorjaHzV
STRCrpalkeGrfs11ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[11].ReferencaRemote
STRCrpalkeGrfs11StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[11].StevecUr2h
STRCrpalkeGrfs11SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[11].SystemFeedback
STRCrpalkeGrfs11SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[11].SystemReference
STRCrpalkeGrfs11TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[11].TemperaturaMotorja
STRCrpalkeGrfs11UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[11].UreXC200
STRCrpalkeGrfs12DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[12].DeltaSetPoint
STRCrpalkeGrfs12EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[12].EnergijaPoraba
STRCrpalkeGrfs12FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[12].FrekPretvornikDCNapetost
STRCrpalkeGrfs12FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[12].FrekPretvornikDCTok
STRCrpalkeGrfs12FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[12].FreqMax
STRCrpalkeGrfs12FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[12].FreqMin
STRCrpalkeGrfs12FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[12].FreqUpper
STRCrpalkeGrfs12MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[12].MocMax
STRCrpalkeGrfs12MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[12].MocTrenutna
STRCrpalkeGrfs12MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[12].MotorHitrost
STRCrpalkeGrfs12MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[12].MotorTok
STRCrpalkeGrfs12NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[12].NapajanjeTok
STRCrpalkeGrfs12NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[12].NastavitevLokalna
STRCrpalkeGrfs12NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[12].NastavitevTrenutna
STRCrpalkeGrfs12PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[12].PretokMax
STRCrpalkeGrfs12PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[12].PretokMin
STRCrpalkeGrfs12PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[12].PretokTrenutni
STRCrpalkeGrfs12PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[12].PritiskMax
STRCrpalkeGrfs12PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[12].PritiskTrenutni
STRCrpalkeGrfs12ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[12].ReferencaMotorjaHzV
STRCrpalkeGrfs12ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[12].ReferencaRemote
STRCrpalkeGrfs12StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[12].StevecUr2h
STRCrpalkeGrfs12SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[12].SystemFeedback
STRCrpalkeGrfs12SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[12].SystemReference
STRCrpalkeGrfs12TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[12].TemperaturaMotorja
STRCrpalkeGrfs12UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[12].UreXC200
STRCrpalkeGrfs13DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[13].DeltaSetPoint
STRCrpalkeGrfs13EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[13].EnergijaPoraba
STRCrpalkeGrfs13FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[13].FrekPretvornikDCNapetost
STRCrpalkeGrfs13FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[13].FrekPretvornikDCTok
STRCrpalkeGrfs13FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[13].FreqMax
STRCrpalkeGrfs13FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[13].FreqMin
STRCrpalkeGrfs13FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[13].FreqUpper
STRCrpalkeGrfs13MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[13].MocMax
STRCrpalkeGrfs13MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[13].MocTrenutna
STRCrpalkeGrfs13MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[13].MotorHitrost
STRCrpalkeGrfs13MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[13].MotorTok
STRCrpalkeGrfs13NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[13].NapajanjeTok
STRCrpalkeGrfs13NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[13].NastavitevLokalna
STRCrpalkeGrfs13NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[13].NastavitevTrenutna
STRCrpalkeGrfs13PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[13].PretokMax
STRCrpalkeGrfs13PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[13].PretokMin
STRCrpalkeGrfs13PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[13].PretokTrenutni
STRCrpalkeGrfs13PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[13].PritiskMax
STRCrpalkeGrfs13PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[13].PritiskTrenutni
STRCrpalkeGrfs13ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[13].ReferencaMotorjaHzV
STRCrpalkeGrfs13ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[13].ReferencaRemote
STRCrpalkeGrfs13StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[13].StevecUr2h
STRCrpalkeGrfs13SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[13].SystemFeedback
STRCrpalkeGrfs13SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[13].SystemReference
STRCrpalkeGrfs13TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[13].TemperaturaMotorja
STRCrpalkeGrfs13UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[13].UreXC200
STRCrpalkeGrfs14DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[14].DeltaSetPoint
STRCrpalkeGrfs14EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[14].EnergijaPoraba
STRCrpalkeGrfs14FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[14].FrekPretvornikDCNapetost
STRCrpalkeGrfs14FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[14].FrekPretvornikDCTok
STRCrpalkeGrfs14FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[14].FreqMax
STRCrpalkeGrfs14FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[14].FreqMin
STRCrpalkeGrfs14FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[14].FreqUpper
STRCrpalkeGrfs14MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[14].MocMax
STRCrpalkeGrfs14MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[14].MocTrenutna
STRCrpalkeGrfs14MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[14].MotorHitrost
STRCrpalkeGrfs14MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[14].MotorTok
STRCrpalkeGrfs14NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[14].NapajanjeTok
STRCrpalkeGrfs14NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[14].NastavitevLokalna
STRCrpalkeGrfs14NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[14].NastavitevTrenutna
STRCrpalkeGrfs14PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[14].PretokMax
STRCrpalkeGrfs14PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[14].PretokMin
STRCrpalkeGrfs14PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[14].PretokTrenutni
STRCrpalkeGrfs14PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[14].PritiskMax
STRCrpalkeGrfs14PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[14].PritiskTrenutni
STRCrpalkeGrfs14ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[14].ReferencaMotorjaHzV
STRCrpalkeGrfs14ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[14].ReferencaRemote
STRCrpalkeGrfs14StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[14].StevecUr2h
STRCrpalkeGrfs14SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[14].SystemFeedback
STRCrpalkeGrfs14SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[14].SystemReference
STRCrpalkeGrfs14TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[14].TemperaturaMotorja
STRCrpalkeGrfs14UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[14].UreXC200
STRCrpalkeGrfs1DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[1].DeltaSetPoint
STRCrpalkeGrfs1EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[1].EnergijaPoraba
STRCrpalkeGrfs1FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[1].FrekPretvornikDCNapetost
STRCrpalkeGrfs1FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[1].FrekPretvornikDCTok
STRCrpalkeGrfs1FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[1].FreqMax
STRCrpalkeGrfs1FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[1].FreqMin
STRCrpalkeGrfs1FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[1].FreqUpper
STRCrpalkeGrfs1MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[1].MocMax
STRCrpalkeGrfs1MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[1].MocTrenutna
STRCrpalkeGrfs1MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[1].MotorHitrost
STRCrpalkeGrfs1MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[1].MotorTok
STRCrpalkeGrfs1NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[1].NapajanjeTok
STRCrpalkeGrfs1NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[1].NastavitevLokalna
STRCrpalkeGrfs1NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[1].NastavitevTrenutna
STRCrpalkeGrfs1PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[1].PretokMax
STRCrpalkeGrfs1PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[1].PretokMin
STRCrpalkeGrfs1PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[1].PretokTrenutni
STRCrpalkeGrfs1PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[1].PritiskMax
STRCrpalkeGrfs1PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[1].PritiskTrenutni
STRCrpalkeGrfs1ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[1].ReferencaMotorjaHzV
STRCrpalkeGrfs1ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[1].ReferencaRemote
STRCrpalkeGrfs1StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[1].StevecUr2h
STRCrpalkeGrfs1SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[1].SystemFeedback
STRCrpalkeGrfs1SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[1].SystemReference
STRCrpalkeGrfs1TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[1].TemperaturaMotorja
STRCrpalkeGrfs1UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[1].UreXC200
STRCrpalkeGrfs2DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[2].DeltaSetPoint
STRCrpalkeGrfs2EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[2].EnergijaPoraba
STRCrpalkeGrfs2FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[2].FrekPretvornikDCNapetost
STRCrpalkeGrfs2FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[2].FrekPretvornikDCTok
STRCrpalkeGrfs2FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[2].FreqMax
STRCrpalkeGrfs2FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[2].FreqMin
STRCrpalkeGrfs2FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[2].FreqUpper
STRCrpalkeGrfs2MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[2].MocMax
STRCrpalkeGrfs2MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[2].MocTrenutna
STRCrpalkeGrfs2MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[2].MotorHitrost
STRCrpalkeGrfs2MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[2].MotorTok
STRCrpalkeGrfs2NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[2].NapajanjeTok
STRCrpalkeGrfs2NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[2].NastavitevLokalna
STRCrpalkeGrfs2NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[2].NastavitevTrenutna
STRCrpalkeGrfs2PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[2].PretokMax
STRCrpalkeGrfs2PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[2].PretokMin
STRCrpalkeGrfs2PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[2].PretokTrenutni
STRCrpalkeGrfs2PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[2].PritiskMax
STRCrpalkeGrfs2PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[2].PritiskTrenutni
STRCrpalkeGrfs2ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[2].ReferencaMotorjaHzV
STRCrpalkeGrfs2ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[2].ReferencaRemote
STRCrpalkeGrfs2StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[2].StevecUr2h
STRCrpalkeGrfs2SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[2].SystemFeedback
STRCrpalkeGrfs2SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[2].SystemReference
STRCrpalkeGrfs2TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[2].TemperaturaMotorja
STRCrpalkeGrfs2UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[2].UreXC200
STRCrpalkeGrfs3DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[3].DeltaSetPoint
STRCrpalkeGrfs3EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[3].EnergijaPoraba
STRCrpalkeGrfs3FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[3].FrekPretvornikDCNapetost
STRCrpalkeGrfs3FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[3].FrekPretvornikDCTok
STRCrpalkeGrfs3FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[3].FreqMax
STRCrpalkeGrfs3FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[3].FreqMin
STRCrpalkeGrfs3FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[3].FreqUpper
STRCrpalkeGrfs3MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[3].MocMax
STRCrpalkeGrfs3MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[3].MocTrenutna
STRCrpalkeGrfs3MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[3].MotorHitrost
STRCrpalkeGrfs3MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[3].MotorTok
STRCrpalkeGrfs3NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[3].NapajanjeTok
STRCrpalkeGrfs3NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[3].NastavitevLokalna
STRCrpalkeGrfs3NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[3].NastavitevTrenutna
STRCrpalkeGrfs3PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[3].PretokMax
STRCrpalkeGrfs3PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[3].PretokMin
STRCrpalkeGrfs3PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[3].PretokTrenutni
STRCrpalkeGrfs3PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[3].PritiskMax
STRCrpalkeGrfs3PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[3].PritiskTrenutni
STRCrpalkeGrfs3ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[3].ReferencaMotorjaHzV
STRCrpalkeGrfs3ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[3].ReferencaRemote
STRCrpalkeGrfs3StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[3].StevecUr2h
STRCrpalkeGrfs3SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[3].SystemFeedback
STRCrpalkeGrfs3SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[3].SystemReference
STRCrpalkeGrfs3TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[3].TemperaturaMotorja
STRCrpalkeGrfs3UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[3].UreXC200
STRCrpalkeGrfs4DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[4].DeltaSetPoint
STRCrpalkeGrfs4EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[4].EnergijaPoraba
STRCrpalkeGrfs4FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[4].FrekPretvornikDCNapetost
STRCrpalkeGrfs4FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[4].FrekPretvornikDCTok
STRCrpalkeGrfs4FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[4].FreqMax
STRCrpalkeGrfs4FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[4].FreqMin
STRCrpalkeGrfs4FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[4].FreqUpper
STRCrpalkeGrfs4MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[4].MocMax
STRCrpalkeGrfs4MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[4].MocTrenutna
STRCrpalkeGrfs4MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[4].MotorHitrost
STRCrpalkeGrfs4MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[4].MotorTok
STRCrpalkeGrfs4NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[4].NapajanjeTok
STRCrpalkeGrfs4NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[4].NastavitevLokalna
STRCrpalkeGrfs4NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[4].NastavitevTrenutna
STRCrpalkeGrfs4PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[4].PretokMax
STRCrpalkeGrfs4PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[4].PretokMin
STRCrpalkeGrfs4PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[4].PretokTrenutni
STRCrpalkeGrfs4PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[4].PritiskMax
STRCrpalkeGrfs4PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[4].PritiskTrenutni
STRCrpalkeGrfs4ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[4].ReferencaMotorjaHzV
STRCrpalkeGrfs4ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[4].ReferencaRemote
STRCrpalkeGrfs4StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[4].StevecUr2h
STRCrpalkeGrfs4SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[4].SystemFeedback
STRCrpalkeGrfs4SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[4].SystemReference
STRCrpalkeGrfs4TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[4].TemperaturaMotorja
STRCrpalkeGrfs4UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[4].UreXC200
STRCrpalkeGrfs5DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[5].DeltaSetPoint
STRCrpalkeGrfs5EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[5].EnergijaPoraba
STRCrpalkeGrfs5FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[5].FrekPretvornikDCNapetost
STRCrpalkeGrfs5FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[5].FrekPretvornikDCTok
STRCrpalkeGrfs5FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[5].FreqMax
STRCrpalkeGrfs5FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[5].FreqMin
STRCrpalkeGrfs5FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[5].FreqUpper
STRCrpalkeGrfs5MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[5].MocMax
STRCrpalkeGrfs5MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[5].MocTrenutna
STRCrpalkeGrfs5MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[5].MotorHitrost
STRCrpalkeGrfs5MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[5].MotorTok
STRCrpalkeGrfs5NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[5].NapajanjeTok
STRCrpalkeGrfs5NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[5].NastavitevLokalna
STRCrpalkeGrfs5NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[5].NastavitevTrenutna
STRCrpalkeGrfs5PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[5].PretokMax
STRCrpalkeGrfs5PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[5].PretokMin
STRCrpalkeGrfs5PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[5].PretokTrenutni
STRCrpalkeGrfs5PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[5].PritiskMax
STRCrpalkeGrfs5PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[5].PritiskTrenutni
STRCrpalkeGrfs5ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[5].ReferencaMotorjaHzV
STRCrpalkeGrfs5ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[5].ReferencaRemote
STRCrpalkeGrfs5StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[5].StevecUr2h
STRCrpalkeGrfs5SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[5].SystemFeedback
STRCrpalkeGrfs5SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[5].SystemReference
STRCrpalkeGrfs5TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[5].TemperaturaMotorja
STRCrpalkeGrfs5UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[5].UreXC200
STRCrpalkeGrfs6DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[6].DeltaSetPoint
STRCrpalkeGrfs6EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[6].EnergijaPoraba
STRCrpalkeGrfs6FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[6].FrekPretvornikDCNapetost
STRCrpalkeGrfs6FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[6].FrekPretvornikDCTok
STRCrpalkeGrfs6FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[6].FreqMax
STRCrpalkeGrfs6FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[6].FreqMin
STRCrpalkeGrfs6FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[6].FreqUpper
STRCrpalkeGrfs6MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[6].MocMax
STRCrpalkeGrfs6MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[6].MocTrenutna
STRCrpalkeGrfs6MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[6].MotorHitrost
STRCrpalkeGrfs6MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[6].MotorTok
STRCrpalkeGrfs6NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[6].NapajanjeTok
STRCrpalkeGrfs6NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[6].NastavitevLokalna
STRCrpalkeGrfs6NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[6].NastavitevTrenutna
STRCrpalkeGrfs6PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[6].PretokMax
STRCrpalkeGrfs6PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[6].PretokMin
STRCrpalkeGrfs6PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[6].PretokTrenutni
STRCrpalkeGrfs6PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[6].PritiskMax
STRCrpalkeGrfs6PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[6].PritiskTrenutni
STRCrpalkeGrfs6ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[6].ReferencaMotorjaHzV
STRCrpalkeGrfs6ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[6].ReferencaRemote
STRCrpalkeGrfs6StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[6].StevecUr2h
STRCrpalkeGrfs6SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[6].SystemFeedback
STRCrpalkeGrfs6SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[6].SystemReference
STRCrpalkeGrfs6TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[6].TemperaturaMotorja
STRCrpalkeGrfs6UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[6].UreXC200
STRCrpalkeGrfs7DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[7].DeltaSetPoint
STRCrpalkeGrfs7EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[7].EnergijaPoraba
STRCrpalkeGrfs7FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[7].FrekPretvornikDCNapetost
STRCrpalkeGrfs7FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[7].FrekPretvornikDCTok
STRCrpalkeGrfs7FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[7].FreqMax
STRCrpalkeGrfs7FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[7].FreqMin
STRCrpalkeGrfs7FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[7].FreqUpper
STRCrpalkeGrfs7MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[7].MocMax
STRCrpalkeGrfs7MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[7].MocTrenutna
STRCrpalkeGrfs7MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[7].MotorHitrost
STRCrpalkeGrfs7MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[7].MotorTok
STRCrpalkeGrfs7NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[7].NapajanjeTok
STRCrpalkeGrfs7NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[7].NastavitevLokalna
STRCrpalkeGrfs7NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[7].NastavitevTrenutna
STRCrpalkeGrfs7PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[7].PretokMax
STRCrpalkeGrfs7PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[7].PretokMin
STRCrpalkeGrfs7PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[7].PretokTrenutni
STRCrpalkeGrfs7PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[7].PritiskMax
STRCrpalkeGrfs7PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[7].PritiskTrenutni
STRCrpalkeGrfs7ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[7].ReferencaMotorjaHzV
STRCrpalkeGrfs7ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[7].ReferencaRemote
STRCrpalkeGrfs7StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[7].StevecUr2h
STRCrpalkeGrfs7SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[7].SystemFeedback
STRCrpalkeGrfs7SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[7].SystemReference
STRCrpalkeGrfs7TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[7].TemperaturaMotorja
STRCrpalkeGrfs7UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[7].UreXC200
STRCrpalkeGrfs8DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[8].DeltaSetPoint
STRCrpalkeGrfs8EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[8].EnergijaPoraba
STRCrpalkeGrfs8FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[8].FrekPretvornikDCNapetost
STRCrpalkeGrfs8FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[8].FrekPretvornikDCTok
STRCrpalkeGrfs8FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[8].FreqMax
STRCrpalkeGrfs8FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[8].FreqMin
STRCrpalkeGrfs8FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[8].FreqUpper
STRCrpalkeGrfs8MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[8].MocMax
STRCrpalkeGrfs8MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[8].MocTrenutna
STRCrpalkeGrfs8MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[8].MotorHitrost
STRCrpalkeGrfs8MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[8].MotorTok
STRCrpalkeGrfs8NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[8].NapajanjeTok
STRCrpalkeGrfs8NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[8].NastavitevLokalna
STRCrpalkeGrfs8NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[8].NastavitevTrenutna
STRCrpalkeGrfs8PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[8].PretokMax
STRCrpalkeGrfs8PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[8].PretokMin
STRCrpalkeGrfs8PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[8].PretokTrenutni
STRCrpalkeGrfs8PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[8].PritiskMax
STRCrpalkeGrfs8PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[8].PritiskTrenutni
STRCrpalkeGrfs8ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[8].ReferencaMotorjaHzV
STRCrpalkeGrfs8ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[8].ReferencaRemote
STRCrpalkeGrfs8StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[8].StevecUr2h
STRCrpalkeGrfs8SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[8].SystemFeedback
STRCrpalkeGrfs8SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[8].SystemReference
STRCrpalkeGrfs8TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[8].TemperaturaMotorja
STRCrpalkeGrfs8UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[8].UreXC200
STRCrpalkeGrfs9DeltaSetPoint | REAL | IOD_STR | STR:.CrpalkeGrfs[9].DeltaSetPoint
STRCrpalkeGrfs9EnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfs[9].EnergijaPoraba
STRCrpalkeGrfs9FrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfs[9].FrekPretvornikDCNapetost
STRCrpalkeGrfs9FrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfs[9].FrekPretvornikDCTok
STRCrpalkeGrfs9FreqMax | REAL | IOD_STR | STR:.CrpalkeGrfs[9].FreqMax
STRCrpalkeGrfs9FreqMin | REAL | IOD_STR | STR:.CrpalkeGrfs[9].FreqMin
STRCrpalkeGrfs9FreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfs[9].FreqUpper
STRCrpalkeGrfs9MocMax | REAL | IOD_STR | STR:.CrpalkeGrfs[9].MocMax
STRCrpalkeGrfs9MocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[9].MocTrenutna
STRCrpalkeGrfs9MotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfs[9].MotorHitrost
STRCrpalkeGrfs9MotorTok | REAL | IOD_STR | STR:.CrpalkeGrfs[9].MotorTok
STRCrpalkeGrfs9NapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfs[9].NapajanjeTok
STRCrpalkeGrfs9NastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfs[9].NastavitevLokalna
STRCrpalkeGrfs9NastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfs[9].NastavitevTrenutna
STRCrpalkeGrfs9PretokMax | REAL | IOD_STR | STR:.CrpalkeGrfs[9].PretokMax
STRCrpalkeGrfs9PretokMin | REAL | IOD_STR | STR:.CrpalkeGrfs[9].PretokMin
STRCrpalkeGrfs9PretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[9].PretokTrenutni
STRCrpalkeGrfs9PritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfs[9].PritiskMax
STRCrpalkeGrfs9PritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfs[9].PritiskTrenutni
STRCrpalkeGrfs9ReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfs[9].ReferencaMotorjaHzV
STRCrpalkeGrfs9ReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfs[9].ReferencaRemote
STRCrpalkeGrfs9StevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfs[9].StevecUr2h
STRCrpalkeGrfs9SystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfs[9].SystemFeedback
STRCrpalkeGrfs9SystemReference | REAL | IOD_STR | STR:.CrpalkeGrfs[9].SystemReference
STRCrpalkeGrfs9TemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfs[9].TemperaturaMotorja
STRCrpalkeGrfs9UreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfs[9].UreXC200
STRCrpGrundfosTlakSP1 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[1]
STRCrpGrundfosTlakSP2 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[2]
STRCrpGrundfosTlakSP3 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[3]
STRCrpGrundfosTlakSP4 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[4]
STRCrpGrundfosTlakSP5 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[5]
STRCrpGrundfosTlakSP6 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[6]
STRCrpGrundfosTlakSP7 | REAL | IOD_STR | STR:.CrpGrundfosTlakSP[7]
STRExp1TlakMin | REAL | IOD_STR | STR:.Exp1TlakMin
STRExp2TlakMin | REAL | IOD_STR | STR:.Exp2TlakMin
STRHladStrojObratovalneUre | REAL | IOD_STR | STR:.HladStroj.ObratovalneUre
STRHladStrojPritiskSonda1 | REAL | IOD_STR | STR:.HladStroj.PritiskSonda1
STRHladStrojPritiskSonda2 | REAL | IOD_STR | STR:.HladStroj.PritiskSonda2
STRHladStrojPritiskSonda3 | REAL | IOD_STR | STR:.HladStroj.PritiskSonda3
STRHladStrojPritiskSonda4 | REAL | IOD_STR | STR:.HladStroj.PritiskSonda4
STRHladStrojTempH2OvhodIzparilnika | REAL | IOD_STR | STR:.HladStroj.TempH2OvhodIzparilnika
STRHladStrojTempIzhodnaSonda1 | REAL | IOD_STR | STR:.HladStroj.TempIzhodnaSonda1
STRHladStrojTempIzhodnaSonda3 | REAL | IOD_STR | STR:.HladStroj.TempIzhodnaSonda3
STRHladStrojTempSetPoint | REAL | IOD_STR | STR:.HladStroj.TempSetPoint
STRKlima1HitrostVentilatorjev | REAL | IOD_STR | STR:.Klima[1].HitrostVentilatorjev
STRKlima1NastTempProstora | REAL | IOD_STR | STR:.Klima[1].NastTempProstora
STRKlima1ObratovalneUre | REAL | IOD_STR | STR:.Klima[1].ObratovalneUre
STRKlima1ProtizmrzZasc | REAL | IOD_STR | STR:.Klima[1].ProtizmrzZasc
STRKlima1RezimDelovanja | REAL | IOD_STR | STR:.Klima[1].RezimDelovanja
STRKlima1TemperaturaDovoda | REAL | IOD_STR | STR:.Klima[1].TemperaturaDovoda
STRKlima1TemperaturaProstora | REAL | IOD_STR | STR:.Klima[1].TemperaturaProstora
STRKlima1TempPredRekN2 | REAL | IOD_STR | STR:.Klima[1].TempPredRekN2
STRKlima1TempZaRekN2 | REAL | IOD_STR | STR:.Klima[1].TempZaRekN2
STRKlima1TlakDovKanal | REAL | IOD_STR | STR:.Klima[1].TlakDovKanal
STRKlima1TlakOdvodKanal | REAL | IOD_STR | STR:.Klima[1].TlakOdvodKanal
STRKlima1VlagaDovoda | REAL | IOD_STR | STR:.Klima[1].VlagaDovoda
STRKlima1VlagaVprostor | REAL | IOD_STR | STR:.Klima[1].VlagaVprostor
STRKlima1ZunanjaTemp | REAL | IOD_STR | STR:.Klima[1].ZunanjaTemp
STRKlima2HitrostVentilatorjev | REAL | IOD_STR | STR:.Klima[2].HitrostVentilatorjev
STRKlima2NastTempProstora | REAL | IOD_STR | STR:.Klima[2].NastTempProstora
STRKlima2ObratovalneUre | REAL | IOD_STR | STR:.Klima[2].ObratovalneUre
STRKlima2ProtizmrzZasc | REAL | IOD_STR | STR:.Klima[2].ProtizmrzZasc
STRKlima2RezimDelovanja | REAL | IOD_STR | STR:.Klima[2].RezimDelovanja
STRKlima2TemperaturaDovoda | REAL | IOD_STR | STR:.Klima[2].TemperaturaDovoda
STRKlima2TemperaturaProstora | REAL | IOD_STR | STR:.Klima[2].TemperaturaProstora
STRKlima2TempPredRekN2 | REAL | IOD_STR | STR:.Klima[2].TempPredRekN2
STRKlima2TempZaRekN2 | REAL | IOD_STR | STR:.Klima[2].TempZaRekN2
STRKlima2TlakDovKanal | REAL | IOD_STR | STR:.Klima[2].TlakDovKanal
STRKlima2TlakOdvodKanal | REAL | IOD_STR | STR:.Klima[2].TlakOdvodKanal
STRKlima2VlagaDovoda | REAL | IOD_STR | STR:.Klima[2].VlagaDovoda
STRKlima2VlagaVprostor | REAL | IOD_STR | STR:.Klima[2].VlagaVprostor
STRKlima2ZunanjaTemp | REAL | IOD_STR | STR:.Klima[2].ZunanjaTemp
STRrVersion | REAL | IOD_STR | STR:.rVersion
STRSenzorTempTIA1 | REAL | IOD_STR | STR:.SenzorTempTIA[1]
STRSenzorTempTIA2 | REAL | IOD_STR | STR:.SenzorTempTIA[2]
STRSenzorTempTIA3 | REAL | IOD_STR | STR:.SenzorTempTIA[3]
STRSenzorTempTIA4 | REAL | IOD_STR | STR:.SenzorTempTIA[4]
STRSenzorVlagaHIA1 | REAL | IOD_STR | STR:.SenzorVlagaHIA[1]
STRSenzorVlagaHIA2 | REAL | IOD_STR | STR:.SenzorVlagaHIA[2]
STRSenzorVlagaHIA3 | REAL | IOD_STR | STR:.SenzorVlagaHIA[3]
STRSenzorVlagaHIA4 | REAL | IOD_STR | STR:.SenzorVlagaHIA[4]
STRTEgrelecTempMAX | REAL | IOD_STR | STR:.TEgrelecTempMAX
STRTEgrelecTempMIN | REAL | IOD_STR | STR:.TEgrelecTempMIN
STRTempAlarmPoint | REAL | IOD_STR | STR:.TempAlarmPoint
STRTempTIApovprecna | REAL | IOD_STR | STR:.TempTIApovprecna
STRToplPostHKdotokNastTemp | REAL | IOD_STR | STR:.ToplPost.HKdotokNastTemp
STRToplPostHKdotokTemp | REAL | IOD_STR | STR:.ToplPost.HKdotokTemp
STRToplPostHKpovtatekTemp | REAL | IOD_STR | STR:.ToplPost.HKpovtatekTemp
STRToplPostHKpovtratekNastTemp | REAL | IOD_STR | STR:.ToplPost.HKpovtratekNastTemp
STRToplPostHKzunanjaTemp | REAL | IOD_STR | STR:.ToplPost.HKzunanjaTemp
STRToplPostTVdotokNastTemp | REAL | IOD_STR | STR:.ToplPost.TVdotokNastTemp
STRToplPostTVdotokTemp | REAL | IOD_STR | STR:.ToplPost.TVdotokTemp
STRToplPostTVpovratekTemp | REAL | IOD_STR | STR:.ToplPost.TVpovratekTemp
STRToplPostTVrezervoarTemp | REAL | IOD_STR | STR:.ToplPost.TVrezervoarTemp
STRTYventilMax1 | REAL | IOD_STR | STR:.TYventilMax[1]
STRTYventilMax2 | REAL | IOD_STR | STR:.TYventilMax[2]
STRTYventilMax3 | REAL | IOD_STR | STR:.TYventilMax[3]
STRTYventilMax4 | REAL | IOD_STR | STR:.TYventilMax[4]
STRTYventilMin1 | REAL | IOD_STR | STR:.TYventilMin[1]
STRTYventilMin2 | REAL | IOD_STR | STR:.TYventilMin[2]
STRTYventilMin3 | REAL | IOD_STR | STR:.TYventilMin[3]
STRTYventilMin4 | REAL | IOD_STR | STR:.TYventilMin[4]
STRTYventilTempRazlika1 | REAL | IOD_STR | STR:.TYventilTempRazlika[1]
STRTYventilTempRazlika2 | REAL | IOD_STR | STR:.TYventilTempRazlika[2]
STRTYventilTempRazlika3 | REAL | IOD_STR | STR:.TYventilTempRazlika[3]
STRTYventilTempRazlika4 | REAL | IOD_STR | STR:.TYventilTempRazlika[4]
STRValAI_Temp1B1 | REAL | IOD_STR | STR:.ValAI_Temp1B1
STRValAI_Temp1B2 | REAL | IOD_STR | STR:.ValAI_Temp1B2
STRValAI_Temp1B3 | REAL | IOD_STR | STR:.ValAI_Temp1B3
STRValAI_Temp2B2 | REAL | IOD_STR | STR:.ValAI_Temp2B2
STRValAI_Temp2B3 | REAL | IOD_STR | STR:.ValAI_Temp2B3
STRValAI_TempHB2 | REAL | IOD_STR | STR:.ValAI_TempHB2
STRValAI_TempHB4 | REAL | IOD_STR | STR:.ValAI_TempHB4
STRValAI_TempHB9 | REAL | IOD_STR | STR:.ValAI_TempHB9
STRValAI_TempTB1 | REAL | IOD_STR | STR:.ValAI_TempTB1
STRValAI_TempTB10 | REAL | IOD_STR | STR:.ValAI_TempTB10
STRValAI_TempTB2 | REAL | IOD_STR | STR:.ValAI_TempTB2
STRValAI_TempTB3 | REAL | IOD_STR | STR:.ValAI_TempTB3
STRValAI_TempTB4 | REAL | IOD_STR | STR:.ValAI_TempTB4
STRValAI_TempTB8 | REAL | IOD_STR | STR:.ValAI_TempTB8
STRValAI_TlakExp1S1 | REAL | IOD_STR | STR:.ValAI_TlakExp1S1
STRValAI_TlakExp1S2 | REAL | IOD_STR | STR:.ValAI_TlakExp1S2
STRValAI_TlakExp2S1 | REAL | IOD_STR | STR:.ValAI_TlakExp2S1
STRValAI_TlakExp2S2 | REAL | IOD_STR | STR:.ValAI_TlakExp2S2
STRValAI_TlakHB15 | REAL | IOD_STR | STR:.ValAI_TlakHB15
STRValAI_TlakHB16 | REAL | IOD_STR | STR:.ValAI_TlakHB16
STRValAI_TlakHB17 | REAL | IOD_STR | STR:.ValAI_TlakHB17
STRValAI_TlakHB3 | REAL | IOD_STR | STR:.ValAI_TlakHB3
STRValAI_TlakTB11 | REAL | IOD_STR | STR:.ValAI_TlakTB11
STRValAI_TlakTB12 | REAL | IOD_STR | STR:.ValAI_TlakTB12
STRValAI_TlakTB13 | REAL | IOD_STR | STR:.ValAI_TlakTB13
STRValAI_TlakTB14 | REAL | IOD_STR | STR:.ValAI_TlakTB14
STRValAI_Vlaga1B4 | REAL | IOD_STR | STR:.ValAI_Vlaga1B4
STRValAI_Vlaga2B4 | REAL | IOD_STR | STR:.ValAI_Vlaga2B4
STRValAO_RegVentTY1 | REAL | IOD_STR | STR:.ValAO_RegVentTY[1]
STRValAO_RegVentTY2 | REAL | IOD_STR | STR:.ValAO_RegVentTY[2]
STRValAO_RegVentTY3 | REAL | IOD_STR | STR:.ValAO_RegVentTY[3]
STRValAO_RegVentTY4 | REAL | IOD_STR | STR:.ValAO_RegVentTY[4]
STRVlagaHIApovprecna | REAL | IOD_STR | STR:.VlagaHIApovprecna
STRCircutorCosFi_III | REAL | IOD_STR | STR:.Circutor.CosFi_III
STRCircutorDelovnaEnergija | REAL | IOD_STR | STR:.Circutor.DelovnaEnergija
STRCircutorDelovnaMoc_III | REAL | IOD_STR | STR:.Circutor.DelovnaMoc_III
STRCircutorDelovnaMoc_L1 | REAL | IOD_STR | STR:.Circutor.DelovnaMoc_L1
STRCircutorDelovnaMoc_L2 | REAL | IOD_STR | STR:.Circutor.DelovnaMoc_L2
STRCircutorDelovnaMoc_L3 | REAL | IOD_STR | STR:.Circutor.DelovnaMoc_L3
STRCircutorFrekvenca_L1 | REAL | IOD_STR | STR:.Circutor.Frekvenca_L1
STRCircutorInduktivnaEnergija | REAL | IOD_STR | STR:.Circutor.InduktivnaEnergija
STRCircutorInduktivnaMoc_III | REAL | IOD_STR | STR:.Circutor.InduktivnaMoc_III
STRCircutorJalovaMoc_L1 | REAL | IOD_STR | STR:.Circutor.JalovaMoc_L1
STRCircutorJalovaMoc_L2 | REAL | IOD_STR | STR:.Circutor.JalovaMoc_L2
STRCircutorJalovaMoc_L3 | REAL | IOD_STR | STR:.Circutor.JalovaMoc_L3
STRCircutorKapacitivnaEnergija | REAL | IOD_STR | STR:.Circutor.KapacitivnaEnergija
STRCircutorKapacitivnaMoc_III | REAL | IOD_STR | STR:.Circutor.KapacitivnaMoc_III
STRCircutorMaximumDemand | REAL | IOD_STR | STR:.Circutor.MaximumDemand
STRCircutorNapetost_L1_L2 | REAL | IOD_STR | STR:.Circutor.Napetost_L1_L2
STRCircutorNapetost_L1_N | REAL | IOD_STR | STR:.Circutor.Napetost_L1_N
STRCircutorNapetost_L2_L3 | REAL | IOD_STR | STR:.Circutor.Napetost_L2_L3
STRCircutorNapetost_L2_N | REAL | IOD_STR | STR:.Circutor.Napetost_L2_N
STRCircutorNapetost_L3_L1 | REAL | IOD_STR | STR:.Circutor.Napetost_L3_L1
STRCircutorNapetost_L3_N | REAL | IOD_STR | STR:.Circutor.Napetost_L3_N
STRCircutorNavideznaMoc_III | REAL | IOD_STR | STR:.Circutor.NavideznaMoc_III
STRCircutorNicelniTok | REAL | IOD_STR | STR:.Circutor.NicelniTok
STRCircutorPowerFactor_III | REAL | IOD_STR | STR:.Circutor.PowerFactor_III
STRCircutorPowerFactor_L1 | REAL | IOD_STR | STR:.Circutor.PowerFactor_L1
STRCircutorPowerFactor_L2 | REAL | IOD_STR | STR:.Circutor.PowerFactor_L2
STRCircutorPowerFactor_L3 | REAL | IOD_STR | STR:.Circutor.PowerFactor_L3
STRCircutorTHDI_L1 | REAL | IOD_STR | STR:.Circutor.THDI_L1
STRCircutorTHDI_L2 | REAL | IOD_STR | STR:.Circutor.THDI_L2
STRCircutorTHDI_L3 | REAL | IOD_STR | STR:.Circutor.THDI_L3
STRCircutorTHDV_L1 | REAL | IOD_STR | STR:.Circutor.THDV_L1
STRCircutorTHDV_L2 | REAL | IOD_STR | STR:.Circutor.THDV_L2
STRCircutorTHDV_L3 | REAL | IOD_STR | STR:.Circutor.THDV_L3
STRCircutorTok_L1 | REAL | IOD_STR | STR:.Circutor.Tok_L1
STRCircutorTok_L2 | REAL | IOD_STR | STR:.Circutor.Tok_L2
STRCircutorTok_L3 | REAL | IOD_STR | STR:.Circutor.Tok_L3
STRCircutorTokPovprecje_III | REAL | IOD_STR | STR:.Circutor.TokPovprecje_III
STRCrpalkeGrfsGalEnergijaPoraba | REAL | IOD_STR | STR:.CrpalkeGrfsGal.EnergijaPoraba
STRCrpalkeGrfsGalFrekPretvornikDCNapetost | REAL | IOD_STR | STR:.CrpalkeGrfsGal.FrekPretvornikDCNapetost
STRCrpalkeGrfsGalFrekPretvornikDCTok | REAL | IOD_STR | STR:.CrpalkeGrfsGal.FrekPretvornikDCTok
STRCrpalkeGrfsGalFreqMax | REAL | IOD_STR | STR:.CrpalkeGrfsGal.FreqMax
STRCrpalkeGrfsGalFreqMin | REAL | IOD_STR | STR:.CrpalkeGrfsGal.FreqMin
STRCrpalkeGrfsGalFreqUpper | REAL | IOD_STR | STR:.CrpalkeGrfsGal.FreqUpper
STRCrpalkeGrfsGalMocMax | REAL | IOD_STR | STR:.CrpalkeGrfsGal.MocMax
STRCrpalkeGrfsGalMocTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfsGal.MocTrenutna
STRCrpalkeGrfsGalMotorHitrost | REAL | IOD_STR | STR:.CrpalkeGrfsGal.MotorHitrost
STRCrpalkeGrfsGalMotorTok | REAL | IOD_STR | STR:.CrpalkeGrfsGal.MotorTok
STRCrpalkeGrfsGalNapajanjeTok | REAL | IOD_STR | STR:.CrpalkeGrfsGal.NapajanjeTok
STRCrpalkeGrfsGalNastavitevLokalna | REAL | IOD_STR | STR:.CrpalkeGrfsGal.NastavitevLokalna
STRCrpalkeGrfsGalNastavitevTrenutna | REAL | IOD_STR | STR:.CrpalkeGrfsGal.NastavitevTrenutna
STRCrpalkeGrfsGalPretokMax | REAL | IOD_STR | STR:.CrpalkeGrfsGal.PretokMax
STRCrpalkeGrfsGalPretokMin | REAL | IOD_STR | STR:.CrpalkeGrfsGal.PretokMin
STRCrpalkeGrfsGalPretokTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfsGal.PretokTrenutni
STRCrpalkeGrfsGalPritiskMax | REAL | IOD_STR | STR:.CrpalkeGrfsGal.PritiskMax
STRCrpalkeGrfsGalPritiskTrenutni | REAL | IOD_STR | STR:.CrpalkeGrfsGal.PritiskTrenutni
STRCrpalkeGrfsGalReferencaMotorjaHzV | REAL | IOD_STR | STR:.CrpalkeGrfsGal.ReferencaMotorjaHzV
STRCrpalkeGrfsGalReferencaRemote | REAL | IOD_STR | STR:.CrpalkeGrfsGal.ReferencaRemote
STRCrpalkeGrfsGalStevecUr2h | REAL | IOD_STR | STR:.CrpalkeGrfsGal.StevecUr2h
STRCrpalkeGrfsGalSystemFeedback | REAL | IOD_STR | STR:.CrpalkeGrfsGal.SystemFeedback
STRCrpalkeGrfsGalSystemReference | REAL | IOD_STR | STR:.CrpalkeGrfsGal.SystemReference
STRCrpalkeGrfsGalTemperaturaMotorja | REAL | IOD_STR | STR:.CrpalkeGrfsGal.TemperaturaMotorja
STRCrpalkeGrfsGalUreXC200 | REAL | IOD_STR | STR:.CrpalkeGrfsGal.UreXC200
STRCrpGrfsPIDregKP | REAL | IOD_STR | STR:.CrpGrfsPIDregKP
STRValAI_TempTB5 | REAL | IOD_STR | STR:.ValAI_TempTB5
STRXVH_CrpGrundfosTlakSP | REAL | IOD_STR | STR:.XVH_CrpGrundfosTlakSP
STRXVH_GrafTemp1 | REAL | IOD_STR | STR:.XVH_GrafTemp[1]
STRXVH_GrafTemp2 | REAL | IOD_STR | STR:.XVH_GrafTemp[2]
STRXVH_GrafTemp3 | REAL | IOD_STR | STR:.XVH_GrafTemp[3]
STRXVH_GrafTemp4 | REAL | IOD_STR | STR:.XVH_GrafTemp[4]
STRXVH_GrafTemp5 | REAL | IOD_STR | STR:.XVH_GrafTemp[5]
STRXVH_GrafVlaga1 | REAL | IOD_STR | STR:.XVH_GrafVlaga[1]
STRXVH_GrafVlaga2 | REAL | IOD_STR | STR:.XVH_GrafVlaga[2]
STRXVH_GrafVlaga3 | REAL | IOD_STR | STR:.XVH_GrafVlaga[3]
STRXVH_GrafVlaga4 | REAL | IOD_STR | STR:.XVH_GrafVlaga[4]
STRXVH_GrafVlaga5 | REAL | IOD_STR | STR:.XVH_GrafVlaga[5]
STRXVH_TlakSenzor | REAL | IOD_STR | STR:.XVH_TlakSenzor
STRCirc1MaximumDemandA2 | REAL | IOD_STR | STR:.Circ[1].MaximumDemandA2
STRCirc1MaximumDemandA3 | REAL | IOD_STR | STR:.Circ[1].MaximumDemandA3
STRCirc1RazEner_D_SCADA | REAL | IOD_STR | STR:.Circ[1].RazEner_D_SCADA
STRCirc1RazEner_T_SCADA | REAL | IOD_STR | STR:.Circ[1].RazEner_T_SCADA
STRCirc1RazEner_M_SCADA | REAL | IOD_STR | STR:.Circ[1].RazEner_M_SCADA
STRUserCurrentName | STRING | IOD_STR | STR:.UserCurrentName
STRDate_Time0 | STRING | IOD_STR | STR:.Date_Time[0]
STRDate_Time1 | STRING | IOD_STR | STR:.Date_Time[1]
STRDate_Time2 | STRING | IOD_STR | STR:.Date_Time[2]
STRDate_Time3 | STRING | IOD_STR | STR:.Date_Time[3]
STRkom_nast_cas_izpada | UINT | IOD_STR | STR:.kom_nast_cas_izpada

## variable_3
STRAkumSanVodeTE1OnOff | DIGITAL | IOD_STR_TCP | 1 | 00001 | AkumSanVodeTE1OnOff
STRAlarmGenCirc1 | DIGITAL | IOD_STR_TCP | 2 | 00002 | AlarmGenCirc1
STRAlarmGenComm | DIGITAL | IOD_STR_TCP | 3 | 00003 | AlarmGenComm
STRAlarmGenDI | DIGITAL | IOD_STR_TCP | 4 | 00004 | AlarmGenDI
STRAlarmGenHladPost | DIGITAL | IOD_STR_TCP | 5 | 00005 | AlarmGenHladPost
STRAlarmGenKlima1 | DIGITAL | IOD_STR_TCP | 6 | 00006 | AlarmGenKlima1
STRAlarmGenKlima2 | DIGITAL | IOD_STR_TCP | 7 | 00007 | AlarmGenKlima2
STRAlarmGenLopute | DIGITAL | IOD_STR_TCP | 8 | 00008 | AlarmGenLopute
STRAlarmGenRest | DIGITAL | IOD_STR_TCP | 9 | 00009 | AlarmGenRest
STRAlarmGenSenzor | DIGITAL | IOD_STR_TCP | 10 | 00010 | AlarmGenSenzor
STRAlarmGenTemp | DIGITAL | IOD_STR_TCP | 11 | 00011 | AlarmGenTemp
STRAlarmGenToplPost | DIGITAL | IOD_STR_TCP | 12 | 00012 | AlarmGenToplPost
STRAlarmGenVent | DIGITAL | IOD_STR_TCP | 13 | 00013 | AlarmGenVent
STRAlarmGenVTV | DIGITAL | IOD_STR_TCP | 14 | 00014 | AlarmGenVTV
STRATVTempPrenizka | DIGITAL | IOD_STR_TCP | 15 | 00015 | ATVTempPrenizka
STRComSCADA | DIGITAL | IOD_STR_TCP | 16 | 00016 | ComSCADA
STRComSCADA1 | DIGITAL | IOD_STR_TCP | 17 | 00017 | ComSCADA1
STRCrpalkaMN1OnOff | DIGITAL | IOD_STR_TCP | 18 | 00018 | CrpalkaMN1OnOff
STRCrpalkaTm11TM12OnOff | DIGITAL | IOD_STR_TCP | 19 | 00019 | CrpalkaTm11TM12OnOff
STRCrpalkeDnfs1AlarmAktiven | DIGITAL | IOD_STR_TCP | 20 | 00020 | CrpalkeDnfs[1].AlarmAktiven
STRCrpalkeDnfs1Deluje | DIGITAL | IOD_STR_TCP | 21 | 00021 | CrpalkeDnfs[1].Deluje
STRCrpalkeDnfs1QuickStop | DIGITAL | IOD_STR_TCP | 22 | 00022 | CrpalkeDnfs[1].QuickStop
STRCrpalkeDnfs1RemoteON | DIGITAL | IOD_STR_TCP | 23 | 00023 | CrpalkeDnfs[1].RemoteON
STRCrpalkeDnfs1Reset | DIGITAL | IOD_STR_TCP | 24 | 00024 | CrpalkeDnfs[1].Reset
STRCrpalkeDnfs1Start | DIGITAL | IOD_STR_TCP | 25 | 00025 | CrpalkeDnfs[1].Start
STRCrpalkeDnfs1Stop | DIGITAL | IOD_STR_TCP | 26 | 00026 | CrpalkeDnfs[1].Stop
STRCrpalkeDnfs2AlarmAktiven | DIGITAL | IOD_STR_TCP | 27 | 00027 | CrpalkeDnfs[2].AlarmAktiven
STRCrpalkeDnfs2Deluje | DIGITAL | IOD_STR_TCP | 28 | 00028 | CrpalkeDnfs[2].Deluje
STRCrpalkeDnfs2QuickStop | DIGITAL | IOD_STR_TCP | 29 | 00029 | CrpalkeDnfs[2].QuickStop
STRCrpalkeDnfs2RemoteON | DIGITAL | IOD_STR_TCP | 30 | 00030 | CrpalkeDnfs[2].RemoteON
STRCrpalkeDnfs2Reset | DIGITAL | IOD_STR_TCP | 31 | 00031 | CrpalkeDnfs[2].Reset
STRCrpalkeDnfs2Start | DIGITAL | IOD_STR_TCP | 32 | 00032 | CrpalkeDnfs[2].Start
STRCrpalkeDnfs2Stop | DIGITAL | IOD_STR_TCP | 33 | 00033 | CrpalkeDnfs[2].Stop
STRCrpalkeDnfs3AlarmAktiven | DIGITAL | IOD_STR_TCP | 34 | 00034 | CrpalkeDnfs[3].AlarmAktiven
STRCrpalkeDnfs3Deluje | DIGITAL | IOD_STR_TCP | 35 | 00035 | CrpalkeDnfs[3].Deluje
STRCrpalkeDnfs3QuickStop | DIGITAL | IOD_STR_TCP | 36 | 00036 | CrpalkeDnfs[3].QuickStop
STRCrpalkeDnfs3RemoteON | DIGITAL | IOD_STR_TCP | 37 | 00037 | CrpalkeDnfs[3].RemoteON
STRCrpalkeDnfs3Reset | DIGITAL | IOD_STR_TCP | 38 | 00038 | CrpalkeDnfs[3].Reset
STRCrpalkeDnfs3Start | DIGITAL | IOD_STR_TCP | 39 | 00039 | CrpalkeDnfs[3].Start
STRCrpalkeDnfs3Stop | DIGITAL | IOD_STR_TCP | 40 | 00040 | CrpalkeDnfs[3].Stop
STRCrpalkeDnfs4AlarmAktiven | DIGITAL | IOD_STR_TCP | 41 | 00041 | CrpalkeDnfs[4].AlarmAktiven
STRCrpalkeDnfs4Deluje | DIGITAL | IOD_STR_TCP | 42 | 00042 | CrpalkeDnfs[4].Deluje
STRCrpalkeDnfs4QuickStop | DIGITAL | IOD_STR_TCP | 43 | 00043 | CrpalkeDnfs[4].QuickStop
STRCrpalkeDnfs4RemoteON | DIGITAL | IOD_STR_TCP | 44 | 00044 | CrpalkeDnfs[4].RemoteON
STRCrpalkeDnfs4Reset | DIGITAL | IOD_STR_TCP | 45 | 00045 | CrpalkeDnfs[4].Reset
STRCrpalkeDnfs4Start | DIGITAL | IOD_STR_TCP | 46 | 00046 | CrpalkeDnfs[4].Start
STRCrpalkeDnfs4Stop | DIGITAL | IOD_STR_TCP | 47 | 00047 | CrpalkeDnfs[4].Stop
STRCrpalkeGrfs10AlarmAktiven | DIGITAL | IOD_STR_TCP | 48 | 00048 | CrpalkeGrfs[10].AlarmAktiven
STRCrpalkeGrfs10Deluje | DIGITAL | IOD_STR_TCP | 49 | 00049 | CrpalkeGrfs[10].Deluje
STRCrpalkeGrfs10LocalMode | DIGITAL | IOD_STR_TCP | 50 | 00050 | CrpalkeGrfs[10].LocalMode
STRCrpalkeGrfs10RemoteON | DIGITAL | IOD_STR_TCP | 51 | 00051 | CrpalkeGrfs[10].RemoteON
STRCrpalkeGrfs10Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 52 | 00052 | CrpalkeGrfs[10].Reset2handkWhValues
STRCrpalkeGrfs10ResetAlarm | DIGITAL | IOD_STR_TCP | 53 | 00053 | CrpalkeGrfs[10].ResetAlarm
STRCrpalkeGrfs10ResetAlarmLog | DIGITAL | IOD_STR_TCP | 54 | 00054 | CrpalkeGrfs[10].ResetAlarmLog
STRCrpalkeGrfs10ResetDevice | DIGITAL | IOD_STR_TCP | 55 | 00055 | CrpalkeGrfs[10].ResetDevice
STRCrpalkeGrfs10SetAutomatic | DIGITAL | IOD_STR_TCP | 56 | 00056 | CrpalkeGrfs[10].SetAutomatic
STRCrpalkeGrfs10SetConstFreqMode | DIGITAL | IOD_STR_TCP | 57 | 00057 | CrpalkeGrfs[10].SetConstFreqMode
STRCrpalkeGrfs10SetConstPress | DIGITAL | IOD_STR_TCP | 58 | 00058 | CrpalkeGrfs[10].SetConstPress
STRCrpalkeGrfs10SetLocalMode | DIGITAL | IOD_STR_TCP | 59 | 00059 | CrpalkeGrfs[10].SetLocalMode
STRCrpalkeGrfs10SetMaxRunMode | DIGITAL | IOD_STR_TCP | 60 | 00060 | CrpalkeGrfs[10].SetMaxRunMode
STRCrpalkeGrfs10SetMinRunMode | DIGITAL | IOD_STR_TCP | 61 | 00061 | CrpalkeGrfs[10].SetMinRunMode
STRCrpalkeGrfs10SetPropPress | DIGITAL | IOD_STR_TCP | 62 | 00062 | CrpalkeGrfs[10].SetPropPress
STRCrpalkeGrfs10SetReference | DIGITAL | IOD_STR_TCP | 63 | 00063 | CrpalkeGrfs[10].SetReference
STRCrpalkeGrfs10SetRemoteMode | DIGITAL | IOD_STR_TCP | 64 | 00064 | CrpalkeGrfs[10].SetRemoteMode
STRCrpalkeGrfs10SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 65 | 00065 | CrpalkeGrfs[10].SetTwinModeAlt
STRCrpalkeGrfs10SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 66 | 00066 | CrpalkeGrfs[10].SetTwinModeSpare
STRCrpalkeGrfs10SetTwinModeSync | DIGITAL | IOD_STR_TCP | 67 | 00067 | CrpalkeGrfs[10].SetTwinModeSync
STRCrpalkeGrfs10Start | DIGITAL | IOD_STR_TCP | 68 | 00068 | CrpalkeGrfs[10].Start
STRCrpalkeGrfs10Stop | DIGITAL | IOD_STR_TCP | 69 | 00069 | CrpalkeGrfs[10].Stop
STRCrpalkeGrfs11AlarmAktiven | DIGITAL | IOD_STR_TCP | 70 | 00070 | CrpalkeGrfs[11].AlarmAktiven
STRCrpalkeGrfs11Deluje | DIGITAL | IOD_STR_TCP | 71 | 00071 | CrpalkeGrfs[11].Deluje
STRCrpalkeGrfs11LocalMode | DIGITAL | IOD_STR_TCP | 72 | 00072 | CrpalkeGrfs[11].LocalMode
STRCrpalkeGrfs11RemoteON | DIGITAL | IOD_STR_TCP | 73 | 00073 | CrpalkeGrfs[11].RemoteON
STRCrpalkeGrfs11Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 74 | 00074 | CrpalkeGrfs[11].Reset2handkWhValues
STRCrpalkeGrfs11ResetAlarm | DIGITAL | IOD_STR_TCP | 75 | 00075 | CrpalkeGrfs[11].ResetAlarm
STRCrpalkeGrfs11ResetAlarmLog | DIGITAL | IOD_STR_TCP | 76 | 00076 | CrpalkeGrfs[11].ResetAlarmLog
STRCrpalkeGrfs11ResetDevice | DIGITAL | IOD_STR_TCP | 77 | 00077 | CrpalkeGrfs[11].ResetDevice
STRCrpalkeGrfs11SetAutomatic | DIGITAL | IOD_STR_TCP | 78 | 00078 | CrpalkeGrfs[11].SetAutomatic
STRCrpalkeGrfs11SetConstFreqMode | DIGITAL | IOD_STR_TCP | 79 | 00079 | CrpalkeGrfs[11].SetConstFreqMode
STRCrpalkeGrfs11SetConstPress | DIGITAL | IOD_STR_TCP | 80 | 00080 | CrpalkeGrfs[11].SetConstPress
STRCrpalkeGrfs11SetLocalMode | DIGITAL | IOD_STR_TCP | 81 | 00081 | CrpalkeGrfs[11].SetLocalMode
STRCrpalkeGrfs11SetMaxRunMode | DIGITAL | IOD_STR_TCP | 82 | 00082 | CrpalkeGrfs[11].SetMaxRunMode
STRCrpalkeGrfs11SetMinRunMode | DIGITAL | IOD_STR_TCP | 83 | 00083 | CrpalkeGrfs[11].SetMinRunMode
STRCrpalkeGrfs11SetPropPress | DIGITAL | IOD_STR_TCP | 84 | 00084 | CrpalkeGrfs[11].SetPropPress
STRCrpalkeGrfs11SetReference | DIGITAL | IOD_STR_TCP | 85 | 00085 | CrpalkeGrfs[11].SetReference
STRCrpalkeGrfs11SetRemoteMode | DIGITAL | IOD_STR_TCP | 86 | 00086 | CrpalkeGrfs[11].SetRemoteMode
STRCrpalkeGrfs11SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 87 | 00087 | CrpalkeGrfs[11].SetTwinModeAlt
STRCrpalkeGrfs11SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 88 | 00088 | CrpalkeGrfs[11].SetTwinModeSpare
STRCrpalkeGrfs11SetTwinModeSync | DIGITAL | IOD_STR_TCP | 89 | 00089 | CrpalkeGrfs[11].SetTwinModeSync
STRCrpalkeGrfs11Start | DIGITAL | IOD_STR_TCP | 90 | 00090 | CrpalkeGrfs[11].Start
STRCrpalkeGrfs11Stop | DIGITAL | IOD_STR_TCP | 91 | 00091 | CrpalkeGrfs[11].Stop
STRCrpalkeGrfs12AlarmAktiven | DIGITAL | IOD_STR_TCP | 92 | 00092 | CrpalkeGrfs[12].AlarmAktiven
STRCrpalkeGrfs12Deluje | DIGITAL | IOD_STR_TCP | 93 | 00093 | CrpalkeGrfs[12].Deluje
STRCrpalkeGrfs12LocalMode | DIGITAL | IOD_STR_TCP | 94 | 00094 | CrpalkeGrfs[12].LocalMode
STRCrpalkeGrfs12RemoteON | DIGITAL | IOD_STR_TCP | 95 | 00095 | CrpalkeGrfs[12].RemoteON
STRCrpalkeGrfs12Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 96 | 00096 | CrpalkeGrfs[12].Reset2handkWhValues
STRCrpalkeGrfs12ResetAlarm | DIGITAL | IOD_STR_TCP | 97 | 00097 | CrpalkeGrfs[12].ResetAlarm
STRCrpalkeGrfs12ResetAlarmLog | DIGITAL | IOD_STR_TCP | 98 | 00098 | CrpalkeGrfs[12].ResetAlarmLog
STRCrpalkeGrfs12ResetDevice | DIGITAL | IOD_STR_TCP | 99 | 00099 | CrpalkeGrfs[12].ResetDevice
STRCrpalkeGrfs12SetAutomatic | DIGITAL | IOD_STR_TCP | 100 | 00100 | CrpalkeGrfs[12].SetAutomatic
STRCrpalkeGrfs12SetConstFreqMode | DIGITAL | IOD_STR_TCP | 101 | 00101 | CrpalkeGrfs[12].SetConstFreqMode
STRCrpalkeGrfs12SetConstPress | DIGITAL | IOD_STR_TCP | 102 | 00102 | CrpalkeGrfs[12].SetConstPress
STRCrpalkeGrfs12SetLocalMode | DIGITAL | IOD_STR_TCP | 103 | 00103 | CrpalkeGrfs[12].SetLocalMode
STRCrpalkeGrfs12SetMaxRunMode | DIGITAL | IOD_STR_TCP | 104 | 00104 | CrpalkeGrfs[12].SetMaxRunMode
STRCrpalkeGrfs12SetMinRunMode | DIGITAL | IOD_STR_TCP | 105 | 00105 | CrpalkeGrfs[12].SetMinRunMode
STRCrpalkeGrfs12SetPropPress | DIGITAL | IOD_STR_TCP | 106 | 00106 | CrpalkeGrfs[12].SetPropPress
STRCrpalkeGrfs12SetReference | DIGITAL | IOD_STR_TCP | 107 | 00107 | CrpalkeGrfs[12].SetReference
STRCrpalkeGrfs12SetRemoteMode | DIGITAL | IOD_STR_TCP | 108 | 00108 | CrpalkeGrfs[12].SetRemoteMode
STRCrpalkeGrfs12SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 109 | 00109 | CrpalkeGrfs[12].SetTwinModeAlt
STRCrpalkeGrfs12SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 110 | 00110 | CrpalkeGrfs[12].SetTwinModeSpare
STRCrpalkeGrfs12SetTwinModeSync | DIGITAL | IOD_STR_TCP | 111 | 00111 | CrpalkeGrfs[12].SetTwinModeSync
STRCrpalkeGrfs12Start | DIGITAL | IOD_STR_TCP | 112 | 00112 | CrpalkeGrfs[12].Start
STRCrpalkeGrfs12Stop | DIGITAL | IOD_STR_TCP | 113 | 00113 | CrpalkeGrfs[12].Stop
STRCrpalkeGrfs13AlarmAktiven | DIGITAL | IOD_STR_TCP | 114 | 00114 | CrpalkeGrfs[13].AlarmAktiven
STRCrpalkeGrfs13Deluje | DIGITAL | IOD_STR_TCP | 115 | 00115 | CrpalkeGrfs[13].Deluje
STRCrpalkeGrfs13LocalMode | DIGITAL | IOD_STR_TCP | 116 | 00116 | CrpalkeGrfs[13].LocalMode
STRCrpalkeGrfs13RemoteON | DIGITAL | IOD_STR_TCP | 117 | 00117 | CrpalkeGrfs[13].RemoteON
STRCrpalkeGrfs13Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 118 | 00118 | CrpalkeGrfs[13].Reset2handkWhValues
STRCrpalkeGrfs13ResetAlarm | DIGITAL | IOD_STR_TCP | 119 | 00119 | CrpalkeGrfs[13].ResetAlarm
STRCrpalkeGrfs13ResetAlarmLog | DIGITAL | IOD_STR_TCP | 120 | 00120 | CrpalkeGrfs[13].ResetAlarmLog
STRCrpalkeGrfs13ResetDevice | DIGITAL | IOD_STR_TCP | 121 | 00121 | CrpalkeGrfs[13].ResetDevice
STRCrpalkeGrfs13SetAutomatic | DIGITAL | IOD_STR_TCP | 122 | 00122 | CrpalkeGrfs[13].SetAutomatic
STRCrpalkeGrfs13SetConstFreqMode | DIGITAL | IOD_STR_TCP | 123 | 00123 | CrpalkeGrfs[13].SetConstFreqMode
STRCrpalkeGrfs13SetConstPress | DIGITAL | IOD_STR_TCP | 124 | 00124 | CrpalkeGrfs[13].SetConstPress
STRCrpalkeGrfs13SetLocalMode | DIGITAL | IOD_STR_TCP | 125 | 00125 | CrpalkeGrfs[13].SetLocalMode
STRCrpalkeGrfs13SetMaxRunMode | DIGITAL | IOD_STR_TCP | 126 | 00126 | CrpalkeGrfs[13].SetMaxRunMode
STRCrpalkeGrfs13SetMinRunMode | DIGITAL | IOD_STR_TCP | 127 | 00127 | CrpalkeGrfs[13].SetMinRunMode
STRCrpalkeGrfs13SetPropPress | DIGITAL | IOD_STR_TCP | 128 | 00128 | CrpalkeGrfs[13].SetPropPress
STRCrpalkeGrfs13SetReference | DIGITAL | IOD_STR_TCP | 129 | 00129 | CrpalkeGrfs[13].SetReference
STRCrpalkeGrfs13SetRemoteMode | DIGITAL | IOD_STR_TCP | 130 | 00130 | CrpalkeGrfs[13].SetRemoteMode
STRCrpalkeGrfs13SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 131 | 00131 | CrpalkeGrfs[13].SetTwinModeAlt
STRCrpalkeGrfs13SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 132 | 00132 | CrpalkeGrfs[13].SetTwinModeSpare
STRCrpalkeGrfs13SetTwinModeSync | DIGITAL | IOD_STR_TCP | 133 | 00133 | CrpalkeGrfs[13].SetTwinModeSync
STRCrpalkeGrfs13Start | DIGITAL | IOD_STR_TCP | 134 | 00134 | CrpalkeGrfs[13].Start
STRCrpalkeGrfs13Stop | DIGITAL | IOD_STR_TCP | 135 | 00135 | CrpalkeGrfs[13].Stop
STRCrpalkeGrfs14AlarmAktiven | DIGITAL | IOD_STR_TCP | 136 | 00136 | CrpalkeGrfs[14].AlarmAktiven
STRCrpalkeGrfs14Deluje | DIGITAL | IOD_STR_TCP | 137 | 00137 | CrpalkeGrfs[14].Deluje
STRCrpalkeGrfs14LocalMode | DIGITAL | IOD_STR_TCP | 138 | 00138 | CrpalkeGrfs[14].LocalMode
STRCrpalkeGrfs14RemoteON | DIGITAL | IOD_STR_TCP | 139 | 00139 | CrpalkeGrfs[14].RemoteON
STRCrpalkeGrfs14Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 140 | 00140 | CrpalkeGrfs[14].Reset2handkWhValues
STRCrpalkeGrfs14ResetAlarm | DIGITAL | IOD_STR_TCP | 141 | 00141 | CrpalkeGrfs[14].ResetAlarm
STRCrpalkeGrfs14ResetAlarmLog | DIGITAL | IOD_STR_TCP | 142 | 00142 | CrpalkeGrfs[14].ResetAlarmLog
STRCrpalkeGrfs14ResetDevice | DIGITAL | IOD_STR_TCP | 143 | 00143 | CrpalkeGrfs[14].ResetDevice
STRCrpalkeGrfs14SetAutomatic | DIGITAL | IOD_STR_TCP | 144 | 00144 | CrpalkeGrfs[14].SetAutomatic
STRCrpalkeGrfs14SetConstFreqMode | DIGITAL | IOD_STR_TCP | 145 | 00145 | CrpalkeGrfs[14].SetConstFreqMode
STRCrpalkeGrfs14SetConstPress | DIGITAL | IOD_STR_TCP | 146 | 00146 | CrpalkeGrfs[14].SetConstPress
STRCrpalkeGrfs14SetLocalMode | DIGITAL | IOD_STR_TCP | 147 | 00147 | CrpalkeGrfs[14].SetLocalMode
STRCrpalkeGrfs14SetMaxRunMode | DIGITAL | IOD_STR_TCP | 148 | 00148 | CrpalkeGrfs[14].SetMaxRunMode
STRCrpalkeGrfs14SetMinRunMode | DIGITAL | IOD_STR_TCP | 149 | 00149 | CrpalkeGrfs[14].SetMinRunMode
STRCrpalkeGrfs14SetPropPress | DIGITAL | IOD_STR_TCP | 150 | 00150 | CrpalkeGrfs[14].SetPropPress
STRCrpalkeGrfs14SetReference | DIGITAL | IOD_STR_TCP | 151 | 00151 | CrpalkeGrfs[14].SetReference
STRCrpalkeGrfs14SetRemoteMode | DIGITAL | IOD_STR_TCP | 152 | 00152 | CrpalkeGrfs[14].SetRemoteMode
STRCrpalkeGrfs14SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 153 | 00153 | CrpalkeGrfs[14].SetTwinModeAlt
STRCrpalkeGrfs14SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 154 | 00154 | CrpalkeGrfs[14].SetTwinModeSpare
STRCrpalkeGrfs14SetTwinModeSync | DIGITAL | IOD_STR_TCP | 155 | 00155 | CrpalkeGrfs[14].SetTwinModeSync
STRCrpalkeGrfs14Start | DIGITAL | IOD_STR_TCP | 156 | 00156 | CrpalkeGrfs[14].Start
STRCrpalkeGrfs14Stop | DIGITAL | IOD_STR_TCP | 157 | 00157 | CrpalkeGrfs[14].Stop
STRCrpalkeGrfs1AlarmAktiven | DIGITAL | IOD_STR_TCP | 158 | 00158 | CrpalkeGrfs[1].AlarmAktiven
STRCrpalkeGrfs1Deluje | DIGITAL | IOD_STR_TCP | 159 | 00159 | CrpalkeGrfs[1].Deluje
STRCrpalkeGrfs1LocalMode | DIGITAL | IOD_STR_TCP | 160 | 00160 | CrpalkeGrfs[1].LocalMode
STRCrpalkeGrfs1RemoteON | DIGITAL | IOD_STR_TCP | 161 | 00161 | CrpalkeGrfs[1].RemoteON
STRCrpalkeGrfs1Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 162 | 00162 | CrpalkeGrfs[1].Reset2handkWhValues
STRCrpalkeGrfs1ResetAlarm | DIGITAL | IOD_STR_TCP | 163 | 00163 | CrpalkeGrfs[1].ResetAlarm
STRCrpalkeGrfs1ResetAlarmLog | DIGITAL | IOD_STR_TCP | 164 | 00164 | CrpalkeGrfs[1].ResetAlarmLog
STRCrpalkeGrfs1ResetDevice | DIGITAL | IOD_STR_TCP | 165 | 00165 | CrpalkeGrfs[1].ResetDevice
STRCrpalkeGrfs1SetAutomatic | DIGITAL | IOD_STR_TCP | 166 | 00166 | CrpalkeGrfs[1].SetAutomatic
STRCrpalkeGrfs1SetConstFreqMode | DIGITAL | IOD_STR_TCP | 167 | 00167 | CrpalkeGrfs[1].SetConstFreqMode
STRCrpalkeGrfs1SetConstPress | DIGITAL | IOD_STR_TCP | 168 | 00168 | CrpalkeGrfs[1].SetConstPress
STRCrpalkeGrfs1SetLocalMode | DIGITAL | IOD_STR_TCP | 169 | 00169 | CrpalkeGrfs[1].SetLocalMode
STRCrpalkeGrfs1SetMaxRunMode | DIGITAL | IOD_STR_TCP | 170 | 00170 | CrpalkeGrfs[1].SetMaxRunMode
STRCrpalkeGrfs1SetMinRunMode | DIGITAL | IOD_STR_TCP | 171 | 00171 | CrpalkeGrfs[1].SetMinRunMode
STRCrpalkeGrfs1SetPropPress | DIGITAL | IOD_STR_TCP | 172 | 00172 | CrpalkeGrfs[1].SetPropPress
STRCrpalkeGrfs1SetReference | DIGITAL | IOD_STR_TCP | 173 | 00173 | CrpalkeGrfs[1].SetReference
STRCrpalkeGrfs1SetRemoteMode | DIGITAL | IOD_STR_TCP | 174 | 00174 | CrpalkeGrfs[1].SetRemoteMode
STRCrpalkeGrfs1SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 175 | 00175 | CrpalkeGrfs[1].SetTwinModeAlt
STRCrpalkeGrfs1SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 176 | 00176 | CrpalkeGrfs[1].SetTwinModeSpare
STRCrpalkeGrfs1SetTwinModeSync | DIGITAL | IOD_STR_TCP | 177 | 00177 | CrpalkeGrfs[1].SetTwinModeSync
STRCrpalkeGrfs1Start | DIGITAL | IOD_STR_TCP | 178 | 00178 | CrpalkeGrfs[1].Start
STRCrpalkeGrfs1Stop | DIGITAL | IOD_STR_TCP | 179 | 00179 | CrpalkeGrfs[1].Stop
STRCrpalkeGrfs2AlarmAktiven | DIGITAL | IOD_STR_TCP | 180 | 00180 | CrpalkeGrfs[2].AlarmAktiven
STRCrpalkeGrfs2Deluje | DIGITAL | IOD_STR_TCP | 181 | 00181 | CrpalkeGrfs[2].Deluje
STRCrpalkeGrfs2LocalMode | DIGITAL | IOD_STR_TCP | 182 | 00182 | CrpalkeGrfs[2].LocalMode
STRCrpalkeGrfs2RemoteON | DIGITAL | IOD_STR_TCP | 183 | 00183 | CrpalkeGrfs[2].RemoteON
STRCrpalkeGrfs2Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 184 | 00184 | CrpalkeGrfs[2].Reset2handkWhValues
STRCrpalkeGrfs2ResetAlarm | DIGITAL | IOD_STR_TCP | 185 | 00185 | CrpalkeGrfs[2].ResetAlarm
STRCrpalkeGrfs2ResetAlarmLog | DIGITAL | IOD_STR_TCP | 186 | 00186 | CrpalkeGrfs[2].ResetAlarmLog
STRCrpalkeGrfs2ResetDevice | DIGITAL | IOD_STR_TCP | 187 | 00187 | CrpalkeGrfs[2].ResetDevice
STRCrpalkeGrfs2SetAutomatic | DIGITAL | IOD_STR_TCP | 188 | 00188 | CrpalkeGrfs[2].SetAutomatic
STRCrpalkeGrfs2SetConstFreqMode | DIGITAL | IOD_STR_TCP | 189 | 00189 | CrpalkeGrfs[2].SetConstFreqMode
STRCrpalkeGrfs2SetConstPress | DIGITAL | IOD_STR_TCP | 190 | 00190 | CrpalkeGrfs[2].SetConstPress
STRCrpalkeGrfs2SetLocalMode | DIGITAL | IOD_STR_TCP | 191 | 00191 | CrpalkeGrfs[2].SetLocalMode
STRCrpalkeGrfs2SetMaxRunMode | DIGITAL | IOD_STR_TCP | 192 | 00192 | CrpalkeGrfs[2].SetMaxRunMode
STRCrpalkeGrfs2SetMinRunMode | DIGITAL | IOD_STR_TCP | 193 | 00193 | CrpalkeGrfs[2].SetMinRunMode
STRCrpalkeGrfs2SetPropPress | DIGITAL | IOD_STR_TCP | 194 | 00194 | CrpalkeGrfs[2].SetPropPress
STRCrpalkeGrfs2SetReference | DIGITAL | IOD_STR_TCP | 195 | 00195 | CrpalkeGrfs[2].SetReference
STRCrpalkeGrfs2SetRemoteMode | DIGITAL | IOD_STR_TCP | 196 | 00196 | CrpalkeGrfs[2].SetRemoteMode
STRCrpalkeGrfs2SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 197 | 00197 | CrpalkeGrfs[2].SetTwinModeAlt
STRCrpalkeGrfs2SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 198 | 00198 | CrpalkeGrfs[2].SetTwinModeSpare
STRCrpalkeGrfs2SetTwinModeSync | DIGITAL | IOD_STR_TCP | 199 | 00199 | CrpalkeGrfs[2].SetTwinModeSync
STRCrpalkeGrfs2Start | DIGITAL | IOD_STR_TCP | 200 | 00200 | CrpalkeGrfs[2].Start
STRCrpalkeGrfs2Stop | DIGITAL | IOD_STR_TCP | 201 | 00201 | CrpalkeGrfs[2].Stop
STRCrpalkeGrfs3AlarmAktiven | DIGITAL | IOD_STR_TCP | 202 | 00202 | CrpalkeGrfs[3].AlarmAktiven
STRCrpalkeGrfs3Deluje | DIGITAL | IOD_STR_TCP | 203 | 00203 | CrpalkeGrfs[3].Deluje
STRCrpalkeGrfs3LocalMode | DIGITAL | IOD_STR_TCP | 204 | 00204 | CrpalkeGrfs[3].LocalMode
STRCrpalkeGrfs3RemoteON | DIGITAL | IOD_STR_TCP | 205 | 00205 | CrpalkeGrfs[3].RemoteON
STRCrpalkeGrfs3Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 206 | 00206 | CrpalkeGrfs[3].Reset2handkWhValues
STRCrpalkeGrfs3ResetAlarm | DIGITAL | IOD_STR_TCP | 207 | 00207 | CrpalkeGrfs[3].ResetAlarm
STRCrpalkeGrfs3ResetAlarmLog | DIGITAL | IOD_STR_TCP | 208 | 00208 | CrpalkeGrfs[3].ResetAlarmLog
STRCrpalkeGrfs3ResetDevice | DIGITAL | IOD_STR_TCP | 209 | 00209 | CrpalkeGrfs[3].ResetDevice
STRCrpalkeGrfs3SetAutomatic | DIGITAL | IOD_STR_TCP | 210 | 00210 | CrpalkeGrfs[3].SetAutomatic
STRCrpalkeGrfs3SetConstFreqMode | DIGITAL | IOD_STR_TCP | 211 | 00211 | CrpalkeGrfs[3].SetConstFreqMode
STRCrpalkeGrfs3SetConstPress | DIGITAL | IOD_STR_TCP | 212 | 00212 | CrpalkeGrfs[3].SetConstPress
STRCrpalkeGrfs3SetLocalMode | DIGITAL | IOD_STR_TCP | 213 | 00213 | CrpalkeGrfs[3].SetLocalMode
STRCrpalkeGrfs3SetMaxRunMode | DIGITAL | IOD_STR_TCP | 214 | 00214 | CrpalkeGrfs[3].SetMaxRunMode
STRCrpalkeGrfs3SetMinRunMode | DIGITAL | IOD_STR_TCP | 215 | 00215 | CrpalkeGrfs[3].SetMinRunMode
STRCrpalkeGrfs3SetPropPress | DIGITAL | IOD_STR_TCP | 216 | 00216 | CrpalkeGrfs[3].SetPropPress
STRCrpalkeGrfs3SetReference | DIGITAL | IOD_STR_TCP | 217 | 00217 | CrpalkeGrfs[3].SetReference
STRCrpalkeGrfs3SetRemoteMode | DIGITAL | IOD_STR_TCP | 218 | 00218 | CrpalkeGrfs[3].SetRemoteMode
STRCrpalkeGrfs3SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 219 | 00219 | CrpalkeGrfs[3].SetTwinModeAlt
STRCrpalkeGrfs3SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 220 | 00220 | CrpalkeGrfs[3].SetTwinModeSpare
STRCrpalkeGrfs3SetTwinModeSync | DIGITAL | IOD_STR_TCP | 221 | 00221 | CrpalkeGrfs[3].SetTwinModeSync
STRCrpalkeGrfs3Start | DIGITAL | IOD_STR_TCP | 222 | 00222 | CrpalkeGrfs[3].Start
STRCrpalkeGrfs3Stop | DIGITAL | IOD_STR_TCP | 223 | 00223 | CrpalkeGrfs[3].Stop
STRCrpalkeGrfs4AlarmAktiven | DIGITAL | IOD_STR_TCP | 224 | 00224 | CrpalkeGrfs[4].AlarmAktiven
STRCrpalkeGrfs4Deluje | DIGITAL | IOD_STR_TCP | 225 | 00225 | CrpalkeGrfs[4].Deluje
STRCrpalkeGrfs4LocalMode | DIGITAL | IOD_STR_TCP | 226 | 00226 | CrpalkeGrfs[4].LocalMode
STRCrpalkeGrfs4RemoteON | DIGITAL | IOD_STR_TCP | 227 | 00227 | CrpalkeGrfs[4].RemoteON
STRCrpalkeGrfs4Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 228 | 00228 | CrpalkeGrfs[4].Reset2handkWhValues
STRCrpalkeGrfs4ResetAlarm | DIGITAL | IOD_STR_TCP | 229 | 00229 | CrpalkeGrfs[4].ResetAlarm
STRCrpalkeGrfs4ResetAlarmLog | DIGITAL | IOD_STR_TCP | 230 | 00230 | CrpalkeGrfs[4].ResetAlarmLog
STRCrpalkeGrfs4ResetDevice | DIGITAL | IOD_STR_TCP | 231 | 00231 | CrpalkeGrfs[4].ResetDevice
STRCrpalkeGrfs4SetAutomatic | DIGITAL | IOD_STR_TCP | 232 | 00232 | CrpalkeGrfs[4].SetAutomatic
STRCrpalkeGrfs4SetConstFreqMode | DIGITAL | IOD_STR_TCP | 233 | 00233 | CrpalkeGrfs[4].SetConstFreqMode
STRCrpalkeGrfs4SetConstPress | DIGITAL | IOD_STR_TCP | 234 | 00234 | CrpalkeGrfs[4].SetConstPress
STRCrpalkeGrfs4SetLocalMode | DIGITAL | IOD_STR_TCP | 235 | 00235 | CrpalkeGrfs[4].SetLocalMode
STRCrpalkeGrfs4SetMaxRunMode | DIGITAL | IOD_STR_TCP | 236 | 00236 | CrpalkeGrfs[4].SetMaxRunMode
STRCrpalkeGrfs4SetMinRunMode | DIGITAL | IOD_STR_TCP | 237 | 00237 | CrpalkeGrfs[4].SetMinRunMode
STRCrpalkeGrfs4SetPropPress | DIGITAL | IOD_STR_TCP | 238 | 00238 | CrpalkeGrfs[4].SetPropPress
STRCrpalkeGrfs4SetReference | DIGITAL | IOD_STR_TCP | 239 | 00239 | CrpalkeGrfs[4].SetReference
STRCrpalkeGrfs4SetRemoteMode | DIGITAL | IOD_STR_TCP | 240 | 00240 | CrpalkeGrfs[4].SetRemoteMode
STRCrpalkeGrfs4SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 241 | 00241 | CrpalkeGrfs[4].SetTwinModeAlt
STRCrpalkeGrfs4SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 242 | 00242 | CrpalkeGrfs[4].SetTwinModeSpare
STRCrpalkeGrfs4SetTwinModeSync | DIGITAL | IOD_STR_TCP | 243 | 00243 | CrpalkeGrfs[4].SetTwinModeSync
STRCrpalkeGrfs4Start | DIGITAL | IOD_STR_TCP | 244 | 00244 | CrpalkeGrfs[4].Start
STRCrpalkeGrfs4Stop | DIGITAL | IOD_STR_TCP | 245 | 00245 | CrpalkeGrfs[4].Stop
STRCrpalkeGrfs5AlarmAktiven | DIGITAL | IOD_STR_TCP | 246 | 00246 | CrpalkeGrfs[5].AlarmAktiven
STRCrpalkeGrfs5Deluje | DIGITAL | IOD_STR_TCP | 247 | 00247 | CrpalkeGrfs[5].Deluje
STRCrpalkeGrfs5LocalMode | DIGITAL | IOD_STR_TCP | 248 | 00248 | CrpalkeGrfs[5].LocalMode
STRCrpalkeGrfs5RemoteON | DIGITAL | IOD_STR_TCP | 249 | 00249 | CrpalkeGrfs[5].RemoteON
STRCrpalkeGrfs5Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 250 | 00250 | CrpalkeGrfs[5].Reset2handkWhValues
STRCrpalkeGrfs5ResetAlarm | DIGITAL | IOD_STR_TCP | 251 | 00251 | CrpalkeGrfs[5].ResetAlarm
STRCrpalkeGrfs5ResetAlarmLog | DIGITAL | IOD_STR_TCP | 252 | 00252 | CrpalkeGrfs[5].ResetAlarmLog
STRCrpalkeGrfs5ResetDevice | DIGITAL | IOD_STR_TCP | 253 | 00253 | CrpalkeGrfs[5].ResetDevice
STRCrpalkeGrfs5SetAutomatic | DIGITAL | IOD_STR_TCP | 254 | 00254 | CrpalkeGrfs[5].SetAutomatic
STRCrpalkeGrfs5SetConstFreqMode | DIGITAL | IOD_STR_TCP | 255 | 00255 | CrpalkeGrfs[5].SetConstFreqMode
STRCrpalkeGrfs5SetConstPress | DIGITAL | IOD_STR_TCP | 256 | 00256 | CrpalkeGrfs[5].SetConstPress
STRCrpalkeGrfs5SetLocalMode | DIGITAL | IOD_STR_TCP | 257 | 00257 | CrpalkeGrfs[5].SetLocalMode
STRCrpalkeGrfs5SetMaxRunMode | DIGITAL | IOD_STR_TCP | 258 | 00258 | CrpalkeGrfs[5].SetMaxRunMode
STRCrpalkeGrfs5SetMinRunMode | DIGITAL | IOD_STR_TCP | 259 | 00259 | CrpalkeGrfs[5].SetMinRunMode
STRCrpalkeGrfs5SetPropPress | DIGITAL | IOD_STR_TCP | 260 | 00260 | CrpalkeGrfs[5].SetPropPress
STRCrpalkeGrfs5SetReference | DIGITAL | IOD_STR_TCP | 261 | 00261 | CrpalkeGrfs[5].SetReference
STRCrpalkeGrfs5SetRemoteMode | DIGITAL | IOD_STR_TCP | 262 | 00262 | CrpalkeGrfs[5].SetRemoteMode
STRCrpalkeGrfs5SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 263 | 00263 | CrpalkeGrfs[5].SetTwinModeAlt
STRCrpalkeGrfs5SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 264 | 00264 | CrpalkeGrfs[5].SetTwinModeSpare
STRCrpalkeGrfs5SetTwinModeSync | DIGITAL | IOD_STR_TCP | 265 | 00265 | CrpalkeGrfs[5].SetTwinModeSync
STRCrpalkeGrfs5Start | DIGITAL | IOD_STR_TCP | 266 | 00266 | CrpalkeGrfs[5].Start
STRCrpalkeGrfs5Stop | DIGITAL | IOD_STR_TCP | 267 | 00267 | CrpalkeGrfs[5].Stop
STRCrpalkeGrfs6AlarmAktiven | DIGITAL | IOD_STR_TCP | 268 | 00268 | CrpalkeGrfs[6].AlarmAktiven
STRCrpalkeGrfs6Deluje | DIGITAL | IOD_STR_TCP | 269 | 00269 | CrpalkeGrfs[6].Deluje
STRCrpalkeGrfs6LocalMode | DIGITAL | IOD_STR_TCP | 270 | 00270 | CrpalkeGrfs[6].LocalMode
STRCrpalkeGrfs6RemoteON | DIGITAL | IOD_STR_TCP | 271 | 00271 | CrpalkeGrfs[6].RemoteON
STRCrpalkeGrfs6Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 272 | 00272 | CrpalkeGrfs[6].Reset2handkWhValues
STRCrpalkeGrfs6ResetAlarm | DIGITAL | IOD_STR_TCP | 273 | 00273 | CrpalkeGrfs[6].ResetAlarm
STRCrpalkeGrfs6ResetAlarmLog | DIGITAL | IOD_STR_TCP | 274 | 00274 | CrpalkeGrfs[6].ResetAlarmLog
STRCrpalkeGrfs6ResetDevice | DIGITAL | IOD_STR_TCP | 275 | 00275 | CrpalkeGrfs[6].ResetDevice
STRCrpalkeGrfs6SetAutomatic | DIGITAL | IOD_STR_TCP | 276 | 00276 | CrpalkeGrfs[6].SetAutomatic
STRCrpalkeGrfs6SetConstFreqMode | DIGITAL | IOD_STR_TCP | 277 | 00277 | CrpalkeGrfs[6].SetConstFreqMode
STRCrpalkeGrfs6SetConstPress | DIGITAL | IOD_STR_TCP | 278 | 00278 | CrpalkeGrfs[6].SetConstPress
STRCrpalkeGrfs6SetLocalMode | DIGITAL | IOD_STR_TCP | 279 | 00279 | CrpalkeGrfs[6].SetLocalMode
STRCrpalkeGrfs6SetMaxRunMode | DIGITAL | IOD_STR_TCP | 280 | 00280 | CrpalkeGrfs[6].SetMaxRunMode
STRCrpalkeGrfs6SetMinRunMode | DIGITAL | IOD_STR_TCP | 281 | 00281 | CrpalkeGrfs[6].SetMinRunMode
STRCrpalkeGrfs6SetPropPress | DIGITAL | IOD_STR_TCP | 282 | 00282 | CrpalkeGrfs[6].SetPropPress
STRCrpalkeGrfs6SetReference | DIGITAL | IOD_STR_TCP | 283 | 00283 | CrpalkeGrfs[6].SetReference
STRCrpalkeGrfs6SetRemoteMode | DIGITAL | IOD_STR_TCP | 284 | 00284 | CrpalkeGrfs[6].SetRemoteMode
STRCrpalkeGrfs6SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 285 | 00285 | CrpalkeGrfs[6].SetTwinModeAlt
STRCrpalkeGrfs6SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 286 | 00286 | CrpalkeGrfs[6].SetTwinModeSpare
STRCrpalkeGrfs6SetTwinModeSync | DIGITAL | IOD_STR_TCP | 287 | 00287 | CrpalkeGrfs[6].SetTwinModeSync
STRCrpalkeGrfs6Start | DIGITAL | IOD_STR_TCP | 288 | 00288 | CrpalkeGrfs[6].Start
STRCrpalkeGrfs6Stop | DIGITAL | IOD_STR_TCP | 289 | 00289 | CrpalkeGrfs[6].Stop
STRCrpalkeGrfs7AlarmAktiven | DIGITAL | IOD_STR_TCP | 290 | 00290 | CrpalkeGrfs[7].AlarmAktiven
STRCrpalkeGrfs7Deluje | DIGITAL | IOD_STR_TCP | 291 | 00291 | CrpalkeGrfs[7].Deluje
STRCrpalkeGrfs7LocalMode | DIGITAL | IOD_STR_TCP | 292 | 00292 | CrpalkeGrfs[7].LocalMode
STRCrpalkeGrfs7RemoteON | DIGITAL | IOD_STR_TCP | 293 | 00293 | CrpalkeGrfs[7].RemoteON
STRCrpalkeGrfs7Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 294 | 00294 | CrpalkeGrfs[7].Reset2handkWhValues
STRCrpalkeGrfs7ResetAlarm | DIGITAL | IOD_STR_TCP | 295 | 00295 | CrpalkeGrfs[7].ResetAlarm
STRCrpalkeGrfs7ResetAlarmLog | DIGITAL | IOD_STR_TCP | 296 | 00296 | CrpalkeGrfs[7].ResetAlarmLog
STRCrpalkeGrfs7ResetDevice | DIGITAL | IOD_STR_TCP | 297 | 00297 | CrpalkeGrfs[7].ResetDevice
STRCrpalkeGrfs7SetAutomatic | DIGITAL | IOD_STR_TCP | 298 | 00298 | CrpalkeGrfs[7].SetAutomatic
STRCrpalkeGrfs7SetConstFreqMode | DIGITAL | IOD_STR_TCP | 299 | 00299 | CrpalkeGrfs[7].SetConstFreqMode
STRCrpalkeGrfs7SetConstPress | DIGITAL | IOD_STR_TCP | 300 | 00300 | CrpalkeGrfs[7].SetConstPress
STRCrpalkeGrfs7SetLocalMode | DIGITAL | IOD_STR_TCP | 301 | 00301 | CrpalkeGrfs[7].SetLocalMode
STRCrpalkeGrfs7SetMaxRunMode | DIGITAL | IOD_STR_TCP | 302 | 00302 | CrpalkeGrfs[7].SetMaxRunMode
STRCrpalkeGrfs7SetMinRunMode | DIGITAL | IOD_STR_TCP | 303 | 00303 | CrpalkeGrfs[7].SetMinRunMode
STRCrpalkeGrfs7SetPropPress | DIGITAL | IOD_STR_TCP | 304 | 00304 | CrpalkeGrfs[7].SetPropPress
STRCrpalkeGrfs7SetReference | DIGITAL | IOD_STR_TCP | 305 | 00305 | CrpalkeGrfs[7].SetReference
STRCrpalkeGrfs7SetRemoteMode | DIGITAL | IOD_STR_TCP | 306 | 00306 | CrpalkeGrfs[7].SetRemoteMode
STRCrpalkeGrfs7SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 307 | 00307 | CrpalkeGrfs[7].SetTwinModeAlt
STRCrpalkeGrfs7SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 308 | 00308 | CrpalkeGrfs[7].SetTwinModeSpare
STRCrpalkeGrfs7SetTwinModeSync | DIGITAL | IOD_STR_TCP | 309 | 00309 | CrpalkeGrfs[7].SetTwinModeSync
STRCrpalkeGrfs7Start | DIGITAL | IOD_STR_TCP | 310 | 00310 | CrpalkeGrfs[7].Start
STRCrpalkeGrfs7Stop | DIGITAL | IOD_STR_TCP | 311 | 00311 | CrpalkeGrfs[7].Stop
STRCrpalkeGrfs8AlarmAktiven | DIGITAL | IOD_STR_TCP | 312 | 00312 | CrpalkeGrfs[8].AlarmAktiven
STRCrpalkeGrfs8Deluje | DIGITAL | IOD_STR_TCP | 313 | 00313 | CrpalkeGrfs[8].Deluje
STRCrpalkeGrfs8LocalMode | DIGITAL | IOD_STR_TCP | 314 | 00314 | CrpalkeGrfs[8].LocalMode
STRCrpalkeGrfs8RemoteON | DIGITAL | IOD_STR_TCP | 315 | 00315 | CrpalkeGrfs[8].RemoteON
STRCrpalkeGrfs8Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 316 | 00316 | CrpalkeGrfs[8].Reset2handkWhValues
STRCrpalkeGrfs8ResetAlarm | DIGITAL | IOD_STR_TCP | 317 | 00317 | CrpalkeGrfs[8].ResetAlarm
STRCrpalkeGrfs8ResetAlarmLog | DIGITAL | IOD_STR_TCP | 318 | 00318 | CrpalkeGrfs[8].ResetAlarmLog
STRCrpalkeGrfs8ResetDevice | DIGITAL | IOD_STR_TCP | 319 | 00319 | CrpalkeGrfs[8].ResetDevice
STRCrpalkeGrfs8SetAutomatic | DIGITAL | IOD_STR_TCP | 320 | 00320 | CrpalkeGrfs[8].SetAutomatic
STRCrpalkeGrfs8SetConstFreqMode | DIGITAL | IOD_STR_TCP | 321 | 00321 | CrpalkeGrfs[8].SetConstFreqMode
STRCrpalkeGrfs8SetConstPress | DIGITAL | IOD_STR_TCP | 322 | 00322 | CrpalkeGrfs[8].SetConstPress
STRCrpalkeGrfs8SetLocalMode | DIGITAL | IOD_STR_TCP | 323 | 00323 | CrpalkeGrfs[8].SetLocalMode
STRCrpalkeGrfs8SetMaxRunMode | DIGITAL | IOD_STR_TCP | 324 | 00324 | CrpalkeGrfs[8].SetMaxRunMode
STRCrpalkeGrfs8SetMinRunMode | DIGITAL | IOD_STR_TCP | 325 | 00325 | CrpalkeGrfs[8].SetMinRunMode
STRCrpalkeGrfs8SetPropPress | DIGITAL | IOD_STR_TCP | 326 | 00326 | CrpalkeGrfs[8].SetPropPress
STRCrpalkeGrfs8SetReference | DIGITAL | IOD_STR_TCP | 327 | 00327 | CrpalkeGrfs[8].SetReference
STRCrpalkeGrfs8SetRemoteMode | DIGITAL | IOD_STR_TCP | 328 | 00328 | CrpalkeGrfs[8].SetRemoteMode
STRCrpalkeGrfs8SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 329 | 00329 | CrpalkeGrfs[8].SetTwinModeAlt
STRCrpalkeGrfs8SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 330 | 00330 | CrpalkeGrfs[8].SetTwinModeSpare
STRCrpalkeGrfs8SetTwinModeSync | DIGITAL | IOD_STR_TCP | 331 | 00331 | CrpalkeGrfs[8].SetTwinModeSync
STRCrpalkeGrfs8Start | DIGITAL | IOD_STR_TCP | 332 | 00332 | CrpalkeGrfs[8].Start
STRCrpalkeGrfs8Stop | DIGITAL | IOD_STR_TCP | 333 | 00333 | CrpalkeGrfs[8].Stop
STRCrpalkeGrfs9AlarmAktiven | DIGITAL | IOD_STR_TCP | 334 | 00334 | CrpalkeGrfs[9].AlarmAktiven
STRCrpalkeGrfs9Deluje | DIGITAL | IOD_STR_TCP | 335 | 00335 | CrpalkeGrfs[9].Deluje
STRCrpalkeGrfs9LocalMode | DIGITAL | IOD_STR_TCP | 336 | 00336 | CrpalkeGrfs[9].LocalMode
STRCrpalkeGrfs9RemoteON | DIGITAL | IOD_STR_TCP | 337 | 00337 | CrpalkeGrfs[9].RemoteON
STRCrpalkeGrfs9Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 338 | 00338 | CrpalkeGrfs[9].Reset2handkWhValues
STRCrpalkeGrfs9ResetAlarm | DIGITAL | IOD_STR_TCP | 339 | 00339 | CrpalkeGrfs[9].ResetAlarm
STRCrpalkeGrfs9ResetAlarmLog | DIGITAL | IOD_STR_TCP | 340 | 00340 | CrpalkeGrfs[9].ResetAlarmLog
STRCrpalkeGrfs9ResetDevice | DIGITAL | IOD_STR_TCP | 341 | 00341 | CrpalkeGrfs[9].ResetDevice
STRCrpalkeGrfs9SetAutomatic | DIGITAL | IOD_STR_TCP | 342 | 00342 | CrpalkeGrfs[9].SetAutomatic
STRCrpalkeGrfs9SetConstFreqMode | DIGITAL | IOD_STR_TCP | 343 | 00343 | CrpalkeGrfs[9].SetConstFreqMode
STRCrpalkeGrfs9SetConstPress | DIGITAL | IOD_STR_TCP | 344 | 00344 | CrpalkeGrfs[9].SetConstPress
STRCrpalkeGrfs9SetLocalMode | DIGITAL | IOD_STR_TCP | 345 | 00345 | CrpalkeGrfs[9].SetLocalMode
STRCrpalkeGrfs9SetMaxRunMode | DIGITAL | IOD_STR_TCP | 346 | 00346 | CrpalkeGrfs[9].SetMaxRunMode
STRCrpalkeGrfs9SetMinRunMode | DIGITAL | IOD_STR_TCP | 347 | 00347 | CrpalkeGrfs[9].SetMinRunMode
STRCrpalkeGrfs9SetPropPress | DIGITAL | IOD_STR_TCP | 348 | 00348 | CrpalkeGrfs[9].SetPropPress
STRCrpalkeGrfs9SetReference | DIGITAL | IOD_STR_TCP | 349 | 00349 | CrpalkeGrfs[9].SetReference
STRCrpalkeGrfs9SetRemoteMode | DIGITAL | IOD_STR_TCP | 350 | 00350 | CrpalkeGrfs[9].SetRemoteMode
STRCrpalkeGrfs9SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 351 | 00351 | CrpalkeGrfs[9].SetTwinModeAlt
STRCrpalkeGrfs9SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 352 | 00352 | CrpalkeGrfs[9].SetTwinModeSpare
STRCrpalkeGrfs9SetTwinModeSync | DIGITAL | IOD_STR_TCP | 353 | 00353 | CrpalkeGrfs[9].SetTwinModeSync
STRCrpalkeGrfs9Start | DIGITAL | IOD_STR_TCP | 354 | 00354 | CrpalkeGrfs[9].Start
STRCrpalkeGrfs9Stop | DIGITAL | IOD_STR_TCP | 355 | 00355 | CrpalkeGrfs[9].Stop
STRCrpDanfossGenError1 | DIGITAL | IOD_STR_TCP | 356 | 00356 | CrpDanfossGenError[1]
STRCrpDanfossGenError2 | DIGITAL | IOD_STR_TCP | 357 | 00357 | CrpDanfossGenError[2]
STRCrpDanfossGenError3 | DIGITAL | IOD_STR_TCP | 358 | 00358 | CrpDanfossGenError[3]
STRCrpDanfossGenError4 | DIGITAL | IOD_STR_TCP | 359 | 00359 | CrpDanfossGenError[4]
STRCrpDanfossNaCas1 | DIGITAL | IOD_STR_TCP | 360 | 00360 | CrpDanfossNaCas[1]
STRCrpDanfossNaCas2 | DIGITAL | IOD_STR_TCP | 361 | 00361 | CrpDanfossNaCas[2]
STRCrpDanfossON1 | DIGITAL | IOD_STR_TCP | 362 | 00362 | CrpDanfossON[1]
STRCrpDanfossON2 | DIGITAL | IOD_STR_TCP | 363 | 00363 | CrpDanfossON[2]
STRCrpDanfossON3 | DIGITAL | IOD_STR_TCP | 364 | 00364 | CrpDanfossON[3]
STRCrpDanfossON4 | DIGITAL | IOD_STR_TCP | 365 | 00365 | CrpDanfossON[4]
STRCrpDanfossStatusError1 | DIGITAL | IOD_STR_TCP | 366 | 00366 | CrpDanfossStatusError[1]
STRCrpDanfossStatusError2 | DIGITAL | IOD_STR_TCP | 367 | 00367 | CrpDanfossStatusError[2]
STRCrpDanfossStatusError3 | DIGITAL | IOD_STR_TCP | 368 | 00368 | CrpDanfossStatusError[3]
STRCrpDanfossStatusError4 | DIGITAL | IOD_STR_TCP | 369 | 00369 | CrpDanfossStatusError[4]
STRCrpGrundfosGenError10 | DIGITAL | IOD_STR_TCP | 370 | 00370 | CrpGrundfosGenError[10]
STRCrpGrundfosGenError11 | DIGITAL | IOD_STR_TCP | 371 | 00371 | CrpGrundfosGenError[11]
STRCrpGrundfosGenError12 | DIGITAL | IOD_STR_TCP | 372 | 00372 | CrpGrundfosGenError[12]
STRCrpGrundfosGenError13 | DIGITAL | IOD_STR_TCP | 373 | 00373 | CrpGrundfosGenError[13]
STRCrpGrundfosGenError14 | DIGITAL | IOD_STR_TCP | 374 | 00374 | CrpGrundfosGenError[14]
STRCrpGrundfosGenError1 | DIGITAL | IOD_STR_TCP | 375 | 00375 | CrpGrundfosGenError[1]
STRCrpGrundfosGenError2 | DIGITAL | IOD_STR_TCP | 376 | 00376 | CrpGrundfosGenError[2]
STRCrpGrundfosGenError3 | DIGITAL | IOD_STR_TCP | 377 | 00377 | CrpGrundfosGenError[3]
STRCrpGrundfosGenError4 | DIGITAL | IOD_STR_TCP | 378 | 00378 | CrpGrundfosGenError[4]
STRCrpGrundfosGenError5 | DIGITAL | IOD_STR_TCP | 379 | 00379 | CrpGrundfosGenError[5]
STRCrpGrundfosGenError6 | DIGITAL | IOD_STR_TCP | 380 | 00380 | CrpGrundfosGenError[6]
STRCrpGrundfosGenError7 | DIGITAL | IOD_STR_TCP | 381 | 00381 | CrpGrundfosGenError[7]
STRCrpGrundfosGenError8 | DIGITAL | IOD_STR_TCP | 382 | 00382 | CrpGrundfosGenError[8]
STRCrpGrundfosGenError9 | DIGITAL | IOD_STR_TCP | 383 | 00383 | CrpGrundfosGenError[9]
STRCrpGrundfosNaCas1 | DIGITAL | IOD_STR_TCP | 384 | 00384 | CrpGrundfosNaCas[1]
STRCrpGrundfosNaCas2 | DIGITAL | IOD_STR_TCP | 385 | 00385 | CrpGrundfosNaCas[2]
STRCrpGrundfosNaCas3 | DIGITAL | IOD_STR_TCP | 386 | 00386 | CrpGrundfosNaCas[3]
STRCrpGrundfosNaCas4 | DIGITAL | IOD_STR_TCP | 387 | 00387 | CrpGrundfosNaCas[4]
STRCrpGrundfosNaCas5 | DIGITAL | IOD_STR_TCP | 388 | 00388 | CrpGrundfosNaCas[5]
STRCrpGrundfosNaCas6 | DIGITAL | IOD_STR_TCP | 389 | 00389 | CrpGrundfosNaCas[6]
STRCrpGrundfosNaCas7 | DIGITAL | IOD_STR_TCP | 390 | 00390 | CrpGrundfosNaCas[7]
STRCrpGrundfosNaTlak1 | DIGITAL | IOD_STR_TCP | 391 | 00391 | CrpGrundfosNaTlak[1]
STRCrpGrundfosNaTlak2 | DIGITAL | IOD_STR_TCP | 392 | 00392 | CrpGrundfosNaTlak[2]
STRCrpGrundfosNaTlak3 | DIGITAL | IOD_STR_TCP | 393 | 00393 | CrpGrundfosNaTlak[3]
STRCrpGrundfosNaTlak4 | DIGITAL | IOD_STR_TCP | 394 | 00394 | CrpGrundfosNaTlak[4]
STRCrpGrundfosNaTlak5 | DIGITAL | IOD_STR_TCP | 395 | 00395 | CrpGrundfosNaTlak[5]
STRCrpGrundfosNaTlak6 | DIGITAL | IOD_STR_TCP | 396 | 00396 | CrpGrundfosNaTlak[6]
STRCrpGrundfosNaTlak7 | DIGITAL | IOD_STR_TCP | 397 | 00397 | CrpGrundfosNaTlak[7]
STRCrpGrundfosON10 | DIGITAL | IOD_STR_TCP | 398 | 00398 | CrpGrundfosON[10]
STRCrpGrundfosON11 | DIGITAL | IOD_STR_TCP | 399 | 00399 | CrpGrundfosON[11]
STRCrpGrundfosON12 | DIGITAL | IOD_STR_TCP | 400 | 00400 | CrpGrundfosON[12]
STRCrpGrundfosON13 | DIGITAL | IOD_STR_TCP | 401 | 00401 | CrpGrundfosON[13]
STRCrpGrundfosON14 | DIGITAL | IOD_STR_TCP | 402 | 00402 | CrpGrundfosON[14]
STRCrpGrundfosON1 | DIGITAL | IOD_STR_TCP | 403 | 00403 | CrpGrundfosON[1]
STRCrpGrundfosON2 | DIGITAL | IOD_STR_TCP | 404 | 00404 | CrpGrundfosON[2]
STRCrpGrundfosON3 | DIGITAL | IOD_STR_TCP | 405 | 00405 | CrpGrundfosON[3]
STRCrpGrundfosON4 | DIGITAL | IOD_STR_TCP | 406 | 00406 | CrpGrundfosON[4]
STRCrpGrundfosON5 | DIGITAL | IOD_STR_TCP | 407 | 00407 | CrpGrundfosON[5]
STRCrpGrundfosON6 | DIGITAL | IOD_STR_TCP | 408 | 00408 | CrpGrundfosON[6]
STRCrpGrundfosON7 | DIGITAL | IOD_STR_TCP | 409 | 00409 | CrpGrundfosON[7]
STRCrpGrundfosON8 | DIGITAL | IOD_STR_TCP | 410 | 00410 | CrpGrundfosON[8]
STRCrpGrundfosON9 | DIGITAL | IOD_STR_TCP | 411 | 00411 | CrpGrundfosON[9]
STRCrpGrundfosStatusError10 | DIGITAL | IOD_STR_TCP | 412 | 00412 | CrpGrundfosStatusError[10]
STRCrpGrundfosStatusError11 | DIGITAL | IOD_STR_TCP | 413 | 00413 | CrpGrundfosStatusError[11]
STRCrpGrundfosStatusError12 | DIGITAL | IOD_STR_TCP | 414 | 00414 | CrpGrundfosStatusError[12]
STRCrpGrundfosStatusError13 | DIGITAL | IOD_STR_TCP | 415 | 00415 | CrpGrundfosStatusError[13]
STRCrpGrundfosStatusError14 | DIGITAL | IOD_STR_TCP | 416 | 00416 | CrpGrundfosStatusError[14]
STRCrpGrundfosStatusError1 | DIGITAL | IOD_STR_TCP | 417 | 00417 | CrpGrundfosStatusError[1]
STRCrpGrundfosStatusError2 | DIGITAL | IOD_STR_TCP | 418 | 00418 | CrpGrundfosStatusError[2]
STRCrpGrundfosStatusError3 | DIGITAL | IOD_STR_TCP | 419 | 00419 | CrpGrundfosStatusError[3]
STRCrpGrundfosStatusError4 | DIGITAL | IOD_STR_TCP | 420 | 00420 | CrpGrundfosStatusError[4]
STRCrpGrundfosStatusError5 | DIGITAL | IOD_STR_TCP | 421 | 00421 | CrpGrundfosStatusError[5]
STRCrpGrundfosStatusError6 | DIGITAL | IOD_STR_TCP | 422 | 00422 | CrpGrundfosStatusError[6]
STRCrpGrundfosStatusError7 | DIGITAL | IOD_STR_TCP | 423 | 00423 | CrpGrundfosStatusError[7]
STRCrpGrundfosStatusError8 | DIGITAL | IOD_STR_TCP | 424 | 00424 | CrpGrundfosStatusError[8]
STRCrpGrundfosStatusError9 | DIGITAL | IOD_STR_TCP | 425 | 00425 | CrpGrundfosStatusError[9]
STRDanfossHMKontOnOff1 | DIGITAL | IOD_STR_TCP | 426 | 00426 | DanfossHMKontOnOff[1]
STRDanfossHMKontOnOff2 | DIGITAL | IOD_STR_TCP | 427 | 00427 | DanfossHMKontOnOff[2]
STRDanfossHMKontOnOff3 | DIGITAL | IOD_STR_TCP | 428 | 00428 | DanfossHMKontOnOff[3]
STRDanfossHMKontOnOff4 | DIGITAL | IOD_STR_TCP | 429 | 00429 | DanfossHMKontOnOff[4]
STRDI_230VAC_OK | DIGITAL | IOD_STR_TCP | 430 | 00430 | DI_230VAC_OK
STRDI_24VAC_OK | DIGITAL | IOD_STR_TCP | 431 | 00431 | DI_24VAC_OK
STRDI_24VDC_OK | DIGITAL | IOD_STR_TCP | 432 | 00432 | DI_24VDC_OK
STRDI_AkumTopVodeAUTO | DIGITAL | IOD_STR_TCP | 433 | 00433 | DI_AkumTopVodeAUTO
STRDI_AkumTopVodeKontON | DIGITAL | IOD_STR_TCP | 434 | 00434 | DI_AkumTopVodeKontON
STRDI_CrpHM1AUTO | DIGITAL | IOD_STR_TCP | 435 | 00435 | DI_CrpHM1AUTO
STRDI_CrpHM1endOFFtoON | DIGITAL | IOD_STR_TCP | 436 | 00436 | DI_CrpHM1endOFFtoON
STRDI_CrpHM1ERR | DIGITAL | IOD_STR_TCP | 437 | 00437 | DI_CrpHM1ERR
STRDI_CrpHM1kontON | DIGITAL | IOD_STR_TCP | 438 | 00438 | DI_CrpHM1kontON
STRDI_CrpHM2AUTO | DIGITAL | IOD_STR_TCP | 439 | 00439 | DI_CrpHM2AUTO
STRDI_CrpHM2endOFFtoON | DIGITAL | IOD_STR_TCP | 440 | 00440 | DI_CrpHM2endOFFtoON
STRDI_CrpHM2ERR | DIGITAL | IOD_STR_TCP | 441 | 00441 | DI_CrpHM2ERR
STRDI_CrpHM2kontON | DIGITAL | IOD_STR_TCP | 442 | 00442 | DI_CrpHM2kontON
STRDI_CrpHM3AUTO | DIGITAL | IOD_STR_TCP | 443 | 00443 | DI_CrpHM3AUTO
STRDI_CrpHM3endOFFtoON | DIGITAL | IOD_STR_TCP | 444 | 00444 | DI_CrpHM3endOFFtoON
STRDI_CrpHM3ERR | DIGITAL | IOD_STR_TCP | 445 | 00445 | DI_CrpHM3ERR
STRDI_CrpHM3kontON | DIGITAL | IOD_STR_TCP | 446 | 00446 | DI_CrpHM3kontON
STRDI_CrpHM4AUTO | DIGITAL | IOD_STR_TCP | 447 | 00447 | DI_CrpHM4AUTO
STRDI_CrpHM4endOFFtoON | DIGITAL | IOD_STR_TCP | 448 | 00448 | DI_CrpHM4endOFFtoON
STRDI_CrpHM4ERR | DIGITAL | IOD_STR_TCP | 449 | 00449 | DI_CrpHM4ERR
STRDI_CrpHM4kontON | DIGITAL | IOD_STR_TCP | 450 | 00450 | DI_CrpHM4kontON
STRDI_CrpHM5AUTO | DIGITAL | IOD_STR_TCP | 451 | 00451 | DI_CrpHM5AUTO
STRDI_CrpHM6AUTO | DIGITAL | IOD_STR_TCP | 452 | 00452 | DI_CrpHM6AUTO
STRDI_CrpHM7AUTO | DIGITAL | IOD_STR_TCP | 453 | 00453 | DI_CrpHM7AUTO
STRDI_CrpHM8AUTO | DIGITAL | IOD_STR_TCP | 454 | 00454 | DI_CrpHM8AUTO
STRDI_CrpMN1AUTO | DIGITAL | IOD_STR_TCP | 455 | 00455 | DI_CrpMN1AUTO
STRDI_CrpMN1kontON | DIGITAL | IOD_STR_TCP | 456 | 00456 | DI_CrpMN1kontON
STRDI_CrpTM10AUTO | DIGITAL | IOD_STR_TCP | 457 | 00457 | DI_CrpTM10AUTO
STRDI_CrpTM11TM12AUTO | DIGITAL | IOD_STR_TCP | 458 | 00458 | DI_CrpTM11TM12AUTO
STRDI_CrpTM11TM12kontON | DIGITAL | IOD_STR_TCP | 459 | 00459 | DI_CrpTM11TM12kontON
STRDI_CrpTM1AUTO | DIGITAL | IOD_STR_TCP | 460 | 00460 | DI_CrpTM1AUTO
STRDI_CrpTM2AUTO | DIGITAL | IOD_STR_TCP | 461 | 00461 | DI_CrpTM2AUTO
STRDI_CrpTM3AUTO | DIGITAL | IOD_STR_TCP | 462 | 00462 | DI_CrpTM3AUTO
STRDI_CrpTM4AUTO | DIGITAL | IOD_STR_TCP | 463 | 00463 | DI_CrpTM4AUTO
STRDI_CrpTM5AUTO | DIGITAL | IOD_STR_TCP | 464 | 00464 | DI_CrpTM5AUTO
STRDI_CrpTM6AUTO | DIGITAL | IOD_STR_TCP | 465 | 00465 | DI_CrpTM6AUTO
STRDI_CrpTM7AUTO | DIGITAL | IOD_STR_TCP | 466 | 00466 | DI_CrpTM7AUTO
STRDI_CrpTM8AUTO | DIGITAL | IOD_STR_TCP | 467 | 00467 | DI_CrpTM8AUTO
STRDI_CrpTM9AUTO | DIGITAL | IOD_STR_TCP | 468 | 00468 | DI_CrpTM9AUTO
STRDI_GlStikaloDieselON | DIGITAL | IOD_STR_TCP | 469 | 00469 | DI_GlStikaloDieselON
STRDI_GlStikaloMrezaON | DIGITAL | IOD_STR_TCP | 470 | 00470 | DI_GlStikaloMrezaON
STRDI_GlStikaloUpsON | DIGITAL | IOD_STR_TCP | 471 | 00471 | DI_GlStikaloUpsON
STRDI_HladStAUTO | DIGITAL | IOD_STR_TCP | 472 | 00472 | DI_HladStAUTO
STRDI_HladStCrpHladH2OON | DIGITAL | IOD_STR_TCP | 473 | 00473 | DI_HladStCrpHladH2OON
STRDI_HladStERR | DIGITAL | IOD_STR_TCP | 474 | 00474 | DI_HladStERR
STRDI_Klima1ERR | DIGITAL | IOD_STR_TCP | 475 | 00475 | DI_Klima1ERR
STRDI_Klima1filterZAM | DIGITAL | IOD_STR_TCP | 476 | 00476 | DI_Klima1filterZAM
STRDI_Klima1FIRE | DIGITAL | IOD_STR_TCP | 477 | 00477 | DI_Klima1FIRE
STRDI_Klima1OFFtoON | DIGITAL | IOD_STR_TCP | 478 | 00478 | DI_Klima1OFFtoON
STRDI_Klima1ON | DIGITAL | IOD_STR_TCP | 479 | 00479 | DI_Klima1ON
STRDI_Klima1zascStON | DIGITAL | IOD_STR_TCP | 480 | 00480 | DI_Klima1zascStON
STRDI_Klima2ERR | DIGITAL | IOD_STR_TCP | 481 | 00481 | DI_Klima2ERR
STRDI_Klima2filterZAM | DIGITAL | IOD_STR_TCP | 482 | 00482 | DI_Klima2filterZAM
STRDI_Klima2FIRE | DIGITAL | IOD_STR_TCP | 483 | 00483 | DI_Klima2FIRE
STRDI_Klima2OFFtoON | DIGITAL | IOD_STR_TCP | 484 | 00484 | DI_Klima2OFFtoON
STRDI_Klima2ON | DIGITAL | IOD_STR_TCP | 485 | 00485 | DI_Klima2ON
STRDI_Klima2zascStON | DIGITAL | IOD_STR_TCP | 486 | 00486 | DI_Klima2zascStON
STRDI_Komp1ERR | DIGITAL | IOD_STR_TCP | 487 | 00487 | DI_Komp1ERR
STRDI_Komp1ON | DIGITAL | IOD_STR_TCP | 488 | 00488 | DI_Komp1ON
STRDI_Komp2ERR | DIGITAL | IOD_STR_TCP | 489 | 00489 | DI_Komp2ERR
STRDI_Komp2ON | DIGITAL | IOD_STR_TCP | 490 | 00490 | DI_Komp2ON
STRDI_Kond1AUTO | DIGITAL | IOD_STR_TCP | 491 | 00491 | DI_Kond1AUTO
STRDI_Kond1FS1FS2 | DIGITAL | IOD_STR_TCP | 492 | 00492 | DI_Kond1FS1FS2
STRDI_Kond1ON | DIGITAL | IOD_STR_TCP | 493 | 00493 | DI_Kond1ON
STRDI_Kond1zascStON | DIGITAL | IOD_STR_TCP | 494 | 00494 | DI_Kond1zascStON
STRDI_Kond2AUTO | DIGITAL | IOD_STR_TCP | 495 | 00495 | DI_Kond2AUTO
STRDI_Kond2FS1FS2 | DIGITAL | IOD_STR_TCP | 496 | 00496 | DI_Kond2FS1FS2
STRDI_Kond2ON | DIGITAL | IOD_STR_TCP | 497 | 00497 | DI_Kond2ON
STRDI_Kond2zascStON | DIGITAL | IOD_STR_TCP | 498 | 00498 | DI_Kond2zascStON
STRDI_Kond3AUTO | DIGITAL | IOD_STR_TCP | 499 | 00499 | DI_Kond3AUTO
STRDI_Kond3FS1FS2 | DIGITAL | IOD_STR_TCP | 500 | 00500 | DI_Kond3FS1FS2
STRDI_Kond3ON | DIGITAL | IOD_STR_TCP | 501 | 00501 | DI_Kond3ON
STRDI_Kond3zascStON | DIGITAL | IOD_STR_TCP | 502 | 00502 | DI_Kond3zascStON
STRDI_Lop1PL1Odprta | DIGITAL | IOD_STR_TCP | 503 | 00503 | DI_Lop1PL1Odprta
STRDI_Lop1PL1Zaprta | DIGITAL | IOD_STR_TCP | 504 | 00504 | DI_Lop1PL1Zaprta
STRDI_Lop1PL2Odprta | DIGITAL | IOD_STR_TCP | 505 | 00505 | DI_Lop1PL2Odprta
STRDI_Lop1PL2Zaprta | DIGITAL | IOD_STR_TCP | 506 | 00506 | DI_Lop1PL2Zaprta
STRDI_Lop1PL3Odprta | DIGITAL | IOD_STR_TCP | 507 | 00507 | DI_Lop1PL3Odprta
STRDI_Lop1PL3Zaprta | DIGITAL | IOD_STR_TCP | 508 | 00508 | DI_Lop1PL3Zaprta
STRDI_Lop3Y1Odprta | DIGITAL | IOD_STR_TCP | 509 | 00509 | DI_Lop3Y1Odprta
STRDI_Lop3Y1Zaprta | DIGITAL | IOD_STR_TCP | 510 | 00510 | DI_Lop3Y1Zaprta
STRDI_Lop4Y1Odprta | DIGITAL | IOD_STR_TCP | 511 | 00511 | DI_Lop4Y1Odprta
STRDI_Lop4Y1Zaprta | DIGITAL | IOD_STR_TCP | 512 | 00512 | DI_Lop4Y1Zaprta
STRDI_PotrditevAlarmov | DIGITAL | IOD_STR_TCP | 513 | 00513 | DI_PotrditevAlarmov
STRDI_RazlitjeVodeEXP1 | DIGITAL | IOD_STR_TCP | 514 | 00514 | DI_RazlitjeVodeEXP1
STRDI_RazlitjeVodeEXP2 | DIGITAL | IOD_STR_TCP | 515 | 00515 | DI_RazlitjeVodeEXP2
STRDI_RazlitjeVodeHP | DIGITAL | IOD_STR_TCP | 516 | 00516 | DI_RazlitjeVodeHP
STRDI_RazlitjeVodeK1 | DIGITAL | IOD_STR_TCP | 517 | 00517 | DI_RazlitjeVodeK1
STRDI_RazlitjeVodeK2 | DIGITAL | IOD_STR_TCP | 518 | 00518 | DI_RazlitjeVodeK2
STRDI_RazlitjeVodeTP | DIGITAL | IOD_STR_TCP | 519 | 00519 | DI_RazlitjeVodeTP
STRDI_ToplPostGenErr | DIGITAL | IOD_STR_TCP | 520 | 00520 | DI_ToplPostGenErr
STRDI_UPS_Alarm | DIGITAL | IOD_STR_TCP | 521 | 00521 | DI_UPS_Alarm
STRDI_UPS_BatNacin | DIGITAL | IOD_STR_TCP | 522 | 00522 | DI_UPS_BatNacin
STRDI_UPS_Polnjenje | DIGITAL | IOD_STR_TCP | 523 | 00523 | DI_UPS_Polnjenje
STRDI_Vent1Auto | DIGITAL | IOD_STR_TCP | 524 | 00524 | DI_Vent1Auto
STRDI_Vent1kontON | DIGITAL | IOD_STR_TCP | 525 | 00525 | DI_Vent1kontON
STRDI_Vent2Auto | DIGITAL | IOD_STR_TCP | 526 | 00526 | DI_Vent2Auto
STRDI_Vent2kontON | DIGITAL | IOD_STR_TCP | 527 | 00527 | DI_Vent2kontON
STRDI_Vent3Auto | DIGITAL | IOD_STR_TCP | 528 | 00528 | DI_Vent3Auto
STRDI_Vent3kontON | DIGITAL | IOD_STR_TCP | 529 | 00529 | DI_Vent3kontON
STRDI_Vent4Auto | DIGITAL | IOD_STR_TCP | 530 | 00530 | DI_Vent4Auto
STRDI_Vent4kontON | DIGITAL | IOD_STR_TCP | 531 | 00531 | DI_Vent4kontON
STRDI_Vent5Auto | DIGITAL | IOD_STR_TCP | 532 | 00532 | DI_Vent5Auto
STRDI_Vent5kontON | DIGITAL | IOD_STR_TCP | 533 | 00533 | DI_Vent5kontON
STRDI_Vent6Auto | DIGITAL | IOD_STR_TCP | 534 | 00534 | DI_Vent6Auto
STRDI_Vent6kontON | DIGITAL | IOD_STR_TCP | 535 | 00535 | DI_Vent6kontON
STRDI_Vlaz1ERR | DIGITAL | IOD_STR_TCP | 536 | 00536 | DI_Vlaz1ERR
STRDI_Vlaz1ON | DIGITAL | IOD_STR_TCP | 537 | 00537 | DI_Vlaz1ON
STRDI_Vlaz2ERR | DIGITAL | IOD_STR_TCP | 538 | 00538 | DI_Vlaz2ERR
STRDI_Vlaz2ON | DIGITAL | IOD_STR_TCP | 539 | 00539 | DI_Vlaz2ON
STRDIN_230VAC_OK | DIGITAL | IOD_STR_TCP | 540 | 00540 | DIN_230VAC_OK
STRDIN_24VAC_OK | DIGITAL | IOD_STR_TCP | 541 | 00541 | DIN_24VAC_OK
STRDIN_24VDC_OK | DIGITAL | IOD_STR_TCP | 542 | 00542 | DIN_24VDC_OK
STRDIN_CrpHM1ERR | DIGITAL | IOD_STR_TCP | 543 | 00543 | DIN_CrpHM1ERR
STRDIN_CrpHM2ERR | DIGITAL | IOD_STR_TCP | 544 | 00544 | DIN_CrpHM2ERR
STRDIN_CrpHM3ERR | DIGITAL | IOD_STR_TCP | 545 | 00545 | DIN_CrpHM3ERR
STRDIN_CrpHM4ERR | DIGITAL | IOD_STR_TCP | 546 | 00546 | DIN_CrpHM4ERR
STRDIN_HladStERR | DIGITAL | IOD_STR_TCP | 547 | 00547 | DIN_HladStERR
STRDIN_Klima1ERR | DIGITAL | IOD_STR_TCP | 548 | 00548 | DIN_Klima1ERR
STRDIN_Klima1filterZAM | DIGITAL | IOD_STR_TCP | 549 | 00549 | DIN_Klima1filterZAM
STRDIN_Klima1zascStON | DIGITAL | IOD_STR_TCP | 550 | 00550 | DIN_Klima1zascStON
STRDIN_Klima2ERR | DIGITAL | IOD_STR_TCP | 551 | 00551 | DIN_Klima2ERR
STRDIN_Klima2filterZAM | DIGITAL | IOD_STR_TCP | 552 | 00552 | DIN_Klima2filterZAM
STRDIN_Klima2zascStON | DIGITAL | IOD_STR_TCP | 553 | 00553 | DIN_Klima2zascStON
STRDIN_Komp1ERR | DIGITAL | IOD_STR_TCP | 554 | 00554 | DIN_Komp1ERR
STRDIN_Komp1ON | DIGITAL | IOD_STR_TCP | 555 | 00555 | DIN_Komp1ON
STRDIN_Komp2ERR | DIGITAL | IOD_STR_TCP | 556 | 00556 | DIN_Komp2ERR
STRDIN_Komp2ON | DIGITAL | IOD_STR_TCP | 557 | 00557 | DIN_Komp2ON
STRDIN_Kond1zascStON | DIGITAL | IOD_STR_TCP | 558 | 00558 | DIN_Kond1zascStON
STRDIN_Kond2zascStON | DIGITAL | IOD_STR_TCP | 559 | 00559 | DIN_Kond2zascStON
STRDIN_Kond3zascStON | DIGITAL | IOD_STR_TCP | 560 | 00560 | DIN_Kond3zascStON
STRDIN_Vlaz1ERR | DIGITAL | IOD_STR_TCP | 561 | 00561 | DIN_Vlaz1ERR
STRDIN_Vlaz2ERR | DIGITAL | IOD_STR_TCP | 562 | 00562 | DIN_Vlaz2ERR
STRDO_BojlerTE1Vklop | DIGITAL | IOD_STR_TCP | 563 | 00563 | DO_BojlerTE1Vklop
STRDO_CrpHM1Vklop | DIGITAL | IOD_STR_TCP | 564 | 00564 | DO_CrpHM1Vklop
STRDO_CrpHM2Vklop | DIGITAL | IOD_STR_TCP | 565 | 00565 | DO_CrpHM2Vklop
STRDO_CrpHM3Vklop | DIGITAL | IOD_STR_TCP | 566 | 00566 | DO_CrpHM3Vklop
STRDO_CrpHM4Vklop | DIGITAL | IOD_STR_TCP | 567 | 00567 | DO_CrpHM4Vklop
STRDO_CrpMN1Vklop | DIGITAL | IOD_STR_TCP | 568 | 00568 | DO_CrpMN1Vklop
STRDO_CrpTM11Vklop | DIGITAL | IOD_STR_TCP | 569 | 00569 | DO_CrpTM11Vklop
STRDO_GrundfosVklopL | DIGITAL | IOD_STR_TCP | 570 | 00570 | DO_GrundfosVklopL
STRDO_GrundfosVklopN | DIGITAL | IOD_STR_TCP | 571 | 00571 | DO_GrundfosVklopN
STRDO_HladStrIzklop | DIGITAL | IOD_STR_TCP | 572 | 00572 | DO_HladStrIzklop
STRDO_KE1Vklop | DIGITAL | IOD_STR_TCP | 573 | 00573 | DO_KE1Vklop
STRDO_KE2Vklop | DIGITAL | IOD_STR_TCP | 574 | 00574 | DO_KE2Vklop
STRDO_KE3Vklop | DIGITAL | IOD_STR_TCP | 575 | 00575 | DO_KE3Vklop
STRDO_Klima1Vklop | DIGITAL | IOD_STR_TCP | 576 | 00576 | DO_Klima1Vklop
STRDO_Klima2Vklop | DIGITAL | IOD_STR_TCP | 577 | 00577 | DO_Klima2Vklop
STRDO_Lop1PL1Vklop | DIGITAL | IOD_STR_TCP | 578 | 00578 | DO_Lop1PL1Vklop
STRDO_Lop1PL2Vklop | DIGITAL | IOD_STR_TCP | 579 | 00579 | DO_Lop1PL2Vklop
STRDO_Lop1PL3Vklop | DIGITAL | IOD_STR_TCP | 580 | 00580 | DO_Lop1PL3Vklop
STRDO_Lop3Y1Vklop | DIGITAL | IOD_STR_TCP | 581 | 00581 | DO_Lop3Y1Vklop
STRDO_Lop4Y1Vklop | DIGITAL | IOD_STR_TCP | 582 | 00582 | DO_Lop4Y1Vklop
STRDO_RazE11_10Vklop | DIGITAL | IOD_STR_TCP | 583 | 00583 | DO_RazE11_10Vklop
STRDO_RazE11_11Vklop | DIGITAL | IOD_STR_TCP | 584 | 00584 | DO_RazE11_11Vklop
STRDO_RazE11_1Vklop | DIGITAL | IOD_STR_TCP | 585 | 00585 | DO_RazE11_1Vklop
STRDO_RazE11_2Vklop | DIGITAL | IOD_STR_TCP | 586 | 00586 | DO_RazE11_2Vklop
STRDO_RazE11_3Vklop | DIGITAL | IOD_STR_TCP | 587 | 00587 | DO_RazE11_3Vklop
STRDO_RazE11_4Vklop | DIGITAL | IOD_STR_TCP | 588 | 00588 | DO_RazE11_4Vklop
STRDO_RazE11_5Vklop | DIGITAL | IOD_STR_TCP | 589 | 00589 | DO_RazE11_5Vklop
STRDO_RazE11_6Vklop | DIGITAL | IOD_STR_TCP | 590 | 00590 | DO_RazE11_6Vklop
STRDO_RazE11_7Vklop | DIGITAL | IOD_STR_TCP | 591 | 00591 | DO_RazE11_7Vklop
STRDO_RazE11_8Vklop | DIGITAL | IOD_STR_TCP | 592 | 00592 | DO_RazE11_8Vklop
STRDO_RazE11_9Vklop | DIGITAL | IOD_STR_TCP | 593 | 00593 | DO_RazE11_9Vklop
STRDO_RazE12_12Vklop | DIGITAL | IOD_STR_TCP | 594 | 00594 | DO_RazE12_12Vklop
STRDO_RazE12_13Vklop | DIGITAL | IOD_STR_TCP | 595 | 00595 | DO_RazE12_13Vklop
STRDO_RazE12_14Vklop | DIGITAL | IOD_STR_TCP | 596 | 00596 | DO_RazE12_14Vklop
STRDO_RazE12_15Vklop | DIGITAL | IOD_STR_TCP | 597 | 00597 | DO_RazE12_15Vklop
STRDO_RazE13_16Vklop | DIGITAL | IOD_STR_TCP | 598 | 00598 | DO_RazE13_16Vklop
STRDO_RazE13_17Vklop | DIGITAL | IOD_STR_TCP | 599 | 00599 | DO_RazE13_17Vklop
STRDO_RazE13_18Vklop | DIGITAL | IOD_STR_TCP | 600 | 00600 | DO_RazE13_18Vklop
STRDO_RazE13_19Vklop | DIGITAL | IOD_STR_TCP | 601 | 00601 | DO_RazE13_19Vklop
STRDO_RazE16_20Vklop | DIGITAL | IOD_STR_TCP | 602 | 00602 | DO_RazE16_20Vklop
STRDO_RazE16_21Vklop | DIGITAL | IOD_STR_TCP | 603 | 00603 | DO_RazE16_21Vklop
STRDO_RazE16_22Vklop | DIGITAL | IOD_STR_TCP | 604 | 00604 | DO_RazE16_22Vklop
STRDO_RazE16_23Vklop | DIGITAL | IOD_STR_TCP | 605 | 00605 | DO_RazE16_23Vklop
STRDO_RazE16_24Vklop | DIGITAL | IOD_STR_TCP | 606 | 00606 | DO_RazE16_24Vklop
STRDO_Vent1Vklop | DIGITAL | IOD_STR_TCP | 607 | 00607 | DO_Vent1Vklop
STRDO_Vent2Vklop | DIGITAL | IOD_STR_TCP | 608 | 00608 | DO_Vent2Vklop
STRDO_Vent3Vklop | DIGITAL | IOD_STR_TCP | 609 | 00609 | DO_Vent3Vklop
STRDO_Vent4Vklop | DIGITAL | IOD_STR_TCP | 610 | 00610 | DO_Vent4Vklop
STRDO_Vent5Vklop | DIGITAL | IOD_STR_TCP | 611 | 00611 | DO_Vent5Vklop
STRDO_Vent6Vklop | DIGITAL | IOD_STR_TCP | 612 | 00612 | DO_Vent6Vklop
STRErrComCirc1 | DIGITAL | IOD_STR_TCP | 613 | 00613 | ErrComCirc[1]
STRErrComCirc2 | DIGITAL | IOD_STR_TCP | 614 | 00614 | ErrComCirc[2]
STRErrComDanfossHM1 | DIGITAL | IOD_STR_TCP | 615 | 00615 | ErrComDanfossHM[1]
STRErrComDanfossHM2 | DIGITAL | IOD_STR_TCP | 616 | 00616 | ErrComDanfossHM[2]
STRErrComDanfossHM3 | DIGITAL | IOD_STR_TCP | 617 | 00617 | ErrComDanfossHM[3]
STRErrComDanfossHM4 | DIGITAL | IOD_STR_TCP | 618 | 00618 | ErrComDanfossHM[4]
STRErrComGrundfos0 | DIGITAL | IOD_STR_TCP | 619 | 00619 | ErrComGrundfos[0]
STRErrComGrundfos10 | DIGITAL | IOD_STR_TCP | 620 | 00620 | ErrComGrundfos[10]
STRErrComGrundfos11 | DIGITAL | IOD_STR_TCP | 621 | 00621 | ErrComGrundfos[11]
STRErrComGrundfos12 | DIGITAL | IOD_STR_TCP | 622 | 00622 | ErrComGrundfos[12]
STRErrComGrundfos13 | DIGITAL | IOD_STR_TCP | 623 | 00623 | ErrComGrundfos[13]
STRErrComGrundfos14 | DIGITAL | IOD_STR_TCP | 624 | 00624 | ErrComGrundfos[14]
STRErrComGrundfos1 | DIGITAL | IOD_STR_TCP | 625 | 00625 | ErrComGrundfos[1]
STRErrComGrundfos2 | DIGITAL | IOD_STR_TCP | 626 | 00626 | ErrComGrundfos[2]
STRErrComGrundfos3 | DIGITAL | IOD_STR_TCP | 627 | 00627 | ErrComGrundfos[3]
STRErrComGrundfos4 | DIGITAL | IOD_STR_TCP | 628 | 00628 | ErrComGrundfos[4]
STRErrComGrundfos5 | DIGITAL | IOD_STR_TCP | 629 | 00629 | ErrComGrundfos[5]
STRErrComGrundfos6 | DIGITAL | IOD_STR_TCP | 630 | 00630 | ErrComGrundfos[6]
STRErrComGrundfos7 | DIGITAL | IOD_STR_TCP | 631 | 00631 | ErrComGrundfos[7]
STRErrComGrundfos8 | DIGITAL | IOD_STR_TCP | 632 | 00632 | ErrComGrundfos[8]
STRErrComGrundfos9 | DIGITAL | IOD_STR_TCP | 633 | 00633 | ErrComGrundfos[9]
STRErrComHladStroj | DIGITAL | IOD_STR_TCP | 634 | 00634 | ErrComHladStroj
STRErrComKlima1 | DIGITAL | IOD_STR_TCP | 635 | 00635 | ErrComKlima[1]
STRErrComKlima2 | DIGITAL | IOD_STR_TCP | 636 | 00636 | ErrComKlima[2]
STRErrCommScada | DIGITAL | IOD_STR_TCP | 637 | 00637 | ErrCommScada
STRErrCommXC100 | DIGITAL | IOD_STR_TCP | 638 | 00638 | ErrCommXC100
STRErrComPanelPLC | DIGITAL | IOD_STR_TCP | 639 | 00639 | ErrComPanelPLC
STRErrComPort2 | DIGITAL | IOD_STR_TCP | 640 | 00640 | ErrComPort2
STRErrComPort3 | DIGITAL | IOD_STR_TCP | 641 | 00641 | ErrComPort3
STRErrComPort4 | DIGITAL | IOD_STR_TCP | 642 | 00642 | ErrComPort4
STRErrComToplPost | DIGITAL | IOD_STR_TCP | 643 | 00643 | ErrComToplPost
STRExp1TlakAlarm | DIGITAL | IOD_STR_TCP | 644 | 00644 | Exp1TlakAlarm
STRExp2TlakAlarm | DIGITAL | IOD_STR_TCP | 645 | 00645 | Exp2TlakAlarm
STRHladilniStrojOnOff | DIGITAL | IOD_STR_TCP | 646 | 00646 | HladilniStrojOnOff
STRHladStrojFazeAlarm | DIGITAL | IOD_STR_TCP | 647 | 00647 | HladStroj.FazeAlarm
STRHladStrojKompresorOljeAlarm | DIGITAL | IOD_STR_TCP | 648 | 00648 | HladStroj.KompresorOljeAlarm
STRHladStrojLANcarelAlarm | DIGITAL | IOD_STR_TCP | 649 | 00649 | HladStroj.LANcarelAlarm
STRHladStrojNapaka | DIGITAL | IOD_STR_TCP | 650 | 00650 | HladStroj.Napaka
STRHladStrojNizekPritiskAlarm | DIGITAL | IOD_STR_TCP | 651 | 00651 | HladStroj.NizekPritiskAlarm
STRHladStrojObratovalneUreOpozorilo | DIGITAL | IOD_STR_TCP | 652 | 00652 | HladStroj.ObratovalneUreOpozorilo
STRHladStrojOffByAlarms | DIGITAL | IOD_STR_TCP | 653 | 00653 | HladStroj.OffByAlarms
STRHladStrojPretokAlarm | DIGITAL | IOD_STR_TCP | 654 | 00654 | HladStroj.PretokAlarm
STRHladStrojRemoteOn | DIGITAL | IOD_STR_TCP | 655 | 00655 | HladStroj.RemoteOn
STRHladStrojSenzorAlarm | DIGITAL | IOD_STR_TCP | 656 | 00656 | HladStroj.SenzorAlarm
STRHladStrojSummerOperation | DIGITAL | IOD_STR_TCP | 657 | 00657 | HladStroj.SummerOperation
STRHladStrojTemperaturaAlarm | DIGITAL | IOD_STR_TCP | 658 | 00658 | HladStroj.TemperaturaAlarm
STRHladStrojUnitOn | DIGITAL | IOD_STR_TCP | 659 | 00659 | HladStroj.UnitOn
STRHladStrojUraAlarm | DIGITAL | IOD_STR_TCP | 660 | 00660 | HladStroj.UraAlarm
STRHladStrojVisokPritiskAlarm | DIGITAL | IOD_STR_TCP | 661 | 00661 | HladStroj.VisokPritiskAlarm
STRHladStrojVisokPritiskOpozorilo | DIGITAL | IOD_STR_TCP | 662 | 00662 | HladStroj.VisokPritiskOpozorilo
STRHladStrojZmrzalniAlarm | DIGITAL | IOD_STR_TCP | 663 | 00663 | HladStroj.ZmrzalniAlarm
STRHladStrojErrors10 | DIGITAL | IOD_STR_TCP | 664 | 00664 | HladStrojErrors[10]
STRHladStrojErrors11 | DIGITAL | IOD_STR_TCP | 665 | 00665 | HladStrojErrors[11]
STRHladStrojErrors12 | DIGITAL | IOD_STR_TCP | 666 | 00666 | HladStrojErrors[12]
STRHladStrojErrors13 | DIGITAL | IOD_STR_TCP | 667 | 00667 | HladStrojErrors[13]
STRHladStrojErrors14 | DIGITAL | IOD_STR_TCP | 668 | 00668 | HladStrojErrors[14]
STRHladStrojErrors15 | DIGITAL | IOD_STR_TCP | 669 | 00669 | HladStrojErrors[15]
STRHladStrojErrors16 | DIGITAL | IOD_STR_TCP | 670 | 00670 | HladStrojErrors[16]
STRHladStrojErrors1 | DIGITAL | IOD_STR_TCP | 671 | 00671 | HladStrojErrors[1]
STRHladStrojErrors2 | DIGITAL | IOD_STR_TCP | 672 | 00672 | HladStrojErrors[2]
STRHladStrojErrors3 | DIGITAL | IOD_STR_TCP | 673 | 00673 | HladStrojErrors[3]
STRHladStrojErrors4 | DIGITAL | IOD_STR_TCP | 674 | 00674 | HladStrojErrors[4]
STRHladStrojErrors5 | DIGITAL | IOD_STR_TCP | 675 | 00675 | HladStrojErrors[5]
STRHladStrojErrors6 | DIGITAL | IOD_STR_TCP | 676 | 00676 | HladStrojErrors[6]
STRHladStrojErrors7 | DIGITAL | IOD_STR_TCP | 677 | 00677 | HladStrojErrors[7]
STRHladStrojErrors8 | DIGITAL | IOD_STR_TCP | 678 | 00678 | HladStrojErrors[8]
STRHladStrojErrors9 | DIGITAL | IOD_STR_TCP | 679 | 00679 | HladStrojErrors[9]
STRKlima1errors10 | DIGITAL | IOD_STR_TCP | 680 | 00680 | Klima1errors[10]
STRKlima1errors11 | DIGITAL | IOD_STR_TCP | 681 | 00681 | Klima1errors[11]
STRKlima1errors12 | DIGITAL | IOD_STR_TCP | 682 | 00682 | Klima1errors[12]
STRKlima1errors1 | DIGITAL | IOD_STR_TCP | 683 | 00683 | Klima1errors[1]
STRKlima1errors2 | DIGITAL | IOD_STR_TCP | 684 | 00684 | Klima1errors[2]
STRKlima1errors3 | DIGITAL | IOD_STR_TCP | 685 | 00685 | Klima1errors[3]
STRKlima1errors4 | DIGITAL | IOD_STR_TCP | 686 | 00686 | Klima1errors[4]
STRKlima1errors5 | DIGITAL | IOD_STR_TCP | 687 | 00687 | Klima1errors[5]
STRKlima1errors6 | DIGITAL | IOD_STR_TCP | 688 | 00688 | Klima1errors[6]
STRKlima1errors7 | DIGITAL | IOD_STR_TCP | 689 | 00689 | Klima1errors[7]
STRKlima1errors8 | DIGITAL | IOD_STR_TCP | 690 | 00690 | Klima1errors[8]
STRKlima1errors9 | DIGITAL | IOD_STR_TCP | 691 | 00691 | Klima1errors[9]
STRKlima2errors10 | DIGITAL | IOD_STR_TCP | 692 | 00692 | Klima2errors[10]
STRKlima2errors11 | DIGITAL | IOD_STR_TCP | 693 | 00693 | Klima2errors[11]
STRKlima2errors12 | DIGITAL | IOD_STR_TCP | 694 | 00694 | Klima2errors[12]
STRKlima2errors1 | DIGITAL | IOD_STR_TCP | 695 | 00695 | Klima2errors[1]
STRKlima2errors2 | DIGITAL | IOD_STR_TCP | 696 | 00696 | Klima2errors[2]
STRKlima2errors3 | DIGITAL | IOD_STR_TCP | 697 | 00697 | Klima2errors[3]
STRKlima2errors4 | DIGITAL | IOD_STR_TCP | 698 | 00698 | Klima2errors[4]
STRKlima2errors5 | DIGITAL | IOD_STR_TCP | 699 | 00699 | Klima2errors[5]
STRKlima2errors6 | DIGITAL | IOD_STR_TCP | 700 | 00700 | Klima2errors[6]
STRKlima2errors7 | DIGITAL | IOD_STR_TCP | 701 | 00701 | Klima2errors[7]
STRKlima2errors8 | DIGITAL | IOD_STR_TCP | 702 | 00702 | Klima2errors[8]
STRKlima2errors9 | DIGITAL | IOD_STR_TCP | 703 | 00703 | Klima2errors[9]
STRKlima1CrpalkaGrelnika | DIGITAL | IOD_STR_TCP | 704 | 00704 | Klima[1].CrpalkaGrelnika
STRKlima1DelovanjeVentH1 | DIGITAL | IOD_STR_TCP | 705 | 00705 | Klima[1].DelovanjeVentH1
STRKlima1DelovanjeVentH2 | DIGITAL | IOD_STR_TCP | 706 | 00706 | Klima[1].DelovanjeVentH2
STRKlima1Deluje | DIGITAL | IOD_STR_TCP | 707 | 00707 | Klima[1].Deluje
STRKlima1FilterError | DIGITAL | IOD_STR_TCP | 708 | 00708 | Klima[1].FilterError
STRKlima1Napaka | DIGITAL | IOD_STR_TCP | 709 | 00709 | Klima[1].Napaka
STRKlima1NapakaPriPretokuZraka | DIGITAL | IOD_STR_TCP | 710 | 00710 | Klima[1].NapakaPriPretokuZraka
STRKlima1OkvaraRototerma | DIGITAL | IOD_STR_TCP | 711 | 00711 | Klima[1].OkvaraRototerma
STRKlima1OkvaraVlazilne | DIGITAL | IOD_STR_TCP | 712 | 00712 | Klima[1].OkvaraVlazilne
STRKlima1PozarError | DIGITAL | IOD_STR_TCP | 713 | 00713 | Klima[1].PozarError
STRKlima1PozarniAlarm | DIGITAL | IOD_STR_TCP | 714 | 00714 | Klima[1].PozarniAlarm
STRKlima1PreobremenitevMotCrpGr | DIGITAL | IOD_STR_TCP | 715 | 00715 | Klima[1].PreobremenitevMotCrpGr
STRKlima1PreobremenitevMotVent | DIGITAL | IOD_STR_TCP | 716 | 00716 | Klima[1].PreobremenitevMotVent
STRKlima1ProtizmrzAktivna | DIGITAL | IOD_STR_TCP | 717 | 00717 | Klima[1].ProtizmrzAktivna
STRKlima1SkupniAlarmA | DIGITAL | IOD_STR_TCP | 718 | 00718 | Klima[1].SkupniAlarmA
STRKlima1SkupniAlarmB | DIGITAL | IOD_STR_TCP | 719 | 00719 | Klima[1].SkupniAlarmB
STRKlima1VklopRegulacije | DIGITAL | IOD_STR_TCP | 720 | 00720 | Klima[1].VklopRegulacije
STRKlima1ZamasenFilter | DIGITAL | IOD_STR_TCP | 721 | 00721 | Klima[1].ZamasenFilter
STRKlima2CrpalkaGrelnika | DIGITAL | IOD_STR_TCP | 722 | 00722 | Klima[2].CrpalkaGrelnika
STRKlima2DelovanjeVentH1 | DIGITAL | IOD_STR_TCP | 723 | 00723 | Klima[2].DelovanjeVentH1
STRKlima2DelovanjeVentH2 | DIGITAL | IOD_STR_TCP | 724 | 00724 | Klima[2].DelovanjeVentH2
STRKlima2Deluje | DIGITAL | IOD_STR_TCP | 725 | 00725 | Klima[2].Deluje
STRKlima2FilterError | DIGITAL | IOD_STR_TCP | 726 | 00726 | Klima[2].FilterError
STRKlima2Napaka | DIGITAL | IOD_STR_TCP | 727 | 00727 | Klima[2].Napaka
STRKlima2NapakaPriPretokuZraka | DIGITAL | IOD_STR_TCP | 728 | 00728 | Klima[2].NapakaPriPretokuZraka
STRKlima2OkvaraRototerma | DIGITAL | IOD_STR_TCP | 729 | 00729 | Klima[2].OkvaraRototerma
STRKlima2OkvaraVlazilne | DIGITAL | IOD_STR_TCP | 730 | 00730 | Klima[2].OkvaraVlazilne
STRKlima2PozarError | DIGITAL | IOD_STR_TCP | 731 | 00731 | Klima[2].PozarError
STRKlima2PozarniAlarm | DIGITAL | IOD_STR_TCP | 732 | 00732 | Klima[2].PozarniAlarm
STRKlima2PreobremenitevMotCrpGr | DIGITAL | IOD_STR_TCP | 733 | 00733 | Klima[2].PreobremenitevMotCrpGr
STRKlima2PreobremenitevMotVent | DIGITAL | IOD_STR_TCP | 734 | 00734 | Klima[2].PreobremenitevMotVent
STRKlima2ProtizmrzAktivna | DIGITAL | IOD_STR_TCP | 735 | 00735 | Klima[2].ProtizmrzAktivna
STRKlima2SkupniAlarmA | DIGITAL | IOD_STR_TCP | 736 | 00736 | Klima[2].SkupniAlarmA
STRKlima2SkupniAlarmB | DIGITAL | IOD_STR_TCP | 737 | 00737 | Klima[2].SkupniAlarmB
STRKlima2VklopRegulacije | DIGITAL | IOD_STR_TCP | 738 | 00738 | Klima[2].VklopRegulacije
STRKlima2ZamasenFilter | DIGITAL | IOD_STR_TCP | 739 | 00739 | Klima[2].ZamasenFilter
STRKondEnotaOnOff1 | DIGITAL | IOD_STR_TCP | 740 | 00740 | KondEnotaOnOff[1]
STRKondEnotaOnOff2 | DIGITAL | IOD_STR_TCP | 741 | 00741 | KondEnotaOnOff[2]
STRKondEnotaOnOff3 | DIGITAL | IOD_STR_TCP | 742 | 00742 | KondEnotaOnOff[3]
STRKontRezervaOnOff1 | DIGITAL | IOD_STR_TCP | 743 | 00743 | KontRezervaOnOff[1]
STRKontRezervaOnOff2 | DIGITAL | IOD_STR_TCP | 744 | 00744 | KontRezervaOnOff[2]
STRKontRezervaOnOff3 | DIGITAL | IOD_STR_TCP | 745 | 00745 | KontRezervaOnOff[3]
STRNapakaSenzorAI10 | DIGITAL | IOD_STR_TCP | 746 | 00746 | NapakaSenzorAI[10]
STRNapakaSenzorAI11 | DIGITAL | IOD_STR_TCP | 747 | 00747 | NapakaSenzorAI[11]
STRNapakaSenzorAI12 | DIGITAL | IOD_STR_TCP | 748 | 00748 | NapakaSenzorAI[12]
STRNapakaSenzorAI13 | DIGITAL | IOD_STR_TCP | 749 | 00749 | NapakaSenzorAI[13]
STRNapakaSenzorAI14 | DIGITAL | IOD_STR_TCP | 750 | 00750 | NapakaSenzorAI[14]
STRNapakaSenzorAI15 | DIGITAL | IOD_STR_TCP | 751 | 00751 | NapakaSenzorAI[15]
STRNapakaSenzorAI16 | DIGITAL | IOD_STR_TCP | 752 | 00752 | NapakaSenzorAI[16]
STRNapakaSenzorAI17 | DIGITAL | IOD_STR_TCP | 753 | 00753 | NapakaSenzorAI[17]
STRNapakaSenzorAI18 | DIGITAL | IOD_STR_TCP | 754 | 00754 | NapakaSenzorAI[18]
STRNapakaSenzorAI19 | DIGITAL | IOD_STR_TCP | 755 | 00755 | NapakaSenzorAI[19]
STRNapakaSenzorAI1 | DIGITAL | IOD_STR_TCP | 756 | 00756 | NapakaSenzorAI[1]
STRNapakaSenzorAI20 | DIGITAL | IOD_STR_TCP | 757 | 00757 | NapakaSenzorAI[20]
STRNapakaSenzorAI21 | DIGITAL | IOD_STR_TCP | 758 | 00758 | NapakaSenzorAI[21]
STRNapakaSenzorAI22 | DIGITAL | IOD_STR_TCP | 759 | 00759 | NapakaSenzorAI[22]
STRNapakaSenzorAI23 | DIGITAL | IOD_STR_TCP | 760 | 00760 | NapakaSenzorAI[23]
STRNapakaSenzorAI24 | DIGITAL | IOD_STR_TCP | 761 | 00761 | NapakaSenzorAI[24]
STRNapakaSenzorAI25 | DIGITAL | IOD_STR_TCP | 762 | 00762 | NapakaSenzorAI[25]
STRNapakaSenzorAI26 | DIGITAL | IOD_STR_TCP | 763 | 00763 | NapakaSenzorAI[26]
STRNapakaSenzorAI27 | DIGITAL | IOD_STR_TCP | 764 | 00764 | NapakaSenzorAI[27]
STRNapakaSenzorAI28 | DIGITAL | IOD_STR_TCP | 765 | 00765 | NapakaSenzorAI[28]
STRNapakaSenzorAI29 | DIGITAL | IOD_STR_TCP | 766 | 00766 | NapakaSenzorAI[29]
STRNapakaSenzorAI2 | DIGITAL | IOD_STR_TCP | 767 | 00767 | NapakaSenzorAI[2]
STRNapakaSenzorAI30 | DIGITAL | IOD_STR_TCP | 768 | 00768 | NapakaSenzorAI[30]
STRNapakaSenzorAI31 | DIGITAL | IOD_STR_TCP | 769 | 00769 | NapakaSenzorAI[31]
STRNapakaSenzorAI32 | DIGITAL | IOD_STR_TCP | 770 | 00770 | NapakaSenzorAI[32]
STRNapakaSenzorAI33 | DIGITAL | IOD_STR_TCP | 771 | 00771 | NapakaSenzorAI[33]
STRNapakaSenzorAI34 | DIGITAL | IOD_STR_TCP | 772 | 00772 | NapakaSenzorAI[34]
STRNapakaSenzorAI35 | DIGITAL | IOD_STR_TCP | 773 | 00773 | NapakaSenzorAI[35]
STRNapakaSenzorAI36 | DIGITAL | IOD_STR_TCP | 774 | 00774 | NapakaSenzorAI[36]
STRNapakaSenzorAI37 | DIGITAL | IOD_STR_TCP | 775 | 00775 | NapakaSenzorAI[37]
STRNapakaSenzorAI38 | DIGITAL | IOD_STR_TCP | 776 | 00776 | NapakaSenzorAI[38]
STRNapakaSenzorAI39 | DIGITAL | IOD_STR_TCP | 777 | 00777 | NapakaSenzorAI[39]
STRNapakaSenzorAI3 | DIGITAL | IOD_STR_TCP | 778 | 00778 | NapakaSenzorAI[3]
STRNapakaSenzorAI40 | DIGITAL | IOD_STR_TCP | 779 | 00779 | NapakaSenzorAI[40]
STRNapakaSenzorAI4 | DIGITAL | IOD_STR_TCP | 780 | 00780 | NapakaSenzorAI[4]
STRNapakaSenzorAI5 | DIGITAL | IOD_STR_TCP | 781 | 00781 | NapakaSenzorAI[5]
STRNapakaSenzorAI6 | DIGITAL | IOD_STR_TCP | 782 | 00782 | NapakaSenzorAI[6]
STRNapakaSenzorAI7 | DIGITAL | IOD_STR_TCP | 783 | 00783 | NapakaSenzorAI[7]
STRNapakaSenzorAI8 | DIGITAL | IOD_STR_TCP | 784 | 00784 | NapakaSenzorAI[8]
STRNapakaSenzorAI9 | DIGITAL | IOD_STR_TCP | 785 | 00785 | NapakaSenzorAI[9]
STRNapakaSenzorHIA1 | DIGITAL | IOD_STR_TCP | 786 | 00786 | NapakaSenzorHIA[1]
STRNapakaSenzorHIA2 | DIGITAL | IOD_STR_TCP | 787 | 00787 | NapakaSenzorHIA[2]
STRNapakaSenzorHIA3 | DIGITAL | IOD_STR_TCP | 788 | 00788 | NapakaSenzorHIA[3]
STRNapakaSenzorHIA4 | DIGITAL | IOD_STR_TCP | 789 | 00789 | NapakaSenzorHIA[4]
STRNapakaSenzorTIA1 | DIGITAL | IOD_STR_TCP | 790 | 00790 | NapakaSenzorTIA[1]
STRNapakaSenzorTIA2 | DIGITAL | IOD_STR_TCP | 791 | 00791 | NapakaSenzorTIA[2]
STRNapakaSenzorTIA3 | DIGITAL | IOD_STR_TCP | 792 | 00792 | NapakaSenzorTIA[3]
STRNapakaSenzorTIA4 | DIGITAL | IOD_STR_TCP | 793 | 00793 | NapakaSenzorTIA[4]
STRPozarnaLoputaOnOffError1 | DIGITAL | IOD_STR_TCP | 794 | 00794 | PozarnaLoputaOnOffError[1]
STRPozarnaLoputaOnOffError2 | DIGITAL | IOD_STR_TCP | 795 | 00795 | PozarnaLoputaOnOffError[2]
STRPozarnaLoputaOnOffError3 | DIGITAL | IOD_STR_TCP | 796 | 00796 | PozarnaLoputaOnOffError[3]
STRPozarnaLoputaOnOffError4 | DIGITAL | IOD_STR_TCP | 797 | 00797 | PozarnaLoputaOnOffError[4]
STRPozarnaLoputaOnOffError5 | DIGITAL | IOD_STR_TCP | 798 | 00798 | PozarnaLoputaOnOffError[5]
STRPozarnaLoputOnOff1 | DIGITAL | IOD_STR_TCP | 799 | 00799 | PozarnaLoputOnOff[1]
STRPozarnaLoputOnOff2 | DIGITAL | IOD_STR_TCP | 800 | 00800 | PozarnaLoputOnOff[2]
STRPozarnaLoputOnOff3 | DIGITAL | IOD_STR_TCP | 801 | 00801 | PozarnaLoputOnOff[3]
STRPozarnaLoputOnOff4 | DIGITAL | IOD_STR_TCP | 802 | 00802 | PozarnaLoputOnOff[4]
STRPozarnaLoputOnOff5 | DIGITAL | IOD_STR_TCP | 803 | 00803 | PozarnaLoputOnOff[5]
STRPozarniAlarm | DIGITAL | IOD_STR_TCP | 804 | 00804 | PozarniAlarm
STRPrenosUrnika10 | DIGITAL | IOD_STR_TCP | 805 | 00805 | PrenosUrnika[10]
STRPrenosUrnika11 | DIGITAL | IOD_STR_TCP | 806 | 00806 | PrenosUrnika[11]
STRPrenosUrnika12 | DIGITAL | IOD_STR_TCP | 807 | 00807 | PrenosUrnika[12]
STRPrenosUrnika13 | DIGITAL | IOD_STR_TCP | 808 | 00808 | PrenosUrnika[13]
STRPrenosUrnika14 | DIGITAL | IOD_STR_TCP | 809 | 00809 | PrenosUrnika[14]
STRPrenosUrnika15 | DIGITAL | IOD_STR_TCP | 810 | 00810 | PrenosUrnika[15]
STRPrenosUrnika16 | DIGITAL | IOD_STR_TCP | 811 | 00811 | PrenosUrnika[16]
STRPrenosUrnika17 | DIGITAL | IOD_STR_TCP | 812 | 00812 | PrenosUrnika[17]
STRPrenosUrnika18 | DIGITAL | IOD_STR_TCP | 813 | 00813 | PrenosUrnika[18]
STRPrenosUrnika19 | DIGITAL | IOD_STR_TCP | 814 | 00814 | PrenosUrnika[19]
STRPrenosUrnika1 | DIGITAL | IOD_STR_TCP | 815 | 00815 | PrenosUrnika[1]
STRPrenosUrnika20 | DIGITAL | IOD_STR_TCP | 816 | 00816 | PrenosUrnika[20]
STRPrenosUrnika21 | DIGITAL | IOD_STR_TCP | 817 | 00817 | PrenosUrnika[21]
STRPrenosUrnika22 | DIGITAL | IOD_STR_TCP | 818 | 00818 | PrenosUrnika[22]
STRPrenosUrnika23 | DIGITAL | IOD_STR_TCP | 819 | 00819 | PrenosUrnika[23]
STRPrenosUrnika24 | DIGITAL | IOD_STR_TCP | 820 | 00820 | PrenosUrnika[24]
STRPrenosUrnika25 | DIGITAL | IOD_STR_TCP | 821 | 00821 | PrenosUrnika[25]
STRPrenosUrnika2 | DIGITAL | IOD_STR_TCP | 822 | 00822 | PrenosUrnika[2]
STRPrenosUrnika3 | DIGITAL | IOD_STR_TCP | 823 | 00823 | PrenosUrnika[3]
STRPrenosUrnika4 | DIGITAL | IOD_STR_TCP | 824 | 00824 | PrenosUrnika[4]
STRPrenosUrnika5 | DIGITAL | IOD_STR_TCP | 825 | 00825 | PrenosUrnika[5]
STRPrenosUrnika6 | DIGITAL | IOD_STR_TCP | 826 | 00826 | PrenosUrnika[6]
STRPrenosUrnika7 | DIGITAL | IOD_STR_TCP | 827 | 00827 | PrenosUrnika[7]
STRPrenosUrnika8 | DIGITAL | IOD_STR_TCP | 828 | 00828 | PrenosUrnika[8]
STRPrenosUrnika9 | DIGITAL | IOD_STR_TCP | 829 | 00829 | PrenosUrnika[9]
STRRazsvetljavaOnOff10 | DIGITAL | IOD_STR_TCP | 830 | 00830 | RazsvetljavaOnOff[10]
STRRazsvetljavaOnOff11 | DIGITAL | IOD_STR_TCP | 831 | 00831 | RazsvetljavaOnOff[11]
STRRazsvetljavaOnOff12 | DIGITAL | IOD_STR_TCP | 832 | 00832 | RazsvetljavaOnOff[12]
STRRazsvetljavaOnOff13 | DIGITAL | IOD_STR_TCP | 833 | 00833 | RazsvetljavaOnOff[13]
STRRazsvetljavaOnOff14 | DIGITAL | IOD_STR_TCP | 834 | 00834 | RazsvetljavaOnOff[14]
STRRazsvetljavaOnOff15 | DIGITAL | IOD_STR_TCP | 835 | 00835 | RazsvetljavaOnOff[15]
STRRazsvetljavaOnOff16 | DIGITAL | IOD_STR_TCP | 836 | 00836 | RazsvetljavaOnOff[16]
STRRazsvetljavaOnOff17 | DIGITAL | IOD_STR_TCP | 837 | 00837 | RazsvetljavaOnOff[17]
STRRazsvetljavaOnOff18 | DIGITAL | IOD_STR_TCP | 838 | 00838 | RazsvetljavaOnOff[18]
STRRazsvetljavaOnOff19 | DIGITAL | IOD_STR_TCP | 839 | 00839 | RazsvetljavaOnOff[19]
STRRazsvetljavaOnOff1 | DIGITAL | IOD_STR_TCP | 840 | 00840 | RazsvetljavaOnOff[1]
STRRazsvetljavaOnOff20 | DIGITAL | IOD_STR_TCP | 841 | 00841 | RazsvetljavaOnOff[20]
STRRazsvetljavaOnOff21 | DIGITAL | IOD_STR_TCP | 842 | 00842 | RazsvetljavaOnOff[21]
STRRazsvetljavaOnOff22 | DIGITAL | IOD_STR_TCP | 843 | 00843 | RazsvetljavaOnOff[22]
STRRazsvetljavaOnOff23 | DIGITAL | IOD_STR_TCP | 844 | 00844 | RazsvetljavaOnOff[23]
STRRazsvetljavaOnOff24 | DIGITAL | IOD_STR_TCP | 845 | 00845 | RazsvetljavaOnOff[24]
STRRazsvetljavaOnOff25 | DIGITAL | IOD_STR_TCP | 846 | 00846 | RazsvetljavaOnOff[25]
STRRazsvetljavaOnOff2 | DIGITAL | IOD_STR_TCP | 847 | 00847 | RazsvetljavaOnOff[2]
STRRazsvetljavaOnOff3 | DIGITAL | IOD_STR_TCP | 848 | 00848 | RazsvetljavaOnOff[3]
STRRazsvetljavaOnOff4 | DIGITAL | IOD_STR_TCP | 849 | 00849 | RazsvetljavaOnOff[4]
STRRazsvetljavaOnOff5 | DIGITAL | IOD_STR_TCP | 850 | 00850 | RazsvetljavaOnOff[5]
STRRazsvetljavaOnOff6 | DIGITAL | IOD_STR_TCP | 851 | 00851 | RazsvetljavaOnOff[6]
STRRazsvetljavaOnOff7 | DIGITAL | IOD_STR_TCP | 852 | 00852 | RazsvetljavaOnOff[7]
STRRazsvetljavaOnOff8 | DIGITAL | IOD_STR_TCP | 853 | 00853 | RazsvetljavaOnOff[8]
STRRazsvetljavaOnOff9 | DIGITAL | IOD_STR_TCP | 854 | 00854 | RazsvetljavaOnOff[9]
STRRazsvetljavaRocno | DIGITAL | IOD_STR_TCP | 855 | 00855 | RazsvetljavaRocno
STRSetDateTime | DIGITAL | IOD_STR_TCP | 856 | 00856 | SetDateTime
STRSetDateTimeDemand | DIGITAL | IOD_STR_TCP | 857 | 00857 | SetDateTimeDemand
STRSetDateTimeError | DIGITAL | IOD_STR_TCP | 858 | 00858 | SetDateTimeError
STRSetDateTimeFinished | DIGITAL | IOD_STR_TCP | 859 | 00859 | SetDateTimeFinished
STRSetRemoteOnOff1 | DIGITAL | IOD_STR_TCP | 860 | 00860 | SetRemoteOnOff[1]
STRSetRemoteOnOff2 | DIGITAL | IOD_STR_TCP | 861 | 00861 | SetRemoteOnOff[2]
STRSlabaBaterijaPLC_A1 | DIGITAL | IOD_STR_TCP | 862 | 00862 | SlabaBaterijaPLC_A1
STRSlabaBaterijaPLC_A100 | DIGITAL | IOD_STR_TCP | 863 | 00863 | SlabaBaterijaPLC_A100
STRSO_BojlerTE1Vklop | DIGITAL | IOD_STR_TCP | 864 | 00864 | SO_BojlerTE1Vklop
STRSO_CrpHM1Vklop | DIGITAL | IOD_STR_TCP | 865 | 00865 | SO_CrpHM1Vklop
STRSO_CrpHM2Vklop | DIGITAL | IOD_STR_TCP | 866 | 00866 | SO_CrpHM2Vklop
STRSO_CrpHM3Vklop | DIGITAL | IOD_STR_TCP | 867 | 00867 | SO_CrpHM3Vklop
STRSO_CrpHM4Vklop | DIGITAL | IOD_STR_TCP | 868 | 00868 | SO_CrpHM4Vklop
STRSO_CrpMN1Vklop | DIGITAL | IOD_STR_TCP | 869 | 00869 | SO_CrpMN1Vklop
STRSO_CrpTM11Vklop | DIGITAL | IOD_STR_TCP | 870 | 00870 | SO_CrpTM11Vklop
STRSO_HladStrVklop | DIGITAL | IOD_STR_TCP | 871 | 00871 | SO_HladStrVklop
STRSO_KE1Vklop | DIGITAL | IOD_STR_TCP | 872 | 00872 | SO_KE1Vklop
STRSO_KE2Vklop | DIGITAL | IOD_STR_TCP | 873 | 00873 | SO_KE2Vklop
STRSO_KE3Vklop | DIGITAL | IOD_STR_TCP | 874 | 00874 | SO_KE3Vklop
STRSO_rezerva1_3 | DIGITAL | IOD_STR_TCP | 875 | 00875 | SO_rezerva1_3
STRSO_rezerva1_4 | DIGITAL | IOD_STR_TCP | 876 | 00876 | SO_rezerva1_4
STRSO_rezerva1_5 | DIGITAL | IOD_STR_TCP | 877 | 00877 | SO_rezerva1_5
STRSO_Vent1Vklop | DIGITAL | IOD_STR_TCP | 878 | 00878 | SO_Vent1Vklop
STRSO_Vent2Vklop | DIGITAL | IOD_STR_TCP | 879 | 00879 | SO_Vent2Vklop
STRSO_Vent3Vklop | DIGITAL | IOD_STR_TCP | 880 | 00880 | SO_Vent3Vklop
STRSO_Vent4Vklop | DIGITAL | IOD_STR_TCP | 881 | 00881 | SO_Vent4Vklop
STRSO_Vent5Vklop | DIGITAL | IOD_STR_TCP | 882 | 00882 | SO_Vent5Vklop
STRSO_Vent6Vklop | DIGITAL | IOD_STR_TCP | 883 | 00883 | SO_Vent6Vklop
STRTEgrelecNaTemp | DIGITAL | IOD_STR_TCP | 884 | 00884 | TEgrelecNaTemp
STRTEgrelecTempVklop | DIGITAL | IOD_STR_TCP | 885 | 00885 | TEgrelecTempVklop
STRTempTSprevisoka | DIGITAL | IOD_STR_TCP | 886 | 00886 | TempTSprevisoka
STRToplPostHKcrpalkaON | DIGITAL | IOD_STR_TCP | 887 | 00887 | ToplPost.HKcrpalkaON
STRToplPostHKcrpDnevniRezim | DIGITAL | IOD_STR_TCP | 888 | 00888 | ToplPost.HKcrpDnevniRezim
STRToplPostHKcrpNocniRezim | DIGITAL | IOD_STR_TCP | 889 | 00889 | ToplPost.HKcrpNocniRezim
STRToplPostHKrocniRezim | DIGITAL | IOD_STR_TCP | 890 | 00890 | ToplPost.HKrocniRezim
STRToplPostSkupnaNapaka | DIGITAL | IOD_STR_TCP | 891 | 00891 | ToplPost.SkupnaNapaka
STRToplPostTVcrpalkaON | DIGITAL | IOD_STR_TCP | 892 | 00892 | ToplPost.TVcrpalkaON
STRToplPostTVrocniRezim | DIGITAL | IOD_STR_TCP | 893 | 00893 | ToplPost.TVrocniRezim
STRToplPostErrors0 | DIGITAL | IOD_STR_TCP | 894 | 00894 | ToplPostErrors[0]
STRToplPostErrors10 | DIGITAL | IOD_STR_TCP | 895 | 00895 | ToplPostErrors[10]
STRToplPostErrors11 | DIGITAL | IOD_STR_TCP | 896 | 00896 | ToplPostErrors[11]
STRToplPostErrors12 | DIGITAL | IOD_STR_TCP | 897 | 00897 | ToplPostErrors[12]
STRToplPostErrors13 | DIGITAL | IOD_STR_TCP | 898 | 00898 | ToplPostErrors[13]
STRToplPostErrors14 | DIGITAL | IOD_STR_TCP | 899 | 00899 | ToplPostErrors[14]
STRToplPostErrors15 | DIGITAL | IOD_STR_TCP | 900 | 00900 | ToplPostErrors[15]
STRToplPostErrors16 | DIGITAL | IOD_STR_TCP | 901 | 00901 | ToplPostErrors[16]
STRToplPostErrors17 | DIGITAL | IOD_STR_TCP | 902 | 00902 | ToplPostErrors[17]
STRToplPostErrors1 | DIGITAL | IOD_STR_TCP | 903 | 00903 | ToplPostErrors[1]
STRToplPostErrors2 | DIGITAL | IOD_STR_TCP | 904 | 00904 | ToplPostErrors[2]
STRToplPostErrors3 | DIGITAL | IOD_STR_TCP | 905 | 00905 | ToplPostErrors[3]
STRToplPostErrors4 | DIGITAL | IOD_STR_TCP | 906 | 00906 | ToplPostErrors[4]
STRToplPostErrors5 | DIGITAL | IOD_STR_TCP | 907 | 00907 | ToplPostErrors[5]
STRToplPostErrors6 | DIGITAL | IOD_STR_TCP | 908 | 00908 | ToplPostErrors[6]
STRToplPostErrors7 | DIGITAL | IOD_STR_TCP | 909 | 00909 | ToplPostErrors[7]
STRToplPostErrors8 | DIGITAL | IOD_STR_TCP | 910 | 00910 | ToplPostErrors[8]
STRToplPostErrors9 | DIGITAL | IOD_STR_TCP | 911 | 00911 | ToplPostErrors[9]
STRTYventilNaTemp1 | DIGITAL | IOD_STR_TCP | 912 | 00912 | TYventilNaTemp[1]
STRTYventilNaTemp2 | DIGITAL | IOD_STR_TCP | 913 | 00913 | TYventilNaTemp[2]
STRTYventilNaTemp3 | DIGITAL | IOD_STR_TCP | 914 | 00914 | TYventilNaTemp[3]
STRTYventilNaTemp4 | DIGITAL | IOD_STR_TCP | 915 | 00915 | TYventilNaTemp[4]
STRUserLoggedIn | DIGITAL | IOD_STR_TCP | 916 | 00916 | UserLoggedIn
STRVentilatorOnOff1 | DIGITAL | IOD_STR_TCP | 917 | 00917 | VentilatorOnOff[1]
STRVentilatorOnOff2 | DIGITAL | IOD_STR_TCP | 918 | 00918 | VentilatorOnOff[2]
STRVentilatorOnOff3 | DIGITAL | IOD_STR_TCP | 919 | 00919 | VentilatorOnOff[3]
STRVentilatorOnOff4 | DIGITAL | IOD_STR_TCP | 920 | 00920 | VentilatorOnOff[4]
STRVentilatorOnOff5 | DIGITAL | IOD_STR_TCP | 921 | 00921 | VentilatorOnOff[5]
STRVentilatorOnOff6 | DIGITAL | IOD_STR_TCP | 922 | 00922 | VentilatorOnOff[6]
STRVklopSCFBNapaka10 | DIGITAL | IOD_STR_TCP | 923 | 00923 | VklopSCFBNapaka[10]
STRVklopSCFBNapaka11 | DIGITAL | IOD_STR_TCP | 924 | 00924 | VklopSCFBNapaka[11]
STRVklopSCFBNapaka12 | DIGITAL | IOD_STR_TCP | 925 | 00925 | VklopSCFBNapaka[12]
STRVklopSCFBNapaka13 | DIGITAL | IOD_STR_TCP | 926 | 00926 | VklopSCFBNapaka[13]
STRVklopSCFBNapaka14 | DIGITAL | IOD_STR_TCP | 927 | 00927 | VklopSCFBNapaka[14]
STRVklopSCFBNapaka15 | DIGITAL | IOD_STR_TCP | 928 | 00928 | VklopSCFBNapaka[15]
STRVklopSCFBNapaka16 | DIGITAL | IOD_STR_TCP | 929 | 00929 | VklopSCFBNapaka[16]
STRVklopSCFBNapaka17 | DIGITAL | IOD_STR_TCP | 930 | 00930 | VklopSCFBNapaka[17]
STRVklopSCFBNapaka18 | DIGITAL | IOD_STR_TCP | 931 | 00931 | VklopSCFBNapaka[18]
STRVklopSCFBNapaka19 | DIGITAL | IOD_STR_TCP | 932 | 00932 | VklopSCFBNapaka[19]
STRVklopSCFBNapaka1 | DIGITAL | IOD_STR_TCP | 933 | 00933 | VklopSCFBNapaka[1]
STRVklopSCFBNapaka20 | DIGITAL | IOD_STR_TCP | 934 | 00934 | VklopSCFBNapaka[20]
STRVklopSCFBNapaka21 | DIGITAL | IOD_STR_TCP | 935 | 00935 | VklopSCFBNapaka[21]
STRVklopSCFBNapaka22 | DIGITAL | IOD_STR_TCP | 936 | 00936 | VklopSCFBNapaka[22]
STRVklopSCFBNapaka23 | DIGITAL | IOD_STR_TCP | 937 | 00937 | VklopSCFBNapaka[23]
STRVklopSCFBNapaka24 | DIGITAL | IOD_STR_TCP | 938 | 00938 | VklopSCFBNapaka[24]
STRVklopSCFBNapaka25 | DIGITAL | IOD_STR_TCP | 939 | 00939 | VklopSCFBNapaka[25]
STRVklopSCFBNapaka2 | DIGITAL | IOD_STR_TCP | 940 | 00940 | VklopSCFBNapaka[2]
STRVklopSCFBNapaka3 | DIGITAL | IOD_STR_TCP | 941 | 00941 | VklopSCFBNapaka[3]
STRVklopSCFBNapaka4 | DIGITAL | IOD_STR_TCP | 942 | 00942 | VklopSCFBNapaka[4]
STRVklopSCFBNapaka5 | DIGITAL | IOD_STR_TCP | 943 | 00943 | VklopSCFBNapaka[5]
STRVklopSCFBNapaka6 | DIGITAL | IOD_STR_TCP | 944 | 00944 | VklopSCFBNapaka[6]
STRVklopSCFBNapaka7 | DIGITAL | IOD_STR_TCP | 945 | 00945 | VklopSCFBNapaka[7]
STRVklopSCFBNapaka8 | DIGITAL | IOD_STR_TCP | 946 | 00946 | VklopSCFBNapaka[8]
STRVklopSCFBNapaka9 | DIGITAL | IOD_STR_TCP | 947 | 00947 | VklopSCFBNapaka[9]
STRXVH_AlarmOn | DIGITAL | IOD_STR_TCP | 948 | 00948 | XVH_AlarmOn
STRXVH_IzklopVsehLuci | DIGITAL | IOD_STR_TCP | 949 | 00949 | XVH_IzklopVsehLuci
STRXVH_VklopVsehLuci | DIGITAL | IOD_STR_TCP | 950 | 00950 | XVH_VklopVsehLuci
STRPrenasanjeUrnikovAktivno | DIGITAL | IOD_STR_TCP | 951 | 00951 | PrenasanjeUrnikovAktivno
STRPrenasanjeUrnikovAktivno1 | DIGITAL | IOD_STR_TCP | 952 | 00952 | PrenasanjeUrnikovAktivno1
STRCrpalkeGrfsGalAlarmAktiven | DIGITAL | IOD_STR_TCP | 953 | 00953 | CrpalkeGrfsGal.AlarmAktiven
STRCrpalkeGrfsGalDeluje | DIGITAL | IOD_STR_TCP | 954 | 00954 | CrpalkeGrfsGal.Deluje
STRCrpalkeGrfsGalLocalMode | DIGITAL | IOD_STR_TCP | 955 | 00955 | CrpalkeGrfsGal.LocalMode
STRCrpalkeGrfsGalRemoteON | DIGITAL | IOD_STR_TCP | 956 | 00956 | CrpalkeGrfsGal.RemoteON
STRCrpalkeGrfsGalReset2handkWhValues | DIGITAL | IOD_STR_TCP | 957 | 00957 | CrpalkeGrfsGal.Reset2handkWhValues
STRCrpalkeGrfsGalResetAlarm | DIGITAL | IOD_STR_TCP | 958 | 00958 | CrpalkeGrfsGal.ResetAlarm
STRCrpalkeGrfsGalResetAlarmLog | DIGITAL | IOD_STR_TCP | 959 | 00959 | CrpalkeGrfsGal.ResetAlarmLog
STRCrpalkeGrfsGalResetDevice | DIGITAL | IOD_STR_TCP | 960 | 00960 | CrpalkeGrfsGal.ResetDevice
STRCrpalkeGrfsGalSetAutomatic | DIGITAL | IOD_STR_TCP | 961 | 00961 | CrpalkeGrfsGal.SetAutomatic
STRCrpalkeGrfsGalSetConstFreqMode | DIGITAL | IOD_STR_TCP | 962 | 00962 | CrpalkeGrfsGal.SetConstFreqMode
STRCrpalkeGrfsGalSetConstPress | DIGITAL | IOD_STR_TCP | 963 | 00963 | CrpalkeGrfsGal.SetConstPress
STRCrpalkeGrfsGalSetLocalMode | DIGITAL | IOD_STR_TCP | 964 | 00964 | CrpalkeGrfsGal.SetLocalMode
STRCrpalkeGrfsGalSetMaxRunMode | DIGITAL | IOD_STR_TCP | 965 | 00965 | CrpalkeGrfsGal.SetMaxRunMode
STRCrpalkeGrfsGalSetMinRunMode | DIGITAL | IOD_STR_TCP | 966 | 00966 | CrpalkeGrfsGal.SetMinRunMode
STRCrpalkeGrfsGalSetPropPress | DIGITAL | IOD_STR_TCP | 967 | 00967 | CrpalkeGrfsGal.SetPropPress
STRCrpalkeGrfsGalSetReference | DIGITAL | IOD_STR_TCP | 968 | 00968 | CrpalkeGrfsGal.SetReference
STRCrpalkeGrfsGalSetRemoteMode | DIGITAL | IOD_STR_TCP | 969 | 00969 | CrpalkeGrfsGal.SetRemoteMode
STRCrpalkeGrfsGalSetTwinModeAlt | DIGITAL | IOD_STR_TCP | 970 | 00970 | CrpalkeGrfsGal.SetTwinModeAlt
STRCrpalkeGrfsGalSetTwinModeSpare | DIGITAL | IOD_STR_TCP | 971 | 00971 | CrpalkeGrfsGal.SetTwinModeSpare
STRCrpalkeGrfsGalSetTwinModeSync | DIGITAL | IOD_STR_TCP | 972 | 00972 | CrpalkeGrfsGal.SetTwinModeSync
STRCrpalkeGrfsGalStart | DIGITAL | IOD_STR_TCP | 973 | 00973 | CrpalkeGrfsGal.Start
STRCrpalkeGrfsGalStop | DIGITAL | IOD_STR_TCP | 974 | 00974 | CrpalkeGrfsGal.Stop
STRDI_rezerva10_2 | DIGITAL | IOD_STR_TCP | 975 | 00975 | DI_rezerva10_2
STRDI_rezerva10_7 | DIGITAL | IOD_STR_TCP | 976 | 00976 | DI_rezerva10_7
STRDI_rezerva11_4 | DIGITAL | IOD_STR_TCP | 977 | 00977 | DI_rezerva11_4
STRDI_rezerva14_0 | DIGITAL | IOD_STR_TCP | 978 | 00978 | DI_rezerva14_0
STRDI_rezerva14_2 | DIGITAL | IOD_STR_TCP | 979 | 00979 | DI_rezerva14_2
STRDI_rezerva14_3 | DIGITAL | IOD_STR_TCP | 980 | 00980 | DI_rezerva14_3
STRDI_rezerva14_4 | DIGITAL | IOD_STR_TCP | 981 | 00981 | DI_rezerva14_4
STRDI_rezerva14_5 | DIGITAL | IOD_STR_TCP | 982 | 00982 | DI_rezerva14_5
STRDI_rezerva14_7 | DIGITAL | IOD_STR_TCP | 983 | 00983 | DI_rezerva14_7
STRDI_rezerva2_4 | DIGITAL | IOD_STR_TCP | 984 | 00984 | DI_rezerva2_4
STRDI_rezerva3_5 | DIGITAL | IOD_STR_TCP | 985 | 00985 | DI_rezerva3_5
STRDIN_AkumTopVodeAUTO | DIGITAL | IOD_STR_TCP | 986 | 00986 | DIN_AkumTopVodeAUTO
STRDIN_CrpHM1AUTO | DIGITAL | IOD_STR_TCP | 987 | 00987 | DIN_CrpHM1AUTO
STRDIN_CrpHM1kontON | DIGITAL | IOD_STR_TCP | 988 | 00988 | DIN_CrpHM1kontON
STRDIN_CrpHM2AUTO | DIGITAL | IOD_STR_TCP | 989 | 00989 | DIN_CrpHM2AUTO
STRDIN_CrpHM2kontON | DIGITAL | IOD_STR_TCP | 990 | 00990 | DIN_CrpHM2kontON
STRDIN_CrpHM3AUTO | DIGITAL | IOD_STR_TCP | 991 | 00991 | DIN_CrpHM3AUTO
STRDIN_CrpHM3kontON | DIGITAL | IOD_STR_TCP | 992 | 00992 | DIN_CrpHM3kontON
STRDIN_CrpHM4AUTO | DIGITAL | IOD_STR_TCP | 993 | 00993 | DIN_CrpHM4AUTO
STRDIN_CrpHM4kontON | DIGITAL | IOD_STR_TCP | 994 | 00994 | DIN_CrpHM4kontON
STRDIN_CrpHM5AUTO | DIGITAL | IOD_STR_TCP | 995 | 00995 | DIN_CrpHM5AUTO
STRDIN_CrpHM6AUTO | DIGITAL | IOD_STR_TCP | 996 | 00996 | DIN_CrpHM6AUTO
STRDIN_CrpHM7AUTO | DIGITAL | IOD_STR_TCP | 997 | 00997 | DIN_CrpHM7AUTO
STRDIN_CrpHM8AUTO | DIGITAL | IOD_STR_TCP | 998 | 00998 | DIN_CrpHM8AUTO
STRDIN_CrpMN1AUTO | DIGITAL | IOD_STR_TCP | 999 | 00999 | DIN_CrpMN1AUTO
STRDIN_CrpMN1kontON | DIGITAL | IOD_STR_TCP | 1000 | 01000 | DIN_CrpMN1kontON
STRDIN_CrpTM10AUTO | DIGITAL | IOD_STR_TCP | 1001 | 01001 | DIN_CrpTM10AUTO
STRDIN_CrpTM11TM12AUTO | DIGITAL | IOD_STR_TCP | 1002 | 01002 | DIN_CrpTM11TM12AUTO
STRDIN_CrpTM11TM12kontON | DIGITAL | IOD_STR_TCP | 1003 | 01003 | DIN_CrpTM11TM12kontON
STRDIN_CrpTM1AUTO | DIGITAL | IOD_STR_TCP | 1004 | 01004 | DIN_CrpTM1AUTO
STRDIN_CrpTM2AUTO | DIGITAL | IOD_STR_TCP | 1005 | 01005 | DIN_CrpTM2AUTO
STRDIN_CrpTM3AUTO | DIGITAL | IOD_STR_TCP | 1006 | 01006 | DIN_CrpTM3AUTO
STRDIN_CrpTM4AUTO | DIGITAL | IOD_STR_TCP | 1007 | 01007 | DIN_CrpTM4AUTO
STRDIN_CrpTM5AUTO | DIGITAL | IOD_STR_TCP | 1008 | 01008 | DIN_CrpTM5AUTO
STRDIN_CrpTM6AUTO | DIGITAL | IOD_STR_TCP | 1009 | 01009 | DIN_CrpTM6AUTO
STRDIN_CrpTM7AUTO | DIGITAL | IOD_STR_TCP | 1010 | 01010 | DIN_CrpTM7AUTO
STRDIN_CrpTM8AUTO | DIGITAL | IOD_STR_TCP | 1011 | 01011 | DIN_CrpTM8AUTO
STRDIN_CrpTM9AUTO | DIGITAL | IOD_STR_TCP | 1012 | 01012 | DIN_CrpTM9AUTO
STRDIN_GlStikaloDieselON | DIGITAL | IOD_STR_TCP | 1013 | 01013 | DIN_GlStikaloDieselON
STRDIN_GlStikaloMrezaON | DIGITAL | IOD_STR_TCP | 1014 | 01014 | DIN_GlStikaloMrezaON
STRDIN_GlStikaloUpsON | DIGITAL | IOD_STR_TCP | 1015 | 01015 | DIN_GlStikaloUpsON
STRDIN_HladStAUTO | DIGITAL | IOD_STR_TCP | 1016 | 01016 | DIN_HladStAUTO
STRDIN_Kond1AUTO | DIGITAL | IOD_STR_TCP | 1017 | 01017 | DIN_Kond1AUTO
STRDIN_Kond2AUTO | DIGITAL | IOD_STR_TCP | 1018 | 01018 | DIN_Kond2AUTO
STRDIN_Kond3AUTO | DIGITAL | IOD_STR_TCP | 1019 | 01019 | DIN_Kond3AUTO
STRDIN_Vent1Auto | DIGITAL | IOD_STR_TCP | 1020 | 01020 | DIN_Vent1Auto
STRDIN_Vent1kontON | DIGITAL | IOD_STR_TCP | 1021 | 01021 | DIN_Vent1kontON
STRDIN_Vent2Auto | DIGITAL | IOD_STR_TCP | 1022 | 01022 | DIN_Vent2Auto
STRDIN_Vent2kontON | DIGITAL | IOD_STR_TCP | 1023 | 01023 | DIN_Vent2kontON
STRDIN_Vent3Auto | DIGITAL | IOD_STR_TCP | 1024 | 01024 | DIN_Vent3Auto
STRDIN_Vent3kontON | DIGITAL | IOD_STR_TCP | 1025 | 01025 | DIN_Vent3kontON
STRDIN_Vent4Auto | DIGITAL | IOD_STR_TCP | 1026 | 01026 | DIN_Vent4Auto
STRDIN_Vent4kontON | DIGITAL | IOD_STR_TCP | 1027 | 01027 | DIN_Vent4kontON
STRDIN_Vent5Auto | DIGITAL | IOD_STR_TCP | 1028 | 01028 | DIN_Vent5Auto
STRDIN_Vent5kontON | DIGITAL | IOD_STR_TCP | 1029 | 01029 | DIN_Vent5kontON
STRDIN_Vent6Auto | DIGITAL | IOD_STR_TCP | 1030 | 01030 | DIN_Vent6Auto
STRDIN_Vent6kontON | DIGITAL | IOD_STR_TCP | 1031 | 01031 | DIN_Vent6kontON
STRDO_rezerva0_2 | DIGITAL | IOD_STR_TCP | 1032 | 01032 | DO_rezerva0_2
STRDO_rezerva0_3 | DIGITAL | IOD_STR_TCP | 1033 | 01033 | DO_rezerva0_3
STRDO_rezerva0_4 | DIGITAL | IOD_STR_TCP | 1034 | 01034 | DO_rezerva0_4
STRDO_rezerva0_5 | DIGITAL | IOD_STR_TCP | 1035 | 01035 | DO_rezerva0_5
STRDO_rezerva1_3 | DIGITAL | IOD_STR_TCP | 1036 | 01036 | DO_rezerva1_3
STRDO_rezerva1_4 | DIGITAL | IOD_STR_TCP | 1037 | 01037 | DO_rezerva1_4
STRDO_rezerva1_5 | DIGITAL | IOD_STR_TCP | 1038 | 01038 | DO_rezerva1_5
STRDO_rezerva3_4 | DIGITAL | IOD_STR_TCP | 1039 | 01039 | DO_rezerva3_4
STRDO_rezerva3_6 | DIGITAL | IOD_STR_TCP | 1040 | 01040 | DO_rezerva3_6
STRDO_rezerva4_0 | DIGITAL | IOD_STR_TCP | 1041 | 01041 | DO_rezerva4_0
STRPrenosUrnika26 | DIGITAL | IOD_STR_TCP | 1042 | 01042 | PrenosUrnika[26]
STRPrenosUrnika27 | DIGITAL | IOD_STR_TCP | 1043 | 01043 | PrenosUrnika[27]
STRPrenosUrnika28 | DIGITAL | IOD_STR_TCP | 1044 | 01044 | PrenosUrnika[28]
STRPrenosUrnika29 | DIGITAL | IOD_STR_TCP | 1045 | 01045 | PrenosUrnika[29]
STRPrenosUrnika30 | DIGITAL | IOD_STR_TCP | 1046 | 01046 | PrenosUrnika[30]
STRPrenosUrnika31 | DIGITAL | IOD_STR_TCP | 1047 | 01047 | PrenosUrnika[31]
STRPrenosUrnika32 | DIGITAL | IOD_STR_TCP | 1048 | 01048 | PrenosUrnika[32]
STRPrenosUrnika33 | DIGITAL | IOD_STR_TCP | 1049 | 01049 | PrenosUrnika[33]
STRPrenosUrnika34 | DIGITAL | IOD_STR_TCP | 1050 | 01050 | PrenosUrnika[34]
STRPrenosUrnika35 | DIGITAL | IOD_STR_TCP | 1051 | 01051 | PrenosUrnika[35]
STRPrenosUrnika36 | DIGITAL | IOD_STR_TCP | 1052 | 01052 | PrenosUrnika[36]
STRPrenosUrnika37 | DIGITAL | IOD_STR_TCP | 1053 | 01053 | PrenosUrnika[37]
STRPrenosUrnika38 | DIGITAL | IOD_STR_TCP | 1054 | 01054 | PrenosUrnika[38]
STRPrenosUrnika39 | DIGITAL | IOD_STR_TCP | 1055 | 01055 | PrenosUrnika[39]
STRPrenosUrnika40 | DIGITAL | IOD_STR_TCP | 1056 | 01056 | PrenosUrnika[40]
STRPrenosUrnika41 | DIGITAL | IOD_STR_TCP | 1057 | 01057 | PrenosUrnika[41]
STRPrenosUrnika42 | DIGITAL | IOD_STR_TCP | 1058 | 01058 | PrenosUrnika[42]
STRPrenosUrnika43 | DIGITAL | IOD_STR_TCP | 1059 | 01059 | PrenosUrnika[43]
STRPrenosUrnika44 | DIGITAL | IOD_STR_TCP | 1060 | 01060 | PrenosUrnika[44]
STRPrenosUrnika45 | DIGITAL | IOD_STR_TCP | 1061 | 01061 | PrenosUrnika[45]
STRPrenosUrnika46 | DIGITAL | IOD_STR_TCP | 1062 | 01062 | PrenosUrnika[46]
STRPrenosUrnika47 | DIGITAL | IOD_STR_TCP | 1063 | 01063 | PrenosUrnika[47]
STRPrenosUrnika48 | DIGITAL | IOD_STR_TCP | 1064 | 01064 | PrenosUrnika[48]
STRPrenosUrnika49 | DIGITAL | IOD_STR_TCP | 1065 | 01065 | PrenosUrnika[49]
STRPrenosUrnika50 | DIGITAL | IOD_STR_TCP | 1066 | 01066 | PrenosUrnika[50]
STRPrenosUrnika51 | DIGITAL | IOD_STR_TCP | 1067 | 01067 | PrenosUrnika[51]
STRPrenosUrnika52 | DIGITAL | IOD_STR_TCP | 1068 | 01068 | PrenosUrnika[52]
STRPrenosUrnika53 | DIGITAL | IOD_STR_TCP | 1069 | 01069 | PrenosUrnika[53]
STRPrenosUrnika54 | DIGITAL | IOD_STR_TCP | 1070 | 01070 | PrenosUrnika[54]
STRPrenosUrnika55 | DIGITAL | IOD_STR_TCP | 1071 | 01071 | PrenosUrnika[55]
STRPrenosUrnika56 | DIGITAL | IOD_STR_TCP | 1072 | 01072 | PrenosUrnika[56]
STRPrenosUrnika57 | DIGITAL | IOD_STR_TCP | 1073 | 01073 | PrenosUrnika[57]
STRPrenosUrnika58 | DIGITAL | IOD_STR_TCP | 1074 | 01074 | PrenosUrnika[58]
STRPrenosUrnika59 | DIGITAL | IOD_STR_TCP | 1075 | 01075 | PrenosUrnika[59]
STRPrenosUrnika60 | DIGITAL | IOD_STR_TCP | 1076 | 01076 | PrenosUrnika[60]
STRPrenosUrnika61 | DIGITAL | IOD_STR_TCP | 1077 | 01077 | PrenosUrnika[61]
STRPrenosUrnika62 | DIGITAL | IOD_STR_TCP | 1078 | 01078 | PrenosUrnika[62]
STRPrenosUrnika63 | DIGITAL | IOD_STR_TCP | 1079 | 01079 | PrenosUrnika[63]
STRPrenosUrnika64 | DIGITAL | IOD_STR_TCP | 1080 | 01080 | PrenosUrnika[64]
STRPrenosUrnika65 | DIGITAL | IOD_STR_TCP | 1081 | 01081 | PrenosUrnika[65]
STRPrenosUrnika66 | DIGITAL | IOD_STR_TCP | 1082 | 01082 | PrenosUrnika[66]
STRPrenosUrnika67 | DIGITAL | IOD_STR_TCP | 1083 | 01083 | PrenosUrnika[67]
STRPrenosUrnika68 | DIGITAL | IOD_STR_TCP | 1084 | 01084 | PrenosUrnika[68]
STRPrenosUrnika69 | DIGITAL | IOD_STR_TCP | 1085 | 01085 | PrenosUrnika[69]
STRPrenosUrnika70 | DIGITAL | IOD_STR_TCP | 1086 | 01086 | PrenosUrnika[70]
STRPrenosUrnika71 | DIGITAL | IOD_STR_TCP | 1087 | 01087 | PrenosUrnika[71]
STRPrenosUrnika72 | DIGITAL | IOD_STR_TCP | 1088 | 01088 | PrenosUrnika[72]
STRPrenosUrnika73 | DIGITAL | IOD_STR_TCP | 1089 | 01089 | PrenosUrnika[73]
STRPrenosUrnika74 | DIGITAL | IOD_STR_TCP | 1090 | 01090 | PrenosUrnika[74]
STRPrenosUrnika75 | DIGITAL | IOD_STR_TCP | 1091 | 01091 | PrenosUrnika[75]
STRPrenosUrnika76 | DIGITAL | IOD_STR_TCP | 1092 | 01092 | PrenosUrnika[76]
STRPrenosUrnika77 | DIGITAL | IOD_STR_TCP | 1093 | 01093 | PrenosUrnika[77]
STRPrenosUrnika78 | DIGITAL | IOD_STR_TCP | 1094 | 01094 | PrenosUrnika[78]
STRPrenosUrnika79 | DIGITAL | IOD_STR_TCP | 1095 | 01095 | PrenosUrnika[79]
STRPrenosUrnika80 | DIGITAL | IOD_STR_TCP | 1096 | 01096 | PrenosUrnika[80]
STRPrenosUrnika81 | DIGITAL | IOD_STR_TCP | 1097 | 01097 | PrenosUrnika[81]
STRPrenosUrnika82 | DIGITAL | IOD_STR_TCP | 1098 | 01098 | PrenosUrnika[82]
STRPrenosUrnika83 | DIGITAL | IOD_STR_TCP | 1099 | 01099 | PrenosUrnika[83]
STRPrenosUrnika84 | DIGITAL | IOD_STR_TCP | 1100 | 01100 | PrenosUrnika[84]
STRPrenosUrnika85 | DIGITAL | IOD_STR_TCP | 1101 | 01101 | PrenosUrnika[85]
STRPrenosUrnika86 | DIGITAL | IOD_STR_TCP | 1102 | 01102 | PrenosUrnika[86]
STRPrenosUrnika87 | DIGITAL | IOD_STR_TCP | 1103 | 01103 | PrenosUrnika[87]
STRPrenosUrnika88 | DIGITAL | IOD_STR_TCP | 1104 | 01104 | PrenosUrnika[88]
STRPrenosUrnika89 | DIGITAL | IOD_STR_TCP | 1105 | 01105 | PrenosUrnika[89]
STRPrenosUrnika90 | DIGITAL | IOD_STR_TCP | 1106 | 01106 | PrenosUrnika[90]
STRPrenosUrnika91 | DIGITAL | IOD_STR_TCP | 1107 | 01107 | PrenosUrnika[91]
STRPrenosUrnika92 | DIGITAL | IOD_STR_TCP | 1108 | 01108 | PrenosUrnika[92]
STRPrenosUrnika93 | DIGITAL | IOD_STR_TCP | 1109 | 01109 | PrenosUrnika[93]
STRPrenosUrnika94 | DIGITAL | IOD_STR_TCP | 1110 | 01110 | PrenosUrnika[94]
STRPrenosUrnika95 | DIGITAL | IOD_STR_TCP | 1111 | 01111 | PrenosUrnika[95]
STRPrenosUrnika96 | DIGITAL | IOD_STR_TCP | 1112 | 01112 | PrenosUrnika[96]
STRRazsvRocnoEnaLuc10 | DIGITAL | IOD_STR_TCP | 1113 | 01113 | RazsvRocnoEnaLuc[10]
STRRazsvRocnoEnaLuc11 | DIGITAL | IOD_STR_TCP | 1114 | 01114 | RazsvRocnoEnaLuc[11]
STRRazsvRocnoEnaLuc12 | DIGITAL | IOD_STR_TCP | 1115 | 01115 | RazsvRocnoEnaLuc[12]
STRRazsvRocnoEnaLuc13 | DIGITAL | IOD_STR_TCP | 1116 | 01116 | RazsvRocnoEnaLuc[13]
STRRazsvRocnoEnaLuc14 | DIGITAL | IOD_STR_TCP | 1117 | 01117 | RazsvRocnoEnaLuc[14]
STRRazsvRocnoEnaLuc15 | DIGITAL | IOD_STR_TCP | 1118 | 01118 | RazsvRocnoEnaLuc[15]
STRRazsvRocnoEnaLuc16 | DIGITAL | IOD_STR_TCP | 1119 | 01119 | RazsvRocnoEnaLuc[16]
STRRazsvRocnoEnaLuc17 | DIGITAL | IOD_STR_TCP | 1120 | 01120 | RazsvRocnoEnaLuc[17]
STRRazsvRocnoEnaLuc18 | DIGITAL | IOD_STR_TCP | 1121 | 01121 | RazsvRocnoEnaLuc[18]
STRRazsvRocnoEnaLuc19 | DIGITAL | IOD_STR_TCP | 1122 | 01122 | RazsvRocnoEnaLuc[19]
STRRazsvRocnoEnaLuc1 | DIGITAL | IOD_STR_TCP | 1123 | 01123 | RazsvRocnoEnaLuc[1]
STRRazsvRocnoEnaLuc20 | DIGITAL | IOD_STR_TCP | 1124 | 01124 | RazsvRocnoEnaLuc[20]
STRRazsvRocnoEnaLuc21 | DIGITAL | IOD_STR_TCP | 1125 | 01125 | RazsvRocnoEnaLuc[21]
STRRazsvRocnoEnaLuc22 | DIGITAL | IOD_STR_TCP | 1126 | 01126 | RazsvRocnoEnaLuc[22]
STRRazsvRocnoEnaLuc23 | DIGITAL | IOD_STR_TCP | 1127 | 01127 | RazsvRocnoEnaLuc[23]
STRRazsvRocnoEnaLuc24 | DIGITAL | IOD_STR_TCP | 1128 | 01128 | RazsvRocnoEnaLuc[24]
STRRazsvRocnoEnaLuc25 | DIGITAL | IOD_STR_TCP | 1129 | 01129 | RazsvRocnoEnaLuc[25]
STRRazsvRocnoEnaLuc2 | DIGITAL | IOD_STR_TCP | 1130 | 01130 | RazsvRocnoEnaLuc[2]
STRRazsvRocnoEnaLuc3 | DIGITAL | IOD_STR_TCP | 1131 | 01131 | RazsvRocnoEnaLuc[3]
STRRazsvRocnoEnaLuc4 | DIGITAL | IOD_STR_TCP | 1132 | 01132 | RazsvRocnoEnaLuc[4]
STRRazsvRocnoEnaLuc5 | DIGITAL | IOD_STR_TCP | 1133 | 01133 | RazsvRocnoEnaLuc[5]
STRRazsvRocnoEnaLuc6 | DIGITAL | IOD_STR_TCP | 1134 | 01134 | RazsvRocnoEnaLuc[6]
STRRazsvRocnoEnaLuc7 | DIGITAL | IOD_STR_TCP | 1135 | 01135 | RazsvRocnoEnaLuc[7]
STRRazsvRocnoEnaLuc8 | DIGITAL | IOD_STR_TCP | 1136 | 01136 | RazsvRocnoEnaLuc[8]
STRRazsvRocnoEnaLuc9 | DIGITAL | IOD_STR_TCP | 1137 | 01137 | RazsvRocnoEnaLuc[9]
STRXVH_CrpalkaGrfsPair | DIGITAL | IOD_STR_TCP | 1138 | 01138 | XVH_CrpalkaGrfsPair
STRXVH_CrpGrfsCommErr | DIGITAL | IOD_STR_TCP | 1139 | 01139 | XVH_CrpGrfsCommErr
STRXVH_CrpGrfsON10 | DIGITAL | IOD_STR_TCP | 1140 | 01140 | XVH_CrpGrfsON[10]
STRXVH_CrpGrfsON11 | DIGITAL | IOD_STR_TCP | 1141 | 01141 | XVH_CrpGrfsON[11]
STRXVH_CrpGrfsON12 | DIGITAL | IOD_STR_TCP | 1142 | 01142 | XVH_CrpGrfsON[12]
STRXVH_CrpGrfsON13 | DIGITAL | IOD_STR_TCP | 1143 | 01143 | XVH_CrpGrfsON[13]
STRXVH_CrpGrfsON14 | DIGITAL | IOD_STR_TCP | 1144 | 01144 | XVH_CrpGrfsON[14]
STRXVH_CrpGrfsON1 | DIGITAL | IOD_STR_TCP | 1145 | 01145 | XVH_CrpGrfsON[1]
STRXVH_CrpGrfsON2 | DIGITAL | IOD_STR_TCP | 1146 | 01146 | XVH_CrpGrfsON[2]
STRXVH_CrpGrfsON3 | DIGITAL | IOD_STR_TCP | 1147 | 01147 | XVH_CrpGrfsON[3]
STRXVH_CrpGrfsON4 | DIGITAL | IOD_STR_TCP | 1148 | 01148 | XVH_CrpGrfsON[4]
STRXVH_CrpGrfsON5 | DIGITAL | IOD_STR_TCP | 1149 | 01149 | XVH_CrpGrfsON[5]
STRXVH_CrpGrfsON6 | DIGITAL | IOD_STR_TCP | 1150 | 01150 | XVH_CrpGrfsON[6]
STRXVH_CrpGrfsON7 | DIGITAL | IOD_STR_TCP | 1151 | 01151 | XVH_CrpGrfsON[7]
STRXVH_CrpGrfsON8 | DIGITAL | IOD_STR_TCP | 1152 | 01152 | XVH_CrpGrfsON[8]
STRXVH_CrpGrfsON9 | DIGITAL | IOD_STR_TCP | 1153 | 01153 | XVH_CrpGrfsON[9]
STRXVH_CrpGrfsPIDreset | DIGITAL | IOD_STR_TCP | 1154 | 01154 | XVH_CrpGrfsPIDreset
STRXVH_CrpGrfsVisibleData10 | DIGITAL | IOD_STR_TCP | 1155 | 01155 | XVH_CrpGrfsVisibleData[10]
STRXVH_CrpGrfsVisibleData11 | DIGITAL | IOD_STR_TCP | 1156 | 01156 | XVH_CrpGrfsVisibleData[11]
STRXVH_CrpGrfsVisibleData12 | DIGITAL | IOD_STR_TCP | 1157 | 01157 | XVH_CrpGrfsVisibleData[12]
STRXVH_CrpGrfsVisibleData13 | DIGITAL | IOD_STR_TCP | 1158 | 01158 | XVH_CrpGrfsVisibleData[13]
STRXVH_CrpGrfsVisibleData14 | DIGITAL | IOD_STR_TCP | 1159 | 01159 | XVH_CrpGrfsVisibleData[14]
STRXVH_CrpGrfsVisibleData15 | DIGITAL | IOD_STR_TCP | 1160 | 01160 | XVH_CrpGrfsVisibleData[15]
STRXVH_CrpGrfsVisibleData16 | DIGITAL | IOD_STR_TCP | 1161 | 01161 | XVH_CrpGrfsVisibleData[16]
STRXVH_CrpGrfsVisibleData1 | DIGITAL | IOD_STR_TCP | 1162 | 01162 | XVH_CrpGrfsVisibleData[1]
STRXVH_CrpGrfsVisibleData2 | DIGITAL | IOD_STR_TCP | 1163 | 01163 | XVH_CrpGrfsVisibleData[2]
STRXVH_CrpGrfsVisibleData3 | DIGITAL | IOD_STR_TCP | 1164 | 01164 | XVH_CrpGrfsVisibleData[3]
STRXVH_CrpGrfsVisibleData4 | DIGITAL | IOD_STR_TCP | 1165 | 01165 | XVH_CrpGrfsVisibleData[4]
STRXVH_CrpGrfsVisibleData5 | DIGITAL | IOD_STR_TCP | 1166 | 01166 | XVH_CrpGrfsVisibleData[5]
STRXVH_CrpGrfsVisibleData6 | DIGITAL | IOD_STR_TCP | 1167 | 01167 | XVH_CrpGrfsVisibleData[6]
STRXVH_CrpGrfsVisibleData7 | DIGITAL | IOD_STR_TCP | 1168 | 01168 | XVH_CrpGrfsVisibleData[7]
STRXVH_CrpGrfsVisibleData8 | DIGITAL | IOD_STR_TCP | 1169 | 01169 | XVH_CrpGrfsVisibleData[8]
STRXVH_CrpGrfsVisibleData9 | DIGITAL | IOD_STR_TCP | 1170 | 01170 | XVH_CrpGrfsVisibleData[9]
STRXVH_CrpGrundfosNaCas | DIGITAL | IOD_STR_TCP | 1171 | 01171 | XVH_CrpGrundfosNaCas
STRXVH_CrpGrundfosNaTlak | DIGITAL | IOD_STR_TCP | 1172 | 01172 | XVH_CrpGrundfosNaTlak
STRXVH_CrpGrundfosON | DIGITAL | IOD_STR_TCP | 1173 | 01173 | XVH_CrpGrundfosON
STRXVH_CrpGrundfosResetAlarm | DIGITAL | IOD_STR_TCP | 1174 | 01174 | XVH_CrpGrundfosResetAlarm
STRXVH_CrpGrundfosResetAlarmLog | DIGITAL | IOD_STR_TCP | 1175 | 01175 | XVH_CrpGrundfosResetAlarmLog
STRXVH_CrpGrundfosSetRef | DIGITAL | IOD_STR_TCP | 1176 | 01176 | XVH_CrpGrundfosSetRef
STRXVH_RazsvOnOff | DIGITAL | IOD_STR_TCP | 1177 | 01177 | XVH_RazsvOnOff
STRXVH_setCircNum1 | DIGITAL | IOD_STR_TCP | 1178 | 01178 | XVH_setCircNum[1]
STRXVH_setCircNum2 | DIGITAL | IOD_STR_TCP | 1179 | 01179 | XVH_setCircNum[2]
STRXVH_setCircNum3 | DIGITAL | IOD_STR_TCP | 1180 | 01180 | XVH_setCircNum[3]
STRXVH_setCircNum4 | DIGITAL | IOD_STR_TCP | 1181 | 01181 | XVH_setCircNum[4]
STRXVH_setCircNum5 | DIGITAL | IOD_STR_TCP | 1182 | 01182 | XVH_setCircNum[5]
STRXVH_UrnikNalozi | DIGITAL | IOD_STR_TCP | 1183 | 01183 | XVH_UrnikNalozi
STRXVH_UrnikNonStop | DIGITAL | IOD_STR_TCP | 1184 | 01184 | XVH_UrnikNonStop
STRXVH_UrnikPotrdiVpis | DIGITAL | IOD_STR_TCP | 1185 | 01185 | XVH_UrnikPotrdiVpis
STRXVH_UrnikPreklicVpisa | DIGITAL | IOD_STR_TCP | 1186 | 01186 | XVH_UrnikPreklicVpisa
STRXVH_UrnikShrani | DIGITAL | IOD_STR_TCP | 1187 | 01187 | XVH_UrnikShrani
STRXVH_VpisUrnika | DIGITAL | IOD_STR_TCP | 1188 | 01188 | XVH_VpisUrnika
STRErrCommScada2 | DIGITAL | IOD_STR_TCP | 1189 | 01189 | ErrCommScada2
STRComSCADA2 | DIGITAL | IOD_STR_TCP | 1190 | 01190 | ComSCADA2
STRComSCADA3 | DIGITAL | IOD_STR_TCP | 1191 | 01191 | ComSCADA3
STRCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_STR_TCP | 1192 | 01192 | Circ_Vpis_Dnevne_energija_scada1
STRCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_STR_TCP | 1193 | 01193 | Circ_Vpis_Dnevne_energija_scada2
STRCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_STR_TCP | 1194 | 01194 | Circ_Vpis_Tedenska_energija_scada1
STRCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_STR_TCP | 1195 | 01195 | Circ_Vpis_Tedenska_energija_scada2
STRCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_STR_TCP | 1196 | 01196 | Circ_Vpis_Mesecna_energija_scada1
STRCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_STR_TCP | 1197 | 01197 | Circ_Vpis_Mesecna_energija_scada2
STRCrpalkeDnfs1PreklopkaMode | INT | IOD_STR_TCP | 1 | 40001 | CrpalkeDnfs[1].PreklopkaMode
STRCrpalkeDnfs1StarterStatus0do7 | INT | IOD_STR_TCP | 2 | 40002 | CrpalkeDnfs[1].StarterStatus0do7 | BYTE
STRCrpalkeDnfs1StatusCrpalke | INT | IOD_STR_TCP | 3 | 40003 | CrpalkeDnfs[1].StatusCrpalke | BYTE
STRCrpalkeDnfs1StatusKontaktor | INT | IOD_STR_TCP | 4 | 40004 | CrpalkeDnfs[1].StatusKontaktor
STRCrpalkeDnfs2PreklopkaMode | INT | IOD_STR_TCP | 5 | 40005 | CrpalkeDnfs[2].PreklopkaMode
STRCrpalkeDnfs2StarterStatus0do7 | INT | IOD_STR_TCP | 6 | 40006 | CrpalkeDnfs[2].StarterStatus0do7 | BYTE
STRCrpalkeDnfs2StatusCrpalke | INT | IOD_STR_TCP | 7 | 40007 | CrpalkeDnfs[2].StatusCrpalke | BYTE
STRCrpalkeDnfs2StatusKontaktor | INT | IOD_STR_TCP | 8 | 40008 | CrpalkeDnfs[2].StatusKontaktor
STRCrpalkeDnfs3PreklopkaMode | INT | IOD_STR_TCP | 9 | 40009 | CrpalkeDnfs[3].PreklopkaMode
STRCrpalkeDnfs3StarterStatus0do7 | INT | IOD_STR_TCP | 10 | 40010 | CrpalkeDnfs[3].StarterStatus0do7 | BYTE
STRCrpalkeDnfs3StatusCrpalke | INT | IOD_STR_TCP | 11 | 40011 | CrpalkeDnfs[3].StatusCrpalke | BYTE
STRCrpalkeDnfs3StatusKontaktor | INT | IOD_STR_TCP | 12 | 40012 | CrpalkeDnfs[3].StatusKontaktor
STRCrpalkeDnfs4PreklopkaMode | INT | IOD_STR_TCP | 13 | 40013 | CrpalkeDnfs[4].PreklopkaMode
STRCrpalkeDnfs4StarterStatus0do7 | INT | IOD_STR_TCP | 14 | 40014 | CrpalkeDnfs[4].StarterStatus0do7 | BYTE
STRCrpalkeDnfs4StatusCrpalke | INT | IOD_STR_TCP | 15 | 40015 | CrpalkeDnfs[4].StatusCrpalke | BYTE
STRCrpalkeDnfs4StatusKontaktor | INT | IOD_STR_TCP | 16 | 40016 | CrpalkeDnfs[4].StatusKontaktor
STRCrpalkeGrfs10AlarmActiveCode | INT | IOD_STR_TCP | 17 | 40017 | CrpalkeGrfs[10].AlarmActiveCode
STRCrpalkeGrfs10AlarmCodeLog1 | INT | IOD_STR_TCP | 18 | 40018 | CrpalkeGrfs[10].AlarmCodeLog1
STRCrpalkeGrfs10AlarmCodeLog2 | INT | IOD_STR_TCP | 19 | 40019 | CrpalkeGrfs[10].AlarmCodeLog2
STRCrpalkeGrfs10AlarmCodeLog3 | INT | IOD_STR_TCP | 20 | 40020 | CrpalkeGrfs[10].AlarmCodeLog3
STRCrpalkeGrfs10AlarmCodeLog4 | INT | IOD_STR_TCP | 21 | 40021 | CrpalkeGrfs[10].AlarmCodeLog4
STRCrpalkeGrfs10AlarmCodeLog5 | INT | IOD_STR_TCP | 22 | 40022 | CrpalkeGrfs[10].AlarmCodeLog5
STRCrpalkeGrfs10AlarmGroupXVH0 | INT | IOD_STR_TCP | 23 | 40023 | CrpalkeGrfs[10].AlarmGroupXVH[0]
STRCrpalkeGrfs10AlarmGroupXVH10 | INT | IOD_STR_TCP | 24 | 40024 | CrpalkeGrfs[10].AlarmGroupXVH[10]
STRCrpalkeGrfs10AlarmGroupXVH11 | INT | IOD_STR_TCP | 25 | 40025 | CrpalkeGrfs[10].AlarmGroupXVH[11]
STRCrpalkeGrfs10AlarmGroupXVH12 | INT | IOD_STR_TCP | 26 | 40026 | CrpalkeGrfs[10].AlarmGroupXVH[12]
STRCrpalkeGrfs10AlarmGroupXVH13 | INT | IOD_STR_TCP | 27 | 40027 | CrpalkeGrfs[10].AlarmGroupXVH[13]
STRCrpalkeGrfs10AlarmGroupXVH14 | INT | IOD_STR_TCP | 28 | 40028 | CrpalkeGrfs[10].AlarmGroupXVH[14]
STRCrpalkeGrfs10AlarmGroupXVH15 | INT | IOD_STR_TCP | 29 | 40029 | CrpalkeGrfs[10].AlarmGroupXVH[15]
STRCrpalkeGrfs10AlarmGroupXVH16 | INT | IOD_STR_TCP | 30 | 40030 | CrpalkeGrfs[10].AlarmGroupXVH[16]
STRCrpalkeGrfs10AlarmGroupXVH1 | INT | IOD_STR_TCP | 31 | 40031 | CrpalkeGrfs[10].AlarmGroupXVH[1]
STRCrpalkeGrfs10AlarmGroupXVH2 | INT | IOD_STR_TCP | 32 | 40032 | CrpalkeGrfs[10].AlarmGroupXVH[2]
STRCrpalkeGrfs10AlarmGroupXVH3 | INT | IOD_STR_TCP | 33 | 40033 | CrpalkeGrfs[10].AlarmGroupXVH[3]
STRCrpalkeGrfs10AlarmGroupXVH4 | INT | IOD_STR_TCP | 34 | 40034 | CrpalkeGrfs[10].AlarmGroupXVH[4]
STRCrpalkeGrfs10AlarmGroupXVH5 | INT | IOD_STR_TCP | 35 | 40035 | CrpalkeGrfs[10].AlarmGroupXVH[5]
STRCrpalkeGrfs10AlarmGroupXVH6 | INT | IOD_STR_TCP | 36 | 40036 | CrpalkeGrfs[10].AlarmGroupXVH[6]
STRCrpalkeGrfs10AlarmGroupXVH7 | INT | IOD_STR_TCP | 37 | 40037 | CrpalkeGrfs[10].AlarmGroupXVH[7]
STRCrpalkeGrfs10AlarmGroupXVH8 | INT | IOD_STR_TCP | 38 | 40038 | CrpalkeGrfs[10].AlarmGroupXVH[8]
STRCrpalkeGrfs10AlarmGroupXVH9 | INT | IOD_STR_TCP | 39 | 40039 | CrpalkeGrfs[10].AlarmGroupXVH[9]
STRCrpalkeGrfs10AlarmQSD1 | INT | IOD_STR_TCP | 40 | 40040 | CrpalkeGrfs[10].AlarmQSD1
STRCrpalkeGrfs10AlarmQSD2 | INT | IOD_STR_TCP | 41 | 40041 | CrpalkeGrfs[10].AlarmQSD2
STRCrpalkeGrfs10AlarmStart1 | INT | IOD_STR_TCP | 42 | 40042 | CrpalkeGrfs[10].AlarmStart1
STRCrpalkeGrfs10AlarmStart2 | INT | IOD_STR_TCP | 43 | 40043 | CrpalkeGrfs[10].AlarmStart2
STRCrpalkeGrfs10AlarmStop1 | INT | IOD_STR_TCP | 44 | 40044 | CrpalkeGrfs[10].AlarmStop1
STRCrpalkeGrfs10AlarmStop2 | INT | IOD_STR_TCP | 45 | 40045 | CrpalkeGrfs[10].AlarmStop2
STRCrpalkeGrfs10AlarmStop3 | INT | IOD_STR_TCP | 46 | 40046 | CrpalkeGrfs[10].AlarmStop3
STRCrpalkeGrfs10AlarmSurv1 | INT | IOD_STR_TCP | 47 | 40047 | CrpalkeGrfs[10].AlarmSurv1
STRCrpalkeGrfs10AlarmSurv2 | INT | IOD_STR_TCP | 48 | 40048 | CrpalkeGrfs[10].AlarmSurv2
STRCrpalkeGrfs10ControlSource | INT | IOD_STR_TCP | 49 | 40049 | CrpalkeGrfs[10].ControlSource
STRCrpalkeGrfs10ExternInputSetup | INT | IOD_STR_TCP | 50 | 40050 | CrpalkeGrfs[10].ExternInputSetup
STRCrpalkeGrfs10ExternInputsStatus | INT | IOD_STR_TCP | 51 | 40051 | CrpalkeGrfs[10].ExternInputsStatus
STRCrpalkeGrfs10LocalSetupMode1 | INT | IOD_STR_TCP | 52 | 40052 | CrpalkeGrfs[10].LocalSetupMode1
STRCrpalkeGrfs10PreklopkaMode | INT | IOD_STR_TCP | 53 | 40053 | CrpalkeGrfs[10].PreklopkaMode
STRCrpalkeGrfs10Relay1setup | INT | IOD_STR_TCP | 54 | 40054 | CrpalkeGrfs[10].Relay1setup
STRCrpalkeGrfs10RemoteSetupMode1 | INT | IOD_STR_TCP | 55 | 40055 | CrpalkeGrfs[10].RemoteSetupMode1
STRCrpalkeGrfs10StatusCrpalke | INT | IOD_STR_TCP | 56 | 40056 | CrpalkeGrfs[10].StatusCrpalke | BYTE
STRCrpalkeGrfs10StatusMode1 | INT | IOD_STR_TCP | 57 | 40057 | CrpalkeGrfs[10].StatusMode1
STRCrpalkeGrfs10StatusMode1co | INT | IOD_STR_TCP | 58 | 40058 | CrpalkeGrfs[10].StatusMode1co | BYTE
STRCrpalkeGrfs10StatusMode1op | INT | IOD_STR_TCP | 59 | 40059 | CrpalkeGrfs[10].StatusMode1op | BYTE
STRCrpalkeGrfs10StatusMode2 | INT | IOD_STR_TCP | 60 | 40060 | CrpalkeGrfs[10].StatusMode2
STRCrpalkeGrfs10StatusMode3 | INT | IOD_STR_TCP | 61 | 40061 | CrpalkeGrfs[10].StatusMode3
STRCrpalkeGrfs11AlarmActiveCode | INT | IOD_STR_TCP | 62 | 40062 | CrpalkeGrfs[11].AlarmActiveCode
STRCrpalkeGrfs11AlarmCodeLog1 | INT | IOD_STR_TCP | 63 | 40063 | CrpalkeGrfs[11].AlarmCodeLog1
STRCrpalkeGrfs11AlarmCodeLog2 | INT | IOD_STR_TCP | 64 | 40064 | CrpalkeGrfs[11].AlarmCodeLog2
STRCrpalkeGrfs11AlarmCodeLog3 | INT | IOD_STR_TCP | 65 | 40065 | CrpalkeGrfs[11].AlarmCodeLog3
STRCrpalkeGrfs11AlarmCodeLog4 | INT | IOD_STR_TCP | 66 | 40066 | CrpalkeGrfs[11].AlarmCodeLog4
STRCrpalkeGrfs11AlarmCodeLog5 | INT | IOD_STR_TCP | 67 | 40067 | CrpalkeGrfs[11].AlarmCodeLog5
STRCrpalkeGrfs11AlarmGroupXVH0 | INT | IOD_STR_TCP | 68 | 40068 | CrpalkeGrfs[11].AlarmGroupXVH[0]
STRCrpalkeGrfs11AlarmGroupXVH10 | INT | IOD_STR_TCP | 69 | 40069 | CrpalkeGrfs[11].AlarmGroupXVH[10]
STRCrpalkeGrfs11AlarmGroupXVH11 | INT | IOD_STR_TCP | 70 | 40070 | CrpalkeGrfs[11].AlarmGroupXVH[11]
STRCrpalkeGrfs11AlarmGroupXVH12 | INT | IOD_STR_TCP | 71 | 40071 | CrpalkeGrfs[11].AlarmGroupXVH[12]
STRCrpalkeGrfs11AlarmGroupXVH13 | INT | IOD_STR_TCP | 72 | 40072 | CrpalkeGrfs[11].AlarmGroupXVH[13]
STRCrpalkeGrfs11AlarmGroupXVH14 | INT | IOD_STR_TCP | 73 | 40073 | CrpalkeGrfs[11].AlarmGroupXVH[14]
STRCrpalkeGrfs11AlarmGroupXVH15 | INT | IOD_STR_TCP | 74 | 40074 | CrpalkeGrfs[11].AlarmGroupXVH[15]
STRCrpalkeGrfs11AlarmGroupXVH16 | INT | IOD_STR_TCP | 75 | 40075 | CrpalkeGrfs[11].AlarmGroupXVH[16]
STRCrpalkeGrfs11AlarmGroupXVH1 | INT | IOD_STR_TCP | 76 | 40076 | CrpalkeGrfs[11].AlarmGroupXVH[1]
STRCrpalkeGrfs11AlarmGroupXVH2 | INT | IOD_STR_TCP | 77 | 40077 | CrpalkeGrfs[11].AlarmGroupXVH[2]
STRCrpalkeGrfs11AlarmGroupXVH3 | INT | IOD_STR_TCP | 78 | 40078 | CrpalkeGrfs[11].AlarmGroupXVH[3]
STRCrpalkeGrfs11AlarmGroupXVH4 | INT | IOD_STR_TCP | 79 | 40079 | CrpalkeGrfs[11].AlarmGroupXVH[4]
STRCrpalkeGrfs11AlarmGroupXVH5 | INT | IOD_STR_TCP | 80 | 40080 | CrpalkeGrfs[11].AlarmGroupXVH[5]
STRCrpalkeGrfs11AlarmGroupXVH6 | INT | IOD_STR_TCP | 81 | 40081 | CrpalkeGrfs[11].AlarmGroupXVH[6]
STRCrpalkeGrfs11AlarmGroupXVH7 | INT | IOD_STR_TCP | 82 | 40082 | CrpalkeGrfs[11].AlarmGroupXVH[7]
STRCrpalkeGrfs11AlarmGroupXVH8 | INT | IOD_STR_TCP | 83 | 40083 | CrpalkeGrfs[11].AlarmGroupXVH[8]
STRCrpalkeGrfs11AlarmGroupXVH9 | INT | IOD_STR_TCP | 84 | 40084 | CrpalkeGrfs[11].AlarmGroupXVH[9]
STRCrpalkeGrfs11AlarmQSD1 | INT | IOD_STR_TCP | 85 | 40085 | CrpalkeGrfs[11].AlarmQSD1
STRCrpalkeGrfs11AlarmQSD2 | INT | IOD_STR_TCP | 86 | 40086 | CrpalkeGrfs[11].AlarmQSD2
STRCrpalkeGrfs11AlarmStart1 | INT | IOD_STR_TCP | 87 | 40087 | CrpalkeGrfs[11].AlarmStart1
STRCrpalkeGrfs11AlarmStart2 | INT | IOD_STR_TCP | 88 | 40088 | CrpalkeGrfs[11].AlarmStart2
STRCrpalkeGrfs11AlarmStop1 | INT | IOD_STR_TCP | 89 | 40089 | CrpalkeGrfs[11].AlarmStop1
STRCrpalkeGrfs11AlarmStop2 | INT | IOD_STR_TCP | 90 | 40090 | CrpalkeGrfs[11].AlarmStop2
STRCrpalkeGrfs11AlarmStop3 | INT | IOD_STR_TCP | 91 | 40091 | CrpalkeGrfs[11].AlarmStop3
STRCrpalkeGrfs11AlarmSurv1 | INT | IOD_STR_TCP | 92 | 40092 | CrpalkeGrfs[11].AlarmSurv1
STRCrpalkeGrfs11AlarmSurv2 | INT | IOD_STR_TCP | 93 | 40093 | CrpalkeGrfs[11].AlarmSurv2
STRCrpalkeGrfs11ControlSource | INT | IOD_STR_TCP | 94 | 40094 | CrpalkeGrfs[11].ControlSource
STRCrpalkeGrfs11ExternInputSetup | INT | IOD_STR_TCP | 95 | 40095 | CrpalkeGrfs[11].ExternInputSetup
STRCrpalkeGrfs11ExternInputsStatus | INT | IOD_STR_TCP | 96 | 40096 | CrpalkeGrfs[11].ExternInputsStatus
STRCrpalkeGrfs11LocalSetupMode1 | INT | IOD_STR_TCP | 97 | 40097 | CrpalkeGrfs[11].LocalSetupMode1
STRCrpalkeGrfs11PreklopkaMode | INT | IOD_STR_TCP | 98 | 40098 | CrpalkeGrfs[11].PreklopkaMode
STRCrpalkeGrfs11Relay1setup | INT | IOD_STR_TCP | 99 | 40099 | CrpalkeGrfs[11].Relay1setup
STRCrpalkeGrfs11RemoteSetupMode1 | INT | IOD_STR_TCP | 100 | 40100 | CrpalkeGrfs[11].RemoteSetupMode1
STRCrpalkeGrfs11StatusCrpalke | INT | IOD_STR_TCP | 101 | 40101 | CrpalkeGrfs[11].StatusCrpalke | BYTE
STRCrpalkeGrfs11StatusMode1 | INT | IOD_STR_TCP | 102 | 40102 | CrpalkeGrfs[11].StatusMode1
STRCrpalkeGrfs11StatusMode1co | INT | IOD_STR_TCP | 103 | 40103 | CrpalkeGrfs[11].StatusMode1co | BYTE
STRCrpalkeGrfs11StatusMode1op | INT | IOD_STR_TCP | 104 | 40104 | CrpalkeGrfs[11].StatusMode1op | BYTE
STRCrpalkeGrfs11StatusMode2 | INT | IOD_STR_TCP | 105 | 40105 | CrpalkeGrfs[11].StatusMode2
STRCrpalkeGrfs11StatusMode3 | INT | IOD_STR_TCP | 106 | 40106 | CrpalkeGrfs[11].StatusMode3
STRCrpalkeGrfs12AlarmActiveCode | INT | IOD_STR_TCP | 107 | 40107 | CrpalkeGrfs[12].AlarmActiveCode
STRCrpalkeGrfs12AlarmCodeLog1 | INT | IOD_STR_TCP | 108 | 40108 | CrpalkeGrfs[12].AlarmCodeLog1
STRCrpalkeGrfs12AlarmCodeLog2 | INT | IOD_STR_TCP | 109 | 40109 | CrpalkeGrfs[12].AlarmCodeLog2
STRCrpalkeGrfs12AlarmCodeLog3 | INT | IOD_STR_TCP | 110 | 40110 | CrpalkeGrfs[12].AlarmCodeLog3
STRCrpalkeGrfs12AlarmCodeLog4 | INT | IOD_STR_TCP | 111 | 40111 | CrpalkeGrfs[12].AlarmCodeLog4
STRCrpalkeGrfs12AlarmCodeLog5 | INT | IOD_STR_TCP | 112 | 40112 | CrpalkeGrfs[12].AlarmCodeLog5
STRCrpalkeGrfs12AlarmGroupXVH0 | INT | IOD_STR_TCP | 113 | 40113 | CrpalkeGrfs[12].AlarmGroupXVH[0]
STRCrpalkeGrfs12AlarmGroupXVH10 | INT | IOD_STR_TCP | 114 | 40114 | CrpalkeGrfs[12].AlarmGroupXVH[10]
STRCrpalkeGrfs12AlarmGroupXVH11 | INT | IOD_STR_TCP | 115 | 40115 | CrpalkeGrfs[12].AlarmGroupXVH[11]
STRCrpalkeGrfs12AlarmGroupXVH12 | INT | IOD_STR_TCP | 116 | 40116 | CrpalkeGrfs[12].AlarmGroupXVH[12]
STRCrpalkeGrfs12AlarmGroupXVH13 | INT | IOD_STR_TCP | 117 | 40117 | CrpalkeGrfs[12].AlarmGroupXVH[13]
STRCrpalkeGrfs12AlarmGroupXVH14 | INT | IOD_STR_TCP | 118 | 40118 | CrpalkeGrfs[12].AlarmGroupXVH[14]
STRCrpalkeGrfs12AlarmGroupXVH15 | INT | IOD_STR_TCP | 119 | 40119 | CrpalkeGrfs[12].AlarmGroupXVH[15]
STRCrpalkeGrfs12AlarmGroupXVH16 | INT | IOD_STR_TCP | 120 | 40120 | CrpalkeGrfs[12].AlarmGroupXVH[16]
STRCrpalkeGrfs12AlarmGroupXVH1 | INT | IOD_STR_TCP | 121 | 40121 | CrpalkeGrfs[12].AlarmGroupXVH[1]
STRCrpalkeGrfs12AlarmGroupXVH2 | INT | IOD_STR_TCP | 122 | 40122 | CrpalkeGrfs[12].AlarmGroupXVH[2]
STRCrpalkeGrfs12AlarmGroupXVH3 | INT | IOD_STR_TCP | 123 | 40123 | CrpalkeGrfs[12].AlarmGroupXVH[3]
STRCrpalkeGrfs12AlarmGroupXVH4 | INT | IOD_STR_TCP | 124 | 40124 | CrpalkeGrfs[12].AlarmGroupXVH[4]
STRCrpalkeGrfs12AlarmGroupXVH5 | INT | IOD_STR_TCP | 125 | 40125 | CrpalkeGrfs[12].AlarmGroupXVH[5]
STRCrpalkeGrfs12AlarmGroupXVH6 | INT | IOD_STR_TCP | 126 | 40126 | CrpalkeGrfs[12].AlarmGroupXVH[6]
STRCrpalkeGrfs12AlarmGroupXVH7 | INT | IOD_STR_TCP | 127 | 40127 | CrpalkeGrfs[12].AlarmGroupXVH[7]
STRCrpalkeGrfs12AlarmGroupXVH8 | INT | IOD_STR_TCP | 128 | 40128 | CrpalkeGrfs[12].AlarmGroupXVH[8]
STRCrpalkeGrfs12AlarmGroupXVH9 | INT | IOD_STR_TCP | 129 | 40129 | CrpalkeGrfs[12].AlarmGroupXVH[9]
STRCrpalkeGrfs12AlarmQSD1 | INT | IOD_STR_TCP | 130 | 40130 | CrpalkeGrfs[12].AlarmQSD1
STRCrpalkeGrfs12AlarmQSD2 | INT | IOD_STR_TCP | 131 | 40131 | CrpalkeGrfs[12].AlarmQSD2
STRCrpalkeGrfs12AlarmStart1 | INT | IOD_STR_TCP | 132 | 40132 | CrpalkeGrfs[12].AlarmStart1
STRCrpalkeGrfs12AlarmStart2 | INT | IOD_STR_TCP | 133 | 40133 | CrpalkeGrfs[12].AlarmStart2
STRCrpalkeGrfs12AlarmStop1 | INT | IOD_STR_TCP | 134 | 40134 | CrpalkeGrfs[12].AlarmStop1
STRCrpalkeGrfs12AlarmStop2 | INT | IOD_STR_TCP | 135 | 40135 | CrpalkeGrfs[12].AlarmStop2
STRCrpalkeGrfs12AlarmStop3 | INT | IOD_STR_TCP | 136 | 40136 | CrpalkeGrfs[12].AlarmStop3
STRCrpalkeGrfs12AlarmSurv1 | INT | IOD_STR_TCP | 137 | 40137 | CrpalkeGrfs[12].AlarmSurv1
STRCrpalkeGrfs12AlarmSurv2 | INT | IOD_STR_TCP | 138 | 40138 | CrpalkeGrfs[12].AlarmSurv2
STRCrpalkeGrfs12ControlSource | INT | IOD_STR_TCP | 139 | 40139 | CrpalkeGrfs[12].ControlSource
STRCrpalkeGrfs12ExternInputSetup | INT | IOD_STR_TCP | 140 | 40140 | CrpalkeGrfs[12].ExternInputSetup
STRCrpalkeGrfs12ExternInputsStatus | INT | IOD_STR_TCP | 141 | 40141 | CrpalkeGrfs[12].ExternInputsStatus
STRCrpalkeGrfs12LocalSetupMode1 | INT | IOD_STR_TCP | 142 | 40142 | CrpalkeGrfs[12].LocalSetupMode1
STRCrpalkeGrfs12PreklopkaMode | INT | IOD_STR_TCP | 143 | 40143 | CrpalkeGrfs[12].PreklopkaMode
STRCrpalkeGrfs12Relay1setup | INT | IOD_STR_TCP | 144 | 40144 | CrpalkeGrfs[12].Relay1setup
STRCrpalkeGrfs12RemoteSetupMode1 | INT | IOD_STR_TCP | 145 | 40145 | CrpalkeGrfs[12].RemoteSetupMode1
STRCrpalkeGrfs12StatusCrpalke | INT | IOD_STR_TCP | 146 | 40146 | CrpalkeGrfs[12].StatusCrpalke | BYTE
STRCrpalkeGrfs12StatusMode1 | INT | IOD_STR_TCP | 147 | 40147 | CrpalkeGrfs[12].StatusMode1
STRCrpalkeGrfs12StatusMode1co | INT | IOD_STR_TCP | 148 | 40148 | CrpalkeGrfs[12].StatusMode1co | BYTE
STRCrpalkeGrfs12StatusMode1op | INT | IOD_STR_TCP | 149 | 40149 | CrpalkeGrfs[12].StatusMode1op | BYTE
STRCrpalkeGrfs12StatusMode2 | INT | IOD_STR_TCP | 150 | 40150 | CrpalkeGrfs[12].StatusMode2
STRCrpalkeGrfs12StatusMode3 | INT | IOD_STR_TCP | 151 | 40151 | CrpalkeGrfs[12].StatusMode3
STRCrpalkeGrfs13AlarmActiveCode | INT | IOD_STR_TCP | 152 | 40152 | CrpalkeGrfs[13].AlarmActiveCode
STRCrpalkeGrfs13AlarmCodeLog1 | INT | IOD_STR_TCP | 153 | 40153 | CrpalkeGrfs[13].AlarmCodeLog1
STRCrpalkeGrfs13AlarmCodeLog2 | INT | IOD_STR_TCP | 154 | 40154 | CrpalkeGrfs[13].AlarmCodeLog2
STRCrpalkeGrfs13AlarmCodeLog3 | INT | IOD_STR_TCP | 155 | 40155 | CrpalkeGrfs[13].AlarmCodeLog3
STRCrpalkeGrfs13AlarmCodeLog4 | INT | IOD_STR_TCP | 156 | 40156 | CrpalkeGrfs[13].AlarmCodeLog4
STRCrpalkeGrfs13AlarmCodeLog5 | INT | IOD_STR_TCP | 157 | 40157 | CrpalkeGrfs[13].AlarmCodeLog5
STRCrpalkeGrfs13AlarmGroupXVH0 | INT | IOD_STR_TCP | 158 | 40158 | CrpalkeGrfs[13].AlarmGroupXVH[0]
STRCrpalkeGrfs13AlarmGroupXVH10 | INT | IOD_STR_TCP | 159 | 40159 | CrpalkeGrfs[13].AlarmGroupXVH[10]
STRCrpalkeGrfs13AlarmGroupXVH11 | INT | IOD_STR_TCP | 160 | 40160 | CrpalkeGrfs[13].AlarmGroupXVH[11]
STRCrpalkeGrfs13AlarmGroupXVH12 | INT | IOD_STR_TCP | 161 | 40161 | CrpalkeGrfs[13].AlarmGroupXVH[12]
STRCrpalkeGrfs13AlarmGroupXVH13 | INT | IOD_STR_TCP | 162 | 40162 | CrpalkeGrfs[13].AlarmGroupXVH[13]
STRCrpalkeGrfs13AlarmGroupXVH14 | INT | IOD_STR_TCP | 163 | 40163 | CrpalkeGrfs[13].AlarmGroupXVH[14]
STRCrpalkeGrfs13AlarmGroupXVH15 | INT | IOD_STR_TCP | 164 | 40164 | CrpalkeGrfs[13].AlarmGroupXVH[15]
STRCrpalkeGrfs13AlarmGroupXVH16 | INT | IOD_STR_TCP | 165 | 40165 | CrpalkeGrfs[13].AlarmGroupXVH[16]
STRCrpalkeGrfs13AlarmGroupXVH1 | INT | IOD_STR_TCP | 166 | 40166 | CrpalkeGrfs[13].AlarmGroupXVH[1]
STRCrpalkeGrfs13AlarmGroupXVH2 | INT | IOD_STR_TCP | 167 | 40167 | CrpalkeGrfs[13].AlarmGroupXVH[2]
STRCrpalkeGrfs13AlarmGroupXVH3 | INT | IOD_STR_TCP | 168 | 40168 | CrpalkeGrfs[13].AlarmGroupXVH[3]
STRCrpalkeGrfs13AlarmGroupXVH4 | INT | IOD_STR_TCP | 169 | 40169 | CrpalkeGrfs[13].AlarmGroupXVH[4]
STRCrpalkeGrfs13AlarmGroupXVH5 | INT | IOD_STR_TCP | 170 | 40170 | CrpalkeGrfs[13].AlarmGroupXVH[5]
STRCrpalkeGrfs13AlarmGroupXVH6 | INT | IOD_STR_TCP | 171 | 40171 | CrpalkeGrfs[13].AlarmGroupXVH[6]
STRCrpalkeGrfs13AlarmGroupXVH7 | INT | IOD_STR_TCP | 172 | 40172 | CrpalkeGrfs[13].AlarmGroupXVH[7]
STRCrpalkeGrfs13AlarmGroupXVH8 | INT | IOD_STR_TCP | 173 | 40173 | CrpalkeGrfs[13].AlarmGroupXVH[8]
STRCrpalkeGrfs13AlarmGroupXVH9 | INT | IOD_STR_TCP | 174 | 40174 | CrpalkeGrfs[13].AlarmGroupXVH[9]
STRCrpalkeGrfs13AlarmQSD1 | INT | IOD_STR_TCP | 175 | 40175 | CrpalkeGrfs[13].AlarmQSD1
STRCrpalkeGrfs13AlarmQSD2 | INT | IOD_STR_TCP | 176 | 40176 | CrpalkeGrfs[13].AlarmQSD2
STRCrpalkeGrfs13AlarmStart1 | INT | IOD_STR_TCP | 177 | 40177 | CrpalkeGrfs[13].AlarmStart1
STRCrpalkeGrfs13AlarmStart2 | INT | IOD_STR_TCP | 178 | 40178 | CrpalkeGrfs[13].AlarmStart2
STRCrpalkeGrfs13AlarmStop1 | INT | IOD_STR_TCP | 179 | 40179 | CrpalkeGrfs[13].AlarmStop1
STRCrpalkeGrfs13AlarmStop2 | INT | IOD_STR_TCP | 180 | 40180 | CrpalkeGrfs[13].AlarmStop2
STRCrpalkeGrfs13AlarmStop3 | INT | IOD_STR_TCP | 181 | 40181 | CrpalkeGrfs[13].AlarmStop3
STRCrpalkeGrfs13AlarmSurv1 | INT | IOD_STR_TCP | 182 | 40182 | CrpalkeGrfs[13].AlarmSurv1
STRCrpalkeGrfs13AlarmSurv2 | INT | IOD_STR_TCP | 183 | 40183 | CrpalkeGrfs[13].AlarmSurv2
STRCrpalkeGrfs13ControlSource | INT | IOD_STR_TCP | 184 | 40184 | CrpalkeGrfs[13].ControlSource
STRCrpalkeGrfs13ExternInputSetup | INT | IOD_STR_TCP | 185 | 40185 | CrpalkeGrfs[13].ExternInputSetup
STRCrpalkeGrfs13ExternInputsStatus | INT | IOD_STR_TCP | 186 | 40186 | CrpalkeGrfs[13].ExternInputsStatus
STRCrpalkeGrfs13LocalSetupMode1 | INT | IOD_STR_TCP | 187 | 40187 | CrpalkeGrfs[13].LocalSetupMode1
STRCrpalkeGrfs13PreklopkaMode | INT | IOD_STR_TCP | 188 | 40188 | CrpalkeGrfs[13].PreklopkaMode
STRCrpalkeGrfs13Relay1setup | INT | IOD_STR_TCP | 189 | 40189 | CrpalkeGrfs[13].Relay1setup
STRCrpalkeGrfs13RemoteSetupMode1 | INT | IOD_STR_TCP | 190 | 40190 | CrpalkeGrfs[13].RemoteSetupMode1
STRCrpalkeGrfs13StatusCrpalke | INT | IOD_STR_TCP | 191 | 40191 | CrpalkeGrfs[13].StatusCrpalke | BYTE
STRCrpalkeGrfs13StatusMode1 | INT | IOD_STR_TCP | 192 | 40192 | CrpalkeGrfs[13].StatusMode1
STRCrpalkeGrfs13StatusMode1co | INT | IOD_STR_TCP | 193 | 40193 | CrpalkeGrfs[13].StatusMode1co | BYTE
STRCrpalkeGrfs13StatusMode1op | INT | IOD_STR_TCP | 194 | 40194 | CrpalkeGrfs[13].StatusMode1op | BYTE
STRCrpalkeGrfs13StatusMode2 | INT | IOD_STR_TCP | 195 | 40195 | CrpalkeGrfs[13].StatusMode2
STRCrpalkeGrfs13StatusMode3 | INT | IOD_STR_TCP | 196 | 40196 | CrpalkeGrfs[13].StatusMode3
STRCrpalkeGrfs14AlarmActiveCode | INT | IOD_STR_TCP | 197 | 40197 | CrpalkeGrfs[14].AlarmActiveCode
STRCrpalkeGrfs14AlarmCodeLog1 | INT | IOD_STR_TCP | 198 | 40198 | CrpalkeGrfs[14].AlarmCodeLog1
STRCrpalkeGrfs14AlarmCodeLog2 | INT | IOD_STR_TCP | 199 | 40199 | CrpalkeGrfs[14].AlarmCodeLog2
STRCrpalkeGrfs14AlarmCodeLog3 | INT | IOD_STR_TCP | 200 | 40200 | CrpalkeGrfs[14].AlarmCodeLog3
STRCrpalkeGrfs14AlarmCodeLog4 | INT | IOD_STR_TCP | 201 | 40201 | CrpalkeGrfs[14].AlarmCodeLog4
STRCrpalkeGrfs14AlarmCodeLog5 | INT | IOD_STR_TCP | 202 | 40202 | CrpalkeGrfs[14].AlarmCodeLog5
STRCrpalkeGrfs14AlarmGroupXVH0 | INT | IOD_STR_TCP | 203 | 40203 | CrpalkeGrfs[14].AlarmGroupXVH[0]
STRCrpalkeGrfs14AlarmGroupXVH10 | INT | IOD_STR_TCP | 204 | 40204 | CrpalkeGrfs[14].AlarmGroupXVH[10]
STRCrpalkeGrfs14AlarmGroupXVH11 | INT | IOD_STR_TCP | 205 | 40205 | CrpalkeGrfs[14].AlarmGroupXVH[11]
STRCrpalkeGrfs14AlarmGroupXVH12 | INT | IOD_STR_TCP | 206 | 40206 | CrpalkeGrfs[14].AlarmGroupXVH[12]
STRCrpalkeGrfs14AlarmGroupXVH13 | INT | IOD_STR_TCP | 207 | 40207 | CrpalkeGrfs[14].AlarmGroupXVH[13]
STRCrpalkeGrfs14AlarmGroupXVH14 | INT | IOD_STR_TCP | 208 | 40208 | CrpalkeGrfs[14].AlarmGroupXVH[14]
STRCrpalkeGrfs14AlarmGroupXVH15 | INT | IOD_STR_TCP | 209 | 40209 | CrpalkeGrfs[14].AlarmGroupXVH[15]
STRCrpalkeGrfs14AlarmGroupXVH16 | INT | IOD_STR_TCP | 210 | 40210 | CrpalkeGrfs[14].AlarmGroupXVH[16]
STRCrpalkeGrfs14AlarmGroupXVH1 | INT | IOD_STR_TCP | 211 | 40211 | CrpalkeGrfs[14].AlarmGroupXVH[1]
STRCrpalkeGrfs14AlarmGroupXVH2 | INT | IOD_STR_TCP | 212 | 40212 | CrpalkeGrfs[14].AlarmGroupXVH[2]
STRCrpalkeGrfs14AlarmGroupXVH3 | INT | IOD_STR_TCP | 213 | 40213 | CrpalkeGrfs[14].AlarmGroupXVH[3]
STRCrpalkeGrfs14AlarmGroupXVH4 | INT | IOD_STR_TCP | 214 | 40214 | CrpalkeGrfs[14].AlarmGroupXVH[4]
STRCrpalkeGrfs14AlarmGroupXVH5 | INT | IOD_STR_TCP | 215 | 40215 | CrpalkeGrfs[14].AlarmGroupXVH[5]
STRCrpalkeGrfs14AlarmGroupXVH6 | INT | IOD_STR_TCP | 216 | 40216 | CrpalkeGrfs[14].AlarmGroupXVH[6]
STRCrpalkeGrfs14AlarmGroupXVH7 | INT | IOD_STR_TCP | 217 | 40217 | CrpalkeGrfs[14].AlarmGroupXVH[7]
STRCrpalkeGrfs14AlarmGroupXVH8 | INT | IOD_STR_TCP | 218 | 40218 | CrpalkeGrfs[14].AlarmGroupXVH[8]
STRCrpalkeGrfs14AlarmGroupXVH9 | INT | IOD_STR_TCP | 219 | 40219 | CrpalkeGrfs[14].AlarmGroupXVH[9]
STRCrpalkeGrfs14AlarmQSD1 | INT | IOD_STR_TCP | 220 | 40220 | CrpalkeGrfs[14].AlarmQSD1
STRCrpalkeGrfs14AlarmQSD2 | INT | IOD_STR_TCP | 221 | 40221 | CrpalkeGrfs[14].AlarmQSD2
STRCrpalkeGrfs14AlarmStart1 | INT | IOD_STR_TCP | 222 | 40222 | CrpalkeGrfs[14].AlarmStart1
STRCrpalkeGrfs14AlarmStart2 | INT | IOD_STR_TCP | 223 | 40223 | CrpalkeGrfs[14].AlarmStart2
STRCrpalkeGrfs14AlarmStop1 | INT | IOD_STR_TCP | 224 | 40224 | CrpalkeGrfs[14].AlarmStop1
STRCrpalkeGrfs14AlarmStop2 | INT | IOD_STR_TCP | 225 | 40225 | CrpalkeGrfs[14].AlarmStop2
STRCrpalkeGrfs14AlarmStop3 | INT | IOD_STR_TCP | 226 | 40226 | CrpalkeGrfs[14].AlarmStop3
STRCrpalkeGrfs14AlarmSurv1 | INT | IOD_STR_TCP | 227 | 40227 | CrpalkeGrfs[14].AlarmSurv1
STRCrpalkeGrfs14AlarmSurv2 | INT | IOD_STR_TCP | 228 | 40228 | CrpalkeGrfs[14].AlarmSurv2
STRCrpalkeGrfs14ControlSource | INT | IOD_STR_TCP | 229 | 40229 | CrpalkeGrfs[14].ControlSource
STRCrpalkeGrfs14ExternInputSetup | INT | IOD_STR_TCP | 230 | 40230 | CrpalkeGrfs[14].ExternInputSetup
STRCrpalkeGrfs14ExternInputsStatus | INT | IOD_STR_TCP | 231 | 40231 | CrpalkeGrfs[14].ExternInputsStatus
STRCrpalkeGrfs14LocalSetupMode1 | INT | IOD_STR_TCP | 232 | 40232 | CrpalkeGrfs[14].LocalSetupMode1
STRCrpalkeGrfs14PreklopkaMode | INT | IOD_STR_TCP | 233 | 40233 | CrpalkeGrfs[14].PreklopkaMode
STRCrpalkeGrfs14Relay1setup | INT | IOD_STR_TCP | 234 | 40234 | CrpalkeGrfs[14].Relay1setup
STRCrpalkeGrfs14RemoteSetupMode1 | INT | IOD_STR_TCP | 235 | 40235 | CrpalkeGrfs[14].RemoteSetupMode1
STRCrpalkeGrfs14StatusCrpalke | INT | IOD_STR_TCP | 236 | 40236 | CrpalkeGrfs[14].StatusCrpalke | BYTE
STRCrpalkeGrfs14StatusMode1 | INT | IOD_STR_TCP | 237 | 40237 | CrpalkeGrfs[14].StatusMode1
STRCrpalkeGrfs14StatusMode1co | INT | IOD_STR_TCP | 238 | 40238 | CrpalkeGrfs[14].StatusMode1co | BYTE
STRCrpalkeGrfs14StatusMode1op | INT | IOD_STR_TCP | 239 | 40239 | CrpalkeGrfs[14].StatusMode1op | BYTE
STRCrpalkeGrfs14StatusMode2 | INT | IOD_STR_TCP | 240 | 40240 | CrpalkeGrfs[14].StatusMode2
STRCrpalkeGrfs14StatusMode3 | INT | IOD_STR_TCP | 241 | 40241 | CrpalkeGrfs[14].StatusMode3
STRCrpalkeGrfs1AlarmActiveCode | INT | IOD_STR_TCP | 242 | 40242 | CrpalkeGrfs[1].AlarmActiveCode
STRCrpalkeGrfs1AlarmCodeLog1 | INT | IOD_STR_TCP | 243 | 40243 | CrpalkeGrfs[1].AlarmCodeLog1
STRCrpalkeGrfs1AlarmCodeLog2 | INT | IOD_STR_TCP | 244 | 40244 | CrpalkeGrfs[1].AlarmCodeLog2
STRCrpalkeGrfs1AlarmCodeLog3 | INT | IOD_STR_TCP | 245 | 40245 | CrpalkeGrfs[1].AlarmCodeLog3
STRCrpalkeGrfs1AlarmCodeLog4 | INT | IOD_STR_TCP | 246 | 40246 | CrpalkeGrfs[1].AlarmCodeLog4
STRCrpalkeGrfs1AlarmCodeLog5 | INT | IOD_STR_TCP | 247 | 40247 | CrpalkeGrfs[1].AlarmCodeLog5
STRCrpalkeGrfs1AlarmGroupXVH0 | INT | IOD_STR_TCP | 248 | 40248 | CrpalkeGrfs[1].AlarmGroupXVH[0]
STRCrpalkeGrfs1AlarmGroupXVH10 | INT | IOD_STR_TCP | 249 | 40249 | CrpalkeGrfs[1].AlarmGroupXVH[10]
STRCrpalkeGrfs1AlarmGroupXVH11 | INT | IOD_STR_TCP | 250 | 40250 | CrpalkeGrfs[1].AlarmGroupXVH[11]
STRCrpalkeGrfs1AlarmGroupXVH12 | INT | IOD_STR_TCP | 251 | 40251 | CrpalkeGrfs[1].AlarmGroupXVH[12]
STRCrpalkeGrfs1AlarmGroupXVH13 | INT | IOD_STR_TCP | 252 | 40252 | CrpalkeGrfs[1].AlarmGroupXVH[13]
STRCrpalkeGrfs1AlarmGroupXVH14 | INT | IOD_STR_TCP | 253 | 40253 | CrpalkeGrfs[1].AlarmGroupXVH[14]
STRCrpalkeGrfs1AlarmGroupXVH15 | INT | IOD_STR_TCP | 254 | 40254 | CrpalkeGrfs[1].AlarmGroupXVH[15]
STRCrpalkeGrfs1AlarmGroupXVH16 | INT | IOD_STR_TCP | 255 | 40255 | CrpalkeGrfs[1].AlarmGroupXVH[16]
STRCrpalkeGrfs1AlarmGroupXVH1 | INT | IOD_STR_TCP | 256 | 40256 | CrpalkeGrfs[1].AlarmGroupXVH[1]
STRCrpalkeGrfs1AlarmGroupXVH2 | INT | IOD_STR_TCP | 257 | 40257 | CrpalkeGrfs[1].AlarmGroupXVH[2]
STRCrpalkeGrfs1AlarmGroupXVH3 | INT | IOD_STR_TCP | 258 | 40258 | CrpalkeGrfs[1].AlarmGroupXVH[3]
STRCrpalkeGrfs1AlarmGroupXVH4 | INT | IOD_STR_TCP | 259 | 40259 | CrpalkeGrfs[1].AlarmGroupXVH[4]
STRCrpalkeGrfs1AlarmGroupXVH5 | INT | IOD_STR_TCP | 260 | 40260 | CrpalkeGrfs[1].AlarmGroupXVH[5]
STRCrpalkeGrfs1AlarmGroupXVH6 | INT | IOD_STR_TCP | 261 | 40261 | CrpalkeGrfs[1].AlarmGroupXVH[6]
STRCrpalkeGrfs1AlarmGroupXVH7 | INT | IOD_STR_TCP | 262 | 40262 | CrpalkeGrfs[1].AlarmGroupXVH[7]
STRCrpalkeGrfs1AlarmGroupXVH8 | INT | IOD_STR_TCP | 263 | 40263 | CrpalkeGrfs[1].AlarmGroupXVH[8]
STRCrpalkeGrfs1AlarmGroupXVH9 | INT | IOD_STR_TCP | 264 | 40264 | CrpalkeGrfs[1].AlarmGroupXVH[9]
STRCrpalkeGrfs1AlarmQSD1 | INT | IOD_STR_TCP | 265 | 40265 | CrpalkeGrfs[1].AlarmQSD1
STRCrpalkeGrfs1AlarmQSD2 | INT | IOD_STR_TCP | 266 | 40266 | CrpalkeGrfs[1].AlarmQSD2
STRCrpalkeGrfs1AlarmStart1 | INT | IOD_STR_TCP | 267 | 40267 | CrpalkeGrfs[1].AlarmStart1
STRCrpalkeGrfs1AlarmStart2 | INT | IOD_STR_TCP | 268 | 40268 | CrpalkeGrfs[1].AlarmStart2
STRCrpalkeGrfs1AlarmStop1 | INT | IOD_STR_TCP | 269 | 40269 | CrpalkeGrfs[1].AlarmStop1
STRCrpalkeGrfs1AlarmStop2 | INT | IOD_STR_TCP | 270 | 40270 | CrpalkeGrfs[1].AlarmStop2
STRCrpalkeGrfs1AlarmStop3 | INT | IOD_STR_TCP | 271 | 40271 | CrpalkeGrfs[1].AlarmStop3
STRCrpalkeGrfs1AlarmSurv1 | INT | IOD_STR_TCP | 272 | 40272 | CrpalkeGrfs[1].AlarmSurv1
STRCrpalkeGrfs1AlarmSurv2 | INT | IOD_STR_TCP | 273 | 40273 | CrpalkeGrfs[1].AlarmSurv2
STRCrpalkeGrfs1ControlSource | INT | IOD_STR_TCP | 274 | 40274 | CrpalkeGrfs[1].ControlSource
STRCrpalkeGrfs1ExternInputSetup | INT | IOD_STR_TCP | 275 | 40275 | CrpalkeGrfs[1].ExternInputSetup
STRCrpalkeGrfs1ExternInputsStatus | INT | IOD_STR_TCP | 276 | 40276 | CrpalkeGrfs[1].ExternInputsStatus
STRCrpalkeGrfs1LocalSetupMode1 | INT | IOD_STR_TCP | 277 | 40277 | CrpalkeGrfs[1].LocalSetupMode1
STRCrpalkeGrfs1PreklopkaMode | INT | IOD_STR_TCP | 278 | 40278 | CrpalkeGrfs[1].PreklopkaMode
STRCrpalkeGrfs1Relay1setup | INT | IOD_STR_TCP | 279 | 40279 | CrpalkeGrfs[1].Relay1setup
STRCrpalkeGrfs1RemoteSetupMode1 | INT | IOD_STR_TCP | 280 | 40280 | CrpalkeGrfs[1].RemoteSetupMode1
STRCrpalkeGrfs1StatusCrpalke | INT | IOD_STR_TCP | 281 | 40281 | CrpalkeGrfs[1].StatusCrpalke | BYTE
STRCrpalkeGrfs1StatusMode1 | INT | IOD_STR_TCP | 282 | 40282 | CrpalkeGrfs[1].StatusMode1
STRCrpalkeGrfs1StatusMode1co | INT | IOD_STR_TCP | 283 | 40283 | CrpalkeGrfs[1].StatusMode1co | BYTE
STRCrpalkeGrfs1StatusMode1op | INT | IOD_STR_TCP | 284 | 40284 | CrpalkeGrfs[1].StatusMode1op | BYTE
STRCrpalkeGrfs1StatusMode2 | INT | IOD_STR_TCP | 285 | 40285 | CrpalkeGrfs[1].StatusMode2
STRCrpalkeGrfs1StatusMode3 | INT | IOD_STR_TCP | 286 | 40286 | CrpalkeGrfs[1].StatusMode3
STRCrpalkeGrfs2AlarmActiveCode | INT | IOD_STR_TCP | 287 | 40287 | CrpalkeGrfs[2].AlarmActiveCode
STRCrpalkeGrfs2AlarmCodeLog1 | INT | IOD_STR_TCP | 288 | 40288 | CrpalkeGrfs[2].AlarmCodeLog1
STRCrpalkeGrfs2AlarmCodeLog2 | INT | IOD_STR_TCP | 289 | 40289 | CrpalkeGrfs[2].AlarmCodeLog2
STRCrpalkeGrfs2AlarmCodeLog3 | INT | IOD_STR_TCP | 290 | 40290 | CrpalkeGrfs[2].AlarmCodeLog3
STRCrpalkeGrfs2AlarmCodeLog4 | INT | IOD_STR_TCP | 291 | 40291 | CrpalkeGrfs[2].AlarmCodeLog4
STRCrpalkeGrfs2AlarmCodeLog5 | INT | IOD_STR_TCP | 292 | 40292 | CrpalkeGrfs[2].AlarmCodeLog5
STRCrpalkeGrfs2AlarmGroupXVH0 | INT | IOD_STR_TCP | 293 | 40293 | CrpalkeGrfs[2].AlarmGroupXVH[0]
STRCrpalkeGrfs2AlarmGroupXVH10 | INT | IOD_STR_TCP | 294 | 40294 | CrpalkeGrfs[2].AlarmGroupXVH[10]
STRCrpalkeGrfs2AlarmGroupXVH11 | INT | IOD_STR_TCP | 295 | 40295 | CrpalkeGrfs[2].AlarmGroupXVH[11]
STRCrpalkeGrfs2AlarmGroupXVH12 | INT | IOD_STR_TCP | 296 | 40296 | CrpalkeGrfs[2].AlarmGroupXVH[12]
STRCrpalkeGrfs2AlarmGroupXVH13 | INT | IOD_STR_TCP | 297 | 40297 | CrpalkeGrfs[2].AlarmGroupXVH[13]
STRCrpalkeGrfs2AlarmGroupXVH14 | INT | IOD_STR_TCP | 298 | 40298 | CrpalkeGrfs[2].AlarmGroupXVH[14]
STRCrpalkeGrfs2AlarmGroupXVH15 | INT | IOD_STR_TCP | 299 | 40299 | CrpalkeGrfs[2].AlarmGroupXVH[15]
STRCrpalkeGrfs2AlarmGroupXVH16 | INT | IOD_STR_TCP | 300 | 40300 | CrpalkeGrfs[2].AlarmGroupXVH[16]
STRCrpalkeGrfs2AlarmGroupXVH1 | INT | IOD_STR_TCP | 301 | 40301 | CrpalkeGrfs[2].AlarmGroupXVH[1]
STRCrpalkeGrfs2AlarmGroupXVH2 | INT | IOD_STR_TCP | 302 | 40302 | CrpalkeGrfs[2].AlarmGroupXVH[2]
STRCrpalkeGrfs2AlarmGroupXVH3 | INT | IOD_STR_TCP | 303 | 40303 | CrpalkeGrfs[2].AlarmGroupXVH[3]
STRCrpalkeGrfs2AlarmGroupXVH4 | INT | IOD_STR_TCP | 304 | 40304 | CrpalkeGrfs[2].AlarmGroupXVH[4]
STRCrpalkeGrfs2AlarmGroupXVH5 | INT | IOD_STR_TCP | 305 | 40305 | CrpalkeGrfs[2].AlarmGroupXVH[5]
STRCrpalkeGrfs2AlarmGroupXVH6 | INT | IOD_STR_TCP | 306 | 40306 | CrpalkeGrfs[2].AlarmGroupXVH[6]
STRCrpalkeGrfs2AlarmGroupXVH7 | INT | IOD_STR_TCP | 307 | 40307 | CrpalkeGrfs[2].AlarmGroupXVH[7]
STRCrpalkeGrfs2AlarmGroupXVH8 | INT | IOD_STR_TCP | 308 | 40308 | CrpalkeGrfs[2].AlarmGroupXVH[8]
STRCrpalkeGrfs2AlarmGroupXVH9 | INT | IOD_STR_TCP | 309 | 40309 | CrpalkeGrfs[2].AlarmGroupXVH[9]
STRCrpalkeGrfs2AlarmQSD1 | INT | IOD_STR_TCP | 310 | 40310 | CrpalkeGrfs[2].AlarmQSD1
STRCrpalkeGrfs2AlarmQSD2 | INT | IOD_STR_TCP | 311 | 40311 | CrpalkeGrfs[2].AlarmQSD2
STRCrpalkeGrfs2AlarmStart1 | INT | IOD_STR_TCP | 312 | 40312 | CrpalkeGrfs[2].AlarmStart1
STRCrpalkeGrfs2AlarmStart2 | INT | IOD_STR_TCP | 313 | 40313 | CrpalkeGrfs[2].AlarmStart2
STRCrpalkeGrfs2AlarmStop1 | INT | IOD_STR_TCP | 314 | 40314 | CrpalkeGrfs[2].AlarmStop1
STRCrpalkeGrfs2AlarmStop2 | INT | IOD_STR_TCP | 315 | 40315 | CrpalkeGrfs[2].AlarmStop2
STRCrpalkeGrfs2AlarmStop3 | INT | IOD_STR_TCP | 316 | 40316 | CrpalkeGrfs[2].AlarmStop3
STRCrpalkeGrfs2AlarmSurv1 | INT | IOD_STR_TCP | 317 | 40317 | CrpalkeGrfs[2].AlarmSurv1
STRCrpalkeGrfs2AlarmSurv2 | INT | IOD_STR_TCP | 318 | 40318 | CrpalkeGrfs[2].AlarmSurv2
STRCrpalkeGrfs2ControlSource | INT | IOD_STR_TCP | 319 | 40319 | CrpalkeGrfs[2].ControlSource
STRCrpalkeGrfs2ExternInputSetup | INT | IOD_STR_TCP | 320 | 40320 | CrpalkeGrfs[2].ExternInputSetup
STRCrpalkeGrfs2ExternInputsStatus | INT | IOD_STR_TCP | 321 | 40321 | CrpalkeGrfs[2].ExternInputsStatus
STRCrpalkeGrfs2LocalSetupMode1 | INT | IOD_STR_TCP | 322 | 40322 | CrpalkeGrfs[2].LocalSetupMode1
STRCrpalkeGrfs2PreklopkaMode | INT | IOD_STR_TCP | 323 | 40323 | CrpalkeGrfs[2].PreklopkaMode
STRCrpalkeGrfs2Relay1setup | INT | IOD_STR_TCP | 324 | 40324 | CrpalkeGrfs[2].Relay1setup
STRCrpalkeGrfs2RemoteSetupMode1 | INT | IOD_STR_TCP | 325 | 40325 | CrpalkeGrfs[2].RemoteSetupMode1
STRCrpalkeGrfs2StatusCrpalke | INT | IOD_STR_TCP | 326 | 40326 | CrpalkeGrfs[2].StatusCrpalke | BYTE
STRCrpalkeGrfs2StatusMode1 | INT | IOD_STR_TCP | 327 | 40327 | CrpalkeGrfs[2].StatusMode1
STRCrpalkeGrfs2StatusMode1co | INT | IOD_STR_TCP | 328 | 40328 | CrpalkeGrfs[2].StatusMode1co | BYTE
STRCrpalkeGrfs2StatusMode1op | INT | IOD_STR_TCP | 329 | 40329 | CrpalkeGrfs[2].StatusMode1op | BYTE
STRCrpalkeGrfs2StatusMode2 | INT | IOD_STR_TCP | 330 | 40330 | CrpalkeGrfs[2].StatusMode2
STRCrpalkeGrfs2StatusMode3 | INT | IOD_STR_TCP | 331 | 40331 | CrpalkeGrfs[2].StatusMode3
STRCrpalkeGrfs3AlarmActiveCode | INT | IOD_STR_TCP | 332 | 40332 | CrpalkeGrfs[3].AlarmActiveCode
STRCrpalkeGrfs3AlarmCodeLog1 | INT | IOD_STR_TCP | 333 | 40333 | CrpalkeGrfs[3].AlarmCodeLog1
STRCrpalkeGrfs3AlarmCodeLog2 | INT | IOD_STR_TCP | 334 | 40334 | CrpalkeGrfs[3].AlarmCodeLog2
STRCrpalkeGrfs3AlarmCodeLog3 | INT | IOD_STR_TCP | 335 | 40335 | CrpalkeGrfs[3].AlarmCodeLog3
STRCrpalkeGrfs3AlarmCodeLog4 | INT | IOD_STR_TCP | 336 | 40336 | CrpalkeGrfs[3].AlarmCodeLog4
STRCrpalkeGrfs3AlarmCodeLog5 | INT | IOD_STR_TCP | 337 | 40337 | CrpalkeGrfs[3].AlarmCodeLog5
STRCrpalkeGrfs3AlarmGroupXVH0 | INT | IOD_STR_TCP | 338 | 40338 | CrpalkeGrfs[3].AlarmGroupXVH[0]
STRCrpalkeGrfs3AlarmGroupXVH10 | INT | IOD_STR_TCP | 339 | 40339 | CrpalkeGrfs[3].AlarmGroupXVH[10]
STRCrpalkeGrfs3AlarmGroupXVH11 | INT | IOD_STR_TCP | 340 | 40340 | CrpalkeGrfs[3].AlarmGroupXVH[11]
STRCrpalkeGrfs3AlarmGroupXVH12 | INT | IOD_STR_TCP | 341 | 40341 | CrpalkeGrfs[3].AlarmGroupXVH[12]
STRCrpalkeGrfs3AlarmGroupXVH13 | INT | IOD_STR_TCP | 342 | 40342 | CrpalkeGrfs[3].AlarmGroupXVH[13]
STRCrpalkeGrfs3AlarmGroupXVH14 | INT | IOD_STR_TCP | 343 | 40343 | CrpalkeGrfs[3].AlarmGroupXVH[14]
STRCrpalkeGrfs3AlarmGroupXVH15 | INT | IOD_STR_TCP | 344 | 40344 | CrpalkeGrfs[3].AlarmGroupXVH[15]
STRCrpalkeGrfs3AlarmGroupXVH16 | INT | IOD_STR_TCP | 345 | 40345 | CrpalkeGrfs[3].AlarmGroupXVH[16]
STRCrpalkeGrfs3AlarmGroupXVH1 | INT | IOD_STR_TCP | 346 | 40346 | CrpalkeGrfs[3].AlarmGroupXVH[1]
STRCrpalkeGrfs3AlarmGroupXVH2 | INT | IOD_STR_TCP | 347 | 40347 | CrpalkeGrfs[3].AlarmGroupXVH[2]
STRCrpalkeGrfs3AlarmGroupXVH3 | INT | IOD_STR_TCP | 348 | 40348 | CrpalkeGrfs[3].AlarmGroupXVH[3]
STRCrpalkeGrfs3AlarmGroupXVH4 | INT | IOD_STR_TCP | 349 | 40349 | CrpalkeGrfs[3].AlarmGroupXVH[4]
STRCrpalkeGrfs3AlarmGroupXVH5 | INT | IOD_STR_TCP | 350 | 40350 | CrpalkeGrfs[3].AlarmGroupXVH[5]
STRCrpalkeGrfs3AlarmGroupXVH6 | INT | IOD_STR_TCP | 351 | 40351 | CrpalkeGrfs[3].AlarmGroupXVH[6]
STRCrpalkeGrfs3AlarmGroupXVH7 | INT | IOD_STR_TCP | 352 | 40352 | CrpalkeGrfs[3].AlarmGroupXVH[7]
STRCrpalkeGrfs3AlarmGroupXVH8 | INT | IOD_STR_TCP | 353 | 40353 | CrpalkeGrfs[3].AlarmGroupXVH[8]
STRCrpalkeGrfs3AlarmGroupXVH9 | INT | IOD_STR_TCP | 354 | 40354 | CrpalkeGrfs[3].AlarmGroupXVH[9]
STRCrpalkeGrfs3AlarmQSD1 | INT | IOD_STR_TCP | 355 | 40355 | CrpalkeGrfs[3].AlarmQSD1
STRCrpalkeGrfs3AlarmQSD2 | INT | IOD_STR_TCP | 356 | 40356 | CrpalkeGrfs[3].AlarmQSD2
STRCrpalkeGrfs3AlarmStart1 | INT | IOD_STR_TCP | 357 | 40357 | CrpalkeGrfs[3].AlarmStart1
STRCrpalkeGrfs3AlarmStart2 | INT | IOD_STR_TCP | 358 | 40358 | CrpalkeGrfs[3].AlarmStart2
STRCrpalkeGrfs3AlarmStop1 | INT | IOD_STR_TCP | 359 | 40359 | CrpalkeGrfs[3].AlarmStop1
STRCrpalkeGrfs3AlarmStop2 | INT | IOD_STR_TCP | 360 | 40360 | CrpalkeGrfs[3].AlarmStop2
STRCrpalkeGrfs3AlarmStop3 | INT | IOD_STR_TCP | 361 | 40361 | CrpalkeGrfs[3].AlarmStop3
STRCrpalkeGrfs3AlarmSurv1 | INT | IOD_STR_TCP | 362 | 40362 | CrpalkeGrfs[3].AlarmSurv1
STRCrpalkeGrfs3AlarmSurv2 | INT | IOD_STR_TCP | 363 | 40363 | CrpalkeGrfs[3].AlarmSurv2
STRCrpalkeGrfs3ControlSource | INT | IOD_STR_TCP | 364 | 40364 | CrpalkeGrfs[3].ControlSource
STRCrpalkeGrfs3ExternInputSetup | INT | IOD_STR_TCP | 365 | 40365 | CrpalkeGrfs[3].ExternInputSetup
STRCrpalkeGrfs3ExternInputsStatus | INT | IOD_STR_TCP | 366 | 40366 | CrpalkeGrfs[3].ExternInputsStatus
STRCrpalkeGrfs3LocalSetupMode1 | INT | IOD_STR_TCP | 367 | 40367 | CrpalkeGrfs[3].LocalSetupMode1
STRCrpalkeGrfs3PreklopkaMode | INT | IOD_STR_TCP | 368 | 40368 | CrpalkeGrfs[3].PreklopkaMode
STRCrpalkeGrfs3Relay1setup | INT | IOD_STR_TCP | 369 | 40369 | CrpalkeGrfs[3].Relay1setup
STRCrpalkeGrfs3RemoteSetupMode1 | INT | IOD_STR_TCP | 370 | 40370 | CrpalkeGrfs[3].RemoteSetupMode1
STRCrpalkeGrfs3StatusCrpalke | INT | IOD_STR_TCP | 371 | 40371 | CrpalkeGrfs[3].StatusCrpalke | BYTE
STRCrpalkeGrfs3StatusMode1 | INT | IOD_STR_TCP | 372 | 40372 | CrpalkeGrfs[3].StatusMode1
STRCrpalkeGrfs3StatusMode1co | INT | IOD_STR_TCP | 373 | 40373 | CrpalkeGrfs[3].StatusMode1co | BYTE
STRCrpalkeGrfs3StatusMode1op | INT | IOD_STR_TCP | 374 | 40374 | CrpalkeGrfs[3].StatusMode1op | BYTE
STRCrpalkeGrfs3StatusMode2 | INT | IOD_STR_TCP | 375 | 40375 | CrpalkeGrfs[3].StatusMode2
STRCrpalkeGrfs3StatusMode3 | INT | IOD_STR_TCP | 376 | 40376 | CrpalkeGrfs[3].StatusMode3
STRCrpalkeGrfs4AlarmActiveCode | INT | IOD_STR_TCP | 377 | 40377 | CrpalkeGrfs[4].AlarmActiveCode
STRCrpalkeGrfs4AlarmCodeLog1 | INT | IOD_STR_TCP | 378 | 40378 | CrpalkeGrfs[4].AlarmCodeLog1
STRCrpalkeGrfs4AlarmCodeLog2 | INT | IOD_STR_TCP | 379 | 40379 | CrpalkeGrfs[4].AlarmCodeLog2
STRCrpalkeGrfs4AlarmCodeLog3 | INT | IOD_STR_TCP | 380 | 40380 | CrpalkeGrfs[4].AlarmCodeLog3
STRCrpalkeGrfs4AlarmCodeLog4 | INT | IOD_STR_TCP | 381 | 40381 | CrpalkeGrfs[4].AlarmCodeLog4
STRCrpalkeGrfs4AlarmCodeLog5 | INT | IOD_STR_TCP | 382 | 40382 | CrpalkeGrfs[4].AlarmCodeLog5
STRCrpalkeGrfs4AlarmGroupXVH0 | INT | IOD_STR_TCP | 383 | 40383 | CrpalkeGrfs[4].AlarmGroupXVH[0]
STRCrpalkeGrfs4AlarmGroupXVH10 | INT | IOD_STR_TCP | 384 | 40384 | CrpalkeGrfs[4].AlarmGroupXVH[10]
STRCrpalkeGrfs4AlarmGroupXVH11 | INT | IOD_STR_TCP | 385 | 40385 | CrpalkeGrfs[4].AlarmGroupXVH[11]
STRCrpalkeGrfs4AlarmGroupXVH12 | INT | IOD_STR_TCP | 386 | 40386 | CrpalkeGrfs[4].AlarmGroupXVH[12]
STRCrpalkeGrfs4AlarmGroupXVH13 | INT | IOD_STR_TCP | 387 | 40387 | CrpalkeGrfs[4].AlarmGroupXVH[13]
STRCrpalkeGrfs4AlarmGroupXVH14 | INT | IOD_STR_TCP | 388 | 40388 | CrpalkeGrfs[4].AlarmGroupXVH[14]
STRCrpalkeGrfs4AlarmGroupXVH15 | INT | IOD_STR_TCP | 389 | 40389 | CrpalkeGrfs[4].AlarmGroupXVH[15]
STRCrpalkeGrfs4AlarmGroupXVH16 | INT | IOD_STR_TCP | 390 | 40390 | CrpalkeGrfs[4].AlarmGroupXVH[16]
STRCrpalkeGrfs4AlarmGroupXVH1 | INT | IOD_STR_TCP | 391 | 40391 | CrpalkeGrfs[4].AlarmGroupXVH[1]
STRCrpalkeGrfs4AlarmGroupXVH2 | INT | IOD_STR_TCP | 392 | 40392 | CrpalkeGrfs[4].AlarmGroupXVH[2]
STRCrpalkeGrfs4AlarmGroupXVH3 | INT | IOD_STR_TCP | 393 | 40393 | CrpalkeGrfs[4].AlarmGroupXVH[3]
STRCrpalkeGrfs4AlarmGroupXVH4 | INT | IOD_STR_TCP | 394 | 40394 | CrpalkeGrfs[4].AlarmGroupXVH[4]
STRCrpalkeGrfs4AlarmGroupXVH5 | INT | IOD_STR_TCP | 395 | 40395 | CrpalkeGrfs[4].AlarmGroupXVH[5]
STRCrpalkeGrfs4AlarmGroupXVH6 | INT | IOD_STR_TCP | 396 | 40396 | CrpalkeGrfs[4].AlarmGroupXVH[6]
STRCrpalkeGrfs4AlarmGroupXVH7 | INT | IOD_STR_TCP | 397 | 40397 | CrpalkeGrfs[4].AlarmGroupXVH[7]
STRCrpalkeGrfs4AlarmGroupXVH8 | INT | IOD_STR_TCP | 398 | 40398 | CrpalkeGrfs[4].AlarmGroupXVH[8]
STRCrpalkeGrfs4AlarmGroupXVH9 | INT | IOD_STR_TCP | 399 | 40399 | CrpalkeGrfs[4].AlarmGroupXVH[9]
STRCrpalkeGrfs4AlarmQSD1 | INT | IOD_STR_TCP | 400 | 40400 | CrpalkeGrfs[4].AlarmQSD1
STRCrpalkeGrfs4AlarmQSD2 | INT | IOD_STR_TCP | 401 | 40401 | CrpalkeGrfs[4].AlarmQSD2
STRCrpalkeGrfs4AlarmStart1 | INT | IOD_STR_TCP | 402 | 40402 | CrpalkeGrfs[4].AlarmStart1
STRCrpalkeGrfs4AlarmStart2 | INT | IOD_STR_TCP | 403 | 40403 | CrpalkeGrfs[4].AlarmStart2
STRCrpalkeGrfs4AlarmStop1 | INT | IOD_STR_TCP | 404 | 40404 | CrpalkeGrfs[4].AlarmStop1
STRCrpalkeGrfs4AlarmStop2 | INT | IOD_STR_TCP | 405 | 40405 | CrpalkeGrfs[4].AlarmStop2
STRCrpalkeGrfs4AlarmStop3 | INT | IOD_STR_TCP | 406 | 40406 | CrpalkeGrfs[4].AlarmStop3
STRCrpalkeGrfs4AlarmSurv1 | INT | IOD_STR_TCP | 407 | 40407 | CrpalkeGrfs[4].AlarmSurv1
STRCrpalkeGrfs4AlarmSurv2 | INT | IOD_STR_TCP | 408 | 40408 | CrpalkeGrfs[4].AlarmSurv2
STRCrpalkeGrfs4ControlSource | INT | IOD_STR_TCP | 409 | 40409 | CrpalkeGrfs[4].ControlSource
STRCrpalkeGrfs4ExternInputSetup | INT | IOD_STR_TCP | 410 | 40410 | CrpalkeGrfs[4].ExternInputSetup
STRCrpalkeGrfs4ExternInputsStatus | INT | IOD_STR_TCP | 411 | 40411 | CrpalkeGrfs[4].ExternInputsStatus
STRCrpalkeGrfs4LocalSetupMode1 | INT | IOD_STR_TCP | 412 | 40412 | CrpalkeGrfs[4].LocalSetupMode1
STRCrpalkeGrfs4PreklopkaMode | INT | IOD_STR_TCP | 413 | 40413 | CrpalkeGrfs[4].PreklopkaMode
STRCrpalkeGrfs4Relay1setup | INT | IOD_STR_TCP | 414 | 40414 | CrpalkeGrfs[4].Relay1setup
STRCrpalkeGrfs4RemoteSetupMode1 | INT | IOD_STR_TCP | 415 | 40415 | CrpalkeGrfs[4].RemoteSetupMode1
STRCrpalkeGrfs4StatusCrpalke | INT | IOD_STR_TCP | 416 | 40416 | CrpalkeGrfs[4].StatusCrpalke | BYTE
STRCrpalkeGrfs4StatusMode1 | INT | IOD_STR_TCP | 417 | 40417 | CrpalkeGrfs[4].StatusMode1
STRCrpalkeGrfs4StatusMode1co | INT | IOD_STR_TCP | 418 | 40418 | CrpalkeGrfs[4].StatusMode1co | BYTE
STRCrpalkeGrfs4StatusMode1op | INT | IOD_STR_TCP | 419 | 40419 | CrpalkeGrfs[4].StatusMode1op | BYTE
STRCrpalkeGrfs4StatusMode2 | INT | IOD_STR_TCP | 420 | 40420 | CrpalkeGrfs[4].StatusMode2
STRCrpalkeGrfs4StatusMode3 | INT | IOD_STR_TCP | 421 | 40421 | CrpalkeGrfs[4].StatusMode3
STRCrpalkeGrfs5AlarmActiveCode | INT | IOD_STR_TCP | 422 | 40422 | CrpalkeGrfs[5].AlarmActiveCode
STRCrpalkeGrfs5AlarmCodeLog1 | INT | IOD_STR_TCP | 423 | 40423 | CrpalkeGrfs[5].AlarmCodeLog1
STRCrpalkeGrfs5AlarmCodeLog2 | INT | IOD_STR_TCP | 424 | 40424 | CrpalkeGrfs[5].AlarmCodeLog2
STRCrpalkeGrfs5AlarmCodeLog3 | INT | IOD_STR_TCP | 425 | 40425 | CrpalkeGrfs[5].AlarmCodeLog3
STRCrpalkeGrfs5AlarmCodeLog4 | INT | IOD_STR_TCP | 426 | 40426 | CrpalkeGrfs[5].AlarmCodeLog4
STRCrpalkeGrfs5AlarmCodeLog5 | INT | IOD_STR_TCP | 427 | 40427 | CrpalkeGrfs[5].AlarmCodeLog5
STRCrpalkeGrfs5AlarmGroupXVH0 | INT | IOD_STR_TCP | 428 | 40428 | CrpalkeGrfs[5].AlarmGroupXVH[0]
STRCrpalkeGrfs5AlarmGroupXVH10 | INT | IOD_STR_TCP | 429 | 40429 | CrpalkeGrfs[5].AlarmGroupXVH[10]
STRCrpalkeGrfs5AlarmGroupXVH11 | INT | IOD_STR_TCP | 430 | 40430 | CrpalkeGrfs[5].AlarmGroupXVH[11]
STRCrpalkeGrfs5AlarmGroupXVH12 | INT | IOD_STR_TCP | 431 | 40431 | CrpalkeGrfs[5].AlarmGroupXVH[12]
STRCrpalkeGrfs5AlarmGroupXVH13 | INT | IOD_STR_TCP | 432 | 40432 | CrpalkeGrfs[5].AlarmGroupXVH[13]
STRCrpalkeGrfs5AlarmGroupXVH14 | INT | IOD_STR_TCP | 433 | 40433 | CrpalkeGrfs[5].AlarmGroupXVH[14]
STRCrpalkeGrfs5AlarmGroupXVH15 | INT | IOD_STR_TCP | 434 | 40434 | CrpalkeGrfs[5].AlarmGroupXVH[15]
STRCrpalkeGrfs5AlarmGroupXVH16 | INT | IOD_STR_TCP | 435 | 40435 | CrpalkeGrfs[5].AlarmGroupXVH[16]
STRCrpalkeGrfs5AlarmGroupXVH1 | INT | IOD_STR_TCP | 436 | 40436 | CrpalkeGrfs[5].AlarmGroupXVH[1]
STRCrpalkeGrfs5AlarmGroupXVH2 | INT | IOD_STR_TCP | 437 | 40437 | CrpalkeGrfs[5].AlarmGroupXVH[2]
STRCrpalkeGrfs5AlarmGroupXVH3 | INT | IOD_STR_TCP | 438 | 40438 | CrpalkeGrfs[5].AlarmGroupXVH[3]
STRCrpalkeGrfs5AlarmGroupXVH4 | INT | IOD_STR_TCP | 439 | 40439 | CrpalkeGrfs[5].AlarmGroupXVH[4]
STRCrpalkeGrfs5AlarmGroupXVH5 | INT | IOD_STR_TCP | 440 | 40440 | CrpalkeGrfs[5].AlarmGroupXVH[5]
STRCrpalkeGrfs5AlarmGroupXVH6 | INT | IOD_STR_TCP | 441 | 40441 | CrpalkeGrfs[5].AlarmGroupXVH[6]
STRCrpalkeGrfs5AlarmGroupXVH7 | INT | IOD_STR_TCP | 442 | 40442 | CrpalkeGrfs[5].AlarmGroupXVH[7]
STRCrpalkeGrfs5AlarmGroupXVH8 | INT | IOD_STR_TCP | 443 | 40443 | CrpalkeGrfs[5].AlarmGroupXVH[8]
STRCrpalkeGrfs5AlarmGroupXVH9 | INT | IOD_STR_TCP | 444 | 40444 | CrpalkeGrfs[5].AlarmGroupXVH[9]
STRCrpalkeGrfs5AlarmQSD1 | INT | IOD_STR_TCP | 445 | 40445 | CrpalkeGrfs[5].AlarmQSD1
STRCrpalkeGrfs5AlarmQSD2 | INT | IOD_STR_TCP | 446 | 40446 | CrpalkeGrfs[5].AlarmQSD2
STRCrpalkeGrfs5AlarmStart1 | INT | IOD_STR_TCP | 447 | 40447 | CrpalkeGrfs[5].AlarmStart1
STRCrpalkeGrfs5AlarmStart2 | INT | IOD_STR_TCP | 448 | 40448 | CrpalkeGrfs[5].AlarmStart2
STRCrpalkeGrfs5AlarmStop1 | INT | IOD_STR_TCP | 449 | 40449 | CrpalkeGrfs[5].AlarmStop1
STRCrpalkeGrfs5AlarmStop2 | INT | IOD_STR_TCP | 450 | 40450 | CrpalkeGrfs[5].AlarmStop2
STRCrpalkeGrfs5AlarmStop3 | INT | IOD_STR_TCP | 451 | 40451 | CrpalkeGrfs[5].AlarmStop3
STRCrpalkeGrfs5AlarmSurv1 | INT | IOD_STR_TCP | 452 | 40452 | CrpalkeGrfs[5].AlarmSurv1
STRCrpalkeGrfs5AlarmSurv2 | INT | IOD_STR_TCP | 453 | 40453 | CrpalkeGrfs[5].AlarmSurv2
STRCrpalkeGrfs5ControlSource | INT | IOD_STR_TCP | 454 | 40454 | CrpalkeGrfs[5].ControlSource
STRCrpalkeGrfs5ExternInputSetup | INT | IOD_STR_TCP | 455 | 40455 | CrpalkeGrfs[5].ExternInputSetup
STRCrpalkeGrfs5ExternInputsStatus | INT | IOD_STR_TCP | 456 | 40456 | CrpalkeGrfs[5].ExternInputsStatus
STRCrpalkeGrfs5LocalSetupMode1 | INT | IOD_STR_TCP | 457 | 40457 | CrpalkeGrfs[5].LocalSetupMode1
STRCrpalkeGrfs5PreklopkaMode | INT | IOD_STR_TCP | 458 | 40458 | CrpalkeGrfs[5].PreklopkaMode
STRCrpalkeGrfs5Relay1setup | INT | IOD_STR_TCP | 459 | 40459 | CrpalkeGrfs[5].Relay1setup
STRCrpalkeGrfs5RemoteSetupMode1 | INT | IOD_STR_TCP | 460 | 40460 | CrpalkeGrfs[5].RemoteSetupMode1
STRCrpalkeGrfs5StatusCrpalke | INT | IOD_STR_TCP | 461 | 40461 | CrpalkeGrfs[5].StatusCrpalke | BYTE
STRCrpalkeGrfs5StatusMode1 | INT | IOD_STR_TCP | 462 | 40462 | CrpalkeGrfs[5].StatusMode1
STRCrpalkeGrfs5StatusMode1co | INT | IOD_STR_TCP | 463 | 40463 | CrpalkeGrfs[5].StatusMode1co | BYTE
STRCrpalkeGrfs5StatusMode1op | INT | IOD_STR_TCP | 464 | 40464 | CrpalkeGrfs[5].StatusMode1op | BYTE
STRCrpalkeGrfs5StatusMode2 | INT | IOD_STR_TCP | 465 | 40465 | CrpalkeGrfs[5].StatusMode2
STRCrpalkeGrfs5StatusMode3 | INT | IOD_STR_TCP | 466 | 40466 | CrpalkeGrfs[5].StatusMode3
STRCrpalkeGrfs6AlarmActiveCode | INT | IOD_STR_TCP | 467 | 40467 | CrpalkeGrfs[6].AlarmActiveCode
STRCrpalkeGrfs6AlarmCodeLog1 | INT | IOD_STR_TCP | 468 | 40468 | CrpalkeGrfs[6].AlarmCodeLog1
STRCrpalkeGrfs6AlarmCodeLog2 | INT | IOD_STR_TCP | 469 | 40469 | CrpalkeGrfs[6].AlarmCodeLog2
STRCrpalkeGrfs6AlarmCodeLog3 | INT | IOD_STR_TCP | 470 | 40470 | CrpalkeGrfs[6].AlarmCodeLog3
STRCrpalkeGrfs6AlarmCodeLog4 | INT | IOD_STR_TCP | 471 | 40471 | CrpalkeGrfs[6].AlarmCodeLog4
STRCrpalkeGrfs6AlarmCodeLog5 | INT | IOD_STR_TCP | 472 | 40472 | CrpalkeGrfs[6].AlarmCodeLog5
STRCrpalkeGrfs6AlarmGroupXVH0 | INT | IOD_STR_TCP | 473 | 40473 | CrpalkeGrfs[6].AlarmGroupXVH[0]
STRCrpalkeGrfs6AlarmGroupXVH10 | INT | IOD_STR_TCP | 474 | 40474 | CrpalkeGrfs[6].AlarmGroupXVH[10]
STRCrpalkeGrfs6AlarmGroupXVH11 | INT | IOD_STR_TCP | 475 | 40475 | CrpalkeGrfs[6].AlarmGroupXVH[11]
STRCrpalkeGrfs6AlarmGroupXVH12 | INT | IOD_STR_TCP | 476 | 40476 | CrpalkeGrfs[6].AlarmGroupXVH[12]
STRCrpalkeGrfs6AlarmGroupXVH13 | INT | IOD_STR_TCP | 477 | 40477 | CrpalkeGrfs[6].AlarmGroupXVH[13]
STRCrpalkeGrfs6AlarmGroupXVH14 | INT | IOD_STR_TCP | 478 | 40478 | CrpalkeGrfs[6].AlarmGroupXVH[14]
STRCrpalkeGrfs6AlarmGroupXVH15 | INT | IOD_STR_TCP | 479 | 40479 | CrpalkeGrfs[6].AlarmGroupXVH[15]
STRCrpalkeGrfs6AlarmGroupXVH16 | INT | IOD_STR_TCP | 480 | 40480 | CrpalkeGrfs[6].AlarmGroupXVH[16]
STRCrpalkeGrfs6AlarmGroupXVH1 | INT | IOD_STR_TCP | 481 | 40481 | CrpalkeGrfs[6].AlarmGroupXVH[1]
STRCrpalkeGrfs6AlarmGroupXVH2 | INT | IOD_STR_TCP | 482 | 40482 | CrpalkeGrfs[6].AlarmGroupXVH[2]
STRCrpalkeGrfs6AlarmGroupXVH3 | INT | IOD_STR_TCP | 483 | 40483 | CrpalkeGrfs[6].AlarmGroupXVH[3]
STRCrpalkeGrfs6AlarmGroupXVH4 | INT | IOD_STR_TCP | 484 | 40484 | CrpalkeGrfs[6].AlarmGroupXVH[4]
STRCrpalkeGrfs6AlarmGroupXVH5 | INT | IOD_STR_TCP | 485 | 40485 | CrpalkeGrfs[6].AlarmGroupXVH[5]
STRCrpalkeGrfs6AlarmGroupXVH6 | INT | IOD_STR_TCP | 486 | 40486 | CrpalkeGrfs[6].AlarmGroupXVH[6]
STRCrpalkeGrfs6AlarmGroupXVH7 | INT | IOD_STR_TCP | 487 | 40487 | CrpalkeGrfs[6].AlarmGroupXVH[7]
STRCrpalkeGrfs6AlarmGroupXVH8 | INT | IOD_STR_TCP | 488 | 40488 | CrpalkeGrfs[6].AlarmGroupXVH[8]
STRCrpalkeGrfs6AlarmGroupXVH9 | INT | IOD_STR_TCP | 489 | 40489 | CrpalkeGrfs[6].AlarmGroupXVH[9]
STRCrpalkeGrfs6AlarmQSD1 | INT | IOD_STR_TCP | 490 | 40490 | CrpalkeGrfs[6].AlarmQSD1
STRCrpalkeGrfs6AlarmQSD2 | INT | IOD_STR_TCP | 491 | 40491 | CrpalkeGrfs[6].AlarmQSD2
STRCrpalkeGrfs6AlarmStart1 | INT | IOD_STR_TCP | 492 | 40492 | CrpalkeGrfs[6].AlarmStart1
STRCrpalkeGrfs6AlarmStart2 | INT | IOD_STR_TCP | 493 | 40493 | CrpalkeGrfs[6].AlarmStart2
STRCrpalkeGrfs6AlarmStop1 | INT | IOD_STR_TCP | 494 | 40494 | CrpalkeGrfs[6].AlarmStop1
STRCrpalkeGrfs6AlarmStop2 | INT | IOD_STR_TCP | 495 | 40495 | CrpalkeGrfs[6].AlarmStop2
STRCrpalkeGrfs6AlarmStop3 | INT | IOD_STR_TCP | 496 | 40496 | CrpalkeGrfs[6].AlarmStop3
STRCrpalkeGrfs6AlarmSurv1 | INT | IOD_STR_TCP | 497 | 40497 | CrpalkeGrfs[6].AlarmSurv1
STRCrpalkeGrfs6AlarmSurv2 | INT | IOD_STR_TCP | 498 | 40498 | CrpalkeGrfs[6].AlarmSurv2
STRCrpalkeGrfs6ControlSource | INT | IOD_STR_TCP | 499 | 40499 | CrpalkeGrfs[6].ControlSource
STRCrpalkeGrfs6ExternInputSetup | INT | IOD_STR_TCP | 500 | 40500 | CrpalkeGrfs[6].ExternInputSetup
STRCrpalkeGrfs6ExternInputsStatus | INT | IOD_STR_TCP | 501 | 40501 | CrpalkeGrfs[6].ExternInputsStatus
STRCrpalkeGrfs6LocalSetupMode1 | INT | IOD_STR_TCP | 502 | 40502 | CrpalkeGrfs[6].LocalSetupMode1
STRCrpalkeGrfs6PreklopkaMode | INT | IOD_STR_TCP | 503 | 40503 | CrpalkeGrfs[6].PreklopkaMode
STRCrpalkeGrfs6Relay1setup | INT | IOD_STR_TCP | 504 | 40504 | CrpalkeGrfs[6].Relay1setup
STRCrpalkeGrfs6RemoteSetupMode1 | INT | IOD_STR_TCP | 505 | 40505 | CrpalkeGrfs[6].RemoteSetupMode1
STRCrpalkeGrfs6StatusCrpalke | INT | IOD_STR_TCP | 506 | 40506 | CrpalkeGrfs[6].StatusCrpalke | BYTE
STRCrpalkeGrfs6StatusMode1 | INT | IOD_STR_TCP | 507 | 40507 | CrpalkeGrfs[6].StatusMode1
STRCrpalkeGrfs6StatusMode1co | INT | IOD_STR_TCP | 508 | 40508 | CrpalkeGrfs[6].StatusMode1co | BYTE
STRCrpalkeGrfs6StatusMode1op | INT | IOD_STR_TCP | 509 | 40509 | CrpalkeGrfs[6].StatusMode1op | BYTE
STRCrpalkeGrfs6StatusMode2 | INT | IOD_STR_TCP | 510 | 40510 | CrpalkeGrfs[6].StatusMode2
STRCrpalkeGrfs6StatusMode3 | INT | IOD_STR_TCP | 511 | 40511 | CrpalkeGrfs[6].StatusMode3
STRCrpalkeGrfs7AlarmActiveCode | INT | IOD_STR_TCP | 512 | 40512 | CrpalkeGrfs[7].AlarmActiveCode
STRCrpalkeGrfs7AlarmCodeLog1 | INT | IOD_STR_TCP | 513 | 40513 | CrpalkeGrfs[7].AlarmCodeLog1
STRCrpalkeGrfs7AlarmCodeLog2 | INT | IOD_STR_TCP | 514 | 40514 | CrpalkeGrfs[7].AlarmCodeLog2
STRCrpalkeGrfs7AlarmCodeLog3 | INT | IOD_STR_TCP | 515 | 40515 | CrpalkeGrfs[7].AlarmCodeLog3
STRCrpalkeGrfs7AlarmCodeLog4 | INT | IOD_STR_TCP | 516 | 40516 | CrpalkeGrfs[7].AlarmCodeLog4
STRCrpalkeGrfs7AlarmCodeLog5 | INT | IOD_STR_TCP | 517 | 40517 | CrpalkeGrfs[7].AlarmCodeLog5
STRCrpalkeGrfs7AlarmGroupXVH0 | INT | IOD_STR_TCP | 518 | 40518 | CrpalkeGrfs[7].AlarmGroupXVH[0]
STRCrpalkeGrfs7AlarmGroupXVH10 | INT | IOD_STR_TCP | 519 | 40519 | CrpalkeGrfs[7].AlarmGroupXVH[10]
STRCrpalkeGrfs7AlarmGroupXVH11 | INT | IOD_STR_TCP | 520 | 40520 | CrpalkeGrfs[7].AlarmGroupXVH[11]
STRCrpalkeGrfs7AlarmGroupXVH12 | INT | IOD_STR_TCP | 521 | 40521 | CrpalkeGrfs[7].AlarmGroupXVH[12]
STRCrpalkeGrfs7AlarmGroupXVH13 | INT | IOD_STR_TCP | 522 | 40522 | CrpalkeGrfs[7].AlarmGroupXVH[13]
STRCrpalkeGrfs7AlarmGroupXVH14 | INT | IOD_STR_TCP | 523 | 40523 | CrpalkeGrfs[7].AlarmGroupXVH[14]
STRCrpalkeGrfs7AlarmGroupXVH15 | INT | IOD_STR_TCP | 524 | 40524 | CrpalkeGrfs[7].AlarmGroupXVH[15]
STRCrpalkeGrfs7AlarmGroupXVH16 | INT | IOD_STR_TCP | 525 | 40525 | CrpalkeGrfs[7].AlarmGroupXVH[16]
STRCrpalkeGrfs7AlarmGroupXVH1 | INT | IOD_STR_TCP | 526 | 40526 | CrpalkeGrfs[7].AlarmGroupXVH[1]
STRCrpalkeGrfs7AlarmGroupXVH2 | INT | IOD_STR_TCP | 527 | 40527 | CrpalkeGrfs[7].AlarmGroupXVH[2]
STRCrpalkeGrfs7AlarmGroupXVH3 | INT | IOD_STR_TCP | 528 | 40528 | CrpalkeGrfs[7].AlarmGroupXVH[3]
STRCrpalkeGrfs7AlarmGroupXVH4 | INT | IOD_STR_TCP | 529 | 40529 | CrpalkeGrfs[7].AlarmGroupXVH[4]
STRCrpalkeGrfs7AlarmGroupXVH5 | INT | IOD_STR_TCP | 530 | 40530 | CrpalkeGrfs[7].AlarmGroupXVH[5]
STRCrpalkeGrfs7AlarmGroupXVH6 | INT | IOD_STR_TCP | 531 | 40531 | CrpalkeGrfs[7].AlarmGroupXVH[6]
STRCrpalkeGrfs7AlarmGroupXVH7 | INT | IOD_STR_TCP | 532 | 40532 | CrpalkeGrfs[7].AlarmGroupXVH[7]
STRCrpalkeGrfs7AlarmGroupXVH8 | INT | IOD_STR_TCP | 533 | 40533 | CrpalkeGrfs[7].AlarmGroupXVH[8]
STRCrpalkeGrfs7AlarmGroupXVH9 | INT | IOD_STR_TCP | 534 | 40534 | CrpalkeGrfs[7].AlarmGroupXVH[9]
STRCrpalkeGrfs7AlarmQSD1 | INT | IOD_STR_TCP | 535 | 40535 | CrpalkeGrfs[7].AlarmQSD1
STRCrpalkeGrfs7AlarmQSD2 | INT | IOD_STR_TCP | 536 | 40536 | CrpalkeGrfs[7].AlarmQSD2
STRCrpalkeGrfs7AlarmStart1 | INT | IOD_STR_TCP | 537 | 40537 | CrpalkeGrfs[7].AlarmStart1
STRCrpalkeGrfs7AlarmStart2 | INT | IOD_STR_TCP | 538 | 40538 | CrpalkeGrfs[7].AlarmStart2
STRCrpalkeGrfs7AlarmStop1 | INT | IOD_STR_TCP | 539 | 40539 | CrpalkeGrfs[7].AlarmStop1
STRCrpalkeGrfs7AlarmStop2 | INT | IOD_STR_TCP | 540 | 40540 | CrpalkeGrfs[7].AlarmStop2
STRCrpalkeGrfs7AlarmStop3 | INT | IOD_STR_TCP | 541 | 40541 | CrpalkeGrfs[7].AlarmStop3
STRCrpalkeGrfs7AlarmSurv1 | INT | IOD_STR_TCP | 542 | 40542 | CrpalkeGrfs[7].AlarmSurv1
STRCrpalkeGrfs7AlarmSurv2 | INT | IOD_STR_TCP | 543 | 40543 | CrpalkeGrfs[7].AlarmSurv2
STRCrpalkeGrfs7ControlSource | INT | IOD_STR_TCP | 544 | 40544 | CrpalkeGrfs[7].ControlSource
STRCrpalkeGrfs7ExternInputSetup | INT | IOD_STR_TCP | 545 | 40545 | CrpalkeGrfs[7].ExternInputSetup
STRCrpalkeGrfs7ExternInputsStatus | INT | IOD_STR_TCP | 546 | 40546 | CrpalkeGrfs[7].ExternInputsStatus
STRCrpalkeGrfs7LocalSetupMode1 | INT | IOD_STR_TCP | 547 | 40547 | CrpalkeGrfs[7].LocalSetupMode1
STRCrpalkeGrfs7PreklopkaMode | INT | IOD_STR_TCP | 548 | 40548 | CrpalkeGrfs[7].PreklopkaMode
STRCrpalkeGrfs7Relay1setup | INT | IOD_STR_TCP | 549 | 40549 | CrpalkeGrfs[7].Relay1setup
STRCrpalkeGrfs7RemoteSetupMode1 | INT | IOD_STR_TCP | 550 | 40550 | CrpalkeGrfs[7].RemoteSetupMode1
STRCrpalkeGrfs7StatusCrpalke | INT | IOD_STR_TCP | 551 | 40551 | CrpalkeGrfs[7].StatusCrpalke | BYTE
STRCrpalkeGrfs7StatusMode1 | INT | IOD_STR_TCP | 552 | 40552 | CrpalkeGrfs[7].StatusMode1
STRCrpalkeGrfs7StatusMode1co | INT | IOD_STR_TCP | 553 | 40553 | CrpalkeGrfs[7].StatusMode1co | BYTE
STRCrpalkeGrfs7StatusMode1op | INT | IOD_STR_TCP | 554 | 40554 | CrpalkeGrfs[7].StatusMode1op | BYTE
STRCrpalkeGrfs7StatusMode2 | INT | IOD_STR_TCP | 555 | 40555 | CrpalkeGrfs[7].StatusMode2
STRCrpalkeGrfs7StatusMode3 | INT | IOD_STR_TCP | 556 | 40556 | CrpalkeGrfs[7].StatusMode3
STRCrpalkeGrfs8AlarmActiveCode | INT | IOD_STR_TCP | 557 | 40557 | CrpalkeGrfs[8].AlarmActiveCode
STRCrpalkeGrfs8AlarmCodeLog1 | INT | IOD_STR_TCP | 558 | 40558 | CrpalkeGrfs[8].AlarmCodeLog1
STRCrpalkeGrfs8AlarmCodeLog2 | INT | IOD_STR_TCP | 559 | 40559 | CrpalkeGrfs[8].AlarmCodeLog2
STRCrpalkeGrfs8AlarmCodeLog3 | INT | IOD_STR_TCP | 560 | 40560 | CrpalkeGrfs[8].AlarmCodeLog3
STRCrpalkeGrfs8AlarmCodeLog4 | INT | IOD_STR_TCP | 561 | 40561 | CrpalkeGrfs[8].AlarmCodeLog4
STRCrpalkeGrfs8AlarmCodeLog5 | INT | IOD_STR_TCP | 562 | 40562 | CrpalkeGrfs[8].AlarmCodeLog5
STRCrpalkeGrfs8AlarmGroupXVH0 | INT | IOD_STR_TCP | 563 | 40563 | CrpalkeGrfs[8].AlarmGroupXVH[0]
STRCrpalkeGrfs8AlarmGroupXVH10 | INT | IOD_STR_TCP | 564 | 40564 | CrpalkeGrfs[8].AlarmGroupXVH[10]
STRCrpalkeGrfs8AlarmGroupXVH11 | INT | IOD_STR_TCP | 565 | 40565 | CrpalkeGrfs[8].AlarmGroupXVH[11]
STRCrpalkeGrfs8AlarmGroupXVH12 | INT | IOD_STR_TCP | 566 | 40566 | CrpalkeGrfs[8].AlarmGroupXVH[12]
STRCrpalkeGrfs8AlarmGroupXVH13 | INT | IOD_STR_TCP | 567 | 40567 | CrpalkeGrfs[8].AlarmGroupXVH[13]
STRCrpalkeGrfs8AlarmGroupXVH14 | INT | IOD_STR_TCP | 568 | 40568 | CrpalkeGrfs[8].AlarmGroupXVH[14]
STRCrpalkeGrfs8AlarmGroupXVH15 | INT | IOD_STR_TCP | 569 | 40569 | CrpalkeGrfs[8].AlarmGroupXVH[15]
STRCrpalkeGrfs8AlarmGroupXVH16 | INT | IOD_STR_TCP | 570 | 40570 | CrpalkeGrfs[8].AlarmGroupXVH[16]
STRCrpalkeGrfs8AlarmGroupXVH1 | INT | IOD_STR_TCP | 571 | 40571 | CrpalkeGrfs[8].AlarmGroupXVH[1]
STRCrpalkeGrfs8AlarmGroupXVH2 | INT | IOD_STR_TCP | 572 | 40572 | CrpalkeGrfs[8].AlarmGroupXVH[2]
STRCrpalkeGrfs8AlarmGroupXVH3 | INT | IOD_STR_TCP | 573 | 40573 | CrpalkeGrfs[8].AlarmGroupXVH[3]
STRCrpalkeGrfs8AlarmGroupXVH4 | INT | IOD_STR_TCP | 574 | 40574 | CrpalkeGrfs[8].AlarmGroupXVH[4]
STRCrpalkeGrfs8AlarmGroupXVH5 | INT | IOD_STR_TCP | 575 | 40575 | CrpalkeGrfs[8].AlarmGroupXVH[5]
STRCrpalkeGrfs8AlarmGroupXVH6 | INT | IOD_STR_TCP | 576 | 40576 | CrpalkeGrfs[8].AlarmGroupXVH[6]
STRCrpalkeGrfs8AlarmGroupXVH7 | INT | IOD_STR_TCP | 577 | 40577 | CrpalkeGrfs[8].AlarmGroupXVH[7]
STRCrpalkeGrfs8AlarmGroupXVH8 | INT | IOD_STR_TCP | 578 | 40578 | CrpalkeGrfs[8].AlarmGroupXVH[8]
STRCrpalkeGrfs8AlarmGroupXVH9 | INT | IOD_STR_TCP | 579 | 40579 | CrpalkeGrfs[8].AlarmGroupXVH[9]
STRCrpalkeGrfs8AlarmQSD1 | INT | IOD_STR_TCP | 580 | 40580 | CrpalkeGrfs[8].AlarmQSD1
STRCrpalkeGrfs8AlarmQSD2 | INT | IOD_STR_TCP | 581 | 40581 | CrpalkeGrfs[8].AlarmQSD2
STRCrpalkeGrfs8AlarmStart1 | INT | IOD_STR_TCP | 582 | 40582 | CrpalkeGrfs[8].AlarmStart1
STRCrpalkeGrfs8AlarmStart2 | INT | IOD_STR_TCP | 583 | 40583 | CrpalkeGrfs[8].AlarmStart2
STRCrpalkeGrfs8AlarmStop1 | INT | IOD_STR_TCP | 584 | 40584 | CrpalkeGrfs[8].AlarmStop1
STRCrpalkeGrfs8AlarmStop2 | INT | IOD_STR_TCP | 585 | 40585 | CrpalkeGrfs[8].AlarmStop2
STRCrpalkeGrfs8AlarmStop3 | INT | IOD_STR_TCP | 586 | 40586 | CrpalkeGrfs[8].AlarmStop3
STRCrpalkeGrfs8AlarmSurv1 | INT | IOD_STR_TCP | 587 | 40587 | CrpalkeGrfs[8].AlarmSurv1
STRCrpalkeGrfs8AlarmSurv2 | INT | IOD_STR_TCP | 588 | 40588 | CrpalkeGrfs[8].AlarmSurv2
STRCrpalkeGrfs8ControlSource | INT | IOD_STR_TCP | 589 | 40589 | CrpalkeGrfs[8].ControlSource
STRCrpalkeGrfs8ExternInputSetup | INT | IOD_STR_TCP | 590 | 40590 | CrpalkeGrfs[8].ExternInputSetup
STRCrpalkeGrfs8ExternInputsStatus | INT | IOD_STR_TCP | 591 | 40591 | CrpalkeGrfs[8].ExternInputsStatus
STRCrpalkeGrfs8LocalSetupMode1 | INT | IOD_STR_TCP | 592 | 40592 | CrpalkeGrfs[8].LocalSetupMode1
STRCrpalkeGrfs8PreklopkaMode | INT | IOD_STR_TCP | 593 | 40593 | CrpalkeGrfs[8].PreklopkaMode
STRCrpalkeGrfs8Relay1setup | INT | IOD_STR_TCP | 594 | 40594 | CrpalkeGrfs[8].Relay1setup
STRCrpalkeGrfs8RemoteSetupMode1 | INT | IOD_STR_TCP | 595 | 40595 | CrpalkeGrfs[8].RemoteSetupMode1
STRCrpalkeGrfs8StatusCrpalke | INT | IOD_STR_TCP | 596 | 40596 | CrpalkeGrfs[8].StatusCrpalke | BYTE
STRCrpalkeGrfs8StatusMode1 | INT | IOD_STR_TCP | 597 | 40597 | CrpalkeGrfs[8].StatusMode1
STRCrpalkeGrfs8StatusMode1co | INT | IOD_STR_TCP | 598 | 40598 | CrpalkeGrfs[8].StatusMode1co | BYTE
STRCrpalkeGrfs8StatusMode1op | INT | IOD_STR_TCP | 599 | 40599 | CrpalkeGrfs[8].StatusMode1op | BYTE
STRCrpalkeGrfs8StatusMode2 | INT | IOD_STR_TCP | 600 | 40600 | CrpalkeGrfs[8].StatusMode2
STRCrpalkeGrfs8StatusMode3 | INT | IOD_STR_TCP | 601 | 40601 | CrpalkeGrfs[8].StatusMode3
STRCrpalkeGrfs9AlarmActiveCode | INT | IOD_STR_TCP | 602 | 40602 | CrpalkeGrfs[9].AlarmActiveCode
STRCrpalkeGrfs9AlarmCodeLog1 | INT | IOD_STR_TCP | 603 | 40603 | CrpalkeGrfs[9].AlarmCodeLog1
STRCrpalkeGrfs9AlarmCodeLog2 | INT | IOD_STR_TCP | 604 | 40604 | CrpalkeGrfs[9].AlarmCodeLog2
STRCrpalkeGrfs9AlarmCodeLog3 | INT | IOD_STR_TCP | 605 | 40605 | CrpalkeGrfs[9].AlarmCodeLog3
STRCrpalkeGrfs9AlarmCodeLog4 | INT | IOD_STR_TCP | 606 | 40606 | CrpalkeGrfs[9].AlarmCodeLog4
STRCrpalkeGrfs9AlarmCodeLog5 | INT | IOD_STR_TCP | 607 | 40607 | CrpalkeGrfs[9].AlarmCodeLog5
STRCrpalkeGrfs9AlarmGroupXVH0 | INT | IOD_STR_TCP | 608 | 40608 | CrpalkeGrfs[9].AlarmGroupXVH[0]
STRCrpalkeGrfs9AlarmGroupXVH10 | INT | IOD_STR_TCP | 609 | 40609 | CrpalkeGrfs[9].AlarmGroupXVH[10]
STRCrpalkeGrfs9AlarmGroupXVH11 | INT | IOD_STR_TCP | 610 | 40610 | CrpalkeGrfs[9].AlarmGroupXVH[11]
STRCrpalkeGrfs9AlarmGroupXVH12 | INT | IOD_STR_TCP | 611 | 40611 | CrpalkeGrfs[9].AlarmGroupXVH[12]
STRCrpalkeGrfs9AlarmGroupXVH13 | INT | IOD_STR_TCP | 612 | 40612 | CrpalkeGrfs[9].AlarmGroupXVH[13]
STRCrpalkeGrfs9AlarmGroupXVH14 | INT | IOD_STR_TCP | 613 | 40613 | CrpalkeGrfs[9].AlarmGroupXVH[14]
STRCrpalkeGrfs9AlarmGroupXVH15 | INT | IOD_STR_TCP | 614 | 40614 | CrpalkeGrfs[9].AlarmGroupXVH[15]
STRCrpalkeGrfs9AlarmGroupXVH16 | INT | IOD_STR_TCP | 615 | 40615 | CrpalkeGrfs[9].AlarmGroupXVH[16]
STRCrpalkeGrfs9AlarmGroupXVH1 | INT | IOD_STR_TCP | 616 | 40616 | CrpalkeGrfs[9].AlarmGroupXVH[1]
STRCrpalkeGrfs9AlarmGroupXVH2 | INT | IOD_STR_TCP | 617 | 40617 | CrpalkeGrfs[9].AlarmGroupXVH[2]
STRCrpalkeGrfs9AlarmGroupXVH3 | INT | IOD_STR_TCP | 618 | 40618 | CrpalkeGrfs[9].AlarmGroupXVH[3]
STRCrpalkeGrfs9AlarmGroupXVH4 | INT | IOD_STR_TCP | 619 | 40619 | CrpalkeGrfs[9].AlarmGroupXVH[4]
STRCrpalkeGrfs9AlarmGroupXVH5 | INT | IOD_STR_TCP | 620 | 40620 | CrpalkeGrfs[9].AlarmGroupXVH[5]
STRCrpalkeGrfs9AlarmGroupXVH6 | INT | IOD_STR_TCP | 621 | 40621 | CrpalkeGrfs[9].AlarmGroupXVH[6]
STRCrpalkeGrfs9AlarmGroupXVH7 | INT | IOD_STR_TCP | 622 | 40622 | CrpalkeGrfs[9].AlarmGroupXVH[7]
STRCrpalkeGrfs9AlarmGroupXVH8 | INT | IOD_STR_TCP | 623 | 40623 | CrpalkeGrfs[9].AlarmGroupXVH[8]
STRCrpalkeGrfs9AlarmGroupXVH9 | INT | IOD_STR_TCP | 624 | 40624 | CrpalkeGrfs[9].AlarmGroupXVH[9]
STRCrpalkeGrfs9AlarmQSD1 | INT | IOD_STR_TCP | 625 | 40625 | CrpalkeGrfs[9].AlarmQSD1
STRCrpalkeGrfs9AlarmQSD2 | INT | IOD_STR_TCP | 626 | 40626 | CrpalkeGrfs[9].AlarmQSD2
STRCrpalkeGrfs9AlarmStart1 | INT | IOD_STR_TCP | 627 | 40627 | CrpalkeGrfs[9].AlarmStart1
STRCrpalkeGrfs9AlarmStart2 | INT | IOD_STR_TCP | 628 | 40628 | CrpalkeGrfs[9].AlarmStart2
STRCrpalkeGrfs9AlarmStop1 | INT | IOD_STR_TCP | 629 | 40629 | CrpalkeGrfs[9].AlarmStop1
STRCrpalkeGrfs9AlarmStop2 | INT | IOD_STR_TCP | 630 | 40630 | CrpalkeGrfs[9].AlarmStop2
STRCrpalkeGrfs9AlarmStop3 | INT | IOD_STR_TCP | 631 | 40631 | CrpalkeGrfs[9].AlarmStop3
STRCrpalkeGrfs9AlarmSurv1 | INT | IOD_STR_TCP | 632 | 40632 | CrpalkeGrfs[9].AlarmSurv1
STRCrpalkeGrfs9AlarmSurv2 | INT | IOD_STR_TCP | 633 | 40633 | CrpalkeGrfs[9].AlarmSurv2
STRCrpalkeGrfs9ControlSource | INT | IOD_STR_TCP | 634 | 40634 | CrpalkeGrfs[9].ControlSource
STRCrpalkeGrfs9ExternInputSetup | INT | IOD_STR_TCP | 635 | 40635 | CrpalkeGrfs[9].ExternInputSetup
STRCrpalkeGrfs9ExternInputsStatus | INT | IOD_STR_TCP | 636 | 40636 | CrpalkeGrfs[9].ExternInputsStatus
STRCrpalkeGrfs9LocalSetupMode1 | INT | IOD_STR_TCP | 637 | 40637 | CrpalkeGrfs[9].LocalSetupMode1
STRCrpalkeGrfs9PreklopkaMode | INT | IOD_STR_TCP | 638 | 40638 | CrpalkeGrfs[9].PreklopkaMode
STRCrpalkeGrfs9Relay1setup | INT | IOD_STR_TCP | 639 | 40639 | CrpalkeGrfs[9].Relay1setup
STRCrpalkeGrfs9RemoteSetupMode1 | INT | IOD_STR_TCP | 640 | 40640 | CrpalkeGrfs[9].RemoteSetupMode1
STRCrpalkeGrfs9StatusCrpalke | INT | IOD_STR_TCP | 641 | 40641 | CrpalkeGrfs[9].StatusCrpalke | BYTE
STRCrpalkeGrfs9StatusMode1 | INT | IOD_STR_TCP | 642 | 40642 | CrpalkeGrfs[9].StatusMode1
STRCrpalkeGrfs9StatusMode1co | INT | IOD_STR_TCP | 643 | 40643 | CrpalkeGrfs[9].StatusMode1co | BYTE
STRCrpalkeGrfs9StatusMode1op | INT | IOD_STR_TCP | 644 | 40644 | CrpalkeGrfs[9].StatusMode1op | BYTE
STRCrpalkeGrfs9StatusMode2 | INT | IOD_STR_TCP | 645 | 40645 | CrpalkeGrfs[9].StatusMode2
STRCrpalkeGrfs9StatusMode3 | INT | IOD_STR_TCP | 646 | 40646 | CrpalkeGrfs[9].StatusMode3
STRDateTimeDan | INT | IOD_STR_TCP | 647 | 40647 | DateTime.Dan | BYTE
STRDateTimeLeto | INT | IOD_STR_TCP | 648 | 40648 | DateTime.Leto | BYTE
STRDateTimeMesec | INT | IOD_STR_TCP | 649 | 40649 | DateTime.Mesec | BYTE
STRDateTimeMinuta | INT | IOD_STR_TCP | 650 | 40650 | DateTime.Minuta | BYTE
STRDateTimeSekunda | INT | IOD_STR_TCP | 651 | 40651 | DateTime.Sekunda | BYTE
STRDateTimeUra | INT | IOD_STR_TCP | 652 | 40652 | DateTime.Ura | BYTE
STRHladStrojKompresorOljeAlarmB | INT | IOD_STR_TCP | 653 | 40653 | HladStroj.KompresorOljeAlarmB | BYTE
STRHladStrojNizekPritiskAlarmB | INT | IOD_STR_TCP | 654 | 40654 | HladStroj.NizekPritiskAlarmB | BYTE
STRHladStrojObratovalneUreOpozoriloB | INT | IOD_STR_TCP | 655 | 40655 | HladStroj.ObratovalneUreOpozoriloB | BYTE
STRHladStrojTemperaturaAlarmB | INT | IOD_STR_TCP | 656 | 40656 | HladStroj.TemperaturaAlarmB | BYTE
STRHladStrojUnitStatus | INT | IOD_STR_TCP | 657 | 40657 | HladStroj.UnitStatus
STRHladStrojVisokPritiskAlarmB | INT | IOD_STR_TCP | 658 | 40658 | HladStroj.VisokPritiskAlarmB | BYTE
STRHladStrojVisokPritiskOpozoriloB | INT | IOD_STR_TCP | 659 | 40659 | HladStroj.VisokPritiskOpozoriloB | BYTE
STRHladStrojZmrzalniAlarmB | INT | IOD_STR_TCP | 660 | 40660 | HladStroj.ZmrzalniAlarmB | BYTE
STRKlima1CrpalkaStatus | INT | IOD_STR_TCP | 661 | 40661 | Klima[1].CrpalkaStatus | BYTE
STRKlima1HitrostVentStatus | INT | IOD_STR_TCP | 662 | 40662 | Klima[1].HitrostVentStatus | BYTE
STRKlima1IzhodniVentStatus | INT | IOD_STR_TCP | 663 | 40663 | Klima[1].IzhodniVentStatus | BYTE
STRKlima2CrpalkaStatus | INT | IOD_STR_TCP | 664 | 40664 | Klima[2].CrpalkaStatus | BYTE
STRKlima2HitrostVentStatus | INT | IOD_STR_TCP | 665 | 40665 | Klima[2].HitrostVentStatus | BYTE
STRKlima2IzhodniVentStatus | INT | IOD_STR_TCP | 666 | 40666 | Klima[2].IzhodniVentStatus | BYTE
STRPozarnaLoputaStatus1 | INT | IOD_STR_TCP | 667 | 40667 | PozarnaLoputaStatus[1] | BYTE
STRPozarnaLoputaStatus2 | INT | IOD_STR_TCP | 668 | 40668 | PozarnaLoputaStatus[2] | BYTE
STRPozarnaLoputaStatus3 | INT | IOD_STR_TCP | 669 | 40669 | PozarnaLoputaStatus[3] | BYTE
STRPozarnaLoputaStatus4 | INT | IOD_STR_TCP | 670 | 40670 | PozarnaLoputaStatus[4] | BYTE
STRPozarnaLoputaStatus5 | INT | IOD_STR_TCP | 671 | 40671 | PozarnaLoputaStatus[5] | BYTE
STRStatusKondenzEnota0 | INT | IOD_STR_TCP | 672 | 40672 | StatusKondenzEnota[0] | BYTE
STRStatusKondenzEnota1 | INT | IOD_STR_TCP | 673 | 40673 | StatusKondenzEnota[1] | BYTE
STRStatusKondenzEnota2 | INT | IOD_STR_TCP | 674 | 40674 | StatusKondenzEnota[2] | BYTE
STRStatusKondenzEnota3 | INT | IOD_STR_TCP | 675 | 40675 | StatusKondenzEnota[3] | BYTE
STRStatusKontaktor10 | INT | IOD_STR_TCP | 676 | 40676 | StatusKontaktor[10] | BYTE
STRStatusKontaktor11 | INT | IOD_STR_TCP | 677 | 40677 | StatusKontaktor[11] | BYTE
STRStatusKontaktor12 | INT | IOD_STR_TCP | 678 | 40678 | StatusKontaktor[12] | BYTE
STRStatusKontaktor13 | INT | IOD_STR_TCP | 679 | 40679 | StatusKontaktor[13] | BYTE
STRStatusKontaktor14 | INT | IOD_STR_TCP | 680 | 40680 | StatusKontaktor[14] | BYTE
STRStatusKontaktor15 | INT | IOD_STR_TCP | 681 | 40681 | StatusKontaktor[15] | BYTE
STRStatusKontaktor16 | INT | IOD_STR_TCP | 682 | 40682 | StatusKontaktor[16] | BYTE
STRStatusKontaktor17 | INT | IOD_STR_TCP | 683 | 40683 | StatusKontaktor[17] | BYTE
STRStatusKontaktor18 | INT | IOD_STR_TCP | 684 | 40684 | StatusKontaktor[18] | BYTE
STRStatusKontaktor19 | INT | IOD_STR_TCP | 685 | 40685 | StatusKontaktor[19] | BYTE
STRStatusKontaktor1 | INT | IOD_STR_TCP | 686 | 40686 | StatusKontaktor[1] | BYTE
STRStatusKontaktor20 | INT | IOD_STR_TCP | 687 | 40687 | StatusKontaktor[20] | BYTE
STRStatusKontaktor21 | INT | IOD_STR_TCP | 688 | 40688 | StatusKontaktor[21] | BYTE
STRStatusKontaktor22 | INT | IOD_STR_TCP | 689 | 40689 | StatusKontaktor[22] | BYTE
STRStatusKontaktor23 | INT | IOD_STR_TCP | 690 | 40690 | StatusKontaktor[23] | BYTE
STRStatusKontaktor24 | INT | IOD_STR_TCP | 691 | 40691 | StatusKontaktor[24] | BYTE
STRStatusKontaktor25 | INT | IOD_STR_TCP | 692 | 40692 | StatusKontaktor[25] | BYTE
STRStatusKontaktor2 | INT | IOD_STR_TCP | 693 | 40693 | StatusKontaktor[2] | BYTE
STRStatusKontaktor3 | INT | IOD_STR_TCP | 694 | 40694 | StatusKontaktor[3] | BYTE
STRStatusKontaktor4 | INT | IOD_STR_TCP | 695 | 40695 | StatusKontaktor[4] | BYTE
STRStatusKontaktor5 | INT | IOD_STR_TCP | 696 | 40696 | StatusKontaktor[5] | BYTE
STRStatusKontaktor6 | INT | IOD_STR_TCP | 697 | 40697 | StatusKontaktor[6] | BYTE
STRStatusKontaktor7 | INT | IOD_STR_TCP | 698 | 40698 | StatusKontaktor[7] | BYTE
STRStatusKontaktor8 | INT | IOD_STR_TCP | 699 | 40699 | StatusKontaktor[8] | BYTE
STRStatusKontaktor9 | INT | IOD_STR_TCP | 700 | 40700 | StatusKontaktor[9] | BYTE
STRStatusPreklopke10 | INT | IOD_STR_TCP | 701 | 40701 | StatusPreklopke[10] | BYTE
STRStatusPreklopke11 | INT | IOD_STR_TCP | 702 | 40702 | StatusPreklopke[11] | BYTE
STRStatusPreklopke12 | INT | IOD_STR_TCP | 703 | 40703 | StatusPreklopke[12] | BYTE
STRStatusPreklopke13 | INT | IOD_STR_TCP | 704 | 40704 | StatusPreklopke[13] | BYTE
STRStatusPreklopke14 | INT | IOD_STR_TCP | 705 | 40705 | StatusPreklopke[14] | BYTE
STRStatusPreklopke15 | INT | IOD_STR_TCP | 706 | 40706 | StatusPreklopke[15] | BYTE
STRStatusPreklopke16 | INT | IOD_STR_TCP | 707 | 40707 | StatusPreklopke[16] | BYTE
STRStatusPreklopke17 | INT | IOD_STR_TCP | 708 | 40708 | StatusPreklopke[17] | BYTE
STRStatusPreklopke18 | INT | IOD_STR_TCP | 709 | 40709 | StatusPreklopke[18] | BYTE
STRStatusPreklopke19 | INT | IOD_STR_TCP | 710 | 40710 | StatusPreklopke[19] | BYTE
STRStatusPreklopke1 | INT | IOD_STR_TCP | 711 | 40711 | StatusPreklopke[1] | BYTE
STRStatusPreklopke20 | INT | IOD_STR_TCP | 712 | 40712 | StatusPreklopke[20] | BYTE
STRStatusPreklopke21 | INT | IOD_STR_TCP | 713 | 40713 | StatusPreklopke[21] | BYTE
STRStatusPreklopke22 | INT | IOD_STR_TCP | 714 | 40714 | StatusPreklopke[22] | BYTE
STRStatusPreklopke23 | INT | IOD_STR_TCP | 715 | 40715 | StatusPreklopke[23] | BYTE
STRStatusPreklopke24 | INT | IOD_STR_TCP | 716 | 40716 | StatusPreklopke[24] | BYTE
STRStatusPreklopke25 | INT | IOD_STR_TCP | 717 | 40717 | StatusPreklopke[25] | BYTE
STRStatusPreklopke2 | INT | IOD_STR_TCP | 718 | 40718 | StatusPreklopke[2] | BYTE
STRStatusPreklopke3 | INT | IOD_STR_TCP | 719 | 40719 | StatusPreklopke[3] | BYTE
STRStatusPreklopke4 | INT | IOD_STR_TCP | 720 | 40720 | StatusPreklopke[4] | BYTE
STRStatusPreklopke5 | INT | IOD_STR_TCP | 721 | 40721 | StatusPreklopke[5] | BYTE
STRStatusPreklopke6 | INT | IOD_STR_TCP | 722 | 40722 | StatusPreklopke[6] | BYTE
STRStatusPreklopke7 | INT | IOD_STR_TCP | 723 | 40723 | StatusPreklopke[7] | BYTE
STRStatusPreklopke8 | INT | IOD_STR_TCP | 724 | 40724 | StatusPreklopke[8] | BYTE
STRStatusPreklopke9 | INT | IOD_STR_TCP | 725 | 40725 | StatusPreklopke[9] | BYTE
STRToplPostNapakaRegister | INT | IOD_STR_TCP | 726 | 40726 | ToplPost.NapakaRegister
STRUrnik_SCtoXCpot | INT | IOD_STR_TCP | 727 | 40727 | Urnik_SCtoXCpot
STRUrnik_SCtoXCzah | INT | IOD_STR_TCP | 728 | 40728 | Urnik_SCtoXCzah
STRUrnik_XCtoSCpot | INT | IOD_STR_TCP | 729 | 40729 | Urnik_XCtoSCpot
STRUrnik_XCtoSCzah | INT | IOD_STR_TCP | 730 | 40730 | Urnik_XCtoSCzah
STRUrnikSCtoXCDan1Off1Mna | INT | IOD_STR_TCP | 731 | 40731 | UrnikSCtoXC.Dan[1].Off[1].Mna | BYTE
STRUrnikSCtoXCDan1Off1Ura | INT | IOD_STR_TCP | 732 | 40732 | UrnikSCtoXC.Dan[1].Off[1].Ura | BYTE
STRUrnikSCtoXCDan1Off2Mna | INT | IOD_STR_TCP | 733 | 40733 | UrnikSCtoXC.Dan[1].Off[2].Mna | BYTE
STRUrnikSCtoXCDan1Off2Ura | INT | IOD_STR_TCP | 734 | 40734 | UrnikSCtoXC.Dan[1].Off[2].Ura | BYTE
STRUrnikSCtoXCDan1Off3Mna | INT | IOD_STR_TCP | 735 | 40735 | UrnikSCtoXC.Dan[1].Off[3].Mna | BYTE
STRUrnikSCtoXCDan1Off3Ura | INT | IOD_STR_TCP | 736 | 40736 | UrnikSCtoXC.Dan[1].Off[3].Ura | BYTE
STRUrnikSCtoXCDan1On1Mna | INT | IOD_STR_TCP | 737 | 40737 | UrnikSCtoXC.Dan[1].On[1].Mna | BYTE
STRUrnikSCtoXCDan1On1Ura | INT | IOD_STR_TCP | 738 | 40738 | UrnikSCtoXC.Dan[1].On[1].Ura | BYTE
STRUrnikSCtoXCDan1On2Mna | INT | IOD_STR_TCP | 739 | 40739 | UrnikSCtoXC.Dan[1].On[2].Mna | BYTE
STRUrnikSCtoXCDan1On2Ura | INT | IOD_STR_TCP | 740 | 40740 | UrnikSCtoXC.Dan[1].On[2].Ura | BYTE
STRUrnikSCtoXCDan1On3Mna | INT | IOD_STR_TCP | 741 | 40741 | UrnikSCtoXC.Dan[1].On[3].Mna | BYTE
STRUrnikSCtoXCDan1On3Ura | INT | IOD_STR_TCP | 742 | 40742 | UrnikSCtoXC.Dan[1].On[3].Ura | BYTE
STRUrnikSCtoXCDan2Off1Mna | INT | IOD_STR_TCP | 743 | 40743 | UrnikSCtoXC.Dan[2].Off[1].Mna | BYTE
STRUrnikSCtoXCDan2Off1Ura | INT | IOD_STR_TCP | 744 | 40744 | UrnikSCtoXC.Dan[2].Off[1].Ura | BYTE
STRUrnikSCtoXCDan2Off2Mna | INT | IOD_STR_TCP | 745 | 40745 | UrnikSCtoXC.Dan[2].Off[2].Mna | BYTE
STRUrnikSCtoXCDan2Off2Ura | INT | IOD_STR_TCP | 746 | 40746 | UrnikSCtoXC.Dan[2].Off[2].Ura | BYTE
STRUrnikSCtoXCDan2Off3Mna | INT | IOD_STR_TCP | 747 | 40747 | UrnikSCtoXC.Dan[2].Off[3].Mna | BYTE
STRUrnikSCtoXCDan2Off3Ura | INT | IOD_STR_TCP | 748 | 40748 | UrnikSCtoXC.Dan[2].Off[3].Ura | BYTE
STRUrnikSCtoXCDan2On1Mna | INT | IOD_STR_TCP | 749 | 40749 | UrnikSCtoXC.Dan[2].On[1].Mna | BYTE
STRUrnikSCtoXCDan2On1Ura | INT | IOD_STR_TCP | 750 | 40750 | UrnikSCtoXC.Dan[2].On[1].Ura | BYTE
STRUrnikSCtoXCDan2On2Mna | INT | IOD_STR_TCP | 751 | 40751 | UrnikSCtoXC.Dan[2].On[2].Mna | BYTE
STRUrnikSCtoXCDan2On2Ura | INT | IOD_STR_TCP | 752 | 40752 | UrnikSCtoXC.Dan[2].On[2].Ura | BYTE
STRUrnikSCtoXCDan2On3Mna | INT | IOD_STR_TCP | 753 | 40753 | UrnikSCtoXC.Dan[2].On[3].Mna | BYTE
STRUrnikSCtoXCDan2On3Ura | INT | IOD_STR_TCP | 754 | 40754 | UrnikSCtoXC.Dan[2].On[3].Ura | BYTE
STRUrnikSCtoXCDan3Off1Mna | INT | IOD_STR_TCP | 755 | 40755 | UrnikSCtoXC.Dan[3].Off[1].Mna | BYTE
STRUrnikSCtoXCDan3Off1Ura | INT | IOD_STR_TCP | 756 | 40756 | UrnikSCtoXC.Dan[3].Off[1].Ura | BYTE
STRUrnikSCtoXCDan3Off2Mna | INT | IOD_STR_TCP | 757 | 40757 | UrnikSCtoXC.Dan[3].Off[2].Mna | BYTE
STRUrnikSCtoXCDan3Off2Ura | INT | IOD_STR_TCP | 758 | 40758 | UrnikSCtoXC.Dan[3].Off[2].Ura | BYTE
STRUrnikSCtoXCDan3Off3Mna | INT | IOD_STR_TCP | 759 | 40759 | UrnikSCtoXC.Dan[3].Off[3].Mna | BYTE
STRUrnikSCtoXCDan3Off3Ura | INT | IOD_STR_TCP | 760 | 40760 | UrnikSCtoXC.Dan[3].Off[3].Ura | BYTE
STRUrnikSCtoXCDan3On1Mna | INT | IOD_STR_TCP | 761 | 40761 | UrnikSCtoXC.Dan[3].On[1].Mna | BYTE
STRUrnikSCtoXCDan3On1Ura | INT | IOD_STR_TCP | 762 | 40762 | UrnikSCtoXC.Dan[3].On[1].Ura | BYTE
STRUrnikSCtoXCDan3On2Mna | INT | IOD_STR_TCP | 763 | 40763 | UrnikSCtoXC.Dan[3].On[2].Mna | BYTE
STRUrnikSCtoXCDan3On2Ura | INT | IOD_STR_TCP | 764 | 40764 | UrnikSCtoXC.Dan[3].On[2].Ura | BYTE
STRUrnikSCtoXCDan3On3Mna | INT | IOD_STR_TCP | 765 | 40765 | UrnikSCtoXC.Dan[3].On[3].Mna | BYTE
STRUrnikSCtoXCDan3On3Ura | INT | IOD_STR_TCP | 766 | 40766 | UrnikSCtoXC.Dan[3].On[3].Ura | BYTE
STRUrnikSCtoXCDan4Off1Mna | INT | IOD_STR_TCP | 767 | 40767 | UrnikSCtoXC.Dan[4].Off[1].Mna | BYTE
STRUrnikSCtoXCDan4Off1Ura | INT | IOD_STR_TCP | 768 | 40768 | UrnikSCtoXC.Dan[4].Off[1].Ura | BYTE
STRUrnikSCtoXCDan4Off2Mna | INT | IOD_STR_TCP | 769 | 40769 | UrnikSCtoXC.Dan[4].Off[2].Mna | BYTE
STRUrnikSCtoXCDan4Off2Ura | INT | IOD_STR_TCP | 770 | 40770 | UrnikSCtoXC.Dan[4].Off[2].Ura | BYTE
STRUrnikSCtoXCDan4Off3Mna | INT | IOD_STR_TCP | 771 | 40771 | UrnikSCtoXC.Dan[4].Off[3].Mna | BYTE
STRUrnikSCtoXCDan4Off3Ura | INT | IOD_STR_TCP | 772 | 40772 | UrnikSCtoXC.Dan[4].Off[3].Ura | BYTE
STRUrnikSCtoXCDan4On1Mna | INT | IOD_STR_TCP | 773 | 40773 | UrnikSCtoXC.Dan[4].On[1].Mna | BYTE
STRUrnikSCtoXCDan4On1Ura | INT | IOD_STR_TCP | 774 | 40774 | UrnikSCtoXC.Dan[4].On[1].Ura | BYTE
STRUrnikSCtoXCDan4On2Mna | INT | IOD_STR_TCP | 775 | 40775 | UrnikSCtoXC.Dan[4].On[2].Mna | BYTE
STRUrnikSCtoXCDan4On2Ura | INT | IOD_STR_TCP | 776 | 40776 | UrnikSCtoXC.Dan[4].On[2].Ura | BYTE
STRUrnikSCtoXCDan4On3Mna | INT | IOD_STR_TCP | 777 | 40777 | UrnikSCtoXC.Dan[4].On[3].Mna | BYTE
STRUrnikSCtoXCDan4On3Ura | INT | IOD_STR_TCP | 778 | 40778 | UrnikSCtoXC.Dan[4].On[3].Ura | BYTE
STRUrnikSCtoXCDan5Off1Mna | INT | IOD_STR_TCP | 779 | 40779 | UrnikSCtoXC.Dan[5].Off[1].Mna | BYTE
STRUrnikSCtoXCDan5Off1Ura | INT | IOD_STR_TCP | 780 | 40780 | UrnikSCtoXC.Dan[5].Off[1].Ura | BYTE
STRUrnikSCtoXCDan5Off2Mna | INT | IOD_STR_TCP | 781 | 40781 | UrnikSCtoXC.Dan[5].Off[2].Mna | BYTE
STRUrnikSCtoXCDan5Off2Ura | INT | IOD_STR_TCP | 782 | 40782 | UrnikSCtoXC.Dan[5].Off[2].Ura | BYTE
STRUrnikSCtoXCDan5Off3Mna | INT | IOD_STR_TCP | 783 | 40783 | UrnikSCtoXC.Dan[5].Off[3].Mna | BYTE
STRUrnikSCtoXCDan5Off3Ura | INT | IOD_STR_TCP | 784 | 40784 | UrnikSCtoXC.Dan[5].Off[3].Ura | BYTE
STRUrnikSCtoXCDan5On1Mna | INT | IOD_STR_TCP | 785 | 40785 | UrnikSCtoXC.Dan[5].On[1].Mna | BYTE
STRUrnikSCtoXCDan5On1Ura | INT | IOD_STR_TCP | 786 | 40786 | UrnikSCtoXC.Dan[5].On[1].Ura | BYTE
STRUrnikSCtoXCDan5On2Mna | INT | IOD_STR_TCP | 787 | 40787 | UrnikSCtoXC.Dan[5].On[2].Mna | BYTE
STRUrnikSCtoXCDan5On2Ura | INT | IOD_STR_TCP | 788 | 40788 | UrnikSCtoXC.Dan[5].On[2].Ura | BYTE
STRUrnikSCtoXCDan5On3Mna | INT | IOD_STR_TCP | 789 | 40789 | UrnikSCtoXC.Dan[5].On[3].Mna | BYTE
STRUrnikSCtoXCDan5On3Ura | INT | IOD_STR_TCP | 790 | 40790 | UrnikSCtoXC.Dan[5].On[3].Ura | BYTE
STRUrnikSCtoXCDan6Off1Mna | INT | IOD_STR_TCP | 791 | 40791 | UrnikSCtoXC.Dan[6].Off[1].Mna | BYTE
STRUrnikSCtoXCDan6Off1Ura | INT | IOD_STR_TCP | 792 | 40792 | UrnikSCtoXC.Dan[6].Off[1].Ura | BYTE
STRUrnikSCtoXCDan6Off2Mna | INT | IOD_STR_TCP | 793 | 40793 | UrnikSCtoXC.Dan[6].Off[2].Mna | BYTE
STRUrnikSCtoXCDan6Off2Ura | INT | IOD_STR_TCP | 794 | 40794 | UrnikSCtoXC.Dan[6].Off[2].Ura | BYTE
STRUrnikSCtoXCDan6Off3Mna | INT | IOD_STR_TCP | 795 | 40795 | UrnikSCtoXC.Dan[6].Off[3].Mna | BYTE
STRUrnikSCtoXCDan6Off3Ura | INT | IOD_STR_TCP | 796 | 40796 | UrnikSCtoXC.Dan[6].Off[3].Ura | BYTE
STRUrnikSCtoXCDan6On1Mna | INT | IOD_STR_TCP | 797 | 40797 | UrnikSCtoXC.Dan[6].On[1].Mna | BYTE
STRUrnikSCtoXCDan6On1Ura | INT | IOD_STR_TCP | 798 | 40798 | UrnikSCtoXC.Dan[6].On[1].Ura | BYTE
STRUrnikSCtoXCDan6On2Mna | INT | IOD_STR_TCP | 799 | 40799 | UrnikSCtoXC.Dan[6].On[2].Mna | BYTE
STRUrnikSCtoXCDan6On2Ura | INT | IOD_STR_TCP | 800 | 40800 | UrnikSCtoXC.Dan[6].On[2].Ura | BYTE
STRUrnikSCtoXCDan6On3Mna | INT | IOD_STR_TCP | 801 | 40801 | UrnikSCtoXC.Dan[6].On[3].Mna | BYTE
STRUrnikSCtoXCDan6On3Ura | INT | IOD_STR_TCP | 802 | 40802 | UrnikSCtoXC.Dan[6].On[3].Ura | BYTE
STRUrnikSCtoXCDan7Off1Mna | INT | IOD_STR_TCP | 803 | 40803 | UrnikSCtoXC.Dan[7].Off[1].Mna | BYTE
STRUrnikSCtoXCDan7Off1Ura | INT | IOD_STR_TCP | 804 | 40804 | UrnikSCtoXC.Dan[7].Off[1].Ura | BYTE
STRUrnikSCtoXCDan7Off2Mna | INT | IOD_STR_TCP | 805 | 40805 | UrnikSCtoXC.Dan[7].Off[2].Mna | BYTE
STRUrnikSCtoXCDan7Off2Ura | INT | IOD_STR_TCP | 806 | 40806 | UrnikSCtoXC.Dan[7].Off[2].Ura | BYTE
STRUrnikSCtoXCDan7Off3Mna | INT | IOD_STR_TCP | 807 | 40807 | UrnikSCtoXC.Dan[7].Off[3].Mna | BYTE
STRUrnikSCtoXCDan7Off3Ura | INT | IOD_STR_TCP | 808 | 40808 | UrnikSCtoXC.Dan[7].Off[3].Ura | BYTE
STRUrnikSCtoXCDan7On1Mna | INT | IOD_STR_TCP | 809 | 40809 | UrnikSCtoXC.Dan[7].On[1].Mna | BYTE
STRUrnikSCtoXCDan7On1Ura | INT | IOD_STR_TCP | 810 | 40810 | UrnikSCtoXC.Dan[7].On[1].Ura | BYTE
STRUrnikSCtoXCDan7On2Mna | INT | IOD_STR_TCP | 811 | 40811 | UrnikSCtoXC.Dan[7].On[2].Mna | BYTE
STRUrnikSCtoXCDan7On2Ura | INT | IOD_STR_TCP | 812 | 40812 | UrnikSCtoXC.Dan[7].On[2].Ura | BYTE
STRUrnikSCtoXCDan7On3Mna | INT | IOD_STR_TCP | 813 | 40813 | UrnikSCtoXC.Dan[7].On[3].Mna | BYTE
STRUrnikSCtoXCDan7On3Ura | INT | IOD_STR_TCP | 814 | 40814 | UrnikSCtoXC.Dan[7].On[3].Ura | BYTE
STRUrnikXCtoSCDan1Off1Mna | INT | IOD_STR_TCP | 815 | 40815 | UrnikXCtoSC.Dan[1].Off[1].Mna | BYTE
STRUrnikXCtoSCDan1Off1Ura | INT | IOD_STR_TCP | 816 | 40816 | UrnikXCtoSC.Dan[1].Off[1].Ura | BYTE
STRUrnikXCtoSCDan1Off2Mna | INT | IOD_STR_TCP | 817 | 40817 | UrnikXCtoSC.Dan[1].Off[2].Mna | BYTE
STRUrnikXCtoSCDan1Off2Ura | INT | IOD_STR_TCP | 818 | 40818 | UrnikXCtoSC.Dan[1].Off[2].Ura | BYTE
STRUrnikXCtoSCDan1Off3Mna | INT | IOD_STR_TCP | 819 | 40819 | UrnikXCtoSC.Dan[1].Off[3].Mna | BYTE
STRUrnikXCtoSCDan1Off3Ura | INT | IOD_STR_TCP | 820 | 40820 | UrnikXCtoSC.Dan[1].Off[3].Ura | BYTE
STRUrnikXCtoSCDan1On1Mna | INT | IOD_STR_TCP | 821 | 40821 | UrnikXCtoSC.Dan[1].On[1].Mna | BYTE
STRUrnikXCtoSCDan1On1Ura | INT | IOD_STR_TCP | 822 | 40822 | UrnikXCtoSC.Dan[1].On[1].Ura | BYTE
STRUrnikXCtoSCDan1On2Mna | INT | IOD_STR_TCP | 823 | 40823 | UrnikXCtoSC.Dan[1].On[2].Mna | BYTE
STRUrnikXCtoSCDan1On2Ura | INT | IOD_STR_TCP | 824 | 40824 | UrnikXCtoSC.Dan[1].On[2].Ura | BYTE
STRUrnikXCtoSCDan1On3Mna | INT | IOD_STR_TCP | 825 | 40825 | UrnikXCtoSC.Dan[1].On[3].Mna | BYTE
STRUrnikXCtoSCDan1On3Ura | INT | IOD_STR_TCP | 826 | 40826 | UrnikXCtoSC.Dan[1].On[3].Ura | BYTE
STRUrnikXCtoSCDan2Off1Mna | INT | IOD_STR_TCP | 827 | 40827 | UrnikXCtoSC.Dan[2].Off[1].Mna | BYTE
STRUrnikXCtoSCDan2Off1Ura | INT | IOD_STR_TCP | 828 | 40828 | UrnikXCtoSC.Dan[2].Off[1].Ura | BYTE
STRUrnikXCtoSCDan2Off2Mna | INT | IOD_STR_TCP | 829 | 40829 | UrnikXCtoSC.Dan[2].Off[2].Mna | BYTE
STRUrnikXCtoSCDan2Off2Ura | INT | IOD_STR_TCP | 830 | 40830 | UrnikXCtoSC.Dan[2].Off[2].Ura | BYTE
STRUrnikXCtoSCDan2Off3Mna | INT | IOD_STR_TCP | 831 | 40831 | UrnikXCtoSC.Dan[2].Off[3].Mna | BYTE
STRUrnikXCtoSCDan2Off3Ura | INT | IOD_STR_TCP | 832 | 40832 | UrnikXCtoSC.Dan[2].Off[3].Ura | BYTE
STRUrnikXCtoSCDan2On1Mna | INT | IOD_STR_TCP | 833 | 40833 | UrnikXCtoSC.Dan[2].On[1].Mna | BYTE
STRUrnikXCtoSCDan2On1Ura | INT | IOD_STR_TCP | 834 | 40834 | UrnikXCtoSC.Dan[2].On[1].Ura | BYTE
STRUrnikXCtoSCDan2On2Mna | INT | IOD_STR_TCP | 835 | 40835 | UrnikXCtoSC.Dan[2].On[2].Mna | BYTE
STRUrnikXCtoSCDan2On2Ura | INT | IOD_STR_TCP | 836 | 40836 | UrnikXCtoSC.Dan[2].On[2].Ura | BYTE
STRUrnikXCtoSCDan2On3Mna | INT | IOD_STR_TCP | 837 | 40837 | UrnikXCtoSC.Dan[2].On[3].Mna | BYTE
STRUrnikXCtoSCDan2On3Ura | INT | IOD_STR_TCP | 838 | 40838 | UrnikXCtoSC.Dan[2].On[3].Ura | BYTE
STRUrnikXCtoSCDan3Off1Mna | INT | IOD_STR_TCP | 839 | 40839 | UrnikXCtoSC.Dan[3].Off[1].Mna | BYTE
STRUrnikXCtoSCDan3Off1Ura | INT | IOD_STR_TCP | 840 | 40840 | UrnikXCtoSC.Dan[3].Off[1].Ura | BYTE
STRUrnikXCtoSCDan3Off2Mna | INT | IOD_STR_TCP | 841 | 40841 | UrnikXCtoSC.Dan[3].Off[2].Mna | BYTE
STRUrnikXCtoSCDan3Off2Ura | INT | IOD_STR_TCP | 842 | 40842 | UrnikXCtoSC.Dan[3].Off[2].Ura | BYTE
STRUrnikXCtoSCDan3Off3Mna | INT | IOD_STR_TCP | 843 | 40843 | UrnikXCtoSC.Dan[3].Off[3].Mna | BYTE
STRUrnikXCtoSCDan3Off3Ura | INT | IOD_STR_TCP | 844 | 40844 | UrnikXCtoSC.Dan[3].Off[3].Ura | BYTE
STRUrnikXCtoSCDan3On1Mna | INT | IOD_STR_TCP | 845 | 40845 | UrnikXCtoSC.Dan[3].On[1].Mna | BYTE
STRUrnikXCtoSCDan3On1Ura | INT | IOD_STR_TCP | 846 | 40846 | UrnikXCtoSC.Dan[3].On[1].Ura | BYTE
STRUrnikXCtoSCDan3On2Mna | INT | IOD_STR_TCP | 847 | 40847 | UrnikXCtoSC.Dan[3].On[2].Mna | BYTE
STRUrnikXCtoSCDan3On2Ura | INT | IOD_STR_TCP | 848 | 40848 | UrnikXCtoSC.Dan[3].On[2].Ura | BYTE
STRUrnikXCtoSCDan3On3Mna | INT | IOD_STR_TCP | 849 | 40849 | UrnikXCtoSC.Dan[3].On[3].Mna | BYTE
STRUrnikXCtoSCDan3On3Ura | INT | IOD_STR_TCP | 850 | 40850 | UrnikXCtoSC.Dan[3].On[3].Ura | BYTE
STRUrnikXCtoSCDan4Off1Mna | INT | IOD_STR_TCP | 851 | 40851 | UrnikXCtoSC.Dan[4].Off[1].Mna | BYTE
STRUrnikXCtoSCDan4Off1Ura | INT | IOD_STR_TCP | 852 | 40852 | UrnikXCtoSC.Dan[4].Off[1].Ura | BYTE
STRUrnikXCtoSCDan4Off2Mna | INT | IOD_STR_TCP | 853 | 40853 | UrnikXCtoSC.Dan[4].Off[2].Mna | BYTE
STRUrnikXCtoSCDan4Off2Ura | INT | IOD_STR_TCP | 854 | 40854 | UrnikXCtoSC.Dan[4].Off[2].Ura | BYTE
STRUrnikXCtoSCDan4Off3Mna | INT | IOD_STR_TCP | 855 | 40855 | UrnikXCtoSC.Dan[4].Off[3].Mna | BYTE
STRUrnikXCtoSCDan4Off3Ura | INT | IOD_STR_TCP | 856 | 40856 | UrnikXCtoSC.Dan[4].Off[3].Ura | BYTE
STRUrnikXCtoSCDan4On1Mna | INT | IOD_STR_TCP | 857 | 40857 | UrnikXCtoSC.Dan[4].On[1].Mna | BYTE
STRUrnikXCtoSCDan4On1Ura | INT | IOD_STR_TCP | 858 | 40858 | UrnikXCtoSC.Dan[4].On[1].Ura | BYTE
STRUrnikXCtoSCDan4On2Mna | INT | IOD_STR_TCP | 859 | 40859 | UrnikXCtoSC.Dan[4].On[2].Mna | BYTE
STRUrnikXCtoSCDan4On2Ura | INT | IOD_STR_TCP | 860 | 40860 | UrnikXCtoSC.Dan[4].On[2].Ura | BYTE
STRUrnikXCtoSCDan4On3Mna | INT | IOD_STR_TCP | 861 | 40861 | UrnikXCtoSC.Dan[4].On[3].Mna | BYTE
STRUrnikXCtoSCDan4On3Ura | INT | IOD_STR_TCP | 862 | 40862 | UrnikXCtoSC.Dan[4].On[3].Ura | BYTE
STRUrnikXCtoSCDan5Off1Mna | INT | IOD_STR_TCP | 863 | 40863 | UrnikXCtoSC.Dan[5].Off[1].Mna | BYTE
STRUrnikXCtoSCDan5Off1Ura | INT | IOD_STR_TCP | 864 | 40864 | UrnikXCtoSC.Dan[5].Off[1].Ura | BYTE
STRUrnikXCtoSCDan5Off2Mna | INT | IOD_STR_TCP | 865 | 40865 | UrnikXCtoSC.Dan[5].Off[2].Mna | BYTE
STRUrnikXCtoSCDan5Off2Ura | INT | IOD_STR_TCP | 866 | 40866 | UrnikXCtoSC.Dan[5].Off[2].Ura | BYTE
STRUrnikXCtoSCDan5Off3Mna | INT | IOD_STR_TCP | 867 | 40867 | UrnikXCtoSC.Dan[5].Off[3].Mna | BYTE
STRUrnikXCtoSCDan5Off3Ura | INT | IOD_STR_TCP | 868 | 40868 | UrnikXCtoSC.Dan[5].Off[3].Ura | BYTE
STRUrnikXCtoSCDan5On1Mna | INT | IOD_STR_TCP | 869 | 40869 | UrnikXCtoSC.Dan[5].On[1].Mna | BYTE
STRUrnikXCtoSCDan5On1Ura | INT | IOD_STR_TCP | 870 | 40870 | UrnikXCtoSC.Dan[5].On[1].Ura | BYTE
STRUrnikXCtoSCDan5On2Mna | INT | IOD_STR_TCP | 871 | 40871 | UrnikXCtoSC.Dan[5].On[2].Mna | BYTE
STRUrnikXCtoSCDan5On2Ura | INT | IOD_STR_TCP | 872 | 40872 | UrnikXCtoSC.Dan[5].On[2].Ura | BYTE
STRUrnikXCtoSCDan5On3Mna | INT | IOD_STR_TCP | 873 | 40873 | UrnikXCtoSC.Dan[5].On[3].Mna | BYTE
STRUrnikXCtoSCDan5On3Ura | INT | IOD_STR_TCP | 874 | 40874 | UrnikXCtoSC.Dan[5].On[3].Ura | BYTE
STRUrnikXCtoSCDan6Off1Mna | INT | IOD_STR_TCP | 875 | 40875 | UrnikXCtoSC.Dan[6].Off[1].Mna | BYTE
STRUrnikXCtoSCDan6Off1Ura | INT | IOD_STR_TCP | 876 | 40876 | UrnikXCtoSC.Dan[6].Off[1].Ura | BYTE
STRUrnikXCtoSCDan6Off2Mna | INT | IOD_STR_TCP | 877 | 40877 | UrnikXCtoSC.Dan[6].Off[2].Mna | BYTE
STRUrnikXCtoSCDan6Off2Ura | INT | IOD_STR_TCP | 878 | 40878 | UrnikXCtoSC.Dan[6].Off[2].Ura | BYTE
STRUrnikXCtoSCDan6Off3Mna | INT | IOD_STR_TCP | 879 | 40879 | UrnikXCtoSC.Dan[6].Off[3].Mna | BYTE
STRUrnikXCtoSCDan6Off3Ura | INT | IOD_STR_TCP | 880 | 40880 | UrnikXCtoSC.Dan[6].Off[3].Ura | BYTE
STRUrnikXCtoSCDan6On1Mna | INT | IOD_STR_TCP | 881 | 40881 | UrnikXCtoSC.Dan[6].On[1].Mna | BYTE
STRUrnikXCtoSCDan6On1Ura | INT | IOD_STR_TCP | 882 | 40882 | UrnikXCtoSC.Dan[6].On[1].Ura | BYTE
STRUrnikXCtoSCDan6On2Mna | INT | IOD_STR_TCP | 883 | 40883 | UrnikXCtoSC.Dan[6].On[2].Mna | BYTE
STRUrnikXCtoSCDan6On2Ura | INT | IOD_STR_TCP | 884 | 40884 | UrnikXCtoSC.Dan[6].On[2].Ura | BYTE
STRUrnikXCtoSCDan6On3Mna | INT | IOD_STR_TCP | 885 | 40885 | UrnikXCtoSC.Dan[6].On[3].Mna | BYTE
STRUrnikXCtoSCDan6On3Ura | INT | IOD_STR_TCP | 886 | 40886 | UrnikXCtoSC.Dan[6].On[3].Ura | BYTE
STRUrnikXCtoSCDan7Off1Mna | INT | IOD_STR_TCP | 887 | 40887 | UrnikXCtoSC.Dan[7].Off[1].Mna | BYTE
STRUrnikXCtoSCDan7Off1Ura | INT | IOD_STR_TCP | 888 | 40888 | UrnikXCtoSC.Dan[7].Off[1].Ura | BYTE
STRUrnikXCtoSCDan7Off2Mna | INT | IOD_STR_TCP | 889 | 40889 | UrnikXCtoSC.Dan[7].Off[2].Mna | BYTE
STRUrnikXCtoSCDan7Off2Ura | INT | IOD_STR_TCP | 890 | 40890 | UrnikXCtoSC.Dan[7].Off[2].Ura | BYTE
STRUrnikXCtoSCDan7Off3Mna | INT | IOD_STR_TCP | 891 | 40891 | UrnikXCtoSC.Dan[7].Off[3].Mna | BYTE
STRUrnikXCtoSCDan7Off3Ura | INT | IOD_STR_TCP | 892 | 40892 | UrnikXCtoSC.Dan[7].Off[3].Ura | BYTE
STRUrnikXCtoSCDan7On1Mna | INT | IOD_STR_TCP | 893 | 40893 | UrnikXCtoSC.Dan[7].On[1].Mna | BYTE
STRUrnikXCtoSCDan7On1Ura | INT | IOD_STR_TCP | 894 | 40894 | UrnikXCtoSC.Dan[7].On[1].Ura | BYTE
STRUrnikXCtoSCDan7On2Mna | INT | IOD_STR_TCP | 895 | 40895 | UrnikXCtoSC.Dan[7].On[2].Mna | BYTE
STRUrnikXCtoSCDan7On2Ura | INT | IOD_STR_TCP | 896 | 40896 | UrnikXCtoSC.Dan[7].On[2].Ura | BYTE
STRUrnikXCtoSCDan7On3Mna | INT | IOD_STR_TCP | 897 | 40897 | UrnikXCtoSC.Dan[7].On[3].Mna | BYTE
STRUrnikXCtoSCDan7On3Ura | INT | IOD_STR_TCP | 898 | 40898 | UrnikXCtoSC.Dan[7].On[3].Ura | BYTE
STRUserCurrentLevel | INT | IOD_STR_TCP | 899 | 40899 | UserCurrentLevel | BYTE
STRCrpalkeGrfsGalAlarmActiveCode | INT | IOD_STR_TCP | 900 | 40900 | CrpalkeGrfsGal.AlarmActiveCode
STRCrpalkeGrfsGalAlarmCodeLog1 | INT | IOD_STR_TCP | 901 | 40901 | CrpalkeGrfsGal.AlarmCodeLog1
STRCrpalkeGrfsGalAlarmCodeLog2 | INT | IOD_STR_TCP | 902 | 40902 | CrpalkeGrfsGal.AlarmCodeLog2
STRCrpalkeGrfsGalAlarmCodeLog3 | INT | IOD_STR_TCP | 903 | 40903 | CrpalkeGrfsGal.AlarmCodeLog3
STRCrpalkeGrfsGalAlarmCodeLog4 | INT | IOD_STR_TCP | 904 | 40904 | CrpalkeGrfsGal.AlarmCodeLog4
STRCrpalkeGrfsGalAlarmCodeLog5 | INT | IOD_STR_TCP | 905 | 40905 | CrpalkeGrfsGal.AlarmCodeLog5
STRCrpalkeGrfsGalAlarmGroupXVH0 | INT | IOD_STR_TCP | 906 | 40906 | CrpalkeGrfsGal.AlarmGroupXVH[0]
STRCrpalkeGrfsGalAlarmGroupXVH10 | INT | IOD_STR_TCP | 907 | 40907 | CrpalkeGrfsGal.AlarmGroupXVH[10]
STRCrpalkeGrfsGalAlarmGroupXVH11 | INT | IOD_STR_TCP | 908 | 40908 | CrpalkeGrfsGal.AlarmGroupXVH[11]
STRCrpalkeGrfsGalAlarmGroupXVH12 | INT | IOD_STR_TCP | 909 | 40909 | CrpalkeGrfsGal.AlarmGroupXVH[12]
STRCrpalkeGrfsGalAlarmGroupXVH13 | INT | IOD_STR_TCP | 910 | 40910 | CrpalkeGrfsGal.AlarmGroupXVH[13]
STRCrpalkeGrfsGalAlarmGroupXVH14 | INT | IOD_STR_TCP | 911 | 40911 | CrpalkeGrfsGal.AlarmGroupXVH[14]
STRCrpalkeGrfsGalAlarmGroupXVH15 | INT | IOD_STR_TCP | 912 | 40912 | CrpalkeGrfsGal.AlarmGroupXVH[15]
STRCrpalkeGrfsGalAlarmGroupXVH16 | INT | IOD_STR_TCP | 913 | 40913 | CrpalkeGrfsGal.AlarmGroupXVH[16]
STRCrpalkeGrfsGalAlarmGroupXVH1 | INT | IOD_STR_TCP | 914 | 40914 | CrpalkeGrfsGal.AlarmGroupXVH[1]
STRCrpalkeGrfsGalAlarmGroupXVH2 | INT | IOD_STR_TCP | 915 | 40915 | CrpalkeGrfsGal.AlarmGroupXVH[2]
STRCrpalkeGrfsGalAlarmGroupXVH3 | INT | IOD_STR_TCP | 916 | 40916 | CrpalkeGrfsGal.AlarmGroupXVH[3]
STRCrpalkeGrfsGalAlarmGroupXVH4 | INT | IOD_STR_TCP | 917 | 40917 | CrpalkeGrfsGal.AlarmGroupXVH[4]
STRCrpalkeGrfsGalAlarmGroupXVH5 | INT | IOD_STR_TCP | 918 | 40918 | CrpalkeGrfsGal.AlarmGroupXVH[5]
STRCrpalkeGrfsGalAlarmGroupXVH6 | INT | IOD_STR_TCP | 919 | 40919 | CrpalkeGrfsGal.AlarmGroupXVH[6]
STRCrpalkeGrfsGalAlarmGroupXVH7 | INT | IOD_STR_TCP | 920 | 40920 | CrpalkeGrfsGal.AlarmGroupXVH[7]
STRCrpalkeGrfsGalAlarmGroupXVH8 | INT | IOD_STR_TCP | 921 | 40921 | CrpalkeGrfsGal.AlarmGroupXVH[8]
STRCrpalkeGrfsGalAlarmGroupXVH9 | INT | IOD_STR_TCP | 922 | 40922 | CrpalkeGrfsGal.AlarmGroupXVH[9]
STRCrpalkeGrfsGalAlarmQSD1 | INT | IOD_STR_TCP | 923 | 40923 | CrpalkeGrfsGal.AlarmQSD1
STRCrpalkeGrfsGalAlarmQSD2 | INT | IOD_STR_TCP | 924 | 40924 | CrpalkeGrfsGal.AlarmQSD2
STRCrpalkeGrfsGalAlarmStart1 | INT | IOD_STR_TCP | 925 | 40925 | CrpalkeGrfsGal.AlarmStart1
STRCrpalkeGrfsGalAlarmStart2 | INT | IOD_STR_TCP | 926 | 40926 | CrpalkeGrfsGal.AlarmStart2
STRCrpalkeGrfsGalAlarmStop1 | INT | IOD_STR_TCP | 927 | 40927 | CrpalkeGrfsGal.AlarmStop1
STRCrpalkeGrfsGalAlarmStop2 | INT | IOD_STR_TCP | 928 | 40928 | CrpalkeGrfsGal.AlarmStop2
STRCrpalkeGrfsGalAlarmStop3 | INT | IOD_STR_TCP | 929 | 40929 | CrpalkeGrfsGal.AlarmStop3
STRCrpalkeGrfsGalAlarmSurv1 | INT | IOD_STR_TCP | 930 | 40930 | CrpalkeGrfsGal.AlarmSurv1
STRCrpalkeGrfsGalAlarmSurv2 | INT | IOD_STR_TCP | 931 | 40931 | CrpalkeGrfsGal.AlarmSurv2
STRCrpalkeGrfsGalControlSource | INT | IOD_STR_TCP | 932 | 40932 | CrpalkeGrfsGal.ControlSource
STRCrpalkeGrfsGalExternInputSetup | INT | IOD_STR_TCP | 933 | 40933 | CrpalkeGrfsGal.ExternInputSetup
STRCrpalkeGrfsGalExternInputsStatus | INT | IOD_STR_TCP | 934 | 40934 | CrpalkeGrfsGal.ExternInputsStatus
STRCrpalkeGrfsGalLocalSetupMode1 | INT | IOD_STR_TCP | 935 | 40935 | CrpalkeGrfsGal.LocalSetupMode1
STRCrpalkeGrfsGalPreklopkaMode | INT | IOD_STR_TCP | 936 | 40936 | CrpalkeGrfsGal.PreklopkaMode
STRCrpalkeGrfsGalRelay1setup | INT | IOD_STR_TCP | 937 | 40937 | CrpalkeGrfsGal.Relay1setup
STRCrpalkeGrfsGalRemoteSetupMode1 | INT | IOD_STR_TCP | 938 | 40938 | CrpalkeGrfsGal.RemoteSetupMode1
STRCrpalkeGrfsGalStatusCrpalke | INT | IOD_STR_TCP | 939 | 40939 | CrpalkeGrfsGal.StatusCrpalke | BYTE
STRCrpalkeGrfsGalStatusMode1 | INT | IOD_STR_TCP | 940 | 40940 | CrpalkeGrfsGal.StatusMode1
STRCrpalkeGrfsGalStatusMode1co | INT | IOD_STR_TCP | 941 | 40941 | CrpalkeGrfsGal.StatusMode1co | BYTE
STRCrpalkeGrfsGalStatusMode1op | INT | IOD_STR_TCP | 942 | 40942 | CrpalkeGrfsGal.StatusMode1op | BYTE
STRCrpalkeGrfsGalStatusMode2 | INT | IOD_STR_TCP | 943 | 40943 | CrpalkeGrfsGal.StatusMode2
STRCrpalkeGrfsGalStatusMode3 | INT | IOD_STR_TCP | 944 | 40944 | CrpalkeGrfsGal.StatusMode3
STRCrpGrfsPIDregTN | INT | IOD_STR_TCP | 945 | 40945 | CrpGrfsPIDregTN
STRDateTimeDanVtednu | INT | IOD_STR_TCP | 946 | 40946 | DateTime.DanVtednu | BYTE
STRLetniCasDatumi111 | INT | IOD_STR_TCP | 947 | 40947 | LetniCasDatumi[1,1,1]
STRLetniCasDatumi112 | INT | IOD_STR_TCP | 948 | 40948 | LetniCasDatumi[1,1,2]
STRLetniCasDatumi121 | INT | IOD_STR_TCP | 949 | 40949 | LetniCasDatumi[1,2,1]
STRLetniCasDatumi122 | INT | IOD_STR_TCP | 950 | 40950 | LetniCasDatumi[1,2,2]
STRLetniCasDatumi131 | INT | IOD_STR_TCP | 951 | 40951 | LetniCasDatumi[1,3,1]
STRLetniCasDatumi132 | INT | IOD_STR_TCP | 952 | 40952 | LetniCasDatumi[1,3,2]
STRLetniCasDatumi141 | INT | IOD_STR_TCP | 953 | 40953 | LetniCasDatumi[1,4,1]
STRLetniCasDatumi142 | INT | IOD_STR_TCP | 954 | 40954 | LetniCasDatumi[1,4,2]
STRLetniCasDatumi211 | INT | IOD_STR_TCP | 955 | 40955 | LetniCasDatumi[2,1,1]
STRLetniCasDatumi212 | INT | IOD_STR_TCP | 956 | 40956 | LetniCasDatumi[2,1,2]
STRLetniCasDatumi221 | INT | IOD_STR_TCP | 957 | 40957 | LetniCasDatumi[2,2,1]
STRLetniCasDatumi222 | INT | IOD_STR_TCP | 958 | 40958 | LetniCasDatumi[2,2,2]
STRLetniCasDatumi231 | INT | IOD_STR_TCP | 959 | 40959 | LetniCasDatumi[2,3,1]
STRLetniCasDatumi232 | INT | IOD_STR_TCP | 960 | 40960 | LetniCasDatumi[2,3,2]
STRLetniCasDatumi241 | INT | IOD_STR_TCP | 961 | 40961 | LetniCasDatumi[2,4,1]
STRLetniCasDatumi242 | INT | IOD_STR_TCP | 962 | 40962 | LetniCasDatumi[2,4,2]
STRUrnikSaveDan1Off1Mna | INT | IOD_STR_TCP | 963 | 40963 | UrnikSave.Dan[1].Off[1].Mna | BYTE
STRUrnikSaveDan1Off1Ura | INT | IOD_STR_TCP | 964 | 40964 | UrnikSave.Dan[1].Off[1].Ura | BYTE
STRUrnikSaveDan1Off2Mna | INT | IOD_STR_TCP | 965 | 40965 | UrnikSave.Dan[1].Off[2].Mna | BYTE
STRUrnikSaveDan1Off2Ura | INT | IOD_STR_TCP | 966 | 40966 | UrnikSave.Dan[1].Off[2].Ura | BYTE
STRUrnikSaveDan1Off3Mna | INT | IOD_STR_TCP | 967 | 40967 | UrnikSave.Dan[1].Off[3].Mna | BYTE
STRUrnikSaveDan1Off3Ura | INT | IOD_STR_TCP | 968 | 40968 | UrnikSave.Dan[1].Off[3].Ura | BYTE
STRUrnikSaveDan1On1Mna | INT | IOD_STR_TCP | 969 | 40969 | UrnikSave.Dan[1].On[1].Mna | BYTE
STRUrnikSaveDan1On1Ura | INT | IOD_STR_TCP | 970 | 40970 | UrnikSave.Dan[1].On[1].Ura | BYTE
STRUrnikSaveDan1On2Mna | INT | IOD_STR_TCP | 971 | 40971 | UrnikSave.Dan[1].On[2].Mna | BYTE
STRUrnikSaveDan1On2Ura | INT | IOD_STR_TCP | 972 | 40972 | UrnikSave.Dan[1].On[2].Ura | BYTE
STRUrnikSaveDan1On3Mna | INT | IOD_STR_TCP | 973 | 40973 | UrnikSave.Dan[1].On[3].Mna | BYTE
STRUrnikSaveDan1On3Ura | INT | IOD_STR_TCP | 974 | 40974 | UrnikSave.Dan[1].On[3].Ura | BYTE
STRUrnikSaveDan2Off1Mna | INT | IOD_STR_TCP | 975 | 40975 | UrnikSave.Dan[2].Off[1].Mna | BYTE
STRUrnikSaveDan2Off1Ura | INT | IOD_STR_TCP | 976 | 40976 | UrnikSave.Dan[2].Off[1].Ura | BYTE
STRUrnikSaveDan2Off2Mna | INT | IOD_STR_TCP | 977 | 40977 | UrnikSave.Dan[2].Off[2].Mna | BYTE
STRUrnikSaveDan2Off2Ura | INT | IOD_STR_TCP | 978 | 40978 | UrnikSave.Dan[2].Off[2].Ura | BYTE
STRUrnikSaveDan2Off3Mna | INT | IOD_STR_TCP | 979 | 40979 | UrnikSave.Dan[2].Off[3].Mna | BYTE
STRUrnikSaveDan2Off3Ura | INT | IOD_STR_TCP | 980 | 40980 | UrnikSave.Dan[2].Off[3].Ura | BYTE
STRUrnikSaveDan2On1Mna | INT | IOD_STR_TCP | 981 | 40981 | UrnikSave.Dan[2].On[1].Mna | BYTE
STRUrnikSaveDan2On1Ura | INT | IOD_STR_TCP | 982 | 40982 | UrnikSave.Dan[2].On[1].Ura | BYTE
STRUrnikSaveDan2On2Mna | INT | IOD_STR_TCP | 983 | 40983 | UrnikSave.Dan[2].On[2].Mna | BYTE
STRUrnikSaveDan2On2Ura | INT | IOD_STR_TCP | 984 | 40984 | UrnikSave.Dan[2].On[2].Ura | BYTE
STRUrnikSaveDan2On3Mna | INT | IOD_STR_TCP | 985 | 40985 | UrnikSave.Dan[2].On[3].Mna | BYTE
STRUrnikSaveDan2On3Ura | INT | IOD_STR_TCP | 986 | 40986 | UrnikSave.Dan[2].On[3].Ura | BYTE
STRUrnikSaveDan3Off1Mna | INT | IOD_STR_TCP | 987 | 40987 | UrnikSave.Dan[3].Off[1].Mna | BYTE
STRUrnikSaveDan3Off1Ura | INT | IOD_STR_TCP | 988 | 40988 | UrnikSave.Dan[3].Off[1].Ura | BYTE
STRUrnikSaveDan3Off2Mna | INT | IOD_STR_TCP | 989 | 40989 | UrnikSave.Dan[3].Off[2].Mna | BYTE
STRUrnikSaveDan3Off2Ura | INT | IOD_STR_TCP | 990 | 40990 | UrnikSave.Dan[3].Off[2].Ura | BYTE
STRUrnikSaveDan3Off3Mna | INT | IOD_STR_TCP | 991 | 40991 | UrnikSave.Dan[3].Off[3].Mna | BYTE
STRUrnikSaveDan3Off3Ura | INT | IOD_STR_TCP | 992 | 40992 | UrnikSave.Dan[3].Off[3].Ura | BYTE
STRUrnikSaveDan3On1Mna | INT | IOD_STR_TCP | 993 | 40993 | UrnikSave.Dan[3].On[1].Mna | BYTE
STRUrnikSaveDan3On1Ura | INT | IOD_STR_TCP | 994 | 40994 | UrnikSave.Dan[3].On[1].Ura | BYTE
STRUrnikSaveDan3On2Mna | INT | IOD_STR_TCP | 995 | 40995 | UrnikSave.Dan[3].On[2].Mna | BYTE
STRUrnikSaveDan3On2Ura | INT | IOD_STR_TCP | 996 | 40996 | UrnikSave.Dan[3].On[2].Ura | BYTE
STRUrnikSaveDan3On3Mna | INT | IOD_STR_TCP | 997 | 40997 | UrnikSave.Dan[3].On[3].Mna | BYTE
STRUrnikSaveDan3On3Ura | INT | IOD_STR_TCP | 998 | 40998 | UrnikSave.Dan[3].On[3].Ura | BYTE
STRUrnikSaveDan4Off1Mna | INT | IOD_STR_TCP | 999 | 40999 | UrnikSave.Dan[4].Off[1].Mna | BYTE
STRUrnikSaveDan4Off1Ura | INT | IOD_STR_TCP | 1000 | 41000 | UrnikSave.Dan[4].Off[1].Ura | BYTE
STRUrnikSaveDan4Off2Mna | INT | IOD_STR_TCP | 1001 | 41001 | UrnikSave.Dan[4].Off[2].Mna | BYTE
STRUrnikSaveDan4Off2Ura | INT | IOD_STR_TCP | 1002 | 41002 | UrnikSave.Dan[4].Off[2].Ura | BYTE
STRUrnikSaveDan4Off3Mna | INT | IOD_STR_TCP | 1003 | 41003 | UrnikSave.Dan[4].Off[3].Mna | BYTE
STRUrnikSaveDan4Off3Ura | INT | IOD_STR_TCP | 1004 | 41004 | UrnikSave.Dan[4].Off[3].Ura | BYTE
STRUrnikSaveDan4On1Mna | INT | IOD_STR_TCP | 1005 | 41005 | UrnikSave.Dan[4].On[1].Mna | BYTE
STRUrnikSaveDan4On1Ura | INT | IOD_STR_TCP | 1006 | 41006 | UrnikSave.Dan[4].On[1].Ura | BYTE
STRUrnikSaveDan4On2Mna | INT | IOD_STR_TCP | 1007 | 41007 | UrnikSave.Dan[4].On[2].Mna | BYTE
STRUrnikSaveDan4On2Ura | INT | IOD_STR_TCP | 1008 | 41008 | UrnikSave.Dan[4].On[2].Ura | BYTE
STRUrnikSaveDan4On3Mna | INT | IOD_STR_TCP | 1009 | 41009 | UrnikSave.Dan[4].On[3].Mna | BYTE
STRUrnikSaveDan4On3Ura | INT | IOD_STR_TCP | 1010 | 41010 | UrnikSave.Dan[4].On[3].Ura | BYTE
STRUrnikSaveDan5Off1Mna | INT | IOD_STR_TCP | 1011 | 41011 | UrnikSave.Dan[5].Off[1].Mna | BYTE
STRUrnikSaveDan5Off1Ura | INT | IOD_STR_TCP | 1012 | 41012 | UrnikSave.Dan[5].Off[1].Ura | BYTE
STRUrnikSaveDan5Off2Mna | INT | IOD_STR_TCP | 1013 | 41013 | UrnikSave.Dan[5].Off[2].Mna | BYTE
STRUrnikSaveDan5Off2Ura | INT | IOD_STR_TCP | 1014 | 41014 | UrnikSave.Dan[5].Off[2].Ura | BYTE
STRUrnikSaveDan5Off3Mna | INT | IOD_STR_TCP | 1015 | 41015 | UrnikSave.Dan[5].Off[3].Mna | BYTE
STRUrnikSaveDan5Off3Ura | INT | IOD_STR_TCP | 1016 | 41016 | UrnikSave.Dan[5].Off[3].Ura | BYTE
STRUrnikSaveDan5On1Mna | INT | IOD_STR_TCP | 1017 | 41017 | UrnikSave.Dan[5].On[1].Mna | BYTE
STRUrnikSaveDan5On1Ura | INT | IOD_STR_TCP | 1018 | 41018 | UrnikSave.Dan[5].On[1].Ura | BYTE
STRUrnikSaveDan5On2Mna | INT | IOD_STR_TCP | 1019 | 41019 | UrnikSave.Dan[5].On[2].Mna | BYTE
STRUrnikSaveDan5On2Ura | INT | IOD_STR_TCP | 1020 | 41020 | UrnikSave.Dan[5].On[2].Ura | BYTE
STRUrnikSaveDan5On3Mna | INT | IOD_STR_TCP | 1021 | 41021 | UrnikSave.Dan[5].On[3].Mna | BYTE
STRUrnikSaveDan5On3Ura | INT | IOD_STR_TCP | 1022 | 41022 | UrnikSave.Dan[5].On[3].Ura | BYTE
STRUrnikSaveDan6Off1Mna | INT | IOD_STR_TCP | 1023 | 41023 | UrnikSave.Dan[6].Off[1].Mna | BYTE
STRUrnikSaveDan6Off1Ura | INT | IOD_STR_TCP | 1024 | 41024 | UrnikSave.Dan[6].Off[1].Ura | BYTE
STRUrnikSaveDan6Off2Mna | INT | IOD_STR_TCP | 1025 | 41025 | UrnikSave.Dan[6].Off[2].Mna | BYTE
STRUrnikSaveDan6Off2Ura | INT | IOD_STR_TCP | 1026 | 41026 | UrnikSave.Dan[6].Off[2].Ura | BYTE
STRUrnikSaveDan6Off3Mna | INT | IOD_STR_TCP | 1027 | 41027 | UrnikSave.Dan[6].Off[3].Mna | BYTE
STRUrnikSaveDan6Off3Ura | INT | IOD_STR_TCP | 1028 | 41028 | UrnikSave.Dan[6].Off[3].Ura | BYTE
STRUrnikSaveDan6On1Mna | INT | IOD_STR_TCP | 1029 | 41029 | UrnikSave.Dan[6].On[1].Mna | BYTE
STRUrnikSaveDan6On1Ura | INT | IOD_STR_TCP | 1030 | 41030 | UrnikSave.Dan[6].On[1].Ura | BYTE
STRUrnikSaveDan6On2Mna | INT | IOD_STR_TCP | 1031 | 41031 | UrnikSave.Dan[6].On[2].Mna | BYTE
STRUrnikSaveDan6On2Ura | INT | IOD_STR_TCP | 1032 | 41032 | UrnikSave.Dan[6].On[2].Ura | BYTE
STRUrnikSaveDan6On3Mna | INT | IOD_STR_TCP | 1033 | 41033 | UrnikSave.Dan[6].On[3].Mna | BYTE
STRUrnikSaveDan6On3Ura | INT | IOD_STR_TCP | 1034 | 41034 | UrnikSave.Dan[6].On[3].Ura | BYTE
STRUrnikSaveDan7Off1Mna | INT | IOD_STR_TCP | 1035 | 41035 | UrnikSave.Dan[7].Off[1].Mna | BYTE
STRUrnikSaveDan7Off1Ura | INT | IOD_STR_TCP | 1036 | 41036 | UrnikSave.Dan[7].Off[1].Ura | BYTE
STRUrnikSaveDan7Off2Mna | INT | IOD_STR_TCP | 1037 | 41037 | UrnikSave.Dan[7].Off[2].Mna | BYTE
STRUrnikSaveDan7Off2Ura | INT | IOD_STR_TCP | 1038 | 41038 | UrnikSave.Dan[7].Off[2].Ura | BYTE
STRUrnikSaveDan7Off3Mna | INT | IOD_STR_TCP | 1039 | 41039 | UrnikSave.Dan[7].Off[3].Mna | BYTE
STRUrnikSaveDan7Off3Ura | INT | IOD_STR_TCP | 1040 | 41040 | UrnikSave.Dan[7].Off[3].Ura | BYTE
STRUrnikSaveDan7On1Mna | INT | IOD_STR_TCP | 1041 | 41041 | UrnikSave.Dan[7].On[1].Mna | BYTE
STRUrnikSaveDan7On1Ura | INT | IOD_STR_TCP | 1042 | 41042 | UrnikSave.Dan[7].On[1].Ura | BYTE
STRUrnikSaveDan7On2Mna | INT | IOD_STR_TCP | 1043 | 41043 | UrnikSave.Dan[7].On[2].Mna | BYTE
STRUrnikSaveDan7On2Ura | INT | IOD_STR_TCP | 1044 | 41044 | UrnikSave.Dan[7].On[2].Ura | BYTE
STRUrnikSaveDan7On3Mna | INT | IOD_STR_TCP | 1045 | 41045 | UrnikSave.Dan[7].On[3].Mna | BYTE
STRUrnikSaveDan7On3Ura | INT | IOD_STR_TCP | 1046 | 41046 | UrnikSave.Dan[7].On[3].Ura | BYTE
STRXVH_CircNumber | INT | IOD_STR_TCP | 1047 | 41047 | XVH_CircNumber | BYTE
STRXVH_KompStatus1 | INT | IOD_STR_TCP | 1048 | 41048 | XVH_KompStatus[1] | BYTE
STRXVH_KompStatus2 | INT | IOD_STR_TCP | 1049 | 41049 | XVH_KompStatus[2] | BYTE
STRXVH_ReferencaUpper | INT | IOD_STR_TCP | 1050 | 41050 | XVH_ReferencaUpper
STRXVH_UPSstatus | INT | IOD_STR_TCP | 1051 | 41051 | XVH_UPSstatus | BYTE
STRXVH_UrnikDan1Off1Mna | INT | IOD_STR_TCP | 1052 | 41052 | XVH_Urnik.Dan[1].Off[1].Mna | BYTE
STRXVH_UrnikDan1Off1Ura | INT | IOD_STR_TCP | 1053 | 41053 | XVH_Urnik.Dan[1].Off[1].Ura | BYTE
STRXVH_UrnikDan1Off2Mna | INT | IOD_STR_TCP | 1054 | 41054 | XVH_Urnik.Dan[1].Off[2].Mna | BYTE
STRXVH_UrnikDan1Off2Ura | INT | IOD_STR_TCP | 1055 | 41055 | XVH_Urnik.Dan[1].Off[2].Ura | BYTE
STRXVH_UrnikDan1Off3Mna | INT | IOD_STR_TCP | 1056 | 41056 | XVH_Urnik.Dan[1].Off[3].Mna | BYTE
STRXVH_UrnikDan1Off3Ura | INT | IOD_STR_TCP | 1057 | 41057 | XVH_Urnik.Dan[1].Off[3].Ura | BYTE
STRXVH_UrnikDan1On1Mna | INT | IOD_STR_TCP | 1058 | 41058 | XVH_Urnik.Dan[1].On[1].Mna | BYTE
STRXVH_UrnikDan1On1Ura | INT | IOD_STR_TCP | 1059 | 41059 | XVH_Urnik.Dan[1].On[1].Ura | BYTE
STRXVH_UrnikDan1On2Mna | INT | IOD_STR_TCP | 1060 | 41060 | XVH_Urnik.Dan[1].On[2].Mna | BYTE
STRXVH_UrnikDan1On2Ura | INT | IOD_STR_TCP | 1061 | 41061 | XVH_Urnik.Dan[1].On[2].Ura | BYTE
STRXVH_UrnikDan1On3Mna | INT | IOD_STR_TCP | 1062 | 41062 | XVH_Urnik.Dan[1].On[3].Mna | BYTE
STRXVH_UrnikDan1On3Ura | INT | IOD_STR_TCP | 1063 | 41063 | XVH_Urnik.Dan[1].On[3].Ura | BYTE
STRXVH_UrnikDan2Off1Mna | INT | IOD_STR_TCP | 1064 | 41064 | XVH_Urnik.Dan[2].Off[1].Mna | BYTE
STRXVH_UrnikDan2Off1Ura | INT | IOD_STR_TCP | 1065 | 41065 | XVH_Urnik.Dan[2].Off[1].Ura | BYTE
STRXVH_UrnikDan2Off2Mna | INT | IOD_STR_TCP | 1066 | 41066 | XVH_Urnik.Dan[2].Off[2].Mna | BYTE
STRXVH_UrnikDan2Off2Ura | INT | IOD_STR_TCP | 1067 | 41067 | XVH_Urnik.Dan[2].Off[2].Ura | BYTE
STRXVH_UrnikDan2Off3Mna | INT | IOD_STR_TCP | 1068 | 41068 | XVH_Urnik.Dan[2].Off[3].Mna | BYTE
STRXVH_UrnikDan2Off3Ura | INT | IOD_STR_TCP | 1069 | 41069 | XVH_Urnik.Dan[2].Off[3].Ura | BYTE
STRXVH_UrnikDan2On1Mna | INT | IOD_STR_TCP | 1070 | 41070 | XVH_Urnik.Dan[2].On[1].Mna | BYTE
STRXVH_UrnikDan2On1Ura | INT | IOD_STR_TCP | 1071 | 41071 | XVH_Urnik.Dan[2].On[1].Ura | BYTE
STRXVH_UrnikDan2On2Mna | INT | IOD_STR_TCP | 1072 | 41072 | XVH_Urnik.Dan[2].On[2].Mna | BYTE
STRXVH_UrnikDan2On2Ura | INT | IOD_STR_TCP | 1073 | 41073 | XVH_Urnik.Dan[2].On[2].Ura | BYTE
STRXVH_UrnikDan2On3Mna | INT | IOD_STR_TCP | 1074 | 41074 | XVH_Urnik.Dan[2].On[3].Mna | BYTE
STRXVH_UrnikDan2On3Ura | INT | IOD_STR_TCP | 1075 | 41075 | XVH_Urnik.Dan[2].On[3].Ura | BYTE
STRXVH_UrnikDan3Off1Mna | INT | IOD_STR_TCP | 1076 | 41076 | XVH_Urnik.Dan[3].Off[1].Mna | BYTE
STRXVH_UrnikDan3Off1Ura | INT | IOD_STR_TCP | 1077 | 41077 | XVH_Urnik.Dan[3].Off[1].Ura | BYTE
STRXVH_UrnikDan3Off2Mna | INT | IOD_STR_TCP | 1078 | 41078 | XVH_Urnik.Dan[3].Off[2].Mna | BYTE
STRXVH_UrnikDan3Off2Ura | INT | IOD_STR_TCP | 1079 | 41079 | XVH_Urnik.Dan[3].Off[2].Ura | BYTE
STRXVH_UrnikDan3Off3Mna | INT | IOD_STR_TCP | 1080 | 41080 | XVH_Urnik.Dan[3].Off[3].Mna | BYTE
STRXVH_UrnikDan3Off3Ura | INT | IOD_STR_TCP | 1081 | 41081 | XVH_Urnik.Dan[3].Off[3].Ura | BYTE
STRXVH_UrnikDan3On1Mna | INT | IOD_STR_TCP | 1082 | 41082 | XVH_Urnik.Dan[3].On[1].Mna | BYTE
STRXVH_UrnikDan3On1Ura | INT | IOD_STR_TCP | 1083 | 41083 | XVH_Urnik.Dan[3].On[1].Ura | BYTE
STRXVH_UrnikDan3On2Mna | INT | IOD_STR_TCP | 1084 | 41084 | XVH_Urnik.Dan[3].On[2].Mna | BYTE
STRXVH_UrnikDan3On2Ura | INT | IOD_STR_TCP | 1085 | 41085 | XVH_Urnik.Dan[3].On[2].Ura | BYTE
STRXVH_UrnikDan3On3Mna | INT | IOD_STR_TCP | 1086 | 41086 | XVH_Urnik.Dan[3].On[3].Mna | BYTE
STRXVH_UrnikDan3On3Ura | INT | IOD_STR_TCP | 1087 | 41087 | XVH_Urnik.Dan[3].On[3].Ura | BYTE
STRXVH_UrnikDan4Off1Mna | INT | IOD_STR_TCP | 1088 | 41088 | XVH_Urnik.Dan[4].Off[1].Mna | BYTE
STRXVH_UrnikDan4Off1Ura | INT | IOD_STR_TCP | 1089 | 41089 | XVH_Urnik.Dan[4].Off[1].Ura | BYTE
STRXVH_UrnikDan4Off2Mna | INT | IOD_STR_TCP | 1090 | 41090 | XVH_Urnik.Dan[4].Off[2].Mna | BYTE
STRXVH_UrnikDan4Off2Ura | INT | IOD_STR_TCP | 1091 | 41091 | XVH_Urnik.Dan[4].Off[2].Ura | BYTE
STRXVH_UrnikDan4Off3Mna | INT | IOD_STR_TCP | 1092 | 41092 | XVH_Urnik.Dan[4].Off[3].Mna | BYTE
STRXVH_UrnikDan4Off3Ura | INT | IOD_STR_TCP | 1093 | 41093 | XVH_Urnik.Dan[4].Off[3].Ura | BYTE
STRXVH_UrnikDan4On1Mna | INT | IOD_STR_TCP | 1094 | 41094 | XVH_Urnik.Dan[4].On[1].Mna | BYTE
STRXVH_UrnikDan4On1Ura | INT | IOD_STR_TCP | 1095 | 41095 | XVH_Urnik.Dan[4].On[1].Ura | BYTE
STRXVH_UrnikDan4On2Mna | INT | IOD_STR_TCP | 1096 | 41096 | XVH_Urnik.Dan[4].On[2].Mna | BYTE
STRXVH_UrnikDan4On2Ura | INT | IOD_STR_TCP | 1097 | 41097 | XVH_Urnik.Dan[4].On[2].Ura | BYTE
STRXVH_UrnikDan4On3Mna | INT | IOD_STR_TCP | 1098 | 41098 | XVH_Urnik.Dan[4].On[3].Mna | BYTE
STRXVH_UrnikDan4On3Ura | INT | IOD_STR_TCP | 1099 | 41099 | XVH_Urnik.Dan[4].On[3].Ura | BYTE
STRXVH_UrnikDan5Off1Mna | INT | IOD_STR_TCP | 1100 | 41100 | XVH_Urnik.Dan[5].Off[1].Mna | BYTE
STRXVH_UrnikDan5Off1Ura | INT | IOD_STR_TCP | 1101 | 41101 | XVH_Urnik.Dan[5].Off[1].Ura | BYTE
STRXVH_UrnikDan5Off2Mna | INT | IOD_STR_TCP | 1102 | 41102 | XVH_Urnik.Dan[5].Off[2].Mna | BYTE
STRXVH_UrnikDan5Off2Ura | INT | IOD_STR_TCP | 1103 | 41103 | XVH_Urnik.Dan[5].Off[2].Ura | BYTE
STRXVH_UrnikDan5Off3Mna | INT | IOD_STR_TCP | 1104 | 41104 | XVH_Urnik.Dan[5].Off[3].Mna | BYTE
STRXVH_UrnikDan5Off3Ura | INT | IOD_STR_TCP | 1105 | 41105 | XVH_Urnik.Dan[5].Off[3].Ura | BYTE
STRXVH_UrnikDan5On1Mna | INT | IOD_STR_TCP | 1106 | 41106 | XVH_Urnik.Dan[5].On[1].Mna | BYTE
STRXVH_UrnikDan5On1Ura | INT | IOD_STR_TCP | 1107 | 41107 | XVH_Urnik.Dan[5].On[1].Ura | BYTE
STRXVH_UrnikDan5On2Mna | INT | IOD_STR_TCP | 1108 | 41108 | XVH_Urnik.Dan[5].On[2].Mna | BYTE
STRXVH_UrnikDan5On2Ura | INT | IOD_STR_TCP | 1109 | 41109 | XVH_Urnik.Dan[5].On[2].Ura | BYTE
STRXVH_UrnikDan5On3Mna | INT | IOD_STR_TCP | 1110 | 41110 | XVH_Urnik.Dan[5].On[3].Mna | BYTE
STRXVH_UrnikDan5On3Ura | INT | IOD_STR_TCP | 1111 | 41111 | XVH_Urnik.Dan[5].On[3].Ura | BYTE
STRXVH_UrnikDan6Off1Mna | INT | IOD_STR_TCP | 1112 | 41112 | XVH_Urnik.Dan[6].Off[1].Mna | BYTE
STRXVH_UrnikDan6Off1Ura | INT | IOD_STR_TCP | 1113 | 41113 | XVH_Urnik.Dan[6].Off[1].Ura | BYTE
STRXVH_UrnikDan6Off2Mna | INT | IOD_STR_TCP | 1114 | 41114 | XVH_Urnik.Dan[6].Off[2].Mna | BYTE
STRXVH_UrnikDan6Off2Ura | INT | IOD_STR_TCP | 1115 | 41115 | XVH_Urnik.Dan[6].Off[2].Ura | BYTE
STRXVH_UrnikDan6Off3Mna | INT | IOD_STR_TCP | 1116 | 41116 | XVH_Urnik.Dan[6].Off[3].Mna | BYTE
STRXVH_UrnikDan6Off3Ura | INT | IOD_STR_TCP | 1117 | 41117 | XVH_Urnik.Dan[6].Off[3].Ura | BYTE
STRXVH_UrnikDan6On1Mna | INT | IOD_STR_TCP | 1118 | 41118 | XVH_Urnik.Dan[6].On[1].Mna | BYTE
STRXVH_UrnikDan6On1Ura | INT | IOD_STR_TCP | 1119 | 41119 | XVH_Urnik.Dan[6].On[1].Ura | BYTE
STRXVH_UrnikDan6On2Mna | INT | IOD_STR_TCP | 1120 | 41120 | XVH_Urnik.Dan[6].On[2].Mna | BYTE
STRXVH_UrnikDan6On2Ura | INT | IOD_STR_TCP | 1121 | 41121 | XVH_Urnik.Dan[6].On[2].Ura | BYTE
STRXVH_UrnikDan6On3Mna | INT | IOD_STR_TCP | 1122 | 41122 | XVH_Urnik.Dan[6].On[3].Mna | BYTE
STRXVH_UrnikDan6On3Ura | INT | IOD_STR_TCP | 1123 | 41123 | XVH_Urnik.Dan[6].On[3].Ura | BYTE
STRXVH_UrnikDan7Off1Mna | INT | IOD_STR_TCP | 1124 | 41124 | XVH_Urnik.Dan[7].Off[1].Mna | BYTE
STRXVH_UrnikDan7Off1Ura | INT | IOD_STR_TCP | 1125 | 41125 | XVH_Urnik.Dan[7].Off[1].Ura | BYTE
STRXVH_UrnikDan7Off2Mna | INT | IOD_STR_TCP | 1126 | 41126 | XVH_Urnik.Dan[7].Off[2].Mna | BYTE
STRXVH_UrnikDan7Off2Ura | INT | IOD_STR_TCP | 1127 | 41127 | XVH_Urnik.Dan[7].Off[2].Ura | BYTE
STRXVH_UrnikDan7Off3Mna | INT | IOD_STR_TCP | 1128 | 41128 | XVH_Urnik.Dan[7].Off[3].Mna | BYTE
STRXVH_UrnikDan7Off3Ura | INT | IOD_STR_TCP | 1129 | 41129 | XVH_Urnik.Dan[7].Off[3].Ura | BYTE
STRXVH_UrnikDan7On1Mna | INT | IOD_STR_TCP | 1130 | 41130 | XVH_Urnik.Dan[7].On[1].Mna | BYTE
STRXVH_UrnikDan7On1Ura | INT | IOD_STR_TCP | 1131 | 41131 | XVH_Urnik.Dan[7].On[1].Ura | BYTE
STRXVH_UrnikDan7On2Mna | INT | IOD_STR_TCP | 1132 | 41132 | XVH_Urnik.Dan[7].On[2].Mna | BYTE
STRXVH_UrnikDan7On2Ura | INT | IOD_STR_TCP | 1133 | 41133 | XVH_Urnik.Dan[7].On[2].Ura | BYTE
STRXVH_UrnikDan7On3Mna | INT | IOD_STR_TCP | 1134 | 41134 | XVH_Urnik.Dan[7].On[3].Mna | BYTE
STRXVH_UrnikDan7On3Ura | INT | IOD_STR_TCP | 1135 | 41135 | XVH_Urnik.Dan[7].On[3].Ura | BYTE
STRXVH_VentilTYValue11 | INT | IOD_STR_TCP | 1136 | 41136 | XVH_VentilTYValue[1,1] | BYTE
STRXVH_VentilTYValue12 | INT | IOD_STR_TCP | 1137 | 41137 | XVH_VentilTYValue[1,2] | BYTE
STRXVH_VentilTYValue21 | INT | IOD_STR_TCP | 1138 | 41138 | XVH_VentilTYValue[2,1] | BYTE
STRXVH_VentilTYValue22 | INT | IOD_STR_TCP | 1139 | 41139 | XVH_VentilTYValue[2,2] | BYTE
STRXVH_VentilTYValue31 | INT | IOD_STR_TCP | 1140 | 41140 | XVH_VentilTYValue[3,1] | BYTE
STRXVH_VentilTYValue32 | INT | IOD_STR_TCP | 1141 | 41141 | XVH_VentilTYValue[3,2] | BYTE
STRXVH_VentilTYValue41 | INT | IOD_STR_TCP | 1142 | 41142 | XVH_VentilTYValue[4,1] | BYTE
STRXVH_VentilTYValue42 | INT | IOD_STR_TCP | 1143 | 41143 | XVH_VentilTYValue[4,2] | BYTE
STRXVH_VlazilecStatus1 | INT | IOD_STR_TCP | 1144 | 41144 | XVH_VlazilecStatus[1] | BYTE
STRXVH_VlazilecStatus2 | INT | IOD_STR_TCP | 1145 | 41145 | XVH_VlazilecStatus[2] | BYTE
STRXVHnum10 | INT | IOD_STR_TCP | 1146 | 41146 | XVHnum[10] | BYTE
STRXVHnum11 | INT | IOD_STR_TCP | 1147 | 41147 | XVHnum[11] | BYTE
STRXVHnum12 | INT | IOD_STR_TCP | 1148 | 41148 | XVHnum[12] | BYTE
STRXVHnum13 | INT | IOD_STR_TCP | 1149 | 41149 | XVHnum[13] | BYTE
STRXVHnum14 | INT | IOD_STR_TCP | 1150 | 41150 | XVHnum[14] | BYTE
STRXVHnum1 | INT | IOD_STR_TCP | 1151 | 41151 | XVHnum[1] | BYTE
STRXVHnum2 | INT | IOD_STR_TCP | 1152 | 41152 | XVHnum[2] | BYTE
STRXVHnum3 | INT | IOD_STR_TCP | 1153 | 41153 | XVHnum[3] | BYTE
STRXVHnum4 | INT | IOD_STR_TCP | 1154 | 41154 | XVHnum[4] | BYTE
STRXVHnum5 | INT | IOD_STR_TCP | 1155 | 41155 | XVHnum[5] | BYTE
STRXVHnum6 | INT | IOD_STR_TCP | 1156 | 41156 | XVHnum[6] | BYTE
STRXVHnum7 | INT | IOD_STR_TCP | 1157 | 41157 | XVHnum[7] | BYTE
STRXVHnum8 | INT | IOD_STR_TCP | 1158 | 41158 | XVHnum[8] | BYTE
STRXVHnum9 | INT | IOD_STR_TCP | 1159 | 41159 | XVHnum[9] | BYTE
STRXVH_CrpalkaGrfsNum | LONG | IOD_STR_TCP | 4001 | 44001 | XVH_CrpalkaGrfsNum
STRXVH_StUrnika | LONG | IOD_STR_TCP | 4003 | 44003 | XVH_StUrnika
STRATVAlarmTemp | REAL | IOD_STR_TCP | 5001 | 45001 | ATVAlarmTemp
STRCirc1CosFi_III | REAL | IOD_STR_TCP | 5003 | 45003 | Circ[1].CosFi_III
STRCirc1DelovnaEnergija | REAL | IOD_STR_TCP | 5005 | 45005 | Circ[1].DelovnaEnergija
STRCirc1DelovnaMoc_III | REAL | IOD_STR_TCP | 5007 | 45007 | Circ[1].DelovnaMoc_III
STRCirc1DelovnaMoc_L1 | REAL | IOD_STR_TCP | 5009 | 45009 | Circ[1].DelovnaMoc_L1
STRCirc1DelovnaMoc_L2 | REAL | IOD_STR_TCP | 5011 | 45011 | Circ[1].DelovnaMoc_L2
STRCirc1DelovnaMoc_L3 | REAL | IOD_STR_TCP | 5013 | 45013 | Circ[1].DelovnaMoc_L3
STRCirc1Frekvenca_L1 | REAL | IOD_STR_TCP | 5015 | 45015 | Circ[1].Frekvenca_L1
STRCirc1InduktivnaEnergija | REAL | IOD_STR_TCP | 5017 | 45017 | Circ[1].InduktivnaEnergija
STRCirc1InduktivnaMoc_III | REAL | IOD_STR_TCP | 5019 | 45019 | Circ[1].InduktivnaMoc_III
STRCirc1JalovaMoc_L1 | REAL | IOD_STR_TCP | 5021 | 45021 | Circ[1].JalovaMoc_L1
STRCirc1JalovaMoc_L2 | REAL | IOD_STR_TCP | 5023 | 45023 | Circ[1].JalovaMoc_L2
STRCirc1JalovaMoc_L3 | REAL | IOD_STR_TCP | 5025 | 45025 | Circ[1].JalovaMoc_L3
STRCirc1KapacitivnaEnergija | REAL | IOD_STR_TCP | 5027 | 45027 | Circ[1].KapacitivnaEnergija
STRCirc1KapacitivnaMoc_III | REAL | IOD_STR_TCP | 5029 | 45029 | Circ[1].KapacitivnaMoc_III
STRCirc1MaximumDemand | REAL | IOD_STR_TCP | 5031 | 45031 | Circ[1].MaximumDemand
STRCirc1Napetost_L1_L2 | REAL | IOD_STR_TCP | 5033 | 45033 | Circ[1].Napetost_L1_L2
STRCirc1Napetost_L1_N | REAL | IOD_STR_TCP | 5035 | 45035 | Circ[1].Napetost_L1_N
STRCirc1Napetost_L2_L3 | REAL | IOD_STR_TCP | 5037 | 45037 | Circ[1].Napetost_L2_L3
STRCirc1Napetost_L2_N | REAL | IOD_STR_TCP | 5039 | 45039 | Circ[1].Napetost_L2_N
STRCirc1Napetost_L3_L1 | REAL | IOD_STR_TCP | 5041 | 45041 | Circ[1].Napetost_L3_L1
STRCirc1Napetost_L3_N | REAL | IOD_STR_TCP | 5043 | 45043 | Circ[1].Napetost_L3_N
STRCirc1NavideznaMoc_III | REAL | IOD_STR_TCP | 5045 | 45045 | Circ[1].NavideznaMoc_III
STRCirc1NicelniTok | REAL | IOD_STR_TCP | 5047 | 45047 | Circ[1].NicelniTok
STRCirc1PowerFactor_III | REAL | IOD_STR_TCP | 5049 | 45049 | Circ[1].PowerFactor_III
STRCirc1PowerFactor_L1 | REAL | IOD_STR_TCP | 5051 | 45051 | Circ[1].PowerFactor_L1
STRCirc1PowerFactor_L2 | REAL | IOD_STR_TCP | 5053 | 45053 | Circ[1].PowerFactor_L2
STRCirc1PowerFactor_L3 | REAL | IOD_STR_TCP | 5055 | 45055 | Circ[1].PowerFactor_L3
STRCirc1THDI_L1 | REAL | IOD_STR_TCP | 5057 | 45057 | Circ[1].THDI_L1
STRCirc1THDI_L2 | REAL | IOD_STR_TCP | 5059 | 45059 | Circ[1].THDI_L2
STRCirc1THDI_L3 | REAL | IOD_STR_TCP | 5061 | 45061 | Circ[1].THDI_L3
STRCirc1THDV_L1 | REAL | IOD_STR_TCP | 5063 | 45063 | Circ[1].THDV_L1
STRCirc1THDV_L2 | REAL | IOD_STR_TCP | 5065 | 45065 | Circ[1].THDV_L2
STRCirc1THDV_L3 | REAL | IOD_STR_TCP | 5067 | 45067 | Circ[1].THDV_L3
STRCirc1Tok_L1 | REAL | IOD_STR_TCP | 5069 | 45069 | Circ[1].Tok_L1
STRCirc1Tok_L2 | REAL | IOD_STR_TCP | 5071 | 45071 | Circ[1].Tok_L2
STRCirc1Tok_L3 | REAL | IOD_STR_TCP | 5073 | 45073 | Circ[1].Tok_L3
STRCirc1TokPovprecje_III | REAL | IOD_STR_TCP | 5075 | 45075 | Circ[1].TokPovprecje_III
STRCrpalkeDnfs1Current | REAL | IOD_STR_TCP | 5077 | 45077 | CrpalkeDnfs[1].Current
STRCrpalkeDnfs1StarterStatus | REAL | IOD_STR_TCP | 5079 | 45079 | CrpalkeDnfs[1].StarterStatus
STRCrpalkeDnfs1Temerature | REAL | IOD_STR_TCP | 5081 | 45081 | CrpalkeDnfs[1].Temerature
STRCrpalkeDnfs1TripCode | REAL | IOD_STR_TCP | 5083 | 45083 | CrpalkeDnfs[1].TripCode
STRCrpalkeDnfs1UreXC200 | REAL | IOD_STR_TCP | 5085 | 45085 | CrpalkeDnfs[1].UreXC200
STRCrpalkeDnfs2Current | REAL | IOD_STR_TCP | 5087 | 45087 | CrpalkeDnfs[2].Current
STRCrpalkeDnfs2StarterStatus | REAL | IOD_STR_TCP | 5089 | 45089 | CrpalkeDnfs[2].StarterStatus
STRCrpalkeDnfs2Temerature | REAL | IOD_STR_TCP | 5091 | 45091 | CrpalkeDnfs[2].Temerature
STRCrpalkeDnfs2TripCode | REAL | IOD_STR_TCP | 5093 | 45093 | CrpalkeDnfs[2].TripCode
STRCrpalkeDnfs2UreXC200 | REAL | IOD_STR_TCP | 5095 | 45095 | CrpalkeDnfs[2].UreXC200
STRCrpalkeDnfs3Current | REAL | IOD_STR_TCP | 5097 | 45097 | CrpalkeDnfs[3].Current
STRCrpalkeDnfs3StarterStatus | REAL | IOD_STR_TCP | 5099 | 45099 | CrpalkeDnfs[3].StarterStatus
STRCrpalkeDnfs3Temerature | REAL | IOD_STR_TCP | 5101 | 45101 | CrpalkeDnfs[3].Temerature
STRCrpalkeDnfs3TripCode | REAL | IOD_STR_TCP | 5103 | 45103 | CrpalkeDnfs[3].TripCode
STRCrpalkeDnfs3UreXC200 | REAL | IOD_STR_TCP | 5105 | 45105 | CrpalkeDnfs[3].UreXC200
STRCrpalkeDnfs4Current | REAL | IOD_STR_TCP | 5107 | 45107 | CrpalkeDnfs[4].Current
STRCrpalkeDnfs4StarterStatus | REAL | IOD_STR_TCP | 5109 | 45109 | CrpalkeDnfs[4].StarterStatus
STRCrpalkeDnfs4Temerature | REAL | IOD_STR_TCP | 5111 | 45111 | CrpalkeDnfs[4].Temerature
STRCrpalkeDnfs4TripCode | REAL | IOD_STR_TCP | 5113 | 45113 | CrpalkeDnfs[4].TripCode
STRCrpalkeDnfs4UreXC200 | REAL | IOD_STR_TCP | 5115 | 45115 | CrpalkeDnfs[4].UreXC200
STRCrpalkeGrfs10DeltaSetPoint | REAL | IOD_STR_TCP | 5117 | 45117 | CrpalkeGrfs[10].DeltaSetPoint
STRCrpalkeGrfs10EnergijaPoraba | REAL | IOD_STR_TCP | 5119 | 45119 | CrpalkeGrfs[10].EnergijaPoraba
STRCrpalkeGrfs10FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 5121 | 45121 | CrpalkeGrfs[10].FrekPretvornikDCNapetost
STRCrpalkeGrfs10FrekPretvornikDCTok | REAL | IOD_STR_TCP | 5123 | 45123 | CrpalkeGrfs[10].FrekPretvornikDCTok
STRCrpalkeGrfs10FreqMax | REAL | IOD_STR_TCP | 5125 | 45125 | CrpalkeGrfs[10].FreqMax
STRCrpalkeGrfs10FreqMin | REAL | IOD_STR_TCP | 5127 | 45127 | CrpalkeGrfs[10].FreqMin
STRCrpalkeGrfs10FreqUpper | REAL | IOD_STR_TCP | 5129 | 45129 | CrpalkeGrfs[10].FreqUpper
STRCrpalkeGrfs10MocMax | REAL | IOD_STR_TCP | 5131 | 45131 | CrpalkeGrfs[10].MocMax
STRCrpalkeGrfs10MocTrenutna | REAL | IOD_STR_TCP | 5133 | 45133 | CrpalkeGrfs[10].MocTrenutna
STRCrpalkeGrfs10MotorHitrost | REAL | IOD_STR_TCP | 5135 | 45135 | CrpalkeGrfs[10].MotorHitrost
STRCrpalkeGrfs10MotorTok | REAL | IOD_STR_TCP | 5137 | 45137 | CrpalkeGrfs[10].MotorTok
STRCrpalkeGrfs10NapajanjeTok | REAL | IOD_STR_TCP | 5139 | 45139 | CrpalkeGrfs[10].NapajanjeTok
STRCrpalkeGrfs10NastavitevLokalna | REAL | IOD_STR_TCP | 5141 | 45141 | CrpalkeGrfs[10].NastavitevLokalna
STRCrpalkeGrfs10NastavitevTrenutna | REAL | IOD_STR_TCP | 5143 | 45143 | CrpalkeGrfs[10].NastavitevTrenutna
STRCrpalkeGrfs10PretokMax | REAL | IOD_STR_TCP | 5145 | 45145 | CrpalkeGrfs[10].PretokMax
STRCrpalkeGrfs10PretokMin | REAL | IOD_STR_TCP | 5147 | 45147 | CrpalkeGrfs[10].PretokMin
STRCrpalkeGrfs10PretokTrenutni | REAL | IOD_STR_TCP | 5149 | 45149 | CrpalkeGrfs[10].PretokTrenutni
STRCrpalkeGrfs10PritiskMax | REAL | IOD_STR_TCP | 5151 | 45151 | CrpalkeGrfs[10].PritiskMax
STRCrpalkeGrfs10PritiskTrenutni | REAL | IOD_STR_TCP | 5153 | 45153 | CrpalkeGrfs[10].PritiskTrenutni
STRCrpalkeGrfs10ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 5155 | 45155 | CrpalkeGrfs[10].ReferencaMotorjaHzV
STRCrpalkeGrfs10ReferencaRemote | REAL | IOD_STR_TCP | 5157 | 45157 | CrpalkeGrfs[10].ReferencaRemote
STRCrpalkeGrfs10StevecUr2h | REAL | IOD_STR_TCP | 5159 | 45159 | CrpalkeGrfs[10].StevecUr2h
STRCrpalkeGrfs10SystemFeedback | REAL | IOD_STR_TCP | 5161 | 45161 | CrpalkeGrfs[10].SystemFeedback
STRCrpalkeGrfs10SystemReference | REAL | IOD_STR_TCP | 5163 | 45163 | CrpalkeGrfs[10].SystemReference
STRCrpalkeGrfs10TemperaturaMotorja | REAL | IOD_STR_TCP | 5165 | 45165 | CrpalkeGrfs[10].TemperaturaMotorja
STRCrpalkeGrfs10UreXC200 | REAL | IOD_STR_TCP | 5167 | 45167 | CrpalkeGrfs[10].UreXC200
STRCrpalkeGrfs11DeltaSetPoint | REAL | IOD_STR_TCP | 5169 | 45169 | CrpalkeGrfs[11].DeltaSetPoint
STRCrpalkeGrfs11EnergijaPoraba | REAL | IOD_STR_TCP | 5171 | 45171 | CrpalkeGrfs[11].EnergijaPoraba
STRCrpalkeGrfs11FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 5173 | 45173 | CrpalkeGrfs[11].FrekPretvornikDCNapetost
STRCrpalkeGrfs11FrekPretvornikDCTok | REAL | IOD_STR_TCP | 5175 | 45175 | CrpalkeGrfs[11].FrekPretvornikDCTok
STRCrpalkeGrfs11FreqMax | REAL | IOD_STR_TCP | 5177 | 45177 | CrpalkeGrfs[11].FreqMax
STRCrpalkeGrfs11FreqMin | REAL | IOD_STR_TCP | 5179 | 45179 | CrpalkeGrfs[11].FreqMin
STRCrpalkeGrfs11FreqUpper | REAL | IOD_STR_TCP | 5181 | 45181 | CrpalkeGrfs[11].FreqUpper
STRCrpalkeGrfs11MocMax | REAL | IOD_STR_TCP | 5183 | 45183 | CrpalkeGrfs[11].MocMax
STRCrpalkeGrfs11MocTrenutna | REAL | IOD_STR_TCP | 5185 | 45185 | CrpalkeGrfs[11].MocTrenutna
STRCrpalkeGrfs11MotorHitrost | REAL | IOD_STR_TCP | 5187 | 45187 | CrpalkeGrfs[11].MotorHitrost
STRCrpalkeGrfs11MotorTok | REAL | IOD_STR_TCP | 5189 | 45189 | CrpalkeGrfs[11].MotorTok
STRCrpalkeGrfs11NapajanjeTok | REAL | IOD_STR_TCP | 5191 | 45191 | CrpalkeGrfs[11].NapajanjeTok
STRCrpalkeGrfs11NastavitevLokalna | REAL | IOD_STR_TCP | 5193 | 45193 | CrpalkeGrfs[11].NastavitevLokalna
STRCrpalkeGrfs11NastavitevTrenutna | REAL | IOD_STR_TCP | 5195 | 45195 | CrpalkeGrfs[11].NastavitevTrenutna
STRCrpalkeGrfs11PretokMax | REAL | IOD_STR_TCP | 5197 | 45197 | CrpalkeGrfs[11].PretokMax
STRCrpalkeGrfs11PretokMin | REAL | IOD_STR_TCP | 5199 | 45199 | CrpalkeGrfs[11].PretokMin
STRCrpalkeGrfs11PretokTrenutni | REAL | IOD_STR_TCP | 5201 | 45201 | CrpalkeGrfs[11].PretokTrenutni
STRCrpalkeGrfs11PritiskMax | REAL | IOD_STR_TCP | 5203 | 45203 | CrpalkeGrfs[11].PritiskMax
STRCrpalkeGrfs11PritiskTrenutni | REAL | IOD_STR_TCP | 5205 | 45205 | CrpalkeGrfs[11].PritiskTrenutni
STRCrpalkeGrfs11ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 5207 | 45207 | CrpalkeGrfs[11].ReferencaMotorjaHzV
STRCrpalkeGrfs11ReferencaRemote | REAL | IOD_STR_TCP | 5209 | 45209 | CrpalkeGrfs[11].ReferencaRemote
STRCrpalkeGrfs11StevecUr2h | REAL | IOD_STR_TCP | 5211 | 45211 | CrpalkeGrfs[11].StevecUr2h
STRCrpalkeGrfs11SystemFeedback | REAL | IOD_STR_TCP | 5213 | 45213 | CrpalkeGrfs[11].SystemFeedback
STRCrpalkeGrfs11SystemReference | REAL | IOD_STR_TCP | 5215 | 45215 | CrpalkeGrfs[11].SystemReference
STRCrpalkeGrfs11TemperaturaMotorja | REAL | IOD_STR_TCP | 5217 | 45217 | CrpalkeGrfs[11].TemperaturaMotorja
STRCrpalkeGrfs11UreXC200 | REAL | IOD_STR_TCP | 5219 | 45219 | CrpalkeGrfs[11].UreXC200
STRCrpalkeGrfs12DeltaSetPoint | REAL | IOD_STR_TCP | 5221 | 45221 | CrpalkeGrfs[12].DeltaSetPoint
STRCrpalkeGrfs12EnergijaPoraba | REAL | IOD_STR_TCP | 5223 | 45223 | CrpalkeGrfs[12].EnergijaPoraba
STRCrpalkeGrfs12FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 5225 | 45225 | CrpalkeGrfs[12].FrekPretvornikDCNapetost
STRCrpalkeGrfs12FrekPretvornikDCTok | REAL | IOD_STR_TCP | 5227 | 45227 | CrpalkeGrfs[12].FrekPretvornikDCTok
STRCrpalkeGrfs12FreqMax | REAL | IOD_STR_TCP | 5229 | 45229 | CrpalkeGrfs[12].FreqMax
STRCrpalkeGrfs12FreqMin | REAL | IOD_STR_TCP | 5231 | 45231 | CrpalkeGrfs[12].FreqMin
STRCrpalkeGrfs12FreqUpper | REAL | IOD_STR_TCP | 5233 | 45233 | CrpalkeGrfs[12].FreqUpper
STRCrpalkeGrfs12MocMax | REAL | IOD_STR_TCP | 5235 | 45235 | CrpalkeGrfs[12].MocMax
STRCrpalkeGrfs12MocTrenutna | REAL | IOD_STR_TCP | 5237 | 45237 | CrpalkeGrfs[12].MocTrenutna
STRCrpalkeGrfs12MotorHitrost | REAL | IOD_STR_TCP | 5239 | 45239 | CrpalkeGrfs[12].MotorHitrost
STRCrpalkeGrfs12MotorTok | REAL | IOD_STR_TCP | 5241 | 45241 | CrpalkeGrfs[12].MotorTok
STRCrpalkeGrfs12NapajanjeTok | REAL | IOD_STR_TCP | 5243 | 45243 | CrpalkeGrfs[12].NapajanjeTok
STRCrpalkeGrfs12NastavitevLokalna | REAL | IOD_STR_TCP | 5245 | 45245 | CrpalkeGrfs[12].NastavitevLokalna
STRCrpalkeGrfs12NastavitevTrenutna | REAL | IOD_STR_TCP | 5247 | 45247 | CrpalkeGrfs[12].NastavitevTrenutna
STRCrpalkeGrfs12PretokMax | REAL | IOD_STR_TCP | 5249 | 45249 | CrpalkeGrfs[12].PretokMax
STRCrpalkeGrfs12PretokMin | REAL | IOD_STR_TCP | 5251 | 45251 | CrpalkeGrfs[12].PretokMin
STRCrpalkeGrfs12PretokTrenutni | REAL | IOD_STR_TCP | 5253 | 45253 | CrpalkeGrfs[12].PretokTrenutni
STRCrpalkeGrfs12PritiskMax | REAL | IOD_STR_TCP | 5255 | 45255 | CrpalkeGrfs[12].PritiskMax
STRCrpalkeGrfs12PritiskTrenutni | REAL | IOD_STR_TCP | 5257 | 45257 | CrpalkeGrfs[12].PritiskTrenutni
STRCrpalkeGrfs12ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 5259 | 45259 | CrpalkeGrfs[12].ReferencaMotorjaHzV
STRCrpalkeGrfs12ReferencaRemote | REAL | IOD_STR_TCP | 5261 | 45261 | CrpalkeGrfs[12].ReferencaRemote
STRCrpalkeGrfs12StevecUr2h | REAL | IOD_STR_TCP | 5263 | 45263 | CrpalkeGrfs[12].StevecUr2h
STRCrpalkeGrfs12SystemFeedback | REAL | IOD_STR_TCP | 5265 | 45265 | CrpalkeGrfs[12].SystemFeedback
STRCrpalkeGrfs12SystemReference | REAL | IOD_STR_TCP | 5267 | 45267 | CrpalkeGrfs[12].SystemReference
STRCrpalkeGrfs12TemperaturaMotorja | REAL | IOD_STR_TCP | 5269 | 45269 | CrpalkeGrfs[12].TemperaturaMotorja
STRCrpalkeGrfs12UreXC200 | REAL | IOD_STR_TCP | 5271 | 45271 | CrpalkeGrfs[12].UreXC200
STRCrpalkeGrfs13DeltaSetPoint | REAL | IOD_STR_TCP | 5273 | 45273 | CrpalkeGrfs[13].DeltaSetPoint
STRCrpalkeGrfs13EnergijaPoraba | REAL | IOD_STR_TCP | 5275 | 45275 | CrpalkeGrfs[13].EnergijaPoraba
STRCrpalkeGrfs13FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 5277 | 45277 | CrpalkeGrfs[13].FrekPretvornikDCNapetost
STRCrpalkeGrfs13FrekPretvornikDCTok | REAL | IOD_STR_TCP | 5279 | 45279 | CrpalkeGrfs[13].FrekPretvornikDCTok
STRCrpalkeGrfs13FreqMax | REAL | IOD_STR_TCP | 5281 | 45281 | CrpalkeGrfs[13].FreqMax
STRCrpalkeGrfs13FreqMin | REAL | IOD_STR_TCP | 5283 | 45283 | CrpalkeGrfs[13].FreqMin
STRCrpalkeGrfs13FreqUpper | REAL | IOD_STR_TCP | 5285 | 45285 | CrpalkeGrfs[13].FreqUpper
STRCrpalkeGrfs13MocMax | REAL | IOD_STR_TCP | 5287 | 45287 | CrpalkeGrfs[13].MocMax
STRCrpalkeGrfs13MocTrenutna | REAL | IOD_STR_TCP | 5289 | 45289 | CrpalkeGrfs[13].MocTrenutna
STRCrpalkeGrfs13MotorHitrost | REAL | IOD_STR_TCP | 5291 | 45291 | CrpalkeGrfs[13].MotorHitrost
STRCrpalkeGrfs13MotorTok | REAL | IOD_STR_TCP | 5293 | 45293 | CrpalkeGrfs[13].MotorTok
STRCrpalkeGrfs13NapajanjeTok | REAL | IOD_STR_TCP | 5295 | 45295 | CrpalkeGrfs[13].NapajanjeTok
STRCrpalkeGrfs13NastavitevLokalna | REAL | IOD_STR_TCP | 5297 | 45297 | CrpalkeGrfs[13].NastavitevLokalna
STRCrpalkeGrfs13NastavitevTrenutna | REAL | IOD_STR_TCP | 5299 | 45299 | CrpalkeGrfs[13].NastavitevTrenutna
STRCrpalkeGrfs13PretokMax | REAL | IOD_STR_TCP | 5301 | 45301 | CrpalkeGrfs[13].PretokMax
STRCrpalkeGrfs13PretokMin | REAL | IOD_STR_TCP | 5303 | 45303 | CrpalkeGrfs[13].PretokMin
STRCrpalkeGrfs13PretokTrenutni | REAL | IOD_STR_TCP | 5305 | 45305 | CrpalkeGrfs[13].PretokTrenutni
STRCrpalkeGrfs13PritiskMax | REAL | IOD_STR_TCP | 5307 | 45307 | CrpalkeGrfs[13].PritiskMax
STRCrpalkeGrfs13PritiskTrenutni | REAL | IOD_STR_TCP | 5309 | 45309 | CrpalkeGrfs[13].PritiskTrenutni
STRCrpalkeGrfs13ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 5311 | 45311 | CrpalkeGrfs[13].ReferencaMotorjaHzV
STRCrpalkeGrfs13ReferencaRemote | REAL | IOD_STR_TCP | 5313 | 45313 | CrpalkeGrfs[13].ReferencaRemote
STRCrpalkeGrfs13StevecUr2h | REAL | IOD_STR_TCP | 5315 | 45315 | CrpalkeGrfs[13].StevecUr2h
STRCrpalkeGrfs13SystemFeedback | REAL | IOD_STR_TCP | 5317 | 45317 | CrpalkeGrfs[13].SystemFeedback
STRCrpalkeGrfs13SystemReference | REAL | IOD_STR_TCP | 5319 | 45319 | CrpalkeGrfs[13].SystemReference
STRCrpalkeGrfs13TemperaturaMotorja | REAL | IOD_STR_TCP | 5321 | 45321 | CrpalkeGrfs[13].TemperaturaMotorja
STRCrpalkeGrfs13UreXC200 | REAL | IOD_STR_TCP | 5323 | 45323 | CrpalkeGrfs[13].UreXC200
STRCrpalkeGrfs14DeltaSetPoint | REAL | IOD_STR_TCP | 5325 | 45325 | CrpalkeGrfs[14].DeltaSetPoint
STRCrpalkeGrfs14EnergijaPoraba | REAL | IOD_STR_TCP | 5327 | 45327 | CrpalkeGrfs[14].EnergijaPoraba
STRCrpalkeGrfs14FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 5329 | 45329 | CrpalkeGrfs[14].FrekPretvornikDCNapetost
STRCrpalkeGrfs14FrekPretvornikDCTok | REAL | IOD_STR_TCP | 5331 | 45331 | CrpalkeGrfs[14].FrekPretvornikDCTok
STRCrpalkeGrfs14FreqMax | REAL | IOD_STR_TCP | 5333 | 45333 | CrpalkeGrfs[14].FreqMax
STRCrpalkeGrfs14FreqMin | REAL | IOD_STR_TCP | 5335 | 45335 | CrpalkeGrfs[14].FreqMin
STRCrpalkeGrfs14FreqUpper | REAL | IOD_STR_TCP | 5337 | 45337 | CrpalkeGrfs[14].FreqUpper
STRCrpalkeGrfs14MocMax | REAL | IOD_STR_TCP | 5339 | 45339 | CrpalkeGrfs[14].MocMax
STRCrpalkeGrfs14MocTrenutna | REAL | IOD_STR_TCP | 5341 | 45341 | CrpalkeGrfs[14].MocTrenutna
STRCrpalkeGrfs14MotorHitrost | REAL | IOD_STR_TCP | 5343 | 45343 | CrpalkeGrfs[14].MotorHitrost
STRCrpalkeGrfs14MotorTok | REAL | IOD_STR_TCP | 5345 | 45345 | CrpalkeGrfs[14].MotorTok
STRCrpalkeGrfs14NapajanjeTok | REAL | IOD_STR_TCP | 5347 | 45347 | CrpalkeGrfs[14].NapajanjeTok
STRCrpalkeGrfs14NastavitevLokalna | REAL | IOD_STR_TCP | 5349 | 45349 | CrpalkeGrfs[14].NastavitevLokalna
STRCrpalkeGrfs14NastavitevTrenutna | REAL | IOD_STR_TCP | 5351 | 45351 | CrpalkeGrfs[14].NastavitevTrenutna
STRCrpalkeGrfs14PretokMax | REAL | IOD_STR_TCP | 5353 | 45353 | CrpalkeGrfs[14].PretokMax
STRCrpalkeGrfs14PretokMin | REAL | IOD_STR_TCP | 5355 | 45355 | CrpalkeGrfs[14].PretokMin
STRCrpalkeGrfs14PretokTrenutni | REAL | IOD_STR_TCP | 5357 | 45357 | CrpalkeGrfs[14].PretokTrenutni
STRCrpalkeGrfs14PritiskMax | REAL | IOD_STR_TCP | 5359 | 45359 | CrpalkeGrfs[14].PritiskMax
STRCrpalkeGrfs14PritiskTrenutni | REAL | IOD_STR_TCP | 5361 | 45361 | CrpalkeGrfs[14].PritiskTrenutni
STRCrpalkeGrfs14ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 5363 | 45363 | CrpalkeGrfs[14].ReferencaMotorjaHzV
STRCrpalkeGrfs14ReferencaRemote | REAL | IOD_STR_TCP | 5365 | 45365 | CrpalkeGrfs[14].ReferencaRemote
STRCrpalkeGrfs14StevecUr2h | REAL | IOD_STR_TCP | 5367 | 45367 | CrpalkeGrfs[14].StevecUr2h
STRCrpalkeGrfs14SystemFeedback | REAL | IOD_STR_TCP | 5369 | 45369 | CrpalkeGrfs[14].SystemFeedback
STRCrpalkeGrfs14SystemReference | REAL | IOD_STR_TCP | 5371 | 45371 | CrpalkeGrfs[14].SystemReference
STRCrpalkeGrfs14TemperaturaMotorja | REAL | IOD_STR_TCP | 5373 | 45373 | CrpalkeGrfs[14].TemperaturaMotorja
STRCrpalkeGrfs14UreXC200 | REAL | IOD_STR_TCP | 5375 | 45375 | CrpalkeGrfs[14].UreXC200
STRCrpalkeGrfs1DeltaSetPoint | REAL | IOD_STR_TCP | 5377 | 45377 | CrpalkeGrfs[1].DeltaSetPoint
STRCrpalkeGrfs1EnergijaPoraba | REAL | IOD_STR_TCP | 5379 | 45379 | CrpalkeGrfs[1].EnergijaPoraba
STRCrpalkeGrfs1FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 5381 | 45381 | CrpalkeGrfs[1].FrekPretvornikDCNapetost
STRCrpalkeGrfs1FrekPretvornikDCTok | REAL | IOD_STR_TCP | 5383 | 45383 | CrpalkeGrfs[1].FrekPretvornikDCTok
STRCrpalkeGrfs1FreqMax | REAL | IOD_STR_TCP | 5385 | 45385 | CrpalkeGrfs[1].FreqMax
STRCrpalkeGrfs1FreqMin | REAL | IOD_STR_TCP | 5387 | 45387 | CrpalkeGrfs[1].FreqMin
STRCrpalkeGrfs1FreqUpper | REAL | IOD_STR_TCP | 5389 | 45389 | CrpalkeGrfs[1].FreqUpper
STRCrpalkeGrfs1MocMax | REAL | IOD_STR_TCP | 5391 | 45391 | CrpalkeGrfs[1].MocMax
STRCrpalkeGrfs1MocTrenutna | REAL | IOD_STR_TCP | 5393 | 45393 | CrpalkeGrfs[1].MocTrenutna
STRCrpalkeGrfs1MotorHitrost | REAL | IOD_STR_TCP | 5395 | 45395 | CrpalkeGrfs[1].MotorHitrost
STRCrpalkeGrfs1MotorTok | REAL | IOD_STR_TCP | 5397 | 45397 | CrpalkeGrfs[1].MotorTok
STRCrpalkeGrfs1NapajanjeTok | REAL | IOD_STR_TCP | 5399 | 45399 | CrpalkeGrfs[1].NapajanjeTok
STRCrpalkeGrfs1NastavitevLokalna | REAL | IOD_STR_TCP | 5401 | 45401 | CrpalkeGrfs[1].NastavitevLokalna
STRCrpalkeGrfs1NastavitevTrenutna | REAL | IOD_STR_TCP | 5403 | 45403 | CrpalkeGrfs[1].NastavitevTrenutna
STRCrpalkeGrfs1PretokMax | REAL | IOD_STR_TCP | 5405 | 45405 | CrpalkeGrfs[1].PretokMax
STRCrpalkeGrfs1PretokMin | REAL | IOD_STR_TCP | 5407 | 45407 | CrpalkeGrfs[1].PretokMin
STRCrpalkeGrfs1PretokTrenutni | REAL | IOD_STR_TCP | 5409 | 45409 | CrpalkeGrfs[1].PretokTrenutni
STRCrpalkeGrfs1PritiskMax | REAL | IOD_STR_TCP | 5411 | 45411 | CrpalkeGrfs[1].PritiskMax
STRCrpalkeGrfs1PritiskTrenutni | REAL | IOD_STR_TCP | 5413 | 45413 | CrpalkeGrfs[1].PritiskTrenutni
STRCrpalkeGrfs1ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 5415 | 45415 | CrpalkeGrfs[1].ReferencaMotorjaHzV
STRCrpalkeGrfs1ReferencaRemote | REAL | IOD_STR_TCP | 5417 | 45417 | CrpalkeGrfs[1].ReferencaRemote
STRCrpalkeGrfs1StevecUr2h | REAL | IOD_STR_TCP | 5419 | 45419 | CrpalkeGrfs[1].StevecUr2h
STRCrpalkeGrfs1SystemFeedback | REAL | IOD_STR_TCP | 5421 | 45421 | CrpalkeGrfs[1].SystemFeedback
STRCrpalkeGrfs1SystemReference | REAL | IOD_STR_TCP | 5423 | 45423 | CrpalkeGrfs[1].SystemReference
STRCrpalkeGrfs1TemperaturaMotorja | REAL | IOD_STR_TCP | 5425 | 45425 | CrpalkeGrfs[1].TemperaturaMotorja
STRCrpalkeGrfs1UreXC200 | REAL | IOD_STR_TCP | 5427 | 45427 | CrpalkeGrfs[1].UreXC200
STRCrpalkeGrfs2DeltaSetPoint | REAL | IOD_STR_TCP | 5429 | 45429 | CrpalkeGrfs[2].DeltaSetPoint
STRCrpalkeGrfs2EnergijaPoraba | REAL | IOD_STR_TCP | 5431 | 45431 | CrpalkeGrfs[2].EnergijaPoraba
STRCrpalkeGrfs2FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 5433 | 45433 | CrpalkeGrfs[2].FrekPretvornikDCNapetost
STRCrpalkeGrfs2FrekPretvornikDCTok | REAL | IOD_STR_TCP | 5435 | 45435 | CrpalkeGrfs[2].FrekPretvornikDCTok
STRCrpalkeGrfs2FreqMax | REAL | IOD_STR_TCP | 5437 | 45437 | CrpalkeGrfs[2].FreqMax
STRCrpalkeGrfs2FreqMin | REAL | IOD_STR_TCP | 5439 | 45439 | CrpalkeGrfs[2].FreqMin
STRCrpalkeGrfs2FreqUpper | REAL | IOD_STR_TCP | 5441 | 45441 | CrpalkeGrfs[2].FreqUpper
STRCrpalkeGrfs2MocMax | REAL | IOD_STR_TCP | 5443 | 45443 | CrpalkeGrfs[2].MocMax
STRCrpalkeGrfs2MocTrenutna | REAL | IOD_STR_TCP | 5445 | 45445 | CrpalkeGrfs[2].MocTrenutna
STRCrpalkeGrfs2MotorHitrost | REAL | IOD_STR_TCP | 5447 | 45447 | CrpalkeGrfs[2].MotorHitrost
STRCrpalkeGrfs2MotorTok | REAL | IOD_STR_TCP | 5449 | 45449 | CrpalkeGrfs[2].MotorTok
STRCrpalkeGrfs2NapajanjeTok | REAL | IOD_STR_TCP | 5451 | 45451 | CrpalkeGrfs[2].NapajanjeTok
STRCrpalkeGrfs2NastavitevLokalna | REAL | IOD_STR_TCP | 5453 | 45453 | CrpalkeGrfs[2].NastavitevLokalna
STRCrpalkeGrfs2NastavitevTrenutna | REAL | IOD_STR_TCP | 5455 | 45455 | CrpalkeGrfs[2].NastavitevTrenutna
STRCrpalkeGrfs2PretokMax | REAL | IOD_STR_TCP | 5457 | 45457 | CrpalkeGrfs[2].PretokMax
STRCrpalkeGrfs2PretokMin | REAL | IOD_STR_TCP | 5459 | 45459 | CrpalkeGrfs[2].PretokMin
STRCrpalkeGrfs2PretokTrenutni | REAL | IOD_STR_TCP | 5461 | 45461 | CrpalkeGrfs[2].PretokTrenutni
STRCrpalkeGrfs2PritiskMax | REAL | IOD_STR_TCP | 5463 | 45463 | CrpalkeGrfs[2].PritiskMax
STRCrpalkeGrfs2PritiskTrenutni | REAL | IOD_STR_TCP | 5465 | 45465 | CrpalkeGrfs[2].PritiskTrenutni
STRCrpalkeGrfs2ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 5467 | 45467 | CrpalkeGrfs[2].ReferencaMotorjaHzV
STRCrpalkeGrfs2ReferencaRemote | REAL | IOD_STR_TCP | 5469 | 45469 | CrpalkeGrfs[2].ReferencaRemote
STRCrpalkeGrfs2StevecUr2h | REAL | IOD_STR_TCP | 5471 | 45471 | CrpalkeGrfs[2].StevecUr2h
STRCrpalkeGrfs2SystemFeedback | REAL | IOD_STR_TCP | 5473 | 45473 | CrpalkeGrfs[2].SystemFeedback
STRCrpalkeGrfs2SystemReference | REAL | IOD_STR_TCP | 5475 | 45475 | CrpalkeGrfs[2].SystemReference
STRCrpalkeGrfs2TemperaturaMotorja | REAL | IOD_STR_TCP | 5477 | 45477 | CrpalkeGrfs[2].TemperaturaMotorja
STRCrpalkeGrfs2UreXC200 | REAL | IOD_STR_TCP | 5479 | 45479 | CrpalkeGrfs[2].UreXC200
STRCrpalkeGrfs3DeltaSetPoint | REAL | IOD_STR_TCP | 5481 | 45481 | CrpalkeGrfs[3].DeltaSetPoint
STRCrpalkeGrfs3EnergijaPoraba | REAL | IOD_STR_TCP | 5483 | 45483 | CrpalkeGrfs[3].EnergijaPoraba
STRCrpalkeGrfs3FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 5485 | 45485 | CrpalkeGrfs[3].FrekPretvornikDCNapetost
STRCrpalkeGrfs3FrekPretvornikDCTok | REAL | IOD_STR_TCP | 5487 | 45487 | CrpalkeGrfs[3].FrekPretvornikDCTok
STRCrpalkeGrfs3FreqMax | REAL | IOD_STR_TCP | 5489 | 45489 | CrpalkeGrfs[3].FreqMax
STRCrpalkeGrfs3FreqMin | REAL | IOD_STR_TCP | 5491 | 45491 | CrpalkeGrfs[3].FreqMin
STRCrpalkeGrfs3FreqUpper | REAL | IOD_STR_TCP | 5493 | 45493 | CrpalkeGrfs[3].FreqUpper
STRCrpalkeGrfs3MocMax | REAL | IOD_STR_TCP | 5495 | 45495 | CrpalkeGrfs[3].MocMax
STRCrpalkeGrfs3MocTrenutna | REAL | IOD_STR_TCP | 5497 | 45497 | CrpalkeGrfs[3].MocTrenutna
STRCrpalkeGrfs3MotorHitrost | REAL | IOD_STR_TCP | 5499 | 45499 | CrpalkeGrfs[3].MotorHitrost
STRCrpalkeGrfs3MotorTok | REAL | IOD_STR_TCP | 5501 | 45501 | CrpalkeGrfs[3].MotorTok
STRCrpalkeGrfs3NapajanjeTok | REAL | IOD_STR_TCP | 5503 | 45503 | CrpalkeGrfs[3].NapajanjeTok
STRCrpalkeGrfs3NastavitevLokalna | REAL | IOD_STR_TCP | 5505 | 45505 | CrpalkeGrfs[3].NastavitevLokalna
STRCrpalkeGrfs3NastavitevTrenutna | REAL | IOD_STR_TCP | 5507 | 45507 | CrpalkeGrfs[3].NastavitevTrenutna
STRCrpalkeGrfs3PretokMax | REAL | IOD_STR_TCP | 5509 | 45509 | CrpalkeGrfs[3].PretokMax
STRCrpalkeGrfs3PretokMin | REAL | IOD_STR_TCP | 5511 | 45511 | CrpalkeGrfs[3].PretokMin
STRCrpalkeGrfs3PretokTrenutni | REAL | IOD_STR_TCP | 5513 | 45513 | CrpalkeGrfs[3].PretokTrenutni
STRCrpalkeGrfs3PritiskMax | REAL | IOD_STR_TCP | 5515 | 45515 | CrpalkeGrfs[3].PritiskMax
STRCrpalkeGrfs3PritiskTrenutni | REAL | IOD_STR_TCP | 5517 | 45517 | CrpalkeGrfs[3].PritiskTrenutni
STRCrpalkeGrfs3ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 5519 | 45519 | CrpalkeGrfs[3].ReferencaMotorjaHzV
STRCrpalkeGrfs3ReferencaRemote | REAL | IOD_STR_TCP | 5521 | 45521 | CrpalkeGrfs[3].ReferencaRemote
STRCrpalkeGrfs3StevecUr2h | REAL | IOD_STR_TCP | 5523 | 45523 | CrpalkeGrfs[3].StevecUr2h
STRCrpalkeGrfs3SystemFeedback | REAL | IOD_STR_TCP | 5525 | 45525 | CrpalkeGrfs[3].SystemFeedback
STRCrpalkeGrfs3SystemReference | REAL | IOD_STR_TCP | 5527 | 45527 | CrpalkeGrfs[3].SystemReference
STRCrpalkeGrfs3TemperaturaMotorja | REAL | IOD_STR_TCP | 5529 | 45529 | CrpalkeGrfs[3].TemperaturaMotorja
STRCrpalkeGrfs3UreXC200 | REAL | IOD_STR_TCP | 5531 | 45531 | CrpalkeGrfs[3].UreXC200
STRCrpalkeGrfs4DeltaSetPoint | REAL | IOD_STR_TCP | 5533 | 45533 | CrpalkeGrfs[4].DeltaSetPoint
STRCrpalkeGrfs4EnergijaPoraba | REAL | IOD_STR_TCP | 5535 | 45535 | CrpalkeGrfs[4].EnergijaPoraba
STRCrpalkeGrfs4FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 5537 | 45537 | CrpalkeGrfs[4].FrekPretvornikDCNapetost
STRCrpalkeGrfs4FrekPretvornikDCTok | REAL | IOD_STR_TCP | 5539 | 45539 | CrpalkeGrfs[4].FrekPretvornikDCTok
STRCrpalkeGrfs4FreqMax | REAL | IOD_STR_TCP | 5541 | 45541 | CrpalkeGrfs[4].FreqMax
STRCrpalkeGrfs4FreqMin | REAL | IOD_STR_TCP | 5543 | 45543 | CrpalkeGrfs[4].FreqMin
STRCrpalkeGrfs4FreqUpper | REAL | IOD_STR_TCP | 5545 | 45545 | CrpalkeGrfs[4].FreqUpper
STRCrpalkeGrfs4MocMax | REAL | IOD_STR_TCP | 5547 | 45547 | CrpalkeGrfs[4].MocMax
STRCrpalkeGrfs4MocTrenutna | REAL | IOD_STR_TCP | 5549 | 45549 | CrpalkeGrfs[4].MocTrenutna
STRCrpalkeGrfs4MotorHitrost | REAL | IOD_STR_TCP | 5551 | 45551 | CrpalkeGrfs[4].MotorHitrost
STRCrpalkeGrfs4MotorTok | REAL | IOD_STR_TCP | 5553 | 45553 | CrpalkeGrfs[4].MotorTok
STRCrpalkeGrfs4NapajanjeTok | REAL | IOD_STR_TCP | 5555 | 45555 | CrpalkeGrfs[4].NapajanjeTok
STRCrpalkeGrfs4NastavitevLokalna | REAL | IOD_STR_TCP | 5557 | 45557 | CrpalkeGrfs[4].NastavitevLokalna
STRCrpalkeGrfs4NastavitevTrenutna | REAL | IOD_STR_TCP | 5559 | 45559 | CrpalkeGrfs[4].NastavitevTrenutna
STRCrpalkeGrfs4PretokMax | REAL | IOD_STR_TCP | 5561 | 45561 | CrpalkeGrfs[4].PretokMax
STRCrpalkeGrfs4PretokMin | REAL | IOD_STR_TCP | 5563 | 45563 | CrpalkeGrfs[4].PretokMin
STRCrpalkeGrfs4PretokTrenutni | REAL | IOD_STR_TCP | 5565 | 45565 | CrpalkeGrfs[4].PretokTrenutni
STRCrpalkeGrfs4PritiskMax | REAL | IOD_STR_TCP | 5567 | 45567 | CrpalkeGrfs[4].PritiskMax
STRCrpalkeGrfs4PritiskTrenutni | REAL | IOD_STR_TCP | 5569 | 45569 | CrpalkeGrfs[4].PritiskTrenutni
STRCrpalkeGrfs4ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 5571 | 45571 | CrpalkeGrfs[4].ReferencaMotorjaHzV
STRCrpalkeGrfs4ReferencaRemote | REAL | IOD_STR_TCP | 5573 | 45573 | CrpalkeGrfs[4].ReferencaRemote
STRCrpalkeGrfs4StevecUr2h | REAL | IOD_STR_TCP | 5575 | 45575 | CrpalkeGrfs[4].StevecUr2h
STRCrpalkeGrfs4SystemFeedback | REAL | IOD_STR_TCP | 5577 | 45577 | CrpalkeGrfs[4].SystemFeedback
STRCrpalkeGrfs4SystemReference | REAL | IOD_STR_TCP | 5579 | 45579 | CrpalkeGrfs[4].SystemReference
STRCrpalkeGrfs4TemperaturaMotorja | REAL | IOD_STR_TCP | 5581 | 45581 | CrpalkeGrfs[4].TemperaturaMotorja
STRCrpalkeGrfs4UreXC200 | REAL | IOD_STR_TCP | 5583 | 45583 | CrpalkeGrfs[4].UreXC200
STRCrpalkeGrfs5DeltaSetPoint | REAL | IOD_STR_TCP | 5585 | 45585 | CrpalkeGrfs[5].DeltaSetPoint
STRCrpalkeGrfs5EnergijaPoraba | REAL | IOD_STR_TCP | 5587 | 45587 | CrpalkeGrfs[5].EnergijaPoraba
STRCrpalkeGrfs5FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 5589 | 45589 | CrpalkeGrfs[5].FrekPretvornikDCNapetost
STRCrpalkeGrfs5FrekPretvornikDCTok | REAL | IOD_STR_TCP | 5591 | 45591 | CrpalkeGrfs[5].FrekPretvornikDCTok
STRCrpalkeGrfs5FreqMax | REAL | IOD_STR_TCP | 5593 | 45593 | CrpalkeGrfs[5].FreqMax
STRCrpalkeGrfs5FreqMin | REAL | IOD_STR_TCP | 5595 | 45595 | CrpalkeGrfs[5].FreqMin
STRCrpalkeGrfs5FreqUpper | REAL | IOD_STR_TCP | 5597 | 45597 | CrpalkeGrfs[5].FreqUpper
STRCrpalkeGrfs5MocMax | REAL | IOD_STR_TCP | 5599 | 45599 | CrpalkeGrfs[5].MocMax
STRCrpalkeGrfs5MocTrenutna | REAL | IOD_STR_TCP | 5601 | 45601 | CrpalkeGrfs[5].MocTrenutna
STRCrpalkeGrfs5MotorHitrost | REAL | IOD_STR_TCP | 5603 | 45603 | CrpalkeGrfs[5].MotorHitrost
STRCrpalkeGrfs5MotorTok | REAL | IOD_STR_TCP | 5605 | 45605 | CrpalkeGrfs[5].MotorTok
STRCrpalkeGrfs5NapajanjeTok | REAL | IOD_STR_TCP | 5607 | 45607 | CrpalkeGrfs[5].NapajanjeTok
STRCrpalkeGrfs5NastavitevLokalna | REAL | IOD_STR_TCP | 5609 | 45609 | CrpalkeGrfs[5].NastavitevLokalna
STRCrpalkeGrfs5NastavitevTrenutna | REAL | IOD_STR_TCP | 5611 | 45611 | CrpalkeGrfs[5].NastavitevTrenutna
STRCrpalkeGrfs5PretokMax | REAL | IOD_STR_TCP | 5613 | 45613 | CrpalkeGrfs[5].PretokMax
STRCrpalkeGrfs5PretokMin | REAL | IOD_STR_TCP | 5615 | 45615 | CrpalkeGrfs[5].PretokMin
STRCrpalkeGrfs5PretokTrenutni | REAL | IOD_STR_TCP | 5617 | 45617 | CrpalkeGrfs[5].PretokTrenutni
STRCrpalkeGrfs5PritiskMax | REAL | IOD_STR_TCP | 5619 | 45619 | CrpalkeGrfs[5].PritiskMax
STRCrpalkeGrfs5PritiskTrenutni | REAL | IOD_STR_TCP | 5621 | 45621 | CrpalkeGrfs[5].PritiskTrenutni
STRCrpalkeGrfs5ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 5623 | 45623 | CrpalkeGrfs[5].ReferencaMotorjaHzV
STRCrpalkeGrfs5ReferencaRemote | REAL | IOD_STR_TCP | 5625 | 45625 | CrpalkeGrfs[5].ReferencaRemote
STRCrpalkeGrfs5StevecUr2h | REAL | IOD_STR_TCP | 5627 | 45627 | CrpalkeGrfs[5].StevecUr2h
STRCrpalkeGrfs5SystemFeedback | REAL | IOD_STR_TCP | 5629 | 45629 | CrpalkeGrfs[5].SystemFeedback
STRCrpalkeGrfs5SystemReference | REAL | IOD_STR_TCP | 5631 | 45631 | CrpalkeGrfs[5].SystemReference
STRCrpalkeGrfs5TemperaturaMotorja | REAL | IOD_STR_TCP | 5633 | 45633 | CrpalkeGrfs[5].TemperaturaMotorja
STRCrpalkeGrfs5UreXC200 | REAL | IOD_STR_TCP | 5635 | 45635 | CrpalkeGrfs[5].UreXC200
STRCrpalkeGrfs6DeltaSetPoint | REAL | IOD_STR_TCP | 5637 | 45637 | CrpalkeGrfs[6].DeltaSetPoint
STRCrpalkeGrfs6EnergijaPoraba | REAL | IOD_STR_TCP | 5639 | 45639 | CrpalkeGrfs[6].EnergijaPoraba
STRCrpalkeGrfs6FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 5641 | 45641 | CrpalkeGrfs[6].FrekPretvornikDCNapetost
STRCrpalkeGrfs6FrekPretvornikDCTok | REAL | IOD_STR_TCP | 5643 | 45643 | CrpalkeGrfs[6].FrekPretvornikDCTok
STRCrpalkeGrfs6FreqMax | REAL | IOD_STR_TCP | 5645 | 45645 | CrpalkeGrfs[6].FreqMax
STRCrpalkeGrfs6FreqMin | REAL | IOD_STR_TCP | 5647 | 45647 | CrpalkeGrfs[6].FreqMin
STRCrpalkeGrfs6FreqUpper | REAL | IOD_STR_TCP | 5649 | 45649 | CrpalkeGrfs[6].FreqUpper
STRCrpalkeGrfs6MocMax | REAL | IOD_STR_TCP | 5651 | 45651 | CrpalkeGrfs[6].MocMax
STRCrpalkeGrfs6MocTrenutna | REAL | IOD_STR_TCP | 5653 | 45653 | CrpalkeGrfs[6].MocTrenutna
STRCrpalkeGrfs6MotorHitrost | REAL | IOD_STR_TCP | 5655 | 45655 | CrpalkeGrfs[6].MotorHitrost
STRCrpalkeGrfs6MotorTok | REAL | IOD_STR_TCP | 5657 | 45657 | CrpalkeGrfs[6].MotorTok
STRCrpalkeGrfs6NapajanjeTok | REAL | IOD_STR_TCP | 5659 | 45659 | CrpalkeGrfs[6].NapajanjeTok
STRCrpalkeGrfs6NastavitevLokalna | REAL | IOD_STR_TCP | 5661 | 45661 | CrpalkeGrfs[6].NastavitevLokalna
STRCrpalkeGrfs6NastavitevTrenutna | REAL | IOD_STR_TCP | 5663 | 45663 | CrpalkeGrfs[6].NastavitevTrenutna
STRCrpalkeGrfs6PretokMax | REAL | IOD_STR_TCP | 5665 | 45665 | CrpalkeGrfs[6].PretokMax
STRCrpalkeGrfs6PretokMin | REAL | IOD_STR_TCP | 5667 | 45667 | CrpalkeGrfs[6].PretokMin
STRCrpalkeGrfs6PretokTrenutni | REAL | IOD_STR_TCP | 5669 | 45669 | CrpalkeGrfs[6].PretokTrenutni
STRCrpalkeGrfs6PritiskMax | REAL | IOD_STR_TCP | 5671 | 45671 | CrpalkeGrfs[6].PritiskMax
STRCrpalkeGrfs6PritiskTrenutni | REAL | IOD_STR_TCP | 5673 | 45673 | CrpalkeGrfs[6].PritiskTrenutni
STRCrpalkeGrfs6ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 5675 | 45675 | CrpalkeGrfs[6].ReferencaMotorjaHzV
STRCrpalkeGrfs6ReferencaRemote | REAL | IOD_STR_TCP | 5677 | 45677 | CrpalkeGrfs[6].ReferencaRemote
STRCrpalkeGrfs6StevecUr2h | REAL | IOD_STR_TCP | 5679 | 45679 | CrpalkeGrfs[6].StevecUr2h
STRCrpalkeGrfs6SystemFeedback | REAL | IOD_STR_TCP | 5681 | 45681 | CrpalkeGrfs[6].SystemFeedback
STRCrpalkeGrfs6SystemReference | REAL | IOD_STR_TCP | 5683 | 45683 | CrpalkeGrfs[6].SystemReference
STRCrpalkeGrfs6TemperaturaMotorja | REAL | IOD_STR_TCP | 5685 | 45685 | CrpalkeGrfs[6].TemperaturaMotorja
STRCrpalkeGrfs6UreXC200 | REAL | IOD_STR_TCP | 5687 | 45687 | CrpalkeGrfs[6].UreXC200
STRCrpalkeGrfs7DeltaSetPoint | REAL | IOD_STR_TCP | 5689 | 45689 | CrpalkeGrfs[7].DeltaSetPoint
STRCrpalkeGrfs7EnergijaPoraba | REAL | IOD_STR_TCP | 5691 | 45691 | CrpalkeGrfs[7].EnergijaPoraba
STRCrpalkeGrfs7FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 5693 | 45693 | CrpalkeGrfs[7].FrekPretvornikDCNapetost
STRCrpalkeGrfs7FrekPretvornikDCTok | REAL | IOD_STR_TCP | 5695 | 45695 | CrpalkeGrfs[7].FrekPretvornikDCTok
STRCrpalkeGrfs7FreqMax | REAL | IOD_STR_TCP | 5697 | 45697 | CrpalkeGrfs[7].FreqMax
STRCrpalkeGrfs7FreqMin | REAL | IOD_STR_TCP | 5699 | 45699 | CrpalkeGrfs[7].FreqMin
STRCrpalkeGrfs7FreqUpper | REAL | IOD_STR_TCP | 5701 | 45701 | CrpalkeGrfs[7].FreqUpper
STRCrpalkeGrfs7MocMax | REAL | IOD_STR_TCP | 5703 | 45703 | CrpalkeGrfs[7].MocMax
STRCrpalkeGrfs7MocTrenutna | REAL | IOD_STR_TCP | 5705 | 45705 | CrpalkeGrfs[7].MocTrenutna
STRCrpalkeGrfs7MotorHitrost | REAL | IOD_STR_TCP | 5707 | 45707 | CrpalkeGrfs[7].MotorHitrost
STRCrpalkeGrfs7MotorTok | REAL | IOD_STR_TCP | 5709 | 45709 | CrpalkeGrfs[7].MotorTok
STRCrpalkeGrfs7NapajanjeTok | REAL | IOD_STR_TCP | 5711 | 45711 | CrpalkeGrfs[7].NapajanjeTok
STRCrpalkeGrfs7NastavitevLokalna | REAL | IOD_STR_TCP | 5713 | 45713 | CrpalkeGrfs[7].NastavitevLokalna
STRCrpalkeGrfs7NastavitevTrenutna | REAL | IOD_STR_TCP | 5715 | 45715 | CrpalkeGrfs[7].NastavitevTrenutna
STRCrpalkeGrfs7PretokMax | REAL | IOD_STR_TCP | 5717 | 45717 | CrpalkeGrfs[7].PretokMax
STRCrpalkeGrfs7PretokMin | REAL | IOD_STR_TCP | 5719 | 45719 | CrpalkeGrfs[7].PretokMin
STRCrpalkeGrfs7PretokTrenutni | REAL | IOD_STR_TCP | 5721 | 45721 | CrpalkeGrfs[7].PretokTrenutni
STRCrpalkeGrfs7PritiskMax | REAL | IOD_STR_TCP | 5723 | 45723 | CrpalkeGrfs[7].PritiskMax
STRCrpalkeGrfs7PritiskTrenutni | REAL | IOD_STR_TCP | 5725 | 45725 | CrpalkeGrfs[7].PritiskTrenutni
STRCrpalkeGrfs7ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 5727 | 45727 | CrpalkeGrfs[7].ReferencaMotorjaHzV
STRCrpalkeGrfs7ReferencaRemote | REAL | IOD_STR_TCP | 5729 | 45729 | CrpalkeGrfs[7].ReferencaRemote
STRCrpalkeGrfs7StevecUr2h | REAL | IOD_STR_TCP | 5731 | 45731 | CrpalkeGrfs[7].StevecUr2h
STRCrpalkeGrfs7SystemFeedback | REAL | IOD_STR_TCP | 5733 | 45733 | CrpalkeGrfs[7].SystemFeedback
STRCrpalkeGrfs7SystemReference | REAL | IOD_STR_TCP | 5735 | 45735 | CrpalkeGrfs[7].SystemReference
STRCrpalkeGrfs7TemperaturaMotorja | REAL | IOD_STR_TCP | 5737 | 45737 | CrpalkeGrfs[7].TemperaturaMotorja
STRCrpalkeGrfs7UreXC200 | REAL | IOD_STR_TCP | 5739 | 45739 | CrpalkeGrfs[7].UreXC200
STRCrpalkeGrfs8DeltaSetPoint | REAL | IOD_STR_TCP | 5741 | 45741 | CrpalkeGrfs[8].DeltaSetPoint
STRCrpalkeGrfs8EnergijaPoraba | REAL | IOD_STR_TCP | 5743 | 45743 | CrpalkeGrfs[8].EnergijaPoraba
STRCrpalkeGrfs8FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 5745 | 45745 | CrpalkeGrfs[8].FrekPretvornikDCNapetost
STRCrpalkeGrfs8FrekPretvornikDCTok | REAL | IOD_STR_TCP | 5747 | 45747 | CrpalkeGrfs[8].FrekPretvornikDCTok
STRCrpalkeGrfs8FreqMax | REAL | IOD_STR_TCP | 5749 | 45749 | CrpalkeGrfs[8].FreqMax
STRCrpalkeGrfs8FreqMin | REAL | IOD_STR_TCP | 5751 | 45751 | CrpalkeGrfs[8].FreqMin
STRCrpalkeGrfs8FreqUpper | REAL | IOD_STR_TCP | 5753 | 45753 | CrpalkeGrfs[8].FreqUpper
STRCrpalkeGrfs8MocMax | REAL | IOD_STR_TCP | 5755 | 45755 | CrpalkeGrfs[8].MocMax
STRCrpalkeGrfs8MocTrenutna | REAL | IOD_STR_TCP | 5757 | 45757 | CrpalkeGrfs[8].MocTrenutna
STRCrpalkeGrfs8MotorHitrost | REAL | IOD_STR_TCP | 5759 | 45759 | CrpalkeGrfs[8].MotorHitrost
STRCrpalkeGrfs8MotorTok | REAL | IOD_STR_TCP | 5761 | 45761 | CrpalkeGrfs[8].MotorTok
STRCrpalkeGrfs8NapajanjeTok | REAL | IOD_STR_TCP | 5763 | 45763 | CrpalkeGrfs[8].NapajanjeTok
STRCrpalkeGrfs8NastavitevLokalna | REAL | IOD_STR_TCP | 5765 | 45765 | CrpalkeGrfs[8].NastavitevLokalna
STRCrpalkeGrfs8NastavitevTrenutna | REAL | IOD_STR_TCP | 5767 | 45767 | CrpalkeGrfs[8].NastavitevTrenutna
STRCrpalkeGrfs8PretokMax | REAL | IOD_STR_TCP | 5769 | 45769 | CrpalkeGrfs[8].PretokMax
STRCrpalkeGrfs8PretokMin | REAL | IOD_STR_TCP | 5771 | 45771 | CrpalkeGrfs[8].PretokMin
STRCrpalkeGrfs8PretokTrenutni | REAL | IOD_STR_TCP | 5773 | 45773 | CrpalkeGrfs[8].PretokTrenutni
STRCrpalkeGrfs8PritiskMax | REAL | IOD_STR_TCP | 5775 | 45775 | CrpalkeGrfs[8].PritiskMax
STRCrpalkeGrfs8PritiskTrenutni | REAL | IOD_STR_TCP | 5777 | 45777 | CrpalkeGrfs[8].PritiskTrenutni
STRCrpalkeGrfs8ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 5779 | 45779 | CrpalkeGrfs[8].ReferencaMotorjaHzV
STRCrpalkeGrfs8ReferencaRemote | REAL | IOD_STR_TCP | 5781 | 45781 | CrpalkeGrfs[8].ReferencaRemote
STRCrpalkeGrfs8StevecUr2h | REAL | IOD_STR_TCP | 5783 | 45783 | CrpalkeGrfs[8].StevecUr2h
STRCrpalkeGrfs8SystemFeedback | REAL | IOD_STR_TCP | 5785 | 45785 | CrpalkeGrfs[8].SystemFeedback
STRCrpalkeGrfs8SystemReference | REAL | IOD_STR_TCP | 5787 | 45787 | CrpalkeGrfs[8].SystemReference
STRCrpalkeGrfs8TemperaturaMotorja | REAL | IOD_STR_TCP | 5789 | 45789 | CrpalkeGrfs[8].TemperaturaMotorja
STRCrpalkeGrfs8UreXC200 | REAL | IOD_STR_TCP | 5791 | 45791 | CrpalkeGrfs[8].UreXC200
STRCrpalkeGrfs9DeltaSetPoint | REAL | IOD_STR_TCP | 5793 | 45793 | CrpalkeGrfs[9].DeltaSetPoint
STRCrpalkeGrfs9EnergijaPoraba | REAL | IOD_STR_TCP | 5795 | 45795 | CrpalkeGrfs[9].EnergijaPoraba
STRCrpalkeGrfs9FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 5797 | 45797 | CrpalkeGrfs[9].FrekPretvornikDCNapetost
STRCrpalkeGrfs9FrekPretvornikDCTok | REAL | IOD_STR_TCP | 5799 | 45799 | CrpalkeGrfs[9].FrekPretvornikDCTok
STRCrpalkeGrfs9FreqMax | REAL | IOD_STR_TCP | 5801 | 45801 | CrpalkeGrfs[9].FreqMax
STRCrpalkeGrfs9FreqMin | REAL | IOD_STR_TCP | 5803 | 45803 | CrpalkeGrfs[9].FreqMin
STRCrpalkeGrfs9FreqUpper | REAL | IOD_STR_TCP | 5805 | 45805 | CrpalkeGrfs[9].FreqUpper
STRCrpalkeGrfs9MocMax | REAL | IOD_STR_TCP | 5807 | 45807 | CrpalkeGrfs[9].MocMax
STRCrpalkeGrfs9MocTrenutna | REAL | IOD_STR_TCP | 5809 | 45809 | CrpalkeGrfs[9].MocTrenutna
STRCrpalkeGrfs9MotorHitrost | REAL | IOD_STR_TCP | 5811 | 45811 | CrpalkeGrfs[9].MotorHitrost
STRCrpalkeGrfs9MotorTok | REAL | IOD_STR_TCP | 5813 | 45813 | CrpalkeGrfs[9].MotorTok
STRCrpalkeGrfs9NapajanjeTok | REAL | IOD_STR_TCP | 5815 | 45815 | CrpalkeGrfs[9].NapajanjeTok
STRCrpalkeGrfs9NastavitevLokalna | REAL | IOD_STR_TCP | 5817 | 45817 | CrpalkeGrfs[9].NastavitevLokalna
STRCrpalkeGrfs9NastavitevTrenutna | REAL | IOD_STR_TCP | 5819 | 45819 | CrpalkeGrfs[9].NastavitevTrenutna
STRCrpalkeGrfs9PretokMax | REAL | IOD_STR_TCP | 5821 | 45821 | CrpalkeGrfs[9].PretokMax
STRCrpalkeGrfs9PretokMin | REAL | IOD_STR_TCP | 5823 | 45823 | CrpalkeGrfs[9].PretokMin
STRCrpalkeGrfs9PretokTrenutni | REAL | IOD_STR_TCP | 5825 | 45825 | CrpalkeGrfs[9].PretokTrenutni
STRCrpalkeGrfs9PritiskMax | REAL | IOD_STR_TCP | 5827 | 45827 | CrpalkeGrfs[9].PritiskMax
STRCrpalkeGrfs9PritiskTrenutni | REAL | IOD_STR_TCP | 5829 | 45829 | CrpalkeGrfs[9].PritiskTrenutni
STRCrpalkeGrfs9ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 5831 | 45831 | CrpalkeGrfs[9].ReferencaMotorjaHzV
STRCrpalkeGrfs9ReferencaRemote | REAL | IOD_STR_TCP | 5833 | 45833 | CrpalkeGrfs[9].ReferencaRemote
STRCrpalkeGrfs9StevecUr2h | REAL | IOD_STR_TCP | 5835 | 45835 | CrpalkeGrfs[9].StevecUr2h
STRCrpalkeGrfs9SystemFeedback | REAL | IOD_STR_TCP | 5837 | 45837 | CrpalkeGrfs[9].SystemFeedback
STRCrpalkeGrfs9SystemReference | REAL | IOD_STR_TCP | 5839 | 45839 | CrpalkeGrfs[9].SystemReference
STRCrpalkeGrfs9TemperaturaMotorja | REAL | IOD_STR_TCP | 5841 | 45841 | CrpalkeGrfs[9].TemperaturaMotorja
STRCrpalkeGrfs9UreXC200 | REAL | IOD_STR_TCP | 5843 | 45843 | CrpalkeGrfs[9].UreXC200
STRCrpGrundfosTlakSP1 | REAL | IOD_STR_TCP | 5845 | 45845 | CrpGrundfosTlakSP[1]
STRCrpGrundfosTlakSP2 | REAL | IOD_STR_TCP | 5847 | 45847 | CrpGrundfosTlakSP[2]
STRCrpGrundfosTlakSP3 | REAL | IOD_STR_TCP | 5849 | 45849 | CrpGrundfosTlakSP[3]
STRCrpGrundfosTlakSP4 | REAL | IOD_STR_TCP | 5851 | 45851 | CrpGrundfosTlakSP[4]
STRCrpGrundfosTlakSP5 | REAL | IOD_STR_TCP | 5853 | 45853 | CrpGrundfosTlakSP[5]
STRCrpGrundfosTlakSP6 | REAL | IOD_STR_TCP | 5855 | 45855 | CrpGrundfosTlakSP[6]
STRCrpGrundfosTlakSP7 | REAL | IOD_STR_TCP | 5857 | 45857 | CrpGrundfosTlakSP[7]
STRExp1TlakMin | REAL | IOD_STR_TCP | 5859 | 45859 | Exp1TlakMin
STRExp2TlakMin | REAL | IOD_STR_TCP | 5861 | 45861 | Exp2TlakMin
STRHladStrojObratovalneUre | REAL | IOD_STR_TCP | 5863 | 45863 | HladStroj.ObratovalneUre
STRHladStrojPritiskSonda1 | REAL | IOD_STR_TCP | 5865 | 45865 | HladStroj.PritiskSonda1
STRHladStrojPritiskSonda2 | REAL | IOD_STR_TCP | 5867 | 45867 | HladStroj.PritiskSonda2
STRHladStrojPritiskSonda3 | REAL | IOD_STR_TCP | 5869 | 45869 | HladStroj.PritiskSonda3
STRHladStrojPritiskSonda4 | REAL | IOD_STR_TCP | 5871 | 45871 | HladStroj.PritiskSonda4
STRHladStrojTempH2OvhodIzparilnika | REAL | IOD_STR_TCP | 5873 | 45873 | HladStroj.TempH2OvhodIzparilnika
STRHladStrojTempIzhodnaSonda1 | REAL | IOD_STR_TCP | 5875 | 45875 | HladStroj.TempIzhodnaSonda1
STRHladStrojTempIzhodnaSonda3 | REAL | IOD_STR_TCP | 5877 | 45877 | HladStroj.TempIzhodnaSonda3
STRHladStrojTempSetPoint | REAL | IOD_STR_TCP | 5879 | 45879 | HladStroj.TempSetPoint
STRKlima1HitrostVentilatorjev | REAL | IOD_STR_TCP | 5881 | 45881 | Klima[1].HitrostVentilatorjev
STRKlima1NastTempProstora | REAL | IOD_STR_TCP | 5883 | 45883 | Klima[1].NastTempProstora
STRKlima1ObratovalneUre | REAL | IOD_STR_TCP | 5885 | 45885 | Klima[1].ObratovalneUre
STRKlima1ProtizmrzZasc | REAL | IOD_STR_TCP | 5887 | 45887 | Klima[1].ProtizmrzZasc
STRKlima1RezimDelovanja | REAL | IOD_STR_TCP | 5889 | 45889 | Klima[1].RezimDelovanja
STRKlima1TemperaturaDovoda | REAL | IOD_STR_TCP | 5891 | 45891 | Klima[1].TemperaturaDovoda
STRKlima1TemperaturaProstora | REAL | IOD_STR_TCP | 5893 | 45893 | Klima[1].TemperaturaProstora
STRKlima1TempPredRekN2 | REAL | IOD_STR_TCP | 5895 | 45895 | Klima[1].TempPredRekN2
STRKlima1TempZaRekN2 | REAL | IOD_STR_TCP | 5897 | 45897 | Klima[1].TempZaRekN2
STRKlima1TlakDovKanal | REAL | IOD_STR_TCP | 5899 | 45899 | Klima[1].TlakDovKanal
STRKlima1TlakOdvodKanal | REAL | IOD_STR_TCP | 5901 | 45901 | Klima[1].TlakOdvodKanal
STRKlima1VlagaDovoda | REAL | IOD_STR_TCP | 5903 | 45903 | Klima[1].VlagaDovoda
STRKlima1VlagaVprostor | REAL | IOD_STR_TCP | 5905 | 45905 | Klima[1].VlagaVprostor
STRKlima1ZunanjaTemp | REAL | IOD_STR_TCP | 5907 | 45907 | Klima[1].ZunanjaTemp
STRKlima2HitrostVentilatorjev | REAL | IOD_STR_TCP | 5909 | 45909 | Klima[2].HitrostVentilatorjev
STRKlima2NastTempProstora | REAL | IOD_STR_TCP | 5911 | 45911 | Klima[2].NastTempProstora
STRKlima2ObratovalneUre | REAL | IOD_STR_TCP | 5913 | 45913 | Klima[2].ObratovalneUre
STRKlima2ProtizmrzZasc | REAL | IOD_STR_TCP | 5915 | 45915 | Klima[2].ProtizmrzZasc
STRKlima2RezimDelovanja | REAL | IOD_STR_TCP | 5917 | 45917 | Klima[2].RezimDelovanja
STRKlima2TemperaturaDovoda | REAL | IOD_STR_TCP | 5919 | 45919 | Klima[2].TemperaturaDovoda
STRKlima2TemperaturaProstora | REAL | IOD_STR_TCP | 5921 | 45921 | Klima[2].TemperaturaProstora
STRKlima2TempPredRekN2 | REAL | IOD_STR_TCP | 5923 | 45923 | Klima[2].TempPredRekN2
STRKlima2TempZaRekN2 | REAL | IOD_STR_TCP | 5925 | 45925 | Klima[2].TempZaRekN2
STRKlima2TlakDovKanal | REAL | IOD_STR_TCP | 5927 | 45927 | Klima[2].TlakDovKanal
STRKlima2TlakOdvodKanal | REAL | IOD_STR_TCP | 5929 | 45929 | Klima[2].TlakOdvodKanal
STRKlima2VlagaDovoda | REAL | IOD_STR_TCP | 5931 | 45931 | Klima[2].VlagaDovoda
STRKlima2VlagaVprostor | REAL | IOD_STR_TCP | 5933 | 45933 | Klima[2].VlagaVprostor
STRKlima2ZunanjaTemp | REAL | IOD_STR_TCP | 5935 | 45935 | Klima[2].ZunanjaTemp
STRrVersion | REAL | IOD_STR_TCP | 5937 | 45937 | rVersion
STRSenzorTempTIA1 | REAL | IOD_STR_TCP | 5939 | 45939 | SenzorTempTIA[1]
STRSenzorTempTIA2 | REAL | IOD_STR_TCP | 5941 | 45941 | SenzorTempTIA[2]
STRSenzorTempTIA3 | REAL | IOD_STR_TCP | 5943 | 45943 | SenzorTempTIA[3]
STRSenzorTempTIA4 | REAL | IOD_STR_TCP | 5945 | 45945 | SenzorTempTIA[4]
STRSenzorVlagaHIA1 | REAL | IOD_STR_TCP | 5947 | 45947 | SenzorVlagaHIA[1]
STRSenzorVlagaHIA2 | REAL | IOD_STR_TCP | 5949 | 45949 | SenzorVlagaHIA[2]
STRSenzorVlagaHIA3 | REAL | IOD_STR_TCP | 5951 | 45951 | SenzorVlagaHIA[3]
STRSenzorVlagaHIA4 | REAL | IOD_STR_TCP | 5953 | 45953 | SenzorVlagaHIA[4]
STRTEgrelecTempMAX | REAL | IOD_STR_TCP | 5955 | 45955 | TEgrelecTempMAX
STRTEgrelecTempMIN | REAL | IOD_STR_TCP | 5957 | 45957 | TEgrelecTempMIN
STRTempAlarmPoint | REAL | IOD_STR_TCP | 5959 | 45959 | TempAlarmPoint
STRTempTIApovprecna | REAL | IOD_STR_TCP | 5961 | 45961 | TempTIApovprecna
STRToplPostHKdotokNastTemp | REAL | IOD_STR_TCP | 5963 | 45963 | ToplPost.HKdotokNastTemp
STRToplPostHKdotokTemp | REAL | IOD_STR_TCP | 5965 | 45965 | ToplPost.HKdotokTemp
STRToplPostHKpovtatekTemp | REAL | IOD_STR_TCP | 5967 | 45967 | ToplPost.HKpovtatekTemp
STRToplPostHKpovtratekNastTemp | REAL | IOD_STR_TCP | 5969 | 45969 | ToplPost.HKpovtratekNastTemp
STRToplPostHKzunanjaTemp | REAL | IOD_STR_TCP | 5971 | 45971 | ToplPost.HKzunanjaTemp
STRToplPostTVdotokNastTemp | REAL | IOD_STR_TCP | 5973 | 45973 | ToplPost.TVdotokNastTemp
STRToplPostTVdotokTemp | REAL | IOD_STR_TCP | 5975 | 45975 | ToplPost.TVdotokTemp
STRToplPostTVpovratekTemp | REAL | IOD_STR_TCP | 5977 | 45977 | ToplPost.TVpovratekTemp
STRToplPostTVrezervoarTemp | REAL | IOD_STR_TCP | 5979 | 45979 | ToplPost.TVrezervoarTemp
STRTYventilMax1 | REAL | IOD_STR_TCP | 5981 | 45981 | TYventilMax[1]
STRTYventilMax2 | REAL | IOD_STR_TCP | 5983 | 45983 | TYventilMax[2]
STRTYventilMax3 | REAL | IOD_STR_TCP | 5985 | 45985 | TYventilMax[3]
STRTYventilMax4 | REAL | IOD_STR_TCP | 5987 | 45987 | TYventilMax[4]
STRTYventilMin1 | REAL | IOD_STR_TCP | 5989 | 45989 | TYventilMin[1]
STRTYventilMin2 | REAL | IOD_STR_TCP | 5991 | 45991 | TYventilMin[2]
STRTYventilMin3 | REAL | IOD_STR_TCP | 5993 | 45993 | TYventilMin[3]
STRTYventilMin4 | REAL | IOD_STR_TCP | 5995 | 45995 | TYventilMin[4]
STRTYventilTempRazlika1 | REAL | IOD_STR_TCP | 5997 | 45997 | TYventilTempRazlika[1]
STRTYventilTempRazlika2 | REAL | IOD_STR_TCP | 5999 | 45999 | TYventilTempRazlika[2]
STRTYventilTempRazlika3 | REAL | IOD_STR_TCP | 6001 | 46001 | TYventilTempRazlika[3]
STRTYventilTempRazlika4 | REAL | IOD_STR_TCP | 6003 | 46003 | TYventilTempRazlika[4]
STRValAI_Temp1B1 | REAL | IOD_STR_TCP | 6005 | 46005 | ValAI_Temp1B1
STRValAI_Temp1B2 | REAL | IOD_STR_TCP | 6007 | 46007 | ValAI_Temp1B2
STRValAI_Temp1B3 | REAL | IOD_STR_TCP | 6009 | 46009 | ValAI_Temp1B3
STRValAI_Temp2B2 | REAL | IOD_STR_TCP | 6011 | 46011 | ValAI_Temp2B2
STRValAI_Temp2B3 | REAL | IOD_STR_TCP | 6013 | 46013 | ValAI_Temp2B3
STRValAI_TempHB2 | REAL | IOD_STR_TCP | 6015 | 46015 | ValAI_TempHB2
STRValAI_TempHB4 | REAL | IOD_STR_TCP | 6017 | 46017 | ValAI_TempHB4
STRValAI_TempHB9 | REAL | IOD_STR_TCP | 6019 | 46019 | ValAI_TempHB9
STRValAI_TempTB1 | REAL | IOD_STR_TCP | 6021 | 46021 | ValAI_TempTB1
STRValAI_TempTB10 | REAL | IOD_STR_TCP | 6023 | 46023 | ValAI_TempTB10
STRValAI_TempTB2 | REAL | IOD_STR_TCP | 6025 | 46025 | ValAI_TempTB2
STRValAI_TempTB3 | REAL | IOD_STR_TCP | 6027 | 46027 | ValAI_TempTB3
STRValAI_TempTB4 | REAL | IOD_STR_TCP | 6029 | 46029 | ValAI_TempTB4
STRValAI_TempTB8 | REAL | IOD_STR_TCP | 6031 | 46031 | ValAI_TempTB8
STRValAI_TlakExp1S1 | REAL | IOD_STR_TCP | 6033 | 46033 | ValAI_TlakExp1S1
STRValAI_TlakExp1S2 | REAL | IOD_STR_TCP | 6035 | 46035 | ValAI_TlakExp1S2
STRValAI_TlakExp2S1 | REAL | IOD_STR_TCP | 6037 | 46037 | ValAI_TlakExp2S1
STRValAI_TlakExp2S2 | REAL | IOD_STR_TCP | 6039 | 46039 | ValAI_TlakExp2S2
STRValAI_TlakHB15 | REAL | IOD_STR_TCP | 6041 | 46041 | ValAI_TlakHB15
STRValAI_TlakHB16 | REAL | IOD_STR_TCP | 6043 | 46043 | ValAI_TlakHB16
STRValAI_TlakHB17 | REAL | IOD_STR_TCP | 6045 | 46045 | ValAI_TlakHB17
STRValAI_TlakHB3 | REAL | IOD_STR_TCP | 6047 | 46047 | ValAI_TlakHB3
STRValAI_TlakTB11 | REAL | IOD_STR_TCP | 6049 | 46049 | ValAI_TlakTB11
STRValAI_TlakTB12 | REAL | IOD_STR_TCP | 6051 | 46051 | ValAI_TlakTB12
STRValAI_TlakTB13 | REAL | IOD_STR_TCP | 6053 | 46053 | ValAI_TlakTB13
STRValAI_TlakTB14 | REAL | IOD_STR_TCP | 6055 | 46055 | ValAI_TlakTB14
STRValAI_Vlaga1B4 | REAL | IOD_STR_TCP | 6057 | 46057 | ValAI_Vlaga1B4
STRValAI_Vlaga2B4 | REAL | IOD_STR_TCP | 6059 | 46059 | ValAI_Vlaga2B4
STRValAO_RegVentTY1 | REAL | IOD_STR_TCP | 6061 | 46061 | ValAO_RegVentTY[1]
STRValAO_RegVentTY2 | REAL | IOD_STR_TCP | 6063 | 46063 | ValAO_RegVentTY[2]
STRValAO_RegVentTY3 | REAL | IOD_STR_TCP | 6065 | 46065 | ValAO_RegVentTY[3]
STRValAO_RegVentTY4 | REAL | IOD_STR_TCP | 6067 | 46067 | ValAO_RegVentTY[4]
STRVlagaHIApovprecna | REAL | IOD_STR_TCP | 6069 | 46069 | VlagaHIApovprecna
STRCircutorCosFi_III | REAL | IOD_STR_TCP | 6071 | 46071 | Circutor.CosFi_III
STRCircutorDelovnaEnergija | REAL | IOD_STR_TCP | 6073 | 46073 | Circutor.DelovnaEnergija
STRCircutorDelovnaMoc_III | REAL | IOD_STR_TCP | 6075 | 46075 | Circutor.DelovnaMoc_III
STRCircutorDelovnaMoc_L1 | REAL | IOD_STR_TCP | 6077 | 46077 | Circutor.DelovnaMoc_L1
STRCircutorDelovnaMoc_L2 | REAL | IOD_STR_TCP | 6079 | 46079 | Circutor.DelovnaMoc_L2
STRCircutorDelovnaMoc_L3 | REAL | IOD_STR_TCP | 6081 | 46081 | Circutor.DelovnaMoc_L3
STRCircutorFrekvenca_L1 | REAL | IOD_STR_TCP | 6083 | 46083 | Circutor.Frekvenca_L1
STRCircutorInduktivnaEnergija | REAL | IOD_STR_TCP | 6085 | 46085 | Circutor.InduktivnaEnergija
STRCircutorInduktivnaMoc_III | REAL | IOD_STR_TCP | 6087 | 46087 | Circutor.InduktivnaMoc_III
STRCircutorJalovaMoc_L1 | REAL | IOD_STR_TCP | 6089 | 46089 | Circutor.JalovaMoc_L1
STRCircutorJalovaMoc_L2 | REAL | IOD_STR_TCP | 6091 | 46091 | Circutor.JalovaMoc_L2
STRCircutorJalovaMoc_L3 | REAL | IOD_STR_TCP | 6093 | 46093 | Circutor.JalovaMoc_L3
STRCircutorKapacitivnaEnergija | REAL | IOD_STR_TCP | 6095 | 46095 | Circutor.KapacitivnaEnergija
STRCircutorKapacitivnaMoc_III | REAL | IOD_STR_TCP | 6097 | 46097 | Circutor.KapacitivnaMoc_III
STRCircutorMaximumDemand | REAL | IOD_STR_TCP | 6099 | 46099 | Circutor.MaximumDemand
STRCircutorNapetost_L1_L2 | REAL | IOD_STR_TCP | 6101 | 46101 | Circutor.Napetost_L1_L2
STRCircutorNapetost_L1_N | REAL | IOD_STR_TCP | 6103 | 46103 | Circutor.Napetost_L1_N
STRCircutorNapetost_L2_L3 | REAL | IOD_STR_TCP | 6105 | 46105 | Circutor.Napetost_L2_L3
STRCircutorNapetost_L2_N | REAL | IOD_STR_TCP | 6107 | 46107 | Circutor.Napetost_L2_N
STRCircutorNapetost_L3_L1 | REAL | IOD_STR_TCP | 6109 | 46109 | Circutor.Napetost_L3_L1
STRCircutorNapetost_L3_N | REAL | IOD_STR_TCP | 6111 | 46111 | Circutor.Napetost_L3_N
STRCircutorNavideznaMoc_III | REAL | IOD_STR_TCP | 6113 | 46113 | Circutor.NavideznaMoc_III
STRCircutorNicelniTok | REAL | IOD_STR_TCP | 6115 | 46115 | Circutor.NicelniTok
STRCircutorPowerFactor_III | REAL | IOD_STR_TCP | 6117 | 46117 | Circutor.PowerFactor_III
STRCircutorPowerFactor_L1 | REAL | IOD_STR_TCP | 6119 | 46119 | Circutor.PowerFactor_L1
STRCircutorPowerFactor_L2 | REAL | IOD_STR_TCP | 6121 | 46121 | Circutor.PowerFactor_L2
STRCircutorPowerFactor_L3 | REAL | IOD_STR_TCP | 6123 | 46123 | Circutor.PowerFactor_L3
STRCircutorTHDI_L1 | REAL | IOD_STR_TCP | 6125 | 46125 | Circutor.THDI_L1
STRCircutorTHDI_L2 | REAL | IOD_STR_TCP | 6127 | 46127 | Circutor.THDI_L2
STRCircutorTHDI_L3 | REAL | IOD_STR_TCP | 6129 | 46129 | Circutor.THDI_L3
STRCircutorTHDV_L1 | REAL | IOD_STR_TCP | 6131 | 46131 | Circutor.THDV_L1
STRCircutorTHDV_L2 | REAL | IOD_STR_TCP | 6133 | 46133 | Circutor.THDV_L2
STRCircutorTHDV_L3 | REAL | IOD_STR_TCP | 6135 | 46135 | Circutor.THDV_L3
STRCircutorTok_L1 | REAL | IOD_STR_TCP | 6137 | 46137 | Circutor.Tok_L1
STRCircutorTok_L2 | REAL | IOD_STR_TCP | 6139 | 46139 | Circutor.Tok_L2
STRCircutorTok_L3 | REAL | IOD_STR_TCP | 6141 | 46141 | Circutor.Tok_L3
STRCircutorTokPovprecje_III | REAL | IOD_STR_TCP | 6143 | 46143 | Circutor.TokPovprecje_III
STRCrpalkeGrfsGalEnergijaPoraba | REAL | IOD_STR_TCP | 6145 | 46145 | CrpalkeGrfsGal.EnergijaPoraba
STRCrpalkeGrfsGalFrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 6147 | 46147 | CrpalkeGrfsGal.FrekPretvornikDCNapetost
STRCrpalkeGrfsGalFrekPretvornikDCTok | REAL | IOD_STR_TCP | 6149 | 46149 | CrpalkeGrfsGal.FrekPretvornikDCTok
STRCrpalkeGrfsGalFreqMax | REAL | IOD_STR_TCP | 6151 | 46151 | CrpalkeGrfsGal.FreqMax
STRCrpalkeGrfsGalFreqMin | REAL | IOD_STR_TCP | 6153 | 46153 | CrpalkeGrfsGal.FreqMin
STRCrpalkeGrfsGalFreqUpper | REAL | IOD_STR_TCP | 6155 | 46155 | CrpalkeGrfsGal.FreqUpper
STRCrpalkeGrfsGalMocMax | REAL | IOD_STR_TCP | 6157 | 46157 | CrpalkeGrfsGal.MocMax
STRCrpalkeGrfsGalMocTrenutna | REAL | IOD_STR_TCP | 6159 | 46159 | CrpalkeGrfsGal.MocTrenutna
STRCrpalkeGrfsGalMotorHitrost | REAL | IOD_STR_TCP | 6161 | 46161 | CrpalkeGrfsGal.MotorHitrost
STRCrpalkeGrfsGalMotorTok | REAL | IOD_STR_TCP | 6163 | 46163 | CrpalkeGrfsGal.MotorTok
STRCrpalkeGrfsGalNapajanjeTok | REAL | IOD_STR_TCP | 6165 | 46165 | CrpalkeGrfsGal.NapajanjeTok
STRCrpalkeGrfsGalNastavitevLokalna | REAL | IOD_STR_TCP | 6167 | 46167 | CrpalkeGrfsGal.NastavitevLokalna
STRCrpalkeGrfsGalNastavitevTrenutna | REAL | IOD_STR_TCP | 6169 | 46169 | CrpalkeGrfsGal.NastavitevTrenutna
STRCrpalkeGrfsGalPretokMax | REAL | IOD_STR_TCP | 6171 | 46171 | CrpalkeGrfsGal.PretokMax
STRCrpalkeGrfsGalPretokMin | REAL | IOD_STR_TCP | 6173 | 46173 | CrpalkeGrfsGal.PretokMin
STRCrpalkeGrfsGalPretokTrenutni | REAL | IOD_STR_TCP | 6175 | 46175 | CrpalkeGrfsGal.PretokTrenutni
STRCrpalkeGrfsGalPritiskMax | REAL | IOD_STR_TCP | 6177 | 46177 | CrpalkeGrfsGal.PritiskMax
STRCrpalkeGrfsGalPritiskTrenutni | REAL | IOD_STR_TCP | 6179 | 46179 | CrpalkeGrfsGal.PritiskTrenutni
STRCrpalkeGrfsGalReferencaMotorjaHzV | REAL | IOD_STR_TCP | 6181 | 46181 | CrpalkeGrfsGal.ReferencaMotorjaHzV
STRCrpalkeGrfsGalReferencaRemote | REAL | IOD_STR_TCP | 6183 | 46183 | CrpalkeGrfsGal.ReferencaRemote
STRCrpalkeGrfsGalStevecUr2h | REAL | IOD_STR_TCP | 6185 | 46185 | CrpalkeGrfsGal.StevecUr2h
STRCrpalkeGrfsGalSystemFeedback | REAL | IOD_STR_TCP | 6187 | 46187 | CrpalkeGrfsGal.SystemFeedback
STRCrpalkeGrfsGalSystemReference | REAL | IOD_STR_TCP | 6189 | 46189 | CrpalkeGrfsGal.SystemReference
STRCrpalkeGrfsGalTemperaturaMotorja | REAL | IOD_STR_TCP | 6191 | 46191 | CrpalkeGrfsGal.TemperaturaMotorja
STRCrpalkeGrfsGalUreXC200 | REAL | IOD_STR_TCP | 6193 | 46193 | CrpalkeGrfsGal.UreXC200
STRCrpGrfsPIDregKP | REAL | IOD_STR_TCP | 6195 | 46195 | CrpGrfsPIDregKP
STRValAI_TempTB5 | REAL | IOD_STR_TCP | 6197 | 46197 | ValAI_TempTB5
STRXVH_CrpGrundfosTlakSP | REAL | IOD_STR_TCP | 6199 | 46199 | XVH_CrpGrundfosTlakSP
STRXVH_GrafTemp1 | REAL | IOD_STR_TCP | 6201 | 46201 | XVH_GrafTemp[1]
STRXVH_GrafTemp2 | REAL | IOD_STR_TCP | 6203 | 46203 | XVH_GrafTemp[2]
STRXVH_GrafTemp3 | REAL | IOD_STR_TCP | 6205 | 46205 | XVH_GrafTemp[3]
STRXVH_GrafTemp4 | REAL | IOD_STR_TCP | 6207 | 46207 | XVH_GrafTemp[4]
STRXVH_GrafTemp5 | REAL | IOD_STR_TCP | 6209 | 46209 | XVH_GrafTemp[5]
STRXVH_GrafVlaga1 | REAL | IOD_STR_TCP | 6211 | 46211 | XVH_GrafVlaga[1]
STRXVH_GrafVlaga2 | REAL | IOD_STR_TCP | 6213 | 46213 | XVH_GrafVlaga[2]
STRXVH_GrafVlaga3 | REAL | IOD_STR_TCP | 6215 | 46215 | XVH_GrafVlaga[3]
STRXVH_GrafVlaga4 | REAL | IOD_STR_TCP | 6217 | 46217 | XVH_GrafVlaga[4]
STRXVH_GrafVlaga5 | REAL | IOD_STR_TCP | 6219 | 46219 | XVH_GrafVlaga[5]
STRXVH_TlakSenzor | REAL | IOD_STR_TCP | 6221 | 46221 | XVH_TlakSenzor
STRCirc1MaximumDemandA2 | REAL | IOD_STR_TCP | 6223 | 46223 | Circ[1].MaximumDemandA2
STRCirc1MaximumDemandA3 | REAL | IOD_STR_TCP | 6225 | 46225 | Circ[1].MaximumDemandA3
STRCirc1RazEner_D_SCADA | REAL | IOD_STR_TCP | 6227 | 46227 | Circ[1].RazEner_D_SCADA
STRCirc1RazEner_T_SCADA | REAL | IOD_STR_TCP | 6229 | 46229 | Circ[1].RazEner_T_SCADA
STRCirc1RazEner_M_SCADA | REAL | IOD_STR_TCP | 6231 | 46231 | Circ[1].RazEner_M_SCADA
STRUserCurrentName | STRING | IOD_STR_TCP | 7001 | 47001[15] | UserCurrentName
STRDate_Time0 | STRING | IOD_STR_TCP | 7016 | 47016[15] | Date_Time[0]
STRDate_Time1 | STRING | IOD_STR_TCP | 7031 | 47031[15] | Date_Time[1]
STRDate_Time2 | STRING | IOD_STR_TCP | 7046 | 47046[15] | Date_Time[2]
STRDate_Time3 | STRING | IOD_STR_TCP | 7061 | 47061[15] | Date_Time[3]
STRkom_nast_cas_izpada | UINT | IOD_STR_TCP | 8001 | 48001 | kom_nast_cas_izpada

## variable_new
STRUrnikKopiraj | DIGITAL | IOD_STR_disk | D328
STRToplPostSkupnaNapaka_Omogoci | DIGITAL | IOD_STR_disk | D1
STRKlima1OkvaraVlazilne_Omogoci | DIGITAL | IOD_STR_disk | D3
STRKlima1OkvaraRototerma_Omogoci | DIGITAL | IOD_STR_disk | D4
STRKlima1PozarniAlarm_Omogoci | DIGITAL | IOD_STR_disk | D5
STRKlima1NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_STR_disk | D6
STRKlima1PreobremenitevMotVent_Omogoci | DIGITAL | IOD_STR_disk | D7
STRKlima1PreobremenitevMotCrpGr_Omogoci | DIGITAL | IOD_STR_disk | D8
STRKlima1ProtizmrzAktivna_Omogoci | DIGITAL | IOD_STR_disk | D9
STRKlima1ZamasenFilter_Omogoci | DIGITAL | IOD_STR_disk | D10
STRKlima1SkupniAlarmA_Omogoci | DIGITAL | IOD_STR_disk | D11
STRKlima1SkupniAlarmB_Omogoci | DIGITAL | IOD_STR_disk | D12
STRKlima2OkvaraVlazilne_Omogoci | DIGITAL | IOD_STR_disk | D14
STRKlima2OkvaraRototerma_Omogoci | DIGITAL | IOD_STR_disk | D15
STRKlima2PozarniAlarm_Omogoci | DIGITAL | IOD_STR_disk | D16
STRKlima2NapakaPriPretokuZraka_Omogoci | DIGITAL | IOD_STR_disk | D17
STRKlima2PreobremenitevMotVent_Omogoci | DIGITAL | IOD_STR_disk | D18
STRKlima2PreobremenitevMotCrpGr_Omogoci | DIGITAL | IOD_STR_disk | D19
STRKlima2ProtizmrzAktivna_Omogoci | DIGITAL | IOD_STR_disk | D20
STRKlima2ZamasenFilter_Omogoci | DIGITAL | IOD_STR_disk | D21
STRKlima2SkupniAlarmA_Omogoci | DIGITAL | IOD_STR_disk | D22
STRKlima2SkupniAlarmB_Omogoci | DIGITAL | IOD_STR_disk | D23
ASTR_Omogoci_SMS_Alarm | DIGITAL | IOD_STR_disk2 | D1[299]
BSTR_Omogoci_SMS_Alarm | DIGITAL | IOD_STR_disk2 | D301[299]
CSTR_Omogoci_SMS_Alarm | DIGITAL | IOD_STR_disk2 | D602[299]
DSTR_Omogoci_SMS_Alarm | DIGITAL | IOD_STR_disk2 | D903[299]
ESTR_Omogoci_SMS_Alarm | DIGITAL | IOD_STR_disk2 | D1204[299]
FSTR_Omogoci_SMS_Alarm | DIGITAL | IOD_STR_disk2 | D1505[299]
STROmogociVseSMSAlarme | DIGITAL | IOD_STR_disk | D24
STROmogociVseAlarme | DIGITAL | IOD_STR_disk | D25
STROmogociVseDogodke_DO | DIGITAL | IOD_STR_disk | D295
STROmogociVseDogodke_DI | DIGITAL | IOD_STR_disk | D296
STROmogociVseDogodke_COM | DIGITAL | IOD_STR_disk | D297
STR_meja_tok_opozorilo | LONG | IOD_STR_disk | L1[9]
STR_meja_tok_alarm | LONG | IOD_STR_disk | L10[9]
STR_meja_tok_opozorilo_Omogoci | DIGITAL | IOD_STR_disk | D30[9]
STR_meja_tok_alarm_Omogoci | DIGITAL | IOD_STR_disk | D40[9]
STR_razlika_energ_dan | REAL | IOD_STR_disk | R4000
STR_razlika_energ_ted | REAL | IOD_STR_disk | R4004
STR_razlika_energ_mes | REAL | IOD_STR_disk | R4008
STR_DanEnergCirc | REAL | IOD_STR_disk | R4012[30]
STR_CasDDanEnergCirc | INT | IOD_STR_disk | I0[30]
STR_CasMDanEnergCirc | INT | IOD_STR_disk | I30[30]
STR_TedenEnergCirc | REAL | IOD_STR_disk | R4042[30]
STR_CasDTedenEnergCirc | INT | IOD_STR_disk | I60[30]
STR_CasMTedenEnergCirc | INT | IOD_STR_disk | I90[30]
STR_MesecEnergCirc | REAL | IOD_STR_disk | R4072[30]
STR_CasDMesecEnergCirc | INT | IOD_STR_disk | I120[30]
STR_CasMMesecEnergCirc | INT | IOD_STR_disk | I150[30]
STR_StSt_DanEnergCirc | REAL | IOD_STR_disk | R4102
STR_StSt_TedenEnergCirc | REAL | IOD_STR_disk | R4106
STR_StSt_MesecEnergCirc | REAL | IOD_STR_disk | R4110
STR_StStCasDDanEnergCirc | INT | IOD_STR_disk | I276
STR_StStCasMDanEnergCirc | INT | IOD_STR_disk | I277
STR_StStCasDTedenEnergCirc | INT | IOD_STR_disk | I278
STR_StStCasMTedenEnergCirc | INT | IOD_STR_disk | I279
STR_StStCasDMesecEnergCirc | INT | IOD_STR_disk | I280
STR_StStCasMMesecEnergCirc | INT | IOD_STR_disk | I281
STR_MaxDnevnaEnergija1 | REAL | IOD_STR_disk | R4111 | [5 empty] | #######
STR_MaxMesecnaEnergija1 | REAL | IOD_STR_disk | R4114 | [5 empty] | #######
STR_MaxTedenskaEnergija1 | REAL | IOD_STR_disk | R4118 | [5 empty] | #######
STRComSCADA_stevec1 | INT | IOD_STR_disk | I200
STRComSCADA_stevec2 | INT | IOD_STR_disk | I201
STRPulz1s | DIGITAL | IOD_STR_disk | D62
STRHladStrojPretokAlarm_Omogoci | DIGITAL | IOD_STR_disk | D63
STRHladStrojFazeAlarm_Omogoci | DIGITAL | IOD_STR_disk | D64
STRHladStrojVisokPritiskAlarm_Omogoci | DIGITAL | IOD_STR_disk | D65
STRHladStrojTemperaturaAlarm_Omogoci | DIGITAL | IOD_STR_disk | D66
STRHladStrojUraAlarm_Omogoci | DIGITAL | IOD_STR_disk | D67
STRHladStrojSenzorAlarm_Omogoci | DIGITAL | IOD_STR_disk | D68
STRHladStrojKompresorOljeAlarm_Omogoci | DIGITAL | IOD_STR_disk | D69
STRHladStrojZmrzalniAlarm_Omogoci | DIGITAL | IOD_STR_disk | D70
STRHladStrojZmrzalniAlarmB_Omogoci | DIGITAL | IOD_STR_disk | D71
STRHladStrojVisokPritiskOpozorilo_Omogoci | DIGITAL | IOD_STR_disk | D72
STRHladStrojNizekPritiskAlarm_Omogoci | DIGITAL | IOD_STR_disk | D73
STRHladStrojLANcarelAlarm_Omogoci | DIGITAL | IOD_STR_disk | D74
STRHladStrojObratovalneUreOpozorilo_Omogoci | DIGITAL | IOD_STR_disk | D75
STRNapakaSenzorHIA1_Omogoci | DIGITAL | IOD_STR_disk | D78
STRNapakaSenzorHIA2_Omogoci | DIGITAL | IOD_STR_disk | D79
STRNapakaSenzorHIA3_Omogoci | DIGITAL | IOD_STR_disk | D80
STRNapakaSenzorHIA4_Omogoci | DIGITAL | IOD_STR_disk | D81
STRNapakaSenzorTIA1_Omogoci | DIGITAL | IOD_STR_disk | D82
STRNapakaSenzorTIA2_Omogoci | DIGITAL | IOD_STR_disk | D83
STRNapakaSenzorTIA3_Omogoci | DIGITAL | IOD_STR_disk | D84
STRNapakaSenzorTIA4_Omogoci | DIGITAL | IOD_STR_disk | D85
STRDI_HladStERR_Omogoci | DIGITAL | IOD_STR_disk | D100
STRDI_Lop3Y1Zaprta_Omogoci | DIGITAL | IOD_STR_disk | D101
STRDI_Lop3Y1Odprta_Omogoci | DIGITAL | IOD_STR_disk | D102
STRDI_Lop4Y1Zaprta_Omogoci | DIGITAL | IOD_STR_disk | D103
STRDI_Lop4Y1Odprta_Omogoci | DIGITAL | IOD_STR_disk | D104
STRDI_Lop1PL1Zaprta_Omogoci | DIGITAL | IOD_STR_disk | D105
STRDI_Lop1PL1Odprta_Omogoci | DIGITAL | IOD_STR_disk | D106
STRDI_Lop1PL2Zaprta_Omogoci | DIGITAL | IOD_STR_disk | D107
STRDI_Lop1PL2Odprta_Omogoci | DIGITAL | IOD_STR_disk | D108
STRDI_Lop1PL3Zaprta_Omogoci | DIGITAL | IOD_STR_disk | D109
STRDI_Lop1PL3Odprta_Omogoci | DIGITAL | IOD_STR_disk | D110
STRDI_RazlitjeVodeK1_Omogoci | DIGITAL | IOD_STR_disk | D111
STRDI_RazlitjeVodeK2_Omogoci | DIGITAL | IOD_STR_disk | D112
STRDI_RazlitjeVodeHP_Omogoci | DIGITAL | IOD_STR_disk | D113
STRDI_RazlitjeVodeTP_Omogoci | DIGITAL | IOD_STR_disk | D114
STRDI_RazlitjeVodeEXP1_Omogoci | DIGITAL | IOD_STR_disk | D115
STRDI_RazlitjeVodeEXP2_Omogoci | DIGITAL | IOD_STR_disk | D116
STRDI_ToplPostGenErr_Omogoci | DIGITAL | IOD_STR_disk | D117
STRCrpalkeGrfs1AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D118
STRCrpalkeGrfs2AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D119
STRCrpalkeGrfs3AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D120
STRCrpalkeGrfs4AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D121
STRCrpalkeGrfs5AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D122
STRCrpalkeGrfs6AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D123
STRCrpalkeGrfs7AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D124
STRCrpalkeGrfs8AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D125
STRCrpalkeGrfs9AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D126
STRCrpalkeGrfs10AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D127
STRCrpalkeGrfs11AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D128
STRCrpalkeGrfs12AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D129
STRCrpalkeGrfs13AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D130
STRCrpalkeGrfs14AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D131
STRCrpalkeDnfs1AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D132
STRCrpalkeDnfs2AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D133
STRCrpalkeDnfs3AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D134
STRCrpalkeDnfs4AlarmAktiven_Omogoci | DIGITAL | IOD_STR_disk | D135
STRErrCommScada_Omogoci | DIGITAL | IOD_STR_disk | D136
STRErrComPanelPLC_Omogoci | DIGITAL | IOD_STR_disk | D137
STRErrComPort2_Omogoci | DIGITAL | IOD_STR_disk | D138
STRErrComPort3_Omogoci | DIGITAL | IOD_STR_disk | D139
STRErrComPort4_Omogoci | DIGITAL | IOD_STR_disk | D140
STRErrComCirc1_Omogoci | DIGITAL | IOD_STR_disk | D141
STRErrComKlima1_Omogoci | DIGITAL | IOD_STR_disk | D142
STRErrComKlima2_Omogoci | DIGITAL | IOD_STR_disk | D143
STRErrComDanfossHM1_Omogoci | DIGITAL | IOD_STR_disk | D144
STRErrComDanfossHM2_Omogoci | DIGITAL | IOD_STR_disk | D145
STRErrComDanfossHM3_Omogoci | DIGITAL | IOD_STR_disk | D146
STRErrComDanfossHM4_Omogoci | DIGITAL | IOD_STR_disk | D147
STRErrComHladStroj_Omogoci | DIGITAL | IOD_STR_disk | D148
STRErrComToplPost_Omogoci | DIGITAL | IOD_STR_disk | D149
STRErrCommXC100_Omogoci | DIGITAL | IOD_STR_disk | D150
STRErrComGrundfos0_Omogoci | DIGITAL | IOD_STR_disk | D151
STRErrComGrundfos1_Omogoci | DIGITAL | IOD_STR_disk | D152
STRErrComGrundfos2_Omogoci | DIGITAL | IOD_STR_disk | D153
STRErrComGrundfos3_Omogoci | DIGITAL | IOD_STR_disk | D154
STRErrComGrundfos4_Omogoci | DIGITAL | IOD_STR_disk | D155
STRErrComGrundfos5_Omogoci | DIGITAL | IOD_STR_disk | D156
STRErrComGrundfos6_Omogoci | DIGITAL | IOD_STR_disk | D157
STRErrComGrundfos7_Omogoci | DIGITAL | IOD_STR_disk | D158
STRErrComGrundfos8_Omogoci | DIGITAL | IOD_STR_disk | D159
STRErrComGrundfos9_Omogoci | DIGITAL | IOD_STR_disk | D160
STRErrComGrundfos10_Omogoci | DIGITAL | IOD_STR_disk | D161
STRErrComGrundfos11_Omogoci | DIGITAL | IOD_STR_disk | D162
STRErrComGrundfos12_Omogoci | DIGITAL | IOD_STR_disk | D163
STRErrComGrundfos13_Omogoci | DIGITAL | IOD_STR_disk | D164
STRErrComGrundfos14_Omogoci | DIGITAL | IOD_STR_disk | D165
STRDIN_230VAC_OK_Omogoci | DIGITAL | IOD_STR_disk | D166
STRDIN_24VAC_OK_Omogoci | DIGITAL | IOD_STR_disk | D167
STRDIN_24VDC_OK_Omogoci | DIGITAL | IOD_STR_disk | D168
STRDIN_CrpHM1ERR_Omogoci | DIGITAL | IOD_STR_disk | D169
STRDIN_CrpHM2ERR_Omogoci | DIGITAL | IOD_STR_disk | D170
STRDIN_CrpHM3ERR_Omogoci | DIGITAL | IOD_STR_disk | D171
STRDIN_CrpHM4ERR_Omogoci | DIGITAL | IOD_STR_disk | D172
STRDIN_HladStERR_Omogoci | DIGITAL | IOD_STR_disk | D173
STRDI_HladStFS11_Omogoci | DIGITAL | IOD_STR_disk | D174
STRDIN_Klima1ERR_Omogoci | DIGITAL | IOD_STR_disk | D175
STRDIN_Klima1filterZAM_Omogoci | DIGITAL | IOD_STR_disk | D176
STRDI_Klima1FIRE_Omogoci | DIGITAL | IOD_STR_disk | D177
STRDIN_Klima2ERR_Omogoci | DIGITAL | IOD_STR_disk | D178
STRDIN_Klima2filterZAM_Omogoci | DIGITAL | IOD_STR_disk | D179
STRDI_Klima2FIRE_Omogoci | DIGITAL | IOD_STR_disk | D180
STRDI_Komp1ERR_Omogoci | DIGITAL | IOD_STR_disk | D181
STRDI_Komp2ERR_Omogoci | DIGITAL | IOD_STR_disk | D182
STRDI_Kond1FS1FS2_Omogoci | DIGITAL | IOD_STR_disk | D183
STRDI_Kond2FS1FS2_Omogoci | DIGITAL | IOD_STR_disk | D184
STRDI_Kond3FS1FS2_Omogoci | DIGITAL | IOD_STR_disk | D185
STRDIN_Vlaz1ERR_Omogoci | DIGITAL | IOD_STR_disk | D186
STRDIN_Vlaz2ERR_Omogoci | DIGITAL | IOD_STR_disk | D187
STRDIN_Klima1zascStON_Omogoci | DIGITAL | IOD_STR_disk | D188
STRDIN_Klima2zascStON_Omogoci | DIGITAL | IOD_STR_disk | D189
STRDIN_Kond1zascStON_Omogoci | DIGITAL | IOD_STR_disk | D190
STRDIN_Kond2zascStON_Omogoci | DIGITAL | IOD_STR_disk | D191
STRDIN_Kond3zascStON_Omogoci | DIGITAL | IOD_STR_disk | D192
STRDI_UPS_Alarm_Omogoci | DIGITAL | IOD_STR_disk | D193
STRDI_UPS_BatNacin_Omogoci | DIGITAL | IOD_STR_disk | D194
STRDI_UPS_Polnjenje_Omogoci | DIGITAL | IOD_STR_disk | D195
STRVklopSCFBNapaka1_Omogoci | DIGITAL | IOD_STR_disk | D196
STRVklopSCFBNapaka2_Omogoci | DIGITAL | IOD_STR_disk | D197
STRVklopSCFBNapaka3_Omogoci | DIGITAL | IOD_STR_disk | D198
STRVklopSCFBNapaka4_Omogoci | DIGITAL | IOD_STR_disk | D199
STRVklopSCFBNapaka5_Omogoci | DIGITAL | IOD_STR_disk | D200
STRVklopSCFBNapaka6_Omogoci | DIGITAL | IOD_STR_disk | D201
STRVklopSCFBNapaka7_Omogoci | DIGITAL | IOD_STR_disk | D202
STRVklopSCFBNapaka8_Omogoci | DIGITAL | IOD_STR_disk | D203
STRVklopSCFBNapaka9_Omogoci | DIGITAL | IOD_STR_disk | D204
STRVklopSCFBNapaka10_Omogoci | DIGITAL | IOD_STR_disk | D205
STRVklopSCFBNapaka11_Omogoci | DIGITAL | IOD_STR_disk | D206
STRVklopSCFBNapaka12_Omogoci | DIGITAL | IOD_STR_disk | D207
STRVklopSCFBNapaka13_Omogoci | DIGITAL | IOD_STR_disk | D208
STRVklopSCFBNapaka14_Omogoci | DIGITAL | IOD_STR_disk | D209
STRVklopSCFBNapaka15_Omogoci | DIGITAL | IOD_STR_disk | D210
STRVklopSCFBNapaka16_Omogoci | DIGITAL | IOD_STR_disk | D211
STRVklopSCFBNapaka17_Omogoci | DIGITAL | IOD_STR_disk | D212
STRVklopSCFBNapaka18_Omogoci | DIGITAL | IOD_STR_disk | D213
STRVklopSCFBNapaka19_Omogoci | DIGITAL | IOD_STR_disk | D214
STRVklopSCFBNapaka20_Omogoci | DIGITAL | IOD_STR_disk | D215
STRVklopSCFBNapaka21_Omogoci | DIGITAL | IOD_STR_disk | D216
STRVklopSCFBNapaka22_Omogoci | DIGITAL | IOD_STR_disk | D217
STRVklopSCFBNapaka23_Omogoci | DIGITAL | IOD_STR_disk | D218
STRVklopSCFBNapaka24_Omogoci | DIGITAL | IOD_STR_disk | D219
STRVklopSCFBNapaka25_Omogoci | DIGITAL | IOD_STR_disk | D220
STRSetDateTimeError_Omogoci | DIGITAL | IOD_STR_disk | D221
STRSlabaBaterijaPLC_A1_Omogoci | DIGITAL | IOD_STR_disk | D222
STRSlabaBaterijaPLC_A100_Omogoci | DIGITAL | IOD_STR_disk | D223
STRTempTSprevisoka_Omogoci | DIGITAL | IOD_STR_disk | D224
STRPozarnaLoputaOnOffError1_Omogoci | DIGITAL | IOD_STR_disk | D225
STRPozarnaLoputaOnOffError2_Omogoci | DIGITAL | IOD_STR_disk | D226
STRPozarnaLoputaOnOffError3_Omogoci | DIGITAL | IOD_STR_disk | D227
STRPozarnaLoputaOnOffError4_Omogoci | DIGITAL | IOD_STR_disk | D228
STRPozarnaLoputaOnOffError5_Omogoci | DIGITAL | IOD_STR_disk | D229
STRNapakaSenzorAI1_Omogoci | DIGITAL | IOD_STR_disk | D230
STRNapakaSenzorAI2_Omogoci | DIGITAL | IOD_STR_disk | D231
STRNapakaSenzorAI3_Omogoci | DIGITAL | IOD_STR_disk | D232
STRNapakaSenzorAI4_Omogoci | DIGITAL | IOD_STR_disk | D233
STRNapakaSenzorAI5_Omogoci | DIGITAL | IOD_STR_disk | D234
STRNapakaSenzorAI6_Omogoci | DIGITAL | IOD_STR_disk | D235
STRNapakaSenzorAI7_Omogoci | DIGITAL | IOD_STR_disk | D236
STRNapakaSenzorAI8_Omogoci | DIGITAL | IOD_STR_disk | D237
STRNapakaSenzorAI9_Omogoci | DIGITAL | IOD_STR_disk | D238
STRNapakaSenzorAI10_Omogoci | DIGITAL | IOD_STR_disk | D239
STRNapakaSenzorAI11_Omogoci | DIGITAL | IOD_STR_disk | D240
STRNapakaSenzorAI12_Omogoci | DIGITAL | IOD_STR_disk | D241
STRNapakaSenzorAI13_Omogoci | DIGITAL | IOD_STR_disk | D242
STRNapakaSenzorAI14_Omogoci | DIGITAL | IOD_STR_disk | D243
STRNapakaSenzorAI15_Omogoci | DIGITAL | IOD_STR_disk | D244
STRNapakaSenzorAI16_Omogoci | DIGITAL | IOD_STR_disk | D245
STRNapakaSenzorAI17_Omogoci | DIGITAL | IOD_STR_disk | D246
STRNapakaSenzorAI18_Omogoci | DIGITAL | IOD_STR_disk | D247
STRNapakaSenzorAI19_Omogoci | DIGITAL | IOD_STR_disk | D248
STRNapakaSenzorAI20_Omogoci | DIGITAL | IOD_STR_disk | D249
STRNapakaSenzorAI21_Omogoci | DIGITAL | IOD_STR_disk | D250
STRNapakaSenzorAI22_Omogoci | DIGITAL | IOD_STR_disk | D251
STRNapakaSenzorAI23_Omogoci | DIGITAL | IOD_STR_disk | D252
STRNapakaSenzorAI24_Omogoci | DIGITAL | IOD_STR_disk | D253
STRNapakaSenzorAI25_Omogoci | DIGITAL | IOD_STR_disk | D254
STRNapakaSenzorAI26_Omogoci | DIGITAL | IOD_STR_disk | D255
STRNapakaSenzorAI27_Omogoci | DIGITAL | IOD_STR_disk | D256
STRNapakaSenzorAI28_Omogoci | DIGITAL | IOD_STR_disk | D257
STRNapakaSenzorAI29_Omogoci | DIGITAL | IOD_STR_disk | D258
STRCrpGrundfosGenError1_Omogoci | DIGITAL | IOD_STR_disk | D259
STRCrpGrundfosGenError2_Omogoci | DIGITAL | IOD_STR_disk | D260
STRCrpGrundfosGenError3_Omogoci | DIGITAL | IOD_STR_disk | D261
STRCrpGrundfosGenError4_Omogoci | DIGITAL | IOD_STR_disk | D262
STRCrpGrundfosGenError5_Omogoci | DIGITAL | IOD_STR_disk | D263
STRCrpGrundfosGenError6_Omogoci | DIGITAL | IOD_STR_disk | D264
STRCrpGrundfosGenError7_Omogoci | DIGITAL | IOD_STR_disk | D265
STRCrpGrundfosGenError8_Omogoci | DIGITAL | IOD_STR_disk | D266
STRCrpGrundfosGenError9_Omogoci | DIGITAL | IOD_STR_disk | D267
STRCrpGrundfosGenError10_Omogoci | DIGITAL | IOD_STR_disk | D268
STRCrpGrundfosGenError11_Omogoci | DIGITAL | IOD_STR_disk | D269
STRCrpGrundfosGenError12_Omogoci | DIGITAL | IOD_STR_disk | D270
STRCrpGrundfosGenError13_Omogoci | DIGITAL | IOD_STR_disk | D271
STRCrpGrundfosGenError14_Omogoci | DIGITAL | IOD_STR_disk | D272
STRCrpGrundfosStatusError1_Omogoci | DIGITAL | IOD_STR_disk | D273
STRCrpGrundfosStatusError2_Omogoci | DIGITAL | IOD_STR_disk | D274
STRCrpGrundfosStatusError3_Omogoci | DIGITAL | IOD_STR_disk | D275
STRCrpGrundfosStatusError4_Omogoci | DIGITAL | IOD_STR_disk | D276
STRCrpGrundfosStatusError5_Omogoci | DIGITAL | IOD_STR_disk | D277
STRCrpGrundfosStatusError6_Omogoci | DIGITAL | IOD_STR_disk | D278
STRCrpGrundfosStatusError7_Omogoci | DIGITAL | IOD_STR_disk | D279
STRCrpGrundfosStatusError8_Omogoci | DIGITAL | IOD_STR_disk | D280
STRCrpGrundfosStatusError9_Omogoci | DIGITAL | IOD_STR_disk | D281
STRCrpGrundfosStatusError10_Omogoci | DIGITAL | IOD_STR_disk | D282
STRCrpGrundfosStatusError11_Omogoci | DIGITAL | IOD_STR_disk | D283
STRCrpGrundfosStatusError12_Omogoci | DIGITAL | IOD_STR_disk | D284
STRCrpGrundfosStatusError13_Omogoci | DIGITAL | IOD_STR_disk | D285
STRCrpGrundfosStatusError14_Omogoci | DIGITAL | IOD_STR_disk | D286
STRCrpDanfossGenError1_Omogoci | DIGITAL | IOD_STR_disk | D287
STRCrpDanfossGenError2_Omogoci | DIGITAL | IOD_STR_disk | D288
STRCrpDanfossGenError3_Omogoci | DIGITAL | IOD_STR_disk | D289
STRCrpDanfossGenError4_Omogoci | DIGITAL | IOD_STR_disk | D290
STRCrpDanfossStatusError1_Omogoci | DIGITAL | IOD_STR_disk | D291
STRCrpDanfossStatusError2_Omogoci | DIGITAL | IOD_STR_disk | D292
STRCrpDanfossStatusError3_Omogoci | DIGITAL | IOD_STR_disk | D293
STRCrpDanfossStatusError4_Omogoci | DIGITAL | IOD_STR_disk | D294
STRSkupnaNapakaPLC_GENIbus_črpalke | DIGITAL | IOD_STR_disk | D298
STRSkupnaNapakaPLC_GENIbus_črpalke_Omogoci | DIGITAL | IOD_STR_disk | D299
STRSkupnaNApakaSenzorjevHS | DIGITAL | IOD_STR_disk | D300
STRSkupnaNApakaSenzorjevTP | DIGITAL | IOD_STR_disk | D301
STRSkupnaNApakaSenzorjevHS_Omogoci | DIGITAL | IOD_STR_disk | D302
STRSkupnaNApakaSenzorjevTP_Omogoci | DIGITAL | IOD_STR_disk | D303
STRSkupnaNApakaSenzorjevKN1 | DIGITAL | IOD_STR_disk | D304
STRSkupnaNApakaSenzorjevKN2 | DIGITAL | IOD_STR_disk | D305
STRSkupnaNApakaSenzorjevKN1_Omogoci | DIGITAL | IOD_STR_disk | D306
STRSkupnaNApakaSenzorjevKN2_Omogoci | DIGITAL | IOD_STR_disk | D307
STRDIN_Komp1ON_Omogoci | DIGITAL | IOD_STR_disk | D308
STRDIN_Komp2ON_Omogoci | DIGITAL | IOD_STR_disk | D309
STRCrpalkeGrfs1AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D310
STRCrpalkeGrfs2AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D311
STRCrpalkeGrfs3AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D312
STRCrpalkeGrfs4AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D313
STRCrpalkeGrfs5AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D314
STRCrpalkeGrfs6AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D315
STRCrpalkeGrfs7AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D316
STRCrpalkeGrfs8AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D317
STRCrpalkeGrfs9AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D318
STRCrpalkeGrfs10AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D319
STRCrpalkeGrfs11AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D320
STRCrpalkeGrfs12AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D321
STRCrpalkeGrfs13AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D322
STRCrpalkeGrfs14AlarmGroupXVH10_Omogoci | DIGITAL | IOD_STR_disk | D323
STRSkpnaNapakaKondenzEnoteInVlazilcev | DIGITAL | IOD_STR_disk | D324
STRSkpnaNapakaKondenzEnoteInVlazilcev_Omogoci | DIGITAL | IOD_STR_disk | D325
STRHladStrojNapaka_Omogoci | DIGITAL | IOD_STR_disk | D329
STRExp1TlakAlarm_Omogoci | DIGITAL | IOD_STR_disk | D330
STRExp2TlakAlarm_Omogoci | DIGITAL | IOD_STR_disk | D331
STRATVTempPrenizka_Omogoci | DIGITAL | IOD_STR_disk | D332
STRUrnikiUrejaj | DIGITAL | IOD_STR_disk | D326
STRDI_GlStikaloDieselON_Omogoci | DIGITAL | IOD_STR_disk | D400
STRDIN_GlStikaloDieselON_Omogoci | DIGITAL | IOD_STR_disk | D401
STRDI_GlStikaloMrezaON_Omogoci | DIGITAL | IOD_STR_disk | D402
STRDIN_GlStikaloMrezaON_Omogoci | DIGITAL | IOD_STR_disk | D403
STRDI_GlStikaloUpsON_Omogoci | DIGITAL | IOD_STR_disk | D404
STRDIN_GlStikaloUpsON_Omogoci | DIGITAL | IOD_STR_disk | D405
STRIzbiraUrnikaB | INT | IOD_STR_disk | I500
STRUrnikiDelovniSCDan1On1Ura | INT | IOD_STR_disk | I501
STRUrnikiDelovniSCDan1On1Mna | INT | IOD_STR_disk | I502
STRUrnikiDelovniSCDan1Off1Ura | INT | IOD_STR_disk | I503
STRUrnikiDelovniSCDan1Off1Mna | INT | IOD_STR_disk | I504
STRUrnikiDelovniSCDan1On2Ura | INT | IOD_STR_disk | I505
STRUrnikiDelovniSCDan1On2Mna | INT | IOD_STR_disk | I506
STRUrnikiDelovniSCDan1Off2Ura | INT | IOD_STR_disk | I507
STRUrnikiDelovniSCDan1Off2Mna | INT | IOD_STR_disk | I508
STRUrnikiDelovniSCDan1On3Ura | INT | IOD_STR_disk | I509
STRUrnikiDelovniSCDan1On3Mna | INT | IOD_STR_disk | I510
STRUrnikiDelovniSCDan1Off3Ura | INT | IOD_STR_disk | I511
STRUrnikiDelovniSCDan1Off3Mna | INT | IOD_STR_disk | I512
STRUrnikiDelovniSCDan2On1Ura | INT | IOD_STR_disk | I513
STRUrnikiDelovniSCDan2On1Mna | INT | IOD_STR_disk | I514
STRUrnikiDelovniSCDan2Off1Ura | INT | IOD_STR_disk | I515
STRUrnikiDelovniSCDan2Off1Mna | INT | IOD_STR_disk | I516
STRUrnikiDelovniSCDan2On2Ura | INT | IOD_STR_disk | I517
STRUrnikiDelovniSCDan2On2Mna | INT | IOD_STR_disk | I518
STRUrnikiDelovniSCDan2Off2Ura | INT | IOD_STR_disk | I519
STRUrnikiDelovniSCDan2Off2Mna | INT | IOD_STR_disk | I520
STRUrnikiDelovniSCDan2On3Ura | INT | IOD_STR_disk | I521
STRUrnikiDelovniSCDan2On3Mna | INT | IOD_STR_disk | I522
STRUrnikiDelovniSCDan2Off3Ura | INT | IOD_STR_disk | I523
STRUrnikiDelovniSCDan2Off3Mna | INT | IOD_STR_disk | I524
STRUrnikiDelovniSCDan3On1Ura | INT | IOD_STR_disk | I525
STRUrnikiDelovniSCDan3On1Mna | INT | IOD_STR_disk | I526
STRUrnikiDelovniSCDan3Off1Ura | INT | IOD_STR_disk | I527
STRUrnikiDelovniSCDan3Off1Mna | INT | IOD_STR_disk | I528
STRUrnikiDelovniSCDan3On2Ura | INT | IOD_STR_disk | I529
STRUrnikiDelovniSCDan3On2Mna | INT | IOD_STR_disk | I530
STRUrnikiDelovniSCDan3Off2Ura | INT | IOD_STR_disk | I531
STRUrnikiDelovniSCDan3Off2Mna | INT | IOD_STR_disk | I532
STRUrnikiDelovniSCDan3On3Ura | INT | IOD_STR_disk | I533
STRUrnikiDelovniSCDan3On3Mna | INT | IOD_STR_disk | I534
STRUrnikiDelovniSCDan3Off3Ura | INT | IOD_STR_disk | I535
STRUrnikiDelovniSCDan3Off3Mna | INT | IOD_STR_disk | I536
STRUrnikiDelovniSCDan4On1Ura | INT | IOD_STR_disk | I537
STRUrnikiDelovniSCDan4On1Mna | INT | IOD_STR_disk | I538
STRUrnikiDelovniSCDan4Off1Ura | INT | IOD_STR_disk | I539
STRUrnikiDelovniSCDan4Off1Mna | INT | IOD_STR_disk | I540
STRUrnikiDelovniSCDan4On2Ura | INT | IOD_STR_disk | I541
STRUrnikiDelovniSCDan4On2Mna | INT | IOD_STR_disk | I542
STRUrnikiDelovniSCDan4Off2Ura | INT | IOD_STR_disk | I543
STRUrnikiDelovniSCDan4Off2Mna | INT | IOD_STR_disk | I544
STRUrnikiDelovniSCDan4On3Ura | INT | IOD_STR_disk | I545
STRUrnikiDelovniSCDan4On3Mna | INT | IOD_STR_disk | I546
STRUrnikiDelovniSCDan4Off3Ura | INT | IOD_STR_disk | I547
STRUrnikiDelovniSCDan4Off3Mna | INT | IOD_STR_disk | I548
STRUrnikiDelovniSCDan5On1Ura | INT | IOD_STR_disk | I549
STRUrnikiDelovniSCDan5On1Mna | INT | IOD_STR_disk | I550
STRUrnikiDelovniSCDan5Off1Ura | INT | IOD_STR_disk | I551
STRUrnikiDelovniSCDan5Off1Mna | INT | IOD_STR_disk | I552
STRUrnikiDelovniSCDan5On2Ura | INT | IOD_STR_disk | I553
STRUrnikiDelovniSCDan5On2Mna | INT | IOD_STR_disk | I554
STRUrnikiDelovniSCDan5Off2Ura | INT | IOD_STR_disk | I555
STRUrnikiDelovniSCDan5Off2Mna | INT | IOD_STR_disk | I556
STRUrnikiDelovniSCDan5On3Ura | INT | IOD_STR_disk | I557
STRUrnikiDelovniSCDan5On3Mna | INT | IOD_STR_disk | I558
STRUrnikiDelovniSCDan5Off3Ura | INT | IOD_STR_disk | I559
STRUrnikiDelovniSCDan5Off3Mna | INT | IOD_STR_disk | I560
STRUrnikiDelovniSCDan6On1Ura | INT | IOD_STR_disk | I561
STRUrnikiDelovniSCDan6On1Mna | INT | IOD_STR_disk | I562
STRUrnikiDelovniSCDan6Off1Ura | INT | IOD_STR_disk | I563
STRUrnikiDelovniSCDan6Off1Mna | INT | IOD_STR_disk | I564
STRUrnikiDelovniSCDan6On2Ura | INT | IOD_STR_disk | I565
STRUrnikiDelovniSCDan6On2Mna | INT | IOD_STR_disk | I566
STRUrnikiDelovniSCDan6Off2Ura | INT | IOD_STR_disk | I567
STRUrnikiDelovniSCDan6Off2Mna | INT | IOD_STR_disk | I568
STRUrnikiDelovniSCDan6On3Ura | INT | IOD_STR_disk | I569
STRUrnikiDelovniSCDan6On3Mna | INT | IOD_STR_disk | I570
STRUrnikiDelovniSCDan6Off3Ura | INT | IOD_STR_disk | I571
STRUrnikiDelovniSCDan6Off3Mna | INT | IOD_STR_disk | I572
STRUrnikiDelovniSCDan7On1Ura | INT | IOD_STR_disk | I573
STRUrnikiDelovniSCDan7On1Mna | INT | IOD_STR_disk | I574
STRUrnikiDelovniSCDan7Off1Ura | INT | IOD_STR_disk | I575
STRUrnikiDelovniSCDan7Off1Mna | INT | IOD_STR_disk | I576
STRUrnikiDelovniSCDan7On2Ura | INT | IOD_STR_disk | I577
STRUrnikiDelovniSCDan7On2Mna | INT | IOD_STR_disk | I578
STRUrnikiDelovniSCDan7Off2Ura | INT | IOD_STR_disk | I579
STRUrnikiDelovniSCDan7Off2Mna | INT | IOD_STR_disk | I580
STRUrnikiDelovniSCDan7On3Ura | INT | IOD_STR_disk | I581
STRUrnikiDelovniSCDan7On3Mna | INT | IOD_STR_disk | I582
STRUrnikiDelovniSCDan7Off3Ura | INT | IOD_STR_disk | I583
STRUrnikiDelovniSCDan7Off3Mna | INT | IOD_STR_disk | I584
STRUrnikiSC1Dan1Urn1UraON | INT | IOD_STR_disk | I1000
STRUrnikiSC1Dan1Urn2UraON | INT | IOD_STR_disk | I1001
STRUrnikiSC1Dan1Urn3UraON | INT | IOD_STR_disk | I1002
STRUrnikiSC1Dan1Urn1UraOFF | INT | IOD_STR_disk | I1003
STRUrnikiSC1Dan1Urn2UraOFF | INT | IOD_STR_disk | I1004
STRUrnikiSC1Dan1Urn3UraOFF | INT | IOD_STR_disk | I1005
STRUrnikiSC1Dan1Urn1MinON | INT | IOD_STR_disk | I1006
STRUrnikiSC1Dan1Urn2MinON | INT | IOD_STR_disk | I1007
STRUrnikiSC1Dan1Urn3MinON | INT | IOD_STR_disk | I1008
STRUrnikiSC1Dan1Urn1MinOFF | INT | IOD_STR_disk | I1009
STRUrnikiSC1Dan1Urn2MinOFF | INT | IOD_STR_disk | I1010
STRUrnikiSC1Dan1Urn3MinOFF | INT | IOD_STR_disk | I1011
STRUrnikiSC1Dan2Urn1UraON | INT | IOD_STR_disk | I1012
STRUrnikiSC1Dan2Urn2UraON | INT | IOD_STR_disk | I1013
STRUrnikiSC1Dan2Urn3UraON | INT | IOD_STR_disk | I1014
STRUrnikiSC1Dan2Urn1UraOFF | INT | IOD_STR_disk | I1015
STRUrnikiSC1Dan2Urn2UraOFF | INT | IOD_STR_disk | I1016
STRUrnikiSC1Dan2Urn3UraOFF | INT | IOD_STR_disk | I1017
STRUrnikiSC1Dan2Urn1MinON | INT | IOD_STR_disk | I1018
STRUrnikiSC1Dan2Urn2MinON | INT | IOD_STR_disk | I1019
STRUrnikiSC1Dan2Urn3MinON | INT | IOD_STR_disk | I1020
STRUrnikiSC1Dan2Urn1MinOFF | INT | IOD_STR_disk | I1021
STRUrnikiSC1Dan2Urn2MinOFF | INT | IOD_STR_disk | I1022
STRUrnikiSC1Dan2Urn3MinOFF | INT | IOD_STR_disk | I1023
STRUrnikiSC1Dan3Urn1UraON | INT | IOD_STR_disk | I1024
STRUrnikiSC1Dan3Urn2UraON | INT | IOD_STR_disk | I1025
STRUrnikiSC1Dan3Urn3UraON | INT | IOD_STR_disk | I1026
STRUrnikiSC1Dan3Urn1UraOFF | INT | IOD_STR_disk | I1027
STRUrnikiSC1Dan3Urn2UraOFF | INT | IOD_STR_disk | I1028
STRUrnikiSC1Dan3Urn3UraOFF | INT | IOD_STR_disk | I1029
STRUrnikiSC1Dan3Urn1MinON | INT | IOD_STR_disk | I1030
STRUrnikiSC1Dan3Urn2MinON | INT | IOD_STR_disk | I1031
STRUrnikiSC1Dan3Urn3MinON | INT | IOD_STR_disk | I1032
STRUrnikiSC1Dan3Urn1MinOFF | INT | IOD_STR_disk | I1033
STRUrnikiSC1Dan3Urn2MinOFF | INT | IOD_STR_disk | I1034
STRUrnikiSC1Dan3Urn3MinOFF | INT | IOD_STR_disk | I1035
STRUrnikiSC1Dan4Urn1UraON | INT | IOD_STR_disk | I1036
STRUrnikiSC1Dan4Urn2UraON | INT | IOD_STR_disk | I1037
STRUrnikiSC1Dan4Urn3UraON | INT | IOD_STR_disk | I1038
STRUrnikiSC1Dan4Urn1UraOFF | INT | IOD_STR_disk | I1039
STRUrnikiSC1Dan4Urn2UraOFF | INT | IOD_STR_disk | I1040
STRUrnikiSC1Dan4Urn3UraOFF | INT | IOD_STR_disk | I1041
STRUrnikiSC1Dan4Urn1MinON | INT | IOD_STR_disk | I1042
STRUrnikiSC1Dan4Urn2MinON | INT | IOD_STR_disk | I1043
STRUrnikiSC1Dan4Urn3MinON | INT | IOD_STR_disk | I1044
STRUrnikiSC1Dan4Urn1MinOFF | INT | IOD_STR_disk | I1045
STRUrnikiSC1Dan4Urn2MinOFF | INT | IOD_STR_disk | I1046
STRUrnikiSC1Dan4Urn3MinOFF | INT | IOD_STR_disk | I1047
STRUrnikiSC1Dan5Urn1UraON | INT | IOD_STR_disk | I1048
STRUrnikiSC1Dan5Urn2UraON | INT | IOD_STR_disk | I1049
STRUrnikiSC1Dan5Urn3UraON | INT | IOD_STR_disk | I1050
STRUrnikiSC1Dan5Urn1UraOFF | INT | IOD_STR_disk | I1051
STRUrnikiSC1Dan5Urn2UraOFF | INT | IOD_STR_disk | I1052
STRUrnikiSC1Dan5Urn3UraOFF | INT | IOD_STR_disk | I1053
STRUrnikiSC1Dan5Urn1MinON | INT | IOD_STR_disk | I1054
STRUrnikiSC1Dan5Urn2MinON | INT | IOD_STR_disk | I1055
STRUrnikiSC1Dan5Urn3MinON | INT | IOD_STR_disk | I1056
STRUrnikiSC1Dan5Urn1MinOFF | INT | IOD_STR_disk | I1057
STRUrnikiSC1Dan5Urn2MinOFF | INT | IOD_STR_disk | I1058
STRUrnikiSC1Dan5Urn3MinOFF | INT | IOD_STR_disk | I1059
STRUrnikiSC1Dan6Urn1UraON | INT | IOD_STR_disk | I1060
STRUrnikiSC1Dan6Urn2UraON | INT | IOD_STR_disk | I1061
STRUrnikiSC1Dan6Urn3UraON | INT | IOD_STR_disk | I1062
STRUrnikiSC1Dan6Urn1UraOFF | INT | IOD_STR_disk | I1063
STRUrnikiSC1Dan6Urn2UraOFF | INT | IOD_STR_disk | I1064
STRUrnikiSC1Dan6Urn3UraOFF | INT | IOD_STR_disk | I1065
STRUrnikiSC1Dan6Urn1MinON | INT | IOD_STR_disk | I1066
STRUrnikiSC1Dan6Urn2MinON | INT | IOD_STR_disk | I1067
STRUrnikiSC1Dan6Urn3MinON | INT | IOD_STR_disk | I1068
STRUrnikiSC1Dan6Urn1MinOFF | INT | IOD_STR_disk | I1069
STRUrnikiSC1Dan6Urn2MinOFF | INT | IOD_STR_disk | I1070
STRUrnikiSC1Dan6Urn3MinOFF | INT | IOD_STR_disk | I1071
STRUrnikiSC1Dan7Urn1UraON | INT | IOD_STR_disk | I1072
STRUrnikiSC1Dan7Urn2UraON | INT | IOD_STR_disk | I1073
STRUrnikiSC1Dan7Urn3UraON | INT | IOD_STR_disk | I1074
STRUrnikiSC1Dan7Urn1UraOFF | INT | IOD_STR_disk | I1075
STRUrnikiSC1Dan7Urn2UraOFF | INT | IOD_STR_disk | I1076
STRUrnikiSC1Dan7Urn3UraOFF | INT | IOD_STR_disk | I1077
STRUrnikiSC1Dan7Urn1MinON | INT | IOD_STR_disk | I1078
STRUrnikiSC1Dan7Urn2MinON | INT | IOD_STR_disk | I1079
STRUrnikiSC1Dan7Urn3MinON | INT | IOD_STR_disk | I1080
STRUrnikiSC1Dan7Urn1MinOFF | INT | IOD_STR_disk | I1081
STRUrnikiSC1Dan7Urn2MinOFF | INT | IOD_STR_disk | I1082
STRUrnikiSC1Dan7Urn3MinOFF | INT | IOD_STR_disk | I1083
STRUrnikiSC2Dan1Urn1UraON | INT | IOD_STR_disk | I1084
STRUrnikiSC2Dan1Urn2UraON | INT | IOD_STR_disk | I1085
STRUrnikiSC2Dan1Urn3UraON | INT | IOD_STR_disk | I1086
STRUrnikiSC2Dan1Urn1UraOFF | INT | IOD_STR_disk | I1087
STRUrnikiSC2Dan1Urn2UraOFF | INT | IOD_STR_disk | I1088
STRUrnikiSC2Dan1Urn3UraOFF | INT | IOD_STR_disk | I1089
STRUrnikiSC2Dan1Urn1MinON | INT | IOD_STR_disk | I1090
STRUrnikiSC2Dan1Urn2MinON | INT | IOD_STR_disk | I1091
STRUrnikiSC2Dan1Urn3MinON | INT | IOD_STR_disk | I1092
STRUrnikiSC2Dan1Urn1MinOFF | INT | IOD_STR_disk | I1093
STRUrnikiSC2Dan1Urn2MinOFF | INT | IOD_STR_disk | I1094
STRUrnikiSC2Dan1Urn3MinOFF | INT | IOD_STR_disk | I1095
STRUrnikiSC2Dan2Urn1UraON | INT | IOD_STR_disk | I1096
STRUrnikiSC2Dan2Urn2UraON | INT | IOD_STR_disk | I1097
STRUrnikiSC2Dan2Urn3UraON | INT | IOD_STR_disk | I1098
STRUrnikiSC2Dan2Urn1UraOFF | INT | IOD_STR_disk | I1099
STRUrnikiSC2Dan2Urn2UraOFF | INT | IOD_STR_disk | I1100
STRUrnikiSC2Dan2Urn3UraOFF | INT | IOD_STR_disk | I1101
STRUrnikiSC2Dan2Urn1MinON | INT | IOD_STR_disk | I1102
STRUrnikiSC2Dan2Urn2MinON | INT | IOD_STR_disk | I1103
STRUrnikiSC2Dan2Urn3MinON | INT | IOD_STR_disk | I1104
STRUrnikiSC2Dan2Urn1MinOFF | INT | IOD_STR_disk | I1105
STRUrnikiSC2Dan2Urn2MinOFF | INT | IOD_STR_disk | I1106
STRUrnikiSC2Dan2Urn3MinOFF | INT | IOD_STR_disk | I1107
STRUrnikiSC2Dan3Urn1UraON | INT | IOD_STR_disk | I1108
STRUrnikiSC2Dan3Urn2UraON | INT | IOD_STR_disk | I1109
STRUrnikiSC2Dan3Urn3UraON | INT | IOD_STR_disk | I1110
STRUrnikiSC2Dan3Urn1UraOFF | INT | IOD_STR_disk | I1111
STRUrnikiSC2Dan3Urn2UraOFF | INT | IOD_STR_disk | I1112
STRUrnikiSC2Dan3Urn3UraOFF | INT | IOD_STR_disk | I1113
STRUrnikiSC2Dan3Urn1MinON | INT | IOD_STR_disk | I1114
STRUrnikiSC2Dan3Urn2MinON | INT | IOD_STR_disk | I1115
STRUrnikiSC2Dan3Urn3MinON | INT | IOD_STR_disk | I1116
STRUrnikiSC2Dan3Urn1MinOFF | INT | IOD_STR_disk | I1117
STRUrnikiSC2Dan3Urn2MinOFF | INT | IOD_STR_disk | I1118
STRUrnikiSC2Dan3Urn3MinOFF | INT | IOD_STR_disk | I1119
STRUrnikiSC2Dan4Urn1UraON | INT | IOD_STR_disk | I1120
STRUrnikiSC2Dan4Urn2UraON | INT | IOD_STR_disk | I1121
STRUrnikiSC2Dan4Urn3UraON | INT | IOD_STR_disk | I1122
STRUrnikiSC2Dan4Urn1UraOFF | INT | IOD_STR_disk | I1123
STRUrnikiSC2Dan4Urn2UraOFF | INT | IOD_STR_disk | I1124
STRUrnikiSC2Dan4Urn3UraOFF | INT | IOD_STR_disk | I1125
STRUrnikiSC2Dan4Urn1MinON | INT | IOD_STR_disk | I1126
STRUrnikiSC2Dan4Urn2MinON | INT | IOD_STR_disk | I1127
STRUrnikiSC2Dan4Urn3MinON | INT | IOD_STR_disk | I1128
STRUrnikiSC2Dan4Urn1MinOFF | INT | IOD_STR_disk | I1129
STRUrnikiSC2Dan4Urn2MinOFF | INT | IOD_STR_disk | I1130
STRUrnikiSC2Dan4Urn3MinOFF | INT | IOD_STR_disk | I1131
STRUrnikiSC2Dan5Urn1UraON | INT | IOD_STR_disk | I1132
STRUrnikiSC2Dan5Urn2UraON | INT | IOD_STR_disk | I1133
STRUrnikiSC2Dan5Urn3UraON | INT | IOD_STR_disk | I1134
STRUrnikiSC2Dan5Urn1UraOFF | INT | IOD_STR_disk | I1135
STRUrnikiSC2Dan5Urn2UraOFF | INT | IOD_STR_disk | I1136
STRUrnikiSC2Dan5Urn3UraOFF | INT | IOD_STR_disk | I1137
STRUrnikiSC2Dan5Urn1MinON | INT | IOD_STR_disk | I1138
STRUrnikiSC2Dan5Urn2MinON | INT | IOD_STR_disk | I1139
STRUrnikiSC2Dan5Urn3MinON | INT | IOD_STR_disk | I1140
STRUrnikiSC2Dan5Urn1MinOFF | INT | IOD_STR_disk | I1141
STRUrnikiSC2Dan5Urn2MinOFF | INT | IOD_STR_disk | I1142
STRUrnikiSC2Dan5Urn3MinOFF | INT | IOD_STR_disk | I1143
STRUrnikiSC2Dan6Urn1UraON | INT | IOD_STR_disk | I1144
STRUrnikiSC2Dan6Urn2UraON | INT | IOD_STR_disk | I1145
STRUrnikiSC2Dan6Urn3UraON | INT | IOD_STR_disk | I1146
STRUrnikiSC2Dan6Urn1UraOFF | INT | IOD_STR_disk | I1147
STRUrnikiSC2Dan6Urn2UraOFF | INT | IOD_STR_disk | I1148
STRUrnikiSC2Dan6Urn3UraOFF | INT | IOD_STR_disk | I1149
STRUrnikiSC2Dan6Urn1MinON | INT | IOD_STR_disk | I1150
STRUrnikiSC2Dan6Urn2MinON | INT | IOD_STR_disk | I1151
STRUrnikiSC2Dan6Urn3MinON | INT | IOD_STR_disk | I1152
STRUrnikiSC2Dan6Urn1MinOFF | INT | IOD_STR_disk | I1153
STRUrnikiSC2Dan6Urn2MinOFF | INT | IOD_STR_disk | I1154
STRUrnikiSC2Dan6Urn3MinOFF | INT | IOD_STR_disk | I1155
STRUrnikiSC2Dan7Urn1UraON | INT | IOD_STR_disk | I1156
STRUrnikiSC2Dan7Urn2UraON | INT | IOD_STR_disk | I1157
STRUrnikiSC2Dan7Urn3UraON | INT | IOD_STR_disk | I1158
STRUrnikiSC2Dan7Urn1UraOFF | INT | IOD_STR_disk | I1159
STRUrnikiSC2Dan7Urn2UraOFF | INT | IOD_STR_disk | I1160
STRUrnikiSC2Dan7Urn3UraOFF | INT | IOD_STR_disk | I1161
STRUrnikiSC2Dan7Urn1MinON | INT | IOD_STR_disk | I1162
STRUrnikiSC2Dan7Urn2MinON | INT | IOD_STR_disk | I1163
STRUrnikiSC2Dan7Urn3MinON | INT | IOD_STR_disk | I1164
STRUrnikiSC2Dan7Urn1MinOFF | INT | IOD_STR_disk | I1165
STRUrnikiSC2Dan7Urn2MinOFF | INT | IOD_STR_disk | I1166
STRUrnikiSC2Dan7Urn3MinOFF | INT | IOD_STR_disk | I1167
STRUrnikiSC3Dan1Urn1UraON | INT | IOD_STR_disk | I1168
STRUrnikiSC3Dan1Urn2UraON | INT | IOD_STR_disk | I1169
STRUrnikiSC3Dan1Urn3UraON | INT | IOD_STR_disk | I1170
STRUrnikiSC3Dan1Urn1UraOFF | INT | IOD_STR_disk | I1171
STRUrnikiSC3Dan1Urn2UraOFF | INT | IOD_STR_disk | I1172
STRUrnikiSC3Dan1Urn3UraOFF | INT | IOD_STR_disk | I1173
STRUrnikiSC3Dan1Urn1MinON | INT | IOD_STR_disk | I1174
STRUrnikiSC3Dan1Urn2MinON | INT | IOD_STR_disk | I1175
STRUrnikiSC3Dan1Urn3MinON | INT | IOD_STR_disk | I1176
STRUrnikiSC3Dan1Urn1MinOFF | INT | IOD_STR_disk | I1177
STRUrnikiSC3Dan1Urn2MinOFF | INT | IOD_STR_disk | I1178
STRUrnikiSC3Dan1Urn3MinOFF | INT | IOD_STR_disk | I1179
STRUrnikiSC3Dan2Urn1UraON | INT | IOD_STR_disk | I1180
STRUrnikiSC3Dan2Urn2UraON | INT | IOD_STR_disk | I1181
STRUrnikiSC3Dan2Urn3UraON | INT | IOD_STR_disk | I1182
STRUrnikiSC3Dan2Urn1UraOFF | INT | IOD_STR_disk | I1183
STRUrnikiSC3Dan2Urn2UraOFF | INT | IOD_STR_disk | I1184
STRUrnikiSC3Dan2Urn3UraOFF | INT | IOD_STR_disk | I1185
STRUrnikiSC3Dan2Urn1MinON | INT | IOD_STR_disk | I1186
STRUrnikiSC3Dan2Urn2MinON | INT | IOD_STR_disk | I1187
STRUrnikiSC3Dan2Urn3MinON | INT | IOD_STR_disk | I1188
STRUrnikiSC3Dan2Urn1MinOFF | INT | IOD_STR_disk | I1189
STRUrnikiSC3Dan2Urn2MinOFF | INT | IOD_STR_disk | I1190
STRUrnikiSC3Dan2Urn3MinOFF | INT | IOD_STR_disk | I1191
STRUrnikiSC3Dan3Urn1UraON | INT | IOD_STR_disk | I1192
STRUrnikiSC3Dan3Urn2UraON | INT | IOD_STR_disk | I1193
STRUrnikiSC3Dan3Urn3UraON | INT | IOD_STR_disk | I1194
STRUrnikiSC3Dan3Urn1UraOFF | INT | IOD_STR_disk | I1195
STRUrnikiSC3Dan3Urn2UraOFF | INT | IOD_STR_disk | I1196
STRUrnikiSC3Dan3Urn3UraOFF | INT | IOD_STR_disk | I1197
STRUrnikiSC3Dan3Urn1MinON | INT | IOD_STR_disk | I1198
STRUrnikiSC3Dan3Urn2MinON | INT | IOD_STR_disk | I1199
STRUrnikiSC3Dan3Urn3MinON | INT | IOD_STR_disk | I1200
STRUrnikiSC3Dan3Urn1MinOFF | INT | IOD_STR_disk | I1201
STRUrnikiSC3Dan3Urn2MinOFF | INT | IOD_STR_disk | I1202
STRUrnikiSC3Dan3Urn3MinOFF | INT | IOD_STR_disk | I1203
STRUrnikiSC3Dan4Urn1UraON | INT | IOD_STR_disk | I1204
STRUrnikiSC3Dan4Urn2UraON | INT | IOD_STR_disk | I1205
STRUrnikiSC3Dan4Urn3UraON | INT | IOD_STR_disk | I1206
STRUrnikiSC3Dan4Urn1UraOFF | INT | IOD_STR_disk | I1207
STRUrnikiSC3Dan4Urn2UraOFF | INT | IOD_STR_disk | I1208
STRUrnikiSC3Dan4Urn3UraOFF | INT | IOD_STR_disk | I1209
STRUrnikiSC3Dan4Urn1MinON | INT | IOD_STR_disk | I1210
STRUrnikiSC3Dan4Urn2MinON | INT | IOD_STR_disk | I1211
STRUrnikiSC3Dan4Urn3MinON | INT | IOD_STR_disk | I1212
STRUrnikiSC3Dan4Urn1MinOFF | INT | IOD_STR_disk | I1213
STRUrnikiSC3Dan4Urn2MinOFF | INT | IOD_STR_disk | I1214
STRUrnikiSC3Dan4Urn3MinOFF | INT | IOD_STR_disk | I1215
STRUrnikiSC3Dan5Urn1UraON | INT | IOD_STR_disk | I1216
STRUrnikiSC3Dan5Urn2UraON | INT | IOD_STR_disk | I1217
STRUrnikiSC3Dan5Urn3UraON | INT | IOD_STR_disk | I1218
STRUrnikiSC3Dan5Urn1UraOFF | INT | IOD_STR_disk | I1219
STRUrnikiSC3Dan5Urn2UraOFF | INT | IOD_STR_disk | I1220
STRUrnikiSC3Dan5Urn3UraOFF | INT | IOD_STR_disk | I1221
STRUrnikiSC3Dan5Urn1MinON | INT | IOD_STR_disk | I1222
STRUrnikiSC3Dan5Urn2MinON | INT | IOD_STR_disk | I1223
STRUrnikiSC3Dan5Urn3MinON | INT | IOD_STR_disk | I1224
STRUrnikiSC3Dan5Urn1MinOFF | INT | IOD_STR_disk | I1225
STRUrnikiSC3Dan5Urn2MinOFF | INT | IOD_STR_disk | I1226
STRUrnikiSC3Dan5Urn3MinOFF | INT | IOD_STR_disk | I1227
STRUrnikiSC3Dan6Urn1UraON | INT | IOD_STR_disk | I1228
STRUrnikiSC3Dan6Urn2UraON | INT | IOD_STR_disk | I1229
STRUrnikiSC3Dan6Urn3UraON | INT | IOD_STR_disk | I1230
STRUrnikiSC3Dan6Urn1UraOFF | INT | IOD_STR_disk | I1231
STRUrnikiSC3Dan6Urn2UraOFF | INT | IOD_STR_disk | I1232
STRUrnikiSC3Dan6Urn3UraOFF | INT | IOD_STR_disk | I1233
STRUrnikiSC3Dan6Urn1MinON | INT | IOD_STR_disk | I1234
STRUrnikiSC3Dan6Urn2MinON | INT | IOD_STR_disk | I1235
STRUrnikiSC3Dan6Urn3MinON | INT | IOD_STR_disk | I1236
STRUrnikiSC3Dan6Urn1MinOFF | INT | IOD_STR_disk | I1237
STRUrnikiSC3Dan6Urn2MinOFF | INT | IOD_STR_disk | I1238
STRUrnikiSC3Dan6Urn3MinOFF | INT | IOD_STR_disk | I1239
STRUrnikiSC3Dan7Urn1UraON | INT | IOD_STR_disk | I1240
STRUrnikiSC3Dan7Urn2UraON | INT | IOD_STR_disk | I1241
STRUrnikiSC3Dan7Urn3UraON | INT | IOD_STR_disk | I1242
STRUrnikiSC3Dan7Urn1UraOFF | INT | IOD_STR_disk | I1243
STRUrnikiSC3Dan7Urn2UraOFF | INT | IOD_STR_disk | I1244
STRUrnikiSC3Dan7Urn3UraOFF | INT | IOD_STR_disk | I1245
STRUrnikiSC3Dan7Urn1MinON | INT | IOD_STR_disk | I1246
STRUrnikiSC3Dan7Urn2MinON | INT | IOD_STR_disk | I1247
STRUrnikiSC3Dan7Urn3MinON | INT | IOD_STR_disk | I1248
STRUrnikiSC3Dan7Urn1MinOFF | INT | IOD_STR_disk | I1249
STRUrnikiSC3Dan7Urn2MinOFF | INT | IOD_STR_disk | I1250
STRUrnikiSC3Dan7Urn3MinOFF | INT | IOD_STR_disk | I1251
STRUrnikiSC4Dan1Urn1UraON | INT | IOD_STR_disk | I1252
STRUrnikiSC4Dan1Urn2UraON | INT | IOD_STR_disk | I1253
STRUrnikiSC4Dan1Urn3UraON | INT | IOD_STR_disk | I1254
STRUrnikiSC4Dan1Urn1UraOFF | INT | IOD_STR_disk | I1255
STRUrnikiSC4Dan1Urn2UraOFF | INT | IOD_STR_disk | I1256
STRUrnikiSC4Dan1Urn3UraOFF | INT | IOD_STR_disk | I1257
STRUrnikiSC4Dan1Urn1MinON | INT | IOD_STR_disk | I1258
STRUrnikiSC4Dan1Urn2MinON | INT | IOD_STR_disk | I1259
STRUrnikiSC4Dan1Urn3MinON | INT | IOD_STR_disk | I1260
STRUrnikiSC4Dan1Urn1MinOFF | INT | IOD_STR_disk | I1261
STRUrnikiSC4Dan1Urn2MinOFF | INT | IOD_STR_disk | I1262
STRUrnikiSC4Dan1Urn3MinOFF | INT | IOD_STR_disk | I1263
STRUrnikiSC4Dan2Urn1UraON | INT | IOD_STR_disk | I1264
STRUrnikiSC4Dan2Urn2UraON | INT | IOD_STR_disk | I1265
STRUrnikiSC4Dan2Urn3UraON | INT | IOD_STR_disk | I1266
STRUrnikiSC4Dan2Urn1UraOFF | INT | IOD_STR_disk | I1267
STRUrnikiSC4Dan2Urn2UraOFF | INT | IOD_STR_disk | I1268
STRUrnikiSC4Dan2Urn3UraOFF | INT | IOD_STR_disk | I1269
STRUrnikiSC4Dan2Urn1MinON | INT | IOD_STR_disk | I1270
STRUrnikiSC4Dan2Urn2MinON | INT | IOD_STR_disk | I1271
STRUrnikiSC4Dan2Urn3MinON | INT | IOD_STR_disk | I1272
STRUrnikiSC4Dan2Urn1MinOFF | INT | IOD_STR_disk | I1273
STRUrnikiSC4Dan2Urn2MinOFF | INT | IOD_STR_disk | I1274
STRUrnikiSC4Dan2Urn3MinOFF | INT | IOD_STR_disk | I1275
STRUrnikiSC4Dan3Urn1UraON | INT | IOD_STR_disk | I1276
STRUrnikiSC4Dan3Urn2UraON | INT | IOD_STR_disk | I1277
STRUrnikiSC4Dan3Urn3UraON | INT | IOD_STR_disk | I1278
STRUrnikiSC4Dan3Urn1UraOFF | INT | IOD_STR_disk | I1279
STRUrnikiSC4Dan3Urn2UraOFF | INT | IOD_STR_disk | I1280
STRUrnikiSC4Dan3Urn3UraOFF | INT | IOD_STR_disk | I1281
STRUrnikiSC4Dan3Urn1MinON | INT | IOD_STR_disk | I1282
STRUrnikiSC4Dan3Urn2MinON | INT | IOD_STR_disk | I1283
STRUrnikiSC4Dan3Urn3MinON | INT | IOD_STR_disk | I1284
STRUrnikiSC4Dan3Urn1MinOFF | INT | IOD_STR_disk | I1285
STRUrnikiSC4Dan3Urn2MinOFF | INT | IOD_STR_disk | I1286
STRUrnikiSC4Dan3Urn3MinOFF | INT | IOD_STR_disk | I1287
STRUrnikiSC4Dan4Urn1UraON | INT | IOD_STR_disk | I1288
STRUrnikiSC4Dan4Urn2UraON | INT | IOD_STR_disk | I1289
STRUrnikiSC4Dan4Urn3UraON | INT | IOD_STR_disk | I1290
STRUrnikiSC4Dan4Urn1UraOFF | INT | IOD_STR_disk | I1291
STRUrnikiSC4Dan4Urn2UraOFF | INT | IOD_STR_disk | I1292
STRUrnikiSC4Dan4Urn3UraOFF | INT | IOD_STR_disk | I1293
STRUrnikiSC4Dan4Urn1MinON | INT | IOD_STR_disk | I1294
STRUrnikiSC4Dan4Urn2MinON | INT | IOD_STR_disk | I1295
STRUrnikiSC4Dan4Urn3MinON | INT | IOD_STR_disk | I1296
STRUrnikiSC4Dan4Urn1MinOFF | INT | IOD_STR_disk | I1297
STRUrnikiSC4Dan4Urn2MinOFF | INT | IOD_STR_disk | I1298
STRUrnikiSC4Dan4Urn3MinOFF | INT | IOD_STR_disk | I1299
STRUrnikiSC4Dan5Urn1UraON | INT | IOD_STR_disk | I1300
STRUrnikiSC4Dan5Urn2UraON | INT | IOD_STR_disk | I1301
STRUrnikiSC4Dan5Urn3UraON | INT | IOD_STR_disk | I1302
STRUrnikiSC4Dan5Urn1UraOFF | INT | IOD_STR_disk | I1303
STRUrnikiSC4Dan5Urn2UraOFF | INT | IOD_STR_disk | I1304
STRUrnikiSC4Dan5Urn3UraOFF | INT | IOD_STR_disk | I1305
STRUrnikiSC4Dan5Urn1MinON | INT | IOD_STR_disk | I1306
STRUrnikiSC4Dan5Urn2MinON | INT | IOD_STR_disk | I1307
STRUrnikiSC4Dan5Urn3MinON | INT | IOD_STR_disk | I1308
STRUrnikiSC4Dan5Urn1MinOFF | INT | IOD_STR_disk | I1309
STRUrnikiSC4Dan5Urn2MinOFF | INT | IOD_STR_disk | I1310
STRUrnikiSC4Dan5Urn3MinOFF | INT | IOD_STR_disk | I1311
STRUrnikiSC4Dan6Urn1UraON | INT | IOD_STR_disk | I1312
STRUrnikiSC4Dan6Urn2UraON | INT | IOD_STR_disk | I1313
STRUrnikiSC4Dan6Urn3UraON | INT | IOD_STR_disk | I1314
STRUrnikiSC4Dan6Urn1UraOFF | INT | IOD_STR_disk | I1315
STRUrnikiSC4Dan6Urn2UraOFF | INT | IOD_STR_disk | I1316
STRUrnikiSC4Dan6Urn3UraOFF | INT | IOD_STR_disk | I1317
STRUrnikiSC4Dan6Urn1MinON | INT | IOD_STR_disk | I1318
STRUrnikiSC4Dan6Urn2MinON | INT | IOD_STR_disk | I1319
STRUrnikiSC4Dan6Urn3MinON | INT | IOD_STR_disk | I1320
STRUrnikiSC4Dan6Urn1MinOFF | INT | IOD_STR_disk | I1321
STRUrnikiSC4Dan6Urn2MinOFF | INT | IOD_STR_disk | I1322
STRUrnikiSC4Dan6Urn3MinOFF | INT | IOD_STR_disk | I1323
STRUrnikiSC4Dan7Urn1UraON | INT | IOD_STR_disk | I1324
STRUrnikiSC4Dan7Urn2UraON | INT | IOD_STR_disk | I1325
STRUrnikiSC4Dan7Urn3UraON | INT | IOD_STR_disk | I1326
STRUrnikiSC4Dan7Urn1UraOFF | INT | IOD_STR_disk | I1327
STRUrnikiSC4Dan7Urn2UraOFF | INT | IOD_STR_disk | I1328
STRUrnikiSC4Dan7Urn3UraOFF | INT | IOD_STR_disk | I1329
STRUrnikiSC4Dan7Urn1MinON | INT | IOD_STR_disk | I1330
STRUrnikiSC4Dan7Urn2MinON | INT | IOD_STR_disk | I1331
STRUrnikiSC4Dan7Urn3MinON | INT | IOD_STR_disk | I1332
STRUrnikiSC4Dan7Urn1MinOFF | INT | IOD_STR_disk | I1333
STRUrnikiSC4Dan7Urn2MinOFF | INT | IOD_STR_disk | I1334
STRUrnikiSC4Dan7Urn3MinOFF | INT | IOD_STR_disk | I1335
STRUrnikiSC5Dan1Urn1UraON | INT | IOD_STR_disk | I1336
STRUrnikiSC5Dan1Urn2UraON | INT | IOD_STR_disk | I1337
STRUrnikiSC5Dan1Urn3UraON | INT | IOD_STR_disk | I1338
STRUrnikiSC5Dan1Urn1UraOFF | INT | IOD_STR_disk | I1339
STRUrnikiSC5Dan1Urn2UraOFF | INT | IOD_STR_disk | I1340
STRUrnikiSC5Dan1Urn3UraOFF | INT | IOD_STR_disk | I1341
STRUrnikiSC5Dan1Urn1MinON | INT | IOD_STR_disk | I1342
STRUrnikiSC5Dan1Urn2MinON | INT | IOD_STR_disk | I1343
STRUrnikiSC5Dan1Urn3MinON | INT | IOD_STR_disk | I1344
STRUrnikiSC5Dan1Urn1MinOFF | INT | IOD_STR_disk | I1345
STRUrnikiSC5Dan1Urn2MinOFF | INT | IOD_STR_disk | I1346
STRUrnikiSC5Dan1Urn3MinOFF | INT | IOD_STR_disk | I1347
STRUrnikiSC5Dan2Urn1UraON | INT | IOD_STR_disk | I1348
STRUrnikiSC5Dan2Urn2UraON | INT | IOD_STR_disk | I1349
STRUrnikiSC5Dan2Urn3UraON | INT | IOD_STR_disk | I1350
STRUrnikiSC5Dan2Urn1UraOFF | INT | IOD_STR_disk | I1351
STRUrnikiSC5Dan2Urn2UraOFF | INT | IOD_STR_disk | I1352
STRUrnikiSC5Dan2Urn3UraOFF | INT | IOD_STR_disk | I1353
STRUrnikiSC5Dan2Urn1MinON | INT | IOD_STR_disk | I1354
STRUrnikiSC5Dan2Urn2MinON | INT | IOD_STR_disk | I1355
STRUrnikiSC5Dan2Urn3MinON | INT | IOD_STR_disk | I1356
STRUrnikiSC5Dan2Urn1MinOFF | INT | IOD_STR_disk | I1357
STRUrnikiSC5Dan2Urn2MinOFF | INT | IOD_STR_disk | I1358
STRUrnikiSC5Dan2Urn3MinOFF | INT | IOD_STR_disk | I1359
STRUrnikiSC5Dan3Urn1UraON | INT | IOD_STR_disk | I1360
STRUrnikiSC5Dan3Urn2UraON | INT | IOD_STR_disk | I1361
STRUrnikiSC5Dan3Urn3UraON | INT | IOD_STR_disk | I1362
STRUrnikiSC5Dan3Urn1UraOFF | INT | IOD_STR_disk | I1363
STRUrnikiSC5Dan3Urn2UraOFF | INT | IOD_STR_disk | I1364
STRUrnikiSC5Dan3Urn3UraOFF | INT | IOD_STR_disk | I1365
STRUrnikiSC5Dan3Urn1MinON | INT | IOD_STR_disk | I1366
STRUrnikiSC5Dan3Urn2MinON | INT | IOD_STR_disk | I1367
STRUrnikiSC5Dan3Urn3MinON | INT | IOD_STR_disk | I1368
STRUrnikiSC5Dan3Urn1MinOFF | INT | IOD_STR_disk | I1369
STRUrnikiSC5Dan3Urn2MinOFF | INT | IOD_STR_disk | I1370
STRUrnikiSC5Dan3Urn3MinOFF | INT | IOD_STR_disk | I1371
STRUrnikiSC5Dan4Urn1UraON | INT | IOD_STR_disk | I1372
STRUrnikiSC5Dan4Urn2UraON | INT | IOD_STR_disk | I1373
STRUrnikiSC5Dan4Urn3UraON | INT | IOD_STR_disk | I1374
STRUrnikiSC5Dan4Urn1UraOFF | INT | IOD_STR_disk | I1375
STRUrnikiSC5Dan4Urn2UraOFF | INT | IOD_STR_disk | I1376
STRUrnikiSC5Dan4Urn3UraOFF | INT | IOD_STR_disk | I1377
STRUrnikiSC5Dan4Urn1MinON | INT | IOD_STR_disk | I1378
STRUrnikiSC5Dan4Urn2MinON | INT | IOD_STR_disk | I1379
STRUrnikiSC5Dan4Urn3MinON | INT | IOD_STR_disk | I1380
STRUrnikiSC5Dan4Urn1MinOFF | INT | IOD_STR_disk | I1381
STRUrnikiSC5Dan4Urn2MinOFF | INT | IOD_STR_disk | I1382
STRUrnikiSC5Dan4Urn3MinOFF | INT | IOD_STR_disk | I1383
STRUrnikiSC5Dan5Urn1UraON | INT | IOD_STR_disk | I1384
STRUrnikiSC5Dan5Urn2UraON | INT | IOD_STR_disk | I1385
STRUrnikiSC5Dan5Urn3UraON | INT | IOD_STR_disk | I1386
STRUrnikiSC5Dan5Urn1UraOFF | INT | IOD_STR_disk | I1387
STRUrnikiSC5Dan5Urn2UraOFF | INT | IOD_STR_disk | I1388
STRUrnikiSC5Dan5Urn3UraOFF | INT | IOD_STR_disk | I1389
STRUrnikiSC5Dan5Urn1MinON | INT | IOD_STR_disk | I1390
STRUrnikiSC5Dan5Urn2MinON | INT | IOD_STR_disk | I1391
STRUrnikiSC5Dan5Urn3MinON | INT | IOD_STR_disk | I1392
STRUrnikiSC5Dan5Urn1MinOFF | INT | IOD_STR_disk | I1393
STRUrnikiSC5Dan5Urn2MinOFF | INT | IOD_STR_disk | I1394
STRUrnikiSC5Dan5Urn3MinOFF | INT | IOD_STR_disk | I1395
STRUrnikiSC5Dan6Urn1UraON | INT | IOD_STR_disk | I1396
STRUrnikiSC5Dan6Urn2UraON | INT | IOD_STR_disk | I1397
STRUrnikiSC5Dan6Urn3UraON | INT | IOD_STR_disk | I1398
STRUrnikiSC5Dan6Urn1UraOFF | INT | IOD_STR_disk | I1399
STRUrnikiSC5Dan6Urn2UraOFF | INT | IOD_STR_disk | I1400
STRUrnikiSC5Dan6Urn3UraOFF | INT | IOD_STR_disk | I1401
STRUrnikiSC5Dan6Urn1MinON | INT | IOD_STR_disk | I1402
STRUrnikiSC5Dan6Urn2MinON | INT | IOD_STR_disk | I1403
STRUrnikiSC5Dan6Urn3MinON | INT | IOD_STR_disk | I1404
STRUrnikiSC5Dan6Urn1MinOFF | INT | IOD_STR_disk | I1405
STRUrnikiSC5Dan6Urn2MinOFF | INT | IOD_STR_disk | I1406
STRUrnikiSC5Dan6Urn3MinOFF | INT | IOD_STR_disk | I1407
STRUrnikiSC5Dan7Urn1UraON | INT | IOD_STR_disk | I1408
STRUrnikiSC5Dan7Urn2UraON | INT | IOD_STR_disk | I1409
STRUrnikiSC5Dan7Urn3UraON | INT | IOD_STR_disk | I1410
STRUrnikiSC5Dan7Urn1UraOFF | INT | IOD_STR_disk | I1411
STRUrnikiSC5Dan7Urn2UraOFF | INT | IOD_STR_disk | I1412
STRUrnikiSC5Dan7Urn3UraOFF | INT | IOD_STR_disk | I1413
STRUrnikiSC5Dan7Urn1MinON | INT | IOD_STR_disk | I1414
STRUrnikiSC5Dan7Urn2MinON | INT | IOD_STR_disk | I1415
STRUrnikiSC5Dan7Urn3MinON | INT | IOD_STR_disk | I1416
STRUrnikiSC5Dan7Urn1MinOFF | INT | IOD_STR_disk | I1417
STRUrnikiSC5Dan7Urn2MinOFF | INT | IOD_STR_disk | I1418
STRUrnikiSC5Dan7Urn3MinOFF | INT | IOD_STR_disk | I1419
STRUrnikiSC6Dan1Urn1UraON | INT | IOD_STR_disk | I1420
STRUrnikiSC6Dan1Urn2UraON | INT | IOD_STR_disk | I1421
STRUrnikiSC6Dan1Urn3UraON | INT | IOD_STR_disk | I1422
STRUrnikiSC6Dan1Urn1UraOFF | INT | IOD_STR_disk | I1423
STRUrnikiSC6Dan1Urn2UraOFF | INT | IOD_STR_disk | I1424
STRUrnikiSC6Dan1Urn3UraOFF | INT | IOD_STR_disk | I1425
STRUrnikiSC6Dan1Urn1MinON | INT | IOD_STR_disk | I1426
STRUrnikiSC6Dan1Urn2MinON | INT | IOD_STR_disk | I1427
STRUrnikiSC6Dan1Urn3MinON | INT | IOD_STR_disk | I1428
STRUrnikiSC6Dan1Urn1MinOFF | INT | IOD_STR_disk | I1429
STRUrnikiSC6Dan1Urn2MinOFF | INT | IOD_STR_disk | I1430
STRUrnikiSC6Dan1Urn3MinOFF | INT | IOD_STR_disk | I1431
STRUrnikiSC6Dan2Urn1UraON | INT | IOD_STR_disk | I1432
STRUrnikiSC6Dan2Urn2UraON | INT | IOD_STR_disk | I1433
STRUrnikiSC6Dan2Urn3UraON | INT | IOD_STR_disk | I1434
STRUrnikiSC6Dan2Urn1UraOFF | INT | IOD_STR_disk | I1435
STRUrnikiSC6Dan2Urn2UraOFF | INT | IOD_STR_disk | I1436
STRUrnikiSC6Dan2Urn3UraOFF | INT | IOD_STR_disk | I1437
STRUrnikiSC6Dan2Urn1MinON | INT | IOD_STR_disk | I1438
STRUrnikiSC6Dan2Urn2MinON | INT | IOD_STR_disk | I1439
STRUrnikiSC6Dan2Urn3MinON | INT | IOD_STR_disk | I1440
STRUrnikiSC6Dan2Urn1MinOFF | INT | IOD_STR_disk | I1441
STRUrnikiSC6Dan2Urn2MinOFF | INT | IOD_STR_disk | I1442
STRUrnikiSC6Dan2Urn3MinOFF | INT | IOD_STR_disk | I1443
STRUrnikiSC6Dan3Urn1UraON | INT | IOD_STR_disk | I1444
STRUrnikiSC6Dan3Urn2UraON | INT | IOD_STR_disk | I1445
STRUrnikiSC6Dan3Urn3UraON | INT | IOD_STR_disk | I1446
STRUrnikiSC6Dan3Urn1UraOFF | INT | IOD_STR_disk | I1447
STRUrnikiSC6Dan3Urn2UraOFF | INT | IOD_STR_disk | I1448
STRUrnikiSC6Dan3Urn3UraOFF | INT | IOD_STR_disk | I1449
STRUrnikiSC6Dan3Urn1MinON | INT | IOD_STR_disk | I1450
STRUrnikiSC6Dan3Urn2MinON | INT | IOD_STR_disk | I1451
STRUrnikiSC6Dan3Urn3MinON | INT | IOD_STR_disk | I1452
STRUrnikiSC6Dan3Urn1MinOFF | INT | IOD_STR_disk | I1453
STRUrnikiSC6Dan3Urn2MinOFF | INT | IOD_STR_disk | I1454
STRUrnikiSC6Dan3Urn3MinOFF | INT | IOD_STR_disk | I1455
STRUrnikiSC6Dan4Urn1UraON | INT | IOD_STR_disk | I1456
STRUrnikiSC6Dan4Urn2UraON | INT | IOD_STR_disk | I1457
STRUrnikiSC6Dan4Urn3UraON | INT | IOD_STR_disk | I1458
STRUrnikiSC6Dan4Urn1UraOFF | INT | IOD_STR_disk | I1459
STRUrnikiSC6Dan4Urn2UraOFF | INT | IOD_STR_disk | I1460
STRUrnikiSC6Dan4Urn3UraOFF | INT | IOD_STR_disk | I1461
STRUrnikiSC6Dan4Urn1MinON | INT | IOD_STR_disk | I1462
STRUrnikiSC6Dan4Urn2MinON | INT | IOD_STR_disk | I1463
STRUrnikiSC6Dan4Urn3MinON | INT | IOD_STR_disk | I1464
STRUrnikiSC6Dan4Urn1MinOFF | INT | IOD_STR_disk | I1465
STRUrnikiSC6Dan4Urn2MinOFF | INT | IOD_STR_disk | I1466
STRUrnikiSC6Dan4Urn3MinOFF | INT | IOD_STR_disk | I1467
STRUrnikiSC6Dan5Urn1UraON | INT | IOD_STR_disk | I1468
STRUrnikiSC6Dan5Urn2UraON | INT | IOD_STR_disk | I1469
STRUrnikiSC6Dan5Urn3UraON | INT | IOD_STR_disk | I1470
STRUrnikiSC6Dan5Urn1UraOFF | INT | IOD_STR_disk | I1471
STRUrnikiSC6Dan5Urn2UraOFF | INT | IOD_STR_disk | I1472
STRUrnikiSC6Dan5Urn3UraOFF | INT | IOD_STR_disk | I1473
STRUrnikiSC6Dan5Urn1MinON | INT | IOD_STR_disk | I1474
STRUrnikiSC6Dan5Urn2MinON | INT | IOD_STR_disk | I1475
STRUrnikiSC6Dan5Urn3MinON | INT | IOD_STR_disk | I1476
STRUrnikiSC6Dan5Urn1MinOFF | INT | IOD_STR_disk | I1477
STRUrnikiSC6Dan5Urn2MinOFF | INT | IOD_STR_disk | I1478
STRUrnikiSC6Dan5Urn3MinOFF | INT | IOD_STR_disk | I1479
STRUrnikiSC6Dan6Urn1UraON | INT | IOD_STR_disk | I1480
STRUrnikiSC6Dan6Urn2UraON | INT | IOD_STR_disk | I1481
STRUrnikiSC6Dan6Urn3UraON | INT | IOD_STR_disk | I1482
STRUrnikiSC6Dan6Urn1UraOFF | INT | IOD_STR_disk | I1483
STRUrnikiSC6Dan6Urn2UraOFF | INT | IOD_STR_disk | I1484
STRUrnikiSC6Dan6Urn3UraOFF | INT | IOD_STR_disk | I1485
STRUrnikiSC6Dan6Urn1MinON | INT | IOD_STR_disk | I1486
STRUrnikiSC6Dan6Urn2MinON | INT | IOD_STR_disk | I1487
STRUrnikiSC6Dan6Urn3MinON | INT | IOD_STR_disk | I1488
STRUrnikiSC6Dan6Urn1MinOFF | INT | IOD_STR_disk | I1489
STRUrnikiSC6Dan6Urn2MinOFF | INT | IOD_STR_disk | I1490
STRUrnikiSC6Dan6Urn3MinOFF | INT | IOD_STR_disk | I1491
STRUrnikiSC6Dan7Urn1UraON | INT | IOD_STR_disk | I1492
STRUrnikiSC6Dan7Urn2UraON | INT | IOD_STR_disk | I1493
STRUrnikiSC6Dan7Urn3UraON | INT | IOD_STR_disk | I1494
STRUrnikiSC6Dan7Urn1UraOFF | INT | IOD_STR_disk | I1495
STRUrnikiSC6Dan7Urn2UraOFF | INT | IOD_STR_disk | I1496
STRUrnikiSC6Dan7Urn3UraOFF | INT | IOD_STR_disk | I1497
STRUrnikiSC6Dan7Urn1MinON | INT | IOD_STR_disk | I1498
STRUrnikiSC6Dan7Urn2MinON | INT | IOD_STR_disk | I1499
STRUrnikiSC6Dan7Urn3MinON | INT | IOD_STR_disk | I1500
STRUrnikiSC6Dan7Urn1MinOFF | INT | IOD_STR_disk | I1501
STRUrnikiSC6Dan7Urn2MinOFF | INT | IOD_STR_disk | I1502
STRUrnikiSC6Dan7Urn3MinOFF | INT | IOD_STR_disk | I1503
STRUrnikiSC7Dan1Urn1UraON | INT | IOD_STR_disk | I1504
STRUrnikiSC7Dan1Urn2UraON | INT | IOD_STR_disk | I1505
STRUrnikiSC7Dan1Urn3UraON | INT | IOD_STR_disk | I1506
STRUrnikiSC7Dan1Urn1UraOFF | INT | IOD_STR_disk | I1507
STRUrnikiSC7Dan1Urn2UraOFF | INT | IOD_STR_disk | I1508
STRUrnikiSC7Dan1Urn3UraOFF | INT | IOD_STR_disk | I1509
STRUrnikiSC7Dan1Urn1MinON | INT | IOD_STR_disk | I1510
STRUrnikiSC7Dan1Urn2MinON | INT | IOD_STR_disk | I1511
STRUrnikiSC7Dan1Urn3MinON | INT | IOD_STR_disk | I1512
STRUrnikiSC7Dan1Urn1MinOFF | INT | IOD_STR_disk | I1513
STRUrnikiSC7Dan1Urn2MinOFF | INT | IOD_STR_disk | I1514
STRUrnikiSC7Dan1Urn3MinOFF | INT | IOD_STR_disk | I1515
STRUrnikiSC7Dan2Urn1UraON | INT | IOD_STR_disk | I1516
STRUrnikiSC7Dan2Urn2UraON | INT | IOD_STR_disk | I1517
STRUrnikiSC7Dan2Urn3UraON | INT | IOD_STR_disk | I1518
STRUrnikiSC7Dan2Urn1UraOFF | INT | IOD_STR_disk | I1519
STRUrnikiSC7Dan2Urn2UraOFF | INT | IOD_STR_disk | I1520
STRUrnikiSC7Dan2Urn3UraOFF | INT | IOD_STR_disk | I1521
STRUrnikiSC7Dan2Urn1MinON | INT | IOD_STR_disk | I1522
STRUrnikiSC7Dan2Urn2MinON | INT | IOD_STR_disk | I1523
STRUrnikiSC7Dan2Urn3MinON | INT | IOD_STR_disk | I1524
STRUrnikiSC7Dan2Urn1MinOFF | INT | IOD_STR_disk | I1525
STRUrnikiSC7Dan2Urn2MinOFF | INT | IOD_STR_disk | I1526
STRUrnikiSC7Dan2Urn3MinOFF | INT | IOD_STR_disk | I1527
STRUrnikiSC7Dan3Urn1UraON | INT | IOD_STR_disk | I1528
STRUrnikiSC7Dan3Urn2UraON | INT | IOD_STR_disk | I1529
STRUrnikiSC7Dan3Urn3UraON | INT | IOD_STR_disk | I1530
STRUrnikiSC7Dan3Urn1UraOFF | INT | IOD_STR_disk | I1531
STRUrnikiSC7Dan3Urn2UraOFF | INT | IOD_STR_disk | I1532
STRUrnikiSC7Dan3Urn3UraOFF | INT | IOD_STR_disk | I1533
STRUrnikiSC7Dan3Urn1MinON | INT | IOD_STR_disk | I1534
STRUrnikiSC7Dan3Urn2MinON | INT | IOD_STR_disk | I1535
STRUrnikiSC7Dan3Urn3MinON | INT | IOD_STR_disk | I1536
STRUrnikiSC7Dan3Urn1MinOFF | INT | IOD_STR_disk | I1537
STRUrnikiSC7Dan3Urn2MinOFF | INT | IOD_STR_disk | I1538
STRUrnikiSC7Dan3Urn3MinOFF | INT | IOD_STR_disk | I1539
STRUrnikiSC7Dan4Urn1UraON | INT | IOD_STR_disk | I1540
STRUrnikiSC7Dan4Urn2UraON | INT | IOD_STR_disk | I1541
STRUrnikiSC7Dan4Urn3UraON | INT | IOD_STR_disk | I1542
STRUrnikiSC7Dan4Urn1UraOFF | INT | IOD_STR_disk | I1543
STRUrnikiSC7Dan4Urn2UraOFF | INT | IOD_STR_disk | I1544
STRUrnikiSC7Dan4Urn3UraOFF | INT | IOD_STR_disk | I1545
STRUrnikiSC7Dan4Urn1MinON | INT | IOD_STR_disk | I1546
STRUrnikiSC7Dan4Urn2MinON | INT | IOD_STR_disk | I1547
STRUrnikiSC7Dan4Urn3MinON | INT | IOD_STR_disk | I1548
STRUrnikiSC7Dan4Urn1MinOFF | INT | IOD_STR_disk | I1549
STRUrnikiSC7Dan4Urn2MinOFF | INT | IOD_STR_disk | I1550
STRUrnikiSC7Dan4Urn3MinOFF | INT | IOD_STR_disk | I1551
STRUrnikiSC7Dan5Urn1UraON | INT | IOD_STR_disk | I1552
STRUrnikiSC7Dan5Urn2UraON | INT | IOD_STR_disk | I1553
STRUrnikiSC7Dan5Urn3UraON | INT | IOD_STR_disk | I1554
STRUrnikiSC7Dan5Urn1UraOFF | INT | IOD_STR_disk | I1555
STRUrnikiSC7Dan5Urn2UraOFF | INT | IOD_STR_disk | I1556
STRUrnikiSC7Dan5Urn3UraOFF | INT | IOD_STR_disk | I1557
STRUrnikiSC7Dan5Urn1MinON | INT | IOD_STR_disk | I1558
STRUrnikiSC7Dan5Urn2MinON | INT | IOD_STR_disk | I1559
STRUrnikiSC7Dan5Urn3MinON | INT | IOD_STR_disk | I1560
STRUrnikiSC7Dan5Urn1MinOFF | INT | IOD_STR_disk | I1561
STRUrnikiSC7Dan5Urn2MinOFF | INT | IOD_STR_disk | I1562
STRUrnikiSC7Dan5Urn3MinOFF | INT | IOD_STR_disk | I1563
STRUrnikiSC7Dan6Urn1UraON | INT | IOD_STR_disk | I1564
STRUrnikiSC7Dan6Urn2UraON | INT | IOD_STR_disk | I1565
STRUrnikiSC7Dan6Urn3UraON | INT | IOD_STR_disk | I1566
STRUrnikiSC7Dan6Urn1UraOFF | INT | IOD_STR_disk | I1567
STRUrnikiSC7Dan6Urn2UraOFF | INT | IOD_STR_disk | I1568
STRUrnikiSC7Dan6Urn3UraOFF | INT | IOD_STR_disk | I1569
STRUrnikiSC7Dan6Urn1MinON | INT | IOD_STR_disk | I1570
STRUrnikiSC7Dan6Urn2MinON | INT | IOD_STR_disk | I1571
STRUrnikiSC7Dan6Urn3MinON | INT | IOD_STR_disk | I1572
STRUrnikiSC7Dan6Urn1MinOFF | INT | IOD_STR_disk | I1573
STRUrnikiSC7Dan6Urn2MinOFF | INT | IOD_STR_disk | I1574
STRUrnikiSC7Dan6Urn3MinOFF | INT | IOD_STR_disk | I1575
STRUrnikiSC7Dan7Urn1UraON | INT | IOD_STR_disk | I1576
STRUrnikiSC7Dan7Urn2UraON | INT | IOD_STR_disk | I1577
STRUrnikiSC7Dan7Urn3UraON | INT | IOD_STR_disk | I1578
STRUrnikiSC7Dan7Urn1UraOFF | INT | IOD_STR_disk | I1579
STRUrnikiSC7Dan7Urn2UraOFF | INT | IOD_STR_disk | I1580
STRUrnikiSC7Dan7Urn3UraOFF | INT | IOD_STR_disk | I1581
STRUrnikiSC7Dan7Urn1MinON | INT | IOD_STR_disk | I1582
STRUrnikiSC7Dan7Urn2MinON | INT | IOD_STR_disk | I1583
STRUrnikiSC7Dan7Urn3MinON | INT | IOD_STR_disk | I1584
STRUrnikiSC7Dan7Urn1MinOFF | INT | IOD_STR_disk | I1585
STRUrnikiSC7Dan7Urn2MinOFF | INT | IOD_STR_disk | I1586
STRUrnikiSC7Dan7Urn3MinOFF | INT | IOD_STR_disk | I1587
STRUrnikiSC8Dan1Urn1UraON | INT | IOD_STR_disk | I1588
STRUrnikiSC8Dan1Urn2UraON | INT | IOD_STR_disk | I1589
STRUrnikiSC8Dan1Urn3UraON | INT | IOD_STR_disk | I1590
STRUrnikiSC8Dan1Urn1UraOFF | INT | IOD_STR_disk | I1591
STRUrnikiSC8Dan1Urn2UraOFF | INT | IOD_STR_disk | I1592
STRUrnikiSC8Dan1Urn3UraOFF | INT | IOD_STR_disk | I1593
STRUrnikiSC8Dan1Urn1MinON | INT | IOD_STR_disk | I1594
STRUrnikiSC8Dan1Urn2MinON | INT | IOD_STR_disk | I1595
STRUrnikiSC8Dan1Urn3MinON | INT | IOD_STR_disk | I1596
STRUrnikiSC8Dan1Urn1MinOFF | INT | IOD_STR_disk | I1597
STRUrnikiSC8Dan1Urn2MinOFF | INT | IOD_STR_disk | I1598
STRUrnikiSC8Dan1Urn3MinOFF | INT | IOD_STR_disk | I1599
STRUrnikiSC8Dan2Urn1UraON | INT | IOD_STR_disk | I1600
STRUrnikiSC8Dan2Urn2UraON | INT | IOD_STR_disk | I1601
STRUrnikiSC8Dan2Urn3UraON | INT | IOD_STR_disk | I1602
STRUrnikiSC8Dan2Urn1UraOFF | INT | IOD_STR_disk | I1603
STRUrnikiSC8Dan2Urn2UraOFF | INT | IOD_STR_disk | I1604
STRUrnikiSC8Dan2Urn3UraOFF | INT | IOD_STR_disk | I1605
STRUrnikiSC8Dan2Urn1MinON | INT | IOD_STR_disk | I1606
STRUrnikiSC8Dan2Urn2MinON | INT | IOD_STR_disk | I1607
STRUrnikiSC8Dan2Urn3MinON | INT | IOD_STR_disk | I1608
STRUrnikiSC8Dan2Urn1MinOFF | INT | IOD_STR_disk | I1609
STRUrnikiSC8Dan2Urn2MinOFF | INT | IOD_STR_disk | I1610
STRUrnikiSC8Dan2Urn3MinOFF | INT | IOD_STR_disk | I1611
STRUrnikiSC8Dan3Urn1UraON | INT | IOD_STR_disk | I1612
STRUrnikiSC8Dan3Urn2UraON | INT | IOD_STR_disk | I1613
STRUrnikiSC8Dan3Urn3UraON | INT | IOD_STR_disk | I1614
STRUrnikiSC8Dan3Urn1UraOFF | INT | IOD_STR_disk | I1615
STRUrnikiSC8Dan3Urn2UraOFF | INT | IOD_STR_disk | I1616
STRUrnikiSC8Dan3Urn3UraOFF | INT | IOD_STR_disk | I1617
STRUrnikiSC8Dan3Urn1MinON | INT | IOD_STR_disk | I1618
STRUrnikiSC8Dan3Urn2MinON | INT | IOD_STR_disk | I1619
STRUrnikiSC8Dan3Urn3MinON | INT | IOD_STR_disk | I1620
STRUrnikiSC8Dan3Urn1MinOFF | INT | IOD_STR_disk | I1621
STRUrnikiSC8Dan3Urn2MinOFF | INT | IOD_STR_disk | I1622
STRUrnikiSC8Dan3Urn3MinOFF | INT | IOD_STR_disk | I1623
STRUrnikiSC8Dan4Urn1UraON | INT | IOD_STR_disk | I1624
STRUrnikiSC8Dan4Urn2UraON | INT | IOD_STR_disk | I1625
STRUrnikiSC8Dan4Urn3UraON | INT | IOD_STR_disk | I1626
STRUrnikiSC8Dan4Urn1UraOFF | INT | IOD_STR_disk | I1627
STRUrnikiSC8Dan4Urn2UraOFF | INT | IOD_STR_disk | I1628
STRUrnikiSC8Dan4Urn3UraOFF | INT | IOD_STR_disk | I1629
STRUrnikiSC8Dan4Urn1MinON | INT | IOD_STR_disk | I1630
STRUrnikiSC8Dan4Urn2MinON | INT | IOD_STR_disk | I1631
STRUrnikiSC8Dan4Urn3MinON | INT | IOD_STR_disk | I1632
STRUrnikiSC8Dan4Urn1MinOFF | INT | IOD_STR_disk | I1633
STRUrnikiSC8Dan4Urn2MinOFF | INT | IOD_STR_disk | I1634
STRUrnikiSC8Dan4Urn3MinOFF | INT | IOD_STR_disk | I1635
STRUrnikiSC8Dan5Urn1UraON | INT | IOD_STR_disk | I1636
STRUrnikiSC8Dan5Urn2UraON | INT | IOD_STR_disk | I1637
STRUrnikiSC8Dan5Urn3UraON | INT | IOD_STR_disk | I1638
STRUrnikiSC8Dan5Urn1UraOFF | INT | IOD_STR_disk | I1639
STRUrnikiSC8Dan5Urn2UraOFF | INT | IOD_STR_disk | I1640
STRUrnikiSC8Dan5Urn3UraOFF | INT | IOD_STR_disk | I1641
STRUrnikiSC8Dan5Urn1MinON | INT | IOD_STR_disk | I1642
STRUrnikiSC8Dan5Urn2MinON | INT | IOD_STR_disk | I1643
STRUrnikiSC8Dan5Urn3MinON | INT | IOD_STR_disk | I1644
STRUrnikiSC8Dan5Urn1MinOFF | INT | IOD_STR_disk | I1645
STRUrnikiSC8Dan5Urn2MinOFF | INT | IOD_STR_disk | I1646
STRUrnikiSC8Dan5Urn3MinOFF | INT | IOD_STR_disk | I1647
STRUrnikiSC8Dan6Urn1UraON | INT | IOD_STR_disk | I1648
STRUrnikiSC8Dan6Urn2UraON | INT | IOD_STR_disk | I1649
STRUrnikiSC8Dan6Urn3UraON | INT | IOD_STR_disk | I1650
STRUrnikiSC8Dan6Urn1UraOFF | INT | IOD_STR_disk | I1651
STRUrnikiSC8Dan6Urn2UraOFF | INT | IOD_STR_disk | I1652
STRUrnikiSC8Dan6Urn3UraOFF | INT | IOD_STR_disk | I1653
STRUrnikiSC8Dan6Urn1MinON | INT | IOD_STR_disk | I1654
STRUrnikiSC8Dan6Urn2MinON | INT | IOD_STR_disk | I1655
STRUrnikiSC8Dan6Urn3MinON | INT | IOD_STR_disk | I1656
STRUrnikiSC8Dan6Urn1MinOFF | INT | IOD_STR_disk | I1657
STRUrnikiSC8Dan6Urn2MinOFF | INT | IOD_STR_disk | I1658
STRUrnikiSC8Dan6Urn3MinOFF | INT | IOD_STR_disk | I1659
STRUrnikiSC8Dan7Urn1UraON | INT | IOD_STR_disk | I1660
STRUrnikiSC8Dan7Urn2UraON | INT | IOD_STR_disk | I1661
STRUrnikiSC8Dan7Urn3UraON | INT | IOD_STR_disk | I1662
STRUrnikiSC8Dan7Urn1UraOFF | INT | IOD_STR_disk | I1663
STRUrnikiSC8Dan7Urn2UraOFF | INT | IOD_STR_disk | I1664
STRUrnikiSC8Dan7Urn3UraOFF | INT | IOD_STR_disk | I1665
STRUrnikiSC8Dan7Urn1MinON | INT | IOD_STR_disk | I1666
STRUrnikiSC8Dan7Urn2MinON | INT | IOD_STR_disk | I1667
STRUrnikiSC8Dan7Urn3MinON | INT | IOD_STR_disk | I1668
STRUrnikiSC8Dan7Urn1MinOFF | INT | IOD_STR_disk | I1669
STRUrnikiSC8Dan7Urn2MinOFF | INT | IOD_STR_disk | I1670
STRUrnikiSC8Dan7Urn3MinOFF | INT | IOD_STR_disk | I1671
STRUrnikiSC9Dan1Urn1UraON | INT | IOD_STR_disk | I1672
STRUrnikiSC9Dan1Urn2UraON | INT | IOD_STR_disk | I1673
STRUrnikiSC9Dan1Urn3UraON | INT | IOD_STR_disk | I1674
STRUrnikiSC9Dan1Urn1UraOFF | INT | IOD_STR_disk | I1675
STRUrnikiSC9Dan1Urn2UraOFF | INT | IOD_STR_disk | I1676
STRUrnikiSC9Dan1Urn3UraOFF | INT | IOD_STR_disk | I1677
STRUrnikiSC9Dan1Urn1MinON | INT | IOD_STR_disk | I1678
STRUrnikiSC9Dan1Urn2MinON | INT | IOD_STR_disk | I1679
STRUrnikiSC9Dan1Urn3MinON | INT | IOD_STR_disk | I1680
STRUrnikiSC9Dan1Urn1MinOFF | INT | IOD_STR_disk | I1681
STRUrnikiSC9Dan1Urn2MinOFF | INT | IOD_STR_disk | I1682
STRUrnikiSC9Dan1Urn3MinOFF | INT | IOD_STR_disk | I1683
STRUrnikiSC9Dan2Urn1UraON | INT | IOD_STR_disk | I1684
STRUrnikiSC9Dan2Urn2UraON | INT | IOD_STR_disk | I1685
STRUrnikiSC9Dan2Urn3UraON | INT | IOD_STR_disk | I1686
STRUrnikiSC9Dan2Urn1UraOFF | INT | IOD_STR_disk | I1687
STRUrnikiSC9Dan2Urn2UraOFF | INT | IOD_STR_disk | I1688
STRUrnikiSC9Dan2Urn3UraOFF | INT | IOD_STR_disk | I1689
STRUrnikiSC9Dan2Urn1MinON | INT | IOD_STR_disk | I1690
STRUrnikiSC9Dan2Urn2MinON | INT | IOD_STR_disk | I1691
STRUrnikiSC9Dan2Urn3MinON | INT | IOD_STR_disk | I1692
STRUrnikiSC9Dan2Urn1MinOFF | INT | IOD_STR_disk | I1693
STRUrnikiSC9Dan2Urn2MinOFF | INT | IOD_STR_disk | I1694
STRUrnikiSC9Dan2Urn3MinOFF | INT | IOD_STR_disk | I1695
STRUrnikiSC9Dan3Urn1UraON | INT | IOD_STR_disk | I1696
STRUrnikiSC9Dan3Urn2UraON | INT | IOD_STR_disk | I1697
STRUrnikiSC9Dan3Urn3UraON | INT | IOD_STR_disk | I1698
STRUrnikiSC9Dan3Urn1UraOFF | INT | IOD_STR_disk | I1699
STRUrnikiSC9Dan3Urn2UraOFF | INT | IOD_STR_disk | I1700
STRUrnikiSC9Dan3Urn3UraOFF | INT | IOD_STR_disk | I1701
STRUrnikiSC9Dan3Urn1MinON | INT | IOD_STR_disk | I1702
STRUrnikiSC9Dan3Urn2MinON | INT | IOD_STR_disk | I1703
STRUrnikiSC9Dan3Urn3MinON | INT | IOD_STR_disk | I1704
STRUrnikiSC9Dan3Urn1MinOFF | INT | IOD_STR_disk | I1705
STRUrnikiSC9Dan3Urn2MinOFF | INT | IOD_STR_disk | I1706
STRUrnikiSC9Dan3Urn3MinOFF | INT | IOD_STR_disk | I1707
STRUrnikiSC9Dan4Urn1UraON | INT | IOD_STR_disk | I1708
STRUrnikiSC9Dan4Urn2UraON | INT | IOD_STR_disk | I1709
STRUrnikiSC9Dan4Urn3UraON | INT | IOD_STR_disk | I1710
STRUrnikiSC9Dan4Urn1UraOFF | INT | IOD_STR_disk | I1711
STRUrnikiSC9Dan4Urn2UraOFF | INT | IOD_STR_disk | I1712
STRUrnikiSC9Dan4Urn3UraOFF | INT | IOD_STR_disk | I1713
STRUrnikiSC9Dan4Urn1MinON | INT | IOD_STR_disk | I1714
STRUrnikiSC9Dan4Urn2MinON | INT | IOD_STR_disk | I1715
STRUrnikiSC9Dan4Urn3MinON | INT | IOD_STR_disk | I1716
STRUrnikiSC9Dan4Urn1MinOFF | INT | IOD_STR_disk | I1717
STRUrnikiSC9Dan4Urn2MinOFF | INT | IOD_STR_disk | I1718
STRUrnikiSC9Dan4Urn3MinOFF | INT | IOD_STR_disk | I1719
STRUrnikiSC9Dan5Urn1UraON | INT | IOD_STR_disk | I1720
STRUrnikiSC9Dan5Urn2UraON | INT | IOD_STR_disk | I1721
STRUrnikiSC9Dan5Urn3UraON | INT | IOD_STR_disk | I1722
STRUrnikiSC9Dan5Urn1UraOFF | INT | IOD_STR_disk | I1723
STRUrnikiSC9Dan5Urn2UraOFF | INT | IOD_STR_disk | I1724
STRUrnikiSC9Dan5Urn3UraOFF | INT | IOD_STR_disk | I1725
STRUrnikiSC9Dan5Urn1MinON | INT | IOD_STR_disk | I1726
STRUrnikiSC9Dan5Urn2MinON | INT | IOD_STR_disk | I1727
STRUrnikiSC9Dan5Urn3MinON | INT | IOD_STR_disk | I1728
STRUrnikiSC9Dan5Urn1MinOFF | INT | IOD_STR_disk | I1729
STRUrnikiSC9Dan5Urn2MinOFF | INT | IOD_STR_disk | I1730
STRUrnikiSC9Dan5Urn3MinOFF | INT | IOD_STR_disk | I1731
STRUrnikiSC9Dan6Urn1UraON | INT | IOD_STR_disk | I1732
STRUrnikiSC9Dan6Urn2UraON | INT | IOD_STR_disk | I1733
STRUrnikiSC9Dan6Urn3UraON | INT | IOD_STR_disk | I1734
STRUrnikiSC9Dan6Urn1UraOFF | INT | IOD_STR_disk | I1735
STRUrnikiSC9Dan6Urn2UraOFF | INT | IOD_STR_disk | I1736
STRUrnikiSC9Dan6Urn3UraOFF | INT | IOD_STR_disk | I1737
STRUrnikiSC9Dan6Urn1MinON | INT | IOD_STR_disk | I1738
STRUrnikiSC9Dan6Urn2MinON | INT | IOD_STR_disk | I1739
STRUrnikiSC9Dan6Urn3MinON | INT | IOD_STR_disk | I1740
STRUrnikiSC9Dan6Urn1MinOFF | INT | IOD_STR_disk | I1741
STRUrnikiSC9Dan6Urn2MinOFF | INT | IOD_STR_disk | I1742
STRUrnikiSC9Dan6Urn3MinOFF | INT | IOD_STR_disk | I1743
STRUrnikiSC9Dan7Urn1UraON | INT | IOD_STR_disk | I1744
STRUrnikiSC9Dan7Urn2UraON | INT | IOD_STR_disk | I1745
STRUrnikiSC9Dan7Urn3UraON | INT | IOD_STR_disk | I1746
STRUrnikiSC9Dan7Urn1UraOFF | INT | IOD_STR_disk | I1747
STRUrnikiSC9Dan7Urn2UraOFF | INT | IOD_STR_disk | I1748
STRUrnikiSC9Dan7Urn3UraOFF | INT | IOD_STR_disk | I1749
STRUrnikiSC9Dan7Urn1MinON | INT | IOD_STR_disk | I1750
STRUrnikiSC9Dan7Urn2MinON | INT | IOD_STR_disk | I1751
STRUrnikiSC9Dan7Urn3MinON | INT | IOD_STR_disk | I1752
STRUrnikiSC9Dan7Urn1MinOFF | INT | IOD_STR_disk | I1753
STRUrnikiSC9Dan7Urn2MinOFF | INT | IOD_STR_disk | I1754
STRUrnikiSC9Dan7Urn3MinOFF | INT | IOD_STR_disk | I1755
STRUrnikiSC10Dan1Urn1UraON | INT | IOD_STR_disk | I1756
STRUrnikiSC10Dan1Urn2UraON | INT | IOD_STR_disk | I1757
STRUrnikiSC10Dan1Urn3UraON | INT | IOD_STR_disk | I1758
STRUrnikiSC10Dan1Urn1UraOFF | INT | IOD_STR_disk | I1759
STRUrnikiSC10Dan1Urn2UraOFF | INT | IOD_STR_disk | I1760
STRUrnikiSC10Dan1Urn3UraOFF | INT | IOD_STR_disk | I1761
STRUrnikiSC10Dan1Urn1MinON | INT | IOD_STR_disk | I1762
STRUrnikiSC10Dan1Urn2MinON | INT | IOD_STR_disk | I1763
STRUrnikiSC10Dan1Urn3MinON | INT | IOD_STR_disk | I1764
STRUrnikiSC10Dan1Urn1MinOFF | INT | IOD_STR_disk | I1765
STRUrnikiSC10Dan1Urn2MinOFF | INT | IOD_STR_disk | I1766
STRUrnikiSC10Dan1Urn3MinOFF | INT | IOD_STR_disk | I1767
STRUrnikiSC10Dan2Urn1UraON | INT | IOD_STR_disk | I1768
STRUrnikiSC10Dan2Urn2UraON | INT | IOD_STR_disk | I1769
STRUrnikiSC10Dan2Urn3UraON | INT | IOD_STR_disk | I1770
STRUrnikiSC10Dan2Urn1UraOFF | INT | IOD_STR_disk | I1771
STRUrnikiSC10Dan2Urn2UraOFF | INT | IOD_STR_disk | I1772
STRUrnikiSC10Dan2Urn3UraOFF | INT | IOD_STR_disk | I1773
STRUrnikiSC10Dan2Urn1MinON | INT | IOD_STR_disk | I1774
STRUrnikiSC10Dan2Urn2MinON | INT | IOD_STR_disk | I1775
STRUrnikiSC10Dan2Urn3MinON | INT | IOD_STR_disk | I1776
STRUrnikiSC10Dan2Urn1MinOFF | INT | IOD_STR_disk | I1777
STRUrnikiSC10Dan2Urn2MinOFF | INT | IOD_STR_disk | I1778
STRUrnikiSC10Dan2Urn3MinOFF | INT | IOD_STR_disk | I1779
STRUrnikiSC10Dan3Urn1UraON | INT | IOD_STR_disk | I1780
STRUrnikiSC10Dan3Urn2UraON | INT | IOD_STR_disk | I1781
STRUrnikiSC10Dan3Urn3UraON | INT | IOD_STR_disk | I1782
STRUrnikiSC10Dan3Urn1UraOFF | INT | IOD_STR_disk | I1783
STRUrnikiSC10Dan3Urn2UraOFF | INT | IOD_STR_disk | I1784
STRUrnikiSC10Dan3Urn3UraOFF | INT | IOD_STR_disk | I1785
STRUrnikiSC10Dan3Urn1MinON | INT | IOD_STR_disk | I1786
STRUrnikiSC10Dan3Urn2MinON | INT | IOD_STR_disk | I1787
STRUrnikiSC10Dan3Urn3MinON | INT | IOD_STR_disk | I1788
STRUrnikiSC10Dan3Urn1MinOFF | INT | IOD_STR_disk | I1789
STRUrnikiSC10Dan3Urn2MinOFF | INT | IOD_STR_disk | I1790
STRUrnikiSC10Dan3Urn3MinOFF | INT | IOD_STR_disk | I1791
STRUrnikiSC10Dan4Urn1UraON | INT | IOD_STR_disk | I1792
STRUrnikiSC10Dan4Urn2UraON | INT | IOD_STR_disk | I1793
STRUrnikiSC10Dan4Urn3UraON | INT | IOD_STR_disk | I1794
STRUrnikiSC10Dan4Urn1UraOFF | INT | IOD_STR_disk | I1795
STRUrnikiSC10Dan4Urn2UraOFF | INT | IOD_STR_disk | I1796
STRUrnikiSC10Dan4Urn3UraOFF | INT | IOD_STR_disk | I1797
STRUrnikiSC10Dan4Urn1MinON | INT | IOD_STR_disk | I1798
STRUrnikiSC10Dan4Urn2MinON | INT | IOD_STR_disk | I1799
STRUrnikiSC10Dan4Urn3MinON | INT | IOD_STR_disk | I1800
STRUrnikiSC10Dan4Urn1MinOFF | INT | IOD_STR_disk | I1801
STRUrnikiSC10Dan4Urn2MinOFF | INT | IOD_STR_disk | I1802
STRUrnikiSC10Dan4Urn3MinOFF | INT | IOD_STR_disk | I1803
STRUrnikiSC10Dan5Urn1UraON | INT | IOD_STR_disk | I1804
STRUrnikiSC10Dan5Urn2UraON | INT | IOD_STR_disk | I1805
STRUrnikiSC10Dan5Urn3UraON | INT | IOD_STR_disk | I1806
STRUrnikiSC10Dan5Urn1UraOFF | INT | IOD_STR_disk | I1807
STRUrnikiSC10Dan5Urn2UraOFF | INT | IOD_STR_disk | I1808
STRUrnikiSC10Dan5Urn3UraOFF | INT | IOD_STR_disk | I1809
STRUrnikiSC10Dan5Urn1MinON | INT | IOD_STR_disk | I1810
STRUrnikiSC10Dan5Urn2MinON | INT | IOD_STR_disk | I1811
STRUrnikiSC10Dan5Urn3MinON | INT | IOD_STR_disk | I1812
STRUrnikiSC10Dan5Urn1MinOFF | INT | IOD_STR_disk | I1813
STRUrnikiSC10Dan5Urn2MinOFF | INT | IOD_STR_disk | I1814
STRUrnikiSC10Dan5Urn3MinOFF | INT | IOD_STR_disk | I1815
STRUrnikiSC10Dan6Urn1UraON | INT | IOD_STR_disk | I1816
STRUrnikiSC10Dan6Urn2UraON | INT | IOD_STR_disk | I1817
STRUrnikiSC10Dan6Urn3UraON | INT | IOD_STR_disk | I1818
STRUrnikiSC10Dan6Urn1UraOFF | INT | IOD_STR_disk | I1819
STRUrnikiSC10Dan6Urn2UraOFF | INT | IOD_STR_disk | I1820
STRUrnikiSC10Dan6Urn3UraOFF | INT | IOD_STR_disk | I1821
STRUrnikiSC10Dan6Urn1MinON | INT | IOD_STR_disk | I1822
STRUrnikiSC10Dan6Urn2MinON | INT | IOD_STR_disk | I1823
STRUrnikiSC10Dan6Urn3MinON | INT | IOD_STR_disk | I1824
STRUrnikiSC10Dan6Urn1MinOFF | INT | IOD_STR_disk | I1825
STRUrnikiSC10Dan6Urn2MinOFF | INT | IOD_STR_disk | I1826
STRUrnikiSC10Dan6Urn3MinOFF | INT | IOD_STR_disk | I1827
STRUrnikiSC10Dan7Urn1UraON | INT | IOD_STR_disk | I1828
STRUrnikiSC10Dan7Urn2UraON | INT | IOD_STR_disk | I1829
STRUrnikiSC10Dan7Urn3UraON | INT | IOD_STR_disk | I1830
STRUrnikiSC10Dan7Urn1UraOFF | INT | IOD_STR_disk | I1831
STRUrnikiSC10Dan7Urn2UraOFF | INT | IOD_STR_disk | I1832
STRUrnikiSC10Dan7Urn3UraOFF | INT | IOD_STR_disk | I1833
STRUrnikiSC10Dan7Urn1MinON | INT | IOD_STR_disk | I1834
STRUrnikiSC10Dan7Urn2MinON | INT | IOD_STR_disk | I1835
STRUrnikiSC10Dan7Urn3MinON | INT | IOD_STR_disk | I1836
STRUrnikiSC10Dan7Urn1MinOFF | INT | IOD_STR_disk | I1837
STRUrnikiSC10Dan7Urn2MinOFF | INT | IOD_STR_disk | I1838
STRUrnikiSC10Dan7Urn3MinOFF | INT | IOD_STR_disk | I1839
STRUrnikiSC11Dan1Urn1UraON | INT | IOD_STR_disk | I1840
STRUrnikiSC11Dan1Urn2UraON | INT | IOD_STR_disk | I1841
STRUrnikiSC11Dan1Urn3UraON | INT | IOD_STR_disk | I1842
STRUrnikiSC11Dan1Urn1UraOFF | INT | IOD_STR_disk | I1843
STRUrnikiSC11Dan1Urn2UraOFF | INT | IOD_STR_disk | I1844
STRUrnikiSC11Dan1Urn3UraOFF | INT | IOD_STR_disk | I1845
STRUrnikiSC11Dan1Urn1MinON | INT | IOD_STR_disk | I1846
STRUrnikiSC11Dan1Urn2MinON | INT | IOD_STR_disk | I1847
STRUrnikiSC11Dan1Urn3MinON | INT | IOD_STR_disk | I1848
STRUrnikiSC11Dan1Urn1MinOFF | INT | IOD_STR_disk | I1849
STRUrnikiSC11Dan1Urn2MinOFF | INT | IOD_STR_disk | I1850
STRUrnikiSC11Dan1Urn3MinOFF | INT | IOD_STR_disk | I1851
STRUrnikiSC11Dan2Urn1UraON | INT | IOD_STR_disk | I1852
STRUrnikiSC11Dan2Urn2UraON | INT | IOD_STR_disk | I1853
STRUrnikiSC11Dan2Urn3UraON | INT | IOD_STR_disk | I1854
STRUrnikiSC11Dan2Urn1UraOFF | INT | IOD_STR_disk | I1855
STRUrnikiSC11Dan2Urn2UraOFF | INT | IOD_STR_disk | I1856
STRUrnikiSC11Dan2Urn3UraOFF | INT | IOD_STR_disk | I1857
STRUrnikiSC11Dan2Urn1MinON | INT | IOD_STR_disk | I1858
STRUrnikiSC11Dan2Urn2MinON | INT | IOD_STR_disk | I1859
STRUrnikiSC11Dan2Urn3MinON | INT | IOD_STR_disk | I1860
STRUrnikiSC11Dan2Urn1MinOFF | INT | IOD_STR_disk | I1861
STRUrnikiSC11Dan2Urn2MinOFF | INT | IOD_STR_disk | I1862
STRUrnikiSC11Dan2Urn3MinOFF | INT | IOD_STR_disk | I1863
STRUrnikiSC11Dan3Urn1UraON | INT | IOD_STR_disk | I1864
STRUrnikiSC11Dan3Urn2UraON | INT | IOD_STR_disk | I1865
STRUrnikiSC11Dan3Urn3UraON | INT | IOD_STR_disk | I1866
STRUrnikiSC11Dan3Urn1UraOFF | INT | IOD_STR_disk | I1867
STRUrnikiSC11Dan3Urn2UraOFF | INT | IOD_STR_disk | I1868
STRUrnikiSC11Dan3Urn3UraOFF | INT | IOD_STR_disk | I1869
STRUrnikiSC11Dan3Urn1MinON | INT | IOD_STR_disk | I1870
STRUrnikiSC11Dan3Urn2MinON | INT | IOD_STR_disk | I1871
STRUrnikiSC11Dan3Urn3MinON | INT | IOD_STR_disk | I1872
STRUrnikiSC11Dan3Urn1MinOFF | INT | IOD_STR_disk | I1873
STRUrnikiSC11Dan3Urn2MinOFF | INT | IOD_STR_disk | I1874
STRUrnikiSC11Dan3Urn3MinOFF | INT | IOD_STR_disk | I1875
STRUrnikiSC11Dan4Urn1UraON | INT | IOD_STR_disk | I1876
STRUrnikiSC11Dan4Urn2UraON | INT | IOD_STR_disk | I1877
STRUrnikiSC11Dan4Urn3UraON | INT | IOD_STR_disk | I1878
STRUrnikiSC11Dan4Urn1UraOFF | INT | IOD_STR_disk | I1879
STRUrnikiSC11Dan4Urn2UraOFF | INT | IOD_STR_disk | I1880
STRUrnikiSC11Dan4Urn3UraOFF | INT | IOD_STR_disk | I1881
STRUrnikiSC11Dan4Urn1MinON | INT | IOD_STR_disk | I1882
STRUrnikiSC11Dan4Urn2MinON | INT | IOD_STR_disk | I1883
STRUrnikiSC11Dan4Urn3MinON | INT | IOD_STR_disk | I1884
STRUrnikiSC11Dan4Urn1MinOFF | INT | IOD_STR_disk | I1885
STRUrnikiSC11Dan4Urn2MinOFF | INT | IOD_STR_disk | I1886
STRUrnikiSC11Dan4Urn3MinOFF | INT | IOD_STR_disk | I1887
STRUrnikiSC11Dan5Urn1UraON | INT | IOD_STR_disk | I1888
STRUrnikiSC11Dan5Urn2UraON | INT | IOD_STR_disk | I1889
STRUrnikiSC11Dan5Urn3UraON | INT | IOD_STR_disk | I1890
STRUrnikiSC11Dan5Urn1UraOFF | INT | IOD_STR_disk | I1891
STRUrnikiSC11Dan5Urn2UraOFF | INT | IOD_STR_disk | I1892
STRUrnikiSC11Dan5Urn3UraOFF | INT | IOD_STR_disk | I1893
STRUrnikiSC11Dan5Urn1MinON | INT | IOD_STR_disk | I1894
STRUrnikiSC11Dan5Urn2MinON | INT | IOD_STR_disk | I1895
STRUrnikiSC11Dan5Urn3MinON | INT | IOD_STR_disk | I1896
STRUrnikiSC11Dan5Urn1MinOFF | INT | IOD_STR_disk | I1897
STRUrnikiSC11Dan5Urn2MinOFF | INT | IOD_STR_disk | I1898
STRUrnikiSC11Dan5Urn3MinOFF | INT | IOD_STR_disk | I1899
STRUrnikiSC11Dan6Urn1UraON | INT | IOD_STR_disk | I1900
STRUrnikiSC11Dan6Urn2UraON | INT | IOD_STR_disk | I1901
STRUrnikiSC11Dan6Urn3UraON | INT | IOD_STR_disk | I1902
STRUrnikiSC11Dan6Urn1UraOFF | INT | IOD_STR_disk | I1903
STRUrnikiSC11Dan6Urn2UraOFF | INT | IOD_STR_disk | I1904
STRUrnikiSC11Dan6Urn3UraOFF | INT | IOD_STR_disk | I1905
STRUrnikiSC11Dan6Urn1MinON | INT | IOD_STR_disk | I1906
STRUrnikiSC11Dan6Urn2MinON | INT | IOD_STR_disk | I1907
STRUrnikiSC11Dan6Urn3MinON | INT | IOD_STR_disk | I1908
STRUrnikiSC11Dan6Urn1MinOFF | INT | IOD_STR_disk | I1909
STRUrnikiSC11Dan6Urn2MinOFF | INT | IOD_STR_disk | I1910
STRUrnikiSC11Dan6Urn3MinOFF | INT | IOD_STR_disk | I1911
STRUrnikiSC11Dan7Urn1UraON | INT | IOD_STR_disk | I1912
STRUrnikiSC11Dan7Urn2UraON | INT | IOD_STR_disk | I1913
STRUrnikiSC11Dan7Urn3UraON | INT | IOD_STR_disk | I1914
STRUrnikiSC11Dan7Urn1UraOFF | INT | IOD_STR_disk | I1915
STRUrnikiSC11Dan7Urn2UraOFF | INT | IOD_STR_disk | I1916
STRUrnikiSC11Dan7Urn3UraOFF | INT | IOD_STR_disk | I1917
STRUrnikiSC11Dan7Urn1MinON | INT | IOD_STR_disk | I1918
STRUrnikiSC11Dan7Urn2MinON | INT | IOD_STR_disk | I1919
STRUrnikiSC11Dan7Urn3MinON | INT | IOD_STR_disk | I1920
STRUrnikiSC11Dan7Urn1MinOFF | INT | IOD_STR_disk | I1921
STRUrnikiSC11Dan7Urn2MinOFF | INT | IOD_STR_disk | I1922
STRUrnikiSC11Dan7Urn3MinOFF | INT | IOD_STR_disk | I1923
STRUrnikiSC12Dan1Urn1UraON | INT | IOD_STR_disk | I1924
STRUrnikiSC12Dan1Urn2UraON | INT | IOD_STR_disk | I1925
STRUrnikiSC12Dan1Urn3UraON | INT | IOD_STR_disk | I1926
STRUrnikiSC12Dan1Urn1UraOFF | INT | IOD_STR_disk | I1927
STRUrnikiSC12Dan1Urn2UraOFF | INT | IOD_STR_disk | I1928
STRUrnikiSC12Dan1Urn3UraOFF | INT | IOD_STR_disk | I1929
STRUrnikiSC12Dan1Urn1MinON | INT | IOD_STR_disk | I1930
STRUrnikiSC12Dan1Urn2MinON | INT | IOD_STR_disk | I1931
STRUrnikiSC12Dan1Urn3MinON | INT | IOD_STR_disk | I1932
STRUrnikiSC12Dan1Urn1MinOFF | INT | IOD_STR_disk | I1933
STRUrnikiSC12Dan1Urn2MinOFF | INT | IOD_STR_disk | I1934
STRUrnikiSC12Dan1Urn3MinOFF | INT | IOD_STR_disk | I1935
STRUrnikiSC12Dan2Urn1UraON | INT | IOD_STR_disk | I1936
STRUrnikiSC12Dan2Urn2UraON | INT | IOD_STR_disk | I1937
STRUrnikiSC12Dan2Urn3UraON | INT | IOD_STR_disk | I1938
STRUrnikiSC12Dan2Urn1UraOFF | INT | IOD_STR_disk | I1939
STRUrnikiSC12Dan2Urn2UraOFF | INT | IOD_STR_disk | I1940
STRUrnikiSC12Dan2Urn3UraOFF | INT | IOD_STR_disk | I1941
STRUrnikiSC12Dan2Urn1MinON | INT | IOD_STR_disk | I1942
STRUrnikiSC12Dan2Urn2MinON | INT | IOD_STR_disk | I1943
STRUrnikiSC12Dan2Urn3MinON | INT | IOD_STR_disk | I1944
STRUrnikiSC12Dan2Urn1MinOFF | INT | IOD_STR_disk | I1945
STRUrnikiSC12Dan2Urn2MinOFF | INT | IOD_STR_disk | I1946
STRUrnikiSC12Dan2Urn3MinOFF | INT | IOD_STR_disk | I1947
STRUrnikiSC12Dan3Urn1UraON | INT | IOD_STR_disk | I1948
STRUrnikiSC12Dan3Urn2UraON | INT | IOD_STR_disk | I1949
STRUrnikiSC12Dan3Urn3UraON | INT | IOD_STR_disk | I1950
STRUrnikiSC12Dan3Urn1UraOFF | INT | IOD_STR_disk | I1951
STRUrnikiSC12Dan3Urn2UraOFF | INT | IOD_STR_disk | I1952
STRUrnikiSC12Dan3Urn3UraOFF | INT | IOD_STR_disk | I1953
STRUrnikiSC12Dan3Urn1MinON | INT | IOD_STR_disk | I1954
STRUrnikiSC12Dan3Urn2MinON | INT | IOD_STR_disk | I1955
STRUrnikiSC12Dan3Urn3MinON | INT | IOD_STR_disk | I1956
STRUrnikiSC12Dan3Urn1MinOFF | INT | IOD_STR_disk | I1957
STRUrnikiSC12Dan3Urn2MinOFF | INT | IOD_STR_disk | I1958
STRUrnikiSC12Dan3Urn3MinOFF | INT | IOD_STR_disk | I1959
STRUrnikiSC12Dan4Urn1UraON | INT | IOD_STR_disk | I1960
STRUrnikiSC12Dan4Urn2UraON | INT | IOD_STR_disk | I1961
STRUrnikiSC12Dan4Urn3UraON | INT | IOD_STR_disk | I1962
STRUrnikiSC12Dan4Urn1UraOFF | INT | IOD_STR_disk | I1963
STRUrnikiSC12Dan4Urn2UraOFF | INT | IOD_STR_disk | I1964
STRUrnikiSC12Dan4Urn3UraOFF | INT | IOD_STR_disk | I1965
STRUrnikiSC12Dan4Urn1MinON | INT | IOD_STR_disk | I1966
STRUrnikiSC12Dan4Urn2MinON | INT | IOD_STR_disk | I1967
STRUrnikiSC12Dan4Urn3MinON | INT | IOD_STR_disk | I1968
STRUrnikiSC12Dan4Urn1MinOFF | INT | IOD_STR_disk | I1969
STRUrnikiSC12Dan4Urn2MinOFF | INT | IOD_STR_disk | I1970
STRUrnikiSC12Dan4Urn3MinOFF | INT | IOD_STR_disk | I1971
STRUrnikiSC12Dan5Urn1UraON | INT | IOD_STR_disk | I1972
STRUrnikiSC12Dan5Urn2UraON | INT | IOD_STR_disk | I1973
STRUrnikiSC12Dan5Urn3UraON | INT | IOD_STR_disk | I1974
STRUrnikiSC12Dan5Urn1UraOFF | INT | IOD_STR_disk | I1975
STRUrnikiSC12Dan5Urn2UraOFF | INT | IOD_STR_disk | I1976
STRUrnikiSC12Dan5Urn3UraOFF | INT | IOD_STR_disk | I1977
STRUrnikiSC12Dan5Urn1MinON | INT | IOD_STR_disk | I1978
STRUrnikiSC12Dan5Urn2MinON | INT | IOD_STR_disk | I1979
STRUrnikiSC12Dan5Urn3MinON | INT | IOD_STR_disk | I1980
STRUrnikiSC12Dan5Urn1MinOFF | INT | IOD_STR_disk | I1981
STRUrnikiSC12Dan5Urn2MinOFF | INT | IOD_STR_disk | I1982
STRUrnikiSC12Dan5Urn3MinOFF | INT | IOD_STR_disk | I1983
STRUrnikiSC12Dan6Urn1UraON | INT | IOD_STR_disk | I1984
STRUrnikiSC12Dan6Urn2UraON | INT | IOD_STR_disk | I1985
STRUrnikiSC12Dan6Urn3UraON | INT | IOD_STR_disk | I1986
STRUrnikiSC12Dan6Urn1UraOFF | INT | IOD_STR_disk | I1987
STRUrnikiSC12Dan6Urn2UraOFF | INT | IOD_STR_disk | I1988
STRUrnikiSC12Dan6Urn3UraOFF | INT | IOD_STR_disk | I1989
STRUrnikiSC12Dan6Urn1MinON | INT | IOD_STR_disk | I1990
STRUrnikiSC12Dan6Urn2MinON | INT | IOD_STR_disk | I1991
STRUrnikiSC12Dan6Urn3MinON | INT | IOD_STR_disk | I1992
STRUrnikiSC12Dan6Urn1MinOFF | INT | IOD_STR_disk | I1993
STRUrnikiSC12Dan6Urn2MinOFF | INT | IOD_STR_disk | I1994
STRUrnikiSC12Dan6Urn3MinOFF | INT | IOD_STR_disk | I1995
STRUrnikiSC12Dan7Urn1UraON | INT | IOD_STR_disk | I1996
STRUrnikiSC12Dan7Urn2UraON | INT | IOD_STR_disk | I1997
STRUrnikiSC12Dan7Urn3UraON | INT | IOD_STR_disk | I1998
STRUrnikiSC12Dan7Urn1UraOFF | INT | IOD_STR_disk | I1999
STRUrnikiSC12Dan7Urn2UraOFF | INT | IOD_STR_disk | I2000
STRUrnikiSC12Dan7Urn3UraOFF | INT | IOD_STR_disk | I2001
STRUrnikiSC12Dan7Urn1MinON | INT | IOD_STR_disk | I2002
STRUrnikiSC12Dan7Urn2MinON | INT | IOD_STR_disk | I2003
STRUrnikiSC12Dan7Urn3MinON | INT | IOD_STR_disk | I2004
STRUrnikiSC12Dan7Urn1MinOFF | INT | IOD_STR_disk | I2005
STRUrnikiSC12Dan7Urn2MinOFF | INT | IOD_STR_disk | I2006
STRUrnikiSC12Dan7Urn3MinOFF | INT | IOD_STR_disk | I2007
STRUrnikiSC13Dan1Urn1UraON | INT | IOD_STR_disk | I2008
STRUrnikiSC13Dan1Urn2UraON | INT | IOD_STR_disk | I2009
STRUrnikiSC13Dan1Urn3UraON | INT | IOD_STR_disk | I2010
STRUrnikiSC13Dan1Urn1UraOFF | INT | IOD_STR_disk | I2011
STRUrnikiSC13Dan1Urn2UraOFF | INT | IOD_STR_disk | I2012
STRUrnikiSC13Dan1Urn3UraOFF | INT | IOD_STR_disk | I2013
STRUrnikiSC13Dan1Urn1MinON | INT | IOD_STR_disk | I2014
STRUrnikiSC13Dan1Urn2MinON | INT | IOD_STR_disk | I2015
STRUrnikiSC13Dan1Urn3MinON | INT | IOD_STR_disk | I2016
STRUrnikiSC13Dan1Urn1MinOFF | INT | IOD_STR_disk | I2017
STRUrnikiSC13Dan1Urn2MinOFF | INT | IOD_STR_disk | I2018
STRUrnikiSC13Dan1Urn3MinOFF | INT | IOD_STR_disk | I2019
STRUrnikiSC13Dan2Urn1UraON | INT | IOD_STR_disk | I2020
STRUrnikiSC13Dan2Urn2UraON | INT | IOD_STR_disk | I2021
STRUrnikiSC13Dan2Urn3UraON | INT | IOD_STR_disk | I2022
STRUrnikiSC13Dan2Urn1UraOFF | INT | IOD_STR_disk | I2023
STRUrnikiSC13Dan2Urn2UraOFF | INT | IOD_STR_disk | I2024
STRUrnikiSC13Dan2Urn3UraOFF | INT | IOD_STR_disk | I2025
STRUrnikiSC13Dan2Urn1MinON | INT | IOD_STR_disk | I2026
STRUrnikiSC13Dan2Urn2MinON | INT | IOD_STR_disk | I2027
STRUrnikiSC13Dan2Urn3MinON | INT | IOD_STR_disk | I2028
STRUrnikiSC13Dan2Urn1MinOFF | INT | IOD_STR_disk | I2029
STRUrnikiSC13Dan2Urn2MinOFF | INT | IOD_STR_disk | I2030
STRUrnikiSC13Dan2Urn3MinOFF | INT | IOD_STR_disk | I2031
STRUrnikiSC13Dan3Urn1UraON | INT | IOD_STR_disk | I2032
STRUrnikiSC13Dan3Urn2UraON | INT | IOD_STR_disk | I2033
STRUrnikiSC13Dan3Urn3UraON | INT | IOD_STR_disk | I2034
STRUrnikiSC13Dan3Urn1UraOFF | INT | IOD_STR_disk | I2035
STRUrnikiSC13Dan3Urn2UraOFF | INT | IOD_STR_disk | I2036
STRUrnikiSC13Dan3Urn3UraOFF | INT | IOD_STR_disk | I2037
STRUrnikiSC13Dan3Urn1MinON | INT | IOD_STR_disk | I2038
STRUrnikiSC13Dan3Urn2MinON | INT | IOD_STR_disk | I2039
STRUrnikiSC13Dan3Urn3MinON | INT | IOD_STR_disk | I2040
STRUrnikiSC13Dan3Urn1MinOFF | INT | IOD_STR_disk | I2041
STRUrnikiSC13Dan3Urn2MinOFF | INT | IOD_STR_disk | I2042
STRUrnikiSC13Dan3Urn3MinOFF | INT | IOD_STR_disk | I2043
STRUrnikiSC13Dan4Urn1UraON | INT | IOD_STR_disk | I2044
STRUrnikiSC13Dan4Urn2UraON | INT | IOD_STR_disk | I2045
STRUrnikiSC13Dan4Urn3UraON | INT | IOD_STR_disk | I2046
STRUrnikiSC13Dan4Urn1UraOFF | INT | IOD_STR_disk | I2047
STRUrnikiSC13Dan4Urn2UraOFF | INT | IOD_STR_disk | I2048
STRUrnikiSC13Dan4Urn3UraOFF | INT | IOD_STR_disk | I2049
STRUrnikiSC13Dan4Urn1MinON | INT | IOD_STR_disk | I2050
STRUrnikiSC13Dan4Urn2MinON | INT | IOD_STR_disk | I2051
STRUrnikiSC13Dan4Urn3MinON | INT | IOD_STR_disk | I2052
STRUrnikiSC13Dan4Urn1MinOFF | INT | IOD_STR_disk | I2053
STRUrnikiSC13Dan4Urn2MinOFF | INT | IOD_STR_disk | I2054
STRUrnikiSC13Dan4Urn3MinOFF | INT | IOD_STR_disk | I2055
STRUrnikiSC13Dan5Urn1UraON | INT | IOD_STR_disk | I2056
STRUrnikiSC13Dan5Urn2UraON | INT | IOD_STR_disk | I2057
STRUrnikiSC13Dan5Urn3UraON | INT | IOD_STR_disk | I2058
STRUrnikiSC13Dan5Urn1UraOFF | INT | IOD_STR_disk | I2059
STRUrnikiSC13Dan5Urn2UraOFF | INT | IOD_STR_disk | I2060
STRUrnikiSC13Dan5Urn3UraOFF | INT | IOD_STR_disk | I2061
STRUrnikiSC13Dan5Urn1MinON | INT | IOD_STR_disk | I2062
STRUrnikiSC13Dan5Urn2MinON | INT | IOD_STR_disk | I2063
STRUrnikiSC13Dan5Urn3MinON | INT | IOD_STR_disk | I2064
STRUrnikiSC13Dan5Urn1MinOFF | INT | IOD_STR_disk | I2065
STRUrnikiSC13Dan5Urn2MinOFF | INT | IOD_STR_disk | I2066
STRUrnikiSC13Dan5Urn3MinOFF | INT | IOD_STR_disk | I2067
STRUrnikiSC13Dan6Urn1UraON | INT | IOD_STR_disk | I2068
STRUrnikiSC13Dan6Urn2UraON | INT | IOD_STR_disk | I2069
STRUrnikiSC13Dan6Urn3UraON | INT | IOD_STR_disk | I2070
STRUrnikiSC13Dan6Urn1UraOFF | INT | IOD_STR_disk | I2071
STRUrnikiSC13Dan6Urn2UraOFF | INT | IOD_STR_disk | I2072
STRUrnikiSC13Dan6Urn3UraOFF | INT | IOD_STR_disk | I2073
STRUrnikiSC13Dan6Urn1MinON | INT | IOD_STR_disk | I2074
STRUrnikiSC13Dan6Urn2MinON | INT | IOD_STR_disk | I2075
STRUrnikiSC13Dan6Urn3MinON | INT | IOD_STR_disk | I2076
STRUrnikiSC13Dan6Urn1MinOFF | INT | IOD_STR_disk | I2077
STRUrnikiSC13Dan6Urn2MinOFF | INT | IOD_STR_disk | I2078
STRUrnikiSC13Dan6Urn3MinOFF | INT | IOD_STR_disk | I2079
STRUrnikiSC13Dan7Urn1UraON | INT | IOD_STR_disk | I2080
STRUrnikiSC13Dan7Urn2UraON | INT | IOD_STR_disk | I2081
STRUrnikiSC13Dan7Urn3UraON | INT | IOD_STR_disk | I2082
STRUrnikiSC13Dan7Urn1UraOFF | INT | IOD_STR_disk | I2083
STRUrnikiSC13Dan7Urn2UraOFF | INT | IOD_STR_disk | I2084
STRUrnikiSC13Dan7Urn3UraOFF | INT | IOD_STR_disk | I2085
STRUrnikiSC13Dan7Urn1MinON | INT | IOD_STR_disk | I2086
STRUrnikiSC13Dan7Urn2MinON | INT | IOD_STR_disk | I2087
STRUrnikiSC13Dan7Urn3MinON | INT | IOD_STR_disk | I2088
STRUrnikiSC13Dan7Urn1MinOFF | INT | IOD_STR_disk | I2089
STRUrnikiSC13Dan7Urn2MinOFF | INT | IOD_STR_disk | I2090
STRUrnikiSC13Dan7Urn3MinOFF | INT | IOD_STR_disk | I2091
STRUrnikiSC14Dan1Urn1UraON | INT | IOD_STR_disk | I2092
STRUrnikiSC14Dan1Urn2UraON | INT | IOD_STR_disk | I2093
STRUrnikiSC14Dan1Urn3UraON | INT | IOD_STR_disk | I2094
STRUrnikiSC14Dan1Urn1UraOFF | INT | IOD_STR_disk | I2095
STRUrnikiSC14Dan1Urn2UraOFF | INT | IOD_STR_disk | I2096
STRUrnikiSC14Dan1Urn3UraOFF | INT | IOD_STR_disk | I2097
STRUrnikiSC14Dan1Urn1MinON | INT | IOD_STR_disk | I2098
STRUrnikiSC14Dan1Urn2MinON | INT | IOD_STR_disk | I2099
STRUrnikiSC14Dan1Urn3MinON | INT | IOD_STR_disk | I2100
STRUrnikiSC14Dan1Urn1MinOFF | INT | IOD_STR_disk | I2101
STRUrnikiSC14Dan1Urn2MinOFF | INT | IOD_STR_disk | I2102
STRUrnikiSC14Dan1Urn3MinOFF | INT | IOD_STR_disk | I2103
STRUrnikiSC14Dan2Urn1UraON | INT | IOD_STR_disk | I2104
STRUrnikiSC14Dan2Urn2UraON | INT | IOD_STR_disk | I2105
STRUrnikiSC14Dan2Urn3UraON | INT | IOD_STR_disk | I2106
STRUrnikiSC14Dan2Urn1UraOFF | INT | IOD_STR_disk | I2107
STRUrnikiSC14Dan2Urn2UraOFF | INT | IOD_STR_disk | I2108
STRUrnikiSC14Dan2Urn3UraOFF | INT | IOD_STR_disk | I2109
STRUrnikiSC14Dan2Urn1MinON | INT | IOD_STR_disk | I2110
STRUrnikiSC14Dan2Urn2MinON | INT | IOD_STR_disk | I2111
STRUrnikiSC14Dan2Urn3MinON | INT | IOD_STR_disk | I2112
STRUrnikiSC14Dan2Urn1MinOFF | INT | IOD_STR_disk | I2113
STRUrnikiSC14Dan2Urn2MinOFF | INT | IOD_STR_disk | I2114
STRUrnikiSC14Dan2Urn3MinOFF | INT | IOD_STR_disk | I2115
STRUrnikiSC14Dan3Urn1UraON | INT | IOD_STR_disk | I2116
STRUrnikiSC14Dan3Urn2UraON | INT | IOD_STR_disk | I2117
STRUrnikiSC14Dan3Urn3UraON | INT | IOD_STR_disk | I2118
STRUrnikiSC14Dan3Urn1UraOFF | INT | IOD_STR_disk | I2119
STRUrnikiSC14Dan3Urn2UraOFF | INT | IOD_STR_disk | I2120
STRUrnikiSC14Dan3Urn3UraOFF | INT | IOD_STR_disk | I2121
STRUrnikiSC14Dan3Urn1MinON | INT | IOD_STR_disk | I2122
STRUrnikiSC14Dan3Urn2MinON | INT | IOD_STR_disk | I2123
STRUrnikiSC14Dan3Urn3MinON | INT | IOD_STR_disk | I2124
STRUrnikiSC14Dan3Urn1MinOFF | INT | IOD_STR_disk | I2125
STRUrnikiSC14Dan3Urn2MinOFF | INT | IOD_STR_disk | I2126
STRUrnikiSC14Dan3Urn3MinOFF | INT | IOD_STR_disk | I2127
STRUrnikiSC14Dan4Urn1UraON | INT | IOD_STR_disk | I2128
STRUrnikiSC14Dan4Urn2UraON | INT | IOD_STR_disk | I2129
STRUrnikiSC14Dan4Urn3UraON | INT | IOD_STR_disk | I2130
STRUrnikiSC14Dan4Urn1UraOFF | INT | IOD_STR_disk | I2131
STRUrnikiSC14Dan4Urn2UraOFF | INT | IOD_STR_disk | I2132
STRUrnikiSC14Dan4Urn3UraOFF | INT | IOD_STR_disk | I2133
STRUrnikiSC14Dan4Urn1MinON | INT | IOD_STR_disk | I2134
STRUrnikiSC14Dan4Urn2MinON | INT | IOD_STR_disk | I2135
STRUrnikiSC14Dan4Urn3MinON | INT | IOD_STR_disk | I2136
STRUrnikiSC14Dan4Urn1MinOFF | INT | IOD_STR_disk | I2137
STRUrnikiSC14Dan4Urn2MinOFF | INT | IOD_STR_disk | I2138
STRUrnikiSC14Dan4Urn3MinOFF | INT | IOD_STR_disk | I2139
STRUrnikiSC14Dan5Urn1UraON | INT | IOD_STR_disk | I2140
STRUrnikiSC14Dan5Urn2UraON | INT | IOD_STR_disk | I2141
STRUrnikiSC14Dan5Urn3UraON | INT | IOD_STR_disk | I2142
STRUrnikiSC14Dan5Urn1UraOFF | INT | IOD_STR_disk | I2143
STRUrnikiSC14Dan5Urn2UraOFF | INT | IOD_STR_disk | I2144
STRUrnikiSC14Dan5Urn3UraOFF | INT | IOD_STR_disk | I2145
STRUrnikiSC14Dan5Urn1MinON | INT | IOD_STR_disk | I2146
STRUrnikiSC14Dan5Urn2MinON | INT | IOD_STR_disk | I2147
STRUrnikiSC14Dan5Urn3MinON | INT | IOD_STR_disk | I2148
STRUrnikiSC14Dan5Urn1MinOFF | INT | IOD_STR_disk | I2149
STRUrnikiSC14Dan5Urn2MinOFF | INT | IOD_STR_disk | I2150
STRUrnikiSC14Dan5Urn3MinOFF | INT | IOD_STR_disk | I2151
STRUrnikiSC14Dan6Urn1UraON | INT | IOD_STR_disk | I2152
STRUrnikiSC14Dan6Urn2UraON | INT | IOD_STR_disk | I2153
STRUrnikiSC14Dan6Urn3UraON | INT | IOD_STR_disk | I2154
STRUrnikiSC14Dan6Urn1UraOFF | INT | IOD_STR_disk | I2155
STRUrnikiSC14Dan6Urn2UraOFF | INT | IOD_STR_disk | I2156
STRUrnikiSC14Dan6Urn3UraOFF | INT | IOD_STR_disk | I2157
STRUrnikiSC14Dan6Urn1MinON | INT | IOD_STR_disk | I2158
STRUrnikiSC14Dan6Urn2MinON | INT | IOD_STR_disk | I2159
STRUrnikiSC14Dan6Urn3MinON | INT | IOD_STR_disk | I2160
STRUrnikiSC14Dan6Urn1MinOFF | INT | IOD_STR_disk | I2161
STRUrnikiSC14Dan6Urn2MinOFF | INT | IOD_STR_disk | I2162
STRUrnikiSC14Dan6Urn3MinOFF | INT | IOD_STR_disk | I2163
STRUrnikiSC14Dan7Urn1UraON | INT | IOD_STR_disk | I2164
STRUrnikiSC14Dan7Urn2UraON | INT | IOD_STR_disk | I2165
STRUrnikiSC14Dan7Urn3UraON | INT | IOD_STR_disk | I2166
STRUrnikiSC14Dan7Urn1UraOFF | INT | IOD_STR_disk | I2167
STRUrnikiSC14Dan7Urn2UraOFF | INT | IOD_STR_disk | I2168
STRUrnikiSC14Dan7Urn3UraOFF | INT | IOD_STR_disk | I2169
STRUrnikiSC14Dan7Urn1MinON | INT | IOD_STR_disk | I2170
STRUrnikiSC14Dan7Urn2MinON | INT | IOD_STR_disk | I2171
STRUrnikiSC14Dan7Urn3MinON | INT | IOD_STR_disk | I2172
STRUrnikiSC14Dan7Urn1MinOFF | INT | IOD_STR_disk | I2173
STRUrnikiSC14Dan7Urn2MinOFF | INT | IOD_STR_disk | I2174
STRUrnikiSC14Dan7Urn3MinOFF | INT | IOD_STR_disk | I2175
STRUrnikiSC15Dan1Urn1UraON | INT | IOD_STR_disk | I2176
STRUrnikiSC15Dan1Urn2UraON | INT | IOD_STR_disk | I2177
STRUrnikiSC15Dan1Urn3UraON | INT | IOD_STR_disk | I2178
STRUrnikiSC15Dan1Urn1UraOFF | INT | IOD_STR_disk | I2179
STRUrnikiSC15Dan1Urn2UraOFF | INT | IOD_STR_disk | I2180
STRUrnikiSC15Dan1Urn3UraOFF | INT | IOD_STR_disk | I2181
STRUrnikiSC15Dan1Urn1MinON | INT | IOD_STR_disk | I2182
STRUrnikiSC15Dan1Urn2MinON | INT | IOD_STR_disk | I2183
STRUrnikiSC15Dan1Urn3MinON | INT | IOD_STR_disk | I2184
STRUrnikiSC15Dan1Urn1MinOFF | INT | IOD_STR_disk | I2185
STRUrnikiSC15Dan1Urn2MinOFF | INT | IOD_STR_disk | I2186
STRUrnikiSC15Dan1Urn3MinOFF | INT | IOD_STR_disk | I2187
STRUrnikiSC15Dan2Urn1UraON | INT | IOD_STR_disk | I2188
STRUrnikiSC15Dan2Urn2UraON | INT | IOD_STR_disk | I2189
STRUrnikiSC15Dan2Urn3UraON | INT | IOD_STR_disk | I2190
STRUrnikiSC15Dan2Urn1UraOFF | INT | IOD_STR_disk | I2191
STRUrnikiSC15Dan2Urn2UraOFF | INT | IOD_STR_disk | I2192
STRUrnikiSC15Dan2Urn3UraOFF | INT | IOD_STR_disk | I2193
STRUrnikiSC15Dan2Urn1MinON | INT | IOD_STR_disk | I2194
STRUrnikiSC15Dan2Urn2MinON | INT | IOD_STR_disk | I2195
STRUrnikiSC15Dan2Urn3MinON | INT | IOD_STR_disk | I2196
STRUrnikiSC15Dan2Urn1MinOFF | INT | IOD_STR_disk | I2197
STRUrnikiSC15Dan2Urn2MinOFF | INT | IOD_STR_disk | I2198
STRUrnikiSC15Dan2Urn3MinOFF | INT | IOD_STR_disk | I2199
STRUrnikiSC15Dan3Urn1UraON | INT | IOD_STR_disk | I2200
STRUrnikiSC15Dan3Urn2UraON | INT | IOD_STR_disk | I2201
STRUrnikiSC15Dan3Urn3UraON | INT | IOD_STR_disk | I2202
STRUrnikiSC15Dan3Urn1UraOFF | INT | IOD_STR_disk | I2203
STRUrnikiSC15Dan3Urn2UraOFF | INT | IOD_STR_disk | I2204
STRUrnikiSC15Dan3Urn3UraOFF | INT | IOD_STR_disk | I2205
STRUrnikiSC15Dan3Urn1MinON | INT | IOD_STR_disk | I2206
STRUrnikiSC15Dan3Urn2MinON | INT | IOD_STR_disk | I2207
STRUrnikiSC15Dan3Urn3MinON | INT | IOD_STR_disk | I2208
STRUrnikiSC15Dan3Urn1MinOFF | INT | IOD_STR_disk | I2209
STRUrnikiSC15Dan3Urn2MinOFF | INT | IOD_STR_disk | I2210
STRUrnikiSC15Dan3Urn3MinOFF | INT | IOD_STR_disk | I2211
STRUrnikiSC15Dan4Urn1UraON | INT | IOD_STR_disk | I2212
STRUrnikiSC15Dan4Urn2UraON | INT | IOD_STR_disk | I2213
STRUrnikiSC15Dan4Urn3UraON | INT | IOD_STR_disk | I2214
STRUrnikiSC15Dan4Urn1UraOFF | INT | IOD_STR_disk | I2215
STRUrnikiSC15Dan4Urn2UraOFF | INT | IOD_STR_disk | I2216
STRUrnikiSC15Dan4Urn3UraOFF | INT | IOD_STR_disk | I2217
STRUrnikiSC15Dan4Urn1MinON | INT | IOD_STR_disk | I2218
STRUrnikiSC15Dan4Urn2MinON | INT | IOD_STR_disk | I2219
STRUrnikiSC15Dan4Urn3MinON | INT | IOD_STR_disk | I2220
STRUrnikiSC15Dan4Urn1MinOFF | INT | IOD_STR_disk | I2221
STRUrnikiSC15Dan4Urn2MinOFF | INT | IOD_STR_disk | I2222
STRUrnikiSC15Dan4Urn3MinOFF | INT | IOD_STR_disk | I2223
STRUrnikiSC15Dan5Urn1UraON | INT | IOD_STR_disk | I2224
STRUrnikiSC15Dan5Urn2UraON | INT | IOD_STR_disk | I2225
STRUrnikiSC15Dan5Urn3UraON | INT | IOD_STR_disk | I2226
STRUrnikiSC15Dan5Urn1UraOFF | INT | IOD_STR_disk | I2227
STRUrnikiSC15Dan5Urn2UraOFF | INT | IOD_STR_disk | I2228
STRUrnikiSC15Dan5Urn3UraOFF | INT | IOD_STR_disk | I2229
STRUrnikiSC15Dan5Urn1MinON | INT | IOD_STR_disk | I2230
STRUrnikiSC15Dan5Urn2MinON | INT | IOD_STR_disk | I2231
STRUrnikiSC15Dan5Urn3MinON | INT | IOD_STR_disk | I2232
STRUrnikiSC15Dan5Urn1MinOFF | INT | IOD_STR_disk | I2233
STRUrnikiSC15Dan5Urn2MinOFF | INT | IOD_STR_disk | I2234
STRUrnikiSC15Dan5Urn3MinOFF | INT | IOD_STR_disk | I2235
STRUrnikiSC15Dan6Urn1UraON | INT | IOD_STR_disk | I2236
STRUrnikiSC15Dan6Urn2UraON | INT | IOD_STR_disk | I2237
STRUrnikiSC15Dan6Urn3UraON | INT | IOD_STR_disk | I2238
STRUrnikiSC15Dan6Urn1UraOFF | INT | IOD_STR_disk | I2239
STRUrnikiSC15Dan6Urn2UraOFF | INT | IOD_STR_disk | I2240
STRUrnikiSC15Dan6Urn3UraOFF | INT | IOD_STR_disk | I2241
STRUrnikiSC15Dan6Urn1MinON | INT | IOD_STR_disk | I2242
STRUrnikiSC15Dan6Urn2MinON | INT | IOD_STR_disk | I2243
STRUrnikiSC15Dan6Urn3MinON | INT | IOD_STR_disk | I2244
STRUrnikiSC15Dan6Urn1MinOFF | INT | IOD_STR_disk | I2245
STRUrnikiSC15Dan6Urn2MinOFF | INT | IOD_STR_disk | I2246
STRUrnikiSC15Dan6Urn3MinOFF | INT | IOD_STR_disk | I2247
STRUrnikiSC15Dan7Urn1UraON | INT | IOD_STR_disk | I2248
STRUrnikiSC15Dan7Urn2UraON | INT | IOD_STR_disk | I2249
STRUrnikiSC15Dan7Urn3UraON | INT | IOD_STR_disk | I2250
STRUrnikiSC15Dan7Urn1UraOFF | INT | IOD_STR_disk | I2251
STRUrnikiSC15Dan7Urn2UraOFF | INT | IOD_STR_disk | I2252
STRUrnikiSC15Dan7Urn3UraOFF | INT | IOD_STR_disk | I2253
STRUrnikiSC15Dan7Urn1MinON | INT | IOD_STR_disk | I2254
STRUrnikiSC15Dan7Urn2MinON | INT | IOD_STR_disk | I2255
STRUrnikiSC15Dan7Urn3MinON | INT | IOD_STR_disk | I2256
STRUrnikiSC15Dan7Urn1MinOFF | INT | IOD_STR_disk | I2257
STRUrnikiSC15Dan7Urn2MinOFF | INT | IOD_STR_disk | I2258
STRUrnikiSC15Dan7Urn3MinOFF | INT | IOD_STR_disk | I2259
STRUrnikiSC16Dan1Urn1UraON | INT | IOD_STR_disk | I2260
STRUrnikiSC16Dan1Urn2UraON | INT | IOD_STR_disk | I2261
STRUrnikiSC16Dan1Urn3UraON | INT | IOD_STR_disk | I2262
STRUrnikiSC16Dan1Urn1UraOFF | INT | IOD_STR_disk | I2263
STRUrnikiSC16Dan1Urn2UraOFF | INT | IOD_STR_disk | I2264
STRUrnikiSC16Dan1Urn3UraOFF | INT | IOD_STR_disk | I2265
STRUrnikiSC16Dan1Urn1MinON | INT | IOD_STR_disk | I2266
STRUrnikiSC16Dan1Urn2MinON | INT | IOD_STR_disk | I2267
STRUrnikiSC16Dan1Urn3MinON | INT | IOD_STR_disk | I2268
STRUrnikiSC16Dan1Urn1MinOFF | INT | IOD_STR_disk | I2269
STRUrnikiSC16Dan1Urn2MinOFF | INT | IOD_STR_disk | I2270
STRUrnikiSC16Dan1Urn3MinOFF | INT | IOD_STR_disk | I2271
STRUrnikiSC16Dan2Urn1UraON | INT | IOD_STR_disk | I2272
STRUrnikiSC16Dan2Urn2UraON | INT | IOD_STR_disk | I2273
STRUrnikiSC16Dan2Urn3UraON | INT | IOD_STR_disk | I2274
STRUrnikiSC16Dan2Urn1UraOFF | INT | IOD_STR_disk | I2275
STRUrnikiSC16Dan2Urn2UraOFF | INT | IOD_STR_disk | I2276
STRUrnikiSC16Dan2Urn3UraOFF | INT | IOD_STR_disk | I2277
STRUrnikiSC16Dan2Urn1MinON | INT | IOD_STR_disk | I2278
STRUrnikiSC16Dan2Urn2MinON | INT | IOD_STR_disk | I2279
STRUrnikiSC16Dan2Urn3MinON | INT | IOD_STR_disk | I2280
STRUrnikiSC16Dan2Urn1MinOFF | INT | IOD_STR_disk | I2281
STRUrnikiSC16Dan2Urn2MinOFF | INT | IOD_STR_disk | I2282
STRUrnikiSC16Dan2Urn3MinOFF | INT | IOD_STR_disk | I2283
STRUrnikiSC16Dan3Urn1UraON | INT | IOD_STR_disk | I2284
STRUrnikiSC16Dan3Urn2UraON | INT | IOD_STR_disk | I2285
STRUrnikiSC16Dan3Urn3UraON | INT | IOD_STR_disk | I2286
STRUrnikiSC16Dan3Urn1UraOFF | INT | IOD_STR_disk | I2287
STRUrnikiSC16Dan3Urn2UraOFF | INT | IOD_STR_disk | I2288
STRUrnikiSC16Dan3Urn3UraOFF | INT | IOD_STR_disk | I2289
STRUrnikiSC16Dan3Urn1MinON | INT | IOD_STR_disk | I2290
STRUrnikiSC16Dan3Urn2MinON | INT | IOD_STR_disk | I2291
STRUrnikiSC16Dan3Urn3MinON | INT | IOD_STR_disk | I2292
STRUrnikiSC16Dan3Urn1MinOFF | INT | IOD_STR_disk | I2293
STRUrnikiSC16Dan3Urn2MinOFF | INT | IOD_STR_disk | I2294
STRUrnikiSC16Dan3Urn3MinOFF | INT | IOD_STR_disk | I2295
STRUrnikiSC16Dan4Urn1UraON | INT | IOD_STR_disk | I2296
STRUrnikiSC16Dan4Urn2UraON | INT | IOD_STR_disk | I2297
STRUrnikiSC16Dan4Urn3UraON | INT | IOD_STR_disk | I2298
STRUrnikiSC16Dan4Urn1UraOFF | INT | IOD_STR_disk | I2299
STRUrnikiSC16Dan4Urn2UraOFF | INT | IOD_STR_disk | I2300
STRUrnikiSC16Dan4Urn3UraOFF | INT | IOD_STR_disk | I2301
STRUrnikiSC16Dan4Urn1MinON | INT | IOD_STR_disk | I2302
STRUrnikiSC16Dan4Urn2MinON | INT | IOD_STR_disk | I2303
STRUrnikiSC16Dan4Urn3MinON | INT | IOD_STR_disk | I2304
STRUrnikiSC16Dan4Urn1MinOFF | INT | IOD_STR_disk | I2305
STRUrnikiSC16Dan4Urn2MinOFF | INT | IOD_STR_disk | I2306
STRUrnikiSC16Dan4Urn3MinOFF | INT | IOD_STR_disk | I2307
STRUrnikiSC16Dan5Urn1UraON | INT | IOD_STR_disk | I2308
STRUrnikiSC16Dan5Urn2UraON | INT | IOD_STR_disk | I2309
STRUrnikiSC16Dan5Urn3UraON | INT | IOD_STR_disk | I2310
STRUrnikiSC16Dan5Urn1UraOFF | INT | IOD_STR_disk | I2311
STRUrnikiSC16Dan5Urn2UraOFF | INT | IOD_STR_disk | I2312
STRUrnikiSC16Dan5Urn3UraOFF | INT | IOD_STR_disk | I2313
STRUrnikiSC16Dan5Urn1MinON | INT | IOD_STR_disk | I2314
STRUrnikiSC16Dan5Urn2MinON | INT | IOD_STR_disk | I2315
STRUrnikiSC16Dan5Urn3MinON | INT | IOD_STR_disk | I2316
STRUrnikiSC16Dan5Urn1MinOFF | INT | IOD_STR_disk | I2317
STRUrnikiSC16Dan5Urn2MinOFF | INT | IOD_STR_disk | I2318
STRUrnikiSC16Dan5Urn3MinOFF | INT | IOD_STR_disk | I2319
STRUrnikiSC16Dan6Urn1UraON | INT | IOD_STR_disk | I2320
STRUrnikiSC16Dan6Urn2UraON | INT | IOD_STR_disk | I2321
STRUrnikiSC16Dan6Urn3UraON | INT | IOD_STR_disk | I2322
STRUrnikiSC16Dan6Urn1UraOFF | INT | IOD_STR_disk | I2323
STRUrnikiSC16Dan6Urn2UraOFF | INT | IOD_STR_disk | I2324
STRUrnikiSC16Dan6Urn3UraOFF | INT | IOD_STR_disk | I2325
STRUrnikiSC16Dan6Urn1MinON | INT | IOD_STR_disk | I2326
STRUrnikiSC16Dan6Urn2MinON | INT | IOD_STR_disk | I2327
STRUrnikiSC16Dan6Urn3MinON | INT | IOD_STR_disk | I2328
STRUrnikiSC16Dan6Urn1MinOFF | INT | IOD_STR_disk | I2329
STRUrnikiSC16Dan6Urn2MinOFF | INT | IOD_STR_disk | I2330
STRUrnikiSC16Dan6Urn3MinOFF | INT | IOD_STR_disk | I2331
STRUrnikiSC16Dan7Urn1UraON | INT | IOD_STR_disk | I2332
STRUrnikiSC16Dan7Urn2UraON | INT | IOD_STR_disk | I2333
STRUrnikiSC16Dan7Urn3UraON | INT | IOD_STR_disk | I2334
STRUrnikiSC16Dan7Urn1UraOFF | INT | IOD_STR_disk | I2335
STRUrnikiSC16Dan7Urn2UraOFF | INT | IOD_STR_disk | I2336
STRUrnikiSC16Dan7Urn3UraOFF | INT | IOD_STR_disk | I2337
STRUrnikiSC16Dan7Urn1MinON | INT | IOD_STR_disk | I2338
STRUrnikiSC16Dan7Urn2MinON | INT | IOD_STR_disk | I2339
STRUrnikiSC16Dan7Urn3MinON | INT | IOD_STR_disk | I2340
STRUrnikiSC16Dan7Urn1MinOFF | INT | IOD_STR_disk | I2341
STRUrnikiSC16Dan7Urn2MinOFF | INT | IOD_STR_disk | I2342
STRUrnikiSC16Dan7Urn3MinOFF | INT | IOD_STR_disk | I2343
STRUrnikiSC17Dan1Urn1UraON | INT | IOD_STR_disk | I2344
STRUrnikiSC17Dan1Urn2UraON | INT | IOD_STR_disk | I2345
STRUrnikiSC17Dan1Urn3UraON | INT | IOD_STR_disk | I2346
STRUrnikiSC17Dan1Urn1UraOFF | INT | IOD_STR_disk | I2347
STRUrnikiSC17Dan1Urn2UraOFF | INT | IOD_STR_disk | I2348
STRUrnikiSC17Dan1Urn3UraOFF | INT | IOD_STR_disk | I2349
STRUrnikiSC17Dan1Urn1MinON | INT | IOD_STR_disk | I2350
STRUrnikiSC17Dan1Urn2MinON | INT | IOD_STR_disk | I2351
STRUrnikiSC17Dan1Urn3MinON | INT | IOD_STR_disk | I2352
STRUrnikiSC17Dan1Urn1MinOFF | INT | IOD_STR_disk | I2353
STRUrnikiSC17Dan1Urn2MinOFF | INT | IOD_STR_disk | I2354
STRUrnikiSC17Dan1Urn3MinOFF | INT | IOD_STR_disk | I2355
STRUrnikiSC17Dan2Urn1UraON | INT | IOD_STR_disk | I2356
STRUrnikiSC17Dan2Urn2UraON | INT | IOD_STR_disk | I2357
STRUrnikiSC17Dan2Urn3UraON | INT | IOD_STR_disk | I2358
STRUrnikiSC17Dan2Urn1UraOFF | INT | IOD_STR_disk | I2359
STRUrnikiSC17Dan2Urn2UraOFF | INT | IOD_STR_disk | I2360
STRUrnikiSC17Dan2Urn3UraOFF | INT | IOD_STR_disk | I2361
STRUrnikiSC17Dan2Urn1MinON | INT | IOD_STR_disk | I2362
STRUrnikiSC17Dan2Urn2MinON | INT | IOD_STR_disk | I2363
STRUrnikiSC17Dan2Urn3MinON | INT | IOD_STR_disk | I2364
STRUrnikiSC17Dan2Urn1MinOFF | INT | IOD_STR_disk | I2365
STRUrnikiSC17Dan2Urn2MinOFF | INT | IOD_STR_disk | I2366
STRUrnikiSC17Dan2Urn3MinOFF | INT | IOD_STR_disk | I2367
STRUrnikiSC17Dan3Urn1UraON | INT | IOD_STR_disk | I2368
STRUrnikiSC17Dan3Urn2UraON | INT | IOD_STR_disk | I2369
STRUrnikiSC17Dan3Urn3UraON | INT | IOD_STR_disk | I2370
STRUrnikiSC17Dan3Urn1UraOFF | INT | IOD_STR_disk | I2371
STRUrnikiSC17Dan3Urn2UraOFF | INT | IOD_STR_disk | I2372
STRUrnikiSC17Dan3Urn3UraOFF | INT | IOD_STR_disk | I2373
STRUrnikiSC17Dan3Urn1MinON | INT | IOD_STR_disk | I2374
STRUrnikiSC17Dan3Urn2MinON | INT | IOD_STR_disk | I2375
STRUrnikiSC17Dan3Urn3MinON | INT | IOD_STR_disk | I2376
STRUrnikiSC17Dan3Urn1MinOFF | INT | IOD_STR_disk | I2377
STRUrnikiSC17Dan3Urn2MinOFF | INT | IOD_STR_disk | I2378
STRUrnikiSC17Dan3Urn3MinOFF | INT | IOD_STR_disk | I2379
STRUrnikiSC17Dan4Urn1UraON | INT | IOD_STR_disk | I2380
STRUrnikiSC17Dan4Urn2UraON | INT | IOD_STR_disk | I2381
STRUrnikiSC17Dan4Urn3UraON | INT | IOD_STR_disk | I2382
STRUrnikiSC17Dan4Urn1UraOFF | INT | IOD_STR_disk | I2383
STRUrnikiSC17Dan4Urn2UraOFF | INT | IOD_STR_disk | I2384
STRUrnikiSC17Dan4Urn3UraOFF | INT | IOD_STR_disk | I2385
STRUrnikiSC17Dan4Urn1MinON | INT | IOD_STR_disk | I2386
STRUrnikiSC17Dan4Urn2MinON | INT | IOD_STR_disk | I2387
STRUrnikiSC17Dan4Urn3MinON | INT | IOD_STR_disk | I2388
STRUrnikiSC17Dan4Urn1MinOFF | INT | IOD_STR_disk | I2389
STRUrnikiSC17Dan4Urn2MinOFF | INT | IOD_STR_disk | I2390
STRUrnikiSC17Dan4Urn3MinOFF | INT | IOD_STR_disk | I2391
STRUrnikiSC17Dan5Urn1UraON | INT | IOD_STR_disk | I2392
STRUrnikiSC17Dan5Urn2UraON | INT | IOD_STR_disk | I2393
STRUrnikiSC17Dan5Urn3UraON | INT | IOD_STR_disk | I2394
STRUrnikiSC17Dan5Urn1UraOFF | INT | IOD_STR_disk | I2395
STRUrnikiSC17Dan5Urn2UraOFF | INT | IOD_STR_disk | I2396
STRUrnikiSC17Dan5Urn3UraOFF | INT | IOD_STR_disk | I2397
STRUrnikiSC17Dan5Urn1MinON | INT | IOD_STR_disk | I2398
STRUrnikiSC17Dan5Urn2MinON | INT | IOD_STR_disk | I2399
STRUrnikiSC17Dan5Urn3MinON | INT | IOD_STR_disk | I2400
STRUrnikiSC17Dan5Urn1MinOFF | INT | IOD_STR_disk | I2401
STRUrnikiSC17Dan5Urn2MinOFF | INT | IOD_STR_disk | I2402
STRUrnikiSC17Dan5Urn3MinOFF | INT | IOD_STR_disk | I2403
STRUrnikiSC17Dan6Urn1UraON | INT | IOD_STR_disk | I2404
STRUrnikiSC17Dan6Urn2UraON | INT | IOD_STR_disk | I2405
STRUrnikiSC17Dan6Urn3UraON | INT | IOD_STR_disk | I2406
STRUrnikiSC17Dan6Urn1UraOFF | INT | IOD_STR_disk | I2407
STRUrnikiSC17Dan6Urn2UraOFF | INT | IOD_STR_disk | I2408
STRUrnikiSC17Dan6Urn3UraOFF | INT | IOD_STR_disk | I2409
STRUrnikiSC17Dan6Urn1MinON | INT | IOD_STR_disk | I2410
STRUrnikiSC17Dan6Urn2MinON | INT | IOD_STR_disk | I2411
STRUrnikiSC17Dan6Urn3MinON | INT | IOD_STR_disk | I2412
STRUrnikiSC17Dan6Urn1MinOFF | INT | IOD_STR_disk | I2413
STRUrnikiSC17Dan6Urn2MinOFF | INT | IOD_STR_disk | I2414
STRUrnikiSC17Dan6Urn3MinOFF | INT | IOD_STR_disk | I2415
STRUrnikiSC17Dan7Urn1UraON | INT | IOD_STR_disk | I2416
STRUrnikiSC17Dan7Urn2UraON | INT | IOD_STR_disk | I2417
STRUrnikiSC17Dan7Urn3UraON | INT | IOD_STR_disk | I2418
STRUrnikiSC17Dan7Urn1UraOFF | INT | IOD_STR_disk | I2419
STRUrnikiSC17Dan7Urn2UraOFF | INT | IOD_STR_disk | I2420
STRUrnikiSC17Dan7Urn3UraOFF | INT | IOD_STR_disk | I2421
STRUrnikiSC17Dan7Urn1MinON | INT | IOD_STR_disk | I2422
STRUrnikiSC17Dan7Urn2MinON | INT | IOD_STR_disk | I2423
STRUrnikiSC17Dan7Urn3MinON | INT | IOD_STR_disk | I2424
STRUrnikiSC17Dan7Urn1MinOFF | INT | IOD_STR_disk | I2425
STRUrnikiSC17Dan7Urn2MinOFF | INT | IOD_STR_disk | I2426
STRUrnikiSC17Dan7Urn3MinOFF | INT | IOD_STR_disk | I2427
STRUrnikiSC18Dan1Urn1UraON | INT | IOD_STR_disk | I2428
STRUrnikiSC18Dan1Urn2UraON | INT | IOD_STR_disk | I2429
STRUrnikiSC18Dan1Urn3UraON | INT | IOD_STR_disk | I2430
STRUrnikiSC18Dan1Urn1UraOFF | INT | IOD_STR_disk | I2431
STRUrnikiSC18Dan1Urn2UraOFF | INT | IOD_STR_disk | I2432
STRUrnikiSC18Dan1Urn3UraOFF | INT | IOD_STR_disk | I2433
STRUrnikiSC18Dan1Urn1MinON | INT | IOD_STR_disk | I2434
STRUrnikiSC18Dan1Urn2MinON | INT | IOD_STR_disk | I2435
STRUrnikiSC18Dan1Urn3MinON | INT | IOD_STR_disk | I2436
STRUrnikiSC18Dan1Urn1MinOFF | INT | IOD_STR_disk | I2437
STRUrnikiSC18Dan1Urn2MinOFF | INT | IOD_STR_disk | I2438
STRUrnikiSC18Dan1Urn3MinOFF | INT | IOD_STR_disk | I2439
STRUrnikiSC18Dan2Urn1UraON | INT | IOD_STR_disk | I2440
STRUrnikiSC18Dan2Urn2UraON | INT | IOD_STR_disk | I2441
STRUrnikiSC18Dan2Urn3UraON | INT | IOD_STR_disk | I2442
STRUrnikiSC18Dan2Urn1UraOFF | INT | IOD_STR_disk | I2443
STRUrnikiSC18Dan2Urn2UraOFF | INT | IOD_STR_disk | I2444
STRUrnikiSC18Dan2Urn3UraOFF | INT | IOD_STR_disk | I2445
STRUrnikiSC18Dan2Urn1MinON | INT | IOD_STR_disk | I2446
STRUrnikiSC18Dan2Urn2MinON | INT | IOD_STR_disk | I2447
STRUrnikiSC18Dan2Urn3MinON | INT | IOD_STR_disk | I2448
STRUrnikiSC18Dan2Urn1MinOFF | INT | IOD_STR_disk | I2449
STRUrnikiSC18Dan2Urn2MinOFF | INT | IOD_STR_disk | I2450
STRUrnikiSC18Dan2Urn3MinOFF | INT | IOD_STR_disk | I2451
STRUrnikiSC18Dan3Urn1UraON | INT | IOD_STR_disk | I2452
STRUrnikiSC18Dan3Urn2UraON | INT | IOD_STR_disk | I2453
STRUrnikiSC18Dan3Urn3UraON | INT | IOD_STR_disk | I2454
STRUrnikiSC18Dan3Urn1UraOFF | INT | IOD_STR_disk | I2455
STRUrnikiSC18Dan3Urn2UraOFF | INT | IOD_STR_disk | I2456
STRUrnikiSC18Dan3Urn3UraOFF | INT | IOD_STR_disk | I2457
STRUrnikiSC18Dan3Urn1MinON | INT | IOD_STR_disk | I2458
STRUrnikiSC18Dan3Urn2MinON | INT | IOD_STR_disk | I2459
STRUrnikiSC18Dan3Urn3MinON | INT | IOD_STR_disk | I2460
STRUrnikiSC18Dan3Urn1MinOFF | INT | IOD_STR_disk | I2461
STRUrnikiSC18Dan3Urn2MinOFF | INT | IOD_STR_disk | I2462
STRUrnikiSC18Dan3Urn3MinOFF | INT | IOD_STR_disk | I2463
STRUrnikiSC18Dan4Urn1UraON | INT | IOD_STR_disk | I2464
STRUrnikiSC18Dan4Urn2UraON | INT | IOD_STR_disk | I2465
STRUrnikiSC18Dan4Urn3UraON | INT | IOD_STR_disk | I2466
STRUrnikiSC18Dan4Urn1UraOFF | INT | IOD_STR_disk | I2467
STRUrnikiSC18Dan4Urn2UraOFF | INT | IOD_STR_disk | I2468
STRUrnikiSC18Dan4Urn3UraOFF | INT | IOD_STR_disk | I2469
STRUrnikiSC18Dan4Urn1MinON | INT | IOD_STR_disk | I2470
STRUrnikiSC18Dan4Urn2MinON | INT | IOD_STR_disk | I2471
STRUrnikiSC18Dan4Urn3MinON | INT | IOD_STR_disk | I2472
STRUrnikiSC18Dan4Urn1MinOFF | INT | IOD_STR_disk | I2473
STRUrnikiSC18Dan4Urn2MinOFF | INT | IOD_STR_disk | I2474
STRUrnikiSC18Dan4Urn3MinOFF | INT | IOD_STR_disk | I2475
STRUrnikiSC18Dan5Urn1UraON | INT | IOD_STR_disk | I2476
STRUrnikiSC18Dan5Urn2UraON | INT | IOD_STR_disk | I2477
STRUrnikiSC18Dan5Urn3UraON | INT | IOD_STR_disk | I2478
STRUrnikiSC18Dan5Urn1UraOFF | INT | IOD_STR_disk | I2479
STRUrnikiSC18Dan5Urn2UraOFF | INT | IOD_STR_disk | I2480
STRUrnikiSC18Dan5Urn3UraOFF | INT | IOD_STR_disk | I2481
STRUrnikiSC18Dan5Urn1MinON | INT | IOD_STR_disk | I2482
STRUrnikiSC18Dan5Urn2MinON | INT | IOD_STR_disk | I2483
STRUrnikiSC18Dan5Urn3MinON | INT | IOD_STR_disk | I2484
STRUrnikiSC18Dan5Urn1MinOFF | INT | IOD_STR_disk | I2485
STRUrnikiSC18Dan5Urn2MinOFF | INT | IOD_STR_disk | I2486
STRUrnikiSC18Dan5Urn3MinOFF | INT | IOD_STR_disk | I2487
STRUrnikiSC18Dan6Urn1UraON | INT | IOD_STR_disk | I2488
STRUrnikiSC18Dan6Urn2UraON | INT | IOD_STR_disk | I2489
STRUrnikiSC18Dan6Urn3UraON | INT | IOD_STR_disk | I2490
STRUrnikiSC18Dan6Urn1UraOFF | INT | IOD_STR_disk | I2491
STRUrnikiSC18Dan6Urn2UraOFF | INT | IOD_STR_disk | I2492
STRUrnikiSC18Dan6Urn3UraOFF | INT | IOD_STR_disk | I2493
STRUrnikiSC18Dan6Urn1MinON | INT | IOD_STR_disk | I2494
STRUrnikiSC18Dan6Urn2MinON | INT | IOD_STR_disk | I2495
STRUrnikiSC18Dan6Urn3MinON | INT | IOD_STR_disk | I2496
STRUrnikiSC18Dan6Urn1MinOFF | INT | IOD_STR_disk | I2497
STRUrnikiSC18Dan6Urn2MinOFF | INT | IOD_STR_disk | I2498
STRUrnikiSC18Dan6Urn3MinOFF | INT | IOD_STR_disk | I2499
STRUrnikiSC18Dan7Urn1UraON | INT | IOD_STR_disk | I2500
STRUrnikiSC18Dan7Urn2UraON | INT | IOD_STR_disk | I2501
STRUrnikiSC18Dan7Urn3UraON | INT | IOD_STR_disk | I2502
STRUrnikiSC18Dan7Urn1UraOFF | INT | IOD_STR_disk | I2503
STRUrnikiSC18Dan7Urn2UraOFF | INT | IOD_STR_disk | I2504
STRUrnikiSC18Dan7Urn3UraOFF | INT | IOD_STR_disk | I2505
STRUrnikiSC18Dan7Urn1MinON | INT | IOD_STR_disk | I2506
STRUrnikiSC18Dan7Urn2MinON | INT | IOD_STR_disk | I2507
STRUrnikiSC18Dan7Urn3MinON | INT | IOD_STR_disk | I2508
STRUrnikiSC18Dan7Urn1MinOFF | INT | IOD_STR_disk | I2509
STRUrnikiSC18Dan7Urn2MinOFF | INT | IOD_STR_disk | I2510
STRUrnikiSC18Dan7Urn3MinOFF | INT | IOD_STR_disk | I2511
STRUrnikiSC19Dan1Urn1UraON | INT | IOD_STR_disk | I2512
STRUrnikiSC19Dan1Urn2UraON | INT | IOD_STR_disk | I2513
STRUrnikiSC19Dan1Urn3UraON | INT | IOD_STR_disk | I2514
STRUrnikiSC19Dan1Urn1UraOFF | INT | IOD_STR_disk | I2515
STRUrnikiSC19Dan1Urn2UraOFF | INT | IOD_STR_disk | I2516
STRUrnikiSC19Dan1Urn3UraOFF | INT | IOD_STR_disk | I2517
STRUrnikiSC19Dan1Urn1MinON | INT | IOD_STR_disk | I2518
STRUrnikiSC19Dan1Urn2MinON | INT | IOD_STR_disk | I2519
STRUrnikiSC19Dan1Urn3MinON | INT | IOD_STR_disk | I2520
STRUrnikiSC19Dan1Urn1MinOFF | INT | IOD_STR_disk | I2521
STRUrnikiSC19Dan1Urn2MinOFF | INT | IOD_STR_disk | I2522
STRUrnikiSC19Dan1Urn3MinOFF | INT | IOD_STR_disk | I2523
STRUrnikiSC19Dan2Urn1UraON | INT | IOD_STR_disk | I2524
STRUrnikiSC19Dan2Urn2UraON | INT | IOD_STR_disk | I2525
STRUrnikiSC19Dan2Urn3UraON | INT | IOD_STR_disk | I2526
STRUrnikiSC19Dan2Urn1UraOFF | INT | IOD_STR_disk | I2527
STRUrnikiSC19Dan2Urn2UraOFF | INT | IOD_STR_disk | I2528
STRUrnikiSC19Dan2Urn3UraOFF | INT | IOD_STR_disk | I2529
STRUrnikiSC19Dan2Urn1MinON | INT | IOD_STR_disk | I2530
STRUrnikiSC19Dan2Urn2MinON | INT | IOD_STR_disk | I2531
STRUrnikiSC19Dan2Urn3MinON | INT | IOD_STR_disk | I2532
STRUrnikiSC19Dan2Urn1MinOFF | INT | IOD_STR_disk | I2533
STRUrnikiSC19Dan2Urn2MinOFF | INT | IOD_STR_disk | I2534
STRUrnikiSC19Dan2Urn3MinOFF | INT | IOD_STR_disk | I2535
STRUrnikiSC19Dan3Urn1UraON | INT | IOD_STR_disk | I2536
STRUrnikiSC19Dan3Urn2UraON | INT | IOD_STR_disk | I2537
STRUrnikiSC19Dan3Urn3UraON | INT | IOD_STR_disk | I2538
STRUrnikiSC19Dan3Urn1UraOFF | INT | IOD_STR_disk | I2539
STRUrnikiSC19Dan3Urn2UraOFF | INT | IOD_STR_disk | I2540
STRUrnikiSC19Dan3Urn3UraOFF | INT | IOD_STR_disk | I2541
STRUrnikiSC19Dan3Urn1MinON | INT | IOD_STR_disk | I2542
STRUrnikiSC19Dan3Urn2MinON | INT | IOD_STR_disk | I2543
STRUrnikiSC19Dan3Urn3MinON | INT | IOD_STR_disk | I2544
STRUrnikiSC19Dan3Urn1MinOFF | INT | IOD_STR_disk | I2545
STRUrnikiSC19Dan3Urn2MinOFF | INT | IOD_STR_disk | I2546
STRUrnikiSC19Dan3Urn3MinOFF | INT | IOD_STR_disk | I2547
STRUrnikiSC19Dan4Urn1UraON | INT | IOD_STR_disk | I2548
STRUrnikiSC19Dan4Urn2UraON | INT | IOD_STR_disk | I2549
STRUrnikiSC19Dan4Urn3UraON | INT | IOD_STR_disk | I2550
STRUrnikiSC19Dan4Urn1UraOFF | INT | IOD_STR_disk | I2551
STRUrnikiSC19Dan4Urn2UraOFF | INT | IOD_STR_disk | I2552
STRUrnikiSC19Dan4Urn3UraOFF | INT | IOD_STR_disk | I2553
STRUrnikiSC19Dan4Urn1MinON | INT | IOD_STR_disk | I2554
STRUrnikiSC19Dan4Urn2MinON | INT | IOD_STR_disk | I2555
STRUrnikiSC19Dan4Urn3MinON | INT | IOD_STR_disk | I2556
STRUrnikiSC19Dan4Urn1MinOFF | INT | IOD_STR_disk | I2557
STRUrnikiSC19Dan4Urn2MinOFF | INT | IOD_STR_disk | I2558
STRUrnikiSC19Dan4Urn3MinOFF | INT | IOD_STR_disk | I2559
STRUrnikiSC19Dan5Urn1UraON | INT | IOD_STR_disk | I2560
STRUrnikiSC19Dan5Urn2UraON | INT | IOD_STR_disk | I2561
STRUrnikiSC19Dan5Urn3UraON | INT | IOD_STR_disk | I2562
STRUrnikiSC19Dan5Urn1UraOFF | INT | IOD_STR_disk | I2563
STRUrnikiSC19Dan5Urn2UraOFF | INT | IOD_STR_disk | I2564
STRUrnikiSC19Dan5Urn3UraOFF | INT | IOD_STR_disk | I2565
STRUrnikiSC19Dan5Urn1MinON | INT | IOD_STR_disk | I2566
STRUrnikiSC19Dan5Urn2MinON | INT | IOD_STR_disk | I2567
STRUrnikiSC19Dan5Urn3MinON | INT | IOD_STR_disk | I2568
STRUrnikiSC19Dan5Urn1MinOFF | INT | IOD_STR_disk | I2569
STRUrnikiSC19Dan5Urn2MinOFF | INT | IOD_STR_disk | I2570
STRUrnikiSC19Dan5Urn3MinOFF | INT | IOD_STR_disk | I2571
STRUrnikiSC19Dan6Urn1UraON | INT | IOD_STR_disk | I2572
STRUrnikiSC19Dan6Urn2UraON | INT | IOD_STR_disk | I2573
STRUrnikiSC19Dan6Urn3UraON | INT | IOD_STR_disk | I2574
STRUrnikiSC19Dan6Urn1UraOFF | INT | IOD_STR_disk | I2575
STRUrnikiSC19Dan6Urn2UraOFF | INT | IOD_STR_disk | I2576
STRUrnikiSC19Dan6Urn3UraOFF | INT | IOD_STR_disk | I2577
STRUrnikiSC19Dan6Urn1MinON | INT | IOD_STR_disk | I2578
STRUrnikiSC19Dan6Urn2MinON | INT | IOD_STR_disk | I2579
STRUrnikiSC19Dan6Urn3MinON | INT | IOD_STR_disk | I2580
STRUrnikiSC19Dan6Urn1MinOFF | INT | IOD_STR_disk | I2581
STRUrnikiSC19Dan6Urn2MinOFF | INT | IOD_STR_disk | I2582
STRUrnikiSC19Dan6Urn3MinOFF | INT | IOD_STR_disk | I2583
STRUrnikiSC19Dan7Urn1UraON | INT | IOD_STR_disk | I2584
STRUrnikiSC19Dan7Urn2UraON | INT | IOD_STR_disk | I2585
STRUrnikiSC19Dan7Urn3UraON | INT | IOD_STR_disk | I2586
STRUrnikiSC19Dan7Urn1UraOFF | INT | IOD_STR_disk | I2587
STRUrnikiSC19Dan7Urn2UraOFF | INT | IOD_STR_disk | I2588
STRUrnikiSC19Dan7Urn3UraOFF | INT | IOD_STR_disk | I2589
STRUrnikiSC19Dan7Urn1MinON | INT | IOD_STR_disk | I2590
STRUrnikiSC19Dan7Urn2MinON | INT | IOD_STR_disk | I2591
STRUrnikiSC19Dan7Urn3MinON | INT | IOD_STR_disk | I2592
STRUrnikiSC19Dan7Urn1MinOFF | INT | IOD_STR_disk | I2593
STRUrnikiSC19Dan7Urn2MinOFF | INT | IOD_STR_disk | I2594
STRUrnikiSC19Dan7Urn3MinOFF | INT | IOD_STR_disk | I2595
STRUrnikiSC20Dan1Urn1UraON | INT | IOD_STR_disk | I2596
STRUrnikiSC20Dan1Urn2UraON | INT | IOD_STR_disk | I2597
STRUrnikiSC20Dan1Urn3UraON | INT | IOD_STR_disk | I2598
STRUrnikiSC20Dan1Urn1UraOFF | INT | IOD_STR_disk | I2599
STRUrnikiSC20Dan1Urn2UraOFF | INT | IOD_STR_disk | I2600
STRUrnikiSC20Dan1Urn3UraOFF | INT | IOD_STR_disk | I2601
STRUrnikiSC20Dan1Urn1MinON | INT | IOD_STR_disk | I2602
STRUrnikiSC20Dan1Urn2MinON | INT | IOD_STR_disk | I2603
STRUrnikiSC20Dan1Urn3MinON | INT | IOD_STR_disk | I2604
STRUrnikiSC20Dan1Urn1MinOFF | INT | IOD_STR_disk | I2605
STRUrnikiSC20Dan1Urn2MinOFF | INT | IOD_STR_disk | I2606
STRUrnikiSC20Dan1Urn3MinOFF | INT | IOD_STR_disk | I2607
STRUrnikiSC20Dan2Urn1UraON | INT | IOD_STR_disk | I2608
STRUrnikiSC20Dan2Urn2UraON | INT | IOD_STR_disk | I2609
STRUrnikiSC20Dan2Urn3UraON | INT | IOD_STR_disk | I2610
STRUrnikiSC20Dan2Urn1UraOFF | INT | IOD_STR_disk | I2611
STRUrnikiSC20Dan2Urn2UraOFF | INT | IOD_STR_disk | I2612
STRUrnikiSC20Dan2Urn3UraOFF | INT | IOD_STR_disk | I2613
STRUrnikiSC20Dan2Urn1MinON | INT | IOD_STR_disk | I2614
STRUrnikiSC20Dan2Urn2MinON | INT | IOD_STR_disk | I2615
STRUrnikiSC20Dan2Urn3MinON | INT | IOD_STR_disk | I2616
STRUrnikiSC20Dan2Urn1MinOFF | INT | IOD_STR_disk | I2617
STRUrnikiSC20Dan2Urn2MinOFF | INT | IOD_STR_disk | I2618
STRUrnikiSC20Dan2Urn3MinOFF | INT | IOD_STR_disk | I2619
STRUrnikiSC20Dan3Urn1UraON | INT | IOD_STR_disk | I2620
STRUrnikiSC20Dan3Urn2UraON | INT | IOD_STR_disk | I2621
STRUrnikiSC20Dan3Urn3UraON | INT | IOD_STR_disk | I2622
STRUrnikiSC20Dan3Urn1UraOFF | INT | IOD_STR_disk | I2623
STRUrnikiSC20Dan3Urn2UraOFF | INT | IOD_STR_disk | I2624
STRUrnikiSC20Dan3Urn3UraOFF | INT | IOD_STR_disk | I2625
STRUrnikiSC20Dan3Urn1MinON | INT | IOD_STR_disk | I2626
STRUrnikiSC20Dan3Urn2MinON | INT | IOD_STR_disk | I2627
STRUrnikiSC20Dan3Urn3MinON | INT | IOD_STR_disk | I2628
STRUrnikiSC20Dan3Urn1MinOFF | INT | IOD_STR_disk | I2629
STRUrnikiSC20Dan3Urn2MinOFF | INT | IOD_STR_disk | I2630
STRUrnikiSC20Dan3Urn3MinOFF | INT | IOD_STR_disk | I2631
STRUrnikiSC20Dan4Urn1UraON | INT | IOD_STR_disk | I2632
STRUrnikiSC20Dan4Urn2UraON | INT | IOD_STR_disk | I2633
STRUrnikiSC20Dan4Urn3UraON | INT | IOD_STR_disk | I2634
STRUrnikiSC20Dan4Urn1UraOFF | INT | IOD_STR_disk | I2635
STRUrnikiSC20Dan4Urn2UraOFF | INT | IOD_STR_disk | I2636
STRUrnikiSC20Dan4Urn3UraOFF | INT | IOD_STR_disk | I2637
STRUrnikiSC20Dan4Urn1MinON | INT | IOD_STR_disk | I2638
STRUrnikiSC20Dan4Urn2MinON | INT | IOD_STR_disk | I2639
STRUrnikiSC20Dan4Urn3MinON | INT | IOD_STR_disk | I2640
STRUrnikiSC20Dan4Urn1MinOFF | INT | IOD_STR_disk | I2641
STRUrnikiSC20Dan4Urn2MinOFF | INT | IOD_STR_disk | I2642
STRUrnikiSC20Dan4Urn3MinOFF | INT | IOD_STR_disk | I2643
STRUrnikiSC20Dan5Urn1UraON | INT | IOD_STR_disk | I2644
STRUrnikiSC20Dan5Urn2UraON | INT | IOD_STR_disk | I2645
STRUrnikiSC20Dan5Urn3UraON | INT | IOD_STR_disk | I2646
STRUrnikiSC20Dan5Urn1UraOFF | INT | IOD_STR_disk | I2647
STRUrnikiSC20Dan5Urn2UraOFF | INT | IOD_STR_disk | I2648
STRUrnikiSC20Dan5Urn3UraOFF | INT | IOD_STR_disk | I2649
STRUrnikiSC20Dan5Urn1MinON | INT | IOD_STR_disk | I2650
STRUrnikiSC20Dan5Urn2MinON | INT | IOD_STR_disk | I2651
STRUrnikiSC20Dan5Urn3MinON | INT | IOD_STR_disk | I2652
STRUrnikiSC20Dan5Urn1MinOFF | INT | IOD_STR_disk | I2653
STRUrnikiSC20Dan5Urn2MinOFF | INT | IOD_STR_disk | I2654
STRUrnikiSC20Dan5Urn3MinOFF | INT | IOD_STR_disk | I2655
STRUrnikiSC20Dan6Urn1UraON | INT | IOD_STR_disk | I2656
STRUrnikiSC20Dan6Urn2UraON | INT | IOD_STR_disk | I2657
STRUrnikiSC20Dan6Urn3UraON | INT | IOD_STR_disk | I2658
STRUrnikiSC20Dan6Urn1UraOFF | INT | IOD_STR_disk | I2659
STRUrnikiSC20Dan6Urn2UraOFF | INT | IOD_STR_disk | I2660
STRUrnikiSC20Dan6Urn3UraOFF | INT | IOD_STR_disk | I2661
STRUrnikiSC20Dan6Urn1MinON | INT | IOD_STR_disk | I2662
STRUrnikiSC20Dan6Urn2MinON | INT | IOD_STR_disk | I2663
STRUrnikiSC20Dan6Urn3MinON | INT | IOD_STR_disk | I2664
STRUrnikiSC20Dan6Urn1MinOFF | INT | IOD_STR_disk | I2665
STRUrnikiSC20Dan6Urn2MinOFF | INT | IOD_STR_disk | I2666
STRUrnikiSC20Dan6Urn3MinOFF | INT | IOD_STR_disk | I2667
STRUrnikiSC20Dan7Urn1UraON | INT | IOD_STR_disk | I2668
STRUrnikiSC20Dan7Urn2UraON | INT | IOD_STR_disk | I2669
STRUrnikiSC20Dan7Urn3UraON | INT | IOD_STR_disk | I2670
STRUrnikiSC20Dan7Urn1UraOFF | INT | IOD_STR_disk | I2671
STRUrnikiSC20Dan7Urn2UraOFF | INT | IOD_STR_disk | I2672
STRUrnikiSC20Dan7Urn3UraOFF | INT | IOD_STR_disk | I2673
STRUrnikiSC20Dan7Urn1MinON | INT | IOD_STR_disk | I2674
STRUrnikiSC20Dan7Urn2MinON | INT | IOD_STR_disk | I2675
STRUrnikiSC20Dan7Urn3MinON | INT | IOD_STR_disk | I2676
STRUrnikiSC20Dan7Urn1MinOFF | INT | IOD_STR_disk | I2677
STRUrnikiSC20Dan7Urn2MinOFF | INT | IOD_STR_disk | I2678
STRUrnikiSC20Dan7Urn3MinOFF | INT | IOD_STR_disk | I2679
STRUrnikiSC21Dan1Urn1UraON | INT | IOD_STR_disk | I2680
STRUrnikiSC21Dan1Urn2UraON | INT | IOD_STR_disk | I2681
STRUrnikiSC21Dan1Urn3UraON | INT | IOD_STR_disk | I2682
STRUrnikiSC21Dan1Urn1UraOFF | INT | IOD_STR_disk | I2683
STRUrnikiSC21Dan1Urn2UraOFF | INT | IOD_STR_disk | I2684
STRUrnikiSC21Dan1Urn3UraOFF | INT | IOD_STR_disk | I2685
STRUrnikiSC21Dan1Urn1MinON | INT | IOD_STR_disk | I2686
STRUrnikiSC21Dan1Urn2MinON | INT | IOD_STR_disk | I2687
STRUrnikiSC21Dan1Urn3MinON | INT | IOD_STR_disk | I2688
STRUrnikiSC21Dan1Urn1MinOFF | INT | IOD_STR_disk | I2689
STRUrnikiSC21Dan1Urn2MinOFF | INT | IOD_STR_disk | I2690
STRUrnikiSC21Dan1Urn3MinOFF | INT | IOD_STR_disk | I2691
STRUrnikiSC21Dan2Urn1UraON | INT | IOD_STR_disk | I2692
STRUrnikiSC21Dan2Urn2UraON | INT | IOD_STR_disk | I2693
STRUrnikiSC21Dan2Urn3UraON | INT | IOD_STR_disk | I2694
STRUrnikiSC21Dan2Urn1UraOFF | INT | IOD_STR_disk | I2695
STRUrnikiSC21Dan2Urn2UraOFF | INT | IOD_STR_disk | I2696
STRUrnikiSC21Dan2Urn3UraOFF | INT | IOD_STR_disk | I2697
STRUrnikiSC21Dan2Urn1MinON | INT | IOD_STR_disk | I2698
STRUrnikiSC21Dan2Urn2MinON | INT | IOD_STR_disk | I2699
STRUrnikiSC21Dan2Urn3MinON | INT | IOD_STR_disk | I2700
STRUrnikiSC21Dan2Urn1MinOFF | INT | IOD_STR_disk | I2701
STRUrnikiSC21Dan2Urn2MinOFF | INT | IOD_STR_disk | I2702
STRUrnikiSC21Dan2Urn3MinOFF | INT | IOD_STR_disk | I2703
STRUrnikiSC21Dan3Urn1UraON | INT | IOD_STR_disk | I2704
STRUrnikiSC21Dan3Urn2UraON | INT | IOD_STR_disk | I2705
STRUrnikiSC21Dan3Urn3UraON | INT | IOD_STR_disk | I2706
STRUrnikiSC21Dan3Urn1UraOFF | INT | IOD_STR_disk | I2707
STRUrnikiSC21Dan3Urn2UraOFF | INT | IOD_STR_disk | I2708
STRUrnikiSC21Dan3Urn3UraOFF | INT | IOD_STR_disk | I2709
STRUrnikiSC21Dan3Urn1MinON | INT | IOD_STR_disk | I2710
STRUrnikiSC21Dan3Urn2MinON | INT | IOD_STR_disk | I2711
STRUrnikiSC21Dan3Urn3MinON | INT | IOD_STR_disk | I2712
STRUrnikiSC21Dan3Urn1MinOFF | INT | IOD_STR_disk | I2713
STRUrnikiSC21Dan3Urn2MinOFF | INT | IOD_STR_disk | I2714
STRUrnikiSC21Dan3Urn3MinOFF | INT | IOD_STR_disk | I2715
STRUrnikiSC21Dan4Urn1UraON | INT | IOD_STR_disk | I2716
STRUrnikiSC21Dan4Urn2UraON | INT | IOD_STR_disk | I2717
STRUrnikiSC21Dan4Urn3UraON | INT | IOD_STR_disk | I2718
STRUrnikiSC21Dan4Urn1UraOFF | INT | IOD_STR_disk | I2719
STRUrnikiSC21Dan4Urn2UraOFF | INT | IOD_STR_disk | I2720
STRUrnikiSC21Dan4Urn3UraOFF | INT | IOD_STR_disk | I2721
STRUrnikiSC21Dan4Urn1MinON | INT | IOD_STR_disk | I2722
STRUrnikiSC21Dan4Urn2MinON | INT | IOD_STR_disk | I2723
STRUrnikiSC21Dan4Urn3MinON | INT | IOD_STR_disk | I2724
STRUrnikiSC21Dan4Urn1MinOFF | INT | IOD_STR_disk | I2725
STRUrnikiSC21Dan4Urn2MinOFF | INT | IOD_STR_disk | I2726
STRUrnikiSC21Dan4Urn3MinOFF | INT | IOD_STR_disk | I2727
STRUrnikiSC21Dan5Urn1UraON | INT | IOD_STR_disk | I2728
STRUrnikiSC21Dan5Urn2UraON | INT | IOD_STR_disk | I2729
STRUrnikiSC21Dan5Urn3UraON | INT | IOD_STR_disk | I2730
STRUrnikiSC21Dan5Urn1UraOFF | INT | IOD_STR_disk | I2731
STRUrnikiSC21Dan5Urn2UraOFF | INT | IOD_STR_disk | I2732
STRUrnikiSC21Dan5Urn3UraOFF | INT | IOD_STR_disk | I2733
STRUrnikiSC21Dan5Urn1MinON | INT | IOD_STR_disk | I2734
STRUrnikiSC21Dan5Urn2MinON | INT | IOD_STR_disk | I2735
STRUrnikiSC21Dan5Urn3MinON | INT | IOD_STR_disk | I2736
STRUrnikiSC21Dan5Urn1MinOFF | INT | IOD_STR_disk | I2737
STRUrnikiSC21Dan5Urn2MinOFF | INT | IOD_STR_disk | I2738
STRUrnikiSC21Dan5Urn3MinOFF | INT | IOD_STR_disk | I2739
STRUrnikiSC21Dan6Urn1UraON | INT | IOD_STR_disk | I2740
STRUrnikiSC21Dan6Urn2UraON | INT | IOD_STR_disk | I2741
STRUrnikiSC21Dan6Urn3UraON | INT | IOD_STR_disk | I2742
STRUrnikiSC21Dan6Urn1UraOFF | INT | IOD_STR_disk | I2743
STRUrnikiSC21Dan6Urn2UraOFF | INT | IOD_STR_disk | I2744
STRUrnikiSC21Dan6Urn3UraOFF | INT | IOD_STR_disk | I2745
STRUrnikiSC21Dan6Urn1MinON | INT | IOD_STR_disk | I2746
STRUrnikiSC21Dan6Urn2MinON | INT | IOD_STR_disk | I2747
STRUrnikiSC21Dan6Urn3MinON | INT | IOD_STR_disk | I2748
STRUrnikiSC21Dan6Urn1MinOFF | INT | IOD_STR_disk | I2749
STRUrnikiSC21Dan6Urn2MinOFF | INT | IOD_STR_disk | I2750
STRUrnikiSC21Dan6Urn3MinOFF | INT | IOD_STR_disk | I2751
STRUrnikiSC21Dan7Urn1UraON | INT | IOD_STR_disk | I2752
STRUrnikiSC21Dan7Urn2UraON | INT | IOD_STR_disk | I2753
STRUrnikiSC21Dan7Urn3UraON | INT | IOD_STR_disk | I2754
STRUrnikiSC21Dan7Urn1UraOFF | INT | IOD_STR_disk | I2755
STRUrnikiSC21Dan7Urn2UraOFF | INT | IOD_STR_disk | I2756
STRUrnikiSC21Dan7Urn3UraOFF | INT | IOD_STR_disk | I2757
STRUrnikiSC21Dan7Urn1MinON | INT | IOD_STR_disk | I2758
STRUrnikiSC21Dan7Urn2MinON | INT | IOD_STR_disk | I2759
STRUrnikiSC21Dan7Urn3MinON | INT | IOD_STR_disk | I2760
STRUrnikiSC21Dan7Urn1MinOFF | INT | IOD_STR_disk | I2761
STRUrnikiSC21Dan7Urn2MinOFF | INT | IOD_STR_disk | I2762
STRUrnikiSC21Dan7Urn3MinOFF | INT | IOD_STR_disk | I2763
STRUrnikiSC22Dan1Urn1UraON | INT | IOD_STR_disk | I2764
STRUrnikiSC22Dan1Urn2UraON | INT | IOD_STR_disk | I2765
STRUrnikiSC22Dan1Urn3UraON | INT | IOD_STR_disk | I2766
STRUrnikiSC22Dan1Urn1UraOFF | INT | IOD_STR_disk | I2767
STRUrnikiSC22Dan1Urn2UraOFF | INT | IOD_STR_disk | I2768
STRUrnikiSC22Dan1Urn3UraOFF | INT | IOD_STR_disk | I2769
STRUrnikiSC22Dan1Urn1MinON | INT | IOD_STR_disk | I2770
STRUrnikiSC22Dan1Urn2MinON | INT | IOD_STR_disk | I2771
STRUrnikiSC22Dan1Urn3MinON | INT | IOD_STR_disk | I2772
STRUrnikiSC22Dan1Urn1MinOFF | INT | IOD_STR_disk | I2773
STRUrnikiSC22Dan1Urn2MinOFF | INT | IOD_STR_disk | I2774
STRUrnikiSC22Dan1Urn3MinOFF | INT | IOD_STR_disk | I2775
STRUrnikiSC22Dan2Urn1UraON | INT | IOD_STR_disk | I2776
STRUrnikiSC22Dan2Urn2UraON | INT | IOD_STR_disk | I2777
STRUrnikiSC22Dan2Urn3UraON | INT | IOD_STR_disk | I2778
STRUrnikiSC22Dan2Urn1UraOFF | INT | IOD_STR_disk | I2779
STRUrnikiSC22Dan2Urn2UraOFF | INT | IOD_STR_disk | I2780
STRUrnikiSC22Dan2Urn3UraOFF | INT | IOD_STR_disk | I2781
STRUrnikiSC22Dan2Urn1MinON | INT | IOD_STR_disk | I2782
STRUrnikiSC22Dan2Urn2MinON | INT | IOD_STR_disk | I2783
STRUrnikiSC22Dan2Urn3MinON | INT | IOD_STR_disk | I2784
STRUrnikiSC22Dan2Urn1MinOFF | INT | IOD_STR_disk | I2785
STRUrnikiSC22Dan2Urn2MinOFF | INT | IOD_STR_disk | I2786
STRUrnikiSC22Dan2Urn3MinOFF | INT | IOD_STR_disk | I2787
STRUrnikiSC22Dan3Urn1UraON | INT | IOD_STR_disk | I2788
STRUrnikiSC22Dan3Urn2UraON | INT | IOD_STR_disk | I2789
STRUrnikiSC22Dan3Urn3UraON | INT | IOD_STR_disk | I2790
STRUrnikiSC22Dan3Urn1UraOFF | INT | IOD_STR_disk | I2791
STRUrnikiSC22Dan3Urn2UraOFF | INT | IOD_STR_disk | I2792
STRUrnikiSC22Dan3Urn3UraOFF | INT | IOD_STR_disk | I2793
STRUrnikiSC22Dan3Urn1MinON | INT | IOD_STR_disk | I2794
STRUrnikiSC22Dan3Urn2MinON | INT | IOD_STR_disk | I2795
STRUrnikiSC22Dan3Urn3MinON | INT | IOD_STR_disk | I2796
STRUrnikiSC22Dan3Urn1MinOFF | INT | IOD_STR_disk | I2797
STRUrnikiSC22Dan3Urn2MinOFF | INT | IOD_STR_disk | I2798
STRUrnikiSC22Dan3Urn3MinOFF | INT | IOD_STR_disk | I2799
STRUrnikiSC22Dan4Urn1UraON | INT | IOD_STR_disk | I2800
STRUrnikiSC22Dan4Urn2UraON | INT | IOD_STR_disk | I2801
STRUrnikiSC22Dan4Urn3UraON | INT | IOD_STR_disk | I2802
STRUrnikiSC22Dan4Urn1UraOFF | INT | IOD_STR_disk | I2803
STRUrnikiSC22Dan4Urn2UraOFF | INT | IOD_STR_disk | I2804
STRUrnikiSC22Dan4Urn3UraOFF | INT | IOD_STR_disk | I2805
STRUrnikiSC22Dan4Urn1MinON | INT | IOD_STR_disk | I2806
STRUrnikiSC22Dan4Urn2MinON | INT | IOD_STR_disk | I2807
STRUrnikiSC22Dan4Urn3MinON | INT | IOD_STR_disk | I2808
STRUrnikiSC22Dan4Urn1MinOFF | INT | IOD_STR_disk | I2809
STRUrnikiSC22Dan4Urn2MinOFF | INT | IOD_STR_disk | I2810
STRUrnikiSC22Dan4Urn3MinOFF | INT | IOD_STR_disk | I2811
STRUrnikiSC22Dan5Urn1UraON | INT | IOD_STR_disk | I2812
STRUrnikiSC22Dan5Urn2UraON | INT | IOD_STR_disk | I2813
STRUrnikiSC22Dan5Urn3UraON | INT | IOD_STR_disk | I2814
STRUrnikiSC22Dan5Urn1UraOFF | INT | IOD_STR_disk | I2815
STRUrnikiSC22Dan5Urn2UraOFF | INT | IOD_STR_disk | I2816
STRUrnikiSC22Dan5Urn3UraOFF | INT | IOD_STR_disk | I2817
STRUrnikiSC22Dan5Urn1MinON | INT | IOD_STR_disk | I2818
STRUrnikiSC22Dan5Urn2MinON | INT | IOD_STR_disk | I2819
STRUrnikiSC22Dan5Urn3MinON | INT | IOD_STR_disk | I2820
STRUrnikiSC22Dan5Urn1MinOFF | INT | IOD_STR_disk | I2821
STRUrnikiSC22Dan5Urn2MinOFF | INT | IOD_STR_disk | I2822
STRUrnikiSC22Dan5Urn3MinOFF | INT | IOD_STR_disk | I2823
STRUrnikiSC22Dan6Urn1UraON | INT | IOD_STR_disk | I2824
STRUrnikiSC22Dan6Urn2UraON | INT | IOD_STR_disk | I2825
STRUrnikiSC22Dan6Urn3UraON | INT | IOD_STR_disk | I2826
STRUrnikiSC22Dan6Urn1UraOFF | INT | IOD_STR_disk | I2827
STRUrnikiSC22Dan6Urn2UraOFF | INT | IOD_STR_disk | I2828
STRUrnikiSC22Dan6Urn3UraOFF | INT | IOD_STR_disk | I2829
STRUrnikiSC22Dan6Urn1MinON | INT | IOD_STR_disk | I2830
STRUrnikiSC22Dan6Urn2MinON | INT | IOD_STR_disk | I2831
STRUrnikiSC22Dan6Urn3MinON | INT | IOD_STR_disk | I2832
STRUrnikiSC22Dan6Urn1MinOFF | INT | IOD_STR_disk | I2833
STRUrnikiSC22Dan6Urn2MinOFF | INT | IOD_STR_disk | I2834
STRUrnikiSC22Dan6Urn3MinOFF | INT | IOD_STR_disk | I2835
STRUrnikiSC22Dan7Urn1UraON | INT | IOD_STR_disk | I2836
STRUrnikiSC22Dan7Urn2UraON | INT | IOD_STR_disk | I2837
STRUrnikiSC22Dan7Urn3UraON | INT | IOD_STR_disk | I2838
STRUrnikiSC22Dan7Urn1UraOFF | INT | IOD_STR_disk | I2839
STRUrnikiSC22Dan7Urn2UraOFF | INT | IOD_STR_disk | I2840
STRUrnikiSC22Dan7Urn3UraOFF | INT | IOD_STR_disk | I2841
STRUrnikiSC22Dan7Urn1MinON | INT | IOD_STR_disk | I2842
STRUrnikiSC22Dan7Urn2MinON | INT | IOD_STR_disk | I2843
STRUrnikiSC22Dan7Urn3MinON | INT | IOD_STR_disk | I2844
STRUrnikiSC22Dan7Urn1MinOFF | INT | IOD_STR_disk | I2845
STRUrnikiSC22Dan7Urn2MinOFF | INT | IOD_STR_disk | I2846
STRUrnikiSC22Dan7Urn3MinOFF | INT | IOD_STR_disk | I2847
STRUrnikiSC23Dan1Urn1UraON | INT | IOD_STR_disk | I2848
STRUrnikiSC23Dan1Urn2UraON | INT | IOD_STR_disk | I2849
STRUrnikiSC23Dan1Urn3UraON | INT | IOD_STR_disk | I2850
STRUrnikiSC23Dan1Urn1UraOFF | INT | IOD_STR_disk | I2851
STRUrnikiSC23Dan1Urn2UraOFF | INT | IOD_STR_disk | I2852
STRUrnikiSC23Dan1Urn3UraOFF | INT | IOD_STR_disk | I2853
STRUrnikiSC23Dan1Urn1MinON | INT | IOD_STR_disk | I2854
STRUrnikiSC23Dan1Urn2MinON | INT | IOD_STR_disk | I2855
STRUrnikiSC23Dan1Urn3MinON | INT | IOD_STR_disk | I2856
STRUrnikiSC23Dan1Urn1MinOFF | INT | IOD_STR_disk | I2857
STRUrnikiSC23Dan1Urn2MinOFF | INT | IOD_STR_disk | I2858
STRUrnikiSC23Dan1Urn3MinOFF | INT | IOD_STR_disk | I2859
STRUrnikiSC23Dan2Urn1UraON | INT | IOD_STR_disk | I2860
STRUrnikiSC23Dan2Urn2UraON | INT | IOD_STR_disk | I2861
STRUrnikiSC23Dan2Urn3UraON | INT | IOD_STR_disk | I2862
STRUrnikiSC23Dan2Urn1UraOFF | INT | IOD_STR_disk | I2863
STRUrnikiSC23Dan2Urn2UraOFF | INT | IOD_STR_disk | I2864
STRUrnikiSC23Dan2Urn3UraOFF | INT | IOD_STR_disk | I2865
STRUrnikiSC23Dan2Urn1MinON | INT | IOD_STR_disk | I2866
STRUrnikiSC23Dan2Urn2MinON | INT | IOD_STR_disk | I2867
STRUrnikiSC23Dan2Urn3MinON | INT | IOD_STR_disk | I2868
STRUrnikiSC23Dan2Urn1MinOFF | INT | IOD_STR_disk | I2869
STRUrnikiSC23Dan2Urn2MinOFF | INT | IOD_STR_disk | I2870
STRUrnikiSC23Dan2Urn3MinOFF | INT | IOD_STR_disk | I2871
STRUrnikiSC23Dan3Urn1UraON | INT | IOD_STR_disk | I2872
STRUrnikiSC23Dan3Urn2UraON | INT | IOD_STR_disk | I2873
STRUrnikiSC23Dan3Urn3UraON | INT | IOD_STR_disk | I2874
STRUrnikiSC23Dan3Urn1UraOFF | INT | IOD_STR_disk | I2875
STRUrnikiSC23Dan3Urn2UraOFF | INT | IOD_STR_disk | I2876
STRUrnikiSC23Dan3Urn3UraOFF | INT | IOD_STR_disk | I2877
STRUrnikiSC23Dan3Urn1MinON | INT | IOD_STR_disk | I2878
STRUrnikiSC23Dan3Urn2MinON | INT | IOD_STR_disk | I2879
STRUrnikiSC23Dan3Urn3MinON | INT | IOD_STR_disk | I2880
STRUrnikiSC23Dan3Urn1MinOFF | INT | IOD_STR_disk | I2881
STRUrnikiSC23Dan3Urn2MinOFF | INT | IOD_STR_disk | I2882
STRUrnikiSC23Dan3Urn3MinOFF | INT | IOD_STR_disk | I2883
STRUrnikiSC23Dan4Urn1UraON | INT | IOD_STR_disk | I2884
STRUrnikiSC23Dan4Urn2UraON | INT | IOD_STR_disk | I2885
STRUrnikiSC23Dan4Urn3UraON | INT | IOD_STR_disk | I2886
STRUrnikiSC23Dan4Urn1UraOFF | INT | IOD_STR_disk | I2887
STRUrnikiSC23Dan4Urn2UraOFF | INT | IOD_STR_disk | I2888
STRUrnikiSC23Dan4Urn3UraOFF | INT | IOD_STR_disk | I2889
STRUrnikiSC23Dan4Urn1MinON | INT | IOD_STR_disk | I2890
STRUrnikiSC23Dan4Urn2MinON | INT | IOD_STR_disk | I2891
STRUrnikiSC23Dan4Urn3MinON | INT | IOD_STR_disk | I2892
STRUrnikiSC23Dan4Urn1MinOFF | INT | IOD_STR_disk | I2893
STRUrnikiSC23Dan4Urn2MinOFF | INT | IOD_STR_disk | I2894
STRUrnikiSC23Dan4Urn3MinOFF | INT | IOD_STR_disk | I2895
STRUrnikiSC23Dan5Urn1UraON | INT | IOD_STR_disk | I2896
STRUrnikiSC23Dan5Urn2UraON | INT | IOD_STR_disk | I2897
STRUrnikiSC23Dan5Urn3UraON | INT | IOD_STR_disk | I2898
STRUrnikiSC23Dan5Urn1UraOFF | INT | IOD_STR_disk | I2899
STRUrnikiSC23Dan5Urn2UraOFF | INT | IOD_STR_disk | I2900
STRUrnikiSC23Dan5Urn3UraOFF | INT | IOD_STR_disk | I2901
STRUrnikiSC23Dan5Urn1MinON | INT | IOD_STR_disk | I2902
STRUrnikiSC23Dan5Urn2MinON | INT | IOD_STR_disk | I2903
STRUrnikiSC23Dan5Urn3MinON | INT | IOD_STR_disk | I2904
STRUrnikiSC23Dan5Urn1MinOFF | INT | IOD_STR_disk | I2905
STRUrnikiSC23Dan5Urn2MinOFF | INT | IOD_STR_disk | I2906
STRUrnikiSC23Dan5Urn3MinOFF | INT | IOD_STR_disk | I2907
STRUrnikiSC23Dan6Urn1UraON | INT | IOD_STR_disk | I2908
STRUrnikiSC23Dan6Urn2UraON | INT | IOD_STR_disk | I2909
STRUrnikiSC23Dan6Urn3UraON | INT | IOD_STR_disk | I2910
STRUrnikiSC23Dan6Urn1UraOFF | INT | IOD_STR_disk | I2911
STRUrnikiSC23Dan6Urn2UraOFF | INT | IOD_STR_disk | I2912
STRUrnikiSC23Dan6Urn3UraOFF | INT | IOD_STR_disk | I2913
STRUrnikiSC23Dan6Urn1MinON | INT | IOD_STR_disk | I2914
STRUrnikiSC23Dan6Urn2MinON | INT | IOD_STR_disk | I2915
STRUrnikiSC23Dan6Urn3MinON | INT | IOD_STR_disk | I2916
STRUrnikiSC23Dan6Urn1MinOFF | INT | IOD_STR_disk | I2917
STRUrnikiSC23Dan6Urn2MinOFF | INT | IOD_STR_disk | I2918
STRUrnikiSC23Dan6Urn3MinOFF | INT | IOD_STR_disk | I2919
STRUrnikiSC23Dan7Urn1UraON | INT | IOD_STR_disk | I2920
STRUrnikiSC23Dan7Urn2UraON | INT | IOD_STR_disk | I2921
STRUrnikiSC23Dan7Urn3UraON | INT | IOD_STR_disk | I2922
STRUrnikiSC23Dan7Urn1UraOFF | INT | IOD_STR_disk | I2923
STRUrnikiSC23Dan7Urn2UraOFF | INT | IOD_STR_disk | I2924
STRUrnikiSC23Dan7Urn3UraOFF | INT | IOD_STR_disk | I2925
STRUrnikiSC23Dan7Urn1MinON | INT | IOD_STR_disk | I2926
STRUrnikiSC23Dan7Urn2MinON | INT | IOD_STR_disk | I2927
STRUrnikiSC23Dan7Urn3MinON | INT | IOD_STR_disk | I2928
STRUrnikiSC23Dan7Urn1MinOFF | INT | IOD_STR_disk | I2929
STRUrnikiSC23Dan7Urn2MinOFF | INT | IOD_STR_disk | I2930
STRUrnikiSC23Dan7Urn3MinOFF | INT | IOD_STR_disk | I2931
STRUrnikiSC24Dan1Urn1UraON | INT | IOD_STR_disk | I2932
STRUrnikiSC24Dan1Urn2UraON | INT | IOD_STR_disk | I2933
STRUrnikiSC24Dan1Urn3UraON | INT | IOD_STR_disk | I2934
STRUrnikiSC24Dan1Urn1UraOFF | INT | IOD_STR_disk | I2935
STRUrnikiSC24Dan1Urn2UraOFF | INT | IOD_STR_disk | I2936
STRUrnikiSC24Dan1Urn3UraOFF | INT | IOD_STR_disk | I2937
STRUrnikiSC24Dan1Urn1MinON | INT | IOD_STR_disk | I2938
STRUrnikiSC24Dan1Urn2MinON | INT | IOD_STR_disk | I2939
STRUrnikiSC24Dan1Urn3MinON | INT | IOD_STR_disk | I2940
STRUrnikiSC24Dan1Urn1MinOFF | INT | IOD_STR_disk | I2941
STRUrnikiSC24Dan1Urn2MinOFF | INT | IOD_STR_disk | I2942
STRUrnikiSC24Dan1Urn3MinOFF | INT | IOD_STR_disk | I2943
STRUrnikiSC24Dan2Urn1UraON | INT | IOD_STR_disk | I2944
STRUrnikiSC24Dan2Urn2UraON | INT | IOD_STR_disk | I2945
STRUrnikiSC24Dan2Urn3UraON | INT | IOD_STR_disk | I2946
STRUrnikiSC24Dan2Urn1UraOFF | INT | IOD_STR_disk | I2947
STRUrnikiSC24Dan2Urn2UraOFF | INT | IOD_STR_disk | I2948
STRUrnikiSC24Dan2Urn3UraOFF | INT | IOD_STR_disk | I2949
STRUrnikiSC24Dan2Urn1MinON | INT | IOD_STR_disk | I2950
STRUrnikiSC24Dan2Urn2MinON | INT | IOD_STR_disk | I2951
STRUrnikiSC24Dan2Urn3MinON | INT | IOD_STR_disk | I2952
STRUrnikiSC24Dan2Urn1MinOFF | INT | IOD_STR_disk | I2953
STRUrnikiSC24Dan2Urn2MinOFF | INT | IOD_STR_disk | I2954
STRUrnikiSC24Dan2Urn3MinOFF | INT | IOD_STR_disk | I2955
STRUrnikiSC24Dan3Urn1UraON | INT | IOD_STR_disk | I2956
STRUrnikiSC24Dan3Urn2UraON | INT | IOD_STR_disk | I2957
STRUrnikiSC24Dan3Urn3UraON | INT | IOD_STR_disk | I2958
STRUrnikiSC24Dan3Urn1UraOFF | INT | IOD_STR_disk | I2959
STRUrnikiSC24Dan3Urn2UraOFF | INT | IOD_STR_disk | I2960
STRUrnikiSC24Dan3Urn3UraOFF | INT | IOD_STR_disk | I2961
STRUrnikiSC24Dan3Urn1MinON | INT | IOD_STR_disk | I2962
STRUrnikiSC24Dan3Urn2MinON | INT | IOD_STR_disk | I2963
STRUrnikiSC24Dan3Urn3MinON | INT | IOD_STR_disk | I2964
STRUrnikiSC24Dan3Urn1MinOFF | INT | IOD_STR_disk | I2965
STRUrnikiSC24Dan3Urn2MinOFF | INT | IOD_STR_disk | I2966
STRUrnikiSC24Dan3Urn3MinOFF | INT | IOD_STR_disk | I2967
STRUrnikiSC24Dan4Urn1UraON | INT | IOD_STR_disk | I2968
STRUrnikiSC24Dan4Urn2UraON | INT | IOD_STR_disk | I2969
STRUrnikiSC24Dan4Urn3UraON | INT | IOD_STR_disk | I2970
STRUrnikiSC24Dan4Urn1UraOFF | INT | IOD_STR_disk | I2971
STRUrnikiSC24Dan4Urn2UraOFF | INT | IOD_STR_disk | I2972
STRUrnikiSC24Dan4Urn3UraOFF | INT | IOD_STR_disk | I2973
STRUrnikiSC24Dan4Urn1MinON | INT | IOD_STR_disk | I2974
STRUrnikiSC24Dan4Urn2MinON | INT | IOD_STR_disk | I2975
STRUrnikiSC24Dan4Urn3MinON | INT | IOD_STR_disk | I2976
STRUrnikiSC24Dan4Urn1MinOFF | INT | IOD_STR_disk | I2977
STRUrnikiSC24Dan4Urn2MinOFF | INT | IOD_STR_disk | I2978
STRUrnikiSC24Dan4Urn3MinOFF | INT | IOD_STR_disk | I2979
STRUrnikiSC24Dan5Urn1UraON | INT | IOD_STR_disk | I2980
STRUrnikiSC24Dan5Urn2UraON | INT | IOD_STR_disk | I2981
STRUrnikiSC24Dan5Urn3UraON | INT | IOD_STR_disk | I2982
STRUrnikiSC24Dan5Urn1UraOFF | INT | IOD_STR_disk | I2983
STRUrnikiSC24Dan5Urn2UraOFF | INT | IOD_STR_disk | I2984
STRUrnikiSC24Dan5Urn3UraOFF | INT | IOD_STR_disk | I2985
STRUrnikiSC24Dan5Urn1MinON | INT | IOD_STR_disk | I2986
STRUrnikiSC24Dan5Urn2MinON | INT | IOD_STR_disk | I2987
STRUrnikiSC24Dan5Urn3MinON | INT | IOD_STR_disk | I2988
STRUrnikiSC24Dan5Urn1MinOFF | INT | IOD_STR_disk | I2989
STRUrnikiSC24Dan5Urn2MinOFF | INT | IOD_STR_disk | I2990
STRUrnikiSC24Dan5Urn3MinOFF | INT | IOD_STR_disk | I2991
STRUrnikiSC24Dan6Urn1UraON | INT | IOD_STR_disk | I2992
STRUrnikiSC24Dan6Urn2UraON | INT | IOD_STR_disk | I2993
STRUrnikiSC24Dan6Urn3UraON | INT | IOD_STR_disk | I2994
STRUrnikiSC24Dan6Urn1UraOFF | INT | IOD_STR_disk | I2995
STRUrnikiSC24Dan6Urn2UraOFF | INT | IOD_STR_disk | I2996
STRUrnikiSC24Dan6Urn3UraOFF | INT | IOD_STR_disk | I2997
STRUrnikiSC24Dan6Urn1MinON | INT | IOD_STR_disk | I2998
STRUrnikiSC24Dan6Urn2MinON | INT | IOD_STR_disk | I2999
STRUrnikiSC24Dan6Urn3MinON | INT | IOD_STR_disk | I3000
STRUrnikiSC24Dan6Urn1MinOFF | INT | IOD_STR_disk | I3001
STRUrnikiSC24Dan6Urn2MinOFF | INT | IOD_STR_disk | I3002
STRUrnikiSC24Dan6Urn3MinOFF | INT | IOD_STR_disk | I3003
STRUrnikiSC24Dan7Urn1UraON | INT | IOD_STR_disk | I3004
STRUrnikiSC24Dan7Urn2UraON | INT | IOD_STR_disk | I3005
STRUrnikiSC24Dan7Urn3UraON | INT | IOD_STR_disk | I3006
STRUrnikiSC24Dan7Urn1UraOFF | INT | IOD_STR_disk | I3007
STRUrnikiSC24Dan7Urn2UraOFF | INT | IOD_STR_disk | I3008
STRUrnikiSC24Dan7Urn3UraOFF | INT | IOD_STR_disk | I3009
STRUrnikiSC24Dan7Urn1MinON | INT | IOD_STR_disk | I3010
STRUrnikiSC24Dan7Urn2MinON | INT | IOD_STR_disk | I3011
STRUrnikiSC24Dan7Urn3MinON | INT | IOD_STR_disk | I3012
STRUrnikiSC24Dan7Urn1MinOFF | INT | IOD_STR_disk | I3013
STRUrnikiSC24Dan7Urn2MinOFF | INT | IOD_STR_disk | I3014
STRUrnikiSC24Dan7Urn3MinOFF | INT | IOD_STR_disk | I3015
STRPotrdiVpisUrnikaSC | DIGITAL | IOD_STR_disk | D327
STRUrnikiSaveSCDan1On1Ura | INT | IOD_STR_disk | I3016
STRUrnikiSaveSCDan1On1Mna | INT | IOD_STR_disk | I3017
STRUrnikiSaveSCDan1Off1Ura | INT | IOD_STR_disk | I3018
STRUrnikiSaveSCDan1Off1Mna | INT | IOD_STR_disk | I3019
STRUrnikiSaveSCDan1On2Ura | INT | IOD_STR_disk | I3020
STRUrnikiSaveSCDan1On2Mna | INT | IOD_STR_disk | I3021
STRUrnikiSaveSCDan1Off2Ura | INT | IOD_STR_disk | I3022
STRUrnikiSaveSCDan1Off2Mna | INT | IOD_STR_disk | I3023
STRUrnikiSaveSCDan1On3Ura | INT | IOD_STR_disk | I3024
STRUrnikiSaveSCDan1On3Mna | INT | IOD_STR_disk | I3025
STRUrnikiSaveSCDan1Off3Ura | INT | IOD_STR_disk | I3026
STRUrnikiSaveSCDan1Off3Mna | INT | IOD_STR_disk | I3027
STRUrnikiSaveSCDan2On1Ura | INT | IOD_STR_disk | I3028
STRUrnikiSaveSCDan2On1Mna | INT | IOD_STR_disk | I3029
STRUrnikiSaveSCDan2Off1Ura | INT | IOD_STR_disk | I3030
STRUrnikiSaveSCDan2Off1Mna | INT | IOD_STR_disk | I3031
STRUrnikiSaveSCDan2On2Ura | INT | IOD_STR_disk | I3032
STRUrnikiSaveSCDan2On2Mna | INT | IOD_STR_disk | I3033
STRUrnikiSaveSCDan2Off2Ura | INT | IOD_STR_disk | I3034
STRUrnikiSaveSCDan2Off2Mna | INT | IOD_STR_disk | I3035
STRUrnikiSaveSCDan2On3Ura | INT | IOD_STR_disk | I3036
STRUrnikiSaveSCDan2On3Mna | INT | IOD_STR_disk | I3037
STRUrnikiSaveSCDan2Off3Ura | INT | IOD_STR_disk | I3038
STRUrnikiSaveSCDan2Off3Mna | INT | IOD_STR_disk | I3039
STRUrnikiSaveSCDan3On1Ura | INT | IOD_STR_disk | I3040
STRUrnikiSaveSCDan3On1Mna | INT | IOD_STR_disk | I3041
STRUrnikiSaveSCDan3Off1Ura | INT | IOD_STR_disk | I3042
STRUrnikiSaveSCDan3Off1Mna | INT | IOD_STR_disk | I3043
STRUrnikiSaveSCDan3On2Ura | INT | IOD_STR_disk | I3044
STRUrnikiSaveSCDan3On2Mna | INT | IOD_STR_disk | I3045
STRUrnikiSaveSCDan3Off2Ura | INT | IOD_STR_disk | I3046
STRUrnikiSaveSCDan3Off2Mna | INT | IOD_STR_disk | I3047
STRUrnikiSaveSCDan3On3Ura | INT | IOD_STR_disk | I3048
STRUrnikiSaveSCDan3On3Mna | INT | IOD_STR_disk | I3049
STRUrnikiSaveSCDan3Off3Ura | INT | IOD_STR_disk | I3050
STRUrnikiSaveSCDan3Off3Mna | INT | IOD_STR_disk | I3051
STRUrnikiSaveSCDan4On1Ura | INT | IOD_STR_disk | I3052
STRUrnikiSaveSCDan4On1Mna | INT | IOD_STR_disk | I3053
STRUrnikiSaveSCDan4Off1Ura | INT | IOD_STR_disk | I3054
STRUrnikiSaveSCDan4Off1Mna | INT | IOD_STR_disk | I3055
STRUrnikiSaveSCDan4On2Ura | INT | IOD_STR_disk | I3056
STRUrnikiSaveSCDan4On2Mna | INT | IOD_STR_disk | I3057
STRUrnikiSaveSCDan4Off2Ura | INT | IOD_STR_disk | I3058
STRUrnikiSaveSCDan4Off2Mna | INT | IOD_STR_disk | I3059
STRUrnikiSaveSCDan4On3Ura | INT | IOD_STR_disk | I3060
STRUrnikiSaveSCDan4On3Mna | INT | IOD_STR_disk | I3061
STRUrnikiSaveSCDan4Off3Ura | INT | IOD_STR_disk | I3062
STRUrnikiSaveSCDan4Off3Mna | INT | IOD_STR_disk | I3063
STRUrnikiSaveSCDan5On1Ura | INT | IOD_STR_disk | I3064
STRUrnikiSaveSCDan5On1Mna | INT | IOD_STR_disk | I3065
STRUrnikiSaveSCDan5Off1Ura | INT | IOD_STR_disk | I3066
STRUrnikiSaveSCDan5Off1Mna | INT | IOD_STR_disk | I3067
STRUrnikiSaveSCDan5On2Ura | INT | IOD_STR_disk | I3068
STRUrnikiSaveSCDan5On2Mna | INT | IOD_STR_disk | I3069
STRUrnikiSaveSCDan5Off2Ura | INT | IOD_STR_disk | I3070
STRUrnikiSaveSCDan5Off2Mna | INT | IOD_STR_disk | I3071
STRUrnikiSaveSCDan5On3Ura | INT | IOD_STR_disk | I3072
STRUrnikiSaveSCDan5On3Mna | INT | IOD_STR_disk | I3073
STRUrnikiSaveSCDan5Off3Ura | INT | IOD_STR_disk | I3074
STRUrnikiSaveSCDan5Off3Mna | INT | IOD_STR_disk | I3075
STRUrnikiSaveSCDan6On1Ura | INT | IOD_STR_disk | I3076
STRUrnikiSaveSCDan6On1Mna | INT | IOD_STR_disk | I3077
STRUrnikiSaveSCDan6Off1Ura | INT | IOD_STR_disk | I3078
STRUrnikiSaveSCDan6Off1Mna | INT | IOD_STR_disk | I3079
STRUrnikiSaveSCDan6On2Ura | INT | IOD_STR_disk | I3080
STRUrnikiSaveSCDan6On2Mna | INT | IOD_STR_disk | I3081
STRUrnikiSaveSCDan6Off2Ura | INT | IOD_STR_disk | I3082
STRUrnikiSaveSCDan6Off2Mna | INT | IOD_STR_disk | I3083
STRUrnikiSaveSCDan6On3Ura | INT | IOD_STR_disk | I3084
STRUrnikiSaveSCDan6On3Mna | INT | IOD_STR_disk | I3085
STRUrnikiSaveSCDan6Off3Ura | INT | IOD_STR_disk | I3086
STRUrnikiSaveSCDan6Off3Mna | INT | IOD_STR_disk | I3087
STRUrnikiSaveSCDan7On1Ura | INT | IOD_STR_disk | I3088
STRUrnikiSaveSCDan7On1Mna | INT | IOD_STR_disk | I3089
STRUrnikiSaveSCDan7Off1Ura | INT | IOD_STR_disk | I3090
STRUrnikiSaveSCDan7Off1Mna | INT | IOD_STR_disk | I3091
STRUrnikiSaveSCDan7On2Ura | INT | IOD_STR_disk | I3092
STRUrnikiSaveSCDan7On2Mna | INT | IOD_STR_disk | I3093
STRUrnikiSaveSCDan7Off2Ura | INT | IOD_STR_disk | I3094
STRUrnikiSaveSCDan7Off2Mna | INT | IOD_STR_disk | I3095
STRUrnikiSaveSCDan7On3Ura | INT | IOD_STR_disk | I3096
STRUrnikiSaveSCDan7On3Mna | INT | IOD_STR_disk | I3097
STRUrnikiSaveSCDan7Off3Ura | INT | IOD_STR_disk | I3098
STRUrnikiSaveSCDan7Off3Mna | INT | IOD_STR_disk | I3099
STRAkumSanVodeTE1OnOff | DIGITAL | IOD_STR_TCP | 00001
STRAlarmGenCirc1 | DIGITAL | IOD_STR_TCP | 00002
STRAlarmGenComm | DIGITAL | IOD_STR_TCP | 00003
STRAlarmGenDI | DIGITAL | IOD_STR_TCP | 00004
STRAlarmGenHladPost | DIGITAL | IOD_STR_TCP | 00005
STRAlarmGenKlima1 | DIGITAL | IOD_STR_TCP | 00006
STRAlarmGenKlima2 | DIGITAL | IOD_STR_TCP | 00007
STRAlarmGenLopute | DIGITAL | IOD_STR_TCP | 00008
STRAlarmGenRest | DIGITAL | IOD_STR_TCP | 00009
STRAlarmGenSenzor | DIGITAL | IOD_STR_TCP | 00010
STRAlarmGenTemp | DIGITAL | IOD_STR_TCP | 00011
STRAlarmGenToplPost | DIGITAL | IOD_STR_TCP | 00012
STRAlarmGenVent | DIGITAL | IOD_STR_TCP | 00013
STRAlarmGenVTV | DIGITAL | IOD_STR_TCP | 00014
STRATVAlarmTemp | REAL | IOD_STR_TCP | 45001 | 0 | 100 | 0 | 100 | °C | ####.#
STRATVTempPrenizka | DIGITAL | IOD_STR_TCP | 00015
STRCirc1CosFi_III | REAL | IOD_STR_TCP | 45003 | -100 | 100 | -1 | 1 |  | ##.##
STRCirc1DelovnaEnergija | REAL | IOD_STR_TCP | 45005 | 0 | 1200 | 0 | 1200 | kW | ###.#
STRCirc1DelovnaMoc_III | REAL | IOD_STR_TCP | 45007 | 0 | 1200 | 0 | 1200 | kW | ###.#
STRCirc1DelovnaMoc_L1 | REAL | IOD_STR_TCP | 45009 | 0 | 1200 | 0 | 1200 | kW | ###.#
STRCirc1DelovnaMoc_L2 | REAL | IOD_STR_TCP | 45011 | 0 | 1200 | 0 | 1200 | kW | ###.#
STRCirc1DelovnaMoc_L3 | REAL | IOD_STR_TCP | 45013 | 0 | 1200 | 0 | 1200 | kW | ###.#
STRCirc1Frekvenca_L1 | REAL | IOD_STR_TCP | 45015 | 0 | 60 | 0 | 60 | Hz | ##.#
STRCirc1InduktivnaEnergija | REAL | IOD_STR_TCP | 45017 | 0 | 1000 | 0 | 1000 | kW | ###.#
STRCirc1InduktivnaMoc_III | REAL | IOD_STR_TCP | 45019 | 0 | 1200 | 0 | 1200 | kVAR | ###.#
STRCirc1JalovaMoc_L1 | REAL | IOD_STR_TCP | 45021 | 0 | 1200 | 0 | 1200 | kVAR | ###.#
STRCirc1JalovaMoc_L2 | REAL | IOD_STR_TCP | 45023 | 0 | 1200 | 0 | 1200 | kVAR | ###.#
STRCirc1JalovaMoc_L3 | REAL | IOD_STR_TCP | 45025 | 0 | 1200 | 0 | 1200 | kVAR | ###.#
STRCirc1KapacitivnaEnergija | REAL | IOD_STR_TCP | 45027
STRCirc1KapacitivnaMoc_III | REAL | IOD_STR_TCP | 45029 | 0 | 1000 | 0 | 1000 | kVAR | ###.#
STRCirc1MaximumDemand | REAL | IOD_STR_TCP | 45031 | 0 | 1200 | 0 | 1200 | A | ###.#
STRCirc1Napetost_L1_L2 | REAL | IOD_STR_TCP | 45033 | 0 | 450 | 0 | 450 | V | ###.#
STRCirc1Napetost_L1_N | REAL | IOD_STR_TCP | 45035 | 0 | 270 | 0 | 270 | V | ###.#
STRCirc1Napetost_L2_L3 | REAL | IOD_STR_TCP | 45037 | 0 | 450 | 0 | 450 | V | ###.#
STRCirc1Napetost_L2_N | REAL | IOD_STR_TCP | 45039 | 0 | 270 | 0 | 270 | V | ###.#
STRCirc1Napetost_L3_L1 | REAL | IOD_STR_TCP | 45041 | 0 | 450 | 0 | 450 | V | ###.#
STRCirc1Napetost_L3_N | REAL | IOD_STR_TCP | 45043 | 0 | 270 | 0 | 270 | V | ###.#
STRCirc1NavideznaMoc_III | REAL | IOD_STR_TCP | 45045 | 0 | 1200 | 0 | 1200 | kVA | ###.#
STRCirc1NicelniTok | REAL | IOD_STR_TCP | 45047 | 0 | 1200 | 0 | 1200 | A | ###.#
STRCirc1PowerFactor_III | REAL | IOD_STR_TCP | 45049 | -100 | 100 | -1 | 1 |  | ##.##
STRCirc1PowerFactor_L1 | REAL | IOD_STR_TCP | 45051 | -100 | 100 | -1 | 1 |  | ##.##
STRCirc1PowerFactor_L2 | REAL | IOD_STR_TCP | 45053 | -100 | 100 | -1 | 1 |  | ##.##
STRCirc1PowerFactor_L3 | REAL | IOD_STR_TCP | 45055 | -100 | 100 | -1 | 1 |  | ##.##
STRCirc1THDI_L1 | REAL | IOD_STR_TCP | 45057 | 0 | 100 | 0 | 10 | % | ###.#
STRCirc1THDI_L2 | REAL | IOD_STR_TCP | 45059 | 0 | 100 | 0 | 10 | % | ###.#
STRCirc1THDI_L3 | REAL | IOD_STR_TCP | 45061 | 0 | 100 | 0 | 10 | % | ###.#
STRCirc1THDV_L1 | REAL | IOD_STR_TCP | 45063 | 0 | 100 | 0 | 10 | % | ###.#
STRCirc1THDV_L2 | REAL | IOD_STR_TCP | 45065 | 0 | 100 | 0 | 10 | % | ###.#
STRCirc1THDV_L3 | REAL | IOD_STR_TCP | 45067 | 0 | 100 | 0 | 10 | % | ###.#
STRCirc1Tok_L1 | REAL | IOD_STR_TCP | 45069 | 0 | 1200 | 0 | 1200 | A | ###.#
STRCirc1Tok_L2 | REAL | IOD_STR_TCP | 45071 | 0 | 1200 | 0 | 1200 | A | ###.#
STRCirc1Tok_L3 | REAL | IOD_STR_TCP | 45073 | 0 | 1200 | 0 | 1200 | A | ###.#
STRCirc1TokPovprecje_III | REAL | IOD_STR_TCP | 45075 | 0 | 1200 | 0 | 1200 | A | ###.#
STRComSCADA | DIGITAL | IOD_STR_TCP | 00016
STRComSCADA1 | DIGITAL | IOD_STR_TCP | 00017
STRCrpalkaMN1OnOff | DIGITAL | IOD_STR_TCP | 00018
STRCrpalkaTm11TM12OnOff | DIGITAL | IOD_STR_TCP | 00019
STRCrpalkeDnfs1AlarmAktiven | DIGITAL | IOD_STR_TCP | 00020
STRCrpalkeDnfs1Current | REAL | IOD_STR_TCP | 45077 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeDnfs1Deluje | DIGITAL | IOD_STR_TCP | 00021
STRCrpalkeDnfs1PreklopkaMode | INT | IOD_STR_TCP | 40001
STRCrpalkeDnfs1QuickStop | DIGITAL | IOD_STR_TCP | 00022
STRCrpalkeDnfs1RemoteON | DIGITAL | IOD_STR_TCP | 00023
STRCrpalkeDnfs1Reset | DIGITAL | IOD_STR_TCP | 00024
STRCrpalkeDnfs1Start | DIGITAL | IOD_STR_TCP | 00025
STRCrpalkeDnfs1StarterStatus | REAL | IOD_STR_TCP | 45079
STRCrpalkeDnfs1StarterStatus0do7 | INT | IOD_STR_TCP | 40002
STRCrpalkeDnfs1StatusCrpalke | INT | IOD_STR_TCP | 40003
STRCrpalkeDnfs1StatusKontaktor | INT | IOD_STR_TCP | 40004
STRCrpalkeDnfs1Stop | DIGITAL | IOD_STR_TCP | 00026
STRCrpalkeDnfs1Temerature | REAL | IOD_STR_TCP | 45081 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeDnfs1TripCode | REAL | IOD_STR_TCP | 45083
STRCrpalkeDnfs1UreXC200 | REAL | IOD_STR_TCP | 45085 |  |  |  |  | h | ####
STRCrpalkeDnfs2AlarmAktiven | DIGITAL | IOD_STR_TCP | 00027
STRCrpalkeDnfs2Current | REAL | IOD_STR_TCP | 45087 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeDnfs2Deluje | DIGITAL | IOD_STR_TCP | 00028
STRCrpalkeDnfs2PreklopkaMode | INT | IOD_STR_TCP | 40005
STRCrpalkeDnfs2QuickStop | DIGITAL | IOD_STR_TCP | 00029
STRCrpalkeDnfs2RemoteON | DIGITAL | IOD_STR_TCP | 00030
STRCrpalkeDnfs2Reset | DIGITAL | IOD_STR_TCP | 00031
STRCrpalkeDnfs2Start | DIGITAL | IOD_STR_TCP | 00032
STRCrpalkeDnfs2StarterStatus | REAL | IOD_STR_TCP | 45089
STRCrpalkeDnfs2StarterStatus0do7 | INT | IOD_STR_TCP | 40006
STRCrpalkeDnfs2StatusCrpalke | INT | IOD_STR_TCP | 40007
STRCrpalkeDnfs2StatusKontaktor | INT | IOD_STR_TCP | 40008
STRCrpalkeDnfs2Stop | DIGITAL | IOD_STR_TCP | 00033
STRCrpalkeDnfs2Temerature | REAL | IOD_STR_TCP | 45091 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeDnfs2TripCode | REAL | IOD_STR_TCP | 45093
STRCrpalkeDnfs2UreXC200 | REAL | IOD_STR_TCP | 45095 |  |  |  |  | h | ####
STRCrpalkeDnfs3AlarmAktiven | DIGITAL | IOD_STR_TCP | 00034
STRCrpalkeDnfs3Current | REAL | IOD_STR_TCP | 45097 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeDnfs3Deluje | DIGITAL | IOD_STR_TCP | 00035
STRCrpalkeDnfs3PreklopkaMode | INT | IOD_STR_TCP | 40009
STRCrpalkeDnfs3QuickStop | DIGITAL | IOD_STR_TCP | 00036
STRCrpalkeDnfs3RemoteON | DIGITAL | IOD_STR_TCP | 00037
STRCrpalkeDnfs3Reset | DIGITAL | IOD_STR_TCP | 00038
STRCrpalkeDnfs3Start | DIGITAL | IOD_STR_TCP | 00039
STRCrpalkeDnfs3StarterStatus | REAL | IOD_STR_TCP | 45099
STRCrpalkeDnfs3StarterStatus0do7 | INT | IOD_STR_TCP | 40010
STRCrpalkeDnfs3StatusCrpalke | INT | IOD_STR_TCP | 40011
STRCrpalkeDnfs3StatusKontaktor | INT | IOD_STR_TCP | 40012
STRCrpalkeDnfs3Stop | DIGITAL | IOD_STR_TCP | 00040
STRCrpalkeDnfs3Temerature | REAL | IOD_STR_TCP | 45101 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeDnfs3TripCode | REAL | IOD_STR_TCP | 45103
STRCrpalkeDnfs3UreXC200 | REAL | IOD_STR_TCP | 45105 |  |  |  |  | h | ####
STRCrpalkeDnfs4AlarmAktiven | DIGITAL | IOD_STR_TCP | 00041
STRCrpalkeDnfs4Current | REAL | IOD_STR_TCP | 45107 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeDnfs4Deluje | DIGITAL | IOD_STR_TCP | 00042
STRCrpalkeDnfs4PreklopkaMode | INT | IOD_STR_TCP | 40013
STRCrpalkeDnfs4QuickStop | DIGITAL | IOD_STR_TCP | 00043
STRCrpalkeDnfs4RemoteON | DIGITAL | IOD_STR_TCP | 00044
STRCrpalkeDnfs4Reset | DIGITAL | IOD_STR_TCP | 00045
STRCrpalkeDnfs4Start | DIGITAL | IOD_STR_TCP | 00046
STRCrpalkeDnfs4StarterStatus | REAL | IOD_STR_TCP | 45109
STRCrpalkeDnfs4StarterStatus0do7 | INT | IOD_STR_TCP | 40014
STRCrpalkeDnfs4StatusCrpalke | INT | IOD_STR_TCP | 40015
STRCrpalkeDnfs4StatusKontaktor | INT | IOD_STR_TCP | 40016
STRCrpalkeDnfs4Stop | DIGITAL | IOD_STR_TCP | 00047
STRCrpalkeDnfs4Temerature | REAL | IOD_STR_TCP | 45111 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeDnfs4TripCode | REAL | IOD_STR_TCP | 45113
STRCrpalkeDnfs4UreXC200 | REAL | IOD_STR_TCP | 45115 |  |  |  |  | h | ####
STRCrpalkeGrfs10AlarmActiveCode | INT | IOD_STR_TCP | 40017
STRCrpalkeGrfs10AlarmAktiven | DIGITAL | IOD_STR_TCP | 00048
STRCrpalkeGrfs10AlarmCodeLog1 | INT | IOD_STR_TCP | 40018
STRCrpalkeGrfs10AlarmCodeLog2 | INT | IOD_STR_TCP | 40019
STRCrpalkeGrfs10AlarmCodeLog3 | INT | IOD_STR_TCP | 40020
STRCrpalkeGrfs10AlarmCodeLog4 | INT | IOD_STR_TCP | 40021
STRCrpalkeGrfs10AlarmCodeLog5 | INT | IOD_STR_TCP | 40022
STRCrpalkeGrfs10AlarmGroupXVH0 | INT | IOD_STR_TCP | 40023
STRCrpalkeGrfs10AlarmGroupXVH10 | INT | IOD_STR_TCP | 40024
STRCrpalkeGrfs10AlarmGroupXVH11 | INT | IOD_STR_TCP | 40025
STRCrpalkeGrfs10AlarmGroupXVH12 | INT | IOD_STR_TCP | 40026
STRCrpalkeGrfs10AlarmGroupXVH13 | INT | IOD_STR_TCP | 40027
STRCrpalkeGrfs10AlarmGroupXVH14 | INT | IOD_STR_TCP | 40028
STRCrpalkeGrfs10AlarmGroupXVH15 | INT | IOD_STR_TCP | 40029
STRCrpalkeGrfs10AlarmGroupXVH16 | INT | IOD_STR_TCP | 40030
STRCrpalkeGrfs10AlarmGroupXVH1 | INT | IOD_STR_TCP | 40031
STRCrpalkeGrfs10AlarmGroupXVH2 | INT | IOD_STR_TCP | 40032
STRCrpalkeGrfs10AlarmGroupXVH3 | INT | IOD_STR_TCP | 40033
STRCrpalkeGrfs10AlarmGroupXVH4 | INT | IOD_STR_TCP | 40034
STRCrpalkeGrfs10AlarmGroupXVH5 | INT | IOD_STR_TCP | 40035
STRCrpalkeGrfs10AlarmGroupXVH6 | INT | IOD_STR_TCP | 40036
STRCrpalkeGrfs10AlarmGroupXVH7 | INT | IOD_STR_TCP | 40037
STRCrpalkeGrfs10AlarmGroupXVH8 | INT | IOD_STR_TCP | 40038
STRCrpalkeGrfs10AlarmGroupXVH9 | INT | IOD_STR_TCP | 40039
STRCrpalkeGrfs10AlarmQSD1 | INT | IOD_STR_TCP | 40040
STRCrpalkeGrfs10AlarmQSD2 | INT | IOD_STR_TCP | 40041
STRCrpalkeGrfs10AlarmStart1 | INT | IOD_STR_TCP | 40042
STRCrpalkeGrfs10AlarmStart2 | INT | IOD_STR_TCP | 40043
STRCrpalkeGrfs10AlarmStop1 | INT | IOD_STR_TCP | 40044
STRCrpalkeGrfs10AlarmStop2 | INT | IOD_STR_TCP | 40045
STRCrpalkeGrfs10AlarmStop3 | INT | IOD_STR_TCP | 40046
STRCrpalkeGrfs10AlarmSurv1 | INT | IOD_STR_TCP | 40047
STRCrpalkeGrfs10AlarmSurv2 | INT | IOD_STR_TCP | 40048
STRCrpalkeGrfs10ControlSource | INT | IOD_STR_TCP | 40049
STRCrpalkeGrfs10DeltaSetPoint | REAL | IOD_STR_TCP | 45117
STRCrpalkeGrfs10Deluje | DIGITAL | IOD_STR_TCP | 00049
STRCrpalkeGrfs10EnergijaPoraba | REAL | IOD_STR_TCP | 45119 |  |  |  |  | kWh | ####.#
STRCrpalkeGrfs10ExternInputSetup | INT | IOD_STR_TCP | 40050
STRCrpalkeGrfs10ExternInputsStatus | INT | IOD_STR_TCP | 40051
STRCrpalkeGrfs10FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 45121 | 0 | 500 | 0 | 500 | V | ####.#
STRCrpalkeGrfs10FrekPretvornikDCTok | REAL | IOD_STR_TCP | 45123 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs10FreqMax | REAL | IOD_STR_TCP | 45125 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs10FreqMin | REAL | IOD_STR_TCP | 45127 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs10FreqUpper | REAL | IOD_STR_TCP | 45129 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs10LocalMode | DIGITAL | IOD_STR_TCP | 00050
STRCrpalkeGrfs10LocalSetupMode1 | INT | IOD_STR_TCP | 40052
STRCrpalkeGrfs10MocMax | REAL | IOD_STR_TCP | 45131 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs10MocTrenutna | REAL | IOD_STR_TCP | 45133 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs10MotorHitrost | REAL | IOD_STR_TCP | 45135 | 0 | 2500 | 0 | 2500 | obr/min | ####.#
STRCrpalkeGrfs10MotorTok | REAL | IOD_STR_TCP | 45137 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs10NapajanjeTok | REAL | IOD_STR_TCP | 45139 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs10NastavitevLokalna | REAL | IOD_STR_TCP | 45141
STRCrpalkeGrfs10NastavitevTrenutna | REAL | IOD_STR_TCP | 45143
STRCrpalkeGrfs10PreklopkaMode | INT | IOD_STR_TCP | 40053
STRCrpalkeGrfs10PretokMax | REAL | IOD_STR_TCP | 45145 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs10PretokMin | REAL | IOD_STR_TCP | 45147 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs10PretokTrenutni | REAL | IOD_STR_TCP | 45149 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs10PritiskMax | REAL | IOD_STR_TCP | 45151 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs10PritiskTrenutni | REAL | IOD_STR_TCP | 45153 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs10ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 45155 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs10ReferencaRemote | REAL | IOD_STR_TCP | 45157 | 0 | 100 | 0 | 100 | % | ####.#
STRCrpalkeGrfs10Relay1setup | INT | IOD_STR_TCP | 40054
STRCrpalkeGrfs10RemoteON | DIGITAL | IOD_STR_TCP | 00051
STRCrpalkeGrfs10RemoteSetupMode1 | INT | IOD_STR_TCP | 40055
STRCrpalkeGrfs10Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 00052
STRCrpalkeGrfs10ResetAlarm | DIGITAL | IOD_STR_TCP | 00053
STRCrpalkeGrfs10ResetAlarmLog | DIGITAL | IOD_STR_TCP | 00054
STRCrpalkeGrfs10ResetDevice | DIGITAL | IOD_STR_TCP | 00055
STRCrpalkeGrfs10SetAutomatic | DIGITAL | IOD_STR_TCP | 00056
STRCrpalkeGrfs10SetConstFreqMode | DIGITAL | IOD_STR_TCP | 00057
STRCrpalkeGrfs10SetConstPress | DIGITAL | IOD_STR_TCP | 00058
STRCrpalkeGrfs10SetLocalMode | DIGITAL | IOD_STR_TCP | 00059
STRCrpalkeGrfs10SetMaxRunMode | DIGITAL | IOD_STR_TCP | 00060
STRCrpalkeGrfs10SetMinRunMode | DIGITAL | IOD_STR_TCP | 00061
STRCrpalkeGrfs10SetPropPress | DIGITAL | IOD_STR_TCP | 00062
STRCrpalkeGrfs10SetReference | DIGITAL | IOD_STR_TCP | 00063
STRCrpalkeGrfs10SetRemoteMode | DIGITAL | IOD_STR_TCP | 00064
STRCrpalkeGrfs10SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 00065
STRCrpalkeGrfs10SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 00066
STRCrpalkeGrfs10SetTwinModeSync | DIGITAL | IOD_STR_TCP | 00067
STRCrpalkeGrfs10Start | DIGITAL | IOD_STR_TCP | 00068
STRCrpalkeGrfs10StatusCrpalke | INT | IOD_STR_TCP | 40056
STRCrpalkeGrfs10StatusMode1 | INT | IOD_STR_TCP | 40057
STRCrpalkeGrfs10StatusMode1co | INT | IOD_STR_TCP | 40058
STRCrpalkeGrfs10StatusMode1op | INT | IOD_STR_TCP | 40059
STRCrpalkeGrfs10StatusMode2 | INT | IOD_STR_TCP | 40060
STRCrpalkeGrfs10StatusMode3 | INT | IOD_STR_TCP | 40061
STRCrpalkeGrfs10StevecUr2h | REAL | IOD_STR_TCP | 45159 |  |  |  |  | 2h
STRCrpalkeGrfs10Stop | DIGITAL | IOD_STR_TCP | 00069
STRCrpalkeGrfs10SystemFeedback | REAL | IOD_STR_TCP | 45161
STRCrpalkeGrfs10SystemReference | REAL | IOD_STR_TCP | 45163
STRCrpalkeGrfs10TemperaturaMotorja | REAL | IOD_STR_TCP | 45165 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeGrfs10UreXC200 | REAL | IOD_STR_TCP | 45167 |  |  |  |  | h | ####.#
STRCrpalkeGrfs11AlarmActiveCode | INT | IOD_STR_TCP | 40062
STRCrpalkeGrfs11AlarmAktiven | DIGITAL | IOD_STR_TCP | 00070
STRCrpalkeGrfs11AlarmCodeLog1 | INT | IOD_STR_TCP | 40063
STRCrpalkeGrfs11AlarmCodeLog2 | INT | IOD_STR_TCP | 40064
STRCrpalkeGrfs11AlarmCodeLog3 | INT | IOD_STR_TCP | 40065
STRCrpalkeGrfs11AlarmCodeLog4 | INT | IOD_STR_TCP | 40066
STRCrpalkeGrfs11AlarmCodeLog5 | INT | IOD_STR_TCP | 40067
STRCrpalkeGrfs11AlarmGroupXVH0 | INT | IOD_STR_TCP | 40068
STRCrpalkeGrfs11AlarmGroupXVH10 | INT | IOD_STR_TCP | 40069
STRCrpalkeGrfs11AlarmGroupXVH11 | INT | IOD_STR_TCP | 40070
STRCrpalkeGrfs11AlarmGroupXVH12 | INT | IOD_STR_TCP | 40071
STRCrpalkeGrfs11AlarmGroupXVH13 | INT | IOD_STR_TCP | 40072
STRCrpalkeGrfs11AlarmGroupXVH14 | INT | IOD_STR_TCP | 40073
STRCrpalkeGrfs11AlarmGroupXVH15 | INT | IOD_STR_TCP | 40074
STRCrpalkeGrfs11AlarmGroupXVH16 | INT | IOD_STR_TCP | 40075
STRCrpalkeGrfs11AlarmGroupXVH1 | INT | IOD_STR_TCP | 40076
STRCrpalkeGrfs11AlarmGroupXVH2 | INT | IOD_STR_TCP | 40077
STRCrpalkeGrfs11AlarmGroupXVH3 | INT | IOD_STR_TCP | 40078
STRCrpalkeGrfs11AlarmGroupXVH4 | INT | IOD_STR_TCP | 40079
STRCrpalkeGrfs11AlarmGroupXVH5 | INT | IOD_STR_TCP | 40080
STRCrpalkeGrfs11AlarmGroupXVH6 | INT | IOD_STR_TCP | 40081
STRCrpalkeGrfs11AlarmGroupXVH7 | INT | IOD_STR_TCP | 40082
STRCrpalkeGrfs11AlarmGroupXVH8 | INT | IOD_STR_TCP | 40083
STRCrpalkeGrfs11AlarmGroupXVH9 | INT | IOD_STR_TCP | 40084
STRCrpalkeGrfs11AlarmQSD1 | INT | IOD_STR_TCP | 40085
STRCrpalkeGrfs11AlarmQSD2 | INT | IOD_STR_TCP | 40086
STRCrpalkeGrfs11AlarmStart1 | INT | IOD_STR_TCP | 40087
STRCrpalkeGrfs11AlarmStart2 | INT | IOD_STR_TCP | 40088
STRCrpalkeGrfs11AlarmStop1 | INT | IOD_STR_TCP | 40089
STRCrpalkeGrfs11AlarmStop2 | INT | IOD_STR_TCP | 40090
STRCrpalkeGrfs11AlarmStop3 | INT | IOD_STR_TCP | 40091
STRCrpalkeGrfs11AlarmSurv1 | INT | IOD_STR_TCP | 40092
STRCrpalkeGrfs11AlarmSurv2 | INT | IOD_STR_TCP | 40093
STRCrpalkeGrfs11ControlSource | INT | IOD_STR_TCP | 40094
STRCrpalkeGrfs11DeltaSetPoint | REAL | IOD_STR_TCP | 45169
STRCrpalkeGrfs11Deluje | DIGITAL | IOD_STR_TCP | 00071
STRCrpalkeGrfs11EnergijaPoraba | REAL | IOD_STR_TCP | 45171 |  |  |  |  | kWh | ####.#
STRCrpalkeGrfs11ExternInputSetup | INT | IOD_STR_TCP | 40095
STRCrpalkeGrfs11ExternInputsStatus | INT | IOD_STR_TCP | 40096
STRCrpalkeGrfs11FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 45173 | 0 | 500 | 0 | 500 | V | ####.#
STRCrpalkeGrfs11FrekPretvornikDCTok | REAL | IOD_STR_TCP | 45175 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs11FreqMax | REAL | IOD_STR_TCP | 45177 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs11FreqMin | REAL | IOD_STR_TCP | 45179 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs11FreqUpper | REAL | IOD_STR_TCP | 45181 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs11LocalMode | DIGITAL | IOD_STR_TCP | 00072
STRCrpalkeGrfs11LocalSetupMode1 | INT | IOD_STR_TCP | 40097
STRCrpalkeGrfs11MocMax | REAL | IOD_STR_TCP | 45183 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs11MocTrenutna | REAL | IOD_STR_TCP | 45185 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs11MotorHitrost | REAL | IOD_STR_TCP | 45187 | 0 | 2500 | 0 | 2500 | obr/min | ####.#
STRCrpalkeGrfs11MotorTok | REAL | IOD_STR_TCP | 45189 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs11NapajanjeTok | REAL | IOD_STR_TCP | 45191 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs11NastavitevLokalna | REAL | IOD_STR_TCP | 45193
STRCrpalkeGrfs11NastavitevTrenutna | REAL | IOD_STR_TCP | 45195
STRCrpalkeGrfs11PreklopkaMode | INT | IOD_STR_TCP | 40098
STRCrpalkeGrfs11PretokMax | REAL | IOD_STR_TCP | 45197 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs11PretokMin | REAL | IOD_STR_TCP | 45199 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs11PretokTrenutni | REAL | IOD_STR_TCP | 45201 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs11PritiskMax | REAL | IOD_STR_TCP | 45203 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs11PritiskTrenutni | REAL | IOD_STR_TCP | 45205 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs11ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 45207 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs11ReferencaRemote | REAL | IOD_STR_TCP | 45209 | 0 | 100 | 0 | 100 | % | ####.#
STRCrpalkeGrfs11Relay1setup | INT | IOD_STR_TCP | 40099
STRCrpalkeGrfs11RemoteON | DIGITAL | IOD_STR_TCP | 00073
STRCrpalkeGrfs11RemoteSetupMode1 | INT | IOD_STR_TCP | 40100
STRCrpalkeGrfs11Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 00074
STRCrpalkeGrfs11ResetAlarm | DIGITAL | IOD_STR_TCP | 00075
STRCrpalkeGrfs11ResetAlarmLog | DIGITAL | IOD_STR_TCP | 00076
STRCrpalkeGrfs11ResetDevice | DIGITAL | IOD_STR_TCP | 00077
STRCrpalkeGrfs11SetAutomatic | DIGITAL | IOD_STR_TCP | 00078
STRCrpalkeGrfs11SetConstFreqMode | DIGITAL | IOD_STR_TCP | 00079
STRCrpalkeGrfs11SetConstPress | DIGITAL | IOD_STR_TCP | 00080
STRCrpalkeGrfs11SetLocalMode | DIGITAL | IOD_STR_TCP | 00081
STRCrpalkeGrfs11SetMaxRunMode | DIGITAL | IOD_STR_TCP | 00082
STRCrpalkeGrfs11SetMinRunMode | DIGITAL | IOD_STR_TCP | 00083
STRCrpalkeGrfs11SetPropPress | DIGITAL | IOD_STR_TCP | 00084
STRCrpalkeGrfs11SetReference | DIGITAL | IOD_STR_TCP | 00085
STRCrpalkeGrfs11SetRemoteMode | DIGITAL | IOD_STR_TCP | 00086
STRCrpalkeGrfs11SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 00087
STRCrpalkeGrfs11SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 00088
STRCrpalkeGrfs11SetTwinModeSync | DIGITAL | IOD_STR_TCP | 00089
STRCrpalkeGrfs11Start | DIGITAL | IOD_STR_TCP | 00090
STRCrpalkeGrfs11StatusCrpalke | INT | IOD_STR_TCP | 40101
STRCrpalkeGrfs11StatusMode1 | INT | IOD_STR_TCP | 40102
STRCrpalkeGrfs11StatusMode1co | INT | IOD_STR_TCP | 40103
STRCrpalkeGrfs11StatusMode1op | INT | IOD_STR_TCP | 40104
STRCrpalkeGrfs11StatusMode2 | INT | IOD_STR_TCP | 40105
STRCrpalkeGrfs11StatusMode3 | INT | IOD_STR_TCP | 40106
STRCrpalkeGrfs11StevecUr2h | REAL | IOD_STR_TCP | 45211 |  |  |  |  | 2h
STRCrpalkeGrfs11Stop | DIGITAL | IOD_STR_TCP | 00091
STRCrpalkeGrfs11SystemFeedback | REAL | IOD_STR_TCP | 45213
STRCrpalkeGrfs11SystemReference | REAL | IOD_STR_TCP | 45215
STRCrpalkeGrfs11TemperaturaMotorja | REAL | IOD_STR_TCP | 45217 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeGrfs11UreXC200 | REAL | IOD_STR_TCP | 45219 |  |  |  |  | h | ####.#
STRCrpalkeGrfs12AlarmActiveCode | INT | IOD_STR_TCP | 40107
STRCrpalkeGrfs12AlarmAktiven | DIGITAL | IOD_STR_TCP | 00092
STRCrpalkeGrfs12AlarmCodeLog1 | INT | IOD_STR_TCP | 40108
STRCrpalkeGrfs12AlarmCodeLog2 | INT | IOD_STR_TCP | 40109
STRCrpalkeGrfs12AlarmCodeLog3 | INT | IOD_STR_TCP | 40110
STRCrpalkeGrfs12AlarmCodeLog4 | INT | IOD_STR_TCP | 40111
STRCrpalkeGrfs12AlarmCodeLog5 | INT | IOD_STR_TCP | 40112
STRCrpalkeGrfs12AlarmGroupXVH0 | INT | IOD_STR_TCP | 40113
STRCrpalkeGrfs12AlarmGroupXVH10 | INT | IOD_STR_TCP | 40114
STRCrpalkeGrfs12AlarmGroupXVH11 | INT | IOD_STR_TCP | 40115
STRCrpalkeGrfs12AlarmGroupXVH12 | INT | IOD_STR_TCP | 40116
STRCrpalkeGrfs12AlarmGroupXVH13 | INT | IOD_STR_TCP | 40117
STRCrpalkeGrfs12AlarmGroupXVH14 | INT | IOD_STR_TCP | 40118
STRCrpalkeGrfs12AlarmGroupXVH15 | INT | IOD_STR_TCP | 40119
STRCrpalkeGrfs12AlarmGroupXVH16 | INT | IOD_STR_TCP | 40120
STRCrpalkeGrfs12AlarmGroupXVH1 | INT | IOD_STR_TCP | 40121
STRCrpalkeGrfs12AlarmGroupXVH2 | INT | IOD_STR_TCP | 40122
STRCrpalkeGrfs12AlarmGroupXVH3 | INT | IOD_STR_TCP | 40123
STRCrpalkeGrfs12AlarmGroupXVH4 | INT | IOD_STR_TCP | 40124
STRCrpalkeGrfs12AlarmGroupXVH5 | INT | IOD_STR_TCP | 40125
STRCrpalkeGrfs12AlarmGroupXVH6 | INT | IOD_STR_TCP | 40126
STRCrpalkeGrfs12AlarmGroupXVH7 | INT | IOD_STR_TCP | 40127
STRCrpalkeGrfs12AlarmGroupXVH8 | INT | IOD_STR_TCP | 40128
STRCrpalkeGrfs12AlarmGroupXVH9 | INT | IOD_STR_TCP | 40129
STRCrpalkeGrfs12AlarmQSD1 | INT | IOD_STR_TCP | 40130
STRCrpalkeGrfs12AlarmQSD2 | INT | IOD_STR_TCP | 40131
STRCrpalkeGrfs12AlarmStart1 | INT | IOD_STR_TCP | 40132
STRCrpalkeGrfs12AlarmStart2 | INT | IOD_STR_TCP | 40133
STRCrpalkeGrfs12AlarmStop1 | INT | IOD_STR_TCP | 40134
STRCrpalkeGrfs12AlarmStop2 | INT | IOD_STR_TCP | 40135
STRCrpalkeGrfs12AlarmStop3 | INT | IOD_STR_TCP | 40136
STRCrpalkeGrfs12AlarmSurv1 | INT | IOD_STR_TCP | 40137
STRCrpalkeGrfs12AlarmSurv2 | INT | IOD_STR_TCP | 40138
STRCrpalkeGrfs12ControlSource | INT | IOD_STR_TCP | 40139
STRCrpalkeGrfs12DeltaSetPoint | REAL | IOD_STR_TCP | 45221
STRCrpalkeGrfs12Deluje | DIGITAL | IOD_STR_TCP | 00093
STRCrpalkeGrfs12EnergijaPoraba | REAL | IOD_STR_TCP | 45223 |  |  |  |  | kWh | ####.#
STRCrpalkeGrfs12ExternInputSetup | INT | IOD_STR_TCP | 40140
STRCrpalkeGrfs12ExternInputsStatus | INT | IOD_STR_TCP | 40141
STRCrpalkeGrfs12FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 45225 | 0 | 500 | 0 | 500 | V | ####.#
STRCrpalkeGrfs12FrekPretvornikDCTok | REAL | IOD_STR_TCP | 45227 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs12FreqMax | REAL | IOD_STR_TCP | 45229 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs12FreqMin | REAL | IOD_STR_TCP | 45231 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs12FreqUpper | REAL | IOD_STR_TCP | 45233 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs12LocalMode | DIGITAL | IOD_STR_TCP | 00094
STRCrpalkeGrfs12LocalSetupMode1 | INT | IOD_STR_TCP | 40142
STRCrpalkeGrfs12MocMax | REAL | IOD_STR_TCP | 45235 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs12MocTrenutna | REAL | IOD_STR_TCP | 45237 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs12MotorHitrost | REAL | IOD_STR_TCP | 45239 | 0 | 2500 | 0 | 2500 | obr/min | ####.#
STRCrpalkeGrfs12MotorTok | REAL | IOD_STR_TCP | 45241 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs12NapajanjeTok | REAL | IOD_STR_TCP | 45243 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs12NastavitevLokalna | REAL | IOD_STR_TCP | 45245
STRCrpalkeGrfs12NastavitevTrenutna | REAL | IOD_STR_TCP | 45247
STRCrpalkeGrfs12PreklopkaMode | INT | IOD_STR_TCP | 40143
STRCrpalkeGrfs12PretokMax | REAL | IOD_STR_TCP | 45249 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs12PretokMin | REAL | IOD_STR_TCP | 45251 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs12PretokTrenutni | REAL | IOD_STR_TCP | 45253 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs12PritiskMax | REAL | IOD_STR_TCP | 45255 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs12PritiskTrenutni | REAL | IOD_STR_TCP | 45257 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs12ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 45259 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs12ReferencaRemote | REAL | IOD_STR_TCP | 45261 | 0 | 100 | 0 | 100 | % | ####.#
STRCrpalkeGrfs12Relay1setup | INT | IOD_STR_TCP | 40144
STRCrpalkeGrfs12RemoteON | DIGITAL | IOD_STR_TCP | 00095
STRCrpalkeGrfs12RemoteSetupMode1 | INT | IOD_STR_TCP | 40145
STRCrpalkeGrfs12Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 00096
STRCrpalkeGrfs12ResetAlarm | DIGITAL | IOD_STR_TCP | 00097
STRCrpalkeGrfs12ResetAlarmLog | DIGITAL | IOD_STR_TCP | 00098
STRCrpalkeGrfs12ResetDevice | DIGITAL | IOD_STR_TCP | 00099
STRCrpalkeGrfs12SetAutomatic | DIGITAL | IOD_STR_TCP | 00100
STRCrpalkeGrfs12SetConstFreqMode | DIGITAL | IOD_STR_TCP | 00101
STRCrpalkeGrfs12SetConstPress | DIGITAL | IOD_STR_TCP | 00102
STRCrpalkeGrfs12SetLocalMode | DIGITAL | IOD_STR_TCP | 00103
STRCrpalkeGrfs12SetMaxRunMode | DIGITAL | IOD_STR_TCP | 00104
STRCrpalkeGrfs12SetMinRunMode | DIGITAL | IOD_STR_TCP | 00105
STRCrpalkeGrfs12SetPropPress | DIGITAL | IOD_STR_TCP | 00106
STRCrpalkeGrfs12SetReference | DIGITAL | IOD_STR_TCP | 00107
STRCrpalkeGrfs12SetRemoteMode | DIGITAL | IOD_STR_TCP | 00108
STRCrpalkeGrfs12SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 00109
STRCrpalkeGrfs12SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 00110
STRCrpalkeGrfs12SetTwinModeSync | DIGITAL | IOD_STR_TCP | 00111
STRCrpalkeGrfs12Start | DIGITAL | IOD_STR_TCP | 00112
STRCrpalkeGrfs12StatusCrpalke | INT | IOD_STR_TCP | 40146
STRCrpalkeGrfs12StatusMode1 | INT | IOD_STR_TCP | 40147
STRCrpalkeGrfs12StatusMode1co | INT | IOD_STR_TCP | 40148
STRCrpalkeGrfs12StatusMode1op | INT | IOD_STR_TCP | 40149
STRCrpalkeGrfs12StatusMode2 | INT | IOD_STR_TCP | 40150
STRCrpalkeGrfs12StatusMode3 | INT | IOD_STR_TCP | 40151
STRCrpalkeGrfs12StevecUr2h | REAL | IOD_STR_TCP | 45263 |  |  |  |  | 2h
STRCrpalkeGrfs12Stop | DIGITAL | IOD_STR_TCP | 00113
STRCrpalkeGrfs12SystemFeedback | REAL | IOD_STR_TCP | 45265
STRCrpalkeGrfs12SystemReference | REAL | IOD_STR_TCP | 45267
STRCrpalkeGrfs12TemperaturaMotorja | REAL | IOD_STR_TCP | 45269 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeGrfs12UreXC200 | REAL | IOD_STR_TCP | 45271 |  |  |  |  | h | ####.#
STRCrpalkeGrfs13AlarmActiveCode | INT | IOD_STR_TCP | 40152
STRCrpalkeGrfs13AlarmAktiven | DIGITAL | IOD_STR_TCP | 00114
STRCrpalkeGrfs13AlarmCodeLog1 | INT | IOD_STR_TCP | 40153
STRCrpalkeGrfs13AlarmCodeLog2 | INT | IOD_STR_TCP | 40154
STRCrpalkeGrfs13AlarmCodeLog3 | INT | IOD_STR_TCP | 40155
STRCrpalkeGrfs13AlarmCodeLog4 | INT | IOD_STR_TCP | 40156
STRCrpalkeGrfs13AlarmCodeLog5 | INT | IOD_STR_TCP | 40157
STRCrpalkeGrfs13AlarmGroupXVH0 | INT | IOD_STR_TCP | 40158
STRCrpalkeGrfs13AlarmGroupXVH10 | INT | IOD_STR_TCP | 40159
STRCrpalkeGrfs13AlarmGroupXVH11 | INT | IOD_STR_TCP | 40160
STRCrpalkeGrfs13AlarmGroupXVH12 | INT | IOD_STR_TCP | 40161
STRCrpalkeGrfs13AlarmGroupXVH13 | INT | IOD_STR_TCP | 40162
STRCrpalkeGrfs13AlarmGroupXVH14 | INT | IOD_STR_TCP | 40163
STRCrpalkeGrfs13AlarmGroupXVH15 | INT | IOD_STR_TCP | 40164
STRCrpalkeGrfs13AlarmGroupXVH16 | INT | IOD_STR_TCP | 40165
STRCrpalkeGrfs13AlarmGroupXVH1 | INT | IOD_STR_TCP | 40166
STRCrpalkeGrfs13AlarmGroupXVH2 | INT | IOD_STR_TCP | 40167
STRCrpalkeGrfs13AlarmGroupXVH3 | INT | IOD_STR_TCP | 40168
STRCrpalkeGrfs13AlarmGroupXVH4 | INT | IOD_STR_TCP | 40169
STRCrpalkeGrfs13AlarmGroupXVH5 | INT | IOD_STR_TCP | 40170
STRCrpalkeGrfs13AlarmGroupXVH6 | INT | IOD_STR_TCP | 40171
STRCrpalkeGrfs13AlarmGroupXVH7 | INT | IOD_STR_TCP | 40172
STRCrpalkeGrfs13AlarmGroupXVH8 | INT | IOD_STR_TCP | 40173
STRCrpalkeGrfs13AlarmGroupXVH9 | INT | IOD_STR_TCP | 40174
STRCrpalkeGrfs13AlarmQSD1 | INT | IOD_STR_TCP | 40175
STRCrpalkeGrfs13AlarmQSD2 | INT | IOD_STR_TCP | 40176
STRCrpalkeGrfs13AlarmStart1 | INT | IOD_STR_TCP | 40177
STRCrpalkeGrfs13AlarmStart2 | INT | IOD_STR_TCP | 40178
STRCrpalkeGrfs13AlarmStop1 | INT | IOD_STR_TCP | 40179
STRCrpalkeGrfs13AlarmStop2 | INT | IOD_STR_TCP | 40180
STRCrpalkeGrfs13AlarmStop3 | INT | IOD_STR_TCP | 40181
STRCrpalkeGrfs13AlarmSurv1 | INT | IOD_STR_TCP | 40182
STRCrpalkeGrfs13AlarmSurv2 | INT | IOD_STR_TCP | 40183
STRCrpalkeGrfs13ControlSource | INT | IOD_STR_TCP | 40184
STRCrpalkeGrfs13DeltaSetPoint | REAL | IOD_STR_TCP | 45273
STRCrpalkeGrfs13Deluje | DIGITAL | IOD_STR_TCP | 00115
STRCrpalkeGrfs13EnergijaPoraba | REAL | IOD_STR_TCP | 45275 |  |  |  |  | kWh | ####.#
STRCrpalkeGrfs13ExternInputSetup | INT | IOD_STR_TCP | 40185
STRCrpalkeGrfs13ExternInputsStatus | INT | IOD_STR_TCP | 40186
STRCrpalkeGrfs13FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 45277 | 0 | 500 | 0 | 500 | V | ####.#
STRCrpalkeGrfs13FrekPretvornikDCTok | REAL | IOD_STR_TCP | 45279 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs13FreqMax | REAL | IOD_STR_TCP | 45281 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs13FreqMin | REAL | IOD_STR_TCP | 45283 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs13FreqUpper | REAL | IOD_STR_TCP | 45285 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs13LocalMode | DIGITAL | IOD_STR_TCP | 00116
STRCrpalkeGrfs13LocalSetupMode1 | INT | IOD_STR_TCP | 40187
STRCrpalkeGrfs13MocMax | REAL | IOD_STR_TCP | 45287 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs13MocTrenutna | REAL | IOD_STR_TCP | 45289 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs13MotorHitrost | REAL | IOD_STR_TCP | 45291 | 0 | 2500 | 0 | 2500 | obr/min | ####.#
STRCrpalkeGrfs13MotorTok | REAL | IOD_STR_TCP | 45293 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs13NapajanjeTok | REAL | IOD_STR_TCP | 45295 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs13NastavitevLokalna | REAL | IOD_STR_TCP | 45297
STRCrpalkeGrfs13NastavitevTrenutna | REAL | IOD_STR_TCP | 45299
STRCrpalkeGrfs13PreklopkaMode | INT | IOD_STR_TCP | 40188
STRCrpalkeGrfs13PretokMax | REAL | IOD_STR_TCP | 45301 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs13PretokMin | REAL | IOD_STR_TCP | 45303 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs13PretokTrenutni | REAL | IOD_STR_TCP | 45305 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs13PritiskMax | REAL | IOD_STR_TCP | 45307 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs13PritiskTrenutni | REAL | IOD_STR_TCP | 45309 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs13ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 45311 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs13ReferencaRemote | REAL | IOD_STR_TCP | 45313 | 0 | 100 | 0 | 100 | % | ####.#
STRCrpalkeGrfs13Relay1setup | INT | IOD_STR_TCP | 40189
STRCrpalkeGrfs13RemoteON | DIGITAL | IOD_STR_TCP | 00117
STRCrpalkeGrfs13RemoteSetupMode1 | INT | IOD_STR_TCP | 40190
STRCrpalkeGrfs13Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 00118
STRCrpalkeGrfs13ResetAlarm | DIGITAL | IOD_STR_TCP | 00119
STRCrpalkeGrfs13ResetAlarmLog | DIGITAL | IOD_STR_TCP | 00120
STRCrpalkeGrfs13ResetDevice | DIGITAL | IOD_STR_TCP | 00121
STRCrpalkeGrfs13SetAutomatic | DIGITAL | IOD_STR_TCP | 00122
STRCrpalkeGrfs13SetConstFreqMode | DIGITAL | IOD_STR_TCP | 00123
STRCrpalkeGrfs13SetConstPress | DIGITAL | IOD_STR_TCP | 00124
STRCrpalkeGrfs13SetLocalMode | DIGITAL | IOD_STR_TCP | 00125
STRCrpalkeGrfs13SetMaxRunMode | DIGITAL | IOD_STR_TCP | 00126
STRCrpalkeGrfs13SetMinRunMode | DIGITAL | IOD_STR_TCP | 00127
STRCrpalkeGrfs13SetPropPress | DIGITAL | IOD_STR_TCP | 00128
STRCrpalkeGrfs13SetReference | DIGITAL | IOD_STR_TCP | 00129
STRCrpalkeGrfs13SetRemoteMode | DIGITAL | IOD_STR_TCP | 00130
STRCrpalkeGrfs13SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 00131
STRCrpalkeGrfs13SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 00132
STRCrpalkeGrfs13SetTwinModeSync | DIGITAL | IOD_STR_TCP | 00133
STRCrpalkeGrfs13Start | DIGITAL | IOD_STR_TCP | 00134
STRCrpalkeGrfs13StatusCrpalke | INT | IOD_STR_TCP | 40191
STRCrpalkeGrfs13StatusMode1 | INT | IOD_STR_TCP | 40192
STRCrpalkeGrfs13StatusMode1co | INT | IOD_STR_TCP | 40193
STRCrpalkeGrfs13StatusMode1op | INT | IOD_STR_TCP | 40194
STRCrpalkeGrfs13StatusMode2 | INT | IOD_STR_TCP | 40195
STRCrpalkeGrfs13StatusMode3 | INT | IOD_STR_TCP | 40196
STRCrpalkeGrfs13StevecUr2h | REAL | IOD_STR_TCP | 45315 |  |  |  |  | 2h
STRCrpalkeGrfs13Stop | DIGITAL | IOD_STR_TCP | 00135
STRCrpalkeGrfs13SystemFeedback | REAL | IOD_STR_TCP | 45317
STRCrpalkeGrfs13SystemReference | REAL | IOD_STR_TCP | 45319
STRCrpalkeGrfs13TemperaturaMotorja | REAL | IOD_STR_TCP | 45321 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeGrfs13UreXC200 | REAL | IOD_STR_TCP | 45323 |  |  |  |  | h | ####.#
STRCrpalkeGrfs14AlarmActiveCode | INT | IOD_STR_TCP | 40197
STRCrpalkeGrfs14AlarmAktiven | DIGITAL | IOD_STR_TCP | 00136
STRCrpalkeGrfs14AlarmCodeLog1 | INT | IOD_STR_TCP | 40198
STRCrpalkeGrfs14AlarmCodeLog2 | INT | IOD_STR_TCP | 40199
STRCrpalkeGrfs14AlarmCodeLog3 | INT | IOD_STR_TCP | 40200
STRCrpalkeGrfs14AlarmCodeLog4 | INT | IOD_STR_TCP | 40201
STRCrpalkeGrfs14AlarmCodeLog5 | INT | IOD_STR_TCP | 40202
STRCrpalkeGrfs14AlarmGroupXVH0 | INT | IOD_STR_TCP | 40203
STRCrpalkeGrfs14AlarmGroupXVH10 | INT | IOD_STR_TCP | 40204
STRCrpalkeGrfs14AlarmGroupXVH11 | INT | IOD_STR_TCP | 40205
STRCrpalkeGrfs14AlarmGroupXVH12 | INT | IOD_STR_TCP | 40206
STRCrpalkeGrfs14AlarmGroupXVH13 | INT | IOD_STR_TCP | 40207
STRCrpalkeGrfs14AlarmGroupXVH14 | INT | IOD_STR_TCP | 40208
STRCrpalkeGrfs14AlarmGroupXVH15 | INT | IOD_STR_TCP | 40209
STRCrpalkeGrfs14AlarmGroupXVH16 | INT | IOD_STR_TCP | 40210
STRCrpalkeGrfs14AlarmGroupXVH1 | INT | IOD_STR_TCP | 40211
STRCrpalkeGrfs14AlarmGroupXVH2 | INT | IOD_STR_TCP | 40212
STRCrpalkeGrfs14AlarmGroupXVH3 | INT | IOD_STR_TCP | 40213
STRCrpalkeGrfs14AlarmGroupXVH4 | INT | IOD_STR_TCP | 40214
STRCrpalkeGrfs14AlarmGroupXVH5 | INT | IOD_STR_TCP | 40215
STRCrpalkeGrfs14AlarmGroupXVH6 | INT | IOD_STR_TCP | 40216
STRCrpalkeGrfs14AlarmGroupXVH7 | INT | IOD_STR_TCP | 40217
STRCrpalkeGrfs14AlarmGroupXVH8 | INT | IOD_STR_TCP | 40218
STRCrpalkeGrfs14AlarmGroupXVH9 | INT | IOD_STR_TCP | 40219
STRCrpalkeGrfs14AlarmQSD1 | INT | IOD_STR_TCP | 40220
STRCrpalkeGrfs14AlarmQSD2 | INT | IOD_STR_TCP | 40221
STRCrpalkeGrfs14AlarmStart1 | INT | IOD_STR_TCP | 40222
STRCrpalkeGrfs14AlarmStart2 | INT | IOD_STR_TCP | 40223
STRCrpalkeGrfs14AlarmStop1 | INT | IOD_STR_TCP | 40224
STRCrpalkeGrfs14AlarmStop2 | INT | IOD_STR_TCP | 40225
STRCrpalkeGrfs14AlarmStop3 | INT | IOD_STR_TCP | 40226
STRCrpalkeGrfs14AlarmSurv1 | INT | IOD_STR_TCP | 40227
STRCrpalkeGrfs14AlarmSurv2 | INT | IOD_STR_TCP | 40228
STRCrpalkeGrfs14ControlSource | INT | IOD_STR_TCP | 40229
STRCrpalkeGrfs14DeltaSetPoint | REAL | IOD_STR_TCP | 45325
STRCrpalkeGrfs14Deluje | DIGITAL | IOD_STR_TCP | 00137
STRCrpalkeGrfs14EnergijaPoraba | REAL | IOD_STR_TCP | 45327 |  |  |  |  | kWh | ####.#
STRCrpalkeGrfs14ExternInputSetup | INT | IOD_STR_TCP | 40230
STRCrpalkeGrfs14ExternInputsStatus | INT | IOD_STR_TCP | 40231
STRCrpalkeGrfs14FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 45329 | 0 | 500 | 0 | 500 | V | ####.#
STRCrpalkeGrfs14FrekPretvornikDCTok | REAL | IOD_STR_TCP | 45331 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs14FreqMax | REAL | IOD_STR_TCP | 45333 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs14FreqMin | REAL | IOD_STR_TCP | 45335 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs14FreqUpper | REAL | IOD_STR_TCP | 45337 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs14LocalMode | DIGITAL | IOD_STR_TCP | 00138
STRCrpalkeGrfs14LocalSetupMode1 | INT | IOD_STR_TCP | 40232
STRCrpalkeGrfs14MocMax | REAL | IOD_STR_TCP | 45339 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs14MocTrenutna | REAL | IOD_STR_TCP | 45341 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs14MotorHitrost | REAL | IOD_STR_TCP | 45343 | 0 | 2500 | 0 | 2500 | obr/min | ####.#
STRCrpalkeGrfs14MotorTok | REAL | IOD_STR_TCP | 45345 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs14NapajanjeTok | REAL | IOD_STR_TCP | 45347 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs14NastavitevLokalna | REAL | IOD_STR_TCP | 45349
STRCrpalkeGrfs14NastavitevTrenutna | REAL | IOD_STR_TCP | 45351
STRCrpalkeGrfs14PreklopkaMode | INT | IOD_STR_TCP | 40233
STRCrpalkeGrfs14PretokMax | REAL | IOD_STR_TCP | 45353 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs14PretokMin | REAL | IOD_STR_TCP | 45355 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs14PretokTrenutni | REAL | IOD_STR_TCP | 45357 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs14PritiskMax | REAL | IOD_STR_TCP | 45359 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs14PritiskTrenutni | REAL | IOD_STR_TCP | 45361 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs14ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 45363 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs14ReferencaRemote | REAL | IOD_STR_TCP | 45365 | 0 | 100 | 0 | 100 | % | ####.#
STRCrpalkeGrfs14Relay1setup | INT | IOD_STR_TCP | 40234
STRCrpalkeGrfs14RemoteON | DIGITAL | IOD_STR_TCP | 00139
STRCrpalkeGrfs14RemoteSetupMode1 | INT | IOD_STR_TCP | 40235
STRCrpalkeGrfs14Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 00140
STRCrpalkeGrfs14ResetAlarm | DIGITAL | IOD_STR_TCP | 00141
STRCrpalkeGrfs14ResetAlarmLog | DIGITAL | IOD_STR_TCP | 00142
STRCrpalkeGrfs14ResetDevice | DIGITAL | IOD_STR_TCP | 00143
STRCrpalkeGrfs14SetAutomatic | DIGITAL | IOD_STR_TCP | 00144
STRCrpalkeGrfs14SetConstFreqMode | DIGITAL | IOD_STR_TCP | 00145
STRCrpalkeGrfs14SetConstPress | DIGITAL | IOD_STR_TCP | 00146
STRCrpalkeGrfs14SetLocalMode | DIGITAL | IOD_STR_TCP | 00147
STRCrpalkeGrfs14SetMaxRunMode | DIGITAL | IOD_STR_TCP | 00148
STRCrpalkeGrfs14SetMinRunMode | DIGITAL | IOD_STR_TCP | 00149
STRCrpalkeGrfs14SetPropPress | DIGITAL | IOD_STR_TCP | 00150
STRCrpalkeGrfs14SetReference | DIGITAL | IOD_STR_TCP | 00151
STRCrpalkeGrfs14SetRemoteMode | DIGITAL | IOD_STR_TCP | 00152
STRCrpalkeGrfs14SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 00153
STRCrpalkeGrfs14SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 00154
STRCrpalkeGrfs14SetTwinModeSync | DIGITAL | IOD_STR_TCP | 00155
STRCrpalkeGrfs14Start | DIGITAL | IOD_STR_TCP | 00156
STRCrpalkeGrfs14StatusCrpalke | INT | IOD_STR_TCP | 40236
STRCrpalkeGrfs14StatusMode1 | INT | IOD_STR_TCP | 40237
STRCrpalkeGrfs14StatusMode1co | INT | IOD_STR_TCP | 40238
STRCrpalkeGrfs14StatusMode1op | INT | IOD_STR_TCP | 40239
STRCrpalkeGrfs14StatusMode2 | INT | IOD_STR_TCP | 40240
STRCrpalkeGrfs14StatusMode3 | INT | IOD_STR_TCP | 40241
STRCrpalkeGrfs14StevecUr2h | REAL | IOD_STR_TCP | 45367 |  |  |  |  | 2h
STRCrpalkeGrfs14Stop | DIGITAL | IOD_STR_TCP | 00157
STRCrpalkeGrfs14SystemFeedback | REAL | IOD_STR_TCP | 45369
STRCrpalkeGrfs14SystemReference | REAL | IOD_STR_TCP | 45371
STRCrpalkeGrfs14TemperaturaMotorja | REAL | IOD_STR_TCP | 45373 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeGrfs14UreXC200 | REAL | IOD_STR_TCP | 45375 |  |  |  |  | h | ####.#
STRCrpalkeGrfs1AlarmActiveCode | INT | IOD_STR_TCP | 40242
STRCrpalkeGrfs1AlarmAktiven | DIGITAL | IOD_STR_TCP | 00158
STRCrpalkeGrfs1AlarmCodeLog1 | INT | IOD_STR_TCP | 40243
STRCrpalkeGrfs1AlarmCodeLog2 | INT | IOD_STR_TCP | 40244
STRCrpalkeGrfs1AlarmCodeLog3 | INT | IOD_STR_TCP | 40245
STRCrpalkeGrfs1AlarmCodeLog4 | INT | IOD_STR_TCP | 40246
STRCrpalkeGrfs1AlarmCodeLog5 | INT | IOD_STR_TCP | 40247
STRCrpalkeGrfs1AlarmGroupXVH0 | INT | IOD_STR_TCP | 40248
STRCrpalkeGrfs1AlarmGroupXVH10 | INT | IOD_STR_TCP | 40249
STRCrpalkeGrfs1AlarmGroupXVH11 | INT | IOD_STR_TCP | 40250
STRCrpalkeGrfs1AlarmGroupXVH12 | INT | IOD_STR_TCP | 40251
STRCrpalkeGrfs1AlarmGroupXVH13 | INT | IOD_STR_TCP | 40252
STRCrpalkeGrfs1AlarmGroupXVH14 | INT | IOD_STR_TCP | 40253
STRCrpalkeGrfs1AlarmGroupXVH15 | INT | IOD_STR_TCP | 40254
STRCrpalkeGrfs1AlarmGroupXVH16 | INT | IOD_STR_TCP | 40255
STRCrpalkeGrfs1AlarmGroupXVH1 | INT | IOD_STR_TCP | 40256
STRCrpalkeGrfs1AlarmGroupXVH2 | INT | IOD_STR_TCP | 40257
STRCrpalkeGrfs1AlarmGroupXVH3 | INT | IOD_STR_TCP | 40258
STRCrpalkeGrfs1AlarmGroupXVH4 | INT | IOD_STR_TCP | 40259
STRCrpalkeGrfs1AlarmGroupXVH5 | INT | IOD_STR_TCP | 40260
STRCrpalkeGrfs1AlarmGroupXVH6 | INT | IOD_STR_TCP | 40261
STRCrpalkeGrfs1AlarmGroupXVH7 | INT | IOD_STR_TCP | 40262
STRCrpalkeGrfs1AlarmGroupXVH8 | INT | IOD_STR_TCP | 40263
STRCrpalkeGrfs1AlarmGroupXVH9 | INT | IOD_STR_TCP | 40264
STRCrpalkeGrfs1AlarmQSD1 | INT | IOD_STR_TCP | 40265
STRCrpalkeGrfs1AlarmQSD2 | INT | IOD_STR_TCP | 40266
STRCrpalkeGrfs1AlarmStart1 | INT | IOD_STR_TCP | 40267
STRCrpalkeGrfs1AlarmStart2 | INT | IOD_STR_TCP | 40268
STRCrpalkeGrfs1AlarmStop1 | INT | IOD_STR_TCP | 40269
STRCrpalkeGrfs1AlarmStop2 | INT | IOD_STR_TCP | 40270
STRCrpalkeGrfs1AlarmStop3 | INT | IOD_STR_TCP | 40271
STRCrpalkeGrfs1AlarmSurv1 | INT | IOD_STR_TCP | 40272
STRCrpalkeGrfs1AlarmSurv2 | INT | IOD_STR_TCP | 40273
STRCrpalkeGrfs1ControlSource | INT | IOD_STR_TCP | 40274
STRCrpalkeGrfs1DeltaSetPoint | REAL | IOD_STR_TCP | 45377
STRCrpalkeGrfs1Deluje | DIGITAL | IOD_STR_TCP | 00159
STRCrpalkeGrfs1EnergijaPoraba | REAL | IOD_STR_TCP | 45379 |  |  |  |  | kWh | ####.#
STRCrpalkeGrfs1ExternInputSetup | INT | IOD_STR_TCP | 40275
STRCrpalkeGrfs1ExternInputsStatus | INT | IOD_STR_TCP | 40276
STRCrpalkeGrfs1FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 45381 | 0 | 500 | 0 | 500 | V | ####.#
STRCrpalkeGrfs1FrekPretvornikDCTok | REAL | IOD_STR_TCP | 45383 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs1FreqMax | REAL | IOD_STR_TCP | 45385 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs1FreqMin | REAL | IOD_STR_TCP | 45387 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs1FreqUpper | REAL | IOD_STR_TCP | 45389 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs1LocalMode | DIGITAL | IOD_STR_TCP | 00160
STRCrpalkeGrfs1LocalSetupMode1 | INT | IOD_STR_TCP | 40277
STRCrpalkeGrfs1MocMax | REAL | IOD_STR_TCP | 45391 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs1MocTrenutna | REAL | IOD_STR_TCP | 45393 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs1MotorHitrost | REAL | IOD_STR_TCP | 45395 | 0 | 2500 | 0 | 2500 | obr/min | ####.#
STRCrpalkeGrfs1MotorTok | REAL | IOD_STR_TCP | 45397 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs1NapajanjeTok | REAL | IOD_STR_TCP | 45399 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs1NastavitevLokalna | REAL | IOD_STR_TCP | 45401
STRCrpalkeGrfs1NastavitevTrenutna | REAL | IOD_STR_TCP | 45403
STRCrpalkeGrfs1PreklopkaMode | INT | IOD_STR_TCP | 40278
STRCrpalkeGrfs1PretokMax | REAL | IOD_STR_TCP | 45405 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs1PretokMin | REAL | IOD_STR_TCP | 45407 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs1PretokTrenutni | REAL | IOD_STR_TCP | 45409 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs1PritiskMax | REAL | IOD_STR_TCP | 45411 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs1PritiskTrenutni | REAL | IOD_STR_TCP | 45413 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs1ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 45415 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs1ReferencaRemote | REAL | IOD_STR_TCP | 45417 | 0 | 100 | 0 | 100 | % | ####.#
STRCrpalkeGrfs1Relay1setup | INT | IOD_STR_TCP | 40279
STRCrpalkeGrfs1RemoteON | DIGITAL | IOD_STR_TCP | 00161
STRCrpalkeGrfs1RemoteSetupMode1 | INT | IOD_STR_TCP | 40280
STRCrpalkeGrfs1Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 00162
STRCrpalkeGrfs1ResetAlarm | DIGITAL | IOD_STR_TCP | 00163
STRCrpalkeGrfs1ResetAlarmLog | DIGITAL | IOD_STR_TCP | 00164
STRCrpalkeGrfs1ResetDevice | DIGITAL | IOD_STR_TCP | 00165
STRCrpalkeGrfs1SetAutomatic | DIGITAL | IOD_STR_TCP | 00166
STRCrpalkeGrfs1SetConstFreqMode | DIGITAL | IOD_STR_TCP | 00167
STRCrpalkeGrfs1SetConstPress | DIGITAL | IOD_STR_TCP | 00168
STRCrpalkeGrfs1SetLocalMode | DIGITAL | IOD_STR_TCP | 00169
STRCrpalkeGrfs1SetMaxRunMode | DIGITAL | IOD_STR_TCP | 00170
STRCrpalkeGrfs1SetMinRunMode | DIGITAL | IOD_STR_TCP | 00171
STRCrpalkeGrfs1SetPropPress | DIGITAL | IOD_STR_TCP | 00172
STRCrpalkeGrfs1SetReference | DIGITAL | IOD_STR_TCP | 00173
STRCrpalkeGrfs1SetRemoteMode | DIGITAL | IOD_STR_TCP | 00174
STRCrpalkeGrfs1SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 00175
STRCrpalkeGrfs1SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 00176
STRCrpalkeGrfs1SetTwinModeSync | DIGITAL | IOD_STR_TCP | 00177
STRCrpalkeGrfs1Start | DIGITAL | IOD_STR_TCP | 00178
STRCrpalkeGrfs1StatusCrpalke | INT | IOD_STR_TCP | 40281
STRCrpalkeGrfs1StatusMode1 | INT | IOD_STR_TCP | 40282
STRCrpalkeGrfs1StatusMode1co | INT | IOD_STR_TCP | 40283
STRCrpalkeGrfs1StatusMode1op | INT | IOD_STR_TCP | 40284
STRCrpalkeGrfs1StatusMode2 | INT | IOD_STR_TCP | 40285
STRCrpalkeGrfs1StatusMode3 | INT | IOD_STR_TCP | 40286
STRCrpalkeGrfs1StevecUr2h | REAL | IOD_STR_TCP | 45419 |  |  |  |  | 2h
STRCrpalkeGrfs1Stop | DIGITAL | IOD_STR_TCP | 00179
STRCrpalkeGrfs1SystemFeedback | REAL | IOD_STR_TCP | 45421
STRCrpalkeGrfs1SystemReference | REAL | IOD_STR_TCP | 45423
STRCrpalkeGrfs1TemperaturaMotorja | REAL | IOD_STR_TCP | 45425 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeGrfs1UreXC200 | REAL | IOD_STR_TCP | 45427 |  |  |  |  | h | ####.#
STRCrpalkeGrfs2AlarmActiveCode | INT | IOD_STR_TCP | 40287
STRCrpalkeGrfs2AlarmAktiven | DIGITAL | IOD_STR_TCP | 00180
STRCrpalkeGrfs2AlarmCodeLog1 | INT | IOD_STR_TCP | 40288
STRCrpalkeGrfs2AlarmCodeLog2 | INT | IOD_STR_TCP | 40289
STRCrpalkeGrfs2AlarmCodeLog3 | INT | IOD_STR_TCP | 40290
STRCrpalkeGrfs2AlarmCodeLog4 | INT | IOD_STR_TCP | 40291
STRCrpalkeGrfs2AlarmCodeLog5 | INT | IOD_STR_TCP | 40292
STRCrpalkeGrfs2AlarmGroupXVH0 | INT | IOD_STR_TCP | 40293
STRCrpalkeGrfs2AlarmGroupXVH10 | INT | IOD_STR_TCP | 40294
STRCrpalkeGrfs2AlarmGroupXVH11 | INT | IOD_STR_TCP | 40295
STRCrpalkeGrfs2AlarmGroupXVH12 | INT | IOD_STR_TCP | 40296
STRCrpalkeGrfs2AlarmGroupXVH13 | INT | IOD_STR_TCP | 40297
STRCrpalkeGrfs2AlarmGroupXVH14 | INT | IOD_STR_TCP | 40298
STRCrpalkeGrfs2AlarmGroupXVH15 | INT | IOD_STR_TCP | 40299
STRCrpalkeGrfs2AlarmGroupXVH16 | INT | IOD_STR_TCP | 40300
STRCrpalkeGrfs2AlarmGroupXVH1 | INT | IOD_STR_TCP | 40301
STRCrpalkeGrfs2AlarmGroupXVH2 | INT | IOD_STR_TCP | 40302
STRCrpalkeGrfs2AlarmGroupXVH3 | INT | IOD_STR_TCP | 40303
STRCrpalkeGrfs2AlarmGroupXVH4 | INT | IOD_STR_TCP | 40304
STRCrpalkeGrfs2AlarmGroupXVH5 | INT | IOD_STR_TCP | 40305
STRCrpalkeGrfs2AlarmGroupXVH6 | INT | IOD_STR_TCP | 40306
STRCrpalkeGrfs2AlarmGroupXVH7 | INT | IOD_STR_TCP | 40307
STRCrpalkeGrfs2AlarmGroupXVH8 | INT | IOD_STR_TCP | 40308
STRCrpalkeGrfs2AlarmGroupXVH9 | INT | IOD_STR_TCP | 40309
STRCrpalkeGrfs2AlarmQSD1 | INT | IOD_STR_TCP | 40310
STRCrpalkeGrfs2AlarmQSD2 | INT | IOD_STR_TCP | 40311
STRCrpalkeGrfs2AlarmStart1 | INT | IOD_STR_TCP | 40312
STRCrpalkeGrfs2AlarmStart2 | INT | IOD_STR_TCP | 40313
STRCrpalkeGrfs2AlarmStop1 | INT | IOD_STR_TCP | 40314
STRCrpalkeGrfs2AlarmStop2 | INT | IOD_STR_TCP | 40315
STRCrpalkeGrfs2AlarmStop3 | INT | IOD_STR_TCP | 40316
STRCrpalkeGrfs2AlarmSurv1 | INT | IOD_STR_TCP | 40317
STRCrpalkeGrfs2AlarmSurv2 | INT | IOD_STR_TCP | 40318
STRCrpalkeGrfs2ControlSource | INT | IOD_STR_TCP | 40319
STRCrpalkeGrfs2DeltaSetPoint | REAL | IOD_STR_TCP | 45429
STRCrpalkeGrfs2Deluje | DIGITAL | IOD_STR_TCP | 00181
STRCrpalkeGrfs2EnergijaPoraba | REAL | IOD_STR_TCP | 45431 |  |  |  |  | kWh | ####.#
STRCrpalkeGrfs2ExternInputSetup | INT | IOD_STR_TCP | 40320
STRCrpalkeGrfs2ExternInputsStatus | INT | IOD_STR_TCP | 40321
STRCrpalkeGrfs2FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 45433 | 0 | 500 | 0 | 500 | V | ####.#
STRCrpalkeGrfs2FrekPretvornikDCTok | REAL | IOD_STR_TCP | 45435 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs2FreqMax | REAL | IOD_STR_TCP | 45437 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs2FreqMin | REAL | IOD_STR_TCP | 45439 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs2FreqUpper | REAL | IOD_STR_TCP | 45441 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs2LocalMode | DIGITAL | IOD_STR_TCP | 00182
STRCrpalkeGrfs2LocalSetupMode1 | INT | IOD_STR_TCP | 40322
STRCrpalkeGrfs2MocMax | REAL | IOD_STR_TCP | 45443 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs2MocTrenutna | REAL | IOD_STR_TCP | 45445 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs2MotorHitrost | REAL | IOD_STR_TCP | 45447 | 0 | 2500 | 0 | 2500 | obr/min | ####.#
STRCrpalkeGrfs2MotorTok | REAL | IOD_STR_TCP | 45449 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs2NapajanjeTok | REAL | IOD_STR_TCP | 45451 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs2NastavitevLokalna | REAL | IOD_STR_TCP | 45453
STRCrpalkeGrfs2NastavitevTrenutna | REAL | IOD_STR_TCP | 45455
STRCrpalkeGrfs2PreklopkaMode | INT | IOD_STR_TCP | 40323
STRCrpalkeGrfs2PretokMax | REAL | IOD_STR_TCP | 45457 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs2PretokMin | REAL | IOD_STR_TCP | 45459 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs2PretokTrenutni | REAL | IOD_STR_TCP | 45461 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs2PritiskMax | REAL | IOD_STR_TCP | 45463 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs2PritiskTrenutni | REAL | IOD_STR_TCP | 45465 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs2ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 45467 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs2ReferencaRemote | REAL | IOD_STR_TCP | 45469 | 0 | 100 | 0 | 100 | % | ####.#
STRCrpalkeGrfs2Relay1setup | INT | IOD_STR_TCP | 40324
STRCrpalkeGrfs2RemoteON | DIGITAL | IOD_STR_TCP | 00183
STRCrpalkeGrfs2RemoteSetupMode1 | INT | IOD_STR_TCP | 40325
STRCrpalkeGrfs2Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 00184
STRCrpalkeGrfs2ResetAlarm | DIGITAL | IOD_STR_TCP | 00185
STRCrpalkeGrfs2ResetAlarmLog | DIGITAL | IOD_STR_TCP | 00186
STRCrpalkeGrfs2ResetDevice | DIGITAL | IOD_STR_TCP | 00187
STRCrpalkeGrfs2SetAutomatic | DIGITAL | IOD_STR_TCP | 00188
STRCrpalkeGrfs2SetConstFreqMode | DIGITAL | IOD_STR_TCP | 00189
STRCrpalkeGrfs2SetConstPress | DIGITAL | IOD_STR_TCP | 00190
STRCrpalkeGrfs2SetLocalMode | DIGITAL | IOD_STR_TCP | 00191
STRCrpalkeGrfs2SetMaxRunMode | DIGITAL | IOD_STR_TCP | 00192
STRCrpalkeGrfs2SetMinRunMode | DIGITAL | IOD_STR_TCP | 00193
STRCrpalkeGrfs2SetPropPress | DIGITAL | IOD_STR_TCP | 00194
STRCrpalkeGrfs2SetReference | DIGITAL | IOD_STR_TCP | 00195
STRCrpalkeGrfs2SetRemoteMode | DIGITAL | IOD_STR_TCP | 00196
STRCrpalkeGrfs2SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 00197
STRCrpalkeGrfs2SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 00198
STRCrpalkeGrfs2SetTwinModeSync | DIGITAL | IOD_STR_TCP | 00199
STRCrpalkeGrfs2Start | DIGITAL | IOD_STR_TCP | 00200
STRCrpalkeGrfs2StatusCrpalke | INT | IOD_STR_TCP | 40326
STRCrpalkeGrfs2StatusMode1 | INT | IOD_STR_TCP | 40327
STRCrpalkeGrfs2StatusMode1co | INT | IOD_STR_TCP | 40328
STRCrpalkeGrfs2StatusMode1op | INT | IOD_STR_TCP | 40329
STRCrpalkeGrfs2StatusMode2 | INT | IOD_STR_TCP | 40330
STRCrpalkeGrfs2StatusMode3 | INT | IOD_STR_TCP | 40331
STRCrpalkeGrfs2StevecUr2h | REAL | IOD_STR_TCP | 45471 |  |  |  |  | 2h
STRCrpalkeGrfs2Stop | DIGITAL | IOD_STR_TCP | 00201
STRCrpalkeGrfs2SystemFeedback | REAL | IOD_STR_TCP | 45473
STRCrpalkeGrfs2SystemReference | REAL | IOD_STR_TCP | 45475
STRCrpalkeGrfs2TemperaturaMotorja | REAL | IOD_STR_TCP | 45477 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeGrfs2UreXC200 | REAL | IOD_STR_TCP | 45479 |  |  |  |  | h | ####.#
STRCrpalkeGrfs3AlarmActiveCode | INT | IOD_STR_TCP | 40332
STRCrpalkeGrfs3AlarmAktiven | DIGITAL | IOD_STR_TCP | 00202
STRCrpalkeGrfs3AlarmCodeLog1 | INT | IOD_STR_TCP | 40333
STRCrpalkeGrfs3AlarmCodeLog2 | INT | IOD_STR_TCP | 40334
STRCrpalkeGrfs3AlarmCodeLog3 | INT | IOD_STR_TCP | 40335
STRCrpalkeGrfs3AlarmCodeLog4 | INT | IOD_STR_TCP | 40336
STRCrpalkeGrfs3AlarmCodeLog5 | INT | IOD_STR_TCP | 40337
STRCrpalkeGrfs3AlarmGroupXVH0 | INT | IOD_STR_TCP | 40338
STRCrpalkeGrfs3AlarmGroupXVH10 | INT | IOD_STR_TCP | 40339
STRCrpalkeGrfs3AlarmGroupXVH11 | INT | IOD_STR_TCP | 40340
STRCrpalkeGrfs3AlarmGroupXVH12 | INT | IOD_STR_TCP | 40341
STRCrpalkeGrfs3AlarmGroupXVH13 | INT | IOD_STR_TCP | 40342
STRCrpalkeGrfs3AlarmGroupXVH14 | INT | IOD_STR_TCP | 40343
STRCrpalkeGrfs3AlarmGroupXVH15 | INT | IOD_STR_TCP | 40344
STRCrpalkeGrfs3AlarmGroupXVH16 | INT | IOD_STR_TCP | 40345
STRCrpalkeGrfs3AlarmGroupXVH1 | INT | IOD_STR_TCP | 40346
STRCrpalkeGrfs3AlarmGroupXVH2 | INT | IOD_STR_TCP | 40347
STRCrpalkeGrfs3AlarmGroupXVH3 | INT | IOD_STR_TCP | 40348
STRCrpalkeGrfs3AlarmGroupXVH4 | INT | IOD_STR_TCP | 40349
STRCrpalkeGrfs3AlarmGroupXVH5 | INT | IOD_STR_TCP | 40350
STRCrpalkeGrfs3AlarmGroupXVH6 | INT | IOD_STR_TCP | 40351
STRCrpalkeGrfs3AlarmGroupXVH7 | INT | IOD_STR_TCP | 40352
STRCrpalkeGrfs3AlarmGroupXVH8 | INT | IOD_STR_TCP | 40353
STRCrpalkeGrfs3AlarmGroupXVH9 | INT | IOD_STR_TCP | 40354
STRCrpalkeGrfs3AlarmQSD1 | INT | IOD_STR_TCP | 40355
STRCrpalkeGrfs3AlarmQSD2 | INT | IOD_STR_TCP | 40356
STRCrpalkeGrfs3AlarmStart1 | INT | IOD_STR_TCP | 40357
STRCrpalkeGrfs3AlarmStart2 | INT | IOD_STR_TCP | 40358
STRCrpalkeGrfs3AlarmStop1 | INT | IOD_STR_TCP | 40359
STRCrpalkeGrfs3AlarmStop2 | INT | IOD_STR_TCP | 40360
STRCrpalkeGrfs3AlarmStop3 | INT | IOD_STR_TCP | 40361
STRCrpalkeGrfs3AlarmSurv1 | INT | IOD_STR_TCP | 40362
STRCrpalkeGrfs3AlarmSurv2 | INT | IOD_STR_TCP | 40363
STRCrpalkeGrfs3ControlSource | INT | IOD_STR_TCP | 40364
STRCrpalkeGrfs3DeltaSetPoint | REAL | IOD_STR_TCP | 45481
STRCrpalkeGrfs3Deluje | DIGITAL | IOD_STR_TCP | 00203
STRCrpalkeGrfs3EnergijaPoraba | REAL | IOD_STR_TCP | 45483 |  |  |  |  | kWh | ####.#
STRCrpalkeGrfs3ExternInputSetup | INT | IOD_STR_TCP | 40365
STRCrpalkeGrfs3ExternInputsStatus | INT | IOD_STR_TCP | 40366
STRCrpalkeGrfs3FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 45485 | 0 | 500 | 0 | 500 | V | ####.#
STRCrpalkeGrfs3FrekPretvornikDCTok | REAL | IOD_STR_TCP | 45487 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs3FreqMax | REAL | IOD_STR_TCP | 45489 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs3FreqMin | REAL | IOD_STR_TCP | 45491 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs3FreqUpper | REAL | IOD_STR_TCP | 45493 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs3LocalMode | DIGITAL | IOD_STR_TCP | 00204
STRCrpalkeGrfs3LocalSetupMode1 | INT | IOD_STR_TCP | 40367
STRCrpalkeGrfs3MocMax | REAL | IOD_STR_TCP | 45495 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs3MocTrenutna | REAL | IOD_STR_TCP | 45497 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs3MotorHitrost | REAL | IOD_STR_TCP | 45499 | 0 | 2500 | 0 | 2500 | obr/min | ####.#
STRCrpalkeGrfs3MotorTok | REAL | IOD_STR_TCP | 45501 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs3NapajanjeTok | REAL | IOD_STR_TCP | 45503 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs3NastavitevLokalna | REAL | IOD_STR_TCP | 45505
STRCrpalkeGrfs3NastavitevTrenutna | REAL | IOD_STR_TCP | 45507
STRCrpalkeGrfs3PreklopkaMode | INT | IOD_STR_TCP | 40368
STRCrpalkeGrfs3PretokMax | REAL | IOD_STR_TCP | 45509 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs3PretokMin | REAL | IOD_STR_TCP | 45511 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs3PretokTrenutni | REAL | IOD_STR_TCP | 45513 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs3PritiskMax | REAL | IOD_STR_TCP | 45515 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs3PritiskTrenutni | REAL | IOD_STR_TCP | 45517 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs3ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 45519 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs3ReferencaRemote | REAL | IOD_STR_TCP | 45521 | 0 | 100 | 0 | 100 | % | ####.#
STRCrpalkeGrfs3Relay1setup | INT | IOD_STR_TCP | 40369
STRCrpalkeGrfs3RemoteON | DIGITAL | IOD_STR_TCP | 00205
STRCrpalkeGrfs3RemoteSetupMode1 | INT | IOD_STR_TCP | 40370
STRCrpalkeGrfs3Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 00206
STRCrpalkeGrfs3ResetAlarm | DIGITAL | IOD_STR_TCP | 00207
STRCrpalkeGrfs3ResetAlarmLog | DIGITAL | IOD_STR_TCP | 00208
STRCrpalkeGrfs3ResetDevice | DIGITAL | IOD_STR_TCP | 00209
STRCrpalkeGrfs3SetAutomatic | DIGITAL | IOD_STR_TCP | 00210
STRCrpalkeGrfs3SetConstFreqMode | DIGITAL | IOD_STR_TCP | 00211
STRCrpalkeGrfs3SetConstPress | DIGITAL | IOD_STR_TCP | 00212
STRCrpalkeGrfs3SetLocalMode | DIGITAL | IOD_STR_TCP | 00213
STRCrpalkeGrfs3SetMaxRunMode | DIGITAL | IOD_STR_TCP | 00214
STRCrpalkeGrfs3SetMinRunMode | DIGITAL | IOD_STR_TCP | 00215
STRCrpalkeGrfs3SetPropPress | DIGITAL | IOD_STR_TCP | 00216
STRCrpalkeGrfs3SetReference | DIGITAL | IOD_STR_TCP | 00217
STRCrpalkeGrfs3SetRemoteMode | DIGITAL | IOD_STR_TCP | 00218
STRCrpalkeGrfs3SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 00219
STRCrpalkeGrfs3SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 00220
STRCrpalkeGrfs3SetTwinModeSync | DIGITAL | IOD_STR_TCP | 00221
STRCrpalkeGrfs3Start | DIGITAL | IOD_STR_TCP | 00222
STRCrpalkeGrfs3StatusCrpalke | INT | IOD_STR_TCP | 40371
STRCrpalkeGrfs3StatusMode1 | INT | IOD_STR_TCP | 40372
STRCrpalkeGrfs3StatusMode1co | INT | IOD_STR_TCP | 40373
STRCrpalkeGrfs3StatusMode1op | INT | IOD_STR_TCP | 40374
STRCrpalkeGrfs3StatusMode2 | INT | IOD_STR_TCP | 40375
STRCrpalkeGrfs3StatusMode3 | INT | IOD_STR_TCP | 40376
STRCrpalkeGrfs3StevecUr2h | REAL | IOD_STR_TCP | 45523 |  |  |  |  | 2h
STRCrpalkeGrfs3Stop | DIGITAL | IOD_STR_TCP | 00223
STRCrpalkeGrfs3SystemFeedback | REAL | IOD_STR_TCP | 45525
STRCrpalkeGrfs3SystemReference | REAL | IOD_STR_TCP | 45527
STRCrpalkeGrfs3TemperaturaMotorja | REAL | IOD_STR_TCP | 45529 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeGrfs3UreXC200 | REAL | IOD_STR_TCP | 45531 |  |  |  |  | h | ####.#
STRCrpalkeGrfs4AlarmActiveCode | INT | IOD_STR_TCP | 40377
STRCrpalkeGrfs4AlarmAktiven | DIGITAL | IOD_STR_TCP | 00224
STRCrpalkeGrfs4AlarmCodeLog1 | INT | IOD_STR_TCP | 40378
STRCrpalkeGrfs4AlarmCodeLog2 | INT | IOD_STR_TCP | 40379
STRCrpalkeGrfs4AlarmCodeLog3 | INT | IOD_STR_TCP | 40380
STRCrpalkeGrfs4AlarmCodeLog4 | INT | IOD_STR_TCP | 40381
STRCrpalkeGrfs4AlarmCodeLog5 | INT | IOD_STR_TCP | 40382
STRCrpalkeGrfs4AlarmGroupXVH0 | INT | IOD_STR_TCP | 40383
STRCrpalkeGrfs4AlarmGroupXVH10 | INT | IOD_STR_TCP | 40384
STRCrpalkeGrfs4AlarmGroupXVH11 | INT | IOD_STR_TCP | 40385
STRCrpalkeGrfs4AlarmGroupXVH12 | INT | IOD_STR_TCP | 40386
STRCrpalkeGrfs4AlarmGroupXVH13 | INT | IOD_STR_TCP | 40387
STRCrpalkeGrfs4AlarmGroupXVH14 | INT | IOD_STR_TCP | 40388
STRCrpalkeGrfs4AlarmGroupXVH15 | INT | IOD_STR_TCP | 40389
STRCrpalkeGrfs4AlarmGroupXVH16 | INT | IOD_STR_TCP | 40390
STRCrpalkeGrfs4AlarmGroupXVH1 | INT | IOD_STR_TCP | 40391
STRCrpalkeGrfs4AlarmGroupXVH2 | INT | IOD_STR_TCP | 40392
STRCrpalkeGrfs4AlarmGroupXVH3 | INT | IOD_STR_TCP | 40393
STRCrpalkeGrfs4AlarmGroupXVH4 | INT | IOD_STR_TCP | 40394
STRCrpalkeGrfs4AlarmGroupXVH5 | INT | IOD_STR_TCP | 40395
STRCrpalkeGrfs4AlarmGroupXVH6 | INT | IOD_STR_TCP | 40396
STRCrpalkeGrfs4AlarmGroupXVH7 | INT | IOD_STR_TCP | 40397
STRCrpalkeGrfs4AlarmGroupXVH8 | INT | IOD_STR_TCP | 40398
STRCrpalkeGrfs4AlarmGroupXVH9 | INT | IOD_STR_TCP | 40399
STRCrpalkeGrfs4AlarmQSD1 | INT | IOD_STR_TCP | 40400
STRCrpalkeGrfs4AlarmQSD2 | INT | IOD_STR_TCP | 40401
STRCrpalkeGrfs4AlarmStart1 | INT | IOD_STR_TCP | 40402
STRCrpalkeGrfs4AlarmStart2 | INT | IOD_STR_TCP | 40403
STRCrpalkeGrfs4AlarmStop1 | INT | IOD_STR_TCP | 40404
STRCrpalkeGrfs4AlarmStop2 | INT | IOD_STR_TCP | 40405
STRCrpalkeGrfs4AlarmStop3 | INT | IOD_STR_TCP | 40406
STRCrpalkeGrfs4AlarmSurv1 | INT | IOD_STR_TCP | 40407
STRCrpalkeGrfs4AlarmSurv2 | INT | IOD_STR_TCP | 40408
STRCrpalkeGrfs4ControlSource | INT | IOD_STR_TCP | 40409
STRCrpalkeGrfs4DeltaSetPoint | REAL | IOD_STR_TCP | 45533
STRCrpalkeGrfs4Deluje | DIGITAL | IOD_STR_TCP | 00225
STRCrpalkeGrfs4EnergijaPoraba | REAL | IOD_STR_TCP | 45535 |  |  |  |  | kWh | ####.#
STRCrpalkeGrfs4ExternInputSetup | INT | IOD_STR_TCP | 40410
STRCrpalkeGrfs4ExternInputsStatus | INT | IOD_STR_TCP | 40411
STRCrpalkeGrfs4FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 45537 | 0 | 500 | 0 | 500 | V | ####.#
STRCrpalkeGrfs4FrekPretvornikDCTok | REAL | IOD_STR_TCP | 45539 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs4FreqMax | REAL | IOD_STR_TCP | 45541 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs4FreqMin | REAL | IOD_STR_TCP | 45543 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs4FreqUpper | REAL | IOD_STR_TCP | 45545 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs4LocalMode | DIGITAL | IOD_STR_TCP | 00226
STRCrpalkeGrfs4LocalSetupMode1 | INT | IOD_STR_TCP | 40412
STRCrpalkeGrfs4MocMax | REAL | IOD_STR_TCP | 45547 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs4MocTrenutna | REAL | IOD_STR_TCP | 45549 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs4MotorHitrost | REAL | IOD_STR_TCP | 45551 | 0 | 2500 | 0 | 2500 | obr/min | ####.#
STRCrpalkeGrfs4MotorTok | REAL | IOD_STR_TCP | 45553 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs4NapajanjeTok | REAL | IOD_STR_TCP | 45555 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs4NastavitevLokalna | REAL | IOD_STR_TCP | 45557
STRCrpalkeGrfs4NastavitevTrenutna | REAL | IOD_STR_TCP | 45559
STRCrpalkeGrfs4PreklopkaMode | INT | IOD_STR_TCP | 40413
STRCrpalkeGrfs4PretokMax | REAL | IOD_STR_TCP | 45561 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs4PretokMin | REAL | IOD_STR_TCP | 45563 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs4PretokTrenutni | REAL | IOD_STR_TCP | 45565 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs4PritiskMax | REAL | IOD_STR_TCP | 45567 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs4PritiskTrenutni | REAL | IOD_STR_TCP | 45569 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs4ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 45571 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs4ReferencaRemote | REAL | IOD_STR_TCP | 45573 | 0 | 100 | 0 | 100 | % | ####.#
STRCrpalkeGrfs4Relay1setup | INT | IOD_STR_TCP | 40414
STRCrpalkeGrfs4RemoteON | DIGITAL | IOD_STR_TCP | 00227
STRCrpalkeGrfs4RemoteSetupMode1 | INT | IOD_STR_TCP | 40415
STRCrpalkeGrfs4Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 00228
STRCrpalkeGrfs4ResetAlarm | DIGITAL | IOD_STR_TCP | 00229
STRCrpalkeGrfs4ResetAlarmLog | DIGITAL | IOD_STR_TCP | 00230
STRCrpalkeGrfs4ResetDevice | DIGITAL | IOD_STR_TCP | 00231
STRCrpalkeGrfs4SetAutomatic | DIGITAL | IOD_STR_TCP | 00232
STRCrpalkeGrfs4SetConstFreqMode | DIGITAL | IOD_STR_TCP | 00233
STRCrpalkeGrfs4SetConstPress | DIGITAL | IOD_STR_TCP | 00234
STRCrpalkeGrfs4SetLocalMode | DIGITAL | IOD_STR_TCP | 00235
STRCrpalkeGrfs4SetMaxRunMode | DIGITAL | IOD_STR_TCP | 00236
STRCrpalkeGrfs4SetMinRunMode | DIGITAL | IOD_STR_TCP | 00237
STRCrpalkeGrfs4SetPropPress | DIGITAL | IOD_STR_TCP | 00238
STRCrpalkeGrfs4SetReference | DIGITAL | IOD_STR_TCP | 00239
STRCrpalkeGrfs4SetRemoteMode | DIGITAL | IOD_STR_TCP | 00240
STRCrpalkeGrfs4SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 00241
STRCrpalkeGrfs4SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 00242
STRCrpalkeGrfs4SetTwinModeSync | DIGITAL | IOD_STR_TCP | 00243
STRCrpalkeGrfs4Start | DIGITAL | IOD_STR_TCP | 00244
STRCrpalkeGrfs4StatusCrpalke | INT | IOD_STR_TCP | 40416
STRCrpalkeGrfs4StatusMode1 | INT | IOD_STR_TCP | 40417
STRCrpalkeGrfs4StatusMode1co | INT | IOD_STR_TCP | 40418
STRCrpalkeGrfs4StatusMode1op | INT | IOD_STR_TCP | 40419
STRCrpalkeGrfs4StatusMode2 | INT | IOD_STR_TCP | 40420
STRCrpalkeGrfs4StatusMode3 | INT | IOD_STR_TCP | 40421
STRCrpalkeGrfs4StevecUr2h | REAL | IOD_STR_TCP | 45575 |  |  |  |  | 2h
STRCrpalkeGrfs4Stop | DIGITAL | IOD_STR_TCP | 00245
STRCrpalkeGrfs4SystemFeedback | REAL | IOD_STR_TCP | 45577
STRCrpalkeGrfs4SystemReference | REAL | IOD_STR_TCP | 45579
STRCrpalkeGrfs4TemperaturaMotorja | REAL | IOD_STR_TCP | 45581 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeGrfs4UreXC200 | REAL | IOD_STR_TCP | 45583 |  |  |  |  | h | ####.#
STRCrpalkeGrfs5AlarmActiveCode | INT | IOD_STR_TCP | 40422
STRCrpalkeGrfs5AlarmAktiven | DIGITAL | IOD_STR_TCP | 00246
STRCrpalkeGrfs5AlarmCodeLog1 | INT | IOD_STR_TCP | 40423
STRCrpalkeGrfs5AlarmCodeLog2 | INT | IOD_STR_TCP | 40424
STRCrpalkeGrfs5AlarmCodeLog3 | INT | IOD_STR_TCP | 40425
STRCrpalkeGrfs5AlarmCodeLog4 | INT | IOD_STR_TCP | 40426
STRCrpalkeGrfs5AlarmCodeLog5 | INT | IOD_STR_TCP | 40427
STRCrpalkeGrfs5AlarmGroupXVH0 | INT | IOD_STR_TCP | 40428
STRCrpalkeGrfs5AlarmGroupXVH10 | INT | IOD_STR_TCP | 40429
STRCrpalkeGrfs5AlarmGroupXVH11 | INT | IOD_STR_TCP | 40430
STRCrpalkeGrfs5AlarmGroupXVH12 | INT | IOD_STR_TCP | 40431
STRCrpalkeGrfs5AlarmGroupXVH13 | INT | IOD_STR_TCP | 40432
STRCrpalkeGrfs5AlarmGroupXVH14 | INT | IOD_STR_TCP | 40433
STRCrpalkeGrfs5AlarmGroupXVH15 | INT | IOD_STR_TCP | 40434
STRCrpalkeGrfs5AlarmGroupXVH16 | INT | IOD_STR_TCP | 40435
STRCrpalkeGrfs5AlarmGroupXVH1 | INT | IOD_STR_TCP | 40436
STRCrpalkeGrfs5AlarmGroupXVH2 | INT | IOD_STR_TCP | 40437
STRCrpalkeGrfs5AlarmGroupXVH3 | INT | IOD_STR_TCP | 40438
STRCrpalkeGrfs5AlarmGroupXVH4 | INT | IOD_STR_TCP | 40439
STRCrpalkeGrfs5AlarmGroupXVH5 | INT | IOD_STR_TCP | 40440
STRCrpalkeGrfs5AlarmGroupXVH6 | INT | IOD_STR_TCP | 40441
STRCrpalkeGrfs5AlarmGroupXVH7 | INT | IOD_STR_TCP | 40442
STRCrpalkeGrfs5AlarmGroupXVH8 | INT | IOD_STR_TCP | 40443
STRCrpalkeGrfs5AlarmGroupXVH9 | INT | IOD_STR_TCP | 40444
STRCrpalkeGrfs5AlarmQSD1 | INT | IOD_STR_TCP | 40445
STRCrpalkeGrfs5AlarmQSD2 | INT | IOD_STR_TCP | 40446
STRCrpalkeGrfs5AlarmStart1 | INT | IOD_STR_TCP | 40447
STRCrpalkeGrfs5AlarmStart2 | INT | IOD_STR_TCP | 40448
STRCrpalkeGrfs5AlarmStop1 | INT | IOD_STR_TCP | 40449
STRCrpalkeGrfs5AlarmStop2 | INT | IOD_STR_TCP | 40450
STRCrpalkeGrfs5AlarmStop3 | INT | IOD_STR_TCP | 40451
STRCrpalkeGrfs5AlarmSurv1 | INT | IOD_STR_TCP | 40452
STRCrpalkeGrfs5AlarmSurv2 | INT | IOD_STR_TCP | 40453
STRCrpalkeGrfs5ControlSource | INT | IOD_STR_TCP | 40454
STRCrpalkeGrfs5DeltaSetPoint | REAL | IOD_STR_TCP | 45585
STRCrpalkeGrfs5Deluje | DIGITAL | IOD_STR_TCP | 00247
STRCrpalkeGrfs5EnergijaPoraba | REAL | IOD_STR_TCP | 45587 |  |  |  |  | kWh | ####.#
STRCrpalkeGrfs5ExternInputSetup | INT | IOD_STR_TCP | 40455
STRCrpalkeGrfs5ExternInputsStatus | INT | IOD_STR_TCP | 40456
STRCrpalkeGrfs5FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 45589 | 0 | 500 | 0 | 500 | V | ####.#
STRCrpalkeGrfs5FrekPretvornikDCTok | REAL | IOD_STR_TCP | 45591 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs5FreqMax | REAL | IOD_STR_TCP | 45593 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs5FreqMin | REAL | IOD_STR_TCP | 45595 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs5FreqUpper | REAL | IOD_STR_TCP | 45597 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs5LocalMode | DIGITAL | IOD_STR_TCP | 00248
STRCrpalkeGrfs5LocalSetupMode1 | INT | IOD_STR_TCP | 40457
STRCrpalkeGrfs5MocMax | REAL | IOD_STR_TCP | 45599 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs5MocTrenutna | REAL | IOD_STR_TCP | 45601 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs5MotorHitrost | REAL | IOD_STR_TCP | 45603 | 0 | 2500 | 0 | 2500 | obr/min | ####.#
STRCrpalkeGrfs5MotorTok | REAL | IOD_STR_TCP | 45605 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs5NapajanjeTok | REAL | IOD_STR_TCP | 45607 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs5NastavitevLokalna | REAL | IOD_STR_TCP | 45609
STRCrpalkeGrfs5NastavitevTrenutna | REAL | IOD_STR_TCP | 45611
STRCrpalkeGrfs5PreklopkaMode | INT | IOD_STR_TCP | 40458
STRCrpalkeGrfs5PretokMax | REAL | IOD_STR_TCP | 45613 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs5PretokMin | REAL | IOD_STR_TCP | 45615 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs5PretokTrenutni | REAL | IOD_STR_TCP | 45617 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs5PritiskMax | REAL | IOD_STR_TCP | 45619 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs5PritiskTrenutni | REAL | IOD_STR_TCP | 45621 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs5ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 45623 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs5ReferencaRemote | REAL | IOD_STR_TCP | 45625 | 0 | 100 | 0 | 100 | % | ####.#
STRCrpalkeGrfs5Relay1setup | INT | IOD_STR_TCP | 40459
STRCrpalkeGrfs5RemoteON | DIGITAL | IOD_STR_TCP | 00249
STRCrpalkeGrfs5RemoteSetupMode1 | INT | IOD_STR_TCP | 40460
STRCrpalkeGrfs5Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 00250
STRCrpalkeGrfs5ResetAlarm | DIGITAL | IOD_STR_TCP | 00251
STRCrpalkeGrfs5ResetAlarmLog | DIGITAL | IOD_STR_TCP | 00252
STRCrpalkeGrfs5ResetDevice | DIGITAL | IOD_STR_TCP | 00253
STRCrpalkeGrfs5SetAutomatic | DIGITAL | IOD_STR_TCP | 00254
STRCrpalkeGrfs5SetConstFreqMode | DIGITAL | IOD_STR_TCP | 00255
STRCrpalkeGrfs5SetConstPress | DIGITAL | IOD_STR_TCP | 00256
STRCrpalkeGrfs5SetLocalMode | DIGITAL | IOD_STR_TCP | 00257
STRCrpalkeGrfs5SetMaxRunMode | DIGITAL | IOD_STR_TCP | 00258
STRCrpalkeGrfs5SetMinRunMode | DIGITAL | IOD_STR_TCP | 00259
STRCrpalkeGrfs5SetPropPress | DIGITAL | IOD_STR_TCP | 00260
STRCrpalkeGrfs5SetReference | DIGITAL | IOD_STR_TCP | 00261
STRCrpalkeGrfs5SetRemoteMode | DIGITAL | IOD_STR_TCP | 00262
STRCrpalkeGrfs5SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 00263
STRCrpalkeGrfs5SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 00264
STRCrpalkeGrfs5SetTwinModeSync | DIGITAL | IOD_STR_TCP | 00265
STRCrpalkeGrfs5Start | DIGITAL | IOD_STR_TCP | 00266
STRCrpalkeGrfs5StatusCrpalke | INT | IOD_STR_TCP | 40461
STRCrpalkeGrfs5StatusMode1 | INT | IOD_STR_TCP | 40462
STRCrpalkeGrfs5StatusMode1co | INT | IOD_STR_TCP | 40463
STRCrpalkeGrfs5StatusMode1op | INT | IOD_STR_TCP | 40464
STRCrpalkeGrfs5StatusMode2 | INT | IOD_STR_TCP | 40465
STRCrpalkeGrfs5StatusMode3 | INT | IOD_STR_TCP | 40466
STRCrpalkeGrfs5StevecUr2h | REAL | IOD_STR_TCP | 45627 |  |  |  |  | 2h
STRCrpalkeGrfs5Stop | DIGITAL | IOD_STR_TCP | 00267
STRCrpalkeGrfs5SystemFeedback | REAL | IOD_STR_TCP | 45629
STRCrpalkeGrfs5SystemReference | REAL | IOD_STR_TCP | 45631
STRCrpalkeGrfs5TemperaturaMotorja | REAL | IOD_STR_TCP | 45633 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeGrfs5UreXC200 | REAL | IOD_STR_TCP | 45635 |  |  |  |  | h | ####.#
STRCrpalkeGrfs6AlarmActiveCode | INT | IOD_STR_TCP | 40467
STRCrpalkeGrfs6AlarmAktiven | DIGITAL | IOD_STR_TCP | 00268
STRCrpalkeGrfs6AlarmCodeLog1 | INT | IOD_STR_TCP | 40468
STRCrpalkeGrfs6AlarmCodeLog2 | INT | IOD_STR_TCP | 40469
STRCrpalkeGrfs6AlarmCodeLog3 | INT | IOD_STR_TCP | 40470
STRCrpalkeGrfs6AlarmCodeLog4 | INT | IOD_STR_TCP | 40471
STRCrpalkeGrfs6AlarmCodeLog5 | INT | IOD_STR_TCP | 40472
STRCrpalkeGrfs6AlarmGroupXVH0 | INT | IOD_STR_TCP | 40473
STRCrpalkeGrfs6AlarmGroupXVH10 | INT | IOD_STR_TCP | 40474
STRCrpalkeGrfs6AlarmGroupXVH11 | INT | IOD_STR_TCP | 40475
STRCrpalkeGrfs6AlarmGroupXVH12 | INT | IOD_STR_TCP | 40476
STRCrpalkeGrfs6AlarmGroupXVH13 | INT | IOD_STR_TCP | 40477
STRCrpalkeGrfs6AlarmGroupXVH14 | INT | IOD_STR_TCP | 40478
STRCrpalkeGrfs6AlarmGroupXVH15 | INT | IOD_STR_TCP | 40479
STRCrpalkeGrfs6AlarmGroupXVH16 | INT | IOD_STR_TCP | 40480
STRCrpalkeGrfs6AlarmGroupXVH1 | INT | IOD_STR_TCP | 40481
STRCrpalkeGrfs6AlarmGroupXVH2 | INT | IOD_STR_TCP | 40482
STRCrpalkeGrfs6AlarmGroupXVH3 | INT | IOD_STR_TCP | 40483
STRCrpalkeGrfs6AlarmGroupXVH4 | INT | IOD_STR_TCP | 40484
STRCrpalkeGrfs6AlarmGroupXVH5 | INT | IOD_STR_TCP | 40485
STRCrpalkeGrfs6AlarmGroupXVH6 | INT | IOD_STR_TCP | 40486
STRCrpalkeGrfs6AlarmGroupXVH7 | INT | IOD_STR_TCP | 40487
STRCrpalkeGrfs6AlarmGroupXVH8 | INT | IOD_STR_TCP | 40488
STRCrpalkeGrfs6AlarmGroupXVH9 | INT | IOD_STR_TCP | 40489
STRCrpalkeGrfs6AlarmQSD1 | INT | IOD_STR_TCP | 40490
STRCrpalkeGrfs6AlarmQSD2 | INT | IOD_STR_TCP | 40491
STRCrpalkeGrfs6AlarmStart1 | INT | IOD_STR_TCP | 40492
STRCrpalkeGrfs6AlarmStart2 | INT | IOD_STR_TCP | 40493
STRCrpalkeGrfs6AlarmStop1 | INT | IOD_STR_TCP | 40494
STRCrpalkeGrfs6AlarmStop2 | INT | IOD_STR_TCP | 40495
STRCrpalkeGrfs6AlarmStop3 | INT | IOD_STR_TCP | 40496
STRCrpalkeGrfs6AlarmSurv1 | INT | IOD_STR_TCP | 40497
STRCrpalkeGrfs6AlarmSurv2 | INT | IOD_STR_TCP | 40498
STRCrpalkeGrfs6ControlSource | INT | IOD_STR_TCP | 40499
STRCrpalkeGrfs6DeltaSetPoint | REAL | IOD_STR_TCP | 45637
STRCrpalkeGrfs6Deluje | DIGITAL | IOD_STR_TCP | 00269
STRCrpalkeGrfs6EnergijaPoraba | REAL | IOD_STR_TCP | 45639 |  |  |  |  | kWh | ####.#
STRCrpalkeGrfs6ExternInputSetup | INT | IOD_STR_TCP | 40500
STRCrpalkeGrfs6ExternInputsStatus | INT | IOD_STR_TCP | 40501
STRCrpalkeGrfs6FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 45641 | 0 | 500 | 0 | 500 | V | ####.#
STRCrpalkeGrfs6FrekPretvornikDCTok | REAL | IOD_STR_TCP | 45643 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs6FreqMax | REAL | IOD_STR_TCP | 45645 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs6FreqMin | REAL | IOD_STR_TCP | 45647 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs6FreqUpper | REAL | IOD_STR_TCP | 45649 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs6LocalMode | DIGITAL | IOD_STR_TCP | 00270
STRCrpalkeGrfs6LocalSetupMode1 | INT | IOD_STR_TCP | 40502
STRCrpalkeGrfs6MocMax | REAL | IOD_STR_TCP | 45651 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs6MocTrenutna | REAL | IOD_STR_TCP | 45653 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs6MotorHitrost | REAL | IOD_STR_TCP | 45655 | 0 | 2500 | 0 | 2500 | obr/min | ####.#
STRCrpalkeGrfs6MotorTok | REAL | IOD_STR_TCP | 45657 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs6NapajanjeTok | REAL | IOD_STR_TCP | 45659 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs6NastavitevLokalna | REAL | IOD_STR_TCP | 45661
STRCrpalkeGrfs6NastavitevTrenutna | REAL | IOD_STR_TCP | 45663
STRCrpalkeGrfs6PreklopkaMode | INT | IOD_STR_TCP | 40503
STRCrpalkeGrfs6PretokMax | REAL | IOD_STR_TCP | 45665 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs6PretokMin | REAL | IOD_STR_TCP | 45667 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs6PretokTrenutni | REAL | IOD_STR_TCP | 45669 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs6PritiskMax | REAL | IOD_STR_TCP | 45671 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs6PritiskTrenutni | REAL | IOD_STR_TCP | 45673 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs6ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 45675 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs6ReferencaRemote | REAL | IOD_STR_TCP | 45677 | 0 | 100 | 0 | 100 | % | ####.#
STRCrpalkeGrfs6Relay1setup | INT | IOD_STR_TCP | 40504
STRCrpalkeGrfs6RemoteON | DIGITAL | IOD_STR_TCP | 00271
STRCrpalkeGrfs6RemoteSetupMode1 | INT | IOD_STR_TCP | 40505
STRCrpalkeGrfs6Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 00272
STRCrpalkeGrfs6ResetAlarm | DIGITAL | IOD_STR_TCP | 00273
STRCrpalkeGrfs6ResetAlarmLog | DIGITAL | IOD_STR_TCP | 00274
STRCrpalkeGrfs6ResetDevice | DIGITAL | IOD_STR_TCP | 00275
STRCrpalkeGrfs6SetAutomatic | DIGITAL | IOD_STR_TCP | 00276
STRCrpalkeGrfs6SetConstFreqMode | DIGITAL | IOD_STR_TCP | 00277
STRCrpalkeGrfs6SetConstPress | DIGITAL | IOD_STR_TCP | 00278
STRCrpalkeGrfs6SetLocalMode | DIGITAL | IOD_STR_TCP | 00279
STRCrpalkeGrfs6SetMaxRunMode | DIGITAL | IOD_STR_TCP | 00280
STRCrpalkeGrfs6SetMinRunMode | DIGITAL | IOD_STR_TCP | 00281
STRCrpalkeGrfs6SetPropPress | DIGITAL | IOD_STR_TCP | 00282
STRCrpalkeGrfs6SetReference | DIGITAL | IOD_STR_TCP | 00283
STRCrpalkeGrfs6SetRemoteMode | DIGITAL | IOD_STR_TCP | 00284
STRCrpalkeGrfs6SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 00285
STRCrpalkeGrfs6SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 00286
STRCrpalkeGrfs6SetTwinModeSync | DIGITAL | IOD_STR_TCP | 00287
STRCrpalkeGrfs6Start | DIGITAL | IOD_STR_TCP | 00288
STRCrpalkeGrfs6StatusCrpalke | INT | IOD_STR_TCP | 40506
STRCrpalkeGrfs6StatusMode1 | INT | IOD_STR_TCP | 40507
STRCrpalkeGrfs6StatusMode1co | INT | IOD_STR_TCP | 40508
STRCrpalkeGrfs6StatusMode1op | INT | IOD_STR_TCP | 40509
STRCrpalkeGrfs6StatusMode2 | INT | IOD_STR_TCP | 40510
STRCrpalkeGrfs6StatusMode3 | INT | IOD_STR_TCP | 40511
STRCrpalkeGrfs6StevecUr2h | REAL | IOD_STR_TCP | 45679 |  |  |  |  | 2h
STRCrpalkeGrfs6Stop | DIGITAL | IOD_STR_TCP | 00289
STRCrpalkeGrfs6SystemFeedback | REAL | IOD_STR_TCP | 45681
STRCrpalkeGrfs6SystemReference | REAL | IOD_STR_TCP | 45683
STRCrpalkeGrfs6TemperaturaMotorja | REAL | IOD_STR_TCP | 45685 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeGrfs6UreXC200 | REAL | IOD_STR_TCP | 45687 |  |  |  |  | h | ####.#
STRCrpalkeGrfs7AlarmActiveCode | INT | IOD_STR_TCP | 40512
STRCrpalkeGrfs7AlarmAktiven | DIGITAL | IOD_STR_TCP | 00290
STRCrpalkeGrfs7AlarmCodeLog1 | INT | IOD_STR_TCP | 40513
STRCrpalkeGrfs7AlarmCodeLog2 | INT | IOD_STR_TCP | 40514
STRCrpalkeGrfs7AlarmCodeLog3 | INT | IOD_STR_TCP | 40515
STRCrpalkeGrfs7AlarmCodeLog4 | INT | IOD_STR_TCP | 40516
STRCrpalkeGrfs7AlarmCodeLog5 | INT | IOD_STR_TCP | 40517
STRCrpalkeGrfs7AlarmGroupXVH0 | INT | IOD_STR_TCP | 40518
STRCrpalkeGrfs7AlarmGroupXVH10 | INT | IOD_STR_TCP | 40519
STRCrpalkeGrfs7AlarmGroupXVH11 | INT | IOD_STR_TCP | 40520
STRCrpalkeGrfs7AlarmGroupXVH12 | INT | IOD_STR_TCP | 40521
STRCrpalkeGrfs7AlarmGroupXVH13 | INT | IOD_STR_TCP | 40522
STRCrpalkeGrfs7AlarmGroupXVH14 | INT | IOD_STR_TCP | 40523
STRCrpalkeGrfs7AlarmGroupXVH15 | INT | IOD_STR_TCP | 40524
STRCrpalkeGrfs7AlarmGroupXVH16 | INT | IOD_STR_TCP | 40525
STRCrpalkeGrfs7AlarmGroupXVH1 | INT | IOD_STR_TCP | 40526
STRCrpalkeGrfs7AlarmGroupXVH2 | INT | IOD_STR_TCP | 40527
STRCrpalkeGrfs7AlarmGroupXVH3 | INT | IOD_STR_TCP | 40528
STRCrpalkeGrfs7AlarmGroupXVH4 | INT | IOD_STR_TCP | 40529
STRCrpalkeGrfs7AlarmGroupXVH5 | INT | IOD_STR_TCP | 40530
STRCrpalkeGrfs7AlarmGroupXVH6 | INT | IOD_STR_TCP | 40531
STRCrpalkeGrfs7AlarmGroupXVH7 | INT | IOD_STR_TCP | 40532
STRCrpalkeGrfs7AlarmGroupXVH8 | INT | IOD_STR_TCP | 40533
STRCrpalkeGrfs7AlarmGroupXVH9 | INT | IOD_STR_TCP | 40534
STRCrpalkeGrfs7AlarmQSD1 | INT | IOD_STR_TCP | 40535
STRCrpalkeGrfs7AlarmQSD2 | INT | IOD_STR_TCP | 40536
STRCrpalkeGrfs7AlarmStart1 | INT | IOD_STR_TCP | 40537
STRCrpalkeGrfs7AlarmStart2 | INT | IOD_STR_TCP | 40538
STRCrpalkeGrfs7AlarmStop1 | INT | IOD_STR_TCP | 40539
STRCrpalkeGrfs7AlarmStop2 | INT | IOD_STR_TCP | 40540
STRCrpalkeGrfs7AlarmStop3 | INT | IOD_STR_TCP | 40541
STRCrpalkeGrfs7AlarmSurv1 | INT | IOD_STR_TCP | 40542
STRCrpalkeGrfs7AlarmSurv2 | INT | IOD_STR_TCP | 40543
STRCrpalkeGrfs7ControlSource | INT | IOD_STR_TCP | 40544
STRCrpalkeGrfs7DeltaSetPoint | REAL | IOD_STR_TCP | 45689
STRCrpalkeGrfs7Deluje | DIGITAL | IOD_STR_TCP | 00291
STRCrpalkeGrfs7EnergijaPoraba | REAL | IOD_STR_TCP | 45691 |  |  |  |  | kWh | ####.#
STRCrpalkeGrfs7ExternInputSetup | INT | IOD_STR_TCP | 40545
STRCrpalkeGrfs7ExternInputsStatus | INT | IOD_STR_TCP | 40546
STRCrpalkeGrfs7FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 45693 | 0 | 500 | 0 | 500 | V | ####.#
STRCrpalkeGrfs7FrekPretvornikDCTok | REAL | IOD_STR_TCP | 45695 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs7FreqMax | REAL | IOD_STR_TCP | 45697 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs7FreqMin | REAL | IOD_STR_TCP | 45699 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs7FreqUpper | REAL | IOD_STR_TCP | 45701 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs7LocalMode | DIGITAL | IOD_STR_TCP | 00292
STRCrpalkeGrfs7LocalSetupMode1 | INT | IOD_STR_TCP | 40547
STRCrpalkeGrfs7MocMax | REAL | IOD_STR_TCP | 45703 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs7MocTrenutna | REAL | IOD_STR_TCP | 45705 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs7MotorHitrost | REAL | IOD_STR_TCP | 45707 | 0 | 2500 | 0 | 2500 | obr/min | ####.#
STRCrpalkeGrfs7MotorTok | REAL | IOD_STR_TCP | 45709 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs7NapajanjeTok | REAL | IOD_STR_TCP | 45711 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs7NastavitevLokalna | REAL | IOD_STR_TCP | 45713
STRCrpalkeGrfs7NastavitevTrenutna | REAL | IOD_STR_TCP | 45715
STRCrpalkeGrfs7PreklopkaMode | INT | IOD_STR_TCP | 40548
STRCrpalkeGrfs7PretokMax | REAL | IOD_STR_TCP | 45717 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs7PretokMin | REAL | IOD_STR_TCP | 45719 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs7PretokTrenutni | REAL | IOD_STR_TCP | 45721 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs7PritiskMax | REAL | IOD_STR_TCP | 45723 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs7PritiskTrenutni | REAL | IOD_STR_TCP | 45725 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs7ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 45727 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs7ReferencaRemote | REAL | IOD_STR_TCP | 45729 | 0 | 100 | 0 | 100 | % | ####.#
STRCrpalkeGrfs7Relay1setup | INT | IOD_STR_TCP | 40549
STRCrpalkeGrfs7RemoteON | DIGITAL | IOD_STR_TCP | 00293
STRCrpalkeGrfs7RemoteSetupMode1 | INT | IOD_STR_TCP | 40550
STRCrpalkeGrfs7Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 00294
STRCrpalkeGrfs7ResetAlarm | DIGITAL | IOD_STR_TCP | 00295
STRCrpalkeGrfs7ResetAlarmLog | DIGITAL | IOD_STR_TCP | 00296
STRCrpalkeGrfs7ResetDevice | DIGITAL | IOD_STR_TCP | 00297
STRCrpalkeGrfs7SetAutomatic | DIGITAL | IOD_STR_TCP | 00298
STRCrpalkeGrfs7SetConstFreqMode | DIGITAL | IOD_STR_TCP | 00299
STRCrpalkeGrfs7SetConstPress | DIGITAL | IOD_STR_TCP | 00300
STRCrpalkeGrfs7SetLocalMode | DIGITAL | IOD_STR_TCP | 00301
STRCrpalkeGrfs7SetMaxRunMode | DIGITAL | IOD_STR_TCP | 00302
STRCrpalkeGrfs7SetMinRunMode | DIGITAL | IOD_STR_TCP | 00303
STRCrpalkeGrfs7SetPropPress | DIGITAL | IOD_STR_TCP | 00304
STRCrpalkeGrfs7SetReference | DIGITAL | IOD_STR_TCP | 00305
STRCrpalkeGrfs7SetRemoteMode | DIGITAL | IOD_STR_TCP | 00306
STRCrpalkeGrfs7SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 00307
STRCrpalkeGrfs7SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 00308
STRCrpalkeGrfs7SetTwinModeSync | DIGITAL | IOD_STR_TCP | 00309
STRCrpalkeGrfs7Start | DIGITAL | IOD_STR_TCP | 00310
STRCrpalkeGrfs7StatusCrpalke | INT | IOD_STR_TCP | 40551
STRCrpalkeGrfs7StatusMode1 | INT | IOD_STR_TCP | 40552
STRCrpalkeGrfs7StatusMode1co | INT | IOD_STR_TCP | 40553
STRCrpalkeGrfs7StatusMode1op | INT | IOD_STR_TCP | 40554
STRCrpalkeGrfs7StatusMode2 | INT | IOD_STR_TCP | 40555
STRCrpalkeGrfs7StatusMode3 | INT | IOD_STR_TCP | 40556
STRCrpalkeGrfs7StevecUr2h | REAL | IOD_STR_TCP | 45731 |  |  |  |  | 2h
STRCrpalkeGrfs7Stop | DIGITAL | IOD_STR_TCP | 00311
STRCrpalkeGrfs7SystemFeedback | REAL | IOD_STR_TCP | 45733
STRCrpalkeGrfs7SystemReference | REAL | IOD_STR_TCP | 45735
STRCrpalkeGrfs7TemperaturaMotorja | REAL | IOD_STR_TCP | 45737 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeGrfs7UreXC200 | REAL | IOD_STR_TCP | 45739 |  |  |  |  | h | ####.#
STRCrpalkeGrfs8AlarmActiveCode | INT | IOD_STR_TCP | 40557
STRCrpalkeGrfs8AlarmAktiven | DIGITAL | IOD_STR_TCP | 00312
STRCrpalkeGrfs8AlarmCodeLog1 | INT | IOD_STR_TCP | 40558
STRCrpalkeGrfs8AlarmCodeLog2 | INT | IOD_STR_TCP | 40559
STRCrpalkeGrfs8AlarmCodeLog3 | INT | IOD_STR_TCP | 40560
STRCrpalkeGrfs8AlarmCodeLog4 | INT | IOD_STR_TCP | 40561
STRCrpalkeGrfs8AlarmCodeLog5 | INT | IOD_STR_TCP | 40562
STRCrpalkeGrfs8AlarmGroupXVH0 | INT | IOD_STR_TCP | 40563
STRCrpalkeGrfs8AlarmGroupXVH10 | INT | IOD_STR_TCP | 40564
STRCrpalkeGrfs8AlarmGroupXVH11 | INT | IOD_STR_TCP | 40565
STRCrpalkeGrfs8AlarmGroupXVH12 | INT | IOD_STR_TCP | 40566
STRCrpalkeGrfs8AlarmGroupXVH13 | INT | IOD_STR_TCP | 40567
STRCrpalkeGrfs8AlarmGroupXVH14 | INT | IOD_STR_TCP | 40568
STRCrpalkeGrfs8AlarmGroupXVH15 | INT | IOD_STR_TCP | 40569
STRCrpalkeGrfs8AlarmGroupXVH16 | INT | IOD_STR_TCP | 40570
STRCrpalkeGrfs8AlarmGroupXVH1 | INT | IOD_STR_TCP | 40571
STRCrpalkeGrfs8AlarmGroupXVH2 | INT | IOD_STR_TCP | 40572
STRCrpalkeGrfs8AlarmGroupXVH3 | INT | IOD_STR_TCP | 40573
STRCrpalkeGrfs8AlarmGroupXVH4 | INT | IOD_STR_TCP | 40574
STRCrpalkeGrfs8AlarmGroupXVH5 | INT | IOD_STR_TCP | 40575
STRCrpalkeGrfs8AlarmGroupXVH6 | INT | IOD_STR_TCP | 40576
STRCrpalkeGrfs8AlarmGroupXVH7 | INT | IOD_STR_TCP | 40577
STRCrpalkeGrfs8AlarmGroupXVH8 | INT | IOD_STR_TCP | 40578
STRCrpalkeGrfs8AlarmGroupXVH9 | INT | IOD_STR_TCP | 40579
STRCrpalkeGrfs8AlarmQSD1 | INT | IOD_STR_TCP | 40580
STRCrpalkeGrfs8AlarmQSD2 | INT | IOD_STR_TCP | 40581
STRCrpalkeGrfs8AlarmStart1 | INT | IOD_STR_TCP | 40582
STRCrpalkeGrfs8AlarmStart2 | INT | IOD_STR_TCP | 40583
STRCrpalkeGrfs8AlarmStop1 | INT | IOD_STR_TCP | 40584
STRCrpalkeGrfs8AlarmStop2 | INT | IOD_STR_TCP | 40585
STRCrpalkeGrfs8AlarmStop3 | INT | IOD_STR_TCP | 40586
STRCrpalkeGrfs8AlarmSurv1 | INT | IOD_STR_TCP | 40587
STRCrpalkeGrfs8AlarmSurv2 | INT | IOD_STR_TCP | 40588
STRCrpalkeGrfs8ControlSource | INT | IOD_STR_TCP | 40589
STRCrpalkeGrfs8DeltaSetPoint | REAL | IOD_STR_TCP | 45741
STRCrpalkeGrfs8Deluje | DIGITAL | IOD_STR_TCP | 00313
STRCrpalkeGrfs8EnergijaPoraba | REAL | IOD_STR_TCP | 45743 |  |  |  |  | kWh | ####.#
STRCrpalkeGrfs8ExternInputSetup | INT | IOD_STR_TCP | 40590
STRCrpalkeGrfs8ExternInputsStatus | INT | IOD_STR_TCP | 40591
STRCrpalkeGrfs8FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 45745 | 0 | 500 | 0 | 500 | V | ####.#
STRCrpalkeGrfs8FrekPretvornikDCTok | REAL | IOD_STR_TCP | 45747 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs8FreqMax | REAL | IOD_STR_TCP | 45749 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs8FreqMin | REAL | IOD_STR_TCP | 45751 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs8FreqUpper | REAL | IOD_STR_TCP | 45753 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs8LocalMode | DIGITAL | IOD_STR_TCP | 00314
STRCrpalkeGrfs8LocalSetupMode1 | INT | IOD_STR_TCP | 40592
STRCrpalkeGrfs8MocMax | REAL | IOD_STR_TCP | 45755 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs8MocTrenutna | REAL | IOD_STR_TCP | 45757 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs8MotorHitrost | REAL | IOD_STR_TCP | 45759 | 0 | 2500 | 0 | 2500 | obr/min | ####.#
STRCrpalkeGrfs8MotorTok | REAL | IOD_STR_TCP | 45761 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs8NapajanjeTok | REAL | IOD_STR_TCP | 45763 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs8NastavitevLokalna | REAL | IOD_STR_TCP | 45765
STRCrpalkeGrfs8NastavitevTrenutna | REAL | IOD_STR_TCP | 45767
STRCrpalkeGrfs8PreklopkaMode | INT | IOD_STR_TCP | 40593
STRCrpalkeGrfs8PretokMax | REAL | IOD_STR_TCP | 45769 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs8PretokMin | REAL | IOD_STR_TCP | 45771 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs8PretokTrenutni | REAL | IOD_STR_TCP | 45773 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs8PritiskMax | REAL | IOD_STR_TCP | 45775 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs8PritiskTrenutni | REAL | IOD_STR_TCP | 45777 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs8ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 45779 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs8ReferencaRemote | REAL | IOD_STR_TCP | 45781 | 0 | 100 | 0 | 100 | % | ####.#
STRCrpalkeGrfs8Relay1setup | INT | IOD_STR_TCP | 40594
STRCrpalkeGrfs8RemoteON | DIGITAL | IOD_STR_TCP | 00315
STRCrpalkeGrfs8RemoteSetupMode1 | INT | IOD_STR_TCP | 40595
STRCrpalkeGrfs8Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 00316
STRCrpalkeGrfs8ResetAlarm | DIGITAL | IOD_STR_TCP | 00317
STRCrpalkeGrfs8ResetAlarmLog | DIGITAL | IOD_STR_TCP | 00318
STRCrpalkeGrfs8ResetDevice | DIGITAL | IOD_STR_TCP | 00319
STRCrpalkeGrfs8SetAutomatic | DIGITAL | IOD_STR_TCP | 00320
STRCrpalkeGrfs8SetConstFreqMode | DIGITAL | IOD_STR_TCP | 00321
STRCrpalkeGrfs8SetConstPress | DIGITAL | IOD_STR_TCP | 00322
STRCrpalkeGrfs8SetLocalMode | DIGITAL | IOD_STR_TCP | 00323
STRCrpalkeGrfs8SetMaxRunMode | DIGITAL | IOD_STR_TCP | 00324
STRCrpalkeGrfs8SetMinRunMode | DIGITAL | IOD_STR_TCP | 00325
STRCrpalkeGrfs8SetPropPress | DIGITAL | IOD_STR_TCP | 00326
STRCrpalkeGrfs8SetReference | DIGITAL | IOD_STR_TCP | 00327
STRCrpalkeGrfs8SetRemoteMode | DIGITAL | IOD_STR_TCP | 00328
STRCrpalkeGrfs8SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 00329
STRCrpalkeGrfs8SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 00330
STRCrpalkeGrfs8SetTwinModeSync | DIGITAL | IOD_STR_TCP | 00331
STRCrpalkeGrfs8Start | DIGITAL | IOD_STR_TCP | 00332
STRCrpalkeGrfs8StatusCrpalke | INT | IOD_STR_TCP | 40596
STRCrpalkeGrfs8StatusMode1 | INT | IOD_STR_TCP | 40597
STRCrpalkeGrfs8StatusMode1co | INT | IOD_STR_TCP | 40598
STRCrpalkeGrfs8StatusMode1op | INT | IOD_STR_TCP | 40599
STRCrpalkeGrfs8StatusMode2 | INT | IOD_STR_TCP | 40600
STRCrpalkeGrfs8StatusMode3 | INT | IOD_STR_TCP | 40601
STRCrpalkeGrfs8StevecUr2h | REAL | IOD_STR_TCP | 45783 |  |  |  |  | 2h
STRCrpalkeGrfs8Stop | DIGITAL | IOD_STR_TCP | 00333
STRCrpalkeGrfs8SystemFeedback | REAL | IOD_STR_TCP | 45785
STRCrpalkeGrfs8SystemReference | REAL | IOD_STR_TCP | 45787
STRCrpalkeGrfs8TemperaturaMotorja | REAL | IOD_STR_TCP | 45789 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeGrfs8UreXC200 | REAL | IOD_STR_TCP | 45791 |  |  |  |  | h | ####.#
STRCrpalkeGrfs9AlarmActiveCode | INT | IOD_STR_TCP | 40602
STRCrpalkeGrfs9AlarmAktiven | DIGITAL | IOD_STR_TCP | 00334
STRCrpalkeGrfs9AlarmCodeLog1 | INT | IOD_STR_TCP | 40603
STRCrpalkeGrfs9AlarmCodeLog2 | INT | IOD_STR_TCP | 40604
STRCrpalkeGrfs9AlarmCodeLog3 | INT | IOD_STR_TCP | 40605
STRCrpalkeGrfs9AlarmCodeLog4 | INT | IOD_STR_TCP | 40606
STRCrpalkeGrfs9AlarmCodeLog5 | INT | IOD_STR_TCP | 40607
STRCrpalkeGrfs9AlarmGroupXVH0 | INT | IOD_STR_TCP | 40608
STRCrpalkeGrfs9AlarmGroupXVH10 | INT | IOD_STR_TCP | 40609
STRCrpalkeGrfs9AlarmGroupXVH11 | INT | IOD_STR_TCP | 40610
STRCrpalkeGrfs9AlarmGroupXVH12 | INT | IOD_STR_TCP | 40611
STRCrpalkeGrfs9AlarmGroupXVH13 | INT | IOD_STR_TCP | 40612
STRCrpalkeGrfs9AlarmGroupXVH14 | INT | IOD_STR_TCP | 40613
STRCrpalkeGrfs9AlarmGroupXVH15 | INT | IOD_STR_TCP | 40614
STRCrpalkeGrfs9AlarmGroupXVH16 | INT | IOD_STR_TCP | 40615
STRCrpalkeGrfs9AlarmGroupXVH1 | INT | IOD_STR_TCP | 40616
STRCrpalkeGrfs9AlarmGroupXVH2 | INT | IOD_STR_TCP | 40617
STRCrpalkeGrfs9AlarmGroupXVH3 | INT | IOD_STR_TCP | 40618
STRCrpalkeGrfs9AlarmGroupXVH4 | INT | IOD_STR_TCP | 40619
STRCrpalkeGrfs9AlarmGroupXVH5 | INT | IOD_STR_TCP | 40620
STRCrpalkeGrfs9AlarmGroupXVH6 | INT | IOD_STR_TCP | 40621
STRCrpalkeGrfs9AlarmGroupXVH7 | INT | IOD_STR_TCP | 40622
STRCrpalkeGrfs9AlarmGroupXVH8 | INT | IOD_STR_TCP | 40623
STRCrpalkeGrfs9AlarmGroupXVH9 | INT | IOD_STR_TCP | 40624
STRCrpalkeGrfs9AlarmQSD1 | INT | IOD_STR_TCP | 40625
STRCrpalkeGrfs9AlarmQSD2 | INT | IOD_STR_TCP | 40626
STRCrpalkeGrfs9AlarmStart1 | INT | IOD_STR_TCP | 40627
STRCrpalkeGrfs9AlarmStart2 | INT | IOD_STR_TCP | 40628
STRCrpalkeGrfs9AlarmStop1 | INT | IOD_STR_TCP | 40629
STRCrpalkeGrfs9AlarmStop2 | INT | IOD_STR_TCP | 40630
STRCrpalkeGrfs9AlarmStop3 | INT | IOD_STR_TCP | 40631
STRCrpalkeGrfs9AlarmSurv1 | INT | IOD_STR_TCP | 40632
STRCrpalkeGrfs9AlarmSurv2 | INT | IOD_STR_TCP | 40633
STRCrpalkeGrfs9ControlSource | INT | IOD_STR_TCP | 40634
STRCrpalkeGrfs9DeltaSetPoint | REAL | IOD_STR_TCP | 45793
STRCrpalkeGrfs9Deluje | DIGITAL | IOD_STR_TCP | 00335
STRCrpalkeGrfs9EnergijaPoraba | REAL | IOD_STR_TCP | 45795 |  |  |  |  | kWh | ####.#
STRCrpalkeGrfs9ExternInputSetup | INT | IOD_STR_TCP | 40635
STRCrpalkeGrfs9ExternInputsStatus | INT | IOD_STR_TCP | 40636
STRCrpalkeGrfs9FrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 45797 | 0 | 500 | 0 | 500 | V | ####.#
STRCrpalkeGrfs9FrekPretvornikDCTok | REAL | IOD_STR_TCP | 45799 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs9FreqMax | REAL | IOD_STR_TCP | 45801 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs9FreqMin | REAL | IOD_STR_TCP | 45803 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs9FreqUpper | REAL | IOD_STR_TCP | 45805 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs9LocalMode | DIGITAL | IOD_STR_TCP | 00336
STRCrpalkeGrfs9LocalSetupMode1 | INT | IOD_STR_TCP | 40637
STRCrpalkeGrfs9MocMax | REAL | IOD_STR_TCP | 45807 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs9MocTrenutna | REAL | IOD_STR_TCP | 45809 | 0 | 10000 | 0 | 10000 | W | ####.#
STRCrpalkeGrfs9MotorHitrost | REAL | IOD_STR_TCP | 45811 | 0 | 2500 | 0 | 2500 | obr/min | ####.#
STRCrpalkeGrfs9MotorTok | REAL | IOD_STR_TCP | 45813 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs9NapajanjeTok | REAL | IOD_STR_TCP | 45815 | 0 | 100 | 0 | 100 | A | ####.#
STRCrpalkeGrfs9NastavitevLokalna | REAL | IOD_STR_TCP | 45817
STRCrpalkeGrfs9NastavitevTrenutna | REAL | IOD_STR_TCP | 45819
STRCrpalkeGrfs9PreklopkaMode | INT | IOD_STR_TCP | 40638
STRCrpalkeGrfs9PretokMax | REAL | IOD_STR_TCP | 45821 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs9PretokMin | REAL | IOD_STR_TCP | 45823 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs9PretokTrenutni | REAL | IOD_STR_TCP | 45825 | 0 | 10 | 0 | 10 | m3/h | ####.#
STRCrpalkeGrfs9PritiskMax | REAL | IOD_STR_TCP | 45827 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs9PritiskTrenutni | REAL | IOD_STR_TCP | 45829 | 0 | 15 | 0 | 15 | bar | ####.#
STRCrpalkeGrfs9ReferencaMotorjaHzV | REAL | IOD_STR_TCP | 45831 | 0 | 70 | 0 | 70 | Hz | ####.#
STRCrpalkeGrfs9ReferencaRemote | REAL | IOD_STR_TCP | 45833 | 0 | 100 | 0 | 100 | % | ####.#
STRCrpalkeGrfs9Relay1setup | INT | IOD_STR_TCP | 40639
STRCrpalkeGrfs9RemoteON | DIGITAL | IOD_STR_TCP | 00337
STRCrpalkeGrfs9RemoteSetupMode1 | INT | IOD_STR_TCP | 40640
STRCrpalkeGrfs9Reset2handkWhValues | DIGITAL | IOD_STR_TCP | 00338
STRCrpalkeGrfs9ResetAlarm | DIGITAL | IOD_STR_TCP | 00339
STRCrpalkeGrfs9ResetAlarmLog | DIGITAL | IOD_STR_TCP | 00340
STRCrpalkeGrfs9ResetDevice | DIGITAL | IOD_STR_TCP | 00341
STRCrpalkeGrfs9SetAutomatic | DIGITAL | IOD_STR_TCP | 00342
STRCrpalkeGrfs9SetConstFreqMode | DIGITAL | IOD_STR_TCP | 00343
STRCrpalkeGrfs9SetConstPress | DIGITAL | IOD_STR_TCP | 00344
STRCrpalkeGrfs9SetLocalMode | DIGITAL | IOD_STR_TCP | 00345
STRCrpalkeGrfs9SetMaxRunMode | DIGITAL | IOD_STR_TCP | 00346
STRCrpalkeGrfs9SetMinRunMode | DIGITAL | IOD_STR_TCP | 00347
STRCrpalkeGrfs9SetPropPress | DIGITAL | IOD_STR_TCP | 00348
STRCrpalkeGrfs9SetReference | DIGITAL | IOD_STR_TCP | 00349
STRCrpalkeGrfs9SetRemoteMode | DIGITAL | IOD_STR_TCP | 00350
STRCrpalkeGrfs9SetTwinModeAlt | DIGITAL | IOD_STR_TCP | 00351
STRCrpalkeGrfs9SetTwinModeSpare | DIGITAL | IOD_STR_TCP | 00352
STRCrpalkeGrfs9SetTwinModeSync | DIGITAL | IOD_STR_TCP | 00353
STRCrpalkeGrfs9Start | DIGITAL | IOD_STR_TCP | 00354
STRCrpalkeGrfs9StatusCrpalke | INT | IOD_STR_TCP | 40641
STRCrpalkeGrfs9StatusMode1 | INT | IOD_STR_TCP | 40642
STRCrpalkeGrfs9StatusMode1co | INT | IOD_STR_TCP | 40643
STRCrpalkeGrfs9StatusMode1op | INT | IOD_STR_TCP | 40644
STRCrpalkeGrfs9StatusMode2 | INT | IOD_STR_TCP | 40645
STRCrpalkeGrfs9StatusMode3 | INT | IOD_STR_TCP | 40646
STRCrpalkeGrfs9StevecUr2h | REAL | IOD_STR_TCP | 45835 |  |  |  |  | 2h
STRCrpalkeGrfs9Stop | DIGITAL | IOD_STR_TCP | 00355
STRCrpalkeGrfs9SystemFeedback | REAL | IOD_STR_TCP | 45837
STRCrpalkeGrfs9SystemReference | REAL | IOD_STR_TCP | 45839
STRCrpalkeGrfs9TemperaturaMotorja | REAL | IOD_STR_TCP | 45841 | 0 | 150 | 0 | 150 | °C | ####.#
STRCrpalkeGrfs9UreXC200 | REAL | IOD_STR_TCP | 45843 |  |  |  |  | h | ####.#
STRCrpDanfossGenError1 | DIGITAL | IOD_STR_TCP | 00356
STRCrpDanfossGenError2 | DIGITAL | IOD_STR_TCP | 00357
STRCrpDanfossGenError3 | DIGITAL | IOD_STR_TCP | 00358
STRCrpDanfossGenError4 | DIGITAL | IOD_STR_TCP | 00359
STRCrpDanfossNaCas1 | DIGITAL | IOD_STR_TCP | 00360
STRCrpDanfossNaCas2 | DIGITAL | IOD_STR_TCP | 00361
STRCrpDanfossON1 | DIGITAL | IOD_STR_TCP | 00362
STRCrpDanfossON2 | DIGITAL | IOD_STR_TCP | 00363
STRCrpDanfossON3 | DIGITAL | IOD_STR_TCP | 00364
STRCrpDanfossON4 | DIGITAL | IOD_STR_TCP | 00365
STRCrpDanfossStatusError1 | DIGITAL | IOD_STR_TCP | 00366
STRCrpDanfossStatusError2 | DIGITAL | IOD_STR_TCP | 00367
STRCrpDanfossStatusError3 | DIGITAL | IOD_STR_TCP | 00368
STRCrpDanfossStatusError4 | DIGITAL | IOD_STR_TCP | 00369
STRCrpGrundfosGenError10 | DIGITAL | IOD_STR_TCP | 00370
STRCrpGrundfosGenError11 | DIGITAL | IOD_STR_TCP | 00371
STRCrpGrundfosGenError12 | DIGITAL | IOD_STR_TCP | 00372
STRCrpGrundfosGenError13 | DIGITAL | IOD_STR_TCP | 00373
STRCrpGrundfosGenError14 | DIGITAL | IOD_STR_TCP | 00374
STRCrpGrundfosGenError1 | DIGITAL | IOD_STR_TCP | 00375
STRCrpGrundfosGenError2 | DIGITAL | IOD_STR_TCP | 00376
STRCrpGrundfosGenError3 | DIGITAL | IOD_STR_TCP | 00377
STRCrpGrundfosGenError4 | DIGITAL | IOD_STR_TCP | 00378
STRCrpGrundfosGenError5 | DIGITAL | IOD_STR_TCP | 00379
STRCrpGrundfosGenError6 | DIGITAL | IOD_STR_TCP | 00380
STRCrpGrundfosGenError7 | DIGITAL | IOD_STR_TCP | 00381
STRCrpGrundfosGenError8 | DIGITAL | IOD_STR_TCP | 00382
STRCrpGrundfosGenError9 | DIGITAL | IOD_STR_TCP | 00383
STRCrpGrundfosNaCas1 | DIGITAL | IOD_STR_TCP | 00384
STRCrpGrundfosNaCas2 | DIGITAL | IOD_STR_TCP | 00385
STRCrpGrundfosNaCas3 | DIGITAL | IOD_STR_TCP | 00386
STRCrpGrundfosNaCas4 | DIGITAL | IOD_STR_TCP | 00387
STRCrpGrundfosNaCas5 | DIGITAL | IOD_STR_TCP | 00388
STRCrpGrundfosNaCas6 | DIGITAL | IOD_STR_TCP | 00389
STRCrpGrundfosNaCas7 | DIGITAL | IOD_STR_TCP | 00390
STRCrpGrundfosNaTlak1 | DIGITAL | IOD_STR_TCP | 00391
STRCrpGrundfosNaTlak2 | DIGITAL | IOD_STR_TCP | 00392
STRCrpGrundfosNaTlak3 | DIGITAL | IOD_STR_TCP | 00393
STRCrpGrundfosNaTlak4 | DIGITAL | IOD_STR_TCP | 00394
STRCrpGrundfosNaTlak5 | DIGITAL | IOD_STR_TCP | 00395
STRCrpGrundfosNaTlak6 | DIGITAL | IOD_STR_TCP | 00396
STRCrpGrundfosNaTlak7 | DIGITAL | IOD_STR_TCP | 00397
STRCrpGrundfosON10 | DIGITAL | IOD_STR_TCP | 00398
STRCrpGrundfosON11 | DIGITAL | IOD_STR_TCP | 00399
STRCrpGrundfosON12 | DIGITAL | IOD_STR_TCP | 00400
STRCrpGrundfosON13 | DIGITAL | IOD_STR_TCP | 00401
STRCrpGrundfosON14 | DIGITAL | IOD_STR_TCP | 00402
STRCrpGrundfosON1 | DIGITAL | IOD_STR_TCP | 00403
STRCrpGrundfosON2 | DIGITAL | IOD_STR_TCP | 00404
STRCrpGrundfosON3 | DIGITAL | IOD_STR_TCP | 00405
STRCrpGrundfosON4 | DIGITAL | IOD_STR_TCP | 00406
STRCrpGrundfosON5 | DIGITAL | IOD_STR_TCP | 00407
STRCrpGrundfosON6 | DIGITAL | IOD_STR_TCP | 00408
STRCrpGrundfosON7 | DIGITAL | IOD_STR_TCP | 00409
STRCrpGrundfosON8 | DIGITAL | IOD_STR_TCP | 00410
STRCrpGrundfosON9 | DIGITAL | IOD_STR_TCP | 00411
STRCrpGrundfosStatusError10 | DIGITAL | IOD_STR_TCP | 00412
STRCrpGrundfosStatusError11 | DIGITAL | IOD_STR_TCP | 00413
STRCrpGrundfosStatusError12 | DIGITAL | IOD_STR_TCP | 00414
STRCrpGrundfosStatusError13 | DIGITAL | IOD_STR_TCP | 00415
STRCrpGrundfosStatusError14 | DIGITAL | IOD_STR_TCP | 00416
STRCrpGrundfosStatusError1 | DIGITAL | IOD_STR_TCP | 00417
STRCrpGrundfosStatusError2 | DIGITAL | IOD_STR_TCP | 00418
STRCrpGrundfosStatusError3 | DIGITAL | IOD_STR_TCP | 00419
STRCrpGrundfosStatusError4 | DIGITAL | IOD_STR_TCP | 00420
STRCrpGrundfosStatusError5 | DIGITAL | IOD_STR_TCP | 00421
STRCrpGrundfosStatusError6 | DIGITAL | IOD_STR_TCP | 00422
STRCrpGrundfosStatusError7 | DIGITAL | IOD_STR_TCP | 00423
STRCrpGrundfosStatusError8 | DIGITAL | IOD_STR_TCP | 00424
STRCrpGrundfosStatusError9 | DIGITAL | IOD_STR_TCP | 00425
STRCrpGrundfosTlakSP1 | REAL | IOD_STR_TCP | 45845 | 0 | 5 | 0 | 5 | bar | ####.#
STRCrpGrundfosTlakSP2 | REAL | IOD_STR_TCP | 45847 | 0 | 5 | 0 | 5 | bar | ####.#
STRCrpGrundfosTlakSP3 | REAL | IOD_STR_TCP | 45849 | 0 | 5 | 0 | 5 | bar | ####.#
STRCrpGrundfosTlakSP4 | REAL | IOD_STR_TCP | 45851 | 0 | 5 | 0 | 5 | bar | ####.#
STRCrpGrundfosTlakSP5 | REAL | IOD_STR_TCP | 45853 | 0 | 5 | 0 | 5 | bar | ####.#
STRCrpGrundfosTlakSP6 | REAL | IOD_STR_TCP | 45855 | 0 | 5 | 0 | 5 | bar | ####.#
STRCrpGrundfosTlakSP7 | REAL | IOD_STR_TCP | 45857 | 0 | 5 | 0 | 5 | bar | ####.#
STRDanfossHMKontOnOff1 | DIGITAL | IOD_STR_TCP | 00426
STRDanfossHMKontOnOff2 | DIGITAL | IOD_STR_TCP | 00427
STRDanfossHMKontOnOff3 | DIGITAL | IOD_STR_TCP | 00428
STRDanfossHMKontOnOff4 | DIGITAL | IOD_STR_TCP | 00429
STRDateTimeDan | INT | IOD_STR_TCP | 40647
STRDateTimeLeto | INT | IOD_STR_TCP | 40648
STRDateTimeMesec | INT | IOD_STR_TCP | 40649
STRDateTimeMinuta | INT | IOD_STR_TCP | 40650
STRDateTimeSekunda | INT | IOD_STR_TCP | 40651
STRDateTimeUra | INT | IOD_STR_TCP | 40652
STRDI_230VAC_OK | DIGITAL | IOD_STR_TCP | 00430
STRDI_24VAC_OK | DIGITAL | IOD_STR_TCP | 00431
STRDI_24VDC_OK | DIGITAL | IOD_STR_TCP | 00432
STRDI_AkumTopVodeAUTO | DIGITAL | IOD_STR_TCP | 00433
STRDI_AkumTopVodeKontON | DIGITAL | IOD_STR_TCP | 00434
STRDI_CrpHM1AUTO | DIGITAL | IOD_STR_TCP | 00435
STRDI_CrpHM1endOFFtoON | DIGITAL | IOD_STR_TCP | 00436
STRDI_CrpHM1ERR | DIGITAL | IOD_STR_TCP | 00437
STRDI_CrpHM1kontON | DIGITAL | IOD_STR_TCP | 00438
STRDI_CrpHM2AUTO | DIGITAL | IOD_STR_TCP | 00439
STRDI_CrpHM2endOFFtoON | DIGITAL | IOD_STR_TCP | 00440
STRDI_CrpHM2ERR | DIGITAL | IOD_STR_TCP | 00441
STRDI_CrpHM2kontON | DIGITAL | IOD_STR_TCP | 00442
STRDI_CrpHM3AUTO | DIGITAL | IOD_STR_TCP | 00443
STRDI_CrpHM3endOFFtoON | DIGITAL | IOD_STR_TCP | 00444
STRDI_CrpHM3ERR | DIGITAL | IOD_STR_TCP | 00445
STRDI_CrpHM3kontON | DIGITAL | IOD_STR_TCP | 00446
STRDI_CrpHM4AUTO | DIGITAL | IOD_STR_TCP | 00447
STRDI_CrpHM4endOFFtoON | DIGITAL | IOD_STR_TCP | 00448
STRDI_CrpHM4ERR | DIGITAL | IOD_STR_TCP | 00449
STRDI_CrpHM4kontON | DIGITAL | IOD_STR_TCP | 00450
STRDI_CrpHM5AUTO | DIGITAL | IOD_STR_TCP | 00451
STRDI_CrpHM6AUTO | DIGITAL | IOD_STR_TCP | 00452
STRDI_CrpHM7AUTO | DIGITAL | IOD_STR_TCP | 00453
STRDI_CrpHM8AUTO | DIGITAL | IOD_STR_TCP | 00454
STRDI_CrpMN1AUTO | DIGITAL | IOD_STR_TCP | 00455
STRDI_CrpMN1kontON | DIGITAL | IOD_STR_TCP | 00456
STRDI_CrpTM10AUTO | DIGITAL | IOD_STR_TCP | 00457
STRDI_CrpTM11TM12AUTO | DIGITAL | IOD_STR_TCP | 00458
STRDI_CrpTM11TM12kontON | DIGITAL | IOD_STR_TCP | 00459
STRDI_CrpTM1AUTO | DIGITAL | IOD_STR_TCP | 00460
STRDI_CrpTM2AUTO | DIGITAL | IOD_STR_TCP | 00461
STRDI_CrpTM3AUTO | DIGITAL | IOD_STR_TCP | 00462
STRDI_CrpTM4AUTO | DIGITAL | IOD_STR_TCP | 00463
STRDI_CrpTM5AUTO | DIGITAL | IOD_STR_TCP | 00464
STRDI_CrpTM6AUTO | DIGITAL | IOD_STR_TCP | 00465
STRDI_CrpTM7AUTO | DIGITAL | IOD_STR_TCP | 00466
STRDI_CrpTM8AUTO | DIGITAL | IOD_STR_TCP | 00467
STRDI_CrpTM9AUTO | DIGITAL | IOD_STR_TCP | 00468
STRDI_GlStikaloDieselON | DIGITAL | IOD_STR_TCP | 00469
STRDI_GlStikaloMrezaON | DIGITAL | IOD_STR_TCP | 00470
STRDI_GlStikaloUpsON | DIGITAL | IOD_STR_TCP | 00471
STRDI_HladStAUTO | DIGITAL | IOD_STR_TCP | 00472
STRDI_HladStCrpHladH2OON | DIGITAL | IOD_STR_TCP | 00473
STRDI_HladStERR | DIGITAL | IOD_STR_TCP | 00474
STRDI_Klima1ERR | DIGITAL | IOD_STR_TCP | 00475
STRDI_Klima1filterZAM | DIGITAL | IOD_STR_TCP | 00476
STRDI_Klima1FIRE | DIGITAL | IOD_STR_TCP | 00477
STRDI_Klima1OFFtoON | DIGITAL | IOD_STR_TCP | 00478
STRDI_Klima1ON | DIGITAL | IOD_STR_TCP | 00479
STRDI_Klima1zascStON | DIGITAL | IOD_STR_TCP | 00480
STRDI_Klima2ERR | DIGITAL | IOD_STR_TCP | 00481
STRDI_Klima2filterZAM | DIGITAL | IOD_STR_TCP | 00482
STRDI_Klima2FIRE | DIGITAL | IOD_STR_TCP | 00483
STRDI_Klima2OFFtoON | DIGITAL | IOD_STR_TCP | 00484
STRDI_Klima2ON | DIGITAL | IOD_STR_TCP | 00485
STRDI_Klima2zascStON | DIGITAL | IOD_STR_TCP | 00486
STRDI_Komp1ERR | DIGITAL | IOD_STR_TCP | 00487
STRDI_Komp1ON | DIGITAL | IOD_STR_TCP | 00488
STRDI_Komp2ERR | DIGITAL | IOD_STR_TCP | 00489
STRDI_Komp2ON | DIGITAL | IOD_STR_TCP | 00490
STRDI_Kond1AUTO | DIGITAL | IOD_STR_TCP | 00491
STRDI_Kond1FS1FS2 | DIGITAL | IOD_STR_TCP | 00492
STRDI_Kond1ON | DIGITAL | IOD_STR_TCP | 00493
STRDI_Kond1zascStON | DIGITAL | IOD_STR_TCP | 00494
STRDI_Kond2AUTO | DIGITAL | IOD_STR_TCP | 00495
STRDI_Kond2FS1FS2 | DIGITAL | IOD_STR_TCP | 00496
STRDI_Kond2ON | DIGITAL | IOD_STR_TCP | 00497
STRDI_Kond2zascStON | DIGITAL | IOD_STR_TCP | 00498
STRDI_Kond3AUTO | DIGITAL | IOD_STR_TCP | 00499
STRDI_Kond3FS1FS2 | DIGITAL | IOD_STR_TCP | 00500
STRDI_Kond3ON | DIGITAL | IOD_STR_TCP | 00501
STRDI_Kond3zascStON | DIGITAL | IOD_STR_TCP | 00502
STRDI_Lop1PL1Odprta | DIGITAL | IOD_STR_TCP | 00503
STRDI_Lop1PL1Zaprta | DIGITAL | IOD_STR_TCP | 00504
STRDI_Lop1PL2Odprta | DIGITAL | IOD_STR_TCP | 00505
STRDI_Lop1PL2Zaprta | DIGITAL | IOD_STR_TCP | 00506
STRDI_Lop1PL3Odprta | DIGITAL | IOD_STR_TCP | 00507
STRDI_Lop1PL3Zaprta | DIGITAL | IOD_STR_TCP | 00508
STRDI_Lop3Y1Odprta | DIGITAL | IOD_STR_TCP | 00509
STRDI_Lop3Y1Zaprta | DIGITAL | IOD_STR_TCP | 00510
STRDI_Lop4Y1Odprta | DIGITAL | IOD_STR_TCP | 00511
STRDI_Lop4Y1Zaprta | DIGITAL | IOD_STR_TCP | 00512
STRDI_PotrditevAlarmov | DIGITAL | IOD_STR_TCP | 00513
STRDI_RazlitjeVodeEXP1 | DIGITAL | IOD_STR_TCP | 00514
STRDI_RazlitjeVodeEXP2 | DIGITAL | IOD_STR_TCP | 00515
STRDI_RazlitjeVodeHP | DIGITAL | IOD_STR_TCP | 00516
STRDI_RazlitjeVodeK1 | DIGITAL | IOD_STR_TCP | 00517
STRDI_RazlitjeVodeK2 | DIGITAL | IOD_STR_TCP | 00518
STRDI_RazlitjeVodeTP | DIGITAL | IOD_STR_TCP | 00519
STRDI_ToplPostGenErr | DIGITAL | IOD_STR_TCP | 00520
STRDI_UPS_Alarm | DIGITAL | IOD_STR_TCP | 00521
STRDI_UPS_BatNacin | DIGITAL | IOD_STR_TCP | 00522
STRDI_UPS_Polnjenje | DIGITAL | IOD_STR_TCP | 00523
STRDI_Vent1Auto | DIGITAL | IOD_STR_TCP | 00524
STRDI_Vent1kontON | DIGITAL | IOD_STR_TCP | 00525
STRDI_Vent2Auto | DIGITAL | IOD_STR_TCP | 00526
STRDI_Vent2kontON | DIGITAL | IOD_STR_TCP | 00527
STRDI_Vent3Auto | DIGITAL | IOD_STR_TCP | 00528
STRDI_Vent3kontON | DIGITAL | IOD_STR_TCP | 00529
STRDI_Vent4Auto | DIGITAL | IOD_STR_TCP | 00530
STRDI_Vent4kontON | DIGITAL | IOD_STR_TCP | 00531
STRDI_Vent5Auto | DIGITAL | IOD_STR_TCP | 00532
STRDI_Vent5kontON | DIGITAL | IOD_STR_TCP | 00533
STRDI_Vent6Auto | DIGITAL | IOD_STR_TCP | 00534
STRDI_Vent6kontON | DIGITAL | IOD_STR_TCP | 00535
STRDI_Vlaz1ERR | DIGITAL | IOD_STR_TCP | 00536
STRDI_Vlaz1ON | DIGITAL | IOD_STR_TCP | 00537
STRDI_Vlaz2ERR | DIGITAL | IOD_STR_TCP | 00538
STRDI_Vlaz2ON | DIGITAL | IOD_STR_TCP | 00539
STRDIN_230VAC_OK | DIGITAL | IOD_STR_TCP | 00540
STRDIN_24VAC_OK | DIGITAL | IOD_STR_TCP | 00541
STRDIN_24VDC_OK | DIGITAL | IOD_STR_TCP | 00542
STRDIN_CrpHM1ERR | DIGITAL | IOD_STR_TCP | 00543
STRDIN_CrpHM2ERR | DIGITAL | IOD_STR_TCP | 00544
STRDIN_CrpHM3ERR | DIGITAL | IOD_STR_TCP | 00545
STRDIN_CrpHM4ERR | DIGITAL | IOD_STR_TCP | 00546
STRDIN_HladStERR | DIGITAL | IOD_STR_TCP | 00547
STRDIN_Klima1ERR | DIGITAL | IOD_STR_TCP | 00548
STRDIN_Klima1filterZAM | DIGITAL | IOD_STR_TCP | 00549
STRDIN_Klima1zascStON | DIGITAL | IOD_STR_TCP | 00550
STRDIN_Klima2ERR | DIGITAL | IOD_STR_TCP | 00551
STRDIN_Klima2filterZAM | DIGITAL | IOD_STR_TCP | 00552
STRDIN_Klima2zascStON | DIGITAL | IOD_STR_TCP | 00553
STRDIN_Komp1ERR | DIGITAL | IOD_STR_TCP | 00554
STRDIN_Komp1ON | DIGITAL | IOD_STR_TCP | 00555
STRDIN_Komp2ERR | DIGITAL | IOD_STR_TCP | 00556
STRDIN_Komp2ON | DIGITAL | IOD_STR_TCP | 00557
STRDIN_Kond1zascStON | DIGITAL | IOD_STR_TCP | 00558
STRDIN_Kond2zascStON | DIGITAL | IOD_STR_TCP | 00559
STRDIN_Kond3zascStON | DIGITAL | IOD_STR_TCP | 00560
STRDIN_Vlaz1ERR | DIGITAL | IOD_STR_TCP | 00561
STRDIN_Vlaz2ERR | DIGITAL | IOD_STR_TCP | 00562
STRDO_BojlerTE1Vklop | DIGITAL | IOD_STR_TCP | 00563
STRDO_CrpHM1Vklop | DIGITAL | IOD_STR_TCP | 00564
STRDO_CrpHM2Vklop | DIGITAL | IOD_STR_TCP | 00565
STRDO_CrpHM3Vklop | DIGITAL | IOD_STR_TCP | 00566
STRDO_CrpHM4Vklop | DIGITAL | IOD_STR_TCP | 00567
STRDO_CrpMN1Vklop | DIGITAL | IOD_STR_TCP | 00568
STRDO_CrpTM11Vklop | DIGITAL | IOD_STR_TCP | 00569
STRDO_GrundfosVklopL | DIGITAL | IOD_STR_TCP | 00570
STRDO_GrundfosVklopN | DIGITAL | IOD_STR_TCP | 00571
STRDO_HladStrIzklop | DIGITAL | IOD_STR_TCP | 00572
STRDO_KE1Vklop | DIGITAL | IOD_STR_TCP | 00573
STRDO_KE2Vklop | DIGITAL | IOD_STR_TCP | 00574
STRDO_KE3Vklop | DIGITAL | IOD_STR_TCP | 00575
STRDO_Klima1Vklop | DIGITAL | IOD_STR_TCP | 00576
STRDO_Klima2Vklop | DIGITAL | IOD_STR_TCP | 00577
STRDO_Lop1PL1Vklop | DIGITAL | IOD_STR_TCP | 00578
STRDO_Lop1PL2Vklop | DIGITAL | IOD_STR_TCP | 00579
STRDO_Lop1PL3Vklop | DIGITAL | IOD_STR_TCP | 00580
STRDO_Lop3Y1Vklop | DIGITAL | IOD_STR_TCP | 00581
STRDO_Lop4Y1Vklop | DIGITAL | IOD_STR_TCP | 00582
STRDO_RazE11_10Vklop | DIGITAL | IOD_STR_TCP | 00583
STRDO_RazE11_11Vklop | DIGITAL | IOD_STR_TCP | 00584
STRDO_RazE11_1Vklop | DIGITAL | IOD_STR_TCP | 00585
STRDO_RazE11_2Vklop | DIGITAL | IOD_STR_TCP | 00586
STRDO_RazE11_3Vklop | DIGITAL | IOD_STR_TCP | 00587
STRDO_RazE11_4Vklop | DIGITAL | IOD_STR_TCP | 00588
STRDO_RazE11_5Vklop | DIGITAL | IOD_STR_TCP | 00589
STRDO_RazE11_6Vklop | DIGITAL | IOD_STR_TCP | 00590
STRDO_RazE11_7Vklop | DIGITAL | IOD_STR_TCP | 00591
STRDO_RazE11_8Vklop | DIGITAL | IOD_STR_TCP | 00592
STRDO_RazE11_9Vklop | DIGITAL | IOD_STR_TCP | 00593
STRDO_RazE12_12Vklop | DIGITAL | IOD_STR_TCP | 00594
STRDO_RazE12_13Vklop | DIGITAL | IOD_STR_TCP | 00595
STRDO_RazE12_14Vklop | DIGITAL | IOD_STR_TCP | 00596
STRDO_RazE12_15Vklop | DIGITAL | IOD_STR_TCP | 00597
STRDO_RazE13_16Vklop | DIGITAL | IOD_STR_TCP | 00598
STRDO_RazE13_17Vklop | DIGITAL | IOD_STR_TCP | 00599
STRDO_RazE13_18Vklop | DIGITAL | IOD_STR_TCP | 00600
STRDO_RazE13_19Vklop | DIGITAL | IOD_STR_TCP | 00601
STRDO_RazE16_20Vklop | DIGITAL | IOD_STR_TCP | 00602
STRDO_RazE16_21Vklop | DIGITAL | IOD_STR_TCP | 00603
STRDO_RazE16_22Vklop | DIGITAL | IOD_STR_TCP | 00604
STRDO_RazE16_23Vklop | DIGITAL | IOD_STR_TCP | 00605
STRDO_RazE16_24Vklop | DIGITAL | IOD_STR_TCP | 00606
STRDO_Vent1Vklop | DIGITAL | IOD_STR_TCP | 00607
STRDO_Vent2Vklop | DIGITAL | IOD_STR_TCP | 00608
STRDO_Vent3Vklop | DIGITAL | IOD_STR_TCP | 00609
STRDO_Vent4Vklop | DIGITAL | IOD_STR_TCP | 00610
STRDO_Vent5Vklop | DIGITAL | IOD_STR_TCP | 00611
STRDO_Vent6Vklop | DIGITAL | IOD_STR_TCP | 00612
STRErrComCirc1 | DIGITAL | IOD_STR_TCP | 00613
STRErrComCirc2 | DIGITAL | IOD_STR_TCP | 00614
STRErrComDanfossHM1 | DIGITAL | IOD_STR_TCP | 00615
STRErrComDanfossHM2 | DIGITAL | IOD_STR_TCP | 00616
STRErrComDanfossHM3 | DIGITAL | IOD_STR_TCP | 00617
STRErrComDanfossHM4 | DIGITAL | IOD_STR_TCP | 00618
STRErrComGrundfos0 | DIGITAL | IOD_STR_TCP | 00619
STRErrComGrundfos10 | DIGITAL | IOD_STR_TCP | 00620
STRErrComGrundfos11 | DIGITAL | IOD_STR_TCP | 00621
STRErrComGrundfos12 | DIGITAL | IOD_STR_TCP | 00622
STRErrComGrundfos13 | DIGITAL | IOD_STR_TCP | 00623
STRErrComGrundfos14 | DIGITAL | IOD_STR_TCP | 00624
STRErrComGrundfos1 | DIGITAL | IOD_STR_TCP | 00625
STRErrComGrundfos2 | DIGITAL | IOD_STR_TCP | 00626
STRErrComGrundfos3 | DIGITAL | IOD_STR_TCP | 00627
STRErrComGrundfos4 | DIGITAL | IOD_STR_TCP | 00628
STRErrComGrundfos5 | DIGITAL | IOD_STR_TCP | 00629
STRErrComGrundfos6 | DIGITAL | IOD_STR_TCP | 00630
STRErrComGrundfos7 | DIGITAL | IOD_STR_TCP | 00631
STRErrComGrundfos8 | DIGITAL | IOD_STR_TCP | 00632
STRErrComGrundfos9 | DIGITAL | IOD_STR_TCP | 00633
STRErrComHladStroj | DIGITAL | IOD_STR_TCP | 00634
STRErrComKlima1 | DIGITAL | IOD_STR_TCP | 00635
STRErrComKlima2 | DIGITAL | IOD_STR_TCP | 00636
STRErrCommScada | DIGITAL | IOD_STR_TCP | 00637
STRErrCommXC100 | DIGITAL | IOD_STR_TCP | 00638
STRErrComPanelPLC | DIGITAL | IOD_STR_TCP | 00639
STRErrComPort2 | DIGITAL | IOD_STR_TCP | 00640
STRErrComPort3 | DIGITAL | IOD_STR_TCP | 00641
STRErrComPort4 | DIGITAL | IOD_STR_TCP | 00642
STRErrComToplPost | DIGITAL | IOD_STR_TCP | 00643
STRExp1TlakAlarm | DIGITAL | IOD_STR_TCP | 00644
STRExp1TlakMin | REAL | IOD_STR_TCP | 45859 | 0 | 10 | 0 | 10 | bar | ####.#
STRExp2TlakAlarm | DIGITAL | IOD_STR_TCP | 00645
STRExp2TlakMin | REAL | IOD_STR_TCP | 45861 | 0 | 16 | 0 | 16 | bar | ####.#
STRHladilniStrojOnOff | DIGITAL | IOD_STR_TCP | 00646
STRHladStrojFazeAlarm | DIGITAL | IOD_STR_TCP | 00647
STRHladStrojKompresorOljeAlarm | DIGITAL | IOD_STR_TCP | 00648
STRHladStrojKompresorOljeAlarmB | INT | IOD_STR_TCP | 40653
STRHladStrojLANcarelAlarm | DIGITAL | IOD_STR_TCP | 00649
STRHladStrojNapaka | DIGITAL | IOD_STR_TCP | 00650
STRHladStrojNizekPritiskAlarm | DIGITAL | IOD_STR_TCP | 00651
STRHladStrojNizekPritiskAlarmB | INT | IOD_STR_TCP | 40654
STRHladStrojObratovalneUre | REAL | IOD_STR_TCP | 45863 |  |  |  |  | h | ####
STRHladStrojObratovalneUreOpozorilo | DIGITAL | IOD_STR_TCP | 00652
STRHladStrojObratovalneUreOpozoriloB | INT | IOD_STR_TCP | 40655
STRHladStrojOffByAlarms | DIGITAL | IOD_STR_TCP | 00653
STRHladStrojPretokAlarm | DIGITAL | IOD_STR_TCP | 00654
STRHladStrojPritiskSonda1 | REAL | IOD_STR_TCP | 45865 | 0 | 5 | 0 | 5 | bar | ####.#
STRHladStrojPritiskSonda2 | REAL | IOD_STR_TCP | 45867 | 0 | 5 | 0 | 5 | bar | ####.#
STRHladStrojPritiskSonda3 | REAL | IOD_STR_TCP | 45869 | 0 | 5 | 0 | 5 | bar | ####.#
STRHladStrojPritiskSonda4 | REAL | IOD_STR_TCP | 45871 | 0 | 5 | 0 | 5 | bar | ####.#
STRHladStrojRemoteOn | DIGITAL | IOD_STR_TCP | 00655
STRHladStrojSenzorAlarm | DIGITAL | IOD_STR_TCP | 00656
STRHladStrojSummerOperation | DIGITAL | IOD_STR_TCP | 00657
STRHladStrojTemperaturaAlarm | DIGITAL | IOD_STR_TCP | 00658
STRHladStrojTemperaturaAlarmB | INT | IOD_STR_TCP | 40656
STRHladStrojTempH2OvhodIzparilnika | REAL | IOD_STR_TCP | 45873 | 0 | 150 | 0 | 150 | °C | ####.#
STRHladStrojTempIzhodnaSonda1 | REAL | IOD_STR_TCP | 45875 | 0 | 150 | 0 | 150 | °C | ####.#
STRHladStrojTempIzhodnaSonda3 | REAL | IOD_STR_TCP | 45877 | 0 | 150 | 0 | 150 | °C | ####.#
STRHladStrojTempSetPoint | REAL | IOD_STR_TCP | 45879 | 0 | 60 | 0 | 60 | °C | ####.#
STRHladStrojUnitOn | DIGITAL | IOD_STR_TCP | 00659
STRHladStrojUnitStatus | INT | IOD_STR_TCP | 40657
STRHladStrojUraAlarm | DIGITAL | IOD_STR_TCP | 00660
STRHladStrojVisokPritiskAlarm | DIGITAL | IOD_STR_TCP | 00661
STRHladStrojVisokPritiskAlarmB | INT | IOD_STR_TCP | 40658
STRHladStrojVisokPritiskOpozorilo | DIGITAL | IOD_STR_TCP | 00662
STRHladStrojVisokPritiskOpozoriloB | INT | IOD_STR_TCP | 40659
STRHladStrojZmrzalniAlarm | DIGITAL | IOD_STR_TCP | 00663
STRHladStrojZmrzalniAlarmB | INT | IOD_STR_TCP | 40660
STRHladStrojErrors10 | DIGITAL | IOD_STR_TCP | 00664
STRHladStrojErrors11 | DIGITAL | IOD_STR_TCP | 00665
STRHladStrojErrors12 | DIGITAL | IOD_STR_TCP | 00666
STRHladStrojErrors13 | DIGITAL | IOD_STR_TCP | 00667
STRHladStrojErrors14 | DIGITAL | IOD_STR_TCP | 00668
STRHladStrojErrors15 | DIGITAL | IOD_STR_TCP | 00669
STRHladStrojErrors16 | DIGITAL | IOD_STR_TCP | 00670
STRHladStrojErrors1 | DIGITAL | IOD_STR_TCP | 00671
STRHladStrojErrors2 | DIGITAL | IOD_STR_TCP | 00672
STRHladStrojErrors3 | DIGITAL | IOD_STR_TCP | 00673
STRHladStrojErrors4 | DIGITAL | IOD_STR_TCP | 00674
STRHladStrojErrors5 | DIGITAL | IOD_STR_TCP | 00675
STRHladStrojErrors6 | DIGITAL | IOD_STR_TCP | 00676
STRHladStrojErrors7 | DIGITAL | IOD_STR_TCP | 00677
STRHladStrojErrors8 | DIGITAL | IOD_STR_TCP | 00678
STRHladStrojErrors9 | DIGITAL | IOD_STR_TCP | 00679
STRKlima1errors10 | DIGITAL | IOD_STR_TCP | 00680
STRKlima1errors11 | DIGITAL | IOD_STR_TCP | 00681
STRKlima1errors12 | DIGITAL | IOD_STR_TCP | 00682
STRKlima1errors1 | DIGITAL | IOD_STR_TCP | 00683
STRKlima1errors2 | DIGITAL | IOD_STR_TCP | 00684
STRKlima1errors3 | DIGITAL | IOD_STR_TCP | 00685
STRKlima1errors4 | DIGITAL | IOD_STR_TCP | 00686
STRKlima1errors5 | DIGITAL | IOD_STR_TCP | 00687
STRKlima1errors6 | DIGITAL | IOD_STR_TCP | 00688
STRKlima1errors7 | DIGITAL | IOD_STR_TCP | 00689
STRKlima1errors8 | DIGITAL | IOD_STR_TCP | 00690
STRKlima1errors9 | DIGITAL | IOD_STR_TCP | 00691
STRKlima2errors10 | DIGITAL | IOD_STR_TCP | 00692
STRKlima2errors11 | DIGITAL | IOD_STR_TCP | 00693
STRKlima2errors12 | DIGITAL | IOD_STR_TCP | 00694
STRKlima2errors1 | DIGITAL | IOD_STR_TCP | 00695
STRKlima2errors2 | DIGITAL | IOD_STR_TCP | 00696
STRKlima2errors3 | DIGITAL | IOD_STR_TCP | 00697
STRKlima2errors4 | DIGITAL | IOD_STR_TCP | 00698
STRKlima2errors5 | DIGITAL | IOD_STR_TCP | 00699
STRKlima2errors6 | DIGITAL | IOD_STR_TCP | 00700
STRKlima2errors7 | DIGITAL | IOD_STR_TCP | 00701
STRKlima2errors8 | DIGITAL | IOD_STR_TCP | 00702
STRKlima2errors9 | DIGITAL | IOD_STR_TCP | 00703
STRKlima1CrpalkaGrelnika | DIGITAL | IOD_STR_TCP | 00704
STRKlima1CrpalkaStatus | INT | IOD_STR_TCP | 40661
STRKlima1DelovanjeVentH1 | DIGITAL | IOD_STR_TCP | 00705
STRKlima1DelovanjeVentH2 | DIGITAL | IOD_STR_TCP | 00706
STRKlima1Deluje | DIGITAL | IOD_STR_TCP | 00707
STRKlima1FilterError | DIGITAL | IOD_STR_TCP | 00708
STRKlima1HitrostVentilatorjev | REAL | IOD_STR_TCP | 45881 | 0 | 5000 | 0 | 5000 | obt/min | ####.#
STRKlima1HitrostVentStatus | INT | IOD_STR_TCP | 40662
STRKlima1IzhodniVentStatus | INT | IOD_STR_TCP | 40663
STRKlima1Napaka | DIGITAL | IOD_STR_TCP | 00709
STRKlima1NapakaPriPretokuZraka | DIGITAL | IOD_STR_TCP | 00710
STRKlima1NastTempProstora | REAL | IOD_STR_TCP | 45883 | 0 | 60 | 0 | 60 | °C | ####.#
STRKlima1ObratovalneUre | REAL | IOD_STR_TCP | 45885 |  |  |  |  | h | ####
STRKlima1OkvaraRototerma | DIGITAL | IOD_STR_TCP | 00711
STRKlima1OkvaraVlazilne | DIGITAL | IOD_STR_TCP | 00712
STRKlima1PozarError | DIGITAL | IOD_STR_TCP | 00713
STRKlima1PozarniAlarm | DIGITAL | IOD_STR_TCP | 00714
STRKlima1PreobremenitevMotCrpGr | DIGITAL | IOD_STR_TCP | 00715
STRKlima1PreobremenitevMotVent | DIGITAL | IOD_STR_TCP | 00716
STRKlima1ProtizmrzAktivna | DIGITAL | IOD_STR_TCP | 00717
STRKlima1ProtizmrzZasc | REAL | IOD_STR_TCP | 45887 | -30 | 60 | -30 | 60 | °C | ####.#
STRKlima1RezimDelovanja | REAL | IOD_STR_TCP | 45889
STRKlima1SkupniAlarmA | DIGITAL | IOD_STR_TCP | 00718
STRKlima1SkupniAlarmB | DIGITAL | IOD_STR_TCP | 00719
STRKlima1TemperaturaDovoda | REAL | IOD_STR_TCP | 45891 | 0 | 60 | 0 | 60 | °C | ####.#
STRKlima1TemperaturaProstora | REAL | IOD_STR_TCP | 45893 | 0 | 60 | 0 | 60 | °C | ####.#
STRKlima1TempPredRekN2 | REAL | IOD_STR_TCP | 45895 | 0 | 60 | 0 | 60 | °C | ####.#
STRKlima1TempZaRekN2 | REAL | IOD_STR_TCP | 45897 | 0 | 60 | 0 | 60 | °C | ####.#
STRKlima1TlakDovKanal | REAL | IOD_STR_TCP | 45899 | 0 | 5 | 0 | 5 | bar | ####.#
STRKlima1TlakOdvodKanal | REAL | IOD_STR_TCP | 45901 | 0 | 5 | 0 | 5 | bar | ####.#
STRKlima1VklopRegulacije | DIGITAL | IOD_STR_TCP | 00720
STRKlima1VlagaDovoda | REAL | IOD_STR_TCP | 45903 | 0 | 100 | 0 | 100 | % | ####.#
STRKlima1VlagaVprostor | REAL | IOD_STR_TCP | 45905 | 0 | 100 | 0 | 100 | % | ####.#
STRKlima1ZamasenFilter | DIGITAL | IOD_STR_TCP | 00721
STRKlima1ZunanjaTemp | REAL | IOD_STR_TCP | 45907 | -30 | 60 | -30 | 60 | °C | ####.#
STRKlima2CrpalkaGrelnika | DIGITAL | IOD_STR_TCP | 00722
STRKlima2CrpalkaStatus | INT | IOD_STR_TCP | 40664
STRKlima2DelovanjeVentH1 | DIGITAL | IOD_STR_TCP | 00723
STRKlima2DelovanjeVentH2 | DIGITAL | IOD_STR_TCP | 00724
STRKlima2Deluje | DIGITAL | IOD_STR_TCP | 00725
STRKlima2FilterError | DIGITAL | IOD_STR_TCP | 00726
STRKlima2HitrostVentilatorjev | REAL | IOD_STR_TCP | 45909 | 0 | 5000 | 0 | 5000 | obt/min | ####.#
STRKlima2HitrostVentStatus | INT | IOD_STR_TCP | 40665
STRKlima2IzhodniVentStatus | INT | IOD_STR_TCP | 40666
STRKlima2Napaka | DIGITAL | IOD_STR_TCP | 00727
STRKlima2NapakaPriPretokuZraka | DIGITAL | IOD_STR_TCP | 00728
STRKlima2NastTempProstora | REAL | IOD_STR_TCP | 45911 | 0 | 60 | 0 | 60 | °C | ####.#
STRKlima2ObratovalneUre | REAL | IOD_STR_TCP | 45913 |  |  |  |  | h | ####
STRKlima2OkvaraRototerma | DIGITAL | IOD_STR_TCP | 00729
STRKlima2OkvaraVlazilne | DIGITAL | IOD_STR_TCP | 00730
STRKlima2PozarError | DIGITAL | IOD_STR_TCP | 00731
STRKlima2PozarniAlarm | DIGITAL | IOD_STR_TCP | 00732
STRKlima2PreobremenitevMotCrpGr | DIGITAL | IOD_STR_TCP | 00733
STRKlima2PreobremenitevMotVent | DIGITAL | IOD_STR_TCP | 00734
STRKlima2ProtizmrzAktivna | DIGITAL | IOD_STR_TCP | 00735
STRKlima2ProtizmrzZasc | REAL | IOD_STR_TCP | 45915 | -30 | 50 | -30 | 50 | °C | ####.#
STRKlima2RezimDelovanja | REAL | IOD_STR_TCP | 45917
STRKlima2SkupniAlarmA | DIGITAL | IOD_STR_TCP | 00736
STRKlima2SkupniAlarmB | DIGITAL | IOD_STR_TCP | 00737
STRKlima2TemperaturaDovoda | REAL | IOD_STR_TCP | 45919 | 0 | 60 | 0 | 60 | °C | ####.#
STRKlima2TemperaturaProstora | REAL | IOD_STR_TCP | 45921 | 0 | 60 | 0 | 60 | °C | ####.#
STRKlima2TempPredRekN2 | REAL | IOD_STR_TCP | 45923 | 0 | 60 | 0 | 60 | °C | ####.#
STRKlima2TempZaRekN2 | REAL | IOD_STR_TCP | 45925 | 0 | 60 | 0 | 60 | °C | ####.#
STRKlima2TlakDovKanal | REAL | IOD_STR_TCP | 45927 | 0 | 5 | 0 | 5 | bar | ####.#
STRKlima2TlakOdvodKanal | REAL | IOD_STR_TCP | 45929 | 0 | 5 | 0 | 5 | bar | ####.#
STRKlima2VklopRegulacije | DIGITAL | IOD_STR_TCP | 00738
STRKlima2VlagaDovoda | REAL | IOD_STR_TCP | 45931 | 0 | 100 | 0 | 100 | % | ####.#
STRKlima2VlagaVprostor | REAL | IOD_STR_TCP | 45933 | 0 | 100 | 0 | 100 | % | ####.#
STRKlima2ZamasenFilter | DIGITAL | IOD_STR_TCP | 00739
STRKlima2ZunanjaTemp | REAL | IOD_STR_TCP | 45935 | -30 | 60 | -30 | 60 | °C | ####.#
STRKondEnotaOnOff1 | DIGITAL | IOD_STR_TCP | 00740
STRKondEnotaOnOff2 | DIGITAL | IOD_STR_TCP | 00741
STRKondEnotaOnOff3 | DIGITAL | IOD_STR_TCP | 00742
STRKontRezervaOnOff1 | DIGITAL | IOD_STR_TCP | 00743
STRKontRezervaOnOff2 | DIGITAL | IOD_STR_TCP | 00744
STRKontRezervaOnOff3 | DIGITAL | IOD_STR_TCP | 00745
STRNapakaSenzorAI10 | DIGITAL | IOD_STR_TCP | 00746
STRNapakaSenzorAI11 | DIGITAL | IOD_STR_TCP | 00747
STRNapakaSenzorAI12 | DIGITAL | IOD_STR_TCP | 00748
STRNapakaSenzorAI13 | DIGITAL | IOD_STR_TCP | 00749
STRNapakaSenzorAI14 | DIGITAL | IOD_STR_TCP | 00750
STRNapakaSenzorAI15 | DIGITAL | IOD_STR_TCP | 00751
STRNapakaSenzorAI16 | DIGITAL | IOD_STR_TCP | 00752
STRNapakaSenzorAI17 | DIGITAL | IOD_STR_TCP | 00753
STRNapakaSenzorAI18 | DIGITAL | IOD_STR_TCP | 00754
STRNapakaSenzorAI19 | DIGITAL | IOD_STR_TCP | 00755
STRNapakaSenzorAI1 | DIGITAL | IOD_STR_TCP | 00756
STRNapakaSenzorAI20 | DIGITAL | IOD_STR_TCP | 00757
STRNapakaSenzorAI21 | DIGITAL | IOD_STR_TCP | 00758
STRNapakaSenzorAI22 | DIGITAL | IOD_STR_TCP | 00759
STRNapakaSenzorAI23 | DIGITAL | IOD_STR_TCP | 00760
STRNapakaSenzorAI24 | DIGITAL | IOD_STR_TCP | 00761
STRNapakaSenzorAI25 | DIGITAL | IOD_STR_TCP | 00762
STRNapakaSenzorAI26 | DIGITAL | IOD_STR_TCP | 00763
STRNapakaSenzorAI27 | DIGITAL | IOD_STR_TCP | 00764
STRNapakaSenzorAI28 | DIGITAL | IOD_STR_TCP | 00765
STRNapakaSenzorAI29 | DIGITAL | IOD_STR_TCP | 00766
STRNapakaSenzorAI2 | DIGITAL | IOD_STR_TCP | 00767
STRNapakaSenzorAI30 | DIGITAL | IOD_STR_TCP | 00768
STRNapakaSenzorAI31 | DIGITAL | IOD_STR_TCP | 00769
STRNapakaSenzorAI32 | DIGITAL | IOD_STR_TCP | 00770
STRNapakaSenzorAI33 | DIGITAL | IOD_STR_TCP | 00771
STRNapakaSenzorAI34 | DIGITAL | IOD_STR_TCP | 00772
STRNapakaSenzorAI35 | DIGITAL | IOD_STR_TCP | 00773
STRNapakaSenzorAI36 | DIGITAL | IOD_STR_TCP | 00774
STRNapakaSenzorAI37 | DIGITAL | IOD_STR_TCP | 00775
STRNapakaSenzorAI38 | DIGITAL | IOD_STR_TCP | 00776
STRNapakaSenzorAI39 | DIGITAL | IOD_STR_TCP | 00777
STRNapakaSenzorAI3 | DIGITAL | IOD_STR_TCP | 00778
STRNapakaSenzorAI40 | DIGITAL | IOD_STR_TCP | 00779
STRNapakaSenzorAI4 | DIGITAL | IOD_STR_TCP | 00780
STRNapakaSenzorAI5 | DIGITAL | IOD_STR_TCP | 00781
STRNapakaSenzorAI6 | DIGITAL | IOD_STR_TCP | 00782
STRNapakaSenzorAI7 | DIGITAL | IOD_STR_TCP | 00783
STRNapakaSenzorAI8 | DIGITAL | IOD_STR_TCP | 00784
STRNapakaSenzorAI9 | DIGITAL | IOD_STR_TCP | 00785
STRNapakaSenzorHIA1 | DIGITAL | IOD_STR_TCP | 00786
STRNapakaSenzorHIA2 | DIGITAL | IOD_STR_TCP | 00787
STRNapakaSenzorHIA3 | DIGITAL | IOD_STR_TCP | 00788
STRNapakaSenzorHIA4 | DIGITAL | IOD_STR_TCP | 00789
STRNapakaSenzorTIA1 | DIGITAL | IOD_STR_TCP | 00790
STRNapakaSenzorTIA2 | DIGITAL | IOD_STR_TCP | 00791
STRNapakaSenzorTIA3 | DIGITAL | IOD_STR_TCP | 00792
STRNapakaSenzorTIA4 | DIGITAL | IOD_STR_TCP | 00793
STRPozarnaLoputaOnOffError1 | DIGITAL | IOD_STR_TCP | 00794
STRPozarnaLoputaOnOffError2 | DIGITAL | IOD_STR_TCP | 00795
STRPozarnaLoputaOnOffError3 | DIGITAL | IOD_STR_TCP | 00796
STRPozarnaLoputaOnOffError4 | DIGITAL | IOD_STR_TCP | 00797
STRPozarnaLoputaOnOffError5 | DIGITAL | IOD_STR_TCP | 00798
STRPozarnaLoputaStatus1 | INT | IOD_STR_TCP | 40667
STRPozarnaLoputaStatus2 | INT | IOD_STR_TCP | 40668
STRPozarnaLoputaStatus3 | INT | IOD_STR_TCP | 40669
STRPozarnaLoputaStatus4 | INT | IOD_STR_TCP | 40670
STRPozarnaLoputaStatus5 | INT | IOD_STR_TCP | 40671
STRPozarnaLoputOnOff1 | DIGITAL | IOD_STR_TCP | 00799
STRPozarnaLoputOnOff2 | DIGITAL | IOD_STR_TCP | 00800
STRPozarnaLoputOnOff3 | DIGITAL | IOD_STR_TCP | 00801
STRPozarnaLoputOnOff4 | DIGITAL | IOD_STR_TCP | 00802
STRPozarnaLoputOnOff5 | DIGITAL | IOD_STR_TCP | 00803
STRPozarniAlarm | DIGITAL | IOD_STR_TCP | 00804
STRPrenosUrnika10 | DIGITAL | IOD_STR_TCP | 00805
STRPrenosUrnika11 | DIGITAL | IOD_STR_TCP | 00806
STRPrenosUrnika12 | DIGITAL | IOD_STR_TCP | 00807
STRPrenosUrnika13 | DIGITAL | IOD_STR_TCP | 00808
STRPrenosUrnika14 | DIGITAL | IOD_STR_TCP | 00809
STRPrenosUrnika15 | DIGITAL | IOD_STR_TCP | 00810
STRPrenosUrnika16 | DIGITAL | IOD_STR_TCP | 00811
STRPrenosUrnika17 | DIGITAL | IOD_STR_TCP | 00812
STRPrenosUrnika18 | DIGITAL | IOD_STR_TCP | 00813
STRPrenosUrnika19 | DIGITAL | IOD_STR_TCP | 00814
STRPrenosUrnika1 | DIGITAL | IOD_STR_TCP | 00815
STRPrenosUrnika20 | DIGITAL | IOD_STR_TCP | 00816
STRPrenosUrnika21 | DIGITAL | IOD_STR_TCP | 00817
STRPrenosUrnika22 | DIGITAL | IOD_STR_TCP | 00818
STRPrenosUrnika23 | DIGITAL | IOD_STR_TCP | 00819
STRPrenosUrnika24 | DIGITAL | IOD_STR_TCP | 00820
STRPrenosUrnika25 | DIGITAL | IOD_STR_TCP | 00821
STRPrenosUrnika2 | DIGITAL | IOD_STR_TCP | 00822
STRPrenosUrnika3 | DIGITAL | IOD_STR_TCP | 00823
STRPrenosUrnika4 | DIGITAL | IOD_STR_TCP | 00824
STRPrenosUrnika5 | DIGITAL | IOD_STR_TCP | 00825
STRPrenosUrnika6 | DIGITAL | IOD_STR_TCP | 00826
STRPrenosUrnika7 | DIGITAL | IOD_STR_TCP | 00827
STRPrenosUrnika8 | DIGITAL | IOD_STR_TCP | 00828
STRPrenosUrnika9 | DIGITAL | IOD_STR_TCP | 00829
STRRazsvetljavaOnOff10 | DIGITAL | IOD_STR_TCP | 00830
STRRazsvetljavaOnOff11 | DIGITAL | IOD_STR_TCP | 00831
STRRazsvetljavaOnOff12 | DIGITAL | IOD_STR_TCP | 00832
STRRazsvetljavaOnOff13 | DIGITAL | IOD_STR_TCP | 00833
STRRazsvetljavaOnOff14 | DIGITAL | IOD_STR_TCP | 00834
STRRazsvetljavaOnOff15 | DIGITAL | IOD_STR_TCP | 00835
STRRazsvetljavaOnOff16 | DIGITAL | IOD_STR_TCP | 00836
STRRazsvetljavaOnOff17 | DIGITAL | IOD_STR_TCP | 00837
STRRazsvetljavaOnOff18 | DIGITAL | IOD_STR_TCP | 00838
STRRazsvetljavaOnOff19 | DIGITAL | IOD_STR_TCP | 00839
STRRazsvetljavaOnOff1 | DIGITAL | IOD_STR_TCP | 00840
STRRazsvetljavaOnOff20 | DIGITAL | IOD_STR_TCP | 00841
STRRazsvetljavaOnOff21 | DIGITAL | IOD_STR_TCP | 00842
STRRazsvetljavaOnOff22 | DIGITAL | IOD_STR_TCP | 00843
STRRazsvetljavaOnOff23 | DIGITAL | IOD_STR_TCP | 00844
STRRazsvetljavaOnOff24 | DIGITAL | IOD_STR_TCP | 00845
STRRazsvetljavaOnOff25 | DIGITAL | IOD_STR_TCP | 00846
STRRazsvetljavaOnOff2 | DIGITAL | IOD_STR_TCP | 00847
STRRazsvetljavaOnOff3 | DIGITAL | IOD_STR_TCP | 00848
STRRazsvetljavaOnOff4 | DIGITAL | IOD_STR_TCP | 00849
STRRazsvetljavaOnOff5 | DIGITAL | IOD_STR_TCP | 00850
STRRazsvetljavaOnOff6 | DIGITAL | IOD_STR_TCP | 00851
STRRazsvetljavaOnOff7 | DIGITAL | IOD_STR_TCP | 00852
STRRazsvetljavaOnOff8 | DIGITAL | IOD_STR_TCP | 00853
STRRazsvetljavaOnOff9 | DIGITAL | IOD_STR_TCP | 00854
STRRazsvetljavaRocno | DIGITAL | IOD_STR_TCP | 00855
STRrVersion | REAL | IOD_STR_TCP | 45937
STRSenzorTempTIA1 | REAL | IOD_STR_TCP | 45939 | 0 | 60 | 0 | 60 | °C | ####.#
STRSenzorTempTIA2 | REAL | IOD_STR_TCP | 45941 | 0 | 60 | 0 | 60 | °C | ####.#
STRSenzorTempTIA3 | REAL | IOD_STR_TCP | 45943 | 0 | 60 | 0 | 60 | °C | ####.#
STRSenzorTempTIA4 | REAL | IOD_STR_TCP | 45945 | 0 | 60 | 0 | 60 | °C | ####.#
STRSenzorVlagaHIA1 | REAL | IOD_STR_TCP | 45947 | 0 | 100 | 0 | 100 | % | ####.#
STRSenzorVlagaHIA2 | REAL | IOD_STR_TCP | 45949 | 0 | 100 | 0 | 100 | % | ####.#
STRSenzorVlagaHIA3 | REAL | IOD_STR_TCP | 45951 | 0 | 100 | 0 | 100 | % | ####.#
STRSenzorVlagaHIA4 | REAL | IOD_STR_TCP | 45953 | 0 | 100 | 0 | 100 | % | ####.#
STRSetDateTime | DIGITAL | IOD_STR_TCP | 00856
STRSetDateTimeDemand | DIGITAL | IOD_STR_TCP | 00857
STRSetDateTimeError | DIGITAL | IOD_STR_TCP | 00858
STRSetDateTimeFinished | DIGITAL | IOD_STR_TCP | 00859
STRSetRemoteOnOff1 | DIGITAL | IOD_STR_TCP | 00860
STRSetRemoteOnOff2 | DIGITAL | IOD_STR_TCP | 00861
STRSlabaBaterijaPLC_A1 | DIGITAL | IOD_STR_TCP | 00862
STRSlabaBaterijaPLC_A100 | DIGITAL | IOD_STR_TCP | 00863
STRSO_BojlerTE1Vklop | DIGITAL | IOD_STR_TCP | 00864
STRSO_CrpHM1Vklop | DIGITAL | IOD_STR_TCP | 00865
STRSO_CrpHM2Vklop | DIGITAL | IOD_STR_TCP | 00866
STRSO_CrpHM3Vklop | DIGITAL | IOD_STR_TCP | 00867
STRSO_CrpHM4Vklop | DIGITAL | IOD_STR_TCP | 00868
STRSO_CrpMN1Vklop | DIGITAL | IOD_STR_TCP | 00869
STRSO_CrpTM11Vklop | DIGITAL | IOD_STR_TCP | 00870
STRSO_HladStrVklop | DIGITAL | IOD_STR_TCP | 00871
STRSO_KE1Vklop | DIGITAL | IOD_STR_TCP | 00872
STRSO_KE2Vklop | DIGITAL | IOD_STR_TCP | 00873
STRSO_KE3Vklop | DIGITAL | IOD_STR_TCP | 00874
STRSO_rezerva1_3 | DIGITAL | IOD_STR_TCP | 00875
STRSO_rezerva1_4 | DIGITAL | IOD_STR_TCP | 00876
STRSO_rezerva1_5 | DIGITAL | IOD_STR_TCP | 00877
STRSO_Vent1Vklop | DIGITAL | IOD_STR_TCP | 00878
STRSO_Vent2Vklop | DIGITAL | IOD_STR_TCP | 00879
STRSO_Vent3Vklop | DIGITAL | IOD_STR_TCP | 00880
STRSO_Vent4Vklop | DIGITAL | IOD_STR_TCP | 00881
STRSO_Vent5Vklop | DIGITAL | IOD_STR_TCP | 00882
STRSO_Vent6Vklop | DIGITAL | IOD_STR_TCP | 00883
STRStatusKondenzEnota0 | INT | IOD_STR_TCP | 40672
STRStatusKondenzEnota1 | INT | IOD_STR_TCP | 40673
STRStatusKondenzEnota2 | INT | IOD_STR_TCP | 40674
STRStatusKondenzEnota3 | INT | IOD_STR_TCP | 40675
STRStatusKontaktor10 | INT | IOD_STR_TCP | 40676
STRStatusKontaktor11 | INT | IOD_STR_TCP | 40677
STRStatusKontaktor12 | INT | IOD_STR_TCP | 40678
STRStatusKontaktor13 | INT | IOD_STR_TCP | 40679
STRStatusKontaktor14 | INT | IOD_STR_TCP | 40680
STRStatusKontaktor15 | INT | IOD_STR_TCP | 40681
STRStatusKontaktor16 | INT | IOD_STR_TCP | 40682
STRStatusKontaktor17 | INT | IOD_STR_TCP | 40683
STRStatusKontaktor18 | INT | IOD_STR_TCP | 40684
STRStatusKontaktor19 | INT | IOD_STR_TCP | 40685
STRStatusKontaktor1 | INT | IOD_STR_TCP | 40686
STRStatusKontaktor20 | INT | IOD_STR_TCP | 40687
STRStatusKontaktor21 | INT | IOD_STR_TCP | 40688
STRStatusKontaktor22 | INT | IOD_STR_TCP | 40689
STRStatusKontaktor23 | INT | IOD_STR_TCP | 40690
STRStatusKontaktor24 | INT | IOD_STR_TCP | 40691
STRStatusKontaktor25 | INT | IOD_STR_TCP | 40692
STRStatusKontaktor2 | INT | IOD_STR_TCP | 40693
STRStatusKontaktor3 | INT | IOD_STR_TCP | 40694
STRStatusKontaktor4 | INT | IOD_STR_TCP | 40695
STRStatusKontaktor5 | INT | IOD_STR_TCP | 40696
STRStatusKontaktor6 | INT | IOD_STR_TCP | 40697
STRStatusKontaktor7 | INT | IOD_STR_TCP | 40698
STRStatusKontaktor8 | INT | IOD_STR_TCP | 40699
STRStatusKontaktor9 | INT | IOD_STR_TCP | 40700
STRStatusPreklopke10 | INT | IOD_STR_TCP | 40701
STRStatusPreklopke11 | INT | IOD_STR_TCP | 40702
STRStatusPreklopke12 | INT | IOD_STR_TCP | 40703
STRStatusPreklopke13 | INT | IOD_STR_TCP | 40704
STRStatusPreklopke14 | INT | IOD_STR_TCP | 40705
STRStatusPreklopke15 | INT | IOD_STR_TCP | 40706
STRStatusPreklopke16 | INT | IOD_STR_TCP | 40707
STRStatusPreklopke17 | INT | IOD_STR_TCP | 40708
STRStatusPreklopke18 | INT | IOD_STR_TCP | 40709
STRStatusPreklopke19 | INT | IOD_STR_TCP | 40710
STRStatusPreklopke1 | INT | IOD_STR_TCP | 40711
STRStatusPreklopke20 | INT | IOD_STR_TCP | 40712
STRStatusPreklopke21 | INT | IOD_STR_TCP | 40713
STRStatusPreklopke22 | INT | IOD_STR_TCP | 40714
STRStatusPreklopke23 | INT | IOD_STR_TCP | 40715
STRStatusPreklopke24 | INT | IOD_STR_TCP | 40716
STRStatusPreklopke25 | INT | IOD_STR_TCP | 40717
STRStatusPreklopke2 | INT | IOD_STR_TCP | 40718
STRStatusPreklopke3 | INT | IOD_STR_TCP | 40719
STRStatusPreklopke4 | INT | IOD_STR_TCP | 40720
STRStatusPreklopke5 | INT | IOD_STR_TCP | 40721
STRStatusPreklopke6 | INT | IOD_STR_TCP | 40722
STRStatusPreklopke7 | INT | IOD_STR_TCP | 40723
STRStatusPreklopke8 | INT | IOD_STR_TCP | 40724
STRStatusPreklopke9 | INT | IOD_STR_TCP | 40725
STRTEgrelecNaTemp | DIGITAL | IOD_STR_TCP | 00884
STRTEgrelecTempMAX | REAL | IOD_STR_TCP | 45955 | 0 | 100 | 0 | 100 | °C | ####.#
STRTEgrelecTempMIN | REAL | IOD_STR_TCP | 45957 | 0 | 100 | 0 | 100 | °C | ####.#
STRTEgrelecTempVklop | DIGITAL | IOD_STR_TCP | 00885
STRTempAlarmPoint | REAL | IOD_STR_TCP | 45959 | 0 | 60 | 0 | 60 | °C | ####.#
STRTempTIApovprecna | REAL | IOD_STR_TCP | 45961 | 0 | 60 | 0 | 60 | °C | ####.#
STRTempTSprevisoka | DIGITAL | IOD_STR_TCP | 00886
STRToplPostHKcrpalkaON | DIGITAL | IOD_STR_TCP | 00887
STRToplPostHKcrpDnevniRezim | DIGITAL | IOD_STR_TCP | 00888
STRToplPostHKcrpNocniRezim | DIGITAL | IOD_STR_TCP | 00889
STRToplPostHKdotokNastTemp | REAL | IOD_STR_TCP | 45963 | 0 | 100 | 0 | 100 | °C | ####.#
STRToplPostHKdotokTemp | REAL | IOD_STR_TCP | 45965 | 0 | 100 | 0 | 100 | °C | ####.#
STRToplPostHKpovtatekTemp | REAL | IOD_STR_TCP | 45967 | 0 | 100 | 0 | 100 | °C | ####.#
STRToplPostHKpovtratekNastTemp | REAL | IOD_STR_TCP | 45969 | 0 | 100 | 0 | 100 | °C | ####.#
STRToplPostHKrocniRezim | DIGITAL | IOD_STR_TCP | 00890
STRToplPostHKzunanjaTemp | REAL | IOD_STR_TCP | 45971 | -30 | 60 | -30 | 60 | °C | ####.#
STRToplPostNapakaRegister | INT | IOD_STR_TCP | 40726
STRToplPostSkupnaNapaka | DIGITAL | IOD_STR_TCP | 00891
STRToplPostTVcrpalkaON | DIGITAL | IOD_STR_TCP | 00892
STRToplPostTVdotokNastTemp | REAL | IOD_STR_TCP | 45973 | 0 | 100 | 0 | 100 | °C | ####.#
STRToplPostTVdotokTemp | REAL | IOD_STR_TCP | 45975 | 0 | 100 | 0 | 100 | °C | ####.#
STRToplPostTVpovratekTemp | REAL | IOD_STR_TCP | 45977 | 0 | 100 | 0 | 100 | °C | ####.#
STRToplPostTVrezervoarTemp | REAL | IOD_STR_TCP | 45979 | 0 | 100 | 0 | 100 | °C | ####.#
STRToplPostTVrocniRezim | DIGITAL | IOD_STR_TCP | 00893
STRToplPostErrors0 | DIGITAL | IOD_STR_TCP | 00894
STRToplPostErrors10 | DIGITAL | IOD_STR_TCP | 00895
STRToplPostErrors11 | DIGITAL | IOD_STR_TCP | 00896
STRToplPostErrors12 | DIGITAL | IOD_STR_TCP | 00897
STRToplPostErrors13 | DIGITAL | IOD_STR_TCP | 00898
STRToplPostErrors14 | DIGITAL | IOD_STR_TCP | 00899
STRToplPostErrors15 | DIGITAL | IOD_STR_TCP | 00900
STRToplPostErrors16 | DIGITAL | IOD_STR_TCP | 00901
STRToplPostErrors17 | DIGITAL | IOD_STR_TCP | 00902
STRToplPostErrors1 | DIGITAL | IOD_STR_TCP | 00903
STRToplPostErrors2 | DIGITAL | IOD_STR_TCP | 00904
STRToplPostErrors3 | DIGITAL | IOD_STR_TCP | 00905
STRToplPostErrors4 | DIGITAL | IOD_STR_TCP | 00906
STRToplPostErrors5 | DIGITAL | IOD_STR_TCP | 00907
STRToplPostErrors6 | DIGITAL | IOD_STR_TCP | 00908
STRToplPostErrors7 | DIGITAL | IOD_STR_TCP | 00909
STRToplPostErrors8 | DIGITAL | IOD_STR_TCP | 00910
STRToplPostErrors9 | DIGITAL | IOD_STR_TCP | 00911
STRTYventilMax1 | REAL | IOD_STR_TCP | 45981 | 0 | 100 | 0 | 100 | % | ###
STRTYventilMax2 | REAL | IOD_STR_TCP | 45983 | 0 | 100 | 0 | 100 | % | ###
STRTYventilMax3 | REAL | IOD_STR_TCP | 45985 | 0 | 100 | 0 | 100 | % | ###
STRTYventilMax4 | REAL | IOD_STR_TCP | 45987 | 0 | 100 | 0 | 100 | % | ###
STRTYventilMin1 | REAL | IOD_STR_TCP | 45989 | 0 | 100 | 0 | 100 | % | ###
STRTYventilMin2 | REAL | IOD_STR_TCP | 45991 | 0 | 100 | 0 | 100 | % | ###
STRTYventilMin3 | REAL | IOD_STR_TCP | 45993 | 0 | 100 | 0 | 100 | % | ###
STRTYventilMin4 | REAL | IOD_STR_TCP | 45995 | 0 | 100 | 0 | 100 | % | ###
STRTYventilNaTemp1 | DIGITAL | IOD_STR_TCP | 00912
STRTYventilNaTemp2 | DIGITAL | IOD_STR_TCP | 00913
STRTYventilNaTemp3 | DIGITAL | IOD_STR_TCP | 00914
STRTYventilNaTemp4 | DIGITAL | IOD_STR_TCP | 00915
STRTYventilTempRazlika1 | REAL | IOD_STR_TCP | 45997 | 0 | 100 | 0 | 100 | °C | ####.#
STRTYventilTempRazlika2 | REAL | IOD_STR_TCP | 45999 | 0 | 100 | 0 | 100 | °C | ####.#
STRTYventilTempRazlika3 | REAL | IOD_STR_TCP | 46001 | 0 | 100 | 0 | 100 | °C | ####.#
STRTYventilTempRazlika4 | REAL | IOD_STR_TCP | 46003 | 0 | 100 | 0 | 100 | °C | ####.#
STRUrnik_SCtoXCpot | INT | IOD_STR_TCP | 40727
STRUrnik_SCtoXCzah | INT | IOD_STR_TCP | 40728
STRUrnik_XCtoSCpot | INT | IOD_STR_TCP | 40729
STRUrnik_XCtoSCzah | INT | IOD_STR_TCP | 40730
STRUrnikSCtoXCDan1Off1Mna | INT | IOD_STR_TCP | 40731
STRUrnikSCtoXCDan1Off1Ura | INT | IOD_STR_TCP | 40732
STRUrnikSCtoXCDan1Off2Mna | INT | IOD_STR_TCP | 40733
STRUrnikSCtoXCDan1Off2Ura | INT | IOD_STR_TCP | 40734
STRUrnikSCtoXCDan1Off3Mna | INT | IOD_STR_TCP | 40735
STRUrnikSCtoXCDan1Off3Ura | INT | IOD_STR_TCP | 40736
STRUrnikSCtoXCDan1On1Mna | INT | IOD_STR_TCP | 40737
STRUrnikSCtoXCDan1On1Ura | INT | IOD_STR_TCP | 40738
STRUrnikSCtoXCDan1On2Mna | INT | IOD_STR_TCP | 40739
STRUrnikSCtoXCDan1On2Ura | INT | IOD_STR_TCP | 40740
STRUrnikSCtoXCDan1On3Mna | INT | IOD_STR_TCP | 40741
STRUrnikSCtoXCDan1On3Ura | INT | IOD_STR_TCP | 40742
STRUrnikSCtoXCDan2Off1Mna | INT | IOD_STR_TCP | 40743
STRUrnikSCtoXCDan2Off1Ura | INT | IOD_STR_TCP | 40744
STRUrnikSCtoXCDan2Off2Mna | INT | IOD_STR_TCP | 40745
STRUrnikSCtoXCDan2Off2Ura | INT | IOD_STR_TCP | 40746
STRUrnikSCtoXCDan2Off3Mna | INT | IOD_STR_TCP | 40747
STRUrnikSCtoXCDan2Off3Ura | INT | IOD_STR_TCP | 40748
STRUrnikSCtoXCDan2On1Mna | INT | IOD_STR_TCP | 40749
STRUrnikSCtoXCDan2On1Ura | INT | IOD_STR_TCP | 40750
STRUrnikSCtoXCDan2On2Mna | INT | IOD_STR_TCP | 40751
STRUrnikSCtoXCDan2On2Ura | INT | IOD_STR_TCP | 40752
STRUrnikSCtoXCDan2On3Mna | INT | IOD_STR_TCP | 40753
STRUrnikSCtoXCDan2On3Ura | INT | IOD_STR_TCP | 40754
STRUrnikSCtoXCDan3Off1Mna | INT | IOD_STR_TCP | 40755
STRUrnikSCtoXCDan3Off1Ura | INT | IOD_STR_TCP | 40756
STRUrnikSCtoXCDan3Off2Mna | INT | IOD_STR_TCP | 40757
STRUrnikSCtoXCDan3Off2Ura | INT | IOD_STR_TCP | 40758
STRUrnikSCtoXCDan3Off3Mna | INT | IOD_STR_TCP | 40759
STRUrnikSCtoXCDan3Off3Ura | INT | IOD_STR_TCP | 40760
STRUrnikSCtoXCDan3On1Mna | INT | IOD_STR_TCP | 40761
STRUrnikSCtoXCDan3On1Ura | INT | IOD_STR_TCP | 40762
STRUrnikSCtoXCDan3On2Mna | INT | IOD_STR_TCP | 40763
STRUrnikSCtoXCDan3On2Ura | INT | IOD_STR_TCP | 40764
STRUrnikSCtoXCDan3On3Mna | INT | IOD_STR_TCP | 40765
STRUrnikSCtoXCDan3On3Ura | INT | IOD_STR_TCP | 40766
STRUrnikSCtoXCDan4Off1Mna | INT | IOD_STR_TCP | 40767
STRUrnikSCtoXCDan4Off1Ura | INT | IOD_STR_TCP | 40768
STRUrnikSCtoXCDan4Off2Mna | INT | IOD_STR_TCP | 40769
STRUrnikSCtoXCDan4Off2Ura | INT | IOD_STR_TCP | 40770
STRUrnikSCtoXCDan4Off3Mna | INT | IOD_STR_TCP | 40771
STRUrnikSCtoXCDan4Off3Ura | INT | IOD_STR_TCP | 40772
STRUrnikSCtoXCDan4On1Mna | INT | IOD_STR_TCP | 40773
STRUrnikSCtoXCDan4On1Ura | INT | IOD_STR_TCP | 40774
STRUrnikSCtoXCDan4On2Mna | INT | IOD_STR_TCP | 40775
STRUrnikSCtoXCDan4On2Ura | INT | IOD_STR_TCP | 40776
STRUrnikSCtoXCDan4On3Mna | INT | IOD_STR_TCP | 40777
STRUrnikSCtoXCDan4On3Ura | INT | IOD_STR_TCP | 40778
STRUrnikSCtoXCDan5Off1Mna | INT | IOD_STR_TCP | 40779
STRUrnikSCtoXCDan5Off1Ura | INT | IOD_STR_TCP | 40780
STRUrnikSCtoXCDan5Off2Mna | INT | IOD_STR_TCP | 40781
STRUrnikSCtoXCDan5Off2Ura | INT | IOD_STR_TCP | 40782
STRUrnikSCtoXCDan5Off3Mna | INT | IOD_STR_TCP | 40783
STRUrnikSCtoXCDan5Off3Ura | INT | IOD_STR_TCP | 40784
STRUrnikSCtoXCDan5On1Mna | INT | IOD_STR_TCP | 40785
STRUrnikSCtoXCDan5On1Ura | INT | IOD_STR_TCP | 40786
STRUrnikSCtoXCDan5On2Mna | INT | IOD_STR_TCP | 40787
STRUrnikSCtoXCDan5On2Ura | INT | IOD_STR_TCP | 40788
STRUrnikSCtoXCDan5On3Mna | INT | IOD_STR_TCP | 40789
STRUrnikSCtoXCDan5On3Ura | INT | IOD_STR_TCP | 40790
STRUrnikSCtoXCDan6Off1Mna | INT | IOD_STR_TCP | 40791
STRUrnikSCtoXCDan6Off1Ura | INT | IOD_STR_TCP | 40792
STRUrnikSCtoXCDan6Off2Mna | INT | IOD_STR_TCP | 40793
STRUrnikSCtoXCDan6Off2Ura | INT | IOD_STR_TCP | 40794
STRUrnikSCtoXCDan6Off3Mna | INT | IOD_STR_TCP | 40795
STRUrnikSCtoXCDan6Off3Ura | INT | IOD_STR_TCP | 40796
STRUrnikSCtoXCDan6On1Mna | INT | IOD_STR_TCP | 40797
STRUrnikSCtoXCDan6On1Ura | INT | IOD_STR_TCP | 40798
STRUrnikSCtoXCDan6On2Mna | INT | IOD_STR_TCP | 40799
STRUrnikSCtoXCDan6On2Ura | INT | IOD_STR_TCP | 40800
STRUrnikSCtoXCDan6On3Mna | INT | IOD_STR_TCP | 40801
STRUrnikSCtoXCDan6On3Ura | INT | IOD_STR_TCP | 40802
STRUrnikSCtoXCDan7Off1Mna | INT | IOD_STR_TCP | 40803
STRUrnikSCtoXCDan7Off1Ura | INT | IOD_STR_TCP | 40804
STRUrnikSCtoXCDan7Off2Mna | INT | IOD_STR_TCP | 40805
STRUrnikSCtoXCDan7Off2Ura | INT | IOD_STR_TCP | 40806
STRUrnikSCtoXCDan7Off3Mna | INT | IOD_STR_TCP | 40807
STRUrnikSCtoXCDan7Off3Ura | INT | IOD_STR_TCP | 40808
STRUrnikSCtoXCDan7On1Mna | INT | IOD_STR_TCP | 40809
STRUrnikSCtoXCDan7On1Ura | INT | IOD_STR_TCP | 40810
STRUrnikSCtoXCDan7On2Mna | INT | IOD_STR_TCP | 40811
STRUrnikSCtoXCDan7On2Ura | INT | IOD_STR_TCP | 40812
STRUrnikSCtoXCDan7On3Mna | INT | IOD_STR_TCP | 40813
STRUrnikSCtoXCDan7On3Ura | INT | IOD_STR_TCP | 40814
STRUrnikXCtoSCDan1Off1Mna | INT | IOD_STR_TCP | 40815
STRUrnikXCtoSCDan1Off1Ura | INT | IOD_STR_TCP | 40816
STRUrnikXCtoSCDan1Off2Mna | INT | IOD_STR_TCP | 40817
STRUrnikXCtoSCDan1Off2Ura | INT | IOD_STR_TCP | 40818
STRUrnikXCtoSCDan1Off3Mna | INT | IOD_STR_TCP | 40819
STRUrnikXCtoSCDan1Off3Ura | INT | IOD_STR_TCP | 40820
STRUrnikXCtoSCDan1On1Mna | INT | IOD_STR_TCP | 40821
STRUrnikXCtoSCDan1On1Ura | INT | IOD_STR_TCP | 40822
STRUrnikXCtoSCDan1On2Mna | INT | IOD_STR_TCP | 40823
STRUrnikXCtoSCDan1On2Ura | INT | IOD_STR_TCP | 40824
STRUrnikXCtoSCDan1On3Mna | INT | IOD_STR_TCP | 40825
STRUrnikXCtoSCDan1On3Ura | INT | IOD_STR_TCP | 40826
STRUrnikXCtoSCDan2Off1Mna | INT | IOD_STR_TCP | 40827
STRUrnikXCtoSCDan2Off1Ura | INT | IOD_STR_TCP | 40828
STRUrnikXCtoSCDan2Off2Mna | INT | IOD_STR_TCP | 40829
STRUrnikXCtoSCDan2Off2Ura | INT | IOD_STR_TCP | 40830
STRUrnikXCtoSCDan2Off3Mna | INT | IOD_STR_TCP | 40831
STRUrnikXCtoSCDan2Off3Ura | INT | IOD_STR_TCP | 40832
STRUrnikXCtoSCDan2On1Mna | INT | IOD_STR_TCP | 40833
STRUrnikXCtoSCDan2On1Ura | INT | IOD_STR_TCP | 40834
STRUrnikXCtoSCDan2On2Mna | INT | IOD_STR_TCP | 40835
STRUrnikXCtoSCDan2On2Ura | INT | IOD_STR_TCP | 40836
STRUrnikXCtoSCDan2On3Mna | INT | IOD_STR_TCP | 40837
STRUrnikXCtoSCDan2On3Ura | INT | IOD_STR_TCP | 40838
STRUrnikXCtoSCDan3Off1Mna | INT | IOD_STR_TCP | 40839
STRUrnikXCtoSCDan3Off1Ura | INT | IOD_STR_TCP | 40840
STRUrnikXCtoSCDan3Off2Mna | INT | IOD_STR_TCP | 40841
STRUrnikXCtoSCDan3Off2Ura | INT | IOD_STR_TCP | 40842
STRUrnikXCtoSCDan3Off3Mna | INT | IOD_STR_TCP | 40843
STRUrnikXCtoSCDan3Off3Ura | INT | IOD_STR_TCP | 40844
STRUrnikXCtoSCDan3On1Mna | INT | IOD_STR_TCP | 40845
STRUrnikXCtoSCDan3On1Ura | INT | IOD_STR_TCP | 40846
STRUrnikXCtoSCDan3On2Mna | INT | IOD_STR_TCP | 40847
STRUrnikXCtoSCDan3On2Ura | INT | IOD_STR_TCP | 40848
STRUrnikXCtoSCDan3On3Mna | INT | IOD_STR_TCP | 40849
STRUrnikXCtoSCDan3On3Ura | INT | IOD_STR_TCP | 40850
STRUrnikXCtoSCDan4Off1Mna | INT | IOD_STR_TCP | 40851
STRUrnikXCtoSCDan4Off1Ura | INT | IOD_STR_TCP | 40852
STRUrnikXCtoSCDan4Off2Mna | INT | IOD_STR_TCP | 40853
STRUrnikXCtoSCDan4Off2Ura | INT | IOD_STR_TCP | 40854
STRUrnikXCtoSCDan4Off3Mna | INT | IOD_STR_TCP | 40855
STRUrnikXCtoSCDan4Off3Ura | INT | IOD_STR_TCP | 40856
STRUrnikXCtoSCDan4On1Mna | INT | IOD_STR_TCP | 40857
STRUrnikXCtoSCDan4On1Ura | INT | IOD_STR_TCP | 40858
STRUrnikXCtoSCDan4On2Mna | INT | IOD_STR_TCP | 40859
STRUrnikXCtoSCDan4On2Ura | INT | IOD_STR_TCP | 40860
STRUrnikXCtoSCDan4On3Mna | INT | IOD_STR_TCP | 40861
STRUrnikXCtoSCDan4On3Ura | INT | IOD_STR_TCP | 40862
STRUrnikXCtoSCDan5Off1Mna | INT | IOD_STR_TCP | 40863
STRUrnikXCtoSCDan5Off1Ura | INT | IOD_STR_TCP | 40864
STRUrnikXCtoSCDan5Off2Mna | INT | IOD_STR_TCP | 40865
STRUrnikXCtoSCDan5Off2Ura | INT | IOD_STR_TCP | 40866
STRUrnikXCtoSCDan5Off3Mna | INT | IOD_STR_TCP | 40867
STRUrnikXCtoSCDan5Off3Ura | INT | IOD_STR_TCP | 40868
STRUrnikXCtoSCDan5On1Mna | INT | IOD_STR_TCP | 40869
STRUrnikXCtoSCDan5On1Ura | INT | IOD_STR_TCP | 40870
STRUrnikXCtoSCDan5On2Mna | INT | IOD_STR_TCP | 40871
STRUrnikXCtoSCDan5On2Ura | INT | IOD_STR_TCP | 40872
STRUrnikXCtoSCDan5On3Mna | INT | IOD_STR_TCP | 40873
STRUrnikXCtoSCDan5On3Ura | INT | IOD_STR_TCP | 40874
STRUrnikXCtoSCDan6Off1Mna | INT | IOD_STR_TCP | 40875
STRUrnikXCtoSCDan6Off1Ura | INT | IOD_STR_TCP | 40876
STRUrnikXCtoSCDan6Off2Mna | INT | IOD_STR_TCP | 40877
STRUrnikXCtoSCDan6Off2Ura | INT | IOD_STR_TCP | 40878
STRUrnikXCtoSCDan6Off3Mna | INT | IOD_STR_TCP | 40879
STRUrnikXCtoSCDan6Off3Ura | INT | IOD_STR_TCP | 40880
STRUrnikXCtoSCDan6On1Mna | INT | IOD_STR_TCP | 40881
STRUrnikXCtoSCDan6On1Ura | INT | IOD_STR_TCP | 40882
STRUrnikXCtoSCDan6On2Mna | INT | IOD_STR_TCP | 40883
STRUrnikXCtoSCDan6On2Ura | INT | IOD_STR_TCP | 40884
STRUrnikXCtoSCDan6On3Mna | INT | IOD_STR_TCP | 40885
STRUrnikXCtoSCDan6On3Ura | INT | IOD_STR_TCP | 40886
STRUrnikXCtoSCDan7Off1Mna | INT | IOD_STR_TCP | 40887
STRUrnikXCtoSCDan7Off1Ura | INT | IOD_STR_TCP | 40888
STRUrnikXCtoSCDan7Off2Mna | INT | IOD_STR_TCP | 40889
STRUrnikXCtoSCDan7Off2Ura | INT | IOD_STR_TCP | 40890
STRUrnikXCtoSCDan7Off3Mna | INT | IOD_STR_TCP | 40891
STRUrnikXCtoSCDan7Off3Ura | INT | IOD_STR_TCP | 40892
STRUrnikXCtoSCDan7On1Mna | INT | IOD_STR_TCP | 40893
STRUrnikXCtoSCDan7On1Ura | INT | IOD_STR_TCP | 40894
STRUrnikXCtoSCDan7On2Mna | INT | IOD_STR_TCP | 40895
STRUrnikXCtoSCDan7On2Ura | INT | IOD_STR_TCP | 40896
STRUrnikXCtoSCDan7On3Mna | INT | IOD_STR_TCP | 40897
STRUrnikXCtoSCDan7On3Ura | INT | IOD_STR_TCP | 40898
STRUserCurrentLevel | INT | IOD_STR_TCP | 40899
STRUserCurrentName | STRING | IOD_STR_TCP | 47001[15]
STRUserLoggedIn | DIGITAL | IOD_STR_TCP | 00916
STRValAI_Temp1B1 | REAL | IOD_STR_TCP | 46005 | -40 | 60 | -40 | 60 | °C | ####.#
STRValAI_Temp1B2 | REAL | IOD_STR_TCP | 46007 | 0 | 50 | 0 | 50 | °C | ####.#
STRValAI_Temp1B3 | REAL | IOD_STR_TCP | 46009 | 0 | 50 | 0 | 50 | °C | ####.#
STRValAI_Temp2B2 | REAL | IOD_STR_TCP | 46011 | 0 | 50 | 0 | 50 | °C | ####.#
STRValAI_Temp2B3 | REAL | IOD_STR_TCP | 46013 | 0 | 50 | 0 | 50 | °C | ####.#
STRValAI_TempHB2 | REAL | IOD_STR_TCP | 46015 | -10 | 110 | -10 | 110 | °C | ####.#
STRValAI_TempHB4 | REAL | IOD_STR_TCP | 46017 | -10 | 40 | -10 | 40 | °C | ####.#
STRValAI_TempHB9 | REAL | IOD_STR_TCP | 46019 | -10 | 110 | -10 | 110 | °C | ####.#
STRValAI_TempTB1 | REAL | IOD_STR_TCP | 46021 | -10 | 110 | -10 | 110 | °C | ####.#
STRValAI_TempTB10 | REAL | IOD_STR_TCP | 46023 | -40 | 50 | -40 | 50 | °C | ####.#
STRValAI_TempTB2 | REAL | IOD_STR_TCP | 46025 | -10 | 110 | -10 | 110 | °C | ####.#
STRValAI_TempTB3 | REAL | IOD_STR_TCP | 46027 | -10 | 110 | -10 | 110 | °C | ####.#
STRValAI_TempTB4 | REAL | IOD_STR_TCP | 46029 | -10 | 110 | -10 | 110 | °C | ####.#
STRValAI_TempTB8 | REAL | IOD_STR_TCP | 46031 | -10 | 110 | -10 | 110 | °C | ####.#
STRValAI_TlakExp1S1 | REAL | IOD_STR_TCP | 46033 | 0 | 10 | 0 | 10 | bar | ####.#
STRValAI_TlakExp1S2 | REAL | IOD_STR_TCP | 46035 | 0 | 10 | 0 | 10 | bar | ####.#
STRValAI_TlakExp2S1 | REAL | IOD_STR_TCP | 46037 | 0 | 16 | 0 | 16 | bar | ####.#
STRValAI_TlakExp2S2 | REAL | IOD_STR_TCP | 46039 | 0 | 16 | 0 | 16 | bar | ####.#
STRValAI_TlakHB15 | REAL | IOD_STR_TCP | 46041 | 0 | 16 | 0 | 16 | bar | ####.#
STRValAI_TlakHB16 | REAL | IOD_STR_TCP | 46043 | 0 | 6 | 0 | 6 | bar | ####.#
STRValAI_TlakHB17 | REAL | IOD_STR_TCP | 46045 | 0 | 6 | 0 | 6 | bar | ####.#
STRValAI_TlakHB3 | REAL | IOD_STR_TCP | 46047 | 0 | 6 | 0 | 6 | bar | ####.#
STRValAI_TlakTB11 | REAL | IOD_STR_TCP | 46049 | 0 | 6 | 0 | 6 | bar | ####.#
STRValAI_TlakTB12 | REAL | IOD_STR_TCP | 46051 | 0 | 6 | 0 | 6 | bar | ####.#
STRValAI_TlakTB13 | REAL | IOD_STR_TCP | 46053 | 0 | 6 | 0 | 6 | bar | ####.#
STRValAI_TlakTB14 | REAL | IOD_STR_TCP | 46055 | 0 | 6 | 0 | 6 | bar | ####.#
STRValAI_Vlaga1B4 | REAL | IOD_STR_TCP | 46057 | 0 | 100 | 0 | 100 | % | ####.#
STRValAI_Vlaga2B4 | REAL | IOD_STR_TCP | 46059 | 0 | 100 | 0 | 100 | % | ####.#
STRValAO_RegVentTY1 | REAL | IOD_STR_TCP | 46061 | 0 | 100 | 0 | 100 | % | ####
STRValAO_RegVentTY2 | REAL | IOD_STR_TCP | 46063 | 0 | 100 | 0 | 100 | % | ####
STRValAO_RegVentTY3 | REAL | IOD_STR_TCP | 46065 | 0 | 100 | 0 | 100 | % | ####
STRValAO_RegVentTY4 | REAL | IOD_STR_TCP | 46067 | 0 | 100 | 0 | 100 | % | ####
STRVentilatorOnOff1 | DIGITAL | IOD_STR_TCP | 00917
STRVentilatorOnOff2 | DIGITAL | IOD_STR_TCP | 00918
STRVentilatorOnOff3 | DIGITAL | IOD_STR_TCP | 00919
STRVentilatorOnOff4 | DIGITAL | IOD_STR_TCP | 00920
STRVentilatorOnOff5 | DIGITAL | IOD_STR_TCP | 00921
STRVentilatorOnOff6 | DIGITAL | IOD_STR_TCP | 00922
STRVklopSCFBNapaka10 | DIGITAL | IOD_STR_TCP | 00923
STRVklopSCFBNapaka11 | DIGITAL | IOD_STR_TCP | 00924
STRVklopSCFBNapaka12 | DIGITAL | IOD_STR_TCP | 00925
STRVklopSCFBNapaka13 | DIGITAL | IOD_STR_TCP | 00926
STRVklopSCFBNapaka14 | DIGITAL | IOD_STR_TCP | 00927
STRVklopSCFBNapaka15 | DIGITAL | IOD_STR_TCP | 00928
STRVklopSCFBNapaka16 | DIGITAL | IOD_STR_TCP | 00929
STRVklopSCFBNapaka17 | DIGITAL | IOD_STR_TCP | 00930
STRVklopSCFBNapaka18 | DIGITAL | IOD_STR_TCP | 00931
STRVklopSCFBNapaka19 | DIGITAL | IOD_STR_TCP | 00932
STRVklopSCFBNapaka1 | DIGITAL | IOD_STR_TCP | 00933
STRVklopSCFBNapaka20 | DIGITAL | IOD_STR_TCP | 00934
STRVklopSCFBNapaka21 | DIGITAL | IOD_STR_TCP | 00935
STRVklopSCFBNapaka22 | DIGITAL | IOD_STR_TCP | 00936
STRVklopSCFBNapaka23 | DIGITAL | IOD_STR_TCP | 00937
STRVklopSCFBNapaka24 | DIGITAL | IOD_STR_TCP | 00938
STRVklopSCFBNapaka25 | DIGITAL | IOD_STR_TCP | 00939
STRVklopSCFBNapaka2 | DIGITAL | IOD_STR_TCP | 00940
STRVklopSCFBNapaka3 | DIGITAL | IOD_STR_TCP | 00941
STRVklopSCFBNapaka4 | DIGITAL | IOD_STR_TCP | 00942
STRVklopSCFBNapaka5 | DIGITAL | IOD_STR_TCP | 00943
STRVklopSCFBNapaka6 | DIGITAL | IOD_STR_TCP | 00944
STRVklopSCFBNapaka7 | DIGITAL | IOD_STR_TCP | 00945
STRVklopSCFBNapaka8 | DIGITAL | IOD_STR_TCP | 00946
STRVklopSCFBNapaka9 | DIGITAL | IOD_STR_TCP | 00947
STRVlagaHIApovprecna | REAL | IOD_STR_TCP | 46069 | 0 | 100 | 0 | 100 | % | ####.#
STRXVH_AlarmOn | DIGITAL | IOD_STR_TCP | 00948
STRXVH_CrpalkaGrfsNum | LONG | IOD_STR_TCP | 44001
STRXVH_StUrnika | LONG | IOD_STR_TCP | 44003
STRXVH_IzklopVsehLuci | DIGITAL | IOD_STR_TCP | 00949
STRXVH_VklopVsehLuci | DIGITAL | IOD_STR_TCP | 00950
STRUserloggedIn_mem | DIGITAL | IOD_STR_disk | D500
STRSkupnaNapakaKomunikacije | DIGITAL | IOD_STR_disk | D333
STRUrnikiLetniCas | INT | IOD_STR_disk | I3099
STRUrnikZaPrenosTemp | INT | IOD_STR_disk | I3100
STRPrenosUrnikaGor | DIGITAL | IOD_STR_disk | D505
STRZapisiUrnikNaXC | DIGITAL | IOD_STR_disk | D506
STRUrnikCopy | DIGITAL | IOD_STR_disk | D507
STRUrnikPaste | DIGITAL | IOD_STR_disk | D508
STRPomikZaUroPlus | DIGITAL | IOD_STR_disk | D509
STRPomikZaUroMinus | DIGITAL | IOD_STR_disk | D510
STRPrenasanjeUrnikovAktivno | DIGITAL | IOD_STR_TCP | 00951
STRPrenasanjeUrnikovAktivno1 | DIGITAL | IOD_STR_TCP | 00952
STRCircutorCosFi_III | REAL | IOD_STR_TCP | 46071
STRCircutorDelovnaEnergija | REAL | IOD_STR_TCP | 46073
STRCircutorDelovnaMoc_III | REAL | IOD_STR_TCP | 46075
STRCircutorDelovnaMoc_L1 | REAL | IOD_STR_TCP | 46077
STRCircutorDelovnaMoc_L2 | REAL | IOD_STR_TCP | 46079
STRCircutorDelovnaMoc_L3 | REAL | IOD_STR_TCP | 46081
STRCircutorFrekvenca_L1 | REAL | IOD_STR_TCP | 46083
STRCircutorInduktivnaEnergija | REAL | IOD_STR_TCP | 46085
STRCircutorInduktivnaMoc_III | REAL | IOD_STR_TCP | 46087
STRCircutorJalovaMoc_L1 | REAL | IOD_STR_TCP | 46089
STRCircutorJalovaMoc_L2 | REAL | IOD_STR_TCP | 46091
STRCircutorJalovaMoc_L3 | REAL | IOD_STR_TCP | 46093
STRCircutorKapacitivnaEnergija | REAL | IOD_STR_TCP | 46095
STRCircutorKapacitivnaMoc_III | REAL | IOD_STR_TCP | 46097
STRCircutorMaximumDemand | REAL | IOD_STR_TCP | 46099
STRCircutorNapetost_L1_L2 | REAL | IOD_STR_TCP | 46101
STRCircutorNapetost_L1_N | REAL | IOD_STR_TCP | 46103
STRCircutorNapetost_L2_L3 | REAL | IOD_STR_TCP | 46105
STRCircutorNapetost_L2_N | REAL | IOD_STR_TCP | 46107
STRCircutorNapetost_L3_L1 | REAL | IOD_STR_TCP | 46109
STRCircutorNapetost_L3_N | REAL | IOD_STR_TCP | 46111
STRCircutorNavideznaMoc_III | REAL | IOD_STR_TCP | 46113
STRCircutorNicelniTok | REAL | IOD_STR_TCP | 46115
STRCircutorPowerFactor_III | REAL | IOD_STR_TCP | 46117
STRCircutorPowerFactor_L1 | REAL | IOD_STR_TCP | 46119
STRCircutorPowerFactor_L2 | REAL | IOD_STR_TCP | 46121
STRCircutorPowerFactor_L3 | REAL | IOD_STR_TCP | 46123
STRCircutorTHDI_L1 | REAL | IOD_STR_TCP | 46125
STRCircutorTHDI_L2 | REAL | IOD_STR_TCP | 46127
STRCircutorTHDI_L3 | REAL | IOD_STR_TCP | 46129
STRCircutorTHDV_L1 | REAL | IOD_STR_TCP | 46131
STRCircutorTHDV_L2 | REAL | IOD_STR_TCP | 46133
STRCircutorTHDV_L3 | REAL | IOD_STR_TCP | 46135
STRCircutorTok_L1 | REAL | IOD_STR_TCP | 46137
STRCircutorTok_L2 | REAL | IOD_STR_TCP | 46139
STRCircutorTok_L3 | REAL | IOD_STR_TCP | 46141
STRCircutorTokPovprecje_III | REAL | IOD_STR_TCP | 46143
STRCrpalkeGrfsGalAlarmActiveCode | INT | IOD_STR_TCP | 40900
STRCrpalkeGrfsGalAlarmAktiven | DIGITAL | IOD_STR_TCP | 00953
STRCrpalkeGrfsGalAlarmCodeLog1 | INT | IOD_STR_TCP | 40901
STRCrpalkeGrfsGalAlarmCodeLog2 | INT | IOD_STR_TCP | 40902
STRCrpalkeGrfsGalAlarmCodeLog3 | INT | IOD_STR_TCP | 40903
STRCrpalkeGrfsGalAlarmCodeLog4 | INT | IOD_STR_TCP | 40904
STRCrpalkeGrfsGalAlarmCodeLog5 | INT | IOD_STR_TCP | 40905
STRCrpalkeGrfsGalAlarmGroupXVH0 | INT | IOD_STR_TCP | 40906
STRCrpalkeGrfsGalAlarmGroupXVH10 | INT | IOD_STR_TCP | 40907
STRCrpalkeGrfsGalAlarmGroupXVH11 | INT | IOD_STR_TCP | 40908
STRCrpalkeGrfsGalAlarmGroupXVH12 | INT | IOD_STR_TCP | 40909
STRCrpalkeGrfsGalAlarmGroupXVH13 | INT | IOD_STR_TCP | 40910
STRCrpalkeGrfsGalAlarmGroupXVH14 | INT | IOD_STR_TCP | 40911
STRCrpalkeGrfsGalAlarmGroupXVH15 | INT | IOD_STR_TCP | 40912
STRCrpalkeGrfsGalAlarmGroupXVH16 | INT | IOD_STR_TCP | 40913
STRCrpalkeGrfsGalAlarmGroupXVH1 | INT | IOD_STR_TCP | 40914
STRCrpalkeGrfsGalAlarmGroupXVH2 | INT | IOD_STR_TCP | 40915
STRCrpalkeGrfsGalAlarmGroupXVH3 | INT | IOD_STR_TCP | 40916
STRCrpalkeGrfsGalAlarmGroupXVH4 | INT | IOD_STR_TCP | 40917
STRCrpalkeGrfsGalAlarmGroupXVH5 | INT | IOD_STR_TCP | 40918
STRCrpalkeGrfsGalAlarmGroupXVH6 | INT | IOD_STR_TCP | 40919
STRCrpalkeGrfsGalAlarmGroupXVH7 | INT | IOD_STR_TCP | 40920
STRCrpalkeGrfsGalAlarmGroupXVH8 | INT | IOD_STR_TCP | 40921
STRCrpalkeGrfsGalAlarmGroupXVH9 | INT | IOD_STR_TCP | 40922
STRCrpalkeGrfsGalAlarmQSD1 | INT | IOD_STR_TCP | 40923
STRCrpalkeGrfsGalAlarmQSD2 | INT | IOD_STR_TCP | 40924
STRCrpalkeGrfsGalAlarmStart1 | INT | IOD_STR_TCP | 40925
STRCrpalkeGrfsGalAlarmStart2 | INT | IOD_STR_TCP | 40926
STRCrpalkeGrfsGalAlarmStop1 | INT | IOD_STR_TCP | 40927
STRCrpalkeGrfsGalAlarmStop2 | INT | IOD_STR_TCP | 40928
STRCrpalkeGrfsGalAlarmStop3 | INT | IOD_STR_TCP | 40929
STRCrpalkeGrfsGalAlarmSurv1 | INT | IOD_STR_TCP | 40930
STRCrpalkeGrfsGalAlarmSurv2 | INT | IOD_STR_TCP | 40931
STRCrpalkeGrfsGalControlSource | INT | IOD_STR_TCP | 40932
STRCrpalkeGrfsGalDeluje | DIGITAL | IOD_STR_TCP | 00954
STRCrpalkeGrfsGalEnergijaPoraba | REAL | IOD_STR_TCP | 46145
STRCrpalkeGrfsGalExternInputSetup | INT | IOD_STR_TCP | 40933
STRCrpalkeGrfsGalExternInputsStatus | INT | IOD_STR_TCP | 40934
STRCrpalkeGrfsGalFrekPretvornikDCNapetost | REAL | IOD_STR_TCP | 46147
STRCrpalkeGrfsGalFrekPretvornikDCTok | REAL | IOD_STR_TCP | 46149
STRCrpalkeGrfsGalFreqMax | REAL | IOD_STR_TCP | 46151
STRCrpalkeGrfsGalFreqMin | REAL | IOD_STR_TCP | 46153
STRCrpalkeGrfsGalFreqUpper | REAL | IOD_STR_TCP | 46155
STRCrpalkeGrfsGalLocalMode | DIGITAL | IOD_STR_TCP | 00955
STRCrpalkeGrfsGalLocalSetupMode1 | INT | IOD_STR_TCP | 40935
STRCrpalkeGrfsGalMocMax | REAL | IOD_STR_TCP | 46157
STRCrpalkeGrfsGalMocTrenutna | REAL | IOD_STR_TCP | 46159
STRCrpalkeGrfsGalMotorHitrost | REAL | IOD_STR_TCP | 46161
STRCrpalkeGrfsGalMotorTok | REAL | IOD_STR_TCP | 46163
STRCrpalkeGrfsGalNapajanjeTok | REAL | IOD_STR_TCP | 46165
STRCrpalkeGrfsGalNastavitevLokalna | REAL | IOD_STR_TCP | 46167
STRCrpalkeGrfsGalNastavitevTrenutna | REAL | IOD_STR_TCP | 46169
STRCrpalkeGrfsGalPreklopkaMode | INT | IOD_STR_TCP | 40936
STRCrpalkeGrfsGalPretokMax | REAL | IOD_STR_TCP | 46171
STRCrpalkeGrfsGalPretokMin | REAL | IOD_STR_TCP | 46173
STRCrpalkeGrfsGalPretokTrenutni | REAL | IOD_STR_TCP | 46175
STRCrpalkeGrfsGalPritiskMax | REAL | IOD_STR_TCP | 46177
STRCrpalkeGrfsGalPritiskTrenutni | REAL | IOD_STR_TCP | 46179
STRCrpalkeGrfsGalReferencaMotorjaHzV | REAL | IOD_STR_TCP | 46181
STRCrpalkeGrfsGalReferencaRemote | REAL | IOD_STR_TCP | 46183
STRCrpalkeGrfsGalRelay1setup | INT | IOD_STR_TCP | 40937
STRCrpalkeGrfsGalRemoteON | DIGITAL | IOD_STR_TCP | 00956
STRCrpalkeGrfsGalRemoteSetupMode1 | INT | IOD_STR_TCP | 40938
STRCrpalkeGrfsGalReset2handkWhValues | DIGITAL | IOD_STR_TCP | 00957
STRCrpalkeGrfsGalResetAlarm | DIGITAL | IOD_STR_TCP | 00958
STRCrpalkeGrfsGalResetAlarmLog | DIGITAL | IOD_STR_TCP | 00959
STRCrpalkeGrfsGalResetDevice | DIGITAL | IOD_STR_TCP | 00960
STRCrpalkeGrfsGalSetAutomatic | DIGITAL | IOD_STR_TCP | 00961
STRCrpalkeGrfsGalSetConstFreqMode | DIGITAL | IOD_STR_TCP | 00962
STRCrpalkeGrfsGalSetConstPress | DIGITAL | IOD_STR_TCP | 00963
STRCrpalkeGrfsGalSetLocalMode | DIGITAL | IOD_STR_TCP | 00964
STRCrpalkeGrfsGalSetMaxRunMode | DIGITAL | IOD_STR_TCP | 00965
STRCrpalkeGrfsGalSetMinRunMode | DIGITAL | IOD_STR_TCP | 00966
STRCrpalkeGrfsGalSetPropPress | DIGITAL | IOD_STR_TCP | 00967
STRCrpalkeGrfsGalSetReference | DIGITAL | IOD_STR_TCP | 00968
STRCrpalkeGrfsGalSetRemoteMode | DIGITAL | IOD_STR_TCP | 00969
STRCrpalkeGrfsGalSetTwinModeAlt | DIGITAL | IOD_STR_TCP | 00970
STRCrpalkeGrfsGalSetTwinModeSpare | DIGITAL | IOD_STR_TCP | 00971
STRCrpalkeGrfsGalSetTwinModeSync | DIGITAL | IOD_STR_TCP | 00972
STRCrpalkeGrfsGalStart | DIGITAL | IOD_STR_TCP | 00973
STRCrpalkeGrfsGalStatusCrpalke | INT | IOD_STR_TCP | 40939
STRCrpalkeGrfsGalStatusMode1 | INT | IOD_STR_TCP | 40940
STRCrpalkeGrfsGalStatusMode1co | INT | IOD_STR_TCP | 40941
STRCrpalkeGrfsGalStatusMode1op | INT | IOD_STR_TCP | 40942
STRCrpalkeGrfsGalStatusMode2 | INT | IOD_STR_TCP | 40943
STRCrpalkeGrfsGalStatusMode3 | INT | IOD_STR_TCP | 40944
STRCrpalkeGrfsGalStevecUr2h | REAL | IOD_STR_TCP | 46185
STRCrpalkeGrfsGalStop | DIGITAL | IOD_STR_TCP | 00974
STRCrpalkeGrfsGalSystemFeedback | REAL | IOD_STR_TCP | 46187
STRCrpalkeGrfsGalSystemReference | REAL | IOD_STR_TCP | 46189
STRCrpalkeGrfsGalTemperaturaMotorja | REAL | IOD_STR_TCP | 46191
STRCrpalkeGrfsGalUreXC200 | REAL | IOD_STR_TCP | 46193
STRCrpGrfsPIDregKP | REAL | IOD_STR_TCP | 46195
STRCrpGrfsPIDregTN | INT | IOD_STR_TCP | 40945
STRDate_Time0 | STRING | IOD_STR_TCP | 47016[15]
STRDate_Time1 | STRING | IOD_STR_TCP | 47031[15]
STRDate_Time2 | STRING | IOD_STR_TCP | 47046[15]
STRDate_Time3 | STRING | IOD_STR_TCP | 47061[15]
STRDateTimeDanVtednu | INT | IOD_STR_TCP | 40946
STRDI_rezerva10_2 | DIGITAL | IOD_STR_TCP | 00975
STRDI_rezerva10_7 | DIGITAL | IOD_STR_TCP | 00976
STRDI_rezerva11_4 | DIGITAL | IOD_STR_TCP | 00977
STRDI_rezerva14_0 | DIGITAL | IOD_STR_TCP | 00978
STRDI_rezerva14_2 | DIGITAL | IOD_STR_TCP | 00979
STRDI_rezerva14_3 | DIGITAL | IOD_STR_TCP | 00980
STRDI_rezerva14_4 | DIGITAL | IOD_STR_TCP | 00981
STRDI_rezerva14_5 | DIGITAL | IOD_STR_TCP | 00982
STRDI_rezerva14_7 | DIGITAL | IOD_STR_TCP | 00983
STRDI_rezerva2_4 | DIGITAL | IOD_STR_TCP | 00984
STRDI_rezerva3_5 | DIGITAL | IOD_STR_TCP | 00985
STRDIN_AkumTopVodeAUTO | DIGITAL | IOD_STR_TCP | 00986
STRDIN_CrpHM1AUTO | DIGITAL | IOD_STR_TCP | 00987
STRDIN_CrpHM1kontON | DIGITAL | IOD_STR_TCP | 00988
STRDIN_CrpHM2AUTO | DIGITAL | IOD_STR_TCP | 00989
STRDIN_CrpHM2kontON | DIGITAL | IOD_STR_TCP | 00990
STRDIN_CrpHM3AUTO | DIGITAL | IOD_STR_TCP | 00991
STRDIN_CrpHM3kontON | DIGITAL | IOD_STR_TCP | 00992
STRDIN_CrpHM4AUTO | DIGITAL | IOD_STR_TCP | 00993
STRDIN_CrpHM4kontON | DIGITAL | IOD_STR_TCP | 00994
STRDIN_CrpHM5AUTO | DIGITAL | IOD_STR_TCP | 00995
STRDIN_CrpHM6AUTO | DIGITAL | IOD_STR_TCP | 00996
STRDIN_CrpHM7AUTO | DIGITAL | IOD_STR_TCP | 00997
STRDIN_CrpHM8AUTO | DIGITAL | IOD_STR_TCP | 00998
STRDIN_CrpMN1AUTO | DIGITAL | IOD_STR_TCP | 00999
STRDIN_CrpMN1kontON | DIGITAL | IOD_STR_TCP | 01000
STRDIN_CrpTM10AUTO | DIGITAL | IOD_STR_TCP | 01001
STRDIN_CrpTM11TM12AUTO | DIGITAL | IOD_STR_TCP | 01002
STRDIN_CrpTM11TM12kontON | DIGITAL | IOD_STR_TCP | 01003
STRDIN_CrpTM1AUTO | DIGITAL | IOD_STR_TCP | 01004
STRDIN_CrpTM2AUTO | DIGITAL | IOD_STR_TCP | 01005
STRDIN_CrpTM3AUTO | DIGITAL | IOD_STR_TCP | 01006
STRDIN_CrpTM4AUTO | DIGITAL | IOD_STR_TCP | 01007
STRDIN_CrpTM5AUTO | DIGITAL | IOD_STR_TCP | 01008
STRDIN_CrpTM6AUTO | DIGITAL | IOD_STR_TCP | 01009
STRDIN_CrpTM7AUTO | DIGITAL | IOD_STR_TCP | 01010
STRDIN_CrpTM8AUTO | DIGITAL | IOD_STR_TCP | 01011
STRDIN_CrpTM9AUTO | DIGITAL | IOD_STR_TCP | 01012
STRDIN_GlStikaloDieselON | DIGITAL | IOD_STR_TCP | 01013
STRDIN_GlStikaloMrezaON | DIGITAL | IOD_STR_TCP | 01014
STRDIN_GlStikaloUpsON | DIGITAL | IOD_STR_TCP | 01015
STRDIN_HladStAUTO | DIGITAL | IOD_STR_TCP | 01016
STRDIN_Kond1AUTO | DIGITAL | IOD_STR_TCP | 01017
STRDIN_Kond2AUTO | DIGITAL | IOD_STR_TCP | 01018
STRDIN_Kond3AUTO | DIGITAL | IOD_STR_TCP | 01019
STRDIN_Vent1Auto | DIGITAL | IOD_STR_TCP | 01020
STRDIN_Vent1kontON | DIGITAL | IOD_STR_TCP | 01021
STRDIN_Vent2Auto | DIGITAL | IOD_STR_TCP | 01022
STRDIN_Vent2kontON | DIGITAL | IOD_STR_TCP | 01023
STRDIN_Vent3Auto | DIGITAL | IOD_STR_TCP | 01024
STRDIN_Vent3kontON | DIGITAL | IOD_STR_TCP | 01025
STRDIN_Vent4Auto | DIGITAL | IOD_STR_TCP | 01026
STRDIN_Vent4kontON | DIGITAL | IOD_STR_TCP | 01027
STRDIN_Vent5Auto | DIGITAL | IOD_STR_TCP | 01028
STRDIN_Vent5kontON | DIGITAL | IOD_STR_TCP | 01029
STRDIN_Vent6Auto | DIGITAL | IOD_STR_TCP | 01030
STRDIN_Vent6kontON | DIGITAL | IOD_STR_TCP | 01031
STRDO_rezerva0_2 | DIGITAL | IOD_STR_TCP | 01032
STRDO_rezerva0_3 | DIGITAL | IOD_STR_TCP | 01033
STRDO_rezerva0_4 | DIGITAL | IOD_STR_TCP | 01034
STRDO_rezerva0_5 | DIGITAL | IOD_STR_TCP | 01035
STRDO_rezerva1_3 | DIGITAL | IOD_STR_TCP | 01036
STRDO_rezerva1_4 | DIGITAL | IOD_STR_TCP | 01037
STRDO_rezerva1_5 | DIGITAL | IOD_STR_TCP | 01038
STRDO_rezerva3_4 | DIGITAL | IOD_STR_TCP | 01039
STRDO_rezerva3_6 | DIGITAL | IOD_STR_TCP | 01040
STRDO_rezerva4_0 | DIGITAL | IOD_STR_TCP | 01041
STRLetniCasDatumi111 | INT | IOD_STR_TCP | 40947
STRLetniCasDatumi112 | INT | IOD_STR_TCP | 40948
STRLetniCasDatumi121 | INT | IOD_STR_TCP | 40949
STRLetniCasDatumi122 | INT | IOD_STR_TCP | 40950
STRLetniCasDatumi131 | INT | IOD_STR_TCP | 40951
STRLetniCasDatumi132 | INT | IOD_STR_TCP | 40952
STRLetniCasDatumi141 | INT | IOD_STR_TCP | 40953
STRLetniCasDatumi142 | INT | IOD_STR_TCP | 40954
STRLetniCasDatumi211 | INT | IOD_STR_TCP | 40955
STRLetniCasDatumi212 | INT | IOD_STR_TCP | 40956
STRLetniCasDatumi221 | INT | IOD_STR_TCP | 40957
STRLetniCasDatumi222 | INT | IOD_STR_TCP | 40958
STRLetniCasDatumi231 | INT | IOD_STR_TCP | 40959
STRLetniCasDatumi232 | INT | IOD_STR_TCP | 40960
STRLetniCasDatumi241 | INT | IOD_STR_TCP | 40961
STRLetniCasDatumi242 | INT | IOD_STR_TCP | 40962
STRPrenosUrnika26 | DIGITAL | IOD_STR_TCP | 01042
STRPrenosUrnika27 | DIGITAL | IOD_STR_TCP | 01043
STRPrenosUrnika28 | DIGITAL | IOD_STR_TCP | 01044
STRPrenosUrnika29 | DIGITAL | IOD_STR_TCP | 01045
STRPrenosUrnika30 | DIGITAL | IOD_STR_TCP | 01046
STRPrenosUrnika31 | DIGITAL | IOD_STR_TCP | 01047
STRPrenosUrnika32 | DIGITAL | IOD_STR_TCP | 01048
STRPrenosUrnika33 | DIGITAL | IOD_STR_TCP | 01049
STRPrenosUrnika34 | DIGITAL | IOD_STR_TCP | 01050
STRPrenosUrnika35 | DIGITAL | IOD_STR_TCP | 01051
STRPrenosUrnika36 | DIGITAL | IOD_STR_TCP | 01052
STRPrenosUrnika37 | DIGITAL | IOD_STR_TCP | 01053
STRPrenosUrnika38 | DIGITAL | IOD_STR_TCP | 01054
STRPrenosUrnika39 | DIGITAL | IOD_STR_TCP | 01055
STRPrenosUrnika40 | DIGITAL | IOD_STR_TCP | 01056
STRPrenosUrnika41 | DIGITAL | IOD_STR_TCP | 01057
STRPrenosUrnika42 | DIGITAL | IOD_STR_TCP | 01058
STRPrenosUrnika43 | DIGITAL | IOD_STR_TCP | 01059
STRPrenosUrnika44 | DIGITAL | IOD_STR_TCP | 01060
STRPrenosUrnika45 | DIGITAL | IOD_STR_TCP | 01061
STRPrenosUrnika46 | DIGITAL | IOD_STR_TCP | 01062
STRPrenosUrnika47 | DIGITAL | IOD_STR_TCP | 01063
STRPrenosUrnika48 | DIGITAL | IOD_STR_TCP | 01064
STRPrenosUrnika49 | DIGITAL | IOD_STR_TCP | 01065
STRPrenosUrnika50 | DIGITAL | IOD_STR_TCP | 01066
STRPrenosUrnika51 | DIGITAL | IOD_STR_TCP | 01067
STRPrenosUrnika52 | DIGITAL | IOD_STR_TCP | 01068
STRPrenosUrnika53 | DIGITAL | IOD_STR_TCP | 01069
STRPrenosUrnika54 | DIGITAL | IOD_STR_TCP | 01070
STRPrenosUrnika55 | DIGITAL | IOD_STR_TCP | 01071
STRPrenosUrnika56 | DIGITAL | IOD_STR_TCP | 01072
STRPrenosUrnika57 | DIGITAL | IOD_STR_TCP | 01073
STRPrenosUrnika58 | DIGITAL | IOD_STR_TCP | 01074
STRPrenosUrnika59 | DIGITAL | IOD_STR_TCP | 01075
STRPrenosUrnika60 | DIGITAL | IOD_STR_TCP | 01076
STRPrenosUrnika61 | DIGITAL | IOD_STR_TCP | 01077
STRPrenosUrnika62 | DIGITAL | IOD_STR_TCP | 01078
STRPrenosUrnika63 | DIGITAL | IOD_STR_TCP | 01079
STRPrenosUrnika64 | DIGITAL | IOD_STR_TCP | 01080
STRPrenosUrnika65 | DIGITAL | IOD_STR_TCP | 01081
STRPrenosUrnika66 | DIGITAL | IOD_STR_TCP | 01082
STRPrenosUrnika67 | DIGITAL | IOD_STR_TCP | 01083
STRPrenosUrnika68 | DIGITAL | IOD_STR_TCP | 01084
STRPrenosUrnika69 | DIGITAL | IOD_STR_TCP | 01085
STRPrenosUrnika70 | DIGITAL | IOD_STR_TCP | 01086
STRPrenosUrnika71 | DIGITAL | IOD_STR_TCP | 01087
STRPrenosUrnika72 | DIGITAL | IOD_STR_TCP | 01088
STRPrenosUrnika73 | DIGITAL | IOD_STR_TCP | 01089
STRPrenosUrnika74 | DIGITAL | IOD_STR_TCP | 01090
STRPrenosUrnika75 | DIGITAL | IOD_STR_TCP | 01091
STRPrenosUrnika76 | DIGITAL | IOD_STR_TCP | 01092
STRPrenosUrnika77 | DIGITAL | IOD_STR_TCP | 01093
STRPrenosUrnika78 | DIGITAL | IOD_STR_TCP | 01094
STRPrenosUrnika79 | DIGITAL | IOD_STR_TCP | 01095
STRPrenosUrnika80 | DIGITAL | IOD_STR_TCP | 01096
STRPrenosUrnika81 | DIGITAL | IOD_STR_TCP | 01097
STRPrenosUrnika82 | DIGITAL | IOD_STR_TCP | 01098
STRPrenosUrnika83 | DIGITAL | IOD_STR_TCP | 01099
STRPrenosUrnika84 | DIGITAL | IOD_STR_TCP | 01100
STRPrenosUrnika85 | DIGITAL | IOD_STR_TCP | 01101
STRPrenosUrnika86 | DIGITAL | IOD_STR_TCP | 01102
STRPrenosUrnika87 | DIGITAL | IOD_STR_TCP | 01103
STRPrenosUrnika88 | DIGITAL | IOD_STR_TCP | 01104
STRPrenosUrnika89 | DIGITAL | IOD_STR_TCP | 01105
STRPrenosUrnika90 | DIGITAL | IOD_STR_TCP | 01106
STRPrenosUrnika91 | DIGITAL | IOD_STR_TCP | 01107
STRPrenosUrnika92 | DIGITAL | IOD_STR_TCP | 01108
STRPrenosUrnika93 | DIGITAL | IOD_STR_TCP | 01109
STRPrenosUrnika94 | DIGITAL | IOD_STR_TCP | 01110
STRPrenosUrnika95 | DIGITAL | IOD_STR_TCP | 01111
STRPrenosUrnika96 | DIGITAL | IOD_STR_TCP | 01112
STRRazsvRocnoEnaLuc10 | DIGITAL | IOD_STR_TCP | 01113
STRRazsvRocnoEnaLuc11 | DIGITAL | IOD_STR_TCP | 01114
STRRazsvRocnoEnaLuc12 | DIGITAL | IOD_STR_TCP | 01115
STRRazsvRocnoEnaLuc13 | DIGITAL | IOD_STR_TCP | 01116
STRRazsvRocnoEnaLuc14 | DIGITAL | IOD_STR_TCP | 01117
STRRazsvRocnoEnaLuc15 | DIGITAL | IOD_STR_TCP | 01118
STRRazsvRocnoEnaLuc16 | DIGITAL | IOD_STR_TCP | 01119
STRRazsvRocnoEnaLuc17 | DIGITAL | IOD_STR_TCP | 01120
STRRazsvRocnoEnaLuc18 | DIGITAL | IOD_STR_TCP | 01121
STRRazsvRocnoEnaLuc19 | DIGITAL | IOD_STR_TCP | 01122
STRRazsvRocnoEnaLuc1 | DIGITAL | IOD_STR_TCP | 01123
STRRazsvRocnoEnaLuc20 | DIGITAL | IOD_STR_TCP | 01124
STRRazsvRocnoEnaLuc21 | DIGITAL | IOD_STR_TCP | 01125
STRRazsvRocnoEnaLuc22 | DIGITAL | IOD_STR_TCP | 01126
STRRazsvRocnoEnaLuc23 | DIGITAL | IOD_STR_TCP | 01127
STRRazsvRocnoEnaLuc24 | DIGITAL | IOD_STR_TCP | 01128
STRRazsvRocnoEnaLuc25 | DIGITAL | IOD_STR_TCP | 01129
STRRazsvRocnoEnaLuc2 | DIGITAL | IOD_STR_TCP | 01130
STRRazsvRocnoEnaLuc3 | DIGITAL | IOD_STR_TCP | 01131
STRRazsvRocnoEnaLuc4 | DIGITAL | IOD_STR_TCP | 01132
STRRazsvRocnoEnaLuc5 | DIGITAL | IOD_STR_TCP | 01133
STRRazsvRocnoEnaLuc6 | DIGITAL | IOD_STR_TCP | 01134
STRRazsvRocnoEnaLuc7 | DIGITAL | IOD_STR_TCP | 01135
STRRazsvRocnoEnaLuc8 | DIGITAL | IOD_STR_TCP | 01136
STRRazsvRocnoEnaLuc9 | DIGITAL | IOD_STR_TCP | 01137
STRUrnikSaveDan1Off1Mna | INT | IOD_STR_TCP | 40963
STRUrnikSaveDan1Off1Ura | INT | IOD_STR_TCP | 40964
STRUrnikSaveDan1Off2Mna | INT | IOD_STR_TCP | 40965
STRUrnikSaveDan1Off2Ura | INT | IOD_STR_TCP | 40966
STRUrnikSaveDan1Off3Mna | INT | IOD_STR_TCP | 40967
STRUrnikSaveDan1Off3Ura | INT | IOD_STR_TCP | 40968
STRUrnikSaveDan1On1Mna | INT | IOD_STR_TCP | 40969
STRUrnikSaveDan1On1Ura | INT | IOD_STR_TCP | 40970
STRUrnikSaveDan1On2Mna | INT | IOD_STR_TCP | 40971
STRUrnikSaveDan1On2Ura | INT | IOD_STR_TCP | 40972
STRUrnikSaveDan1On3Mna | INT | IOD_STR_TCP | 40973
STRUrnikSaveDan1On3Ura | INT | IOD_STR_TCP | 40974
STRUrnikSaveDan2Off1Mna | INT | IOD_STR_TCP | 40975
STRUrnikSaveDan2Off1Ura | INT | IOD_STR_TCP | 40976
STRUrnikSaveDan2Off2Mna | INT | IOD_STR_TCP | 40977
STRUrnikSaveDan2Off2Ura | INT | IOD_STR_TCP | 40978
STRUrnikSaveDan2Off3Mna | INT | IOD_STR_TCP | 40979
STRUrnikSaveDan2Off3Ura | INT | IOD_STR_TCP | 40980
STRUrnikSaveDan2On1Mna | INT | IOD_STR_TCP | 40981
STRUrnikSaveDan2On1Ura | INT | IOD_STR_TCP | 40982
STRUrnikSaveDan2On2Mna | INT | IOD_STR_TCP | 40983
STRUrnikSaveDan2On2Ura | INT | IOD_STR_TCP | 40984
STRUrnikSaveDan2On3Mna | INT | IOD_STR_TCP | 40985
STRUrnikSaveDan2On3Ura | INT | IOD_STR_TCP | 40986
STRUrnikSaveDan3Off1Mna | INT | IOD_STR_TCP | 40987
STRUrnikSaveDan3Off1Ura | INT | IOD_STR_TCP | 40988
STRUrnikSaveDan3Off2Mna | INT | IOD_STR_TCP | 40989
STRUrnikSaveDan3Off2Ura | INT | IOD_STR_TCP | 40990
STRUrnikSaveDan3Off3Mna | INT | IOD_STR_TCP | 40991
STRUrnikSaveDan3Off3Ura | INT | IOD_STR_TCP | 40992
STRUrnikSaveDan3On1Mna | INT | IOD_STR_TCP | 40993
STRUrnikSaveDan3On1Ura | INT | IOD_STR_TCP | 40994
STRUrnikSaveDan3On2Mna | INT | IOD_STR_TCP | 40995
STRUrnikSaveDan3On2Ura | INT | IOD_STR_TCP | 40996
STRUrnikSaveDan3On3Mna | INT | IOD_STR_TCP | 40997
STRUrnikSaveDan3On3Ura | INT | IOD_STR_TCP | 40998
STRUrnikSaveDan4Off1Mna | INT | IOD_STR_TCP | 40999
STRUrnikSaveDan4Off1Ura | INT | IOD_STR_TCP | 41000
STRUrnikSaveDan4Off2Mna | INT | IOD_STR_TCP | 41001
STRUrnikSaveDan4Off2Ura | INT | IOD_STR_TCP | 41002
STRUrnikSaveDan4Off3Mna | INT | IOD_STR_TCP | 41003
STRUrnikSaveDan4Off3Ura | INT | IOD_STR_TCP | 41004
STRUrnikSaveDan4On1Mna | INT | IOD_STR_TCP | 41005
STRUrnikSaveDan4On1Ura | INT | IOD_STR_TCP | 41006
STRUrnikSaveDan4On2Mna | INT | IOD_STR_TCP | 41007
STRUrnikSaveDan4On2Ura | INT | IOD_STR_TCP | 41008
STRUrnikSaveDan4On3Mna | INT | IOD_STR_TCP | 41009
STRUrnikSaveDan4On3Ura | INT | IOD_STR_TCP | 41010
STRUrnikSaveDan5Off1Mna | INT | IOD_STR_TCP | 41011
STRUrnikSaveDan5Off1Ura | INT | IOD_STR_TCP | 41012
STRUrnikSaveDan5Off2Mna | INT | IOD_STR_TCP | 41013
STRUrnikSaveDan5Off2Ura | INT | IOD_STR_TCP | 41014
STRUrnikSaveDan5Off3Mna | INT | IOD_STR_TCP | 41015
STRUrnikSaveDan5Off3Ura | INT | IOD_STR_TCP | 41016
STRUrnikSaveDan5On1Mna | INT | IOD_STR_TCP | 41017
STRUrnikSaveDan5On1Ura | INT | IOD_STR_TCP | 41018
STRUrnikSaveDan5On2Mna | INT | IOD_STR_TCP | 41019
STRUrnikSaveDan5On2Ura | INT | IOD_STR_TCP | 41020
STRUrnikSaveDan5On3Mna | INT | IOD_STR_TCP | 41021
STRUrnikSaveDan5On3Ura | INT | IOD_STR_TCP | 41022
STRUrnikSaveDan6Off1Mna | INT | IOD_STR_TCP | 41023
STRUrnikSaveDan6Off1Ura | INT | IOD_STR_TCP | 41024
STRUrnikSaveDan6Off2Mna | INT | IOD_STR_TCP | 41025
STRUrnikSaveDan6Off2Ura | INT | IOD_STR_TCP | 41026
STRUrnikSaveDan6Off3Mna | INT | IOD_STR_TCP | 41027
STRUrnikSaveDan6Off3Ura | INT | IOD_STR_TCP | 41028
STRUrnikSaveDan6On1Mna | INT | IOD_STR_TCP | 41029
STRUrnikSaveDan6On1Ura | INT | IOD_STR_TCP | 41030
STRUrnikSaveDan6On2Mna | INT | IOD_STR_TCP | 41031
STRUrnikSaveDan6On2Ura | INT | IOD_STR_TCP | 41032
STRUrnikSaveDan6On3Mna | INT | IOD_STR_TCP | 41033
STRUrnikSaveDan6On3Ura | INT | IOD_STR_TCP | 41034
STRUrnikSaveDan7Off1Mna | INT | IOD_STR_TCP | 41035
STRUrnikSaveDan7Off1Ura | INT | IOD_STR_TCP | 41036
STRUrnikSaveDan7Off2Mna | INT | IOD_STR_TCP | 41037
STRUrnikSaveDan7Off2Ura | INT | IOD_STR_TCP | 41038
STRUrnikSaveDan7Off3Mna | INT | IOD_STR_TCP | 41039
STRUrnikSaveDan7Off3Ura | INT | IOD_STR_TCP | 41040
STRUrnikSaveDan7On1Mna | INT | IOD_STR_TCP | 41041
STRUrnikSaveDan7On1Ura | INT | IOD_STR_TCP | 41042
STRUrnikSaveDan7On2Mna | INT | IOD_STR_TCP | 41043
STRUrnikSaveDan7On2Ura | INT | IOD_STR_TCP | 41044
STRUrnikSaveDan7On3Mna | INT | IOD_STR_TCP | 41045
STRUrnikSaveDan7On3Ura | INT | IOD_STR_TCP | 41046
STRValAI_TempTB5 | REAL | IOD_STR_TCP | 46197
STRXVH_CircNumber | INT | IOD_STR_TCP | 41047
STRXVH_CrpalkaGrfsPair | DIGITAL | IOD_STR_TCP | 01138
STRXVH_CrpGrfsCommErr | DIGITAL | IOD_STR_TCP | 01139
STRXVH_CrpGrfsON10 | DIGITAL | IOD_STR_TCP | 01140
STRXVH_CrpGrfsON11 | DIGITAL | IOD_STR_TCP | 01141
STRXVH_CrpGrfsON12 | DIGITAL | IOD_STR_TCP | 01142
STRXVH_CrpGrfsON13 | DIGITAL | IOD_STR_TCP | 01143
STRXVH_CrpGrfsON14 | DIGITAL | IOD_STR_TCP | 01144
STRXVH_CrpGrfsON1 | DIGITAL | IOD_STR_TCP | 01145
STRXVH_CrpGrfsON2 | DIGITAL | IOD_STR_TCP | 01146
STRXVH_CrpGrfsON3 | DIGITAL | IOD_STR_TCP | 01147
STRXVH_CrpGrfsON4 | DIGITAL | IOD_STR_TCP | 01148
STRXVH_CrpGrfsON5 | DIGITAL | IOD_STR_TCP | 01149
STRXVH_CrpGrfsON6 | DIGITAL | IOD_STR_TCP | 01150
STRXVH_CrpGrfsON7 | DIGITAL | IOD_STR_TCP | 01151
STRXVH_CrpGrfsON8 | DIGITAL | IOD_STR_TCP | 01152
STRXVH_CrpGrfsON9 | DIGITAL | IOD_STR_TCP | 01153
STRXVH_CrpGrfsPIDreset | DIGITAL | IOD_STR_TCP | 01154
STRXVH_CrpGrfsVisibleData10 | DIGITAL | IOD_STR_TCP | 01155
STRXVH_CrpGrfsVisibleData11 | DIGITAL | IOD_STR_TCP | 01156
STRXVH_CrpGrfsVisibleData12 | DIGITAL | IOD_STR_TCP | 01157
STRXVH_CrpGrfsVisibleData13 | DIGITAL | IOD_STR_TCP | 01158
STRXVH_CrpGrfsVisibleData14 | DIGITAL | IOD_STR_TCP | 01159
STRXVH_CrpGrfsVisibleData15 | DIGITAL | IOD_STR_TCP | 01160
STRXVH_CrpGrfsVisibleData16 | DIGITAL | IOD_STR_TCP | 01161
STRXVH_CrpGrfsVisibleData1 | DIGITAL | IOD_STR_TCP | 01162
STRXVH_CrpGrfsVisibleData2 | DIGITAL | IOD_STR_TCP | 01163
STRXVH_CrpGrfsVisibleData3 | DIGITAL | IOD_STR_TCP | 01164
STRXVH_CrpGrfsVisibleData4 | DIGITAL | IOD_STR_TCP | 01165
STRXVH_CrpGrfsVisibleData5 | DIGITAL | IOD_STR_TCP | 01166
STRXVH_CrpGrfsVisibleData6 | DIGITAL | IOD_STR_TCP | 01167
STRXVH_CrpGrfsVisibleData7 | DIGITAL | IOD_STR_TCP | 01168
STRXVH_CrpGrfsVisibleData8 | DIGITAL | IOD_STR_TCP | 01169
STRXVH_CrpGrfsVisibleData9 | DIGITAL | IOD_STR_TCP | 01170
STRXVH_CrpGrundfosNaCas | DIGITAL | IOD_STR_TCP | 01171
STRXVH_CrpGrundfosNaTlak | DIGITAL | IOD_STR_TCP | 01172
STRXVH_CrpGrundfosON | DIGITAL | IOD_STR_TCP | 01173
STRXVH_CrpGrundfosResetAlarm | DIGITAL | IOD_STR_TCP | 01174
STRXVH_CrpGrundfosResetAlarmLog | DIGITAL | IOD_STR_TCP | 01175
STRXVH_CrpGrundfosSetRef | DIGITAL | IOD_STR_TCP | 01176
STRXVH_CrpGrundfosTlakSP | REAL | IOD_STR_TCP | 46199
STRXVH_GrafTemp1 | REAL | IOD_STR_TCP | 46201
STRXVH_GrafTemp2 | REAL | IOD_STR_TCP | 46203
STRXVH_GrafTemp3 | REAL | IOD_STR_TCP | 46205
STRXVH_GrafTemp4 | REAL | IOD_STR_TCP | 46207
STRXVH_GrafTemp5 | REAL | IOD_STR_TCP | 46209
STRXVH_GrafVlaga1 | REAL | IOD_STR_TCP | 46211
STRXVH_GrafVlaga2 | REAL | IOD_STR_TCP | 46213
STRXVH_GrafVlaga3 | REAL | IOD_STR_TCP | 46215
STRXVH_GrafVlaga4 | REAL | IOD_STR_TCP | 46217
STRXVH_GrafVlaga5 | REAL | IOD_STR_TCP | 46219
STRXVH_KompStatus1 | INT | IOD_STR_TCP | 41048
STRXVH_KompStatus2 | INT | IOD_STR_TCP | 41049
STRXVH_RazsvOnOff | DIGITAL | IOD_STR_TCP | 01177
STRXVH_ReferencaUpper | INT | IOD_STR_TCP | 41050
STRXVH_setCircNum1 | DIGITAL | IOD_STR_TCP | 01178
STRXVH_setCircNum2 | DIGITAL | IOD_STR_TCP | 01179
STRXVH_setCircNum3 | DIGITAL | IOD_STR_TCP | 01180
STRXVH_setCircNum4 | DIGITAL | IOD_STR_TCP | 01181
STRXVH_setCircNum5 | DIGITAL | IOD_STR_TCP | 01182
STRXVH_TlakSenzor | REAL | IOD_STR_TCP | 46221
STRXVH_UPSstatus | INT | IOD_STR_TCP | 41051
STRXVH_UrnikDan1Off1Mna | INT | IOD_STR_TCP | 41052
STRXVH_UrnikDan1Off1Ura | INT | IOD_STR_TCP | 41053
STRXVH_UrnikDan1Off2Mna | INT | IOD_STR_TCP | 41054
STRXVH_UrnikDan1Off2Ura | INT | IOD_STR_TCP | 41055
STRXVH_UrnikDan1Off3Mna | INT | IOD_STR_TCP | 41056
STRXVH_UrnikDan1Off3Ura | INT | IOD_STR_TCP | 41057
STRXVH_UrnikDan1On1Mna | INT | IOD_STR_TCP | 41058
STRXVH_UrnikDan1On1Ura | INT | IOD_STR_TCP | 41059
STRXVH_UrnikDan1On2Mna | INT | IOD_STR_TCP | 41060
STRXVH_UrnikDan1On2Ura | INT | IOD_STR_TCP | 41061
STRXVH_UrnikDan1On3Mna | INT | IOD_STR_TCP | 41062
STRXVH_UrnikDan1On3Ura | INT | IOD_STR_TCP | 41063
STRXVH_UrnikDan2Off1Mna | INT | IOD_STR_TCP | 41064
STRXVH_UrnikDan2Off1Ura | INT | IOD_STR_TCP | 41065
STRXVH_UrnikDan2Off2Mna | INT | IOD_STR_TCP | 41066
STRXVH_UrnikDan2Off2Ura | INT | IOD_STR_TCP | 41067
STRXVH_UrnikDan2Off3Mna | INT | IOD_STR_TCP | 41068
STRXVH_UrnikDan2Off3Ura | INT | IOD_STR_TCP | 41069
STRXVH_UrnikDan2On1Mna | INT | IOD_STR_TCP | 41070
STRXVH_UrnikDan2On1Ura | INT | IOD_STR_TCP | 41071
STRXVH_UrnikDan2On2Mna | INT | IOD_STR_TCP | 41072
STRXVH_UrnikDan2On2Ura | INT | IOD_STR_TCP | 41073
STRXVH_UrnikDan2On3Mna | INT | IOD_STR_TCP | 41074
STRXVH_UrnikDan2On3Ura | INT | IOD_STR_TCP | 41075
STRXVH_UrnikDan3Off1Mna | INT | IOD_STR_TCP | 41076
STRXVH_UrnikDan3Off1Ura | INT | IOD_STR_TCP | 41077
STRXVH_UrnikDan3Off2Mna | INT | IOD_STR_TCP | 41078
STRXVH_UrnikDan3Off2Ura | INT | IOD_STR_TCP | 41079
STRXVH_UrnikDan3Off3Mna | INT | IOD_STR_TCP | 41080
STRXVH_UrnikDan3Off3Ura | INT | IOD_STR_TCP | 41081
STRXVH_UrnikDan3On1Mna | INT | IOD_STR_TCP | 41082
STRXVH_UrnikDan3On1Ura | INT | IOD_STR_TCP | 41083
STRXVH_UrnikDan3On2Mna | INT | IOD_STR_TCP | 41084
STRXVH_UrnikDan3On2Ura | INT | IOD_STR_TCP | 41085
STRXVH_UrnikDan3On3Mna | INT | IOD_STR_TCP | 41086
STRXVH_UrnikDan3On3Ura | INT | IOD_STR_TCP | 41087
STRXVH_UrnikDan4Off1Mna | INT | IOD_STR_TCP | 41088
STRXVH_UrnikDan4Off1Ura | INT | IOD_STR_TCP | 41089
STRXVH_UrnikDan4Off2Mna | INT | IOD_STR_TCP | 41090
STRXVH_UrnikDan4Off2Ura | INT | IOD_STR_TCP | 41091
STRXVH_UrnikDan4Off3Mna | INT | IOD_STR_TCP | 41092
STRXVH_UrnikDan4Off3Ura | INT | IOD_STR_TCP | 41093
STRXVH_UrnikDan4On1Mna | INT | IOD_STR_TCP | 41094
STRXVH_UrnikDan4On1Ura | INT | IOD_STR_TCP | 41095
STRXVH_UrnikDan4On2Mna | INT | IOD_STR_TCP | 41096
STRXVH_UrnikDan4On2Ura | INT | IOD_STR_TCP | 41097
STRXVH_UrnikDan4On3Mna | INT | IOD_STR_TCP | 41098
STRXVH_UrnikDan4On3Ura | INT | IOD_STR_TCP | 41099
STRXVH_UrnikDan5Off1Mna | INT | IOD_STR_TCP | 41100
STRXVH_UrnikDan5Off1Ura | INT | IOD_STR_TCP | 41101
STRXVH_UrnikDan5Off2Mna | INT | IOD_STR_TCP | 41102
STRXVH_UrnikDan5Off2Ura | INT | IOD_STR_TCP | 41103
STRXVH_UrnikDan5Off3Mna | INT | IOD_STR_TCP | 41104
STRXVH_UrnikDan5Off3Ura | INT | IOD_STR_TCP | 41105
STRXVH_UrnikDan5On1Mna | INT | IOD_STR_TCP | 41106
STRXVH_UrnikDan5On1Ura | INT | IOD_STR_TCP | 41107
STRXVH_UrnikDan5On2Mna | INT | IOD_STR_TCP | 41108
STRXVH_UrnikDan5On2Ura | INT | IOD_STR_TCP | 41109
STRXVH_UrnikDan5On3Mna | INT | IOD_STR_TCP | 41110
STRXVH_UrnikDan5On3Ura | INT | IOD_STR_TCP | 41111
STRXVH_UrnikDan6Off1Mna | INT | IOD_STR_TCP | 41112
STRXVH_UrnikDan6Off1Ura | INT | IOD_STR_TCP | 41113
STRXVH_UrnikDan6Off2Mna | INT | IOD_STR_TCP | 41114
STRXVH_UrnikDan6Off2Ura | INT | IOD_STR_TCP | 41115
STRXVH_UrnikDan6Off3Mna | INT | IOD_STR_TCP | 41116
STRXVH_UrnikDan6Off3Ura | INT | IOD_STR_TCP | 41117
STRXVH_UrnikDan6On1Mna | INT | IOD_STR_TCP | 41118
STRXVH_UrnikDan6On1Ura | INT | IOD_STR_TCP | 41119
STRXVH_UrnikDan6On2Mna | INT | IOD_STR_TCP | 41120
STRXVH_UrnikDan6On2Ura | INT | IOD_STR_TCP | 41121
STRXVH_UrnikDan6On3Mna | INT | IOD_STR_TCP | 41122
STRXVH_UrnikDan6On3Ura | INT | IOD_STR_TCP | 41123
STRXVH_UrnikDan7Off1Mna | INT | IOD_STR_TCP | 41124
STRXVH_UrnikDan7Off1Ura | INT | IOD_STR_TCP | 41125
STRXVH_UrnikDan7Off2Mna | INT | IOD_STR_TCP | 41126
STRXVH_UrnikDan7Off2Ura | INT | IOD_STR_TCP | 41127
STRXVH_UrnikDan7Off3Mna | INT | IOD_STR_TCP | 41128
STRXVH_UrnikDan7Off3Ura | INT | IOD_STR_TCP | 41129
STRXVH_UrnikDan7On1Mna | INT | IOD_STR_TCP | 41130
STRXVH_UrnikDan7On1Ura | INT | IOD_STR_TCP | 41131
STRXVH_UrnikDan7On2Mna | INT | IOD_STR_TCP | 41132
STRXVH_UrnikDan7On2Ura | INT | IOD_STR_TCP | 41133
STRXVH_UrnikDan7On3Mna | INT | IOD_STR_TCP | 41134
STRXVH_UrnikDan7On3Ura | INT | IOD_STR_TCP | 41135
STRXVH_UrnikNalozi | DIGITAL | IOD_STR_TCP | 01183
STRXVH_UrnikNonStop | DIGITAL | IOD_STR_TCP | 01184
STRXVH_UrnikPotrdiVpis | DIGITAL | IOD_STR_TCP | 01185
STRXVH_UrnikPreklicVpisa | DIGITAL | IOD_STR_TCP | 01186
STRXVH_UrnikShrani | DIGITAL | IOD_STR_TCP | 01187
STRXVH_VentilTYValue11 | INT | IOD_STR_TCP | 41136
STRXVH_VentilTYValue12 | INT | IOD_STR_TCP | 41137
STRXVH_VentilTYValue21 | INT | IOD_STR_TCP | 41138
STRXVH_VentilTYValue22 | INT | IOD_STR_TCP | 41139
STRXVH_VentilTYValue31 | INT | IOD_STR_TCP | 41140
STRXVH_VentilTYValue32 | INT | IOD_STR_TCP | 41141
STRXVH_VentilTYValue41 | INT | IOD_STR_TCP | 41142
STRXVH_VentilTYValue42 | INT | IOD_STR_TCP | 41143
STRXVH_VlazilecStatus1 | INT | IOD_STR_TCP | 41144
STRXVH_VlazilecStatus2 | INT | IOD_STR_TCP | 41145
STRXVH_VpisUrnika | DIGITAL | IOD_STR_TCP | 01188
STRXVHnum10 | INT | IOD_STR_TCP | 41146
STRXVHnum11 | INT | IOD_STR_TCP | 41147
STRXVHnum12 | INT | IOD_STR_TCP | 41148
STRXVHnum13 | INT | IOD_STR_TCP | 41149
STRXVHnum14 | INT | IOD_STR_TCP | 41150
STRXVHnum1 | INT | IOD_STR_TCP | 41151
STRXVHnum2 | INT | IOD_STR_TCP | 41152
STRXVHnum3 | INT | IOD_STR_TCP | 41153
STRXVHnum4 | INT | IOD_STR_TCP | 41154
STRXVHnum5 | INT | IOD_STR_TCP | 41155
STRXVHnum6 | INT | IOD_STR_TCP | 41156
STRXVHnum7 | INT | IOD_STR_TCP | 41157
STRXVHnum8 | INT | IOD_STR_TCP | 41158
STRXVHnum9 | INT | IOD_STR_TCP | 41159
STRErrCommScada2 | DIGITAL | IOD_STR_TCP | 01189
STRComSCADA2 | DIGITAL | IOD_STR_TCP | 01190
STRErrCommScada_Omogoci2 | DIGITAL | IOD_STR_disk | D4202
STRServer_A_Izpad | DIGITAL | IOD_STR_disk | D4203
STRServer_B_Izpad | DIGITAL | IOD_STR_disk | D4204
STRComSCADA_stevec3 | INT | IOD_STR_disk | I4206
STRComSCADA_stevec | INT | IOD_STR_disk | I4208
STRComSCADA3 | DIGITAL | IOD_STR_TCP | 01191
STRkom_nast_cas_izpada | UINT | IOD_STR_TCP | 48001
STRCirc1MaximumDemandA2 | REAL | IOD_STR_TCP | 46223 | 0 | 1200 | 0 | 1200 | A | ###.#
STRCirc1MaximumDemandA3 | REAL | IOD_STR_TCP | 46225 | 0 | 1200 | 0 | 1200 | A | ###.#
STRCirc1RazEner_D_SCADA | REAL | IOD_STR_TCP | 46227
STRCirc1RazEner_T_SCADA | REAL | IOD_STR_TCP | 46229
STRCirc1RazEner_M_SCADA | REAL | IOD_STR_TCP | 46231
STRCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_STR_TCP | 01192
STRCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_STR_TCP | 01193
STRCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_STR_TCP | 01194
STRCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_STR_TCP | 01195
STRCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_STR_TCP | 01196
STRCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_STR_TCP | 01197
STRCirc_Vpis_Dnevne_energija_scada1_mem | DIGITAL | IOD_STR_disk | D4210
STRCirc_Vpis_Dnevne_energija_scada2_mem | DIGITAL | IOD_STR_disk | D4211
STRCirc_Vpis_Tedenska_energija_scada1_mem | DIGITAL | IOD_STR_disk | D4212
STRCirc_Vpis_Tedenska_energija_scada2_mem | DIGITAL | IOD_STR_disk | D4213
STRCirc_Vpis_Mesecna_energija_scada1_mem | DIGITAL | IOD_STR_disk | D4214
STRCirc_Vpis_Mesecna_energija_scada2_mem | DIGITAL | IOD_STR_disk | D4215

## XSoft
mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Write_BOOL(FC) | mod_Write_Word(FC) | mod_Write_Word(FC) | mod_Write_dWord(FC) | mod_Write_dWord(FC) | mod_Write_String(FC)
(*Branje BOOL*) | (*Branje INT*) | (*Branje UINT*) | (*Branje LONG*) | (*Branje REAL*) | (*Branje STRING*) | (*Pisanje BOOL*) | (*Pisanje INT*) | (*Pisanje UINT*) | (*Pisanje LONG*) | (*Pisanje REAL*) | (*Pisanje STRING*)
(**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**)
mind_bool[0]:=AkumSanVodeTE1OnOff; | mind[0]:=CrpalkeDnfs[1].PreklopkaMode; | mind[8000]:=kom_nast_cas_izpada; | Read_dWord(rVar:=XVH_CrpalkaGrfsNum,lo:=4000,hi:=4001); | Read_Real(rVar:=ATVAlarmTemp,lo:=5000,hi:=5001); | Read_String(sVar:=UserCurrentName,start:=7000); | 0:AkumSanVodeTE1OnOff:=Bit_0; | 0:CrpalkeDnfs[1].PreklopkaMode:=Word_01; | 8000:kom_nast_cas_izpada:=Word_01; | 4001:XVH_CrpalkaGrfsNum:=Long_0; | 5001:ATVAlarmTemp:=Real_0; | 7000:UserCurrentName:=String_0;
mind_bool[1]:=AlarmGenCirc1; | mind[1]:=CrpalkeDnfs[1].StarterStatus0do7; |  | Read_dWord(rVar:=XVH_StUrnika,lo:=4002,hi:=4003); | Read_Real(rVar:=Circ[1].CosFi_III,lo:=5002,hi:=5003); | Read_String(sVar:=Date_Time[0],start:=7015); | 1:AlarmGenCirc1:=Bit_0; | 1:CrpalkeDnfs[1].StarterStatus0do7:=Byte_0; |  | 4003:XVH_StUrnika:=Long_0; | 5003:Circ[1].CosFi_III:=Real_0; | 7015:Date_Time[0]:=String_0;
mind_bool[2]:=AlarmGenComm; | mind[2]:=CrpalkeDnfs[1].StatusCrpalke; |  |  | Read_Real(rVar:=Circ[1].DelovnaEnergija,lo:=5004,hi:=5005); | Read_String(sVar:=Date_Time[1],start:=7030); | 2:AlarmGenComm:=Bit_0; | 2:CrpalkeDnfs[1].StatusCrpalke:=Byte_0; |  |  | 5005:Circ[1].DelovnaEnergija:=Real_0; | 7030:Date_Time[1]:=String_0;
mind_bool[3]:=AlarmGenDI; | mind[3]:=CrpalkeDnfs[1].StatusKontaktor; |  |  | Read_Real(rVar:=Circ[1].DelovnaMoc_III,lo:=5006,hi:=5007); | Read_String(sVar:=Date_Time[2],start:=7045); | 3:AlarmGenDI:=Bit_0; | 3:CrpalkeDnfs[1].StatusKontaktor:=Word_01; |  |  | 5007:Circ[1].DelovnaMoc_III:=Real_0; | 7045:Date_Time[2]:=String_0;
mind_bool[4]:=AlarmGenHladPost; | mind[4]:=CrpalkeDnfs[2].PreklopkaMode; |  |  | Read_Real(rVar:=Circ[1].DelovnaMoc_L1,lo:=5008,hi:=5009); | Read_String(sVar:=Date_Time[3],start:=7060); | 4:AlarmGenHladPost:=Bit_0; | 4:CrpalkeDnfs[2].PreklopkaMode:=Word_01; |  |  | 5009:Circ[1].DelovnaMoc_L1:=Real_0; | 7060:Date_Time[3]:=String_0;
mind_bool[5]:=AlarmGenKlima1; | mind[5]:=CrpalkeDnfs[2].StarterStatus0do7; |  |  | Read_Real(rVar:=Circ[1].DelovnaMoc_L2,lo:=5010,hi:=5011); |  | 5:AlarmGenKlima1:=Bit_0; | 5:CrpalkeDnfs[2].StarterStatus0do7:=Byte_0; |  |  | 5011:Circ[1].DelovnaMoc_L2:=Real_0;
mind_bool[6]:=AlarmGenKlima2; | mind[6]:=CrpalkeDnfs[2].StatusCrpalke; |  |  | Read_Real(rVar:=Circ[1].DelovnaMoc_L3,lo:=5012,hi:=5013); |  | 6:AlarmGenKlima2:=Bit_0; | 6:CrpalkeDnfs[2].StatusCrpalke:=Byte_0; |  |  | 5013:Circ[1].DelovnaMoc_L3:=Real_0;
mind_bool[7]:=AlarmGenLopute; | mind[7]:=CrpalkeDnfs[2].StatusKontaktor; |  |  | Read_Real(rVar:=Circ[1].Frekvenca_L1,lo:=5014,hi:=5015); |  | 7:AlarmGenLopute:=Bit_0; | 7:CrpalkeDnfs[2].StatusKontaktor:=Word_01; |  |  | 5015:Circ[1].Frekvenca_L1:=Real_0;
mind_bool[8]:=AlarmGenRest; | mind[8]:=CrpalkeDnfs[3].PreklopkaMode; |  |  | Read_Real(rVar:=Circ[1].InduktivnaEnergija,lo:=5016,hi:=5017); |  | 8:AlarmGenRest:=Bit_0; | 8:CrpalkeDnfs[3].PreklopkaMode:=Word_01; |  |  | 5017:Circ[1].InduktivnaEnergija:=Real_0;
mind_bool[9]:=AlarmGenSenzor; | mind[9]:=CrpalkeDnfs[3].StarterStatus0do7; |  |  | Read_Real(rVar:=Circ[1].InduktivnaMoc_III,lo:=5018,hi:=5019); |  | 9:AlarmGenSenzor:=Bit_0; | 9:CrpalkeDnfs[3].StarterStatus0do7:=Byte_0; |  |  | 5019:Circ[1].InduktivnaMoc_III:=Real_0;
mind_bool[10]:=AlarmGenTemp; | mind[10]:=CrpalkeDnfs[3].StatusCrpalke; |  |  | Read_Real(rVar:=Circ[1].JalovaMoc_L1,lo:=5020,hi:=5021); |  | 10:AlarmGenTemp:=Bit_0; | 10:CrpalkeDnfs[3].StatusCrpalke:=Byte_0; |  |  | 5021:Circ[1].JalovaMoc_L1:=Real_0;
mind_bool[11]:=AlarmGenToplPost; | mind[11]:=CrpalkeDnfs[3].StatusKontaktor; |  |  | Read_Real(rVar:=Circ[1].JalovaMoc_L2,lo:=5022,hi:=5023); |  | 11:AlarmGenToplPost:=Bit_0; | 11:CrpalkeDnfs[3].StatusKontaktor:=Word_01; |  |  | 5023:Circ[1].JalovaMoc_L2:=Real_0;
mind_bool[12]:=AlarmGenVent; | mind[12]:=CrpalkeDnfs[4].PreklopkaMode; |  |  | Read_Real(rVar:=Circ[1].JalovaMoc_L3,lo:=5024,hi:=5025); |  | 12:AlarmGenVent:=Bit_0; | 12:CrpalkeDnfs[4].PreklopkaMode:=Word_01; |  |  | 5025:Circ[1].JalovaMoc_L3:=Real_0;
mind_bool[13]:=AlarmGenVTV; | mind[13]:=CrpalkeDnfs[4].StarterStatus0do7; |  |  | Read_Real(rVar:=Circ[1].KapacitivnaEnergija,lo:=5026,hi:=5027); |  | 13:AlarmGenVTV:=Bit_0; | 13:CrpalkeDnfs[4].StarterStatus0do7:=Byte_0; |  |  | 5027:Circ[1].KapacitivnaEnergija:=Real_0;
mind_bool[14]:=ATVTempPrenizka; | mind[14]:=CrpalkeDnfs[4].StatusCrpalke; |  |  | Read_Real(rVar:=Circ[1].KapacitivnaMoc_III,lo:=5028,hi:=5029); |  | 14:ATVTempPrenizka:=Bit_0; | 14:CrpalkeDnfs[4].StatusCrpalke:=Byte_0; |  |  | 5029:Circ[1].KapacitivnaMoc_III:=Real_0;
mind_bool[15]:=ComSCADA; | mind[15]:=CrpalkeDnfs[4].StatusKontaktor; |  |  | Read_Real(rVar:=Circ[1].MaximumDemand,lo:=5030,hi:=5031); |  | 15:ComSCADA:=Bit_0; | 15:CrpalkeDnfs[4].StatusKontaktor:=Word_01; |  |  | 5031:Circ[1].MaximumDemand:=Real_0;
mind_bool[16]:=ComSCADA1; | mind[16]:=CrpalkeGrfs[10].AlarmActiveCode; |  |  | Read_Real(rVar:=Circ[1].Napetost_L1_L2,lo:=5032,hi:=5033); |  | 16:ComSCADA1:=Bit_0; | 16:CrpalkeGrfs[10].AlarmActiveCode:=Word_01; |  |  | 5033:Circ[1].Napetost_L1_L2:=Real_0;
mind_bool[17]:=CrpalkaMN1OnOff; | mind[17]:=CrpalkeGrfs[10].AlarmCodeLog1; |  |  | Read_Real(rVar:=Circ[1].Napetost_L1_N,lo:=5034,hi:=5035); |  | 17:CrpalkaMN1OnOff:=Bit_0; | 17:CrpalkeGrfs[10].AlarmCodeLog1:=Word_01; |  |  | 5035:Circ[1].Napetost_L1_N:=Real_0;
mind_bool[18]:=CrpalkaTm11TM12OnOff; | mind[18]:=CrpalkeGrfs[10].AlarmCodeLog2; |  |  | Read_Real(rVar:=Circ[1].Napetost_L2_L3,lo:=5036,hi:=5037); |  | 18:CrpalkaTm11TM12OnOff:=Bit_0; | 18:CrpalkeGrfs[10].AlarmCodeLog2:=Word_01; |  |  | 5037:Circ[1].Napetost_L2_L3:=Real_0;
mind_bool[19]:=CrpalkeDnfs[1].AlarmAktiven; | mind[19]:=CrpalkeGrfs[10].AlarmCodeLog3; |  |  | Read_Real(rVar:=Circ[1].Napetost_L2_N,lo:=5038,hi:=5039); |  | 19:CrpalkeDnfs[1].AlarmAktiven:=Bit_0; | 19:CrpalkeGrfs[10].AlarmCodeLog3:=Word_01; |  |  | 5039:Circ[1].Napetost_L2_N:=Real_0;
mind_bool[20]:=CrpalkeDnfs[1].Deluje; | mind[20]:=CrpalkeGrfs[10].AlarmCodeLog4; |  |  | Read_Real(rVar:=Circ[1].Napetost_L3_L1,lo:=5040,hi:=5041); |  | 20:CrpalkeDnfs[1].Deluje:=Bit_0; | 20:CrpalkeGrfs[10].AlarmCodeLog4:=Word_01; |  |  | 5041:Circ[1].Napetost_L3_L1:=Real_0;
mind_bool[21]:=CrpalkeDnfs[1].QuickStop; | mind[21]:=CrpalkeGrfs[10].AlarmCodeLog5; |  |  | Read_Real(rVar:=Circ[1].Napetost_L3_N,lo:=5042,hi:=5043); |  | 21:CrpalkeDnfs[1].QuickStop:=Bit_0; | 21:CrpalkeGrfs[10].AlarmCodeLog5:=Word_01; |  |  | 5043:Circ[1].Napetost_L3_N:=Real_0;
mind_bool[22]:=CrpalkeDnfs[1].RemoteON; | mind[22]:=CrpalkeGrfs[10].AlarmGroupXVH[0]; |  |  | Read_Real(rVar:=Circ[1].NavideznaMoc_III,lo:=5044,hi:=5045); |  | 22:CrpalkeDnfs[1].RemoteON:=Bit_0; | 22:CrpalkeGrfs[10].AlarmGroupXVH[0]:=Word_01; |  |  | 5045:Circ[1].NavideznaMoc_III:=Real_0;
mind_bool[23]:=CrpalkeDnfs[1].Reset; | mind[23]:=CrpalkeGrfs[10].AlarmGroupXVH[10]; |  |  | Read_Real(rVar:=Circ[1].NicelniTok,lo:=5046,hi:=5047); |  | 23:CrpalkeDnfs[1].Reset:=Bit_0; | 23:CrpalkeGrfs[10].AlarmGroupXVH[10]:=Word_01; |  |  | 5047:Circ[1].NicelniTok:=Real_0;
mind_bool[24]:=CrpalkeDnfs[1].Start; | mind[24]:=CrpalkeGrfs[10].AlarmGroupXVH[11]; |  |  | Read_Real(rVar:=Circ[1].PowerFactor_III,lo:=5048,hi:=5049); |  | 24:CrpalkeDnfs[1].Start:=Bit_0; | 24:CrpalkeGrfs[10].AlarmGroupXVH[11]:=Word_01; |  |  | 5049:Circ[1].PowerFactor_III:=Real_0;
mind_bool[25]:=CrpalkeDnfs[1].Stop; | mind[25]:=CrpalkeGrfs[10].AlarmGroupXVH[12]; |  |  | Read_Real(rVar:=Circ[1].PowerFactor_L1,lo:=5050,hi:=5051); |  | 25:CrpalkeDnfs[1].Stop:=Bit_0; | 25:CrpalkeGrfs[10].AlarmGroupXVH[12]:=Word_01; |  |  | 5051:Circ[1].PowerFactor_L1:=Real_0;
mind_bool[26]:=CrpalkeDnfs[2].AlarmAktiven; | mind[26]:=CrpalkeGrfs[10].AlarmGroupXVH[13]; |  |  | Read_Real(rVar:=Circ[1].PowerFactor_L2,lo:=5052,hi:=5053); |  | 26:CrpalkeDnfs[2].AlarmAktiven:=Bit_0; | 26:CrpalkeGrfs[10].AlarmGroupXVH[13]:=Word_01; |  |  | 5053:Circ[1].PowerFactor_L2:=Real_0;
mind_bool[27]:=CrpalkeDnfs[2].Deluje; | mind[27]:=CrpalkeGrfs[10].AlarmGroupXVH[14]; |  |  | Read_Real(rVar:=Circ[1].PowerFactor_L3,lo:=5054,hi:=5055); |  | 27:CrpalkeDnfs[2].Deluje:=Bit_0; | 27:CrpalkeGrfs[10].AlarmGroupXVH[14]:=Word_01; |  |  | 5055:Circ[1].PowerFactor_L3:=Real_0;
mind_bool[28]:=CrpalkeDnfs[2].QuickStop; | mind[28]:=CrpalkeGrfs[10].AlarmGroupXVH[15]; |  |  | Read_Real(rVar:=Circ[1].THDI_L1,lo:=5056,hi:=5057); |  | 28:CrpalkeDnfs[2].QuickStop:=Bit_0; | 28:CrpalkeGrfs[10].AlarmGroupXVH[15]:=Word_01; |  |  | 5057:Circ[1].THDI_L1:=Real_0;
mind_bool[29]:=CrpalkeDnfs[2].RemoteON; | mind[29]:=CrpalkeGrfs[10].AlarmGroupXVH[16]; |  |  | Read_Real(rVar:=Circ[1].THDI_L2,lo:=5058,hi:=5059); |  | 29:CrpalkeDnfs[2].RemoteON:=Bit_0; | 29:CrpalkeGrfs[10].AlarmGroupXVH[16]:=Word_01; |  |  | 5059:Circ[1].THDI_L2:=Real_0;
mind_bool[30]:=CrpalkeDnfs[2].Reset; | mind[30]:=CrpalkeGrfs[10].AlarmGroupXVH[1]; |  |  | Read_Real(rVar:=Circ[1].THDI_L3,lo:=5060,hi:=5061); |  | 30:CrpalkeDnfs[2].Reset:=Bit_0; | 30:CrpalkeGrfs[10].AlarmGroupXVH[1]:=Word_01; |  |  | 5061:Circ[1].THDI_L3:=Real_0;
mind_bool[31]:=CrpalkeDnfs[2].Start; | mind[31]:=CrpalkeGrfs[10].AlarmGroupXVH[2]; |  |  | Read_Real(rVar:=Circ[1].THDV_L1,lo:=5062,hi:=5063); |  | 31:CrpalkeDnfs[2].Start:=Bit_0; | 31:CrpalkeGrfs[10].AlarmGroupXVH[2]:=Word_01; |  |  | 5063:Circ[1].THDV_L1:=Real_0;
mind_bool[32]:=CrpalkeDnfs[2].Stop; | mind[32]:=CrpalkeGrfs[10].AlarmGroupXVH[3]; |  |  | Read_Real(rVar:=Circ[1].THDV_L2,lo:=5064,hi:=5065); |  | 32:CrpalkeDnfs[2].Stop:=Bit_0; | 32:CrpalkeGrfs[10].AlarmGroupXVH[3]:=Word_01; |  |  | 5065:Circ[1].THDV_L2:=Real_0;
mind_bool[33]:=CrpalkeDnfs[3].AlarmAktiven; | mind[33]:=CrpalkeGrfs[10].AlarmGroupXVH[4]; |  |  | Read_Real(rVar:=Circ[1].THDV_L3,lo:=5066,hi:=5067); |  | 33:CrpalkeDnfs[3].AlarmAktiven:=Bit_0; | 33:CrpalkeGrfs[10].AlarmGroupXVH[4]:=Word_01; |  |  | 5067:Circ[1].THDV_L3:=Real_0;
mind_bool[34]:=CrpalkeDnfs[3].Deluje; | mind[34]:=CrpalkeGrfs[10].AlarmGroupXVH[5]; |  |  | Read_Real(rVar:=Circ[1].Tok_L1,lo:=5068,hi:=5069); |  | 34:CrpalkeDnfs[3].Deluje:=Bit_0; | 34:CrpalkeGrfs[10].AlarmGroupXVH[5]:=Word_01; |  |  | 5069:Circ[1].Tok_L1:=Real_0;
mind_bool[35]:=CrpalkeDnfs[3].QuickStop; | mind[35]:=CrpalkeGrfs[10].AlarmGroupXVH[6]; |  |  | Read_Real(rVar:=Circ[1].Tok_L2,lo:=5070,hi:=5071); |  | 35:CrpalkeDnfs[3].QuickStop:=Bit_0; | 35:CrpalkeGrfs[10].AlarmGroupXVH[6]:=Word_01; |  |  | 5071:Circ[1].Tok_L2:=Real_0;
mind_bool[36]:=CrpalkeDnfs[3].RemoteON; | mind[36]:=CrpalkeGrfs[10].AlarmGroupXVH[7]; |  |  | Read_Real(rVar:=Circ[1].Tok_L3,lo:=5072,hi:=5073); |  | 36:CrpalkeDnfs[3].RemoteON:=Bit_0; | 36:CrpalkeGrfs[10].AlarmGroupXVH[7]:=Word_01; |  |  | 5073:Circ[1].Tok_L3:=Real_0;
mind_bool[37]:=CrpalkeDnfs[3].Reset; | mind[37]:=CrpalkeGrfs[10].AlarmGroupXVH[8]; |  |  | Read_Real(rVar:=Circ[1].TokPovprecje_III,lo:=5074,hi:=5075); |  | 37:CrpalkeDnfs[3].Reset:=Bit_0; | 37:CrpalkeGrfs[10].AlarmGroupXVH[8]:=Word_01; |  |  | 5075:Circ[1].TokPovprecje_III:=Real_0;
mind_bool[38]:=CrpalkeDnfs[3].Start; | mind[38]:=CrpalkeGrfs[10].AlarmGroupXVH[9]; |  |  | Read_Real(rVar:=CrpalkeDnfs[1].Current,lo:=5076,hi:=5077); |  | 38:CrpalkeDnfs[3].Start:=Bit_0; | 38:CrpalkeGrfs[10].AlarmGroupXVH[9]:=Word_01; |  |  | 5077:CrpalkeDnfs[1].Current:=Real_0;
mind_bool[39]:=CrpalkeDnfs[3].Stop; | mind[39]:=CrpalkeGrfs[10].AlarmQSD1; |  |  | Read_Real(rVar:=CrpalkeDnfs[1].StarterStatus,lo:=5078,hi:=5079); |  | 39:CrpalkeDnfs[3].Stop:=Bit_0; | 39:CrpalkeGrfs[10].AlarmQSD1:=Word_01; |  |  | 5079:CrpalkeDnfs[1].StarterStatus:=Real_0;
mind_bool[40]:=CrpalkeDnfs[4].AlarmAktiven; | mind[40]:=CrpalkeGrfs[10].AlarmQSD2; |  |  | Read_Real(rVar:=CrpalkeDnfs[1].Temerature,lo:=5080,hi:=5081); |  | 40:CrpalkeDnfs[4].AlarmAktiven:=Bit_0; | 40:CrpalkeGrfs[10].AlarmQSD2:=Word_01; |  |  | 5081:CrpalkeDnfs[1].Temerature:=Real_0;
mind_bool[41]:=CrpalkeDnfs[4].Deluje; | mind[41]:=CrpalkeGrfs[10].AlarmStart1; |  |  | Read_Real(rVar:=CrpalkeDnfs[1].TripCode,lo:=5082,hi:=5083); |  | 41:CrpalkeDnfs[4].Deluje:=Bit_0; | 41:CrpalkeGrfs[10].AlarmStart1:=Word_01; |  |  | 5083:CrpalkeDnfs[1].TripCode:=Real_0;
mind_bool[42]:=CrpalkeDnfs[4].QuickStop; | mind[42]:=CrpalkeGrfs[10].AlarmStart2; |  |  | Read_Real(rVar:=CrpalkeDnfs[1].UreXC200,lo:=5084,hi:=5085); |  | 42:CrpalkeDnfs[4].QuickStop:=Bit_0; | 42:CrpalkeGrfs[10].AlarmStart2:=Word_01; |  |  | 5085:CrpalkeDnfs[1].UreXC200:=Real_0;
mind_bool[43]:=CrpalkeDnfs[4].RemoteON; | mind[43]:=CrpalkeGrfs[10].AlarmStop1; |  |  | Read_Real(rVar:=CrpalkeDnfs[2].Current,lo:=5086,hi:=5087); |  | 43:CrpalkeDnfs[4].RemoteON:=Bit_0; | 43:CrpalkeGrfs[10].AlarmStop1:=Word_01; |  |  | 5087:CrpalkeDnfs[2].Current:=Real_0;
mind_bool[44]:=CrpalkeDnfs[4].Reset; | mind[44]:=CrpalkeGrfs[10].AlarmStop2; |  |  | Read_Real(rVar:=CrpalkeDnfs[2].StarterStatus,lo:=5088,hi:=5089); |  | 44:CrpalkeDnfs[4].Reset:=Bit_0; | 44:CrpalkeGrfs[10].AlarmStop2:=Word_01; |  |  | 5089:CrpalkeDnfs[2].StarterStatus:=Real_0;
mind_bool[45]:=CrpalkeDnfs[4].Start; | mind[45]:=CrpalkeGrfs[10].AlarmStop3; |  |  | Read_Real(rVar:=CrpalkeDnfs[2].Temerature,lo:=5090,hi:=5091); |  | 45:CrpalkeDnfs[4].Start:=Bit_0; | 45:CrpalkeGrfs[10].AlarmStop3:=Word_01; |  |  | 5091:CrpalkeDnfs[2].Temerature:=Real_0;
mind_bool[46]:=CrpalkeDnfs[4].Stop; | mind[46]:=CrpalkeGrfs[10].AlarmSurv1; |  |  | Read_Real(rVar:=CrpalkeDnfs[2].TripCode,lo:=5092,hi:=5093); |  | 46:CrpalkeDnfs[4].Stop:=Bit_0; | 46:CrpalkeGrfs[10].AlarmSurv1:=Word_01; |  |  | 5093:CrpalkeDnfs[2].TripCode:=Real_0;
mind_bool[47]:=CrpalkeGrfs[10].AlarmAktiven; | mind[47]:=CrpalkeGrfs[10].AlarmSurv2; |  |  | Read_Real(rVar:=CrpalkeDnfs[2].UreXC200,lo:=5094,hi:=5095); |  | 47:CrpalkeGrfs[10].AlarmAktiven:=Bit_0; | 47:CrpalkeGrfs[10].AlarmSurv2:=Word_01; |  |  | 5095:CrpalkeDnfs[2].UreXC200:=Real_0;
mind_bool[48]:=CrpalkeGrfs[10].Deluje; | mind[48]:=CrpalkeGrfs[10].ControlSource; |  |  | Read_Real(rVar:=CrpalkeDnfs[3].Current,lo:=5096,hi:=5097); |  | 48:CrpalkeGrfs[10].Deluje:=Bit_0; | 48:CrpalkeGrfs[10].ControlSource:=Word_01; |  |  | 5097:CrpalkeDnfs[3].Current:=Real_0;
mind_bool[49]:=CrpalkeGrfs[10].LocalMode; | mind[49]:=CrpalkeGrfs[10].ExternInputSetup; |  |  | Read_Real(rVar:=CrpalkeDnfs[3].StarterStatus,lo:=5098,hi:=5099); |  | 49:CrpalkeGrfs[10].LocalMode:=Bit_0; | 49:CrpalkeGrfs[10].ExternInputSetup:=Word_01; |  |  | 5099:CrpalkeDnfs[3].StarterStatus:=Real_0;
mind_bool[50]:=CrpalkeGrfs[10].RemoteON; | mind[50]:=CrpalkeGrfs[10].ExternInputsStatus; |  |  | Read_Real(rVar:=CrpalkeDnfs[3].Temerature,lo:=5100,hi:=5101); |  | 50:CrpalkeGrfs[10].RemoteON:=Bit_0; | 50:CrpalkeGrfs[10].ExternInputsStatus:=Word_01; |  |  | 5101:CrpalkeDnfs[3].Temerature:=Real_0;
mind_bool[51]:=CrpalkeGrfs[10].Reset2handkWhValues; | mind[51]:=CrpalkeGrfs[10].LocalSetupMode1; |  |  | Read_Real(rVar:=CrpalkeDnfs[3].TripCode,lo:=5102,hi:=5103); |  | 51:CrpalkeGrfs[10].Reset2handkWhValues:=Bit_0; | 51:CrpalkeGrfs[10].LocalSetupMode1:=Word_01; |  |  | 5103:CrpalkeDnfs[3].TripCode:=Real_0;
mind_bool[52]:=CrpalkeGrfs[10].ResetAlarm; | mind[52]:=CrpalkeGrfs[10].PreklopkaMode; |  |  | Read_Real(rVar:=CrpalkeDnfs[3].UreXC200,lo:=5104,hi:=5105); |  | 52:CrpalkeGrfs[10].ResetAlarm:=Bit_0; | 52:CrpalkeGrfs[10].PreklopkaMode:=Word_01; |  |  | 5105:CrpalkeDnfs[3].UreXC200:=Real_0;
mind_bool[53]:=CrpalkeGrfs[10].ResetAlarmLog; | mind[53]:=CrpalkeGrfs[10].Relay1setup; |  |  | Read_Real(rVar:=CrpalkeDnfs[4].Current,lo:=5106,hi:=5107); |  | 53:CrpalkeGrfs[10].ResetAlarmLog:=Bit_0; | 53:CrpalkeGrfs[10].Relay1setup:=Word_01; |  |  | 5107:CrpalkeDnfs[4].Current:=Real_0;
mind_bool[54]:=CrpalkeGrfs[10].ResetDevice; | mind[54]:=CrpalkeGrfs[10].RemoteSetupMode1; |  |  | Read_Real(rVar:=CrpalkeDnfs[4].StarterStatus,lo:=5108,hi:=5109); |  | 54:CrpalkeGrfs[10].ResetDevice:=Bit_0; | 54:CrpalkeGrfs[10].RemoteSetupMode1:=Word_01; |  |  | 5109:CrpalkeDnfs[4].StarterStatus:=Real_0;
mind_bool[55]:=CrpalkeGrfs[10].SetAutomatic; | mind[55]:=CrpalkeGrfs[10].StatusCrpalke; |  |  | Read_Real(rVar:=CrpalkeDnfs[4].Temerature,lo:=5110,hi:=5111); |  | 55:CrpalkeGrfs[10].SetAutomatic:=Bit_0; | 55:CrpalkeGrfs[10].StatusCrpalke:=Byte_0; |  |  | 5111:CrpalkeDnfs[4].Temerature:=Real_0;
mind_bool[56]:=CrpalkeGrfs[10].SetConstFreqMode; | mind[56]:=CrpalkeGrfs[10].StatusMode1; |  |  | Read_Real(rVar:=CrpalkeDnfs[4].TripCode,lo:=5112,hi:=5113); |  | 56:CrpalkeGrfs[10].SetConstFreqMode:=Bit_0; | 56:CrpalkeGrfs[10].StatusMode1:=Word_01; |  |  | 5113:CrpalkeDnfs[4].TripCode:=Real_0;
mind_bool[57]:=CrpalkeGrfs[10].SetConstPress; | mind[57]:=CrpalkeGrfs[10].StatusMode1co; |  |  | Read_Real(rVar:=CrpalkeDnfs[4].UreXC200,lo:=5114,hi:=5115); |  | 57:CrpalkeGrfs[10].SetConstPress:=Bit_0; | 57:CrpalkeGrfs[10].StatusMode1co:=Byte_0; |  |  | 5115:CrpalkeDnfs[4].UreXC200:=Real_0;
mind_bool[58]:=CrpalkeGrfs[10].SetLocalMode; | mind[58]:=CrpalkeGrfs[10].StatusMode1op; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].DeltaSetPoint,lo:=5116,hi:=5117); |  | 58:CrpalkeGrfs[10].SetLocalMode:=Bit_0; | 58:CrpalkeGrfs[10].StatusMode1op:=Byte_0; |  |  | 5117:CrpalkeGrfs[10].DeltaSetPoint:=Real_0;
mind_bool[59]:=CrpalkeGrfs[10].SetMaxRunMode; | mind[59]:=CrpalkeGrfs[10].StatusMode2; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].EnergijaPoraba,lo:=5118,hi:=5119); |  | 59:CrpalkeGrfs[10].SetMaxRunMode:=Bit_0; | 59:CrpalkeGrfs[10].StatusMode2:=Word_01; |  |  | 5119:CrpalkeGrfs[10].EnergijaPoraba:=Real_0;
mind_bool[60]:=CrpalkeGrfs[10].SetMinRunMode; | mind[60]:=CrpalkeGrfs[10].StatusMode3; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].FrekPretvornikDCNapetost,lo:=5120,hi:=5121); |  | 60:CrpalkeGrfs[10].SetMinRunMode:=Bit_0; | 60:CrpalkeGrfs[10].StatusMode3:=Word_01; |  |  | 5121:CrpalkeGrfs[10].FrekPretvornikDCNapetost:=Real_0;
mind_bool[61]:=CrpalkeGrfs[10].SetPropPress; | mind[61]:=CrpalkeGrfs[11].AlarmActiveCode; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].FrekPretvornikDCTok,lo:=5122,hi:=5123); |  | 61:CrpalkeGrfs[10].SetPropPress:=Bit_0; | 61:CrpalkeGrfs[11].AlarmActiveCode:=Word_01; |  |  | 5123:CrpalkeGrfs[10].FrekPretvornikDCTok:=Real_0;
mind_bool[62]:=CrpalkeGrfs[10].SetReference; | mind[62]:=CrpalkeGrfs[11].AlarmCodeLog1; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].FreqMax,lo:=5124,hi:=5125); |  | 62:CrpalkeGrfs[10].SetReference:=Bit_0; | 62:CrpalkeGrfs[11].AlarmCodeLog1:=Word_01; |  |  | 5125:CrpalkeGrfs[10].FreqMax:=Real_0;
mind_bool[63]:=CrpalkeGrfs[10].SetRemoteMode; | mind[63]:=CrpalkeGrfs[11].AlarmCodeLog2; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].FreqMin,lo:=5126,hi:=5127); |  | 63:CrpalkeGrfs[10].SetRemoteMode:=Bit_0; | 63:CrpalkeGrfs[11].AlarmCodeLog2:=Word_01; |  |  | 5127:CrpalkeGrfs[10].FreqMin:=Real_0;
mind_bool[64]:=CrpalkeGrfs[10].SetTwinModeAlt; | mind[64]:=CrpalkeGrfs[11].AlarmCodeLog3; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].FreqUpper,lo:=5128,hi:=5129); |  | 64:CrpalkeGrfs[10].SetTwinModeAlt:=Bit_0; | 64:CrpalkeGrfs[11].AlarmCodeLog3:=Word_01; |  |  | 5129:CrpalkeGrfs[10].FreqUpper:=Real_0;
mind_bool[65]:=CrpalkeGrfs[10].SetTwinModeSpare; | mind[65]:=CrpalkeGrfs[11].AlarmCodeLog4; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].MocMax,lo:=5130,hi:=5131); |  | 65:CrpalkeGrfs[10].SetTwinModeSpare:=Bit_0; | 65:CrpalkeGrfs[11].AlarmCodeLog4:=Word_01; |  |  | 5131:CrpalkeGrfs[10].MocMax:=Real_0;
mind_bool[66]:=CrpalkeGrfs[10].SetTwinModeSync; | mind[66]:=CrpalkeGrfs[11].AlarmCodeLog5; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].MocTrenutna,lo:=5132,hi:=5133); |  | 66:CrpalkeGrfs[10].SetTwinModeSync:=Bit_0; | 66:CrpalkeGrfs[11].AlarmCodeLog5:=Word_01; |  |  | 5133:CrpalkeGrfs[10].MocTrenutna:=Real_0;
mind_bool[67]:=CrpalkeGrfs[10].Start; | mind[67]:=CrpalkeGrfs[11].AlarmGroupXVH[0]; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].MotorHitrost,lo:=5134,hi:=5135); |  | 67:CrpalkeGrfs[10].Start:=Bit_0; | 67:CrpalkeGrfs[11].AlarmGroupXVH[0]:=Word_01; |  |  | 5135:CrpalkeGrfs[10].MotorHitrost:=Real_0;
mind_bool[68]:=CrpalkeGrfs[10].Stop; | mind[68]:=CrpalkeGrfs[11].AlarmGroupXVH[10]; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].MotorTok,lo:=5136,hi:=5137); |  | 68:CrpalkeGrfs[10].Stop:=Bit_0; | 68:CrpalkeGrfs[11].AlarmGroupXVH[10]:=Word_01; |  |  | 5137:CrpalkeGrfs[10].MotorTok:=Real_0;
mind_bool[69]:=CrpalkeGrfs[11].AlarmAktiven; | mind[69]:=CrpalkeGrfs[11].AlarmGroupXVH[11]; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].NapajanjeTok,lo:=5138,hi:=5139); |  | 69:CrpalkeGrfs[11].AlarmAktiven:=Bit_0; | 69:CrpalkeGrfs[11].AlarmGroupXVH[11]:=Word_01; |  |  | 5139:CrpalkeGrfs[10].NapajanjeTok:=Real_0;
mind_bool[70]:=CrpalkeGrfs[11].Deluje; | mind[70]:=CrpalkeGrfs[11].AlarmGroupXVH[12]; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].NastavitevLokalna,lo:=5140,hi:=5141); |  | 70:CrpalkeGrfs[11].Deluje:=Bit_0; | 70:CrpalkeGrfs[11].AlarmGroupXVH[12]:=Word_01; |  |  | 5141:CrpalkeGrfs[10].NastavitevLokalna:=Real_0;
mind_bool[71]:=CrpalkeGrfs[11].LocalMode; | mind[71]:=CrpalkeGrfs[11].AlarmGroupXVH[13]; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].NastavitevTrenutna,lo:=5142,hi:=5143); |  | 71:CrpalkeGrfs[11].LocalMode:=Bit_0; | 71:CrpalkeGrfs[11].AlarmGroupXVH[13]:=Word_01; |  |  | 5143:CrpalkeGrfs[10].NastavitevTrenutna:=Real_0;
mind_bool[72]:=CrpalkeGrfs[11].RemoteON; | mind[72]:=CrpalkeGrfs[11].AlarmGroupXVH[14]; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].PretokMax,lo:=5144,hi:=5145); |  | 72:CrpalkeGrfs[11].RemoteON:=Bit_0; | 72:CrpalkeGrfs[11].AlarmGroupXVH[14]:=Word_01; |  |  | 5145:CrpalkeGrfs[10].PretokMax:=Real_0;
mind_bool[73]:=CrpalkeGrfs[11].Reset2handkWhValues; | mind[73]:=CrpalkeGrfs[11].AlarmGroupXVH[15]; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].PretokMin,lo:=5146,hi:=5147); |  | 73:CrpalkeGrfs[11].Reset2handkWhValues:=Bit_0; | 73:CrpalkeGrfs[11].AlarmGroupXVH[15]:=Word_01; |  |  | 5147:CrpalkeGrfs[10].PretokMin:=Real_0;
mind_bool[74]:=CrpalkeGrfs[11].ResetAlarm; | mind[74]:=CrpalkeGrfs[11].AlarmGroupXVH[16]; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].PretokTrenutni,lo:=5148,hi:=5149); |  | 74:CrpalkeGrfs[11].ResetAlarm:=Bit_0; | 74:CrpalkeGrfs[11].AlarmGroupXVH[16]:=Word_01; |  |  | 5149:CrpalkeGrfs[10].PretokTrenutni:=Real_0;
mind_bool[75]:=CrpalkeGrfs[11].ResetAlarmLog; | mind[75]:=CrpalkeGrfs[11].AlarmGroupXVH[1]; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].PritiskMax,lo:=5150,hi:=5151); |  | 75:CrpalkeGrfs[11].ResetAlarmLog:=Bit_0; | 75:CrpalkeGrfs[11].AlarmGroupXVH[1]:=Word_01; |  |  | 5151:CrpalkeGrfs[10].PritiskMax:=Real_0;
mind_bool[76]:=CrpalkeGrfs[11].ResetDevice; | mind[76]:=CrpalkeGrfs[11].AlarmGroupXVH[2]; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].PritiskTrenutni,lo:=5152,hi:=5153); |  | 76:CrpalkeGrfs[11].ResetDevice:=Bit_0; | 76:CrpalkeGrfs[11].AlarmGroupXVH[2]:=Word_01; |  |  | 5153:CrpalkeGrfs[10].PritiskTrenutni:=Real_0;
mind_bool[77]:=CrpalkeGrfs[11].SetAutomatic; | mind[77]:=CrpalkeGrfs[11].AlarmGroupXVH[3]; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].ReferencaMotorjaHzV,lo:=5154,hi:=5155); |  | 77:CrpalkeGrfs[11].SetAutomatic:=Bit_0; | 77:CrpalkeGrfs[11].AlarmGroupXVH[3]:=Word_01; |  |  | 5155:CrpalkeGrfs[10].ReferencaMotorjaHzV:=Real_0;
mind_bool[78]:=CrpalkeGrfs[11].SetConstFreqMode; | mind[78]:=CrpalkeGrfs[11].AlarmGroupXVH[4]; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].ReferencaRemote,lo:=5156,hi:=5157); |  | 78:CrpalkeGrfs[11].SetConstFreqMode:=Bit_0; | 78:CrpalkeGrfs[11].AlarmGroupXVH[4]:=Word_01; |  |  | 5157:CrpalkeGrfs[10].ReferencaRemote:=Real_0;
mind_bool[79]:=CrpalkeGrfs[11].SetConstPress; | mind[79]:=CrpalkeGrfs[11].AlarmGroupXVH[5]; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].StevecUr2h,lo:=5158,hi:=5159); |  | 79:CrpalkeGrfs[11].SetConstPress:=Bit_0; | 79:CrpalkeGrfs[11].AlarmGroupXVH[5]:=Word_01; |  |  | 5159:CrpalkeGrfs[10].StevecUr2h:=Real_0;
mind_bool[80]:=CrpalkeGrfs[11].SetLocalMode; | mind[80]:=CrpalkeGrfs[11].AlarmGroupXVH[6]; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].SystemFeedback,lo:=5160,hi:=5161); |  | 80:CrpalkeGrfs[11].SetLocalMode:=Bit_0; | 80:CrpalkeGrfs[11].AlarmGroupXVH[6]:=Word_01; |  |  | 5161:CrpalkeGrfs[10].SystemFeedback:=Real_0;
mind_bool[81]:=CrpalkeGrfs[11].SetMaxRunMode; | mind[81]:=CrpalkeGrfs[11].AlarmGroupXVH[7]; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].SystemReference,lo:=5162,hi:=5163); |  | 81:CrpalkeGrfs[11].SetMaxRunMode:=Bit_0; | 81:CrpalkeGrfs[11].AlarmGroupXVH[7]:=Word_01; |  |  | 5163:CrpalkeGrfs[10].SystemReference:=Real_0;
mind_bool[82]:=CrpalkeGrfs[11].SetMinRunMode; | mind[82]:=CrpalkeGrfs[11].AlarmGroupXVH[8]; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].TemperaturaMotorja,lo:=5164,hi:=5165); |  | 82:CrpalkeGrfs[11].SetMinRunMode:=Bit_0; | 82:CrpalkeGrfs[11].AlarmGroupXVH[8]:=Word_01; |  |  | 5165:CrpalkeGrfs[10].TemperaturaMotorja:=Real_0;
mind_bool[83]:=CrpalkeGrfs[11].SetPropPress; | mind[83]:=CrpalkeGrfs[11].AlarmGroupXVH[9]; |  |  | Read_Real(rVar:=CrpalkeGrfs[10].UreXC200,lo:=5166,hi:=5167); |  | 83:CrpalkeGrfs[11].SetPropPress:=Bit_0; | 83:CrpalkeGrfs[11].AlarmGroupXVH[9]:=Word_01; |  |  | 5167:CrpalkeGrfs[10].UreXC200:=Real_0;
mind_bool[84]:=CrpalkeGrfs[11].SetReference; | mind[84]:=CrpalkeGrfs[11].AlarmQSD1; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].DeltaSetPoint,lo:=5168,hi:=5169); |  | 84:CrpalkeGrfs[11].SetReference:=Bit_0; | 84:CrpalkeGrfs[11].AlarmQSD1:=Word_01; |  |  | 5169:CrpalkeGrfs[11].DeltaSetPoint:=Real_0;
mind_bool[85]:=CrpalkeGrfs[11].SetRemoteMode; | mind[85]:=CrpalkeGrfs[11].AlarmQSD2; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].EnergijaPoraba,lo:=5170,hi:=5171); |  | 85:CrpalkeGrfs[11].SetRemoteMode:=Bit_0; | 85:CrpalkeGrfs[11].AlarmQSD2:=Word_01; |  |  | 5171:CrpalkeGrfs[11].EnergijaPoraba:=Real_0;
mind_bool[86]:=CrpalkeGrfs[11].SetTwinModeAlt; | mind[86]:=CrpalkeGrfs[11].AlarmStart1; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].FrekPretvornikDCNapetost,lo:=5172,hi:=5173); |  | 86:CrpalkeGrfs[11].SetTwinModeAlt:=Bit_0; | 86:CrpalkeGrfs[11].AlarmStart1:=Word_01; |  |  | 5173:CrpalkeGrfs[11].FrekPretvornikDCNapetost:=Real_0;
mind_bool[87]:=CrpalkeGrfs[11].SetTwinModeSpare; | mind[87]:=CrpalkeGrfs[11].AlarmStart2; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].FrekPretvornikDCTok,lo:=5174,hi:=5175); |  | 87:CrpalkeGrfs[11].SetTwinModeSpare:=Bit_0; | 87:CrpalkeGrfs[11].AlarmStart2:=Word_01; |  |  | 5175:CrpalkeGrfs[11].FrekPretvornikDCTok:=Real_0;
mind_bool[88]:=CrpalkeGrfs[11].SetTwinModeSync; | mind[88]:=CrpalkeGrfs[11].AlarmStop1; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].FreqMax,lo:=5176,hi:=5177); |  | 88:CrpalkeGrfs[11].SetTwinModeSync:=Bit_0; | 88:CrpalkeGrfs[11].AlarmStop1:=Word_01; |  |  | 5177:CrpalkeGrfs[11].FreqMax:=Real_0;
mind_bool[89]:=CrpalkeGrfs[11].Start; | mind[89]:=CrpalkeGrfs[11].AlarmStop2; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].FreqMin,lo:=5178,hi:=5179); |  | 89:CrpalkeGrfs[11].Start:=Bit_0; | 89:CrpalkeGrfs[11].AlarmStop2:=Word_01; |  |  | 5179:CrpalkeGrfs[11].FreqMin:=Real_0;
mind_bool[90]:=CrpalkeGrfs[11].Stop; | mind[90]:=CrpalkeGrfs[11].AlarmStop3; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].FreqUpper,lo:=5180,hi:=5181); |  | 90:CrpalkeGrfs[11].Stop:=Bit_0; | 90:CrpalkeGrfs[11].AlarmStop3:=Word_01; |  |  | 5181:CrpalkeGrfs[11].FreqUpper:=Real_0;
mind_bool[91]:=CrpalkeGrfs[12].AlarmAktiven; | mind[91]:=CrpalkeGrfs[11].AlarmSurv1; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].MocMax,lo:=5182,hi:=5183); |  | 91:CrpalkeGrfs[12].AlarmAktiven:=Bit_0; | 91:CrpalkeGrfs[11].AlarmSurv1:=Word_01; |  |  | 5183:CrpalkeGrfs[11].MocMax:=Real_0;
mind_bool[92]:=CrpalkeGrfs[12].Deluje; | mind[92]:=CrpalkeGrfs[11].AlarmSurv2; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].MocTrenutna,lo:=5184,hi:=5185); |  | 92:CrpalkeGrfs[12].Deluje:=Bit_0; | 92:CrpalkeGrfs[11].AlarmSurv2:=Word_01; |  |  | 5185:CrpalkeGrfs[11].MocTrenutna:=Real_0;
mind_bool[93]:=CrpalkeGrfs[12].LocalMode; | mind[93]:=CrpalkeGrfs[11].ControlSource; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].MotorHitrost,lo:=5186,hi:=5187); |  | 93:CrpalkeGrfs[12].LocalMode:=Bit_0; | 93:CrpalkeGrfs[11].ControlSource:=Word_01; |  |  | 5187:CrpalkeGrfs[11].MotorHitrost:=Real_0;
mind_bool[94]:=CrpalkeGrfs[12].RemoteON; | mind[94]:=CrpalkeGrfs[11].ExternInputSetup; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].MotorTok,lo:=5188,hi:=5189); |  | 94:CrpalkeGrfs[12].RemoteON:=Bit_0; | 94:CrpalkeGrfs[11].ExternInputSetup:=Word_01; |  |  | 5189:CrpalkeGrfs[11].MotorTok:=Real_0;
mind_bool[95]:=CrpalkeGrfs[12].Reset2handkWhValues; | mind[95]:=CrpalkeGrfs[11].ExternInputsStatus; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].NapajanjeTok,lo:=5190,hi:=5191); |  | 95:CrpalkeGrfs[12].Reset2handkWhValues:=Bit_0; | 95:CrpalkeGrfs[11].ExternInputsStatus:=Word_01; |  |  | 5191:CrpalkeGrfs[11].NapajanjeTok:=Real_0;
mind_bool[96]:=CrpalkeGrfs[12].ResetAlarm; | mind[96]:=CrpalkeGrfs[11].LocalSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].NastavitevLokalna,lo:=5192,hi:=5193); |  | 96:CrpalkeGrfs[12].ResetAlarm:=Bit_0; | 96:CrpalkeGrfs[11].LocalSetupMode1:=Word_01; |  |  | 5193:CrpalkeGrfs[11].NastavitevLokalna:=Real_0;
mind_bool[97]:=CrpalkeGrfs[12].ResetAlarmLog; | mind[97]:=CrpalkeGrfs[11].PreklopkaMode; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].NastavitevTrenutna,lo:=5194,hi:=5195); |  | 97:CrpalkeGrfs[12].ResetAlarmLog:=Bit_0; | 97:CrpalkeGrfs[11].PreklopkaMode:=Word_01; |  |  | 5195:CrpalkeGrfs[11].NastavitevTrenutna:=Real_0;
mind_bool[98]:=CrpalkeGrfs[12].ResetDevice; | mind[98]:=CrpalkeGrfs[11].Relay1setup; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].PretokMax,lo:=5196,hi:=5197); |  | 98:CrpalkeGrfs[12].ResetDevice:=Bit_0; | 98:CrpalkeGrfs[11].Relay1setup:=Word_01; |  |  | 5197:CrpalkeGrfs[11].PretokMax:=Real_0;
mind_bool[99]:=CrpalkeGrfs[12].SetAutomatic; | mind[99]:=CrpalkeGrfs[11].RemoteSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].PretokMin,lo:=5198,hi:=5199); |  | 99:CrpalkeGrfs[12].SetAutomatic:=Bit_0; | 99:CrpalkeGrfs[11].RemoteSetupMode1:=Word_01; |  |  | 5199:CrpalkeGrfs[11].PretokMin:=Real_0;
mind_bool[100]:=CrpalkeGrfs[12].SetConstFreqMode; | mind[100]:=CrpalkeGrfs[11].StatusCrpalke; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].PretokTrenutni,lo:=5200,hi:=5201); |  | 100:CrpalkeGrfs[12].SetConstFreqMode:=Bit_0; | 100:CrpalkeGrfs[11].StatusCrpalke:=Byte_0; |  |  | 5201:CrpalkeGrfs[11].PretokTrenutni:=Real_0;
mind_bool[101]:=CrpalkeGrfs[12].SetConstPress; | mind[101]:=CrpalkeGrfs[11].StatusMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].PritiskMax,lo:=5202,hi:=5203); |  | 101:CrpalkeGrfs[12].SetConstPress:=Bit_0; | 101:CrpalkeGrfs[11].StatusMode1:=Word_01; |  |  | 5203:CrpalkeGrfs[11].PritiskMax:=Real_0;
mind_bool[102]:=CrpalkeGrfs[12].SetLocalMode; | mind[102]:=CrpalkeGrfs[11].StatusMode1co; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].PritiskTrenutni,lo:=5204,hi:=5205); |  | 102:CrpalkeGrfs[12].SetLocalMode:=Bit_0; | 102:CrpalkeGrfs[11].StatusMode1co:=Byte_0; |  |  | 5205:CrpalkeGrfs[11].PritiskTrenutni:=Real_0;
mind_bool[103]:=CrpalkeGrfs[12].SetMaxRunMode; | mind[103]:=CrpalkeGrfs[11].StatusMode1op; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].ReferencaMotorjaHzV,lo:=5206,hi:=5207); |  | 103:CrpalkeGrfs[12].SetMaxRunMode:=Bit_0; | 103:CrpalkeGrfs[11].StatusMode1op:=Byte_0; |  |  | 5207:CrpalkeGrfs[11].ReferencaMotorjaHzV:=Real_0;
mind_bool[104]:=CrpalkeGrfs[12].SetMinRunMode; | mind[104]:=CrpalkeGrfs[11].StatusMode2; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].ReferencaRemote,lo:=5208,hi:=5209); |  | 104:CrpalkeGrfs[12].SetMinRunMode:=Bit_0; | 104:CrpalkeGrfs[11].StatusMode2:=Word_01; |  |  | 5209:CrpalkeGrfs[11].ReferencaRemote:=Real_0;
mind_bool[105]:=CrpalkeGrfs[12].SetPropPress; | mind[105]:=CrpalkeGrfs[11].StatusMode3; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].StevecUr2h,lo:=5210,hi:=5211); |  | 105:CrpalkeGrfs[12].SetPropPress:=Bit_0; | 105:CrpalkeGrfs[11].StatusMode3:=Word_01; |  |  | 5211:CrpalkeGrfs[11].StevecUr2h:=Real_0;
mind_bool[106]:=CrpalkeGrfs[12].SetReference; | mind[106]:=CrpalkeGrfs[12].AlarmActiveCode; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].SystemFeedback,lo:=5212,hi:=5213); |  | 106:CrpalkeGrfs[12].SetReference:=Bit_0; | 106:CrpalkeGrfs[12].AlarmActiveCode:=Word_01; |  |  | 5213:CrpalkeGrfs[11].SystemFeedback:=Real_0;
mind_bool[107]:=CrpalkeGrfs[12].SetRemoteMode; | mind[107]:=CrpalkeGrfs[12].AlarmCodeLog1; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].SystemReference,lo:=5214,hi:=5215); |  | 107:CrpalkeGrfs[12].SetRemoteMode:=Bit_0; | 107:CrpalkeGrfs[12].AlarmCodeLog1:=Word_01; |  |  | 5215:CrpalkeGrfs[11].SystemReference:=Real_0;
mind_bool[108]:=CrpalkeGrfs[12].SetTwinModeAlt; | mind[108]:=CrpalkeGrfs[12].AlarmCodeLog2; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].TemperaturaMotorja,lo:=5216,hi:=5217); |  | 108:CrpalkeGrfs[12].SetTwinModeAlt:=Bit_0; | 108:CrpalkeGrfs[12].AlarmCodeLog2:=Word_01; |  |  | 5217:CrpalkeGrfs[11].TemperaturaMotorja:=Real_0;
mind_bool[109]:=CrpalkeGrfs[12].SetTwinModeSpare; | mind[109]:=CrpalkeGrfs[12].AlarmCodeLog3; |  |  | Read_Real(rVar:=CrpalkeGrfs[11].UreXC200,lo:=5218,hi:=5219); |  | 109:CrpalkeGrfs[12].SetTwinModeSpare:=Bit_0; | 109:CrpalkeGrfs[12].AlarmCodeLog3:=Word_01; |  |  | 5219:CrpalkeGrfs[11].UreXC200:=Real_0;
mind_bool[110]:=CrpalkeGrfs[12].SetTwinModeSync; | mind[110]:=CrpalkeGrfs[12].AlarmCodeLog4; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].DeltaSetPoint,lo:=5220,hi:=5221); |  | 110:CrpalkeGrfs[12].SetTwinModeSync:=Bit_0; | 110:CrpalkeGrfs[12].AlarmCodeLog4:=Word_01; |  |  | 5221:CrpalkeGrfs[12].DeltaSetPoint:=Real_0;
mind_bool[111]:=CrpalkeGrfs[12].Start; | mind[111]:=CrpalkeGrfs[12].AlarmCodeLog5; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].EnergijaPoraba,lo:=5222,hi:=5223); |  | 111:CrpalkeGrfs[12].Start:=Bit_0; | 111:CrpalkeGrfs[12].AlarmCodeLog5:=Word_01; |  |  | 5223:CrpalkeGrfs[12].EnergijaPoraba:=Real_0;
mind_bool[112]:=CrpalkeGrfs[12].Stop; | mind[112]:=CrpalkeGrfs[12].AlarmGroupXVH[0]; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].FrekPretvornikDCNapetost,lo:=5224,hi:=5225); |  | 112:CrpalkeGrfs[12].Stop:=Bit_0; | 112:CrpalkeGrfs[12].AlarmGroupXVH[0]:=Word_01; |  |  | 5225:CrpalkeGrfs[12].FrekPretvornikDCNapetost:=Real_0;
mind_bool[113]:=CrpalkeGrfs[13].AlarmAktiven; | mind[113]:=CrpalkeGrfs[12].AlarmGroupXVH[10]; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].FrekPretvornikDCTok,lo:=5226,hi:=5227); |  | 113:CrpalkeGrfs[13].AlarmAktiven:=Bit_0; | 113:CrpalkeGrfs[12].AlarmGroupXVH[10]:=Word_01; |  |  | 5227:CrpalkeGrfs[12].FrekPretvornikDCTok:=Real_0;
mind_bool[114]:=CrpalkeGrfs[13].Deluje; | mind[114]:=CrpalkeGrfs[12].AlarmGroupXVH[11]; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].FreqMax,lo:=5228,hi:=5229); |  | 114:CrpalkeGrfs[13].Deluje:=Bit_0; | 114:CrpalkeGrfs[12].AlarmGroupXVH[11]:=Word_01; |  |  | 5229:CrpalkeGrfs[12].FreqMax:=Real_0;
mind_bool[115]:=CrpalkeGrfs[13].LocalMode; | mind[115]:=CrpalkeGrfs[12].AlarmGroupXVH[12]; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].FreqMin,lo:=5230,hi:=5231); |  | 115:CrpalkeGrfs[13].LocalMode:=Bit_0; | 115:CrpalkeGrfs[12].AlarmGroupXVH[12]:=Word_01; |  |  | 5231:CrpalkeGrfs[12].FreqMin:=Real_0;
mind_bool[116]:=CrpalkeGrfs[13].RemoteON; | mind[116]:=CrpalkeGrfs[12].AlarmGroupXVH[13]; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].FreqUpper,lo:=5232,hi:=5233); |  | 116:CrpalkeGrfs[13].RemoteON:=Bit_0; | 116:CrpalkeGrfs[12].AlarmGroupXVH[13]:=Word_01; |  |  | 5233:CrpalkeGrfs[12].FreqUpper:=Real_0;
mind_bool[117]:=CrpalkeGrfs[13].Reset2handkWhValues; | mind[117]:=CrpalkeGrfs[12].AlarmGroupXVH[14]; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].MocMax,lo:=5234,hi:=5235); |  | 117:CrpalkeGrfs[13].Reset2handkWhValues:=Bit_0; | 117:CrpalkeGrfs[12].AlarmGroupXVH[14]:=Word_01; |  |  | 5235:CrpalkeGrfs[12].MocMax:=Real_0;
mind_bool[118]:=CrpalkeGrfs[13].ResetAlarm; | mind[118]:=CrpalkeGrfs[12].AlarmGroupXVH[15]; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].MocTrenutna,lo:=5236,hi:=5237); |  | 118:CrpalkeGrfs[13].ResetAlarm:=Bit_0; | 118:CrpalkeGrfs[12].AlarmGroupXVH[15]:=Word_01; |  |  | 5237:CrpalkeGrfs[12].MocTrenutna:=Real_0;
mind_bool[119]:=CrpalkeGrfs[13].ResetAlarmLog; | mind[119]:=CrpalkeGrfs[12].AlarmGroupXVH[16]; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].MotorHitrost,lo:=5238,hi:=5239); |  | 119:CrpalkeGrfs[13].ResetAlarmLog:=Bit_0; | 119:CrpalkeGrfs[12].AlarmGroupXVH[16]:=Word_01; |  |  | 5239:CrpalkeGrfs[12].MotorHitrost:=Real_0;
mind_bool[120]:=CrpalkeGrfs[13].ResetDevice; | mind[120]:=CrpalkeGrfs[12].AlarmGroupXVH[1]; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].MotorTok,lo:=5240,hi:=5241); |  | 120:CrpalkeGrfs[13].ResetDevice:=Bit_0; | 120:CrpalkeGrfs[12].AlarmGroupXVH[1]:=Word_01; |  |  | 5241:CrpalkeGrfs[12].MotorTok:=Real_0;
mind_bool[121]:=CrpalkeGrfs[13].SetAutomatic; | mind[121]:=CrpalkeGrfs[12].AlarmGroupXVH[2]; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].NapajanjeTok,lo:=5242,hi:=5243); |  | 121:CrpalkeGrfs[13].SetAutomatic:=Bit_0; | 121:CrpalkeGrfs[12].AlarmGroupXVH[2]:=Word_01; |  |  | 5243:CrpalkeGrfs[12].NapajanjeTok:=Real_0;
mind_bool[122]:=CrpalkeGrfs[13].SetConstFreqMode; | mind[122]:=CrpalkeGrfs[12].AlarmGroupXVH[3]; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].NastavitevLokalna,lo:=5244,hi:=5245); |  | 122:CrpalkeGrfs[13].SetConstFreqMode:=Bit_0; | 122:CrpalkeGrfs[12].AlarmGroupXVH[3]:=Word_01; |  |  | 5245:CrpalkeGrfs[12].NastavitevLokalna:=Real_0;
mind_bool[123]:=CrpalkeGrfs[13].SetConstPress; | mind[123]:=CrpalkeGrfs[12].AlarmGroupXVH[4]; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].NastavitevTrenutna,lo:=5246,hi:=5247); |  | 123:CrpalkeGrfs[13].SetConstPress:=Bit_0; | 123:CrpalkeGrfs[12].AlarmGroupXVH[4]:=Word_01; |  |  | 5247:CrpalkeGrfs[12].NastavitevTrenutna:=Real_0;
mind_bool[124]:=CrpalkeGrfs[13].SetLocalMode; | mind[124]:=CrpalkeGrfs[12].AlarmGroupXVH[5]; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].PretokMax,lo:=5248,hi:=5249); |  | 124:CrpalkeGrfs[13].SetLocalMode:=Bit_0; | 124:CrpalkeGrfs[12].AlarmGroupXVH[5]:=Word_01; |  |  | 5249:CrpalkeGrfs[12].PretokMax:=Real_0;
mind_bool[125]:=CrpalkeGrfs[13].SetMaxRunMode; | mind[125]:=CrpalkeGrfs[12].AlarmGroupXVH[6]; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].PretokMin,lo:=5250,hi:=5251); |  | 125:CrpalkeGrfs[13].SetMaxRunMode:=Bit_0; | 125:CrpalkeGrfs[12].AlarmGroupXVH[6]:=Word_01; |  |  | 5251:CrpalkeGrfs[12].PretokMin:=Real_0;
mind_bool[126]:=CrpalkeGrfs[13].SetMinRunMode; | mind[126]:=CrpalkeGrfs[12].AlarmGroupXVH[7]; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].PretokTrenutni,lo:=5252,hi:=5253); |  | 126:CrpalkeGrfs[13].SetMinRunMode:=Bit_0; | 126:CrpalkeGrfs[12].AlarmGroupXVH[7]:=Word_01; |  |  | 5253:CrpalkeGrfs[12].PretokTrenutni:=Real_0;
mind_bool[127]:=CrpalkeGrfs[13].SetPropPress; | mind[127]:=CrpalkeGrfs[12].AlarmGroupXVH[8]; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].PritiskMax,lo:=5254,hi:=5255); |  | 127:CrpalkeGrfs[13].SetPropPress:=Bit_0; | 127:CrpalkeGrfs[12].AlarmGroupXVH[8]:=Word_01; |  |  | 5255:CrpalkeGrfs[12].PritiskMax:=Real_0;
mind_bool[128]:=CrpalkeGrfs[13].SetReference; | mind[128]:=CrpalkeGrfs[12].AlarmGroupXVH[9]; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].PritiskTrenutni,lo:=5256,hi:=5257); |  | 128:CrpalkeGrfs[13].SetReference:=Bit_0; | 128:CrpalkeGrfs[12].AlarmGroupXVH[9]:=Word_01; |  |  | 5257:CrpalkeGrfs[12].PritiskTrenutni:=Real_0;
mind_bool[129]:=CrpalkeGrfs[13].SetRemoteMode; | mind[129]:=CrpalkeGrfs[12].AlarmQSD1; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].ReferencaMotorjaHzV,lo:=5258,hi:=5259); |  | 129:CrpalkeGrfs[13].SetRemoteMode:=Bit_0; | 129:CrpalkeGrfs[12].AlarmQSD1:=Word_01; |  |  | 5259:CrpalkeGrfs[12].ReferencaMotorjaHzV:=Real_0;
mind_bool[130]:=CrpalkeGrfs[13].SetTwinModeAlt; | mind[130]:=CrpalkeGrfs[12].AlarmQSD2; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].ReferencaRemote,lo:=5260,hi:=5261); |  | 130:CrpalkeGrfs[13].SetTwinModeAlt:=Bit_0; | 130:CrpalkeGrfs[12].AlarmQSD2:=Word_01; |  |  | 5261:CrpalkeGrfs[12].ReferencaRemote:=Real_0;
mind_bool[131]:=CrpalkeGrfs[13].SetTwinModeSpare; | mind[131]:=CrpalkeGrfs[12].AlarmStart1; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].StevecUr2h,lo:=5262,hi:=5263); |  | 131:CrpalkeGrfs[13].SetTwinModeSpare:=Bit_0; | 131:CrpalkeGrfs[12].AlarmStart1:=Word_01; |  |  | 5263:CrpalkeGrfs[12].StevecUr2h:=Real_0;
mind_bool[132]:=CrpalkeGrfs[13].SetTwinModeSync; | mind[132]:=CrpalkeGrfs[12].AlarmStart2; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].SystemFeedback,lo:=5264,hi:=5265); |  | 132:CrpalkeGrfs[13].SetTwinModeSync:=Bit_0; | 132:CrpalkeGrfs[12].AlarmStart2:=Word_01; |  |  | 5265:CrpalkeGrfs[12].SystemFeedback:=Real_0;
mind_bool[133]:=CrpalkeGrfs[13].Start; | mind[133]:=CrpalkeGrfs[12].AlarmStop1; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].SystemReference,lo:=5266,hi:=5267); |  | 133:CrpalkeGrfs[13].Start:=Bit_0; | 133:CrpalkeGrfs[12].AlarmStop1:=Word_01; |  |  | 5267:CrpalkeGrfs[12].SystemReference:=Real_0;
mind_bool[134]:=CrpalkeGrfs[13].Stop; | mind[134]:=CrpalkeGrfs[12].AlarmStop2; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].TemperaturaMotorja,lo:=5268,hi:=5269); |  | 134:CrpalkeGrfs[13].Stop:=Bit_0; | 134:CrpalkeGrfs[12].AlarmStop2:=Word_01; |  |  | 5269:CrpalkeGrfs[12].TemperaturaMotorja:=Real_0;
mind_bool[135]:=CrpalkeGrfs[14].AlarmAktiven; | mind[135]:=CrpalkeGrfs[12].AlarmStop3; |  |  | Read_Real(rVar:=CrpalkeGrfs[12].UreXC200,lo:=5270,hi:=5271); |  | 135:CrpalkeGrfs[14].AlarmAktiven:=Bit_0; | 135:CrpalkeGrfs[12].AlarmStop3:=Word_01; |  |  | 5271:CrpalkeGrfs[12].UreXC200:=Real_0;
mind_bool[136]:=CrpalkeGrfs[14].Deluje; | mind[136]:=CrpalkeGrfs[12].AlarmSurv1; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].DeltaSetPoint,lo:=5272,hi:=5273); |  | 136:CrpalkeGrfs[14].Deluje:=Bit_0; | 136:CrpalkeGrfs[12].AlarmSurv1:=Word_01; |  |  | 5273:CrpalkeGrfs[13].DeltaSetPoint:=Real_0;
mind_bool[137]:=CrpalkeGrfs[14].LocalMode; | mind[137]:=CrpalkeGrfs[12].AlarmSurv2; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].EnergijaPoraba,lo:=5274,hi:=5275); |  | 137:CrpalkeGrfs[14].LocalMode:=Bit_0; | 137:CrpalkeGrfs[12].AlarmSurv2:=Word_01; |  |  | 5275:CrpalkeGrfs[13].EnergijaPoraba:=Real_0;
mind_bool[138]:=CrpalkeGrfs[14].RemoteON; | mind[138]:=CrpalkeGrfs[12].ControlSource; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].FrekPretvornikDCNapetost,lo:=5276,hi:=5277); |  | 138:CrpalkeGrfs[14].RemoteON:=Bit_0; | 138:CrpalkeGrfs[12].ControlSource:=Word_01; |  |  | 5277:CrpalkeGrfs[13].FrekPretvornikDCNapetost:=Real_0;
mind_bool[139]:=CrpalkeGrfs[14].Reset2handkWhValues; | mind[139]:=CrpalkeGrfs[12].ExternInputSetup; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].FrekPretvornikDCTok,lo:=5278,hi:=5279); |  | 139:CrpalkeGrfs[14].Reset2handkWhValues:=Bit_0; | 139:CrpalkeGrfs[12].ExternInputSetup:=Word_01; |  |  | 5279:CrpalkeGrfs[13].FrekPretvornikDCTok:=Real_0;
mind_bool[140]:=CrpalkeGrfs[14].ResetAlarm; | mind[140]:=CrpalkeGrfs[12].ExternInputsStatus; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].FreqMax,lo:=5280,hi:=5281); |  | 140:CrpalkeGrfs[14].ResetAlarm:=Bit_0; | 140:CrpalkeGrfs[12].ExternInputsStatus:=Word_01; |  |  | 5281:CrpalkeGrfs[13].FreqMax:=Real_0;
mind_bool[141]:=CrpalkeGrfs[14].ResetAlarmLog; | mind[141]:=CrpalkeGrfs[12].LocalSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].FreqMin,lo:=5282,hi:=5283); |  | 141:CrpalkeGrfs[14].ResetAlarmLog:=Bit_0; | 141:CrpalkeGrfs[12].LocalSetupMode1:=Word_01; |  |  | 5283:CrpalkeGrfs[13].FreqMin:=Real_0;
mind_bool[142]:=CrpalkeGrfs[14].ResetDevice; | mind[142]:=CrpalkeGrfs[12].PreklopkaMode; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].FreqUpper,lo:=5284,hi:=5285); |  | 142:CrpalkeGrfs[14].ResetDevice:=Bit_0; | 142:CrpalkeGrfs[12].PreklopkaMode:=Word_01; |  |  | 5285:CrpalkeGrfs[13].FreqUpper:=Real_0;
mind_bool[143]:=CrpalkeGrfs[14].SetAutomatic; | mind[143]:=CrpalkeGrfs[12].Relay1setup; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].MocMax,lo:=5286,hi:=5287); |  | 143:CrpalkeGrfs[14].SetAutomatic:=Bit_0; | 143:CrpalkeGrfs[12].Relay1setup:=Word_01; |  |  | 5287:CrpalkeGrfs[13].MocMax:=Real_0;
mind_bool[144]:=CrpalkeGrfs[14].SetConstFreqMode; | mind[144]:=CrpalkeGrfs[12].RemoteSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].MocTrenutna,lo:=5288,hi:=5289); |  | 144:CrpalkeGrfs[14].SetConstFreqMode:=Bit_0; | 144:CrpalkeGrfs[12].RemoteSetupMode1:=Word_01; |  |  | 5289:CrpalkeGrfs[13].MocTrenutna:=Real_0;
mind_bool[145]:=CrpalkeGrfs[14].SetConstPress; | mind[145]:=CrpalkeGrfs[12].StatusCrpalke; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].MotorHitrost,lo:=5290,hi:=5291); |  | 145:CrpalkeGrfs[14].SetConstPress:=Bit_0; | 145:CrpalkeGrfs[12].StatusCrpalke:=Byte_0; |  |  | 5291:CrpalkeGrfs[13].MotorHitrost:=Real_0;
mind_bool[146]:=CrpalkeGrfs[14].SetLocalMode; | mind[146]:=CrpalkeGrfs[12].StatusMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].MotorTok,lo:=5292,hi:=5293); |  | 146:CrpalkeGrfs[14].SetLocalMode:=Bit_0; | 146:CrpalkeGrfs[12].StatusMode1:=Word_01; |  |  | 5293:CrpalkeGrfs[13].MotorTok:=Real_0;
mind_bool[147]:=CrpalkeGrfs[14].SetMaxRunMode; | mind[147]:=CrpalkeGrfs[12].StatusMode1co; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].NapajanjeTok,lo:=5294,hi:=5295); |  | 147:CrpalkeGrfs[14].SetMaxRunMode:=Bit_0; | 147:CrpalkeGrfs[12].StatusMode1co:=Byte_0; |  |  | 5295:CrpalkeGrfs[13].NapajanjeTok:=Real_0;
mind_bool[148]:=CrpalkeGrfs[14].SetMinRunMode; | mind[148]:=CrpalkeGrfs[12].StatusMode1op; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].NastavitevLokalna,lo:=5296,hi:=5297); |  | 148:CrpalkeGrfs[14].SetMinRunMode:=Bit_0; | 148:CrpalkeGrfs[12].StatusMode1op:=Byte_0; |  |  | 5297:CrpalkeGrfs[13].NastavitevLokalna:=Real_0;
mind_bool[149]:=CrpalkeGrfs[14].SetPropPress; | mind[149]:=CrpalkeGrfs[12].StatusMode2; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].NastavitevTrenutna,lo:=5298,hi:=5299); |  | 149:CrpalkeGrfs[14].SetPropPress:=Bit_0; | 149:CrpalkeGrfs[12].StatusMode2:=Word_01; |  |  | 5299:CrpalkeGrfs[13].NastavitevTrenutna:=Real_0;
mind_bool[150]:=CrpalkeGrfs[14].SetReference; | mind[150]:=CrpalkeGrfs[12].StatusMode3; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].PretokMax,lo:=5300,hi:=5301); |  | 150:CrpalkeGrfs[14].SetReference:=Bit_0; | 150:CrpalkeGrfs[12].StatusMode3:=Word_01; |  |  | 5301:CrpalkeGrfs[13].PretokMax:=Real_0;
mind_bool[151]:=CrpalkeGrfs[14].SetRemoteMode; | mind[151]:=CrpalkeGrfs[13].AlarmActiveCode; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].PretokMin,lo:=5302,hi:=5303); |  | 151:CrpalkeGrfs[14].SetRemoteMode:=Bit_0; | 151:CrpalkeGrfs[13].AlarmActiveCode:=Word_01; |  |  | 5303:CrpalkeGrfs[13].PretokMin:=Real_0;
mind_bool[152]:=CrpalkeGrfs[14].SetTwinModeAlt; | mind[152]:=CrpalkeGrfs[13].AlarmCodeLog1; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].PretokTrenutni,lo:=5304,hi:=5305); |  | 152:CrpalkeGrfs[14].SetTwinModeAlt:=Bit_0; | 152:CrpalkeGrfs[13].AlarmCodeLog1:=Word_01; |  |  | 5305:CrpalkeGrfs[13].PretokTrenutni:=Real_0;
mind_bool[153]:=CrpalkeGrfs[14].SetTwinModeSpare; | mind[153]:=CrpalkeGrfs[13].AlarmCodeLog2; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].PritiskMax,lo:=5306,hi:=5307); |  | 153:CrpalkeGrfs[14].SetTwinModeSpare:=Bit_0; | 153:CrpalkeGrfs[13].AlarmCodeLog2:=Word_01; |  |  | 5307:CrpalkeGrfs[13].PritiskMax:=Real_0;
mind_bool[154]:=CrpalkeGrfs[14].SetTwinModeSync; | mind[154]:=CrpalkeGrfs[13].AlarmCodeLog3; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].PritiskTrenutni,lo:=5308,hi:=5309); |  | 154:CrpalkeGrfs[14].SetTwinModeSync:=Bit_0; | 154:CrpalkeGrfs[13].AlarmCodeLog3:=Word_01; |  |  | 5309:CrpalkeGrfs[13].PritiskTrenutni:=Real_0;
mind_bool[155]:=CrpalkeGrfs[14].Start; | mind[155]:=CrpalkeGrfs[13].AlarmCodeLog4; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].ReferencaMotorjaHzV,lo:=5310,hi:=5311); |  | 155:CrpalkeGrfs[14].Start:=Bit_0; | 155:CrpalkeGrfs[13].AlarmCodeLog4:=Word_01; |  |  | 5311:CrpalkeGrfs[13].ReferencaMotorjaHzV:=Real_0;
mind_bool[156]:=CrpalkeGrfs[14].Stop; | mind[156]:=CrpalkeGrfs[13].AlarmCodeLog5; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].ReferencaRemote,lo:=5312,hi:=5313); |  | 156:CrpalkeGrfs[14].Stop:=Bit_0; | 156:CrpalkeGrfs[13].AlarmCodeLog5:=Word_01; |  |  | 5313:CrpalkeGrfs[13].ReferencaRemote:=Real_0;
mind_bool[157]:=CrpalkeGrfs[1].AlarmAktiven; | mind[157]:=CrpalkeGrfs[13].AlarmGroupXVH[0]; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].StevecUr2h,lo:=5314,hi:=5315); |  | 157:CrpalkeGrfs[1].AlarmAktiven:=Bit_0; | 157:CrpalkeGrfs[13].AlarmGroupXVH[0]:=Word_01; |  |  | 5315:CrpalkeGrfs[13].StevecUr2h:=Real_0;
mind_bool[158]:=CrpalkeGrfs[1].Deluje; | mind[158]:=CrpalkeGrfs[13].AlarmGroupXVH[10]; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].SystemFeedback,lo:=5316,hi:=5317); |  | 158:CrpalkeGrfs[1].Deluje:=Bit_0; | 158:CrpalkeGrfs[13].AlarmGroupXVH[10]:=Word_01; |  |  | 5317:CrpalkeGrfs[13].SystemFeedback:=Real_0;
mind_bool[159]:=CrpalkeGrfs[1].LocalMode; | mind[159]:=CrpalkeGrfs[13].AlarmGroupXVH[11]; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].SystemReference,lo:=5318,hi:=5319); |  | 159:CrpalkeGrfs[1].LocalMode:=Bit_0; | 159:CrpalkeGrfs[13].AlarmGroupXVH[11]:=Word_01; |  |  | 5319:CrpalkeGrfs[13].SystemReference:=Real_0;
mind_bool[160]:=CrpalkeGrfs[1].RemoteON; | mind[160]:=CrpalkeGrfs[13].AlarmGroupXVH[12]; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].TemperaturaMotorja,lo:=5320,hi:=5321); |  | 160:CrpalkeGrfs[1].RemoteON:=Bit_0; | 160:CrpalkeGrfs[13].AlarmGroupXVH[12]:=Word_01; |  |  | 5321:CrpalkeGrfs[13].TemperaturaMotorja:=Real_0;
mind_bool[161]:=CrpalkeGrfs[1].Reset2handkWhValues; | mind[161]:=CrpalkeGrfs[13].AlarmGroupXVH[13]; |  |  | Read_Real(rVar:=CrpalkeGrfs[13].UreXC200,lo:=5322,hi:=5323); |  | 161:CrpalkeGrfs[1].Reset2handkWhValues:=Bit_0; | 161:CrpalkeGrfs[13].AlarmGroupXVH[13]:=Word_01; |  |  | 5323:CrpalkeGrfs[13].UreXC200:=Real_0;
mind_bool[162]:=CrpalkeGrfs[1].ResetAlarm; | mind[162]:=CrpalkeGrfs[13].AlarmGroupXVH[14]; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].DeltaSetPoint,lo:=5324,hi:=5325); |  | 162:CrpalkeGrfs[1].ResetAlarm:=Bit_0; | 162:CrpalkeGrfs[13].AlarmGroupXVH[14]:=Word_01; |  |  | 5325:CrpalkeGrfs[14].DeltaSetPoint:=Real_0;
mind_bool[163]:=CrpalkeGrfs[1].ResetAlarmLog; | mind[163]:=CrpalkeGrfs[13].AlarmGroupXVH[15]; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].EnergijaPoraba,lo:=5326,hi:=5327); |  | 163:CrpalkeGrfs[1].ResetAlarmLog:=Bit_0; | 163:CrpalkeGrfs[13].AlarmGroupXVH[15]:=Word_01; |  |  | 5327:CrpalkeGrfs[14].EnergijaPoraba:=Real_0;
mind_bool[164]:=CrpalkeGrfs[1].ResetDevice; | mind[164]:=CrpalkeGrfs[13].AlarmGroupXVH[16]; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].FrekPretvornikDCNapetost,lo:=5328,hi:=5329); |  | 164:CrpalkeGrfs[1].ResetDevice:=Bit_0; | 164:CrpalkeGrfs[13].AlarmGroupXVH[16]:=Word_01; |  |  | 5329:CrpalkeGrfs[14].FrekPretvornikDCNapetost:=Real_0;
mind_bool[165]:=CrpalkeGrfs[1].SetAutomatic; | mind[165]:=CrpalkeGrfs[13].AlarmGroupXVH[1]; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].FrekPretvornikDCTok,lo:=5330,hi:=5331); |  | 165:CrpalkeGrfs[1].SetAutomatic:=Bit_0; | 165:CrpalkeGrfs[13].AlarmGroupXVH[1]:=Word_01; |  |  | 5331:CrpalkeGrfs[14].FrekPretvornikDCTok:=Real_0;
mind_bool[166]:=CrpalkeGrfs[1].SetConstFreqMode; | mind[166]:=CrpalkeGrfs[13].AlarmGroupXVH[2]; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].FreqMax,lo:=5332,hi:=5333); |  | 166:CrpalkeGrfs[1].SetConstFreqMode:=Bit_0; | 166:CrpalkeGrfs[13].AlarmGroupXVH[2]:=Word_01; |  |  | 5333:CrpalkeGrfs[14].FreqMax:=Real_0;
mind_bool[167]:=CrpalkeGrfs[1].SetConstPress; | mind[167]:=CrpalkeGrfs[13].AlarmGroupXVH[3]; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].FreqMin,lo:=5334,hi:=5335); |  | 167:CrpalkeGrfs[1].SetConstPress:=Bit_0; | 167:CrpalkeGrfs[13].AlarmGroupXVH[3]:=Word_01; |  |  | 5335:CrpalkeGrfs[14].FreqMin:=Real_0;
mind_bool[168]:=CrpalkeGrfs[1].SetLocalMode; | mind[168]:=CrpalkeGrfs[13].AlarmGroupXVH[4]; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].FreqUpper,lo:=5336,hi:=5337); |  | 168:CrpalkeGrfs[1].SetLocalMode:=Bit_0; | 168:CrpalkeGrfs[13].AlarmGroupXVH[4]:=Word_01; |  |  | 5337:CrpalkeGrfs[14].FreqUpper:=Real_0;
mind_bool[169]:=CrpalkeGrfs[1].SetMaxRunMode; | mind[169]:=CrpalkeGrfs[13].AlarmGroupXVH[5]; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].MocMax,lo:=5338,hi:=5339); |  | 169:CrpalkeGrfs[1].SetMaxRunMode:=Bit_0; | 169:CrpalkeGrfs[13].AlarmGroupXVH[5]:=Word_01; |  |  | 5339:CrpalkeGrfs[14].MocMax:=Real_0;
mind_bool[170]:=CrpalkeGrfs[1].SetMinRunMode; | mind[170]:=CrpalkeGrfs[13].AlarmGroupXVH[6]; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].MocTrenutna,lo:=5340,hi:=5341); |  | 170:CrpalkeGrfs[1].SetMinRunMode:=Bit_0; | 170:CrpalkeGrfs[13].AlarmGroupXVH[6]:=Word_01; |  |  | 5341:CrpalkeGrfs[14].MocTrenutna:=Real_0;
mind_bool[171]:=CrpalkeGrfs[1].SetPropPress; | mind[171]:=CrpalkeGrfs[13].AlarmGroupXVH[7]; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].MotorHitrost,lo:=5342,hi:=5343); |  | 171:CrpalkeGrfs[1].SetPropPress:=Bit_0; | 171:CrpalkeGrfs[13].AlarmGroupXVH[7]:=Word_01; |  |  | 5343:CrpalkeGrfs[14].MotorHitrost:=Real_0;
mind_bool[172]:=CrpalkeGrfs[1].SetReference; | mind[172]:=CrpalkeGrfs[13].AlarmGroupXVH[8]; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].MotorTok,lo:=5344,hi:=5345); |  | 172:CrpalkeGrfs[1].SetReference:=Bit_0; | 172:CrpalkeGrfs[13].AlarmGroupXVH[8]:=Word_01; |  |  | 5345:CrpalkeGrfs[14].MotorTok:=Real_0;
mind_bool[173]:=CrpalkeGrfs[1].SetRemoteMode; | mind[173]:=CrpalkeGrfs[13].AlarmGroupXVH[9]; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].NapajanjeTok,lo:=5346,hi:=5347); |  | 173:CrpalkeGrfs[1].SetRemoteMode:=Bit_0; | 173:CrpalkeGrfs[13].AlarmGroupXVH[9]:=Word_01; |  |  | 5347:CrpalkeGrfs[14].NapajanjeTok:=Real_0;
mind_bool[174]:=CrpalkeGrfs[1].SetTwinModeAlt; | mind[174]:=CrpalkeGrfs[13].AlarmQSD1; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].NastavitevLokalna,lo:=5348,hi:=5349); |  | 174:CrpalkeGrfs[1].SetTwinModeAlt:=Bit_0; | 174:CrpalkeGrfs[13].AlarmQSD1:=Word_01; |  |  | 5349:CrpalkeGrfs[14].NastavitevLokalna:=Real_0;
mind_bool[175]:=CrpalkeGrfs[1].SetTwinModeSpare; | mind[175]:=CrpalkeGrfs[13].AlarmQSD2; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].NastavitevTrenutna,lo:=5350,hi:=5351); |  | 175:CrpalkeGrfs[1].SetTwinModeSpare:=Bit_0; | 175:CrpalkeGrfs[13].AlarmQSD2:=Word_01; |  |  | 5351:CrpalkeGrfs[14].NastavitevTrenutna:=Real_0;
mind_bool[176]:=CrpalkeGrfs[1].SetTwinModeSync; | mind[176]:=CrpalkeGrfs[13].AlarmStart1; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].PretokMax,lo:=5352,hi:=5353); |  | 176:CrpalkeGrfs[1].SetTwinModeSync:=Bit_0; | 176:CrpalkeGrfs[13].AlarmStart1:=Word_01; |  |  | 5353:CrpalkeGrfs[14].PretokMax:=Real_0;
mind_bool[177]:=CrpalkeGrfs[1].Start; | mind[177]:=CrpalkeGrfs[13].AlarmStart2; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].PretokMin,lo:=5354,hi:=5355); |  | 177:CrpalkeGrfs[1].Start:=Bit_0; | 177:CrpalkeGrfs[13].AlarmStart2:=Word_01; |  |  | 5355:CrpalkeGrfs[14].PretokMin:=Real_0;
mind_bool[178]:=CrpalkeGrfs[1].Stop; | mind[178]:=CrpalkeGrfs[13].AlarmStop1; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].PretokTrenutni,lo:=5356,hi:=5357); |  | 178:CrpalkeGrfs[1].Stop:=Bit_0; | 178:CrpalkeGrfs[13].AlarmStop1:=Word_01; |  |  | 5357:CrpalkeGrfs[14].PretokTrenutni:=Real_0;
mind_bool[179]:=CrpalkeGrfs[2].AlarmAktiven; | mind[179]:=CrpalkeGrfs[13].AlarmStop2; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].PritiskMax,lo:=5358,hi:=5359); |  | 179:CrpalkeGrfs[2].AlarmAktiven:=Bit_0; | 179:CrpalkeGrfs[13].AlarmStop2:=Word_01; |  |  | 5359:CrpalkeGrfs[14].PritiskMax:=Real_0;
mind_bool[180]:=CrpalkeGrfs[2].Deluje; | mind[180]:=CrpalkeGrfs[13].AlarmStop3; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].PritiskTrenutni,lo:=5360,hi:=5361); |  | 180:CrpalkeGrfs[2].Deluje:=Bit_0; | 180:CrpalkeGrfs[13].AlarmStop3:=Word_01; |  |  | 5361:CrpalkeGrfs[14].PritiskTrenutni:=Real_0;
mind_bool[181]:=CrpalkeGrfs[2].LocalMode; | mind[181]:=CrpalkeGrfs[13].AlarmSurv1; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].ReferencaMotorjaHzV,lo:=5362,hi:=5363); |  | 181:CrpalkeGrfs[2].LocalMode:=Bit_0; | 181:CrpalkeGrfs[13].AlarmSurv1:=Word_01; |  |  | 5363:CrpalkeGrfs[14].ReferencaMotorjaHzV:=Real_0;
mind_bool[182]:=CrpalkeGrfs[2].RemoteON; | mind[182]:=CrpalkeGrfs[13].AlarmSurv2; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].ReferencaRemote,lo:=5364,hi:=5365); |  | 182:CrpalkeGrfs[2].RemoteON:=Bit_0; | 182:CrpalkeGrfs[13].AlarmSurv2:=Word_01; |  |  | 5365:CrpalkeGrfs[14].ReferencaRemote:=Real_0;
mind_bool[183]:=CrpalkeGrfs[2].Reset2handkWhValues; | mind[183]:=CrpalkeGrfs[13].ControlSource; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].StevecUr2h,lo:=5366,hi:=5367); |  | 183:CrpalkeGrfs[2].Reset2handkWhValues:=Bit_0; | 183:CrpalkeGrfs[13].ControlSource:=Word_01; |  |  | 5367:CrpalkeGrfs[14].StevecUr2h:=Real_0;
mind_bool[184]:=CrpalkeGrfs[2].ResetAlarm; | mind[184]:=CrpalkeGrfs[13].ExternInputSetup; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].SystemFeedback,lo:=5368,hi:=5369); |  | 184:CrpalkeGrfs[2].ResetAlarm:=Bit_0; | 184:CrpalkeGrfs[13].ExternInputSetup:=Word_01; |  |  | 5369:CrpalkeGrfs[14].SystemFeedback:=Real_0;
mind_bool[185]:=CrpalkeGrfs[2].ResetAlarmLog; | mind[185]:=CrpalkeGrfs[13].ExternInputsStatus; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].SystemReference,lo:=5370,hi:=5371); |  | 185:CrpalkeGrfs[2].ResetAlarmLog:=Bit_0; | 185:CrpalkeGrfs[13].ExternInputsStatus:=Word_01; |  |  | 5371:CrpalkeGrfs[14].SystemReference:=Real_0;
mind_bool[186]:=CrpalkeGrfs[2].ResetDevice; | mind[186]:=CrpalkeGrfs[13].LocalSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].TemperaturaMotorja,lo:=5372,hi:=5373); |  | 186:CrpalkeGrfs[2].ResetDevice:=Bit_0; | 186:CrpalkeGrfs[13].LocalSetupMode1:=Word_01; |  |  | 5373:CrpalkeGrfs[14].TemperaturaMotorja:=Real_0;
mind_bool[187]:=CrpalkeGrfs[2].SetAutomatic; | mind[187]:=CrpalkeGrfs[13].PreklopkaMode; |  |  | Read_Real(rVar:=CrpalkeGrfs[14].UreXC200,lo:=5374,hi:=5375); |  | 187:CrpalkeGrfs[2].SetAutomatic:=Bit_0; | 187:CrpalkeGrfs[13].PreklopkaMode:=Word_01; |  |  | 5375:CrpalkeGrfs[14].UreXC200:=Real_0;
mind_bool[188]:=CrpalkeGrfs[2].SetConstFreqMode; | mind[188]:=CrpalkeGrfs[13].Relay1setup; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].DeltaSetPoint,lo:=5376,hi:=5377); |  | 188:CrpalkeGrfs[2].SetConstFreqMode:=Bit_0; | 188:CrpalkeGrfs[13].Relay1setup:=Word_01; |  |  | 5377:CrpalkeGrfs[1].DeltaSetPoint:=Real_0;
mind_bool[189]:=CrpalkeGrfs[2].SetConstPress; | mind[189]:=CrpalkeGrfs[13].RemoteSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].EnergijaPoraba,lo:=5378,hi:=5379); |  | 189:CrpalkeGrfs[2].SetConstPress:=Bit_0; | 189:CrpalkeGrfs[13].RemoteSetupMode1:=Word_01; |  |  | 5379:CrpalkeGrfs[1].EnergijaPoraba:=Real_0;
mind_bool[190]:=CrpalkeGrfs[2].SetLocalMode; | mind[190]:=CrpalkeGrfs[13].StatusCrpalke; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].FrekPretvornikDCNapetost,lo:=5380,hi:=5381); |  | 190:CrpalkeGrfs[2].SetLocalMode:=Bit_0; | 190:CrpalkeGrfs[13].StatusCrpalke:=Byte_0; |  |  | 5381:CrpalkeGrfs[1].FrekPretvornikDCNapetost:=Real_0;
mind_bool[191]:=CrpalkeGrfs[2].SetMaxRunMode; | mind[191]:=CrpalkeGrfs[13].StatusMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].FrekPretvornikDCTok,lo:=5382,hi:=5383); |  | 191:CrpalkeGrfs[2].SetMaxRunMode:=Bit_0; | 191:CrpalkeGrfs[13].StatusMode1:=Word_01; |  |  | 5383:CrpalkeGrfs[1].FrekPretvornikDCTok:=Real_0;
mind_bool[192]:=CrpalkeGrfs[2].SetMinRunMode; | mind[192]:=CrpalkeGrfs[13].StatusMode1co; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].FreqMax,lo:=5384,hi:=5385); |  | 192:CrpalkeGrfs[2].SetMinRunMode:=Bit_0; | 192:CrpalkeGrfs[13].StatusMode1co:=Byte_0; |  |  | 5385:CrpalkeGrfs[1].FreqMax:=Real_0;
mind_bool[193]:=CrpalkeGrfs[2].SetPropPress; | mind[193]:=CrpalkeGrfs[13].StatusMode1op; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].FreqMin,lo:=5386,hi:=5387); |  | 193:CrpalkeGrfs[2].SetPropPress:=Bit_0; | 193:CrpalkeGrfs[13].StatusMode1op:=Byte_0; |  |  | 5387:CrpalkeGrfs[1].FreqMin:=Real_0;
mind_bool[194]:=CrpalkeGrfs[2].SetReference; | mind[194]:=CrpalkeGrfs[13].StatusMode2; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].FreqUpper,lo:=5388,hi:=5389); |  | 194:CrpalkeGrfs[2].SetReference:=Bit_0; | 194:CrpalkeGrfs[13].StatusMode2:=Word_01; |  |  | 5389:CrpalkeGrfs[1].FreqUpper:=Real_0;
mind_bool[195]:=CrpalkeGrfs[2].SetRemoteMode; | mind[195]:=CrpalkeGrfs[13].StatusMode3; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].MocMax,lo:=5390,hi:=5391); |  | 195:CrpalkeGrfs[2].SetRemoteMode:=Bit_0; | 195:CrpalkeGrfs[13].StatusMode3:=Word_01; |  |  | 5391:CrpalkeGrfs[1].MocMax:=Real_0;
mind_bool[196]:=CrpalkeGrfs[2].SetTwinModeAlt; | mind[196]:=CrpalkeGrfs[14].AlarmActiveCode; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].MocTrenutna,lo:=5392,hi:=5393); |  | 196:CrpalkeGrfs[2].SetTwinModeAlt:=Bit_0; | 196:CrpalkeGrfs[14].AlarmActiveCode:=Word_01; |  |  | 5393:CrpalkeGrfs[1].MocTrenutna:=Real_0;
mind_bool[197]:=CrpalkeGrfs[2].SetTwinModeSpare; | mind[197]:=CrpalkeGrfs[14].AlarmCodeLog1; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].MotorHitrost,lo:=5394,hi:=5395); |  | 197:CrpalkeGrfs[2].SetTwinModeSpare:=Bit_0; | 197:CrpalkeGrfs[14].AlarmCodeLog1:=Word_01; |  |  | 5395:CrpalkeGrfs[1].MotorHitrost:=Real_0;
mind_bool[198]:=CrpalkeGrfs[2].SetTwinModeSync; | mind[198]:=CrpalkeGrfs[14].AlarmCodeLog2; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].MotorTok,lo:=5396,hi:=5397); |  | 198:CrpalkeGrfs[2].SetTwinModeSync:=Bit_0; | 198:CrpalkeGrfs[14].AlarmCodeLog2:=Word_01; |  |  | 5397:CrpalkeGrfs[1].MotorTok:=Real_0;
mind_bool[199]:=CrpalkeGrfs[2].Start; | mind[199]:=CrpalkeGrfs[14].AlarmCodeLog3; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].NapajanjeTok,lo:=5398,hi:=5399); |  | 199:CrpalkeGrfs[2].Start:=Bit_0; | 199:CrpalkeGrfs[14].AlarmCodeLog3:=Word_01; |  |  | 5399:CrpalkeGrfs[1].NapajanjeTok:=Real_0;
mind_bool[200]:=CrpalkeGrfs[2].Stop; | mind[200]:=CrpalkeGrfs[14].AlarmCodeLog4; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].NastavitevLokalna,lo:=5400,hi:=5401); |  | 200:CrpalkeGrfs[2].Stop:=Bit_0; | 200:CrpalkeGrfs[14].AlarmCodeLog4:=Word_01; |  |  | 5401:CrpalkeGrfs[1].NastavitevLokalna:=Real_0;
mind_bool[201]:=CrpalkeGrfs[3].AlarmAktiven; | mind[201]:=CrpalkeGrfs[14].AlarmCodeLog5; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].NastavitevTrenutna,lo:=5402,hi:=5403); |  | 201:CrpalkeGrfs[3].AlarmAktiven:=Bit_0; | 201:CrpalkeGrfs[14].AlarmCodeLog5:=Word_01; |  |  | 5403:CrpalkeGrfs[1].NastavitevTrenutna:=Real_0;
mind_bool[202]:=CrpalkeGrfs[3].Deluje; | mind[202]:=CrpalkeGrfs[14].AlarmGroupXVH[0]; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].PretokMax,lo:=5404,hi:=5405); |  | 202:CrpalkeGrfs[3].Deluje:=Bit_0; | 202:CrpalkeGrfs[14].AlarmGroupXVH[0]:=Word_01; |  |  | 5405:CrpalkeGrfs[1].PretokMax:=Real_0;
mind_bool[203]:=CrpalkeGrfs[3].LocalMode; | mind[203]:=CrpalkeGrfs[14].AlarmGroupXVH[10]; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].PretokMin,lo:=5406,hi:=5407); |  | 203:CrpalkeGrfs[3].LocalMode:=Bit_0; | 203:CrpalkeGrfs[14].AlarmGroupXVH[10]:=Word_01; |  |  | 5407:CrpalkeGrfs[1].PretokMin:=Real_0;
mind_bool[204]:=CrpalkeGrfs[3].RemoteON; | mind[204]:=CrpalkeGrfs[14].AlarmGroupXVH[11]; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].PretokTrenutni,lo:=5408,hi:=5409); |  | 204:CrpalkeGrfs[3].RemoteON:=Bit_0; | 204:CrpalkeGrfs[14].AlarmGroupXVH[11]:=Word_01; |  |  | 5409:CrpalkeGrfs[1].PretokTrenutni:=Real_0;
mind_bool[205]:=CrpalkeGrfs[3].Reset2handkWhValues; | mind[205]:=CrpalkeGrfs[14].AlarmGroupXVH[12]; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].PritiskMax,lo:=5410,hi:=5411); |  | 205:CrpalkeGrfs[3].Reset2handkWhValues:=Bit_0; | 205:CrpalkeGrfs[14].AlarmGroupXVH[12]:=Word_01; |  |  | 5411:CrpalkeGrfs[1].PritiskMax:=Real_0;
mind_bool[206]:=CrpalkeGrfs[3].ResetAlarm; | mind[206]:=CrpalkeGrfs[14].AlarmGroupXVH[13]; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].PritiskTrenutni,lo:=5412,hi:=5413); |  | 206:CrpalkeGrfs[3].ResetAlarm:=Bit_0; | 206:CrpalkeGrfs[14].AlarmGroupXVH[13]:=Word_01; |  |  | 5413:CrpalkeGrfs[1].PritiskTrenutni:=Real_0;
mind_bool[207]:=CrpalkeGrfs[3].ResetAlarmLog; | mind[207]:=CrpalkeGrfs[14].AlarmGroupXVH[14]; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].ReferencaMotorjaHzV,lo:=5414,hi:=5415); |  | 207:CrpalkeGrfs[3].ResetAlarmLog:=Bit_0; | 207:CrpalkeGrfs[14].AlarmGroupXVH[14]:=Word_01; |  |  | 5415:CrpalkeGrfs[1].ReferencaMotorjaHzV:=Real_0;
mind_bool[208]:=CrpalkeGrfs[3].ResetDevice; | mind[208]:=CrpalkeGrfs[14].AlarmGroupXVH[15]; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].ReferencaRemote,lo:=5416,hi:=5417); |  | 208:CrpalkeGrfs[3].ResetDevice:=Bit_0; | 208:CrpalkeGrfs[14].AlarmGroupXVH[15]:=Word_01; |  |  | 5417:CrpalkeGrfs[1].ReferencaRemote:=Real_0;
mind_bool[209]:=CrpalkeGrfs[3].SetAutomatic; | mind[209]:=CrpalkeGrfs[14].AlarmGroupXVH[16]; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].StevecUr2h,lo:=5418,hi:=5419); |  | 209:CrpalkeGrfs[3].SetAutomatic:=Bit_0; | 209:CrpalkeGrfs[14].AlarmGroupXVH[16]:=Word_01; |  |  | 5419:CrpalkeGrfs[1].StevecUr2h:=Real_0;
mind_bool[210]:=CrpalkeGrfs[3].SetConstFreqMode; | mind[210]:=CrpalkeGrfs[14].AlarmGroupXVH[1]; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].SystemFeedback,lo:=5420,hi:=5421); |  | 210:CrpalkeGrfs[3].SetConstFreqMode:=Bit_0; | 210:CrpalkeGrfs[14].AlarmGroupXVH[1]:=Word_01; |  |  | 5421:CrpalkeGrfs[1].SystemFeedback:=Real_0;
mind_bool[211]:=CrpalkeGrfs[3].SetConstPress; | mind[211]:=CrpalkeGrfs[14].AlarmGroupXVH[2]; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].SystemReference,lo:=5422,hi:=5423); |  | 211:CrpalkeGrfs[3].SetConstPress:=Bit_0; | 211:CrpalkeGrfs[14].AlarmGroupXVH[2]:=Word_01; |  |  | 5423:CrpalkeGrfs[1].SystemReference:=Real_0;
mind_bool[212]:=CrpalkeGrfs[3].SetLocalMode; | mind[212]:=CrpalkeGrfs[14].AlarmGroupXVH[3]; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].TemperaturaMotorja,lo:=5424,hi:=5425); |  | 212:CrpalkeGrfs[3].SetLocalMode:=Bit_0; | 212:CrpalkeGrfs[14].AlarmGroupXVH[3]:=Word_01; |  |  | 5425:CrpalkeGrfs[1].TemperaturaMotorja:=Real_0;
mind_bool[213]:=CrpalkeGrfs[3].SetMaxRunMode; | mind[213]:=CrpalkeGrfs[14].AlarmGroupXVH[4]; |  |  | Read_Real(rVar:=CrpalkeGrfs[1].UreXC200,lo:=5426,hi:=5427); |  | 213:CrpalkeGrfs[3].SetMaxRunMode:=Bit_0; | 213:CrpalkeGrfs[14].AlarmGroupXVH[4]:=Word_01; |  |  | 5427:CrpalkeGrfs[1].UreXC200:=Real_0;
mind_bool[214]:=CrpalkeGrfs[3].SetMinRunMode; | mind[214]:=CrpalkeGrfs[14].AlarmGroupXVH[5]; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].DeltaSetPoint,lo:=5428,hi:=5429); |  | 214:CrpalkeGrfs[3].SetMinRunMode:=Bit_0; | 214:CrpalkeGrfs[14].AlarmGroupXVH[5]:=Word_01; |  |  | 5429:CrpalkeGrfs[2].DeltaSetPoint:=Real_0;
mind_bool[215]:=CrpalkeGrfs[3].SetPropPress; | mind[215]:=CrpalkeGrfs[14].AlarmGroupXVH[6]; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].EnergijaPoraba,lo:=5430,hi:=5431); |  | 215:CrpalkeGrfs[3].SetPropPress:=Bit_0; | 215:CrpalkeGrfs[14].AlarmGroupXVH[6]:=Word_01; |  |  | 5431:CrpalkeGrfs[2].EnergijaPoraba:=Real_0;
mind_bool[216]:=CrpalkeGrfs[3].SetReference; | mind[216]:=CrpalkeGrfs[14].AlarmGroupXVH[7]; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].FrekPretvornikDCNapetost,lo:=5432,hi:=5433); |  | 216:CrpalkeGrfs[3].SetReference:=Bit_0; | 216:CrpalkeGrfs[14].AlarmGroupXVH[7]:=Word_01; |  |  | 5433:CrpalkeGrfs[2].FrekPretvornikDCNapetost:=Real_0;
mind_bool[217]:=CrpalkeGrfs[3].SetRemoteMode; | mind[217]:=CrpalkeGrfs[14].AlarmGroupXVH[8]; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].FrekPretvornikDCTok,lo:=5434,hi:=5435); |  | 217:CrpalkeGrfs[3].SetRemoteMode:=Bit_0; | 217:CrpalkeGrfs[14].AlarmGroupXVH[8]:=Word_01; |  |  | 5435:CrpalkeGrfs[2].FrekPretvornikDCTok:=Real_0;
mind_bool[218]:=CrpalkeGrfs[3].SetTwinModeAlt; | mind[218]:=CrpalkeGrfs[14].AlarmGroupXVH[9]; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].FreqMax,lo:=5436,hi:=5437); |  | 218:CrpalkeGrfs[3].SetTwinModeAlt:=Bit_0; | 218:CrpalkeGrfs[14].AlarmGroupXVH[9]:=Word_01; |  |  | 5437:CrpalkeGrfs[2].FreqMax:=Real_0;
mind_bool[219]:=CrpalkeGrfs[3].SetTwinModeSpare; | mind[219]:=CrpalkeGrfs[14].AlarmQSD1; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].FreqMin,lo:=5438,hi:=5439); |  | 219:CrpalkeGrfs[3].SetTwinModeSpare:=Bit_0; | 219:CrpalkeGrfs[14].AlarmQSD1:=Word_01; |  |  | 5439:CrpalkeGrfs[2].FreqMin:=Real_0;
mind_bool[220]:=CrpalkeGrfs[3].SetTwinModeSync; | mind[220]:=CrpalkeGrfs[14].AlarmQSD2; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].FreqUpper,lo:=5440,hi:=5441); |  | 220:CrpalkeGrfs[3].SetTwinModeSync:=Bit_0; | 220:CrpalkeGrfs[14].AlarmQSD2:=Word_01; |  |  | 5441:CrpalkeGrfs[2].FreqUpper:=Real_0;
mind_bool[221]:=CrpalkeGrfs[3].Start; | mind[221]:=CrpalkeGrfs[14].AlarmStart1; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].MocMax,lo:=5442,hi:=5443); |  | 221:CrpalkeGrfs[3].Start:=Bit_0; | 221:CrpalkeGrfs[14].AlarmStart1:=Word_01; |  |  | 5443:CrpalkeGrfs[2].MocMax:=Real_0;
mind_bool[222]:=CrpalkeGrfs[3].Stop; | mind[222]:=CrpalkeGrfs[14].AlarmStart2; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].MocTrenutna,lo:=5444,hi:=5445); |  | 222:CrpalkeGrfs[3].Stop:=Bit_0; | 222:CrpalkeGrfs[14].AlarmStart2:=Word_01; |  |  | 5445:CrpalkeGrfs[2].MocTrenutna:=Real_0;
mind_bool[223]:=CrpalkeGrfs[4].AlarmAktiven; | mind[223]:=CrpalkeGrfs[14].AlarmStop1; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].MotorHitrost,lo:=5446,hi:=5447); |  | 223:CrpalkeGrfs[4].AlarmAktiven:=Bit_0; | 223:CrpalkeGrfs[14].AlarmStop1:=Word_01; |  |  | 5447:CrpalkeGrfs[2].MotorHitrost:=Real_0;
mind_bool[224]:=CrpalkeGrfs[4].Deluje; | mind[224]:=CrpalkeGrfs[14].AlarmStop2; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].MotorTok,lo:=5448,hi:=5449); |  | 224:CrpalkeGrfs[4].Deluje:=Bit_0; | 224:CrpalkeGrfs[14].AlarmStop2:=Word_01; |  |  | 5449:CrpalkeGrfs[2].MotorTok:=Real_0;
mind_bool[225]:=CrpalkeGrfs[4].LocalMode; | mind[225]:=CrpalkeGrfs[14].AlarmStop3; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].NapajanjeTok,lo:=5450,hi:=5451); |  | 225:CrpalkeGrfs[4].LocalMode:=Bit_0; | 225:CrpalkeGrfs[14].AlarmStop3:=Word_01; |  |  | 5451:CrpalkeGrfs[2].NapajanjeTok:=Real_0;
mind_bool[226]:=CrpalkeGrfs[4].RemoteON; | mind[226]:=CrpalkeGrfs[14].AlarmSurv1; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].NastavitevLokalna,lo:=5452,hi:=5453); |  | 226:CrpalkeGrfs[4].RemoteON:=Bit_0; | 226:CrpalkeGrfs[14].AlarmSurv1:=Word_01; |  |  | 5453:CrpalkeGrfs[2].NastavitevLokalna:=Real_0;
mind_bool[227]:=CrpalkeGrfs[4].Reset2handkWhValues; | mind[227]:=CrpalkeGrfs[14].AlarmSurv2; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].NastavitevTrenutna,lo:=5454,hi:=5455); |  | 227:CrpalkeGrfs[4].Reset2handkWhValues:=Bit_0; | 227:CrpalkeGrfs[14].AlarmSurv2:=Word_01; |  |  | 5455:CrpalkeGrfs[2].NastavitevTrenutna:=Real_0;
mind_bool[228]:=CrpalkeGrfs[4].ResetAlarm; | mind[228]:=CrpalkeGrfs[14].ControlSource; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].PretokMax,lo:=5456,hi:=5457); |  | 228:CrpalkeGrfs[4].ResetAlarm:=Bit_0; | 228:CrpalkeGrfs[14].ControlSource:=Word_01; |  |  | 5457:CrpalkeGrfs[2].PretokMax:=Real_0;
mind_bool[229]:=CrpalkeGrfs[4].ResetAlarmLog; | mind[229]:=CrpalkeGrfs[14].ExternInputSetup; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].PretokMin,lo:=5458,hi:=5459); |  | 229:CrpalkeGrfs[4].ResetAlarmLog:=Bit_0; | 229:CrpalkeGrfs[14].ExternInputSetup:=Word_01; |  |  | 5459:CrpalkeGrfs[2].PretokMin:=Real_0;
mind_bool[230]:=CrpalkeGrfs[4].ResetDevice; | mind[230]:=CrpalkeGrfs[14].ExternInputsStatus; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].PretokTrenutni,lo:=5460,hi:=5461); |  | 230:CrpalkeGrfs[4].ResetDevice:=Bit_0; | 230:CrpalkeGrfs[14].ExternInputsStatus:=Word_01; |  |  | 5461:CrpalkeGrfs[2].PretokTrenutni:=Real_0;
mind_bool[231]:=CrpalkeGrfs[4].SetAutomatic; | mind[231]:=CrpalkeGrfs[14].LocalSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].PritiskMax,lo:=5462,hi:=5463); |  | 231:CrpalkeGrfs[4].SetAutomatic:=Bit_0; | 231:CrpalkeGrfs[14].LocalSetupMode1:=Word_01; |  |  | 5463:CrpalkeGrfs[2].PritiskMax:=Real_0;
mind_bool[232]:=CrpalkeGrfs[4].SetConstFreqMode; | mind[232]:=CrpalkeGrfs[14].PreklopkaMode; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].PritiskTrenutni,lo:=5464,hi:=5465); |  | 232:CrpalkeGrfs[4].SetConstFreqMode:=Bit_0; | 232:CrpalkeGrfs[14].PreklopkaMode:=Word_01; |  |  | 5465:CrpalkeGrfs[2].PritiskTrenutni:=Real_0;
mind_bool[233]:=CrpalkeGrfs[4].SetConstPress; | mind[233]:=CrpalkeGrfs[14].Relay1setup; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].ReferencaMotorjaHzV,lo:=5466,hi:=5467); |  | 233:CrpalkeGrfs[4].SetConstPress:=Bit_0; | 233:CrpalkeGrfs[14].Relay1setup:=Word_01; |  |  | 5467:CrpalkeGrfs[2].ReferencaMotorjaHzV:=Real_0;
mind_bool[234]:=CrpalkeGrfs[4].SetLocalMode; | mind[234]:=CrpalkeGrfs[14].RemoteSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].ReferencaRemote,lo:=5468,hi:=5469); |  | 234:CrpalkeGrfs[4].SetLocalMode:=Bit_0; | 234:CrpalkeGrfs[14].RemoteSetupMode1:=Word_01; |  |  | 5469:CrpalkeGrfs[2].ReferencaRemote:=Real_0;
mind_bool[235]:=CrpalkeGrfs[4].SetMaxRunMode; | mind[235]:=CrpalkeGrfs[14].StatusCrpalke; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].StevecUr2h,lo:=5470,hi:=5471); |  | 235:CrpalkeGrfs[4].SetMaxRunMode:=Bit_0; | 235:CrpalkeGrfs[14].StatusCrpalke:=Byte_0; |  |  | 5471:CrpalkeGrfs[2].StevecUr2h:=Real_0;
mind_bool[236]:=CrpalkeGrfs[4].SetMinRunMode; | mind[236]:=CrpalkeGrfs[14].StatusMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].SystemFeedback,lo:=5472,hi:=5473); |  | 236:CrpalkeGrfs[4].SetMinRunMode:=Bit_0; | 236:CrpalkeGrfs[14].StatusMode1:=Word_01; |  |  | 5473:CrpalkeGrfs[2].SystemFeedback:=Real_0;
mind_bool[237]:=CrpalkeGrfs[4].SetPropPress; | mind[237]:=CrpalkeGrfs[14].StatusMode1co; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].SystemReference,lo:=5474,hi:=5475); |  | 237:CrpalkeGrfs[4].SetPropPress:=Bit_0; | 237:CrpalkeGrfs[14].StatusMode1co:=Byte_0; |  |  | 5475:CrpalkeGrfs[2].SystemReference:=Real_0;
mind_bool[238]:=CrpalkeGrfs[4].SetReference; | mind[238]:=CrpalkeGrfs[14].StatusMode1op; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].TemperaturaMotorja,lo:=5476,hi:=5477); |  | 238:CrpalkeGrfs[4].SetReference:=Bit_0; | 238:CrpalkeGrfs[14].StatusMode1op:=Byte_0; |  |  | 5477:CrpalkeGrfs[2].TemperaturaMotorja:=Real_0;
mind_bool[239]:=CrpalkeGrfs[4].SetRemoteMode; | mind[239]:=CrpalkeGrfs[14].StatusMode2; |  |  | Read_Real(rVar:=CrpalkeGrfs[2].UreXC200,lo:=5478,hi:=5479); |  | 239:CrpalkeGrfs[4].SetRemoteMode:=Bit_0; | 239:CrpalkeGrfs[14].StatusMode2:=Word_01; |  |  | 5479:CrpalkeGrfs[2].UreXC200:=Real_0;
mind_bool[240]:=CrpalkeGrfs[4].SetTwinModeAlt; | mind[240]:=CrpalkeGrfs[14].StatusMode3; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].DeltaSetPoint,lo:=5480,hi:=5481); |  | 240:CrpalkeGrfs[4].SetTwinModeAlt:=Bit_0; | 240:CrpalkeGrfs[14].StatusMode3:=Word_01; |  |  | 5481:CrpalkeGrfs[3].DeltaSetPoint:=Real_0;
mind_bool[241]:=CrpalkeGrfs[4].SetTwinModeSpare; | mind[241]:=CrpalkeGrfs[1].AlarmActiveCode; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].EnergijaPoraba,lo:=5482,hi:=5483); |  | 241:CrpalkeGrfs[4].SetTwinModeSpare:=Bit_0; | 241:CrpalkeGrfs[1].AlarmActiveCode:=Word_01; |  |  | 5483:CrpalkeGrfs[3].EnergijaPoraba:=Real_0;
mind_bool[242]:=CrpalkeGrfs[4].SetTwinModeSync; | mind[242]:=CrpalkeGrfs[1].AlarmCodeLog1; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].FrekPretvornikDCNapetost,lo:=5484,hi:=5485); |  | 242:CrpalkeGrfs[4].SetTwinModeSync:=Bit_0; | 242:CrpalkeGrfs[1].AlarmCodeLog1:=Word_01; |  |  | 5485:CrpalkeGrfs[3].FrekPretvornikDCNapetost:=Real_0;
mind_bool[243]:=CrpalkeGrfs[4].Start; | mind[243]:=CrpalkeGrfs[1].AlarmCodeLog2; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].FrekPretvornikDCTok,lo:=5486,hi:=5487); |  | 243:CrpalkeGrfs[4].Start:=Bit_0; | 243:CrpalkeGrfs[1].AlarmCodeLog2:=Word_01; |  |  | 5487:CrpalkeGrfs[3].FrekPretvornikDCTok:=Real_0;
mind_bool[244]:=CrpalkeGrfs[4].Stop; | mind[244]:=CrpalkeGrfs[1].AlarmCodeLog3; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].FreqMax,lo:=5488,hi:=5489); |  | 244:CrpalkeGrfs[4].Stop:=Bit_0; | 244:CrpalkeGrfs[1].AlarmCodeLog3:=Word_01; |  |  | 5489:CrpalkeGrfs[3].FreqMax:=Real_0;
mind_bool[245]:=CrpalkeGrfs[5].AlarmAktiven; | mind[245]:=CrpalkeGrfs[1].AlarmCodeLog4; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].FreqMin,lo:=5490,hi:=5491); |  | 245:CrpalkeGrfs[5].AlarmAktiven:=Bit_0; | 245:CrpalkeGrfs[1].AlarmCodeLog4:=Word_01; |  |  | 5491:CrpalkeGrfs[3].FreqMin:=Real_0;
mind_bool[246]:=CrpalkeGrfs[5].Deluje; | mind[246]:=CrpalkeGrfs[1].AlarmCodeLog5; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].FreqUpper,lo:=5492,hi:=5493); |  | 246:CrpalkeGrfs[5].Deluje:=Bit_0; | 246:CrpalkeGrfs[1].AlarmCodeLog5:=Word_01; |  |  | 5493:CrpalkeGrfs[3].FreqUpper:=Real_0;
mind_bool[247]:=CrpalkeGrfs[5].LocalMode; | mind[247]:=CrpalkeGrfs[1].AlarmGroupXVH[0]; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].MocMax,lo:=5494,hi:=5495); |  | 247:CrpalkeGrfs[5].LocalMode:=Bit_0; | 247:CrpalkeGrfs[1].AlarmGroupXVH[0]:=Word_01; |  |  | 5495:CrpalkeGrfs[3].MocMax:=Real_0;
mind_bool[248]:=CrpalkeGrfs[5].RemoteON; | mind[248]:=CrpalkeGrfs[1].AlarmGroupXVH[10]; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].MocTrenutna,lo:=5496,hi:=5497); |  | 248:CrpalkeGrfs[5].RemoteON:=Bit_0; | 248:CrpalkeGrfs[1].AlarmGroupXVH[10]:=Word_01; |  |  | 5497:CrpalkeGrfs[3].MocTrenutna:=Real_0;
mind_bool[249]:=CrpalkeGrfs[5].Reset2handkWhValues; | mind[249]:=CrpalkeGrfs[1].AlarmGroupXVH[11]; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].MotorHitrost,lo:=5498,hi:=5499); |  | 249:CrpalkeGrfs[5].Reset2handkWhValues:=Bit_0; | 249:CrpalkeGrfs[1].AlarmGroupXVH[11]:=Word_01; |  |  | 5499:CrpalkeGrfs[3].MotorHitrost:=Real_0;
mind_bool[250]:=CrpalkeGrfs[5].ResetAlarm; | mind[250]:=CrpalkeGrfs[1].AlarmGroupXVH[12]; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].MotorTok,lo:=5500,hi:=5501); |  | 250:CrpalkeGrfs[5].ResetAlarm:=Bit_0; | 250:CrpalkeGrfs[1].AlarmGroupXVH[12]:=Word_01; |  |  | 5501:CrpalkeGrfs[3].MotorTok:=Real_0;
mind_bool[251]:=CrpalkeGrfs[5].ResetAlarmLog; | mind[251]:=CrpalkeGrfs[1].AlarmGroupXVH[13]; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].NapajanjeTok,lo:=5502,hi:=5503); |  | 251:CrpalkeGrfs[5].ResetAlarmLog:=Bit_0; | 251:CrpalkeGrfs[1].AlarmGroupXVH[13]:=Word_01; |  |  | 5503:CrpalkeGrfs[3].NapajanjeTok:=Real_0;
mind_bool[252]:=CrpalkeGrfs[5].ResetDevice; | mind[252]:=CrpalkeGrfs[1].AlarmGroupXVH[14]; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].NastavitevLokalna,lo:=5504,hi:=5505); |  | 252:CrpalkeGrfs[5].ResetDevice:=Bit_0; | 252:CrpalkeGrfs[1].AlarmGroupXVH[14]:=Word_01; |  |  | 5505:CrpalkeGrfs[3].NastavitevLokalna:=Real_0;
mind_bool[253]:=CrpalkeGrfs[5].SetAutomatic; | mind[253]:=CrpalkeGrfs[1].AlarmGroupXVH[15]; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].NastavitevTrenutna,lo:=5506,hi:=5507); |  | 253:CrpalkeGrfs[5].SetAutomatic:=Bit_0; | 253:CrpalkeGrfs[1].AlarmGroupXVH[15]:=Word_01; |  |  | 5507:CrpalkeGrfs[3].NastavitevTrenutna:=Real_0;
mind_bool[254]:=CrpalkeGrfs[5].SetConstFreqMode; | mind[254]:=CrpalkeGrfs[1].AlarmGroupXVH[16]; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].PretokMax,lo:=5508,hi:=5509); |  | 254:CrpalkeGrfs[5].SetConstFreqMode:=Bit_0; | 254:CrpalkeGrfs[1].AlarmGroupXVH[16]:=Word_01; |  |  | 5509:CrpalkeGrfs[3].PretokMax:=Real_0;
mind_bool[255]:=CrpalkeGrfs[5].SetConstPress; | mind[255]:=CrpalkeGrfs[1].AlarmGroupXVH[1]; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].PretokMin,lo:=5510,hi:=5511); |  | 255:CrpalkeGrfs[5].SetConstPress:=Bit_0; | 255:CrpalkeGrfs[1].AlarmGroupXVH[1]:=Word_01; |  |  | 5511:CrpalkeGrfs[3].PretokMin:=Real_0;
mind_bool[256]:=CrpalkeGrfs[5].SetLocalMode; | mind[256]:=CrpalkeGrfs[1].AlarmGroupXVH[2]; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].PretokTrenutni,lo:=5512,hi:=5513); |  | 256:CrpalkeGrfs[5].SetLocalMode:=Bit_0; | 256:CrpalkeGrfs[1].AlarmGroupXVH[2]:=Word_01; |  |  | 5513:CrpalkeGrfs[3].PretokTrenutni:=Real_0;
mind_bool[257]:=CrpalkeGrfs[5].SetMaxRunMode; | mind[257]:=CrpalkeGrfs[1].AlarmGroupXVH[3]; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].PritiskMax,lo:=5514,hi:=5515); |  | 257:CrpalkeGrfs[5].SetMaxRunMode:=Bit_0; | 257:CrpalkeGrfs[1].AlarmGroupXVH[3]:=Word_01; |  |  | 5515:CrpalkeGrfs[3].PritiskMax:=Real_0;
mind_bool[258]:=CrpalkeGrfs[5].SetMinRunMode; | mind[258]:=CrpalkeGrfs[1].AlarmGroupXVH[4]; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].PritiskTrenutni,lo:=5516,hi:=5517); |  | 258:CrpalkeGrfs[5].SetMinRunMode:=Bit_0; | 258:CrpalkeGrfs[1].AlarmGroupXVH[4]:=Word_01; |  |  | 5517:CrpalkeGrfs[3].PritiskTrenutni:=Real_0;
mind_bool[259]:=CrpalkeGrfs[5].SetPropPress; | mind[259]:=CrpalkeGrfs[1].AlarmGroupXVH[5]; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].ReferencaMotorjaHzV,lo:=5518,hi:=5519); |  | 259:CrpalkeGrfs[5].SetPropPress:=Bit_0; | 259:CrpalkeGrfs[1].AlarmGroupXVH[5]:=Word_01; |  |  | 5519:CrpalkeGrfs[3].ReferencaMotorjaHzV:=Real_0;
mind_bool[260]:=CrpalkeGrfs[5].SetReference; | mind[260]:=CrpalkeGrfs[1].AlarmGroupXVH[6]; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].ReferencaRemote,lo:=5520,hi:=5521); |  | 260:CrpalkeGrfs[5].SetReference:=Bit_0; | 260:CrpalkeGrfs[1].AlarmGroupXVH[6]:=Word_01; |  |  | 5521:CrpalkeGrfs[3].ReferencaRemote:=Real_0;
mind_bool[261]:=CrpalkeGrfs[5].SetRemoteMode; | mind[261]:=CrpalkeGrfs[1].AlarmGroupXVH[7]; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].StevecUr2h,lo:=5522,hi:=5523); |  | 261:CrpalkeGrfs[5].SetRemoteMode:=Bit_0; | 261:CrpalkeGrfs[1].AlarmGroupXVH[7]:=Word_01; |  |  | 5523:CrpalkeGrfs[3].StevecUr2h:=Real_0;
mind_bool[262]:=CrpalkeGrfs[5].SetTwinModeAlt; | mind[262]:=CrpalkeGrfs[1].AlarmGroupXVH[8]; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].SystemFeedback,lo:=5524,hi:=5525); |  | 262:CrpalkeGrfs[5].SetTwinModeAlt:=Bit_0; | 262:CrpalkeGrfs[1].AlarmGroupXVH[8]:=Word_01; |  |  | 5525:CrpalkeGrfs[3].SystemFeedback:=Real_0;
mind_bool[263]:=CrpalkeGrfs[5].SetTwinModeSpare; | mind[263]:=CrpalkeGrfs[1].AlarmGroupXVH[9]; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].SystemReference,lo:=5526,hi:=5527); |  | 263:CrpalkeGrfs[5].SetTwinModeSpare:=Bit_0; | 263:CrpalkeGrfs[1].AlarmGroupXVH[9]:=Word_01; |  |  | 5527:CrpalkeGrfs[3].SystemReference:=Real_0;
mind_bool[264]:=CrpalkeGrfs[5].SetTwinModeSync; | mind[264]:=CrpalkeGrfs[1].AlarmQSD1; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].TemperaturaMotorja,lo:=5528,hi:=5529); |  | 264:CrpalkeGrfs[5].SetTwinModeSync:=Bit_0; | 264:CrpalkeGrfs[1].AlarmQSD1:=Word_01; |  |  | 5529:CrpalkeGrfs[3].TemperaturaMotorja:=Real_0;
mind_bool[265]:=CrpalkeGrfs[5].Start; | mind[265]:=CrpalkeGrfs[1].AlarmQSD2; |  |  | Read_Real(rVar:=CrpalkeGrfs[3].UreXC200,lo:=5530,hi:=5531); |  | 265:CrpalkeGrfs[5].Start:=Bit_0; | 265:CrpalkeGrfs[1].AlarmQSD2:=Word_01; |  |  | 5531:CrpalkeGrfs[3].UreXC200:=Real_0;
mind_bool[266]:=CrpalkeGrfs[5].Stop; | mind[266]:=CrpalkeGrfs[1].AlarmStart1; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].DeltaSetPoint,lo:=5532,hi:=5533); |  | 266:CrpalkeGrfs[5].Stop:=Bit_0; | 266:CrpalkeGrfs[1].AlarmStart1:=Word_01; |  |  | 5533:CrpalkeGrfs[4].DeltaSetPoint:=Real_0;
mind_bool[267]:=CrpalkeGrfs[6].AlarmAktiven; | mind[267]:=CrpalkeGrfs[1].AlarmStart2; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].EnergijaPoraba,lo:=5534,hi:=5535); |  | 267:CrpalkeGrfs[6].AlarmAktiven:=Bit_0; | 267:CrpalkeGrfs[1].AlarmStart2:=Word_01; |  |  | 5535:CrpalkeGrfs[4].EnergijaPoraba:=Real_0;
mind_bool[268]:=CrpalkeGrfs[6].Deluje; | mind[268]:=CrpalkeGrfs[1].AlarmStop1; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].FrekPretvornikDCNapetost,lo:=5536,hi:=5537); |  | 268:CrpalkeGrfs[6].Deluje:=Bit_0; | 268:CrpalkeGrfs[1].AlarmStop1:=Word_01; |  |  | 5537:CrpalkeGrfs[4].FrekPretvornikDCNapetost:=Real_0;
mind_bool[269]:=CrpalkeGrfs[6].LocalMode; | mind[269]:=CrpalkeGrfs[1].AlarmStop2; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].FrekPretvornikDCTok,lo:=5538,hi:=5539); |  | 269:CrpalkeGrfs[6].LocalMode:=Bit_0; | 269:CrpalkeGrfs[1].AlarmStop2:=Word_01; |  |  | 5539:CrpalkeGrfs[4].FrekPretvornikDCTok:=Real_0;
mind_bool[270]:=CrpalkeGrfs[6].RemoteON; | mind[270]:=CrpalkeGrfs[1].AlarmStop3; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].FreqMax,lo:=5540,hi:=5541); |  | 270:CrpalkeGrfs[6].RemoteON:=Bit_0; | 270:CrpalkeGrfs[1].AlarmStop3:=Word_01; |  |  | 5541:CrpalkeGrfs[4].FreqMax:=Real_0;
mind_bool[271]:=CrpalkeGrfs[6].Reset2handkWhValues; | mind[271]:=CrpalkeGrfs[1].AlarmSurv1; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].FreqMin,lo:=5542,hi:=5543); |  | 271:CrpalkeGrfs[6].Reset2handkWhValues:=Bit_0; | 271:CrpalkeGrfs[1].AlarmSurv1:=Word_01; |  |  | 5543:CrpalkeGrfs[4].FreqMin:=Real_0;
mind_bool[272]:=CrpalkeGrfs[6].ResetAlarm; | mind[272]:=CrpalkeGrfs[1].AlarmSurv2; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].FreqUpper,lo:=5544,hi:=5545); |  | 272:CrpalkeGrfs[6].ResetAlarm:=Bit_0; | 272:CrpalkeGrfs[1].AlarmSurv2:=Word_01; |  |  | 5545:CrpalkeGrfs[4].FreqUpper:=Real_0;
mind_bool[273]:=CrpalkeGrfs[6].ResetAlarmLog; | mind[273]:=CrpalkeGrfs[1].ControlSource; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].MocMax,lo:=5546,hi:=5547); |  | 273:CrpalkeGrfs[6].ResetAlarmLog:=Bit_0; | 273:CrpalkeGrfs[1].ControlSource:=Word_01; |  |  | 5547:CrpalkeGrfs[4].MocMax:=Real_0;
mind_bool[274]:=CrpalkeGrfs[6].ResetDevice; | mind[274]:=CrpalkeGrfs[1].ExternInputSetup; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].MocTrenutna,lo:=5548,hi:=5549); |  | 274:CrpalkeGrfs[6].ResetDevice:=Bit_0; | 274:CrpalkeGrfs[1].ExternInputSetup:=Word_01; |  |  | 5549:CrpalkeGrfs[4].MocTrenutna:=Real_0;
mind_bool[275]:=CrpalkeGrfs[6].SetAutomatic; | mind[275]:=CrpalkeGrfs[1].ExternInputsStatus; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].MotorHitrost,lo:=5550,hi:=5551); |  | 275:CrpalkeGrfs[6].SetAutomatic:=Bit_0; | 275:CrpalkeGrfs[1].ExternInputsStatus:=Word_01; |  |  | 5551:CrpalkeGrfs[4].MotorHitrost:=Real_0;
mind_bool[276]:=CrpalkeGrfs[6].SetConstFreqMode; | mind[276]:=CrpalkeGrfs[1].LocalSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].MotorTok,lo:=5552,hi:=5553); |  | 276:CrpalkeGrfs[6].SetConstFreqMode:=Bit_0; | 276:CrpalkeGrfs[1].LocalSetupMode1:=Word_01; |  |  | 5553:CrpalkeGrfs[4].MotorTok:=Real_0;
mind_bool[277]:=CrpalkeGrfs[6].SetConstPress; | mind[277]:=CrpalkeGrfs[1].PreklopkaMode; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].NapajanjeTok,lo:=5554,hi:=5555); |  | 277:CrpalkeGrfs[6].SetConstPress:=Bit_0; | 277:CrpalkeGrfs[1].PreklopkaMode:=Word_01; |  |  | 5555:CrpalkeGrfs[4].NapajanjeTok:=Real_0;
mind_bool[278]:=CrpalkeGrfs[6].SetLocalMode; | mind[278]:=CrpalkeGrfs[1].Relay1setup; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].NastavitevLokalna,lo:=5556,hi:=5557); |  | 278:CrpalkeGrfs[6].SetLocalMode:=Bit_0; | 278:CrpalkeGrfs[1].Relay1setup:=Word_01; |  |  | 5557:CrpalkeGrfs[4].NastavitevLokalna:=Real_0;
mind_bool[279]:=CrpalkeGrfs[6].SetMaxRunMode; | mind[279]:=CrpalkeGrfs[1].RemoteSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].NastavitevTrenutna,lo:=5558,hi:=5559); |  | 279:CrpalkeGrfs[6].SetMaxRunMode:=Bit_0; | 279:CrpalkeGrfs[1].RemoteSetupMode1:=Word_01; |  |  | 5559:CrpalkeGrfs[4].NastavitevTrenutna:=Real_0;
mind_bool[280]:=CrpalkeGrfs[6].SetMinRunMode; | mind[280]:=CrpalkeGrfs[1].StatusCrpalke; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].PretokMax,lo:=5560,hi:=5561); |  | 280:CrpalkeGrfs[6].SetMinRunMode:=Bit_0; | 280:CrpalkeGrfs[1].StatusCrpalke:=Byte_0; |  |  | 5561:CrpalkeGrfs[4].PretokMax:=Real_0;
mind_bool[281]:=CrpalkeGrfs[6].SetPropPress; | mind[281]:=CrpalkeGrfs[1].StatusMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].PretokMin,lo:=5562,hi:=5563); |  | 281:CrpalkeGrfs[6].SetPropPress:=Bit_0; | 281:CrpalkeGrfs[1].StatusMode1:=Word_01; |  |  | 5563:CrpalkeGrfs[4].PretokMin:=Real_0;
mind_bool[282]:=CrpalkeGrfs[6].SetReference; | mind[282]:=CrpalkeGrfs[1].StatusMode1co; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].PretokTrenutni,lo:=5564,hi:=5565); |  | 282:CrpalkeGrfs[6].SetReference:=Bit_0; | 282:CrpalkeGrfs[1].StatusMode1co:=Byte_0; |  |  | 5565:CrpalkeGrfs[4].PretokTrenutni:=Real_0;
mind_bool[283]:=CrpalkeGrfs[6].SetRemoteMode; | mind[283]:=CrpalkeGrfs[1].StatusMode1op; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].PritiskMax,lo:=5566,hi:=5567); |  | 283:CrpalkeGrfs[6].SetRemoteMode:=Bit_0; | 283:CrpalkeGrfs[1].StatusMode1op:=Byte_0; |  |  | 5567:CrpalkeGrfs[4].PritiskMax:=Real_0;
mind_bool[284]:=CrpalkeGrfs[6].SetTwinModeAlt; | mind[284]:=CrpalkeGrfs[1].StatusMode2; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].PritiskTrenutni,lo:=5568,hi:=5569); |  | 284:CrpalkeGrfs[6].SetTwinModeAlt:=Bit_0; | 284:CrpalkeGrfs[1].StatusMode2:=Word_01; |  |  | 5569:CrpalkeGrfs[4].PritiskTrenutni:=Real_0;
mind_bool[285]:=CrpalkeGrfs[6].SetTwinModeSpare; | mind[285]:=CrpalkeGrfs[1].StatusMode3; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].ReferencaMotorjaHzV,lo:=5570,hi:=5571); |  | 285:CrpalkeGrfs[6].SetTwinModeSpare:=Bit_0; | 285:CrpalkeGrfs[1].StatusMode3:=Word_01; |  |  | 5571:CrpalkeGrfs[4].ReferencaMotorjaHzV:=Real_0;
mind_bool[286]:=CrpalkeGrfs[6].SetTwinModeSync; | mind[286]:=CrpalkeGrfs[2].AlarmActiveCode; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].ReferencaRemote,lo:=5572,hi:=5573); |  | 286:CrpalkeGrfs[6].SetTwinModeSync:=Bit_0; | 286:CrpalkeGrfs[2].AlarmActiveCode:=Word_01; |  |  | 5573:CrpalkeGrfs[4].ReferencaRemote:=Real_0;
mind_bool[287]:=CrpalkeGrfs[6].Start; | mind[287]:=CrpalkeGrfs[2].AlarmCodeLog1; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].StevecUr2h,lo:=5574,hi:=5575); |  | 287:CrpalkeGrfs[6].Start:=Bit_0; | 287:CrpalkeGrfs[2].AlarmCodeLog1:=Word_01; |  |  | 5575:CrpalkeGrfs[4].StevecUr2h:=Real_0;
mind_bool[288]:=CrpalkeGrfs[6].Stop; | mind[288]:=CrpalkeGrfs[2].AlarmCodeLog2; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].SystemFeedback,lo:=5576,hi:=5577); |  | 288:CrpalkeGrfs[6].Stop:=Bit_0; | 288:CrpalkeGrfs[2].AlarmCodeLog2:=Word_01; |  |  | 5577:CrpalkeGrfs[4].SystemFeedback:=Real_0;
mind_bool[289]:=CrpalkeGrfs[7].AlarmAktiven; | mind[289]:=CrpalkeGrfs[2].AlarmCodeLog3; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].SystemReference,lo:=5578,hi:=5579); |  | 289:CrpalkeGrfs[7].AlarmAktiven:=Bit_0; | 289:CrpalkeGrfs[2].AlarmCodeLog3:=Word_01; |  |  | 5579:CrpalkeGrfs[4].SystemReference:=Real_0;
mind_bool[290]:=CrpalkeGrfs[7].Deluje; | mind[290]:=CrpalkeGrfs[2].AlarmCodeLog4; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].TemperaturaMotorja,lo:=5580,hi:=5581); |  | 290:CrpalkeGrfs[7].Deluje:=Bit_0; | 290:CrpalkeGrfs[2].AlarmCodeLog4:=Word_01; |  |  | 5581:CrpalkeGrfs[4].TemperaturaMotorja:=Real_0;
mind_bool[291]:=CrpalkeGrfs[7].LocalMode; | mind[291]:=CrpalkeGrfs[2].AlarmCodeLog5; |  |  | Read_Real(rVar:=CrpalkeGrfs[4].UreXC200,lo:=5582,hi:=5583); |  | 291:CrpalkeGrfs[7].LocalMode:=Bit_0; | 291:CrpalkeGrfs[2].AlarmCodeLog5:=Word_01; |  |  | 5583:CrpalkeGrfs[4].UreXC200:=Real_0;
mind_bool[292]:=CrpalkeGrfs[7].RemoteON; | mind[292]:=CrpalkeGrfs[2].AlarmGroupXVH[0]; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].DeltaSetPoint,lo:=5584,hi:=5585); |  | 292:CrpalkeGrfs[7].RemoteON:=Bit_0; | 292:CrpalkeGrfs[2].AlarmGroupXVH[0]:=Word_01; |  |  | 5585:CrpalkeGrfs[5].DeltaSetPoint:=Real_0;
mind_bool[293]:=CrpalkeGrfs[7].Reset2handkWhValues; | mind[293]:=CrpalkeGrfs[2].AlarmGroupXVH[10]; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].EnergijaPoraba,lo:=5586,hi:=5587); |  | 293:CrpalkeGrfs[7].Reset2handkWhValues:=Bit_0; | 293:CrpalkeGrfs[2].AlarmGroupXVH[10]:=Word_01; |  |  | 5587:CrpalkeGrfs[5].EnergijaPoraba:=Real_0;
mind_bool[294]:=CrpalkeGrfs[7].ResetAlarm; | mind[294]:=CrpalkeGrfs[2].AlarmGroupXVH[11]; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].FrekPretvornikDCNapetost,lo:=5588,hi:=5589); |  | 294:CrpalkeGrfs[7].ResetAlarm:=Bit_0; | 294:CrpalkeGrfs[2].AlarmGroupXVH[11]:=Word_01; |  |  | 5589:CrpalkeGrfs[5].FrekPretvornikDCNapetost:=Real_0;
mind_bool[295]:=CrpalkeGrfs[7].ResetAlarmLog; | mind[295]:=CrpalkeGrfs[2].AlarmGroupXVH[12]; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].FrekPretvornikDCTok,lo:=5590,hi:=5591); |  | 295:CrpalkeGrfs[7].ResetAlarmLog:=Bit_0; | 295:CrpalkeGrfs[2].AlarmGroupXVH[12]:=Word_01; |  |  | 5591:CrpalkeGrfs[5].FrekPretvornikDCTok:=Real_0;
mind_bool[296]:=CrpalkeGrfs[7].ResetDevice; | mind[296]:=CrpalkeGrfs[2].AlarmGroupXVH[13]; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].FreqMax,lo:=5592,hi:=5593); |  | 296:CrpalkeGrfs[7].ResetDevice:=Bit_0; | 296:CrpalkeGrfs[2].AlarmGroupXVH[13]:=Word_01; |  |  | 5593:CrpalkeGrfs[5].FreqMax:=Real_0;
mind_bool[297]:=CrpalkeGrfs[7].SetAutomatic; | mind[297]:=CrpalkeGrfs[2].AlarmGroupXVH[14]; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].FreqMin,lo:=5594,hi:=5595); |  | 297:CrpalkeGrfs[7].SetAutomatic:=Bit_0; | 297:CrpalkeGrfs[2].AlarmGroupXVH[14]:=Word_01; |  |  | 5595:CrpalkeGrfs[5].FreqMin:=Real_0;
mind_bool[298]:=CrpalkeGrfs[7].SetConstFreqMode; | mind[298]:=CrpalkeGrfs[2].AlarmGroupXVH[15]; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].FreqUpper,lo:=5596,hi:=5597); |  | 298:CrpalkeGrfs[7].SetConstFreqMode:=Bit_0; | 298:CrpalkeGrfs[2].AlarmGroupXVH[15]:=Word_01; |  |  | 5597:CrpalkeGrfs[5].FreqUpper:=Real_0;
mind_bool[299]:=CrpalkeGrfs[7].SetConstPress; | mind[299]:=CrpalkeGrfs[2].AlarmGroupXVH[16]; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].MocMax,lo:=5598,hi:=5599); |  | 299:CrpalkeGrfs[7].SetConstPress:=Bit_0; | 299:CrpalkeGrfs[2].AlarmGroupXVH[16]:=Word_01; |  |  | 5599:CrpalkeGrfs[5].MocMax:=Real_0;
mind_bool[300]:=CrpalkeGrfs[7].SetLocalMode; | mind[300]:=CrpalkeGrfs[2].AlarmGroupXVH[1]; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].MocTrenutna,lo:=5600,hi:=5601); |  | 300:CrpalkeGrfs[7].SetLocalMode:=Bit_0; | 300:CrpalkeGrfs[2].AlarmGroupXVH[1]:=Word_01; |  |  | 5601:CrpalkeGrfs[5].MocTrenutna:=Real_0;
mind_bool[301]:=CrpalkeGrfs[7].SetMaxRunMode; | mind[301]:=CrpalkeGrfs[2].AlarmGroupXVH[2]; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].MotorHitrost,lo:=5602,hi:=5603); |  | 301:CrpalkeGrfs[7].SetMaxRunMode:=Bit_0; | 301:CrpalkeGrfs[2].AlarmGroupXVH[2]:=Word_01; |  |  | 5603:CrpalkeGrfs[5].MotorHitrost:=Real_0;
mind_bool[302]:=CrpalkeGrfs[7].SetMinRunMode; | mind[302]:=CrpalkeGrfs[2].AlarmGroupXVH[3]; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].MotorTok,lo:=5604,hi:=5605); |  | 302:CrpalkeGrfs[7].SetMinRunMode:=Bit_0; | 302:CrpalkeGrfs[2].AlarmGroupXVH[3]:=Word_01; |  |  | 5605:CrpalkeGrfs[5].MotorTok:=Real_0;
mind_bool[303]:=CrpalkeGrfs[7].SetPropPress; | mind[303]:=CrpalkeGrfs[2].AlarmGroupXVH[4]; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].NapajanjeTok,lo:=5606,hi:=5607); |  | 303:CrpalkeGrfs[7].SetPropPress:=Bit_0; | 303:CrpalkeGrfs[2].AlarmGroupXVH[4]:=Word_01; |  |  | 5607:CrpalkeGrfs[5].NapajanjeTok:=Real_0;
mind_bool[304]:=CrpalkeGrfs[7].SetReference; | mind[304]:=CrpalkeGrfs[2].AlarmGroupXVH[5]; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].NastavitevLokalna,lo:=5608,hi:=5609); |  | 304:CrpalkeGrfs[7].SetReference:=Bit_0; | 304:CrpalkeGrfs[2].AlarmGroupXVH[5]:=Word_01; |  |  | 5609:CrpalkeGrfs[5].NastavitevLokalna:=Real_0;
mind_bool[305]:=CrpalkeGrfs[7].SetRemoteMode; | mind[305]:=CrpalkeGrfs[2].AlarmGroupXVH[6]; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].NastavitevTrenutna,lo:=5610,hi:=5611); |  | 305:CrpalkeGrfs[7].SetRemoteMode:=Bit_0; | 305:CrpalkeGrfs[2].AlarmGroupXVH[6]:=Word_01; |  |  | 5611:CrpalkeGrfs[5].NastavitevTrenutna:=Real_0;
mind_bool[306]:=CrpalkeGrfs[7].SetTwinModeAlt; | mind[306]:=CrpalkeGrfs[2].AlarmGroupXVH[7]; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].PretokMax,lo:=5612,hi:=5613); |  | 306:CrpalkeGrfs[7].SetTwinModeAlt:=Bit_0; | 306:CrpalkeGrfs[2].AlarmGroupXVH[7]:=Word_01; |  |  | 5613:CrpalkeGrfs[5].PretokMax:=Real_0;
mind_bool[307]:=CrpalkeGrfs[7].SetTwinModeSpare; | mind[307]:=CrpalkeGrfs[2].AlarmGroupXVH[8]; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].PretokMin,lo:=5614,hi:=5615); |  | 307:CrpalkeGrfs[7].SetTwinModeSpare:=Bit_0; | 307:CrpalkeGrfs[2].AlarmGroupXVH[8]:=Word_01; |  |  | 5615:CrpalkeGrfs[5].PretokMin:=Real_0;
mind_bool[308]:=CrpalkeGrfs[7].SetTwinModeSync; | mind[308]:=CrpalkeGrfs[2].AlarmGroupXVH[9]; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].PretokTrenutni,lo:=5616,hi:=5617); |  | 308:CrpalkeGrfs[7].SetTwinModeSync:=Bit_0; | 308:CrpalkeGrfs[2].AlarmGroupXVH[9]:=Word_01; |  |  | 5617:CrpalkeGrfs[5].PretokTrenutni:=Real_0;
mind_bool[309]:=CrpalkeGrfs[7].Start; | mind[309]:=CrpalkeGrfs[2].AlarmQSD1; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].PritiskMax,lo:=5618,hi:=5619); |  | 309:CrpalkeGrfs[7].Start:=Bit_0; | 309:CrpalkeGrfs[2].AlarmQSD1:=Word_01; |  |  | 5619:CrpalkeGrfs[5].PritiskMax:=Real_0;
mind_bool[310]:=CrpalkeGrfs[7].Stop; | mind[310]:=CrpalkeGrfs[2].AlarmQSD2; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].PritiskTrenutni,lo:=5620,hi:=5621); |  | 310:CrpalkeGrfs[7].Stop:=Bit_0; | 310:CrpalkeGrfs[2].AlarmQSD2:=Word_01; |  |  | 5621:CrpalkeGrfs[5].PritiskTrenutni:=Real_0;
mind_bool[311]:=CrpalkeGrfs[8].AlarmAktiven; | mind[311]:=CrpalkeGrfs[2].AlarmStart1; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].ReferencaMotorjaHzV,lo:=5622,hi:=5623); |  | 311:CrpalkeGrfs[8].AlarmAktiven:=Bit_0; | 311:CrpalkeGrfs[2].AlarmStart1:=Word_01; |  |  | 5623:CrpalkeGrfs[5].ReferencaMotorjaHzV:=Real_0;
mind_bool[312]:=CrpalkeGrfs[8].Deluje; | mind[312]:=CrpalkeGrfs[2].AlarmStart2; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].ReferencaRemote,lo:=5624,hi:=5625); |  | 312:CrpalkeGrfs[8].Deluje:=Bit_0; | 312:CrpalkeGrfs[2].AlarmStart2:=Word_01; |  |  | 5625:CrpalkeGrfs[5].ReferencaRemote:=Real_0;
mind_bool[313]:=CrpalkeGrfs[8].LocalMode; | mind[313]:=CrpalkeGrfs[2].AlarmStop1; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].StevecUr2h,lo:=5626,hi:=5627); |  | 313:CrpalkeGrfs[8].LocalMode:=Bit_0; | 313:CrpalkeGrfs[2].AlarmStop1:=Word_01; |  |  | 5627:CrpalkeGrfs[5].StevecUr2h:=Real_0;
mind_bool[314]:=CrpalkeGrfs[8].RemoteON; | mind[314]:=CrpalkeGrfs[2].AlarmStop2; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].SystemFeedback,lo:=5628,hi:=5629); |  | 314:CrpalkeGrfs[8].RemoteON:=Bit_0; | 314:CrpalkeGrfs[2].AlarmStop2:=Word_01; |  |  | 5629:CrpalkeGrfs[5].SystemFeedback:=Real_0;
mind_bool[315]:=CrpalkeGrfs[8].Reset2handkWhValues; | mind[315]:=CrpalkeGrfs[2].AlarmStop3; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].SystemReference,lo:=5630,hi:=5631); |  | 315:CrpalkeGrfs[8].Reset2handkWhValues:=Bit_0; | 315:CrpalkeGrfs[2].AlarmStop3:=Word_01; |  |  | 5631:CrpalkeGrfs[5].SystemReference:=Real_0;
mind_bool[316]:=CrpalkeGrfs[8].ResetAlarm; | mind[316]:=CrpalkeGrfs[2].AlarmSurv1; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].TemperaturaMotorja,lo:=5632,hi:=5633); |  | 316:CrpalkeGrfs[8].ResetAlarm:=Bit_0; | 316:CrpalkeGrfs[2].AlarmSurv1:=Word_01; |  |  | 5633:CrpalkeGrfs[5].TemperaturaMotorja:=Real_0;
mind_bool[317]:=CrpalkeGrfs[8].ResetAlarmLog; | mind[317]:=CrpalkeGrfs[2].AlarmSurv2; |  |  | Read_Real(rVar:=CrpalkeGrfs[5].UreXC200,lo:=5634,hi:=5635); |  | 317:CrpalkeGrfs[8].ResetAlarmLog:=Bit_0; | 317:CrpalkeGrfs[2].AlarmSurv2:=Word_01; |  |  | 5635:CrpalkeGrfs[5].UreXC200:=Real_0;
mind_bool[318]:=CrpalkeGrfs[8].ResetDevice; | mind[318]:=CrpalkeGrfs[2].ControlSource; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].DeltaSetPoint,lo:=5636,hi:=5637); |  | 318:CrpalkeGrfs[8].ResetDevice:=Bit_0; | 318:CrpalkeGrfs[2].ControlSource:=Word_01; |  |  | 5637:CrpalkeGrfs[6].DeltaSetPoint:=Real_0;
mind_bool[319]:=CrpalkeGrfs[8].SetAutomatic; | mind[319]:=CrpalkeGrfs[2].ExternInputSetup; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].EnergijaPoraba,lo:=5638,hi:=5639); |  | 319:CrpalkeGrfs[8].SetAutomatic:=Bit_0; | 319:CrpalkeGrfs[2].ExternInputSetup:=Word_01; |  |  | 5639:CrpalkeGrfs[6].EnergijaPoraba:=Real_0;
mind_bool[320]:=CrpalkeGrfs[8].SetConstFreqMode; | mind[320]:=CrpalkeGrfs[2].ExternInputsStatus; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].FrekPretvornikDCNapetost,lo:=5640,hi:=5641); |  | 320:CrpalkeGrfs[8].SetConstFreqMode:=Bit_0; | 320:CrpalkeGrfs[2].ExternInputsStatus:=Word_01; |  |  | 5641:CrpalkeGrfs[6].FrekPretvornikDCNapetost:=Real_0;
mind_bool[321]:=CrpalkeGrfs[8].SetConstPress; | mind[321]:=CrpalkeGrfs[2].LocalSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].FrekPretvornikDCTok,lo:=5642,hi:=5643); |  | 321:CrpalkeGrfs[8].SetConstPress:=Bit_0; | 321:CrpalkeGrfs[2].LocalSetupMode1:=Word_01; |  |  | 5643:CrpalkeGrfs[6].FrekPretvornikDCTok:=Real_0;
mind_bool[322]:=CrpalkeGrfs[8].SetLocalMode; | mind[322]:=CrpalkeGrfs[2].PreklopkaMode; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].FreqMax,lo:=5644,hi:=5645); |  | 322:CrpalkeGrfs[8].SetLocalMode:=Bit_0; | 322:CrpalkeGrfs[2].PreklopkaMode:=Word_01; |  |  | 5645:CrpalkeGrfs[6].FreqMax:=Real_0;
mind_bool[323]:=CrpalkeGrfs[8].SetMaxRunMode; | mind[323]:=CrpalkeGrfs[2].Relay1setup; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].FreqMin,lo:=5646,hi:=5647); |  | 323:CrpalkeGrfs[8].SetMaxRunMode:=Bit_0; | 323:CrpalkeGrfs[2].Relay1setup:=Word_01; |  |  | 5647:CrpalkeGrfs[6].FreqMin:=Real_0;
mind_bool[324]:=CrpalkeGrfs[8].SetMinRunMode; | mind[324]:=CrpalkeGrfs[2].RemoteSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].FreqUpper,lo:=5648,hi:=5649); |  | 324:CrpalkeGrfs[8].SetMinRunMode:=Bit_0; | 324:CrpalkeGrfs[2].RemoteSetupMode1:=Word_01; |  |  | 5649:CrpalkeGrfs[6].FreqUpper:=Real_0;
mind_bool[325]:=CrpalkeGrfs[8].SetPropPress; | mind[325]:=CrpalkeGrfs[2].StatusCrpalke; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].MocMax,lo:=5650,hi:=5651); |  | 325:CrpalkeGrfs[8].SetPropPress:=Bit_0; | 325:CrpalkeGrfs[2].StatusCrpalke:=Byte_0; |  |  | 5651:CrpalkeGrfs[6].MocMax:=Real_0;
mind_bool[326]:=CrpalkeGrfs[8].SetReference; | mind[326]:=CrpalkeGrfs[2].StatusMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].MocTrenutna,lo:=5652,hi:=5653); |  | 326:CrpalkeGrfs[8].SetReference:=Bit_0; | 326:CrpalkeGrfs[2].StatusMode1:=Word_01; |  |  | 5653:CrpalkeGrfs[6].MocTrenutna:=Real_0;
mind_bool[327]:=CrpalkeGrfs[8].SetRemoteMode; | mind[327]:=CrpalkeGrfs[2].StatusMode1co; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].MotorHitrost,lo:=5654,hi:=5655); |  | 327:CrpalkeGrfs[8].SetRemoteMode:=Bit_0; | 327:CrpalkeGrfs[2].StatusMode1co:=Byte_0; |  |  | 5655:CrpalkeGrfs[6].MotorHitrost:=Real_0;
mind_bool[328]:=CrpalkeGrfs[8].SetTwinModeAlt; | mind[328]:=CrpalkeGrfs[2].StatusMode1op; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].MotorTok,lo:=5656,hi:=5657); |  | 328:CrpalkeGrfs[8].SetTwinModeAlt:=Bit_0; | 328:CrpalkeGrfs[2].StatusMode1op:=Byte_0; |  |  | 5657:CrpalkeGrfs[6].MotorTok:=Real_0;
mind_bool[329]:=CrpalkeGrfs[8].SetTwinModeSpare; | mind[329]:=CrpalkeGrfs[2].StatusMode2; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].NapajanjeTok,lo:=5658,hi:=5659); |  | 329:CrpalkeGrfs[8].SetTwinModeSpare:=Bit_0; | 329:CrpalkeGrfs[2].StatusMode2:=Word_01; |  |  | 5659:CrpalkeGrfs[6].NapajanjeTok:=Real_0;
mind_bool[330]:=CrpalkeGrfs[8].SetTwinModeSync; | mind[330]:=CrpalkeGrfs[2].StatusMode3; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].NastavitevLokalna,lo:=5660,hi:=5661); |  | 330:CrpalkeGrfs[8].SetTwinModeSync:=Bit_0; | 330:CrpalkeGrfs[2].StatusMode3:=Word_01; |  |  | 5661:CrpalkeGrfs[6].NastavitevLokalna:=Real_0;
mind_bool[331]:=CrpalkeGrfs[8].Start; | mind[331]:=CrpalkeGrfs[3].AlarmActiveCode; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].NastavitevTrenutna,lo:=5662,hi:=5663); |  | 331:CrpalkeGrfs[8].Start:=Bit_0; | 331:CrpalkeGrfs[3].AlarmActiveCode:=Word_01; |  |  | 5663:CrpalkeGrfs[6].NastavitevTrenutna:=Real_0;
mind_bool[332]:=CrpalkeGrfs[8].Stop; | mind[332]:=CrpalkeGrfs[3].AlarmCodeLog1; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].PretokMax,lo:=5664,hi:=5665); |  | 332:CrpalkeGrfs[8].Stop:=Bit_0; | 332:CrpalkeGrfs[3].AlarmCodeLog1:=Word_01; |  |  | 5665:CrpalkeGrfs[6].PretokMax:=Real_0;
mind_bool[333]:=CrpalkeGrfs[9].AlarmAktiven; | mind[333]:=CrpalkeGrfs[3].AlarmCodeLog2; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].PretokMin,lo:=5666,hi:=5667); |  | 333:CrpalkeGrfs[9].AlarmAktiven:=Bit_0; | 333:CrpalkeGrfs[3].AlarmCodeLog2:=Word_01; |  |  | 5667:CrpalkeGrfs[6].PretokMin:=Real_0;
mind_bool[334]:=CrpalkeGrfs[9].Deluje; | mind[334]:=CrpalkeGrfs[3].AlarmCodeLog3; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].PretokTrenutni,lo:=5668,hi:=5669); |  | 334:CrpalkeGrfs[9].Deluje:=Bit_0; | 334:CrpalkeGrfs[3].AlarmCodeLog3:=Word_01; |  |  | 5669:CrpalkeGrfs[6].PretokTrenutni:=Real_0;
mind_bool[335]:=CrpalkeGrfs[9].LocalMode; | mind[335]:=CrpalkeGrfs[3].AlarmCodeLog4; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].PritiskMax,lo:=5670,hi:=5671); |  | 335:CrpalkeGrfs[9].LocalMode:=Bit_0; | 335:CrpalkeGrfs[3].AlarmCodeLog4:=Word_01; |  |  | 5671:CrpalkeGrfs[6].PritiskMax:=Real_0;
mind_bool[336]:=CrpalkeGrfs[9].RemoteON; | mind[336]:=CrpalkeGrfs[3].AlarmCodeLog5; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].PritiskTrenutni,lo:=5672,hi:=5673); |  | 336:CrpalkeGrfs[9].RemoteON:=Bit_0; | 336:CrpalkeGrfs[3].AlarmCodeLog5:=Word_01; |  |  | 5673:CrpalkeGrfs[6].PritiskTrenutni:=Real_0;
mind_bool[337]:=CrpalkeGrfs[9].Reset2handkWhValues; | mind[337]:=CrpalkeGrfs[3].AlarmGroupXVH[0]; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].ReferencaMotorjaHzV,lo:=5674,hi:=5675); |  | 337:CrpalkeGrfs[9].Reset2handkWhValues:=Bit_0; | 337:CrpalkeGrfs[3].AlarmGroupXVH[0]:=Word_01; |  |  | 5675:CrpalkeGrfs[6].ReferencaMotorjaHzV:=Real_0;
mind_bool[338]:=CrpalkeGrfs[9].ResetAlarm; | mind[338]:=CrpalkeGrfs[3].AlarmGroupXVH[10]; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].ReferencaRemote,lo:=5676,hi:=5677); |  | 338:CrpalkeGrfs[9].ResetAlarm:=Bit_0; | 338:CrpalkeGrfs[3].AlarmGroupXVH[10]:=Word_01; |  |  | 5677:CrpalkeGrfs[6].ReferencaRemote:=Real_0;
mind_bool[339]:=CrpalkeGrfs[9].ResetAlarmLog; | mind[339]:=CrpalkeGrfs[3].AlarmGroupXVH[11]; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].StevecUr2h,lo:=5678,hi:=5679); |  | 339:CrpalkeGrfs[9].ResetAlarmLog:=Bit_0; | 339:CrpalkeGrfs[3].AlarmGroupXVH[11]:=Word_01; |  |  | 5679:CrpalkeGrfs[6].StevecUr2h:=Real_0;
mind_bool[340]:=CrpalkeGrfs[9].ResetDevice; | mind[340]:=CrpalkeGrfs[3].AlarmGroupXVH[12]; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].SystemFeedback,lo:=5680,hi:=5681); |  | 340:CrpalkeGrfs[9].ResetDevice:=Bit_0; | 340:CrpalkeGrfs[3].AlarmGroupXVH[12]:=Word_01; |  |  | 5681:CrpalkeGrfs[6].SystemFeedback:=Real_0;
mind_bool[341]:=CrpalkeGrfs[9].SetAutomatic; | mind[341]:=CrpalkeGrfs[3].AlarmGroupXVH[13]; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].SystemReference,lo:=5682,hi:=5683); |  | 341:CrpalkeGrfs[9].SetAutomatic:=Bit_0; | 341:CrpalkeGrfs[3].AlarmGroupXVH[13]:=Word_01; |  |  | 5683:CrpalkeGrfs[6].SystemReference:=Real_0;
mind_bool[342]:=CrpalkeGrfs[9].SetConstFreqMode; | mind[342]:=CrpalkeGrfs[3].AlarmGroupXVH[14]; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].TemperaturaMotorja,lo:=5684,hi:=5685); |  | 342:CrpalkeGrfs[9].SetConstFreqMode:=Bit_0; | 342:CrpalkeGrfs[3].AlarmGroupXVH[14]:=Word_01; |  |  | 5685:CrpalkeGrfs[6].TemperaturaMotorja:=Real_0;
mind_bool[343]:=CrpalkeGrfs[9].SetConstPress; | mind[343]:=CrpalkeGrfs[3].AlarmGroupXVH[15]; |  |  | Read_Real(rVar:=CrpalkeGrfs[6].UreXC200,lo:=5686,hi:=5687); |  | 343:CrpalkeGrfs[9].SetConstPress:=Bit_0; | 343:CrpalkeGrfs[3].AlarmGroupXVH[15]:=Word_01; |  |  | 5687:CrpalkeGrfs[6].UreXC200:=Real_0;
mind_bool[344]:=CrpalkeGrfs[9].SetLocalMode; | mind[344]:=CrpalkeGrfs[3].AlarmGroupXVH[16]; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].DeltaSetPoint,lo:=5688,hi:=5689); |  | 344:CrpalkeGrfs[9].SetLocalMode:=Bit_0; | 344:CrpalkeGrfs[3].AlarmGroupXVH[16]:=Word_01; |  |  | 5689:CrpalkeGrfs[7].DeltaSetPoint:=Real_0;
mind_bool[345]:=CrpalkeGrfs[9].SetMaxRunMode; | mind[345]:=CrpalkeGrfs[3].AlarmGroupXVH[1]; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].EnergijaPoraba,lo:=5690,hi:=5691); |  | 345:CrpalkeGrfs[9].SetMaxRunMode:=Bit_0; | 345:CrpalkeGrfs[3].AlarmGroupXVH[1]:=Word_01; |  |  | 5691:CrpalkeGrfs[7].EnergijaPoraba:=Real_0;
mind_bool[346]:=CrpalkeGrfs[9].SetMinRunMode; | mind[346]:=CrpalkeGrfs[3].AlarmGroupXVH[2]; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].FrekPretvornikDCNapetost,lo:=5692,hi:=5693); |  | 346:CrpalkeGrfs[9].SetMinRunMode:=Bit_0; | 346:CrpalkeGrfs[3].AlarmGroupXVH[2]:=Word_01; |  |  | 5693:CrpalkeGrfs[7].FrekPretvornikDCNapetost:=Real_0;
mind_bool[347]:=CrpalkeGrfs[9].SetPropPress; | mind[347]:=CrpalkeGrfs[3].AlarmGroupXVH[3]; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].FrekPretvornikDCTok,lo:=5694,hi:=5695); |  | 347:CrpalkeGrfs[9].SetPropPress:=Bit_0; | 347:CrpalkeGrfs[3].AlarmGroupXVH[3]:=Word_01; |  |  | 5695:CrpalkeGrfs[7].FrekPretvornikDCTok:=Real_0;
mind_bool[348]:=CrpalkeGrfs[9].SetReference; | mind[348]:=CrpalkeGrfs[3].AlarmGroupXVH[4]; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].FreqMax,lo:=5696,hi:=5697); |  | 348:CrpalkeGrfs[9].SetReference:=Bit_0; | 348:CrpalkeGrfs[3].AlarmGroupXVH[4]:=Word_01; |  |  | 5697:CrpalkeGrfs[7].FreqMax:=Real_0;
mind_bool[349]:=CrpalkeGrfs[9].SetRemoteMode; | mind[349]:=CrpalkeGrfs[3].AlarmGroupXVH[5]; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].FreqMin,lo:=5698,hi:=5699); |  | 349:CrpalkeGrfs[9].SetRemoteMode:=Bit_0; | 349:CrpalkeGrfs[3].AlarmGroupXVH[5]:=Word_01; |  |  | 5699:CrpalkeGrfs[7].FreqMin:=Real_0;
mind_bool[350]:=CrpalkeGrfs[9].SetTwinModeAlt; | mind[350]:=CrpalkeGrfs[3].AlarmGroupXVH[6]; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].FreqUpper,lo:=5700,hi:=5701); |  | 350:CrpalkeGrfs[9].SetTwinModeAlt:=Bit_0; | 350:CrpalkeGrfs[3].AlarmGroupXVH[6]:=Word_01; |  |  | 5701:CrpalkeGrfs[7].FreqUpper:=Real_0;
mind_bool[351]:=CrpalkeGrfs[9].SetTwinModeSpare; | mind[351]:=CrpalkeGrfs[3].AlarmGroupXVH[7]; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].MocMax,lo:=5702,hi:=5703); |  | 351:CrpalkeGrfs[9].SetTwinModeSpare:=Bit_0; | 351:CrpalkeGrfs[3].AlarmGroupXVH[7]:=Word_01; |  |  | 5703:CrpalkeGrfs[7].MocMax:=Real_0;
mind_bool[352]:=CrpalkeGrfs[9].SetTwinModeSync; | mind[352]:=CrpalkeGrfs[3].AlarmGroupXVH[8]; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].MocTrenutna,lo:=5704,hi:=5705); |  | 352:CrpalkeGrfs[9].SetTwinModeSync:=Bit_0; | 352:CrpalkeGrfs[3].AlarmGroupXVH[8]:=Word_01; |  |  | 5705:CrpalkeGrfs[7].MocTrenutna:=Real_0;
mind_bool[353]:=CrpalkeGrfs[9].Start; | mind[353]:=CrpalkeGrfs[3].AlarmGroupXVH[9]; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].MotorHitrost,lo:=5706,hi:=5707); |  | 353:CrpalkeGrfs[9].Start:=Bit_0; | 353:CrpalkeGrfs[3].AlarmGroupXVH[9]:=Word_01; |  |  | 5707:CrpalkeGrfs[7].MotorHitrost:=Real_0;
mind_bool[354]:=CrpalkeGrfs[9].Stop; | mind[354]:=CrpalkeGrfs[3].AlarmQSD1; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].MotorTok,lo:=5708,hi:=5709); |  | 354:CrpalkeGrfs[9].Stop:=Bit_0; | 354:CrpalkeGrfs[3].AlarmQSD1:=Word_01; |  |  | 5709:CrpalkeGrfs[7].MotorTok:=Real_0;
mind_bool[355]:=CrpDanfossGenError[1]; | mind[355]:=CrpalkeGrfs[3].AlarmQSD2; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].NapajanjeTok,lo:=5710,hi:=5711); |  | 355:CrpDanfossGenError[1]:=Bit_0; | 355:CrpalkeGrfs[3].AlarmQSD2:=Word_01; |  |  | 5711:CrpalkeGrfs[7].NapajanjeTok:=Real_0;
mind_bool[356]:=CrpDanfossGenError[2]; | mind[356]:=CrpalkeGrfs[3].AlarmStart1; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].NastavitevLokalna,lo:=5712,hi:=5713); |  | 356:CrpDanfossGenError[2]:=Bit_0; | 356:CrpalkeGrfs[3].AlarmStart1:=Word_01; |  |  | 5713:CrpalkeGrfs[7].NastavitevLokalna:=Real_0;
mind_bool[357]:=CrpDanfossGenError[3]; | mind[357]:=CrpalkeGrfs[3].AlarmStart2; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].NastavitevTrenutna,lo:=5714,hi:=5715); |  | 357:CrpDanfossGenError[3]:=Bit_0; | 357:CrpalkeGrfs[3].AlarmStart2:=Word_01; |  |  | 5715:CrpalkeGrfs[7].NastavitevTrenutna:=Real_0;
mind_bool[358]:=CrpDanfossGenError[4]; | mind[358]:=CrpalkeGrfs[3].AlarmStop1; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].PretokMax,lo:=5716,hi:=5717); |  | 358:CrpDanfossGenError[4]:=Bit_0; | 358:CrpalkeGrfs[3].AlarmStop1:=Word_01; |  |  | 5717:CrpalkeGrfs[7].PretokMax:=Real_0;
mind_bool[359]:=CrpDanfossNaCas[1]; | mind[359]:=CrpalkeGrfs[3].AlarmStop2; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].PretokMin,lo:=5718,hi:=5719); |  | 359:CrpDanfossNaCas[1]:=Bit_0; | 359:CrpalkeGrfs[3].AlarmStop2:=Word_01; |  |  | 5719:CrpalkeGrfs[7].PretokMin:=Real_0;
mind_bool[360]:=CrpDanfossNaCas[2]; | mind[360]:=CrpalkeGrfs[3].AlarmStop3; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].PretokTrenutni,lo:=5720,hi:=5721); |  | 360:CrpDanfossNaCas[2]:=Bit_0; | 360:CrpalkeGrfs[3].AlarmStop3:=Word_01; |  |  | 5721:CrpalkeGrfs[7].PretokTrenutni:=Real_0;
mind_bool[361]:=CrpDanfossON[1]; | mind[361]:=CrpalkeGrfs[3].AlarmSurv1; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].PritiskMax,lo:=5722,hi:=5723); |  | 361:CrpDanfossON[1]:=Bit_0; | 361:CrpalkeGrfs[3].AlarmSurv1:=Word_01; |  |  | 5723:CrpalkeGrfs[7].PritiskMax:=Real_0;
mind_bool[362]:=CrpDanfossON[2]; | mind[362]:=CrpalkeGrfs[3].AlarmSurv2; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].PritiskTrenutni,lo:=5724,hi:=5725); |  | 362:CrpDanfossON[2]:=Bit_0; | 362:CrpalkeGrfs[3].AlarmSurv2:=Word_01; |  |  | 5725:CrpalkeGrfs[7].PritiskTrenutni:=Real_0;
mind_bool[363]:=CrpDanfossON[3]; | mind[363]:=CrpalkeGrfs[3].ControlSource; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].ReferencaMotorjaHzV,lo:=5726,hi:=5727); |  | 363:CrpDanfossON[3]:=Bit_0; | 363:CrpalkeGrfs[3].ControlSource:=Word_01; |  |  | 5727:CrpalkeGrfs[7].ReferencaMotorjaHzV:=Real_0;
mind_bool[364]:=CrpDanfossON[4]; | mind[364]:=CrpalkeGrfs[3].ExternInputSetup; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].ReferencaRemote,lo:=5728,hi:=5729); |  | 364:CrpDanfossON[4]:=Bit_0; | 364:CrpalkeGrfs[3].ExternInputSetup:=Word_01; |  |  | 5729:CrpalkeGrfs[7].ReferencaRemote:=Real_0;
mind_bool[365]:=CrpDanfossStatusError[1]; | mind[365]:=CrpalkeGrfs[3].ExternInputsStatus; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].StevecUr2h,lo:=5730,hi:=5731); |  | 365:CrpDanfossStatusError[1]:=Bit_0; | 365:CrpalkeGrfs[3].ExternInputsStatus:=Word_01; |  |  | 5731:CrpalkeGrfs[7].StevecUr2h:=Real_0;
mind_bool[366]:=CrpDanfossStatusError[2]; | mind[366]:=CrpalkeGrfs[3].LocalSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].SystemFeedback,lo:=5732,hi:=5733); |  | 366:CrpDanfossStatusError[2]:=Bit_0; | 366:CrpalkeGrfs[3].LocalSetupMode1:=Word_01; |  |  | 5733:CrpalkeGrfs[7].SystemFeedback:=Real_0;
mind_bool[367]:=CrpDanfossStatusError[3]; | mind[367]:=CrpalkeGrfs[3].PreklopkaMode; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].SystemReference,lo:=5734,hi:=5735); |  | 367:CrpDanfossStatusError[3]:=Bit_0; | 367:CrpalkeGrfs[3].PreklopkaMode:=Word_01; |  |  | 5735:CrpalkeGrfs[7].SystemReference:=Real_0;
mind_bool[368]:=CrpDanfossStatusError[4]; | mind[368]:=CrpalkeGrfs[3].Relay1setup; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].TemperaturaMotorja,lo:=5736,hi:=5737); |  | 368:CrpDanfossStatusError[4]:=Bit_0; | 368:CrpalkeGrfs[3].Relay1setup:=Word_01; |  |  | 5737:CrpalkeGrfs[7].TemperaturaMotorja:=Real_0;
mind_bool[369]:=CrpGrundfosGenError[10]; | mind[369]:=CrpalkeGrfs[3].RemoteSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[7].UreXC200,lo:=5738,hi:=5739); |  | 369:CrpGrundfosGenError[10]:=Bit_0; | 369:CrpalkeGrfs[3].RemoteSetupMode1:=Word_01; |  |  | 5739:CrpalkeGrfs[7].UreXC200:=Real_0;
mind_bool[370]:=CrpGrundfosGenError[11]; | mind[370]:=CrpalkeGrfs[3].StatusCrpalke; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].DeltaSetPoint,lo:=5740,hi:=5741); |  | 370:CrpGrundfosGenError[11]:=Bit_0; | 370:CrpalkeGrfs[3].StatusCrpalke:=Byte_0; |  |  | 5741:CrpalkeGrfs[8].DeltaSetPoint:=Real_0;
mind_bool[371]:=CrpGrundfosGenError[12]; | mind[371]:=CrpalkeGrfs[3].StatusMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].EnergijaPoraba,lo:=5742,hi:=5743); |  | 371:CrpGrundfosGenError[12]:=Bit_0; | 371:CrpalkeGrfs[3].StatusMode1:=Word_01; |  |  | 5743:CrpalkeGrfs[8].EnergijaPoraba:=Real_0;
mind_bool[372]:=CrpGrundfosGenError[13]; | mind[372]:=CrpalkeGrfs[3].StatusMode1co; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].FrekPretvornikDCNapetost,lo:=5744,hi:=5745); |  | 372:CrpGrundfosGenError[13]:=Bit_0; | 372:CrpalkeGrfs[3].StatusMode1co:=Byte_0; |  |  | 5745:CrpalkeGrfs[8].FrekPretvornikDCNapetost:=Real_0;
mind_bool[373]:=CrpGrundfosGenError[14]; | mind[373]:=CrpalkeGrfs[3].StatusMode1op; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].FrekPretvornikDCTok,lo:=5746,hi:=5747); |  | 373:CrpGrundfosGenError[14]:=Bit_0; | 373:CrpalkeGrfs[3].StatusMode1op:=Byte_0; |  |  | 5747:CrpalkeGrfs[8].FrekPretvornikDCTok:=Real_0;
mind_bool[374]:=CrpGrundfosGenError[1]; | mind[374]:=CrpalkeGrfs[3].StatusMode2; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].FreqMax,lo:=5748,hi:=5749); |  | 374:CrpGrundfosGenError[1]:=Bit_0; | 374:CrpalkeGrfs[3].StatusMode2:=Word_01; |  |  | 5749:CrpalkeGrfs[8].FreqMax:=Real_0;
mind_bool[375]:=CrpGrundfosGenError[2]; | mind[375]:=CrpalkeGrfs[3].StatusMode3; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].FreqMin,lo:=5750,hi:=5751); |  | 375:CrpGrundfosGenError[2]:=Bit_0; | 375:CrpalkeGrfs[3].StatusMode3:=Word_01; |  |  | 5751:CrpalkeGrfs[8].FreqMin:=Real_0;
mind_bool[376]:=CrpGrundfosGenError[3]; | mind[376]:=CrpalkeGrfs[4].AlarmActiveCode; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].FreqUpper,lo:=5752,hi:=5753); |  | 376:CrpGrundfosGenError[3]:=Bit_0; | 376:CrpalkeGrfs[4].AlarmActiveCode:=Word_01; |  |  | 5753:CrpalkeGrfs[8].FreqUpper:=Real_0;
mind_bool[377]:=CrpGrundfosGenError[4]; | mind[377]:=CrpalkeGrfs[4].AlarmCodeLog1; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].MocMax,lo:=5754,hi:=5755); |  | 377:CrpGrundfosGenError[4]:=Bit_0; | 377:CrpalkeGrfs[4].AlarmCodeLog1:=Word_01; |  |  | 5755:CrpalkeGrfs[8].MocMax:=Real_0;
mind_bool[378]:=CrpGrundfosGenError[5]; | mind[378]:=CrpalkeGrfs[4].AlarmCodeLog2; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].MocTrenutna,lo:=5756,hi:=5757); |  | 378:CrpGrundfosGenError[5]:=Bit_0; | 378:CrpalkeGrfs[4].AlarmCodeLog2:=Word_01; |  |  | 5757:CrpalkeGrfs[8].MocTrenutna:=Real_0;
mind_bool[379]:=CrpGrundfosGenError[6]; | mind[379]:=CrpalkeGrfs[4].AlarmCodeLog3; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].MotorHitrost,lo:=5758,hi:=5759); |  | 379:CrpGrundfosGenError[6]:=Bit_0; | 379:CrpalkeGrfs[4].AlarmCodeLog3:=Word_01; |  |  | 5759:CrpalkeGrfs[8].MotorHitrost:=Real_0;
mind_bool[380]:=CrpGrundfosGenError[7]; | mind[380]:=CrpalkeGrfs[4].AlarmCodeLog4; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].MotorTok,lo:=5760,hi:=5761); |  | 380:CrpGrundfosGenError[7]:=Bit_0; | 380:CrpalkeGrfs[4].AlarmCodeLog4:=Word_01; |  |  | 5761:CrpalkeGrfs[8].MotorTok:=Real_0;
mind_bool[381]:=CrpGrundfosGenError[8]; | mind[381]:=CrpalkeGrfs[4].AlarmCodeLog5; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].NapajanjeTok,lo:=5762,hi:=5763); |  | 381:CrpGrundfosGenError[8]:=Bit_0; | 381:CrpalkeGrfs[4].AlarmCodeLog5:=Word_01; |  |  | 5763:CrpalkeGrfs[8].NapajanjeTok:=Real_0;
mind_bool[382]:=CrpGrundfosGenError[9]; | mind[382]:=CrpalkeGrfs[4].AlarmGroupXVH[0]; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].NastavitevLokalna,lo:=5764,hi:=5765); |  | 382:CrpGrundfosGenError[9]:=Bit_0; | 382:CrpalkeGrfs[4].AlarmGroupXVH[0]:=Word_01; |  |  | 5765:CrpalkeGrfs[8].NastavitevLokalna:=Real_0;
mind_bool[383]:=CrpGrundfosNaCas[1]; | mind[383]:=CrpalkeGrfs[4].AlarmGroupXVH[10]; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].NastavitevTrenutna,lo:=5766,hi:=5767); |  | 383:CrpGrundfosNaCas[1]:=Bit_0; | 383:CrpalkeGrfs[4].AlarmGroupXVH[10]:=Word_01; |  |  | 5767:CrpalkeGrfs[8].NastavitevTrenutna:=Real_0;
mind_bool[384]:=CrpGrundfosNaCas[2]; | mind[384]:=CrpalkeGrfs[4].AlarmGroupXVH[11]; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].PretokMax,lo:=5768,hi:=5769); |  | 384:CrpGrundfosNaCas[2]:=Bit_0; | 384:CrpalkeGrfs[4].AlarmGroupXVH[11]:=Word_01; |  |  | 5769:CrpalkeGrfs[8].PretokMax:=Real_0;
mind_bool[385]:=CrpGrundfosNaCas[3]; | mind[385]:=CrpalkeGrfs[4].AlarmGroupXVH[12]; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].PretokMin,lo:=5770,hi:=5771); |  | 385:CrpGrundfosNaCas[3]:=Bit_0; | 385:CrpalkeGrfs[4].AlarmGroupXVH[12]:=Word_01; |  |  | 5771:CrpalkeGrfs[8].PretokMin:=Real_0;
mind_bool[386]:=CrpGrundfosNaCas[4]; | mind[386]:=CrpalkeGrfs[4].AlarmGroupXVH[13]; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].PretokTrenutni,lo:=5772,hi:=5773); |  | 386:CrpGrundfosNaCas[4]:=Bit_0; | 386:CrpalkeGrfs[4].AlarmGroupXVH[13]:=Word_01; |  |  | 5773:CrpalkeGrfs[8].PretokTrenutni:=Real_0;
mind_bool[387]:=CrpGrundfosNaCas[5]; | mind[387]:=CrpalkeGrfs[4].AlarmGroupXVH[14]; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].PritiskMax,lo:=5774,hi:=5775); |  | 387:CrpGrundfosNaCas[5]:=Bit_0; | 387:CrpalkeGrfs[4].AlarmGroupXVH[14]:=Word_01; |  |  | 5775:CrpalkeGrfs[8].PritiskMax:=Real_0;
mind_bool[388]:=CrpGrundfosNaCas[6]; | mind[388]:=CrpalkeGrfs[4].AlarmGroupXVH[15]; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].PritiskTrenutni,lo:=5776,hi:=5777); |  | 388:CrpGrundfosNaCas[6]:=Bit_0; | 388:CrpalkeGrfs[4].AlarmGroupXVH[15]:=Word_01; |  |  | 5777:CrpalkeGrfs[8].PritiskTrenutni:=Real_0;
mind_bool[389]:=CrpGrundfosNaCas[7]; | mind[389]:=CrpalkeGrfs[4].AlarmGroupXVH[16]; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].ReferencaMotorjaHzV,lo:=5778,hi:=5779); |  | 389:CrpGrundfosNaCas[7]:=Bit_0; | 389:CrpalkeGrfs[4].AlarmGroupXVH[16]:=Word_01; |  |  | 5779:CrpalkeGrfs[8].ReferencaMotorjaHzV:=Real_0;
mind_bool[390]:=CrpGrundfosNaTlak[1]; | mind[390]:=CrpalkeGrfs[4].AlarmGroupXVH[1]; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].ReferencaRemote,lo:=5780,hi:=5781); |  | 390:CrpGrundfosNaTlak[1]:=Bit_0; | 390:CrpalkeGrfs[4].AlarmGroupXVH[1]:=Word_01; |  |  | 5781:CrpalkeGrfs[8].ReferencaRemote:=Real_0;
mind_bool[391]:=CrpGrundfosNaTlak[2]; | mind[391]:=CrpalkeGrfs[4].AlarmGroupXVH[2]; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].StevecUr2h,lo:=5782,hi:=5783); |  | 391:CrpGrundfosNaTlak[2]:=Bit_0; | 391:CrpalkeGrfs[4].AlarmGroupXVH[2]:=Word_01; |  |  | 5783:CrpalkeGrfs[8].StevecUr2h:=Real_0;
mind_bool[392]:=CrpGrundfosNaTlak[3]; | mind[392]:=CrpalkeGrfs[4].AlarmGroupXVH[3]; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].SystemFeedback,lo:=5784,hi:=5785); |  | 392:CrpGrundfosNaTlak[3]:=Bit_0; | 392:CrpalkeGrfs[4].AlarmGroupXVH[3]:=Word_01; |  |  | 5785:CrpalkeGrfs[8].SystemFeedback:=Real_0;
mind_bool[393]:=CrpGrundfosNaTlak[4]; | mind[393]:=CrpalkeGrfs[4].AlarmGroupXVH[4]; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].SystemReference,lo:=5786,hi:=5787); |  | 393:CrpGrundfosNaTlak[4]:=Bit_0; | 393:CrpalkeGrfs[4].AlarmGroupXVH[4]:=Word_01; |  |  | 5787:CrpalkeGrfs[8].SystemReference:=Real_0;
mind_bool[394]:=CrpGrundfosNaTlak[5]; | mind[394]:=CrpalkeGrfs[4].AlarmGroupXVH[5]; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].TemperaturaMotorja,lo:=5788,hi:=5789); |  | 394:CrpGrundfosNaTlak[5]:=Bit_0; | 394:CrpalkeGrfs[4].AlarmGroupXVH[5]:=Word_01; |  |  | 5789:CrpalkeGrfs[8].TemperaturaMotorja:=Real_0;
mind_bool[395]:=CrpGrundfosNaTlak[6]; | mind[395]:=CrpalkeGrfs[4].AlarmGroupXVH[6]; |  |  | Read_Real(rVar:=CrpalkeGrfs[8].UreXC200,lo:=5790,hi:=5791); |  | 395:CrpGrundfosNaTlak[6]:=Bit_0; | 395:CrpalkeGrfs[4].AlarmGroupXVH[6]:=Word_01; |  |  | 5791:CrpalkeGrfs[8].UreXC200:=Real_0;
mind_bool[396]:=CrpGrundfosNaTlak[7]; | mind[396]:=CrpalkeGrfs[4].AlarmGroupXVH[7]; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].DeltaSetPoint,lo:=5792,hi:=5793); |  | 396:CrpGrundfosNaTlak[7]:=Bit_0; | 396:CrpalkeGrfs[4].AlarmGroupXVH[7]:=Word_01; |  |  | 5793:CrpalkeGrfs[9].DeltaSetPoint:=Real_0;
mind_bool[397]:=CrpGrundfosON[10]; | mind[397]:=CrpalkeGrfs[4].AlarmGroupXVH[8]; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].EnergijaPoraba,lo:=5794,hi:=5795); |  | 397:CrpGrundfosON[10]:=Bit_0; | 397:CrpalkeGrfs[4].AlarmGroupXVH[8]:=Word_01; |  |  | 5795:CrpalkeGrfs[9].EnergijaPoraba:=Real_0;
mind_bool[398]:=CrpGrundfosON[11]; | mind[398]:=CrpalkeGrfs[4].AlarmGroupXVH[9]; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].FrekPretvornikDCNapetost,lo:=5796,hi:=5797); |  | 398:CrpGrundfosON[11]:=Bit_0; | 398:CrpalkeGrfs[4].AlarmGroupXVH[9]:=Word_01; |  |  | 5797:CrpalkeGrfs[9].FrekPretvornikDCNapetost:=Real_0;
mind_bool[399]:=CrpGrundfosON[12]; | mind[399]:=CrpalkeGrfs[4].AlarmQSD1; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].FrekPretvornikDCTok,lo:=5798,hi:=5799); |  | 399:CrpGrundfosON[12]:=Bit_0; | 399:CrpalkeGrfs[4].AlarmQSD1:=Word_01; |  |  | 5799:CrpalkeGrfs[9].FrekPretvornikDCTok:=Real_0;
mind_bool[400]:=CrpGrundfosON[13]; | mind[400]:=CrpalkeGrfs[4].AlarmQSD2; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].FreqMax,lo:=5800,hi:=5801); |  | 400:CrpGrundfosON[13]:=Bit_0; | 400:CrpalkeGrfs[4].AlarmQSD2:=Word_01; |  |  | 5801:CrpalkeGrfs[9].FreqMax:=Real_0;
mind_bool[401]:=CrpGrundfosON[14]; | mind[401]:=CrpalkeGrfs[4].AlarmStart1; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].FreqMin,lo:=5802,hi:=5803); |  | 401:CrpGrundfosON[14]:=Bit_0; | 401:CrpalkeGrfs[4].AlarmStart1:=Word_01; |  |  | 5803:CrpalkeGrfs[9].FreqMin:=Real_0;
mind_bool[402]:=CrpGrundfosON[1]; | mind[402]:=CrpalkeGrfs[4].AlarmStart2; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].FreqUpper,lo:=5804,hi:=5805); |  | 402:CrpGrundfosON[1]:=Bit_0; | 402:CrpalkeGrfs[4].AlarmStart2:=Word_01; |  |  | 5805:CrpalkeGrfs[9].FreqUpper:=Real_0;
mind_bool[403]:=CrpGrundfosON[2]; | mind[403]:=CrpalkeGrfs[4].AlarmStop1; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].MocMax,lo:=5806,hi:=5807); |  | 403:CrpGrundfosON[2]:=Bit_0; | 403:CrpalkeGrfs[4].AlarmStop1:=Word_01; |  |  | 5807:CrpalkeGrfs[9].MocMax:=Real_0;
mind_bool[404]:=CrpGrundfosON[3]; | mind[404]:=CrpalkeGrfs[4].AlarmStop2; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].MocTrenutna,lo:=5808,hi:=5809); |  | 404:CrpGrundfosON[3]:=Bit_0; | 404:CrpalkeGrfs[4].AlarmStop2:=Word_01; |  |  | 5809:CrpalkeGrfs[9].MocTrenutna:=Real_0;
mind_bool[405]:=CrpGrundfosON[4]; | mind[405]:=CrpalkeGrfs[4].AlarmStop3; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].MotorHitrost,lo:=5810,hi:=5811); |  | 405:CrpGrundfosON[4]:=Bit_0; | 405:CrpalkeGrfs[4].AlarmStop3:=Word_01; |  |  | 5811:CrpalkeGrfs[9].MotorHitrost:=Real_0;
mind_bool[406]:=CrpGrundfosON[5]; | mind[406]:=CrpalkeGrfs[4].AlarmSurv1; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].MotorTok,lo:=5812,hi:=5813); |  | 406:CrpGrundfosON[5]:=Bit_0; | 406:CrpalkeGrfs[4].AlarmSurv1:=Word_01; |  |  | 5813:CrpalkeGrfs[9].MotorTok:=Real_0;
mind_bool[407]:=CrpGrundfosON[6]; | mind[407]:=CrpalkeGrfs[4].AlarmSurv2; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].NapajanjeTok,lo:=5814,hi:=5815); |  | 407:CrpGrundfosON[6]:=Bit_0; | 407:CrpalkeGrfs[4].AlarmSurv2:=Word_01; |  |  | 5815:CrpalkeGrfs[9].NapajanjeTok:=Real_0;
mind_bool[408]:=CrpGrundfosON[7]; | mind[408]:=CrpalkeGrfs[4].ControlSource; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].NastavitevLokalna,lo:=5816,hi:=5817); |  | 408:CrpGrundfosON[7]:=Bit_0; | 408:CrpalkeGrfs[4].ControlSource:=Word_01; |  |  | 5817:CrpalkeGrfs[9].NastavitevLokalna:=Real_0;
mind_bool[409]:=CrpGrundfosON[8]; | mind[409]:=CrpalkeGrfs[4].ExternInputSetup; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].NastavitevTrenutna,lo:=5818,hi:=5819); |  | 409:CrpGrundfosON[8]:=Bit_0; | 409:CrpalkeGrfs[4].ExternInputSetup:=Word_01; |  |  | 5819:CrpalkeGrfs[9].NastavitevTrenutna:=Real_0;
mind_bool[410]:=CrpGrundfosON[9]; | mind[410]:=CrpalkeGrfs[4].ExternInputsStatus; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].PretokMax,lo:=5820,hi:=5821); |  | 410:CrpGrundfosON[9]:=Bit_0; | 410:CrpalkeGrfs[4].ExternInputsStatus:=Word_01; |  |  | 5821:CrpalkeGrfs[9].PretokMax:=Real_0;
mind_bool[411]:=CrpGrundfosStatusError[10]; | mind[411]:=CrpalkeGrfs[4].LocalSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].PretokMin,lo:=5822,hi:=5823); |  | 411:CrpGrundfosStatusError[10]:=Bit_0; | 411:CrpalkeGrfs[4].LocalSetupMode1:=Word_01; |  |  | 5823:CrpalkeGrfs[9].PretokMin:=Real_0;
mind_bool[412]:=CrpGrundfosStatusError[11]; | mind[412]:=CrpalkeGrfs[4].PreklopkaMode; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].PretokTrenutni,lo:=5824,hi:=5825); |  | 412:CrpGrundfosStatusError[11]:=Bit_0; | 412:CrpalkeGrfs[4].PreklopkaMode:=Word_01; |  |  | 5825:CrpalkeGrfs[9].PretokTrenutni:=Real_0;
mind_bool[413]:=CrpGrundfosStatusError[12]; | mind[413]:=CrpalkeGrfs[4].Relay1setup; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].PritiskMax,lo:=5826,hi:=5827); |  | 413:CrpGrundfosStatusError[12]:=Bit_0; | 413:CrpalkeGrfs[4].Relay1setup:=Word_01; |  |  | 5827:CrpalkeGrfs[9].PritiskMax:=Real_0;
mind_bool[414]:=CrpGrundfosStatusError[13]; | mind[414]:=CrpalkeGrfs[4].RemoteSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].PritiskTrenutni,lo:=5828,hi:=5829); |  | 414:CrpGrundfosStatusError[13]:=Bit_0; | 414:CrpalkeGrfs[4].RemoteSetupMode1:=Word_01; |  |  | 5829:CrpalkeGrfs[9].PritiskTrenutni:=Real_0;
mind_bool[415]:=CrpGrundfosStatusError[14]; | mind[415]:=CrpalkeGrfs[4].StatusCrpalke; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].ReferencaMotorjaHzV,lo:=5830,hi:=5831); |  | 415:CrpGrundfosStatusError[14]:=Bit_0; | 415:CrpalkeGrfs[4].StatusCrpalke:=Byte_0; |  |  | 5831:CrpalkeGrfs[9].ReferencaMotorjaHzV:=Real_0;
mind_bool[416]:=CrpGrundfosStatusError[1]; | mind[416]:=CrpalkeGrfs[4].StatusMode1; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].ReferencaRemote,lo:=5832,hi:=5833); |  | 416:CrpGrundfosStatusError[1]:=Bit_0; | 416:CrpalkeGrfs[4].StatusMode1:=Word_01; |  |  | 5833:CrpalkeGrfs[9].ReferencaRemote:=Real_0;
mind_bool[417]:=CrpGrundfosStatusError[2]; | mind[417]:=CrpalkeGrfs[4].StatusMode1co; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].StevecUr2h,lo:=5834,hi:=5835); |  | 417:CrpGrundfosStatusError[2]:=Bit_0; | 417:CrpalkeGrfs[4].StatusMode1co:=Byte_0; |  |  | 5835:CrpalkeGrfs[9].StevecUr2h:=Real_0;
mind_bool[418]:=CrpGrundfosStatusError[3]; | mind[418]:=CrpalkeGrfs[4].StatusMode1op; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].SystemFeedback,lo:=5836,hi:=5837); |  | 418:CrpGrundfosStatusError[3]:=Bit_0; | 418:CrpalkeGrfs[4].StatusMode1op:=Byte_0; |  |  | 5837:CrpalkeGrfs[9].SystemFeedback:=Real_0;
mind_bool[419]:=CrpGrundfosStatusError[4]; | mind[419]:=CrpalkeGrfs[4].StatusMode2; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].SystemReference,lo:=5838,hi:=5839); |  | 419:CrpGrundfosStatusError[4]:=Bit_0; | 419:CrpalkeGrfs[4].StatusMode2:=Word_01; |  |  | 5839:CrpalkeGrfs[9].SystemReference:=Real_0;
mind_bool[420]:=CrpGrundfosStatusError[5]; | mind[420]:=CrpalkeGrfs[4].StatusMode3; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].TemperaturaMotorja,lo:=5840,hi:=5841); |  | 420:CrpGrundfosStatusError[5]:=Bit_0; | 420:CrpalkeGrfs[4].StatusMode3:=Word_01; |  |  | 5841:CrpalkeGrfs[9].TemperaturaMotorja:=Real_0;
mind_bool[421]:=CrpGrundfosStatusError[6]; | mind[421]:=CrpalkeGrfs[5].AlarmActiveCode; |  |  | Read_Real(rVar:=CrpalkeGrfs[9].UreXC200,lo:=5842,hi:=5843); |  | 421:CrpGrundfosStatusError[6]:=Bit_0; | 421:CrpalkeGrfs[5].AlarmActiveCode:=Word_01; |  |  | 5843:CrpalkeGrfs[9].UreXC200:=Real_0;
mind_bool[422]:=CrpGrundfosStatusError[7]; | mind[422]:=CrpalkeGrfs[5].AlarmCodeLog1; |  |  | Read_Real(rVar:=CrpGrundfosTlakSP[1],lo:=5844,hi:=5845); |  | 422:CrpGrundfosStatusError[7]:=Bit_0; | 422:CrpalkeGrfs[5].AlarmCodeLog1:=Word_01; |  |  | 5845:CrpGrundfosTlakSP[1]:=Real_0;
mind_bool[423]:=CrpGrundfosStatusError[8]; | mind[423]:=CrpalkeGrfs[5].AlarmCodeLog2; |  |  | Read_Real(rVar:=CrpGrundfosTlakSP[2],lo:=5846,hi:=5847); |  | 423:CrpGrundfosStatusError[8]:=Bit_0; | 423:CrpalkeGrfs[5].AlarmCodeLog2:=Word_01; |  |  | 5847:CrpGrundfosTlakSP[2]:=Real_0;
mind_bool[424]:=CrpGrundfosStatusError[9]; | mind[424]:=CrpalkeGrfs[5].AlarmCodeLog3; |  |  | Read_Real(rVar:=CrpGrundfosTlakSP[3],lo:=5848,hi:=5849); |  | 424:CrpGrundfosStatusError[9]:=Bit_0; | 424:CrpalkeGrfs[5].AlarmCodeLog3:=Word_01; |  |  | 5849:CrpGrundfosTlakSP[3]:=Real_0;
mind_bool[425]:=DanfossHMKontOnOff[1]; | mind[425]:=CrpalkeGrfs[5].AlarmCodeLog4; |  |  | Read_Real(rVar:=CrpGrundfosTlakSP[4],lo:=5850,hi:=5851); |  | 425:DanfossHMKontOnOff[1]:=Bit_0; | 425:CrpalkeGrfs[5].AlarmCodeLog4:=Word_01; |  |  | 5851:CrpGrundfosTlakSP[4]:=Real_0;
mind_bool[426]:=DanfossHMKontOnOff[2]; | mind[426]:=CrpalkeGrfs[5].AlarmCodeLog5; |  |  | Read_Real(rVar:=CrpGrundfosTlakSP[5],lo:=5852,hi:=5853); |  | 426:DanfossHMKontOnOff[2]:=Bit_0; | 426:CrpalkeGrfs[5].AlarmCodeLog5:=Word_01; |  |  | 5853:CrpGrundfosTlakSP[5]:=Real_0;
mind_bool[427]:=DanfossHMKontOnOff[3]; | mind[427]:=CrpalkeGrfs[5].AlarmGroupXVH[0]; |  |  | Read_Real(rVar:=CrpGrundfosTlakSP[6],lo:=5854,hi:=5855); |  | 427:DanfossHMKontOnOff[3]:=Bit_0; | 427:CrpalkeGrfs[5].AlarmGroupXVH[0]:=Word_01; |  |  | 5855:CrpGrundfosTlakSP[6]:=Real_0;
mind_bool[428]:=DanfossHMKontOnOff[4]; | mind[428]:=CrpalkeGrfs[5].AlarmGroupXVH[10]; |  |  | Read_Real(rVar:=CrpGrundfosTlakSP[7],lo:=5856,hi:=5857); |  | 428:DanfossHMKontOnOff[4]:=Bit_0; | 428:CrpalkeGrfs[5].AlarmGroupXVH[10]:=Word_01; |  |  | 5857:CrpGrundfosTlakSP[7]:=Real_0;
mind_bool[429]:=DI_230VAC_OK; | mind[429]:=CrpalkeGrfs[5].AlarmGroupXVH[11]; |  |  | Read_Real(rVar:=Exp1TlakMin,lo:=5858,hi:=5859); |  | 429:DI_230VAC_OK:=Bit_0; | 429:CrpalkeGrfs[5].AlarmGroupXVH[11]:=Word_01; |  |  | 5859:Exp1TlakMin:=Real_0;
mind_bool[430]:=DI_24VAC_OK; | mind[430]:=CrpalkeGrfs[5].AlarmGroupXVH[12]; |  |  | Read_Real(rVar:=Exp2TlakMin,lo:=5860,hi:=5861); |  | 430:DI_24VAC_OK:=Bit_0; | 430:CrpalkeGrfs[5].AlarmGroupXVH[12]:=Word_01; |  |  | 5861:Exp2TlakMin:=Real_0;
mind_bool[431]:=DI_24VDC_OK; | mind[431]:=CrpalkeGrfs[5].AlarmGroupXVH[13]; |  |  | Read_Real(rVar:=HladStroj.ObratovalneUre,lo:=5862,hi:=5863); |  | 431:DI_24VDC_OK:=Bit_0; | 431:CrpalkeGrfs[5].AlarmGroupXVH[13]:=Word_01; |  |  | 5863:HladStroj.ObratovalneUre:=Real_0;
mind_bool[432]:=DI_AkumTopVodeAUTO; | mind[432]:=CrpalkeGrfs[5].AlarmGroupXVH[14]; |  |  | Read_Real(rVar:=HladStroj.PritiskSonda1,lo:=5864,hi:=5865); |  | 432:DI_AkumTopVodeAUTO:=Bit_0; | 432:CrpalkeGrfs[5].AlarmGroupXVH[14]:=Word_01; |  |  | 5865:HladStroj.PritiskSonda1:=Real_0;
mind_bool[433]:=DI_AkumTopVodeKontON; | mind[433]:=CrpalkeGrfs[5].AlarmGroupXVH[15]; |  |  | Read_Real(rVar:=HladStroj.PritiskSonda2,lo:=5866,hi:=5867); |  | 433:DI_AkumTopVodeKontON:=Bit_0; | 433:CrpalkeGrfs[5].AlarmGroupXVH[15]:=Word_01; |  |  | 5867:HladStroj.PritiskSonda2:=Real_0;
mind_bool[434]:=DI_CrpHM1AUTO; | mind[434]:=CrpalkeGrfs[5].AlarmGroupXVH[16]; |  |  | Read_Real(rVar:=HladStroj.PritiskSonda3,lo:=5868,hi:=5869); |  | 434:DI_CrpHM1AUTO:=Bit_0; | 434:CrpalkeGrfs[5].AlarmGroupXVH[16]:=Word_01; |  |  | 5869:HladStroj.PritiskSonda3:=Real_0;
mind_bool[435]:=DI_CrpHM1endOFFtoON; | mind[435]:=CrpalkeGrfs[5].AlarmGroupXVH[1]; |  |  | Read_Real(rVar:=HladStroj.PritiskSonda4,lo:=5870,hi:=5871); |  | 435:DI_CrpHM1endOFFtoON:=Bit_0; | 435:CrpalkeGrfs[5].AlarmGroupXVH[1]:=Word_01; |  |  | 5871:HladStroj.PritiskSonda4:=Real_0;
mind_bool[436]:=DI_CrpHM1ERR; | mind[436]:=CrpalkeGrfs[5].AlarmGroupXVH[2]; |  |  | Read_Real(rVar:=HladStroj.TempH2OvhodIzparilnika,lo:=5872,hi:=5873); |  | 436:DI_CrpHM1ERR:=Bit_0; | 436:CrpalkeGrfs[5].AlarmGroupXVH[2]:=Word_01; |  |  | 5873:HladStroj.TempH2OvhodIzparilnika:=Real_0;
mind_bool[437]:=DI_CrpHM1kontON; | mind[437]:=CrpalkeGrfs[5].AlarmGroupXVH[3]; |  |  | Read_Real(rVar:=HladStroj.TempIzhodnaSonda1,lo:=5874,hi:=5875); |  | 437:DI_CrpHM1kontON:=Bit_0; | 437:CrpalkeGrfs[5].AlarmGroupXVH[3]:=Word_01; |  |  | 5875:HladStroj.TempIzhodnaSonda1:=Real_0;
mind_bool[438]:=DI_CrpHM2AUTO; | mind[438]:=CrpalkeGrfs[5].AlarmGroupXVH[4]; |  |  | Read_Real(rVar:=HladStroj.TempIzhodnaSonda3,lo:=5876,hi:=5877); |  | 438:DI_CrpHM2AUTO:=Bit_0; | 438:CrpalkeGrfs[5].AlarmGroupXVH[4]:=Word_01; |  |  | 5877:HladStroj.TempIzhodnaSonda3:=Real_0;
mind_bool[439]:=DI_CrpHM2endOFFtoON; | mind[439]:=CrpalkeGrfs[5].AlarmGroupXVH[5]; |  |  | Read_Real(rVar:=HladStroj.TempSetPoint,lo:=5878,hi:=5879); |  | 439:DI_CrpHM2endOFFtoON:=Bit_0; | 439:CrpalkeGrfs[5].AlarmGroupXVH[5]:=Word_01; |  |  | 5879:HladStroj.TempSetPoint:=Real_0;
mind_bool[440]:=DI_CrpHM2ERR; | mind[440]:=CrpalkeGrfs[5].AlarmGroupXVH[6]; |  |  | Read_Real(rVar:=Klima[1].HitrostVentilatorjev,lo:=5880,hi:=5881); |  | 440:DI_CrpHM2ERR:=Bit_0; | 440:CrpalkeGrfs[5].AlarmGroupXVH[6]:=Word_01; |  |  | 5881:Klima[1].HitrostVentilatorjev:=Real_0;
mind_bool[441]:=DI_CrpHM2kontON; | mind[441]:=CrpalkeGrfs[5].AlarmGroupXVH[7]; |  |  | Read_Real(rVar:=Klima[1].NastTempProstora,lo:=5882,hi:=5883); |  | 441:DI_CrpHM2kontON:=Bit_0; | 441:CrpalkeGrfs[5].AlarmGroupXVH[7]:=Word_01; |  |  | 5883:Klima[1].NastTempProstora:=Real_0;
mind_bool[442]:=DI_CrpHM3AUTO; | mind[442]:=CrpalkeGrfs[5].AlarmGroupXVH[8]; |  |  | Read_Real(rVar:=Klima[1].ObratovalneUre,lo:=5884,hi:=5885); |  | 442:DI_CrpHM3AUTO:=Bit_0; | 442:CrpalkeGrfs[5].AlarmGroupXVH[8]:=Word_01; |  |  | 5885:Klima[1].ObratovalneUre:=Real_0;
mind_bool[443]:=DI_CrpHM3endOFFtoON; | mind[443]:=CrpalkeGrfs[5].AlarmGroupXVH[9]; |  |  | Read_Real(rVar:=Klima[1].ProtizmrzZasc,lo:=5886,hi:=5887); |  | 443:DI_CrpHM3endOFFtoON:=Bit_0; | 443:CrpalkeGrfs[5].AlarmGroupXVH[9]:=Word_01; |  |  | 5887:Klima[1].ProtizmrzZasc:=Real_0;
mind_bool[444]:=DI_CrpHM3ERR; | mind[444]:=CrpalkeGrfs[5].AlarmQSD1; |  |  | Read_Real(rVar:=Klima[1].RezimDelovanja,lo:=5888,hi:=5889); |  | 444:DI_CrpHM3ERR:=Bit_0; | 444:CrpalkeGrfs[5].AlarmQSD1:=Word_01; |  |  | 5889:Klima[1].RezimDelovanja:=Real_0;
mind_bool[445]:=DI_CrpHM3kontON; | mind[445]:=CrpalkeGrfs[5].AlarmQSD2; |  |  | Read_Real(rVar:=Klima[1].TemperaturaDovoda,lo:=5890,hi:=5891); |  | 445:DI_CrpHM3kontON:=Bit_0; | 445:CrpalkeGrfs[5].AlarmQSD2:=Word_01; |  |  | 5891:Klima[1].TemperaturaDovoda:=Real_0;
mind_bool[446]:=DI_CrpHM4AUTO; | mind[446]:=CrpalkeGrfs[5].AlarmStart1; |  |  | Read_Real(rVar:=Klima[1].TemperaturaProstora,lo:=5892,hi:=5893); |  | 446:DI_CrpHM4AUTO:=Bit_0; | 446:CrpalkeGrfs[5].AlarmStart1:=Word_01; |  |  | 5893:Klima[1].TemperaturaProstora:=Real_0;
mind_bool[447]:=DI_CrpHM4endOFFtoON; | mind[447]:=CrpalkeGrfs[5].AlarmStart2; |  |  | Read_Real(rVar:=Klima[1].TempPredRekN2,lo:=5894,hi:=5895); |  | 447:DI_CrpHM4endOFFtoON:=Bit_0; | 447:CrpalkeGrfs[5].AlarmStart2:=Word_01; |  |  | 5895:Klima[1].TempPredRekN2:=Real_0;
mind_bool[448]:=DI_CrpHM4ERR; | mind[448]:=CrpalkeGrfs[5].AlarmStop1; |  |  | Read_Real(rVar:=Klima[1].TempZaRekN2,lo:=5896,hi:=5897); |  | 448:DI_CrpHM4ERR:=Bit_0; | 448:CrpalkeGrfs[5].AlarmStop1:=Word_01; |  |  | 5897:Klima[1].TempZaRekN2:=Real_0;
mind_bool[449]:=DI_CrpHM4kontON; | mind[449]:=CrpalkeGrfs[5].AlarmStop2; |  |  | Read_Real(rVar:=Klima[1].TlakDovKanal,lo:=5898,hi:=5899); |  | 449:DI_CrpHM4kontON:=Bit_0; | 449:CrpalkeGrfs[5].AlarmStop2:=Word_01; |  |  | 5899:Klima[1].TlakDovKanal:=Real_0;
mind_bool[450]:=DI_CrpHM5AUTO; | mind[450]:=CrpalkeGrfs[5].AlarmStop3; |  |  | Read_Real(rVar:=Klima[1].TlakOdvodKanal,lo:=5900,hi:=5901); |  | 450:DI_CrpHM5AUTO:=Bit_0; | 450:CrpalkeGrfs[5].AlarmStop3:=Word_01; |  |  | 5901:Klima[1].TlakOdvodKanal:=Real_0;
mind_bool[451]:=DI_CrpHM6AUTO; | mind[451]:=CrpalkeGrfs[5].AlarmSurv1; |  |  | Read_Real(rVar:=Klima[1].VlagaDovoda,lo:=5902,hi:=5903); |  | 451:DI_CrpHM6AUTO:=Bit_0; | 451:CrpalkeGrfs[5].AlarmSurv1:=Word_01; |  |  | 5903:Klima[1].VlagaDovoda:=Real_0;
mind_bool[452]:=DI_CrpHM7AUTO; | mind[452]:=CrpalkeGrfs[5].AlarmSurv2; |  |  | Read_Real(rVar:=Klima[1].VlagaVprostor,lo:=5904,hi:=5905); |  | 452:DI_CrpHM7AUTO:=Bit_0; | 452:CrpalkeGrfs[5].AlarmSurv2:=Word_01; |  |  | 5905:Klima[1].VlagaVprostor:=Real_0;
mind_bool[453]:=DI_CrpHM8AUTO; | mind[453]:=CrpalkeGrfs[5].ControlSource; |  |  | Read_Real(rVar:=Klima[1].ZunanjaTemp,lo:=5906,hi:=5907); |  | 453:DI_CrpHM8AUTO:=Bit_0; | 453:CrpalkeGrfs[5].ControlSource:=Word_01; |  |  | 5907:Klima[1].ZunanjaTemp:=Real_0;
mind_bool[454]:=DI_CrpMN1AUTO; | mind[454]:=CrpalkeGrfs[5].ExternInputSetup; |  |  | Read_Real(rVar:=Klima[2].HitrostVentilatorjev,lo:=5908,hi:=5909); |  | 454:DI_CrpMN1AUTO:=Bit_0; | 454:CrpalkeGrfs[5].ExternInputSetup:=Word_01; |  |  | 5909:Klima[2].HitrostVentilatorjev:=Real_0;
mind_bool[455]:=DI_CrpMN1kontON; | mind[455]:=CrpalkeGrfs[5].ExternInputsStatus; |  |  | Read_Real(rVar:=Klima[2].NastTempProstora,lo:=5910,hi:=5911); |  | 455:DI_CrpMN1kontON:=Bit_0; | 455:CrpalkeGrfs[5].ExternInputsStatus:=Word_01; |  |  | 5911:Klima[2].NastTempProstora:=Real_0;
mind_bool[456]:=DI_CrpTM10AUTO; | mind[456]:=CrpalkeGrfs[5].LocalSetupMode1; |  |  | Read_Real(rVar:=Klima[2].ObratovalneUre,lo:=5912,hi:=5913); |  | 456:DI_CrpTM10AUTO:=Bit_0; | 456:CrpalkeGrfs[5].LocalSetupMode1:=Word_01; |  |  | 5913:Klima[2].ObratovalneUre:=Real_0;
mind_bool[457]:=DI_CrpTM11TM12AUTO; | mind[457]:=CrpalkeGrfs[5].PreklopkaMode; |  |  | Read_Real(rVar:=Klima[2].ProtizmrzZasc,lo:=5914,hi:=5915); |  | 457:DI_CrpTM11TM12AUTO:=Bit_0; | 457:CrpalkeGrfs[5].PreklopkaMode:=Word_01; |  |  | 5915:Klima[2].ProtizmrzZasc:=Real_0;
mind_bool[458]:=DI_CrpTM11TM12kontON; | mind[458]:=CrpalkeGrfs[5].Relay1setup; |  |  | Read_Real(rVar:=Klima[2].RezimDelovanja,lo:=5916,hi:=5917); |  | 458:DI_CrpTM11TM12kontON:=Bit_0; | 458:CrpalkeGrfs[5].Relay1setup:=Word_01; |  |  | 5917:Klima[2].RezimDelovanja:=Real_0;
mind_bool[459]:=DI_CrpTM1AUTO; | mind[459]:=CrpalkeGrfs[5].RemoteSetupMode1; |  |  | Read_Real(rVar:=Klima[2].TemperaturaDovoda,lo:=5918,hi:=5919); |  | 459:DI_CrpTM1AUTO:=Bit_0; | 459:CrpalkeGrfs[5].RemoteSetupMode1:=Word_01; |  |  | 5919:Klima[2].TemperaturaDovoda:=Real_0;
mind_bool[460]:=DI_CrpTM2AUTO; | mind[460]:=CrpalkeGrfs[5].StatusCrpalke; |  |  | Read_Real(rVar:=Klima[2].TemperaturaProstora,lo:=5920,hi:=5921); |  | 460:DI_CrpTM2AUTO:=Bit_0; | 460:CrpalkeGrfs[5].StatusCrpalke:=Byte_0; |  |  | 5921:Klima[2].TemperaturaProstora:=Real_0;
mind_bool[461]:=DI_CrpTM3AUTO; | mind[461]:=CrpalkeGrfs[5].StatusMode1; |  |  | Read_Real(rVar:=Klima[2].TempPredRekN2,lo:=5922,hi:=5923); |  | 461:DI_CrpTM3AUTO:=Bit_0; | 461:CrpalkeGrfs[5].StatusMode1:=Word_01; |  |  | 5923:Klima[2].TempPredRekN2:=Real_0;
mind_bool[462]:=DI_CrpTM4AUTO; | mind[462]:=CrpalkeGrfs[5].StatusMode1co; |  |  | Read_Real(rVar:=Klima[2].TempZaRekN2,lo:=5924,hi:=5925); |  | 462:DI_CrpTM4AUTO:=Bit_0; | 462:CrpalkeGrfs[5].StatusMode1co:=Byte_0; |  |  | 5925:Klima[2].TempZaRekN2:=Real_0;
mind_bool[463]:=DI_CrpTM5AUTO; | mind[463]:=CrpalkeGrfs[5].StatusMode1op; |  |  | Read_Real(rVar:=Klima[2].TlakDovKanal,lo:=5926,hi:=5927); |  | 463:DI_CrpTM5AUTO:=Bit_0; | 463:CrpalkeGrfs[5].StatusMode1op:=Byte_0; |  |  | 5927:Klima[2].TlakDovKanal:=Real_0;
mind_bool[464]:=DI_CrpTM6AUTO; | mind[464]:=CrpalkeGrfs[5].StatusMode2; |  |  | Read_Real(rVar:=Klima[2].TlakOdvodKanal,lo:=5928,hi:=5929); |  | 464:DI_CrpTM6AUTO:=Bit_0; | 464:CrpalkeGrfs[5].StatusMode2:=Word_01; |  |  | 5929:Klima[2].TlakOdvodKanal:=Real_0;
mind_bool[465]:=DI_CrpTM7AUTO; | mind[465]:=CrpalkeGrfs[5].StatusMode3; |  |  | Read_Real(rVar:=Klima[2].VlagaDovoda,lo:=5930,hi:=5931); |  | 465:DI_CrpTM7AUTO:=Bit_0; | 465:CrpalkeGrfs[5].StatusMode3:=Word_01; |  |  | 5931:Klima[2].VlagaDovoda:=Real_0;
mind_bool[466]:=DI_CrpTM8AUTO; | mind[466]:=CrpalkeGrfs[6].AlarmActiveCode; |  |  | Read_Real(rVar:=Klima[2].VlagaVprostor,lo:=5932,hi:=5933); |  | 466:DI_CrpTM8AUTO:=Bit_0; | 466:CrpalkeGrfs[6].AlarmActiveCode:=Word_01; |  |  | 5933:Klima[2].VlagaVprostor:=Real_0;
mind_bool[467]:=DI_CrpTM9AUTO; | mind[467]:=CrpalkeGrfs[6].AlarmCodeLog1; |  |  | Read_Real(rVar:=Klima[2].ZunanjaTemp,lo:=5934,hi:=5935); |  | 467:DI_CrpTM9AUTO:=Bit_0; | 467:CrpalkeGrfs[6].AlarmCodeLog1:=Word_01; |  |  | 5935:Klima[2].ZunanjaTemp:=Real_0;
mind_bool[468]:=DI_GlStikaloDieselON; | mind[468]:=CrpalkeGrfs[6].AlarmCodeLog2; |  |  | Read_Real(rVar:=rVersion,lo:=5936,hi:=5937); |  | 468:DI_GlStikaloDieselON:=Bit_0; | 468:CrpalkeGrfs[6].AlarmCodeLog2:=Word_01; |  |  | 5937:rVersion:=Real_0;
mind_bool[469]:=DI_GlStikaloMrezaON; | mind[469]:=CrpalkeGrfs[6].AlarmCodeLog3; |  |  | Read_Real(rVar:=SenzorTempTIA[1],lo:=5938,hi:=5939); |  | 469:DI_GlStikaloMrezaON:=Bit_0; | 469:CrpalkeGrfs[6].AlarmCodeLog3:=Word_01; |  |  | 5939:SenzorTempTIA[1]:=Real_0;
mind_bool[470]:=DI_GlStikaloUpsON; | mind[470]:=CrpalkeGrfs[6].AlarmCodeLog4; |  |  | Read_Real(rVar:=SenzorTempTIA[2],lo:=5940,hi:=5941); |  | 470:DI_GlStikaloUpsON:=Bit_0; | 470:CrpalkeGrfs[6].AlarmCodeLog4:=Word_01; |  |  | 5941:SenzorTempTIA[2]:=Real_0;
mind_bool[471]:=DI_HladStAUTO; | mind[471]:=CrpalkeGrfs[6].AlarmCodeLog5; |  |  | Read_Real(rVar:=SenzorTempTIA[3],lo:=5942,hi:=5943); |  | 471:DI_HladStAUTO:=Bit_0; | 471:CrpalkeGrfs[6].AlarmCodeLog5:=Word_01; |  |  | 5943:SenzorTempTIA[3]:=Real_0;
mind_bool[472]:=DI_HladStCrpHladH2OON; | mind[472]:=CrpalkeGrfs[6].AlarmGroupXVH[0]; |  |  | Read_Real(rVar:=SenzorTempTIA[4],lo:=5944,hi:=5945); |  | 472:DI_HladStCrpHladH2OON:=Bit_0; | 472:CrpalkeGrfs[6].AlarmGroupXVH[0]:=Word_01; |  |  | 5945:SenzorTempTIA[4]:=Real_0;
mind_bool[473]:=DI_HladStERR; | mind[473]:=CrpalkeGrfs[6].AlarmGroupXVH[10]; |  |  | Read_Real(rVar:=SenzorVlagaHIA[1],lo:=5946,hi:=5947); |  | 473:DI_HladStERR:=Bit_0; | 473:CrpalkeGrfs[6].AlarmGroupXVH[10]:=Word_01; |  |  | 5947:SenzorVlagaHIA[1]:=Real_0;
mind_bool[474]:=DI_Klima1ERR; | mind[474]:=CrpalkeGrfs[6].AlarmGroupXVH[11]; |  |  | Read_Real(rVar:=SenzorVlagaHIA[2],lo:=5948,hi:=5949); |  | 474:DI_Klima1ERR:=Bit_0; | 474:CrpalkeGrfs[6].AlarmGroupXVH[11]:=Word_01; |  |  | 5949:SenzorVlagaHIA[2]:=Real_0;
mind_bool[475]:=DI_Klima1filterZAM; | mind[475]:=CrpalkeGrfs[6].AlarmGroupXVH[12]; |  |  | Read_Real(rVar:=SenzorVlagaHIA[3],lo:=5950,hi:=5951); |  | 475:DI_Klima1filterZAM:=Bit_0; | 475:CrpalkeGrfs[6].AlarmGroupXVH[12]:=Word_01; |  |  | 5951:SenzorVlagaHIA[3]:=Real_0;
mind_bool[476]:=DI_Klima1FIRE; | mind[476]:=CrpalkeGrfs[6].AlarmGroupXVH[13]; |  |  | Read_Real(rVar:=SenzorVlagaHIA[4],lo:=5952,hi:=5953); |  | 476:DI_Klima1FIRE:=Bit_0; | 476:CrpalkeGrfs[6].AlarmGroupXVH[13]:=Word_01; |  |  | 5953:SenzorVlagaHIA[4]:=Real_0;
mind_bool[477]:=DI_Klima1OFFtoON; | mind[477]:=CrpalkeGrfs[6].AlarmGroupXVH[14]; |  |  | Read_Real(rVar:=TEgrelecTempMAX,lo:=5954,hi:=5955); |  | 477:DI_Klima1OFFtoON:=Bit_0; | 477:CrpalkeGrfs[6].AlarmGroupXVH[14]:=Word_01; |  |  | 5955:TEgrelecTempMAX:=Real_0;
mind_bool[478]:=DI_Klima1ON; | mind[478]:=CrpalkeGrfs[6].AlarmGroupXVH[15]; |  |  | Read_Real(rVar:=TEgrelecTempMIN,lo:=5956,hi:=5957); |  | 478:DI_Klima1ON:=Bit_0; | 478:CrpalkeGrfs[6].AlarmGroupXVH[15]:=Word_01; |  |  | 5957:TEgrelecTempMIN:=Real_0;
mind_bool[479]:=DI_Klima1zascStON; | mind[479]:=CrpalkeGrfs[6].AlarmGroupXVH[16]; |  |  | Read_Real(rVar:=TempAlarmPoint,lo:=5958,hi:=5959); |  | 479:DI_Klima1zascStON:=Bit_0; | 479:CrpalkeGrfs[6].AlarmGroupXVH[16]:=Word_01; |  |  | 5959:TempAlarmPoint:=Real_0;
mind_bool[480]:=DI_Klima2ERR; | mind[480]:=CrpalkeGrfs[6].AlarmGroupXVH[1]; |  |  | Read_Real(rVar:=TempTIApovprecna,lo:=5960,hi:=5961); |  | 480:DI_Klima2ERR:=Bit_0; | 480:CrpalkeGrfs[6].AlarmGroupXVH[1]:=Word_01; |  |  | 5961:TempTIApovprecna:=Real_0;
mind_bool[481]:=DI_Klima2filterZAM; | mind[481]:=CrpalkeGrfs[6].AlarmGroupXVH[2]; |  |  | Read_Real(rVar:=ToplPost.HKdotokNastTemp,lo:=5962,hi:=5963); |  | 481:DI_Klima2filterZAM:=Bit_0; | 481:CrpalkeGrfs[6].AlarmGroupXVH[2]:=Word_01; |  |  | 5963:ToplPost.HKdotokNastTemp:=Real_0;
mind_bool[482]:=DI_Klima2FIRE; | mind[482]:=CrpalkeGrfs[6].AlarmGroupXVH[3]; |  |  | Read_Real(rVar:=ToplPost.HKdotokTemp,lo:=5964,hi:=5965); |  | 482:DI_Klima2FIRE:=Bit_0; | 482:CrpalkeGrfs[6].AlarmGroupXVH[3]:=Word_01; |  |  | 5965:ToplPost.HKdotokTemp:=Real_0;
mind_bool[483]:=DI_Klima2OFFtoON; | mind[483]:=CrpalkeGrfs[6].AlarmGroupXVH[4]; |  |  | Read_Real(rVar:=ToplPost.HKpovtatekTemp,lo:=5966,hi:=5967); |  | 483:DI_Klima2OFFtoON:=Bit_0; | 483:CrpalkeGrfs[6].AlarmGroupXVH[4]:=Word_01; |  |  | 5967:ToplPost.HKpovtatekTemp:=Real_0;
mind_bool[484]:=DI_Klima2ON; | mind[484]:=CrpalkeGrfs[6].AlarmGroupXVH[5]; |  |  | Read_Real(rVar:=ToplPost.HKpovtratekNastTemp,lo:=5968,hi:=5969); |  | 484:DI_Klima2ON:=Bit_0; | 484:CrpalkeGrfs[6].AlarmGroupXVH[5]:=Word_01; |  |  | 5969:ToplPost.HKpovtratekNastTemp:=Real_0;
mind_bool[485]:=DI_Klima2zascStON; | mind[485]:=CrpalkeGrfs[6].AlarmGroupXVH[6]; |  |  | Read_Real(rVar:=ToplPost.HKzunanjaTemp,lo:=5970,hi:=5971); |  | 485:DI_Klima2zascStON:=Bit_0; | 485:CrpalkeGrfs[6].AlarmGroupXVH[6]:=Word_01; |  |  | 5971:ToplPost.HKzunanjaTemp:=Real_0;
mind_bool[486]:=DI_Komp1ERR; | mind[486]:=CrpalkeGrfs[6].AlarmGroupXVH[7]; |  |  | Read_Real(rVar:=ToplPost.TVdotokNastTemp,lo:=5972,hi:=5973); |  | 486:DI_Komp1ERR:=Bit_0; | 486:CrpalkeGrfs[6].AlarmGroupXVH[7]:=Word_01; |  |  | 5973:ToplPost.TVdotokNastTemp:=Real_0;
mind_bool[487]:=DI_Komp1ON; | mind[487]:=CrpalkeGrfs[6].AlarmGroupXVH[8]; |  |  | Read_Real(rVar:=ToplPost.TVdotokTemp,lo:=5974,hi:=5975); |  | 487:DI_Komp1ON:=Bit_0; | 487:CrpalkeGrfs[6].AlarmGroupXVH[8]:=Word_01; |  |  | 5975:ToplPost.TVdotokTemp:=Real_0;
mind_bool[488]:=DI_Komp2ERR; | mind[488]:=CrpalkeGrfs[6].AlarmGroupXVH[9]; |  |  | Read_Real(rVar:=ToplPost.TVpovratekTemp,lo:=5976,hi:=5977); |  | 488:DI_Komp2ERR:=Bit_0; | 488:CrpalkeGrfs[6].AlarmGroupXVH[9]:=Word_01; |  |  | 5977:ToplPost.TVpovratekTemp:=Real_0;
mind_bool[489]:=DI_Komp2ON; | mind[489]:=CrpalkeGrfs[6].AlarmQSD1; |  |  | Read_Real(rVar:=ToplPost.TVrezervoarTemp,lo:=5978,hi:=5979); |  | 489:DI_Komp2ON:=Bit_0; | 489:CrpalkeGrfs[6].AlarmQSD1:=Word_01; |  |  | 5979:ToplPost.TVrezervoarTemp:=Real_0;
mind_bool[490]:=DI_Kond1AUTO; | mind[490]:=CrpalkeGrfs[6].AlarmQSD2; |  |  | Read_Real(rVar:=TYventilMax[1],lo:=5980,hi:=5981); |  | 490:DI_Kond1AUTO:=Bit_0; | 490:CrpalkeGrfs[6].AlarmQSD2:=Word_01; |  |  | 5981:TYventilMax[1]:=Real_0;
mind_bool[491]:=DI_Kond1FS1FS2; | mind[491]:=CrpalkeGrfs[6].AlarmStart1; |  |  | Read_Real(rVar:=TYventilMax[2],lo:=5982,hi:=5983); |  | 491:DI_Kond1FS1FS2:=Bit_0; | 491:CrpalkeGrfs[6].AlarmStart1:=Word_01; |  |  | 5983:TYventilMax[2]:=Real_0;
mind_bool[492]:=DI_Kond1ON; | mind[492]:=CrpalkeGrfs[6].AlarmStart2; |  |  | Read_Real(rVar:=TYventilMax[3],lo:=5984,hi:=5985); |  | 492:DI_Kond1ON:=Bit_0; | 492:CrpalkeGrfs[6].AlarmStart2:=Word_01; |  |  | 5985:TYventilMax[3]:=Real_0;
mind_bool[493]:=DI_Kond1zascStON; | mind[493]:=CrpalkeGrfs[6].AlarmStop1; |  |  | Read_Real(rVar:=TYventilMax[4],lo:=5986,hi:=5987); |  | 493:DI_Kond1zascStON:=Bit_0; | 493:CrpalkeGrfs[6].AlarmStop1:=Word_01; |  |  | 5987:TYventilMax[4]:=Real_0;
mind_bool[494]:=DI_Kond2AUTO; | mind[494]:=CrpalkeGrfs[6].AlarmStop2; |  |  | Read_Real(rVar:=TYventilMin[1],lo:=5988,hi:=5989); |  | 494:DI_Kond2AUTO:=Bit_0; | 494:CrpalkeGrfs[6].AlarmStop2:=Word_01; |  |  | 5989:TYventilMin[1]:=Real_0;
mind_bool[495]:=DI_Kond2FS1FS2; | mind[495]:=CrpalkeGrfs[6].AlarmStop3; |  |  | Read_Real(rVar:=TYventilMin[2],lo:=5990,hi:=5991); |  | 495:DI_Kond2FS1FS2:=Bit_0; | 495:CrpalkeGrfs[6].AlarmStop3:=Word_01; |  |  | 5991:TYventilMin[2]:=Real_0;
mind_bool[496]:=DI_Kond2ON; | mind[496]:=CrpalkeGrfs[6].AlarmSurv1; |  |  | Read_Real(rVar:=TYventilMin[3],lo:=5992,hi:=5993); |  | 496:DI_Kond2ON:=Bit_0; | 496:CrpalkeGrfs[6].AlarmSurv1:=Word_01; |  |  | 5993:TYventilMin[3]:=Real_0;
mind_bool[497]:=DI_Kond2zascStON; | mind[497]:=CrpalkeGrfs[6].AlarmSurv2; |  |  | Read_Real(rVar:=TYventilMin[4],lo:=5994,hi:=5995); |  | 497:DI_Kond2zascStON:=Bit_0; | 497:CrpalkeGrfs[6].AlarmSurv2:=Word_01; |  |  | 5995:TYventilMin[4]:=Real_0;
mind_bool[498]:=DI_Kond3AUTO; | mind[498]:=CrpalkeGrfs[6].ControlSource; |  |  | Read_Real(rVar:=TYventilTempRazlika[1],lo:=5996,hi:=5997); |  | 498:DI_Kond3AUTO:=Bit_0; | 498:CrpalkeGrfs[6].ControlSource:=Word_01; |  |  | 5997:TYventilTempRazlika[1]:=Real_0;
mind_bool[499]:=DI_Kond3FS1FS2; | mind[499]:=CrpalkeGrfs[6].ExternInputSetup; |  |  | Read_Real(rVar:=TYventilTempRazlika[2],lo:=5998,hi:=5999); |  | 499:DI_Kond3FS1FS2:=Bit_0; | 499:CrpalkeGrfs[6].ExternInputSetup:=Word_01; |  |  | 5999:TYventilTempRazlika[2]:=Real_0;
mind_bool[500]:=DI_Kond3ON; | mind[500]:=CrpalkeGrfs[6].ExternInputsStatus; |  |  | Read_Real(rVar:=TYventilTempRazlika[3],lo:=6000,hi:=6001); |  | 500:DI_Kond3ON:=Bit_0; | 500:CrpalkeGrfs[6].ExternInputsStatus:=Word_01; |  |  | 6001:TYventilTempRazlika[3]:=Real_0;
mind_bool[501]:=DI_Kond3zascStON; | mind[501]:=CrpalkeGrfs[6].LocalSetupMode1; |  |  | Read_Real(rVar:=TYventilTempRazlika[4],lo:=6002,hi:=6003); |  | 501:DI_Kond3zascStON:=Bit_0; | 501:CrpalkeGrfs[6].LocalSetupMode1:=Word_01; |  |  | 6003:TYventilTempRazlika[4]:=Real_0;
mind_bool[502]:=DI_Lop1PL1Odprta; | mind[502]:=CrpalkeGrfs[6].PreklopkaMode; |  |  | Read_Real(rVar:=ValAI_Temp1B1,lo:=6004,hi:=6005); |  | 502:DI_Lop1PL1Odprta:=Bit_0; | 502:CrpalkeGrfs[6].PreklopkaMode:=Word_01; |  |  | 6005:ValAI_Temp1B1:=Real_0;
mind_bool[503]:=DI_Lop1PL1Zaprta; | mind[503]:=CrpalkeGrfs[6].Relay1setup; |  |  | Read_Real(rVar:=ValAI_Temp1B2,lo:=6006,hi:=6007); |  | 503:DI_Lop1PL1Zaprta:=Bit_0; | 503:CrpalkeGrfs[6].Relay1setup:=Word_01; |  |  | 6007:ValAI_Temp1B2:=Real_0;
mind_bool[504]:=DI_Lop1PL2Odprta; | mind[504]:=CrpalkeGrfs[6].RemoteSetupMode1; |  |  | Read_Real(rVar:=ValAI_Temp1B3,lo:=6008,hi:=6009); |  | 504:DI_Lop1PL2Odprta:=Bit_0; | 504:CrpalkeGrfs[6].RemoteSetupMode1:=Word_01; |  |  | 6009:ValAI_Temp1B3:=Real_0;
mind_bool[505]:=DI_Lop1PL2Zaprta; | mind[505]:=CrpalkeGrfs[6].StatusCrpalke; |  |  | Read_Real(rVar:=ValAI_Temp2B2,lo:=6010,hi:=6011); |  | 505:DI_Lop1PL2Zaprta:=Bit_0; | 505:CrpalkeGrfs[6].StatusCrpalke:=Byte_0; |  |  | 6011:ValAI_Temp2B2:=Real_0;
mind_bool[506]:=DI_Lop1PL3Odprta; | mind[506]:=CrpalkeGrfs[6].StatusMode1; |  |  | Read_Real(rVar:=ValAI_Temp2B3,lo:=6012,hi:=6013); |  | 506:DI_Lop1PL3Odprta:=Bit_0; | 506:CrpalkeGrfs[6].StatusMode1:=Word_01; |  |  | 6013:ValAI_Temp2B3:=Real_0;
mind_bool[507]:=DI_Lop1PL3Zaprta; | mind[507]:=CrpalkeGrfs[6].StatusMode1co; |  |  | Read_Real(rVar:=ValAI_TempHB2,lo:=6014,hi:=6015); |  | 507:DI_Lop1PL3Zaprta:=Bit_0; | 507:CrpalkeGrfs[6].StatusMode1co:=Byte_0; |  |  | 6015:ValAI_TempHB2:=Real_0;
mind_bool[508]:=DI_Lop3Y1Odprta; | mind[508]:=CrpalkeGrfs[6].StatusMode1op; |  |  | Read_Real(rVar:=ValAI_TempHB4,lo:=6016,hi:=6017); |  | 508:DI_Lop3Y1Odprta:=Bit_0; | 508:CrpalkeGrfs[6].StatusMode1op:=Byte_0; |  |  | 6017:ValAI_TempHB4:=Real_0;
mind_bool[509]:=DI_Lop3Y1Zaprta; | mind[509]:=CrpalkeGrfs[6].StatusMode2; |  |  | Read_Real(rVar:=ValAI_TempHB9,lo:=6018,hi:=6019); |  | 509:DI_Lop3Y1Zaprta:=Bit_0; | 509:CrpalkeGrfs[6].StatusMode2:=Word_01; |  |  | 6019:ValAI_TempHB9:=Real_0;
mind_bool[510]:=DI_Lop4Y1Odprta; | mind[510]:=CrpalkeGrfs[6].StatusMode3; |  |  | Read_Real(rVar:=ValAI_TempTB1,lo:=6020,hi:=6021); |  | 510:DI_Lop4Y1Odprta:=Bit_0; | 510:CrpalkeGrfs[6].StatusMode3:=Word_01; |  |  | 6021:ValAI_TempTB1:=Real_0;
mind_bool[511]:=DI_Lop4Y1Zaprta; | mind[511]:=CrpalkeGrfs[7].AlarmActiveCode; |  |  | Read_Real(rVar:=ValAI_TempTB10,lo:=6022,hi:=6023); |  | 511:DI_Lop4Y1Zaprta:=Bit_0; | 511:CrpalkeGrfs[7].AlarmActiveCode:=Word_01; |  |  | 6023:ValAI_TempTB10:=Real_0;
mind_bool[512]:=DI_PotrditevAlarmov; | mind[512]:=CrpalkeGrfs[7].AlarmCodeLog1; |  |  | Read_Real(rVar:=ValAI_TempTB2,lo:=6024,hi:=6025); |  | 512:DI_PotrditevAlarmov:=Bit_0; | 512:CrpalkeGrfs[7].AlarmCodeLog1:=Word_01; |  |  | 6025:ValAI_TempTB2:=Real_0;
mind_bool[513]:=DI_RazlitjeVodeEXP1; | mind[513]:=CrpalkeGrfs[7].AlarmCodeLog2; |  |  | Read_Real(rVar:=ValAI_TempTB3,lo:=6026,hi:=6027); |  | 513:DI_RazlitjeVodeEXP1:=Bit_0; | 513:CrpalkeGrfs[7].AlarmCodeLog2:=Word_01; |  |  | 6027:ValAI_TempTB3:=Real_0;
mind_bool[514]:=DI_RazlitjeVodeEXP2; | mind[514]:=CrpalkeGrfs[7].AlarmCodeLog3; |  |  | Read_Real(rVar:=ValAI_TempTB4,lo:=6028,hi:=6029); |  | 514:DI_RazlitjeVodeEXP2:=Bit_0; | 514:CrpalkeGrfs[7].AlarmCodeLog3:=Word_01; |  |  | 6029:ValAI_TempTB4:=Real_0;
mind_bool[515]:=DI_RazlitjeVodeHP; | mind[515]:=CrpalkeGrfs[7].AlarmCodeLog4; |  |  | Read_Real(rVar:=ValAI_TempTB8,lo:=6030,hi:=6031); |  | 515:DI_RazlitjeVodeHP:=Bit_0; | 515:CrpalkeGrfs[7].AlarmCodeLog4:=Word_01; |  |  | 6031:ValAI_TempTB8:=Real_0;
mind_bool[516]:=DI_RazlitjeVodeK1; | mind[516]:=CrpalkeGrfs[7].AlarmCodeLog5; |  |  | Read_Real(rVar:=ValAI_TlakExp1S1,lo:=6032,hi:=6033); |  | 516:DI_RazlitjeVodeK1:=Bit_0; | 516:CrpalkeGrfs[7].AlarmCodeLog5:=Word_01; |  |  | 6033:ValAI_TlakExp1S1:=Real_0;
mind_bool[517]:=DI_RazlitjeVodeK2; | mind[517]:=CrpalkeGrfs[7].AlarmGroupXVH[0]; |  |  | Read_Real(rVar:=ValAI_TlakExp1S2,lo:=6034,hi:=6035); |  | 517:DI_RazlitjeVodeK2:=Bit_0; | 517:CrpalkeGrfs[7].AlarmGroupXVH[0]:=Word_01; |  |  | 6035:ValAI_TlakExp1S2:=Real_0;
mind_bool[518]:=DI_RazlitjeVodeTP; | mind[518]:=CrpalkeGrfs[7].AlarmGroupXVH[10]; |  |  | Read_Real(rVar:=ValAI_TlakExp2S1,lo:=6036,hi:=6037); |  | 518:DI_RazlitjeVodeTP:=Bit_0; | 518:CrpalkeGrfs[7].AlarmGroupXVH[10]:=Word_01; |  |  | 6037:ValAI_TlakExp2S1:=Real_0;
mind_bool[519]:=DI_ToplPostGenErr; | mind[519]:=CrpalkeGrfs[7].AlarmGroupXVH[11]; |  |  | Read_Real(rVar:=ValAI_TlakExp2S2,lo:=6038,hi:=6039); |  | 519:DI_ToplPostGenErr:=Bit_0; | 519:CrpalkeGrfs[7].AlarmGroupXVH[11]:=Word_01; |  |  | 6039:ValAI_TlakExp2S2:=Real_0;
mind_bool[520]:=DI_UPS_Alarm; | mind[520]:=CrpalkeGrfs[7].AlarmGroupXVH[12]; |  |  | Read_Real(rVar:=ValAI_TlakHB15,lo:=6040,hi:=6041); |  | 520:DI_UPS_Alarm:=Bit_0; | 520:CrpalkeGrfs[7].AlarmGroupXVH[12]:=Word_01; |  |  | 6041:ValAI_TlakHB15:=Real_0;
mind_bool[521]:=DI_UPS_BatNacin; | mind[521]:=CrpalkeGrfs[7].AlarmGroupXVH[13]; |  |  | Read_Real(rVar:=ValAI_TlakHB16,lo:=6042,hi:=6043); |  | 521:DI_UPS_BatNacin:=Bit_0; | 521:CrpalkeGrfs[7].AlarmGroupXVH[13]:=Word_01; |  |  | 6043:ValAI_TlakHB16:=Real_0;
mind_bool[522]:=DI_UPS_Polnjenje; | mind[522]:=CrpalkeGrfs[7].AlarmGroupXVH[14]; |  |  | Read_Real(rVar:=ValAI_TlakHB17,lo:=6044,hi:=6045); |  | 522:DI_UPS_Polnjenje:=Bit_0; | 522:CrpalkeGrfs[7].AlarmGroupXVH[14]:=Word_01; |  |  | 6045:ValAI_TlakHB17:=Real_0;
mind_bool[523]:=DI_Vent1Auto; | mind[523]:=CrpalkeGrfs[7].AlarmGroupXVH[15]; |  |  | Read_Real(rVar:=ValAI_TlakHB3,lo:=6046,hi:=6047); |  | 523:DI_Vent1Auto:=Bit_0; | 523:CrpalkeGrfs[7].AlarmGroupXVH[15]:=Word_01; |  |  | 6047:ValAI_TlakHB3:=Real_0;
mind_bool[524]:=DI_Vent1kontON; | mind[524]:=CrpalkeGrfs[7].AlarmGroupXVH[16]; |  |  | Read_Real(rVar:=ValAI_TlakTB11,lo:=6048,hi:=6049); |  | 524:DI_Vent1kontON:=Bit_0; | 524:CrpalkeGrfs[7].AlarmGroupXVH[16]:=Word_01; |  |  | 6049:ValAI_TlakTB11:=Real_0;
mind_bool[525]:=DI_Vent2Auto; | mind[525]:=CrpalkeGrfs[7].AlarmGroupXVH[1]; |  |  | Read_Real(rVar:=ValAI_TlakTB12,lo:=6050,hi:=6051); |  | 525:DI_Vent2Auto:=Bit_0; | 525:CrpalkeGrfs[7].AlarmGroupXVH[1]:=Word_01; |  |  | 6051:ValAI_TlakTB12:=Real_0;
mind_bool[526]:=DI_Vent2kontON; | mind[526]:=CrpalkeGrfs[7].AlarmGroupXVH[2]; |  |  | Read_Real(rVar:=ValAI_TlakTB13,lo:=6052,hi:=6053); |  | 526:DI_Vent2kontON:=Bit_0; | 526:CrpalkeGrfs[7].AlarmGroupXVH[2]:=Word_01; |  |  | 6053:ValAI_TlakTB13:=Real_0;
mind_bool[527]:=DI_Vent3Auto; | mind[527]:=CrpalkeGrfs[7].AlarmGroupXVH[3]; |  |  | Read_Real(rVar:=ValAI_TlakTB14,lo:=6054,hi:=6055); |  | 527:DI_Vent3Auto:=Bit_0; | 527:CrpalkeGrfs[7].AlarmGroupXVH[3]:=Word_01; |  |  | 6055:ValAI_TlakTB14:=Real_0;
mind_bool[528]:=DI_Vent3kontON; | mind[528]:=CrpalkeGrfs[7].AlarmGroupXVH[4]; |  |  | Read_Real(rVar:=ValAI_Vlaga1B4,lo:=6056,hi:=6057); |  | 528:DI_Vent3kontON:=Bit_0; | 528:CrpalkeGrfs[7].AlarmGroupXVH[4]:=Word_01; |  |  | 6057:ValAI_Vlaga1B4:=Real_0;
mind_bool[529]:=DI_Vent4Auto; | mind[529]:=CrpalkeGrfs[7].AlarmGroupXVH[5]; |  |  | Read_Real(rVar:=ValAI_Vlaga2B4,lo:=6058,hi:=6059); |  | 529:DI_Vent4Auto:=Bit_0; | 529:CrpalkeGrfs[7].AlarmGroupXVH[5]:=Word_01; |  |  | 6059:ValAI_Vlaga2B4:=Real_0;
mind_bool[530]:=DI_Vent4kontON; | mind[530]:=CrpalkeGrfs[7].AlarmGroupXVH[6]; |  |  | Read_Real(rVar:=ValAO_RegVentTY[1],lo:=6060,hi:=6061); |  | 530:DI_Vent4kontON:=Bit_0; | 530:CrpalkeGrfs[7].AlarmGroupXVH[6]:=Word_01; |  |  | 6061:ValAO_RegVentTY[1]:=Real_0;
mind_bool[531]:=DI_Vent5Auto; | mind[531]:=CrpalkeGrfs[7].AlarmGroupXVH[7]; |  |  | Read_Real(rVar:=ValAO_RegVentTY[2],lo:=6062,hi:=6063); |  | 531:DI_Vent5Auto:=Bit_0; | 531:CrpalkeGrfs[7].AlarmGroupXVH[7]:=Word_01; |  |  | 6063:ValAO_RegVentTY[2]:=Real_0;
mind_bool[532]:=DI_Vent5kontON; | mind[532]:=CrpalkeGrfs[7].AlarmGroupXVH[8]; |  |  | Read_Real(rVar:=ValAO_RegVentTY[3],lo:=6064,hi:=6065); |  | 532:DI_Vent5kontON:=Bit_0; | 532:CrpalkeGrfs[7].AlarmGroupXVH[8]:=Word_01; |  |  | 6065:ValAO_RegVentTY[3]:=Real_0;
mind_bool[533]:=DI_Vent6Auto; | mind[533]:=CrpalkeGrfs[7].AlarmGroupXVH[9]; |  |  | Read_Real(rVar:=ValAO_RegVentTY[4],lo:=6066,hi:=6067); |  | 533:DI_Vent6Auto:=Bit_0; | 533:CrpalkeGrfs[7].AlarmGroupXVH[9]:=Word_01; |  |  | 6067:ValAO_RegVentTY[4]:=Real_0;
mind_bool[534]:=DI_Vent6kontON; | mind[534]:=CrpalkeGrfs[7].AlarmQSD1; |  |  | Read_Real(rVar:=VlagaHIApovprecna,lo:=6068,hi:=6069); |  | 534:DI_Vent6kontON:=Bit_0; | 534:CrpalkeGrfs[7].AlarmQSD1:=Word_01; |  |  | 6069:VlagaHIApovprecna:=Real_0;
mind_bool[535]:=DI_Vlaz1ERR; | mind[535]:=CrpalkeGrfs[7].AlarmQSD2; |  |  | Read_Real(rVar:=Circutor.CosFi_III,lo:=6070,hi:=6071); |  | 535:DI_Vlaz1ERR:=Bit_0; | 535:CrpalkeGrfs[7].AlarmQSD2:=Word_01; |  |  | 6071:Circutor.CosFi_III:=Real_0;
mind_bool[536]:=DI_Vlaz1ON; | mind[536]:=CrpalkeGrfs[7].AlarmStart1; |  |  | Read_Real(rVar:=Circutor.DelovnaEnergija,lo:=6072,hi:=6073); |  | 536:DI_Vlaz1ON:=Bit_0; | 536:CrpalkeGrfs[7].AlarmStart1:=Word_01; |  |  | 6073:Circutor.DelovnaEnergija:=Real_0;
mind_bool[537]:=DI_Vlaz2ERR; | mind[537]:=CrpalkeGrfs[7].AlarmStart2; |  |  | Read_Real(rVar:=Circutor.DelovnaMoc_III,lo:=6074,hi:=6075); |  | 537:DI_Vlaz2ERR:=Bit_0; | 537:CrpalkeGrfs[7].AlarmStart2:=Word_01; |  |  | 6075:Circutor.DelovnaMoc_III:=Real_0;
mind_bool[538]:=DI_Vlaz2ON; | mind[538]:=CrpalkeGrfs[7].AlarmStop1; |  |  | Read_Real(rVar:=Circutor.DelovnaMoc_L1,lo:=6076,hi:=6077); |  | 538:DI_Vlaz2ON:=Bit_0; | 538:CrpalkeGrfs[7].AlarmStop1:=Word_01; |  |  | 6077:Circutor.DelovnaMoc_L1:=Real_0;
mind_bool[539]:=DIN_230VAC_OK; | mind[539]:=CrpalkeGrfs[7].AlarmStop2; |  |  | Read_Real(rVar:=Circutor.DelovnaMoc_L2,lo:=6078,hi:=6079); |  | 539:DIN_230VAC_OK:=Bit_0; | 539:CrpalkeGrfs[7].AlarmStop2:=Word_01; |  |  | 6079:Circutor.DelovnaMoc_L2:=Real_0;
mind_bool[540]:=DIN_24VAC_OK; | mind[540]:=CrpalkeGrfs[7].AlarmStop3; |  |  | Read_Real(rVar:=Circutor.DelovnaMoc_L3,lo:=6080,hi:=6081); |  | 540:DIN_24VAC_OK:=Bit_0; | 540:CrpalkeGrfs[7].AlarmStop3:=Word_01; |  |  | 6081:Circutor.DelovnaMoc_L3:=Real_0;
mind_bool[541]:=DIN_24VDC_OK; | mind[541]:=CrpalkeGrfs[7].AlarmSurv1; |  |  | Read_Real(rVar:=Circutor.Frekvenca_L1,lo:=6082,hi:=6083); |  | 541:DIN_24VDC_OK:=Bit_0; | 541:CrpalkeGrfs[7].AlarmSurv1:=Word_01; |  |  | 6083:Circutor.Frekvenca_L1:=Real_0;
mind_bool[542]:=DIN_CrpHM1ERR; | mind[542]:=CrpalkeGrfs[7].AlarmSurv2; |  |  | Read_Real(rVar:=Circutor.InduktivnaEnergija,lo:=6084,hi:=6085); |  | 542:DIN_CrpHM1ERR:=Bit_0; | 542:CrpalkeGrfs[7].AlarmSurv2:=Word_01; |  |  | 6085:Circutor.InduktivnaEnergija:=Real_0;
mind_bool[543]:=DIN_CrpHM2ERR; | mind[543]:=CrpalkeGrfs[7].ControlSource; |  |  | Read_Real(rVar:=Circutor.InduktivnaMoc_III,lo:=6086,hi:=6087); |  | 543:DIN_CrpHM2ERR:=Bit_0; | 543:CrpalkeGrfs[7].ControlSource:=Word_01; |  |  | 6087:Circutor.InduktivnaMoc_III:=Real_0;
mind_bool[544]:=DIN_CrpHM3ERR; | mind[544]:=CrpalkeGrfs[7].ExternInputSetup; |  |  | Read_Real(rVar:=Circutor.JalovaMoc_L1,lo:=6088,hi:=6089); |  | 544:DIN_CrpHM3ERR:=Bit_0; | 544:CrpalkeGrfs[7].ExternInputSetup:=Word_01; |  |  | 6089:Circutor.JalovaMoc_L1:=Real_0;
mind_bool[545]:=DIN_CrpHM4ERR; | mind[545]:=CrpalkeGrfs[7].ExternInputsStatus; |  |  | Read_Real(rVar:=Circutor.JalovaMoc_L2,lo:=6090,hi:=6091); |  | 545:DIN_CrpHM4ERR:=Bit_0; | 545:CrpalkeGrfs[7].ExternInputsStatus:=Word_01; |  |  | 6091:Circutor.JalovaMoc_L2:=Real_0;
mind_bool[546]:=DIN_HladStERR; | mind[546]:=CrpalkeGrfs[7].LocalSetupMode1; |  |  | Read_Real(rVar:=Circutor.JalovaMoc_L3,lo:=6092,hi:=6093); |  | 546:DIN_HladStERR:=Bit_0; | 546:CrpalkeGrfs[7].LocalSetupMode1:=Word_01; |  |  | 6093:Circutor.JalovaMoc_L3:=Real_0;
mind_bool[547]:=DIN_Klima1ERR; | mind[547]:=CrpalkeGrfs[7].PreklopkaMode; |  |  | Read_Real(rVar:=Circutor.KapacitivnaEnergija,lo:=6094,hi:=6095); |  | 547:DIN_Klima1ERR:=Bit_0; | 547:CrpalkeGrfs[7].PreklopkaMode:=Word_01; |  |  | 6095:Circutor.KapacitivnaEnergija:=Real_0;
mind_bool[548]:=DIN_Klima1filterZAM; | mind[548]:=CrpalkeGrfs[7].Relay1setup; |  |  | Read_Real(rVar:=Circutor.KapacitivnaMoc_III,lo:=6096,hi:=6097); |  | 548:DIN_Klima1filterZAM:=Bit_0; | 548:CrpalkeGrfs[7].Relay1setup:=Word_01; |  |  | 6097:Circutor.KapacitivnaMoc_III:=Real_0;
mind_bool[549]:=DIN_Klima1zascStON; | mind[549]:=CrpalkeGrfs[7].RemoteSetupMode1; |  |  | Read_Real(rVar:=Circutor.MaximumDemand,lo:=6098,hi:=6099); |  | 549:DIN_Klima1zascStON:=Bit_0; | 549:CrpalkeGrfs[7].RemoteSetupMode1:=Word_01; |  |  | 6099:Circutor.MaximumDemand:=Real_0;
mind_bool[550]:=DIN_Klima2ERR; | mind[550]:=CrpalkeGrfs[7].StatusCrpalke; |  |  | Read_Real(rVar:=Circutor.Napetost_L1_L2,lo:=6100,hi:=6101); |  | 550:DIN_Klima2ERR:=Bit_0; | 550:CrpalkeGrfs[7].StatusCrpalke:=Byte_0; |  |  | 6101:Circutor.Napetost_L1_L2:=Real_0;
mind_bool[551]:=DIN_Klima2filterZAM; | mind[551]:=CrpalkeGrfs[7].StatusMode1; |  |  | Read_Real(rVar:=Circutor.Napetost_L1_N,lo:=6102,hi:=6103); |  | 551:DIN_Klima2filterZAM:=Bit_0; | 551:CrpalkeGrfs[7].StatusMode1:=Word_01; |  |  | 6103:Circutor.Napetost_L1_N:=Real_0;
mind_bool[552]:=DIN_Klima2zascStON; | mind[552]:=CrpalkeGrfs[7].StatusMode1co; |  |  | Read_Real(rVar:=Circutor.Napetost_L2_L3,lo:=6104,hi:=6105); |  | 552:DIN_Klima2zascStON:=Bit_0; | 552:CrpalkeGrfs[7].StatusMode1co:=Byte_0; |  |  | 6105:Circutor.Napetost_L2_L3:=Real_0;
mind_bool[553]:=DIN_Komp1ERR; | mind[553]:=CrpalkeGrfs[7].StatusMode1op; |  |  | Read_Real(rVar:=Circutor.Napetost_L2_N,lo:=6106,hi:=6107); |  | 553:DIN_Komp1ERR:=Bit_0; | 553:CrpalkeGrfs[7].StatusMode1op:=Byte_0; |  |  | 6107:Circutor.Napetost_L2_N:=Real_0;
mind_bool[554]:=DIN_Komp1ON; | mind[554]:=CrpalkeGrfs[7].StatusMode2; |  |  | Read_Real(rVar:=Circutor.Napetost_L3_L1,lo:=6108,hi:=6109); |  | 554:DIN_Komp1ON:=Bit_0; | 554:CrpalkeGrfs[7].StatusMode2:=Word_01; |  |  | 6109:Circutor.Napetost_L3_L1:=Real_0;
mind_bool[555]:=DIN_Komp2ERR; | mind[555]:=CrpalkeGrfs[7].StatusMode3; |  |  | Read_Real(rVar:=Circutor.Napetost_L3_N,lo:=6110,hi:=6111); |  | 555:DIN_Komp2ERR:=Bit_0; | 555:CrpalkeGrfs[7].StatusMode3:=Word_01; |  |  | 6111:Circutor.Napetost_L3_N:=Real_0;
mind_bool[556]:=DIN_Komp2ON; | mind[556]:=CrpalkeGrfs[8].AlarmActiveCode; |  |  | Read_Real(rVar:=Circutor.NavideznaMoc_III,lo:=6112,hi:=6113); |  | 556:DIN_Komp2ON:=Bit_0; | 556:CrpalkeGrfs[8].AlarmActiveCode:=Word_01; |  |  | 6113:Circutor.NavideznaMoc_III:=Real_0;
mind_bool[557]:=DIN_Kond1zascStON; | mind[557]:=CrpalkeGrfs[8].AlarmCodeLog1; |  |  | Read_Real(rVar:=Circutor.NicelniTok,lo:=6114,hi:=6115); |  | 557:DIN_Kond1zascStON:=Bit_0; | 557:CrpalkeGrfs[8].AlarmCodeLog1:=Word_01; |  |  | 6115:Circutor.NicelniTok:=Real_0;
mind_bool[558]:=DIN_Kond2zascStON; | mind[558]:=CrpalkeGrfs[8].AlarmCodeLog2; |  |  | Read_Real(rVar:=Circutor.PowerFactor_III,lo:=6116,hi:=6117); |  | 558:DIN_Kond2zascStON:=Bit_0; | 558:CrpalkeGrfs[8].AlarmCodeLog2:=Word_01; |  |  | 6117:Circutor.PowerFactor_III:=Real_0;
mind_bool[559]:=DIN_Kond3zascStON; | mind[559]:=CrpalkeGrfs[8].AlarmCodeLog3; |  |  | Read_Real(rVar:=Circutor.PowerFactor_L1,lo:=6118,hi:=6119); |  | 559:DIN_Kond3zascStON:=Bit_0; | 559:CrpalkeGrfs[8].AlarmCodeLog3:=Word_01; |  |  | 6119:Circutor.PowerFactor_L1:=Real_0;
mind_bool[560]:=DIN_Vlaz1ERR; | mind[560]:=CrpalkeGrfs[8].AlarmCodeLog4; |  |  | Read_Real(rVar:=Circutor.PowerFactor_L2,lo:=6120,hi:=6121); |  | 560:DIN_Vlaz1ERR:=Bit_0; | 560:CrpalkeGrfs[8].AlarmCodeLog4:=Word_01; |  |  | 6121:Circutor.PowerFactor_L2:=Real_0;
mind_bool[561]:=DIN_Vlaz2ERR; | mind[561]:=CrpalkeGrfs[8].AlarmCodeLog5; |  |  | Read_Real(rVar:=Circutor.PowerFactor_L3,lo:=6122,hi:=6123); |  | 561:DIN_Vlaz2ERR:=Bit_0; | 561:CrpalkeGrfs[8].AlarmCodeLog5:=Word_01; |  |  | 6123:Circutor.PowerFactor_L3:=Real_0;
mind_bool[562]:=DO_BojlerTE1Vklop; | mind[562]:=CrpalkeGrfs[8].AlarmGroupXVH[0]; |  |  | Read_Real(rVar:=Circutor.THDI_L1,lo:=6124,hi:=6125); |  | 562:DO_BojlerTE1Vklop:=Bit_0; | 562:CrpalkeGrfs[8].AlarmGroupXVH[0]:=Word_01; |  |  | 6125:Circutor.THDI_L1:=Real_0;
mind_bool[563]:=DO_CrpHM1Vklop; | mind[563]:=CrpalkeGrfs[8].AlarmGroupXVH[10]; |  |  | Read_Real(rVar:=Circutor.THDI_L2,lo:=6126,hi:=6127); |  | 563:DO_CrpHM1Vklop:=Bit_0; | 563:CrpalkeGrfs[8].AlarmGroupXVH[10]:=Word_01; |  |  | 6127:Circutor.THDI_L2:=Real_0;
mind_bool[564]:=DO_CrpHM2Vklop; | mind[564]:=CrpalkeGrfs[8].AlarmGroupXVH[11]; |  |  | Read_Real(rVar:=Circutor.THDI_L3,lo:=6128,hi:=6129); |  | 564:DO_CrpHM2Vklop:=Bit_0; | 564:CrpalkeGrfs[8].AlarmGroupXVH[11]:=Word_01; |  |  | 6129:Circutor.THDI_L3:=Real_0;
mind_bool[565]:=DO_CrpHM3Vklop; | mind[565]:=CrpalkeGrfs[8].AlarmGroupXVH[12]; |  |  | Read_Real(rVar:=Circutor.THDV_L1,lo:=6130,hi:=6131); |  | 565:DO_CrpHM3Vklop:=Bit_0; | 565:CrpalkeGrfs[8].AlarmGroupXVH[12]:=Word_01; |  |  | 6131:Circutor.THDV_L1:=Real_0;
mind_bool[566]:=DO_CrpHM4Vklop; | mind[566]:=CrpalkeGrfs[8].AlarmGroupXVH[13]; |  |  | Read_Real(rVar:=Circutor.THDV_L2,lo:=6132,hi:=6133); |  | 566:DO_CrpHM4Vklop:=Bit_0; | 566:CrpalkeGrfs[8].AlarmGroupXVH[13]:=Word_01; |  |  | 6133:Circutor.THDV_L2:=Real_0;
mind_bool[567]:=DO_CrpMN1Vklop; | mind[567]:=CrpalkeGrfs[8].AlarmGroupXVH[14]; |  |  | Read_Real(rVar:=Circutor.THDV_L3,lo:=6134,hi:=6135); |  | 567:DO_CrpMN1Vklop:=Bit_0; | 567:CrpalkeGrfs[8].AlarmGroupXVH[14]:=Word_01; |  |  | 6135:Circutor.THDV_L3:=Real_0;
mind_bool[568]:=DO_CrpTM11Vklop; | mind[568]:=CrpalkeGrfs[8].AlarmGroupXVH[15]; |  |  | Read_Real(rVar:=Circutor.Tok_L1,lo:=6136,hi:=6137); |  | 568:DO_CrpTM11Vklop:=Bit_0; | 568:CrpalkeGrfs[8].AlarmGroupXVH[15]:=Word_01; |  |  | 6137:Circutor.Tok_L1:=Real_0;
mind_bool[569]:=DO_GrundfosVklopL; | mind[569]:=CrpalkeGrfs[8].AlarmGroupXVH[16]; |  |  | Read_Real(rVar:=Circutor.Tok_L2,lo:=6138,hi:=6139); |  | 569:DO_GrundfosVklopL:=Bit_0; | 569:CrpalkeGrfs[8].AlarmGroupXVH[16]:=Word_01; |  |  | 6139:Circutor.Tok_L2:=Real_0;
mind_bool[570]:=DO_GrundfosVklopN; | mind[570]:=CrpalkeGrfs[8].AlarmGroupXVH[1]; |  |  | Read_Real(rVar:=Circutor.Tok_L3,lo:=6140,hi:=6141); |  | 570:DO_GrundfosVklopN:=Bit_0; | 570:CrpalkeGrfs[8].AlarmGroupXVH[1]:=Word_01; |  |  | 6141:Circutor.Tok_L3:=Real_0;
mind_bool[571]:=DO_HladStrIzklop; | mind[571]:=CrpalkeGrfs[8].AlarmGroupXVH[2]; |  |  | Read_Real(rVar:=Circutor.TokPovprecje_III,lo:=6142,hi:=6143); |  | 571:DO_HladStrIzklop:=Bit_0; | 571:CrpalkeGrfs[8].AlarmGroupXVH[2]:=Word_01; |  |  | 6143:Circutor.TokPovprecje_III:=Real_0;
mind_bool[572]:=DO_KE1Vklop; | mind[572]:=CrpalkeGrfs[8].AlarmGroupXVH[3]; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.EnergijaPoraba,lo:=6144,hi:=6145); |  | 572:DO_KE1Vklop:=Bit_0; | 572:CrpalkeGrfs[8].AlarmGroupXVH[3]:=Word_01; |  |  | 6145:CrpalkeGrfsGal.EnergijaPoraba:=Real_0;
mind_bool[573]:=DO_KE2Vklop; | mind[573]:=CrpalkeGrfs[8].AlarmGroupXVH[4]; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.FrekPretvornikDCNapetost,lo:=6146,hi:=6147); |  | 573:DO_KE2Vklop:=Bit_0; | 573:CrpalkeGrfs[8].AlarmGroupXVH[4]:=Word_01; |  |  | 6147:CrpalkeGrfsGal.FrekPretvornikDCNapetost:=Real_0;
mind_bool[574]:=DO_KE3Vklop; | mind[574]:=CrpalkeGrfs[8].AlarmGroupXVH[5]; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.FrekPretvornikDCTok,lo:=6148,hi:=6149); |  | 574:DO_KE3Vklop:=Bit_0; | 574:CrpalkeGrfs[8].AlarmGroupXVH[5]:=Word_01; |  |  | 6149:CrpalkeGrfsGal.FrekPretvornikDCTok:=Real_0;
mind_bool[575]:=DO_Klima1Vklop; | mind[575]:=CrpalkeGrfs[8].AlarmGroupXVH[6]; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.FreqMax,lo:=6150,hi:=6151); |  | 575:DO_Klima1Vklop:=Bit_0; | 575:CrpalkeGrfs[8].AlarmGroupXVH[6]:=Word_01; |  |  | 6151:CrpalkeGrfsGal.FreqMax:=Real_0;
mind_bool[576]:=DO_Klima2Vklop; | mind[576]:=CrpalkeGrfs[8].AlarmGroupXVH[7]; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.FreqMin,lo:=6152,hi:=6153); |  | 576:DO_Klima2Vklop:=Bit_0; | 576:CrpalkeGrfs[8].AlarmGroupXVH[7]:=Word_01; |  |  | 6153:CrpalkeGrfsGal.FreqMin:=Real_0;
mind_bool[577]:=DO_Lop1PL1Vklop; | mind[577]:=CrpalkeGrfs[8].AlarmGroupXVH[8]; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.FreqUpper,lo:=6154,hi:=6155); |  | 577:DO_Lop1PL1Vklop:=Bit_0; | 577:CrpalkeGrfs[8].AlarmGroupXVH[8]:=Word_01; |  |  | 6155:CrpalkeGrfsGal.FreqUpper:=Real_0;
mind_bool[578]:=DO_Lop1PL2Vklop; | mind[578]:=CrpalkeGrfs[8].AlarmGroupXVH[9]; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.MocMax,lo:=6156,hi:=6157); |  | 578:DO_Lop1PL2Vklop:=Bit_0; | 578:CrpalkeGrfs[8].AlarmGroupXVH[9]:=Word_01; |  |  | 6157:CrpalkeGrfsGal.MocMax:=Real_0;
mind_bool[579]:=DO_Lop1PL3Vklop; | mind[579]:=CrpalkeGrfs[8].AlarmQSD1; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.MocTrenutna,lo:=6158,hi:=6159); |  | 579:DO_Lop1PL3Vklop:=Bit_0; | 579:CrpalkeGrfs[8].AlarmQSD1:=Word_01; |  |  | 6159:CrpalkeGrfsGal.MocTrenutna:=Real_0;
mind_bool[580]:=DO_Lop3Y1Vklop; | mind[580]:=CrpalkeGrfs[8].AlarmQSD2; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.MotorHitrost,lo:=6160,hi:=6161); |  | 580:DO_Lop3Y1Vklop:=Bit_0; | 580:CrpalkeGrfs[8].AlarmQSD2:=Word_01; |  |  | 6161:CrpalkeGrfsGal.MotorHitrost:=Real_0;
mind_bool[581]:=DO_Lop4Y1Vklop; | mind[581]:=CrpalkeGrfs[8].AlarmStart1; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.MotorTok,lo:=6162,hi:=6163); |  | 581:DO_Lop4Y1Vklop:=Bit_0; | 581:CrpalkeGrfs[8].AlarmStart1:=Word_01; |  |  | 6163:CrpalkeGrfsGal.MotorTok:=Real_0;
mind_bool[582]:=DO_RazE11_10Vklop; | mind[582]:=CrpalkeGrfs[8].AlarmStart2; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.NapajanjeTok,lo:=6164,hi:=6165); |  | 582:DO_RazE11_10Vklop:=Bit_0; | 582:CrpalkeGrfs[8].AlarmStart2:=Word_01; |  |  | 6165:CrpalkeGrfsGal.NapajanjeTok:=Real_0;
mind_bool[583]:=DO_RazE11_11Vklop; | mind[583]:=CrpalkeGrfs[8].AlarmStop1; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.NastavitevLokalna,lo:=6166,hi:=6167); |  | 583:DO_RazE11_11Vklop:=Bit_0; | 583:CrpalkeGrfs[8].AlarmStop1:=Word_01; |  |  | 6167:CrpalkeGrfsGal.NastavitevLokalna:=Real_0;
mind_bool[584]:=DO_RazE11_1Vklop; | mind[584]:=CrpalkeGrfs[8].AlarmStop2; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.NastavitevTrenutna,lo:=6168,hi:=6169); |  | 584:DO_RazE11_1Vklop:=Bit_0; | 584:CrpalkeGrfs[8].AlarmStop2:=Word_01; |  |  | 6169:CrpalkeGrfsGal.NastavitevTrenutna:=Real_0;
mind_bool[585]:=DO_RazE11_2Vklop; | mind[585]:=CrpalkeGrfs[8].AlarmStop3; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.PretokMax,lo:=6170,hi:=6171); |  | 585:DO_RazE11_2Vklop:=Bit_0; | 585:CrpalkeGrfs[8].AlarmStop3:=Word_01; |  |  | 6171:CrpalkeGrfsGal.PretokMax:=Real_0;
mind_bool[586]:=DO_RazE11_3Vklop; | mind[586]:=CrpalkeGrfs[8].AlarmSurv1; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.PretokMin,lo:=6172,hi:=6173); |  | 586:DO_RazE11_3Vklop:=Bit_0; | 586:CrpalkeGrfs[8].AlarmSurv1:=Word_01; |  |  | 6173:CrpalkeGrfsGal.PretokMin:=Real_0;
mind_bool[587]:=DO_RazE11_4Vklop; | mind[587]:=CrpalkeGrfs[8].AlarmSurv2; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.PretokTrenutni,lo:=6174,hi:=6175); |  | 587:DO_RazE11_4Vklop:=Bit_0; | 587:CrpalkeGrfs[8].AlarmSurv2:=Word_01; |  |  | 6175:CrpalkeGrfsGal.PretokTrenutni:=Real_0;
mind_bool[588]:=DO_RazE11_5Vklop; | mind[588]:=CrpalkeGrfs[8].ControlSource; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.PritiskMax,lo:=6176,hi:=6177); |  | 588:DO_RazE11_5Vklop:=Bit_0; | 588:CrpalkeGrfs[8].ControlSource:=Word_01; |  |  | 6177:CrpalkeGrfsGal.PritiskMax:=Real_0;
mind_bool[589]:=DO_RazE11_6Vklop; | mind[589]:=CrpalkeGrfs[8].ExternInputSetup; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.PritiskTrenutni,lo:=6178,hi:=6179); |  | 589:DO_RazE11_6Vklop:=Bit_0; | 589:CrpalkeGrfs[8].ExternInputSetup:=Word_01; |  |  | 6179:CrpalkeGrfsGal.PritiskTrenutni:=Real_0;
mind_bool[590]:=DO_RazE11_7Vklop; | mind[590]:=CrpalkeGrfs[8].ExternInputsStatus; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.ReferencaMotorjaHzV,lo:=6180,hi:=6181); |  | 590:DO_RazE11_7Vklop:=Bit_0; | 590:CrpalkeGrfs[8].ExternInputsStatus:=Word_01; |  |  | 6181:CrpalkeGrfsGal.ReferencaMotorjaHzV:=Real_0;
mind_bool[591]:=DO_RazE11_8Vklop; | mind[591]:=CrpalkeGrfs[8].LocalSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.ReferencaRemote,lo:=6182,hi:=6183); |  | 591:DO_RazE11_8Vklop:=Bit_0; | 591:CrpalkeGrfs[8].LocalSetupMode1:=Word_01; |  |  | 6183:CrpalkeGrfsGal.ReferencaRemote:=Real_0;
mind_bool[592]:=DO_RazE11_9Vklop; | mind[592]:=CrpalkeGrfs[8].PreklopkaMode; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.StevecUr2h,lo:=6184,hi:=6185); |  | 592:DO_RazE11_9Vklop:=Bit_0; | 592:CrpalkeGrfs[8].PreklopkaMode:=Word_01; |  |  | 6185:CrpalkeGrfsGal.StevecUr2h:=Real_0;
mind_bool[593]:=DO_RazE12_12Vklop; | mind[593]:=CrpalkeGrfs[8].Relay1setup; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.SystemFeedback,lo:=6186,hi:=6187); |  | 593:DO_RazE12_12Vklop:=Bit_0; | 593:CrpalkeGrfs[8].Relay1setup:=Word_01; |  |  | 6187:CrpalkeGrfsGal.SystemFeedback:=Real_0;
mind_bool[594]:=DO_RazE12_13Vklop; | mind[594]:=CrpalkeGrfs[8].RemoteSetupMode1; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.SystemReference,lo:=6188,hi:=6189); |  | 594:DO_RazE12_13Vklop:=Bit_0; | 594:CrpalkeGrfs[8].RemoteSetupMode1:=Word_01; |  |  | 6189:CrpalkeGrfsGal.SystemReference:=Real_0;
mind_bool[595]:=DO_RazE12_14Vklop; | mind[595]:=CrpalkeGrfs[8].StatusCrpalke; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.TemperaturaMotorja,lo:=6190,hi:=6191); |  | 595:DO_RazE12_14Vklop:=Bit_0; | 595:CrpalkeGrfs[8].StatusCrpalke:=Byte_0; |  |  | 6191:CrpalkeGrfsGal.TemperaturaMotorja:=Real_0;
mind_bool[596]:=DO_RazE12_15Vklop; | mind[596]:=CrpalkeGrfs[8].StatusMode1; |  |  | Read_Real(rVar:=CrpalkeGrfsGal.UreXC200,lo:=6192,hi:=6193); |  | 596:DO_RazE12_15Vklop:=Bit_0; | 596:CrpalkeGrfs[8].StatusMode1:=Word_01; |  |  | 6193:CrpalkeGrfsGal.UreXC200:=Real_0;
mind_bool[597]:=DO_RazE13_16Vklop; | mind[597]:=CrpalkeGrfs[8].StatusMode1co; |  |  | Read_Real(rVar:=CrpGrfsPIDregKP,lo:=6194,hi:=6195); |  | 597:DO_RazE13_16Vklop:=Bit_0; | 597:CrpalkeGrfs[8].StatusMode1co:=Byte_0; |  |  | 6195:CrpGrfsPIDregKP:=Real_0;
mind_bool[598]:=DO_RazE13_17Vklop; | mind[598]:=CrpalkeGrfs[8].StatusMode1op; |  |  | Read_Real(rVar:=ValAI_TempTB5,lo:=6196,hi:=6197); |  | 598:DO_RazE13_17Vklop:=Bit_0; | 598:CrpalkeGrfs[8].StatusMode1op:=Byte_0; |  |  | 6197:ValAI_TempTB5:=Real_0;
mind_bool[599]:=DO_RazE13_18Vklop; | mind[599]:=CrpalkeGrfs[8].StatusMode2; |  |  | Read_Real(rVar:=XVH_CrpGrundfosTlakSP,lo:=6198,hi:=6199); |  | 599:DO_RazE13_18Vklop:=Bit_0; | 599:CrpalkeGrfs[8].StatusMode2:=Word_01; |  |  | 6199:XVH_CrpGrundfosTlakSP:=Real_0;
mind_bool[600]:=DO_RazE13_19Vklop; | mind[600]:=CrpalkeGrfs[8].StatusMode3; |  |  | Read_Real(rVar:=XVH_GrafTemp[1],lo:=6200,hi:=6201); |  | 600:DO_RazE13_19Vklop:=Bit_0; | 600:CrpalkeGrfs[8].StatusMode3:=Word_01; |  |  | 6201:XVH_GrafTemp[1]:=Real_0;
mind_bool[601]:=DO_RazE16_20Vklop; | mind[601]:=CrpalkeGrfs[9].AlarmActiveCode; |  |  | Read_Real(rVar:=XVH_GrafTemp[2],lo:=6202,hi:=6203); |  | 601:DO_RazE16_20Vklop:=Bit_0; | 601:CrpalkeGrfs[9].AlarmActiveCode:=Word_01; |  |  | 6203:XVH_GrafTemp[2]:=Real_0;
mind_bool[602]:=DO_RazE16_21Vklop; | mind[602]:=CrpalkeGrfs[9].AlarmCodeLog1; |  |  | Read_Real(rVar:=XVH_GrafTemp[3],lo:=6204,hi:=6205); |  | 602:DO_RazE16_21Vklop:=Bit_0; | 602:CrpalkeGrfs[9].AlarmCodeLog1:=Word_01; |  |  | 6205:XVH_GrafTemp[3]:=Real_0;
mind_bool[603]:=DO_RazE16_22Vklop; | mind[603]:=CrpalkeGrfs[9].AlarmCodeLog2; |  |  | Read_Real(rVar:=XVH_GrafTemp[4],lo:=6206,hi:=6207); |  | 603:DO_RazE16_22Vklop:=Bit_0; | 603:CrpalkeGrfs[9].AlarmCodeLog2:=Word_01; |  |  | 6207:XVH_GrafTemp[4]:=Real_0;
mind_bool[604]:=DO_RazE16_23Vklop; | mind[604]:=CrpalkeGrfs[9].AlarmCodeLog3; |  |  | Read_Real(rVar:=XVH_GrafTemp[5],lo:=6208,hi:=6209); |  | 604:DO_RazE16_23Vklop:=Bit_0; | 604:CrpalkeGrfs[9].AlarmCodeLog3:=Word_01; |  |  | 6209:XVH_GrafTemp[5]:=Real_0;
mind_bool[605]:=DO_RazE16_24Vklop; | mind[605]:=CrpalkeGrfs[9].AlarmCodeLog4; |  |  | Read_Real(rVar:=XVH_GrafVlaga[1],lo:=6210,hi:=6211); |  | 605:DO_RazE16_24Vklop:=Bit_0; | 605:CrpalkeGrfs[9].AlarmCodeLog4:=Word_01; |  |  | 6211:XVH_GrafVlaga[1]:=Real_0;
mind_bool[606]:=DO_Vent1Vklop; | mind[606]:=CrpalkeGrfs[9].AlarmCodeLog5; |  |  | Read_Real(rVar:=XVH_GrafVlaga[2],lo:=6212,hi:=6213); |  | 606:DO_Vent1Vklop:=Bit_0; | 606:CrpalkeGrfs[9].AlarmCodeLog5:=Word_01; |  |  | 6213:XVH_GrafVlaga[2]:=Real_0;
mind_bool[607]:=DO_Vent2Vklop; | mind[607]:=CrpalkeGrfs[9].AlarmGroupXVH[0]; |  |  | Read_Real(rVar:=XVH_GrafVlaga[3],lo:=6214,hi:=6215); |  | 607:DO_Vent2Vklop:=Bit_0; | 607:CrpalkeGrfs[9].AlarmGroupXVH[0]:=Word_01; |  |  | 6215:XVH_GrafVlaga[3]:=Real_0;
mind_bool[608]:=DO_Vent3Vklop; | mind[608]:=CrpalkeGrfs[9].AlarmGroupXVH[10]; |  |  | Read_Real(rVar:=XVH_GrafVlaga[4],lo:=6216,hi:=6217); |  | 608:DO_Vent3Vklop:=Bit_0; | 608:CrpalkeGrfs[9].AlarmGroupXVH[10]:=Word_01; |  |  | 6217:XVH_GrafVlaga[4]:=Real_0;
mind_bool[609]:=DO_Vent4Vklop; | mind[609]:=CrpalkeGrfs[9].AlarmGroupXVH[11]; |  |  | Read_Real(rVar:=XVH_GrafVlaga[5],lo:=6218,hi:=6219); |  | 609:DO_Vent4Vklop:=Bit_0; | 609:CrpalkeGrfs[9].AlarmGroupXVH[11]:=Word_01; |  |  | 6219:XVH_GrafVlaga[5]:=Real_0;
mind_bool[610]:=DO_Vent5Vklop; | mind[610]:=CrpalkeGrfs[9].AlarmGroupXVH[12]; |  |  | Read_Real(rVar:=XVH_TlakSenzor,lo:=6220,hi:=6221); |  | 610:DO_Vent5Vklop:=Bit_0; | 610:CrpalkeGrfs[9].AlarmGroupXVH[12]:=Word_01; |  |  | 6221:XVH_TlakSenzor:=Real_0;
mind_bool[611]:=DO_Vent6Vklop; | mind[611]:=CrpalkeGrfs[9].AlarmGroupXVH[13]; |  |  | Read_Real(rVar:=Circ[1].MaximumDemandA2,lo:=6222,hi:=6223); |  | 611:DO_Vent6Vklop:=Bit_0; | 611:CrpalkeGrfs[9].AlarmGroupXVH[13]:=Word_01; |  |  | 6223:Circ[1].MaximumDemandA2:=Real_0;
mind_bool[612]:=ErrComCirc[1]; | mind[612]:=CrpalkeGrfs[9].AlarmGroupXVH[14]; |  |  | Read_Real(rVar:=Circ[1].MaximumDemandA3,lo:=6224,hi:=6225); |  | 612:ErrComCirc[1]:=Bit_0; | 612:CrpalkeGrfs[9].AlarmGroupXVH[14]:=Word_01; |  |  | 6225:Circ[1].MaximumDemandA3:=Real_0;
mind_bool[613]:=ErrComCirc[2]; | mind[613]:=CrpalkeGrfs[9].AlarmGroupXVH[15]; |  |  | Read_Real(rVar:=Circ[1].RazEner_D_SCADA,lo:=6226,hi:=6227); |  | 613:ErrComCirc[2]:=Bit_0; | 613:CrpalkeGrfs[9].AlarmGroupXVH[15]:=Word_01; |  |  | 6227:Circ[1].RazEner_D_SCADA:=Real_0;
mind_bool[614]:=ErrComDanfossHM[1]; | mind[614]:=CrpalkeGrfs[9].AlarmGroupXVH[16]; |  |  | Read_Real(rVar:=Circ[1].RazEner_T_SCADA,lo:=6228,hi:=6229); |  | 614:ErrComDanfossHM[1]:=Bit_0; | 614:CrpalkeGrfs[9].AlarmGroupXVH[16]:=Word_01; |  |  | 6229:Circ[1].RazEner_T_SCADA:=Real_0;
mind_bool[615]:=ErrComDanfossHM[2]; | mind[615]:=CrpalkeGrfs[9].AlarmGroupXVH[1]; |  |  | Read_Real(rVar:=Circ[1].RazEner_M_SCADA,lo:=6230,hi:=6231); |  | 615:ErrComDanfossHM[2]:=Bit_0; | 615:CrpalkeGrfs[9].AlarmGroupXVH[1]:=Word_01; |  |  | 6231:Circ[1].RazEner_M_SCADA:=Real_0;
mind_bool[616]:=ErrComDanfossHM[3]; | mind[616]:=CrpalkeGrfs[9].AlarmGroupXVH[2]; |  |  |  |  | 616:ErrComDanfossHM[3]:=Bit_0; | 616:CrpalkeGrfs[9].AlarmGroupXVH[2]:=Word_01;
mind_bool[617]:=ErrComDanfossHM[4]; | mind[617]:=CrpalkeGrfs[9].AlarmGroupXVH[3]; |  |  |  |  | 617:ErrComDanfossHM[4]:=Bit_0; | 617:CrpalkeGrfs[9].AlarmGroupXVH[3]:=Word_01;
mind_bool[618]:=ErrComGrundfos[0]; | mind[618]:=CrpalkeGrfs[9].AlarmGroupXVH[4]; |  |  |  |  | 618:ErrComGrundfos[0]:=Bit_0; | 618:CrpalkeGrfs[9].AlarmGroupXVH[4]:=Word_01;
mind_bool[619]:=ErrComGrundfos[10]; | mind[619]:=CrpalkeGrfs[9].AlarmGroupXVH[5]; |  |  |  |  | 619:ErrComGrundfos[10]:=Bit_0; | 619:CrpalkeGrfs[9].AlarmGroupXVH[5]:=Word_01;
mind_bool[620]:=ErrComGrundfos[11]; | mind[620]:=CrpalkeGrfs[9].AlarmGroupXVH[6]; |  |  |  |  | 620:ErrComGrundfos[11]:=Bit_0; | 620:CrpalkeGrfs[9].AlarmGroupXVH[6]:=Word_01;
mind_bool[621]:=ErrComGrundfos[12]; | mind[621]:=CrpalkeGrfs[9].AlarmGroupXVH[7]; |  |  |  |  | 621:ErrComGrundfos[12]:=Bit_0; | 621:CrpalkeGrfs[9].AlarmGroupXVH[7]:=Word_01;
mind_bool[622]:=ErrComGrundfos[13]; | mind[622]:=CrpalkeGrfs[9].AlarmGroupXVH[8]; |  |  |  |  | 622:ErrComGrundfos[13]:=Bit_0; | 622:CrpalkeGrfs[9].AlarmGroupXVH[8]:=Word_01;
mind_bool[623]:=ErrComGrundfos[14]; | mind[623]:=CrpalkeGrfs[9].AlarmGroupXVH[9]; |  |  |  |  | 623:ErrComGrundfos[14]:=Bit_0; | 623:CrpalkeGrfs[9].AlarmGroupXVH[9]:=Word_01;
mind_bool[624]:=ErrComGrundfos[1]; | mind[624]:=CrpalkeGrfs[9].AlarmQSD1; |  |  |  |  | 624:ErrComGrundfos[1]:=Bit_0; | 624:CrpalkeGrfs[9].AlarmQSD1:=Word_01;
mind_bool[625]:=ErrComGrundfos[2]; | mind[625]:=CrpalkeGrfs[9].AlarmQSD2; |  |  |  |  | 625:ErrComGrundfos[2]:=Bit_0; | 625:CrpalkeGrfs[9].AlarmQSD2:=Word_01;
mind_bool[626]:=ErrComGrundfos[3]; | mind[626]:=CrpalkeGrfs[9].AlarmStart1; |  |  |  |  | 626:ErrComGrundfos[3]:=Bit_0; | 626:CrpalkeGrfs[9].AlarmStart1:=Word_01;
mind_bool[627]:=ErrComGrundfos[4]; | mind[627]:=CrpalkeGrfs[9].AlarmStart2; |  |  |  |  | 627:ErrComGrundfos[4]:=Bit_0; | 627:CrpalkeGrfs[9].AlarmStart2:=Word_01;
mind_bool[628]:=ErrComGrundfos[5]; | mind[628]:=CrpalkeGrfs[9].AlarmStop1; |  |  |  |  | 628:ErrComGrundfos[5]:=Bit_0; | 628:CrpalkeGrfs[9].AlarmStop1:=Word_01;
mind_bool[629]:=ErrComGrundfos[6]; | mind[629]:=CrpalkeGrfs[9].AlarmStop2; |  |  |  |  | 629:ErrComGrundfos[6]:=Bit_0; | 629:CrpalkeGrfs[9].AlarmStop2:=Word_01;
mind_bool[630]:=ErrComGrundfos[7]; | mind[630]:=CrpalkeGrfs[9].AlarmStop3; |  |  |  |  | 630:ErrComGrundfos[7]:=Bit_0; | 630:CrpalkeGrfs[9].AlarmStop3:=Word_01;
mind_bool[631]:=ErrComGrundfos[8]; | mind[631]:=CrpalkeGrfs[9].AlarmSurv1; |  |  |  |  | 631:ErrComGrundfos[8]:=Bit_0; | 631:CrpalkeGrfs[9].AlarmSurv1:=Word_01;
mind_bool[632]:=ErrComGrundfos[9]; | mind[632]:=CrpalkeGrfs[9].AlarmSurv2; |  |  |  |  | 632:ErrComGrundfos[9]:=Bit_0; | 632:CrpalkeGrfs[9].AlarmSurv2:=Word_01;
mind_bool[633]:=ErrComHladStroj; | mind[633]:=CrpalkeGrfs[9].ControlSource; |  |  |  |  | 633:ErrComHladStroj:=Bit_0; | 633:CrpalkeGrfs[9].ControlSource:=Word_01;
mind_bool[634]:=ErrComKlima[1]; | mind[634]:=CrpalkeGrfs[9].ExternInputSetup; |  |  |  |  | 634:ErrComKlima[1]:=Bit_0; | 634:CrpalkeGrfs[9].ExternInputSetup:=Word_01;
mind_bool[635]:=ErrComKlima[2]; | mind[635]:=CrpalkeGrfs[9].ExternInputsStatus; |  |  |  |  | 635:ErrComKlima[2]:=Bit_0; | 635:CrpalkeGrfs[9].ExternInputsStatus:=Word_01;
mind_bool[636]:=ErrCommScada; | mind[636]:=CrpalkeGrfs[9].LocalSetupMode1; |  |  |  |  | 636:ErrCommScada:=Bit_0; | 636:CrpalkeGrfs[9].LocalSetupMode1:=Word_01;
mind_bool[637]:=ErrCommXC100; | mind[637]:=CrpalkeGrfs[9].PreklopkaMode; |  |  |  |  | 637:ErrCommXC100:=Bit_0; | 637:CrpalkeGrfs[9].PreklopkaMode:=Word_01;
mind_bool[638]:=ErrComPanelPLC; | mind[638]:=CrpalkeGrfs[9].Relay1setup; |  |  |  |  | 638:ErrComPanelPLC:=Bit_0; | 638:CrpalkeGrfs[9].Relay1setup:=Word_01;
mind_bool[639]:=ErrComPort2; | mind[639]:=CrpalkeGrfs[9].RemoteSetupMode1; |  |  |  |  | 639:ErrComPort2:=Bit_0; | 639:CrpalkeGrfs[9].RemoteSetupMode1:=Word_01;
mind_bool[640]:=ErrComPort3; | mind[640]:=CrpalkeGrfs[9].StatusCrpalke; |  |  |  |  | 640:ErrComPort3:=Bit_0; | 640:CrpalkeGrfs[9].StatusCrpalke:=Byte_0;
mind_bool[641]:=ErrComPort4; | mind[641]:=CrpalkeGrfs[9].StatusMode1; |  |  |  |  | 641:ErrComPort4:=Bit_0; | 641:CrpalkeGrfs[9].StatusMode1:=Word_01;
mind_bool[642]:=ErrComToplPost; | mind[642]:=CrpalkeGrfs[9].StatusMode1co; |  |  |  |  | 642:ErrComToplPost:=Bit_0; | 642:CrpalkeGrfs[9].StatusMode1co:=Byte_0;
mind_bool[643]:=Exp1TlakAlarm; | mind[643]:=CrpalkeGrfs[9].StatusMode1op; |  |  |  |  | 643:Exp1TlakAlarm:=Bit_0; | 643:CrpalkeGrfs[9].StatusMode1op:=Byte_0;
mind_bool[644]:=Exp2TlakAlarm; | mind[644]:=CrpalkeGrfs[9].StatusMode2; |  |  |  |  | 644:Exp2TlakAlarm:=Bit_0; | 644:CrpalkeGrfs[9].StatusMode2:=Word_01;
mind_bool[645]:=HladilniStrojOnOff; | mind[645]:=CrpalkeGrfs[9].StatusMode3; |  |  |  |  | 645:HladilniStrojOnOff:=Bit_0; | 645:CrpalkeGrfs[9].StatusMode3:=Word_01;
mind_bool[646]:=HladStroj.FazeAlarm; | mind[646]:=DateTime.Dan; |  |  |  |  | 646:HladStroj.FazeAlarm:=Bit_0; | 646:DateTime.Dan:=Byte_0;
mind_bool[647]:=HladStroj.KompresorOljeAlarm; | mind[647]:=DateTime.Leto; |  |  |  |  | 647:HladStroj.KompresorOljeAlarm:=Bit_0; | 647:DateTime.Leto:=Byte_0;
mind_bool[648]:=HladStroj.LANcarelAlarm; | mind[648]:=DateTime.Mesec; |  |  |  |  | 648:HladStroj.LANcarelAlarm:=Bit_0; | 648:DateTime.Mesec:=Byte_0;
mind_bool[649]:=HladStroj.Napaka; | mind[649]:=DateTime.Minuta; |  |  |  |  | 649:HladStroj.Napaka:=Bit_0; | 649:DateTime.Minuta:=Byte_0;
mind_bool[650]:=HladStroj.NizekPritiskAlarm; | mind[650]:=DateTime.Sekunda; |  |  |  |  | 650:HladStroj.NizekPritiskAlarm:=Bit_0; | 650:DateTime.Sekunda:=Byte_0;
mind_bool[651]:=HladStroj.ObratovalneUreOpozorilo; | mind[651]:=DateTime.Ura; |  |  |  |  | 651:HladStroj.ObratovalneUreOpozorilo:=Bit_0; | 651:DateTime.Ura:=Byte_0;
mind_bool[652]:=HladStroj.OffByAlarms; | mind[652]:=HladStroj.KompresorOljeAlarmB; |  |  |  |  | 652:HladStroj.OffByAlarms:=Bit_0; | 652:HladStroj.KompresorOljeAlarmB:=Byte_0;
mind_bool[653]:=HladStroj.PretokAlarm; | mind[653]:=HladStroj.NizekPritiskAlarmB; |  |  |  |  | 653:HladStroj.PretokAlarm:=Bit_0; | 653:HladStroj.NizekPritiskAlarmB:=Byte_0;
mind_bool[654]:=HladStroj.RemoteOn; | mind[654]:=HladStroj.ObratovalneUreOpozoriloB; |  |  |  |  | 654:HladStroj.RemoteOn:=Bit_0; | 654:HladStroj.ObratovalneUreOpozoriloB:=Byte_0;
mind_bool[655]:=HladStroj.SenzorAlarm; | mind[655]:=HladStroj.TemperaturaAlarmB; |  |  |  |  | 655:HladStroj.SenzorAlarm:=Bit_0; | 655:HladStroj.TemperaturaAlarmB:=Byte_0;
mind_bool[656]:=HladStroj.SummerOperation; | mind[656]:=HladStroj.UnitStatus; |  |  |  |  | 656:HladStroj.SummerOperation:=Bit_0; | 656:HladStroj.UnitStatus:=Word_01;
mind_bool[657]:=HladStroj.TemperaturaAlarm; | mind[657]:=HladStroj.VisokPritiskAlarmB; |  |  |  |  | 657:HladStroj.TemperaturaAlarm:=Bit_0; | 657:HladStroj.VisokPritiskAlarmB:=Byte_0;
mind_bool[658]:=HladStroj.UnitOn; | mind[658]:=HladStroj.VisokPritiskOpozoriloB; |  |  |  |  | 658:HladStroj.UnitOn:=Bit_0; | 658:HladStroj.VisokPritiskOpozoriloB:=Byte_0;
mind_bool[659]:=HladStroj.UraAlarm; | mind[659]:=HladStroj.ZmrzalniAlarmB; |  |  |  |  | 659:HladStroj.UraAlarm:=Bit_0; | 659:HladStroj.ZmrzalniAlarmB:=Byte_0;
mind_bool[660]:=HladStroj.VisokPritiskAlarm; | mind[660]:=Klima[1].CrpalkaStatus; |  |  |  |  | 660:HladStroj.VisokPritiskAlarm:=Bit_0; | 660:Klima[1].CrpalkaStatus:=Byte_0;
mind_bool[661]:=HladStroj.VisokPritiskOpozorilo; | mind[661]:=Klima[1].HitrostVentStatus; |  |  |  |  | 661:HladStroj.VisokPritiskOpozorilo:=Bit_0; | 661:Klima[1].HitrostVentStatus:=Byte_0;
mind_bool[662]:=HladStroj.ZmrzalniAlarm; | mind[662]:=Klima[1].IzhodniVentStatus; |  |  |  |  | 662:HladStroj.ZmrzalniAlarm:=Bit_0; | 662:Klima[1].IzhodniVentStatus:=Byte_0;
mind_bool[663]:=HladStrojErrors[10]; | mind[663]:=Klima[2].CrpalkaStatus; |  |  |  |  | 663:HladStrojErrors[10]:=Bit_0; | 663:Klima[2].CrpalkaStatus:=Byte_0;
mind_bool[664]:=HladStrojErrors[11]; | mind[664]:=Klima[2].HitrostVentStatus; |  |  |  |  | 664:HladStrojErrors[11]:=Bit_0; | 664:Klima[2].HitrostVentStatus:=Byte_0;
mind_bool[665]:=HladStrojErrors[12]; | mind[665]:=Klima[2].IzhodniVentStatus; |  |  |  |  | 665:HladStrojErrors[12]:=Bit_0; | 665:Klima[2].IzhodniVentStatus:=Byte_0;
mind_bool[666]:=HladStrojErrors[13]; | mind[666]:=PozarnaLoputaStatus[1]; |  |  |  |  | 666:HladStrojErrors[13]:=Bit_0; | 666:PozarnaLoputaStatus[1]:=Byte_0;
mind_bool[667]:=HladStrojErrors[14]; | mind[667]:=PozarnaLoputaStatus[2]; |  |  |  |  | 667:HladStrojErrors[14]:=Bit_0; | 667:PozarnaLoputaStatus[2]:=Byte_0;
mind_bool[668]:=HladStrojErrors[15]; | mind[668]:=PozarnaLoputaStatus[3]; |  |  |  |  | 668:HladStrojErrors[15]:=Bit_0; | 668:PozarnaLoputaStatus[3]:=Byte_0;
mind_bool[669]:=HladStrojErrors[16]; | mind[669]:=PozarnaLoputaStatus[4]; |  |  |  |  | 669:HladStrojErrors[16]:=Bit_0; | 669:PozarnaLoputaStatus[4]:=Byte_0;
mind_bool[670]:=HladStrojErrors[1]; | mind[670]:=PozarnaLoputaStatus[5]; |  |  |  |  | 670:HladStrojErrors[1]:=Bit_0; | 670:PozarnaLoputaStatus[5]:=Byte_0;
mind_bool[671]:=HladStrojErrors[2]; | mind[671]:=StatusKondenzEnota[0]; |  |  |  |  | 671:HladStrojErrors[2]:=Bit_0; | 671:StatusKondenzEnota[0]:=Byte_0;
mind_bool[672]:=HladStrojErrors[3]; | mind[672]:=StatusKondenzEnota[1]; |  |  |  |  | 672:HladStrojErrors[3]:=Bit_0; | 672:StatusKondenzEnota[1]:=Byte_0;
mind_bool[673]:=HladStrojErrors[4]; | mind[673]:=StatusKondenzEnota[2]; |  |  |  |  | 673:HladStrojErrors[4]:=Bit_0; | 673:StatusKondenzEnota[2]:=Byte_0;
mind_bool[674]:=HladStrojErrors[5]; | mind[674]:=StatusKondenzEnota[3]; |  |  |  |  | 674:HladStrojErrors[5]:=Bit_0; | 674:StatusKondenzEnota[3]:=Byte_0;
mind_bool[675]:=HladStrojErrors[6]; | mind[675]:=StatusKontaktor[10]; |  |  |  |  | 675:HladStrojErrors[6]:=Bit_0; | 675:StatusKontaktor[10]:=Byte_0;
mind_bool[676]:=HladStrojErrors[7]; | mind[676]:=StatusKontaktor[11]; |  |  |  |  | 676:HladStrojErrors[7]:=Bit_0; | 676:StatusKontaktor[11]:=Byte_0;
mind_bool[677]:=HladStrojErrors[8]; | mind[677]:=StatusKontaktor[12]; |  |  |  |  | 677:HladStrojErrors[8]:=Bit_0; | 677:StatusKontaktor[12]:=Byte_0;
mind_bool[678]:=HladStrojErrors[9]; | mind[678]:=StatusKontaktor[13]; |  |  |  |  | 678:HladStrojErrors[9]:=Bit_0; | 678:StatusKontaktor[13]:=Byte_0;
mind_bool[679]:=Klima1errors[10]; | mind[679]:=StatusKontaktor[14]; |  |  |  |  | 679:Klima1errors[10]:=Bit_0; | 679:StatusKontaktor[14]:=Byte_0;
mind_bool[680]:=Klima1errors[11]; | mind[680]:=StatusKontaktor[15]; |  |  |  |  | 680:Klima1errors[11]:=Bit_0; | 680:StatusKontaktor[15]:=Byte_0;
mind_bool[681]:=Klima1errors[12]; | mind[681]:=StatusKontaktor[16]; |  |  |  |  | 681:Klima1errors[12]:=Bit_0; | 681:StatusKontaktor[16]:=Byte_0;
mind_bool[682]:=Klima1errors[1]; | mind[682]:=StatusKontaktor[17]; |  |  |  |  | 682:Klima1errors[1]:=Bit_0; | 682:StatusKontaktor[17]:=Byte_0;
mind_bool[683]:=Klima1errors[2]; | mind[683]:=StatusKontaktor[18]; |  |  |  |  | 683:Klima1errors[2]:=Bit_0; | 683:StatusKontaktor[18]:=Byte_0;
mind_bool[684]:=Klima1errors[3]; | mind[684]:=StatusKontaktor[19]; |  |  |  |  | 684:Klima1errors[3]:=Bit_0; | 684:StatusKontaktor[19]:=Byte_0;
mind_bool[685]:=Klima1errors[4]; | mind[685]:=StatusKontaktor[1]; |  |  |  |  | 685:Klima1errors[4]:=Bit_0; | 685:StatusKontaktor[1]:=Byte_0;
mind_bool[686]:=Klima1errors[5]; | mind[686]:=StatusKontaktor[20]; |  |  |  |  | 686:Klima1errors[5]:=Bit_0; | 686:StatusKontaktor[20]:=Byte_0;
mind_bool[687]:=Klima1errors[6]; | mind[687]:=StatusKontaktor[21]; |  |  |  |  | 687:Klima1errors[6]:=Bit_0; | 687:StatusKontaktor[21]:=Byte_0;
mind_bool[688]:=Klima1errors[7]; | mind[688]:=StatusKontaktor[22]; |  |  |  |  | 688:Klima1errors[7]:=Bit_0; | 688:StatusKontaktor[22]:=Byte_0;
mind_bool[689]:=Klima1errors[8]; | mind[689]:=StatusKontaktor[23]; |  |  |  |  | 689:Klima1errors[8]:=Bit_0; | 689:StatusKontaktor[23]:=Byte_0;
mind_bool[690]:=Klima1errors[9]; | mind[690]:=StatusKontaktor[24]; |  |  |  |  | 690:Klima1errors[9]:=Bit_0; | 690:StatusKontaktor[24]:=Byte_0;
mind_bool[691]:=Klima2errors[10]; | mind[691]:=StatusKontaktor[25]; |  |  |  |  | 691:Klima2errors[10]:=Bit_0; | 691:StatusKontaktor[25]:=Byte_0;
mind_bool[692]:=Klima2errors[11]; | mind[692]:=StatusKontaktor[2]; |  |  |  |  | 692:Klima2errors[11]:=Bit_0; | 692:StatusKontaktor[2]:=Byte_0;
mind_bool[693]:=Klima2errors[12]; | mind[693]:=StatusKontaktor[3]; |  |  |  |  | 693:Klima2errors[12]:=Bit_0; | 693:StatusKontaktor[3]:=Byte_0;
mind_bool[694]:=Klima2errors[1]; | mind[694]:=StatusKontaktor[4]; |  |  |  |  | 694:Klima2errors[1]:=Bit_0; | 694:StatusKontaktor[4]:=Byte_0;
mind_bool[695]:=Klima2errors[2]; | mind[695]:=StatusKontaktor[5]; |  |  |  |  | 695:Klima2errors[2]:=Bit_0; | 695:StatusKontaktor[5]:=Byte_0;
mind_bool[696]:=Klima2errors[3]; | mind[696]:=StatusKontaktor[6]; |  |  |  |  | 696:Klima2errors[3]:=Bit_0; | 696:StatusKontaktor[6]:=Byte_0;
mind_bool[697]:=Klima2errors[4]; | mind[697]:=StatusKontaktor[7]; |  |  |  |  | 697:Klima2errors[4]:=Bit_0; | 697:StatusKontaktor[7]:=Byte_0;
mind_bool[698]:=Klima2errors[5]; | mind[698]:=StatusKontaktor[8]; |  |  |  |  | 698:Klima2errors[5]:=Bit_0; | 698:StatusKontaktor[8]:=Byte_0;
mind_bool[699]:=Klima2errors[6]; | mind[699]:=StatusKontaktor[9]; |  |  |  |  | 699:Klima2errors[6]:=Bit_0; | 699:StatusKontaktor[9]:=Byte_0;
mind_bool[700]:=Klima2errors[7]; | mind[700]:=StatusPreklopke[10]; |  |  |  |  | 700:Klima2errors[7]:=Bit_0; | 700:StatusPreklopke[10]:=Byte_0;
mind_bool[701]:=Klima2errors[8]; | mind[701]:=StatusPreklopke[11]; |  |  |  |  | 701:Klima2errors[8]:=Bit_0; | 701:StatusPreklopke[11]:=Byte_0;
mind_bool[702]:=Klima2errors[9]; | mind[702]:=StatusPreklopke[12]; |  |  |  |  | 702:Klima2errors[9]:=Bit_0; | 702:StatusPreklopke[12]:=Byte_0;
mind_bool[703]:=Klima[1].CrpalkaGrelnika; | mind[703]:=StatusPreklopke[13]; |  |  |  |  | 703:Klima[1].CrpalkaGrelnika:=Bit_0; | 703:StatusPreklopke[13]:=Byte_0;
mind_bool[704]:=Klima[1].DelovanjeVentH1; | mind[704]:=StatusPreklopke[14]; |  |  |  |  | 704:Klima[1].DelovanjeVentH1:=Bit_0; | 704:StatusPreklopke[14]:=Byte_0;
mind_bool[705]:=Klima[1].DelovanjeVentH2; | mind[705]:=StatusPreklopke[15]; |  |  |  |  | 705:Klima[1].DelovanjeVentH2:=Bit_0; | 705:StatusPreklopke[15]:=Byte_0;
mind_bool[706]:=Klima[1].Deluje; | mind[706]:=StatusPreklopke[16]; |  |  |  |  | 706:Klima[1].Deluje:=Bit_0; | 706:StatusPreklopke[16]:=Byte_0;
mind_bool[707]:=Klima[1].FilterError; | mind[707]:=StatusPreklopke[17]; |  |  |  |  | 707:Klima[1].FilterError:=Bit_0; | 707:StatusPreklopke[17]:=Byte_0;
mind_bool[708]:=Klima[1].Napaka; | mind[708]:=StatusPreklopke[18]; |  |  |  |  | 708:Klima[1].Napaka:=Bit_0; | 708:StatusPreklopke[18]:=Byte_0;
mind_bool[709]:=Klima[1].NapakaPriPretokuZraka; | mind[709]:=StatusPreklopke[19]; |  |  |  |  | 709:Klima[1].NapakaPriPretokuZraka:=Bit_0; | 709:StatusPreklopke[19]:=Byte_0;
mind_bool[710]:=Klima[1].OkvaraRototerma; | mind[710]:=StatusPreklopke[1]; |  |  |  |  | 710:Klima[1].OkvaraRototerma:=Bit_0; | 710:StatusPreklopke[1]:=Byte_0;
mind_bool[711]:=Klima[1].OkvaraVlazilne; | mind[711]:=StatusPreklopke[20]; |  |  |  |  | 711:Klima[1].OkvaraVlazilne:=Bit_0; | 711:StatusPreklopke[20]:=Byte_0;
mind_bool[712]:=Klima[1].PozarError; | mind[712]:=StatusPreklopke[21]; |  |  |  |  | 712:Klima[1].PozarError:=Bit_0; | 712:StatusPreklopke[21]:=Byte_0;
mind_bool[713]:=Klima[1].PozarniAlarm; | mind[713]:=StatusPreklopke[22]; |  |  |  |  | 713:Klima[1].PozarniAlarm:=Bit_0; | 713:StatusPreklopke[22]:=Byte_0;
mind_bool[714]:=Klima[1].PreobremenitevMotCrpGr; | mind[714]:=StatusPreklopke[23]; |  |  |  |  | 714:Klima[1].PreobremenitevMotCrpGr:=Bit_0; | 714:StatusPreklopke[23]:=Byte_0;
mind_bool[715]:=Klima[1].PreobremenitevMotVent; | mind[715]:=StatusPreklopke[24]; |  |  |  |  | 715:Klima[1].PreobremenitevMotVent:=Bit_0; | 715:StatusPreklopke[24]:=Byte_0;
mind_bool[716]:=Klima[1].ProtizmrzAktivna; | mind[716]:=StatusPreklopke[25]; |  |  |  |  | 716:Klima[1].ProtizmrzAktivna:=Bit_0; | 716:StatusPreklopke[25]:=Byte_0;
mind_bool[717]:=Klima[1].SkupniAlarmA; | mind[717]:=StatusPreklopke[2]; |  |  |  |  | 717:Klima[1].SkupniAlarmA:=Bit_0; | 717:StatusPreklopke[2]:=Byte_0;
mind_bool[718]:=Klima[1].SkupniAlarmB; | mind[718]:=StatusPreklopke[3]; |  |  |  |  | 718:Klima[1].SkupniAlarmB:=Bit_0; | 718:StatusPreklopke[3]:=Byte_0;
mind_bool[719]:=Klima[1].VklopRegulacije; | mind[719]:=StatusPreklopke[4]; |  |  |  |  | 719:Klima[1].VklopRegulacije:=Bit_0; | 719:StatusPreklopke[4]:=Byte_0;
mind_bool[720]:=Klima[1].ZamasenFilter; | mind[720]:=StatusPreklopke[5]; |  |  |  |  | 720:Klima[1].ZamasenFilter:=Bit_0; | 720:StatusPreklopke[5]:=Byte_0;
mind_bool[721]:=Klima[2].CrpalkaGrelnika; | mind[721]:=StatusPreklopke[6]; |  |  |  |  | 721:Klima[2].CrpalkaGrelnika:=Bit_0; | 721:StatusPreklopke[6]:=Byte_0;
mind_bool[722]:=Klima[2].DelovanjeVentH1; | mind[722]:=StatusPreklopke[7]; |  |  |  |  | 722:Klima[2].DelovanjeVentH1:=Bit_0; | 722:StatusPreklopke[7]:=Byte_0;
mind_bool[723]:=Klima[2].DelovanjeVentH2; | mind[723]:=StatusPreklopke[8]; |  |  |  |  | 723:Klima[2].DelovanjeVentH2:=Bit_0; | 723:StatusPreklopke[8]:=Byte_0;
mind_bool[724]:=Klima[2].Deluje; | mind[724]:=StatusPreklopke[9]; |  |  |  |  | 724:Klima[2].Deluje:=Bit_0; | 724:StatusPreklopke[9]:=Byte_0;
mind_bool[725]:=Klima[2].FilterError; | mind[725]:=ToplPost.NapakaRegister; |  |  |  |  | 725:Klima[2].FilterError:=Bit_0; | 725:ToplPost.NapakaRegister:=Word_01;
mind_bool[726]:=Klima[2].Napaka; | mind[726]:=Urnik_SCtoXCpot; |  |  |  |  | 726:Klima[2].Napaka:=Bit_0; | 726:Urnik_SCtoXCpot:=Word_01;
mind_bool[727]:=Klima[2].NapakaPriPretokuZraka; | mind[727]:=Urnik_SCtoXCzah; |  |  |  |  | 727:Klima[2].NapakaPriPretokuZraka:=Bit_0; | 727:Urnik_SCtoXCzah:=Word_01;
mind_bool[728]:=Klima[2].OkvaraRototerma; | mind[728]:=Urnik_XCtoSCpot; |  |  |  |  | 728:Klima[2].OkvaraRototerma:=Bit_0; | 728:Urnik_XCtoSCpot:=Word_01;
mind_bool[729]:=Klima[2].OkvaraVlazilne; | mind[729]:=Urnik_XCtoSCzah; |  |  |  |  | 729:Klima[2].OkvaraVlazilne:=Bit_0; | 729:Urnik_XCtoSCzah:=Word_01;
mind_bool[730]:=Klima[2].PozarError; | mind[730]:=UrnikSCtoXC.Dan[1].Off[1].Mna; |  |  |  |  | 730:Klima[2].PozarError:=Bit_0; | 730:UrnikSCtoXC.Dan[1].Off[1].Mna:=Byte_0;
mind_bool[731]:=Klima[2].PozarniAlarm; | mind[731]:=UrnikSCtoXC.Dan[1].Off[1].Ura; |  |  |  |  | 731:Klima[2].PozarniAlarm:=Bit_0; | 731:UrnikSCtoXC.Dan[1].Off[1].Ura:=Byte_0;
mind_bool[732]:=Klima[2].PreobremenitevMotCrpGr; | mind[732]:=UrnikSCtoXC.Dan[1].Off[2].Mna; |  |  |  |  | 732:Klima[2].PreobremenitevMotCrpGr:=Bit_0; | 732:UrnikSCtoXC.Dan[1].Off[2].Mna:=Byte_0;
mind_bool[733]:=Klima[2].PreobremenitevMotVent; | mind[733]:=UrnikSCtoXC.Dan[1].Off[2].Ura; |  |  |  |  | 733:Klima[2].PreobremenitevMotVent:=Bit_0; | 733:UrnikSCtoXC.Dan[1].Off[2].Ura:=Byte_0;
mind_bool[734]:=Klima[2].ProtizmrzAktivna; | mind[734]:=UrnikSCtoXC.Dan[1].Off[3].Mna; |  |  |  |  | 734:Klima[2].ProtizmrzAktivna:=Bit_0; | 734:UrnikSCtoXC.Dan[1].Off[3].Mna:=Byte_0;
mind_bool[735]:=Klima[2].SkupniAlarmA; | mind[735]:=UrnikSCtoXC.Dan[1].Off[3].Ura; |  |  |  |  | 735:Klima[2].SkupniAlarmA:=Bit_0; | 735:UrnikSCtoXC.Dan[1].Off[3].Ura:=Byte_0;
mind_bool[736]:=Klima[2].SkupniAlarmB; | mind[736]:=UrnikSCtoXC.Dan[1].On[1].Mna; |  |  |  |  | 736:Klima[2].SkupniAlarmB:=Bit_0; | 736:UrnikSCtoXC.Dan[1].On[1].Mna:=Byte_0;
mind_bool[737]:=Klima[2].VklopRegulacije; | mind[737]:=UrnikSCtoXC.Dan[1].On[1].Ura; |  |  |  |  | 737:Klima[2].VklopRegulacije:=Bit_0; | 737:UrnikSCtoXC.Dan[1].On[1].Ura:=Byte_0;
mind_bool[738]:=Klima[2].ZamasenFilter; | mind[738]:=UrnikSCtoXC.Dan[1].On[2].Mna; |  |  |  |  | 738:Klima[2].ZamasenFilter:=Bit_0; | 738:UrnikSCtoXC.Dan[1].On[2].Mna:=Byte_0;
mind_bool[739]:=KondEnotaOnOff[1]; | mind[739]:=UrnikSCtoXC.Dan[1].On[2].Ura; |  |  |  |  | 739:KondEnotaOnOff[1]:=Bit_0; | 739:UrnikSCtoXC.Dan[1].On[2].Ura:=Byte_0;
mind_bool[740]:=KondEnotaOnOff[2]; | mind[740]:=UrnikSCtoXC.Dan[1].On[3].Mna; |  |  |  |  | 740:KondEnotaOnOff[2]:=Bit_0; | 740:UrnikSCtoXC.Dan[1].On[3].Mna:=Byte_0;
mind_bool[741]:=KondEnotaOnOff[3]; | mind[741]:=UrnikSCtoXC.Dan[1].On[3].Ura; |  |  |  |  | 741:KondEnotaOnOff[3]:=Bit_0; | 741:UrnikSCtoXC.Dan[1].On[3].Ura:=Byte_0;
mind_bool[742]:=KontRezervaOnOff[1]; | mind[742]:=UrnikSCtoXC.Dan[2].Off[1].Mna; |  |  |  |  | 742:KontRezervaOnOff[1]:=Bit_0; | 742:UrnikSCtoXC.Dan[2].Off[1].Mna:=Byte_0;
mind_bool[743]:=KontRezervaOnOff[2]; | mind[743]:=UrnikSCtoXC.Dan[2].Off[1].Ura; |  |  |  |  | 743:KontRezervaOnOff[2]:=Bit_0; | 743:UrnikSCtoXC.Dan[2].Off[1].Ura:=Byte_0;
mind_bool[744]:=KontRezervaOnOff[3]; | mind[744]:=UrnikSCtoXC.Dan[2].Off[2].Mna; |  |  |  |  | 744:KontRezervaOnOff[3]:=Bit_0; | 744:UrnikSCtoXC.Dan[2].Off[2].Mna:=Byte_0;
mind_bool[745]:=NapakaSenzorAI[10]; | mind[745]:=UrnikSCtoXC.Dan[2].Off[2].Ura; |  |  |  |  | 745:NapakaSenzorAI[10]:=Bit_0; | 745:UrnikSCtoXC.Dan[2].Off[2].Ura:=Byte_0;
mind_bool[746]:=NapakaSenzorAI[11]; | mind[746]:=UrnikSCtoXC.Dan[2].Off[3].Mna; |  |  |  |  | 746:NapakaSenzorAI[11]:=Bit_0; | 746:UrnikSCtoXC.Dan[2].Off[3].Mna:=Byte_0;
mind_bool[747]:=NapakaSenzorAI[12]; | mind[747]:=UrnikSCtoXC.Dan[2].Off[3].Ura; |  |  |  |  | 747:NapakaSenzorAI[12]:=Bit_0; | 747:UrnikSCtoXC.Dan[2].Off[3].Ura:=Byte_0;
mind_bool[748]:=NapakaSenzorAI[13]; | mind[748]:=UrnikSCtoXC.Dan[2].On[1].Mna; |  |  |  |  | 748:NapakaSenzorAI[13]:=Bit_0; | 748:UrnikSCtoXC.Dan[2].On[1].Mna:=Byte_0;
mind_bool[749]:=NapakaSenzorAI[14]; | mind[749]:=UrnikSCtoXC.Dan[2].On[1].Ura; |  |  |  |  | 749:NapakaSenzorAI[14]:=Bit_0; | 749:UrnikSCtoXC.Dan[2].On[1].Ura:=Byte_0;
mind_bool[750]:=NapakaSenzorAI[15]; | mind[750]:=UrnikSCtoXC.Dan[2].On[2].Mna; |  |  |  |  | 750:NapakaSenzorAI[15]:=Bit_0; | 750:UrnikSCtoXC.Dan[2].On[2].Mna:=Byte_0;
mind_bool[751]:=NapakaSenzorAI[16]; | mind[751]:=UrnikSCtoXC.Dan[2].On[2].Ura; |  |  |  |  | 751:NapakaSenzorAI[16]:=Bit_0; | 751:UrnikSCtoXC.Dan[2].On[2].Ura:=Byte_0;
mind_bool[752]:=NapakaSenzorAI[17]; | mind[752]:=UrnikSCtoXC.Dan[2].On[3].Mna; |  |  |  |  | 752:NapakaSenzorAI[17]:=Bit_0; | 752:UrnikSCtoXC.Dan[2].On[3].Mna:=Byte_0;
mind_bool[753]:=NapakaSenzorAI[18]; | mind[753]:=UrnikSCtoXC.Dan[2].On[3].Ura; |  |  |  |  | 753:NapakaSenzorAI[18]:=Bit_0; | 753:UrnikSCtoXC.Dan[2].On[3].Ura:=Byte_0;
mind_bool[754]:=NapakaSenzorAI[19]; | mind[754]:=UrnikSCtoXC.Dan[3].Off[1].Mna; |  |  |  |  | 754:NapakaSenzorAI[19]:=Bit_0; | 754:UrnikSCtoXC.Dan[3].Off[1].Mna:=Byte_0;
mind_bool[755]:=NapakaSenzorAI[1]; | mind[755]:=UrnikSCtoXC.Dan[3].Off[1].Ura; |  |  |  |  | 755:NapakaSenzorAI[1]:=Bit_0; | 755:UrnikSCtoXC.Dan[3].Off[1].Ura:=Byte_0;
mind_bool[756]:=NapakaSenzorAI[20]; | mind[756]:=UrnikSCtoXC.Dan[3].Off[2].Mna; |  |  |  |  | 756:NapakaSenzorAI[20]:=Bit_0; | 756:UrnikSCtoXC.Dan[3].Off[2].Mna:=Byte_0;
mind_bool[757]:=NapakaSenzorAI[21]; | mind[757]:=UrnikSCtoXC.Dan[3].Off[2].Ura; |  |  |  |  | 757:NapakaSenzorAI[21]:=Bit_0; | 757:UrnikSCtoXC.Dan[3].Off[2].Ura:=Byte_0;
mind_bool[758]:=NapakaSenzorAI[22]; | mind[758]:=UrnikSCtoXC.Dan[3].Off[3].Mna; |  |  |  |  | 758:NapakaSenzorAI[22]:=Bit_0; | 758:UrnikSCtoXC.Dan[3].Off[3].Mna:=Byte_0;
mind_bool[759]:=NapakaSenzorAI[23]; | mind[759]:=UrnikSCtoXC.Dan[3].Off[3].Ura; |  |  |  |  | 759:NapakaSenzorAI[23]:=Bit_0; | 759:UrnikSCtoXC.Dan[3].Off[3].Ura:=Byte_0;
mind_bool[760]:=NapakaSenzorAI[24]; | mind[760]:=UrnikSCtoXC.Dan[3].On[1].Mna; |  |  |  |  | 760:NapakaSenzorAI[24]:=Bit_0; | 760:UrnikSCtoXC.Dan[3].On[1].Mna:=Byte_0;
mind_bool[761]:=NapakaSenzorAI[25]; | mind[761]:=UrnikSCtoXC.Dan[3].On[1].Ura; |  |  |  |  | 761:NapakaSenzorAI[25]:=Bit_0; | 761:UrnikSCtoXC.Dan[3].On[1].Ura:=Byte_0;
mind_bool[762]:=NapakaSenzorAI[26]; | mind[762]:=UrnikSCtoXC.Dan[3].On[2].Mna; |  |  |  |  | 762:NapakaSenzorAI[26]:=Bit_0; | 762:UrnikSCtoXC.Dan[3].On[2].Mna:=Byte_0;
mind_bool[763]:=NapakaSenzorAI[27]; | mind[763]:=UrnikSCtoXC.Dan[3].On[2].Ura; |  |  |  |  | 763:NapakaSenzorAI[27]:=Bit_0; | 763:UrnikSCtoXC.Dan[3].On[2].Ura:=Byte_0;
mind_bool[764]:=NapakaSenzorAI[28]; | mind[764]:=UrnikSCtoXC.Dan[3].On[3].Mna; |  |  |  |  | 764:NapakaSenzorAI[28]:=Bit_0; | 764:UrnikSCtoXC.Dan[3].On[3].Mna:=Byte_0;
mind_bool[765]:=NapakaSenzorAI[29]; | mind[765]:=UrnikSCtoXC.Dan[3].On[3].Ura; |  |  |  |  | 765:NapakaSenzorAI[29]:=Bit_0; | 765:UrnikSCtoXC.Dan[3].On[3].Ura:=Byte_0;
mind_bool[766]:=NapakaSenzorAI[2]; | mind[766]:=UrnikSCtoXC.Dan[4].Off[1].Mna; |  |  |  |  | 766:NapakaSenzorAI[2]:=Bit_0; | 766:UrnikSCtoXC.Dan[4].Off[1].Mna:=Byte_0;
mind_bool[767]:=NapakaSenzorAI[30]; | mind[767]:=UrnikSCtoXC.Dan[4].Off[1].Ura; |  |  |  |  | 767:NapakaSenzorAI[30]:=Bit_0; | 767:UrnikSCtoXC.Dan[4].Off[1].Ura:=Byte_0;
mind_bool[768]:=NapakaSenzorAI[31]; | mind[768]:=UrnikSCtoXC.Dan[4].Off[2].Mna; |  |  |  |  | 768:NapakaSenzorAI[31]:=Bit_0; | 768:UrnikSCtoXC.Dan[4].Off[2].Mna:=Byte_0;
mind_bool[769]:=NapakaSenzorAI[32]; | mind[769]:=UrnikSCtoXC.Dan[4].Off[2].Ura; |  |  |  |  | 769:NapakaSenzorAI[32]:=Bit_0; | 769:UrnikSCtoXC.Dan[4].Off[2].Ura:=Byte_0;
mind_bool[770]:=NapakaSenzorAI[33]; | mind[770]:=UrnikSCtoXC.Dan[4].Off[3].Mna; |  |  |  |  | 770:NapakaSenzorAI[33]:=Bit_0; | 770:UrnikSCtoXC.Dan[4].Off[3].Mna:=Byte_0;
mind_bool[771]:=NapakaSenzorAI[34]; | mind[771]:=UrnikSCtoXC.Dan[4].Off[3].Ura; |  |  |  |  | 771:NapakaSenzorAI[34]:=Bit_0; | 771:UrnikSCtoXC.Dan[4].Off[3].Ura:=Byte_0;
mind_bool[772]:=NapakaSenzorAI[35]; | mind[772]:=UrnikSCtoXC.Dan[4].On[1].Mna; |  |  |  |  | 772:NapakaSenzorAI[35]:=Bit_0; | 772:UrnikSCtoXC.Dan[4].On[1].Mna:=Byte_0;
mind_bool[773]:=NapakaSenzorAI[36]; | mind[773]:=UrnikSCtoXC.Dan[4].On[1].Ura; |  |  |  |  | 773:NapakaSenzorAI[36]:=Bit_0; | 773:UrnikSCtoXC.Dan[4].On[1].Ura:=Byte_0;
mind_bool[774]:=NapakaSenzorAI[37]; | mind[774]:=UrnikSCtoXC.Dan[4].On[2].Mna; |  |  |  |  | 774:NapakaSenzorAI[37]:=Bit_0; | 774:UrnikSCtoXC.Dan[4].On[2].Mna:=Byte_0;
mind_bool[775]:=NapakaSenzorAI[38]; | mind[775]:=UrnikSCtoXC.Dan[4].On[2].Ura; |  |  |  |  | 775:NapakaSenzorAI[38]:=Bit_0; | 775:UrnikSCtoXC.Dan[4].On[2].Ura:=Byte_0;
mind_bool[776]:=NapakaSenzorAI[39]; | mind[776]:=UrnikSCtoXC.Dan[4].On[3].Mna; |  |  |  |  | 776:NapakaSenzorAI[39]:=Bit_0; | 776:UrnikSCtoXC.Dan[4].On[3].Mna:=Byte_0;
mind_bool[777]:=NapakaSenzorAI[3]; | mind[777]:=UrnikSCtoXC.Dan[4].On[3].Ura; |  |  |  |  | 777:NapakaSenzorAI[3]:=Bit_0; | 777:UrnikSCtoXC.Dan[4].On[3].Ura:=Byte_0;
mind_bool[778]:=NapakaSenzorAI[40]; | mind[778]:=UrnikSCtoXC.Dan[5].Off[1].Mna; |  |  |  |  | 778:NapakaSenzorAI[40]:=Bit_0; | 778:UrnikSCtoXC.Dan[5].Off[1].Mna:=Byte_0;
mind_bool[779]:=NapakaSenzorAI[4]; | mind[779]:=UrnikSCtoXC.Dan[5].Off[1].Ura; |  |  |  |  | 779:NapakaSenzorAI[4]:=Bit_0; | 779:UrnikSCtoXC.Dan[5].Off[1].Ura:=Byte_0;
mind_bool[780]:=NapakaSenzorAI[5]; | mind[780]:=UrnikSCtoXC.Dan[5].Off[2].Mna; |  |  |  |  | 780:NapakaSenzorAI[5]:=Bit_0; | 780:UrnikSCtoXC.Dan[5].Off[2].Mna:=Byte_0;
mind_bool[781]:=NapakaSenzorAI[6]; | mind[781]:=UrnikSCtoXC.Dan[5].Off[2].Ura; |  |  |  |  | 781:NapakaSenzorAI[6]:=Bit_0; | 781:UrnikSCtoXC.Dan[5].Off[2].Ura:=Byte_0;
mind_bool[782]:=NapakaSenzorAI[7]; | mind[782]:=UrnikSCtoXC.Dan[5].Off[3].Mna; |  |  |  |  | 782:NapakaSenzorAI[7]:=Bit_0; | 782:UrnikSCtoXC.Dan[5].Off[3].Mna:=Byte_0;
mind_bool[783]:=NapakaSenzorAI[8]; | mind[783]:=UrnikSCtoXC.Dan[5].Off[3].Ura; |  |  |  |  | 783:NapakaSenzorAI[8]:=Bit_0; | 783:UrnikSCtoXC.Dan[5].Off[3].Ura:=Byte_0;
mind_bool[784]:=NapakaSenzorAI[9]; | mind[784]:=UrnikSCtoXC.Dan[5].On[1].Mna; |  |  |  |  | 784:NapakaSenzorAI[9]:=Bit_0; | 784:UrnikSCtoXC.Dan[5].On[1].Mna:=Byte_0;
mind_bool[785]:=NapakaSenzorHIA[1]; | mind[785]:=UrnikSCtoXC.Dan[5].On[1].Ura; |  |  |  |  | 785:NapakaSenzorHIA[1]:=Bit_0; | 785:UrnikSCtoXC.Dan[5].On[1].Ura:=Byte_0;
mind_bool[786]:=NapakaSenzorHIA[2]; | mind[786]:=UrnikSCtoXC.Dan[5].On[2].Mna; |  |  |  |  | 786:NapakaSenzorHIA[2]:=Bit_0; | 786:UrnikSCtoXC.Dan[5].On[2].Mna:=Byte_0;
mind_bool[787]:=NapakaSenzorHIA[3]; | mind[787]:=UrnikSCtoXC.Dan[5].On[2].Ura; |  |  |  |  | 787:NapakaSenzorHIA[3]:=Bit_0; | 787:UrnikSCtoXC.Dan[5].On[2].Ura:=Byte_0;
mind_bool[788]:=NapakaSenzorHIA[4]; | mind[788]:=UrnikSCtoXC.Dan[5].On[3].Mna; |  |  |  |  | 788:NapakaSenzorHIA[4]:=Bit_0; | 788:UrnikSCtoXC.Dan[5].On[3].Mna:=Byte_0;
mind_bool[789]:=NapakaSenzorTIA[1]; | mind[789]:=UrnikSCtoXC.Dan[5].On[3].Ura; |  |  |  |  | 789:NapakaSenzorTIA[1]:=Bit_0; | 789:UrnikSCtoXC.Dan[5].On[3].Ura:=Byte_0;
mind_bool[790]:=NapakaSenzorTIA[2]; | mind[790]:=UrnikSCtoXC.Dan[6].Off[1].Mna; |  |  |  |  | 790:NapakaSenzorTIA[2]:=Bit_0; | 790:UrnikSCtoXC.Dan[6].Off[1].Mna:=Byte_0;
mind_bool[791]:=NapakaSenzorTIA[3]; | mind[791]:=UrnikSCtoXC.Dan[6].Off[1].Ura; |  |  |  |  | 791:NapakaSenzorTIA[3]:=Bit_0; | 791:UrnikSCtoXC.Dan[6].Off[1].Ura:=Byte_0;
mind_bool[792]:=NapakaSenzorTIA[4]; | mind[792]:=UrnikSCtoXC.Dan[6].Off[2].Mna; |  |  |  |  | 792:NapakaSenzorTIA[4]:=Bit_0; | 792:UrnikSCtoXC.Dan[6].Off[2].Mna:=Byte_0;
mind_bool[793]:=PozarnaLoputaOnOffError[1]; | mind[793]:=UrnikSCtoXC.Dan[6].Off[2].Ura; |  |  |  |  | 793:PozarnaLoputaOnOffError[1]:=Bit_0; | 793:UrnikSCtoXC.Dan[6].Off[2].Ura:=Byte_0;
mind_bool[794]:=PozarnaLoputaOnOffError[2]; | mind[794]:=UrnikSCtoXC.Dan[6].Off[3].Mna; |  |  |  |  | 794:PozarnaLoputaOnOffError[2]:=Bit_0; | 794:UrnikSCtoXC.Dan[6].Off[3].Mna:=Byte_0;
mind_bool[795]:=PozarnaLoputaOnOffError[3]; | mind[795]:=UrnikSCtoXC.Dan[6].Off[3].Ura; |  |  |  |  | 795:PozarnaLoputaOnOffError[3]:=Bit_0; | 795:UrnikSCtoXC.Dan[6].Off[3].Ura:=Byte_0;
mind_bool[796]:=PozarnaLoputaOnOffError[4]; | mind[796]:=UrnikSCtoXC.Dan[6].On[1].Mna; |  |  |  |  | 796:PozarnaLoputaOnOffError[4]:=Bit_0; | 796:UrnikSCtoXC.Dan[6].On[1].Mna:=Byte_0;
mind_bool[797]:=PozarnaLoputaOnOffError[5]; | mind[797]:=UrnikSCtoXC.Dan[6].On[1].Ura; |  |  |  |  | 797:PozarnaLoputaOnOffError[5]:=Bit_0; | 797:UrnikSCtoXC.Dan[6].On[1].Ura:=Byte_0;
mind_bool[798]:=PozarnaLoputOnOff[1]; | mind[798]:=UrnikSCtoXC.Dan[6].On[2].Mna; |  |  |  |  | 798:PozarnaLoputOnOff[1]:=Bit_0; | 798:UrnikSCtoXC.Dan[6].On[2].Mna:=Byte_0;
mind_bool[799]:=PozarnaLoputOnOff[2]; | mind[799]:=UrnikSCtoXC.Dan[6].On[2].Ura; |  |  |  |  | 799:PozarnaLoputOnOff[2]:=Bit_0; | 799:UrnikSCtoXC.Dan[6].On[2].Ura:=Byte_0;
mind_bool[800]:=PozarnaLoputOnOff[3]; | mind[800]:=UrnikSCtoXC.Dan[6].On[3].Mna; |  |  |  |  | 800:PozarnaLoputOnOff[3]:=Bit_0; | 800:UrnikSCtoXC.Dan[6].On[3].Mna:=Byte_0;
mind_bool[801]:=PozarnaLoputOnOff[4]; | mind[801]:=UrnikSCtoXC.Dan[6].On[3].Ura; |  |  |  |  | 801:PozarnaLoputOnOff[4]:=Bit_0; | 801:UrnikSCtoXC.Dan[6].On[3].Ura:=Byte_0;
mind_bool[802]:=PozarnaLoputOnOff[5]; | mind[802]:=UrnikSCtoXC.Dan[7].Off[1].Mna; |  |  |  |  | 802:PozarnaLoputOnOff[5]:=Bit_0; | 802:UrnikSCtoXC.Dan[7].Off[1].Mna:=Byte_0;
mind_bool[803]:=PozarniAlarm; | mind[803]:=UrnikSCtoXC.Dan[7].Off[1].Ura; |  |  |  |  | 803:PozarniAlarm:=Bit_0; | 803:UrnikSCtoXC.Dan[7].Off[1].Ura:=Byte_0;
mind_bool[804]:=PrenosUrnika[10]; | mind[804]:=UrnikSCtoXC.Dan[7].Off[2].Mna; |  |  |  |  | 804:PrenosUrnika[10]:=Bit_0; | 804:UrnikSCtoXC.Dan[7].Off[2].Mna:=Byte_0;
mind_bool[805]:=PrenosUrnika[11]; | mind[805]:=UrnikSCtoXC.Dan[7].Off[2].Ura; |  |  |  |  | 805:PrenosUrnika[11]:=Bit_0; | 805:UrnikSCtoXC.Dan[7].Off[2].Ura:=Byte_0;
mind_bool[806]:=PrenosUrnika[12]; | mind[806]:=UrnikSCtoXC.Dan[7].Off[3].Mna; |  |  |  |  | 806:PrenosUrnika[12]:=Bit_0; | 806:UrnikSCtoXC.Dan[7].Off[3].Mna:=Byte_0;
mind_bool[807]:=PrenosUrnika[13]; | mind[807]:=UrnikSCtoXC.Dan[7].Off[3].Ura; |  |  |  |  | 807:PrenosUrnika[13]:=Bit_0; | 807:UrnikSCtoXC.Dan[7].Off[3].Ura:=Byte_0;
mind_bool[808]:=PrenosUrnika[14]; | mind[808]:=UrnikSCtoXC.Dan[7].On[1].Mna; |  |  |  |  | 808:PrenosUrnika[14]:=Bit_0; | 808:UrnikSCtoXC.Dan[7].On[1].Mna:=Byte_0;
mind_bool[809]:=PrenosUrnika[15]; | mind[809]:=UrnikSCtoXC.Dan[7].On[1].Ura; |  |  |  |  | 809:PrenosUrnika[15]:=Bit_0; | 809:UrnikSCtoXC.Dan[7].On[1].Ura:=Byte_0;
mind_bool[810]:=PrenosUrnika[16]; | mind[810]:=UrnikSCtoXC.Dan[7].On[2].Mna; |  |  |  |  | 810:PrenosUrnika[16]:=Bit_0; | 810:UrnikSCtoXC.Dan[7].On[2].Mna:=Byte_0;
mind_bool[811]:=PrenosUrnika[17]; | mind[811]:=UrnikSCtoXC.Dan[7].On[2].Ura; |  |  |  |  | 811:PrenosUrnika[17]:=Bit_0; | 811:UrnikSCtoXC.Dan[7].On[2].Ura:=Byte_0;
mind_bool[812]:=PrenosUrnika[18]; | mind[812]:=UrnikSCtoXC.Dan[7].On[3].Mna; |  |  |  |  | 812:PrenosUrnika[18]:=Bit_0; | 812:UrnikSCtoXC.Dan[7].On[3].Mna:=Byte_0;
mind_bool[813]:=PrenosUrnika[19]; | mind[813]:=UrnikSCtoXC.Dan[7].On[3].Ura; |  |  |  |  | 813:PrenosUrnika[19]:=Bit_0; | 813:UrnikSCtoXC.Dan[7].On[3].Ura:=Byte_0;
mind_bool[814]:=PrenosUrnika[1]; | mind[814]:=UrnikXCtoSC.Dan[1].Off[1].Mna; |  |  |  |  | 814:PrenosUrnika[1]:=Bit_0; | 814:UrnikXCtoSC.Dan[1].Off[1].Mna:=Byte_0;
mind_bool[815]:=PrenosUrnika[20]; | mind[815]:=UrnikXCtoSC.Dan[1].Off[1].Ura; |  |  |  |  | 815:PrenosUrnika[20]:=Bit_0; | 815:UrnikXCtoSC.Dan[1].Off[1].Ura:=Byte_0;
mind_bool[816]:=PrenosUrnika[21]; | mind[816]:=UrnikXCtoSC.Dan[1].Off[2].Mna; |  |  |  |  | 816:PrenosUrnika[21]:=Bit_0; | 816:UrnikXCtoSC.Dan[1].Off[2].Mna:=Byte_0;
mind_bool[817]:=PrenosUrnika[22]; | mind[817]:=UrnikXCtoSC.Dan[1].Off[2].Ura; |  |  |  |  | 817:PrenosUrnika[22]:=Bit_0; | 817:UrnikXCtoSC.Dan[1].Off[2].Ura:=Byte_0;
mind_bool[818]:=PrenosUrnika[23]; | mind[818]:=UrnikXCtoSC.Dan[1].Off[3].Mna; |  |  |  |  | 818:PrenosUrnika[23]:=Bit_0; | 818:UrnikXCtoSC.Dan[1].Off[3].Mna:=Byte_0;
mind_bool[819]:=PrenosUrnika[24]; | mind[819]:=UrnikXCtoSC.Dan[1].Off[3].Ura; |  |  |  |  | 819:PrenosUrnika[24]:=Bit_0; | 819:UrnikXCtoSC.Dan[1].Off[3].Ura:=Byte_0;
mind_bool[820]:=PrenosUrnika[25]; | mind[820]:=UrnikXCtoSC.Dan[1].On[1].Mna; |  |  |  |  | 820:PrenosUrnika[25]:=Bit_0; | 820:UrnikXCtoSC.Dan[1].On[1].Mna:=Byte_0;
mind_bool[821]:=PrenosUrnika[2]; | mind[821]:=UrnikXCtoSC.Dan[1].On[1].Ura; |  |  |  |  | 821:PrenosUrnika[2]:=Bit_0; | 821:UrnikXCtoSC.Dan[1].On[1].Ura:=Byte_0;
mind_bool[822]:=PrenosUrnika[3]; | mind[822]:=UrnikXCtoSC.Dan[1].On[2].Mna; |  |  |  |  | 822:PrenosUrnika[3]:=Bit_0; | 822:UrnikXCtoSC.Dan[1].On[2].Mna:=Byte_0;
mind_bool[823]:=PrenosUrnika[4]; | mind[823]:=UrnikXCtoSC.Dan[1].On[2].Ura; |  |  |  |  | 823:PrenosUrnika[4]:=Bit_0; | 823:UrnikXCtoSC.Dan[1].On[2].Ura:=Byte_0;
mind_bool[824]:=PrenosUrnika[5]; | mind[824]:=UrnikXCtoSC.Dan[1].On[3].Mna; |  |  |  |  | 824:PrenosUrnika[5]:=Bit_0; | 824:UrnikXCtoSC.Dan[1].On[3].Mna:=Byte_0;
mind_bool[825]:=PrenosUrnika[6]; | mind[825]:=UrnikXCtoSC.Dan[1].On[3].Ura; |  |  |  |  | 825:PrenosUrnika[6]:=Bit_0; | 825:UrnikXCtoSC.Dan[1].On[3].Ura:=Byte_0;
mind_bool[826]:=PrenosUrnika[7]; | mind[826]:=UrnikXCtoSC.Dan[2].Off[1].Mna; |  |  |  |  | 826:PrenosUrnika[7]:=Bit_0; | 826:UrnikXCtoSC.Dan[2].Off[1].Mna:=Byte_0;
mind_bool[827]:=PrenosUrnika[8]; | mind[827]:=UrnikXCtoSC.Dan[2].Off[1].Ura; |  |  |  |  | 827:PrenosUrnika[8]:=Bit_0; | 827:UrnikXCtoSC.Dan[2].Off[1].Ura:=Byte_0;
mind_bool[828]:=PrenosUrnika[9]; | mind[828]:=UrnikXCtoSC.Dan[2].Off[2].Mna; |  |  |  |  | 828:PrenosUrnika[9]:=Bit_0; | 828:UrnikXCtoSC.Dan[2].Off[2].Mna:=Byte_0;
mind_bool[829]:=RazsvetljavaOnOff[10]; | mind[829]:=UrnikXCtoSC.Dan[2].Off[2].Ura; |  |  |  |  | 829:RazsvetljavaOnOff[10]:=Bit_0; | 829:UrnikXCtoSC.Dan[2].Off[2].Ura:=Byte_0;
mind_bool[830]:=RazsvetljavaOnOff[11]; | mind[830]:=UrnikXCtoSC.Dan[2].Off[3].Mna; |  |  |  |  | 830:RazsvetljavaOnOff[11]:=Bit_0; | 830:UrnikXCtoSC.Dan[2].Off[3].Mna:=Byte_0;
mind_bool[831]:=RazsvetljavaOnOff[12]; | mind[831]:=UrnikXCtoSC.Dan[2].Off[3].Ura; |  |  |  |  | 831:RazsvetljavaOnOff[12]:=Bit_0; | 831:UrnikXCtoSC.Dan[2].Off[3].Ura:=Byte_0;
mind_bool[832]:=RazsvetljavaOnOff[13]; | mind[832]:=UrnikXCtoSC.Dan[2].On[1].Mna; |  |  |  |  | 832:RazsvetljavaOnOff[13]:=Bit_0; | 832:UrnikXCtoSC.Dan[2].On[1].Mna:=Byte_0;
mind_bool[833]:=RazsvetljavaOnOff[14]; | mind[833]:=UrnikXCtoSC.Dan[2].On[1].Ura; |  |  |  |  | 833:RazsvetljavaOnOff[14]:=Bit_0; | 833:UrnikXCtoSC.Dan[2].On[1].Ura:=Byte_0;
mind_bool[834]:=RazsvetljavaOnOff[15]; | mind[834]:=UrnikXCtoSC.Dan[2].On[2].Mna; |  |  |  |  | 834:RazsvetljavaOnOff[15]:=Bit_0; | 834:UrnikXCtoSC.Dan[2].On[2].Mna:=Byte_0;
mind_bool[835]:=RazsvetljavaOnOff[16]; | mind[835]:=UrnikXCtoSC.Dan[2].On[2].Ura; |  |  |  |  | 835:RazsvetljavaOnOff[16]:=Bit_0; | 835:UrnikXCtoSC.Dan[2].On[2].Ura:=Byte_0;
mind_bool[836]:=RazsvetljavaOnOff[17]; | mind[836]:=UrnikXCtoSC.Dan[2].On[3].Mna; |  |  |  |  | 836:RazsvetljavaOnOff[17]:=Bit_0; | 836:UrnikXCtoSC.Dan[2].On[3].Mna:=Byte_0;
mind_bool[837]:=RazsvetljavaOnOff[18]; | mind[837]:=UrnikXCtoSC.Dan[2].On[3].Ura; |  |  |  |  | 837:RazsvetljavaOnOff[18]:=Bit_0; | 837:UrnikXCtoSC.Dan[2].On[3].Ura:=Byte_0;
mind_bool[838]:=RazsvetljavaOnOff[19]; | mind[838]:=UrnikXCtoSC.Dan[3].Off[1].Mna; |  |  |  |  | 838:RazsvetljavaOnOff[19]:=Bit_0; | 838:UrnikXCtoSC.Dan[3].Off[1].Mna:=Byte_0;
mind_bool[839]:=RazsvetljavaOnOff[1]; | mind[839]:=UrnikXCtoSC.Dan[3].Off[1].Ura; |  |  |  |  | 839:RazsvetljavaOnOff[1]:=Bit_0; | 839:UrnikXCtoSC.Dan[3].Off[1].Ura:=Byte_0;
mind_bool[840]:=RazsvetljavaOnOff[20]; | mind[840]:=UrnikXCtoSC.Dan[3].Off[2].Mna; |  |  |  |  | 840:RazsvetljavaOnOff[20]:=Bit_0; | 840:UrnikXCtoSC.Dan[3].Off[2].Mna:=Byte_0;
mind_bool[841]:=RazsvetljavaOnOff[21]; | mind[841]:=UrnikXCtoSC.Dan[3].Off[2].Ura; |  |  |  |  | 841:RazsvetljavaOnOff[21]:=Bit_0; | 841:UrnikXCtoSC.Dan[3].Off[2].Ura:=Byte_0;
mind_bool[842]:=RazsvetljavaOnOff[22]; | mind[842]:=UrnikXCtoSC.Dan[3].Off[3].Mna; |  |  |  |  | 842:RazsvetljavaOnOff[22]:=Bit_0; | 842:UrnikXCtoSC.Dan[3].Off[3].Mna:=Byte_0;
mind_bool[843]:=RazsvetljavaOnOff[23]; | mind[843]:=UrnikXCtoSC.Dan[3].Off[3].Ura; |  |  |  |  | 843:RazsvetljavaOnOff[23]:=Bit_0; | 843:UrnikXCtoSC.Dan[3].Off[3].Ura:=Byte_0;
mind_bool[844]:=RazsvetljavaOnOff[24]; | mind[844]:=UrnikXCtoSC.Dan[3].On[1].Mna; |  |  |  |  | 844:RazsvetljavaOnOff[24]:=Bit_0; | 844:UrnikXCtoSC.Dan[3].On[1].Mna:=Byte_0;
mind_bool[845]:=RazsvetljavaOnOff[25]; | mind[845]:=UrnikXCtoSC.Dan[3].On[1].Ura; |  |  |  |  | 845:RazsvetljavaOnOff[25]:=Bit_0; | 845:UrnikXCtoSC.Dan[3].On[1].Ura:=Byte_0;
mind_bool[846]:=RazsvetljavaOnOff[2]; | mind[846]:=UrnikXCtoSC.Dan[3].On[2].Mna; |  |  |  |  | 846:RazsvetljavaOnOff[2]:=Bit_0; | 846:UrnikXCtoSC.Dan[3].On[2].Mna:=Byte_0;
mind_bool[847]:=RazsvetljavaOnOff[3]; | mind[847]:=UrnikXCtoSC.Dan[3].On[2].Ura; |  |  |  |  | 847:RazsvetljavaOnOff[3]:=Bit_0; | 847:UrnikXCtoSC.Dan[3].On[2].Ura:=Byte_0;
mind_bool[848]:=RazsvetljavaOnOff[4]; | mind[848]:=UrnikXCtoSC.Dan[3].On[3].Mna; |  |  |  |  | 848:RazsvetljavaOnOff[4]:=Bit_0; | 848:UrnikXCtoSC.Dan[3].On[3].Mna:=Byte_0;
mind_bool[849]:=RazsvetljavaOnOff[5]; | mind[849]:=UrnikXCtoSC.Dan[3].On[3].Ura; |  |  |  |  | 849:RazsvetljavaOnOff[5]:=Bit_0; | 849:UrnikXCtoSC.Dan[3].On[3].Ura:=Byte_0;
mind_bool[850]:=RazsvetljavaOnOff[6]; | mind[850]:=UrnikXCtoSC.Dan[4].Off[1].Mna; |  |  |  |  | 850:RazsvetljavaOnOff[6]:=Bit_0; | 850:UrnikXCtoSC.Dan[4].Off[1].Mna:=Byte_0;
mind_bool[851]:=RazsvetljavaOnOff[7]; | mind[851]:=UrnikXCtoSC.Dan[4].Off[1].Ura; |  |  |  |  | 851:RazsvetljavaOnOff[7]:=Bit_0; | 851:UrnikXCtoSC.Dan[4].Off[1].Ura:=Byte_0;
mind_bool[852]:=RazsvetljavaOnOff[8]; | mind[852]:=UrnikXCtoSC.Dan[4].Off[2].Mna; |  |  |  |  | 852:RazsvetljavaOnOff[8]:=Bit_0; | 852:UrnikXCtoSC.Dan[4].Off[2].Mna:=Byte_0;
mind_bool[853]:=RazsvetljavaOnOff[9]; | mind[853]:=UrnikXCtoSC.Dan[4].Off[2].Ura; |  |  |  |  | 853:RazsvetljavaOnOff[9]:=Bit_0; | 853:UrnikXCtoSC.Dan[4].Off[2].Ura:=Byte_0;
mind_bool[854]:=RazsvetljavaRocno; | mind[854]:=UrnikXCtoSC.Dan[4].Off[3].Mna; |  |  |  |  | 854:RazsvetljavaRocno:=Bit_0; | 854:UrnikXCtoSC.Dan[4].Off[3].Mna:=Byte_0;
mind_bool[855]:=SetDateTime; | mind[855]:=UrnikXCtoSC.Dan[4].Off[3].Ura; |  |  |  |  | 855:SetDateTime:=Bit_0; | 855:UrnikXCtoSC.Dan[4].Off[3].Ura:=Byte_0;
mind_bool[856]:=SetDateTimeDemand; | mind[856]:=UrnikXCtoSC.Dan[4].On[1].Mna; |  |  |  |  | 856:SetDateTimeDemand:=Bit_0; | 856:UrnikXCtoSC.Dan[4].On[1].Mna:=Byte_0;
mind_bool[857]:=SetDateTimeError; | mind[857]:=UrnikXCtoSC.Dan[4].On[1].Ura; |  |  |  |  | 857:SetDateTimeError:=Bit_0; | 857:UrnikXCtoSC.Dan[4].On[1].Ura:=Byte_0;
mind_bool[858]:=SetDateTimeFinished; | mind[858]:=UrnikXCtoSC.Dan[4].On[2].Mna; |  |  |  |  | 858:SetDateTimeFinished:=Bit_0; | 858:UrnikXCtoSC.Dan[4].On[2].Mna:=Byte_0;
mind_bool[859]:=SetRemoteOnOff[1]; | mind[859]:=UrnikXCtoSC.Dan[4].On[2].Ura; |  |  |  |  | 859:SetRemoteOnOff[1]:=Bit_0; | 859:UrnikXCtoSC.Dan[4].On[2].Ura:=Byte_0;
mind_bool[860]:=SetRemoteOnOff[2]; | mind[860]:=UrnikXCtoSC.Dan[4].On[3].Mna; |  |  |  |  | 860:SetRemoteOnOff[2]:=Bit_0; | 860:UrnikXCtoSC.Dan[4].On[3].Mna:=Byte_0;
mind_bool[861]:=SlabaBaterijaPLC_A1; | mind[861]:=UrnikXCtoSC.Dan[4].On[3].Ura; |  |  |  |  | 861:SlabaBaterijaPLC_A1:=Bit_0; | 861:UrnikXCtoSC.Dan[4].On[3].Ura:=Byte_0;
mind_bool[862]:=SlabaBaterijaPLC_A100; | mind[862]:=UrnikXCtoSC.Dan[5].Off[1].Mna; |  |  |  |  | 862:SlabaBaterijaPLC_A100:=Bit_0; | 862:UrnikXCtoSC.Dan[5].Off[1].Mna:=Byte_0;
mind_bool[863]:=SO_BojlerTE1Vklop; | mind[863]:=UrnikXCtoSC.Dan[5].Off[1].Ura; |  |  |  |  | 863:SO_BojlerTE1Vklop:=Bit_0; | 863:UrnikXCtoSC.Dan[5].Off[1].Ura:=Byte_0;
mind_bool[864]:=SO_CrpHM1Vklop; | mind[864]:=UrnikXCtoSC.Dan[5].Off[2].Mna; |  |  |  |  | 864:SO_CrpHM1Vklop:=Bit_0; | 864:UrnikXCtoSC.Dan[5].Off[2].Mna:=Byte_0;
mind_bool[865]:=SO_CrpHM2Vklop; | mind[865]:=UrnikXCtoSC.Dan[5].Off[2].Ura; |  |  |  |  | 865:SO_CrpHM2Vklop:=Bit_0; | 865:UrnikXCtoSC.Dan[5].Off[2].Ura:=Byte_0;
mind_bool[866]:=SO_CrpHM3Vklop; | mind[866]:=UrnikXCtoSC.Dan[5].Off[3].Mna; |  |  |  |  | 866:SO_CrpHM3Vklop:=Bit_0; | 866:UrnikXCtoSC.Dan[5].Off[3].Mna:=Byte_0;
mind_bool[867]:=SO_CrpHM4Vklop; | mind[867]:=UrnikXCtoSC.Dan[5].Off[3].Ura; |  |  |  |  | 867:SO_CrpHM4Vklop:=Bit_0; | 867:UrnikXCtoSC.Dan[5].Off[3].Ura:=Byte_0;
mind_bool[868]:=SO_CrpMN1Vklop; | mind[868]:=UrnikXCtoSC.Dan[5].On[1].Mna; |  |  |  |  | 868:SO_CrpMN1Vklop:=Bit_0; | 868:UrnikXCtoSC.Dan[5].On[1].Mna:=Byte_0;
mind_bool[869]:=SO_CrpTM11Vklop; | mind[869]:=UrnikXCtoSC.Dan[5].On[1].Ura; |  |  |  |  | 869:SO_CrpTM11Vklop:=Bit_0; | 869:UrnikXCtoSC.Dan[5].On[1].Ura:=Byte_0;
mind_bool[870]:=SO_HladStrVklop; | mind[870]:=UrnikXCtoSC.Dan[5].On[2].Mna; |  |  |  |  | 870:SO_HladStrVklop:=Bit_0; | 870:UrnikXCtoSC.Dan[5].On[2].Mna:=Byte_0;
mind_bool[871]:=SO_KE1Vklop; | mind[871]:=UrnikXCtoSC.Dan[5].On[2].Ura; |  |  |  |  | 871:SO_KE1Vklop:=Bit_0; | 871:UrnikXCtoSC.Dan[5].On[2].Ura:=Byte_0;
mind_bool[872]:=SO_KE2Vklop; | mind[872]:=UrnikXCtoSC.Dan[5].On[3].Mna; |  |  |  |  | 872:SO_KE2Vklop:=Bit_0; | 872:UrnikXCtoSC.Dan[5].On[3].Mna:=Byte_0;
mind_bool[873]:=SO_KE3Vklop; | mind[873]:=UrnikXCtoSC.Dan[5].On[3].Ura; |  |  |  |  | 873:SO_KE3Vklop:=Bit_0; | 873:UrnikXCtoSC.Dan[5].On[3].Ura:=Byte_0;
mind_bool[874]:=SO_rezerva1_3; | mind[874]:=UrnikXCtoSC.Dan[6].Off[1].Mna; |  |  |  |  | 874:SO_rezerva1_3:=Bit_0; | 874:UrnikXCtoSC.Dan[6].Off[1].Mna:=Byte_0;
mind_bool[875]:=SO_rezerva1_4; | mind[875]:=UrnikXCtoSC.Dan[6].Off[1].Ura; |  |  |  |  | 875:SO_rezerva1_4:=Bit_0; | 875:UrnikXCtoSC.Dan[6].Off[1].Ura:=Byte_0;
mind_bool[876]:=SO_rezerva1_5; | mind[876]:=UrnikXCtoSC.Dan[6].Off[2].Mna; |  |  |  |  | 876:SO_rezerva1_5:=Bit_0; | 876:UrnikXCtoSC.Dan[6].Off[2].Mna:=Byte_0;
mind_bool[877]:=SO_Vent1Vklop; | mind[877]:=UrnikXCtoSC.Dan[6].Off[2].Ura; |  |  |  |  | 877:SO_Vent1Vklop:=Bit_0; | 877:UrnikXCtoSC.Dan[6].Off[2].Ura:=Byte_0;
mind_bool[878]:=SO_Vent2Vklop; | mind[878]:=UrnikXCtoSC.Dan[6].Off[3].Mna; |  |  |  |  | 878:SO_Vent2Vklop:=Bit_0; | 878:UrnikXCtoSC.Dan[6].Off[3].Mna:=Byte_0;
mind_bool[879]:=SO_Vent3Vklop; | mind[879]:=UrnikXCtoSC.Dan[6].Off[3].Ura; |  |  |  |  | 879:SO_Vent3Vklop:=Bit_0; | 879:UrnikXCtoSC.Dan[6].Off[3].Ura:=Byte_0;
mind_bool[880]:=SO_Vent4Vklop; | mind[880]:=UrnikXCtoSC.Dan[6].On[1].Mna; |  |  |  |  | 880:SO_Vent4Vklop:=Bit_0; | 880:UrnikXCtoSC.Dan[6].On[1].Mna:=Byte_0;
mind_bool[881]:=SO_Vent5Vklop; | mind[881]:=UrnikXCtoSC.Dan[6].On[1].Ura; |  |  |  |  | 881:SO_Vent5Vklop:=Bit_0; | 881:UrnikXCtoSC.Dan[6].On[1].Ura:=Byte_0;
mind_bool[882]:=SO_Vent6Vklop; | mind[882]:=UrnikXCtoSC.Dan[6].On[2].Mna; |  |  |  |  | 882:SO_Vent6Vklop:=Bit_0; | 882:UrnikXCtoSC.Dan[6].On[2].Mna:=Byte_0;
mind_bool[883]:=TEgrelecNaTemp; | mind[883]:=UrnikXCtoSC.Dan[6].On[2].Ura; |  |  |  |  | 883:TEgrelecNaTemp:=Bit_0; | 883:UrnikXCtoSC.Dan[6].On[2].Ura:=Byte_0;
mind_bool[884]:=TEgrelecTempVklop; | mind[884]:=UrnikXCtoSC.Dan[6].On[3].Mna; |  |  |  |  | 884:TEgrelecTempVklop:=Bit_0; | 884:UrnikXCtoSC.Dan[6].On[3].Mna:=Byte_0;
mind_bool[885]:=TempTSprevisoka; | mind[885]:=UrnikXCtoSC.Dan[6].On[3].Ura; |  |  |  |  | 885:TempTSprevisoka:=Bit_0; | 885:UrnikXCtoSC.Dan[6].On[3].Ura:=Byte_0;
mind_bool[886]:=ToplPost.HKcrpalkaON; | mind[886]:=UrnikXCtoSC.Dan[7].Off[1].Mna; |  |  |  |  | 886:ToplPost.HKcrpalkaON:=Bit_0; | 886:UrnikXCtoSC.Dan[7].Off[1].Mna:=Byte_0;
mind_bool[887]:=ToplPost.HKcrpDnevniRezim; | mind[887]:=UrnikXCtoSC.Dan[7].Off[1].Ura; |  |  |  |  | 887:ToplPost.HKcrpDnevniRezim:=Bit_0; | 887:UrnikXCtoSC.Dan[7].Off[1].Ura:=Byte_0;
mind_bool[888]:=ToplPost.HKcrpNocniRezim; | mind[888]:=UrnikXCtoSC.Dan[7].Off[2].Mna; |  |  |  |  | 888:ToplPost.HKcrpNocniRezim:=Bit_0; | 888:UrnikXCtoSC.Dan[7].Off[2].Mna:=Byte_0;
mind_bool[889]:=ToplPost.HKrocniRezim; | mind[889]:=UrnikXCtoSC.Dan[7].Off[2].Ura; |  |  |  |  | 889:ToplPost.HKrocniRezim:=Bit_0; | 889:UrnikXCtoSC.Dan[7].Off[2].Ura:=Byte_0;
mind_bool[890]:=ToplPost.SkupnaNapaka; | mind[890]:=UrnikXCtoSC.Dan[7].Off[3].Mna; |  |  |  |  | 890:ToplPost.SkupnaNapaka:=Bit_0; | 890:UrnikXCtoSC.Dan[7].Off[3].Mna:=Byte_0;
mind_bool[891]:=ToplPost.TVcrpalkaON; | mind[891]:=UrnikXCtoSC.Dan[7].Off[3].Ura; |  |  |  |  | 891:ToplPost.TVcrpalkaON:=Bit_0; | 891:UrnikXCtoSC.Dan[7].Off[3].Ura:=Byte_0;
mind_bool[892]:=ToplPost.TVrocniRezim; | mind[892]:=UrnikXCtoSC.Dan[7].On[1].Mna; |  |  |  |  | 892:ToplPost.TVrocniRezim:=Bit_0; | 892:UrnikXCtoSC.Dan[7].On[1].Mna:=Byte_0;
mind_bool[893]:=ToplPostErrors[0]; | mind[893]:=UrnikXCtoSC.Dan[7].On[1].Ura; |  |  |  |  | 893:ToplPostErrors[0]:=Bit_0; | 893:UrnikXCtoSC.Dan[7].On[1].Ura:=Byte_0;
mind_bool[894]:=ToplPostErrors[10]; | mind[894]:=UrnikXCtoSC.Dan[7].On[2].Mna; |  |  |  |  | 894:ToplPostErrors[10]:=Bit_0; | 894:UrnikXCtoSC.Dan[7].On[2].Mna:=Byte_0;
mind_bool[895]:=ToplPostErrors[11]; | mind[895]:=UrnikXCtoSC.Dan[7].On[2].Ura; |  |  |  |  | 895:ToplPostErrors[11]:=Bit_0; | 895:UrnikXCtoSC.Dan[7].On[2].Ura:=Byte_0;
mind_bool[896]:=ToplPostErrors[12]; | mind[896]:=UrnikXCtoSC.Dan[7].On[3].Mna; |  |  |  |  | 896:ToplPostErrors[12]:=Bit_0; | 896:UrnikXCtoSC.Dan[7].On[3].Mna:=Byte_0;
mind_bool[897]:=ToplPostErrors[13]; | mind[897]:=UrnikXCtoSC.Dan[7].On[3].Ura; |  |  |  |  | 897:ToplPostErrors[13]:=Bit_0; | 897:UrnikXCtoSC.Dan[7].On[3].Ura:=Byte_0;
mind_bool[898]:=ToplPostErrors[14]; | mind[898]:=UserCurrentLevel; |  |  |  |  | 898:ToplPostErrors[14]:=Bit_0; | 898:UserCurrentLevel:=Byte_0;
mind_bool[899]:=ToplPostErrors[15]; | mind[899]:=CrpalkeGrfsGal.AlarmActiveCode; |  |  |  |  | 899:ToplPostErrors[15]:=Bit_0; | 899:CrpalkeGrfsGal.AlarmActiveCode:=Word_01;
mind_bool[900]:=ToplPostErrors[16]; | mind[900]:=CrpalkeGrfsGal.AlarmCodeLog1; |  |  |  |  | 900:ToplPostErrors[16]:=Bit_0; | 900:CrpalkeGrfsGal.AlarmCodeLog1:=Word_01;
mind_bool[901]:=ToplPostErrors[17]; | mind[901]:=CrpalkeGrfsGal.AlarmCodeLog2; |  |  |  |  | 901:ToplPostErrors[17]:=Bit_0; | 901:CrpalkeGrfsGal.AlarmCodeLog2:=Word_01;
mind_bool[902]:=ToplPostErrors[1]; | mind[902]:=CrpalkeGrfsGal.AlarmCodeLog3; |  |  |  |  | 902:ToplPostErrors[1]:=Bit_0; | 902:CrpalkeGrfsGal.AlarmCodeLog3:=Word_01;
mind_bool[903]:=ToplPostErrors[2]; | mind[903]:=CrpalkeGrfsGal.AlarmCodeLog4; |  |  |  |  | 903:ToplPostErrors[2]:=Bit_0; | 903:CrpalkeGrfsGal.AlarmCodeLog4:=Word_01;
mind_bool[904]:=ToplPostErrors[3]; | mind[904]:=CrpalkeGrfsGal.AlarmCodeLog5; |  |  |  |  | 904:ToplPostErrors[3]:=Bit_0; | 904:CrpalkeGrfsGal.AlarmCodeLog5:=Word_01;
mind_bool[905]:=ToplPostErrors[4]; | mind[905]:=CrpalkeGrfsGal.AlarmGroupXVH[0]; |  |  |  |  | 905:ToplPostErrors[4]:=Bit_0; | 905:CrpalkeGrfsGal.AlarmGroupXVH[0]:=Word_01;
mind_bool[906]:=ToplPostErrors[5]; | mind[906]:=CrpalkeGrfsGal.AlarmGroupXVH[10]; |  |  |  |  | 906:ToplPostErrors[5]:=Bit_0; | 906:CrpalkeGrfsGal.AlarmGroupXVH[10]:=Word_01;
mind_bool[907]:=ToplPostErrors[6]; | mind[907]:=CrpalkeGrfsGal.AlarmGroupXVH[11]; |  |  |  |  | 907:ToplPostErrors[6]:=Bit_0; | 907:CrpalkeGrfsGal.AlarmGroupXVH[11]:=Word_01;
mind_bool[908]:=ToplPostErrors[7]; | mind[908]:=CrpalkeGrfsGal.AlarmGroupXVH[12]; |  |  |  |  | 908:ToplPostErrors[7]:=Bit_0; | 908:CrpalkeGrfsGal.AlarmGroupXVH[12]:=Word_01;
mind_bool[909]:=ToplPostErrors[8]; | mind[909]:=CrpalkeGrfsGal.AlarmGroupXVH[13]; |  |  |  |  | 909:ToplPostErrors[8]:=Bit_0; | 909:CrpalkeGrfsGal.AlarmGroupXVH[13]:=Word_01;
mind_bool[910]:=ToplPostErrors[9]; | mind[910]:=CrpalkeGrfsGal.AlarmGroupXVH[14]; |  |  |  |  | 910:ToplPostErrors[9]:=Bit_0; | 910:CrpalkeGrfsGal.AlarmGroupXVH[14]:=Word_01;
mind_bool[911]:=TYventilNaTemp[1]; | mind[911]:=CrpalkeGrfsGal.AlarmGroupXVH[15]; |  |  |  |  | 911:TYventilNaTemp[1]:=Bit_0; | 911:CrpalkeGrfsGal.AlarmGroupXVH[15]:=Word_01;
mind_bool[912]:=TYventilNaTemp[2]; | mind[912]:=CrpalkeGrfsGal.AlarmGroupXVH[16]; |  |  |  |  | 912:TYventilNaTemp[2]:=Bit_0; | 912:CrpalkeGrfsGal.AlarmGroupXVH[16]:=Word_01;
mind_bool[913]:=TYventilNaTemp[3]; | mind[913]:=CrpalkeGrfsGal.AlarmGroupXVH[1]; |  |  |  |  | 913:TYventilNaTemp[3]:=Bit_0; | 913:CrpalkeGrfsGal.AlarmGroupXVH[1]:=Word_01;
mind_bool[914]:=TYventilNaTemp[4]; | mind[914]:=CrpalkeGrfsGal.AlarmGroupXVH[2]; |  |  |  |  | 914:TYventilNaTemp[4]:=Bit_0; | 914:CrpalkeGrfsGal.AlarmGroupXVH[2]:=Word_01;
mind_bool[915]:=UserLoggedIn; | mind[915]:=CrpalkeGrfsGal.AlarmGroupXVH[3]; |  |  |  |  | 915:UserLoggedIn:=Bit_0; | 915:CrpalkeGrfsGal.AlarmGroupXVH[3]:=Word_01;
mind_bool[916]:=VentilatorOnOff[1]; | mind[916]:=CrpalkeGrfsGal.AlarmGroupXVH[4]; |  |  |  |  | 916:VentilatorOnOff[1]:=Bit_0; | 916:CrpalkeGrfsGal.AlarmGroupXVH[4]:=Word_01;
mind_bool[917]:=VentilatorOnOff[2]; | mind[917]:=CrpalkeGrfsGal.AlarmGroupXVH[5]; |  |  |  |  | 917:VentilatorOnOff[2]:=Bit_0; | 917:CrpalkeGrfsGal.AlarmGroupXVH[5]:=Word_01;
mind_bool[918]:=VentilatorOnOff[3]; | mind[918]:=CrpalkeGrfsGal.AlarmGroupXVH[6]; |  |  |  |  | 918:VentilatorOnOff[3]:=Bit_0; | 918:CrpalkeGrfsGal.AlarmGroupXVH[6]:=Word_01;
mind_bool[919]:=VentilatorOnOff[4]; | mind[919]:=CrpalkeGrfsGal.AlarmGroupXVH[7]; |  |  |  |  | 919:VentilatorOnOff[4]:=Bit_0; | 919:CrpalkeGrfsGal.AlarmGroupXVH[7]:=Word_01;
mind_bool[920]:=VentilatorOnOff[5]; | mind[920]:=CrpalkeGrfsGal.AlarmGroupXVH[8]; |  |  |  |  | 920:VentilatorOnOff[5]:=Bit_0; | 920:CrpalkeGrfsGal.AlarmGroupXVH[8]:=Word_01;
mind_bool[921]:=VentilatorOnOff[6]; | mind[921]:=CrpalkeGrfsGal.AlarmGroupXVH[9]; |  |  |  |  | 921:VentilatorOnOff[6]:=Bit_0; | 921:CrpalkeGrfsGal.AlarmGroupXVH[9]:=Word_01;
mind_bool[922]:=VklopSCFBNapaka[10]; | mind[922]:=CrpalkeGrfsGal.AlarmQSD1; |  |  |  |  | 922:VklopSCFBNapaka[10]:=Bit_0; | 922:CrpalkeGrfsGal.AlarmQSD1:=Word_01;
mind_bool[923]:=VklopSCFBNapaka[11]; | mind[923]:=CrpalkeGrfsGal.AlarmQSD2; |  |  |  |  | 923:VklopSCFBNapaka[11]:=Bit_0; | 923:CrpalkeGrfsGal.AlarmQSD2:=Word_01;
mind_bool[924]:=VklopSCFBNapaka[12]; | mind[924]:=CrpalkeGrfsGal.AlarmStart1; |  |  |  |  | 924:VklopSCFBNapaka[12]:=Bit_0; | 924:CrpalkeGrfsGal.AlarmStart1:=Word_01;
mind_bool[925]:=VklopSCFBNapaka[13]; | mind[925]:=CrpalkeGrfsGal.AlarmStart2; |  |  |  |  | 925:VklopSCFBNapaka[13]:=Bit_0; | 925:CrpalkeGrfsGal.AlarmStart2:=Word_01;
mind_bool[926]:=VklopSCFBNapaka[14]; | mind[926]:=CrpalkeGrfsGal.AlarmStop1; |  |  |  |  | 926:VklopSCFBNapaka[14]:=Bit_0; | 926:CrpalkeGrfsGal.AlarmStop1:=Word_01;
mind_bool[927]:=VklopSCFBNapaka[15]; | mind[927]:=CrpalkeGrfsGal.AlarmStop2; |  |  |  |  | 927:VklopSCFBNapaka[15]:=Bit_0; | 927:CrpalkeGrfsGal.AlarmStop2:=Word_01;
mind_bool[928]:=VklopSCFBNapaka[16]; | mind[928]:=CrpalkeGrfsGal.AlarmStop3; |  |  |  |  | 928:VklopSCFBNapaka[16]:=Bit_0; | 928:CrpalkeGrfsGal.AlarmStop3:=Word_01;
mind_bool[929]:=VklopSCFBNapaka[17]; | mind[929]:=CrpalkeGrfsGal.AlarmSurv1; |  |  |  |  | 929:VklopSCFBNapaka[17]:=Bit_0; | 929:CrpalkeGrfsGal.AlarmSurv1:=Word_01;
mind_bool[930]:=VklopSCFBNapaka[18]; | mind[930]:=CrpalkeGrfsGal.AlarmSurv2; |  |  |  |  | 930:VklopSCFBNapaka[18]:=Bit_0; | 930:CrpalkeGrfsGal.AlarmSurv2:=Word_01;
mind_bool[931]:=VklopSCFBNapaka[19]; | mind[931]:=CrpalkeGrfsGal.ControlSource; |  |  |  |  | 931:VklopSCFBNapaka[19]:=Bit_0; | 931:CrpalkeGrfsGal.ControlSource:=Word_01;
mind_bool[932]:=VklopSCFBNapaka[1]; | mind[932]:=CrpalkeGrfsGal.ExternInputSetup; |  |  |  |  | 932:VklopSCFBNapaka[1]:=Bit_0; | 932:CrpalkeGrfsGal.ExternInputSetup:=Word_01;
mind_bool[933]:=VklopSCFBNapaka[20]; | mind[933]:=CrpalkeGrfsGal.ExternInputsStatus; |  |  |  |  | 933:VklopSCFBNapaka[20]:=Bit_0; | 933:CrpalkeGrfsGal.ExternInputsStatus:=Word_01;
mind_bool[934]:=VklopSCFBNapaka[21]; | mind[934]:=CrpalkeGrfsGal.LocalSetupMode1; |  |  |  |  | 934:VklopSCFBNapaka[21]:=Bit_0; | 934:CrpalkeGrfsGal.LocalSetupMode1:=Word_01;
mind_bool[935]:=VklopSCFBNapaka[22]; | mind[935]:=CrpalkeGrfsGal.PreklopkaMode; |  |  |  |  | 935:VklopSCFBNapaka[22]:=Bit_0; | 935:CrpalkeGrfsGal.PreklopkaMode:=Word_01;
mind_bool[936]:=VklopSCFBNapaka[23]; | mind[936]:=CrpalkeGrfsGal.Relay1setup; |  |  |  |  | 936:VklopSCFBNapaka[23]:=Bit_0; | 936:CrpalkeGrfsGal.Relay1setup:=Word_01;
mind_bool[937]:=VklopSCFBNapaka[24]; | mind[937]:=CrpalkeGrfsGal.RemoteSetupMode1; |  |  |  |  | 937:VklopSCFBNapaka[24]:=Bit_0; | 937:CrpalkeGrfsGal.RemoteSetupMode1:=Word_01;
mind_bool[938]:=VklopSCFBNapaka[25]; | mind[938]:=CrpalkeGrfsGal.StatusCrpalke; |  |  |  |  | 938:VklopSCFBNapaka[25]:=Bit_0; | 938:CrpalkeGrfsGal.StatusCrpalke:=Byte_0;
mind_bool[939]:=VklopSCFBNapaka[2]; | mind[939]:=CrpalkeGrfsGal.StatusMode1; |  |  |  |  | 939:VklopSCFBNapaka[2]:=Bit_0; | 939:CrpalkeGrfsGal.StatusMode1:=Word_01;
mind_bool[940]:=VklopSCFBNapaka[3]; | mind[940]:=CrpalkeGrfsGal.StatusMode1co; |  |  |  |  | 940:VklopSCFBNapaka[3]:=Bit_0; | 940:CrpalkeGrfsGal.StatusMode1co:=Byte_0;
mind_bool[941]:=VklopSCFBNapaka[4]; | mind[941]:=CrpalkeGrfsGal.StatusMode1op; |  |  |  |  | 941:VklopSCFBNapaka[4]:=Bit_0; | 941:CrpalkeGrfsGal.StatusMode1op:=Byte_0;
mind_bool[942]:=VklopSCFBNapaka[5]; | mind[942]:=CrpalkeGrfsGal.StatusMode2; |  |  |  |  | 942:VklopSCFBNapaka[5]:=Bit_0; | 942:CrpalkeGrfsGal.StatusMode2:=Word_01;
mind_bool[943]:=VklopSCFBNapaka[6]; | mind[943]:=CrpalkeGrfsGal.StatusMode3; |  |  |  |  | 943:VklopSCFBNapaka[6]:=Bit_0; | 943:CrpalkeGrfsGal.StatusMode3:=Word_01;
mind_bool[944]:=VklopSCFBNapaka[7]; | mind[944]:=CrpGrfsPIDregTN; |  |  |  |  | 944:VklopSCFBNapaka[7]:=Bit_0; | 944:CrpGrfsPIDregTN:=Word_01;
mind_bool[945]:=VklopSCFBNapaka[8]; | mind[945]:=DateTime.DanVtednu; |  |  |  |  | 945:VklopSCFBNapaka[8]:=Bit_0; | 945:DateTime.DanVtednu:=Byte_0;
mind_bool[946]:=VklopSCFBNapaka[9]; | mind[946]:=LetniCasDatumi[1,1,1]; |  |  |  |  | 946:VklopSCFBNapaka[9]:=Bit_0; | 946:LetniCasDatumi[1,1,1]:=Word_01;
mind_bool[947]:=XVH_AlarmOn; | mind[947]:=LetniCasDatumi[1,1,2]; |  |  |  |  | 947:XVH_AlarmOn:=Bit_0; | 947:LetniCasDatumi[1,1,2]:=Word_01;
mind_bool[948]:=XVH_IzklopVsehLuci; | mind[948]:=LetniCasDatumi[1,2,1]; |  |  |  |  | 948:XVH_IzklopVsehLuci:=Bit_0; | 948:LetniCasDatumi[1,2,1]:=Word_01;
mind_bool[949]:=XVH_VklopVsehLuci; | mind[949]:=LetniCasDatumi[1,2,2]; |  |  |  |  | 949:XVH_VklopVsehLuci:=Bit_0; | 949:LetniCasDatumi[1,2,2]:=Word_01;
mind_bool[950]:=PrenasanjeUrnikovAktivno; | mind[950]:=LetniCasDatumi[1,3,1]; |  |  |  |  | 950:PrenasanjeUrnikovAktivno:=Bit_0; | 950:LetniCasDatumi[1,3,1]:=Word_01;
mind_bool[951]:=PrenasanjeUrnikovAktivno1; | mind[951]:=LetniCasDatumi[1,3,2]; |  |  |  |  | 951:PrenasanjeUrnikovAktivno1:=Bit_0; | 951:LetniCasDatumi[1,3,2]:=Word_01;
mind_bool[952]:=CrpalkeGrfsGal.AlarmAktiven; | mind[952]:=LetniCasDatumi[1,4,1]; |  |  |  |  | 952:CrpalkeGrfsGal.AlarmAktiven:=Bit_0; | 952:LetniCasDatumi[1,4,1]:=Word_01;
mind_bool[953]:=CrpalkeGrfsGal.Deluje; | mind[953]:=LetniCasDatumi[1,4,2]; |  |  |  |  | 953:CrpalkeGrfsGal.Deluje:=Bit_0; | 953:LetniCasDatumi[1,4,2]:=Word_01;
mind_bool[954]:=CrpalkeGrfsGal.LocalMode; | mind[954]:=LetniCasDatumi[2,1,1]; |  |  |  |  | 954:CrpalkeGrfsGal.LocalMode:=Bit_0; | 954:LetniCasDatumi[2,1,1]:=Word_01;
mind_bool[955]:=CrpalkeGrfsGal.RemoteON; | mind[955]:=LetniCasDatumi[2,1,2]; |  |  |  |  | 955:CrpalkeGrfsGal.RemoteON:=Bit_0; | 955:LetniCasDatumi[2,1,2]:=Word_01;
mind_bool[956]:=CrpalkeGrfsGal.Reset2handkWhValues; | mind[956]:=LetniCasDatumi[2,2,1]; |  |  |  |  | 956:CrpalkeGrfsGal.Reset2handkWhValues:=Bit_0; | 956:LetniCasDatumi[2,2,1]:=Word_01;
mind_bool[957]:=CrpalkeGrfsGal.ResetAlarm; | mind[957]:=LetniCasDatumi[2,2,2]; |  |  |  |  | 957:CrpalkeGrfsGal.ResetAlarm:=Bit_0; | 957:LetniCasDatumi[2,2,2]:=Word_01;
mind_bool[958]:=CrpalkeGrfsGal.ResetAlarmLog; | mind[958]:=LetniCasDatumi[2,3,1]; |  |  |  |  | 958:CrpalkeGrfsGal.ResetAlarmLog:=Bit_0; | 958:LetniCasDatumi[2,3,1]:=Word_01;
mind_bool[959]:=CrpalkeGrfsGal.ResetDevice; | mind[959]:=LetniCasDatumi[2,3,2]; |  |  |  |  | 959:CrpalkeGrfsGal.ResetDevice:=Bit_0; | 959:LetniCasDatumi[2,3,2]:=Word_01;
mind_bool[960]:=CrpalkeGrfsGal.SetAutomatic; | mind[960]:=LetniCasDatumi[2,4,1]; |  |  |  |  | 960:CrpalkeGrfsGal.SetAutomatic:=Bit_0; | 960:LetniCasDatumi[2,4,1]:=Word_01;
mind_bool[961]:=CrpalkeGrfsGal.SetConstFreqMode; | mind[961]:=LetniCasDatumi[2,4,2]; |  |  |  |  | 961:CrpalkeGrfsGal.SetConstFreqMode:=Bit_0; | 961:LetniCasDatumi[2,4,2]:=Word_01;
mind_bool[962]:=CrpalkeGrfsGal.SetConstPress; | mind[962]:=UrnikSave.Dan[1].Off[1].Mna; |  |  |  |  | 962:CrpalkeGrfsGal.SetConstPress:=Bit_0; | 962:UrnikSave.Dan[1].Off[1].Mna:=Byte_0;
mind_bool[963]:=CrpalkeGrfsGal.SetLocalMode; | mind[963]:=UrnikSave.Dan[1].Off[1].Ura; |  |  |  |  | 963:CrpalkeGrfsGal.SetLocalMode:=Bit_0; | 963:UrnikSave.Dan[1].Off[1].Ura:=Byte_0;
mind_bool[964]:=CrpalkeGrfsGal.SetMaxRunMode; | mind[964]:=UrnikSave.Dan[1].Off[2].Mna; |  |  |  |  | 964:CrpalkeGrfsGal.SetMaxRunMode:=Bit_0; | 964:UrnikSave.Dan[1].Off[2].Mna:=Byte_0;
mind_bool[965]:=CrpalkeGrfsGal.SetMinRunMode; | mind[965]:=UrnikSave.Dan[1].Off[2].Ura; |  |  |  |  | 965:CrpalkeGrfsGal.SetMinRunMode:=Bit_0; | 965:UrnikSave.Dan[1].Off[2].Ura:=Byte_0;
mind_bool[966]:=CrpalkeGrfsGal.SetPropPress; | mind[966]:=UrnikSave.Dan[1].Off[3].Mna; |  |  |  |  | 966:CrpalkeGrfsGal.SetPropPress:=Bit_0; | 966:UrnikSave.Dan[1].Off[3].Mna:=Byte_0;
mind_bool[967]:=CrpalkeGrfsGal.SetReference; | mind[967]:=UrnikSave.Dan[1].Off[3].Ura; |  |  |  |  | 967:CrpalkeGrfsGal.SetReference:=Bit_0; | 967:UrnikSave.Dan[1].Off[3].Ura:=Byte_0;
mind_bool[968]:=CrpalkeGrfsGal.SetRemoteMode; | mind[968]:=UrnikSave.Dan[1].On[1].Mna; |  |  |  |  | 968:CrpalkeGrfsGal.SetRemoteMode:=Bit_0; | 968:UrnikSave.Dan[1].On[1].Mna:=Byte_0;
mind_bool[969]:=CrpalkeGrfsGal.SetTwinModeAlt; | mind[969]:=UrnikSave.Dan[1].On[1].Ura; |  |  |  |  | 969:CrpalkeGrfsGal.SetTwinModeAlt:=Bit_0; | 969:UrnikSave.Dan[1].On[1].Ura:=Byte_0;
mind_bool[970]:=CrpalkeGrfsGal.SetTwinModeSpare; | mind[970]:=UrnikSave.Dan[1].On[2].Mna; |  |  |  |  | 970:CrpalkeGrfsGal.SetTwinModeSpare:=Bit_0; | 970:UrnikSave.Dan[1].On[2].Mna:=Byte_0;
mind_bool[971]:=CrpalkeGrfsGal.SetTwinModeSync; | mind[971]:=UrnikSave.Dan[1].On[2].Ura; |  |  |  |  | 971:CrpalkeGrfsGal.SetTwinModeSync:=Bit_0; | 971:UrnikSave.Dan[1].On[2].Ura:=Byte_0;
mind_bool[972]:=CrpalkeGrfsGal.Start; | mind[972]:=UrnikSave.Dan[1].On[3].Mna; |  |  |  |  | 972:CrpalkeGrfsGal.Start:=Bit_0; | 972:UrnikSave.Dan[1].On[3].Mna:=Byte_0;
mind_bool[973]:=CrpalkeGrfsGal.Stop; | mind[973]:=UrnikSave.Dan[1].On[3].Ura; |  |  |  |  | 973:CrpalkeGrfsGal.Stop:=Bit_0; | 973:UrnikSave.Dan[1].On[3].Ura:=Byte_0;
mind_bool[974]:=DI_rezerva10_2; | mind[974]:=UrnikSave.Dan[2].Off[1].Mna; |  |  |  |  | 974:DI_rezerva10_2:=Bit_0; | 974:UrnikSave.Dan[2].Off[1].Mna:=Byte_0;
mind_bool[975]:=DI_rezerva10_7; | mind[975]:=UrnikSave.Dan[2].Off[1].Ura; |  |  |  |  | 975:DI_rezerva10_7:=Bit_0; | 975:UrnikSave.Dan[2].Off[1].Ura:=Byte_0;
mind_bool[976]:=DI_rezerva11_4; | mind[976]:=UrnikSave.Dan[2].Off[2].Mna; |  |  |  |  | 976:DI_rezerva11_4:=Bit_0; | 976:UrnikSave.Dan[2].Off[2].Mna:=Byte_0;
mind_bool[977]:=DI_rezerva14_0; | mind[977]:=UrnikSave.Dan[2].Off[2].Ura; |  |  |  |  | 977:DI_rezerva14_0:=Bit_0; | 977:UrnikSave.Dan[2].Off[2].Ura:=Byte_0;
mind_bool[978]:=DI_rezerva14_2; | mind[978]:=UrnikSave.Dan[2].Off[3].Mna; |  |  |  |  | 978:DI_rezerva14_2:=Bit_0; | 978:UrnikSave.Dan[2].Off[3].Mna:=Byte_0;
mind_bool[979]:=DI_rezerva14_3; | mind[979]:=UrnikSave.Dan[2].Off[3].Ura; |  |  |  |  | 979:DI_rezerva14_3:=Bit_0; | 979:UrnikSave.Dan[2].Off[3].Ura:=Byte_0;
mind_bool[980]:=DI_rezerva14_4; | mind[980]:=UrnikSave.Dan[2].On[1].Mna; |  |  |  |  | 980:DI_rezerva14_4:=Bit_0; | 980:UrnikSave.Dan[2].On[1].Mna:=Byte_0;
mind_bool[981]:=DI_rezerva14_5; | mind[981]:=UrnikSave.Dan[2].On[1].Ura; |  |  |  |  | 981:DI_rezerva14_5:=Bit_0; | 981:UrnikSave.Dan[2].On[1].Ura:=Byte_0;
mind_bool[982]:=DI_rezerva14_7; | mind[982]:=UrnikSave.Dan[2].On[2].Mna; |  |  |  |  | 982:DI_rezerva14_7:=Bit_0; | 982:UrnikSave.Dan[2].On[2].Mna:=Byte_0;
mind_bool[983]:=DI_rezerva2_4; | mind[983]:=UrnikSave.Dan[2].On[2].Ura; |  |  |  |  | 983:DI_rezerva2_4:=Bit_0; | 983:UrnikSave.Dan[2].On[2].Ura:=Byte_0;
mind_bool[984]:=DI_rezerva3_5; | mind[984]:=UrnikSave.Dan[2].On[3].Mna; |  |  |  |  | 984:DI_rezerva3_5:=Bit_0; | 984:UrnikSave.Dan[2].On[3].Mna:=Byte_0;
mind_bool[985]:=DIN_AkumTopVodeAUTO; | mind[985]:=UrnikSave.Dan[2].On[3].Ura; |  |  |  |  | 985:DIN_AkumTopVodeAUTO:=Bit_0; | 985:UrnikSave.Dan[2].On[3].Ura:=Byte_0;
mind_bool[986]:=DIN_CrpHM1AUTO; | mind[986]:=UrnikSave.Dan[3].Off[1].Mna; |  |  |  |  | 986:DIN_CrpHM1AUTO:=Bit_0; | 986:UrnikSave.Dan[3].Off[1].Mna:=Byte_0;
mind_bool[987]:=DIN_CrpHM1kontON; | mind[987]:=UrnikSave.Dan[3].Off[1].Ura; |  |  |  |  | 987:DIN_CrpHM1kontON:=Bit_0; | 987:UrnikSave.Dan[3].Off[1].Ura:=Byte_0;
mind_bool[988]:=DIN_CrpHM2AUTO; | mind[988]:=UrnikSave.Dan[3].Off[2].Mna; |  |  |  |  | 988:DIN_CrpHM2AUTO:=Bit_0; | 988:UrnikSave.Dan[3].Off[2].Mna:=Byte_0;
mind_bool[989]:=DIN_CrpHM2kontON; | mind[989]:=UrnikSave.Dan[3].Off[2].Ura; |  |  |  |  | 989:DIN_CrpHM2kontON:=Bit_0; | 989:UrnikSave.Dan[3].Off[2].Ura:=Byte_0;
mind_bool[990]:=DIN_CrpHM3AUTO; | mind[990]:=UrnikSave.Dan[3].Off[3].Mna; |  |  |  |  | 990:DIN_CrpHM3AUTO:=Bit_0; | 990:UrnikSave.Dan[3].Off[3].Mna:=Byte_0;
mind_bool[991]:=DIN_CrpHM3kontON; | mind[991]:=UrnikSave.Dan[3].Off[3].Ura; |  |  |  |  | 991:DIN_CrpHM3kontON:=Bit_0; | 991:UrnikSave.Dan[3].Off[3].Ura:=Byte_0;
mind_bool[992]:=DIN_CrpHM4AUTO; | mind[992]:=UrnikSave.Dan[3].On[1].Mna; |  |  |  |  | 992:DIN_CrpHM4AUTO:=Bit_0; | 992:UrnikSave.Dan[3].On[1].Mna:=Byte_0;
mind_bool[993]:=DIN_CrpHM4kontON; | mind[993]:=UrnikSave.Dan[3].On[1].Ura; |  |  |  |  | 993:DIN_CrpHM4kontON:=Bit_0; | 993:UrnikSave.Dan[3].On[1].Ura:=Byte_0;
mind_bool[994]:=DIN_CrpHM5AUTO; | mind[994]:=UrnikSave.Dan[3].On[2].Mna; |  |  |  |  | 994:DIN_CrpHM5AUTO:=Bit_0; | 994:UrnikSave.Dan[3].On[2].Mna:=Byte_0;
mind_bool[995]:=DIN_CrpHM6AUTO; | mind[995]:=UrnikSave.Dan[3].On[2].Ura; |  |  |  |  | 995:DIN_CrpHM6AUTO:=Bit_0; | 995:UrnikSave.Dan[3].On[2].Ura:=Byte_0;
mind_bool[996]:=DIN_CrpHM7AUTO; | mind[996]:=UrnikSave.Dan[3].On[3].Mna; |  |  |  |  | 996:DIN_CrpHM7AUTO:=Bit_0; | 996:UrnikSave.Dan[3].On[3].Mna:=Byte_0;
mind_bool[997]:=DIN_CrpHM8AUTO; | mind[997]:=UrnikSave.Dan[3].On[3].Ura; |  |  |  |  | 997:DIN_CrpHM8AUTO:=Bit_0; | 997:UrnikSave.Dan[3].On[3].Ura:=Byte_0;
mind_bool[998]:=DIN_CrpMN1AUTO; | mind[998]:=UrnikSave.Dan[4].Off[1].Mna; |  |  |  |  | 998:DIN_CrpMN1AUTO:=Bit_0; | 998:UrnikSave.Dan[4].Off[1].Mna:=Byte_0;
mind_bool[999]:=DIN_CrpMN1kontON; | mind[999]:=UrnikSave.Dan[4].Off[1].Ura; |  |  |  |  | 999:DIN_CrpMN1kontON:=Bit_0; | 999:UrnikSave.Dan[4].Off[1].Ura:=Byte_0;
mind_bool[1000]:=DIN_CrpTM10AUTO; | mind[1000]:=UrnikSave.Dan[4].Off[2].Mna; |  |  |  |  | 1000:DIN_CrpTM10AUTO:=Bit_0; | 1000:UrnikSave.Dan[4].Off[2].Mna:=Byte_0;
mind_bool[1001]:=DIN_CrpTM11TM12AUTO; | mind[1001]:=UrnikSave.Dan[4].Off[2].Ura; |  |  |  |  | 1001:DIN_CrpTM11TM12AUTO:=Bit_0; | 1001:UrnikSave.Dan[4].Off[2].Ura:=Byte_0;
mind_bool[1002]:=DIN_CrpTM11TM12kontON; | mind[1002]:=UrnikSave.Dan[4].Off[3].Mna; |  |  |  |  | 1002:DIN_CrpTM11TM12kontON:=Bit_0; | 1002:UrnikSave.Dan[4].Off[3].Mna:=Byte_0;
mind_bool[1003]:=DIN_CrpTM1AUTO; | mind[1003]:=UrnikSave.Dan[4].Off[3].Ura; |  |  |  |  | 1003:DIN_CrpTM1AUTO:=Bit_0; | 1003:UrnikSave.Dan[4].Off[3].Ura:=Byte_0;
mind_bool[1004]:=DIN_CrpTM2AUTO; | mind[1004]:=UrnikSave.Dan[4].On[1].Mna; |  |  |  |  | 1004:DIN_CrpTM2AUTO:=Bit_0; | 1004:UrnikSave.Dan[4].On[1].Mna:=Byte_0;
mind_bool[1005]:=DIN_CrpTM3AUTO; | mind[1005]:=UrnikSave.Dan[4].On[1].Ura; |  |  |  |  | 1005:DIN_CrpTM3AUTO:=Bit_0; | 1005:UrnikSave.Dan[4].On[1].Ura:=Byte_0;
mind_bool[1006]:=DIN_CrpTM4AUTO; | mind[1006]:=UrnikSave.Dan[4].On[2].Mna; |  |  |  |  | 1006:DIN_CrpTM4AUTO:=Bit_0; | 1006:UrnikSave.Dan[4].On[2].Mna:=Byte_0;
mind_bool[1007]:=DIN_CrpTM5AUTO; | mind[1007]:=UrnikSave.Dan[4].On[2].Ura; |  |  |  |  | 1007:DIN_CrpTM5AUTO:=Bit_0; | 1007:UrnikSave.Dan[4].On[2].Ura:=Byte_0;
mind_bool[1008]:=DIN_CrpTM6AUTO; | mind[1008]:=UrnikSave.Dan[4].On[3].Mna; |  |  |  |  | 1008:DIN_CrpTM6AUTO:=Bit_0; | 1008:UrnikSave.Dan[4].On[3].Mna:=Byte_0;
mind_bool[1009]:=DIN_CrpTM7AUTO; | mind[1009]:=UrnikSave.Dan[4].On[3].Ura; |  |  |  |  | 1009:DIN_CrpTM7AUTO:=Bit_0; | 1009:UrnikSave.Dan[4].On[3].Ura:=Byte_0;
mind_bool[1010]:=DIN_CrpTM8AUTO; | mind[1010]:=UrnikSave.Dan[5].Off[1].Mna; |  |  |  |  | 1010:DIN_CrpTM8AUTO:=Bit_0; | 1010:UrnikSave.Dan[5].Off[1].Mna:=Byte_0;
mind_bool[1011]:=DIN_CrpTM9AUTO; | mind[1011]:=UrnikSave.Dan[5].Off[1].Ura; |  |  |  |  | 1011:DIN_CrpTM9AUTO:=Bit_0; | 1011:UrnikSave.Dan[5].Off[1].Ura:=Byte_0;
mind_bool[1012]:=DIN_GlStikaloDieselON; | mind[1012]:=UrnikSave.Dan[5].Off[2].Mna; |  |  |  |  | 1012:DIN_GlStikaloDieselON:=Bit_0; | 1012:UrnikSave.Dan[5].Off[2].Mna:=Byte_0;
mind_bool[1013]:=DIN_GlStikaloMrezaON; | mind[1013]:=UrnikSave.Dan[5].Off[2].Ura; |  |  |  |  | 1013:DIN_GlStikaloMrezaON:=Bit_0; | 1013:UrnikSave.Dan[5].Off[2].Ura:=Byte_0;
mind_bool[1014]:=DIN_GlStikaloUpsON; | mind[1014]:=UrnikSave.Dan[5].Off[3].Mna; |  |  |  |  | 1014:DIN_GlStikaloUpsON:=Bit_0; | 1014:UrnikSave.Dan[5].Off[3].Mna:=Byte_0;
mind_bool[1015]:=DIN_HladStAUTO; | mind[1015]:=UrnikSave.Dan[5].Off[3].Ura; |  |  |  |  | 1015:DIN_HladStAUTO:=Bit_0; | 1015:UrnikSave.Dan[5].Off[3].Ura:=Byte_0;
mind_bool[1016]:=DIN_Kond1AUTO; | mind[1016]:=UrnikSave.Dan[5].On[1].Mna; |  |  |  |  | 1016:DIN_Kond1AUTO:=Bit_0; | 1016:UrnikSave.Dan[5].On[1].Mna:=Byte_0;
mind_bool[1017]:=DIN_Kond2AUTO; | mind[1017]:=UrnikSave.Dan[5].On[1].Ura; |  |  |  |  | 1017:DIN_Kond2AUTO:=Bit_0; | 1017:UrnikSave.Dan[5].On[1].Ura:=Byte_0;
mind_bool[1018]:=DIN_Kond3AUTO; | mind[1018]:=UrnikSave.Dan[5].On[2].Mna; |  |  |  |  | 1018:DIN_Kond3AUTO:=Bit_0; | 1018:UrnikSave.Dan[5].On[2].Mna:=Byte_0;
mind_bool[1019]:=DIN_Vent1Auto; | mind[1019]:=UrnikSave.Dan[5].On[2].Ura; |  |  |  |  | 1019:DIN_Vent1Auto:=Bit_0; | 1019:UrnikSave.Dan[5].On[2].Ura:=Byte_0;
mind_bool[1020]:=DIN_Vent1kontON; | mind[1020]:=UrnikSave.Dan[5].On[3].Mna; |  |  |  |  | 1020:DIN_Vent1kontON:=Bit_0; | 1020:UrnikSave.Dan[5].On[3].Mna:=Byte_0;
mind_bool[1021]:=DIN_Vent2Auto; | mind[1021]:=UrnikSave.Dan[5].On[3].Ura; |  |  |  |  | 1021:DIN_Vent2Auto:=Bit_0; | 1021:UrnikSave.Dan[5].On[3].Ura:=Byte_0;
mind_bool[1022]:=DIN_Vent2kontON; | mind[1022]:=UrnikSave.Dan[6].Off[1].Mna; |  |  |  |  | 1022:DIN_Vent2kontON:=Bit_0; | 1022:UrnikSave.Dan[6].Off[1].Mna:=Byte_0;
mind_bool[1023]:=DIN_Vent3Auto; | mind[1023]:=UrnikSave.Dan[6].Off[1].Ura; |  |  |  |  | 1023:DIN_Vent3Auto:=Bit_0; | 1023:UrnikSave.Dan[6].Off[1].Ura:=Byte_0;
mind_bool[1024]:=DIN_Vent3kontON; | mind[1024]:=UrnikSave.Dan[6].Off[2].Mna; |  |  |  |  | 1024:DIN_Vent3kontON:=Bit_0; | 1024:UrnikSave.Dan[6].Off[2].Mna:=Byte_0;
mind_bool[1025]:=DIN_Vent4Auto; | mind[1025]:=UrnikSave.Dan[6].Off[2].Ura; |  |  |  |  | 1025:DIN_Vent4Auto:=Bit_0; | 1025:UrnikSave.Dan[6].Off[2].Ura:=Byte_0;
mind_bool[1026]:=DIN_Vent4kontON; | mind[1026]:=UrnikSave.Dan[6].Off[3].Mna; |  |  |  |  | 1026:DIN_Vent4kontON:=Bit_0; | 1026:UrnikSave.Dan[6].Off[3].Mna:=Byte_0;
mind_bool[1027]:=DIN_Vent5Auto; | mind[1027]:=UrnikSave.Dan[6].Off[3].Ura; |  |  |  |  | 1027:DIN_Vent5Auto:=Bit_0; | 1027:UrnikSave.Dan[6].Off[3].Ura:=Byte_0;
mind_bool[1028]:=DIN_Vent5kontON; | mind[1028]:=UrnikSave.Dan[6].On[1].Mna; |  |  |  |  | 1028:DIN_Vent5kontON:=Bit_0; | 1028:UrnikSave.Dan[6].On[1].Mna:=Byte_0;
mind_bool[1029]:=DIN_Vent6Auto; | mind[1029]:=UrnikSave.Dan[6].On[1].Ura; |  |  |  |  | 1029:DIN_Vent6Auto:=Bit_0; | 1029:UrnikSave.Dan[6].On[1].Ura:=Byte_0;
mind_bool[1030]:=DIN_Vent6kontON; | mind[1030]:=UrnikSave.Dan[6].On[2].Mna; |  |  |  |  | 1030:DIN_Vent6kontON:=Bit_0; | 1030:UrnikSave.Dan[6].On[2].Mna:=Byte_0;
mind_bool[1031]:=DO_rezerva0_2; | mind[1031]:=UrnikSave.Dan[6].On[2].Ura; |  |  |  |  | 1031:DO_rezerva0_2:=Bit_0; | 1031:UrnikSave.Dan[6].On[2].Ura:=Byte_0;
mind_bool[1032]:=DO_rezerva0_3; | mind[1032]:=UrnikSave.Dan[6].On[3].Mna; |  |  |  |  | 1032:DO_rezerva0_3:=Bit_0; | 1032:UrnikSave.Dan[6].On[3].Mna:=Byte_0;
mind_bool[1033]:=DO_rezerva0_4; | mind[1033]:=UrnikSave.Dan[6].On[3].Ura; |  |  |  |  | 1033:DO_rezerva0_4:=Bit_0; | 1033:UrnikSave.Dan[6].On[3].Ura:=Byte_0;
mind_bool[1034]:=DO_rezerva0_5; | mind[1034]:=UrnikSave.Dan[7].Off[1].Mna; |  |  |  |  | 1034:DO_rezerva0_5:=Bit_0; | 1034:UrnikSave.Dan[7].Off[1].Mna:=Byte_0;
mind_bool[1035]:=DO_rezerva1_3; | mind[1035]:=UrnikSave.Dan[7].Off[1].Ura; |  |  |  |  | 1035:DO_rezerva1_3:=Bit_0; | 1035:UrnikSave.Dan[7].Off[1].Ura:=Byte_0;
mind_bool[1036]:=DO_rezerva1_4; | mind[1036]:=UrnikSave.Dan[7].Off[2].Mna; |  |  |  |  | 1036:DO_rezerva1_4:=Bit_0; | 1036:UrnikSave.Dan[7].Off[2].Mna:=Byte_0;
mind_bool[1037]:=DO_rezerva1_5; | mind[1037]:=UrnikSave.Dan[7].Off[2].Ura; |  |  |  |  | 1037:DO_rezerva1_5:=Bit_0; | 1037:UrnikSave.Dan[7].Off[2].Ura:=Byte_0;
mind_bool[1038]:=DO_rezerva3_4; | mind[1038]:=UrnikSave.Dan[7].Off[3].Mna; |  |  |  |  | 1038:DO_rezerva3_4:=Bit_0; | 1038:UrnikSave.Dan[7].Off[3].Mna:=Byte_0;
mind_bool[1039]:=DO_rezerva3_6; | mind[1039]:=UrnikSave.Dan[7].Off[3].Ura; |  |  |  |  | 1039:DO_rezerva3_6:=Bit_0; | 1039:UrnikSave.Dan[7].Off[3].Ura:=Byte_0;
mind_bool[1040]:=DO_rezerva4_0; | mind[1040]:=UrnikSave.Dan[7].On[1].Mna; |  |  |  |  | 1040:DO_rezerva4_0:=Bit_0; | 1040:UrnikSave.Dan[7].On[1].Mna:=Byte_0;
mind_bool[1041]:=PrenosUrnika[26]; | mind[1041]:=UrnikSave.Dan[7].On[1].Ura; |  |  |  |  | 1041:PrenosUrnika[26]:=Bit_0; | 1041:UrnikSave.Dan[7].On[1].Ura:=Byte_0;
mind_bool[1042]:=PrenosUrnika[27]; | mind[1042]:=UrnikSave.Dan[7].On[2].Mna; |  |  |  |  | 1042:PrenosUrnika[27]:=Bit_0; | 1042:UrnikSave.Dan[7].On[2].Mna:=Byte_0;
mind_bool[1043]:=PrenosUrnika[28]; | mind[1043]:=UrnikSave.Dan[7].On[2].Ura; |  |  |  |  | 1043:PrenosUrnika[28]:=Bit_0; | 1043:UrnikSave.Dan[7].On[2].Ura:=Byte_0;
mind_bool[1044]:=PrenosUrnika[29]; | mind[1044]:=UrnikSave.Dan[7].On[3].Mna; |  |  |  |  | 1044:PrenosUrnika[29]:=Bit_0; | 1044:UrnikSave.Dan[7].On[3].Mna:=Byte_0;
mind_bool[1045]:=PrenosUrnika[30]; | mind[1045]:=UrnikSave.Dan[7].On[3].Ura; |  |  |  |  | 1045:PrenosUrnika[30]:=Bit_0; | 1045:UrnikSave.Dan[7].On[3].Ura:=Byte_0;
mind_bool[1046]:=PrenosUrnika[31]; | mind[1046]:=XVH_CircNumber; |  |  |  |  | 1046:PrenosUrnika[31]:=Bit_0; | 1046:XVH_CircNumber:=Byte_0;
mind_bool[1047]:=PrenosUrnika[32]; | mind[1047]:=XVH_KompStatus[1]; |  |  |  |  | 1047:PrenosUrnika[32]:=Bit_0; | 1047:XVH_KompStatus[1]:=Byte_0;
mind_bool[1048]:=PrenosUrnika[33]; | mind[1048]:=XVH_KompStatus[2]; |  |  |  |  | 1048:PrenosUrnika[33]:=Bit_0; | 1048:XVH_KompStatus[2]:=Byte_0;
mind_bool[1049]:=PrenosUrnika[34]; | mind[1049]:=XVH_ReferencaUpper; |  |  |  |  | 1049:PrenosUrnika[34]:=Bit_0; | 1049:XVH_ReferencaUpper:=Word_01;
mind_bool[1050]:=PrenosUrnika[35]; | mind[1050]:=XVH_UPSstatus; |  |  |  |  | 1050:PrenosUrnika[35]:=Bit_0; | 1050:XVH_UPSstatus:=Byte_0;
mind_bool[1051]:=PrenosUrnika[36]; | mind[1051]:=XVH_Urnik.Dan[1].Off[1].Mna; |  |  |  |  | 1051:PrenosUrnika[36]:=Bit_0; | 1051:XVH_Urnik.Dan[1].Off[1].Mna:=Byte_0;
mind_bool[1052]:=PrenosUrnika[37]; | mind[1052]:=XVH_Urnik.Dan[1].Off[1].Ura; |  |  |  |  | 1052:PrenosUrnika[37]:=Bit_0; | 1052:XVH_Urnik.Dan[1].Off[1].Ura:=Byte_0;
mind_bool[1053]:=PrenosUrnika[38]; | mind[1053]:=XVH_Urnik.Dan[1].Off[2].Mna; |  |  |  |  | 1053:PrenosUrnika[38]:=Bit_0; | 1053:XVH_Urnik.Dan[1].Off[2].Mna:=Byte_0;
mind_bool[1054]:=PrenosUrnika[39]; | mind[1054]:=XVH_Urnik.Dan[1].Off[2].Ura; |  |  |  |  | 1054:PrenosUrnika[39]:=Bit_0; | 1054:XVH_Urnik.Dan[1].Off[2].Ura:=Byte_0;
mind_bool[1055]:=PrenosUrnika[40]; | mind[1055]:=XVH_Urnik.Dan[1].Off[3].Mna; |  |  |  |  | 1055:PrenosUrnika[40]:=Bit_0; | 1055:XVH_Urnik.Dan[1].Off[3].Mna:=Byte_0;
mind_bool[1056]:=PrenosUrnika[41]; | mind[1056]:=XVH_Urnik.Dan[1].Off[3].Ura; |  |  |  |  | 1056:PrenosUrnika[41]:=Bit_0; | 1056:XVH_Urnik.Dan[1].Off[3].Ura:=Byte_0;
mind_bool[1057]:=PrenosUrnika[42]; | mind[1057]:=XVH_Urnik.Dan[1].On[1].Mna; |  |  |  |  | 1057:PrenosUrnika[42]:=Bit_0; | 1057:XVH_Urnik.Dan[1].On[1].Mna:=Byte_0;
mind_bool[1058]:=PrenosUrnika[43]; | mind[1058]:=XVH_Urnik.Dan[1].On[1].Ura; |  |  |  |  | 1058:PrenosUrnika[43]:=Bit_0; | 1058:XVH_Urnik.Dan[1].On[1].Ura:=Byte_0;
mind_bool[1059]:=PrenosUrnika[44]; | mind[1059]:=XVH_Urnik.Dan[1].On[2].Mna; |  |  |  |  | 1059:PrenosUrnika[44]:=Bit_0; | 1059:XVH_Urnik.Dan[1].On[2].Mna:=Byte_0;
mind_bool[1060]:=PrenosUrnika[45]; | mind[1060]:=XVH_Urnik.Dan[1].On[2].Ura; |  |  |  |  | 1060:PrenosUrnika[45]:=Bit_0; | 1060:XVH_Urnik.Dan[1].On[2].Ura:=Byte_0;
mind_bool[1061]:=PrenosUrnika[46]; | mind[1061]:=XVH_Urnik.Dan[1].On[3].Mna; |  |  |  |  | 1061:PrenosUrnika[46]:=Bit_0; | 1061:XVH_Urnik.Dan[1].On[3].Mna:=Byte_0;
mind_bool[1062]:=PrenosUrnika[47]; | mind[1062]:=XVH_Urnik.Dan[1].On[3].Ura; |  |  |  |  | 1062:PrenosUrnika[47]:=Bit_0; | 1062:XVH_Urnik.Dan[1].On[3].Ura:=Byte_0;
mind_bool[1063]:=PrenosUrnika[48]; | mind[1063]:=XVH_Urnik.Dan[2].Off[1].Mna; |  |  |  |  | 1063:PrenosUrnika[48]:=Bit_0; | 1063:XVH_Urnik.Dan[2].Off[1].Mna:=Byte_0;
mind_bool[1064]:=PrenosUrnika[49]; | mind[1064]:=XVH_Urnik.Dan[2].Off[1].Ura; |  |  |  |  | 1064:PrenosUrnika[49]:=Bit_0; | 1064:XVH_Urnik.Dan[2].Off[1].Ura:=Byte_0;
mind_bool[1065]:=PrenosUrnika[50]; | mind[1065]:=XVH_Urnik.Dan[2].Off[2].Mna; |  |  |  |  | 1065:PrenosUrnika[50]:=Bit_0; | 1065:XVH_Urnik.Dan[2].Off[2].Mna:=Byte_0;
mind_bool[1066]:=PrenosUrnika[51]; | mind[1066]:=XVH_Urnik.Dan[2].Off[2].Ura; |  |  |  |  | 1066:PrenosUrnika[51]:=Bit_0; | 1066:XVH_Urnik.Dan[2].Off[2].Ura:=Byte_0;
mind_bool[1067]:=PrenosUrnika[52]; | mind[1067]:=XVH_Urnik.Dan[2].Off[3].Mna; |  |  |  |  | 1067:PrenosUrnika[52]:=Bit_0; | 1067:XVH_Urnik.Dan[2].Off[3].Mna:=Byte_0;
mind_bool[1068]:=PrenosUrnika[53]; | mind[1068]:=XVH_Urnik.Dan[2].Off[3].Ura; |  |  |  |  | 1068:PrenosUrnika[53]:=Bit_0; | 1068:XVH_Urnik.Dan[2].Off[3].Ura:=Byte_0;
mind_bool[1069]:=PrenosUrnika[54]; | mind[1069]:=XVH_Urnik.Dan[2].On[1].Mna; |  |  |  |  | 1069:PrenosUrnika[54]:=Bit_0; | 1069:XVH_Urnik.Dan[2].On[1].Mna:=Byte_0;
mind_bool[1070]:=PrenosUrnika[55]; | mind[1070]:=XVH_Urnik.Dan[2].On[1].Ura; |  |  |  |  | 1070:PrenosUrnika[55]:=Bit_0; | 1070:XVH_Urnik.Dan[2].On[1].Ura:=Byte_0;
mind_bool[1071]:=PrenosUrnika[56]; | mind[1071]:=XVH_Urnik.Dan[2].On[2].Mna; |  |  |  |  | 1071:PrenosUrnika[56]:=Bit_0; | 1071:XVH_Urnik.Dan[2].On[2].Mna:=Byte_0;
mind_bool[1072]:=PrenosUrnika[57]; | mind[1072]:=XVH_Urnik.Dan[2].On[2].Ura; |  |  |  |  | 1072:PrenosUrnika[57]:=Bit_0; | 1072:XVH_Urnik.Dan[2].On[2].Ura:=Byte_0;
mind_bool[1073]:=PrenosUrnika[58]; | mind[1073]:=XVH_Urnik.Dan[2].On[3].Mna; |  |  |  |  | 1073:PrenosUrnika[58]:=Bit_0; | 1073:XVH_Urnik.Dan[2].On[3].Mna:=Byte_0;
mind_bool[1074]:=PrenosUrnika[59]; | mind[1074]:=XVH_Urnik.Dan[2].On[3].Ura; |  |  |  |  | 1074:PrenosUrnika[59]:=Bit_0; | 1074:XVH_Urnik.Dan[2].On[3].Ura:=Byte_0;
mind_bool[1075]:=PrenosUrnika[60]; | mind[1075]:=XVH_Urnik.Dan[3].Off[1].Mna; |  |  |  |  | 1075:PrenosUrnika[60]:=Bit_0; | 1075:XVH_Urnik.Dan[3].Off[1].Mna:=Byte_0;
mind_bool[1076]:=PrenosUrnika[61]; | mind[1076]:=XVH_Urnik.Dan[3].Off[1].Ura; |  |  |  |  | 1076:PrenosUrnika[61]:=Bit_0; | 1076:XVH_Urnik.Dan[3].Off[1].Ura:=Byte_0;
mind_bool[1077]:=PrenosUrnika[62]; | mind[1077]:=XVH_Urnik.Dan[3].Off[2].Mna; |  |  |  |  | 1077:PrenosUrnika[62]:=Bit_0; | 1077:XVH_Urnik.Dan[3].Off[2].Mna:=Byte_0;
mind_bool[1078]:=PrenosUrnika[63]; | mind[1078]:=XVH_Urnik.Dan[3].Off[2].Ura; |  |  |  |  | 1078:PrenosUrnika[63]:=Bit_0; | 1078:XVH_Urnik.Dan[3].Off[2].Ura:=Byte_0;
mind_bool[1079]:=PrenosUrnika[64]; | mind[1079]:=XVH_Urnik.Dan[3].Off[3].Mna; |  |  |  |  | 1079:PrenosUrnika[64]:=Bit_0; | 1079:XVH_Urnik.Dan[3].Off[3].Mna:=Byte_0;
mind_bool[1080]:=PrenosUrnika[65]; | mind[1080]:=XVH_Urnik.Dan[3].Off[3].Ura; |  |  |  |  | 1080:PrenosUrnika[65]:=Bit_0; | 1080:XVH_Urnik.Dan[3].Off[3].Ura:=Byte_0;
mind_bool[1081]:=PrenosUrnika[66]; | mind[1081]:=XVH_Urnik.Dan[3].On[1].Mna; |  |  |  |  | 1081:PrenosUrnika[66]:=Bit_0; | 1081:XVH_Urnik.Dan[3].On[1].Mna:=Byte_0;
mind_bool[1082]:=PrenosUrnika[67]; | mind[1082]:=XVH_Urnik.Dan[3].On[1].Ura; |  |  |  |  | 1082:PrenosUrnika[67]:=Bit_0; | 1082:XVH_Urnik.Dan[3].On[1].Ura:=Byte_0;
mind_bool[1083]:=PrenosUrnika[68]; | mind[1083]:=XVH_Urnik.Dan[3].On[2].Mna; |  |  |  |  | 1083:PrenosUrnika[68]:=Bit_0; | 1083:XVH_Urnik.Dan[3].On[2].Mna:=Byte_0;
mind_bool[1084]:=PrenosUrnika[69]; | mind[1084]:=XVH_Urnik.Dan[3].On[2].Ura; |  |  |  |  | 1084:PrenosUrnika[69]:=Bit_0; | 1084:XVH_Urnik.Dan[3].On[2].Ura:=Byte_0;
mind_bool[1085]:=PrenosUrnika[70]; | mind[1085]:=XVH_Urnik.Dan[3].On[3].Mna; |  |  |  |  | 1085:PrenosUrnika[70]:=Bit_0; | 1085:XVH_Urnik.Dan[3].On[3].Mna:=Byte_0;
mind_bool[1086]:=PrenosUrnika[71]; | mind[1086]:=XVH_Urnik.Dan[3].On[3].Ura; |  |  |  |  | 1086:PrenosUrnika[71]:=Bit_0; | 1086:XVH_Urnik.Dan[3].On[3].Ura:=Byte_0;
mind_bool[1087]:=PrenosUrnika[72]; | mind[1087]:=XVH_Urnik.Dan[4].Off[1].Mna; |  |  |  |  | 1087:PrenosUrnika[72]:=Bit_0; | 1087:XVH_Urnik.Dan[4].Off[1].Mna:=Byte_0;
mind_bool[1088]:=PrenosUrnika[73]; | mind[1088]:=XVH_Urnik.Dan[4].Off[1].Ura; |  |  |  |  | 1088:PrenosUrnika[73]:=Bit_0; | 1088:XVH_Urnik.Dan[4].Off[1].Ura:=Byte_0;
mind_bool[1089]:=PrenosUrnika[74]; | mind[1089]:=XVH_Urnik.Dan[4].Off[2].Mna; |  |  |  |  | 1089:PrenosUrnika[74]:=Bit_0; | 1089:XVH_Urnik.Dan[4].Off[2].Mna:=Byte_0;
mind_bool[1090]:=PrenosUrnika[75]; | mind[1090]:=XVH_Urnik.Dan[4].Off[2].Ura; |  |  |  |  | 1090:PrenosUrnika[75]:=Bit_0; | 1090:XVH_Urnik.Dan[4].Off[2].Ura:=Byte_0;
mind_bool[1091]:=PrenosUrnika[76]; | mind[1091]:=XVH_Urnik.Dan[4].Off[3].Mna; |  |  |  |  | 1091:PrenosUrnika[76]:=Bit_0; | 1091:XVH_Urnik.Dan[4].Off[3].Mna:=Byte_0;
mind_bool[1092]:=PrenosUrnika[77]; | mind[1092]:=XVH_Urnik.Dan[4].Off[3].Ura; |  |  |  |  | 1092:PrenosUrnika[77]:=Bit_0; | 1092:XVH_Urnik.Dan[4].Off[3].Ura:=Byte_0;
mind_bool[1093]:=PrenosUrnika[78]; | mind[1093]:=XVH_Urnik.Dan[4].On[1].Mna; |  |  |  |  | 1093:PrenosUrnika[78]:=Bit_0; | 1093:XVH_Urnik.Dan[4].On[1].Mna:=Byte_0;
mind_bool[1094]:=PrenosUrnika[79]; | mind[1094]:=XVH_Urnik.Dan[4].On[1].Ura; |  |  |  |  | 1094:PrenosUrnika[79]:=Bit_0; | 1094:XVH_Urnik.Dan[4].On[1].Ura:=Byte_0;
mind_bool[1095]:=PrenosUrnika[80]; | mind[1095]:=XVH_Urnik.Dan[4].On[2].Mna; |  |  |  |  | 1095:PrenosUrnika[80]:=Bit_0; | 1095:XVH_Urnik.Dan[4].On[2].Mna:=Byte_0;
mind_bool[1096]:=PrenosUrnika[81]; | mind[1096]:=XVH_Urnik.Dan[4].On[2].Ura; |  |  |  |  | 1096:PrenosUrnika[81]:=Bit_0; | 1096:XVH_Urnik.Dan[4].On[2].Ura:=Byte_0;
mind_bool[1097]:=PrenosUrnika[82]; | mind[1097]:=XVH_Urnik.Dan[4].On[3].Mna; |  |  |  |  | 1097:PrenosUrnika[82]:=Bit_0; | 1097:XVH_Urnik.Dan[4].On[3].Mna:=Byte_0;
mind_bool[1098]:=PrenosUrnika[83]; | mind[1098]:=XVH_Urnik.Dan[4].On[3].Ura; |  |  |  |  | 1098:PrenosUrnika[83]:=Bit_0; | 1098:XVH_Urnik.Dan[4].On[3].Ura:=Byte_0;
mind_bool[1099]:=PrenosUrnika[84]; | mind[1099]:=XVH_Urnik.Dan[5].Off[1].Mna; |  |  |  |  | 1099:PrenosUrnika[84]:=Bit_0; | 1099:XVH_Urnik.Dan[5].Off[1].Mna:=Byte_0;
mind_bool[1100]:=PrenosUrnika[85]; | mind[1100]:=XVH_Urnik.Dan[5].Off[1].Ura; |  |  |  |  | 1100:PrenosUrnika[85]:=Bit_0; | 1100:XVH_Urnik.Dan[5].Off[1].Ura:=Byte_0;
mind_bool[1101]:=PrenosUrnika[86]; | mind[1101]:=XVH_Urnik.Dan[5].Off[2].Mna; |  |  |  |  | 1101:PrenosUrnika[86]:=Bit_0; | 1101:XVH_Urnik.Dan[5].Off[2].Mna:=Byte_0;
mind_bool[1102]:=PrenosUrnika[87]; | mind[1102]:=XVH_Urnik.Dan[5].Off[2].Ura; |  |  |  |  | 1102:PrenosUrnika[87]:=Bit_0; | 1102:XVH_Urnik.Dan[5].Off[2].Ura:=Byte_0;
mind_bool[1103]:=PrenosUrnika[88]; | mind[1103]:=XVH_Urnik.Dan[5].Off[3].Mna; |  |  |  |  | 1103:PrenosUrnika[88]:=Bit_0; | 1103:XVH_Urnik.Dan[5].Off[3].Mna:=Byte_0;
mind_bool[1104]:=PrenosUrnika[89]; | mind[1104]:=XVH_Urnik.Dan[5].Off[3].Ura; |  |  |  |  | 1104:PrenosUrnika[89]:=Bit_0; | 1104:XVH_Urnik.Dan[5].Off[3].Ura:=Byte_0;
mind_bool[1105]:=PrenosUrnika[90]; | mind[1105]:=XVH_Urnik.Dan[5].On[1].Mna; |  |  |  |  | 1105:PrenosUrnika[90]:=Bit_0; | 1105:XVH_Urnik.Dan[5].On[1].Mna:=Byte_0;
mind_bool[1106]:=PrenosUrnika[91]; | mind[1106]:=XVH_Urnik.Dan[5].On[1].Ura; |  |  |  |  | 1106:PrenosUrnika[91]:=Bit_0; | 1106:XVH_Urnik.Dan[5].On[1].Ura:=Byte_0;
mind_bool[1107]:=PrenosUrnika[92]; | mind[1107]:=XVH_Urnik.Dan[5].On[2].Mna; |  |  |  |  | 1107:PrenosUrnika[92]:=Bit_0; | 1107:XVH_Urnik.Dan[5].On[2].Mna:=Byte_0;
mind_bool[1108]:=PrenosUrnika[93]; | mind[1108]:=XVH_Urnik.Dan[5].On[2].Ura; |  |  |  |  | 1108:PrenosUrnika[93]:=Bit_0; | 1108:XVH_Urnik.Dan[5].On[2].Ura:=Byte_0;
mind_bool[1109]:=PrenosUrnika[94]; | mind[1109]:=XVH_Urnik.Dan[5].On[3].Mna; |  |  |  |  | 1109:PrenosUrnika[94]:=Bit_0; | 1109:XVH_Urnik.Dan[5].On[3].Mna:=Byte_0;
mind_bool[1110]:=PrenosUrnika[95]; | mind[1110]:=XVH_Urnik.Dan[5].On[3].Ura; |  |  |  |  | 1110:PrenosUrnika[95]:=Bit_0; | 1110:XVH_Urnik.Dan[5].On[3].Ura:=Byte_0;
mind_bool[1111]:=PrenosUrnika[96]; | mind[1111]:=XVH_Urnik.Dan[6].Off[1].Mna; |  |  |  |  | 1111:PrenosUrnika[96]:=Bit_0; | 1111:XVH_Urnik.Dan[6].Off[1].Mna:=Byte_0;
mind_bool[1112]:=RazsvRocnoEnaLuc[10]; | mind[1112]:=XVH_Urnik.Dan[6].Off[1].Ura; |  |  |  |  | 1112:RazsvRocnoEnaLuc[10]:=Bit_0; | 1112:XVH_Urnik.Dan[6].Off[1].Ura:=Byte_0;
mind_bool[1113]:=RazsvRocnoEnaLuc[11]; | mind[1113]:=XVH_Urnik.Dan[6].Off[2].Mna; |  |  |  |  | 1113:RazsvRocnoEnaLuc[11]:=Bit_0; | 1113:XVH_Urnik.Dan[6].Off[2].Mna:=Byte_0;
mind_bool[1114]:=RazsvRocnoEnaLuc[12]; | mind[1114]:=XVH_Urnik.Dan[6].Off[2].Ura; |  |  |  |  | 1114:RazsvRocnoEnaLuc[12]:=Bit_0; | 1114:XVH_Urnik.Dan[6].Off[2].Ura:=Byte_0;
mind_bool[1115]:=RazsvRocnoEnaLuc[13]; | mind[1115]:=XVH_Urnik.Dan[6].Off[3].Mna; |  |  |  |  | 1115:RazsvRocnoEnaLuc[13]:=Bit_0; | 1115:XVH_Urnik.Dan[6].Off[3].Mna:=Byte_0;
mind_bool[1116]:=RazsvRocnoEnaLuc[14]; | mind[1116]:=XVH_Urnik.Dan[6].Off[3].Ura; |  |  |  |  | 1116:RazsvRocnoEnaLuc[14]:=Bit_0; | 1116:XVH_Urnik.Dan[6].Off[3].Ura:=Byte_0;
mind_bool[1117]:=RazsvRocnoEnaLuc[15]; | mind[1117]:=XVH_Urnik.Dan[6].On[1].Mna; |  |  |  |  | 1117:RazsvRocnoEnaLuc[15]:=Bit_0; | 1117:XVH_Urnik.Dan[6].On[1].Mna:=Byte_0;
mind_bool[1118]:=RazsvRocnoEnaLuc[16]; | mind[1118]:=XVH_Urnik.Dan[6].On[1].Ura; |  |  |  |  | 1118:RazsvRocnoEnaLuc[16]:=Bit_0; | 1118:XVH_Urnik.Dan[6].On[1].Ura:=Byte_0;
mind_bool[1119]:=RazsvRocnoEnaLuc[17]; | mind[1119]:=XVH_Urnik.Dan[6].On[2].Mna; |  |  |  |  | 1119:RazsvRocnoEnaLuc[17]:=Bit_0; | 1119:XVH_Urnik.Dan[6].On[2].Mna:=Byte_0;
mind_bool[1120]:=RazsvRocnoEnaLuc[18]; | mind[1120]:=XVH_Urnik.Dan[6].On[2].Ura; |  |  |  |  | 1120:RazsvRocnoEnaLuc[18]:=Bit_0; | 1120:XVH_Urnik.Dan[6].On[2].Ura:=Byte_0;
mind_bool[1121]:=RazsvRocnoEnaLuc[19]; | mind[1121]:=XVH_Urnik.Dan[6].On[3].Mna; |  |  |  |  | 1121:RazsvRocnoEnaLuc[19]:=Bit_0; | 1121:XVH_Urnik.Dan[6].On[3].Mna:=Byte_0;
mind_bool[1122]:=RazsvRocnoEnaLuc[1]; | mind[1122]:=XVH_Urnik.Dan[6].On[3].Ura; |  |  |  |  | 1122:RazsvRocnoEnaLuc[1]:=Bit_0; | 1122:XVH_Urnik.Dan[6].On[3].Ura:=Byte_0;
mind_bool[1123]:=RazsvRocnoEnaLuc[20]; | mind[1123]:=XVH_Urnik.Dan[7].Off[1].Mna; |  |  |  |  | 1123:RazsvRocnoEnaLuc[20]:=Bit_0; | 1123:XVH_Urnik.Dan[7].Off[1].Mna:=Byte_0;
mind_bool[1124]:=RazsvRocnoEnaLuc[21]; | mind[1124]:=XVH_Urnik.Dan[7].Off[1].Ura; |  |  |  |  | 1124:RazsvRocnoEnaLuc[21]:=Bit_0; | 1124:XVH_Urnik.Dan[7].Off[1].Ura:=Byte_0;
mind_bool[1125]:=RazsvRocnoEnaLuc[22]; | mind[1125]:=XVH_Urnik.Dan[7].Off[2].Mna; |  |  |  |  | 1125:RazsvRocnoEnaLuc[22]:=Bit_0; | 1125:XVH_Urnik.Dan[7].Off[2].Mna:=Byte_0;
mind_bool[1126]:=RazsvRocnoEnaLuc[23]; | mind[1126]:=XVH_Urnik.Dan[7].Off[2].Ura; |  |  |  |  | 1126:RazsvRocnoEnaLuc[23]:=Bit_0; | 1126:XVH_Urnik.Dan[7].Off[2].Ura:=Byte_0;
mind_bool[1127]:=RazsvRocnoEnaLuc[24]; | mind[1127]:=XVH_Urnik.Dan[7].Off[3].Mna; |  |  |  |  | 1127:RazsvRocnoEnaLuc[24]:=Bit_0; | 1127:XVH_Urnik.Dan[7].Off[3].Mna:=Byte_0;
mind_bool[1128]:=RazsvRocnoEnaLuc[25]; | mind[1128]:=XVH_Urnik.Dan[7].Off[3].Ura; |  |  |  |  | 1128:RazsvRocnoEnaLuc[25]:=Bit_0; | 1128:XVH_Urnik.Dan[7].Off[3].Ura:=Byte_0;
mind_bool[1129]:=RazsvRocnoEnaLuc[2]; | mind[1129]:=XVH_Urnik.Dan[7].On[1].Mna; |  |  |  |  | 1129:RazsvRocnoEnaLuc[2]:=Bit_0; | 1129:XVH_Urnik.Dan[7].On[1].Mna:=Byte_0;
mind_bool[1130]:=RazsvRocnoEnaLuc[3]; | mind[1130]:=XVH_Urnik.Dan[7].On[1].Ura; |  |  |  |  | 1130:RazsvRocnoEnaLuc[3]:=Bit_0; | 1130:XVH_Urnik.Dan[7].On[1].Ura:=Byte_0;
mind_bool[1131]:=RazsvRocnoEnaLuc[4]; | mind[1131]:=XVH_Urnik.Dan[7].On[2].Mna; |  |  |  |  | 1131:RazsvRocnoEnaLuc[4]:=Bit_0; | 1131:XVH_Urnik.Dan[7].On[2].Mna:=Byte_0;
mind_bool[1132]:=RazsvRocnoEnaLuc[5]; | mind[1132]:=XVH_Urnik.Dan[7].On[2].Ura; |  |  |  |  | 1132:RazsvRocnoEnaLuc[5]:=Bit_0; | 1132:XVH_Urnik.Dan[7].On[2].Ura:=Byte_0;
mind_bool[1133]:=RazsvRocnoEnaLuc[6]; | mind[1133]:=XVH_Urnik.Dan[7].On[3].Mna; |  |  |  |  | 1133:RazsvRocnoEnaLuc[6]:=Bit_0; | 1133:XVH_Urnik.Dan[7].On[3].Mna:=Byte_0;
mind_bool[1134]:=RazsvRocnoEnaLuc[7]; | mind[1134]:=XVH_Urnik.Dan[7].On[3].Ura; |  |  |  |  | 1134:RazsvRocnoEnaLuc[7]:=Bit_0; | 1134:XVH_Urnik.Dan[7].On[3].Ura:=Byte_0;
mind_bool[1135]:=RazsvRocnoEnaLuc[8]; | mind[1135]:=XVH_VentilTYValue[1,1]; |  |  |  |  | 1135:RazsvRocnoEnaLuc[8]:=Bit_0; | 1135:XVH_VentilTYValue[1,1]:=Byte_0;
mind_bool[1136]:=RazsvRocnoEnaLuc[9]; | mind[1136]:=XVH_VentilTYValue[1,2]; |  |  |  |  | 1136:RazsvRocnoEnaLuc[9]:=Bit_0; | 1136:XVH_VentilTYValue[1,2]:=Byte_0;
mind_bool[1137]:=XVH_CrpalkaGrfsPair; | mind[1137]:=XVH_VentilTYValue[2,1]; |  |  |  |  | 1137:XVH_CrpalkaGrfsPair:=Bit_0; | 1137:XVH_VentilTYValue[2,1]:=Byte_0;
mind_bool[1138]:=XVH_CrpGrfsCommErr; | mind[1138]:=XVH_VentilTYValue[2,2]; |  |  |  |  | 1138:XVH_CrpGrfsCommErr:=Bit_0; | 1138:XVH_VentilTYValue[2,2]:=Byte_0;
mind_bool[1139]:=XVH_CrpGrfsON[10]; | mind[1139]:=XVH_VentilTYValue[3,1]; |  |  |  |  | 1139:XVH_CrpGrfsON[10]:=Bit_0; | 1139:XVH_VentilTYValue[3,1]:=Byte_0;
mind_bool[1140]:=XVH_CrpGrfsON[11]; | mind[1140]:=XVH_VentilTYValue[3,2]; |  |  |  |  | 1140:XVH_CrpGrfsON[11]:=Bit_0; | 1140:XVH_VentilTYValue[3,2]:=Byte_0;
mind_bool[1141]:=XVH_CrpGrfsON[12]; | mind[1141]:=XVH_VentilTYValue[4,1]; |  |  |  |  | 1141:XVH_CrpGrfsON[12]:=Bit_0; | 1141:XVH_VentilTYValue[4,1]:=Byte_0;
mind_bool[1142]:=XVH_CrpGrfsON[13]; | mind[1142]:=XVH_VentilTYValue[4,2]; |  |  |  |  | 1142:XVH_CrpGrfsON[13]:=Bit_0; | 1142:XVH_VentilTYValue[4,2]:=Byte_0;
mind_bool[1143]:=XVH_CrpGrfsON[14]; | mind[1143]:=XVH_VlazilecStatus[1]; |  |  |  |  | 1143:XVH_CrpGrfsON[14]:=Bit_0; | 1143:XVH_VlazilecStatus[1]:=Byte_0;
mind_bool[1144]:=XVH_CrpGrfsON[1]; | mind[1144]:=XVH_VlazilecStatus[2]; |  |  |  |  | 1144:XVH_CrpGrfsON[1]:=Bit_0; | 1144:XVH_VlazilecStatus[2]:=Byte_0;
mind_bool[1145]:=XVH_CrpGrfsON[2]; | mind[1145]:=XVHnum[10]; |  |  |  |  | 1145:XVH_CrpGrfsON[2]:=Bit_0; | 1145:XVHnum[10]:=Byte_0;
mind_bool[1146]:=XVH_CrpGrfsON[3]; | mind[1146]:=XVHnum[11]; |  |  |  |  | 1146:XVH_CrpGrfsON[3]:=Bit_0; | 1146:XVHnum[11]:=Byte_0;
mind_bool[1147]:=XVH_CrpGrfsON[4]; | mind[1147]:=XVHnum[12]; |  |  |  |  | 1147:XVH_CrpGrfsON[4]:=Bit_0; | 1147:XVHnum[12]:=Byte_0;
mind_bool[1148]:=XVH_CrpGrfsON[5]; | mind[1148]:=XVHnum[13]; |  |  |  |  | 1148:XVH_CrpGrfsON[5]:=Bit_0; | 1148:XVHnum[13]:=Byte_0;
mind_bool[1149]:=XVH_CrpGrfsON[6]; | mind[1149]:=XVHnum[14]; |  |  |  |  | 1149:XVH_CrpGrfsON[6]:=Bit_0; | 1149:XVHnum[14]:=Byte_0;
mind_bool[1150]:=XVH_CrpGrfsON[7]; | mind[1150]:=XVHnum[1]; |  |  |  |  | 1150:XVH_CrpGrfsON[7]:=Bit_0; | 1150:XVHnum[1]:=Byte_0;
mind_bool[1151]:=XVH_CrpGrfsON[8]; | mind[1151]:=XVHnum[2]; |  |  |  |  | 1151:XVH_CrpGrfsON[8]:=Bit_0; | 1151:XVHnum[2]:=Byte_0;
mind_bool[1152]:=XVH_CrpGrfsON[9]; | mind[1152]:=XVHnum[3]; |  |  |  |  | 1152:XVH_CrpGrfsON[9]:=Bit_0; | 1152:XVHnum[3]:=Byte_0;
mind_bool[1153]:=XVH_CrpGrfsPIDreset; | mind[1153]:=XVHnum[4]; |  |  |  |  | 1153:XVH_CrpGrfsPIDreset:=Bit_0; | 1153:XVHnum[4]:=Byte_0;
mind_bool[1154]:=XVH_CrpGrfsVisibleData[10]; | mind[1154]:=XVHnum[5]; |  |  |  |  | 1154:XVH_CrpGrfsVisibleData[10]:=Bit_0; | 1154:XVHnum[5]:=Byte_0;
mind_bool[1155]:=XVH_CrpGrfsVisibleData[11]; | mind[1155]:=XVHnum[6]; |  |  |  |  | 1155:XVH_CrpGrfsVisibleData[11]:=Bit_0; | 1155:XVHnum[6]:=Byte_0;
mind_bool[1156]:=XVH_CrpGrfsVisibleData[12]; | mind[1156]:=XVHnum[7]; |  |  |  |  | 1156:XVH_CrpGrfsVisibleData[12]:=Bit_0; | 1156:XVHnum[7]:=Byte_0;
mind_bool[1157]:=XVH_CrpGrfsVisibleData[13]; | mind[1157]:=XVHnum[8]; |  |  |  |  | 1157:XVH_CrpGrfsVisibleData[13]:=Bit_0; | 1157:XVHnum[8]:=Byte_0;
mind_bool[1158]:=XVH_CrpGrfsVisibleData[14]; | mind[1158]:=XVHnum[9]; |  |  |  |  | 1158:XVH_CrpGrfsVisibleData[14]:=Bit_0; | 1158:XVHnum[9]:=Byte_0;
mind_bool[1159]:=XVH_CrpGrfsVisibleData[15]; | [5 empty] | 1159:XVH_CrpGrfsVisibleData[15]:=Bit_0;
mind_bool[1160]:=XVH_CrpGrfsVisibleData[16]; | [5 empty] | 1160:XVH_CrpGrfsVisibleData[16]:=Bit_0;
mind_bool[1161]:=XVH_CrpGrfsVisibleData[1]; | [5 empty] | 1161:XVH_CrpGrfsVisibleData[1]:=Bit_0;
mind_bool[1162]:=XVH_CrpGrfsVisibleData[2]; | [5 empty] | 1162:XVH_CrpGrfsVisibleData[2]:=Bit_0;
mind_bool[1163]:=XVH_CrpGrfsVisibleData[3]; | [5 empty] | 1163:XVH_CrpGrfsVisibleData[3]:=Bit_0;
mind_bool[1164]:=XVH_CrpGrfsVisibleData[4]; | [5 empty] | 1164:XVH_CrpGrfsVisibleData[4]:=Bit_0;
mind_bool[1165]:=XVH_CrpGrfsVisibleData[5]; | [5 empty] | 1165:XVH_CrpGrfsVisibleData[5]:=Bit_0;
mind_bool[1166]:=XVH_CrpGrfsVisibleData[6]; | [5 empty] | 1166:XVH_CrpGrfsVisibleData[6]:=Bit_0;
mind_bool[1167]:=XVH_CrpGrfsVisibleData[7]; | [5 empty] | 1167:XVH_CrpGrfsVisibleData[7]:=Bit_0;
mind_bool[1168]:=XVH_CrpGrfsVisibleData[8]; | [5 empty] | 1168:XVH_CrpGrfsVisibleData[8]:=Bit_0;
mind_bool[1169]:=XVH_CrpGrfsVisibleData[9]; | [5 empty] | 1169:XVH_CrpGrfsVisibleData[9]:=Bit_0;
mind_bool[1170]:=XVH_CrpGrundfosNaCas; | [5 empty] | 1170:XVH_CrpGrundfosNaCas:=Bit_0;
mind_bool[1171]:=XVH_CrpGrundfosNaTlak; | [5 empty] | 1171:XVH_CrpGrundfosNaTlak:=Bit_0;
mind_bool[1172]:=XVH_CrpGrundfosON; | [5 empty] | 1172:XVH_CrpGrundfosON:=Bit_0;
mind_bool[1173]:=XVH_CrpGrundfosResetAlarm; | [5 empty] | 1173:XVH_CrpGrundfosResetAlarm:=Bit_0;
mind_bool[1174]:=XVH_CrpGrundfosResetAlarmLog; | [5 empty] | 1174:XVH_CrpGrundfosResetAlarmLog:=Bit_0;
mind_bool[1175]:=XVH_CrpGrundfosSetRef; | [5 empty] | 1175:XVH_CrpGrundfosSetRef:=Bit_0;
mind_bool[1176]:=XVH_RazsvOnOff; | [5 empty] | 1176:XVH_RazsvOnOff:=Bit_0;
mind_bool[1177]:=XVH_setCircNum[1]; | [5 empty] | 1177:XVH_setCircNum[1]:=Bit_0;
mind_bool[1178]:=XVH_setCircNum[2]; | [5 empty] | 1178:XVH_setCircNum[2]:=Bit_0;
mind_bool[1179]:=XVH_setCircNum[3]; | [5 empty] | 1179:XVH_setCircNum[3]:=Bit_0;
mind_bool[1180]:=XVH_setCircNum[4]; | [5 empty] | 1180:XVH_setCircNum[4]:=Bit_0;
mind_bool[1181]:=XVH_setCircNum[5]; | [5 empty] | 1181:XVH_setCircNum[5]:=Bit_0;
mind_bool[1182]:=XVH_UrnikNalozi; | [5 empty] | 1182:XVH_UrnikNalozi:=Bit_0;
mind_bool[1183]:=XVH_UrnikNonStop; | [5 empty] | 1183:XVH_UrnikNonStop:=Bit_0;
mind_bool[1184]:=XVH_UrnikPotrdiVpis; | [5 empty] | 1184:XVH_UrnikPotrdiVpis:=Bit_0;
mind_bool[1185]:=XVH_UrnikPreklicVpisa; | [5 empty] | 1185:XVH_UrnikPreklicVpisa:=Bit_0;
mind_bool[1186]:=XVH_UrnikShrani; | [5 empty] | 1186:XVH_UrnikShrani:=Bit_0;
mind_bool[1187]:=XVH_VpisUrnika; | [5 empty] | 1187:XVH_VpisUrnika:=Bit_0;
mind_bool[1188]:=ErrCommScada2; | [5 empty] | 1188:ErrCommScada2:=Bit_0;
mind_bool[1189]:=ComSCADA2; | [5 empty] | 1189:ComSCADA2:=Bit_0;
mind_bool[1190]:=ComSCADA3; | [5 empty] | 1190:ComSCADA3:=Bit_0;
mind_bool[1191]:=Circ_Vpis_Dnevne_energija_scada1; | [5 empty] | 1191:Circ_Vpis_Dnevne_energija_scada1:=Bit_0;
mind_bool[1192]:=Circ_Vpis_Dnevne_energija_scada2; | [5 empty] | 1192:Circ_Vpis_Dnevne_energija_scada2:=Bit_0;
mind_bool[1193]:=Circ_Vpis_Tedenska_energija_scada1; | [5 empty] | 1193:Circ_Vpis_Tedenska_energija_scada1:=Bit_0;
mind_bool[1194]:=Circ_Vpis_Tedenska_energija_scada2; | [5 empty] | 1194:Circ_Vpis_Tedenska_energija_scada2:=Bit_0;
mind_bool[1195]:=Circ_Vpis_Mesecna_energija_scada1; | [5 empty] | 1195:Circ_Vpis_Mesecna_energija_scada1:=Bit_0;
mind_bool[1196]:=Circ_Vpis_Mesecna_energija_scada2; | [5 empty] | 1196:Circ_Vpis_Mesecna_energija_scada2:=Bit_0;

## XSoft_EXP
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
PROGRAM mod_Read
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*Branje BOOL*)
(**)
mind_bool[0]:=AkumSanVodeTE1OnOff;
mind_bool[1]:=AlarmGenCirc1;
mind_bool[2]:=AlarmGenComm;
mind_bool[3]:=AlarmGenDI;
mind_bool[4]:=AlarmGenHladPost;
mind_bool[5]:=AlarmGenKlima1;
mind_bool[6]:=AlarmGenKlima2;
mind_bool[7]:=AlarmGenLopute;
mind_bool[8]:=AlarmGenRest;
mind_bool[9]:=AlarmGenSenzor;
mind_bool[10]:=AlarmGenTemp;
mind_bool[11]:=AlarmGenToplPost;
mind_bool[12]:=AlarmGenVent;
mind_bool[13]:=AlarmGenVTV;
mind_bool[14]:=ATVTempPrenizka;
mind_bool[15]:=ComSCADA;
mind_bool[16]:=ComSCADA1;
mind_bool[17]:=CrpalkaMN1OnOff;
mind_bool[18]:=CrpalkaTm11TM12OnOff;
mind_bool[19]:=CrpalkeDnfs[1].AlarmAktiven;
mind_bool[20]:=CrpalkeDnfs[1].Deluje;
mind_bool[21]:=CrpalkeDnfs[1].QuickStop;
mind_bool[22]:=CrpalkeDnfs[1].RemoteON;
mind_bool[23]:=CrpalkeDnfs[1].Reset;
mind_bool[24]:=CrpalkeDnfs[1].Start;
mind_bool[25]:=CrpalkeDnfs[1].Stop;
mind_bool[26]:=CrpalkeDnfs[2].AlarmAktiven;
mind_bool[27]:=CrpalkeDnfs[2].Deluje;
mind_bool[28]:=CrpalkeDnfs[2].QuickStop;
mind_bool[29]:=CrpalkeDnfs[2].RemoteON;
mind_bool[30]:=CrpalkeDnfs[2].Reset;
mind_bool[31]:=CrpalkeDnfs[2].Start;
mind_bool[32]:=CrpalkeDnfs[2].Stop;
mind_bool[33]:=CrpalkeDnfs[3].AlarmAktiven;
mind_bool[34]:=CrpalkeDnfs[3].Deluje;
mind_bool[35]:=CrpalkeDnfs[3].QuickStop;
mind_bool[36]:=CrpalkeDnfs[3].RemoteON;
mind_bool[37]:=CrpalkeDnfs[3].Reset;
mind_bool[38]:=CrpalkeDnfs[3].Start;
mind_bool[39]:=CrpalkeDnfs[3].Stop;
mind_bool[40]:=CrpalkeDnfs[4].AlarmAktiven;
mind_bool[41]:=CrpalkeDnfs[4].Deluje;
mind_bool[42]:=CrpalkeDnfs[4].QuickStop;
mind_bool[43]:=CrpalkeDnfs[4].RemoteON;
mind_bool[44]:=CrpalkeDnfs[4].Reset;
mind_bool[45]:=CrpalkeDnfs[4].Start;
mind_bool[46]:=CrpalkeDnfs[4].Stop;
mind_bool[47]:=CrpalkeGrfs[10].AlarmAktiven;
mind_bool[48]:=CrpalkeGrfs[10].Deluje;
mind_bool[49]:=CrpalkeGrfs[10].LocalMode;
mind_bool[50]:=CrpalkeGrfs[10].RemoteON;
mind_bool[51]:=CrpalkeGrfs[10].Reset2handkWhValues;
mind_bool[52]:=CrpalkeGrfs[10].ResetAlarm;
mind_bool[53]:=CrpalkeGrfs[10].ResetAlarmLog;
mind_bool[54]:=CrpalkeGrfs[10].ResetDevice;
mind_bool[55]:=CrpalkeGrfs[10].SetAutomatic;
mind_bool[56]:=CrpalkeGrfs[10].SetConstFreqMode;
mind_bool[57]:=CrpalkeGrfs[10].SetConstPress;
mind_bool[58]:=CrpalkeGrfs[10].SetLocalMode;
mind_bool[59]:=CrpalkeGrfs[10].SetMaxRunMode;
mind_bool[60]:=CrpalkeGrfs[10].SetMinRunMode;
mind_bool[61]:=CrpalkeGrfs[10].SetPropPress;
mind_bool[62]:=CrpalkeGrfs[10].SetReference;
mind_bool[63]:=CrpalkeGrfs[10].SetRemoteMode;
mind_bool[64]:=CrpalkeGrfs[10].SetTwinModeAlt;
mind_bool[65]:=CrpalkeGrfs[10].SetTwinModeSpare;
mind_bool[66]:=CrpalkeGrfs[10].SetTwinModeSync;
mind_bool[67]:=CrpalkeGrfs[10].Start;
mind_bool[68]:=CrpalkeGrfs[10].Stop;
mind_bool[69]:=CrpalkeGrfs[11].AlarmAktiven;
mind_bool[70]:=CrpalkeGrfs[11].Deluje;
mind_bool[71]:=CrpalkeGrfs[11].LocalMode;
mind_bool[72]:=CrpalkeGrfs[11].RemoteON;
mind_bool[73]:=CrpalkeGrfs[11].Reset2handkWhValues;
mind_bool[74]:=CrpalkeGrfs[11].ResetAlarm;
mind_bool[75]:=CrpalkeGrfs[11].ResetAlarmLog;
mind_bool[76]:=CrpalkeGrfs[11].ResetDevice;
mind_bool[77]:=CrpalkeGrfs[11].SetAutomatic;
mind_bool[78]:=CrpalkeGrfs[11].SetConstFreqMode;
mind_bool[79]:=CrpalkeGrfs[11].SetConstPress;
mind_bool[80]:=CrpalkeGrfs[11].SetLocalMode;
mind_bool[81]:=CrpalkeGrfs[11].SetMaxRunMode;
mind_bool[82]:=CrpalkeGrfs[11].SetMinRunMode;
mind_bool[83]:=CrpalkeGrfs[11].SetPropPress;
mind_bool[84]:=CrpalkeGrfs[11].SetReference;
mind_bool[85]:=CrpalkeGrfs[11].SetRemoteMode;
mind_bool[86]:=CrpalkeGrfs[11].SetTwinModeAlt;
mind_bool[87]:=CrpalkeGrfs[11].SetTwinModeSpare;
mind_bool[88]:=CrpalkeGrfs[11].SetTwinModeSync;
mind_bool[89]:=CrpalkeGrfs[11].Start;
mind_bool[90]:=CrpalkeGrfs[11].Stop;
mind_bool[91]:=CrpalkeGrfs[12].AlarmAktiven;
mind_bool[92]:=CrpalkeGrfs[12].Deluje;
mind_bool[93]:=CrpalkeGrfs[12].LocalMode;
mind_bool[94]:=CrpalkeGrfs[12].RemoteON;
mind_bool[95]:=CrpalkeGrfs[12].Reset2handkWhValues;
mind_bool[96]:=CrpalkeGrfs[12].ResetAlarm;
mind_bool[97]:=CrpalkeGrfs[12].ResetAlarmLog;
mind_bool[98]:=CrpalkeGrfs[12].ResetDevice;
mind_bool[99]:=CrpalkeGrfs[12].SetAutomatic;
mind_bool[100]:=CrpalkeGrfs[12].SetConstFreqMode;
mind_bool[101]:=CrpalkeGrfs[12].SetConstPress;
mind_bool[102]:=CrpalkeGrfs[12].SetLocalMode;
mind_bool[103]:=CrpalkeGrfs[12].SetMaxRunMode;
mind_bool[104]:=CrpalkeGrfs[12].SetMinRunMode;
mind_bool[105]:=CrpalkeGrfs[12].SetPropPress;
mind_bool[106]:=CrpalkeGrfs[12].SetReference;
mind_bool[107]:=CrpalkeGrfs[12].SetRemoteMode;
mind_bool[108]:=CrpalkeGrfs[12].SetTwinModeAlt;
mind_bool[109]:=CrpalkeGrfs[12].SetTwinModeSpare;
mind_bool[110]:=CrpalkeGrfs[12].SetTwinModeSync;
mind_bool[111]:=CrpalkeGrfs[12].Start;
mind_bool[112]:=CrpalkeGrfs[12].Stop;
mind_bool[113]:=CrpalkeGrfs[13].AlarmAktiven;
mind_bool[114]:=CrpalkeGrfs[13].Deluje;
mind_bool[115]:=CrpalkeGrfs[13].LocalMode;
mind_bool[116]:=CrpalkeGrfs[13].RemoteON;
mind_bool[117]:=CrpalkeGrfs[13].Reset2handkWhValues;
mind_bool[118]:=CrpalkeGrfs[13].ResetAlarm;
mind_bool[119]:=CrpalkeGrfs[13].ResetAlarmLog;
mind_bool[120]:=CrpalkeGrfs[13].ResetDevice;
mind_bool[121]:=CrpalkeGrfs[13].SetAutomatic;
mind_bool[122]:=CrpalkeGrfs[13].SetConstFreqMode;
mind_bool[123]:=CrpalkeGrfs[13].SetConstPress;
mind_bool[124]:=CrpalkeGrfs[13].SetLocalMode;
mind_bool[125]:=CrpalkeGrfs[13].SetMaxRunMode;
mind_bool[126]:=CrpalkeGrfs[13].SetMinRunMode;
mind_bool[127]:=CrpalkeGrfs[13].SetPropPress;
mind_bool[128]:=CrpalkeGrfs[13].SetReference;
mind_bool[129]:=CrpalkeGrfs[13].SetRemoteMode;
mind_bool[130]:=CrpalkeGrfs[13].SetTwinModeAlt;
mind_bool[131]:=CrpalkeGrfs[13].SetTwinModeSpare;
mind_bool[132]:=CrpalkeGrfs[13].SetTwinModeSync;
mind_bool[133]:=CrpalkeGrfs[13].Start;
mind_bool[134]:=CrpalkeGrfs[13].Stop;
mind_bool[135]:=CrpalkeGrfs[14].AlarmAktiven;
mind_bool[136]:=CrpalkeGrfs[14].Deluje;
mind_bool[137]:=CrpalkeGrfs[14].LocalMode;
mind_bool[138]:=CrpalkeGrfs[14].RemoteON;
mind_bool[139]:=CrpalkeGrfs[14].Reset2handkWhValues;
mind_bool[140]:=CrpalkeGrfs[14].ResetAlarm;
mind_bool[141]:=CrpalkeGrfs[14].ResetAlarmLog;
mind_bool[142]:=CrpalkeGrfs[14].ResetDevice;
mind_bool[143]:=CrpalkeGrfs[14].SetAutomatic;
mind_bool[144]:=CrpalkeGrfs[14].SetConstFreqMode;
mind_bool[145]:=CrpalkeGrfs[14].SetConstPress;
mind_bool[146]:=CrpalkeGrfs[14].SetLocalMode;
mind_bool[147]:=CrpalkeGrfs[14].SetMaxRunMode;
mind_bool[148]:=CrpalkeGrfs[14].SetMinRunMode;
mind_bool[149]:=CrpalkeGrfs[14].SetPropPress;
mind_bool[150]:=CrpalkeGrfs[14].SetReference;
mind_bool[151]:=CrpalkeGrfs[14].SetRemoteMode;
mind_bool[152]:=CrpalkeGrfs[14].SetTwinModeAlt;
mind_bool[153]:=CrpalkeGrfs[14].SetTwinModeSpare;
mind_bool[154]:=CrpalkeGrfs[14].SetTwinModeSync;
mind_bool[155]:=CrpalkeGrfs[14].Start;
mind_bool[156]:=CrpalkeGrfs[14].Stop;
mind_bool[157]:=CrpalkeGrfs[1].AlarmAktiven;
mind_bool[158]:=CrpalkeGrfs[1].Deluje;
mind_bool[159]:=CrpalkeGrfs[1].LocalMode;
mind_bool[160]:=CrpalkeGrfs[1].RemoteON;
mind_bool[161]:=CrpalkeGrfs[1].Reset2handkWhValues;
mind_bool[162]:=CrpalkeGrfs[1].ResetAlarm;
mind_bool[163]:=CrpalkeGrfs[1].ResetAlarmLog;
mind_bool[164]:=CrpalkeGrfs[1].ResetDevice;
mind_bool[165]:=CrpalkeGrfs[1].SetAutomatic;
mind_bool[166]:=CrpalkeGrfs[1].SetConstFreqMode;
mind_bool[167]:=CrpalkeGrfs[1].SetConstPress;
mind_bool[168]:=CrpalkeGrfs[1].SetLocalMode;
mind_bool[169]:=CrpalkeGrfs[1].SetMaxRunMode;
mind_bool[170]:=CrpalkeGrfs[1].SetMinRunMode;
mind_bool[171]:=CrpalkeGrfs[1].SetPropPress;
mind_bool[172]:=CrpalkeGrfs[1].SetReference;
mind_bool[173]:=CrpalkeGrfs[1].SetRemoteMode;
mind_bool[174]:=CrpalkeGrfs[1].SetTwinModeAlt;
mind_bool[175]:=CrpalkeGrfs[1].SetTwinModeSpare;
mind_bool[176]:=CrpalkeGrfs[1].SetTwinModeSync;
mind_bool[177]:=CrpalkeGrfs[1].Start;
mind_bool[178]:=CrpalkeGrfs[1].Stop;
mind_bool[179]:=CrpalkeGrfs[2].AlarmAktiven;
mind_bool[180]:=CrpalkeGrfs[2].Deluje;
mind_bool[181]:=CrpalkeGrfs[2].LocalMode;
mind_bool[182]:=CrpalkeGrfs[2].RemoteON;
mind_bool[183]:=CrpalkeGrfs[2].Reset2handkWhValues;
mind_bool[184]:=CrpalkeGrfs[2].ResetAlarm;
mind_bool[185]:=CrpalkeGrfs[2].ResetAlarmLog;
mind_bool[186]:=CrpalkeGrfs[2].ResetDevice;
mind_bool[187]:=CrpalkeGrfs[2].SetAutomatic;
mind_bool[188]:=CrpalkeGrfs[2].SetConstFreqMode;
mind_bool[189]:=CrpalkeGrfs[2].SetConstPress;
mind_bool[190]:=CrpalkeGrfs[2].SetLocalMode;
mind_bool[191]:=CrpalkeGrfs[2].SetMaxRunMode;
mind_bool[192]:=CrpalkeGrfs[2].SetMinRunMode;
mind_bool[193]:=CrpalkeGrfs[2].SetPropPress;
mind_bool[194]:=CrpalkeGrfs[2].SetReference;
mind_bool[195]:=CrpalkeGrfs[2].SetRemoteMode;
mind_bool[196]:=CrpalkeGrfs[2].SetTwinModeAlt;
mind_bool[197]:=CrpalkeGrfs[2].SetTwinModeSpare;
mind_bool[198]:=CrpalkeGrfs[2].SetTwinModeSync;
mind_bool[199]:=CrpalkeGrfs[2].Start;
mind_bool[200]:=CrpalkeGrfs[2].Stop;
mind_bool[201]:=CrpalkeGrfs[3].AlarmAktiven;
mind_bool[202]:=CrpalkeGrfs[3].Deluje;
mind_bool[203]:=CrpalkeGrfs[3].LocalMode;
mind_bool[204]:=CrpalkeGrfs[3].RemoteON;
mind_bool[205]:=CrpalkeGrfs[3].Reset2handkWhValues;
mind_bool[206]:=CrpalkeGrfs[3].ResetAlarm;
mind_bool[207]:=CrpalkeGrfs[3].ResetAlarmLog;
mind_bool[208]:=CrpalkeGrfs[3].ResetDevice;
mind_bool[209]:=CrpalkeGrfs[3].SetAutomatic;
mind_bool[210]:=CrpalkeGrfs[3].SetConstFreqMode;
mind_bool[211]:=CrpalkeGrfs[3].SetConstPress;
mind_bool[212]:=CrpalkeGrfs[3].SetLocalMode;
mind_bool[213]:=CrpalkeGrfs[3].SetMaxRunMode;
mind_bool[214]:=CrpalkeGrfs[3].SetMinRunMode;
mind_bool[215]:=CrpalkeGrfs[3].SetPropPress;
mind_bool[216]:=CrpalkeGrfs[3].SetReference;
mind_bool[217]:=CrpalkeGrfs[3].SetRemoteMode;
mind_bool[218]:=CrpalkeGrfs[3].SetTwinModeAlt;
mind_bool[219]:=CrpalkeGrfs[3].SetTwinModeSpare;
mind_bool[220]:=CrpalkeGrfs[3].SetTwinModeSync;
mind_bool[221]:=CrpalkeGrfs[3].Start;
mind_bool[222]:=CrpalkeGrfs[3].Stop;
mind_bool[223]:=CrpalkeGrfs[4].AlarmAktiven;
mind_bool[224]:=CrpalkeGrfs[4].Deluje;
mind_bool[225]:=CrpalkeGrfs[4].LocalMode;
mind_bool[226]:=CrpalkeGrfs[4].RemoteON;
mind_bool[227]:=CrpalkeGrfs[4].Reset2handkWhValues;
mind_bool[228]:=CrpalkeGrfs[4].ResetAlarm;
mind_bool[229]:=CrpalkeGrfs[4].ResetAlarmLog;
mind_bool[230]:=CrpalkeGrfs[4].ResetDevice;
mind_bool[231]:=CrpalkeGrfs[4].SetAutomatic;
mind_bool[232]:=CrpalkeGrfs[4].SetConstFreqMode;
mind_bool[233]:=CrpalkeGrfs[4].SetConstPress;
mind_bool[234]:=CrpalkeGrfs[4].SetLocalMode;
mind_bool[235]:=CrpalkeGrfs[4].SetMaxRunMode;
mind_bool[236]:=CrpalkeGrfs[4].SetMinRunMode;
mind_bool[237]:=CrpalkeGrfs[4].SetPropPress;
mind_bool[238]:=CrpalkeGrfs[4].SetReference;
mind_bool[239]:=CrpalkeGrfs[4].SetRemoteMode;
mind_bool[240]:=CrpalkeGrfs[4].SetTwinModeAlt;
mind_bool[241]:=CrpalkeGrfs[4].SetTwinModeSpare;
mind_bool[242]:=CrpalkeGrfs[4].SetTwinModeSync;
mind_bool[243]:=CrpalkeGrfs[4].Start;
mind_bool[244]:=CrpalkeGrfs[4].Stop;
mind_bool[245]:=CrpalkeGrfs[5].AlarmAktiven;
mind_bool[246]:=CrpalkeGrfs[5].Deluje;
mind_bool[247]:=CrpalkeGrfs[5].LocalMode;
mind_bool[248]:=CrpalkeGrfs[5].RemoteON;
mind_bool[249]:=CrpalkeGrfs[5].Reset2handkWhValues;
mind_bool[250]:=CrpalkeGrfs[5].ResetAlarm;
mind_bool[251]:=CrpalkeGrfs[5].ResetAlarmLog;
mind_bool[252]:=CrpalkeGrfs[5].ResetDevice;
mind_bool[253]:=CrpalkeGrfs[5].SetAutomatic;
mind_bool[254]:=CrpalkeGrfs[5].SetConstFreqMode;
mind_bool[255]:=CrpalkeGrfs[5].SetConstPress;
mind_bool[256]:=CrpalkeGrfs[5].SetLocalMode;
mind_bool[257]:=CrpalkeGrfs[5].SetMaxRunMode;
mind_bool[258]:=CrpalkeGrfs[5].SetMinRunMode;
mind_bool[259]:=CrpalkeGrfs[5].SetPropPress;
mind_bool[260]:=CrpalkeGrfs[5].SetReference;
mind_bool[261]:=CrpalkeGrfs[5].SetRemoteMode;
mind_bool[262]:=CrpalkeGrfs[5].SetTwinModeAlt;
mind_bool[263]:=CrpalkeGrfs[5].SetTwinModeSpare;
mind_bool[264]:=CrpalkeGrfs[5].SetTwinModeSync;
mind_bool[265]:=CrpalkeGrfs[5].Start;
mind_bool[266]:=CrpalkeGrfs[5].Stop;
mind_bool[267]:=CrpalkeGrfs[6].AlarmAktiven;
mind_bool[268]:=CrpalkeGrfs[6].Deluje;
mind_bool[269]:=CrpalkeGrfs[6].LocalMode;
mind_bool[270]:=CrpalkeGrfs[6].RemoteON;
mind_bool[271]:=CrpalkeGrfs[6].Reset2handkWhValues;
mind_bool[272]:=CrpalkeGrfs[6].ResetAlarm;
mind_bool[273]:=CrpalkeGrfs[6].ResetAlarmLog;
mind_bool[274]:=CrpalkeGrfs[6].ResetDevice;
mind_bool[275]:=CrpalkeGrfs[6].SetAutomatic;
mind_bool[276]:=CrpalkeGrfs[6].SetConstFreqMode;
mind_bool[277]:=CrpalkeGrfs[6].SetConstPress;
mind_bool[278]:=CrpalkeGrfs[6].SetLocalMode;
mind_bool[279]:=CrpalkeGrfs[6].SetMaxRunMode;
mind_bool[280]:=CrpalkeGrfs[6].SetMinRunMode;
mind_bool[281]:=CrpalkeGrfs[6].SetPropPress;
mind_bool[282]:=CrpalkeGrfs[6].SetReference;
mind_bool[283]:=CrpalkeGrfs[6].SetRemoteMode;
mind_bool[284]:=CrpalkeGrfs[6].SetTwinModeAlt;
mind_bool[285]:=CrpalkeGrfs[6].SetTwinModeSpare;
mind_bool[286]:=CrpalkeGrfs[6].SetTwinModeSync;
mind_bool[287]:=CrpalkeGrfs[6].Start;
mind_bool[288]:=CrpalkeGrfs[6].Stop;
mind_bool[289]:=CrpalkeGrfs[7].AlarmAktiven;
mind_bool[290]:=CrpalkeGrfs[7].Deluje;
mind_bool[291]:=CrpalkeGrfs[7].LocalMode;
mind_bool[292]:=CrpalkeGrfs[7].RemoteON;
mind_bool[293]:=CrpalkeGrfs[7].Reset2handkWhValues;
mind_bool[294]:=CrpalkeGrfs[7].ResetAlarm;
mind_bool[295]:=CrpalkeGrfs[7].ResetAlarmLog;
mind_bool[296]:=CrpalkeGrfs[7].ResetDevice;
mind_bool[297]:=CrpalkeGrfs[7].SetAutomatic;
mind_bool[298]:=CrpalkeGrfs[7].SetConstFreqMode;
mind_bool[299]:=CrpalkeGrfs[7].SetConstPress;
mind_bool[300]:=CrpalkeGrfs[7].SetLocalMode;
mind_bool[301]:=CrpalkeGrfs[7].SetMaxRunMode;
mind_bool[302]:=CrpalkeGrfs[7].SetMinRunMode;
mind_bool[303]:=CrpalkeGrfs[7].SetPropPress;
mind_bool[304]:=CrpalkeGrfs[7].SetReference;
mind_bool[305]:=CrpalkeGrfs[7].SetRemoteMode;
mind_bool[306]:=CrpalkeGrfs[7].SetTwinModeAlt;
mind_bool[307]:=CrpalkeGrfs[7].SetTwinModeSpare;
mind_bool[308]:=CrpalkeGrfs[7].SetTwinModeSync;
mind_bool[309]:=CrpalkeGrfs[7].Start;
mind_bool[310]:=CrpalkeGrfs[7].Stop;
mind_bool[311]:=CrpalkeGrfs[8].AlarmAktiven;
mind_bool[312]:=CrpalkeGrfs[8].Deluje;
mind_bool[313]:=CrpalkeGrfs[8].LocalMode;
mind_bool[314]:=CrpalkeGrfs[8].RemoteON;
mind_bool[315]:=CrpalkeGrfs[8].Reset2handkWhValues;
mind_bool[316]:=CrpalkeGrfs[8].ResetAlarm;
mind_bool[317]:=CrpalkeGrfs[8].ResetAlarmLog;
mind_bool[318]:=CrpalkeGrfs[8].ResetDevice;
mind_bool[319]:=CrpalkeGrfs[8].SetAutomatic;
mind_bool[320]:=CrpalkeGrfs[8].SetConstFreqMode;
mind_bool[321]:=CrpalkeGrfs[8].SetConstPress;
mind_bool[322]:=CrpalkeGrfs[8].SetLocalMode;
mind_bool[323]:=CrpalkeGrfs[8].SetMaxRunMode;
mind_bool[324]:=CrpalkeGrfs[8].SetMinRunMode;
mind_bool[325]:=CrpalkeGrfs[8].SetPropPress;
mind_bool[326]:=CrpalkeGrfs[8].SetReference;
mind_bool[327]:=CrpalkeGrfs[8].SetRemoteMode;
mind_bool[328]:=CrpalkeGrfs[8].SetTwinModeAlt;
mind_bool[329]:=CrpalkeGrfs[8].SetTwinModeSpare;
mind_bool[330]:=CrpalkeGrfs[8].SetTwinModeSync;
mind_bool[331]:=CrpalkeGrfs[8].Start;
mind_bool[332]:=CrpalkeGrfs[8].Stop;
mind_bool[333]:=CrpalkeGrfs[9].AlarmAktiven;
mind_bool[334]:=CrpalkeGrfs[9].Deluje;
mind_bool[335]:=CrpalkeGrfs[9].LocalMode;
mind_bool[336]:=CrpalkeGrfs[9].RemoteON;
mind_bool[337]:=CrpalkeGrfs[9].Reset2handkWhValues;
mind_bool[338]:=CrpalkeGrfs[9].ResetAlarm;
mind_bool[339]:=CrpalkeGrfs[9].ResetAlarmLog;
mind_bool[340]:=CrpalkeGrfs[9].ResetDevice;
mind_bool[341]:=CrpalkeGrfs[9].SetAutomatic;
mind_bool[342]:=CrpalkeGrfs[9].SetConstFreqMode;
mind_bool[343]:=CrpalkeGrfs[9].SetConstPress;
mind_bool[344]:=CrpalkeGrfs[9].SetLocalMode;
mind_bool[345]:=CrpalkeGrfs[9].SetMaxRunMode;
mind_bool[346]:=CrpalkeGrfs[9].SetMinRunMode;
mind_bool[347]:=CrpalkeGrfs[9].SetPropPress;
mind_bool[348]:=CrpalkeGrfs[9].SetReference;
mind_bool[349]:=CrpalkeGrfs[9].SetRemoteMode;
mind_bool[350]:=CrpalkeGrfs[9].SetTwinModeAlt;
mind_bool[351]:=CrpalkeGrfs[9].SetTwinModeSpare;
mind_bool[352]:=CrpalkeGrfs[9].SetTwinModeSync;
mind_bool[353]:=CrpalkeGrfs[9].Start;
mind_bool[354]:=CrpalkeGrfs[9].Stop;
mind_bool[355]:=CrpDanfossGenError[1];
mind_bool[356]:=CrpDanfossGenError[2];
mind_bool[357]:=CrpDanfossGenError[3];
mind_bool[358]:=CrpDanfossGenError[4];
mind_bool[359]:=CrpDanfossNaCas[1];
mind_bool[360]:=CrpDanfossNaCas[2];
mind_bool[361]:=CrpDanfossON[1];
mind_bool[362]:=CrpDanfossON[2];
mind_bool[363]:=CrpDanfossON[3];
mind_bool[364]:=CrpDanfossON[4];
mind_bool[365]:=CrpDanfossStatusError[1];
mind_bool[366]:=CrpDanfossStatusError[2];
mind_bool[367]:=CrpDanfossStatusError[3];
mind_bool[368]:=CrpDanfossStatusError[4];
mind_bool[369]:=CrpGrundfosGenError[10];
mind_bool[370]:=CrpGrundfosGenError[11];
mind_bool[371]:=CrpGrundfosGenError[12];
mind_bool[372]:=CrpGrundfosGenError[13];
mind_bool[373]:=CrpGrundfosGenError[14];
mind_bool[374]:=CrpGrundfosGenError[1];
mind_bool[375]:=CrpGrundfosGenError[2];
mind_bool[376]:=CrpGrundfosGenError[3];
mind_bool[377]:=CrpGrundfosGenError[4];
mind_bool[378]:=CrpGrundfosGenError[5];
mind_bool[379]:=CrpGrundfosGenError[6];
mind_bool[380]:=CrpGrundfosGenError[7];
mind_bool[381]:=CrpGrundfosGenError[8];
mind_bool[382]:=CrpGrundfosGenError[9];
mind_bool[383]:=CrpGrundfosNaCas[1];
mind_bool[384]:=CrpGrundfosNaCas[2];
mind_bool[385]:=CrpGrundfosNaCas[3];
mind_bool[386]:=CrpGrundfosNaCas[4];
mind_bool[387]:=CrpGrundfosNaCas[5];
mind_bool[388]:=CrpGrundfosNaCas[6];
mind_bool[389]:=CrpGrundfosNaCas[7];
mind_bool[390]:=CrpGrundfosNaTlak[1];
mind_bool[391]:=CrpGrundfosNaTlak[2];
mind_bool[392]:=CrpGrundfosNaTlak[3];
mind_bool[393]:=CrpGrundfosNaTlak[4];
mind_bool[394]:=CrpGrundfosNaTlak[5];
mind_bool[395]:=CrpGrundfosNaTlak[6];
mind_bool[396]:=CrpGrundfosNaTlak[7];
mind_bool[397]:=CrpGrundfosON[10];
mind_bool[398]:=CrpGrundfosON[11];
mind_bool[399]:=CrpGrundfosON[12];
mind_bool[400]:=CrpGrundfosON[13];
mind_bool[401]:=CrpGrundfosON[14];
mind_bool[402]:=CrpGrundfosON[1];
mind_bool[403]:=CrpGrundfosON[2];
mind_bool[404]:=CrpGrundfosON[3];
mind_bool[405]:=CrpGrundfosON[4];
mind_bool[406]:=CrpGrundfosON[5];
mind_bool[407]:=CrpGrundfosON[6];
mind_bool[408]:=CrpGrundfosON[7];
mind_bool[409]:=CrpGrundfosON[8];
mind_bool[410]:=CrpGrundfosON[9];
mind_bool[411]:=CrpGrundfosStatusError[10];
mind_bool[412]:=CrpGrundfosStatusError[11];
mind_bool[413]:=CrpGrundfosStatusError[12];
mind_bool[414]:=CrpGrundfosStatusError[13];
mind_bool[415]:=CrpGrundfosStatusError[14];
mind_bool[416]:=CrpGrundfosStatusError[1];
mind_bool[417]:=CrpGrundfosStatusError[2];
mind_bool[418]:=CrpGrundfosStatusError[3];
mind_bool[419]:=CrpGrundfosStatusError[4];
mind_bool[420]:=CrpGrundfosStatusError[5];
mind_bool[421]:=CrpGrundfosStatusError[6];
mind_bool[422]:=CrpGrundfosStatusError[7];
mind_bool[423]:=CrpGrundfosStatusError[8];
mind_bool[424]:=CrpGrundfosStatusError[9];
mind_bool[425]:=DanfossHMKontOnOff[1];
mind_bool[426]:=DanfossHMKontOnOff[2];
mind_bool[427]:=DanfossHMKontOnOff[3];
mind_bool[428]:=DanfossHMKontOnOff[4];
mind_bool[429]:=DI_230VAC_OK;
mind_bool[430]:=DI_24VAC_OK;
mind_bool[431]:=DI_24VDC_OK;
mind_bool[432]:=DI_AkumTopVodeAUTO;
mind_bool[433]:=DI_AkumTopVodeKontON;
mind_bool[434]:=DI_CrpHM1AUTO;
mind_bool[435]:=DI_CrpHM1endOFFtoON;
mind_bool[436]:=DI_CrpHM1ERR;
mind_bool[437]:=DI_CrpHM1kontON;
mind_bool[438]:=DI_CrpHM2AUTO;
mind_bool[439]:=DI_CrpHM2endOFFtoON;
mind_bool[440]:=DI_CrpHM2ERR;
mind_bool[441]:=DI_CrpHM2kontON;
mind_bool[442]:=DI_CrpHM3AUTO;
mind_bool[443]:=DI_CrpHM3endOFFtoON;
mind_bool[444]:=DI_CrpHM3ERR;
mind_bool[445]:=DI_CrpHM3kontON;
mind_bool[446]:=DI_CrpHM4AUTO;
mind_bool[447]:=DI_CrpHM4endOFFtoON;
mind_bool[448]:=DI_CrpHM4ERR;
mind_bool[449]:=DI_CrpHM4kontON;
mind_bool[450]:=DI_CrpHM5AUTO;
mind_bool[451]:=DI_CrpHM6AUTO;
mind_bool[452]:=DI_CrpHM7AUTO;
mind_bool[453]:=DI_CrpHM8AUTO;
mind_bool[454]:=DI_CrpMN1AUTO;
mind_bool[455]:=DI_CrpMN1kontON;
mind_bool[456]:=DI_CrpTM10AUTO;
mind_bool[457]:=DI_CrpTM11TM12AUTO;
mind_bool[458]:=DI_CrpTM11TM12kontON;
mind_bool[459]:=DI_CrpTM1AUTO;
mind_bool[460]:=DI_CrpTM2AUTO;
mind_bool[461]:=DI_CrpTM3AUTO;
mind_bool[462]:=DI_CrpTM4AUTO;
mind_bool[463]:=DI_CrpTM5AUTO;
mind_bool[464]:=DI_CrpTM6AUTO;
mind_bool[465]:=DI_CrpTM7AUTO;
mind_bool[466]:=DI_CrpTM8AUTO;
mind_bool[467]:=DI_CrpTM9AUTO;
mind_bool[468]:=DI_GlStikaloDieselON;
mind_bool[469]:=DI_GlStikaloMrezaON;
mind_bool[470]:=DI_GlStikaloUpsON;
mind_bool[471]:=DI_HladStAUTO;
mind_bool[472]:=DI_HladStCrpHladH2OON;
mind_bool[473]:=DI_HladStERR;
mind_bool[474]:=DI_Klima1ERR;
mind_bool[475]:=DI_Klima1filterZAM;
mind_bool[476]:=DI_Klima1FIRE;
mind_bool[477]:=DI_Klima1OFFtoON;
mind_bool[478]:=DI_Klima1ON;
mind_bool[479]:=DI_Klima1zascStON;
mind_bool[480]:=DI_Klima2ERR;
mind_bool[481]:=DI_Klima2filterZAM;
mind_bool[482]:=DI_Klima2FIRE;
mind_bool[483]:=DI_Klima2OFFtoON;
mind_bool[484]:=DI_Klima2ON;
mind_bool[485]:=DI_Klima2zascStON;
mind_bool[486]:=DI_Komp1ERR;
mind_bool[487]:=DI_Komp1ON;
mind_bool[488]:=DI_Komp2ERR;
mind_bool[489]:=DI_Komp2ON;
mind_bool[490]:=DI_Kond1AUTO;
mind_bool[491]:=DI_Kond1FS1FS2;
mind_bool[492]:=DI_Kond1ON;
mind_bool[493]:=DI_Kond1zascStON;
mind_bool[494]:=DI_Kond2AUTO;
mind_bool[495]:=DI_Kond2FS1FS2;
mind_bool[496]:=DI_Kond2ON;
mind_bool[497]:=DI_Kond2zascStON;
mind_bool[498]:=DI_Kond3AUTO;
mind_bool[499]:=DI_Kond3FS1FS2;
mind_bool[500]:=DI_Kond3ON;
mind_bool[501]:=DI_Kond3zascStON;
mind_bool[502]:=DI_Lop1PL1Odprta;
mind_bool[503]:=DI_Lop1PL1Zaprta;
mind_bool[504]:=DI_Lop1PL2Odprta;
mind_bool[505]:=DI_Lop1PL2Zaprta;
mind_bool[506]:=DI_Lop1PL3Odprta;
mind_bool[507]:=DI_Lop1PL3Zaprta;
mind_bool[508]:=DI_Lop3Y1Odprta;
mind_bool[509]:=DI_Lop3Y1Zaprta;
mind_bool[510]:=DI_Lop4Y1Odprta;
mind_bool[511]:=DI_Lop4Y1Zaprta;
mind_bool[512]:=DI_PotrditevAlarmov;
mind_bool[513]:=DI_RazlitjeVodeEXP1;
mind_bool[514]:=DI_RazlitjeVodeEXP2;
mind_bool[515]:=DI_RazlitjeVodeHP;
mind_bool[516]:=DI_RazlitjeVodeK1;
mind_bool[517]:=DI_RazlitjeVodeK2;
mind_bool[518]:=DI_RazlitjeVodeTP;
mind_bool[519]:=DI_ToplPostGenErr;
mind_bool[520]:=DI_UPS_Alarm;
mind_bool[521]:=DI_UPS_BatNacin;
mind_bool[522]:=DI_UPS_Polnjenje;
mind_bool[523]:=DI_Vent1Auto;
mind_bool[524]:=DI_Vent1kontON;
mind_bool[525]:=DI_Vent2Auto;
mind_bool[526]:=DI_Vent2kontON;
mind_bool[527]:=DI_Vent3Auto;
mind_bool[528]:=DI_Vent3kontON;
mind_bool[529]:=DI_Vent4Auto;
mind_bool[530]:=DI_Vent4kontON;
mind_bool[531]:=DI_Vent5Auto;
mind_bool[532]:=DI_Vent5kontON;
mind_bool[533]:=DI_Vent6Auto;
mind_bool[534]:=DI_Vent6kontON;
mind_bool[535]:=DI_Vlaz1ERR;
mind_bool[536]:=DI_Vlaz1ON;
mind_bool[537]:=DI_Vlaz2ERR;
mind_bool[538]:=DI_Vlaz2ON;
mind_bool[539]:=DIN_230VAC_OK;
mind_bool[540]:=DIN_24VAC_OK;
mind_bool[541]:=DIN_24VDC_OK;
mind_bool[542]:=DIN_CrpHM1ERR;
mind_bool[543]:=DIN_CrpHM2ERR;
mind_bool[544]:=DIN_CrpHM3ERR;
mind_bool[545]:=DIN_CrpHM4ERR;
mind_bool[546]:=DIN_HladStERR;
mind_bool[547]:=DIN_Klima1ERR;
mind_bool[548]:=DIN_Klima1filterZAM;
mind_bool[549]:=DIN_Klima1zascStON;
mind_bool[550]:=DIN_Klima2ERR;
mind_bool[551]:=DIN_Klima2filterZAM;
mind_bool[552]:=DIN_Klima2zascStON;
mind_bool[553]:=DIN_Komp1ERR;
mind_bool[554]:=DIN_Komp1ON;
mind_bool[555]:=DIN_Komp2ERR;
mind_bool[556]:=DIN_Komp2ON;
mind_bool[557]:=DIN_Kond1zascStON;
mind_bool[558]:=DIN_Kond2zascStON;
mind_bool[559]:=DIN_Kond3zascStON;
mind_bool[560]:=DIN_Vlaz1ERR;
mind_bool[561]:=DIN_Vlaz2ERR;
mind_bool[562]:=DO_BojlerTE1Vklop;
mind_bool[563]:=DO_CrpHM1Vklop;
mind_bool[564]:=DO_CrpHM2Vklop;
mind_bool[565]:=DO_CrpHM3Vklop;
mind_bool[566]:=DO_CrpHM4Vklop;
mind_bool[567]:=DO_CrpMN1Vklop;
mind_bool[568]:=DO_CrpTM11Vklop;
mind_bool[569]:=DO_GrundfosVklopL;
mind_bool[570]:=DO_GrundfosVklopN;
mind_bool[571]:=DO_HladStrIzklop;
mind_bool[572]:=DO_KE1Vklop;
mind_bool[573]:=DO_KE2Vklop;
mind_bool[574]:=DO_KE3Vklop;
mind_bool[575]:=DO_Klima1Vklop;
mind_bool[576]:=DO_Klima2Vklop;
mind_bool[577]:=DO_Lop1PL1Vklop;
mind_bool[578]:=DO_Lop1PL2Vklop;
mind_bool[579]:=DO_Lop1PL3Vklop;
mind_bool[580]:=DO_Lop3Y1Vklop;
mind_bool[581]:=DO_Lop4Y1Vklop;
mind_bool[582]:=DO_RazE11_10Vklop;
mind_bool[583]:=DO_RazE11_11Vklop;
mind_bool[584]:=DO_RazE11_1Vklop;
mind_bool[585]:=DO_RazE11_2Vklop;
mind_bool[586]:=DO_RazE11_3Vklop;
mind_bool[587]:=DO_RazE11_4Vklop;
mind_bool[588]:=DO_RazE11_5Vklop;
mind_bool[589]:=DO_RazE11_6Vklop;
mind_bool[590]:=DO_RazE11_7Vklop;
mind_bool[591]:=DO_RazE11_8Vklop;
mind_bool[592]:=DO_RazE11_9Vklop;
mind_bool[593]:=DO_RazE12_12Vklop;
mind_bool[594]:=DO_RazE12_13Vklop;
mind_bool[595]:=DO_RazE12_14Vklop;
mind_bool[596]:=DO_RazE12_15Vklop;
mind_bool[597]:=DO_RazE13_16Vklop;
mind_bool[598]:=DO_RazE13_17Vklop;
mind_bool[599]:=DO_RazE13_18Vklop;
mind_bool[600]:=DO_RazE13_19Vklop;
mind_bool[601]:=DO_RazE16_20Vklop;
mind_bool[602]:=DO_RazE16_21Vklop;
mind_bool[603]:=DO_RazE16_22Vklop;
mind_bool[604]:=DO_RazE16_23Vklop;
mind_bool[605]:=DO_RazE16_24Vklop;
mind_bool[606]:=DO_Vent1Vklop;
mind_bool[607]:=DO_Vent2Vklop;
mind_bool[608]:=DO_Vent3Vklop;
mind_bool[609]:=DO_Vent4Vklop;
mind_bool[610]:=DO_Vent5Vklop;
mind_bool[611]:=DO_Vent6Vklop;
mind_bool[612]:=ErrComCirc[1];
mind_bool[613]:=ErrComCirc[2];
mind_bool[614]:=ErrComDanfossHM[1];
mind_bool[615]:=ErrComDanfossHM[2];
mind_bool[616]:=ErrComDanfossHM[3];
mind_bool[617]:=ErrComDanfossHM[4];
mind_bool[618]:=ErrComGrundfos[0];
mind_bool[619]:=ErrComGrundfos[10];
mind_bool[620]:=ErrComGrundfos[11];
mind_bool[621]:=ErrComGrundfos[12];
mind_bool[622]:=ErrComGrundfos[13];
mind_bool[623]:=ErrComGrundfos[14];
mind_bool[624]:=ErrComGrundfos[1];
mind_bool[625]:=ErrComGrundfos[2];
mind_bool[626]:=ErrComGrundfos[3];
mind_bool[627]:=ErrComGrundfos[4];
mind_bool[628]:=ErrComGrundfos[5];
mind_bool[629]:=ErrComGrundfos[6];
mind_bool[630]:=ErrComGrundfos[7];
mind_bool[631]:=ErrComGrundfos[8];
mind_bool[632]:=ErrComGrundfos[9];
mind_bool[633]:=ErrComHladStroj;
mind_bool[634]:=ErrComKlima[1];
mind_bool[635]:=ErrComKlima[2];
mind_bool[636]:=ErrCommScada;
mind_bool[637]:=ErrCommXC100;
mind_bool[638]:=ErrComPanelPLC;
mind_bool[639]:=ErrComPort2;
mind_bool[640]:=ErrComPort3;
mind_bool[641]:=ErrComPort4;
mind_bool[642]:=ErrComToplPost;
mind_bool[643]:=Exp1TlakAlarm;
mind_bool[644]:=Exp2TlakAlarm;
mind_bool[645]:=HladilniStrojOnOff;
mind_bool[646]:=HladStroj.FazeAlarm;
mind_bool[647]:=HladStroj.KompresorOljeAlarm;
mind_bool[648]:=HladStroj.LANcarelAlarm;
mind_bool[649]:=HladStroj.Napaka;
mind_bool[650]:=HladStroj.NizekPritiskAlarm;
mind_bool[651]:=HladStroj.ObratovalneUreOpozorilo;
mind_bool[652]:=HladStroj.OffByAlarms;
mind_bool[653]:=HladStroj.PretokAlarm;
mind_bool[654]:=HladStroj.RemoteOn;
mind_bool[655]:=HladStroj.SenzorAlarm;
mind_bool[656]:=HladStroj.SummerOperation;
mind_bool[657]:=HladStroj.TemperaturaAlarm;
mind_bool[658]:=HladStroj.UnitOn;
mind_bool[659]:=HladStroj.UraAlarm;
mind_bool[660]:=HladStroj.VisokPritiskAlarm;
mind_bool[661]:=HladStroj.VisokPritiskOpozorilo;
mind_bool[662]:=HladStroj.ZmrzalniAlarm;
mind_bool[663]:=HladStrojErrors[10];
mind_bool[664]:=HladStrojErrors[11];
mind_bool[665]:=HladStrojErrors[12];
mind_bool[666]:=HladStrojErrors[13];
mind_bool[667]:=HladStrojErrors[14];
mind_bool[668]:=HladStrojErrors[15];
mind_bool[669]:=HladStrojErrors[16];
mind_bool[670]:=HladStrojErrors[1];
mind_bool[671]:=HladStrojErrors[2];
mind_bool[672]:=HladStrojErrors[3];
mind_bool[673]:=HladStrojErrors[4];
mind_bool[674]:=HladStrojErrors[5];
mind_bool[675]:=HladStrojErrors[6];
mind_bool[676]:=HladStrojErrors[7];
mind_bool[677]:=HladStrojErrors[8];
mind_bool[678]:=HladStrojErrors[9];
mind_bool[679]:=Klima1errors[10];
mind_bool[680]:=Klima1errors[11];
mind_bool[681]:=Klima1errors[12];
mind_bool[682]:=Klima1errors[1];
mind_bool[683]:=Klima1errors[2];
mind_bool[684]:=Klima1errors[3];
mind_bool[685]:=Klima1errors[4];
mind_bool[686]:=Klima1errors[5];
mind_bool[687]:=Klima1errors[6];
mind_bool[688]:=Klima1errors[7];
mind_bool[689]:=Klima1errors[8];
mind_bool[690]:=Klima1errors[9];
mind_bool[691]:=Klima2errors[10];
mind_bool[692]:=Klima2errors[11];
mind_bool[693]:=Klima2errors[12];
mind_bool[694]:=Klima2errors[1];
mind_bool[695]:=Klima2errors[2];
mind_bool[696]:=Klima2errors[3];
mind_bool[697]:=Klima2errors[4];
mind_bool[698]:=Klima2errors[5];
mind_bool[699]:=Klima2errors[6];
mind_bool[700]:=Klima2errors[7];
mind_bool[701]:=Klima2errors[8];
mind_bool[702]:=Klima2errors[9];
mind_bool[703]:=Klima[1].CrpalkaGrelnika;
mind_bool[704]:=Klima[1].DelovanjeVentH1;
mind_bool[705]:=Klima[1].DelovanjeVentH2;
mind_bool[706]:=Klima[1].Deluje;
mind_bool[707]:=Klima[1].FilterError;
mind_bool[708]:=Klima[1].Napaka;
mind_bool[709]:=Klima[1].NapakaPriPretokuZraka;
mind_bool[710]:=Klima[1].OkvaraRototerma;
mind_bool[711]:=Klima[1].OkvaraVlazilne;
mind_bool[712]:=Klima[1].PozarError;
mind_bool[713]:=Klima[1].PozarniAlarm;
mind_bool[714]:=Klima[1].PreobremenitevMotCrpGr;
mind_bool[715]:=Klima[1].PreobremenitevMotVent;
mind_bool[716]:=Klima[1].ProtizmrzAktivna;
mind_bool[717]:=Klima[1].SkupniAlarmA;
mind_bool[718]:=Klima[1].SkupniAlarmB;
mind_bool[719]:=Klima[1].VklopRegulacije;
mind_bool[720]:=Klima[1].ZamasenFilter;
mind_bool[721]:=Klima[2].CrpalkaGrelnika;
mind_bool[722]:=Klima[2].DelovanjeVentH1;
mind_bool[723]:=Klima[2].DelovanjeVentH2;
mind_bool[724]:=Klima[2].Deluje;
mind_bool[725]:=Klima[2].FilterError;
mind_bool[726]:=Klima[2].Napaka;
mind_bool[727]:=Klima[2].NapakaPriPretokuZraka;
mind_bool[728]:=Klima[2].OkvaraRototerma;
mind_bool[729]:=Klima[2].OkvaraVlazilne;
mind_bool[730]:=Klima[2].PozarError;
mind_bool[731]:=Klima[2].PozarniAlarm;
mind_bool[732]:=Klima[2].PreobremenitevMotCrpGr;
mind_bool[733]:=Klima[2].PreobremenitevMotVent;
mind_bool[734]:=Klima[2].ProtizmrzAktivna;
mind_bool[735]:=Klima[2].SkupniAlarmA;
mind_bool[736]:=Klima[2].SkupniAlarmB;
mind_bool[737]:=Klima[2].VklopRegulacije;
mind_bool[738]:=Klima[2].ZamasenFilter;
mind_bool[739]:=KondEnotaOnOff[1];
mind_bool[740]:=KondEnotaOnOff[2];
mind_bool[741]:=KondEnotaOnOff[3];
mind_bool[742]:=KontRezervaOnOff[1];
mind_bool[743]:=KontRezervaOnOff[2];
mind_bool[744]:=KontRezervaOnOff[3];
mind_bool[745]:=NapakaSenzorAI[10];
mind_bool[746]:=NapakaSenzorAI[11];
mind_bool[747]:=NapakaSenzorAI[12];
mind_bool[748]:=NapakaSenzorAI[13];
mind_bool[749]:=NapakaSenzorAI[14];
mind_bool[750]:=NapakaSenzorAI[15];
mind_bool[751]:=NapakaSenzorAI[16];
mind_bool[752]:=NapakaSenzorAI[17];
mind_bool[753]:=NapakaSenzorAI[18];
mind_bool[754]:=NapakaSenzorAI[19];
mind_bool[755]:=NapakaSenzorAI[1];
mind_bool[756]:=NapakaSenzorAI[20];
mind_bool[757]:=NapakaSenzorAI[21];
mind_bool[758]:=NapakaSenzorAI[22];
mind_bool[759]:=NapakaSenzorAI[23];
mind_bool[760]:=NapakaSenzorAI[24];
mind_bool[761]:=NapakaSenzorAI[25];
mind_bool[762]:=NapakaSenzorAI[26];
mind_bool[763]:=NapakaSenzorAI[27];
mind_bool[764]:=NapakaSenzorAI[28];
mind_bool[765]:=NapakaSenzorAI[29];
mind_bool[766]:=NapakaSenzorAI[2];
mind_bool[767]:=NapakaSenzorAI[30];
mind_bool[768]:=NapakaSenzorAI[31];
mind_bool[769]:=NapakaSenzorAI[32];
mind_bool[770]:=NapakaSenzorAI[33];
mind_bool[771]:=NapakaSenzorAI[34];
mind_bool[772]:=NapakaSenzorAI[35];
mind_bool[773]:=NapakaSenzorAI[36];
mind_bool[774]:=NapakaSenzorAI[37];
mind_bool[775]:=NapakaSenzorAI[38];
mind_bool[776]:=NapakaSenzorAI[39];
mind_bool[777]:=NapakaSenzorAI[3];
mind_bool[778]:=NapakaSenzorAI[40];
mind_bool[779]:=NapakaSenzorAI[4];
mind_bool[780]:=NapakaSenzorAI[5];
mind_bool[781]:=NapakaSenzorAI[6];
mind_bool[782]:=NapakaSenzorAI[7];
mind_bool[783]:=NapakaSenzorAI[8];
mind_bool[784]:=NapakaSenzorAI[9];
mind_bool[785]:=NapakaSenzorHIA[1];
mind_bool[786]:=NapakaSenzorHIA[2];
mind_bool[787]:=NapakaSenzorHIA[3];
mind_bool[788]:=NapakaSenzorHIA[4];
mind_bool[789]:=NapakaSenzorTIA[1];
mind_bool[790]:=NapakaSenzorTIA[2];
mind_bool[791]:=NapakaSenzorTIA[3];
mind_bool[792]:=NapakaSenzorTIA[4];
mind_bool[793]:=PozarnaLoputaOnOffError[1];
mind_bool[794]:=PozarnaLoputaOnOffError[2];
mind_bool[795]:=PozarnaLoputaOnOffError[3];
mind_bool[796]:=PozarnaLoputaOnOffError[4];
mind_bool[797]:=PozarnaLoputaOnOffError[5];
mind_bool[798]:=PozarnaLoputOnOff[1];
mind_bool[799]:=PozarnaLoputOnOff[2];
mind_bool[800]:=PozarnaLoputOnOff[3];
mind_bool[801]:=PozarnaLoputOnOff[4];
mind_bool[802]:=PozarnaLoputOnOff[5];
mind_bool[803]:=PozarniAlarm;
mind_bool[804]:=PrenosUrnika[10];
mind_bool[805]:=PrenosUrnika[11];
mind_bool[806]:=PrenosUrnika[12];
mind_bool[807]:=PrenosUrnika[13];
mind_bool[808]:=PrenosUrnika[14];
mind_bool[809]:=PrenosUrnika[15];
mind_bool[810]:=PrenosUrnika[16];
mind_bool[811]:=PrenosUrnika[17];
mind_bool[812]:=PrenosUrnika[18];
mind_bool[813]:=PrenosUrnika[19];
mind_bool[814]:=PrenosUrnika[1];
mind_bool[815]:=PrenosUrnika[20];
mind_bool[816]:=PrenosUrnika[21];
mind_bool[817]:=PrenosUrnika[22];
mind_bool[818]:=PrenosUrnika[23];
mind_bool[819]:=PrenosUrnika[24];
mind_bool[820]:=PrenosUrnika[25];
mind_bool[821]:=PrenosUrnika[2];
mind_bool[822]:=PrenosUrnika[3];
mind_bool[823]:=PrenosUrnika[4];
mind_bool[824]:=PrenosUrnika[5];
mind_bool[825]:=PrenosUrnika[6];
mind_bool[826]:=PrenosUrnika[7];
mind_bool[827]:=PrenosUrnika[8];
mind_bool[828]:=PrenosUrnika[9];
mind_bool[829]:=RazsvetljavaOnOff[10];
mind_bool[830]:=RazsvetljavaOnOff[11];
mind_bool[831]:=RazsvetljavaOnOff[12];
mind_bool[832]:=RazsvetljavaOnOff[13];
mind_bool[833]:=RazsvetljavaOnOff[14];
mind_bool[834]:=RazsvetljavaOnOff[15];
mind_bool[835]:=RazsvetljavaOnOff[16];
mind_bool[836]:=RazsvetljavaOnOff[17];
mind_bool[837]:=RazsvetljavaOnOff[18];
mind_bool[838]:=RazsvetljavaOnOff[19];
mind_bool[839]:=RazsvetljavaOnOff[1];
mind_bool[840]:=RazsvetljavaOnOff[20];
mind_bool[841]:=RazsvetljavaOnOff[21];
mind_bool[842]:=RazsvetljavaOnOff[22];
mind_bool[843]:=RazsvetljavaOnOff[23];
mind_bool[844]:=RazsvetljavaOnOff[24];
mind_bool[845]:=RazsvetljavaOnOff[25];
mind_bool[846]:=RazsvetljavaOnOff[2];
mind_bool[847]:=RazsvetljavaOnOff[3];
mind_bool[848]:=RazsvetljavaOnOff[4];
mind_bool[849]:=RazsvetljavaOnOff[5];
mind_bool[850]:=RazsvetljavaOnOff[6];
mind_bool[851]:=RazsvetljavaOnOff[7];
mind_bool[852]:=RazsvetljavaOnOff[8];
mind_bool[853]:=RazsvetljavaOnOff[9];
mind_bool[854]:=RazsvetljavaRocno;
mind_bool[855]:=SetDateTime;
mind_bool[856]:=SetDateTimeDemand;
mind_bool[857]:=SetDateTimeError;
mind_bool[858]:=SetDateTimeFinished;
mind_bool[859]:=SetRemoteOnOff[1];
mind_bool[860]:=SetRemoteOnOff[2];
mind_bool[861]:=SlabaBaterijaPLC_A1;
mind_bool[862]:=SlabaBaterijaPLC_A100;
mind_bool[863]:=SO_BojlerTE1Vklop;
mind_bool[864]:=SO_CrpHM1Vklop;
mind_bool[865]:=SO_CrpHM2Vklop;
mind_bool[866]:=SO_CrpHM3Vklop;
mind_bool[867]:=SO_CrpHM4Vklop;
mind_bool[868]:=SO_CrpMN1Vklop;
mind_bool[869]:=SO_CrpTM11Vklop;
mind_bool[870]:=SO_HladStrVklop;
mind_bool[871]:=SO_KE1Vklop;
mind_bool[872]:=SO_KE2Vklop;
mind_bool[873]:=SO_KE3Vklop;
mind_bool[874]:=SO_rezerva1_3;
mind_bool[875]:=SO_rezerva1_4;
mind_bool[876]:=SO_rezerva1_5;
mind_bool[877]:=SO_Vent1Vklop;
mind_bool[878]:=SO_Vent2Vklop;
mind_bool[879]:=SO_Vent3Vklop;
mind_bool[880]:=SO_Vent4Vklop;
mind_bool[881]:=SO_Vent5Vklop;
mind_bool[882]:=SO_Vent6Vklop;
mind_bool[883]:=TEgrelecNaTemp;
mind_bool[884]:=TEgrelecTempVklop;
mind_bool[885]:=TempTSprevisoka;
mind_bool[886]:=ToplPost.HKcrpalkaON;
mind_bool[887]:=ToplPost.HKcrpDnevniRezim;
mind_bool[888]:=ToplPost.HKcrpNocniRezim;
mind_bool[889]:=ToplPost.HKrocniRezim;
mind_bool[890]:=ToplPost.SkupnaNapaka;
mind_bool[891]:=ToplPost.TVcrpalkaON;
mind_bool[892]:=ToplPost.TVrocniRezim;
mind_bool[893]:=ToplPostErrors[0];
mind_bool[894]:=ToplPostErrors[10];
mind_bool[895]:=ToplPostErrors[11];
mind_bool[896]:=ToplPostErrors[12];
mind_bool[897]:=ToplPostErrors[13];
mind_bool[898]:=ToplPostErrors[14];
mind_bool[899]:=ToplPostErrors[15];
mind_bool[900]:=ToplPostErrors[16];
mind_bool[901]:=ToplPostErrors[17];
mind_bool[902]:=ToplPostErrors[1];
mind_bool[903]:=ToplPostErrors[2];
mind_bool[904]:=ToplPostErrors[3];
mind_bool[905]:=ToplPostErrors[4];
mind_bool[906]:=ToplPostErrors[5];
mind_bool[907]:=ToplPostErrors[6];
mind_bool[908]:=ToplPostErrors[7];
mind_bool[909]:=ToplPostErrors[8];
mind_bool[910]:=ToplPostErrors[9];
mind_bool[911]:=TYventilNaTemp[1];
mind_bool[912]:=TYventilNaTemp[2];
mind_bool[913]:=TYventilNaTemp[3];
mind_bool[914]:=TYventilNaTemp[4];
mind_bool[915]:=UserLoggedIn;
mind_bool[916]:=VentilatorOnOff[1];
mind_bool[917]:=VentilatorOnOff[2];
mind_bool[918]:=VentilatorOnOff[3];
mind_bool[919]:=VentilatorOnOff[4];
mind_bool[920]:=VentilatorOnOff[5];
mind_bool[921]:=VentilatorOnOff[6];
mind_bool[922]:=VklopSCFBNapaka[10];
mind_bool[923]:=VklopSCFBNapaka[11];
mind_bool[924]:=VklopSCFBNapaka[12];
mind_bool[925]:=VklopSCFBNapaka[13];
mind_bool[926]:=VklopSCFBNapaka[14];
mind_bool[927]:=VklopSCFBNapaka[15];
mind_bool[928]:=VklopSCFBNapaka[16];
mind_bool[929]:=VklopSCFBNapaka[17];
mind_bool[930]:=VklopSCFBNapaka[18];
mind_bool[931]:=VklopSCFBNapaka[19];
mind_bool[932]:=VklopSCFBNapaka[1];
mind_bool[933]:=VklopSCFBNapaka[20];
mind_bool[934]:=VklopSCFBNapaka[21];
mind_bool[935]:=VklopSCFBNapaka[22];
mind_bool[936]:=VklopSCFBNapaka[23];
mind_bool[937]:=VklopSCFBNapaka[24];
mind_bool[938]:=VklopSCFBNapaka[25];
mind_bool[939]:=VklopSCFBNapaka[2];
mind_bool[940]:=VklopSCFBNapaka[3];
mind_bool[941]:=VklopSCFBNapaka[4];
mind_bool[942]:=VklopSCFBNapaka[5];
mind_bool[943]:=VklopSCFBNapaka[6];
mind_bool[944]:=VklopSCFBNapaka[7];
mind_bool[945]:=VklopSCFBNapaka[8];
mind_bool[946]:=VklopSCFBNapaka[9];
mind_bool[947]:=XVH_AlarmOn;
mind_bool[948]:=XVH_IzklopVsehLuci;
mind_bool[949]:=XVH_VklopVsehLuci;
mind_bool[950]:=PrenasanjeUrnikovAktivno;
mind_bool[951]:=PrenasanjeUrnikovAktivno1;
mind_bool[952]:=CrpalkeGrfsGal.AlarmAktiven;
mind_bool[953]:=CrpalkeGrfsGal.Deluje;
mind_bool[954]:=CrpalkeGrfsGal.LocalMode;
mind_bool[955]:=CrpalkeGrfsGal.RemoteON;
mind_bool[956]:=CrpalkeGrfsGal.Reset2handkWhValues;
mind_bool[957]:=CrpalkeGrfsGal.ResetAlarm;
mind_bool[958]:=CrpalkeGrfsGal.ResetAlarmLog;
mind_bool[959]:=CrpalkeGrfsGal.ResetDevice;
mind_bool[960]:=CrpalkeGrfsGal.SetAutomatic;
mind_bool[961]:=CrpalkeGrfsGal.SetConstFreqMode;
mind_bool[962]:=CrpalkeGrfsGal.SetConstPress;
mind_bool[963]:=CrpalkeGrfsGal.SetLocalMode;
mind_bool[964]:=CrpalkeGrfsGal.SetMaxRunMode;
mind_bool[965]:=CrpalkeGrfsGal.SetMinRunMode;
mind_bool[966]:=CrpalkeGrfsGal.SetPropPress;
mind_bool[967]:=CrpalkeGrfsGal.SetReference;
mind_bool[968]:=CrpalkeGrfsGal.SetRemoteMode;
mind_bool[969]:=CrpalkeGrfsGal.SetTwinModeAlt;
mind_bool[970]:=CrpalkeGrfsGal.SetTwinModeSpare;
mind_bool[971]:=CrpalkeGrfsGal.SetTwinModeSync;
mind_bool[972]:=CrpalkeGrfsGal.Start;
mind_bool[973]:=CrpalkeGrfsGal.Stop;
mind_bool[974]:=DI_rezerva10_2;
mind_bool[975]:=DI_rezerva10_7;
mind_bool[976]:=DI_rezerva11_4;
mind_bool[977]:=DI_rezerva14_0;
mind_bool[978]:=DI_rezerva14_2;
mind_bool[979]:=DI_rezerva14_3;
mind_bool[980]:=DI_rezerva14_4;
mind_bool[981]:=DI_rezerva14_5;
mind_bool[982]:=DI_rezerva14_7;
mind_bool[983]:=DI_rezerva2_4;
mind_bool[984]:=DI_rezerva3_5;
mind_bool[985]:=DIN_AkumTopVodeAUTO;
mind_bool[986]:=DIN_CrpHM1AUTO;
mind_bool[987]:=DIN_CrpHM1kontON;
mind_bool[988]:=DIN_CrpHM2AUTO;
mind_bool[989]:=DIN_CrpHM2kontON;
mind_bool[990]:=DIN_CrpHM3AUTO;
mind_bool[991]:=DIN_CrpHM3kontON;
mind_bool[992]:=DIN_CrpHM4AUTO;
mind_bool[993]:=DIN_CrpHM4kontON;
mind_bool[994]:=DIN_CrpHM5AUTO;
mind_bool[995]:=DIN_CrpHM6AUTO;
mind_bool[996]:=DIN_CrpHM7AUTO;
mind_bool[997]:=DIN_CrpHM8AUTO;
mind_bool[998]:=DIN_CrpMN1AUTO;
mind_bool[999]:=DIN_CrpMN1kontON;
mind_bool[1000]:=DIN_CrpTM10AUTO;
mind_bool[1001]:=DIN_CrpTM11TM12AUTO;
mind_bool[1002]:=DIN_CrpTM11TM12kontON;
mind_bool[1003]:=DIN_CrpTM1AUTO;
mind_bool[1004]:=DIN_CrpTM2AUTO;
mind_bool[1005]:=DIN_CrpTM3AUTO;
mind_bool[1006]:=DIN_CrpTM4AUTO;
mind_bool[1007]:=DIN_CrpTM5AUTO;
mind_bool[1008]:=DIN_CrpTM6AUTO;
mind_bool[1009]:=DIN_CrpTM7AUTO;
mind_bool[1010]:=DIN_CrpTM8AUTO;
mind_bool[1011]:=DIN_CrpTM9AUTO;
mind_bool[1012]:=DIN_GlStikaloDieselON;
mind_bool[1013]:=DIN_GlStikaloMrezaON;
mind_bool[1014]:=DIN_GlStikaloUpsON;
mind_bool[1015]:=DIN_HladStAUTO;
mind_bool[1016]:=DIN_Kond1AUTO;
mind_bool[1017]:=DIN_Kond2AUTO;
mind_bool[1018]:=DIN_Kond3AUTO;
mind_bool[1019]:=DIN_Vent1Auto;
mind_bool[1020]:=DIN_Vent1kontON;
mind_bool[1021]:=DIN_Vent2Auto;
mind_bool[1022]:=DIN_Vent2kontON;
mind_bool[1023]:=DIN_Vent3Auto;
mind_bool[1024]:=DIN_Vent3kontON;
mind_bool[1025]:=DIN_Vent4Auto;
mind_bool[1026]:=DIN_Vent4kontON;
mind_bool[1027]:=DIN_Vent5Auto;
mind_bool[1028]:=DIN_Vent5kontON;
mind_bool[1029]:=DIN_Vent6Auto;
mind_bool[1030]:=DIN_Vent6kontON;
mind_bool[1031]:=DO_rezerva0_2;
mind_bool[1032]:=DO_rezerva0_3;
mind_bool[1033]:=DO_rezerva0_4;
mind_bool[1034]:=DO_rezerva0_5;
mind_bool[1035]:=DO_rezerva1_3;
mind_bool[1036]:=DO_rezerva1_4;
mind_bool[1037]:=DO_rezerva1_5;
mind_bool[1038]:=DO_rezerva3_4;
mind_bool[1039]:=DO_rezerva3_6;
mind_bool[1040]:=DO_rezerva4_0;
mind_bool[1041]:=PrenosUrnika[26];
mind_bool[1042]:=PrenosUrnika[27];
mind_bool[1043]:=PrenosUrnika[28];
mind_bool[1044]:=PrenosUrnika[29];
mind_bool[1045]:=PrenosUrnika[30];
mind_bool[1046]:=PrenosUrnika[31];
mind_bool[1047]:=PrenosUrnika[32];
mind_bool[1048]:=PrenosUrnika[33];
mind_bool[1049]:=PrenosUrnika[34];
mind_bool[1050]:=PrenosUrnika[35];
mind_bool[1051]:=PrenosUrnika[36];
mind_bool[1052]:=PrenosUrnika[37];
mind_bool[1053]:=PrenosUrnika[38];
mind_bool[1054]:=PrenosUrnika[39];
mind_bool[1055]:=PrenosUrnika[40];
mind_bool[1056]:=PrenosUrnika[41];
mind_bool[1057]:=PrenosUrnika[42];
mind_bool[1058]:=PrenosUrnika[43];
mind_bool[1059]:=PrenosUrnika[44];
mind_bool[1060]:=PrenosUrnika[45];
mind_bool[1061]:=PrenosUrnika[46];
mind_bool[1062]:=PrenosUrnika[47];
mind_bool[1063]:=PrenosUrnika[48];
mind_bool[1064]:=PrenosUrnika[49];
mind_bool[1065]:=PrenosUrnika[50];
mind_bool[1066]:=PrenosUrnika[51];
mind_bool[1067]:=PrenosUrnika[52];
mind_bool[1068]:=PrenosUrnika[53];
mind_bool[1069]:=PrenosUrnika[54];
mind_bool[1070]:=PrenosUrnika[55];
mind_bool[1071]:=PrenosUrnika[56];
mind_bool[1072]:=PrenosUrnika[57];
mind_bool[1073]:=PrenosUrnika[58];
mind_bool[1074]:=PrenosUrnika[59];
mind_bool[1075]:=PrenosUrnika[60];
mind_bool[1076]:=PrenosUrnika[61];
mind_bool[1077]:=PrenosUrnika[62];
mind_bool[1078]:=PrenosUrnika[63];
mind_bool[1079]:=PrenosUrnika[64];
mind_bool[1080]:=PrenosUrnika[65];
mind_bool[1081]:=PrenosUrnika[66];
mind_bool[1082]:=PrenosUrnika[67];
mind_bool[1083]:=PrenosUrnika[68];
mind_bool[1084]:=PrenosUrnika[69];
mind_bool[1085]:=PrenosUrnika[70];
mind_bool[1086]:=PrenosUrnika[71];
mind_bool[1087]:=PrenosUrnika[72];
mind_bool[1088]:=PrenosUrnika[73];
mind_bool[1089]:=PrenosUrnika[74];
mind_bool[1090]:=PrenosUrnika[75];
mind_bool[1091]:=PrenosUrnika[76];
mind_bool[1092]:=PrenosUrnika[77];
mind_bool[1093]:=PrenosUrnika[78];
mind_bool[1094]:=PrenosUrnika[79];
mind_bool[1095]:=PrenosUrnika[80];
mind_bool[1096]:=PrenosUrnika[81];
mind_bool[1097]:=PrenosUrnika[82];
mind_bool[1098]:=PrenosUrnika[83];
mind_bool[1099]:=PrenosUrnika[84];
mind_bool[1100]:=PrenosUrnika[85];
mind_bool[1101]:=PrenosUrnika[86];
mind_bool[1102]:=PrenosUrnika[87];
mind_bool[1103]:=PrenosUrnika[88];
mind_bool[1104]:=PrenosUrnika[89];
mind_bool[1105]:=PrenosUrnika[90];
mind_bool[1106]:=PrenosUrnika[91];
mind_bool[1107]:=PrenosUrnika[92];
mind_bool[1108]:=PrenosUrnika[93];
mind_bool[1109]:=PrenosUrnika[94];
mind_bool[1110]:=PrenosUrnika[95];
mind_bool[1111]:=PrenosUrnika[96];
mind_bool[1112]:=RazsvRocnoEnaLuc[10];
mind_bool[1113]:=RazsvRocnoEnaLuc[11];
mind_bool[1114]:=RazsvRocnoEnaLuc[12];
mind_bool[1115]:=RazsvRocnoEnaLuc[13];
mind_bool[1116]:=RazsvRocnoEnaLuc[14];
mind_bool[1117]:=RazsvRocnoEnaLuc[15];
mind_bool[1118]:=RazsvRocnoEnaLuc[16];
mind_bool[1119]:=RazsvRocnoEnaLuc[17];
mind_bool[1120]:=RazsvRocnoEnaLuc[18];
mind_bool[1121]:=RazsvRocnoEnaLuc[19];
mind_bool[1122]:=RazsvRocnoEnaLuc[1];
mind_bool[1123]:=RazsvRocnoEnaLuc[20];
mind_bool[1124]:=RazsvRocnoEnaLuc[21];
mind_bool[1125]:=RazsvRocnoEnaLuc[22];
mind_bool[1126]:=RazsvRocnoEnaLuc[23];
mind_bool[1127]:=RazsvRocnoEnaLuc[24];
mind_bool[1128]:=RazsvRocnoEnaLuc[25];
mind_bool[1129]:=RazsvRocnoEnaLuc[2];
mind_bool[1130]:=RazsvRocnoEnaLuc[3];
mind_bool[1131]:=RazsvRocnoEnaLuc[4];
mind_bool[1132]:=RazsvRocnoEnaLuc[5];
mind_bool[1133]:=RazsvRocnoEnaLuc[6];
mind_bool[1134]:=RazsvRocnoEnaLuc[7];
mind_bool[1135]:=RazsvRocnoEnaLuc[8];
mind_bool[1136]:=RazsvRocnoEnaLuc[9];
mind_bool[1137]:=XVH_CrpalkaGrfsPair;
mind_bool[1138]:=XVH_CrpGrfsCommErr;
mind_bool[1139]:=XVH_CrpGrfsON[10];
mind_bool[1140]:=XVH_CrpGrfsON[11];
mind_bool[1141]:=XVH_CrpGrfsON[12];
mind_bool[1142]:=XVH_CrpGrfsON[13];
mind_bool[1143]:=XVH_CrpGrfsON[14];
mind_bool[1144]:=XVH_CrpGrfsON[1];
mind_bool[1145]:=XVH_CrpGrfsON[2];
mind_bool[1146]:=XVH_CrpGrfsON[3];
mind_bool[1147]:=XVH_CrpGrfsON[4];
mind_bool[1148]:=XVH_CrpGrfsON[5];
mind_bool[1149]:=XVH_CrpGrfsON[6];
mind_bool[1150]:=XVH_CrpGrfsON[7];
mind_bool[1151]:=XVH_CrpGrfsON[8];
mind_bool[1152]:=XVH_CrpGrfsON[9];
mind_bool[1153]:=XVH_CrpGrfsPIDreset;
mind_bool[1154]:=XVH_CrpGrfsVisibleData[10];
mind_bool[1155]:=XVH_CrpGrfsVisibleData[11];
mind_bool[1156]:=XVH_CrpGrfsVisibleData[12];
mind_bool[1157]:=XVH_CrpGrfsVisibleData[13];
mind_bool[1158]:=XVH_CrpGrfsVisibleData[14];
mind_bool[1159]:=XVH_CrpGrfsVisibleData[15];
mind_bool[1160]:=XVH_CrpGrfsVisibleData[16];
mind_bool[1161]:=XVH_CrpGrfsVisibleData[1];
mind_bool[1162]:=XVH_CrpGrfsVisibleData[2];
mind_bool[1163]:=XVH_CrpGrfsVisibleData[3];
mind_bool[1164]:=XVH_CrpGrfsVisibleData[4];
mind_bool[1165]:=XVH_CrpGrfsVisibleData[5];
mind_bool[1166]:=XVH_CrpGrfsVisibleData[6];
mind_bool[1167]:=XVH_CrpGrfsVisibleData[7];
mind_bool[1168]:=XVH_CrpGrfsVisibleData[8];
mind_bool[1169]:=XVH_CrpGrfsVisibleData[9];
mind_bool[1170]:=XVH_CrpGrundfosNaCas;
mind_bool[1171]:=XVH_CrpGrundfosNaTlak;
mind_bool[1172]:=XVH_CrpGrundfosON;
mind_bool[1173]:=XVH_CrpGrundfosResetAlarm;
mind_bool[1174]:=XVH_CrpGrundfosResetAlarmLog;
mind_bool[1175]:=XVH_CrpGrundfosSetRef;
mind_bool[1176]:=XVH_RazsvOnOff;
mind_bool[1177]:=XVH_setCircNum[1];
mind_bool[1178]:=XVH_setCircNum[2];
mind_bool[1179]:=XVH_setCircNum[3];
mind_bool[1180]:=XVH_setCircNum[4];
mind_bool[1181]:=XVH_setCircNum[5];
mind_bool[1182]:=XVH_UrnikNalozi;
mind_bool[1183]:=XVH_UrnikNonStop;
mind_bool[1184]:=XVH_UrnikPotrdiVpis;
mind_bool[1185]:=XVH_UrnikPreklicVpisa;
mind_bool[1186]:=XVH_UrnikShrani;
mind_bool[1187]:=XVH_VpisUrnika;
mind_bool[1188]:=ErrCommScada2;
mind_bool[1189]:=ComSCADA2;
mind_bool[1190]:=ComSCADA3;
mind_bool[1191]:=Circ_Vpis_Dnevne_energija_scada1;
mind_bool[1192]:=Circ_Vpis_Dnevne_energija_scada2;
mind_bool[1193]:=Circ_Vpis_Tedenska_energija_scada1;
mind_bool[1194]:=Circ_Vpis_Tedenska_energija_scada2;
mind_bool[1195]:=Circ_Vpis_Mesecna_energija_scada1;
mind_bool[1196]:=Circ_Vpis_Mesecna_energija_scada2;
(*Branje INT*)
(**)
mind[0]:=CrpalkeDnfs[1].PreklopkaMode;
mind[1]:=CrpalkeDnfs[1].StarterStatus0do7;
mind[2]:=CrpalkeDnfs[1].StatusCrpalke;
mind[3]:=CrpalkeDnfs[1].StatusKontaktor;
mind[4]:=CrpalkeDnfs[2].PreklopkaMode;
mind[5]:=CrpalkeDnfs[2].StarterStatus0do7;
mind[6]:=CrpalkeDnfs[2].StatusCrpalke;
mind[7]:=CrpalkeDnfs[2].StatusKontaktor;
mind[8]:=CrpalkeDnfs[3].PreklopkaMode;
mind[9]:=CrpalkeDnfs[3].StarterStatus0do7;
mind[10]:=CrpalkeDnfs[3].StatusCrpalke;
mind[11]:=CrpalkeDnfs[3].StatusKontaktor;
mind[12]:=CrpalkeDnfs[4].PreklopkaMode;
mind[13]:=CrpalkeDnfs[4].StarterStatus0do7;
mind[14]:=CrpalkeDnfs[4].StatusCrpalke;
mind[15]:=CrpalkeDnfs[4].StatusKontaktor;
mind[16]:=CrpalkeGrfs[10].AlarmActiveCode;
mind[17]:=CrpalkeGrfs[10].AlarmCodeLog1;
mind[18]:=CrpalkeGrfs[10].AlarmCodeLog2;
mind[19]:=CrpalkeGrfs[10].AlarmCodeLog3;
mind[20]:=CrpalkeGrfs[10].AlarmCodeLog4;
mind[21]:=CrpalkeGrfs[10].AlarmCodeLog5;
mind[22]:=CrpalkeGrfs[10].AlarmGroupXVH[0];
mind[23]:=CrpalkeGrfs[10].AlarmGroupXVH[10];
mind[24]:=CrpalkeGrfs[10].AlarmGroupXVH[11];
mind[25]:=CrpalkeGrfs[10].AlarmGroupXVH[12];
mind[26]:=CrpalkeGrfs[10].AlarmGroupXVH[13];
mind[27]:=CrpalkeGrfs[10].AlarmGroupXVH[14];
mind[28]:=CrpalkeGrfs[10].AlarmGroupXVH[15];
mind[29]:=CrpalkeGrfs[10].AlarmGroupXVH[16];
mind[30]:=CrpalkeGrfs[10].AlarmGroupXVH[1];
mind[31]:=CrpalkeGrfs[10].AlarmGroupXVH[2];
mind[32]:=CrpalkeGrfs[10].AlarmGroupXVH[3];
mind[33]:=CrpalkeGrfs[10].AlarmGroupXVH[4];
mind[34]:=CrpalkeGrfs[10].AlarmGroupXVH[5];
mind[35]:=CrpalkeGrfs[10].AlarmGroupXVH[6];
mind[36]:=CrpalkeGrfs[10].AlarmGroupXVH[7];
mind[37]:=CrpalkeGrfs[10].AlarmGroupXVH[8];
mind[38]:=CrpalkeGrfs[10].AlarmGroupXVH[9];
mind[39]:=CrpalkeGrfs[10].AlarmQSD1;
mind[40]:=CrpalkeGrfs[10].AlarmQSD2;
mind[41]:=CrpalkeGrfs[10].AlarmStart1;
mind[42]:=CrpalkeGrfs[10].AlarmStart2;
mind[43]:=CrpalkeGrfs[10].AlarmStop1;
mind[44]:=CrpalkeGrfs[10].AlarmStop2;
mind[45]:=CrpalkeGrfs[10].AlarmStop3;
mind[46]:=CrpalkeGrfs[10].AlarmSurv1;
mind[47]:=CrpalkeGrfs[10].AlarmSurv2;
mind[48]:=CrpalkeGrfs[10].ControlSource;
mind[49]:=CrpalkeGrfs[10].ExternInputSetup;
mind[50]:=CrpalkeGrfs[10].ExternInputsStatus;
mind[51]:=CrpalkeGrfs[10].LocalSetupMode1;
mind[52]:=CrpalkeGrfs[10].PreklopkaMode;
mind[53]:=CrpalkeGrfs[10].Relay1setup;
mind[54]:=CrpalkeGrfs[10].RemoteSetupMode1;
mind[55]:=CrpalkeGrfs[10].StatusCrpalke;
mind[56]:=CrpalkeGrfs[10].StatusMode1;
mind[57]:=CrpalkeGrfs[10].StatusMode1co;
mind[58]:=CrpalkeGrfs[10].StatusMode1op;
mind[59]:=CrpalkeGrfs[10].StatusMode2;
mind[60]:=CrpalkeGrfs[10].StatusMode3;
mind[61]:=CrpalkeGrfs[11].AlarmActiveCode;
mind[62]:=CrpalkeGrfs[11].AlarmCodeLog1;
mind[63]:=CrpalkeGrfs[11].AlarmCodeLog2;
mind[64]:=CrpalkeGrfs[11].AlarmCodeLog3;
mind[65]:=CrpalkeGrfs[11].AlarmCodeLog4;
mind[66]:=CrpalkeGrfs[11].AlarmCodeLog5;
mind[67]:=CrpalkeGrfs[11].AlarmGroupXVH[0];
mind[68]:=CrpalkeGrfs[11].AlarmGroupXVH[10];
mind[69]:=CrpalkeGrfs[11].AlarmGroupXVH[11];
mind[70]:=CrpalkeGrfs[11].AlarmGroupXVH[12];
mind[71]:=CrpalkeGrfs[11].AlarmGroupXVH[13];
mind[72]:=CrpalkeGrfs[11].AlarmGroupXVH[14];
mind[73]:=CrpalkeGrfs[11].AlarmGroupXVH[15];
mind[74]:=CrpalkeGrfs[11].AlarmGroupXVH[16];
mind[75]:=CrpalkeGrfs[11].AlarmGroupXVH[1];
mind[76]:=CrpalkeGrfs[11].AlarmGroupXVH[2];
mind[77]:=CrpalkeGrfs[11].AlarmGroupXVH[3];
mind[78]:=CrpalkeGrfs[11].AlarmGroupXVH[4];
mind[79]:=CrpalkeGrfs[11].AlarmGroupXVH[5];
mind[80]:=CrpalkeGrfs[11].AlarmGroupXVH[6];
mind[81]:=CrpalkeGrfs[11].AlarmGroupXVH[7];
mind[82]:=CrpalkeGrfs[11].AlarmGroupXVH[8];
mind[83]:=CrpalkeGrfs[11].AlarmGroupXVH[9];
mind[84]:=CrpalkeGrfs[11].AlarmQSD1;
mind[85]:=CrpalkeGrfs[11].AlarmQSD2;
mind[86]:=CrpalkeGrfs[11].AlarmStart1;
mind[87]:=CrpalkeGrfs[11].AlarmStart2;
mind[88]:=CrpalkeGrfs[11].AlarmStop1;
mind[89]:=CrpalkeGrfs[11].AlarmStop2;
mind[90]:=CrpalkeGrfs[11].AlarmStop3;
mind[91]:=CrpalkeGrfs[11].AlarmSurv1;
mind[92]:=CrpalkeGrfs[11].AlarmSurv2;
mind[93]:=CrpalkeGrfs[11].ControlSource;
mind[94]:=CrpalkeGrfs[11].ExternInputSetup;
mind[95]:=CrpalkeGrfs[11].ExternInputsStatus;
mind[96]:=CrpalkeGrfs[11].LocalSetupMode1;
mind[97]:=CrpalkeGrfs[11].PreklopkaMode;
mind[98]:=CrpalkeGrfs[11].Relay1setup;
mind[99]:=CrpalkeGrfs[11].RemoteSetupMode1;
mind[100]:=CrpalkeGrfs[11].StatusCrpalke;
mind[101]:=CrpalkeGrfs[11].StatusMode1;
mind[102]:=CrpalkeGrfs[11].StatusMode1co;
mind[103]:=CrpalkeGrfs[11].StatusMode1op;
mind[104]:=CrpalkeGrfs[11].StatusMode2;
mind[105]:=CrpalkeGrfs[11].StatusMode3;
mind[106]:=CrpalkeGrfs[12].AlarmActiveCode;
mind[107]:=CrpalkeGrfs[12].AlarmCodeLog1;
mind[108]:=CrpalkeGrfs[12].AlarmCodeLog2;
mind[109]:=CrpalkeGrfs[12].AlarmCodeLog3;
mind[110]:=CrpalkeGrfs[12].AlarmCodeLog4;
mind[111]:=CrpalkeGrfs[12].AlarmCodeLog5;
mind[112]:=CrpalkeGrfs[12].AlarmGroupXVH[0];
mind[113]:=CrpalkeGrfs[12].AlarmGroupXVH[10];
mind[114]:=CrpalkeGrfs[12].AlarmGroupXVH[11];
mind[115]:=CrpalkeGrfs[12].AlarmGroupXVH[12];
mind[116]:=CrpalkeGrfs[12].AlarmGroupXVH[13];
mind[117]:=CrpalkeGrfs[12].AlarmGroupXVH[14];
mind[118]:=CrpalkeGrfs[12].AlarmGroupXVH[15];
mind[119]:=CrpalkeGrfs[12].AlarmGroupXVH[16];
mind[120]:=CrpalkeGrfs[12].AlarmGroupXVH[1];
mind[121]:=CrpalkeGrfs[12].AlarmGroupXVH[2];
mind[122]:=CrpalkeGrfs[12].AlarmGroupXVH[3];
mind[123]:=CrpalkeGrfs[12].AlarmGroupXVH[4];
mind[124]:=CrpalkeGrfs[12].AlarmGroupXVH[5];
mind[125]:=CrpalkeGrfs[12].AlarmGroupXVH[6];
mind[126]:=CrpalkeGrfs[12].AlarmGroupXVH[7];
mind[127]:=CrpalkeGrfs[12].AlarmGroupXVH[8];
mind[128]:=CrpalkeGrfs[12].AlarmGroupXVH[9];
mind[129]:=CrpalkeGrfs[12].AlarmQSD1;
mind[130]:=CrpalkeGrfs[12].AlarmQSD2;
mind[131]:=CrpalkeGrfs[12].AlarmStart1;
mind[132]:=CrpalkeGrfs[12].AlarmStart2;
mind[133]:=CrpalkeGrfs[12].AlarmStop1;
mind[134]:=CrpalkeGrfs[12].AlarmStop2;
mind[135]:=CrpalkeGrfs[12].AlarmStop3;
mind[136]:=CrpalkeGrfs[12].AlarmSurv1;
mind[137]:=CrpalkeGrfs[12].AlarmSurv2;
mind[138]:=CrpalkeGrfs[12].ControlSource;
mind[139]:=CrpalkeGrfs[12].ExternInputSetup;
mind[140]:=CrpalkeGrfs[12].ExternInputsStatus;
mind[141]:=CrpalkeGrfs[12].LocalSetupMode1;
mind[142]:=CrpalkeGrfs[12].PreklopkaMode;
mind[143]:=CrpalkeGrfs[12].Relay1setup;
mind[144]:=CrpalkeGrfs[12].RemoteSetupMode1;
mind[145]:=CrpalkeGrfs[12].StatusCrpalke;
mind[146]:=CrpalkeGrfs[12].StatusMode1;
mind[147]:=CrpalkeGrfs[12].StatusMode1co;
mind[148]:=CrpalkeGrfs[12].StatusMode1op;
mind[149]:=CrpalkeGrfs[12].StatusMode2;
mind[150]:=CrpalkeGrfs[12].StatusMode3;
mind[151]:=CrpalkeGrfs[13].AlarmActiveCode;
mind[152]:=CrpalkeGrfs[13].AlarmCodeLog1;
mind[153]:=CrpalkeGrfs[13].AlarmCodeLog2;
mind[154]:=CrpalkeGrfs[13].AlarmCodeLog3;
mind[155]:=CrpalkeGrfs[13].AlarmCodeLog4;
mind[156]:=CrpalkeGrfs[13].AlarmCodeLog5;
mind[157]:=CrpalkeGrfs[13].AlarmGroupXVH[0];
mind[158]:=CrpalkeGrfs[13].AlarmGroupXVH[10];
mind[159]:=CrpalkeGrfs[13].AlarmGroupXVH[11];
mind[160]:=CrpalkeGrfs[13].AlarmGroupXVH[12];
mind[161]:=CrpalkeGrfs[13].AlarmGroupXVH[13];
mind[162]:=CrpalkeGrfs[13].AlarmGroupXVH[14];
mind[163]:=CrpalkeGrfs[13].AlarmGroupXVH[15];
mind[164]:=CrpalkeGrfs[13].AlarmGroupXVH[16];
mind[165]:=CrpalkeGrfs[13].AlarmGroupXVH[1];
mind[166]:=CrpalkeGrfs[13].AlarmGroupXVH[2];
mind[167]:=CrpalkeGrfs[13].AlarmGroupXVH[3];
mind[168]:=CrpalkeGrfs[13].AlarmGroupXVH[4];
mind[169]:=CrpalkeGrfs[13].AlarmGroupXVH[5];
mind[170]:=CrpalkeGrfs[13].AlarmGroupXVH[6];
mind[171]:=CrpalkeGrfs[13].AlarmGroupXVH[7];
mind[172]:=CrpalkeGrfs[13].AlarmGroupXVH[8];
mind[173]:=CrpalkeGrfs[13].AlarmGroupXVH[9];
mind[174]:=CrpalkeGrfs[13].AlarmQSD1;
mind[175]:=CrpalkeGrfs[13].AlarmQSD2;
mind[176]:=CrpalkeGrfs[13].AlarmStart1;
mind[177]:=CrpalkeGrfs[13].AlarmStart2;
mind[178]:=CrpalkeGrfs[13].AlarmStop1;
mind[179]:=CrpalkeGrfs[13].AlarmStop2;
mind[180]:=CrpalkeGrfs[13].AlarmStop3;
mind[181]:=CrpalkeGrfs[13].AlarmSurv1;
mind[182]:=CrpalkeGrfs[13].AlarmSurv2;
mind[183]:=CrpalkeGrfs[13].ControlSource;
mind[184]:=CrpalkeGrfs[13].ExternInputSetup;
mind[185]:=CrpalkeGrfs[13].ExternInputsStatus;
mind[186]:=CrpalkeGrfs[13].LocalSetupMode1;
mind[187]:=CrpalkeGrfs[13].PreklopkaMode;
mind[188]:=CrpalkeGrfs[13].Relay1setup;
mind[189]:=CrpalkeGrfs[13].RemoteSetupMode1;
mind[190]:=CrpalkeGrfs[13].StatusCrpalke;
mind[191]:=CrpalkeGrfs[13].StatusMode1;
mind[192]:=CrpalkeGrfs[13].StatusMode1co;
mind[193]:=CrpalkeGrfs[13].StatusMode1op;
mind[194]:=CrpalkeGrfs[13].StatusMode2;
mind[195]:=CrpalkeGrfs[13].StatusMode3;
mind[196]:=CrpalkeGrfs[14].AlarmActiveCode;
mind[197]:=CrpalkeGrfs[14].AlarmCodeLog1;
mind[198]:=CrpalkeGrfs[14].AlarmCodeLog2;
mind[199]:=CrpalkeGrfs[14].AlarmCodeLog3;
mind[200]:=CrpalkeGrfs[14].AlarmCodeLog4;
mind[201]:=CrpalkeGrfs[14].AlarmCodeLog5;
mind[202]:=CrpalkeGrfs[14].AlarmGroupXVH[0];
mind[203]:=CrpalkeGrfs[14].AlarmGroupXVH[10];
mind[204]:=CrpalkeGrfs[14].AlarmGroupXVH[11];
mind[205]:=CrpalkeGrfs[14].AlarmGroupXVH[12];
mind[206]:=CrpalkeGrfs[14].AlarmGroupXVH[13];
mind[207]:=CrpalkeGrfs[14].AlarmGroupXVH[14];
mind[208]:=CrpalkeGrfs[14].AlarmGroupXVH[15];
mind[209]:=CrpalkeGrfs[14].AlarmGroupXVH[16];
mind[210]:=CrpalkeGrfs[14].AlarmGroupXVH[1];
mind[211]:=CrpalkeGrfs[14].AlarmGroupXVH[2];
mind[212]:=CrpalkeGrfs[14].AlarmGroupXVH[3];
mind[213]:=CrpalkeGrfs[14].AlarmGroupXVH[4];
mind[214]:=CrpalkeGrfs[14].AlarmGroupXVH[5];
mind[215]:=CrpalkeGrfs[14].AlarmGroupXVH[6];
mind[216]:=CrpalkeGrfs[14].AlarmGroupXVH[7];
mind[217]:=CrpalkeGrfs[14].AlarmGroupXVH[8];
mind[218]:=CrpalkeGrfs[14].AlarmGroupXVH[9];
mind[219]:=CrpalkeGrfs[14].AlarmQSD1;
mind[220]:=CrpalkeGrfs[14].AlarmQSD2;
mind[221]:=CrpalkeGrfs[14].AlarmStart1;
mind[222]:=CrpalkeGrfs[14].AlarmStart2;
mind[223]:=CrpalkeGrfs[14].AlarmStop1;
mind[224]:=CrpalkeGrfs[14].AlarmStop2;
mind[225]:=CrpalkeGrfs[14].AlarmStop3;
mind[226]:=CrpalkeGrfs[14].AlarmSurv1;
mind[227]:=CrpalkeGrfs[14].AlarmSurv2;
mind[228]:=CrpalkeGrfs[14].ControlSource;
mind[229]:=CrpalkeGrfs[14].ExternInputSetup;
mind[230]:=CrpalkeGrfs[14].ExternInputsStatus;
mind[231]:=CrpalkeGrfs[14].LocalSetupMode1;
mind[232]:=CrpalkeGrfs[14].PreklopkaMode;
mind[233]:=CrpalkeGrfs[14].Relay1setup;
mind[234]:=CrpalkeGrfs[14].RemoteSetupMode1;
mind[235]:=CrpalkeGrfs[14].StatusCrpalke;
mind[236]:=CrpalkeGrfs[14].StatusMode1;
mind[237]:=CrpalkeGrfs[14].StatusMode1co;
mind[238]:=CrpalkeGrfs[14].StatusMode1op;
mind[239]:=CrpalkeGrfs[14].StatusMode2;
mind[240]:=CrpalkeGrfs[14].StatusMode3;
mind[241]:=CrpalkeGrfs[1].AlarmActiveCode;
mind[242]:=CrpalkeGrfs[1].AlarmCodeLog1;
mind[243]:=CrpalkeGrfs[1].AlarmCodeLog2;
mind[244]:=CrpalkeGrfs[1].AlarmCodeLog3;
mind[245]:=CrpalkeGrfs[1].AlarmCodeLog4;
mind[246]:=CrpalkeGrfs[1].AlarmCodeLog5;
mind[247]:=CrpalkeGrfs[1].AlarmGroupXVH[0];
mind[248]:=CrpalkeGrfs[1].AlarmGroupXVH[10];
mind[249]:=CrpalkeGrfs[1].AlarmGroupXVH[11];
mind[250]:=CrpalkeGrfs[1].AlarmGroupXVH[12];
mind[251]:=CrpalkeGrfs[1].AlarmGroupXVH[13];
mind[252]:=CrpalkeGrfs[1].AlarmGroupXVH[14];
mind[253]:=CrpalkeGrfs[1].AlarmGroupXVH[15];
mind[254]:=CrpalkeGrfs[1].AlarmGroupXVH[16];
mind[255]:=CrpalkeGrfs[1].AlarmGroupXVH[1];
mind[256]:=CrpalkeGrfs[1].AlarmGroupXVH[2];
mind[257]:=CrpalkeGrfs[1].AlarmGroupXVH[3];
mind[258]:=CrpalkeGrfs[1].AlarmGroupXVH[4];
mind[259]:=CrpalkeGrfs[1].AlarmGroupXVH[5];
mind[260]:=CrpalkeGrfs[1].AlarmGroupXVH[6];
mind[261]:=CrpalkeGrfs[1].AlarmGroupXVH[7];
mind[262]:=CrpalkeGrfs[1].AlarmGroupXVH[8];
mind[263]:=CrpalkeGrfs[1].AlarmGroupXVH[9];
mind[264]:=CrpalkeGrfs[1].AlarmQSD1;
mind[265]:=CrpalkeGrfs[1].AlarmQSD2;
mind[266]:=CrpalkeGrfs[1].AlarmStart1;
mind[267]:=CrpalkeGrfs[1].AlarmStart2;
mind[268]:=CrpalkeGrfs[1].AlarmStop1;
mind[269]:=CrpalkeGrfs[1].AlarmStop2;
mind[270]:=CrpalkeGrfs[1].AlarmStop3;
mind[271]:=CrpalkeGrfs[1].AlarmSurv1;
mind[272]:=CrpalkeGrfs[1].AlarmSurv2;
mind[273]:=CrpalkeGrfs[1].ControlSource;
mind[274]:=CrpalkeGrfs[1].ExternInputSetup;
mind[275]:=CrpalkeGrfs[1].ExternInputsStatus;
mind[276]:=CrpalkeGrfs[1].LocalSetupMode1;
mind[277]:=CrpalkeGrfs[1].PreklopkaMode;
mind[278]:=CrpalkeGrfs[1].Relay1setup;
mind[279]:=CrpalkeGrfs[1].RemoteSetupMode1;
mind[280]:=CrpalkeGrfs[1].StatusCrpalke;
mind[281]:=CrpalkeGrfs[1].StatusMode1;
mind[282]:=CrpalkeGrfs[1].StatusMode1co;
mind[283]:=CrpalkeGrfs[1].StatusMode1op;
mind[284]:=CrpalkeGrfs[1].StatusMode2;
mind[285]:=CrpalkeGrfs[1].StatusMode3;
mind[286]:=CrpalkeGrfs[2].AlarmActiveCode;
mind[287]:=CrpalkeGrfs[2].AlarmCodeLog1;
mind[288]:=CrpalkeGrfs[2].AlarmCodeLog2;
mind[289]:=CrpalkeGrfs[2].AlarmCodeLog3;
mind[290]:=CrpalkeGrfs[2].AlarmCodeLog4;
mind[291]:=CrpalkeGrfs[2].AlarmCodeLog5;
mind[292]:=CrpalkeGrfs[2].AlarmGroupXVH[0];
mind[293]:=CrpalkeGrfs[2].AlarmGroupXVH[10];
mind[294]:=CrpalkeGrfs[2].AlarmGroupXVH[11];
mind[295]:=CrpalkeGrfs[2].AlarmGroupXVH[12];
mind[296]:=CrpalkeGrfs[2].AlarmGroupXVH[13];
mind[297]:=CrpalkeGrfs[2].AlarmGroupXVH[14];
mind[298]:=CrpalkeGrfs[2].AlarmGroupXVH[15];
mind[299]:=CrpalkeGrfs[2].AlarmGroupXVH[16];
mind[300]:=CrpalkeGrfs[2].AlarmGroupXVH[1];
mind[301]:=CrpalkeGrfs[2].AlarmGroupXVH[2];
mind[302]:=CrpalkeGrfs[2].AlarmGroupXVH[3];
mind[303]:=CrpalkeGrfs[2].AlarmGroupXVH[4];
mind[304]:=CrpalkeGrfs[2].AlarmGroupXVH[5];
mind[305]:=CrpalkeGrfs[2].AlarmGroupXVH[6];
mind[306]:=CrpalkeGrfs[2].AlarmGroupXVH[7];
mind[307]:=CrpalkeGrfs[2].AlarmGroupXVH[8];
mind[308]:=CrpalkeGrfs[2].AlarmGroupXVH[9];
mind[309]:=CrpalkeGrfs[2].AlarmQSD1;
mind[310]:=CrpalkeGrfs[2].AlarmQSD2;
mind[311]:=CrpalkeGrfs[2].AlarmStart1;
mind[312]:=CrpalkeGrfs[2].AlarmStart2;
mind[313]:=CrpalkeGrfs[2].AlarmStop1;
mind[314]:=CrpalkeGrfs[2].AlarmStop2;
mind[315]:=CrpalkeGrfs[2].AlarmStop3;
mind[316]:=CrpalkeGrfs[2].AlarmSurv1;
mind[317]:=CrpalkeGrfs[2].AlarmSurv2;
mind[318]:=CrpalkeGrfs[2].ControlSource;
mind[319]:=CrpalkeGrfs[2].ExternInputSetup;
mind[320]:=CrpalkeGrfs[2].ExternInputsStatus;
mind[321]:=CrpalkeGrfs[2].LocalSetupMode1;
mind[322]:=CrpalkeGrfs[2].PreklopkaMode;
mind[323]:=CrpalkeGrfs[2].Relay1setup;
mind[324]:=CrpalkeGrfs[2].RemoteSetupMode1;
mind[325]:=CrpalkeGrfs[2].StatusCrpalke;
mind[326]:=CrpalkeGrfs[2].StatusMode1;
mind[327]:=CrpalkeGrfs[2].StatusMode1co;
mind[328]:=CrpalkeGrfs[2].StatusMode1op;
mind[329]:=CrpalkeGrfs[2].StatusMode2;
mind[330]:=CrpalkeGrfs[2].StatusMode3;
mind[331]:=CrpalkeGrfs[3].AlarmActiveCode;
mind[332]:=CrpalkeGrfs[3].AlarmCodeLog1;
mind[333]:=CrpalkeGrfs[3].AlarmCodeLog2;
mind[334]:=CrpalkeGrfs[3].AlarmCodeLog3;
mind[335]:=CrpalkeGrfs[3].AlarmCodeLog4;
mind[336]:=CrpalkeGrfs[3].AlarmCodeLog5;
mind[337]:=CrpalkeGrfs[3].AlarmGroupXVH[0];
mind[338]:=CrpalkeGrfs[3].AlarmGroupXVH[10];
mind[339]:=CrpalkeGrfs[3].AlarmGroupXVH[11];
mind[340]:=CrpalkeGrfs[3].AlarmGroupXVH[12];
mind[341]:=CrpalkeGrfs[3].AlarmGroupXVH[13];
mind[342]:=CrpalkeGrfs[3].AlarmGroupXVH[14];
mind[343]:=CrpalkeGrfs[3].AlarmGroupXVH[15];
mind[344]:=CrpalkeGrfs[3].AlarmGroupXVH[16];
mind[345]:=CrpalkeGrfs[3].AlarmGroupXVH[1];
mind[346]:=CrpalkeGrfs[3].AlarmGroupXVH[2];
mind[347]:=CrpalkeGrfs[3].AlarmGroupXVH[3];
mind[348]:=CrpalkeGrfs[3].AlarmGroupXVH[4];
mind[349]:=CrpalkeGrfs[3].AlarmGroupXVH[5];
mind[350]:=CrpalkeGrfs[3].AlarmGroupXVH[6];
mind[351]:=CrpalkeGrfs[3].AlarmGroupXVH[7];
mind[352]:=CrpalkeGrfs[3].AlarmGroupXVH[8];
mind[353]:=CrpalkeGrfs[3].AlarmGroupXVH[9];
mind[354]:=CrpalkeGrfs[3].AlarmQSD1;
mind[355]:=CrpalkeGrfs[3].AlarmQSD2;
mind[356]:=CrpalkeGrfs[3].AlarmStart1;
mind[357]:=CrpalkeGrfs[3].AlarmStart2;
mind[358]:=CrpalkeGrfs[3].AlarmStop1;
mind[359]:=CrpalkeGrfs[3].AlarmStop2;
mind[360]:=CrpalkeGrfs[3].AlarmStop3;
mind[361]:=CrpalkeGrfs[3].AlarmSurv1;
mind[362]:=CrpalkeGrfs[3].AlarmSurv2;
mind[363]:=CrpalkeGrfs[3].ControlSource;
mind[364]:=CrpalkeGrfs[3].ExternInputSetup;
mind[365]:=CrpalkeGrfs[3].ExternInputsStatus;
mind[366]:=CrpalkeGrfs[3].LocalSetupMode1;
mind[367]:=CrpalkeGrfs[3].PreklopkaMode;
mind[368]:=CrpalkeGrfs[3].Relay1setup;
mind[369]:=CrpalkeGrfs[3].RemoteSetupMode1;
mind[370]:=CrpalkeGrfs[3].StatusCrpalke;
mind[371]:=CrpalkeGrfs[3].StatusMode1;
mind[372]:=CrpalkeGrfs[3].StatusMode1co;
mind[373]:=CrpalkeGrfs[3].StatusMode1op;
mind[374]:=CrpalkeGrfs[3].StatusMode2;
mind[375]:=CrpalkeGrfs[3].StatusMode3;
mind[376]:=CrpalkeGrfs[4].AlarmActiveCode;
mind[377]:=CrpalkeGrfs[4].AlarmCodeLog1;
mind[378]:=CrpalkeGrfs[4].AlarmCodeLog2;
mind[379]:=CrpalkeGrfs[4].AlarmCodeLog3;
mind[380]:=CrpalkeGrfs[4].AlarmCodeLog4;
mind[381]:=CrpalkeGrfs[4].AlarmCodeLog5;
mind[382]:=CrpalkeGrfs[4].AlarmGroupXVH[0];
mind[383]:=CrpalkeGrfs[4].AlarmGroupXVH[10];
mind[384]:=CrpalkeGrfs[4].AlarmGroupXVH[11];
mind[385]:=CrpalkeGrfs[4].AlarmGroupXVH[12];
mind[386]:=CrpalkeGrfs[4].AlarmGroupXVH[13];
mind[387]:=CrpalkeGrfs[4].AlarmGroupXVH[14];
mind[388]:=CrpalkeGrfs[4].AlarmGroupXVH[15];
mind[389]:=CrpalkeGrfs[4].AlarmGroupXVH[16];
mind[390]:=CrpalkeGrfs[4].AlarmGroupXVH[1];
mind[391]:=CrpalkeGrfs[4].AlarmGroupXVH[2];
mind[392]:=CrpalkeGrfs[4].AlarmGroupXVH[3];
mind[393]:=CrpalkeGrfs[4].AlarmGroupXVH[4];
mind[394]:=CrpalkeGrfs[4].AlarmGroupXVH[5];
mind[395]:=CrpalkeGrfs[4].AlarmGroupXVH[6];
mind[396]:=CrpalkeGrfs[4].AlarmGroupXVH[7];
mind[397]:=CrpalkeGrfs[4].AlarmGroupXVH[8];
mind[398]:=CrpalkeGrfs[4].AlarmGroupXVH[9];
mind[399]:=CrpalkeGrfs[4].AlarmQSD1;
mind[400]:=CrpalkeGrfs[4].AlarmQSD2;
mind[401]:=CrpalkeGrfs[4].AlarmStart1;
mind[402]:=CrpalkeGrfs[4].AlarmStart2;
mind[403]:=CrpalkeGrfs[4].AlarmStop1;
mind[404]:=CrpalkeGrfs[4].AlarmStop2;
mind[405]:=CrpalkeGrfs[4].AlarmStop3;
mind[406]:=CrpalkeGrfs[4].AlarmSurv1;
mind[407]:=CrpalkeGrfs[4].AlarmSurv2;
mind[408]:=CrpalkeGrfs[4].ControlSource;
mind[409]:=CrpalkeGrfs[4].ExternInputSetup;
mind[410]:=CrpalkeGrfs[4].ExternInputsStatus;
mind[411]:=CrpalkeGrfs[4].LocalSetupMode1;
mind[412]:=CrpalkeGrfs[4].PreklopkaMode;
mind[413]:=CrpalkeGrfs[4].Relay1setup;
mind[414]:=CrpalkeGrfs[4].RemoteSetupMode1;
mind[415]:=CrpalkeGrfs[4].StatusCrpalke;
mind[416]:=CrpalkeGrfs[4].StatusMode1;
mind[417]:=CrpalkeGrfs[4].StatusMode1co;
mind[418]:=CrpalkeGrfs[4].StatusMode1op;
mind[419]:=CrpalkeGrfs[4].StatusMode2;
mind[420]:=CrpalkeGrfs[4].StatusMode3;
mind[421]:=CrpalkeGrfs[5].AlarmActiveCode;
mind[422]:=CrpalkeGrfs[5].AlarmCodeLog1;
mind[423]:=CrpalkeGrfs[5].AlarmCodeLog2;
mind[424]:=CrpalkeGrfs[5].AlarmCodeLog3;
mind[425]:=CrpalkeGrfs[5].AlarmCodeLog4;
mind[426]:=CrpalkeGrfs[5].AlarmCodeLog5;
mind[427]:=CrpalkeGrfs[5].AlarmGroupXVH[0];
mind[428]:=CrpalkeGrfs[5].AlarmGroupXVH[10];
mind[429]:=CrpalkeGrfs[5].AlarmGroupXVH[11];
mind[430]:=CrpalkeGrfs[5].AlarmGroupXVH[12];
mind[431]:=CrpalkeGrfs[5].AlarmGroupXVH[13];
mind[432]:=CrpalkeGrfs[5].AlarmGroupXVH[14];
mind[433]:=CrpalkeGrfs[5].AlarmGroupXVH[15];
mind[434]:=CrpalkeGrfs[5].AlarmGroupXVH[16];
mind[435]:=CrpalkeGrfs[5].AlarmGroupXVH[1];
mind[436]:=CrpalkeGrfs[5].AlarmGroupXVH[2];
mind[437]:=CrpalkeGrfs[5].AlarmGroupXVH[3];
mind[438]:=CrpalkeGrfs[5].AlarmGroupXVH[4];
mind[439]:=CrpalkeGrfs[5].AlarmGroupXVH[5];
mind[440]:=CrpalkeGrfs[5].AlarmGroupXVH[6];
mind[441]:=CrpalkeGrfs[5].AlarmGroupXVH[7];
mind[442]:=CrpalkeGrfs[5].AlarmGroupXVH[8];
mind[443]:=CrpalkeGrfs[5].AlarmGroupXVH[9];
mind[444]:=CrpalkeGrfs[5].AlarmQSD1;
mind[445]:=CrpalkeGrfs[5].AlarmQSD2;
mind[446]:=CrpalkeGrfs[5].AlarmStart1;
mind[447]:=CrpalkeGrfs[5].AlarmStart2;
mind[448]:=CrpalkeGrfs[5].AlarmStop1;
mind[449]:=CrpalkeGrfs[5].AlarmStop2;
mind[450]:=CrpalkeGrfs[5].AlarmStop3;
mind[451]:=CrpalkeGrfs[5].AlarmSurv1;
mind[452]:=CrpalkeGrfs[5].AlarmSurv2;
mind[453]:=CrpalkeGrfs[5].ControlSource;
mind[454]:=CrpalkeGrfs[5].ExternInputSetup;
mind[455]:=CrpalkeGrfs[5].ExternInputsStatus;
mind[456]:=CrpalkeGrfs[5].LocalSetupMode1;
mind[457]:=CrpalkeGrfs[5].PreklopkaMode;
mind[458]:=CrpalkeGrfs[5].Relay1setup;
mind[459]:=CrpalkeGrfs[5].RemoteSetupMode1;
mind[460]:=CrpalkeGrfs[5].StatusCrpalke;
mind[461]:=CrpalkeGrfs[5].StatusMode1;
mind[462]:=CrpalkeGrfs[5].StatusMode1co;
mind[463]:=CrpalkeGrfs[5].StatusMode1op;
mind[464]:=CrpalkeGrfs[5].StatusMode2;
mind[465]:=CrpalkeGrfs[5].StatusMode3;
mind[466]:=CrpalkeGrfs[6].AlarmActiveCode;
mind[467]:=CrpalkeGrfs[6].AlarmCodeLog1;
mind[468]:=CrpalkeGrfs[6].AlarmCodeLog2;
mind[469]:=CrpalkeGrfs[6].AlarmCodeLog3;
mind[470]:=CrpalkeGrfs[6].AlarmCodeLog4;
mind[471]:=CrpalkeGrfs[6].AlarmCodeLog5;
mind[472]:=CrpalkeGrfs[6].AlarmGroupXVH[0];
mind[473]:=CrpalkeGrfs[6].AlarmGroupXVH[10];
mind[474]:=CrpalkeGrfs[6].AlarmGroupXVH[11];
mind[475]:=CrpalkeGrfs[6].AlarmGroupXVH[12];
mind[476]:=CrpalkeGrfs[6].AlarmGroupXVH[13];
mind[477]:=CrpalkeGrfs[6].AlarmGroupXVH[14];
mind[478]:=CrpalkeGrfs[6].AlarmGroupXVH[15];
mind[479]:=CrpalkeGrfs[6].AlarmGroupXVH[16];
mind[480]:=CrpalkeGrfs[6].AlarmGroupXVH[1];
mind[481]:=CrpalkeGrfs[6].AlarmGroupXVH[2];
mind[482]:=CrpalkeGrfs[6].AlarmGroupXVH[3];
mind[483]:=CrpalkeGrfs[6].AlarmGroupXVH[4];
mind[484]:=CrpalkeGrfs[6].AlarmGroupXVH[5];
mind[485]:=CrpalkeGrfs[6].AlarmGroupXVH[6];
mind[486]:=CrpalkeGrfs[6].AlarmGroupXVH[7];
mind[487]:=CrpalkeGrfs[6].AlarmGroupXVH[8];
mind[488]:=CrpalkeGrfs[6].AlarmGroupXVH[9];
mind[489]:=CrpalkeGrfs[6].AlarmQSD1;
mind[490]:=CrpalkeGrfs[6].AlarmQSD2;
mind[491]:=CrpalkeGrfs[6].AlarmStart1;
mind[492]:=CrpalkeGrfs[6].AlarmStart2;
mind[493]:=CrpalkeGrfs[6].AlarmStop1;
mind[494]:=CrpalkeGrfs[6].AlarmStop2;
mind[495]:=CrpalkeGrfs[6].AlarmStop3;
mind[496]:=CrpalkeGrfs[6].AlarmSurv1;
mind[497]:=CrpalkeGrfs[6].AlarmSurv2;
mind[498]:=CrpalkeGrfs[6].ControlSource;
mind[499]:=CrpalkeGrfs[6].ExternInputSetup;
mind[500]:=CrpalkeGrfs[6].ExternInputsStatus;
mind[501]:=CrpalkeGrfs[6].LocalSetupMode1;
mind[502]:=CrpalkeGrfs[6].PreklopkaMode;
mind[503]:=CrpalkeGrfs[6].Relay1setup;
mind[504]:=CrpalkeGrfs[6].RemoteSetupMode1;
mind[505]:=CrpalkeGrfs[6].StatusCrpalke;
mind[506]:=CrpalkeGrfs[6].StatusMode1;
mind[507]:=CrpalkeGrfs[6].StatusMode1co;
mind[508]:=CrpalkeGrfs[6].StatusMode1op;
mind[509]:=CrpalkeGrfs[6].StatusMode2;
mind[510]:=CrpalkeGrfs[6].StatusMode3;
mind[511]:=CrpalkeGrfs[7].AlarmActiveCode;
mind[512]:=CrpalkeGrfs[7].AlarmCodeLog1;
mind[513]:=CrpalkeGrfs[7].AlarmCodeLog2;
mind[514]:=CrpalkeGrfs[7].AlarmCodeLog3;
mind[515]:=CrpalkeGrfs[7].AlarmCodeLog4;
mind[516]:=CrpalkeGrfs[7].AlarmCodeLog5;
mind[517]:=CrpalkeGrfs[7].AlarmGroupXVH[0];
mind[518]:=CrpalkeGrfs[7].AlarmGroupXVH[10];
mind[519]:=CrpalkeGrfs[7].AlarmGroupXVH[11];
mind[520]:=CrpalkeGrfs[7].AlarmGroupXVH[12];
mind[521]:=CrpalkeGrfs[7].AlarmGroupXVH[13];
mind[522]:=CrpalkeGrfs[7].AlarmGroupXVH[14];
mind[523]:=CrpalkeGrfs[7].AlarmGroupXVH[15];
mind[524]:=CrpalkeGrfs[7].AlarmGroupXVH[16];
mind[525]:=CrpalkeGrfs[7].AlarmGroupXVH[1];
mind[526]:=CrpalkeGrfs[7].AlarmGroupXVH[2];
mind[527]:=CrpalkeGrfs[7].AlarmGroupXVH[3];
mind[528]:=CrpalkeGrfs[7].AlarmGroupXVH[4];
mind[529]:=CrpalkeGrfs[7].AlarmGroupXVH[5];
mind[530]:=CrpalkeGrfs[7].AlarmGroupXVH[6];
mind[531]:=CrpalkeGrfs[7].AlarmGroupXVH[7];
mind[532]:=CrpalkeGrfs[7].AlarmGroupXVH[8];
mind[533]:=CrpalkeGrfs[7].AlarmGroupXVH[9];
mind[534]:=CrpalkeGrfs[7].AlarmQSD1;
mind[535]:=CrpalkeGrfs[7].AlarmQSD2;
mind[536]:=CrpalkeGrfs[7].AlarmStart1;
mind[537]:=CrpalkeGrfs[7].AlarmStart2;
mind[538]:=CrpalkeGrfs[7].AlarmStop1;
mind[539]:=CrpalkeGrfs[7].AlarmStop2;
mind[540]:=CrpalkeGrfs[7].AlarmStop3;
mind[541]:=CrpalkeGrfs[7].AlarmSurv1;
mind[542]:=CrpalkeGrfs[7].AlarmSurv2;
mind[543]:=CrpalkeGrfs[7].ControlSource;
mind[544]:=CrpalkeGrfs[7].ExternInputSetup;
mind[545]:=CrpalkeGrfs[7].ExternInputsStatus;
mind[546]:=CrpalkeGrfs[7].LocalSetupMode1;
mind[547]:=CrpalkeGrfs[7].PreklopkaMode;
mind[548]:=CrpalkeGrfs[7].Relay1setup;
mind[549]:=CrpalkeGrfs[7].RemoteSetupMode1;
mind[550]:=CrpalkeGrfs[7].StatusCrpalke;
mind[551]:=CrpalkeGrfs[7].StatusMode1;
mind[552]:=CrpalkeGrfs[7].StatusMode1co;
mind[553]:=CrpalkeGrfs[7].StatusMode1op;
mind[554]:=CrpalkeGrfs[7].StatusMode2;
mind[555]:=CrpalkeGrfs[7].StatusMode3;
mind[556]:=CrpalkeGrfs[8].AlarmActiveCode;
mind[557]:=CrpalkeGrfs[8].AlarmCodeLog1;
mind[558]:=CrpalkeGrfs[8].AlarmCodeLog2;
mind[559]:=CrpalkeGrfs[8].AlarmCodeLog3;
mind[560]:=CrpalkeGrfs[8].AlarmCodeLog4;
mind[561]:=CrpalkeGrfs[8].AlarmCodeLog5;
mind[562]:=CrpalkeGrfs[8].AlarmGroupXVH[0];
mind[563]:=CrpalkeGrfs[8].AlarmGroupXVH[10];
mind[564]:=CrpalkeGrfs[8].AlarmGroupXVH[11];
mind[565]:=CrpalkeGrfs[8].AlarmGroupXVH[12];
mind[566]:=CrpalkeGrfs[8].AlarmGroupXVH[13];
mind[567]:=CrpalkeGrfs[8].AlarmGroupXVH[14];
mind[568]:=CrpalkeGrfs[8].AlarmGroupXVH[15];
mind[569]:=CrpalkeGrfs[8].AlarmGroupXVH[16];
mind[570]:=CrpalkeGrfs[8].AlarmGroupXVH[1];
mind[571]:=CrpalkeGrfs[8].AlarmGroupXVH[2];
mind[572]:=CrpalkeGrfs[8].AlarmGroupXVH[3];
mind[573]:=CrpalkeGrfs[8].AlarmGroupXVH[4];
mind[574]:=CrpalkeGrfs[8].AlarmGroupXVH[5];
mind[575]:=CrpalkeGrfs[8].AlarmGroupXVH[6];
mind[576]:=CrpalkeGrfs[8].AlarmGroupXVH[7];
mind[577]:=CrpalkeGrfs[8].AlarmGroupXVH[8];
mind[578]:=CrpalkeGrfs[8].AlarmGroupXVH[9];
mind[579]:=CrpalkeGrfs[8].AlarmQSD1;
mind[580]:=CrpalkeGrfs[8].AlarmQSD2;
mind[581]:=CrpalkeGrfs[8].AlarmStart1;
mind[582]:=CrpalkeGrfs[8].AlarmStart2;
mind[583]:=CrpalkeGrfs[8].AlarmStop1;
mind[584]:=CrpalkeGrfs[8].AlarmStop2;
mind[585]:=CrpalkeGrfs[8].AlarmStop3;
mind[586]:=CrpalkeGrfs[8].AlarmSurv1;
mind[587]:=CrpalkeGrfs[8].AlarmSurv2;
mind[588]:=CrpalkeGrfs[8].ControlSource;
mind[589]:=CrpalkeGrfs[8].ExternInputSetup;
mind[590]:=CrpalkeGrfs[8].ExternInputsStatus;
mind[591]:=CrpalkeGrfs[8].LocalSetupMode1;
mind[592]:=CrpalkeGrfs[8].PreklopkaMode;
mind[593]:=CrpalkeGrfs[8].Relay1setup;
mind[594]:=CrpalkeGrfs[8].RemoteSetupMode1;
mind[595]:=CrpalkeGrfs[8].StatusCrpalke;
mind[596]:=CrpalkeGrfs[8].StatusMode1;
mind[597]:=CrpalkeGrfs[8].StatusMode1co;
mind[598]:=CrpalkeGrfs[8].StatusMode1op;
mind[599]:=CrpalkeGrfs[8].StatusMode2;
mind[600]:=CrpalkeGrfs[8].StatusMode3;
mind[601]:=CrpalkeGrfs[9].AlarmActiveCode;
mind[602]:=CrpalkeGrfs[9].AlarmCodeLog1;
mind[603]:=CrpalkeGrfs[9].AlarmCodeLog2;
mind[604]:=CrpalkeGrfs[9].AlarmCodeLog3;
mind[605]:=CrpalkeGrfs[9].AlarmCodeLog4;
mind[606]:=CrpalkeGrfs[9].AlarmCodeLog5;
mind[607]:=CrpalkeGrfs[9].AlarmGroupXVH[0];
mind[608]:=CrpalkeGrfs[9].AlarmGroupXVH[10];
mind[609]:=CrpalkeGrfs[9].AlarmGroupXVH[11];
mind[610]:=CrpalkeGrfs[9].AlarmGroupXVH[12];
mind[611]:=CrpalkeGrfs[9].AlarmGroupXVH[13];
mind[612]:=CrpalkeGrfs[9].AlarmGroupXVH[14];
mind[613]:=CrpalkeGrfs[9].AlarmGroupXVH[15];
mind[614]:=CrpalkeGrfs[9].AlarmGroupXVH[16];
mind[615]:=CrpalkeGrfs[9].AlarmGroupXVH[1];
mind[616]:=CrpalkeGrfs[9].AlarmGroupXVH[2];
mind[617]:=CrpalkeGrfs[9].AlarmGroupXVH[3];
mind[618]:=CrpalkeGrfs[9].AlarmGroupXVH[4];
mind[619]:=CrpalkeGrfs[9].AlarmGroupXVH[5];
mind[620]:=CrpalkeGrfs[9].AlarmGroupXVH[6];
mind[621]:=CrpalkeGrfs[9].AlarmGroupXVH[7];
mind[622]:=CrpalkeGrfs[9].AlarmGroupXVH[8];
mind[623]:=CrpalkeGrfs[9].AlarmGroupXVH[9];
mind[624]:=CrpalkeGrfs[9].AlarmQSD1;
mind[625]:=CrpalkeGrfs[9].AlarmQSD2;
mind[626]:=CrpalkeGrfs[9].AlarmStart1;
mind[627]:=CrpalkeGrfs[9].AlarmStart2;
mind[628]:=CrpalkeGrfs[9].AlarmStop1;
mind[629]:=CrpalkeGrfs[9].AlarmStop2;
mind[630]:=CrpalkeGrfs[9].AlarmStop3;
mind[631]:=CrpalkeGrfs[9].AlarmSurv1;
mind[632]:=CrpalkeGrfs[9].AlarmSurv2;
mind[633]:=CrpalkeGrfs[9].ControlSource;
mind[634]:=CrpalkeGrfs[9].ExternInputSetup;
mind[635]:=CrpalkeGrfs[9].ExternInputsStatus;
mind[636]:=CrpalkeGrfs[9].LocalSetupMode1;
mind[637]:=CrpalkeGrfs[9].PreklopkaMode;
mind[638]:=CrpalkeGrfs[9].Relay1setup;
mind[639]:=CrpalkeGrfs[9].RemoteSetupMode1;
mind[640]:=CrpalkeGrfs[9].StatusCrpalke;
mind[641]:=CrpalkeGrfs[9].StatusMode1;
mind[642]:=CrpalkeGrfs[9].StatusMode1co;
mind[643]:=CrpalkeGrfs[9].StatusMode1op;
mind[644]:=CrpalkeGrfs[9].StatusMode2;
mind[645]:=CrpalkeGrfs[9].StatusMode3;
mind[646]:=DateTime.Dan;
mind[647]:=DateTime.Leto;
mind[648]:=DateTime.Mesec;
mind[649]:=DateTime.Minuta;
mind[650]:=DateTime.Sekunda;
mind[651]:=DateTime.Ura;
mind[652]:=HladStroj.KompresorOljeAlarmB;
mind[653]:=HladStroj.NizekPritiskAlarmB;
mind[654]:=HladStroj.ObratovalneUreOpozoriloB;
mind[655]:=HladStroj.TemperaturaAlarmB;
mind[656]:=HladStroj.UnitStatus;
mind[657]:=HladStroj.VisokPritiskAlarmB;
mind[658]:=HladStroj.VisokPritiskOpozoriloB;
mind[659]:=HladStroj.ZmrzalniAlarmB;
mind[660]:=Klima[1].CrpalkaStatus;
mind[661]:=Klima[1].HitrostVentStatus;
mind[662]:=Klima[1].IzhodniVentStatus;
mind[663]:=Klima[2].CrpalkaStatus;
mind[664]:=Klima[2].HitrostVentStatus;
mind[665]:=Klima[2].IzhodniVentStatus;
mind[666]:=PozarnaLoputaStatus[1];
mind[667]:=PozarnaLoputaStatus[2];
mind[668]:=PozarnaLoputaStatus[3];
mind[669]:=PozarnaLoputaStatus[4];
mind[670]:=PozarnaLoputaStatus[5];
mind[671]:=StatusKondenzEnota[0];
mind[672]:=StatusKondenzEnota[1];
mind[673]:=StatusKondenzEnota[2];
mind[674]:=StatusKondenzEnota[3];
mind[675]:=StatusKontaktor[10];
mind[676]:=StatusKontaktor[11];
mind[677]:=StatusKontaktor[12];
mind[678]:=StatusKontaktor[13];
mind[679]:=StatusKontaktor[14];
mind[680]:=StatusKontaktor[15];
mind[681]:=StatusKontaktor[16];
mind[682]:=StatusKontaktor[17];
mind[683]:=StatusKontaktor[18];
mind[684]:=StatusKontaktor[19];
mind[685]:=StatusKontaktor[1];
mind[686]:=StatusKontaktor[20];
mind[687]:=StatusKontaktor[21];
mind[688]:=StatusKontaktor[22];
mind[689]:=StatusKontaktor[23];
mind[690]:=StatusKontaktor[24];
mind[691]:=StatusKontaktor[25];
mind[692]:=StatusKontaktor[2];
mind[693]:=StatusKontaktor[3];
mind[694]:=StatusKontaktor[4];
mind[695]:=StatusKontaktor[5];
mind[696]:=StatusKontaktor[6];
mind[697]:=StatusKontaktor[7];
mind[698]:=StatusKontaktor[8];
mind[699]:=StatusKontaktor[9];
mind[700]:=StatusPreklopke[10];
mind[701]:=StatusPreklopke[11];
mind[702]:=StatusPreklopke[12];
mind[703]:=StatusPreklopke[13];
mind[704]:=StatusPreklopke[14];
mind[705]:=StatusPreklopke[15];
mind[706]:=StatusPreklopke[16];
mind[707]:=StatusPreklopke[17];
mind[708]:=StatusPreklopke[18];
mind[709]:=StatusPreklopke[19];
mind[710]:=StatusPreklopke[1];
mind[711]:=StatusPreklopke[20];
mind[712]:=StatusPreklopke[21];
mind[713]:=StatusPreklopke[22];
mind[714]:=StatusPreklopke[23];
mind[715]:=StatusPreklopke[24];
mind[716]:=StatusPreklopke[25];
mind[717]:=StatusPreklopke[2];
mind[718]:=StatusPreklopke[3];
mind[719]:=StatusPreklopke[4];
mind[720]:=StatusPreklopke[5];
mind[721]:=StatusPreklopke[6];
mind[722]:=StatusPreklopke[7];
mind[723]:=StatusPreklopke[8];
mind[724]:=StatusPreklopke[9];
mind[725]:=ToplPost.NapakaRegister;
mind[726]:=Urnik_SCtoXCpot;
mind[727]:=Urnik_SCtoXCzah;
mind[728]:=Urnik_XCtoSCpot;
mind[729]:=Urnik_XCtoSCzah;
mind[730]:=UrnikSCtoXC.Dan[1].Off[1].Mna;
mind[731]:=UrnikSCtoXC.Dan[1].Off[1].Ura;
mind[732]:=UrnikSCtoXC.Dan[1].Off[2].Mna;
mind[733]:=UrnikSCtoXC.Dan[1].Off[2].Ura;
mind[734]:=UrnikSCtoXC.Dan[1].Off[3].Mna;
mind[735]:=UrnikSCtoXC.Dan[1].Off[3].Ura;
mind[736]:=UrnikSCtoXC.Dan[1].On[1].Mna;
mind[737]:=UrnikSCtoXC.Dan[1].On[1].Ura;
mind[738]:=UrnikSCtoXC.Dan[1].On[2].Mna;
mind[739]:=UrnikSCtoXC.Dan[1].On[2].Ura;
mind[740]:=UrnikSCtoXC.Dan[1].On[3].Mna;
mind[741]:=UrnikSCtoXC.Dan[1].On[3].Ura;
mind[742]:=UrnikSCtoXC.Dan[2].Off[1].Mna;
mind[743]:=UrnikSCtoXC.Dan[2].Off[1].Ura;
mind[744]:=UrnikSCtoXC.Dan[2].Off[2].Mna;
mind[745]:=UrnikSCtoXC.Dan[2].Off[2].Ura;
mind[746]:=UrnikSCtoXC.Dan[2].Off[3].Mna;
mind[747]:=UrnikSCtoXC.Dan[2].Off[3].Ura;
mind[748]:=UrnikSCtoXC.Dan[2].On[1].Mna;
mind[749]:=UrnikSCtoXC.Dan[2].On[1].Ura;
mind[750]:=UrnikSCtoXC.Dan[2].On[2].Mna;
mind[751]:=UrnikSCtoXC.Dan[2].On[2].Ura;
mind[752]:=UrnikSCtoXC.Dan[2].On[3].Mna;
mind[753]:=UrnikSCtoXC.Dan[2].On[3].Ura;
mind[754]:=UrnikSCtoXC.Dan[3].Off[1].Mna;
mind[755]:=UrnikSCtoXC.Dan[3].Off[1].Ura;
mind[756]:=UrnikSCtoXC.Dan[3].Off[2].Mna;
mind[757]:=UrnikSCtoXC.Dan[3].Off[2].Ura;
mind[758]:=UrnikSCtoXC.Dan[3].Off[3].Mna;
mind[759]:=UrnikSCtoXC.Dan[3].Off[3].Ura;
mind[760]:=UrnikSCtoXC.Dan[3].On[1].Mna;
mind[761]:=UrnikSCtoXC.Dan[3].On[1].Ura;
mind[762]:=UrnikSCtoXC.Dan[3].On[2].Mna;
mind[763]:=UrnikSCtoXC.Dan[3].On[2].Ura;
mind[764]:=UrnikSCtoXC.Dan[3].On[3].Mna;
mind[765]:=UrnikSCtoXC.Dan[3].On[3].Ura;
mind[766]:=UrnikSCtoXC.Dan[4].Off[1].Mna;
mind[767]:=UrnikSCtoXC.Dan[4].Off[1].Ura;
mind[768]:=UrnikSCtoXC.Dan[4].Off[2].Mna;
mind[769]:=UrnikSCtoXC.Dan[4].Off[2].Ura;
mind[770]:=UrnikSCtoXC.Dan[4].Off[3].Mna;
mind[771]:=UrnikSCtoXC.Dan[4].Off[3].Ura;
mind[772]:=UrnikSCtoXC.Dan[4].On[1].Mna;
mind[773]:=UrnikSCtoXC.Dan[4].On[1].Ura;
mind[774]:=UrnikSCtoXC.Dan[4].On[2].Mna;
mind[775]:=UrnikSCtoXC.Dan[4].On[2].Ura;
mind[776]:=UrnikSCtoXC.Dan[4].On[3].Mna;
mind[777]:=UrnikSCtoXC.Dan[4].On[3].Ura;
mind[778]:=UrnikSCtoXC.Dan[5].Off[1].Mna;
mind[779]:=UrnikSCtoXC.Dan[5].Off[1].Ura;
mind[780]:=UrnikSCtoXC.Dan[5].Off[2].Mna;
mind[781]:=UrnikSCtoXC.Dan[5].Off[2].Ura;
mind[782]:=UrnikSCtoXC.Dan[5].Off[3].Mna;
mind[783]:=UrnikSCtoXC.Dan[5].Off[3].Ura;
mind[784]:=UrnikSCtoXC.Dan[5].On[1].Mna;
mind[785]:=UrnikSCtoXC.Dan[5].On[1].Ura;
mind[786]:=UrnikSCtoXC.Dan[5].On[2].Mna;
mind[787]:=UrnikSCtoXC.Dan[5].On[2].Ura;
mind[788]:=UrnikSCtoXC.Dan[5].On[3].Mna;
mind[789]:=UrnikSCtoXC.Dan[5].On[3].Ura;
mind[790]:=UrnikSCtoXC.Dan[6].Off[1].Mna;
mind[791]:=UrnikSCtoXC.Dan[6].Off[1].Ura;
mind[792]:=UrnikSCtoXC.Dan[6].Off[2].Mna;
mind[793]:=UrnikSCtoXC.Dan[6].Off[2].Ura;
mind[794]:=UrnikSCtoXC.Dan[6].Off[3].Mna;
mind[795]:=UrnikSCtoXC.Dan[6].Off[3].Ura;
mind[796]:=UrnikSCtoXC.Dan[6].On[1].Mna;
mind[797]:=UrnikSCtoXC.Dan[6].On[1].Ura;
mind[798]:=UrnikSCtoXC.Dan[6].On[2].Mna;
mind[799]:=UrnikSCtoXC.Dan[6].On[2].Ura;
mind[800]:=UrnikSCtoXC.Dan[6].On[3].Mna;
mind[801]:=UrnikSCtoXC.Dan[6].On[3].Ura;
mind[802]:=UrnikSCtoXC.Dan[7].Off[1].Mna;
mind[803]:=UrnikSCtoXC.Dan[7].Off[1].Ura;
mind[804]:=UrnikSCtoXC.Dan[7].Off[2].Mna;
mind[805]:=UrnikSCtoXC.Dan[7].Off[2].Ura;
mind[806]:=UrnikSCtoXC.Dan[7].Off[3].Mna;
mind[807]:=UrnikSCtoXC.Dan[7].Off[3].Ura;
mind[808]:=UrnikSCtoXC.Dan[7].On[1].Mna;
mind[809]:=UrnikSCtoXC.Dan[7].On[1].Ura;
mind[810]:=UrnikSCtoXC.Dan[7].On[2].Mna;
mind[811]:=UrnikSCtoXC.Dan[7].On[2].Ura;
mind[812]:=UrnikSCtoXC.Dan[7].On[3].Mna;
mind[813]:=UrnikSCtoXC.Dan[7].On[3].Ura;
mind[814]:=UrnikXCtoSC.Dan[1].Off[1].Mna;
mind[815]:=UrnikXCtoSC.Dan[1].Off[1].Ura;
mind[816]:=UrnikXCtoSC.Dan[1].Off[2].Mna;
mind[817]:=UrnikXCtoSC.Dan[1].Off[2].Ura;
mind[818]:=UrnikXCtoSC.Dan[1].Off[3].Mna;
mind[819]:=UrnikXCtoSC.Dan[1].Off[3].Ura;
mind[820]:=UrnikXCtoSC.Dan[1].On[1].Mna;
mind[821]:=UrnikXCtoSC.Dan[1].On[1].Ura;
mind[822]:=UrnikXCtoSC.Dan[1].On[2].Mna;
mind[823]:=UrnikXCtoSC.Dan[1].On[2].Ura;
mind[824]:=UrnikXCtoSC.Dan[1].On[3].Mna;
mind[825]:=UrnikXCtoSC.Dan[1].On[3].Ura;
mind[826]:=UrnikXCtoSC.Dan[2].Off[1].Mna;
mind[827]:=UrnikXCtoSC.Dan[2].Off[1].Ura;
mind[828]:=UrnikXCtoSC.Dan[2].Off[2].Mna;
mind[829]:=UrnikXCtoSC.Dan[2].Off[2].Ura;
mind[830]:=UrnikXCtoSC.Dan[2].Off[3].Mna;
mind[831]:=UrnikXCtoSC.Dan[2].Off[3].Ura;
mind[832]:=UrnikXCtoSC.Dan[2].On[1].Mna;
mind[833]:=UrnikXCtoSC.Dan[2].On[1].Ura;
mind[834]:=UrnikXCtoSC.Dan[2].On[2].Mna;
mind[835]:=UrnikXCtoSC.Dan[2].On[2].Ura;
mind[836]:=UrnikXCtoSC.Dan[2].On[3].Mna;
mind[837]:=UrnikXCtoSC.Dan[2].On[3].Ura;
mind[838]:=UrnikXCtoSC.Dan[3].Off[1].Mna;
mind[839]:=UrnikXCtoSC.Dan[3].Off[1].Ura;
mind[840]:=UrnikXCtoSC.Dan[3].Off[2].Mna;
mind[841]:=UrnikXCtoSC.Dan[3].Off[2].Ura;
mind[842]:=UrnikXCtoSC.Dan[3].Off[3].Mna;
mind[843]:=UrnikXCtoSC.Dan[3].Off[3].Ura;
mind[844]:=UrnikXCtoSC.Dan[3].On[1].Mna;
mind[845]:=UrnikXCtoSC.Dan[3].On[1].Ura;
mind[846]:=UrnikXCtoSC.Dan[3].On[2].Mna;
mind[847]:=UrnikXCtoSC.Dan[3].On[2].Ura;
mind[848]:=UrnikXCtoSC.Dan[3].On[3].Mna;
mind[849]:=UrnikXCtoSC.Dan[3].On[3].Ura;
mind[850]:=UrnikXCtoSC.Dan[4].Off[1].Mna;
mind[851]:=UrnikXCtoSC.Dan[4].Off[1].Ura;
mind[852]:=UrnikXCtoSC.Dan[4].Off[2].Mna;
mind[853]:=UrnikXCtoSC.Dan[4].Off[2].Ura;
mind[854]:=UrnikXCtoSC.Dan[4].Off[3].Mna;
mind[855]:=UrnikXCtoSC.Dan[4].Off[3].Ura;
mind[856]:=UrnikXCtoSC.Dan[4].On[1].Mna;
mind[857]:=UrnikXCtoSC.Dan[4].On[1].Ura;
mind[858]:=UrnikXCtoSC.Dan[4].On[2].Mna;
mind[859]:=UrnikXCtoSC.Dan[4].On[2].Ura;
mind[860]:=UrnikXCtoSC.Dan[4].On[3].Mna;
mind[861]:=UrnikXCtoSC.Dan[4].On[3].Ura;
mind[862]:=UrnikXCtoSC.Dan[5].Off[1].Mna;
mind[863]:=UrnikXCtoSC.Dan[5].Off[1].Ura;
mind[864]:=UrnikXCtoSC.Dan[5].Off[2].Mna;
mind[865]:=UrnikXCtoSC.Dan[5].Off[2].Ura;
mind[866]:=UrnikXCtoSC.Dan[5].Off[3].Mna;
mind[867]:=UrnikXCtoSC.Dan[5].Off[3].Ura;
mind[868]:=UrnikXCtoSC.Dan[5].On[1].Mna;
mind[869]:=UrnikXCtoSC.Dan[5].On[1].Ura;
mind[870]:=UrnikXCtoSC.Dan[5].On[2].Mna;
mind[871]:=UrnikXCtoSC.Dan[5].On[2].Ura;
mind[872]:=UrnikXCtoSC.Dan[5].On[3].Mna;
mind[873]:=UrnikXCtoSC.Dan[5].On[3].Ura;
mind[874]:=UrnikXCtoSC.Dan[6].Off[1].Mna;
mind[875]:=UrnikXCtoSC.Dan[6].Off[1].Ura;
mind[876]:=UrnikXCtoSC.Dan[6].Off[2].Mna;
mind[877]:=UrnikXCtoSC.Dan[6].Off[2].Ura;
mind[878]:=UrnikXCtoSC.Dan[6].Off[3].Mna;
mind[879]:=UrnikXCtoSC.Dan[6].Off[3].Ura;
mind[880]:=UrnikXCtoSC.Dan[6].On[1].Mna;
mind[881]:=UrnikXCtoSC.Dan[6].On[1].Ura;
mind[882]:=UrnikXCtoSC.Dan[6].On[2].Mna;
mind[883]:=UrnikXCtoSC.Dan[6].On[2].Ura;
mind[884]:=UrnikXCtoSC.Dan[6].On[3].Mna;
mind[885]:=UrnikXCtoSC.Dan[6].On[3].Ura;
mind[886]:=UrnikXCtoSC.Dan[7].Off[1].Mna;
mind[887]:=UrnikXCtoSC.Dan[7].Off[1].Ura;
mind[888]:=UrnikXCtoSC.Dan[7].Off[2].Mna;
mind[889]:=UrnikXCtoSC.Dan[7].Off[2].Ura;
mind[890]:=UrnikXCtoSC.Dan[7].Off[3].Mna;
mind[891]:=UrnikXCtoSC.Dan[7].Off[3].Ura;
mind[892]:=UrnikXCtoSC.Dan[7].On[1].Mna;
mind[893]:=UrnikXCtoSC.Dan[7].On[1].Ura;
mind[894]:=UrnikXCtoSC.Dan[7].On[2].Mna;
mind[895]:=UrnikXCtoSC.Dan[7].On[2].Ura;
mind[896]:=UrnikXCtoSC.Dan[7].On[3].Mna;
mind[897]:=UrnikXCtoSC.Dan[7].On[3].Ura;
mind[898]:=UserCurrentLevel;
mind[899]:=CrpalkeGrfsGal.AlarmActiveCode;
mind[900]:=CrpalkeGrfsGal.AlarmCodeLog1;
mind[901]:=CrpalkeGrfsGal.AlarmCodeLog2;
mind[902]:=CrpalkeGrfsGal.AlarmCodeLog3;
mind[903]:=CrpalkeGrfsGal.AlarmCodeLog4;
mind[904]:=CrpalkeGrfsGal.AlarmCodeLog5;
mind[905]:=CrpalkeGrfsGal.AlarmGroupXVH[0];
mind[906]:=CrpalkeGrfsGal.AlarmGroupXVH[10];
mind[907]:=CrpalkeGrfsGal.AlarmGroupXVH[11];
mind[908]:=CrpalkeGrfsGal.AlarmGroupXVH[12];
mind[909]:=CrpalkeGrfsGal.AlarmGroupXVH[13];
mind[910]:=CrpalkeGrfsGal.AlarmGroupXVH[14];
mind[911]:=CrpalkeGrfsGal.AlarmGroupXVH[15];
mind[912]:=CrpalkeGrfsGal.AlarmGroupXVH[16];
mind[913]:=CrpalkeGrfsGal.AlarmGroupXVH[1];
mind[914]:=CrpalkeGrfsGal.AlarmGroupXVH[2];
mind[915]:=CrpalkeGrfsGal.AlarmGroupXVH[3];
mind[916]:=CrpalkeGrfsGal.AlarmGroupXVH[4];
mind[917]:=CrpalkeGrfsGal.AlarmGroupXVH[5];
mind[918]:=CrpalkeGrfsGal.AlarmGroupXVH[6];
mind[919]:=CrpalkeGrfsGal.AlarmGroupXVH[7];
mind[920]:=CrpalkeGrfsGal.AlarmGroupXVH[8];
mind[921]:=CrpalkeGrfsGal.AlarmGroupXVH[9];
mind[922]:=CrpalkeGrfsGal.AlarmQSD1;
mind[923]:=CrpalkeGrfsGal.AlarmQSD2;
mind[924]:=CrpalkeGrfsGal.AlarmStart1;
mind[925]:=CrpalkeGrfsGal.AlarmStart2;
mind[926]:=CrpalkeGrfsGal.AlarmStop1;
mind[927]:=CrpalkeGrfsGal.AlarmStop2;
mind[928]:=CrpalkeGrfsGal.AlarmStop3;
mind[929]:=CrpalkeGrfsGal.AlarmSurv1;
mind[930]:=CrpalkeGrfsGal.AlarmSurv2;
mind[931]:=CrpalkeGrfsGal.ControlSource;
mind[932]:=CrpalkeGrfsGal.ExternInputSetup;
mind[933]:=CrpalkeGrfsGal.ExternInputsStatus;
mind[934]:=CrpalkeGrfsGal.LocalSetupMode1;
mind[935]:=CrpalkeGrfsGal.PreklopkaMode;
mind[936]:=CrpalkeGrfsGal.Relay1setup;
mind[937]:=CrpalkeGrfsGal.RemoteSetupMode1;
mind[938]:=CrpalkeGrfsGal.StatusCrpalke;
mind[939]:=CrpalkeGrfsGal.StatusMode1;
mind[940]:=CrpalkeGrfsGal.StatusMode1co;
mind[941]:=CrpalkeGrfsGal.StatusMode1op;
mind[942]:=CrpalkeGrfsGal.StatusMode2;
mind[943]:=CrpalkeGrfsGal.StatusMode3;
mind[944]:=CrpGrfsPIDregTN;
mind[945]:=DateTime.DanVtednu;
mind[946]:=LetniCasDatumi[1,1,1];
mind[947]:=LetniCasDatumi[1,1,2];
mind[948]:=LetniCasDatumi[1,2,1];
mind[949]:=LetniCasDatumi[1,2,2];
mind[950]:=LetniCasDatumi[1,3,1];
mind[951]:=LetniCasDatumi[1,3,2];
mind[952]:=LetniCasDatumi[1,4,1];
mind[953]:=LetniCasDatumi[1,4,2];
mind[954]:=LetniCasDatumi[2,1,1];
mind[955]:=LetniCasDatumi[2,1,2];
mind[956]:=LetniCasDatumi[2,2,1];
mind[957]:=LetniCasDatumi[2,2,2];
mind[958]:=LetniCasDatumi[2,3,1];
mind[959]:=LetniCasDatumi[2,3,2];
mind[960]:=LetniCasDatumi[2,4,1];
mind[961]:=LetniCasDatumi[2,4,2];
mind[962]:=UrnikSave.Dan[1].Off[1].Mna;
mind[963]:=UrnikSave.Dan[1].Off[1].Ura;
mind[964]:=UrnikSave.Dan[1].Off[2].Mna;
mind[965]:=UrnikSave.Dan[1].Off[2].Ura;
mind[966]:=UrnikSave.Dan[1].Off[3].Mna;
mind[967]:=UrnikSave.Dan[1].Off[3].Ura;
mind[968]:=UrnikSave.Dan[1].On[1].Mna;
mind[969]:=UrnikSave.Dan[1].On[1].Ura;
mind[970]:=UrnikSave.Dan[1].On[2].Mna;
mind[971]:=UrnikSave.Dan[1].On[2].Ura;
mind[972]:=UrnikSave.Dan[1].On[3].Mna;
mind[973]:=UrnikSave.Dan[1].On[3].Ura;
mind[974]:=UrnikSave.Dan[2].Off[1].Mna;
mind[975]:=UrnikSave.Dan[2].Off[1].Ura;
mind[976]:=UrnikSave.Dan[2].Off[2].Mna;
mind[977]:=UrnikSave.Dan[2].Off[2].Ura;
mind[978]:=UrnikSave.Dan[2].Off[3].Mna;
mind[979]:=UrnikSave.Dan[2].Off[3].Ura;
mind[980]:=UrnikSave.Dan[2].On[1].Mna;
mind[981]:=UrnikSave.Dan[2].On[1].Ura;
mind[982]:=UrnikSave.Dan[2].On[2].Mna;
mind[983]:=UrnikSave.Dan[2].On[2].Ura;
mind[984]:=UrnikSave.Dan[2].On[3].Mna;
mind[985]:=UrnikSave.Dan[2].On[3].Ura;
mind[986]:=UrnikSave.Dan[3].Off[1].Mna;
mind[987]:=UrnikSave.Dan[3].Off[1].Ura;
mind[988]:=UrnikSave.Dan[3].Off[2].Mna;
mind[989]:=UrnikSave.Dan[3].Off[2].Ura;
mind[990]:=UrnikSave.Dan[3].Off[3].Mna;
mind[991]:=UrnikSave.Dan[3].Off[3].Ura;
mind[992]:=UrnikSave.Dan[3].On[1].Mna;
mind[993]:=UrnikSave.Dan[3].On[1].Ura;
mind[994]:=UrnikSave.Dan[3].On[2].Mna;
mind[995]:=UrnikSave.Dan[3].On[2].Ura;
mind[996]:=UrnikSave.Dan[3].On[3].Mna;
mind[997]:=UrnikSave.Dan[3].On[3].Ura;
mind[998]:=UrnikSave.Dan[4].Off[1].Mna;
mind[999]:=UrnikSave.Dan[4].Off[1].Ura;
mind[1000]:=UrnikSave.Dan[4].Off[2].Mna;
mind[1001]:=UrnikSave.Dan[4].Off[2].Ura;
mind[1002]:=UrnikSave.Dan[4].Off[3].Mna;
mind[1003]:=UrnikSave.Dan[4].Off[3].Ura;
mind[1004]:=UrnikSave.Dan[4].On[1].Mna;
mind[1005]:=UrnikSave.Dan[4].On[1].Ura;
mind[1006]:=UrnikSave.Dan[4].On[2].Mna;
mind[1007]:=UrnikSave.Dan[4].On[2].Ura;
mind[1008]:=UrnikSave.Dan[4].On[3].Mna;
mind[1009]:=UrnikSave.Dan[4].On[3].Ura;
mind[1010]:=UrnikSave.Dan[5].Off[1].Mna;
mind[1011]:=UrnikSave.Dan[5].Off[1].Ura;
mind[1012]:=UrnikSave.Dan[5].Off[2].Mna;
mind[1013]:=UrnikSave.Dan[5].Off[2].Ura;
mind[1014]:=UrnikSave.Dan[5].Off[3].Mna;
mind[1015]:=UrnikSave.Dan[5].Off[3].Ura;
mind[1016]:=UrnikSave.Dan[5].On[1].Mna;
mind[1017]:=UrnikSave.Dan[5].On[1].Ura;
mind[1018]:=UrnikSave.Dan[5].On[2].Mna;
mind[1019]:=UrnikSave.Dan[5].On[2].Ura;
mind[1020]:=UrnikSave.Dan[5].On[3].Mna;
mind[1021]:=UrnikSave.Dan[5].On[3].Ura;
mind[1022]:=UrnikSave.Dan[6].Off[1].Mna;
mind[1023]:=UrnikSave.Dan[6].Off[1].Ura;
mind[1024]:=UrnikSave.Dan[6].Off[2].Mna;
mind[1025]:=UrnikSave.Dan[6].Off[2].Ura;
mind[1026]:=UrnikSave.Dan[6].Off[3].Mna;
mind[1027]:=UrnikSave.Dan[6].Off[3].Ura;
mind[1028]:=UrnikSave.Dan[6].On[1].Mna;
mind[1029]:=UrnikSave.Dan[6].On[1].Ura;
mind[1030]:=UrnikSave.Dan[6].On[2].Mna;
mind[1031]:=UrnikSave.Dan[6].On[2].Ura;
mind[1032]:=UrnikSave.Dan[6].On[3].Mna;
mind[1033]:=UrnikSave.Dan[6].On[3].Ura;
mind[1034]:=UrnikSave.Dan[7].Off[1].Mna;
mind[1035]:=UrnikSave.Dan[7].Off[1].Ura;
mind[1036]:=UrnikSave.Dan[7].Off[2].Mna;
mind[1037]:=UrnikSave.Dan[7].Off[2].Ura;
mind[1038]:=UrnikSave.Dan[7].Off[3].Mna;
mind[1039]:=UrnikSave.Dan[7].Off[3].Ura;
mind[1040]:=UrnikSave.Dan[7].On[1].Mna;
mind[1041]:=UrnikSave.Dan[7].On[1].Ura;
mind[1042]:=UrnikSave.Dan[7].On[2].Mna;
mind[1043]:=UrnikSave.Dan[7].On[2].Ura;
mind[1044]:=UrnikSave.Dan[7].On[3].Mna;
mind[1045]:=UrnikSave.Dan[7].On[3].Ura;
mind[1046]:=XVH_CircNumber;
mind[1047]:=XVH_KompStatus[1];
mind[1048]:=XVH_KompStatus[2];
mind[1049]:=XVH_ReferencaUpper;
mind[1050]:=XVH_UPSstatus;
mind[1051]:=XVH_Urnik.Dan[1].Off[1].Mna;
mind[1052]:=XVH_Urnik.Dan[1].Off[1].Ura;
mind[1053]:=XVH_Urnik.Dan[1].Off[2].Mna;
mind[1054]:=XVH_Urnik.Dan[1].Off[2].Ura;
mind[1055]:=XVH_Urnik.Dan[1].Off[3].Mna;
mind[1056]:=XVH_Urnik.Dan[1].Off[3].Ura;
mind[1057]:=XVH_Urnik.Dan[1].On[1].Mna;
mind[1058]:=XVH_Urnik.Dan[1].On[1].Ura;
mind[1059]:=XVH_Urnik.Dan[1].On[2].Mna;
mind[1060]:=XVH_Urnik.Dan[1].On[2].Ura;
mind[1061]:=XVH_Urnik.Dan[1].On[3].Mna;
mind[1062]:=XVH_Urnik.Dan[1].On[3].Ura;
mind[1063]:=XVH_Urnik.Dan[2].Off[1].Mna;
mind[1064]:=XVH_Urnik.Dan[2].Off[1].Ura;
mind[1065]:=XVH_Urnik.Dan[2].Off[2].Mna;
mind[1066]:=XVH_Urnik.Dan[2].Off[2].Ura;
mind[1067]:=XVH_Urnik.Dan[2].Off[3].Mna;
mind[1068]:=XVH_Urnik.Dan[2].Off[3].Ura;
mind[1069]:=XVH_Urnik.Dan[2].On[1].Mna;
mind[1070]:=XVH_Urnik.Dan[2].On[1].Ura;
mind[1071]:=XVH_Urnik.Dan[2].On[2].Mna;
mind[1072]:=XVH_Urnik.Dan[2].On[2].Ura;
mind[1073]:=XVH_Urnik.Dan[2].On[3].Mna;
mind[1074]:=XVH_Urnik.Dan[2].On[3].Ura;
mind[1075]:=XVH_Urnik.Dan[3].Off[1].Mna;
mind[1076]:=XVH_Urnik.Dan[3].Off[1].Ura;
mind[1077]:=XVH_Urnik.Dan[3].Off[2].Mna;
mind[1078]:=XVH_Urnik.Dan[3].Off[2].Ura;
mind[1079]:=XVH_Urnik.Dan[3].Off[3].Mna;
mind[1080]:=XVH_Urnik.Dan[3].Off[3].Ura;
mind[1081]:=XVH_Urnik.Dan[3].On[1].Mna;
mind[1082]:=XVH_Urnik.Dan[3].On[1].Ura;
mind[1083]:=XVH_Urnik.Dan[3].On[2].Mna;
mind[1084]:=XVH_Urnik.Dan[3].On[2].Ura;
mind[1085]:=XVH_Urnik.Dan[3].On[3].Mna;
mind[1086]:=XVH_Urnik.Dan[3].On[3].Ura;
mind[1087]:=XVH_Urnik.Dan[4].Off[1].Mna;
mind[1088]:=XVH_Urnik.Dan[4].Off[1].Ura;
mind[1089]:=XVH_Urnik.Dan[4].Off[2].Mna;
mind[1090]:=XVH_Urnik.Dan[4].Off[2].Ura;
mind[1091]:=XVH_Urnik.Dan[4].Off[3].Mna;
mind[1092]:=XVH_Urnik.Dan[4].Off[3].Ura;
mind[1093]:=XVH_Urnik.Dan[4].On[1].Mna;
mind[1094]:=XVH_Urnik.Dan[4].On[1].Ura;
mind[1095]:=XVH_Urnik.Dan[4].On[2].Mna;
mind[1096]:=XVH_Urnik.Dan[4].On[2].Ura;
mind[1097]:=XVH_Urnik.Dan[4].On[3].Mna;
mind[1098]:=XVH_Urnik.Dan[4].On[3].Ura;
mind[1099]:=XVH_Urnik.Dan[5].Off[1].Mna;
mind[1100]:=XVH_Urnik.Dan[5].Off[1].Ura;
mind[1101]:=XVH_Urnik.Dan[5].Off[2].Mna;
mind[1102]:=XVH_Urnik.Dan[5].Off[2].Ura;
mind[1103]:=XVH_Urnik.Dan[5].Off[3].Mna;
mind[1104]:=XVH_Urnik.Dan[5].Off[3].Ura;
mind[1105]:=XVH_Urnik.Dan[5].On[1].Mna;
mind[1106]:=XVH_Urnik.Dan[5].On[1].Ura;
mind[1107]:=XVH_Urnik.Dan[5].On[2].Mna;
mind[1108]:=XVH_Urnik.Dan[5].On[2].Ura;
mind[1109]:=XVH_Urnik.Dan[5].On[3].Mna;
mind[1110]:=XVH_Urnik.Dan[5].On[3].Ura;
mind[1111]:=XVH_Urnik.Dan[6].Off[1].Mna;
mind[1112]:=XVH_Urnik.Dan[6].Off[1].Ura;
mind[1113]:=XVH_Urnik.Dan[6].Off[2].Mna;
mind[1114]:=XVH_Urnik.Dan[6].Off[2].Ura;
mind[1115]:=XVH_Urnik.Dan[6].Off[3].Mna;
mind[1116]:=XVH_Urnik.Dan[6].Off[3].Ura;
mind[1117]:=XVH_Urnik.Dan[6].On[1].Mna;
mind[1118]:=XVH_Urnik.Dan[6].On[1].Ura;
mind[1119]:=XVH_Urnik.Dan[6].On[2].Mna;
mind[1120]:=XVH_Urnik.Dan[6].On[2].Ura;
mind[1121]:=XVH_Urnik.Dan[6].On[3].Mna;
mind[1122]:=XVH_Urnik.Dan[6].On[3].Ura;
mind[1123]:=XVH_Urnik.Dan[7].Off[1].Mna;
mind[1124]:=XVH_Urnik.Dan[7].Off[1].Ura;
mind[1125]:=XVH_Urnik.Dan[7].Off[2].Mna;
mind[1126]:=XVH_Urnik.Dan[7].Off[2].Ura;
mind[1127]:=XVH_Urnik.Dan[7].Off[3].Mna;
mind[1128]:=XVH_Urnik.Dan[7].Off[3].Ura;
mind[1129]:=XVH_Urnik.Dan[7].On[1].Mna;
mind[1130]:=XVH_Urnik.Dan[7].On[1].Ura;
mind[1131]:=XVH_Urnik.Dan[7].On[2].Mna;
mind[1132]:=XVH_Urnik.Dan[7].On[2].Ura;
mind[1133]:=XVH_Urnik.Dan[7].On[3].Mna;
mind[1134]:=XVH_Urnik.Dan[7].On[3].Ura;
mind[1135]:=XVH_VentilTYValue[1,1];
mind[1136]:=XVH_VentilTYValue[1,2];
mind[1137]:=XVH_VentilTYValue[2,1];
mind[1138]:=XVH_VentilTYValue[2,2];
mind[1139]:=XVH_VentilTYValue[3,1];
mind[1140]:=XVH_VentilTYValue[3,2];
mind[1141]:=XVH_VentilTYValue[4,1];
mind[1142]:=XVH_VentilTYValue[4,2];
mind[1143]:=XVH_VlazilecStatus[1];
mind[1144]:=XVH_VlazilecStatus[2];
mind[1145]:=XVHnum[10];
mind[1146]:=XVHnum[11];
mind[1147]:=XVHnum[12];
mind[1148]:=XVHnum[13];
mind[1149]:=XVHnum[14];
mind[1150]:=XVHnum[1];
mind[1151]:=XVHnum[2];
mind[1152]:=XVHnum[3];
mind[1153]:=XVHnum[4];
mind[1154]:=XVHnum[5];
mind[1155]:=XVHnum[6];
mind[1156]:=XVHnum[7];
mind[1157]:=XVHnum[8];
mind[1158]:=XVHnum[9];
(*Branje UINT*)
(**)
mind[8000]:=kom_nast_cas_izpada;
(*Branje LONG*)
(**)
Read_dWord(rVar:=XVH_CrpalkaGrfsNum,lo:=4000,hi:=4001);
Read_dWord(rVar:=XVH_StUrnika,lo:=4002,hi:=4003);
(*Branje REAL*)
(**)
Read_Real(rVar:=ATVAlarmTemp,lo:=5000,hi:=5001);
Read_Real(rVar:=Circ[1].CosFi_III,lo:=5002,hi:=5003);
Read_Real(rVar:=Circ[1].DelovnaEnergija,lo:=5004,hi:=5005);
Read_Real(rVar:=Circ[1].DelovnaMoc_III,lo:=5006,hi:=5007);
Read_Real(rVar:=Circ[1].DelovnaMoc_L1,lo:=5008,hi:=5009);
Read_Real(rVar:=Circ[1].DelovnaMoc_L2,lo:=5010,hi:=5011);
Read_Real(rVar:=Circ[1].DelovnaMoc_L3,lo:=5012,hi:=5013);
Read_Real(rVar:=Circ[1].Frekvenca_L1,lo:=5014,hi:=5015);
Read_Real(rVar:=Circ[1].InduktivnaEnergija,lo:=5016,hi:=5017);
Read_Real(rVar:=Circ[1].InduktivnaMoc_III,lo:=5018,hi:=5019);
Read_Real(rVar:=Circ[1].JalovaMoc_L1,lo:=5020,hi:=5021);
Read_Real(rVar:=Circ[1].JalovaMoc_L2,lo:=5022,hi:=5023);
Read_Real(rVar:=Circ[1].JalovaMoc_L3,lo:=5024,hi:=5025);
Read_Real(rVar:=Circ[1].KapacitivnaEnergija,lo:=5026,hi:=5027);
Read_Real(rVar:=Circ[1].KapacitivnaMoc_III,lo:=5028,hi:=5029);
Read_Real(rVar:=Circ[1].MaximumDemand,lo:=5030,hi:=5031);
Read_Real(rVar:=Circ[1].Napetost_L1_L2,lo:=5032,hi:=5033);
Read_Real(rVar:=Circ[1].Napetost_L1_N,lo:=5034,hi:=5035);
Read_Real(rVar:=Circ[1].Napetost_L2_L3,lo:=5036,hi:=5037);
Read_Real(rVar:=Circ[1].Napetost_L2_N,lo:=5038,hi:=5039);
Read_Real(rVar:=Circ[1].Napetost_L3_L1,lo:=5040,hi:=5041);
Read_Real(rVar:=Circ[1].Napetost_L3_N,lo:=5042,hi:=5043);
Read_Real(rVar:=Circ[1].NavideznaMoc_III,lo:=5044,hi:=5045);
Read_Real(rVar:=Circ[1].NicelniTok,lo:=5046,hi:=5047);
Read_Real(rVar:=Circ[1].PowerFactor_III,lo:=5048,hi:=5049);
Read_Real(rVar:=Circ[1].PowerFactor_L1,lo:=5050,hi:=5051);
Read_Real(rVar:=Circ[1].PowerFactor_L2,lo:=5052,hi:=5053);
Read_Real(rVar:=Circ[1].PowerFactor_L3,lo:=5054,hi:=5055);
Read_Real(rVar:=Circ[1].THDI_L1,lo:=5056,hi:=5057);
Read_Real(rVar:=Circ[1].THDI_L2,lo:=5058,hi:=5059);
Read_Real(rVar:=Circ[1].THDI_L3,lo:=5060,hi:=5061);
Read_Real(rVar:=Circ[1].THDV_L1,lo:=5062,hi:=5063);
Read_Real(rVar:=Circ[1].THDV_L2,lo:=5064,hi:=5065);
Read_Real(rVar:=Circ[1].THDV_L3,lo:=5066,hi:=5067);
Read_Real(rVar:=Circ[1].Tok_L1,lo:=5068,hi:=5069);
Read_Real(rVar:=Circ[1].Tok_L2,lo:=5070,hi:=5071);
Read_Real(rVar:=Circ[1].Tok_L3,lo:=5072,hi:=5073);
Read_Real(rVar:=Circ[1].TokPovprecje_III,lo:=5074,hi:=5075);
Read_Real(rVar:=CrpalkeDnfs[1].Current,lo:=5076,hi:=5077);
Read_Real(rVar:=CrpalkeDnfs[1].StarterStatus,lo:=5078,hi:=5079);
Read_Real(rVar:=CrpalkeDnfs[1].Temerature,lo:=5080,hi:=5081);
Read_Real(rVar:=CrpalkeDnfs[1].TripCode,lo:=5082,hi:=5083);
Read_Real(rVar:=CrpalkeDnfs[1].UreXC200,lo:=5084,hi:=5085);
Read_Real(rVar:=CrpalkeDnfs[2].Current,lo:=5086,hi:=5087);
Read_Real(rVar:=CrpalkeDnfs[2].StarterStatus,lo:=5088,hi:=5089);
Read_Real(rVar:=CrpalkeDnfs[2].Temerature,lo:=5090,hi:=5091);
Read_Real(rVar:=CrpalkeDnfs[2].TripCode,lo:=5092,hi:=5093);
Read_Real(rVar:=CrpalkeDnfs[2].UreXC200,lo:=5094,hi:=5095);
Read_Real(rVar:=CrpalkeDnfs[3].Current,lo:=5096,hi:=5097);
Read_Real(rVar:=CrpalkeDnfs[3].StarterStatus,lo:=5098,hi:=5099);
Read_Real(rVar:=CrpalkeDnfs[3].Temerature,lo:=5100,hi:=5101);
Read_Real(rVar:=CrpalkeDnfs[3].TripCode,lo:=5102,hi:=5103);
Read_Real(rVar:=CrpalkeDnfs[3].UreXC200,lo:=5104,hi:=5105);
Read_Real(rVar:=CrpalkeDnfs[4].Current,lo:=5106,hi:=5107);
Read_Real(rVar:=CrpalkeDnfs[4].StarterStatus,lo:=5108,hi:=5109);
Read_Real(rVar:=CrpalkeDnfs[4].Temerature,lo:=5110,hi:=5111);
Read_Real(rVar:=CrpalkeDnfs[4].TripCode,lo:=5112,hi:=5113);
Read_Real(rVar:=CrpalkeDnfs[4].UreXC200,lo:=5114,hi:=5115);
Read_Real(rVar:=CrpalkeGrfs[10].DeltaSetPoint,lo:=5116,hi:=5117);
Read_Real(rVar:=CrpalkeGrfs[10].EnergijaPoraba,lo:=5118,hi:=5119);
Read_Real(rVar:=CrpalkeGrfs[10].FrekPretvornikDCNapetost,lo:=5120,hi:=5121);
Read_Real(rVar:=CrpalkeGrfs[10].FrekPretvornikDCTok,lo:=5122,hi:=5123);
Read_Real(rVar:=CrpalkeGrfs[10].FreqMax,lo:=5124,hi:=5125);
Read_Real(rVar:=CrpalkeGrfs[10].FreqMin,lo:=5126,hi:=5127);
Read_Real(rVar:=CrpalkeGrfs[10].FreqUpper,lo:=5128,hi:=5129);
Read_Real(rVar:=CrpalkeGrfs[10].MocMax,lo:=5130,hi:=5131);
Read_Real(rVar:=CrpalkeGrfs[10].MocTrenutna,lo:=5132,hi:=5133);
Read_Real(rVar:=CrpalkeGrfs[10].MotorHitrost,lo:=5134,hi:=5135);
Read_Real(rVar:=CrpalkeGrfs[10].MotorTok,lo:=5136,hi:=5137);
Read_Real(rVar:=CrpalkeGrfs[10].NapajanjeTok,lo:=5138,hi:=5139);
Read_Real(rVar:=CrpalkeGrfs[10].NastavitevLokalna,lo:=5140,hi:=5141);
Read_Real(rVar:=CrpalkeGrfs[10].NastavitevTrenutna,lo:=5142,hi:=5143);
Read_Real(rVar:=CrpalkeGrfs[10].PretokMax,lo:=5144,hi:=5145);
Read_Real(rVar:=CrpalkeGrfs[10].PretokMin,lo:=5146,hi:=5147);
Read_Real(rVar:=CrpalkeGrfs[10].PretokTrenutni,lo:=5148,hi:=5149);
Read_Real(rVar:=CrpalkeGrfs[10].PritiskMax,lo:=5150,hi:=5151);
Read_Real(rVar:=CrpalkeGrfs[10].PritiskTrenutni,lo:=5152,hi:=5153);
Read_Real(rVar:=CrpalkeGrfs[10].ReferencaMotorjaHzV,lo:=5154,hi:=5155);
Read_Real(rVar:=CrpalkeGrfs[10].ReferencaRemote,lo:=5156,hi:=5157);
Read_Real(rVar:=CrpalkeGrfs[10].StevecUr2h,lo:=5158,hi:=5159);
Read_Real(rVar:=CrpalkeGrfs[10].SystemFeedback,lo:=5160,hi:=5161);
Read_Real(rVar:=CrpalkeGrfs[10].SystemReference,lo:=5162,hi:=5163);
Read_Real(rVar:=CrpalkeGrfs[10].TemperaturaMotorja,lo:=5164,hi:=5165);
Read_Real(rVar:=CrpalkeGrfs[10].UreXC200,lo:=5166,hi:=5167);
Read_Real(rVar:=CrpalkeGrfs[11].DeltaSetPoint,lo:=5168,hi:=5169);
Read_Real(rVar:=CrpalkeGrfs[11].EnergijaPoraba,lo:=5170,hi:=5171);
Read_Real(rVar:=CrpalkeGrfs[11].FrekPretvornikDCNapetost,lo:=5172,hi:=5173);
Read_Real(rVar:=CrpalkeGrfs[11].FrekPretvornikDCTok,lo:=5174,hi:=5175);
Read_Real(rVar:=CrpalkeGrfs[11].FreqMax,lo:=5176,hi:=5177);
Read_Real(rVar:=CrpalkeGrfs[11].FreqMin,lo:=5178,hi:=5179);
Read_Real(rVar:=CrpalkeGrfs[11].FreqUpper,lo:=5180,hi:=5181);
Read_Real(rVar:=CrpalkeGrfs[11].MocMax,lo:=5182,hi:=5183);
Read_Real(rVar:=CrpalkeGrfs[11].MocTrenutna,lo:=5184,hi:=5185);
Read_Real(rVar:=CrpalkeGrfs[11].MotorHitrost,lo:=5186,hi:=5187);
Read_Real(rVar:=CrpalkeGrfs[11].MotorTok,lo:=5188,hi:=5189);
Read_Real(rVar:=CrpalkeGrfs[11].NapajanjeTok,lo:=5190,hi:=5191);
Read_Real(rVar:=CrpalkeGrfs[11].NastavitevLokalna,lo:=5192,hi:=5193);
Read_Real(rVar:=CrpalkeGrfs[11].NastavitevTrenutna,lo:=5194,hi:=5195);
Read_Real(rVar:=CrpalkeGrfs[11].PretokMax,lo:=5196,hi:=5197);
Read_Real(rVar:=CrpalkeGrfs[11].PretokMin,lo:=5198,hi:=5199);
Read_Real(rVar:=CrpalkeGrfs[11].PretokTrenutni,lo:=5200,hi:=5201);
Read_Real(rVar:=CrpalkeGrfs[11].PritiskMax,lo:=5202,hi:=5203);
Read_Real(rVar:=CrpalkeGrfs[11].PritiskTrenutni,lo:=5204,hi:=5205);
Read_Real(rVar:=CrpalkeGrfs[11].ReferencaMotorjaHzV,lo:=5206,hi:=5207);
Read_Real(rVar:=CrpalkeGrfs[11].ReferencaRemote,lo:=5208,hi:=5209);
Read_Real(rVar:=CrpalkeGrfs[11].StevecUr2h,lo:=5210,hi:=5211);
Read_Real(rVar:=CrpalkeGrfs[11].SystemFeedback,lo:=5212,hi:=5213);
Read_Real(rVar:=CrpalkeGrfs[11].SystemReference,lo:=5214,hi:=5215);
Read_Real(rVar:=CrpalkeGrfs[11].TemperaturaMotorja,lo:=5216,hi:=5217);
Read_Real(rVar:=CrpalkeGrfs[11].UreXC200,lo:=5218,hi:=5219);
Read_Real(rVar:=CrpalkeGrfs[12].DeltaSetPoint,lo:=5220,hi:=5221);
Read_Real(rVar:=CrpalkeGrfs[12].EnergijaPoraba,lo:=5222,hi:=5223);
Read_Real(rVar:=CrpalkeGrfs[12].FrekPretvornikDCNapetost,lo:=5224,hi:=5225);
Read_Real(rVar:=CrpalkeGrfs[12].FrekPretvornikDCTok,lo:=5226,hi:=5227);
Read_Real(rVar:=CrpalkeGrfs[12].FreqMax,lo:=5228,hi:=5229);
Read_Real(rVar:=CrpalkeGrfs[12].FreqMin,lo:=5230,hi:=5231);
Read_Real(rVar:=CrpalkeGrfs[12].FreqUpper,lo:=5232,hi:=5233);
Read_Real(rVar:=CrpalkeGrfs[12].MocMax,lo:=5234,hi:=5235);
Read_Real(rVar:=CrpalkeGrfs[12].MocTrenutna,lo:=5236,hi:=5237);
Read_Real(rVar:=CrpalkeGrfs[12].MotorHitrost,lo:=5238,hi:=5239);
Read_Real(rVar:=CrpalkeGrfs[12].MotorTok,lo:=5240,hi:=5241);
Read_Real(rVar:=CrpalkeGrfs[12].NapajanjeTok,lo:=5242,hi:=5243);
Read_Real(rVar:=CrpalkeGrfs[12].NastavitevLokalna,lo:=5244,hi:=5245);
Read_Real(rVar:=CrpalkeGrfs[12].NastavitevTrenutna,lo:=5246,hi:=5247);
Read_Real(rVar:=CrpalkeGrfs[12].PretokMax,lo:=5248,hi:=5249);
Read_Real(rVar:=CrpalkeGrfs[12].PretokMin,lo:=5250,hi:=5251);
Read_Real(rVar:=CrpalkeGrfs[12].PretokTrenutni,lo:=5252,hi:=5253);
Read_Real(rVar:=CrpalkeGrfs[12].PritiskMax,lo:=5254,hi:=5255);
Read_Real(rVar:=CrpalkeGrfs[12].PritiskTrenutni,lo:=5256,hi:=5257);
Read_Real(rVar:=CrpalkeGrfs[12].ReferencaMotorjaHzV,lo:=5258,hi:=5259);
Read_Real(rVar:=CrpalkeGrfs[12].ReferencaRemote,lo:=5260,hi:=5261);
Read_Real(rVar:=CrpalkeGrfs[12].StevecUr2h,lo:=5262,hi:=5263);
Read_Real(rVar:=CrpalkeGrfs[12].SystemFeedback,lo:=5264,hi:=5265);
Read_Real(rVar:=CrpalkeGrfs[12].SystemReference,lo:=5266,hi:=5267);
Read_Real(rVar:=CrpalkeGrfs[12].TemperaturaMotorja,lo:=5268,hi:=5269);
Read_Real(rVar:=CrpalkeGrfs[12].UreXC200,lo:=5270,hi:=5271);
Read_Real(rVar:=CrpalkeGrfs[13].DeltaSetPoint,lo:=5272,hi:=5273);
Read_Real(rVar:=CrpalkeGrfs[13].EnergijaPoraba,lo:=5274,hi:=5275);
Read_Real(rVar:=CrpalkeGrfs[13].FrekPretvornikDCNapetost,lo:=5276,hi:=5277);
Read_Real(rVar:=CrpalkeGrfs[13].FrekPretvornikDCTok,lo:=5278,hi:=5279);
Read_Real(rVar:=CrpalkeGrfs[13].FreqMax,lo:=5280,hi:=5281);
Read_Real(rVar:=CrpalkeGrfs[13].FreqMin,lo:=5282,hi:=5283);
Read_Real(rVar:=CrpalkeGrfs[13].FreqUpper,lo:=5284,hi:=5285);
Read_Real(rVar:=CrpalkeGrfs[13].MocMax,lo:=5286,hi:=5287);
Read_Real(rVar:=CrpalkeGrfs[13].MocTrenutna,lo:=5288,hi:=5289);
Read_Real(rVar:=CrpalkeGrfs[13].MotorHitrost,lo:=5290,hi:=5291);
Read_Real(rVar:=CrpalkeGrfs[13].MotorTok,lo:=5292,hi:=5293);
Read_Real(rVar:=CrpalkeGrfs[13].NapajanjeTok,lo:=5294,hi:=5295);
Read_Real(rVar:=CrpalkeGrfs[13].NastavitevLokalna,lo:=5296,hi:=5297);
Read_Real(rVar:=CrpalkeGrfs[13].NastavitevTrenutna,lo:=5298,hi:=5299);
Read_Real(rVar:=CrpalkeGrfs[13].PretokMax,lo:=5300,hi:=5301);
Read_Real(rVar:=CrpalkeGrfs[13].PretokMin,lo:=5302,hi:=5303);
Read_Real(rVar:=CrpalkeGrfs[13].PretokTrenutni,lo:=5304,hi:=5305);
Read_Real(rVar:=CrpalkeGrfs[13].PritiskMax,lo:=5306,hi:=5307);
Read_Real(rVar:=CrpalkeGrfs[13].PritiskTrenutni,lo:=5308,hi:=5309);
Read_Real(rVar:=CrpalkeGrfs[13].ReferencaMotorjaHzV,lo:=5310,hi:=5311);
Read_Real(rVar:=CrpalkeGrfs[13].ReferencaRemote,lo:=5312,hi:=5313);
Read_Real(rVar:=CrpalkeGrfs[13].StevecUr2h,lo:=5314,hi:=5315);
Read_Real(rVar:=CrpalkeGrfs[13].SystemFeedback,lo:=5316,hi:=5317);
Read_Real(rVar:=CrpalkeGrfs[13].SystemReference,lo:=5318,hi:=5319);
Read_Real(rVar:=CrpalkeGrfs[13].TemperaturaMotorja,lo:=5320,hi:=5321);
Read_Real(rVar:=CrpalkeGrfs[13].UreXC200,lo:=5322,hi:=5323);
Read_Real(rVar:=CrpalkeGrfs[14].DeltaSetPoint,lo:=5324,hi:=5325);
Read_Real(rVar:=CrpalkeGrfs[14].EnergijaPoraba,lo:=5326,hi:=5327);
Read_Real(rVar:=CrpalkeGrfs[14].FrekPretvornikDCNapetost,lo:=5328,hi:=5329);
Read_Real(rVar:=CrpalkeGrfs[14].FrekPretvornikDCTok,lo:=5330,hi:=5331);
Read_Real(rVar:=CrpalkeGrfs[14].FreqMax,lo:=5332,hi:=5333);
Read_Real(rVar:=CrpalkeGrfs[14].FreqMin,lo:=5334,hi:=5335);
Read_Real(rVar:=CrpalkeGrfs[14].FreqUpper,lo:=5336,hi:=5337);
Read_Real(rVar:=CrpalkeGrfs[14].MocMax,lo:=5338,hi:=5339);
Read_Real(rVar:=CrpalkeGrfs[14].MocTrenutna,lo:=5340,hi:=5341);
Read_Real(rVar:=CrpalkeGrfs[14].MotorHitrost,lo:=5342,hi:=5343);
Read_Real(rVar:=CrpalkeGrfs[14].MotorTok,lo:=5344,hi:=5345);
Read_Real(rVar:=CrpalkeGrfs[14].NapajanjeTok,lo:=5346,hi:=5347);
Read_Real(rVar:=CrpalkeGrfs[14].NastavitevLokalna,lo:=5348,hi:=5349);
Read_Real(rVar:=CrpalkeGrfs[14].NastavitevTrenutna,lo:=5350,hi:=5351);
Read_Real(rVar:=CrpalkeGrfs[14].PretokMax,lo:=5352,hi:=5353);
Read_Real(rVar:=CrpalkeGrfs[14].PretokMin,lo:=5354,hi:=5355);
Read_Real(rVar:=CrpalkeGrfs[14].PretokTrenutni,lo:=5356,hi:=5357);
Read_Real(rVar:=CrpalkeGrfs[14].PritiskMax,lo:=5358,hi:=5359);
Read_Real(rVar:=CrpalkeGrfs[14].PritiskTrenutni,lo:=5360,hi:=5361);
Read_Real(rVar:=CrpalkeGrfs[14].ReferencaMotorjaHzV,lo:=5362,hi:=5363);
Read_Real(rVar:=CrpalkeGrfs[14].ReferencaRemote,lo:=5364,hi:=5365);
Read_Real(rVar:=CrpalkeGrfs[14].StevecUr2h,lo:=5366,hi:=5367);
Read_Real(rVar:=CrpalkeGrfs[14].SystemFeedback,lo:=5368,hi:=5369);
Read_Real(rVar:=CrpalkeGrfs[14].SystemReference,lo:=5370,hi:=5371);
Read_Real(rVar:=CrpalkeGrfs[14].TemperaturaMotorja,lo:=5372,hi:=5373);
Read_Real(rVar:=CrpalkeGrfs[14].UreXC200,lo:=5374,hi:=5375);
Read_Real(rVar:=CrpalkeGrfs[1].DeltaSetPoint,lo:=5376,hi:=5377);
Read_Real(rVar:=CrpalkeGrfs[1].EnergijaPoraba,lo:=5378,hi:=5379);
Read_Real(rVar:=CrpalkeGrfs[1].FrekPretvornikDCNapetost,lo:=5380,hi:=5381);
Read_Real(rVar:=CrpalkeGrfs[1].FrekPretvornikDCTok,lo:=5382,hi:=5383);
Read_Real(rVar:=CrpalkeGrfs[1].FreqMax,lo:=5384,hi:=5385);
Read_Real(rVar:=CrpalkeGrfs[1].FreqMin,lo:=5386,hi:=5387);
Read_Real(rVar:=CrpalkeGrfs[1].FreqUpper,lo:=5388,hi:=5389);
Read_Real(rVar:=CrpalkeGrfs[1].MocMax,lo:=5390,hi:=5391);
Read_Real(rVar:=CrpalkeGrfs[1].MocTrenutna,lo:=5392,hi:=5393);
Read_Real(rVar:=CrpalkeGrfs[1].MotorHitrost,lo:=5394,hi:=5395);
Read_Real(rVar:=CrpalkeGrfs[1].MotorTok,lo:=5396,hi:=5397);
Read_Real(rVar:=CrpalkeGrfs[1].NapajanjeTok,lo:=5398,hi:=5399);
Read_Real(rVar:=CrpalkeGrfs[1].NastavitevLokalna,lo:=5400,hi:=5401);
Read_Real(rVar:=CrpalkeGrfs[1].NastavitevTrenutna,lo:=5402,hi:=5403);
Read_Real(rVar:=CrpalkeGrfs[1].PretokMax,lo:=5404,hi:=5405);
Read_Real(rVar:=CrpalkeGrfs[1].PretokMin,lo:=5406,hi:=5407);
Read_Real(rVar:=CrpalkeGrfs[1].PretokTrenutni,lo:=5408,hi:=5409);
Read_Real(rVar:=CrpalkeGrfs[1].PritiskMax,lo:=5410,hi:=5411);
Read_Real(rVar:=CrpalkeGrfs[1].PritiskTrenutni,lo:=5412,hi:=5413);
Read_Real(rVar:=CrpalkeGrfs[1].ReferencaMotorjaHzV,lo:=5414,hi:=5415);
Read_Real(rVar:=CrpalkeGrfs[1].ReferencaRemote,lo:=5416,hi:=5417);
Read_Real(rVar:=CrpalkeGrfs[1].StevecUr2h,lo:=5418,hi:=5419);
Read_Real(rVar:=CrpalkeGrfs[1].SystemFeedback,lo:=5420,hi:=5421);
Read_Real(rVar:=CrpalkeGrfs[1].SystemReference,lo:=5422,hi:=5423);
Read_Real(rVar:=CrpalkeGrfs[1].TemperaturaMotorja,lo:=5424,hi:=5425);
Read_Real(rVar:=CrpalkeGrfs[1].UreXC200,lo:=5426,hi:=5427);
Read_Real(rVar:=CrpalkeGrfs[2].DeltaSetPoint,lo:=5428,hi:=5429);
Read_Real(rVar:=CrpalkeGrfs[2].EnergijaPoraba,lo:=5430,hi:=5431);
Read_Real(rVar:=CrpalkeGrfs[2].FrekPretvornikDCNapetost,lo:=5432,hi:=5433);
Read_Real(rVar:=CrpalkeGrfs[2].FrekPretvornikDCTok,lo:=5434,hi:=5435);
Read_Real(rVar:=CrpalkeGrfs[2].FreqMax,lo:=5436,hi:=5437);
Read_Real(rVar:=CrpalkeGrfs[2].FreqMin,lo:=5438,hi:=5439);
Read_Real(rVar:=CrpalkeGrfs[2].FreqUpper,lo:=5440,hi:=5441);
Read_Real(rVar:=CrpalkeGrfs[2].MocMax,lo:=5442,hi:=5443);
Read_Real(rVar:=CrpalkeGrfs[2].MocTrenutna,lo:=5444,hi:=5445);
Read_Real(rVar:=CrpalkeGrfs[2].MotorHitrost,lo:=5446,hi:=5447);
Read_Real(rVar:=CrpalkeGrfs[2].MotorTok,lo:=5448,hi:=5449);
Read_Real(rVar:=CrpalkeGrfs[2].NapajanjeTok,lo:=5450,hi:=5451);
Read_Real(rVar:=CrpalkeGrfs[2].NastavitevLokalna,lo:=5452,hi:=5453);
Read_Real(rVar:=CrpalkeGrfs[2].NastavitevTrenutna,lo:=5454,hi:=5455);
Read_Real(rVar:=CrpalkeGrfs[2].PretokMax,lo:=5456,hi:=5457);
Read_Real(rVar:=CrpalkeGrfs[2].PretokMin,lo:=5458,hi:=5459);
Read_Real(rVar:=CrpalkeGrfs[2].PretokTrenutni,lo:=5460,hi:=5461);
Read_Real(rVar:=CrpalkeGrfs[2].PritiskMax,lo:=5462,hi:=5463);
Read_Real(rVar:=CrpalkeGrfs[2].PritiskTrenutni,lo:=5464,hi:=5465);
Read_Real(rVar:=CrpalkeGrfs[2].ReferencaMotorjaHzV,lo:=5466,hi:=5467);
Read_Real(rVar:=CrpalkeGrfs[2].ReferencaRemote,lo:=5468,hi:=5469);
Read_Real(rVar:=CrpalkeGrfs[2].StevecUr2h,lo:=5470,hi:=5471);
Read_Real(rVar:=CrpalkeGrfs[2].SystemFeedback,lo:=5472,hi:=5473);
Read_Real(rVar:=CrpalkeGrfs[2].SystemReference,lo:=5474,hi:=5475);
Read_Real(rVar:=CrpalkeGrfs[2].TemperaturaMotorja,lo:=5476,hi:=5477);
Read_Real(rVar:=CrpalkeGrfs[2].UreXC200,lo:=5478,hi:=5479);
Read_Real(rVar:=CrpalkeGrfs[3].DeltaSetPoint,lo:=5480,hi:=5481);
Read_Real(rVar:=CrpalkeGrfs[3].EnergijaPoraba,lo:=5482,hi:=5483);
Read_Real(rVar:=CrpalkeGrfs[3].FrekPretvornikDCNapetost,lo:=5484,hi:=5485);
Read_Real(rVar:=CrpalkeGrfs[3].FrekPretvornikDCTok,lo:=5486,hi:=5487);
Read_Real(rVar:=CrpalkeGrfs[3].FreqMax,lo:=5488,hi:=5489);
Read_Real(rVar:=CrpalkeGrfs[3].FreqMin,lo:=5490,hi:=5491);
Read_Real(rVar:=CrpalkeGrfs[3].FreqUpper,lo:=5492,hi:=5493);
Read_Real(rVar:=CrpalkeGrfs[3].MocMax,lo:=5494,hi:=5495);
Read_Real(rVar:=CrpalkeGrfs[3].MocTrenutna,lo:=5496,hi:=5497);
Read_Real(rVar:=CrpalkeGrfs[3].MotorHitrost,lo:=5498,hi:=5499);
Read_Real(rVar:=CrpalkeGrfs[3].MotorTok,lo:=5500,hi:=5501);
Read_Real(rVar:=CrpalkeGrfs[3].NapajanjeTok,lo:=5502,hi:=5503);
Read_Real(rVar:=CrpalkeGrfs[3].NastavitevLokalna,lo:=5504,hi:=5505);
Read_Real(rVar:=CrpalkeGrfs[3].NastavitevTrenutna,lo:=5506,hi:=5507);
Read_Real(rVar:=CrpalkeGrfs[3].PretokMax,lo:=5508,hi:=5509);
Read_Real(rVar:=CrpalkeGrfs[3].PretokMin,lo:=5510,hi:=5511);
Read_Real(rVar:=CrpalkeGrfs[3].PretokTrenutni,lo:=5512,hi:=5513);
Read_Real(rVar:=CrpalkeGrfs[3].PritiskMax,lo:=5514,hi:=5515);
Read_Real(rVar:=CrpalkeGrfs[3].PritiskTrenutni,lo:=5516,hi:=5517);
Read_Real(rVar:=CrpalkeGrfs[3].ReferencaMotorjaHzV,lo:=5518,hi:=5519);
Read_Real(rVar:=CrpalkeGrfs[3].ReferencaRemote,lo:=5520,hi:=5521);
Read_Real(rVar:=CrpalkeGrfs[3].StevecUr2h,lo:=5522,hi:=5523);
Read_Real(rVar:=CrpalkeGrfs[3].SystemFeedback,lo:=5524,hi:=5525);
Read_Real(rVar:=CrpalkeGrfs[3].SystemReference,lo:=5526,hi:=5527);
Read_Real(rVar:=CrpalkeGrfs[3].TemperaturaMotorja,lo:=5528,hi:=5529);
Read_Real(rVar:=CrpalkeGrfs[3].UreXC200,lo:=5530,hi:=5531);
Read_Real(rVar:=CrpalkeGrfs[4].DeltaSetPoint,lo:=5532,hi:=5533);
Read_Real(rVar:=CrpalkeGrfs[4].EnergijaPoraba,lo:=5534,hi:=5535);
Read_Real(rVar:=CrpalkeGrfs[4].FrekPretvornikDCNapetost,lo:=5536,hi:=5537);
Read_Real(rVar:=CrpalkeGrfs[4].FrekPretvornikDCTok,lo:=5538,hi:=5539);
Read_Real(rVar:=CrpalkeGrfs[4].FreqMax,lo:=5540,hi:=5541);
Read_Real(rVar:=CrpalkeGrfs[4].FreqMin,lo:=5542,hi:=5543);
Read_Real(rVar:=CrpalkeGrfs[4].FreqUpper,lo:=5544,hi:=5545);
Read_Real(rVar:=CrpalkeGrfs[4].MocMax,lo:=5546,hi:=5547);
Read_Real(rVar:=CrpalkeGrfs[4].MocTrenutna,lo:=5548,hi:=5549);
Read_Real(rVar:=CrpalkeGrfs[4].MotorHitrost,lo:=5550,hi:=5551);
Read_Real(rVar:=CrpalkeGrfs[4].MotorTok,lo:=5552,hi:=5553);
Read_Real(rVar:=CrpalkeGrfs[4].NapajanjeTok,lo:=5554,hi:=5555);
Read_Real(rVar:=CrpalkeGrfs[4].NastavitevLokalna,lo:=5556,hi:=5557);
Read_Real(rVar:=CrpalkeGrfs[4].NastavitevTrenutna,lo:=5558,hi:=5559);
Read_Real(rVar:=CrpalkeGrfs[4].PretokMax,lo:=5560,hi:=5561);
Read_Real(rVar:=CrpalkeGrfs[4].PretokMin,lo:=5562,hi:=5563);
Read_Real(rVar:=CrpalkeGrfs[4].PretokTrenutni,lo:=5564,hi:=5565);
Read_Real(rVar:=CrpalkeGrfs[4].PritiskMax,lo:=5566,hi:=5567);
Read_Real(rVar:=CrpalkeGrfs[4].PritiskTrenutni,lo:=5568,hi:=5569);
Read_Real(rVar:=CrpalkeGrfs[4].ReferencaMotorjaHzV,lo:=5570,hi:=5571);
Read_Real(rVar:=CrpalkeGrfs[4].ReferencaRemote,lo:=5572,hi:=5573);
Read_Real(rVar:=CrpalkeGrfs[4].StevecUr2h,lo:=5574,hi:=5575);
Read_Real(rVar:=CrpalkeGrfs[4].SystemFeedback,lo:=5576,hi:=5577);
Read_Real(rVar:=CrpalkeGrfs[4].SystemReference,lo:=5578,hi:=5579);
Read_Real(rVar:=CrpalkeGrfs[4].TemperaturaMotorja,lo:=5580,hi:=5581);
Read_Real(rVar:=CrpalkeGrfs[4].UreXC200,lo:=5582,hi:=5583);
Read_Real(rVar:=CrpalkeGrfs[5].DeltaSetPoint,lo:=5584,hi:=5585);
Read_Real(rVar:=CrpalkeGrfs[5].EnergijaPoraba,lo:=5586,hi:=5587);
Read_Real(rVar:=CrpalkeGrfs[5].FrekPretvornikDCNapetost,lo:=5588,hi:=5589);
Read_Real(rVar:=CrpalkeGrfs[5].FrekPretvornikDCTok,lo:=5590,hi:=5591);
Read_Real(rVar:=CrpalkeGrfs[5].FreqMax,lo:=5592,hi:=5593);
Read_Real(rVar:=CrpalkeGrfs[5].FreqMin,lo:=5594,hi:=5595);
Read_Real(rVar:=CrpalkeGrfs[5].FreqUpper,lo:=5596,hi:=5597);
Read_Real(rVar:=CrpalkeGrfs[5].MocMax,lo:=5598,hi:=5599);
Read_Real(rVar:=CrpalkeGrfs[5].MocTrenutna,lo:=5600,hi:=5601);
Read_Real(rVar:=CrpalkeGrfs[5].MotorHitrost,lo:=5602,hi:=5603);
Read_Real(rVar:=CrpalkeGrfs[5].MotorTok,lo:=5604,hi:=5605);
Read_Real(rVar:=CrpalkeGrfs[5].NapajanjeTok,lo:=5606,hi:=5607);
Read_Real(rVar:=CrpalkeGrfs[5].NastavitevLokalna,lo:=5608,hi:=5609);
Read_Real(rVar:=CrpalkeGrfs[5].NastavitevTrenutna,lo:=5610,hi:=5611);
Read_Real(rVar:=CrpalkeGrfs[5].PretokMax,lo:=5612,hi:=5613);
Read_Real(rVar:=CrpalkeGrfs[5].PretokMin,lo:=5614,hi:=5615);
Read_Real(rVar:=CrpalkeGrfs[5].PretokTrenutni,lo:=5616,hi:=5617);
Read_Real(rVar:=CrpalkeGrfs[5].PritiskMax,lo:=5618,hi:=5619);
Read_Real(rVar:=CrpalkeGrfs[5].PritiskTrenutni,lo:=5620,hi:=5621);
Read_Real(rVar:=CrpalkeGrfs[5].ReferencaMotorjaHzV,lo:=5622,hi:=5623);
Read_Real(rVar:=CrpalkeGrfs[5].ReferencaRemote,lo:=5624,hi:=5625);
Read_Real(rVar:=CrpalkeGrfs[5].StevecUr2h,lo:=5626,hi:=5627);
Read_Real(rVar:=CrpalkeGrfs[5].SystemFeedback,lo:=5628,hi:=5629);
Read_Real(rVar:=CrpalkeGrfs[5].SystemReference,lo:=5630,hi:=5631);
Read_Real(rVar:=CrpalkeGrfs[5].TemperaturaMotorja,lo:=5632,hi:=5633);
Read_Real(rVar:=CrpalkeGrfs[5].UreXC200,lo:=5634,hi:=5635);
Read_Real(rVar:=CrpalkeGrfs[6].DeltaSetPoint,lo:=5636,hi:=5637);
Read_Real(rVar:=CrpalkeGrfs[6].EnergijaPoraba,lo:=5638,hi:=5639);
Read_Real(rVar:=CrpalkeGrfs[6].FrekPretvornikDCNapetost,lo:=5640,hi:=5641);
Read_Real(rVar:=CrpalkeGrfs[6].FrekPretvornikDCTok,lo:=5642,hi:=5643);
Read_Real(rVar:=CrpalkeGrfs[6].FreqMax,lo:=5644,hi:=5645);
Read_Real(rVar:=CrpalkeGrfs[6].FreqMin,lo:=5646,hi:=5647);
Read_Real(rVar:=CrpalkeGrfs[6].FreqUpper,lo:=5648,hi:=5649);
Read_Real(rVar:=CrpalkeGrfs[6].MocMax,lo:=5650,hi:=5651);
Read_Real(rVar:=CrpalkeGrfs[6].MocTrenutna,lo:=5652,hi:=5653);
Read_Real(rVar:=CrpalkeGrfs[6].MotorHitrost,lo:=5654,hi:=5655);
Read_Real(rVar:=CrpalkeGrfs[6].MotorTok,lo:=5656,hi:=5657);
Read_Real(rVar:=CrpalkeGrfs[6].NapajanjeTok,lo:=5658,hi:=5659);
Read_Real(rVar:=CrpalkeGrfs[6].NastavitevLokalna,lo:=5660,hi:=5661);
Read_Real(rVar:=CrpalkeGrfs[6].NastavitevTrenutna,lo:=5662,hi:=5663);
Read_Real(rVar:=CrpalkeGrfs[6].PretokMax,lo:=5664,hi:=5665);
Read_Real(rVar:=CrpalkeGrfs[6].PretokMin,lo:=5666,hi:=5667);
Read_Real(rVar:=CrpalkeGrfs[6].PretokTrenutni,lo:=5668,hi:=5669);
Read_Real(rVar:=CrpalkeGrfs[6].PritiskMax,lo:=5670,hi:=5671);
Read_Real(rVar:=CrpalkeGrfs[6].PritiskTrenutni,lo:=5672,hi:=5673);
Read_Real(rVar:=CrpalkeGrfs[6].ReferencaMotorjaHzV,lo:=5674,hi:=5675);
Read_Real(rVar:=CrpalkeGrfs[6].ReferencaRemote,lo:=5676,hi:=5677);
Read_Real(rVar:=CrpalkeGrfs[6].StevecUr2h,lo:=5678,hi:=5679);
Read_Real(rVar:=CrpalkeGrfs[6].SystemFeedback,lo:=5680,hi:=5681);
Read_Real(rVar:=CrpalkeGrfs[6].SystemReference,lo:=5682,hi:=5683);
Read_Real(rVar:=CrpalkeGrfs[6].TemperaturaMotorja,lo:=5684,hi:=5685);
Read_Real(rVar:=CrpalkeGrfs[6].UreXC200,lo:=5686,hi:=5687);
Read_Real(rVar:=CrpalkeGrfs[7].DeltaSetPoint,lo:=5688,hi:=5689);
Read_Real(rVar:=CrpalkeGrfs[7].EnergijaPoraba,lo:=5690,hi:=5691);
Read_Real(rVar:=CrpalkeGrfs[7].FrekPretvornikDCNapetost,lo:=5692,hi:=5693);
Read_Real(rVar:=CrpalkeGrfs[7].FrekPretvornikDCTok,lo:=5694,hi:=5695);
Read_Real(rVar:=CrpalkeGrfs[7].FreqMax,lo:=5696,hi:=5697);
Read_Real(rVar:=CrpalkeGrfs[7].FreqMin,lo:=5698,hi:=5699);
Read_Real(rVar:=CrpalkeGrfs[7].FreqUpper,lo:=5700,hi:=5701);
Read_Real(rVar:=CrpalkeGrfs[7].MocMax,lo:=5702,hi:=5703);
Read_Real(rVar:=CrpalkeGrfs[7].MocTrenutna,lo:=5704,hi:=5705);
Read_Real(rVar:=CrpalkeGrfs[7].MotorHitrost,lo:=5706,hi:=5707);
Read_Real(rVar:=CrpalkeGrfs[7].MotorTok,lo:=5708,hi:=5709);
Read_Real(rVar:=CrpalkeGrfs[7].NapajanjeTok,lo:=5710,hi:=5711);
Read_Real(rVar:=CrpalkeGrfs[7].NastavitevLokalna,lo:=5712,hi:=5713);
Read_Real(rVar:=CrpalkeGrfs[7].NastavitevTrenutna,lo:=5714,hi:=5715);
Read_Real(rVar:=CrpalkeGrfs[7].PretokMax,lo:=5716,hi:=5717);
Read_Real(rVar:=CrpalkeGrfs[7].PretokMin,lo:=5718,hi:=5719);
Read_Real(rVar:=CrpalkeGrfs[7].PretokTrenutni,lo:=5720,hi:=5721);
Read_Real(rVar:=CrpalkeGrfs[7].PritiskMax,lo:=5722,hi:=5723);
Read_Real(rVar:=CrpalkeGrfs[7].PritiskTrenutni,lo:=5724,hi:=5725);
Read_Real(rVar:=CrpalkeGrfs[7].ReferencaMotorjaHzV,lo:=5726,hi:=5727);
Read_Real(rVar:=CrpalkeGrfs[7].ReferencaRemote,lo:=5728,hi:=5729);
Read_Real(rVar:=CrpalkeGrfs[7].StevecUr2h,lo:=5730,hi:=5731);
Read_Real(rVar:=CrpalkeGrfs[7].SystemFeedback,lo:=5732,hi:=5733);
Read_Real(rVar:=CrpalkeGrfs[7].SystemReference,lo:=5734,hi:=5735);
Read_Real(rVar:=CrpalkeGrfs[7].TemperaturaMotorja,lo:=5736,hi:=5737);
Read_Real(rVar:=CrpalkeGrfs[7].UreXC200,lo:=5738,hi:=5739);
Read_Real(rVar:=CrpalkeGrfs[8].DeltaSetPoint,lo:=5740,hi:=5741);
Read_Real(rVar:=CrpalkeGrfs[8].EnergijaPoraba,lo:=5742,hi:=5743);
Read_Real(rVar:=CrpalkeGrfs[8].FrekPretvornikDCNapetost,lo:=5744,hi:=5745);
Read_Real(rVar:=CrpalkeGrfs[8].FrekPretvornikDCTok,lo:=5746,hi:=5747);
Read_Real(rVar:=CrpalkeGrfs[8].FreqMax,lo:=5748,hi:=5749);
Read_Real(rVar:=CrpalkeGrfs[8].FreqMin,lo:=5750,hi:=5751);
Read_Real(rVar:=CrpalkeGrfs[8].FreqUpper,lo:=5752,hi:=5753);
Read_Real(rVar:=CrpalkeGrfs[8].MocMax,lo:=5754,hi:=5755);
Read_Real(rVar:=CrpalkeGrfs[8].MocTrenutna,lo:=5756,hi:=5757);
Read_Real(rVar:=CrpalkeGrfs[8].MotorHitrost,lo:=5758,hi:=5759);
Read_Real(rVar:=CrpalkeGrfs[8].MotorTok,lo:=5760,hi:=5761);
Read_Real(rVar:=CrpalkeGrfs[8].NapajanjeTok,lo:=5762,hi:=5763);
Read_Real(rVar:=CrpalkeGrfs[8].NastavitevLokalna,lo:=5764,hi:=5765);
Read_Real(rVar:=CrpalkeGrfs[8].NastavitevTrenutna,lo:=5766,hi:=5767);
Read_Real(rVar:=CrpalkeGrfs[8].PretokMax,lo:=5768,hi:=5769);
Read_Real(rVar:=CrpalkeGrfs[8].PretokMin,lo:=5770,hi:=5771);
Read_Real(rVar:=CrpalkeGrfs[8].PretokTrenutni,lo:=5772,hi:=5773);
Read_Real(rVar:=CrpalkeGrfs[8].PritiskMax,lo:=5774,hi:=5775);
Read_Real(rVar:=CrpalkeGrfs[8].PritiskTrenutni,lo:=5776,hi:=5777);
Read_Real(rVar:=CrpalkeGrfs[8].ReferencaMotorjaHzV,lo:=5778,hi:=5779);
Read_Real(rVar:=CrpalkeGrfs[8].ReferencaRemote,lo:=5780,hi:=5781);
Read_Real(rVar:=CrpalkeGrfs[8].StevecUr2h,lo:=5782,hi:=5783);
Read_Real(rVar:=CrpalkeGrfs[8].SystemFeedback,lo:=5784,hi:=5785);
Read_Real(rVar:=CrpalkeGrfs[8].SystemReference,lo:=5786,hi:=5787);
Read_Real(rVar:=CrpalkeGrfs[8].TemperaturaMotorja,lo:=5788,hi:=5789);
Read_Real(rVar:=CrpalkeGrfs[8].UreXC200,lo:=5790,hi:=5791);
Read_Real(rVar:=CrpalkeGrfs[9].DeltaSetPoint,lo:=5792,hi:=5793);
Read_Real(rVar:=CrpalkeGrfs[9].EnergijaPoraba,lo:=5794,hi:=5795);
Read_Real(rVar:=CrpalkeGrfs[9].FrekPretvornikDCNapetost,lo:=5796,hi:=5797);
Read_Real(rVar:=CrpalkeGrfs[9].FrekPretvornikDCTok,lo:=5798,hi:=5799);
Read_Real(rVar:=CrpalkeGrfs[9].FreqMax,lo:=5800,hi:=5801);
Read_Real(rVar:=CrpalkeGrfs[9].FreqMin,lo:=5802,hi:=5803);
Read_Real(rVar:=CrpalkeGrfs[9].FreqUpper,lo:=5804,hi:=5805);
Read_Real(rVar:=CrpalkeGrfs[9].MocMax,lo:=5806,hi:=5807);
Read_Real(rVar:=CrpalkeGrfs[9].MocTrenutna,lo:=5808,hi:=5809);
Read_Real(rVar:=CrpalkeGrfs[9].MotorHitrost,lo:=5810,hi:=5811);
Read_Real(rVar:=CrpalkeGrfs[9].MotorTok,lo:=5812,hi:=5813);
Read_Real(rVar:=CrpalkeGrfs[9].NapajanjeTok,lo:=5814,hi:=5815);
Read_Real(rVar:=CrpalkeGrfs[9].NastavitevLokalna,lo:=5816,hi:=5817);
Read_Real(rVar:=CrpalkeGrfs[9].NastavitevTrenutna,lo:=5818,hi:=5819);
Read_Real(rVar:=CrpalkeGrfs[9].PretokMax,lo:=5820,hi:=5821);
Read_Real(rVar:=CrpalkeGrfs[9].PretokMin,lo:=5822,hi:=5823);
Read_Real(rVar:=CrpalkeGrfs[9].PretokTrenutni,lo:=5824,hi:=5825);
Read_Real(rVar:=CrpalkeGrfs[9].PritiskMax,lo:=5826,hi:=5827);
Read_Real(rVar:=CrpalkeGrfs[9].PritiskTrenutni,lo:=5828,hi:=5829);
Read_Real(rVar:=CrpalkeGrfs[9].ReferencaMotorjaHzV,lo:=5830,hi:=5831);
Read_Real(rVar:=CrpalkeGrfs[9].ReferencaRemote,lo:=5832,hi:=5833);
Read_Real(rVar:=CrpalkeGrfs[9].StevecUr2h,lo:=5834,hi:=5835);
Read_Real(rVar:=CrpalkeGrfs[9].SystemFeedback,lo:=5836,hi:=5837);
Read_Real(rVar:=CrpalkeGrfs[9].SystemReference,lo:=5838,hi:=5839);
Read_Real(rVar:=CrpalkeGrfs[9].TemperaturaMotorja,lo:=5840,hi:=5841);
Read_Real(rVar:=CrpalkeGrfs[9].UreXC200,lo:=5842,hi:=5843);
Read_Real(rVar:=CrpGrundfosTlakSP[1],lo:=5844,hi:=5845);
Read_Real(rVar:=CrpGrundfosTlakSP[2],lo:=5846,hi:=5847);
Read_Real(rVar:=CrpGrundfosTlakSP[3],lo:=5848,hi:=5849);
Read_Real(rVar:=CrpGrundfosTlakSP[4],lo:=5850,hi:=5851);
Read_Real(rVar:=CrpGrundfosTlakSP[5],lo:=5852,hi:=5853);
Read_Real(rVar:=CrpGrundfosTlakSP[6],lo:=5854,hi:=5855);
Read_Real(rVar:=CrpGrundfosTlakSP[7],lo:=5856,hi:=5857);
Read_Real(rVar:=Exp1TlakMin,lo:=5858,hi:=5859);
Read_Real(rVar:=Exp2TlakMin,lo:=5860,hi:=5861);
Read_Real(rVar:=HladStroj.ObratovalneUre,lo:=5862,hi:=5863);
Read_Real(rVar:=HladStroj.PritiskSonda1,lo:=5864,hi:=5865);
Read_Real(rVar:=HladStroj.PritiskSonda2,lo:=5866,hi:=5867);
Read_Real(rVar:=HladStroj.PritiskSonda3,lo:=5868,hi:=5869);
Read_Real(rVar:=HladStroj.PritiskSonda4,lo:=5870,hi:=5871);
Read_Real(rVar:=HladStroj.TempH2OvhodIzparilnika,lo:=5872,hi:=5873);
Read_Real(rVar:=HladStroj.TempIzhodnaSonda1,lo:=5874,hi:=5875);
Read_Real(rVar:=HladStroj.TempIzhodnaSonda3,lo:=5876,hi:=5877);
Read_Real(rVar:=HladStroj.TempSetPoint,lo:=5878,hi:=5879);
Read_Real(rVar:=Klima[1].HitrostVentilatorjev,lo:=5880,hi:=5881);
Read_Real(rVar:=Klima[1].NastTempProstora,lo:=5882,hi:=5883);
Read_Real(rVar:=Klima[1].ObratovalneUre,lo:=5884,hi:=5885);
Read_Real(rVar:=Klima[1].ProtizmrzZasc,lo:=5886,hi:=5887);
Read_Real(rVar:=Klima[1].RezimDelovanja,lo:=5888,hi:=5889);
Read_Real(rVar:=Klima[1].TemperaturaDovoda,lo:=5890,hi:=5891);
Read_Real(rVar:=Klima[1].TemperaturaProstora,lo:=5892,hi:=5893);
Read_Real(rVar:=Klima[1].TempPredRekN2,lo:=5894,hi:=5895);
Read_Real(rVar:=Klima[1].TempZaRekN2,lo:=5896,hi:=5897);
Read_Real(rVar:=Klima[1].TlakDovKanal,lo:=5898,hi:=5899);
Read_Real(rVar:=Klima[1].TlakOdvodKanal,lo:=5900,hi:=5901);
Read_Real(rVar:=Klima[1].VlagaDovoda,lo:=5902,hi:=5903);
Read_Real(rVar:=Klima[1].VlagaVprostor,lo:=5904,hi:=5905);
Read_Real(rVar:=Klima[1].ZunanjaTemp,lo:=5906,hi:=5907);
Read_Real(rVar:=Klima[2].HitrostVentilatorjev,lo:=5908,hi:=5909);
Read_Real(rVar:=Klima[2].NastTempProstora,lo:=5910,hi:=5911);
Read_Real(rVar:=Klima[2].ObratovalneUre,lo:=5912,hi:=5913);
Read_Real(rVar:=Klima[2].ProtizmrzZasc,lo:=5914,hi:=5915);
Read_Real(rVar:=Klima[2].RezimDelovanja,lo:=5916,hi:=5917);
Read_Real(rVar:=Klima[2].TemperaturaDovoda,lo:=5918,hi:=5919);
Read_Real(rVar:=Klima[2].TemperaturaProstora,lo:=5920,hi:=5921);
Read_Real(rVar:=Klima[2].TempPredRekN2,lo:=5922,hi:=5923);
Read_Real(rVar:=Klima[2].TempZaRekN2,lo:=5924,hi:=5925);
Read_Real(rVar:=Klima[2].TlakDovKanal,lo:=5926,hi:=5927);
Read_Real(rVar:=Klima[2].TlakOdvodKanal,lo:=5928,hi:=5929);
Read_Real(rVar:=Klima[2].VlagaDovoda,lo:=5930,hi:=5931);
Read_Real(rVar:=Klima[2].VlagaVprostor,lo:=5932,hi:=5933);
Read_Real(rVar:=Klima[2].ZunanjaTemp,lo:=5934,hi:=5935);
Read_Real(rVar:=rVersion,lo:=5936,hi:=5937);
Read_Real(rVar:=SenzorTempTIA[1],lo:=5938,hi:=5939);
Read_Real(rVar:=SenzorTempTIA[2],lo:=5940,hi:=5941);
Read_Real(rVar:=SenzorTempTIA[3],lo:=5942,hi:=5943);
Read_Real(rVar:=SenzorTempTIA[4],lo:=5944,hi:=5945);
Read_Real(rVar:=SenzorVlagaHIA[1],lo:=5946,hi:=5947);
Read_Real(rVar:=SenzorVlagaHIA[2],lo:=5948,hi:=5949);
Read_Real(rVar:=SenzorVlagaHIA[3],lo:=5950,hi:=5951);
Read_Real(rVar:=SenzorVlagaHIA[4],lo:=5952,hi:=5953);
Read_Real(rVar:=TEgrelecTempMAX,lo:=5954,hi:=5955);
Read_Real(rVar:=TEgrelecTempMIN,lo:=5956,hi:=5957);
Read_Real(rVar:=TempAlarmPoint,lo:=5958,hi:=5959);
Read_Real(rVar:=TempTIApovprecna,lo:=5960,hi:=5961);
Read_Real(rVar:=ToplPost.HKdotokNastTemp,lo:=5962,hi:=5963);
Read_Real(rVar:=ToplPost.HKdotokTemp,lo:=5964,hi:=5965);
Read_Real(rVar:=ToplPost.HKpovtatekTemp,lo:=5966,hi:=5967);
Read_Real(rVar:=ToplPost.HKpovtratekNastTemp,lo:=5968,hi:=5969);
Read_Real(rVar:=ToplPost.HKzunanjaTemp,lo:=5970,hi:=5971);
Read_Real(rVar:=ToplPost.TVdotokNastTemp,lo:=5972,hi:=5973);
Read_Real(rVar:=ToplPost.TVdotokTemp,lo:=5974,hi:=5975);
Read_Real(rVar:=ToplPost.TVpovratekTemp,lo:=5976,hi:=5977);
Read_Real(rVar:=ToplPost.TVrezervoarTemp,lo:=5978,hi:=5979);
Read_Real(rVar:=TYventilMax[1],lo:=5980,hi:=5981);
Read_Real(rVar:=TYventilMax[2],lo:=5982,hi:=5983);
Read_Real(rVar:=TYventilMax[3],lo:=5984,hi:=5985);
Read_Real(rVar:=TYventilMax[4],lo:=5986,hi:=5987);
Read_Real(rVar:=TYventilMin[1],lo:=5988,hi:=5989);
Read_Real(rVar:=TYventilMin[2],lo:=5990,hi:=5991);
Read_Real(rVar:=TYventilMin[3],lo:=5992,hi:=5993);
Read_Real(rVar:=TYventilMin[4],lo:=5994,hi:=5995);
Read_Real(rVar:=TYventilTempRazlika[1],lo:=5996,hi:=5997);
Read_Real(rVar:=TYventilTempRazlika[2],lo:=5998,hi:=5999);
Read_Real(rVar:=TYventilTempRazlika[3],lo:=6000,hi:=6001);
Read_Real(rVar:=TYventilTempRazlika[4],lo:=6002,hi:=6003);
Read_Real(rVar:=ValAI_Temp1B1,lo:=6004,hi:=6005);
Read_Real(rVar:=ValAI_Temp1B2,lo:=6006,hi:=6007);
Read_Real(rVar:=ValAI_Temp1B3,lo:=6008,hi:=6009);
Read_Real(rVar:=ValAI_Temp2B2,lo:=6010,hi:=6011);
Read_Real(rVar:=ValAI_Temp2B3,lo:=6012,hi:=6013);
Read_Real(rVar:=ValAI_TempHB2,lo:=6014,hi:=6015);
Read_Real(rVar:=ValAI_TempHB4,lo:=6016,hi:=6017);
Read_Real(rVar:=ValAI_TempHB9,lo:=6018,hi:=6019);
Read_Real(rVar:=ValAI_TempTB1,lo:=6020,hi:=6021);
Read_Real(rVar:=ValAI_TempTB10,lo:=6022,hi:=6023);
Read_Real(rVar:=ValAI_TempTB2,lo:=6024,hi:=6025);
Read_Real(rVar:=ValAI_TempTB3,lo:=6026,hi:=6027);
Read_Real(rVar:=ValAI_TempTB4,lo:=6028,hi:=6029);
Read_Real(rVar:=ValAI_TempTB8,lo:=6030,hi:=6031);
Read_Real(rVar:=ValAI_TlakExp1S1,lo:=6032,hi:=6033);
Read_Real(rVar:=ValAI_TlakExp1S2,lo:=6034,hi:=6035);
Read_Real(rVar:=ValAI_TlakExp2S1,lo:=6036,hi:=6037);
Read_Real(rVar:=ValAI_TlakExp2S2,lo:=6038,hi:=6039);
Read_Real(rVar:=ValAI_TlakHB15,lo:=6040,hi:=6041);
Read_Real(rVar:=ValAI_TlakHB16,lo:=6042,hi:=6043);
Read_Real(rVar:=ValAI_TlakHB17,lo:=6044,hi:=6045);
Read_Real(rVar:=ValAI_TlakHB3,lo:=6046,hi:=6047);
Read_Real(rVar:=ValAI_TlakTB11,lo:=6048,hi:=6049);
Read_Real(rVar:=ValAI_TlakTB12,lo:=6050,hi:=6051);
Read_Real(rVar:=ValAI_TlakTB13,lo:=6052,hi:=6053);
Read_Real(rVar:=ValAI_TlakTB14,lo:=6054,hi:=6055);
Read_Real(rVar:=ValAI_Vlaga1B4,lo:=6056,hi:=6057);
Read_Real(rVar:=ValAI_Vlaga2B4,lo:=6058,hi:=6059);
Read_Real(rVar:=ValAO_RegVentTY[1],lo:=6060,hi:=6061);
Read_Real(rVar:=ValAO_RegVentTY[2],lo:=6062,hi:=6063);
Read_Real(rVar:=ValAO_RegVentTY[3],lo:=6064,hi:=6065);
Read_Real(rVar:=ValAO_RegVentTY[4],lo:=6066,hi:=6067);
Read_Real(rVar:=VlagaHIApovprecna,lo:=6068,hi:=6069);
Read_Real(rVar:=Circutor.CosFi_III,lo:=6070,hi:=6071);
Read_Real(rVar:=Circutor.DelovnaEnergija,lo:=6072,hi:=6073);
Read_Real(rVar:=Circutor.DelovnaMoc_III,lo:=6074,hi:=6075);
Read_Real(rVar:=Circutor.DelovnaMoc_L1,lo:=6076,hi:=6077);
Read_Real(rVar:=Circutor.DelovnaMoc_L2,lo:=6078,hi:=6079);
Read_Real(rVar:=Circutor.DelovnaMoc_L3,lo:=6080,hi:=6081);
Read_Real(rVar:=Circutor.Frekvenca_L1,lo:=6082,hi:=6083);
Read_Real(rVar:=Circutor.InduktivnaEnergija,lo:=6084,hi:=6085);
Read_Real(rVar:=Circutor.InduktivnaMoc_III,lo:=6086,hi:=6087);
Read_Real(rVar:=Circutor.JalovaMoc_L1,lo:=6088,hi:=6089);
Read_Real(rVar:=Circutor.JalovaMoc_L2,lo:=6090,hi:=6091);
Read_Real(rVar:=Circutor.JalovaMoc_L3,lo:=6092,hi:=6093);
Read_Real(rVar:=Circutor.KapacitivnaEnergija,lo:=6094,hi:=6095);
Read_Real(rVar:=Circutor.KapacitivnaMoc_III,lo:=6096,hi:=6097);
Read_Real(rVar:=Circutor.MaximumDemand,lo:=6098,hi:=6099);
Read_Real(rVar:=Circutor.Napetost_L1_L2,lo:=6100,hi:=6101);
Read_Real(rVar:=Circutor.Napetost_L1_N,lo:=6102,hi:=6103);
Read_Real(rVar:=Circutor.Napetost_L2_L3,lo:=6104,hi:=6105);
Read_Real(rVar:=Circutor.Napetost_L2_N,lo:=6106,hi:=6107);
Read_Real(rVar:=Circutor.Napetost_L3_L1,lo:=6108,hi:=6109);
Read_Real(rVar:=Circutor.Napetost_L3_N,lo:=6110,hi:=6111);
Read_Real(rVar:=Circutor.NavideznaMoc_III,lo:=6112,hi:=6113);
Read_Real(rVar:=Circutor.NicelniTok,lo:=6114,hi:=6115);
Read_Real(rVar:=Circutor.PowerFactor_III,lo:=6116,hi:=6117);
Read_Real(rVar:=Circutor.PowerFactor_L1,lo:=6118,hi:=6119);
Read_Real(rVar:=Circutor.PowerFactor_L2,lo:=6120,hi:=6121);
Read_Real(rVar:=Circutor.PowerFactor_L3,lo:=6122,hi:=6123);
Read_Real(rVar:=Circutor.THDI_L1,lo:=6124,hi:=6125);
Read_Real(rVar:=Circutor.THDI_L2,lo:=6126,hi:=6127);
Read_Real(rVar:=Circutor.THDI_L3,lo:=6128,hi:=6129);
Read_Real(rVar:=Circutor.THDV_L1,lo:=6130,hi:=6131);
Read_Real(rVar:=Circutor.THDV_L2,lo:=6132,hi:=6133);
Read_Real(rVar:=Circutor.THDV_L3,lo:=6134,hi:=6135);
Read_Real(rVar:=Circutor.Tok_L1,lo:=6136,hi:=6137);
Read_Real(rVar:=Circutor.Tok_L2,lo:=6138,hi:=6139);
Read_Real(rVar:=Circutor.Tok_L3,lo:=6140,hi:=6141);
Read_Real(rVar:=Circutor.TokPovprecje_III,lo:=6142,hi:=6143);
Read_Real(rVar:=CrpalkeGrfsGal.EnergijaPoraba,lo:=6144,hi:=6145);
Read_Real(rVar:=CrpalkeGrfsGal.FrekPretvornikDCNapetost,lo:=6146,hi:=6147);
Read_Real(rVar:=CrpalkeGrfsGal.FrekPretvornikDCTok,lo:=6148,hi:=6149);
Read_Real(rVar:=CrpalkeGrfsGal.FreqMax,lo:=6150,hi:=6151);
Read_Real(rVar:=CrpalkeGrfsGal.FreqMin,lo:=6152,hi:=6153);
Read_Real(rVar:=CrpalkeGrfsGal.FreqUpper,lo:=6154,hi:=6155);
Read_Real(rVar:=CrpalkeGrfsGal.MocMax,lo:=6156,hi:=6157);
Read_Real(rVar:=CrpalkeGrfsGal.MocTrenutna,lo:=6158,hi:=6159);
Read_Real(rVar:=CrpalkeGrfsGal.MotorHitrost,lo:=6160,hi:=6161);
Read_Real(rVar:=CrpalkeGrfsGal.MotorTok,lo:=6162,hi:=6163);
Read_Real(rVar:=CrpalkeGrfsGal.NapajanjeTok,lo:=6164,hi:=6165);
Read_Real(rVar:=CrpalkeGrfsGal.NastavitevLokalna,lo:=6166,hi:=6167);
Read_Real(rVar:=CrpalkeGrfsGal.NastavitevTrenutna,lo:=6168,hi:=6169);
Read_Real(rVar:=CrpalkeGrfsGal.PretokMax,lo:=6170,hi:=6171);
Read_Real(rVar:=CrpalkeGrfsGal.PretokMin,lo:=6172,hi:=6173);
Read_Real(rVar:=CrpalkeGrfsGal.PretokTrenutni,lo:=6174,hi:=6175);
Read_Real(rVar:=CrpalkeGrfsGal.PritiskMax,lo:=6176,hi:=6177);
Read_Real(rVar:=CrpalkeGrfsGal.PritiskTrenutni,lo:=6178,hi:=6179);
Read_Real(rVar:=CrpalkeGrfsGal.ReferencaMotorjaHzV,lo:=6180,hi:=6181);
Read_Real(rVar:=CrpalkeGrfsGal.ReferencaRemote,lo:=6182,hi:=6183);
Read_Real(rVar:=CrpalkeGrfsGal.StevecUr2h,lo:=6184,hi:=6185);
Read_Real(rVar:=CrpalkeGrfsGal.SystemFeedback,lo:=6186,hi:=6187);
Read_Real(rVar:=CrpalkeGrfsGal.SystemReference,lo:=6188,hi:=6189);
Read_Real(rVar:=CrpalkeGrfsGal.TemperaturaMotorja,lo:=6190,hi:=6191);
Read_Real(rVar:=CrpalkeGrfsGal.UreXC200,lo:=6192,hi:=6193);
Read_Real(rVar:=CrpGrfsPIDregKP,lo:=6194,hi:=6195);
Read_Real(rVar:=ValAI_TempTB5,lo:=6196,hi:=6197);
Read_Real(rVar:=XVH_CrpGrundfosTlakSP,lo:=6198,hi:=6199);
Read_Real(rVar:=XVH_GrafTemp[1],lo:=6200,hi:=6201);
Read_Real(rVar:=XVH_GrafTemp[2],lo:=6202,hi:=6203);
Read_Real(rVar:=XVH_GrafTemp[3],lo:=6204,hi:=6205);
Read_Real(rVar:=XVH_GrafTemp[4],lo:=6206,hi:=6207);
Read_Real(rVar:=XVH_GrafTemp[5],lo:=6208,hi:=6209);
Read_Real(rVar:=XVH_GrafVlaga[1],lo:=6210,hi:=6211);
Read_Real(rVar:=XVH_GrafVlaga[2],lo:=6212,hi:=6213);
Read_Real(rVar:=XVH_GrafVlaga[3],lo:=6214,hi:=6215);
Read_Real(rVar:=XVH_GrafVlaga[4],lo:=6216,hi:=6217);
Read_Real(rVar:=XVH_GrafVlaga[5],lo:=6218,hi:=6219);
Read_Real(rVar:=XVH_TlakSenzor,lo:=6220,hi:=6221);
Read_Real(rVar:=Circ[1].MaximumDemandA2,lo:=6222,hi:=6223);
Read_Real(rVar:=Circ[1].MaximumDemandA3,lo:=6224,hi:=6225);
Read_Real(rVar:=Circ[1].RazEner_D_SCADA,lo:=6226,hi:=6227);
Read_Real(rVar:=Circ[1].RazEner_T_SCADA,lo:=6228,hi:=6229);
Read_Real(rVar:=Circ[1].RazEner_M_SCADA,lo:=6230,hi:=6231);
(*Branje STRING*)
(**)
Read_String(sVar:=UserCurrentName,start:=7000);
Read_String(sVar:=Date_Time[0],start:=7015);
Read_String(sVar:=Date_Time[1],start:=7030);
Read_String(sVar:=Date_Time[2],start:=7045);
Read_String(sVar:=Date_Time[3],start:=7060);
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Bool : BOOL
VAR_INPUT
index: INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje BOOL*)
(**)
0:AkumSanVodeTE1OnOff:=Bit_0;
1:AlarmGenCirc1:=Bit_0;
2:AlarmGenComm:=Bit_0;
3:AlarmGenDI:=Bit_0;
4:AlarmGenHladPost:=Bit_0;
5:AlarmGenKlima1:=Bit_0;
6:AlarmGenKlima2:=Bit_0;
7:AlarmGenLopute:=Bit_0;
8:AlarmGenRest:=Bit_0;
9:AlarmGenSenzor:=Bit_0;
10:AlarmGenTemp:=Bit_0;
11:AlarmGenToplPost:=Bit_0;
12:AlarmGenVent:=Bit_0;
13:AlarmGenVTV:=Bit_0;
14:ATVTempPrenizka:=Bit_0;
15:ComSCADA:=Bit_0;
16:ComSCADA1:=Bit_0;
17:CrpalkaMN1OnOff:=Bit_0;
18:CrpalkaTm11TM12OnOff:=Bit_0;
19:CrpalkeDnfs[1].AlarmAktiven:=Bit_0;
20:CrpalkeDnfs[1].Deluje:=Bit_0;
21:CrpalkeDnfs[1].QuickStop:=Bit_0;
22:CrpalkeDnfs[1].RemoteON:=Bit_0;
23:CrpalkeDnfs[1].Reset:=Bit_0;
24:CrpalkeDnfs[1].Start:=Bit_0;
25:CrpalkeDnfs[1].Stop:=Bit_0;
26:CrpalkeDnfs[2].AlarmAktiven:=Bit_0;
27:CrpalkeDnfs[2].Deluje:=Bit_0;
28:CrpalkeDnfs[2].QuickStop:=Bit_0;
29:CrpalkeDnfs[2].RemoteON:=Bit_0;
30:CrpalkeDnfs[2].Reset:=Bit_0;
31:CrpalkeDnfs[2].Start:=Bit_0;
32:CrpalkeDnfs[2].Stop:=Bit_0;
33:CrpalkeDnfs[3].AlarmAktiven:=Bit_0;
34:CrpalkeDnfs[3].Deluje:=Bit_0;
35:CrpalkeDnfs[3].QuickStop:=Bit_0;
36:CrpalkeDnfs[3].RemoteON:=Bit_0;
37:CrpalkeDnfs[3].Reset:=Bit_0;
38:CrpalkeDnfs[3].Start:=Bit_0;
39:CrpalkeDnfs[3].Stop:=Bit_0;
40:CrpalkeDnfs[4].AlarmAktiven:=Bit_0;
41:CrpalkeDnfs[4].Deluje:=Bit_0;
42:CrpalkeDnfs[4].QuickStop:=Bit_0;
43:CrpalkeDnfs[4].RemoteON:=Bit_0;
44:CrpalkeDnfs[4].Reset:=Bit_0;
45:CrpalkeDnfs[4].Start:=Bit_0;
46:CrpalkeDnfs[4].Stop:=Bit_0;
47:CrpalkeGrfs[10].AlarmAktiven:=Bit_0;
48:CrpalkeGrfs[10].Deluje:=Bit_0;
49:CrpalkeGrfs[10].LocalMode:=Bit_0;
50:CrpalkeGrfs[10].RemoteON:=Bit_0;
51:CrpalkeGrfs[10].Reset2handkWhValues:=Bit_0;
52:CrpalkeGrfs[10].ResetAlarm:=Bit_0;
53:CrpalkeGrfs[10].ResetAlarmLog:=Bit_0;
54:CrpalkeGrfs[10].ResetDevice:=Bit_0;
55:CrpalkeGrfs[10].SetAutomatic:=Bit_0;
56:CrpalkeGrfs[10].SetConstFreqMode:=Bit_0;
57:CrpalkeGrfs[10].SetConstPress:=Bit_0;
58:CrpalkeGrfs[10].SetLocalMode:=Bit_0;
59:CrpalkeGrfs[10].SetMaxRunMode:=Bit_0;
60:CrpalkeGrfs[10].SetMinRunMode:=Bit_0;
61:CrpalkeGrfs[10].SetPropPress:=Bit_0;
62:CrpalkeGrfs[10].SetReference:=Bit_0;
63:CrpalkeGrfs[10].SetRemoteMode:=Bit_0;
64:CrpalkeGrfs[10].SetTwinModeAlt:=Bit_0;
65:CrpalkeGrfs[10].SetTwinModeSpare:=Bit_0;
66:CrpalkeGrfs[10].SetTwinModeSync:=Bit_0;
67:CrpalkeGrfs[10].Start:=Bit_0;
68:CrpalkeGrfs[10].Stop:=Bit_0;
69:CrpalkeGrfs[11].AlarmAktiven:=Bit_0;
70:CrpalkeGrfs[11].Deluje:=Bit_0;
71:CrpalkeGrfs[11].LocalMode:=Bit_0;
72:CrpalkeGrfs[11].RemoteON:=Bit_0;
73:CrpalkeGrfs[11].Reset2handkWhValues:=Bit_0;
74:CrpalkeGrfs[11].ResetAlarm:=Bit_0;
75:CrpalkeGrfs[11].ResetAlarmLog:=Bit_0;
76:CrpalkeGrfs[11].ResetDevice:=Bit_0;
77:CrpalkeGrfs[11].SetAutomatic:=Bit_0;
78:CrpalkeGrfs[11].SetConstFreqMode:=Bit_0;
79:CrpalkeGrfs[11].SetConstPress:=Bit_0;
80:CrpalkeGrfs[11].SetLocalMode:=Bit_0;
81:CrpalkeGrfs[11].SetMaxRunMode:=Bit_0;
82:CrpalkeGrfs[11].SetMinRunMode:=Bit_0;
83:CrpalkeGrfs[11].SetPropPress:=Bit_0;
84:CrpalkeGrfs[11].SetReference:=Bit_0;
85:CrpalkeGrfs[11].SetRemoteMode:=Bit_0;
86:CrpalkeGrfs[11].SetTwinModeAlt:=Bit_0;
87:CrpalkeGrfs[11].SetTwinModeSpare:=Bit_0;
88:CrpalkeGrfs[11].SetTwinModeSync:=Bit_0;
89:CrpalkeGrfs[11].Start:=Bit_0;
90:CrpalkeGrfs[11].Stop:=Bit_0;
91:CrpalkeGrfs[12].AlarmAktiven:=Bit_0;
92:CrpalkeGrfs[12].Deluje:=Bit_0;
93:CrpalkeGrfs[12].LocalMode:=Bit_0;
94:CrpalkeGrfs[12].RemoteON:=Bit_0;
95:CrpalkeGrfs[12].Reset2handkWhValues:=Bit_0;
96:CrpalkeGrfs[12].ResetAlarm:=Bit_0;
97:CrpalkeGrfs[12].ResetAlarmLog:=Bit_0;
98:CrpalkeGrfs[12].ResetDevice:=Bit_0;
99:CrpalkeGrfs[12].SetAutomatic:=Bit_0;
100:CrpalkeGrfs[12].SetConstFreqMode:=Bit_0;
101:CrpalkeGrfs[12].SetConstPress:=Bit_0;
102:CrpalkeGrfs[12].SetLocalMode:=Bit_0;
103:CrpalkeGrfs[12].SetMaxRunMode:=Bit_0;
104:CrpalkeGrfs[12].SetMinRunMode:=Bit_0;
105:CrpalkeGrfs[12].SetPropPress:=Bit_0;
106:CrpalkeGrfs[12].SetReference:=Bit_0;
107:CrpalkeGrfs[12].SetRemoteMode:=Bit_0;
108:CrpalkeGrfs[12].SetTwinModeAlt:=Bit_0;
109:CrpalkeGrfs[12].SetTwinModeSpare:=Bit_0;
110:CrpalkeGrfs[12].SetTwinModeSync:=Bit_0;
111:CrpalkeGrfs[12].Start:=Bit_0;
112:CrpalkeGrfs[12].Stop:=Bit_0;
113:CrpalkeGrfs[13].AlarmAktiven:=Bit_0;
114:CrpalkeGrfs[13].Deluje:=Bit_0;
115:CrpalkeGrfs[13].LocalMode:=Bit_0;
116:CrpalkeGrfs[13].RemoteON:=Bit_0;
117:CrpalkeGrfs[13].Reset2handkWhValues:=Bit_0;
118:CrpalkeGrfs[13].ResetAlarm:=Bit_0;
119:CrpalkeGrfs[13].ResetAlarmLog:=Bit_0;
120:CrpalkeGrfs[13].ResetDevice:=Bit_0;
121:CrpalkeGrfs[13].SetAutomatic:=Bit_0;
122:CrpalkeGrfs[13].SetConstFreqMode:=Bit_0;
123:CrpalkeGrfs[13].SetConstPress:=Bit_0;
124:CrpalkeGrfs[13].SetLocalMode:=Bit_0;
125:CrpalkeGrfs[13].SetMaxRunMode:=Bit_0;
126:CrpalkeGrfs[13].SetMinRunMode:=Bit_0;
127:CrpalkeGrfs[13].SetPropPress:=Bit_0;
128:CrpalkeGrfs[13].SetReference:=Bit_0;
129:CrpalkeGrfs[13].SetRemoteMode:=Bit_0;
130:CrpalkeGrfs[13].SetTwinModeAlt:=Bit_0;
131:CrpalkeGrfs[13].SetTwinModeSpare:=Bit_0;
132:CrpalkeGrfs[13].SetTwinModeSync:=Bit_0;
133:CrpalkeGrfs[13].Start:=Bit_0;
134:CrpalkeGrfs[13].Stop:=Bit_0;
135:CrpalkeGrfs[14].AlarmAktiven:=Bit_0;
136:CrpalkeGrfs[14].Deluje:=Bit_0;
137:CrpalkeGrfs[14].LocalMode:=Bit_0;
138:CrpalkeGrfs[14].RemoteON:=Bit_0;
139:CrpalkeGrfs[14].Reset2handkWhValues:=Bit_0;
140:CrpalkeGrfs[14].ResetAlarm:=Bit_0;
141:CrpalkeGrfs[14].ResetAlarmLog:=Bit_0;
142:CrpalkeGrfs[14].ResetDevice:=Bit_0;
143:CrpalkeGrfs[14].SetAutomatic:=Bit_0;
144:CrpalkeGrfs[14].SetConstFreqMode:=Bit_0;
145:CrpalkeGrfs[14].SetConstPress:=Bit_0;
146:CrpalkeGrfs[14].SetLocalMode:=Bit_0;
147:CrpalkeGrfs[14].SetMaxRunMode:=Bit_0;
148:CrpalkeGrfs[14].SetMinRunMode:=Bit_0;
149:CrpalkeGrfs[14].SetPropPress:=Bit_0;
150:CrpalkeGrfs[14].SetReference:=Bit_0;
151:CrpalkeGrfs[14].SetRemoteMode:=Bit_0;
152:CrpalkeGrfs[14].SetTwinModeAlt:=Bit_0;
153:CrpalkeGrfs[14].SetTwinModeSpare:=Bit_0;
154:CrpalkeGrfs[14].SetTwinModeSync:=Bit_0;
155:CrpalkeGrfs[14].Start:=Bit_0;
156:CrpalkeGrfs[14].Stop:=Bit_0;
157:CrpalkeGrfs[1].AlarmAktiven:=Bit_0;
158:CrpalkeGrfs[1].Deluje:=Bit_0;
159:CrpalkeGrfs[1].LocalMode:=Bit_0;
160:CrpalkeGrfs[1].RemoteON:=Bit_0;
161:CrpalkeGrfs[1].Reset2handkWhValues:=Bit_0;
162:CrpalkeGrfs[1].ResetAlarm:=Bit_0;
163:CrpalkeGrfs[1].ResetAlarmLog:=Bit_0;
164:CrpalkeGrfs[1].ResetDevice:=Bit_0;
165:CrpalkeGrfs[1].SetAutomatic:=Bit_0;
166:CrpalkeGrfs[1].SetConstFreqMode:=Bit_0;
167:CrpalkeGrfs[1].SetConstPress:=Bit_0;
168:CrpalkeGrfs[1].SetLocalMode:=Bit_0;
169:CrpalkeGrfs[1].SetMaxRunMode:=Bit_0;
170:CrpalkeGrfs[1].SetMinRunMode:=Bit_0;
171:CrpalkeGrfs[1].SetPropPress:=Bit_0;
172:CrpalkeGrfs[1].SetReference:=Bit_0;
173:CrpalkeGrfs[1].SetRemoteMode:=Bit_0;
174:CrpalkeGrfs[1].SetTwinModeAlt:=Bit_0;
175:CrpalkeGrfs[1].SetTwinModeSpare:=Bit_0;
176:CrpalkeGrfs[1].SetTwinModeSync:=Bit_0;
177:CrpalkeGrfs[1].Start:=Bit_0;
178:CrpalkeGrfs[1].Stop:=Bit_0;
179:CrpalkeGrfs[2].AlarmAktiven:=Bit_0;
180:CrpalkeGrfs[2].Deluje:=Bit_0;
181:CrpalkeGrfs[2].LocalMode:=Bit_0;
182:CrpalkeGrfs[2].RemoteON:=Bit_0;
183:CrpalkeGrfs[2].Reset2handkWhValues:=Bit_0;
184:CrpalkeGrfs[2].ResetAlarm:=Bit_0;
185:CrpalkeGrfs[2].ResetAlarmLog:=Bit_0;
186:CrpalkeGrfs[2].ResetDevice:=Bit_0;
187:CrpalkeGrfs[2].SetAutomatic:=Bit_0;
188:CrpalkeGrfs[2].SetConstFreqMode:=Bit_0;
189:CrpalkeGrfs[2].SetConstPress:=Bit_0;
190:CrpalkeGrfs[2].SetLocalMode:=Bit_0;
191:CrpalkeGrfs[2].SetMaxRunMode:=Bit_0;
192:CrpalkeGrfs[2].SetMinRunMode:=Bit_0;
193:CrpalkeGrfs[2].SetPropPress:=Bit_0;
194:CrpalkeGrfs[2].SetReference:=Bit_0;
195:CrpalkeGrfs[2].SetRemoteMode:=Bit_0;
196:CrpalkeGrfs[2].SetTwinModeAlt:=Bit_0;
197:CrpalkeGrfs[2].SetTwinModeSpare:=Bit_0;
198:CrpalkeGrfs[2].SetTwinModeSync:=Bit_0;
199:CrpalkeGrfs[2].Start:=Bit_0;
200:CrpalkeGrfs[2].Stop:=Bit_0;
201:CrpalkeGrfs[3].AlarmAktiven:=Bit_0;
202:CrpalkeGrfs[3].Deluje:=Bit_0;
203:CrpalkeGrfs[3].LocalMode:=Bit_0;
204:CrpalkeGrfs[3].RemoteON:=Bit_0;
205:CrpalkeGrfs[3].Reset2handkWhValues:=Bit_0;
206:CrpalkeGrfs[3].ResetAlarm:=Bit_0;
207:CrpalkeGrfs[3].ResetAlarmLog:=Bit_0;
208:CrpalkeGrfs[3].ResetDevice:=Bit_0;
209:CrpalkeGrfs[3].SetAutomatic:=Bit_0;
210:CrpalkeGrfs[3].SetConstFreqMode:=Bit_0;
211:CrpalkeGrfs[3].SetConstPress:=Bit_0;
212:CrpalkeGrfs[3].SetLocalMode:=Bit_0;
213:CrpalkeGrfs[3].SetMaxRunMode:=Bit_0;
214:CrpalkeGrfs[3].SetMinRunMode:=Bit_0;
215:CrpalkeGrfs[3].SetPropPress:=Bit_0;
216:CrpalkeGrfs[3].SetReference:=Bit_0;
217:CrpalkeGrfs[3].SetRemoteMode:=Bit_0;
218:CrpalkeGrfs[3].SetTwinModeAlt:=Bit_0;
219:CrpalkeGrfs[3].SetTwinModeSpare:=Bit_0;
220:CrpalkeGrfs[3].SetTwinModeSync:=Bit_0;
221:CrpalkeGrfs[3].Start:=Bit_0;
222:CrpalkeGrfs[3].Stop:=Bit_0;
223:CrpalkeGrfs[4].AlarmAktiven:=Bit_0;
224:CrpalkeGrfs[4].Deluje:=Bit_0;
225:CrpalkeGrfs[4].LocalMode:=Bit_0;
226:CrpalkeGrfs[4].RemoteON:=Bit_0;
227:CrpalkeGrfs[4].Reset2handkWhValues:=Bit_0;
228:CrpalkeGrfs[4].ResetAlarm:=Bit_0;
229:CrpalkeGrfs[4].ResetAlarmLog:=Bit_0;
230:CrpalkeGrfs[4].ResetDevice:=Bit_0;
231:CrpalkeGrfs[4].SetAutomatic:=Bit_0;
232:CrpalkeGrfs[4].SetConstFreqMode:=Bit_0;
233:CrpalkeGrfs[4].SetConstPress:=Bit_0;
234:CrpalkeGrfs[4].SetLocalMode:=Bit_0;
235:CrpalkeGrfs[4].SetMaxRunMode:=Bit_0;
236:CrpalkeGrfs[4].SetMinRunMode:=Bit_0;
237:CrpalkeGrfs[4].SetPropPress:=Bit_0;
238:CrpalkeGrfs[4].SetReference:=Bit_0;
239:CrpalkeGrfs[4].SetRemoteMode:=Bit_0;
240:CrpalkeGrfs[4].SetTwinModeAlt:=Bit_0;
241:CrpalkeGrfs[4].SetTwinModeSpare:=Bit_0;
242:CrpalkeGrfs[4].SetTwinModeSync:=Bit_0;
243:CrpalkeGrfs[4].Start:=Bit_0;
244:CrpalkeGrfs[4].Stop:=Bit_0;
245:CrpalkeGrfs[5].AlarmAktiven:=Bit_0;
246:CrpalkeGrfs[5].Deluje:=Bit_0;
247:CrpalkeGrfs[5].LocalMode:=Bit_0;
248:CrpalkeGrfs[5].RemoteON:=Bit_0;
249:CrpalkeGrfs[5].Reset2handkWhValues:=Bit_0;
250:CrpalkeGrfs[5].ResetAlarm:=Bit_0;
251:CrpalkeGrfs[5].ResetAlarmLog:=Bit_0;
252:CrpalkeGrfs[5].ResetDevice:=Bit_0;
253:CrpalkeGrfs[5].SetAutomatic:=Bit_0;
254:CrpalkeGrfs[5].SetConstFreqMode:=Bit_0;
255:CrpalkeGrfs[5].SetConstPress:=Bit_0;
256:CrpalkeGrfs[5].SetLocalMode:=Bit_0;
257:CrpalkeGrfs[5].SetMaxRunMode:=Bit_0;
258:CrpalkeGrfs[5].SetMinRunMode:=Bit_0;
259:CrpalkeGrfs[5].SetPropPress:=Bit_0;
260:CrpalkeGrfs[5].SetReference:=Bit_0;
261:CrpalkeGrfs[5].SetRemoteMode:=Bit_0;
262:CrpalkeGrfs[5].SetTwinModeAlt:=Bit_0;
263:CrpalkeGrfs[5].SetTwinModeSpare:=Bit_0;
264:CrpalkeGrfs[5].SetTwinModeSync:=Bit_0;
265:CrpalkeGrfs[5].Start:=Bit_0;
266:CrpalkeGrfs[5].Stop:=Bit_0;
267:CrpalkeGrfs[6].AlarmAktiven:=Bit_0;
268:CrpalkeGrfs[6].Deluje:=Bit_0;
269:CrpalkeGrfs[6].LocalMode:=Bit_0;
270:CrpalkeGrfs[6].RemoteON:=Bit_0;
271:CrpalkeGrfs[6].Reset2handkWhValues:=Bit_0;
272:CrpalkeGrfs[6].ResetAlarm:=Bit_0;
273:CrpalkeGrfs[6].ResetAlarmLog:=Bit_0;
274:CrpalkeGrfs[6].ResetDevice:=Bit_0;
275:CrpalkeGrfs[6].SetAutomatic:=Bit_0;
276:CrpalkeGrfs[6].SetConstFreqMode:=Bit_0;
277:CrpalkeGrfs[6].SetConstPress:=Bit_0;
278:CrpalkeGrfs[6].SetLocalMode:=Bit_0;
279:CrpalkeGrfs[6].SetMaxRunMode:=Bit_0;
280:CrpalkeGrfs[6].SetMinRunMode:=Bit_0;
281:CrpalkeGrfs[6].SetPropPress:=Bit_0;
282:CrpalkeGrfs[6].SetReference:=Bit_0;
283:CrpalkeGrfs[6].SetRemoteMode:=Bit_0;
284:CrpalkeGrfs[6].SetTwinModeAlt:=Bit_0;
285:CrpalkeGrfs[6].SetTwinModeSpare:=Bit_0;
286:CrpalkeGrfs[6].SetTwinModeSync:=Bit_0;
287:CrpalkeGrfs[6].Start:=Bit_0;
288:CrpalkeGrfs[6].Stop:=Bit_0;
289:CrpalkeGrfs[7].AlarmAktiven:=Bit_0;
290:CrpalkeGrfs[7].Deluje:=Bit_0;
291:CrpalkeGrfs[7].LocalMode:=Bit_0;
292:CrpalkeGrfs[7].RemoteON:=Bit_0;
293:CrpalkeGrfs[7].Reset2handkWhValues:=Bit_0;
294:CrpalkeGrfs[7].ResetAlarm:=Bit_0;
295:CrpalkeGrfs[7].ResetAlarmLog:=Bit_0;
296:CrpalkeGrfs[7].ResetDevice:=Bit_0;
297:CrpalkeGrfs[7].SetAutomatic:=Bit_0;
298:CrpalkeGrfs[7].SetConstFreqMode:=Bit_0;
299:CrpalkeGrfs[7].SetConstPress:=Bit_0;
300:CrpalkeGrfs[7].SetLocalMode:=Bit_0;
301:CrpalkeGrfs[7].SetMaxRunMode:=Bit_0;
302:CrpalkeGrfs[7].SetMinRunMode:=Bit_0;
303:CrpalkeGrfs[7].SetPropPress:=Bit_0;
304:CrpalkeGrfs[7].SetReference:=Bit_0;
305:CrpalkeGrfs[7].SetRemoteMode:=Bit_0;
306:CrpalkeGrfs[7].SetTwinModeAlt:=Bit_0;
307:CrpalkeGrfs[7].SetTwinModeSpare:=Bit_0;
308:CrpalkeGrfs[7].SetTwinModeSync:=Bit_0;
309:CrpalkeGrfs[7].Start:=Bit_0;
310:CrpalkeGrfs[7].Stop:=Bit_0;
311:CrpalkeGrfs[8].AlarmAktiven:=Bit_0;
312:CrpalkeGrfs[8].Deluje:=Bit_0;
313:CrpalkeGrfs[8].LocalMode:=Bit_0;
314:CrpalkeGrfs[8].RemoteON:=Bit_0;
315:CrpalkeGrfs[8].Reset2handkWhValues:=Bit_0;
316:CrpalkeGrfs[8].ResetAlarm:=Bit_0;
317:CrpalkeGrfs[8].ResetAlarmLog:=Bit_0;
318:CrpalkeGrfs[8].ResetDevice:=Bit_0;
319:CrpalkeGrfs[8].SetAutomatic:=Bit_0;
320:CrpalkeGrfs[8].SetConstFreqMode:=Bit_0;
321:CrpalkeGrfs[8].SetConstPress:=Bit_0;
322:CrpalkeGrfs[8].SetLocalMode:=Bit_0;
323:CrpalkeGrfs[8].SetMaxRunMode:=Bit_0;
324:CrpalkeGrfs[8].SetMinRunMode:=Bit_0;
325:CrpalkeGrfs[8].SetPropPress:=Bit_0;
326:CrpalkeGrfs[8].SetReference:=Bit_0;
327:CrpalkeGrfs[8].SetRemoteMode:=Bit_0;
328:CrpalkeGrfs[8].SetTwinModeAlt:=Bit_0;
329:CrpalkeGrfs[8].SetTwinModeSpare:=Bit_0;
330:CrpalkeGrfs[8].SetTwinModeSync:=Bit_0;
331:CrpalkeGrfs[8].Start:=Bit_0;
332:CrpalkeGrfs[8].Stop:=Bit_0;
333:CrpalkeGrfs[9].AlarmAktiven:=Bit_0;
334:CrpalkeGrfs[9].Deluje:=Bit_0;
335:CrpalkeGrfs[9].LocalMode:=Bit_0;
336:CrpalkeGrfs[9].RemoteON:=Bit_0;
337:CrpalkeGrfs[9].Reset2handkWhValues:=Bit_0;
338:CrpalkeGrfs[9].ResetAlarm:=Bit_0;
339:CrpalkeGrfs[9].ResetAlarmLog:=Bit_0;
340:CrpalkeGrfs[9].ResetDevice:=Bit_0;
341:CrpalkeGrfs[9].SetAutomatic:=Bit_0;
342:CrpalkeGrfs[9].SetConstFreqMode:=Bit_0;
343:CrpalkeGrfs[9].SetConstPress:=Bit_0;
344:CrpalkeGrfs[9].SetLocalMode:=Bit_0;
345:CrpalkeGrfs[9].SetMaxRunMode:=Bit_0;
346:CrpalkeGrfs[9].SetMinRunMode:=Bit_0;
347:CrpalkeGrfs[9].SetPropPress:=Bit_0;
348:CrpalkeGrfs[9].SetReference:=Bit_0;
349:CrpalkeGrfs[9].SetRemoteMode:=Bit_0;
350:CrpalkeGrfs[9].SetTwinModeAlt:=Bit_0;
351:CrpalkeGrfs[9].SetTwinModeSpare:=Bit_0;
352:CrpalkeGrfs[9].SetTwinModeSync:=Bit_0;
353:CrpalkeGrfs[9].Start:=Bit_0;
354:CrpalkeGrfs[9].Stop:=Bit_0;
355:CrpDanfossGenError[1]:=Bit_0;
356:CrpDanfossGenError[2]:=Bit_0;
357:CrpDanfossGenError[3]:=Bit_0;
358:CrpDanfossGenError[4]:=Bit_0;
359:CrpDanfossNaCas[1]:=Bit_0;
360:CrpDanfossNaCas[2]:=Bit_0;
361:CrpDanfossON[1]:=Bit_0;
362:CrpDanfossON[2]:=Bit_0;
363:CrpDanfossON[3]:=Bit_0;
364:CrpDanfossON[4]:=Bit_0;
365:CrpDanfossStatusError[1]:=Bit_0;
366:CrpDanfossStatusError[2]:=Bit_0;
367:CrpDanfossStatusError[3]:=Bit_0;
368:CrpDanfossStatusError[4]:=Bit_0;
369:CrpGrundfosGenError[10]:=Bit_0;
370:CrpGrundfosGenError[11]:=Bit_0;
371:CrpGrundfosGenError[12]:=Bit_0;
372:CrpGrundfosGenError[13]:=Bit_0;
373:CrpGrundfosGenError[14]:=Bit_0;
374:CrpGrundfosGenError[1]:=Bit_0;
375:CrpGrundfosGenError[2]:=Bit_0;
376:CrpGrundfosGenError[3]:=Bit_0;
377:CrpGrundfosGenError[4]:=Bit_0;
378:CrpGrundfosGenError[5]:=Bit_0;
379:CrpGrundfosGenError[6]:=Bit_0;
380:CrpGrundfosGenError[7]:=Bit_0;
381:CrpGrundfosGenError[8]:=Bit_0;
382:CrpGrundfosGenError[9]:=Bit_0;
383:CrpGrundfosNaCas[1]:=Bit_0;
384:CrpGrundfosNaCas[2]:=Bit_0;
385:CrpGrundfosNaCas[3]:=Bit_0;
386:CrpGrundfosNaCas[4]:=Bit_0;
387:CrpGrundfosNaCas[5]:=Bit_0;
388:CrpGrundfosNaCas[6]:=Bit_0;
389:CrpGrundfosNaCas[7]:=Bit_0;
390:CrpGrundfosNaTlak[1]:=Bit_0;
391:CrpGrundfosNaTlak[2]:=Bit_0;
392:CrpGrundfosNaTlak[3]:=Bit_0;
393:CrpGrundfosNaTlak[4]:=Bit_0;
394:CrpGrundfosNaTlak[5]:=Bit_0;
395:CrpGrundfosNaTlak[6]:=Bit_0;
396:CrpGrundfosNaTlak[7]:=Bit_0;
397:CrpGrundfosON[10]:=Bit_0;
398:CrpGrundfosON[11]:=Bit_0;
399:CrpGrundfosON[12]:=Bit_0;
400:CrpGrundfosON[13]:=Bit_0;
401:CrpGrundfosON[14]:=Bit_0;
402:CrpGrundfosON[1]:=Bit_0;
403:CrpGrundfosON[2]:=Bit_0;
404:CrpGrundfosON[3]:=Bit_0;
405:CrpGrundfosON[4]:=Bit_0;
406:CrpGrundfosON[5]:=Bit_0;
407:CrpGrundfosON[6]:=Bit_0;
408:CrpGrundfosON[7]:=Bit_0;
409:CrpGrundfosON[8]:=Bit_0;
410:CrpGrundfosON[9]:=Bit_0;
411:CrpGrundfosStatusError[10]:=Bit_0;
412:CrpGrundfosStatusError[11]:=Bit_0;
413:CrpGrundfosStatusError[12]:=Bit_0;
414:CrpGrundfosStatusError[13]:=Bit_0;
415:CrpGrundfosStatusError[14]:=Bit_0;
416:CrpGrundfosStatusError[1]:=Bit_0;
417:CrpGrundfosStatusError[2]:=Bit_0;
418:CrpGrundfosStatusError[3]:=Bit_0;
419:CrpGrundfosStatusError[4]:=Bit_0;
420:CrpGrundfosStatusError[5]:=Bit_0;
421:CrpGrundfosStatusError[6]:=Bit_0;
422:CrpGrundfosStatusError[7]:=Bit_0;
423:CrpGrundfosStatusError[8]:=Bit_0;
424:CrpGrundfosStatusError[9]:=Bit_0;
425:DanfossHMKontOnOff[1]:=Bit_0;
426:DanfossHMKontOnOff[2]:=Bit_0;
427:DanfossHMKontOnOff[3]:=Bit_0;
428:DanfossHMKontOnOff[4]:=Bit_0;
429:DI_230VAC_OK:=Bit_0;
430:DI_24VAC_OK:=Bit_0;
431:DI_24VDC_OK:=Bit_0;
432:DI_AkumTopVodeAUTO:=Bit_0;
433:DI_AkumTopVodeKontON:=Bit_0;
434:DI_CrpHM1AUTO:=Bit_0;
435:DI_CrpHM1endOFFtoON:=Bit_0;
436:DI_CrpHM1ERR:=Bit_0;
437:DI_CrpHM1kontON:=Bit_0;
438:DI_CrpHM2AUTO:=Bit_0;
439:DI_CrpHM2endOFFtoON:=Bit_0;
440:DI_CrpHM2ERR:=Bit_0;
441:DI_CrpHM2kontON:=Bit_0;
442:DI_CrpHM3AUTO:=Bit_0;
443:DI_CrpHM3endOFFtoON:=Bit_0;
444:DI_CrpHM3ERR:=Bit_0;
445:DI_CrpHM3kontON:=Bit_0;
446:DI_CrpHM4AUTO:=Bit_0;
447:DI_CrpHM4endOFFtoON:=Bit_0;
448:DI_CrpHM4ERR:=Bit_0;
449:DI_CrpHM4kontON:=Bit_0;
450:DI_CrpHM5AUTO:=Bit_0;
451:DI_CrpHM6AUTO:=Bit_0;
452:DI_CrpHM7AUTO:=Bit_0;
453:DI_CrpHM8AUTO:=Bit_0;
454:DI_CrpMN1AUTO:=Bit_0;
455:DI_CrpMN1kontON:=Bit_0;
456:DI_CrpTM10AUTO:=Bit_0;
457:DI_CrpTM11TM12AUTO:=Bit_0;
458:DI_CrpTM11TM12kontON:=Bit_0;
459:DI_CrpTM1AUTO:=Bit_0;
460:DI_CrpTM2AUTO:=Bit_0;
461:DI_CrpTM3AUTO:=Bit_0;
462:DI_CrpTM4AUTO:=Bit_0;
463:DI_CrpTM5AUTO:=Bit_0;
464:DI_CrpTM6AUTO:=Bit_0;
465:DI_CrpTM7AUTO:=Bit_0;
466:DI_CrpTM8AUTO:=Bit_0;
467:DI_CrpTM9AUTO:=Bit_0;
468:DI_GlStikaloDieselON:=Bit_0;
469:DI_GlStikaloMrezaON:=Bit_0;
470:DI_GlStikaloUpsON:=Bit_0;
471:DI_HladStAUTO:=Bit_0;
472:DI_HladStCrpHladH2OON:=Bit_0;
473:DI_HladStERR:=Bit_0;
474:DI_Klima1ERR:=Bit_0;
475:DI_Klima1filterZAM:=Bit_0;
476:DI_Klima1FIRE:=Bit_0;
477:DI_Klima1OFFtoON:=Bit_0;
478:DI_Klima1ON:=Bit_0;
479:DI_Klima1zascStON:=Bit_0;
480:DI_Klima2ERR:=Bit_0;
481:DI_Klima2filterZAM:=Bit_0;
482:DI_Klima2FIRE:=Bit_0;
483:DI_Klima2OFFtoON:=Bit_0;
484:DI_Klima2ON:=Bit_0;
485:DI_Klima2zascStON:=Bit_0;
486:DI_Komp1ERR:=Bit_0;
487:DI_Komp1ON:=Bit_0;
488:DI_Komp2ERR:=Bit_0;
489:DI_Komp2ON:=Bit_0;
490:DI_Kond1AUTO:=Bit_0;
491:DI_Kond1FS1FS2:=Bit_0;
492:DI_Kond1ON:=Bit_0;
493:DI_Kond1zascStON:=Bit_0;
494:DI_Kond2AUTO:=Bit_0;
495:DI_Kond2FS1FS2:=Bit_0;
496:DI_Kond2ON:=Bit_0;
497:DI_Kond2zascStON:=Bit_0;
498:DI_Kond3AUTO:=Bit_0;
499:DI_Kond3FS1FS2:=Bit_0;
500:DI_Kond3ON:=Bit_0;
501:DI_Kond3zascStON:=Bit_0;
502:DI_Lop1PL1Odprta:=Bit_0;
503:DI_Lop1PL1Zaprta:=Bit_0;
504:DI_Lop1PL2Odprta:=Bit_0;
505:DI_Lop1PL2Zaprta:=Bit_0;
506:DI_Lop1PL3Odprta:=Bit_0;
507:DI_Lop1PL3Zaprta:=Bit_0;
508:DI_Lop3Y1Odprta:=Bit_0;
509:DI_Lop3Y1Zaprta:=Bit_0;
510:DI_Lop4Y1Odprta:=Bit_0;
511:DI_Lop4Y1Zaprta:=Bit_0;
512:DI_PotrditevAlarmov:=Bit_0;
513:DI_RazlitjeVodeEXP1:=Bit_0;
514:DI_RazlitjeVodeEXP2:=Bit_0;
515:DI_RazlitjeVodeHP:=Bit_0;
516:DI_RazlitjeVodeK1:=Bit_0;
517:DI_RazlitjeVodeK2:=Bit_0;
518:DI_RazlitjeVodeTP:=Bit_0;
519:DI_ToplPostGenErr:=Bit_0;
520:DI_UPS_Alarm:=Bit_0;
521:DI_UPS_BatNacin:=Bit_0;
522:DI_UPS_Polnjenje:=Bit_0;
523:DI_Vent1Auto:=Bit_0;
524:DI_Vent1kontON:=Bit_0;
525:DI_Vent2Auto:=Bit_0;
526:DI_Vent2kontON:=Bit_0;
527:DI_Vent3Auto:=Bit_0;
528:DI_Vent3kontON:=Bit_0;
529:DI_Vent4Auto:=Bit_0;
530:DI_Vent4kontON:=Bit_0;
531:DI_Vent5Auto:=Bit_0;
532:DI_Vent5kontON:=Bit_0;
533:DI_Vent6Auto:=Bit_0;
534:DI_Vent6kontON:=Bit_0;
535:DI_Vlaz1ERR:=Bit_0;
536:DI_Vlaz1ON:=Bit_0;
537:DI_Vlaz2ERR:=Bit_0;
538:DI_Vlaz2ON:=Bit_0;
539:DIN_230VAC_OK:=Bit_0;
540:DIN_24VAC_OK:=Bit_0;
541:DIN_24VDC_OK:=Bit_0;
542:DIN_CrpHM1ERR:=Bit_0;
543:DIN_CrpHM2ERR:=Bit_0;
544:DIN_CrpHM3ERR:=Bit_0;
545:DIN_CrpHM4ERR:=Bit_0;
546:DIN_HladStERR:=Bit_0;
547:DIN_Klima1ERR:=Bit_0;
548:DIN_Klima1filterZAM:=Bit_0;
549:DIN_Klima1zascStON:=Bit_0;
550:DIN_Klima2ERR:=Bit_0;
551:DIN_Klima2filterZAM:=Bit_0;
552:DIN_Klima2zascStON:=Bit_0;
553:DIN_Komp1ERR:=Bit_0;
554:DIN_Komp1ON:=Bit_0;
555:DIN_Komp2ERR:=Bit_0;
556:DIN_Komp2ON:=Bit_0;
557:DIN_Kond1zascStON:=Bit_0;
558:DIN_Kond2zascStON:=Bit_0;
559:DIN_Kond3zascStON:=Bit_0;
560:DIN_Vlaz1ERR:=Bit_0;
561:DIN_Vlaz2ERR:=Bit_0;
562:DO_BojlerTE1Vklop:=Bit_0;
563:DO_CrpHM1Vklop:=Bit_0;
564:DO_CrpHM2Vklop:=Bit_0;
565:DO_CrpHM3Vklop:=Bit_0;
566:DO_CrpHM4Vklop:=Bit_0;
567:DO_CrpMN1Vklop:=Bit_0;
568:DO_CrpTM11Vklop:=Bit_0;
569:DO_GrundfosVklopL:=Bit_0;
570:DO_GrundfosVklopN:=Bit_0;
571:DO_HladStrIzklop:=Bit_0;
572:DO_KE1Vklop:=Bit_0;
573:DO_KE2Vklop:=Bit_0;
574:DO_KE3Vklop:=Bit_0;
575:DO_Klima1Vklop:=Bit_0;
576:DO_Klima2Vklop:=Bit_0;
577:DO_Lop1PL1Vklop:=Bit_0;
578:DO_Lop1PL2Vklop:=Bit_0;
579:DO_Lop1PL3Vklop:=Bit_0;
580:DO_Lop3Y1Vklop:=Bit_0;
581:DO_Lop4Y1Vklop:=Bit_0;
582:DO_RazE11_10Vklop:=Bit_0;
583:DO_RazE11_11Vklop:=Bit_0;
584:DO_RazE11_1Vklop:=Bit_0;
585:DO_RazE11_2Vklop:=Bit_0;
586:DO_RazE11_3Vklop:=Bit_0;
587:DO_RazE11_4Vklop:=Bit_0;
588:DO_RazE11_5Vklop:=Bit_0;
589:DO_RazE11_6Vklop:=Bit_0;
590:DO_RazE11_7Vklop:=Bit_0;
591:DO_RazE11_8Vklop:=Bit_0;
592:DO_RazE11_9Vklop:=Bit_0;
593:DO_RazE12_12Vklop:=Bit_0;
594:DO_RazE12_13Vklop:=Bit_0;
595:DO_RazE12_14Vklop:=Bit_0;
596:DO_RazE12_15Vklop:=Bit_0;
597:DO_RazE13_16Vklop:=Bit_0;
598:DO_RazE13_17Vklop:=Bit_0;
599:DO_RazE13_18Vklop:=Bit_0;
600:DO_RazE13_19Vklop:=Bit_0;
601:DO_RazE16_20Vklop:=Bit_0;
602:DO_RazE16_21Vklop:=Bit_0;
603:DO_RazE16_22Vklop:=Bit_0;
604:DO_RazE16_23Vklop:=Bit_0;
605:DO_RazE16_24Vklop:=Bit_0;
606:DO_Vent1Vklop:=Bit_0;
607:DO_Vent2Vklop:=Bit_0;
608:DO_Vent3Vklop:=Bit_0;
609:DO_Vent4Vklop:=Bit_0;
610:DO_Vent5Vklop:=Bit_0;
611:DO_Vent6Vklop:=Bit_0;
612:ErrComCirc[1]:=Bit_0;
613:ErrComCirc[2]:=Bit_0;
614:ErrComDanfossHM[1]:=Bit_0;
615:ErrComDanfossHM[2]:=Bit_0;
616:ErrComDanfossHM[3]:=Bit_0;
617:ErrComDanfossHM[4]:=Bit_0;
618:ErrComGrundfos[0]:=Bit_0;
619:ErrComGrundfos[10]:=Bit_0;
620:ErrComGrundfos[11]:=Bit_0;
621:ErrComGrundfos[12]:=Bit_0;
622:ErrComGrundfos[13]:=Bit_0;
623:ErrComGrundfos[14]:=Bit_0;
624:ErrComGrundfos[1]:=Bit_0;
625:ErrComGrundfos[2]:=Bit_0;
626:ErrComGrundfos[3]:=Bit_0;
627:ErrComGrundfos[4]:=Bit_0;
628:ErrComGrundfos[5]:=Bit_0;
629:ErrComGrundfos[6]:=Bit_0;
630:ErrComGrundfos[7]:=Bit_0;
631:ErrComGrundfos[8]:=Bit_0;
632:ErrComGrundfos[9]:=Bit_0;
633:ErrComHladStroj:=Bit_0;
634:ErrComKlima[1]:=Bit_0;
635:ErrComKlima[2]:=Bit_0;
636:ErrCommScada:=Bit_0;
637:ErrCommXC100:=Bit_0;
638:ErrComPanelPLC:=Bit_0;
639:ErrComPort2:=Bit_0;
640:ErrComPort3:=Bit_0;
641:ErrComPort4:=Bit_0;
642:ErrComToplPost:=Bit_0;
643:Exp1TlakAlarm:=Bit_0;
644:Exp2TlakAlarm:=Bit_0;
645:HladilniStrojOnOff:=Bit_0;
646:HladStroj.FazeAlarm:=Bit_0;
647:HladStroj.KompresorOljeAlarm:=Bit_0;
648:HladStroj.LANcarelAlarm:=Bit_0;
649:HladStroj.Napaka:=Bit_0;
650:HladStroj.NizekPritiskAlarm:=Bit_0;
651:HladStroj.ObratovalneUreOpozorilo:=Bit_0;
652:HladStroj.OffByAlarms:=Bit_0;
653:HladStroj.PretokAlarm:=Bit_0;
654:HladStroj.RemoteOn:=Bit_0;
655:HladStroj.SenzorAlarm:=Bit_0;
656:HladStroj.SummerOperation:=Bit_0;
657:HladStroj.TemperaturaAlarm:=Bit_0;
658:HladStroj.UnitOn:=Bit_0;
659:HladStroj.UraAlarm:=Bit_0;
660:HladStroj.VisokPritiskAlarm:=Bit_0;
661:HladStroj.VisokPritiskOpozorilo:=Bit_0;
662:HladStroj.ZmrzalniAlarm:=Bit_0;
663:HladStrojErrors[10]:=Bit_0;
664:HladStrojErrors[11]:=Bit_0;
665:HladStrojErrors[12]:=Bit_0;
666:HladStrojErrors[13]:=Bit_0;
667:HladStrojErrors[14]:=Bit_0;
668:HladStrojErrors[15]:=Bit_0;
669:HladStrojErrors[16]:=Bit_0;
670:HladStrojErrors[1]:=Bit_0;
671:HladStrojErrors[2]:=Bit_0;
672:HladStrojErrors[3]:=Bit_0;
673:HladStrojErrors[4]:=Bit_0;
674:HladStrojErrors[5]:=Bit_0;
675:HladStrojErrors[6]:=Bit_0;
676:HladStrojErrors[7]:=Bit_0;
677:HladStrojErrors[8]:=Bit_0;
678:HladStrojErrors[9]:=Bit_0;
679:Klima1errors[10]:=Bit_0;
680:Klima1errors[11]:=Bit_0;
681:Klima1errors[12]:=Bit_0;
682:Klima1errors[1]:=Bit_0;
683:Klima1errors[2]:=Bit_0;
684:Klima1errors[3]:=Bit_0;
685:Klima1errors[4]:=Bit_0;
686:Klima1errors[5]:=Bit_0;
687:Klima1errors[6]:=Bit_0;
688:Klima1errors[7]:=Bit_0;
689:Klima1errors[8]:=Bit_0;
690:Klima1errors[9]:=Bit_0;
691:Klima2errors[10]:=Bit_0;
692:Klima2errors[11]:=Bit_0;
693:Klima2errors[12]:=Bit_0;
694:Klima2errors[1]:=Bit_0;
695:Klima2errors[2]:=Bit_0;
696:Klima2errors[3]:=Bit_0;
697:Klima2errors[4]:=Bit_0;
698:Klima2errors[5]:=Bit_0;
699:Klima2errors[6]:=Bit_0;
700:Klima2errors[7]:=Bit_0;
701:Klima2errors[8]:=Bit_0;
702:Klima2errors[9]:=Bit_0;
703:Klima[1].CrpalkaGrelnika:=Bit_0;
704:Klima[1].DelovanjeVentH1:=Bit_0;
705:Klima[1].DelovanjeVentH2:=Bit_0;
706:Klima[1].Deluje:=Bit_0;
707:Klima[1].FilterError:=Bit_0;
708:Klima[1].Napaka:=Bit_0;
709:Klima[1].NapakaPriPretokuZraka:=Bit_0;
710:Klima[1].OkvaraRototerma:=Bit_0;
711:Klima[1].OkvaraVlazilne:=Bit_0;
712:Klima[1].PozarError:=Bit_0;
713:Klima[1].PozarniAlarm:=Bit_0;
714:Klima[1].PreobremenitevMotCrpGr:=Bit_0;
715:Klima[1].PreobremenitevMotVent:=Bit_0;
716:Klima[1].ProtizmrzAktivna:=Bit_0;
717:Klima[1].SkupniAlarmA:=Bit_0;
718:Klima[1].SkupniAlarmB:=Bit_0;
719:Klima[1].VklopRegulacije:=Bit_0;
720:Klima[1].ZamasenFilter:=Bit_0;
721:Klima[2].CrpalkaGrelnika:=Bit_0;
722:Klima[2].DelovanjeVentH1:=Bit_0;
723:Klima[2].DelovanjeVentH2:=Bit_0;
724:Klima[2].Deluje:=Bit_0;
725:Klima[2].FilterError:=Bit_0;
726:Klima[2].Napaka:=Bit_0;
727:Klima[2].NapakaPriPretokuZraka:=Bit_0;
728:Klima[2].OkvaraRototerma:=Bit_0;
729:Klima[2].OkvaraVlazilne:=Bit_0;
730:Klima[2].PozarError:=Bit_0;
731:Klima[2].PozarniAlarm:=Bit_0;
732:Klima[2].PreobremenitevMotCrpGr:=Bit_0;
733:Klima[2].PreobremenitevMotVent:=Bit_0;
734:Klima[2].ProtizmrzAktivna:=Bit_0;
735:Klima[2].SkupniAlarmA:=Bit_0;
736:Klima[2].SkupniAlarmB:=Bit_0;
737:Klima[2].VklopRegulacije:=Bit_0;
738:Klima[2].ZamasenFilter:=Bit_0;
739:KondEnotaOnOff[1]:=Bit_0;
740:KondEnotaOnOff[2]:=Bit_0;
741:KondEnotaOnOff[3]:=Bit_0;
742:KontRezervaOnOff[1]:=Bit_0;
743:KontRezervaOnOff[2]:=Bit_0;
744:KontRezervaOnOff[3]:=Bit_0;
745:NapakaSenzorAI[10]:=Bit_0;
746:NapakaSenzorAI[11]:=Bit_0;
747:NapakaSenzorAI[12]:=Bit_0;
748:NapakaSenzorAI[13]:=Bit_0;
749:NapakaSenzorAI[14]:=Bit_0;
750:NapakaSenzorAI[15]:=Bit_0;
751:NapakaSenzorAI[16]:=Bit_0;
752:NapakaSenzorAI[17]:=Bit_0;
753:NapakaSenzorAI[18]:=Bit_0;
754:NapakaSenzorAI[19]:=Bit_0;
755:NapakaSenzorAI[1]:=Bit_0;
756:NapakaSenzorAI[20]:=Bit_0;
757:NapakaSenzorAI[21]:=Bit_0;
758:NapakaSenzorAI[22]:=Bit_0;
759:NapakaSenzorAI[23]:=Bit_0;
760:NapakaSenzorAI[24]:=Bit_0;
761:NapakaSenzorAI[25]:=Bit_0;
762:NapakaSenzorAI[26]:=Bit_0;
763:NapakaSenzorAI[27]:=Bit_0;
764:NapakaSenzorAI[28]:=Bit_0;
765:NapakaSenzorAI[29]:=Bit_0;
766:NapakaSenzorAI[2]:=Bit_0;
767:NapakaSenzorAI[30]:=Bit_0;
768:NapakaSenzorAI[31]:=Bit_0;
769:NapakaSenzorAI[32]:=Bit_0;
770:NapakaSenzorAI[33]:=Bit_0;
771:NapakaSenzorAI[34]:=Bit_0;
772:NapakaSenzorAI[35]:=Bit_0;
773:NapakaSenzorAI[36]:=Bit_0;
774:NapakaSenzorAI[37]:=Bit_0;
775:NapakaSenzorAI[38]:=Bit_0;
776:NapakaSenzorAI[39]:=Bit_0;
777:NapakaSenzorAI[3]:=Bit_0;
778:NapakaSenzorAI[40]:=Bit_0;
779:NapakaSenzorAI[4]:=Bit_0;
780:NapakaSenzorAI[5]:=Bit_0;
781:NapakaSenzorAI[6]:=Bit_0;
782:NapakaSenzorAI[7]:=Bit_0;
783:NapakaSenzorAI[8]:=Bit_0;
784:NapakaSenzorAI[9]:=Bit_0;
785:NapakaSenzorHIA[1]:=Bit_0;
786:NapakaSenzorHIA[2]:=Bit_0;
787:NapakaSenzorHIA[3]:=Bit_0;
788:NapakaSenzorHIA[4]:=Bit_0;
789:NapakaSenzorTIA[1]:=Bit_0;
790:NapakaSenzorTIA[2]:=Bit_0;
791:NapakaSenzorTIA[3]:=Bit_0;
792:NapakaSenzorTIA[4]:=Bit_0;
793:PozarnaLoputaOnOffError[1]:=Bit_0;
794:PozarnaLoputaOnOffError[2]:=Bit_0;
795:PozarnaLoputaOnOffError[3]:=Bit_0;
796:PozarnaLoputaOnOffError[4]:=Bit_0;
797:PozarnaLoputaOnOffError[5]:=Bit_0;
798:PozarnaLoputOnOff[1]:=Bit_0;
799:PozarnaLoputOnOff[2]:=Bit_0;
800:PozarnaLoputOnOff[3]:=Bit_0;
801:PozarnaLoputOnOff[4]:=Bit_0;
802:PozarnaLoputOnOff[5]:=Bit_0;
803:PozarniAlarm:=Bit_0;
804:PrenosUrnika[10]:=Bit_0;
805:PrenosUrnika[11]:=Bit_0;
806:PrenosUrnika[12]:=Bit_0;
807:PrenosUrnika[13]:=Bit_0;
808:PrenosUrnika[14]:=Bit_0;
809:PrenosUrnika[15]:=Bit_0;
810:PrenosUrnika[16]:=Bit_0;
811:PrenosUrnika[17]:=Bit_0;
812:PrenosUrnika[18]:=Bit_0;
813:PrenosUrnika[19]:=Bit_0;
814:PrenosUrnika[1]:=Bit_0;
815:PrenosUrnika[20]:=Bit_0;
816:PrenosUrnika[21]:=Bit_0;
817:PrenosUrnika[22]:=Bit_0;
818:PrenosUrnika[23]:=Bit_0;
819:PrenosUrnika[24]:=Bit_0;
820:PrenosUrnika[25]:=Bit_0;
821:PrenosUrnika[2]:=Bit_0;
822:PrenosUrnika[3]:=Bit_0;
823:PrenosUrnika[4]:=Bit_0;
824:PrenosUrnika[5]:=Bit_0;
825:PrenosUrnika[6]:=Bit_0;
826:PrenosUrnika[7]:=Bit_0;
827:PrenosUrnika[8]:=Bit_0;
828:PrenosUrnika[9]:=Bit_0;
829:RazsvetljavaOnOff[10]:=Bit_0;
830:RazsvetljavaOnOff[11]:=Bit_0;
831:RazsvetljavaOnOff[12]:=Bit_0;
832:RazsvetljavaOnOff[13]:=Bit_0;
833:RazsvetljavaOnOff[14]:=Bit_0;
834:RazsvetljavaOnOff[15]:=Bit_0;
835:RazsvetljavaOnOff[16]:=Bit_0;
836:RazsvetljavaOnOff[17]:=Bit_0;
837:RazsvetljavaOnOff[18]:=Bit_0;
838:RazsvetljavaOnOff[19]:=Bit_0;
839:RazsvetljavaOnOff[1]:=Bit_0;
840:RazsvetljavaOnOff[20]:=Bit_0;
841:RazsvetljavaOnOff[21]:=Bit_0;
842:RazsvetljavaOnOff[22]:=Bit_0;
843:RazsvetljavaOnOff[23]:=Bit_0;
844:RazsvetljavaOnOff[24]:=Bit_0;
845:RazsvetljavaOnOff[25]:=Bit_0;
846:RazsvetljavaOnOff[2]:=Bit_0;
847:RazsvetljavaOnOff[3]:=Bit_0;
848:RazsvetljavaOnOff[4]:=Bit_0;
849:RazsvetljavaOnOff[5]:=Bit_0;
850:RazsvetljavaOnOff[6]:=Bit_0;
851:RazsvetljavaOnOff[7]:=Bit_0;
852:RazsvetljavaOnOff[8]:=Bit_0;
853:RazsvetljavaOnOff[9]:=Bit_0;
854:RazsvetljavaRocno:=Bit_0;
855:SetDateTime:=Bit_0;
856:SetDateTimeDemand:=Bit_0;
857:SetDateTimeError:=Bit_0;
858:SetDateTimeFinished:=Bit_0;
859:SetRemoteOnOff[1]:=Bit_0;
860:SetRemoteOnOff[2]:=Bit_0;
861:SlabaBaterijaPLC_A1:=Bit_0;
862:SlabaBaterijaPLC_A100:=Bit_0;
863:SO_BojlerTE1Vklop:=Bit_0;
864:SO_CrpHM1Vklop:=Bit_0;
865:SO_CrpHM2Vklop:=Bit_0;
866:SO_CrpHM3Vklop:=Bit_0;
867:SO_CrpHM4Vklop:=Bit_0;
868:SO_CrpMN1Vklop:=Bit_0;
869:SO_CrpTM11Vklop:=Bit_0;
870:SO_HladStrVklop:=Bit_0;
871:SO_KE1Vklop:=Bit_0;
872:SO_KE2Vklop:=Bit_0;
873:SO_KE3Vklop:=Bit_0;
874:SO_rezerva1_3:=Bit_0;
875:SO_rezerva1_4:=Bit_0;
876:SO_rezerva1_5:=Bit_0;
877:SO_Vent1Vklop:=Bit_0;
878:SO_Vent2Vklop:=Bit_0;
879:SO_Vent3Vklop:=Bit_0;
880:SO_Vent4Vklop:=Bit_0;
881:SO_Vent5Vklop:=Bit_0;
882:SO_Vent6Vklop:=Bit_0;
883:TEgrelecNaTemp:=Bit_0;
884:TEgrelecTempVklop:=Bit_0;
885:TempTSprevisoka:=Bit_0;
886:ToplPost.HKcrpalkaON:=Bit_0;
887:ToplPost.HKcrpDnevniRezim:=Bit_0;
888:ToplPost.HKcrpNocniRezim:=Bit_0;
889:ToplPost.HKrocniRezim:=Bit_0;
890:ToplPost.SkupnaNapaka:=Bit_0;
891:ToplPost.TVcrpalkaON:=Bit_0;
892:ToplPost.TVrocniRezim:=Bit_0;
893:ToplPostErrors[0]:=Bit_0;
894:ToplPostErrors[10]:=Bit_0;
895:ToplPostErrors[11]:=Bit_0;
896:ToplPostErrors[12]:=Bit_0;
897:ToplPostErrors[13]:=Bit_0;
898:ToplPostErrors[14]:=Bit_0;
899:ToplPostErrors[15]:=Bit_0;
900:ToplPostErrors[16]:=Bit_0;
901:ToplPostErrors[17]:=Bit_0;
902:ToplPostErrors[1]:=Bit_0;
903:ToplPostErrors[2]:=Bit_0;
904:ToplPostErrors[3]:=Bit_0;
905:ToplPostErrors[4]:=Bit_0;
906:ToplPostErrors[5]:=Bit_0;
907:ToplPostErrors[6]:=Bit_0;
908:ToplPostErrors[7]:=Bit_0;
909:ToplPostErrors[8]:=Bit_0;
910:ToplPostErrors[9]:=Bit_0;
911:TYventilNaTemp[1]:=Bit_0;
912:TYventilNaTemp[2]:=Bit_0;
913:TYventilNaTemp[3]:=Bit_0;
914:TYventilNaTemp[4]:=Bit_0;
915:UserLoggedIn:=Bit_0;
916:VentilatorOnOff[1]:=Bit_0;
917:VentilatorOnOff[2]:=Bit_0;
918:VentilatorOnOff[3]:=Bit_0;
919:VentilatorOnOff[4]:=Bit_0;
920:VentilatorOnOff[5]:=Bit_0;
921:VentilatorOnOff[6]:=Bit_0;
922:VklopSCFBNapaka[10]:=Bit_0;
923:VklopSCFBNapaka[11]:=Bit_0;
924:VklopSCFBNapaka[12]:=Bit_0;
925:VklopSCFBNapaka[13]:=Bit_0;
926:VklopSCFBNapaka[14]:=Bit_0;
927:VklopSCFBNapaka[15]:=Bit_0;
928:VklopSCFBNapaka[16]:=Bit_0;
929:VklopSCFBNapaka[17]:=Bit_0;
930:VklopSCFBNapaka[18]:=Bit_0;
931:VklopSCFBNapaka[19]:=Bit_0;
932:VklopSCFBNapaka[1]:=Bit_0;
933:VklopSCFBNapaka[20]:=Bit_0;
934:VklopSCFBNapaka[21]:=Bit_0;
935:VklopSCFBNapaka[22]:=Bit_0;
936:VklopSCFBNapaka[23]:=Bit_0;
937:VklopSCFBNapaka[24]:=Bit_0;
938:VklopSCFBNapaka[25]:=Bit_0;
939:VklopSCFBNapaka[2]:=Bit_0;
940:VklopSCFBNapaka[3]:=Bit_0;
941:VklopSCFBNapaka[4]:=Bit_0;
942:VklopSCFBNapaka[5]:=Bit_0;
943:VklopSCFBNapaka[6]:=Bit_0;
944:VklopSCFBNapaka[7]:=Bit_0;
945:VklopSCFBNapaka[8]:=Bit_0;
946:VklopSCFBNapaka[9]:=Bit_0;
947:XVH_AlarmOn:=Bit_0;
948:XVH_IzklopVsehLuci:=Bit_0;
949:XVH_VklopVsehLuci:=Bit_0;
950:PrenasanjeUrnikovAktivno:=Bit_0;
951:PrenasanjeUrnikovAktivno1:=Bit_0;
952:CrpalkeGrfsGal.AlarmAktiven:=Bit_0;
953:CrpalkeGrfsGal.Deluje:=Bit_0;
954:CrpalkeGrfsGal.LocalMode:=Bit_0;
955:CrpalkeGrfsGal.RemoteON:=Bit_0;
956:CrpalkeGrfsGal.Reset2handkWhValues:=Bit_0;
957:CrpalkeGrfsGal.ResetAlarm:=Bit_0;
958:CrpalkeGrfsGal.ResetAlarmLog:=Bit_0;
959:CrpalkeGrfsGal.ResetDevice:=Bit_0;
960:CrpalkeGrfsGal.SetAutomatic:=Bit_0;
961:CrpalkeGrfsGal.SetConstFreqMode:=Bit_0;
962:CrpalkeGrfsGal.SetConstPress:=Bit_0;
963:CrpalkeGrfsGal.SetLocalMode:=Bit_0;
964:CrpalkeGrfsGal.SetMaxRunMode:=Bit_0;
965:CrpalkeGrfsGal.SetMinRunMode:=Bit_0;
966:CrpalkeGrfsGal.SetPropPress:=Bit_0;
967:CrpalkeGrfsGal.SetReference:=Bit_0;
968:CrpalkeGrfsGal.SetRemoteMode:=Bit_0;
969:CrpalkeGrfsGal.SetTwinModeAlt:=Bit_0;
970:CrpalkeGrfsGal.SetTwinModeSpare:=Bit_0;
971:CrpalkeGrfsGal.SetTwinModeSync:=Bit_0;
972:CrpalkeGrfsGal.Start:=Bit_0;
973:CrpalkeGrfsGal.Stop:=Bit_0;
974:DI_rezerva10_2:=Bit_0;
975:DI_rezerva10_7:=Bit_0;
976:DI_rezerva11_4:=Bit_0;
977:DI_rezerva14_0:=Bit_0;
978:DI_rezerva14_2:=Bit_0;
979:DI_rezerva14_3:=Bit_0;
980:DI_rezerva14_4:=Bit_0;
981:DI_rezerva14_5:=Bit_0;
982:DI_rezerva14_7:=Bit_0;
983:DI_rezerva2_4:=Bit_0;
984:DI_rezerva3_5:=Bit_0;
985:DIN_AkumTopVodeAUTO:=Bit_0;
986:DIN_CrpHM1AUTO:=Bit_0;
987:DIN_CrpHM1kontON:=Bit_0;
988:DIN_CrpHM2AUTO:=Bit_0;
989:DIN_CrpHM2kontON:=Bit_0;
990:DIN_CrpHM3AUTO:=Bit_0;
991:DIN_CrpHM3kontON:=Bit_0;
992:DIN_CrpHM4AUTO:=Bit_0;
993:DIN_CrpHM4kontON:=Bit_0;
994:DIN_CrpHM5AUTO:=Bit_0;
995:DIN_CrpHM6AUTO:=Bit_0;
996:DIN_CrpHM7AUTO:=Bit_0;
997:DIN_CrpHM8AUTO:=Bit_0;
998:DIN_CrpMN1AUTO:=Bit_0;
999:DIN_CrpMN1kontON:=Bit_0;
1000:DIN_CrpTM10AUTO:=Bit_0;
1001:DIN_CrpTM11TM12AUTO:=Bit_0;
1002:DIN_CrpTM11TM12kontON:=Bit_0;
1003:DIN_CrpTM1AUTO:=Bit_0;
1004:DIN_CrpTM2AUTO:=Bit_0;
1005:DIN_CrpTM3AUTO:=Bit_0;
1006:DIN_CrpTM4AUTO:=Bit_0;
1007:DIN_CrpTM5AUTO:=Bit_0;
1008:DIN_CrpTM6AUTO:=Bit_0;
1009:DIN_CrpTM7AUTO:=Bit_0;
1010:DIN_CrpTM8AUTO:=Bit_0;
1011:DIN_CrpTM9AUTO:=Bit_0;
1012:DIN_GlStikaloDieselON:=Bit_0;
1013:DIN_GlStikaloMrezaON:=Bit_0;
1014:DIN_GlStikaloUpsON:=Bit_0;
1015:DIN_HladStAUTO:=Bit_0;
1016:DIN_Kond1AUTO:=Bit_0;
1017:DIN_Kond2AUTO:=Bit_0;
1018:DIN_Kond3AUTO:=Bit_0;
1019:DIN_Vent1Auto:=Bit_0;
1020:DIN_Vent1kontON:=Bit_0;
1021:DIN_Vent2Auto:=Bit_0;
1022:DIN_Vent2kontON:=Bit_0;
1023:DIN_Vent3Auto:=Bit_0;
1024:DIN_Vent3kontON:=Bit_0;
1025:DIN_Vent4Auto:=Bit_0;
1026:DIN_Vent4kontON:=Bit_0;
1027:DIN_Vent5Auto:=Bit_0;
1028:DIN_Vent5kontON:=Bit_0;
1029:DIN_Vent6Auto:=Bit_0;
1030:DIN_Vent6kontON:=Bit_0;
1031:DO_rezerva0_2:=Bit_0;
1032:DO_rezerva0_3:=Bit_0;
1033:DO_rezerva0_4:=Bit_0;
1034:DO_rezerva0_5:=Bit_0;
1035:DO_rezerva1_3:=Bit_0;
1036:DO_rezerva1_4:=Bit_0;
1037:DO_rezerva1_5:=Bit_0;
1038:DO_rezerva3_4:=Bit_0;
1039:DO_rezerva3_6:=Bit_0;
1040:DO_rezerva4_0:=Bit_0;
1041:PrenosUrnika[26]:=Bit_0;
1042:PrenosUrnika[27]:=Bit_0;
1043:PrenosUrnika[28]:=Bit_0;
1044:PrenosUrnika[29]:=Bit_0;
1045:PrenosUrnika[30]:=Bit_0;
1046:PrenosUrnika[31]:=Bit_0;
1047:PrenosUrnika[32]:=Bit_0;
1048:PrenosUrnika[33]:=Bit_0;
1049:PrenosUrnika[34]:=Bit_0;
1050:PrenosUrnika[35]:=Bit_0;
1051:PrenosUrnika[36]:=Bit_0;
1052:PrenosUrnika[37]:=Bit_0;
1053:PrenosUrnika[38]:=Bit_0;
1054:PrenosUrnika[39]:=Bit_0;
1055:PrenosUrnika[40]:=Bit_0;
1056:PrenosUrnika[41]:=Bit_0;
1057:PrenosUrnika[42]:=Bit_0;
1058:PrenosUrnika[43]:=Bit_0;
1059:PrenosUrnika[44]:=Bit_0;
1060:PrenosUrnika[45]:=Bit_0;
1061:PrenosUrnika[46]:=Bit_0;
1062:PrenosUrnika[47]:=Bit_0;
1063:PrenosUrnika[48]:=Bit_0;
1064:PrenosUrnika[49]:=Bit_0;
1065:PrenosUrnika[50]:=Bit_0;
1066:PrenosUrnika[51]:=Bit_0;
1067:PrenosUrnika[52]:=Bit_0;
1068:PrenosUrnika[53]:=Bit_0;
1069:PrenosUrnika[54]:=Bit_0;
1070:PrenosUrnika[55]:=Bit_0;
1071:PrenosUrnika[56]:=Bit_0;
1072:PrenosUrnika[57]:=Bit_0;
1073:PrenosUrnika[58]:=Bit_0;
1074:PrenosUrnika[59]:=Bit_0;
1075:PrenosUrnika[60]:=Bit_0;
1076:PrenosUrnika[61]:=Bit_0;
1077:PrenosUrnika[62]:=Bit_0;
1078:PrenosUrnika[63]:=Bit_0;
1079:PrenosUrnika[64]:=Bit_0;
1080:PrenosUrnika[65]:=Bit_0;
1081:PrenosUrnika[66]:=Bit_0;
1082:PrenosUrnika[67]:=Bit_0;
1083:PrenosUrnika[68]:=Bit_0;
1084:PrenosUrnika[69]:=Bit_0;
1085:PrenosUrnika[70]:=Bit_0;
1086:PrenosUrnika[71]:=Bit_0;
1087:PrenosUrnika[72]:=Bit_0;
1088:PrenosUrnika[73]:=Bit_0;
1089:PrenosUrnika[74]:=Bit_0;
1090:PrenosUrnika[75]:=Bit_0;
1091:PrenosUrnika[76]:=Bit_0;
1092:PrenosUrnika[77]:=Bit_0;
1093:PrenosUrnika[78]:=Bit_0;
1094:PrenosUrnika[79]:=Bit_0;
1095:PrenosUrnika[80]:=Bit_0;
1096:PrenosUrnika[81]:=Bit_0;
1097:PrenosUrnika[82]:=Bit_0;
1098:PrenosUrnika[83]:=Bit_0;
1099:PrenosUrnika[84]:=Bit_0;
1100:PrenosUrnika[85]:=Bit_0;
1101:PrenosUrnika[86]:=Bit_0;
1102:PrenosUrnika[87]:=Bit_0;
1103:PrenosUrnika[88]:=Bit_0;
1104:PrenosUrnika[89]:=Bit_0;
1105:PrenosUrnika[90]:=Bit_0;
1106:PrenosUrnika[91]:=Bit_0;
1107:PrenosUrnika[92]:=Bit_0;
1108:PrenosUrnika[93]:=Bit_0;
1109:PrenosUrnika[94]:=Bit_0;
1110:PrenosUrnika[95]:=Bit_0;
1111:PrenosUrnika[96]:=Bit_0;
1112:RazsvRocnoEnaLuc[10]:=Bit_0;
1113:RazsvRocnoEnaLuc[11]:=Bit_0;
1114:RazsvRocnoEnaLuc[12]:=Bit_0;
1115:RazsvRocnoEnaLuc[13]:=Bit_0;
1116:RazsvRocnoEnaLuc[14]:=Bit_0;
1117:RazsvRocnoEnaLuc[15]:=Bit_0;
1118:RazsvRocnoEnaLuc[16]:=Bit_0;
1119:RazsvRocnoEnaLuc[17]:=Bit_0;
1120:RazsvRocnoEnaLuc[18]:=Bit_0;
1121:RazsvRocnoEnaLuc[19]:=Bit_0;
1122:RazsvRocnoEnaLuc[1]:=Bit_0;
1123:RazsvRocnoEnaLuc[20]:=Bit_0;
1124:RazsvRocnoEnaLuc[21]:=Bit_0;
1125:RazsvRocnoEnaLuc[22]:=Bit_0;
1126:RazsvRocnoEnaLuc[23]:=Bit_0;
1127:RazsvRocnoEnaLuc[24]:=Bit_0;
1128:RazsvRocnoEnaLuc[25]:=Bit_0;
1129:RazsvRocnoEnaLuc[2]:=Bit_0;
1130:RazsvRocnoEnaLuc[3]:=Bit_0;
1131:RazsvRocnoEnaLuc[4]:=Bit_0;
1132:RazsvRocnoEnaLuc[5]:=Bit_0;
1133:RazsvRocnoEnaLuc[6]:=Bit_0;
1134:RazsvRocnoEnaLuc[7]:=Bit_0;
1135:RazsvRocnoEnaLuc[8]:=Bit_0;
1136:RazsvRocnoEnaLuc[9]:=Bit_0;
1137:XVH_CrpalkaGrfsPair:=Bit_0;
1138:XVH_CrpGrfsCommErr:=Bit_0;
1139:XVH_CrpGrfsON[10]:=Bit_0;
1140:XVH_CrpGrfsON[11]:=Bit_0;
1141:XVH_CrpGrfsON[12]:=Bit_0;
1142:XVH_CrpGrfsON[13]:=Bit_0;
1143:XVH_CrpGrfsON[14]:=Bit_0;
1144:XVH_CrpGrfsON[1]:=Bit_0;
1145:XVH_CrpGrfsON[2]:=Bit_0;
1146:XVH_CrpGrfsON[3]:=Bit_0;
1147:XVH_CrpGrfsON[4]:=Bit_0;
1148:XVH_CrpGrfsON[5]:=Bit_0;
1149:XVH_CrpGrfsON[6]:=Bit_0;
1150:XVH_CrpGrfsON[7]:=Bit_0;
1151:XVH_CrpGrfsON[8]:=Bit_0;
1152:XVH_CrpGrfsON[9]:=Bit_0;
1153:XVH_CrpGrfsPIDreset:=Bit_0;
1154:XVH_CrpGrfsVisibleData[10]:=Bit_0;
1155:XVH_CrpGrfsVisibleData[11]:=Bit_0;
1156:XVH_CrpGrfsVisibleData[12]:=Bit_0;
1157:XVH_CrpGrfsVisibleData[13]:=Bit_0;
1158:XVH_CrpGrfsVisibleData[14]:=Bit_0;
1159:XVH_CrpGrfsVisibleData[15]:=Bit_0;
1160:XVH_CrpGrfsVisibleData[16]:=Bit_0;
1161:XVH_CrpGrfsVisibleData[1]:=Bit_0;
1162:XVH_CrpGrfsVisibleData[2]:=Bit_0;
1163:XVH_CrpGrfsVisibleData[3]:=Bit_0;
1164:XVH_CrpGrfsVisibleData[4]:=Bit_0;
1165:XVH_CrpGrfsVisibleData[5]:=Bit_0;
1166:XVH_CrpGrfsVisibleData[6]:=Bit_0;
1167:XVH_CrpGrfsVisibleData[7]:=Bit_0;
1168:XVH_CrpGrfsVisibleData[8]:=Bit_0;
1169:XVH_CrpGrfsVisibleData[9]:=Bit_0;
1170:XVH_CrpGrundfosNaCas:=Bit_0;
1171:XVH_CrpGrundfosNaTlak:=Bit_0;
1172:XVH_CrpGrundfosON:=Bit_0;
1173:XVH_CrpGrundfosResetAlarm:=Bit_0;
1174:XVH_CrpGrundfosResetAlarmLog:=Bit_0;
1175:XVH_CrpGrundfosSetRef:=Bit_0;
1176:XVH_RazsvOnOff:=Bit_0;
1177:XVH_setCircNum[1]:=Bit_0;
1178:XVH_setCircNum[2]:=Bit_0;
1179:XVH_setCircNum[3]:=Bit_0;
1180:XVH_setCircNum[4]:=Bit_0;
1181:XVH_setCircNum[5]:=Bit_0;
1182:XVH_UrnikNalozi:=Bit_0;
1183:XVH_UrnikNonStop:=Bit_0;
1184:XVH_UrnikPotrdiVpis:=Bit_0;
1185:XVH_UrnikPreklicVpisa:=Bit_0;
1186:XVH_UrnikShrani:=Bit_0;
1187:XVH_VpisUrnika:=Bit_0;
1188:ErrCommScada2:=Bit_0;
1189:ComSCADA2:=Bit_0;
1190:ComSCADA3:=Bit_0;
1191:Circ_Vpis_Dnevne_energija_scada1:=Bit_0;
1192:Circ_Vpis_Dnevne_energija_scada2:=Bit_0;
1193:Circ_Vpis_Tedenska_energija_scada1:=Bit_0;
1194:Circ_Vpis_Tedenska_energija_scada2:=Bit_0;
1195:Circ_Vpis_Mesecna_energija_scada1:=Bit_0;
1196:Circ_Vpis_Mesecna_energija_scada2:=Bit_0;
(*BOOL*)
END_CASE
END_FUNCTION
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_dWord : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje LONG*)
(**)
4001:XVH_CrpalkaGrfsNum:=Long_0;
4003:XVH_StUrnika:=Long_0;
(*Pisanje REAL*)
(**)
5001:ATVAlarmTemp:=Real_0;
5003:Circ[1].CosFi_III:=Real_0;
5005:Circ[1].DelovnaEnergija:=Real_0;
5007:Circ[1].DelovnaMoc_III:=Real_0;
5009:Circ[1].DelovnaMoc_L1:=Real_0;
5011:Circ[1].DelovnaMoc_L2:=Real_0;
5013:Circ[1].DelovnaMoc_L3:=Real_0;
5015:Circ[1].Frekvenca_L1:=Real_0;
5017:Circ[1].InduktivnaEnergija:=Real_0;
5019:Circ[1].InduktivnaMoc_III:=Real_0;
5021:Circ[1].JalovaMoc_L1:=Real_0;
5023:Circ[1].JalovaMoc_L2:=Real_0;
5025:Circ[1].JalovaMoc_L3:=Real_0;
5027:Circ[1].KapacitivnaEnergija:=Real_0;
5029:Circ[1].KapacitivnaMoc_III:=Real_0;
5031:Circ[1].MaximumDemand:=Real_0;
5033:Circ[1].Napetost_L1_L2:=Real_0;
5035:Circ[1].Napetost_L1_N:=Real_0;
5037:Circ[1].Napetost_L2_L3:=Real_0;
5039:Circ[1].Napetost_L2_N:=Real_0;
5041:Circ[1].Napetost_L3_L1:=Real_0;
5043:Circ[1].Napetost_L3_N:=Real_0;
5045:Circ[1].NavideznaMoc_III:=Real_0;
5047:Circ[1].NicelniTok:=Real_0;
5049:Circ[1].PowerFactor_III:=Real_0;
5051:Circ[1].PowerFactor_L1:=Real_0;
5053:Circ[1].PowerFactor_L2:=Real_0;
5055:Circ[1].PowerFactor_L3:=Real_0;
5057:Circ[1].THDI_L1:=Real_0;
5059:Circ[1].THDI_L2:=Real_0;
5061:Circ[1].THDI_L3:=Real_0;
5063:Circ[1].THDV_L1:=Real_0;
5065:Circ[1].THDV_L2:=Real_0;
5067:Circ[1].THDV_L3:=Real_0;
5069:Circ[1].Tok_L1:=Real_0;
5071:Circ[1].Tok_L2:=Real_0;
5073:Circ[1].Tok_L3:=Real_0;
5075:Circ[1].TokPovprecje_III:=Real_0;
5077:CrpalkeDnfs[1].Current:=Real_0;
5079:CrpalkeDnfs[1].StarterStatus:=Real_0;
5081:CrpalkeDnfs[1].Temerature:=Real_0;
5083:CrpalkeDnfs[1].TripCode:=Real_0;
5085:CrpalkeDnfs[1].UreXC200:=Real_0;
5087:CrpalkeDnfs[2].Current:=Real_0;
5089:CrpalkeDnfs[2].StarterStatus:=Real_0;
5091:CrpalkeDnfs[2].Temerature:=Real_0;
5093:CrpalkeDnfs[2].TripCode:=Real_0;
5095:CrpalkeDnfs[2].UreXC200:=Real_0;
5097:CrpalkeDnfs[3].Current:=Real_0;
5099:CrpalkeDnfs[3].StarterStatus:=Real_0;
5101:CrpalkeDnfs[3].Temerature:=Real_0;
5103:CrpalkeDnfs[3].TripCode:=Real_0;
5105:CrpalkeDnfs[3].UreXC200:=Real_0;
5107:CrpalkeDnfs[4].Current:=Real_0;
5109:CrpalkeDnfs[4].StarterStatus:=Real_0;
5111:CrpalkeDnfs[4].Temerature:=Real_0;
5113:CrpalkeDnfs[4].TripCode:=Real_0;
5115:CrpalkeDnfs[4].UreXC200:=Real_0;
5117:CrpalkeGrfs[10].DeltaSetPoint:=Real_0;
5119:CrpalkeGrfs[10].EnergijaPoraba:=Real_0;
5121:CrpalkeGrfs[10].FrekPretvornikDCNapetost:=Real_0;
5123:CrpalkeGrfs[10].FrekPretvornikDCTok:=Real_0;
5125:CrpalkeGrfs[10].FreqMax:=Real_0;
5127:CrpalkeGrfs[10].FreqMin:=Real_0;
5129:CrpalkeGrfs[10].FreqUpper:=Real_0;
5131:CrpalkeGrfs[10].MocMax:=Real_0;
5133:CrpalkeGrfs[10].MocTrenutna:=Real_0;
5135:CrpalkeGrfs[10].MotorHitrost:=Real_0;
5137:CrpalkeGrfs[10].MotorTok:=Real_0;
5139:CrpalkeGrfs[10].NapajanjeTok:=Real_0;
5141:CrpalkeGrfs[10].NastavitevLokalna:=Real_0;
5143:CrpalkeGrfs[10].NastavitevTrenutna:=Real_0;
5145:CrpalkeGrfs[10].PretokMax:=Real_0;
5147:CrpalkeGrfs[10].PretokMin:=Real_0;
5149:CrpalkeGrfs[10].PretokTrenutni:=Real_0;
5151:CrpalkeGrfs[10].PritiskMax:=Real_0;
5153:CrpalkeGrfs[10].PritiskTrenutni:=Real_0;
5155:CrpalkeGrfs[10].ReferencaMotorjaHzV:=Real_0;
5157:CrpalkeGrfs[10].ReferencaRemote:=Real_0;
5159:CrpalkeGrfs[10].StevecUr2h:=Real_0;
5161:CrpalkeGrfs[10].SystemFeedback:=Real_0;
5163:CrpalkeGrfs[10].SystemReference:=Real_0;
5165:CrpalkeGrfs[10].TemperaturaMotorja:=Real_0;
5167:CrpalkeGrfs[10].UreXC200:=Real_0;
5169:CrpalkeGrfs[11].DeltaSetPoint:=Real_0;
5171:CrpalkeGrfs[11].EnergijaPoraba:=Real_0;
5173:CrpalkeGrfs[11].FrekPretvornikDCNapetost:=Real_0;
5175:CrpalkeGrfs[11].FrekPretvornikDCTok:=Real_0;
5177:CrpalkeGrfs[11].FreqMax:=Real_0;
5179:CrpalkeGrfs[11].FreqMin:=Real_0;
5181:CrpalkeGrfs[11].FreqUpper:=Real_0;
5183:CrpalkeGrfs[11].MocMax:=Real_0;
5185:CrpalkeGrfs[11].MocTrenutna:=Real_0;
5187:CrpalkeGrfs[11].MotorHitrost:=Real_0;
5189:CrpalkeGrfs[11].MotorTok:=Real_0;
5191:CrpalkeGrfs[11].NapajanjeTok:=Real_0;
5193:CrpalkeGrfs[11].NastavitevLokalna:=Real_0;
5195:CrpalkeGrfs[11].NastavitevTrenutna:=Real_0;
5197:CrpalkeGrfs[11].PretokMax:=Real_0;
5199:CrpalkeGrfs[11].PretokMin:=Real_0;
5201:CrpalkeGrfs[11].PretokTrenutni:=Real_0;
5203:CrpalkeGrfs[11].PritiskMax:=Real_0;
5205:CrpalkeGrfs[11].PritiskTrenutni:=Real_0;
5207:CrpalkeGrfs[11].ReferencaMotorjaHzV:=Real_0;
5209:CrpalkeGrfs[11].ReferencaRemote:=Real_0;
5211:CrpalkeGrfs[11].StevecUr2h:=Real_0;
5213:CrpalkeGrfs[11].SystemFeedback:=Real_0;
5215:CrpalkeGrfs[11].SystemReference:=Real_0;
5217:CrpalkeGrfs[11].TemperaturaMotorja:=Real_0;
5219:CrpalkeGrfs[11].UreXC200:=Real_0;
5221:CrpalkeGrfs[12].DeltaSetPoint:=Real_0;
5223:CrpalkeGrfs[12].EnergijaPoraba:=Real_0;
5225:CrpalkeGrfs[12].FrekPretvornikDCNapetost:=Real_0;
5227:CrpalkeGrfs[12].FrekPretvornikDCTok:=Real_0;
5229:CrpalkeGrfs[12].FreqMax:=Real_0;
5231:CrpalkeGrfs[12].FreqMin:=Real_0;
5233:CrpalkeGrfs[12].FreqUpper:=Real_0;
5235:CrpalkeGrfs[12].MocMax:=Real_0;
5237:CrpalkeGrfs[12].MocTrenutna:=Real_0;
5239:CrpalkeGrfs[12].MotorHitrost:=Real_0;
5241:CrpalkeGrfs[12].MotorTok:=Real_0;
5243:CrpalkeGrfs[12].NapajanjeTok:=Real_0;
5245:CrpalkeGrfs[12].NastavitevLokalna:=Real_0;
5247:CrpalkeGrfs[12].NastavitevTrenutna:=Real_0;
5249:CrpalkeGrfs[12].PretokMax:=Real_0;
5251:CrpalkeGrfs[12].PretokMin:=Real_0;
5253:CrpalkeGrfs[12].PretokTrenutni:=Real_0;
5255:CrpalkeGrfs[12].PritiskMax:=Real_0;
5257:CrpalkeGrfs[12].PritiskTrenutni:=Real_0;
5259:CrpalkeGrfs[12].ReferencaMotorjaHzV:=Real_0;
5261:CrpalkeGrfs[12].ReferencaRemote:=Real_0;
5263:CrpalkeGrfs[12].StevecUr2h:=Real_0;
5265:CrpalkeGrfs[12].SystemFeedback:=Real_0;
5267:CrpalkeGrfs[12].SystemReference:=Real_0;
5269:CrpalkeGrfs[12].TemperaturaMotorja:=Real_0;
5271:CrpalkeGrfs[12].UreXC200:=Real_0;
5273:CrpalkeGrfs[13].DeltaSetPoint:=Real_0;
5275:CrpalkeGrfs[13].EnergijaPoraba:=Real_0;
5277:CrpalkeGrfs[13].FrekPretvornikDCNapetost:=Real_0;
5279:CrpalkeGrfs[13].FrekPretvornikDCTok:=Real_0;
5281:CrpalkeGrfs[13].FreqMax:=Real_0;
5283:CrpalkeGrfs[13].FreqMin:=Real_0;
5285:CrpalkeGrfs[13].FreqUpper:=Real_0;
5287:CrpalkeGrfs[13].MocMax:=Real_0;
5289:CrpalkeGrfs[13].MocTrenutna:=Real_0;
5291:CrpalkeGrfs[13].MotorHitrost:=Real_0;
5293:CrpalkeGrfs[13].MotorTok:=Real_0;
5295:CrpalkeGrfs[13].NapajanjeTok:=Real_0;
5297:CrpalkeGrfs[13].NastavitevLokalna:=Real_0;
5299:CrpalkeGrfs[13].NastavitevTrenutna:=Real_0;
5301:CrpalkeGrfs[13].PretokMax:=Real_0;
5303:CrpalkeGrfs[13].PretokMin:=Real_0;
5305:CrpalkeGrfs[13].PretokTrenutni:=Real_0;
5307:CrpalkeGrfs[13].PritiskMax:=Real_0;
5309:CrpalkeGrfs[13].PritiskTrenutni:=Real_0;
5311:CrpalkeGrfs[13].ReferencaMotorjaHzV:=Real_0;
5313:CrpalkeGrfs[13].ReferencaRemote:=Real_0;
5315:CrpalkeGrfs[13].StevecUr2h:=Real_0;
5317:CrpalkeGrfs[13].SystemFeedback:=Real_0;
5319:CrpalkeGrfs[13].SystemReference:=Real_0;
5321:CrpalkeGrfs[13].TemperaturaMotorja:=Real_0;
5323:CrpalkeGrfs[13].UreXC200:=Real_0;
5325:CrpalkeGrfs[14].DeltaSetPoint:=Real_0;
5327:CrpalkeGrfs[14].EnergijaPoraba:=Real_0;
5329:CrpalkeGrfs[14].FrekPretvornikDCNapetost:=Real_0;
5331:CrpalkeGrfs[14].FrekPretvornikDCTok:=Real_0;
5333:CrpalkeGrfs[14].FreqMax:=Real_0;
5335:CrpalkeGrfs[14].FreqMin:=Real_0;
5337:CrpalkeGrfs[14].FreqUpper:=Real_0;
5339:CrpalkeGrfs[14].MocMax:=Real_0;
5341:CrpalkeGrfs[14].MocTrenutna:=Real_0;
5343:CrpalkeGrfs[14].MotorHitrost:=Real_0;
5345:CrpalkeGrfs[14].MotorTok:=Real_0;
5347:CrpalkeGrfs[14].NapajanjeTok:=Real_0;
5349:CrpalkeGrfs[14].NastavitevLokalna:=Real_0;
5351:CrpalkeGrfs[14].NastavitevTrenutna:=Real_0;
5353:CrpalkeGrfs[14].PretokMax:=Real_0;
5355:CrpalkeGrfs[14].PretokMin:=Real_0;
5357:CrpalkeGrfs[14].PretokTrenutni:=Real_0;
5359:CrpalkeGrfs[14].PritiskMax:=Real_0;
5361:CrpalkeGrfs[14].PritiskTrenutni:=Real_0;
5363:CrpalkeGrfs[14].ReferencaMotorjaHzV:=Real_0;
5365:CrpalkeGrfs[14].ReferencaRemote:=Real_0;
5367:CrpalkeGrfs[14].StevecUr2h:=Real_0;
5369:CrpalkeGrfs[14].SystemFeedback:=Real_0;
5371:CrpalkeGrfs[14].SystemReference:=Real_0;
5373:CrpalkeGrfs[14].TemperaturaMotorja:=Real_0;
5375:CrpalkeGrfs[14].UreXC200:=Real_0;
5377:CrpalkeGrfs[1].DeltaSetPoint:=Real_0;
5379:CrpalkeGrfs[1].EnergijaPoraba:=Real_0;
5381:CrpalkeGrfs[1].FrekPretvornikDCNapetost:=Real_0;
5383:CrpalkeGrfs[1].FrekPretvornikDCTok:=Real_0;
5385:CrpalkeGrfs[1].FreqMax:=Real_0;
5387:CrpalkeGrfs[1].FreqMin:=Real_0;
5389:CrpalkeGrfs[1].FreqUpper:=Real_0;
5391:CrpalkeGrfs[1].MocMax:=Real_0;
5393:CrpalkeGrfs[1].MocTrenutna:=Real_0;
5395:CrpalkeGrfs[1].MotorHitrost:=Real_0;
5397:CrpalkeGrfs[1].MotorTok:=Real_0;
5399:CrpalkeGrfs[1].NapajanjeTok:=Real_0;
5401:CrpalkeGrfs[1].NastavitevLokalna:=Real_0;
5403:CrpalkeGrfs[1].NastavitevTrenutna:=Real_0;
5405:CrpalkeGrfs[1].PretokMax:=Real_0;
5407:CrpalkeGrfs[1].PretokMin:=Real_0;
5409:CrpalkeGrfs[1].PretokTrenutni:=Real_0;
5411:CrpalkeGrfs[1].PritiskMax:=Real_0;
5413:CrpalkeGrfs[1].PritiskTrenutni:=Real_0;
5415:CrpalkeGrfs[1].ReferencaMotorjaHzV:=Real_0;
5417:CrpalkeGrfs[1].ReferencaRemote:=Real_0;
5419:CrpalkeGrfs[1].StevecUr2h:=Real_0;
5421:CrpalkeGrfs[1].SystemFeedback:=Real_0;
5423:CrpalkeGrfs[1].SystemReference:=Real_0;
5425:CrpalkeGrfs[1].TemperaturaMotorja:=Real_0;
5427:CrpalkeGrfs[1].UreXC200:=Real_0;
5429:CrpalkeGrfs[2].DeltaSetPoint:=Real_0;
5431:CrpalkeGrfs[2].EnergijaPoraba:=Real_0;
5433:CrpalkeGrfs[2].FrekPretvornikDCNapetost:=Real_0;
5435:CrpalkeGrfs[2].FrekPretvornikDCTok:=Real_0;
5437:CrpalkeGrfs[2].FreqMax:=Real_0;
5439:CrpalkeGrfs[2].FreqMin:=Real_0;
5441:CrpalkeGrfs[2].FreqUpper:=Real_0;
5443:CrpalkeGrfs[2].MocMax:=Real_0;
5445:CrpalkeGrfs[2].MocTrenutna:=Real_0;
5447:CrpalkeGrfs[2].MotorHitrost:=Real_0;
5449:CrpalkeGrfs[2].MotorTok:=Real_0;
5451:CrpalkeGrfs[2].NapajanjeTok:=Real_0;
5453:CrpalkeGrfs[2].NastavitevLokalna:=Real_0;
5455:CrpalkeGrfs[2].NastavitevTrenutna:=Real_0;
5457:CrpalkeGrfs[2].PretokMax:=Real_0;
5459:CrpalkeGrfs[2].PretokMin:=Real_0;
5461:CrpalkeGrfs[2].PretokTrenutni:=Real_0;
5463:CrpalkeGrfs[2].PritiskMax:=Real_0;
5465:CrpalkeGrfs[2].PritiskTrenutni:=Real_0;
5467:CrpalkeGrfs[2].ReferencaMotorjaHzV:=Real_0;
5469:CrpalkeGrfs[2].ReferencaRemote:=Real_0;
5471:CrpalkeGrfs[2].StevecUr2h:=Real_0;
5473:CrpalkeGrfs[2].SystemFeedback:=Real_0;
5475:CrpalkeGrfs[2].SystemReference:=Real_0;
5477:CrpalkeGrfs[2].TemperaturaMotorja:=Real_0;
5479:CrpalkeGrfs[2].UreXC200:=Real_0;
5481:CrpalkeGrfs[3].DeltaSetPoint:=Real_0;
5483:CrpalkeGrfs[3].EnergijaPoraba:=Real_0;
5485:CrpalkeGrfs[3].FrekPretvornikDCNapetost:=Real_0;
5487:CrpalkeGrfs[3].FrekPretvornikDCTok:=Real_0;
5489:CrpalkeGrfs[3].FreqMax:=Real_0;
5491:CrpalkeGrfs[3].FreqMin:=Real_0;
5493:CrpalkeGrfs[3].FreqUpper:=Real_0;
5495:CrpalkeGrfs[3].MocMax:=Real_0;
5497:CrpalkeGrfs[3].MocTrenutna:=Real_0;
5499:CrpalkeGrfs[3].MotorHitrost:=Real_0;
5501:CrpalkeGrfs[3].MotorTok:=Real_0;
5503:CrpalkeGrfs[3].NapajanjeTok:=Real_0;
5505:CrpalkeGrfs[3].NastavitevLokalna:=Real_0;
5507:CrpalkeGrfs[3].NastavitevTrenutna:=Real_0;
5509:CrpalkeGrfs[3].PretokMax:=Real_0;
5511:CrpalkeGrfs[3].PretokMin:=Real_0;
5513:CrpalkeGrfs[3].PretokTrenutni:=Real_0;
5515:CrpalkeGrfs[3].PritiskMax:=Real_0;
5517:CrpalkeGrfs[3].PritiskTrenutni:=Real_0;
5519:CrpalkeGrfs[3].ReferencaMotorjaHzV:=Real_0;
5521:CrpalkeGrfs[3].ReferencaRemote:=Real_0;
5523:CrpalkeGrfs[3].StevecUr2h:=Real_0;
5525:CrpalkeGrfs[3].SystemFeedback:=Real_0;
5527:CrpalkeGrfs[3].SystemReference:=Real_0;
5529:CrpalkeGrfs[3].TemperaturaMotorja:=Real_0;
5531:CrpalkeGrfs[3].UreXC200:=Real_0;
5533:CrpalkeGrfs[4].DeltaSetPoint:=Real_0;
5535:CrpalkeGrfs[4].EnergijaPoraba:=Real_0;
5537:CrpalkeGrfs[4].FrekPretvornikDCNapetost:=Real_0;
5539:CrpalkeGrfs[4].FrekPretvornikDCTok:=Real_0;
5541:CrpalkeGrfs[4].FreqMax:=Real_0;
5543:CrpalkeGrfs[4].FreqMin:=Real_0;
5545:CrpalkeGrfs[4].FreqUpper:=Real_0;
5547:CrpalkeGrfs[4].MocMax:=Real_0;
5549:CrpalkeGrfs[4].MocTrenutna:=Real_0;
5551:CrpalkeGrfs[4].MotorHitrost:=Real_0;
5553:CrpalkeGrfs[4].MotorTok:=Real_0;
5555:CrpalkeGrfs[4].NapajanjeTok:=Real_0;
5557:CrpalkeGrfs[4].NastavitevLokalna:=Real_0;
5559:CrpalkeGrfs[4].NastavitevTrenutna:=Real_0;
5561:CrpalkeGrfs[4].PretokMax:=Real_0;
5563:CrpalkeGrfs[4].PretokMin:=Real_0;
5565:CrpalkeGrfs[4].PretokTrenutni:=Real_0;
5567:CrpalkeGrfs[4].PritiskMax:=Real_0;
5569:CrpalkeGrfs[4].PritiskTrenutni:=Real_0;
5571:CrpalkeGrfs[4].ReferencaMotorjaHzV:=Real_0;
5573:CrpalkeGrfs[4].ReferencaRemote:=Real_0;
5575:CrpalkeGrfs[4].StevecUr2h:=Real_0;
5577:CrpalkeGrfs[4].SystemFeedback:=Real_0;
5579:CrpalkeGrfs[4].SystemReference:=Real_0;
5581:CrpalkeGrfs[4].TemperaturaMotorja:=Real_0;
5583:CrpalkeGrfs[4].UreXC200:=Real_0;
5585:CrpalkeGrfs[5].DeltaSetPoint:=Real_0;
5587:CrpalkeGrfs[5].EnergijaPoraba:=Real_0;
5589:CrpalkeGrfs[5].FrekPretvornikDCNapetost:=Real_0;
5591:CrpalkeGrfs[5].FrekPretvornikDCTok:=Real_0;
5593:CrpalkeGrfs[5].FreqMax:=Real_0;
5595:CrpalkeGrfs[5].FreqMin:=Real_0;
5597:CrpalkeGrfs[5].FreqUpper:=Real_0;
5599:CrpalkeGrfs[5].MocMax:=Real_0;
5601:CrpalkeGrfs[5].MocTrenutna:=Real_0;
5603:CrpalkeGrfs[5].MotorHitrost:=Real_0;
5605:CrpalkeGrfs[5].MotorTok:=Real_0;
5607:CrpalkeGrfs[5].NapajanjeTok:=Real_0;
5609:CrpalkeGrfs[5].NastavitevLokalna:=Real_0;
5611:CrpalkeGrfs[5].NastavitevTrenutna:=Real_0;
5613:CrpalkeGrfs[5].PretokMax:=Real_0;
5615:CrpalkeGrfs[5].PretokMin:=Real_0;
5617:CrpalkeGrfs[5].PretokTrenutni:=Real_0;
5619:CrpalkeGrfs[5].PritiskMax:=Real_0;
5621:CrpalkeGrfs[5].PritiskTrenutni:=Real_0;
5623:CrpalkeGrfs[5].ReferencaMotorjaHzV:=Real_0;
5625:CrpalkeGrfs[5].ReferencaRemote:=Real_0;
5627:CrpalkeGrfs[5].StevecUr2h:=Real_0;
5629:CrpalkeGrfs[5].SystemFeedback:=Real_0;
5631:CrpalkeGrfs[5].SystemReference:=Real_0;
5633:CrpalkeGrfs[5].TemperaturaMotorja:=Real_0;
5635:CrpalkeGrfs[5].UreXC200:=Real_0;
5637:CrpalkeGrfs[6].DeltaSetPoint:=Real_0;
5639:CrpalkeGrfs[6].EnergijaPoraba:=Real_0;
5641:CrpalkeGrfs[6].FrekPretvornikDCNapetost:=Real_0;
5643:CrpalkeGrfs[6].FrekPretvornikDCTok:=Real_0;
5645:CrpalkeGrfs[6].FreqMax:=Real_0;
5647:CrpalkeGrfs[6].FreqMin:=Real_0;
5649:CrpalkeGrfs[6].FreqUpper:=Real_0;
5651:CrpalkeGrfs[6].MocMax:=Real_0;
5653:CrpalkeGrfs[6].MocTrenutna:=Real_0;
5655:CrpalkeGrfs[6].MotorHitrost:=Real_0;
5657:CrpalkeGrfs[6].MotorTok:=Real_0;
5659:CrpalkeGrfs[6].NapajanjeTok:=Real_0;
5661:CrpalkeGrfs[6].NastavitevLokalna:=Real_0;
5663:CrpalkeGrfs[6].NastavitevTrenutna:=Real_0;
5665:CrpalkeGrfs[6].PretokMax:=Real_0;
5667:CrpalkeGrfs[6].PretokMin:=Real_0;
5669:CrpalkeGrfs[6].PretokTrenutni:=Real_0;
5671:CrpalkeGrfs[6].PritiskMax:=Real_0;
5673:CrpalkeGrfs[6].PritiskTrenutni:=Real_0;
5675:CrpalkeGrfs[6].ReferencaMotorjaHzV:=Real_0;
5677:CrpalkeGrfs[6].ReferencaRemote:=Real_0;
5679:CrpalkeGrfs[6].StevecUr2h:=Real_0;
5681:CrpalkeGrfs[6].SystemFeedback:=Real_0;
5683:CrpalkeGrfs[6].SystemReference:=Real_0;
5685:CrpalkeGrfs[6].TemperaturaMotorja:=Real_0;
5687:CrpalkeGrfs[6].UreXC200:=Real_0;
5689:CrpalkeGrfs[7].DeltaSetPoint:=Real_0;
5691:CrpalkeGrfs[7].EnergijaPoraba:=Real_0;
5693:CrpalkeGrfs[7].FrekPretvornikDCNapetost:=Real_0;
5695:CrpalkeGrfs[7].FrekPretvornikDCTok:=Real_0;
5697:CrpalkeGrfs[7].FreqMax:=Real_0;
5699:CrpalkeGrfs[7].FreqMin:=Real_0;
5701:CrpalkeGrfs[7].FreqUpper:=Real_0;
5703:CrpalkeGrfs[7].MocMax:=Real_0;
5705:CrpalkeGrfs[7].MocTrenutna:=Real_0;
5707:CrpalkeGrfs[7].MotorHitrost:=Real_0;
5709:CrpalkeGrfs[7].MotorTok:=Real_0;
5711:CrpalkeGrfs[7].NapajanjeTok:=Real_0;
5713:CrpalkeGrfs[7].NastavitevLokalna:=Real_0;
5715:CrpalkeGrfs[7].NastavitevTrenutna:=Real_0;
5717:CrpalkeGrfs[7].PretokMax:=Real_0;
5719:CrpalkeGrfs[7].PretokMin:=Real_0;
5721:CrpalkeGrfs[7].PretokTrenutni:=Real_0;
5723:CrpalkeGrfs[7].PritiskMax:=Real_0;
5725:CrpalkeGrfs[7].PritiskTrenutni:=Real_0;
5727:CrpalkeGrfs[7].ReferencaMotorjaHzV:=Real_0;
5729:CrpalkeGrfs[7].ReferencaRemote:=Real_0;
5731:CrpalkeGrfs[7].StevecUr2h:=Real_0;
5733:CrpalkeGrfs[7].SystemFeedback:=Real_0;
5735:CrpalkeGrfs[7].SystemReference:=Real_0;
5737:CrpalkeGrfs[7].TemperaturaMotorja:=Real_0;
5739:CrpalkeGrfs[7].UreXC200:=Real_0;
5741:CrpalkeGrfs[8].DeltaSetPoint:=Real_0;
5743:CrpalkeGrfs[8].EnergijaPoraba:=Real_0;
5745:CrpalkeGrfs[8].FrekPretvornikDCNapetost:=Real_0;
5747:CrpalkeGrfs[8].FrekPretvornikDCTok:=Real_0;
5749:CrpalkeGrfs[8].FreqMax:=Real_0;
5751:CrpalkeGrfs[8].FreqMin:=Real_0;
5753:CrpalkeGrfs[8].FreqUpper:=Real_0;
5755:CrpalkeGrfs[8].MocMax:=Real_0;
5757:CrpalkeGrfs[8].MocTrenutna:=Real_0;
5759:CrpalkeGrfs[8].MotorHitrost:=Real_0;
5761:CrpalkeGrfs[8].MotorTok:=Real_0;
5763:CrpalkeGrfs[8].NapajanjeTok:=Real_0;
5765:CrpalkeGrfs[8].NastavitevLokalna:=Real_0;
5767:CrpalkeGrfs[8].NastavitevTrenutna:=Real_0;
5769:CrpalkeGrfs[8].PretokMax:=Real_0;
5771:CrpalkeGrfs[8].PretokMin:=Real_0;
5773:CrpalkeGrfs[8].PretokTrenutni:=Real_0;
5775:CrpalkeGrfs[8].PritiskMax:=Real_0;
5777:CrpalkeGrfs[8].PritiskTrenutni:=Real_0;
5779:CrpalkeGrfs[8].ReferencaMotorjaHzV:=Real_0;
5781:CrpalkeGrfs[8].ReferencaRemote:=Real_0;
5783:CrpalkeGrfs[8].StevecUr2h:=Real_0;
5785:CrpalkeGrfs[8].SystemFeedback:=Real_0;
5787:CrpalkeGrfs[8].SystemReference:=Real_0;
5789:CrpalkeGrfs[8].TemperaturaMotorja:=Real_0;
5791:CrpalkeGrfs[8].UreXC200:=Real_0;
5793:CrpalkeGrfs[9].DeltaSetPoint:=Real_0;
5795:CrpalkeGrfs[9].EnergijaPoraba:=Real_0;
5797:CrpalkeGrfs[9].FrekPretvornikDCNapetost:=Real_0;
5799:CrpalkeGrfs[9].FrekPretvornikDCTok:=Real_0;
5801:CrpalkeGrfs[9].FreqMax:=Real_0;
5803:CrpalkeGrfs[9].FreqMin:=Real_0;
5805:CrpalkeGrfs[9].FreqUpper:=Real_0;
5807:CrpalkeGrfs[9].MocMax:=Real_0;
5809:CrpalkeGrfs[9].MocTrenutna:=Real_0;
5811:CrpalkeGrfs[9].MotorHitrost:=Real_0;
5813:CrpalkeGrfs[9].MotorTok:=Real_0;
5815:CrpalkeGrfs[9].NapajanjeTok:=Real_0;
5817:CrpalkeGrfs[9].NastavitevLokalna:=Real_0;
5819:CrpalkeGrfs[9].NastavitevTrenutna:=Real_0;
5821:CrpalkeGrfs[9].PretokMax:=Real_0;
5823:CrpalkeGrfs[9].PretokMin:=Real_0;
5825:CrpalkeGrfs[9].PretokTrenutni:=Real_0;
5827:CrpalkeGrfs[9].PritiskMax:=Real_0;
5829:CrpalkeGrfs[9].PritiskTrenutni:=Real_0;
5831:CrpalkeGrfs[9].ReferencaMotorjaHzV:=Real_0;
5833:CrpalkeGrfs[9].ReferencaRemote:=Real_0;
5835:CrpalkeGrfs[9].StevecUr2h:=Real_0;
5837:CrpalkeGrfs[9].SystemFeedback:=Real_0;
5839:CrpalkeGrfs[9].SystemReference:=Real_0;
5841:CrpalkeGrfs[9].TemperaturaMotorja:=Real_0;
5843:CrpalkeGrfs[9].UreXC200:=Real_0;
5845:CrpGrundfosTlakSP[1]:=Real_0;
5847:CrpGrundfosTlakSP[2]:=Real_0;
5849:CrpGrundfosTlakSP[3]:=Real_0;
5851:CrpGrundfosTlakSP[4]:=Real_0;
5853:CrpGrundfosTlakSP[5]:=Real_0;
5855:CrpGrundfosTlakSP[6]:=Real_0;
5857:CrpGrundfosTlakSP[7]:=Real_0;
5859:Exp1TlakMin:=Real_0;
5861:Exp2TlakMin:=Real_0;
5863:HladStroj.ObratovalneUre:=Real_0;
5865:HladStroj.PritiskSonda1:=Real_0;
5867:HladStroj.PritiskSonda2:=Real_0;
5869:HladStroj.PritiskSonda3:=Real_0;
5871:HladStroj.PritiskSonda4:=Real_0;
5873:HladStroj.TempH2OvhodIzparilnika:=Real_0;
5875:HladStroj.TempIzhodnaSonda1:=Real_0;
5877:HladStroj.TempIzhodnaSonda3:=Real_0;
5879:HladStroj.TempSetPoint:=Real_0;
5881:Klima[1].HitrostVentilatorjev:=Real_0;
5883:Klima[1].NastTempProstora:=Real_0;
5885:Klima[1].ObratovalneUre:=Real_0;
5887:Klima[1].ProtizmrzZasc:=Real_0;
5889:Klima[1].RezimDelovanja:=Real_0;
5891:Klima[1].TemperaturaDovoda:=Real_0;
5893:Klima[1].TemperaturaProstora:=Real_0;
5895:Klima[1].TempPredRekN2:=Real_0;
5897:Klima[1].TempZaRekN2:=Real_0;
5899:Klima[1].TlakDovKanal:=Real_0;
5901:Klima[1].TlakOdvodKanal:=Real_0;
5903:Klima[1].VlagaDovoda:=Real_0;
5905:Klima[1].VlagaVprostor:=Real_0;
5907:Klima[1].ZunanjaTemp:=Real_0;
5909:Klima[2].HitrostVentilatorjev:=Real_0;
5911:Klima[2].NastTempProstora:=Real_0;
5913:Klima[2].ObratovalneUre:=Real_0;
5915:Klima[2].ProtizmrzZasc:=Real_0;
5917:Klima[2].RezimDelovanja:=Real_0;
5919:Klima[2].TemperaturaDovoda:=Real_0;
5921:Klima[2].TemperaturaProstora:=Real_0;
5923:Klima[2].TempPredRekN2:=Real_0;
5925:Klima[2].TempZaRekN2:=Real_0;
5927:Klima[2].TlakDovKanal:=Real_0;
5929:Klima[2].TlakOdvodKanal:=Real_0;
5931:Klima[2].VlagaDovoda:=Real_0;
5933:Klima[2].VlagaVprostor:=Real_0;
5935:Klima[2].ZunanjaTemp:=Real_0;
5937:rVersion:=Real_0;
5939:SenzorTempTIA[1]:=Real_0;
5941:SenzorTempTIA[2]:=Real_0;
5943:SenzorTempTIA[3]:=Real_0;
5945:SenzorTempTIA[4]:=Real_0;
5947:SenzorVlagaHIA[1]:=Real_0;
5949:SenzorVlagaHIA[2]:=Real_0;
5951:SenzorVlagaHIA[3]:=Real_0;
5953:SenzorVlagaHIA[4]:=Real_0;
5955:TEgrelecTempMAX:=Real_0;
5957:TEgrelecTempMIN:=Real_0;
5959:TempAlarmPoint:=Real_0;
5961:TempTIApovprecna:=Real_0;
5963:ToplPost.HKdotokNastTemp:=Real_0;
5965:ToplPost.HKdotokTemp:=Real_0;
5967:ToplPost.HKpovtatekTemp:=Real_0;
5969:ToplPost.HKpovtratekNastTemp:=Real_0;
5971:ToplPost.HKzunanjaTemp:=Real_0;
5973:ToplPost.TVdotokNastTemp:=Real_0;
5975:ToplPost.TVdotokTemp:=Real_0;
5977:ToplPost.TVpovratekTemp:=Real_0;
5979:ToplPost.TVrezervoarTemp:=Real_0;
5981:TYventilMax[1]:=Real_0;
5983:TYventilMax[2]:=Real_0;
5985:TYventilMax[3]:=Real_0;
5987:TYventilMax[4]:=Real_0;
5989:TYventilMin[1]:=Real_0;
5991:TYventilMin[2]:=Real_0;
5993:TYventilMin[3]:=Real_0;
5995:TYventilMin[4]:=Real_0;
5997:TYventilTempRazlika[1]:=Real_0;
5999:TYventilTempRazlika[2]:=Real_0;
6001:TYventilTempRazlika[3]:=Real_0;
6003:TYventilTempRazlika[4]:=Real_0;
6005:ValAI_Temp1B1:=Real_0;
6007:ValAI_Temp1B2:=Real_0;
6009:ValAI_Temp1B3:=Real_0;
6011:ValAI_Temp2B2:=Real_0;
6013:ValAI_Temp2B3:=Real_0;
6015:ValAI_TempHB2:=Real_0;
6017:ValAI_TempHB4:=Real_0;
6019:ValAI_TempHB9:=Real_0;
6021:ValAI_TempTB1:=Real_0;
6023:ValAI_TempTB10:=Real_0;
6025:ValAI_TempTB2:=Real_0;
6027:ValAI_TempTB3:=Real_0;
6029:ValAI_TempTB4:=Real_0;
6031:ValAI_TempTB8:=Real_0;
6033:ValAI_TlakExp1S1:=Real_0;
6035:ValAI_TlakExp1S2:=Real_0;
6037:ValAI_TlakExp2S1:=Real_0;
6039:ValAI_TlakExp2S2:=Real_0;
6041:ValAI_TlakHB15:=Real_0;
6043:ValAI_TlakHB16:=Real_0;
6045:ValAI_TlakHB17:=Real_0;
6047:ValAI_TlakHB3:=Real_0;
6049:ValAI_TlakTB11:=Real_0;
6051:ValAI_TlakTB12:=Real_0;
6053:ValAI_TlakTB13:=Real_0;
6055:ValAI_TlakTB14:=Real_0;
6057:ValAI_Vlaga1B4:=Real_0;
6059:ValAI_Vlaga2B4:=Real_0;
6061:ValAO_RegVentTY[1]:=Real_0;
6063:ValAO_RegVentTY[2]:=Real_0;
6065:ValAO_RegVentTY[3]:=Real_0;
6067:ValAO_RegVentTY[4]:=Real_0;
6069:VlagaHIApovprecna:=Real_0;
6071:Circutor.CosFi_III:=Real_0;
6073:Circutor.DelovnaEnergija:=Real_0;
6075:Circutor.DelovnaMoc_III:=Real_0;
6077:Circutor.DelovnaMoc_L1:=Real_0;
6079:Circutor.DelovnaMoc_L2:=Real_0;
6081:Circutor.DelovnaMoc_L3:=Real_0;
6083:Circutor.Frekvenca_L1:=Real_0;
6085:Circutor.InduktivnaEnergija:=Real_0;
6087:Circutor.InduktivnaMoc_III:=Real_0;
6089:Circutor.JalovaMoc_L1:=Real_0;
6091:Circutor.JalovaMoc_L2:=Real_0;
6093:Circutor.JalovaMoc_L3:=Real_0;
6095:Circutor.KapacitivnaEnergija:=Real_0;
6097:Circutor.KapacitivnaMoc_III:=Real_0;
6099:Circutor.MaximumDemand:=Real_0;
6101:Circutor.Napetost_L1_L2:=Real_0;
6103:Circutor.Napetost_L1_N:=Real_0;
6105:Circutor.Napetost_L2_L3:=Real_0;
6107:Circutor.Napetost_L2_N:=Real_0;
6109:Circutor.Napetost_L3_L1:=Real_0;
6111:Circutor.Napetost_L3_N:=Real_0;
6113:Circutor.NavideznaMoc_III:=Real_0;
6115:Circutor.NicelniTok:=Real_0;
6117:Circutor.PowerFactor_III:=Real_0;
6119:Circutor.PowerFactor_L1:=Real_0;
6121:Circutor.PowerFactor_L2:=Real_0;
6123:Circutor.PowerFactor_L3:=Real_0;
6125:Circutor.THDI_L1:=Real_0;
6127:Circutor.THDI_L2:=Real_0;
6129:Circutor.THDI_L3:=Real_0;
6131:Circutor.THDV_L1:=Real_0;
6133:Circutor.THDV_L2:=Real_0;
6135:Circutor.THDV_L3:=Real_0;
6137:Circutor.Tok_L1:=Real_0;
6139:Circutor.Tok_L2:=Real_0;
6141:Circutor.Tok_L3:=Real_0;
6143:Circutor.TokPovprecje_III:=Real_0;
6145:CrpalkeGrfsGal.EnergijaPoraba:=Real_0;
6147:CrpalkeGrfsGal.FrekPretvornikDCNapetost:=Real_0;
6149:CrpalkeGrfsGal.FrekPretvornikDCTok:=Real_0;
6151:CrpalkeGrfsGal.FreqMax:=Real_0;
6153:CrpalkeGrfsGal.FreqMin:=Real_0;
6155:CrpalkeGrfsGal.FreqUpper:=Real_0;
6157:CrpalkeGrfsGal.MocMax:=Real_0;
6159:CrpalkeGrfsGal.MocTrenutna:=Real_0;
6161:CrpalkeGrfsGal.MotorHitrost:=Real_0;
6163:CrpalkeGrfsGal.MotorTok:=Real_0;
6165:CrpalkeGrfsGal.NapajanjeTok:=Real_0;
6167:CrpalkeGrfsGal.NastavitevLokalna:=Real_0;
6169:CrpalkeGrfsGal.NastavitevTrenutna:=Real_0;
6171:CrpalkeGrfsGal.PretokMax:=Real_0;
6173:CrpalkeGrfsGal.PretokMin:=Real_0;
6175:CrpalkeGrfsGal.PretokTrenutni:=Real_0;
6177:CrpalkeGrfsGal.PritiskMax:=Real_0;
6179:CrpalkeGrfsGal.PritiskTrenutni:=Real_0;
6181:CrpalkeGrfsGal.ReferencaMotorjaHzV:=Real_0;
6183:CrpalkeGrfsGal.ReferencaRemote:=Real_0;
6185:CrpalkeGrfsGal.StevecUr2h:=Real_0;
6187:CrpalkeGrfsGal.SystemFeedback:=Real_0;
6189:CrpalkeGrfsGal.SystemReference:=Real_0;
6191:CrpalkeGrfsGal.TemperaturaMotorja:=Real_0;
6193:CrpalkeGrfsGal.UreXC200:=Real_0;
6195:CrpGrfsPIDregKP:=Real_0;
6197:ValAI_TempTB5:=Real_0;
6199:XVH_CrpGrundfosTlakSP:=Real_0;
6201:XVH_GrafTemp[1]:=Real_0;
6203:XVH_GrafTemp[2]:=Real_0;
6205:XVH_GrafTemp[3]:=Real_0;
6207:XVH_GrafTemp[4]:=Real_0;
6209:XVH_GrafTemp[5]:=Real_0;
6211:XVH_GrafVlaga[1]:=Real_0;
6213:XVH_GrafVlaga[2]:=Real_0;
6215:XVH_GrafVlaga[3]:=Real_0;
6217:XVH_GrafVlaga[4]:=Real_0;
6219:XVH_GrafVlaga[5]:=Real_0;
6221:XVH_TlakSenzor:=Real_0;
6223:Circ[1].MaximumDemandA2:=Real_0;
6225:Circ[1].MaximumDemandA3:=Real_0;
6227:Circ[1].RazEner_D_SCADA:=Real_0;
6229:Circ[1].RazEner_T_SCADA:=Real_0;
6231:Circ[1].RazEner_M_SCADA:=Real_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_String : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje STRING*)
(**)
7000:UserCurrentName:=String_0;
7015:Date_Time[0]:=String_0;
7030:Date_Time[1]:=String_0;
7045:Date_Time[2]:=String_0;
7060:Date_Time[3]:=String_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Word : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje INT*)
(**)
0:CrpalkeDnfs[1].PreklopkaMode:=Word_01;
1:CrpalkeDnfs[1].StarterStatus0do7:=Byte_0;
2:CrpalkeDnfs[1].StatusCrpalke:=Byte_0;
3:CrpalkeDnfs[1].StatusKontaktor:=Word_01;
4:CrpalkeDnfs[2].PreklopkaMode:=Word_01;
5:CrpalkeDnfs[2].StarterStatus0do7:=Byte_0;
6:CrpalkeDnfs[2].StatusCrpalke:=Byte_0;
7:CrpalkeDnfs[2].StatusKontaktor:=Word_01;
8:CrpalkeDnfs[3].PreklopkaMode:=Word_01;
9:CrpalkeDnfs[3].StarterStatus0do7:=Byte_0;
10:CrpalkeDnfs[3].StatusCrpalke:=Byte_0;
11:CrpalkeDnfs[3].StatusKontaktor:=Word_01;
12:CrpalkeDnfs[4].PreklopkaMode:=Word_01;
13:CrpalkeDnfs[4].StarterStatus0do7:=Byte_0;
14:CrpalkeDnfs[4].StatusCrpalke:=Byte_0;
15:CrpalkeDnfs[4].StatusKontaktor:=Word_01;
16:CrpalkeGrfs[10].AlarmActiveCode:=Word_01;
17:CrpalkeGrfs[10].AlarmCodeLog1:=Word_01;
18:CrpalkeGrfs[10].AlarmCodeLog2:=Word_01;
19:CrpalkeGrfs[10].AlarmCodeLog3:=Word_01;
20:CrpalkeGrfs[10].AlarmCodeLog4:=Word_01;
21:CrpalkeGrfs[10].AlarmCodeLog5:=Word_01;
22:CrpalkeGrfs[10].AlarmGroupXVH[0]:=Word_01;
23:CrpalkeGrfs[10].AlarmGroupXVH[10]:=Word_01;
24:CrpalkeGrfs[10].AlarmGroupXVH[11]:=Word_01;
25:CrpalkeGrfs[10].AlarmGroupXVH[12]:=Word_01;
26:CrpalkeGrfs[10].AlarmGroupXVH[13]:=Word_01;
27:CrpalkeGrfs[10].AlarmGroupXVH[14]:=Word_01;
28:CrpalkeGrfs[10].AlarmGroupXVH[15]:=Word_01;
29:CrpalkeGrfs[10].AlarmGroupXVH[16]:=Word_01;
30:CrpalkeGrfs[10].AlarmGroupXVH[1]:=Word_01;
31:CrpalkeGrfs[10].AlarmGroupXVH[2]:=Word_01;
32:CrpalkeGrfs[10].AlarmGroupXVH[3]:=Word_01;
33:CrpalkeGrfs[10].AlarmGroupXVH[4]:=Word_01;
34:CrpalkeGrfs[10].AlarmGroupXVH[5]:=Word_01;
35:CrpalkeGrfs[10].AlarmGroupXVH[6]:=Word_01;
36:CrpalkeGrfs[10].AlarmGroupXVH[7]:=Word_01;
37:CrpalkeGrfs[10].AlarmGroupXVH[8]:=Word_01;
38:CrpalkeGrfs[10].AlarmGroupXVH[9]:=Word_01;
39:CrpalkeGrfs[10].AlarmQSD1:=Word_01;
40:CrpalkeGrfs[10].AlarmQSD2:=Word_01;
41:CrpalkeGrfs[10].AlarmStart1:=Word_01;
42:CrpalkeGrfs[10].AlarmStart2:=Word_01;
43:CrpalkeGrfs[10].AlarmStop1:=Word_01;
44:CrpalkeGrfs[10].AlarmStop2:=Word_01;
45:CrpalkeGrfs[10].AlarmStop3:=Word_01;
46:CrpalkeGrfs[10].AlarmSurv1:=Word_01;
47:CrpalkeGrfs[10].AlarmSurv2:=Word_01;
48:CrpalkeGrfs[10].ControlSource:=Word_01;
49:CrpalkeGrfs[10].ExternInputSetup:=Word_01;
50:CrpalkeGrfs[10].ExternInputsStatus:=Word_01;
51:CrpalkeGrfs[10].LocalSetupMode1:=Word_01;
52:CrpalkeGrfs[10].PreklopkaMode:=Word_01;
53:CrpalkeGrfs[10].Relay1setup:=Word_01;
54:CrpalkeGrfs[10].RemoteSetupMode1:=Word_01;
55:CrpalkeGrfs[10].StatusCrpalke:=Byte_0;
56:CrpalkeGrfs[10].StatusMode1:=Word_01;
57:CrpalkeGrfs[10].StatusMode1co:=Byte_0;
58:CrpalkeGrfs[10].StatusMode1op:=Byte_0;
59:CrpalkeGrfs[10].StatusMode2:=Word_01;
60:CrpalkeGrfs[10].StatusMode3:=Word_01;
61:CrpalkeGrfs[11].AlarmActiveCode:=Word_01;
62:CrpalkeGrfs[11].AlarmCodeLog1:=Word_01;
63:CrpalkeGrfs[11].AlarmCodeLog2:=Word_01;
64:CrpalkeGrfs[11].AlarmCodeLog3:=Word_01;
65:CrpalkeGrfs[11].AlarmCodeLog4:=Word_01;
66:CrpalkeGrfs[11].AlarmCodeLog5:=Word_01;
67:CrpalkeGrfs[11].AlarmGroupXVH[0]:=Word_01;
68:CrpalkeGrfs[11].AlarmGroupXVH[10]:=Word_01;
69:CrpalkeGrfs[11].AlarmGroupXVH[11]:=Word_01;
70:CrpalkeGrfs[11].AlarmGroupXVH[12]:=Word_01;
71:CrpalkeGrfs[11].AlarmGroupXVH[13]:=Word_01;
72:CrpalkeGrfs[11].AlarmGroupXVH[14]:=Word_01;
73:CrpalkeGrfs[11].AlarmGroupXVH[15]:=Word_01;
74:CrpalkeGrfs[11].AlarmGroupXVH[16]:=Word_01;
75:CrpalkeGrfs[11].AlarmGroupXVH[1]:=Word_01;
76:CrpalkeGrfs[11].AlarmGroupXVH[2]:=Word_01;
77:CrpalkeGrfs[11].AlarmGroupXVH[3]:=Word_01;
78:CrpalkeGrfs[11].AlarmGroupXVH[4]:=Word_01;
79:CrpalkeGrfs[11].AlarmGroupXVH[5]:=Word_01;
80:CrpalkeGrfs[11].AlarmGroupXVH[6]:=Word_01;
81:CrpalkeGrfs[11].AlarmGroupXVH[7]:=Word_01;
82:CrpalkeGrfs[11].AlarmGroupXVH[8]:=Word_01;
83:CrpalkeGrfs[11].AlarmGroupXVH[9]:=Word_01;
84:CrpalkeGrfs[11].AlarmQSD1:=Word_01;
85:CrpalkeGrfs[11].AlarmQSD2:=Word_01;
86:CrpalkeGrfs[11].AlarmStart1:=Word_01;
87:CrpalkeGrfs[11].AlarmStart2:=Word_01;
88:CrpalkeGrfs[11].AlarmStop1:=Word_01;
89:CrpalkeGrfs[11].AlarmStop2:=Word_01;
90:CrpalkeGrfs[11].AlarmStop3:=Word_01;
91:CrpalkeGrfs[11].AlarmSurv1:=Word_01;
92:CrpalkeGrfs[11].AlarmSurv2:=Word_01;
93:CrpalkeGrfs[11].ControlSource:=Word_01;
94:CrpalkeGrfs[11].ExternInputSetup:=Word_01;
95:CrpalkeGrfs[11].ExternInputsStatus:=Word_01;
96:CrpalkeGrfs[11].LocalSetupMode1:=Word_01;
97:CrpalkeGrfs[11].PreklopkaMode:=Word_01;
98:CrpalkeGrfs[11].Relay1setup:=Word_01;
99:CrpalkeGrfs[11].RemoteSetupMode1:=Word_01;
100:CrpalkeGrfs[11].StatusCrpalke:=Byte_0;
101:CrpalkeGrfs[11].StatusMode1:=Word_01;
102:CrpalkeGrfs[11].StatusMode1co:=Byte_0;
103:CrpalkeGrfs[11].StatusMode1op:=Byte_0;
104:CrpalkeGrfs[11].StatusMode2:=Word_01;
105:CrpalkeGrfs[11].StatusMode3:=Word_01;
106:CrpalkeGrfs[12].AlarmActiveCode:=Word_01;
107:CrpalkeGrfs[12].AlarmCodeLog1:=Word_01;
108:CrpalkeGrfs[12].AlarmCodeLog2:=Word_01;
109:CrpalkeGrfs[12].AlarmCodeLog3:=Word_01;
110:CrpalkeGrfs[12].AlarmCodeLog4:=Word_01;
111:CrpalkeGrfs[12].AlarmCodeLog5:=Word_01;
112:CrpalkeGrfs[12].AlarmGroupXVH[0]:=Word_01;
113:CrpalkeGrfs[12].AlarmGroupXVH[10]:=Word_01;
114:CrpalkeGrfs[12].AlarmGroupXVH[11]:=Word_01;
115:CrpalkeGrfs[12].AlarmGroupXVH[12]:=Word_01;
116:CrpalkeGrfs[12].AlarmGroupXVH[13]:=Word_01;
117:CrpalkeGrfs[12].AlarmGroupXVH[14]:=Word_01;
118:CrpalkeGrfs[12].AlarmGroupXVH[15]:=Word_01;
119:CrpalkeGrfs[12].AlarmGroupXVH[16]:=Word_01;
120:CrpalkeGrfs[12].AlarmGroupXVH[1]:=Word_01;
121:CrpalkeGrfs[12].AlarmGroupXVH[2]:=Word_01;
122:CrpalkeGrfs[12].AlarmGroupXVH[3]:=Word_01;
123:CrpalkeGrfs[12].AlarmGroupXVH[4]:=Word_01;
124:CrpalkeGrfs[12].AlarmGroupXVH[5]:=Word_01;
125:CrpalkeGrfs[12].AlarmGroupXVH[6]:=Word_01;
126:CrpalkeGrfs[12].AlarmGroupXVH[7]:=Word_01;
127:CrpalkeGrfs[12].AlarmGroupXVH[8]:=Word_01;
128:CrpalkeGrfs[12].AlarmGroupXVH[9]:=Word_01;
129:CrpalkeGrfs[12].AlarmQSD1:=Word_01;
130:CrpalkeGrfs[12].AlarmQSD2:=Word_01;
131:CrpalkeGrfs[12].AlarmStart1:=Word_01;
132:CrpalkeGrfs[12].AlarmStart2:=Word_01;
133:CrpalkeGrfs[12].AlarmStop1:=Word_01;
134:CrpalkeGrfs[12].AlarmStop2:=Word_01;
135:CrpalkeGrfs[12].AlarmStop3:=Word_01;
136:CrpalkeGrfs[12].AlarmSurv1:=Word_01;
137:CrpalkeGrfs[12].AlarmSurv2:=Word_01;
138:CrpalkeGrfs[12].ControlSource:=Word_01;
139:CrpalkeGrfs[12].ExternInputSetup:=Word_01;
140:CrpalkeGrfs[12].ExternInputsStatus:=Word_01;
141:CrpalkeGrfs[12].LocalSetupMode1:=Word_01;
142:CrpalkeGrfs[12].PreklopkaMode:=Word_01;
143:CrpalkeGrfs[12].Relay1setup:=Word_01;
144:CrpalkeGrfs[12].RemoteSetupMode1:=Word_01;
145:CrpalkeGrfs[12].StatusCrpalke:=Byte_0;
146:CrpalkeGrfs[12].StatusMode1:=Word_01;
147:CrpalkeGrfs[12].StatusMode1co:=Byte_0;
148:CrpalkeGrfs[12].StatusMode1op:=Byte_0;
149:CrpalkeGrfs[12].StatusMode2:=Word_01;
150:CrpalkeGrfs[12].StatusMode3:=Word_01;
151:CrpalkeGrfs[13].AlarmActiveCode:=Word_01;
152:CrpalkeGrfs[13].AlarmCodeLog1:=Word_01;
153:CrpalkeGrfs[13].AlarmCodeLog2:=Word_01;
154:CrpalkeGrfs[13].AlarmCodeLog3:=Word_01;
155:CrpalkeGrfs[13].AlarmCodeLog4:=Word_01;
156:CrpalkeGrfs[13].AlarmCodeLog5:=Word_01;
157:CrpalkeGrfs[13].AlarmGroupXVH[0]:=Word_01;
158:CrpalkeGrfs[13].AlarmGroupXVH[10]:=Word_01;
159:CrpalkeGrfs[13].AlarmGroupXVH[11]:=Word_01;
160:CrpalkeGrfs[13].AlarmGroupXVH[12]:=Word_01;
161:CrpalkeGrfs[13].AlarmGroupXVH[13]:=Word_01;
162:CrpalkeGrfs[13].AlarmGroupXVH[14]:=Word_01;
163:CrpalkeGrfs[13].AlarmGroupXVH[15]:=Word_01;
164:CrpalkeGrfs[13].AlarmGroupXVH[16]:=Word_01;
165:CrpalkeGrfs[13].AlarmGroupXVH[1]:=Word_01;
166:CrpalkeGrfs[13].AlarmGroupXVH[2]:=Word_01;
167:CrpalkeGrfs[13].AlarmGroupXVH[3]:=Word_01;
168:CrpalkeGrfs[13].AlarmGroupXVH[4]:=Word_01;
169:CrpalkeGrfs[13].AlarmGroupXVH[5]:=Word_01;
170:CrpalkeGrfs[13].AlarmGroupXVH[6]:=Word_01;
171:CrpalkeGrfs[13].AlarmGroupXVH[7]:=Word_01;
172:CrpalkeGrfs[13].AlarmGroupXVH[8]:=Word_01;
173:CrpalkeGrfs[13].AlarmGroupXVH[9]:=Word_01;
174:CrpalkeGrfs[13].AlarmQSD1:=Word_01;
175:CrpalkeGrfs[13].AlarmQSD2:=Word_01;
176:CrpalkeGrfs[13].AlarmStart1:=Word_01;
177:CrpalkeGrfs[13].AlarmStart2:=Word_01;
178:CrpalkeGrfs[13].AlarmStop1:=Word_01;
179:CrpalkeGrfs[13].AlarmStop2:=Word_01;
180:CrpalkeGrfs[13].AlarmStop3:=Word_01;
181:CrpalkeGrfs[13].AlarmSurv1:=Word_01;
182:CrpalkeGrfs[13].AlarmSurv2:=Word_01;
183:CrpalkeGrfs[13].ControlSource:=Word_01;
184:CrpalkeGrfs[13].ExternInputSetup:=Word_01;
185:CrpalkeGrfs[13].ExternInputsStatus:=Word_01;
186:CrpalkeGrfs[13].LocalSetupMode1:=Word_01;
187:CrpalkeGrfs[13].PreklopkaMode:=Word_01;
188:CrpalkeGrfs[13].Relay1setup:=Word_01;
189:CrpalkeGrfs[13].RemoteSetupMode1:=Word_01;
190:CrpalkeGrfs[13].StatusCrpalke:=Byte_0;
191:CrpalkeGrfs[13].StatusMode1:=Word_01;
192:CrpalkeGrfs[13].StatusMode1co:=Byte_0;
193:CrpalkeGrfs[13].StatusMode1op:=Byte_0;
194:CrpalkeGrfs[13].StatusMode2:=Word_01;
195:CrpalkeGrfs[13].StatusMode3:=Word_01;
196:CrpalkeGrfs[14].AlarmActiveCode:=Word_01;
197:CrpalkeGrfs[14].AlarmCodeLog1:=Word_01;
198:CrpalkeGrfs[14].AlarmCodeLog2:=Word_01;
199:CrpalkeGrfs[14].AlarmCodeLog3:=Word_01;
200:CrpalkeGrfs[14].AlarmCodeLog4:=Word_01;
201:CrpalkeGrfs[14].AlarmCodeLog5:=Word_01;
202:CrpalkeGrfs[14].AlarmGroupXVH[0]:=Word_01;
203:CrpalkeGrfs[14].AlarmGroupXVH[10]:=Word_01;
204:CrpalkeGrfs[14].AlarmGroupXVH[11]:=Word_01;
205:CrpalkeGrfs[14].AlarmGroupXVH[12]:=Word_01;
206:CrpalkeGrfs[14].AlarmGroupXVH[13]:=Word_01;
207:CrpalkeGrfs[14].AlarmGroupXVH[14]:=Word_01;
208:CrpalkeGrfs[14].AlarmGroupXVH[15]:=Word_01;
209:CrpalkeGrfs[14].AlarmGroupXVH[16]:=Word_01;
210:CrpalkeGrfs[14].AlarmGroupXVH[1]:=Word_01;
211:CrpalkeGrfs[14].AlarmGroupXVH[2]:=Word_01;
212:CrpalkeGrfs[14].AlarmGroupXVH[3]:=Word_01;
213:CrpalkeGrfs[14].AlarmGroupXVH[4]:=Word_01;
214:CrpalkeGrfs[14].AlarmGroupXVH[5]:=Word_01;
215:CrpalkeGrfs[14].AlarmGroupXVH[6]:=Word_01;
216:CrpalkeGrfs[14].AlarmGroupXVH[7]:=Word_01;
217:CrpalkeGrfs[14].AlarmGroupXVH[8]:=Word_01;
218:CrpalkeGrfs[14].AlarmGroupXVH[9]:=Word_01;
219:CrpalkeGrfs[14].AlarmQSD1:=Word_01;
220:CrpalkeGrfs[14].AlarmQSD2:=Word_01;
221:CrpalkeGrfs[14].AlarmStart1:=Word_01;
222:CrpalkeGrfs[14].AlarmStart2:=Word_01;
223:CrpalkeGrfs[14].AlarmStop1:=Word_01;
224:CrpalkeGrfs[14].AlarmStop2:=Word_01;
225:CrpalkeGrfs[14].AlarmStop3:=Word_01;
226:CrpalkeGrfs[14].AlarmSurv1:=Word_01;
227:CrpalkeGrfs[14].AlarmSurv2:=Word_01;
228:CrpalkeGrfs[14].ControlSource:=Word_01;
229:CrpalkeGrfs[14].ExternInputSetup:=Word_01;
230:CrpalkeGrfs[14].ExternInputsStatus:=Word_01;
231:CrpalkeGrfs[14].LocalSetupMode1:=Word_01;
232:CrpalkeGrfs[14].PreklopkaMode:=Word_01;
233:CrpalkeGrfs[14].Relay1setup:=Word_01;
234:CrpalkeGrfs[14].RemoteSetupMode1:=Word_01;
235:CrpalkeGrfs[14].StatusCrpalke:=Byte_0;
236:CrpalkeGrfs[14].StatusMode1:=Word_01;
237:CrpalkeGrfs[14].StatusMode1co:=Byte_0;
238:CrpalkeGrfs[14].StatusMode1op:=Byte_0;
239:CrpalkeGrfs[14].StatusMode2:=Word_01;
240:CrpalkeGrfs[14].StatusMode3:=Word_01;
241:CrpalkeGrfs[1].AlarmActiveCode:=Word_01;
242:CrpalkeGrfs[1].AlarmCodeLog1:=Word_01;
243:CrpalkeGrfs[1].AlarmCodeLog2:=Word_01;
244:CrpalkeGrfs[1].AlarmCodeLog3:=Word_01;
245:CrpalkeGrfs[1].AlarmCodeLog4:=Word_01;
246:CrpalkeGrfs[1].AlarmCodeLog5:=Word_01;
247:CrpalkeGrfs[1].AlarmGroupXVH[0]:=Word_01;
248:CrpalkeGrfs[1].AlarmGroupXVH[10]:=Word_01;
249:CrpalkeGrfs[1].AlarmGroupXVH[11]:=Word_01;
250:CrpalkeGrfs[1].AlarmGroupXVH[12]:=Word_01;
251:CrpalkeGrfs[1].AlarmGroupXVH[13]:=Word_01;
252:CrpalkeGrfs[1].AlarmGroupXVH[14]:=Word_01;
253:CrpalkeGrfs[1].AlarmGroupXVH[15]:=Word_01;
254:CrpalkeGrfs[1].AlarmGroupXVH[16]:=Word_01;
255:CrpalkeGrfs[1].AlarmGroupXVH[1]:=Word_01;
256:CrpalkeGrfs[1].AlarmGroupXVH[2]:=Word_01;
257:CrpalkeGrfs[1].AlarmGroupXVH[3]:=Word_01;
258:CrpalkeGrfs[1].AlarmGroupXVH[4]:=Word_01;
259:CrpalkeGrfs[1].AlarmGroupXVH[5]:=Word_01;
260:CrpalkeGrfs[1].AlarmGroupXVH[6]:=Word_01;
261:CrpalkeGrfs[1].AlarmGroupXVH[7]:=Word_01;
262:CrpalkeGrfs[1].AlarmGroupXVH[8]:=Word_01;
263:CrpalkeGrfs[1].AlarmGroupXVH[9]:=Word_01;
264:CrpalkeGrfs[1].AlarmQSD1:=Word_01;
265:CrpalkeGrfs[1].AlarmQSD2:=Word_01;
266:CrpalkeGrfs[1].AlarmStart1:=Word_01;
267:CrpalkeGrfs[1].AlarmStart2:=Word_01;
268:CrpalkeGrfs[1].AlarmStop1:=Word_01;
269:CrpalkeGrfs[1].AlarmStop2:=Word_01;
270:CrpalkeGrfs[1].AlarmStop3:=Word_01;
271:CrpalkeGrfs[1].AlarmSurv1:=Word_01;
272:CrpalkeGrfs[1].AlarmSurv2:=Word_01;
273:CrpalkeGrfs[1].ControlSource:=Word_01;
274:CrpalkeGrfs[1].ExternInputSetup:=Word_01;
275:CrpalkeGrfs[1].ExternInputsStatus:=Word_01;
276:CrpalkeGrfs[1].LocalSetupMode1:=Word_01;
277:CrpalkeGrfs[1].PreklopkaMode:=Word_01;
278:CrpalkeGrfs[1].Relay1setup:=Word_01;
279:CrpalkeGrfs[1].RemoteSetupMode1:=Word_01;
280:CrpalkeGrfs[1].StatusCrpalke:=Byte_0;
281:CrpalkeGrfs[1].StatusMode1:=Word_01;
282:CrpalkeGrfs[1].StatusMode1co:=Byte_0;
283:CrpalkeGrfs[1].StatusMode1op:=Byte_0;
284:CrpalkeGrfs[1].StatusMode2:=Word_01;
285:CrpalkeGrfs[1].StatusMode3:=Word_01;
286:CrpalkeGrfs[2].AlarmActiveCode:=Word_01;
287:CrpalkeGrfs[2].AlarmCodeLog1:=Word_01;
288:CrpalkeGrfs[2].AlarmCodeLog2:=Word_01;
289:CrpalkeGrfs[2].AlarmCodeLog3:=Word_01;
290:CrpalkeGrfs[2].AlarmCodeLog4:=Word_01;
291:CrpalkeGrfs[2].AlarmCodeLog5:=Word_01;
292:CrpalkeGrfs[2].AlarmGroupXVH[0]:=Word_01;
293:CrpalkeGrfs[2].AlarmGroupXVH[10]:=Word_01;
294:CrpalkeGrfs[2].AlarmGroupXVH[11]:=Word_01;
295:CrpalkeGrfs[2].AlarmGroupXVH[12]:=Word_01;
296:CrpalkeGrfs[2].AlarmGroupXVH[13]:=Word_01;
297:CrpalkeGrfs[2].AlarmGroupXVH[14]:=Word_01;
298:CrpalkeGrfs[2].AlarmGroupXVH[15]:=Word_01;
299:CrpalkeGrfs[2].AlarmGroupXVH[16]:=Word_01;
300:CrpalkeGrfs[2].AlarmGroupXVH[1]:=Word_01;
301:CrpalkeGrfs[2].AlarmGroupXVH[2]:=Word_01;
302:CrpalkeGrfs[2].AlarmGroupXVH[3]:=Word_01;
303:CrpalkeGrfs[2].AlarmGroupXVH[4]:=Word_01;
304:CrpalkeGrfs[2].AlarmGroupXVH[5]:=Word_01;
305:CrpalkeGrfs[2].AlarmGroupXVH[6]:=Word_01;
306:CrpalkeGrfs[2].AlarmGroupXVH[7]:=Word_01;
307:CrpalkeGrfs[2].AlarmGroupXVH[8]:=Word_01;
308:CrpalkeGrfs[2].AlarmGroupXVH[9]:=Word_01;
309:CrpalkeGrfs[2].AlarmQSD1:=Word_01;
310:CrpalkeGrfs[2].AlarmQSD2:=Word_01;
311:CrpalkeGrfs[2].AlarmStart1:=Word_01;
312:CrpalkeGrfs[2].AlarmStart2:=Word_01;
313:CrpalkeGrfs[2].AlarmStop1:=Word_01;
314:CrpalkeGrfs[2].AlarmStop2:=Word_01;
315:CrpalkeGrfs[2].AlarmStop3:=Word_01;
316:CrpalkeGrfs[2].AlarmSurv1:=Word_01;
317:CrpalkeGrfs[2].AlarmSurv2:=Word_01;
318:CrpalkeGrfs[2].ControlSource:=Word_01;
319:CrpalkeGrfs[2].ExternInputSetup:=Word_01;
320:CrpalkeGrfs[2].ExternInputsStatus:=Word_01;
321:CrpalkeGrfs[2].LocalSetupMode1:=Word_01;
322:CrpalkeGrfs[2].PreklopkaMode:=Word_01;
323:CrpalkeGrfs[2].Relay1setup:=Word_01;
324:CrpalkeGrfs[2].RemoteSetupMode1:=Word_01;
325:CrpalkeGrfs[2].StatusCrpalke:=Byte_0;
326:CrpalkeGrfs[2].StatusMode1:=Word_01;
327:CrpalkeGrfs[2].StatusMode1co:=Byte_0;
328:CrpalkeGrfs[2].StatusMode1op:=Byte_0;
329:CrpalkeGrfs[2].StatusMode2:=Word_01;
330:CrpalkeGrfs[2].StatusMode3:=Word_01;
331:CrpalkeGrfs[3].AlarmActiveCode:=Word_01;
332:CrpalkeGrfs[3].AlarmCodeLog1:=Word_01;
333:CrpalkeGrfs[3].AlarmCodeLog2:=Word_01;
334:CrpalkeGrfs[3].AlarmCodeLog3:=Word_01;
335:CrpalkeGrfs[3].AlarmCodeLog4:=Word_01;
336:CrpalkeGrfs[3].AlarmCodeLog5:=Word_01;
337:CrpalkeGrfs[3].AlarmGroupXVH[0]:=Word_01;
338:CrpalkeGrfs[3].AlarmGroupXVH[10]:=Word_01;
339:CrpalkeGrfs[3].AlarmGroupXVH[11]:=Word_01;
340:CrpalkeGrfs[3].AlarmGroupXVH[12]:=Word_01;
341:CrpalkeGrfs[3].AlarmGroupXVH[13]:=Word_01;
342:CrpalkeGrfs[3].AlarmGroupXVH[14]:=Word_01;
343:CrpalkeGrfs[3].AlarmGroupXVH[15]:=Word_01;
344:CrpalkeGrfs[3].AlarmGroupXVH[16]:=Word_01;
345:CrpalkeGrfs[3].AlarmGroupXVH[1]:=Word_01;
346:CrpalkeGrfs[3].AlarmGroupXVH[2]:=Word_01;
347:CrpalkeGrfs[3].AlarmGroupXVH[3]:=Word_01;
348:CrpalkeGrfs[3].AlarmGroupXVH[4]:=Word_01;
349:CrpalkeGrfs[3].AlarmGroupXVH[5]:=Word_01;
350:CrpalkeGrfs[3].AlarmGroupXVH[6]:=Word_01;
351:CrpalkeGrfs[3].AlarmGroupXVH[7]:=Word_01;
352:CrpalkeGrfs[3].AlarmGroupXVH[8]:=Word_01;
353:CrpalkeGrfs[3].AlarmGroupXVH[9]:=Word_01;
354:CrpalkeGrfs[3].AlarmQSD1:=Word_01;
355:CrpalkeGrfs[3].AlarmQSD2:=Word_01;
356:CrpalkeGrfs[3].AlarmStart1:=Word_01;
357:CrpalkeGrfs[3].AlarmStart2:=Word_01;
358:CrpalkeGrfs[3].AlarmStop1:=Word_01;
359:CrpalkeGrfs[3].AlarmStop2:=Word_01;
360:CrpalkeGrfs[3].AlarmStop3:=Word_01;
361:CrpalkeGrfs[3].AlarmSurv1:=Word_01;
362:CrpalkeGrfs[3].AlarmSurv2:=Word_01;
363:CrpalkeGrfs[3].ControlSource:=Word_01;
364:CrpalkeGrfs[3].ExternInputSetup:=Word_01;
365:CrpalkeGrfs[3].ExternInputsStatus:=Word_01;
366:CrpalkeGrfs[3].LocalSetupMode1:=Word_01;
367:CrpalkeGrfs[3].PreklopkaMode:=Word_01;
368:CrpalkeGrfs[3].Relay1setup:=Word_01;
369:CrpalkeGrfs[3].RemoteSetupMode1:=Word_01;
370:CrpalkeGrfs[3].StatusCrpalke:=Byte_0;
371:CrpalkeGrfs[3].StatusMode1:=Word_01;
372:CrpalkeGrfs[3].StatusMode1co:=Byte_0;
373:CrpalkeGrfs[3].StatusMode1op:=Byte_0;
374:CrpalkeGrfs[3].StatusMode2:=Word_01;
375:CrpalkeGrfs[3].StatusMode3:=Word_01;
376:CrpalkeGrfs[4].AlarmActiveCode:=Word_01;
377:CrpalkeGrfs[4].AlarmCodeLog1:=Word_01;
378:CrpalkeGrfs[4].AlarmCodeLog2:=Word_01;
379:CrpalkeGrfs[4].AlarmCodeLog3:=Word_01;
380:CrpalkeGrfs[4].AlarmCodeLog4:=Word_01;
381:CrpalkeGrfs[4].AlarmCodeLog5:=Word_01;
382:CrpalkeGrfs[4].AlarmGroupXVH[0]:=Word_01;
383:CrpalkeGrfs[4].AlarmGroupXVH[10]:=Word_01;
384:CrpalkeGrfs[4].AlarmGroupXVH[11]:=Word_01;
385:CrpalkeGrfs[4].AlarmGroupXVH[12]:=Word_01;
386:CrpalkeGrfs[4].AlarmGroupXVH[13]:=Word_01;
387:CrpalkeGrfs[4].AlarmGroupXVH[14]:=Word_01;
388:CrpalkeGrfs[4].AlarmGroupXVH[15]:=Word_01;
389:CrpalkeGrfs[4].AlarmGroupXVH[16]:=Word_01;
390:CrpalkeGrfs[4].AlarmGroupXVH[1]:=Word_01;
391:CrpalkeGrfs[4].AlarmGroupXVH[2]:=Word_01;
392:CrpalkeGrfs[4].AlarmGroupXVH[3]:=Word_01;
393:CrpalkeGrfs[4].AlarmGroupXVH[4]:=Word_01;
394:CrpalkeGrfs[4].AlarmGroupXVH[5]:=Word_01;
395:CrpalkeGrfs[4].AlarmGroupXVH[6]:=Word_01;
396:CrpalkeGrfs[4].AlarmGroupXVH[7]:=Word_01;
397:CrpalkeGrfs[4].AlarmGroupXVH[8]:=Word_01;
398:CrpalkeGrfs[4].AlarmGroupXVH[9]:=Word_01;
399:CrpalkeGrfs[4].AlarmQSD1:=Word_01;
400:CrpalkeGrfs[4].AlarmQSD2:=Word_01;
401:CrpalkeGrfs[4].AlarmStart1:=Word_01;
402:CrpalkeGrfs[4].AlarmStart2:=Word_01;
403:CrpalkeGrfs[4].AlarmStop1:=Word_01;
404:CrpalkeGrfs[4].AlarmStop2:=Word_01;
405:CrpalkeGrfs[4].AlarmStop3:=Word_01;
406:CrpalkeGrfs[4].AlarmSurv1:=Word_01;
407:CrpalkeGrfs[4].AlarmSurv2:=Word_01;
408:CrpalkeGrfs[4].ControlSource:=Word_01;
409:CrpalkeGrfs[4].ExternInputSetup:=Word_01;
410:CrpalkeGrfs[4].ExternInputsStatus:=Word_01;
411:CrpalkeGrfs[4].LocalSetupMode1:=Word_01;
412:CrpalkeGrfs[4].PreklopkaMode:=Word_01;
413:CrpalkeGrfs[4].Relay1setup:=Word_01;
414:CrpalkeGrfs[4].RemoteSetupMode1:=Word_01;
415:CrpalkeGrfs[4].StatusCrpalke:=Byte_0;
416:CrpalkeGrfs[4].StatusMode1:=Word_01;
417:CrpalkeGrfs[4].StatusMode1co:=Byte_0;
418:CrpalkeGrfs[4].StatusMode1op:=Byte_0;
419:CrpalkeGrfs[4].StatusMode2:=Word_01;
420:CrpalkeGrfs[4].StatusMode3:=Word_01;
421:CrpalkeGrfs[5].AlarmActiveCode:=Word_01;
422:CrpalkeGrfs[5].AlarmCodeLog1:=Word_01;
423:CrpalkeGrfs[5].AlarmCodeLog2:=Word_01;
424:CrpalkeGrfs[5].AlarmCodeLog3:=Word_01;
425:CrpalkeGrfs[5].AlarmCodeLog4:=Word_01;
426:CrpalkeGrfs[5].AlarmCodeLog5:=Word_01;
427:CrpalkeGrfs[5].AlarmGroupXVH[0]:=Word_01;
428:CrpalkeGrfs[5].AlarmGroupXVH[10]:=Word_01;
429:CrpalkeGrfs[5].AlarmGroupXVH[11]:=Word_01;
430:CrpalkeGrfs[5].AlarmGroupXVH[12]:=Word_01;
431:CrpalkeGrfs[5].AlarmGroupXVH[13]:=Word_01;
432:CrpalkeGrfs[5].AlarmGroupXVH[14]:=Word_01;
433:CrpalkeGrfs[5].AlarmGroupXVH[15]:=Word_01;
434:CrpalkeGrfs[5].AlarmGroupXVH[16]:=Word_01;
435:CrpalkeGrfs[5].AlarmGroupXVH[1]:=Word_01;
436:CrpalkeGrfs[5].AlarmGroupXVH[2]:=Word_01;
437:CrpalkeGrfs[5].AlarmGroupXVH[3]:=Word_01;
438:CrpalkeGrfs[5].AlarmGroupXVH[4]:=Word_01;
439:CrpalkeGrfs[5].AlarmGroupXVH[5]:=Word_01;
440:CrpalkeGrfs[5].AlarmGroupXVH[6]:=Word_01;
441:CrpalkeGrfs[5].AlarmGroupXVH[7]:=Word_01;
442:CrpalkeGrfs[5].AlarmGroupXVH[8]:=Word_01;
443:CrpalkeGrfs[5].AlarmGroupXVH[9]:=Word_01;
444:CrpalkeGrfs[5].AlarmQSD1:=Word_01;
445:CrpalkeGrfs[5].AlarmQSD2:=Word_01;
446:CrpalkeGrfs[5].AlarmStart1:=Word_01;
447:CrpalkeGrfs[5].AlarmStart2:=Word_01;
448:CrpalkeGrfs[5].AlarmStop1:=Word_01;
449:CrpalkeGrfs[5].AlarmStop2:=Word_01;
450:CrpalkeGrfs[5].AlarmStop3:=Word_01;
451:CrpalkeGrfs[5].AlarmSurv1:=Word_01;
452:CrpalkeGrfs[5].AlarmSurv2:=Word_01;
453:CrpalkeGrfs[5].ControlSource:=Word_01;
454:CrpalkeGrfs[5].ExternInputSetup:=Word_01;
455:CrpalkeGrfs[5].ExternInputsStatus:=Word_01;
456:CrpalkeGrfs[5].LocalSetupMode1:=Word_01;
457:CrpalkeGrfs[5].PreklopkaMode:=Word_01;
458:CrpalkeGrfs[5].Relay1setup:=Word_01;
459:CrpalkeGrfs[5].RemoteSetupMode1:=Word_01;
460:CrpalkeGrfs[5].StatusCrpalke:=Byte_0;
461:CrpalkeGrfs[5].StatusMode1:=Word_01;
462:CrpalkeGrfs[5].StatusMode1co:=Byte_0;
463:CrpalkeGrfs[5].StatusMode1op:=Byte_0;
464:CrpalkeGrfs[5].StatusMode2:=Word_01;
465:CrpalkeGrfs[5].StatusMode3:=Word_01;
466:CrpalkeGrfs[6].AlarmActiveCode:=Word_01;
467:CrpalkeGrfs[6].AlarmCodeLog1:=Word_01;
468:CrpalkeGrfs[6].AlarmCodeLog2:=Word_01;
469:CrpalkeGrfs[6].AlarmCodeLog3:=Word_01;
470:CrpalkeGrfs[6].AlarmCodeLog4:=Word_01;
471:CrpalkeGrfs[6].AlarmCodeLog5:=Word_01;
472:CrpalkeGrfs[6].AlarmGroupXVH[0]:=Word_01;
473:CrpalkeGrfs[6].AlarmGroupXVH[10]:=Word_01;
474:CrpalkeGrfs[6].AlarmGroupXVH[11]:=Word_01;
475:CrpalkeGrfs[6].AlarmGroupXVH[12]:=Word_01;
476:CrpalkeGrfs[6].AlarmGroupXVH[13]:=Word_01;
477:CrpalkeGrfs[6].AlarmGroupXVH[14]:=Word_01;
478:CrpalkeGrfs[6].AlarmGroupXVH[15]:=Word_01;
479:CrpalkeGrfs[6].AlarmGroupXVH[16]:=Word_01;
480:CrpalkeGrfs[6].AlarmGroupXVH[1]:=Word_01;
481:CrpalkeGrfs[6].AlarmGroupXVH[2]:=Word_01;
482:CrpalkeGrfs[6].AlarmGroupXVH[3]:=Word_01;
483:CrpalkeGrfs[6].AlarmGroupXVH[4]:=Word_01;
484:CrpalkeGrfs[6].AlarmGroupXVH[5]:=Word_01;
485:CrpalkeGrfs[6].AlarmGroupXVH[6]:=Word_01;
486:CrpalkeGrfs[6].AlarmGroupXVH[7]:=Word_01;
487:CrpalkeGrfs[6].AlarmGroupXVH[8]:=Word_01;
488:CrpalkeGrfs[6].AlarmGroupXVH[9]:=Word_01;
489:CrpalkeGrfs[6].AlarmQSD1:=Word_01;
490:CrpalkeGrfs[6].AlarmQSD2:=Word_01;
491:CrpalkeGrfs[6].AlarmStart1:=Word_01;
492:CrpalkeGrfs[6].AlarmStart2:=Word_01;
493:CrpalkeGrfs[6].AlarmStop1:=Word_01;
494:CrpalkeGrfs[6].AlarmStop2:=Word_01;
495:CrpalkeGrfs[6].AlarmStop3:=Word_01;
496:CrpalkeGrfs[6].AlarmSurv1:=Word_01;
497:CrpalkeGrfs[6].AlarmSurv2:=Word_01;
498:CrpalkeGrfs[6].ControlSource:=Word_01;
499:CrpalkeGrfs[6].ExternInputSetup:=Word_01;
500:CrpalkeGrfs[6].ExternInputsStatus:=Word_01;
501:CrpalkeGrfs[6].LocalSetupMode1:=Word_01;
502:CrpalkeGrfs[6].PreklopkaMode:=Word_01;
503:CrpalkeGrfs[6].Relay1setup:=Word_01;
504:CrpalkeGrfs[6].RemoteSetupMode1:=Word_01;
505:CrpalkeGrfs[6].StatusCrpalke:=Byte_0;
506:CrpalkeGrfs[6].StatusMode1:=Word_01;
507:CrpalkeGrfs[6].StatusMode1co:=Byte_0;
508:CrpalkeGrfs[6].StatusMode1op:=Byte_0;
509:CrpalkeGrfs[6].StatusMode2:=Word_01;
510:CrpalkeGrfs[6].StatusMode3:=Word_01;
511:CrpalkeGrfs[7].AlarmActiveCode:=Word_01;
512:CrpalkeGrfs[7].AlarmCodeLog1:=Word_01;
513:CrpalkeGrfs[7].AlarmCodeLog2:=Word_01;
514:CrpalkeGrfs[7].AlarmCodeLog3:=Word_01;
515:CrpalkeGrfs[7].AlarmCodeLog4:=Word_01;
516:CrpalkeGrfs[7].AlarmCodeLog5:=Word_01;
517:CrpalkeGrfs[7].AlarmGroupXVH[0]:=Word_01;
518:CrpalkeGrfs[7].AlarmGroupXVH[10]:=Word_01;
519:CrpalkeGrfs[7].AlarmGroupXVH[11]:=Word_01;
520:CrpalkeGrfs[7].AlarmGroupXVH[12]:=Word_01;
521:CrpalkeGrfs[7].AlarmGroupXVH[13]:=Word_01;
522:CrpalkeGrfs[7].AlarmGroupXVH[14]:=Word_01;
523:CrpalkeGrfs[7].AlarmGroupXVH[15]:=Word_01;
524:CrpalkeGrfs[7].AlarmGroupXVH[16]:=Word_01;
525:CrpalkeGrfs[7].AlarmGroupXVH[1]:=Word_01;
526:CrpalkeGrfs[7].AlarmGroupXVH[2]:=Word_01;
527:CrpalkeGrfs[7].AlarmGroupXVH[3]:=Word_01;
528:CrpalkeGrfs[7].AlarmGroupXVH[4]:=Word_01;
529:CrpalkeGrfs[7].AlarmGroupXVH[5]:=Word_01;
530:CrpalkeGrfs[7].AlarmGroupXVH[6]:=Word_01;
531:CrpalkeGrfs[7].AlarmGroupXVH[7]:=Word_01;
532:CrpalkeGrfs[7].AlarmGroupXVH[8]:=Word_01;
533:CrpalkeGrfs[7].AlarmGroupXVH[9]:=Word_01;
534:CrpalkeGrfs[7].AlarmQSD1:=Word_01;
535:CrpalkeGrfs[7].AlarmQSD2:=Word_01;
536:CrpalkeGrfs[7].AlarmStart1:=Word_01;
537:CrpalkeGrfs[7].AlarmStart2:=Word_01;
538:CrpalkeGrfs[7].AlarmStop1:=Word_01;
539:CrpalkeGrfs[7].AlarmStop2:=Word_01;
540:CrpalkeGrfs[7].AlarmStop3:=Word_01;
541:CrpalkeGrfs[7].AlarmSurv1:=Word_01;
542:CrpalkeGrfs[7].AlarmSurv2:=Word_01;
543:CrpalkeGrfs[7].ControlSource:=Word_01;
544:CrpalkeGrfs[7].ExternInputSetup:=Word_01;
545:CrpalkeGrfs[7].ExternInputsStatus:=Word_01;
546:CrpalkeGrfs[7].LocalSetupMode1:=Word_01;
547:CrpalkeGrfs[7].PreklopkaMode:=Word_01;
548:CrpalkeGrfs[7].Relay1setup:=Word_01;
549:CrpalkeGrfs[7].RemoteSetupMode1:=Word_01;
550:CrpalkeGrfs[7].StatusCrpalke:=Byte_0;
551:CrpalkeGrfs[7].StatusMode1:=Word_01;
552:CrpalkeGrfs[7].StatusMode1co:=Byte_0;
553:CrpalkeGrfs[7].StatusMode1op:=Byte_0;
554:CrpalkeGrfs[7].StatusMode2:=Word_01;
555:CrpalkeGrfs[7].StatusMode3:=Word_01;
556:CrpalkeGrfs[8].AlarmActiveCode:=Word_01;
557:CrpalkeGrfs[8].AlarmCodeLog1:=Word_01;
558:CrpalkeGrfs[8].AlarmCodeLog2:=Word_01;
559:CrpalkeGrfs[8].AlarmCodeLog3:=Word_01;
560:CrpalkeGrfs[8].AlarmCodeLog4:=Word_01;
561:CrpalkeGrfs[8].AlarmCodeLog5:=Word_01;
562:CrpalkeGrfs[8].AlarmGroupXVH[0]:=Word_01;
563:CrpalkeGrfs[8].AlarmGroupXVH[10]:=Word_01;
564:CrpalkeGrfs[8].AlarmGroupXVH[11]:=Word_01;
565:CrpalkeGrfs[8].AlarmGroupXVH[12]:=Word_01;
566:CrpalkeGrfs[8].AlarmGroupXVH[13]:=Word_01;
567:CrpalkeGrfs[8].AlarmGroupXVH[14]:=Word_01;
568:CrpalkeGrfs[8].AlarmGroupXVH[15]:=Word_01;
569:CrpalkeGrfs[8].AlarmGroupXVH[16]:=Word_01;
570:CrpalkeGrfs[8].AlarmGroupXVH[1]:=Word_01;
571:CrpalkeGrfs[8].AlarmGroupXVH[2]:=Word_01;
572:CrpalkeGrfs[8].AlarmGroupXVH[3]:=Word_01;
573:CrpalkeGrfs[8].AlarmGroupXVH[4]:=Word_01;
574:CrpalkeGrfs[8].AlarmGroupXVH[5]:=Word_01;
575:CrpalkeGrfs[8].AlarmGroupXVH[6]:=Word_01;
576:CrpalkeGrfs[8].AlarmGroupXVH[7]:=Word_01;
577:CrpalkeGrfs[8].AlarmGroupXVH[8]:=Word_01;
578:CrpalkeGrfs[8].AlarmGroupXVH[9]:=Word_01;
579:CrpalkeGrfs[8].AlarmQSD1:=Word_01;
580:CrpalkeGrfs[8].AlarmQSD2:=Word_01;
581:CrpalkeGrfs[8].AlarmStart1:=Word_01;
582:CrpalkeGrfs[8].AlarmStart2:=Word_01;
583:CrpalkeGrfs[8].AlarmStop1:=Word_01;
584:CrpalkeGrfs[8].AlarmStop2:=Word_01;
585:CrpalkeGrfs[8].AlarmStop3:=Word_01;
586:CrpalkeGrfs[8].AlarmSurv1:=Word_01;
587:CrpalkeGrfs[8].AlarmSurv2:=Word_01;
588:CrpalkeGrfs[8].ControlSource:=Word_01;
589:CrpalkeGrfs[8].ExternInputSetup:=Word_01;
590:CrpalkeGrfs[8].ExternInputsStatus:=Word_01;
591:CrpalkeGrfs[8].LocalSetupMode1:=Word_01;
592:CrpalkeGrfs[8].PreklopkaMode:=Word_01;
593:CrpalkeGrfs[8].Relay1setup:=Word_01;
594:CrpalkeGrfs[8].RemoteSetupMode1:=Word_01;
595:CrpalkeGrfs[8].StatusCrpalke:=Byte_0;
596:CrpalkeGrfs[8].StatusMode1:=Word_01;
597:CrpalkeGrfs[8].StatusMode1co:=Byte_0;
598:CrpalkeGrfs[8].StatusMode1op:=Byte_0;
599:CrpalkeGrfs[8].StatusMode2:=Word_01;
600:CrpalkeGrfs[8].StatusMode3:=Word_01;
601:CrpalkeGrfs[9].AlarmActiveCode:=Word_01;
602:CrpalkeGrfs[9].AlarmCodeLog1:=Word_01;
603:CrpalkeGrfs[9].AlarmCodeLog2:=Word_01;
604:CrpalkeGrfs[9].AlarmCodeLog3:=Word_01;
605:CrpalkeGrfs[9].AlarmCodeLog4:=Word_01;
606:CrpalkeGrfs[9].AlarmCodeLog5:=Word_01;
607:CrpalkeGrfs[9].AlarmGroupXVH[0]:=Word_01;
608:CrpalkeGrfs[9].AlarmGroupXVH[10]:=Word_01;
609:CrpalkeGrfs[9].AlarmGroupXVH[11]:=Word_01;
610:CrpalkeGrfs[9].AlarmGroupXVH[12]:=Word_01;
611:CrpalkeGrfs[9].AlarmGroupXVH[13]:=Word_01;
612:CrpalkeGrfs[9].AlarmGroupXVH[14]:=Word_01;
613:CrpalkeGrfs[9].AlarmGroupXVH[15]:=Word_01;
614:CrpalkeGrfs[9].AlarmGroupXVH[16]:=Word_01;
615:CrpalkeGrfs[9].AlarmGroupXVH[1]:=Word_01;
616:CrpalkeGrfs[9].AlarmGroupXVH[2]:=Word_01;
617:CrpalkeGrfs[9].AlarmGroupXVH[3]:=Word_01;
618:CrpalkeGrfs[9].AlarmGroupXVH[4]:=Word_01;
619:CrpalkeGrfs[9].AlarmGroupXVH[5]:=Word_01;
620:CrpalkeGrfs[9].AlarmGroupXVH[6]:=Word_01;
621:CrpalkeGrfs[9].AlarmGroupXVH[7]:=Word_01;
622:CrpalkeGrfs[9].AlarmGroupXVH[8]:=Word_01;
623:CrpalkeGrfs[9].AlarmGroupXVH[9]:=Word_01;
624:CrpalkeGrfs[9].AlarmQSD1:=Word_01;
625:CrpalkeGrfs[9].AlarmQSD2:=Word_01;
626:CrpalkeGrfs[9].AlarmStart1:=Word_01;
627:CrpalkeGrfs[9].AlarmStart2:=Word_01;
628:CrpalkeGrfs[9].AlarmStop1:=Word_01;
629:CrpalkeGrfs[9].AlarmStop2:=Word_01;
630:CrpalkeGrfs[9].AlarmStop3:=Word_01;
631:CrpalkeGrfs[9].AlarmSurv1:=Word_01;
632:CrpalkeGrfs[9].AlarmSurv2:=Word_01;
633:CrpalkeGrfs[9].ControlSource:=Word_01;
634:CrpalkeGrfs[9].ExternInputSetup:=Word_01;
635:CrpalkeGrfs[9].ExternInputsStatus:=Word_01;
636:CrpalkeGrfs[9].LocalSetupMode1:=Word_01;
637:CrpalkeGrfs[9].PreklopkaMode:=Word_01;
638:CrpalkeGrfs[9].Relay1setup:=Word_01;
639:CrpalkeGrfs[9].RemoteSetupMode1:=Word_01;
640:CrpalkeGrfs[9].StatusCrpalke:=Byte_0;
641:CrpalkeGrfs[9].StatusMode1:=Word_01;
642:CrpalkeGrfs[9].StatusMode1co:=Byte_0;
643:CrpalkeGrfs[9].StatusMode1op:=Byte_0;
644:CrpalkeGrfs[9].StatusMode2:=Word_01;
645:CrpalkeGrfs[9].StatusMode3:=Word_01;
646:DateTime.Dan:=Byte_0;
647:DateTime.Leto:=Byte_0;
648:DateTime.Mesec:=Byte_0;
649:DateTime.Minuta:=Byte_0;
650:DateTime.Sekunda:=Byte_0;
651:DateTime.Ura:=Byte_0;
652:HladStroj.KompresorOljeAlarmB:=Byte_0;
653:HladStroj.NizekPritiskAlarmB:=Byte_0;
654:HladStroj.ObratovalneUreOpozoriloB:=Byte_0;
655:HladStroj.TemperaturaAlarmB:=Byte_0;
656:HladStroj.UnitStatus:=Word_01;
657:HladStroj.VisokPritiskAlarmB:=Byte_0;
658:HladStroj.VisokPritiskOpozoriloB:=Byte_0;
659:HladStroj.ZmrzalniAlarmB:=Byte_0;
660:Klima[1].CrpalkaStatus:=Byte_0;
661:Klima[1].HitrostVentStatus:=Byte_0;
662:Klima[1].IzhodniVentStatus:=Byte_0;
663:Klima[2].CrpalkaStatus:=Byte_0;
664:Klima[2].HitrostVentStatus:=Byte_0;
665:Klima[2].IzhodniVentStatus:=Byte_0;
666:PozarnaLoputaStatus[1]:=Byte_0;
667:PozarnaLoputaStatus[2]:=Byte_0;
668:PozarnaLoputaStatus[3]:=Byte_0;
669:PozarnaLoputaStatus[4]:=Byte_0;
670:PozarnaLoputaStatus[5]:=Byte_0;
671:StatusKondenzEnota[0]:=Byte_0;
672:StatusKondenzEnota[1]:=Byte_0;
673:StatusKondenzEnota[2]:=Byte_0;
674:StatusKondenzEnota[3]:=Byte_0;
675:StatusKontaktor[10]:=Byte_0;
676:StatusKontaktor[11]:=Byte_0;
677:StatusKontaktor[12]:=Byte_0;
678:StatusKontaktor[13]:=Byte_0;
679:StatusKontaktor[14]:=Byte_0;
680:StatusKontaktor[15]:=Byte_0;
681:StatusKontaktor[16]:=Byte_0;
682:StatusKontaktor[17]:=Byte_0;
683:StatusKontaktor[18]:=Byte_0;
684:StatusKontaktor[19]:=Byte_0;
685:StatusKontaktor[1]:=Byte_0;
686:StatusKontaktor[20]:=Byte_0;
687:StatusKontaktor[21]:=Byte_0;
688:StatusKontaktor[22]:=Byte_0;
689:StatusKontaktor[23]:=Byte_0;
690:StatusKontaktor[24]:=Byte_0;
691:StatusKontaktor[25]:=Byte_0;
692:StatusKontaktor[2]:=Byte_0;
693:StatusKontaktor[3]:=Byte_0;
694:StatusKontaktor[4]:=Byte_0;
695:StatusKontaktor[5]:=Byte_0;
696:StatusKontaktor[6]:=Byte_0;
697:StatusKontaktor[7]:=Byte_0;
698:StatusKontaktor[8]:=Byte_0;
699:StatusKontaktor[9]:=Byte_0;
700:StatusPreklopke[10]:=Byte_0;
701:StatusPreklopke[11]:=Byte_0;
702:StatusPreklopke[12]:=Byte_0;
703:StatusPreklopke[13]:=Byte_0;
704:StatusPreklopke[14]:=Byte_0;
705:StatusPreklopke[15]:=Byte_0;
706:StatusPreklopke[16]:=Byte_0;
707:StatusPreklopke[17]:=Byte_0;
708:StatusPreklopke[18]:=Byte_0;
709:StatusPreklopke[19]:=Byte_0;
710:StatusPreklopke[1]:=Byte_0;
711:StatusPreklopke[20]:=Byte_0;
712:StatusPreklopke[21]:=Byte_0;
713:StatusPreklopke[22]:=Byte_0;
714:StatusPreklopke[23]:=Byte_0;
715:StatusPreklopke[24]:=Byte_0;
716:StatusPreklopke[25]:=Byte_0;
717:StatusPreklopke[2]:=Byte_0;
718:StatusPreklopke[3]:=Byte_0;
719:StatusPreklopke[4]:=Byte_0;
720:StatusPreklopke[5]:=Byte_0;
721:StatusPreklopke[6]:=Byte_0;
722:StatusPreklopke[7]:=Byte_0;
723:StatusPreklopke[8]:=Byte_0;
724:StatusPreklopke[9]:=Byte_0;
725:ToplPost.NapakaRegister:=Word_01;
726:Urnik_SCtoXCpot:=Word_01;
727:Urnik_SCtoXCzah:=Word_01;
728:Urnik_XCtoSCpot:=Word_01;
729:Urnik_XCtoSCzah:=Word_01;
730:UrnikSCtoXC.Dan[1].Off[1].Mna:=Byte_0;
731:UrnikSCtoXC.Dan[1].Off[1].Ura:=Byte_0;
732:UrnikSCtoXC.Dan[1].Off[2].Mna:=Byte_0;
733:UrnikSCtoXC.Dan[1].Off[2].Ura:=Byte_0;
734:UrnikSCtoXC.Dan[1].Off[3].Mna:=Byte_0;
735:UrnikSCtoXC.Dan[1].Off[3].Ura:=Byte_0;
736:UrnikSCtoXC.Dan[1].On[1].Mna:=Byte_0;
737:UrnikSCtoXC.Dan[1].On[1].Ura:=Byte_0;
738:UrnikSCtoXC.Dan[1].On[2].Mna:=Byte_0;
739:UrnikSCtoXC.Dan[1].On[2].Ura:=Byte_0;
740:UrnikSCtoXC.Dan[1].On[3].Mna:=Byte_0;
741:UrnikSCtoXC.Dan[1].On[3].Ura:=Byte_0;
742:UrnikSCtoXC.Dan[2].Off[1].Mna:=Byte_0;
743:UrnikSCtoXC.Dan[2].Off[1].Ura:=Byte_0;
744:UrnikSCtoXC.Dan[2].Off[2].Mna:=Byte_0;
745:UrnikSCtoXC.Dan[2].Off[2].Ura:=Byte_0;
746:UrnikSCtoXC.Dan[2].Off[3].Mna:=Byte_0;
747:UrnikSCtoXC.Dan[2].Off[3].Ura:=Byte_0;
748:UrnikSCtoXC.Dan[2].On[1].Mna:=Byte_0;
749:UrnikSCtoXC.Dan[2].On[1].Ura:=Byte_0;
750:UrnikSCtoXC.Dan[2].On[2].Mna:=Byte_0;
751:UrnikSCtoXC.Dan[2].On[2].Ura:=Byte_0;
752:UrnikSCtoXC.Dan[2].On[3].Mna:=Byte_0;
753:UrnikSCtoXC.Dan[2].On[3].Ura:=Byte_0;
754:UrnikSCtoXC.Dan[3].Off[1].Mna:=Byte_0;
755:UrnikSCtoXC.Dan[3].Off[1].Ura:=Byte_0;
756:UrnikSCtoXC.Dan[3].Off[2].Mna:=Byte_0;
757:UrnikSCtoXC.Dan[3].Off[2].Ura:=Byte_0;
758:UrnikSCtoXC.Dan[3].Off[3].Mna:=Byte_0;
759:UrnikSCtoXC.Dan[3].Off[3].Ura:=Byte_0;
760:UrnikSCtoXC.Dan[3].On[1].Mna:=Byte_0;
761:UrnikSCtoXC.Dan[3].On[1].Ura:=Byte_0;
762:UrnikSCtoXC.Dan[3].On[2].Mna:=Byte_0;
763:UrnikSCtoXC.Dan[3].On[2].Ura:=Byte_0;
764:UrnikSCtoXC.Dan[3].On[3].Mna:=Byte_0;
765:UrnikSCtoXC.Dan[3].On[3].Ura:=Byte_0;
766:UrnikSCtoXC.Dan[4].Off[1].Mna:=Byte_0;
767:UrnikSCtoXC.Dan[4].Off[1].Ura:=Byte_0;
768:UrnikSCtoXC.Dan[4].Off[2].Mna:=Byte_0;
769:UrnikSCtoXC.Dan[4].Off[2].Ura:=Byte_0;
770:UrnikSCtoXC.Dan[4].Off[3].Mna:=Byte_0;
771:UrnikSCtoXC.Dan[4].Off[3].Ura:=Byte_0;
772:UrnikSCtoXC.Dan[4].On[1].Mna:=Byte_0;
773:UrnikSCtoXC.Dan[4].On[1].Ura:=Byte_0;
774:UrnikSCtoXC.Dan[4].On[2].Mna:=Byte_0;
775:UrnikSCtoXC.Dan[4].On[2].Ura:=Byte_0;
776:UrnikSCtoXC.Dan[4].On[3].Mna:=Byte_0;
777:UrnikSCtoXC.Dan[4].On[3].Ura:=Byte_0;
778:UrnikSCtoXC.Dan[5].Off[1].Mna:=Byte_0;
779:UrnikSCtoXC.Dan[5].Off[1].Ura:=Byte_0;
780:UrnikSCtoXC.Dan[5].Off[2].Mna:=Byte_0;
781:UrnikSCtoXC.Dan[5].Off[2].Ura:=Byte_0;
782:UrnikSCtoXC.Dan[5].Off[3].Mna:=Byte_0;
783:UrnikSCtoXC.Dan[5].Off[3].Ura:=Byte_0;
784:UrnikSCtoXC.Dan[5].On[1].Mna:=Byte_0;
785:UrnikSCtoXC.Dan[5].On[1].Ura:=Byte_0;
786:UrnikSCtoXC.Dan[5].On[2].Mna:=Byte_0;
787:UrnikSCtoXC.Dan[5].On[2].Ura:=Byte_0;
788:UrnikSCtoXC.Dan[5].On[3].Mna:=Byte_0;
789:UrnikSCtoXC.Dan[5].On[3].Ura:=Byte_0;
790:UrnikSCtoXC.Dan[6].Off[1].Mna:=Byte_0;
791:UrnikSCtoXC.Dan[6].Off[1].Ura:=Byte_0;
792:UrnikSCtoXC.Dan[6].Off[2].Mna:=Byte_0;
793:UrnikSCtoXC.Dan[6].Off[2].Ura:=Byte_0;
794:UrnikSCtoXC.Dan[6].Off[3].Mna:=Byte_0;
795:UrnikSCtoXC.Dan[6].Off[3].Ura:=Byte_0;
796:UrnikSCtoXC.Dan[6].On[1].Mna:=Byte_0;
797:UrnikSCtoXC.Dan[6].On[1].Ura:=Byte_0;
798:UrnikSCtoXC.Dan[6].On[2].Mna:=Byte_0;
799:UrnikSCtoXC.Dan[6].On[2].Ura:=Byte_0;
800:UrnikSCtoXC.Dan[6].On[3].Mna:=Byte_0;
801:UrnikSCtoXC.Dan[6].On[3].Ura:=Byte_0;
802:UrnikSCtoXC.Dan[7].Off[1].Mna:=Byte_0;
803:UrnikSCtoXC.Dan[7].Off[1].Ura:=Byte_0;
804:UrnikSCtoXC.Dan[7].Off[2].Mna:=Byte_0;
805:UrnikSCtoXC.Dan[7].Off[2].Ura:=Byte_0;
806:UrnikSCtoXC.Dan[7].Off[3].Mna:=Byte_0;
807:UrnikSCtoXC.Dan[7].Off[3].Ura:=Byte_0;
808:UrnikSCtoXC.Dan[7].On[1].Mna:=Byte_0;
809:UrnikSCtoXC.Dan[7].On[1].Ura:=Byte_0;
810:UrnikSCtoXC.Dan[7].On[2].Mna:=Byte_0;
811:UrnikSCtoXC.Dan[7].On[2].Ura:=Byte_0;
812:UrnikSCtoXC.Dan[7].On[3].Mna:=Byte_0;
813:UrnikSCtoXC.Dan[7].On[3].Ura:=Byte_0;
814:UrnikXCtoSC.Dan[1].Off[1].Mna:=Byte_0;
815:UrnikXCtoSC.Dan[1].Off[1].Ura:=Byte_0;
816:UrnikXCtoSC.Dan[1].Off[2].Mna:=Byte_0;
817:UrnikXCtoSC.Dan[1].Off[2].Ura:=Byte_0;
818:UrnikXCtoSC.Dan[1].Off[3].Mna:=Byte_0;
819:UrnikXCtoSC.Dan[1].Off[3].Ura:=Byte_0;
820:UrnikXCtoSC.Dan[1].On[1].Mna:=Byte_0;
821:UrnikXCtoSC.Dan[1].On[1].Ura:=Byte_0;
822:UrnikXCtoSC.Dan[1].On[2].Mna:=Byte_0;
823:UrnikXCtoSC.Dan[1].On[2].Ura:=Byte_0;
824:UrnikXCtoSC.Dan[1].On[3].Mna:=Byte_0;
825:UrnikXCtoSC.Dan[1].On[3].Ura:=Byte_0;
826:UrnikXCtoSC.Dan[2].Off[1].Mna:=Byte_0;
827:UrnikXCtoSC.Dan[2].Off[1].Ura:=Byte_0;
828:UrnikXCtoSC.Dan[2].Off[2].Mna:=Byte_0;
829:UrnikXCtoSC.Dan[2].Off[2].Ura:=Byte_0;
830:UrnikXCtoSC.Dan[2].Off[3].Mna:=Byte_0;
831:UrnikXCtoSC.Dan[2].Off[3].Ura:=Byte_0;
832:UrnikXCtoSC.Dan[2].On[1].Mna:=Byte_0;
833:UrnikXCtoSC.Dan[2].On[1].Ura:=Byte_0;
834:UrnikXCtoSC.Dan[2].On[2].Mna:=Byte_0;
835:UrnikXCtoSC.Dan[2].On[2].Ura:=Byte_0;
836:UrnikXCtoSC.Dan[2].On[3].Mna:=Byte_0;
837:UrnikXCtoSC.Dan[2].On[3].Ura:=Byte_0;
838:UrnikXCtoSC.Dan[3].Off[1].Mna:=Byte_0;
839:UrnikXCtoSC.Dan[3].Off[1].Ura:=Byte_0;
840:UrnikXCtoSC.Dan[3].Off[2].Mna:=Byte_0;
841:UrnikXCtoSC.Dan[3].Off[2].Ura:=Byte_0;
842:UrnikXCtoSC.Dan[3].Off[3].Mna:=Byte_0;
843:UrnikXCtoSC.Dan[3].Off[3].Ura:=Byte_0;
844:UrnikXCtoSC.Dan[3].On[1].Mna:=Byte_0;
845:UrnikXCtoSC.Dan[3].On[1].Ura:=Byte_0;
846:UrnikXCtoSC.Dan[3].On[2].Mna:=Byte_0;
847:UrnikXCtoSC.Dan[3].On[2].Ura:=Byte_0;
848:UrnikXCtoSC.Dan[3].On[3].Mna:=Byte_0;
849:UrnikXCtoSC.Dan[3].On[3].Ura:=Byte_0;
850:UrnikXCtoSC.Dan[4].Off[1].Mna:=Byte_0;
851:UrnikXCtoSC.Dan[4].Off[1].Ura:=Byte_0;
852:UrnikXCtoSC.Dan[4].Off[2].Mna:=Byte_0;
853:UrnikXCtoSC.Dan[4].Off[2].Ura:=Byte_0;
854:UrnikXCtoSC.Dan[4].Off[3].Mna:=Byte_0;
855:UrnikXCtoSC.Dan[4].Off[3].Ura:=Byte_0;
856:UrnikXCtoSC.Dan[4].On[1].Mna:=Byte_0;
857:UrnikXCtoSC.Dan[4].On[1].Ura:=Byte_0;
858:UrnikXCtoSC.Dan[4].On[2].Mna:=Byte_0;
859:UrnikXCtoSC.Dan[4].On[2].Ura:=Byte_0;
860:UrnikXCtoSC.Dan[4].On[3].Mna:=Byte_0;
861:UrnikXCtoSC.Dan[4].On[3].Ura:=Byte_0;
862:UrnikXCtoSC.Dan[5].Off[1].Mna:=Byte_0;
863:UrnikXCtoSC.Dan[5].Off[1].Ura:=Byte_0;
864:UrnikXCtoSC.Dan[5].Off[2].Mna:=Byte_0;
865:UrnikXCtoSC.Dan[5].Off[2].Ura:=Byte_0;
866:UrnikXCtoSC.Dan[5].Off[3].Mna:=Byte_0;
867:UrnikXCtoSC.Dan[5].Off[3].Ura:=Byte_0;
868:UrnikXCtoSC.Dan[5].On[1].Mna:=Byte_0;
869:UrnikXCtoSC.Dan[5].On[1].Ura:=Byte_0;
870:UrnikXCtoSC.Dan[5].On[2].Mna:=Byte_0;
871:UrnikXCtoSC.Dan[5].On[2].Ura:=Byte_0;
872:UrnikXCtoSC.Dan[5].On[3].Mna:=Byte_0;
873:UrnikXCtoSC.Dan[5].On[3].Ura:=Byte_0;
874:UrnikXCtoSC.Dan[6].Off[1].Mna:=Byte_0;
875:UrnikXCtoSC.Dan[6].Off[1].Ura:=Byte_0;
876:UrnikXCtoSC.Dan[6].Off[2].Mna:=Byte_0;
877:UrnikXCtoSC.Dan[6].Off[2].Ura:=Byte_0;
878:UrnikXCtoSC.Dan[6].Off[3].Mna:=Byte_0;
879:UrnikXCtoSC.Dan[6].Off[3].Ura:=Byte_0;
880:UrnikXCtoSC.Dan[6].On[1].Mna:=Byte_0;
881:UrnikXCtoSC.Dan[6].On[1].Ura:=Byte_0;
882:UrnikXCtoSC.Dan[6].On[2].Mna:=Byte_0;
883:UrnikXCtoSC.Dan[6].On[2].Ura:=Byte_0;
884:UrnikXCtoSC.Dan[6].On[3].Mna:=Byte_0;
885:UrnikXCtoSC.Dan[6].On[3].Ura:=Byte_0;
886:UrnikXCtoSC.Dan[7].Off[1].Mna:=Byte_0;
887:UrnikXCtoSC.Dan[7].Off[1].Ura:=Byte_0;
888:UrnikXCtoSC.Dan[7].Off[2].Mna:=Byte_0;
889:UrnikXCtoSC.Dan[7].Off[2].Ura:=Byte_0;
890:UrnikXCtoSC.Dan[7].Off[3].Mna:=Byte_0;
891:UrnikXCtoSC.Dan[7].Off[3].Ura:=Byte_0;
892:UrnikXCtoSC.Dan[7].On[1].Mna:=Byte_0;
893:UrnikXCtoSC.Dan[7].On[1].Ura:=Byte_0;
894:UrnikXCtoSC.Dan[7].On[2].Mna:=Byte_0;
895:UrnikXCtoSC.Dan[7].On[2].Ura:=Byte_0;
896:UrnikXCtoSC.Dan[7].On[3].Mna:=Byte_0;
897:UrnikXCtoSC.Dan[7].On[3].Ura:=Byte_0;
898:UserCurrentLevel:=Byte_0;
899:CrpalkeGrfsGal.AlarmActiveCode:=Word_01;
900:CrpalkeGrfsGal.AlarmCodeLog1:=Word_01;
901:CrpalkeGrfsGal.AlarmCodeLog2:=Word_01;
902:CrpalkeGrfsGal.AlarmCodeLog3:=Word_01;
903:CrpalkeGrfsGal.AlarmCodeLog4:=Word_01;
904:CrpalkeGrfsGal.AlarmCodeLog5:=Word_01;
905:CrpalkeGrfsGal.AlarmGroupXVH[0]:=Word_01;
906:CrpalkeGrfsGal.AlarmGroupXVH[10]:=Word_01;
907:CrpalkeGrfsGal.AlarmGroupXVH[11]:=Word_01;
908:CrpalkeGrfsGal.AlarmGroupXVH[12]:=Word_01;
909:CrpalkeGrfsGal.AlarmGroupXVH[13]:=Word_01;
910:CrpalkeGrfsGal.AlarmGroupXVH[14]:=Word_01;
911:CrpalkeGrfsGal.AlarmGroupXVH[15]:=Word_01;
912:CrpalkeGrfsGal.AlarmGroupXVH[16]:=Word_01;
913:CrpalkeGrfsGal.AlarmGroupXVH[1]:=Word_01;
914:CrpalkeGrfsGal.AlarmGroupXVH[2]:=Word_01;
915:CrpalkeGrfsGal.AlarmGroupXVH[3]:=Word_01;
916:CrpalkeGrfsGal.AlarmGroupXVH[4]:=Word_01;
917:CrpalkeGrfsGal.AlarmGroupXVH[5]:=Word_01;
918:CrpalkeGrfsGal.AlarmGroupXVH[6]:=Word_01;
919:CrpalkeGrfsGal.AlarmGroupXVH[7]:=Word_01;
920:CrpalkeGrfsGal.AlarmGroupXVH[8]:=Word_01;
921:CrpalkeGrfsGal.AlarmGroupXVH[9]:=Word_01;
922:CrpalkeGrfsGal.AlarmQSD1:=Word_01;
923:CrpalkeGrfsGal.AlarmQSD2:=Word_01;
924:CrpalkeGrfsGal.AlarmStart1:=Word_01;
925:CrpalkeGrfsGal.AlarmStart2:=Word_01;
926:CrpalkeGrfsGal.AlarmStop1:=Word_01;
927:CrpalkeGrfsGal.AlarmStop2:=Word_01;
928:CrpalkeGrfsGal.AlarmStop3:=Word_01;
929:CrpalkeGrfsGal.AlarmSurv1:=Word_01;
930:CrpalkeGrfsGal.AlarmSurv2:=Word_01;
931:CrpalkeGrfsGal.ControlSource:=Word_01;
932:CrpalkeGrfsGal.ExternInputSetup:=Word_01;
933:CrpalkeGrfsGal.ExternInputsStatus:=Word_01;
934:CrpalkeGrfsGal.LocalSetupMode1:=Word_01;
935:CrpalkeGrfsGal.PreklopkaMode:=Word_01;
936:CrpalkeGrfsGal.Relay1setup:=Word_01;
937:CrpalkeGrfsGal.RemoteSetupMode1:=Word_01;
938:CrpalkeGrfsGal.StatusCrpalke:=Byte_0;
939:CrpalkeGrfsGal.StatusMode1:=Word_01;
940:CrpalkeGrfsGal.StatusMode1co:=Byte_0;
941:CrpalkeGrfsGal.StatusMode1op:=Byte_0;
942:CrpalkeGrfsGal.StatusMode2:=Word_01;
943:CrpalkeGrfsGal.StatusMode3:=Word_01;
944:CrpGrfsPIDregTN:=Word_01;
945:DateTime.DanVtednu:=Byte_0;
946:LetniCasDatumi[1,1,1]:=Word_01;
947:LetniCasDatumi[1,1,2]:=Word_01;
948:LetniCasDatumi[1,2,1]:=Word_01;
949:LetniCasDatumi[1,2,2]:=Word_01;
950:LetniCasDatumi[1,3,1]:=Word_01;
951:LetniCasDatumi[1,3,2]:=Word_01;
952:LetniCasDatumi[1,4,1]:=Word_01;
953:LetniCasDatumi[1,4,2]:=Word_01;
954:LetniCasDatumi[2,1,1]:=Word_01;
955:LetniCasDatumi[2,1,2]:=Word_01;
956:LetniCasDatumi[2,2,1]:=Word_01;
957:LetniCasDatumi[2,2,2]:=Word_01;
958:LetniCasDatumi[2,3,1]:=Word_01;
959:LetniCasDatumi[2,3,2]:=Word_01;
960:LetniCasDatumi[2,4,1]:=Word_01;
961:LetniCasDatumi[2,4,2]:=Word_01;
962:UrnikSave.Dan[1].Off[1].Mna:=Byte_0;
963:UrnikSave.Dan[1].Off[1].Ura:=Byte_0;
964:UrnikSave.Dan[1].Off[2].Mna:=Byte_0;
965:UrnikSave.Dan[1].Off[2].Ura:=Byte_0;
966:UrnikSave.Dan[1].Off[3].Mna:=Byte_0;
967:UrnikSave.Dan[1].Off[3].Ura:=Byte_0;
968:UrnikSave.Dan[1].On[1].Mna:=Byte_0;
969:UrnikSave.Dan[1].On[1].Ura:=Byte_0;
970:UrnikSave.Dan[1].On[2].Mna:=Byte_0;
971:UrnikSave.Dan[1].On[2].Ura:=Byte_0;
972:UrnikSave.Dan[1].On[3].Mna:=Byte_0;
973:UrnikSave.Dan[1].On[3].Ura:=Byte_0;
974:UrnikSave.Dan[2].Off[1].Mna:=Byte_0;
975:UrnikSave.Dan[2].Off[1].Ura:=Byte_0;
976:UrnikSave.Dan[2].Off[2].Mna:=Byte_0;
977:UrnikSave.Dan[2].Off[2].Ura:=Byte_0;
978:UrnikSave.Dan[2].Off[3].Mna:=Byte_0;
979:UrnikSave.Dan[2].Off[3].Ura:=Byte_0;
980:UrnikSave.Dan[2].On[1].Mna:=Byte_0;
981:UrnikSave.Dan[2].On[1].Ura:=Byte_0;
982:UrnikSave.Dan[2].On[2].Mna:=Byte_0;
983:UrnikSave.Dan[2].On[2].Ura:=Byte_0;
984:UrnikSave.Dan[2].On[3].Mna:=Byte_0;
985:UrnikSave.Dan[2].On[3].Ura:=Byte_0;
986:UrnikSave.Dan[3].Off[1].Mna:=Byte_0;
987:UrnikSave.Dan[3].Off[1].Ura:=Byte_0;
988:UrnikSave.Dan[3].Off[2].Mna:=Byte_0;
989:UrnikSave.Dan[3].Off[2].Ura:=Byte_0;
990:UrnikSave.Dan[3].Off[3].Mna:=Byte_0;
991:UrnikSave.Dan[3].Off[3].Ura:=Byte_0;
992:UrnikSave.Dan[3].On[1].Mna:=Byte_0;
993:UrnikSave.Dan[3].On[1].Ura:=Byte_0;
994:UrnikSave.Dan[3].On[2].Mna:=Byte_0;
995:UrnikSave.Dan[3].On[2].Ura:=Byte_0;
996:UrnikSave.Dan[3].On[3].Mna:=Byte_0;
997:UrnikSave.Dan[3].On[3].Ura:=Byte_0;
998:UrnikSave.Dan[4].Off[1].Mna:=Byte_0;
999:UrnikSave.Dan[4].Off[1].Ura:=Byte_0;
1000:UrnikSave.Dan[4].Off[2].Mna:=Byte_0;
1001:UrnikSave.Dan[4].Off[2].Ura:=Byte_0;
1002:UrnikSave.Dan[4].Off[3].Mna:=Byte_0;
1003:UrnikSave.Dan[4].Off[3].Ura:=Byte_0;
1004:UrnikSave.Dan[4].On[1].Mna:=Byte_0;
1005:UrnikSave.Dan[4].On[1].Ura:=Byte_0;
1006:UrnikSave.Dan[4].On[2].Mna:=Byte_0;
1007:UrnikSave.Dan[4].On[2].Ura:=Byte_0;
1008:UrnikSave.Dan[4].On[3].Mna:=Byte_0;
1009:UrnikSave.Dan[4].On[3].Ura:=Byte_0;
1010:UrnikSave.Dan[5].Off[1].Mna:=Byte_0;
1011:UrnikSave.Dan[5].Off[1].Ura:=Byte_0;
1012:UrnikSave.Dan[5].Off[2].Mna:=Byte_0;
1013:UrnikSave.Dan[5].Off[2].Ura:=Byte_0;
1014:UrnikSave.Dan[5].Off[3].Mna:=Byte_0;
1015:UrnikSave.Dan[5].Off[3].Ura:=Byte_0;
1016:UrnikSave.Dan[5].On[1].Mna:=Byte_0;
1017:UrnikSave.Dan[5].On[1].Ura:=Byte_0;
1018:UrnikSave.Dan[5].On[2].Mna:=Byte_0;
1019:UrnikSave.Dan[5].On[2].Ura:=Byte_0;
1020:UrnikSave.Dan[5].On[3].Mna:=Byte_0;
1021:UrnikSave.Dan[5].On[3].Ura:=Byte_0;
1022:UrnikSave.Dan[6].Off[1].Mna:=Byte_0;
1023:UrnikSave.Dan[6].Off[1].Ura:=Byte_0;
1024:UrnikSave.Dan[6].Off[2].Mna:=Byte_0;
1025:UrnikSave.Dan[6].Off[2].Ura:=Byte_0;
1026:UrnikSave.Dan[6].Off[3].Mna:=Byte_0;
1027:UrnikSave.Dan[6].Off[3].Ura:=Byte_0;
1028:UrnikSave.Dan[6].On[1].Mna:=Byte_0;
1029:UrnikSave.Dan[6].On[1].Ura:=Byte_0;
1030:UrnikSave.Dan[6].On[2].Mna:=Byte_0;
1031:UrnikSave.Dan[6].On[2].Ura:=Byte_0;
1032:UrnikSave.Dan[6].On[3].Mna:=Byte_0;
1033:UrnikSave.Dan[6].On[3].Ura:=Byte_0;
1034:UrnikSave.Dan[7].Off[1].Mna:=Byte_0;
1035:UrnikSave.Dan[7].Off[1].Ura:=Byte_0;
1036:UrnikSave.Dan[7].Off[2].Mna:=Byte_0;
1037:UrnikSave.Dan[7].Off[2].Ura:=Byte_0;
1038:UrnikSave.Dan[7].Off[3].Mna:=Byte_0;
1039:UrnikSave.Dan[7].Off[3].Ura:=Byte_0;
1040:UrnikSave.Dan[7].On[1].Mna:=Byte_0;
1041:UrnikSave.Dan[7].On[1].Ura:=Byte_0;
1042:UrnikSave.Dan[7].On[2].Mna:=Byte_0;
1043:UrnikSave.Dan[7].On[2].Ura:=Byte_0;
1044:UrnikSave.Dan[7].On[3].Mna:=Byte_0;
1045:UrnikSave.Dan[7].On[3].Ura:=Byte_0;
1046:XVH_CircNumber:=Byte_0;
1047:XVH_KompStatus[1]:=Byte_0;
1048:XVH_KompStatus[2]:=Byte_0;
1049:XVH_ReferencaUpper:=Word_01;
1050:XVH_UPSstatus:=Byte_0;
1051:XVH_Urnik.Dan[1].Off[1].Mna:=Byte_0;
1052:XVH_Urnik.Dan[1].Off[1].Ura:=Byte_0;
1053:XVH_Urnik.Dan[1].Off[2].Mna:=Byte_0;
1054:XVH_Urnik.Dan[1].Off[2].Ura:=Byte_0;
1055:XVH_Urnik.Dan[1].Off[3].Mna:=Byte_0;
1056:XVH_Urnik.Dan[1].Off[3].Ura:=Byte_0;
1057:XVH_Urnik.Dan[1].On[1].Mna:=Byte_0;
1058:XVH_Urnik.Dan[1].On[1].Ura:=Byte_0;
1059:XVH_Urnik.Dan[1].On[2].Mna:=Byte_0;
1060:XVH_Urnik.Dan[1].On[2].Ura:=Byte_0;
1061:XVH_Urnik.Dan[1].On[3].Mna:=Byte_0;
1062:XVH_Urnik.Dan[1].On[3].Ura:=Byte_0;
1063:XVH_Urnik.Dan[2].Off[1].Mna:=Byte_0;
1064:XVH_Urnik.Dan[2].Off[1].Ura:=Byte_0;
1065:XVH_Urnik.Dan[2].Off[2].Mna:=Byte_0;
1066:XVH_Urnik.Dan[2].Off[2].Ura:=Byte_0;
1067:XVH_Urnik.Dan[2].Off[3].Mna:=Byte_0;
1068:XVH_Urnik.Dan[2].Off[3].Ura:=Byte_0;
1069:XVH_Urnik.Dan[2].On[1].Mna:=Byte_0;
1070:XVH_Urnik.Dan[2].On[1].Ura:=Byte_0;
1071:XVH_Urnik.Dan[2].On[2].Mna:=Byte_0;
1072:XVH_Urnik.Dan[2].On[2].Ura:=Byte_0;
1073:XVH_Urnik.Dan[2].On[3].Mna:=Byte_0;
1074:XVH_Urnik.Dan[2].On[3].Ura:=Byte_0;
1075:XVH_Urnik.Dan[3].Off[1].Mna:=Byte_0;
1076:XVH_Urnik.Dan[3].Off[1].Ura:=Byte_0;
1077:XVH_Urnik.Dan[3].Off[2].Mna:=Byte_0;
1078:XVH_Urnik.Dan[3].Off[2].Ura:=Byte_0;
1079:XVH_Urnik.Dan[3].Off[3].Mna:=Byte_0;
1080:XVH_Urnik.Dan[3].Off[3].Ura:=Byte_0;
1081:XVH_Urnik.Dan[3].On[1].Mna:=Byte_0;
1082:XVH_Urnik.Dan[3].On[1].Ura:=Byte_0;
1083:XVH_Urnik.Dan[3].On[2].Mna:=Byte_0;
1084:XVH_Urnik.Dan[3].On[2].Ura:=Byte_0;
1085:XVH_Urnik.Dan[3].On[3].Mna:=Byte_0;
1086:XVH_Urnik.Dan[3].On[3].Ura:=Byte_0;
1087:XVH_Urnik.Dan[4].Off[1].Mna:=Byte_0;
1088:XVH_Urnik.Dan[4].Off[1].Ura:=Byte_0;
1089:XVH_Urnik.Dan[4].Off[2].Mna:=Byte_0;
1090:XVH_Urnik.Dan[4].Off[2].Ura:=Byte_0;
1091:XVH_Urnik.Dan[4].Off[3].Mna:=Byte_0;
1092:XVH_Urnik.Dan[4].Off[3].Ura:=Byte_0;
1093:XVH_Urnik.Dan[4].On[1].Mna:=Byte_0;
1094:XVH_Urnik.Dan[4].On[1].Ura:=Byte_0;
1095:XVH_Urnik.Dan[4].On[2].Mna:=Byte_0;
1096:XVH_Urnik.Dan[4].On[2].Ura:=Byte_0;
1097:XVH_Urnik.Dan[4].On[3].Mna:=Byte_0;
1098:XVH_Urnik.Dan[4].On[3].Ura:=Byte_0;
1099:XVH_Urnik.Dan[5].Off[1].Mna:=Byte_0;
1100:XVH_Urnik.Dan[5].Off[1].Ura:=Byte_0;
1101:XVH_Urnik.Dan[5].Off[2].Mna:=Byte_0;
1102:XVH_Urnik.Dan[5].Off[2].Ura:=Byte_0;
1103:XVH_Urnik.Dan[5].Off[3].Mna:=Byte_0;
1104:XVH_Urnik.Dan[5].Off[3].Ura:=Byte_0;
1105:XVH_Urnik.Dan[5].On[1].Mna:=Byte_0;
1106:XVH_Urnik.Dan[5].On[1].Ura:=Byte_0;
1107:XVH_Urnik.Dan[5].On[2].Mna:=Byte_0;
1108:XVH_Urnik.Dan[5].On[2].Ura:=Byte_0;
1109:XVH_Urnik.Dan[5].On[3].Mna:=Byte_0;
1110:XVH_Urnik.Dan[5].On[3].Ura:=Byte_0;
1111:XVH_Urnik.Dan[6].Off[1].Mna:=Byte_0;
1112:XVH_Urnik.Dan[6].Off[1].Ura:=Byte_0;
1113:XVH_Urnik.Dan[6].Off[2].Mna:=Byte_0;
1114:XVH_Urnik.Dan[6].Off[2].Ura:=Byte_0;
1115:XVH_Urnik.Dan[6].Off[3].Mna:=Byte_0;
1116:XVH_Urnik.Dan[6].Off[3].Ura:=Byte_0;
1117:XVH_Urnik.Dan[6].On[1].Mna:=Byte_0;
1118:XVH_Urnik.Dan[6].On[1].Ura:=Byte_0;
1119:XVH_Urnik.Dan[6].On[2].Mna:=Byte_0;
1120:XVH_Urnik.Dan[6].On[2].Ura:=Byte_0;
1121:XVH_Urnik.Dan[6].On[3].Mna:=Byte_0;
1122:XVH_Urnik.Dan[6].On[3].Ura:=Byte_0;
1123:XVH_Urnik.Dan[7].Off[1].Mna:=Byte_0;
1124:XVH_Urnik.Dan[7].Off[1].Ura:=Byte_0;
1125:XVH_Urnik.Dan[7].Off[2].Mna:=Byte_0;
1126:XVH_Urnik.Dan[7].Off[2].Ura:=Byte_0;
1127:XVH_Urnik.Dan[7].Off[3].Mna:=Byte_0;
1128:XVH_Urnik.Dan[7].Off[3].Ura:=Byte_0;
1129:XVH_Urnik.Dan[7].On[1].Mna:=Byte_0;
1130:XVH_Urnik.Dan[7].On[1].Ura:=Byte_0;
1131:XVH_Urnik.Dan[7].On[2].Mna:=Byte_0;
1132:XVH_Urnik.Dan[7].On[2].Ura:=Byte_0;
1133:XVH_Urnik.Dan[7].On[3].Mna:=Byte_0;
1134:XVH_Urnik.Dan[7].On[3].Ura:=Byte_0;
1135:XVH_VentilTYValue[1,1]:=Byte_0;
1136:XVH_VentilTYValue[1,2]:=Byte_0;
1137:XVH_VentilTYValue[2,1]:=Byte_0;
1138:XVH_VentilTYValue[2,2]:=Byte_0;
1139:XVH_VentilTYValue[3,1]:=Byte_0;
1140:XVH_VentilTYValue[3,2]:=Byte_0;
1141:XVH_VentilTYValue[4,1]:=Byte_0;
1142:XVH_VentilTYValue[4,2]:=Byte_0;
1143:XVH_VlazilecStatus[1]:=Byte_0;
1144:XVH_VlazilecStatus[2]:=Byte_0;
1145:XVHnum[10]:=Byte_0;
1146:XVHnum[11]:=Byte_0;
1147:XVHnum[12]:=Byte_0;
1148:XVHnum[13]:=Byte_0;
1149:XVHnum[14]:=Byte_0;
1150:XVHnum[1]:=Byte_0;
1151:XVHnum[2]:=Byte_0;
1152:XVHnum[3]:=Byte_0;
1153:XVHnum[4]:=Byte_0;
1154:XVHnum[5]:=Byte_0;
1155:XVHnum[6]:=Byte_0;
1156:XVHnum[7]:=Byte_0;
1157:XVHnum[8]:=Byte_0;
1158:XVHnum[9]:=Byte_0;
(*Pisanje UINT*)
(**)
8000:kom_nast_cas_izpada:=Word_01;
;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
(*Modbus Slave Example*)
PROGRAM PLC_PRG_modnet
VAR
Slave_Adresa:BYTE:=2;
Slave_Port:INT:=502;
SlaveSetup:MBS_Setup;
SlavePoll:MBS_Poll;
SlaveAnswer:MBS_Answer;
step: USINT;
end :BOOL;
i: INT;
cycle :BOOL := FALSE; (* First cycle *)
OpenDefaultPort: BOOL;
Write_16: BOOL;
Write_15: BOOL;
Write_5: BOOL;
j: INT;
slavepollwOffset_temp: INT;
slaveanswerwCount_temp: INT;
slaveanswerwoffset_temp: INT;
END_VAR
(* @END_DECLARATION := '0' *)
(*Modbus Slave Example*)
IF Write_16=TRUE THEN (**)
FOR j := 0 TO (slaveanswerwCount_temp-1)/15 BY 1 DO (*vpiše se dword, real*)
wStr_0:=mind[slaveanswerwoffset_temp+j];
wStr_1:=mind[slaveanswerwoffset_temp+j+1];
wStr_2 :=mind[slaveanswerwoffset_temp+j+2];
wStr_3:=mind[slaveanswerwoffset_temp+j+3];
wStr_4:=mind[slaveanswerwoffset_temp+j+4];
wStr_5 :=mind[slaveanswerwoffset_temp+j+5];
wStr_6:=mind[slaveanswerwoffset_temp+j+6];
wStr_7:=mind[slaveanswerwoffset_temp+j+7];
wStr_8:=mind[slaveanswerwoffset_temp+j+8];
wStr_9:=mind[slaveanswerwoffset_temp+j+9];
wStr_10:=mind[slaveanswerwoffset_temp+j+10];
wStr_11:=mind[slaveanswerwoffset_temp+j+11];
wStr_12:=mind[slaveanswerwoffset_temp+j+12];
wStr_13:=mind[slaveanswerwoffset_temp+j+13];
wStr_14:=mind[slaveanswerwoffset_temp+j+14];
bStr_29:=0;
mod_Write_String(index:=slaveanswerwoffset_temp+j); (*vpis real in string*)
END_FOR;
FOR j := 1 TO slaveanswerwCount_temp-1 BY 2 DO (*vpiše se dword, real*)
Word_01:=mind[slaveanswerwoffset_temp+j-1];
Word_23:=mind[slaveanswerwoffset_temp+j];
mod_Write_dWord(index:=slaveanswerwoffset_temp+j); (*vpis real in dword*)
END_FOR;
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO (*vpiše se word*)
Word_01:=mind[slaveanswerwoffset_temp+j];
mod_Write_Word(index:=slaveanswerwoffset_temp+j); (*vpis word*)
END_FOR;
Write_16:=FALSE;
END_IF;
IF Write_5=TRUE OR Write_15=TRUE THEN (**)
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO
Bit_0:=mind_bool[slaveanswerwoffset_temp+j];
mod_Write_Bool(index:=slaveanswerwoffset_temp+j); (*vpis spremembe v spremenljivko*)
END_FOR;
Write_5:=FALSE;
Write_15:=FALSE;
END_IF;
(*iz scade ni komande za branje*)
IF Write_16=FALSE AND Write_5=FALSE AND Write_15=FALSE THEN
mod_Read();(*branje spremenljivk za scado*)
END_IF
(*Close all sockets on corresponding event*)
IF cycle = FALSE THEN
SysCallbackRegister(INDEXOF(Callback_Stop),event_stop);
SysCallbackRegister(INDEXOF(Callback_Reset),event_before_reset);
SysCallbackRegister(INDEXOF(Callback_Reset),event_shutdown);
cycle := TRUE;
END_IF
(*Close all connections via application *)
IF end = TRUE THEN
MBS_CloseAllConnections();
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=FALSE); (*Close port*)
step := 0;
END_IF
IF OpenDefaultPort=TRUE THEN
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=TRUE); (*Close port*)
step := 0;
OpenDefaultPort:=FALSE;
END_IF
(* State machine for setup, poll and answer *)
CASE step OF
0:(**)
SlaveSetup.bUnitIdentifier:=Slave_Adresa;(*Subunitnumber*)
slavesetup.wDefaultPort:=Slave_Port;(*Standartport *)
SlaveSetup.xAdditionalPortActive:=FALSE;(*Port opened or closed*)
SlaveSetup.xSecureMode:=FALSE;(*If TRUE only preset IPs are accepted*)
SlaveSetup.tTimeout:=T#3m;(*Timeout if no communication with slave established*)
SlaveSetup(xStrobe:=TRUE);(*Strobe starts function*)
IF slavesetup.xBusy = FALSE THEN
slavesetup(xstrobe := FALSE);
step := 1 ;
END_IF;
1:(**)
SlavePoll(xStrobe:=TRUE);(*Searching for master commands*)
IF NOT SlavePoll.xBusy THEN
step:=2;
SlavePoll(xStrobe:=FALSE);
END_IF;
2:(**)
step:= 1;
CASE SlavePoll.bFunctionCode OF (*Connect accepted pollparameters with answerparameters*)
8:(**)(*Poll answers*)
;
15:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind_bool[slaveanswer.woffset+i] := slavepoll.xarData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.xarData:=slavepoll.xarData;
Write_15:=TRUE;
16:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind[slaveanswer.woffset+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.wardata := slavepoll.warData;
Write_16:=TRUE;
1,2:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slavepoll.wcount-1 BY 1 DO
slaveanswer.xarData[i]:=mind_bool[slavepoll.woffset+i]; (*Read from Data-array*)
END_FOR
3,4:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slaveanswer.wCount-1 BY 1 DO
slaveanswer.warData[i]:=mind[slavepoll.woffset+i];(*Read from Data-array*)
END_FOR
5:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
mind_bool[slavepoll.woffset]:=slavepoll.xarData[0];(*Write to Data-array*)
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.xarData := slavepoll.xardata;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
Write_5:=TRUE;
6:
slaveanswer.bFunctionCode:= slavepoll.bFunctionCode;
mind[slavepoll.woffset]:= slavepoll.warData[0];(*Write to Data-array*)
slaveanswer.wOffset:= slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wardata := slavepoll.wardata;
23:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
FOR i:= 0 TO slavepoll.wCountAdd-1 BY 1 DO
mind[slavepoll.woffsetadd+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
FOR i := 0 TO slavepoll.wCount BY 1 DO
slaveanswer.warData[i] := mind[1+slavepoll.woffset+i];(*Read from Data-array*)
END_FOR;
END_CASE;
IF slavepoll.xAvailable = TRUE THEN
slaveanswer();(*When Data ready, send answer*)
END_IF
END_CASE;
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_dWord : BOOL
VAR_INPUT
dVAR: DWORD;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
DWord_0:=dVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_Real : BOOL
VAR_INPUT
rVAR: REAL;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
Real_0:=rVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_String : BOOL
VAR_INPUT
sVar: STRING;
start:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
String_0:=LEFT (sVar,29);
mind[start]:=wStr_0;
mind[start+1]:=wStr_1;
mind[start+2]:=wStr_2;
mind[start+3]:=wStr_3;
mind[start+4]:=wStr_4;
mind[start+5]:=wStr_5;
mind[start+6]:=wStr_6;
mind[start+7]:=wStr_7;
mind[start+8]:=wStr_8;
mind[start+9]:=wStr_9;
mind[start+10]:=wStr_10;
mind[start+11]:=wStr_11;
mind[start+12]:=wStr_12;
mind[start+13]:=wStr_13;
bStr_29:=0;
mind[start+14]:=wStr_14;
END_FUNCTION
(* @GLOBAL_VARIABLE_LIST := 'Global_Variables_Modnet' *)
(* @PATH := '' *)
(* @SYMFILEFLAGS := '2048' *)
VAR_GLOBAL
(*delovno polje za modnet komunikacijo*)
mind :ARRAY [0..9999] OF WORD;
mind_bool :ARRAY [0..9999] OF BOOL; (*Buffer-Array*)
(*Delovni markerji //*)
Bit_0 AT %MX0.0 : BOOL;
Byte_0 AT %MB0 : BYTE;
Byte_1 AT %MB1 : BYTE;
Byte_2 AT %MB2 : BYTE;
Byte_3 AT %MB3 : BYTE;
Real_0 AT %MR0:REAL;
DWord_0 AT %MD0:DWORD;
Word_01 AT %MW0:WORD;
Word_23 AT %MW2:WORD;
String_0 AT %MW10:STRING;
wStr_0 AT %MW10:WORD;
wStr_1 AT %MW12:WORD;
wStr_2 AT %MW14:WORD;
wStr_3 AT %MW16:WORD;
wStr_4 AT %MW18:WORD;
wStr_5 AT %MW20:WORD;
wStr_6 AT %MW22:WORD;
wStr_7 AT %MW24:WORD;
wStr_8 AT %MW26:WORD;
wStr_9 AT %MW28:WORD;
wStr_10 AT %MW30:WORD;
wStr_11 AT %MW32:WORD;
wStr_12 AT %MW34:WORD;
wStr_13 AT %MW36:WORD;
wStr_14 AT %MW38:WORD;
bStr_00 AT %MB10:BYTE;
bStr_01 AT %MB11:BYTE;
bStr_02 AT %MB12:BYTE;
bStr_03 AT %MB13:BYTE;
bStr_04 AT %MB14:BYTE;
bStr_05 AT %MB15:BYTE;
bStr_06 AT %MB16:BYTE;
bStr_07 AT %MB17:BYTE;
bStr_08 AT %MB18:BYTE;
bStr_09 AT %MB19:BYTE;
bStr_10 AT %MB20:BYTE;
bStr_11 AT %MB21:BYTE;
bStr_12 AT %MB22:BYTE;
bStr_13 AT %MB23:BYTE;
bStr_14 AT %MB24:BYTE;
bStr_15 AT %MB25:BYTE;
bStr_16 AT %MB26:BYTE;
bStr_17 AT %MB27:BYTE;
bStr_18 AT %MB28:BYTE;
bStr_19 AT %MB29:BYTE;
bStr_20 AT %MB30:BYTE;
bStr_21 AT %MB31:BYTE;
bStr_22 AT %MB32:BYTE;
bStr_23 AT %MB33:BYTE;
bStr_24 AT %MB34:BYTE;
bStr_25 AT %MB35:BYTE;
bStr_26 AT %MB36:BYTE;
bStr_27 AT %MB37:BYTE;
bStr_28 AT %MB38:BYTE;
bStr_29 AT %MB39:BYTE;
(********************************************)
END_VAR
(* @OBJECT_END := 'Global_Variables_Modnet' *)
(* @CONNECTIONS := Global_Variables_Modnet
FILENAME : ''
FILETIME : 0
EXPORT : 0
NUMOFCONNECTIONS : 0
*)
(*KONEC_KODA*)