## Prva stran
variable | 1474 | 1.KORAK | variable_1 | 2.KORAK | KORAKI!
Device name | Tip | število spremenljivk | Tip (izbrani) | Zamenjaj z | 1.V Sheet "variable" skopiraj vsebino iz variable.dbf - iz Citect SCAD-a projekta, ki ga želiš pretvoriti.
IOD_TIS | BCD | 0 | BCD | INT | 2.V polje A3 vpiši Device ime spremenljivk ki se bodo prenašale preko Modnet protokola
| BYTE | 220 | BYTE | BYTE | 3.V polje A6 vpiši ime krmilnika (npr.:PLC1, če je adresa v spremenljivkah PLC1:.NapakaKoncnega_stikala, drugače pusti polje prazno)
OPC name | DIGITAL | 481 | DIGITAL | DIGITAL | 4. Pritisni gumb 1.KORAK (V poljih C3:C10 se izpiše število spremenljivk, ki imajo Device enak tistemu v polju A3)
TIS | INT | 12 | INT | INT | 5. Pritisni gumb 2.KORAK (V Sheet-u variable_1 se naredi seznam spremenljivk, ki se bodo prenačale preko Modnet protokola)
| LONG | 0 | LONG | LONG | 6. Pritisni gumb 3.KORAK (V poljih C15:C24 se izpiše število spremnljiv po tipih, v poljih F15:F24 se izpiše število potrebni wordow/coilov za prenos spremnljivk)
| REAL | 330 | REAL | REAL | 7. 4.KORAK: V polja C29:C38 je potrebno ročno vpisati začetne naslove spremnljivk. Potrebno je paziti na:
| STRING | 5 | UINT | UINT | *naslov se morajo začeti z lihim številom npr.:1, 101, 551
| UINT | 0 | STRING | STRING | *naslove je potrebno nastaviti tako, da se naslovi sremenljivk ne more prekrivati (naslovi spremenjivk gredo od (začetnega naslova) do (začetnega naslova+število potrebnih wordow))
8. Pritisni gumb 5.KORAK (V Sheet-u variable_2 se naredi seznam spremenljivk, ki so tokrat sortirana po tipih)
9. Pritisni gumb 6.KORAK (V Sheet-u variable_3 se naredi seznam spremenljivk, katerih Device se zamenja z devicom v polju C41)
Trajanje makroja | variable_1 |  |  | 3.KORAK | 10. Pritisni gumb 7.KORAK (V Sheet-u variable_new se generira seznam spremenljivk. To vsebino je potrebno skopirati v variable.dbf)
0 | Tip | število spremenljivk | TIP | št.potrebnih coilov/wordov | *ta korak traja nekoliko dalj časa (odvisno od števila spremenljivk)
| BCD | 0 | BCD | 0 | *če se pojavi težava z adresami ki se začnejo z 0000 (npr.: "00001" se spremeni na "1") je potrebno uporabiti priloženo (prazno) variable.dbf ali v
| BYTE | 0 | BYTE | 0 | ProjectEditoju/VariableTags na poljubni spremenljki nastaviti adreso" 00001"
| DIGITAL | 481 | DIGITAL | 481 (Coil) | 11. Pritisni gumb 8.KORAK in 9.KORAK (V Sheet-u Xsoft se generira koda)
| INT | 232 | INT | 232 (word) | 12. S pritiskom na gumb 10.KORAK se zgenerira EXP koda za Xsoft (Xsoft_EXP)
| LONG | 0 | LONG | 0 (word) | 13. S pritiskom na gumb Save*.EXP se avtomatsko generira datoka *.EXP
| REAL | 330 | REAL | 660 (word)
| STRING | 5 | STRING | 75 (word)
| UINT | 0 | UINT | 0 (word)
POZOR!
*V Sheet-u variable mora biti vsebina skopirana od polja A1 naprej (če je katera vrstica prazna makroji ne bodo delovali pravilno)
*Ena "STRING" spremenljivka zasede 15wordow (to pomeni 29 znakov, 1BYTE=1STRING)
|  | 4.KORAK(vpiši ročno) | variable_2 | 5.KORAK | *Dolžina "STRING" spremenljivk je 29 znakov (lahko tudi več vendar ne z uporabno tega dokumenta in XSoft programa,potrebna je modifikacija makrojev in Xsoft programa)
| Tip | Začetni naslov |  | Sortiraj | *Vsi stringi so enake dolžine (29)
| BCD |  |  | BCD | *"BYTE" spremenljivke se v variable.dbf spremenijo v "INT" (prenašanje posameznih bytov ni mogoče, niti naslavaljanje v citectscadi)
| BYTE |  |  | DIGITAL | *Naslovi spremenljivk se morajo obvezno začeti z lihim naslovom (preizkušeno je z začetnimi naslovi, ki se izpišejo po pritisku na gumb Ponastavi)
| DIGITAL | 1 |  | BYTE | *Z pritiskom na gumb RESET se pobriše vsebina vseh Sheet-ov razen Sheet-a variable (makor reset se izvaja precej časa)
| INT | 1 |  | INT | *makroji ne delujejo pravilno,če je v Sheet-u variable več kot 9999 vrstic oz. spremenljivk (število vseh spremnljivk je prikazano v polju B1)
| LONG | 3001 |  | LONG | *če se vsebine iz variable_new ne gre skpirat v variable.dbf datotek, vsebino skopirajte najprej v *.txt datoteko in nato v variable.dbf
| REAL | 4001 |  | REAL | *v polju A14 na Sheet-u Prva stran se prikazuje število ciklop do konca izvedbe makroja (samo za gumb 7.KORAK)
| STRING | 5001 |  | STRING
| UINT | 6001 |  | UINT
| variable_3 | 6.KORAK | variable_new | 7.KORAK
| New Device name | IOD_TIS_TCP |  | Nova variable dbf
|  |  | xSoft | 8.KORAK in 9.KORAK
xSoft koda
xSoft_EXP
Izvoz*.EXP
1.KORAK
2.KORAK
3.KORAK
5.KORAK
6.KORAK
7.KORAK
8.KORAK
9.KORAK
RESET
Ponastavi
10.KORAK
Save*.EXP

## variable
TISAlarmGenCirc1 | DIGITAL | IOD_TIS | TIS:.AlarmGenCirc1 | [9 empty] | 0x05000010
TISAlarmGenCirc2 | DIGITAL | IOD_TIS | TIS:.AlarmGenCirc2 | [9 empty] | 0x05000020
TISAlarmGenCirc3 | DIGITAL | IOD_TIS | TIS:.AlarmGenCirc3 | [9 empty] | 0x05000030
TISAlarmGenCirc4 | DIGITAL | IOD_TIS | TIS:.AlarmGenCirc4 | [9 empty] | 0x05000040
TISAlarmGenComm | DIGITAL | IOD_TIS | TIS:.AlarmGenComm | [9 empty] | 0x05000050
TISAlarmGenDI | DIGITAL | IOD_TIS | TIS:.AlarmGenDI | [9 empty] | 0x05000060
TISAlarmGenKlima1 | DIGITAL | IOD_TIS | TIS:.AlarmGenKlima1 | [9 empty] | 0x05000070
TISAlarmGenKlima2 | DIGITAL | IOD_TIS | TIS:.AlarmGenKlima2 | [9 empty] | 0x05000080
TISAlarmGenKlima3 | DIGITAL | IOD_TIS | TIS:.AlarmGenKlima3 | [9 empty] | 0x05000090
TISAlarmGenRest | DIGITAL | IOD_TIS | TIS:.AlarmGenRest | [9 empty] | 0x050000a0
TISAlarmGenSenzor | DIGITAL | IOD_TIS | TIS:.AlarmGenSenzor | [9 empty] | 0x050000b0
TISAlarmGenTemp | DIGITAL | IOD_TIS | TIS:.AlarmGenTemp | [9 empty] | 0x050000c0
TISAlarmGenVlPr | DIGITAL | IOD_TIS | TIS:.AlarmGenVlPr | [9 empty] | 0x050000d0
TISAlarmGenVTV | DIGITAL | IOD_TIS | TIS:.AlarmGenVTV | [9 empty] | 0x050000e0
TISCirc1CosFi_III | REAL | IOD_TIS | TIS:.Circ[1].CosFi_III | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-G3]: CosFi III |  |  | 0x050000f0
TISCirc1DelovnaEnergija | REAL | IOD_TIS | TIS:.Circ[1].DelovnaEnergija | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-G3]: DelovnaEnergija |  |  | 0x050000f1
TISCirc1DelovnaMoc_III | REAL | IOD_TIS | TIS:.Circ[1].DelovnaMoc_III | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-G3]: DelovnaMoč III |  |  | 0x050000f2
TISCirc1DelovnaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[1].DelovnaMoc_L1 | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-G3]: DelovnaMoč L1 |  |  | 0x050000f3
TISCirc1DelovnaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[1].DelovnaMoc_L2 | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-G3]: DelovnaMoč L2 |  |  | 0x050000f4
TISCirc1DelovnaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[1].DelovnaMoc_L3 | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-G3]: DelovnaMoč L3 |  |  | 0x050000f5
TISCirc1Frekvenca_L1 | REAL | IOD_TIS | TIS:.Circ[1].Frekvenca_L1 | 0 | 60.0 | 0 | 60.0 | Hz | ##.# | TIS: Analizator[E-G3]: Frekvenca L1 |  |  | 0x050000f6
TISCirc1InduktivnaEnergija | REAL | IOD_TIS | TIS:.Circ[1].InduktivnaEnergija | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-G3]: InduktivnaEnergija |  |  | 0x050000f7
TISCirc1InduktivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[1].InduktivnaMoc_III | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-G3]: InduktivnaMoc III |  |  | 0x050000f8
TISCirc1JalovaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[1].JalovaMoc_L1 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-G3]: JalovaMoč L1 |  |  | 0x050000f9
TISCirc1JalovaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[1].JalovaMoc_L2 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-G3]: JalovaMoč L2 |  |  | 0x050000fa
TISCirc1JalovaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[1].JalovaMoc_L3 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-G3]: JalovaMoc L3 |  |  | 0x050000fb
TISCirc1KapacitivnaEnergija | REAL | IOD_TIS | TIS:.Circ[1].KapacitivnaEnergija | [6 empty] | TIS: Analizator[E-G3]: KapacitivnaEnergija |  |  | 0x050000fc
TISCirc1KapacitivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[1].KapacitivnaMoc_III | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-G3]: KapacitivnaMoc III |  |  | 0x050000fd
TISCirc1MaximumDemand | REAL | IOD_TIS | TIS:.Circ[1].MaximumDemand | 0 | 1200.0 | 0 | 1200.0 | A | ###.# | TIS: Analizator[E-G3]: MaximumDemand |  |  | 0x050000fe
TISCirc1Napetost_L1_L2 | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L1_L2 | 0 | 450.0 | 0 | 450.0 | V | ###.# | TIS: Analizator[E-G3]: Napetost L1-L2 |  |  | 0x050000ff
TISCirc1Napetost_L1_N | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L1_N | 0 | 270.0 | 0 | 270.0 | V | ###.# | TIS: Analizator[E-G3]: Napetost L1-N |  |  | 0x05000100
TISCirc1Napetost_L2_L3 | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L2_L3 | 0 | 450.0 | 0 | 450.0 | V | ###.# | TIS: Analizator[E-G3]: Napetost L2-L3 |  |  | 0x05000101
TISCirc1Napetost_L2_N | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L2_N | 0 | 270.0 | 0 | 270.0 | V | ###.# | TIS: Analizator[E-G3]: Napetost L2-N |  |  | 0x05000102
TISCirc1Napetost_L3_L1 | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L3_L1 | 0 | 450.0 | 0 | 450.0 | V | ###.# | TIS: Analizator[E-G3]: Napetost L3-L1 |  |  | 0x05000103
TISCirc1Napetost_L3_N | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L3_N | 0 | 270.0 | 0 | 270.0 | V | ###.# | TIS: Analizator[E-G3]: Napetost L3-N |  |  | 0x05000104
TISCirc1NavideznaMoc_III | REAL | IOD_TIS | TIS:.Circ[1].NavideznaMoc_III | 0 | 1200.0 | 0 | 1200.0 | kVA | ###.# | TIS: Analizator[E-G3]: NavideznaMoč III |  |  | 0x05000105
TISCirc1NicelniTok | REAL | IOD_TIS | TIS:.Circ[1].NicelniTok | 0 | 1200.0 | 0 | 1200.0 | A | ###.# | TIS: Analizator[E-G3]: NičelniTok |  |  | 0x05000106
TISCirc1PowerFactor_III | REAL | IOD_TIS | TIS:.Circ[1].PowerFactor_III | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-G3]: Faktor moči III |  |  | 0x05000107
TISCirc1PowerFactor_L1 | REAL | IOD_TIS | TIS:.Circ[1].PowerFactor_L1 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-G3]: Faktor moči L1 |  |  | 0x05000108
TISCirc1PowerFactor_L2 | REAL | IOD_TIS | TIS:.Circ[1].PowerFactor_L2 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-G3]: Faktor moči L2 |  |  | 0x05000109
TISCirc1PowerFactor_L3 | REAL | IOD_TIS | TIS:.Circ[1].PowerFactor_L3 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-G3]: Faktor moči L3 |  |  | 0x0500010a
TISCirc1THDI_L1 | REAL | IOD_TIS | TIS:.Circ[1].THDI_L1 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-G3]: THDI L1 |  |  | 0x0500010b
TISCirc1THDI_L2 | REAL | IOD_TIS | TIS:.Circ[1].THDI_L2 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-G3]: THDI L2 |  |  | 0x0500010c
TISCirc1THDI_L3 | REAL | IOD_TIS | TIS:.Circ[1].THDI_L3 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-G3]: THDI L3 |  |  | 0x0500010d
TISCirc1THDV_L1 | REAL | IOD_TIS | TIS:.Circ[1].THDV_L1 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-G3]: THDV L1 |  |  | 0x0500010e
TISCirc1THDV_L2 | REAL | IOD_TIS | TIS:.Circ[1].THDV_L2 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-G3]: THDV L2 |  |  | 0x0500010f
TISCirc1THDV_L3 | REAL | IOD_TIS | TIS:.Circ[1].THDV_L3 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-G3]: THDV L3 |  |  | 0x05000110
TISCirc1Tok_L1 | REAL | IOD_TIS | TIS:.Circ[1].Tok_L1 | 0 | 600.0 | 0 | 600.0 | A | ###.# | TIS: Analizator[E-G3]: Tok L1 |  |  | 0x05000111
TISCirc1Tok_L2 | REAL | IOD_TIS | TIS:.Circ[1].Tok_L2 | 0 | 600.0 | 0 | 600.0 | A | ###.# | TIS: Analizator[E-G3]: Tok L2 |  |  | 0x05000112
TISCirc1Tok_L3 | REAL | IOD_TIS | TIS:.Circ[1].Tok_L3 | 0 | 600.0 | 0 | 600.0 | A | ###.# | TIS: Analizator[E-G3]: Tok L3 |  |  | 0x05000113
TISCirc1TokPovprecje_III | REAL | IOD_TIS | TIS:.Circ[1].TokPovprecje_III | 0 | 600.0 | 0 | 600.0 | A | ###.# | TIS: Analizator[E-G3]: TokPovprecje III |  |  | 0x05000114
TISCirc2CosFi_III | REAL | IOD_TIS | TIS:.Circ[2].CosFi_III | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-DG3]: CosFi III |  |  | 0x05000115
TISCirc2DelovnaEnergija | REAL | IOD_TIS | TIS:.Circ[2].DelovnaEnergija | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-DG3]: DelovnaEnergija |  |  | 0x05000116
TISCirc2DelovnaMoc_III | REAL | IOD_TIS | TIS:.Circ[2].DelovnaMoc_III | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-DG3]: DelovnaMoč III |  |  | 0x05000117
TISCirc2DelovnaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[2].DelovnaMoc_L1 | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-DG3]: DelovnaMoč L1 |  |  | 0x05000118
TISCirc2DelovnaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[2].DelovnaMoc_L2 | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-DG3]: DelovnaMoč L2 |  |  | 0x05000119
TISCirc2DelovnaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[2].DelovnaMoc_L3 | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-DG3]: DelovnaMoč L3 |  |  | 0x0500011a
TISCirc2Frekvenca_L1 | REAL | IOD_TIS | TIS:.Circ[2].Frekvenca_L1 | 0 | 60.0 | 0 | 60.0 | Hz | ##.# | TIS: Analizator[E-DG3]: Frekvenca L1 |  |  | 0x0500011b
TISCirc2InduktivnaEnergija | REAL | IOD_TIS | TIS:.Circ[2].InduktivnaEnergija | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-DG3]: InduktivnaEnergija |  |  | 0x0500011c
TISCirc2InduktivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[2].InduktivnaMoc_III | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-DG3]: InduktivnaMoc III |  |  | 0x0500011d
TISCirc2JalovaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[2].JalovaMoc_L1 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-DG3]: JalovaMoč L1 |  |  | 0x0500011e
TISCirc2JalovaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[2].JalovaMoc_L2 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-DG3]: JalovaMoč L2 |  |  | 0x0500011f
TISCirc2JalovaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[2].JalovaMoc_L3 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-DG3]: JalovaMoc L3 |  |  | 0x05000120
TISCirc2KapacitivnaEnergija | REAL | IOD_TIS | TIS:.Circ[2].KapacitivnaEnergija | [6 empty] | TIS: Analizator[E-DG3]: KapacitivnaEnergija |  |  | 0x05000121
TISCirc2KapacitivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[2].KapacitivnaMoc_III | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-DG3]: KapacitivnaMoc III |  |  | 0x05000122
TISCirc2MaximumDemand | REAL | IOD_TIS | TIS:.Circ[2].MaximumDemand | 0 | 1200.0 | 0 | 1200.0 | A | ###.# | TIS: Analizator[E-DG3]: MaximumDemand |  |  | 0x05000123
TISCirc2Napetost_L1_L2 | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L1_L2 | 0 | 450.0 | 0 | 450.0 | V | ###.# | TIS: Analizator[E-DG3]: Napetost L1-L2 |  |  | 0x05000124
TISCirc2Napetost_L1_N | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L1_N | 0 | 270.0 | 0 | 270.0 | V | ###.# | TIS: Analizator[E-DG3]: Napetost L1-N |  |  | 0x05000125
TISCirc2Napetost_L2_L3 | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L2_L3 | 0 | 450.0 | 0 | 450.0 | V | ###.# | TIS: Analizator[E-DG3]: Napetost L2-L3 |  |  | 0x05000126
TISCirc2Napetost_L2_N | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L2_N | 0 | 270.0 | 0 | 270.0 | V | ###.# | TIS: Analizator[E-DG3]: Napetost L2-N |  |  | 0x05000127
TISCirc2Napetost_L3_L1 | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L3_L1 | 0 | 450.0 | 0 | 450.0 | V | ###.# | TIS: Analizator[E-DG3]: Napetost L3-L1 |  |  | 0x05000128
TISCirc2Napetost_L3_N | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L3_N | 0 | 270.0 | 0 | 270.0 | V | ###.# | TIS: Analizator[E-DG3]: Napetost L3-N |  |  | 0x05000129
TISCirc2NavideznaMoc_III | REAL | IOD_TIS | TIS:.Circ[2].NavideznaMoc_III | 0 | 1200.0 | 0 | 1200.0 | kVA | ###.# | TIS: Analizator[E-DG3]: NavideznaMoč III |  |  | 0x0500012a
TISCirc2NicelniTok | REAL | IOD_TIS | TIS:.Circ[2].NicelniTok | 0 | 1200.0 | 0 | 1200.0 | A | ###.# | TIS: Analizator[E-DG3]: NičelniTok |  |  | 0x0500012b
TISCirc2PowerFactor_III | REAL | IOD_TIS | TIS:.Circ[2].PowerFactor_III | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-DG3]: Faktor moči III |  |  | 0x0500012c
TISCirc2PowerFactor_L1 | REAL | IOD_TIS | TIS:.Circ[2].PowerFactor_L1 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-DG3]: Faktor moči L1 |  |  | 0x0500012d
TISCirc2PowerFactor_L2 | REAL | IOD_TIS | TIS:.Circ[2].PowerFactor_L2 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-DG3]: Faktor moči L2 |  |  | 0x0500012e
TISCirc2PowerFactor_L3 | REAL | IOD_TIS | TIS:.Circ[2].PowerFactor_L3 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-DG3]: Faktor moči L3 |  |  | 0x0500012f
TISCirc2THDI_L1 | REAL | IOD_TIS | TIS:.Circ[2].THDI_L1 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-DG3]: THDI L1 |  |  | 0x05000130
TISCirc2THDI_L2 | REAL | IOD_TIS | TIS:.Circ[2].THDI_L2 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-DG3]: THDI L2 |  |  | 0x05000131
TISCirc2THDI_L3 | REAL | IOD_TIS | TIS:.Circ[2].THDI_L3 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-DG3]: THDI L3 |  |  | 0x05000132
TISCirc2THDV_L1 | REAL | IOD_TIS | TIS:.Circ[2].THDV_L1 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-DG3]: THDV L1 |  |  | 0x05000133
TISCirc2THDV_L2 | REAL | IOD_TIS | TIS:.Circ[2].THDV_L2 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-DG3]: THDV L2 |  |  | 0x05000134
TISCirc2THDV_L3 | REAL | IOD_TIS | TIS:.Circ[2].THDV_L3 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-DG3]: THDV L3 |  |  | 0x05000135
TISCirc2Tok_L1 | REAL | IOD_TIS | TIS:.Circ[2].Tok_L1 | 0 | 600.0 | 0 | 600.0 | A | ###.# | TIS: Analizator[E-DG3]: Tok L1 |  |  | 0x05000136
TISCirc2Tok_L2 | REAL | IOD_TIS | TIS:.Circ[2].Tok_L2 | 0 | 600.0 | 0 | 600.0 | A | ###.# | TIS: Analizator[E-DG3]: Tok L2 |  |  | 0x05000137
TISCirc2Tok_L3 | REAL | IOD_TIS | TIS:.Circ[2].Tok_L3 | 0 | 600.0 | 0 | 600.0 | A | ###.# | TIS: Analizator[E-DG3]: Tok L3 |  |  | 0x05000138
TISCirc2TokPovprecje_III | REAL | IOD_TIS | TIS:.Circ[2].TokPovprecje_III | 0 | 600.0 | 0 | 600.0 | A | ###.# | TIS: Analizator[E-DG3]: TokPovprecje III |  |  | 0x05000139
TISCirc3CosFi_III | REAL | IOD_TIS | TIS:.Circ[3].CosFi_III | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-DG4]: CosFi III |  |  | 0x0500013a
TISCirc3DelovnaEnergija | REAL | IOD_TIS | TIS:.Circ[3].DelovnaEnergija | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-DG4]: DelovnaEnergija |  |  | 0x0500013b
TISCirc3DelovnaMoc_III | REAL | IOD_TIS | TIS:.Circ[3].DelovnaMoc_III | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-DG4]: DelovnaMoč III |  |  | 0x0500013c
TISCirc3DelovnaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[3].DelovnaMoc_L1 | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-DG4]: DelovnaMoč L1 |  |  | 0x0500013d
TISCirc3DelovnaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[3].DelovnaMoc_L2 | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-DG4]: DelovnaMoč L2 |  |  | 0x0500013e
TISCirc3DelovnaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[3].DelovnaMoc_L3 | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-DG4]: DelovnaMoč L3 |  |  | 0x0500013f
TISCirc3Frekvenca_L1 | REAL | IOD_TIS | TIS:.Circ[3].Frekvenca_L1 | 0 | 60.0 | 0 | 60.0 | Hz | ##.# | TIS: Analizator[E-DG4]: Frekvenca L1 |  |  | 0x05000140
TISCirc3InduktivnaEnergija | REAL | IOD_TIS | TIS:.Circ[3].InduktivnaEnergija | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-DG4]: InduktivnaEnergija |  |  | 0x05000141
TISCirc3InduktivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[3].InduktivnaMoc_III | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-DG4]: InduktivnaMoc III |  |  | 0x05000142
TISCirc3JalovaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[3].JalovaMoc_L1 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-DG4]: JalovaMoč L1 |  |  | 0x05000143
TISCirc3JalovaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[3].JalovaMoc_L2 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-DG4]: JalovaMoč L2 |  |  | 0x05000144
TISCirc3JalovaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[3].JalovaMoc_L3 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-DG4]: JalovaMoc L3 |  |  | 0x05000145
TISCirc3KapacitivnaEnergija | REAL | IOD_TIS | TIS:.Circ[3].KapacitivnaEnergija | [6 empty] | TIS: Analizator[E-DG4]: KapacitivnaEnergija |  |  | 0x05000146
TISCirc3KapacitivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[3].KapacitivnaMoc_III | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-DG4]: KapacitivnaMoc III |  |  | 0x05000147
TISCirc3MaximumDemand | REAL | IOD_TIS | TIS:.Circ[3].MaximumDemand | 0 | 1200.0 | 0 | 1200.0 | A | ###.# | TIS: Analizator[E-DG4]: MaximumDemand |  |  | 0x05000148
TISCirc3Napetost_L1_L2 | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L1_L2 | 0 | 450.0 | 0 | 450.0 | V | ###.# | TIS: Analizator[E-DG4]: Napetost L1-L2 |  |  | 0x05000149
TISCirc3Napetost_L1_N | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L1_N | 0 | 270.0 | 0 | 270.0 | V | ###.# | TIS: Analizator[E-DG4]: Napetost L1-N |  |  | 0x0500014a
TISCirc3Napetost_L2_L3 | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L2_L3 | 0 | 450.0 | 0 | 450.0 | V | ###.# | TIS: Analizator[E-DG4]: Napetost L2-L3 |  |  | 0x0500014b
TISCirc3Napetost_L2_N | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L2_N | 0 | 270.0 | 0 | 270.0 | V | ###.# | TIS: Analizator[E-DG4]: Napetost L2-N |  |  | 0x0500014c
TISCirc3Napetost_L3_L1 | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L3_L1 | 0 | 450.0 | 0 | 450.0 | V | ###.# | TIS: Analizator[E-DG4]: Napetost L3-L1 |  |  | 0x0500014d
TISCirc3Napetost_L3_N | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L3_N | 0 | 270.0 | 0 | 270.0 | V | ###.# | TIS: Analizator[E-DG4]: Napetost L3-N |  |  | 0x0500014e
TISCirc3NavideznaMoc_III | REAL | IOD_TIS | TIS:.Circ[3].NavideznaMoc_III | 0 | 1200.0 | 0 | 1200.0 | kVA | ###.# | TIS: Analizator[E-DG4]: NavideznaMoč III |  |  | 0x0500014f
TISCirc3NicelniTok | REAL | IOD_TIS | TIS:.Circ[3].NicelniTok | 0 | 1200.0 | 0 | 1200.0 | A | ###.# | TIS: Analizator[E-DG4]: NičelniTok |  |  | 0x05000150
TISCirc3PowerFactor_III | REAL | IOD_TIS | TIS:.Circ[3].PowerFactor_III | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-DG4]: Faktor moči III |  |  | 0x05000151
TISCirc3PowerFactor_L1 | REAL | IOD_TIS | TIS:.Circ[3].PowerFactor_L1 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-DG4]: Faktor moči L1 |  |  | 0x05000152
TISCirc3PowerFactor_L2 | REAL | IOD_TIS | TIS:.Circ[3].PowerFactor_L2 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-DG4]: Faktor moči L2 |  |  | 0x05000153
TISCirc3PowerFactor_L3 | REAL | IOD_TIS | TIS:.Circ[3].PowerFactor_L3 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-DG4]: Faktor moči L3 |  |  | 0x05000154
TISCirc3THDI_L1 | REAL | IOD_TIS | TIS:.Circ[3].THDI_L1 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-DG4]: THDI L1 |  |  | 0x05000155
TISCirc3THDI_L2 | REAL | IOD_TIS | TIS:.Circ[3].THDI_L2 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-DG4]: THDI L2 |  |  | 0x05000156
TISCirc3THDI_L3 | REAL | IOD_TIS | TIS:.Circ[3].THDI_L3 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-DG4]: THDI L3 |  |  | 0x05000157
TISCirc3THDV_L1 | REAL | IOD_TIS | TIS:.Circ[3].THDV_L1 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-DG4]: THDV L1 |  |  | 0x05000158
TISCirc3THDV_L2 | REAL | IOD_TIS | TIS:.Circ[3].THDV_L2 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-DG4]: THDV L2 |  |  | 0x05000159
TISCirc3THDV_L3 | REAL | IOD_TIS | TIS:.Circ[3].THDV_L3 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-DG4]: THDV L3 |  |  | 0x0500015a
TISCirc3Tok_L1 | REAL | IOD_TIS | TIS:.Circ[3].Tok_L1 | 0 | 600.0 | 0 | 600.0 | A | ###.# | TIS: Analizator[E-DG4]: Tok L1 |  |  | 0x0500015b
TISCirc3Tok_L2 | REAL | IOD_TIS | TIS:.Circ[3].Tok_L2 | 0 | 600.0 | 0 | 600.0 | A | ###.# | TIS: Analizator[E-DG4]: Tok L2 |  |  | 0x0500015c
TISCirc3Tok_L3 | REAL | IOD_TIS | TIS:.Circ[3].Tok_L3 | 0 | 600.0 | 0 | 600.0 | A | ###.# | TIS: Analizator[E-DG4]: Tok L3 |  |  | 0x0500015d
TISCirc3TokPovprecje_III | REAL | IOD_TIS | TIS:.Circ[3].TokPovprecje_III | 0 | 600.0 | 0 | 600.0 | A | ###.# | TIS: Analizator[E-DG4]: TokPovprecje III |  |  | 0x0500015e
TISCirc4CosFi_III | REAL | IOD_TIS | TIS:.Circ[4].CosFi_III | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-UPS3]: CosFi III |  |  | 0x0500015f
TISCirc4DelovnaEnergija | REAL | IOD_TIS | TIS:.Circ[4].DelovnaEnergija | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-UPS3]: DelovnaEnergija |  |  | 0x05000160
TISCirc4DelovnaMoc_III | REAL | IOD_TIS | TIS:.Circ[4].DelovnaMoc_III | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-UPS3]: DelovnaMoč III |  |  | 0x05000161
TISCirc4DelovnaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[4].DelovnaMoc_L1 | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-UPS3]: DelovnaMoč L1 |  |  | 0x05000162
TISCirc4DelovnaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[4].DelovnaMoc_L2 | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-UPS3]: DelovnaMoč L2 |  |  | 0x05000163
TISCirc4DelovnaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[4].DelovnaMoc_L3 | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-UPS3]: DelovnaMoč L3 |  |  | 0x05000164
TISCirc4Frekvenca_L1 | REAL | IOD_TIS | TIS:.Circ[4].Frekvenca_L1 | 0 | 60.0 | 0 | 60.0 | Hz | ##.# | TIS: Analizator[E-UPS3]: Frekvenca L1 |  |  | 0x05000165
TISCirc4InduktivnaEnergija | REAL | IOD_TIS | TIS:.Circ[4].InduktivnaEnergija | 0 | 600.0 | 0 | 600.0 | kW | ###.# | TIS: Analizator[E-UPS3]: InduktivnaEnergija |  |  | 0x05000166
TISCirc4InduktivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[4].InduktivnaMoc_III | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-UPS3]: InduktivnaMoc III |  |  | 0x05000167
TISCirc4JalovaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[4].JalovaMoc_L1 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-UPS3]: JalovaMoč L1 |  |  | 0x05000168
TISCirc4JalovaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[4].JalovaMoc_L2 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-UPS3]: JalovaMoč L2 |  |  | 0x05000169
TISCirc4JalovaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[4].JalovaMoc_L3 | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-UPS3]: JalovaMoc L3 |  |  | 0x0500016a
TISCirc4KapacitivnaEnergija | REAL | IOD_TIS | TIS:.Circ[4].KapacitivnaEnergija | [6 empty] | TIS: Analizator[E-UPS3]: KapacitivnaEnergija |  |  | 0x0500016b
TISCirc4KapacitivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[4].KapacitivnaMoc_III | 0 | 600.0 | 0 | 600.0 | kVAR | ###.# | TIS: Analizator[E-UPS3]: KapacitivnaMoc III |  |  | 0x0500016c
TISCirc4MaximumDemand | REAL | IOD_TIS | TIS:.Circ[4].MaximumDemand | 0 | 1200.0 | 0 | 1200.0 | A | ###.# | TIS: Analizator[E-UPS3]: MaximumDemand |  |  | 0x0500016d
TISCirc4Napetost_L1_L2 | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L1_L2 | 0 | 450.0 | 0 | 450.0 | V | ###.# | TIS: Analizator[E-UPS3]: Napetost L1-L2 |  |  | 0x0500016e
TISCirc4Napetost_L1_N | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L1_N | 0 | 270.0 | 0 | 270.0 | V | ###.# | TIS: Analizator[E-UPS3]: Napetost L1-N |  |  | 0x0500016f
TISCirc4Napetost_L2_L3 | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L2_L3 | 0 | 450.0 | 0 | 450.0 | V | ###.# | TIS: Analizator[E-UPS3]: Napetost L2-L3 |  |  | 0x05000170
TISCirc4Napetost_L2_N | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L2_N | 0 | 270.0 | 0 | 270.0 | V | ###.# | TIS: Analizator[E-UPS3]: Napetost L2-N |  |  | 0x05000171
TISCirc4Napetost_L3_L1 | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L3_L1 | 0 | 450.0 | 0 | 450.0 | V | ###.# | TIS: Analizator[E-UPS3]: Napetost L3-L1 |  |  | 0x05000172
TISCirc4Napetost_L3_N | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L3_N | 0 | 270.0 | 0 | 270.0 | V | ###.# | TIS: Analizator[E-UPS3]: Napetost L3-N |  |  | 0x05000173
TISCirc4NavideznaMoc_III | REAL | IOD_TIS | TIS:.Circ[4].NavideznaMoc_III | 0 | 1200.0 | 0 | 1200.0 | kVA | ###.# | TIS: Analizator[E-UPS3]: NavideznaMoč III |  |  | 0x05000174
TISCirc4NicelniTok | REAL | IOD_TIS | TIS:.Circ[4].NicelniTok | 0 | 1200.0 | 0 | 1200.0 | A | ###.# | TIS: Analizator[E-UPS3]: NičelniTok |  |  | 0x05000175
TISCirc4PowerFactor_III | REAL | IOD_TIS | TIS:.Circ[4].PowerFactor_III | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-UPS3]: Faktor moči III |  |  | 0x05000176
TISCirc4PowerFactor_L1 | REAL | IOD_TIS | TIS:.Circ[4].PowerFactor_L1 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-UPS3]: Faktor moči L1 |  |  | 0x05000177
TISCirc4PowerFactor_L2 | REAL | IOD_TIS | TIS:.Circ[4].PowerFactor_L2 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-UPS3]: Faktor moči L2 |  |  | 0x05000178
TISCirc4PowerFactor_L3 | REAL | IOD_TIS | TIS:.Circ[4].PowerFactor_L3 | -1.00 | 1.00 | -1.00 | 1.00 |  | ##.## | TIS: Analizator[E-UPS3]: Faktor moči L3 |  |  | 0x05000179
TISCirc4THDI_L1 | REAL | IOD_TIS | TIS:.Circ[4].THDI_L1 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-UPS3]: THDI L1 |  |  | 0x0500017a
TISCirc4THDI_L2 | REAL | IOD_TIS | TIS:.Circ[4].THDI_L2 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-UPS3]: THDI L2 |  |  | 0x0500017b
TISCirc4THDI_L3 | REAL | IOD_TIS | TIS:.Circ[4].THDI_L3 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-UPS3]: THDI L3 |  |  | 0x0500017c
TISCirc4THDV_L1 | REAL | IOD_TIS | TIS:.Circ[4].THDV_L1 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-UPS3]: THDV L1 |  |  | 0x0500017d
TISCirc4THDV_L2 | REAL | IOD_TIS | TIS:.Circ[4].THDV_L2 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-UPS3]: THDV L2 |  |  | 0x0500017e
TISCirc4THDV_L3 | REAL | IOD_TIS | TIS:.Circ[4].THDV_L3 | 0 | 10 | 0 | 10 | % | ###.# | TIS: Analizator[E-UPS3]: THDV L3 |  |  | 0x0500017f
TISCirc4Tok_L1 | REAL | IOD_TIS | TIS:.Circ[4].Tok_L1 | 0 | 600.0 | 0 | 600.0 | A | ###.# | TIS: Analizator[E-UPS3]: Tok L1 |  |  | 0x05000180
TISCirc4Tok_L2 | REAL | IOD_TIS | TIS:.Circ[4].Tok_L2 | 0 | 600.0 | 0 | 600.0 | A | ###.# | TIS: Analizator[E-UPS3]: Tok L2 |  |  | 0x05000181
TISCirc4Tok_L3 | REAL | IOD_TIS | TIS:.Circ[4].Tok_L3 | 0 | 600.0 | 0 | 600.0 | A | ###.# | TIS: Analizator[E-UPS3]: Tok L3 |  |  | 0x05000182
TISCirc4TokPovprecje_III | REAL | IOD_TIS | TIS:.Circ[4].TokPovprecje_III | 0 | 600.0 | 0 | 600.0 | A | ###.# | TIS: Analizator[E-UPS3]: TokPovprecje III |  |  | 0x05000183
TISCircutorCosFi_III | REAL | IOD_TIS | TIS:.Circutor.CosFi_III | [9 empty] | 0x05000184
TISCircutorDelovnaEnergija | REAL | IOD_TIS | TIS:.Circutor.DelovnaEnergija | [9 empty] | 0x05000185
TISCircutorDelovnaMoc_III | REAL | IOD_TIS | TIS:.Circutor.DelovnaMoc_III | [9 empty] | 0x05000186
TISCircutorDelovnaMoc_L1 | REAL | IOD_TIS | TIS:.Circutor.DelovnaMoc_L1 | [9 empty] | 0x05000187
TISCircutorDelovnaMoc_L2 | REAL | IOD_TIS | TIS:.Circutor.DelovnaMoc_L2 | [9 empty] | 0x05000188
TISCircutorDelovnaMoc_L3 | REAL | IOD_TIS | TIS:.Circutor.DelovnaMoc_L3 | [9 empty] | 0x05000189
TISCircutorFrekvenca_L1 | REAL | IOD_TIS | TIS:.Circutor.Frekvenca_L1 | [9 empty] | 0x0500018a
TISCircutorInduktivnaEnergija | REAL | IOD_TIS | TIS:.Circutor.InduktivnaEnergija | [9 empty] | 0x0500018b
TISCircutorInduktivnaMoc_III | REAL | IOD_TIS | TIS:.Circutor.InduktivnaMoc_III | [9 empty] | 0x0500018c
TISCircutorJalovaMoc_L1 | REAL | IOD_TIS | TIS:.Circutor.JalovaMoc_L1 | [9 empty] | 0x0500018d
TISCircutorJalovaMoc_L2 | REAL | IOD_TIS | TIS:.Circutor.JalovaMoc_L2 | [9 empty] | 0x0500018e
TISCircutorJalovaMoc_L3 | REAL | IOD_TIS | TIS:.Circutor.JalovaMoc_L3 | [9 empty] | 0x0500018f
TISCircutorKapacitivnaEnergija | REAL | IOD_TIS | TIS:.Circutor.KapacitivnaEnergija | [9 empty] | 0x05000190
TISCircutorKapacitivnaMoc_III | REAL | IOD_TIS | TIS:.Circutor.KapacitivnaMoc_III | [9 empty] | 0x05000191
TISCircutorMaximumDemand | REAL | IOD_TIS | TIS:.Circutor.MaximumDemand | [9 empty] | 0x05000192
TISCircutorNapetost_L1_L2 | REAL | IOD_TIS | TIS:.Circutor.Napetost_L1_L2 | [9 empty] | 0x05000193
TISCircutorNapetost_L1_N | REAL | IOD_TIS | TIS:.Circutor.Napetost_L1_N | [9 empty] | 0x05000194
TISCircutorNapetost_L2_L3 | REAL | IOD_TIS | TIS:.Circutor.Napetost_L2_L3 | [9 empty] | 0x05000195
TISCircutorNapetost_L2_N | REAL | IOD_TIS | TIS:.Circutor.Napetost_L2_N | [9 empty] | 0x05000196
TISCircutorNapetost_L3_L1 | REAL | IOD_TIS | TIS:.Circutor.Napetost_L3_L1 | [9 empty] | 0x05000197
TISCircutorNapetost_L3_N | REAL | IOD_TIS | TIS:.Circutor.Napetost_L3_N | [9 empty] | 0x05000198
TISCircutorNavideznaMoc_III | REAL | IOD_TIS | TIS:.Circutor.NavideznaMoc_III | [9 empty] | 0x05000199
TISCircutorNicelniTok | REAL | IOD_TIS | TIS:.Circutor.NicelniTok | [9 empty] | 0x0500019a
TISCircutorPowerFactor_III | REAL | IOD_TIS | TIS:.Circutor.PowerFactor_III | [9 empty] | 0x0500019b
TISCircutorPowerFactor_L1 | REAL | IOD_TIS | TIS:.Circutor.PowerFactor_L1 | [9 empty] | 0x0500019c
TISCircutorPowerFactor_L2 | REAL | IOD_TIS | TIS:.Circutor.PowerFactor_L2 | [9 empty] | 0x0500019d
TISCircutorPowerFactor_L3 | REAL | IOD_TIS | TIS:.Circutor.PowerFactor_L3 | [9 empty] | 0x0500019e
TISCircutorTHDI_L1 | REAL | IOD_TIS | TIS:.Circutor.THDI_L1 | [9 empty] | 0x0500019f
TISCircutorTHDI_L2 | REAL | IOD_TIS | TIS:.Circutor.THDI_L2 | [9 empty] | 0x050001a0
TISCircutorTHDI_L3 | REAL | IOD_TIS | TIS:.Circutor.THDI_L3 | [9 empty] | 0x050001a1
TISCircutorTHDV_L1 | REAL | IOD_TIS | TIS:.Circutor.THDV_L1 | [9 empty] | 0x050001a2
TISCircutorTHDV_L2 | REAL | IOD_TIS | TIS:.Circutor.THDV_L2 | [9 empty] | 0x050001a3
TISCircutorTHDV_L3 | REAL | IOD_TIS | TIS:.Circutor.THDV_L3 | [9 empty] | 0x050001a4
TISCircutorTok_L1 | REAL | IOD_TIS | TIS:.Circutor.Tok_L1 | [9 empty] | 0x050001a5
TISCircutorTok_L2 | REAL | IOD_TIS | TIS:.Circutor.Tok_L2 | [9 empty] | 0x050001a6
TISCircutorTok_L3 | REAL | IOD_TIS | TIS:.Circutor.Tok_L3 | [9 empty] | 0x050001a7
TISCircutorTokPovprecje_III | REAL | IOD_TIS | TIS:.Circutor.TokPovprecje_III | [9 empty] | 0x050001a8
TISComSCADA | DIGITAL | IOD_TIS | TIS:.ComSCADA | [9 empty] | 0x050001b0
TISComSCADA1 | DIGITAL | IOD_TIS | TIS:.ComSCADA1 | [9 empty] | 0x050001c0
TISDate_Time0 | STRING | IOD_TIS | TIS:.Date_Time[0] | [9 empty] | 0x050001d8
TISDate_Time1 | STRING | IOD_TIS | TIS:.Date_Time[1] | [9 empty] | 0x050001d9
TISDate_Time2 | STRING | IOD_TIS | TIS:.Date_Time[2] | [9 empty] | 0x050001da
TISDate_Time3 | STRING | IOD_TIS | TIS:.Date_Time[3] | [9 empty] | 0x050001db
TISDateTimeDan | BYTE | IOD_TIS | TIS:.DateTime.Dan | [9 empty] | 0x050001dc
TISDateTimeLeto | BYTE | IOD_TIS | TIS:.DateTime.Leto | [9 empty] | 0x050001dd
TISDateTimeMesec | BYTE | IOD_TIS | TIS:.DateTime.Mesec | [9 empty] | 0x050001de
TISDateTimeMinuta | BYTE | IOD_TIS | TIS:.DateTime.Minuta | [9 empty] | 0x050001df
TISDateTimeSekunda | BYTE | IOD_TIS | TIS:.DateTime.Sekunda | [9 empty] | 0x050001e0
TISDateTimeUra | BYTE | IOD_TIS | TIS:.DateTime.Ura | [9 empty] | 0x050001e1
TISDI_F1_OdklHlOm1_IZP | DIGITAL | IOD_TIS | TIS:.DI_F1_OdklHlOm1_IZP | [9 empty] | 0x050001f0
TISDI_F1_OdklHlOm1_ON | DIGITAL | IOD_TIS | TIS:.DI_F1_OdklHlOm1_ON | [9 empty] | 0x05000200
TISDI_F2_OdklHlOm2_IZP | DIGITAL | IOD_TIS | TIS:.DI_F2_OdklHlOm2_IZP | [9 empty] | 0x05000210
TISDI_F2_OdklHlOm2_ON | DIGITAL | IOD_TIS | TIS:.DI_F2_OdklHlOm2_ON | [9 empty] | 0x05000220
TISDI_F3_OdklHlOm3_IZP | DIGITAL | IOD_TIS | TIS:.DI_F3_OdklHlOm3_IZP | [9 empty] | 0x05000230
TISDI_F3_OdklHlOm3_ON | DIGITAL | IOD_TIS | TIS:.DI_F3_OdklHlOm3_ON | [9 empty] | 0x05000240
TISDI_F4_OdkPripVode_IZP | DIGITAL | IOD_TIS | TIS:.DI_F4_OdkPripVode_IZP | [9 empty] | 0x05000250
TISDI_F4_OdkPripVode_ON | DIGITAL | IOD_TIS | TIS:.DI_F4_OdkPripVode_ON | [9 empty] | 0x05000260
TISDI_HladOmara1_ERR | DIGITAL | IOD_TIS | TIS:.DI_HladOmara1_ERR | [9 empty] | 0x05000270
TISDI_HladOmara1_ON | DIGITAL | IOD_TIS | TIS:.DI_HladOmara1_ON | [9 empty] | 0x05000280
TISDI_HladOmara2_ERR | DIGITAL | IOD_TIS | TIS:.DI_HladOmara2_ERR | [9 empty] | 0x05000290
TISDI_HladOmara2_ON | DIGITAL | IOD_TIS | TIS:.DI_HladOmara2_ON | [9 empty] | 0x050002a0
TISDI_HladOmara3_ERR | DIGITAL | IOD_TIS | TIS:.DI_HladOmara3_ERR | [9 empty] | 0x050002b0
TISDI_HladOmara3_ON | DIGITAL | IOD_TIS | TIS:.DI_HladOmara3_ON | [9 empty] | 0x050002c0
TISDI_PripVode1_ERR | DIGITAL | IOD_TIS | TIS:.DI_PripVode1_ERR | [9 empty] | 0x050002d0
TISDI_PripVode1_ON | DIGITAL | IOD_TIS | TIS:.DI_PripVode1_ON | [9 empty] | 0x050002e0
TISDI_PripVode2_ERR | DIGITAL | IOD_TIS | TIS:.DI_PripVode2_ERR | [9 empty] | 0x050002f0
TISDI_PripVode2_ON | DIGITAL | IOD_TIS | TIS:.DI_PripVode2_ON | [9 empty] | 0x05000300
TISDI_Q0_DEG3_ON | DIGITAL | IOD_TIS | TIS:.DI_Q0_DEG3_ON | [9 empty] | 0x05000310
TISDI_Q0_EG3_ON | DIGITAL | IOD_TIS | TIS:.DI_Q0_EG3_ON | [9 empty] | 0x05000320
TISDI_Q0_GlavnoStikalo_ON | DIGITAL | IOD_TIS | TIS:.DI_Q0_GlavnoStikalo_ON | [9 empty] | 0x05000330
TISDI_Q0_UPS3_ON | DIGITAL | IOD_TIS | TIS:.DI_Q0_UPS3_ON | [9 empty] | 0x05000340
TISDI_RazlitjeVodeHO1 | DIGITAL | IOD_TIS | TIS:.DI_RazlitjeVodeHO1 | [9 empty] | 0x05000350
TISDI_RazlitjeVodeHO2 | DIGITAL | IOD_TIS | TIS:.DI_RazlitjeVodeHO2 | [9 empty] | 0x05000360
TISDI_RazlitjeVodeHO3 | DIGITAL | IOD_TIS | TIS:.DI_RazlitjeVodeHO3 | [9 empty] | 0x05000370
TISDI_UPS_Alarm | DIGITAL | IOD_TIS | TIS:.DI_UPS_Alarm | [9 empty] | 0x05000380
TISDI_UPS_BatNacin | DIGITAL | IOD_TIS | TIS:.DI_UPS_BatNacin | [9 empty] | 0x05000390
TISDI_UPS_Polnjenje | DIGITAL | IOD_TIS | TIS:.DI_UPS_Polnjenje | [9 empty] | 0x050003a0
TISDI_Vlazilec1_ERR | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec1_ERR | [9 empty] | 0x050003b0
TISDI_Vlazilec1_ON | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec1_ON | [9 empty] | 0x050003c0
TISDI_Vlazilec2_ERR | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec2_ERR | [9 empty] | 0x050003d0
TISDI_Vlazilec2_ON | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec2_ON | [9 empty] | 0x050003e0
TISDI_Vlazilec3_ERR | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec3_ERR | [9 empty] | 0x050003f0
TISDI_Vlazilec3_ON | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec3_ON | [9 empty] | 0x05000400
TISDIN_F1_OdklHlOm1_IZP | DIGITAL | IOD_TIS | TIS:.DIN_F1_OdklHlOm1_IZP | [9 empty] | 0x05000410
TISDIN_F2_OdklHlOm2_IZP | DIGITAL | IOD_TIS | TIS:.DIN_F2_OdklHlOm2_IZP | [9 empty] | 0x05000420
TISDIN_F3_OdklHlOm3_IZP | DIGITAL | IOD_TIS | TIS:.DIN_F3_OdklHlOm3_IZP | [9 empty] | 0x05000430
TISDIN_F4_OdkPripVode_IZP | DIGITAL | IOD_TIS | TIS:.DIN_F4_OdkPripVode_IZP | [9 empty] | 0x05000440
TISDIN_HladOmara1_ERR | DIGITAL | IOD_TIS | TIS:.DIN_HladOmara1_ERR | [9 empty] | 0x05000450
TISDIN_HladOmara2_ERR | DIGITAL | IOD_TIS | TIS:.DIN_HladOmara2_ERR | [9 empty] | 0x05000460
TISDIN_HladOmara3_ERR | DIGITAL | IOD_TIS | TIS:.DIN_HladOmara3_ERR | [9 empty] | 0x05000470
TISDIN_PripVode1_ERR | DIGITAL | IOD_TIS | TIS:.DIN_PripVode1_ERR | [9 empty] | 0x05000480
TISDIN_PripVode2_ERR | DIGITAL | IOD_TIS | TIS:.DIN_PripVode2_ERR | [9 empty] | 0x05000490
TISDIN_Vlazilec1_ERR | DIGITAL | IOD_TIS | TIS:.DIN_Vlazilec1_ERR | [9 empty] | 0x050004a0
TISDIN_Vlazilec2_ERR | DIGITAL | IOD_TIS | TIS:.DIN_Vlazilec2_ERR | [9 empty] | 0x050004b0
TISDIN_Vlazilec3_ERR | DIGITAL | IOD_TIS | TIS:.DIN_Vlazilec3_ERR | [9 empty] | 0x050004c0
TISDO_HladOm1_Izklop | DIGITAL | IOD_TIS | TIS:.DO_HladOm1_Izklop | [9 empty] | 0x050004d0
TISDO_HladOm2_Izklop | DIGITAL | IOD_TIS | TIS:.DO_HladOm2_Izklop | [9 empty] | 0x050004e0
TISDO_HladOm3_Izklop | DIGITAL | IOD_TIS | TIS:.DO_HladOm3_Izklop | [9 empty] | 0x050004f0
TISErrComCirc1 | DIGITAL | IOD_TIS | TIS:.ErrComCirc[1] | [9 empty] | 0x05000500
TISErrComCirc2 | DIGITAL | IOD_TIS | TIS:.ErrComCirc[2] | [9 empty] | 0x05000510
TISErrComCirc3 | DIGITAL | IOD_TIS | TIS:.ErrComCirc[3] | [9 empty] | 0x05000520
TISErrComCirc4 | DIGITAL | IOD_TIS | TIS:.ErrComCirc[4] | [9 empty] | 0x05000530
TISErrComCirc5 | DIGITAL | IOD_TIS | TIS:.ErrComCirc[5] | [9 empty] | 0x05000540
TISErrComKlima1 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[1] | [9 empty] | 0x05000550
TISErrComKlima2 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[2] | [9 empty] | 0x05000560
TISErrComKlima3 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[3] | [9 empty] | 0x05000570
TISErrComKlima4 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[4] | [9 empty] | 0x05000580
TISErrComKlima5 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[5] | [9 empty] | 0x05000590
TISErrComKlima6 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[6] | [9 empty] | 0x050005a0
TISErrCommScada | DIGITAL | IOD_TIS | TIS:.ErrCommScada | [9 empty] | 0x050005b0
TISErrComPanelPLC | DIGITAL | IOD_TIS | TIS:.ErrComPanelPLC | [9 empty] | 0x050005c0
TISErrComPort2 | DIGITAL | IOD_TIS | TIS:.ErrComPort2 | [9 empty] | 0x050005d0
TISErrorComCirc1Code10 | BYTE | IOD_TIS | TIS:.ErrorComCirc[1].Code[10] | [9 empty] | 0x050005e0
TISErrorComCirc1Code11 | BYTE | IOD_TIS | TIS:.ErrorComCirc[1].Code[11] | [9 empty] | 0x050005e1
TISErrorComCirc1Code12 | BYTE | IOD_TIS | TIS:.ErrorComCirc[1].Code[12] | [9 empty] | 0x050005e2
TISErrorComCirc1Code13 | BYTE | IOD_TIS | TIS:.ErrorComCirc[1].Code[13] | [9 empty] | 0x050005e3
TISErrorComCirc1Code14 | BYTE | IOD_TIS | TIS:.ErrorComCirc[1].Code[14] | [9 empty] | 0x050005e4
TISErrorComCirc1Code15 | BYTE | IOD_TIS | TIS:.ErrorComCirc[1].Code[15] | [9 empty] | 0x050005e5
TISErrorComCirc1Code1 | BYTE | IOD_TIS | TIS:.ErrorComCirc[1].Code[1] | [9 empty] | 0x050005e6
TISErrorComCirc1Code2 | BYTE | IOD_TIS | TIS:.ErrorComCirc[1].Code[2] | [9 empty] | 0x050005e7
TISErrorComCirc1Code3 | BYTE | IOD_TIS | TIS:.ErrorComCirc[1].Code[3] | [9 empty] | 0x050005e8
TISErrorComCirc1Code4 | BYTE | IOD_TIS | TIS:.ErrorComCirc[1].Code[4] | [9 empty] | 0x050005e9
TISErrorComCirc1Code5 | BYTE | IOD_TIS | TIS:.ErrorComCirc[1].Code[5] | [9 empty] | 0x050005ea
TISErrorComCirc1Code6 | BYTE | IOD_TIS | TIS:.ErrorComCirc[1].Code[6] | [9 empty] | 0x050005eb
TISErrorComCirc1Code7 | BYTE | IOD_TIS | TIS:.ErrorComCirc[1].Code[7] | [9 empty] | 0x050005ec
TISErrorComCirc1Code8 | BYTE | IOD_TIS | TIS:.ErrorComCirc[1].Code[8] | [9 empty] | 0x050005ed
TISErrorComCirc1Code9 | BYTE | IOD_TIS | TIS:.ErrorComCirc[1].Code[9] | [9 empty] | 0x050005ee
TISErrorComCirc1Error | DIGITAL | IOD_TIS | TIS:.ErrorComCirc[1].Error | [9 empty] | 0x050005f0
TISErrorComCirc1Status | INT | IOD_TIS | TIS:.ErrorComCirc[1].Status | [9 empty] | 0x05000600
TISErrorComCirc2Code10 | BYTE | IOD_TIS | TIS:.ErrorComCirc[2].Code[10] | [9 empty] | 0x05000601
TISErrorComCirc2Code11 | BYTE | IOD_TIS | TIS:.ErrorComCirc[2].Code[11] | [9 empty] | 0x05000602
TISErrorComCirc2Code12 | BYTE | IOD_TIS | TIS:.ErrorComCirc[2].Code[12] | [9 empty] | 0x05000603
TISErrorComCirc2Code13 | BYTE | IOD_TIS | TIS:.ErrorComCirc[2].Code[13] | [9 empty] | 0x05000604
TISErrorComCirc2Code14 | BYTE | IOD_TIS | TIS:.ErrorComCirc[2].Code[14] | [9 empty] | 0x05000605
TISErrorComCirc2Code15 | BYTE | IOD_TIS | TIS:.ErrorComCirc[2].Code[15] | [9 empty] | 0x05000606
TISErrorComCirc2Code1 | BYTE | IOD_TIS | TIS:.ErrorComCirc[2].Code[1] | [9 empty] | 0x05000607
TISErrorComCirc2Code2 | BYTE | IOD_TIS | TIS:.ErrorComCirc[2].Code[2] | [9 empty] | 0x05000608
TISErrorComCirc2Code3 | BYTE | IOD_TIS | TIS:.ErrorComCirc[2].Code[3] | [9 empty] | 0x05000609
TISErrorComCirc2Code4 | BYTE | IOD_TIS | TIS:.ErrorComCirc[2].Code[4] | [9 empty] | 0x0500060a
TISErrorComCirc2Code5 | BYTE | IOD_TIS | TIS:.ErrorComCirc[2].Code[5] | [9 empty] | 0x0500060b
TISErrorComCirc2Code6 | BYTE | IOD_TIS | TIS:.ErrorComCirc[2].Code[6] | [9 empty] | 0x0500060c
TISErrorComCirc2Code7 | BYTE | IOD_TIS | TIS:.ErrorComCirc[2].Code[7] | [9 empty] | 0x0500060d
TISErrorComCirc2Code8 | BYTE | IOD_TIS | TIS:.ErrorComCirc[2].Code[8] | [9 empty] | 0x0500060e
TISErrorComCirc2Code9 | BYTE | IOD_TIS | TIS:.ErrorComCirc[2].Code[9] | [9 empty] | 0x0500060f
TISErrorComCirc2Error | DIGITAL | IOD_TIS | TIS:.ErrorComCirc[2].Error | [9 empty] | 0x05000610
TISErrorComCirc2Status | INT | IOD_TIS | TIS:.ErrorComCirc[2].Status | [9 empty] | 0x05000620
TISErrorComCirc3Code10 | BYTE | IOD_TIS | TIS:.ErrorComCirc[3].Code[10] | [9 empty] | 0x05000621
TISErrorComCirc3Code11 | BYTE | IOD_TIS | TIS:.ErrorComCirc[3].Code[11] | [9 empty] | 0x05000622
TISErrorComCirc3Code12 | BYTE | IOD_TIS | TIS:.ErrorComCirc[3].Code[12] | [9 empty] | 0x05000623
TISErrorComCirc3Code13 | BYTE | IOD_TIS | TIS:.ErrorComCirc[3].Code[13] | [9 empty] | 0x05000624
TISErrorComCirc3Code14 | BYTE | IOD_TIS | TIS:.ErrorComCirc[3].Code[14] | [9 empty] | 0x05000625
TISErrorComCirc3Code15 | BYTE | IOD_TIS | TIS:.ErrorComCirc[3].Code[15] | [9 empty] | 0x05000626
TISErrorComCirc3Code1 | BYTE | IOD_TIS | TIS:.ErrorComCirc[3].Code[1] | [9 empty] | 0x05000627
TISErrorComCirc3Code2 | BYTE | IOD_TIS | TIS:.ErrorComCirc[3].Code[2] | [9 empty] | 0x05000628
TISErrorComCirc3Code3 | BYTE | IOD_TIS | TIS:.ErrorComCirc[3].Code[3] | [9 empty] | 0x05000629
TISErrorComCirc3Code4 | BYTE | IOD_TIS | TIS:.ErrorComCirc[3].Code[4] | [9 empty] | 0x0500062a
TISErrorComCirc3Code5 | BYTE | IOD_TIS | TIS:.ErrorComCirc[3].Code[5] | [9 empty] | 0x0500062b
TISErrorComCirc3Code6 | BYTE | IOD_TIS | TIS:.ErrorComCirc[3].Code[6] | [9 empty] | 0x0500062c
TISErrorComCirc3Code7 | BYTE | IOD_TIS | TIS:.ErrorComCirc[3].Code[7] | [9 empty] | 0x0500062d
TISErrorComCirc3Code8 | BYTE | IOD_TIS | TIS:.ErrorComCirc[3].Code[8] | [9 empty] | 0x0500062e
TISErrorComCirc3Code9 | BYTE | IOD_TIS | TIS:.ErrorComCirc[3].Code[9] | [9 empty] | 0x0500062f
TISErrorComCirc3Error | DIGITAL | IOD_TIS | TIS:.ErrorComCirc[3].Error | [9 empty] | 0x05000630
TISErrorComCirc3Status | INT | IOD_TIS | TIS:.ErrorComCirc[3].Status | [9 empty] | 0x05000640
TISErrorComCirc4Code10 | BYTE | IOD_TIS | TIS:.ErrorComCirc[4].Code[10] | [9 empty] | 0x05000641
TISErrorComCirc4Code11 | BYTE | IOD_TIS | TIS:.ErrorComCirc[4].Code[11] | [9 empty] | 0x05000642
TISErrorComCirc4Code12 | BYTE | IOD_TIS | TIS:.ErrorComCirc[4].Code[12] | [9 empty] | 0x05000643
TISErrorComCirc4Code13 | BYTE | IOD_TIS | TIS:.ErrorComCirc[4].Code[13] | [9 empty] | 0x05000644
TISErrorComCirc4Code14 | BYTE | IOD_TIS | TIS:.ErrorComCirc[4].Code[14] | [9 empty] | 0x05000645
TISErrorComCirc4Code15 | BYTE | IOD_TIS | TIS:.ErrorComCirc[4].Code[15] | [9 empty] | 0x05000646
TISErrorComCirc4Code1 | BYTE | IOD_TIS | TIS:.ErrorComCirc[4].Code[1] | [9 empty] | 0x05000647
TISErrorComCirc4Code2 | BYTE | IOD_TIS | TIS:.ErrorComCirc[4].Code[2] | [9 empty] | 0x05000648
TISErrorComCirc4Code3 | BYTE | IOD_TIS | TIS:.ErrorComCirc[4].Code[3] | [9 empty] | 0x05000649
TISErrorComCirc4Code4 | BYTE | IOD_TIS | TIS:.ErrorComCirc[4].Code[4] | [9 empty] | 0x0500064a
TISErrorComCirc4Code5 | BYTE | IOD_TIS | TIS:.ErrorComCirc[4].Code[5] | [9 empty] | 0x0500064b
TISErrorComCirc4Code6 | BYTE | IOD_TIS | TIS:.ErrorComCirc[4].Code[6] | [9 empty] | 0x0500064c
TISErrorComCirc4Code7 | BYTE | IOD_TIS | TIS:.ErrorComCirc[4].Code[7] | [9 empty] | 0x0500064d
TISErrorComCirc4Code8 | BYTE | IOD_TIS | TIS:.ErrorComCirc[4].Code[8] | [9 empty] | 0x0500064e
TISErrorComCirc4Code9 | BYTE | IOD_TIS | TIS:.ErrorComCirc[4].Code[9] | [9 empty] | 0x0500064f
TISErrorComCirc4Error | DIGITAL | IOD_TIS | TIS:.ErrorComCirc[4].Error | [9 empty] | 0x05000650
TISErrorComCirc4Status | INT | IOD_TIS | TIS:.ErrorComCirc[4].Status | [9 empty] | 0x05000660
TISErrorComCirc5Code10 | BYTE | IOD_TIS | TIS:.ErrorComCirc[5].Code[10] | [9 empty] | 0x05000661
TISErrorComCirc5Code11 | BYTE | IOD_TIS | TIS:.ErrorComCirc[5].Code[11] | [9 empty] | 0x05000662
TISErrorComCirc5Code12 | BYTE | IOD_TIS | TIS:.ErrorComCirc[5].Code[12] | [9 empty] | 0x05000663
TISErrorComCirc5Code13 | BYTE | IOD_TIS | TIS:.ErrorComCirc[5].Code[13] | [9 empty] | 0x05000664
TISErrorComCirc5Code14 | BYTE | IOD_TIS | TIS:.ErrorComCirc[5].Code[14] | [9 empty] | 0x05000665
TISErrorComCirc5Code15 | BYTE | IOD_TIS | TIS:.ErrorComCirc[5].Code[15] | [9 empty] | 0x05000666
TISErrorComCirc5Code1 | BYTE | IOD_TIS | TIS:.ErrorComCirc[5].Code[1] | [9 empty] | 0x05000667
TISErrorComCirc5Code2 | BYTE | IOD_TIS | TIS:.ErrorComCirc[5].Code[2] | [9 empty] | 0x05000668
TISErrorComCirc5Code3 | BYTE | IOD_TIS | TIS:.ErrorComCirc[5].Code[3] | [9 empty] | 0x05000669
TISErrorComCirc5Code4 | BYTE | IOD_TIS | TIS:.ErrorComCirc[5].Code[4] | [9 empty] | 0x0500066a
TISErrorComCirc5Code5 | BYTE | IOD_TIS | TIS:.ErrorComCirc[5].Code[5] | [9 empty] | 0x0500066b
TISErrorComCirc5Code6 | BYTE | IOD_TIS | TIS:.ErrorComCirc[5].Code[6] | [9 empty] | 0x0500066c
TISErrorComCirc5Code7 | BYTE | IOD_TIS | TIS:.ErrorComCirc[5].Code[7] | [9 empty] | 0x0500066d
TISErrorComCirc5Code8 | BYTE | IOD_TIS | TIS:.ErrorComCirc[5].Code[8] | [9 empty] | 0x0500066e
TISErrorComCirc5Code9 | BYTE | IOD_TIS | TIS:.ErrorComCirc[5].Code[9] | [9 empty] | 0x0500066f
TISErrorComCirc5Error | DIGITAL | IOD_TIS | TIS:.ErrorComCirc[5].Error | [9 empty] | 0x05000670
TISErrorComCirc5Status | INT | IOD_TIS | TIS:.ErrorComCirc[5].Status | [9 empty] | 0x05000680
TISErrorComKlima1Code10 | BYTE | IOD_TIS | TIS:.ErrorComKlima[1].Code[10] | [9 empty] | 0x05000681
TISErrorComKlima1Code11 | BYTE | IOD_TIS | TIS:.ErrorComKlima[1].Code[11] | [9 empty] | 0x05000682
TISErrorComKlima1Code12 | BYTE | IOD_TIS | TIS:.ErrorComKlima[1].Code[12] | [9 empty] | 0x05000683
TISErrorComKlima1Code13 | BYTE | IOD_TIS | TIS:.ErrorComKlima[1].Code[13] | [9 empty] | 0x05000684
TISErrorComKlima1Code14 | BYTE | IOD_TIS | TIS:.ErrorComKlima[1].Code[14] | [9 empty] | 0x05000685
TISErrorComKlima1Code15 | BYTE | IOD_TIS | TIS:.ErrorComKlima[1].Code[15] | [9 empty] | 0x05000686
TISErrorComKlima1Code1 | BYTE | IOD_TIS | TIS:.ErrorComKlima[1].Code[1] | [9 empty] | 0x05000687
TISErrorComKlima1Code2 | BYTE | IOD_TIS | TIS:.ErrorComKlima[1].Code[2] | [9 empty] | 0x05000688
TISErrorComKlima1Code3 | BYTE | IOD_TIS | TIS:.ErrorComKlima[1].Code[3] | [9 empty] | 0x05000689
TISErrorComKlima1Code4 | BYTE | IOD_TIS | TIS:.ErrorComKlima[1].Code[4] | [9 empty] | 0x0500068a
TISErrorComKlima1Code5 | BYTE | IOD_TIS | TIS:.ErrorComKlima[1].Code[5] | [9 empty] | 0x0500068b
TISErrorComKlima1Code6 | BYTE | IOD_TIS | TIS:.ErrorComKlima[1].Code[6] | [9 empty] | 0x0500068c
TISErrorComKlima1Code7 | BYTE | IOD_TIS | TIS:.ErrorComKlima[1].Code[7] | [9 empty] | 0x0500068d
TISErrorComKlima1Code8 | BYTE | IOD_TIS | TIS:.ErrorComKlima[1].Code[8] | [9 empty] | 0x0500068e
TISErrorComKlima1Code9 | BYTE | IOD_TIS | TIS:.ErrorComKlima[1].Code[9] | [9 empty] | 0x0500068f
TISErrorComKlima1Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[1].Error | [9 empty] | 0x05000690
TISErrorComKlima1Status | INT | IOD_TIS | TIS:.ErrorComKlima[1].Status | [9 empty] | 0x050006a0
TISErrorComKlima2Code10 | BYTE | IOD_TIS | TIS:.ErrorComKlima[2].Code[10] | [9 empty] | 0x050006a1
TISErrorComKlima2Code11 | BYTE | IOD_TIS | TIS:.ErrorComKlima[2].Code[11] | [9 empty] | 0x050006a2
TISErrorComKlima2Code12 | BYTE | IOD_TIS | TIS:.ErrorComKlima[2].Code[12] | [9 empty] | 0x050006a3
TISErrorComKlima2Code13 | BYTE | IOD_TIS | TIS:.ErrorComKlima[2].Code[13] | [9 empty] | 0x050006a4
TISErrorComKlima2Code14 | BYTE | IOD_TIS | TIS:.ErrorComKlima[2].Code[14] | [9 empty] | 0x050006a5
TISErrorComKlima2Code15 | BYTE | IOD_TIS | TIS:.ErrorComKlima[2].Code[15] | [9 empty] | 0x050006a6
TISErrorComKlima2Code1 | BYTE | IOD_TIS | TIS:.ErrorComKlima[2].Code[1] | [9 empty] | 0x050006a7
TISErrorComKlima2Code2 | BYTE | IOD_TIS | TIS:.ErrorComKlima[2].Code[2] | [9 empty] | 0x050006a8
TISErrorComKlima2Code3 | BYTE | IOD_TIS | TIS:.ErrorComKlima[2].Code[3] | [9 empty] | 0x050006a9
TISErrorComKlima2Code4 | BYTE | IOD_TIS | TIS:.ErrorComKlima[2].Code[4] | [9 empty] | 0x050006aa
TISErrorComKlima2Code5 | BYTE | IOD_TIS | TIS:.ErrorComKlima[2].Code[5] | [9 empty] | 0x050006ab
TISErrorComKlima2Code6 | BYTE | IOD_TIS | TIS:.ErrorComKlima[2].Code[6] | [9 empty] | 0x050006ac
TISErrorComKlima2Code7 | BYTE | IOD_TIS | TIS:.ErrorComKlima[2].Code[7] | [9 empty] | 0x050006ad
TISErrorComKlima2Code8 | BYTE | IOD_TIS | TIS:.ErrorComKlima[2].Code[8] | [9 empty] | 0x050006ae
TISErrorComKlima2Code9 | BYTE | IOD_TIS | TIS:.ErrorComKlima[2].Code[9] | [9 empty] | 0x050006af
TISErrorComKlima2Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[2].Error | [9 empty] | 0x050006b0
TISErrorComKlima2Status | INT | IOD_TIS | TIS:.ErrorComKlima[2].Status | [9 empty] | 0x050006c0
TISErrorComKlima3Code10 | BYTE | IOD_TIS | TIS:.ErrorComKlima[3].Code[10] | [9 empty] | 0x050006c1
TISErrorComKlima3Code11 | BYTE | IOD_TIS | TIS:.ErrorComKlima[3].Code[11] | [9 empty] | 0x050006c2
TISErrorComKlima3Code12 | BYTE | IOD_TIS | TIS:.ErrorComKlima[3].Code[12] | [9 empty] | 0x050006c3
TISErrorComKlima3Code13 | BYTE | IOD_TIS | TIS:.ErrorComKlima[3].Code[13] | [9 empty] | 0x050006c4
TISErrorComKlima3Code14 | BYTE | IOD_TIS | TIS:.ErrorComKlima[3].Code[14] | [9 empty] | 0x050006c5
TISErrorComKlima3Code15 | BYTE | IOD_TIS | TIS:.ErrorComKlima[3].Code[15] | [9 empty] | 0x050006c6
TISErrorComKlima3Code1 | BYTE | IOD_TIS | TIS:.ErrorComKlima[3].Code[1] | [9 empty] | 0x050006c7
TISErrorComKlima3Code2 | BYTE | IOD_TIS | TIS:.ErrorComKlima[3].Code[2] | [9 empty] | 0x050006c8
TISErrorComKlima3Code3 | BYTE | IOD_TIS | TIS:.ErrorComKlima[3].Code[3] | [9 empty] | 0x050006c9
TISErrorComKlima3Code4 | BYTE | IOD_TIS | TIS:.ErrorComKlima[3].Code[4] | [9 empty] | 0x050006ca
TISErrorComKlima3Code5 | BYTE | IOD_TIS | TIS:.ErrorComKlima[3].Code[5] | [9 empty] | 0x050006cb
TISErrorComKlima3Code6 | BYTE | IOD_TIS | TIS:.ErrorComKlima[3].Code[6] | [9 empty] | 0x050006cc
TISErrorComKlima3Code7 | BYTE | IOD_TIS | TIS:.ErrorComKlima[3].Code[7] | [9 empty] | 0x050006cd
TISErrorComKlima3Code8 | BYTE | IOD_TIS | TIS:.ErrorComKlima[3].Code[8] | [9 empty] | 0x050006ce
TISErrorComKlima3Code9 | BYTE | IOD_TIS | TIS:.ErrorComKlima[3].Code[9] | [9 empty] | 0x050006cf
TISErrorComKlima3Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[3].Error | [9 empty] | 0x050006d0
TISErrorComKlima3Status | INT | IOD_TIS | TIS:.ErrorComKlima[3].Status | [9 empty] | 0x050006e0
TISErrorComKlima4Code10 | BYTE | IOD_TIS | TIS:.ErrorComKlima[4].Code[10] | [9 empty] | 0x050006e1
TISErrorComKlima4Code11 | BYTE | IOD_TIS | TIS:.ErrorComKlima[4].Code[11] | [9 empty] | 0x050006e2
TISErrorComKlima4Code12 | BYTE | IOD_TIS | TIS:.ErrorComKlima[4].Code[12] | [9 empty] | 0x050006e3
TISErrorComKlima4Code13 | BYTE | IOD_TIS | TIS:.ErrorComKlima[4].Code[13] | [9 empty] | 0x050006e4
TISErrorComKlima4Code14 | BYTE | IOD_TIS | TIS:.ErrorComKlima[4].Code[14] | [9 empty] | 0x050006e5
TISErrorComKlima4Code15 | BYTE | IOD_TIS | TIS:.ErrorComKlima[4].Code[15] | [9 empty] | 0x050006e6
TISErrorComKlima4Code1 | BYTE | IOD_TIS | TIS:.ErrorComKlima[4].Code[1] | [9 empty] | 0x050006e7
TISErrorComKlima4Code2 | BYTE | IOD_TIS | TIS:.ErrorComKlima[4].Code[2] | [9 empty] | 0x050006e8
TISErrorComKlima4Code3 | BYTE | IOD_TIS | TIS:.ErrorComKlima[4].Code[3] | [9 empty] | 0x050006e9
TISErrorComKlima4Code4 | BYTE | IOD_TIS | TIS:.ErrorComKlima[4].Code[4] | [9 empty] | 0x050006ea
TISErrorComKlima4Code5 | BYTE | IOD_TIS | TIS:.ErrorComKlima[4].Code[5] | [9 empty] | 0x050006eb
TISErrorComKlima4Code6 | BYTE | IOD_TIS | TIS:.ErrorComKlima[4].Code[6] | [9 empty] | 0x050006ec
TISErrorComKlima4Code7 | BYTE | IOD_TIS | TIS:.ErrorComKlima[4].Code[7] | [9 empty] | 0x050006ed
TISErrorComKlima4Code8 | BYTE | IOD_TIS | TIS:.ErrorComKlima[4].Code[8] | [9 empty] | 0x050006ee
TISErrorComKlima4Code9 | BYTE | IOD_TIS | TIS:.ErrorComKlima[4].Code[9] | [9 empty] | 0x050006ef
TISErrorComKlima4Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[4].Error | [9 empty] | 0x050006f0
TISErrorComKlima4Status | INT | IOD_TIS | TIS:.ErrorComKlima[4].Status | [9 empty] | 0x05000700
TISErrorComKlima5Code10 | BYTE | IOD_TIS | TIS:.ErrorComKlima[5].Code[10] | [9 empty] | 0x05000701
TISErrorComKlima5Code11 | BYTE | IOD_TIS | TIS:.ErrorComKlima[5].Code[11] | [9 empty] | 0x05000702
TISErrorComKlima5Code12 | BYTE | IOD_TIS | TIS:.ErrorComKlima[5].Code[12] | [9 empty] | 0x05000703
TISErrorComKlima5Code13 | BYTE | IOD_TIS | TIS:.ErrorComKlima[5].Code[13] | [9 empty] | 0x05000704
TISErrorComKlima5Code14 | BYTE | IOD_TIS | TIS:.ErrorComKlima[5].Code[14] | [9 empty] | 0x05000705
TISErrorComKlima5Code15 | BYTE | IOD_TIS | TIS:.ErrorComKlima[5].Code[15] | [9 empty] | 0x05000706
TISErrorComKlima5Code1 | BYTE | IOD_TIS | TIS:.ErrorComKlima[5].Code[1] | [9 empty] | 0x05000707
TISErrorComKlima5Code2 | BYTE | IOD_TIS | TIS:.ErrorComKlima[5].Code[2] | [9 empty] | 0x05000708
TISErrorComKlima5Code3 | BYTE | IOD_TIS | TIS:.ErrorComKlima[5].Code[3] | [9 empty] | 0x05000709
TISErrorComKlima5Code4 | BYTE | IOD_TIS | TIS:.ErrorComKlima[5].Code[4] | [9 empty] | 0x0500070a
TISErrorComKlima5Code5 | BYTE | IOD_TIS | TIS:.ErrorComKlima[5].Code[5] | [9 empty] | 0x0500070b
TISErrorComKlima5Code6 | BYTE | IOD_TIS | TIS:.ErrorComKlima[5].Code[6] | [9 empty] | 0x0500070c
TISErrorComKlima5Code7 | BYTE | IOD_TIS | TIS:.ErrorComKlima[5].Code[7] | [9 empty] | 0x0500070d
TISErrorComKlima5Code8 | BYTE | IOD_TIS | TIS:.ErrorComKlima[5].Code[8] | [9 empty] | 0x0500070e
TISErrorComKlima5Code9 | BYTE | IOD_TIS | TIS:.ErrorComKlima[5].Code[9] | [9 empty] | 0x0500070f
TISErrorComKlima5Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[5].Error | [9 empty] | 0x05000710
TISErrorComKlima5Status | INT | IOD_TIS | TIS:.ErrorComKlima[5].Status | [9 empty] | 0x05000720
TISErrorComKlima6Code10 | BYTE | IOD_TIS | TIS:.ErrorComKlima[6].Code[10] | [9 empty] | 0x05000721
TISErrorComKlima6Code11 | BYTE | IOD_TIS | TIS:.ErrorComKlima[6].Code[11] | [9 empty] | 0x05000722
TISErrorComKlima6Code12 | BYTE | IOD_TIS | TIS:.ErrorComKlima[6].Code[12] | [9 empty] | 0x05000723
TISErrorComKlima6Code13 | BYTE | IOD_TIS | TIS:.ErrorComKlima[6].Code[13] | [9 empty] | 0x05000724
TISErrorComKlima6Code14 | BYTE | IOD_TIS | TIS:.ErrorComKlima[6].Code[14] | [9 empty] | 0x05000725
TISErrorComKlima6Code15 | BYTE | IOD_TIS | TIS:.ErrorComKlima[6].Code[15] | [9 empty] | 0x05000726
TISErrorComKlima6Code1 | BYTE | IOD_TIS | TIS:.ErrorComKlima[6].Code[1] | [9 empty] | 0x05000727
TISErrorComKlima6Code2 | BYTE | IOD_TIS | TIS:.ErrorComKlima[6].Code[2] | [9 empty] | 0x05000728
TISErrorComKlima6Code3 | BYTE | IOD_TIS | TIS:.ErrorComKlima[6].Code[3] | [9 empty] | 0x05000729
TISErrorComKlima6Code4 | BYTE | IOD_TIS | TIS:.ErrorComKlima[6].Code[4] | [9 empty] | 0x0500072a
TISErrorComKlima6Code5 | BYTE | IOD_TIS | TIS:.ErrorComKlima[6].Code[5] | [9 empty] | 0x0500072b
TISErrorComKlima6Code6 | BYTE | IOD_TIS | TIS:.ErrorComKlima[6].Code[6] | [9 empty] | 0x0500072c
TISErrorComKlima6Code7 | BYTE | IOD_TIS | TIS:.ErrorComKlima[6].Code[7] | [9 empty] | 0x0500072d
TISErrorComKlima6Code8 | BYTE | IOD_TIS | TIS:.ErrorComKlima[6].Code[8] | [9 empty] | 0x0500072e
TISErrorComKlima6Code9 | BYTE | IOD_TIS | TIS:.ErrorComKlima[6].Code[9] | [9 empty] | 0x0500072f
TISErrorComKlima6Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[6].Error | [9 empty] | 0x05000730
TISErrorComKlima6Status | INT | IOD_TIS | TIS:.ErrorComKlima[6].Status | [9 empty] | 0x05000740
TISKlima1AlarmKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[1].AlarmKompresor1 | [9 empty] | 0x05000750
TISKlima1AlarmKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[1].AlarmKompresor2 | [9 empty] | 0x05000760
TISKlima1Deluje | DIGITAL | IOD_TIS | TIS:.Klima[1].Deluje | [9 empty] | 0x05000770
TISKlima1EnergySaving | DIGITAL | IOD_TIS | TIS:.Klima[1].EnergySaving | [9 empty] | 0x05000780
TISKlima1FaultyEPROM | DIGITAL | IOD_TIS | TIS:.Klima[1].FaultyEPROM | [9 empty] | 0x05000790
TISKlima1FenThermalCutout | DIGITAL | IOD_TIS | TIS:.Klima[1].FenThermalCutout | [9 empty] | 0x050007a0
TISKlima1GeneralAlarm | DIGITAL | IOD_TIS | TIS:.Klima[1].GeneralAlarm | [9 empty] | 0x050007b0
TISKlima1GrelecStatus | BYTE | IOD_TIS | TIS:.Klima[1].GrelecStatus | [9 empty] | 0x050007c0
TISKlima1IzhodniVentStatus | BYTE | IOD_TIS | TIS:.Klima[1].IzhodniVentStatus | [9 empty] | 0x050007c1
TISKlima1Kompresor1naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[1].Kompresor1naMejiObrUr | [9 empty] | 0x050007d0
TISKlima1Kompresor2naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[1].Kompresor2naMejiObrUr | [9 empty] | 0x050007e0
TISKlima1KompresorStatus | BYTE | IOD_TIS | TIS:.Klima[1].KompresorStatus | [9 empty] | 0x050007f0
TISKlima1Napaka | DIGITAL | IOD_TIS | TIS:.Klima[1].Napaka | [9 empty] | 0x05000800
TISKlima1NapakaPriPretokuZraka | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaPriPretokuZraka | [9 empty] | 0x05000810
TISKlima1NapakaSenzorPovratVode | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaSenzorPovratVode | [9 empty] | 0x05000820
TISKlima1NapakaSenzorTempIzpiha | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaSenzorTempIzpiha | [9 empty] | 0x05000830
TISKlima1NapakaSenzorTempProstora | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaSenzorTempProstora | [9 empty] | 0x05000840
TISKlima1NapakaSenzorVlaznosti | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaSenzorVlaznosti | [9 empty] | 0x05000850
TISKlima1NapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaSenzorZunanjeTemp | [9 empty] | 0x05000860
TISKlima1NastMaxTemp | REAL | IOD_TIS | TIS:.Klima[1].NastMaxTemp | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05000870
TISKlima1NastMaxVlaznost | REAL | IOD_TIS | TIS:.Klima[1].NastMaxVlaznost | 0 | 100.0 | 0 | 100.0 | % | ##.# |  |  |  | 0x05000871
TISKlima1NastMinTemp | REAL | IOD_TIS | TIS:.Klima[1].NastMinTemp | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05000872
TISKlima1NastMinVlaznost | REAL | IOD_TIS | TIS:.Klima[1].NastMinVlaznost | 0 | 100.0 | 0 | 100.0 | % | ##.# |  |  |  | 0x05000873
TISKlima1NastTempProstora | REAL | IOD_TIS | TIS:.Klima[1].NastTempProstora | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05000874
TISKlima1NastVlaznost | REAL | IOD_TIS | TIS:.Klima[1].NastVlaznost | 0 | 100.0 | 0 | 100.0 | % | ##.# |  |  |  | 0x05000875
TISKlima1NiTokaVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[1].NiTokaVVlazilcu | [9 empty] | 0x05000880
TISKlima1NiVodeVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[1].NiVodeVVlazilcu | [9 empty] | 0x05000890
TISKlima1NizekPritiskKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[1].NizekPritiskKompresor1 | [9 empty] | 0x050008a0
TISKlima1NizekPritiskKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[1].NizekPritiskKompresor2 | [9 empty] | 0x050008b0
TISKlima1NizkaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[1].NizkaTempPovratneVode | [9 empty] | 0x050008c0
TISKlima1NizkaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[1].NizkaTempVProstoru | [9 empty] | 0x050008d0
TISKlima1NizkaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[1].NizkaVlaznost | [9 empty] | 0x050008e0
TISKlima1ObratovalneUre | REAL | IOD_TIS | TIS:.Klima[1].ObratovalneUre | [9 empty] | 0x050008f0
TISKlima1OnOffEnablingBySupervisor | DIGITAL | IOD_TIS | TIS:.Klima[1].OnOffEnablingBySupervisor | [9 empty] | 0x05000900
TISKlima1PozarniAlarm | DIGITAL | IOD_TIS | TIS:.Klima[1].PozarniAlarm | [9 empty] | 0x05000910
TISKlima1Razvlazevanje | DIGITAL | IOD_TIS | TIS:.Klima[1].Razvlazevanje | [9 empty] | 0x05000920
TISKlima1RemoteOFFtoOutput | DIGITAL | IOD_TIS | TIS:.Klima[1].RemoteOFFtoOutput | [9 empty] | 0x05000930
TISKlima1RemoteOnOff | DIGITAL | IOD_TIS | TIS:.Klima[1].RemoteOnOff | [9 empty] | 0x05000940
TISKlima1RocniIzklop | DIGITAL | IOD_TIS | TIS:.Klima[1].RocniIzklop | [9 empty] | 0x05000950
TISKlima1SenzorjiStatus | DIGITAL | IOD_TIS | TIS:.Klima[1].SenzorjiStatus | [9 empty] | 0x05000960
TISKlima1StoppedByAlarms | DIGITAL | IOD_TIS | TIS:.Klima[1].StoppedByAlarms | [9 empty] | 0x05000970
TISKlima1TemperaturaProstora | REAL | IOD_TIS | TIS:.Klima[1].TemperaturaProstora | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05000980
TISKlima1TempIzpihanegaZraka | REAL | IOD_TIS | TIS:.Klima[1].TempIzpihanegaZraka | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05000981
TISKlima1TempPovratneVode | REAL | IOD_TIS | TIS:.Klima[1].TempPovratneVode | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05000982
TISKlima1ThermalCutoutHeater1 | DIGITAL | IOD_TIS | TIS:.Klima[1].ThermalCutoutHeater1 | [9 empty] | 0x05000990
TISKlima1ThermalCutoutHeater2 | DIGITAL | IOD_TIS | TIS:.Klima[1].ThermalCutoutHeater2 | [9 empty] | 0x050009a0
TISKlima1UnitOnOff | DIGITAL | IOD_TIS | TIS:.Klima[1].UnitOnOff | [9 empty] | 0x050009b0
TISKlima1VentilatorNaMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[1].VentilatorNaMejiObrUr | [9 empty] | 0x050009c0
TISKlima1VentilGretjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[1].VentilGretjeOdpiranje | [9 empty] | 0x050009d0
TISKlima1VentilGretjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[1].VentilGretjeZapiranje | [9 empty] | 0x050009e0
TISKlima1VentilHlajenjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[1].VentilHlajenjeOdpiranje | [9 empty] | 0x050009f0
TISKlima1VentilHlajenjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[1].VentilHlajenjeZapiranje | [9 empty] | 0x05000a00
TISKlima1VisokaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[1].VisokaTempPovratneVode | [9 empty] | 0x05000a10
TISKlima1VisokaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[1].VisokaTempVProstoru | [9 empty] | 0x05000a20
TISKlima1VisokaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[1].VisokaVlaznost | [9 empty] | 0x05000a30
TISKlima1VisokTokVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[1].VisokTokVVlazilcu | [9 empty] | 0x05000a40
TISKlima1Vlazenje | DIGITAL | IOD_TIS | TIS:.Klima[1].Vlazenje | [9 empty] | 0x05000a50
TISKlima1VlazilecStatus | BYTE | IOD_TIS | TIS:.Klima[1].VlazilecStatus | [9 empty] | 0x05000a60
TISKlima1VlaznostProstora | REAL | IOD_TIS | TIS:.Klima[1].VlaznostProstora | 0 | 100 | 0 | 100 | % | ## |  |  |  | 0x05000a61
TISKlima1ZamasenFilter | DIGITAL | IOD_TIS | TIS:.Klima[1].ZamasenFilter | [9 empty] | 0x05000a70
TISKlima1ZunanjaTemp | REAL | IOD_TIS | TIS:.Klima[1].ZunanjaTemp | [9 empty] | 0x05000a80
TISKlima2AlarmKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[2].AlarmKompresor1 | [9 empty] | 0x05000a90
TISKlima2AlarmKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[2].AlarmKompresor2 | [9 empty] | 0x05000aa0
TISKlima2Deluje | DIGITAL | IOD_TIS | TIS:.Klima[2].Deluje | [9 empty] | 0x05000ab0
TISKlima2EnergySaving | DIGITAL | IOD_TIS | TIS:.Klima[2].EnergySaving | [9 empty] | 0x05000ac0
TISKlima2FaultyEPROM | DIGITAL | IOD_TIS | TIS:.Klima[2].FaultyEPROM | [9 empty] | 0x05000ad0
TISKlima2FenThermalCutout | DIGITAL | IOD_TIS | TIS:.Klima[2].FenThermalCutout | [9 empty] | 0x05000ae0
TISKlima2GeneralAlarm | DIGITAL | IOD_TIS | TIS:.Klima[2].GeneralAlarm | [9 empty] | 0x05000af0
TISKlima2GrelecStatus | BYTE | IOD_TIS | TIS:.Klima[2].GrelecStatus | [9 empty] | 0x05000b00
TISKlima2IzhodniVentStatus | BYTE | IOD_TIS | TIS:.Klima[2].IzhodniVentStatus | [9 empty] | 0x05000b01
TISKlima2Kompresor1naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[2].Kompresor1naMejiObrUr | [9 empty] | 0x05000b10
TISKlima2Kompresor2naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[2].Kompresor2naMejiObrUr | [9 empty] | 0x05000b20
TISKlima2KompresorStatus | BYTE | IOD_TIS | TIS:.Klima[2].KompresorStatus | [9 empty] | 0x05000b30
TISKlima2Napaka | DIGITAL | IOD_TIS | TIS:.Klima[2].Napaka | [9 empty] | 0x05000b40
TISKlima2NapakaPriPretokuZraka | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaPriPretokuZraka | [9 empty] | 0x05000b50
TISKlima2NapakaSenzorPovratVode | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaSenzorPovratVode | [9 empty] | 0x05000b60
TISKlima2NapakaSenzorTempIzpiha | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaSenzorTempIzpiha | [9 empty] | 0x05000b70
TISKlima2NapakaSenzorTempProstora | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaSenzorTempProstora | [9 empty] | 0x05000b80
TISKlima2NapakaSenzorVlaznosti | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaSenzorVlaznosti | [9 empty] | 0x05000b90
TISKlima2NapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaSenzorZunanjeTemp | [9 empty] | 0x05000ba0
TISKlima2NastMaxTemp | REAL | IOD_TIS | TIS:.Klima[2].NastMaxTemp | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05000bb0
TISKlima2NastMaxVlaznost | REAL | IOD_TIS | TIS:.Klima[2].NastMaxVlaznost | 0 | 100.0 | 0 | 100.0 | % | ##.# |  |  |  | 0x05000bb1
TISKlima2NastMinTemp | REAL | IOD_TIS | TIS:.Klima[2].NastMinTemp | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05000bb2
TISKlima2NastMinVlaznost | REAL | IOD_TIS | TIS:.Klima[2].NastMinVlaznost | 0 | 100.0 | 0 | 100.0 | % | ##.# |  |  |  | 0x05000bb3
TISKlima2NastTempProstora | REAL | IOD_TIS | TIS:.Klima[2].NastTempProstora | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05000bb4
TISKlima2NastVlaznost | REAL | IOD_TIS | TIS:.Klima[2].NastVlaznost | 0 | 100.0 | 0 | 100.0 | % | ##.# |  |  |  | 0x05000bb5
TISKlima2NiTokaVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[2].NiTokaVVlazilcu | [9 empty] | 0x05000bc0
TISKlima2NiVodeVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[2].NiVodeVVlazilcu | [9 empty] | 0x05000bd0
TISKlima2NizekPritiskKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[2].NizekPritiskKompresor1 | [9 empty] | 0x05000be0
TISKlima2NizekPritiskKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[2].NizekPritiskKompresor2 | [9 empty] | 0x05000bf0
TISKlima2NizkaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[2].NizkaTempPovratneVode | [9 empty] | 0x05000c00
TISKlima2NizkaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[2].NizkaTempVProstoru | [9 empty] | 0x05000c10
TISKlima2NizkaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[2].NizkaVlaznost | [9 empty] | 0x05000c20
TISKlima2ObratovalneUre | REAL | IOD_TIS | TIS:.Klima[2].ObratovalneUre | [9 empty] | 0x05000c30
TISKlima2OnOffEnablingBySupervisor | DIGITAL | IOD_TIS | TIS:.Klima[2].OnOffEnablingBySupervisor | [9 empty] | 0x05000c40
TISKlima2PozarniAlarm | DIGITAL | IOD_TIS | TIS:.Klima[2].PozarniAlarm | [9 empty] | 0x05000c50
TISKlima2Razvlazevanje | DIGITAL | IOD_TIS | TIS:.Klima[2].Razvlazevanje | [9 empty] | 0x05000c60
TISKlima2RemoteOFFtoOutput | DIGITAL | IOD_TIS | TIS:.Klima[2].RemoteOFFtoOutput | [9 empty] | 0x05000c70
TISKlima2RemoteOnOff | DIGITAL | IOD_TIS | TIS:.Klima[2].RemoteOnOff | [9 empty] | 0x05000c80
TISKlima2RocniIzklop | DIGITAL | IOD_TIS | TIS:.Klima[2].RocniIzklop | [9 empty] | 0x05000c90
TISKlima2SenzorjiStatus | DIGITAL | IOD_TIS | TIS:.Klima[2].SenzorjiStatus | [9 empty] | 0x05000ca0
TISKlima2StoppedByAlarms | DIGITAL | IOD_TIS | TIS:.Klima[2].StoppedByAlarms | [9 empty] | 0x05000cb0
TISKlima2TemperaturaProstora | REAL | IOD_TIS | TIS:.Klima[2].TemperaturaProstora | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05000cc0
TISKlima2TempIzpihanegaZraka | REAL | IOD_TIS | TIS:.Klima[2].TempIzpihanegaZraka | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05000cc1
TISKlima2TempPovratneVode | REAL | IOD_TIS | TIS:.Klima[2].TempPovratneVode | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05000cc2
TISKlima2ThermalCutoutHeater1 | DIGITAL | IOD_TIS | TIS:.Klima[2].ThermalCutoutHeater1 | [9 empty] | 0x05000cd0
TISKlima2ThermalCutoutHeater2 | DIGITAL | IOD_TIS | TIS:.Klima[2].ThermalCutoutHeater2 | [9 empty] | 0x05000ce0
TISKlima2UnitOnOff | DIGITAL | IOD_TIS | TIS:.Klima[2].UnitOnOff | [9 empty] | 0x05000cf0
TISKlima2VentilatorNaMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[2].VentilatorNaMejiObrUr | [9 empty] | 0x05000d00
TISKlima2VentilGretjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[2].VentilGretjeOdpiranje | [9 empty] | 0x05000d10
TISKlima2VentilGretjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[2].VentilGretjeZapiranje | [9 empty] | 0x05000d20
TISKlima2VentilHlajenjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[2].VentilHlajenjeOdpiranje | [9 empty] | 0x05000d30
TISKlima2VentilHlajenjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[2].VentilHlajenjeZapiranje | [9 empty] | 0x05000d40
TISKlima2VisokaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[2].VisokaTempPovratneVode | [9 empty] | 0x05000d50
TISKlima2VisokaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[2].VisokaTempVProstoru | [9 empty] | 0x05000d60
TISKlima2VisokaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[2].VisokaVlaznost | [9 empty] | 0x05000d70
TISKlima2VisokTokVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[2].VisokTokVVlazilcu | [9 empty] | 0x05000d80
TISKlima2Vlazenje | DIGITAL | IOD_TIS | TIS:.Klima[2].Vlazenje | [9 empty] | 0x05000d90
TISKlima2VlazilecStatus | BYTE | IOD_TIS | TIS:.Klima[2].VlazilecStatus | [9 empty] | 0x05000da0
TISKlima2VlaznostProstora | REAL | IOD_TIS | TIS:.Klima[2].VlaznostProstora | 0 | 100 | 0 | 100 | % | ## |  |  |  | 0x05000da1
TISKlima2ZamasenFilter | DIGITAL | IOD_TIS | TIS:.Klima[2].ZamasenFilter | [9 empty] | 0x05000db0
TISKlima2ZunanjaTemp | REAL | IOD_TIS | TIS:.Klima[2].ZunanjaTemp | [9 empty] | 0x05000dc0
TISKlima3AlarmKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[3].AlarmKompresor1 | [9 empty] | 0x05000dd0
TISKlima3AlarmKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[3].AlarmKompresor2 | [9 empty] | 0x05000de0
TISKlima3Deluje | DIGITAL | IOD_TIS | TIS:.Klima[3].Deluje | [9 empty] | 0x05000df0
TISKlima3EnergySaving | DIGITAL | IOD_TIS | TIS:.Klima[3].EnergySaving | [9 empty] | 0x05000e00
TISKlima3FaultyEPROM | DIGITAL | IOD_TIS | TIS:.Klima[3].FaultyEPROM | [9 empty] | 0x05000e10
TISKlima3FenThermalCutout | DIGITAL | IOD_TIS | TIS:.Klima[3].FenThermalCutout | [9 empty] | 0x05000e20
TISKlima3GeneralAlarm | DIGITAL | IOD_TIS | TIS:.Klima[3].GeneralAlarm | [9 empty] | 0x05000e30
TISKlima3GrelecStatus | BYTE | IOD_TIS | TIS:.Klima[3].GrelecStatus | [9 empty] | 0x05000e40
TISKlima3IzhodniVentStatus | BYTE | IOD_TIS | TIS:.Klima[3].IzhodniVentStatus | [9 empty] | 0x05000e41
TISKlima3Kompresor1naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[3].Kompresor1naMejiObrUr | [9 empty] | 0x05000e50
TISKlima3Kompresor2naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[3].Kompresor2naMejiObrUr | [9 empty] | 0x05000e60
TISKlima3KompresorStatus | BYTE | IOD_TIS | TIS:.Klima[3].KompresorStatus | [9 empty] | 0x05000e70
TISKlima3Napaka | DIGITAL | IOD_TIS | TIS:.Klima[3].Napaka | [9 empty] | 0x05000e80
TISKlima3NapakaPriPretokuZraka | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaPriPretokuZraka | [9 empty] | 0x05000e90
TISKlima3NapakaSenzorPovratVode | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaSenzorPovratVode | [9 empty] | 0x05000ea0
TISKlima3NapakaSenzorTempIzpiha | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaSenzorTempIzpiha | [9 empty] | 0x05000eb0
TISKlima3NapakaSenzorTempProstora | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaSenzorTempProstora | [9 empty] | 0x05000ec0
TISKlima3NapakaSenzorVlaznosti | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaSenzorVlaznosti | [9 empty] | 0x05000ed0
TISKlima3NapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaSenzorZunanjeTemp | [9 empty] | 0x05000ee0
TISKlima3NastMaxTemp | REAL | IOD_TIS | TIS:.Klima[3].NastMaxTemp | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05000ef0
TISKlima3NastMaxVlaznost | REAL | IOD_TIS | TIS:.Klima[3].NastMaxVlaznost | 0 | 100.0 | 0 | 100.0 | % | ##.# |  |  |  | 0x05000ef1
TISKlima3NastMinTemp | REAL | IOD_TIS | TIS:.Klima[3].NastMinTemp | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05000ef2
TISKlima3NastMinVlaznost | REAL | IOD_TIS | TIS:.Klima[3].NastMinVlaznost | 0 | 100.0 | 0 | 100.0 | % | ##.# |  |  |  | 0x05000ef3
TISKlima3NastTempProstora | REAL | IOD_TIS | TIS:.Klima[3].NastTempProstora | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05000ef4
TISKlima3NastVlaznost | REAL | IOD_TIS | TIS:.Klima[3].NastVlaznost | 0 | 100.0 | 0 | 100.0 | % | ##.# |  |  |  | 0x05000ef5
TISKlima3NiTokaVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[3].NiTokaVVlazilcu | [9 empty] | 0x05000f00
TISKlima3NiVodeVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[3].NiVodeVVlazilcu | [9 empty] | 0x05000f10
TISKlima3NizekPritiskKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[3].NizekPritiskKompresor1 | [9 empty] | 0x05000f20
TISKlima3NizekPritiskKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[3].NizekPritiskKompresor2 | [9 empty] | 0x05000f30
TISKlima3NizkaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[3].NizkaTempPovratneVode | [9 empty] | 0x05000f40
TISKlima3NizkaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[3].NizkaTempVProstoru | [9 empty] | 0x05000f50
TISKlima3NizkaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[3].NizkaVlaznost | [9 empty] | 0x05000f60
TISKlima3ObratovalneUre | REAL | IOD_TIS | TIS:.Klima[3].ObratovalneUre | [9 empty] | 0x05000f70
TISKlima3OnOffEnablingBySupervisor | DIGITAL | IOD_TIS | TIS:.Klima[3].OnOffEnablingBySupervisor | [9 empty] | 0x05000f80
TISKlima3PozarniAlarm | DIGITAL | IOD_TIS | TIS:.Klima[3].PozarniAlarm | [9 empty] | 0x05000f90
TISKlima3Razvlazevanje | DIGITAL | IOD_TIS | TIS:.Klima[3].Razvlazevanje | [9 empty] | 0x05000fa0
TISKlima3RemoteOFFtoOutput | DIGITAL | IOD_TIS | TIS:.Klima[3].RemoteOFFtoOutput | [9 empty] | 0x05000fb0
TISKlima3RemoteOnOff | DIGITAL | IOD_TIS | TIS:.Klima[3].RemoteOnOff | [9 empty] | 0x05000fc0
TISKlima3RocniIzklop | DIGITAL | IOD_TIS | TIS:.Klima[3].RocniIzklop | [9 empty] | 0x05000fd0
TISKlima3SenzorjiStatus | DIGITAL | IOD_TIS | TIS:.Klima[3].SenzorjiStatus | [9 empty] | 0x05000fe0
TISKlima3StoppedByAlarms | DIGITAL | IOD_TIS | TIS:.Klima[3].StoppedByAlarms | [9 empty] | 0x05000ff0
TISKlima3TemperaturaProstora | REAL | IOD_TIS | TIS:.Klima[3].TemperaturaProstora | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05001000
TISKlima3TempIzpihanegaZraka | REAL | IOD_TIS | TIS:.Klima[3].TempIzpihanegaZraka | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05001001
TISKlima3TempPovratneVode | REAL | IOD_TIS | TIS:.Klima[3].TempPovratneVode | 0 | 60.0 | 0 | 60.0 | °C | ##.# |  |  |  | 0x05001002
TISKlima3ThermalCutoutHeater1 | DIGITAL | IOD_TIS | TIS:.Klima[3].ThermalCutoutHeater1 | [9 empty] | 0x05001010
TISKlima3ThermalCutoutHeater2 | DIGITAL | IOD_TIS | TIS:.Klima[3].ThermalCutoutHeater2 | [9 empty] | 0x05001020
TISKlima3UnitOnOff | DIGITAL | IOD_TIS | TIS:.Klima[3].UnitOnOff | [9 empty] | 0x05001030
TISKlima3VentilatorNaMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[3].VentilatorNaMejiObrUr | [9 empty] | 0x05001040
TISKlima3VentilGretjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[3].VentilGretjeOdpiranje | [9 empty] | 0x05001050
TISKlima3VentilGretjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[3].VentilGretjeZapiranje | [9 empty] | 0x05001060
TISKlima3VentilHlajenjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[3].VentilHlajenjeOdpiranje | [9 empty] | 0x05001070
TISKlima3VentilHlajenjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[3].VentilHlajenjeZapiranje | [9 empty] | 0x05001080
TISKlima3VisokaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[3].VisokaTempPovratneVode | [9 empty] | 0x05001090
TISKlima3VisokaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[3].VisokaTempVProstoru | [9 empty] | 0x050010a0
TISKlima3VisokaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[3].VisokaVlaznost | [9 empty] | 0x050010b0
TISKlima3VisokTokVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[3].VisokTokVVlazilcu | [9 empty] | 0x050010c0
TISKlima3Vlazenje | DIGITAL | IOD_TIS | TIS:.Klima[3].Vlazenje | [9 empty] | 0x050010d0
TISKlima3VlazilecStatus | BYTE | IOD_TIS | TIS:.Klima[3].VlazilecStatus | [9 empty] | 0x050010e0
TISKlima3VlaznostProstora | REAL | IOD_TIS | TIS:.Klima[3].VlaznostProstora | 0 | 100 | 0 | 100 | % | ## |  |  |  | 0x050010e1
TISKlima3ZamasenFilter | DIGITAL | IOD_TIS | TIS:.Klima[3].ZamasenFilter | [9 empty] | 0x050010f0
TISKlima3ZunanjaTemp | REAL | IOD_TIS | TIS:.Klima[3].ZunanjaTemp | [9 empty] | 0x05001100
TISKlimaAErrors10 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[10] | [9 empty] | 0x05001110
TISKlimaAErrors11 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[11] | [9 empty] | 0x05001120
TISKlimaAErrors12 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[12] | [9 empty] | 0x05001130
TISKlimaAErrors13 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[13] | [9 empty] | 0x05001140
TISKlimaAErrors14 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[14] | [9 empty] | 0x05001150
TISKlimaAErrors15 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[15] | [9 empty] | 0x05001160
TISKlimaAErrors16 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[16] | [9 empty] | 0x05001170
TISKlimaAErrors17 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[17] | [9 empty] | 0x05001180
TISKlimaAErrors18 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[18] | [9 empty] | 0x05001190
TISKlimaAErrors19 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[19] | [9 empty] | 0x050011a0
TISKlimaAErrors1 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[1] | [9 empty] | 0x050011b0
TISKlimaAErrors20 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[20] | [9 empty] | 0x050011c0
TISKlimaAErrors21 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[21] | [9 empty] | 0x050011d0
TISKlimaAErrors22 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[22] | [9 empty] | 0x050011e0
TISKlimaAErrors23 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[23] | [9 empty] | 0x050011f0
TISKlimaAErrors24 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[24] | [9 empty] | 0x05001200
TISKlimaAErrors25 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[25] | [9 empty] | 0x05001210
TISKlimaAErrors26 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[26] | [9 empty] | 0x05001220
TISKlimaAErrors27 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[27] | [9 empty] | 0x05001230
TISKlimaAErrors28 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[28] | [9 empty] | 0x05001240
TISKlimaAErrors29 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[29] | [9 empty] | 0x05001250
TISKlimaAErrors2 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[2] | [9 empty] | 0x05001260
TISKlimaAErrors30 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[30] | [9 empty] | 0x05001270
TISKlimaAErrors31 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[31] | [9 empty] | 0x05001280
TISKlimaAErrors32 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[32] | [9 empty] | 0x05001290
TISKlimaAErrors33 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[33] | [9 empty] | 0x050012a0
TISKlimaAErrors34 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[34] | [9 empty] | 0x050012b0
TISKlimaAErrors35 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[35] | [9 empty] | 0x050012c0
TISKlimaAErrors36 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[36] | [9 empty] | 0x050012d0
TISKlimaAErrors37 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[37] | [9 empty] | 0x050012e0
TISKlimaAErrors38 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[38] | [9 empty] | 0x050012f0
TISKlimaAErrors39 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[39] | [9 empty] | 0x05001300
TISKlimaAErrors3 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[3] | [9 empty] | 0x05001310
TISKlimaAErrors40 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[40] | [9 empty] | 0x05001320
TISKlimaAErrors4 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[4] | [9 empty] | 0x05001330
TISKlimaAErrors5 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[5] | [9 empty] | 0x05001340
TISKlimaAErrors6 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[6] | [9 empty] | 0x05001350
TISKlimaAErrors7 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[7] | [9 empty] | 0x05001360
TISKlimaAErrors8 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[8] | [9 empty] | 0x05001370
TISKlimaAErrors9 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[9] | [9 empty] | 0x05001380
TISKlimaBErrors10 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[10] | [9 empty] | 0x05001390
TISKlimaBErrors11 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[11] | [9 empty] | 0x050013a0
TISKlimaBErrors12 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[12] | [9 empty] | 0x050013b0
TISKlimaBErrors13 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[13] | [9 empty] | 0x050013c0
TISKlimaBErrors14 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[14] | [9 empty] | 0x050013d0
TISKlimaBErrors15 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[15] | [9 empty] | 0x050013e0
TISKlimaBErrors16 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[16] | [9 empty] | 0x050013f0
TISKlimaBErrors17 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[17] | [9 empty] | 0x05001400
TISKlimaBErrors18 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[18] | [9 empty] | 0x05001410
TISKlimaBErrors19 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[19] | [9 empty] | 0x05001420
TISKlimaBErrors1 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[1] | [9 empty] | 0x05001430
TISKlimaBErrors20 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[20] | [9 empty] | 0x05001440
TISKlimaBErrors21 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[21] | [9 empty] | 0x05001450
TISKlimaBErrors22 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[22] | [9 empty] | 0x05001460
TISKlimaBErrors23 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[23] | [9 empty] | 0x05001470
TISKlimaBErrors24 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[24] | [9 empty] | 0x05001480
TISKlimaBErrors25 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[25] | [9 empty] | 0x05001490
TISKlimaBErrors26 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[26] | [9 empty] | 0x050014a0
TISKlimaBErrors27 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[27] | [9 empty] | 0x050014b0
TISKlimaBErrors28 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[28] | [9 empty] | 0x050014c0
TISKlimaBErrors29 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[29] | [9 empty] | 0x050014d0
TISKlimaBErrors2 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[2] | [9 empty] | 0x050014e0
TISKlimaBErrors30 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[30] | [9 empty] | 0x050014f0
TISKlimaBErrors31 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[31] | [9 empty] | 0x05001500
TISKlimaBErrors32 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[32] | [9 empty] | 0x05001510
TISKlimaBErrors33 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[33] | [9 empty] | 0x05001520
TISKlimaBErrors34 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[34] | [9 empty] | 0x05001530
TISKlimaBErrors35 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[35] | [9 empty] | 0x05001540
TISKlimaBErrors36 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[36] | [9 empty] | 0x05001550
TISKlimaBErrors37 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[37] | [9 empty] | 0x05001560
TISKlimaBErrors38 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[38] | [9 empty] | 0x05001570
TISKlimaBErrors39 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[39] | [9 empty] | 0x05001580
TISKlimaBErrors3 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[3] | [9 empty] | 0x05001590
TISKlimaBErrors40 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[40] | [9 empty] | 0x050015a0
TISKlimaBErrors4 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[4] | [9 empty] | 0x050015b0
TISKlimaBErrors5 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[5] | [9 empty] | 0x050015c0
TISKlimaBErrors6 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[6] | [9 empty] | 0x050015d0
TISKlimaBErrors7 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[7] | [9 empty] | 0x050015e0
TISKlimaBErrors8 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[8] | [9 empty] | 0x050015f0
TISKlimaBErrors9 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[9] | [9 empty] | 0x05001600
TISKlimaCErrors10 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[10] | [9 empty] | 0x05001610
TISKlimaCErrors11 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[11] | [9 empty] | 0x05001620
TISKlimaCErrors12 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[12] | [9 empty] | 0x05001630
TISKlimaCErrors13 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[13] | [9 empty] | 0x05001640
TISKlimaCErrors14 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[14] | [9 empty] | 0x05001650
TISKlimaCErrors15 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[15] | [9 empty] | 0x05001660
TISKlimaCErrors16 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[16] | [9 empty] | 0x05001670
TISKlimaCErrors17 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[17] | [9 empty] | 0x05001680
TISKlimaCErrors18 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[18] | [9 empty] | 0x05001690
TISKlimaCErrors19 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[19] | [9 empty] | 0x050016a0
TISKlimaCErrors1 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[1] | [9 empty] | 0x050016b0
TISKlimaCErrors20 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[20] | [9 empty] | 0x050016c0
TISKlimaCErrors21 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[21] | [9 empty] | 0x050016d0
TISKlimaCErrors22 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[22] | [9 empty] | 0x050016e0
TISKlimaCErrors23 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[23] | [9 empty] | 0x050016f0
TISKlimaCErrors24 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[24] | [9 empty] | 0x05001700
TISKlimaCErrors25 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[25] | [9 empty] | 0x05001710
TISKlimaCErrors26 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[26] | [9 empty] | 0x05001720
TISKlimaCErrors27 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[27] | [9 empty] | 0x05001730
TISKlimaCErrors28 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[28] | [9 empty] | 0x05001740
TISKlimaCErrors29 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[29] | [9 empty] | 0x05001750
TISKlimaCErrors2 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[2] | [9 empty] | 0x05001760
TISKlimaCErrors30 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[30] | [9 empty] | 0x05001770
TISKlimaCErrors31 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[31] | [9 empty] | 0x05001780
TISKlimaCErrors32 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[32] | [9 empty] | 0x05001790
TISKlimaCErrors33 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[33] | [9 empty] | 0x050017a0
TISKlimaCErrors34 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[34] | [9 empty] | 0x050017b0
TISKlimaCErrors35 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[35] | [9 empty] | 0x050017c0
TISKlimaCErrors36 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[36] | [9 empty] | 0x050017d0
TISKlimaCErrors37 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[37] | [9 empty] | 0x050017e0
TISKlimaCErrors38 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[38] | [9 empty] | 0x050017f0
TISKlimaCErrors39 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[39] | [9 empty] | 0x05001800
TISKlimaCErrors3 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[3] | [9 empty] | 0x05001810
TISKlimaCErrors40 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[40] | [9 empty] | 0x05001820
TISKlimaCErrors4 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[4] | [9 empty] | 0x05001830
TISKlimaCErrors5 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[5] | [9 empty] | 0x05001840
TISKlimaCErrors6 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[6] | [9 empty] | 0x05001850
TISKlimaCErrors7 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[7] | [9 empty] | 0x05001860
TISKlimaCErrors8 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[8] | [9 empty] | 0x05001870
TISKlimaCErrors9 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[9] | [9 empty] | 0x05001880
TISKlimaGalAlarmKompresor1 | DIGITAL | IOD_TIS | TIS:.KlimaGal.AlarmKompresor1 | [9 empty] | 0x05001890
TISKlimaGalAlarmKompresor2 | DIGITAL | IOD_TIS | TIS:.KlimaGal.AlarmKompresor2 | [9 empty] | 0x050018a0
TISKlimaGalDeluje | DIGITAL | IOD_TIS | TIS:.KlimaGal.Deluje | [9 empty] | 0x050018b0
TISKlimaGalEnergySaving | DIGITAL | IOD_TIS | TIS:.KlimaGal.EnergySaving | [9 empty] | 0x050018c0
TISKlimaGalFaultyEPROM | DIGITAL | IOD_TIS | TIS:.KlimaGal.FaultyEPROM | [9 empty] | 0x050018d0
TISKlimaGalFenThermalCutout | DIGITAL | IOD_TIS | TIS:.KlimaGal.FenThermalCutout | [9 empty] | 0x050018e0
TISKlimaGalGeneralAlarm | DIGITAL | IOD_TIS | TIS:.KlimaGal.GeneralAlarm | [9 empty] | 0x050018f0
TISKlimaGalGrelecStatus | BYTE | IOD_TIS | TIS:.KlimaGal.GrelecStatus | [9 empty] | 0x05001900
TISKlimaGalIzhodniVentStatus | BYTE | IOD_TIS | TIS:.KlimaGal.IzhodniVentStatus | [9 empty] | 0x05001901
TISKlimaGalKompresor1naMejiObrUr | DIGITAL | IOD_TIS | TIS:.KlimaGal.Kompresor1naMejiObrUr | [9 empty] | 0x05001910
TISKlimaGalKompresor2naMejiObrUr | DIGITAL | IOD_TIS | TIS:.KlimaGal.Kompresor2naMejiObrUr | [9 empty] | 0x05001920
TISKlimaGalKompresorStatus | BYTE | IOD_TIS | TIS:.KlimaGal.KompresorStatus | [9 empty] | 0x05001930
TISKlimaGalNapaka | DIGITAL | IOD_TIS | TIS:.KlimaGal.Napaka | [9 empty] | 0x05001940
TISKlimaGalNapakaPriPretokuZraka | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaPriPretokuZraka | [9 empty] | 0x05001950
TISKlimaGalNapakaSenzorPovratVode | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaSenzorPovratVode | [9 empty] | 0x05001960
TISKlimaGalNapakaSenzorTempIzpiha | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaSenzorTempIzpiha | [9 empty] | 0x05001970
TISKlimaGalNapakaSenzorTempProstora | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaSenzorTempProstora | [9 empty] | 0x05001980
TISKlimaGalNapakaSenzorVlaznosti | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaSenzorVlaznosti | [9 empty] | 0x05001990
TISKlimaGalNapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaSenzorZunanjeTemp | [9 empty] | 0x050019a0
TISKlimaGalNastMaxTemp | REAL | IOD_TIS | TIS:.KlimaGal.NastMaxTemp | [9 empty] | 0x050019b0
TISKlimaGalNastMaxVlaznost | REAL | IOD_TIS | TIS:.KlimaGal.NastMaxVlaznost | [9 empty] | 0x050019b1
TISKlimaGalNastMinTemp | REAL | IOD_TIS | TIS:.KlimaGal.NastMinTemp | [9 empty] | 0x050019b2
TISKlimaGalNastMinVlaznost | REAL | IOD_TIS | TIS:.KlimaGal.NastMinVlaznost | [9 empty] | 0x050019b3
TISKlimaGalNastTempProstora | REAL | IOD_TIS | TIS:.KlimaGal.NastTempProstora | [9 empty] | 0x050019b4
TISKlimaGalNastVlaznost | REAL | IOD_TIS | TIS:.KlimaGal.NastVlaznost | [9 empty] | 0x050019b5
TISKlimaGalNiTokaVVlazilcu | DIGITAL | IOD_TIS | TIS:.KlimaGal.NiTokaVVlazilcu | [9 empty] | 0x050019c0
TISKlimaGalNiVodeVVlazilcu | DIGITAL | IOD_TIS | TIS:.KlimaGal.NiVodeVVlazilcu | [9 empty] | 0x050019d0
TISKlimaGalNizekPritiskKompresor1 | DIGITAL | IOD_TIS | TIS:.KlimaGal.NizekPritiskKompresor1 | [9 empty] | 0x050019e0
TISKlimaGalNizekPritiskKompresor2 | DIGITAL | IOD_TIS | TIS:.KlimaGal.NizekPritiskKompresor2 | [9 empty] | 0x050019f0
TISKlimaGalNizkaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.KlimaGal.NizkaTempPovratneVode | [9 empty] | 0x05001a00
TISKlimaGalNizkaTempVProstoru | DIGITAL | IOD_TIS | TIS:.KlimaGal.NizkaTempVProstoru | [9 empty] | 0x05001a10
TISKlimaGalNizkaVlaznost | DIGITAL | IOD_TIS | TIS:.KlimaGal.NizkaVlaznost | [9 empty] | 0x05001a20
TISKlimaGalObratovalneUre | REAL | IOD_TIS | TIS:.KlimaGal.ObratovalneUre | [9 empty] | 0x05001a30
TISKlimaGalOnOffEnablingBySupervisor | DIGITAL | IOD_TIS | TIS:.KlimaGal.OnOffEnablingBySupervisor | [9 empty] | 0x05001a40
TISKlimaGalPozarniAlarm | DIGITAL | IOD_TIS | TIS:.KlimaGal.PozarniAlarm | [9 empty] | 0x05001a50
TISKlimaGalRazvlazevanje | DIGITAL | IOD_TIS | TIS:.KlimaGal.Razvlazevanje | [9 empty] | 0x05001a60
TISKlimaGalRemoteOFFtoOutput | DIGITAL | IOD_TIS | TIS:.KlimaGal.RemoteOFFtoOutput | [9 empty] | 0x05001a70
TISKlimaGalRemoteOnOff | DIGITAL | IOD_TIS | TIS:.KlimaGal.RemoteOnOff | [9 empty] | 0x05001a80
TISKlimaGalRocniIzklop | DIGITAL | IOD_TIS | TIS:.KlimaGal.RocniIzklop | [9 empty] | 0x05001a90
TISKlimaGalSenzorjiStatus | DIGITAL | IOD_TIS | TIS:.KlimaGal.SenzorjiStatus | [9 empty] | 0x05001aa0
TISKlimaGalStoppedByAlarms | DIGITAL | IOD_TIS | TIS:.KlimaGal.StoppedByAlarms | [9 empty] | 0x05001ab0
TISKlimaGalTemperaturaProstora | REAL | IOD_TIS | TIS:.KlimaGal.TemperaturaProstora | [9 empty] | 0x05001ac0
TISKlimaGalTempIzpihanegaZraka | REAL | IOD_TIS | TIS:.KlimaGal.TempIzpihanegaZraka | [9 empty] | 0x05001ac1
TISKlimaGalTempPovratneVode | REAL | IOD_TIS | TIS:.KlimaGal.TempPovratneVode | [9 empty] | 0x05001ac2
TISKlimaGalThermalCutoutHeater1 | DIGITAL | IOD_TIS | TIS:.KlimaGal.ThermalCutoutHeater1 | [9 empty] | 0x05001ad0
TISKlimaGalThermalCutoutHeater2 | DIGITAL | IOD_TIS | TIS:.KlimaGal.ThermalCutoutHeater2 | [9 empty] | 0x05001ae0
TISKlimaGalUnitOnOff | DIGITAL | IOD_TIS | TIS:.KlimaGal.UnitOnOff | [9 empty] | 0x05001af0
TISKlimaGalVentilatorNaMejiObrUr | DIGITAL | IOD_TIS | TIS:.KlimaGal.VentilatorNaMejiObrUr | [9 empty] | 0x05001b00
TISKlimaGalVentilGretjeOdpiranje | DIGITAL | IOD_TIS | TIS:.KlimaGal.VentilGretjeOdpiranje | [9 empty] | 0x05001b10
TISKlimaGalVentilGretjeZapiranje | DIGITAL | IOD_TIS | TIS:.KlimaGal.VentilGretjeZapiranje | [9 empty] | 0x05001b20
TISKlimaGalVentilHlajenjeOdpiranje | DIGITAL | IOD_TIS | TIS:.KlimaGal.VentilHlajenjeOdpiranje | [9 empty] | 0x05001b30
TISKlimaGalVentilHlajenjeZapiranje | DIGITAL | IOD_TIS | TIS:.KlimaGal.VentilHlajenjeZapiranje | [9 empty] | 0x05001b40
TISKlimaGalVisokaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.KlimaGal.VisokaTempPovratneVode | [9 empty] | 0x05001b50
TISKlimaGalVisokaTempVProstoru | DIGITAL | IOD_TIS | TIS:.KlimaGal.VisokaTempVProstoru | [9 empty] | 0x05001b60
TISKlimaGalVisokaVlaznost | DIGITAL | IOD_TIS | TIS:.KlimaGal.VisokaVlaznost | [9 empty] | 0x05001b70
TISKlimaGalVisokTokVVlazilcu | DIGITAL | IOD_TIS | TIS:.KlimaGal.VisokTokVVlazilcu | [9 empty] | 0x05001b80
TISKlimaGalVlazenje | DIGITAL | IOD_TIS | TIS:.KlimaGal.Vlazenje | [9 empty] | 0x05001b90
TISKlimaGalVlazilecStatus | BYTE | IOD_TIS | TIS:.KlimaGal.VlazilecStatus | [9 empty] | 0x05001ba0
TISKlimaGalVlaznostProstora | REAL | IOD_TIS | TIS:.KlimaGal.VlaznostProstora | [9 empty] | 0x05001ba1
TISKlimaGalZamasenFilter | DIGITAL | IOD_TIS | TIS:.KlimaGal.ZamasenFilter | [9 empty] | 0x05001bb0
TISKlimaGalZunanjaTemp | REAL | IOD_TIS | TIS:.KlimaGal.ZunanjaTemp | [9 empty] | 0x05001bc0
TISKlimeNaCas | DIGITAL | IOD_TIS | TIS:.KlimeNaCas | [9 empty] | 0x05001bd0
TISNapakaSenzorTemp10 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[10] | [9 empty] | 0x05001be0
TISNapakaSenzorTemp11 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[11] | [9 empty] | 0x05001bf0
TISNapakaSenzorTemp12 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[12] | [9 empty] | 0x05001c00
TISNapakaSenzorTemp13 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[13] | [9 empty] | 0x05001c10
TISNapakaSenzorTemp14 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[14] | [9 empty] | 0x05001c20
TISNapakaSenzorTemp15 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[15] | [9 empty] | 0x05001c30
TISNapakaSenzorTemp16 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[16] | [9 empty] | 0x05001c40
TISNapakaSenzorTemp17 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[17] | [9 empty] | 0x05001c50
TISNapakaSenzorTemp18 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[18] | [9 empty] | 0x05001c60
TISNapakaSenzorTemp19 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[19] | [9 empty] | 0x05001c70
TISNapakaSenzorTemp1 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[1] | [9 empty] | 0x05001c80
TISNapakaSenzorTemp2 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[2] | [9 empty] | 0x05001c90
TISNapakaSenzorTemp3 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[3] | [9 empty] | 0x05001ca0
TISNapakaSenzorTemp4 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[4] | [9 empty] | 0x05001cb0
TISNapakaSenzorTemp5 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[5] | [9 empty] | 0x05001cc0
TISNapakaSenzorTemp6 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[6] | [9 empty] | 0x05001cd0
TISNapakaSenzorTemp7 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[7] | [9 empty] | 0x05001ce0
TISNapakaSenzorTemp8 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[8] | [9 empty] | 0x05001cf0
TISNapakaSenzorTemp9 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[9] | [9 empty] | 0x05001d00
TISNapakaSenzorVlaga10 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[10] | [9 empty] | 0x05001d10
TISNapakaSenzorVlaga11 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[11] | [9 empty] | 0x05001d20
TISNapakaSenzorVlaga12 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[12] | [9 empty] | 0x05001d30
TISNapakaSenzorVlaga13 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[13] | [9 empty] | 0x05001d40
TISNapakaSenzorVlaga14 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[14] | [9 empty] | 0x05001d50
TISNapakaSenzorVlaga15 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[15] | [9 empty] | 0x05001d60
TISNapakaSenzorVlaga16 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[16] | [9 empty] | 0x05001d70
TISNapakaSenzorVlaga17 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[17] | [9 empty] | 0x05001d80
TISNapakaSenzorVlaga18 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[18] | [9 empty] | 0x05001d90
TISNapakaSenzorVlaga19 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[19] | [9 empty] | 0x05001da0
TISNapakaSenzorVlaga1 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[1] | [9 empty] | 0x05001db0
TISNapakaSenzorVlaga2 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[2] | [9 empty] | 0x05001dc0
TISNapakaSenzorVlaga3 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[3] | [9 empty] | 0x05001dd0
TISNapakaSenzorVlaga4 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[4] | [9 empty] | 0x05001de0
TISNapakaSenzorVlaga5 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[5] | [9 empty] | 0x05001df0
TISNapakaSenzorVlaga6 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[6] | [9 empty] | 0x05001e00
TISNapakaSenzorVlaga7 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[7] | [9 empty] | 0x05001e10
TISNapakaSenzorVlaga8 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[8] | [9 empty] | 0x05001e20
TISNapakaSenzorVlaga9 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[9] | [9 empty] | 0x05001e30
TISQstanje10 | BYTE | IOD_TIS | TIS:.Qstanje[10] | [9 empty] | 0x05001e40
TISQstanje1 | BYTE | IOD_TIS | TIS:.Qstanje[1] | [9 empty] | 0x05001e41
TISQstanje2 | BYTE | IOD_TIS | TIS:.Qstanje[2] | [9 empty] | 0x05001e42
TISQstanje3 | BYTE | IOD_TIS | TIS:.Qstanje[3] | [9 empty] | 0x05001e43
TISQstanje4 | BYTE | IOD_TIS | TIS:.Qstanje[4] | [9 empty] | 0x05001e44
TISQstanje5 | BYTE | IOD_TIS | TIS:.Qstanje[5] | [9 empty] | 0x05001e45
TISQstanje6 | BYTE | IOD_TIS | TIS:.Qstanje[6] | [9 empty] | 0x05001e46
TISQstanje7 | BYTE | IOD_TIS | TIS:.Qstanje[7] | [9 empty] | 0x05001e47
TISQstanje8 | BYTE | IOD_TIS | TIS:.Qstanje[8] | [9 empty] | 0x05001e48
TISQstanje9 | BYTE | IOD_TIS | TIS:.Qstanje[9] | [9 empty] | 0x05001e49
TISSenzorTemp10 | REAL | IOD_TIS | TIS:.SenzorTemp[10] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e4a
TISSenzorTemp11 | REAL | IOD_TIS | TIS:.SenzorTemp[11] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e4b
TISSenzorTemp12 | REAL | IOD_TIS | TIS:.SenzorTemp[12] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e4c
TISSenzorTemp13 | REAL | IOD_TIS | TIS:.SenzorTemp[13] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e4d
TISSenzorTemp14 | REAL | IOD_TIS | TIS:.SenzorTemp[14] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e4e
TISSenzorTemp15 | REAL | IOD_TIS | TIS:.SenzorTemp[15] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e4f
TISSenzorTemp16 | REAL | IOD_TIS | TIS:.SenzorTemp[16] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e50
TISSenzorTemp17 | REAL | IOD_TIS | TIS:.SenzorTemp[17] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e51
TISSenzorTemp18 | REAL | IOD_TIS | TIS:.SenzorTemp[18] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e52
TISSenzorTemp19 | REAL | IOD_TIS | TIS:.SenzorTemp[19] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e53
TISSenzorTemp1 | REAL | IOD_TIS | TIS:.SenzorTemp[1] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e54
TISSenzorTemp2 | REAL | IOD_TIS | TIS:.SenzorTemp[2] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e55
TISSenzorTemp3 | REAL | IOD_TIS | TIS:.SenzorTemp[3] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e56
TISSenzorTemp4 | REAL | IOD_TIS | TIS:.SenzorTemp[4] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e57
TISSenzorTemp5 | REAL | IOD_TIS | TIS:.SenzorTemp[5] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e58
TISSenzorTemp6 | REAL | IOD_TIS | TIS:.SenzorTemp[6] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e59
TISSenzorTemp7 | REAL | IOD_TIS | TIS:.SenzorTemp[7] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e5a
TISSenzorTemp8 | REAL | IOD_TIS | TIS:.SenzorTemp[8] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e5b
TISSenzorTemp9 | REAL | IOD_TIS | TIS:.SenzorTemp[9] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001e5c
TISSenzorVlaga10 | REAL | IOD_TIS | TIS:.SenzorVlaga[10] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e5d
TISSenzorVlaga11 | REAL | IOD_TIS | TIS:.SenzorVlaga[11] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e5e
TISSenzorVlaga12 | REAL | IOD_TIS | TIS:.SenzorVlaga[12] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e5f
TISSenzorVlaga13 | REAL | IOD_TIS | TIS:.SenzorVlaga[13] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e60
TISSenzorVlaga14 | REAL | IOD_TIS | TIS:.SenzorVlaga[14] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e61
TISSenzorVlaga15 | REAL | IOD_TIS | TIS:.SenzorVlaga[15] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e62
TISSenzorVlaga16 | REAL | IOD_TIS | TIS:.SenzorVlaga[16] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e63
TISSenzorVlaga17 | REAL | IOD_TIS | TIS:.SenzorVlaga[17] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e64
TISSenzorVlaga18 | REAL | IOD_TIS | TIS:.SenzorVlaga[18] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e65
TISSenzorVlaga19 | REAL | IOD_TIS | TIS:.SenzorVlaga[19] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e66
TISSenzorVlaga1 | REAL | IOD_TIS | TIS:.SenzorVlaga[1] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e67
TISSenzorVlaga2 | REAL | IOD_TIS | TIS:.SenzorVlaga[2] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e68
TISSenzorVlaga3 | REAL | IOD_TIS | TIS:.SenzorVlaga[3] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e69
TISSenzorVlaga4 | REAL | IOD_TIS | TIS:.SenzorVlaga[4] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e6a
TISSenzorVlaga5 | REAL | IOD_TIS | TIS:.SenzorVlaga[5] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e6b
TISSenzorVlaga6 | REAL | IOD_TIS | TIS:.SenzorVlaga[6] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e6c
TISSenzorVlaga7 | REAL | IOD_TIS | TIS:.SenzorVlaga[7] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e6d
TISSenzorVlaga8 | REAL | IOD_TIS | TIS:.SenzorVlaga[8] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e6e
TISSenzorVlaga9 | REAL | IOD_TIS | TIS:.SenzorVlaga[9] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05001e6f
TISSetDateTime | DIGITAL | IOD_TIS | TIS:.SetDateTime | [9 empty] | 0x05001e70
TISSetDateTimeDemand | DIGITAL | IOD_TIS | TIS:.SetDateTimeDemand | [9 empty] | 0x05001e80
TISSetDateTimeError | DIGITAL | IOD_TIS | TIS:.SetDateTimeError | [9 empty] | 0x05001e90
TISSetDateTimeFinished | DIGITAL | IOD_TIS | TIS:.SetDateTimeFinished | [9 empty] | 0x05001ea0
TISSetRemoteOnOff1 | DIGITAL | IOD_TIS | TIS:.SetRemoteOnOff[1] | [9 empty] | 0x05001eb0
TISSetRemoteOnOff2 | DIGITAL | IOD_TIS | TIS:.SetRemoteOnOff[2] | [9 empty] | 0x05001ec0
TISSetRemoteOnOff3 | DIGITAL | IOD_TIS | TIS:.SetRemoteOnOff[3] | [9 empty] | 0x05001ed0
TISSlabaBaterijaPLC_A1 | DIGITAL | IOD_TIS | TIS:.SlabaBaterijaPLC_A1 | [9 empty] | 0x05001ee0
TISTempAlarmPoint1 | REAL | IOD_TIS | TIS:.TempAlarmPoint[1] | 0 | 60 | 0 | 60 | °C | ## |  |  |  | 0x05001ef8
TISTempAlarmPoint2 | REAL | IOD_TIS | TIS:.TempAlarmPoint[2] | 0 | 60 | 0 | 60 | °C | ## |  |  |  | 0x05001ef9
TISTempAlarmPoint3 | REAL | IOD_TIS | TIS:.TempAlarmPoint[3] | 0 | 60 | 0 | 60 | °C | ## |  |  |  | 0x05001efa
TISTempMaxPoint1 | REAL | IOD_TIS | TIS:.TempMaxPoint[1] | 0 | 60 | 0 | 60 | °C | ## |  |  |  | 0x05001efb
TISTempMaxPoint2 | REAL | IOD_TIS | TIS:.TempMaxPoint[2] | 0 | 60 | 0 | 60 | °C | ## |  |  |  | 0x05001efc
TISTempMaxPoint3 | REAL | IOD_TIS | TIS:.TempMaxPoint[3] | 0 | 60 | 0 | 60 | °C | ## |  |  |  | 0x05001efd
TISTempPovp1 | REAL | IOD_TIS | TIS:.TempPovp[1] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001efe
TISTempPovp2 | REAL | IOD_TIS | TIS:.TempPovp[2] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001eff
TISTempPovp3 | REAL | IOD_TIS | TIS:.TempPovp[3] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001f00
TISTempPovp4 | REAL | IOD_TIS | TIS:.TempPovp[4] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001f01
TISTempPovp5 | REAL | IOD_TIS | TIS:.TempPovp[5] | 0 | 60 | 0 | 60 | °C | ##.# |  |  |  | 0x05001f02
TISTempSetPoint1 | REAL | IOD_TIS | TIS:.TempSetPoint[1] | 0 | 60 | 0 | 60 | °C | ## |  |  |  | 0x05001f03
TISTempSetPoint2 | REAL | IOD_TIS | TIS:.TempSetPoint[2] | 0 | 60 | 0 | 60 | °C | ## |  |  |  | 0x05001f04
TISTempSetPoint3 | REAL | IOD_TIS | TIS:.TempSetPoint[3] | 0 | 60 | 0 | 60 | °C | ## |  |  |  | 0x05001f05
TISTempTSprevisoka10 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[10] | [9 empty] | 0x05001f10
TISTempTSprevisoka11 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[11] | [9 empty] | 0x05001f20
TISTempTSprevisoka12 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[12] | [9 empty] | 0x05001f30
TISTempTSprevisoka13 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[13] | [9 empty] | 0x05001f40
TISTempTSprevisoka14 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[14] | [9 empty] | 0x05001f50
TISTempTSprevisoka15 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[15] | [9 empty] | 0x05001f60
TISTempTSprevisoka16 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[16] | [9 empty] | 0x05001f70
TISTempTSprevisoka17 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[17] | [9 empty] | 0x05001f80
TISTempTSprevisoka18 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[18] | [9 empty] | 0x05001f90
TISTempTSprevisoka19 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[19] | [9 empty] | 0x05001fa0
TISTempTSprevisoka1 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[1] | [9 empty] | 0x05001fb0
TISTempTSprevisoka2 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[2] | [9 empty] | 0x05001fc0
TISTempTSprevisoka3 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[3] | [9 empty] | 0x05001fd0
TISTempTSprevisoka4 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[4] | [9 empty] | 0x05001fe0
TISTempTSprevisoka5 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[5] | [9 empty] | 0x05001ff0
TISTempTSprevisoka6 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[6] | [9 empty] | 0x05002000
TISTempTSprevisoka7 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[7] | [9 empty] | 0x05002010
TISTempTSprevisoka8 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[8] | [9 empty] | 0x05002020
TISTempTSprevisoka9 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[9] | [9 empty] | 0x05002030
TISUserCurrentLevel | BYTE | IOD_TIS | TIS:.UserCurrentLevel | [9 empty] | 0x05002040
TISUserCurrentName | STRING | IOD_TIS | TIS:.UserCurrentName | [9 empty] | 0x05002041
TISUserLoggedIn | DIGITAL | IOD_TIS | TIS:.UserLoggedIn | [9 empty] | 0x05002050
TISVlagaPovp1 | REAL | IOD_TIS | TIS:.VlagaPovp[1] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05002060
TISVlagaPovp2 | REAL | IOD_TIS | TIS:.VlagaPovp[2] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05002061
TISVlagaPovp3 | REAL | IOD_TIS | TIS:.VlagaPovp[3] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05002062
TISVlagaPovp4 | REAL | IOD_TIS | TIS:.VlagaPovp[4] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05002063
TISVlagaPovp5 | REAL | IOD_TIS | TIS:.VlagaPovp[5] | 0 | 100 | 0 | 100 | % | ##.# |  |  |  | 0x05002064
TISXVH_AlarmOn | DIGITAL | IOD_TIS | TIS:.XVH_AlarmOn | [9 empty] | 0x05002070
TISXVH_CircNumber | BYTE | IOD_TIS | TIS:.XVH_CircNumber | [9 empty] | 0x05002080
TISXVH_GrafTemp1 | REAL | IOD_TIS | TIS:.XVH_GrafTemp[1] | [9 empty] | 0x05002081
TISXVH_GrafTemp2 | REAL | IOD_TIS | TIS:.XVH_GrafTemp[2] | [9 empty] | 0x05002082
TISXVH_GrafTemp3 | REAL | IOD_TIS | TIS:.XVH_GrafTemp[3] | [9 empty] | 0x05002083
TISXVH_GrafTemp4 | REAL | IOD_TIS | TIS:.XVH_GrafTemp[4] | [9 empty] | 0x05002084
TISXVH_GrafTemp5 | REAL | IOD_TIS | TIS:.XVH_GrafTemp[5] | [9 empty] | 0x05002085
TISXVH_GrafVlaga1 | REAL | IOD_TIS | TIS:.XVH_GrafVlaga[1] | [9 empty] | 0x05002086
TISXVH_GrafVlaga2 | REAL | IOD_TIS | TIS:.XVH_GrafVlaga[2] | [9 empty] | 0x05002087
TISXVH_GrafVlaga3 | REAL | IOD_TIS | TIS:.XVH_GrafVlaga[3] | [9 empty] | 0x05002088
TISXVH_GrafVlaga4 | REAL | IOD_TIS | TIS:.XVH_GrafVlaga[4] | [9 empty] | 0x05002089
TISXVH_GrafVlaga5 | REAL | IOD_TIS | TIS:.XVH_GrafVlaga[5] | [9 empty] | 0x0500208a
TISXVH_KlimaNumber | BYTE | IOD_TIS | TIS:.XVH_KlimaNumber | [9 empty] | 0x0500208b
TISXVH_NastTempProstora1 | REAL | IOD_TIS | TIS:.XVH_NastTempProstora[1] | [9 empty] | 0x0500208c
TISXVH_NastTempProstora2 | REAL | IOD_TIS | TIS:.XVH_NastTempProstora[2] | [9 empty] | 0x0500208d
TISXVH_NastTempProstora3 | REAL | IOD_TIS | TIS:.XVH_NastTempProstora[3] | [9 empty] | 0x0500208e
TISXVH_ObratovalneUre1 | REAL | IOD_TIS | TIS:.XVH_ObratovalneUre[1] | [9 empty] | 0x0500208f
TISXVH_ObratovalneUre2 | REAL | IOD_TIS | TIS:.XVH_ObratovalneUre[2] | [9 empty] | 0x05002090
TISXVH_ObratovalneUre3 | REAL | IOD_TIS | TIS:.XVH_ObratovalneUre[3] | [9 empty] | 0x05002091
TISXVH_PripravaVodeStat1 | BYTE | IOD_TIS | TIS:.XVH_PripravaVodeStat[1] | [9 empty] | 0x05002092
TISXVH_PripravaVodeStat2 | BYTE | IOD_TIS | TIS:.XVH_PripravaVodeStat[2] | [9 empty] | 0x05002093
TISXVH_RemoteStatus1 | DIGITAL | IOD_TIS | TIS:.XVH_RemoteStatus[1] | [9 empty] | 0x050020a0
TISXVH_RemoteStatus2 | DIGITAL | IOD_TIS | TIS:.XVH_RemoteStatus[2] | [9 empty] | 0x050020b0
TISXVH_RemoteStatus3 | DIGITAL | IOD_TIS | TIS:.XVH_RemoteStatus[3] | [9 empty] | 0x050020c0
TISXVH_setCircNum1 | DIGITAL | IOD_TIS | TIS:.XVH_setCircNum[1] | [9 empty] | 0x050020d0
TISXVH_setCircNum2 | DIGITAL | IOD_TIS | TIS:.XVH_setCircNum[2] | [9 empty] | 0x050020e0
TISXVH_setCircNum3 | DIGITAL | IOD_TIS | TIS:.XVH_setCircNum[3] | [9 empty] | 0x050020f0
TISXVH_setCircNum4 | DIGITAL | IOD_TIS | TIS:.XVH_setCircNum[4] | [9 empty] | 0x05002100
TISXVH_setCircNum5 | DIGITAL | IOD_TIS | TIS:.XVH_setCircNum[5] | [9 empty] | 0x05002110
TISXVH_setKlimaNum1 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[1] | [9 empty] | 0x05002120
TISXVH_setKlimaNum2 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[2] | [9 empty] | 0x05002130
TISXVH_setKlimaNum3 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[3] | [9 empty] | 0x05002140
TISXVH_setKlimaNum4 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[4] | [9 empty] | 0x05002150
TISXVH_setKlimaNum5 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[5] | [9 empty] | 0x05002160
TISXVH_setKlimaNum6 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[6] | [9 empty] | 0x05002170
TISXVH_UPSstatus | BYTE | IOD_TIS | TIS:.XVH_UPSstatus | [9 empty] | 0x05002180
TISXVH_VlazilecStatus1 | BYTE | IOD_TIS | TIS:.XVH_VlazilecStatus[1] | [9 empty] | 0x05002181
TISXVH_VlazilecStatus2 | BYTE | IOD_TIS | TIS:.XVH_VlazilecStatus[2] | [9 empty] | 0x05002182
TISXVH_VlazilecStatus3 | BYTE | IOD_TIS | TIS:.XVH_VlazilecStatus[3] | [9 empty] | 0x05002183
TISXVHhighHum | REAL | IOD_TIS | TIS:.XVHhighHum | [9 empty] | 0x05002184
TISXVHhighTemp | REAL | IOD_TIS | TIS:.XVHhighTemp | [9 empty] | 0x05002185
TISXVHlowHum | REAL | IOD_TIS | TIS:.XVHlowHum | [9 empty] | 0x05002186
TISXVHlowTemp | REAL | IOD_TIS | TIS:.XVHlowTemp | [9 empty] | 0x05002187
TISXVHnum10 | BYTE | IOD_TIS | TIS:.XVHnum[10] | [9 empty] | 0x05002188
TISXVHnum11 | BYTE | IOD_TIS | TIS:.XVHnum[11] | [9 empty] | 0x05002189
TISXVHnum12 | BYTE | IOD_TIS | TIS:.XVHnum[12] | [9 empty] | 0x0500218a
TISXVHnum13 | BYTE | IOD_TIS | TIS:.XVHnum[13] | [9 empty] | 0x0500218b
TISXVHnum14 | BYTE | IOD_TIS | TIS:.XVHnum[14] | [9 empty] | 0x0500218c
TISXVHnum1 | BYTE | IOD_TIS | TIS:.XVHnum[1] | [9 empty] | 0x0500218d
TISXVHnum2 | BYTE | IOD_TIS | TIS:.XVHnum[2] | [9 empty] | 0x0500218e
TISXVHnum3 | BYTE | IOD_TIS | TIS:.XVHnum[3] | [9 empty] | 0x0500218f
TISXVHnum4 | BYTE | IOD_TIS | TIS:.XVHnum[4] | [9 empty] | 0x05002190
TISXVHnum5 | BYTE | IOD_TIS | TIS:.XVHnum[5] | [9 empty] | 0x05002191
TISXVHnum6 | BYTE | IOD_TIS | TIS:.XVHnum[6] | [9 empty] | 0x05002192
TISXVHnum7 | BYTE | IOD_TIS | TIS:.XVHnum[7] | [9 empty] | 0x05002193
TISXVHnum8 | BYTE | IOD_TIS | TIS:.XVHnum[8] | [9 empty] | 0x05002194
TISXVHnum9 | BYTE | IOD_TIS | TIS:.XVHnum[9] | [9 empty] | 0x05002195
TIS_DanEnergCircE_G3 | REAL | IOD_TIS_disk | R0[30] | [9 empty] | 0x0500219a
TIS_CasDDanEnergCircE_G3 | INT | IOD_TIS_disk | I30[30] | [9 empty] | 0x0500219b
TIS_CasMDanEnergCircE_G3 | INT | IOD_TIS_disk | I60[30] | [9 empty] | 0x0500219c
TIS_TedenEnergCircE_G3 | REAL | IOD_TIS_disk | R3374[30] | [9 empty] | 0x0500219d
TIS_CasDTedenEnergCircE_G3 | INT | IOD_TIS_disk | I120[30] | [9 empty] | 0x0500219e
TIS_CasMTedenEnergCircE_G3 | INT | IOD_TIS_disk | I150[30] | [9 empty] | 0x0500219f
TIS_MesecEnergCircE_G3 | REAL | IOD_TIS_disk | R3404[30] | [9 empty] | 0x050021a0
TIS_CasDMesecEnergCircE_G3 | INT | IOD_TIS_disk | I210[30] | [9 empty] | 0x050021a1
TIS_CasMMesecEnergCircE_G3 | INT | IOD_TIS_disk | I240[30] | [9 empty] | 0x050021a2
TIS_StSt_DanEnergCircE_G3 | REAL | IOD_TIS_disk | R3434 | [9 empty] | 0x050021a3
TIS_StSt_TedenEnergCircE_G3 | REAL | IOD_TIS_disk | R3438 | [9 empty] | 0x050021a4
TIS_StSt_MesecEnergCircE_G3 | REAL | IOD_TIS_disk | R3442 | [9 empty] | 0x050021a5
TIS_StStCasDDanEnergCircE_G3 | INT | IOD_TIS_disk | I276 | [9 empty] | 0x050021a6
TIS_StStCasMDanEnergCircE_G3 | INT | IOD_TIS_disk | I278 | [9 empty] | 0x050021a7
TIS_StStCasDTedenEnergCircE_G3 | INT | IOD_TIS_disk | I280 | [9 empty] | 0x050021a8
TIS_StStCasMTedenEnergCircE_G3 | INT | IOD_TIS_disk | I282 | [9 empty] | 0x050021a9
TIS_StStCasDMesecEnergCircE_G3 | INT | IOD_TIS_disk | I284 | [9 empty] | 0x050021aa
TIS_StStCasMMesecEnergCircE_G3 | INT | IOD_TIS_disk | I286 | [9 empty] | 0x050021ab
TIS_DanEnergCircE_DG3 | REAL | IOD_TIS_disk | R3446[30] | [9 empty] | 0x050021ac
TIS_CasDDanEnergCircE_DG3 | INT | IOD_TIS_disk | I318[30] | [9 empty] | 0x050021ad
TIS_CasMDanEnergCircE_DG3 | INT | IOD_TIS_disk | I358[30] | [9 empty] | 0x050021ae
TIS_TedenEnergCircE_DG3 | REAL | IOD_TIS_disk | R3476[30] | [9 empty] | 0x050021af
TIS_CasDTedenEnergCircE_DG3 | INT | IOD_TIS_disk | I418[30] | [9 empty] | 0x050021b0
TIS_CasMTedenEnergCircE_DG3 | INT | IOD_TIS_disk | I448[30] | [9 empty] | 0x050021b1
TIS_MesecEnergCircE_DG3 | REAL | IOD_TIS_disk | R3506[30] | [9 empty] | 0x050021b2
TIS_CasDMesecEnergCircE_DG3 | INT | IOD_TIS_disk | I508[30] | [9 empty] | 0x050021b3
TIS_CasMMesecEnergCircE_DG3 | INT | IOD_TIS_disk | I538[30] | [9 empty] | 0x050021b4
TIS_StSt_DanEnergCircE_DG3 | REAL | IOD_TIS_disk | R3536 | [9 empty] | 0x050021b5
TIS_StSt_TedenEnergCircE_DG3 | REAL | IOD_TIS_disk | R3540 | [9 empty] | 0x050021b6
TIS_StSt_MesecEnergCircE_DG3 | REAL | IOD_TIS_disk | R3544 | [9 empty] | 0x050021b7
TIS_StStCasDDanEnergCircE_DG3 | INT | IOD_TIS_disk | I574 | [9 empty] | 0x050021b8
TIS_StStCasMDanEnergCircE_DG3 | INT | IOD_TIS_disk | I576 | [9 empty] | 0x050021b9
TIS_StStCasDTedenEnergCircE_DG3 | INT | IOD_TIS_disk | I578 | [9 empty] | 0x050021ba
TIS_StStCasMTedenEnergCircE_DG3 | INT | IOD_TIS_disk | I580 | [9 empty] | 0x050021bb
TIS_StStCasDMesecEnergCircE_DG3 | INT | IOD_TIS_disk | I582 | [9 empty] | 0x050021bc
TIS_StStCasMMesecEnergCircE_DG3 | INT | IOD_TIS_disk | I584 | [9 empty] | 0x050021bd
TIS_DanEnergCircE_UPS3 | REAL | IOD_TIS_disk | R3550[30] | [9 empty] | 0x050021be
TIS_CasDDanEnergCircE_UPS3 | INT | IOD_TIS_disk | I644[30] | [9 empty] | 0x050021bf
TIS_CasMDanEnergCircE_UPS3 | INT | IOD_TIS_disk | I674[30] | [9 empty] | 0x050021c0
TIS_TedenEnergCircE_UPS3 | REAL | IOD_TIS_disk | R3580[30] | [9 empty] | 0x050021c1
TIS_CasDTedenEnergCircE_UPS3 | INT | IOD_TIS_disk | I734[30] | [9 empty] | 0x050021c2
TIS_CasMTedenEnergCircE_UPS3 | INT | IOD_TIS_disk | I764[30] | [9 empty] | 0x050021c3
TIS_MesecEnergCircE_UPS3 | REAL | IOD_TIS_disk | R3610[30] | [9 empty] | 0x050021c4
TIS_CasDMesecEnergCircE_UPS3 | INT | IOD_TIS_disk | I824[30] | [9 empty] | 0x050021c5
TIS_CasMMesecEnergCircE_UPS3 | INT | IOD_TIS_disk | I854[30] | [9 empty] | 0x050021c6
TIS_StSt_DanEnergCircE_UPS3 | REAL | IOD_TIS_disk | R3640 | [9 empty] | 0x050021c7
TIS_StSt_TedenEnergCircE_UPS3 | REAL | IOD_TIS_disk | R3644 | [9 empty] | 0x050021c8
TIS_StSt_MesecEnergCircE_UPS3 | REAL | IOD_TIS_disk | R3648 | [9 empty] | 0x050021c9
TIS_StStCasDDanEnergCircE_UPS3 | INT | IOD_TIS_disk | I870 | [9 empty] | 0x050021ca
TIS_StStCasMDanEnergCircE_UPS3 | INT | IOD_TIS_disk | I872 | [9 empty] | 0x050021cb
TIS_StStCasDTedenEnergCircE_UPS3 | INT | IOD_TIS_disk | I874 | [9 empty] | 0x050021cc
TIS_StStCasMTedenEnergCircE_UPS3 | INT | IOD_TIS_disk | I876 | [9 empty] | 0x050021cd
TIS_StStCasDMesecEnergCircE_UPS3 | INT | IOD_TIS_disk | I878 | [9 empty] | 0x050021ce
TIS_StStCasMMesecEnergCircE_UPS3 | INT | IOD_TIS_disk | I880 | [9 empty] | 0x050021cf
TIS_DanEnergCircE_DG4 | REAL | IOD_TIS_disk | R3650[30] | [9 empty] | 0x050021d0
TIS_CasDDanEnergCircE_DG4 | INT | IOD_TIS_disk | I940[30] | [9 empty] | 0x050021d1
TIS_CasMDanEnergCircE_DG4 | INT | IOD_TIS_disk | I970[30] | [9 empty] | 0x050021d2
TIS_TedenEnergCircE_DG4 | REAL | IOD_TIS_disk | R3680[30] | [9 empty] | 0x050021d3
TIS_CasDTedenEnergCircE_DG4 | INT | IOD_TIS_disk | I940[30] | [9 empty] | 0x050021d4
TIS_CasMTedenEnergCircE_DG4 | INT | IOD_TIS_disk | I970[30] | [9 empty] | 0x050021d5
TIS_MesecEnergCircE_DG4 | REAL | IOD_TIS_disk | R3710[30] | [9 empty] | 0x050021d6
TIS_CasDMesecEnergCircE_DG4 | INT | IOD_TIS_disk | I1030[30] | [9 empty] | 0x050021d7
TIS_CasMMesecEnergCircE_DG4 | INT | IOD_TIS_disk | I1060[30] | [9 empty] | 0x050021d8
TIS_StSt_DanEnergCircE_DG4 | REAL | IOD_TIS_disk | R3740 | [9 empty] | 0x050021d9
TIS_StSt_TedenEnergCircE_DG4 | REAL | IOD_TIS_disk | R3744 | [9 empty] | 0x050021da
TIS_StSt_MesecEnergCircE_DG4 | REAL | IOD_TIS_disk | R3748 | [9 empty] | 0x050021db
TIS_StStCasDDanEnergCircE_DG4 | INT | IOD_TIS_disk | I1098 | [9 empty] | 0x050021dc
TIS_StStCasMDanEnergCircE_DG4 | INT | IOD_TIS_disk | I1100 | [9 empty] | 0x050021dd
TIS_StStCasDTedenEnergCircE_DG4 | INT | IOD_TIS_disk | I1102 | [9 empty] | 0x050021de
TIS_StStCasMTedenEnergCircE_DG4 | INT | IOD_TIS_disk | I1104 | [9 empty] | 0x050021df
TIS_StStCasDMesecEnergCircE_DG4 | INT | IOD_TIS_disk | I1106 | [9 empty] | 0x050021e0
TIS_StStCasMMesecEnergCircE_DG4 | INT | IOD_TIS_disk | I1108 | [9 empty] | 0x050021e1
TIS_MaxDnevnaEnergijaE_DG4 | REAL | IOD_TIS_disk | R3750 | [5 empty] | ########## |  |  |  | 0x050021e2
TIS_MaxTedenskaEnergijaE_DG4 | REAL | IOD_TIS_disk | R3752 | [5 empty] | ########## |  |  |  | 0x050021e3
TIS_MaxMesecnaEnergijaE_DG4 | REAL | IOD_TIS_disk | R3754 | [5 empty] | ########## |  |  |  | 0x050021e4
TIS_MaxDnevnaEnergijaE_G3 | REAL | IOD_TIS_disk | R3756 | [5 empty] | ########## |  |  |  | 0x050021e5
TIS_MaxTedenskaEnergijaE_G3 | REAL | IOD_TIS_disk | R3758 | [5 empty] | ########## |  |  |  | 0x050021e6
TIS_MaxMesecnaEnergijaE_G3 | REAL | IOD_TIS_disk | R3760 | [5 empty] | ########## |  |  |  | 0x050021e7
TIS_MaxDnevnaEnergijaE_DG3 | REAL | IOD_TIS_disk | R3762 | [5 empty] | ########## |  |  |  | 0x050021e8
TIS_MaxTedenskaEnergijaE_DG3 | REAL | IOD_TIS_disk | R3764 | [5 empty] | ########## |  |  |  | 0x050021e9
TIS_MaxMesecnaEnergijaE_DG3 | REAL | IOD_TIS_disk | R3766 | [5 empty] | ########## |  |  |  | 0x050021ea
TIS_MaxDnevnaEnergijaE_UPS3 | REAL | IOD_TIS_disk | R3768 | [5 empty] | ########## |  |  |  | 0x050021eb
TIS_MaxTedenskaEnergijaE_UPS3 | REAL | IOD_TIS_disk | R3770 | [5 empty] | ########## |  |  |  | 0x050021ec
TIS_MaxMesecnaEnergijaE_UPS3 | REAL | IOD_TIS_disk | R3772 | [5 empty] | ########## |  |  |  | 0x050021ed
TIS_Sekunda1s_utripanje | DIGITAL | IOD_TIS_mem | D1134 | [9 empty] | 0x050021f0
TISNacDelovanjaKlimeAvtomatsko | DIGITAL | IOD_TIS_mem | D1135 | [9 empty] | 0x05002200
TISComSCADA_stevec2 | INT | IOD_TIS_mem | I1136 | [9 empty] | 0x05002210
TISComSCADA_stevec1 | INT | IOD_TIS_mem | I1138 | [9 empty] | 0x05002211
TIS_meja_tok_opozorilo | DIGITAL | IOD_TIS_disk | D1140[14] | [9 empty] | 0x05002220
TIS_meja_tok_alarm | DIGITAL | IOD_TIS_disk | D1154[14] | [9 empty] | 0x05002230
TIS_omogocanje_tok_opozorila | DIGITAL | IOD_TIS_disk | D1200 | [9 empty] | 0x05002240
TIS_omogocanje_tok_alarm | DIGITAL | IOD_TIS_disk | D1201 | [9 empty] | 0x05002250
TIS_ComScadaPlc_omog | DIGITAL | IOD_TIS_disk | D1202 | [9 empty] | 0x05002260
TISErrComPanelPLC_omog | DIGITAL | IOD_TIS_disk | D1203 | [9 empty] | 0x05002270
TISErrComPort2_omog | DIGITAL | IOD_TIS_disk | D1204 | [9 empty] | 0x05002280
TISErrComCirc1_omog | DIGITAL | IOD_TIS_disk | D1205 | [9 empty] | 0x05002290
TISErrComCirc2_omog | DIGITAL | IOD_TIS_disk | D1206 | [9 empty] | 0x050022a0
TISErrComCirc3_omog | DIGITAL | IOD_TIS_disk | D1207 | [9 empty] | 0x050022b0
TISErrComCirc4_omog | DIGITAL | IOD_TIS_disk | D1208 | [9 empty] | 0x050022c0
TISErrComCirc5_omog | DIGITAL | IOD_TIS_disk | D1209 | [9 empty] | 0x050022d0
TISErrComKlima2_omog | DIGITAL | IOD_TIS_disk | D1210 | [9 empty] | 0x050022e0
TISErrComKlima3_omog | DIGITAL | IOD_TIS_disk | D1211 | [9 empty] | 0x050022f0
TISDIN_F1_OdklHlOm1_IZP_omog | DIGITAL | IOD_TIS_disk | D1212 | [9 empty] | 0x05002300
TISDIN_F2_OdklHlOm2_IZP_omog | DIGITAL | IOD_TIS_disk | D1213 | [9 empty] | 0x05002310
TISDIN_F3_OdklHlOm3_IZP_omog | DIGITAL | IOD_TIS_disk | D1214 | [9 empty] | 0x05002320
TISDIN_F4_OdkPripVode_IZP_omog | DIGITAL | IOD_TIS_disk | D1215 | [9 empty] | 0x05002330
TISDI_HladOmara1_ERR_omog | DIGITAL | IOD_TIS_disk | D1216 | [9 empty] | 0x05002340
TISDI_HladOmara2_ERR_omog | DIGITAL | IOD_TIS_disk | D1217 | [9 empty] | 0x05002350
TISDI_HladOmara3_ERR_omog | DIGITAL | IOD_TIS_disk | D1218 | [9 empty] | 0x05002360
TISDI_Vlazilec1_ERR_omog | DIGITAL | IOD_TIS_disk | D1219 | [9 empty] | 0x05002370
TISDI_Vlazilec2_ERR_omog | DIGITAL | IOD_TIS_disk | D1220 | [9 empty] | 0x05002380
TISDI_Vlazilec3_ERR_omog | DIGITAL | IOD_TIS_disk | D1221 | [9 empty] | 0x05002390
TISDIN_PripVode1_ERR_omog | DIGITAL | IOD_TIS_disk | D1222 | [9 empty] | 0x050023a0
TISDIN_PripVode2_ERR_omog | DIGITAL | IOD_TIS_disk | D1223 | [9 empty] | 0x050023b0
TISDI_UPS_Alarm_omog | DIGITAL | IOD_TIS_disk | D1224 | [9 empty] | 0x050023c0
TISDIN_RazlitjeVodeHO1_omog | DIGITAL | IOD_TIS_disk | D1225 | [9 empty] | 0x050023d0
TISDIN_RazlitjeVodeHO2_omog | DIGITAL | IOD_TIS_disk | D1226 | [9 empty] | 0x050023e0
TISDIN_RazlitjeVodeHO3_omog | DIGITAL | IOD_TIS_disk | D1227 | [9 empty] | 0x050023f0
TISSetDateTimeError_omog | DIGITAL | IOD_TIS_disk | D1228 | [9 empty] | 0x05002400
TISSlabaBaterijaPLC_A1_omog | DIGITAL | IOD_TIS_disk | D1229 | [9 empty] | 0x05002410
TISTempTSprevisoka1_omog | DIGITAL | IOD_TIS_disk | D1230 | [9 empty] | 0x05002420
TISTempTSprevisoka2_omog | DIGITAL | IOD_TIS_disk | D1231 | [9 empty] | 0x05002430
TISTempTSprevisoka3_omog | DIGITAL | IOD_TIS_disk | D1232 | [9 empty] | 0x05002440
TISTempTSprevisoka4_omog | DIGITAL | IOD_TIS_disk | D1233 | [9 empty] | 0x05002450
TISTempTSprevisoka5_omog | DIGITAL | IOD_TIS_disk | D1234 | [9 empty] | 0x05002460
TISTempTSprevisoka6_omog | DIGITAL | IOD_TIS_disk | D1235 | [9 empty] | 0x05002470
TISTempTSprevisoka7_omog | DIGITAL | IOD_TIS_disk | D1236 | [9 empty] | 0x05002480
TISTempTSprevisoka8_omog | DIGITAL | IOD_TIS_disk | D1237 | [9 empty] | 0x05002490
TISTempTSprevisoka9_omog | DIGITAL | IOD_TIS_disk | D1238 | [9 empty] | 0x050024a0
TISTempTSprevisoka10_omog | DIGITAL | IOD_TIS_disk | D1239 | [9 empty] | 0x050024b0
TISTempTSprevisoka11_omog | DIGITAL | IOD_TIS_disk | D1240 | [9 empty] | 0x050024c0
TISTempTSprevisoka12_omog | DIGITAL | IOD_TIS_disk | D1241 | [9 empty] | 0x050024d0
TISTempTSprevisoka13_omog | DIGITAL | IOD_TIS_disk | D1242 | [9 empty] | 0x050024e0
TISTempTSprevisoka14_omog | DIGITAL | IOD_TIS_disk | D1243 | [9 empty] | 0x050024f0
TISTempTSprevisoka15_omog | DIGITAL | IOD_TIS_disk | D1244 | [9 empty] | 0x05002500
TISTempTSprevisoka16_omog | DIGITAL | IOD_TIS_disk | D1245 | [9 empty] | 0x05002510
TISTempTSprevisoka17_omog | DIGITAL | IOD_TIS_disk | D1246 | [9 empty] | 0x05002520
TISTempTSprevisoka18_omog | DIGITAL | IOD_TIS_disk | D1247 | [9 empty] | 0x05002530
TISTempTSprevisoka19_omog | DIGITAL | IOD_TIS_disk | D1248 | [9 empty] | 0x05002540
TISNapakaSenzorTemp1_omog | DIGITAL | IOD_TIS_disk | D1249 | [9 empty] | 0x05002550
TISNapakaSenzorTemp2_omog | DIGITAL | IOD_TIS_disk | D1250 | [9 empty] | 0x05002560
TISNapakaSenzorTemp3_omog | DIGITAL | IOD_TIS_disk | D1251 | [9 empty] | 0x05002570
TISNapakaSenzorTemp4_omog | DIGITAL | IOD_TIS_disk | D1252 | [9 empty] | 0x05002580
TISNapakaSenzorTemp5_omog | DIGITAL | IOD_TIS_disk | D1253 | [9 empty] | 0x05002590
TISNapakaSenzorTemp6_omog | DIGITAL | IOD_TIS_disk | D1254 | [9 empty] | 0x050025a0
TISNapakaSenzorTemp7_omog | DIGITAL | IOD_TIS_disk | D1255 | [9 empty] | 0x050025b0
TISNapakaSenzorTemp8_omog | DIGITAL | IOD_TIS_disk | D1256 | [9 empty] | 0x050025c0
TISNapakaSenzorTemp9_omog | DIGITAL | IOD_TIS_disk | D1257 | [9 empty] | 0x050025d0
TISNapakaSenzorTemp10_omog | DIGITAL | IOD_TIS_disk | D1258 | [9 empty] | 0x050025e0
TISNapakaSenzorTemp11_omog | DIGITAL | IOD_TIS_disk | D1259 | [9 empty] | 0x050025f0
TISNapakaSenzorTemp12_omog | DIGITAL | IOD_TIS_disk | D1260 | [9 empty] | 0x05002600
TISNapakaSenzorTemp13_omog | DIGITAL | IOD_TIS_disk | D1261 | [9 empty] | 0x05002610
TISNapakaSenzorTemp14_omog | DIGITAL | IOD_TIS_disk | D1262 | [9 empty] | 0x05002620
TISNapakaSenzorTemp15_omog | DIGITAL | IOD_TIS_disk | D1263 | [9 empty] | 0x05002630
TISNapakaSenzorTemp16_omog | DIGITAL | IOD_TIS_disk | D1264 | [9 empty] | 0x05002640
TISNapakaSenzorTemp17_omog | DIGITAL | IOD_TIS_disk | D1265 | [9 empty] | 0x05002650
TISNapakaSenzorTemp18_omog | DIGITAL | IOD_TIS_disk | D1266 | [9 empty] | 0x05002660
TISNapakaSenzorTemp19_omog | DIGITAL | IOD_TIS_disk | D1267 | [9 empty] | 0x05002670
TISNapakaSenzorVlaga1_omog | DIGITAL | IOD_TIS_disk | D1268 | [9 empty] | 0x05002680
TISNapakaSenzorVlaga2_omog | DIGITAL | IOD_TIS_disk | D1269 | [9 empty] | 0x05002690
TISNapakaSenzorVlaga3_omog | DIGITAL | IOD_TIS_disk | D1270 | [9 empty] | 0x050026a0
TISNapakaSenzorVlaga4_omog | DIGITAL | IOD_TIS_disk | D1271 | [9 empty] | 0x050026b0
TISNapakaSenzorVlaga5_omog | DIGITAL | IOD_TIS_disk | D1272 | [9 empty] | 0x050026c0
TISNapakaSenzorVlaga6_omog | DIGITAL | IOD_TIS_disk | D1273 | [9 empty] | 0x050026d0
TISNapakaSenzorVlaga7_omog | DIGITAL | IOD_TIS_disk | D1274 | [9 empty] | 0x050026e0
TISNapakaSenzorVlaga8_omog | DIGITAL | IOD_TIS_disk | D1275 | [9 empty] | 0x050026f0
TISNapakaSenzorVlaga9_omog | DIGITAL | IOD_TIS_disk | D1276 | [9 empty] | 0x05002700
TISNapakaSenzorVlaga10_omog | DIGITAL | IOD_TIS_disk | D1277 | [9 empty] | 0x05002710
TISNapakaSenzorVlaga11_omog | DIGITAL | IOD_TIS_disk | D1278 | [9 empty] | 0x05002720
TISNapakaSenzorVlaga12_omog | DIGITAL | IOD_TIS_disk | D1279 | [9 empty] | 0x05002730
TISNapakaSenzorVlaga13_omog | DIGITAL | IOD_TIS_disk | D1280 | [9 empty] | 0x05002740
TISNapakaSenzorVlaga14_omog | DIGITAL | IOD_TIS_disk | D1281 | [9 empty] | 0x05002750
TISNapakaSenzorVlaga15_omog | DIGITAL | IOD_TIS_disk | D1282 | [9 empty] | 0x05002760
TISNapakaSenzorVlaga16_omog | DIGITAL | IOD_TIS_disk | D1283 | [9 empty] | 0x05002770
TISNapakaSenzorVlaga17_omog | DIGITAL | IOD_TIS_disk | D1284 | [9 empty] | 0x05002780
TISNapakaSenzorVlaga18_omog | DIGITAL | IOD_TIS_disk | D1285 | [9 empty] | 0x05002790
TISNapakaSenzorVlaga19_omog | DIGITAL | IOD_TIS_disk | D1286 | [9 empty] | 0x050027a0
TISKlima1AlarmKompresor1_omog | DIGITAL | IOD_TIS_disk | D1287 | [9 empty] | 0x050027b0
TISKlima1AlarmKompresor2_omog | DIGITAL | IOD_TIS_disk | D1288 | [9 empty] | 0x050027c0
TISKlima1NizekPritiskKompresor1_omog | DIGITAL | IOD_TIS_disk | D1289 | [9 empty] | 0x050027d0
TISKlima1NizekPritiskKompresor2_omog | DIGITAL | IOD_TIS_disk | D1290 | [9 empty] | 0x050027e0
TISKlima1NapakaPriPretokuZraka_omog | DIGITAL | IOD_TIS_disk | D1291 | [9 empty] | 0x050027f0
TISKlima1FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1292 | [9 empty] | 0x05002800
TISKlima1ThermalCutoutHeater1_omog | DIGITAL | IOD_TIS_disk | D1293 | [9 empty] | 0x05002810
TISKlima1ThermalCutoutHeater2_omog | DIGITAL | IOD_TIS_disk | D1294 | [9 empty] | 0x05002820
TISKlima1PozarniAlarm_omog | DIGITAL | IOD_TIS_disk | D1295 | [9 empty] | 0x05002830
TISKlima1ZamasenFilter_omog | DIGITAL | IOD_TIS_disk | D1296 | [9 empty] | 0x05002840
TISKlima1VisokaTempVProstoru_omog | DIGITAL | IOD_TIS_disk | D1297 | [9 empty] | 0x05002850
TISKlima1NizkaTempVProstoru_omog | DIGITAL | IOD_TIS_disk | D1298 | [9 empty] | 0x05002860
TISKlima1VisokaVlaznost_omog | DIGITAL | IOD_TIS_disk | D1299 | [9 empty] | 0x05002870
TISKlima1NizkaVlaznost_omog | DIGITAL | IOD_TIS_disk | D1300 | [9 empty] | 0x05002880
TISKlima1Kompresor1naMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1301 | [9 empty] | 0x05002890
TISKlima1Kompresor2naMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1302 | [9 empty] | 0x050028a0
TISKlima1VentilatorNaMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1303 | [9 empty] | 0x050028b0
TISKlima1NapakaSenzorTempProstora_omog | DIGITAL | IOD_TIS_disk | D1304 | [9 empty] | 0x050028c0
TISKlima1NapakaSenzorPovratVode_omog | DIGITAL | IOD_TIS_disk | D1305 | [9 empty] | 0x050028d0
TISKlima1NapakaSenzorZunanjeTemp_omog | DIGITAL | IOD_TIS_disk | D1306 | [9 empty] | 0x050028e0
TISKlima1NapakaSenzorTempIzpiha_omog | DIGITAL | IOD_TIS_disk | D1307 | [9 empty] | 0x050028f0
TISKlima1NapakaSenzorVlaznosti_omog | DIGITAL | IOD_TIS_disk | D1308 | [9 empty] | 0x05002900
TISKlima1NapakaSenzorPritiska1_omog | DIGITAL | IOD_TIS_disk | D1309 | [9 empty] | 0x05002910
TISKlima1NapakaSenzorPritiska2_omog | DIGITAL | IOD_TIS_disk | D1310 | [9 empty] | 0x05002920
TISKlima1NapakaSenzorKondTemp1_omog | DIGITAL | IOD_TIS_disk | D1311 | [9 empty] | 0x05002930
TISKlima1NapakaSenzorKondTemp2_omog | DIGITAL | IOD_TIS_disk | D1312 | [9 empty] | 0x05002940
TISKlima1VisokTokVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1313 | [9 empty] | 0x05002950
TISKlima1NiVodeVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1314 | [9 empty] | 0x05002960
TISKlima1NiTokaVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1315 | [9 empty] | 0x05002970
TISKlima1ClockCardFault_omog | DIGITAL | IOD_TIS_disk | D1316 | [9 empty] | 0x05002980
TISKlima1VisokPritiskVKrogu1_omog | DIGITAL | IOD_TIS_disk | D1317 | [9 empty] | 0x05002990
TISKlima1VisokPritiskVKrogu2_omog | DIGITAL | IOD_TIS_disk | D1318 | [9 empty] | 0x050029a0
TISKlima1IzlivVode_omog | DIGITAL | IOD_TIS_disk | D1319 | [9 empty] | 0x050029b0
TISKlima1ZunanjiAlarm_omog | DIGITAL | IOD_TIS_disk | D1320 | [9 empty] | 0x050029c0
TISKlima1TermZascVisokPritiskKpr1_omog | DIGITAL | IOD_TIS_disk | D1321 | [9 empty] | 0x050029d0
TISKlima1VlazilecNaMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1322 | [9 empty] | 0x050029e0
TISKlima1TermZascVisokPritiskKpr2_omog | DIGITAL | IOD_TIS_disk | D1323 | [9 empty] | 0x050029f0
TISKlima1Kond1FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1324 | [9 empty] | 0x05002a00
TISKlima1Kond2FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1325 | [9 empty] | 0x05002a10
TISKlima1NapakaPriPretokuVode_omog | DIGITAL | IOD_TIS_disk | D1326 | [9 empty] | 0x05002a20
TISKlima1RocniIzklop_omog | DIGITAL | IOD_TIS_disk | D1327 | [9 empty] | 0x05002a30
TISKlima1Napaka_omog | DIGITAL | IOD_TIS_disk | D1328 | [9 empty] | 0x05002a40
TISKlima2AlarmKompresor1_omog | DIGITAL | IOD_TIS_disk | D1329 | [9 empty] | 0x05002a50
TISKlima2AlarmKompresor2_omog | DIGITAL | IOD_TIS_disk | D1330 | [9 empty] | 0x05002a60
TISKlima2NizekPritiskKompresor1_omog | DIGITAL | IOD_TIS_disk | D1331 | [9 empty] | 0x05002a70
TISKlima2NizekPritiskKompresor2_omog | DIGITAL | IOD_TIS_disk | D1332 | [9 empty] | 0x05002a80
TISKlima2NapakaPriPretokuZraka_omog | DIGITAL | IOD_TIS_disk | D1333 | [9 empty] | 0x05002a90
TISKlima2FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1334 | [9 empty] | 0x05002aa0
TISKlima2ThermalCutoutHeater1_omog | DIGITAL | IOD_TIS_disk | D1335 | [9 empty] | 0x05002ab0
TISKlima2ThermalCutoutHeater2_omog | DIGITAL | IOD_TIS_disk | D1336 | [9 empty] | 0x05002ac0
TISKlima2PozarniAlarm_omog | DIGITAL | IOD_TIS_disk | D1337 | [9 empty] | 0x05002ad0
TISKlima2ZamasenFilter_omog | DIGITAL | IOD_TIS_disk | D1338 | [9 empty] | 0x05002ae0
TISKlima2VisokaTempVProstoru_omog | DIGITAL | IOD_TIS_disk | D1339 | [9 empty] | 0x05002af0
TISKlima2NizkaTempVProstoru_omog | DIGITAL | IOD_TIS_disk | D1340 | [9 empty] | 0x05002b00
TISKlima2VisokaVlaznost_omog | DIGITAL | IOD_TIS_disk | D1341 | [9 empty] | 0x05002b10
TISKlima2NizkaVlaznost_omog | DIGITAL | IOD_TIS_disk | D1342 | [9 empty] | 0x05002b20
TISKlima2Kompresor1naMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1343 | [9 empty] | 0x05002b30
TISKlima2Kompresor2naMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1344 | [9 empty] | 0x05002b40
TISKlima2VentilatorNaMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1345 | [9 empty] | 0x05002b50
TISKlima2NapakaSenzorTempProstora_omog | DIGITAL | IOD_TIS_disk | D1346 | [9 empty] | 0x05002b60
TISKlima2NapakaSenzorPovratVode_omog | DIGITAL | IOD_TIS_disk | D1347 | [9 empty] | 0x05002b70
TISKlima2NapakaSenzorZunanjeTemp_omog | DIGITAL | IOD_TIS_disk | D1348 | [9 empty] | 0x05002b80
TISKlima2NapakaSenzorTempIzpiha_omog | DIGITAL | IOD_TIS_disk | D1349 | [9 empty] | 0x05002b90
TISKlima2NapakaSenzorVlaznosti_omog | DIGITAL | IOD_TIS_disk | D1350 | [9 empty] | 0x05002ba0
TISKlima2NapakaSenzorPritiska1_omog | DIGITAL | IOD_TIS_disk | D1351 | [9 empty] | 0x05002bb0
TISKlima2NapakaSenzorPritiska2_omog | DIGITAL | IOD_TIS_disk | D1352 | [9 empty] | 0x05002bc0
TISKlima2NapakaSenzorKondTemp1_omog | DIGITAL | IOD_TIS_disk | D1353 | [9 empty] | 0x05002bd0
TISKlima2NapakaSenzorKondTemp2_omog | DIGITAL | IOD_TIS_disk | D1354 | [9 empty] | 0x05002be0
TISKlima2VisokTokVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1355 | [9 empty] | 0x05002bf0
TISKlima2NiVodeVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1356 | [9 empty] | 0x05002c00
TISKlima2NiTokaVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1357 | [9 empty] | 0x05002c10
TISKlima2ClockCardFault_omog | DIGITAL | IOD_TIS_disk | D1358 | [9 empty] | 0x05002c20
TISKlima2VisokPritiskVKrogu1_omog | DIGITAL | IOD_TIS_disk | D1359 | [9 empty] | 0x05002c30
TISKlima2VisokPritiskVKrogu2_omog | DIGITAL | IOD_TIS_disk | D1360 | [9 empty] | 0x05002c40
TISKlima2IzlivVode_omog | DIGITAL | IOD_TIS_disk | D1361 | [9 empty] | 0x05002c50
TISKlima2ZunanjiAlarm_omog | DIGITAL | IOD_TIS_disk | D1362 | [9 empty] | 0x05002c60
TISKlima2TermZascVisokPritiskKpr1_omog | DIGITAL | IOD_TIS_disk | D1363 | [9 empty] | 0x05002c70
TISKlima2VlazilecNaMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1364 | [9 empty] | 0x05002c80
TISKlima2TermZascVisokPritiskKpr2_omog | DIGITAL | IOD_TIS_disk | D1365 | [9 empty] | 0x05002c90
TISKlima2Kond1FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1366 | [9 empty] | 0x05002ca0
TISKlima2Kond2FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1367 | [9 empty] | 0x05002cb0
TISKlima2NapakaPriPretokuVode_omog | DIGITAL | IOD_TIS_disk | D1368 | [9 empty] | 0x05002cc0
TISKlima2RocniIzklop_omog | DIGITAL | IOD_TIS_disk | D1369 | [9 empty] | 0x05002cd0
TISKlima2Napaka_omog | DIGITAL | IOD_TIS_disk | D1370 | [9 empty] | 0x05002ce0
TISKlima3AlarmKompresor1_omog | DIGITAL | IOD_TIS_disk | D1371 | [9 empty] | 0x05002cf0
TISKlima3AlarmKompresor2_omog | DIGITAL | IOD_TIS_disk | D1372 | [9 empty] | 0x05002d00
TISKlima3NizekPritiskKompresor1_omog | DIGITAL | IOD_TIS_disk | D1373 | [9 empty] | 0x05002d10
TISKlima3NizekPritiskKompresor2_omog | DIGITAL | IOD_TIS_disk | D1374 | [9 empty] | 0x05002d20
TISKlima3NapakaPriPretokuZraka_omog | DIGITAL | IOD_TIS_disk | D1375 | [9 empty] | 0x05002d30
TISKlima3FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1376 | [9 empty] | 0x05002d40
TISKlima3ThermalCutoutHeater1_omog | DIGITAL | IOD_TIS_disk | D1377 | [9 empty] | 0x05002d50
TISKlima3ThermalCutoutHeater2_omog | DIGITAL | IOD_TIS_disk | D1378 | [9 empty] | 0x05002d60
TISKlima3PozarniAlarm_omog | DIGITAL | IOD_TIS_disk | D1379 | [9 empty] | 0x05002d70
TISKlima3ZamasenFilter_omog | DIGITAL | IOD_TIS_disk | D1380 | [9 empty] | 0x05002d80
TISKlima3VisokaTempVProstoru_omog | DIGITAL | IOD_TIS_disk | D1381 | [9 empty] | 0x05002d90
TISKlima3NizkaTempVProstoru_omog | DIGITAL | IOD_TIS_disk | D1382 | [9 empty] | 0x05002da0
TISKlima3VisokaVlaznost_omog | DIGITAL | IOD_TIS_disk | D1383 | [9 empty] | 0x05002db0
TISKlima3NizkaVlaznost_omog | DIGITAL | IOD_TIS_disk | D1384 | [9 empty] | 0x05002dc0
TISKlima3Kompresor1naMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1385 | [9 empty] | 0x05002dd0
TISKlima3Kompresor2naMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1386 | [9 empty] | 0x05002de0
TISKlima3VentilatorNaMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1387 | [9 empty] | 0x05002df0
TISKlima3NapakaSenzorTempProstora_omog | DIGITAL | IOD_TIS_disk | D1388 | [9 empty] | 0x05002e00
TISKlima3NapakaSenzorPovratVode_omog | DIGITAL | IOD_TIS_disk | D1389 | [9 empty] | 0x05002e10
TISKlima3NapakaSenzorZunanjeTemp_omog | DIGITAL | IOD_TIS_disk | D1390 | [9 empty] | 0x05002e20
TISKlima3NapakaSenzorTempIzpiha_omog | DIGITAL | IOD_TIS_disk | D1391 | [9 empty] | 0x05002e30
TISKlima3NapakaSenzorVlaznosti_omog | DIGITAL | IOD_TIS_disk | D1392 | [9 empty] | 0x05002e40
TISKlima3NapakaSenzorPritiska1_omog | DIGITAL | IOD_TIS_disk | D1393 | [9 empty] | 0x05002e50
TISKlima3NapakaSenzorPritiska2_omog | DIGITAL | IOD_TIS_disk | D1394 | [9 empty] | 0x05002e60
TISKlima3NapakaSenzorKondTemp1_omog | DIGITAL | IOD_TIS_disk | D1395 | [9 empty] | 0x05002e70
TISKlima3NapakaSenzorKondTemp2_omog | DIGITAL | IOD_TIS_disk | D1396 | [9 empty] | 0x05002e80
TISKlima3VisokTokVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1397 | [9 empty] | 0x05002e90
TISKlima3NiVodeVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1398 | [9 empty] | 0x05002ea0
TISKlima3NiTokaVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1399 | [9 empty] | 0x05002eb0
TISKlima3ClockCardFault_omog | DIGITAL | IOD_TIS_disk | D1400 | [9 empty] | 0x05002ec0
TISKlima3VisokPritiskVKrogu1_omog | DIGITAL | IOD_TIS_disk | D1401 | [9 empty] | 0x05002ed0
TISKlima3VisokPritiskVKrogu2_omog | DIGITAL | IOD_TIS_disk | D1402 | [9 empty] | 0x05002ee0
TISKlima3IzlivVode_omog | DIGITAL | IOD_TIS_disk | D1403 | [9 empty] | 0x05002ef0
TISKlima3ZunanjiAlarm_omog | DIGITAL | IOD_TIS_disk | D1404 | [9 empty] | 0x05002f00
TISKlima3TermZascVisokPritiskKpr1_omog | DIGITAL | IOD_TIS_disk | D1405 | [9 empty] | 0x05002f10
TISKlima3VlazilecNaMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1406 | [9 empty] | 0x05002f20
TISKlima3TermZascVisokPritiskKpr2_omog | DIGITAL | IOD_TIS_disk | D1407 | [9 empty] | 0x05002f30
TISKlima3Kond1FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1408 | [9 empty] | 0x05002f40
TISKlima3Kond2FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1409 | [9 empty] | 0x05002f50
TISKlima3NapakaPriPretokuVode_omog | DIGITAL | IOD_TIS_disk | D1410 | [9 empty] | 0x05002f60
TISKlima3RocniIzklop_omog | DIGITAL | IOD_TIS_disk | D1411 | [9 empty] | 0x05002f70
TISKlima3Napaka_omog | DIGITAL | IOD_TIS_disk | D1412 | [9 empty] | 0x05002f80
ATIS_omogoci_sms | DIGITAL | IOD_TIS_disk | D1414[300] | [9 empty] | 0x05002f90
BTIS_omogoci_sms | DIGITAL | IOD_TIS_disk | D1716[300] | [9 empty] | 0x05002fa0
CTIS_omogoci_sms | DIGITAL | IOD_TIS_disk | D2018[300] | [9 empty] | 0x05002fb0
DTIS_omogoci_sms | DIGITAL | IOD_TIS_disk | D2320[300] | [9 empty] | 0x05002fc0
ETIS_omogoci_sms | DIGITAL | IOD_TIS_disk | D2622[300] | [9 empty] | 0x05002fd0
FTIS_omogoci_sms | DIGITAL | IOD_TIS_disk | D2924[300] | [9 empty] | 0x05002fe0
TISUserLoggedIn_mem | DIGITAL | IOD_TIS_disk | D3226 | [9 empty] | 0x05002ff0
TISErrComKlima1_omog | DIGITAL | IOD_TIS_disk | D3227 | [9 empty] | 0x05003000
TIS_omogocanje_tok_alarm1 | DIGITAL | IOD_TIS_disk | D3229 | [9 empty] | 0x05003010
TIS_omogocanje_tok_alarm2 | DIGITAL | IOD_TIS_disk | D3230 | [9 empty] | 0x05003020
TIS_omogocanje_tok_alarm3 | DIGITAL | IOD_TIS_disk | D3231 | [9 empty] | 0x05003030
TIS_omogocanje_tok_alarm4 | DIGITAL | IOD_TIS_disk | D3232 | [9 empty] | 0x05003040
TIS_omogocanje_tok_alarm5 | DIGITAL | IOD_TIS_disk | D3233 | [9 empty] | 0x05003050
TIS_omogocanje_tok_alarm6 | DIGITAL | IOD_TIS_disk | D3234 | [9 empty] | 0x05003060
TIS_omogocanje_tok_alarm7 | DIGITAL | IOD_TIS_disk | D3235 | [9 empty] | 0x05003070
TIS_omogocanje_tok_alarm8 | DIGITAL | IOD_TIS_disk | D3236 | [9 empty] | 0x05003080
TIS_omogocanje_tok_alarm9 | DIGITAL | IOD_TIS_disk | D3237 | [9 empty] | 0x05003090
TIS_omogocanje_tok_alarm10 | DIGITAL | IOD_TIS_disk | D3238 | [9 empty] | 0x050030a0
TIS_omogocanje_tok_alarm11 | DIGITAL | IOD_TIS_disk | D3239 | [9 empty] | 0x050030b0
TIS_omogocanje_tok_alarm12 | DIGITAL | IOD_TIS_disk | D3240 | [9 empty] | 0x050030c0
TIS_omogocanje_tok_opozorila1 | DIGITAL | IOD_TIS_disk | D3241 | [9 empty] | 0x050030d0
TIS_omogocanje_tok_opozorila2 | DIGITAL | IOD_TIS_disk | D3242 | [9 empty] | 0x050030e0
TIS_omogocanje_tok_opozorila3 | DIGITAL | IOD_TIS_disk | D3243 | [9 empty] | 0x050030f0
TIS_omogocanje_tok_opozorila4 | DIGITAL | IOD_TIS_disk | D3244 | [9 empty] | 0x05003100
TIS_omogocanje_tok_opozorila5 | DIGITAL | IOD_TIS_disk | D3245 | [9 empty] | 0x05003110
TIS_omogocanje_tok_opozorila6 | DIGITAL | IOD_TIS_disk | D3246 | [9 empty] | 0x05003120
TIS_omogocanje_tok_opozorila7 | DIGITAL | IOD_TIS_disk | D3247 | [9 empty] | 0x05003130
TIS_omogocanje_tok_opozorila8 | DIGITAL | IOD_TIS_disk | D3248 | [9 empty] | 0x05003140
TIS_omogocanje_tok_opozorila9 | DIGITAL | IOD_TIS_disk | D3249 | [9 empty] | 0x05003150
TIS_omogocanje_tok_opozorila10 | DIGITAL | IOD_TIS_disk | D3250 | [9 empty] | 0x05003160
TIS_omogocanje_tok_opozorila11 | DIGITAL | IOD_TIS_disk | D3251 | [9 empty] | 0x05003170
TIS_omogocanje_tok_opozorila12 | DIGITAL | IOD_TIS_disk | D3252 | [9 empty] | 0x05003180
TIS_meja_tok_opozorilo1 | LONG | IOD_TIS_disk | L3278 | [9 empty] | 0x05003190
TIS_meja_tok_opozorilo2 | LONG | IOD_TIS_disk | L3280 | [9 empty] | 0x05003191
TIS_meja_tok_opozorilo3 | LONG | IOD_TIS_disk | L3282 | [9 empty] | 0x05003192
TIS_meja_tok_opozorilo4 | LONG | IOD_TIS_disk | L3284 | [9 empty] | 0x05003193
TIS_meja_tok_opozorilo5 | LONG | IOD_TIS_disk | L3286 | [9 empty] | 0x05003194
TIS_meja_tok_opozorilo6 | LONG | IOD_TIS_disk | L3288 | [9 empty] | 0x05003195
TIS_meja_tok_opozorilo7 | LONG | IOD_TIS_disk | L3290 | [9 empty] | 0x05003196
TIS_meja_tok_opozorilo8 | LONG | IOD_TIS_disk | L3292 | [9 empty] | 0x05003197
TIS_meja_tok_opozorilo9 | LONG | IOD_TIS_disk | L3294 | [9 empty] | 0x05003198
TIS_meja_tok_opozorilo10 | LONG | IOD_TIS_disk | L3296 | [9 empty] | 0x05003199
TIS_meja_tok_opozorilo11 | LONG | IOD_TIS_disk | L3298 | [9 empty] | 0x0500319a
TIS_meja_tok_opozorilo12 | LONG | IOD_TIS_disk | L3300 | [9 empty] | 0x0500319b
TIS_meja_tok_alarm1 | LONG | IOD_TIS_disk | L3302 | [9 empty] | 0x0500319c
TIS_meja_tok_alarm2 | LONG | IOD_TIS_disk | L3304 | [9 empty] | 0x0500319d
TIS_meja_tok_alarm3 | LONG | IOD_TIS_disk | L3306 | [9 empty] | 0x0500319e
TIS_meja_tok_alarm4 | LONG | IOD_TIS_disk | L3308 | [9 empty] | 0x0500319f
TIS_meja_tok_alarm5 | LONG | IOD_TIS_disk | L3310 | [9 empty] | 0x050031a0
TIS_meja_tok_alarm6 | LONG | IOD_TIS_disk | L3312 | [9 empty] | 0x050031a1
TIS_meja_tok_alarm7 | LONG | IOD_TIS_disk | L3314 | [9 empty] | 0x050031a2
TIS_meja_tok_alarm8 | LONG | IOD_TIS_disk | L3316 | [9 empty] | 0x050031a3
TIS_meja_tok_alarm9 | LONG | IOD_TIS_disk | L3318 | [9 empty] | 0x050031a4
TIS_meja_tok_alarm10 | LONG | IOD_TIS_disk | L3320 | [9 empty] | 0x050031a5
TIS_meja_tok_alarm11 | LONG | IOD_TIS_disk | L3322 | [9 empty] | 0x050031a6
TIS_meja_tok_alarm12 | LONG | IOD_TIS_disk | L3324 | [9 empty] | 0x050031a7
TIS_Anali_razlika_dnevna_E_G3 | REAL | IOD_TIS_disk | R3774 | [9 empty] | 0x050031a8
TIS_Anali_razlika_teden_E_G3 | REAL | IOD_TIS_disk | R3776 | [9 empty] | 0x050031a9
TIS_Anali_razlika_mes_E_G3 | REAL | IOD_TIS_disk | R3778 | [9 empty] | 0x050031aa
TIS_Anali_razlika_dnevna_E_DG3 | REAL | IOD_TIS_disk | R3780 | [9 empty] | 0x050031ab
TIS_Anali_razlika_teden_E_DG3 | REAL | IOD_TIS_disk | R3782 | [9 empty] | 0x050031ac
TIS_Anali_razlika_mes_E_DG3 | REAL | IOD_TIS_disk | R3784 | [9 empty] | 0x050031ad
TIS_Anali_razlika_dnevna_E_UPS3 | REAL | IOD_TIS_disk | R3786 | [9 empty] | 0x050031ae
TIS_Anali_razlika_teden_E_UPS3 | REAL | IOD_TIS_disk | R3788 | [9 empty] | 0x050031af
TIS_Anali_razlika_mes_E_UPS3 | REAL | IOD_TIS_disk | R3790 | [9 empty] | 0x050031b0
TIS_Anali_razlika_dnevna_E_DG4 | REAL | IOD_TIS_disk | R3792 | [9 empty] | 0x050031b1
TIS_Anali_razlika_teden_E_DG4 | REAL | IOD_TIS_disk | R3794 | [9 empty] | 0x050031b2
TIS_Anali_razlika_mes_E_DG4 | REAL | IOD_TIS_disk | R3796 | [9 empty] | 0x050031b3
TISDI_RazlitjeVodeHO1_omog | DIGITAL | IOD_TIS_disk | D3376 | [9 empty] | 0x050031c0
TISDI_RazlitjeVodeHO2_omog | DIGITAL | IOD_TIS_disk | D3377 | [9 empty] | 0x050031d0
TISDI_RazlitjeVodeHO3_omog | DIGITAL | IOD_TIS_disk | D3378 | [9 empty] | 0x050031e0
TISDI_F1_OdklHlOm1_ON_omog | DIGITAL | IOD_TIS_disk | D3379 | [9 empty] | 0x050031f0
TISDI_F2_OdklHlOm2_ON_omog | DIGITAL | IOD_TIS_disk | D3380 | [9 empty] | 0x05003200
TISDI_F3_OdklHlOm3_ON_omog | DIGITAL | IOD_TIS_disk | D3381 | [9 empty] | 0x05003210
TISDI_F4_OdkPripVode_ON_omog | DIGITAL | IOD_TIS_disk | D3382 | [9 empty] | 0x05003220
TISDI_HladOmara1_ON_omog | DIGITAL | IOD_TIS_disk | D3383 | [9 empty] | 0x05003230
TISDI_HladOmara2_ON_omog | DIGITAL | IOD_TIS_disk | D3384 | [9 empty] | 0x05003240
TISDI_HladOmara3_ON_omog | DIGITAL | IOD_TIS_disk | D3385 | [9 empty] | 0x05003250
TISDI_PripVode1_ON_omog | DIGITAL | IOD_TIS_disk | D3386 | [9 empty] | 0x05003260
TISDI_PripVode2_ON_omog | DIGITAL | IOD_TIS_disk | D3387 | [9 empty] | 0x05003270
TISDI_Q0_DEG3_ON_omog | DIGITAL | IOD_TIS_disk | D3388 | [9 empty] | 0x05003280
TISDI_Q0_EG3_ON_omog | DIGITAL | IOD_TIS_disk | D3389 | [9 empty] | 0x05003290
TISDI_Q0_GlavnoStikalo_ON_omog | DIGITAL | IOD_TIS_disk | D3390 | [9 empty] | 0x050032a0
TISDI_Q0_UPS3_ON_omog | DIGITAL | IOD_TIS_disk | D3391 | [9 empty] | 0x050032b0
TISDI_UPS_BatNacin_omog | DIGITAL | IOD_TIS_disk | D3392 | [9 empty] | 0x050032c0
TISDI_UPS_Polnjenje_omog | DIGITAL | IOD_TIS_disk | D3393 | [9 empty] | 0x050032d0
TISDI_Vlazilec1_ON_omog | DIGITAL | IOD_TIS_disk | D3394 | [9 empty] | 0x050032e0
TISDI_Vlazilec2_ON_omog | DIGITAL | IOD_TIS_disk | D3395 | [9 empty] | 0x050032f0
TISDI_Vlazilec3_ON_omog | DIGITAL | IOD_TIS_disk | D3396 | [9 empty] | 0x05003300
TISKlima1Razvlazevanje_omog | DIGITAL | IOD_TIS_disk | D3397 | [9 empty] | 0x05003310
TISKlima1VentilGretjeOdpiranje_omog | DIGITAL | IOD_TIS_disk | D3398 | [9 empty] | 0x05003320
TISKlima1VentilGretjeZapiranje_omog | DIGITAL | IOD_TIS_disk | D3399 | [9 empty] | 0x05003330
TISKlima1Vlazenje_omog | DIGITAL | IOD_TIS_disk | D3400 | [9 empty] | 0x05003340
TISKlima1Deluje_omog | DIGITAL | IOD_TIS_disk | D3401 | [9 empty] | 0x05003350
TISKlima2Razvlazevanje_omog | DIGITAL | IOD_TIS_disk | D3402 | [9 empty] | 0x05003360
TISKlima2VentilGretjeOdpiranje_omog | DIGITAL | IOD_TIS_disk | D3403 | [9 empty] | 0x05003370
TISKlima2VentilGretjeZapiranje_omog | DIGITAL | IOD_TIS_disk | D3404 | [9 empty] | 0x05003380
TISKlima2Vlazenje_omog | DIGITAL | IOD_TIS_disk | D3405 | [9 empty] | 0x05003390
TISKlima2Deluje_omog | DIGITAL | IOD_TIS_disk | D3406 | [9 empty] | 0x050033a0
TISKlima3Razvlazevanje_omog | DIGITAL | IOD_TIS_disk | D3407 | [9 empty] | 0x050033b0
TISKlima3VentilGretjeOdpiranje_omog | DIGITAL | IOD_TIS_disk | D3408 | [9 empty] | 0x050033c0
TISKlima3VentilGretjeZapiranje_omog | DIGITAL | IOD_TIS_disk | D3409 | [9 empty] | 0x050033d0
TISKlima3Vlazenje_omog | DIGITAL | IOD_TIS_disk | D3410 | [9 empty] | 0x050033e0
TISKlima3Deluje_omog | DIGITAL | IOD_TIS_disk | D3411 | [9 empty] | 0x050033f0
NeTISDI_F1_OdklHlOm1_ON_omog | DIGITAL | IOD_TIS_disk | D3412 | [9 empty] | 0x05003400
NeTISDI_F2_OdklHlOm2_ON_omog | DIGITAL | IOD_TIS_disk | D3413 | [9 empty] | 0x05003410
NeTISDI_F3_OdklHlOm3_ON_omog | DIGITAL | IOD_TIS_disk | D3414 | [9 empty] | 0x05003420
NeTISDI_F4_OdkPripVode_ON_omog | DIGITAL | IOD_TIS_disk | D3415 | [9 empty] | 0x05003430
NeTISDI_Q0_DEG3_ON_omog | DIGITAL | IOD_TIS_disk | D3416 | [9 empty] | 0x05003440
NeTISDI_Q0_EG3_ON_omog | DIGITAL | IOD_TIS_disk | D3417 | [9 empty] | 0x05003450
NeTISDI_Q0_GlavnoStikalo_ON_omog | DIGITAL | IOD_TIS_disk | D3418 | [9 empty] | 0x05003460
NeTISDI_Q0_UPS3_ON_omog | DIGITAL | IOD_TIS_disk | D3419 | [9 empty] | 0x05003470
TIS_ComScadaPlc_omog2 | DIGITAL | IOD_TIS_disk | D3420 | [9 empty] | 0x05003480
TISComSCADA2 | DIGITAL | IOD_TIS | TIS:.ComSCADA2 | [9 empty] | 0x05003490
TISErrCommScada2 | DIGITAL | IOD_TIS | TIS:.ErrCommScada2 | [9 empty] | 0x050034a0
TISServer_A_Izpad | DIGITAL | IOD_TIS_disk | D3423 | [9 empty] | 0x050034b0
TISServer_B_Izpad | DIGITAL | IOD_TIS_disk | D3424 | [9 empty] | 0x050034c0
TISComSCADA_stevec3 | INT | IOD_TIS_mem | I3426 | [9 empty] | 0x050034d0
TISComSCADA_stevec | INT | IOD_TIS_mem | I3428 | [9 empty] | 0x050034d1
TISComSCADA3 | DIGITAL | IOD_TIS | TIS:.ComSCADA3 | [9 empty] | 0x050034e0
TISkom_nast_cas_izpada | INT | IOD_TIS | TIS:.kom_nast_cas_izpada | [9 empty] | 0x050034f0
TISCirc1MaximumDemandA2 | REAL | IOD_TIS | TIS:.Circ[1].MaximumDemandA2 | 0 | 1200.0 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x050034f1
TISCirc1MaximumDemandA3 | REAL | IOD_TIS | TIS:.Circ[1].MaximumDemandA3 | 0 | 1200.0 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x050034f2
TISCirc2MaximumDemandA2 | REAL | IOD_TIS | TIS:.Circ[2].MaximumDemandA2 | 0 | 1200.0 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x050034f3
TISCirc2MaximumDemandA3 | REAL | IOD_TIS | TIS:.Circ[2].MaximumDemandA3 | 0 | 1200.0 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x050034f4
TISCirc3MaximumDemandA2 | REAL | IOD_TIS | TIS:.Circ[3].MaximumDemandA2 | 0 | 1200.0 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x050034f5
TISCirc3MaximumDemandA3 | REAL | IOD_TIS | TIS:.Circ[3].MaximumDemandA3 | 0 | 1200.0 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x050034f6
TISCirc4MaximumDemandA2 | REAL | IOD_TIS | TIS:.Circ[4].MaximumDemandA2 | 0 | 1200.0 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x050034f7
TISCirc4MaximumDemandA3 | REAL | IOD_TIS | TIS:.Circ[4].MaximumDemandA3 | 0 | 1200.0 | 0 | 1200.0 | A | ###.# |  | 6157 | 1 | 0x050034f8
TISCirc1RazEner_D_SCADA | REAL | IOD_TIS | TIS:.Circ[1].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x050035c0
TISCirc1RazEner_T_SCADA | REAL | IOD_TIS | TIS:.Circ[1].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x050035c1
TISCirc1RazEner_M_SCADA | REAL | IOD_TIS | TIS:.Circ[1].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x050035c2
TISCirc2RazEner_D_SCADA | REAL | IOD_TIS | TIS:.Circ[2].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x050035c3
TISCirc2RazEner_T_SCADA | REAL | IOD_TIS | TIS:.Circ[2].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x050035c4
TISCirc2RazEner_M_SCADA | REAL | IOD_TIS | TIS:.Circ[2].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x050035c5
TISCirc3RazEner_D_SCADA | REAL | IOD_TIS | TIS:.Circ[3].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x050035c6
TISCirc3RazEner_T_SCADA | REAL | IOD_TIS | TIS:.Circ[3].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x050035c7
TISCirc3RazEner_M_SCADA | REAL | IOD_TIS | TIS:.Circ[3].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x050035c8
TISCirc4RazEner_D_SCADA | REAL | IOD_TIS | TIS:.Circ[4].RazEner_D_SCADA | [7 empty] | 6157 | 1 | 0x050035c9
TISCirc4RazEner_T_SCADA | REAL | IOD_TIS | TIS:.Circ[4].RazEner_T_SCADA | [7 empty] | 6157 | 1 | 0x050035ca
TISCirc4RazEner_M_SCADA | REAL | IOD_TIS | TIS:.Circ[4].RazEner_M_SCADA | [7 empty] | 6157 | 1 | 0x050035cb
TISCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Dnevne_energija_scada1 | [7 empty] | 6157 | 1 | 0x050035d0
TISCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Dnevne_energija_scada2 | [7 empty] | 6157 | 1 | 0x050035e0
TISCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Tedenska_energija_scada1 | [7 empty] | 6157 | 1 | 0x050035f0
TISCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Tedenska_energija_scada2 | [7 empty] | 6157 | 1 | 0x05003600
TISCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Mesecna_energija_scada1 | [7 empty] | 6157 | 1 | 0x05003610
TISCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Mesecna_energija_scada2 | [7 empty] | 6157 | 1 | 0x05003620
TISCirc_Vpis_Dnevne_energija_scada1_mem | DIGITAL | IOD_TIS_disk | D3425 | [9 empty] | 0x05003630
TISCirc_Vpis_Dnevne_energija_scada2_mem | DIGITAL | IOD_TIS_disk | D3426 | [9 empty] | 0x05003640
TISCirc_Vpis_Tedenska_energija_scada1_mem | DIGITAL | IOD_TIS_disk | D3427 | [9 empty] | 0x05003650
TISCirc_Vpis_Tedenska_energija_scada2_mem | DIGITAL | IOD_TIS_disk | D3428 | [9 empty] | 0x05003660
TISCirc_Vpis_Mesecna_energija_scada1_mem | DIGITAL | IOD_TIS_disk | D3429 | [9 empty] | 0x05003670
TISCirc_Vpis_Mesecna_energija_scada2_mem | DIGITAL | IOD_TIS_disk | D3430 | [9 empty] | 0x05003680

## variable_1
TISAlarmGenCirc1 | DIGITAL | IOD_TIS | TIS:.AlarmGenCirc1
TISAlarmGenCirc2 | DIGITAL | IOD_TIS | TIS:.AlarmGenCirc2
TISAlarmGenCirc3 | DIGITAL | IOD_TIS | TIS:.AlarmGenCirc3
TISAlarmGenCirc4 | DIGITAL | IOD_TIS | TIS:.AlarmGenCirc4
TISAlarmGenComm | DIGITAL | IOD_TIS | TIS:.AlarmGenComm
TISAlarmGenDI | DIGITAL | IOD_TIS | TIS:.AlarmGenDI
TISAlarmGenKlima1 | DIGITAL | IOD_TIS | TIS:.AlarmGenKlima1
TISAlarmGenKlima2 | DIGITAL | IOD_TIS | TIS:.AlarmGenKlima2
TISAlarmGenKlima3 | DIGITAL | IOD_TIS | TIS:.AlarmGenKlima3
TISAlarmGenRest | DIGITAL | IOD_TIS | TIS:.AlarmGenRest
TISAlarmGenSenzor | DIGITAL | IOD_TIS | TIS:.AlarmGenSenzor
TISAlarmGenTemp | DIGITAL | IOD_TIS | TIS:.AlarmGenTemp
TISAlarmGenVlPr | DIGITAL | IOD_TIS | TIS:.AlarmGenVlPr
TISAlarmGenVTV | DIGITAL | IOD_TIS | TIS:.AlarmGenVTV
TISCirc1CosFi_III | REAL | IOD_TIS | TIS:.Circ[1].CosFi_III
TISCirc1DelovnaEnergija | REAL | IOD_TIS | TIS:.Circ[1].DelovnaEnergija
TISCirc1DelovnaMoc_III | REAL | IOD_TIS | TIS:.Circ[1].DelovnaMoc_III
TISCirc1DelovnaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[1].DelovnaMoc_L1
TISCirc1DelovnaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[1].DelovnaMoc_L2
TISCirc1DelovnaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[1].DelovnaMoc_L3
TISCirc1Frekvenca_L1 | REAL | IOD_TIS | TIS:.Circ[1].Frekvenca_L1
TISCirc1InduktivnaEnergija | REAL | IOD_TIS | TIS:.Circ[1].InduktivnaEnergija
TISCirc1InduktivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[1].InduktivnaMoc_III
TISCirc1JalovaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[1].JalovaMoc_L1
TISCirc1JalovaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[1].JalovaMoc_L2
TISCirc1JalovaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[1].JalovaMoc_L3
TISCirc1KapacitivnaEnergija | REAL | IOD_TIS | TIS:.Circ[1].KapacitivnaEnergija
TISCirc1KapacitivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[1].KapacitivnaMoc_III
TISCirc1MaximumDemand | REAL | IOD_TIS | TIS:.Circ[1].MaximumDemand
TISCirc1Napetost_L1_L2 | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L1_L2
TISCirc1Napetost_L1_N | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L1_N
TISCirc1Napetost_L2_L3 | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L2_L3
TISCirc1Napetost_L2_N | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L2_N
TISCirc1Napetost_L3_L1 | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L3_L1
TISCirc1Napetost_L3_N | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L3_N
TISCirc1NavideznaMoc_III | REAL | IOD_TIS | TIS:.Circ[1].NavideznaMoc_III
TISCirc1NicelniTok | REAL | IOD_TIS | TIS:.Circ[1].NicelniTok
TISCirc1PowerFactor_III | REAL | IOD_TIS | TIS:.Circ[1].PowerFactor_III
TISCirc1PowerFactor_L1 | REAL | IOD_TIS | TIS:.Circ[1].PowerFactor_L1
TISCirc1PowerFactor_L2 | REAL | IOD_TIS | TIS:.Circ[1].PowerFactor_L2
TISCirc1PowerFactor_L3 | REAL | IOD_TIS | TIS:.Circ[1].PowerFactor_L3
TISCirc1THDI_L1 | REAL | IOD_TIS | TIS:.Circ[1].THDI_L1
TISCirc1THDI_L2 | REAL | IOD_TIS | TIS:.Circ[1].THDI_L2
TISCirc1THDI_L3 | REAL | IOD_TIS | TIS:.Circ[1].THDI_L3
TISCirc1THDV_L1 | REAL | IOD_TIS | TIS:.Circ[1].THDV_L1
TISCirc1THDV_L2 | REAL | IOD_TIS | TIS:.Circ[1].THDV_L2
TISCirc1THDV_L3 | REAL | IOD_TIS | TIS:.Circ[1].THDV_L3
TISCirc1Tok_L1 | REAL | IOD_TIS | TIS:.Circ[1].Tok_L1
TISCirc1Tok_L2 | REAL | IOD_TIS | TIS:.Circ[1].Tok_L2
TISCirc1Tok_L3 | REAL | IOD_TIS | TIS:.Circ[1].Tok_L3
TISCirc1TokPovprecje_III | REAL | IOD_TIS | TIS:.Circ[1].TokPovprecje_III
TISCirc2CosFi_III | REAL | IOD_TIS | TIS:.Circ[2].CosFi_III
TISCirc2DelovnaEnergija | REAL | IOD_TIS | TIS:.Circ[2].DelovnaEnergija
TISCirc2DelovnaMoc_III | REAL | IOD_TIS | TIS:.Circ[2].DelovnaMoc_III
TISCirc2DelovnaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[2].DelovnaMoc_L1
TISCirc2DelovnaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[2].DelovnaMoc_L2
TISCirc2DelovnaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[2].DelovnaMoc_L3
TISCirc2Frekvenca_L1 | REAL | IOD_TIS | TIS:.Circ[2].Frekvenca_L1
TISCirc2InduktivnaEnergija | REAL | IOD_TIS | TIS:.Circ[2].InduktivnaEnergija
TISCirc2InduktivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[2].InduktivnaMoc_III
TISCirc2JalovaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[2].JalovaMoc_L1
TISCirc2JalovaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[2].JalovaMoc_L2
TISCirc2JalovaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[2].JalovaMoc_L3
TISCirc2KapacitivnaEnergija | REAL | IOD_TIS | TIS:.Circ[2].KapacitivnaEnergija
TISCirc2KapacitivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[2].KapacitivnaMoc_III
TISCirc2MaximumDemand | REAL | IOD_TIS | TIS:.Circ[2].MaximumDemand
TISCirc2Napetost_L1_L2 | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L1_L2
TISCirc2Napetost_L1_N | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L1_N
TISCirc2Napetost_L2_L3 | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L2_L3
TISCirc2Napetost_L2_N | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L2_N
TISCirc2Napetost_L3_L1 | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L3_L1
TISCirc2Napetost_L3_N | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L3_N
TISCirc2NavideznaMoc_III | REAL | IOD_TIS | TIS:.Circ[2].NavideznaMoc_III
TISCirc2NicelniTok | REAL | IOD_TIS | TIS:.Circ[2].NicelniTok
TISCirc2PowerFactor_III | REAL | IOD_TIS | TIS:.Circ[2].PowerFactor_III
TISCirc2PowerFactor_L1 | REAL | IOD_TIS | TIS:.Circ[2].PowerFactor_L1
TISCirc2PowerFactor_L2 | REAL | IOD_TIS | TIS:.Circ[2].PowerFactor_L2
TISCirc2PowerFactor_L3 | REAL | IOD_TIS | TIS:.Circ[2].PowerFactor_L3
TISCirc2THDI_L1 | REAL | IOD_TIS | TIS:.Circ[2].THDI_L1
TISCirc2THDI_L2 | REAL | IOD_TIS | TIS:.Circ[2].THDI_L2
TISCirc2THDI_L3 | REAL | IOD_TIS | TIS:.Circ[2].THDI_L3
TISCirc2THDV_L1 | REAL | IOD_TIS | TIS:.Circ[2].THDV_L1
TISCirc2THDV_L2 | REAL | IOD_TIS | TIS:.Circ[2].THDV_L2
TISCirc2THDV_L3 | REAL | IOD_TIS | TIS:.Circ[2].THDV_L3
TISCirc2Tok_L1 | REAL | IOD_TIS | TIS:.Circ[2].Tok_L1
TISCirc2Tok_L2 | REAL | IOD_TIS | TIS:.Circ[2].Tok_L2
TISCirc2Tok_L3 | REAL | IOD_TIS | TIS:.Circ[2].Tok_L3
TISCirc2TokPovprecje_III | REAL | IOD_TIS | TIS:.Circ[2].TokPovprecje_III
TISCirc3CosFi_III | REAL | IOD_TIS | TIS:.Circ[3].CosFi_III
TISCirc3DelovnaEnergija | REAL | IOD_TIS | TIS:.Circ[3].DelovnaEnergija
TISCirc3DelovnaMoc_III | REAL | IOD_TIS | TIS:.Circ[3].DelovnaMoc_III
TISCirc3DelovnaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[3].DelovnaMoc_L1
TISCirc3DelovnaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[3].DelovnaMoc_L2
TISCirc3DelovnaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[3].DelovnaMoc_L3
TISCirc3Frekvenca_L1 | REAL | IOD_TIS | TIS:.Circ[3].Frekvenca_L1
TISCirc3InduktivnaEnergija | REAL | IOD_TIS | TIS:.Circ[3].InduktivnaEnergija
TISCirc3InduktivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[3].InduktivnaMoc_III
TISCirc3JalovaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[3].JalovaMoc_L1
TISCirc3JalovaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[3].JalovaMoc_L2
TISCirc3JalovaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[3].JalovaMoc_L3
TISCirc3KapacitivnaEnergija | REAL | IOD_TIS | TIS:.Circ[3].KapacitivnaEnergija
TISCirc3KapacitivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[3].KapacitivnaMoc_III
TISCirc3MaximumDemand | REAL | IOD_TIS | TIS:.Circ[3].MaximumDemand
TISCirc3Napetost_L1_L2 | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L1_L2
TISCirc3Napetost_L1_N | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L1_N
TISCirc3Napetost_L2_L3 | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L2_L3
TISCirc3Napetost_L2_N | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L2_N
TISCirc3Napetost_L3_L1 | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L3_L1
TISCirc3Napetost_L3_N | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L3_N
TISCirc3NavideznaMoc_III | REAL | IOD_TIS | TIS:.Circ[3].NavideznaMoc_III
TISCirc3NicelniTok | REAL | IOD_TIS | TIS:.Circ[3].NicelniTok
TISCirc3PowerFactor_III | REAL | IOD_TIS | TIS:.Circ[3].PowerFactor_III
TISCirc3PowerFactor_L1 | REAL | IOD_TIS | TIS:.Circ[3].PowerFactor_L1
TISCirc3PowerFactor_L2 | REAL | IOD_TIS | TIS:.Circ[3].PowerFactor_L2
TISCirc3PowerFactor_L3 | REAL | IOD_TIS | TIS:.Circ[3].PowerFactor_L3
TISCirc3THDI_L1 | REAL | IOD_TIS | TIS:.Circ[3].THDI_L1
TISCirc3THDI_L2 | REAL | IOD_TIS | TIS:.Circ[3].THDI_L2
TISCirc3THDI_L3 | REAL | IOD_TIS | TIS:.Circ[3].THDI_L3
TISCirc3THDV_L1 | REAL | IOD_TIS | TIS:.Circ[3].THDV_L1
TISCirc3THDV_L2 | REAL | IOD_TIS | TIS:.Circ[3].THDV_L2
TISCirc3THDV_L3 | REAL | IOD_TIS | TIS:.Circ[3].THDV_L3
TISCirc3Tok_L1 | REAL | IOD_TIS | TIS:.Circ[3].Tok_L1
TISCirc3Tok_L2 | REAL | IOD_TIS | TIS:.Circ[3].Tok_L2
TISCirc3Tok_L3 | REAL | IOD_TIS | TIS:.Circ[3].Tok_L3
TISCirc3TokPovprecje_III | REAL | IOD_TIS | TIS:.Circ[3].TokPovprecje_III
TISCirc4CosFi_III | REAL | IOD_TIS | TIS:.Circ[4].CosFi_III
TISCirc4DelovnaEnergija | REAL | IOD_TIS | TIS:.Circ[4].DelovnaEnergija
TISCirc4DelovnaMoc_III | REAL | IOD_TIS | TIS:.Circ[4].DelovnaMoc_III
TISCirc4DelovnaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[4].DelovnaMoc_L1
TISCirc4DelovnaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[4].DelovnaMoc_L2
TISCirc4DelovnaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[4].DelovnaMoc_L3
TISCirc4Frekvenca_L1 | REAL | IOD_TIS | TIS:.Circ[4].Frekvenca_L1
TISCirc4InduktivnaEnergija | REAL | IOD_TIS | TIS:.Circ[4].InduktivnaEnergija
TISCirc4InduktivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[4].InduktivnaMoc_III
TISCirc4JalovaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[4].JalovaMoc_L1
TISCirc4JalovaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[4].JalovaMoc_L2
TISCirc4JalovaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[4].JalovaMoc_L3
TISCirc4KapacitivnaEnergija | REAL | IOD_TIS | TIS:.Circ[4].KapacitivnaEnergija
TISCirc4KapacitivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[4].KapacitivnaMoc_III
TISCirc4MaximumDemand | REAL | IOD_TIS | TIS:.Circ[4].MaximumDemand
TISCirc4Napetost_L1_L2 | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L1_L2
TISCirc4Napetost_L1_N | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L1_N
TISCirc4Napetost_L2_L3 | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L2_L3
TISCirc4Napetost_L2_N | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L2_N
TISCirc4Napetost_L3_L1 | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L3_L1
TISCirc4Napetost_L3_N | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L3_N
TISCirc4NavideznaMoc_III | REAL | IOD_TIS | TIS:.Circ[4].NavideznaMoc_III
TISCirc4NicelniTok | REAL | IOD_TIS | TIS:.Circ[4].NicelniTok
TISCirc4PowerFactor_III | REAL | IOD_TIS | TIS:.Circ[4].PowerFactor_III
TISCirc4PowerFactor_L1 | REAL | IOD_TIS | TIS:.Circ[4].PowerFactor_L1
TISCirc4PowerFactor_L2 | REAL | IOD_TIS | TIS:.Circ[4].PowerFactor_L2
TISCirc4PowerFactor_L3 | REAL | IOD_TIS | TIS:.Circ[4].PowerFactor_L3
TISCirc4THDI_L1 | REAL | IOD_TIS | TIS:.Circ[4].THDI_L1
TISCirc4THDI_L2 | REAL | IOD_TIS | TIS:.Circ[4].THDI_L2
TISCirc4THDI_L3 | REAL | IOD_TIS | TIS:.Circ[4].THDI_L3
TISCirc4THDV_L1 | REAL | IOD_TIS | TIS:.Circ[4].THDV_L1
TISCirc4THDV_L2 | REAL | IOD_TIS | TIS:.Circ[4].THDV_L2
TISCirc4THDV_L3 | REAL | IOD_TIS | TIS:.Circ[4].THDV_L3
TISCirc4Tok_L1 | REAL | IOD_TIS | TIS:.Circ[4].Tok_L1
TISCirc4Tok_L2 | REAL | IOD_TIS | TIS:.Circ[4].Tok_L2
TISCirc4Tok_L3 | REAL | IOD_TIS | TIS:.Circ[4].Tok_L3
TISCirc4TokPovprecje_III | REAL | IOD_TIS | TIS:.Circ[4].TokPovprecje_III
TISCircutorCosFi_III | REAL | IOD_TIS | TIS:.Circutor.CosFi_III
TISCircutorDelovnaEnergija | REAL | IOD_TIS | TIS:.Circutor.DelovnaEnergija
TISCircutorDelovnaMoc_III | REAL | IOD_TIS | TIS:.Circutor.DelovnaMoc_III
TISCircutorDelovnaMoc_L1 | REAL | IOD_TIS | TIS:.Circutor.DelovnaMoc_L1
TISCircutorDelovnaMoc_L2 | REAL | IOD_TIS | TIS:.Circutor.DelovnaMoc_L2
TISCircutorDelovnaMoc_L3 | REAL | IOD_TIS | TIS:.Circutor.DelovnaMoc_L3
TISCircutorFrekvenca_L1 | REAL | IOD_TIS | TIS:.Circutor.Frekvenca_L1
TISCircutorInduktivnaEnergija | REAL | IOD_TIS | TIS:.Circutor.InduktivnaEnergija
TISCircutorInduktivnaMoc_III | REAL | IOD_TIS | TIS:.Circutor.InduktivnaMoc_III
TISCircutorJalovaMoc_L1 | REAL | IOD_TIS | TIS:.Circutor.JalovaMoc_L1
TISCircutorJalovaMoc_L2 | REAL | IOD_TIS | TIS:.Circutor.JalovaMoc_L2
TISCircutorJalovaMoc_L3 | REAL | IOD_TIS | TIS:.Circutor.JalovaMoc_L3
TISCircutorKapacitivnaEnergija | REAL | IOD_TIS | TIS:.Circutor.KapacitivnaEnergija
TISCircutorKapacitivnaMoc_III | REAL | IOD_TIS | TIS:.Circutor.KapacitivnaMoc_III
TISCircutorMaximumDemand | REAL | IOD_TIS | TIS:.Circutor.MaximumDemand
TISCircutorNapetost_L1_L2 | REAL | IOD_TIS | TIS:.Circutor.Napetost_L1_L2
TISCircutorNapetost_L1_N | REAL | IOD_TIS | TIS:.Circutor.Napetost_L1_N
TISCircutorNapetost_L2_L3 | REAL | IOD_TIS | TIS:.Circutor.Napetost_L2_L3
TISCircutorNapetost_L2_N | REAL | IOD_TIS | TIS:.Circutor.Napetost_L2_N
TISCircutorNapetost_L3_L1 | REAL | IOD_TIS | TIS:.Circutor.Napetost_L3_L1
TISCircutorNapetost_L3_N | REAL | IOD_TIS | TIS:.Circutor.Napetost_L3_N
TISCircutorNavideznaMoc_III | REAL | IOD_TIS | TIS:.Circutor.NavideznaMoc_III
TISCircutorNicelniTok | REAL | IOD_TIS | TIS:.Circutor.NicelniTok
TISCircutorPowerFactor_III | REAL | IOD_TIS | TIS:.Circutor.PowerFactor_III
TISCircutorPowerFactor_L1 | REAL | IOD_TIS | TIS:.Circutor.PowerFactor_L1
TISCircutorPowerFactor_L2 | REAL | IOD_TIS | TIS:.Circutor.PowerFactor_L2
TISCircutorPowerFactor_L3 | REAL | IOD_TIS | TIS:.Circutor.PowerFactor_L3
TISCircutorTHDI_L1 | REAL | IOD_TIS | TIS:.Circutor.THDI_L1
TISCircutorTHDI_L2 | REAL | IOD_TIS | TIS:.Circutor.THDI_L2
TISCircutorTHDI_L3 | REAL | IOD_TIS | TIS:.Circutor.THDI_L3
TISCircutorTHDV_L1 | REAL | IOD_TIS | TIS:.Circutor.THDV_L1
TISCircutorTHDV_L2 | REAL | IOD_TIS | TIS:.Circutor.THDV_L2
TISCircutorTHDV_L3 | REAL | IOD_TIS | TIS:.Circutor.THDV_L3
TISCircutorTok_L1 | REAL | IOD_TIS | TIS:.Circutor.Tok_L1
TISCircutorTok_L2 | REAL | IOD_TIS | TIS:.Circutor.Tok_L2
TISCircutorTok_L3 | REAL | IOD_TIS | TIS:.Circutor.Tok_L3
TISCircutorTokPovprecje_III | REAL | IOD_TIS | TIS:.Circutor.TokPovprecje_III
TISComSCADA | DIGITAL | IOD_TIS | TIS:.ComSCADA
TISComSCADA1 | DIGITAL | IOD_TIS | TIS:.ComSCADA1
TISDate_Time0 | STRING | IOD_TIS | TIS:.Date_Time[0]
TISDate_Time1 | STRING | IOD_TIS | TIS:.Date_Time[1]
TISDate_Time2 | STRING | IOD_TIS | TIS:.Date_Time[2]
TISDate_Time3 | STRING | IOD_TIS | TIS:.Date_Time[3]
TISDateTimeDan | INT | IOD_TIS | TIS:.DateTime.Dan | BYTE
TISDateTimeLeto | INT | IOD_TIS | TIS:.DateTime.Leto | BYTE
TISDateTimeMesec | INT | IOD_TIS | TIS:.DateTime.Mesec | BYTE
TISDateTimeMinuta | INT | IOD_TIS | TIS:.DateTime.Minuta | BYTE
TISDateTimeSekunda | INT | IOD_TIS | TIS:.DateTime.Sekunda | BYTE
TISDateTimeUra | INT | IOD_TIS | TIS:.DateTime.Ura | BYTE
TISDI_F1_OdklHlOm1_IZP | DIGITAL | IOD_TIS | TIS:.DI_F1_OdklHlOm1_IZP
TISDI_F1_OdklHlOm1_ON | DIGITAL | IOD_TIS | TIS:.DI_F1_OdklHlOm1_ON
TISDI_F2_OdklHlOm2_IZP | DIGITAL | IOD_TIS | TIS:.DI_F2_OdklHlOm2_IZP
TISDI_F2_OdklHlOm2_ON | DIGITAL | IOD_TIS | TIS:.DI_F2_OdklHlOm2_ON
TISDI_F3_OdklHlOm3_IZP | DIGITAL | IOD_TIS | TIS:.DI_F3_OdklHlOm3_IZP
TISDI_F3_OdklHlOm3_ON | DIGITAL | IOD_TIS | TIS:.DI_F3_OdklHlOm3_ON
TISDI_F4_OdkPripVode_IZP | DIGITAL | IOD_TIS | TIS:.DI_F4_OdkPripVode_IZP
TISDI_F4_OdkPripVode_ON | DIGITAL | IOD_TIS | TIS:.DI_F4_OdkPripVode_ON
TISDI_HladOmara1_ERR | DIGITAL | IOD_TIS | TIS:.DI_HladOmara1_ERR
TISDI_HladOmara1_ON | DIGITAL | IOD_TIS | TIS:.DI_HladOmara1_ON
TISDI_HladOmara2_ERR | DIGITAL | IOD_TIS | TIS:.DI_HladOmara2_ERR
TISDI_HladOmara2_ON | DIGITAL | IOD_TIS | TIS:.DI_HladOmara2_ON
TISDI_HladOmara3_ERR | DIGITAL | IOD_TIS | TIS:.DI_HladOmara3_ERR
TISDI_HladOmara3_ON | DIGITAL | IOD_TIS | TIS:.DI_HladOmara3_ON
TISDI_PripVode1_ERR | DIGITAL | IOD_TIS | TIS:.DI_PripVode1_ERR
TISDI_PripVode1_ON | DIGITAL | IOD_TIS | TIS:.DI_PripVode1_ON
TISDI_PripVode2_ERR | DIGITAL | IOD_TIS | TIS:.DI_PripVode2_ERR
TISDI_PripVode2_ON | DIGITAL | IOD_TIS | TIS:.DI_PripVode2_ON
TISDI_Q0_DEG3_ON | DIGITAL | IOD_TIS | TIS:.DI_Q0_DEG3_ON
TISDI_Q0_EG3_ON | DIGITAL | IOD_TIS | TIS:.DI_Q0_EG3_ON
TISDI_Q0_GlavnoStikalo_ON | DIGITAL | IOD_TIS | TIS:.DI_Q0_GlavnoStikalo_ON
TISDI_Q0_UPS3_ON | DIGITAL | IOD_TIS | TIS:.DI_Q0_UPS3_ON
TISDI_RazlitjeVodeHO1 | DIGITAL | IOD_TIS | TIS:.DI_RazlitjeVodeHO1
TISDI_RazlitjeVodeHO2 | DIGITAL | IOD_TIS | TIS:.DI_RazlitjeVodeHO2
TISDI_RazlitjeVodeHO3 | DIGITAL | IOD_TIS | TIS:.DI_RazlitjeVodeHO3
TISDI_UPS_Alarm | DIGITAL | IOD_TIS | TIS:.DI_UPS_Alarm
TISDI_UPS_BatNacin | DIGITAL | IOD_TIS | TIS:.DI_UPS_BatNacin
TISDI_UPS_Polnjenje | DIGITAL | IOD_TIS | TIS:.DI_UPS_Polnjenje
TISDI_Vlazilec1_ERR | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec1_ERR
TISDI_Vlazilec1_ON | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec1_ON
TISDI_Vlazilec2_ERR | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec2_ERR
TISDI_Vlazilec2_ON | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec2_ON
TISDI_Vlazilec3_ERR | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec3_ERR
TISDI_Vlazilec3_ON | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec3_ON
TISDIN_F1_OdklHlOm1_IZP | DIGITAL | IOD_TIS | TIS:.DIN_F1_OdklHlOm1_IZP
TISDIN_F2_OdklHlOm2_IZP | DIGITAL | IOD_TIS | TIS:.DIN_F2_OdklHlOm2_IZP
TISDIN_F3_OdklHlOm3_IZP | DIGITAL | IOD_TIS | TIS:.DIN_F3_OdklHlOm3_IZP
TISDIN_F4_OdkPripVode_IZP | DIGITAL | IOD_TIS | TIS:.DIN_F4_OdkPripVode_IZP
TISDIN_HladOmara1_ERR | DIGITAL | IOD_TIS | TIS:.DIN_HladOmara1_ERR
TISDIN_HladOmara2_ERR | DIGITAL | IOD_TIS | TIS:.DIN_HladOmara2_ERR
TISDIN_HladOmara3_ERR | DIGITAL | IOD_TIS | TIS:.DIN_HladOmara3_ERR
TISDIN_PripVode1_ERR | DIGITAL | IOD_TIS | TIS:.DIN_PripVode1_ERR
TISDIN_PripVode2_ERR | DIGITAL | IOD_TIS | TIS:.DIN_PripVode2_ERR
TISDIN_Vlazilec1_ERR | DIGITAL | IOD_TIS | TIS:.DIN_Vlazilec1_ERR
TISDIN_Vlazilec2_ERR | DIGITAL | IOD_TIS | TIS:.DIN_Vlazilec2_ERR
TISDIN_Vlazilec3_ERR | DIGITAL | IOD_TIS | TIS:.DIN_Vlazilec3_ERR
TISDO_HladOm1_Izklop | DIGITAL | IOD_TIS | TIS:.DO_HladOm1_Izklop
TISDO_HladOm2_Izklop | DIGITAL | IOD_TIS | TIS:.DO_HladOm2_Izklop
TISDO_HladOm3_Izklop | DIGITAL | IOD_TIS | TIS:.DO_HladOm3_Izklop
TISErrComCirc1 | DIGITAL | IOD_TIS | TIS:.ErrComCirc[1]
TISErrComCirc2 | DIGITAL | IOD_TIS | TIS:.ErrComCirc[2]
TISErrComCirc3 | DIGITAL | IOD_TIS | TIS:.ErrComCirc[3]
TISErrComCirc4 | DIGITAL | IOD_TIS | TIS:.ErrComCirc[4]
TISErrComCirc5 | DIGITAL | IOD_TIS | TIS:.ErrComCirc[5]
TISErrComKlima1 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[1]
TISErrComKlima2 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[2]
TISErrComKlima3 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[3]
TISErrComKlima4 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[4]
TISErrComKlima5 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[5]
TISErrComKlima6 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[6]
TISErrCommScada | DIGITAL | IOD_TIS | TIS:.ErrCommScada
TISErrComPanelPLC | DIGITAL | IOD_TIS | TIS:.ErrComPanelPLC
TISErrComPort2 | DIGITAL | IOD_TIS | TIS:.ErrComPort2
TISErrorComCirc1Code10 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[10] | BYTE
TISErrorComCirc1Code11 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[11] | BYTE
TISErrorComCirc1Code12 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[12] | BYTE
TISErrorComCirc1Code13 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[13] | BYTE
TISErrorComCirc1Code14 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[14] | BYTE
TISErrorComCirc1Code15 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[15] | BYTE
TISErrorComCirc1Code1 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[1] | BYTE
TISErrorComCirc1Code2 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[2] | BYTE
TISErrorComCirc1Code3 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[3] | BYTE
TISErrorComCirc1Code4 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[4] | BYTE
TISErrorComCirc1Code5 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[5] | BYTE
TISErrorComCirc1Code6 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[6] | BYTE
TISErrorComCirc1Code7 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[7] | BYTE
TISErrorComCirc1Code8 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[8] | BYTE
TISErrorComCirc1Code9 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[9] | BYTE
TISErrorComCirc1Error | DIGITAL | IOD_TIS | TIS:.ErrorComCirc[1].Error
TISErrorComCirc1Status | INT | IOD_TIS | TIS:.ErrorComCirc[1].Status
TISErrorComCirc2Code10 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[10] | BYTE
TISErrorComCirc2Code11 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[11] | BYTE
TISErrorComCirc2Code12 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[12] | BYTE
TISErrorComCirc2Code13 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[13] | BYTE
TISErrorComCirc2Code14 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[14] | BYTE
TISErrorComCirc2Code15 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[15] | BYTE
TISErrorComCirc2Code1 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[1] | BYTE
TISErrorComCirc2Code2 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[2] | BYTE
TISErrorComCirc2Code3 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[3] | BYTE
TISErrorComCirc2Code4 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[4] | BYTE
TISErrorComCirc2Code5 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[5] | BYTE
TISErrorComCirc2Code6 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[6] | BYTE
TISErrorComCirc2Code7 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[7] | BYTE
TISErrorComCirc2Code8 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[8] | BYTE
TISErrorComCirc2Code9 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[9] | BYTE
TISErrorComCirc2Error | DIGITAL | IOD_TIS | TIS:.ErrorComCirc[2].Error
TISErrorComCirc2Status | INT | IOD_TIS | TIS:.ErrorComCirc[2].Status
TISErrorComCirc3Code10 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[10] | BYTE
TISErrorComCirc3Code11 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[11] | BYTE
TISErrorComCirc3Code12 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[12] | BYTE
TISErrorComCirc3Code13 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[13] | BYTE
TISErrorComCirc3Code14 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[14] | BYTE
TISErrorComCirc3Code15 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[15] | BYTE
TISErrorComCirc3Code1 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[1] | BYTE
TISErrorComCirc3Code2 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[2] | BYTE
TISErrorComCirc3Code3 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[3] | BYTE
TISErrorComCirc3Code4 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[4] | BYTE
TISErrorComCirc3Code5 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[5] | BYTE
TISErrorComCirc3Code6 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[6] | BYTE
TISErrorComCirc3Code7 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[7] | BYTE
TISErrorComCirc3Code8 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[8] | BYTE
TISErrorComCirc3Code9 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[9] | BYTE
TISErrorComCirc3Error | DIGITAL | IOD_TIS | TIS:.ErrorComCirc[3].Error
TISErrorComCirc3Status | INT | IOD_TIS | TIS:.ErrorComCirc[3].Status
TISErrorComCirc4Code10 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[10] | BYTE
TISErrorComCirc4Code11 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[11] | BYTE
TISErrorComCirc4Code12 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[12] | BYTE
TISErrorComCirc4Code13 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[13] | BYTE
TISErrorComCirc4Code14 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[14] | BYTE
TISErrorComCirc4Code15 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[15] | BYTE
TISErrorComCirc4Code1 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[1] | BYTE
TISErrorComCirc4Code2 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[2] | BYTE
TISErrorComCirc4Code3 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[3] | BYTE
TISErrorComCirc4Code4 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[4] | BYTE
TISErrorComCirc4Code5 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[5] | BYTE
TISErrorComCirc4Code6 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[6] | BYTE
TISErrorComCirc4Code7 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[7] | BYTE
TISErrorComCirc4Code8 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[8] | BYTE
TISErrorComCirc4Code9 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[9] | BYTE
TISErrorComCirc4Error | DIGITAL | IOD_TIS | TIS:.ErrorComCirc[4].Error
TISErrorComCirc4Status | INT | IOD_TIS | TIS:.ErrorComCirc[4].Status
TISErrorComCirc5Code10 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[10] | BYTE
TISErrorComCirc5Code11 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[11] | BYTE
TISErrorComCirc5Code12 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[12] | BYTE
TISErrorComCirc5Code13 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[13] | BYTE
TISErrorComCirc5Code14 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[14] | BYTE
TISErrorComCirc5Code15 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[15] | BYTE
TISErrorComCirc5Code1 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[1] | BYTE
TISErrorComCirc5Code2 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[2] | BYTE
TISErrorComCirc5Code3 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[3] | BYTE
TISErrorComCirc5Code4 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[4] | BYTE
TISErrorComCirc5Code5 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[5] | BYTE
TISErrorComCirc5Code6 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[6] | BYTE
TISErrorComCirc5Code7 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[7] | BYTE
TISErrorComCirc5Code8 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[8] | BYTE
TISErrorComCirc5Code9 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[9] | BYTE
TISErrorComCirc5Error | DIGITAL | IOD_TIS | TIS:.ErrorComCirc[5].Error
TISErrorComCirc5Status | INT | IOD_TIS | TIS:.ErrorComCirc[5].Status
TISErrorComKlima1Code10 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[10] | BYTE
TISErrorComKlima1Code11 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[11] | BYTE
TISErrorComKlima1Code12 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[12] | BYTE
TISErrorComKlima1Code13 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[13] | BYTE
TISErrorComKlima1Code14 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[14] | BYTE
TISErrorComKlima1Code15 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[15] | BYTE
TISErrorComKlima1Code1 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[1] | BYTE
TISErrorComKlima1Code2 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[2] | BYTE
TISErrorComKlima1Code3 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[3] | BYTE
TISErrorComKlima1Code4 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[4] | BYTE
TISErrorComKlima1Code5 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[5] | BYTE
TISErrorComKlima1Code6 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[6] | BYTE
TISErrorComKlima1Code7 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[7] | BYTE
TISErrorComKlima1Code8 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[8] | BYTE
TISErrorComKlima1Code9 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[9] | BYTE
TISErrorComKlima1Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[1].Error
TISErrorComKlima1Status | INT | IOD_TIS | TIS:.ErrorComKlima[1].Status
TISErrorComKlima2Code10 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[10] | BYTE
TISErrorComKlima2Code11 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[11] | BYTE
TISErrorComKlima2Code12 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[12] | BYTE
TISErrorComKlima2Code13 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[13] | BYTE
TISErrorComKlima2Code14 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[14] | BYTE
TISErrorComKlima2Code15 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[15] | BYTE
TISErrorComKlima2Code1 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[1] | BYTE
TISErrorComKlima2Code2 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[2] | BYTE
TISErrorComKlima2Code3 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[3] | BYTE
TISErrorComKlima2Code4 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[4] | BYTE
TISErrorComKlima2Code5 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[5] | BYTE
TISErrorComKlima2Code6 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[6] | BYTE
TISErrorComKlima2Code7 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[7] | BYTE
TISErrorComKlima2Code8 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[8] | BYTE
TISErrorComKlima2Code9 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[9] | BYTE
TISErrorComKlima2Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[2].Error
TISErrorComKlima2Status | INT | IOD_TIS | TIS:.ErrorComKlima[2].Status
TISErrorComKlima3Code10 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[10] | BYTE
TISErrorComKlima3Code11 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[11] | BYTE
TISErrorComKlima3Code12 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[12] | BYTE
TISErrorComKlima3Code13 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[13] | BYTE
TISErrorComKlima3Code14 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[14] | BYTE
TISErrorComKlima3Code15 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[15] | BYTE
TISErrorComKlima3Code1 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[1] | BYTE
TISErrorComKlima3Code2 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[2] | BYTE
TISErrorComKlima3Code3 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[3] | BYTE
TISErrorComKlima3Code4 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[4] | BYTE
TISErrorComKlima3Code5 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[5] | BYTE
TISErrorComKlima3Code6 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[6] | BYTE
TISErrorComKlima3Code7 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[7] | BYTE
TISErrorComKlima3Code8 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[8] | BYTE
TISErrorComKlima3Code9 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[9] | BYTE
TISErrorComKlima3Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[3].Error
TISErrorComKlima3Status | INT | IOD_TIS | TIS:.ErrorComKlima[3].Status
TISErrorComKlima4Code10 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[10] | BYTE
TISErrorComKlima4Code11 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[11] | BYTE
TISErrorComKlima4Code12 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[12] | BYTE
TISErrorComKlima4Code13 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[13] | BYTE
TISErrorComKlima4Code14 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[14] | BYTE
TISErrorComKlima4Code15 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[15] | BYTE
TISErrorComKlima4Code1 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[1] | BYTE
TISErrorComKlima4Code2 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[2] | BYTE
TISErrorComKlima4Code3 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[3] | BYTE
TISErrorComKlima4Code4 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[4] | BYTE
TISErrorComKlima4Code5 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[5] | BYTE
TISErrorComKlima4Code6 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[6] | BYTE
TISErrorComKlima4Code7 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[7] | BYTE
TISErrorComKlima4Code8 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[8] | BYTE
TISErrorComKlima4Code9 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[9] | BYTE
TISErrorComKlima4Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[4].Error
TISErrorComKlima4Status | INT | IOD_TIS | TIS:.ErrorComKlima[4].Status
TISErrorComKlima5Code10 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[10] | BYTE
TISErrorComKlima5Code11 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[11] | BYTE
TISErrorComKlima5Code12 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[12] | BYTE
TISErrorComKlima5Code13 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[13] | BYTE
TISErrorComKlima5Code14 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[14] | BYTE
TISErrorComKlima5Code15 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[15] | BYTE
TISErrorComKlima5Code1 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[1] | BYTE
TISErrorComKlima5Code2 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[2] | BYTE
TISErrorComKlima5Code3 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[3] | BYTE
TISErrorComKlima5Code4 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[4] | BYTE
TISErrorComKlima5Code5 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[5] | BYTE
TISErrorComKlima5Code6 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[6] | BYTE
TISErrorComKlima5Code7 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[7] | BYTE
TISErrorComKlima5Code8 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[8] | BYTE
TISErrorComKlima5Code9 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[9] | BYTE
TISErrorComKlima5Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[5].Error
TISErrorComKlima5Status | INT | IOD_TIS | TIS:.ErrorComKlima[5].Status
TISErrorComKlima6Code10 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[10] | BYTE
TISErrorComKlima6Code11 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[11] | BYTE
TISErrorComKlima6Code12 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[12] | BYTE
TISErrorComKlima6Code13 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[13] | BYTE
TISErrorComKlima6Code14 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[14] | BYTE
TISErrorComKlima6Code15 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[15] | BYTE
TISErrorComKlima6Code1 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[1] | BYTE
TISErrorComKlima6Code2 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[2] | BYTE
TISErrorComKlima6Code3 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[3] | BYTE
TISErrorComKlima6Code4 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[4] | BYTE
TISErrorComKlima6Code5 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[5] | BYTE
TISErrorComKlima6Code6 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[6] | BYTE
TISErrorComKlima6Code7 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[7] | BYTE
TISErrorComKlima6Code8 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[8] | BYTE
TISErrorComKlima6Code9 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[9] | BYTE
TISErrorComKlima6Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[6].Error
TISErrorComKlima6Status | INT | IOD_TIS | TIS:.ErrorComKlima[6].Status
TISKlima1AlarmKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[1].AlarmKompresor1
TISKlima1AlarmKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[1].AlarmKompresor2
TISKlima1Deluje | DIGITAL | IOD_TIS | TIS:.Klima[1].Deluje
TISKlima1EnergySaving | DIGITAL | IOD_TIS | TIS:.Klima[1].EnergySaving
TISKlima1FaultyEPROM | DIGITAL | IOD_TIS | TIS:.Klima[1].FaultyEPROM
TISKlima1FenThermalCutout | DIGITAL | IOD_TIS | TIS:.Klima[1].FenThermalCutout
TISKlima1GeneralAlarm | DIGITAL | IOD_TIS | TIS:.Klima[1].GeneralAlarm
TISKlima1GrelecStatus | INT | IOD_TIS | TIS:.Klima[1].GrelecStatus | BYTE
TISKlima1IzhodniVentStatus | INT | IOD_TIS | TIS:.Klima[1].IzhodniVentStatus | BYTE
TISKlima1Kompresor1naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[1].Kompresor1naMejiObrUr
TISKlima1Kompresor2naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[1].Kompresor2naMejiObrUr
TISKlima1KompresorStatus | INT | IOD_TIS | TIS:.Klima[1].KompresorStatus | BYTE
TISKlima1Napaka | DIGITAL | IOD_TIS | TIS:.Klima[1].Napaka
TISKlima1NapakaPriPretokuZraka | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaPriPretokuZraka
TISKlima1NapakaSenzorPovratVode | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaSenzorPovratVode
TISKlima1NapakaSenzorTempIzpiha | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaSenzorTempIzpiha
TISKlima1NapakaSenzorTempProstora | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaSenzorTempProstora
TISKlima1NapakaSenzorVlaznosti | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaSenzorVlaznosti
TISKlima1NapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaSenzorZunanjeTemp
TISKlima1NastMaxTemp | REAL | IOD_TIS | TIS:.Klima[1].NastMaxTemp
TISKlima1NastMaxVlaznost | REAL | IOD_TIS | TIS:.Klima[1].NastMaxVlaznost
TISKlima1NastMinTemp | REAL | IOD_TIS | TIS:.Klima[1].NastMinTemp
TISKlima1NastMinVlaznost | REAL | IOD_TIS | TIS:.Klima[1].NastMinVlaznost
TISKlima1NastTempProstora | REAL | IOD_TIS | TIS:.Klima[1].NastTempProstora
TISKlima1NastVlaznost | REAL | IOD_TIS | TIS:.Klima[1].NastVlaznost
TISKlima1NiTokaVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[1].NiTokaVVlazilcu
TISKlima1NiVodeVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[1].NiVodeVVlazilcu
TISKlima1NizekPritiskKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[1].NizekPritiskKompresor1
TISKlima1NizekPritiskKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[1].NizekPritiskKompresor2
TISKlima1NizkaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[1].NizkaTempPovratneVode
TISKlima1NizkaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[1].NizkaTempVProstoru
TISKlima1NizkaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[1].NizkaVlaznost
TISKlima1ObratovalneUre | REAL | IOD_TIS | TIS:.Klima[1].ObratovalneUre
TISKlima1OnOffEnablingBySupervisor | DIGITAL | IOD_TIS | TIS:.Klima[1].OnOffEnablingBySupervisor
TISKlima1PozarniAlarm | DIGITAL | IOD_TIS | TIS:.Klima[1].PozarniAlarm
TISKlima1Razvlazevanje | DIGITAL | IOD_TIS | TIS:.Klima[1].Razvlazevanje
TISKlima1RemoteOFFtoOutput | DIGITAL | IOD_TIS | TIS:.Klima[1].RemoteOFFtoOutput
TISKlima1RemoteOnOff | DIGITAL | IOD_TIS | TIS:.Klima[1].RemoteOnOff
TISKlima1RocniIzklop | DIGITAL | IOD_TIS | TIS:.Klima[1].RocniIzklop
TISKlima1SenzorjiStatus | DIGITAL | IOD_TIS | TIS:.Klima[1].SenzorjiStatus
TISKlima1StoppedByAlarms | DIGITAL | IOD_TIS | TIS:.Klima[1].StoppedByAlarms
TISKlima1TemperaturaProstora | REAL | IOD_TIS | TIS:.Klima[1].TemperaturaProstora
TISKlima1TempIzpihanegaZraka | REAL | IOD_TIS | TIS:.Klima[1].TempIzpihanegaZraka
TISKlima1TempPovratneVode | REAL | IOD_TIS | TIS:.Klima[1].TempPovratneVode
TISKlima1ThermalCutoutHeater1 | DIGITAL | IOD_TIS | TIS:.Klima[1].ThermalCutoutHeater1
TISKlima1ThermalCutoutHeater2 | DIGITAL | IOD_TIS | TIS:.Klima[1].ThermalCutoutHeater2
TISKlima1UnitOnOff | DIGITAL | IOD_TIS | TIS:.Klima[1].UnitOnOff
TISKlima1VentilatorNaMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[1].VentilatorNaMejiObrUr
TISKlima1VentilGretjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[1].VentilGretjeOdpiranje
TISKlima1VentilGretjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[1].VentilGretjeZapiranje
TISKlima1VentilHlajenjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[1].VentilHlajenjeOdpiranje
TISKlima1VentilHlajenjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[1].VentilHlajenjeZapiranje
TISKlima1VisokaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[1].VisokaTempPovratneVode
TISKlima1VisokaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[1].VisokaTempVProstoru
TISKlima1VisokaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[1].VisokaVlaznost
TISKlima1VisokTokVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[1].VisokTokVVlazilcu
TISKlima1Vlazenje | DIGITAL | IOD_TIS | TIS:.Klima[1].Vlazenje
TISKlima1VlazilecStatus | INT | IOD_TIS | TIS:.Klima[1].VlazilecStatus | BYTE
TISKlima1VlaznostProstora | REAL | IOD_TIS | TIS:.Klima[1].VlaznostProstora
TISKlima1ZamasenFilter | DIGITAL | IOD_TIS | TIS:.Klima[1].ZamasenFilter
TISKlima1ZunanjaTemp | REAL | IOD_TIS | TIS:.Klima[1].ZunanjaTemp
TISKlima2AlarmKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[2].AlarmKompresor1
TISKlima2AlarmKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[2].AlarmKompresor2
TISKlima2Deluje | DIGITAL | IOD_TIS | TIS:.Klima[2].Deluje
TISKlima2EnergySaving | DIGITAL | IOD_TIS | TIS:.Klima[2].EnergySaving
TISKlima2FaultyEPROM | DIGITAL | IOD_TIS | TIS:.Klima[2].FaultyEPROM
TISKlima2FenThermalCutout | DIGITAL | IOD_TIS | TIS:.Klima[2].FenThermalCutout
TISKlima2GeneralAlarm | DIGITAL | IOD_TIS | TIS:.Klima[2].GeneralAlarm
TISKlima2GrelecStatus | INT | IOD_TIS | TIS:.Klima[2].GrelecStatus | BYTE
TISKlima2IzhodniVentStatus | INT | IOD_TIS | TIS:.Klima[2].IzhodniVentStatus | BYTE
TISKlima2Kompresor1naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[2].Kompresor1naMejiObrUr
TISKlima2Kompresor2naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[2].Kompresor2naMejiObrUr
TISKlima2KompresorStatus | INT | IOD_TIS | TIS:.Klima[2].KompresorStatus | BYTE
TISKlima2Napaka | DIGITAL | IOD_TIS | TIS:.Klima[2].Napaka
TISKlima2NapakaPriPretokuZraka | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaPriPretokuZraka
TISKlima2NapakaSenzorPovratVode | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaSenzorPovratVode
TISKlima2NapakaSenzorTempIzpiha | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaSenzorTempIzpiha
TISKlima2NapakaSenzorTempProstora | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaSenzorTempProstora
TISKlima2NapakaSenzorVlaznosti | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaSenzorVlaznosti
TISKlima2NapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaSenzorZunanjeTemp
TISKlima2NastMaxTemp | REAL | IOD_TIS | TIS:.Klima[2].NastMaxTemp
TISKlima2NastMaxVlaznost | REAL | IOD_TIS | TIS:.Klima[2].NastMaxVlaznost
TISKlima2NastMinTemp | REAL | IOD_TIS | TIS:.Klima[2].NastMinTemp
TISKlima2NastMinVlaznost | REAL | IOD_TIS | TIS:.Klima[2].NastMinVlaznost
TISKlima2NastTempProstora | REAL | IOD_TIS | TIS:.Klima[2].NastTempProstora
TISKlima2NastVlaznost | REAL | IOD_TIS | TIS:.Klima[2].NastVlaznost
TISKlima2NiTokaVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[2].NiTokaVVlazilcu
TISKlima2NiVodeVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[2].NiVodeVVlazilcu
TISKlima2NizekPritiskKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[2].NizekPritiskKompresor1
TISKlima2NizekPritiskKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[2].NizekPritiskKompresor2
TISKlima2NizkaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[2].NizkaTempPovratneVode
TISKlima2NizkaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[2].NizkaTempVProstoru
TISKlima2NizkaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[2].NizkaVlaznost
TISKlima2ObratovalneUre | REAL | IOD_TIS | TIS:.Klima[2].ObratovalneUre
TISKlima2OnOffEnablingBySupervisor | DIGITAL | IOD_TIS | TIS:.Klima[2].OnOffEnablingBySupervisor
TISKlima2PozarniAlarm | DIGITAL | IOD_TIS | TIS:.Klima[2].PozarniAlarm
TISKlima2Razvlazevanje | DIGITAL | IOD_TIS | TIS:.Klima[2].Razvlazevanje
TISKlima2RemoteOFFtoOutput | DIGITAL | IOD_TIS | TIS:.Klima[2].RemoteOFFtoOutput
TISKlima2RemoteOnOff | DIGITAL | IOD_TIS | TIS:.Klima[2].RemoteOnOff
TISKlima2RocniIzklop | DIGITAL | IOD_TIS | TIS:.Klima[2].RocniIzklop
TISKlima2SenzorjiStatus | DIGITAL | IOD_TIS | TIS:.Klima[2].SenzorjiStatus
TISKlima2StoppedByAlarms | DIGITAL | IOD_TIS | TIS:.Klima[2].StoppedByAlarms
TISKlima2TemperaturaProstora | REAL | IOD_TIS | TIS:.Klima[2].TemperaturaProstora
TISKlima2TempIzpihanegaZraka | REAL | IOD_TIS | TIS:.Klima[2].TempIzpihanegaZraka
TISKlima2TempPovratneVode | REAL | IOD_TIS | TIS:.Klima[2].TempPovratneVode
TISKlima2ThermalCutoutHeater1 | DIGITAL | IOD_TIS | TIS:.Klima[2].ThermalCutoutHeater1
TISKlima2ThermalCutoutHeater2 | DIGITAL | IOD_TIS | TIS:.Klima[2].ThermalCutoutHeater2
TISKlima2UnitOnOff | DIGITAL | IOD_TIS | TIS:.Klima[2].UnitOnOff
TISKlima2VentilatorNaMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[2].VentilatorNaMejiObrUr
TISKlima2VentilGretjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[2].VentilGretjeOdpiranje
TISKlima2VentilGretjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[2].VentilGretjeZapiranje
TISKlima2VentilHlajenjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[2].VentilHlajenjeOdpiranje
TISKlima2VentilHlajenjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[2].VentilHlajenjeZapiranje
TISKlima2VisokaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[2].VisokaTempPovratneVode
TISKlima2VisokaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[2].VisokaTempVProstoru
TISKlima2VisokaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[2].VisokaVlaznost
TISKlima2VisokTokVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[2].VisokTokVVlazilcu
TISKlima2Vlazenje | DIGITAL | IOD_TIS | TIS:.Klima[2].Vlazenje
TISKlima2VlazilecStatus | INT | IOD_TIS | TIS:.Klima[2].VlazilecStatus | BYTE
TISKlima2VlaznostProstora | REAL | IOD_TIS | TIS:.Klima[2].VlaznostProstora
TISKlima2ZamasenFilter | DIGITAL | IOD_TIS | TIS:.Klima[2].ZamasenFilter
TISKlima2ZunanjaTemp | REAL | IOD_TIS | TIS:.Klima[2].ZunanjaTemp
TISKlima3AlarmKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[3].AlarmKompresor1
TISKlima3AlarmKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[3].AlarmKompresor2
TISKlima3Deluje | DIGITAL | IOD_TIS | TIS:.Klima[3].Deluje
TISKlima3EnergySaving | DIGITAL | IOD_TIS | TIS:.Klima[3].EnergySaving
TISKlima3FaultyEPROM | DIGITAL | IOD_TIS | TIS:.Klima[3].FaultyEPROM
TISKlima3FenThermalCutout | DIGITAL | IOD_TIS | TIS:.Klima[3].FenThermalCutout
TISKlima3GeneralAlarm | DIGITAL | IOD_TIS | TIS:.Klima[3].GeneralAlarm
TISKlima3GrelecStatus | INT | IOD_TIS | TIS:.Klima[3].GrelecStatus | BYTE
TISKlima3IzhodniVentStatus | INT | IOD_TIS | TIS:.Klima[3].IzhodniVentStatus | BYTE
TISKlima3Kompresor1naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[3].Kompresor1naMejiObrUr
TISKlima3Kompresor2naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[3].Kompresor2naMejiObrUr
TISKlima3KompresorStatus | INT | IOD_TIS | TIS:.Klima[3].KompresorStatus | BYTE
TISKlima3Napaka | DIGITAL | IOD_TIS | TIS:.Klima[3].Napaka
TISKlima3NapakaPriPretokuZraka | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaPriPretokuZraka
TISKlima3NapakaSenzorPovratVode | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaSenzorPovratVode
TISKlima3NapakaSenzorTempIzpiha | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaSenzorTempIzpiha
TISKlima3NapakaSenzorTempProstora | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaSenzorTempProstora
TISKlima3NapakaSenzorVlaznosti | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaSenzorVlaznosti
TISKlima3NapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaSenzorZunanjeTemp
TISKlima3NastMaxTemp | REAL | IOD_TIS | TIS:.Klima[3].NastMaxTemp
TISKlima3NastMaxVlaznost | REAL | IOD_TIS | TIS:.Klima[3].NastMaxVlaznost
TISKlima3NastMinTemp | REAL | IOD_TIS | TIS:.Klima[3].NastMinTemp
TISKlima3NastMinVlaznost | REAL | IOD_TIS | TIS:.Klima[3].NastMinVlaznost
TISKlima3NastTempProstora | REAL | IOD_TIS | TIS:.Klima[3].NastTempProstora
TISKlima3NastVlaznost | REAL | IOD_TIS | TIS:.Klima[3].NastVlaznost
TISKlima3NiTokaVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[3].NiTokaVVlazilcu
TISKlima3NiVodeVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[3].NiVodeVVlazilcu
TISKlima3NizekPritiskKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[3].NizekPritiskKompresor1
TISKlima3NizekPritiskKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[3].NizekPritiskKompresor2
TISKlima3NizkaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[3].NizkaTempPovratneVode
TISKlima3NizkaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[3].NizkaTempVProstoru
TISKlima3NizkaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[3].NizkaVlaznost
TISKlima3ObratovalneUre | REAL | IOD_TIS | TIS:.Klima[3].ObratovalneUre
TISKlima3OnOffEnablingBySupervisor | DIGITAL | IOD_TIS | TIS:.Klima[3].OnOffEnablingBySupervisor
TISKlima3PozarniAlarm | DIGITAL | IOD_TIS | TIS:.Klima[3].PozarniAlarm
TISKlima3Razvlazevanje | DIGITAL | IOD_TIS | TIS:.Klima[3].Razvlazevanje
TISKlima3RemoteOFFtoOutput | DIGITAL | IOD_TIS | TIS:.Klima[3].RemoteOFFtoOutput
TISKlima3RemoteOnOff | DIGITAL | IOD_TIS | TIS:.Klima[3].RemoteOnOff
TISKlima3RocniIzklop | DIGITAL | IOD_TIS | TIS:.Klima[3].RocniIzklop
TISKlima3SenzorjiStatus | DIGITAL | IOD_TIS | TIS:.Klima[3].SenzorjiStatus
TISKlima3StoppedByAlarms | DIGITAL | IOD_TIS | TIS:.Klima[3].StoppedByAlarms
TISKlima3TemperaturaProstora | REAL | IOD_TIS | TIS:.Klima[3].TemperaturaProstora
TISKlima3TempIzpihanegaZraka | REAL | IOD_TIS | TIS:.Klima[3].TempIzpihanegaZraka
TISKlima3TempPovratneVode | REAL | IOD_TIS | TIS:.Klima[3].TempPovratneVode
TISKlima3ThermalCutoutHeater1 | DIGITAL | IOD_TIS | TIS:.Klima[3].ThermalCutoutHeater1
TISKlima3ThermalCutoutHeater2 | DIGITAL | IOD_TIS | TIS:.Klima[3].ThermalCutoutHeater2
TISKlima3UnitOnOff | DIGITAL | IOD_TIS | TIS:.Klima[3].UnitOnOff
TISKlima3VentilatorNaMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[3].VentilatorNaMejiObrUr
TISKlima3VentilGretjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[3].VentilGretjeOdpiranje
TISKlima3VentilGretjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[3].VentilGretjeZapiranje
TISKlima3VentilHlajenjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[3].VentilHlajenjeOdpiranje
TISKlima3VentilHlajenjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[3].VentilHlajenjeZapiranje
TISKlima3VisokaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[3].VisokaTempPovratneVode
TISKlima3VisokaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[3].VisokaTempVProstoru
TISKlima3VisokaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[3].VisokaVlaznost
TISKlima3VisokTokVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[3].VisokTokVVlazilcu
TISKlima3Vlazenje | DIGITAL | IOD_TIS | TIS:.Klima[3].Vlazenje
TISKlima3VlazilecStatus | INT | IOD_TIS | TIS:.Klima[3].VlazilecStatus | BYTE
TISKlima3VlaznostProstora | REAL | IOD_TIS | TIS:.Klima[3].VlaznostProstora
TISKlima3ZamasenFilter | DIGITAL | IOD_TIS | TIS:.Klima[3].ZamasenFilter
TISKlima3ZunanjaTemp | REAL | IOD_TIS | TIS:.Klima[3].ZunanjaTemp
TISKlimaAErrors10 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[10]
TISKlimaAErrors11 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[11]
TISKlimaAErrors12 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[12]
TISKlimaAErrors13 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[13]
TISKlimaAErrors14 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[14]
TISKlimaAErrors15 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[15]
TISKlimaAErrors16 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[16]
TISKlimaAErrors17 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[17]
TISKlimaAErrors18 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[18]
TISKlimaAErrors19 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[19]
TISKlimaAErrors1 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[1]
TISKlimaAErrors20 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[20]
TISKlimaAErrors21 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[21]
TISKlimaAErrors22 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[22]
TISKlimaAErrors23 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[23]
TISKlimaAErrors24 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[24]
TISKlimaAErrors25 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[25]
TISKlimaAErrors26 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[26]
TISKlimaAErrors27 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[27]
TISKlimaAErrors28 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[28]
TISKlimaAErrors29 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[29]
TISKlimaAErrors2 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[2]
TISKlimaAErrors30 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[30]
TISKlimaAErrors31 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[31]
TISKlimaAErrors32 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[32]
TISKlimaAErrors33 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[33]
TISKlimaAErrors34 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[34]
TISKlimaAErrors35 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[35]
TISKlimaAErrors36 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[36]
TISKlimaAErrors37 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[37]
TISKlimaAErrors38 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[38]
TISKlimaAErrors39 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[39]
TISKlimaAErrors3 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[3]
TISKlimaAErrors40 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[40]
TISKlimaAErrors4 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[4]
TISKlimaAErrors5 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[5]
TISKlimaAErrors6 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[6]
TISKlimaAErrors7 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[7]
TISKlimaAErrors8 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[8]
TISKlimaAErrors9 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[9]
TISKlimaBErrors10 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[10]
TISKlimaBErrors11 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[11]
TISKlimaBErrors12 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[12]
TISKlimaBErrors13 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[13]
TISKlimaBErrors14 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[14]
TISKlimaBErrors15 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[15]
TISKlimaBErrors16 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[16]
TISKlimaBErrors17 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[17]
TISKlimaBErrors18 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[18]
TISKlimaBErrors19 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[19]
TISKlimaBErrors1 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[1]
TISKlimaBErrors20 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[20]
TISKlimaBErrors21 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[21]
TISKlimaBErrors22 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[22]
TISKlimaBErrors23 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[23]
TISKlimaBErrors24 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[24]
TISKlimaBErrors25 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[25]
TISKlimaBErrors26 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[26]
TISKlimaBErrors27 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[27]
TISKlimaBErrors28 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[28]
TISKlimaBErrors29 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[29]
TISKlimaBErrors2 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[2]
TISKlimaBErrors30 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[30]
TISKlimaBErrors31 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[31]
TISKlimaBErrors32 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[32]
TISKlimaBErrors33 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[33]
TISKlimaBErrors34 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[34]
TISKlimaBErrors35 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[35]
TISKlimaBErrors36 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[36]
TISKlimaBErrors37 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[37]
TISKlimaBErrors38 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[38]
TISKlimaBErrors39 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[39]
TISKlimaBErrors3 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[3]
TISKlimaBErrors40 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[40]
TISKlimaBErrors4 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[4]
TISKlimaBErrors5 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[5]
TISKlimaBErrors6 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[6]
TISKlimaBErrors7 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[7]
TISKlimaBErrors8 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[8]
TISKlimaBErrors9 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[9]
TISKlimaCErrors10 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[10]
TISKlimaCErrors11 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[11]
TISKlimaCErrors12 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[12]
TISKlimaCErrors13 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[13]
TISKlimaCErrors14 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[14]
TISKlimaCErrors15 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[15]
TISKlimaCErrors16 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[16]
TISKlimaCErrors17 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[17]
TISKlimaCErrors18 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[18]
TISKlimaCErrors19 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[19]
TISKlimaCErrors1 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[1]
TISKlimaCErrors20 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[20]
TISKlimaCErrors21 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[21]
TISKlimaCErrors22 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[22]
TISKlimaCErrors23 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[23]
TISKlimaCErrors24 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[24]
TISKlimaCErrors25 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[25]
TISKlimaCErrors26 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[26]
TISKlimaCErrors27 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[27]
TISKlimaCErrors28 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[28]
TISKlimaCErrors29 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[29]
TISKlimaCErrors2 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[2]
TISKlimaCErrors30 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[30]
TISKlimaCErrors31 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[31]
TISKlimaCErrors32 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[32]
TISKlimaCErrors33 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[33]
TISKlimaCErrors34 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[34]
TISKlimaCErrors35 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[35]
TISKlimaCErrors36 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[36]
TISKlimaCErrors37 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[37]
TISKlimaCErrors38 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[38]
TISKlimaCErrors39 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[39]
TISKlimaCErrors3 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[3]
TISKlimaCErrors40 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[40]
TISKlimaCErrors4 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[4]
TISKlimaCErrors5 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[5]
TISKlimaCErrors6 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[6]
TISKlimaCErrors7 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[7]
TISKlimaCErrors8 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[8]
TISKlimaCErrors9 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[9]
TISKlimaGalAlarmKompresor1 | DIGITAL | IOD_TIS | TIS:.KlimaGal.AlarmKompresor1
TISKlimaGalAlarmKompresor2 | DIGITAL | IOD_TIS | TIS:.KlimaGal.AlarmKompresor2
TISKlimaGalDeluje | DIGITAL | IOD_TIS | TIS:.KlimaGal.Deluje
TISKlimaGalEnergySaving | DIGITAL | IOD_TIS | TIS:.KlimaGal.EnergySaving
TISKlimaGalFaultyEPROM | DIGITAL | IOD_TIS | TIS:.KlimaGal.FaultyEPROM
TISKlimaGalFenThermalCutout | DIGITAL | IOD_TIS | TIS:.KlimaGal.FenThermalCutout
TISKlimaGalGeneralAlarm | DIGITAL | IOD_TIS | TIS:.KlimaGal.GeneralAlarm
TISKlimaGalGrelecStatus | INT | IOD_TIS | TIS:.KlimaGal.GrelecStatus | BYTE
TISKlimaGalIzhodniVentStatus | INT | IOD_TIS | TIS:.KlimaGal.IzhodniVentStatus | BYTE
TISKlimaGalKompresor1naMejiObrUr | DIGITAL | IOD_TIS | TIS:.KlimaGal.Kompresor1naMejiObrUr
TISKlimaGalKompresor2naMejiObrUr | DIGITAL | IOD_TIS | TIS:.KlimaGal.Kompresor2naMejiObrUr
TISKlimaGalKompresorStatus | INT | IOD_TIS | TIS:.KlimaGal.KompresorStatus | BYTE
TISKlimaGalNapaka | DIGITAL | IOD_TIS | TIS:.KlimaGal.Napaka
TISKlimaGalNapakaPriPretokuZraka | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaPriPretokuZraka
TISKlimaGalNapakaSenzorPovratVode | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaSenzorPovratVode
TISKlimaGalNapakaSenzorTempIzpiha | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaSenzorTempIzpiha
TISKlimaGalNapakaSenzorTempProstora | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaSenzorTempProstora
TISKlimaGalNapakaSenzorVlaznosti | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaSenzorVlaznosti
TISKlimaGalNapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaSenzorZunanjeTemp
TISKlimaGalNastMaxTemp | REAL | IOD_TIS | TIS:.KlimaGal.NastMaxTemp
TISKlimaGalNastMaxVlaznost | REAL | IOD_TIS | TIS:.KlimaGal.NastMaxVlaznost
TISKlimaGalNastMinTemp | REAL | IOD_TIS | TIS:.KlimaGal.NastMinTemp
TISKlimaGalNastMinVlaznost | REAL | IOD_TIS | TIS:.KlimaGal.NastMinVlaznost
TISKlimaGalNastTempProstora | REAL | IOD_TIS | TIS:.KlimaGal.NastTempProstora
TISKlimaGalNastVlaznost | REAL | IOD_TIS | TIS:.KlimaGal.NastVlaznost
TISKlimaGalNiTokaVVlazilcu | DIGITAL | IOD_TIS | TIS:.KlimaGal.NiTokaVVlazilcu
TISKlimaGalNiVodeVVlazilcu | DIGITAL | IOD_TIS | TIS:.KlimaGal.NiVodeVVlazilcu
TISKlimaGalNizekPritiskKompresor1 | DIGITAL | IOD_TIS | TIS:.KlimaGal.NizekPritiskKompresor1
TISKlimaGalNizekPritiskKompresor2 | DIGITAL | IOD_TIS | TIS:.KlimaGal.NizekPritiskKompresor2
TISKlimaGalNizkaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.KlimaGal.NizkaTempPovratneVode
TISKlimaGalNizkaTempVProstoru | DIGITAL | IOD_TIS | TIS:.KlimaGal.NizkaTempVProstoru
TISKlimaGalNizkaVlaznost | DIGITAL | IOD_TIS | TIS:.KlimaGal.NizkaVlaznost
TISKlimaGalObratovalneUre | REAL | IOD_TIS | TIS:.KlimaGal.ObratovalneUre
TISKlimaGalOnOffEnablingBySupervisor | DIGITAL | IOD_TIS | TIS:.KlimaGal.OnOffEnablingBySupervisor
TISKlimaGalPozarniAlarm | DIGITAL | IOD_TIS | TIS:.KlimaGal.PozarniAlarm
TISKlimaGalRazvlazevanje | DIGITAL | IOD_TIS | TIS:.KlimaGal.Razvlazevanje
TISKlimaGalRemoteOFFtoOutput | DIGITAL | IOD_TIS | TIS:.KlimaGal.RemoteOFFtoOutput
TISKlimaGalRemoteOnOff | DIGITAL | IOD_TIS | TIS:.KlimaGal.RemoteOnOff
TISKlimaGalRocniIzklop | DIGITAL | IOD_TIS | TIS:.KlimaGal.RocniIzklop
TISKlimaGalSenzorjiStatus | DIGITAL | IOD_TIS | TIS:.KlimaGal.SenzorjiStatus
TISKlimaGalStoppedByAlarms | DIGITAL | IOD_TIS | TIS:.KlimaGal.StoppedByAlarms
TISKlimaGalTemperaturaProstora | REAL | IOD_TIS | TIS:.KlimaGal.TemperaturaProstora
TISKlimaGalTempIzpihanegaZraka | REAL | IOD_TIS | TIS:.KlimaGal.TempIzpihanegaZraka
TISKlimaGalTempPovratneVode | REAL | IOD_TIS | TIS:.KlimaGal.TempPovratneVode
TISKlimaGalThermalCutoutHeater1 | DIGITAL | IOD_TIS | TIS:.KlimaGal.ThermalCutoutHeater1
TISKlimaGalThermalCutoutHeater2 | DIGITAL | IOD_TIS | TIS:.KlimaGal.ThermalCutoutHeater2
TISKlimaGalUnitOnOff | DIGITAL | IOD_TIS | TIS:.KlimaGal.UnitOnOff
TISKlimaGalVentilatorNaMejiObrUr | DIGITAL | IOD_TIS | TIS:.KlimaGal.VentilatorNaMejiObrUr
TISKlimaGalVentilGretjeOdpiranje | DIGITAL | IOD_TIS | TIS:.KlimaGal.VentilGretjeOdpiranje
TISKlimaGalVentilGretjeZapiranje | DIGITAL | IOD_TIS | TIS:.KlimaGal.VentilGretjeZapiranje
TISKlimaGalVentilHlajenjeOdpiranje | DIGITAL | IOD_TIS | TIS:.KlimaGal.VentilHlajenjeOdpiranje
TISKlimaGalVentilHlajenjeZapiranje | DIGITAL | IOD_TIS | TIS:.KlimaGal.VentilHlajenjeZapiranje
TISKlimaGalVisokaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.KlimaGal.VisokaTempPovratneVode
TISKlimaGalVisokaTempVProstoru | DIGITAL | IOD_TIS | TIS:.KlimaGal.VisokaTempVProstoru
TISKlimaGalVisokaVlaznost | DIGITAL | IOD_TIS | TIS:.KlimaGal.VisokaVlaznost
TISKlimaGalVisokTokVVlazilcu | DIGITAL | IOD_TIS | TIS:.KlimaGal.VisokTokVVlazilcu
TISKlimaGalVlazenje | DIGITAL | IOD_TIS | TIS:.KlimaGal.Vlazenje
TISKlimaGalVlazilecStatus | INT | IOD_TIS | TIS:.KlimaGal.VlazilecStatus | BYTE
TISKlimaGalVlaznostProstora | REAL | IOD_TIS | TIS:.KlimaGal.VlaznostProstora
TISKlimaGalZamasenFilter | DIGITAL | IOD_TIS | TIS:.KlimaGal.ZamasenFilter
TISKlimaGalZunanjaTemp | REAL | IOD_TIS | TIS:.KlimaGal.ZunanjaTemp
TISKlimeNaCas | DIGITAL | IOD_TIS | TIS:.KlimeNaCas
TISNapakaSenzorTemp10 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[10]
TISNapakaSenzorTemp11 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[11]
TISNapakaSenzorTemp12 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[12]
TISNapakaSenzorTemp13 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[13]
TISNapakaSenzorTemp14 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[14]
TISNapakaSenzorTemp15 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[15]
TISNapakaSenzorTemp16 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[16]
TISNapakaSenzorTemp17 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[17]
TISNapakaSenzorTemp18 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[18]
TISNapakaSenzorTemp19 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[19]
TISNapakaSenzorTemp1 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[1]
TISNapakaSenzorTemp2 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[2]
TISNapakaSenzorTemp3 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[3]
TISNapakaSenzorTemp4 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[4]
TISNapakaSenzorTemp5 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[5]
TISNapakaSenzorTemp6 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[6]
TISNapakaSenzorTemp7 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[7]
TISNapakaSenzorTemp8 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[8]
TISNapakaSenzorTemp9 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[9]
TISNapakaSenzorVlaga10 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[10]
TISNapakaSenzorVlaga11 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[11]
TISNapakaSenzorVlaga12 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[12]
TISNapakaSenzorVlaga13 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[13]
TISNapakaSenzorVlaga14 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[14]
TISNapakaSenzorVlaga15 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[15]
TISNapakaSenzorVlaga16 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[16]
TISNapakaSenzorVlaga17 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[17]
TISNapakaSenzorVlaga18 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[18]
TISNapakaSenzorVlaga19 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[19]
TISNapakaSenzorVlaga1 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[1]
TISNapakaSenzorVlaga2 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[2]
TISNapakaSenzorVlaga3 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[3]
TISNapakaSenzorVlaga4 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[4]
TISNapakaSenzorVlaga5 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[5]
TISNapakaSenzorVlaga6 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[6]
TISNapakaSenzorVlaga7 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[7]
TISNapakaSenzorVlaga8 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[8]
TISNapakaSenzorVlaga9 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[9]
TISQstanje10 | INT | IOD_TIS | TIS:.Qstanje[10] | BYTE
TISQstanje1 | INT | IOD_TIS | TIS:.Qstanje[1] | BYTE
TISQstanje2 | INT | IOD_TIS | TIS:.Qstanje[2] | BYTE
TISQstanje3 | INT | IOD_TIS | TIS:.Qstanje[3] | BYTE
TISQstanje4 | INT | IOD_TIS | TIS:.Qstanje[4] | BYTE
TISQstanje5 | INT | IOD_TIS | TIS:.Qstanje[5] | BYTE
TISQstanje6 | INT | IOD_TIS | TIS:.Qstanje[6] | BYTE
TISQstanje7 | INT | IOD_TIS | TIS:.Qstanje[7] | BYTE
TISQstanje8 | INT | IOD_TIS | TIS:.Qstanje[8] | BYTE
TISQstanje9 | INT | IOD_TIS | TIS:.Qstanje[9] | BYTE
TISSenzorTemp10 | REAL | IOD_TIS | TIS:.SenzorTemp[10]
TISSenzorTemp11 | REAL | IOD_TIS | TIS:.SenzorTemp[11]
TISSenzorTemp12 | REAL | IOD_TIS | TIS:.SenzorTemp[12]
TISSenzorTemp13 | REAL | IOD_TIS | TIS:.SenzorTemp[13]
TISSenzorTemp14 | REAL | IOD_TIS | TIS:.SenzorTemp[14]
TISSenzorTemp15 | REAL | IOD_TIS | TIS:.SenzorTemp[15]
TISSenzorTemp16 | REAL | IOD_TIS | TIS:.SenzorTemp[16]
TISSenzorTemp17 | REAL | IOD_TIS | TIS:.SenzorTemp[17]
TISSenzorTemp18 | REAL | IOD_TIS | TIS:.SenzorTemp[18]
TISSenzorTemp19 | REAL | IOD_TIS | TIS:.SenzorTemp[19]
TISSenzorTemp1 | REAL | IOD_TIS | TIS:.SenzorTemp[1]
TISSenzorTemp2 | REAL | IOD_TIS | TIS:.SenzorTemp[2]
TISSenzorTemp3 | REAL | IOD_TIS | TIS:.SenzorTemp[3]
TISSenzorTemp4 | REAL | IOD_TIS | TIS:.SenzorTemp[4]
TISSenzorTemp5 | REAL | IOD_TIS | TIS:.SenzorTemp[5]
TISSenzorTemp6 | REAL | IOD_TIS | TIS:.SenzorTemp[6]
TISSenzorTemp7 | REAL | IOD_TIS | TIS:.SenzorTemp[7]
TISSenzorTemp8 | REAL | IOD_TIS | TIS:.SenzorTemp[8]
TISSenzorTemp9 | REAL | IOD_TIS | TIS:.SenzorTemp[9]
TISSenzorVlaga10 | REAL | IOD_TIS | TIS:.SenzorVlaga[10]
TISSenzorVlaga11 | REAL | IOD_TIS | TIS:.SenzorVlaga[11]
TISSenzorVlaga12 | REAL | IOD_TIS | TIS:.SenzorVlaga[12]
TISSenzorVlaga13 | REAL | IOD_TIS | TIS:.SenzorVlaga[13]
TISSenzorVlaga14 | REAL | IOD_TIS | TIS:.SenzorVlaga[14]
TISSenzorVlaga15 | REAL | IOD_TIS | TIS:.SenzorVlaga[15]
TISSenzorVlaga16 | REAL | IOD_TIS | TIS:.SenzorVlaga[16]
TISSenzorVlaga17 | REAL | IOD_TIS | TIS:.SenzorVlaga[17]
TISSenzorVlaga18 | REAL | IOD_TIS | TIS:.SenzorVlaga[18]
TISSenzorVlaga19 | REAL | IOD_TIS | TIS:.SenzorVlaga[19]
TISSenzorVlaga1 | REAL | IOD_TIS | TIS:.SenzorVlaga[1]
TISSenzorVlaga2 | REAL | IOD_TIS | TIS:.SenzorVlaga[2]
TISSenzorVlaga3 | REAL | IOD_TIS | TIS:.SenzorVlaga[3]
TISSenzorVlaga4 | REAL | IOD_TIS | TIS:.SenzorVlaga[4]
TISSenzorVlaga5 | REAL | IOD_TIS | TIS:.SenzorVlaga[5]
TISSenzorVlaga6 | REAL | IOD_TIS | TIS:.SenzorVlaga[6]
TISSenzorVlaga7 | REAL | IOD_TIS | TIS:.SenzorVlaga[7]
TISSenzorVlaga8 | REAL | IOD_TIS | TIS:.SenzorVlaga[8]
TISSenzorVlaga9 | REAL | IOD_TIS | TIS:.SenzorVlaga[9]
TISSetDateTime | DIGITAL | IOD_TIS | TIS:.SetDateTime
TISSetDateTimeDemand | DIGITAL | IOD_TIS | TIS:.SetDateTimeDemand
TISSetDateTimeError | DIGITAL | IOD_TIS | TIS:.SetDateTimeError
TISSetDateTimeFinished | DIGITAL | IOD_TIS | TIS:.SetDateTimeFinished
TISSetRemoteOnOff1 | DIGITAL | IOD_TIS | TIS:.SetRemoteOnOff[1]
TISSetRemoteOnOff2 | DIGITAL | IOD_TIS | TIS:.SetRemoteOnOff[2]
TISSetRemoteOnOff3 | DIGITAL | IOD_TIS | TIS:.SetRemoteOnOff[3]
TISSlabaBaterijaPLC_A1 | DIGITAL | IOD_TIS | TIS:.SlabaBaterijaPLC_A1
TISTempAlarmPoint1 | REAL | IOD_TIS | TIS:.TempAlarmPoint[1]
TISTempAlarmPoint2 | REAL | IOD_TIS | TIS:.TempAlarmPoint[2]
TISTempAlarmPoint3 | REAL | IOD_TIS | TIS:.TempAlarmPoint[3]
TISTempMaxPoint1 | REAL | IOD_TIS | TIS:.TempMaxPoint[1]
TISTempMaxPoint2 | REAL | IOD_TIS | TIS:.TempMaxPoint[2]
TISTempMaxPoint3 | REAL | IOD_TIS | TIS:.TempMaxPoint[3]
TISTempPovp1 | REAL | IOD_TIS | TIS:.TempPovp[1]
TISTempPovp2 | REAL | IOD_TIS | TIS:.TempPovp[2]
TISTempPovp3 | REAL | IOD_TIS | TIS:.TempPovp[3]
TISTempPovp4 | REAL | IOD_TIS | TIS:.TempPovp[4]
TISTempPovp5 | REAL | IOD_TIS | TIS:.TempPovp[5]
TISTempSetPoint1 | REAL | IOD_TIS | TIS:.TempSetPoint[1]
TISTempSetPoint2 | REAL | IOD_TIS | TIS:.TempSetPoint[2]
TISTempSetPoint3 | REAL | IOD_TIS | TIS:.TempSetPoint[3]
TISTempTSprevisoka10 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[10]
TISTempTSprevisoka11 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[11]
TISTempTSprevisoka12 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[12]
TISTempTSprevisoka13 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[13]
TISTempTSprevisoka14 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[14]
TISTempTSprevisoka15 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[15]
TISTempTSprevisoka16 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[16]
TISTempTSprevisoka17 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[17]
TISTempTSprevisoka18 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[18]
TISTempTSprevisoka19 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[19]
TISTempTSprevisoka1 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[1]
TISTempTSprevisoka2 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[2]
TISTempTSprevisoka3 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[3]
TISTempTSprevisoka4 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[4]
TISTempTSprevisoka5 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[5]
TISTempTSprevisoka6 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[6]
TISTempTSprevisoka7 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[7]
TISTempTSprevisoka8 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[8]
TISTempTSprevisoka9 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[9]
TISUserCurrentLevel | INT | IOD_TIS | TIS:.UserCurrentLevel | BYTE
TISUserCurrentName | STRING | IOD_TIS | TIS:.UserCurrentName
TISUserLoggedIn | DIGITAL | IOD_TIS | TIS:.UserLoggedIn
TISVlagaPovp1 | REAL | IOD_TIS | TIS:.VlagaPovp[1]
TISVlagaPovp2 | REAL | IOD_TIS | TIS:.VlagaPovp[2]
TISVlagaPovp3 | REAL | IOD_TIS | TIS:.VlagaPovp[3]
TISVlagaPovp4 | REAL | IOD_TIS | TIS:.VlagaPovp[4]
TISVlagaPovp5 | REAL | IOD_TIS | TIS:.VlagaPovp[5]
TISXVH_AlarmOn | DIGITAL | IOD_TIS | TIS:.XVH_AlarmOn
TISXVH_CircNumber | INT | IOD_TIS | TIS:.XVH_CircNumber | BYTE
TISXVH_GrafTemp1 | REAL | IOD_TIS | TIS:.XVH_GrafTemp[1]
TISXVH_GrafTemp2 | REAL | IOD_TIS | TIS:.XVH_GrafTemp[2]
TISXVH_GrafTemp3 | REAL | IOD_TIS | TIS:.XVH_GrafTemp[3]
TISXVH_GrafTemp4 | REAL | IOD_TIS | TIS:.XVH_GrafTemp[4]
TISXVH_GrafTemp5 | REAL | IOD_TIS | TIS:.XVH_GrafTemp[5]
TISXVH_GrafVlaga1 | REAL | IOD_TIS | TIS:.XVH_GrafVlaga[1]
TISXVH_GrafVlaga2 | REAL | IOD_TIS | TIS:.XVH_GrafVlaga[2]
TISXVH_GrafVlaga3 | REAL | IOD_TIS | TIS:.XVH_GrafVlaga[3]
TISXVH_GrafVlaga4 | REAL | IOD_TIS | TIS:.XVH_GrafVlaga[4]
TISXVH_GrafVlaga5 | REAL | IOD_TIS | TIS:.XVH_GrafVlaga[5]
TISXVH_KlimaNumber | INT | IOD_TIS | TIS:.XVH_KlimaNumber | BYTE
TISXVH_NastTempProstora1 | REAL | IOD_TIS | TIS:.XVH_NastTempProstora[1]
TISXVH_NastTempProstora2 | REAL | IOD_TIS | TIS:.XVH_NastTempProstora[2]
TISXVH_NastTempProstora3 | REAL | IOD_TIS | TIS:.XVH_NastTempProstora[3]
TISXVH_ObratovalneUre1 | REAL | IOD_TIS | TIS:.XVH_ObratovalneUre[1]
TISXVH_ObratovalneUre2 | REAL | IOD_TIS | TIS:.XVH_ObratovalneUre[2]
TISXVH_ObratovalneUre3 | REAL | IOD_TIS | TIS:.XVH_ObratovalneUre[3]
TISXVH_PripravaVodeStat1 | INT | IOD_TIS | TIS:.XVH_PripravaVodeStat[1] | BYTE
TISXVH_PripravaVodeStat2 | INT | IOD_TIS | TIS:.XVH_PripravaVodeStat[2] | BYTE
TISXVH_RemoteStatus1 | DIGITAL | IOD_TIS | TIS:.XVH_RemoteStatus[1]
TISXVH_RemoteStatus2 | DIGITAL | IOD_TIS | TIS:.XVH_RemoteStatus[2]
TISXVH_RemoteStatus3 | DIGITAL | IOD_TIS | TIS:.XVH_RemoteStatus[3]
TISXVH_setCircNum1 | DIGITAL | IOD_TIS | TIS:.XVH_setCircNum[1]
TISXVH_setCircNum2 | DIGITAL | IOD_TIS | TIS:.XVH_setCircNum[2]
TISXVH_setCircNum3 | DIGITAL | IOD_TIS | TIS:.XVH_setCircNum[3]
TISXVH_setCircNum4 | DIGITAL | IOD_TIS | TIS:.XVH_setCircNum[4]
TISXVH_setCircNum5 | DIGITAL | IOD_TIS | TIS:.XVH_setCircNum[5]
TISXVH_setKlimaNum1 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[1]
TISXVH_setKlimaNum2 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[2]
TISXVH_setKlimaNum3 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[3]
TISXVH_setKlimaNum4 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[4]
TISXVH_setKlimaNum5 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[5]
TISXVH_setKlimaNum6 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[6]
TISXVH_UPSstatus | INT | IOD_TIS | TIS:.XVH_UPSstatus | BYTE
TISXVH_VlazilecStatus1 | INT | IOD_TIS | TIS:.XVH_VlazilecStatus[1] | BYTE
TISXVH_VlazilecStatus2 | INT | IOD_TIS | TIS:.XVH_VlazilecStatus[2] | BYTE
TISXVH_VlazilecStatus3 | INT | IOD_TIS | TIS:.XVH_VlazilecStatus[3] | BYTE
TISXVHhighHum | REAL | IOD_TIS | TIS:.XVHhighHum
TISXVHhighTemp | REAL | IOD_TIS | TIS:.XVHhighTemp
TISXVHlowHum | REAL | IOD_TIS | TIS:.XVHlowHum
TISXVHlowTemp | REAL | IOD_TIS | TIS:.XVHlowTemp
TISXVHnum10 | INT | IOD_TIS | TIS:.XVHnum[10] | BYTE
TISXVHnum11 | INT | IOD_TIS | TIS:.XVHnum[11] | BYTE
TISXVHnum12 | INT | IOD_TIS | TIS:.XVHnum[12] | BYTE
TISXVHnum13 | INT | IOD_TIS | TIS:.XVHnum[13] | BYTE
TISXVHnum14 | INT | IOD_TIS | TIS:.XVHnum[14] | BYTE
TISXVHnum1 | INT | IOD_TIS | TIS:.XVHnum[1] | BYTE
TISXVHnum2 | INT | IOD_TIS | TIS:.XVHnum[2] | BYTE
TISXVHnum3 | INT | IOD_TIS | TIS:.XVHnum[3] | BYTE
TISXVHnum4 | INT | IOD_TIS | TIS:.XVHnum[4] | BYTE
TISXVHnum5 | INT | IOD_TIS | TIS:.XVHnum[5] | BYTE
TISXVHnum6 | INT | IOD_TIS | TIS:.XVHnum[6] | BYTE
TISXVHnum7 | INT | IOD_TIS | TIS:.XVHnum[7] | BYTE
TISXVHnum8 | INT | IOD_TIS | TIS:.XVHnum[8] | BYTE
TISXVHnum9 | INT | IOD_TIS | TIS:.XVHnum[9] | BYTE
TISComSCADA2 | DIGITAL | IOD_TIS | TIS:.ComSCADA2
TISErrCommScada2 | DIGITAL | IOD_TIS | TIS:.ErrCommScada2
TISComSCADA3 | DIGITAL | IOD_TIS | TIS:.ComSCADA3
TISkom_nast_cas_izpada | INT | IOD_TIS | TIS:.kom_nast_cas_izpada
TISCirc1MaximumDemandA2 | REAL | IOD_TIS | TIS:.Circ[1].MaximumDemandA2
TISCirc1MaximumDemandA3 | REAL | IOD_TIS | TIS:.Circ[1].MaximumDemandA3
TISCirc2MaximumDemandA2 | REAL | IOD_TIS | TIS:.Circ[2].MaximumDemandA2
TISCirc2MaximumDemandA3 | REAL | IOD_TIS | TIS:.Circ[2].MaximumDemandA3
TISCirc3MaximumDemandA2 | REAL | IOD_TIS | TIS:.Circ[3].MaximumDemandA2
TISCirc3MaximumDemandA3 | REAL | IOD_TIS | TIS:.Circ[3].MaximumDemandA3
TISCirc4MaximumDemandA2 | REAL | IOD_TIS | TIS:.Circ[4].MaximumDemandA2
TISCirc4MaximumDemandA3 | REAL | IOD_TIS | TIS:.Circ[4].MaximumDemandA3
TISCirc1RazEner_D_SCADA | REAL | IOD_TIS | TIS:.Circ[1].RazEner_D_SCADA
TISCirc1RazEner_T_SCADA | REAL | IOD_TIS | TIS:.Circ[1].RazEner_T_SCADA
TISCirc1RazEner_M_SCADA | REAL | IOD_TIS | TIS:.Circ[1].RazEner_M_SCADA
TISCirc2RazEner_D_SCADA | REAL | IOD_TIS | TIS:.Circ[2].RazEner_D_SCADA
TISCirc2RazEner_T_SCADA | REAL | IOD_TIS | TIS:.Circ[2].RazEner_T_SCADA
TISCirc2RazEner_M_SCADA | REAL | IOD_TIS | TIS:.Circ[2].RazEner_M_SCADA
TISCirc3RazEner_D_SCADA | REAL | IOD_TIS | TIS:.Circ[3].RazEner_D_SCADA
TISCirc3RazEner_T_SCADA | REAL | IOD_TIS | TIS:.Circ[3].RazEner_T_SCADA
TISCirc3RazEner_M_SCADA | REAL | IOD_TIS | TIS:.Circ[3].RazEner_M_SCADA
TISCirc4RazEner_D_SCADA | REAL | IOD_TIS | TIS:.Circ[4].RazEner_D_SCADA
TISCirc4RazEner_T_SCADA | REAL | IOD_TIS | TIS:.Circ[4].RazEner_T_SCADA
TISCirc4RazEner_M_SCADA | REAL | IOD_TIS | TIS:.Circ[4].RazEner_M_SCADA
TISCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Dnevne_energija_scada1
TISCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Dnevne_energija_scada2
TISCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Tedenska_energija_scada1
TISCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Tedenska_energija_scada2
TISCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Mesecna_energija_scada1
TISCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Mesecna_energija_scada2

## variable_2
TISAlarmGenCirc1 | DIGITAL | IOD_TIS | TIS:.AlarmGenCirc1
TISAlarmGenCirc2 | DIGITAL | IOD_TIS | TIS:.AlarmGenCirc2
TISAlarmGenCirc3 | DIGITAL | IOD_TIS | TIS:.AlarmGenCirc3
TISAlarmGenCirc4 | DIGITAL | IOD_TIS | TIS:.AlarmGenCirc4
TISAlarmGenComm | DIGITAL | IOD_TIS | TIS:.AlarmGenComm
TISAlarmGenDI | DIGITAL | IOD_TIS | TIS:.AlarmGenDI
TISAlarmGenKlima1 | DIGITAL | IOD_TIS | TIS:.AlarmGenKlima1
TISAlarmGenKlima2 | DIGITAL | IOD_TIS | TIS:.AlarmGenKlima2
TISAlarmGenKlima3 | DIGITAL | IOD_TIS | TIS:.AlarmGenKlima3
TISAlarmGenRest | DIGITAL | IOD_TIS | TIS:.AlarmGenRest
TISAlarmGenSenzor | DIGITAL | IOD_TIS | TIS:.AlarmGenSenzor
TISAlarmGenTemp | DIGITAL | IOD_TIS | TIS:.AlarmGenTemp
TISAlarmGenVlPr | DIGITAL | IOD_TIS | TIS:.AlarmGenVlPr
TISAlarmGenVTV | DIGITAL | IOD_TIS | TIS:.AlarmGenVTV
TISComSCADA | DIGITAL | IOD_TIS | TIS:.ComSCADA
TISComSCADA1 | DIGITAL | IOD_TIS | TIS:.ComSCADA1
TISDI_F1_OdklHlOm1_IZP | DIGITAL | IOD_TIS | TIS:.DI_F1_OdklHlOm1_IZP
TISDI_F1_OdklHlOm1_ON | DIGITAL | IOD_TIS | TIS:.DI_F1_OdklHlOm1_ON
TISDI_F2_OdklHlOm2_IZP | DIGITAL | IOD_TIS | TIS:.DI_F2_OdklHlOm2_IZP
TISDI_F2_OdklHlOm2_ON | DIGITAL | IOD_TIS | TIS:.DI_F2_OdklHlOm2_ON
TISDI_F3_OdklHlOm3_IZP | DIGITAL | IOD_TIS | TIS:.DI_F3_OdklHlOm3_IZP
TISDI_F3_OdklHlOm3_ON | DIGITAL | IOD_TIS | TIS:.DI_F3_OdklHlOm3_ON
TISDI_F4_OdkPripVode_IZP | DIGITAL | IOD_TIS | TIS:.DI_F4_OdkPripVode_IZP
TISDI_F4_OdkPripVode_ON | DIGITAL | IOD_TIS | TIS:.DI_F4_OdkPripVode_ON
TISDI_HladOmara1_ERR | DIGITAL | IOD_TIS | TIS:.DI_HladOmara1_ERR
TISDI_HladOmara1_ON | DIGITAL | IOD_TIS | TIS:.DI_HladOmara1_ON
TISDI_HladOmara2_ERR | DIGITAL | IOD_TIS | TIS:.DI_HladOmara2_ERR
TISDI_HladOmara2_ON | DIGITAL | IOD_TIS | TIS:.DI_HladOmara2_ON
TISDI_HladOmara3_ERR | DIGITAL | IOD_TIS | TIS:.DI_HladOmara3_ERR
TISDI_HladOmara3_ON | DIGITAL | IOD_TIS | TIS:.DI_HladOmara3_ON
TISDI_PripVode1_ERR | DIGITAL | IOD_TIS | TIS:.DI_PripVode1_ERR
TISDI_PripVode1_ON | DIGITAL | IOD_TIS | TIS:.DI_PripVode1_ON
TISDI_PripVode2_ERR | DIGITAL | IOD_TIS | TIS:.DI_PripVode2_ERR
TISDI_PripVode2_ON | DIGITAL | IOD_TIS | TIS:.DI_PripVode2_ON
TISDI_Q0_DEG3_ON | DIGITAL | IOD_TIS | TIS:.DI_Q0_DEG3_ON
TISDI_Q0_EG3_ON | DIGITAL | IOD_TIS | TIS:.DI_Q0_EG3_ON
TISDI_Q0_GlavnoStikalo_ON | DIGITAL | IOD_TIS | TIS:.DI_Q0_GlavnoStikalo_ON
TISDI_Q0_UPS3_ON | DIGITAL | IOD_TIS | TIS:.DI_Q0_UPS3_ON
TISDI_RazlitjeVodeHO1 | DIGITAL | IOD_TIS | TIS:.DI_RazlitjeVodeHO1
TISDI_RazlitjeVodeHO2 | DIGITAL | IOD_TIS | TIS:.DI_RazlitjeVodeHO2
TISDI_RazlitjeVodeHO3 | DIGITAL | IOD_TIS | TIS:.DI_RazlitjeVodeHO3
TISDI_UPS_Alarm | DIGITAL | IOD_TIS | TIS:.DI_UPS_Alarm
TISDI_UPS_BatNacin | DIGITAL | IOD_TIS | TIS:.DI_UPS_BatNacin
TISDI_UPS_Polnjenje | DIGITAL | IOD_TIS | TIS:.DI_UPS_Polnjenje
TISDI_Vlazilec1_ERR | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec1_ERR
TISDI_Vlazilec1_ON | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec1_ON
TISDI_Vlazilec2_ERR | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec2_ERR
TISDI_Vlazilec2_ON | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec2_ON
TISDI_Vlazilec3_ERR | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec3_ERR
TISDI_Vlazilec3_ON | DIGITAL | IOD_TIS | TIS:.DI_Vlazilec3_ON
TISDIN_F1_OdklHlOm1_IZP | DIGITAL | IOD_TIS | TIS:.DIN_F1_OdklHlOm1_IZP
TISDIN_F2_OdklHlOm2_IZP | DIGITAL | IOD_TIS | TIS:.DIN_F2_OdklHlOm2_IZP
TISDIN_F3_OdklHlOm3_IZP | DIGITAL | IOD_TIS | TIS:.DIN_F3_OdklHlOm3_IZP
TISDIN_F4_OdkPripVode_IZP | DIGITAL | IOD_TIS | TIS:.DIN_F4_OdkPripVode_IZP
TISDIN_HladOmara1_ERR | DIGITAL | IOD_TIS | TIS:.DIN_HladOmara1_ERR
TISDIN_HladOmara2_ERR | DIGITAL | IOD_TIS | TIS:.DIN_HladOmara2_ERR
TISDIN_HladOmara3_ERR | DIGITAL | IOD_TIS | TIS:.DIN_HladOmara3_ERR
TISDIN_PripVode1_ERR | DIGITAL | IOD_TIS | TIS:.DIN_PripVode1_ERR
TISDIN_PripVode2_ERR | DIGITAL | IOD_TIS | TIS:.DIN_PripVode2_ERR
TISDIN_Vlazilec1_ERR | DIGITAL | IOD_TIS | TIS:.DIN_Vlazilec1_ERR
TISDIN_Vlazilec2_ERR | DIGITAL | IOD_TIS | TIS:.DIN_Vlazilec2_ERR
TISDIN_Vlazilec3_ERR | DIGITAL | IOD_TIS | TIS:.DIN_Vlazilec3_ERR
TISDO_HladOm1_Izklop | DIGITAL | IOD_TIS | TIS:.DO_HladOm1_Izklop
TISDO_HladOm2_Izklop | DIGITAL | IOD_TIS | TIS:.DO_HladOm2_Izklop
TISDO_HladOm3_Izklop | DIGITAL | IOD_TIS | TIS:.DO_HladOm3_Izklop
TISErrComCirc1 | DIGITAL | IOD_TIS | TIS:.ErrComCirc[1]
TISErrComCirc2 | DIGITAL | IOD_TIS | TIS:.ErrComCirc[2]
TISErrComCirc3 | DIGITAL | IOD_TIS | TIS:.ErrComCirc[3]
TISErrComCirc4 | DIGITAL | IOD_TIS | TIS:.ErrComCirc[4]
TISErrComCirc5 | DIGITAL | IOD_TIS | TIS:.ErrComCirc[5]
TISErrComKlima1 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[1]
TISErrComKlima2 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[2]
TISErrComKlima3 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[3]
TISErrComKlima4 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[4]
TISErrComKlima5 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[5]
TISErrComKlima6 | DIGITAL | IOD_TIS | TIS:.ErrComKlima[6]
TISErrCommScada | DIGITAL | IOD_TIS | TIS:.ErrCommScada
TISErrComPanelPLC | DIGITAL | IOD_TIS | TIS:.ErrComPanelPLC
TISErrComPort2 | DIGITAL | IOD_TIS | TIS:.ErrComPort2
TISErrorComCirc1Error | DIGITAL | IOD_TIS | TIS:.ErrorComCirc[1].Error
TISErrorComCirc2Error | DIGITAL | IOD_TIS | TIS:.ErrorComCirc[2].Error
TISErrorComCirc3Error | DIGITAL | IOD_TIS | TIS:.ErrorComCirc[3].Error
TISErrorComCirc4Error | DIGITAL | IOD_TIS | TIS:.ErrorComCirc[4].Error
TISErrorComCirc5Error | DIGITAL | IOD_TIS | TIS:.ErrorComCirc[5].Error
TISErrorComKlima1Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[1].Error
TISErrorComKlima2Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[2].Error
TISErrorComKlima3Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[3].Error
TISErrorComKlima4Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[4].Error
TISErrorComKlima5Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[5].Error
TISErrorComKlima6Error | DIGITAL | IOD_TIS | TIS:.ErrorComKlima[6].Error
TISKlima1AlarmKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[1].AlarmKompresor1
TISKlima1AlarmKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[1].AlarmKompresor2
TISKlima1Deluje | DIGITAL | IOD_TIS | TIS:.Klima[1].Deluje
TISKlima1EnergySaving | DIGITAL | IOD_TIS | TIS:.Klima[1].EnergySaving
TISKlima1FaultyEPROM | DIGITAL | IOD_TIS | TIS:.Klima[1].FaultyEPROM
TISKlima1FenThermalCutout | DIGITAL | IOD_TIS | TIS:.Klima[1].FenThermalCutout
TISKlima1GeneralAlarm | DIGITAL | IOD_TIS | TIS:.Klima[1].GeneralAlarm
TISKlima1Kompresor1naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[1].Kompresor1naMejiObrUr
TISKlima1Kompresor2naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[1].Kompresor2naMejiObrUr
TISKlima1Napaka | DIGITAL | IOD_TIS | TIS:.Klima[1].Napaka
TISKlima1NapakaPriPretokuZraka | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaPriPretokuZraka
TISKlima1NapakaSenzorPovratVode | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaSenzorPovratVode
TISKlima1NapakaSenzorTempIzpiha | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaSenzorTempIzpiha
TISKlima1NapakaSenzorTempProstora | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaSenzorTempProstora
TISKlima1NapakaSenzorVlaznosti | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaSenzorVlaznosti
TISKlima1NapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS | TIS:.Klima[1].NapakaSenzorZunanjeTemp
TISKlima1NiTokaVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[1].NiTokaVVlazilcu
TISKlima1NiVodeVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[1].NiVodeVVlazilcu
TISKlima1NizekPritiskKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[1].NizekPritiskKompresor1
TISKlima1NizekPritiskKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[1].NizekPritiskKompresor2
TISKlima1NizkaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[1].NizkaTempPovratneVode
TISKlima1NizkaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[1].NizkaTempVProstoru
TISKlima1NizkaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[1].NizkaVlaznost
TISKlima1OnOffEnablingBySupervisor | DIGITAL | IOD_TIS | TIS:.Klima[1].OnOffEnablingBySupervisor
TISKlima1PozarniAlarm | DIGITAL | IOD_TIS | TIS:.Klima[1].PozarniAlarm
TISKlima1Razvlazevanje | DIGITAL | IOD_TIS | TIS:.Klima[1].Razvlazevanje
TISKlima1RemoteOFFtoOutput | DIGITAL | IOD_TIS | TIS:.Klima[1].RemoteOFFtoOutput
TISKlima1RemoteOnOff | DIGITAL | IOD_TIS | TIS:.Klima[1].RemoteOnOff
TISKlima1RocniIzklop | DIGITAL | IOD_TIS | TIS:.Klima[1].RocniIzklop
TISKlima1SenzorjiStatus | DIGITAL | IOD_TIS | TIS:.Klima[1].SenzorjiStatus
TISKlima1StoppedByAlarms | DIGITAL | IOD_TIS | TIS:.Klima[1].StoppedByAlarms
TISKlima1ThermalCutoutHeater1 | DIGITAL | IOD_TIS | TIS:.Klima[1].ThermalCutoutHeater1
TISKlima1ThermalCutoutHeater2 | DIGITAL | IOD_TIS | TIS:.Klima[1].ThermalCutoutHeater2
TISKlima1UnitOnOff | DIGITAL | IOD_TIS | TIS:.Klima[1].UnitOnOff
TISKlima1VentilatorNaMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[1].VentilatorNaMejiObrUr
TISKlima1VentilGretjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[1].VentilGretjeOdpiranje
TISKlima1VentilGretjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[1].VentilGretjeZapiranje
TISKlima1VentilHlajenjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[1].VentilHlajenjeOdpiranje
TISKlima1VentilHlajenjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[1].VentilHlajenjeZapiranje
TISKlima1VisokaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[1].VisokaTempPovratneVode
TISKlima1VisokaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[1].VisokaTempVProstoru
TISKlima1VisokaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[1].VisokaVlaznost
TISKlima1VisokTokVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[1].VisokTokVVlazilcu
TISKlima1Vlazenje | DIGITAL | IOD_TIS | TIS:.Klima[1].Vlazenje
TISKlima1ZamasenFilter | DIGITAL | IOD_TIS | TIS:.Klima[1].ZamasenFilter
TISKlima2AlarmKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[2].AlarmKompresor1
TISKlima2AlarmKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[2].AlarmKompresor2
TISKlima2Deluje | DIGITAL | IOD_TIS | TIS:.Klima[2].Deluje
TISKlima2EnergySaving | DIGITAL | IOD_TIS | TIS:.Klima[2].EnergySaving
TISKlima2FaultyEPROM | DIGITAL | IOD_TIS | TIS:.Klima[2].FaultyEPROM
TISKlima2FenThermalCutout | DIGITAL | IOD_TIS | TIS:.Klima[2].FenThermalCutout
TISKlima2GeneralAlarm | DIGITAL | IOD_TIS | TIS:.Klima[2].GeneralAlarm
TISKlima2Kompresor1naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[2].Kompresor1naMejiObrUr
TISKlima2Kompresor2naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[2].Kompresor2naMejiObrUr
TISKlima2Napaka | DIGITAL | IOD_TIS | TIS:.Klima[2].Napaka
TISKlima2NapakaPriPretokuZraka | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaPriPretokuZraka
TISKlima2NapakaSenzorPovratVode | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaSenzorPovratVode
TISKlima2NapakaSenzorTempIzpiha | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaSenzorTempIzpiha
TISKlima2NapakaSenzorTempProstora | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaSenzorTempProstora
TISKlima2NapakaSenzorVlaznosti | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaSenzorVlaznosti
TISKlima2NapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS | TIS:.Klima[2].NapakaSenzorZunanjeTemp
TISKlima2NiTokaVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[2].NiTokaVVlazilcu
TISKlima2NiVodeVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[2].NiVodeVVlazilcu
TISKlima2NizekPritiskKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[2].NizekPritiskKompresor1
TISKlima2NizekPritiskKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[2].NizekPritiskKompresor2
TISKlima2NizkaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[2].NizkaTempPovratneVode
TISKlima2NizkaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[2].NizkaTempVProstoru
TISKlima2NizkaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[2].NizkaVlaznost
TISKlima2OnOffEnablingBySupervisor | DIGITAL | IOD_TIS | TIS:.Klima[2].OnOffEnablingBySupervisor
TISKlima2PozarniAlarm | DIGITAL | IOD_TIS | TIS:.Klima[2].PozarniAlarm
TISKlima2Razvlazevanje | DIGITAL | IOD_TIS | TIS:.Klima[2].Razvlazevanje
TISKlima2RemoteOFFtoOutput | DIGITAL | IOD_TIS | TIS:.Klima[2].RemoteOFFtoOutput
TISKlima2RemoteOnOff | DIGITAL | IOD_TIS | TIS:.Klima[2].RemoteOnOff
TISKlima2RocniIzklop | DIGITAL | IOD_TIS | TIS:.Klima[2].RocniIzklop
TISKlima2SenzorjiStatus | DIGITAL | IOD_TIS | TIS:.Klima[2].SenzorjiStatus
TISKlima2StoppedByAlarms | DIGITAL | IOD_TIS | TIS:.Klima[2].StoppedByAlarms
TISKlima2ThermalCutoutHeater1 | DIGITAL | IOD_TIS | TIS:.Klima[2].ThermalCutoutHeater1
TISKlima2ThermalCutoutHeater2 | DIGITAL | IOD_TIS | TIS:.Klima[2].ThermalCutoutHeater2
TISKlima2UnitOnOff | DIGITAL | IOD_TIS | TIS:.Klima[2].UnitOnOff
TISKlima2VentilatorNaMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[2].VentilatorNaMejiObrUr
TISKlima2VentilGretjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[2].VentilGretjeOdpiranje
TISKlima2VentilGretjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[2].VentilGretjeZapiranje
TISKlima2VentilHlajenjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[2].VentilHlajenjeOdpiranje
TISKlima2VentilHlajenjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[2].VentilHlajenjeZapiranje
TISKlima2VisokaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[2].VisokaTempPovratneVode
TISKlima2VisokaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[2].VisokaTempVProstoru
TISKlima2VisokaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[2].VisokaVlaznost
TISKlima2VisokTokVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[2].VisokTokVVlazilcu
TISKlima2Vlazenje | DIGITAL | IOD_TIS | TIS:.Klima[2].Vlazenje
TISKlima2ZamasenFilter | DIGITAL | IOD_TIS | TIS:.Klima[2].ZamasenFilter
TISKlima3AlarmKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[3].AlarmKompresor1
TISKlima3AlarmKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[3].AlarmKompresor2
TISKlima3Deluje | DIGITAL | IOD_TIS | TIS:.Klima[3].Deluje
TISKlima3EnergySaving | DIGITAL | IOD_TIS | TIS:.Klima[3].EnergySaving
TISKlima3FaultyEPROM | DIGITAL | IOD_TIS | TIS:.Klima[3].FaultyEPROM
TISKlima3FenThermalCutout | DIGITAL | IOD_TIS | TIS:.Klima[3].FenThermalCutout
TISKlima3GeneralAlarm | DIGITAL | IOD_TIS | TIS:.Klima[3].GeneralAlarm
TISKlima3Kompresor1naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[3].Kompresor1naMejiObrUr
TISKlima3Kompresor2naMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[3].Kompresor2naMejiObrUr
TISKlima3Napaka | DIGITAL | IOD_TIS | TIS:.Klima[3].Napaka
TISKlima3NapakaPriPretokuZraka | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaPriPretokuZraka
TISKlima3NapakaSenzorPovratVode | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaSenzorPovratVode
TISKlima3NapakaSenzorTempIzpiha | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaSenzorTempIzpiha
TISKlima3NapakaSenzorTempProstora | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaSenzorTempProstora
TISKlima3NapakaSenzorVlaznosti | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaSenzorVlaznosti
TISKlima3NapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS | TIS:.Klima[3].NapakaSenzorZunanjeTemp
TISKlima3NiTokaVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[3].NiTokaVVlazilcu
TISKlima3NiVodeVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[3].NiVodeVVlazilcu
TISKlima3NizekPritiskKompresor1 | DIGITAL | IOD_TIS | TIS:.Klima[3].NizekPritiskKompresor1
TISKlima3NizekPritiskKompresor2 | DIGITAL | IOD_TIS | TIS:.Klima[3].NizekPritiskKompresor2
TISKlima3NizkaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[3].NizkaTempPovratneVode
TISKlima3NizkaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[3].NizkaTempVProstoru
TISKlima3NizkaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[3].NizkaVlaznost
TISKlima3OnOffEnablingBySupervisor | DIGITAL | IOD_TIS | TIS:.Klima[3].OnOffEnablingBySupervisor
TISKlima3PozarniAlarm | DIGITAL | IOD_TIS | TIS:.Klima[3].PozarniAlarm
TISKlima3Razvlazevanje | DIGITAL | IOD_TIS | TIS:.Klima[3].Razvlazevanje
TISKlima3RemoteOFFtoOutput | DIGITAL | IOD_TIS | TIS:.Klima[3].RemoteOFFtoOutput
TISKlima3RemoteOnOff | DIGITAL | IOD_TIS | TIS:.Klima[3].RemoteOnOff
TISKlima3RocniIzklop | DIGITAL | IOD_TIS | TIS:.Klima[3].RocniIzklop
TISKlima3SenzorjiStatus | DIGITAL | IOD_TIS | TIS:.Klima[3].SenzorjiStatus
TISKlima3StoppedByAlarms | DIGITAL | IOD_TIS | TIS:.Klima[3].StoppedByAlarms
TISKlima3ThermalCutoutHeater1 | DIGITAL | IOD_TIS | TIS:.Klima[3].ThermalCutoutHeater1
TISKlima3ThermalCutoutHeater2 | DIGITAL | IOD_TIS | TIS:.Klima[3].ThermalCutoutHeater2
TISKlima3UnitOnOff | DIGITAL | IOD_TIS | TIS:.Klima[3].UnitOnOff
TISKlima3VentilatorNaMejiObrUr | DIGITAL | IOD_TIS | TIS:.Klima[3].VentilatorNaMejiObrUr
TISKlima3VentilGretjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[3].VentilGretjeOdpiranje
TISKlima3VentilGretjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[3].VentilGretjeZapiranje
TISKlima3VentilHlajenjeOdpiranje | DIGITAL | IOD_TIS | TIS:.Klima[3].VentilHlajenjeOdpiranje
TISKlima3VentilHlajenjeZapiranje | DIGITAL | IOD_TIS | TIS:.Klima[3].VentilHlajenjeZapiranje
TISKlima3VisokaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.Klima[3].VisokaTempPovratneVode
TISKlima3VisokaTempVProstoru | DIGITAL | IOD_TIS | TIS:.Klima[3].VisokaTempVProstoru
TISKlima3VisokaVlaznost | DIGITAL | IOD_TIS | TIS:.Klima[3].VisokaVlaznost
TISKlima3VisokTokVVlazilcu | DIGITAL | IOD_TIS | TIS:.Klima[3].VisokTokVVlazilcu
TISKlima3Vlazenje | DIGITAL | IOD_TIS | TIS:.Klima[3].Vlazenje
TISKlima3ZamasenFilter | DIGITAL | IOD_TIS | TIS:.Klima[3].ZamasenFilter
TISKlimaAErrors10 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[10]
TISKlimaAErrors11 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[11]
TISKlimaAErrors12 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[12]
TISKlimaAErrors13 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[13]
TISKlimaAErrors14 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[14]
TISKlimaAErrors15 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[15]
TISKlimaAErrors16 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[16]
TISKlimaAErrors17 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[17]
TISKlimaAErrors18 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[18]
TISKlimaAErrors19 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[19]
TISKlimaAErrors1 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[1]
TISKlimaAErrors20 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[20]
TISKlimaAErrors21 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[21]
TISKlimaAErrors22 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[22]
TISKlimaAErrors23 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[23]
TISKlimaAErrors24 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[24]
TISKlimaAErrors25 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[25]
TISKlimaAErrors26 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[26]
TISKlimaAErrors27 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[27]
TISKlimaAErrors28 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[28]
TISKlimaAErrors29 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[29]
TISKlimaAErrors2 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[2]
TISKlimaAErrors30 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[30]
TISKlimaAErrors31 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[31]
TISKlimaAErrors32 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[32]
TISKlimaAErrors33 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[33]
TISKlimaAErrors34 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[34]
TISKlimaAErrors35 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[35]
TISKlimaAErrors36 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[36]
TISKlimaAErrors37 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[37]
TISKlimaAErrors38 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[38]
TISKlimaAErrors39 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[39]
TISKlimaAErrors3 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[3]
TISKlimaAErrors40 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[40]
TISKlimaAErrors4 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[4]
TISKlimaAErrors5 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[5]
TISKlimaAErrors6 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[6]
TISKlimaAErrors7 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[7]
TISKlimaAErrors8 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[8]
TISKlimaAErrors9 | DIGITAL | IOD_TIS | TIS:.KlimaAErrors[9]
TISKlimaBErrors10 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[10]
TISKlimaBErrors11 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[11]
TISKlimaBErrors12 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[12]
TISKlimaBErrors13 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[13]
TISKlimaBErrors14 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[14]
TISKlimaBErrors15 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[15]
TISKlimaBErrors16 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[16]
TISKlimaBErrors17 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[17]
TISKlimaBErrors18 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[18]
TISKlimaBErrors19 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[19]
TISKlimaBErrors1 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[1]
TISKlimaBErrors20 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[20]
TISKlimaBErrors21 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[21]
TISKlimaBErrors22 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[22]
TISKlimaBErrors23 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[23]
TISKlimaBErrors24 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[24]
TISKlimaBErrors25 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[25]
TISKlimaBErrors26 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[26]
TISKlimaBErrors27 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[27]
TISKlimaBErrors28 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[28]
TISKlimaBErrors29 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[29]
TISKlimaBErrors2 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[2]
TISKlimaBErrors30 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[30]
TISKlimaBErrors31 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[31]
TISKlimaBErrors32 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[32]
TISKlimaBErrors33 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[33]
TISKlimaBErrors34 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[34]
TISKlimaBErrors35 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[35]
TISKlimaBErrors36 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[36]
TISKlimaBErrors37 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[37]
TISKlimaBErrors38 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[38]
TISKlimaBErrors39 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[39]
TISKlimaBErrors3 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[3]
TISKlimaBErrors40 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[40]
TISKlimaBErrors4 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[4]
TISKlimaBErrors5 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[5]
TISKlimaBErrors6 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[6]
TISKlimaBErrors7 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[7]
TISKlimaBErrors8 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[8]
TISKlimaBErrors9 | DIGITAL | IOD_TIS | TIS:.KlimaBErrors[9]
TISKlimaCErrors10 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[10]
TISKlimaCErrors11 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[11]
TISKlimaCErrors12 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[12]
TISKlimaCErrors13 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[13]
TISKlimaCErrors14 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[14]
TISKlimaCErrors15 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[15]
TISKlimaCErrors16 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[16]
TISKlimaCErrors17 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[17]
TISKlimaCErrors18 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[18]
TISKlimaCErrors19 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[19]
TISKlimaCErrors1 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[1]
TISKlimaCErrors20 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[20]
TISKlimaCErrors21 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[21]
TISKlimaCErrors22 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[22]
TISKlimaCErrors23 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[23]
TISKlimaCErrors24 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[24]
TISKlimaCErrors25 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[25]
TISKlimaCErrors26 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[26]
TISKlimaCErrors27 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[27]
TISKlimaCErrors28 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[28]
TISKlimaCErrors29 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[29]
TISKlimaCErrors2 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[2]
TISKlimaCErrors30 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[30]
TISKlimaCErrors31 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[31]
TISKlimaCErrors32 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[32]
TISKlimaCErrors33 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[33]
TISKlimaCErrors34 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[34]
TISKlimaCErrors35 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[35]
TISKlimaCErrors36 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[36]
TISKlimaCErrors37 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[37]
TISKlimaCErrors38 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[38]
TISKlimaCErrors39 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[39]
TISKlimaCErrors3 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[3]
TISKlimaCErrors40 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[40]
TISKlimaCErrors4 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[4]
TISKlimaCErrors5 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[5]
TISKlimaCErrors6 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[6]
TISKlimaCErrors7 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[7]
TISKlimaCErrors8 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[8]
TISKlimaCErrors9 | DIGITAL | IOD_TIS | TIS:.KlimaCErrors[9]
TISKlimaGalAlarmKompresor1 | DIGITAL | IOD_TIS | TIS:.KlimaGal.AlarmKompresor1
TISKlimaGalAlarmKompresor2 | DIGITAL | IOD_TIS | TIS:.KlimaGal.AlarmKompresor2
TISKlimaGalDeluje | DIGITAL | IOD_TIS | TIS:.KlimaGal.Deluje
TISKlimaGalEnergySaving | DIGITAL | IOD_TIS | TIS:.KlimaGal.EnergySaving
TISKlimaGalFaultyEPROM | DIGITAL | IOD_TIS | TIS:.KlimaGal.FaultyEPROM
TISKlimaGalFenThermalCutout | DIGITAL | IOD_TIS | TIS:.KlimaGal.FenThermalCutout
TISKlimaGalGeneralAlarm | DIGITAL | IOD_TIS | TIS:.KlimaGal.GeneralAlarm
TISKlimaGalKompresor1naMejiObrUr | DIGITAL | IOD_TIS | TIS:.KlimaGal.Kompresor1naMejiObrUr
TISKlimaGalKompresor2naMejiObrUr | DIGITAL | IOD_TIS | TIS:.KlimaGal.Kompresor2naMejiObrUr
TISKlimaGalNapaka | DIGITAL | IOD_TIS | TIS:.KlimaGal.Napaka
TISKlimaGalNapakaPriPretokuZraka | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaPriPretokuZraka
TISKlimaGalNapakaSenzorPovratVode | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaSenzorPovratVode
TISKlimaGalNapakaSenzorTempIzpiha | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaSenzorTempIzpiha
TISKlimaGalNapakaSenzorTempProstora | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaSenzorTempProstora
TISKlimaGalNapakaSenzorVlaznosti | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaSenzorVlaznosti
TISKlimaGalNapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS | TIS:.KlimaGal.NapakaSenzorZunanjeTemp
TISKlimaGalNiTokaVVlazilcu | DIGITAL | IOD_TIS | TIS:.KlimaGal.NiTokaVVlazilcu
TISKlimaGalNiVodeVVlazilcu | DIGITAL | IOD_TIS | TIS:.KlimaGal.NiVodeVVlazilcu
TISKlimaGalNizekPritiskKompresor1 | DIGITAL | IOD_TIS | TIS:.KlimaGal.NizekPritiskKompresor1
TISKlimaGalNizekPritiskKompresor2 | DIGITAL | IOD_TIS | TIS:.KlimaGal.NizekPritiskKompresor2
TISKlimaGalNizkaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.KlimaGal.NizkaTempPovratneVode
TISKlimaGalNizkaTempVProstoru | DIGITAL | IOD_TIS | TIS:.KlimaGal.NizkaTempVProstoru
TISKlimaGalNizkaVlaznost | DIGITAL | IOD_TIS | TIS:.KlimaGal.NizkaVlaznost
TISKlimaGalOnOffEnablingBySupervisor | DIGITAL | IOD_TIS | TIS:.KlimaGal.OnOffEnablingBySupervisor
TISKlimaGalPozarniAlarm | DIGITAL | IOD_TIS | TIS:.KlimaGal.PozarniAlarm
TISKlimaGalRazvlazevanje | DIGITAL | IOD_TIS | TIS:.KlimaGal.Razvlazevanje
TISKlimaGalRemoteOFFtoOutput | DIGITAL | IOD_TIS | TIS:.KlimaGal.RemoteOFFtoOutput
TISKlimaGalRemoteOnOff | DIGITAL | IOD_TIS | TIS:.KlimaGal.RemoteOnOff
TISKlimaGalRocniIzklop | DIGITAL | IOD_TIS | TIS:.KlimaGal.RocniIzklop
TISKlimaGalSenzorjiStatus | DIGITAL | IOD_TIS | TIS:.KlimaGal.SenzorjiStatus
TISKlimaGalStoppedByAlarms | DIGITAL | IOD_TIS | TIS:.KlimaGal.StoppedByAlarms
TISKlimaGalThermalCutoutHeater1 | DIGITAL | IOD_TIS | TIS:.KlimaGal.ThermalCutoutHeater1
TISKlimaGalThermalCutoutHeater2 | DIGITAL | IOD_TIS | TIS:.KlimaGal.ThermalCutoutHeater2
TISKlimaGalUnitOnOff | DIGITAL | IOD_TIS | TIS:.KlimaGal.UnitOnOff
TISKlimaGalVentilatorNaMejiObrUr | DIGITAL | IOD_TIS | TIS:.KlimaGal.VentilatorNaMejiObrUr
TISKlimaGalVentilGretjeOdpiranje | DIGITAL | IOD_TIS | TIS:.KlimaGal.VentilGretjeOdpiranje
TISKlimaGalVentilGretjeZapiranje | DIGITAL | IOD_TIS | TIS:.KlimaGal.VentilGretjeZapiranje
TISKlimaGalVentilHlajenjeOdpiranje | DIGITAL | IOD_TIS | TIS:.KlimaGal.VentilHlajenjeOdpiranje
TISKlimaGalVentilHlajenjeZapiranje | DIGITAL | IOD_TIS | TIS:.KlimaGal.VentilHlajenjeZapiranje
TISKlimaGalVisokaTempPovratneVode | DIGITAL | IOD_TIS | TIS:.KlimaGal.VisokaTempPovratneVode
TISKlimaGalVisokaTempVProstoru | DIGITAL | IOD_TIS | TIS:.KlimaGal.VisokaTempVProstoru
TISKlimaGalVisokaVlaznost | DIGITAL | IOD_TIS | TIS:.KlimaGal.VisokaVlaznost
TISKlimaGalVisokTokVVlazilcu | DIGITAL | IOD_TIS | TIS:.KlimaGal.VisokTokVVlazilcu
TISKlimaGalVlazenje | DIGITAL | IOD_TIS | TIS:.KlimaGal.Vlazenje
TISKlimaGalZamasenFilter | DIGITAL | IOD_TIS | TIS:.KlimaGal.ZamasenFilter
TISKlimeNaCas | DIGITAL | IOD_TIS | TIS:.KlimeNaCas
TISNapakaSenzorTemp10 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[10]
TISNapakaSenzorTemp11 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[11]
TISNapakaSenzorTemp12 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[12]
TISNapakaSenzorTemp13 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[13]
TISNapakaSenzorTemp14 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[14]
TISNapakaSenzorTemp15 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[15]
TISNapakaSenzorTemp16 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[16]
TISNapakaSenzorTemp17 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[17]
TISNapakaSenzorTemp18 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[18]
TISNapakaSenzorTemp19 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[19]
TISNapakaSenzorTemp1 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[1]
TISNapakaSenzorTemp2 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[2]
TISNapakaSenzorTemp3 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[3]
TISNapakaSenzorTemp4 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[4]
TISNapakaSenzorTemp5 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[5]
TISNapakaSenzorTemp6 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[6]
TISNapakaSenzorTemp7 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[7]
TISNapakaSenzorTemp8 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[8]
TISNapakaSenzorTemp9 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorTemp[9]
TISNapakaSenzorVlaga10 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[10]
TISNapakaSenzorVlaga11 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[11]
TISNapakaSenzorVlaga12 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[12]
TISNapakaSenzorVlaga13 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[13]
TISNapakaSenzorVlaga14 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[14]
TISNapakaSenzorVlaga15 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[15]
TISNapakaSenzorVlaga16 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[16]
TISNapakaSenzorVlaga17 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[17]
TISNapakaSenzorVlaga18 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[18]
TISNapakaSenzorVlaga19 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[19]
TISNapakaSenzorVlaga1 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[1]
TISNapakaSenzorVlaga2 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[2]
TISNapakaSenzorVlaga3 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[3]
TISNapakaSenzorVlaga4 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[4]
TISNapakaSenzorVlaga5 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[5]
TISNapakaSenzorVlaga6 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[6]
TISNapakaSenzorVlaga7 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[7]
TISNapakaSenzorVlaga8 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[8]
TISNapakaSenzorVlaga9 | DIGITAL | IOD_TIS | TIS:.NapakaSenzorVlaga[9]
TISSetDateTime | DIGITAL | IOD_TIS | TIS:.SetDateTime
TISSetDateTimeDemand | DIGITAL | IOD_TIS | TIS:.SetDateTimeDemand
TISSetDateTimeError | DIGITAL | IOD_TIS | TIS:.SetDateTimeError
TISSetDateTimeFinished | DIGITAL | IOD_TIS | TIS:.SetDateTimeFinished
TISSetRemoteOnOff1 | DIGITAL | IOD_TIS | TIS:.SetRemoteOnOff[1]
TISSetRemoteOnOff2 | DIGITAL | IOD_TIS | TIS:.SetRemoteOnOff[2]
TISSetRemoteOnOff3 | DIGITAL | IOD_TIS | TIS:.SetRemoteOnOff[3]
TISSlabaBaterijaPLC_A1 | DIGITAL | IOD_TIS | TIS:.SlabaBaterijaPLC_A1
TISTempTSprevisoka10 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[10]
TISTempTSprevisoka11 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[11]
TISTempTSprevisoka12 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[12]
TISTempTSprevisoka13 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[13]
TISTempTSprevisoka14 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[14]
TISTempTSprevisoka15 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[15]
TISTempTSprevisoka16 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[16]
TISTempTSprevisoka17 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[17]
TISTempTSprevisoka18 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[18]
TISTempTSprevisoka19 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[19]
TISTempTSprevisoka1 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[1]
TISTempTSprevisoka2 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[2]
TISTempTSprevisoka3 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[3]
TISTempTSprevisoka4 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[4]
TISTempTSprevisoka5 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[5]
TISTempTSprevisoka6 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[6]
TISTempTSprevisoka7 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[7]
TISTempTSprevisoka8 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[8]
TISTempTSprevisoka9 | DIGITAL | IOD_TIS | TIS:.TempTSprevisoka[9]
TISUserLoggedIn | DIGITAL | IOD_TIS | TIS:.UserLoggedIn
TISXVH_AlarmOn | DIGITAL | IOD_TIS | TIS:.XVH_AlarmOn
TISXVH_RemoteStatus1 | DIGITAL | IOD_TIS | TIS:.XVH_RemoteStatus[1]
TISXVH_RemoteStatus2 | DIGITAL | IOD_TIS | TIS:.XVH_RemoteStatus[2]
TISXVH_RemoteStatus3 | DIGITAL | IOD_TIS | TIS:.XVH_RemoteStatus[3]
TISXVH_setCircNum1 | DIGITAL | IOD_TIS | TIS:.XVH_setCircNum[1]
TISXVH_setCircNum2 | DIGITAL | IOD_TIS | TIS:.XVH_setCircNum[2]
TISXVH_setCircNum3 | DIGITAL | IOD_TIS | TIS:.XVH_setCircNum[3]
TISXVH_setCircNum4 | DIGITAL | IOD_TIS | TIS:.XVH_setCircNum[4]
TISXVH_setCircNum5 | DIGITAL | IOD_TIS | TIS:.XVH_setCircNum[5]
TISXVH_setKlimaNum1 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[1]
TISXVH_setKlimaNum2 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[2]
TISXVH_setKlimaNum3 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[3]
TISXVH_setKlimaNum4 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[4]
TISXVH_setKlimaNum5 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[5]
TISXVH_setKlimaNum6 | DIGITAL | IOD_TIS | TIS:.XVH_setKlimaNum[6]
TISComSCADA2 | DIGITAL | IOD_TIS | TIS:.ComSCADA2
TISErrCommScada2 | DIGITAL | IOD_TIS | TIS:.ErrCommScada2
TISComSCADA3 | DIGITAL | IOD_TIS | TIS:.ComSCADA3
TISCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Dnevne_energija_scada1
TISCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Dnevne_energija_scada2
TISCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Tedenska_energija_scada1
TISCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Tedenska_energija_scada2
TISCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Mesecna_energija_scada1
TISCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_TIS | TIS:.Circ_Vpis_Mesecna_energija_scada2
TISDateTimeDan | INT | IOD_TIS | TIS:.DateTime.Dan | BYTE
TISDateTimeLeto | INT | IOD_TIS | TIS:.DateTime.Leto | BYTE
TISDateTimeMesec | INT | IOD_TIS | TIS:.DateTime.Mesec | BYTE
TISDateTimeMinuta | INT | IOD_TIS | TIS:.DateTime.Minuta | BYTE
TISDateTimeSekunda | INT | IOD_TIS | TIS:.DateTime.Sekunda | BYTE
TISDateTimeUra | INT | IOD_TIS | TIS:.DateTime.Ura | BYTE
TISErrorComCirc1Code10 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[10] | BYTE
TISErrorComCirc1Code11 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[11] | BYTE
TISErrorComCirc1Code12 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[12] | BYTE
TISErrorComCirc1Code13 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[13] | BYTE
TISErrorComCirc1Code14 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[14] | BYTE
TISErrorComCirc1Code15 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[15] | BYTE
TISErrorComCirc1Code1 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[1] | BYTE
TISErrorComCirc1Code2 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[2] | BYTE
TISErrorComCirc1Code3 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[3] | BYTE
TISErrorComCirc1Code4 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[4] | BYTE
TISErrorComCirc1Code5 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[5] | BYTE
TISErrorComCirc1Code6 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[6] | BYTE
TISErrorComCirc1Code7 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[7] | BYTE
TISErrorComCirc1Code8 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[8] | BYTE
TISErrorComCirc1Code9 | INT | IOD_TIS | TIS:.ErrorComCirc[1].Code[9] | BYTE
TISErrorComCirc1Status | INT | IOD_TIS | TIS:.ErrorComCirc[1].Status
TISErrorComCirc2Code10 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[10] | BYTE
TISErrorComCirc2Code11 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[11] | BYTE
TISErrorComCirc2Code12 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[12] | BYTE
TISErrorComCirc2Code13 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[13] | BYTE
TISErrorComCirc2Code14 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[14] | BYTE
TISErrorComCirc2Code15 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[15] | BYTE
TISErrorComCirc2Code1 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[1] | BYTE
TISErrorComCirc2Code2 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[2] | BYTE
TISErrorComCirc2Code3 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[3] | BYTE
TISErrorComCirc2Code4 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[4] | BYTE
TISErrorComCirc2Code5 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[5] | BYTE
TISErrorComCirc2Code6 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[6] | BYTE
TISErrorComCirc2Code7 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[7] | BYTE
TISErrorComCirc2Code8 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[8] | BYTE
TISErrorComCirc2Code9 | INT | IOD_TIS | TIS:.ErrorComCirc[2].Code[9] | BYTE
TISErrorComCirc2Status | INT | IOD_TIS | TIS:.ErrorComCirc[2].Status
TISErrorComCirc3Code10 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[10] | BYTE
TISErrorComCirc3Code11 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[11] | BYTE
TISErrorComCirc3Code12 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[12] | BYTE
TISErrorComCirc3Code13 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[13] | BYTE
TISErrorComCirc3Code14 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[14] | BYTE
TISErrorComCirc3Code15 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[15] | BYTE
TISErrorComCirc3Code1 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[1] | BYTE
TISErrorComCirc3Code2 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[2] | BYTE
TISErrorComCirc3Code3 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[3] | BYTE
TISErrorComCirc3Code4 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[4] | BYTE
TISErrorComCirc3Code5 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[5] | BYTE
TISErrorComCirc3Code6 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[6] | BYTE
TISErrorComCirc3Code7 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[7] | BYTE
TISErrorComCirc3Code8 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[8] | BYTE
TISErrorComCirc3Code9 | INT | IOD_TIS | TIS:.ErrorComCirc[3].Code[9] | BYTE
TISErrorComCirc3Status | INT | IOD_TIS | TIS:.ErrorComCirc[3].Status
TISErrorComCirc4Code10 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[10] | BYTE
TISErrorComCirc4Code11 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[11] | BYTE
TISErrorComCirc4Code12 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[12] | BYTE
TISErrorComCirc4Code13 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[13] | BYTE
TISErrorComCirc4Code14 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[14] | BYTE
TISErrorComCirc4Code15 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[15] | BYTE
TISErrorComCirc4Code1 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[1] | BYTE
TISErrorComCirc4Code2 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[2] | BYTE
TISErrorComCirc4Code3 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[3] | BYTE
TISErrorComCirc4Code4 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[4] | BYTE
TISErrorComCirc4Code5 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[5] | BYTE
TISErrorComCirc4Code6 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[6] | BYTE
TISErrorComCirc4Code7 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[7] | BYTE
TISErrorComCirc4Code8 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[8] | BYTE
TISErrorComCirc4Code9 | INT | IOD_TIS | TIS:.ErrorComCirc[4].Code[9] | BYTE
TISErrorComCirc4Status | INT | IOD_TIS | TIS:.ErrorComCirc[4].Status
TISErrorComCirc5Code10 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[10] | BYTE
TISErrorComCirc5Code11 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[11] | BYTE
TISErrorComCirc5Code12 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[12] | BYTE
TISErrorComCirc5Code13 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[13] | BYTE
TISErrorComCirc5Code14 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[14] | BYTE
TISErrorComCirc5Code15 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[15] | BYTE
TISErrorComCirc5Code1 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[1] | BYTE
TISErrorComCirc5Code2 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[2] | BYTE
TISErrorComCirc5Code3 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[3] | BYTE
TISErrorComCirc5Code4 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[4] | BYTE
TISErrorComCirc5Code5 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[5] | BYTE
TISErrorComCirc5Code6 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[6] | BYTE
TISErrorComCirc5Code7 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[7] | BYTE
TISErrorComCirc5Code8 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[8] | BYTE
TISErrorComCirc5Code9 | INT | IOD_TIS | TIS:.ErrorComCirc[5].Code[9] | BYTE
TISErrorComCirc5Status | INT | IOD_TIS | TIS:.ErrorComCirc[5].Status
TISErrorComKlima1Code10 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[10] | BYTE
TISErrorComKlima1Code11 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[11] | BYTE
TISErrorComKlima1Code12 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[12] | BYTE
TISErrorComKlima1Code13 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[13] | BYTE
TISErrorComKlima1Code14 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[14] | BYTE
TISErrorComKlima1Code15 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[15] | BYTE
TISErrorComKlima1Code1 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[1] | BYTE
TISErrorComKlima1Code2 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[2] | BYTE
TISErrorComKlima1Code3 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[3] | BYTE
TISErrorComKlima1Code4 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[4] | BYTE
TISErrorComKlima1Code5 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[5] | BYTE
TISErrorComKlima1Code6 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[6] | BYTE
TISErrorComKlima1Code7 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[7] | BYTE
TISErrorComKlima1Code8 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[8] | BYTE
TISErrorComKlima1Code9 | INT | IOD_TIS | TIS:.ErrorComKlima[1].Code[9] | BYTE
TISErrorComKlima1Status | INT | IOD_TIS | TIS:.ErrorComKlima[1].Status
TISErrorComKlima2Code10 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[10] | BYTE
TISErrorComKlima2Code11 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[11] | BYTE
TISErrorComKlima2Code12 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[12] | BYTE
TISErrorComKlima2Code13 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[13] | BYTE
TISErrorComKlima2Code14 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[14] | BYTE
TISErrorComKlima2Code15 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[15] | BYTE
TISErrorComKlima2Code1 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[1] | BYTE
TISErrorComKlima2Code2 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[2] | BYTE
TISErrorComKlima2Code3 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[3] | BYTE
TISErrorComKlima2Code4 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[4] | BYTE
TISErrorComKlima2Code5 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[5] | BYTE
TISErrorComKlima2Code6 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[6] | BYTE
TISErrorComKlima2Code7 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[7] | BYTE
TISErrorComKlima2Code8 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[8] | BYTE
TISErrorComKlima2Code9 | INT | IOD_TIS | TIS:.ErrorComKlima[2].Code[9] | BYTE
TISErrorComKlima2Status | INT | IOD_TIS | TIS:.ErrorComKlima[2].Status
TISErrorComKlima3Code10 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[10] | BYTE
TISErrorComKlima3Code11 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[11] | BYTE
TISErrorComKlima3Code12 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[12] | BYTE
TISErrorComKlima3Code13 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[13] | BYTE
TISErrorComKlima3Code14 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[14] | BYTE
TISErrorComKlima3Code15 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[15] | BYTE
TISErrorComKlima3Code1 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[1] | BYTE
TISErrorComKlima3Code2 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[2] | BYTE
TISErrorComKlima3Code3 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[3] | BYTE
TISErrorComKlima3Code4 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[4] | BYTE
TISErrorComKlima3Code5 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[5] | BYTE
TISErrorComKlima3Code6 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[6] | BYTE
TISErrorComKlima3Code7 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[7] | BYTE
TISErrorComKlima3Code8 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[8] | BYTE
TISErrorComKlima3Code9 | INT | IOD_TIS | TIS:.ErrorComKlima[3].Code[9] | BYTE
TISErrorComKlima3Status | INT | IOD_TIS | TIS:.ErrorComKlima[3].Status
TISErrorComKlima4Code10 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[10] | BYTE
TISErrorComKlima4Code11 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[11] | BYTE
TISErrorComKlima4Code12 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[12] | BYTE
TISErrorComKlima4Code13 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[13] | BYTE
TISErrorComKlima4Code14 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[14] | BYTE
TISErrorComKlima4Code15 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[15] | BYTE
TISErrorComKlima4Code1 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[1] | BYTE
TISErrorComKlima4Code2 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[2] | BYTE
TISErrorComKlima4Code3 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[3] | BYTE
TISErrorComKlima4Code4 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[4] | BYTE
TISErrorComKlima4Code5 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[5] | BYTE
TISErrorComKlima4Code6 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[6] | BYTE
TISErrorComKlima4Code7 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[7] | BYTE
TISErrorComKlima4Code8 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[8] | BYTE
TISErrorComKlima4Code9 | INT | IOD_TIS | TIS:.ErrorComKlima[4].Code[9] | BYTE
TISErrorComKlima4Status | INT | IOD_TIS | TIS:.ErrorComKlima[4].Status
TISErrorComKlima5Code10 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[10] | BYTE
TISErrorComKlima5Code11 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[11] | BYTE
TISErrorComKlima5Code12 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[12] | BYTE
TISErrorComKlima5Code13 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[13] | BYTE
TISErrorComKlima5Code14 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[14] | BYTE
TISErrorComKlima5Code15 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[15] | BYTE
TISErrorComKlima5Code1 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[1] | BYTE
TISErrorComKlima5Code2 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[2] | BYTE
TISErrorComKlima5Code3 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[3] | BYTE
TISErrorComKlima5Code4 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[4] | BYTE
TISErrorComKlima5Code5 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[5] | BYTE
TISErrorComKlima5Code6 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[6] | BYTE
TISErrorComKlima5Code7 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[7] | BYTE
TISErrorComKlima5Code8 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[8] | BYTE
TISErrorComKlima5Code9 | INT | IOD_TIS | TIS:.ErrorComKlima[5].Code[9] | BYTE
TISErrorComKlima5Status | INT | IOD_TIS | TIS:.ErrorComKlima[5].Status
TISErrorComKlima6Code10 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[10] | BYTE
TISErrorComKlima6Code11 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[11] | BYTE
TISErrorComKlima6Code12 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[12] | BYTE
TISErrorComKlima6Code13 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[13] | BYTE
TISErrorComKlima6Code14 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[14] | BYTE
TISErrorComKlima6Code15 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[15] | BYTE
TISErrorComKlima6Code1 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[1] | BYTE
TISErrorComKlima6Code2 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[2] | BYTE
TISErrorComKlima6Code3 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[3] | BYTE
TISErrorComKlima6Code4 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[4] | BYTE
TISErrorComKlima6Code5 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[5] | BYTE
TISErrorComKlima6Code6 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[6] | BYTE
TISErrorComKlima6Code7 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[7] | BYTE
TISErrorComKlima6Code8 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[8] | BYTE
TISErrorComKlima6Code9 | INT | IOD_TIS | TIS:.ErrorComKlima[6].Code[9] | BYTE
TISErrorComKlima6Status | INT | IOD_TIS | TIS:.ErrorComKlima[6].Status
TISKlima1GrelecStatus | INT | IOD_TIS | TIS:.Klima[1].GrelecStatus | BYTE
TISKlima1IzhodniVentStatus | INT | IOD_TIS | TIS:.Klima[1].IzhodniVentStatus | BYTE
TISKlima1KompresorStatus | INT | IOD_TIS | TIS:.Klima[1].KompresorStatus | BYTE
TISKlima1VlazilecStatus | INT | IOD_TIS | TIS:.Klima[1].VlazilecStatus | BYTE
TISKlima2GrelecStatus | INT | IOD_TIS | TIS:.Klima[2].GrelecStatus | BYTE
TISKlima2IzhodniVentStatus | INT | IOD_TIS | TIS:.Klima[2].IzhodniVentStatus | BYTE
TISKlima2KompresorStatus | INT | IOD_TIS | TIS:.Klima[2].KompresorStatus | BYTE
TISKlima2VlazilecStatus | INT | IOD_TIS | TIS:.Klima[2].VlazilecStatus | BYTE
TISKlima3GrelecStatus | INT | IOD_TIS | TIS:.Klima[3].GrelecStatus | BYTE
TISKlima3IzhodniVentStatus | INT | IOD_TIS | TIS:.Klima[3].IzhodniVentStatus | BYTE
TISKlima3KompresorStatus | INT | IOD_TIS | TIS:.Klima[3].KompresorStatus | BYTE
TISKlima3VlazilecStatus | INT | IOD_TIS | TIS:.Klima[3].VlazilecStatus | BYTE
TISKlimaGalGrelecStatus | INT | IOD_TIS | TIS:.KlimaGal.GrelecStatus | BYTE
TISKlimaGalIzhodniVentStatus | INT | IOD_TIS | TIS:.KlimaGal.IzhodniVentStatus | BYTE
TISKlimaGalKompresorStatus | INT | IOD_TIS | TIS:.KlimaGal.KompresorStatus | BYTE
TISKlimaGalVlazilecStatus | INT | IOD_TIS | TIS:.KlimaGal.VlazilecStatus | BYTE
TISQstanje10 | INT | IOD_TIS | TIS:.Qstanje[10] | BYTE
TISQstanje1 | INT | IOD_TIS | TIS:.Qstanje[1] | BYTE
TISQstanje2 | INT | IOD_TIS | TIS:.Qstanje[2] | BYTE
TISQstanje3 | INT | IOD_TIS | TIS:.Qstanje[3] | BYTE
TISQstanje4 | INT | IOD_TIS | TIS:.Qstanje[4] | BYTE
TISQstanje5 | INT | IOD_TIS | TIS:.Qstanje[5] | BYTE
TISQstanje6 | INT | IOD_TIS | TIS:.Qstanje[6] | BYTE
TISQstanje7 | INT | IOD_TIS | TIS:.Qstanje[7] | BYTE
TISQstanje8 | INT | IOD_TIS | TIS:.Qstanje[8] | BYTE
TISQstanje9 | INT | IOD_TIS | TIS:.Qstanje[9] | BYTE
TISUserCurrentLevel | INT | IOD_TIS | TIS:.UserCurrentLevel | BYTE
TISXVH_CircNumber | INT | IOD_TIS | TIS:.XVH_CircNumber | BYTE
TISXVH_KlimaNumber | INT | IOD_TIS | TIS:.XVH_KlimaNumber | BYTE
TISXVH_PripravaVodeStat1 | INT | IOD_TIS | TIS:.XVH_PripravaVodeStat[1] | BYTE
TISXVH_PripravaVodeStat2 | INT | IOD_TIS | TIS:.XVH_PripravaVodeStat[2] | BYTE
TISXVH_UPSstatus | INT | IOD_TIS | TIS:.XVH_UPSstatus | BYTE
TISXVH_VlazilecStatus1 | INT | IOD_TIS | TIS:.XVH_VlazilecStatus[1] | BYTE
TISXVH_VlazilecStatus2 | INT | IOD_TIS | TIS:.XVH_VlazilecStatus[2] | BYTE
TISXVH_VlazilecStatus3 | INT | IOD_TIS | TIS:.XVH_VlazilecStatus[3] | BYTE
TISXVHnum10 | INT | IOD_TIS | TIS:.XVHnum[10] | BYTE
TISXVHnum11 | INT | IOD_TIS | TIS:.XVHnum[11] | BYTE
TISXVHnum12 | INT | IOD_TIS | TIS:.XVHnum[12] | BYTE
TISXVHnum13 | INT | IOD_TIS | TIS:.XVHnum[13] | BYTE
TISXVHnum14 | INT | IOD_TIS | TIS:.XVHnum[14] | BYTE
TISXVHnum1 | INT | IOD_TIS | TIS:.XVHnum[1] | BYTE
TISXVHnum2 | INT | IOD_TIS | TIS:.XVHnum[2] | BYTE
TISXVHnum3 | INT | IOD_TIS | TIS:.XVHnum[3] | BYTE
TISXVHnum4 | INT | IOD_TIS | TIS:.XVHnum[4] | BYTE
TISXVHnum5 | INT | IOD_TIS | TIS:.XVHnum[5] | BYTE
TISXVHnum6 | INT | IOD_TIS | TIS:.XVHnum[6] | BYTE
TISXVHnum7 | INT | IOD_TIS | TIS:.XVHnum[7] | BYTE
TISXVHnum8 | INT | IOD_TIS | TIS:.XVHnum[8] | BYTE
TISXVHnum9 | INT | IOD_TIS | TIS:.XVHnum[9] | BYTE
TISkom_nast_cas_izpada | INT | IOD_TIS | TIS:.kom_nast_cas_izpada
TISCirc1CosFi_III | REAL | IOD_TIS | TIS:.Circ[1].CosFi_III
TISCirc1DelovnaEnergija | REAL | IOD_TIS | TIS:.Circ[1].DelovnaEnergija
TISCirc1DelovnaMoc_III | REAL | IOD_TIS | TIS:.Circ[1].DelovnaMoc_III
TISCirc1DelovnaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[1].DelovnaMoc_L1
TISCirc1DelovnaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[1].DelovnaMoc_L2
TISCirc1DelovnaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[1].DelovnaMoc_L3
TISCirc1Frekvenca_L1 | REAL | IOD_TIS | TIS:.Circ[1].Frekvenca_L1
TISCirc1InduktivnaEnergija | REAL | IOD_TIS | TIS:.Circ[1].InduktivnaEnergija
TISCirc1InduktivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[1].InduktivnaMoc_III
TISCirc1JalovaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[1].JalovaMoc_L1
TISCirc1JalovaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[1].JalovaMoc_L2
TISCirc1JalovaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[1].JalovaMoc_L3
TISCirc1KapacitivnaEnergija | REAL | IOD_TIS | TIS:.Circ[1].KapacitivnaEnergija
TISCirc1KapacitivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[1].KapacitivnaMoc_III
TISCirc1MaximumDemand | REAL | IOD_TIS | TIS:.Circ[1].MaximumDemand
TISCirc1Napetost_L1_L2 | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L1_L2
TISCirc1Napetost_L1_N | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L1_N
TISCirc1Napetost_L2_L3 | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L2_L3
TISCirc1Napetost_L2_N | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L2_N
TISCirc1Napetost_L3_L1 | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L3_L1
TISCirc1Napetost_L3_N | REAL | IOD_TIS | TIS:.Circ[1].Napetost_L3_N
TISCirc1NavideznaMoc_III | REAL | IOD_TIS | TIS:.Circ[1].NavideznaMoc_III
TISCirc1NicelniTok | REAL | IOD_TIS | TIS:.Circ[1].NicelniTok
TISCirc1PowerFactor_III | REAL | IOD_TIS | TIS:.Circ[1].PowerFactor_III
TISCirc1PowerFactor_L1 | REAL | IOD_TIS | TIS:.Circ[1].PowerFactor_L1
TISCirc1PowerFactor_L2 | REAL | IOD_TIS | TIS:.Circ[1].PowerFactor_L2
TISCirc1PowerFactor_L3 | REAL | IOD_TIS | TIS:.Circ[1].PowerFactor_L3
TISCirc1THDI_L1 | REAL | IOD_TIS | TIS:.Circ[1].THDI_L1
TISCirc1THDI_L2 | REAL | IOD_TIS | TIS:.Circ[1].THDI_L2
TISCirc1THDI_L3 | REAL | IOD_TIS | TIS:.Circ[1].THDI_L3
TISCirc1THDV_L1 | REAL | IOD_TIS | TIS:.Circ[1].THDV_L1
TISCirc1THDV_L2 | REAL | IOD_TIS | TIS:.Circ[1].THDV_L2
TISCirc1THDV_L3 | REAL | IOD_TIS | TIS:.Circ[1].THDV_L3
TISCirc1Tok_L1 | REAL | IOD_TIS | TIS:.Circ[1].Tok_L1
TISCirc1Tok_L2 | REAL | IOD_TIS | TIS:.Circ[1].Tok_L2
TISCirc1Tok_L3 | REAL | IOD_TIS | TIS:.Circ[1].Tok_L3
TISCirc1TokPovprecje_III | REAL | IOD_TIS | TIS:.Circ[1].TokPovprecje_III
TISCirc2CosFi_III | REAL | IOD_TIS | TIS:.Circ[2].CosFi_III
TISCirc2DelovnaEnergija | REAL | IOD_TIS | TIS:.Circ[2].DelovnaEnergija
TISCirc2DelovnaMoc_III | REAL | IOD_TIS | TIS:.Circ[2].DelovnaMoc_III
TISCirc2DelovnaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[2].DelovnaMoc_L1
TISCirc2DelovnaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[2].DelovnaMoc_L2
TISCirc2DelovnaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[2].DelovnaMoc_L3
TISCirc2Frekvenca_L1 | REAL | IOD_TIS | TIS:.Circ[2].Frekvenca_L1
TISCirc2InduktivnaEnergija | REAL | IOD_TIS | TIS:.Circ[2].InduktivnaEnergija
TISCirc2InduktivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[2].InduktivnaMoc_III
TISCirc2JalovaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[2].JalovaMoc_L1
TISCirc2JalovaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[2].JalovaMoc_L2
TISCirc2JalovaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[2].JalovaMoc_L3
TISCirc2KapacitivnaEnergija | REAL | IOD_TIS | TIS:.Circ[2].KapacitivnaEnergija
TISCirc2KapacitivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[2].KapacitivnaMoc_III
TISCirc2MaximumDemand | REAL | IOD_TIS | TIS:.Circ[2].MaximumDemand
TISCirc2Napetost_L1_L2 | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L1_L2
TISCirc2Napetost_L1_N | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L1_N
TISCirc2Napetost_L2_L3 | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L2_L3
TISCirc2Napetost_L2_N | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L2_N
TISCirc2Napetost_L3_L1 | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L3_L1
TISCirc2Napetost_L3_N | REAL | IOD_TIS | TIS:.Circ[2].Napetost_L3_N
TISCirc2NavideznaMoc_III | REAL | IOD_TIS | TIS:.Circ[2].NavideznaMoc_III
TISCirc2NicelniTok | REAL | IOD_TIS | TIS:.Circ[2].NicelniTok
TISCirc2PowerFactor_III | REAL | IOD_TIS | TIS:.Circ[2].PowerFactor_III
TISCirc2PowerFactor_L1 | REAL | IOD_TIS | TIS:.Circ[2].PowerFactor_L1
TISCirc2PowerFactor_L2 | REAL | IOD_TIS | TIS:.Circ[2].PowerFactor_L2
TISCirc2PowerFactor_L3 | REAL | IOD_TIS | TIS:.Circ[2].PowerFactor_L3
TISCirc2THDI_L1 | REAL | IOD_TIS | TIS:.Circ[2].THDI_L1
TISCirc2THDI_L2 | REAL | IOD_TIS | TIS:.Circ[2].THDI_L2
TISCirc2THDI_L3 | REAL | IOD_TIS | TIS:.Circ[2].THDI_L3
TISCirc2THDV_L1 | REAL | IOD_TIS | TIS:.Circ[2].THDV_L1
TISCirc2THDV_L2 | REAL | IOD_TIS | TIS:.Circ[2].THDV_L2
TISCirc2THDV_L3 | REAL | IOD_TIS | TIS:.Circ[2].THDV_L3
TISCirc2Tok_L1 | REAL | IOD_TIS | TIS:.Circ[2].Tok_L1
TISCirc2Tok_L2 | REAL | IOD_TIS | TIS:.Circ[2].Tok_L2
TISCirc2Tok_L3 | REAL | IOD_TIS | TIS:.Circ[2].Tok_L3
TISCirc2TokPovprecje_III | REAL | IOD_TIS | TIS:.Circ[2].TokPovprecje_III
TISCirc3CosFi_III | REAL | IOD_TIS | TIS:.Circ[3].CosFi_III
TISCirc3DelovnaEnergija | REAL | IOD_TIS | TIS:.Circ[3].DelovnaEnergija
TISCirc3DelovnaMoc_III | REAL | IOD_TIS | TIS:.Circ[3].DelovnaMoc_III
TISCirc3DelovnaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[3].DelovnaMoc_L1
TISCirc3DelovnaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[3].DelovnaMoc_L2
TISCirc3DelovnaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[3].DelovnaMoc_L3
TISCirc3Frekvenca_L1 | REAL | IOD_TIS | TIS:.Circ[3].Frekvenca_L1
TISCirc3InduktivnaEnergija | REAL | IOD_TIS | TIS:.Circ[3].InduktivnaEnergija
TISCirc3InduktivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[3].InduktivnaMoc_III
TISCirc3JalovaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[3].JalovaMoc_L1
TISCirc3JalovaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[3].JalovaMoc_L2
TISCirc3JalovaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[3].JalovaMoc_L3
TISCirc3KapacitivnaEnergija | REAL | IOD_TIS | TIS:.Circ[3].KapacitivnaEnergija
TISCirc3KapacitivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[3].KapacitivnaMoc_III
TISCirc3MaximumDemand | REAL | IOD_TIS | TIS:.Circ[3].MaximumDemand
TISCirc3Napetost_L1_L2 | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L1_L2
TISCirc3Napetost_L1_N | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L1_N
TISCirc3Napetost_L2_L3 | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L2_L3
TISCirc3Napetost_L2_N | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L2_N
TISCirc3Napetost_L3_L1 | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L3_L1
TISCirc3Napetost_L3_N | REAL | IOD_TIS | TIS:.Circ[3].Napetost_L3_N
TISCirc3NavideznaMoc_III | REAL | IOD_TIS | TIS:.Circ[3].NavideznaMoc_III
TISCirc3NicelniTok | REAL | IOD_TIS | TIS:.Circ[3].NicelniTok
TISCirc3PowerFactor_III | REAL | IOD_TIS | TIS:.Circ[3].PowerFactor_III
TISCirc3PowerFactor_L1 | REAL | IOD_TIS | TIS:.Circ[3].PowerFactor_L1
TISCirc3PowerFactor_L2 | REAL | IOD_TIS | TIS:.Circ[3].PowerFactor_L2
TISCirc3PowerFactor_L3 | REAL | IOD_TIS | TIS:.Circ[3].PowerFactor_L3
TISCirc3THDI_L1 | REAL | IOD_TIS | TIS:.Circ[3].THDI_L1
TISCirc3THDI_L2 | REAL | IOD_TIS | TIS:.Circ[3].THDI_L2
TISCirc3THDI_L3 | REAL | IOD_TIS | TIS:.Circ[3].THDI_L3
TISCirc3THDV_L1 | REAL | IOD_TIS | TIS:.Circ[3].THDV_L1
TISCirc3THDV_L2 | REAL | IOD_TIS | TIS:.Circ[3].THDV_L2
TISCirc3THDV_L3 | REAL | IOD_TIS | TIS:.Circ[3].THDV_L3
TISCirc3Tok_L1 | REAL | IOD_TIS | TIS:.Circ[3].Tok_L1
TISCirc3Tok_L2 | REAL | IOD_TIS | TIS:.Circ[3].Tok_L2
TISCirc3Tok_L3 | REAL | IOD_TIS | TIS:.Circ[3].Tok_L3
TISCirc3TokPovprecje_III | REAL | IOD_TIS | TIS:.Circ[3].TokPovprecje_III
TISCirc4CosFi_III | REAL | IOD_TIS | TIS:.Circ[4].CosFi_III
TISCirc4DelovnaEnergija | REAL | IOD_TIS | TIS:.Circ[4].DelovnaEnergija
TISCirc4DelovnaMoc_III | REAL | IOD_TIS | TIS:.Circ[4].DelovnaMoc_III
TISCirc4DelovnaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[4].DelovnaMoc_L1
TISCirc4DelovnaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[4].DelovnaMoc_L2
TISCirc4DelovnaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[4].DelovnaMoc_L3
TISCirc4Frekvenca_L1 | REAL | IOD_TIS | TIS:.Circ[4].Frekvenca_L1
TISCirc4InduktivnaEnergija | REAL | IOD_TIS | TIS:.Circ[4].InduktivnaEnergija
TISCirc4InduktivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[4].InduktivnaMoc_III
TISCirc4JalovaMoc_L1 | REAL | IOD_TIS | TIS:.Circ[4].JalovaMoc_L1
TISCirc4JalovaMoc_L2 | REAL | IOD_TIS | TIS:.Circ[4].JalovaMoc_L2
TISCirc4JalovaMoc_L3 | REAL | IOD_TIS | TIS:.Circ[4].JalovaMoc_L3
TISCirc4KapacitivnaEnergija | REAL | IOD_TIS | TIS:.Circ[4].KapacitivnaEnergija
TISCirc4KapacitivnaMoc_III | REAL | IOD_TIS | TIS:.Circ[4].KapacitivnaMoc_III
TISCirc4MaximumDemand | REAL | IOD_TIS | TIS:.Circ[4].MaximumDemand
TISCirc4Napetost_L1_L2 | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L1_L2
TISCirc4Napetost_L1_N | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L1_N
TISCirc4Napetost_L2_L3 | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L2_L3
TISCirc4Napetost_L2_N | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L2_N
TISCirc4Napetost_L3_L1 | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L3_L1
TISCirc4Napetost_L3_N | REAL | IOD_TIS | TIS:.Circ[4].Napetost_L3_N
TISCirc4NavideznaMoc_III | REAL | IOD_TIS | TIS:.Circ[4].NavideznaMoc_III
TISCirc4NicelniTok | REAL | IOD_TIS | TIS:.Circ[4].NicelniTok
TISCirc4PowerFactor_III | REAL | IOD_TIS | TIS:.Circ[4].PowerFactor_III
TISCirc4PowerFactor_L1 | REAL | IOD_TIS | TIS:.Circ[4].PowerFactor_L1
TISCirc4PowerFactor_L2 | REAL | IOD_TIS | TIS:.Circ[4].PowerFactor_L2
TISCirc4PowerFactor_L3 | REAL | IOD_TIS | TIS:.Circ[4].PowerFactor_L3
TISCirc4THDI_L1 | REAL | IOD_TIS | TIS:.Circ[4].THDI_L1
TISCirc4THDI_L2 | REAL | IOD_TIS | TIS:.Circ[4].THDI_L2
TISCirc4THDI_L3 | REAL | IOD_TIS | TIS:.Circ[4].THDI_L3
TISCirc4THDV_L1 | REAL | IOD_TIS | TIS:.Circ[4].THDV_L1
TISCirc4THDV_L2 | REAL | IOD_TIS | TIS:.Circ[4].THDV_L2
TISCirc4THDV_L3 | REAL | IOD_TIS | TIS:.Circ[4].THDV_L3
TISCirc4Tok_L1 | REAL | IOD_TIS | TIS:.Circ[4].Tok_L1
TISCirc4Tok_L2 | REAL | IOD_TIS | TIS:.Circ[4].Tok_L2
TISCirc4Tok_L3 | REAL | IOD_TIS | TIS:.Circ[4].Tok_L3
TISCirc4TokPovprecje_III | REAL | IOD_TIS | TIS:.Circ[4].TokPovprecje_III
TISCircutorCosFi_III | REAL | IOD_TIS | TIS:.Circutor.CosFi_III
TISCircutorDelovnaEnergija | REAL | IOD_TIS | TIS:.Circutor.DelovnaEnergija
TISCircutorDelovnaMoc_III | REAL | IOD_TIS | TIS:.Circutor.DelovnaMoc_III
TISCircutorDelovnaMoc_L1 | REAL | IOD_TIS | TIS:.Circutor.DelovnaMoc_L1
TISCircutorDelovnaMoc_L2 | REAL | IOD_TIS | TIS:.Circutor.DelovnaMoc_L2
TISCircutorDelovnaMoc_L3 | REAL | IOD_TIS | TIS:.Circutor.DelovnaMoc_L3
TISCircutorFrekvenca_L1 | REAL | IOD_TIS | TIS:.Circutor.Frekvenca_L1
TISCircutorInduktivnaEnergija | REAL | IOD_TIS | TIS:.Circutor.InduktivnaEnergija
TISCircutorInduktivnaMoc_III | REAL | IOD_TIS | TIS:.Circutor.InduktivnaMoc_III
TISCircutorJalovaMoc_L1 | REAL | IOD_TIS | TIS:.Circutor.JalovaMoc_L1
TISCircutorJalovaMoc_L2 | REAL | IOD_TIS | TIS:.Circutor.JalovaMoc_L2
TISCircutorJalovaMoc_L3 | REAL | IOD_TIS | TIS:.Circutor.JalovaMoc_L3
TISCircutorKapacitivnaEnergija | REAL | IOD_TIS | TIS:.Circutor.KapacitivnaEnergija
TISCircutorKapacitivnaMoc_III | REAL | IOD_TIS | TIS:.Circutor.KapacitivnaMoc_III
TISCircutorMaximumDemand | REAL | IOD_TIS | TIS:.Circutor.MaximumDemand
TISCircutorNapetost_L1_L2 | REAL | IOD_TIS | TIS:.Circutor.Napetost_L1_L2
TISCircutorNapetost_L1_N | REAL | IOD_TIS | TIS:.Circutor.Napetost_L1_N
TISCircutorNapetost_L2_L3 | REAL | IOD_TIS | TIS:.Circutor.Napetost_L2_L3
TISCircutorNapetost_L2_N | REAL | IOD_TIS | TIS:.Circutor.Napetost_L2_N
TISCircutorNapetost_L3_L1 | REAL | IOD_TIS | TIS:.Circutor.Napetost_L3_L1
TISCircutorNapetost_L3_N | REAL | IOD_TIS | TIS:.Circutor.Napetost_L3_N
TISCircutorNavideznaMoc_III | REAL | IOD_TIS | TIS:.Circutor.NavideznaMoc_III
TISCircutorNicelniTok | REAL | IOD_TIS | TIS:.Circutor.NicelniTok
TISCircutorPowerFactor_III | REAL | IOD_TIS | TIS:.Circutor.PowerFactor_III
TISCircutorPowerFactor_L1 | REAL | IOD_TIS | TIS:.Circutor.PowerFactor_L1
TISCircutorPowerFactor_L2 | REAL | IOD_TIS | TIS:.Circutor.PowerFactor_L2
TISCircutorPowerFactor_L3 | REAL | IOD_TIS | TIS:.Circutor.PowerFactor_L3
TISCircutorTHDI_L1 | REAL | IOD_TIS | TIS:.Circutor.THDI_L1
TISCircutorTHDI_L2 | REAL | IOD_TIS | TIS:.Circutor.THDI_L2
TISCircutorTHDI_L3 | REAL | IOD_TIS | TIS:.Circutor.THDI_L3
TISCircutorTHDV_L1 | REAL | IOD_TIS | TIS:.Circutor.THDV_L1
TISCircutorTHDV_L2 | REAL | IOD_TIS | TIS:.Circutor.THDV_L2
TISCircutorTHDV_L3 | REAL | IOD_TIS | TIS:.Circutor.THDV_L3
TISCircutorTok_L1 | REAL | IOD_TIS | TIS:.Circutor.Tok_L1
TISCircutorTok_L2 | REAL | IOD_TIS | TIS:.Circutor.Tok_L2
TISCircutorTok_L3 | REAL | IOD_TIS | TIS:.Circutor.Tok_L3
TISCircutorTokPovprecje_III | REAL | IOD_TIS | TIS:.Circutor.TokPovprecje_III
TISKlima1NastMaxTemp | REAL | IOD_TIS | TIS:.Klima[1].NastMaxTemp
TISKlima1NastMaxVlaznost | REAL | IOD_TIS | TIS:.Klima[1].NastMaxVlaznost
TISKlima1NastMinTemp | REAL | IOD_TIS | TIS:.Klima[1].NastMinTemp
TISKlima1NastMinVlaznost | REAL | IOD_TIS | TIS:.Klima[1].NastMinVlaznost
TISKlima1NastTempProstora | REAL | IOD_TIS | TIS:.Klima[1].NastTempProstora
TISKlima1NastVlaznost | REAL | IOD_TIS | TIS:.Klima[1].NastVlaznost
TISKlima1ObratovalneUre | REAL | IOD_TIS | TIS:.Klima[1].ObratovalneUre
TISKlima1TemperaturaProstora | REAL | IOD_TIS | TIS:.Klima[1].TemperaturaProstora
TISKlima1TempIzpihanegaZraka | REAL | IOD_TIS | TIS:.Klima[1].TempIzpihanegaZraka
TISKlima1TempPovratneVode | REAL | IOD_TIS | TIS:.Klima[1].TempPovratneVode
TISKlima1VlaznostProstora | REAL | IOD_TIS | TIS:.Klima[1].VlaznostProstora
TISKlima1ZunanjaTemp | REAL | IOD_TIS | TIS:.Klima[1].ZunanjaTemp
TISKlima2NastMaxTemp | REAL | IOD_TIS | TIS:.Klima[2].NastMaxTemp
TISKlima2NastMaxVlaznost | REAL | IOD_TIS | TIS:.Klima[2].NastMaxVlaznost
TISKlima2NastMinTemp | REAL | IOD_TIS | TIS:.Klima[2].NastMinTemp
TISKlima2NastMinVlaznost | REAL | IOD_TIS | TIS:.Klima[2].NastMinVlaznost
TISKlima2NastTempProstora | REAL | IOD_TIS | TIS:.Klima[2].NastTempProstora
TISKlima2NastVlaznost | REAL | IOD_TIS | TIS:.Klima[2].NastVlaznost
TISKlima2ObratovalneUre | REAL | IOD_TIS | TIS:.Klima[2].ObratovalneUre
TISKlima2TemperaturaProstora | REAL | IOD_TIS | TIS:.Klima[2].TemperaturaProstora
TISKlima2TempIzpihanegaZraka | REAL | IOD_TIS | TIS:.Klima[2].TempIzpihanegaZraka
TISKlima2TempPovratneVode | REAL | IOD_TIS | TIS:.Klima[2].TempPovratneVode
TISKlima2VlaznostProstora | REAL | IOD_TIS | TIS:.Klima[2].VlaznostProstora
TISKlima2ZunanjaTemp | REAL | IOD_TIS | TIS:.Klima[2].ZunanjaTemp
TISKlima3NastMaxTemp | REAL | IOD_TIS | TIS:.Klima[3].NastMaxTemp
TISKlima3NastMaxVlaznost | REAL | IOD_TIS | TIS:.Klima[3].NastMaxVlaznost
TISKlima3NastMinTemp | REAL | IOD_TIS | TIS:.Klima[3].NastMinTemp
TISKlima3NastMinVlaznost | REAL | IOD_TIS | TIS:.Klima[3].NastMinVlaznost
TISKlima3NastTempProstora | REAL | IOD_TIS | TIS:.Klima[3].NastTempProstora
TISKlima3NastVlaznost | REAL | IOD_TIS | TIS:.Klima[3].NastVlaznost
TISKlima3ObratovalneUre | REAL | IOD_TIS | TIS:.Klima[3].ObratovalneUre
TISKlima3TemperaturaProstora | REAL | IOD_TIS | TIS:.Klima[3].TemperaturaProstora
TISKlima3TempIzpihanegaZraka | REAL | IOD_TIS | TIS:.Klima[3].TempIzpihanegaZraka
TISKlima3TempPovratneVode | REAL | IOD_TIS | TIS:.Klima[3].TempPovratneVode
TISKlima3VlaznostProstora | REAL | IOD_TIS | TIS:.Klima[3].VlaznostProstora
TISKlima3ZunanjaTemp | REAL | IOD_TIS | TIS:.Klima[3].ZunanjaTemp
TISKlimaGalNastMaxTemp | REAL | IOD_TIS | TIS:.KlimaGal.NastMaxTemp
TISKlimaGalNastMaxVlaznost | REAL | IOD_TIS | TIS:.KlimaGal.NastMaxVlaznost
TISKlimaGalNastMinTemp | REAL | IOD_TIS | TIS:.KlimaGal.NastMinTemp
TISKlimaGalNastMinVlaznost | REAL | IOD_TIS | TIS:.KlimaGal.NastMinVlaznost
TISKlimaGalNastTempProstora | REAL | IOD_TIS | TIS:.KlimaGal.NastTempProstora
TISKlimaGalNastVlaznost | REAL | IOD_TIS | TIS:.KlimaGal.NastVlaznost
TISKlimaGalObratovalneUre | REAL | IOD_TIS | TIS:.KlimaGal.ObratovalneUre
TISKlimaGalTemperaturaProstora | REAL | IOD_TIS | TIS:.KlimaGal.TemperaturaProstora
TISKlimaGalTempIzpihanegaZraka | REAL | IOD_TIS | TIS:.KlimaGal.TempIzpihanegaZraka
TISKlimaGalTempPovratneVode | REAL | IOD_TIS | TIS:.KlimaGal.TempPovratneVode
TISKlimaGalVlaznostProstora | REAL | IOD_TIS | TIS:.KlimaGal.VlaznostProstora
TISKlimaGalZunanjaTemp | REAL | IOD_TIS | TIS:.KlimaGal.ZunanjaTemp
TISSenzorTemp10 | REAL | IOD_TIS | TIS:.SenzorTemp[10]
TISSenzorTemp11 | REAL | IOD_TIS | TIS:.SenzorTemp[11]
TISSenzorTemp12 | REAL | IOD_TIS | TIS:.SenzorTemp[12]
TISSenzorTemp13 | REAL | IOD_TIS | TIS:.SenzorTemp[13]
TISSenzorTemp14 | REAL | IOD_TIS | TIS:.SenzorTemp[14]
TISSenzorTemp15 | REAL | IOD_TIS | TIS:.SenzorTemp[15]
TISSenzorTemp16 | REAL | IOD_TIS | TIS:.SenzorTemp[16]
TISSenzorTemp17 | REAL | IOD_TIS | TIS:.SenzorTemp[17]
TISSenzorTemp18 | REAL | IOD_TIS | TIS:.SenzorTemp[18]
TISSenzorTemp19 | REAL | IOD_TIS | TIS:.SenzorTemp[19]
TISSenzorTemp1 | REAL | IOD_TIS | TIS:.SenzorTemp[1]
TISSenzorTemp2 | REAL | IOD_TIS | TIS:.SenzorTemp[2]
TISSenzorTemp3 | REAL | IOD_TIS | TIS:.SenzorTemp[3]
TISSenzorTemp4 | REAL | IOD_TIS | TIS:.SenzorTemp[4]
TISSenzorTemp5 | REAL | IOD_TIS | TIS:.SenzorTemp[5]
TISSenzorTemp6 | REAL | IOD_TIS | TIS:.SenzorTemp[6]
TISSenzorTemp7 | REAL | IOD_TIS | TIS:.SenzorTemp[7]
TISSenzorTemp8 | REAL | IOD_TIS | TIS:.SenzorTemp[8]
TISSenzorTemp9 | REAL | IOD_TIS | TIS:.SenzorTemp[9]
TISSenzorVlaga10 | REAL | IOD_TIS | TIS:.SenzorVlaga[10]
TISSenzorVlaga11 | REAL | IOD_TIS | TIS:.SenzorVlaga[11]
TISSenzorVlaga12 | REAL | IOD_TIS | TIS:.SenzorVlaga[12]
TISSenzorVlaga13 | REAL | IOD_TIS | TIS:.SenzorVlaga[13]
TISSenzorVlaga14 | REAL | IOD_TIS | TIS:.SenzorVlaga[14]
TISSenzorVlaga15 | REAL | IOD_TIS | TIS:.SenzorVlaga[15]
TISSenzorVlaga16 | REAL | IOD_TIS | TIS:.SenzorVlaga[16]
TISSenzorVlaga17 | REAL | IOD_TIS | TIS:.SenzorVlaga[17]
TISSenzorVlaga18 | REAL | IOD_TIS | TIS:.SenzorVlaga[18]
TISSenzorVlaga19 | REAL | IOD_TIS | TIS:.SenzorVlaga[19]
TISSenzorVlaga1 | REAL | IOD_TIS | TIS:.SenzorVlaga[1]
TISSenzorVlaga2 | REAL | IOD_TIS | TIS:.SenzorVlaga[2]
TISSenzorVlaga3 | REAL | IOD_TIS | TIS:.SenzorVlaga[3]
TISSenzorVlaga4 | REAL | IOD_TIS | TIS:.SenzorVlaga[4]
TISSenzorVlaga5 | REAL | IOD_TIS | TIS:.SenzorVlaga[5]
TISSenzorVlaga6 | REAL | IOD_TIS | TIS:.SenzorVlaga[6]
TISSenzorVlaga7 | REAL | IOD_TIS | TIS:.SenzorVlaga[7]
TISSenzorVlaga8 | REAL | IOD_TIS | TIS:.SenzorVlaga[8]
TISSenzorVlaga9 | REAL | IOD_TIS | TIS:.SenzorVlaga[9]
TISTempAlarmPoint1 | REAL | IOD_TIS | TIS:.TempAlarmPoint[1]
TISTempAlarmPoint2 | REAL | IOD_TIS | TIS:.TempAlarmPoint[2]
TISTempAlarmPoint3 | REAL | IOD_TIS | TIS:.TempAlarmPoint[3]
TISTempMaxPoint1 | REAL | IOD_TIS | TIS:.TempMaxPoint[1]
TISTempMaxPoint2 | REAL | IOD_TIS | TIS:.TempMaxPoint[2]
TISTempMaxPoint3 | REAL | IOD_TIS | TIS:.TempMaxPoint[3]
TISTempPovp1 | REAL | IOD_TIS | TIS:.TempPovp[1]
TISTempPovp2 | REAL | IOD_TIS | TIS:.TempPovp[2]
TISTempPovp3 | REAL | IOD_TIS | TIS:.TempPovp[3]
TISTempPovp4 | REAL | IOD_TIS | TIS:.TempPovp[4]
TISTempPovp5 | REAL | IOD_TIS | TIS:.TempPovp[5]
TISTempSetPoint1 | REAL | IOD_TIS | TIS:.TempSetPoint[1]
TISTempSetPoint2 | REAL | IOD_TIS | TIS:.TempSetPoint[2]
TISTempSetPoint3 | REAL | IOD_TIS | TIS:.TempSetPoint[3]
TISVlagaPovp1 | REAL | IOD_TIS | TIS:.VlagaPovp[1]
TISVlagaPovp2 | REAL | IOD_TIS | TIS:.VlagaPovp[2]
TISVlagaPovp3 | REAL | IOD_TIS | TIS:.VlagaPovp[3]
TISVlagaPovp4 | REAL | IOD_TIS | TIS:.VlagaPovp[4]
TISVlagaPovp5 | REAL | IOD_TIS | TIS:.VlagaPovp[5]
TISXVH_GrafTemp1 | REAL | IOD_TIS | TIS:.XVH_GrafTemp[1]
TISXVH_GrafTemp2 | REAL | IOD_TIS | TIS:.XVH_GrafTemp[2]
TISXVH_GrafTemp3 | REAL | IOD_TIS | TIS:.XVH_GrafTemp[3]
TISXVH_GrafTemp4 | REAL | IOD_TIS | TIS:.XVH_GrafTemp[4]
TISXVH_GrafTemp5 | REAL | IOD_TIS | TIS:.XVH_GrafTemp[5]
TISXVH_GrafVlaga1 | REAL | IOD_TIS | TIS:.XVH_GrafVlaga[1]
TISXVH_GrafVlaga2 | REAL | IOD_TIS | TIS:.XVH_GrafVlaga[2]
TISXVH_GrafVlaga3 | REAL | IOD_TIS | TIS:.XVH_GrafVlaga[3]
TISXVH_GrafVlaga4 | REAL | IOD_TIS | TIS:.XVH_GrafVlaga[4]
TISXVH_GrafVlaga5 | REAL | IOD_TIS | TIS:.XVH_GrafVlaga[5]
TISXVH_NastTempProstora1 | REAL | IOD_TIS | TIS:.XVH_NastTempProstora[1]
TISXVH_NastTempProstora2 | REAL | IOD_TIS | TIS:.XVH_NastTempProstora[2]
TISXVH_NastTempProstora3 | REAL | IOD_TIS | TIS:.XVH_NastTempProstora[3]
TISXVH_ObratovalneUre1 | REAL | IOD_TIS | TIS:.XVH_ObratovalneUre[1]
TISXVH_ObratovalneUre2 | REAL | IOD_TIS | TIS:.XVH_ObratovalneUre[2]
TISXVH_ObratovalneUre3 | REAL | IOD_TIS | TIS:.XVH_ObratovalneUre[3]
TISXVHhighHum | REAL | IOD_TIS | TIS:.XVHhighHum
TISXVHhighTemp | REAL | IOD_TIS | TIS:.XVHhighTemp
TISXVHlowHum | REAL | IOD_TIS | TIS:.XVHlowHum
TISXVHlowTemp | REAL | IOD_TIS | TIS:.XVHlowTemp
TISCirc1MaximumDemandA2 | REAL | IOD_TIS | TIS:.Circ[1].MaximumDemandA2
TISCirc1MaximumDemandA3 | REAL | IOD_TIS | TIS:.Circ[1].MaximumDemandA3
TISCirc2MaximumDemandA2 | REAL | IOD_TIS | TIS:.Circ[2].MaximumDemandA2
TISCirc2MaximumDemandA3 | REAL | IOD_TIS | TIS:.Circ[2].MaximumDemandA3
TISCirc3MaximumDemandA2 | REAL | IOD_TIS | TIS:.Circ[3].MaximumDemandA2
TISCirc3MaximumDemandA3 | REAL | IOD_TIS | TIS:.Circ[3].MaximumDemandA3
TISCirc4MaximumDemandA2 | REAL | IOD_TIS | TIS:.Circ[4].MaximumDemandA2
TISCirc4MaximumDemandA3 | REAL | IOD_TIS | TIS:.Circ[4].MaximumDemandA3
TISCirc1RazEner_D_SCADA | REAL | IOD_TIS | TIS:.Circ[1].RazEner_D_SCADA
TISCirc1RazEner_T_SCADA | REAL | IOD_TIS | TIS:.Circ[1].RazEner_T_SCADA
TISCirc1RazEner_M_SCADA | REAL | IOD_TIS | TIS:.Circ[1].RazEner_M_SCADA
TISCirc2RazEner_D_SCADA | REAL | IOD_TIS | TIS:.Circ[2].RazEner_D_SCADA
TISCirc2RazEner_T_SCADA | REAL | IOD_TIS | TIS:.Circ[2].RazEner_T_SCADA
TISCirc2RazEner_M_SCADA | REAL | IOD_TIS | TIS:.Circ[2].RazEner_M_SCADA
TISCirc3RazEner_D_SCADA | REAL | IOD_TIS | TIS:.Circ[3].RazEner_D_SCADA
TISCirc3RazEner_T_SCADA | REAL | IOD_TIS | TIS:.Circ[3].RazEner_T_SCADA
TISCirc3RazEner_M_SCADA | REAL | IOD_TIS | TIS:.Circ[3].RazEner_M_SCADA
TISCirc4RazEner_D_SCADA | REAL | IOD_TIS | TIS:.Circ[4].RazEner_D_SCADA
TISCirc4RazEner_T_SCADA | REAL | IOD_TIS | TIS:.Circ[4].RazEner_T_SCADA
TISCirc4RazEner_M_SCADA | REAL | IOD_TIS | TIS:.Circ[4].RazEner_M_SCADA
TISDate_Time0 | STRING | IOD_TIS | TIS:.Date_Time[0]
TISDate_Time1 | STRING | IOD_TIS | TIS:.Date_Time[1]
TISDate_Time2 | STRING | IOD_TIS | TIS:.Date_Time[2]
TISDate_Time3 | STRING | IOD_TIS | TIS:.Date_Time[3]
TISUserCurrentName | STRING | IOD_TIS | TIS:.UserCurrentName

## variable_3
TISAlarmGenCirc1 | DIGITAL | IOD_TIS_TCP | 1 | 00001 | AlarmGenCirc1
TISAlarmGenCirc2 | DIGITAL | IOD_TIS_TCP | 2 | 00002 | AlarmGenCirc2
TISAlarmGenCirc3 | DIGITAL | IOD_TIS_TCP | 3 | 00003 | AlarmGenCirc3
TISAlarmGenCirc4 | DIGITAL | IOD_TIS_TCP | 4 | 00004 | AlarmGenCirc4
TISAlarmGenComm | DIGITAL | IOD_TIS_TCP | 5 | 00005 | AlarmGenComm
TISAlarmGenDI | DIGITAL | IOD_TIS_TCP | 6 | 00006 | AlarmGenDI
TISAlarmGenKlima1 | DIGITAL | IOD_TIS_TCP | 7 | 00007 | AlarmGenKlima1
TISAlarmGenKlima2 | DIGITAL | IOD_TIS_TCP | 8 | 00008 | AlarmGenKlima2
TISAlarmGenKlima3 | DIGITAL | IOD_TIS_TCP | 9 | 00009 | AlarmGenKlima3
TISAlarmGenRest | DIGITAL | IOD_TIS_TCP | 10 | 00010 | AlarmGenRest
TISAlarmGenSenzor | DIGITAL | IOD_TIS_TCP | 11 | 00011 | AlarmGenSenzor
TISAlarmGenTemp | DIGITAL | IOD_TIS_TCP | 12 | 00012 | AlarmGenTemp
TISAlarmGenVlPr | DIGITAL | IOD_TIS_TCP | 13 | 00013 | AlarmGenVlPr
TISAlarmGenVTV | DIGITAL | IOD_TIS_TCP | 14 | 00014 | AlarmGenVTV
TISComSCADA | DIGITAL | IOD_TIS_TCP | 15 | 00015 | ComSCADA
TISComSCADA1 | DIGITAL | IOD_TIS_TCP | 16 | 00016 | ComSCADA1
TISDI_F1_OdklHlOm1_IZP | DIGITAL | IOD_TIS_TCP | 17 | 00017 | DI_F1_OdklHlOm1_IZP
TISDI_F1_OdklHlOm1_ON | DIGITAL | IOD_TIS_TCP | 18 | 00018 | DI_F1_OdklHlOm1_ON
TISDI_F2_OdklHlOm2_IZP | DIGITAL | IOD_TIS_TCP | 19 | 00019 | DI_F2_OdklHlOm2_IZP
TISDI_F2_OdklHlOm2_ON | DIGITAL | IOD_TIS_TCP | 20 | 00020 | DI_F2_OdklHlOm2_ON
TISDI_F3_OdklHlOm3_IZP | DIGITAL | IOD_TIS_TCP | 21 | 00021 | DI_F3_OdklHlOm3_IZP
TISDI_F3_OdklHlOm3_ON | DIGITAL | IOD_TIS_TCP | 22 | 00022 | DI_F3_OdklHlOm3_ON
TISDI_F4_OdkPripVode_IZP | DIGITAL | IOD_TIS_TCP | 23 | 00023 | DI_F4_OdkPripVode_IZP
TISDI_F4_OdkPripVode_ON | DIGITAL | IOD_TIS_TCP | 24 | 00024 | DI_F4_OdkPripVode_ON
TISDI_HladOmara1_ERR | DIGITAL | IOD_TIS_TCP | 25 | 00025 | DI_HladOmara1_ERR
TISDI_HladOmara1_ON | DIGITAL | IOD_TIS_TCP | 26 | 00026 | DI_HladOmara1_ON
TISDI_HladOmara2_ERR | DIGITAL | IOD_TIS_TCP | 27 | 00027 | DI_HladOmara2_ERR
TISDI_HladOmara2_ON | DIGITAL | IOD_TIS_TCP | 28 | 00028 | DI_HladOmara2_ON
TISDI_HladOmara3_ERR | DIGITAL | IOD_TIS_TCP | 29 | 00029 | DI_HladOmara3_ERR
TISDI_HladOmara3_ON | DIGITAL | IOD_TIS_TCP | 30 | 00030 | DI_HladOmara3_ON
TISDI_PripVode1_ERR | DIGITAL | IOD_TIS_TCP | 31 | 00031 | DI_PripVode1_ERR
TISDI_PripVode1_ON | DIGITAL | IOD_TIS_TCP | 32 | 00032 | DI_PripVode1_ON
TISDI_PripVode2_ERR | DIGITAL | IOD_TIS_TCP | 33 | 00033 | DI_PripVode2_ERR
TISDI_PripVode2_ON | DIGITAL | IOD_TIS_TCP | 34 | 00034 | DI_PripVode2_ON
TISDI_Q0_DEG3_ON | DIGITAL | IOD_TIS_TCP | 35 | 00035 | DI_Q0_DEG3_ON
TISDI_Q0_EG3_ON | DIGITAL | IOD_TIS_TCP | 36 | 00036 | DI_Q0_EG3_ON
TISDI_Q0_GlavnoStikalo_ON | DIGITAL | IOD_TIS_TCP | 37 | 00037 | DI_Q0_GlavnoStikalo_ON
TISDI_Q0_UPS3_ON | DIGITAL | IOD_TIS_TCP | 38 | 00038 | DI_Q0_UPS3_ON
TISDI_RazlitjeVodeHO1 | DIGITAL | IOD_TIS_TCP | 39 | 00039 | DI_RazlitjeVodeHO1
TISDI_RazlitjeVodeHO2 | DIGITAL | IOD_TIS_TCP | 40 | 00040 | DI_RazlitjeVodeHO2
TISDI_RazlitjeVodeHO3 | DIGITAL | IOD_TIS_TCP | 41 | 00041 | DI_RazlitjeVodeHO3
TISDI_UPS_Alarm | DIGITAL | IOD_TIS_TCP | 42 | 00042 | DI_UPS_Alarm
TISDI_UPS_BatNacin | DIGITAL | IOD_TIS_TCP | 43 | 00043 | DI_UPS_BatNacin
TISDI_UPS_Polnjenje | DIGITAL | IOD_TIS_TCP | 44 | 00044 | DI_UPS_Polnjenje
TISDI_Vlazilec1_ERR | DIGITAL | IOD_TIS_TCP | 45 | 00045 | DI_Vlazilec1_ERR
TISDI_Vlazilec1_ON | DIGITAL | IOD_TIS_TCP | 46 | 00046 | DI_Vlazilec1_ON
TISDI_Vlazilec2_ERR | DIGITAL | IOD_TIS_TCP | 47 | 00047 | DI_Vlazilec2_ERR
TISDI_Vlazilec2_ON | DIGITAL | IOD_TIS_TCP | 48 | 00048 | DI_Vlazilec2_ON
TISDI_Vlazilec3_ERR | DIGITAL | IOD_TIS_TCP | 49 | 00049 | DI_Vlazilec3_ERR
TISDI_Vlazilec3_ON | DIGITAL | IOD_TIS_TCP | 50 | 00050 | DI_Vlazilec3_ON
TISDIN_F1_OdklHlOm1_IZP | DIGITAL | IOD_TIS_TCP | 51 | 00051 | DIN_F1_OdklHlOm1_IZP
TISDIN_F2_OdklHlOm2_IZP | DIGITAL | IOD_TIS_TCP | 52 | 00052 | DIN_F2_OdklHlOm2_IZP
TISDIN_F3_OdklHlOm3_IZP | DIGITAL | IOD_TIS_TCP | 53 | 00053 | DIN_F3_OdklHlOm3_IZP
TISDIN_F4_OdkPripVode_IZP | DIGITAL | IOD_TIS_TCP | 54 | 00054 | DIN_F4_OdkPripVode_IZP
TISDIN_HladOmara1_ERR | DIGITAL | IOD_TIS_TCP | 55 | 00055 | DIN_HladOmara1_ERR
TISDIN_HladOmara2_ERR | DIGITAL | IOD_TIS_TCP | 56 | 00056 | DIN_HladOmara2_ERR
TISDIN_HladOmara3_ERR | DIGITAL | IOD_TIS_TCP | 57 | 00057 | DIN_HladOmara3_ERR
TISDIN_PripVode1_ERR | DIGITAL | IOD_TIS_TCP | 58 | 00058 | DIN_PripVode1_ERR
TISDIN_PripVode2_ERR | DIGITAL | IOD_TIS_TCP | 59 | 00059 | DIN_PripVode2_ERR
TISDIN_Vlazilec1_ERR | DIGITAL | IOD_TIS_TCP | 60 | 00060 | DIN_Vlazilec1_ERR
TISDIN_Vlazilec2_ERR | DIGITAL | IOD_TIS_TCP | 61 | 00061 | DIN_Vlazilec2_ERR
TISDIN_Vlazilec3_ERR | DIGITAL | IOD_TIS_TCP | 62 | 00062 | DIN_Vlazilec3_ERR
TISDO_HladOm1_Izklop | DIGITAL | IOD_TIS_TCP | 63 | 00063 | DO_HladOm1_Izklop
TISDO_HladOm2_Izklop | DIGITAL | IOD_TIS_TCP | 64 | 00064 | DO_HladOm2_Izklop
TISDO_HladOm3_Izklop | DIGITAL | IOD_TIS_TCP | 65 | 00065 | DO_HladOm3_Izklop
TISErrComCirc1 | DIGITAL | IOD_TIS_TCP | 66 | 00066 | ErrComCirc[1]
TISErrComCirc2 | DIGITAL | IOD_TIS_TCP | 67 | 00067 | ErrComCirc[2]
TISErrComCirc3 | DIGITAL | IOD_TIS_TCP | 68 | 00068 | ErrComCirc[3]
TISErrComCirc4 | DIGITAL | IOD_TIS_TCP | 69 | 00069 | ErrComCirc[4]
TISErrComCirc5 | DIGITAL | IOD_TIS_TCP | 70 | 00070 | ErrComCirc[5]
TISErrComKlima1 | DIGITAL | IOD_TIS_TCP | 71 | 00071 | ErrComKlima[1]
TISErrComKlima2 | DIGITAL | IOD_TIS_TCP | 72 | 00072 | ErrComKlima[2]
TISErrComKlima3 | DIGITAL | IOD_TIS_TCP | 73 | 00073 | ErrComKlima[3]
TISErrComKlima4 | DIGITAL | IOD_TIS_TCP | 74 | 00074 | ErrComKlima[4]
TISErrComKlima5 | DIGITAL | IOD_TIS_TCP | 75 | 00075 | ErrComKlima[5]
TISErrComKlima6 | DIGITAL | IOD_TIS_TCP | 76 | 00076 | ErrComKlima[6]
TISErrCommScada | DIGITAL | IOD_TIS_TCP | 77 | 00077 | ErrCommScada
TISErrComPanelPLC | DIGITAL | IOD_TIS_TCP | 78 | 00078 | ErrComPanelPLC
TISErrComPort2 | DIGITAL | IOD_TIS_TCP | 79 | 00079 | ErrComPort2
TISErrorComCirc1Error | DIGITAL | IOD_TIS_TCP | 80 | 00080 | ErrorComCirc[1].Error
TISErrorComCirc2Error | DIGITAL | IOD_TIS_TCP | 81 | 00081 | ErrorComCirc[2].Error
TISErrorComCirc3Error | DIGITAL | IOD_TIS_TCP | 82 | 00082 | ErrorComCirc[3].Error
TISErrorComCirc4Error | DIGITAL | IOD_TIS_TCP | 83 | 00083 | ErrorComCirc[4].Error
TISErrorComCirc5Error | DIGITAL | IOD_TIS_TCP | 84 | 00084 | ErrorComCirc[5].Error
TISErrorComKlima1Error | DIGITAL | IOD_TIS_TCP | 85 | 00085 | ErrorComKlima[1].Error
TISErrorComKlima2Error | DIGITAL | IOD_TIS_TCP | 86 | 00086 | ErrorComKlima[2].Error
TISErrorComKlima3Error | DIGITAL | IOD_TIS_TCP | 87 | 00087 | ErrorComKlima[3].Error
TISErrorComKlima4Error | DIGITAL | IOD_TIS_TCP | 88 | 00088 | ErrorComKlima[4].Error
TISErrorComKlima5Error | DIGITAL | IOD_TIS_TCP | 89 | 00089 | ErrorComKlima[5].Error
TISErrorComKlima6Error | DIGITAL | IOD_TIS_TCP | 90 | 00090 | ErrorComKlima[6].Error
TISKlima1AlarmKompresor1 | DIGITAL | IOD_TIS_TCP | 91 | 00091 | Klima[1].AlarmKompresor1
TISKlima1AlarmKompresor2 | DIGITAL | IOD_TIS_TCP | 92 | 00092 | Klima[1].AlarmKompresor2
TISKlima1Deluje | DIGITAL | IOD_TIS_TCP | 93 | 00093 | Klima[1].Deluje
TISKlima1EnergySaving | DIGITAL | IOD_TIS_TCP | 94 | 00094 | Klima[1].EnergySaving
TISKlima1FaultyEPROM | DIGITAL | IOD_TIS_TCP | 95 | 00095 | Klima[1].FaultyEPROM
TISKlima1FenThermalCutout | DIGITAL | IOD_TIS_TCP | 96 | 00096 | Klima[1].FenThermalCutout
TISKlima1GeneralAlarm | DIGITAL | IOD_TIS_TCP | 97 | 00097 | Klima[1].GeneralAlarm
TISKlima1Kompresor1naMejiObrUr | DIGITAL | IOD_TIS_TCP | 98 | 00098 | Klima[1].Kompresor1naMejiObrUr
TISKlima1Kompresor2naMejiObrUr | DIGITAL | IOD_TIS_TCP | 99 | 00099 | Klima[1].Kompresor2naMejiObrUr
TISKlima1Napaka | DIGITAL | IOD_TIS_TCP | 100 | 00100 | Klima[1].Napaka
TISKlima1NapakaPriPretokuZraka | DIGITAL | IOD_TIS_TCP | 101 | 00101 | Klima[1].NapakaPriPretokuZraka
TISKlima1NapakaSenzorPovratVode | DIGITAL | IOD_TIS_TCP | 102 | 00102 | Klima[1].NapakaSenzorPovratVode
TISKlima1NapakaSenzorTempIzpiha | DIGITAL | IOD_TIS_TCP | 103 | 00103 | Klima[1].NapakaSenzorTempIzpiha
TISKlima1NapakaSenzorTempProstora | DIGITAL | IOD_TIS_TCP | 104 | 00104 | Klima[1].NapakaSenzorTempProstora
TISKlima1NapakaSenzorVlaznosti | DIGITAL | IOD_TIS_TCP | 105 | 00105 | Klima[1].NapakaSenzorVlaznosti
TISKlima1NapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS_TCP | 106 | 00106 | Klima[1].NapakaSenzorZunanjeTemp
TISKlima1NiTokaVVlazilcu | DIGITAL | IOD_TIS_TCP | 107 | 00107 | Klima[1].NiTokaVVlazilcu
TISKlima1NiVodeVVlazilcu | DIGITAL | IOD_TIS_TCP | 108 | 00108 | Klima[1].NiVodeVVlazilcu
TISKlima1NizekPritiskKompresor1 | DIGITAL | IOD_TIS_TCP | 109 | 00109 | Klima[1].NizekPritiskKompresor1
TISKlima1NizekPritiskKompresor2 | DIGITAL | IOD_TIS_TCP | 110 | 00110 | Klima[1].NizekPritiskKompresor2
TISKlima1NizkaTempPovratneVode | DIGITAL | IOD_TIS_TCP | 111 | 00111 | Klima[1].NizkaTempPovratneVode
TISKlima1NizkaTempVProstoru | DIGITAL | IOD_TIS_TCP | 112 | 00112 | Klima[1].NizkaTempVProstoru
TISKlima1NizkaVlaznost | DIGITAL | IOD_TIS_TCP | 113 | 00113 | Klima[1].NizkaVlaznost
TISKlima1OnOffEnablingBySupervisor | DIGITAL | IOD_TIS_TCP | 114 | 00114 | Klima[1].OnOffEnablingBySupervisor
TISKlima1PozarniAlarm | DIGITAL | IOD_TIS_TCP | 115 | 00115 | Klima[1].PozarniAlarm
TISKlima1Razvlazevanje | DIGITAL | IOD_TIS_TCP | 116 | 00116 | Klima[1].Razvlazevanje
TISKlima1RemoteOFFtoOutput | DIGITAL | IOD_TIS_TCP | 117 | 00117 | Klima[1].RemoteOFFtoOutput
TISKlima1RemoteOnOff | DIGITAL | IOD_TIS_TCP | 118 | 00118 | Klima[1].RemoteOnOff
TISKlima1RocniIzklop | DIGITAL | IOD_TIS_TCP | 119 | 00119 | Klima[1].RocniIzklop
TISKlima1SenzorjiStatus | DIGITAL | IOD_TIS_TCP | 120 | 00120 | Klima[1].SenzorjiStatus
TISKlima1StoppedByAlarms | DIGITAL | IOD_TIS_TCP | 121 | 00121 | Klima[1].StoppedByAlarms
TISKlima1ThermalCutoutHeater1 | DIGITAL | IOD_TIS_TCP | 122 | 00122 | Klima[1].ThermalCutoutHeater1
TISKlima1ThermalCutoutHeater2 | DIGITAL | IOD_TIS_TCP | 123 | 00123 | Klima[1].ThermalCutoutHeater2
TISKlima1UnitOnOff | DIGITAL | IOD_TIS_TCP | 124 | 00124 | Klima[1].UnitOnOff
TISKlima1VentilatorNaMejiObrUr | DIGITAL | IOD_TIS_TCP | 125 | 00125 | Klima[1].VentilatorNaMejiObrUr
TISKlima1VentilGretjeOdpiranje | DIGITAL | IOD_TIS_TCP | 126 | 00126 | Klima[1].VentilGretjeOdpiranje
TISKlima1VentilGretjeZapiranje | DIGITAL | IOD_TIS_TCP | 127 | 00127 | Klima[1].VentilGretjeZapiranje
TISKlima1VentilHlajenjeOdpiranje | DIGITAL | IOD_TIS_TCP | 128 | 00128 | Klima[1].VentilHlajenjeOdpiranje
TISKlima1VentilHlajenjeZapiranje | DIGITAL | IOD_TIS_TCP | 129 | 00129 | Klima[1].VentilHlajenjeZapiranje
TISKlima1VisokaTempPovratneVode | DIGITAL | IOD_TIS_TCP | 130 | 00130 | Klima[1].VisokaTempPovratneVode
TISKlima1VisokaTempVProstoru | DIGITAL | IOD_TIS_TCP | 131 | 00131 | Klima[1].VisokaTempVProstoru
TISKlima1VisokaVlaznost | DIGITAL | IOD_TIS_TCP | 132 | 00132 | Klima[1].VisokaVlaznost
TISKlima1VisokTokVVlazilcu | DIGITAL | IOD_TIS_TCP | 133 | 00133 | Klima[1].VisokTokVVlazilcu
TISKlima1Vlazenje | DIGITAL | IOD_TIS_TCP | 134 | 00134 | Klima[1].Vlazenje
TISKlima1ZamasenFilter | DIGITAL | IOD_TIS_TCP | 135 | 00135 | Klima[1].ZamasenFilter
TISKlima2AlarmKompresor1 | DIGITAL | IOD_TIS_TCP | 136 | 00136 | Klima[2].AlarmKompresor1
TISKlima2AlarmKompresor2 | DIGITAL | IOD_TIS_TCP | 137 | 00137 | Klima[2].AlarmKompresor2
TISKlima2Deluje | DIGITAL | IOD_TIS_TCP | 138 | 00138 | Klima[2].Deluje
TISKlima2EnergySaving | DIGITAL | IOD_TIS_TCP | 139 | 00139 | Klima[2].EnergySaving
TISKlima2FaultyEPROM | DIGITAL | IOD_TIS_TCP | 140 | 00140 | Klima[2].FaultyEPROM
TISKlima2FenThermalCutout | DIGITAL | IOD_TIS_TCP | 141 | 00141 | Klima[2].FenThermalCutout
TISKlima2GeneralAlarm | DIGITAL | IOD_TIS_TCP | 142 | 00142 | Klima[2].GeneralAlarm
TISKlima2Kompresor1naMejiObrUr | DIGITAL | IOD_TIS_TCP | 143 | 00143 | Klima[2].Kompresor1naMejiObrUr
TISKlima2Kompresor2naMejiObrUr | DIGITAL | IOD_TIS_TCP | 144 | 00144 | Klima[2].Kompresor2naMejiObrUr
TISKlima2Napaka | DIGITAL | IOD_TIS_TCP | 145 | 00145 | Klima[2].Napaka
TISKlima2NapakaPriPretokuZraka | DIGITAL | IOD_TIS_TCP | 146 | 00146 | Klima[2].NapakaPriPretokuZraka
TISKlima2NapakaSenzorPovratVode | DIGITAL | IOD_TIS_TCP | 147 | 00147 | Klima[2].NapakaSenzorPovratVode
TISKlima2NapakaSenzorTempIzpiha | DIGITAL | IOD_TIS_TCP | 148 | 00148 | Klima[2].NapakaSenzorTempIzpiha
TISKlima2NapakaSenzorTempProstora | DIGITAL | IOD_TIS_TCP | 149 | 00149 | Klima[2].NapakaSenzorTempProstora
TISKlima2NapakaSenzorVlaznosti | DIGITAL | IOD_TIS_TCP | 150 | 00150 | Klima[2].NapakaSenzorVlaznosti
TISKlima2NapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS_TCP | 151 | 00151 | Klima[2].NapakaSenzorZunanjeTemp
TISKlima2NiTokaVVlazilcu | DIGITAL | IOD_TIS_TCP | 152 | 00152 | Klima[2].NiTokaVVlazilcu
TISKlima2NiVodeVVlazilcu | DIGITAL | IOD_TIS_TCP | 153 | 00153 | Klima[2].NiVodeVVlazilcu
TISKlima2NizekPritiskKompresor1 | DIGITAL | IOD_TIS_TCP | 154 | 00154 | Klima[2].NizekPritiskKompresor1
TISKlima2NizekPritiskKompresor2 | DIGITAL | IOD_TIS_TCP | 155 | 00155 | Klima[2].NizekPritiskKompresor2
TISKlima2NizkaTempPovratneVode | DIGITAL | IOD_TIS_TCP | 156 | 00156 | Klima[2].NizkaTempPovratneVode
TISKlima2NizkaTempVProstoru | DIGITAL | IOD_TIS_TCP | 157 | 00157 | Klima[2].NizkaTempVProstoru
TISKlima2NizkaVlaznost | DIGITAL | IOD_TIS_TCP | 158 | 00158 | Klima[2].NizkaVlaznost
TISKlima2OnOffEnablingBySupervisor | DIGITAL | IOD_TIS_TCP | 159 | 00159 | Klima[2].OnOffEnablingBySupervisor
TISKlima2PozarniAlarm | DIGITAL | IOD_TIS_TCP | 160 | 00160 | Klima[2].PozarniAlarm
TISKlima2Razvlazevanje | DIGITAL | IOD_TIS_TCP | 161 | 00161 | Klima[2].Razvlazevanje
TISKlima2RemoteOFFtoOutput | DIGITAL | IOD_TIS_TCP | 162 | 00162 | Klima[2].RemoteOFFtoOutput
TISKlima2RemoteOnOff | DIGITAL | IOD_TIS_TCP | 163 | 00163 | Klima[2].RemoteOnOff
TISKlima2RocniIzklop | DIGITAL | IOD_TIS_TCP | 164 | 00164 | Klima[2].RocniIzklop
TISKlima2SenzorjiStatus | DIGITAL | IOD_TIS_TCP | 165 | 00165 | Klima[2].SenzorjiStatus
TISKlima2StoppedByAlarms | DIGITAL | IOD_TIS_TCP | 166 | 00166 | Klima[2].StoppedByAlarms
TISKlima2ThermalCutoutHeater1 | DIGITAL | IOD_TIS_TCP | 167 | 00167 | Klima[2].ThermalCutoutHeater1
TISKlima2ThermalCutoutHeater2 | DIGITAL | IOD_TIS_TCP | 168 | 00168 | Klima[2].ThermalCutoutHeater2
TISKlima2UnitOnOff | DIGITAL | IOD_TIS_TCP | 169 | 00169 | Klima[2].UnitOnOff
TISKlima2VentilatorNaMejiObrUr | DIGITAL | IOD_TIS_TCP | 170 | 00170 | Klima[2].VentilatorNaMejiObrUr
TISKlima2VentilGretjeOdpiranje | DIGITAL | IOD_TIS_TCP | 171 | 00171 | Klima[2].VentilGretjeOdpiranje
TISKlima2VentilGretjeZapiranje | DIGITAL | IOD_TIS_TCP | 172 | 00172 | Klima[2].VentilGretjeZapiranje
TISKlima2VentilHlajenjeOdpiranje | DIGITAL | IOD_TIS_TCP | 173 | 00173 | Klima[2].VentilHlajenjeOdpiranje
TISKlima2VentilHlajenjeZapiranje | DIGITAL | IOD_TIS_TCP | 174 | 00174 | Klima[2].VentilHlajenjeZapiranje
TISKlima2VisokaTempPovratneVode | DIGITAL | IOD_TIS_TCP | 175 | 00175 | Klima[2].VisokaTempPovratneVode
TISKlima2VisokaTempVProstoru | DIGITAL | IOD_TIS_TCP | 176 | 00176 | Klima[2].VisokaTempVProstoru
TISKlima2VisokaVlaznost | DIGITAL | IOD_TIS_TCP | 177 | 00177 | Klima[2].VisokaVlaznost
TISKlima2VisokTokVVlazilcu | DIGITAL | IOD_TIS_TCP | 178 | 00178 | Klima[2].VisokTokVVlazilcu
TISKlima2Vlazenje | DIGITAL | IOD_TIS_TCP | 179 | 00179 | Klima[2].Vlazenje
TISKlima2ZamasenFilter | DIGITAL | IOD_TIS_TCP | 180 | 00180 | Klima[2].ZamasenFilter
TISKlima3AlarmKompresor1 | DIGITAL | IOD_TIS_TCP | 181 | 00181 | Klima[3].AlarmKompresor1
TISKlima3AlarmKompresor2 | DIGITAL | IOD_TIS_TCP | 182 | 00182 | Klima[3].AlarmKompresor2
TISKlima3Deluje | DIGITAL | IOD_TIS_TCP | 183 | 00183 | Klima[3].Deluje
TISKlima3EnergySaving | DIGITAL | IOD_TIS_TCP | 184 | 00184 | Klima[3].EnergySaving
TISKlima3FaultyEPROM | DIGITAL | IOD_TIS_TCP | 185 | 00185 | Klima[3].FaultyEPROM
TISKlima3FenThermalCutout | DIGITAL | IOD_TIS_TCP | 186 | 00186 | Klima[3].FenThermalCutout
TISKlima3GeneralAlarm | DIGITAL | IOD_TIS_TCP | 187 | 00187 | Klima[3].GeneralAlarm
TISKlima3Kompresor1naMejiObrUr | DIGITAL | IOD_TIS_TCP | 188 | 00188 | Klima[3].Kompresor1naMejiObrUr
TISKlima3Kompresor2naMejiObrUr | DIGITAL | IOD_TIS_TCP | 189 | 00189 | Klima[3].Kompresor2naMejiObrUr
TISKlima3Napaka | DIGITAL | IOD_TIS_TCP | 190 | 00190 | Klima[3].Napaka
TISKlima3NapakaPriPretokuZraka | DIGITAL | IOD_TIS_TCP | 191 | 00191 | Klima[3].NapakaPriPretokuZraka
TISKlima3NapakaSenzorPovratVode | DIGITAL | IOD_TIS_TCP | 192 | 00192 | Klima[3].NapakaSenzorPovratVode
TISKlima3NapakaSenzorTempIzpiha | DIGITAL | IOD_TIS_TCP | 193 | 00193 | Klima[3].NapakaSenzorTempIzpiha
TISKlima3NapakaSenzorTempProstora | DIGITAL | IOD_TIS_TCP | 194 | 00194 | Klima[3].NapakaSenzorTempProstora
TISKlima3NapakaSenzorVlaznosti | DIGITAL | IOD_TIS_TCP | 195 | 00195 | Klima[3].NapakaSenzorVlaznosti
TISKlima3NapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS_TCP | 196 | 00196 | Klima[3].NapakaSenzorZunanjeTemp
TISKlima3NiTokaVVlazilcu | DIGITAL | IOD_TIS_TCP | 197 | 00197 | Klima[3].NiTokaVVlazilcu
TISKlima3NiVodeVVlazilcu | DIGITAL | IOD_TIS_TCP | 198 | 00198 | Klima[3].NiVodeVVlazilcu
TISKlima3NizekPritiskKompresor1 | DIGITAL | IOD_TIS_TCP | 199 | 00199 | Klima[3].NizekPritiskKompresor1
TISKlima3NizekPritiskKompresor2 | DIGITAL | IOD_TIS_TCP | 200 | 00200 | Klima[3].NizekPritiskKompresor2
TISKlima3NizkaTempPovratneVode | DIGITAL | IOD_TIS_TCP | 201 | 00201 | Klima[3].NizkaTempPovratneVode
TISKlima3NizkaTempVProstoru | DIGITAL | IOD_TIS_TCP | 202 | 00202 | Klima[3].NizkaTempVProstoru
TISKlima3NizkaVlaznost | DIGITAL | IOD_TIS_TCP | 203 | 00203 | Klima[3].NizkaVlaznost
TISKlima3OnOffEnablingBySupervisor | DIGITAL | IOD_TIS_TCP | 204 | 00204 | Klima[3].OnOffEnablingBySupervisor
TISKlima3PozarniAlarm | DIGITAL | IOD_TIS_TCP | 205 | 00205 | Klima[3].PozarniAlarm
TISKlima3Razvlazevanje | DIGITAL | IOD_TIS_TCP | 206 | 00206 | Klima[3].Razvlazevanje
TISKlima3RemoteOFFtoOutput | DIGITAL | IOD_TIS_TCP | 207 | 00207 | Klima[3].RemoteOFFtoOutput
TISKlima3RemoteOnOff | DIGITAL | IOD_TIS_TCP | 208 | 00208 | Klima[3].RemoteOnOff
TISKlima3RocniIzklop | DIGITAL | IOD_TIS_TCP | 209 | 00209 | Klima[3].RocniIzklop
TISKlima3SenzorjiStatus | DIGITAL | IOD_TIS_TCP | 210 | 00210 | Klima[3].SenzorjiStatus
TISKlima3StoppedByAlarms | DIGITAL | IOD_TIS_TCP | 211 | 00211 | Klima[3].StoppedByAlarms
TISKlima3ThermalCutoutHeater1 | DIGITAL | IOD_TIS_TCP | 212 | 00212 | Klima[3].ThermalCutoutHeater1
TISKlima3ThermalCutoutHeater2 | DIGITAL | IOD_TIS_TCP | 213 | 00213 | Klima[3].ThermalCutoutHeater2
TISKlima3UnitOnOff | DIGITAL | IOD_TIS_TCP | 214 | 00214 | Klima[3].UnitOnOff
TISKlima3VentilatorNaMejiObrUr | DIGITAL | IOD_TIS_TCP | 215 | 00215 | Klima[3].VentilatorNaMejiObrUr
TISKlima3VentilGretjeOdpiranje | DIGITAL | IOD_TIS_TCP | 216 | 00216 | Klima[3].VentilGretjeOdpiranje
TISKlima3VentilGretjeZapiranje | DIGITAL | IOD_TIS_TCP | 217 | 00217 | Klima[3].VentilGretjeZapiranje
TISKlima3VentilHlajenjeOdpiranje | DIGITAL | IOD_TIS_TCP | 218 | 00218 | Klima[3].VentilHlajenjeOdpiranje
TISKlima3VentilHlajenjeZapiranje | DIGITAL | IOD_TIS_TCP | 219 | 00219 | Klima[3].VentilHlajenjeZapiranje
TISKlima3VisokaTempPovratneVode | DIGITAL | IOD_TIS_TCP | 220 | 00220 | Klima[3].VisokaTempPovratneVode
TISKlima3VisokaTempVProstoru | DIGITAL | IOD_TIS_TCP | 221 | 00221 | Klima[3].VisokaTempVProstoru
TISKlima3VisokaVlaznost | DIGITAL | IOD_TIS_TCP | 222 | 00222 | Klima[3].VisokaVlaznost
TISKlima3VisokTokVVlazilcu | DIGITAL | IOD_TIS_TCP | 223 | 00223 | Klima[3].VisokTokVVlazilcu
TISKlima3Vlazenje | DIGITAL | IOD_TIS_TCP | 224 | 00224 | Klima[3].Vlazenje
TISKlima3ZamasenFilter | DIGITAL | IOD_TIS_TCP | 225 | 00225 | Klima[3].ZamasenFilter
TISKlimaAErrors10 | DIGITAL | IOD_TIS_TCP | 226 | 00226 | KlimaAErrors[10]
TISKlimaAErrors11 | DIGITAL | IOD_TIS_TCP | 227 | 00227 | KlimaAErrors[11]
TISKlimaAErrors12 | DIGITAL | IOD_TIS_TCP | 228 | 00228 | KlimaAErrors[12]
TISKlimaAErrors13 | DIGITAL | IOD_TIS_TCP | 229 | 00229 | KlimaAErrors[13]
TISKlimaAErrors14 | DIGITAL | IOD_TIS_TCP | 230 | 00230 | KlimaAErrors[14]
TISKlimaAErrors15 | DIGITAL | IOD_TIS_TCP | 231 | 00231 | KlimaAErrors[15]
TISKlimaAErrors16 | DIGITAL | IOD_TIS_TCP | 232 | 00232 | KlimaAErrors[16]
TISKlimaAErrors17 | DIGITAL | IOD_TIS_TCP | 233 | 00233 | KlimaAErrors[17]
TISKlimaAErrors18 | DIGITAL | IOD_TIS_TCP | 234 | 00234 | KlimaAErrors[18]
TISKlimaAErrors19 | DIGITAL | IOD_TIS_TCP | 235 | 00235 | KlimaAErrors[19]
TISKlimaAErrors1 | DIGITAL | IOD_TIS_TCP | 236 | 00236 | KlimaAErrors[1]
TISKlimaAErrors20 | DIGITAL | IOD_TIS_TCP | 237 | 00237 | KlimaAErrors[20]
TISKlimaAErrors21 | DIGITAL | IOD_TIS_TCP | 238 | 00238 | KlimaAErrors[21]
TISKlimaAErrors22 | DIGITAL | IOD_TIS_TCP | 239 | 00239 | KlimaAErrors[22]
TISKlimaAErrors23 | DIGITAL | IOD_TIS_TCP | 240 | 00240 | KlimaAErrors[23]
TISKlimaAErrors24 | DIGITAL | IOD_TIS_TCP | 241 | 00241 | KlimaAErrors[24]
TISKlimaAErrors25 | DIGITAL | IOD_TIS_TCP | 242 | 00242 | KlimaAErrors[25]
TISKlimaAErrors26 | DIGITAL | IOD_TIS_TCP | 243 | 00243 | KlimaAErrors[26]
TISKlimaAErrors27 | DIGITAL | IOD_TIS_TCP | 244 | 00244 | KlimaAErrors[27]
TISKlimaAErrors28 | DIGITAL | IOD_TIS_TCP | 245 | 00245 | KlimaAErrors[28]
TISKlimaAErrors29 | DIGITAL | IOD_TIS_TCP | 246 | 00246 | KlimaAErrors[29]
TISKlimaAErrors2 | DIGITAL | IOD_TIS_TCP | 247 | 00247 | KlimaAErrors[2]
TISKlimaAErrors30 | DIGITAL | IOD_TIS_TCP | 248 | 00248 | KlimaAErrors[30]
TISKlimaAErrors31 | DIGITAL | IOD_TIS_TCP | 249 | 00249 | KlimaAErrors[31]
TISKlimaAErrors32 | DIGITAL | IOD_TIS_TCP | 250 | 00250 | KlimaAErrors[32]
TISKlimaAErrors33 | DIGITAL | IOD_TIS_TCP | 251 | 00251 | KlimaAErrors[33]
TISKlimaAErrors34 | DIGITAL | IOD_TIS_TCP | 252 | 00252 | KlimaAErrors[34]
TISKlimaAErrors35 | DIGITAL | IOD_TIS_TCP | 253 | 00253 | KlimaAErrors[35]
TISKlimaAErrors36 | DIGITAL | IOD_TIS_TCP | 254 | 00254 | KlimaAErrors[36]
TISKlimaAErrors37 | DIGITAL | IOD_TIS_TCP | 255 | 00255 | KlimaAErrors[37]
TISKlimaAErrors38 | DIGITAL | IOD_TIS_TCP | 256 | 00256 | KlimaAErrors[38]
TISKlimaAErrors39 | DIGITAL | IOD_TIS_TCP | 257 | 00257 | KlimaAErrors[39]
TISKlimaAErrors3 | DIGITAL | IOD_TIS_TCP | 258 | 00258 | KlimaAErrors[3]
TISKlimaAErrors40 | DIGITAL | IOD_TIS_TCP | 259 | 00259 | KlimaAErrors[40]
TISKlimaAErrors4 | DIGITAL | IOD_TIS_TCP | 260 | 00260 | KlimaAErrors[4]
TISKlimaAErrors5 | DIGITAL | IOD_TIS_TCP | 261 | 00261 | KlimaAErrors[5]
TISKlimaAErrors6 | DIGITAL | IOD_TIS_TCP | 262 | 00262 | KlimaAErrors[6]
TISKlimaAErrors7 | DIGITAL | IOD_TIS_TCP | 263 | 00263 | KlimaAErrors[7]
TISKlimaAErrors8 | DIGITAL | IOD_TIS_TCP | 264 | 00264 | KlimaAErrors[8]
TISKlimaAErrors9 | DIGITAL | IOD_TIS_TCP | 265 | 00265 | KlimaAErrors[9]
TISKlimaBErrors10 | DIGITAL | IOD_TIS_TCP | 266 | 00266 | KlimaBErrors[10]
TISKlimaBErrors11 | DIGITAL | IOD_TIS_TCP | 267 | 00267 | KlimaBErrors[11]
TISKlimaBErrors12 | DIGITAL | IOD_TIS_TCP | 268 | 00268 | KlimaBErrors[12]
TISKlimaBErrors13 | DIGITAL | IOD_TIS_TCP | 269 | 00269 | KlimaBErrors[13]
TISKlimaBErrors14 | DIGITAL | IOD_TIS_TCP | 270 | 00270 | KlimaBErrors[14]
TISKlimaBErrors15 | DIGITAL | IOD_TIS_TCP | 271 | 00271 | KlimaBErrors[15]
TISKlimaBErrors16 | DIGITAL | IOD_TIS_TCP | 272 | 00272 | KlimaBErrors[16]
TISKlimaBErrors17 | DIGITAL | IOD_TIS_TCP | 273 | 00273 | KlimaBErrors[17]
TISKlimaBErrors18 | DIGITAL | IOD_TIS_TCP | 274 | 00274 | KlimaBErrors[18]
TISKlimaBErrors19 | DIGITAL | IOD_TIS_TCP | 275 | 00275 | KlimaBErrors[19]
TISKlimaBErrors1 | DIGITAL | IOD_TIS_TCP | 276 | 00276 | KlimaBErrors[1]
TISKlimaBErrors20 | DIGITAL | IOD_TIS_TCP | 277 | 00277 | KlimaBErrors[20]
TISKlimaBErrors21 | DIGITAL | IOD_TIS_TCP | 278 | 00278 | KlimaBErrors[21]
TISKlimaBErrors22 | DIGITAL | IOD_TIS_TCP | 279 | 00279 | KlimaBErrors[22]
TISKlimaBErrors23 | DIGITAL | IOD_TIS_TCP | 280 | 00280 | KlimaBErrors[23]
TISKlimaBErrors24 | DIGITAL | IOD_TIS_TCP | 281 | 00281 | KlimaBErrors[24]
TISKlimaBErrors25 | DIGITAL | IOD_TIS_TCP | 282 | 00282 | KlimaBErrors[25]
TISKlimaBErrors26 | DIGITAL | IOD_TIS_TCP | 283 | 00283 | KlimaBErrors[26]
TISKlimaBErrors27 | DIGITAL | IOD_TIS_TCP | 284 | 00284 | KlimaBErrors[27]
TISKlimaBErrors28 | DIGITAL | IOD_TIS_TCP | 285 | 00285 | KlimaBErrors[28]
TISKlimaBErrors29 | DIGITAL | IOD_TIS_TCP | 286 | 00286 | KlimaBErrors[29]
TISKlimaBErrors2 | DIGITAL | IOD_TIS_TCP | 287 | 00287 | KlimaBErrors[2]
TISKlimaBErrors30 | DIGITAL | IOD_TIS_TCP | 288 | 00288 | KlimaBErrors[30]
TISKlimaBErrors31 | DIGITAL | IOD_TIS_TCP | 289 | 00289 | KlimaBErrors[31]
TISKlimaBErrors32 | DIGITAL | IOD_TIS_TCP | 290 | 00290 | KlimaBErrors[32]
TISKlimaBErrors33 | DIGITAL | IOD_TIS_TCP | 291 | 00291 | KlimaBErrors[33]
TISKlimaBErrors34 | DIGITAL | IOD_TIS_TCP | 292 | 00292 | KlimaBErrors[34]
TISKlimaBErrors35 | DIGITAL | IOD_TIS_TCP | 293 | 00293 | KlimaBErrors[35]
TISKlimaBErrors36 | DIGITAL | IOD_TIS_TCP | 294 | 00294 | KlimaBErrors[36]
TISKlimaBErrors37 | DIGITAL | IOD_TIS_TCP | 295 | 00295 | KlimaBErrors[37]
TISKlimaBErrors38 | DIGITAL | IOD_TIS_TCP | 296 | 00296 | KlimaBErrors[38]
TISKlimaBErrors39 | DIGITAL | IOD_TIS_TCP | 297 | 00297 | KlimaBErrors[39]
TISKlimaBErrors3 | DIGITAL | IOD_TIS_TCP | 298 | 00298 | KlimaBErrors[3]
TISKlimaBErrors40 | DIGITAL | IOD_TIS_TCP | 299 | 00299 | KlimaBErrors[40]
TISKlimaBErrors4 | DIGITAL | IOD_TIS_TCP | 300 | 00300 | KlimaBErrors[4]
TISKlimaBErrors5 | DIGITAL | IOD_TIS_TCP | 301 | 00301 | KlimaBErrors[5]
TISKlimaBErrors6 | DIGITAL | IOD_TIS_TCP | 302 | 00302 | KlimaBErrors[6]
TISKlimaBErrors7 | DIGITAL | IOD_TIS_TCP | 303 | 00303 | KlimaBErrors[7]
TISKlimaBErrors8 | DIGITAL | IOD_TIS_TCP | 304 | 00304 | KlimaBErrors[8]
TISKlimaBErrors9 | DIGITAL | IOD_TIS_TCP | 305 | 00305 | KlimaBErrors[9]
TISKlimaCErrors10 | DIGITAL | IOD_TIS_TCP | 306 | 00306 | KlimaCErrors[10]
TISKlimaCErrors11 | DIGITAL | IOD_TIS_TCP | 307 | 00307 | KlimaCErrors[11]
TISKlimaCErrors12 | DIGITAL | IOD_TIS_TCP | 308 | 00308 | KlimaCErrors[12]
TISKlimaCErrors13 | DIGITAL | IOD_TIS_TCP | 309 | 00309 | KlimaCErrors[13]
TISKlimaCErrors14 | DIGITAL | IOD_TIS_TCP | 310 | 00310 | KlimaCErrors[14]
TISKlimaCErrors15 | DIGITAL | IOD_TIS_TCP | 311 | 00311 | KlimaCErrors[15]
TISKlimaCErrors16 | DIGITAL | IOD_TIS_TCP | 312 | 00312 | KlimaCErrors[16]
TISKlimaCErrors17 | DIGITAL | IOD_TIS_TCP | 313 | 00313 | KlimaCErrors[17]
TISKlimaCErrors18 | DIGITAL | IOD_TIS_TCP | 314 | 00314 | KlimaCErrors[18]
TISKlimaCErrors19 | DIGITAL | IOD_TIS_TCP | 315 | 00315 | KlimaCErrors[19]
TISKlimaCErrors1 | DIGITAL | IOD_TIS_TCP | 316 | 00316 | KlimaCErrors[1]
TISKlimaCErrors20 | DIGITAL | IOD_TIS_TCP | 317 | 00317 | KlimaCErrors[20]
TISKlimaCErrors21 | DIGITAL | IOD_TIS_TCP | 318 | 00318 | KlimaCErrors[21]
TISKlimaCErrors22 | DIGITAL | IOD_TIS_TCP | 319 | 00319 | KlimaCErrors[22]
TISKlimaCErrors23 | DIGITAL | IOD_TIS_TCP | 320 | 00320 | KlimaCErrors[23]
TISKlimaCErrors24 | DIGITAL | IOD_TIS_TCP | 321 | 00321 | KlimaCErrors[24]
TISKlimaCErrors25 | DIGITAL | IOD_TIS_TCP | 322 | 00322 | KlimaCErrors[25]
TISKlimaCErrors26 | DIGITAL | IOD_TIS_TCP | 323 | 00323 | KlimaCErrors[26]
TISKlimaCErrors27 | DIGITAL | IOD_TIS_TCP | 324 | 00324 | KlimaCErrors[27]
TISKlimaCErrors28 | DIGITAL | IOD_TIS_TCP | 325 | 00325 | KlimaCErrors[28]
TISKlimaCErrors29 | DIGITAL | IOD_TIS_TCP | 326 | 00326 | KlimaCErrors[29]
TISKlimaCErrors2 | DIGITAL | IOD_TIS_TCP | 327 | 00327 | KlimaCErrors[2]
TISKlimaCErrors30 | DIGITAL | IOD_TIS_TCP | 328 | 00328 | KlimaCErrors[30]
TISKlimaCErrors31 | DIGITAL | IOD_TIS_TCP | 329 | 00329 | KlimaCErrors[31]
TISKlimaCErrors32 | DIGITAL | IOD_TIS_TCP | 330 | 00330 | KlimaCErrors[32]
TISKlimaCErrors33 | DIGITAL | IOD_TIS_TCP | 331 | 00331 | KlimaCErrors[33]
TISKlimaCErrors34 | DIGITAL | IOD_TIS_TCP | 332 | 00332 | KlimaCErrors[34]
TISKlimaCErrors35 | DIGITAL | IOD_TIS_TCP | 333 | 00333 | KlimaCErrors[35]
TISKlimaCErrors36 | DIGITAL | IOD_TIS_TCP | 334 | 00334 | KlimaCErrors[36]
TISKlimaCErrors37 | DIGITAL | IOD_TIS_TCP | 335 | 00335 | KlimaCErrors[37]
TISKlimaCErrors38 | DIGITAL | IOD_TIS_TCP | 336 | 00336 | KlimaCErrors[38]
TISKlimaCErrors39 | DIGITAL | IOD_TIS_TCP | 337 | 00337 | KlimaCErrors[39]
TISKlimaCErrors3 | DIGITAL | IOD_TIS_TCP | 338 | 00338 | KlimaCErrors[3]
TISKlimaCErrors40 | DIGITAL | IOD_TIS_TCP | 339 | 00339 | KlimaCErrors[40]
TISKlimaCErrors4 | DIGITAL | IOD_TIS_TCP | 340 | 00340 | KlimaCErrors[4]
TISKlimaCErrors5 | DIGITAL | IOD_TIS_TCP | 341 | 00341 | KlimaCErrors[5]
TISKlimaCErrors6 | DIGITAL | IOD_TIS_TCP | 342 | 00342 | KlimaCErrors[6]
TISKlimaCErrors7 | DIGITAL | IOD_TIS_TCP | 343 | 00343 | KlimaCErrors[7]
TISKlimaCErrors8 | DIGITAL | IOD_TIS_TCP | 344 | 00344 | KlimaCErrors[8]
TISKlimaCErrors9 | DIGITAL | IOD_TIS_TCP | 345 | 00345 | KlimaCErrors[9]
TISKlimaGalAlarmKompresor1 | DIGITAL | IOD_TIS_TCP | 346 | 00346 | KlimaGal.AlarmKompresor1
TISKlimaGalAlarmKompresor2 | DIGITAL | IOD_TIS_TCP | 347 | 00347 | KlimaGal.AlarmKompresor2
TISKlimaGalDeluje | DIGITAL | IOD_TIS_TCP | 348 | 00348 | KlimaGal.Deluje
TISKlimaGalEnergySaving | DIGITAL | IOD_TIS_TCP | 349 | 00349 | KlimaGal.EnergySaving
TISKlimaGalFaultyEPROM | DIGITAL | IOD_TIS_TCP | 350 | 00350 | KlimaGal.FaultyEPROM
TISKlimaGalFenThermalCutout | DIGITAL | IOD_TIS_TCP | 351 | 00351 | KlimaGal.FenThermalCutout
TISKlimaGalGeneralAlarm | DIGITAL | IOD_TIS_TCP | 352 | 00352 | KlimaGal.GeneralAlarm
TISKlimaGalKompresor1naMejiObrUr | DIGITAL | IOD_TIS_TCP | 353 | 00353 | KlimaGal.Kompresor1naMejiObrUr
TISKlimaGalKompresor2naMejiObrUr | DIGITAL | IOD_TIS_TCP | 354 | 00354 | KlimaGal.Kompresor2naMejiObrUr
TISKlimaGalNapaka | DIGITAL | IOD_TIS_TCP | 355 | 00355 | KlimaGal.Napaka
TISKlimaGalNapakaPriPretokuZraka | DIGITAL | IOD_TIS_TCP | 356 | 00356 | KlimaGal.NapakaPriPretokuZraka
TISKlimaGalNapakaSenzorPovratVode | DIGITAL | IOD_TIS_TCP | 357 | 00357 | KlimaGal.NapakaSenzorPovratVode
TISKlimaGalNapakaSenzorTempIzpiha | DIGITAL | IOD_TIS_TCP | 358 | 00358 | KlimaGal.NapakaSenzorTempIzpiha
TISKlimaGalNapakaSenzorTempProstora | DIGITAL | IOD_TIS_TCP | 359 | 00359 | KlimaGal.NapakaSenzorTempProstora
TISKlimaGalNapakaSenzorVlaznosti | DIGITAL | IOD_TIS_TCP | 360 | 00360 | KlimaGal.NapakaSenzorVlaznosti
TISKlimaGalNapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS_TCP | 361 | 00361 | KlimaGal.NapakaSenzorZunanjeTemp
TISKlimaGalNiTokaVVlazilcu | DIGITAL | IOD_TIS_TCP | 362 | 00362 | KlimaGal.NiTokaVVlazilcu
TISKlimaGalNiVodeVVlazilcu | DIGITAL | IOD_TIS_TCP | 363 | 00363 | KlimaGal.NiVodeVVlazilcu
TISKlimaGalNizekPritiskKompresor1 | DIGITAL | IOD_TIS_TCP | 364 | 00364 | KlimaGal.NizekPritiskKompresor1
TISKlimaGalNizekPritiskKompresor2 | DIGITAL | IOD_TIS_TCP | 365 | 00365 | KlimaGal.NizekPritiskKompresor2
TISKlimaGalNizkaTempPovratneVode | DIGITAL | IOD_TIS_TCP | 366 | 00366 | KlimaGal.NizkaTempPovratneVode
TISKlimaGalNizkaTempVProstoru | DIGITAL | IOD_TIS_TCP | 367 | 00367 | KlimaGal.NizkaTempVProstoru
TISKlimaGalNizkaVlaznost | DIGITAL | IOD_TIS_TCP | 368 | 00368 | KlimaGal.NizkaVlaznost
TISKlimaGalOnOffEnablingBySupervisor | DIGITAL | IOD_TIS_TCP | 369 | 00369 | KlimaGal.OnOffEnablingBySupervisor
TISKlimaGalPozarniAlarm | DIGITAL | IOD_TIS_TCP | 370 | 00370 | KlimaGal.PozarniAlarm
TISKlimaGalRazvlazevanje | DIGITAL | IOD_TIS_TCP | 371 | 00371 | KlimaGal.Razvlazevanje
TISKlimaGalRemoteOFFtoOutput | DIGITAL | IOD_TIS_TCP | 372 | 00372 | KlimaGal.RemoteOFFtoOutput
TISKlimaGalRemoteOnOff | DIGITAL | IOD_TIS_TCP | 373 | 00373 | KlimaGal.RemoteOnOff
TISKlimaGalRocniIzklop | DIGITAL | IOD_TIS_TCP | 374 | 00374 | KlimaGal.RocniIzklop
TISKlimaGalSenzorjiStatus | DIGITAL | IOD_TIS_TCP | 375 | 00375 | KlimaGal.SenzorjiStatus
TISKlimaGalStoppedByAlarms | DIGITAL | IOD_TIS_TCP | 376 | 00376 | KlimaGal.StoppedByAlarms
TISKlimaGalThermalCutoutHeater1 | DIGITAL | IOD_TIS_TCP | 377 | 00377 | KlimaGal.ThermalCutoutHeater1
TISKlimaGalThermalCutoutHeater2 | DIGITAL | IOD_TIS_TCP | 378 | 00378 | KlimaGal.ThermalCutoutHeater2
TISKlimaGalUnitOnOff | DIGITAL | IOD_TIS_TCP | 379 | 00379 | KlimaGal.UnitOnOff
TISKlimaGalVentilatorNaMejiObrUr | DIGITAL | IOD_TIS_TCP | 380 | 00380 | KlimaGal.VentilatorNaMejiObrUr
TISKlimaGalVentilGretjeOdpiranje | DIGITAL | IOD_TIS_TCP | 381 | 00381 | KlimaGal.VentilGretjeOdpiranje
TISKlimaGalVentilGretjeZapiranje | DIGITAL | IOD_TIS_TCP | 382 | 00382 | KlimaGal.VentilGretjeZapiranje
TISKlimaGalVentilHlajenjeOdpiranje | DIGITAL | IOD_TIS_TCP | 383 | 00383 | KlimaGal.VentilHlajenjeOdpiranje
TISKlimaGalVentilHlajenjeZapiranje | DIGITAL | IOD_TIS_TCP | 384 | 00384 | KlimaGal.VentilHlajenjeZapiranje
TISKlimaGalVisokaTempPovratneVode | DIGITAL | IOD_TIS_TCP | 385 | 00385 | KlimaGal.VisokaTempPovratneVode
TISKlimaGalVisokaTempVProstoru | DIGITAL | IOD_TIS_TCP | 386 | 00386 | KlimaGal.VisokaTempVProstoru
TISKlimaGalVisokaVlaznost | DIGITAL | IOD_TIS_TCP | 387 | 00387 | KlimaGal.VisokaVlaznost
TISKlimaGalVisokTokVVlazilcu | DIGITAL | IOD_TIS_TCP | 388 | 00388 | KlimaGal.VisokTokVVlazilcu
TISKlimaGalVlazenje | DIGITAL | IOD_TIS_TCP | 389 | 00389 | KlimaGal.Vlazenje
TISKlimaGalZamasenFilter | DIGITAL | IOD_TIS_TCP | 390 | 00390 | KlimaGal.ZamasenFilter
TISKlimeNaCas | DIGITAL | IOD_TIS_TCP | 391 | 00391 | KlimeNaCas
TISNapakaSenzorTemp10 | DIGITAL | IOD_TIS_TCP | 392 | 00392 | NapakaSenzorTemp[10]
TISNapakaSenzorTemp11 | DIGITAL | IOD_TIS_TCP | 393 | 00393 | NapakaSenzorTemp[11]
TISNapakaSenzorTemp12 | DIGITAL | IOD_TIS_TCP | 394 | 00394 | NapakaSenzorTemp[12]
TISNapakaSenzorTemp13 | DIGITAL | IOD_TIS_TCP | 395 | 00395 | NapakaSenzorTemp[13]
TISNapakaSenzorTemp14 | DIGITAL | IOD_TIS_TCP | 396 | 00396 | NapakaSenzorTemp[14]
TISNapakaSenzorTemp15 | DIGITAL | IOD_TIS_TCP | 397 | 00397 | NapakaSenzorTemp[15]
TISNapakaSenzorTemp16 | DIGITAL | IOD_TIS_TCP | 398 | 00398 | NapakaSenzorTemp[16]
TISNapakaSenzorTemp17 | DIGITAL | IOD_TIS_TCP | 399 | 00399 | NapakaSenzorTemp[17]
TISNapakaSenzorTemp18 | DIGITAL | IOD_TIS_TCP | 400 | 00400 | NapakaSenzorTemp[18]
TISNapakaSenzorTemp19 | DIGITAL | IOD_TIS_TCP | 401 | 00401 | NapakaSenzorTemp[19]
TISNapakaSenzorTemp1 | DIGITAL | IOD_TIS_TCP | 402 | 00402 | NapakaSenzorTemp[1]
TISNapakaSenzorTemp2 | DIGITAL | IOD_TIS_TCP | 403 | 00403 | NapakaSenzorTemp[2]
TISNapakaSenzorTemp3 | DIGITAL | IOD_TIS_TCP | 404 | 00404 | NapakaSenzorTemp[3]
TISNapakaSenzorTemp4 | DIGITAL | IOD_TIS_TCP | 405 | 00405 | NapakaSenzorTemp[4]
TISNapakaSenzorTemp5 | DIGITAL | IOD_TIS_TCP | 406 | 00406 | NapakaSenzorTemp[5]
TISNapakaSenzorTemp6 | DIGITAL | IOD_TIS_TCP | 407 | 00407 | NapakaSenzorTemp[6]
TISNapakaSenzorTemp7 | DIGITAL | IOD_TIS_TCP | 408 | 00408 | NapakaSenzorTemp[7]
TISNapakaSenzorTemp8 | DIGITAL | IOD_TIS_TCP | 409 | 00409 | NapakaSenzorTemp[8]
TISNapakaSenzorTemp9 | DIGITAL | IOD_TIS_TCP | 410 | 00410 | NapakaSenzorTemp[9]
TISNapakaSenzorVlaga10 | DIGITAL | IOD_TIS_TCP | 411 | 00411 | NapakaSenzorVlaga[10]
TISNapakaSenzorVlaga11 | DIGITAL | IOD_TIS_TCP | 412 | 00412 | NapakaSenzorVlaga[11]
TISNapakaSenzorVlaga12 | DIGITAL | IOD_TIS_TCP | 413 | 00413 | NapakaSenzorVlaga[12]
TISNapakaSenzorVlaga13 | DIGITAL | IOD_TIS_TCP | 414 | 00414 | NapakaSenzorVlaga[13]
TISNapakaSenzorVlaga14 | DIGITAL | IOD_TIS_TCP | 415 | 00415 | NapakaSenzorVlaga[14]
TISNapakaSenzorVlaga15 | DIGITAL | IOD_TIS_TCP | 416 | 00416 | NapakaSenzorVlaga[15]
TISNapakaSenzorVlaga16 | DIGITAL | IOD_TIS_TCP | 417 | 00417 | NapakaSenzorVlaga[16]
TISNapakaSenzorVlaga17 | DIGITAL | IOD_TIS_TCP | 418 | 00418 | NapakaSenzorVlaga[17]
TISNapakaSenzorVlaga18 | DIGITAL | IOD_TIS_TCP | 419 | 00419 | NapakaSenzorVlaga[18]
TISNapakaSenzorVlaga19 | DIGITAL | IOD_TIS_TCP | 420 | 00420 | NapakaSenzorVlaga[19]
TISNapakaSenzorVlaga1 | DIGITAL | IOD_TIS_TCP | 421 | 00421 | NapakaSenzorVlaga[1]
TISNapakaSenzorVlaga2 | DIGITAL | IOD_TIS_TCP | 422 | 00422 | NapakaSenzorVlaga[2]
TISNapakaSenzorVlaga3 | DIGITAL | IOD_TIS_TCP | 423 | 00423 | NapakaSenzorVlaga[3]
TISNapakaSenzorVlaga4 | DIGITAL | IOD_TIS_TCP | 424 | 00424 | NapakaSenzorVlaga[4]
TISNapakaSenzorVlaga5 | DIGITAL | IOD_TIS_TCP | 425 | 00425 | NapakaSenzorVlaga[5]
TISNapakaSenzorVlaga6 | DIGITAL | IOD_TIS_TCP | 426 | 00426 | NapakaSenzorVlaga[6]
TISNapakaSenzorVlaga7 | DIGITAL | IOD_TIS_TCP | 427 | 00427 | NapakaSenzorVlaga[7]
TISNapakaSenzorVlaga8 | DIGITAL | IOD_TIS_TCP | 428 | 00428 | NapakaSenzorVlaga[8]
TISNapakaSenzorVlaga9 | DIGITAL | IOD_TIS_TCP | 429 | 00429 | NapakaSenzorVlaga[9]
TISSetDateTime | DIGITAL | IOD_TIS_TCP | 430 | 00430 | SetDateTime
TISSetDateTimeDemand | DIGITAL | IOD_TIS_TCP | 431 | 00431 | SetDateTimeDemand
TISSetDateTimeError | DIGITAL | IOD_TIS_TCP | 432 | 00432 | SetDateTimeError
TISSetDateTimeFinished | DIGITAL | IOD_TIS_TCP | 433 | 00433 | SetDateTimeFinished
TISSetRemoteOnOff1 | DIGITAL | IOD_TIS_TCP | 434 | 00434 | SetRemoteOnOff[1]
TISSetRemoteOnOff2 | DIGITAL | IOD_TIS_TCP | 435 | 00435 | SetRemoteOnOff[2]
TISSetRemoteOnOff3 | DIGITAL | IOD_TIS_TCP | 436 | 00436 | SetRemoteOnOff[3]
TISSlabaBaterijaPLC_A1 | DIGITAL | IOD_TIS_TCP | 437 | 00437 | SlabaBaterijaPLC_A1
TISTempTSprevisoka10 | DIGITAL | IOD_TIS_TCP | 438 | 00438 | TempTSprevisoka[10]
TISTempTSprevisoka11 | DIGITAL | IOD_TIS_TCP | 439 | 00439 | TempTSprevisoka[11]
TISTempTSprevisoka12 | DIGITAL | IOD_TIS_TCP | 440 | 00440 | TempTSprevisoka[12]
TISTempTSprevisoka13 | DIGITAL | IOD_TIS_TCP | 441 | 00441 | TempTSprevisoka[13]
TISTempTSprevisoka14 | DIGITAL | IOD_TIS_TCP | 442 | 00442 | TempTSprevisoka[14]
TISTempTSprevisoka15 | DIGITAL | IOD_TIS_TCP | 443 | 00443 | TempTSprevisoka[15]
TISTempTSprevisoka16 | DIGITAL | IOD_TIS_TCP | 444 | 00444 | TempTSprevisoka[16]
TISTempTSprevisoka17 | DIGITAL | IOD_TIS_TCP | 445 | 00445 | TempTSprevisoka[17]
TISTempTSprevisoka18 | DIGITAL | IOD_TIS_TCP | 446 | 00446 | TempTSprevisoka[18]
TISTempTSprevisoka19 | DIGITAL | IOD_TIS_TCP | 447 | 00447 | TempTSprevisoka[19]
TISTempTSprevisoka1 | DIGITAL | IOD_TIS_TCP | 448 | 00448 | TempTSprevisoka[1]
TISTempTSprevisoka2 | DIGITAL | IOD_TIS_TCP | 449 | 00449 | TempTSprevisoka[2]
TISTempTSprevisoka3 | DIGITAL | IOD_TIS_TCP | 450 | 00450 | TempTSprevisoka[3]
TISTempTSprevisoka4 | DIGITAL | IOD_TIS_TCP | 451 | 00451 | TempTSprevisoka[4]
TISTempTSprevisoka5 | DIGITAL | IOD_TIS_TCP | 452 | 00452 | TempTSprevisoka[5]
TISTempTSprevisoka6 | DIGITAL | IOD_TIS_TCP | 453 | 00453 | TempTSprevisoka[6]
TISTempTSprevisoka7 | DIGITAL | IOD_TIS_TCP | 454 | 00454 | TempTSprevisoka[7]
TISTempTSprevisoka8 | DIGITAL | IOD_TIS_TCP | 455 | 00455 | TempTSprevisoka[8]
TISTempTSprevisoka9 | DIGITAL | IOD_TIS_TCP | 456 | 00456 | TempTSprevisoka[9]
TISUserLoggedIn | DIGITAL | IOD_TIS_TCP | 457 | 00457 | UserLoggedIn
TISXVH_AlarmOn | DIGITAL | IOD_TIS_TCP | 458 | 00458 | XVH_AlarmOn
TISXVH_RemoteStatus1 | DIGITAL | IOD_TIS_TCP | 459 | 00459 | XVH_RemoteStatus[1]
TISXVH_RemoteStatus2 | DIGITAL | IOD_TIS_TCP | 460 | 00460 | XVH_RemoteStatus[2]
TISXVH_RemoteStatus3 | DIGITAL | IOD_TIS_TCP | 461 | 00461 | XVH_RemoteStatus[3]
TISXVH_setCircNum1 | DIGITAL | IOD_TIS_TCP | 462 | 00462 | XVH_setCircNum[1]
TISXVH_setCircNum2 | DIGITAL | IOD_TIS_TCP | 463 | 00463 | XVH_setCircNum[2]
TISXVH_setCircNum3 | DIGITAL | IOD_TIS_TCP | 464 | 00464 | XVH_setCircNum[3]
TISXVH_setCircNum4 | DIGITAL | IOD_TIS_TCP | 465 | 00465 | XVH_setCircNum[4]
TISXVH_setCircNum5 | DIGITAL | IOD_TIS_TCP | 466 | 00466 | XVH_setCircNum[5]
TISXVH_setKlimaNum1 | DIGITAL | IOD_TIS_TCP | 467 | 00467 | XVH_setKlimaNum[1]
TISXVH_setKlimaNum2 | DIGITAL | IOD_TIS_TCP | 468 | 00468 | XVH_setKlimaNum[2]
TISXVH_setKlimaNum3 | DIGITAL | IOD_TIS_TCP | 469 | 00469 | XVH_setKlimaNum[3]
TISXVH_setKlimaNum4 | DIGITAL | IOD_TIS_TCP | 470 | 00470 | XVH_setKlimaNum[4]
TISXVH_setKlimaNum5 | DIGITAL | IOD_TIS_TCP | 471 | 00471 | XVH_setKlimaNum[5]
TISXVH_setKlimaNum6 | DIGITAL | IOD_TIS_TCP | 472 | 00472 | XVH_setKlimaNum[6]
TISComSCADA2 | DIGITAL | IOD_TIS_TCP | 473 | 00473 | ComSCADA2
TISErrCommScada2 | DIGITAL | IOD_TIS_TCP | 474 | 00474 | ErrCommScada2
TISComSCADA3 | DIGITAL | IOD_TIS_TCP | 475 | 00475 | ComSCADA3
TISCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_TIS_TCP | 476 | 00476 | Circ_Vpis_Dnevne_energija_scada1
TISCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_TIS_TCP | 477 | 00477 | Circ_Vpis_Dnevne_energija_scada2
TISCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_TIS_TCP | 478 | 00478 | Circ_Vpis_Tedenska_energija_scada1
TISCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_TIS_TCP | 479 | 00479 | Circ_Vpis_Tedenska_energija_scada2
TISCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_TIS_TCP | 480 | 00480 | Circ_Vpis_Mesecna_energija_scada1
TISCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_TIS_TCP | 481 | 00481 | Circ_Vpis_Mesecna_energija_scada2
TISDateTimeDan | INT | IOD_TIS_TCP | 1 | 40001 | DateTime.Dan | BYTE
TISDateTimeLeto | INT | IOD_TIS_TCP | 2 | 40002 | DateTime.Leto | BYTE
TISDateTimeMesec | INT | IOD_TIS_TCP | 3 | 40003 | DateTime.Mesec | BYTE
TISDateTimeMinuta | INT | IOD_TIS_TCP | 4 | 40004 | DateTime.Minuta | BYTE
TISDateTimeSekunda | INT | IOD_TIS_TCP | 5 | 40005 | DateTime.Sekunda | BYTE
TISDateTimeUra | INT | IOD_TIS_TCP | 6 | 40006 | DateTime.Ura | BYTE
TISErrorComCirc1Code10 | INT | IOD_TIS_TCP | 7 | 40007 | ErrorComCirc[1].Code[10] | BYTE
TISErrorComCirc1Code11 | INT | IOD_TIS_TCP | 8 | 40008 | ErrorComCirc[1].Code[11] | BYTE
TISErrorComCirc1Code12 | INT | IOD_TIS_TCP | 9 | 40009 | ErrorComCirc[1].Code[12] | BYTE
TISErrorComCirc1Code13 | INT | IOD_TIS_TCP | 10 | 40010 | ErrorComCirc[1].Code[13] | BYTE
TISErrorComCirc1Code14 | INT | IOD_TIS_TCP | 11 | 40011 | ErrorComCirc[1].Code[14] | BYTE
TISErrorComCirc1Code15 | INT | IOD_TIS_TCP | 12 | 40012 | ErrorComCirc[1].Code[15] | BYTE
TISErrorComCirc1Code1 | INT | IOD_TIS_TCP | 13 | 40013 | ErrorComCirc[1].Code[1] | BYTE
TISErrorComCirc1Code2 | INT | IOD_TIS_TCP | 14 | 40014 | ErrorComCirc[1].Code[2] | BYTE
TISErrorComCirc1Code3 | INT | IOD_TIS_TCP | 15 | 40015 | ErrorComCirc[1].Code[3] | BYTE
TISErrorComCirc1Code4 | INT | IOD_TIS_TCP | 16 | 40016 | ErrorComCirc[1].Code[4] | BYTE
TISErrorComCirc1Code5 | INT | IOD_TIS_TCP | 17 | 40017 | ErrorComCirc[1].Code[5] | BYTE
TISErrorComCirc1Code6 | INT | IOD_TIS_TCP | 18 | 40018 | ErrorComCirc[1].Code[6] | BYTE
TISErrorComCirc1Code7 | INT | IOD_TIS_TCP | 19 | 40019 | ErrorComCirc[1].Code[7] | BYTE
TISErrorComCirc1Code8 | INT | IOD_TIS_TCP | 20 | 40020 | ErrorComCirc[1].Code[8] | BYTE
TISErrorComCirc1Code9 | INT | IOD_TIS_TCP | 21 | 40021 | ErrorComCirc[1].Code[9] | BYTE
TISErrorComCirc1Status | INT | IOD_TIS_TCP | 22 | 40022 | ErrorComCirc[1].Status
TISErrorComCirc2Code10 | INT | IOD_TIS_TCP | 23 | 40023 | ErrorComCirc[2].Code[10] | BYTE
TISErrorComCirc2Code11 | INT | IOD_TIS_TCP | 24 | 40024 | ErrorComCirc[2].Code[11] | BYTE
TISErrorComCirc2Code12 | INT | IOD_TIS_TCP | 25 | 40025 | ErrorComCirc[2].Code[12] | BYTE
TISErrorComCirc2Code13 | INT | IOD_TIS_TCP | 26 | 40026 | ErrorComCirc[2].Code[13] | BYTE
TISErrorComCirc2Code14 | INT | IOD_TIS_TCP | 27 | 40027 | ErrorComCirc[2].Code[14] | BYTE
TISErrorComCirc2Code15 | INT | IOD_TIS_TCP | 28 | 40028 | ErrorComCirc[2].Code[15] | BYTE
TISErrorComCirc2Code1 | INT | IOD_TIS_TCP | 29 | 40029 | ErrorComCirc[2].Code[1] | BYTE
TISErrorComCirc2Code2 | INT | IOD_TIS_TCP | 30 | 40030 | ErrorComCirc[2].Code[2] | BYTE
TISErrorComCirc2Code3 | INT | IOD_TIS_TCP | 31 | 40031 | ErrorComCirc[2].Code[3] | BYTE
TISErrorComCirc2Code4 | INT | IOD_TIS_TCP | 32 | 40032 | ErrorComCirc[2].Code[4] | BYTE
TISErrorComCirc2Code5 | INT | IOD_TIS_TCP | 33 | 40033 | ErrorComCirc[2].Code[5] | BYTE
TISErrorComCirc2Code6 | INT | IOD_TIS_TCP | 34 | 40034 | ErrorComCirc[2].Code[6] | BYTE
TISErrorComCirc2Code7 | INT | IOD_TIS_TCP | 35 | 40035 | ErrorComCirc[2].Code[7] | BYTE
TISErrorComCirc2Code8 | INT | IOD_TIS_TCP | 36 | 40036 | ErrorComCirc[2].Code[8] | BYTE
TISErrorComCirc2Code9 | INT | IOD_TIS_TCP | 37 | 40037 | ErrorComCirc[2].Code[9] | BYTE
TISErrorComCirc2Status | INT | IOD_TIS_TCP | 38 | 40038 | ErrorComCirc[2].Status
TISErrorComCirc3Code10 | INT | IOD_TIS_TCP | 39 | 40039 | ErrorComCirc[3].Code[10] | BYTE
TISErrorComCirc3Code11 | INT | IOD_TIS_TCP | 40 | 40040 | ErrorComCirc[3].Code[11] | BYTE
TISErrorComCirc3Code12 | INT | IOD_TIS_TCP | 41 | 40041 | ErrorComCirc[3].Code[12] | BYTE
TISErrorComCirc3Code13 | INT | IOD_TIS_TCP | 42 | 40042 | ErrorComCirc[3].Code[13] | BYTE
TISErrorComCirc3Code14 | INT | IOD_TIS_TCP | 43 | 40043 | ErrorComCirc[3].Code[14] | BYTE
TISErrorComCirc3Code15 | INT | IOD_TIS_TCP | 44 | 40044 | ErrorComCirc[3].Code[15] | BYTE
TISErrorComCirc3Code1 | INT | IOD_TIS_TCP | 45 | 40045 | ErrorComCirc[3].Code[1] | BYTE
TISErrorComCirc3Code2 | INT | IOD_TIS_TCP | 46 | 40046 | ErrorComCirc[3].Code[2] | BYTE
TISErrorComCirc3Code3 | INT | IOD_TIS_TCP | 47 | 40047 | ErrorComCirc[3].Code[3] | BYTE
TISErrorComCirc3Code4 | INT | IOD_TIS_TCP | 48 | 40048 | ErrorComCirc[3].Code[4] | BYTE
TISErrorComCirc3Code5 | INT | IOD_TIS_TCP | 49 | 40049 | ErrorComCirc[3].Code[5] | BYTE
TISErrorComCirc3Code6 | INT | IOD_TIS_TCP | 50 | 40050 | ErrorComCirc[3].Code[6] | BYTE
TISErrorComCirc3Code7 | INT | IOD_TIS_TCP | 51 | 40051 | ErrorComCirc[3].Code[7] | BYTE
TISErrorComCirc3Code8 | INT | IOD_TIS_TCP | 52 | 40052 | ErrorComCirc[3].Code[8] | BYTE
TISErrorComCirc3Code9 | INT | IOD_TIS_TCP | 53 | 40053 | ErrorComCirc[3].Code[9] | BYTE
TISErrorComCirc3Status | INT | IOD_TIS_TCP | 54 | 40054 | ErrorComCirc[3].Status
TISErrorComCirc4Code10 | INT | IOD_TIS_TCP | 55 | 40055 | ErrorComCirc[4].Code[10] | BYTE
TISErrorComCirc4Code11 | INT | IOD_TIS_TCP | 56 | 40056 | ErrorComCirc[4].Code[11] | BYTE
TISErrorComCirc4Code12 | INT | IOD_TIS_TCP | 57 | 40057 | ErrorComCirc[4].Code[12] | BYTE
TISErrorComCirc4Code13 | INT | IOD_TIS_TCP | 58 | 40058 | ErrorComCirc[4].Code[13] | BYTE
TISErrorComCirc4Code14 | INT | IOD_TIS_TCP | 59 | 40059 | ErrorComCirc[4].Code[14] | BYTE
TISErrorComCirc4Code15 | INT | IOD_TIS_TCP | 60 | 40060 | ErrorComCirc[4].Code[15] | BYTE
TISErrorComCirc4Code1 | INT | IOD_TIS_TCP | 61 | 40061 | ErrorComCirc[4].Code[1] | BYTE
TISErrorComCirc4Code2 | INT | IOD_TIS_TCP | 62 | 40062 | ErrorComCirc[4].Code[2] | BYTE
TISErrorComCirc4Code3 | INT | IOD_TIS_TCP | 63 | 40063 | ErrorComCirc[4].Code[3] | BYTE
TISErrorComCirc4Code4 | INT | IOD_TIS_TCP | 64 | 40064 | ErrorComCirc[4].Code[4] | BYTE
TISErrorComCirc4Code5 | INT | IOD_TIS_TCP | 65 | 40065 | ErrorComCirc[4].Code[5] | BYTE
TISErrorComCirc4Code6 | INT | IOD_TIS_TCP | 66 | 40066 | ErrorComCirc[4].Code[6] | BYTE
TISErrorComCirc4Code7 | INT | IOD_TIS_TCP | 67 | 40067 | ErrorComCirc[4].Code[7] | BYTE
TISErrorComCirc4Code8 | INT | IOD_TIS_TCP | 68 | 40068 | ErrorComCirc[4].Code[8] | BYTE
TISErrorComCirc4Code9 | INT | IOD_TIS_TCP | 69 | 40069 | ErrorComCirc[4].Code[9] | BYTE
TISErrorComCirc4Status | INT | IOD_TIS_TCP | 70 | 40070 | ErrorComCirc[4].Status
TISErrorComCirc5Code10 | INT | IOD_TIS_TCP | 71 | 40071 | ErrorComCirc[5].Code[10] | BYTE
TISErrorComCirc5Code11 | INT | IOD_TIS_TCP | 72 | 40072 | ErrorComCirc[5].Code[11] | BYTE
TISErrorComCirc5Code12 | INT | IOD_TIS_TCP | 73 | 40073 | ErrorComCirc[5].Code[12] | BYTE
TISErrorComCirc5Code13 | INT | IOD_TIS_TCP | 74 | 40074 | ErrorComCirc[5].Code[13] | BYTE
TISErrorComCirc5Code14 | INT | IOD_TIS_TCP | 75 | 40075 | ErrorComCirc[5].Code[14] | BYTE
TISErrorComCirc5Code15 | INT | IOD_TIS_TCP | 76 | 40076 | ErrorComCirc[5].Code[15] | BYTE
TISErrorComCirc5Code1 | INT | IOD_TIS_TCP | 77 | 40077 | ErrorComCirc[5].Code[1] | BYTE
TISErrorComCirc5Code2 | INT | IOD_TIS_TCP | 78 | 40078 | ErrorComCirc[5].Code[2] | BYTE
TISErrorComCirc5Code3 | INT | IOD_TIS_TCP | 79 | 40079 | ErrorComCirc[5].Code[3] | BYTE
TISErrorComCirc5Code4 | INT | IOD_TIS_TCP | 80 | 40080 | ErrorComCirc[5].Code[4] | BYTE
TISErrorComCirc5Code5 | INT | IOD_TIS_TCP | 81 | 40081 | ErrorComCirc[5].Code[5] | BYTE
TISErrorComCirc5Code6 | INT | IOD_TIS_TCP | 82 | 40082 | ErrorComCirc[5].Code[6] | BYTE
TISErrorComCirc5Code7 | INT | IOD_TIS_TCP | 83 | 40083 | ErrorComCirc[5].Code[7] | BYTE
TISErrorComCirc5Code8 | INT | IOD_TIS_TCP | 84 | 40084 | ErrorComCirc[5].Code[8] | BYTE
TISErrorComCirc5Code9 | INT | IOD_TIS_TCP | 85 | 40085 | ErrorComCirc[5].Code[9] | BYTE
TISErrorComCirc5Status | INT | IOD_TIS_TCP | 86 | 40086 | ErrorComCirc[5].Status
TISErrorComKlima1Code10 | INT | IOD_TIS_TCP | 87 | 40087 | ErrorComKlima[1].Code[10] | BYTE
TISErrorComKlima1Code11 | INT | IOD_TIS_TCP | 88 | 40088 | ErrorComKlima[1].Code[11] | BYTE
TISErrorComKlima1Code12 | INT | IOD_TIS_TCP | 89 | 40089 | ErrorComKlima[1].Code[12] | BYTE
TISErrorComKlima1Code13 | INT | IOD_TIS_TCP | 90 | 40090 | ErrorComKlima[1].Code[13] | BYTE
TISErrorComKlima1Code14 | INT | IOD_TIS_TCP | 91 | 40091 | ErrorComKlima[1].Code[14] | BYTE
TISErrorComKlima1Code15 | INT | IOD_TIS_TCP | 92 | 40092 | ErrorComKlima[1].Code[15] | BYTE
TISErrorComKlima1Code1 | INT | IOD_TIS_TCP | 93 | 40093 | ErrorComKlima[1].Code[1] | BYTE
TISErrorComKlima1Code2 | INT | IOD_TIS_TCP | 94 | 40094 | ErrorComKlima[1].Code[2] | BYTE
TISErrorComKlima1Code3 | INT | IOD_TIS_TCP | 95 | 40095 | ErrorComKlima[1].Code[3] | BYTE
TISErrorComKlima1Code4 | INT | IOD_TIS_TCP | 96 | 40096 | ErrorComKlima[1].Code[4] | BYTE
TISErrorComKlima1Code5 | INT | IOD_TIS_TCP | 97 | 40097 | ErrorComKlima[1].Code[5] | BYTE
TISErrorComKlima1Code6 | INT | IOD_TIS_TCP | 98 | 40098 | ErrorComKlima[1].Code[6] | BYTE
TISErrorComKlima1Code7 | INT | IOD_TIS_TCP | 99 | 40099 | ErrorComKlima[1].Code[7] | BYTE
TISErrorComKlima1Code8 | INT | IOD_TIS_TCP | 100 | 40100 | ErrorComKlima[1].Code[8] | BYTE
TISErrorComKlima1Code9 | INT | IOD_TIS_TCP | 101 | 40101 | ErrorComKlima[1].Code[9] | BYTE
TISErrorComKlima1Status | INT | IOD_TIS_TCP | 102 | 40102 | ErrorComKlima[1].Status
TISErrorComKlima2Code10 | INT | IOD_TIS_TCP | 103 | 40103 | ErrorComKlima[2].Code[10] | BYTE
TISErrorComKlima2Code11 | INT | IOD_TIS_TCP | 104 | 40104 | ErrorComKlima[2].Code[11] | BYTE
TISErrorComKlima2Code12 | INT | IOD_TIS_TCP | 105 | 40105 | ErrorComKlima[2].Code[12] | BYTE
TISErrorComKlima2Code13 | INT | IOD_TIS_TCP | 106 | 40106 | ErrorComKlima[2].Code[13] | BYTE
TISErrorComKlima2Code14 | INT | IOD_TIS_TCP | 107 | 40107 | ErrorComKlima[2].Code[14] | BYTE
TISErrorComKlima2Code15 | INT | IOD_TIS_TCP | 108 | 40108 | ErrorComKlima[2].Code[15] | BYTE
TISErrorComKlima2Code1 | INT | IOD_TIS_TCP | 109 | 40109 | ErrorComKlima[2].Code[1] | BYTE
TISErrorComKlima2Code2 | INT | IOD_TIS_TCP | 110 | 40110 | ErrorComKlima[2].Code[2] | BYTE
TISErrorComKlima2Code3 | INT | IOD_TIS_TCP | 111 | 40111 | ErrorComKlima[2].Code[3] | BYTE
TISErrorComKlima2Code4 | INT | IOD_TIS_TCP | 112 | 40112 | ErrorComKlima[2].Code[4] | BYTE
TISErrorComKlima2Code5 | INT | IOD_TIS_TCP | 113 | 40113 | ErrorComKlima[2].Code[5] | BYTE
TISErrorComKlima2Code6 | INT | IOD_TIS_TCP | 114 | 40114 | ErrorComKlima[2].Code[6] | BYTE
TISErrorComKlima2Code7 | INT | IOD_TIS_TCP | 115 | 40115 | ErrorComKlima[2].Code[7] | BYTE
TISErrorComKlima2Code8 | INT | IOD_TIS_TCP | 116 | 40116 | ErrorComKlima[2].Code[8] | BYTE
TISErrorComKlima2Code9 | INT | IOD_TIS_TCP | 117 | 40117 | ErrorComKlima[2].Code[9] | BYTE
TISErrorComKlima2Status | INT | IOD_TIS_TCP | 118 | 40118 | ErrorComKlima[2].Status
TISErrorComKlima3Code10 | INT | IOD_TIS_TCP | 119 | 40119 | ErrorComKlima[3].Code[10] | BYTE
TISErrorComKlima3Code11 | INT | IOD_TIS_TCP | 120 | 40120 | ErrorComKlima[3].Code[11] | BYTE
TISErrorComKlima3Code12 | INT | IOD_TIS_TCP | 121 | 40121 | ErrorComKlima[3].Code[12] | BYTE
TISErrorComKlima3Code13 | INT | IOD_TIS_TCP | 122 | 40122 | ErrorComKlima[3].Code[13] | BYTE
TISErrorComKlima3Code14 | INT | IOD_TIS_TCP | 123 | 40123 | ErrorComKlima[3].Code[14] | BYTE
TISErrorComKlima3Code15 | INT | IOD_TIS_TCP | 124 | 40124 | ErrorComKlima[3].Code[15] | BYTE
TISErrorComKlima3Code1 | INT | IOD_TIS_TCP | 125 | 40125 | ErrorComKlima[3].Code[1] | BYTE
TISErrorComKlima3Code2 | INT | IOD_TIS_TCP | 126 | 40126 | ErrorComKlima[3].Code[2] | BYTE
TISErrorComKlima3Code3 | INT | IOD_TIS_TCP | 127 | 40127 | ErrorComKlima[3].Code[3] | BYTE
TISErrorComKlima3Code4 | INT | IOD_TIS_TCP | 128 | 40128 | ErrorComKlima[3].Code[4] | BYTE
TISErrorComKlima3Code5 | INT | IOD_TIS_TCP | 129 | 40129 | ErrorComKlima[3].Code[5] | BYTE
TISErrorComKlima3Code6 | INT | IOD_TIS_TCP | 130 | 40130 | ErrorComKlima[3].Code[6] | BYTE
TISErrorComKlima3Code7 | INT | IOD_TIS_TCP | 131 | 40131 | ErrorComKlima[3].Code[7] | BYTE
TISErrorComKlima3Code8 | INT | IOD_TIS_TCP | 132 | 40132 | ErrorComKlima[3].Code[8] | BYTE
TISErrorComKlima3Code9 | INT | IOD_TIS_TCP | 133 | 40133 | ErrorComKlima[3].Code[9] | BYTE
TISErrorComKlima3Status | INT | IOD_TIS_TCP | 134 | 40134 | ErrorComKlima[3].Status
TISErrorComKlima4Code10 | INT | IOD_TIS_TCP | 135 | 40135 | ErrorComKlima[4].Code[10] | BYTE
TISErrorComKlima4Code11 | INT | IOD_TIS_TCP | 136 | 40136 | ErrorComKlima[4].Code[11] | BYTE
TISErrorComKlima4Code12 | INT | IOD_TIS_TCP | 137 | 40137 | ErrorComKlima[4].Code[12] | BYTE
TISErrorComKlima4Code13 | INT | IOD_TIS_TCP | 138 | 40138 | ErrorComKlima[4].Code[13] | BYTE
TISErrorComKlima4Code14 | INT | IOD_TIS_TCP | 139 | 40139 | ErrorComKlima[4].Code[14] | BYTE
TISErrorComKlima4Code15 | INT | IOD_TIS_TCP | 140 | 40140 | ErrorComKlima[4].Code[15] | BYTE
TISErrorComKlima4Code1 | INT | IOD_TIS_TCP | 141 | 40141 | ErrorComKlima[4].Code[1] | BYTE
TISErrorComKlima4Code2 | INT | IOD_TIS_TCP | 142 | 40142 | ErrorComKlima[4].Code[2] | BYTE
TISErrorComKlima4Code3 | INT | IOD_TIS_TCP | 143 | 40143 | ErrorComKlima[4].Code[3] | BYTE
TISErrorComKlima4Code4 | INT | IOD_TIS_TCP | 144 | 40144 | ErrorComKlima[4].Code[4] | BYTE
TISErrorComKlima4Code5 | INT | IOD_TIS_TCP | 145 | 40145 | ErrorComKlima[4].Code[5] | BYTE
TISErrorComKlima4Code6 | INT | IOD_TIS_TCP | 146 | 40146 | ErrorComKlima[4].Code[6] | BYTE
TISErrorComKlima4Code7 | INT | IOD_TIS_TCP | 147 | 40147 | ErrorComKlima[4].Code[7] | BYTE
TISErrorComKlima4Code8 | INT | IOD_TIS_TCP | 148 | 40148 | ErrorComKlima[4].Code[8] | BYTE
TISErrorComKlima4Code9 | INT | IOD_TIS_TCP | 149 | 40149 | ErrorComKlima[4].Code[9] | BYTE
TISErrorComKlima4Status | INT | IOD_TIS_TCP | 150 | 40150 | ErrorComKlima[4].Status
TISErrorComKlima5Code10 | INT | IOD_TIS_TCP | 151 | 40151 | ErrorComKlima[5].Code[10] | BYTE
TISErrorComKlima5Code11 | INT | IOD_TIS_TCP | 152 | 40152 | ErrorComKlima[5].Code[11] | BYTE
TISErrorComKlima5Code12 | INT | IOD_TIS_TCP | 153 | 40153 | ErrorComKlima[5].Code[12] | BYTE
TISErrorComKlima5Code13 | INT | IOD_TIS_TCP | 154 | 40154 | ErrorComKlima[5].Code[13] | BYTE
TISErrorComKlima5Code14 | INT | IOD_TIS_TCP | 155 | 40155 | ErrorComKlima[5].Code[14] | BYTE
TISErrorComKlima5Code15 | INT | IOD_TIS_TCP | 156 | 40156 | ErrorComKlima[5].Code[15] | BYTE
TISErrorComKlima5Code1 | INT | IOD_TIS_TCP | 157 | 40157 | ErrorComKlima[5].Code[1] | BYTE
TISErrorComKlima5Code2 | INT | IOD_TIS_TCP | 158 | 40158 | ErrorComKlima[5].Code[2] | BYTE
TISErrorComKlima5Code3 | INT | IOD_TIS_TCP | 159 | 40159 | ErrorComKlima[5].Code[3] | BYTE
TISErrorComKlima5Code4 | INT | IOD_TIS_TCP | 160 | 40160 | ErrorComKlima[5].Code[4] | BYTE
TISErrorComKlima5Code5 | INT | IOD_TIS_TCP | 161 | 40161 | ErrorComKlima[5].Code[5] | BYTE
TISErrorComKlima5Code6 | INT | IOD_TIS_TCP | 162 | 40162 | ErrorComKlima[5].Code[6] | BYTE
TISErrorComKlima5Code7 | INT | IOD_TIS_TCP | 163 | 40163 | ErrorComKlima[5].Code[7] | BYTE
TISErrorComKlima5Code8 | INT | IOD_TIS_TCP | 164 | 40164 | ErrorComKlima[5].Code[8] | BYTE
TISErrorComKlima5Code9 | INT | IOD_TIS_TCP | 165 | 40165 | ErrorComKlima[5].Code[9] | BYTE
TISErrorComKlima5Status | INT | IOD_TIS_TCP | 166 | 40166 | ErrorComKlima[5].Status
TISErrorComKlima6Code10 | INT | IOD_TIS_TCP | 167 | 40167 | ErrorComKlima[6].Code[10] | BYTE
TISErrorComKlima6Code11 | INT | IOD_TIS_TCP | 168 | 40168 | ErrorComKlima[6].Code[11] | BYTE
TISErrorComKlima6Code12 | INT | IOD_TIS_TCP | 169 | 40169 | ErrorComKlima[6].Code[12] | BYTE
TISErrorComKlima6Code13 | INT | IOD_TIS_TCP | 170 | 40170 | ErrorComKlima[6].Code[13] | BYTE
TISErrorComKlima6Code14 | INT | IOD_TIS_TCP | 171 | 40171 | ErrorComKlima[6].Code[14] | BYTE
TISErrorComKlima6Code15 | INT | IOD_TIS_TCP | 172 | 40172 | ErrorComKlima[6].Code[15] | BYTE
TISErrorComKlima6Code1 | INT | IOD_TIS_TCP | 173 | 40173 | ErrorComKlima[6].Code[1] | BYTE
TISErrorComKlima6Code2 | INT | IOD_TIS_TCP | 174 | 40174 | ErrorComKlima[6].Code[2] | BYTE
TISErrorComKlima6Code3 | INT | IOD_TIS_TCP | 175 | 40175 | ErrorComKlima[6].Code[3] | BYTE
TISErrorComKlima6Code4 | INT | IOD_TIS_TCP | 176 | 40176 | ErrorComKlima[6].Code[4] | BYTE
TISErrorComKlima6Code5 | INT | IOD_TIS_TCP | 177 | 40177 | ErrorComKlima[6].Code[5] | BYTE
TISErrorComKlima6Code6 | INT | IOD_TIS_TCP | 178 | 40178 | ErrorComKlima[6].Code[6] | BYTE
TISErrorComKlima6Code7 | INT | IOD_TIS_TCP | 179 | 40179 | ErrorComKlima[6].Code[7] | BYTE
TISErrorComKlima6Code8 | INT | IOD_TIS_TCP | 180 | 40180 | ErrorComKlima[6].Code[8] | BYTE
TISErrorComKlima6Code9 | INT | IOD_TIS_TCP | 181 | 40181 | ErrorComKlima[6].Code[9] | BYTE
TISErrorComKlima6Status | INT | IOD_TIS_TCP | 182 | 40182 | ErrorComKlima[6].Status
TISKlima1GrelecStatus | INT | IOD_TIS_TCP | 183 | 40183 | Klima[1].GrelecStatus | BYTE
TISKlima1IzhodniVentStatus | INT | IOD_TIS_TCP | 184 | 40184 | Klima[1].IzhodniVentStatus | BYTE
TISKlima1KompresorStatus | INT | IOD_TIS_TCP | 185 | 40185 | Klima[1].KompresorStatus | BYTE
TISKlima1VlazilecStatus | INT | IOD_TIS_TCP | 186 | 40186 | Klima[1].VlazilecStatus | BYTE
TISKlima2GrelecStatus | INT | IOD_TIS_TCP | 187 | 40187 | Klima[2].GrelecStatus | BYTE
TISKlima2IzhodniVentStatus | INT | IOD_TIS_TCP | 188 | 40188 | Klima[2].IzhodniVentStatus | BYTE
TISKlima2KompresorStatus | INT | IOD_TIS_TCP | 189 | 40189 | Klima[2].KompresorStatus | BYTE
TISKlima2VlazilecStatus | INT | IOD_TIS_TCP | 190 | 40190 | Klima[2].VlazilecStatus | BYTE
TISKlima3GrelecStatus | INT | IOD_TIS_TCP | 191 | 40191 | Klima[3].GrelecStatus | BYTE
TISKlima3IzhodniVentStatus | INT | IOD_TIS_TCP | 192 | 40192 | Klima[3].IzhodniVentStatus | BYTE
TISKlima3KompresorStatus | INT | IOD_TIS_TCP | 193 | 40193 | Klima[3].KompresorStatus | BYTE
TISKlima3VlazilecStatus | INT | IOD_TIS_TCP | 194 | 40194 | Klima[3].VlazilecStatus | BYTE
TISKlimaGalGrelecStatus | INT | IOD_TIS_TCP | 195 | 40195 | KlimaGal.GrelecStatus | BYTE
TISKlimaGalIzhodniVentStatus | INT | IOD_TIS_TCP | 196 | 40196 | KlimaGal.IzhodniVentStatus | BYTE
TISKlimaGalKompresorStatus | INT | IOD_TIS_TCP | 197 | 40197 | KlimaGal.KompresorStatus | BYTE
TISKlimaGalVlazilecStatus | INT | IOD_TIS_TCP | 198 | 40198 | KlimaGal.VlazilecStatus | BYTE
TISQstanje10 | INT | IOD_TIS_TCP | 199 | 40199 | Qstanje[10] | BYTE
TISQstanje1 | INT | IOD_TIS_TCP | 200 | 40200 | Qstanje[1] | BYTE
TISQstanje2 | INT | IOD_TIS_TCP | 201 | 40201 | Qstanje[2] | BYTE
TISQstanje3 | INT | IOD_TIS_TCP | 202 | 40202 | Qstanje[3] | BYTE
TISQstanje4 | INT | IOD_TIS_TCP | 203 | 40203 | Qstanje[4] | BYTE
TISQstanje5 | INT | IOD_TIS_TCP | 204 | 40204 | Qstanje[5] | BYTE
TISQstanje6 | INT | IOD_TIS_TCP | 205 | 40205 | Qstanje[6] | BYTE
TISQstanje7 | INT | IOD_TIS_TCP | 206 | 40206 | Qstanje[7] | BYTE
TISQstanje8 | INT | IOD_TIS_TCP | 207 | 40207 | Qstanje[8] | BYTE
TISQstanje9 | INT | IOD_TIS_TCP | 208 | 40208 | Qstanje[9] | BYTE
TISUserCurrentLevel | INT | IOD_TIS_TCP | 209 | 40209 | UserCurrentLevel | BYTE
TISXVH_CircNumber | INT | IOD_TIS_TCP | 210 | 40210 | XVH_CircNumber | BYTE
TISXVH_KlimaNumber | INT | IOD_TIS_TCP | 211 | 40211 | XVH_KlimaNumber | BYTE
TISXVH_PripravaVodeStat1 | INT | IOD_TIS_TCP | 212 | 40212 | XVH_PripravaVodeStat[1] | BYTE
TISXVH_PripravaVodeStat2 | INT | IOD_TIS_TCP | 213 | 40213 | XVH_PripravaVodeStat[2] | BYTE
TISXVH_UPSstatus | INT | IOD_TIS_TCP | 214 | 40214 | XVH_UPSstatus | BYTE
TISXVH_VlazilecStatus1 | INT | IOD_TIS_TCP | 215 | 40215 | XVH_VlazilecStatus[1] | BYTE
TISXVH_VlazilecStatus2 | INT | IOD_TIS_TCP | 216 | 40216 | XVH_VlazilecStatus[2] | BYTE
TISXVH_VlazilecStatus3 | INT | IOD_TIS_TCP | 217 | 40217 | XVH_VlazilecStatus[3] | BYTE
TISXVHnum10 | INT | IOD_TIS_TCP | 218 | 40218 | XVHnum[10] | BYTE
TISXVHnum11 | INT | IOD_TIS_TCP | 219 | 40219 | XVHnum[11] | BYTE
TISXVHnum12 | INT | IOD_TIS_TCP | 220 | 40220 | XVHnum[12] | BYTE
TISXVHnum13 | INT | IOD_TIS_TCP | 221 | 40221 | XVHnum[13] | BYTE
TISXVHnum14 | INT | IOD_TIS_TCP | 222 | 40222 | XVHnum[14] | BYTE
TISXVHnum1 | INT | IOD_TIS_TCP | 223 | 40223 | XVHnum[1] | BYTE
TISXVHnum2 | INT | IOD_TIS_TCP | 224 | 40224 | XVHnum[2] | BYTE
TISXVHnum3 | INT | IOD_TIS_TCP | 225 | 40225 | XVHnum[3] | BYTE
TISXVHnum4 | INT | IOD_TIS_TCP | 226 | 40226 | XVHnum[4] | BYTE
TISXVHnum5 | INT | IOD_TIS_TCP | 227 | 40227 | XVHnum[5] | BYTE
TISXVHnum6 | INT | IOD_TIS_TCP | 228 | 40228 | XVHnum[6] | BYTE
TISXVHnum7 | INT | IOD_TIS_TCP | 229 | 40229 | XVHnum[7] | BYTE
TISXVHnum8 | INT | IOD_TIS_TCP | 230 | 40230 | XVHnum[8] | BYTE
TISXVHnum9 | INT | IOD_TIS_TCP | 231 | 40231 | XVHnum[9] | BYTE
TISkom_nast_cas_izpada | INT | IOD_TIS_TCP | 232 | 40232 | kom_nast_cas_izpada
TISCirc1CosFi_III | REAL | IOD_TIS_TCP | 4001 | 44001 | Circ[1].CosFi_III
TISCirc1DelovnaEnergija | REAL | IOD_TIS_TCP | 4003 | 44003 | Circ[1].DelovnaEnergija
TISCirc1DelovnaMoc_III | REAL | IOD_TIS_TCP | 4005 | 44005 | Circ[1].DelovnaMoc_III
TISCirc1DelovnaMoc_L1 | REAL | IOD_TIS_TCP | 4007 | 44007 | Circ[1].DelovnaMoc_L1
TISCirc1DelovnaMoc_L2 | REAL | IOD_TIS_TCP | 4009 | 44009 | Circ[1].DelovnaMoc_L2
TISCirc1DelovnaMoc_L3 | REAL | IOD_TIS_TCP | 4011 | 44011 | Circ[1].DelovnaMoc_L3
TISCirc1Frekvenca_L1 | REAL | IOD_TIS_TCP | 4013 | 44013 | Circ[1].Frekvenca_L1
TISCirc1InduktivnaEnergija | REAL | IOD_TIS_TCP | 4015 | 44015 | Circ[1].InduktivnaEnergija
TISCirc1InduktivnaMoc_III | REAL | IOD_TIS_TCP | 4017 | 44017 | Circ[1].InduktivnaMoc_III
TISCirc1JalovaMoc_L1 | REAL | IOD_TIS_TCP | 4019 | 44019 | Circ[1].JalovaMoc_L1
TISCirc1JalovaMoc_L2 | REAL | IOD_TIS_TCP | 4021 | 44021 | Circ[1].JalovaMoc_L2
TISCirc1JalovaMoc_L3 | REAL | IOD_TIS_TCP | 4023 | 44023 | Circ[1].JalovaMoc_L3
TISCirc1KapacitivnaEnergija | REAL | IOD_TIS_TCP | 4025 | 44025 | Circ[1].KapacitivnaEnergija
TISCirc1KapacitivnaMoc_III | REAL | IOD_TIS_TCP | 4027 | 44027 | Circ[1].KapacitivnaMoc_III
TISCirc1MaximumDemand | REAL | IOD_TIS_TCP | 4029 | 44029 | Circ[1].MaximumDemand
TISCirc1Napetost_L1_L2 | REAL | IOD_TIS_TCP | 4031 | 44031 | Circ[1].Napetost_L1_L2
TISCirc1Napetost_L1_N | REAL | IOD_TIS_TCP | 4033 | 44033 | Circ[1].Napetost_L1_N
TISCirc1Napetost_L2_L3 | REAL | IOD_TIS_TCP | 4035 | 44035 | Circ[1].Napetost_L2_L3
TISCirc1Napetost_L2_N | REAL | IOD_TIS_TCP | 4037 | 44037 | Circ[1].Napetost_L2_N
TISCirc1Napetost_L3_L1 | REAL | IOD_TIS_TCP | 4039 | 44039 | Circ[1].Napetost_L3_L1
TISCirc1Napetost_L3_N | REAL | IOD_TIS_TCP | 4041 | 44041 | Circ[1].Napetost_L3_N
TISCirc1NavideznaMoc_III | REAL | IOD_TIS_TCP | 4043 | 44043 | Circ[1].NavideznaMoc_III
TISCirc1NicelniTok | REAL | IOD_TIS_TCP | 4045 | 44045 | Circ[1].NicelniTok
TISCirc1PowerFactor_III | REAL | IOD_TIS_TCP | 4047 | 44047 | Circ[1].PowerFactor_III
TISCirc1PowerFactor_L1 | REAL | IOD_TIS_TCP | 4049 | 44049 | Circ[1].PowerFactor_L1
TISCirc1PowerFactor_L2 | REAL | IOD_TIS_TCP | 4051 | 44051 | Circ[1].PowerFactor_L2
TISCirc1PowerFactor_L3 | REAL | IOD_TIS_TCP | 4053 | 44053 | Circ[1].PowerFactor_L3
TISCirc1THDI_L1 | REAL | IOD_TIS_TCP | 4055 | 44055 | Circ[1].THDI_L1
TISCirc1THDI_L2 | REAL | IOD_TIS_TCP | 4057 | 44057 | Circ[1].THDI_L2
TISCirc1THDI_L3 | REAL | IOD_TIS_TCP | 4059 | 44059 | Circ[1].THDI_L3
TISCirc1THDV_L1 | REAL | IOD_TIS_TCP | 4061 | 44061 | Circ[1].THDV_L1
TISCirc1THDV_L2 | REAL | IOD_TIS_TCP | 4063 | 44063 | Circ[1].THDV_L2
TISCirc1THDV_L3 | REAL | IOD_TIS_TCP | 4065 | 44065 | Circ[1].THDV_L3
TISCirc1Tok_L1 | REAL | IOD_TIS_TCP | 4067 | 44067 | Circ[1].Tok_L1
TISCirc1Tok_L2 | REAL | IOD_TIS_TCP | 4069 | 44069 | Circ[1].Tok_L2
TISCirc1Tok_L3 | REAL | IOD_TIS_TCP | 4071 | 44071 | Circ[1].Tok_L3
TISCirc1TokPovprecje_III | REAL | IOD_TIS_TCP | 4073 | 44073 | Circ[1].TokPovprecje_III
TISCirc2CosFi_III | REAL | IOD_TIS_TCP | 4075 | 44075 | Circ[2].CosFi_III
TISCirc2DelovnaEnergija | REAL | IOD_TIS_TCP | 4077 | 44077 | Circ[2].DelovnaEnergija
TISCirc2DelovnaMoc_III | REAL | IOD_TIS_TCP | 4079 | 44079 | Circ[2].DelovnaMoc_III
TISCirc2DelovnaMoc_L1 | REAL | IOD_TIS_TCP | 4081 | 44081 | Circ[2].DelovnaMoc_L1
TISCirc2DelovnaMoc_L2 | REAL | IOD_TIS_TCP | 4083 | 44083 | Circ[2].DelovnaMoc_L2
TISCirc2DelovnaMoc_L3 | REAL | IOD_TIS_TCP | 4085 | 44085 | Circ[2].DelovnaMoc_L3
TISCirc2Frekvenca_L1 | REAL | IOD_TIS_TCP | 4087 | 44087 | Circ[2].Frekvenca_L1
TISCirc2InduktivnaEnergija | REAL | IOD_TIS_TCP | 4089 | 44089 | Circ[2].InduktivnaEnergija
TISCirc2InduktivnaMoc_III | REAL | IOD_TIS_TCP | 4091 | 44091 | Circ[2].InduktivnaMoc_III
TISCirc2JalovaMoc_L1 | REAL | IOD_TIS_TCP | 4093 | 44093 | Circ[2].JalovaMoc_L1
TISCirc2JalovaMoc_L2 | REAL | IOD_TIS_TCP | 4095 | 44095 | Circ[2].JalovaMoc_L2
TISCirc2JalovaMoc_L3 | REAL | IOD_TIS_TCP | 4097 | 44097 | Circ[2].JalovaMoc_L3
TISCirc2KapacitivnaEnergija | REAL | IOD_TIS_TCP | 4099 | 44099 | Circ[2].KapacitivnaEnergija
TISCirc2KapacitivnaMoc_III | REAL | IOD_TIS_TCP | 4101 | 44101 | Circ[2].KapacitivnaMoc_III
TISCirc2MaximumDemand | REAL | IOD_TIS_TCP | 4103 | 44103 | Circ[2].MaximumDemand
TISCirc2Napetost_L1_L2 | REAL | IOD_TIS_TCP | 4105 | 44105 | Circ[2].Napetost_L1_L2
TISCirc2Napetost_L1_N | REAL | IOD_TIS_TCP | 4107 | 44107 | Circ[2].Napetost_L1_N
TISCirc2Napetost_L2_L3 | REAL | IOD_TIS_TCP | 4109 | 44109 | Circ[2].Napetost_L2_L3
TISCirc2Napetost_L2_N | REAL | IOD_TIS_TCP | 4111 | 44111 | Circ[2].Napetost_L2_N
TISCirc2Napetost_L3_L1 | REAL | IOD_TIS_TCP | 4113 | 44113 | Circ[2].Napetost_L3_L1
TISCirc2Napetost_L3_N | REAL | IOD_TIS_TCP | 4115 | 44115 | Circ[2].Napetost_L3_N
TISCirc2NavideznaMoc_III | REAL | IOD_TIS_TCP | 4117 | 44117 | Circ[2].NavideznaMoc_III
TISCirc2NicelniTok | REAL | IOD_TIS_TCP | 4119 | 44119 | Circ[2].NicelniTok
TISCirc2PowerFactor_III | REAL | IOD_TIS_TCP | 4121 | 44121 | Circ[2].PowerFactor_III
TISCirc2PowerFactor_L1 | REAL | IOD_TIS_TCP | 4123 | 44123 | Circ[2].PowerFactor_L1
TISCirc2PowerFactor_L2 | REAL | IOD_TIS_TCP | 4125 | 44125 | Circ[2].PowerFactor_L2
TISCirc2PowerFactor_L3 | REAL | IOD_TIS_TCP | 4127 | 44127 | Circ[2].PowerFactor_L3
TISCirc2THDI_L1 | REAL | IOD_TIS_TCP | 4129 | 44129 | Circ[2].THDI_L1
TISCirc2THDI_L2 | REAL | IOD_TIS_TCP | 4131 | 44131 | Circ[2].THDI_L2
TISCirc2THDI_L3 | REAL | IOD_TIS_TCP | 4133 | 44133 | Circ[2].THDI_L3
TISCirc2THDV_L1 | REAL | IOD_TIS_TCP | 4135 | 44135 | Circ[2].THDV_L1
TISCirc2THDV_L2 | REAL | IOD_TIS_TCP | 4137 | 44137 | Circ[2].THDV_L2
TISCirc2THDV_L3 | REAL | IOD_TIS_TCP | 4139 | 44139 | Circ[2].THDV_L3
TISCirc2Tok_L1 | REAL | IOD_TIS_TCP | 4141 | 44141 | Circ[2].Tok_L1
TISCirc2Tok_L2 | REAL | IOD_TIS_TCP | 4143 | 44143 | Circ[2].Tok_L2
TISCirc2Tok_L3 | REAL | IOD_TIS_TCP | 4145 | 44145 | Circ[2].Tok_L3
TISCirc2TokPovprecje_III | REAL | IOD_TIS_TCP | 4147 | 44147 | Circ[2].TokPovprecje_III
TISCirc3CosFi_III | REAL | IOD_TIS_TCP | 4149 | 44149 | Circ[3].CosFi_III
TISCirc3DelovnaEnergija | REAL | IOD_TIS_TCP | 4151 | 44151 | Circ[3].DelovnaEnergija
TISCirc3DelovnaMoc_III | REAL | IOD_TIS_TCP | 4153 | 44153 | Circ[3].DelovnaMoc_III
TISCirc3DelovnaMoc_L1 | REAL | IOD_TIS_TCP | 4155 | 44155 | Circ[3].DelovnaMoc_L1
TISCirc3DelovnaMoc_L2 | REAL | IOD_TIS_TCP | 4157 | 44157 | Circ[3].DelovnaMoc_L2
TISCirc3DelovnaMoc_L3 | REAL | IOD_TIS_TCP | 4159 | 44159 | Circ[3].DelovnaMoc_L3
TISCirc3Frekvenca_L1 | REAL | IOD_TIS_TCP | 4161 | 44161 | Circ[3].Frekvenca_L1
TISCirc3InduktivnaEnergija | REAL | IOD_TIS_TCP | 4163 | 44163 | Circ[3].InduktivnaEnergija
TISCirc3InduktivnaMoc_III | REAL | IOD_TIS_TCP | 4165 | 44165 | Circ[3].InduktivnaMoc_III
TISCirc3JalovaMoc_L1 | REAL | IOD_TIS_TCP | 4167 | 44167 | Circ[3].JalovaMoc_L1
TISCirc3JalovaMoc_L2 | REAL | IOD_TIS_TCP | 4169 | 44169 | Circ[3].JalovaMoc_L2
TISCirc3JalovaMoc_L3 | REAL | IOD_TIS_TCP | 4171 | 44171 | Circ[3].JalovaMoc_L3
TISCirc3KapacitivnaEnergija | REAL | IOD_TIS_TCP | 4173 | 44173 | Circ[3].KapacitivnaEnergija
TISCirc3KapacitivnaMoc_III | REAL | IOD_TIS_TCP | 4175 | 44175 | Circ[3].KapacitivnaMoc_III
TISCirc3MaximumDemand | REAL | IOD_TIS_TCP | 4177 | 44177 | Circ[3].MaximumDemand
TISCirc3Napetost_L1_L2 | REAL | IOD_TIS_TCP | 4179 | 44179 | Circ[3].Napetost_L1_L2
TISCirc3Napetost_L1_N | REAL | IOD_TIS_TCP | 4181 | 44181 | Circ[3].Napetost_L1_N
TISCirc3Napetost_L2_L3 | REAL | IOD_TIS_TCP | 4183 | 44183 | Circ[3].Napetost_L2_L3
TISCirc3Napetost_L2_N | REAL | IOD_TIS_TCP | 4185 | 44185 | Circ[3].Napetost_L2_N
TISCirc3Napetost_L3_L1 | REAL | IOD_TIS_TCP | 4187 | 44187 | Circ[3].Napetost_L3_L1
TISCirc3Napetost_L3_N | REAL | IOD_TIS_TCP | 4189 | 44189 | Circ[3].Napetost_L3_N
TISCirc3NavideznaMoc_III | REAL | IOD_TIS_TCP | 4191 | 44191 | Circ[3].NavideznaMoc_III
TISCirc3NicelniTok | REAL | IOD_TIS_TCP | 4193 | 44193 | Circ[3].NicelniTok
TISCirc3PowerFactor_III | REAL | IOD_TIS_TCP | 4195 | 44195 | Circ[3].PowerFactor_III
TISCirc3PowerFactor_L1 | REAL | IOD_TIS_TCP | 4197 | 44197 | Circ[3].PowerFactor_L1
TISCirc3PowerFactor_L2 | REAL | IOD_TIS_TCP | 4199 | 44199 | Circ[3].PowerFactor_L2
TISCirc3PowerFactor_L3 | REAL | IOD_TIS_TCP | 4201 | 44201 | Circ[3].PowerFactor_L3
TISCirc3THDI_L1 | REAL | IOD_TIS_TCP | 4203 | 44203 | Circ[3].THDI_L1
TISCirc3THDI_L2 | REAL | IOD_TIS_TCP | 4205 | 44205 | Circ[3].THDI_L2
TISCirc3THDI_L3 | REAL | IOD_TIS_TCP | 4207 | 44207 | Circ[3].THDI_L3
TISCirc3THDV_L1 | REAL | IOD_TIS_TCP | 4209 | 44209 | Circ[3].THDV_L1
TISCirc3THDV_L2 | REAL | IOD_TIS_TCP | 4211 | 44211 | Circ[3].THDV_L2
TISCirc3THDV_L3 | REAL | IOD_TIS_TCP | 4213 | 44213 | Circ[3].THDV_L3
TISCirc3Tok_L1 | REAL | IOD_TIS_TCP | 4215 | 44215 | Circ[3].Tok_L1
TISCirc3Tok_L2 | REAL | IOD_TIS_TCP | 4217 | 44217 | Circ[3].Tok_L2
TISCirc3Tok_L3 | REAL | IOD_TIS_TCP | 4219 | 44219 | Circ[3].Tok_L3
TISCirc3TokPovprecje_III | REAL | IOD_TIS_TCP | 4221 | 44221 | Circ[3].TokPovprecje_III
TISCirc4CosFi_III | REAL | IOD_TIS_TCP | 4223 | 44223 | Circ[4].CosFi_III
TISCirc4DelovnaEnergija | REAL | IOD_TIS_TCP | 4225 | 44225 | Circ[4].DelovnaEnergija
TISCirc4DelovnaMoc_III | REAL | IOD_TIS_TCP | 4227 | 44227 | Circ[4].DelovnaMoc_III
TISCirc4DelovnaMoc_L1 | REAL | IOD_TIS_TCP | 4229 | 44229 | Circ[4].DelovnaMoc_L1
TISCirc4DelovnaMoc_L2 | REAL | IOD_TIS_TCP | 4231 | 44231 | Circ[4].DelovnaMoc_L2
TISCirc4DelovnaMoc_L3 | REAL | IOD_TIS_TCP | 4233 | 44233 | Circ[4].DelovnaMoc_L3
TISCirc4Frekvenca_L1 | REAL | IOD_TIS_TCP | 4235 | 44235 | Circ[4].Frekvenca_L1
TISCirc4InduktivnaEnergija | REAL | IOD_TIS_TCP | 4237 | 44237 | Circ[4].InduktivnaEnergija
TISCirc4InduktivnaMoc_III | REAL | IOD_TIS_TCP | 4239 | 44239 | Circ[4].InduktivnaMoc_III
TISCirc4JalovaMoc_L1 | REAL | IOD_TIS_TCP | 4241 | 44241 | Circ[4].JalovaMoc_L1
TISCirc4JalovaMoc_L2 | REAL | IOD_TIS_TCP | 4243 | 44243 | Circ[4].JalovaMoc_L2
TISCirc4JalovaMoc_L3 | REAL | IOD_TIS_TCP | 4245 | 44245 | Circ[4].JalovaMoc_L3
TISCirc4KapacitivnaEnergija | REAL | IOD_TIS_TCP | 4247 | 44247 | Circ[4].KapacitivnaEnergija
TISCirc4KapacitivnaMoc_III | REAL | IOD_TIS_TCP | 4249 | 44249 | Circ[4].KapacitivnaMoc_III
TISCirc4MaximumDemand | REAL | IOD_TIS_TCP | 4251 | 44251 | Circ[4].MaximumDemand
TISCirc4Napetost_L1_L2 | REAL | IOD_TIS_TCP | 4253 | 44253 | Circ[4].Napetost_L1_L2
TISCirc4Napetost_L1_N | REAL | IOD_TIS_TCP | 4255 | 44255 | Circ[4].Napetost_L1_N
TISCirc4Napetost_L2_L3 | REAL | IOD_TIS_TCP | 4257 | 44257 | Circ[4].Napetost_L2_L3
TISCirc4Napetost_L2_N | REAL | IOD_TIS_TCP | 4259 | 44259 | Circ[4].Napetost_L2_N
TISCirc4Napetost_L3_L1 | REAL | IOD_TIS_TCP | 4261 | 44261 | Circ[4].Napetost_L3_L1
TISCirc4Napetost_L3_N | REAL | IOD_TIS_TCP | 4263 | 44263 | Circ[4].Napetost_L3_N
TISCirc4NavideznaMoc_III | REAL | IOD_TIS_TCP | 4265 | 44265 | Circ[4].NavideznaMoc_III
TISCirc4NicelniTok | REAL | IOD_TIS_TCP | 4267 | 44267 | Circ[4].NicelniTok
TISCirc4PowerFactor_III | REAL | IOD_TIS_TCP | 4269 | 44269 | Circ[4].PowerFactor_III
TISCirc4PowerFactor_L1 | REAL | IOD_TIS_TCP | 4271 | 44271 | Circ[4].PowerFactor_L1
TISCirc4PowerFactor_L2 | REAL | IOD_TIS_TCP | 4273 | 44273 | Circ[4].PowerFactor_L2
TISCirc4PowerFactor_L3 | REAL | IOD_TIS_TCP | 4275 | 44275 | Circ[4].PowerFactor_L3
TISCirc4THDI_L1 | REAL | IOD_TIS_TCP | 4277 | 44277 | Circ[4].THDI_L1
TISCirc4THDI_L2 | REAL | IOD_TIS_TCP | 4279 | 44279 | Circ[4].THDI_L2
TISCirc4THDI_L3 | REAL | IOD_TIS_TCP | 4281 | 44281 | Circ[4].THDI_L3
TISCirc4THDV_L1 | REAL | IOD_TIS_TCP | 4283 | 44283 | Circ[4].THDV_L1
TISCirc4THDV_L2 | REAL | IOD_TIS_TCP | 4285 | 44285 | Circ[4].THDV_L2
TISCirc4THDV_L3 | REAL | IOD_TIS_TCP | 4287 | 44287 | Circ[4].THDV_L3
TISCirc4Tok_L1 | REAL | IOD_TIS_TCP | 4289 | 44289 | Circ[4].Tok_L1
TISCirc4Tok_L2 | REAL | IOD_TIS_TCP | 4291 | 44291 | Circ[4].Tok_L2
TISCirc4Tok_L3 | REAL | IOD_TIS_TCP | 4293 | 44293 | Circ[4].Tok_L3
TISCirc4TokPovprecje_III | REAL | IOD_TIS_TCP | 4295 | 44295 | Circ[4].TokPovprecje_III
TISCircutorCosFi_III | REAL | IOD_TIS_TCP | 4297 | 44297 | Circutor.CosFi_III
TISCircutorDelovnaEnergija | REAL | IOD_TIS_TCP | 4299 | 44299 | Circutor.DelovnaEnergija
TISCircutorDelovnaMoc_III | REAL | IOD_TIS_TCP | 4301 | 44301 | Circutor.DelovnaMoc_III
TISCircutorDelovnaMoc_L1 | REAL | IOD_TIS_TCP | 4303 | 44303 | Circutor.DelovnaMoc_L1
TISCircutorDelovnaMoc_L2 | REAL | IOD_TIS_TCP | 4305 | 44305 | Circutor.DelovnaMoc_L2
TISCircutorDelovnaMoc_L3 | REAL | IOD_TIS_TCP | 4307 | 44307 | Circutor.DelovnaMoc_L3
TISCircutorFrekvenca_L1 | REAL | IOD_TIS_TCP | 4309 | 44309 | Circutor.Frekvenca_L1
TISCircutorInduktivnaEnergija | REAL | IOD_TIS_TCP | 4311 | 44311 | Circutor.InduktivnaEnergija
TISCircutorInduktivnaMoc_III | REAL | IOD_TIS_TCP | 4313 | 44313 | Circutor.InduktivnaMoc_III
TISCircutorJalovaMoc_L1 | REAL | IOD_TIS_TCP | 4315 | 44315 | Circutor.JalovaMoc_L1
TISCircutorJalovaMoc_L2 | REAL | IOD_TIS_TCP | 4317 | 44317 | Circutor.JalovaMoc_L2
TISCircutorJalovaMoc_L3 | REAL | IOD_TIS_TCP | 4319 | 44319 | Circutor.JalovaMoc_L3
TISCircutorKapacitivnaEnergija | REAL | IOD_TIS_TCP | 4321 | 44321 | Circutor.KapacitivnaEnergija
TISCircutorKapacitivnaMoc_III | REAL | IOD_TIS_TCP | 4323 | 44323 | Circutor.KapacitivnaMoc_III
TISCircutorMaximumDemand | REAL | IOD_TIS_TCP | 4325 | 44325 | Circutor.MaximumDemand
TISCircutorNapetost_L1_L2 | REAL | IOD_TIS_TCP | 4327 | 44327 | Circutor.Napetost_L1_L2
TISCircutorNapetost_L1_N | REAL | IOD_TIS_TCP | 4329 | 44329 | Circutor.Napetost_L1_N
TISCircutorNapetost_L2_L3 | REAL | IOD_TIS_TCP | 4331 | 44331 | Circutor.Napetost_L2_L3
TISCircutorNapetost_L2_N | REAL | IOD_TIS_TCP | 4333 | 44333 | Circutor.Napetost_L2_N
TISCircutorNapetost_L3_L1 | REAL | IOD_TIS_TCP | 4335 | 44335 | Circutor.Napetost_L3_L1
TISCircutorNapetost_L3_N | REAL | IOD_TIS_TCP | 4337 | 44337 | Circutor.Napetost_L3_N
TISCircutorNavideznaMoc_III | REAL | IOD_TIS_TCP | 4339 | 44339 | Circutor.NavideznaMoc_III
TISCircutorNicelniTok | REAL | IOD_TIS_TCP | 4341 | 44341 | Circutor.NicelniTok
TISCircutorPowerFactor_III | REAL | IOD_TIS_TCP | 4343 | 44343 | Circutor.PowerFactor_III
TISCircutorPowerFactor_L1 | REAL | IOD_TIS_TCP | 4345 | 44345 | Circutor.PowerFactor_L1
TISCircutorPowerFactor_L2 | REAL | IOD_TIS_TCP | 4347 | 44347 | Circutor.PowerFactor_L2
TISCircutorPowerFactor_L3 | REAL | IOD_TIS_TCP | 4349 | 44349 | Circutor.PowerFactor_L3
TISCircutorTHDI_L1 | REAL | IOD_TIS_TCP | 4351 | 44351 | Circutor.THDI_L1
TISCircutorTHDI_L2 | REAL | IOD_TIS_TCP | 4353 | 44353 | Circutor.THDI_L2
TISCircutorTHDI_L3 | REAL | IOD_TIS_TCP | 4355 | 44355 | Circutor.THDI_L3
TISCircutorTHDV_L1 | REAL | IOD_TIS_TCP | 4357 | 44357 | Circutor.THDV_L1
TISCircutorTHDV_L2 | REAL | IOD_TIS_TCP | 4359 | 44359 | Circutor.THDV_L2
TISCircutorTHDV_L3 | REAL | IOD_TIS_TCP | 4361 | 44361 | Circutor.THDV_L3
TISCircutorTok_L1 | REAL | IOD_TIS_TCP | 4363 | 44363 | Circutor.Tok_L1
TISCircutorTok_L2 | REAL | IOD_TIS_TCP | 4365 | 44365 | Circutor.Tok_L2
TISCircutorTok_L3 | REAL | IOD_TIS_TCP | 4367 | 44367 | Circutor.Tok_L3
TISCircutorTokPovprecje_III | REAL | IOD_TIS_TCP | 4369 | 44369 | Circutor.TokPovprecje_III
TISKlima1NastMaxTemp | REAL | IOD_TIS_TCP | 4371 | 44371 | Klima[1].NastMaxTemp
TISKlima1NastMaxVlaznost | REAL | IOD_TIS_TCP | 4373 | 44373 | Klima[1].NastMaxVlaznost
TISKlima1NastMinTemp | REAL | IOD_TIS_TCP | 4375 | 44375 | Klima[1].NastMinTemp
TISKlima1NastMinVlaznost | REAL | IOD_TIS_TCP | 4377 | 44377 | Klima[1].NastMinVlaznost
TISKlima1NastTempProstora | REAL | IOD_TIS_TCP | 4379 | 44379 | Klima[1].NastTempProstora
TISKlima1NastVlaznost | REAL | IOD_TIS_TCP | 4381 | 44381 | Klima[1].NastVlaznost
TISKlima1ObratovalneUre | REAL | IOD_TIS_TCP | 4383 | 44383 | Klima[1].ObratovalneUre
TISKlima1TemperaturaProstora | REAL | IOD_TIS_TCP | 4385 | 44385 | Klima[1].TemperaturaProstora
TISKlima1TempIzpihanegaZraka | REAL | IOD_TIS_TCP | 4387 | 44387 | Klima[1].TempIzpihanegaZraka
TISKlima1TempPovratneVode | REAL | IOD_TIS_TCP | 4389 | 44389 | Klima[1].TempPovratneVode
TISKlima1VlaznostProstora | REAL | IOD_TIS_TCP | 4391 | 44391 | Klima[1].VlaznostProstora
TISKlima1ZunanjaTemp | REAL | IOD_TIS_TCP | 4393 | 44393 | Klima[1].ZunanjaTemp
TISKlima2NastMaxTemp | REAL | IOD_TIS_TCP | 4395 | 44395 | Klima[2].NastMaxTemp
TISKlima2NastMaxVlaznost | REAL | IOD_TIS_TCP | 4397 | 44397 | Klima[2].NastMaxVlaznost
TISKlima2NastMinTemp | REAL | IOD_TIS_TCP | 4399 | 44399 | Klima[2].NastMinTemp
TISKlima2NastMinVlaznost | REAL | IOD_TIS_TCP | 4401 | 44401 | Klima[2].NastMinVlaznost
TISKlima2NastTempProstora | REAL | IOD_TIS_TCP | 4403 | 44403 | Klima[2].NastTempProstora
TISKlima2NastVlaznost | REAL | IOD_TIS_TCP | 4405 | 44405 | Klima[2].NastVlaznost
TISKlima2ObratovalneUre | REAL | IOD_TIS_TCP | 4407 | 44407 | Klima[2].ObratovalneUre
TISKlima2TemperaturaProstora | REAL | IOD_TIS_TCP | 4409 | 44409 | Klima[2].TemperaturaProstora
TISKlima2TempIzpihanegaZraka | REAL | IOD_TIS_TCP | 4411 | 44411 | Klima[2].TempIzpihanegaZraka
TISKlima2TempPovratneVode | REAL | IOD_TIS_TCP | 4413 | 44413 | Klima[2].TempPovratneVode
TISKlima2VlaznostProstora | REAL | IOD_TIS_TCP | 4415 | 44415 | Klima[2].VlaznostProstora
TISKlima2ZunanjaTemp | REAL | IOD_TIS_TCP | 4417 | 44417 | Klima[2].ZunanjaTemp
TISKlima3NastMaxTemp | REAL | IOD_TIS_TCP | 4419 | 44419 | Klima[3].NastMaxTemp
TISKlima3NastMaxVlaznost | REAL | IOD_TIS_TCP | 4421 | 44421 | Klima[3].NastMaxVlaznost
TISKlima3NastMinTemp | REAL | IOD_TIS_TCP | 4423 | 44423 | Klima[3].NastMinTemp
TISKlima3NastMinVlaznost | REAL | IOD_TIS_TCP | 4425 | 44425 | Klima[3].NastMinVlaznost
TISKlima3NastTempProstora | REAL | IOD_TIS_TCP | 4427 | 44427 | Klima[3].NastTempProstora
TISKlima3NastVlaznost | REAL | IOD_TIS_TCP | 4429 | 44429 | Klima[3].NastVlaznost
TISKlima3ObratovalneUre | REAL | IOD_TIS_TCP | 4431 | 44431 | Klima[3].ObratovalneUre
TISKlima3TemperaturaProstora | REAL | IOD_TIS_TCP | 4433 | 44433 | Klima[3].TemperaturaProstora
TISKlima3TempIzpihanegaZraka | REAL | IOD_TIS_TCP | 4435 | 44435 | Klima[3].TempIzpihanegaZraka
TISKlima3TempPovratneVode | REAL | IOD_TIS_TCP | 4437 | 44437 | Klima[3].TempPovratneVode
TISKlima3VlaznostProstora | REAL | IOD_TIS_TCP | 4439 | 44439 | Klima[3].VlaznostProstora
TISKlima3ZunanjaTemp | REAL | IOD_TIS_TCP | 4441 | 44441 | Klima[3].ZunanjaTemp
TISKlimaGalNastMaxTemp | REAL | IOD_TIS_TCP | 4443 | 44443 | KlimaGal.NastMaxTemp
TISKlimaGalNastMaxVlaznost | REAL | IOD_TIS_TCP | 4445 | 44445 | KlimaGal.NastMaxVlaznost
TISKlimaGalNastMinTemp | REAL | IOD_TIS_TCP | 4447 | 44447 | KlimaGal.NastMinTemp
TISKlimaGalNastMinVlaznost | REAL | IOD_TIS_TCP | 4449 | 44449 | KlimaGal.NastMinVlaznost
TISKlimaGalNastTempProstora | REAL | IOD_TIS_TCP | 4451 | 44451 | KlimaGal.NastTempProstora
TISKlimaGalNastVlaznost | REAL | IOD_TIS_TCP | 4453 | 44453 | KlimaGal.NastVlaznost
TISKlimaGalObratovalneUre | REAL | IOD_TIS_TCP | 4455 | 44455 | KlimaGal.ObratovalneUre
TISKlimaGalTemperaturaProstora | REAL | IOD_TIS_TCP | 4457 | 44457 | KlimaGal.TemperaturaProstora
TISKlimaGalTempIzpihanegaZraka | REAL | IOD_TIS_TCP | 4459 | 44459 | KlimaGal.TempIzpihanegaZraka
TISKlimaGalTempPovratneVode | REAL | IOD_TIS_TCP | 4461 | 44461 | KlimaGal.TempPovratneVode
TISKlimaGalVlaznostProstora | REAL | IOD_TIS_TCP | 4463 | 44463 | KlimaGal.VlaznostProstora
TISKlimaGalZunanjaTemp | REAL | IOD_TIS_TCP | 4465 | 44465 | KlimaGal.ZunanjaTemp
TISSenzorTemp10 | REAL | IOD_TIS_TCP | 4467 | 44467 | SenzorTemp[10]
TISSenzorTemp11 | REAL | IOD_TIS_TCP | 4469 | 44469 | SenzorTemp[11]
TISSenzorTemp12 | REAL | IOD_TIS_TCP | 4471 | 44471 | SenzorTemp[12]
TISSenzorTemp13 | REAL | IOD_TIS_TCP | 4473 | 44473 | SenzorTemp[13]
TISSenzorTemp14 | REAL | IOD_TIS_TCP | 4475 | 44475 | SenzorTemp[14]
TISSenzorTemp15 | REAL | IOD_TIS_TCP | 4477 | 44477 | SenzorTemp[15]
TISSenzorTemp16 | REAL | IOD_TIS_TCP | 4479 | 44479 | SenzorTemp[16]
TISSenzorTemp17 | REAL | IOD_TIS_TCP | 4481 | 44481 | SenzorTemp[17]
TISSenzorTemp18 | REAL | IOD_TIS_TCP | 4483 | 44483 | SenzorTemp[18]
TISSenzorTemp19 | REAL | IOD_TIS_TCP | 4485 | 44485 | SenzorTemp[19]
TISSenzorTemp1 | REAL | IOD_TIS_TCP | 4487 | 44487 | SenzorTemp[1]
TISSenzorTemp2 | REAL | IOD_TIS_TCP | 4489 | 44489 | SenzorTemp[2]
TISSenzorTemp3 | REAL | IOD_TIS_TCP | 4491 | 44491 | SenzorTemp[3]
TISSenzorTemp4 | REAL | IOD_TIS_TCP | 4493 | 44493 | SenzorTemp[4]
TISSenzorTemp5 | REAL | IOD_TIS_TCP | 4495 | 44495 | SenzorTemp[5]
TISSenzorTemp6 | REAL | IOD_TIS_TCP | 4497 | 44497 | SenzorTemp[6]
TISSenzorTemp7 | REAL | IOD_TIS_TCP | 4499 | 44499 | SenzorTemp[7]
TISSenzorTemp8 | REAL | IOD_TIS_TCP | 4501 | 44501 | SenzorTemp[8]
TISSenzorTemp9 | REAL | IOD_TIS_TCP | 4503 | 44503 | SenzorTemp[9]
TISSenzorVlaga10 | REAL | IOD_TIS_TCP | 4505 | 44505 | SenzorVlaga[10]
TISSenzorVlaga11 | REAL | IOD_TIS_TCP | 4507 | 44507 | SenzorVlaga[11]
TISSenzorVlaga12 | REAL | IOD_TIS_TCP | 4509 | 44509 | SenzorVlaga[12]
TISSenzorVlaga13 | REAL | IOD_TIS_TCP | 4511 | 44511 | SenzorVlaga[13]
TISSenzorVlaga14 | REAL | IOD_TIS_TCP | 4513 | 44513 | SenzorVlaga[14]
TISSenzorVlaga15 | REAL | IOD_TIS_TCP | 4515 | 44515 | SenzorVlaga[15]
TISSenzorVlaga16 | REAL | IOD_TIS_TCP | 4517 | 44517 | SenzorVlaga[16]
TISSenzorVlaga17 | REAL | IOD_TIS_TCP | 4519 | 44519 | SenzorVlaga[17]
TISSenzorVlaga18 | REAL | IOD_TIS_TCP | 4521 | 44521 | SenzorVlaga[18]
TISSenzorVlaga19 | REAL | IOD_TIS_TCP | 4523 | 44523 | SenzorVlaga[19]
TISSenzorVlaga1 | REAL | IOD_TIS_TCP | 4525 | 44525 | SenzorVlaga[1]
TISSenzorVlaga2 | REAL | IOD_TIS_TCP | 4527 | 44527 | SenzorVlaga[2]
TISSenzorVlaga3 | REAL | IOD_TIS_TCP | 4529 | 44529 | SenzorVlaga[3]
TISSenzorVlaga4 | REAL | IOD_TIS_TCP | 4531 | 44531 | SenzorVlaga[4]
TISSenzorVlaga5 | REAL | IOD_TIS_TCP | 4533 | 44533 | SenzorVlaga[5]
TISSenzorVlaga6 | REAL | IOD_TIS_TCP | 4535 | 44535 | SenzorVlaga[6]
TISSenzorVlaga7 | REAL | IOD_TIS_TCP | 4537 | 44537 | SenzorVlaga[7]
TISSenzorVlaga8 | REAL | IOD_TIS_TCP | 4539 | 44539 | SenzorVlaga[8]
TISSenzorVlaga9 | REAL | IOD_TIS_TCP | 4541 | 44541 | SenzorVlaga[9]
TISTempAlarmPoint1 | REAL | IOD_TIS_TCP | 4543 | 44543 | TempAlarmPoint[1]
TISTempAlarmPoint2 | REAL | IOD_TIS_TCP | 4545 | 44545 | TempAlarmPoint[2]
TISTempAlarmPoint3 | REAL | IOD_TIS_TCP | 4547 | 44547 | TempAlarmPoint[3]
TISTempMaxPoint1 | REAL | IOD_TIS_TCP | 4549 | 44549 | TempMaxPoint[1]
TISTempMaxPoint2 | REAL | IOD_TIS_TCP | 4551 | 44551 | TempMaxPoint[2]
TISTempMaxPoint3 | REAL | IOD_TIS_TCP | 4553 | 44553 | TempMaxPoint[3]
TISTempPovp1 | REAL | IOD_TIS_TCP | 4555 | 44555 | TempPovp[1]
TISTempPovp2 | REAL | IOD_TIS_TCP | 4557 | 44557 | TempPovp[2]
TISTempPovp3 | REAL | IOD_TIS_TCP | 4559 | 44559 | TempPovp[3]
TISTempPovp4 | REAL | IOD_TIS_TCP | 4561 | 44561 | TempPovp[4]
TISTempPovp5 | REAL | IOD_TIS_TCP | 4563 | 44563 | TempPovp[5]
TISTempSetPoint1 | REAL | IOD_TIS_TCP | 4565 | 44565 | TempSetPoint[1]
TISTempSetPoint2 | REAL | IOD_TIS_TCP | 4567 | 44567 | TempSetPoint[2]
TISTempSetPoint3 | REAL | IOD_TIS_TCP | 4569 | 44569 | TempSetPoint[3]
TISVlagaPovp1 | REAL | IOD_TIS_TCP | 4571 | 44571 | VlagaPovp[1]
TISVlagaPovp2 | REAL | IOD_TIS_TCP | 4573 | 44573 | VlagaPovp[2]
TISVlagaPovp3 | REAL | IOD_TIS_TCP | 4575 | 44575 | VlagaPovp[3]
TISVlagaPovp4 | REAL | IOD_TIS_TCP | 4577 | 44577 | VlagaPovp[4]
TISVlagaPovp5 | REAL | IOD_TIS_TCP | 4579 | 44579 | VlagaPovp[5]
TISXVH_GrafTemp1 | REAL | IOD_TIS_TCP | 4581 | 44581 | XVH_GrafTemp[1]
TISXVH_GrafTemp2 | REAL | IOD_TIS_TCP | 4583 | 44583 | XVH_GrafTemp[2]
TISXVH_GrafTemp3 | REAL | IOD_TIS_TCP | 4585 | 44585 | XVH_GrafTemp[3]
TISXVH_GrafTemp4 | REAL | IOD_TIS_TCP | 4587 | 44587 | XVH_GrafTemp[4]
TISXVH_GrafTemp5 | REAL | IOD_TIS_TCP | 4589 | 44589 | XVH_GrafTemp[5]
TISXVH_GrafVlaga1 | REAL | IOD_TIS_TCP | 4591 | 44591 | XVH_GrafVlaga[1]
TISXVH_GrafVlaga2 | REAL | IOD_TIS_TCP | 4593 | 44593 | XVH_GrafVlaga[2]
TISXVH_GrafVlaga3 | REAL | IOD_TIS_TCP | 4595 | 44595 | XVH_GrafVlaga[3]
TISXVH_GrafVlaga4 | REAL | IOD_TIS_TCP | 4597 | 44597 | XVH_GrafVlaga[4]
TISXVH_GrafVlaga5 | REAL | IOD_TIS_TCP | 4599 | 44599 | XVH_GrafVlaga[5]
TISXVH_NastTempProstora1 | REAL | IOD_TIS_TCP | 4601 | 44601 | XVH_NastTempProstora[1]
TISXVH_NastTempProstora2 | REAL | IOD_TIS_TCP | 4603 | 44603 | XVH_NastTempProstora[2]
TISXVH_NastTempProstora3 | REAL | IOD_TIS_TCP | 4605 | 44605 | XVH_NastTempProstora[3]
TISXVH_ObratovalneUre1 | REAL | IOD_TIS_TCP | 4607 | 44607 | XVH_ObratovalneUre[1]
TISXVH_ObratovalneUre2 | REAL | IOD_TIS_TCP | 4609 | 44609 | XVH_ObratovalneUre[2]
TISXVH_ObratovalneUre3 | REAL | IOD_TIS_TCP | 4611 | 44611 | XVH_ObratovalneUre[3]
TISXVHhighHum | REAL | IOD_TIS_TCP | 4613 | 44613 | XVHhighHum
TISXVHhighTemp | REAL | IOD_TIS_TCP | 4615 | 44615 | XVHhighTemp
TISXVHlowHum | REAL | IOD_TIS_TCP | 4617 | 44617 | XVHlowHum
TISXVHlowTemp | REAL | IOD_TIS_TCP | 4619 | 44619 | XVHlowTemp
TISCirc1MaximumDemandA2 | REAL | IOD_TIS_TCP | 4621 | 44621 | Circ[1].MaximumDemandA2
TISCirc1MaximumDemandA3 | REAL | IOD_TIS_TCP | 4623 | 44623 | Circ[1].MaximumDemandA3
TISCirc2MaximumDemandA2 | REAL | IOD_TIS_TCP | 4625 | 44625 | Circ[2].MaximumDemandA2
TISCirc2MaximumDemandA3 | REAL | IOD_TIS_TCP | 4627 | 44627 | Circ[2].MaximumDemandA3
TISCirc3MaximumDemandA2 | REAL | IOD_TIS_TCP | 4629 | 44629 | Circ[3].MaximumDemandA2
TISCirc3MaximumDemandA3 | REAL | IOD_TIS_TCP | 4631 | 44631 | Circ[3].MaximumDemandA3
TISCirc4MaximumDemandA2 | REAL | IOD_TIS_TCP | 4633 | 44633 | Circ[4].MaximumDemandA2
TISCirc4MaximumDemandA3 | REAL | IOD_TIS_TCP | 4635 | 44635 | Circ[4].MaximumDemandA3
TISCirc1RazEner_D_SCADA | REAL | IOD_TIS_TCP | 4637 | 44637 | Circ[1].RazEner_D_SCADA
TISCirc1RazEner_T_SCADA | REAL | IOD_TIS_TCP | 4639 | 44639 | Circ[1].RazEner_T_SCADA
TISCirc1RazEner_M_SCADA | REAL | IOD_TIS_TCP | 4641 | 44641 | Circ[1].RazEner_M_SCADA
TISCirc2RazEner_D_SCADA | REAL | IOD_TIS_TCP | 4643 | 44643 | Circ[2].RazEner_D_SCADA
TISCirc2RazEner_T_SCADA | REAL | IOD_TIS_TCP | 4645 | 44645 | Circ[2].RazEner_T_SCADA
TISCirc2RazEner_M_SCADA | REAL | IOD_TIS_TCP | 4647 | 44647 | Circ[2].RazEner_M_SCADA
TISCirc3RazEner_D_SCADA | REAL | IOD_TIS_TCP | 4649 | 44649 | Circ[3].RazEner_D_SCADA
TISCirc3RazEner_T_SCADA | REAL | IOD_TIS_TCP | 4651 | 44651 | Circ[3].RazEner_T_SCADA
TISCirc3RazEner_M_SCADA | REAL | IOD_TIS_TCP | 4653 | 44653 | Circ[3].RazEner_M_SCADA
TISCirc4RazEner_D_SCADA | REAL | IOD_TIS_TCP | 4655 | 44655 | Circ[4].RazEner_D_SCADA
TISCirc4RazEner_T_SCADA | REAL | IOD_TIS_TCP | 4657 | 44657 | Circ[4].RazEner_T_SCADA
TISCirc4RazEner_M_SCADA | REAL | IOD_TIS_TCP | 4659 | 44659 | Circ[4].RazEner_M_SCADA
TISDate_Time0 | STRING | IOD_TIS_TCP | 5001 | 45001[15] | Date_Time[0]
TISDate_Time1 | STRING | IOD_TIS_TCP | 5016 | 45016[15] | Date_Time[1]
TISDate_Time2 | STRING | IOD_TIS_TCP | 5031 | 45031[15] | Date_Time[2]
TISDate_Time3 | STRING | IOD_TIS_TCP | 5046 | 45046[15] | Date_Time[3]
TISUserCurrentName | STRING | IOD_TIS_TCP | 5061 | 45061[15] | UserCurrentName

## variable_new
TISAlarmGenCirc1 | DIGITAL | IOD_TIS_TCP | 00001
TISAlarmGenCirc2 | DIGITAL | IOD_TIS_TCP | 00002
TISAlarmGenCirc3 | DIGITAL | IOD_TIS_TCP | 00003
TISAlarmGenCirc4 | DIGITAL | IOD_TIS_TCP | 00004
TISAlarmGenComm | DIGITAL | IOD_TIS_TCP | 00005
TISAlarmGenDI | DIGITAL | IOD_TIS_TCP | 00006
TISAlarmGenKlima1 | DIGITAL | IOD_TIS_TCP | 00007
TISAlarmGenKlima2 | DIGITAL | IOD_TIS_TCP | 00008
TISAlarmGenKlima3 | DIGITAL | IOD_TIS_TCP | 00009
TISAlarmGenRest | DIGITAL | IOD_TIS_TCP | 00010
TISAlarmGenSenzor | DIGITAL | IOD_TIS_TCP | 00011
TISAlarmGenTemp | DIGITAL | IOD_TIS_TCP | 00012
TISAlarmGenVlPr | DIGITAL | IOD_TIS_TCP | 00013
TISAlarmGenVTV | DIGITAL | IOD_TIS_TCP | 00014
TISCirc1CosFi_III | REAL | IOD_TIS_TCP | 44001 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc1DelovnaEnergija | REAL | IOD_TIS_TCP | 44003 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc1DelovnaMoc_III | REAL | IOD_TIS_TCP | 44005 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc1DelovnaMoc_L1 | REAL | IOD_TIS_TCP | 44007 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc1DelovnaMoc_L2 | REAL | IOD_TIS_TCP | 44009 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc1DelovnaMoc_L3 | REAL | IOD_TIS_TCP | 44011 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc1Frekvenca_L1 | REAL | IOD_TIS_TCP | 44013 | 0 | 60 | 0 | 60 | Hz | ##.#
TISCirc1InduktivnaEnergija | REAL | IOD_TIS_TCP | 44015 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc1InduktivnaMoc_III | REAL | IOD_TIS_TCP | 44017 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc1JalovaMoc_L1 | REAL | IOD_TIS_TCP | 44019 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc1JalovaMoc_L2 | REAL | IOD_TIS_TCP | 44021 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc1JalovaMoc_L3 | REAL | IOD_TIS_TCP | 44023 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc1KapacitivnaEnergija | REAL | IOD_TIS_TCP | 44025
TISCirc1KapacitivnaMoc_III | REAL | IOD_TIS_TCP | 44027 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc1MaximumDemand | REAL | IOD_TIS_TCP | 44029 | 0 | 1200 | 0 | 1200 | A | ###.#
TISCirc1Napetost_L1_L2 | REAL | IOD_TIS_TCP | 44031 | 0 | 450 | 0 | 450 | V | ###.#
TISCirc1Napetost_L1_N | REAL | IOD_TIS_TCP | 44033 | 0 | 270 | 0 | 270 | V | ###.#
TISCirc1Napetost_L2_L3 | REAL | IOD_TIS_TCP | 44035 | 0 | 450 | 0 | 450 | V | ###.#
TISCirc1Napetost_L2_N | REAL | IOD_TIS_TCP | 44037 | 0 | 270 | 0 | 270 | V | ###.#
TISCirc1Napetost_L3_L1 | REAL | IOD_TIS_TCP | 44039 | 0 | 450 | 0 | 450 | V | ###.#
TISCirc1Napetost_L3_N | REAL | IOD_TIS_TCP | 44041 | 0 | 270 | 0 | 270 | V | ###.#
TISCirc1NavideznaMoc_III | REAL | IOD_TIS_TCP | 44043 | 0 | 1200 | 0 | 1200 | kVA | ###.#
TISCirc1NicelniTok | REAL | IOD_TIS_TCP | 44045 | 0 | 1200 | 0 | 1200 | A | ###.#
TISCirc1PowerFactor_III | REAL | IOD_TIS_TCP | 44047 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc1PowerFactor_L1 | REAL | IOD_TIS_TCP | 44049 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc1PowerFactor_L2 | REAL | IOD_TIS_TCP | 44051 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc1PowerFactor_L3 | REAL | IOD_TIS_TCP | 44053 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc1THDI_L1 | REAL | IOD_TIS_TCP | 44055 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc1THDI_L2 | REAL | IOD_TIS_TCP | 44057 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc1THDI_L3 | REAL | IOD_TIS_TCP | 44059 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc1THDV_L1 | REAL | IOD_TIS_TCP | 44061 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc1THDV_L2 | REAL | IOD_TIS_TCP | 44063 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc1THDV_L3 | REAL | IOD_TIS_TCP | 44065 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc1Tok_L1 | REAL | IOD_TIS_TCP | 44067 | 0 | 600 | 0 | 600 | A | ###.#
TISCirc1Tok_L2 | REAL | IOD_TIS_TCP | 44069 | 0 | 600 | 0 | 600 | A | ###.#
TISCirc1Tok_L3 | REAL | IOD_TIS_TCP | 44071 | 0 | 600 | 0 | 600 | A | ###.#
TISCirc1TokPovprecje_III | REAL | IOD_TIS_TCP | 44073 | 0 | 600 | 0 | 600 | A | ###.#
TISCirc2CosFi_III | REAL | IOD_TIS_TCP | 44075 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc2DelovnaEnergija | REAL | IOD_TIS_TCP | 44077 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc2DelovnaMoc_III | REAL | IOD_TIS_TCP | 44079 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc2DelovnaMoc_L1 | REAL | IOD_TIS_TCP | 44081 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc2DelovnaMoc_L2 | REAL | IOD_TIS_TCP | 44083 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc2DelovnaMoc_L3 | REAL | IOD_TIS_TCP | 44085 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc2Frekvenca_L1 | REAL | IOD_TIS_TCP | 44087 | 0 | 60 | 0 | 60 | Hz | ##.#
TISCirc2InduktivnaEnergija | REAL | IOD_TIS_TCP | 44089 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc2InduktivnaMoc_III | REAL | IOD_TIS_TCP | 44091 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc2JalovaMoc_L1 | REAL | IOD_TIS_TCP | 44093 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc2JalovaMoc_L2 | REAL | IOD_TIS_TCP | 44095 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc2JalovaMoc_L3 | REAL | IOD_TIS_TCP | 44097 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc2KapacitivnaEnergija | REAL | IOD_TIS_TCP | 44099
TISCirc2KapacitivnaMoc_III | REAL | IOD_TIS_TCP | 44101 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc2MaximumDemand | REAL | IOD_TIS_TCP | 44103 | 0 | 1200 | 0 | 1200 | A | ###.#
TISCirc2Napetost_L1_L2 | REAL | IOD_TIS_TCP | 44105 | 0 | 450 | 0 | 450 | V | ###.#
TISCirc2Napetost_L1_N | REAL | IOD_TIS_TCP | 44107 | 0 | 270 | 0 | 270 | V | ###.#
TISCirc2Napetost_L2_L3 | REAL | IOD_TIS_TCP | 44109 | 0 | 450 | 0 | 450 | V | ###.#
TISCirc2Napetost_L2_N | REAL | IOD_TIS_TCP | 44111 | 0 | 270 | 0 | 270 | V | ###.#
TISCirc2Napetost_L3_L1 | REAL | IOD_TIS_TCP | 44113 | 0 | 450 | 0 | 450 | V | ###.#
TISCirc2Napetost_L3_N | REAL | IOD_TIS_TCP | 44115 | 0 | 270 | 0 | 270 | V | ###.#
TISCirc2NavideznaMoc_III | REAL | IOD_TIS_TCP | 44117 | 0 | 1200 | 0 | 1200 | kVA | ###.#
TISCirc2NicelniTok | REAL | IOD_TIS_TCP | 44119 | 0 | 1200 | 0 | 1200 | A | ###.#
TISCirc2PowerFactor_III | REAL | IOD_TIS_TCP | 44121 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc2PowerFactor_L1 | REAL | IOD_TIS_TCP | 44123 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc2PowerFactor_L2 | REAL | IOD_TIS_TCP | 44125 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc2PowerFactor_L3 | REAL | IOD_TIS_TCP | 44127 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc2THDI_L1 | REAL | IOD_TIS_TCP | 44129 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc2THDI_L2 | REAL | IOD_TIS_TCP | 44131 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc2THDI_L3 | REAL | IOD_TIS_TCP | 44133 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc2THDV_L1 | REAL | IOD_TIS_TCP | 44135 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc2THDV_L2 | REAL | IOD_TIS_TCP | 44137 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc2THDV_L3 | REAL | IOD_TIS_TCP | 44139 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc2Tok_L1 | REAL | IOD_TIS_TCP | 44141 | 0 | 600 | 0 | 600 | A | ###.#
TISCirc2Tok_L2 | REAL | IOD_TIS_TCP | 44143 | 0 | 600 | 0 | 600 | A | ###.#
TISCirc2Tok_L3 | REAL | IOD_TIS_TCP | 44145 | 0 | 600 | 0 | 600 | A | ###.#
TISCirc2TokPovprecje_III | REAL | IOD_TIS_TCP | 44147 | 0 | 600 | 0 | 600 | A | ###.#
TISCirc3CosFi_III | REAL | IOD_TIS_TCP | 44149 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc3DelovnaEnergija | REAL | IOD_TIS_TCP | 44151 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc3DelovnaMoc_III | REAL | IOD_TIS_TCP | 44153 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc3DelovnaMoc_L1 | REAL | IOD_TIS_TCP | 44155 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc3DelovnaMoc_L2 | REAL | IOD_TIS_TCP | 44157 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc3DelovnaMoc_L3 | REAL | IOD_TIS_TCP | 44159 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc3Frekvenca_L1 | REAL | IOD_TIS_TCP | 44161 | 0 | 60 | 0 | 60 | Hz | ##.#
TISCirc3InduktivnaEnergija | REAL | IOD_TIS_TCP | 44163 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc3InduktivnaMoc_III | REAL | IOD_TIS_TCP | 44165 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc3JalovaMoc_L1 | REAL | IOD_TIS_TCP | 44167 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc3JalovaMoc_L2 | REAL | IOD_TIS_TCP | 44169 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc3JalovaMoc_L3 | REAL | IOD_TIS_TCP | 44171 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc3KapacitivnaEnergija | REAL | IOD_TIS_TCP | 44173
TISCirc3KapacitivnaMoc_III | REAL | IOD_TIS_TCP | 44175 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc3MaximumDemand | REAL | IOD_TIS_TCP | 44177 | 0 | 1200 | 0 | 1200 | A | ###.#
TISCirc3Napetost_L1_L2 | REAL | IOD_TIS_TCP | 44179 | 0 | 450 | 0 | 450 | V | ###.#
TISCirc3Napetost_L1_N | REAL | IOD_TIS_TCP | 44181 | 0 | 270 | 0 | 270 | V | ###.#
TISCirc3Napetost_L2_L3 | REAL | IOD_TIS_TCP | 44183 | 0 | 450 | 0 | 450 | V | ###.#
TISCirc3Napetost_L2_N | REAL | IOD_TIS_TCP | 44185 | 0 | 270 | 0 | 270 | V | ###.#
TISCirc3Napetost_L3_L1 | REAL | IOD_TIS_TCP | 44187 | 0 | 450 | 0 | 450 | V | ###.#
TISCirc3Napetost_L3_N | REAL | IOD_TIS_TCP | 44189 | 0 | 270 | 0 | 270 | V | ###.#
TISCirc3NavideznaMoc_III | REAL | IOD_TIS_TCP | 44191 | 0 | 1200 | 0 | 1200 | kVA | ###.#
TISCirc3NicelniTok | REAL | IOD_TIS_TCP | 44193 | 0 | 1200 | 0 | 1200 | A | ###.#
TISCirc3PowerFactor_III | REAL | IOD_TIS_TCP | 44195 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc3PowerFactor_L1 | REAL | IOD_TIS_TCP | 44197 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc3PowerFactor_L2 | REAL | IOD_TIS_TCP | 44199 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc3PowerFactor_L3 | REAL | IOD_TIS_TCP | 44201 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc3THDI_L1 | REAL | IOD_TIS_TCP | 44203 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc3THDI_L2 | REAL | IOD_TIS_TCP | 44205 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc3THDI_L3 | REAL | IOD_TIS_TCP | 44207 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc3THDV_L1 | REAL | IOD_TIS_TCP | 44209 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc3THDV_L2 | REAL | IOD_TIS_TCP | 44211 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc3THDV_L3 | REAL | IOD_TIS_TCP | 44213 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc3Tok_L1 | REAL | IOD_TIS_TCP | 44215 | 0 | 600 | 0 | 600 | A | ###.#
TISCirc3Tok_L2 | REAL | IOD_TIS_TCP | 44217 | 0 | 600 | 0 | 600 | A | ###.#
TISCirc3Tok_L3 | REAL | IOD_TIS_TCP | 44219 | 0 | 600 | 0 | 600 | A | ###.#
TISCirc3TokPovprecje_III | REAL | IOD_TIS_TCP | 44221 | 0 | 600 | 0 | 600 | A | ###.#
TISCirc4CosFi_III | REAL | IOD_TIS_TCP | 44223 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc4DelovnaEnergija | REAL | IOD_TIS_TCP | 44225 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc4DelovnaMoc_III | REAL | IOD_TIS_TCP | 44227 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc4DelovnaMoc_L1 | REAL | IOD_TIS_TCP | 44229 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc4DelovnaMoc_L2 | REAL | IOD_TIS_TCP | 44231 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc4DelovnaMoc_L3 | REAL | IOD_TIS_TCP | 44233 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc4Frekvenca_L1 | REAL | IOD_TIS_TCP | 44235 | 0 | 60 | 0 | 60 | Hz | ##.#
TISCirc4InduktivnaEnergija | REAL | IOD_TIS_TCP | 44237 | 0 | 600 | 0 | 600 | kW | ###.#
TISCirc4InduktivnaMoc_III | REAL | IOD_TIS_TCP | 44239 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc4JalovaMoc_L1 | REAL | IOD_TIS_TCP | 44241 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc4JalovaMoc_L2 | REAL | IOD_TIS_TCP | 44243 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc4JalovaMoc_L3 | REAL | IOD_TIS_TCP | 44245 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc4KapacitivnaEnergija | REAL | IOD_TIS_TCP | 44247
TISCirc4KapacitivnaMoc_III | REAL | IOD_TIS_TCP | 44249 | 0 | 600 | 0 | 600 | kVAR | ###.#
TISCirc4MaximumDemand | REAL | IOD_TIS_TCP | 44251 | 0 | 1200 | 0 | 1200 | A | ###.#
TISCirc4Napetost_L1_L2 | REAL | IOD_TIS_TCP | 44253 | 0 | 450 | 0 | 450 | V | ###.#
TISCirc4Napetost_L1_N | REAL | IOD_TIS_TCP | 44255 | 0 | 270 | 0 | 270 | V | ###.#
TISCirc4Napetost_L2_L3 | REAL | IOD_TIS_TCP | 44257 | 0 | 450 | 0 | 450 | V | ###.#
TISCirc4Napetost_L2_N | REAL | IOD_TIS_TCP | 44259 | 0 | 270 | 0 | 270 | V | ###.#
TISCirc4Napetost_L3_L1 | REAL | IOD_TIS_TCP | 44261 | 0 | 450 | 0 | 450 | V | ###.#
TISCirc4Napetost_L3_N | REAL | IOD_TIS_TCP | 44263 | 0 | 270 | 0 | 270 | V | ###.#
TISCirc4NavideznaMoc_III | REAL | IOD_TIS_TCP | 44265 | 0 | 1200 | 0 | 1200 | kVA | ###.#
TISCirc4NicelniTok | REAL | IOD_TIS_TCP | 44267 | 0 | 1200 | 0 | 1200 | A | ###.#
TISCirc4PowerFactor_III | REAL | IOD_TIS_TCP | 44269 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc4PowerFactor_L1 | REAL | IOD_TIS_TCP | 44271 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc4PowerFactor_L2 | REAL | IOD_TIS_TCP | 44273 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc4PowerFactor_L3 | REAL | IOD_TIS_TCP | 44275 | -1 | 1 | -1 | 1 |  | ##.##
TISCirc4THDI_L1 | REAL | IOD_TIS_TCP | 44277 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc4THDI_L2 | REAL | IOD_TIS_TCP | 44279 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc4THDI_L3 | REAL | IOD_TIS_TCP | 44281 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc4THDV_L1 | REAL | IOD_TIS_TCP | 44283 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc4THDV_L2 | REAL | IOD_TIS_TCP | 44285 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc4THDV_L3 | REAL | IOD_TIS_TCP | 44287 | 0 | 10 | 0 | 10 | % | ###.#
TISCirc4Tok_L1 | REAL | IOD_TIS_TCP | 44289 | 0 | 600 | 0 | 600 | A | ###.#
TISCirc4Tok_L2 | REAL | IOD_TIS_TCP | 44291 | 0 | 600 | 0 | 600 | A | ###.#
TISCirc4Tok_L3 | REAL | IOD_TIS_TCP | 44293 | 0 | 600 | 0 | 600 | A | ###.#
TISCirc4TokPovprecje_III | REAL | IOD_TIS_TCP | 44295 | 0 | 600 | 0 | 600 | A | ###.#
TISCircutorCosFi_III | REAL | IOD_TIS_TCP | 44297
TISCircutorDelovnaEnergija | REAL | IOD_TIS_TCP | 44299
TISCircutorDelovnaMoc_III | REAL | IOD_TIS_TCP | 44301
TISCircutorDelovnaMoc_L1 | REAL | IOD_TIS_TCP | 44303
TISCircutorDelovnaMoc_L2 | REAL | IOD_TIS_TCP | 44305
TISCircutorDelovnaMoc_L3 | REAL | IOD_TIS_TCP | 44307
TISCircutorFrekvenca_L1 | REAL | IOD_TIS_TCP | 44309
TISCircutorInduktivnaEnergija | REAL | IOD_TIS_TCP | 44311
TISCircutorInduktivnaMoc_III | REAL | IOD_TIS_TCP | 44313
TISCircutorJalovaMoc_L1 | REAL | IOD_TIS_TCP | 44315
TISCircutorJalovaMoc_L2 | REAL | IOD_TIS_TCP | 44317
TISCircutorJalovaMoc_L3 | REAL | IOD_TIS_TCP | 44319
TISCircutorKapacitivnaEnergija | REAL | IOD_TIS_TCP | 44321
TISCircutorKapacitivnaMoc_III | REAL | IOD_TIS_TCP | 44323
TISCircutorMaximumDemand | REAL | IOD_TIS_TCP | 44325
TISCircutorNapetost_L1_L2 | REAL | IOD_TIS_TCP | 44327
TISCircutorNapetost_L1_N | REAL | IOD_TIS_TCP | 44329
TISCircutorNapetost_L2_L3 | REAL | IOD_TIS_TCP | 44331
TISCircutorNapetost_L2_N | REAL | IOD_TIS_TCP | 44333
TISCircutorNapetost_L3_L1 | REAL | IOD_TIS_TCP | 44335
TISCircutorNapetost_L3_N | REAL | IOD_TIS_TCP | 44337
TISCircutorNavideznaMoc_III | REAL | IOD_TIS_TCP | 44339
TISCircutorNicelniTok | REAL | IOD_TIS_TCP | 44341
TISCircutorPowerFactor_III | REAL | IOD_TIS_TCP | 44343
TISCircutorPowerFactor_L1 | REAL | IOD_TIS_TCP | 44345
TISCircutorPowerFactor_L2 | REAL | IOD_TIS_TCP | 44347
TISCircutorPowerFactor_L3 | REAL | IOD_TIS_TCP | 44349
TISCircutorTHDI_L1 | REAL | IOD_TIS_TCP | 44351
TISCircutorTHDI_L2 | REAL | IOD_TIS_TCP | 44353
TISCircutorTHDI_L3 | REAL | IOD_TIS_TCP | 44355
TISCircutorTHDV_L1 | REAL | IOD_TIS_TCP | 44357
TISCircutorTHDV_L2 | REAL | IOD_TIS_TCP | 44359
TISCircutorTHDV_L3 | REAL | IOD_TIS_TCP | 44361
TISCircutorTok_L1 | REAL | IOD_TIS_TCP | 44363
TISCircutorTok_L2 | REAL | IOD_TIS_TCP | 44365
TISCircutorTok_L3 | REAL | IOD_TIS_TCP | 44367
TISCircutorTokPovprecje_III | REAL | IOD_TIS_TCP | 44369
TISComSCADA | DIGITAL | IOD_TIS_TCP | 00015
TISComSCADA1 | DIGITAL | IOD_TIS_TCP | 00016
TISDate_Time0 | STRING | IOD_TIS_TCP | 45001[15]
TISDate_Time1 | STRING | IOD_TIS_TCP | 45016[15]
TISDate_Time2 | STRING | IOD_TIS_TCP | 45031[15]
TISDate_Time3 | STRING | IOD_TIS_TCP | 45046[15]
TISDateTimeDan | INT | IOD_TIS_TCP | 40001
TISDateTimeLeto | INT | IOD_TIS_TCP | 40002
TISDateTimeMesec | INT | IOD_TIS_TCP | 40003
TISDateTimeMinuta | INT | IOD_TIS_TCP | 40004
TISDateTimeSekunda | INT | IOD_TIS_TCP | 40005
TISDateTimeUra | INT | IOD_TIS_TCP | 40006
TISDI_F1_OdklHlOm1_IZP | DIGITAL | IOD_TIS_TCP | 00017
TISDI_F1_OdklHlOm1_ON | DIGITAL | IOD_TIS_TCP | 00018
TISDI_F2_OdklHlOm2_IZP | DIGITAL | IOD_TIS_TCP | 00019
TISDI_F2_OdklHlOm2_ON | DIGITAL | IOD_TIS_TCP | 00020
TISDI_F3_OdklHlOm3_IZP | DIGITAL | IOD_TIS_TCP | 00021
TISDI_F3_OdklHlOm3_ON | DIGITAL | IOD_TIS_TCP | 00022
TISDI_F4_OdkPripVode_IZP | DIGITAL | IOD_TIS_TCP | 00023
TISDI_F4_OdkPripVode_ON | DIGITAL | IOD_TIS_TCP | 00024
TISDI_HladOmara1_ERR | DIGITAL | IOD_TIS_TCP | 00025
TISDI_HladOmara1_ON | DIGITAL | IOD_TIS_TCP | 00026
TISDI_HladOmara2_ERR | DIGITAL | IOD_TIS_TCP | 00027
TISDI_HladOmara2_ON | DIGITAL | IOD_TIS_TCP | 00028
TISDI_HladOmara3_ERR | DIGITAL | IOD_TIS_TCP | 00029
TISDI_HladOmara3_ON | DIGITAL | IOD_TIS_TCP | 00030
TISDI_PripVode1_ERR | DIGITAL | IOD_TIS_TCP | 00031
TISDI_PripVode1_ON | DIGITAL | IOD_TIS_TCP | 00032
TISDI_PripVode2_ERR | DIGITAL | IOD_TIS_TCP | 00033
TISDI_PripVode2_ON | DIGITAL | IOD_TIS_TCP | 00034
TISDI_Q0_DEG3_ON | DIGITAL | IOD_TIS_TCP | 00035
TISDI_Q0_EG3_ON | DIGITAL | IOD_TIS_TCP | 00036
TISDI_Q0_GlavnoStikalo_ON | DIGITAL | IOD_TIS_TCP | 00037
TISDI_Q0_UPS3_ON | DIGITAL | IOD_TIS_TCP | 00038
TISDI_RazlitjeVodeHO1 | DIGITAL | IOD_TIS_TCP | 00039
TISDI_RazlitjeVodeHO2 | DIGITAL | IOD_TIS_TCP | 00040
TISDI_RazlitjeVodeHO3 | DIGITAL | IOD_TIS_TCP | 00041
TISDI_UPS_Alarm | DIGITAL | IOD_TIS_TCP | 00042
TISDI_UPS_BatNacin | DIGITAL | IOD_TIS_TCP | 00043
TISDI_UPS_Polnjenje | DIGITAL | IOD_TIS_TCP | 00044
TISDI_Vlazilec1_ERR | DIGITAL | IOD_TIS_TCP | 00045
TISDI_Vlazilec1_ON | DIGITAL | IOD_TIS_TCP | 00046
TISDI_Vlazilec2_ERR | DIGITAL | IOD_TIS_TCP | 00047
TISDI_Vlazilec2_ON | DIGITAL | IOD_TIS_TCP | 00048
TISDI_Vlazilec3_ERR | DIGITAL | IOD_TIS_TCP | 00049
TISDI_Vlazilec3_ON | DIGITAL | IOD_TIS_TCP | 00050
TISDIN_F1_OdklHlOm1_IZP | DIGITAL | IOD_TIS_TCP | 00051
TISDIN_F2_OdklHlOm2_IZP | DIGITAL | IOD_TIS_TCP | 00052
TISDIN_F3_OdklHlOm3_IZP | DIGITAL | IOD_TIS_TCP | 00053
TISDIN_F4_OdkPripVode_IZP | DIGITAL | IOD_TIS_TCP | 00054
TISDIN_HladOmara1_ERR | DIGITAL | IOD_TIS_TCP | 00055
TISDIN_HladOmara2_ERR | DIGITAL | IOD_TIS_TCP | 00056
TISDIN_HladOmara3_ERR | DIGITAL | IOD_TIS_TCP | 00057
TISDIN_PripVode1_ERR | DIGITAL | IOD_TIS_TCP | 00058
TISDIN_PripVode2_ERR | DIGITAL | IOD_TIS_TCP | 00059
TISDIN_Vlazilec1_ERR | DIGITAL | IOD_TIS_TCP | 00060
TISDIN_Vlazilec2_ERR | DIGITAL | IOD_TIS_TCP | 00061
TISDIN_Vlazilec3_ERR | DIGITAL | IOD_TIS_TCP | 00062
TISDO_HladOm1_Izklop | DIGITAL | IOD_TIS_TCP | 00063
TISDO_HladOm2_Izklop | DIGITAL | IOD_TIS_TCP | 00064
TISDO_HladOm3_Izklop | DIGITAL | IOD_TIS_TCP | 00065
TISErrComCirc1 | DIGITAL | IOD_TIS_TCP | 00066
TISErrComCirc2 | DIGITAL | IOD_TIS_TCP | 00067
TISErrComCirc3 | DIGITAL | IOD_TIS_TCP | 00068
TISErrComCirc4 | DIGITAL | IOD_TIS_TCP | 00069
TISErrComCirc5 | DIGITAL | IOD_TIS_TCP | 00070
TISErrComKlima1 | DIGITAL | IOD_TIS_TCP | 00071
TISErrComKlima2 | DIGITAL | IOD_TIS_TCP | 00072
TISErrComKlima3 | DIGITAL | IOD_TIS_TCP | 00073
TISErrComKlima4 | DIGITAL | IOD_TIS_TCP | 00074
TISErrComKlima5 | DIGITAL | IOD_TIS_TCP | 00075
TISErrComKlima6 | DIGITAL | IOD_TIS_TCP | 00076
TISErrCommScada | DIGITAL | IOD_TIS_TCP | 00077
TISErrComPanelPLC | DIGITAL | IOD_TIS_TCP | 00078
TISErrComPort2 | DIGITAL | IOD_TIS_TCP | 00079
TISErrorComCirc1Code10 | INT | IOD_TIS_TCP | 40007
TISErrorComCirc1Code11 | INT | IOD_TIS_TCP | 40008
TISErrorComCirc1Code12 | INT | IOD_TIS_TCP | 40009
TISErrorComCirc1Code13 | INT | IOD_TIS_TCP | 40010
TISErrorComCirc1Code14 | INT | IOD_TIS_TCP | 40011
TISErrorComCirc1Code15 | INT | IOD_TIS_TCP | 40012
TISErrorComCirc1Code1 | INT | IOD_TIS_TCP | 40013
TISErrorComCirc1Code2 | INT | IOD_TIS_TCP | 40014
TISErrorComCirc1Code3 | INT | IOD_TIS_TCP | 40015
TISErrorComCirc1Code4 | INT | IOD_TIS_TCP | 40016
TISErrorComCirc1Code5 | INT | IOD_TIS_TCP | 40017
TISErrorComCirc1Code6 | INT | IOD_TIS_TCP | 40018
TISErrorComCirc1Code7 | INT | IOD_TIS_TCP | 40019
TISErrorComCirc1Code8 | INT | IOD_TIS_TCP | 40020
TISErrorComCirc1Code9 | INT | IOD_TIS_TCP | 40021
TISErrorComCirc1Error | DIGITAL | IOD_TIS_TCP | 00080
TISErrorComCirc1Status | INT | IOD_TIS_TCP | 40022
TISErrorComCirc2Code10 | INT | IOD_TIS_TCP | 40023
TISErrorComCirc2Code11 | INT | IOD_TIS_TCP | 40024
TISErrorComCirc2Code12 | INT | IOD_TIS_TCP | 40025
TISErrorComCirc2Code13 | INT | IOD_TIS_TCP | 40026
TISErrorComCirc2Code14 | INT | IOD_TIS_TCP | 40027
TISErrorComCirc2Code15 | INT | IOD_TIS_TCP | 40028
TISErrorComCirc2Code1 | INT | IOD_TIS_TCP | 40029
TISErrorComCirc2Code2 | INT | IOD_TIS_TCP | 40030
TISErrorComCirc2Code3 | INT | IOD_TIS_TCP | 40031
TISErrorComCirc2Code4 | INT | IOD_TIS_TCP | 40032
TISErrorComCirc2Code5 | INT | IOD_TIS_TCP | 40033
TISErrorComCirc2Code6 | INT | IOD_TIS_TCP | 40034
TISErrorComCirc2Code7 | INT | IOD_TIS_TCP | 40035
TISErrorComCirc2Code8 | INT | IOD_TIS_TCP | 40036
TISErrorComCirc2Code9 | INT | IOD_TIS_TCP | 40037
TISErrorComCirc2Error | DIGITAL | IOD_TIS_TCP | 00081
TISErrorComCirc2Status | INT | IOD_TIS_TCP | 40038
TISErrorComCirc3Code10 | INT | IOD_TIS_TCP | 40039
TISErrorComCirc3Code11 | INT | IOD_TIS_TCP | 40040
TISErrorComCirc3Code12 | INT | IOD_TIS_TCP | 40041
TISErrorComCirc3Code13 | INT | IOD_TIS_TCP | 40042
TISErrorComCirc3Code14 | INT | IOD_TIS_TCP | 40043
TISErrorComCirc3Code15 | INT | IOD_TIS_TCP | 40044
TISErrorComCirc3Code1 | INT | IOD_TIS_TCP | 40045
TISErrorComCirc3Code2 | INT | IOD_TIS_TCP | 40046
TISErrorComCirc3Code3 | INT | IOD_TIS_TCP | 40047
TISErrorComCirc3Code4 | INT | IOD_TIS_TCP | 40048
TISErrorComCirc3Code5 | INT | IOD_TIS_TCP | 40049
TISErrorComCirc3Code6 | INT | IOD_TIS_TCP | 40050
TISErrorComCirc3Code7 | INT | IOD_TIS_TCP | 40051
TISErrorComCirc3Code8 | INT | IOD_TIS_TCP | 40052
TISErrorComCirc3Code9 | INT | IOD_TIS_TCP | 40053
TISErrorComCirc3Error | DIGITAL | IOD_TIS_TCP | 00082
TISErrorComCirc3Status | INT | IOD_TIS_TCP | 40054
TISErrorComCirc4Code10 | INT | IOD_TIS_TCP | 40055
TISErrorComCirc4Code11 | INT | IOD_TIS_TCP | 40056
TISErrorComCirc4Code12 | INT | IOD_TIS_TCP | 40057
TISErrorComCirc4Code13 | INT | IOD_TIS_TCP | 40058
TISErrorComCirc4Code14 | INT | IOD_TIS_TCP | 40059
TISErrorComCirc4Code15 | INT | IOD_TIS_TCP | 40060
TISErrorComCirc4Code1 | INT | IOD_TIS_TCP | 40061
TISErrorComCirc4Code2 | INT | IOD_TIS_TCP | 40062
TISErrorComCirc4Code3 | INT | IOD_TIS_TCP | 40063
TISErrorComCirc4Code4 | INT | IOD_TIS_TCP | 40064
TISErrorComCirc4Code5 | INT | IOD_TIS_TCP | 40065
TISErrorComCirc4Code6 | INT | IOD_TIS_TCP | 40066
TISErrorComCirc4Code7 | INT | IOD_TIS_TCP | 40067
TISErrorComCirc4Code8 | INT | IOD_TIS_TCP | 40068
TISErrorComCirc4Code9 | INT | IOD_TIS_TCP | 40069
TISErrorComCirc4Error | DIGITAL | IOD_TIS_TCP | 00083
TISErrorComCirc4Status | INT | IOD_TIS_TCP | 40070
TISErrorComCirc5Code10 | INT | IOD_TIS_TCP | 40071
TISErrorComCirc5Code11 | INT | IOD_TIS_TCP | 40072
TISErrorComCirc5Code12 | INT | IOD_TIS_TCP | 40073
TISErrorComCirc5Code13 | INT | IOD_TIS_TCP | 40074
TISErrorComCirc5Code14 | INT | IOD_TIS_TCP | 40075
TISErrorComCirc5Code15 | INT | IOD_TIS_TCP | 40076
TISErrorComCirc5Code1 | INT | IOD_TIS_TCP | 40077
TISErrorComCirc5Code2 | INT | IOD_TIS_TCP | 40078
TISErrorComCirc5Code3 | INT | IOD_TIS_TCP | 40079
TISErrorComCirc5Code4 | INT | IOD_TIS_TCP | 40080
TISErrorComCirc5Code5 | INT | IOD_TIS_TCP | 40081
TISErrorComCirc5Code6 | INT | IOD_TIS_TCP | 40082
TISErrorComCirc5Code7 | INT | IOD_TIS_TCP | 40083
TISErrorComCirc5Code8 | INT | IOD_TIS_TCP | 40084
TISErrorComCirc5Code9 | INT | IOD_TIS_TCP | 40085
TISErrorComCirc5Error | DIGITAL | IOD_TIS_TCP | 00084
TISErrorComCirc5Status | INT | IOD_TIS_TCP | 40086
TISErrorComKlima1Code10 | INT | IOD_TIS_TCP | 40087
TISErrorComKlima1Code11 | INT | IOD_TIS_TCP | 40088
TISErrorComKlima1Code12 | INT | IOD_TIS_TCP | 40089
TISErrorComKlima1Code13 | INT | IOD_TIS_TCP | 40090
TISErrorComKlima1Code14 | INT | IOD_TIS_TCP | 40091
TISErrorComKlima1Code15 | INT | IOD_TIS_TCP | 40092
TISErrorComKlima1Code1 | INT | IOD_TIS_TCP | 40093
TISErrorComKlima1Code2 | INT | IOD_TIS_TCP | 40094
TISErrorComKlima1Code3 | INT | IOD_TIS_TCP | 40095
TISErrorComKlima1Code4 | INT | IOD_TIS_TCP | 40096
TISErrorComKlima1Code5 | INT | IOD_TIS_TCP | 40097
TISErrorComKlima1Code6 | INT | IOD_TIS_TCP | 40098
TISErrorComKlima1Code7 | INT | IOD_TIS_TCP | 40099
TISErrorComKlima1Code8 | INT | IOD_TIS_TCP | 40100
TISErrorComKlima1Code9 | INT | IOD_TIS_TCP | 40101
TISErrorComKlima1Error | DIGITAL | IOD_TIS_TCP | 00085
TISErrorComKlima1Status | INT | IOD_TIS_TCP | 40102
TISErrorComKlima2Code10 | INT | IOD_TIS_TCP | 40103
TISErrorComKlima2Code11 | INT | IOD_TIS_TCP | 40104
TISErrorComKlima2Code12 | INT | IOD_TIS_TCP | 40105
TISErrorComKlima2Code13 | INT | IOD_TIS_TCP | 40106
TISErrorComKlima2Code14 | INT | IOD_TIS_TCP | 40107
TISErrorComKlima2Code15 | INT | IOD_TIS_TCP | 40108
TISErrorComKlima2Code1 | INT | IOD_TIS_TCP | 40109
TISErrorComKlima2Code2 | INT | IOD_TIS_TCP | 40110
TISErrorComKlima2Code3 | INT | IOD_TIS_TCP | 40111
TISErrorComKlima2Code4 | INT | IOD_TIS_TCP | 40112
TISErrorComKlima2Code5 | INT | IOD_TIS_TCP | 40113
TISErrorComKlima2Code6 | INT | IOD_TIS_TCP | 40114
TISErrorComKlima2Code7 | INT | IOD_TIS_TCP | 40115
TISErrorComKlima2Code8 | INT | IOD_TIS_TCP | 40116
TISErrorComKlima2Code9 | INT | IOD_TIS_TCP | 40117
TISErrorComKlima2Error | DIGITAL | IOD_TIS_TCP | 00086
TISErrorComKlima2Status | INT | IOD_TIS_TCP | 40118
TISErrorComKlima3Code10 | INT | IOD_TIS_TCP | 40119
TISErrorComKlima3Code11 | INT | IOD_TIS_TCP | 40120
TISErrorComKlima3Code12 | INT | IOD_TIS_TCP | 40121
TISErrorComKlima3Code13 | INT | IOD_TIS_TCP | 40122
TISErrorComKlima3Code14 | INT | IOD_TIS_TCP | 40123
TISErrorComKlima3Code15 | INT | IOD_TIS_TCP | 40124
TISErrorComKlima3Code1 | INT | IOD_TIS_TCP | 40125
TISErrorComKlima3Code2 | INT | IOD_TIS_TCP | 40126
TISErrorComKlima3Code3 | INT | IOD_TIS_TCP | 40127
TISErrorComKlima3Code4 | INT | IOD_TIS_TCP | 40128
TISErrorComKlima3Code5 | INT | IOD_TIS_TCP | 40129
TISErrorComKlima3Code6 | INT | IOD_TIS_TCP | 40130
TISErrorComKlima3Code7 | INT | IOD_TIS_TCP | 40131
TISErrorComKlima3Code8 | INT | IOD_TIS_TCP | 40132
TISErrorComKlima3Code9 | INT | IOD_TIS_TCP | 40133
TISErrorComKlima3Error | DIGITAL | IOD_TIS_TCP | 00087
TISErrorComKlima3Status | INT | IOD_TIS_TCP | 40134
TISErrorComKlima4Code10 | INT | IOD_TIS_TCP | 40135
TISErrorComKlima4Code11 | INT | IOD_TIS_TCP | 40136
TISErrorComKlima4Code12 | INT | IOD_TIS_TCP | 40137
TISErrorComKlima4Code13 | INT | IOD_TIS_TCP | 40138
TISErrorComKlima4Code14 | INT | IOD_TIS_TCP | 40139
TISErrorComKlima4Code15 | INT | IOD_TIS_TCP | 40140
TISErrorComKlima4Code1 | INT | IOD_TIS_TCP | 40141
TISErrorComKlima4Code2 | INT | IOD_TIS_TCP | 40142
TISErrorComKlima4Code3 | INT | IOD_TIS_TCP | 40143
TISErrorComKlima4Code4 | INT | IOD_TIS_TCP | 40144
TISErrorComKlima4Code5 | INT | IOD_TIS_TCP | 40145
TISErrorComKlima4Code6 | INT | IOD_TIS_TCP | 40146
TISErrorComKlima4Code7 | INT | IOD_TIS_TCP | 40147
TISErrorComKlima4Code8 | INT | IOD_TIS_TCP | 40148
TISErrorComKlima4Code9 | INT | IOD_TIS_TCP | 40149
TISErrorComKlima4Error | DIGITAL | IOD_TIS_TCP | 00088
TISErrorComKlima4Status | INT | IOD_TIS_TCP | 40150
TISErrorComKlima5Code10 | INT | IOD_TIS_TCP | 40151
TISErrorComKlima5Code11 | INT | IOD_TIS_TCP | 40152
TISErrorComKlima5Code12 | INT | IOD_TIS_TCP | 40153
TISErrorComKlima5Code13 | INT | IOD_TIS_TCP | 40154
TISErrorComKlima5Code14 | INT | IOD_TIS_TCP | 40155
TISErrorComKlima5Code15 | INT | IOD_TIS_TCP | 40156
TISErrorComKlima5Code1 | INT | IOD_TIS_TCP | 40157
TISErrorComKlima5Code2 | INT | IOD_TIS_TCP | 40158
TISErrorComKlima5Code3 | INT | IOD_TIS_TCP | 40159
TISErrorComKlima5Code4 | INT | IOD_TIS_TCP | 40160
TISErrorComKlima5Code5 | INT | IOD_TIS_TCP | 40161
TISErrorComKlima5Code6 | INT | IOD_TIS_TCP | 40162
TISErrorComKlima5Code7 | INT | IOD_TIS_TCP | 40163
TISErrorComKlima5Code8 | INT | IOD_TIS_TCP | 40164
TISErrorComKlima5Code9 | INT | IOD_TIS_TCP | 40165
TISErrorComKlima5Error | DIGITAL | IOD_TIS_TCP | 00089
TISErrorComKlima5Status | INT | IOD_TIS_TCP | 40166
TISErrorComKlima6Code10 | INT | IOD_TIS_TCP | 40167
TISErrorComKlima6Code11 | INT | IOD_TIS_TCP | 40168
TISErrorComKlima6Code12 | INT | IOD_TIS_TCP | 40169
TISErrorComKlima6Code13 | INT | IOD_TIS_TCP | 40170
TISErrorComKlima6Code14 | INT | IOD_TIS_TCP | 40171
TISErrorComKlima6Code15 | INT | IOD_TIS_TCP | 40172
TISErrorComKlima6Code1 | INT | IOD_TIS_TCP | 40173
TISErrorComKlima6Code2 | INT | IOD_TIS_TCP | 40174
TISErrorComKlima6Code3 | INT | IOD_TIS_TCP | 40175
TISErrorComKlima6Code4 | INT | IOD_TIS_TCP | 40176
TISErrorComKlima6Code5 | INT | IOD_TIS_TCP | 40177
TISErrorComKlima6Code6 | INT | IOD_TIS_TCP | 40178
TISErrorComKlima6Code7 | INT | IOD_TIS_TCP | 40179
TISErrorComKlima6Code8 | INT | IOD_TIS_TCP | 40180
TISErrorComKlima6Code9 | INT | IOD_TIS_TCP | 40181
TISErrorComKlima6Error | DIGITAL | IOD_TIS_TCP | 00090
TISErrorComKlima6Status | INT | IOD_TIS_TCP | 40182
TISKlima1AlarmKompresor1 | DIGITAL | IOD_TIS_TCP | 00091
TISKlima1AlarmKompresor2 | DIGITAL | IOD_TIS_TCP | 00092
TISKlima1Deluje | DIGITAL | IOD_TIS_TCP | 00093
TISKlima1EnergySaving | DIGITAL | IOD_TIS_TCP | 00094
TISKlima1FaultyEPROM | DIGITAL | IOD_TIS_TCP | 00095
TISKlima1FenThermalCutout | DIGITAL | IOD_TIS_TCP | 00096
TISKlima1GeneralAlarm | DIGITAL | IOD_TIS_TCP | 00097
TISKlima1GrelecStatus | INT | IOD_TIS_TCP | 40183
TISKlima1IzhodniVentStatus | INT | IOD_TIS_TCP | 40184
TISKlima1Kompresor1naMejiObrUr | DIGITAL | IOD_TIS_TCP | 00098
TISKlima1Kompresor2naMejiObrUr | DIGITAL | IOD_TIS_TCP | 00099
TISKlima1KompresorStatus | INT | IOD_TIS_TCP | 40185
TISKlima1Napaka | DIGITAL | IOD_TIS_TCP | 00100
TISKlima1NapakaPriPretokuZraka | DIGITAL | IOD_TIS_TCP | 00101
TISKlima1NapakaSenzorPovratVode | DIGITAL | IOD_TIS_TCP | 00102
TISKlima1NapakaSenzorTempIzpiha | DIGITAL | IOD_TIS_TCP | 00103
TISKlima1NapakaSenzorTempProstora | DIGITAL | IOD_TIS_TCP | 00104
TISKlima1NapakaSenzorVlaznosti | DIGITAL | IOD_TIS_TCP | 00105
TISKlima1NapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS_TCP | 00106
TISKlima1NastMaxTemp | REAL | IOD_TIS_TCP | 44371 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima1NastMaxVlaznost | REAL | IOD_TIS_TCP | 44373 | 0 | 100 | 0 | 100 | % | ##.#
TISKlima1NastMinTemp | REAL | IOD_TIS_TCP | 44375 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima1NastMinVlaznost | REAL | IOD_TIS_TCP | 44377 | 0 | 100 | 0 | 100 | % | ##.#
TISKlima1NastTempProstora | REAL | IOD_TIS_TCP | 44379 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima1NastVlaznost | REAL | IOD_TIS_TCP | 44381 | 0 | 100 | 0 | 100 | % | ##.#
TISKlima1NiTokaVVlazilcu | DIGITAL | IOD_TIS_TCP | 00107
TISKlima1NiVodeVVlazilcu | DIGITAL | IOD_TIS_TCP | 00108
TISKlima1NizekPritiskKompresor1 | DIGITAL | IOD_TIS_TCP | 00109
TISKlima1NizekPritiskKompresor2 | DIGITAL | IOD_TIS_TCP | 00110
TISKlima1NizkaTempPovratneVode | DIGITAL | IOD_TIS_TCP | 00111
TISKlima1NizkaTempVProstoru | DIGITAL | IOD_TIS_TCP | 00112
TISKlima1NizkaVlaznost | DIGITAL | IOD_TIS_TCP | 00113
TISKlima1ObratovalneUre | REAL | IOD_TIS_TCP | 44383
TISKlima1OnOffEnablingBySupervisor | DIGITAL | IOD_TIS_TCP | 00114
TISKlima1PozarniAlarm | DIGITAL | IOD_TIS_TCP | 00115
TISKlima1Razvlazevanje | DIGITAL | IOD_TIS_TCP | 00116
TISKlima1RemoteOFFtoOutput | DIGITAL | IOD_TIS_TCP | 00117
TISKlima1RemoteOnOff | DIGITAL | IOD_TIS_TCP | 00118
TISKlima1RocniIzklop | DIGITAL | IOD_TIS_TCP | 00119
TISKlima1SenzorjiStatus | DIGITAL | IOD_TIS_TCP | 00120
TISKlima1StoppedByAlarms | DIGITAL | IOD_TIS_TCP | 00121
TISKlima1TemperaturaProstora | REAL | IOD_TIS_TCP | 44385 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima1TempIzpihanegaZraka | REAL | IOD_TIS_TCP | 44387 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima1TempPovratneVode | REAL | IOD_TIS_TCP | 44389 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima1ThermalCutoutHeater1 | DIGITAL | IOD_TIS_TCP | 00122
TISKlima1ThermalCutoutHeater2 | DIGITAL | IOD_TIS_TCP | 00123
TISKlima1UnitOnOff | DIGITAL | IOD_TIS_TCP | 00124
TISKlima1VentilatorNaMejiObrUr | DIGITAL | IOD_TIS_TCP | 00125
TISKlima1VentilGretjeOdpiranje | DIGITAL | IOD_TIS_TCP | 00126
TISKlima1VentilGretjeZapiranje | DIGITAL | IOD_TIS_TCP | 00127
TISKlima1VentilHlajenjeOdpiranje | DIGITAL | IOD_TIS_TCP | 00128
TISKlima1VentilHlajenjeZapiranje | DIGITAL | IOD_TIS_TCP | 00129
TISKlima1VisokaTempPovratneVode | DIGITAL | IOD_TIS_TCP | 00130
TISKlima1VisokaTempVProstoru | DIGITAL | IOD_TIS_TCP | 00131
TISKlima1VisokaVlaznost | DIGITAL | IOD_TIS_TCP | 00132
TISKlima1VisokTokVVlazilcu | DIGITAL | IOD_TIS_TCP | 00133
TISKlima1Vlazenje | DIGITAL | IOD_TIS_TCP | 00134
TISKlima1VlazilecStatus | INT | IOD_TIS_TCP | 40186
TISKlima1VlaznostProstora | REAL | IOD_TIS_TCP | 44391 | 0 | 100 | 0 | 100 | % | ##
TISKlima1ZamasenFilter | DIGITAL | IOD_TIS_TCP | 00135
TISKlima1ZunanjaTemp | REAL | IOD_TIS_TCP | 44393
TISKlima2AlarmKompresor1 | DIGITAL | IOD_TIS_TCP | 00136
TISKlima2AlarmKompresor2 | DIGITAL | IOD_TIS_TCP | 00137
TISKlima2Deluje | DIGITAL | IOD_TIS_TCP | 00138
TISKlima2EnergySaving | DIGITAL | IOD_TIS_TCP | 00139
TISKlima2FaultyEPROM | DIGITAL | IOD_TIS_TCP | 00140
TISKlima2FenThermalCutout | DIGITAL | IOD_TIS_TCP | 00141
TISKlima2GeneralAlarm | DIGITAL | IOD_TIS_TCP | 00142
TISKlima2GrelecStatus | INT | IOD_TIS_TCP | 40187
TISKlima2IzhodniVentStatus | INT | IOD_TIS_TCP | 40188
TISKlima2Kompresor1naMejiObrUr | DIGITAL | IOD_TIS_TCP | 00143
TISKlima2Kompresor2naMejiObrUr | DIGITAL | IOD_TIS_TCP | 00144
TISKlima2KompresorStatus | INT | IOD_TIS_TCP | 40189
TISKlima2Napaka | DIGITAL | IOD_TIS_TCP | 00145
TISKlima2NapakaPriPretokuZraka | DIGITAL | IOD_TIS_TCP | 00146
TISKlima2NapakaSenzorPovratVode | DIGITAL | IOD_TIS_TCP | 00147
TISKlima2NapakaSenzorTempIzpiha | DIGITAL | IOD_TIS_TCP | 00148
TISKlima2NapakaSenzorTempProstora | DIGITAL | IOD_TIS_TCP | 00149
TISKlima2NapakaSenzorVlaznosti | DIGITAL | IOD_TIS_TCP | 00150
TISKlima2NapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS_TCP | 00151
TISKlima2NastMaxTemp | REAL | IOD_TIS_TCP | 44395 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima2NastMaxVlaznost | REAL | IOD_TIS_TCP | 44397 | 0 | 100 | 0 | 100 | % | ##.#
TISKlima2NastMinTemp | REAL | IOD_TIS_TCP | 44399 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima2NastMinVlaznost | REAL | IOD_TIS_TCP | 44401 | 0 | 100 | 0 | 100 | % | ##.#
TISKlima2NastTempProstora | REAL | IOD_TIS_TCP | 44403 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima2NastVlaznost | REAL | IOD_TIS_TCP | 44405 | 0 | 100 | 0 | 100 | % | ##.#
TISKlima2NiTokaVVlazilcu | DIGITAL | IOD_TIS_TCP | 00152
TISKlima2NiVodeVVlazilcu | DIGITAL | IOD_TIS_TCP | 00153
TISKlima2NizekPritiskKompresor1 | DIGITAL | IOD_TIS_TCP | 00154
TISKlima2NizekPritiskKompresor2 | DIGITAL | IOD_TIS_TCP | 00155
TISKlima2NizkaTempPovratneVode | DIGITAL | IOD_TIS_TCP | 00156
TISKlima2NizkaTempVProstoru | DIGITAL | IOD_TIS_TCP | 00157
TISKlima2NizkaVlaznost | DIGITAL | IOD_TIS_TCP | 00158
TISKlima2ObratovalneUre | REAL | IOD_TIS_TCP | 44407
TISKlima2OnOffEnablingBySupervisor | DIGITAL | IOD_TIS_TCP | 00159
TISKlima2PozarniAlarm | DIGITAL | IOD_TIS_TCP | 00160
TISKlima2Razvlazevanje | DIGITAL | IOD_TIS_TCP | 00161
TISKlima2RemoteOFFtoOutput | DIGITAL | IOD_TIS_TCP | 00162
TISKlima2RemoteOnOff | DIGITAL | IOD_TIS_TCP | 00163
TISKlima2RocniIzklop | DIGITAL | IOD_TIS_TCP | 00164
TISKlima2SenzorjiStatus | DIGITAL | IOD_TIS_TCP | 00165
TISKlima2StoppedByAlarms | DIGITAL | IOD_TIS_TCP | 00166
TISKlima2TemperaturaProstora | REAL | IOD_TIS_TCP | 44409 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima2TempIzpihanegaZraka | REAL | IOD_TIS_TCP | 44411 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima2TempPovratneVode | REAL | IOD_TIS_TCP | 44413 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima2ThermalCutoutHeater1 | DIGITAL | IOD_TIS_TCP | 00167
TISKlima2ThermalCutoutHeater2 | DIGITAL | IOD_TIS_TCP | 00168
TISKlima2UnitOnOff | DIGITAL | IOD_TIS_TCP | 00169
TISKlima2VentilatorNaMejiObrUr | DIGITAL | IOD_TIS_TCP | 00170
TISKlima2VentilGretjeOdpiranje | DIGITAL | IOD_TIS_TCP | 00171
TISKlima2VentilGretjeZapiranje | DIGITAL | IOD_TIS_TCP | 00172
TISKlima2VentilHlajenjeOdpiranje | DIGITAL | IOD_TIS_TCP | 00173
TISKlima2VentilHlajenjeZapiranje | DIGITAL | IOD_TIS_TCP | 00174
TISKlima2VisokaTempPovratneVode | DIGITAL | IOD_TIS_TCP | 00175
TISKlima2VisokaTempVProstoru | DIGITAL | IOD_TIS_TCP | 00176
TISKlima2VisokaVlaznost | DIGITAL | IOD_TIS_TCP | 00177
TISKlima2VisokTokVVlazilcu | DIGITAL | IOD_TIS_TCP | 00178
TISKlima2Vlazenje | DIGITAL | IOD_TIS_TCP | 00179
TISKlima2VlazilecStatus | INT | IOD_TIS_TCP | 40190
TISKlima2VlaznostProstora | REAL | IOD_TIS_TCP | 44415 | 0 | 100 | 0 | 100 | % | ##
TISKlima2ZamasenFilter | DIGITAL | IOD_TIS_TCP | 00180
TISKlima2ZunanjaTemp | REAL | IOD_TIS_TCP | 44417
TISKlima3AlarmKompresor1 | DIGITAL | IOD_TIS_TCP | 00181
TISKlima3AlarmKompresor2 | DIGITAL | IOD_TIS_TCP | 00182
TISKlima3Deluje | DIGITAL | IOD_TIS_TCP | 00183
TISKlima3EnergySaving | DIGITAL | IOD_TIS_TCP | 00184
TISKlima3FaultyEPROM | DIGITAL | IOD_TIS_TCP | 00185
TISKlima3FenThermalCutout | DIGITAL | IOD_TIS_TCP | 00186
TISKlima3GeneralAlarm | DIGITAL | IOD_TIS_TCP | 00187
TISKlima3GrelecStatus | INT | IOD_TIS_TCP | 40191
TISKlima3IzhodniVentStatus | INT | IOD_TIS_TCP | 40192
TISKlima3Kompresor1naMejiObrUr | DIGITAL | IOD_TIS_TCP | 00188
TISKlima3Kompresor2naMejiObrUr | DIGITAL | IOD_TIS_TCP | 00189
TISKlima3KompresorStatus | INT | IOD_TIS_TCP | 40193
TISKlima3Napaka | DIGITAL | IOD_TIS_TCP | 00190
TISKlima3NapakaPriPretokuZraka | DIGITAL | IOD_TIS_TCP | 00191
TISKlima3NapakaSenzorPovratVode | DIGITAL | IOD_TIS_TCP | 00192
TISKlima3NapakaSenzorTempIzpiha | DIGITAL | IOD_TIS_TCP | 00193
TISKlima3NapakaSenzorTempProstora | DIGITAL | IOD_TIS_TCP | 00194
TISKlima3NapakaSenzorVlaznosti | DIGITAL | IOD_TIS_TCP | 00195
TISKlima3NapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS_TCP | 00196
TISKlima3NastMaxTemp | REAL | IOD_TIS_TCP | 44419 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima3NastMaxVlaznost | REAL | IOD_TIS_TCP | 44421 | 0 | 100 | 0 | 100 | % | ##.#
TISKlima3NastMinTemp | REAL | IOD_TIS_TCP | 44423 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima3NastMinVlaznost | REAL | IOD_TIS_TCP | 44425 | 0 | 100 | 0 | 100 | % | ##.#
TISKlima3NastTempProstora | REAL | IOD_TIS_TCP | 44427 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima3NastVlaznost | REAL | IOD_TIS_TCP | 44429 | 0 | 100 | 0 | 100 | % | ##.#
TISKlima3NiTokaVVlazilcu | DIGITAL | IOD_TIS_TCP | 00197
TISKlima3NiVodeVVlazilcu | DIGITAL | IOD_TIS_TCP | 00198
TISKlima3NizekPritiskKompresor1 | DIGITAL | IOD_TIS_TCP | 00199
TISKlima3NizekPritiskKompresor2 | DIGITAL | IOD_TIS_TCP | 00200
TISKlima3NizkaTempPovratneVode | DIGITAL | IOD_TIS_TCP | 00201
TISKlima3NizkaTempVProstoru | DIGITAL | IOD_TIS_TCP | 00202
TISKlima3NizkaVlaznost | DIGITAL | IOD_TIS_TCP | 00203
TISKlima3ObratovalneUre | REAL | IOD_TIS_TCP | 44431
TISKlima3OnOffEnablingBySupervisor | DIGITAL | IOD_TIS_TCP | 00204
TISKlima3PozarniAlarm | DIGITAL | IOD_TIS_TCP | 00205
TISKlima3Razvlazevanje | DIGITAL | IOD_TIS_TCP | 00206
TISKlima3RemoteOFFtoOutput | DIGITAL | IOD_TIS_TCP | 00207
TISKlima3RemoteOnOff | DIGITAL | IOD_TIS_TCP | 00208
TISKlima3RocniIzklop | DIGITAL | IOD_TIS_TCP | 00209
TISKlima3SenzorjiStatus | DIGITAL | IOD_TIS_TCP | 00210
TISKlima3StoppedByAlarms | DIGITAL | IOD_TIS_TCP | 00211
TISKlima3TemperaturaProstora | REAL | IOD_TIS_TCP | 44433 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima3TempIzpihanegaZraka | REAL | IOD_TIS_TCP | 44435 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima3TempPovratneVode | REAL | IOD_TIS_TCP | 44437 | 0 | 60 | 0 | 60 | °C | ##.#
TISKlima3ThermalCutoutHeater1 | DIGITAL | IOD_TIS_TCP | 00212
TISKlima3ThermalCutoutHeater2 | DIGITAL | IOD_TIS_TCP | 00213
TISKlima3UnitOnOff | DIGITAL | IOD_TIS_TCP | 00214
TISKlima3VentilatorNaMejiObrUr | DIGITAL | IOD_TIS_TCP | 00215
TISKlima3VentilGretjeOdpiranje | DIGITAL | IOD_TIS_TCP | 00216
TISKlima3VentilGretjeZapiranje | DIGITAL | IOD_TIS_TCP | 00217
TISKlima3VentilHlajenjeOdpiranje | DIGITAL | IOD_TIS_TCP | 00218
TISKlima3VentilHlajenjeZapiranje | DIGITAL | IOD_TIS_TCP | 00219
TISKlima3VisokaTempPovratneVode | DIGITAL | IOD_TIS_TCP | 00220
TISKlima3VisokaTempVProstoru | DIGITAL | IOD_TIS_TCP | 00221
TISKlima3VisokaVlaznost | DIGITAL | IOD_TIS_TCP | 00222
TISKlima3VisokTokVVlazilcu | DIGITAL | IOD_TIS_TCP | 00223
TISKlima3Vlazenje | DIGITAL | IOD_TIS_TCP | 00224
TISKlima3VlazilecStatus | INT | IOD_TIS_TCP | 40194
TISKlima3VlaznostProstora | REAL | IOD_TIS_TCP | 44439 | 0 | 100 | 0 | 100 | % | ##
TISKlima3ZamasenFilter | DIGITAL | IOD_TIS_TCP | 00225
TISKlima3ZunanjaTemp | REAL | IOD_TIS_TCP | 44441
TISKlimaAErrors10 | DIGITAL | IOD_TIS_TCP | 00226
TISKlimaAErrors11 | DIGITAL | IOD_TIS_TCP | 00227
TISKlimaAErrors12 | DIGITAL | IOD_TIS_TCP | 00228
TISKlimaAErrors13 | DIGITAL | IOD_TIS_TCP | 00229
TISKlimaAErrors14 | DIGITAL | IOD_TIS_TCP | 00230
TISKlimaAErrors15 | DIGITAL | IOD_TIS_TCP | 00231
TISKlimaAErrors16 | DIGITAL | IOD_TIS_TCP | 00232
TISKlimaAErrors17 | DIGITAL | IOD_TIS_TCP | 00233
TISKlimaAErrors18 | DIGITAL | IOD_TIS_TCP | 00234
TISKlimaAErrors19 | DIGITAL | IOD_TIS_TCP | 00235
TISKlimaAErrors1 | DIGITAL | IOD_TIS_TCP | 00236
TISKlimaAErrors20 | DIGITAL | IOD_TIS_TCP | 00237
TISKlimaAErrors21 | DIGITAL | IOD_TIS_TCP | 00238
TISKlimaAErrors22 | DIGITAL | IOD_TIS_TCP | 00239
TISKlimaAErrors23 | DIGITAL | IOD_TIS_TCP | 00240
TISKlimaAErrors24 | DIGITAL | IOD_TIS_TCP | 00241
TISKlimaAErrors25 | DIGITAL | IOD_TIS_TCP | 00242
TISKlimaAErrors26 | DIGITAL | IOD_TIS_TCP | 00243
TISKlimaAErrors27 | DIGITAL | IOD_TIS_TCP | 00244
TISKlimaAErrors28 | DIGITAL | IOD_TIS_TCP | 00245
TISKlimaAErrors29 | DIGITAL | IOD_TIS_TCP | 00246
TISKlimaAErrors2 | DIGITAL | IOD_TIS_TCP | 00247
TISKlimaAErrors30 | DIGITAL | IOD_TIS_TCP | 00248
TISKlimaAErrors31 | DIGITAL | IOD_TIS_TCP | 00249
TISKlimaAErrors32 | DIGITAL | IOD_TIS_TCP | 00250
TISKlimaAErrors33 | DIGITAL | IOD_TIS_TCP | 00251
TISKlimaAErrors34 | DIGITAL | IOD_TIS_TCP | 00252
TISKlimaAErrors35 | DIGITAL | IOD_TIS_TCP | 00253
TISKlimaAErrors36 | DIGITAL | IOD_TIS_TCP | 00254
TISKlimaAErrors37 | DIGITAL | IOD_TIS_TCP | 00255
TISKlimaAErrors38 | DIGITAL | IOD_TIS_TCP | 00256
TISKlimaAErrors39 | DIGITAL | IOD_TIS_TCP | 00257
TISKlimaAErrors3 | DIGITAL | IOD_TIS_TCP | 00258
TISKlimaAErrors40 | DIGITAL | IOD_TIS_TCP | 00259
TISKlimaAErrors4 | DIGITAL | IOD_TIS_TCP | 00260
TISKlimaAErrors5 | DIGITAL | IOD_TIS_TCP | 00261
TISKlimaAErrors6 | DIGITAL | IOD_TIS_TCP | 00262
TISKlimaAErrors7 | DIGITAL | IOD_TIS_TCP | 00263
TISKlimaAErrors8 | DIGITAL | IOD_TIS_TCP | 00264
TISKlimaAErrors9 | DIGITAL | IOD_TIS_TCP | 00265
TISKlimaBErrors10 | DIGITAL | IOD_TIS_TCP | 00266
TISKlimaBErrors11 | DIGITAL | IOD_TIS_TCP | 00267
TISKlimaBErrors12 | DIGITAL | IOD_TIS_TCP | 00268
TISKlimaBErrors13 | DIGITAL | IOD_TIS_TCP | 00269
TISKlimaBErrors14 | DIGITAL | IOD_TIS_TCP | 00270
TISKlimaBErrors15 | DIGITAL | IOD_TIS_TCP | 00271
TISKlimaBErrors16 | DIGITAL | IOD_TIS_TCP | 00272
TISKlimaBErrors17 | DIGITAL | IOD_TIS_TCP | 00273
TISKlimaBErrors18 | DIGITAL | IOD_TIS_TCP | 00274
TISKlimaBErrors19 | DIGITAL | IOD_TIS_TCP | 00275
TISKlimaBErrors1 | DIGITAL | IOD_TIS_TCP | 00276
TISKlimaBErrors20 | DIGITAL | IOD_TIS_TCP | 00277
TISKlimaBErrors21 | DIGITAL | IOD_TIS_TCP | 00278
TISKlimaBErrors22 | DIGITAL | IOD_TIS_TCP | 00279
TISKlimaBErrors23 | DIGITAL | IOD_TIS_TCP | 00280
TISKlimaBErrors24 | DIGITAL | IOD_TIS_TCP | 00281
TISKlimaBErrors25 | DIGITAL | IOD_TIS_TCP | 00282
TISKlimaBErrors26 | DIGITAL | IOD_TIS_TCP | 00283
TISKlimaBErrors27 | DIGITAL | IOD_TIS_TCP | 00284
TISKlimaBErrors28 | DIGITAL | IOD_TIS_TCP | 00285
TISKlimaBErrors29 | DIGITAL | IOD_TIS_TCP | 00286
TISKlimaBErrors2 | DIGITAL | IOD_TIS_TCP | 00287
TISKlimaBErrors30 | DIGITAL | IOD_TIS_TCP | 00288
TISKlimaBErrors31 | DIGITAL | IOD_TIS_TCP | 00289
TISKlimaBErrors32 | DIGITAL | IOD_TIS_TCP | 00290
TISKlimaBErrors33 | DIGITAL | IOD_TIS_TCP | 00291
TISKlimaBErrors34 | DIGITAL | IOD_TIS_TCP | 00292
TISKlimaBErrors35 | DIGITAL | IOD_TIS_TCP | 00293
TISKlimaBErrors36 | DIGITAL | IOD_TIS_TCP | 00294
TISKlimaBErrors37 | DIGITAL | IOD_TIS_TCP | 00295
TISKlimaBErrors38 | DIGITAL | IOD_TIS_TCP | 00296
TISKlimaBErrors39 | DIGITAL | IOD_TIS_TCP | 00297
TISKlimaBErrors3 | DIGITAL | IOD_TIS_TCP | 00298
TISKlimaBErrors40 | DIGITAL | IOD_TIS_TCP | 00299
TISKlimaBErrors4 | DIGITAL | IOD_TIS_TCP | 00300
TISKlimaBErrors5 | DIGITAL | IOD_TIS_TCP | 00301
TISKlimaBErrors6 | DIGITAL | IOD_TIS_TCP | 00302
TISKlimaBErrors7 | DIGITAL | IOD_TIS_TCP | 00303
TISKlimaBErrors8 | DIGITAL | IOD_TIS_TCP | 00304
TISKlimaBErrors9 | DIGITAL | IOD_TIS_TCP | 00305
TISKlimaCErrors10 | DIGITAL | IOD_TIS_TCP | 00306
TISKlimaCErrors11 | DIGITAL | IOD_TIS_TCP | 00307
TISKlimaCErrors12 | DIGITAL | IOD_TIS_TCP | 00308
TISKlimaCErrors13 | DIGITAL | IOD_TIS_TCP | 00309
TISKlimaCErrors14 | DIGITAL | IOD_TIS_TCP | 00310
TISKlimaCErrors15 | DIGITAL | IOD_TIS_TCP | 00311
TISKlimaCErrors16 | DIGITAL | IOD_TIS_TCP | 00312
TISKlimaCErrors17 | DIGITAL | IOD_TIS_TCP | 00313
TISKlimaCErrors18 | DIGITAL | IOD_TIS_TCP | 00314
TISKlimaCErrors19 | DIGITAL | IOD_TIS_TCP | 00315
TISKlimaCErrors1 | DIGITAL | IOD_TIS_TCP | 00316
TISKlimaCErrors20 | DIGITAL | IOD_TIS_TCP | 00317
TISKlimaCErrors21 | DIGITAL | IOD_TIS_TCP | 00318
TISKlimaCErrors22 | DIGITAL | IOD_TIS_TCP | 00319
TISKlimaCErrors23 | DIGITAL | IOD_TIS_TCP | 00320
TISKlimaCErrors24 | DIGITAL | IOD_TIS_TCP | 00321
TISKlimaCErrors25 | DIGITAL | IOD_TIS_TCP | 00322
TISKlimaCErrors26 | DIGITAL | IOD_TIS_TCP | 00323
TISKlimaCErrors27 | DIGITAL | IOD_TIS_TCP | 00324
TISKlimaCErrors28 | DIGITAL | IOD_TIS_TCP | 00325
TISKlimaCErrors29 | DIGITAL | IOD_TIS_TCP | 00326
TISKlimaCErrors2 | DIGITAL | IOD_TIS_TCP | 00327
TISKlimaCErrors30 | DIGITAL | IOD_TIS_TCP | 00328
TISKlimaCErrors31 | DIGITAL | IOD_TIS_TCP | 00329
TISKlimaCErrors32 | DIGITAL | IOD_TIS_TCP | 00330
TISKlimaCErrors33 | DIGITAL | IOD_TIS_TCP | 00331
TISKlimaCErrors34 | DIGITAL | IOD_TIS_TCP | 00332
TISKlimaCErrors35 | DIGITAL | IOD_TIS_TCP | 00333
TISKlimaCErrors36 | DIGITAL | IOD_TIS_TCP | 00334
TISKlimaCErrors37 | DIGITAL | IOD_TIS_TCP | 00335
TISKlimaCErrors38 | DIGITAL | IOD_TIS_TCP | 00336
TISKlimaCErrors39 | DIGITAL | IOD_TIS_TCP | 00337
TISKlimaCErrors3 | DIGITAL | IOD_TIS_TCP | 00338
TISKlimaCErrors40 | DIGITAL | IOD_TIS_TCP | 00339
TISKlimaCErrors4 | DIGITAL | IOD_TIS_TCP | 00340
TISKlimaCErrors5 | DIGITAL | IOD_TIS_TCP | 00341
TISKlimaCErrors6 | DIGITAL | IOD_TIS_TCP | 00342
TISKlimaCErrors7 | DIGITAL | IOD_TIS_TCP | 00343
TISKlimaCErrors8 | DIGITAL | IOD_TIS_TCP | 00344
TISKlimaCErrors9 | DIGITAL | IOD_TIS_TCP | 00345
TISKlimaGalAlarmKompresor1 | DIGITAL | IOD_TIS_TCP | 00346
TISKlimaGalAlarmKompresor2 | DIGITAL | IOD_TIS_TCP | 00347
TISKlimaGalDeluje | DIGITAL | IOD_TIS_TCP | 00348
TISKlimaGalEnergySaving | DIGITAL | IOD_TIS_TCP | 00349
TISKlimaGalFaultyEPROM | DIGITAL | IOD_TIS_TCP | 00350
TISKlimaGalFenThermalCutout | DIGITAL | IOD_TIS_TCP | 00351
TISKlimaGalGeneralAlarm | DIGITAL | IOD_TIS_TCP | 00352
TISKlimaGalGrelecStatus | INT | IOD_TIS_TCP | 40195
TISKlimaGalIzhodniVentStatus | INT | IOD_TIS_TCP | 40196
TISKlimaGalKompresor1naMejiObrUr | DIGITAL | IOD_TIS_TCP | 00353
TISKlimaGalKompresor2naMejiObrUr | DIGITAL | IOD_TIS_TCP | 00354
TISKlimaGalKompresorStatus | INT | IOD_TIS_TCP | 40197
TISKlimaGalNapaka | DIGITAL | IOD_TIS_TCP | 00355
TISKlimaGalNapakaPriPretokuZraka | DIGITAL | IOD_TIS_TCP | 00356
TISKlimaGalNapakaSenzorPovratVode | DIGITAL | IOD_TIS_TCP | 00357
TISKlimaGalNapakaSenzorTempIzpiha | DIGITAL | IOD_TIS_TCP | 00358
TISKlimaGalNapakaSenzorTempProstora | DIGITAL | IOD_TIS_TCP | 00359
TISKlimaGalNapakaSenzorVlaznosti | DIGITAL | IOD_TIS_TCP | 00360
TISKlimaGalNapakaSenzorZunanjeTemp | DIGITAL | IOD_TIS_TCP | 00361
TISKlimaGalNastMaxTemp | REAL | IOD_TIS_TCP | 44443
TISKlimaGalNastMaxVlaznost | REAL | IOD_TIS_TCP | 44445
TISKlimaGalNastMinTemp | REAL | IOD_TIS_TCP | 44447
TISKlimaGalNastMinVlaznost | REAL | IOD_TIS_TCP | 44449
TISKlimaGalNastTempProstora | REAL | IOD_TIS_TCP | 44451
TISKlimaGalNastVlaznost | REAL | IOD_TIS_TCP | 44453
TISKlimaGalNiTokaVVlazilcu | DIGITAL | IOD_TIS_TCP | 00362
TISKlimaGalNiVodeVVlazilcu | DIGITAL | IOD_TIS_TCP | 00363
TISKlimaGalNizekPritiskKompresor1 | DIGITAL | IOD_TIS_TCP | 00364
TISKlimaGalNizekPritiskKompresor2 | DIGITAL | IOD_TIS_TCP | 00365
TISKlimaGalNizkaTempPovratneVode | DIGITAL | IOD_TIS_TCP | 00366
TISKlimaGalNizkaTempVProstoru | DIGITAL | IOD_TIS_TCP | 00367
TISKlimaGalNizkaVlaznost | DIGITAL | IOD_TIS_TCP | 00368
TISKlimaGalObratovalneUre | REAL | IOD_TIS_TCP | 44455
TISKlimaGalOnOffEnablingBySupervisor | DIGITAL | IOD_TIS_TCP | 00369
TISKlimaGalPozarniAlarm | DIGITAL | IOD_TIS_TCP | 00370
TISKlimaGalRazvlazevanje | DIGITAL | IOD_TIS_TCP | 00371
TISKlimaGalRemoteOFFtoOutput | DIGITAL | IOD_TIS_TCP | 00372
TISKlimaGalRemoteOnOff | DIGITAL | IOD_TIS_TCP | 00373
TISKlimaGalRocniIzklop | DIGITAL | IOD_TIS_TCP | 00374
TISKlimaGalSenzorjiStatus | DIGITAL | IOD_TIS_TCP | 00375
TISKlimaGalStoppedByAlarms | DIGITAL | IOD_TIS_TCP | 00376
TISKlimaGalTemperaturaProstora | REAL | IOD_TIS_TCP | 44457
TISKlimaGalTempIzpihanegaZraka | REAL | IOD_TIS_TCP | 44459
TISKlimaGalTempPovratneVode | REAL | IOD_TIS_TCP | 44461
TISKlimaGalThermalCutoutHeater1 | DIGITAL | IOD_TIS_TCP | 00377
TISKlimaGalThermalCutoutHeater2 | DIGITAL | IOD_TIS_TCP | 00378
TISKlimaGalUnitOnOff | DIGITAL | IOD_TIS_TCP | 00379
TISKlimaGalVentilatorNaMejiObrUr | DIGITAL | IOD_TIS_TCP | 00380
TISKlimaGalVentilGretjeOdpiranje | DIGITAL | IOD_TIS_TCP | 00381
TISKlimaGalVentilGretjeZapiranje | DIGITAL | IOD_TIS_TCP | 00382
TISKlimaGalVentilHlajenjeOdpiranje | DIGITAL | IOD_TIS_TCP | 00383
TISKlimaGalVentilHlajenjeZapiranje | DIGITAL | IOD_TIS_TCP | 00384
TISKlimaGalVisokaTempPovratneVode | DIGITAL | IOD_TIS_TCP | 00385
TISKlimaGalVisokaTempVProstoru | DIGITAL | IOD_TIS_TCP | 00386
TISKlimaGalVisokaVlaznost | DIGITAL | IOD_TIS_TCP | 00387
TISKlimaGalVisokTokVVlazilcu | DIGITAL | IOD_TIS_TCP | 00388
TISKlimaGalVlazenje | DIGITAL | IOD_TIS_TCP | 00389
TISKlimaGalVlazilecStatus | INT | IOD_TIS_TCP | 40198
TISKlimaGalVlaznostProstora | REAL | IOD_TIS_TCP | 44463
TISKlimaGalZamasenFilter | DIGITAL | IOD_TIS_TCP | 00390
TISKlimaGalZunanjaTemp | REAL | IOD_TIS_TCP | 44465
TISKlimeNaCas | DIGITAL | IOD_TIS_TCP | 00391
TISNapakaSenzorTemp10 | DIGITAL | IOD_TIS_TCP | 00392
TISNapakaSenzorTemp11 | DIGITAL | IOD_TIS_TCP | 00393
TISNapakaSenzorTemp12 | DIGITAL | IOD_TIS_TCP | 00394
TISNapakaSenzorTemp13 | DIGITAL | IOD_TIS_TCP | 00395
TISNapakaSenzorTemp14 | DIGITAL | IOD_TIS_TCP | 00396
TISNapakaSenzorTemp15 | DIGITAL | IOD_TIS_TCP | 00397
TISNapakaSenzorTemp16 | DIGITAL | IOD_TIS_TCP | 00398
TISNapakaSenzorTemp17 | DIGITAL | IOD_TIS_TCP | 00399
TISNapakaSenzorTemp18 | DIGITAL | IOD_TIS_TCP | 00400
TISNapakaSenzorTemp19 | DIGITAL | IOD_TIS_TCP | 00401
TISNapakaSenzorTemp1 | DIGITAL | IOD_TIS_TCP | 00402
TISNapakaSenzorTemp2 | DIGITAL | IOD_TIS_TCP | 00403
TISNapakaSenzorTemp3 | DIGITAL | IOD_TIS_TCP | 00404
TISNapakaSenzorTemp4 | DIGITAL | IOD_TIS_TCP | 00405
TISNapakaSenzorTemp5 | DIGITAL | IOD_TIS_TCP | 00406
TISNapakaSenzorTemp6 | DIGITAL | IOD_TIS_TCP | 00407
TISNapakaSenzorTemp7 | DIGITAL | IOD_TIS_TCP | 00408
TISNapakaSenzorTemp8 | DIGITAL | IOD_TIS_TCP | 00409
TISNapakaSenzorTemp9 | DIGITAL | IOD_TIS_TCP | 00410
TISNapakaSenzorVlaga10 | DIGITAL | IOD_TIS_TCP | 00411
TISNapakaSenzorVlaga11 | DIGITAL | IOD_TIS_TCP | 00412
TISNapakaSenzorVlaga12 | DIGITAL | IOD_TIS_TCP | 00413
TISNapakaSenzorVlaga13 | DIGITAL | IOD_TIS_TCP | 00414
TISNapakaSenzorVlaga14 | DIGITAL | IOD_TIS_TCP | 00415
TISNapakaSenzorVlaga15 | DIGITAL | IOD_TIS_TCP | 00416
TISNapakaSenzorVlaga16 | DIGITAL | IOD_TIS_TCP | 00417
TISNapakaSenzorVlaga17 | DIGITAL | IOD_TIS_TCP | 00418
TISNapakaSenzorVlaga18 | DIGITAL | IOD_TIS_TCP | 00419
TISNapakaSenzorVlaga19 | DIGITAL | IOD_TIS_TCP | 00420
TISNapakaSenzorVlaga1 | DIGITAL | IOD_TIS_TCP | 00421
TISNapakaSenzorVlaga2 | DIGITAL | IOD_TIS_TCP | 00422
TISNapakaSenzorVlaga3 | DIGITAL | IOD_TIS_TCP | 00423
TISNapakaSenzorVlaga4 | DIGITAL | IOD_TIS_TCP | 00424
TISNapakaSenzorVlaga5 | DIGITAL | IOD_TIS_TCP | 00425
TISNapakaSenzorVlaga6 | DIGITAL | IOD_TIS_TCP | 00426
TISNapakaSenzorVlaga7 | DIGITAL | IOD_TIS_TCP | 00427
TISNapakaSenzorVlaga8 | DIGITAL | IOD_TIS_TCP | 00428
TISNapakaSenzorVlaga9 | DIGITAL | IOD_TIS_TCP | 00429
TISQstanje10 | INT | IOD_TIS_TCP | 40199
TISQstanje1 | INT | IOD_TIS_TCP | 40200
TISQstanje2 | INT | IOD_TIS_TCP | 40201
TISQstanje3 | INT | IOD_TIS_TCP | 40202
TISQstanje4 | INT | IOD_TIS_TCP | 40203
TISQstanje5 | INT | IOD_TIS_TCP | 40204
TISQstanje6 | INT | IOD_TIS_TCP | 40205
TISQstanje7 | INT | IOD_TIS_TCP | 40206
TISQstanje8 | INT | IOD_TIS_TCP | 40207
TISQstanje9 | INT | IOD_TIS_TCP | 40208
TISSenzorTemp10 | REAL | IOD_TIS_TCP | 44467 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp11 | REAL | IOD_TIS_TCP | 44469 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp12 | REAL | IOD_TIS_TCP | 44471 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp13 | REAL | IOD_TIS_TCP | 44473 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp14 | REAL | IOD_TIS_TCP | 44475 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp15 | REAL | IOD_TIS_TCP | 44477 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp16 | REAL | IOD_TIS_TCP | 44479 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp17 | REAL | IOD_TIS_TCP | 44481 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp18 | REAL | IOD_TIS_TCP | 44483 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp19 | REAL | IOD_TIS_TCP | 44485 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp1 | REAL | IOD_TIS_TCP | 44487 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp2 | REAL | IOD_TIS_TCP | 44489 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp3 | REAL | IOD_TIS_TCP | 44491 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp4 | REAL | IOD_TIS_TCP | 44493 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp5 | REAL | IOD_TIS_TCP | 44495 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp6 | REAL | IOD_TIS_TCP | 44497 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp7 | REAL | IOD_TIS_TCP | 44499 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp8 | REAL | IOD_TIS_TCP | 44501 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorTemp9 | REAL | IOD_TIS_TCP | 44503 | 0 | 60 | 0 | 60 | °C | ##.#
TISSenzorVlaga10 | REAL | IOD_TIS_TCP | 44505 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga11 | REAL | IOD_TIS_TCP | 44507 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga12 | REAL | IOD_TIS_TCP | 44509 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga13 | REAL | IOD_TIS_TCP | 44511 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga14 | REAL | IOD_TIS_TCP | 44513 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga15 | REAL | IOD_TIS_TCP | 44515 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga16 | REAL | IOD_TIS_TCP | 44517 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga17 | REAL | IOD_TIS_TCP | 44519 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga18 | REAL | IOD_TIS_TCP | 44521 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga19 | REAL | IOD_TIS_TCP | 44523 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga1 | REAL | IOD_TIS_TCP | 44525 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga2 | REAL | IOD_TIS_TCP | 44527 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga3 | REAL | IOD_TIS_TCP | 44529 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga4 | REAL | IOD_TIS_TCP | 44531 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga5 | REAL | IOD_TIS_TCP | 44533 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga6 | REAL | IOD_TIS_TCP | 44535 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga7 | REAL | IOD_TIS_TCP | 44537 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga8 | REAL | IOD_TIS_TCP | 44539 | 0 | 100 | 0 | 100 | % | ##.#
TISSenzorVlaga9 | REAL | IOD_TIS_TCP | 44541 | 0 | 100 | 0 | 100 | % | ##.#
TISSetDateTime | DIGITAL | IOD_TIS_TCP | 00430
TISSetDateTimeDemand | DIGITAL | IOD_TIS_TCP | 00431
TISSetDateTimeError | DIGITAL | IOD_TIS_TCP | 00432
TISSetDateTimeFinished | DIGITAL | IOD_TIS_TCP | 00433
TISSetRemoteOnOff1 | DIGITAL | IOD_TIS_TCP | 00434
TISSetRemoteOnOff2 | DIGITAL | IOD_TIS_TCP | 00435
TISSetRemoteOnOff3 | DIGITAL | IOD_TIS_TCP | 00436
TISSlabaBaterijaPLC_A1 | DIGITAL | IOD_TIS_TCP | 00437
TISTempAlarmPoint1 | REAL | IOD_TIS_TCP | 44543 | 0 | 60 | 0 | 60 | °C | ##
TISTempAlarmPoint2 | REAL | IOD_TIS_TCP | 44545 | 0 | 60 | 0 | 60 | °C | ##
TISTempAlarmPoint3 | REAL | IOD_TIS_TCP | 44547 | 0 | 60 | 0 | 60 | °C | ##
TISTempMaxPoint1 | REAL | IOD_TIS_TCP | 44549 | 0 | 60 | 0 | 60 | °C | ##
TISTempMaxPoint2 | REAL | IOD_TIS_TCP | 44551 | 0 | 60 | 0 | 60 | °C | ##
TISTempMaxPoint3 | REAL | IOD_TIS_TCP | 44553 | 0 | 60 | 0 | 60 | °C | ##
TISTempPovp1 | REAL | IOD_TIS_TCP | 44555 | 0 | 60 | 0 | 60 | °C | ##.#
TISTempPovp2 | REAL | IOD_TIS_TCP | 44557 | 0 | 60 | 0 | 60 | °C | ##.#
TISTempPovp3 | REAL | IOD_TIS_TCP | 44559 | 0 | 60 | 0 | 60 | °C | ##.#
TISTempPovp4 | REAL | IOD_TIS_TCP | 44561 | 0 | 60 | 0 | 60 | °C | ##.#
TISTempPovp5 | REAL | IOD_TIS_TCP | 44563 | 0 | 60 | 0 | 60 | °C | ##.#
TISTempSetPoint1 | REAL | IOD_TIS_TCP | 44565 | 0 | 60 | 0 | 60 | °C | ##
TISTempSetPoint2 | REAL | IOD_TIS_TCP | 44567 | 0 | 60 | 0 | 60 | °C | ##
TISTempSetPoint3 | REAL | IOD_TIS_TCP | 44569 | 0 | 60 | 0 | 60 | °C | ##
TISTempTSprevisoka10 | DIGITAL | IOD_TIS_TCP | 00438
TISTempTSprevisoka11 | DIGITAL | IOD_TIS_TCP | 00439
TISTempTSprevisoka12 | DIGITAL | IOD_TIS_TCP | 00440
TISTempTSprevisoka13 | DIGITAL | IOD_TIS_TCP | 00441
TISTempTSprevisoka14 | DIGITAL | IOD_TIS_TCP | 00442
TISTempTSprevisoka15 | DIGITAL | IOD_TIS_TCP | 00443
TISTempTSprevisoka16 | DIGITAL | IOD_TIS_TCP | 00444
TISTempTSprevisoka17 | DIGITAL | IOD_TIS_TCP | 00445
TISTempTSprevisoka18 | DIGITAL | IOD_TIS_TCP | 00446
TISTempTSprevisoka19 | DIGITAL | IOD_TIS_TCP | 00447
TISTempTSprevisoka1 | DIGITAL | IOD_TIS_TCP | 00448
TISTempTSprevisoka2 | DIGITAL | IOD_TIS_TCP | 00449
TISTempTSprevisoka3 | DIGITAL | IOD_TIS_TCP | 00450
TISTempTSprevisoka4 | DIGITAL | IOD_TIS_TCP | 00451
TISTempTSprevisoka5 | DIGITAL | IOD_TIS_TCP | 00452
TISTempTSprevisoka6 | DIGITAL | IOD_TIS_TCP | 00453
TISTempTSprevisoka7 | DIGITAL | IOD_TIS_TCP | 00454
TISTempTSprevisoka8 | DIGITAL | IOD_TIS_TCP | 00455
TISTempTSprevisoka9 | DIGITAL | IOD_TIS_TCP | 00456
TISUserCurrentLevel | INT | IOD_TIS_TCP | 40209
TISUserCurrentName | STRING | IOD_TIS_TCP | 45061[15]
TISUserLoggedIn | DIGITAL | IOD_TIS_TCP | 00457
TISVlagaPovp1 | REAL | IOD_TIS_TCP | 44571 | 0 | 100 | 0 | 100 | % | ##.#
TISVlagaPovp2 | REAL | IOD_TIS_TCP | 44573 | 0 | 100 | 0 | 100 | % | ##.#
TISVlagaPovp3 | REAL | IOD_TIS_TCP | 44575 | 0 | 100 | 0 | 100 | % | ##.#
TISVlagaPovp4 | REAL | IOD_TIS_TCP | 44577 | 0 | 100 | 0 | 100 | % | ##.#
TISVlagaPovp5 | REAL | IOD_TIS_TCP | 44579 | 0 | 100 | 0 | 100 | % | ##.#
TISXVH_AlarmOn | DIGITAL | IOD_TIS_TCP | 00458
TISXVH_CircNumber | INT | IOD_TIS_TCP | 40210
TISXVH_GrafTemp1 | REAL | IOD_TIS_TCP | 44581
TISXVH_GrafTemp2 | REAL | IOD_TIS_TCP | 44583
TISXVH_GrafTemp3 | REAL | IOD_TIS_TCP | 44585
TISXVH_GrafTemp4 | REAL | IOD_TIS_TCP | 44587
TISXVH_GrafTemp5 | REAL | IOD_TIS_TCP | 44589
TISXVH_GrafVlaga1 | REAL | IOD_TIS_TCP | 44591
TISXVH_GrafVlaga2 | REAL | IOD_TIS_TCP | 44593
TISXVH_GrafVlaga3 | REAL | IOD_TIS_TCP | 44595
TISXVH_GrafVlaga4 | REAL | IOD_TIS_TCP | 44597
TISXVH_GrafVlaga5 | REAL | IOD_TIS_TCP | 44599
TISXVH_KlimaNumber | INT | IOD_TIS_TCP | 40211
TISXVH_NastTempProstora1 | REAL | IOD_TIS_TCP | 44601
TISXVH_NastTempProstora2 | REAL | IOD_TIS_TCP | 44603
TISXVH_NastTempProstora3 | REAL | IOD_TIS_TCP | 44605
TISXVH_ObratovalneUre1 | REAL | IOD_TIS_TCP | 44607
TISXVH_ObratovalneUre2 | REAL | IOD_TIS_TCP | 44609
TISXVH_ObratovalneUre3 | REAL | IOD_TIS_TCP | 44611
TISXVH_PripravaVodeStat1 | INT | IOD_TIS_TCP | 40212
TISXVH_PripravaVodeStat2 | INT | IOD_TIS_TCP | 40213
TISXVH_RemoteStatus1 | DIGITAL | IOD_TIS_TCP | 00459
TISXVH_RemoteStatus2 | DIGITAL | IOD_TIS_TCP | 00460
TISXVH_RemoteStatus3 | DIGITAL | IOD_TIS_TCP | 00461
TISXVH_setCircNum1 | DIGITAL | IOD_TIS_TCP | 00462
TISXVH_setCircNum2 | DIGITAL | IOD_TIS_TCP | 00463
TISXVH_setCircNum3 | DIGITAL | IOD_TIS_TCP | 00464
TISXVH_setCircNum4 | DIGITAL | IOD_TIS_TCP | 00465
TISXVH_setCircNum5 | DIGITAL | IOD_TIS_TCP | 00466
TISXVH_setKlimaNum1 | DIGITAL | IOD_TIS_TCP | 00467
TISXVH_setKlimaNum2 | DIGITAL | IOD_TIS_TCP | 00468
TISXVH_setKlimaNum3 | DIGITAL | IOD_TIS_TCP | 00469
TISXVH_setKlimaNum4 | DIGITAL | IOD_TIS_TCP | 00470
TISXVH_setKlimaNum5 | DIGITAL | IOD_TIS_TCP | 00471
TISXVH_setKlimaNum6 | DIGITAL | IOD_TIS_TCP | 00472
TISXVH_UPSstatus | INT | IOD_TIS_TCP | 40214
TISXVH_VlazilecStatus1 | INT | IOD_TIS_TCP | 40215
TISXVH_VlazilecStatus2 | INT | IOD_TIS_TCP | 40216
TISXVH_VlazilecStatus3 | INT | IOD_TIS_TCP | 40217
TISXVHhighHum | REAL | IOD_TIS_TCP | 44613
TISXVHhighTemp | REAL | IOD_TIS_TCP | 44615
TISXVHlowHum | REAL | IOD_TIS_TCP | 44617
TISXVHlowTemp | REAL | IOD_TIS_TCP | 44619
TISXVHnum10 | INT | IOD_TIS_TCP | 40218
TISXVHnum11 | INT | IOD_TIS_TCP | 40219
TISXVHnum12 | INT | IOD_TIS_TCP | 40220
TISXVHnum13 | INT | IOD_TIS_TCP | 40221
TISXVHnum14 | INT | IOD_TIS_TCP | 40222
TISXVHnum1 | INT | IOD_TIS_TCP | 40223
TISXVHnum2 | INT | IOD_TIS_TCP | 40224
TISXVHnum3 | INT | IOD_TIS_TCP | 40225
TISXVHnum4 | INT | IOD_TIS_TCP | 40226
TISXVHnum5 | INT | IOD_TIS_TCP | 40227
TISXVHnum6 | INT | IOD_TIS_TCP | 40228
TISXVHnum7 | INT | IOD_TIS_TCP | 40229
TISXVHnum8 | INT | IOD_TIS_TCP | 40230
TISXVHnum9 | INT | IOD_TIS_TCP | 40231
TIS_DanEnergCircE_G3 | REAL | IOD_TIS_disk | R0[30]
TIS_CasDDanEnergCircE_G3 | INT | IOD_TIS_disk | I30[30]
TIS_CasMDanEnergCircE_G3 | INT | IOD_TIS_disk | I60[30]
TIS_TedenEnergCircE_G3 | REAL | IOD_TIS_disk | R3374[30]
TIS_CasDTedenEnergCircE_G3 | INT | IOD_TIS_disk | I120[30]
TIS_CasMTedenEnergCircE_G3 | INT | IOD_TIS_disk | I150[30]
TIS_MesecEnergCircE_G3 | REAL | IOD_TIS_disk | R3404[30]
TIS_CasDMesecEnergCircE_G3 | INT | IOD_TIS_disk | I210[30]
TIS_CasMMesecEnergCircE_G3 | INT | IOD_TIS_disk | I240[30]
TIS_StSt_DanEnergCircE_G3 | REAL | IOD_TIS_disk | R3434
TIS_StSt_TedenEnergCircE_G3 | REAL | IOD_TIS_disk | R3438
TIS_StSt_MesecEnergCircE_G3 | REAL | IOD_TIS_disk | R3442
TIS_StStCasDDanEnergCircE_G3 | INT | IOD_TIS_disk | I276
TIS_StStCasMDanEnergCircE_G3 | INT | IOD_TIS_disk | I278
TIS_StStCasDTedenEnergCircE_G3 | INT | IOD_TIS_disk | I280
TIS_StStCasMTedenEnergCircE_G3 | INT | IOD_TIS_disk | I282
TIS_StStCasDMesecEnergCircE_G3 | INT | IOD_TIS_disk | I284
TIS_StStCasMMesecEnergCircE_G3 | INT | IOD_TIS_disk | I286
TIS_DanEnergCircE_DG3 | REAL | IOD_TIS_disk | R3446[30]
TIS_CasDDanEnergCircE_DG3 | INT | IOD_TIS_disk | I318[30]
TIS_CasMDanEnergCircE_DG3 | INT | IOD_TIS_disk | I358[30]
TIS_TedenEnergCircE_DG3 | REAL | IOD_TIS_disk | R3476[30]
TIS_CasDTedenEnergCircE_DG3 | INT | IOD_TIS_disk | I418[30]
TIS_CasMTedenEnergCircE_DG3 | INT | IOD_TIS_disk | I448[30]
TIS_MesecEnergCircE_DG3 | REAL | IOD_TIS_disk | R3506[30]
TIS_CasDMesecEnergCircE_DG3 | INT | IOD_TIS_disk | I508[30]
TIS_CasMMesecEnergCircE_DG3 | INT | IOD_TIS_disk | I538[30]
TIS_StSt_DanEnergCircE_DG3 | REAL | IOD_TIS_disk | R3536
TIS_StSt_TedenEnergCircE_DG3 | REAL | IOD_TIS_disk | R3540
TIS_StSt_MesecEnergCircE_DG3 | REAL | IOD_TIS_disk | R3544
TIS_StStCasDDanEnergCircE_DG3 | INT | IOD_TIS_disk | I574
TIS_StStCasMDanEnergCircE_DG3 | INT | IOD_TIS_disk | I576
TIS_StStCasDTedenEnergCircE_DG3 | INT | IOD_TIS_disk | I578
TIS_StStCasMTedenEnergCircE_DG3 | INT | IOD_TIS_disk | I580
TIS_StStCasDMesecEnergCircE_DG3 | INT | IOD_TIS_disk | I582
TIS_StStCasMMesecEnergCircE_DG3 | INT | IOD_TIS_disk | I584
TIS_DanEnergCircE_UPS3 | REAL | IOD_TIS_disk | R3550[30]
TIS_CasDDanEnergCircE_UPS3 | INT | IOD_TIS_disk | I644[30]
TIS_CasMDanEnergCircE_UPS3 | INT | IOD_TIS_disk | I674[30]
TIS_TedenEnergCircE_UPS3 | REAL | IOD_TIS_disk | R3580[30]
TIS_CasDTedenEnergCircE_UPS3 | INT | IOD_TIS_disk | I734[30]
TIS_CasMTedenEnergCircE_UPS3 | INT | IOD_TIS_disk | I764[30]
TIS_MesecEnergCircE_UPS3 | REAL | IOD_TIS_disk | R3610[30]
TIS_CasDMesecEnergCircE_UPS3 | INT | IOD_TIS_disk | I824[30]
TIS_CasMMesecEnergCircE_UPS3 | INT | IOD_TIS_disk | I854[30]
TIS_StSt_DanEnergCircE_UPS3 | REAL | IOD_TIS_disk | R3640
TIS_StSt_TedenEnergCircE_UPS3 | REAL | IOD_TIS_disk | R3644
TIS_StSt_MesecEnergCircE_UPS3 | REAL | IOD_TIS_disk | R3648
TIS_StStCasDDanEnergCircE_UPS3 | INT | IOD_TIS_disk | I870
TIS_StStCasMDanEnergCircE_UPS3 | INT | IOD_TIS_disk | I872
TIS_StStCasDTedenEnergCircE_UPS3 | INT | IOD_TIS_disk | I874
TIS_StStCasMTedenEnergCircE_UPS3 | INT | IOD_TIS_disk | I876
TIS_StStCasDMesecEnergCircE_UPS3 | INT | IOD_TIS_disk | I878
TIS_StStCasMMesecEnergCircE_UPS3 | INT | IOD_TIS_disk | I880
TIS_DanEnergCircE_DG4 | REAL | IOD_TIS_disk | R3650[30]
TIS_CasDDanEnergCircE_DG4 | INT | IOD_TIS_disk | I940[30]
TIS_CasMDanEnergCircE_DG4 | INT | IOD_TIS_disk | I970[30]
TIS_TedenEnergCircE_DG4 | REAL | IOD_TIS_disk | R3680[30]
TIS_CasDTedenEnergCircE_DG4 | INT | IOD_TIS_disk | I940[30]
TIS_CasMTedenEnergCircE_DG4 | INT | IOD_TIS_disk | I970[30]
TIS_MesecEnergCircE_DG4 | REAL | IOD_TIS_disk | R3710[30]
TIS_CasDMesecEnergCircE_DG4 | INT | IOD_TIS_disk | I1030[30]
TIS_CasMMesecEnergCircE_DG4 | INT | IOD_TIS_disk | I1060[30]
TIS_StSt_DanEnergCircE_DG4 | REAL | IOD_TIS_disk | R3740
TIS_StSt_TedenEnergCircE_DG4 | REAL | IOD_TIS_disk | R3744
TIS_StSt_MesecEnergCircE_DG4 | REAL | IOD_TIS_disk | R3748
TIS_StStCasDDanEnergCircE_DG4 | INT | IOD_TIS_disk | I1098
TIS_StStCasMDanEnergCircE_DG4 | INT | IOD_TIS_disk | I1100
TIS_StStCasDTedenEnergCircE_DG4 | INT | IOD_TIS_disk | I1102
TIS_StStCasMTedenEnergCircE_DG4 | INT | IOD_TIS_disk | I1104
TIS_StStCasDMesecEnergCircE_DG4 | INT | IOD_TIS_disk | I1106
TIS_StStCasMMesecEnergCircE_DG4 | INT | IOD_TIS_disk | I1108
TIS_MaxDnevnaEnergijaE_DG4 | REAL | IOD_TIS_disk | R3750 | [5 empty] | ##########
TIS_MaxTedenskaEnergijaE_DG4 | REAL | IOD_TIS_disk | R3752 | [5 empty] | ##########
TIS_MaxMesecnaEnergijaE_DG4 | REAL | IOD_TIS_disk | R3754 | [5 empty] | ##########
TIS_MaxDnevnaEnergijaE_G3 | REAL | IOD_TIS_disk | R3756 | [5 empty] | ##########
TIS_MaxTedenskaEnergijaE_G3 | REAL | IOD_TIS_disk | R3758 | [5 empty] | ##########
TIS_MaxMesecnaEnergijaE_G3 | REAL | IOD_TIS_disk | R3760 | [5 empty] | ##########
TIS_MaxDnevnaEnergijaE_DG3 | REAL | IOD_TIS_disk | R3762 | [5 empty] | ##########
TIS_MaxTedenskaEnergijaE_DG3 | REAL | IOD_TIS_disk | R3764 | [5 empty] | ##########
TIS_MaxMesecnaEnergijaE_DG3 | REAL | IOD_TIS_disk | R3766 | [5 empty] | ##########
TIS_MaxDnevnaEnergijaE_UPS3 | REAL | IOD_TIS_disk | R3768 | [5 empty] | ##########
TIS_MaxTedenskaEnergijaE_UPS3 | REAL | IOD_TIS_disk | R3770 | [5 empty] | ##########
TIS_MaxMesecnaEnergijaE_UPS3 | REAL | IOD_TIS_disk | R3772 | [5 empty] | ##########
TIS_Sekunda1s_utripanje | DIGITAL | IOD_TIS_mem | D1134
TISNacDelovanjaKlimeAvtomatsko | DIGITAL | IOD_TIS_mem | D1135
TISComSCADA_stevec2 | INT | IOD_TIS_mem | I1136
TISComSCADA_stevec1 | INT | IOD_TIS_mem | I1138
TIS_meja_tok_opozorilo | DIGITAL | IOD_TIS_disk | D1140[14]
TIS_meja_tok_alarm | DIGITAL | IOD_TIS_disk | D1154[14]
TIS_omogocanje_tok_opozorila | DIGITAL | IOD_TIS_disk | D1200
TIS_omogocanje_tok_alarm | DIGITAL | IOD_TIS_disk | D1201
TIS_ComScadaPlc_omog | DIGITAL | IOD_TIS_disk | D1202
TISErrComPanelPLC_omog | DIGITAL | IOD_TIS_disk | D1203
TISErrComPort2_omog | DIGITAL | IOD_TIS_disk | D1204
TISErrComCirc1_omog | DIGITAL | IOD_TIS_disk | D1205
TISErrComCirc2_omog | DIGITAL | IOD_TIS_disk | D1206
TISErrComCirc3_omog | DIGITAL | IOD_TIS_disk | D1207
TISErrComCirc4_omog | DIGITAL | IOD_TIS_disk | D1208
TISErrComCirc5_omog | DIGITAL | IOD_TIS_disk | D1209
TISErrComKlima2_omog | DIGITAL | IOD_TIS_disk | D1210
TISErrComKlima3_omog | DIGITAL | IOD_TIS_disk | D1211
TISDIN_F1_OdklHlOm1_IZP_omog | DIGITAL | IOD_TIS_disk | D1212
TISDIN_F2_OdklHlOm2_IZP_omog | DIGITAL | IOD_TIS_disk | D1213
TISDIN_F3_OdklHlOm3_IZP_omog | DIGITAL | IOD_TIS_disk | D1214
TISDIN_F4_OdkPripVode_IZP_omog | DIGITAL | IOD_TIS_disk | D1215
TISDI_HladOmara1_ERR_omog | DIGITAL | IOD_TIS_disk | D1216
TISDI_HladOmara2_ERR_omog | DIGITAL | IOD_TIS_disk | D1217
TISDI_HladOmara3_ERR_omog | DIGITAL | IOD_TIS_disk | D1218
TISDI_Vlazilec1_ERR_omog | DIGITAL | IOD_TIS_disk | D1219
TISDI_Vlazilec2_ERR_omog | DIGITAL | IOD_TIS_disk | D1220
TISDI_Vlazilec3_ERR_omog | DIGITAL | IOD_TIS_disk | D1221
TISDIN_PripVode1_ERR_omog | DIGITAL | IOD_TIS_disk | D1222
TISDIN_PripVode2_ERR_omog | DIGITAL | IOD_TIS_disk | D1223
TISDI_UPS_Alarm_omog | DIGITAL | IOD_TIS_disk | D1224
TISDIN_RazlitjeVodeHO1_omog | DIGITAL | IOD_TIS_disk | D1225
TISDIN_RazlitjeVodeHO2_omog | DIGITAL | IOD_TIS_disk | D1226
TISDIN_RazlitjeVodeHO3_omog | DIGITAL | IOD_TIS_disk | D1227
TISSetDateTimeError_omog | DIGITAL | IOD_TIS_disk | D1228
TISSlabaBaterijaPLC_A1_omog | DIGITAL | IOD_TIS_disk | D1229
TISTempTSprevisoka1_omog | DIGITAL | IOD_TIS_disk | D1230
TISTempTSprevisoka2_omog | DIGITAL | IOD_TIS_disk | D1231
TISTempTSprevisoka3_omog | DIGITAL | IOD_TIS_disk | D1232
TISTempTSprevisoka4_omog | DIGITAL | IOD_TIS_disk | D1233
TISTempTSprevisoka5_omog | DIGITAL | IOD_TIS_disk | D1234
TISTempTSprevisoka6_omog | DIGITAL | IOD_TIS_disk | D1235
TISTempTSprevisoka7_omog | DIGITAL | IOD_TIS_disk | D1236
TISTempTSprevisoka8_omog | DIGITAL | IOD_TIS_disk | D1237
TISTempTSprevisoka9_omog | DIGITAL | IOD_TIS_disk | D1238
TISTempTSprevisoka10_omog | DIGITAL | IOD_TIS_disk | D1239
TISTempTSprevisoka11_omog | DIGITAL | IOD_TIS_disk | D1240
TISTempTSprevisoka12_omog | DIGITAL | IOD_TIS_disk | D1241
TISTempTSprevisoka13_omog | DIGITAL | IOD_TIS_disk | D1242
TISTempTSprevisoka14_omog | DIGITAL | IOD_TIS_disk | D1243
TISTempTSprevisoka15_omog | DIGITAL | IOD_TIS_disk | D1244
TISTempTSprevisoka16_omog | DIGITAL | IOD_TIS_disk | D1245
TISTempTSprevisoka17_omog | DIGITAL | IOD_TIS_disk | D1246
TISTempTSprevisoka18_omog | DIGITAL | IOD_TIS_disk | D1247
TISTempTSprevisoka19_omog | DIGITAL | IOD_TIS_disk | D1248
TISNapakaSenzorTemp1_omog | DIGITAL | IOD_TIS_disk | D1249
TISNapakaSenzorTemp2_omog | DIGITAL | IOD_TIS_disk | D1250
TISNapakaSenzorTemp3_omog | DIGITAL | IOD_TIS_disk | D1251
TISNapakaSenzorTemp4_omog | DIGITAL | IOD_TIS_disk | D1252
TISNapakaSenzorTemp5_omog | DIGITAL | IOD_TIS_disk | D1253
TISNapakaSenzorTemp6_omog | DIGITAL | IOD_TIS_disk | D1254
TISNapakaSenzorTemp7_omog | DIGITAL | IOD_TIS_disk | D1255
TISNapakaSenzorTemp8_omog | DIGITAL | IOD_TIS_disk | D1256
TISNapakaSenzorTemp9_omog | DIGITAL | IOD_TIS_disk | D1257
TISNapakaSenzorTemp10_omog | DIGITAL | IOD_TIS_disk | D1258
TISNapakaSenzorTemp11_omog | DIGITAL | IOD_TIS_disk | D1259
TISNapakaSenzorTemp12_omog | DIGITAL | IOD_TIS_disk | D1260
TISNapakaSenzorTemp13_omog | DIGITAL | IOD_TIS_disk | D1261
TISNapakaSenzorTemp14_omog | DIGITAL | IOD_TIS_disk | D1262
TISNapakaSenzorTemp15_omog | DIGITAL | IOD_TIS_disk | D1263
TISNapakaSenzorTemp16_omog | DIGITAL | IOD_TIS_disk | D1264
TISNapakaSenzorTemp17_omog | DIGITAL | IOD_TIS_disk | D1265
TISNapakaSenzorTemp18_omog | DIGITAL | IOD_TIS_disk | D1266
TISNapakaSenzorTemp19_omog | DIGITAL | IOD_TIS_disk | D1267
TISNapakaSenzorVlaga1_omog | DIGITAL | IOD_TIS_disk | D1268
TISNapakaSenzorVlaga2_omog | DIGITAL | IOD_TIS_disk | D1269
TISNapakaSenzorVlaga3_omog | DIGITAL | IOD_TIS_disk | D1270
TISNapakaSenzorVlaga4_omog | DIGITAL | IOD_TIS_disk | D1271
TISNapakaSenzorVlaga5_omog | DIGITAL | IOD_TIS_disk | D1272
TISNapakaSenzorVlaga6_omog | DIGITAL | IOD_TIS_disk | D1273
TISNapakaSenzorVlaga7_omog | DIGITAL | IOD_TIS_disk | D1274
TISNapakaSenzorVlaga8_omog | DIGITAL | IOD_TIS_disk | D1275
TISNapakaSenzorVlaga9_omog | DIGITAL | IOD_TIS_disk | D1276
TISNapakaSenzorVlaga10_omog | DIGITAL | IOD_TIS_disk | D1277
TISNapakaSenzorVlaga11_omog | DIGITAL | IOD_TIS_disk | D1278
TISNapakaSenzorVlaga12_omog | DIGITAL | IOD_TIS_disk | D1279
TISNapakaSenzorVlaga13_omog | DIGITAL | IOD_TIS_disk | D1280
TISNapakaSenzorVlaga14_omog | DIGITAL | IOD_TIS_disk | D1281
TISNapakaSenzorVlaga15_omog | DIGITAL | IOD_TIS_disk | D1282
TISNapakaSenzorVlaga16_omog | DIGITAL | IOD_TIS_disk | D1283
TISNapakaSenzorVlaga17_omog | DIGITAL | IOD_TIS_disk | D1284
TISNapakaSenzorVlaga18_omog | DIGITAL | IOD_TIS_disk | D1285
TISNapakaSenzorVlaga19_omog | DIGITAL | IOD_TIS_disk | D1286
TISKlima1AlarmKompresor1_omog | DIGITAL | IOD_TIS_disk | D1287
TISKlima1AlarmKompresor2_omog | DIGITAL | IOD_TIS_disk | D1288
TISKlima1NizekPritiskKompresor1_omog | DIGITAL | IOD_TIS_disk | D1289
TISKlima1NizekPritiskKompresor2_omog | DIGITAL | IOD_TIS_disk | D1290
TISKlima1NapakaPriPretokuZraka_omog | DIGITAL | IOD_TIS_disk | D1291
TISKlima1FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1292
TISKlima1ThermalCutoutHeater1_omog | DIGITAL | IOD_TIS_disk | D1293
TISKlima1ThermalCutoutHeater2_omog | DIGITAL | IOD_TIS_disk | D1294
TISKlima1PozarniAlarm_omog | DIGITAL | IOD_TIS_disk | D1295
TISKlima1ZamasenFilter_omog | DIGITAL | IOD_TIS_disk | D1296
TISKlima1VisokaTempVProstoru_omog | DIGITAL | IOD_TIS_disk | D1297
TISKlima1NizkaTempVProstoru_omog | DIGITAL | IOD_TIS_disk | D1298
TISKlima1VisokaVlaznost_omog | DIGITAL | IOD_TIS_disk | D1299
TISKlima1NizkaVlaznost_omog | DIGITAL | IOD_TIS_disk | D1300
TISKlima1Kompresor1naMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1301
TISKlima1Kompresor2naMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1302
TISKlima1VentilatorNaMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1303
TISKlima1NapakaSenzorTempProstora_omog | DIGITAL | IOD_TIS_disk | D1304
TISKlima1NapakaSenzorPovratVode_omog | DIGITAL | IOD_TIS_disk | D1305
TISKlima1NapakaSenzorZunanjeTemp_omog | DIGITAL | IOD_TIS_disk | D1306
TISKlima1NapakaSenzorTempIzpiha_omog | DIGITAL | IOD_TIS_disk | D1307
TISKlima1NapakaSenzorVlaznosti_omog | DIGITAL | IOD_TIS_disk | D1308
TISKlima1NapakaSenzorPritiska1_omog | DIGITAL | IOD_TIS_disk | D1309
TISKlima1NapakaSenzorPritiska2_omog | DIGITAL | IOD_TIS_disk | D1310
TISKlima1NapakaSenzorKondTemp1_omog | DIGITAL | IOD_TIS_disk | D1311
TISKlima1NapakaSenzorKondTemp2_omog | DIGITAL | IOD_TIS_disk | D1312
TISKlima1VisokTokVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1313
TISKlima1NiVodeVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1314
TISKlima1NiTokaVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1315
TISKlima1ClockCardFault_omog | DIGITAL | IOD_TIS_disk | D1316
TISKlima1VisokPritiskVKrogu1_omog | DIGITAL | IOD_TIS_disk | D1317
TISKlima1VisokPritiskVKrogu2_omog | DIGITAL | IOD_TIS_disk | D1318
TISKlima1IzlivVode_omog | DIGITAL | IOD_TIS_disk | D1319
TISKlima1ZunanjiAlarm_omog | DIGITAL | IOD_TIS_disk | D1320
TISKlima1TermZascVisokPritiskKpr1_omog | DIGITAL | IOD_TIS_disk | D1321
TISKlima1VlazilecNaMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1322
TISKlima1TermZascVisokPritiskKpr2_omog | DIGITAL | IOD_TIS_disk | D1323
TISKlima1Kond1FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1324
TISKlima1Kond2FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1325
TISKlima1NapakaPriPretokuVode_omog | DIGITAL | IOD_TIS_disk | D1326
TISKlima1RocniIzklop_omog | DIGITAL | IOD_TIS_disk | D1327
TISKlima1Napaka_omog | DIGITAL | IOD_TIS_disk | D1328
TISKlima2AlarmKompresor1_omog | DIGITAL | IOD_TIS_disk | D1329
TISKlima2AlarmKompresor2_omog | DIGITAL | IOD_TIS_disk | D1330
TISKlima2NizekPritiskKompresor1_omog | DIGITAL | IOD_TIS_disk | D1331
TISKlima2NizekPritiskKompresor2_omog | DIGITAL | IOD_TIS_disk | D1332
TISKlima2NapakaPriPretokuZraka_omog | DIGITAL | IOD_TIS_disk | D1333
TISKlima2FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1334
TISKlima2ThermalCutoutHeater1_omog | DIGITAL | IOD_TIS_disk | D1335
TISKlima2ThermalCutoutHeater2_omog | DIGITAL | IOD_TIS_disk | D1336
TISKlima2PozarniAlarm_omog | DIGITAL | IOD_TIS_disk | D1337
TISKlima2ZamasenFilter_omog | DIGITAL | IOD_TIS_disk | D1338
TISKlima2VisokaTempVProstoru_omog | DIGITAL | IOD_TIS_disk | D1339
TISKlima2NizkaTempVProstoru_omog | DIGITAL | IOD_TIS_disk | D1340
TISKlima2VisokaVlaznost_omog | DIGITAL | IOD_TIS_disk | D1341
TISKlima2NizkaVlaznost_omog | DIGITAL | IOD_TIS_disk | D1342
TISKlima2Kompresor1naMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1343
TISKlima2Kompresor2naMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1344
TISKlima2VentilatorNaMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1345
TISKlima2NapakaSenzorTempProstora_omog | DIGITAL | IOD_TIS_disk | D1346
TISKlima2NapakaSenzorPovratVode_omog | DIGITAL | IOD_TIS_disk | D1347
TISKlima2NapakaSenzorZunanjeTemp_omog | DIGITAL | IOD_TIS_disk | D1348
TISKlima2NapakaSenzorTempIzpiha_omog | DIGITAL | IOD_TIS_disk | D1349
TISKlima2NapakaSenzorVlaznosti_omog | DIGITAL | IOD_TIS_disk | D1350
TISKlima2NapakaSenzorPritiska1_omog | DIGITAL | IOD_TIS_disk | D1351
TISKlima2NapakaSenzorPritiska2_omog | DIGITAL | IOD_TIS_disk | D1352
TISKlima2NapakaSenzorKondTemp1_omog | DIGITAL | IOD_TIS_disk | D1353
TISKlima2NapakaSenzorKondTemp2_omog | DIGITAL | IOD_TIS_disk | D1354
TISKlima2VisokTokVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1355
TISKlima2NiVodeVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1356
TISKlima2NiTokaVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1357
TISKlima2ClockCardFault_omog | DIGITAL | IOD_TIS_disk | D1358
TISKlima2VisokPritiskVKrogu1_omog | DIGITAL | IOD_TIS_disk | D1359
TISKlima2VisokPritiskVKrogu2_omog | DIGITAL | IOD_TIS_disk | D1360
TISKlima2IzlivVode_omog | DIGITAL | IOD_TIS_disk | D1361
TISKlima2ZunanjiAlarm_omog | DIGITAL | IOD_TIS_disk | D1362
TISKlima2TermZascVisokPritiskKpr1_omog | DIGITAL | IOD_TIS_disk | D1363
TISKlima2VlazilecNaMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1364
TISKlima2TermZascVisokPritiskKpr2_omog | DIGITAL | IOD_TIS_disk | D1365
TISKlima2Kond1FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1366
TISKlima2Kond2FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1367
TISKlima2NapakaPriPretokuVode_omog | DIGITAL | IOD_TIS_disk | D1368
TISKlima2RocniIzklop_omog | DIGITAL | IOD_TIS_disk | D1369
TISKlima2Napaka_omog | DIGITAL | IOD_TIS_disk | D1370
TISKlima3AlarmKompresor1_omog | DIGITAL | IOD_TIS_disk | D1371
TISKlima3AlarmKompresor2_omog | DIGITAL | IOD_TIS_disk | D1372
TISKlima3NizekPritiskKompresor1_omog | DIGITAL | IOD_TIS_disk | D1373
TISKlima3NizekPritiskKompresor2_omog | DIGITAL | IOD_TIS_disk | D1374
TISKlima3NapakaPriPretokuZraka_omog | DIGITAL | IOD_TIS_disk | D1375
TISKlima3FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1376
TISKlima3ThermalCutoutHeater1_omog | DIGITAL | IOD_TIS_disk | D1377
TISKlima3ThermalCutoutHeater2_omog | DIGITAL | IOD_TIS_disk | D1378
TISKlima3PozarniAlarm_omog | DIGITAL | IOD_TIS_disk | D1379
TISKlima3ZamasenFilter_omog | DIGITAL | IOD_TIS_disk | D1380
TISKlima3VisokaTempVProstoru_omog | DIGITAL | IOD_TIS_disk | D1381
TISKlima3NizkaTempVProstoru_omog | DIGITAL | IOD_TIS_disk | D1382
TISKlima3VisokaVlaznost_omog | DIGITAL | IOD_TIS_disk | D1383
TISKlima3NizkaVlaznost_omog | DIGITAL | IOD_TIS_disk | D1384
TISKlima3Kompresor1naMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1385
TISKlima3Kompresor2naMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1386
TISKlima3VentilatorNaMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1387
TISKlima3NapakaSenzorTempProstora_omog | DIGITAL | IOD_TIS_disk | D1388
TISKlima3NapakaSenzorPovratVode_omog | DIGITAL | IOD_TIS_disk | D1389
TISKlima3NapakaSenzorZunanjeTemp_omog | DIGITAL | IOD_TIS_disk | D1390
TISKlima3NapakaSenzorTempIzpiha_omog | DIGITAL | IOD_TIS_disk | D1391
TISKlima3NapakaSenzorVlaznosti_omog | DIGITAL | IOD_TIS_disk | D1392
TISKlima3NapakaSenzorPritiska1_omog | DIGITAL | IOD_TIS_disk | D1393
TISKlima3NapakaSenzorPritiska2_omog | DIGITAL | IOD_TIS_disk | D1394
TISKlima3NapakaSenzorKondTemp1_omog | DIGITAL | IOD_TIS_disk | D1395
TISKlima3NapakaSenzorKondTemp2_omog | DIGITAL | IOD_TIS_disk | D1396
TISKlima3VisokTokVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1397
TISKlima3NiVodeVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1398
TISKlima3NiTokaVVlazilcu_omog | DIGITAL | IOD_TIS_disk | D1399
TISKlima3ClockCardFault_omog | DIGITAL | IOD_TIS_disk | D1400
TISKlima3VisokPritiskVKrogu1_omog | DIGITAL | IOD_TIS_disk | D1401
TISKlima3VisokPritiskVKrogu2_omog | DIGITAL | IOD_TIS_disk | D1402
TISKlima3IzlivVode_omog | DIGITAL | IOD_TIS_disk | D1403
TISKlima3ZunanjiAlarm_omog | DIGITAL | IOD_TIS_disk | D1404
TISKlima3TermZascVisokPritiskKpr1_omog | DIGITAL | IOD_TIS_disk | D1405
TISKlima3VlazilecNaMejiObrUr_omog | DIGITAL | IOD_TIS_disk | D1406
TISKlima3TermZascVisokPritiskKpr2_omog | DIGITAL | IOD_TIS_disk | D1407
TISKlima3Kond1FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1408
TISKlima3Kond2FenThermalCutout_omog | DIGITAL | IOD_TIS_disk | D1409
TISKlima3NapakaPriPretokuVode_omog | DIGITAL | IOD_TIS_disk | D1410
TISKlima3RocniIzklop_omog | DIGITAL | IOD_TIS_disk | D1411
TISKlima3Napaka_omog | DIGITAL | IOD_TIS_disk | D1412
ATIS_omogoci_sms | DIGITAL | IOD_TIS_disk | D1414[300]
BTIS_omogoci_sms | DIGITAL | IOD_TIS_disk | D1716[300]
CTIS_omogoci_sms | DIGITAL | IOD_TIS_disk | D2018[300]
DTIS_omogoci_sms | DIGITAL | IOD_TIS_disk | D2320[300]
ETIS_omogoci_sms | DIGITAL | IOD_TIS_disk | D2622[300]
FTIS_omogoci_sms | DIGITAL | IOD_TIS_disk | D2924[300]
TISUserLoggedIn_mem | DIGITAL | IOD_TIS_disk | D3226
TISErrComKlima1_omog | DIGITAL | IOD_TIS_disk | D3227
TIS_omogocanje_tok_alarm1 | DIGITAL | IOD_TIS_disk | D3229
TIS_omogocanje_tok_alarm2 | DIGITAL | IOD_TIS_disk | D3230
TIS_omogocanje_tok_alarm3 | DIGITAL | IOD_TIS_disk | D3231
TIS_omogocanje_tok_alarm4 | DIGITAL | IOD_TIS_disk | D3232
TIS_omogocanje_tok_alarm5 | DIGITAL | IOD_TIS_disk | D3233
TIS_omogocanje_tok_alarm6 | DIGITAL | IOD_TIS_disk | D3234
TIS_omogocanje_tok_alarm7 | DIGITAL | IOD_TIS_disk | D3235
TIS_omogocanje_tok_alarm8 | DIGITAL | IOD_TIS_disk | D3236
TIS_omogocanje_tok_alarm9 | DIGITAL | IOD_TIS_disk | D3237
TIS_omogocanje_tok_alarm10 | DIGITAL | IOD_TIS_disk | D3238
TIS_omogocanje_tok_alarm11 | DIGITAL | IOD_TIS_disk | D3239
TIS_omogocanje_tok_alarm12 | DIGITAL | IOD_TIS_disk | D3240
TIS_omogocanje_tok_opozorila1 | DIGITAL | IOD_TIS_disk | D3241
TIS_omogocanje_tok_opozorila2 | DIGITAL | IOD_TIS_disk | D3242
TIS_omogocanje_tok_opozorila3 | DIGITAL | IOD_TIS_disk | D3243
TIS_omogocanje_tok_opozorila4 | DIGITAL | IOD_TIS_disk | D3244
TIS_omogocanje_tok_opozorila5 | DIGITAL | IOD_TIS_disk | D3245
TIS_omogocanje_tok_opozorila6 | DIGITAL | IOD_TIS_disk | D3246
TIS_omogocanje_tok_opozorila7 | DIGITAL | IOD_TIS_disk | D3247
TIS_omogocanje_tok_opozorila8 | DIGITAL | IOD_TIS_disk | D3248
TIS_omogocanje_tok_opozorila9 | DIGITAL | IOD_TIS_disk | D3249
TIS_omogocanje_tok_opozorila10 | DIGITAL | IOD_TIS_disk | D3250
TIS_omogocanje_tok_opozorila11 | DIGITAL | IOD_TIS_disk | D3251
TIS_omogocanje_tok_opozorila12 | DIGITAL | IOD_TIS_disk | D3252
TIS_meja_tok_opozorilo1 | LONG | IOD_TIS_disk | L3278
TIS_meja_tok_opozorilo2 | LONG | IOD_TIS_disk | L3280
TIS_meja_tok_opozorilo3 | LONG | IOD_TIS_disk | L3282
TIS_meja_tok_opozorilo4 | LONG | IOD_TIS_disk | L3284
TIS_meja_tok_opozorilo5 | LONG | IOD_TIS_disk | L3286
TIS_meja_tok_opozorilo6 | LONG | IOD_TIS_disk | L3288
TIS_meja_tok_opozorilo7 | LONG | IOD_TIS_disk | L3290
TIS_meja_tok_opozorilo8 | LONG | IOD_TIS_disk | L3292
TIS_meja_tok_opozorilo9 | LONG | IOD_TIS_disk | L3294
TIS_meja_tok_opozorilo10 | LONG | IOD_TIS_disk | L3296
TIS_meja_tok_opozorilo11 | LONG | IOD_TIS_disk | L3298
TIS_meja_tok_opozorilo12 | LONG | IOD_TIS_disk | L3300
TIS_meja_tok_alarm1 | LONG | IOD_TIS_disk | L3302
TIS_meja_tok_alarm2 | LONG | IOD_TIS_disk | L3304
TIS_meja_tok_alarm3 | LONG | IOD_TIS_disk | L3306
TIS_meja_tok_alarm4 | LONG | IOD_TIS_disk | L3308
TIS_meja_tok_alarm5 | LONG | IOD_TIS_disk | L3310
TIS_meja_tok_alarm6 | LONG | IOD_TIS_disk | L3312
TIS_meja_tok_alarm7 | LONG | IOD_TIS_disk | L3314
TIS_meja_tok_alarm8 | LONG | IOD_TIS_disk | L3316
TIS_meja_tok_alarm9 | LONG | IOD_TIS_disk | L3318
TIS_meja_tok_alarm10 | LONG | IOD_TIS_disk | L3320
TIS_meja_tok_alarm11 | LONG | IOD_TIS_disk | L3322
TIS_meja_tok_alarm12 | LONG | IOD_TIS_disk | L3324
TIS_Anali_razlika_dnevna_E_G3 | REAL | IOD_TIS_disk | R3774
TIS_Anali_razlika_teden_E_G3 | REAL | IOD_TIS_disk | R3776
TIS_Anali_razlika_mes_E_G3 | REAL | IOD_TIS_disk | R3778
TIS_Anali_razlika_dnevna_E_DG3 | REAL | IOD_TIS_disk | R3780
TIS_Anali_razlika_teden_E_DG3 | REAL | IOD_TIS_disk | R3782
TIS_Anali_razlika_mes_E_DG3 | REAL | IOD_TIS_disk | R3784
TIS_Anali_razlika_dnevna_E_UPS3 | REAL | IOD_TIS_disk | R3786
TIS_Anali_razlika_teden_E_UPS3 | REAL | IOD_TIS_disk | R3788
TIS_Anali_razlika_mes_E_UPS3 | REAL | IOD_TIS_disk | R3790
TIS_Anali_razlika_dnevna_E_DG4 | REAL | IOD_TIS_disk | R3792
TIS_Anali_razlika_teden_E_DG4 | REAL | IOD_TIS_disk | R3794
TIS_Anali_razlika_mes_E_DG4 | REAL | IOD_TIS_disk | R3796
TISDI_RazlitjeVodeHO1_omog | DIGITAL | IOD_TIS_disk | D3376
TISDI_RazlitjeVodeHO2_omog | DIGITAL | IOD_TIS_disk | D3377
TISDI_RazlitjeVodeHO3_omog | DIGITAL | IOD_TIS_disk | D3378
TISDI_F1_OdklHlOm1_ON_omog | DIGITAL | IOD_TIS_disk | D3379
TISDI_F2_OdklHlOm2_ON_omog | DIGITAL | IOD_TIS_disk | D3380
TISDI_F3_OdklHlOm3_ON_omog | DIGITAL | IOD_TIS_disk | D3381
TISDI_F4_OdkPripVode_ON_omog | DIGITAL | IOD_TIS_disk | D3382
TISDI_HladOmara1_ON_omog | DIGITAL | IOD_TIS_disk | D3383
TISDI_HladOmara2_ON_omog | DIGITAL | IOD_TIS_disk | D3384
TISDI_HladOmara3_ON_omog | DIGITAL | IOD_TIS_disk | D3385
TISDI_PripVode1_ON_omog | DIGITAL | IOD_TIS_disk | D3386
TISDI_PripVode2_ON_omog | DIGITAL | IOD_TIS_disk | D3387
TISDI_Q0_DEG3_ON_omog | DIGITAL | IOD_TIS_disk | D3388
TISDI_Q0_EG3_ON_omog | DIGITAL | IOD_TIS_disk | D3389
TISDI_Q0_GlavnoStikalo_ON_omog | DIGITAL | IOD_TIS_disk | D3390
TISDI_Q0_UPS3_ON_omog | DIGITAL | IOD_TIS_disk | D3391
TISDI_UPS_BatNacin_omog | DIGITAL | IOD_TIS_disk | D3392
TISDI_UPS_Polnjenje_omog | DIGITAL | IOD_TIS_disk | D3393
TISDI_Vlazilec1_ON_omog | DIGITAL | IOD_TIS_disk | D3394
TISDI_Vlazilec2_ON_omog | DIGITAL | IOD_TIS_disk | D3395
TISDI_Vlazilec3_ON_omog | DIGITAL | IOD_TIS_disk | D3396
TISKlima1Razvlazevanje_omog | DIGITAL | IOD_TIS_disk | D3397
TISKlima1VentilGretjeOdpiranje_omog | DIGITAL | IOD_TIS_disk | D3398
TISKlima1VentilGretjeZapiranje_omog | DIGITAL | IOD_TIS_disk | D3399
TISKlima1Vlazenje_omog | DIGITAL | IOD_TIS_disk | D3400
TISKlima1Deluje_omog | DIGITAL | IOD_TIS_disk | D3401
TISKlima2Razvlazevanje_omog | DIGITAL | IOD_TIS_disk | D3402
TISKlima2VentilGretjeOdpiranje_omog | DIGITAL | IOD_TIS_disk | D3403
TISKlima2VentilGretjeZapiranje_omog | DIGITAL | IOD_TIS_disk | D3404
TISKlima2Vlazenje_omog | DIGITAL | IOD_TIS_disk | D3405
TISKlima2Deluje_omog | DIGITAL | IOD_TIS_disk | D3406
TISKlima3Razvlazevanje_omog | DIGITAL | IOD_TIS_disk | D3407
TISKlima3VentilGretjeOdpiranje_omog | DIGITAL | IOD_TIS_disk | D3408
TISKlima3VentilGretjeZapiranje_omog | DIGITAL | IOD_TIS_disk | D3409
TISKlima3Vlazenje_omog | DIGITAL | IOD_TIS_disk | D3410
TISKlima3Deluje_omog | DIGITAL | IOD_TIS_disk | D3411
NeTISDI_F1_OdklHlOm1_ON_omog | DIGITAL | IOD_TIS_disk | D3412
NeTISDI_F2_OdklHlOm2_ON_omog | DIGITAL | IOD_TIS_disk | D3413
NeTISDI_F3_OdklHlOm3_ON_omog | DIGITAL | IOD_TIS_disk | D3414
NeTISDI_F4_OdkPripVode_ON_omog | DIGITAL | IOD_TIS_disk | D3415
NeTISDI_Q0_DEG3_ON_omog | DIGITAL | IOD_TIS_disk | D3416
NeTISDI_Q0_EG3_ON_omog | DIGITAL | IOD_TIS_disk | D3417
NeTISDI_Q0_GlavnoStikalo_ON_omog | DIGITAL | IOD_TIS_disk | D3418
NeTISDI_Q0_UPS3_ON_omog | DIGITAL | IOD_TIS_disk | D3419
TIS_ComScadaPlc_omog2 | DIGITAL | IOD_TIS_disk | D3420
TISComSCADA2 | DIGITAL | IOD_TIS_TCP | 00473
TISErrCommScada2 | DIGITAL | IOD_TIS_TCP | 00474
TISServer_A_Izpad | DIGITAL | IOD_TIS_disk | D3423
TISServer_B_Izpad | DIGITAL | IOD_TIS_disk | D3424
TISComSCADA_stevec3 | INT | IOD_TIS_mem | I3426
TISComSCADA_stevec | INT | IOD_TIS_mem | I3428
TISComSCADA3 | DIGITAL | IOD_TIS_TCP | 00475
TISkom_nast_cas_izpada | INT | IOD_TIS_TCP | 40232
TISCirc1MaximumDemandA2 | REAL | IOD_TIS_TCP | 44621 | 0 | 1200 | 0 | 1200 | A | ###.#
TISCirc1MaximumDemandA3 | REAL | IOD_TIS_TCP | 44623 | 0 | 1200 | 0 | 1200 | A | ###.#
TISCirc2MaximumDemandA2 | REAL | IOD_TIS_TCP | 44625 | 0 | 1200 | 0 | 1200 | A | ###.#
TISCirc2MaximumDemandA3 | REAL | IOD_TIS_TCP | 44627 | 0 | 1200 | 0 | 1200 | A | ###.#
TISCirc3MaximumDemandA2 | REAL | IOD_TIS_TCP | 44629 | 0 | 1200 | 0 | 1200 | A | ###.#
TISCirc3MaximumDemandA3 | REAL | IOD_TIS_TCP | 44631 | 0 | 1200 | 0 | 1200 | A | ###.#
TISCirc4MaximumDemandA2 | REAL | IOD_TIS_TCP | 44633 | 0 | 1200 | 0 | 1200 | A | ###.#
TISCirc4MaximumDemandA3 | REAL | IOD_TIS_TCP | 44635 | 0 | 1200 | 0 | 1200 | A | ###.#
TISCirc1RazEner_D_SCADA | REAL | IOD_TIS_TCP | 44637
TISCirc1RazEner_T_SCADA | REAL | IOD_TIS_TCP | 44639
TISCirc1RazEner_M_SCADA | REAL | IOD_TIS_TCP | 44641
TISCirc2RazEner_D_SCADA | REAL | IOD_TIS_TCP | 44643
TISCirc2RazEner_T_SCADA | REAL | IOD_TIS_TCP | 44645
TISCirc2RazEner_M_SCADA | REAL | IOD_TIS_TCP | 44647
TISCirc3RazEner_D_SCADA | REAL | IOD_TIS_TCP | 44649
TISCirc3RazEner_T_SCADA | REAL | IOD_TIS_TCP | 44651
TISCirc3RazEner_M_SCADA | REAL | IOD_TIS_TCP | 44653
TISCirc4RazEner_D_SCADA | REAL | IOD_TIS_TCP | 44655
TISCirc4RazEner_T_SCADA | REAL | IOD_TIS_TCP | 44657
TISCirc4RazEner_M_SCADA | REAL | IOD_TIS_TCP | 44659
TISCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_TIS_TCP | 00476
TISCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_TIS_TCP | 00477
TISCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_TIS_TCP | 00478
TISCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_TIS_TCP | 00479
TISCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_TIS_TCP | 00480
TISCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_TIS_TCP | 00481
TISCirc_Vpis_Dnevne_energija_scada1_mem | DIGITAL | IOD_TIS_disk | D3425
TISCirc_Vpis_Dnevne_energija_scada2_mem | DIGITAL | IOD_TIS_disk | D3426
TISCirc_Vpis_Tedenska_energija_scada1_mem | DIGITAL | IOD_TIS_disk | D3427
TISCirc_Vpis_Tedenska_energija_scada2_mem | DIGITAL | IOD_TIS_disk | D3428
TISCirc_Vpis_Mesecna_energija_scada1_mem | DIGITAL | IOD_TIS_disk | D3429
TISCirc_Vpis_Mesecna_energija_scada2_mem | DIGITAL | IOD_TIS_disk | D3430

## XSoft
mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Write_BOOL(FC) | mod_Write_Word(FC) | mod_Write_Word(FC) | mod_Write_dWord(FC) | mod_Write_dWord(FC) | mod_Write_String(FC)
(*Branje BOOL*) | (*Branje INT*) | (*Branje UINT*) | (*Branje LONG*) | (*Branje REAL*) | (*Branje STRING*) | (*Pisanje BOOL*) | (*Pisanje INT*) | (*Pisanje UINT*) | (*Pisanje LONG*) | (*Pisanje REAL*) | (*Pisanje STRING*)
(**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**)
mind_bool[0]:=AlarmGenCirc1; | mind[0]:=DateTime.Dan; |  |  | Read_Real(rVar:=Circ[1].CosFi_III,lo:=4000,hi:=4001); | Read_String(sVar:=Date_Time[0],start:=5000); | 0:AlarmGenCirc1:=Bit_0; | 0:DateTime.Dan:=Byte_0; |  |  | 4001:Circ[1].CosFi_III:=Real_0; | 5000:Date_Time[0]:=String_0;
mind_bool[1]:=AlarmGenCirc2; | mind[1]:=DateTime.Leto; |  |  | Read_Real(rVar:=Circ[1].DelovnaEnergija,lo:=4002,hi:=4003); | Read_String(sVar:=Date_Time[1],start:=5015); | 1:AlarmGenCirc2:=Bit_0; | 1:DateTime.Leto:=Byte_0; |  |  | 4003:Circ[1].DelovnaEnergija:=Real_0; | 5015:Date_Time[1]:=String_0;
mind_bool[2]:=AlarmGenCirc3; | mind[2]:=DateTime.Mesec; |  |  | Read_Real(rVar:=Circ[1].DelovnaMoc_III,lo:=4004,hi:=4005); | Read_String(sVar:=Date_Time[2],start:=5030); | 2:AlarmGenCirc3:=Bit_0; | 2:DateTime.Mesec:=Byte_0; |  |  | 4005:Circ[1].DelovnaMoc_III:=Real_0; | 5030:Date_Time[2]:=String_0;
mind_bool[3]:=AlarmGenCirc4; | mind[3]:=DateTime.Minuta; |  |  | Read_Real(rVar:=Circ[1].DelovnaMoc_L1,lo:=4006,hi:=4007); | Read_String(sVar:=Date_Time[3],start:=5045); | 3:AlarmGenCirc4:=Bit_0; | 3:DateTime.Minuta:=Byte_0; |  |  | 4007:Circ[1].DelovnaMoc_L1:=Real_0; | 5045:Date_Time[3]:=String_0;
mind_bool[4]:=AlarmGenComm; | mind[4]:=DateTime.Sekunda; |  |  | Read_Real(rVar:=Circ[1].DelovnaMoc_L2,lo:=4008,hi:=4009); | Read_String(sVar:=UserCurrentName,start:=5060); | 4:AlarmGenComm:=Bit_0; | 4:DateTime.Sekunda:=Byte_0; |  |  | 4009:Circ[1].DelovnaMoc_L2:=Real_0; | 5060:UserCurrentName:=String_0;
mind_bool[5]:=AlarmGenDI; | mind[5]:=DateTime.Ura; |  |  | Read_Real(rVar:=Circ[1].DelovnaMoc_L3,lo:=4010,hi:=4011); |  | 5:AlarmGenDI:=Bit_0; | 5:DateTime.Ura:=Byte_0; |  |  | 4011:Circ[1].DelovnaMoc_L3:=Real_0;
mind_bool[6]:=AlarmGenKlima1; | mind[6]:=ErrorComCirc[1].Code[10]; |  |  | Read_Real(rVar:=Circ[1].Frekvenca_L1,lo:=4012,hi:=4013); |  | 6:AlarmGenKlima1:=Bit_0; | 6:ErrorComCirc[1].Code[10]:=Byte_0; |  |  | 4013:Circ[1].Frekvenca_L1:=Real_0;
mind_bool[7]:=AlarmGenKlima2; | mind[7]:=ErrorComCirc[1].Code[11]; |  |  | Read_Real(rVar:=Circ[1].InduktivnaEnergija,lo:=4014,hi:=4015); |  | 7:AlarmGenKlima2:=Bit_0; | 7:ErrorComCirc[1].Code[11]:=Byte_0; |  |  | 4015:Circ[1].InduktivnaEnergija:=Real_0;
mind_bool[8]:=AlarmGenKlima3; | mind[8]:=ErrorComCirc[1].Code[12]; |  |  | Read_Real(rVar:=Circ[1].InduktivnaMoc_III,lo:=4016,hi:=4017); |  | 8:AlarmGenKlima3:=Bit_0; | 8:ErrorComCirc[1].Code[12]:=Byte_0; |  |  | 4017:Circ[1].InduktivnaMoc_III:=Real_0;
mind_bool[9]:=AlarmGenRest; | mind[9]:=ErrorComCirc[1].Code[13]; |  |  | Read_Real(rVar:=Circ[1].JalovaMoc_L1,lo:=4018,hi:=4019); |  | 9:AlarmGenRest:=Bit_0; | 9:ErrorComCirc[1].Code[13]:=Byte_0; |  |  | 4019:Circ[1].JalovaMoc_L1:=Real_0;
mind_bool[10]:=AlarmGenSenzor; | mind[10]:=ErrorComCirc[1].Code[14]; |  |  | Read_Real(rVar:=Circ[1].JalovaMoc_L2,lo:=4020,hi:=4021); |  | 10:AlarmGenSenzor:=Bit_0; | 10:ErrorComCirc[1].Code[14]:=Byte_0; |  |  | 4021:Circ[1].JalovaMoc_L2:=Real_0;
mind_bool[11]:=AlarmGenTemp; | mind[11]:=ErrorComCirc[1].Code[15]; |  |  | Read_Real(rVar:=Circ[1].JalovaMoc_L3,lo:=4022,hi:=4023); |  | 11:AlarmGenTemp:=Bit_0; | 11:ErrorComCirc[1].Code[15]:=Byte_0; |  |  | 4023:Circ[1].JalovaMoc_L3:=Real_0;
mind_bool[12]:=AlarmGenVlPr; | mind[12]:=ErrorComCirc[1].Code[1]; |  |  | Read_Real(rVar:=Circ[1].KapacitivnaEnergija,lo:=4024,hi:=4025); |  | 12:AlarmGenVlPr:=Bit_0; | 12:ErrorComCirc[1].Code[1]:=Byte_0; |  |  | 4025:Circ[1].KapacitivnaEnergija:=Real_0;
mind_bool[13]:=AlarmGenVTV; | mind[13]:=ErrorComCirc[1].Code[2]; |  |  | Read_Real(rVar:=Circ[1].KapacitivnaMoc_III,lo:=4026,hi:=4027); |  | 13:AlarmGenVTV:=Bit_0; | 13:ErrorComCirc[1].Code[2]:=Byte_0; |  |  | 4027:Circ[1].KapacitivnaMoc_III:=Real_0;
mind_bool[14]:=ComSCADA; | mind[14]:=ErrorComCirc[1].Code[3]; |  |  | Read_Real(rVar:=Circ[1].MaximumDemand,lo:=4028,hi:=4029); |  | 14:ComSCADA:=Bit_0; | 14:ErrorComCirc[1].Code[3]:=Byte_0; |  |  | 4029:Circ[1].MaximumDemand:=Real_0;
mind_bool[15]:=ComSCADA1; | mind[15]:=ErrorComCirc[1].Code[4]; |  |  | Read_Real(rVar:=Circ[1].Napetost_L1_L2,lo:=4030,hi:=4031); |  | 15:ComSCADA1:=Bit_0; | 15:ErrorComCirc[1].Code[4]:=Byte_0; |  |  | 4031:Circ[1].Napetost_L1_L2:=Real_0;
mind_bool[16]:=DI_F1_OdklHlOm1_IZP; | mind[16]:=ErrorComCirc[1].Code[5]; |  |  | Read_Real(rVar:=Circ[1].Napetost_L1_N,lo:=4032,hi:=4033); |  | 16:DI_F1_OdklHlOm1_IZP:=Bit_0; | 16:ErrorComCirc[1].Code[5]:=Byte_0; |  |  | 4033:Circ[1].Napetost_L1_N:=Real_0;
mind_bool[17]:=DI_F1_OdklHlOm1_ON; | mind[17]:=ErrorComCirc[1].Code[6]; |  |  | Read_Real(rVar:=Circ[1].Napetost_L2_L3,lo:=4034,hi:=4035); |  | 17:DI_F1_OdklHlOm1_ON:=Bit_0; | 17:ErrorComCirc[1].Code[6]:=Byte_0; |  |  | 4035:Circ[1].Napetost_L2_L3:=Real_0;
mind_bool[18]:=DI_F2_OdklHlOm2_IZP; | mind[18]:=ErrorComCirc[1].Code[7]; |  |  | Read_Real(rVar:=Circ[1].Napetost_L2_N,lo:=4036,hi:=4037); |  | 18:DI_F2_OdklHlOm2_IZP:=Bit_0; | 18:ErrorComCirc[1].Code[7]:=Byte_0; |  |  | 4037:Circ[1].Napetost_L2_N:=Real_0;
mind_bool[19]:=DI_F2_OdklHlOm2_ON; | mind[19]:=ErrorComCirc[1].Code[8]; |  |  | Read_Real(rVar:=Circ[1].Napetost_L3_L1,lo:=4038,hi:=4039); |  | 19:DI_F2_OdklHlOm2_ON:=Bit_0; | 19:ErrorComCirc[1].Code[8]:=Byte_0; |  |  | 4039:Circ[1].Napetost_L3_L1:=Real_0;
mind_bool[20]:=DI_F3_OdklHlOm3_IZP; | mind[20]:=ErrorComCirc[1].Code[9]; |  |  | Read_Real(rVar:=Circ[1].Napetost_L3_N,lo:=4040,hi:=4041); |  | 20:DI_F3_OdklHlOm3_IZP:=Bit_0; | 20:ErrorComCirc[1].Code[9]:=Byte_0; |  |  | 4041:Circ[1].Napetost_L3_N:=Real_0;
mind_bool[21]:=DI_F3_OdklHlOm3_ON; | mind[21]:=ErrorComCirc[1].Status; |  |  | Read_Real(rVar:=Circ[1].NavideznaMoc_III,lo:=4042,hi:=4043); |  | 21:DI_F3_OdklHlOm3_ON:=Bit_0; | 21:ErrorComCirc[1].Status:=Word_01; |  |  | 4043:Circ[1].NavideznaMoc_III:=Real_0;
mind_bool[22]:=DI_F4_OdkPripVode_IZP; | mind[22]:=ErrorComCirc[2].Code[10]; |  |  | Read_Real(rVar:=Circ[1].NicelniTok,lo:=4044,hi:=4045); |  | 22:DI_F4_OdkPripVode_IZP:=Bit_0; | 22:ErrorComCirc[2].Code[10]:=Byte_0; |  |  | 4045:Circ[1].NicelniTok:=Real_0;
mind_bool[23]:=DI_F4_OdkPripVode_ON; | mind[23]:=ErrorComCirc[2].Code[11]; |  |  | Read_Real(rVar:=Circ[1].PowerFactor_III,lo:=4046,hi:=4047); |  | 23:DI_F4_OdkPripVode_ON:=Bit_0; | 23:ErrorComCirc[2].Code[11]:=Byte_0; |  |  | 4047:Circ[1].PowerFactor_III:=Real_0;
mind_bool[24]:=DI_HladOmara1_ERR; | mind[24]:=ErrorComCirc[2].Code[12]; |  |  | Read_Real(rVar:=Circ[1].PowerFactor_L1,lo:=4048,hi:=4049); |  | 24:DI_HladOmara1_ERR:=Bit_0; | 24:ErrorComCirc[2].Code[12]:=Byte_0; |  |  | 4049:Circ[1].PowerFactor_L1:=Real_0;
mind_bool[25]:=DI_HladOmara1_ON; | mind[25]:=ErrorComCirc[2].Code[13]; |  |  | Read_Real(rVar:=Circ[1].PowerFactor_L2,lo:=4050,hi:=4051); |  | 25:DI_HladOmara1_ON:=Bit_0; | 25:ErrorComCirc[2].Code[13]:=Byte_0; |  |  | 4051:Circ[1].PowerFactor_L2:=Real_0;
mind_bool[26]:=DI_HladOmara2_ERR; | mind[26]:=ErrorComCirc[2].Code[14]; |  |  | Read_Real(rVar:=Circ[1].PowerFactor_L3,lo:=4052,hi:=4053); |  | 26:DI_HladOmara2_ERR:=Bit_0; | 26:ErrorComCirc[2].Code[14]:=Byte_0; |  |  | 4053:Circ[1].PowerFactor_L3:=Real_0;
mind_bool[27]:=DI_HladOmara2_ON; | mind[27]:=ErrorComCirc[2].Code[15]; |  |  | Read_Real(rVar:=Circ[1].THDI_L1,lo:=4054,hi:=4055); |  | 27:DI_HladOmara2_ON:=Bit_0; | 27:ErrorComCirc[2].Code[15]:=Byte_0; |  |  | 4055:Circ[1].THDI_L1:=Real_0;
mind_bool[28]:=DI_HladOmara3_ERR; | mind[28]:=ErrorComCirc[2].Code[1]; |  |  | Read_Real(rVar:=Circ[1].THDI_L2,lo:=4056,hi:=4057); |  | 28:DI_HladOmara3_ERR:=Bit_0; | 28:ErrorComCirc[2].Code[1]:=Byte_0; |  |  | 4057:Circ[1].THDI_L2:=Real_0;
mind_bool[29]:=DI_HladOmara3_ON; | mind[29]:=ErrorComCirc[2].Code[2]; |  |  | Read_Real(rVar:=Circ[1].THDI_L3,lo:=4058,hi:=4059); |  | 29:DI_HladOmara3_ON:=Bit_0; | 29:ErrorComCirc[2].Code[2]:=Byte_0; |  |  | 4059:Circ[1].THDI_L3:=Real_0;
mind_bool[30]:=DI_PripVode1_ERR; | mind[30]:=ErrorComCirc[2].Code[3]; |  |  | Read_Real(rVar:=Circ[1].THDV_L1,lo:=4060,hi:=4061); |  | 30:DI_PripVode1_ERR:=Bit_0; | 30:ErrorComCirc[2].Code[3]:=Byte_0; |  |  | 4061:Circ[1].THDV_L1:=Real_0;
mind_bool[31]:=DI_PripVode1_ON; | mind[31]:=ErrorComCirc[2].Code[4]; |  |  | Read_Real(rVar:=Circ[1].THDV_L2,lo:=4062,hi:=4063); |  | 31:DI_PripVode1_ON:=Bit_0; | 31:ErrorComCirc[2].Code[4]:=Byte_0; |  |  | 4063:Circ[1].THDV_L2:=Real_0;
mind_bool[32]:=DI_PripVode2_ERR; | mind[32]:=ErrorComCirc[2].Code[5]; |  |  | Read_Real(rVar:=Circ[1].THDV_L3,lo:=4064,hi:=4065); |  | 32:DI_PripVode2_ERR:=Bit_0; | 32:ErrorComCirc[2].Code[5]:=Byte_0; |  |  | 4065:Circ[1].THDV_L3:=Real_0;
mind_bool[33]:=DI_PripVode2_ON; | mind[33]:=ErrorComCirc[2].Code[6]; |  |  | Read_Real(rVar:=Circ[1].Tok_L1,lo:=4066,hi:=4067); |  | 33:DI_PripVode2_ON:=Bit_0; | 33:ErrorComCirc[2].Code[6]:=Byte_0; |  |  | 4067:Circ[1].Tok_L1:=Real_0;
mind_bool[34]:=DI_Q0_DEG3_ON; | mind[34]:=ErrorComCirc[2].Code[7]; |  |  | Read_Real(rVar:=Circ[1].Tok_L2,lo:=4068,hi:=4069); |  | 34:DI_Q0_DEG3_ON:=Bit_0; | 34:ErrorComCirc[2].Code[7]:=Byte_0; |  |  | 4069:Circ[1].Tok_L2:=Real_0;
mind_bool[35]:=DI_Q0_EG3_ON; | mind[35]:=ErrorComCirc[2].Code[8]; |  |  | Read_Real(rVar:=Circ[1].Tok_L3,lo:=4070,hi:=4071); |  | 35:DI_Q0_EG3_ON:=Bit_0; | 35:ErrorComCirc[2].Code[8]:=Byte_0; |  |  | 4071:Circ[1].Tok_L3:=Real_0;
mind_bool[36]:=DI_Q0_GlavnoStikalo_ON; | mind[36]:=ErrorComCirc[2].Code[9]; |  |  | Read_Real(rVar:=Circ[1].TokPovprecje_III,lo:=4072,hi:=4073); |  | 36:DI_Q0_GlavnoStikalo_ON:=Bit_0; | 36:ErrorComCirc[2].Code[9]:=Byte_0; |  |  | 4073:Circ[1].TokPovprecje_III:=Real_0;
mind_bool[37]:=DI_Q0_UPS3_ON; | mind[37]:=ErrorComCirc[2].Status; |  |  | Read_Real(rVar:=Circ[2].CosFi_III,lo:=4074,hi:=4075); |  | 37:DI_Q0_UPS3_ON:=Bit_0; | 37:ErrorComCirc[2].Status:=Word_01; |  |  | 4075:Circ[2].CosFi_III:=Real_0;
mind_bool[38]:=DI_RazlitjeVodeHO1; | mind[38]:=ErrorComCirc[3].Code[10]; |  |  | Read_Real(rVar:=Circ[2].DelovnaEnergija,lo:=4076,hi:=4077); |  | 38:DI_RazlitjeVodeHO1:=Bit_0; | 38:ErrorComCirc[3].Code[10]:=Byte_0; |  |  | 4077:Circ[2].DelovnaEnergija:=Real_0;
mind_bool[39]:=DI_RazlitjeVodeHO2; | mind[39]:=ErrorComCirc[3].Code[11]; |  |  | Read_Real(rVar:=Circ[2].DelovnaMoc_III,lo:=4078,hi:=4079); |  | 39:DI_RazlitjeVodeHO2:=Bit_0; | 39:ErrorComCirc[3].Code[11]:=Byte_0; |  |  | 4079:Circ[2].DelovnaMoc_III:=Real_0;
mind_bool[40]:=DI_RazlitjeVodeHO3; | mind[40]:=ErrorComCirc[3].Code[12]; |  |  | Read_Real(rVar:=Circ[2].DelovnaMoc_L1,lo:=4080,hi:=4081); |  | 40:DI_RazlitjeVodeHO3:=Bit_0; | 40:ErrorComCirc[3].Code[12]:=Byte_0; |  |  | 4081:Circ[2].DelovnaMoc_L1:=Real_0;
mind_bool[41]:=DI_UPS_Alarm; | mind[41]:=ErrorComCirc[3].Code[13]; |  |  | Read_Real(rVar:=Circ[2].DelovnaMoc_L2,lo:=4082,hi:=4083); |  | 41:DI_UPS_Alarm:=Bit_0; | 41:ErrorComCirc[3].Code[13]:=Byte_0; |  |  | 4083:Circ[2].DelovnaMoc_L2:=Real_0;
mind_bool[42]:=DI_UPS_BatNacin; | mind[42]:=ErrorComCirc[3].Code[14]; |  |  | Read_Real(rVar:=Circ[2].DelovnaMoc_L3,lo:=4084,hi:=4085); |  | 42:DI_UPS_BatNacin:=Bit_0; | 42:ErrorComCirc[3].Code[14]:=Byte_0; |  |  | 4085:Circ[2].DelovnaMoc_L3:=Real_0;
mind_bool[43]:=DI_UPS_Polnjenje; | mind[43]:=ErrorComCirc[3].Code[15]; |  |  | Read_Real(rVar:=Circ[2].Frekvenca_L1,lo:=4086,hi:=4087); |  | 43:DI_UPS_Polnjenje:=Bit_0; | 43:ErrorComCirc[3].Code[15]:=Byte_0; |  |  | 4087:Circ[2].Frekvenca_L1:=Real_0;
mind_bool[44]:=DI_Vlazilec1_ERR; | mind[44]:=ErrorComCirc[3].Code[1]; |  |  | Read_Real(rVar:=Circ[2].InduktivnaEnergija,lo:=4088,hi:=4089); |  | 44:DI_Vlazilec1_ERR:=Bit_0; | 44:ErrorComCirc[3].Code[1]:=Byte_0; |  |  | 4089:Circ[2].InduktivnaEnergija:=Real_0;
mind_bool[45]:=DI_Vlazilec1_ON; | mind[45]:=ErrorComCirc[3].Code[2]; |  |  | Read_Real(rVar:=Circ[2].InduktivnaMoc_III,lo:=4090,hi:=4091); |  | 45:DI_Vlazilec1_ON:=Bit_0; | 45:ErrorComCirc[3].Code[2]:=Byte_0; |  |  | 4091:Circ[2].InduktivnaMoc_III:=Real_0;
mind_bool[46]:=DI_Vlazilec2_ERR; | mind[46]:=ErrorComCirc[3].Code[3]; |  |  | Read_Real(rVar:=Circ[2].JalovaMoc_L1,lo:=4092,hi:=4093); |  | 46:DI_Vlazilec2_ERR:=Bit_0; | 46:ErrorComCirc[3].Code[3]:=Byte_0; |  |  | 4093:Circ[2].JalovaMoc_L1:=Real_0;
mind_bool[47]:=DI_Vlazilec2_ON; | mind[47]:=ErrorComCirc[3].Code[4]; |  |  | Read_Real(rVar:=Circ[2].JalovaMoc_L2,lo:=4094,hi:=4095); |  | 47:DI_Vlazilec2_ON:=Bit_0; | 47:ErrorComCirc[3].Code[4]:=Byte_0; |  |  | 4095:Circ[2].JalovaMoc_L2:=Real_0;
mind_bool[48]:=DI_Vlazilec3_ERR; | mind[48]:=ErrorComCirc[3].Code[5]; |  |  | Read_Real(rVar:=Circ[2].JalovaMoc_L3,lo:=4096,hi:=4097); |  | 48:DI_Vlazilec3_ERR:=Bit_0; | 48:ErrorComCirc[3].Code[5]:=Byte_0; |  |  | 4097:Circ[2].JalovaMoc_L3:=Real_0;
mind_bool[49]:=DI_Vlazilec3_ON; | mind[49]:=ErrorComCirc[3].Code[6]; |  |  | Read_Real(rVar:=Circ[2].KapacitivnaEnergija,lo:=4098,hi:=4099); |  | 49:DI_Vlazilec3_ON:=Bit_0; | 49:ErrorComCirc[3].Code[6]:=Byte_0; |  |  | 4099:Circ[2].KapacitivnaEnergija:=Real_0;
mind_bool[50]:=DIN_F1_OdklHlOm1_IZP; | mind[50]:=ErrorComCirc[3].Code[7]; |  |  | Read_Real(rVar:=Circ[2].KapacitivnaMoc_III,lo:=4100,hi:=4101); |  | 50:DIN_F1_OdklHlOm1_IZP:=Bit_0; | 50:ErrorComCirc[3].Code[7]:=Byte_0; |  |  | 4101:Circ[2].KapacitivnaMoc_III:=Real_0;
mind_bool[51]:=DIN_F2_OdklHlOm2_IZP; | mind[51]:=ErrorComCirc[3].Code[8]; |  |  | Read_Real(rVar:=Circ[2].MaximumDemand,lo:=4102,hi:=4103); |  | 51:DIN_F2_OdklHlOm2_IZP:=Bit_0; | 51:ErrorComCirc[3].Code[8]:=Byte_0; |  |  | 4103:Circ[2].MaximumDemand:=Real_0;
mind_bool[52]:=DIN_F3_OdklHlOm3_IZP; | mind[52]:=ErrorComCirc[3].Code[9]; |  |  | Read_Real(rVar:=Circ[2].Napetost_L1_L2,lo:=4104,hi:=4105); |  | 52:DIN_F3_OdklHlOm3_IZP:=Bit_0; | 52:ErrorComCirc[3].Code[9]:=Byte_0; |  |  | 4105:Circ[2].Napetost_L1_L2:=Real_0;
mind_bool[53]:=DIN_F4_OdkPripVode_IZP; | mind[53]:=ErrorComCirc[3].Status; |  |  | Read_Real(rVar:=Circ[2].Napetost_L1_N,lo:=4106,hi:=4107); |  | 53:DIN_F4_OdkPripVode_IZP:=Bit_0; | 53:ErrorComCirc[3].Status:=Word_01; |  |  | 4107:Circ[2].Napetost_L1_N:=Real_0;
mind_bool[54]:=DIN_HladOmara1_ERR; | mind[54]:=ErrorComCirc[4].Code[10]; |  |  | Read_Real(rVar:=Circ[2].Napetost_L2_L3,lo:=4108,hi:=4109); |  | 54:DIN_HladOmara1_ERR:=Bit_0; | 54:ErrorComCirc[4].Code[10]:=Byte_0; |  |  | 4109:Circ[2].Napetost_L2_L3:=Real_0;
mind_bool[55]:=DIN_HladOmara2_ERR; | mind[55]:=ErrorComCirc[4].Code[11]; |  |  | Read_Real(rVar:=Circ[2].Napetost_L2_N,lo:=4110,hi:=4111); |  | 55:DIN_HladOmara2_ERR:=Bit_0; | 55:ErrorComCirc[4].Code[11]:=Byte_0; |  |  | 4111:Circ[2].Napetost_L2_N:=Real_0;
mind_bool[56]:=DIN_HladOmara3_ERR; | mind[56]:=ErrorComCirc[4].Code[12]; |  |  | Read_Real(rVar:=Circ[2].Napetost_L3_L1,lo:=4112,hi:=4113); |  | 56:DIN_HladOmara3_ERR:=Bit_0; | 56:ErrorComCirc[4].Code[12]:=Byte_0; |  |  | 4113:Circ[2].Napetost_L3_L1:=Real_0;
mind_bool[57]:=DIN_PripVode1_ERR; | mind[57]:=ErrorComCirc[4].Code[13]; |  |  | Read_Real(rVar:=Circ[2].Napetost_L3_N,lo:=4114,hi:=4115); |  | 57:DIN_PripVode1_ERR:=Bit_0; | 57:ErrorComCirc[4].Code[13]:=Byte_0; |  |  | 4115:Circ[2].Napetost_L3_N:=Real_0;
mind_bool[58]:=DIN_PripVode2_ERR; | mind[58]:=ErrorComCirc[4].Code[14]; |  |  | Read_Real(rVar:=Circ[2].NavideznaMoc_III,lo:=4116,hi:=4117); |  | 58:DIN_PripVode2_ERR:=Bit_0; | 58:ErrorComCirc[4].Code[14]:=Byte_0; |  |  | 4117:Circ[2].NavideznaMoc_III:=Real_0;
mind_bool[59]:=DIN_Vlazilec1_ERR; | mind[59]:=ErrorComCirc[4].Code[15]; |  |  | Read_Real(rVar:=Circ[2].NicelniTok,lo:=4118,hi:=4119); |  | 59:DIN_Vlazilec1_ERR:=Bit_0; | 59:ErrorComCirc[4].Code[15]:=Byte_0; |  |  | 4119:Circ[2].NicelniTok:=Real_0;
mind_bool[60]:=DIN_Vlazilec2_ERR; | mind[60]:=ErrorComCirc[4].Code[1]; |  |  | Read_Real(rVar:=Circ[2].PowerFactor_III,lo:=4120,hi:=4121); |  | 60:DIN_Vlazilec2_ERR:=Bit_0; | 60:ErrorComCirc[4].Code[1]:=Byte_0; |  |  | 4121:Circ[2].PowerFactor_III:=Real_0;
mind_bool[61]:=DIN_Vlazilec3_ERR; | mind[61]:=ErrorComCirc[4].Code[2]; |  |  | Read_Real(rVar:=Circ[2].PowerFactor_L1,lo:=4122,hi:=4123); |  | 61:DIN_Vlazilec3_ERR:=Bit_0; | 61:ErrorComCirc[4].Code[2]:=Byte_0; |  |  | 4123:Circ[2].PowerFactor_L1:=Real_0;
mind_bool[62]:=DO_HladOm1_Izklop; | mind[62]:=ErrorComCirc[4].Code[3]; |  |  | Read_Real(rVar:=Circ[2].PowerFactor_L2,lo:=4124,hi:=4125); |  | 62:DO_HladOm1_Izklop:=Bit_0; | 62:ErrorComCirc[4].Code[3]:=Byte_0; |  |  | 4125:Circ[2].PowerFactor_L2:=Real_0;
mind_bool[63]:=DO_HladOm2_Izklop; | mind[63]:=ErrorComCirc[4].Code[4]; |  |  | Read_Real(rVar:=Circ[2].PowerFactor_L3,lo:=4126,hi:=4127); |  | 63:DO_HladOm2_Izklop:=Bit_0; | 63:ErrorComCirc[4].Code[4]:=Byte_0; |  |  | 4127:Circ[2].PowerFactor_L3:=Real_0;
mind_bool[64]:=DO_HladOm3_Izklop; | mind[64]:=ErrorComCirc[4].Code[5]; |  |  | Read_Real(rVar:=Circ[2].THDI_L1,lo:=4128,hi:=4129); |  | 64:DO_HladOm3_Izklop:=Bit_0; | 64:ErrorComCirc[4].Code[5]:=Byte_0; |  |  | 4129:Circ[2].THDI_L1:=Real_0;
mind_bool[65]:=ErrComCirc[1]; | mind[65]:=ErrorComCirc[4].Code[6]; |  |  | Read_Real(rVar:=Circ[2].THDI_L2,lo:=4130,hi:=4131); |  | 65:ErrComCirc[1]:=Bit_0; | 65:ErrorComCirc[4].Code[6]:=Byte_0; |  |  | 4131:Circ[2].THDI_L2:=Real_0;
mind_bool[66]:=ErrComCirc[2]; | mind[66]:=ErrorComCirc[4].Code[7]; |  |  | Read_Real(rVar:=Circ[2].THDI_L3,lo:=4132,hi:=4133); |  | 66:ErrComCirc[2]:=Bit_0; | 66:ErrorComCirc[4].Code[7]:=Byte_0; |  |  | 4133:Circ[2].THDI_L3:=Real_0;
mind_bool[67]:=ErrComCirc[3]; | mind[67]:=ErrorComCirc[4].Code[8]; |  |  | Read_Real(rVar:=Circ[2].THDV_L1,lo:=4134,hi:=4135); |  | 67:ErrComCirc[3]:=Bit_0; | 67:ErrorComCirc[4].Code[8]:=Byte_0; |  |  | 4135:Circ[2].THDV_L1:=Real_0;
mind_bool[68]:=ErrComCirc[4]; | mind[68]:=ErrorComCirc[4].Code[9]; |  |  | Read_Real(rVar:=Circ[2].THDV_L2,lo:=4136,hi:=4137); |  | 68:ErrComCirc[4]:=Bit_0; | 68:ErrorComCirc[4].Code[9]:=Byte_0; |  |  | 4137:Circ[2].THDV_L2:=Real_0;
mind_bool[69]:=ErrComCirc[5]; | mind[69]:=ErrorComCirc[4].Status; |  |  | Read_Real(rVar:=Circ[2].THDV_L3,lo:=4138,hi:=4139); |  | 69:ErrComCirc[5]:=Bit_0; | 69:ErrorComCirc[4].Status:=Word_01; |  |  | 4139:Circ[2].THDV_L3:=Real_0;
mind_bool[70]:=ErrComKlima[1]; | mind[70]:=ErrorComCirc[5].Code[10]; |  |  | Read_Real(rVar:=Circ[2].Tok_L1,lo:=4140,hi:=4141); |  | 70:ErrComKlima[1]:=Bit_0; | 70:ErrorComCirc[5].Code[10]:=Byte_0; |  |  | 4141:Circ[2].Tok_L1:=Real_0;
mind_bool[71]:=ErrComKlima[2]; | mind[71]:=ErrorComCirc[5].Code[11]; |  |  | Read_Real(rVar:=Circ[2].Tok_L2,lo:=4142,hi:=4143); |  | 71:ErrComKlima[2]:=Bit_0; | 71:ErrorComCirc[5].Code[11]:=Byte_0; |  |  | 4143:Circ[2].Tok_L2:=Real_0;
mind_bool[72]:=ErrComKlima[3]; | mind[72]:=ErrorComCirc[5].Code[12]; |  |  | Read_Real(rVar:=Circ[2].Tok_L3,lo:=4144,hi:=4145); |  | 72:ErrComKlima[3]:=Bit_0; | 72:ErrorComCirc[5].Code[12]:=Byte_0; |  |  | 4145:Circ[2].Tok_L3:=Real_0;
mind_bool[73]:=ErrComKlima[4]; | mind[73]:=ErrorComCirc[5].Code[13]; |  |  | Read_Real(rVar:=Circ[2].TokPovprecje_III,lo:=4146,hi:=4147); |  | 73:ErrComKlima[4]:=Bit_0; | 73:ErrorComCirc[5].Code[13]:=Byte_0; |  |  | 4147:Circ[2].TokPovprecje_III:=Real_0;
mind_bool[74]:=ErrComKlima[5]; | mind[74]:=ErrorComCirc[5].Code[14]; |  |  | Read_Real(rVar:=Circ[3].CosFi_III,lo:=4148,hi:=4149); |  | 74:ErrComKlima[5]:=Bit_0; | 74:ErrorComCirc[5].Code[14]:=Byte_0; |  |  | 4149:Circ[3].CosFi_III:=Real_0;
mind_bool[75]:=ErrComKlima[6]; | mind[75]:=ErrorComCirc[5].Code[15]; |  |  | Read_Real(rVar:=Circ[3].DelovnaEnergija,lo:=4150,hi:=4151); |  | 75:ErrComKlima[6]:=Bit_0; | 75:ErrorComCirc[5].Code[15]:=Byte_0; |  |  | 4151:Circ[3].DelovnaEnergija:=Real_0;
mind_bool[76]:=ErrCommScada; | mind[76]:=ErrorComCirc[5].Code[1]; |  |  | Read_Real(rVar:=Circ[3].DelovnaMoc_III,lo:=4152,hi:=4153); |  | 76:ErrCommScada:=Bit_0; | 76:ErrorComCirc[5].Code[1]:=Byte_0; |  |  | 4153:Circ[3].DelovnaMoc_III:=Real_0;
mind_bool[77]:=ErrComPanelPLC; | mind[77]:=ErrorComCirc[5].Code[2]; |  |  | Read_Real(rVar:=Circ[3].DelovnaMoc_L1,lo:=4154,hi:=4155); |  | 77:ErrComPanelPLC:=Bit_0; | 77:ErrorComCirc[5].Code[2]:=Byte_0; |  |  | 4155:Circ[3].DelovnaMoc_L1:=Real_0;
mind_bool[78]:=ErrComPort2; | mind[78]:=ErrorComCirc[5].Code[3]; |  |  | Read_Real(rVar:=Circ[3].DelovnaMoc_L2,lo:=4156,hi:=4157); |  | 78:ErrComPort2:=Bit_0; | 78:ErrorComCirc[5].Code[3]:=Byte_0; |  |  | 4157:Circ[3].DelovnaMoc_L2:=Real_0;
mind_bool[79]:=ErrorComCirc[1].Error; | mind[79]:=ErrorComCirc[5].Code[4]; |  |  | Read_Real(rVar:=Circ[3].DelovnaMoc_L3,lo:=4158,hi:=4159); |  | 79:ErrorComCirc[1].Error:=Bit_0; | 79:ErrorComCirc[5].Code[4]:=Byte_0; |  |  | 4159:Circ[3].DelovnaMoc_L3:=Real_0;
mind_bool[80]:=ErrorComCirc[2].Error; | mind[80]:=ErrorComCirc[5].Code[5]; |  |  | Read_Real(rVar:=Circ[3].Frekvenca_L1,lo:=4160,hi:=4161); |  | 80:ErrorComCirc[2].Error:=Bit_0; | 80:ErrorComCirc[5].Code[5]:=Byte_0; |  |  | 4161:Circ[3].Frekvenca_L1:=Real_0;
mind_bool[81]:=ErrorComCirc[3].Error; | mind[81]:=ErrorComCirc[5].Code[6]; |  |  | Read_Real(rVar:=Circ[3].InduktivnaEnergija,lo:=4162,hi:=4163); |  | 81:ErrorComCirc[3].Error:=Bit_0; | 81:ErrorComCirc[5].Code[6]:=Byte_0; |  |  | 4163:Circ[3].InduktivnaEnergija:=Real_0;
mind_bool[82]:=ErrorComCirc[4].Error; | mind[82]:=ErrorComCirc[5].Code[7]; |  |  | Read_Real(rVar:=Circ[3].InduktivnaMoc_III,lo:=4164,hi:=4165); |  | 82:ErrorComCirc[4].Error:=Bit_0; | 82:ErrorComCirc[5].Code[7]:=Byte_0; |  |  | 4165:Circ[3].InduktivnaMoc_III:=Real_0;
mind_bool[83]:=ErrorComCirc[5].Error; | mind[83]:=ErrorComCirc[5].Code[8]; |  |  | Read_Real(rVar:=Circ[3].JalovaMoc_L1,lo:=4166,hi:=4167); |  | 83:ErrorComCirc[5].Error:=Bit_0; | 83:ErrorComCirc[5].Code[8]:=Byte_0; |  |  | 4167:Circ[3].JalovaMoc_L1:=Real_0;
mind_bool[84]:=ErrorComKlima[1].Error; | mind[84]:=ErrorComCirc[5].Code[9]; |  |  | Read_Real(rVar:=Circ[3].JalovaMoc_L2,lo:=4168,hi:=4169); |  | 84:ErrorComKlima[1].Error:=Bit_0; | 84:ErrorComCirc[5].Code[9]:=Byte_0; |  |  | 4169:Circ[3].JalovaMoc_L2:=Real_0;
mind_bool[85]:=ErrorComKlima[2].Error; | mind[85]:=ErrorComCirc[5].Status; |  |  | Read_Real(rVar:=Circ[3].JalovaMoc_L3,lo:=4170,hi:=4171); |  | 85:ErrorComKlima[2].Error:=Bit_0; | 85:ErrorComCirc[5].Status:=Word_01; |  |  | 4171:Circ[3].JalovaMoc_L3:=Real_0;
mind_bool[86]:=ErrorComKlima[3].Error; | mind[86]:=ErrorComKlima[1].Code[10]; |  |  | Read_Real(rVar:=Circ[3].KapacitivnaEnergija,lo:=4172,hi:=4173); |  | 86:ErrorComKlima[3].Error:=Bit_0; | 86:ErrorComKlima[1].Code[10]:=Byte_0; |  |  | 4173:Circ[3].KapacitivnaEnergija:=Real_0;
mind_bool[87]:=ErrorComKlima[4].Error; | mind[87]:=ErrorComKlima[1].Code[11]; |  |  | Read_Real(rVar:=Circ[3].KapacitivnaMoc_III,lo:=4174,hi:=4175); |  | 87:ErrorComKlima[4].Error:=Bit_0; | 87:ErrorComKlima[1].Code[11]:=Byte_0; |  |  | 4175:Circ[3].KapacitivnaMoc_III:=Real_0;
mind_bool[88]:=ErrorComKlima[5].Error; | mind[88]:=ErrorComKlima[1].Code[12]; |  |  | Read_Real(rVar:=Circ[3].MaximumDemand,lo:=4176,hi:=4177); |  | 88:ErrorComKlima[5].Error:=Bit_0; | 88:ErrorComKlima[1].Code[12]:=Byte_0; |  |  | 4177:Circ[3].MaximumDemand:=Real_0;
mind_bool[89]:=ErrorComKlima[6].Error; | mind[89]:=ErrorComKlima[1].Code[13]; |  |  | Read_Real(rVar:=Circ[3].Napetost_L1_L2,lo:=4178,hi:=4179); |  | 89:ErrorComKlima[6].Error:=Bit_0; | 89:ErrorComKlima[1].Code[13]:=Byte_0; |  |  | 4179:Circ[3].Napetost_L1_L2:=Real_0;
mind_bool[90]:=Klima[1].AlarmKompresor1; | mind[90]:=ErrorComKlima[1].Code[14]; |  |  | Read_Real(rVar:=Circ[3].Napetost_L1_N,lo:=4180,hi:=4181); |  | 90:Klima[1].AlarmKompresor1:=Bit_0; | 90:ErrorComKlima[1].Code[14]:=Byte_0; |  |  | 4181:Circ[3].Napetost_L1_N:=Real_0;
mind_bool[91]:=Klima[1].AlarmKompresor2; | mind[91]:=ErrorComKlima[1].Code[15]; |  |  | Read_Real(rVar:=Circ[3].Napetost_L2_L3,lo:=4182,hi:=4183); |  | 91:Klima[1].AlarmKompresor2:=Bit_0; | 91:ErrorComKlima[1].Code[15]:=Byte_0; |  |  | 4183:Circ[3].Napetost_L2_L3:=Real_0;
mind_bool[92]:=Klima[1].Deluje; | mind[92]:=ErrorComKlima[1].Code[1]; |  |  | Read_Real(rVar:=Circ[3].Napetost_L2_N,lo:=4184,hi:=4185); |  | 92:Klima[1].Deluje:=Bit_0; | 92:ErrorComKlima[1].Code[1]:=Byte_0; |  |  | 4185:Circ[3].Napetost_L2_N:=Real_0;
mind_bool[93]:=Klima[1].EnergySaving; | mind[93]:=ErrorComKlima[1].Code[2]; |  |  | Read_Real(rVar:=Circ[3].Napetost_L3_L1,lo:=4186,hi:=4187); |  | 93:Klima[1].EnergySaving:=Bit_0; | 93:ErrorComKlima[1].Code[2]:=Byte_0; |  |  | 4187:Circ[3].Napetost_L3_L1:=Real_0;
mind_bool[94]:=Klima[1].FaultyEPROM; | mind[94]:=ErrorComKlima[1].Code[3]; |  |  | Read_Real(rVar:=Circ[3].Napetost_L3_N,lo:=4188,hi:=4189); |  | 94:Klima[1].FaultyEPROM:=Bit_0; | 94:ErrorComKlima[1].Code[3]:=Byte_0; |  |  | 4189:Circ[3].Napetost_L3_N:=Real_0;
mind_bool[95]:=Klima[1].FenThermalCutout; | mind[95]:=ErrorComKlima[1].Code[4]; |  |  | Read_Real(rVar:=Circ[3].NavideznaMoc_III,lo:=4190,hi:=4191); |  | 95:Klima[1].FenThermalCutout:=Bit_0; | 95:ErrorComKlima[1].Code[4]:=Byte_0; |  |  | 4191:Circ[3].NavideznaMoc_III:=Real_0;
mind_bool[96]:=Klima[1].GeneralAlarm; | mind[96]:=ErrorComKlima[1].Code[5]; |  |  | Read_Real(rVar:=Circ[3].NicelniTok,lo:=4192,hi:=4193); |  | 96:Klima[1].GeneralAlarm:=Bit_0; | 96:ErrorComKlima[1].Code[5]:=Byte_0; |  |  | 4193:Circ[3].NicelniTok:=Real_0;
mind_bool[97]:=Klima[1].Kompresor1naMejiObrUr; | mind[97]:=ErrorComKlima[1].Code[6]; |  |  | Read_Real(rVar:=Circ[3].PowerFactor_III,lo:=4194,hi:=4195); |  | 97:Klima[1].Kompresor1naMejiObrUr:=Bit_0; | 97:ErrorComKlima[1].Code[6]:=Byte_0; |  |  | 4195:Circ[3].PowerFactor_III:=Real_0;
mind_bool[98]:=Klima[1].Kompresor2naMejiObrUr; | mind[98]:=ErrorComKlima[1].Code[7]; |  |  | Read_Real(rVar:=Circ[3].PowerFactor_L1,lo:=4196,hi:=4197); |  | 98:Klima[1].Kompresor2naMejiObrUr:=Bit_0; | 98:ErrorComKlima[1].Code[7]:=Byte_0; |  |  | 4197:Circ[3].PowerFactor_L1:=Real_0;
mind_bool[99]:=Klima[1].Napaka; | mind[99]:=ErrorComKlima[1].Code[8]; |  |  | Read_Real(rVar:=Circ[3].PowerFactor_L2,lo:=4198,hi:=4199); |  | 99:Klima[1].Napaka:=Bit_0; | 99:ErrorComKlima[1].Code[8]:=Byte_0; |  |  | 4199:Circ[3].PowerFactor_L2:=Real_0;
mind_bool[100]:=Klima[1].NapakaPriPretokuZraka; | mind[100]:=ErrorComKlima[1].Code[9]; |  |  | Read_Real(rVar:=Circ[3].PowerFactor_L3,lo:=4200,hi:=4201); |  | 100:Klima[1].NapakaPriPretokuZraka:=Bit_0; | 100:ErrorComKlima[1].Code[9]:=Byte_0; |  |  | 4201:Circ[3].PowerFactor_L3:=Real_0;
mind_bool[101]:=Klima[1].NapakaSenzorPovratVode; | mind[101]:=ErrorComKlima[1].Status; |  |  | Read_Real(rVar:=Circ[3].THDI_L1,lo:=4202,hi:=4203); |  | 101:Klima[1].NapakaSenzorPovratVode:=Bit_0; | 101:ErrorComKlima[1].Status:=Word_01; |  |  | 4203:Circ[3].THDI_L1:=Real_0;
mind_bool[102]:=Klima[1].NapakaSenzorTempIzpiha; | mind[102]:=ErrorComKlima[2].Code[10]; |  |  | Read_Real(rVar:=Circ[3].THDI_L2,lo:=4204,hi:=4205); |  | 102:Klima[1].NapakaSenzorTempIzpiha:=Bit_0; | 102:ErrorComKlima[2].Code[10]:=Byte_0; |  |  | 4205:Circ[3].THDI_L2:=Real_0;
mind_bool[103]:=Klima[1].NapakaSenzorTempProstora; | mind[103]:=ErrorComKlima[2].Code[11]; |  |  | Read_Real(rVar:=Circ[3].THDI_L3,lo:=4206,hi:=4207); |  | 103:Klima[1].NapakaSenzorTempProstora:=Bit_0; | 103:ErrorComKlima[2].Code[11]:=Byte_0; |  |  | 4207:Circ[3].THDI_L3:=Real_0;
mind_bool[104]:=Klima[1].NapakaSenzorVlaznosti; | mind[104]:=ErrorComKlima[2].Code[12]; |  |  | Read_Real(rVar:=Circ[3].THDV_L1,lo:=4208,hi:=4209); |  | 104:Klima[1].NapakaSenzorVlaznosti:=Bit_0; | 104:ErrorComKlima[2].Code[12]:=Byte_0; |  |  | 4209:Circ[3].THDV_L1:=Real_0;
mind_bool[105]:=Klima[1].NapakaSenzorZunanjeTemp; | mind[105]:=ErrorComKlima[2].Code[13]; |  |  | Read_Real(rVar:=Circ[3].THDV_L2,lo:=4210,hi:=4211); |  | 105:Klima[1].NapakaSenzorZunanjeTemp:=Bit_0; | 105:ErrorComKlima[2].Code[13]:=Byte_0; |  |  | 4211:Circ[3].THDV_L2:=Real_0;
mind_bool[106]:=Klima[1].NiTokaVVlazilcu; | mind[106]:=ErrorComKlima[2].Code[14]; |  |  | Read_Real(rVar:=Circ[3].THDV_L3,lo:=4212,hi:=4213); |  | 106:Klima[1].NiTokaVVlazilcu:=Bit_0; | 106:ErrorComKlima[2].Code[14]:=Byte_0; |  |  | 4213:Circ[3].THDV_L3:=Real_0;
mind_bool[107]:=Klima[1].NiVodeVVlazilcu; | mind[107]:=ErrorComKlima[2].Code[15]; |  |  | Read_Real(rVar:=Circ[3].Tok_L1,lo:=4214,hi:=4215); |  | 107:Klima[1].NiVodeVVlazilcu:=Bit_0; | 107:ErrorComKlima[2].Code[15]:=Byte_0; |  |  | 4215:Circ[3].Tok_L1:=Real_0;
mind_bool[108]:=Klima[1].NizekPritiskKompresor1; | mind[108]:=ErrorComKlima[2].Code[1]; |  |  | Read_Real(rVar:=Circ[3].Tok_L2,lo:=4216,hi:=4217); |  | 108:Klima[1].NizekPritiskKompresor1:=Bit_0; | 108:ErrorComKlima[2].Code[1]:=Byte_0; |  |  | 4217:Circ[3].Tok_L2:=Real_0;
mind_bool[109]:=Klima[1].NizekPritiskKompresor2; | mind[109]:=ErrorComKlima[2].Code[2]; |  |  | Read_Real(rVar:=Circ[3].Tok_L3,lo:=4218,hi:=4219); |  | 109:Klima[1].NizekPritiskKompresor2:=Bit_0; | 109:ErrorComKlima[2].Code[2]:=Byte_0; |  |  | 4219:Circ[3].Tok_L3:=Real_0;
mind_bool[110]:=Klima[1].NizkaTempPovratneVode; | mind[110]:=ErrorComKlima[2].Code[3]; |  |  | Read_Real(rVar:=Circ[3].TokPovprecje_III,lo:=4220,hi:=4221); |  | 110:Klima[1].NizkaTempPovratneVode:=Bit_0; | 110:ErrorComKlima[2].Code[3]:=Byte_0; |  |  | 4221:Circ[3].TokPovprecje_III:=Real_0;
mind_bool[111]:=Klima[1].NizkaTempVProstoru; | mind[111]:=ErrorComKlima[2].Code[4]; |  |  | Read_Real(rVar:=Circ[4].CosFi_III,lo:=4222,hi:=4223); |  | 111:Klima[1].NizkaTempVProstoru:=Bit_0; | 111:ErrorComKlima[2].Code[4]:=Byte_0; |  |  | 4223:Circ[4].CosFi_III:=Real_0;
mind_bool[112]:=Klima[1].NizkaVlaznost; | mind[112]:=ErrorComKlima[2].Code[5]; |  |  | Read_Real(rVar:=Circ[4].DelovnaEnergija,lo:=4224,hi:=4225); |  | 112:Klima[1].NizkaVlaznost:=Bit_0; | 112:ErrorComKlima[2].Code[5]:=Byte_0; |  |  | 4225:Circ[4].DelovnaEnergija:=Real_0;
mind_bool[113]:=Klima[1].OnOffEnablingBySupervisor; | mind[113]:=ErrorComKlima[2].Code[6]; |  |  | Read_Real(rVar:=Circ[4].DelovnaMoc_III,lo:=4226,hi:=4227); |  | 113:Klima[1].OnOffEnablingBySupervisor:=Bit_0; | 113:ErrorComKlima[2].Code[6]:=Byte_0; |  |  | 4227:Circ[4].DelovnaMoc_III:=Real_0;
mind_bool[114]:=Klima[1].PozarniAlarm; | mind[114]:=ErrorComKlima[2].Code[7]; |  |  | Read_Real(rVar:=Circ[4].DelovnaMoc_L1,lo:=4228,hi:=4229); |  | 114:Klima[1].PozarniAlarm:=Bit_0; | 114:ErrorComKlima[2].Code[7]:=Byte_0; |  |  | 4229:Circ[4].DelovnaMoc_L1:=Real_0;
mind_bool[115]:=Klima[1].Razvlazevanje; | mind[115]:=ErrorComKlima[2].Code[8]; |  |  | Read_Real(rVar:=Circ[4].DelovnaMoc_L2,lo:=4230,hi:=4231); |  | 115:Klima[1].Razvlazevanje:=Bit_0; | 115:ErrorComKlima[2].Code[8]:=Byte_0; |  |  | 4231:Circ[4].DelovnaMoc_L2:=Real_0;
mind_bool[116]:=Klima[1].RemoteOFFtoOutput; | mind[116]:=ErrorComKlima[2].Code[9]; |  |  | Read_Real(rVar:=Circ[4].DelovnaMoc_L3,lo:=4232,hi:=4233); |  | 116:Klima[1].RemoteOFFtoOutput:=Bit_0; | 116:ErrorComKlima[2].Code[9]:=Byte_0; |  |  | 4233:Circ[4].DelovnaMoc_L3:=Real_0;
mind_bool[117]:=Klima[1].RemoteOnOff; | mind[117]:=ErrorComKlima[2].Status; |  |  | Read_Real(rVar:=Circ[4].Frekvenca_L1,lo:=4234,hi:=4235); |  | 117:Klima[1].RemoteOnOff:=Bit_0; | 117:ErrorComKlima[2].Status:=Word_01; |  |  | 4235:Circ[4].Frekvenca_L1:=Real_0;
mind_bool[118]:=Klima[1].RocniIzklop; | mind[118]:=ErrorComKlima[3].Code[10]; |  |  | Read_Real(rVar:=Circ[4].InduktivnaEnergija,lo:=4236,hi:=4237); |  | 118:Klima[1].RocniIzklop:=Bit_0; | 118:ErrorComKlima[3].Code[10]:=Byte_0; |  |  | 4237:Circ[4].InduktivnaEnergija:=Real_0;
mind_bool[119]:=Klima[1].SenzorjiStatus; | mind[119]:=ErrorComKlima[3].Code[11]; |  |  | Read_Real(rVar:=Circ[4].InduktivnaMoc_III,lo:=4238,hi:=4239); |  | 119:Klima[1].SenzorjiStatus:=Bit_0; | 119:ErrorComKlima[3].Code[11]:=Byte_0; |  |  | 4239:Circ[4].InduktivnaMoc_III:=Real_0;
mind_bool[120]:=Klima[1].StoppedByAlarms; | mind[120]:=ErrorComKlima[3].Code[12]; |  |  | Read_Real(rVar:=Circ[4].JalovaMoc_L1,lo:=4240,hi:=4241); |  | 120:Klima[1].StoppedByAlarms:=Bit_0; | 120:ErrorComKlima[3].Code[12]:=Byte_0; |  |  | 4241:Circ[4].JalovaMoc_L1:=Real_0;
mind_bool[121]:=Klima[1].ThermalCutoutHeater1; | mind[121]:=ErrorComKlima[3].Code[13]; |  |  | Read_Real(rVar:=Circ[4].JalovaMoc_L2,lo:=4242,hi:=4243); |  | 121:Klima[1].ThermalCutoutHeater1:=Bit_0; | 121:ErrorComKlima[3].Code[13]:=Byte_0; |  |  | 4243:Circ[4].JalovaMoc_L2:=Real_0;
mind_bool[122]:=Klima[1].ThermalCutoutHeater2; | mind[122]:=ErrorComKlima[3].Code[14]; |  |  | Read_Real(rVar:=Circ[4].JalovaMoc_L3,lo:=4244,hi:=4245); |  | 122:Klima[1].ThermalCutoutHeater2:=Bit_0; | 122:ErrorComKlima[3].Code[14]:=Byte_0; |  |  | 4245:Circ[4].JalovaMoc_L3:=Real_0;
mind_bool[123]:=Klima[1].UnitOnOff; | mind[123]:=ErrorComKlima[3].Code[15]; |  |  | Read_Real(rVar:=Circ[4].KapacitivnaEnergija,lo:=4246,hi:=4247); |  | 123:Klima[1].UnitOnOff:=Bit_0; | 123:ErrorComKlima[3].Code[15]:=Byte_0; |  |  | 4247:Circ[4].KapacitivnaEnergija:=Real_0;
mind_bool[124]:=Klima[1].VentilatorNaMejiObrUr; | mind[124]:=ErrorComKlima[3].Code[1]; |  |  | Read_Real(rVar:=Circ[4].KapacitivnaMoc_III,lo:=4248,hi:=4249); |  | 124:Klima[1].VentilatorNaMejiObrUr:=Bit_0; | 124:ErrorComKlima[3].Code[1]:=Byte_0; |  |  | 4249:Circ[4].KapacitivnaMoc_III:=Real_0;
mind_bool[125]:=Klima[1].VentilGretjeOdpiranje; | mind[125]:=ErrorComKlima[3].Code[2]; |  |  | Read_Real(rVar:=Circ[4].MaximumDemand,lo:=4250,hi:=4251); |  | 125:Klima[1].VentilGretjeOdpiranje:=Bit_0; | 125:ErrorComKlima[3].Code[2]:=Byte_0; |  |  | 4251:Circ[4].MaximumDemand:=Real_0;
mind_bool[126]:=Klima[1].VentilGretjeZapiranje; | mind[126]:=ErrorComKlima[3].Code[3]; |  |  | Read_Real(rVar:=Circ[4].Napetost_L1_L2,lo:=4252,hi:=4253); |  | 126:Klima[1].VentilGretjeZapiranje:=Bit_0; | 126:ErrorComKlima[3].Code[3]:=Byte_0; |  |  | 4253:Circ[4].Napetost_L1_L2:=Real_0;
mind_bool[127]:=Klima[1].VentilHlajenjeOdpiranje; | mind[127]:=ErrorComKlima[3].Code[4]; |  |  | Read_Real(rVar:=Circ[4].Napetost_L1_N,lo:=4254,hi:=4255); |  | 127:Klima[1].VentilHlajenjeOdpiranje:=Bit_0; | 127:ErrorComKlima[3].Code[4]:=Byte_0; |  |  | 4255:Circ[4].Napetost_L1_N:=Real_0;
mind_bool[128]:=Klima[1].VentilHlajenjeZapiranje; | mind[128]:=ErrorComKlima[3].Code[5]; |  |  | Read_Real(rVar:=Circ[4].Napetost_L2_L3,lo:=4256,hi:=4257); |  | 128:Klima[1].VentilHlajenjeZapiranje:=Bit_0; | 128:ErrorComKlima[3].Code[5]:=Byte_0; |  |  | 4257:Circ[4].Napetost_L2_L3:=Real_0;
mind_bool[129]:=Klima[1].VisokaTempPovratneVode; | mind[129]:=ErrorComKlima[3].Code[6]; |  |  | Read_Real(rVar:=Circ[4].Napetost_L2_N,lo:=4258,hi:=4259); |  | 129:Klima[1].VisokaTempPovratneVode:=Bit_0; | 129:ErrorComKlima[3].Code[6]:=Byte_0; |  |  | 4259:Circ[4].Napetost_L2_N:=Real_0;
mind_bool[130]:=Klima[1].VisokaTempVProstoru; | mind[130]:=ErrorComKlima[3].Code[7]; |  |  | Read_Real(rVar:=Circ[4].Napetost_L3_L1,lo:=4260,hi:=4261); |  | 130:Klima[1].VisokaTempVProstoru:=Bit_0; | 130:ErrorComKlima[3].Code[7]:=Byte_0; |  |  | 4261:Circ[4].Napetost_L3_L1:=Real_0;
mind_bool[131]:=Klima[1].VisokaVlaznost; | mind[131]:=ErrorComKlima[3].Code[8]; |  |  | Read_Real(rVar:=Circ[4].Napetost_L3_N,lo:=4262,hi:=4263); |  | 131:Klima[1].VisokaVlaznost:=Bit_0; | 131:ErrorComKlima[3].Code[8]:=Byte_0; |  |  | 4263:Circ[4].Napetost_L3_N:=Real_0;
mind_bool[132]:=Klima[1].VisokTokVVlazilcu; | mind[132]:=ErrorComKlima[3].Code[9]; |  |  | Read_Real(rVar:=Circ[4].NavideznaMoc_III,lo:=4264,hi:=4265); |  | 132:Klima[1].VisokTokVVlazilcu:=Bit_0; | 132:ErrorComKlima[3].Code[9]:=Byte_0; |  |  | 4265:Circ[4].NavideznaMoc_III:=Real_0;
mind_bool[133]:=Klima[1].Vlazenje; | mind[133]:=ErrorComKlima[3].Status; |  |  | Read_Real(rVar:=Circ[4].NicelniTok,lo:=4266,hi:=4267); |  | 133:Klima[1].Vlazenje:=Bit_0; | 133:ErrorComKlima[3].Status:=Word_01; |  |  | 4267:Circ[4].NicelniTok:=Real_0;
mind_bool[134]:=Klima[1].ZamasenFilter; | mind[134]:=ErrorComKlima[4].Code[10]; |  |  | Read_Real(rVar:=Circ[4].PowerFactor_III,lo:=4268,hi:=4269); |  | 134:Klima[1].ZamasenFilter:=Bit_0; | 134:ErrorComKlima[4].Code[10]:=Byte_0; |  |  | 4269:Circ[4].PowerFactor_III:=Real_0;
mind_bool[135]:=Klima[2].AlarmKompresor1; | mind[135]:=ErrorComKlima[4].Code[11]; |  |  | Read_Real(rVar:=Circ[4].PowerFactor_L1,lo:=4270,hi:=4271); |  | 135:Klima[2].AlarmKompresor1:=Bit_0; | 135:ErrorComKlima[4].Code[11]:=Byte_0; |  |  | 4271:Circ[4].PowerFactor_L1:=Real_0;
mind_bool[136]:=Klima[2].AlarmKompresor2; | mind[136]:=ErrorComKlima[4].Code[12]; |  |  | Read_Real(rVar:=Circ[4].PowerFactor_L2,lo:=4272,hi:=4273); |  | 136:Klima[2].AlarmKompresor2:=Bit_0; | 136:ErrorComKlima[4].Code[12]:=Byte_0; |  |  | 4273:Circ[4].PowerFactor_L2:=Real_0;
mind_bool[137]:=Klima[2].Deluje; | mind[137]:=ErrorComKlima[4].Code[13]; |  |  | Read_Real(rVar:=Circ[4].PowerFactor_L3,lo:=4274,hi:=4275); |  | 137:Klima[2].Deluje:=Bit_0; | 137:ErrorComKlima[4].Code[13]:=Byte_0; |  |  | 4275:Circ[4].PowerFactor_L3:=Real_0;
mind_bool[138]:=Klima[2].EnergySaving; | mind[138]:=ErrorComKlima[4].Code[14]; |  |  | Read_Real(rVar:=Circ[4].THDI_L1,lo:=4276,hi:=4277); |  | 138:Klima[2].EnergySaving:=Bit_0; | 138:ErrorComKlima[4].Code[14]:=Byte_0; |  |  | 4277:Circ[4].THDI_L1:=Real_0;
mind_bool[139]:=Klima[2].FaultyEPROM; | mind[139]:=ErrorComKlima[4].Code[15]; |  |  | Read_Real(rVar:=Circ[4].THDI_L2,lo:=4278,hi:=4279); |  | 139:Klima[2].FaultyEPROM:=Bit_0; | 139:ErrorComKlima[4].Code[15]:=Byte_0; |  |  | 4279:Circ[4].THDI_L2:=Real_0;
mind_bool[140]:=Klima[2].FenThermalCutout; | mind[140]:=ErrorComKlima[4].Code[1]; |  |  | Read_Real(rVar:=Circ[4].THDI_L3,lo:=4280,hi:=4281); |  | 140:Klima[2].FenThermalCutout:=Bit_0; | 140:ErrorComKlima[4].Code[1]:=Byte_0; |  |  | 4281:Circ[4].THDI_L3:=Real_0;
mind_bool[141]:=Klima[2].GeneralAlarm; | mind[141]:=ErrorComKlima[4].Code[2]; |  |  | Read_Real(rVar:=Circ[4].THDV_L1,lo:=4282,hi:=4283); |  | 141:Klima[2].GeneralAlarm:=Bit_0; | 141:ErrorComKlima[4].Code[2]:=Byte_0; |  |  | 4283:Circ[4].THDV_L1:=Real_0;
mind_bool[142]:=Klima[2].Kompresor1naMejiObrUr; | mind[142]:=ErrorComKlima[4].Code[3]; |  |  | Read_Real(rVar:=Circ[4].THDV_L2,lo:=4284,hi:=4285); |  | 142:Klima[2].Kompresor1naMejiObrUr:=Bit_0; | 142:ErrorComKlima[4].Code[3]:=Byte_0; |  |  | 4285:Circ[4].THDV_L2:=Real_0;
mind_bool[143]:=Klima[2].Kompresor2naMejiObrUr; | mind[143]:=ErrorComKlima[4].Code[4]; |  |  | Read_Real(rVar:=Circ[4].THDV_L3,lo:=4286,hi:=4287); |  | 143:Klima[2].Kompresor2naMejiObrUr:=Bit_0; | 143:ErrorComKlima[4].Code[4]:=Byte_0; |  |  | 4287:Circ[4].THDV_L3:=Real_0;
mind_bool[144]:=Klima[2].Napaka; | mind[144]:=ErrorComKlima[4].Code[5]; |  |  | Read_Real(rVar:=Circ[4].Tok_L1,lo:=4288,hi:=4289); |  | 144:Klima[2].Napaka:=Bit_0; | 144:ErrorComKlima[4].Code[5]:=Byte_0; |  |  | 4289:Circ[4].Tok_L1:=Real_0;
mind_bool[145]:=Klima[2].NapakaPriPretokuZraka; | mind[145]:=ErrorComKlima[4].Code[6]; |  |  | Read_Real(rVar:=Circ[4].Tok_L2,lo:=4290,hi:=4291); |  | 145:Klima[2].NapakaPriPretokuZraka:=Bit_0; | 145:ErrorComKlima[4].Code[6]:=Byte_0; |  |  | 4291:Circ[4].Tok_L2:=Real_0;
mind_bool[146]:=Klima[2].NapakaSenzorPovratVode; | mind[146]:=ErrorComKlima[4].Code[7]; |  |  | Read_Real(rVar:=Circ[4].Tok_L3,lo:=4292,hi:=4293); |  | 146:Klima[2].NapakaSenzorPovratVode:=Bit_0; | 146:ErrorComKlima[4].Code[7]:=Byte_0; |  |  | 4293:Circ[4].Tok_L3:=Real_0;
mind_bool[147]:=Klima[2].NapakaSenzorTempIzpiha; | mind[147]:=ErrorComKlima[4].Code[8]; |  |  | Read_Real(rVar:=Circ[4].TokPovprecje_III,lo:=4294,hi:=4295); |  | 147:Klima[2].NapakaSenzorTempIzpiha:=Bit_0; | 147:ErrorComKlima[4].Code[8]:=Byte_0; |  |  | 4295:Circ[4].TokPovprecje_III:=Real_0;
mind_bool[148]:=Klima[2].NapakaSenzorTempProstora; | mind[148]:=ErrorComKlima[4].Code[9]; |  |  | Read_Real(rVar:=Circutor.CosFi_III,lo:=4296,hi:=4297); |  | 148:Klima[2].NapakaSenzorTempProstora:=Bit_0; | 148:ErrorComKlima[4].Code[9]:=Byte_0; |  |  | 4297:Circutor.CosFi_III:=Real_0;
mind_bool[149]:=Klima[2].NapakaSenzorVlaznosti; | mind[149]:=ErrorComKlima[4].Status; |  |  | Read_Real(rVar:=Circutor.DelovnaEnergija,lo:=4298,hi:=4299); |  | 149:Klima[2].NapakaSenzorVlaznosti:=Bit_0; | 149:ErrorComKlima[4].Status:=Word_01; |  |  | 4299:Circutor.DelovnaEnergija:=Real_0;
mind_bool[150]:=Klima[2].NapakaSenzorZunanjeTemp; | mind[150]:=ErrorComKlima[5].Code[10]; |  |  | Read_Real(rVar:=Circutor.DelovnaMoc_III,lo:=4300,hi:=4301); |  | 150:Klima[2].NapakaSenzorZunanjeTemp:=Bit_0; | 150:ErrorComKlima[5].Code[10]:=Byte_0; |  |  | 4301:Circutor.DelovnaMoc_III:=Real_0;
mind_bool[151]:=Klima[2].NiTokaVVlazilcu; | mind[151]:=ErrorComKlima[5].Code[11]; |  |  | Read_Real(rVar:=Circutor.DelovnaMoc_L1,lo:=4302,hi:=4303); |  | 151:Klima[2].NiTokaVVlazilcu:=Bit_0; | 151:ErrorComKlima[5].Code[11]:=Byte_0; |  |  | 4303:Circutor.DelovnaMoc_L1:=Real_0;
mind_bool[152]:=Klima[2].NiVodeVVlazilcu; | mind[152]:=ErrorComKlima[5].Code[12]; |  |  | Read_Real(rVar:=Circutor.DelovnaMoc_L2,lo:=4304,hi:=4305); |  | 152:Klima[2].NiVodeVVlazilcu:=Bit_0; | 152:ErrorComKlima[5].Code[12]:=Byte_0; |  |  | 4305:Circutor.DelovnaMoc_L2:=Real_0;
mind_bool[153]:=Klima[2].NizekPritiskKompresor1; | mind[153]:=ErrorComKlima[5].Code[13]; |  |  | Read_Real(rVar:=Circutor.DelovnaMoc_L3,lo:=4306,hi:=4307); |  | 153:Klima[2].NizekPritiskKompresor1:=Bit_0; | 153:ErrorComKlima[5].Code[13]:=Byte_0; |  |  | 4307:Circutor.DelovnaMoc_L3:=Real_0;
mind_bool[154]:=Klima[2].NizekPritiskKompresor2; | mind[154]:=ErrorComKlima[5].Code[14]; |  |  | Read_Real(rVar:=Circutor.Frekvenca_L1,lo:=4308,hi:=4309); |  | 154:Klima[2].NizekPritiskKompresor2:=Bit_0; | 154:ErrorComKlima[5].Code[14]:=Byte_0; |  |  | 4309:Circutor.Frekvenca_L1:=Real_0;
mind_bool[155]:=Klima[2].NizkaTempPovratneVode; | mind[155]:=ErrorComKlima[5].Code[15]; |  |  | Read_Real(rVar:=Circutor.InduktivnaEnergija,lo:=4310,hi:=4311); |  | 155:Klima[2].NizkaTempPovratneVode:=Bit_0; | 155:ErrorComKlima[5].Code[15]:=Byte_0; |  |  | 4311:Circutor.InduktivnaEnergija:=Real_0;
mind_bool[156]:=Klima[2].NizkaTempVProstoru; | mind[156]:=ErrorComKlima[5].Code[1]; |  |  | Read_Real(rVar:=Circutor.InduktivnaMoc_III,lo:=4312,hi:=4313); |  | 156:Klima[2].NizkaTempVProstoru:=Bit_0; | 156:ErrorComKlima[5].Code[1]:=Byte_0; |  |  | 4313:Circutor.InduktivnaMoc_III:=Real_0;
mind_bool[157]:=Klima[2].NizkaVlaznost; | mind[157]:=ErrorComKlima[5].Code[2]; |  |  | Read_Real(rVar:=Circutor.JalovaMoc_L1,lo:=4314,hi:=4315); |  | 157:Klima[2].NizkaVlaznost:=Bit_0; | 157:ErrorComKlima[5].Code[2]:=Byte_0; |  |  | 4315:Circutor.JalovaMoc_L1:=Real_0;
mind_bool[158]:=Klima[2].OnOffEnablingBySupervisor; | mind[158]:=ErrorComKlima[5].Code[3]; |  |  | Read_Real(rVar:=Circutor.JalovaMoc_L2,lo:=4316,hi:=4317); |  | 158:Klima[2].OnOffEnablingBySupervisor:=Bit_0; | 158:ErrorComKlima[5].Code[3]:=Byte_0; |  |  | 4317:Circutor.JalovaMoc_L2:=Real_0;
mind_bool[159]:=Klima[2].PozarniAlarm; | mind[159]:=ErrorComKlima[5].Code[4]; |  |  | Read_Real(rVar:=Circutor.JalovaMoc_L3,lo:=4318,hi:=4319); |  | 159:Klima[2].PozarniAlarm:=Bit_0; | 159:ErrorComKlima[5].Code[4]:=Byte_0; |  |  | 4319:Circutor.JalovaMoc_L3:=Real_0;
mind_bool[160]:=Klima[2].Razvlazevanje; | mind[160]:=ErrorComKlima[5].Code[5]; |  |  | Read_Real(rVar:=Circutor.KapacitivnaEnergija,lo:=4320,hi:=4321); |  | 160:Klima[2].Razvlazevanje:=Bit_0; | 160:ErrorComKlima[5].Code[5]:=Byte_0; |  |  | 4321:Circutor.KapacitivnaEnergija:=Real_0;
mind_bool[161]:=Klima[2].RemoteOFFtoOutput; | mind[161]:=ErrorComKlima[5].Code[6]; |  |  | Read_Real(rVar:=Circutor.KapacitivnaMoc_III,lo:=4322,hi:=4323); |  | 161:Klima[2].RemoteOFFtoOutput:=Bit_0; | 161:ErrorComKlima[5].Code[6]:=Byte_0; |  |  | 4323:Circutor.KapacitivnaMoc_III:=Real_0;
mind_bool[162]:=Klima[2].RemoteOnOff; | mind[162]:=ErrorComKlima[5].Code[7]; |  |  | Read_Real(rVar:=Circutor.MaximumDemand,lo:=4324,hi:=4325); |  | 162:Klima[2].RemoteOnOff:=Bit_0; | 162:ErrorComKlima[5].Code[7]:=Byte_0; |  |  | 4325:Circutor.MaximumDemand:=Real_0;
mind_bool[163]:=Klima[2].RocniIzklop; | mind[163]:=ErrorComKlima[5].Code[8]; |  |  | Read_Real(rVar:=Circutor.Napetost_L1_L2,lo:=4326,hi:=4327); |  | 163:Klima[2].RocniIzklop:=Bit_0; | 163:ErrorComKlima[5].Code[8]:=Byte_0; |  |  | 4327:Circutor.Napetost_L1_L2:=Real_0;
mind_bool[164]:=Klima[2].SenzorjiStatus; | mind[164]:=ErrorComKlima[5].Code[9]; |  |  | Read_Real(rVar:=Circutor.Napetost_L1_N,lo:=4328,hi:=4329); |  | 164:Klima[2].SenzorjiStatus:=Bit_0; | 164:ErrorComKlima[5].Code[9]:=Byte_0; |  |  | 4329:Circutor.Napetost_L1_N:=Real_0;
mind_bool[165]:=Klima[2].StoppedByAlarms; | mind[165]:=ErrorComKlima[5].Status; |  |  | Read_Real(rVar:=Circutor.Napetost_L2_L3,lo:=4330,hi:=4331); |  | 165:Klima[2].StoppedByAlarms:=Bit_0; | 165:ErrorComKlima[5].Status:=Word_01; |  |  | 4331:Circutor.Napetost_L2_L3:=Real_0;
mind_bool[166]:=Klima[2].ThermalCutoutHeater1; | mind[166]:=ErrorComKlima[6].Code[10]; |  |  | Read_Real(rVar:=Circutor.Napetost_L2_N,lo:=4332,hi:=4333); |  | 166:Klima[2].ThermalCutoutHeater1:=Bit_0; | 166:ErrorComKlima[6].Code[10]:=Byte_0; |  |  | 4333:Circutor.Napetost_L2_N:=Real_0;
mind_bool[167]:=Klima[2].ThermalCutoutHeater2; | mind[167]:=ErrorComKlima[6].Code[11]; |  |  | Read_Real(rVar:=Circutor.Napetost_L3_L1,lo:=4334,hi:=4335); |  | 167:Klima[2].ThermalCutoutHeater2:=Bit_0; | 167:ErrorComKlima[6].Code[11]:=Byte_0; |  |  | 4335:Circutor.Napetost_L3_L1:=Real_0;
mind_bool[168]:=Klima[2].UnitOnOff; | mind[168]:=ErrorComKlima[6].Code[12]; |  |  | Read_Real(rVar:=Circutor.Napetost_L3_N,lo:=4336,hi:=4337); |  | 168:Klima[2].UnitOnOff:=Bit_0; | 168:ErrorComKlima[6].Code[12]:=Byte_0; |  |  | 4337:Circutor.Napetost_L3_N:=Real_0;
mind_bool[169]:=Klima[2].VentilatorNaMejiObrUr; | mind[169]:=ErrorComKlima[6].Code[13]; |  |  | Read_Real(rVar:=Circutor.NavideznaMoc_III,lo:=4338,hi:=4339); |  | 169:Klima[2].VentilatorNaMejiObrUr:=Bit_0; | 169:ErrorComKlima[6].Code[13]:=Byte_0; |  |  | 4339:Circutor.NavideznaMoc_III:=Real_0;
mind_bool[170]:=Klima[2].VentilGretjeOdpiranje; | mind[170]:=ErrorComKlima[6].Code[14]; |  |  | Read_Real(rVar:=Circutor.NicelniTok,lo:=4340,hi:=4341); |  | 170:Klima[2].VentilGretjeOdpiranje:=Bit_0; | 170:ErrorComKlima[6].Code[14]:=Byte_0; |  |  | 4341:Circutor.NicelniTok:=Real_0;
mind_bool[171]:=Klima[2].VentilGretjeZapiranje; | mind[171]:=ErrorComKlima[6].Code[15]; |  |  | Read_Real(rVar:=Circutor.PowerFactor_III,lo:=4342,hi:=4343); |  | 171:Klima[2].VentilGretjeZapiranje:=Bit_0; | 171:ErrorComKlima[6].Code[15]:=Byte_0; |  |  | 4343:Circutor.PowerFactor_III:=Real_0;
mind_bool[172]:=Klima[2].VentilHlajenjeOdpiranje; | mind[172]:=ErrorComKlima[6].Code[1]; |  |  | Read_Real(rVar:=Circutor.PowerFactor_L1,lo:=4344,hi:=4345); |  | 172:Klima[2].VentilHlajenjeOdpiranje:=Bit_0; | 172:ErrorComKlima[6].Code[1]:=Byte_0; |  |  | 4345:Circutor.PowerFactor_L1:=Real_0;
mind_bool[173]:=Klima[2].VentilHlajenjeZapiranje; | mind[173]:=ErrorComKlima[6].Code[2]; |  |  | Read_Real(rVar:=Circutor.PowerFactor_L2,lo:=4346,hi:=4347); |  | 173:Klima[2].VentilHlajenjeZapiranje:=Bit_0; | 173:ErrorComKlima[6].Code[2]:=Byte_0; |  |  | 4347:Circutor.PowerFactor_L2:=Real_0;
mind_bool[174]:=Klima[2].VisokaTempPovratneVode; | mind[174]:=ErrorComKlima[6].Code[3]; |  |  | Read_Real(rVar:=Circutor.PowerFactor_L3,lo:=4348,hi:=4349); |  | 174:Klima[2].VisokaTempPovratneVode:=Bit_0; | 174:ErrorComKlima[6].Code[3]:=Byte_0; |  |  | 4349:Circutor.PowerFactor_L3:=Real_0;
mind_bool[175]:=Klima[2].VisokaTempVProstoru; | mind[175]:=ErrorComKlima[6].Code[4]; |  |  | Read_Real(rVar:=Circutor.THDI_L1,lo:=4350,hi:=4351); |  | 175:Klima[2].VisokaTempVProstoru:=Bit_0; | 175:ErrorComKlima[6].Code[4]:=Byte_0; |  |  | 4351:Circutor.THDI_L1:=Real_0;
mind_bool[176]:=Klima[2].VisokaVlaznost; | mind[176]:=ErrorComKlima[6].Code[5]; |  |  | Read_Real(rVar:=Circutor.THDI_L2,lo:=4352,hi:=4353); |  | 176:Klima[2].VisokaVlaznost:=Bit_0; | 176:ErrorComKlima[6].Code[5]:=Byte_0; |  |  | 4353:Circutor.THDI_L2:=Real_0;
mind_bool[177]:=Klima[2].VisokTokVVlazilcu; | mind[177]:=ErrorComKlima[6].Code[6]; |  |  | Read_Real(rVar:=Circutor.THDI_L3,lo:=4354,hi:=4355); |  | 177:Klima[2].VisokTokVVlazilcu:=Bit_0; | 177:ErrorComKlima[6].Code[6]:=Byte_0; |  |  | 4355:Circutor.THDI_L3:=Real_0;
mind_bool[178]:=Klima[2].Vlazenje; | mind[178]:=ErrorComKlima[6].Code[7]; |  |  | Read_Real(rVar:=Circutor.THDV_L1,lo:=4356,hi:=4357); |  | 178:Klima[2].Vlazenje:=Bit_0; | 178:ErrorComKlima[6].Code[7]:=Byte_0; |  |  | 4357:Circutor.THDV_L1:=Real_0;
mind_bool[179]:=Klima[2].ZamasenFilter; | mind[179]:=ErrorComKlima[6].Code[8]; |  |  | Read_Real(rVar:=Circutor.THDV_L2,lo:=4358,hi:=4359); |  | 179:Klima[2].ZamasenFilter:=Bit_0; | 179:ErrorComKlima[6].Code[8]:=Byte_0; |  |  | 4359:Circutor.THDV_L2:=Real_0;
mind_bool[180]:=Klima[3].AlarmKompresor1; | mind[180]:=ErrorComKlima[6].Code[9]; |  |  | Read_Real(rVar:=Circutor.THDV_L3,lo:=4360,hi:=4361); |  | 180:Klima[3].AlarmKompresor1:=Bit_0; | 180:ErrorComKlima[6].Code[9]:=Byte_0; |  |  | 4361:Circutor.THDV_L3:=Real_0;
mind_bool[181]:=Klima[3].AlarmKompresor2; | mind[181]:=ErrorComKlima[6].Status; |  |  | Read_Real(rVar:=Circutor.Tok_L1,lo:=4362,hi:=4363); |  | 181:Klima[3].AlarmKompresor2:=Bit_0; | 181:ErrorComKlima[6].Status:=Word_01; |  |  | 4363:Circutor.Tok_L1:=Real_0;
mind_bool[182]:=Klima[3].Deluje; | mind[182]:=Klima[1].GrelecStatus; |  |  | Read_Real(rVar:=Circutor.Tok_L2,lo:=4364,hi:=4365); |  | 182:Klima[3].Deluje:=Bit_0; | 182:Klima[1].GrelecStatus:=Byte_0; |  |  | 4365:Circutor.Tok_L2:=Real_0;
mind_bool[183]:=Klima[3].EnergySaving; | mind[183]:=Klima[1].IzhodniVentStatus; |  |  | Read_Real(rVar:=Circutor.Tok_L3,lo:=4366,hi:=4367); |  | 183:Klima[3].EnergySaving:=Bit_0; | 183:Klima[1].IzhodniVentStatus:=Byte_0; |  |  | 4367:Circutor.Tok_L3:=Real_0;
mind_bool[184]:=Klima[3].FaultyEPROM; | mind[184]:=Klima[1].KompresorStatus; |  |  | Read_Real(rVar:=Circutor.TokPovprecje_III,lo:=4368,hi:=4369); |  | 184:Klima[3].FaultyEPROM:=Bit_0; | 184:Klima[1].KompresorStatus:=Byte_0; |  |  | 4369:Circutor.TokPovprecje_III:=Real_0;
mind_bool[185]:=Klima[3].FenThermalCutout; | mind[185]:=Klima[1].VlazilecStatus; |  |  | Read_Real(rVar:=Klima[1].NastMaxTemp,lo:=4370,hi:=4371); |  | 185:Klima[3].FenThermalCutout:=Bit_0; | 185:Klima[1].VlazilecStatus:=Byte_0; |  |  | 4371:Klima[1].NastMaxTemp:=Real_0;
mind_bool[186]:=Klima[3].GeneralAlarm; | mind[186]:=Klima[2].GrelecStatus; |  |  | Read_Real(rVar:=Klima[1].NastMaxVlaznost,lo:=4372,hi:=4373); |  | 186:Klima[3].GeneralAlarm:=Bit_0; | 186:Klima[2].GrelecStatus:=Byte_0; |  |  | 4373:Klima[1].NastMaxVlaznost:=Real_0;
mind_bool[187]:=Klima[3].Kompresor1naMejiObrUr; | mind[187]:=Klima[2].IzhodniVentStatus; |  |  | Read_Real(rVar:=Klima[1].NastMinTemp,lo:=4374,hi:=4375); |  | 187:Klima[3].Kompresor1naMejiObrUr:=Bit_0; | 187:Klima[2].IzhodniVentStatus:=Byte_0; |  |  | 4375:Klima[1].NastMinTemp:=Real_0;
mind_bool[188]:=Klima[3].Kompresor2naMejiObrUr; | mind[188]:=Klima[2].KompresorStatus; |  |  | Read_Real(rVar:=Klima[1].NastMinVlaznost,lo:=4376,hi:=4377); |  | 188:Klima[3].Kompresor2naMejiObrUr:=Bit_0; | 188:Klima[2].KompresorStatus:=Byte_0; |  |  | 4377:Klima[1].NastMinVlaznost:=Real_0;
mind_bool[189]:=Klima[3].Napaka; | mind[189]:=Klima[2].VlazilecStatus; |  |  | Read_Real(rVar:=Klima[1].NastTempProstora,lo:=4378,hi:=4379); |  | 189:Klima[3].Napaka:=Bit_0; | 189:Klima[2].VlazilecStatus:=Byte_0; |  |  | 4379:Klima[1].NastTempProstora:=Real_0;
mind_bool[190]:=Klima[3].NapakaPriPretokuZraka; | mind[190]:=Klima[3].GrelecStatus; |  |  | Read_Real(rVar:=Klima[1].NastVlaznost,lo:=4380,hi:=4381); |  | 190:Klima[3].NapakaPriPretokuZraka:=Bit_0; | 190:Klima[3].GrelecStatus:=Byte_0; |  |  | 4381:Klima[1].NastVlaznost:=Real_0;
mind_bool[191]:=Klima[3].NapakaSenzorPovratVode; | mind[191]:=Klima[3].IzhodniVentStatus; |  |  | Read_Real(rVar:=Klima[1].ObratovalneUre,lo:=4382,hi:=4383); |  | 191:Klima[3].NapakaSenzorPovratVode:=Bit_0; | 191:Klima[3].IzhodniVentStatus:=Byte_0; |  |  | 4383:Klima[1].ObratovalneUre:=Real_0;
mind_bool[192]:=Klima[3].NapakaSenzorTempIzpiha; | mind[192]:=Klima[3].KompresorStatus; |  |  | Read_Real(rVar:=Klima[1].TemperaturaProstora,lo:=4384,hi:=4385); |  | 192:Klima[3].NapakaSenzorTempIzpiha:=Bit_0; | 192:Klima[3].KompresorStatus:=Byte_0; |  |  | 4385:Klima[1].TemperaturaProstora:=Real_0;
mind_bool[193]:=Klima[3].NapakaSenzorTempProstora; | mind[193]:=Klima[3].VlazilecStatus; |  |  | Read_Real(rVar:=Klima[1].TempIzpihanegaZraka,lo:=4386,hi:=4387); |  | 193:Klima[3].NapakaSenzorTempProstora:=Bit_0; | 193:Klima[3].VlazilecStatus:=Byte_0; |  |  | 4387:Klima[1].TempIzpihanegaZraka:=Real_0;
mind_bool[194]:=Klima[3].NapakaSenzorVlaznosti; | mind[194]:=KlimaGal.GrelecStatus; |  |  | Read_Real(rVar:=Klima[1].TempPovratneVode,lo:=4388,hi:=4389); |  | 194:Klima[3].NapakaSenzorVlaznosti:=Bit_0; | 194:KlimaGal.GrelecStatus:=Byte_0; |  |  | 4389:Klima[1].TempPovratneVode:=Real_0;
mind_bool[195]:=Klima[3].NapakaSenzorZunanjeTemp; | mind[195]:=KlimaGal.IzhodniVentStatus; |  |  | Read_Real(rVar:=Klima[1].VlaznostProstora,lo:=4390,hi:=4391); |  | 195:Klima[3].NapakaSenzorZunanjeTemp:=Bit_0; | 195:KlimaGal.IzhodniVentStatus:=Byte_0; |  |  | 4391:Klima[1].VlaznostProstora:=Real_0;
mind_bool[196]:=Klima[3].NiTokaVVlazilcu; | mind[196]:=KlimaGal.KompresorStatus; |  |  | Read_Real(rVar:=Klima[1].ZunanjaTemp,lo:=4392,hi:=4393); |  | 196:Klima[3].NiTokaVVlazilcu:=Bit_0; | 196:KlimaGal.KompresorStatus:=Byte_0; |  |  | 4393:Klima[1].ZunanjaTemp:=Real_0;
mind_bool[197]:=Klima[3].NiVodeVVlazilcu; | mind[197]:=KlimaGal.VlazilecStatus; |  |  | Read_Real(rVar:=Klima[2].NastMaxTemp,lo:=4394,hi:=4395); |  | 197:Klima[3].NiVodeVVlazilcu:=Bit_0; | 197:KlimaGal.VlazilecStatus:=Byte_0; |  |  | 4395:Klima[2].NastMaxTemp:=Real_0;
mind_bool[198]:=Klima[3].NizekPritiskKompresor1; | mind[198]:=Qstanje[10]; |  |  | Read_Real(rVar:=Klima[2].NastMaxVlaznost,lo:=4396,hi:=4397); |  | 198:Klima[3].NizekPritiskKompresor1:=Bit_0; | 198:Qstanje[10]:=Byte_0; |  |  | 4397:Klima[2].NastMaxVlaznost:=Real_0;
mind_bool[199]:=Klima[3].NizekPritiskKompresor2; | mind[199]:=Qstanje[1]; |  |  | Read_Real(rVar:=Klima[2].NastMinTemp,lo:=4398,hi:=4399); |  | 199:Klima[3].NizekPritiskKompresor2:=Bit_0; | 199:Qstanje[1]:=Byte_0; |  |  | 4399:Klima[2].NastMinTemp:=Real_0;
mind_bool[200]:=Klima[3].NizkaTempPovratneVode; | mind[200]:=Qstanje[2]; |  |  | Read_Real(rVar:=Klima[2].NastMinVlaznost,lo:=4400,hi:=4401); |  | 200:Klima[3].NizkaTempPovratneVode:=Bit_0; | 200:Qstanje[2]:=Byte_0; |  |  | 4401:Klima[2].NastMinVlaznost:=Real_0;
mind_bool[201]:=Klima[3].NizkaTempVProstoru; | mind[201]:=Qstanje[3]; |  |  | Read_Real(rVar:=Klima[2].NastTempProstora,lo:=4402,hi:=4403); |  | 201:Klima[3].NizkaTempVProstoru:=Bit_0; | 201:Qstanje[3]:=Byte_0; |  |  | 4403:Klima[2].NastTempProstora:=Real_0;
mind_bool[202]:=Klima[3].NizkaVlaznost; | mind[202]:=Qstanje[4]; |  |  | Read_Real(rVar:=Klima[2].NastVlaznost,lo:=4404,hi:=4405); |  | 202:Klima[3].NizkaVlaznost:=Bit_0; | 202:Qstanje[4]:=Byte_0; |  |  | 4405:Klima[2].NastVlaznost:=Real_0;
mind_bool[203]:=Klima[3].OnOffEnablingBySupervisor; | mind[203]:=Qstanje[5]; |  |  | Read_Real(rVar:=Klima[2].ObratovalneUre,lo:=4406,hi:=4407); |  | 203:Klima[3].OnOffEnablingBySupervisor:=Bit_0; | 203:Qstanje[5]:=Byte_0; |  |  | 4407:Klima[2].ObratovalneUre:=Real_0;
mind_bool[204]:=Klima[3].PozarniAlarm; | mind[204]:=Qstanje[6]; |  |  | Read_Real(rVar:=Klima[2].TemperaturaProstora,lo:=4408,hi:=4409); |  | 204:Klima[3].PozarniAlarm:=Bit_0; | 204:Qstanje[6]:=Byte_0; |  |  | 4409:Klima[2].TemperaturaProstora:=Real_0;
mind_bool[205]:=Klima[3].Razvlazevanje; | mind[205]:=Qstanje[7]; |  |  | Read_Real(rVar:=Klima[2].TempIzpihanegaZraka,lo:=4410,hi:=4411); |  | 205:Klima[3].Razvlazevanje:=Bit_0; | 205:Qstanje[7]:=Byte_0; |  |  | 4411:Klima[2].TempIzpihanegaZraka:=Real_0;
mind_bool[206]:=Klima[3].RemoteOFFtoOutput; | mind[206]:=Qstanje[8]; |  |  | Read_Real(rVar:=Klima[2].TempPovratneVode,lo:=4412,hi:=4413); |  | 206:Klima[3].RemoteOFFtoOutput:=Bit_0; | 206:Qstanje[8]:=Byte_0; |  |  | 4413:Klima[2].TempPovratneVode:=Real_0;
mind_bool[207]:=Klima[3].RemoteOnOff; | mind[207]:=Qstanje[9]; |  |  | Read_Real(rVar:=Klima[2].VlaznostProstora,lo:=4414,hi:=4415); |  | 207:Klima[3].RemoteOnOff:=Bit_0; | 207:Qstanje[9]:=Byte_0; |  |  | 4415:Klima[2].VlaznostProstora:=Real_0;
mind_bool[208]:=Klima[3].RocniIzklop; | mind[208]:=UserCurrentLevel; |  |  | Read_Real(rVar:=Klima[2].ZunanjaTemp,lo:=4416,hi:=4417); |  | 208:Klima[3].RocniIzklop:=Bit_0; | 208:UserCurrentLevel:=Byte_0; |  |  | 4417:Klima[2].ZunanjaTemp:=Real_0;
mind_bool[209]:=Klima[3].SenzorjiStatus; | mind[209]:=XVH_CircNumber; |  |  | Read_Real(rVar:=Klima[3].NastMaxTemp,lo:=4418,hi:=4419); |  | 209:Klima[3].SenzorjiStatus:=Bit_0; | 209:XVH_CircNumber:=Byte_0; |  |  | 4419:Klima[3].NastMaxTemp:=Real_0;
mind_bool[210]:=Klima[3].StoppedByAlarms; | mind[210]:=XVH_KlimaNumber; |  |  | Read_Real(rVar:=Klima[3].NastMaxVlaznost,lo:=4420,hi:=4421); |  | 210:Klima[3].StoppedByAlarms:=Bit_0; | 210:XVH_KlimaNumber:=Byte_0; |  |  | 4421:Klima[3].NastMaxVlaznost:=Real_0;
mind_bool[211]:=Klima[3].ThermalCutoutHeater1; | mind[211]:=XVH_PripravaVodeStat[1]; |  |  | Read_Real(rVar:=Klima[3].NastMinTemp,lo:=4422,hi:=4423); |  | 211:Klima[3].ThermalCutoutHeater1:=Bit_0; | 211:XVH_PripravaVodeStat[1]:=Byte_0; |  |  | 4423:Klima[3].NastMinTemp:=Real_0;
mind_bool[212]:=Klima[3].ThermalCutoutHeater2; | mind[212]:=XVH_PripravaVodeStat[2]; |  |  | Read_Real(rVar:=Klima[3].NastMinVlaznost,lo:=4424,hi:=4425); |  | 212:Klima[3].ThermalCutoutHeater2:=Bit_0; | 212:XVH_PripravaVodeStat[2]:=Byte_0; |  |  | 4425:Klima[3].NastMinVlaznost:=Real_0;
mind_bool[213]:=Klima[3].UnitOnOff; | mind[213]:=XVH_UPSstatus; |  |  | Read_Real(rVar:=Klima[3].NastTempProstora,lo:=4426,hi:=4427); |  | 213:Klima[3].UnitOnOff:=Bit_0; | 213:XVH_UPSstatus:=Byte_0; |  |  | 4427:Klima[3].NastTempProstora:=Real_0;
mind_bool[214]:=Klima[3].VentilatorNaMejiObrUr; | mind[214]:=XVH_VlazilecStatus[1]; |  |  | Read_Real(rVar:=Klima[3].NastVlaznost,lo:=4428,hi:=4429); |  | 214:Klima[3].VentilatorNaMejiObrUr:=Bit_0; | 214:XVH_VlazilecStatus[1]:=Byte_0; |  |  | 4429:Klima[3].NastVlaznost:=Real_0;
mind_bool[215]:=Klima[3].VentilGretjeOdpiranje; | mind[215]:=XVH_VlazilecStatus[2]; |  |  | Read_Real(rVar:=Klima[3].ObratovalneUre,lo:=4430,hi:=4431); |  | 215:Klima[3].VentilGretjeOdpiranje:=Bit_0; | 215:XVH_VlazilecStatus[2]:=Byte_0; |  |  | 4431:Klima[3].ObratovalneUre:=Real_0;
mind_bool[216]:=Klima[3].VentilGretjeZapiranje; | mind[216]:=XVH_VlazilecStatus[3]; |  |  | Read_Real(rVar:=Klima[3].TemperaturaProstora,lo:=4432,hi:=4433); |  | 216:Klima[3].VentilGretjeZapiranje:=Bit_0; | 216:XVH_VlazilecStatus[3]:=Byte_0; |  |  | 4433:Klima[3].TemperaturaProstora:=Real_0;
mind_bool[217]:=Klima[3].VentilHlajenjeOdpiranje; | mind[217]:=XVHnum[10]; |  |  | Read_Real(rVar:=Klima[3].TempIzpihanegaZraka,lo:=4434,hi:=4435); |  | 217:Klima[3].VentilHlajenjeOdpiranje:=Bit_0; | 217:XVHnum[10]:=Byte_0; |  |  | 4435:Klima[3].TempIzpihanegaZraka:=Real_0;
mind_bool[218]:=Klima[3].VentilHlajenjeZapiranje; | mind[218]:=XVHnum[11]; |  |  | Read_Real(rVar:=Klima[3].TempPovratneVode,lo:=4436,hi:=4437); |  | 218:Klima[3].VentilHlajenjeZapiranje:=Bit_0; | 218:XVHnum[11]:=Byte_0; |  |  | 4437:Klima[3].TempPovratneVode:=Real_0;
mind_bool[219]:=Klima[3].VisokaTempPovratneVode; | mind[219]:=XVHnum[12]; |  |  | Read_Real(rVar:=Klima[3].VlaznostProstora,lo:=4438,hi:=4439); |  | 219:Klima[3].VisokaTempPovratneVode:=Bit_0; | 219:XVHnum[12]:=Byte_0; |  |  | 4439:Klima[3].VlaznostProstora:=Real_0;
mind_bool[220]:=Klima[3].VisokaTempVProstoru; | mind[220]:=XVHnum[13]; |  |  | Read_Real(rVar:=Klima[3].ZunanjaTemp,lo:=4440,hi:=4441); |  | 220:Klima[3].VisokaTempVProstoru:=Bit_0; | 220:XVHnum[13]:=Byte_0; |  |  | 4441:Klima[3].ZunanjaTemp:=Real_0;
mind_bool[221]:=Klima[3].VisokaVlaznost; | mind[221]:=XVHnum[14]; |  |  | Read_Real(rVar:=KlimaGal.NastMaxTemp,lo:=4442,hi:=4443); |  | 221:Klima[3].VisokaVlaznost:=Bit_0; | 221:XVHnum[14]:=Byte_0; |  |  | 4443:KlimaGal.NastMaxTemp:=Real_0;
mind_bool[222]:=Klima[3].VisokTokVVlazilcu; | mind[222]:=XVHnum[1]; |  |  | Read_Real(rVar:=KlimaGal.NastMaxVlaznost,lo:=4444,hi:=4445); |  | 222:Klima[3].VisokTokVVlazilcu:=Bit_0; | 222:XVHnum[1]:=Byte_0; |  |  | 4445:KlimaGal.NastMaxVlaznost:=Real_0;
mind_bool[223]:=Klima[3].Vlazenje; | mind[223]:=XVHnum[2]; |  |  | Read_Real(rVar:=KlimaGal.NastMinTemp,lo:=4446,hi:=4447); |  | 223:Klima[3].Vlazenje:=Bit_0; | 223:XVHnum[2]:=Byte_0; |  |  | 4447:KlimaGal.NastMinTemp:=Real_0;
mind_bool[224]:=Klima[3].ZamasenFilter; | mind[224]:=XVHnum[3]; |  |  | Read_Real(rVar:=KlimaGal.NastMinVlaznost,lo:=4448,hi:=4449); |  | 224:Klima[3].ZamasenFilter:=Bit_0; | 224:XVHnum[3]:=Byte_0; |  |  | 4449:KlimaGal.NastMinVlaznost:=Real_0;
mind_bool[225]:=KlimaAErrors[10]; | mind[225]:=XVHnum[4]; |  |  | Read_Real(rVar:=KlimaGal.NastTempProstora,lo:=4450,hi:=4451); |  | 225:KlimaAErrors[10]:=Bit_0; | 225:XVHnum[4]:=Byte_0; |  |  | 4451:KlimaGal.NastTempProstora:=Real_0;
mind_bool[226]:=KlimaAErrors[11]; | mind[226]:=XVHnum[5]; |  |  | Read_Real(rVar:=KlimaGal.NastVlaznost,lo:=4452,hi:=4453); |  | 226:KlimaAErrors[11]:=Bit_0; | 226:XVHnum[5]:=Byte_0; |  |  | 4453:KlimaGal.NastVlaznost:=Real_0;
mind_bool[227]:=KlimaAErrors[12]; | mind[227]:=XVHnum[6]; |  |  | Read_Real(rVar:=KlimaGal.ObratovalneUre,lo:=4454,hi:=4455); |  | 227:KlimaAErrors[12]:=Bit_0; | 227:XVHnum[6]:=Byte_0; |  |  | 4455:KlimaGal.ObratovalneUre:=Real_0;
mind_bool[228]:=KlimaAErrors[13]; | mind[228]:=XVHnum[7]; |  |  | Read_Real(rVar:=KlimaGal.TemperaturaProstora,lo:=4456,hi:=4457); |  | 228:KlimaAErrors[13]:=Bit_0; | 228:XVHnum[7]:=Byte_0; |  |  | 4457:KlimaGal.TemperaturaProstora:=Real_0;
mind_bool[229]:=KlimaAErrors[14]; | mind[229]:=XVHnum[8]; |  |  | Read_Real(rVar:=KlimaGal.TempIzpihanegaZraka,lo:=4458,hi:=4459); |  | 229:KlimaAErrors[14]:=Bit_0; | 229:XVHnum[8]:=Byte_0; |  |  | 4459:KlimaGal.TempIzpihanegaZraka:=Real_0;
mind_bool[230]:=KlimaAErrors[15]; | mind[230]:=XVHnum[9]; |  |  | Read_Real(rVar:=KlimaGal.TempPovratneVode,lo:=4460,hi:=4461); |  | 230:KlimaAErrors[15]:=Bit_0; | 230:XVHnum[9]:=Byte_0; |  |  | 4461:KlimaGal.TempPovratneVode:=Real_0;
mind_bool[231]:=KlimaAErrors[16]; | mind[231]:=kom_nast_cas_izpada; |  |  | Read_Real(rVar:=KlimaGal.VlaznostProstora,lo:=4462,hi:=4463); |  | 231:KlimaAErrors[16]:=Bit_0; | 231:kom_nast_cas_izpada:=Word_01; |  |  | 4463:KlimaGal.VlaznostProstora:=Real_0;
mind_bool[232]:=KlimaAErrors[17]; |  |  |  | Read_Real(rVar:=KlimaGal.ZunanjaTemp,lo:=4464,hi:=4465); |  | 232:KlimaAErrors[17]:=Bit_0; |  |  |  | 4465:KlimaGal.ZunanjaTemp:=Real_0;
mind_bool[233]:=KlimaAErrors[18]; |  |  |  | Read_Real(rVar:=SenzorTemp[10],lo:=4466,hi:=4467); |  | 233:KlimaAErrors[18]:=Bit_0; |  |  |  | 4467:SenzorTemp[10]:=Real_0;
mind_bool[234]:=KlimaAErrors[19]; |  |  |  | Read_Real(rVar:=SenzorTemp[11],lo:=4468,hi:=4469); |  | 234:KlimaAErrors[19]:=Bit_0; |  |  |  | 4469:SenzorTemp[11]:=Real_0;
mind_bool[235]:=KlimaAErrors[1]; |  |  |  | Read_Real(rVar:=SenzorTemp[12],lo:=4470,hi:=4471); |  | 235:KlimaAErrors[1]:=Bit_0; |  |  |  | 4471:SenzorTemp[12]:=Real_0;
mind_bool[236]:=KlimaAErrors[20]; |  |  |  | Read_Real(rVar:=SenzorTemp[13],lo:=4472,hi:=4473); |  | 236:KlimaAErrors[20]:=Bit_0; |  |  |  | 4473:SenzorTemp[13]:=Real_0;
mind_bool[237]:=KlimaAErrors[21]; |  |  |  | Read_Real(rVar:=SenzorTemp[14],lo:=4474,hi:=4475); |  | 237:KlimaAErrors[21]:=Bit_0; |  |  |  | 4475:SenzorTemp[14]:=Real_0;
mind_bool[238]:=KlimaAErrors[22]; |  |  |  | Read_Real(rVar:=SenzorTemp[15],lo:=4476,hi:=4477); |  | 238:KlimaAErrors[22]:=Bit_0; |  |  |  | 4477:SenzorTemp[15]:=Real_0;
mind_bool[239]:=KlimaAErrors[23]; |  |  |  | Read_Real(rVar:=SenzorTemp[16],lo:=4478,hi:=4479); |  | 239:KlimaAErrors[23]:=Bit_0; |  |  |  | 4479:SenzorTemp[16]:=Real_0;
mind_bool[240]:=KlimaAErrors[24]; |  |  |  | Read_Real(rVar:=SenzorTemp[17],lo:=4480,hi:=4481); |  | 240:KlimaAErrors[24]:=Bit_0; |  |  |  | 4481:SenzorTemp[17]:=Real_0;
mind_bool[241]:=KlimaAErrors[25]; |  |  |  | Read_Real(rVar:=SenzorTemp[18],lo:=4482,hi:=4483); |  | 241:KlimaAErrors[25]:=Bit_0; |  |  |  | 4483:SenzorTemp[18]:=Real_0;
mind_bool[242]:=KlimaAErrors[26]; |  |  |  | Read_Real(rVar:=SenzorTemp[19],lo:=4484,hi:=4485); |  | 242:KlimaAErrors[26]:=Bit_0; |  |  |  | 4485:SenzorTemp[19]:=Real_0;
mind_bool[243]:=KlimaAErrors[27]; |  |  |  | Read_Real(rVar:=SenzorTemp[1],lo:=4486,hi:=4487); |  | 243:KlimaAErrors[27]:=Bit_0; |  |  |  | 4487:SenzorTemp[1]:=Real_0;
mind_bool[244]:=KlimaAErrors[28]; |  |  |  | Read_Real(rVar:=SenzorTemp[2],lo:=4488,hi:=4489); |  | 244:KlimaAErrors[28]:=Bit_0; |  |  |  | 4489:SenzorTemp[2]:=Real_0;
mind_bool[245]:=KlimaAErrors[29]; |  |  |  | Read_Real(rVar:=SenzorTemp[3],lo:=4490,hi:=4491); |  | 245:KlimaAErrors[29]:=Bit_0; |  |  |  | 4491:SenzorTemp[3]:=Real_0;
mind_bool[246]:=KlimaAErrors[2]; |  |  |  | Read_Real(rVar:=SenzorTemp[4],lo:=4492,hi:=4493); |  | 246:KlimaAErrors[2]:=Bit_0; |  |  |  | 4493:SenzorTemp[4]:=Real_0;
mind_bool[247]:=KlimaAErrors[30]; |  |  |  | Read_Real(rVar:=SenzorTemp[5],lo:=4494,hi:=4495); |  | 247:KlimaAErrors[30]:=Bit_0; |  |  |  | 4495:SenzorTemp[5]:=Real_0;
mind_bool[248]:=KlimaAErrors[31]; |  |  |  | Read_Real(rVar:=SenzorTemp[6],lo:=4496,hi:=4497); |  | 248:KlimaAErrors[31]:=Bit_0; |  |  |  | 4497:SenzorTemp[6]:=Real_0;
mind_bool[249]:=KlimaAErrors[32]; |  |  |  | Read_Real(rVar:=SenzorTemp[7],lo:=4498,hi:=4499); |  | 249:KlimaAErrors[32]:=Bit_0; |  |  |  | 4499:SenzorTemp[7]:=Real_0;
mind_bool[250]:=KlimaAErrors[33]; |  |  |  | Read_Real(rVar:=SenzorTemp[8],lo:=4500,hi:=4501); |  | 250:KlimaAErrors[33]:=Bit_0; |  |  |  | 4501:SenzorTemp[8]:=Real_0;
mind_bool[251]:=KlimaAErrors[34]; |  |  |  | Read_Real(rVar:=SenzorTemp[9],lo:=4502,hi:=4503); |  | 251:KlimaAErrors[34]:=Bit_0; |  |  |  | 4503:SenzorTemp[9]:=Real_0;
mind_bool[252]:=KlimaAErrors[35]; |  |  |  | Read_Real(rVar:=SenzorVlaga[10],lo:=4504,hi:=4505); |  | 252:KlimaAErrors[35]:=Bit_0; |  |  |  | 4505:SenzorVlaga[10]:=Real_0;
mind_bool[253]:=KlimaAErrors[36]; |  |  |  | Read_Real(rVar:=SenzorVlaga[11],lo:=4506,hi:=4507); |  | 253:KlimaAErrors[36]:=Bit_0; |  |  |  | 4507:SenzorVlaga[11]:=Real_0;
mind_bool[254]:=KlimaAErrors[37]; |  |  |  | Read_Real(rVar:=SenzorVlaga[12],lo:=4508,hi:=4509); |  | 254:KlimaAErrors[37]:=Bit_0; |  |  |  | 4509:SenzorVlaga[12]:=Real_0;
mind_bool[255]:=KlimaAErrors[38]; |  |  |  | Read_Real(rVar:=SenzorVlaga[13],lo:=4510,hi:=4511); |  | 255:KlimaAErrors[38]:=Bit_0; |  |  |  | 4511:SenzorVlaga[13]:=Real_0;
mind_bool[256]:=KlimaAErrors[39]; |  |  |  | Read_Real(rVar:=SenzorVlaga[14],lo:=4512,hi:=4513); |  | 256:KlimaAErrors[39]:=Bit_0; |  |  |  | 4513:SenzorVlaga[14]:=Real_0;
mind_bool[257]:=KlimaAErrors[3]; |  |  |  | Read_Real(rVar:=SenzorVlaga[15],lo:=4514,hi:=4515); |  | 257:KlimaAErrors[3]:=Bit_0; |  |  |  | 4515:SenzorVlaga[15]:=Real_0;
mind_bool[258]:=KlimaAErrors[40]; |  |  |  | Read_Real(rVar:=SenzorVlaga[16],lo:=4516,hi:=4517); |  | 258:KlimaAErrors[40]:=Bit_0; |  |  |  | 4517:SenzorVlaga[16]:=Real_0;
mind_bool[259]:=KlimaAErrors[4]; |  |  |  | Read_Real(rVar:=SenzorVlaga[17],lo:=4518,hi:=4519); |  | 259:KlimaAErrors[4]:=Bit_0; |  |  |  | 4519:SenzorVlaga[17]:=Real_0;
mind_bool[260]:=KlimaAErrors[5]; |  |  |  | Read_Real(rVar:=SenzorVlaga[18],lo:=4520,hi:=4521); |  | 260:KlimaAErrors[5]:=Bit_0; |  |  |  | 4521:SenzorVlaga[18]:=Real_0;
mind_bool[261]:=KlimaAErrors[6]; |  |  |  | Read_Real(rVar:=SenzorVlaga[19],lo:=4522,hi:=4523); |  | 261:KlimaAErrors[6]:=Bit_0; |  |  |  | 4523:SenzorVlaga[19]:=Real_0;
mind_bool[262]:=KlimaAErrors[7]; |  |  |  | Read_Real(rVar:=SenzorVlaga[1],lo:=4524,hi:=4525); |  | 262:KlimaAErrors[7]:=Bit_0; |  |  |  | 4525:SenzorVlaga[1]:=Real_0;
mind_bool[263]:=KlimaAErrors[8]; |  |  |  | Read_Real(rVar:=SenzorVlaga[2],lo:=4526,hi:=4527); |  | 263:KlimaAErrors[8]:=Bit_0; |  |  |  | 4527:SenzorVlaga[2]:=Real_0;
mind_bool[264]:=KlimaAErrors[9]; |  |  |  | Read_Real(rVar:=SenzorVlaga[3],lo:=4528,hi:=4529); |  | 264:KlimaAErrors[9]:=Bit_0; |  |  |  | 4529:SenzorVlaga[3]:=Real_0;
mind_bool[265]:=KlimaBErrors[10]; |  |  |  | Read_Real(rVar:=SenzorVlaga[4],lo:=4530,hi:=4531); |  | 265:KlimaBErrors[10]:=Bit_0; |  |  |  | 4531:SenzorVlaga[4]:=Real_0;
mind_bool[266]:=KlimaBErrors[11]; |  |  |  | Read_Real(rVar:=SenzorVlaga[5],lo:=4532,hi:=4533); |  | 266:KlimaBErrors[11]:=Bit_0; |  |  |  | 4533:SenzorVlaga[5]:=Real_0;
mind_bool[267]:=KlimaBErrors[12]; |  |  |  | Read_Real(rVar:=SenzorVlaga[6],lo:=4534,hi:=4535); |  | 267:KlimaBErrors[12]:=Bit_0; |  |  |  | 4535:SenzorVlaga[6]:=Real_0;
mind_bool[268]:=KlimaBErrors[13]; |  |  |  | Read_Real(rVar:=SenzorVlaga[7],lo:=4536,hi:=4537); |  | 268:KlimaBErrors[13]:=Bit_0; |  |  |  | 4537:SenzorVlaga[7]:=Real_0;
mind_bool[269]:=KlimaBErrors[14]; |  |  |  | Read_Real(rVar:=SenzorVlaga[8],lo:=4538,hi:=4539); |  | 269:KlimaBErrors[14]:=Bit_0; |  |  |  | 4539:SenzorVlaga[8]:=Real_0;
mind_bool[270]:=KlimaBErrors[15]; |  |  |  | Read_Real(rVar:=SenzorVlaga[9],lo:=4540,hi:=4541); |  | 270:KlimaBErrors[15]:=Bit_0; |  |  |  | 4541:SenzorVlaga[9]:=Real_0;
mind_bool[271]:=KlimaBErrors[16]; |  |  |  | Read_Real(rVar:=TempAlarmPoint[1],lo:=4542,hi:=4543); |  | 271:KlimaBErrors[16]:=Bit_0; |  |  |  | 4543:TempAlarmPoint[1]:=Real_0;
mind_bool[272]:=KlimaBErrors[17]; |  |  |  | Read_Real(rVar:=TempAlarmPoint[2],lo:=4544,hi:=4545); |  | 272:KlimaBErrors[17]:=Bit_0; |  |  |  | 4545:TempAlarmPoint[2]:=Real_0;
mind_bool[273]:=KlimaBErrors[18]; |  |  |  | Read_Real(rVar:=TempAlarmPoint[3],lo:=4546,hi:=4547); |  | 273:KlimaBErrors[18]:=Bit_0; |  |  |  | 4547:TempAlarmPoint[3]:=Real_0;
mind_bool[274]:=KlimaBErrors[19]; |  |  |  | Read_Real(rVar:=TempMaxPoint[1],lo:=4548,hi:=4549); |  | 274:KlimaBErrors[19]:=Bit_0; |  |  |  | 4549:TempMaxPoint[1]:=Real_0;
mind_bool[275]:=KlimaBErrors[1]; |  |  |  | Read_Real(rVar:=TempMaxPoint[2],lo:=4550,hi:=4551); |  | 275:KlimaBErrors[1]:=Bit_0; |  |  |  | 4551:TempMaxPoint[2]:=Real_0;
mind_bool[276]:=KlimaBErrors[20]; |  |  |  | Read_Real(rVar:=TempMaxPoint[3],lo:=4552,hi:=4553); |  | 276:KlimaBErrors[20]:=Bit_0; |  |  |  | 4553:TempMaxPoint[3]:=Real_0;
mind_bool[277]:=KlimaBErrors[21]; |  |  |  | Read_Real(rVar:=TempPovp[1],lo:=4554,hi:=4555); |  | 277:KlimaBErrors[21]:=Bit_0; |  |  |  | 4555:TempPovp[1]:=Real_0;
mind_bool[278]:=KlimaBErrors[22]; |  |  |  | Read_Real(rVar:=TempPovp[2],lo:=4556,hi:=4557); |  | 278:KlimaBErrors[22]:=Bit_0; |  |  |  | 4557:TempPovp[2]:=Real_0;
mind_bool[279]:=KlimaBErrors[23]; |  |  |  | Read_Real(rVar:=TempPovp[3],lo:=4558,hi:=4559); |  | 279:KlimaBErrors[23]:=Bit_0; |  |  |  | 4559:TempPovp[3]:=Real_0;
mind_bool[280]:=KlimaBErrors[24]; |  |  |  | Read_Real(rVar:=TempPovp[4],lo:=4560,hi:=4561); |  | 280:KlimaBErrors[24]:=Bit_0; |  |  |  | 4561:TempPovp[4]:=Real_0;
mind_bool[281]:=KlimaBErrors[25]; |  |  |  | Read_Real(rVar:=TempPovp[5],lo:=4562,hi:=4563); |  | 281:KlimaBErrors[25]:=Bit_0; |  |  |  | 4563:TempPovp[5]:=Real_0;
mind_bool[282]:=KlimaBErrors[26]; |  |  |  | Read_Real(rVar:=TempSetPoint[1],lo:=4564,hi:=4565); |  | 282:KlimaBErrors[26]:=Bit_0; |  |  |  | 4565:TempSetPoint[1]:=Real_0;
mind_bool[283]:=KlimaBErrors[27]; |  |  |  | Read_Real(rVar:=TempSetPoint[2],lo:=4566,hi:=4567); |  | 283:KlimaBErrors[27]:=Bit_0; |  |  |  | 4567:TempSetPoint[2]:=Real_0;
mind_bool[284]:=KlimaBErrors[28]; |  |  |  | Read_Real(rVar:=TempSetPoint[3],lo:=4568,hi:=4569); |  | 284:KlimaBErrors[28]:=Bit_0; |  |  |  | 4569:TempSetPoint[3]:=Real_0;
mind_bool[285]:=KlimaBErrors[29]; |  |  |  | Read_Real(rVar:=VlagaPovp[1],lo:=4570,hi:=4571); |  | 285:KlimaBErrors[29]:=Bit_0; |  |  |  | 4571:VlagaPovp[1]:=Real_0;
mind_bool[286]:=KlimaBErrors[2]; |  |  |  | Read_Real(rVar:=VlagaPovp[2],lo:=4572,hi:=4573); |  | 286:KlimaBErrors[2]:=Bit_0; |  |  |  | 4573:VlagaPovp[2]:=Real_0;
mind_bool[287]:=KlimaBErrors[30]; |  |  |  | Read_Real(rVar:=VlagaPovp[3],lo:=4574,hi:=4575); |  | 287:KlimaBErrors[30]:=Bit_0; |  |  |  | 4575:VlagaPovp[3]:=Real_0;
mind_bool[288]:=KlimaBErrors[31]; |  |  |  | Read_Real(rVar:=VlagaPovp[4],lo:=4576,hi:=4577); |  | 288:KlimaBErrors[31]:=Bit_0; |  |  |  | 4577:VlagaPovp[4]:=Real_0;
mind_bool[289]:=KlimaBErrors[32]; |  |  |  | Read_Real(rVar:=VlagaPovp[5],lo:=4578,hi:=4579); |  | 289:KlimaBErrors[32]:=Bit_0; |  |  |  | 4579:VlagaPovp[5]:=Real_0;
mind_bool[290]:=KlimaBErrors[33]; |  |  |  | Read_Real(rVar:=XVH_GrafTemp[1],lo:=4580,hi:=4581); |  | 290:KlimaBErrors[33]:=Bit_0; |  |  |  | 4581:XVH_GrafTemp[1]:=Real_0;
mind_bool[291]:=KlimaBErrors[34]; |  |  |  | Read_Real(rVar:=XVH_GrafTemp[2],lo:=4582,hi:=4583); |  | 291:KlimaBErrors[34]:=Bit_0; |  |  |  | 4583:XVH_GrafTemp[2]:=Real_0;
mind_bool[292]:=KlimaBErrors[35]; |  |  |  | Read_Real(rVar:=XVH_GrafTemp[3],lo:=4584,hi:=4585); |  | 292:KlimaBErrors[35]:=Bit_0; |  |  |  | 4585:XVH_GrafTemp[3]:=Real_0;
mind_bool[293]:=KlimaBErrors[36]; |  |  |  | Read_Real(rVar:=XVH_GrafTemp[4],lo:=4586,hi:=4587); |  | 293:KlimaBErrors[36]:=Bit_0; |  |  |  | 4587:XVH_GrafTemp[4]:=Real_0;
mind_bool[294]:=KlimaBErrors[37]; |  |  |  | Read_Real(rVar:=XVH_GrafTemp[5],lo:=4588,hi:=4589); |  | 294:KlimaBErrors[37]:=Bit_0; |  |  |  | 4589:XVH_GrafTemp[5]:=Real_0;
mind_bool[295]:=KlimaBErrors[38]; |  |  |  | Read_Real(rVar:=XVH_GrafVlaga[1],lo:=4590,hi:=4591); |  | 295:KlimaBErrors[38]:=Bit_0; |  |  |  | 4591:XVH_GrafVlaga[1]:=Real_0;
mind_bool[296]:=KlimaBErrors[39]; |  |  |  | Read_Real(rVar:=XVH_GrafVlaga[2],lo:=4592,hi:=4593); |  | 296:KlimaBErrors[39]:=Bit_0; |  |  |  | 4593:XVH_GrafVlaga[2]:=Real_0;
mind_bool[297]:=KlimaBErrors[3]; |  |  |  | Read_Real(rVar:=XVH_GrafVlaga[3],lo:=4594,hi:=4595); |  | 297:KlimaBErrors[3]:=Bit_0; |  |  |  | 4595:XVH_GrafVlaga[3]:=Real_0;
mind_bool[298]:=KlimaBErrors[40]; |  |  |  | Read_Real(rVar:=XVH_GrafVlaga[4],lo:=4596,hi:=4597); |  | 298:KlimaBErrors[40]:=Bit_0; |  |  |  | 4597:XVH_GrafVlaga[4]:=Real_0;
mind_bool[299]:=KlimaBErrors[4]; |  |  |  | Read_Real(rVar:=XVH_GrafVlaga[5],lo:=4598,hi:=4599); |  | 299:KlimaBErrors[4]:=Bit_0; |  |  |  | 4599:XVH_GrafVlaga[5]:=Real_0;
mind_bool[300]:=KlimaBErrors[5]; |  |  |  | Read_Real(rVar:=XVH_NastTempProstora[1],lo:=4600,hi:=4601); |  | 300:KlimaBErrors[5]:=Bit_0; |  |  |  | 4601:XVH_NastTempProstora[1]:=Real_0;
mind_bool[301]:=KlimaBErrors[6]; |  |  |  | Read_Real(rVar:=XVH_NastTempProstora[2],lo:=4602,hi:=4603); |  | 301:KlimaBErrors[6]:=Bit_0; |  |  |  | 4603:XVH_NastTempProstora[2]:=Real_0;
mind_bool[302]:=KlimaBErrors[7]; |  |  |  | Read_Real(rVar:=XVH_NastTempProstora[3],lo:=4604,hi:=4605); |  | 302:KlimaBErrors[7]:=Bit_0; |  |  |  | 4605:XVH_NastTempProstora[3]:=Real_0;
mind_bool[303]:=KlimaBErrors[8]; |  |  |  | Read_Real(rVar:=XVH_ObratovalneUre[1],lo:=4606,hi:=4607); |  | 303:KlimaBErrors[8]:=Bit_0; |  |  |  | 4607:XVH_ObratovalneUre[1]:=Real_0;
mind_bool[304]:=KlimaBErrors[9]; |  |  |  | Read_Real(rVar:=XVH_ObratovalneUre[2],lo:=4608,hi:=4609); |  | 304:KlimaBErrors[9]:=Bit_0; |  |  |  | 4609:XVH_ObratovalneUre[2]:=Real_0;
mind_bool[305]:=KlimaCErrors[10]; |  |  |  | Read_Real(rVar:=XVH_ObratovalneUre[3],lo:=4610,hi:=4611); |  | 305:KlimaCErrors[10]:=Bit_0; |  |  |  | 4611:XVH_ObratovalneUre[3]:=Real_0;
mind_bool[306]:=KlimaCErrors[11]; |  |  |  | Read_Real(rVar:=XVHhighHum,lo:=4612,hi:=4613); |  | 306:KlimaCErrors[11]:=Bit_0; |  |  |  | 4613:XVHhighHum:=Real_0;
mind_bool[307]:=KlimaCErrors[12]; |  |  |  | Read_Real(rVar:=XVHhighTemp,lo:=4614,hi:=4615); |  | 307:KlimaCErrors[12]:=Bit_0; |  |  |  | 4615:XVHhighTemp:=Real_0;
mind_bool[308]:=KlimaCErrors[13]; |  |  |  | Read_Real(rVar:=XVHlowHum,lo:=4616,hi:=4617); |  | 308:KlimaCErrors[13]:=Bit_0; |  |  |  | 4617:XVHlowHum:=Real_0;
mind_bool[309]:=KlimaCErrors[14]; |  |  |  | Read_Real(rVar:=XVHlowTemp,lo:=4618,hi:=4619); |  | 309:KlimaCErrors[14]:=Bit_0; |  |  |  | 4619:XVHlowTemp:=Real_0;
mind_bool[310]:=KlimaCErrors[15]; |  |  |  | Read_Real(rVar:=Circ[1].MaximumDemandA2,lo:=4620,hi:=4621); |  | 310:KlimaCErrors[15]:=Bit_0; |  |  |  | 4621:Circ[1].MaximumDemandA2:=Real_0;
mind_bool[311]:=KlimaCErrors[16]; |  |  |  | Read_Real(rVar:=Circ[1].MaximumDemandA3,lo:=4622,hi:=4623); |  | 311:KlimaCErrors[16]:=Bit_0; |  |  |  | 4623:Circ[1].MaximumDemandA3:=Real_0;
mind_bool[312]:=KlimaCErrors[17]; |  |  |  | Read_Real(rVar:=Circ[2].MaximumDemandA2,lo:=4624,hi:=4625); |  | 312:KlimaCErrors[17]:=Bit_0; |  |  |  | 4625:Circ[2].MaximumDemandA2:=Real_0;
mind_bool[313]:=KlimaCErrors[18]; |  |  |  | Read_Real(rVar:=Circ[2].MaximumDemandA3,lo:=4626,hi:=4627); |  | 313:KlimaCErrors[18]:=Bit_0; |  |  |  | 4627:Circ[2].MaximumDemandA3:=Real_0;
mind_bool[314]:=KlimaCErrors[19]; |  |  |  | Read_Real(rVar:=Circ[3].MaximumDemandA2,lo:=4628,hi:=4629); |  | 314:KlimaCErrors[19]:=Bit_0; |  |  |  | 4629:Circ[3].MaximumDemandA2:=Real_0;
mind_bool[315]:=KlimaCErrors[1]; |  |  |  | Read_Real(rVar:=Circ[3].MaximumDemandA3,lo:=4630,hi:=4631); |  | 315:KlimaCErrors[1]:=Bit_0; |  |  |  | 4631:Circ[3].MaximumDemandA3:=Real_0;
mind_bool[316]:=KlimaCErrors[20]; |  |  |  | Read_Real(rVar:=Circ[4].MaximumDemandA2,lo:=4632,hi:=4633); |  | 316:KlimaCErrors[20]:=Bit_0; |  |  |  | 4633:Circ[4].MaximumDemandA2:=Real_0;
mind_bool[317]:=KlimaCErrors[21]; |  |  |  | Read_Real(rVar:=Circ[4].MaximumDemandA3,lo:=4634,hi:=4635); |  | 317:KlimaCErrors[21]:=Bit_0; |  |  |  | 4635:Circ[4].MaximumDemandA3:=Real_0;
mind_bool[318]:=KlimaCErrors[22]; |  |  |  | Read_Real(rVar:=Circ[1].RazEner_D_SCADA,lo:=4636,hi:=4637); |  | 318:KlimaCErrors[22]:=Bit_0; |  |  |  | 4637:Circ[1].RazEner_D_SCADA:=Real_0;
mind_bool[319]:=KlimaCErrors[23]; |  |  |  | Read_Real(rVar:=Circ[1].RazEner_T_SCADA,lo:=4638,hi:=4639); |  | 319:KlimaCErrors[23]:=Bit_0; |  |  |  | 4639:Circ[1].RazEner_T_SCADA:=Real_0;
mind_bool[320]:=KlimaCErrors[24]; |  |  |  | Read_Real(rVar:=Circ[1].RazEner_M_SCADA,lo:=4640,hi:=4641); |  | 320:KlimaCErrors[24]:=Bit_0; |  |  |  | 4641:Circ[1].RazEner_M_SCADA:=Real_0;
mind_bool[321]:=KlimaCErrors[25]; |  |  |  | Read_Real(rVar:=Circ[2].RazEner_D_SCADA,lo:=4642,hi:=4643); |  | 321:KlimaCErrors[25]:=Bit_0; |  |  |  | 4643:Circ[2].RazEner_D_SCADA:=Real_0;
mind_bool[322]:=KlimaCErrors[26]; |  |  |  | Read_Real(rVar:=Circ[2].RazEner_T_SCADA,lo:=4644,hi:=4645); |  | 322:KlimaCErrors[26]:=Bit_0; |  |  |  | 4645:Circ[2].RazEner_T_SCADA:=Real_0;
mind_bool[323]:=KlimaCErrors[27]; |  |  |  | Read_Real(rVar:=Circ[2].RazEner_M_SCADA,lo:=4646,hi:=4647); |  | 323:KlimaCErrors[27]:=Bit_0; |  |  |  | 4647:Circ[2].RazEner_M_SCADA:=Real_0;
mind_bool[324]:=KlimaCErrors[28]; |  |  |  | Read_Real(rVar:=Circ[3].RazEner_D_SCADA,lo:=4648,hi:=4649); |  | 324:KlimaCErrors[28]:=Bit_0; |  |  |  | 4649:Circ[3].RazEner_D_SCADA:=Real_0;
mind_bool[325]:=KlimaCErrors[29]; |  |  |  | Read_Real(rVar:=Circ[3].RazEner_T_SCADA,lo:=4650,hi:=4651); |  | 325:KlimaCErrors[29]:=Bit_0; |  |  |  | 4651:Circ[3].RazEner_T_SCADA:=Real_0;
mind_bool[326]:=KlimaCErrors[2]; |  |  |  | Read_Real(rVar:=Circ[3].RazEner_M_SCADA,lo:=4652,hi:=4653); |  | 326:KlimaCErrors[2]:=Bit_0; |  |  |  | 4653:Circ[3].RazEner_M_SCADA:=Real_0;
mind_bool[327]:=KlimaCErrors[30]; |  |  |  | Read_Real(rVar:=Circ[4].RazEner_D_SCADA,lo:=4654,hi:=4655); |  | 327:KlimaCErrors[30]:=Bit_0; |  |  |  | 4655:Circ[4].RazEner_D_SCADA:=Real_0;
mind_bool[328]:=KlimaCErrors[31]; |  |  |  | Read_Real(rVar:=Circ[4].RazEner_T_SCADA,lo:=4656,hi:=4657); |  | 328:KlimaCErrors[31]:=Bit_0; |  |  |  | 4657:Circ[4].RazEner_T_SCADA:=Real_0;
mind_bool[329]:=KlimaCErrors[32]; |  |  |  | Read_Real(rVar:=Circ[4].RazEner_M_SCADA,lo:=4658,hi:=4659); |  | 329:KlimaCErrors[32]:=Bit_0; |  |  |  | 4659:Circ[4].RazEner_M_SCADA:=Real_0;
mind_bool[330]:=KlimaCErrors[33]; | [5 empty] | 330:KlimaCErrors[33]:=Bit_0;
mind_bool[331]:=KlimaCErrors[34]; | [5 empty] | 331:KlimaCErrors[34]:=Bit_0;
mind_bool[332]:=KlimaCErrors[35]; | [5 empty] | 332:KlimaCErrors[35]:=Bit_0;
mind_bool[333]:=KlimaCErrors[36]; | [5 empty] | 333:KlimaCErrors[36]:=Bit_0;
mind_bool[334]:=KlimaCErrors[37]; | [5 empty] | 334:KlimaCErrors[37]:=Bit_0;
mind_bool[335]:=KlimaCErrors[38]; | [5 empty] | 335:KlimaCErrors[38]:=Bit_0;
mind_bool[336]:=KlimaCErrors[39]; | [5 empty] | 336:KlimaCErrors[39]:=Bit_0;
mind_bool[337]:=KlimaCErrors[3]; | [5 empty] | 337:KlimaCErrors[3]:=Bit_0;
mind_bool[338]:=KlimaCErrors[40]; | [5 empty] | 338:KlimaCErrors[40]:=Bit_0;
mind_bool[339]:=KlimaCErrors[4]; | [5 empty] | 339:KlimaCErrors[4]:=Bit_0;
mind_bool[340]:=KlimaCErrors[5]; | [5 empty] | 340:KlimaCErrors[5]:=Bit_0;
mind_bool[341]:=KlimaCErrors[6]; | [5 empty] | 341:KlimaCErrors[6]:=Bit_0;
mind_bool[342]:=KlimaCErrors[7]; | [5 empty] | 342:KlimaCErrors[7]:=Bit_0;
mind_bool[343]:=KlimaCErrors[8]; | [5 empty] | 343:KlimaCErrors[8]:=Bit_0;
mind_bool[344]:=KlimaCErrors[9]; | [5 empty] | 344:KlimaCErrors[9]:=Bit_0;
mind_bool[345]:=KlimaGal.AlarmKompresor1; | [5 empty] | 345:KlimaGal.AlarmKompresor1:=Bit_0;
mind_bool[346]:=KlimaGal.AlarmKompresor2; | [5 empty] | 346:KlimaGal.AlarmKompresor2:=Bit_0;
mind_bool[347]:=KlimaGal.Deluje; | [5 empty] | 347:KlimaGal.Deluje:=Bit_0;
mind_bool[348]:=KlimaGal.EnergySaving; | [5 empty] | 348:KlimaGal.EnergySaving:=Bit_0;
mind_bool[349]:=KlimaGal.FaultyEPROM; | [5 empty] | 349:KlimaGal.FaultyEPROM:=Bit_0;
mind_bool[350]:=KlimaGal.FenThermalCutout; | [5 empty] | 350:KlimaGal.FenThermalCutout:=Bit_0;
mind_bool[351]:=KlimaGal.GeneralAlarm; | [5 empty] | 351:KlimaGal.GeneralAlarm:=Bit_0;
mind_bool[352]:=KlimaGal.Kompresor1naMejiObrUr; | [5 empty] | 352:KlimaGal.Kompresor1naMejiObrUr:=Bit_0;
mind_bool[353]:=KlimaGal.Kompresor2naMejiObrUr; | [5 empty] | 353:KlimaGal.Kompresor2naMejiObrUr:=Bit_0;
mind_bool[354]:=KlimaGal.Napaka; | [5 empty] | 354:KlimaGal.Napaka:=Bit_0;
mind_bool[355]:=KlimaGal.NapakaPriPretokuZraka; | [5 empty] | 355:KlimaGal.NapakaPriPretokuZraka:=Bit_0;
mind_bool[356]:=KlimaGal.NapakaSenzorPovratVode; | [5 empty] | 356:KlimaGal.NapakaSenzorPovratVode:=Bit_0;
mind_bool[357]:=KlimaGal.NapakaSenzorTempIzpiha; | [5 empty] | 357:KlimaGal.NapakaSenzorTempIzpiha:=Bit_0;
mind_bool[358]:=KlimaGal.NapakaSenzorTempProstora; | [5 empty] | 358:KlimaGal.NapakaSenzorTempProstora:=Bit_0;
mind_bool[359]:=KlimaGal.NapakaSenzorVlaznosti; | [5 empty] | 359:KlimaGal.NapakaSenzorVlaznosti:=Bit_0;
mind_bool[360]:=KlimaGal.NapakaSenzorZunanjeTemp; | [5 empty] | 360:KlimaGal.NapakaSenzorZunanjeTemp:=Bit_0;
mind_bool[361]:=KlimaGal.NiTokaVVlazilcu; | [5 empty] | 361:KlimaGal.NiTokaVVlazilcu:=Bit_0;
mind_bool[362]:=KlimaGal.NiVodeVVlazilcu; | [5 empty] | 362:KlimaGal.NiVodeVVlazilcu:=Bit_0;
mind_bool[363]:=KlimaGal.NizekPritiskKompresor1; | [5 empty] | 363:KlimaGal.NizekPritiskKompresor1:=Bit_0;
mind_bool[364]:=KlimaGal.NizekPritiskKompresor2; | [5 empty] | 364:KlimaGal.NizekPritiskKompresor2:=Bit_0;
mind_bool[365]:=KlimaGal.NizkaTempPovratneVode; | [5 empty] | 365:KlimaGal.NizkaTempPovratneVode:=Bit_0;
mind_bool[366]:=KlimaGal.NizkaTempVProstoru; | [5 empty] | 366:KlimaGal.NizkaTempVProstoru:=Bit_0;
mind_bool[367]:=KlimaGal.NizkaVlaznost; | [5 empty] | 367:KlimaGal.NizkaVlaznost:=Bit_0;
mind_bool[368]:=KlimaGal.OnOffEnablingBySupervisor; | [5 empty] | 368:KlimaGal.OnOffEnablingBySupervisor:=Bit_0;
mind_bool[369]:=KlimaGal.PozarniAlarm; | [5 empty] | 369:KlimaGal.PozarniAlarm:=Bit_0;
mind_bool[370]:=KlimaGal.Razvlazevanje; | [5 empty] | 370:KlimaGal.Razvlazevanje:=Bit_0;
mind_bool[371]:=KlimaGal.RemoteOFFtoOutput; | [5 empty] | 371:KlimaGal.RemoteOFFtoOutput:=Bit_0;
mind_bool[372]:=KlimaGal.RemoteOnOff; | [5 empty] | 372:KlimaGal.RemoteOnOff:=Bit_0;
mind_bool[373]:=KlimaGal.RocniIzklop; | [5 empty] | 373:KlimaGal.RocniIzklop:=Bit_0;
mind_bool[374]:=KlimaGal.SenzorjiStatus; | [5 empty] | 374:KlimaGal.SenzorjiStatus:=Bit_0;
mind_bool[375]:=KlimaGal.StoppedByAlarms; | [5 empty] | 375:KlimaGal.StoppedByAlarms:=Bit_0;
mind_bool[376]:=KlimaGal.ThermalCutoutHeater1; | [5 empty] | 376:KlimaGal.ThermalCutoutHeater1:=Bit_0;
mind_bool[377]:=KlimaGal.ThermalCutoutHeater2; | [5 empty] | 377:KlimaGal.ThermalCutoutHeater2:=Bit_0;
mind_bool[378]:=KlimaGal.UnitOnOff; | [5 empty] | 378:KlimaGal.UnitOnOff:=Bit_0;
mind_bool[379]:=KlimaGal.VentilatorNaMejiObrUr; | [5 empty] | 379:KlimaGal.VentilatorNaMejiObrUr:=Bit_0;
mind_bool[380]:=KlimaGal.VentilGretjeOdpiranje; | [5 empty] | 380:KlimaGal.VentilGretjeOdpiranje:=Bit_0;
mind_bool[381]:=KlimaGal.VentilGretjeZapiranje; | [5 empty] | 381:KlimaGal.VentilGretjeZapiranje:=Bit_0;
mind_bool[382]:=KlimaGal.VentilHlajenjeOdpiranje; | [5 empty] | 382:KlimaGal.VentilHlajenjeOdpiranje:=Bit_0;
mind_bool[383]:=KlimaGal.VentilHlajenjeZapiranje; | [5 empty] | 383:KlimaGal.VentilHlajenjeZapiranje:=Bit_0;
mind_bool[384]:=KlimaGal.VisokaTempPovratneVode; | [5 empty] | 384:KlimaGal.VisokaTempPovratneVode:=Bit_0;
mind_bool[385]:=KlimaGal.VisokaTempVProstoru; | [5 empty] | 385:KlimaGal.VisokaTempVProstoru:=Bit_0;
mind_bool[386]:=KlimaGal.VisokaVlaznost; | [5 empty] | 386:KlimaGal.VisokaVlaznost:=Bit_0;
mind_bool[387]:=KlimaGal.VisokTokVVlazilcu; | [5 empty] | 387:KlimaGal.VisokTokVVlazilcu:=Bit_0;
mind_bool[388]:=KlimaGal.Vlazenje; | [5 empty] | 388:KlimaGal.Vlazenje:=Bit_0;
mind_bool[389]:=KlimaGal.ZamasenFilter; | [5 empty] | 389:KlimaGal.ZamasenFilter:=Bit_0;
mind_bool[390]:=KlimeNaCas; | [5 empty] | 390:KlimeNaCas:=Bit_0;
mind_bool[391]:=NapakaSenzorTemp[10]; | [5 empty] | 391:NapakaSenzorTemp[10]:=Bit_0;
mind_bool[392]:=NapakaSenzorTemp[11]; | [5 empty] | 392:NapakaSenzorTemp[11]:=Bit_0;
mind_bool[393]:=NapakaSenzorTemp[12]; | [5 empty] | 393:NapakaSenzorTemp[12]:=Bit_0;
mind_bool[394]:=NapakaSenzorTemp[13]; | [5 empty] | 394:NapakaSenzorTemp[13]:=Bit_0;
mind_bool[395]:=NapakaSenzorTemp[14]; | [5 empty] | 395:NapakaSenzorTemp[14]:=Bit_0;
mind_bool[396]:=NapakaSenzorTemp[15]; | [5 empty] | 396:NapakaSenzorTemp[15]:=Bit_0;
mind_bool[397]:=NapakaSenzorTemp[16]; | [5 empty] | 397:NapakaSenzorTemp[16]:=Bit_0;
mind_bool[398]:=NapakaSenzorTemp[17]; | [5 empty] | 398:NapakaSenzorTemp[17]:=Bit_0;
mind_bool[399]:=NapakaSenzorTemp[18]; | [5 empty] | 399:NapakaSenzorTemp[18]:=Bit_0;
mind_bool[400]:=NapakaSenzorTemp[19]; | [5 empty] | 400:NapakaSenzorTemp[19]:=Bit_0;
mind_bool[401]:=NapakaSenzorTemp[1]; | [5 empty] | 401:NapakaSenzorTemp[1]:=Bit_0;
mind_bool[402]:=NapakaSenzorTemp[2]; | [5 empty] | 402:NapakaSenzorTemp[2]:=Bit_0;
mind_bool[403]:=NapakaSenzorTemp[3]; | [5 empty] | 403:NapakaSenzorTemp[3]:=Bit_0;
mind_bool[404]:=NapakaSenzorTemp[4]; | [5 empty] | 404:NapakaSenzorTemp[4]:=Bit_0;
mind_bool[405]:=NapakaSenzorTemp[5]; | [5 empty] | 405:NapakaSenzorTemp[5]:=Bit_0;
mind_bool[406]:=NapakaSenzorTemp[6]; | [5 empty] | 406:NapakaSenzorTemp[6]:=Bit_0;
mind_bool[407]:=NapakaSenzorTemp[7]; | [5 empty] | 407:NapakaSenzorTemp[7]:=Bit_0;
mind_bool[408]:=NapakaSenzorTemp[8]; | [5 empty] | 408:NapakaSenzorTemp[8]:=Bit_0;
mind_bool[409]:=NapakaSenzorTemp[9]; | [5 empty] | 409:NapakaSenzorTemp[9]:=Bit_0;
mind_bool[410]:=NapakaSenzorVlaga[10]; | [5 empty] | 410:NapakaSenzorVlaga[10]:=Bit_0;
mind_bool[411]:=NapakaSenzorVlaga[11]; | [5 empty] | 411:NapakaSenzorVlaga[11]:=Bit_0;
mind_bool[412]:=NapakaSenzorVlaga[12]; | [5 empty] | 412:NapakaSenzorVlaga[12]:=Bit_0;
mind_bool[413]:=NapakaSenzorVlaga[13]; | [5 empty] | 413:NapakaSenzorVlaga[13]:=Bit_0;
mind_bool[414]:=NapakaSenzorVlaga[14]; | [5 empty] | 414:NapakaSenzorVlaga[14]:=Bit_0;
mind_bool[415]:=NapakaSenzorVlaga[15]; | [5 empty] | 415:NapakaSenzorVlaga[15]:=Bit_0;
mind_bool[416]:=NapakaSenzorVlaga[16]; | [5 empty] | 416:NapakaSenzorVlaga[16]:=Bit_0;
mind_bool[417]:=NapakaSenzorVlaga[17]; | [5 empty] | 417:NapakaSenzorVlaga[17]:=Bit_0;
mind_bool[418]:=NapakaSenzorVlaga[18]; | [5 empty] | 418:NapakaSenzorVlaga[18]:=Bit_0;
mind_bool[419]:=NapakaSenzorVlaga[19]; | [5 empty] | 419:NapakaSenzorVlaga[19]:=Bit_0;
mind_bool[420]:=NapakaSenzorVlaga[1]; | [5 empty] | 420:NapakaSenzorVlaga[1]:=Bit_0;
mind_bool[421]:=NapakaSenzorVlaga[2]; | [5 empty] | 421:NapakaSenzorVlaga[2]:=Bit_0;
mind_bool[422]:=NapakaSenzorVlaga[3]; | [5 empty] | 422:NapakaSenzorVlaga[3]:=Bit_0;
mind_bool[423]:=NapakaSenzorVlaga[4]; | [5 empty] | 423:NapakaSenzorVlaga[4]:=Bit_0;
mind_bool[424]:=NapakaSenzorVlaga[5]; | [5 empty] | 424:NapakaSenzorVlaga[5]:=Bit_0;
mind_bool[425]:=NapakaSenzorVlaga[6]; | [5 empty] | 425:NapakaSenzorVlaga[6]:=Bit_0;
mind_bool[426]:=NapakaSenzorVlaga[7]; | [5 empty] | 426:NapakaSenzorVlaga[7]:=Bit_0;
mind_bool[427]:=NapakaSenzorVlaga[8]; | [5 empty] | 427:NapakaSenzorVlaga[8]:=Bit_0;
mind_bool[428]:=NapakaSenzorVlaga[9]; | [5 empty] | 428:NapakaSenzorVlaga[9]:=Bit_0;
mind_bool[429]:=SetDateTime; | [5 empty] | 429:SetDateTime:=Bit_0;
mind_bool[430]:=SetDateTimeDemand; | [5 empty] | 430:SetDateTimeDemand:=Bit_0;
mind_bool[431]:=SetDateTimeError; | [5 empty] | 431:SetDateTimeError:=Bit_0;
mind_bool[432]:=SetDateTimeFinished; | [5 empty] | 432:SetDateTimeFinished:=Bit_0;
mind_bool[433]:=SetRemoteOnOff[1]; | [5 empty] | 433:SetRemoteOnOff[1]:=Bit_0;
mind_bool[434]:=SetRemoteOnOff[2]; | [5 empty] | 434:SetRemoteOnOff[2]:=Bit_0;
mind_bool[435]:=SetRemoteOnOff[3]; | [5 empty] | 435:SetRemoteOnOff[3]:=Bit_0;
mind_bool[436]:=SlabaBaterijaPLC_A1; | [5 empty] | 436:SlabaBaterijaPLC_A1:=Bit_0;
mind_bool[437]:=TempTSprevisoka[10]; | [5 empty] | 437:TempTSprevisoka[10]:=Bit_0;
mind_bool[438]:=TempTSprevisoka[11]; | [5 empty] | 438:TempTSprevisoka[11]:=Bit_0;
mind_bool[439]:=TempTSprevisoka[12]; | [5 empty] | 439:TempTSprevisoka[12]:=Bit_0;
mind_bool[440]:=TempTSprevisoka[13]; | [5 empty] | 440:TempTSprevisoka[13]:=Bit_0;
mind_bool[441]:=TempTSprevisoka[14]; | [5 empty] | 441:TempTSprevisoka[14]:=Bit_0;
mind_bool[442]:=TempTSprevisoka[15]; | [5 empty] | 442:TempTSprevisoka[15]:=Bit_0;
mind_bool[443]:=TempTSprevisoka[16]; | [5 empty] | 443:TempTSprevisoka[16]:=Bit_0;
mind_bool[444]:=TempTSprevisoka[17]; | [5 empty] | 444:TempTSprevisoka[17]:=Bit_0;
mind_bool[445]:=TempTSprevisoka[18]; | [5 empty] | 445:TempTSprevisoka[18]:=Bit_0;
mind_bool[446]:=TempTSprevisoka[19]; | [5 empty] | 446:TempTSprevisoka[19]:=Bit_0;
mind_bool[447]:=TempTSprevisoka[1]; | [5 empty] | 447:TempTSprevisoka[1]:=Bit_0;
mind_bool[448]:=TempTSprevisoka[2]; | [5 empty] | 448:TempTSprevisoka[2]:=Bit_0;
mind_bool[449]:=TempTSprevisoka[3]; | [5 empty] | 449:TempTSprevisoka[3]:=Bit_0;
mind_bool[450]:=TempTSprevisoka[4]; | [5 empty] | 450:TempTSprevisoka[4]:=Bit_0;
mind_bool[451]:=TempTSprevisoka[5]; | [5 empty] | 451:TempTSprevisoka[5]:=Bit_0;
mind_bool[452]:=TempTSprevisoka[6]; | [5 empty] | 452:TempTSprevisoka[6]:=Bit_0;
mind_bool[453]:=TempTSprevisoka[7]; | [5 empty] | 453:TempTSprevisoka[7]:=Bit_0;
mind_bool[454]:=TempTSprevisoka[8]; | [5 empty] | 454:TempTSprevisoka[8]:=Bit_0;
mind_bool[455]:=TempTSprevisoka[9]; | [5 empty] | 455:TempTSprevisoka[9]:=Bit_0;
mind_bool[456]:=UserLoggedIn; | [5 empty] | 456:UserLoggedIn:=Bit_0;
mind_bool[457]:=XVH_AlarmOn; | [5 empty] | 457:XVH_AlarmOn:=Bit_0;
mind_bool[458]:=XVH_RemoteStatus[1]; | [5 empty] | 458:XVH_RemoteStatus[1]:=Bit_0;
mind_bool[459]:=XVH_RemoteStatus[2]; | [5 empty] | 459:XVH_RemoteStatus[2]:=Bit_0;
mind_bool[460]:=XVH_RemoteStatus[3]; | [5 empty] | 460:XVH_RemoteStatus[3]:=Bit_0;
mind_bool[461]:=XVH_setCircNum[1]; | [5 empty] | 461:XVH_setCircNum[1]:=Bit_0;
mind_bool[462]:=XVH_setCircNum[2]; | [5 empty] | 462:XVH_setCircNum[2]:=Bit_0;
mind_bool[463]:=XVH_setCircNum[3]; | [5 empty] | 463:XVH_setCircNum[3]:=Bit_0;
mind_bool[464]:=XVH_setCircNum[4]; | [5 empty] | 464:XVH_setCircNum[4]:=Bit_0;
mind_bool[465]:=XVH_setCircNum[5]; | [5 empty] | 465:XVH_setCircNum[5]:=Bit_0;
mind_bool[466]:=XVH_setKlimaNum[1]; | [5 empty] | 466:XVH_setKlimaNum[1]:=Bit_0;
mind_bool[467]:=XVH_setKlimaNum[2]; | [5 empty] | 467:XVH_setKlimaNum[2]:=Bit_0;
mind_bool[468]:=XVH_setKlimaNum[3]; | [5 empty] | 468:XVH_setKlimaNum[3]:=Bit_0;
mind_bool[469]:=XVH_setKlimaNum[4]; | [5 empty] | 469:XVH_setKlimaNum[4]:=Bit_0;
mind_bool[470]:=XVH_setKlimaNum[5]; | [5 empty] | 470:XVH_setKlimaNum[5]:=Bit_0;
mind_bool[471]:=XVH_setKlimaNum[6]; | [5 empty] | 471:XVH_setKlimaNum[6]:=Bit_0;
mind_bool[472]:=ComSCADA2; | [5 empty] | 472:ComSCADA2:=Bit_0;
mind_bool[473]:=ErrCommScada2; | [5 empty] | 473:ErrCommScada2:=Bit_0;
mind_bool[474]:=ComSCADA3; | [5 empty] | 474:ComSCADA3:=Bit_0;
mind_bool[475]:=Circ_Vpis_Dnevne_energija_scada1; | [5 empty] | 475:Circ_Vpis_Dnevne_energija_scada1:=Bit_0;
mind_bool[476]:=Circ_Vpis_Dnevne_energija_scada2; | [5 empty] | 476:Circ_Vpis_Dnevne_energija_scada2:=Bit_0;
mind_bool[477]:=Circ_Vpis_Tedenska_energija_scada1; | [5 empty] | 477:Circ_Vpis_Tedenska_energija_scada1:=Bit_0;
mind_bool[478]:=Circ_Vpis_Tedenska_energija_scada2; | [5 empty] | 478:Circ_Vpis_Tedenska_energija_scada2:=Bit_0;
mind_bool[479]:=Circ_Vpis_Mesecna_energija_scada1; | [5 empty] | 479:Circ_Vpis_Mesecna_energija_scada1:=Bit_0;
mind_bool[480]:=Circ_Vpis_Mesecna_energija_scada2; | [5 empty] | 480:Circ_Vpis_Mesecna_energija_scada2:=Bit_0;

## XSoft_EXP
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
PROGRAM mod_Read
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*Branje BOOL*)
(**)
mind_bool[0]:=AlarmGenCirc1;
mind_bool[1]:=AlarmGenCirc2;
mind_bool[2]:=AlarmGenCirc3;
mind_bool[3]:=AlarmGenCirc4;
mind_bool[4]:=AlarmGenComm;
mind_bool[5]:=AlarmGenDI;
mind_bool[6]:=AlarmGenKlima1;
mind_bool[7]:=AlarmGenKlima2;
mind_bool[8]:=AlarmGenKlima3;
mind_bool[9]:=AlarmGenRest;
mind_bool[10]:=AlarmGenSenzor;
mind_bool[11]:=AlarmGenTemp;
mind_bool[12]:=AlarmGenVlPr;
mind_bool[13]:=AlarmGenVTV;
mind_bool[14]:=ComSCADA;
mind_bool[15]:=ComSCADA1;
mind_bool[16]:=DI_F1_OdklHlOm1_IZP;
mind_bool[17]:=DI_F1_OdklHlOm1_ON;
mind_bool[18]:=DI_F2_OdklHlOm2_IZP;
mind_bool[19]:=DI_F2_OdklHlOm2_ON;
mind_bool[20]:=DI_F3_OdklHlOm3_IZP;
mind_bool[21]:=DI_F3_OdklHlOm3_ON;
mind_bool[22]:=DI_F4_OdkPripVode_IZP;
mind_bool[23]:=DI_F4_OdkPripVode_ON;
mind_bool[24]:=DI_HladOmara1_ERR;
mind_bool[25]:=DI_HladOmara1_ON;
mind_bool[26]:=DI_HladOmara2_ERR;
mind_bool[27]:=DI_HladOmara2_ON;
mind_bool[28]:=DI_HladOmara3_ERR;
mind_bool[29]:=DI_HladOmara3_ON;
mind_bool[30]:=DI_PripVode1_ERR;
mind_bool[31]:=DI_PripVode1_ON;
mind_bool[32]:=DI_PripVode2_ERR;
mind_bool[33]:=DI_PripVode2_ON;
mind_bool[34]:=DI_Q0_DEG3_ON;
mind_bool[35]:=DI_Q0_EG3_ON;
mind_bool[36]:=DI_Q0_GlavnoStikalo_ON;
mind_bool[37]:=DI_Q0_UPS3_ON;
mind_bool[38]:=DI_RazlitjeVodeHO1;
mind_bool[39]:=DI_RazlitjeVodeHO2;
mind_bool[40]:=DI_RazlitjeVodeHO3;
mind_bool[41]:=DI_UPS_Alarm;
mind_bool[42]:=DI_UPS_BatNacin;
mind_bool[43]:=DI_UPS_Polnjenje;
mind_bool[44]:=DI_Vlazilec1_ERR;
mind_bool[45]:=DI_Vlazilec1_ON;
mind_bool[46]:=DI_Vlazilec2_ERR;
mind_bool[47]:=DI_Vlazilec2_ON;
mind_bool[48]:=DI_Vlazilec3_ERR;
mind_bool[49]:=DI_Vlazilec3_ON;
mind_bool[50]:=DIN_F1_OdklHlOm1_IZP;
mind_bool[51]:=DIN_F2_OdklHlOm2_IZP;
mind_bool[52]:=DIN_F3_OdklHlOm3_IZP;
mind_bool[53]:=DIN_F4_OdkPripVode_IZP;
mind_bool[54]:=DIN_HladOmara1_ERR;
mind_bool[55]:=DIN_HladOmara2_ERR;
mind_bool[56]:=DIN_HladOmara3_ERR;
mind_bool[57]:=DIN_PripVode1_ERR;
mind_bool[58]:=DIN_PripVode2_ERR;
mind_bool[59]:=DIN_Vlazilec1_ERR;
mind_bool[60]:=DIN_Vlazilec2_ERR;
mind_bool[61]:=DIN_Vlazilec3_ERR;
mind_bool[62]:=DO_HladOm1_Izklop;
mind_bool[63]:=DO_HladOm2_Izklop;
mind_bool[64]:=DO_HladOm3_Izklop;
mind_bool[65]:=ErrComCirc[1];
mind_bool[66]:=ErrComCirc[2];
mind_bool[67]:=ErrComCirc[3];
mind_bool[68]:=ErrComCirc[4];
mind_bool[69]:=ErrComCirc[5];
mind_bool[70]:=ErrComKlima[1];
mind_bool[71]:=ErrComKlima[2];
mind_bool[72]:=ErrComKlima[3];
mind_bool[73]:=ErrComKlima[4];
mind_bool[74]:=ErrComKlima[5];
mind_bool[75]:=ErrComKlima[6];
mind_bool[76]:=ErrCommScada;
mind_bool[77]:=ErrComPanelPLC;
mind_bool[78]:=ErrComPort2;
mind_bool[79]:=ErrorComCirc[1].Error;
mind_bool[80]:=ErrorComCirc[2].Error;
mind_bool[81]:=ErrorComCirc[3].Error;
mind_bool[82]:=ErrorComCirc[4].Error;
mind_bool[83]:=ErrorComCirc[5].Error;
mind_bool[84]:=ErrorComKlima[1].Error;
mind_bool[85]:=ErrorComKlima[2].Error;
mind_bool[86]:=ErrorComKlima[3].Error;
mind_bool[87]:=ErrorComKlima[4].Error;
mind_bool[88]:=ErrorComKlima[5].Error;
mind_bool[89]:=ErrorComKlima[6].Error;
mind_bool[90]:=Klima[1].AlarmKompresor1;
mind_bool[91]:=Klima[1].AlarmKompresor2;
mind_bool[92]:=Klima[1].Deluje;
mind_bool[93]:=Klima[1].EnergySaving;
mind_bool[94]:=Klima[1].FaultyEPROM;
mind_bool[95]:=Klima[1].FenThermalCutout;
mind_bool[96]:=Klima[1].GeneralAlarm;
mind_bool[97]:=Klima[1].Kompresor1naMejiObrUr;
mind_bool[98]:=Klima[1].Kompresor2naMejiObrUr;
mind_bool[99]:=Klima[1].Napaka;
mind_bool[100]:=Klima[1].NapakaPriPretokuZraka;
mind_bool[101]:=Klima[1].NapakaSenzorPovratVode;
mind_bool[102]:=Klima[1].NapakaSenzorTempIzpiha;
mind_bool[103]:=Klima[1].NapakaSenzorTempProstora;
mind_bool[104]:=Klima[1].NapakaSenzorVlaznosti;
mind_bool[105]:=Klima[1].NapakaSenzorZunanjeTemp;
mind_bool[106]:=Klima[1].NiTokaVVlazilcu;
mind_bool[107]:=Klima[1].NiVodeVVlazilcu;
mind_bool[108]:=Klima[1].NizekPritiskKompresor1;
mind_bool[109]:=Klima[1].NizekPritiskKompresor2;
mind_bool[110]:=Klima[1].NizkaTempPovratneVode;
mind_bool[111]:=Klima[1].NizkaTempVProstoru;
mind_bool[112]:=Klima[1].NizkaVlaznost;
mind_bool[113]:=Klima[1].OnOffEnablingBySupervisor;
mind_bool[114]:=Klima[1].PozarniAlarm;
mind_bool[115]:=Klima[1].Razvlazevanje;
mind_bool[116]:=Klima[1].RemoteOFFtoOutput;
mind_bool[117]:=Klima[1].RemoteOnOff;
mind_bool[118]:=Klima[1].RocniIzklop;
mind_bool[119]:=Klima[1].SenzorjiStatus;
mind_bool[120]:=Klima[1].StoppedByAlarms;
mind_bool[121]:=Klima[1].ThermalCutoutHeater1;
mind_bool[122]:=Klima[1].ThermalCutoutHeater2;
mind_bool[123]:=Klima[1].UnitOnOff;
mind_bool[124]:=Klima[1].VentilatorNaMejiObrUr;
mind_bool[125]:=Klima[1].VentilGretjeOdpiranje;
mind_bool[126]:=Klima[1].VentilGretjeZapiranje;
mind_bool[127]:=Klima[1].VentilHlajenjeOdpiranje;
mind_bool[128]:=Klima[1].VentilHlajenjeZapiranje;
mind_bool[129]:=Klima[1].VisokaTempPovratneVode;
mind_bool[130]:=Klima[1].VisokaTempVProstoru;
mind_bool[131]:=Klima[1].VisokaVlaznost;
mind_bool[132]:=Klima[1].VisokTokVVlazilcu;
mind_bool[133]:=Klima[1].Vlazenje;
mind_bool[134]:=Klima[1].ZamasenFilter;
mind_bool[135]:=Klima[2].AlarmKompresor1;
mind_bool[136]:=Klima[2].AlarmKompresor2;
mind_bool[137]:=Klima[2].Deluje;
mind_bool[138]:=Klima[2].EnergySaving;
mind_bool[139]:=Klima[2].FaultyEPROM;
mind_bool[140]:=Klima[2].FenThermalCutout;
mind_bool[141]:=Klima[2].GeneralAlarm;
mind_bool[142]:=Klima[2].Kompresor1naMejiObrUr;
mind_bool[143]:=Klima[2].Kompresor2naMejiObrUr;
mind_bool[144]:=Klima[2].Napaka;
mind_bool[145]:=Klima[2].NapakaPriPretokuZraka;
mind_bool[146]:=Klima[2].NapakaSenzorPovratVode;
mind_bool[147]:=Klima[2].NapakaSenzorTempIzpiha;
mind_bool[148]:=Klima[2].NapakaSenzorTempProstora;
mind_bool[149]:=Klima[2].NapakaSenzorVlaznosti;
mind_bool[150]:=Klima[2].NapakaSenzorZunanjeTemp;
mind_bool[151]:=Klima[2].NiTokaVVlazilcu;
mind_bool[152]:=Klima[2].NiVodeVVlazilcu;
mind_bool[153]:=Klima[2].NizekPritiskKompresor1;
mind_bool[154]:=Klima[2].NizekPritiskKompresor2;
mind_bool[155]:=Klima[2].NizkaTempPovratneVode;
mind_bool[156]:=Klima[2].NizkaTempVProstoru;
mind_bool[157]:=Klima[2].NizkaVlaznost;
mind_bool[158]:=Klima[2].OnOffEnablingBySupervisor;
mind_bool[159]:=Klima[2].PozarniAlarm;
mind_bool[160]:=Klima[2].Razvlazevanje;
mind_bool[161]:=Klima[2].RemoteOFFtoOutput;
mind_bool[162]:=Klima[2].RemoteOnOff;
mind_bool[163]:=Klima[2].RocniIzklop;
mind_bool[164]:=Klima[2].SenzorjiStatus;
mind_bool[165]:=Klima[2].StoppedByAlarms;
mind_bool[166]:=Klima[2].ThermalCutoutHeater1;
mind_bool[167]:=Klima[2].ThermalCutoutHeater2;
mind_bool[168]:=Klima[2].UnitOnOff;
mind_bool[169]:=Klima[2].VentilatorNaMejiObrUr;
mind_bool[170]:=Klima[2].VentilGretjeOdpiranje;
mind_bool[171]:=Klima[2].VentilGretjeZapiranje;
mind_bool[172]:=Klima[2].VentilHlajenjeOdpiranje;
mind_bool[173]:=Klima[2].VentilHlajenjeZapiranje;
mind_bool[174]:=Klima[2].VisokaTempPovratneVode;
mind_bool[175]:=Klima[2].VisokaTempVProstoru;
mind_bool[176]:=Klima[2].VisokaVlaznost;
mind_bool[177]:=Klima[2].VisokTokVVlazilcu;
mind_bool[178]:=Klima[2].Vlazenje;
mind_bool[179]:=Klima[2].ZamasenFilter;
mind_bool[180]:=Klima[3].AlarmKompresor1;
mind_bool[181]:=Klima[3].AlarmKompresor2;
mind_bool[182]:=Klima[3].Deluje;
mind_bool[183]:=Klima[3].EnergySaving;
mind_bool[184]:=Klima[3].FaultyEPROM;
mind_bool[185]:=Klima[3].FenThermalCutout;
mind_bool[186]:=Klima[3].GeneralAlarm;
mind_bool[187]:=Klima[3].Kompresor1naMejiObrUr;
mind_bool[188]:=Klima[3].Kompresor2naMejiObrUr;
mind_bool[189]:=Klima[3].Napaka;
mind_bool[190]:=Klima[3].NapakaPriPretokuZraka;
mind_bool[191]:=Klima[3].NapakaSenzorPovratVode;
mind_bool[192]:=Klima[3].NapakaSenzorTempIzpiha;
mind_bool[193]:=Klima[3].NapakaSenzorTempProstora;
mind_bool[194]:=Klima[3].NapakaSenzorVlaznosti;
mind_bool[195]:=Klima[3].NapakaSenzorZunanjeTemp;
mind_bool[196]:=Klima[3].NiTokaVVlazilcu;
mind_bool[197]:=Klima[3].NiVodeVVlazilcu;
mind_bool[198]:=Klima[3].NizekPritiskKompresor1;
mind_bool[199]:=Klima[3].NizekPritiskKompresor2;
mind_bool[200]:=Klima[3].NizkaTempPovratneVode;
mind_bool[201]:=Klima[3].NizkaTempVProstoru;
mind_bool[202]:=Klima[3].NizkaVlaznost;
mind_bool[203]:=Klima[3].OnOffEnablingBySupervisor;
mind_bool[204]:=Klima[3].PozarniAlarm;
mind_bool[205]:=Klima[3].Razvlazevanje;
mind_bool[206]:=Klima[3].RemoteOFFtoOutput;
mind_bool[207]:=Klima[3].RemoteOnOff;
mind_bool[208]:=Klima[3].RocniIzklop;
mind_bool[209]:=Klima[3].SenzorjiStatus;
mind_bool[210]:=Klima[3].StoppedByAlarms;
mind_bool[211]:=Klima[3].ThermalCutoutHeater1;
mind_bool[212]:=Klima[3].ThermalCutoutHeater2;
mind_bool[213]:=Klima[3].UnitOnOff;
mind_bool[214]:=Klima[3].VentilatorNaMejiObrUr;
mind_bool[215]:=Klima[3].VentilGretjeOdpiranje;
mind_bool[216]:=Klima[3].VentilGretjeZapiranje;
mind_bool[217]:=Klima[3].VentilHlajenjeOdpiranje;
mind_bool[218]:=Klima[3].VentilHlajenjeZapiranje;
mind_bool[219]:=Klima[3].VisokaTempPovratneVode;
mind_bool[220]:=Klima[3].VisokaTempVProstoru;
mind_bool[221]:=Klima[3].VisokaVlaznost;
mind_bool[222]:=Klima[3].VisokTokVVlazilcu;
mind_bool[223]:=Klima[3].Vlazenje;
mind_bool[224]:=Klima[3].ZamasenFilter;
mind_bool[225]:=KlimaAErrors[10];
mind_bool[226]:=KlimaAErrors[11];
mind_bool[227]:=KlimaAErrors[12];
mind_bool[228]:=KlimaAErrors[13];
mind_bool[229]:=KlimaAErrors[14];
mind_bool[230]:=KlimaAErrors[15];
mind_bool[231]:=KlimaAErrors[16];
mind_bool[232]:=KlimaAErrors[17];
mind_bool[233]:=KlimaAErrors[18];
mind_bool[234]:=KlimaAErrors[19];
mind_bool[235]:=KlimaAErrors[1];
mind_bool[236]:=KlimaAErrors[20];
mind_bool[237]:=KlimaAErrors[21];
mind_bool[238]:=KlimaAErrors[22];
mind_bool[239]:=KlimaAErrors[23];
mind_bool[240]:=KlimaAErrors[24];
mind_bool[241]:=KlimaAErrors[25];
mind_bool[242]:=KlimaAErrors[26];
mind_bool[243]:=KlimaAErrors[27];
mind_bool[244]:=KlimaAErrors[28];
mind_bool[245]:=KlimaAErrors[29];
mind_bool[246]:=KlimaAErrors[2];
mind_bool[247]:=KlimaAErrors[30];
mind_bool[248]:=KlimaAErrors[31];
mind_bool[249]:=KlimaAErrors[32];
mind_bool[250]:=KlimaAErrors[33];
mind_bool[251]:=KlimaAErrors[34];
mind_bool[252]:=KlimaAErrors[35];
mind_bool[253]:=KlimaAErrors[36];
mind_bool[254]:=KlimaAErrors[37];
mind_bool[255]:=KlimaAErrors[38];
mind_bool[256]:=KlimaAErrors[39];
mind_bool[257]:=KlimaAErrors[3];
mind_bool[258]:=KlimaAErrors[40];
mind_bool[259]:=KlimaAErrors[4];
mind_bool[260]:=KlimaAErrors[5];
mind_bool[261]:=KlimaAErrors[6];
mind_bool[262]:=KlimaAErrors[7];
mind_bool[263]:=KlimaAErrors[8];
mind_bool[264]:=KlimaAErrors[9];
mind_bool[265]:=KlimaBErrors[10];
mind_bool[266]:=KlimaBErrors[11];
mind_bool[267]:=KlimaBErrors[12];
mind_bool[268]:=KlimaBErrors[13];
mind_bool[269]:=KlimaBErrors[14];
mind_bool[270]:=KlimaBErrors[15];
mind_bool[271]:=KlimaBErrors[16];
mind_bool[272]:=KlimaBErrors[17];
mind_bool[273]:=KlimaBErrors[18];
mind_bool[274]:=KlimaBErrors[19];
mind_bool[275]:=KlimaBErrors[1];
mind_bool[276]:=KlimaBErrors[20];
mind_bool[277]:=KlimaBErrors[21];
mind_bool[278]:=KlimaBErrors[22];
mind_bool[279]:=KlimaBErrors[23];
mind_bool[280]:=KlimaBErrors[24];
mind_bool[281]:=KlimaBErrors[25];
mind_bool[282]:=KlimaBErrors[26];
mind_bool[283]:=KlimaBErrors[27];
mind_bool[284]:=KlimaBErrors[28];
mind_bool[285]:=KlimaBErrors[29];
mind_bool[286]:=KlimaBErrors[2];
mind_bool[287]:=KlimaBErrors[30];
mind_bool[288]:=KlimaBErrors[31];
mind_bool[289]:=KlimaBErrors[32];
mind_bool[290]:=KlimaBErrors[33];
mind_bool[291]:=KlimaBErrors[34];
mind_bool[292]:=KlimaBErrors[35];
mind_bool[293]:=KlimaBErrors[36];
mind_bool[294]:=KlimaBErrors[37];
mind_bool[295]:=KlimaBErrors[38];
mind_bool[296]:=KlimaBErrors[39];
mind_bool[297]:=KlimaBErrors[3];
mind_bool[298]:=KlimaBErrors[40];
mind_bool[299]:=KlimaBErrors[4];
mind_bool[300]:=KlimaBErrors[5];
mind_bool[301]:=KlimaBErrors[6];
mind_bool[302]:=KlimaBErrors[7];
mind_bool[303]:=KlimaBErrors[8];
mind_bool[304]:=KlimaBErrors[9];
mind_bool[305]:=KlimaCErrors[10];
mind_bool[306]:=KlimaCErrors[11];
mind_bool[307]:=KlimaCErrors[12];
mind_bool[308]:=KlimaCErrors[13];
mind_bool[309]:=KlimaCErrors[14];
mind_bool[310]:=KlimaCErrors[15];
mind_bool[311]:=KlimaCErrors[16];
mind_bool[312]:=KlimaCErrors[17];
mind_bool[313]:=KlimaCErrors[18];
mind_bool[314]:=KlimaCErrors[19];
mind_bool[315]:=KlimaCErrors[1];
mind_bool[316]:=KlimaCErrors[20];
mind_bool[317]:=KlimaCErrors[21];
mind_bool[318]:=KlimaCErrors[22];
mind_bool[319]:=KlimaCErrors[23];
mind_bool[320]:=KlimaCErrors[24];
mind_bool[321]:=KlimaCErrors[25];
mind_bool[322]:=KlimaCErrors[26];
mind_bool[323]:=KlimaCErrors[27];
mind_bool[324]:=KlimaCErrors[28];
mind_bool[325]:=KlimaCErrors[29];
mind_bool[326]:=KlimaCErrors[2];
mind_bool[327]:=KlimaCErrors[30];
mind_bool[328]:=KlimaCErrors[31];
mind_bool[329]:=KlimaCErrors[32];
mind_bool[330]:=KlimaCErrors[33];
mind_bool[331]:=KlimaCErrors[34];
mind_bool[332]:=KlimaCErrors[35];
mind_bool[333]:=KlimaCErrors[36];
mind_bool[334]:=KlimaCErrors[37];
mind_bool[335]:=KlimaCErrors[38];
mind_bool[336]:=KlimaCErrors[39];
mind_bool[337]:=KlimaCErrors[3];
mind_bool[338]:=KlimaCErrors[40];
mind_bool[339]:=KlimaCErrors[4];
mind_bool[340]:=KlimaCErrors[5];
mind_bool[341]:=KlimaCErrors[6];
mind_bool[342]:=KlimaCErrors[7];
mind_bool[343]:=KlimaCErrors[8];
mind_bool[344]:=KlimaCErrors[9];
mind_bool[345]:=KlimaGal.AlarmKompresor1;
mind_bool[346]:=KlimaGal.AlarmKompresor2;
mind_bool[347]:=KlimaGal.Deluje;
mind_bool[348]:=KlimaGal.EnergySaving;
mind_bool[349]:=KlimaGal.FaultyEPROM;
mind_bool[350]:=KlimaGal.FenThermalCutout;
mind_bool[351]:=KlimaGal.GeneralAlarm;
mind_bool[352]:=KlimaGal.Kompresor1naMejiObrUr;
mind_bool[353]:=KlimaGal.Kompresor2naMejiObrUr;
mind_bool[354]:=KlimaGal.Napaka;
mind_bool[355]:=KlimaGal.NapakaPriPretokuZraka;
mind_bool[356]:=KlimaGal.NapakaSenzorPovratVode;
mind_bool[357]:=KlimaGal.NapakaSenzorTempIzpiha;
mind_bool[358]:=KlimaGal.NapakaSenzorTempProstora;
mind_bool[359]:=KlimaGal.NapakaSenzorVlaznosti;
mind_bool[360]:=KlimaGal.NapakaSenzorZunanjeTemp;
mind_bool[361]:=KlimaGal.NiTokaVVlazilcu;
mind_bool[362]:=KlimaGal.NiVodeVVlazilcu;
mind_bool[363]:=KlimaGal.NizekPritiskKompresor1;
mind_bool[364]:=KlimaGal.NizekPritiskKompresor2;
mind_bool[365]:=KlimaGal.NizkaTempPovratneVode;
mind_bool[366]:=KlimaGal.NizkaTempVProstoru;
mind_bool[367]:=KlimaGal.NizkaVlaznost;
mind_bool[368]:=KlimaGal.OnOffEnablingBySupervisor;
mind_bool[369]:=KlimaGal.PozarniAlarm;
mind_bool[370]:=KlimaGal.Razvlazevanje;
mind_bool[371]:=KlimaGal.RemoteOFFtoOutput;
mind_bool[372]:=KlimaGal.RemoteOnOff;
mind_bool[373]:=KlimaGal.RocniIzklop;
mind_bool[374]:=KlimaGal.SenzorjiStatus;
mind_bool[375]:=KlimaGal.StoppedByAlarms;
mind_bool[376]:=KlimaGal.ThermalCutoutHeater1;
mind_bool[377]:=KlimaGal.ThermalCutoutHeater2;
mind_bool[378]:=KlimaGal.UnitOnOff;
mind_bool[379]:=KlimaGal.VentilatorNaMejiObrUr;
mind_bool[380]:=KlimaGal.VentilGretjeOdpiranje;
mind_bool[381]:=KlimaGal.VentilGretjeZapiranje;
mind_bool[382]:=KlimaGal.VentilHlajenjeOdpiranje;
mind_bool[383]:=KlimaGal.VentilHlajenjeZapiranje;
mind_bool[384]:=KlimaGal.VisokaTempPovratneVode;
mind_bool[385]:=KlimaGal.VisokaTempVProstoru;
mind_bool[386]:=KlimaGal.VisokaVlaznost;
mind_bool[387]:=KlimaGal.VisokTokVVlazilcu;
mind_bool[388]:=KlimaGal.Vlazenje;
mind_bool[389]:=KlimaGal.ZamasenFilter;
mind_bool[390]:=KlimeNaCas;
mind_bool[391]:=NapakaSenzorTemp[10];
mind_bool[392]:=NapakaSenzorTemp[11];
mind_bool[393]:=NapakaSenzorTemp[12];
mind_bool[394]:=NapakaSenzorTemp[13];
mind_bool[395]:=NapakaSenzorTemp[14];
mind_bool[396]:=NapakaSenzorTemp[15];
mind_bool[397]:=NapakaSenzorTemp[16];
mind_bool[398]:=NapakaSenzorTemp[17];
mind_bool[399]:=NapakaSenzorTemp[18];
mind_bool[400]:=NapakaSenzorTemp[19];
mind_bool[401]:=NapakaSenzorTemp[1];
mind_bool[402]:=NapakaSenzorTemp[2];
mind_bool[403]:=NapakaSenzorTemp[3];
mind_bool[404]:=NapakaSenzorTemp[4];
mind_bool[405]:=NapakaSenzorTemp[5];
mind_bool[406]:=NapakaSenzorTemp[6];
mind_bool[407]:=NapakaSenzorTemp[7];
mind_bool[408]:=NapakaSenzorTemp[8];
mind_bool[409]:=NapakaSenzorTemp[9];
mind_bool[410]:=NapakaSenzorVlaga[10];
mind_bool[411]:=NapakaSenzorVlaga[11];
mind_bool[412]:=NapakaSenzorVlaga[12];
mind_bool[413]:=NapakaSenzorVlaga[13];
mind_bool[414]:=NapakaSenzorVlaga[14];
mind_bool[415]:=NapakaSenzorVlaga[15];
mind_bool[416]:=NapakaSenzorVlaga[16];
mind_bool[417]:=NapakaSenzorVlaga[17];
mind_bool[418]:=NapakaSenzorVlaga[18];
mind_bool[419]:=NapakaSenzorVlaga[19];
mind_bool[420]:=NapakaSenzorVlaga[1];
mind_bool[421]:=NapakaSenzorVlaga[2];
mind_bool[422]:=NapakaSenzorVlaga[3];
mind_bool[423]:=NapakaSenzorVlaga[4];
mind_bool[424]:=NapakaSenzorVlaga[5];
mind_bool[425]:=NapakaSenzorVlaga[6];
mind_bool[426]:=NapakaSenzorVlaga[7];
mind_bool[427]:=NapakaSenzorVlaga[8];
mind_bool[428]:=NapakaSenzorVlaga[9];
mind_bool[429]:=SetDateTime;
mind_bool[430]:=SetDateTimeDemand;
mind_bool[431]:=SetDateTimeError;
mind_bool[432]:=SetDateTimeFinished;
mind_bool[433]:=SetRemoteOnOff[1];
mind_bool[434]:=SetRemoteOnOff[2];
mind_bool[435]:=SetRemoteOnOff[3];
mind_bool[436]:=SlabaBaterijaPLC_A1;
mind_bool[437]:=TempTSprevisoka[10];
mind_bool[438]:=TempTSprevisoka[11];
mind_bool[439]:=TempTSprevisoka[12];
mind_bool[440]:=TempTSprevisoka[13];
mind_bool[441]:=TempTSprevisoka[14];
mind_bool[442]:=TempTSprevisoka[15];
mind_bool[443]:=TempTSprevisoka[16];
mind_bool[444]:=TempTSprevisoka[17];
mind_bool[445]:=TempTSprevisoka[18];
mind_bool[446]:=TempTSprevisoka[19];
mind_bool[447]:=TempTSprevisoka[1];
mind_bool[448]:=TempTSprevisoka[2];
mind_bool[449]:=TempTSprevisoka[3];
mind_bool[450]:=TempTSprevisoka[4];
mind_bool[451]:=TempTSprevisoka[5];
mind_bool[452]:=TempTSprevisoka[6];
mind_bool[453]:=TempTSprevisoka[7];
mind_bool[454]:=TempTSprevisoka[8];
mind_bool[455]:=TempTSprevisoka[9];
mind_bool[456]:=UserLoggedIn;
mind_bool[457]:=XVH_AlarmOn;
mind_bool[458]:=XVH_RemoteStatus[1];
mind_bool[459]:=XVH_RemoteStatus[2];
mind_bool[460]:=XVH_RemoteStatus[3];
mind_bool[461]:=XVH_setCircNum[1];
mind_bool[462]:=XVH_setCircNum[2];
mind_bool[463]:=XVH_setCircNum[3];
mind_bool[464]:=XVH_setCircNum[4];
mind_bool[465]:=XVH_setCircNum[5];
mind_bool[466]:=XVH_setKlimaNum[1];
mind_bool[467]:=XVH_setKlimaNum[2];
mind_bool[468]:=XVH_setKlimaNum[3];
mind_bool[469]:=XVH_setKlimaNum[4];
mind_bool[470]:=XVH_setKlimaNum[5];
mind_bool[471]:=XVH_setKlimaNum[6];
mind_bool[472]:=ComSCADA2;
mind_bool[473]:=ErrCommScada2;
mind_bool[474]:=ComSCADA3;
mind_bool[475]:=Circ_Vpis_Dnevne_energija_scada1;
mind_bool[476]:=Circ_Vpis_Dnevne_energija_scada2;
mind_bool[477]:=Circ_Vpis_Tedenska_energija_scada1;
mind_bool[478]:=Circ_Vpis_Tedenska_energija_scada2;
mind_bool[479]:=Circ_Vpis_Mesecna_energija_scada1;
mind_bool[480]:=Circ_Vpis_Mesecna_energija_scada2;
(*Branje INT*)
(**)
mind[0]:=DateTime.Dan;
mind[1]:=DateTime.Leto;
mind[2]:=DateTime.Mesec;
mind[3]:=DateTime.Minuta;
mind[4]:=DateTime.Sekunda;
mind[5]:=DateTime.Ura;
mind[6]:=ErrorComCirc[1].Code[10];
mind[7]:=ErrorComCirc[1].Code[11];
mind[8]:=ErrorComCirc[1].Code[12];
mind[9]:=ErrorComCirc[1].Code[13];
mind[10]:=ErrorComCirc[1].Code[14];
mind[11]:=ErrorComCirc[1].Code[15];
mind[12]:=ErrorComCirc[1].Code[1];
mind[13]:=ErrorComCirc[1].Code[2];
mind[14]:=ErrorComCirc[1].Code[3];
mind[15]:=ErrorComCirc[1].Code[4];
mind[16]:=ErrorComCirc[1].Code[5];
mind[17]:=ErrorComCirc[1].Code[6];
mind[18]:=ErrorComCirc[1].Code[7];
mind[19]:=ErrorComCirc[1].Code[8];
mind[20]:=ErrorComCirc[1].Code[9];
mind[21]:=ErrorComCirc[1].Status;
mind[22]:=ErrorComCirc[2].Code[10];
mind[23]:=ErrorComCirc[2].Code[11];
mind[24]:=ErrorComCirc[2].Code[12];
mind[25]:=ErrorComCirc[2].Code[13];
mind[26]:=ErrorComCirc[2].Code[14];
mind[27]:=ErrorComCirc[2].Code[15];
mind[28]:=ErrorComCirc[2].Code[1];
mind[29]:=ErrorComCirc[2].Code[2];
mind[30]:=ErrorComCirc[2].Code[3];
mind[31]:=ErrorComCirc[2].Code[4];
mind[32]:=ErrorComCirc[2].Code[5];
mind[33]:=ErrorComCirc[2].Code[6];
mind[34]:=ErrorComCirc[2].Code[7];
mind[35]:=ErrorComCirc[2].Code[8];
mind[36]:=ErrorComCirc[2].Code[9];
mind[37]:=ErrorComCirc[2].Status;
mind[38]:=ErrorComCirc[3].Code[10];
mind[39]:=ErrorComCirc[3].Code[11];
mind[40]:=ErrorComCirc[3].Code[12];
mind[41]:=ErrorComCirc[3].Code[13];
mind[42]:=ErrorComCirc[3].Code[14];
mind[43]:=ErrorComCirc[3].Code[15];
mind[44]:=ErrorComCirc[3].Code[1];
mind[45]:=ErrorComCirc[3].Code[2];
mind[46]:=ErrorComCirc[3].Code[3];
mind[47]:=ErrorComCirc[3].Code[4];
mind[48]:=ErrorComCirc[3].Code[5];
mind[49]:=ErrorComCirc[3].Code[6];
mind[50]:=ErrorComCirc[3].Code[7];
mind[51]:=ErrorComCirc[3].Code[8];
mind[52]:=ErrorComCirc[3].Code[9];
mind[53]:=ErrorComCirc[3].Status;
mind[54]:=ErrorComCirc[4].Code[10];
mind[55]:=ErrorComCirc[4].Code[11];
mind[56]:=ErrorComCirc[4].Code[12];
mind[57]:=ErrorComCirc[4].Code[13];
mind[58]:=ErrorComCirc[4].Code[14];
mind[59]:=ErrorComCirc[4].Code[15];
mind[60]:=ErrorComCirc[4].Code[1];
mind[61]:=ErrorComCirc[4].Code[2];
mind[62]:=ErrorComCirc[4].Code[3];
mind[63]:=ErrorComCirc[4].Code[4];
mind[64]:=ErrorComCirc[4].Code[5];
mind[65]:=ErrorComCirc[4].Code[6];
mind[66]:=ErrorComCirc[4].Code[7];
mind[67]:=ErrorComCirc[4].Code[8];
mind[68]:=ErrorComCirc[4].Code[9];
mind[69]:=ErrorComCirc[4].Status;
mind[70]:=ErrorComCirc[5].Code[10];
mind[71]:=ErrorComCirc[5].Code[11];
mind[72]:=ErrorComCirc[5].Code[12];
mind[73]:=ErrorComCirc[5].Code[13];
mind[74]:=ErrorComCirc[5].Code[14];
mind[75]:=ErrorComCirc[5].Code[15];
mind[76]:=ErrorComCirc[5].Code[1];
mind[77]:=ErrorComCirc[5].Code[2];
mind[78]:=ErrorComCirc[5].Code[3];
mind[79]:=ErrorComCirc[5].Code[4];
mind[80]:=ErrorComCirc[5].Code[5];
mind[81]:=ErrorComCirc[5].Code[6];
mind[82]:=ErrorComCirc[5].Code[7];
mind[83]:=ErrorComCirc[5].Code[8];
mind[84]:=ErrorComCirc[5].Code[9];
mind[85]:=ErrorComCirc[5].Status;
mind[86]:=ErrorComKlima[1].Code[10];
mind[87]:=ErrorComKlima[1].Code[11];
mind[88]:=ErrorComKlima[1].Code[12];
mind[89]:=ErrorComKlima[1].Code[13];
mind[90]:=ErrorComKlima[1].Code[14];
mind[91]:=ErrorComKlima[1].Code[15];
mind[92]:=ErrorComKlima[1].Code[1];
mind[93]:=ErrorComKlima[1].Code[2];
mind[94]:=ErrorComKlima[1].Code[3];
mind[95]:=ErrorComKlima[1].Code[4];
mind[96]:=ErrorComKlima[1].Code[5];
mind[97]:=ErrorComKlima[1].Code[6];
mind[98]:=ErrorComKlima[1].Code[7];
mind[99]:=ErrorComKlima[1].Code[8];
mind[100]:=ErrorComKlima[1].Code[9];
mind[101]:=ErrorComKlima[1].Status;
mind[102]:=ErrorComKlima[2].Code[10];
mind[103]:=ErrorComKlima[2].Code[11];
mind[104]:=ErrorComKlima[2].Code[12];
mind[105]:=ErrorComKlima[2].Code[13];
mind[106]:=ErrorComKlima[2].Code[14];
mind[107]:=ErrorComKlima[2].Code[15];
mind[108]:=ErrorComKlima[2].Code[1];
mind[109]:=ErrorComKlima[2].Code[2];
mind[110]:=ErrorComKlima[2].Code[3];
mind[111]:=ErrorComKlima[2].Code[4];
mind[112]:=ErrorComKlima[2].Code[5];
mind[113]:=ErrorComKlima[2].Code[6];
mind[114]:=ErrorComKlima[2].Code[7];
mind[115]:=ErrorComKlima[2].Code[8];
mind[116]:=ErrorComKlima[2].Code[9];
mind[117]:=ErrorComKlima[2].Status;
mind[118]:=ErrorComKlima[3].Code[10];
mind[119]:=ErrorComKlima[3].Code[11];
mind[120]:=ErrorComKlima[3].Code[12];
mind[121]:=ErrorComKlima[3].Code[13];
mind[122]:=ErrorComKlima[3].Code[14];
mind[123]:=ErrorComKlima[3].Code[15];
mind[124]:=ErrorComKlima[3].Code[1];
mind[125]:=ErrorComKlima[3].Code[2];
mind[126]:=ErrorComKlima[3].Code[3];
mind[127]:=ErrorComKlima[3].Code[4];
mind[128]:=ErrorComKlima[3].Code[5];
mind[129]:=ErrorComKlima[3].Code[6];
mind[130]:=ErrorComKlima[3].Code[7];
mind[131]:=ErrorComKlima[3].Code[8];
mind[132]:=ErrorComKlima[3].Code[9];
mind[133]:=ErrorComKlima[3].Status;
mind[134]:=ErrorComKlima[4].Code[10];
mind[135]:=ErrorComKlima[4].Code[11];
mind[136]:=ErrorComKlima[4].Code[12];
mind[137]:=ErrorComKlima[4].Code[13];
mind[138]:=ErrorComKlima[4].Code[14];
mind[139]:=ErrorComKlima[4].Code[15];
mind[140]:=ErrorComKlima[4].Code[1];
mind[141]:=ErrorComKlima[4].Code[2];
mind[142]:=ErrorComKlima[4].Code[3];
mind[143]:=ErrorComKlima[4].Code[4];
mind[144]:=ErrorComKlima[4].Code[5];
mind[145]:=ErrorComKlima[4].Code[6];
mind[146]:=ErrorComKlima[4].Code[7];
mind[147]:=ErrorComKlima[4].Code[8];
mind[148]:=ErrorComKlima[4].Code[9];
mind[149]:=ErrorComKlima[4].Status;
mind[150]:=ErrorComKlima[5].Code[10];
mind[151]:=ErrorComKlima[5].Code[11];
mind[152]:=ErrorComKlima[5].Code[12];
mind[153]:=ErrorComKlima[5].Code[13];
mind[154]:=ErrorComKlima[5].Code[14];
mind[155]:=ErrorComKlima[5].Code[15];
mind[156]:=ErrorComKlima[5].Code[1];
mind[157]:=ErrorComKlima[5].Code[2];
mind[158]:=ErrorComKlima[5].Code[3];
mind[159]:=ErrorComKlima[5].Code[4];
mind[160]:=ErrorComKlima[5].Code[5];
mind[161]:=ErrorComKlima[5].Code[6];
mind[162]:=ErrorComKlima[5].Code[7];
mind[163]:=ErrorComKlima[5].Code[8];
mind[164]:=ErrorComKlima[5].Code[9];
mind[165]:=ErrorComKlima[5].Status;
mind[166]:=ErrorComKlima[6].Code[10];
mind[167]:=ErrorComKlima[6].Code[11];
mind[168]:=ErrorComKlima[6].Code[12];
mind[169]:=ErrorComKlima[6].Code[13];
mind[170]:=ErrorComKlima[6].Code[14];
mind[171]:=ErrorComKlima[6].Code[15];
mind[172]:=ErrorComKlima[6].Code[1];
mind[173]:=ErrorComKlima[6].Code[2];
mind[174]:=ErrorComKlima[6].Code[3];
mind[175]:=ErrorComKlima[6].Code[4];
mind[176]:=ErrorComKlima[6].Code[5];
mind[177]:=ErrorComKlima[6].Code[6];
mind[178]:=ErrorComKlima[6].Code[7];
mind[179]:=ErrorComKlima[6].Code[8];
mind[180]:=ErrorComKlima[6].Code[9];
mind[181]:=ErrorComKlima[6].Status;
mind[182]:=Klima[1].GrelecStatus;
mind[183]:=Klima[1].IzhodniVentStatus;
mind[184]:=Klima[1].KompresorStatus;
mind[185]:=Klima[1].VlazilecStatus;
mind[186]:=Klima[2].GrelecStatus;
mind[187]:=Klima[2].IzhodniVentStatus;
mind[188]:=Klima[2].KompresorStatus;
mind[189]:=Klima[2].VlazilecStatus;
mind[190]:=Klima[3].GrelecStatus;
mind[191]:=Klima[3].IzhodniVentStatus;
mind[192]:=Klima[3].KompresorStatus;
mind[193]:=Klima[3].VlazilecStatus;
mind[194]:=KlimaGal.GrelecStatus;
mind[195]:=KlimaGal.IzhodniVentStatus;
mind[196]:=KlimaGal.KompresorStatus;
mind[197]:=KlimaGal.VlazilecStatus;
mind[198]:=Qstanje[10];
mind[199]:=Qstanje[1];
mind[200]:=Qstanje[2];
mind[201]:=Qstanje[3];
mind[202]:=Qstanje[4];
mind[203]:=Qstanje[5];
mind[204]:=Qstanje[6];
mind[205]:=Qstanje[7];
mind[206]:=Qstanje[8];
mind[207]:=Qstanje[9];
mind[208]:=UserCurrentLevel;
mind[209]:=XVH_CircNumber;
mind[210]:=XVH_KlimaNumber;
mind[211]:=XVH_PripravaVodeStat[1];
mind[212]:=XVH_PripravaVodeStat[2];
mind[213]:=XVH_UPSstatus;
mind[214]:=XVH_VlazilecStatus[1];
mind[215]:=XVH_VlazilecStatus[2];
mind[216]:=XVH_VlazilecStatus[3];
mind[217]:=XVHnum[10];
mind[218]:=XVHnum[11];
mind[219]:=XVHnum[12];
mind[220]:=XVHnum[13];
mind[221]:=XVHnum[14];
mind[222]:=XVHnum[1];
mind[223]:=XVHnum[2];
mind[224]:=XVHnum[3];
mind[225]:=XVHnum[4];
mind[226]:=XVHnum[5];
mind[227]:=XVHnum[6];
mind[228]:=XVHnum[7];
mind[229]:=XVHnum[8];
mind[230]:=XVHnum[9];
mind[231]:=kom_nast_cas_izpada;
(*Branje UINT*)
(**)
(*Branje LONG*)
(**)
(*Branje REAL*)
(**)
Read_Real(rVar:=Circ[1].CosFi_III,lo:=4000,hi:=4001);
Read_Real(rVar:=Circ[1].DelovnaEnergija,lo:=4002,hi:=4003);
Read_Real(rVar:=Circ[1].DelovnaMoc_III,lo:=4004,hi:=4005);
Read_Real(rVar:=Circ[1].DelovnaMoc_L1,lo:=4006,hi:=4007);
Read_Real(rVar:=Circ[1].DelovnaMoc_L2,lo:=4008,hi:=4009);
Read_Real(rVar:=Circ[1].DelovnaMoc_L3,lo:=4010,hi:=4011);
Read_Real(rVar:=Circ[1].Frekvenca_L1,lo:=4012,hi:=4013);
Read_Real(rVar:=Circ[1].InduktivnaEnergija,lo:=4014,hi:=4015);
Read_Real(rVar:=Circ[1].InduktivnaMoc_III,lo:=4016,hi:=4017);
Read_Real(rVar:=Circ[1].JalovaMoc_L1,lo:=4018,hi:=4019);
Read_Real(rVar:=Circ[1].JalovaMoc_L2,lo:=4020,hi:=4021);
Read_Real(rVar:=Circ[1].JalovaMoc_L3,lo:=4022,hi:=4023);
Read_Real(rVar:=Circ[1].KapacitivnaEnergija,lo:=4024,hi:=4025);
Read_Real(rVar:=Circ[1].KapacitivnaMoc_III,lo:=4026,hi:=4027);
Read_Real(rVar:=Circ[1].MaximumDemand,lo:=4028,hi:=4029);
Read_Real(rVar:=Circ[1].Napetost_L1_L2,lo:=4030,hi:=4031);
Read_Real(rVar:=Circ[1].Napetost_L1_N,lo:=4032,hi:=4033);
Read_Real(rVar:=Circ[1].Napetost_L2_L3,lo:=4034,hi:=4035);
Read_Real(rVar:=Circ[1].Napetost_L2_N,lo:=4036,hi:=4037);
Read_Real(rVar:=Circ[1].Napetost_L3_L1,lo:=4038,hi:=4039);
Read_Real(rVar:=Circ[1].Napetost_L3_N,lo:=4040,hi:=4041);
Read_Real(rVar:=Circ[1].NavideznaMoc_III,lo:=4042,hi:=4043);
Read_Real(rVar:=Circ[1].NicelniTok,lo:=4044,hi:=4045);
Read_Real(rVar:=Circ[1].PowerFactor_III,lo:=4046,hi:=4047);
Read_Real(rVar:=Circ[1].PowerFactor_L1,lo:=4048,hi:=4049);
Read_Real(rVar:=Circ[1].PowerFactor_L2,lo:=4050,hi:=4051);
Read_Real(rVar:=Circ[1].PowerFactor_L3,lo:=4052,hi:=4053);
Read_Real(rVar:=Circ[1].THDI_L1,lo:=4054,hi:=4055);
Read_Real(rVar:=Circ[1].THDI_L2,lo:=4056,hi:=4057);
Read_Real(rVar:=Circ[1].THDI_L3,lo:=4058,hi:=4059);
Read_Real(rVar:=Circ[1].THDV_L1,lo:=4060,hi:=4061);
Read_Real(rVar:=Circ[1].THDV_L2,lo:=4062,hi:=4063);
Read_Real(rVar:=Circ[1].THDV_L3,lo:=4064,hi:=4065);
Read_Real(rVar:=Circ[1].Tok_L1,lo:=4066,hi:=4067);
Read_Real(rVar:=Circ[1].Tok_L2,lo:=4068,hi:=4069);
Read_Real(rVar:=Circ[1].Tok_L3,lo:=4070,hi:=4071);
Read_Real(rVar:=Circ[1].TokPovprecje_III,lo:=4072,hi:=4073);
Read_Real(rVar:=Circ[2].CosFi_III,lo:=4074,hi:=4075);
Read_Real(rVar:=Circ[2].DelovnaEnergija,lo:=4076,hi:=4077);
Read_Real(rVar:=Circ[2].DelovnaMoc_III,lo:=4078,hi:=4079);
Read_Real(rVar:=Circ[2].DelovnaMoc_L1,lo:=4080,hi:=4081);
Read_Real(rVar:=Circ[2].DelovnaMoc_L2,lo:=4082,hi:=4083);
Read_Real(rVar:=Circ[2].DelovnaMoc_L3,lo:=4084,hi:=4085);
Read_Real(rVar:=Circ[2].Frekvenca_L1,lo:=4086,hi:=4087);
Read_Real(rVar:=Circ[2].InduktivnaEnergija,lo:=4088,hi:=4089);
Read_Real(rVar:=Circ[2].InduktivnaMoc_III,lo:=4090,hi:=4091);
Read_Real(rVar:=Circ[2].JalovaMoc_L1,lo:=4092,hi:=4093);
Read_Real(rVar:=Circ[2].JalovaMoc_L2,lo:=4094,hi:=4095);
Read_Real(rVar:=Circ[2].JalovaMoc_L3,lo:=4096,hi:=4097);
Read_Real(rVar:=Circ[2].KapacitivnaEnergija,lo:=4098,hi:=4099);
Read_Real(rVar:=Circ[2].KapacitivnaMoc_III,lo:=4100,hi:=4101);
Read_Real(rVar:=Circ[2].MaximumDemand,lo:=4102,hi:=4103);
Read_Real(rVar:=Circ[2].Napetost_L1_L2,lo:=4104,hi:=4105);
Read_Real(rVar:=Circ[2].Napetost_L1_N,lo:=4106,hi:=4107);
Read_Real(rVar:=Circ[2].Napetost_L2_L3,lo:=4108,hi:=4109);
Read_Real(rVar:=Circ[2].Napetost_L2_N,lo:=4110,hi:=4111);
Read_Real(rVar:=Circ[2].Napetost_L3_L1,lo:=4112,hi:=4113);
Read_Real(rVar:=Circ[2].Napetost_L3_N,lo:=4114,hi:=4115);
Read_Real(rVar:=Circ[2].NavideznaMoc_III,lo:=4116,hi:=4117);
Read_Real(rVar:=Circ[2].NicelniTok,lo:=4118,hi:=4119);
Read_Real(rVar:=Circ[2].PowerFactor_III,lo:=4120,hi:=4121);
Read_Real(rVar:=Circ[2].PowerFactor_L1,lo:=4122,hi:=4123);
Read_Real(rVar:=Circ[2].PowerFactor_L2,lo:=4124,hi:=4125);
Read_Real(rVar:=Circ[2].PowerFactor_L3,lo:=4126,hi:=4127);
Read_Real(rVar:=Circ[2].THDI_L1,lo:=4128,hi:=4129);
Read_Real(rVar:=Circ[2].THDI_L2,lo:=4130,hi:=4131);
Read_Real(rVar:=Circ[2].THDI_L3,lo:=4132,hi:=4133);
Read_Real(rVar:=Circ[2].THDV_L1,lo:=4134,hi:=4135);
Read_Real(rVar:=Circ[2].THDV_L2,lo:=4136,hi:=4137);
Read_Real(rVar:=Circ[2].THDV_L3,lo:=4138,hi:=4139);
Read_Real(rVar:=Circ[2].Tok_L1,lo:=4140,hi:=4141);
Read_Real(rVar:=Circ[2].Tok_L2,lo:=4142,hi:=4143);
Read_Real(rVar:=Circ[2].Tok_L3,lo:=4144,hi:=4145);
Read_Real(rVar:=Circ[2].TokPovprecje_III,lo:=4146,hi:=4147);
Read_Real(rVar:=Circ[3].CosFi_III,lo:=4148,hi:=4149);
Read_Real(rVar:=Circ[3].DelovnaEnergija,lo:=4150,hi:=4151);
Read_Real(rVar:=Circ[3].DelovnaMoc_III,lo:=4152,hi:=4153);
Read_Real(rVar:=Circ[3].DelovnaMoc_L1,lo:=4154,hi:=4155);
Read_Real(rVar:=Circ[3].DelovnaMoc_L2,lo:=4156,hi:=4157);
Read_Real(rVar:=Circ[3].DelovnaMoc_L3,lo:=4158,hi:=4159);
Read_Real(rVar:=Circ[3].Frekvenca_L1,lo:=4160,hi:=4161);
Read_Real(rVar:=Circ[3].InduktivnaEnergija,lo:=4162,hi:=4163);
Read_Real(rVar:=Circ[3].InduktivnaMoc_III,lo:=4164,hi:=4165);
Read_Real(rVar:=Circ[3].JalovaMoc_L1,lo:=4166,hi:=4167);
Read_Real(rVar:=Circ[3].JalovaMoc_L2,lo:=4168,hi:=4169);
Read_Real(rVar:=Circ[3].JalovaMoc_L3,lo:=4170,hi:=4171);
Read_Real(rVar:=Circ[3].KapacitivnaEnergija,lo:=4172,hi:=4173);
Read_Real(rVar:=Circ[3].KapacitivnaMoc_III,lo:=4174,hi:=4175);
Read_Real(rVar:=Circ[3].MaximumDemand,lo:=4176,hi:=4177);
Read_Real(rVar:=Circ[3].Napetost_L1_L2,lo:=4178,hi:=4179);
Read_Real(rVar:=Circ[3].Napetost_L1_N,lo:=4180,hi:=4181);
Read_Real(rVar:=Circ[3].Napetost_L2_L3,lo:=4182,hi:=4183);
Read_Real(rVar:=Circ[3].Napetost_L2_N,lo:=4184,hi:=4185);
Read_Real(rVar:=Circ[3].Napetost_L3_L1,lo:=4186,hi:=4187);
Read_Real(rVar:=Circ[3].Napetost_L3_N,lo:=4188,hi:=4189);
Read_Real(rVar:=Circ[3].NavideznaMoc_III,lo:=4190,hi:=4191);
Read_Real(rVar:=Circ[3].NicelniTok,lo:=4192,hi:=4193);
Read_Real(rVar:=Circ[3].PowerFactor_III,lo:=4194,hi:=4195);
Read_Real(rVar:=Circ[3].PowerFactor_L1,lo:=4196,hi:=4197);
Read_Real(rVar:=Circ[3].PowerFactor_L2,lo:=4198,hi:=4199);
Read_Real(rVar:=Circ[3].PowerFactor_L3,lo:=4200,hi:=4201);
Read_Real(rVar:=Circ[3].THDI_L1,lo:=4202,hi:=4203);
Read_Real(rVar:=Circ[3].THDI_L2,lo:=4204,hi:=4205);
Read_Real(rVar:=Circ[3].THDI_L3,lo:=4206,hi:=4207);
Read_Real(rVar:=Circ[3].THDV_L1,lo:=4208,hi:=4209);
Read_Real(rVar:=Circ[3].THDV_L2,lo:=4210,hi:=4211);
Read_Real(rVar:=Circ[3].THDV_L3,lo:=4212,hi:=4213);
Read_Real(rVar:=Circ[3].Tok_L1,lo:=4214,hi:=4215);
Read_Real(rVar:=Circ[3].Tok_L2,lo:=4216,hi:=4217);
Read_Real(rVar:=Circ[3].Tok_L3,lo:=4218,hi:=4219);
Read_Real(rVar:=Circ[3].TokPovprecje_III,lo:=4220,hi:=4221);
Read_Real(rVar:=Circ[4].CosFi_III,lo:=4222,hi:=4223);
Read_Real(rVar:=Circ[4].DelovnaEnergija,lo:=4224,hi:=4225);
Read_Real(rVar:=Circ[4].DelovnaMoc_III,lo:=4226,hi:=4227);
Read_Real(rVar:=Circ[4].DelovnaMoc_L1,lo:=4228,hi:=4229);
Read_Real(rVar:=Circ[4].DelovnaMoc_L2,lo:=4230,hi:=4231);
Read_Real(rVar:=Circ[4].DelovnaMoc_L3,lo:=4232,hi:=4233);
Read_Real(rVar:=Circ[4].Frekvenca_L1,lo:=4234,hi:=4235);
Read_Real(rVar:=Circ[4].InduktivnaEnergija,lo:=4236,hi:=4237);
Read_Real(rVar:=Circ[4].InduktivnaMoc_III,lo:=4238,hi:=4239);
Read_Real(rVar:=Circ[4].JalovaMoc_L1,lo:=4240,hi:=4241);
Read_Real(rVar:=Circ[4].JalovaMoc_L2,lo:=4242,hi:=4243);
Read_Real(rVar:=Circ[4].JalovaMoc_L3,lo:=4244,hi:=4245);
Read_Real(rVar:=Circ[4].KapacitivnaEnergija,lo:=4246,hi:=4247);
Read_Real(rVar:=Circ[4].KapacitivnaMoc_III,lo:=4248,hi:=4249);
Read_Real(rVar:=Circ[4].MaximumDemand,lo:=4250,hi:=4251);
Read_Real(rVar:=Circ[4].Napetost_L1_L2,lo:=4252,hi:=4253);
Read_Real(rVar:=Circ[4].Napetost_L1_N,lo:=4254,hi:=4255);
Read_Real(rVar:=Circ[4].Napetost_L2_L3,lo:=4256,hi:=4257);
Read_Real(rVar:=Circ[4].Napetost_L2_N,lo:=4258,hi:=4259);
Read_Real(rVar:=Circ[4].Napetost_L3_L1,lo:=4260,hi:=4261);
Read_Real(rVar:=Circ[4].Napetost_L3_N,lo:=4262,hi:=4263);
Read_Real(rVar:=Circ[4].NavideznaMoc_III,lo:=4264,hi:=4265);
Read_Real(rVar:=Circ[4].NicelniTok,lo:=4266,hi:=4267);
Read_Real(rVar:=Circ[4].PowerFactor_III,lo:=4268,hi:=4269);
Read_Real(rVar:=Circ[4].PowerFactor_L1,lo:=4270,hi:=4271);
Read_Real(rVar:=Circ[4].PowerFactor_L2,lo:=4272,hi:=4273);
Read_Real(rVar:=Circ[4].PowerFactor_L3,lo:=4274,hi:=4275);
Read_Real(rVar:=Circ[4].THDI_L1,lo:=4276,hi:=4277);
Read_Real(rVar:=Circ[4].THDI_L2,lo:=4278,hi:=4279);
Read_Real(rVar:=Circ[4].THDI_L3,lo:=4280,hi:=4281);
Read_Real(rVar:=Circ[4].THDV_L1,lo:=4282,hi:=4283);
Read_Real(rVar:=Circ[4].THDV_L2,lo:=4284,hi:=4285);
Read_Real(rVar:=Circ[4].THDV_L3,lo:=4286,hi:=4287);
Read_Real(rVar:=Circ[4].Tok_L1,lo:=4288,hi:=4289);
Read_Real(rVar:=Circ[4].Tok_L2,lo:=4290,hi:=4291);
Read_Real(rVar:=Circ[4].Tok_L3,lo:=4292,hi:=4293);
Read_Real(rVar:=Circ[4].TokPovprecje_III,lo:=4294,hi:=4295);
Read_Real(rVar:=Circutor.CosFi_III,lo:=4296,hi:=4297);
Read_Real(rVar:=Circutor.DelovnaEnergija,lo:=4298,hi:=4299);
Read_Real(rVar:=Circutor.DelovnaMoc_III,lo:=4300,hi:=4301);
Read_Real(rVar:=Circutor.DelovnaMoc_L1,lo:=4302,hi:=4303);
Read_Real(rVar:=Circutor.DelovnaMoc_L2,lo:=4304,hi:=4305);
Read_Real(rVar:=Circutor.DelovnaMoc_L3,lo:=4306,hi:=4307);
Read_Real(rVar:=Circutor.Frekvenca_L1,lo:=4308,hi:=4309);
Read_Real(rVar:=Circutor.InduktivnaEnergija,lo:=4310,hi:=4311);
Read_Real(rVar:=Circutor.InduktivnaMoc_III,lo:=4312,hi:=4313);
Read_Real(rVar:=Circutor.JalovaMoc_L1,lo:=4314,hi:=4315);
Read_Real(rVar:=Circutor.JalovaMoc_L2,lo:=4316,hi:=4317);
Read_Real(rVar:=Circutor.JalovaMoc_L3,lo:=4318,hi:=4319);
Read_Real(rVar:=Circutor.KapacitivnaEnergija,lo:=4320,hi:=4321);
Read_Real(rVar:=Circutor.KapacitivnaMoc_III,lo:=4322,hi:=4323);
Read_Real(rVar:=Circutor.MaximumDemand,lo:=4324,hi:=4325);
Read_Real(rVar:=Circutor.Napetost_L1_L2,lo:=4326,hi:=4327);
Read_Real(rVar:=Circutor.Napetost_L1_N,lo:=4328,hi:=4329);
Read_Real(rVar:=Circutor.Napetost_L2_L3,lo:=4330,hi:=4331);
Read_Real(rVar:=Circutor.Napetost_L2_N,lo:=4332,hi:=4333);
Read_Real(rVar:=Circutor.Napetost_L3_L1,lo:=4334,hi:=4335);
Read_Real(rVar:=Circutor.Napetost_L3_N,lo:=4336,hi:=4337);
Read_Real(rVar:=Circutor.NavideznaMoc_III,lo:=4338,hi:=4339);
Read_Real(rVar:=Circutor.NicelniTok,lo:=4340,hi:=4341);
Read_Real(rVar:=Circutor.PowerFactor_III,lo:=4342,hi:=4343);
Read_Real(rVar:=Circutor.PowerFactor_L1,lo:=4344,hi:=4345);
Read_Real(rVar:=Circutor.PowerFactor_L2,lo:=4346,hi:=4347);
Read_Real(rVar:=Circutor.PowerFactor_L3,lo:=4348,hi:=4349);
Read_Real(rVar:=Circutor.THDI_L1,lo:=4350,hi:=4351);
Read_Real(rVar:=Circutor.THDI_L2,lo:=4352,hi:=4353);
Read_Real(rVar:=Circutor.THDI_L3,lo:=4354,hi:=4355);
Read_Real(rVar:=Circutor.THDV_L1,lo:=4356,hi:=4357);
Read_Real(rVar:=Circutor.THDV_L2,lo:=4358,hi:=4359);
Read_Real(rVar:=Circutor.THDV_L3,lo:=4360,hi:=4361);
Read_Real(rVar:=Circutor.Tok_L1,lo:=4362,hi:=4363);
Read_Real(rVar:=Circutor.Tok_L2,lo:=4364,hi:=4365);
Read_Real(rVar:=Circutor.Tok_L3,lo:=4366,hi:=4367);
Read_Real(rVar:=Circutor.TokPovprecje_III,lo:=4368,hi:=4369);
Read_Real(rVar:=Klima[1].NastMaxTemp,lo:=4370,hi:=4371);
Read_Real(rVar:=Klima[1].NastMaxVlaznost,lo:=4372,hi:=4373);
Read_Real(rVar:=Klima[1].NastMinTemp,lo:=4374,hi:=4375);
Read_Real(rVar:=Klima[1].NastMinVlaznost,lo:=4376,hi:=4377);
Read_Real(rVar:=Klima[1].NastTempProstora,lo:=4378,hi:=4379);
Read_Real(rVar:=Klima[1].NastVlaznost,lo:=4380,hi:=4381);
Read_Real(rVar:=Klima[1].ObratovalneUre,lo:=4382,hi:=4383);
Read_Real(rVar:=Klima[1].TemperaturaProstora,lo:=4384,hi:=4385);
Read_Real(rVar:=Klima[1].TempIzpihanegaZraka,lo:=4386,hi:=4387);
Read_Real(rVar:=Klima[1].TempPovratneVode,lo:=4388,hi:=4389);
Read_Real(rVar:=Klima[1].VlaznostProstora,lo:=4390,hi:=4391);
Read_Real(rVar:=Klima[1].ZunanjaTemp,lo:=4392,hi:=4393);
Read_Real(rVar:=Klima[2].NastMaxTemp,lo:=4394,hi:=4395);
Read_Real(rVar:=Klima[2].NastMaxVlaznost,lo:=4396,hi:=4397);
Read_Real(rVar:=Klima[2].NastMinTemp,lo:=4398,hi:=4399);
Read_Real(rVar:=Klima[2].NastMinVlaznost,lo:=4400,hi:=4401);
Read_Real(rVar:=Klima[2].NastTempProstora,lo:=4402,hi:=4403);
Read_Real(rVar:=Klima[2].NastVlaznost,lo:=4404,hi:=4405);
Read_Real(rVar:=Klima[2].ObratovalneUre,lo:=4406,hi:=4407);
Read_Real(rVar:=Klima[2].TemperaturaProstora,lo:=4408,hi:=4409);
Read_Real(rVar:=Klima[2].TempIzpihanegaZraka,lo:=4410,hi:=4411);
Read_Real(rVar:=Klima[2].TempPovratneVode,lo:=4412,hi:=4413);
Read_Real(rVar:=Klima[2].VlaznostProstora,lo:=4414,hi:=4415);
Read_Real(rVar:=Klima[2].ZunanjaTemp,lo:=4416,hi:=4417);
Read_Real(rVar:=Klima[3].NastMaxTemp,lo:=4418,hi:=4419);
Read_Real(rVar:=Klima[3].NastMaxVlaznost,lo:=4420,hi:=4421);
Read_Real(rVar:=Klima[3].NastMinTemp,lo:=4422,hi:=4423);
Read_Real(rVar:=Klima[3].NastMinVlaznost,lo:=4424,hi:=4425);
Read_Real(rVar:=Klima[3].NastTempProstora,lo:=4426,hi:=4427);
Read_Real(rVar:=Klima[3].NastVlaznost,lo:=4428,hi:=4429);
Read_Real(rVar:=Klima[3].ObratovalneUre,lo:=4430,hi:=4431);
Read_Real(rVar:=Klima[3].TemperaturaProstora,lo:=4432,hi:=4433);
Read_Real(rVar:=Klima[3].TempIzpihanegaZraka,lo:=4434,hi:=4435);
Read_Real(rVar:=Klima[3].TempPovratneVode,lo:=4436,hi:=4437);
Read_Real(rVar:=Klima[3].VlaznostProstora,lo:=4438,hi:=4439);
Read_Real(rVar:=Klima[3].ZunanjaTemp,lo:=4440,hi:=4441);
Read_Real(rVar:=KlimaGal.NastMaxTemp,lo:=4442,hi:=4443);
Read_Real(rVar:=KlimaGal.NastMaxVlaznost,lo:=4444,hi:=4445);
Read_Real(rVar:=KlimaGal.NastMinTemp,lo:=4446,hi:=4447);
Read_Real(rVar:=KlimaGal.NastMinVlaznost,lo:=4448,hi:=4449);
Read_Real(rVar:=KlimaGal.NastTempProstora,lo:=4450,hi:=4451);
Read_Real(rVar:=KlimaGal.NastVlaznost,lo:=4452,hi:=4453);
Read_Real(rVar:=KlimaGal.ObratovalneUre,lo:=4454,hi:=4455);
Read_Real(rVar:=KlimaGal.TemperaturaProstora,lo:=4456,hi:=4457);
Read_Real(rVar:=KlimaGal.TempIzpihanegaZraka,lo:=4458,hi:=4459);
Read_Real(rVar:=KlimaGal.TempPovratneVode,lo:=4460,hi:=4461);
Read_Real(rVar:=KlimaGal.VlaznostProstora,lo:=4462,hi:=4463);
Read_Real(rVar:=KlimaGal.ZunanjaTemp,lo:=4464,hi:=4465);
Read_Real(rVar:=SenzorTemp[10],lo:=4466,hi:=4467);
Read_Real(rVar:=SenzorTemp[11],lo:=4468,hi:=4469);
Read_Real(rVar:=SenzorTemp[12],lo:=4470,hi:=4471);
Read_Real(rVar:=SenzorTemp[13],lo:=4472,hi:=4473);
Read_Real(rVar:=SenzorTemp[14],lo:=4474,hi:=4475);
Read_Real(rVar:=SenzorTemp[15],lo:=4476,hi:=4477);
Read_Real(rVar:=SenzorTemp[16],lo:=4478,hi:=4479);
Read_Real(rVar:=SenzorTemp[17],lo:=4480,hi:=4481);
Read_Real(rVar:=SenzorTemp[18],lo:=4482,hi:=4483);
Read_Real(rVar:=SenzorTemp[19],lo:=4484,hi:=4485);
Read_Real(rVar:=SenzorTemp[1],lo:=4486,hi:=4487);
Read_Real(rVar:=SenzorTemp[2],lo:=4488,hi:=4489);
Read_Real(rVar:=SenzorTemp[3],lo:=4490,hi:=4491);
Read_Real(rVar:=SenzorTemp[4],lo:=4492,hi:=4493);
Read_Real(rVar:=SenzorTemp[5],lo:=4494,hi:=4495);
Read_Real(rVar:=SenzorTemp[6],lo:=4496,hi:=4497);
Read_Real(rVar:=SenzorTemp[7],lo:=4498,hi:=4499);
Read_Real(rVar:=SenzorTemp[8],lo:=4500,hi:=4501);
Read_Real(rVar:=SenzorTemp[9],lo:=4502,hi:=4503);
Read_Real(rVar:=SenzorVlaga[10],lo:=4504,hi:=4505);
Read_Real(rVar:=SenzorVlaga[11],lo:=4506,hi:=4507);
Read_Real(rVar:=SenzorVlaga[12],lo:=4508,hi:=4509);
Read_Real(rVar:=SenzorVlaga[13],lo:=4510,hi:=4511);
Read_Real(rVar:=SenzorVlaga[14],lo:=4512,hi:=4513);
Read_Real(rVar:=SenzorVlaga[15],lo:=4514,hi:=4515);
Read_Real(rVar:=SenzorVlaga[16],lo:=4516,hi:=4517);
Read_Real(rVar:=SenzorVlaga[17],lo:=4518,hi:=4519);
Read_Real(rVar:=SenzorVlaga[18],lo:=4520,hi:=4521);
Read_Real(rVar:=SenzorVlaga[19],lo:=4522,hi:=4523);
Read_Real(rVar:=SenzorVlaga[1],lo:=4524,hi:=4525);
Read_Real(rVar:=SenzorVlaga[2],lo:=4526,hi:=4527);
Read_Real(rVar:=SenzorVlaga[3],lo:=4528,hi:=4529);
Read_Real(rVar:=SenzorVlaga[4],lo:=4530,hi:=4531);
Read_Real(rVar:=SenzorVlaga[5],lo:=4532,hi:=4533);
Read_Real(rVar:=SenzorVlaga[6],lo:=4534,hi:=4535);
Read_Real(rVar:=SenzorVlaga[7],lo:=4536,hi:=4537);
Read_Real(rVar:=SenzorVlaga[8],lo:=4538,hi:=4539);
Read_Real(rVar:=SenzorVlaga[9],lo:=4540,hi:=4541);
Read_Real(rVar:=TempAlarmPoint[1],lo:=4542,hi:=4543);
Read_Real(rVar:=TempAlarmPoint[2],lo:=4544,hi:=4545);
Read_Real(rVar:=TempAlarmPoint[3],lo:=4546,hi:=4547);
Read_Real(rVar:=TempMaxPoint[1],lo:=4548,hi:=4549);
Read_Real(rVar:=TempMaxPoint[2],lo:=4550,hi:=4551);
Read_Real(rVar:=TempMaxPoint[3],lo:=4552,hi:=4553);
Read_Real(rVar:=TempPovp[1],lo:=4554,hi:=4555);
Read_Real(rVar:=TempPovp[2],lo:=4556,hi:=4557);
Read_Real(rVar:=TempPovp[3],lo:=4558,hi:=4559);
Read_Real(rVar:=TempPovp[4],lo:=4560,hi:=4561);
Read_Real(rVar:=TempPovp[5],lo:=4562,hi:=4563);
Read_Real(rVar:=TempSetPoint[1],lo:=4564,hi:=4565);
Read_Real(rVar:=TempSetPoint[2],lo:=4566,hi:=4567);
Read_Real(rVar:=TempSetPoint[3],lo:=4568,hi:=4569);
Read_Real(rVar:=VlagaPovp[1],lo:=4570,hi:=4571);
Read_Real(rVar:=VlagaPovp[2],lo:=4572,hi:=4573);
Read_Real(rVar:=VlagaPovp[3],lo:=4574,hi:=4575);
Read_Real(rVar:=VlagaPovp[4],lo:=4576,hi:=4577);
Read_Real(rVar:=VlagaPovp[5],lo:=4578,hi:=4579);
Read_Real(rVar:=XVH_GrafTemp[1],lo:=4580,hi:=4581);
Read_Real(rVar:=XVH_GrafTemp[2],lo:=4582,hi:=4583);
Read_Real(rVar:=XVH_GrafTemp[3],lo:=4584,hi:=4585);
Read_Real(rVar:=XVH_GrafTemp[4],lo:=4586,hi:=4587);
Read_Real(rVar:=XVH_GrafTemp[5],lo:=4588,hi:=4589);
Read_Real(rVar:=XVH_GrafVlaga[1],lo:=4590,hi:=4591);
Read_Real(rVar:=XVH_GrafVlaga[2],lo:=4592,hi:=4593);
Read_Real(rVar:=XVH_GrafVlaga[3],lo:=4594,hi:=4595);
Read_Real(rVar:=XVH_GrafVlaga[4],lo:=4596,hi:=4597);
Read_Real(rVar:=XVH_GrafVlaga[5],lo:=4598,hi:=4599);
Read_Real(rVar:=XVH_NastTempProstora[1],lo:=4600,hi:=4601);
Read_Real(rVar:=XVH_NastTempProstora[2],lo:=4602,hi:=4603);
Read_Real(rVar:=XVH_NastTempProstora[3],lo:=4604,hi:=4605);
Read_Real(rVar:=XVH_ObratovalneUre[1],lo:=4606,hi:=4607);
Read_Real(rVar:=XVH_ObratovalneUre[2],lo:=4608,hi:=4609);
Read_Real(rVar:=XVH_ObratovalneUre[3],lo:=4610,hi:=4611);
Read_Real(rVar:=XVHhighHum,lo:=4612,hi:=4613);
Read_Real(rVar:=XVHhighTemp,lo:=4614,hi:=4615);
Read_Real(rVar:=XVHlowHum,lo:=4616,hi:=4617);
Read_Real(rVar:=XVHlowTemp,lo:=4618,hi:=4619);
Read_Real(rVar:=Circ[1].MaximumDemandA2,lo:=4620,hi:=4621);
Read_Real(rVar:=Circ[1].MaximumDemandA3,lo:=4622,hi:=4623);
Read_Real(rVar:=Circ[2].MaximumDemandA2,lo:=4624,hi:=4625);
Read_Real(rVar:=Circ[2].MaximumDemandA3,lo:=4626,hi:=4627);
Read_Real(rVar:=Circ[3].MaximumDemandA2,lo:=4628,hi:=4629);
Read_Real(rVar:=Circ[3].MaximumDemandA3,lo:=4630,hi:=4631);
Read_Real(rVar:=Circ[4].MaximumDemandA2,lo:=4632,hi:=4633);
Read_Real(rVar:=Circ[4].MaximumDemandA3,lo:=4634,hi:=4635);
Read_Real(rVar:=Circ[1].RazEner_D_SCADA,lo:=4636,hi:=4637);
Read_Real(rVar:=Circ[1].RazEner_T_SCADA,lo:=4638,hi:=4639);
Read_Real(rVar:=Circ[1].RazEner_M_SCADA,lo:=4640,hi:=4641);
Read_Real(rVar:=Circ[2].RazEner_D_SCADA,lo:=4642,hi:=4643);
Read_Real(rVar:=Circ[2].RazEner_T_SCADA,lo:=4644,hi:=4645);
Read_Real(rVar:=Circ[2].RazEner_M_SCADA,lo:=4646,hi:=4647);
Read_Real(rVar:=Circ[3].RazEner_D_SCADA,lo:=4648,hi:=4649);
Read_Real(rVar:=Circ[3].RazEner_T_SCADA,lo:=4650,hi:=4651);
Read_Real(rVar:=Circ[3].RazEner_M_SCADA,lo:=4652,hi:=4653);
Read_Real(rVar:=Circ[4].RazEner_D_SCADA,lo:=4654,hi:=4655);
Read_Real(rVar:=Circ[4].RazEner_T_SCADA,lo:=4656,hi:=4657);
Read_Real(rVar:=Circ[4].RazEner_M_SCADA,lo:=4658,hi:=4659);
(*Branje STRING*)
(**)
Read_String(sVar:=Date_Time[0],start:=5000);
Read_String(sVar:=Date_Time[1],start:=5015);
Read_String(sVar:=Date_Time[2],start:=5030);
Read_String(sVar:=Date_Time[3],start:=5045);
Read_String(sVar:=UserCurrentName,start:=5060);
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Bool : BOOL
VAR_INPUT
index: INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje BOOL*)
(**)
0:AlarmGenCirc1:=Bit_0;
1:AlarmGenCirc2:=Bit_0;
2:AlarmGenCirc3:=Bit_0;
3:AlarmGenCirc4:=Bit_0;
4:AlarmGenComm:=Bit_0;
5:AlarmGenDI:=Bit_0;
6:AlarmGenKlima1:=Bit_0;
7:AlarmGenKlima2:=Bit_0;
8:AlarmGenKlima3:=Bit_0;
9:AlarmGenRest:=Bit_0;
10:AlarmGenSenzor:=Bit_0;
11:AlarmGenTemp:=Bit_0;
12:AlarmGenVlPr:=Bit_0;
13:AlarmGenVTV:=Bit_0;
14:ComSCADA:=Bit_0;
15:ComSCADA1:=Bit_0;
16:DI_F1_OdklHlOm1_IZP:=Bit_0;
17:DI_F1_OdklHlOm1_ON:=Bit_0;
18:DI_F2_OdklHlOm2_IZP:=Bit_0;
19:DI_F2_OdklHlOm2_ON:=Bit_0;
20:DI_F3_OdklHlOm3_IZP:=Bit_0;
21:DI_F3_OdklHlOm3_ON:=Bit_0;
22:DI_F4_OdkPripVode_IZP:=Bit_0;
23:DI_F4_OdkPripVode_ON:=Bit_0;
24:DI_HladOmara1_ERR:=Bit_0;
25:DI_HladOmara1_ON:=Bit_0;
26:DI_HladOmara2_ERR:=Bit_0;
27:DI_HladOmara2_ON:=Bit_0;
28:DI_HladOmara3_ERR:=Bit_0;
29:DI_HladOmara3_ON:=Bit_0;
30:DI_PripVode1_ERR:=Bit_0;
31:DI_PripVode1_ON:=Bit_0;
32:DI_PripVode2_ERR:=Bit_0;
33:DI_PripVode2_ON:=Bit_0;
34:DI_Q0_DEG3_ON:=Bit_0;
35:DI_Q0_EG3_ON:=Bit_0;
36:DI_Q0_GlavnoStikalo_ON:=Bit_0;
37:DI_Q0_UPS3_ON:=Bit_0;
38:DI_RazlitjeVodeHO1:=Bit_0;
39:DI_RazlitjeVodeHO2:=Bit_0;
40:DI_RazlitjeVodeHO3:=Bit_0;
41:DI_UPS_Alarm:=Bit_0;
42:DI_UPS_BatNacin:=Bit_0;
43:DI_UPS_Polnjenje:=Bit_0;
44:DI_Vlazilec1_ERR:=Bit_0;
45:DI_Vlazilec1_ON:=Bit_0;
46:DI_Vlazilec2_ERR:=Bit_0;
47:DI_Vlazilec2_ON:=Bit_0;
48:DI_Vlazilec3_ERR:=Bit_0;
49:DI_Vlazilec3_ON:=Bit_0;
50:DIN_F1_OdklHlOm1_IZP:=Bit_0;
51:DIN_F2_OdklHlOm2_IZP:=Bit_0;
52:DIN_F3_OdklHlOm3_IZP:=Bit_0;
53:DIN_F4_OdkPripVode_IZP:=Bit_0;
54:DIN_HladOmara1_ERR:=Bit_0;
55:DIN_HladOmara2_ERR:=Bit_0;
56:DIN_HladOmara3_ERR:=Bit_0;
57:DIN_PripVode1_ERR:=Bit_0;
58:DIN_PripVode2_ERR:=Bit_0;
59:DIN_Vlazilec1_ERR:=Bit_0;
60:DIN_Vlazilec2_ERR:=Bit_0;
61:DIN_Vlazilec3_ERR:=Bit_0;
62:DO_HladOm1_Izklop:=Bit_0;
63:DO_HladOm2_Izklop:=Bit_0;
64:DO_HladOm3_Izklop:=Bit_0;
65:ErrComCirc[1]:=Bit_0;
66:ErrComCirc[2]:=Bit_0;
67:ErrComCirc[3]:=Bit_0;
68:ErrComCirc[4]:=Bit_0;
69:ErrComCirc[5]:=Bit_0;
70:ErrComKlima[1]:=Bit_0;
71:ErrComKlima[2]:=Bit_0;
72:ErrComKlima[3]:=Bit_0;
73:ErrComKlima[4]:=Bit_0;
74:ErrComKlima[5]:=Bit_0;
75:ErrComKlima[6]:=Bit_0;
76:ErrCommScada:=Bit_0;
77:ErrComPanelPLC:=Bit_0;
78:ErrComPort2:=Bit_0;
79:ErrorComCirc[1].Error:=Bit_0;
80:ErrorComCirc[2].Error:=Bit_0;
81:ErrorComCirc[3].Error:=Bit_0;
82:ErrorComCirc[4].Error:=Bit_0;
83:ErrorComCirc[5].Error:=Bit_0;
84:ErrorComKlima[1].Error:=Bit_0;
85:ErrorComKlima[2].Error:=Bit_0;
86:ErrorComKlima[3].Error:=Bit_0;
87:ErrorComKlima[4].Error:=Bit_0;
88:ErrorComKlima[5].Error:=Bit_0;
89:ErrorComKlima[6].Error:=Bit_0;
90:Klima[1].AlarmKompresor1:=Bit_0;
91:Klima[1].AlarmKompresor2:=Bit_0;
92:Klima[1].Deluje:=Bit_0;
93:Klima[1].EnergySaving:=Bit_0;
94:Klima[1].FaultyEPROM:=Bit_0;
95:Klima[1].FenThermalCutout:=Bit_0;
96:Klima[1].GeneralAlarm:=Bit_0;
97:Klima[1].Kompresor1naMejiObrUr:=Bit_0;
98:Klima[1].Kompresor2naMejiObrUr:=Bit_0;
99:Klima[1].Napaka:=Bit_0;
100:Klima[1].NapakaPriPretokuZraka:=Bit_0;
101:Klima[1].NapakaSenzorPovratVode:=Bit_0;
102:Klima[1].NapakaSenzorTempIzpiha:=Bit_0;
103:Klima[1].NapakaSenzorTempProstora:=Bit_0;
104:Klima[1].NapakaSenzorVlaznosti:=Bit_0;
105:Klima[1].NapakaSenzorZunanjeTemp:=Bit_0;
106:Klima[1].NiTokaVVlazilcu:=Bit_0;
107:Klima[1].NiVodeVVlazilcu:=Bit_0;
108:Klima[1].NizekPritiskKompresor1:=Bit_0;
109:Klima[1].NizekPritiskKompresor2:=Bit_0;
110:Klima[1].NizkaTempPovratneVode:=Bit_0;
111:Klima[1].NizkaTempVProstoru:=Bit_0;
112:Klima[1].NizkaVlaznost:=Bit_0;
113:Klima[1].OnOffEnablingBySupervisor:=Bit_0;
114:Klima[1].PozarniAlarm:=Bit_0;
115:Klima[1].Razvlazevanje:=Bit_0;
116:Klima[1].RemoteOFFtoOutput:=Bit_0;
117:Klima[1].RemoteOnOff:=Bit_0;
118:Klima[1].RocniIzklop:=Bit_0;
119:Klima[1].SenzorjiStatus:=Bit_0;
120:Klima[1].StoppedByAlarms:=Bit_0;
121:Klima[1].ThermalCutoutHeater1:=Bit_0;
122:Klima[1].ThermalCutoutHeater2:=Bit_0;
123:Klima[1].UnitOnOff:=Bit_0;
124:Klima[1].VentilatorNaMejiObrUr:=Bit_0;
125:Klima[1].VentilGretjeOdpiranje:=Bit_0;
126:Klima[1].VentilGretjeZapiranje:=Bit_0;
127:Klima[1].VentilHlajenjeOdpiranje:=Bit_0;
128:Klima[1].VentilHlajenjeZapiranje:=Bit_0;
129:Klima[1].VisokaTempPovratneVode:=Bit_0;
130:Klima[1].VisokaTempVProstoru:=Bit_0;
131:Klima[1].VisokaVlaznost:=Bit_0;
132:Klima[1].VisokTokVVlazilcu:=Bit_0;
133:Klima[1].Vlazenje:=Bit_0;
134:Klima[1].ZamasenFilter:=Bit_0;
135:Klima[2].AlarmKompresor1:=Bit_0;
136:Klima[2].AlarmKompresor2:=Bit_0;
137:Klima[2].Deluje:=Bit_0;
138:Klima[2].EnergySaving:=Bit_0;
139:Klima[2].FaultyEPROM:=Bit_0;
140:Klima[2].FenThermalCutout:=Bit_0;
141:Klima[2].GeneralAlarm:=Bit_0;
142:Klima[2].Kompresor1naMejiObrUr:=Bit_0;
143:Klima[2].Kompresor2naMejiObrUr:=Bit_0;
144:Klima[2].Napaka:=Bit_0;
145:Klima[2].NapakaPriPretokuZraka:=Bit_0;
146:Klima[2].NapakaSenzorPovratVode:=Bit_0;
147:Klima[2].NapakaSenzorTempIzpiha:=Bit_0;
148:Klima[2].NapakaSenzorTempProstora:=Bit_0;
149:Klima[2].NapakaSenzorVlaznosti:=Bit_0;
150:Klima[2].NapakaSenzorZunanjeTemp:=Bit_0;
151:Klima[2].NiTokaVVlazilcu:=Bit_0;
152:Klima[2].NiVodeVVlazilcu:=Bit_0;
153:Klima[2].NizekPritiskKompresor1:=Bit_0;
154:Klima[2].NizekPritiskKompresor2:=Bit_0;
155:Klima[2].NizkaTempPovratneVode:=Bit_0;
156:Klima[2].NizkaTempVProstoru:=Bit_0;
157:Klima[2].NizkaVlaznost:=Bit_0;
158:Klima[2].OnOffEnablingBySupervisor:=Bit_0;
159:Klima[2].PozarniAlarm:=Bit_0;
160:Klima[2].Razvlazevanje:=Bit_0;
161:Klima[2].RemoteOFFtoOutput:=Bit_0;
162:Klima[2].RemoteOnOff:=Bit_0;
163:Klima[2].RocniIzklop:=Bit_0;
164:Klima[2].SenzorjiStatus:=Bit_0;
165:Klima[2].StoppedByAlarms:=Bit_0;
166:Klima[2].ThermalCutoutHeater1:=Bit_0;
167:Klima[2].ThermalCutoutHeater2:=Bit_0;
168:Klima[2].UnitOnOff:=Bit_0;
169:Klima[2].VentilatorNaMejiObrUr:=Bit_0;
170:Klima[2].VentilGretjeOdpiranje:=Bit_0;
171:Klima[2].VentilGretjeZapiranje:=Bit_0;
172:Klima[2].VentilHlajenjeOdpiranje:=Bit_0;
173:Klima[2].VentilHlajenjeZapiranje:=Bit_0;
174:Klima[2].VisokaTempPovratneVode:=Bit_0;
175:Klima[2].VisokaTempVProstoru:=Bit_0;
176:Klima[2].VisokaVlaznost:=Bit_0;
177:Klima[2].VisokTokVVlazilcu:=Bit_0;
178:Klima[2].Vlazenje:=Bit_0;
179:Klima[2].ZamasenFilter:=Bit_0;
180:Klima[3].AlarmKompresor1:=Bit_0;
181:Klima[3].AlarmKompresor2:=Bit_0;
182:Klima[3].Deluje:=Bit_0;
183:Klima[3].EnergySaving:=Bit_0;
184:Klima[3].FaultyEPROM:=Bit_0;
185:Klima[3].FenThermalCutout:=Bit_0;
186:Klima[3].GeneralAlarm:=Bit_0;
187:Klima[3].Kompresor1naMejiObrUr:=Bit_0;
188:Klima[3].Kompresor2naMejiObrUr:=Bit_0;
189:Klima[3].Napaka:=Bit_0;
190:Klima[3].NapakaPriPretokuZraka:=Bit_0;
191:Klima[3].NapakaSenzorPovratVode:=Bit_0;
192:Klima[3].NapakaSenzorTempIzpiha:=Bit_0;
193:Klima[3].NapakaSenzorTempProstora:=Bit_0;
194:Klima[3].NapakaSenzorVlaznosti:=Bit_0;
195:Klima[3].NapakaSenzorZunanjeTemp:=Bit_0;
196:Klima[3].NiTokaVVlazilcu:=Bit_0;
197:Klima[3].NiVodeVVlazilcu:=Bit_0;
198:Klima[3].NizekPritiskKompresor1:=Bit_0;
199:Klima[3].NizekPritiskKompresor2:=Bit_0;
200:Klima[3].NizkaTempPovratneVode:=Bit_0;
201:Klima[3].NizkaTempVProstoru:=Bit_0;
202:Klima[3].NizkaVlaznost:=Bit_0;
203:Klima[3].OnOffEnablingBySupervisor:=Bit_0;
204:Klima[3].PozarniAlarm:=Bit_0;
205:Klima[3].Razvlazevanje:=Bit_0;
206:Klima[3].RemoteOFFtoOutput:=Bit_0;
207:Klima[3].RemoteOnOff:=Bit_0;
208:Klima[3].RocniIzklop:=Bit_0;
209:Klima[3].SenzorjiStatus:=Bit_0;
210:Klima[3].StoppedByAlarms:=Bit_0;
211:Klima[3].ThermalCutoutHeater1:=Bit_0;
212:Klima[3].ThermalCutoutHeater2:=Bit_0;
213:Klima[3].UnitOnOff:=Bit_0;
214:Klima[3].VentilatorNaMejiObrUr:=Bit_0;
215:Klima[3].VentilGretjeOdpiranje:=Bit_0;
216:Klima[3].VentilGretjeZapiranje:=Bit_0;
217:Klima[3].VentilHlajenjeOdpiranje:=Bit_0;
218:Klima[3].VentilHlajenjeZapiranje:=Bit_0;
219:Klima[3].VisokaTempPovratneVode:=Bit_0;
220:Klima[3].VisokaTempVProstoru:=Bit_0;
221:Klima[3].VisokaVlaznost:=Bit_0;
222:Klima[3].VisokTokVVlazilcu:=Bit_0;
223:Klima[3].Vlazenje:=Bit_0;
224:Klima[3].ZamasenFilter:=Bit_0;
225:KlimaAErrors[10]:=Bit_0;
226:KlimaAErrors[11]:=Bit_0;
227:KlimaAErrors[12]:=Bit_0;
228:KlimaAErrors[13]:=Bit_0;
229:KlimaAErrors[14]:=Bit_0;
230:KlimaAErrors[15]:=Bit_0;
231:KlimaAErrors[16]:=Bit_0;
232:KlimaAErrors[17]:=Bit_0;
233:KlimaAErrors[18]:=Bit_0;
234:KlimaAErrors[19]:=Bit_0;
235:KlimaAErrors[1]:=Bit_0;
236:KlimaAErrors[20]:=Bit_0;
237:KlimaAErrors[21]:=Bit_0;
238:KlimaAErrors[22]:=Bit_0;
239:KlimaAErrors[23]:=Bit_0;
240:KlimaAErrors[24]:=Bit_0;
241:KlimaAErrors[25]:=Bit_0;
242:KlimaAErrors[26]:=Bit_0;
243:KlimaAErrors[27]:=Bit_0;
244:KlimaAErrors[28]:=Bit_0;
245:KlimaAErrors[29]:=Bit_0;
246:KlimaAErrors[2]:=Bit_0;
247:KlimaAErrors[30]:=Bit_0;
248:KlimaAErrors[31]:=Bit_0;
249:KlimaAErrors[32]:=Bit_0;
250:KlimaAErrors[33]:=Bit_0;
251:KlimaAErrors[34]:=Bit_0;
252:KlimaAErrors[35]:=Bit_0;
253:KlimaAErrors[36]:=Bit_0;
254:KlimaAErrors[37]:=Bit_0;
255:KlimaAErrors[38]:=Bit_0;
256:KlimaAErrors[39]:=Bit_0;
257:KlimaAErrors[3]:=Bit_0;
258:KlimaAErrors[40]:=Bit_0;
259:KlimaAErrors[4]:=Bit_0;
260:KlimaAErrors[5]:=Bit_0;
261:KlimaAErrors[6]:=Bit_0;
262:KlimaAErrors[7]:=Bit_0;
263:KlimaAErrors[8]:=Bit_0;
264:KlimaAErrors[9]:=Bit_0;
265:KlimaBErrors[10]:=Bit_0;
266:KlimaBErrors[11]:=Bit_0;
267:KlimaBErrors[12]:=Bit_0;
268:KlimaBErrors[13]:=Bit_0;
269:KlimaBErrors[14]:=Bit_0;
270:KlimaBErrors[15]:=Bit_0;
271:KlimaBErrors[16]:=Bit_0;
272:KlimaBErrors[17]:=Bit_0;
273:KlimaBErrors[18]:=Bit_0;
274:KlimaBErrors[19]:=Bit_0;
275:KlimaBErrors[1]:=Bit_0;
276:KlimaBErrors[20]:=Bit_0;
277:KlimaBErrors[21]:=Bit_0;
278:KlimaBErrors[22]:=Bit_0;
279:KlimaBErrors[23]:=Bit_0;
280:KlimaBErrors[24]:=Bit_0;
281:KlimaBErrors[25]:=Bit_0;
282:KlimaBErrors[26]:=Bit_0;
283:KlimaBErrors[27]:=Bit_0;
284:KlimaBErrors[28]:=Bit_0;
285:KlimaBErrors[29]:=Bit_0;
286:KlimaBErrors[2]:=Bit_0;
287:KlimaBErrors[30]:=Bit_0;
288:KlimaBErrors[31]:=Bit_0;
289:KlimaBErrors[32]:=Bit_0;
290:KlimaBErrors[33]:=Bit_0;
291:KlimaBErrors[34]:=Bit_0;
292:KlimaBErrors[35]:=Bit_0;
293:KlimaBErrors[36]:=Bit_0;
294:KlimaBErrors[37]:=Bit_0;
295:KlimaBErrors[38]:=Bit_0;
296:KlimaBErrors[39]:=Bit_0;
297:KlimaBErrors[3]:=Bit_0;
298:KlimaBErrors[40]:=Bit_0;
299:KlimaBErrors[4]:=Bit_0;
300:KlimaBErrors[5]:=Bit_0;
301:KlimaBErrors[6]:=Bit_0;
302:KlimaBErrors[7]:=Bit_0;
303:KlimaBErrors[8]:=Bit_0;
304:KlimaBErrors[9]:=Bit_0;
305:KlimaCErrors[10]:=Bit_0;
306:KlimaCErrors[11]:=Bit_0;
307:KlimaCErrors[12]:=Bit_0;
308:KlimaCErrors[13]:=Bit_0;
309:KlimaCErrors[14]:=Bit_0;
310:KlimaCErrors[15]:=Bit_0;
311:KlimaCErrors[16]:=Bit_0;
312:KlimaCErrors[17]:=Bit_0;
313:KlimaCErrors[18]:=Bit_0;
314:KlimaCErrors[19]:=Bit_0;
315:KlimaCErrors[1]:=Bit_0;
316:KlimaCErrors[20]:=Bit_0;
317:KlimaCErrors[21]:=Bit_0;
318:KlimaCErrors[22]:=Bit_0;
319:KlimaCErrors[23]:=Bit_0;
320:KlimaCErrors[24]:=Bit_0;
321:KlimaCErrors[25]:=Bit_0;
322:KlimaCErrors[26]:=Bit_0;
323:KlimaCErrors[27]:=Bit_0;
324:KlimaCErrors[28]:=Bit_0;
325:KlimaCErrors[29]:=Bit_0;
326:KlimaCErrors[2]:=Bit_0;
327:KlimaCErrors[30]:=Bit_0;
328:KlimaCErrors[31]:=Bit_0;
329:KlimaCErrors[32]:=Bit_0;
330:KlimaCErrors[33]:=Bit_0;
331:KlimaCErrors[34]:=Bit_0;
332:KlimaCErrors[35]:=Bit_0;
333:KlimaCErrors[36]:=Bit_0;
334:KlimaCErrors[37]:=Bit_0;
335:KlimaCErrors[38]:=Bit_0;
336:KlimaCErrors[39]:=Bit_0;
337:KlimaCErrors[3]:=Bit_0;
338:KlimaCErrors[40]:=Bit_0;
339:KlimaCErrors[4]:=Bit_0;
340:KlimaCErrors[5]:=Bit_0;
341:KlimaCErrors[6]:=Bit_0;
342:KlimaCErrors[7]:=Bit_0;
343:KlimaCErrors[8]:=Bit_0;
344:KlimaCErrors[9]:=Bit_0;
345:KlimaGal.AlarmKompresor1:=Bit_0;
346:KlimaGal.AlarmKompresor2:=Bit_0;
347:KlimaGal.Deluje:=Bit_0;
348:KlimaGal.EnergySaving:=Bit_0;
349:KlimaGal.FaultyEPROM:=Bit_0;
350:KlimaGal.FenThermalCutout:=Bit_0;
351:KlimaGal.GeneralAlarm:=Bit_0;
352:KlimaGal.Kompresor1naMejiObrUr:=Bit_0;
353:KlimaGal.Kompresor2naMejiObrUr:=Bit_0;
354:KlimaGal.Napaka:=Bit_0;
355:KlimaGal.NapakaPriPretokuZraka:=Bit_0;
356:KlimaGal.NapakaSenzorPovratVode:=Bit_0;
357:KlimaGal.NapakaSenzorTempIzpiha:=Bit_0;
358:KlimaGal.NapakaSenzorTempProstora:=Bit_0;
359:KlimaGal.NapakaSenzorVlaznosti:=Bit_0;
360:KlimaGal.NapakaSenzorZunanjeTemp:=Bit_0;
361:KlimaGal.NiTokaVVlazilcu:=Bit_0;
362:KlimaGal.NiVodeVVlazilcu:=Bit_0;
363:KlimaGal.NizekPritiskKompresor1:=Bit_0;
364:KlimaGal.NizekPritiskKompresor2:=Bit_0;
365:KlimaGal.NizkaTempPovratneVode:=Bit_0;
366:KlimaGal.NizkaTempVProstoru:=Bit_0;
367:KlimaGal.NizkaVlaznost:=Bit_0;
368:KlimaGal.OnOffEnablingBySupervisor:=Bit_0;
369:KlimaGal.PozarniAlarm:=Bit_0;
370:KlimaGal.Razvlazevanje:=Bit_0;
371:KlimaGal.RemoteOFFtoOutput:=Bit_0;
372:KlimaGal.RemoteOnOff:=Bit_0;
373:KlimaGal.RocniIzklop:=Bit_0;
374:KlimaGal.SenzorjiStatus:=Bit_0;
375:KlimaGal.StoppedByAlarms:=Bit_0;
376:KlimaGal.ThermalCutoutHeater1:=Bit_0;
377:KlimaGal.ThermalCutoutHeater2:=Bit_0;
378:KlimaGal.UnitOnOff:=Bit_0;
379:KlimaGal.VentilatorNaMejiObrUr:=Bit_0;
380:KlimaGal.VentilGretjeOdpiranje:=Bit_0;
381:KlimaGal.VentilGretjeZapiranje:=Bit_0;
382:KlimaGal.VentilHlajenjeOdpiranje:=Bit_0;
383:KlimaGal.VentilHlajenjeZapiranje:=Bit_0;
384:KlimaGal.VisokaTempPovratneVode:=Bit_0;
385:KlimaGal.VisokaTempVProstoru:=Bit_0;
386:KlimaGal.VisokaVlaznost:=Bit_0;
387:KlimaGal.VisokTokVVlazilcu:=Bit_0;
388:KlimaGal.Vlazenje:=Bit_0;
389:KlimaGal.ZamasenFilter:=Bit_0;
390:KlimeNaCas:=Bit_0;
391:NapakaSenzorTemp[10]:=Bit_0;
392:NapakaSenzorTemp[11]:=Bit_0;
393:NapakaSenzorTemp[12]:=Bit_0;
394:NapakaSenzorTemp[13]:=Bit_0;
395:NapakaSenzorTemp[14]:=Bit_0;
396:NapakaSenzorTemp[15]:=Bit_0;
397:NapakaSenzorTemp[16]:=Bit_0;
398:NapakaSenzorTemp[17]:=Bit_0;
399:NapakaSenzorTemp[18]:=Bit_0;
400:NapakaSenzorTemp[19]:=Bit_0;
401:NapakaSenzorTemp[1]:=Bit_0;
402:NapakaSenzorTemp[2]:=Bit_0;
403:NapakaSenzorTemp[3]:=Bit_0;
404:NapakaSenzorTemp[4]:=Bit_0;
405:NapakaSenzorTemp[5]:=Bit_0;
406:NapakaSenzorTemp[6]:=Bit_0;
407:NapakaSenzorTemp[7]:=Bit_0;
408:NapakaSenzorTemp[8]:=Bit_0;
409:NapakaSenzorTemp[9]:=Bit_0;
410:NapakaSenzorVlaga[10]:=Bit_0;
411:NapakaSenzorVlaga[11]:=Bit_0;
412:NapakaSenzorVlaga[12]:=Bit_0;
413:NapakaSenzorVlaga[13]:=Bit_0;
414:NapakaSenzorVlaga[14]:=Bit_0;
415:NapakaSenzorVlaga[15]:=Bit_0;
416:NapakaSenzorVlaga[16]:=Bit_0;
417:NapakaSenzorVlaga[17]:=Bit_0;
418:NapakaSenzorVlaga[18]:=Bit_0;
419:NapakaSenzorVlaga[19]:=Bit_0;
420:NapakaSenzorVlaga[1]:=Bit_0;
421:NapakaSenzorVlaga[2]:=Bit_0;
422:NapakaSenzorVlaga[3]:=Bit_0;
423:NapakaSenzorVlaga[4]:=Bit_0;
424:NapakaSenzorVlaga[5]:=Bit_0;
425:NapakaSenzorVlaga[6]:=Bit_0;
426:NapakaSenzorVlaga[7]:=Bit_0;
427:NapakaSenzorVlaga[8]:=Bit_0;
428:NapakaSenzorVlaga[9]:=Bit_0;
429:SetDateTime:=Bit_0;
430:SetDateTimeDemand:=Bit_0;
431:SetDateTimeError:=Bit_0;
432:SetDateTimeFinished:=Bit_0;
433:SetRemoteOnOff[1]:=Bit_0;
434:SetRemoteOnOff[2]:=Bit_0;
435:SetRemoteOnOff[3]:=Bit_0;
436:SlabaBaterijaPLC_A1:=Bit_0;
437:TempTSprevisoka[10]:=Bit_0;
438:TempTSprevisoka[11]:=Bit_0;
439:TempTSprevisoka[12]:=Bit_0;
440:TempTSprevisoka[13]:=Bit_0;
441:TempTSprevisoka[14]:=Bit_0;
442:TempTSprevisoka[15]:=Bit_0;
443:TempTSprevisoka[16]:=Bit_0;
444:TempTSprevisoka[17]:=Bit_0;
445:TempTSprevisoka[18]:=Bit_0;
446:TempTSprevisoka[19]:=Bit_0;
447:TempTSprevisoka[1]:=Bit_0;
448:TempTSprevisoka[2]:=Bit_0;
449:TempTSprevisoka[3]:=Bit_0;
450:TempTSprevisoka[4]:=Bit_0;
451:TempTSprevisoka[5]:=Bit_0;
452:TempTSprevisoka[6]:=Bit_0;
453:TempTSprevisoka[7]:=Bit_0;
454:TempTSprevisoka[8]:=Bit_0;
455:TempTSprevisoka[9]:=Bit_0;
456:UserLoggedIn:=Bit_0;
457:XVH_AlarmOn:=Bit_0;
458:XVH_RemoteStatus[1]:=Bit_0;
459:XVH_RemoteStatus[2]:=Bit_0;
460:XVH_RemoteStatus[3]:=Bit_0;
461:XVH_setCircNum[1]:=Bit_0;
462:XVH_setCircNum[2]:=Bit_0;
463:XVH_setCircNum[3]:=Bit_0;
464:XVH_setCircNum[4]:=Bit_0;
465:XVH_setCircNum[5]:=Bit_0;
466:XVH_setKlimaNum[1]:=Bit_0;
467:XVH_setKlimaNum[2]:=Bit_0;
468:XVH_setKlimaNum[3]:=Bit_0;
469:XVH_setKlimaNum[4]:=Bit_0;
470:XVH_setKlimaNum[5]:=Bit_0;
471:XVH_setKlimaNum[6]:=Bit_0;
472:ComSCADA2:=Bit_0;
473:ErrCommScada2:=Bit_0;
474:ComSCADA3:=Bit_0;
475:Circ_Vpis_Dnevne_energija_scada1:=Bit_0;
476:Circ_Vpis_Dnevne_energija_scada2:=Bit_0;
477:Circ_Vpis_Tedenska_energija_scada1:=Bit_0;
478:Circ_Vpis_Tedenska_energija_scada2:=Bit_0;
479:Circ_Vpis_Mesecna_energija_scada1:=Bit_0;
480:Circ_Vpis_Mesecna_energija_scada2:=Bit_0;
(*BOOL*)
END_CASE
END_FUNCTION
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_dWord : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje LONG*)
(**)
(*Pisanje REAL*)
(**)
4001:Circ[1].CosFi_III:=Real_0;
4003:Circ[1].DelovnaEnergija:=Real_0;
4005:Circ[1].DelovnaMoc_III:=Real_0;
4007:Circ[1].DelovnaMoc_L1:=Real_0;
4009:Circ[1].DelovnaMoc_L2:=Real_0;
4011:Circ[1].DelovnaMoc_L3:=Real_0;
4013:Circ[1].Frekvenca_L1:=Real_0;
4015:Circ[1].InduktivnaEnergija:=Real_0;
4017:Circ[1].InduktivnaMoc_III:=Real_0;
4019:Circ[1].JalovaMoc_L1:=Real_0;
4021:Circ[1].JalovaMoc_L2:=Real_0;
4023:Circ[1].JalovaMoc_L3:=Real_0;
4025:Circ[1].KapacitivnaEnergija:=Real_0;
4027:Circ[1].KapacitivnaMoc_III:=Real_0;
4029:Circ[1].MaximumDemand:=Real_0;
4031:Circ[1].Napetost_L1_L2:=Real_0;
4033:Circ[1].Napetost_L1_N:=Real_0;
4035:Circ[1].Napetost_L2_L3:=Real_0;
4037:Circ[1].Napetost_L2_N:=Real_0;
4039:Circ[1].Napetost_L3_L1:=Real_0;
4041:Circ[1].Napetost_L3_N:=Real_0;
4043:Circ[1].NavideznaMoc_III:=Real_0;
4045:Circ[1].NicelniTok:=Real_0;
4047:Circ[1].PowerFactor_III:=Real_0;
4049:Circ[1].PowerFactor_L1:=Real_0;
4051:Circ[1].PowerFactor_L2:=Real_0;
4053:Circ[1].PowerFactor_L3:=Real_0;
4055:Circ[1].THDI_L1:=Real_0;
4057:Circ[1].THDI_L2:=Real_0;
4059:Circ[1].THDI_L3:=Real_0;
4061:Circ[1].THDV_L1:=Real_0;
4063:Circ[1].THDV_L2:=Real_0;
4065:Circ[1].THDV_L3:=Real_0;
4067:Circ[1].Tok_L1:=Real_0;
4069:Circ[1].Tok_L2:=Real_0;
4071:Circ[1].Tok_L3:=Real_0;
4073:Circ[1].TokPovprecje_III:=Real_0;
4075:Circ[2].CosFi_III:=Real_0;
4077:Circ[2].DelovnaEnergija:=Real_0;
4079:Circ[2].DelovnaMoc_III:=Real_0;
4081:Circ[2].DelovnaMoc_L1:=Real_0;
4083:Circ[2].DelovnaMoc_L2:=Real_0;
4085:Circ[2].DelovnaMoc_L3:=Real_0;
4087:Circ[2].Frekvenca_L1:=Real_0;
4089:Circ[2].InduktivnaEnergija:=Real_0;
4091:Circ[2].InduktivnaMoc_III:=Real_0;
4093:Circ[2].JalovaMoc_L1:=Real_0;
4095:Circ[2].JalovaMoc_L2:=Real_0;
4097:Circ[2].JalovaMoc_L3:=Real_0;
4099:Circ[2].KapacitivnaEnergija:=Real_0;
4101:Circ[2].KapacitivnaMoc_III:=Real_0;
4103:Circ[2].MaximumDemand:=Real_0;
4105:Circ[2].Napetost_L1_L2:=Real_0;
4107:Circ[2].Napetost_L1_N:=Real_0;
4109:Circ[2].Napetost_L2_L3:=Real_0;
4111:Circ[2].Napetost_L2_N:=Real_0;
4113:Circ[2].Napetost_L3_L1:=Real_0;
4115:Circ[2].Napetost_L3_N:=Real_0;
4117:Circ[2].NavideznaMoc_III:=Real_0;
4119:Circ[2].NicelniTok:=Real_0;
4121:Circ[2].PowerFactor_III:=Real_0;
4123:Circ[2].PowerFactor_L1:=Real_0;
4125:Circ[2].PowerFactor_L2:=Real_0;
4127:Circ[2].PowerFactor_L3:=Real_0;
4129:Circ[2].THDI_L1:=Real_0;
4131:Circ[2].THDI_L2:=Real_0;
4133:Circ[2].THDI_L3:=Real_0;
4135:Circ[2].THDV_L1:=Real_0;
4137:Circ[2].THDV_L2:=Real_0;
4139:Circ[2].THDV_L3:=Real_0;
4141:Circ[2].Tok_L1:=Real_0;
4143:Circ[2].Tok_L2:=Real_0;
4145:Circ[2].Tok_L3:=Real_0;
4147:Circ[2].TokPovprecje_III:=Real_0;
4149:Circ[3].CosFi_III:=Real_0;
4151:Circ[3].DelovnaEnergija:=Real_0;
4153:Circ[3].DelovnaMoc_III:=Real_0;
4155:Circ[3].DelovnaMoc_L1:=Real_0;
4157:Circ[3].DelovnaMoc_L2:=Real_0;
4159:Circ[3].DelovnaMoc_L3:=Real_0;
4161:Circ[3].Frekvenca_L1:=Real_0;
4163:Circ[3].InduktivnaEnergija:=Real_0;
4165:Circ[3].InduktivnaMoc_III:=Real_0;
4167:Circ[3].JalovaMoc_L1:=Real_0;
4169:Circ[3].JalovaMoc_L2:=Real_0;
4171:Circ[3].JalovaMoc_L3:=Real_0;
4173:Circ[3].KapacitivnaEnergija:=Real_0;
4175:Circ[3].KapacitivnaMoc_III:=Real_0;
4177:Circ[3].MaximumDemand:=Real_0;
4179:Circ[3].Napetost_L1_L2:=Real_0;
4181:Circ[3].Napetost_L1_N:=Real_0;
4183:Circ[3].Napetost_L2_L3:=Real_0;
4185:Circ[3].Napetost_L2_N:=Real_0;
4187:Circ[3].Napetost_L3_L1:=Real_0;
4189:Circ[3].Napetost_L3_N:=Real_0;
4191:Circ[3].NavideznaMoc_III:=Real_0;
4193:Circ[3].NicelniTok:=Real_0;
4195:Circ[3].PowerFactor_III:=Real_0;
4197:Circ[3].PowerFactor_L1:=Real_0;
4199:Circ[3].PowerFactor_L2:=Real_0;
4201:Circ[3].PowerFactor_L3:=Real_0;
4203:Circ[3].THDI_L1:=Real_0;
4205:Circ[3].THDI_L2:=Real_0;
4207:Circ[3].THDI_L3:=Real_0;
4209:Circ[3].THDV_L1:=Real_0;
4211:Circ[3].THDV_L2:=Real_0;
4213:Circ[3].THDV_L3:=Real_0;
4215:Circ[3].Tok_L1:=Real_0;
4217:Circ[3].Tok_L2:=Real_0;
4219:Circ[3].Tok_L3:=Real_0;
4221:Circ[3].TokPovprecje_III:=Real_0;
4223:Circ[4].CosFi_III:=Real_0;
4225:Circ[4].DelovnaEnergija:=Real_0;
4227:Circ[4].DelovnaMoc_III:=Real_0;
4229:Circ[4].DelovnaMoc_L1:=Real_0;
4231:Circ[4].DelovnaMoc_L2:=Real_0;
4233:Circ[4].DelovnaMoc_L3:=Real_0;
4235:Circ[4].Frekvenca_L1:=Real_0;
4237:Circ[4].InduktivnaEnergija:=Real_0;
4239:Circ[4].InduktivnaMoc_III:=Real_0;
4241:Circ[4].JalovaMoc_L1:=Real_0;
4243:Circ[4].JalovaMoc_L2:=Real_0;
4245:Circ[4].JalovaMoc_L3:=Real_0;
4247:Circ[4].KapacitivnaEnergija:=Real_0;
4249:Circ[4].KapacitivnaMoc_III:=Real_0;
4251:Circ[4].MaximumDemand:=Real_0;
4253:Circ[4].Napetost_L1_L2:=Real_0;
4255:Circ[4].Napetost_L1_N:=Real_0;
4257:Circ[4].Napetost_L2_L3:=Real_0;
4259:Circ[4].Napetost_L2_N:=Real_0;
4261:Circ[4].Napetost_L3_L1:=Real_0;
4263:Circ[4].Napetost_L3_N:=Real_0;
4265:Circ[4].NavideznaMoc_III:=Real_0;
4267:Circ[4].NicelniTok:=Real_0;
4269:Circ[4].PowerFactor_III:=Real_0;
4271:Circ[4].PowerFactor_L1:=Real_0;
4273:Circ[4].PowerFactor_L2:=Real_0;
4275:Circ[4].PowerFactor_L3:=Real_0;
4277:Circ[4].THDI_L1:=Real_0;
4279:Circ[4].THDI_L2:=Real_0;
4281:Circ[4].THDI_L3:=Real_0;
4283:Circ[4].THDV_L1:=Real_0;
4285:Circ[4].THDV_L2:=Real_0;
4287:Circ[4].THDV_L3:=Real_0;
4289:Circ[4].Tok_L1:=Real_0;
4291:Circ[4].Tok_L2:=Real_0;
4293:Circ[4].Tok_L3:=Real_0;
4295:Circ[4].TokPovprecje_III:=Real_0;
4297:Circutor.CosFi_III:=Real_0;
4299:Circutor.DelovnaEnergija:=Real_0;
4301:Circutor.DelovnaMoc_III:=Real_0;
4303:Circutor.DelovnaMoc_L1:=Real_0;
4305:Circutor.DelovnaMoc_L2:=Real_0;
4307:Circutor.DelovnaMoc_L3:=Real_0;
4309:Circutor.Frekvenca_L1:=Real_0;
4311:Circutor.InduktivnaEnergija:=Real_0;
4313:Circutor.InduktivnaMoc_III:=Real_0;
4315:Circutor.JalovaMoc_L1:=Real_0;
4317:Circutor.JalovaMoc_L2:=Real_0;
4319:Circutor.JalovaMoc_L3:=Real_0;
4321:Circutor.KapacitivnaEnergija:=Real_0;
4323:Circutor.KapacitivnaMoc_III:=Real_0;
4325:Circutor.MaximumDemand:=Real_0;
4327:Circutor.Napetost_L1_L2:=Real_0;
4329:Circutor.Napetost_L1_N:=Real_0;
4331:Circutor.Napetost_L2_L3:=Real_0;
4333:Circutor.Napetost_L2_N:=Real_0;
4335:Circutor.Napetost_L3_L1:=Real_0;
4337:Circutor.Napetost_L3_N:=Real_0;
4339:Circutor.NavideznaMoc_III:=Real_0;
4341:Circutor.NicelniTok:=Real_0;
4343:Circutor.PowerFactor_III:=Real_0;
4345:Circutor.PowerFactor_L1:=Real_0;
4347:Circutor.PowerFactor_L2:=Real_0;
4349:Circutor.PowerFactor_L3:=Real_0;
4351:Circutor.THDI_L1:=Real_0;
4353:Circutor.THDI_L2:=Real_0;
4355:Circutor.THDI_L3:=Real_0;
4357:Circutor.THDV_L1:=Real_0;
4359:Circutor.THDV_L2:=Real_0;
4361:Circutor.THDV_L3:=Real_0;
4363:Circutor.Tok_L1:=Real_0;
4365:Circutor.Tok_L2:=Real_0;
4367:Circutor.Tok_L3:=Real_0;
4369:Circutor.TokPovprecje_III:=Real_0;
4371:Klima[1].NastMaxTemp:=Real_0;
4373:Klima[1].NastMaxVlaznost:=Real_0;
4375:Klima[1].NastMinTemp:=Real_0;
4377:Klima[1].NastMinVlaznost:=Real_0;
4379:Klima[1].NastTempProstora:=Real_0;
4381:Klima[1].NastVlaznost:=Real_0;
4383:Klima[1].ObratovalneUre:=Real_0;
4385:Klima[1].TemperaturaProstora:=Real_0;
4387:Klima[1].TempIzpihanegaZraka:=Real_0;
4389:Klima[1].TempPovratneVode:=Real_0;
4391:Klima[1].VlaznostProstora:=Real_0;
4393:Klima[1].ZunanjaTemp:=Real_0;
4395:Klima[2].NastMaxTemp:=Real_0;
4397:Klima[2].NastMaxVlaznost:=Real_0;
4399:Klima[2].NastMinTemp:=Real_0;
4401:Klima[2].NastMinVlaznost:=Real_0;
4403:Klima[2].NastTempProstora:=Real_0;
4405:Klima[2].NastVlaznost:=Real_0;
4407:Klima[2].ObratovalneUre:=Real_0;
4409:Klima[2].TemperaturaProstora:=Real_0;
4411:Klima[2].TempIzpihanegaZraka:=Real_0;
4413:Klima[2].TempPovratneVode:=Real_0;
4415:Klima[2].VlaznostProstora:=Real_0;
4417:Klima[2].ZunanjaTemp:=Real_0;
4419:Klima[3].NastMaxTemp:=Real_0;
4421:Klima[3].NastMaxVlaznost:=Real_0;
4423:Klima[3].NastMinTemp:=Real_0;
4425:Klima[3].NastMinVlaznost:=Real_0;
4427:Klima[3].NastTempProstora:=Real_0;
4429:Klima[3].NastVlaznost:=Real_0;
4431:Klima[3].ObratovalneUre:=Real_0;
4433:Klima[3].TemperaturaProstora:=Real_0;
4435:Klima[3].TempIzpihanegaZraka:=Real_0;
4437:Klima[3].TempPovratneVode:=Real_0;
4439:Klima[3].VlaznostProstora:=Real_0;
4441:Klima[3].ZunanjaTemp:=Real_0;
4443:KlimaGal.NastMaxTemp:=Real_0;
4445:KlimaGal.NastMaxVlaznost:=Real_0;
4447:KlimaGal.NastMinTemp:=Real_0;
4449:KlimaGal.NastMinVlaznost:=Real_0;
4451:KlimaGal.NastTempProstora:=Real_0;
4453:KlimaGal.NastVlaznost:=Real_0;
4455:KlimaGal.ObratovalneUre:=Real_0;
4457:KlimaGal.TemperaturaProstora:=Real_0;
4459:KlimaGal.TempIzpihanegaZraka:=Real_0;
4461:KlimaGal.TempPovratneVode:=Real_0;
4463:KlimaGal.VlaznostProstora:=Real_0;
4465:KlimaGal.ZunanjaTemp:=Real_0;
4467:SenzorTemp[10]:=Real_0;
4469:SenzorTemp[11]:=Real_0;
4471:SenzorTemp[12]:=Real_0;
4473:SenzorTemp[13]:=Real_0;
4475:SenzorTemp[14]:=Real_0;
4477:SenzorTemp[15]:=Real_0;
4479:SenzorTemp[16]:=Real_0;
4481:SenzorTemp[17]:=Real_0;
4483:SenzorTemp[18]:=Real_0;
4485:SenzorTemp[19]:=Real_0;
4487:SenzorTemp[1]:=Real_0;
4489:SenzorTemp[2]:=Real_0;
4491:SenzorTemp[3]:=Real_0;
4493:SenzorTemp[4]:=Real_0;
4495:SenzorTemp[5]:=Real_0;
4497:SenzorTemp[6]:=Real_0;
4499:SenzorTemp[7]:=Real_0;
4501:SenzorTemp[8]:=Real_0;
4503:SenzorTemp[9]:=Real_0;
4505:SenzorVlaga[10]:=Real_0;
4507:SenzorVlaga[11]:=Real_0;
4509:SenzorVlaga[12]:=Real_0;
4511:SenzorVlaga[13]:=Real_0;
4513:SenzorVlaga[14]:=Real_0;
4515:SenzorVlaga[15]:=Real_0;
4517:SenzorVlaga[16]:=Real_0;
4519:SenzorVlaga[17]:=Real_0;
4521:SenzorVlaga[18]:=Real_0;
4523:SenzorVlaga[19]:=Real_0;
4525:SenzorVlaga[1]:=Real_0;
4527:SenzorVlaga[2]:=Real_0;
4529:SenzorVlaga[3]:=Real_0;
4531:SenzorVlaga[4]:=Real_0;
4533:SenzorVlaga[5]:=Real_0;
4535:SenzorVlaga[6]:=Real_0;
4537:SenzorVlaga[7]:=Real_0;
4539:SenzorVlaga[8]:=Real_0;
4541:SenzorVlaga[9]:=Real_0;
4543:TempAlarmPoint[1]:=Real_0;
4545:TempAlarmPoint[2]:=Real_0;
4547:TempAlarmPoint[3]:=Real_0;
4549:TempMaxPoint[1]:=Real_0;
4551:TempMaxPoint[2]:=Real_0;
4553:TempMaxPoint[3]:=Real_0;
4555:TempPovp[1]:=Real_0;
4557:TempPovp[2]:=Real_0;
4559:TempPovp[3]:=Real_0;
4561:TempPovp[4]:=Real_0;
4563:TempPovp[5]:=Real_0;
4565:TempSetPoint[1]:=Real_0;
4567:TempSetPoint[2]:=Real_0;
4569:TempSetPoint[3]:=Real_0;
4571:VlagaPovp[1]:=Real_0;
4573:VlagaPovp[2]:=Real_0;
4575:VlagaPovp[3]:=Real_0;
4577:VlagaPovp[4]:=Real_0;
4579:VlagaPovp[5]:=Real_0;
4581:XVH_GrafTemp[1]:=Real_0;
4583:XVH_GrafTemp[2]:=Real_0;
4585:XVH_GrafTemp[3]:=Real_0;
4587:XVH_GrafTemp[4]:=Real_0;
4589:XVH_GrafTemp[5]:=Real_0;
4591:XVH_GrafVlaga[1]:=Real_0;
4593:XVH_GrafVlaga[2]:=Real_0;
4595:XVH_GrafVlaga[3]:=Real_0;
4597:XVH_GrafVlaga[4]:=Real_0;
4599:XVH_GrafVlaga[5]:=Real_0;
4601:XVH_NastTempProstora[1]:=Real_0;
4603:XVH_NastTempProstora[2]:=Real_0;
4605:XVH_NastTempProstora[3]:=Real_0;
4607:XVH_ObratovalneUre[1]:=Real_0;
4609:XVH_ObratovalneUre[2]:=Real_0;
4611:XVH_ObratovalneUre[3]:=Real_0;
4613:XVHhighHum:=Real_0;
4615:XVHhighTemp:=Real_0;
4617:XVHlowHum:=Real_0;
4619:XVHlowTemp:=Real_0;
4621:Circ[1].MaximumDemandA2:=Real_0;
4623:Circ[1].MaximumDemandA3:=Real_0;
4625:Circ[2].MaximumDemandA2:=Real_0;
4627:Circ[2].MaximumDemandA3:=Real_0;
4629:Circ[3].MaximumDemandA2:=Real_0;
4631:Circ[3].MaximumDemandA3:=Real_0;
4633:Circ[4].MaximumDemandA2:=Real_0;
4635:Circ[4].MaximumDemandA3:=Real_0;
4637:Circ[1].RazEner_D_SCADA:=Real_0;
4639:Circ[1].RazEner_T_SCADA:=Real_0;
4641:Circ[1].RazEner_M_SCADA:=Real_0;
4643:Circ[2].RazEner_D_SCADA:=Real_0;
4645:Circ[2].RazEner_T_SCADA:=Real_0;
4647:Circ[2].RazEner_M_SCADA:=Real_0;
4649:Circ[3].RazEner_D_SCADA:=Real_0;
4651:Circ[3].RazEner_T_SCADA:=Real_0;
4653:Circ[3].RazEner_M_SCADA:=Real_0;
4655:Circ[4].RazEner_D_SCADA:=Real_0;
4657:Circ[4].RazEner_T_SCADA:=Real_0;
4659:Circ[4].RazEner_M_SCADA:=Real_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_String : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje STRING*)
(**)
5000:Date_Time[0]:=String_0;
5015:Date_Time[1]:=String_0;
5030:Date_Time[2]:=String_0;
5045:Date_Time[3]:=String_0;
5060:UserCurrentName:=String_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Word : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje INT*)
(**)
0:DateTime.Dan:=Byte_0;
1:DateTime.Leto:=Byte_0;
2:DateTime.Mesec:=Byte_0;
3:DateTime.Minuta:=Byte_0;
4:DateTime.Sekunda:=Byte_0;
5:DateTime.Ura:=Byte_0;
6:ErrorComCirc[1].Code[10]:=Byte_0;
7:ErrorComCirc[1].Code[11]:=Byte_0;
8:ErrorComCirc[1].Code[12]:=Byte_0;
9:ErrorComCirc[1].Code[13]:=Byte_0;
10:ErrorComCirc[1].Code[14]:=Byte_0;
11:ErrorComCirc[1].Code[15]:=Byte_0;
12:ErrorComCirc[1].Code[1]:=Byte_0;
13:ErrorComCirc[1].Code[2]:=Byte_0;
14:ErrorComCirc[1].Code[3]:=Byte_0;
15:ErrorComCirc[1].Code[4]:=Byte_0;
16:ErrorComCirc[1].Code[5]:=Byte_0;
17:ErrorComCirc[1].Code[6]:=Byte_0;
18:ErrorComCirc[1].Code[7]:=Byte_0;
19:ErrorComCirc[1].Code[8]:=Byte_0;
20:ErrorComCirc[1].Code[9]:=Byte_0;
21:ErrorComCirc[1].Status:=Word_01;
22:ErrorComCirc[2].Code[10]:=Byte_0;
23:ErrorComCirc[2].Code[11]:=Byte_0;
24:ErrorComCirc[2].Code[12]:=Byte_0;
25:ErrorComCirc[2].Code[13]:=Byte_0;
26:ErrorComCirc[2].Code[14]:=Byte_0;
27:ErrorComCirc[2].Code[15]:=Byte_0;
28:ErrorComCirc[2].Code[1]:=Byte_0;
29:ErrorComCirc[2].Code[2]:=Byte_0;
30:ErrorComCirc[2].Code[3]:=Byte_0;
31:ErrorComCirc[2].Code[4]:=Byte_0;
32:ErrorComCirc[2].Code[5]:=Byte_0;
33:ErrorComCirc[2].Code[6]:=Byte_0;
34:ErrorComCirc[2].Code[7]:=Byte_0;
35:ErrorComCirc[2].Code[8]:=Byte_0;
36:ErrorComCirc[2].Code[9]:=Byte_0;
37:ErrorComCirc[2].Status:=Word_01;
38:ErrorComCirc[3].Code[10]:=Byte_0;
39:ErrorComCirc[3].Code[11]:=Byte_0;
40:ErrorComCirc[3].Code[12]:=Byte_0;
41:ErrorComCirc[3].Code[13]:=Byte_0;
42:ErrorComCirc[3].Code[14]:=Byte_0;
43:ErrorComCirc[3].Code[15]:=Byte_0;
44:ErrorComCirc[3].Code[1]:=Byte_0;
45:ErrorComCirc[3].Code[2]:=Byte_0;
46:ErrorComCirc[3].Code[3]:=Byte_0;
47:ErrorComCirc[3].Code[4]:=Byte_0;
48:ErrorComCirc[3].Code[5]:=Byte_0;
49:ErrorComCirc[3].Code[6]:=Byte_0;
50:ErrorComCirc[3].Code[7]:=Byte_0;
51:ErrorComCirc[3].Code[8]:=Byte_0;
52:ErrorComCirc[3].Code[9]:=Byte_0;
53:ErrorComCirc[3].Status:=Word_01;
54:ErrorComCirc[4].Code[10]:=Byte_0;
55:ErrorComCirc[4].Code[11]:=Byte_0;
56:ErrorComCirc[4].Code[12]:=Byte_0;
57:ErrorComCirc[4].Code[13]:=Byte_0;
58:ErrorComCirc[4].Code[14]:=Byte_0;
59:ErrorComCirc[4].Code[15]:=Byte_0;
60:ErrorComCirc[4].Code[1]:=Byte_0;
61:ErrorComCirc[4].Code[2]:=Byte_0;
62:ErrorComCirc[4].Code[3]:=Byte_0;
63:ErrorComCirc[4].Code[4]:=Byte_0;
64:ErrorComCirc[4].Code[5]:=Byte_0;
65:ErrorComCirc[4].Code[6]:=Byte_0;
66:ErrorComCirc[4].Code[7]:=Byte_0;
67:ErrorComCirc[4].Code[8]:=Byte_0;
68:ErrorComCirc[4].Code[9]:=Byte_0;
69:ErrorComCirc[4].Status:=Word_01;
70:ErrorComCirc[5].Code[10]:=Byte_0;
71:ErrorComCirc[5].Code[11]:=Byte_0;
72:ErrorComCirc[5].Code[12]:=Byte_0;
73:ErrorComCirc[5].Code[13]:=Byte_0;
74:ErrorComCirc[5].Code[14]:=Byte_0;
75:ErrorComCirc[5].Code[15]:=Byte_0;
76:ErrorComCirc[5].Code[1]:=Byte_0;
77:ErrorComCirc[5].Code[2]:=Byte_0;
78:ErrorComCirc[5].Code[3]:=Byte_0;
79:ErrorComCirc[5].Code[4]:=Byte_0;
80:ErrorComCirc[5].Code[5]:=Byte_0;
81:ErrorComCirc[5].Code[6]:=Byte_0;
82:ErrorComCirc[5].Code[7]:=Byte_0;
83:ErrorComCirc[5].Code[8]:=Byte_0;
84:ErrorComCirc[5].Code[9]:=Byte_0;
85:ErrorComCirc[5].Status:=Word_01;
86:ErrorComKlima[1].Code[10]:=Byte_0;
87:ErrorComKlima[1].Code[11]:=Byte_0;
88:ErrorComKlima[1].Code[12]:=Byte_0;
89:ErrorComKlima[1].Code[13]:=Byte_0;
90:ErrorComKlima[1].Code[14]:=Byte_0;
91:ErrorComKlima[1].Code[15]:=Byte_0;
92:ErrorComKlima[1].Code[1]:=Byte_0;
93:ErrorComKlima[1].Code[2]:=Byte_0;
94:ErrorComKlima[1].Code[3]:=Byte_0;
95:ErrorComKlima[1].Code[4]:=Byte_0;
96:ErrorComKlima[1].Code[5]:=Byte_0;
97:ErrorComKlima[1].Code[6]:=Byte_0;
98:ErrorComKlima[1].Code[7]:=Byte_0;
99:ErrorComKlima[1].Code[8]:=Byte_0;
100:ErrorComKlima[1].Code[9]:=Byte_0;
101:ErrorComKlima[1].Status:=Word_01;
102:ErrorComKlima[2].Code[10]:=Byte_0;
103:ErrorComKlima[2].Code[11]:=Byte_0;
104:ErrorComKlima[2].Code[12]:=Byte_0;
105:ErrorComKlima[2].Code[13]:=Byte_0;
106:ErrorComKlima[2].Code[14]:=Byte_0;
107:ErrorComKlima[2].Code[15]:=Byte_0;
108:ErrorComKlima[2].Code[1]:=Byte_0;
109:ErrorComKlima[2].Code[2]:=Byte_0;
110:ErrorComKlima[2].Code[3]:=Byte_0;
111:ErrorComKlima[2].Code[4]:=Byte_0;
112:ErrorComKlima[2].Code[5]:=Byte_0;
113:ErrorComKlima[2].Code[6]:=Byte_0;
114:ErrorComKlima[2].Code[7]:=Byte_0;
115:ErrorComKlima[2].Code[8]:=Byte_0;
116:ErrorComKlima[2].Code[9]:=Byte_0;
117:ErrorComKlima[2].Status:=Word_01;
118:ErrorComKlima[3].Code[10]:=Byte_0;
119:ErrorComKlima[3].Code[11]:=Byte_0;
120:ErrorComKlima[3].Code[12]:=Byte_0;
121:ErrorComKlima[3].Code[13]:=Byte_0;
122:ErrorComKlima[3].Code[14]:=Byte_0;
123:ErrorComKlima[3].Code[15]:=Byte_0;
124:ErrorComKlima[3].Code[1]:=Byte_0;
125:ErrorComKlima[3].Code[2]:=Byte_0;
126:ErrorComKlima[3].Code[3]:=Byte_0;
127:ErrorComKlima[3].Code[4]:=Byte_0;
128:ErrorComKlima[3].Code[5]:=Byte_0;
129:ErrorComKlima[3].Code[6]:=Byte_0;
130:ErrorComKlima[3].Code[7]:=Byte_0;
131:ErrorComKlima[3].Code[8]:=Byte_0;
132:ErrorComKlima[3].Code[9]:=Byte_0;
133:ErrorComKlima[3].Status:=Word_01;
134:ErrorComKlima[4].Code[10]:=Byte_0;
135:ErrorComKlima[4].Code[11]:=Byte_0;
136:ErrorComKlima[4].Code[12]:=Byte_0;
137:ErrorComKlima[4].Code[13]:=Byte_0;
138:ErrorComKlima[4].Code[14]:=Byte_0;
139:ErrorComKlima[4].Code[15]:=Byte_0;
140:ErrorComKlima[4].Code[1]:=Byte_0;
141:ErrorComKlima[4].Code[2]:=Byte_0;
142:ErrorComKlima[4].Code[3]:=Byte_0;
143:ErrorComKlima[4].Code[4]:=Byte_0;
144:ErrorComKlima[4].Code[5]:=Byte_0;
145:ErrorComKlima[4].Code[6]:=Byte_0;
146:ErrorComKlima[4].Code[7]:=Byte_0;
147:ErrorComKlima[4].Code[8]:=Byte_0;
148:ErrorComKlima[4].Code[9]:=Byte_0;
149:ErrorComKlima[4].Status:=Word_01;
150:ErrorComKlima[5].Code[10]:=Byte_0;
151:ErrorComKlima[5].Code[11]:=Byte_0;
152:ErrorComKlima[5].Code[12]:=Byte_0;
153:ErrorComKlima[5].Code[13]:=Byte_0;
154:ErrorComKlima[5].Code[14]:=Byte_0;
155:ErrorComKlima[5].Code[15]:=Byte_0;
156:ErrorComKlima[5].Code[1]:=Byte_0;
157:ErrorComKlima[5].Code[2]:=Byte_0;
158:ErrorComKlima[5].Code[3]:=Byte_0;
159:ErrorComKlima[5].Code[4]:=Byte_0;
160:ErrorComKlima[5].Code[5]:=Byte_0;
161:ErrorComKlima[5].Code[6]:=Byte_0;
162:ErrorComKlima[5].Code[7]:=Byte_0;
163:ErrorComKlima[5].Code[8]:=Byte_0;
164:ErrorComKlima[5].Code[9]:=Byte_0;
165:ErrorComKlima[5].Status:=Word_01;
166:ErrorComKlima[6].Code[10]:=Byte_0;
167:ErrorComKlima[6].Code[11]:=Byte_0;
168:ErrorComKlima[6].Code[12]:=Byte_0;
169:ErrorComKlima[6].Code[13]:=Byte_0;
170:ErrorComKlima[6].Code[14]:=Byte_0;
171:ErrorComKlima[6].Code[15]:=Byte_0;
172:ErrorComKlima[6].Code[1]:=Byte_0;
173:ErrorComKlima[6].Code[2]:=Byte_0;
174:ErrorComKlima[6].Code[3]:=Byte_0;
175:ErrorComKlima[6].Code[4]:=Byte_0;
176:ErrorComKlima[6].Code[5]:=Byte_0;
177:ErrorComKlima[6].Code[6]:=Byte_0;
178:ErrorComKlima[6].Code[7]:=Byte_0;
179:ErrorComKlima[6].Code[8]:=Byte_0;
180:ErrorComKlima[6].Code[9]:=Byte_0;
181:ErrorComKlima[6].Status:=Word_01;
182:Klima[1].GrelecStatus:=Byte_0;
183:Klima[1].IzhodniVentStatus:=Byte_0;
184:Klima[1].KompresorStatus:=Byte_0;
185:Klima[1].VlazilecStatus:=Byte_0;
186:Klima[2].GrelecStatus:=Byte_0;
187:Klima[2].IzhodniVentStatus:=Byte_0;
188:Klima[2].KompresorStatus:=Byte_0;
189:Klima[2].VlazilecStatus:=Byte_0;
190:Klima[3].GrelecStatus:=Byte_0;
191:Klima[3].IzhodniVentStatus:=Byte_0;
192:Klima[3].KompresorStatus:=Byte_0;
193:Klima[3].VlazilecStatus:=Byte_0;
194:KlimaGal.GrelecStatus:=Byte_0;
195:KlimaGal.IzhodniVentStatus:=Byte_0;
196:KlimaGal.KompresorStatus:=Byte_0;
197:KlimaGal.VlazilecStatus:=Byte_0;
198:Qstanje[10]:=Byte_0;
199:Qstanje[1]:=Byte_0;
200:Qstanje[2]:=Byte_0;
201:Qstanje[3]:=Byte_0;
202:Qstanje[4]:=Byte_0;
203:Qstanje[5]:=Byte_0;
204:Qstanje[6]:=Byte_0;
205:Qstanje[7]:=Byte_0;
206:Qstanje[8]:=Byte_0;
207:Qstanje[9]:=Byte_0;
208:UserCurrentLevel:=Byte_0;
209:XVH_CircNumber:=Byte_0;
210:XVH_KlimaNumber:=Byte_0;
211:XVH_PripravaVodeStat[1]:=Byte_0;
212:XVH_PripravaVodeStat[2]:=Byte_0;
213:XVH_UPSstatus:=Byte_0;
214:XVH_VlazilecStatus[1]:=Byte_0;
215:XVH_VlazilecStatus[2]:=Byte_0;
216:XVH_VlazilecStatus[3]:=Byte_0;
217:XVHnum[10]:=Byte_0;
218:XVHnum[11]:=Byte_0;
219:XVHnum[12]:=Byte_0;
220:XVHnum[13]:=Byte_0;
221:XVHnum[14]:=Byte_0;
222:XVHnum[1]:=Byte_0;
223:XVHnum[2]:=Byte_0;
224:XVHnum[3]:=Byte_0;
225:XVHnum[4]:=Byte_0;
226:XVHnum[5]:=Byte_0;
227:XVHnum[6]:=Byte_0;
228:XVHnum[7]:=Byte_0;
229:XVHnum[8]:=Byte_0;
230:XVHnum[9]:=Byte_0;
231:kom_nast_cas_izpada:=Word_01;
(*Pisanje UINT*)
(**)
;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
(*Modbus Slave Example*)
PROGRAM PLC_PRG_modnet
VAR
Slave_Adresa:BYTE:=2;
Slave_Port:INT:=502;
SlaveSetup:MBS_Setup;
SlavePoll:MBS_Poll;
SlaveAnswer:MBS_Answer;
step: USINT;
end :BOOL;
i: INT;
cycle :BOOL := FALSE; (* First cycle *)
OpenDefaultPort: BOOL;
Write_16: BOOL;
Write_15: BOOL;
Write_5: BOOL;
j: INT;
slavepollwOffset_temp: INT;
slaveanswerwCount_temp: INT;
slaveanswerwoffset_temp: INT;
END_VAR
(* @END_DECLARATION := '0' *)
(*Modbus Slave Example*)
IF Write_16=TRUE THEN (**)
FOR j := 0 TO (slaveanswerwCount_temp-1)/15 BY 1 DO (*vpiše se dword, real*)
wStr_0:=mind[slaveanswerwoffset_temp+j];
wStr_1:=mind[slaveanswerwoffset_temp+j+1];
wStr_2 :=mind[slaveanswerwoffset_temp+j+2];
wStr_3:=mind[slaveanswerwoffset_temp+j+3];
wStr_4:=mind[slaveanswerwoffset_temp+j+4];
wStr_5 :=mind[slaveanswerwoffset_temp+j+5];
wStr_6:=mind[slaveanswerwoffset_temp+j+6];
wStr_7:=mind[slaveanswerwoffset_temp+j+7];
wStr_8:=mind[slaveanswerwoffset_temp+j+8];
wStr_9:=mind[slaveanswerwoffset_temp+j+9];
wStr_10:=mind[slaveanswerwoffset_temp+j+10];
wStr_11:=mind[slaveanswerwoffset_temp+j+11];
wStr_12:=mind[slaveanswerwoffset_temp+j+12];
wStr_13:=mind[slaveanswerwoffset_temp+j+13];
wStr_14:=mind[slaveanswerwoffset_temp+j+14];
bStr_29:=0;
mod_Write_String(index:=slaveanswerwoffset_temp+j); (*vpis real in string*)
END_FOR;
FOR j := 1 TO slaveanswerwCount_temp-1 BY 2 DO (*vpiše se dword, real*)
Word_01:=mind[slaveanswerwoffset_temp+j-1];
Word_23:=mind[slaveanswerwoffset_temp+j];
mod_Write_dWord(index:=slaveanswerwoffset_temp+j); (*vpis real in dword*)
END_FOR;
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO (*vpiše se word*)
Word_01:=mind[slaveanswerwoffset_temp+j];
mod_Write_Word(index:=slaveanswerwoffset_temp+j); (*vpis word*)
END_FOR;
Write_16:=FALSE;
END_IF;
IF Write_5=TRUE OR Write_15=TRUE THEN (**)
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO
Bit_0:=mind_bool[slaveanswerwoffset_temp+j];
mod_Write_Bool(index:=slaveanswerwoffset_temp+j); (*vpis spremembe v spremenljivko*)
END_FOR;
Write_5:=FALSE;
Write_15:=FALSE;
END_IF;
(*iz scade ni komande za branje*)
IF Write_16=FALSE AND Write_5=FALSE AND Write_15=FALSE THEN
mod_Read();(*branje spremenljivk za scado*)
END_IF
(*Close all sockets on corresponding event*)
IF cycle = FALSE THEN
SysCallbackRegister(INDEXOF(Callback_Stop),event_stop);
SysCallbackRegister(INDEXOF(Callback_Reset),event_before_reset);
SysCallbackRegister(INDEXOF(Callback_Reset),event_shutdown);
cycle := TRUE;
END_IF
(*Close all connections via application *)
IF end = TRUE THEN
MBS_CloseAllConnections();
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=FALSE); (*Close port*)
step := 0;
END_IF
IF OpenDefaultPort=TRUE THEN
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=TRUE); (*Close port*)
step := 0;
OpenDefaultPort:=FALSE;
END_IF
(* State machine for setup, poll and answer *)
CASE step OF
0:(**)
SlaveSetup.bUnitIdentifier:=Slave_Adresa;(*Subunitnumber*)
slavesetup.wDefaultPort:=Slave_Port;(*Standartport *)
SlaveSetup.xAdditionalPortActive:=FALSE;(*Port opened or closed*)
SlaveSetup.xSecureMode:=FALSE;(*If TRUE only preset IPs are accepted*)
SlaveSetup.tTimeout:=T#3m;(*Timeout if no communication with slave established*)
SlaveSetup(xStrobe:=TRUE);(*Strobe starts function*)
IF slavesetup.xBusy = FALSE THEN
slavesetup(xstrobe := FALSE);
step := 1 ;
END_IF;
1:(**)
SlavePoll(xStrobe:=TRUE);(*Searching for master commands*)
IF NOT SlavePoll.xBusy THEN
step:=2;
SlavePoll(xStrobe:=FALSE);
END_IF;
2:(**)
step:= 1;
CASE SlavePoll.bFunctionCode OF (*Connect accepted pollparameters with answerparameters*)
8:(**)(*Poll answers*)
;
15:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind_bool[slaveanswer.woffset+i] := slavepoll.xarData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.xarData:=slavepoll.xarData;
Write_15:=TRUE;
16:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind[slaveanswer.woffset+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.wardata := slavepoll.warData;
Write_16:=TRUE;
1,2:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slavepoll.wcount-1 BY 1 DO
slaveanswer.xarData[i]:=mind_bool[slavepoll.woffset+i]; (*Read from Data-array*)
END_FOR
3,4:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slaveanswer.wCount-1 BY 1 DO
slaveanswer.warData[i]:=mind[slavepoll.woffset+i];(*Read from Data-array*)
END_FOR
5:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
mind_bool[slavepoll.woffset]:=slavepoll.xarData[0];(*Write to Data-array*)
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.xarData := slavepoll.xardata;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
Write_5:=TRUE;
6:
slaveanswer.bFunctionCode:= slavepoll.bFunctionCode;
mind[slavepoll.woffset]:= slavepoll.warData[0];(*Write to Data-array*)
slaveanswer.wOffset:= slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wardata := slavepoll.wardata;
23:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
FOR i:= 0 TO slavepoll.wCountAdd-1 BY 1 DO
mind[slavepoll.woffsetadd+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
FOR i := 0 TO slavepoll.wCount BY 1 DO
slaveanswer.warData[i] := mind[1+slavepoll.woffset+i];(*Read from Data-array*)
END_FOR;
END_CASE;
IF slavepoll.xAvailable = TRUE THEN
slaveanswer();(*When Data ready, send answer*)
END_IF
END_CASE;
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_dWord : BOOL
VAR_INPUT
dVAR: DWORD;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
DWord_0:=dVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_Real : BOOL
VAR_INPUT
rVAR: REAL;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
Real_0:=rVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_String : BOOL
VAR_INPUT
sVar: STRING;
start:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
String_0:=LEFT (sVar,29);
mind[start]:=wStr_0;
mind[start+1]:=wStr_1;
mind[start+2]:=wStr_2;
mind[start+3]:=wStr_3;
mind[start+4]:=wStr_4;
mind[start+5]:=wStr_5;
mind[start+6]:=wStr_6;
mind[start+7]:=wStr_7;
mind[start+8]:=wStr_8;
mind[start+9]:=wStr_9;
mind[start+10]:=wStr_10;
mind[start+11]:=wStr_11;
mind[start+12]:=wStr_12;
mind[start+13]:=wStr_13;
bStr_29:=0;
mind[start+14]:=wStr_14;
END_FUNCTION
(* @GLOBAL_VARIABLE_LIST := 'Global_Variables_Modnet' *)
(* @PATH := '' *)
(* @SYMFILEFLAGS := '2048' *)
VAR_GLOBAL
(*delovno polje za modnet komunikacijo*)
mind :ARRAY [0..9999] OF WORD;
mind_bool :ARRAY [0..9999] OF BOOL; (*Buffer-Array*)
(*Delovni markerji //*)
Bit_0 AT %MX0.0 : BOOL;
Byte_0 AT %MB0 : BYTE;
Byte_1 AT %MB1 : BYTE;
Byte_2 AT %MB2 : BYTE;
Byte_3 AT %MB3 : BYTE;
Real_0 AT %MR0:REAL;
DWord_0 AT %MD0:DWORD;
Word_01 AT %MW0:WORD;
Word_23 AT %MW2:WORD;
String_0 AT %MW10:STRING;
wStr_0 AT %MW10:WORD;
wStr_1 AT %MW12:WORD;
wStr_2 AT %MW14:WORD;
wStr_3 AT %MW16:WORD;
wStr_4 AT %MW18:WORD;
wStr_5 AT %MW20:WORD;
wStr_6 AT %MW22:WORD;
wStr_7 AT %MW24:WORD;
wStr_8 AT %MW26:WORD;
wStr_9 AT %MW28:WORD;
wStr_10 AT %MW30:WORD;
wStr_11 AT %MW32:WORD;
wStr_12 AT %MW34:WORD;
wStr_13 AT %MW36:WORD;
wStr_14 AT %MW38:WORD;
bStr_00 AT %MB10:BYTE;
bStr_01 AT %MB11:BYTE;
bStr_02 AT %MB12:BYTE;
bStr_03 AT %MB13:BYTE;
bStr_04 AT %MB14:BYTE;
bStr_05 AT %MB15:BYTE;
bStr_06 AT %MB16:BYTE;
bStr_07 AT %MB17:BYTE;
bStr_08 AT %MB18:BYTE;
bStr_09 AT %MB19:BYTE;
bStr_10 AT %MB20:BYTE;
bStr_11 AT %MB21:BYTE;
bStr_12 AT %MB22:BYTE;
bStr_13 AT %MB23:BYTE;
bStr_14 AT %MB24:BYTE;
bStr_15 AT %MB25:BYTE;
bStr_16 AT %MB26:BYTE;
bStr_17 AT %MB27:BYTE;
bStr_18 AT %MB28:BYTE;
bStr_19 AT %MB29:BYTE;
bStr_20 AT %MB30:BYTE;
bStr_21 AT %MB31:BYTE;
bStr_22 AT %MB32:BYTE;
bStr_23 AT %MB33:BYTE;
bStr_24 AT %MB34:BYTE;
bStr_25 AT %MB35:BYTE;
bStr_26 AT %MB36:BYTE;
bStr_27 AT %MB37:BYTE;
bStr_28 AT %MB38:BYTE;
bStr_29 AT %MB39:BYTE;
(********************************************)
END_VAR
(* @OBJECT_END := 'Global_Variables_Modnet' *)
(* @CONNECTIONS := Global_Variables_Modnet
FILENAME : ''
FILETIME : 0
EXPORT : 0
NUMOFCONNECTIONS : 0
*)
(*KONEC_KODA*)