## Prva stran
variable | 1905 | 1.KORAK | variable_1 | 2.KORAK | KORAKI!
Device name | Tip | število spremenljivk | Tip (izbrani) | Zamenjaj z | 1.V Sheet "variable" skopiraj vsebino iz variable.dbf - iz Citect SCAD-a projekta, ki ga želiš pretvoriti.
IOD_GSM | BCD | 0 | BCD | INT | 2.V polje A3 vpiši Device ime spremenljivk ki se bodo prenašale preko Modnet protokola
| BYTE | 16 | BYTE | BYTE | 3.V polje A6 vpiši ime krmilnika (npr.:PLC1, če je adresa v spremenljivkah PLC1:.NapakaKoncnega_stikala, drugače pusti polje prazno)
OPC name | DIGITAL | 503 | DIGITAL | DIGITAL | 4. Pritisni gumb 1.KORAK (V poljih C3:C10 se izpiše število spremenljivk, ki imajo Device enak tistemu v polju A3)
GSM | INT | 138 | INT | INT | 5. Pritisni gumb 2.KORAK (V Sheet-u variable_1 se naredi seznam spremenljivk, ki se bodo prenačale preko Modnet protokola)
| LONG | 1 | LONG | LONG | 6. Pritisni gumb 3.KORAK (V poljih C15:C24 se izpiše število spremnljiv po tipih, v poljih F15:F24 se izpiše število potrebni wordow/coilov za prenos spremnljivk)
| REAL | 472 | REAL | REAL | 7. 4.KORAK: V polja C29:C38 je potrebno ročno vpisati začetne naslove spremnljivk. Potrebno je paziti na:
| STRING | 8 | UINT | UINT | *naslov se morajo začeti z lihim številom npr.:1, 101, 551
| UINT | 38 | STRING | STRING | *naslove je potrebno nastaviti tako, da se naslovi sremenljivk ne more prekrivati (naslovi spremenjivk gredo od (začetnega naslova) do (začetnega naslova+število potrebnih wordow))
| ULONG | 0 | ULONG | ULONG | 8. Pritisni gumb 5.KORAK (V Sheet-u variable_2 se naredi seznam spremenljivk, ki so tokrat sortirana po tipih)
9. Pritisni gumb 6.KORAK (V Sheet-u variable_3 se naredi seznam spremenljivk, katerih Device se zamenja z devicom v polju C41)
Trajanje makroja | variable_1 |  |  | 3.KORAK | 10. Pritisni gumb 7.KORAK (V Sheet-u variable_new se generira seznam spremenljivk. To vsebino je potrebno skopirati v variable.dbf)
0 | Tip | število spremenljivk | TIP | št.potrebnih coilov/wordov | *ta korak traja nekoliko dalj časa (odvisno od števila spremenljivk)
| BCD | 0 | BCD | 0 | *če se pojavi težava z adresami ki se začnejo z 0000 (npr.: "00001" se spremeni na "1") je potrebno uporabiti priloženo (prazno) variable.dbf ali v
| BYTE | 0 | BYTE | 0 | ProjectEditoju/VariableTags na poljubni spremenljki nastaviti adreso" 00001"
| DIGITAL | 503 | DIGITAL | 503 (Coil) | 11. Pritisni gumb 8.KORAK in 9.KORAK (V Sheet-u Xsoft se generira koda)
| INT | 154 | INT | 154 (word) | 12. S pritiskom na gumb 10.KORAK se zgenerira EXP koda za Xsoft (Xsoft_EXP)
| LONG | 1 | LONG | 2 (word) | 13. S pritiskom na gumb Save*.EXP se avtomatsko generira datoka *.EXP
| REAL | 472 | REAL | 944 (word)
| STRING | 8 | STRING | 120 (word)
| UINT | 38 | UINT | 38 (word)
| ULONG | 0 | ULONG | 0 (word)
POZOR!
*V Sheet-u variable mora biti vsebina skopirana od polja A1 naprej (če je katera vrstica prazna makroji ne bodo delovali pravilno)
*Ena "STRING" spremenljivka zasede 15wordow (to pomeni 29 znakov, 1BYTE=1STRING)
|  | 4.KORAK(vpiši ročno) | variable_2 | 5.KORAK | *Dolžina "STRING" spremenljivk je 29 znakov (lahko tudi več vendar ne z uporabno tega dokumenta in XSoft programa,potrebna je modifikacija makrojev in Xsoft programa)
| Tip | Začetni naslov |  | Sortiraj | *Vsi stringi so enake dolžine (29)
| BCD |  |  | BCD | *"BYTE" spremenljivke se v variable.dbf spremenijo v "INT" (prenašanje posameznih bytov ni mogoče, niti naslavaljanje v citectscadi)
| BYTE |  |  | DIGITAL | *Naslovi spremenljivk se morajo obvezno začeti z lihim naslovom (preizkušeno je z začetnimi naslovi, ki se izpišejo po pritisku na gumb Ponastavi)
| DIGITAL | 1 |  | BYTE | *Z pritiskom na gumb RESET se pobriše vsebina vseh Sheet-ov razen Sheet-a variable (makor reset se izvaja precej časa)
| INT | 1 |  | INT | *makroji ne delujejo pravilno,če je v Sheet-u variable več kot 9999 vrstic oz. spremenljivk (število vseh spremnljivk je prikazano v polju B1)
| LONG | 3001 |  | LONG | *če se vsebine iz variable_new ne gre skpirat v variable.dbf datotek, vsebino skopirajte najprej v *.txt datoteko in nato v variable.dbf
| REAL | 4001 |  | REAL | *v polju A14 na Sheet-u Prva stran se prikazuje število ciklop do konca izvedbe makroja (samo za gumb 7.KORAK)
| STRING | 5001 |  | STRING
| UINT | 6001 |  | UINT
| ULONG | 7001 |  | ULONG
| variable_3 | 6.KORAK | variable_new | 7.KORAK
| New Device name | IOD_GSM_TCP |  | Nova variable dbf
|  |  | xSoft | 8.KORAK in 9.KORAK
xSoft koda
xSoft_EXP
Izvoz*.EXP
1.KORAK
2.KORAK
3.KORAK
5.KORAK
6.KORAK
7.KORAK
8.KORAK
9.KORAK
RESET
Ponastavi
10.KORAK
Save*.EXP

## variable
GSMAGR_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.AGR_Gasenje_alarm
GSMAGR_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.AGR_PozCent_napaka
GSMAGR_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.AGR_PozSenzor_okvara
GSMAlarmGenUPS_A_V23 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_A_V23
GSMAlarmGenUPS_V23 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_V23
GSMAlarmGenUPS_V25 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_V25
GSMAlarmPMM1VirATokPrevisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirATokPrevisok
GSMAlarmPMM1VirATokVisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirATokVisok
GSMAlarmPMM1VirBTokPrevisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirBTokPrevisok
GSMAlarmPMM1VirBTokVisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirBTokVisok
GSMAlarmPMM2x17nad8010 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[10]
GSMAlarmPMM2x17nad8011 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[11]
GSMAlarmPMM2x17nad8012 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[12]
GSMAlarmPMM2x17nad8013 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[13]
GSMAlarmPMM2x17nad8014 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[14]
GSMAlarmPMM2x17nad8015 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[15]
GSMAlarmPMM2x17nad8016 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[16]
GSMAlarmPMM2x17nad8017 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[17]
GSMAlarmPMM2x17nad8018 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[18]
GSMAlarmPMM2x17nad8019 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[19]
GSMAlarmPMM2x17nad801 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[1]
GSMAlarmPMM2x17nad8020 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[20]
GSMAlarmPMM2x17nad8021 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[21]
GSMAlarmPMM2x17nad8022 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[22]
GSMAlarmPMM2x17nad8023 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[23]
GSMAlarmPMM2x17nad8024 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[24]
GSMAlarmPMM2x17nad8025 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[25]
GSMAlarmPMM2x17nad8026 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[26]
GSMAlarmPMM2x17nad8027 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[27]
GSMAlarmPMM2x17nad8028 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[28]
GSMAlarmPMM2x17nad8029 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[29]
GSMAlarmPMM2x17nad802 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[2]
GSMAlarmPMM2x17nad8030 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[30]
GSMAlarmPMM2x17nad8031 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[31]
GSMAlarmPMM2x17nad8032 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[32]
GSMAlarmPMM2x17nad8033 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[33]
GSMAlarmPMM2x17nad8034 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[34]
GSMAlarmPMM2x17nad8035 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[35]
GSMAlarmPMM2x17nad8036 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[36]
GSMAlarmPMM2x17nad8037 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[37]
GSMAlarmPMM2x17nad8038 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[38]
GSMAlarmPMM2x17nad8039 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[39]
GSMAlarmPMM2x17nad803 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[3]
GSMAlarmPMM2x17nad8040 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[40]
GSMAlarmPMM2x17nad8041 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[41]
GSMAlarmPMM2x17nad8042 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[42]
GSMAlarmPMM2x17nad804 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[4]
GSMAlarmPMM2x17nad805 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[5]
GSMAlarmPMM2x17nad806 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[6]
GSMAlarmPMM2x17nad807 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[7]
GSMAlarmPMM2x17nad808 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[8]
GSMAlarmPMM2x17nad809 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[9]
GSMALM_AGR_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.ALM_AGR_Gasenje_alarm
GSMALM_AGR_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.ALM_AGR_PozCent_napaka
GSMALM_AGR_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.ALM_AGR_PozSenzor_okvara
GSMALM_GSM_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.ALM_GSM_Gasenje_alarm
GSMALM_GSM_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.ALM_GSM_PozCent_napaka
GSMALM_GSM_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.ALM_GSM_PozSenzor_okvara
GSMcas_modbus_izpad | STRING | IOD_GSM | GSM:.cas_modbus_izpad
GSMCirc1CosFi_III | REAL | IOD_GSM | GSM:.Circ[1].CosFi_III
GSMCirc1DelovnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].DelovnaEnergija
GSMCirc1DelovnaEnergija_TEMP | REAL | IOD_GSM | GSM:.Circ[1].DelovnaEnergija_TEMP
GSMCirc1DelovnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_III
GSMCirc1DelovnaMoc_L1 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L1
GSMCirc1DelovnaMoc_L2 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L2
GSMCirc1DelovnaMoc_L3 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L3
GSMCirc1Frekvenca_L1 | REAL | IOD_GSM | GSM:.Circ[1].Frekvenca_L1
GSMCirc1InduktivnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].InduktivnaEnergija
GSMCirc1InduktivnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].InduktivnaMoc_III
GSMCirc1JalovaMoc_L1 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L1
GSMCirc1JalovaMoc_L2 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L2
GSMCirc1JalovaMoc_L3 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L3
GSMCirc1KapacitivnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].KapacitivnaEnergija
GSMCirc1KapacitivnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].KapacitivnaMoc_III
GSMCirc1MaximumDemand | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemand
GSMCirc1MaximumDemandA2 | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemandA2
GSMCirc1MaximumDemandA3 | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemandA3
GSMCirc1Napetost_L1_L2 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L1_L2
GSMCirc1Napetost_L1_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L1_N
GSMCirc1Napetost_L2_L3 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L2_L3
GSMCirc1Napetost_L2_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L2_N
GSMCirc1Napetost_L3_L1 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L3_L1
GSMCirc1Napetost_L3_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L3_N
GSMCirc1NavideznaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].NavideznaMoc_III
GSMCirc1NicelniTok | REAL | IOD_GSM | GSM:.Circ[1].NicelniTok
GSMCirc1PowerFactor_III | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_III
GSMCirc1PowerFactor_L1 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L1
GSMCirc1PowerFactor_L2 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L2
GSMCirc1PowerFactor_L3 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L3
GSMCirc1RazEner_D | REAL | IOD_GSM | GSM:.Circ[1].RazEner_D
GSMCirc1RazEner_D_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_D_SCADA
GSMCirc1RazEner_D_TEMP | REAL | IOD_GSM | GSM:.Circ[1].RazEner_D_TEMP
GSMCirc1RazEner_M | REAL | IOD_GSM | GSM:.Circ[1].RazEner_M
GSMCirc1RazEner_M_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_M_SCADA
GSMCirc1RazEner_M_TEMP | REAL | IOD_GSM | GSM:.Circ[1].RazEner_M_TEMP
GSMCirc1RazEner_T | REAL | IOD_GSM | GSM:.Circ[1].RazEner_T
GSMCirc1RazEner_T_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_T_SCADA
GSMCirc1RazEner_T_TEMP | REAL | IOD_GSM | GSM:.Circ[1].RazEner_T_TEMP
GSMCirc1THDI_L1 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L1
GSMCirc1THDI_L2 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L2
GSMCirc1THDI_L3 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L3
GSMCirc1THDV_L1 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L1
GSMCirc1THDV_L2 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L2
GSMCirc1THDV_L3 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L3
GSMCirc1Tok_L1 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L1
GSMCirc1Tok_L2 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L2
GSMCirc1Tok_L3 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L3
GSMCirc1TokPovprecje_III | REAL | IOD_GSM | GSM:.Circ[1].TokPovprecje_III
GSMCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Dnevne_energija_scada1
GSMCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Dnevne_energija_scada2
GSMCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Mesecna_energija_scada1
GSMCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Mesecna_energija_scada2
GSMCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Tedenska_energija_scada1
GSMCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Tedenska_energija_scada2
GSMComError | DIGITAL | IOD_GSM | GSM:.ComError
GSMComSCADA | DIGITAL | IOD_GSM | GSM:.ComSCADA
GSMComSCADA1 | DIGITAL | IOD_GSM | GSM:.ComSCADA1
GSMComSCADA2 | DIGITAL | IOD_GSM | GSM:.ComSCADA2
GSMComSCADA3 | DIGITAL | IOD_GSM | GSM:.ComSCADA3
GSMDate_Time0 | STRING | IOD_GSM | GSM:.Date_Time[0]
GSMDate_Time1 | STRING | IOD_GSM | GSM:.Date_Time[1]
GSMDate_Time2 | STRING | IOD_GSM | GSM:.Date_Time[2]
GSMDate_Time3 | STRING | IOD_GSM | GSM:.Date_Time[3]
GSMDateTimeDan | BYTE | IOD_GSM | GSM:.DateTime.Dan
GSMDateTimeLeto | BYTE | IOD_GSM | GSM:.DateTime.Leto
GSMDateTimeLeto2 | INT | IOD_GSM | GSM:.DateTime.Leto2
GSMDateTimeMesec | BYTE | IOD_GSM | GSM:.DateTime.Mesec
GSMDateTimeMinuta | BYTE | IOD_GSM | GSM:.DateTime.Minuta
GSMDateTimePLC_Dan | BYTE | IOD_GSM | GSM:.DateTime.PLC_Dan
GSMDateTimePLC_DanVTednu | BYTE | IOD_GSM | GSM:.DateTime.PLC_DanVTednu
GSMDateTimePLC_Leto | BYTE | IOD_GSM | GSM:.DateTime.PLC_Leto
GSMDateTimePLC_Mesec | BYTE | IOD_GSM | GSM:.DateTime.PLC_Mesec
GSMDateTimePLC_Minuta | BYTE | IOD_GSM | GSM:.DateTime.PLC_Minuta
GSMDateTimePLC_Sekunda | BYTE | IOD_GSM | GSM:.DateTime.PLC_Sekunda
GSMDateTimePLC_Ura | BYTE | IOD_GSM | GSM:.DateTime.PLC_Ura
GSMDateTimeSekunda | BYTE | IOD_GSM | GSM:.DateTime.Sekunda
GSMDateTimeUra | BYTE | IOD_GSM | GSM:.DateTime.Ura
GSMDI1_I11 | DIGITAL | IOD_GSM | GSM:.DI1_I11
GSMDI1_I9 | DIGITAL | IOD_GSM | GSM:.DI1_I9
GSMDI2_I14 | DIGITAL | IOD_GSM | GSM:.DI2_I14
GSMDI2_I15 | DIGITAL | IOD_GSM | GSM:.DI2_I15
GSMDI_R3KC_A_Q21_IzkljucenIzpad | DIGITAL | IOD_GSM | GSM:.DI_R3KC_A_Q21_IzkljucenIzpad
GSMDI_R3KC_A_Q22_IzkljucenIzpad | DIGITAL | IOD_GSM | GSM:.DI_R3KC_A_Q22_IzkljucenIzpad
GSMDI_SBi_RAZS_AA_Izolacija_NOT_OK | DIGITAL | IOD_GSM | GSM:.DI_SBi_RAZS_AA_Izolacija_NOT_OK
GSMDI_SBi_RAZS_AB_Izolacija_NOT_OK | DIGITAL | IOD_GSM | GSM:.DI_SBi_RAZS_AB_Izolacija_NOT_OK
GSMErrComCirc1 | DIGITAL | IOD_GSM | GSM:.ErrComCirc[1]
GSMErrComKlima1 | DIGITAL | IOD_GSM | GSM:.ErrComKlima[1]
GSMErrComKlima2 | DIGITAL | IOD_GSM | GSM:.ErrComKlima[2]
GSMErrComPMM1 | DIGITAL | IOD_GSM | GSM:.ErrComPMM[1]
GSMErrComPMM2 | DIGITAL | IOD_GSM | GSM:.ErrComPMM[2]
GSMErrComPort2 | DIGITAL | IOD_GSM | GSM:.ErrComPort2
GSMErrComPort3 | DIGITAL | IOD_GSM | GSM:.ErrComPort3
GSMErrComPort4 | DIGITAL | IOD_GSM | GSM:.ErrComPort4
GSMErrComUPS1 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[1]
GSMErrComUPS2 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[2]
GSMErrComUPS3 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[3]
GSMErrComUPSMGE1 | DIGITAL | IOD_GSM | GSM:.ErrComUPSMGE[1]
GSMF1_1_zascita_ok | DIGITAL | IOD_GSM | GSM:.F1_1_zascita_ok
GSMGSM_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.GSM_Gasenje_alarm
GSMGSM_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.GSM_PozCent_napaka
GSMGSM_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.GSM_PozSenzor_okvara
GSMHIA1_vlaga_s | INT | IOD_GSM | GSM:.HIA1_vlaga_s
GSMHIA2_vlaga_s | INT | IOD_GSM | GSM:.HIA2_vlaga_s
GSMHIA3_vlaga_s | INT | IOD_GSM | GSM:.HIA3_vlaga_s
GSMHIA4_vlaga_s | INT | IOD_GSM | GSM:.HIA4_vlaga_s
GSMHIA5_vlaga_s | INT | IOD_GSM | GSM:.HIA5_vlaga_s
GSMHIA6_vlaga_s | INT | IOD_GSM | GSM:.HIA6_vlaga_s
GSMHIA7_vlaga_s | INT | IOD_GSM | GSM:.HIA7_vlaga_s
GSMK1_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K1_SkupnaNapaka
GSMK1_vklop_izklop_poteka | DIGITAL | IOD_GSM | GSM:.K1_vklop_izklop_poteka
GSMK1AlarmPozara | DIGITAL | IOD_GSM | GSM:.K1AlarmPozara
GSMK1KlimaZdruzenAlarm | DIGITAL | IOD_GSM | GSM:.K1KlimaZdruzenAlarm
GSMK1NiPretoka | DIGITAL | IOD_GSM | GSM:.K1NiPretoka
GSMK1obrat_ure | STRING | IOD_GSM | GSM:.K1obrat_ure
GSMK1OkvaraRototerma | DIGITAL | IOD_GSM | GSM:.K1OkvaraRototerma
GSMK1OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.K1OkvaraVlazNap
GSMK1PreobMotCrpGr | DIGITAL | IOD_GSM | GSM:.K1PreobMotCrpGr
GSMK1PreobMotVent | DIGITAL | IOD_GSM | GSM:.K1PreobMotVent
GSMK1ProtizamrzZascAkt | DIGITAL | IOD_GSM | GSM:.K1ProtizamrzZascAkt
GSMK1ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.K1ZamasenostFiltra
GSMK2_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K2_SkupnaNapaka
GSMK2_vklop_izklop_poteka | DIGITAL | IOD_GSM | GSM:.K2_vklop_izklop_poteka
GSMK2AlarmPozara | DIGITAL | IOD_GSM | GSM:.K2AlarmPozara
GSMK2KlimaZdruzenAlarm | DIGITAL | IOD_GSM | GSM:.K2KlimaZdruzenAlarm
GSMK2NiPretoka | DIGITAL | IOD_GSM | GSM:.K2NiPretoka
GSMK2OkvaraRototerma | DIGITAL | IOD_GSM | GSM:.K2OkvaraRototerma
GSMK2OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.K2OkvaraVlazNap
GSMK2PreobMotCrpGr | DIGITAL | IOD_GSM | GSM:.K2PreobMotCrpGr
GSMK2PreobMotVent | DIGITAL | IOD_GSM | GSM:.K2PreobMotVent
GSMK2ProtizamrzZascAkt | DIGITAL | IOD_GSM | GSM:.K2ProtizamrzZascAkt
GSMK2ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.K2ZamasenostFiltra
GSMK3_deluje | DIGITAL | IOD_GSM | GSM:.K3_deluje
GSMK3_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K3_SkupnaNapaka
GSMKlima1_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima1_izkljucena
GSMKLIMA1_kke_pogon | DIGITAL | IOD_GSM | GSM:.KLIMA1_kke_pogon
GSMKLIMA1_krm_nap_ok | DIGITAL | IOD_GSM | GSM:.KLIMA1_krm_nap_ok
GSMKlima2_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima2_izkljucena
GSMKlima3_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima3_izkljucena
GSMKlima1Alarm_pozar | DIGITAL | IOD_GSM | GSM:.Klima[1].Alarm_pozar
GSMKlima1Analog_izh_mesanje | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_mesanje
GSMKlima1Analog_izh_rekuperator | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_rekuperator
GSMKlima1Analog_izh_VentGrelnika | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_VentGrelnika
GSMKlima1Analog_izh_VentHlajenja | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_VentHlajenja
GSMKlima1Dejanska_zel_temp | INT | IOD_GSM | GSM:.Klima[1].Dejanska_zel_temp
GSMKlima1DelVentHit1 | DIGITAL | IOD_GSM | GSM:.Klima[1].DelVentHit1
GSMKlima1DelVentHit2 | DIGITAL | IOD_GSM | GSM:.Klima[1].DelVentHit2
GSMKlima1Hitrost_del_vent_disp | INT | IOD_GSM | GSM:.Klima[1].Hitrost_del_vent_disp
GSMKlima1Max_vpih | INT | IOD_GSM | GSM:.Klima[1].Max_vpih
GSMKlima1Min_vpih | INT | IOD_GSM | GSM:.Klima[1].Min_vpih
GSMKlima1Ni_pretoka | DIGITAL | IOD_GSM | GSM:.Klima[1].Ni_pretoka
GSMKlima1Obrat_ure_Vent_h1 | INT | IOD_GSM | GSM:.Klima[1].Obrat_ure_Vent_h1
GSMKlima1Obrat_ure_Vent_h2 | INT | IOD_GSM | GSM:.Klima[1].Obrat_ure_Vent_h2
GSMKlima1OkvaraRototerm | DIGITAL | IOD_GSM | GSM:.Klima[1].OkvaraRototerm
GSMKlima1OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.Klima[1].OkvaraVlazNap
GSMKlima1Pol_komp_konec | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_konec
GSMKlima1Pol_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_sprem_zel_vr
GSMKlima1Pol_komp_zacetek | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_zacetek
GSMKlima1PreklopHitDelVent | INT | IOD_GSM | GSM:.Klima[1].PreklopHitDelVent
GSMKlima1PreobMotCrpGrel | DIGITAL | IOD_GSM | GSM:.Klima[1].PreobMotCrpGrel
GSMKlima1PreobMotVent | DIGITAL | IOD_GSM | GSM:.Klima[1].PreobMotVent
GSMKlima1Protizamrz_zascita | INT | IOD_GSM | GSM:.Klima[1].Protizamrz_zascita
GSMKlima1ProtizamrzZascAktivna | DIGITAL | IOD_GSM | GSM:.Klima[1].ProtizamrzZascAktivna
GSMKlima1Rezim_delovanja | INT | IOD_GSM | GSM:.Klima[1].Rezim_delovanja
GSMKlima1Temperatura_dovoda | INT | IOD_GSM | GSM:.Klima[1].Temperatura_dovoda
GSMKlima1Temperatura_prostora | INT | IOD_GSM | GSM:.Klima[1].Temperatura_prostora
GSMKlima1TempPredPloscnimRekup | INT | IOD_GSM | GSM:.Klima[1].TempPredPloscnimRekup
GSMKlima1TempZaPloscnimRekup | INT | IOD_GSM | GSM:.Klima[1].TempZaPloscnimRekup
GSMKlima1VklopRegKlimata | DIGITAL | IOD_GSM | GSM:.Klima[1].VklopRegKlimata
GSMKlima1Vlaga_v_prostoru | INT | IOD_GSM | GSM:.Klima[1].Vlaga_v_prostoru
GSMKlima1VlagaVstopZrakaProstor | INT | IOD_GSM | GSM:.Klima[1].VlagaVstopZrakaProstor
GSMKlima1ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.Klima[1].ZamasenostFiltra
GSMKlima1ZdruzAlarmA | DIGITAL | IOD_GSM | GSM:.Klima[1].ZdruzAlarmA
GSMKlima1ZdruzAlarmB | DIGITAL | IOD_GSM | GSM:.Klima[1].ZdruzAlarmB
GSMKlima1Zel_temp_eko_gretja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_eko_gretja
GSMKlima1Zel_temp_eko_hlajenja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_eko_hlajenja
GSMKlima1Zel_temp_komf_gretja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_komf_gretja
GSMKlima1Zel_temp_komf_hlajenja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_komf_hlajenja
GSMKlima1Zim_komp_konec | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_konec
GSMKlima1Zim_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_sprem_zel_vr
GSMKlima1Zim_komp_zacetek | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_zacetek
GSMKlima1ZimKompMinVpihKonec | INT | IOD_GSM | GSM:.Klima[1].ZimKompMinVpihKonec
GSMKlima1ZimKompMinVpihZac | INT | IOD_GSM | GSM:.Klima[1].ZimKompMinVpihZac
GSMKlima1ZkompMinVpihSpremZelVr | INT | IOD_GSM | GSM:.Klima[1].ZkompMinVpihSpremZelVr
GSMKlima1Zunanja_temp | INT | IOD_GSM | GSM:.Klima[1].Zunanja_temp
GSMKlima2Alarm_pozar | DIGITAL | IOD_GSM | GSM:.Klima[2].Alarm_pozar
GSMKlima2Analog_izh_mesanje | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_mesanje
GSMKlima2Analog_izh_rekuperator | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_rekuperator
GSMKlima2Analog_izh_VentGrelnika | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_VentGrelnika
GSMKlima2Analog_izh_VentHlajenja | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_VentHlajenja
GSMKlima2Dejanska_zel_temp | INT | IOD_GSM | GSM:.Klima[2].Dejanska_zel_temp
GSMKlima2DelVentHit1 | DIGITAL | IOD_GSM | GSM:.Klima[2].DelVentHit1
GSMKlima2DelVentHit2 | DIGITAL | IOD_GSM | GSM:.Klima[2].DelVentHit2
GSMKlima2Hitrost_del_vent_disp | INT | IOD_GSM | GSM:.Klima[2].Hitrost_del_vent_disp
GSMKlima2Max_vpih | INT | IOD_GSM | GSM:.Klima[2].Max_vpih
GSMKlima2Min_vpih | INT | IOD_GSM | GSM:.Klima[2].Min_vpih
GSMKlima2Ni_pretoka | DIGITAL | IOD_GSM | GSM:.Klima[2].Ni_pretoka
GSMKlima2Obrat_ure_Vent_h1 | INT | IOD_GSM | GSM:.Klima[2].Obrat_ure_Vent_h1
GSMKlima2Obrat_ure_Vent_h2 | INT | IOD_GSM | GSM:.Klima[2].Obrat_ure_Vent_h2
GSMKlima2OkvaraRototerm | DIGITAL | IOD_GSM | GSM:.Klima[2].OkvaraRototerm
GSMKlima2OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.Klima[2].OkvaraVlazNap
GSMKlima2Pol_komp_konec | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_konec
GSMKlima2Pol_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_sprem_zel_vr
GSMKlima2Pol_komp_zacetek | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_zacetek
GSMKlima2PreklopHitDelVent | INT | IOD_GSM | GSM:.Klima[2].PreklopHitDelVent
GSMKlima2PreobMotCrpGrel | DIGITAL | IOD_GSM | GSM:.Klima[2].PreobMotCrpGrel
GSMKlima2PreobMotVent | DIGITAL | IOD_GSM | GSM:.Klima[2].PreobMotVent
GSMKlima2Protizamrz_zascita | INT | IOD_GSM | GSM:.Klima[2].Protizamrz_zascita
GSMKlima2ProtizamrzZascAktivna | DIGITAL | IOD_GSM | GSM:.Klima[2].ProtizamrzZascAktivna
GSMKlima2Rezim_delovanja | INT | IOD_GSM | GSM:.Klima[2].Rezim_delovanja
GSMKlima2Temperatura_dovoda | INT | IOD_GSM | GSM:.Klima[2].Temperatura_dovoda
GSMKlima2Temperatura_prostora | INT | IOD_GSM | GSM:.Klima[2].Temperatura_prostora
GSMKlima2TempPredPloscnimRekup | INT | IOD_GSM | GSM:.Klima[2].TempPredPloscnimRekup
GSMKlima2TempZaPloscnimRekup | INT | IOD_GSM | GSM:.Klima[2].TempZaPloscnimRekup
GSMKlima2VklopRegKlimata | DIGITAL | IOD_GSM | GSM:.Klima[2].VklopRegKlimata
GSMKlima2Vlaga_v_prostoru | INT | IOD_GSM | GSM:.Klima[2].Vlaga_v_prostoru
GSMKlima2VlagaVstopZrakaProstor | INT | IOD_GSM | GSM:.Klima[2].VlagaVstopZrakaProstor
GSMKlima2ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.Klima[2].ZamasenostFiltra
GSMKlima2ZdruzAlarmA | DIGITAL | IOD_GSM | GSM:.Klima[2].ZdruzAlarmA
GSMKlima2ZdruzAlarmB | DIGITAL | IOD_GSM | GSM:.Klima[2].ZdruzAlarmB
GSMKlima2Zel_temp_eko_gretja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_eko_gretja
GSMKlima2Zel_temp_eko_hlajenja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_eko_hlajenja
GSMKlima2Zel_temp_komf_gretja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_komf_gretja
GSMKlima2Zel_temp_komf_hlajenja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_komf_hlajenja
GSMKlima2Zim_komp_konec | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_konec
GSMKlima2Zim_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_sprem_zel_vr
GSMKlima2Zim_komp_zacetek | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_zacetek
GSMKlima2ZimKompMinVpihKonec | INT | IOD_GSM | GSM:.Klima[2].ZimKompMinVpihKonec
GSMKlima2ZimKompMinVpihZac | INT | IOD_GSM | GSM:.Klima[2].ZimKompMinVpihZac
GSMKlima2ZkompMinVpihSpremZelVr | INT | IOD_GSM | GSM:.Klima[2].ZkompMinVpihSpremZelVr
GSMKlima2Zunanja_temp | INT | IOD_GSM | GSM:.Klima[2].Zunanja_temp
GSMKLIMA_m1_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMA_m1_delovanje
GSMKLIMA_m1_napaka | DIGITAL | IOD_GSM | GSM:.KLIMA_m1_napaka
GSMKLIMA_m2_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMA_m2_delovanje
GSMKLIMA_m2_napaka | DIGITAL | IOD_GSM | GSM:.KLIMA_m2_napaka
GSMKlimaIzklopObrUre | INT | IOD_GSM | GSM:.KlimaIzklopObrUre
GSMKLIMAT1_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMAT1_delovanje
GSMKLIMAT1_napaka | DIGITAL | IOD_GSM | GSM:.KLIMAT1_napaka
GSMKLIMAT1_R_zakleni | DIGITAL | IOD_GSM | GSM:.KLIMAT1_R_zakleni
GSMKLIMAT1_vklop_delovanja | DIGITAL | IOD_GSM | GSM:.KLIMAT1_vklop_delovanja
GSMKLIMAT1_vklop_delovanjaR | DIGITAL | IOD_GSM | GSM:.KLIMAT1_vklop_delovanjaR
GSMKLIMAT2_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMAT2_delovanje
GSMKLIMAT2_napaka | DIGITAL | IOD_GSM | GSM:.KLIMAT2_napaka
GSMKLIMAT2_R_zakleni | DIGITAL | IOD_GSM | GSM:.KLIMAT2_R_zakleni
GSMKLIMAT2_vklop_delovanja | DIGITAL | IOD_GSM | GSM:.KLIMAT2_vklop_delovanja
GSMKLIMAT2_vklop_delovanjaR | DIGITAL | IOD_GSM | GSM:.KLIMAT2_vklop_delovanjaR
GSMKlime_vklopi_n | INT | IOD_GSM | GSM:.Klime_vklopi_n
GSMKlimeAVTO | DIGITAL | IOD_GSM | GSM:.KlimeAVTO
GSMkom_nast_cas_izpada | INT | IOD_GSM | GSM:.kom_nast_cas_izpada
GSMMAX_SOCKET_FD_SETSIZE | LONG | IOD_GSM | GSM:.MAX_SOCKET_FD_SETSIZE
GSMN_F1_1_zascita_ok | DIGITAL | IOD_GSM | GSM:.N_F1_1_zascita_ok
GSMN_KLIMA1_krm_nap_ok | DIGITAL | IOD_GSM | GSM:.N_KLIMA1_krm_nap_ok
GSMN_KLIMAT1_napaka | DIGITAL | IOD_GSM | GSM:.N_KLIMAT1_napaka
GSMN_KLIMAT2_napaka | DIGITAL | IOD_GSM | GSM:.N_KLIMAT2_napaka
GSMN_KlimeAVTO | DIGITAL | IOD_GSM | GSM:.N_KlimeAVTO
GSMK1_obr_u_skupno | UINT | IOD_GSM | GSM:.K1_obr_u_skupno
GSMK2_obr_u_skupno | UINT | IOD_GSM | GSM:.K2_obr_u_skupno
GSMN_Q12_izpad | DIGITAL | IOD_GSM | GSM:.N_Q12_izpad
GSMN_UPS_A_V23_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_A_V23_delovanje
GSMN_UPS_A_V23_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_A_V23_napaka
GSMN_UPS_V23_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_V23_delovanje
GSMN_UPS_V23_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_V23_napaka
GSMN_UPS_V25_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_V25_delovanje
GSMN_UPS_V25_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_V25_napaka
GSMN_VLAZILEC1_napaka | DIGITAL | IOD_GSM | GSM:.N_VLAZILEC1_napaka
GSMN_VLAZILEC2_napaka | DIGITAL | IOD_GSM | GSM:.N_VLAZILEC2_napaka
GSMnapaka_kom_panel | DIGITAL | IOD_GSM | GSM:.napaka_kom_panel
GSMnapaka_kom_scada | DIGITAL | IOD_GSM | GSM:.napaka_kom_scada
GSMnapaka_kom_scada2 | DIGITAL | IOD_GSM | GSM:.napaka_kom_scada2
GSMNapakaSenzorSkupno | DIGITAL | IOD_GSM | GSM:.NapakaSenzorSkupno
GSMNapakaSenzorVlagaHIA1 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA1
GSMNapakaSenzorVlagaHIA2 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA2
GSMNapakaSenzorVlagaHIA3 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA3
GSMNapakaSenzorVlagaHIA4 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA4
GSMNapakaSenzorVlagaHIA5 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA5
GSMNapakaSenzorVlagaHIA6 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA6
GSMNapakaSenzorVlagaHIA7 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA7
GSMNapakaTSTempTIA1 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA1
GSMNapakaTSTempTIA2 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA2
GSMNapakaTSTempTIA3 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA3
GSMNapakaTSTempTIA4 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA4
GSMNapakaTSTempTIA5 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA5
GSMNapakaTSTempTIA6 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA6
GSMNapakaTSTempTIA7 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA7
GSMOpozoriloPMM2x17med60in8010 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[10]
GSMOpozoriloPMM2x17med60in8011 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[11]
GSMOpozoriloPMM2x17med60in8012 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[12]
GSMOpozoriloPMM2x17med60in8013 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[13]
GSMOpozoriloPMM2x17med60in8014 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[14]
GSMOpozoriloPMM2x17med60in8015 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[15]
GSMOpozoriloPMM2x17med60in8016 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[16]
GSMOpozoriloPMM2x17med60in8017 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[17]
GSMOpozoriloPMM2x17med60in8018 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[18]
GSMOpozoriloPMM2x17med60in8019 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[19]
GSMOpozoriloPMM2x17med60in801 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[1]
GSMOpozoriloPMM2x17med60in8020 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[20]
GSMOpozoriloPMM2x17med60in8021 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[21]
GSMOpozoriloPMM2x17med60in8022 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[22]
GSMOpozoriloPMM2x17med60in8023 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[23]
GSMOpozoriloPMM2x17med60in8024 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[24]
GSMOpozoriloPMM2x17med60in8025 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[25]
GSMOpozoriloPMM2x17med60in8026 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[26]
GSMOpozoriloPMM2x17med60in8027 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[27]
GSMOpozoriloPMM2x17med60in8028 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[28]
GSMOpozoriloPMM2x17med60in8029 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[29]
GSMOpozoriloPMM2x17med60in802 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[2]
GSMOpozoriloPMM2x17med60in8030 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[30]
GSMOpozoriloPMM2x17med60in8031 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[31]
GSMOpozoriloPMM2x17med60in8032 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[32]
GSMOpozoriloPMM2x17med60in8033 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[33]
GSMOpozoriloPMM2x17med60in8034 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[34]
GSMOpozoriloPMM2x17med60in8035 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[35]
GSMOpozoriloPMM2x17med60in8036 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[36]
GSMOpozoriloPMM2x17med60in8037 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[37]
GSMOpozoriloPMM2x17med60in8038 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[38]
GSMOpozoriloPMM2x17med60in8039 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[39]
GSMOpozoriloPMM2x17med60in803 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[3]
GSMOpozoriloPMM2x17med60in8040 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[40]
GSMOpozoriloPMM2x17med60in8041 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[41]
GSMOpozoriloPMM2x17med60in8042 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[42]
GSMOpozoriloPMM2x17med60in804 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[4]
GSMOpozoriloPMM2x17med60in805 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[5]
GSMOpozoriloPMM2x17med60in806 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[6]
GSMOpozoriloPMM2x17med60in807 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[7]
GSMOpozoriloPMM2x17med60in808 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[8]
GSMOpozoriloPMM2x17med60in809 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[9]
GSMPMM1OverCurrentBetw1 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[1]
GSMPMM1OverCurrentBetw2 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[2]
GSMPMM1OverCurrentBetw3 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[3]
GSMPMM1OverCurrentOver1 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[1]
GSMPMM1OverCurrentOver2 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[2]
GSMPMM1OverCurrentOver3 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[3]
GSMPMM2QA1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_GSM | GSM:.PMM2.QA1_GlStik_IZKLOP_IZPAD
GSMPMM2QB1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_GSM | GSM:.PMM2.QB1_GlStik_IZKLOP_IZPAD
GSMPMM2SkNapaka_med60in80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapaka_med60in80
GSMPMM2SkNapaka_nad80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapaka_nad80
GSMPMM2SkNapakaVirA_med60in80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapakaVirA_med60in80
GSMPMM2SkNapakaVirA_nad80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapakaVirA_nad80
GSMPMM2SkNapakaVirB_med60in80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapakaVirB_med60in80
GSMPMM2SkNapakaVirB_nad80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapakaVirB_nad80
GSMPMM2VirACurrent10 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[10]
GSMPMM2VirACurrent11 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[11]
GSMPMM2VirACurrent12 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[12]
GSMPMM2VirACurrent13 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[13]
GSMPMM2VirACurrent14 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[14]
GSMPMM2VirACurrent15 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[15]
GSMPMM2VirACurrent16 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[16]
GSMPMM2VirACurrent17 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[17]
GSMPMM2VirACurrent18 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[18]
GSMPMM2VirACurrent19 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[19]
GSMPMM2VirACurrent1 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[1]
GSMPMM2VirACurrent20 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[20]
GSMPMM2VirACurrent21 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[21]
GSMPMM2VirACurrent22 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[22]
GSMPMM2VirACurrent23 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[23]
GSMPMM2VirACurrent24 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[24]
GSMPMM2VirACurrent25 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[25]
GSMPMM2VirACurrent26 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[26]
GSMPMM2VirACurrent27 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[27]
GSMPMM2VirACurrent28 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[28]
GSMPMM2VirACurrent29 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[29]
GSMPMM2VirACurrent2 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[2]
GSMPMM2VirACurrent30 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[30]
GSMPMM2VirACurrent31 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[31]
GSMPMM2VirACurrent32 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[32]
GSMPMM2VirACurrent33 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[33]
GSMPMM2VirACurrent34 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[34]
GSMPMM2VirACurrent35 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[35]
GSMPMM2VirACurrent36 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[36]
GSMPMM2VirACurrent37 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[37]
GSMPMM2VirACurrent38 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[38]
GSMPMM2VirACurrent39 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[39]
GSMPMM2VirACurrent3 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[3]
GSMPMM2VirACurrent40 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[40]
GSMPMM2VirACurrent41 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[41]
GSMPMM2VirACurrent42 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[42]
GSMPMM2VirACurrent43 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[43]
GSMPMM2VirACurrent44 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[44]
GSMPMM2VirACurrent4 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[4]
GSMPMM2VirACurrent5 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[5]
GSMPMM2VirACurrent6 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[6]
GSMPMM2VirACurrent7 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[7]
GSMPMM2VirACurrent8 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[8]
GSMPMM2VirACurrent9 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[9]
GSMPMM2VirA_fsys | REAL | IOD_GSM | GSM:.PMM2.VirA_fsys
GSMPMM2VirA_Isys | REAL | IOD_GSM | GSM:.PMM2.VirA_Isys
GSMPMM2VirA_NapakaOzemljitve | DIGITAL | IOD_GSM | GSM:.PMM2.VirA_NapakaOzemljitve
GSMPMM2VirA_PFsys | REAL | IOD_GSM | GSM:.PMM2.VirA_PFsys
GSMPMM2VirA_Psys | REAL | IOD_GSM | GSM:.PMM2.VirA_Psys
GSMPMM2VirA_Qsys | REAL | IOD_GSM | GSM:.PMM2.VirA_Qsys
GSMPMM2VirA_Ssys | REAL | IOD_GSM | GSM:.PMM2.VirA_Ssys
GSMPMM2VirA_Usys | REAL | IOD_GSM | GSM:.PMM2.VirA_Usys
GSMPMM2VirAActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM2.VirAActiveEnergyConsumed_kWh
GSMPMM2VirAActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM2.VirAActivePowerPhaseA_kW
GSMPMM2VirAActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM2.VirAActivePowerPhaseB_kW
GSMPMM2VirAActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM2.VirAActivePowerPhaseC_kW
GSMPMM2VirAAlarmPhaseC01_16_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C01_16_60to80
GSMPMM2VirAAlarmPhaseC01_16_over80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C01_16_over80
GSMPMM2VirAAlarmPhaseC17_32_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C17_32_60to80
GSMPMM2VirAAlarmPhaseC17_32_over80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C17_32_over80
GSMPMM2VirAAlarmPhaseC33_44_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C33_44_60to80
GSMPMM2VirAAlarmPhaseC33_44_over80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C33_44_over80
GSMPMM2VirAAparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM2.VirAAparentPowerPhaseA
GSMPMM2VirAAparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM2.VirAAparentPowerPhaseB
GSMPMM2VirAAparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM2.VirAAparentPowerPhaseC
GSMPMM2VirACurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM2.VirACurrentInPhaseA_A
GSMPMM2VirACurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM2.VirACurrentInPhaseB_A
GSMPMM2VirACurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM2.VirACurrentInPhaseC_A
GSMPMM2VirAReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM2.VirAReactiveEnergyConsumed_kVARh
GSMPMM2VirAReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM2.VirAReactivePowerPhaseA
GSMPMM2VirAReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM2.VirAReactivePowerPhaseB
GSMPMM2VirAReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM2.VirAReactivePowerPhaseC
GSMPMM2VirAVoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseAB_V
GSMPMM2VirAVoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseAN_V
GSMPMM2VirAVoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseBC_V
GSMPMM2VirAVoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseBN_V
GSMPMM2VirAVoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseCA_V
GSMPMM2VirAVoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseCN_V
GSMPMM2VirBCurrent10 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[10]
GSMPMM2VirBCurrent11 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[11]
GSMPMM2VirBCurrent12 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[12]
GSMPMM2VirBCurrent13 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[13]
GSMPMM2VirBCurrent14 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[14]
GSMPMM2VirBCurrent15 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[15]
GSMPMM2VirBCurrent16 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[16]
GSMPMM2VirBCurrent17 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[17]
GSMPMM2VirBCurrent18 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[18]
GSMPMM2VirBCurrent19 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[19]
GSMPMM2VirBCurrent1 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[1]
GSMPMM2VirBCurrent20 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[20]
GSMPMM2VirBCurrent21 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[21]
GSMPMM2VirBCurrent22 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[22]
GSMPMM2VirBCurrent23 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[23]
GSMPMM2VirBCurrent24 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[24]
GSMPMM2VirBCurrent25 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[25]
GSMPMM2VirBCurrent26 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[26]
GSMPMM2VirBCurrent27 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[27]
GSMPMM2VirBCurrent28 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[28]
GSMPMM2VirBCurrent29 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[29]
GSMPMM2VirBCurrent2 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[2]
GSMPMM2VirBCurrent30 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[30]
GSMPMM2VirBCurrent31 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[31]
GSMPMM2VirBCurrent32 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[32]
GSMPMM2VirBCurrent33 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[33]
GSMPMM2VirBCurrent34 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[34]
GSMPMM2VirBCurrent35 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[35]
GSMPMM2VirBCurrent36 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[36]
GSMPMM2VirBCurrent37 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[37]
GSMPMM2VirBCurrent38 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[38]
GSMPMM2VirBCurrent39 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[39]
GSMPMM2VirBCurrent3 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[3]
GSMPMM2VirBCurrent40 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[40]
GSMPMM2VirBCurrent41 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[41]
GSMPMM2VirBCurrent42 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[42]
GSMPMM2VirBCurrent43 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[43]
GSMPMM2VirBCurrent44 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[44]
GSMPMM2VirBCurrent4 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[4]
GSMPMM2VirBCurrent5 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[5]
GSMPMM2VirBCurrent6 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[6]
GSMPMM2VirBCurrent7 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[7]
GSMPMM2VirBCurrent8 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[8]
GSMPMM2VirBCurrent9 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[9]
GSMPMM2VirB_fsys | REAL | IOD_GSM | GSM:.PMM2.VirB_fsys
GSMPMM2VirB_Isys | REAL | IOD_GSM | GSM:.PMM2.VirB_Isys
GSMPMM2VirB_NapakaOzemljitve | DIGITAL | IOD_GSM | GSM:.PMM2.VirB_NapakaOzemljitve
GSMPMM2VirB_PFsys | REAL | IOD_GSM | GSM:.PMM2.VirB_PFsys
GSMPMM2VirB_Psys | REAL | IOD_GSM | GSM:.PMM2.VirB_Psys
GSMPMM2VirB_Qsys | REAL | IOD_GSM | GSM:.PMM2.VirB_Qsys
GSMPMM2VirB_Ssys | REAL | IOD_GSM | GSM:.PMM2.VirB_Ssys
GSMPMM2VirB_Usys | REAL | IOD_GSM | GSM:.PMM2.VirB_Usys
GSMPMM2VirBActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM2.VirBActiveEnergyConsumed_kWh
GSMPMM2VirBActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM2.VirBActivePowerPhaseA_kW
GSMPMM2VirBActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM2.VirBActivePowerPhaseB_kW
GSMPMM2VirBActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM2.VirBActivePowerPhaseC_kW
GSMPMM2VirBAlarmPhaseC01_16_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C01_16_60to80
GSMPMM2VirBAlarmPhaseC01_16_over80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C01_16_over80
GSMPMM2VirBAlarmPhaseC17_32_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C17_32_60to80
GSMPMM2VirBAlarmPhaseC17_32_over80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C17_32_over80
GSMPMM2VirBAlarmPhaseC33_44_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C33_44_60to80
GSMPMM2VirBAlarmPhaseC33_44_over80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C33_44_over80
GSMPMM2VirBAparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM2.VirBAparentPowerPhaseA
GSMPMM2VirBAparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM2.VirBAparentPowerPhaseB
GSMPMM2VirBAparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM2.VirBAparentPowerPhaseC
GSMPMM2VirBCurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM2.VirBCurrentInPhaseA_A
GSMPMM2VirBCurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM2.VirBCurrentInPhaseB_A
GSMPMM2VirBCurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM2.VirBCurrentInPhaseC_A
GSMPMM2VirBReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM2.VirBReactiveEnergyConsumed_kVARh
GSMPMM2VirBReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM2.VirBReactivePowerPhaseA
GSMPMM2VirBReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM2.VirBReactivePowerPhaseB
GSMPMM2VirBReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM2.VirBReactivePowerPhaseC
GSMPMM2VirBVoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseAB_V
GSMPMM2VirBVoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseAN_V
GSMPMM2VirBVoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseBC_V
GSMPMM2VirBVoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseBN_V
GSMPMM2VirBVoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseCA_V
GSMPMM2VirBVoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseCN_V
GSMPMM1ActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM[1].ActiveEnergyConsumed_kWh
GSMPMM1ActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseA_kW
GSMPMM1ActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseB_kW
GSMPMM1ActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseC_kW
GSMPMM1AlarmPhase1C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C01_16_60to80
GSMPMM1AlarmPhase1C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C01_16_over80
GSMPMM1AlarmPhase1C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C17_32_60to80
GSMPMM1AlarmPhase1C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C17_32_over80
GSMPMM1AlarmPhase1C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C33_42_60to80
GSMPMM1AlarmPhase1C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C33_42_over80
GSMPMM1AlarmPhase1GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].GlobalAlarmReg
GSMPMM1AlarmPhase2C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C01_16_60to80
GSMPMM1AlarmPhase2C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C01_16_over80
GSMPMM1AlarmPhase2C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C17_32_60to80
GSMPMM1AlarmPhase2C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C17_32_over80
GSMPMM1AlarmPhase2C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C33_42_60to80
GSMPMM1AlarmPhase2C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C33_42_over80
GSMPMM1AlarmPhase2GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].GlobalAlarmReg
GSMPMM1AlarmPhase3C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C01_16_60to80
GSMPMM1AlarmPhase3C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C01_16_over80
GSMPMM1AlarmPhase3C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C17_32_60to80
GSMPMM1AlarmPhase3C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C17_32_over80
GSMPMM1AlarmPhase3C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C33_42_60to80
GSMPMM1AlarmPhase3C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C33_42_over80
GSMPMM1AlarmPhase3GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].GlobalAlarmReg
GSMPMM1AparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseA
GSMPMM1AparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseB
GSMPMM1AparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseC
GSMPMM1AverageCurrent_A | REAL | IOD_GSM | GSM:.PMM[1].AverageCurrent_A
GSMPMM1AveragePhaseToNeutral_V | REAL | IOD_GSM | GSM:.PMM[1].AveragePhaseToNeutral_V
GSMPMM1AveragePhaseToPhase_V | REAL | IOD_GSM | GSM:.PMM[1].AveragePhaseToPhase_V
GSMPMM1CurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseA_A
GSMPMM1CurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseB_A
GSMPMM1CurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseC_A
GSMPMM1Frequency_Hz | REAL | IOD_GSM | GSM:.PMM[1].Frequency_Hz
GSMPMM1Phase1Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[10]
GSMPMM1Phase1Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[11]
GSMPMM1Phase1Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[12]
GSMPMM1Phase1Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[13]
GSMPMM1Phase1Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[14]
GSMPMM1Phase1Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[15]
GSMPMM1Phase1Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[16]
GSMPMM1Phase1Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[17]
GSMPMM1Phase1Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[18]
GSMPMM1Phase1Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[19]
GSMPMM1Phase1Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[1]
GSMPMM1Phase1Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[20]
GSMPMM1Phase1Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[21]
GSMPMM1Phase1Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[22]
GSMPMM1Phase1Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[23]
GSMPMM1Phase1Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[24]
GSMPMM1Phase1Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[25]
GSMPMM1Phase1Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[26]
GSMPMM1Phase1Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[27]
GSMPMM1Phase1Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[28]
GSMPMM1Phase1Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[29]
GSMPMM1Phase1Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[2]
GSMPMM1Phase1Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[30]
GSMPMM1Phase1Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[31]
GSMPMM1Phase1Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[32]
GSMPMM1Phase1Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[33]
GSMPMM1Phase1Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[34]
GSMPMM1Phase1Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[35]
GSMPMM1Phase1Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[36]
GSMPMM1Phase1Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[37]
GSMPMM1Phase1Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[38]
GSMPMM1Phase1Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[39]
GSMPMM1Phase1Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[3]
GSMPMM1Phase1Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[40]
GSMPMM1Phase1Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[41]
GSMPMM1Phase1Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[42]
GSMPMM1Phase1Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[4]
GSMPMM1Phase1Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[5]
GSMPMM1Phase1Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[6]
GSMPMM1Phase1Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[7]
GSMPMM1Phase1Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[8]
GSMPMM1Phase1Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[9]
GSMPMM1Phase2Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[10]
GSMPMM1Phase2Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[11]
GSMPMM1Phase2Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[12]
GSMPMM1Phase2Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[13]
GSMPMM1Phase2Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[14]
GSMPMM1Phase2Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[15]
GSMPMM1Phase2Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[16]
GSMPMM1Phase2Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[17]
GSMPMM1Phase2Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[18]
GSMPMM1Phase2Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[19]
GSMPMM1Phase2Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[1]
GSMPMM1Phase2Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[20]
GSMPMM1Phase2Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[21]
GSMPMM1Phase2Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[22]
GSMPMM1Phase2Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[23]
GSMPMM1Phase2Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[24]
GSMPMM1Phase2Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[25]
GSMPMM1Phase2Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[26]
GSMPMM1Phase2Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[27]
GSMPMM1Phase2Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[28]
GSMPMM1Phase2Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[29]
GSMPMM1Phase2Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[2]
GSMPMM1Phase2Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[30]
GSMPMM1Phase2Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[31]
GSMPMM1Phase2Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[32]
GSMPMM1Phase2Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[33]
GSMPMM1Phase2Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[34]
GSMPMM1Phase2Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[35]
GSMPMM1Phase2Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[36]
GSMPMM1Phase2Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[37]
GSMPMM1Phase2Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[38]
GSMPMM1Phase2Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[39]
GSMPMM1Phase2Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[3]
GSMPMM1Phase2Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[40]
GSMPMM1Phase2Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[41]
GSMPMM1Phase2Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[42]
GSMPMM1Phase2Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[4]
GSMPMM1Phase2Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[5]
GSMPMM1Phase2Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[6]
GSMPMM1Phase2Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[7]
GSMPMM1Phase2Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[8]
GSMPMM1Phase2Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[9]
GSMPMM1Phase3Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[10]
GSMPMM1Phase3Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[11]
GSMPMM1Phase3Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[12]
GSMPMM1Phase3Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[13]
GSMPMM1Phase3Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[14]
GSMPMM1Phase3Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[15]
GSMPMM1Phase3Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[16]
GSMPMM1Phase3Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[17]
GSMPMM1Phase3Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[18]
GSMPMM1Phase3Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[19]
GSMPMM1Phase3Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[1]
GSMPMM1Phase3Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[20]
GSMPMM1Phase3Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[21]
GSMPMM1Phase3Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[22]
GSMPMM1Phase3Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[23]
GSMPMM1Phase3Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[24]
GSMPMM1Phase3Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[25]
GSMPMM1Phase3Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[26]
GSMPMM1Phase3Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[27]
GSMPMM1Phase3Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[28]
GSMPMM1Phase3Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[29]
GSMPMM1Phase3Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[2]
GSMPMM1Phase3Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[30]
GSMPMM1Phase3Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[31]
GSMPMM1Phase3Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[32]
GSMPMM1Phase3Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[33]
GSMPMM1Phase3Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[34]
GSMPMM1Phase3Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[35]
GSMPMM1Phase3Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[36]
GSMPMM1Phase3Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[37]
GSMPMM1Phase3Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[38]
GSMPMM1Phase3Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[39]
GSMPMM1Phase3Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[3]
GSMPMM1Phase3Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[40]
GSMPMM1Phase3Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[41]
GSMPMM1Phase3Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[42]
GSMPMM1Phase3Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[4]
GSMPMM1Phase3Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[5]
GSMPMM1Phase3Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[6]
GSMPMM1Phase3Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[7]
GSMPMM1Phase3Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[8]
GSMPMM1Phase3Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[9]
GSMPMM1PowerFactorSys | REAL | IOD_GSM | GSM:.PMM[1].PowerFactorSys
GSMPMM1ReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM[1].ReactiveEnergyConsumed_kVARh
GSMPMM1ReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseA
GSMPMM1ReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseB
GSMPMM1ReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseC
GSMPMM1TotalActivePower_kW | REAL | IOD_GSM | GSM:.PMM[1].TotalActivePower_kW
GSMPMM1TotalAparentPower_kVA | REAL | IOD_GSM | GSM:.PMM[1].TotalAparentPower_kVA
GSMPMM1TotalPowerFactor | REAL | IOD_GSM | GSM:.PMM[1].TotalPowerFactor
GSMPMM1TotalReactivePower_kVAR | REAL | IOD_GSM | GSM:.PMM[1].TotalReactivePower_kVAR
GSMPMM1VirA_fsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_fsys
GSMPMM1VirA_Isys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Isys
GSMPMM1VirA_PFsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_PFsys
GSMPMM1VirA_Psys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Psys
GSMPMM1VirA_Qsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Qsys
GSMPMM1VirA_Ssys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Ssys
GSMPMM1VirA_Usys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Usys
GSMPMM1VirB_fsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_fsys
GSMPMM1VirB_Isys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Isys
GSMPMM1VirB_PFsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_PFsys
GSMPMM1VirB_Psys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Psys
GSMPMM1VirB_Qsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Qsys
GSMPMM1VirB_Ssys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Ssys
GSMPMM1VirB_Usys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Usys
GSMPMM1VirBActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM[1].VirBActiveEnergyConsumed_kWh
GSMPMM1VirBActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseA_kW
GSMPMM1VirBActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseB_kW
GSMPMM1VirBActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseC_kW
GSMPMM1VirBAparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseA
GSMPMM1VirBAparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseB
GSMPMM1VirBAparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseC
GSMPMM1VirBAverageCurrent_A | REAL | IOD_GSM | GSM:.PMM[1].VirBAverageCurrent_A
GSMPMM1VirBAveragePhaseToNeutral_V | REAL | IOD_GSM | GSM:.PMM[1].VirBAveragePhaseToNeutral_V
GSMPMM1VirBAveragePhaseToPhase_V | REAL | IOD_GSM | GSM:.PMM[1].VirBAveragePhaseToPhase_V
GSMPMM1VirBCurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseA_A
GSMPMM1VirBCurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseB_A
GSMPMM1VirBCurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseC_A
GSMPMM1VirBFrequency_Hz | REAL | IOD_GSM | GSM:.PMM[1].VirBFrequency_Hz
GSMPMM1VirBPowerFactorSys | REAL | IOD_GSM | GSM:.PMM[1].VirBPowerFactorSys
GSMPMM1VirBReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM[1].VirBReactiveEnergyConsumed_kVARh
GSMPMM1VirBReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseA
GSMPMM1VirBReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseB
GSMPMM1VirBReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseC
GSMPMM1VirBTotalActivePower_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalActivePower_kW
GSMPMM1VirBTotalAparentPower_kVA | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalAparentPower_kVA
GSMPMM1VirBTotalPowerFactor | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalPowerFactor
GSMPMM1VirBTotalReactivePower_kVAR | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalReactivePower_kVAR
GSMPMM1VirBVoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseAB_V
GSMPMM1VirBVoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseAN_V
GSMPMM1VirBVoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseBC_V
GSMPMM1VirBVoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseBN_V
GSMPMM1VirBVoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseCA_V
GSMPMM1VirBVoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseCN_V
GSMPMM1VoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseAB_V
GSMPMM1VoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseAN_V
GSMPMM1VoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseBC_V
GSMPMM1VoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseBN_V
GSMPMM1VoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseCA_V
GSMPMM1VoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseCN_V
GSMPMMfaza01 | REAL | IOD_GSM | GSM:.PMMfaza01
GSMPMMfaza02 | REAL | IOD_GSM | GSM:.PMMfaza02
GSMPMMfaza03 | REAL | IOD_GSM | GSM:.PMMfaza03
GSMPMMfaza04 | REAL | IOD_GSM | GSM:.PMMfaza04
GSMPMMfaza05 | REAL | IOD_GSM | GSM:.PMMfaza05
GSMPMMfaza06 | REAL | IOD_GSM | GSM:.PMMfaza06
GSMPMMfaza07 | REAL | IOD_GSM | GSM:.PMMfaza07
GSMPMMfaza08 | REAL | IOD_GSM | GSM:.PMMfaza08
GSMPMMfaza09 | REAL | IOD_GSM | GSM:.PMMfaza09
GSMPMMfaza10 | REAL | IOD_GSM | GSM:.PMMfaza10
GSMPMMfaza11 | REAL | IOD_GSM | GSM:.PMMfaza11
GSMPMMfaza12 | REAL | IOD_GSM | GSM:.PMMfaza12
GSMPMMfaza13 | REAL | IOD_GSM | GSM:.PMMfaza13
GSMPMMfaza14 | REAL | IOD_GSM | GSM:.PMMfaza14
GSMPMMfaza15 | REAL | IOD_GSM | GSM:.PMMfaza15
GSMPMMfaza16 | REAL | IOD_GSM | GSM:.PMMfaza16
GSMPMMfaza17 | REAL | IOD_GSM | GSM:.PMMfaza17
GSMPMMfaza18 | REAL | IOD_GSM | GSM:.PMMfaza18
GSMPMMfaza19 | REAL | IOD_GSM | GSM:.PMMfaza19
GSMPMMfaza20 | REAL | IOD_GSM | GSM:.PMMfaza20
GSMPMMfaza21 | REAL | IOD_GSM | GSM:.PMMfaza21
GSMPMMfaza22 | REAL | IOD_GSM | GSM:.PMMfaza22
GSMPMMfaza23 | REAL | IOD_GSM | GSM:.PMMfaza23
GSMPMMfaza24 | REAL | IOD_GSM | GSM:.PMMfaza24
GSMPMMfaza25 | REAL | IOD_GSM | GSM:.PMMfaza25
GSMPMMfaza26 | REAL | IOD_GSM | GSM:.PMMfaza26
GSMPMMfaza27 | REAL | IOD_GSM | GSM:.PMMfaza27
GSMPMMfaza28 | REAL | IOD_GSM | GSM:.PMMfaza28
GSMPMMfaza29 | REAL | IOD_GSM | GSM:.PMMfaza29
GSMPMMfaza30 | REAL | IOD_GSM | GSM:.PMMfaza30
GSMPMMfaza31 | REAL | IOD_GSM | GSM:.PMMfaza31
GSMPMMfaza32 | REAL | IOD_GSM | GSM:.PMMfaza32
GSMPMMfaza33 | REAL | IOD_GSM | GSM:.PMMfaza33
GSMPMMfaza34 | REAL | IOD_GSM | GSM:.PMMfaza34
GSMPMMfaza35 | REAL | IOD_GSM | GSM:.PMMfaza35
GSMPMMfaza36 | REAL | IOD_GSM | GSM:.PMMfaza36
GSMPMMfaza37 | REAL | IOD_GSM | GSM:.PMMfaza37
GSMPMMfaza38 | REAL | IOD_GSM | GSM:.PMMfaza38
GSMPMMfaza39 | REAL | IOD_GSM | GSM:.PMMfaza39
GSMPMMfaza40 | REAL | IOD_GSM | GSM:.PMMfaza40
GSMPMMfaza41 | REAL | IOD_GSM | GSM:.PMMfaza41
GSMPMMfaza42 | REAL | IOD_GSM | GSM:.PMMfaza42
GSMPMMskupniTokA | REAL | IOD_GSM | GSM:.PMMskupniTokA
GSMPMMskupniTokB | REAL | IOD_GSM | GSM:.PMMskupniTokB
GSMPozarnaCentrala_skupno | DIGITAL | IOD_GSM | GSM:.PozarnaCentrala_skupno
GSMPrevisokaTemp | DIGITAL | IOD_GSM | GSM:.PrevisokaTemp
GSMQ0_izkljuceno | DIGITAL | IOD_GSM | GSM:.Q0_izkljuceno
GSMQ0_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q0_vkljuceno
GSMQ12_izkljuceno | DIGITAL | IOD_GSM | GSM:.Q12_izkljuceno
GSMQ12_izpad | DIGITAL | IOD_GSM | GSM:.Q12_izpad
GSMQ12_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q12_vkljuceno
GSMQ12stanje | BYTE | IOD_GSM | GSM:.Q12stanje
GSMQ21_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q21_vkljuceno
GSMQ22_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q22_vkljuceno
GSMrazlitjeLAH1 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH1
GSMrazlitjeLAH2 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH2
GSMrazlitjeLAH3 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH3
GSMrazlitjeLAH4 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH4
GSMSetDateTime | DIGITAL | IOD_GSM | GSM:.SetDateTime
GSMSetDateTimeDemand | DIGITAL | IOD_GSM | GSM:.SetDateTimeDemand
GSMSetDateTimeError | DIGITAL | IOD_GSM | GSM:.SetDateTimeError
GSMSetDateTimeFinished | DIGITAL | IOD_GSM | GSM:.SetDateTimeFinished
GSMSkupneNapakeNaprav_PMM17VirBVirA | DIGITAL | IOD_GSM | GSM:.SkupneNapakeNaprav_PMM17VirBVirA
GSMSlabaBaterijaPLC | DIGITAL | IOD_GSM | GSM:.SlabaBaterijaPLC
GSMTempHistereza | INT | IOD_GSM | GSM:.TempHistereza
GSMTempPovp234 | INT | IOD_GSM | GSM:.TempPovp234
GSMTempPovp234Alarm | INT | IOD_GSM | GSM:.TempPovp234Alarm
GSMTempPovp234Previs | DIGITAL | IOD_GSM | GSM:.TempPovp234Previs
GSMTempPovp56 | INT | IOD_GSM | GSM:.TempPovp56
GSMTempPovp56Alarm | INT | IOD_GSM | GSM:.TempPovp56Alarm
GSMTempPovp56Previs | DIGITAL | IOD_GSM | GSM:.TempPovp56Previs
GSMTempZaVklopKlim1 | INT | IOD_GSM | GSM:.TempZaVklopKlim1
GSMTempZaVklopKlim2 | INT | IOD_GSM | GSM:.TempZaVklopKlim2
GSMTIA1_alarm | INT | IOD_GSM | GSM:.TIA1_alarm
GSMTIA1_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA1_previs_temp
GSMTIA1_temp_s | INT | IOD_GSM | GSM:.TIA1_temp_s
GSMTIA2_alarm | INT | IOD_GSM | GSM:.TIA2_alarm
GSMTIA2_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA2_previs_temp
GSMTIA2_temp_s | INT | IOD_GSM | GSM:.TIA2_temp_s
GSMTIA3_alarm | INT | IOD_GSM | GSM:.TIA3_alarm
GSMTIA3_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA3_previs_temp
GSMTIA3_temp_s | INT | IOD_GSM | GSM:.TIA3_temp_s
GSMTIA4_alarm | INT | IOD_GSM | GSM:.TIA4_alarm
GSMTIA4_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA4_previs_temp
GSMTIA4_temp_s | INT | IOD_GSM | GSM:.TIA4_temp_s
GSMTIA5_alarm | INT | IOD_GSM | GSM:.TIA5_alarm
GSMTIA5_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA5_previs_temp
GSMTIA5_temp_s | INT | IOD_GSM | GSM:.TIA5_temp_s
GSMTIA6_alarm | INT | IOD_GSM | GSM:.TIA6_alarm
GSMTIA6_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA6_previs_temp
GSMTIA6_temp_s | INT | IOD_GSM | GSM:.TIA6_temp_s
GSMTIA7_alarm | INT | IOD_GSM | GSM:.TIA7_alarm
GSMTIA7_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA7_previs_temp
GSMTIA7_temp_s | INT | IOD_GSM | GSM:.TIA7_temp_s
GSMUPS1_StatusBaterije | UINT | IOD_GSM | GSM:.UPS1_StatusBaterije
GSMUPS1Errors10 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[10]
GSMUPS1Errors11 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[11]
GSMUPS1Errors12 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[12]
GSMUPS1Errors13 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[13]
GSMUPS1Errors14 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[14]
GSMUPS1Errors15 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[15]
GSMUPS1Errors16 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[16]
GSMUPS1Errors17 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[17]
GSMUPS1Errors18 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[18]
GSMUPS1Errors19 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[19]
GSMUPS1Errors1 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[1]
GSMUPS1Errors20 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[20]
GSMUPS1Errors21 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[21]
GSMUPS1Errors22 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[22]
GSMUPS1Errors23 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[23]
GSMUPS1Errors24 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[24]
GSMUPS1Errors25 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[25]
GSMUPS1Errors2 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[2]
GSMUPS1Errors3 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[3]
GSMUPS1Errors4 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[4]
GSMUPS1Errors5 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[5]
GSMUPS1Errors6 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[6]
GSMUPS1Errors7 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[7]
GSMUPS1Errors8 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[8]
GSMUPS1Errors9 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[9]
GSMUPS2_StatusBaterije | UINT | IOD_GSM | GSM:.UPS2_StatusBaterije
GSMUPS2Errors10 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[10]
GSMUPS2Errors11 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[11]
GSMUPS2Errors12 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[12]
GSMUPS2Errors13 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[13]
GSMUPS2Errors14 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[14]
GSMUPS2Errors15 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[15]
GSMUPS2Errors16 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[16]
GSMUPS2Errors17 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[17]
GSMUPS2Errors18 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[18]
GSMUPS2Errors19 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[19]
GSMUPS2Errors1 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[1]
GSMUPS2Errors20 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[20]
GSMUPS2Errors21 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[21]
GSMUPS2Errors22 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[22]
GSMUPS2Errors23 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[23]
GSMUPS2Errors24 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[24]
GSMUPS2Errors25 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[25]
GSMUPS2Errors2 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[2]
GSMUPS2Errors3 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[3]
GSMUPS2Errors4 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[4]
GSMUPS2Errors5 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[5]
GSMUPS2Errors6 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[6]
GSMUPS2Errors7 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[7]
GSMUPS2Errors8 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[8]
GSMUPS2Errors9 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[9]
GSMUPS3_StatusBaterije | UINT | IOD_GSM | GSM:.UPS3_StatusBaterije
GSMUPS3Errors10 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[10]
GSMUPS3Errors11 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[11]
GSMUPS3Errors12 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[12]
GSMUPS3Errors13 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[13]
GSMUPS3Errors14 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[14]
GSMUPS3Errors15 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[15]
GSMUPS3Errors16 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[16]
GSMUPS3Errors17 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[17]
GSMUPS3Errors18 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[18]
GSMUPS3Errors19 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[19]
GSMUPS3Errors1 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[1]
GSMUPS3Errors20 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[20]
GSMUPS3Errors21 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[21]
GSMUPS3Errors22 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[22]
GSMUPS3Errors23 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[23]
GSMUPS3Errors24 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[24]
GSMUPS3Errors25 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[25]
GSMUPS3Errors2 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[2]
GSMUPS3Errors3 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[3]
GSMUPS3Errors4 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[4]
GSMUPS3Errors5 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[5]
GSMUPS3Errors6 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[6]
GSMUPS3Errors7 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[7]
GSMUPS3Errors8 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[8]
GSMUPS3Errors9 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[9]
GSMUPS1AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmAwaitingPower
GSMUPS1AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmBypassBad
GSMUPS1AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmChargerFailed
GSMUPS1AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmCommunicationsLost
GSMUPS1AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmDepletedBattery
GSMUPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmDiagnosticTestFailed
GSMUPS1AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmInverterError
GSMUPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmIzhodOffKotZahtevano
GSMUPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmIzhodPreobremenjen
GSMUPS1AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmLowBattery
GSMUPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmNapakaNaVarovalki
GSMUPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmNapakaNaVentilatorju
GSMUPS1AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmOnBattery
GSMUPS1AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmOnBypass
GSMUPS1AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmShutdownImminent
GSMUPS1AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmShutdownPending
GSMUPS1AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmSlabaBaterija
GSMUPS1AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmSplosnaNapaka
GSMUPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmStanjeIzhodaIzvenToleranc
GSMUPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmStanjeVhodaIzvenToleranc
GSMUPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmTemperaturaIzvenToleranc
GSMUPS1AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmTestInProgres
GSMUPS1AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSIzhodOff
GSMUPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSOffKotZahtevano
GSMUPS1AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSSystemOff
GSMUPS1EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[1].EstimatedChargeRemaining
GSMUPS1EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[1].EstimatedMinutesRemaining
GSMUPS1InverterStatus | INT | IOD_GSM | GSM:.UPS[1].InverterStatus
GSMUPS1IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL1
GSMUPS1IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL2
GSMUPS1IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL3
GSMUPS1Napaka | DIGITAL | IOD_GSM | GSM:.UPS[1].Napaka
GSMUPS1NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[1].NapetostBaterije
GSMUPS1OutputStatus | INT | IOD_GSM | GSM:.UPS[1].OutputStatus
GSMUPS1StatusBaterije | UINT | IOD_GSM | GSM:.UPS[1].StatusBaterije
GSMUPS1StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusEcomodeAktiven
GSMUPS1StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusInverterIsOn
GSMUPS1StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusStopOperation
GSMUPS1SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[1].SteviloIzpadovVhodneLinije
GSMUPS1TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[1].TemperaturaBaterije
GSMUPS1UnitStatus | INT | IOD_GSM | GSM:.UPS[1].UnitStatus
GSMUPS1VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL1
GSMUPS1VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL2
GSMUPS1VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL3
GSMUPS1VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL1
GSMUPS1VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL2
GSMUPS1VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL3
GSMUPS2AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmAwaitingPower
GSMUPS2AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmBypassBad
GSMUPS2AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmChargerFailed
GSMUPS2AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmCommunicationsLost
GSMUPS2AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmDepletedBattery
GSMUPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmDiagnosticTestFailed
GSMUPS2AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmInverterError
GSMUPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmIzhodOffKotZahtevano
GSMUPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmIzhodPreobremenjen
GSMUPS2AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmLowBattery
GSMUPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmNapakaNaVarovalki
GSMUPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmNapakaNaVentilatorju
GSMUPS2AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmOnBattery
GSMUPS2AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmOnBypass
GSMUPS2AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmShutdownImminent
GSMUPS2AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmShutdownPending
GSMUPS2AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmSlabaBaterija
GSMUPS2AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmSplosnaNapaka
GSMUPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmStanjeIzhodaIzvenToleranc
GSMUPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmStanjeVhodaIzvenToleranc
GSMUPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmTemperaturaIzvenToleranc
GSMUPS2AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmTestInProgres
GSMUPS2AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSIzhodOff
GSMUPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSOffKotZahtevano
GSMUPS2AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSSystemOff
GSMUPS2EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[2].EstimatedChargeRemaining
GSMUPS2EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[2].EstimatedMinutesRemaining
GSMUPS2InverterStatus | INT | IOD_GSM | GSM:.UPS[2].InverterStatus
GSMUPS2IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL1
GSMUPS2IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL2
GSMUPS2IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL3
GSMUPS2Napaka | DIGITAL | IOD_GSM | GSM:.UPS[2].Napaka
GSMUPS2NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[2].NapetostBaterije
GSMUPS2OutputStatus | INT | IOD_GSM | GSM:.UPS[2].OutputStatus
GSMUPS2StatusBaterije | UINT | IOD_GSM | GSM:.UPS[2].StatusBaterije
GSMUPS2StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusEcomodeAktiven
GSMUPS2StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusInverterIsOn
GSMUPS2StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusStopOperation
GSMUPS2SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[2].SteviloIzpadovVhodneLinije
GSMUPS2TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[2].TemperaturaBaterije
GSMUPS2UnitStatus | INT | IOD_GSM | GSM:.UPS[2].UnitStatus
GSMUPS2VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL1
GSMUPS2VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL2
GSMUPS2VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL3
GSMUPS2VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL1
GSMUPS2VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL2
GSMUPS2VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL3
GSMUPS3AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmAwaitingPower
GSMUPS3AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmBypassBad
GSMUPS3AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmChargerFailed
GSMUPS3AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmCommunicationsLost
GSMUPS3AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmDepletedBattery
GSMUPS3AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmDiagnosticTestFailed
GSMUPS3AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmInverterError
GSMUPS3AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmIzhodOffKotZahtevano
GSMUPS3AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmIzhodPreobremenjen
GSMUPS3AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmLowBattery
GSMUPS3AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmNapakaNaVarovalki
GSMUPS3AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmNapakaNaVentilatorju
GSMUPS3AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmOnBattery
GSMUPS3AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmOnBypass
GSMUPS3AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmShutdownImminent
GSMUPS3AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmShutdownPending
GSMUPS3AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmSlabaBaterija
GSMUPS3AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmSplosnaNapaka
GSMUPS3AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmStanjeIzhodaIzvenToleranc
GSMUPS3AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmStanjeVhodaIzvenToleranc
GSMUPS3AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmTemperaturaIzvenToleranc
GSMUPS3AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmTestInProgres
GSMUPS3AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSIzhodOff
GSMUPS3AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSOffKotZahtevano
GSMUPS3AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSSystemOff
GSMUPS3EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[3].EstimatedChargeRemaining
GSMUPS3EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[3].EstimatedMinutesRemaining
GSMUPS3InverterStatus | INT | IOD_GSM | GSM:.UPS[3].InverterStatus
GSMUPS3IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL1
GSMUPS3IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL2
GSMUPS3IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL3
GSMUPS3Napaka | DIGITAL | IOD_GSM | GSM:.UPS[3].Napaka
GSMUPS3NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[3].NapetostBaterije
GSMUPS3OutputStatus | INT | IOD_GSM | GSM:.UPS[3].OutputStatus
GSMUPS3StatusBaterije | UINT | IOD_GSM | GSM:.UPS[3].StatusBaterije
GSMUPS3StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusEcomodeAktiven
GSMUPS3StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusInverterIsOn
GSMUPS3StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusStopOperation
GSMUPS3SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[3].SteviloIzpadovVhodneLinije
GSMUPS3TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[3].TemperaturaBaterije
GSMUPS3UnitStatus | INT | IOD_GSM | GSM:.UPS[3].UnitStatus
GSMUPS3VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL1
GSMUPS3VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL2
GSMUPS3VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL3
GSMUPS3VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL1
GSMUPS3VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL2
GSMUPS3VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL3
GSMUPS_A_V23_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_A_V23_delovanje
GSMUPS_A_V23_napaka | DIGITAL | IOD_GSM | GSM:.UPS_A_V23_napaka
GSMups_alarm | DIGITAL | IOD_GSM | GSM:.ups_alarm
GSMups_baterijski_nac | DIGITAL | IOD_GSM | GSM:.ups_baterijski_nac
GSMUPS_MGE1BatteryBackupTime | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryBackupTime
GSMUPS_MGE1BatteryChargedState | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryChargedState
GSMUPS_MGE1BatteryChargingLevel | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryChargingLevel
GSMUPS_MGE1BatteryCircuitBreaker | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryCircuitBreaker
GSMUPS_MGE1BatteryCompInProgress | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryCompInProgress
GSMUPS_MGE1BatteryFuseFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryFuseFault
GSMUPS_MGE1BatteryLowWarning | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryLowWarning
GSMUPS_MGE1BatteryRechargeDuration | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryRechargeDuration
GSMUPS_MGE1BatteryTempOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryTempOutOfToler
GSMUPS_MGE1BypassInFreeFrequency | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BypassInFreeFrequency
GSMUPS_MGE1ChargerGeneralFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].ChargerGeneralFault
GSMUPS_MGE1DeviceVentilationFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].DeviceVentilationFault
GSMUPS_MGE1I1output | INT | IOD_GSM | GSM:.UPS_MGE[1].I1output
GSMUPS_MGE1I2output | INT | IOD_GSM | GSM:.UPS_MGE[1].I2output
GSMUPS_MGE1I3output | INT | IOD_GSM | GSM:.UPS_MGE[1].I3output
GSMUPS_MGE1InverterFrequency | INT | IOD_GSM | GSM:.UPS_MGE[1].InverterFrequency
GSMUPS_MGE1InverterFuseFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterFuseFault
GSMUPS_MGE1InverterOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterOverload
GSMUPS_MGE1InverterThermalOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterThermalOverload
GSMUPS_MGE1Mains1VoltOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains1VoltOutOfToler
GSMUPS_MGE1Mains2Overload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains2Overload
GSMUPS_MGE1Mains2VoltOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains2VoltOutOfToler
GSMUPS_MGE1MaintenancePosition | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].MaintenancePosition
GSMUPS_MGE1ManualBypassSwitch | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].ManualBypassSwitch
GSMUPS_MGE1NapakaNaVarovalkah | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].NapakaNaVarovalkah
GSMUPS_MGE1OutputActivePower1 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower1
GSMUPS_MGE1OutputActivePower2 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower2
GSMUPS_MGE1OutputActivePower3 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower3
GSMUPS_MGE1OutputFrequency | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputFrequency
GSMUPS_MGE1OutputInShortCircuit | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputInShortCircuit
GSMUPS_MGE1OutputLoadLevel | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputLoadLevel
GSMUPS_MGE1OutputOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputOverload
GSMUPS_MGE1OutputThermalOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputThermalOverload
GSMUPS_MGE1RectifierOn | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].RectifierOn
GSMUPS_MGE1RectifierThermOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].RectifierThermOverload
GSMUPS_MGE1Skupna_napaka | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Skupna_napaka
GSMUPS_MGE1StatusBaterije | BYTE | IOD_GSM | GSM:.UPS_MGE[1].StatusBaterije
GSMUPS_MGE1U12mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U12mains1
GSMUPS_MGE1U12mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U12mains2
GSMUPS_MGE1U1N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U1N_inverter
GSMUPS_MGE1U1N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U1N_output
GSMUPS_MGE1U23mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U23mains1
GSMUPS_MGE1U23mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U23mains2
GSMUPS_MGE1U2N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U2N_inverter
GSMUPS_MGE1U2N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U2N_output
GSMUPS_MGE1U31mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U31mains1
GSMUPS_MGE1U31mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U31mains2
GSMUPS_MGE1U3N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U3N_inverter
GSMUPS_MGE1U3N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U3N_output
GSMUPS_MGE1U_battery | INT | IOD_GSM | GSM:.UPS_MGE[1].U_battery
GSMUPS_MGE1UPS_coupled | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_coupled
GSMUPS_MGE1UPS_error | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_error
GSMUPS_MGE1UPS_in_backup | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_in_backup
GSMups_polnjenje | DIGITAL | IOD_GSM | GSM:.ups_polnjenje
GSMUPS_V23_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_V23_delovanje
GSMUPS_V23_napaka | DIGITAL | IOD_GSM | GSM:.UPS_V23_napaka
GSMUPS_V25_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_V25_delovanje
GSMUPS_V25_napaka | DIGITAL | IOD_GSM | GSM:.UPS_V25_napaka
GSMUPSMGEErrors10 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[10]
GSMUPSMGEErrors11 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[11]
GSMUPSMGEErrors12 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[12]
GSMUPSMGEErrors13 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[13]
GSMUPSMGEErrors14 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[14]
GSMUPSMGEErrors15 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[15]
GSMUPSMGEErrors16 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[16]
GSMUPSMGEErrors17 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[17]
GSMUPSMGEErrors1 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[1]
GSMUPSMGEErrors2 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[2]
GSMUPSMGEErrors3 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[3]
GSMUPSMGEErrors4 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[4]
GSMUPSMGEErrors5 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[5]
GSMUPSMGEErrors6 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[6]
GSMUPSMGEErrors7 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[7]
GSMUPSMGEErrors8 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[8]
GSMUPSMGEErrors9 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[9]
GSMUserCurrentLevel | BYTE | IOD_GSM | GSM:.UserCurrentLevel
GSMUserCurrentName | STRING | IOD_GSM | GSM:.UserCurrentName
GSMUserDisplay | STRING | IOD_GSM | GSM:.UserDisplay
GSMUserLoggedIn | DIGITAL | IOD_GSM | GSM:.UserLoggedIn
GSMVLAZILEC1_delovanje | DIGITAL | IOD_GSM | GSM:.VLAZILEC1_delovanje
GSMVLAZILEC1_napaka | DIGITAL | IOD_GSM | GSM:.VLAZILEC1_napaka
GSMVLAZILEC2_delovanje | DIGITAL | IOD_GSM | GSM:.VLAZILEC2_delovanje
GSMVLAZILEC2_napaka | DIGITAL | IOD_GSM | GSM:.VLAZILEC2_napaka
GSMXVH_AlarmOn | DIGITAL | IOD_GSM | GSM:.XVH_AlarmOn
GSMXVH_enopolna_napaka | DIGITAL | IOD_GSM | GSM:.XVH_enopolna_napaka
GSM_DanEnergCirc1 | LONG | IOD_GSM_disk | L0[30]
GSM_CasDDanEnergCirc1 | INT | IOD_GSM_disk | I0[30]
GSM_CasMDanEnergCirc1 | INT | IOD_GSM_disk | I30[30]
GSM_TedenEnergCirc1 | LONG | IOD_GSM_disk | L30[30]
GSM_CasDTedenEnergCirc1 | INT | IOD_GSM_disk | I60[30]
GSM_CasMTedenEnergCirc1 | INT | IOD_GSM_disk | I90[30]
GSM_MesecEnergCirc1 | LONG | IOD_GSM_disk | L90[30]
GSM_CasDMesecEnergCirc1 | INT | IOD_GSM_disk | I120[30]
GSM_CasMMesecEnergCirc1 | INT | IOD_GSM_disk | I150[30]
GSM_StSt_DanEnergCirc1 | LONG | IOD_GSM_disk | L270
GSM_StSt_TedenEnergCirc1 | LONG | IOD_GSM_disk | L272
GSM_StSt_MesecEnergCirc1 | LONG | IOD_GSM_disk | L274
GSM_StStCasDDanEnergCirc1 | INT | IOD_GSM_disk | I276
GSM_StStCasMDanEnergCirc1 | INT | IOD_GSM_disk | I277
GSM_StStCasDTedenEnergCirc1 | INT | IOD_GSM_disk | I278
GSM_StStCasMTedenEnergCirc1 | INT | IOD_GSM_disk | I279
GSM_StStCasDMesecEnergCirc1 | INT | IOD_GSM_disk | I280
GSM_StStCasMMesecEnergCirc1 | INT | IOD_GSM_disk | I281
GSM_MaxDnevnaEnergija | LONG | IOD_GSM_disk | L282 | 0 | 9999999 | 0 | 9999999 | #######
GSM_MaxMesecnaEnergija | LONG | IOD_GSM_disk | L284 | 0 | 9999999 | 0 | 9999999 | #######
GSM_MaxTedenskaEnergija | LONG | IOD_GSM_disk | L286 | 0 | 9999999 | 0 | 9999999 | #######
GSM_Prikaz_analizatorja_ce_je_1 | DIGITAL | IOD_GSM_mem | D287
GSMPMM_2x17_VirA_zavihek | DIGITAL | IOD_GSM_disk | D288
GSMPMM_2x17_VirB_zavihek | DIGITAL | IOD_GSM_disk | D289
GSMServer_B_Izpad | DIGITAL | IOD_GSM_mem | D566
GSMServer_A_Izpad | DIGITAL | IOD_GSM_mem | D567
GSM_meja_tok_opozoriloL1 | INT | IOD_GSM_disk | I300
GSM_meja_tok_opozoriloL2 | INT | IOD_GSM_disk | I302
GSM_meja_tok_opozoriloL3 | INT | IOD_GSM_disk | I304
GSM_meja_tok_alarmL1 | INT | IOD_GSM_disk | I306
GSM_meja_tok_alarmL2 | INT | IOD_GSM_disk | I308
GSM_meja_tok_alarmL3 | INT | IOD_GSM_disk | I310
GSM_omogocanje_tok_opozorilaL1 | DIGITAL | IOD_GSM_disk | D312
GSM_omogocanje_tok_opozorilaL2 | DIGITAL | IOD_GSM_disk | D313
GSM_omogocanje_tok_opozorilaL3 | DIGITAL | IOD_GSM_disk | D314
GSM_omogocanje_tok_alarmL1 | DIGITAL | IOD_GSM_disk | D315
GSM_omogocanje_tok_alarmL2 | DIGITAL | IOD_GSM_disk | D316
GSM_omogocanje_tok_alarmL3 | DIGITAL | IOD_GSM_disk | D317
GSMErrComCirc1_om | DIGITAL | IOD_GSM_disk | D318
GSMErrComKlima1_om | DIGITAL | IOD_GSM_disk | D319
GSMErrComKlima2_om | DIGITAL | IOD_GSM_disk | D320
GSMErrComPMM1_om | DIGITAL | IOD_GSM_disk | D321
GSMErrComPort2_om | DIGITAL | IOD_GSM_disk | D322
GSMErrComPort3_om | DIGITAL | IOD_GSM_disk | D323
GSMErrComPort4_om | DIGITAL | IOD_GSM_disk | D324
GSMErrComUPS1_om | DIGITAL | IOD_GSM_disk | D325
GSMErrComUPS2_om | DIGITAL | IOD_GSM_disk | D326
GSMErrComUPSMGE1_om | DIGITAL | IOD_GSM_disk | D327
GSMrazlitjeLAH1_om | DIGITAL | IOD_GSM_disk | D328
GSMrazlitjeLAH2_om | DIGITAL | IOD_GSM_disk | D329
GSMrazlitjeLAH3_om | DIGITAL | IOD_GSM_disk | D330
GSMrazlitjeLAH4_om | DIGITAL | IOD_GSM_disk | D331
GSMServer_A_Izpad_om | DIGITAL | IOD_GSM_disk | D332
GSMServer_B_Izpad_om | DIGITAL | IOD_GSM_disk | D333
GSMnapaka_kom_panel_om | DIGITAL | IOD_GSM_disk | D334
GSMSetDateTimeError_om | DIGITAL | IOD_GSM_disk | D335
GSMSlabaBaterijaPLC_om | DIGITAL | IOD_GSM_disk | D336
GSMups_baterijski_nac_om | DIGITAL | IOD_GSM_disk | D337
GSMups_alarm_om | DIGITAL | IOD_GSM_disk | D338
GSMups_polnjenje_om | DIGITAL | IOD_GSM_disk | D339
GSMQ0_izkljuceno_om | DIGITAL | IOD_GSM_disk | D340
GSMQ0_vkljuceno_om | DIGITAL | IOD_GSM_disk | D341
GSMQ12_izkljuceno_om | DIGITAL | IOD_GSM_disk | D342
GSMQ12_izpad_om | DIGITAL | IOD_GSM_disk | D343
GSMQ12_vkljuceno_om | DIGITAL | IOD_GSM_disk | D344
GSMN_F1_1_zascita_ok_om | DIGITAL | IOD_GSM_disk | D345
GSMK1_SkupnaNapaka_om | DIGITAL | IOD_GSM_disk | D346
GSMK1AlarmPozara_om | DIGITAL | IOD_GSM_disk | D347
GSMK1KlimaZdruzenAlarm_om | DIGITAL | IOD_GSM_disk | D348
GSMK1NiPretoka_om | DIGITAL | IOD_GSM_disk | D349
GSMK1OkvaraRototerma_om | DIGITAL | IOD_GSM_disk | D350
GSMK1OkvaraVlazNap_om | DIGITAL | IOD_GSM_disk | D351
GSMK1PreobMotCrpGr_om | DIGITAL | IOD_GSM_disk | D352
GSMK1PreobMotVent_om | DIGITAL | IOD_GSM_disk | D353
GSMK1ProtizamrzZascAkt_om | DIGITAL | IOD_GSM_disk | D354
GSMK1ZamasenostFiltra_om | DIGITAL | IOD_GSM_disk | D355
GSMKLIMAT1_delovanje_om | DIGITAL | IOD_GSM_disk | D356
GSMKLIMAT1_vklop_delovanja_om | DIGITAL | IOD_GSM_disk | D357
GSMN_KLIMAT1_napaka_om | DIGITAL | IOD_GSM_disk | D358
GSMKlimeAVTO_om | DIGITAL | IOD_GSM_disk | D359
GSMKlima1_izkljucena_om | DIGITAL | IOD_GSM_disk | D360
GSMN_VLAZILEC1_napaka_om | DIGITAL | IOD_GSM_disk | D361
GSMK2_SkupnaNapaka_om | DIGITAL | IOD_GSM_disk | D362
GSMK2AlarmPozara_om | DIGITAL | IOD_GSM_disk | D363
GSMK2KlimaZdruzenAlarm_om | DIGITAL | IOD_GSM_disk | D364
GSMK2NiPretoka_om | DIGITAL | IOD_GSM_disk | D365
GSMK2OkvaraRototerma_om | DIGITAL | IOD_GSM_disk | D366
GSMK2OkvaraVlazNap_om | DIGITAL | IOD_GSM_disk | D367
GSMK2PreobMotCrpGr_om | DIGITAL | IOD_GSM_disk | D368
GSMK2PreobMotVent_om | DIGITAL | IOD_GSM_disk | D369
GSMK2ProtizamrzZascAkt_om | DIGITAL | IOD_GSM_disk | D370
GSMK2ZamasenostFiltra_om | DIGITAL | IOD_GSM_disk | D371
GSMKLIMAT2_delovanje_om | DIGITAL | IOD_GSM_disk | D372
GSMKLIMAT2_vklop_delovanja_om | DIGITAL | IOD_GSM_disk | D373
GSMN_KLIMAT2_napaka_om | DIGITAL | IOD_GSM_disk | D374
GSMKlima2_izkljucena_om | DIGITAL | IOD_GSM_disk | D375
GSMN_VLAZILEC2_napaka_om | DIGITAL | IOD_GSM_disk | D376
GSMKLIMA_m1_napaka_om | DIGITAL | IOD_GSM_disk | D377
GSMKLIMA_m2_napaka_om | DIGITAL | IOD_GSM_disk | D378
GSMKlima3_izkljucena_om | DIGITAL | IOD_GSM_disk | D379
GSMN_KLIMA1_krm_nap_ok_om | DIGITAL | IOD_GSM_disk | D380
GSMKLIMA1_kke_pogon_om | DIGITAL | IOD_GSM_disk | D381
GSMKLIMA_m1_delovanje_om | DIGITAL | IOD_GSM_disk | D382
GSMKLIMA_m2_delovanje_om | DIGITAL | IOD_GSM_disk | D383
GSMK3_deluje_om | DIGITAL | IOD_GSM_disk | D384
GSMK3_SkupnaNapaka_om | DIGITAL | IOD_GSM_disk | D385
GSMN_UPS_V23_delovanje_om | DIGITAL | IOD_GSM_disk | D386
GSMN_UPS_V23_napaka_om | DIGITAL | IOD_GSM_disk | D387
GSMUPS1AlarmSlabaBaterija_om | DIGITAL | IOD_GSM_disk | D388
GSMUPS1AlarmOnBattery_om | DIGITAL | IOD_GSM_disk | D389
GSMUPS1AlarmLowBattery_om | DIGITAL | IOD_GSM_disk | D390
GSMUPS1AlarmDepletedBattery_om | DIGITAL | IOD_GSM_disk | D391
GSMUPS1AlarmTemperaturaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D392
GSMUPS1AlarmStanjeVhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D393
GSMUPS1AlarmStanjeIzhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D394
GSMUPS1AlarmIzhodPreobremenjen_om | DIGITAL | IOD_GSM_disk | D395
GSMUPS1AlarmOnBypass_om | DIGITAL | IOD_GSM_disk | D396
GSMUPS1AlarmBypassBad_om | DIGITAL | IOD_GSM_disk | D397
GSMUPS1AlarmIzhodOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D398
GSMUPS1AlarmUPSOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D399
GSMUPS1AlarmChargerFailed_om | DIGITAL | IOD_GSM_disk | D400
GSMUPS1AlarmUPSIzhodOff_om | DIGITAL | IOD_GSM_disk | D401
GSMUPS1AlarmUPSSystemOff_om | DIGITAL | IOD_GSM_disk | D402
GSMUPS1AlarmNapakaNaVentilatorju_om | DIGITAL | IOD_GSM_disk | D403
GSMUPS1AlarmNapakaNaVarovalki_om | DIGITAL | IOD_GSM_disk | D404
GSMUPS1AlarmSplosnaNapaka_om | DIGITAL | IOD_GSM_disk | D405
GSMUPS1AlarmDiagnosticTestFailed_om | DIGITAL | IOD_GSM_disk | D406
GSMUPS1AlarmCommunicationsLost_om | DIGITAL | IOD_GSM_disk | D407
GSMUPS1AlarmAwaitingPower_om | DIGITAL | IOD_GSM_disk | D408
GSMUPS1AlarmShutdownPending_om | DIGITAL | IOD_GSM_disk | D409
GSMUPS1AlarmShutdownImminent_om | DIGITAL | IOD_GSM_disk | D410
GSMUPS1AlarmTestInProgres_om | DIGITAL | IOD_GSM_disk | D411
GSMUPS1AlarmInverterError_om | DIGITAL | IOD_GSM_disk | D412
GSMN_UPS_V25_delovanje_om | DIGITAL | IOD_GSM_disk | D413
GSMN_UPS_V25_napaka_om | DIGITAL | IOD_GSM_disk | D414
GSMUPS2AlarmSlabaBaterija_om | DIGITAL | IOD_GSM_disk | D415
GSMUPS2AlarmOnBattery_om | DIGITAL | IOD_GSM_disk | D416
GSMUPS2AlarmLowBattery_om | DIGITAL | IOD_GSM_disk | D417
GSMUPS2AlarmDepletedBattery_om | DIGITAL | IOD_GSM_disk | D418
GSMUPS2AlarmTemperaturaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D419
GSMUPS2AlarmStanjeVhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D420
GSMUPS2AlarmStanjeIzhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D421
GSMUPS2AlarmIzhodPreobremenjen_om | DIGITAL | IOD_GSM_disk | D422
GSMUPS2AlarmOnBypass_om | DIGITAL | IOD_GSM_disk | D423
GSMUPS2AlarmBypassBad_om | DIGITAL | IOD_GSM_disk | D424
GSMUPS2AlarmIzhodOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D425
GSMUPS2AlarmUPSOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D426
GSMUPS2AlarmChargerFailed_om | DIGITAL | IOD_GSM_disk | D427
GSMUPS2AlarmUPSIzhodOff_om | DIGITAL | IOD_GSM_disk | D428
GSMUPS2AlarmUPSSystemOff_om | DIGITAL | IOD_GSM_disk | D429
GSMUPS2AlarmNapakaNaVentilatorju_om | DIGITAL | IOD_GSM_disk | D430
GSMUPS2AlarmNapakaNaVarovalki_om | DIGITAL | IOD_GSM_disk | D431
GSMUPS2AlarmSplosnaNapaka_om | DIGITAL | IOD_GSM_disk | D432
GSMUPS2AlarmDiagnosticTestFailed_om | DIGITAL | IOD_GSM_disk | D433
GSMUPS2AlarmCommunicationsLost_om | DIGITAL | IOD_GSM_disk | D434
GSMUPS2AlarmAwaitingPower_om | DIGITAL | IOD_GSM_disk | D435
GSMUPS2AlarmShutdownPending_om | DIGITAL | IOD_GSM_disk | D436
GSMUPS2AlarmShutdownImminent_om | DIGITAL | IOD_GSM_disk | D437
GSMUPS2AlarmTestInProgres_om | DIGITAL | IOD_GSM_disk | D438
GSMUPS2AlarmInverterError_om | DIGITAL | IOD_GSM_disk | D439
GSMUPS_MGE1UPS_error_om | DIGITAL | IOD_GSM_disk | D440
GSMUPS_MGE1BatteryLowWarning_om | DIGITAL | IOD_GSM_disk | D441
GSMUPS_MGE1DeviceVentilationFault_om | DIGITAL | IOD_GSM_disk | D442
GSMUPS_MGE1BatteryCompInProgress_om | DIGITAL | IOD_GSM_disk | D443
GSMUPS_MGE1BatteryTempOutOfToler_om | DIGITAL | IOD_GSM_disk | D444
GSMUPS_MGE1BatteryFuseFault_om | DIGITAL | IOD_GSM_disk | D445
GSMUPS_MGE1Mains1VoltOutOfToler_om | DIGITAL | IOD_GSM_disk | D446
GSMUPS_MGE1RectifierThermOverload_om | DIGITAL | IOD_GSM_disk | D447
GSMUPS_MGE1MaintenancePosition_om | DIGITAL | IOD_GSM_disk | D448
GSMUPS_MGE1ChargerGeneralFault_om | DIGITAL | IOD_GSM_disk | D449
GSMUPS_MGE1BatteryChargedState_om | DIGITAL | IOD_GSM_disk | D450
GSMUPS_MGE1InverterOverload_om | DIGITAL | IOD_GSM_disk | D451
GSMUPS_MGE1InverterThermalOverload_om | DIGITAL | IOD_GSM_disk | D452
GSMUPS_MGE1OutputThermalOverload_om | DIGITAL | IOD_GSM_disk | D453
GSMUPS_MGE1OutputOverload_om | DIGITAL | IOD_GSM_disk | D454
GSMUPS_MGE1InverterFuseFault_om | DIGITAL | IOD_GSM_disk | D455
GSMUPS_MGE1OutputInShortCircuit_om | DIGITAL | IOD_GSM_disk | D456
GSMNapakaSenzorVlagaHIA1_om | DIGITAL | IOD_GSM_disk | D457
GSMNapakaSenzorVlagaHIA2_om | DIGITAL | IOD_GSM_disk | D458
GSMNapakaSenzorVlagaHIA3_om | DIGITAL | IOD_GSM_disk | D459
GSMNapakaSenzorVlagaHIA4_om | DIGITAL | IOD_GSM_disk | D460
GSMNapakaSenzorVlagaHIA5_om | DIGITAL | IOD_GSM_disk | D461
GSMNapakaSenzorVlagaHIA6_om | DIGITAL | IOD_GSM_disk | D462
GSMNapakaSenzorVlagaHIA7_om | DIGITAL | IOD_GSM_disk | D463
GSMNapakaTSTempTIA1_om | DIGITAL | IOD_GSM_disk | D464
GSMNapakaTSTempTIA2_om | DIGITAL | IOD_GSM_disk | D465
GSMNapakaTSTempTIA3_om | DIGITAL | IOD_GSM_disk | D466
GSMNapakaTSTempTIA4_om | DIGITAL | IOD_GSM_disk | D467
GSMNapakaTSTempTIA5_om | DIGITAL | IOD_GSM_disk | D468
GSMNapakaTSTempTIA6_om | DIGITAL | IOD_GSM_disk | D469
GSMNapakaTSTempTIA7_om | DIGITAL | IOD_GSM_disk | D470
GSMTIA1_previs_temp_om | DIGITAL | IOD_GSM_disk | D471
GSMTIA2_previs_temp_om | DIGITAL | IOD_GSM_disk | D472
GSMTIA3_previs_temp_om | DIGITAL | IOD_GSM_disk | D473
GSMTIA4_previs_temp_om | DIGITAL | IOD_GSM_disk | D474
GSMTIA5_previs_temp_om | DIGITAL | IOD_GSM_disk | D475
GSMTIA6_previs_temp_om | DIGITAL | IOD_GSM_disk | D476
GSMTIA7_previs_temp_om | DIGITAL | IOD_GSM_disk | D477
GSMPMM2OverCurrentBetw_VirA_om | DIGITAL | IOD_GSM_disk | D478
GSMPMM2OverCurrentBetw_VirB_om | DIGITAL | IOD_GSM_disk | D479
GSMPMM2OverCurrentOver_VirA_om | DIGITAL | IOD_GSM_disk | D480
GSMPMM2OverCurrentOver_VirB_om | DIGITAL | IOD_GSM_disk | D481
GSMPMM2OverCurrentBetw_VirA | DIGITAL | IOD_GSM_disk | D482
GSMPMM2OverCurrentBetw_VirB | DIGITAL | IOD_GSM_disk | D483
GSMPMM2OverCurrentOver_VirA | DIGITAL | IOD_GSM_disk | D484
GSMPMM2OverCurrentOver_VirB | DIGITAL | IOD_GSM_disk | D485
GSMAlarmPMM1VirATokPrevisok_om | DIGITAL | IOD_GSM_disk | D486
GSMAlarmPMM1VirATokVisok_om | DIGITAL | IOD_GSM_disk | D487
GSMAlarmPMM1VirBTokPrevisok_om | DIGITAL | IOD_GSM_disk | D488
GSMAlarmPMM1VirBTokVisok_om | DIGITAL | IOD_GSM_disk | D489
GSMAlarmPMM2x17nad801_om | DIGITAL | IOD_GSM_disk | D490
GSMAlarmPMM2x17nad802_om | DIGITAL | IOD_GSM_disk | D491
GSMAlarmPMM2x17nad803_om | DIGITAL | IOD_GSM_disk | D492
GSMAlarmPMM2x17nad804_om | DIGITAL | IOD_GSM_disk | D493
GSMAlarmPMM2x17nad805_om | DIGITAL | IOD_GSM_disk | D494
GSMAlarmPMM2x17nad806_om | DIGITAL | IOD_GSM_disk | D495
GSMAlarmPMM2x17nad807_om | DIGITAL | IOD_GSM_disk | D496
GSMAlarmPMM2x17nad808_om | DIGITAL | IOD_GSM_disk | D497
GSMAlarmPMM2x17nad809_om | DIGITAL | IOD_GSM_disk | D498
GSMAlarmPMM2x17nad8010_om | DIGITAL | IOD_GSM_disk | D499
GSMAlarmPMM2x17nad8011_om | DIGITAL | IOD_GSM_disk | D500
GSMAlarmPMM2x17nad8012_om | DIGITAL | IOD_GSM_disk | D501
GSMAlarmPMM2x17nad8013_om | DIGITAL | IOD_GSM_disk | D502
GSMAlarmPMM2x17nad8014_om | DIGITAL | IOD_GSM_disk | D503
GSMAlarmPMM2x17nad8015_om | DIGITAL | IOD_GSM_disk | D504
GSMAlarmPMM2x17nad8016_om | DIGITAL | IOD_GSM_disk | D505
GSMAlarmPMM2x17nad8017_om | DIGITAL | IOD_GSM_disk | D506
GSMAlarmPMM2x17nad8018_om | DIGITAL | IOD_GSM_disk | D507
GSMAlarmPMM2x17nad8019_om | DIGITAL | IOD_GSM_disk | D508
GSMAlarmPMM2x17nad8020_om | DIGITAL | IOD_GSM_disk | D509
GSMAlarmPMM2x17nad8021_om | DIGITAL | IOD_GSM_disk | D510
GSMAlarmPMM2x17nad8022_om | DIGITAL | IOD_GSM_disk | D511
GSMAlarmPMM2x17nad8023_om | DIGITAL | IOD_GSM_disk | D512
GSMAlarmPMM2x17nad8024_om | DIGITAL | IOD_GSM_disk | D513
GSMAlarmPMM2x17nad8025_om | DIGITAL | IOD_GSM_disk | D514
GSMAlarmPMM2x17nad8026_om | DIGITAL | IOD_GSM_disk | D515
GSMAlarmPMM2x17nad8027_om | DIGITAL | IOD_GSM_disk | D516
GSMAlarmPMM2x17nad8028_om | DIGITAL | IOD_GSM_disk | D517
GSMOpozoriloPMM2x17med60in801_om | DIGITAL | IOD_GSM_disk | D518
GSMOpozoriloPMM2x17med60in802_om | DIGITAL | IOD_GSM_disk | D519
GSMOpozoriloPMM2x17med60in803_om | DIGITAL | IOD_GSM_disk | D520
GSMOpozoriloPMM2x17med60in804_om | DIGITAL | IOD_GSM_disk | D521
GSMOpozoriloPMM2x17med60in805_om | DIGITAL | IOD_GSM_disk | D522
GSMOpozoriloPMM2x17med60in806_om | DIGITAL | IOD_GSM_disk | D523
GSMOpozoriloPMM2x17med60in807_om | DIGITAL | IOD_GSM_disk | D524
GSMOpozoriloPMM2x17med60in808_om | DIGITAL | IOD_GSM_disk | D525
GSMOpozoriloPMM2x17med60in809_om | DIGITAL | IOD_GSM_disk | D526
GSMOpozoriloPMM2x17med60in8010_om | DIGITAL | IOD_GSM_disk | D527
GSMOpozoriloPMM2x17med60in8011_om | DIGITAL | IOD_GSM_disk | D528
GSMOpozoriloPMM2x17med60in8012_om | DIGITAL | IOD_GSM_disk | D529
GSMOpozoriloPMM2x17med60in8013_om | DIGITAL | IOD_GSM_disk | D530
GSMOpozoriloPMM2x17med60in8014_om | DIGITAL | IOD_GSM_disk | D531
GSMOpozoriloPMM2x17med60in8015_om | DIGITAL | IOD_GSM_disk | D532
GSMOpozoriloPMM2x17med60in8016_om | DIGITAL | IOD_GSM_disk | D533
GSMOpozoriloPMM2x17med60in8017_om | DIGITAL | IOD_GSM_disk | D534
GSMOpozoriloPMM2x17med60in8018_om | DIGITAL | IOD_GSM_disk | D535
GSMOpozoriloPMM2x17med60in8019_om | DIGITAL | IOD_GSM_disk | D536
GSMOpozoriloPMM2x17med60in8020_om | DIGITAL | IOD_GSM_disk | D537
GSMOpozoriloPMM2x17med60in8021_om | DIGITAL | IOD_GSM_disk | D538
GSMOpozoriloPMM2x17med60in8022_om | DIGITAL | IOD_GSM_disk | D539
GSMOpozoriloPMM2x17med60in8023_om | DIGITAL | IOD_GSM_disk | D540
GSMOpozoriloPMM2x17med60in8024_om | DIGITAL | IOD_GSM_disk | D541
GSMOpozoriloPMM2x17med60in8025_om | DIGITAL | IOD_GSM_disk | D542
GSMOpozoriloPMM2x17med60in8026_om | DIGITAL | IOD_GSM_disk | D543
GSMOpozoriloPMM2x17med60in8027_om | DIGITAL | IOD_GSM_disk | D544
GSMOpozoriloPMM2x17med60in8028_om | DIGITAL | IOD_GSM_disk | D545
GSMN_UPS_A_V23_delovanje_om | DIGITAL | IOD_GSM_disk | D546
GSMN_UPS_A_V23_napaka_om | DIGITAL | IOD_GSM_disk | D547
GSMUPS1Napaka_om | DIGITAL | IOD_GSM_disk | D548
AGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D600[300]
BGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D900[300]
CGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D1200[300]
DGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D1500[300]
EGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D1800[300]
FGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D2100[300]
GSM_Anali_razlika_dnevnaCirc1 | LONG | IOD_GSM_disk | L290
GSM_Anali_razlika_tedenCirc1 | LONG | IOD_GSM_disk | L292
GSM_Anali_razlika_mesCirc1 | LONG | IOD_GSM_disk | L294
GSMUserloggedIn_mem | DIGITAL | IOD_GSM_mem | D572
GSM_ComSCADA_stevec1 | INT | IOD_GSM_mem | I600
GSM_ComSCADA_stevec2 | INT | IOD_GSM_mem | I601
GSM_ComSCADA_stevec3 | INT | IOD_GSM_mem | I602
GSM_ComSCADA_stevec4 | INT | IOD_GSM_mem | I603
GSMUPS2Napaka_om | DIGITAL | IOD_GSM_disk | D549
GSMUPS3AlarmSlabaBaterija_om | DIGITAL | IOD_GSM_disk | D2400
GSMUPS3AlarmOnBattery_om | DIGITAL | IOD_GSM_disk | D2401
GSMUPS3AlarmLowBattery_om | DIGITAL | IOD_GSM_disk | D2402
GSMUPS3AlarmDepletedBattery_om | DIGITAL | IOD_GSM_disk | D2403
GSMUPS3AlarmTemperaturaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D2404
GSMUPS3AlarmStanjeVhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D2405
GSMUPS3AlarmStanjeIzhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D2406
GSMUPS3AlarmIzhodPreobremenjen_om | DIGITAL | IOD_GSM_disk | D2407
GSMUPS3AlarmOnBypass_om | DIGITAL | IOD_GSM_disk | D2408
GSMUPS3AlarmBypassBad_om | DIGITAL | IOD_GSM_disk | D2409
GSMUPS3AlarmIzhodOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D2410
GSMUPS3AlarmUPSOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D2411
GSMUPS3AlarmChargerFailed_om | DIGITAL | IOD_GSM_disk | D2412
GSMUPS3AlarmUPSIzhodOff_om | DIGITAL | IOD_GSM_disk | D2413
GSMUPS3AlarmUPSSystemOff_om | DIGITAL | IOD_GSM_disk | D2414
GSMUPS3AlarmNapakaNaVentilatorju_om | DIGITAL | IOD_GSM_disk | D2415
GSMUPS3AlarmNapakaNaVarovalki_om | DIGITAL | IOD_GSM_disk | D2416
GSMUPS3AlarmSplosnaNapaka_om | DIGITAL | IOD_GSM_disk | D2417
GSMUPS3AlarmDiagnosticTestFailed_om | DIGITAL | IOD_GSM_disk | D2418
GSMUPS3AlarmCommunicationsLost_om | DIGITAL | IOD_GSM_disk | D2419
GSMUPS3AlarmAwaitingPower_om | DIGITAL | IOD_GSM_disk | D2420
GSMUPS3AlarmShutdownPending_om | DIGITAL | IOD_GSM_disk | D2421
GSMUPS3AlarmShutdownImminent_om | DIGITAL | IOD_GSM_disk | D2422
GSMUPS3AlarmTestInProgres_om | DIGITAL | IOD_GSM_disk | D2423
GSMUPS3AlarmInverterError_om | DIGITAL | IOD_GSM_disk | D2424
GSMUPS3Napaka_om | DIGITAL | IOD_GSM_disk | D2425
GSMGSM_PozCent_napaka_om | DIGITAL | IOD_GSM_disk | D2426
GSMGSM_PozSenzor_okvara_om | DIGITAL | IOD_GSM_disk | D2427
GSMGSM_Gasenje_alarm_om | DIGITAL | IOD_GSM_disk | D2428
GSMAGR_PozCent_napaka_om | DIGITAL | IOD_GSM_disk | D2429
GSMAGR_PozSenzor_okvara_om | DIGITAL | IOD_GSM_disk | D2430
GSMAGR_Gasenje_alarm_om | DIGITAL | IOD_GSM_disk | D2431
GSMCirc_Vpis_Dnevne_energija_scada1_mem | DIGITAL | IOD_GSM_disk | D3000
GSMCirc_Vpis_Dnevne_energija_scada2_mem | DIGITAL | IOD_GSM_disk | D3001
GSMCirc_Vpis_Tedenska_energija_scada1_mem | DIGITAL | IOD_GSM_disk | D3002
GSMCirc_Vpis_Tedenska_energija_scada2_mem | DIGITAL | IOD_GSM_disk | D3003
GSMCirc_Vpis_Mesecna_energija_scada1_mem | DIGITAL | IOD_GSM_disk | D3004
GSMCirc_Vpis_Mesecna_energija_scada2_mem | DIGITAL | IOD_GSM_disk | D3005
GSMPMM2VirACurrent1_med60in80 | DIGITAL | IOD_GSM_disk | D3006
GSMPMM2VirACurrent2_med60in80 | DIGITAL | IOD_GSM_disk | D3007
GSMPMM2VirACurrent3_med60in80 | DIGITAL | IOD_GSM_disk | D3008
GSMPMM2VirACurrent4_med60in80 | DIGITAL | IOD_GSM_disk | D3009
GSMPMM2VirACurrent5_med60in80 | DIGITAL | IOD_GSM_disk | D3010
GSMPMM2VirACurrent6_med60in80 | DIGITAL | IOD_GSM_disk | D3011
GSMPMM2VirACurrent7_med60in80 | DIGITAL | IOD_GSM_disk | D3012
GSMPMM2VirACurrent8_med60in80 | DIGITAL | IOD_GSM_disk | D3013
GSMPMM2VirACurrent9_med60in80 | DIGITAL | IOD_GSM_disk | D3014
GSMPMM2VirACurrent10_med60in80 | DIGITAL | IOD_GSM_disk | D3015
GSMPMM2VirACurrent11_med60in80 | DIGITAL | IOD_GSM_disk | D3016
GSMPMM2VirACurrent12_med60in80 | DIGITAL | IOD_GSM_disk | D3017
GSMPMM2VirACurrent13_med60in80 | DIGITAL | IOD_GSM_disk | D3018
GSMPMM2VirACurrent14_med60in80 | DIGITAL | IOD_GSM_disk | D3019
GSMPMM2VirACurrent15_med60in80 | DIGITAL | IOD_GSM_disk | D3020
GSMPMM2VirACurrent16_med60in80 | DIGITAL | IOD_GSM_disk | D3021
GSMPMM2VirACurrent17_med60in80 | DIGITAL | IOD_GSM_disk | D3022
GSMPMM2VirACurrent18_med60in80 | DIGITAL | IOD_GSM_disk | D3023
GSMPMM2VirACurrent19_med60in80 | DIGITAL | IOD_GSM_disk | D3024
GSMPMM2VirACurrent20_med60in80 | DIGITAL | IOD_GSM_disk | D3025
GSMPMM2VirACurrent21_med60in80 | DIGITAL | IOD_GSM_disk | D3026
GSMPMM2VirACurrent22_med60in80 | DIGITAL | IOD_GSM_disk | D3027
GSMPMM2VirACurrent23_med60in80 | DIGITAL | IOD_GSM_disk | D3028
GSMPMM2VirACurrent24_med60in80 | DIGITAL | IOD_GSM_disk | D3029
GSMPMM2VirACurrent25_med60in80 | DIGITAL | IOD_GSM_disk | D3030
GSMPMM2VirACurrent26_med60in80 | DIGITAL | IOD_GSM_disk | D3031
GSMPMM2VirACurrent27_med60in80 | DIGITAL | IOD_GSM_disk | D3032
GSMPMM2VirACurrent28_med60in80 | DIGITAL | IOD_GSM_disk | D3033
GSMPMM2VirACurrent29_med60in80 | DIGITAL | IOD_GSM_disk | D3034
GSMPMM2VirACurrent30_med60in80 | DIGITAL | IOD_GSM_disk | D3035
GSMPMM2VirACurrent31_med60in80 | DIGITAL | IOD_GSM_disk | D3036
GSMPMM2VirACurrent32_med60in80 | DIGITAL | IOD_GSM_disk | D3037
GSMPMM2VirACurrent33_med60in80 | DIGITAL | IOD_GSM_disk | D3038
GSMPMM2VirACurrent34_med60in80 | DIGITAL | IOD_GSM_disk | D3039
GSMPMM2VirACurrent35_med60in80 | DIGITAL | IOD_GSM_disk | D3040
GSMPMM2VirACurrent36_med60in80 | DIGITAL | IOD_GSM_disk | D3041
GSMPMM2VirACurrent37_med60in80 | DIGITAL | IOD_GSM_disk | D3042
GSMPMM2VirACurrent38_med60in80 | DIGITAL | IOD_GSM_disk | D3043
GSMPMM2VirACurrent39_med60in80 | DIGITAL | IOD_GSM_disk | D3044
GSMPMM2VirACurrent40_med60in80 | DIGITAL | IOD_GSM_disk | D3045
GSMPMM2VirACurrent41_med60in80 | DIGITAL | IOD_GSM_disk | D3046
GSMPMM2VirACurrent42_med60in80 | DIGITAL | IOD_GSM_disk | D3047
GSMPMM2VirACurrent43_med60in80 | DIGITAL | IOD_GSM_disk | D3048
GSMPMM2VirACurrent44_med60in80 | DIGITAL | IOD_GSM_disk | D3049
GSMPMM2VirACurrent1_nad80 | DIGITAL | IOD_GSM_disk | D3050
GSMPMM2VirACurrent2_nad80 | DIGITAL | IOD_GSM_disk | D3051
GSMPMM2VirACurrent3_nad80 | DIGITAL | IOD_GSM_disk | D3052
GSMPMM2VirACurrent4_nad80 | DIGITAL | IOD_GSM_disk | D3053
GSMPMM2VirACurrent5_nad80 | DIGITAL | IOD_GSM_disk | D3054
GSMPMM2VirACurrent6_nad80 | DIGITAL | IOD_GSM_disk | D3055
GSMPMM2VirACurrent7_nad80 | DIGITAL | IOD_GSM_disk | D3056
GSMPMM2VirACurrent8_nad80 | DIGITAL | IOD_GSM_disk | D3057
GSMPMM2VirACurrent9_nad80 | DIGITAL | IOD_GSM_disk | D3058
GSMPMM2VirACurrent10_nad80 | DIGITAL | IOD_GSM_disk | D3059
GSMPMM2VirACurrent11_nad80 | DIGITAL | IOD_GSM_disk | D3060
GSMPMM2VirACurrent12_nad80 | DIGITAL | IOD_GSM_disk | D3061
GSMPMM2VirACurrent13_nad80 | DIGITAL | IOD_GSM_disk | D3062
GSMPMM2VirACurrent14_nad80 | DIGITAL | IOD_GSM_disk | D3063
GSMPMM2VirACurrent15_nad80 | DIGITAL | IOD_GSM_disk | D3064
GSMPMM2VirACurrent16_nad80 | DIGITAL | IOD_GSM_disk | D3065
GSMPMM2VirACurrent17_nad80 | DIGITAL | IOD_GSM_disk | D3066
GSMPMM2VirACurrent18_nad80 | DIGITAL | IOD_GSM_disk | D3067
GSMPMM2VirACurrent19_nad80 | DIGITAL | IOD_GSM_disk | D3068
GSMPMM2VirACurrent20_nad80 | DIGITAL | IOD_GSM_disk | D3069
GSMPMM2VirACurrent21_nad80 | DIGITAL | IOD_GSM_disk | D3070
GSMPMM2VirACurrent22_nad80 | DIGITAL | IOD_GSM_disk | D3071
GSMPMM2VirACurrent23_nad80 | DIGITAL | IOD_GSM_disk | D3072
GSMPMM2VirACurrent24_nad80 | DIGITAL | IOD_GSM_disk | D3073
GSMPMM2VirACurrent25_nad80 | DIGITAL | IOD_GSM_disk | D3074
GSMPMM2VirACurrent26_nad80 | DIGITAL | IOD_GSM_disk | D3075
GSMPMM2VirACurrent27_nad80 | DIGITAL | IOD_GSM_disk | D3076
GSMPMM2VirACurrent28_nad80 | DIGITAL | IOD_GSM_disk | D3077
GSMPMM2VirACurrent29_nad80 | DIGITAL | IOD_GSM_disk | D3078
GSMPMM2VirACurrent30_nad80 | DIGITAL | IOD_GSM_disk | D3079
GSMPMM2VirACurrent31_nad80 | DIGITAL | IOD_GSM_disk | D3080
GSMPMM2VirACurrent32_nad80 | DIGITAL | IOD_GSM_disk | D3081
GSMPMM2VirACurrent33_nad80 | DIGITAL | IOD_GSM_disk | D3082
GSMPMM2VirACurrent34_nad80 | DIGITAL | IOD_GSM_disk | D3083
GSMPMM2VirACurrent35_nad80 | DIGITAL | IOD_GSM_disk | D3084
GSMPMM2VirACurrent36_nad80 | DIGITAL | IOD_GSM_disk | D3085
GSMPMM2VirACurrent37_nad80 | DIGITAL | IOD_GSM_disk | D3086
GSMPMM2VirACurrent38_nad80 | DIGITAL | IOD_GSM_disk | D3087
GSMPMM2VirACurrent39_nad80 | DIGITAL | IOD_GSM_disk | D3088
GSMPMM2VirACurrent40_nad80 | DIGITAL | IOD_GSM_disk | D3089
GSMPMM2VirACurrent41_nad80 | DIGITAL | IOD_GSM_disk | D3090
GSMPMM2VirACurrent42_nad80 | DIGITAL | IOD_GSM_disk | D3091
GSMPMM2VirACurrent43_nad80 | DIGITAL | IOD_GSM_disk | D3092
GSMPMM2VirACurrent44_nad80 | DIGITAL | IOD_GSM_disk | D3093
GSMPMM2PoljeVirATok1_16_nad80 | DIGITAL | IOD_GSM_disk | D3100[16]
GSMPMM2PoljeVirATok17_32_nad80 | DIGITAL | IOD_GSM_disk | D3117[16]
GSMPMM2PoljeVirATok33_44_nad80 | DIGITAL | IOD_GSM_disk | D3134[16]
GSMPMM2PoljeVirBTok1_16_nad80 | DIGITAL | IOD_GSM_disk | D3151[16]
GSMPMM2PoljeVirBTok17_32_nad80 | DIGITAL | IOD_GSM_disk | D3168[16]
GSMPMM2PoljeVirBTok33_44_nad80 | DIGITAL | IOD_GSM_disk | D3185[16]
GSMPMM2PoljeVirATok1_16_med60_80 | DIGITAL | IOD_GSM_disk | D3202[16]
GSMPMM2PoljeVirATok17_32_med60_80 | DIGITAL | IOD_GSM_disk | D3219[16]
GSMPMM2PoljeVirATok33_44_med60_80 | DIGITAL | IOD_GSM_disk | D3236[16]
GSMPMM2PoljeVirBTok1_16_med60_80 | DIGITAL | IOD_GSM_disk | D3253[16]
GSMPMM2PoljeVirBTok17_32_med60_80 | DIGITAL | IOD_GSM_disk | D3270[16]
GSMPMM2PoljeVirBTok33_44_med60_80 | DIGITAL | IOD_GSM_disk | D3287[16]
GSMPrikaziPMM | DIGITAL | IOD_GSM_disk | D3303
GSMPMM_2x63_VirB_zavihek | DIGITAL | IOD_GSM_disk | D3304
GSMPMM_2x63_VirA_zavihek | DIGITAL | IOD_GSM_disk | D3305
GSMPMM2OverCurrentBetw1_VirA | DIGITAL | IOD_GSM_disk | D3306
GSMPMM2OverCurrentBetw1_VirB | DIGITAL | IOD_GSM_disk | D3307
GSMPMM2OverCurrentOver1_VirA | DIGITAL | IOD_GSM_disk | D3308
GSMPMM2OverCurrentOver1_VirB | DIGITAL | IOD_GSM_disk | D3309
GSMPMM2OverCurrentBetw1_VirB_Omogoci | DIGITAL | IOD_GSM_disk | D3310
GSMPMM2OverCurrentBetw1_VirA_Omogoci | DIGITAL | IOD_GSM_disk | D3311
GSMPMM2OverCurrentOver1_VirB_Omogoci | DIGITAL | IOD_GSM_disk | D3312
GSMPMM2OverCurrentOver1_VirA_Omogoci | DIGITAL | IOD_GSM_disk | D3313
GSMPMM1OverVoltage_Omogoci | DIGITAL | IOD_GSM_disk | D3314
GSMErrComPMM2_Omogoci | DIGITAL | IOD_GSM_disk | D3315
GSMPMM2VirACurrent1_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3316
GSMPMM2VirACurrent2_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3317
GSMPMM2VirACurrent3_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3318
GSMPMM2VirACurrent4_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3319
GSMPMM2VirACurrent5_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3320
GSMPMM2VirACurrent6_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3321
GSMPMM2VirACurrent7_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3322
GSMPMM2VirACurrent8_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3323
GSMPMM2VirACurrent9_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3324
GSMPMM2VirACurrent10_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3325
GSMPMM2VirACurrent11_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3326
GSMPMM2VirACurrent12_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3327
GSMPMM2VirACurrent13_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3328
GSMPMM2VirACurrent14_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3329
GSMPMM2VirACurrent15_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3330
GSMPMM2VirACurrent16_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3331
GSMPMM2VirACurrent17_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3332
GSMPMM2VirACurrent18_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3333
GSMPMM2VirACurrent19_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3334
GSMPMM2VirACurrent20_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3335
GSMPMM2VirACurrent21_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3336
GSMPMM2VirACurrent22_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3337
GSMPMM2VirACurrent23_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3338
GSMPMM2VirACurrent24_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3339
GSMPMM2VirACurrent25_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3340
GSMPMM2VirACurrent26_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3341
GSMPMM2VirACurrent27_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3342
GSMPMM2VirACurrent28_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3343
GSMPMM2VirACurrent29_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3344
GSMPMM2VirACurrent30_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3345
GSMPMM2VirACurrent31_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3346
GSMPMM2VirACurrent32_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3347
GSMPMM2VirACurrent33_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3348
GSMPMM2VirACurrent34_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3349
GSMPMM2VirACurrent35_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3350
GSMPMM2VirACurrent36_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3351
GSMPMM2VirACurrent37_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3352
GSMPMM2VirACurrent38_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3353
GSMPMM2VirACurrent39_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3354
GSMPMM2VirACurrent40_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3355
GSMPMM2VirACurrent41_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3356
GSMPMM2VirACurrent42_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3357
GSMPMM2VirACurrent43_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3358
GSMPMM2VirACurrent44_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3359
GSMPMM2VirACurrent1_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3360
GSMPMM2VirACurrent2_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3361
GSMPMM2VirACurrent3_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3362
GSMPMM2VirACurrent4_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3363
GSMPMM2VirACurrent5_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3364
GSMPMM2VirACurrent6_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3365
GSMPMM2VirACurrent7_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3366
GSMPMM2VirACurrent8_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3367
GSMPMM2VirACurrent9_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3368
GSMPMM2VirACurrent10_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3369
GSMPMM2VirACurrent11_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3370
GSMPMM2VirACurrent12_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3371
GSMPMM2VirACurrent13_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3372
GSMPMM2VirACurrent14_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3373
GSMPMM2VirACurrent15_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3374
GSMPMM2VirACurrent16_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3375
GSMPMM2VirACurrent17_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3376
GSMPMM2VirACurrent18_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3377
GSMPMM2VirACurrent19_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3378
GSMPMM2VirACurrent20_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3379
GSMPMM2VirACurrent21_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3380
GSMPMM2VirACurrent22_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3381
GSMPMM2VirACurrent23_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3382
GSMPMM2VirACurrent24_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3383
GSMPMM2VirACurrent25_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3384
GSMPMM2VirACurrent26_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3385
GSMPMM2VirACurrent27_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3386
GSMPMM2VirACurrent28_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3387
GSMPMM2VirACurrent29_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3388
GSMPMM2VirACurrent30_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3389
GSMPMM2VirACurrent31_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3390
GSMPMM2VirACurrent32_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3391
GSMPMM2VirACurrent33_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3392
GSMPMM2VirACurrent34_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3393
GSMPMM2VirACurrent35_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3394
GSMPMM2VirACurrent36_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3395
GSMPMM2VirACurrent37_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3396
GSMPMM2VirACurrent38_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3397
GSMPMM2VirACurrent39_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3398
GSMPMM2VirACurrent40_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3399
GSMPMM2VirACurrent41_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3400
GSMPMM2VirACurrent42_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3401
GSMPMM2VirACurrent43_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3402
GSMPMM2VirACurrent44_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3403
GSMPMM2OverCurrentBetw1_VirB_1 | DIGITAL | IOD_GSM_disk | D3404
GSMPMM2OverCurrentBetw1_VirA_1 | DIGITAL | IOD_GSM_disk | D3405
GSMPMM2OverCurrentOver1_VirB_1 | DIGITAL | IOD_GSM_disk | D3406
GSMPMM2OverCurrentOver1_VirA_1 | DIGITAL | IOD_GSM_disk | D3407
GSMPMM2OverCurrentBetw1_VirB_2 | DIGITAL | IOD_GSM_disk | D3408
GSMPMM2OverCurrentBetw1_VirA_2 | DIGITAL | IOD_GSM_disk | D3409
GSMPMM2OverCurrentBetw1_VirB_3 | DIGITAL | IOD_GSM_disk | D3410
GSMPMM2OverCurrentBetw1_VirA_3 | DIGITAL | IOD_GSM_disk | D3411
GSMPMM2OverCurrentOver1_VirB_2 | DIGITAL | IOD_GSM_disk | D3412
GSMPMM2OverCurrentOver1_VirA_2 | DIGITAL | IOD_GSM_disk | D3413
GSMPMM2OverCurrentOver1_VirB_3 | DIGITAL | IOD_GSM_disk | D3414
GSMPMM2OverCurrentOver1_VirA_3 | DIGITAL | IOD_GSM_disk | D3415
GSMVsotaVirB_1_16B_med | INT | IOD_GSM_disk | I604
GSMVsotaVirB_17_32B_med | INT | IOD_GSM_disk | I605
GSMVsotaVirB_33_44B_med | INT | IOD_GSM_disk | I606
GSMVsotaVirA_1_16A_med | INT | IOD_GSM_disk | I607
GSMVsotaVirA_17_32A_med | INT | IOD_GSM_disk | I608
GSMVsotaVirA_33_44A_med | INT | IOD_GSM_disk | I609
GSMVsotaVirB_1_16B_nad | INT | IOD_GSM_disk | I610
GSMVsotaVirB_17_32B_nad | INT | IOD_GSM_disk | I611
GSMVsotaVirB_33_44B_nad | INT | IOD_GSM_disk | I612
GSMVsotaVirA_1_16A_nad | INT | IOD_GSM_disk | I613
GSMVsotaVirA_17_32A_nad | INT | IOD_GSM_disk | I614
GSMVsotaVirA_33_44A_nad | INT | IOD_GSM_disk | I615
GSMPMM2VirBCurrent1_med60in80 | DIGITAL | IOD_GSM_disk | D3416
GSMPMM2VirBCurrent2_med60in80 | DIGITAL | IOD_GSM_disk | D3417
GSMPMM2VirBCurrent3_med60in80 | DIGITAL | IOD_GSM_disk | D3418
GSMPMM2VirBCurrent4_med60in80 | DIGITAL | IOD_GSM_disk | D3419
GSMPMM2VirBCurrent5_med60in80 | DIGITAL | IOD_GSM_disk | D3420
GSMPMM2VirBCurrent6_med60in80 | DIGITAL | IOD_GSM_disk | D3421
GSMPMM2VirBCurrent7_med60in80 | DIGITAL | IOD_GSM_disk | D3422
GSMPMM2VirBCurrent8_med60in80 | DIGITAL | IOD_GSM_disk | D3423
GSMPMM2VirBCurrent9_med60in80 | DIGITAL | IOD_GSM_disk | D3424
GSMPMM2VirBCurrent10_med60in80 | DIGITAL | IOD_GSM_disk | D3425
GSMPMM2VirBCurrent11_med60in80 | DIGITAL | IOD_GSM_disk | D3426
GSMPMM2VirBCurrent12_med60in80 | DIGITAL | IOD_GSM_disk | D3427
GSMPMM2VirBCurrent13_med60in80 | DIGITAL | IOD_GSM_disk | D3428
GSMPMM2VirBCurrent14_med60in80 | DIGITAL | IOD_GSM_disk | D3429
GSMPMM2VirBCurrent15_med60in80 | DIGITAL | IOD_GSM_disk | D3430
GSMPMM2VirBCurrent16_med60in80 | DIGITAL | IOD_GSM_disk | D3431
GSMPMM2VirBCurrent17_med60in80 | DIGITAL | IOD_GSM_disk | D3432
GSMPMM2VirBCurrent18_med60in80 | DIGITAL | IOD_GSM_disk | D3433
GSMPMM2VirBCurrent19_med60in80 | DIGITAL | IOD_GSM_disk | D3434
GSMPMM2VirBCurrent20_med60in80 | DIGITAL | IOD_GSM_disk | D3435
GSMPMM2VirBCurrent21_med60in80 | DIGITAL | IOD_GSM_disk | D3436
GSMPMM2VirBCurrent22_med60in80 | DIGITAL | IOD_GSM_disk | D3437
GSMPMM2VirBCurrent23_med60in80 | DIGITAL | IOD_GSM_disk | D3438
GSMPMM2VirBCurrent24_med60in80 | DIGITAL | IOD_GSM_disk | D3439
GSMPMM2VirBCurrent25_med60in80 | DIGITAL | IOD_GSM_disk | D3440
GSMPMM2VirBCurrent26_med60in80 | DIGITAL | IOD_GSM_disk | D3441
GSMPMM2VirBCurrent27_med60in80 | DIGITAL | IOD_GSM_disk | D3442
GSMPMM2VirBCurrent28_med60in80 | DIGITAL | IOD_GSM_disk | D3443
GSMPMM2VirBCurrent29_med60in80 | DIGITAL | IOD_GSM_disk | D3444
GSMPMM2VirBCurrent30_med60in80 | DIGITAL | IOD_GSM_disk | D3445
GSMPMM2VirBCurrent31_med60in80 | DIGITAL | IOD_GSM_disk | D3446
GSMPMM2VirBCurrent32_med60in80 | DIGITAL | IOD_GSM_disk | D3447
GSMPMM2VirBCurrent33_med60in80 | DIGITAL | IOD_GSM_disk | D3448
GSMPMM2VirBCurrent34_med60in80 | DIGITAL | IOD_GSM_disk | D3449
GSMPMM2VirBCurrent35_med60in80 | DIGITAL | IOD_GSM_disk | D3450
GSMPMM2VirBCurrent36_med60in80 | DIGITAL | IOD_GSM_disk | D3451
GSMPMM2VirBCurrent37_med60in80 | DIGITAL | IOD_GSM_disk | D3452
GSMPMM2VirBCurrent38_med60in80 | DIGITAL | IOD_GSM_disk | D3453
GSMPMM2VirBCurrent39_med60in80 | DIGITAL | IOD_GSM_disk | D3454
GSMPMM2VirBCurrent40_med60in80 | DIGITAL | IOD_GSM_disk | D3455
GSMPMM2VirBCurrent41_med60in80 | DIGITAL | IOD_GSM_disk | D3456
GSMPMM2VirBCurrent42_med60in80 | DIGITAL | IOD_GSM_disk | D3457
GSMPMM2VirBCurrent43_med60in80 | DIGITAL | IOD_GSM_disk | D3458
GSMPMM2VirBCurrent44_med60in80 | DIGITAL | IOD_GSM_disk | D3459
GSMPMM2VirBCurrent1_nad80 | DIGITAL | IOD_GSM_disk | D3460
GSMPMM2VirBCurrent2_nad80 | DIGITAL | IOD_GSM_disk | D3461
GSMPMM2VirBCurrent3_nad80 | DIGITAL | IOD_GSM_disk | D3462
GSMPMM2VirBCurrent4_nad80 | DIGITAL | IOD_GSM_disk | D3463
GSMPMM2VirBCurrent5_nad80 | DIGITAL | IOD_GSM_disk | D3464
GSMPMM2VirBCurrent6_nad80 | DIGITAL | IOD_GSM_disk | D3465
GSMPMM2VirBCurrent7_nad80 | DIGITAL | IOD_GSM_disk | D3466
GSMPMM2VirBCurrent8_nad80 | DIGITAL | IOD_GSM_disk | D3467
GSMPMM2VirBCurrent9_nad80 | DIGITAL | IOD_GSM_disk | D3468
GSMPMM2VirBCurrent10_nad80 | DIGITAL | IOD_GSM_disk | D3469
GSMPMM2VirBCurrent11_nad80 | DIGITAL | IOD_GSM_disk | D3470
GSMPMM2VirBCurrent12_nad80 | DIGITAL | IOD_GSM_disk | D3471
GSMPMM2VirBCurrent13_nad80 | DIGITAL | IOD_GSM_disk | D3472
GSMPMM2VirBCurrent14_nad80 | DIGITAL | IOD_GSM_disk | D3473
GSMPMM2VirBCurrent15_nad80 | DIGITAL | IOD_GSM_disk | D3474
GSMPMM2VirBCurrent16_nad80 | DIGITAL | IOD_GSM_disk | D3475
GSMPMM2VirBCurrent17_nad80 | DIGITAL | IOD_GSM_disk | D3476
GSMPMM2VirBCurrent18_nad80 | DIGITAL | IOD_GSM_disk | D3477
GSMPMM2VirBCurrent19_nad80 | DIGITAL | IOD_GSM_disk | D3478
GSMPMM2VirBCurrent20_nad80 | DIGITAL | IOD_GSM_disk | D3479
GSMPMM2VirBCurrent21_nad80 | DIGITAL | IOD_GSM_disk | D3480
GSMPMM2VirBCurrent22_nad80 | DIGITAL | IOD_GSM_disk | D3481
GSMPMM2VirBCurrent23_nad80 | DIGITAL | IOD_GSM_disk | D3482
GSMPMM2VirBCurrent24_nad80 | DIGITAL | IOD_GSM_disk | D3483
GSMPMM2VirBCurrent25_nad80 | DIGITAL | IOD_GSM_disk | D3484
GSMPMM2VirBCurrent26_nad80 | DIGITAL | IOD_GSM_disk | D3485
GSMPMM2VirBCurrent27_nad80 | DIGITAL | IOD_GSM_disk | D3486
GSMPMM2VirBCurrent28_nad80 | DIGITAL | IOD_GSM_disk | D3487
GSMPMM2VirBCurrent29_nad80 | DIGITAL | IOD_GSM_disk | D3488
GSMPMM2VirBCurrent30_nad80 | DIGITAL | IOD_GSM_disk | D3489
GSMPMM2VirBCurrent31_nad80 | DIGITAL | IOD_GSM_disk | D3490
GSMPMM2VirBCurrent32_nad80 | DIGITAL | IOD_GSM_disk | D3491
GSMPMM2VirBCurrent33_nad80 | DIGITAL | IOD_GSM_disk | D3492
GSMPMM2VirBCurrent34_nad80 | DIGITAL | IOD_GSM_disk | D3493
GSMPMM2VirBCurrent35_nad80 | DIGITAL | IOD_GSM_disk | D3494
GSMPMM2VirBCurrent36_nad80 | DIGITAL | IOD_GSM_disk | D3495
GSMPMM2VirBCurrent37_nad80 | DIGITAL | IOD_GSM_disk | D3496
GSMPMM2VirBCurrent38_nad80 | DIGITAL | IOD_GSM_disk | D3497
GSMPMM2VirBCurrent39_nad80 | DIGITAL | IOD_GSM_disk | D3498
GSMPMM2VirBCurrent40_nad80 | DIGITAL | IOD_GSM_disk | D3499
GSMPMM2VirBCurrent41_nad80 | DIGITAL | IOD_GSM_disk | D3500
GSMPMM2VirBCurrent42_nad80 | DIGITAL | IOD_GSM_disk | D3501
GSMPMM2VirBCurrent43_nad80 | DIGITAL | IOD_GSM_disk | D3502
GSMPMM2VirBCurrent44_nad80 | DIGITAL | IOD_GSM_disk | D3503
GSMPMM2VirBCurrent1_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3504
GSMPMM2VirBCurrent2_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3505
GSMPMM2VirBCurrent3_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3506
GSMPMM2VirBCurrent4_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3507
GSMPMM2VirBCurrent5_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3508
GSMPMM2VirBCurrent6_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3509
GSMPMM2VirBCurrent7_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3510
GSMPMM2VirBCurrent8_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3511
GSMPMM2VirBCurrent9_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3512
GSMPMM2VirBCurrent10_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3513
GSMPMM2VirBCurrent11_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3514
GSMPMM2VirBCurrent12_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3515
GSMPMM2VirBCurrent13_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3516
GSMPMM2VirBCurrent14_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3517
GSMPMM2VirBCurrent15_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3518
GSMPMM2VirBCurrent16_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3519
GSMPMM2VirBCurrent17_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3520
GSMPMM2VirBCurrent18_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3521
GSMPMM2VirBCurrent19_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3522
GSMPMM2VirBCurrent20_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3523
GSMPMM2VirBCurrent21_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3524
GSMPMM2VirBCurrent22_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3525
GSMPMM2VirBCurrent23_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3526
GSMPMM2VirBCurrent24_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3527
GSMPMM2VirBCurrent25_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3528
GSMPMM2VirBCurrent26_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3529
GSMPMM2VirBCurrent27_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3530
GSMPMM2VirBCurrent28_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3531
GSMPMM2VirBCurrent29_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3532
GSMPMM2VirBCurrent30_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3533
GSMPMM2VirBCurrent31_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3534
GSMPMM2VirBCurrent32_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3535
GSMPMM2VirBCurrent33_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3536
GSMPMM2VirBCurrent34_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3537
GSMPMM2VirBCurrent35_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3538
GSMPMM2VirBCurrent36_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3539
GSMPMM2VirBCurrent37_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3540
GSMPMM2VirBCurrent38_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3541
GSMPMM2VirBCurrent39_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3542
GSMPMM2VirBCurrent40_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3543
GSMPMM2VirBCurrent41_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3544
GSMPMM2VirBCurrent42_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3545
GSMPMM2VirBCurrent43_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3546
GSMPMM2VirBCurrent44_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3547
GSMPMM2VirBCurrent1_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3548
GSMPMM2VirBCurrent2_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3549
GSMPMM2VirBCurrent3_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3550
GSMPMM2VirBCurrent4_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3551
GSMPMM2VirBCurrent5_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3552
GSMPMM2VirBCurrent6_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3553
GSMPMM2VirBCurrent7_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3554
GSMPMM2VirBCurrent8_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3555
GSMPMM2VirBCurrent9_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3556
GSMPMM2VirBCurrent10_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3557
GSMPMM2VirBCurrent11_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3558
GSMPMM2VirBCurrent12_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3559
GSMPMM2VirBCurrent13_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3560
GSMPMM2VirBCurrent14_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3561
GSMPMM2VirBCurrent15_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3562
GSMPMM2VirBCurrent16_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3563
GSMPMM2VirBCurrent17_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3564
GSMPMM2VirBCurrent18_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3565
GSMPMM2VirBCurrent19_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3566
GSMPMM2VirBCurrent20_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3567
GSMPMM2VirBCurrent21_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3568
GSMPMM2VirBCurrent22_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3569
GSMPMM2VirBCurrent23_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3570
GSMPMM2VirBCurrent24_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3571
GSMPMM2VirBCurrent25_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3572
GSMPMM2VirBCurrent26_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3573
GSMPMM2VirBCurrent27_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3574
GSMPMM2VirBCurrent28_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3575
GSMPMM2VirBCurrent29_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3576
GSMPMM2VirBCurrent30_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3577
GSMPMM2VirBCurrent31_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3578
GSMPMM2VirBCurrent32_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3579
GSMPMM2VirBCurrent33_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3580
GSMPMM2VirBCurrent34_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3581
GSMPMM2VirBCurrent35_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3582
GSMPMM2VirBCurrent36_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3583
GSMPMM2VirBCurrent37_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3584
GSMPMM2VirBCurrent38_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3585
GSMPMM2VirBCurrent39_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3586
GSMPMM2VirBCurrent40_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3587
GSMPMM2VirBCurrent41_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3588
GSMPMM2VirBCurrent42_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3589
GSMPMM2VirBCurrent43_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3590
GSMPMM2VirBCurrent44_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3591
GSMDI_R3KC_A_Q21_IzkljucenIzpad_Omogoci | DIGITAL | IOD_GSM_disk | D3592
GSMQ21_vkljuceno_Omogoci | DIGITAL | IOD_GSM_disk | D3593
GSMDI_R3KC_A_Q22_IzkljucenIzpad_Omogoci | DIGITAL | IOD_GSM_disk | D3594
GSMQ22_vkljuceno_Omogoci | DIGITAL | IOD_GSM_disk | D3595
GSMDI_SBi_RAZS_AA_Izolacija_NOT_OK_Omogoci | DIGITAL | IOD_GSM_disk | D3596
GSMDI_SBi_RAZS_AB_Izolacija_NOT_OK_Omogoci | DIGITAL | IOD_GSM_disk | D3597

## variable_1
GSMAGR_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.AGR_Gasenje_alarm
GSMAGR_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.AGR_PozCent_napaka
GSMAGR_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.AGR_PozSenzor_okvara
GSMAlarmGenUPS_A_V23 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_A_V23
GSMAlarmGenUPS_V23 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_V23
GSMAlarmGenUPS_V25 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_V25
GSMAlarmPMM1VirATokPrevisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirATokPrevisok
GSMAlarmPMM1VirATokVisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirATokVisok
GSMAlarmPMM1VirBTokPrevisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirBTokPrevisok
GSMAlarmPMM1VirBTokVisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirBTokVisok
GSMAlarmPMM2x17nad8010 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[10]
GSMAlarmPMM2x17nad8011 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[11]
GSMAlarmPMM2x17nad8012 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[12]
GSMAlarmPMM2x17nad8013 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[13]
GSMAlarmPMM2x17nad8014 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[14]
GSMAlarmPMM2x17nad8015 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[15]
GSMAlarmPMM2x17nad8016 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[16]
GSMAlarmPMM2x17nad8017 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[17]
GSMAlarmPMM2x17nad8018 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[18]
GSMAlarmPMM2x17nad8019 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[19]
GSMAlarmPMM2x17nad801 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[1]
GSMAlarmPMM2x17nad8020 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[20]
GSMAlarmPMM2x17nad8021 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[21]
GSMAlarmPMM2x17nad8022 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[22]
GSMAlarmPMM2x17nad8023 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[23]
GSMAlarmPMM2x17nad8024 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[24]
GSMAlarmPMM2x17nad8025 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[25]
GSMAlarmPMM2x17nad8026 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[26]
GSMAlarmPMM2x17nad8027 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[27]
GSMAlarmPMM2x17nad8028 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[28]
GSMAlarmPMM2x17nad8029 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[29]
GSMAlarmPMM2x17nad802 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[2]
GSMAlarmPMM2x17nad8030 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[30]
GSMAlarmPMM2x17nad8031 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[31]
GSMAlarmPMM2x17nad8032 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[32]
GSMAlarmPMM2x17nad8033 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[33]
GSMAlarmPMM2x17nad8034 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[34]
GSMAlarmPMM2x17nad8035 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[35]
GSMAlarmPMM2x17nad8036 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[36]
GSMAlarmPMM2x17nad8037 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[37]
GSMAlarmPMM2x17nad8038 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[38]
GSMAlarmPMM2x17nad8039 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[39]
GSMAlarmPMM2x17nad803 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[3]
GSMAlarmPMM2x17nad8040 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[40]
GSMAlarmPMM2x17nad8041 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[41]
GSMAlarmPMM2x17nad8042 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[42]
GSMAlarmPMM2x17nad804 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[4]
GSMAlarmPMM2x17nad805 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[5]
GSMAlarmPMM2x17nad806 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[6]
GSMAlarmPMM2x17nad807 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[7]
GSMAlarmPMM2x17nad808 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[8]
GSMAlarmPMM2x17nad809 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[9]
GSMALM_AGR_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.ALM_AGR_Gasenje_alarm
GSMALM_AGR_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.ALM_AGR_PozCent_napaka
GSMALM_AGR_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.ALM_AGR_PozSenzor_okvara
GSMALM_GSM_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.ALM_GSM_Gasenje_alarm
GSMALM_GSM_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.ALM_GSM_PozCent_napaka
GSMALM_GSM_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.ALM_GSM_PozSenzor_okvara
GSMcas_modbus_izpad | STRING | IOD_GSM | GSM:.cas_modbus_izpad
GSMCirc1CosFi_III | REAL | IOD_GSM | GSM:.Circ[1].CosFi_III
GSMCirc1DelovnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].DelovnaEnergija
GSMCirc1DelovnaEnergija_TEMP | REAL | IOD_GSM | GSM:.Circ[1].DelovnaEnergija_TEMP
GSMCirc1DelovnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_III
GSMCirc1DelovnaMoc_L1 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L1
GSMCirc1DelovnaMoc_L2 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L2
GSMCirc1DelovnaMoc_L3 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L3
GSMCirc1Frekvenca_L1 | REAL | IOD_GSM | GSM:.Circ[1].Frekvenca_L1
GSMCirc1InduktivnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].InduktivnaEnergija
GSMCirc1InduktivnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].InduktivnaMoc_III
GSMCirc1JalovaMoc_L1 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L1
GSMCirc1JalovaMoc_L2 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L2
GSMCirc1JalovaMoc_L3 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L3
GSMCirc1KapacitivnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].KapacitivnaEnergija
GSMCirc1KapacitivnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].KapacitivnaMoc_III
GSMCirc1MaximumDemand | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemand
GSMCirc1MaximumDemandA2 | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemandA2
GSMCirc1MaximumDemandA3 | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemandA3
GSMCirc1Napetost_L1_L2 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L1_L2
GSMCirc1Napetost_L1_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L1_N
GSMCirc1Napetost_L2_L3 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L2_L3
GSMCirc1Napetost_L2_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L2_N
GSMCirc1Napetost_L3_L1 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L3_L1
GSMCirc1Napetost_L3_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L3_N
GSMCirc1NavideznaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].NavideznaMoc_III
GSMCirc1NicelniTok | REAL | IOD_GSM | GSM:.Circ[1].NicelniTok
GSMCirc1PowerFactor_III | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_III
GSMCirc1PowerFactor_L1 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L1
GSMCirc1PowerFactor_L2 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L2
GSMCirc1PowerFactor_L3 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L3
GSMCirc1RazEner_D | REAL | IOD_GSM | GSM:.Circ[1].RazEner_D
GSMCirc1RazEner_D_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_D_SCADA
GSMCirc1RazEner_D_TEMP | REAL | IOD_GSM | GSM:.Circ[1].RazEner_D_TEMP
GSMCirc1RazEner_M | REAL | IOD_GSM | GSM:.Circ[1].RazEner_M
GSMCirc1RazEner_M_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_M_SCADA
GSMCirc1RazEner_M_TEMP | REAL | IOD_GSM | GSM:.Circ[1].RazEner_M_TEMP
GSMCirc1RazEner_T | REAL | IOD_GSM | GSM:.Circ[1].RazEner_T
GSMCirc1RazEner_T_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_T_SCADA
GSMCirc1RazEner_T_TEMP | REAL | IOD_GSM | GSM:.Circ[1].RazEner_T_TEMP
GSMCirc1THDI_L1 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L1
GSMCirc1THDI_L2 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L2
GSMCirc1THDI_L3 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L3
GSMCirc1THDV_L1 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L1
GSMCirc1THDV_L2 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L2
GSMCirc1THDV_L3 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L3
GSMCirc1Tok_L1 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L1
GSMCirc1Tok_L2 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L2
GSMCirc1Tok_L3 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L3
GSMCirc1TokPovprecje_III | REAL | IOD_GSM | GSM:.Circ[1].TokPovprecje_III
GSMCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Dnevne_energija_scada1
GSMCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Dnevne_energija_scada2
GSMCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Mesecna_energija_scada1
GSMCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Mesecna_energija_scada2
GSMCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Tedenska_energija_scada1
GSMCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Tedenska_energija_scada2
GSMComError | DIGITAL | IOD_GSM | GSM:.ComError
GSMComSCADA | DIGITAL | IOD_GSM | GSM:.ComSCADA
GSMComSCADA1 | DIGITAL | IOD_GSM | GSM:.ComSCADA1
GSMComSCADA2 | DIGITAL | IOD_GSM | GSM:.ComSCADA2
GSMComSCADA3 | DIGITAL | IOD_GSM | GSM:.ComSCADA3
GSMDate_Time0 | STRING | IOD_GSM | GSM:.Date_Time[0]
GSMDate_Time1 | STRING | IOD_GSM | GSM:.Date_Time[1]
GSMDate_Time2 | STRING | IOD_GSM | GSM:.Date_Time[2]
GSMDate_Time3 | STRING | IOD_GSM | GSM:.Date_Time[3]
GSMDateTimeDan | INT | IOD_GSM | GSM:.DateTime.Dan | BYTE
GSMDateTimeLeto | INT | IOD_GSM | GSM:.DateTime.Leto | BYTE
GSMDateTimeLeto2 | INT | IOD_GSM | GSM:.DateTime.Leto2
GSMDateTimeMesec | INT | IOD_GSM | GSM:.DateTime.Mesec | BYTE
GSMDateTimeMinuta | INT | IOD_GSM | GSM:.DateTime.Minuta | BYTE
GSMDateTimePLC_Dan | INT | IOD_GSM | GSM:.DateTime.PLC_Dan | BYTE
GSMDateTimePLC_DanVTednu | INT | IOD_GSM | GSM:.DateTime.PLC_DanVTednu | BYTE
GSMDateTimePLC_Leto | INT | IOD_GSM | GSM:.DateTime.PLC_Leto | BYTE
GSMDateTimePLC_Mesec | INT | IOD_GSM | GSM:.DateTime.PLC_Mesec | BYTE
GSMDateTimePLC_Minuta | INT | IOD_GSM | GSM:.DateTime.PLC_Minuta | BYTE
GSMDateTimePLC_Sekunda | INT | IOD_GSM | GSM:.DateTime.PLC_Sekunda | BYTE
GSMDateTimePLC_Ura | INT | IOD_GSM | GSM:.DateTime.PLC_Ura | BYTE
GSMDateTimeSekunda | INT | IOD_GSM | GSM:.DateTime.Sekunda | BYTE
GSMDateTimeUra | INT | IOD_GSM | GSM:.DateTime.Ura | BYTE
GSMDI1_I11 | DIGITAL | IOD_GSM | GSM:.DI1_I11
GSMDI1_I9 | DIGITAL | IOD_GSM | GSM:.DI1_I9
GSMDI2_I14 | DIGITAL | IOD_GSM | GSM:.DI2_I14
GSMDI2_I15 | DIGITAL | IOD_GSM | GSM:.DI2_I15
GSMDI_R3KC_A_Q21_IzkljucenIzpad | DIGITAL | IOD_GSM | GSM:.DI_R3KC_A_Q21_IzkljucenIzpad
GSMDI_R3KC_A_Q22_IzkljucenIzpad | DIGITAL | IOD_GSM | GSM:.DI_R3KC_A_Q22_IzkljucenIzpad
GSMDI_SBi_RAZS_AA_Izolacija_NOT_OK | DIGITAL | IOD_GSM | GSM:.DI_SBi_RAZS_AA_Izolacija_NOT_OK
GSMDI_SBi_RAZS_AB_Izolacija_NOT_OK | DIGITAL | IOD_GSM | GSM:.DI_SBi_RAZS_AB_Izolacija_NOT_OK
GSMErrComCirc1 | DIGITAL | IOD_GSM | GSM:.ErrComCirc[1]
GSMErrComKlima1 | DIGITAL | IOD_GSM | GSM:.ErrComKlima[1]
GSMErrComKlima2 | DIGITAL | IOD_GSM | GSM:.ErrComKlima[2]
GSMErrComPMM1 | DIGITAL | IOD_GSM | GSM:.ErrComPMM[1]
GSMErrComPMM2 | DIGITAL | IOD_GSM | GSM:.ErrComPMM[2]
GSMErrComPort2 | DIGITAL | IOD_GSM | GSM:.ErrComPort2
GSMErrComPort3 | DIGITAL | IOD_GSM | GSM:.ErrComPort3
GSMErrComPort4 | DIGITAL | IOD_GSM | GSM:.ErrComPort4
GSMErrComUPS1 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[1]
GSMErrComUPS2 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[2]
GSMErrComUPS3 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[3]
GSMErrComUPSMGE1 | DIGITAL | IOD_GSM | GSM:.ErrComUPSMGE[1]
GSMF1_1_zascita_ok | DIGITAL | IOD_GSM | GSM:.F1_1_zascita_ok
GSMGSM_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.GSM_Gasenje_alarm
GSMGSM_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.GSM_PozCent_napaka
GSMGSM_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.GSM_PozSenzor_okvara
GSMHIA1_vlaga_s | INT | IOD_GSM | GSM:.HIA1_vlaga_s
GSMHIA2_vlaga_s | INT | IOD_GSM | GSM:.HIA2_vlaga_s
GSMHIA3_vlaga_s | INT | IOD_GSM | GSM:.HIA3_vlaga_s
GSMHIA4_vlaga_s | INT | IOD_GSM | GSM:.HIA4_vlaga_s
GSMHIA5_vlaga_s | INT | IOD_GSM | GSM:.HIA5_vlaga_s
GSMHIA6_vlaga_s | INT | IOD_GSM | GSM:.HIA6_vlaga_s
GSMHIA7_vlaga_s | INT | IOD_GSM | GSM:.HIA7_vlaga_s
GSMK1_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K1_SkupnaNapaka
GSMK1_vklop_izklop_poteka | DIGITAL | IOD_GSM | GSM:.K1_vklop_izklop_poteka
GSMK1AlarmPozara | DIGITAL | IOD_GSM | GSM:.K1AlarmPozara
GSMK1KlimaZdruzenAlarm | DIGITAL | IOD_GSM | GSM:.K1KlimaZdruzenAlarm
GSMK1NiPretoka | DIGITAL | IOD_GSM | GSM:.K1NiPretoka
GSMK1obrat_ure | STRING | IOD_GSM | GSM:.K1obrat_ure
GSMK1OkvaraRototerma | DIGITAL | IOD_GSM | GSM:.K1OkvaraRototerma
GSMK1OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.K1OkvaraVlazNap
GSMK1PreobMotCrpGr | DIGITAL | IOD_GSM | GSM:.K1PreobMotCrpGr
GSMK1PreobMotVent | DIGITAL | IOD_GSM | GSM:.K1PreobMotVent
GSMK1ProtizamrzZascAkt | DIGITAL | IOD_GSM | GSM:.K1ProtizamrzZascAkt
GSMK1ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.K1ZamasenostFiltra
GSMK2_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K2_SkupnaNapaka
GSMK2_vklop_izklop_poteka | DIGITAL | IOD_GSM | GSM:.K2_vklop_izklop_poteka
GSMK2AlarmPozara | DIGITAL | IOD_GSM | GSM:.K2AlarmPozara
GSMK2KlimaZdruzenAlarm | DIGITAL | IOD_GSM | GSM:.K2KlimaZdruzenAlarm
GSMK2NiPretoka | DIGITAL | IOD_GSM | GSM:.K2NiPretoka
GSMK2OkvaraRototerma | DIGITAL | IOD_GSM | GSM:.K2OkvaraRototerma
GSMK2OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.K2OkvaraVlazNap
GSMK2PreobMotCrpGr | DIGITAL | IOD_GSM | GSM:.K2PreobMotCrpGr
GSMK2PreobMotVent | DIGITAL | IOD_GSM | GSM:.K2PreobMotVent
GSMK2ProtizamrzZascAkt | DIGITAL | IOD_GSM | GSM:.K2ProtizamrzZascAkt
GSMK2ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.K2ZamasenostFiltra
GSMK3_deluje | DIGITAL | IOD_GSM | GSM:.K3_deluje
GSMK3_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K3_SkupnaNapaka
GSMKlima1_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima1_izkljucena
GSMKLIMA1_kke_pogon | DIGITAL | IOD_GSM | GSM:.KLIMA1_kke_pogon
GSMKLIMA1_krm_nap_ok | DIGITAL | IOD_GSM | GSM:.KLIMA1_krm_nap_ok
GSMKlima2_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima2_izkljucena
GSMKlima3_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima3_izkljucena
GSMKlima1Alarm_pozar | DIGITAL | IOD_GSM | GSM:.Klima[1].Alarm_pozar
GSMKlima1Analog_izh_mesanje | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_mesanje
GSMKlima1Analog_izh_rekuperator | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_rekuperator
GSMKlima1Analog_izh_VentGrelnika | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_VentGrelnika
GSMKlima1Analog_izh_VentHlajenja | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_VentHlajenja
GSMKlima1Dejanska_zel_temp | INT | IOD_GSM | GSM:.Klima[1].Dejanska_zel_temp
GSMKlima1DelVentHit1 | DIGITAL | IOD_GSM | GSM:.Klima[1].DelVentHit1
GSMKlima1DelVentHit2 | DIGITAL | IOD_GSM | GSM:.Klima[1].DelVentHit2
GSMKlima1Hitrost_del_vent_disp | INT | IOD_GSM | GSM:.Klima[1].Hitrost_del_vent_disp
GSMKlima1Max_vpih | INT | IOD_GSM | GSM:.Klima[1].Max_vpih
GSMKlima1Min_vpih | INT | IOD_GSM | GSM:.Klima[1].Min_vpih
GSMKlima1Ni_pretoka | DIGITAL | IOD_GSM | GSM:.Klima[1].Ni_pretoka
GSMKlima1Obrat_ure_Vent_h1 | INT | IOD_GSM | GSM:.Klima[1].Obrat_ure_Vent_h1
GSMKlima1Obrat_ure_Vent_h2 | INT | IOD_GSM | GSM:.Klima[1].Obrat_ure_Vent_h2
GSMKlima1OkvaraRototerm | DIGITAL | IOD_GSM | GSM:.Klima[1].OkvaraRototerm
GSMKlima1OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.Klima[1].OkvaraVlazNap
GSMKlima1Pol_komp_konec | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_konec
GSMKlima1Pol_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_sprem_zel_vr
GSMKlima1Pol_komp_zacetek | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_zacetek
GSMKlima1PreklopHitDelVent | INT | IOD_GSM | GSM:.Klima[1].PreklopHitDelVent
GSMKlima1PreobMotCrpGrel | DIGITAL | IOD_GSM | GSM:.Klima[1].PreobMotCrpGrel
GSMKlima1PreobMotVent | DIGITAL | IOD_GSM | GSM:.Klima[1].PreobMotVent
GSMKlima1Protizamrz_zascita | INT | IOD_GSM | GSM:.Klima[1].Protizamrz_zascita
GSMKlima1ProtizamrzZascAktivna | DIGITAL | IOD_GSM | GSM:.Klima[1].ProtizamrzZascAktivna
GSMKlima1Rezim_delovanja | INT | IOD_GSM | GSM:.Klima[1].Rezim_delovanja
GSMKlima1Temperatura_dovoda | INT | IOD_GSM | GSM:.Klima[1].Temperatura_dovoda
GSMKlima1Temperatura_prostora | INT | IOD_GSM | GSM:.Klima[1].Temperatura_prostora
GSMKlima1TempPredPloscnimRekup | INT | IOD_GSM | GSM:.Klima[1].TempPredPloscnimRekup
GSMKlima1TempZaPloscnimRekup | INT | IOD_GSM | GSM:.Klima[1].TempZaPloscnimRekup
GSMKlima1VklopRegKlimata | DIGITAL | IOD_GSM | GSM:.Klima[1].VklopRegKlimata
GSMKlima1Vlaga_v_prostoru | INT | IOD_GSM | GSM:.Klima[1].Vlaga_v_prostoru
GSMKlima1VlagaVstopZrakaProstor | INT | IOD_GSM | GSM:.Klima[1].VlagaVstopZrakaProstor
GSMKlima1ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.Klima[1].ZamasenostFiltra
GSMKlima1ZdruzAlarmA | DIGITAL | IOD_GSM | GSM:.Klima[1].ZdruzAlarmA
GSMKlima1ZdruzAlarmB | DIGITAL | IOD_GSM | GSM:.Klima[1].ZdruzAlarmB
GSMKlima1Zel_temp_eko_gretja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_eko_gretja
GSMKlima1Zel_temp_eko_hlajenja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_eko_hlajenja
GSMKlima1Zel_temp_komf_gretja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_komf_gretja
GSMKlima1Zel_temp_komf_hlajenja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_komf_hlajenja
GSMKlima1Zim_komp_konec | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_konec
GSMKlima1Zim_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_sprem_zel_vr
GSMKlima1Zim_komp_zacetek | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_zacetek
GSMKlima1ZimKompMinVpihKonec | INT | IOD_GSM | GSM:.Klima[1].ZimKompMinVpihKonec
GSMKlima1ZimKompMinVpihZac | INT | IOD_GSM | GSM:.Klima[1].ZimKompMinVpihZac
GSMKlima1ZkompMinVpihSpremZelVr | INT | IOD_GSM | GSM:.Klima[1].ZkompMinVpihSpremZelVr
GSMKlima1Zunanja_temp | INT | IOD_GSM | GSM:.Klima[1].Zunanja_temp
GSMKlima2Alarm_pozar | DIGITAL | IOD_GSM | GSM:.Klima[2].Alarm_pozar
GSMKlima2Analog_izh_mesanje | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_mesanje
GSMKlima2Analog_izh_rekuperator | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_rekuperator
GSMKlima2Analog_izh_VentGrelnika | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_VentGrelnika
GSMKlima2Analog_izh_VentHlajenja | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_VentHlajenja
GSMKlima2Dejanska_zel_temp | INT | IOD_GSM | GSM:.Klima[2].Dejanska_zel_temp
GSMKlima2DelVentHit1 | DIGITAL | IOD_GSM | GSM:.Klima[2].DelVentHit1
GSMKlima2DelVentHit2 | DIGITAL | IOD_GSM | GSM:.Klima[2].DelVentHit2
GSMKlima2Hitrost_del_vent_disp | INT | IOD_GSM | GSM:.Klima[2].Hitrost_del_vent_disp
GSMKlima2Max_vpih | INT | IOD_GSM | GSM:.Klima[2].Max_vpih
GSMKlima2Min_vpih | INT | IOD_GSM | GSM:.Klima[2].Min_vpih
GSMKlima2Ni_pretoka | DIGITAL | IOD_GSM | GSM:.Klima[2].Ni_pretoka
GSMKlima2Obrat_ure_Vent_h1 | INT | IOD_GSM | GSM:.Klima[2].Obrat_ure_Vent_h1
GSMKlima2Obrat_ure_Vent_h2 | INT | IOD_GSM | GSM:.Klima[2].Obrat_ure_Vent_h2
GSMKlima2OkvaraRototerm | DIGITAL | IOD_GSM | GSM:.Klima[2].OkvaraRototerm
GSMKlima2OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.Klima[2].OkvaraVlazNap
GSMKlima2Pol_komp_konec | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_konec
GSMKlima2Pol_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_sprem_zel_vr
GSMKlima2Pol_komp_zacetek | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_zacetek
GSMKlima2PreklopHitDelVent | INT | IOD_GSM | GSM:.Klima[2].PreklopHitDelVent
GSMKlima2PreobMotCrpGrel | DIGITAL | IOD_GSM | GSM:.Klima[2].PreobMotCrpGrel
GSMKlima2PreobMotVent | DIGITAL | IOD_GSM | GSM:.Klima[2].PreobMotVent
GSMKlima2Protizamrz_zascita | INT | IOD_GSM | GSM:.Klima[2].Protizamrz_zascita
GSMKlima2ProtizamrzZascAktivna | DIGITAL | IOD_GSM | GSM:.Klima[2].ProtizamrzZascAktivna
GSMKlima2Rezim_delovanja | INT | IOD_GSM | GSM:.Klima[2].Rezim_delovanja
GSMKlima2Temperatura_dovoda | INT | IOD_GSM | GSM:.Klima[2].Temperatura_dovoda
GSMKlima2Temperatura_prostora | INT | IOD_GSM | GSM:.Klima[2].Temperatura_prostora
GSMKlima2TempPredPloscnimRekup | INT | IOD_GSM | GSM:.Klima[2].TempPredPloscnimRekup
GSMKlima2TempZaPloscnimRekup | INT | IOD_GSM | GSM:.Klima[2].TempZaPloscnimRekup
GSMKlima2VklopRegKlimata | DIGITAL | IOD_GSM | GSM:.Klima[2].VklopRegKlimata
GSMKlima2Vlaga_v_prostoru | INT | IOD_GSM | GSM:.Klima[2].Vlaga_v_prostoru
GSMKlima2VlagaVstopZrakaProstor | INT | IOD_GSM | GSM:.Klima[2].VlagaVstopZrakaProstor
GSMKlima2ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.Klima[2].ZamasenostFiltra
GSMKlima2ZdruzAlarmA | DIGITAL | IOD_GSM | GSM:.Klima[2].ZdruzAlarmA
GSMKlima2ZdruzAlarmB | DIGITAL | IOD_GSM | GSM:.Klima[2].ZdruzAlarmB
GSMKlima2Zel_temp_eko_gretja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_eko_gretja
GSMKlima2Zel_temp_eko_hlajenja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_eko_hlajenja
GSMKlima2Zel_temp_komf_gretja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_komf_gretja
GSMKlima2Zel_temp_komf_hlajenja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_komf_hlajenja
GSMKlima2Zim_komp_konec | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_konec
GSMKlima2Zim_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_sprem_zel_vr
GSMKlima2Zim_komp_zacetek | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_zacetek
GSMKlima2ZimKompMinVpihKonec | INT | IOD_GSM | GSM:.Klima[2].ZimKompMinVpihKonec
GSMKlima2ZimKompMinVpihZac | INT | IOD_GSM | GSM:.Klima[2].ZimKompMinVpihZac
GSMKlima2ZkompMinVpihSpremZelVr | INT | IOD_GSM | GSM:.Klima[2].ZkompMinVpihSpremZelVr
GSMKlima2Zunanja_temp | INT | IOD_GSM | GSM:.Klima[2].Zunanja_temp
GSMKLIMA_m1_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMA_m1_delovanje
GSMKLIMA_m1_napaka | DIGITAL | IOD_GSM | GSM:.KLIMA_m1_napaka
GSMKLIMA_m2_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMA_m2_delovanje
GSMKLIMA_m2_napaka | DIGITAL | IOD_GSM | GSM:.KLIMA_m2_napaka
GSMKlimaIzklopObrUre | INT | IOD_GSM | GSM:.KlimaIzklopObrUre
GSMKLIMAT1_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMAT1_delovanje
GSMKLIMAT1_napaka | DIGITAL | IOD_GSM | GSM:.KLIMAT1_napaka
GSMKLIMAT1_R_zakleni | DIGITAL | IOD_GSM | GSM:.KLIMAT1_R_zakleni
GSMKLIMAT1_vklop_delovanja | DIGITAL | IOD_GSM | GSM:.KLIMAT1_vklop_delovanja
GSMKLIMAT1_vklop_delovanjaR | DIGITAL | IOD_GSM | GSM:.KLIMAT1_vklop_delovanjaR
GSMKLIMAT2_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMAT2_delovanje
GSMKLIMAT2_napaka | DIGITAL | IOD_GSM | GSM:.KLIMAT2_napaka
GSMKLIMAT2_R_zakleni | DIGITAL | IOD_GSM | GSM:.KLIMAT2_R_zakleni
GSMKLIMAT2_vklop_delovanja | DIGITAL | IOD_GSM | GSM:.KLIMAT2_vklop_delovanja
GSMKLIMAT2_vklop_delovanjaR | DIGITAL | IOD_GSM | GSM:.KLIMAT2_vklop_delovanjaR
GSMKlime_vklopi_n | INT | IOD_GSM | GSM:.Klime_vklopi_n
GSMKlimeAVTO | DIGITAL | IOD_GSM | GSM:.KlimeAVTO
GSMkom_nast_cas_izpada | INT | IOD_GSM | GSM:.kom_nast_cas_izpada
GSMMAX_SOCKET_FD_SETSIZE | LONG | IOD_GSM | GSM:.MAX_SOCKET_FD_SETSIZE
GSMN_F1_1_zascita_ok | DIGITAL | IOD_GSM | GSM:.N_F1_1_zascita_ok
GSMN_KLIMA1_krm_nap_ok | DIGITAL | IOD_GSM | GSM:.N_KLIMA1_krm_nap_ok
GSMN_KLIMAT1_napaka | DIGITAL | IOD_GSM | GSM:.N_KLIMAT1_napaka
GSMN_KLIMAT2_napaka | DIGITAL | IOD_GSM | GSM:.N_KLIMAT2_napaka
GSMN_KlimeAVTO | DIGITAL | IOD_GSM | GSM:.N_KlimeAVTO
GSMK1_obr_u_skupno | UINT | IOD_GSM | GSM:.K1_obr_u_skupno
GSMK2_obr_u_skupno | UINT | IOD_GSM | GSM:.K2_obr_u_skupno
GSMN_Q12_izpad | DIGITAL | IOD_GSM | GSM:.N_Q12_izpad
GSMN_UPS_A_V23_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_A_V23_delovanje
GSMN_UPS_A_V23_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_A_V23_napaka
GSMN_UPS_V23_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_V23_delovanje
GSMN_UPS_V23_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_V23_napaka
GSMN_UPS_V25_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_V25_delovanje
GSMN_UPS_V25_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_V25_napaka
GSMN_VLAZILEC1_napaka | DIGITAL | IOD_GSM | GSM:.N_VLAZILEC1_napaka
GSMN_VLAZILEC2_napaka | DIGITAL | IOD_GSM | GSM:.N_VLAZILEC2_napaka
GSMnapaka_kom_panel | DIGITAL | IOD_GSM | GSM:.napaka_kom_panel
GSMnapaka_kom_scada | DIGITAL | IOD_GSM | GSM:.napaka_kom_scada
GSMnapaka_kom_scada2 | DIGITAL | IOD_GSM | GSM:.napaka_kom_scada2
GSMNapakaSenzorSkupno | DIGITAL | IOD_GSM | GSM:.NapakaSenzorSkupno
GSMNapakaSenzorVlagaHIA1 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA1
GSMNapakaSenzorVlagaHIA2 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA2
GSMNapakaSenzorVlagaHIA3 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA3
GSMNapakaSenzorVlagaHIA4 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA4
GSMNapakaSenzorVlagaHIA5 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA5
GSMNapakaSenzorVlagaHIA6 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA6
GSMNapakaSenzorVlagaHIA7 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA7
GSMNapakaTSTempTIA1 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA1
GSMNapakaTSTempTIA2 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA2
GSMNapakaTSTempTIA3 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA3
GSMNapakaTSTempTIA4 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA4
GSMNapakaTSTempTIA5 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA5
GSMNapakaTSTempTIA6 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA6
GSMNapakaTSTempTIA7 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA7
GSMOpozoriloPMM2x17med60in8010 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[10]
GSMOpozoriloPMM2x17med60in8011 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[11]
GSMOpozoriloPMM2x17med60in8012 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[12]
GSMOpozoriloPMM2x17med60in8013 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[13]
GSMOpozoriloPMM2x17med60in8014 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[14]
GSMOpozoriloPMM2x17med60in8015 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[15]
GSMOpozoriloPMM2x17med60in8016 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[16]
GSMOpozoriloPMM2x17med60in8017 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[17]
GSMOpozoriloPMM2x17med60in8018 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[18]
GSMOpozoriloPMM2x17med60in8019 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[19]
GSMOpozoriloPMM2x17med60in801 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[1]
GSMOpozoriloPMM2x17med60in8020 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[20]
GSMOpozoriloPMM2x17med60in8021 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[21]
GSMOpozoriloPMM2x17med60in8022 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[22]
GSMOpozoriloPMM2x17med60in8023 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[23]
GSMOpozoriloPMM2x17med60in8024 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[24]
GSMOpozoriloPMM2x17med60in8025 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[25]
GSMOpozoriloPMM2x17med60in8026 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[26]
GSMOpozoriloPMM2x17med60in8027 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[27]
GSMOpozoriloPMM2x17med60in8028 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[28]
GSMOpozoriloPMM2x17med60in8029 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[29]
GSMOpozoriloPMM2x17med60in802 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[2]
GSMOpozoriloPMM2x17med60in8030 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[30]
GSMOpozoriloPMM2x17med60in8031 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[31]
GSMOpozoriloPMM2x17med60in8032 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[32]
GSMOpozoriloPMM2x17med60in8033 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[33]
GSMOpozoriloPMM2x17med60in8034 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[34]
GSMOpozoriloPMM2x17med60in8035 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[35]
GSMOpozoriloPMM2x17med60in8036 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[36]
GSMOpozoriloPMM2x17med60in8037 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[37]
GSMOpozoriloPMM2x17med60in8038 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[38]
GSMOpozoriloPMM2x17med60in8039 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[39]
GSMOpozoriloPMM2x17med60in803 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[3]
GSMOpozoriloPMM2x17med60in8040 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[40]
GSMOpozoriloPMM2x17med60in8041 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[41]
GSMOpozoriloPMM2x17med60in8042 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[42]
GSMOpozoriloPMM2x17med60in804 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[4]
GSMOpozoriloPMM2x17med60in805 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[5]
GSMOpozoriloPMM2x17med60in806 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[6]
GSMOpozoriloPMM2x17med60in807 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[7]
GSMOpozoriloPMM2x17med60in808 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[8]
GSMOpozoriloPMM2x17med60in809 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[9]
GSMPMM1OverCurrentBetw1 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[1]
GSMPMM1OverCurrentBetw2 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[2]
GSMPMM1OverCurrentBetw3 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[3]
GSMPMM1OverCurrentOver1 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[1]
GSMPMM1OverCurrentOver2 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[2]
GSMPMM1OverCurrentOver3 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[3]
GSMPMM2QA1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_GSM | GSM:.PMM2.QA1_GlStik_IZKLOP_IZPAD
GSMPMM2QB1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_GSM | GSM:.PMM2.QB1_GlStik_IZKLOP_IZPAD
GSMPMM2SkNapaka_med60in80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapaka_med60in80
GSMPMM2SkNapaka_nad80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapaka_nad80
GSMPMM2SkNapakaVirA_med60in80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapakaVirA_med60in80
GSMPMM2SkNapakaVirA_nad80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapakaVirA_nad80
GSMPMM2SkNapakaVirB_med60in80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapakaVirB_med60in80
GSMPMM2SkNapakaVirB_nad80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapakaVirB_nad80
GSMPMM2VirACurrent10 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[10]
GSMPMM2VirACurrent11 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[11]
GSMPMM2VirACurrent12 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[12]
GSMPMM2VirACurrent13 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[13]
GSMPMM2VirACurrent14 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[14]
GSMPMM2VirACurrent15 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[15]
GSMPMM2VirACurrent16 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[16]
GSMPMM2VirACurrent17 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[17]
GSMPMM2VirACurrent18 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[18]
GSMPMM2VirACurrent19 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[19]
GSMPMM2VirACurrent1 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[1]
GSMPMM2VirACurrent20 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[20]
GSMPMM2VirACurrent21 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[21]
GSMPMM2VirACurrent22 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[22]
GSMPMM2VirACurrent23 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[23]
GSMPMM2VirACurrent24 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[24]
GSMPMM2VirACurrent25 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[25]
GSMPMM2VirACurrent26 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[26]
GSMPMM2VirACurrent27 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[27]
GSMPMM2VirACurrent28 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[28]
GSMPMM2VirACurrent29 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[29]
GSMPMM2VirACurrent2 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[2]
GSMPMM2VirACurrent30 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[30]
GSMPMM2VirACurrent31 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[31]
GSMPMM2VirACurrent32 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[32]
GSMPMM2VirACurrent33 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[33]
GSMPMM2VirACurrent34 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[34]
GSMPMM2VirACurrent35 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[35]
GSMPMM2VirACurrent36 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[36]
GSMPMM2VirACurrent37 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[37]
GSMPMM2VirACurrent38 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[38]
GSMPMM2VirACurrent39 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[39]
GSMPMM2VirACurrent3 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[3]
GSMPMM2VirACurrent40 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[40]
GSMPMM2VirACurrent41 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[41]
GSMPMM2VirACurrent42 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[42]
GSMPMM2VirACurrent43 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[43]
GSMPMM2VirACurrent44 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[44]
GSMPMM2VirACurrent4 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[4]
GSMPMM2VirACurrent5 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[5]
GSMPMM2VirACurrent6 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[6]
GSMPMM2VirACurrent7 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[7]
GSMPMM2VirACurrent8 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[8]
GSMPMM2VirACurrent9 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[9]
GSMPMM2VirA_fsys | REAL | IOD_GSM | GSM:.PMM2.VirA_fsys
GSMPMM2VirA_Isys | REAL | IOD_GSM | GSM:.PMM2.VirA_Isys
GSMPMM2VirA_NapakaOzemljitve | DIGITAL | IOD_GSM | GSM:.PMM2.VirA_NapakaOzemljitve
GSMPMM2VirA_PFsys | REAL | IOD_GSM | GSM:.PMM2.VirA_PFsys
GSMPMM2VirA_Psys | REAL | IOD_GSM | GSM:.PMM2.VirA_Psys
GSMPMM2VirA_Qsys | REAL | IOD_GSM | GSM:.PMM2.VirA_Qsys
GSMPMM2VirA_Ssys | REAL | IOD_GSM | GSM:.PMM2.VirA_Ssys
GSMPMM2VirA_Usys | REAL | IOD_GSM | GSM:.PMM2.VirA_Usys
GSMPMM2VirAActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM2.VirAActiveEnergyConsumed_kWh
GSMPMM2VirAActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM2.VirAActivePowerPhaseA_kW
GSMPMM2VirAActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM2.VirAActivePowerPhaseB_kW
GSMPMM2VirAActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM2.VirAActivePowerPhaseC_kW
GSMPMM2VirAAlarmPhaseC01_16_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C01_16_60to80
GSMPMM2VirAAlarmPhaseC01_16_over80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C01_16_over80
GSMPMM2VirAAlarmPhaseC17_32_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C17_32_60to80
GSMPMM2VirAAlarmPhaseC17_32_over80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C17_32_over80
GSMPMM2VirAAlarmPhaseC33_44_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C33_44_60to80
GSMPMM2VirAAlarmPhaseC33_44_over80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C33_44_over80
GSMPMM2VirAAparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM2.VirAAparentPowerPhaseA
GSMPMM2VirAAparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM2.VirAAparentPowerPhaseB
GSMPMM2VirAAparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM2.VirAAparentPowerPhaseC
GSMPMM2VirACurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM2.VirACurrentInPhaseA_A
GSMPMM2VirACurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM2.VirACurrentInPhaseB_A
GSMPMM2VirACurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM2.VirACurrentInPhaseC_A
GSMPMM2VirAReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM2.VirAReactiveEnergyConsumed_kVARh
GSMPMM2VirAReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM2.VirAReactivePowerPhaseA
GSMPMM2VirAReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM2.VirAReactivePowerPhaseB
GSMPMM2VirAReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM2.VirAReactivePowerPhaseC
GSMPMM2VirAVoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseAB_V
GSMPMM2VirAVoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseAN_V
GSMPMM2VirAVoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseBC_V
GSMPMM2VirAVoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseBN_V
GSMPMM2VirAVoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseCA_V
GSMPMM2VirAVoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseCN_V
GSMPMM2VirBCurrent10 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[10]
GSMPMM2VirBCurrent11 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[11]
GSMPMM2VirBCurrent12 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[12]
GSMPMM2VirBCurrent13 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[13]
GSMPMM2VirBCurrent14 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[14]
GSMPMM2VirBCurrent15 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[15]
GSMPMM2VirBCurrent16 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[16]
GSMPMM2VirBCurrent17 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[17]
GSMPMM2VirBCurrent18 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[18]
GSMPMM2VirBCurrent19 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[19]
GSMPMM2VirBCurrent1 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[1]
GSMPMM2VirBCurrent20 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[20]
GSMPMM2VirBCurrent21 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[21]
GSMPMM2VirBCurrent22 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[22]
GSMPMM2VirBCurrent23 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[23]
GSMPMM2VirBCurrent24 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[24]
GSMPMM2VirBCurrent25 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[25]
GSMPMM2VirBCurrent26 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[26]
GSMPMM2VirBCurrent27 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[27]
GSMPMM2VirBCurrent28 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[28]
GSMPMM2VirBCurrent29 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[29]
GSMPMM2VirBCurrent2 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[2]
GSMPMM2VirBCurrent30 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[30]
GSMPMM2VirBCurrent31 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[31]
GSMPMM2VirBCurrent32 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[32]
GSMPMM2VirBCurrent33 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[33]
GSMPMM2VirBCurrent34 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[34]
GSMPMM2VirBCurrent35 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[35]
GSMPMM2VirBCurrent36 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[36]
GSMPMM2VirBCurrent37 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[37]
GSMPMM2VirBCurrent38 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[38]
GSMPMM2VirBCurrent39 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[39]
GSMPMM2VirBCurrent3 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[3]
GSMPMM2VirBCurrent40 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[40]
GSMPMM2VirBCurrent41 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[41]
GSMPMM2VirBCurrent42 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[42]
GSMPMM2VirBCurrent43 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[43]
GSMPMM2VirBCurrent44 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[44]
GSMPMM2VirBCurrent4 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[4]
GSMPMM2VirBCurrent5 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[5]
GSMPMM2VirBCurrent6 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[6]
GSMPMM2VirBCurrent7 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[7]
GSMPMM2VirBCurrent8 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[8]
GSMPMM2VirBCurrent9 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[9]
GSMPMM2VirB_fsys | REAL | IOD_GSM | GSM:.PMM2.VirB_fsys
GSMPMM2VirB_Isys | REAL | IOD_GSM | GSM:.PMM2.VirB_Isys
GSMPMM2VirB_NapakaOzemljitve | DIGITAL | IOD_GSM | GSM:.PMM2.VirB_NapakaOzemljitve
GSMPMM2VirB_PFsys | REAL | IOD_GSM | GSM:.PMM2.VirB_PFsys
GSMPMM2VirB_Psys | REAL | IOD_GSM | GSM:.PMM2.VirB_Psys
GSMPMM2VirB_Qsys | REAL | IOD_GSM | GSM:.PMM2.VirB_Qsys
GSMPMM2VirB_Ssys | REAL | IOD_GSM | GSM:.PMM2.VirB_Ssys
GSMPMM2VirB_Usys | REAL | IOD_GSM | GSM:.PMM2.VirB_Usys
GSMPMM2VirBActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM2.VirBActiveEnergyConsumed_kWh
GSMPMM2VirBActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM2.VirBActivePowerPhaseA_kW
GSMPMM2VirBActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM2.VirBActivePowerPhaseB_kW
GSMPMM2VirBActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM2.VirBActivePowerPhaseC_kW
GSMPMM2VirBAlarmPhaseC01_16_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C01_16_60to80
GSMPMM2VirBAlarmPhaseC01_16_over80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C01_16_over80
GSMPMM2VirBAlarmPhaseC17_32_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C17_32_60to80
GSMPMM2VirBAlarmPhaseC17_32_over80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C17_32_over80
GSMPMM2VirBAlarmPhaseC33_44_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C33_44_60to80
GSMPMM2VirBAlarmPhaseC33_44_over80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C33_44_over80
GSMPMM2VirBAparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM2.VirBAparentPowerPhaseA
GSMPMM2VirBAparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM2.VirBAparentPowerPhaseB
GSMPMM2VirBAparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM2.VirBAparentPowerPhaseC
GSMPMM2VirBCurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM2.VirBCurrentInPhaseA_A
GSMPMM2VirBCurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM2.VirBCurrentInPhaseB_A
GSMPMM2VirBCurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM2.VirBCurrentInPhaseC_A
GSMPMM2VirBReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM2.VirBReactiveEnergyConsumed_kVARh
GSMPMM2VirBReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM2.VirBReactivePowerPhaseA
GSMPMM2VirBReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM2.VirBReactivePowerPhaseB
GSMPMM2VirBReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM2.VirBReactivePowerPhaseC
GSMPMM2VirBVoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseAB_V
GSMPMM2VirBVoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseAN_V
GSMPMM2VirBVoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseBC_V
GSMPMM2VirBVoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseBN_V
GSMPMM2VirBVoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseCA_V
GSMPMM2VirBVoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseCN_V
GSMPMM1ActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM[1].ActiveEnergyConsumed_kWh
GSMPMM1ActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseA_kW
GSMPMM1ActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseB_kW
GSMPMM1ActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseC_kW
GSMPMM1AlarmPhase1C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C01_16_60to80
GSMPMM1AlarmPhase1C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C01_16_over80
GSMPMM1AlarmPhase1C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C17_32_60to80
GSMPMM1AlarmPhase1C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C17_32_over80
GSMPMM1AlarmPhase1C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C33_42_60to80
GSMPMM1AlarmPhase1C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C33_42_over80
GSMPMM1AlarmPhase1GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].GlobalAlarmReg
GSMPMM1AlarmPhase2C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C01_16_60to80
GSMPMM1AlarmPhase2C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C01_16_over80
GSMPMM1AlarmPhase2C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C17_32_60to80
GSMPMM1AlarmPhase2C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C17_32_over80
GSMPMM1AlarmPhase2C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C33_42_60to80
GSMPMM1AlarmPhase2C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C33_42_over80
GSMPMM1AlarmPhase2GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].GlobalAlarmReg
GSMPMM1AlarmPhase3C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C01_16_60to80
GSMPMM1AlarmPhase3C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C01_16_over80
GSMPMM1AlarmPhase3C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C17_32_60to80
GSMPMM1AlarmPhase3C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C17_32_over80
GSMPMM1AlarmPhase3C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C33_42_60to80
GSMPMM1AlarmPhase3C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C33_42_over80
GSMPMM1AlarmPhase3GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].GlobalAlarmReg
GSMPMM1AparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseA
GSMPMM1AparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseB
GSMPMM1AparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseC
GSMPMM1AverageCurrent_A | REAL | IOD_GSM | GSM:.PMM[1].AverageCurrent_A
GSMPMM1AveragePhaseToNeutral_V | REAL | IOD_GSM | GSM:.PMM[1].AveragePhaseToNeutral_V
GSMPMM1AveragePhaseToPhase_V | REAL | IOD_GSM | GSM:.PMM[1].AveragePhaseToPhase_V
GSMPMM1CurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseA_A
GSMPMM1CurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseB_A
GSMPMM1CurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseC_A
GSMPMM1Frequency_Hz | REAL | IOD_GSM | GSM:.PMM[1].Frequency_Hz
GSMPMM1Phase1Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[10]
GSMPMM1Phase1Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[11]
GSMPMM1Phase1Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[12]
GSMPMM1Phase1Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[13]
GSMPMM1Phase1Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[14]
GSMPMM1Phase1Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[15]
GSMPMM1Phase1Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[16]
GSMPMM1Phase1Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[17]
GSMPMM1Phase1Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[18]
GSMPMM1Phase1Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[19]
GSMPMM1Phase1Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[1]
GSMPMM1Phase1Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[20]
GSMPMM1Phase1Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[21]
GSMPMM1Phase1Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[22]
GSMPMM1Phase1Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[23]
GSMPMM1Phase1Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[24]
GSMPMM1Phase1Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[25]
GSMPMM1Phase1Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[26]
GSMPMM1Phase1Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[27]
GSMPMM1Phase1Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[28]
GSMPMM1Phase1Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[29]
GSMPMM1Phase1Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[2]
GSMPMM1Phase1Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[30]
GSMPMM1Phase1Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[31]
GSMPMM1Phase1Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[32]
GSMPMM1Phase1Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[33]
GSMPMM1Phase1Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[34]
GSMPMM1Phase1Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[35]
GSMPMM1Phase1Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[36]
GSMPMM1Phase1Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[37]
GSMPMM1Phase1Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[38]
GSMPMM1Phase1Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[39]
GSMPMM1Phase1Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[3]
GSMPMM1Phase1Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[40]
GSMPMM1Phase1Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[41]
GSMPMM1Phase1Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[42]
GSMPMM1Phase1Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[4]
GSMPMM1Phase1Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[5]
GSMPMM1Phase1Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[6]
GSMPMM1Phase1Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[7]
GSMPMM1Phase1Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[8]
GSMPMM1Phase1Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[9]
GSMPMM1Phase2Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[10]
GSMPMM1Phase2Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[11]
GSMPMM1Phase2Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[12]
GSMPMM1Phase2Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[13]
GSMPMM1Phase2Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[14]
GSMPMM1Phase2Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[15]
GSMPMM1Phase2Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[16]
GSMPMM1Phase2Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[17]
GSMPMM1Phase2Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[18]
GSMPMM1Phase2Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[19]
GSMPMM1Phase2Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[1]
GSMPMM1Phase2Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[20]
GSMPMM1Phase2Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[21]
GSMPMM1Phase2Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[22]
GSMPMM1Phase2Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[23]
GSMPMM1Phase2Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[24]
GSMPMM1Phase2Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[25]
GSMPMM1Phase2Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[26]
GSMPMM1Phase2Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[27]
GSMPMM1Phase2Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[28]
GSMPMM1Phase2Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[29]
GSMPMM1Phase2Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[2]
GSMPMM1Phase2Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[30]
GSMPMM1Phase2Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[31]
GSMPMM1Phase2Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[32]
GSMPMM1Phase2Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[33]
GSMPMM1Phase2Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[34]
GSMPMM1Phase2Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[35]
GSMPMM1Phase2Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[36]
GSMPMM1Phase2Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[37]
GSMPMM1Phase2Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[38]
GSMPMM1Phase2Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[39]
GSMPMM1Phase2Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[3]
GSMPMM1Phase2Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[40]
GSMPMM1Phase2Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[41]
GSMPMM1Phase2Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[42]
GSMPMM1Phase2Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[4]
GSMPMM1Phase2Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[5]
GSMPMM1Phase2Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[6]
GSMPMM1Phase2Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[7]
GSMPMM1Phase2Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[8]
GSMPMM1Phase2Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[9]
GSMPMM1Phase3Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[10]
GSMPMM1Phase3Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[11]
GSMPMM1Phase3Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[12]
GSMPMM1Phase3Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[13]
GSMPMM1Phase3Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[14]
GSMPMM1Phase3Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[15]
GSMPMM1Phase3Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[16]
GSMPMM1Phase3Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[17]
GSMPMM1Phase3Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[18]
GSMPMM1Phase3Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[19]
GSMPMM1Phase3Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[1]
GSMPMM1Phase3Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[20]
GSMPMM1Phase3Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[21]
GSMPMM1Phase3Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[22]
GSMPMM1Phase3Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[23]
GSMPMM1Phase3Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[24]
GSMPMM1Phase3Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[25]
GSMPMM1Phase3Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[26]
GSMPMM1Phase3Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[27]
GSMPMM1Phase3Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[28]
GSMPMM1Phase3Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[29]
GSMPMM1Phase3Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[2]
GSMPMM1Phase3Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[30]
GSMPMM1Phase3Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[31]
GSMPMM1Phase3Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[32]
GSMPMM1Phase3Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[33]
GSMPMM1Phase3Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[34]
GSMPMM1Phase3Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[35]
GSMPMM1Phase3Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[36]
GSMPMM1Phase3Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[37]
GSMPMM1Phase3Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[38]
GSMPMM1Phase3Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[39]
GSMPMM1Phase3Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[3]
GSMPMM1Phase3Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[40]
GSMPMM1Phase3Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[41]
GSMPMM1Phase3Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[42]
GSMPMM1Phase3Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[4]
GSMPMM1Phase3Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[5]
GSMPMM1Phase3Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[6]
GSMPMM1Phase3Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[7]
GSMPMM1Phase3Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[8]
GSMPMM1Phase3Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[9]
GSMPMM1PowerFactorSys | REAL | IOD_GSM | GSM:.PMM[1].PowerFactorSys
GSMPMM1ReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM[1].ReactiveEnergyConsumed_kVARh
GSMPMM1ReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseA
GSMPMM1ReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseB
GSMPMM1ReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseC
GSMPMM1TotalActivePower_kW | REAL | IOD_GSM | GSM:.PMM[1].TotalActivePower_kW
GSMPMM1TotalAparentPower_kVA | REAL | IOD_GSM | GSM:.PMM[1].TotalAparentPower_kVA
GSMPMM1TotalPowerFactor | REAL | IOD_GSM | GSM:.PMM[1].TotalPowerFactor
GSMPMM1TotalReactivePower_kVAR | REAL | IOD_GSM | GSM:.PMM[1].TotalReactivePower_kVAR
GSMPMM1VirA_fsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_fsys
GSMPMM1VirA_Isys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Isys
GSMPMM1VirA_PFsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_PFsys
GSMPMM1VirA_Psys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Psys
GSMPMM1VirA_Qsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Qsys
GSMPMM1VirA_Ssys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Ssys
GSMPMM1VirA_Usys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Usys
GSMPMM1VirB_fsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_fsys
GSMPMM1VirB_Isys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Isys
GSMPMM1VirB_PFsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_PFsys
GSMPMM1VirB_Psys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Psys
GSMPMM1VirB_Qsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Qsys
GSMPMM1VirB_Ssys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Ssys
GSMPMM1VirB_Usys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Usys
GSMPMM1VirBActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM[1].VirBActiveEnergyConsumed_kWh
GSMPMM1VirBActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseA_kW
GSMPMM1VirBActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseB_kW
GSMPMM1VirBActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseC_kW
GSMPMM1VirBAparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseA
GSMPMM1VirBAparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseB
GSMPMM1VirBAparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseC
GSMPMM1VirBAverageCurrent_A | REAL | IOD_GSM | GSM:.PMM[1].VirBAverageCurrent_A
GSMPMM1VirBAveragePhaseToNeutral_V | REAL | IOD_GSM | GSM:.PMM[1].VirBAveragePhaseToNeutral_V
GSMPMM1VirBAveragePhaseToPhase_V | REAL | IOD_GSM | GSM:.PMM[1].VirBAveragePhaseToPhase_V
GSMPMM1VirBCurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseA_A
GSMPMM1VirBCurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseB_A
GSMPMM1VirBCurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseC_A
GSMPMM1VirBFrequency_Hz | REAL | IOD_GSM | GSM:.PMM[1].VirBFrequency_Hz
GSMPMM1VirBPowerFactorSys | REAL | IOD_GSM | GSM:.PMM[1].VirBPowerFactorSys
GSMPMM1VirBReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM[1].VirBReactiveEnergyConsumed_kVARh
GSMPMM1VirBReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseA
GSMPMM1VirBReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseB
GSMPMM1VirBReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseC
GSMPMM1VirBTotalActivePower_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalActivePower_kW
GSMPMM1VirBTotalAparentPower_kVA | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalAparentPower_kVA
GSMPMM1VirBTotalPowerFactor | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalPowerFactor
GSMPMM1VirBTotalReactivePower_kVAR | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalReactivePower_kVAR
GSMPMM1VirBVoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseAB_V
GSMPMM1VirBVoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseAN_V
GSMPMM1VirBVoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseBC_V
GSMPMM1VirBVoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseBN_V
GSMPMM1VirBVoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseCA_V
GSMPMM1VirBVoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseCN_V
GSMPMM1VoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseAB_V
GSMPMM1VoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseAN_V
GSMPMM1VoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseBC_V
GSMPMM1VoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseBN_V
GSMPMM1VoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseCA_V
GSMPMM1VoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseCN_V
GSMPMMfaza01 | REAL | IOD_GSM | GSM:.PMMfaza01
GSMPMMfaza02 | REAL | IOD_GSM | GSM:.PMMfaza02
GSMPMMfaza03 | REAL | IOD_GSM | GSM:.PMMfaza03
GSMPMMfaza04 | REAL | IOD_GSM | GSM:.PMMfaza04
GSMPMMfaza05 | REAL | IOD_GSM | GSM:.PMMfaza05
GSMPMMfaza06 | REAL | IOD_GSM | GSM:.PMMfaza06
GSMPMMfaza07 | REAL | IOD_GSM | GSM:.PMMfaza07
GSMPMMfaza08 | REAL | IOD_GSM | GSM:.PMMfaza08
GSMPMMfaza09 | REAL | IOD_GSM | GSM:.PMMfaza09
GSMPMMfaza10 | REAL | IOD_GSM | GSM:.PMMfaza10
GSMPMMfaza11 | REAL | IOD_GSM | GSM:.PMMfaza11
GSMPMMfaza12 | REAL | IOD_GSM | GSM:.PMMfaza12
GSMPMMfaza13 | REAL | IOD_GSM | GSM:.PMMfaza13
GSMPMMfaza14 | REAL | IOD_GSM | GSM:.PMMfaza14
GSMPMMfaza15 | REAL | IOD_GSM | GSM:.PMMfaza15
GSMPMMfaza16 | REAL | IOD_GSM | GSM:.PMMfaza16
GSMPMMfaza17 | REAL | IOD_GSM | GSM:.PMMfaza17
GSMPMMfaza18 | REAL | IOD_GSM | GSM:.PMMfaza18
GSMPMMfaza19 | REAL | IOD_GSM | GSM:.PMMfaza19
GSMPMMfaza20 | REAL | IOD_GSM | GSM:.PMMfaza20
GSMPMMfaza21 | REAL | IOD_GSM | GSM:.PMMfaza21
GSMPMMfaza22 | REAL | IOD_GSM | GSM:.PMMfaza22
GSMPMMfaza23 | REAL | IOD_GSM | GSM:.PMMfaza23
GSMPMMfaza24 | REAL | IOD_GSM | GSM:.PMMfaza24
GSMPMMfaza25 | REAL | IOD_GSM | GSM:.PMMfaza25
GSMPMMfaza26 | REAL | IOD_GSM | GSM:.PMMfaza26
GSMPMMfaza27 | REAL | IOD_GSM | GSM:.PMMfaza27
GSMPMMfaza28 | REAL | IOD_GSM | GSM:.PMMfaza28
GSMPMMfaza29 | REAL | IOD_GSM | GSM:.PMMfaza29
GSMPMMfaza30 | REAL | IOD_GSM | GSM:.PMMfaza30
GSMPMMfaza31 | REAL | IOD_GSM | GSM:.PMMfaza31
GSMPMMfaza32 | REAL | IOD_GSM | GSM:.PMMfaza32
GSMPMMfaza33 | REAL | IOD_GSM | GSM:.PMMfaza33
GSMPMMfaza34 | REAL | IOD_GSM | GSM:.PMMfaza34
GSMPMMfaza35 | REAL | IOD_GSM | GSM:.PMMfaza35
GSMPMMfaza36 | REAL | IOD_GSM | GSM:.PMMfaza36
GSMPMMfaza37 | REAL | IOD_GSM | GSM:.PMMfaza37
GSMPMMfaza38 | REAL | IOD_GSM | GSM:.PMMfaza38
GSMPMMfaza39 | REAL | IOD_GSM | GSM:.PMMfaza39
GSMPMMfaza40 | REAL | IOD_GSM | GSM:.PMMfaza40
GSMPMMfaza41 | REAL | IOD_GSM | GSM:.PMMfaza41
GSMPMMfaza42 | REAL | IOD_GSM | GSM:.PMMfaza42
GSMPMMskupniTokA | REAL | IOD_GSM | GSM:.PMMskupniTokA
GSMPMMskupniTokB | REAL | IOD_GSM | GSM:.PMMskupniTokB
GSMPozarnaCentrala_skupno | DIGITAL | IOD_GSM | GSM:.PozarnaCentrala_skupno
GSMPrevisokaTemp | DIGITAL | IOD_GSM | GSM:.PrevisokaTemp
GSMQ0_izkljuceno | DIGITAL | IOD_GSM | GSM:.Q0_izkljuceno
GSMQ0_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q0_vkljuceno
GSMQ12_izkljuceno | DIGITAL | IOD_GSM | GSM:.Q12_izkljuceno
GSMQ12_izpad | DIGITAL | IOD_GSM | GSM:.Q12_izpad
GSMQ12_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q12_vkljuceno
GSMQ12stanje | INT | IOD_GSM | GSM:.Q12stanje | BYTE
GSMQ21_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q21_vkljuceno
GSMQ22_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q22_vkljuceno
GSMrazlitjeLAH1 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH1
GSMrazlitjeLAH2 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH2
GSMrazlitjeLAH3 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH3
GSMrazlitjeLAH4 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH4
GSMSetDateTime | DIGITAL | IOD_GSM | GSM:.SetDateTime
GSMSetDateTimeDemand | DIGITAL | IOD_GSM | GSM:.SetDateTimeDemand
GSMSetDateTimeError | DIGITAL | IOD_GSM | GSM:.SetDateTimeError
GSMSetDateTimeFinished | DIGITAL | IOD_GSM | GSM:.SetDateTimeFinished
GSMSkupneNapakeNaprav_PMM17VirBVirA | DIGITAL | IOD_GSM | GSM:.SkupneNapakeNaprav_PMM17VirBVirA
GSMSlabaBaterijaPLC | DIGITAL | IOD_GSM | GSM:.SlabaBaterijaPLC
GSMTempHistereza | INT | IOD_GSM | GSM:.TempHistereza
GSMTempPovp234 | INT | IOD_GSM | GSM:.TempPovp234
GSMTempPovp234Alarm | INT | IOD_GSM | GSM:.TempPovp234Alarm
GSMTempPovp234Previs | DIGITAL | IOD_GSM | GSM:.TempPovp234Previs
GSMTempPovp56 | INT | IOD_GSM | GSM:.TempPovp56
GSMTempPovp56Alarm | INT | IOD_GSM | GSM:.TempPovp56Alarm
GSMTempPovp56Previs | DIGITAL | IOD_GSM | GSM:.TempPovp56Previs
GSMTempZaVklopKlim1 | INT | IOD_GSM | GSM:.TempZaVklopKlim1
GSMTempZaVklopKlim2 | INT | IOD_GSM | GSM:.TempZaVklopKlim2
GSMTIA1_alarm | INT | IOD_GSM | GSM:.TIA1_alarm
GSMTIA1_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA1_previs_temp
GSMTIA1_temp_s | INT | IOD_GSM | GSM:.TIA1_temp_s
GSMTIA2_alarm | INT | IOD_GSM | GSM:.TIA2_alarm
GSMTIA2_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA2_previs_temp
GSMTIA2_temp_s | INT | IOD_GSM | GSM:.TIA2_temp_s
GSMTIA3_alarm | INT | IOD_GSM | GSM:.TIA3_alarm
GSMTIA3_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA3_previs_temp
GSMTIA3_temp_s | INT | IOD_GSM | GSM:.TIA3_temp_s
GSMTIA4_alarm | INT | IOD_GSM | GSM:.TIA4_alarm
GSMTIA4_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA4_previs_temp
GSMTIA4_temp_s | INT | IOD_GSM | GSM:.TIA4_temp_s
GSMTIA5_alarm | INT | IOD_GSM | GSM:.TIA5_alarm
GSMTIA5_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA5_previs_temp
GSMTIA5_temp_s | INT | IOD_GSM | GSM:.TIA5_temp_s
GSMTIA6_alarm | INT | IOD_GSM | GSM:.TIA6_alarm
GSMTIA6_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA6_previs_temp
GSMTIA6_temp_s | INT | IOD_GSM | GSM:.TIA6_temp_s
GSMTIA7_alarm | INT | IOD_GSM | GSM:.TIA7_alarm
GSMTIA7_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA7_previs_temp
GSMTIA7_temp_s | INT | IOD_GSM | GSM:.TIA7_temp_s
GSMUPS1_StatusBaterije | UINT | IOD_GSM | GSM:.UPS1_StatusBaterije
GSMUPS1Errors10 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[10]
GSMUPS1Errors11 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[11]
GSMUPS1Errors12 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[12]
GSMUPS1Errors13 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[13]
GSMUPS1Errors14 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[14]
GSMUPS1Errors15 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[15]
GSMUPS1Errors16 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[16]
GSMUPS1Errors17 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[17]
GSMUPS1Errors18 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[18]
GSMUPS1Errors19 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[19]
GSMUPS1Errors1 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[1]
GSMUPS1Errors20 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[20]
GSMUPS1Errors21 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[21]
GSMUPS1Errors22 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[22]
GSMUPS1Errors23 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[23]
GSMUPS1Errors24 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[24]
GSMUPS1Errors25 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[25]
GSMUPS1Errors2 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[2]
GSMUPS1Errors3 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[3]
GSMUPS1Errors4 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[4]
GSMUPS1Errors5 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[5]
GSMUPS1Errors6 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[6]
GSMUPS1Errors7 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[7]
GSMUPS1Errors8 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[8]
GSMUPS1Errors9 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[9]
GSMUPS2_StatusBaterije | UINT | IOD_GSM | GSM:.UPS2_StatusBaterije
GSMUPS2Errors10 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[10]
GSMUPS2Errors11 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[11]
GSMUPS2Errors12 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[12]
GSMUPS2Errors13 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[13]
GSMUPS2Errors14 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[14]
GSMUPS2Errors15 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[15]
GSMUPS2Errors16 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[16]
GSMUPS2Errors17 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[17]
GSMUPS2Errors18 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[18]
GSMUPS2Errors19 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[19]
GSMUPS2Errors1 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[1]
GSMUPS2Errors20 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[20]
GSMUPS2Errors21 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[21]
GSMUPS2Errors22 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[22]
GSMUPS2Errors23 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[23]
GSMUPS2Errors24 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[24]
GSMUPS2Errors25 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[25]
GSMUPS2Errors2 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[2]
GSMUPS2Errors3 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[3]
GSMUPS2Errors4 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[4]
GSMUPS2Errors5 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[5]
GSMUPS2Errors6 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[6]
GSMUPS2Errors7 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[7]
GSMUPS2Errors8 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[8]
GSMUPS2Errors9 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[9]
GSMUPS3_StatusBaterije | UINT | IOD_GSM | GSM:.UPS3_StatusBaterije
GSMUPS3Errors10 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[10]
GSMUPS3Errors11 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[11]
GSMUPS3Errors12 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[12]
GSMUPS3Errors13 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[13]
GSMUPS3Errors14 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[14]
GSMUPS3Errors15 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[15]
GSMUPS3Errors16 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[16]
GSMUPS3Errors17 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[17]
GSMUPS3Errors18 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[18]
GSMUPS3Errors19 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[19]
GSMUPS3Errors1 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[1]
GSMUPS3Errors20 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[20]
GSMUPS3Errors21 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[21]
GSMUPS3Errors22 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[22]
GSMUPS3Errors23 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[23]
GSMUPS3Errors24 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[24]
GSMUPS3Errors25 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[25]
GSMUPS3Errors2 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[2]
GSMUPS3Errors3 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[3]
GSMUPS3Errors4 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[4]
GSMUPS3Errors5 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[5]
GSMUPS3Errors6 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[6]
GSMUPS3Errors7 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[7]
GSMUPS3Errors8 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[8]
GSMUPS3Errors9 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[9]
GSMUPS1AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmAwaitingPower
GSMUPS1AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmBypassBad
GSMUPS1AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmChargerFailed
GSMUPS1AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmCommunicationsLost
GSMUPS1AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmDepletedBattery
GSMUPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmDiagnosticTestFailed
GSMUPS1AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmInverterError
GSMUPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmIzhodOffKotZahtevano
GSMUPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmIzhodPreobremenjen
GSMUPS1AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmLowBattery
GSMUPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmNapakaNaVarovalki
GSMUPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmNapakaNaVentilatorju
GSMUPS1AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmOnBattery
GSMUPS1AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmOnBypass
GSMUPS1AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmShutdownImminent
GSMUPS1AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmShutdownPending
GSMUPS1AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmSlabaBaterija
GSMUPS1AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmSplosnaNapaka
GSMUPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmStanjeIzhodaIzvenToleranc
GSMUPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmStanjeVhodaIzvenToleranc
GSMUPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmTemperaturaIzvenToleranc
GSMUPS1AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmTestInProgres
GSMUPS1AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSIzhodOff
GSMUPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSOffKotZahtevano
GSMUPS1AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSSystemOff
GSMUPS1EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[1].EstimatedChargeRemaining
GSMUPS1EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[1].EstimatedMinutesRemaining
GSMUPS1InverterStatus | INT | IOD_GSM | GSM:.UPS[1].InverterStatus
GSMUPS1IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL1
GSMUPS1IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL2
GSMUPS1IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL3
GSMUPS1Napaka | DIGITAL | IOD_GSM | GSM:.UPS[1].Napaka
GSMUPS1NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[1].NapetostBaterije
GSMUPS1OutputStatus | INT | IOD_GSM | GSM:.UPS[1].OutputStatus
GSMUPS1StatusBaterije | UINT | IOD_GSM | GSM:.UPS[1].StatusBaterije
GSMUPS1StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusEcomodeAktiven
GSMUPS1StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusInverterIsOn
GSMUPS1StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusStopOperation
GSMUPS1SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[1].SteviloIzpadovVhodneLinije
GSMUPS1TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[1].TemperaturaBaterije
GSMUPS1UnitStatus | INT | IOD_GSM | GSM:.UPS[1].UnitStatus
GSMUPS1VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL1
GSMUPS1VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL2
GSMUPS1VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL3
GSMUPS1VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL1
GSMUPS1VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL2
GSMUPS1VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL3
GSMUPS2AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmAwaitingPower
GSMUPS2AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmBypassBad
GSMUPS2AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmChargerFailed
GSMUPS2AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmCommunicationsLost
GSMUPS2AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmDepletedBattery
GSMUPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmDiagnosticTestFailed
GSMUPS2AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmInverterError
GSMUPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmIzhodOffKotZahtevano
GSMUPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmIzhodPreobremenjen
GSMUPS2AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmLowBattery
GSMUPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmNapakaNaVarovalki
GSMUPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmNapakaNaVentilatorju
GSMUPS2AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmOnBattery
GSMUPS2AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmOnBypass
GSMUPS2AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmShutdownImminent
GSMUPS2AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmShutdownPending
GSMUPS2AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmSlabaBaterija
GSMUPS2AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmSplosnaNapaka
GSMUPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmStanjeIzhodaIzvenToleranc
GSMUPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmStanjeVhodaIzvenToleranc
GSMUPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmTemperaturaIzvenToleranc
GSMUPS2AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmTestInProgres
GSMUPS2AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSIzhodOff
GSMUPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSOffKotZahtevano
GSMUPS2AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSSystemOff
GSMUPS2EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[2].EstimatedChargeRemaining
GSMUPS2EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[2].EstimatedMinutesRemaining
GSMUPS2InverterStatus | INT | IOD_GSM | GSM:.UPS[2].InverterStatus
GSMUPS2IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL1
GSMUPS2IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL2
GSMUPS2IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL3
GSMUPS2Napaka | DIGITAL | IOD_GSM | GSM:.UPS[2].Napaka
GSMUPS2NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[2].NapetostBaterije
GSMUPS2OutputStatus | INT | IOD_GSM | GSM:.UPS[2].OutputStatus
GSMUPS2StatusBaterije | UINT | IOD_GSM | GSM:.UPS[2].StatusBaterije
GSMUPS2StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusEcomodeAktiven
GSMUPS2StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusInverterIsOn
GSMUPS2StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusStopOperation
GSMUPS2SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[2].SteviloIzpadovVhodneLinije
GSMUPS2TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[2].TemperaturaBaterije
GSMUPS2UnitStatus | INT | IOD_GSM | GSM:.UPS[2].UnitStatus
GSMUPS2VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL1
GSMUPS2VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL2
GSMUPS2VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL3
GSMUPS2VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL1
GSMUPS2VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL2
GSMUPS2VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL3
GSMUPS3AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmAwaitingPower
GSMUPS3AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmBypassBad
GSMUPS3AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmChargerFailed
GSMUPS3AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmCommunicationsLost
GSMUPS3AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmDepletedBattery
GSMUPS3AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmDiagnosticTestFailed
GSMUPS3AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmInverterError
GSMUPS3AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmIzhodOffKotZahtevano
GSMUPS3AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmIzhodPreobremenjen
GSMUPS3AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmLowBattery
GSMUPS3AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmNapakaNaVarovalki
GSMUPS3AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmNapakaNaVentilatorju
GSMUPS3AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmOnBattery
GSMUPS3AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmOnBypass
GSMUPS3AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmShutdownImminent
GSMUPS3AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmShutdownPending
GSMUPS3AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmSlabaBaterija
GSMUPS3AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmSplosnaNapaka
GSMUPS3AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmStanjeIzhodaIzvenToleranc
GSMUPS3AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmStanjeVhodaIzvenToleranc
GSMUPS3AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmTemperaturaIzvenToleranc
GSMUPS3AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmTestInProgres
GSMUPS3AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSIzhodOff
GSMUPS3AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSOffKotZahtevano
GSMUPS3AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSSystemOff
GSMUPS3EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[3].EstimatedChargeRemaining
GSMUPS3EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[3].EstimatedMinutesRemaining
GSMUPS3InverterStatus | INT | IOD_GSM | GSM:.UPS[3].InverterStatus
GSMUPS3IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL1
GSMUPS3IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL2
GSMUPS3IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL3
GSMUPS3Napaka | DIGITAL | IOD_GSM | GSM:.UPS[3].Napaka
GSMUPS3NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[3].NapetostBaterije
GSMUPS3OutputStatus | INT | IOD_GSM | GSM:.UPS[3].OutputStatus
GSMUPS3StatusBaterije | UINT | IOD_GSM | GSM:.UPS[3].StatusBaterije
GSMUPS3StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusEcomodeAktiven
GSMUPS3StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusInverterIsOn
GSMUPS3StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusStopOperation
GSMUPS3SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[3].SteviloIzpadovVhodneLinije
GSMUPS3TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[3].TemperaturaBaterije
GSMUPS3UnitStatus | INT | IOD_GSM | GSM:.UPS[3].UnitStatus
GSMUPS3VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL1
GSMUPS3VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL2
GSMUPS3VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL3
GSMUPS3VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL1
GSMUPS3VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL2
GSMUPS3VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL3
GSMUPS_A_V23_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_A_V23_delovanje
GSMUPS_A_V23_napaka | DIGITAL | IOD_GSM | GSM:.UPS_A_V23_napaka
GSMups_alarm | DIGITAL | IOD_GSM | GSM:.ups_alarm
GSMups_baterijski_nac | DIGITAL | IOD_GSM | GSM:.ups_baterijski_nac
GSMUPS_MGE1BatteryBackupTime | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryBackupTime
GSMUPS_MGE1BatteryChargedState | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryChargedState
GSMUPS_MGE1BatteryChargingLevel | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryChargingLevel
GSMUPS_MGE1BatteryCircuitBreaker | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryCircuitBreaker
GSMUPS_MGE1BatteryCompInProgress | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryCompInProgress
GSMUPS_MGE1BatteryFuseFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryFuseFault
GSMUPS_MGE1BatteryLowWarning | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryLowWarning
GSMUPS_MGE1BatteryRechargeDuration | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryRechargeDuration
GSMUPS_MGE1BatteryTempOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryTempOutOfToler
GSMUPS_MGE1BypassInFreeFrequency | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BypassInFreeFrequency
GSMUPS_MGE1ChargerGeneralFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].ChargerGeneralFault
GSMUPS_MGE1DeviceVentilationFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].DeviceVentilationFault
GSMUPS_MGE1I1output | INT | IOD_GSM | GSM:.UPS_MGE[1].I1output
GSMUPS_MGE1I2output | INT | IOD_GSM | GSM:.UPS_MGE[1].I2output
GSMUPS_MGE1I3output | INT | IOD_GSM | GSM:.UPS_MGE[1].I3output
GSMUPS_MGE1InverterFrequency | INT | IOD_GSM | GSM:.UPS_MGE[1].InverterFrequency
GSMUPS_MGE1InverterFuseFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterFuseFault
GSMUPS_MGE1InverterOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterOverload
GSMUPS_MGE1InverterThermalOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterThermalOverload
GSMUPS_MGE1Mains1VoltOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains1VoltOutOfToler
GSMUPS_MGE1Mains2Overload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains2Overload
GSMUPS_MGE1Mains2VoltOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains2VoltOutOfToler
GSMUPS_MGE1MaintenancePosition | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].MaintenancePosition
GSMUPS_MGE1ManualBypassSwitch | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].ManualBypassSwitch
GSMUPS_MGE1NapakaNaVarovalkah | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].NapakaNaVarovalkah
GSMUPS_MGE1OutputActivePower1 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower1
GSMUPS_MGE1OutputActivePower2 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower2
GSMUPS_MGE1OutputActivePower3 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower3
GSMUPS_MGE1OutputFrequency | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputFrequency
GSMUPS_MGE1OutputInShortCircuit | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputInShortCircuit
GSMUPS_MGE1OutputLoadLevel | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputLoadLevel
GSMUPS_MGE1OutputOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputOverload
GSMUPS_MGE1OutputThermalOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputThermalOverload
GSMUPS_MGE1RectifierOn | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].RectifierOn
GSMUPS_MGE1RectifierThermOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].RectifierThermOverload
GSMUPS_MGE1Skupna_napaka | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Skupna_napaka
GSMUPS_MGE1StatusBaterije | INT | IOD_GSM | GSM:.UPS_MGE[1].StatusBaterije | BYTE
GSMUPS_MGE1U12mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U12mains1
GSMUPS_MGE1U12mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U12mains2
GSMUPS_MGE1U1N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U1N_inverter
GSMUPS_MGE1U1N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U1N_output
GSMUPS_MGE1U23mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U23mains1
GSMUPS_MGE1U23mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U23mains2
GSMUPS_MGE1U2N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U2N_inverter
GSMUPS_MGE1U2N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U2N_output
GSMUPS_MGE1U31mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U31mains1
GSMUPS_MGE1U31mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U31mains2
GSMUPS_MGE1U3N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U3N_inverter
GSMUPS_MGE1U3N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U3N_output
GSMUPS_MGE1U_battery | INT | IOD_GSM | GSM:.UPS_MGE[1].U_battery
GSMUPS_MGE1UPS_coupled | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_coupled
GSMUPS_MGE1UPS_error | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_error
GSMUPS_MGE1UPS_in_backup | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_in_backup
GSMups_polnjenje | DIGITAL | IOD_GSM | GSM:.ups_polnjenje
GSMUPS_V23_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_V23_delovanje
GSMUPS_V23_napaka | DIGITAL | IOD_GSM | GSM:.UPS_V23_napaka
GSMUPS_V25_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_V25_delovanje
GSMUPS_V25_napaka | DIGITAL | IOD_GSM | GSM:.UPS_V25_napaka
GSMUPSMGEErrors10 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[10]
GSMUPSMGEErrors11 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[11]
GSMUPSMGEErrors12 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[12]
GSMUPSMGEErrors13 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[13]
GSMUPSMGEErrors14 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[14]
GSMUPSMGEErrors15 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[15]
GSMUPSMGEErrors16 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[16]
GSMUPSMGEErrors17 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[17]
GSMUPSMGEErrors1 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[1]
GSMUPSMGEErrors2 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[2]
GSMUPSMGEErrors3 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[3]
GSMUPSMGEErrors4 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[4]
GSMUPSMGEErrors5 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[5]
GSMUPSMGEErrors6 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[6]
GSMUPSMGEErrors7 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[7]
GSMUPSMGEErrors8 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[8]
GSMUPSMGEErrors9 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[9]
GSMUserCurrentLevel | INT | IOD_GSM | GSM:.UserCurrentLevel | BYTE
GSMUserCurrentName | STRING | IOD_GSM | GSM:.UserCurrentName
GSMUserDisplay | STRING | IOD_GSM | GSM:.UserDisplay
GSMUserLoggedIn | DIGITAL | IOD_GSM | GSM:.UserLoggedIn
GSMVLAZILEC1_delovanje | DIGITAL | IOD_GSM | GSM:.VLAZILEC1_delovanje
GSMVLAZILEC1_napaka | DIGITAL | IOD_GSM | GSM:.VLAZILEC1_napaka
GSMVLAZILEC2_delovanje | DIGITAL | IOD_GSM | GSM:.VLAZILEC2_delovanje
GSMVLAZILEC2_napaka | DIGITAL | IOD_GSM | GSM:.VLAZILEC2_napaka
GSMXVH_AlarmOn | DIGITAL | IOD_GSM | GSM:.XVH_AlarmOn
GSMXVH_enopolna_napaka | DIGITAL | IOD_GSM | GSM:.XVH_enopolna_napaka

## variable_2
GSMAGR_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.AGR_Gasenje_alarm
GSMAGR_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.AGR_PozCent_napaka
GSMAGR_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.AGR_PozSenzor_okvara
GSMAlarmGenUPS_A_V23 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_A_V23
GSMAlarmGenUPS_V23 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_V23
GSMAlarmGenUPS_V25 | DIGITAL | IOD_GSM | GSM:.AlarmGenUPS_V25
GSMAlarmPMM1VirATokPrevisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirATokPrevisok
GSMAlarmPMM1VirATokVisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirATokVisok
GSMAlarmPMM1VirBTokPrevisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirBTokPrevisok
GSMAlarmPMM1VirBTokVisok | DIGITAL | IOD_GSM | GSM:.AlarmPMM1VirBTokVisok
GSMAlarmPMM2x17nad8010 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[10]
GSMAlarmPMM2x17nad8011 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[11]
GSMAlarmPMM2x17nad8012 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[12]
GSMAlarmPMM2x17nad8013 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[13]
GSMAlarmPMM2x17nad8014 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[14]
GSMAlarmPMM2x17nad8015 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[15]
GSMAlarmPMM2x17nad8016 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[16]
GSMAlarmPMM2x17nad8017 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[17]
GSMAlarmPMM2x17nad8018 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[18]
GSMAlarmPMM2x17nad8019 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[19]
GSMAlarmPMM2x17nad801 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[1]
GSMAlarmPMM2x17nad8020 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[20]
GSMAlarmPMM2x17nad8021 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[21]
GSMAlarmPMM2x17nad8022 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[22]
GSMAlarmPMM2x17nad8023 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[23]
GSMAlarmPMM2x17nad8024 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[24]
GSMAlarmPMM2x17nad8025 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[25]
GSMAlarmPMM2x17nad8026 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[26]
GSMAlarmPMM2x17nad8027 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[27]
GSMAlarmPMM2x17nad8028 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[28]
GSMAlarmPMM2x17nad8029 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[29]
GSMAlarmPMM2x17nad802 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[2]
GSMAlarmPMM2x17nad8030 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[30]
GSMAlarmPMM2x17nad8031 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[31]
GSMAlarmPMM2x17nad8032 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[32]
GSMAlarmPMM2x17nad8033 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[33]
GSMAlarmPMM2x17nad8034 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[34]
GSMAlarmPMM2x17nad8035 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[35]
GSMAlarmPMM2x17nad8036 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[36]
GSMAlarmPMM2x17nad8037 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[37]
GSMAlarmPMM2x17nad8038 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[38]
GSMAlarmPMM2x17nad8039 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[39]
GSMAlarmPMM2x17nad803 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[3]
GSMAlarmPMM2x17nad8040 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[40]
GSMAlarmPMM2x17nad8041 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[41]
GSMAlarmPMM2x17nad8042 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[42]
GSMAlarmPMM2x17nad804 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[4]
GSMAlarmPMM2x17nad805 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[5]
GSMAlarmPMM2x17nad806 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[6]
GSMAlarmPMM2x17nad807 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[7]
GSMAlarmPMM2x17nad808 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[8]
GSMAlarmPMM2x17nad809 | DIGITAL | IOD_GSM | GSM:.AlarmPMM2x17nad80[9]
GSMALM_AGR_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.ALM_AGR_Gasenje_alarm
GSMALM_AGR_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.ALM_AGR_PozCent_napaka
GSMALM_AGR_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.ALM_AGR_PozSenzor_okvara
GSMALM_GSM_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.ALM_GSM_Gasenje_alarm
GSMALM_GSM_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.ALM_GSM_PozCent_napaka
GSMALM_GSM_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.ALM_GSM_PozSenzor_okvara
GSMCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Dnevne_energija_scada1
GSMCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Dnevne_energija_scada2
GSMCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Mesecna_energija_scada1
GSMCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Mesecna_energija_scada2
GSMCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Tedenska_energija_scada1
GSMCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_GSM | GSM:.Circ_Vpis_Tedenska_energija_scada2
GSMComError | DIGITAL | IOD_GSM | GSM:.ComError
GSMComSCADA | DIGITAL | IOD_GSM | GSM:.ComSCADA
GSMComSCADA1 | DIGITAL | IOD_GSM | GSM:.ComSCADA1
GSMComSCADA2 | DIGITAL | IOD_GSM | GSM:.ComSCADA2
GSMComSCADA3 | DIGITAL | IOD_GSM | GSM:.ComSCADA3
GSMDI1_I11 | DIGITAL | IOD_GSM | GSM:.DI1_I11
GSMDI1_I9 | DIGITAL | IOD_GSM | GSM:.DI1_I9
GSMDI2_I14 | DIGITAL | IOD_GSM | GSM:.DI2_I14
GSMDI2_I15 | DIGITAL | IOD_GSM | GSM:.DI2_I15
GSMDI_R3KC_A_Q21_IzkljucenIzpad | DIGITAL | IOD_GSM | GSM:.DI_R3KC_A_Q21_IzkljucenIzpad
GSMDI_R3KC_A_Q22_IzkljucenIzpad | DIGITAL | IOD_GSM | GSM:.DI_R3KC_A_Q22_IzkljucenIzpad
GSMDI_SBi_RAZS_AA_Izolacija_NOT_OK | DIGITAL | IOD_GSM | GSM:.DI_SBi_RAZS_AA_Izolacija_NOT_OK
GSMDI_SBi_RAZS_AB_Izolacija_NOT_OK | DIGITAL | IOD_GSM | GSM:.DI_SBi_RAZS_AB_Izolacija_NOT_OK
GSMErrComCirc1 | DIGITAL | IOD_GSM | GSM:.ErrComCirc[1]
GSMErrComKlima1 | DIGITAL | IOD_GSM | GSM:.ErrComKlima[1]
GSMErrComKlima2 | DIGITAL | IOD_GSM | GSM:.ErrComKlima[2]
GSMErrComPMM1 | DIGITAL | IOD_GSM | GSM:.ErrComPMM[1]
GSMErrComPMM2 | DIGITAL | IOD_GSM | GSM:.ErrComPMM[2]
GSMErrComPort2 | DIGITAL | IOD_GSM | GSM:.ErrComPort2
GSMErrComPort3 | DIGITAL | IOD_GSM | GSM:.ErrComPort3
GSMErrComPort4 | DIGITAL | IOD_GSM | GSM:.ErrComPort4
GSMErrComUPS1 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[1]
GSMErrComUPS2 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[2]
GSMErrComUPS3 | DIGITAL | IOD_GSM | GSM:.ErrComUPS[3]
GSMErrComUPSMGE1 | DIGITAL | IOD_GSM | GSM:.ErrComUPSMGE[1]
GSMF1_1_zascita_ok | DIGITAL | IOD_GSM | GSM:.F1_1_zascita_ok
GSMGSM_Gasenje_alarm | DIGITAL | IOD_GSM | GSM:.GSM_Gasenje_alarm
GSMGSM_PozCent_napaka | DIGITAL | IOD_GSM | GSM:.GSM_PozCent_napaka
GSMGSM_PozSenzor_okvara | DIGITAL | IOD_GSM | GSM:.GSM_PozSenzor_okvara
GSMK1_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K1_SkupnaNapaka
GSMK1_vklop_izklop_poteka | DIGITAL | IOD_GSM | GSM:.K1_vklop_izklop_poteka
GSMK1AlarmPozara | DIGITAL | IOD_GSM | GSM:.K1AlarmPozara
GSMK1KlimaZdruzenAlarm | DIGITAL | IOD_GSM | GSM:.K1KlimaZdruzenAlarm
GSMK1NiPretoka | DIGITAL | IOD_GSM | GSM:.K1NiPretoka
GSMK1OkvaraRototerma | DIGITAL | IOD_GSM | GSM:.K1OkvaraRototerma
GSMK1OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.K1OkvaraVlazNap
GSMK1PreobMotCrpGr | DIGITAL | IOD_GSM | GSM:.K1PreobMotCrpGr
GSMK1PreobMotVent | DIGITAL | IOD_GSM | GSM:.K1PreobMotVent
GSMK1ProtizamrzZascAkt | DIGITAL | IOD_GSM | GSM:.K1ProtizamrzZascAkt
GSMK1ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.K1ZamasenostFiltra
GSMK2_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K2_SkupnaNapaka
GSMK2_vklop_izklop_poteka | DIGITAL | IOD_GSM | GSM:.K2_vklop_izklop_poteka
GSMK2AlarmPozara | DIGITAL | IOD_GSM | GSM:.K2AlarmPozara
GSMK2KlimaZdruzenAlarm | DIGITAL | IOD_GSM | GSM:.K2KlimaZdruzenAlarm
GSMK2NiPretoka | DIGITAL | IOD_GSM | GSM:.K2NiPretoka
GSMK2OkvaraRototerma | DIGITAL | IOD_GSM | GSM:.K2OkvaraRototerma
GSMK2OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.K2OkvaraVlazNap
GSMK2PreobMotCrpGr | DIGITAL | IOD_GSM | GSM:.K2PreobMotCrpGr
GSMK2PreobMotVent | DIGITAL | IOD_GSM | GSM:.K2PreobMotVent
GSMK2ProtizamrzZascAkt | DIGITAL | IOD_GSM | GSM:.K2ProtizamrzZascAkt
GSMK2ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.K2ZamasenostFiltra
GSMK3_deluje | DIGITAL | IOD_GSM | GSM:.K3_deluje
GSMK3_SkupnaNapaka | DIGITAL | IOD_GSM | GSM:.K3_SkupnaNapaka
GSMKlima1_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima1_izkljucena
GSMKLIMA1_kke_pogon | DIGITAL | IOD_GSM | GSM:.KLIMA1_kke_pogon
GSMKLIMA1_krm_nap_ok | DIGITAL | IOD_GSM | GSM:.KLIMA1_krm_nap_ok
GSMKlima2_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima2_izkljucena
GSMKlima3_izkljucena | DIGITAL | IOD_GSM | GSM:.Klima3_izkljucena
GSMKlima1Alarm_pozar | DIGITAL | IOD_GSM | GSM:.Klima[1].Alarm_pozar
GSMKlima1DelVentHit1 | DIGITAL | IOD_GSM | GSM:.Klima[1].DelVentHit1
GSMKlima1DelVentHit2 | DIGITAL | IOD_GSM | GSM:.Klima[1].DelVentHit2
GSMKlima1Ni_pretoka | DIGITAL | IOD_GSM | GSM:.Klima[1].Ni_pretoka
GSMKlima1OkvaraRototerm | DIGITAL | IOD_GSM | GSM:.Klima[1].OkvaraRototerm
GSMKlima1OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.Klima[1].OkvaraVlazNap
GSMKlima1PreobMotCrpGrel | DIGITAL | IOD_GSM | GSM:.Klima[1].PreobMotCrpGrel
GSMKlima1PreobMotVent | DIGITAL | IOD_GSM | GSM:.Klima[1].PreobMotVent
GSMKlima1ProtizamrzZascAktivna | DIGITAL | IOD_GSM | GSM:.Klima[1].ProtizamrzZascAktivna
GSMKlima1VklopRegKlimata | DIGITAL | IOD_GSM | GSM:.Klima[1].VklopRegKlimata
GSMKlima1ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.Klima[1].ZamasenostFiltra
GSMKlima1ZdruzAlarmA | DIGITAL | IOD_GSM | GSM:.Klima[1].ZdruzAlarmA
GSMKlima1ZdruzAlarmB | DIGITAL | IOD_GSM | GSM:.Klima[1].ZdruzAlarmB
GSMKlima2Alarm_pozar | DIGITAL | IOD_GSM | GSM:.Klima[2].Alarm_pozar
GSMKlima2DelVentHit1 | DIGITAL | IOD_GSM | GSM:.Klima[2].DelVentHit1
GSMKlima2DelVentHit2 | DIGITAL | IOD_GSM | GSM:.Klima[2].DelVentHit2
GSMKlima2Ni_pretoka | DIGITAL | IOD_GSM | GSM:.Klima[2].Ni_pretoka
GSMKlima2OkvaraRototerm | DIGITAL | IOD_GSM | GSM:.Klima[2].OkvaraRototerm
GSMKlima2OkvaraVlazNap | DIGITAL | IOD_GSM | GSM:.Klima[2].OkvaraVlazNap
GSMKlima2PreobMotCrpGrel | DIGITAL | IOD_GSM | GSM:.Klima[2].PreobMotCrpGrel
GSMKlima2PreobMotVent | DIGITAL | IOD_GSM | GSM:.Klima[2].PreobMotVent
GSMKlima2ProtizamrzZascAktivna | DIGITAL | IOD_GSM | GSM:.Klima[2].ProtizamrzZascAktivna
GSMKlima2VklopRegKlimata | DIGITAL | IOD_GSM | GSM:.Klima[2].VklopRegKlimata
GSMKlima2ZamasenostFiltra | DIGITAL | IOD_GSM | GSM:.Klima[2].ZamasenostFiltra
GSMKlima2ZdruzAlarmA | DIGITAL | IOD_GSM | GSM:.Klima[2].ZdruzAlarmA
GSMKlima2ZdruzAlarmB | DIGITAL | IOD_GSM | GSM:.Klima[2].ZdruzAlarmB
GSMKLIMA_m1_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMA_m1_delovanje
GSMKLIMA_m1_napaka | DIGITAL | IOD_GSM | GSM:.KLIMA_m1_napaka
GSMKLIMA_m2_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMA_m2_delovanje
GSMKLIMA_m2_napaka | DIGITAL | IOD_GSM | GSM:.KLIMA_m2_napaka
GSMKLIMAT1_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMAT1_delovanje
GSMKLIMAT1_napaka | DIGITAL | IOD_GSM | GSM:.KLIMAT1_napaka
GSMKLIMAT1_R_zakleni | DIGITAL | IOD_GSM | GSM:.KLIMAT1_R_zakleni
GSMKLIMAT1_vklop_delovanja | DIGITAL | IOD_GSM | GSM:.KLIMAT1_vklop_delovanja
GSMKLIMAT1_vklop_delovanjaR | DIGITAL | IOD_GSM | GSM:.KLIMAT1_vklop_delovanjaR
GSMKLIMAT2_delovanje | DIGITAL | IOD_GSM | GSM:.KLIMAT2_delovanje
GSMKLIMAT2_napaka | DIGITAL | IOD_GSM | GSM:.KLIMAT2_napaka
GSMKLIMAT2_R_zakleni | DIGITAL | IOD_GSM | GSM:.KLIMAT2_R_zakleni
GSMKLIMAT2_vklop_delovanja | DIGITAL | IOD_GSM | GSM:.KLIMAT2_vklop_delovanja
GSMKLIMAT2_vklop_delovanjaR | DIGITAL | IOD_GSM | GSM:.KLIMAT2_vklop_delovanjaR
GSMKlimeAVTO | DIGITAL | IOD_GSM | GSM:.KlimeAVTO
GSMN_F1_1_zascita_ok | DIGITAL | IOD_GSM | GSM:.N_F1_1_zascita_ok
GSMN_KLIMA1_krm_nap_ok | DIGITAL | IOD_GSM | GSM:.N_KLIMA1_krm_nap_ok
GSMN_KLIMAT1_napaka | DIGITAL | IOD_GSM | GSM:.N_KLIMAT1_napaka
GSMN_KLIMAT2_napaka | DIGITAL | IOD_GSM | GSM:.N_KLIMAT2_napaka
GSMN_KlimeAVTO | DIGITAL | IOD_GSM | GSM:.N_KlimeAVTO
GSMN_Q12_izpad | DIGITAL | IOD_GSM | GSM:.N_Q12_izpad
GSMN_UPS_A_V23_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_A_V23_delovanje
GSMN_UPS_A_V23_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_A_V23_napaka
GSMN_UPS_V23_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_V23_delovanje
GSMN_UPS_V23_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_V23_napaka
GSMN_UPS_V25_delovanje | DIGITAL | IOD_GSM | GSM:.N_UPS_V25_delovanje
GSMN_UPS_V25_napaka | DIGITAL | IOD_GSM | GSM:.N_UPS_V25_napaka
GSMN_VLAZILEC1_napaka | DIGITAL | IOD_GSM | GSM:.N_VLAZILEC1_napaka
GSMN_VLAZILEC2_napaka | DIGITAL | IOD_GSM | GSM:.N_VLAZILEC2_napaka
GSMnapaka_kom_panel | DIGITAL | IOD_GSM | GSM:.napaka_kom_panel
GSMnapaka_kom_scada | DIGITAL | IOD_GSM | GSM:.napaka_kom_scada
GSMnapaka_kom_scada2 | DIGITAL | IOD_GSM | GSM:.napaka_kom_scada2
GSMNapakaSenzorSkupno | DIGITAL | IOD_GSM | GSM:.NapakaSenzorSkupno
GSMNapakaSenzorVlagaHIA1 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA1
GSMNapakaSenzorVlagaHIA2 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA2
GSMNapakaSenzorVlagaHIA3 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA3
GSMNapakaSenzorVlagaHIA4 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA4
GSMNapakaSenzorVlagaHIA5 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA5
GSMNapakaSenzorVlagaHIA6 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA6
GSMNapakaSenzorVlagaHIA7 | DIGITAL | IOD_GSM | GSM:.NapakaSenzorVlagaHIA7
GSMNapakaTSTempTIA1 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA1
GSMNapakaTSTempTIA2 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA2
GSMNapakaTSTempTIA3 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA3
GSMNapakaTSTempTIA4 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA4
GSMNapakaTSTempTIA5 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA5
GSMNapakaTSTempTIA6 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA6
GSMNapakaTSTempTIA7 | DIGITAL | IOD_GSM | GSM:.NapakaTSTempTIA7
GSMOpozoriloPMM2x17med60in8010 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[10]
GSMOpozoriloPMM2x17med60in8011 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[11]
GSMOpozoriloPMM2x17med60in8012 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[12]
GSMOpozoriloPMM2x17med60in8013 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[13]
GSMOpozoriloPMM2x17med60in8014 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[14]
GSMOpozoriloPMM2x17med60in8015 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[15]
GSMOpozoriloPMM2x17med60in8016 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[16]
GSMOpozoriloPMM2x17med60in8017 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[17]
GSMOpozoriloPMM2x17med60in8018 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[18]
GSMOpozoriloPMM2x17med60in8019 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[19]
GSMOpozoriloPMM2x17med60in801 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[1]
GSMOpozoriloPMM2x17med60in8020 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[20]
GSMOpozoriloPMM2x17med60in8021 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[21]
GSMOpozoriloPMM2x17med60in8022 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[22]
GSMOpozoriloPMM2x17med60in8023 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[23]
GSMOpozoriloPMM2x17med60in8024 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[24]
GSMOpozoriloPMM2x17med60in8025 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[25]
GSMOpozoriloPMM2x17med60in8026 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[26]
GSMOpozoriloPMM2x17med60in8027 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[27]
GSMOpozoriloPMM2x17med60in8028 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[28]
GSMOpozoriloPMM2x17med60in8029 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[29]
GSMOpozoriloPMM2x17med60in802 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[2]
GSMOpozoriloPMM2x17med60in8030 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[30]
GSMOpozoriloPMM2x17med60in8031 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[31]
GSMOpozoriloPMM2x17med60in8032 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[32]
GSMOpozoriloPMM2x17med60in8033 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[33]
GSMOpozoriloPMM2x17med60in8034 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[34]
GSMOpozoriloPMM2x17med60in8035 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[35]
GSMOpozoriloPMM2x17med60in8036 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[36]
GSMOpozoriloPMM2x17med60in8037 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[37]
GSMOpozoriloPMM2x17med60in8038 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[38]
GSMOpozoriloPMM2x17med60in8039 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[39]
GSMOpozoriloPMM2x17med60in803 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[3]
GSMOpozoriloPMM2x17med60in8040 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[40]
GSMOpozoriloPMM2x17med60in8041 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[41]
GSMOpozoriloPMM2x17med60in8042 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[42]
GSMOpozoriloPMM2x17med60in804 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[4]
GSMOpozoriloPMM2x17med60in805 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[5]
GSMOpozoriloPMM2x17med60in806 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[6]
GSMOpozoriloPMM2x17med60in807 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[7]
GSMOpozoriloPMM2x17med60in808 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[8]
GSMOpozoriloPMM2x17med60in809 | DIGITAL | IOD_GSM | GSM:.OpozoriloPMM2x17med60in80[9]
GSMPMM1OverCurrentBetw1 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[1]
GSMPMM1OverCurrentBetw2 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[2]
GSMPMM1OverCurrentBetw3 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentBetw[3]
GSMPMM1OverCurrentOver1 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[1]
GSMPMM1OverCurrentOver2 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[2]
GSMPMM1OverCurrentOver3 | DIGITAL | IOD_GSM | GSM:.PMM1OverCurrentOver[3]
GSMPMM2QA1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_GSM | GSM:.PMM2.QA1_GlStik_IZKLOP_IZPAD
GSMPMM2QB1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_GSM | GSM:.PMM2.QB1_GlStik_IZKLOP_IZPAD
GSMPMM2SkNapaka_med60in80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapaka_med60in80
GSMPMM2SkNapaka_nad80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapaka_nad80
GSMPMM2SkNapakaVirA_med60in80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapakaVirA_med60in80
GSMPMM2SkNapakaVirA_nad80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapakaVirA_nad80
GSMPMM2SkNapakaVirB_med60in80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapakaVirB_med60in80
GSMPMM2SkNapakaVirB_nad80 | DIGITAL | IOD_GSM | GSM:.PMM2.SkNapakaVirB_nad80
GSMPMM2VirA_NapakaOzemljitve | DIGITAL | IOD_GSM | GSM:.PMM2.VirA_NapakaOzemljitve
GSMPMM2VirB_NapakaOzemljitve | DIGITAL | IOD_GSM | GSM:.PMM2.VirB_NapakaOzemljitve
GSMPozarnaCentrala_skupno | DIGITAL | IOD_GSM | GSM:.PozarnaCentrala_skupno
GSMPrevisokaTemp | DIGITAL | IOD_GSM | GSM:.PrevisokaTemp
GSMQ0_izkljuceno | DIGITAL | IOD_GSM | GSM:.Q0_izkljuceno
GSMQ0_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q0_vkljuceno
GSMQ12_izkljuceno | DIGITAL | IOD_GSM | GSM:.Q12_izkljuceno
GSMQ12_izpad | DIGITAL | IOD_GSM | GSM:.Q12_izpad
GSMQ12_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q12_vkljuceno
GSMQ21_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q21_vkljuceno
GSMQ22_vkljuceno | DIGITAL | IOD_GSM | GSM:.Q22_vkljuceno
GSMrazlitjeLAH1 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH1
GSMrazlitjeLAH2 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH2
GSMrazlitjeLAH3 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH3
GSMrazlitjeLAH4 | DIGITAL | IOD_GSM | GSM:.razlitjeLAH4
GSMSetDateTime | DIGITAL | IOD_GSM | GSM:.SetDateTime
GSMSetDateTimeDemand | DIGITAL | IOD_GSM | GSM:.SetDateTimeDemand
GSMSetDateTimeError | DIGITAL | IOD_GSM | GSM:.SetDateTimeError
GSMSetDateTimeFinished | DIGITAL | IOD_GSM | GSM:.SetDateTimeFinished
GSMSkupneNapakeNaprav_PMM17VirBVirA | DIGITAL | IOD_GSM | GSM:.SkupneNapakeNaprav_PMM17VirBVirA
GSMSlabaBaterijaPLC | DIGITAL | IOD_GSM | GSM:.SlabaBaterijaPLC
GSMTempPovp234Previs | DIGITAL | IOD_GSM | GSM:.TempPovp234Previs
GSMTempPovp56Previs | DIGITAL | IOD_GSM | GSM:.TempPovp56Previs
GSMTIA1_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA1_previs_temp
GSMTIA2_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA2_previs_temp
GSMTIA3_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA3_previs_temp
GSMTIA4_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA4_previs_temp
GSMTIA5_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA5_previs_temp
GSMTIA6_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA6_previs_temp
GSMTIA7_previs_temp | DIGITAL | IOD_GSM | GSM:.TIA7_previs_temp
GSMUPS1Errors10 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[10]
GSMUPS1Errors11 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[11]
GSMUPS1Errors12 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[12]
GSMUPS1Errors13 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[13]
GSMUPS1Errors14 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[14]
GSMUPS1Errors15 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[15]
GSMUPS1Errors16 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[16]
GSMUPS1Errors17 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[17]
GSMUPS1Errors18 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[18]
GSMUPS1Errors19 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[19]
GSMUPS1Errors1 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[1]
GSMUPS1Errors20 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[20]
GSMUPS1Errors21 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[21]
GSMUPS1Errors22 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[22]
GSMUPS1Errors23 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[23]
GSMUPS1Errors24 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[24]
GSMUPS1Errors25 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[25]
GSMUPS1Errors2 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[2]
GSMUPS1Errors3 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[3]
GSMUPS1Errors4 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[4]
GSMUPS1Errors5 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[5]
GSMUPS1Errors6 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[6]
GSMUPS1Errors7 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[7]
GSMUPS1Errors8 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[8]
GSMUPS1Errors9 | DIGITAL | IOD_GSM | GSM:.UPS1Errors[9]
GSMUPS2Errors10 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[10]
GSMUPS2Errors11 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[11]
GSMUPS2Errors12 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[12]
GSMUPS2Errors13 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[13]
GSMUPS2Errors14 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[14]
GSMUPS2Errors15 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[15]
GSMUPS2Errors16 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[16]
GSMUPS2Errors17 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[17]
GSMUPS2Errors18 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[18]
GSMUPS2Errors19 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[19]
GSMUPS2Errors1 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[1]
GSMUPS2Errors20 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[20]
GSMUPS2Errors21 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[21]
GSMUPS2Errors22 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[22]
GSMUPS2Errors23 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[23]
GSMUPS2Errors24 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[24]
GSMUPS2Errors25 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[25]
GSMUPS2Errors2 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[2]
GSMUPS2Errors3 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[3]
GSMUPS2Errors4 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[4]
GSMUPS2Errors5 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[5]
GSMUPS2Errors6 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[6]
GSMUPS2Errors7 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[7]
GSMUPS2Errors8 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[8]
GSMUPS2Errors9 | DIGITAL | IOD_GSM | GSM:.UPS2Errors[9]
GSMUPS3Errors10 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[10]
GSMUPS3Errors11 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[11]
GSMUPS3Errors12 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[12]
GSMUPS3Errors13 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[13]
GSMUPS3Errors14 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[14]
GSMUPS3Errors15 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[15]
GSMUPS3Errors16 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[16]
GSMUPS3Errors17 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[17]
GSMUPS3Errors18 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[18]
GSMUPS3Errors19 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[19]
GSMUPS3Errors1 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[1]
GSMUPS3Errors20 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[20]
GSMUPS3Errors21 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[21]
GSMUPS3Errors22 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[22]
GSMUPS3Errors23 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[23]
GSMUPS3Errors24 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[24]
GSMUPS3Errors25 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[25]
GSMUPS3Errors2 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[2]
GSMUPS3Errors3 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[3]
GSMUPS3Errors4 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[4]
GSMUPS3Errors5 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[5]
GSMUPS3Errors6 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[6]
GSMUPS3Errors7 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[7]
GSMUPS3Errors8 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[8]
GSMUPS3Errors9 | DIGITAL | IOD_GSM | GSM:.UPS3Errors[9]
GSMUPS1AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmAwaitingPower
GSMUPS1AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmBypassBad
GSMUPS1AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmChargerFailed
GSMUPS1AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmCommunicationsLost
GSMUPS1AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmDepletedBattery
GSMUPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmDiagnosticTestFailed
GSMUPS1AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmInverterError
GSMUPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmIzhodOffKotZahtevano
GSMUPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmIzhodPreobremenjen
GSMUPS1AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmLowBattery
GSMUPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmNapakaNaVarovalki
GSMUPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmNapakaNaVentilatorju
GSMUPS1AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmOnBattery
GSMUPS1AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmOnBypass
GSMUPS1AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmShutdownImminent
GSMUPS1AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmShutdownPending
GSMUPS1AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmSlabaBaterija
GSMUPS1AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmSplosnaNapaka
GSMUPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmStanjeIzhodaIzvenToleranc
GSMUPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmStanjeVhodaIzvenToleranc
GSMUPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmTemperaturaIzvenToleranc
GSMUPS1AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmTestInProgres
GSMUPS1AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSIzhodOff
GSMUPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSOffKotZahtevano
GSMUPS1AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[1].AlarmUPSSystemOff
GSMUPS1Napaka | DIGITAL | IOD_GSM | GSM:.UPS[1].Napaka
GSMUPS1StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusEcomodeAktiven
GSMUPS1StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusInverterIsOn
GSMUPS1StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[1].StatusStopOperation
GSMUPS2AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmAwaitingPower
GSMUPS2AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmBypassBad
GSMUPS2AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmChargerFailed
GSMUPS2AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmCommunicationsLost
GSMUPS2AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmDepletedBattery
GSMUPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmDiagnosticTestFailed
GSMUPS2AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmInverterError
GSMUPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmIzhodOffKotZahtevano
GSMUPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmIzhodPreobremenjen
GSMUPS2AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmLowBattery
GSMUPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmNapakaNaVarovalki
GSMUPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmNapakaNaVentilatorju
GSMUPS2AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmOnBattery
GSMUPS2AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmOnBypass
GSMUPS2AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmShutdownImminent
GSMUPS2AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmShutdownPending
GSMUPS2AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmSlabaBaterija
GSMUPS2AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmSplosnaNapaka
GSMUPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmStanjeIzhodaIzvenToleranc
GSMUPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmStanjeVhodaIzvenToleranc
GSMUPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmTemperaturaIzvenToleranc
GSMUPS2AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmTestInProgres
GSMUPS2AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSIzhodOff
GSMUPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSOffKotZahtevano
GSMUPS2AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[2].AlarmUPSSystemOff
GSMUPS2Napaka | DIGITAL | IOD_GSM | GSM:.UPS[2].Napaka
GSMUPS2StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusEcomodeAktiven
GSMUPS2StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusInverterIsOn
GSMUPS2StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[2].StatusStopOperation
GSMUPS3AlarmAwaitingPower | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmAwaitingPower
GSMUPS3AlarmBypassBad | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmBypassBad
GSMUPS3AlarmChargerFailed | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmChargerFailed
GSMUPS3AlarmCommunicationsLost | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmCommunicationsLost
GSMUPS3AlarmDepletedBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmDepletedBattery
GSMUPS3AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmDiagnosticTestFailed
GSMUPS3AlarmInverterError | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmInverterError
GSMUPS3AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmIzhodOffKotZahtevano
GSMUPS3AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmIzhodPreobremenjen
GSMUPS3AlarmLowBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmLowBattery
GSMUPS3AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmNapakaNaVarovalki
GSMUPS3AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmNapakaNaVentilatorju
GSMUPS3AlarmOnBattery | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmOnBattery
GSMUPS3AlarmOnBypass | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmOnBypass
GSMUPS3AlarmShutdownImminent | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmShutdownImminent
GSMUPS3AlarmShutdownPending | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmShutdownPending
GSMUPS3AlarmSlabaBaterija | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmSlabaBaterija
GSMUPS3AlarmSplosnaNapaka | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmSplosnaNapaka
GSMUPS3AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmStanjeIzhodaIzvenToleranc
GSMUPS3AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmStanjeVhodaIzvenToleranc
GSMUPS3AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmTemperaturaIzvenToleranc
GSMUPS3AlarmTestInProgres | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmTestInProgres
GSMUPS3AlarmUPSIzhodOff | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSIzhodOff
GSMUPS3AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSOffKotZahtevano
GSMUPS3AlarmUPSSystemOff | DIGITAL | IOD_GSM | GSM:.UPS[3].AlarmUPSSystemOff
GSMUPS3Napaka | DIGITAL | IOD_GSM | GSM:.UPS[3].Napaka
GSMUPS3StatusEcomodeAktiven | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusEcomodeAktiven
GSMUPS3StatusInverterIsOn | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusInverterIsOn
GSMUPS3StatusStopOperation | DIGITAL | IOD_GSM | GSM:.UPS[3].StatusStopOperation
GSMUPS_A_V23_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_A_V23_delovanje
GSMUPS_A_V23_napaka | DIGITAL | IOD_GSM | GSM:.UPS_A_V23_napaka
GSMups_alarm | DIGITAL | IOD_GSM | GSM:.ups_alarm
GSMups_baterijski_nac | DIGITAL | IOD_GSM | GSM:.ups_baterijski_nac
GSMUPS_MGE1BatteryChargedState | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryChargedState
GSMUPS_MGE1BatteryCircuitBreaker | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryCircuitBreaker
GSMUPS_MGE1BatteryCompInProgress | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryCompInProgress
GSMUPS_MGE1BatteryFuseFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryFuseFault
GSMUPS_MGE1BatteryLowWarning | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryLowWarning
GSMUPS_MGE1BatteryTempOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BatteryTempOutOfToler
GSMUPS_MGE1BypassInFreeFrequency | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].BypassInFreeFrequency
GSMUPS_MGE1ChargerGeneralFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].ChargerGeneralFault
GSMUPS_MGE1DeviceVentilationFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].DeviceVentilationFault
GSMUPS_MGE1InverterFuseFault | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterFuseFault
GSMUPS_MGE1InverterOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterOverload
GSMUPS_MGE1InverterThermalOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].InverterThermalOverload
GSMUPS_MGE1Mains1VoltOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains1VoltOutOfToler
GSMUPS_MGE1Mains2Overload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains2Overload
GSMUPS_MGE1Mains2VoltOutOfToler | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Mains2VoltOutOfToler
GSMUPS_MGE1MaintenancePosition | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].MaintenancePosition
GSMUPS_MGE1ManualBypassSwitch | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].ManualBypassSwitch
GSMUPS_MGE1NapakaNaVarovalkah | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].NapakaNaVarovalkah
GSMUPS_MGE1OutputInShortCircuit | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputInShortCircuit
GSMUPS_MGE1OutputOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputOverload
GSMUPS_MGE1OutputThermalOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].OutputThermalOverload
GSMUPS_MGE1RectifierOn | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].RectifierOn
GSMUPS_MGE1RectifierThermOverload | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].RectifierThermOverload
GSMUPS_MGE1Skupna_napaka | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].Skupna_napaka
GSMUPS_MGE1UPS_coupled | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_coupled
GSMUPS_MGE1UPS_error | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_error
GSMUPS_MGE1UPS_in_backup | DIGITAL | IOD_GSM | GSM:.UPS_MGE[1].UPS_in_backup
GSMups_polnjenje | DIGITAL | IOD_GSM | GSM:.ups_polnjenje
GSMUPS_V23_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_V23_delovanje
GSMUPS_V23_napaka | DIGITAL | IOD_GSM | GSM:.UPS_V23_napaka
GSMUPS_V25_delovanje | DIGITAL | IOD_GSM | GSM:.UPS_V25_delovanje
GSMUPS_V25_napaka | DIGITAL | IOD_GSM | GSM:.UPS_V25_napaka
GSMUPSMGEErrors10 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[10]
GSMUPSMGEErrors11 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[11]
GSMUPSMGEErrors12 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[12]
GSMUPSMGEErrors13 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[13]
GSMUPSMGEErrors14 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[14]
GSMUPSMGEErrors15 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[15]
GSMUPSMGEErrors16 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[16]
GSMUPSMGEErrors17 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[17]
GSMUPSMGEErrors1 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[1]
GSMUPSMGEErrors2 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[2]
GSMUPSMGEErrors3 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[3]
GSMUPSMGEErrors4 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[4]
GSMUPSMGEErrors5 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[5]
GSMUPSMGEErrors6 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[6]
GSMUPSMGEErrors7 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[7]
GSMUPSMGEErrors8 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[8]
GSMUPSMGEErrors9 | DIGITAL | IOD_GSM | GSM:.UPSMGEErrors[9]
GSMUserLoggedIn | DIGITAL | IOD_GSM | GSM:.UserLoggedIn
GSMVLAZILEC1_delovanje | DIGITAL | IOD_GSM | GSM:.VLAZILEC1_delovanje
GSMVLAZILEC1_napaka | DIGITAL | IOD_GSM | GSM:.VLAZILEC1_napaka
GSMVLAZILEC2_delovanje | DIGITAL | IOD_GSM | GSM:.VLAZILEC2_delovanje
GSMVLAZILEC2_napaka | DIGITAL | IOD_GSM | GSM:.VLAZILEC2_napaka
GSMXVH_AlarmOn | DIGITAL | IOD_GSM | GSM:.XVH_AlarmOn
GSMXVH_enopolna_napaka | DIGITAL | IOD_GSM | GSM:.XVH_enopolna_napaka
GSMDateTimeDan | INT | IOD_GSM | GSM:.DateTime.Dan | BYTE
GSMDateTimeLeto | INT | IOD_GSM | GSM:.DateTime.Leto | BYTE
GSMDateTimeLeto2 | INT | IOD_GSM | GSM:.DateTime.Leto2
GSMDateTimeMesec | INT | IOD_GSM | GSM:.DateTime.Mesec | BYTE
GSMDateTimeMinuta | INT | IOD_GSM | GSM:.DateTime.Minuta | BYTE
GSMDateTimePLC_Dan | INT | IOD_GSM | GSM:.DateTime.PLC_Dan | BYTE
GSMDateTimePLC_DanVTednu | INT | IOD_GSM | GSM:.DateTime.PLC_DanVTednu | BYTE
GSMDateTimePLC_Leto | INT | IOD_GSM | GSM:.DateTime.PLC_Leto | BYTE
GSMDateTimePLC_Mesec | INT | IOD_GSM | GSM:.DateTime.PLC_Mesec | BYTE
GSMDateTimePLC_Minuta | INT | IOD_GSM | GSM:.DateTime.PLC_Minuta | BYTE
GSMDateTimePLC_Sekunda | INT | IOD_GSM | GSM:.DateTime.PLC_Sekunda | BYTE
GSMDateTimePLC_Ura | INT | IOD_GSM | GSM:.DateTime.PLC_Ura | BYTE
GSMDateTimeSekunda | INT | IOD_GSM | GSM:.DateTime.Sekunda | BYTE
GSMDateTimeUra | INT | IOD_GSM | GSM:.DateTime.Ura | BYTE
GSMHIA1_vlaga_s | INT | IOD_GSM | GSM:.HIA1_vlaga_s
GSMHIA2_vlaga_s | INT | IOD_GSM | GSM:.HIA2_vlaga_s
GSMHIA3_vlaga_s | INT | IOD_GSM | GSM:.HIA3_vlaga_s
GSMHIA4_vlaga_s | INT | IOD_GSM | GSM:.HIA4_vlaga_s
GSMHIA5_vlaga_s | INT | IOD_GSM | GSM:.HIA5_vlaga_s
GSMHIA6_vlaga_s | INT | IOD_GSM | GSM:.HIA6_vlaga_s
GSMHIA7_vlaga_s | INT | IOD_GSM | GSM:.HIA7_vlaga_s
GSMKlima1Analog_izh_mesanje | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_mesanje
GSMKlima1Analog_izh_rekuperator | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_rekuperator
GSMKlima1Analog_izh_VentGrelnika | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_VentGrelnika
GSMKlima1Analog_izh_VentHlajenja | INT | IOD_GSM | GSM:.Klima[1].Analog_izh_VentHlajenja
GSMKlima1Dejanska_zel_temp | INT | IOD_GSM | GSM:.Klima[1].Dejanska_zel_temp
GSMKlima1Hitrost_del_vent_disp | INT | IOD_GSM | GSM:.Klima[1].Hitrost_del_vent_disp
GSMKlima1Max_vpih | INT | IOD_GSM | GSM:.Klima[1].Max_vpih
GSMKlima1Min_vpih | INT | IOD_GSM | GSM:.Klima[1].Min_vpih
GSMKlima1Obrat_ure_Vent_h1 | INT | IOD_GSM | GSM:.Klima[1].Obrat_ure_Vent_h1
GSMKlima1Obrat_ure_Vent_h2 | INT | IOD_GSM | GSM:.Klima[1].Obrat_ure_Vent_h2
GSMKlima1Pol_komp_konec | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_konec
GSMKlima1Pol_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_sprem_zel_vr
GSMKlima1Pol_komp_zacetek | INT | IOD_GSM | GSM:.Klima[1].Pol_komp_zacetek
GSMKlima1PreklopHitDelVent | INT | IOD_GSM | GSM:.Klima[1].PreklopHitDelVent
GSMKlima1Protizamrz_zascita | INT | IOD_GSM | GSM:.Klima[1].Protizamrz_zascita
GSMKlima1Rezim_delovanja | INT | IOD_GSM | GSM:.Klima[1].Rezim_delovanja
GSMKlima1Temperatura_dovoda | INT | IOD_GSM | GSM:.Klima[1].Temperatura_dovoda
GSMKlima1Temperatura_prostora | INT | IOD_GSM | GSM:.Klima[1].Temperatura_prostora
GSMKlima1TempPredPloscnimRekup | INT | IOD_GSM | GSM:.Klima[1].TempPredPloscnimRekup
GSMKlima1TempZaPloscnimRekup | INT | IOD_GSM | GSM:.Klima[1].TempZaPloscnimRekup
GSMKlima1Vlaga_v_prostoru | INT | IOD_GSM | GSM:.Klima[1].Vlaga_v_prostoru
GSMKlima1VlagaVstopZrakaProstor | INT | IOD_GSM | GSM:.Klima[1].VlagaVstopZrakaProstor
GSMKlima1Zel_temp_eko_gretja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_eko_gretja
GSMKlima1Zel_temp_eko_hlajenja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_eko_hlajenja
GSMKlima1Zel_temp_komf_gretja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_komf_gretja
GSMKlima1Zel_temp_komf_hlajenja | INT | IOD_GSM | GSM:.Klima[1].Zel_temp_komf_hlajenja
GSMKlima1Zim_komp_konec | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_konec
GSMKlima1Zim_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_sprem_zel_vr
GSMKlima1Zim_komp_zacetek | INT | IOD_GSM | GSM:.Klima[1].Zim_komp_zacetek
GSMKlima1ZimKompMinVpihKonec | INT | IOD_GSM | GSM:.Klima[1].ZimKompMinVpihKonec
GSMKlima1ZimKompMinVpihZac | INT | IOD_GSM | GSM:.Klima[1].ZimKompMinVpihZac
GSMKlima1ZkompMinVpihSpremZelVr | INT | IOD_GSM | GSM:.Klima[1].ZkompMinVpihSpremZelVr
GSMKlima1Zunanja_temp | INT | IOD_GSM | GSM:.Klima[1].Zunanja_temp
GSMKlima2Analog_izh_mesanje | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_mesanje
GSMKlima2Analog_izh_rekuperator | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_rekuperator
GSMKlima2Analog_izh_VentGrelnika | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_VentGrelnika
GSMKlima2Analog_izh_VentHlajenja | INT | IOD_GSM | GSM:.Klima[2].Analog_izh_VentHlajenja
GSMKlima2Dejanska_zel_temp | INT | IOD_GSM | GSM:.Klima[2].Dejanska_zel_temp
GSMKlima2Hitrost_del_vent_disp | INT | IOD_GSM | GSM:.Klima[2].Hitrost_del_vent_disp
GSMKlima2Max_vpih | INT | IOD_GSM | GSM:.Klima[2].Max_vpih
GSMKlima2Min_vpih | INT | IOD_GSM | GSM:.Klima[2].Min_vpih
GSMKlima2Obrat_ure_Vent_h1 | INT | IOD_GSM | GSM:.Klima[2].Obrat_ure_Vent_h1
GSMKlima2Obrat_ure_Vent_h2 | INT | IOD_GSM | GSM:.Klima[2].Obrat_ure_Vent_h2
GSMKlima2Pol_komp_konec | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_konec
GSMKlima2Pol_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_sprem_zel_vr
GSMKlima2Pol_komp_zacetek | INT | IOD_GSM | GSM:.Klima[2].Pol_komp_zacetek
GSMKlima2PreklopHitDelVent | INT | IOD_GSM | GSM:.Klima[2].PreklopHitDelVent
GSMKlima2Protizamrz_zascita | INT | IOD_GSM | GSM:.Klima[2].Protizamrz_zascita
GSMKlima2Rezim_delovanja | INT | IOD_GSM | GSM:.Klima[2].Rezim_delovanja
GSMKlima2Temperatura_dovoda | INT | IOD_GSM | GSM:.Klima[2].Temperatura_dovoda
GSMKlima2Temperatura_prostora | INT | IOD_GSM | GSM:.Klima[2].Temperatura_prostora
GSMKlima2TempPredPloscnimRekup | INT | IOD_GSM | GSM:.Klima[2].TempPredPloscnimRekup
GSMKlima2TempZaPloscnimRekup | INT | IOD_GSM | GSM:.Klima[2].TempZaPloscnimRekup
GSMKlima2Vlaga_v_prostoru | INT | IOD_GSM | GSM:.Klima[2].Vlaga_v_prostoru
GSMKlima2VlagaVstopZrakaProstor | INT | IOD_GSM | GSM:.Klima[2].VlagaVstopZrakaProstor
GSMKlima2Zel_temp_eko_gretja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_eko_gretja
GSMKlima2Zel_temp_eko_hlajenja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_eko_hlajenja
GSMKlima2Zel_temp_komf_gretja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_komf_gretja
GSMKlima2Zel_temp_komf_hlajenja | INT | IOD_GSM | GSM:.Klima[2].Zel_temp_komf_hlajenja
GSMKlima2Zim_komp_konec | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_konec
GSMKlima2Zim_komp_sprem_zel_vr | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_sprem_zel_vr
GSMKlima2Zim_komp_zacetek | INT | IOD_GSM | GSM:.Klima[2].Zim_komp_zacetek
GSMKlima2ZimKompMinVpihKonec | INT | IOD_GSM | GSM:.Klima[2].ZimKompMinVpihKonec
GSMKlima2ZimKompMinVpihZac | INT | IOD_GSM | GSM:.Klima[2].ZimKompMinVpihZac
GSMKlima2ZkompMinVpihSpremZelVr | INT | IOD_GSM | GSM:.Klima[2].ZkompMinVpihSpremZelVr
GSMKlima2Zunanja_temp | INT | IOD_GSM | GSM:.Klima[2].Zunanja_temp
GSMKlimaIzklopObrUre | INT | IOD_GSM | GSM:.KlimaIzklopObrUre
GSMKlime_vklopi_n | INT | IOD_GSM | GSM:.Klime_vklopi_n
GSMkom_nast_cas_izpada | INT | IOD_GSM | GSM:.kom_nast_cas_izpada
GSMPMM1AlarmPhase1GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].GlobalAlarmReg
GSMPMM1AlarmPhase2GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].GlobalAlarmReg
GSMPMM1AlarmPhase3GlobalAlarmReg | INT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].GlobalAlarmReg
GSMQ12stanje | INT | IOD_GSM | GSM:.Q12stanje | BYTE
GSMTempHistereza | INT | IOD_GSM | GSM:.TempHistereza
GSMTempPovp234 | INT | IOD_GSM | GSM:.TempPovp234
GSMTempPovp234Alarm | INT | IOD_GSM | GSM:.TempPovp234Alarm
GSMTempPovp56 | INT | IOD_GSM | GSM:.TempPovp56
GSMTempPovp56Alarm | INT | IOD_GSM | GSM:.TempPovp56Alarm
GSMTempZaVklopKlim1 | INT | IOD_GSM | GSM:.TempZaVklopKlim1
GSMTempZaVklopKlim2 | INT | IOD_GSM | GSM:.TempZaVklopKlim2
GSMTIA1_alarm | INT | IOD_GSM | GSM:.TIA1_alarm
GSMTIA1_temp_s | INT | IOD_GSM | GSM:.TIA1_temp_s
GSMTIA2_alarm | INT | IOD_GSM | GSM:.TIA2_alarm
GSMTIA2_temp_s | INT | IOD_GSM | GSM:.TIA2_temp_s
GSMTIA3_alarm | INT | IOD_GSM | GSM:.TIA3_alarm
GSMTIA3_temp_s | INT | IOD_GSM | GSM:.TIA3_temp_s
GSMTIA4_alarm | INT | IOD_GSM | GSM:.TIA4_alarm
GSMTIA4_temp_s | INT | IOD_GSM | GSM:.TIA4_temp_s
GSMTIA5_alarm | INT | IOD_GSM | GSM:.TIA5_alarm
GSMTIA5_temp_s | INT | IOD_GSM | GSM:.TIA5_temp_s
GSMTIA6_alarm | INT | IOD_GSM | GSM:.TIA6_alarm
GSMTIA6_temp_s | INT | IOD_GSM | GSM:.TIA6_temp_s
GSMTIA7_alarm | INT | IOD_GSM | GSM:.TIA7_alarm
GSMTIA7_temp_s | INT | IOD_GSM | GSM:.TIA7_temp_s
GSMUPS1InverterStatus | INT | IOD_GSM | GSM:.UPS[1].InverterStatus
GSMUPS1OutputStatus | INT | IOD_GSM | GSM:.UPS[1].OutputStatus
GSMUPS1SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[1].SteviloIzpadovVhodneLinije
GSMUPS1UnitStatus | INT | IOD_GSM | GSM:.UPS[1].UnitStatus
GSMUPS2InverterStatus | INT | IOD_GSM | GSM:.UPS[2].InverterStatus
GSMUPS2OutputStatus | INT | IOD_GSM | GSM:.UPS[2].OutputStatus
GSMUPS2SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[2].SteviloIzpadovVhodneLinije
GSMUPS2UnitStatus | INT | IOD_GSM | GSM:.UPS[2].UnitStatus
GSMUPS3InverterStatus | INT | IOD_GSM | GSM:.UPS[3].InverterStatus
GSMUPS3OutputStatus | INT | IOD_GSM | GSM:.UPS[3].OutputStatus
GSMUPS3SteviloIzpadovVhodneLinije | INT | IOD_GSM | GSM:.UPS[3].SteviloIzpadovVhodneLinije
GSMUPS3UnitStatus | INT | IOD_GSM | GSM:.UPS[3].UnitStatus
GSMUPS_MGE1BatteryBackupTime | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryBackupTime
GSMUPS_MGE1BatteryChargingLevel | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryChargingLevel
GSMUPS_MGE1BatteryRechargeDuration | INT | IOD_GSM | GSM:.UPS_MGE[1].BatteryRechargeDuration
GSMUPS_MGE1I1output | INT | IOD_GSM | GSM:.UPS_MGE[1].I1output
GSMUPS_MGE1I2output | INT | IOD_GSM | GSM:.UPS_MGE[1].I2output
GSMUPS_MGE1I3output | INT | IOD_GSM | GSM:.UPS_MGE[1].I3output
GSMUPS_MGE1InverterFrequency | INT | IOD_GSM | GSM:.UPS_MGE[1].InverterFrequency
GSMUPS_MGE1OutputActivePower1 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower1
GSMUPS_MGE1OutputActivePower2 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower2
GSMUPS_MGE1OutputActivePower3 | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputActivePower3
GSMUPS_MGE1OutputFrequency | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputFrequency
GSMUPS_MGE1OutputLoadLevel | INT | IOD_GSM | GSM:.UPS_MGE[1].OutputLoadLevel
GSMUPS_MGE1StatusBaterije | INT | IOD_GSM | GSM:.UPS_MGE[1].StatusBaterije | BYTE
GSMUPS_MGE1U12mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U12mains1
GSMUPS_MGE1U12mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U12mains2
GSMUPS_MGE1U1N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U1N_inverter
GSMUPS_MGE1U1N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U1N_output
GSMUPS_MGE1U23mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U23mains1
GSMUPS_MGE1U23mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U23mains2
GSMUPS_MGE1U2N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U2N_inverter
GSMUPS_MGE1U2N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U2N_output
GSMUPS_MGE1U31mains1 | INT | IOD_GSM | GSM:.UPS_MGE[1].U31mains1
GSMUPS_MGE1U31mains2 | INT | IOD_GSM | GSM:.UPS_MGE[1].U31mains2
GSMUPS_MGE1U3N_inverter | INT | IOD_GSM | GSM:.UPS_MGE[1].U3N_inverter
GSMUPS_MGE1U3N_output | INT | IOD_GSM | GSM:.UPS_MGE[1].U3N_output
GSMUPS_MGE1U_battery | INT | IOD_GSM | GSM:.UPS_MGE[1].U_battery
GSMUserCurrentLevel | INT | IOD_GSM | GSM:.UserCurrentLevel | BYTE
GSMMAX_SOCKET_FD_SETSIZE | LONG | IOD_GSM | GSM:.MAX_SOCKET_FD_SETSIZE
GSMCirc1CosFi_III | REAL | IOD_GSM | GSM:.Circ[1].CosFi_III
GSMCirc1DelovnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].DelovnaEnergija
GSMCirc1DelovnaEnergija_TEMP | REAL | IOD_GSM | GSM:.Circ[1].DelovnaEnergija_TEMP
GSMCirc1DelovnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_III
GSMCirc1DelovnaMoc_L1 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L1
GSMCirc1DelovnaMoc_L2 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L2
GSMCirc1DelovnaMoc_L3 | REAL | IOD_GSM | GSM:.Circ[1].DelovnaMoc_L3
GSMCirc1Frekvenca_L1 | REAL | IOD_GSM | GSM:.Circ[1].Frekvenca_L1
GSMCirc1InduktivnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].InduktivnaEnergija
GSMCirc1InduktivnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].InduktivnaMoc_III
GSMCirc1JalovaMoc_L1 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L1
GSMCirc1JalovaMoc_L2 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L2
GSMCirc1JalovaMoc_L3 | REAL | IOD_GSM | GSM:.Circ[1].JalovaMoc_L3
GSMCirc1KapacitivnaEnergija | REAL | IOD_GSM | GSM:.Circ[1].KapacitivnaEnergija
GSMCirc1KapacitivnaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].KapacitivnaMoc_III
GSMCirc1MaximumDemand | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemand
GSMCirc1MaximumDemandA2 | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemandA2
GSMCirc1MaximumDemandA3 | REAL | IOD_GSM | GSM:.Circ[1].MaximumDemandA3
GSMCirc1Napetost_L1_L2 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L1_L2
GSMCirc1Napetost_L1_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L1_N
GSMCirc1Napetost_L2_L3 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L2_L3
GSMCirc1Napetost_L2_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L2_N
GSMCirc1Napetost_L3_L1 | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L3_L1
GSMCirc1Napetost_L3_N | REAL | IOD_GSM | GSM:.Circ[1].Napetost_L3_N
GSMCirc1NavideznaMoc_III | REAL | IOD_GSM | GSM:.Circ[1].NavideznaMoc_III
GSMCirc1NicelniTok | REAL | IOD_GSM | GSM:.Circ[1].NicelniTok
GSMCirc1PowerFactor_III | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_III
GSMCirc1PowerFactor_L1 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L1
GSMCirc1PowerFactor_L2 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L2
GSMCirc1PowerFactor_L3 | REAL | IOD_GSM | GSM:.Circ[1].PowerFactor_L3
GSMCirc1RazEner_D | REAL | IOD_GSM | GSM:.Circ[1].RazEner_D
GSMCirc1RazEner_D_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_D_SCADA
GSMCirc1RazEner_D_TEMP | REAL | IOD_GSM | GSM:.Circ[1].RazEner_D_TEMP
GSMCirc1RazEner_M | REAL | IOD_GSM | GSM:.Circ[1].RazEner_M
GSMCirc1RazEner_M_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_M_SCADA
GSMCirc1RazEner_M_TEMP | REAL | IOD_GSM | GSM:.Circ[1].RazEner_M_TEMP
GSMCirc1RazEner_T | REAL | IOD_GSM | GSM:.Circ[1].RazEner_T
GSMCirc1RazEner_T_SCADA | REAL | IOD_GSM | GSM:.Circ[1].RazEner_T_SCADA
GSMCirc1RazEner_T_TEMP | REAL | IOD_GSM | GSM:.Circ[1].RazEner_T_TEMP
GSMCirc1THDI_L1 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L1
GSMCirc1THDI_L2 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L2
GSMCirc1THDI_L3 | REAL | IOD_GSM | GSM:.Circ[1].THDI_L3
GSMCirc1THDV_L1 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L1
GSMCirc1THDV_L2 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L2
GSMCirc1THDV_L3 | REAL | IOD_GSM | GSM:.Circ[1].THDV_L3
GSMCirc1Tok_L1 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L1
GSMCirc1Tok_L2 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L2
GSMCirc1Tok_L3 | REAL | IOD_GSM | GSM:.Circ[1].Tok_L3
GSMCirc1TokPovprecje_III | REAL | IOD_GSM | GSM:.Circ[1].TokPovprecje_III
GSMPMM2VirACurrent10 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[10]
GSMPMM2VirACurrent11 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[11]
GSMPMM2VirACurrent12 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[12]
GSMPMM2VirACurrent13 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[13]
GSMPMM2VirACurrent14 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[14]
GSMPMM2VirACurrent15 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[15]
GSMPMM2VirACurrent16 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[16]
GSMPMM2VirACurrent17 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[17]
GSMPMM2VirACurrent18 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[18]
GSMPMM2VirACurrent19 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[19]
GSMPMM2VirACurrent1 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[1]
GSMPMM2VirACurrent20 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[20]
GSMPMM2VirACurrent21 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[21]
GSMPMM2VirACurrent22 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[22]
GSMPMM2VirACurrent23 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[23]
GSMPMM2VirACurrent24 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[24]
GSMPMM2VirACurrent25 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[25]
GSMPMM2VirACurrent26 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[26]
GSMPMM2VirACurrent27 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[27]
GSMPMM2VirACurrent28 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[28]
GSMPMM2VirACurrent29 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[29]
GSMPMM2VirACurrent2 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[2]
GSMPMM2VirACurrent30 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[30]
GSMPMM2VirACurrent31 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[31]
GSMPMM2VirACurrent32 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[32]
GSMPMM2VirACurrent33 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[33]
GSMPMM2VirACurrent34 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[34]
GSMPMM2VirACurrent35 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[35]
GSMPMM2VirACurrent36 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[36]
GSMPMM2VirACurrent37 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[37]
GSMPMM2VirACurrent38 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[38]
GSMPMM2VirACurrent39 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[39]
GSMPMM2VirACurrent3 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[3]
GSMPMM2VirACurrent40 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[40]
GSMPMM2VirACurrent41 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[41]
GSMPMM2VirACurrent42 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[42]
GSMPMM2VirACurrent43 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[43]
GSMPMM2VirACurrent44 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[44]
GSMPMM2VirACurrent4 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[4]
GSMPMM2VirACurrent5 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[5]
GSMPMM2VirACurrent6 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[6]
GSMPMM2VirACurrent7 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[7]
GSMPMM2VirACurrent8 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[8]
GSMPMM2VirACurrent9 | REAL | IOD_GSM | GSM:.PMM2.VirA.Current[9]
GSMPMM2VirA_fsys | REAL | IOD_GSM | GSM:.PMM2.VirA_fsys
GSMPMM2VirA_Isys | REAL | IOD_GSM | GSM:.PMM2.VirA_Isys
GSMPMM2VirA_PFsys | REAL | IOD_GSM | GSM:.PMM2.VirA_PFsys
GSMPMM2VirA_Psys | REAL | IOD_GSM | GSM:.PMM2.VirA_Psys
GSMPMM2VirA_Qsys | REAL | IOD_GSM | GSM:.PMM2.VirA_Qsys
GSMPMM2VirA_Ssys | REAL | IOD_GSM | GSM:.PMM2.VirA_Ssys
GSMPMM2VirA_Usys | REAL | IOD_GSM | GSM:.PMM2.VirA_Usys
GSMPMM2VirAActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM2.VirAActiveEnergyConsumed_kWh
GSMPMM2VirAActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM2.VirAActivePowerPhaseA_kW
GSMPMM2VirAActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM2.VirAActivePowerPhaseB_kW
GSMPMM2VirAActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM2.VirAActivePowerPhaseC_kW
GSMPMM2VirAAparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM2.VirAAparentPowerPhaseA
GSMPMM2VirAAparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM2.VirAAparentPowerPhaseB
GSMPMM2VirAAparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM2.VirAAparentPowerPhaseC
GSMPMM2VirACurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM2.VirACurrentInPhaseA_A
GSMPMM2VirACurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM2.VirACurrentInPhaseB_A
GSMPMM2VirACurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM2.VirACurrentInPhaseC_A
GSMPMM2VirAReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM2.VirAReactiveEnergyConsumed_kVARh
GSMPMM2VirAReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM2.VirAReactivePowerPhaseA
GSMPMM2VirAReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM2.VirAReactivePowerPhaseB
GSMPMM2VirAReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM2.VirAReactivePowerPhaseC
GSMPMM2VirAVoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseAB_V
GSMPMM2VirAVoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseAN_V
GSMPMM2VirAVoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseBC_V
GSMPMM2VirAVoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseBN_V
GSMPMM2VirAVoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseCA_V
GSMPMM2VirAVoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM2.VirAVoltageBetweenPhaseCN_V
GSMPMM2VirBCurrent10 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[10]
GSMPMM2VirBCurrent11 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[11]
GSMPMM2VirBCurrent12 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[12]
GSMPMM2VirBCurrent13 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[13]
GSMPMM2VirBCurrent14 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[14]
GSMPMM2VirBCurrent15 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[15]
GSMPMM2VirBCurrent16 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[16]
GSMPMM2VirBCurrent17 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[17]
GSMPMM2VirBCurrent18 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[18]
GSMPMM2VirBCurrent19 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[19]
GSMPMM2VirBCurrent1 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[1]
GSMPMM2VirBCurrent20 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[20]
GSMPMM2VirBCurrent21 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[21]
GSMPMM2VirBCurrent22 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[22]
GSMPMM2VirBCurrent23 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[23]
GSMPMM2VirBCurrent24 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[24]
GSMPMM2VirBCurrent25 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[25]
GSMPMM2VirBCurrent26 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[26]
GSMPMM2VirBCurrent27 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[27]
GSMPMM2VirBCurrent28 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[28]
GSMPMM2VirBCurrent29 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[29]
GSMPMM2VirBCurrent2 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[2]
GSMPMM2VirBCurrent30 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[30]
GSMPMM2VirBCurrent31 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[31]
GSMPMM2VirBCurrent32 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[32]
GSMPMM2VirBCurrent33 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[33]
GSMPMM2VirBCurrent34 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[34]
GSMPMM2VirBCurrent35 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[35]
GSMPMM2VirBCurrent36 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[36]
GSMPMM2VirBCurrent37 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[37]
GSMPMM2VirBCurrent38 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[38]
GSMPMM2VirBCurrent39 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[39]
GSMPMM2VirBCurrent3 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[3]
GSMPMM2VirBCurrent40 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[40]
GSMPMM2VirBCurrent41 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[41]
GSMPMM2VirBCurrent42 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[42]
GSMPMM2VirBCurrent43 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[43]
GSMPMM2VirBCurrent44 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[44]
GSMPMM2VirBCurrent4 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[4]
GSMPMM2VirBCurrent5 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[5]
GSMPMM2VirBCurrent6 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[6]
GSMPMM2VirBCurrent7 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[7]
GSMPMM2VirBCurrent8 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[8]
GSMPMM2VirBCurrent9 | REAL | IOD_GSM | GSM:.PMM2.VirB.Current[9]
GSMPMM2VirB_fsys | REAL | IOD_GSM | GSM:.PMM2.VirB_fsys
GSMPMM2VirB_Isys | REAL | IOD_GSM | GSM:.PMM2.VirB_Isys
GSMPMM2VirB_PFsys | REAL | IOD_GSM | GSM:.PMM2.VirB_PFsys
GSMPMM2VirB_Psys | REAL | IOD_GSM | GSM:.PMM2.VirB_Psys
GSMPMM2VirB_Qsys | REAL | IOD_GSM | GSM:.PMM2.VirB_Qsys
GSMPMM2VirB_Ssys | REAL | IOD_GSM | GSM:.PMM2.VirB_Ssys
GSMPMM2VirB_Usys | REAL | IOD_GSM | GSM:.PMM2.VirB_Usys
GSMPMM2VirBActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM2.VirBActiveEnergyConsumed_kWh
GSMPMM2VirBActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM2.VirBActivePowerPhaseA_kW
GSMPMM2VirBActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM2.VirBActivePowerPhaseB_kW
GSMPMM2VirBActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM2.VirBActivePowerPhaseC_kW
GSMPMM2VirBAparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM2.VirBAparentPowerPhaseA
GSMPMM2VirBAparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM2.VirBAparentPowerPhaseB
GSMPMM2VirBAparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM2.VirBAparentPowerPhaseC
GSMPMM2VirBCurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM2.VirBCurrentInPhaseA_A
GSMPMM2VirBCurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM2.VirBCurrentInPhaseB_A
GSMPMM2VirBCurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM2.VirBCurrentInPhaseC_A
GSMPMM2VirBReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM2.VirBReactiveEnergyConsumed_kVARh
GSMPMM2VirBReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM2.VirBReactivePowerPhaseA
GSMPMM2VirBReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM2.VirBReactivePowerPhaseB
GSMPMM2VirBReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM2.VirBReactivePowerPhaseC
GSMPMM2VirBVoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseAB_V
GSMPMM2VirBVoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseAN_V
GSMPMM2VirBVoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseBC_V
GSMPMM2VirBVoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseBN_V
GSMPMM2VirBVoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseCA_V
GSMPMM2VirBVoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM2.VirBVoltageBetweenPhaseCN_V
GSMPMM1ActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM[1].ActiveEnergyConsumed_kWh
GSMPMM1ActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseA_kW
GSMPMM1ActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseB_kW
GSMPMM1ActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM[1].ActivePowerPhaseC_kW
GSMPMM1AparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseA
GSMPMM1AparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseB
GSMPMM1AparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].AparentPowerPhaseC
GSMPMM1AverageCurrent_A | REAL | IOD_GSM | GSM:.PMM[1].AverageCurrent_A
GSMPMM1AveragePhaseToNeutral_V | REAL | IOD_GSM | GSM:.PMM[1].AveragePhaseToNeutral_V
GSMPMM1AveragePhaseToPhase_V | REAL | IOD_GSM | GSM:.PMM[1].AveragePhaseToPhase_V
GSMPMM1CurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseA_A
GSMPMM1CurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseB_A
GSMPMM1CurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM[1].CurrentInPhaseC_A
GSMPMM1Frequency_Hz | REAL | IOD_GSM | GSM:.PMM[1].Frequency_Hz
GSMPMM1Phase1Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[10]
GSMPMM1Phase1Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[11]
GSMPMM1Phase1Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[12]
GSMPMM1Phase1Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[13]
GSMPMM1Phase1Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[14]
GSMPMM1Phase1Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[15]
GSMPMM1Phase1Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[16]
GSMPMM1Phase1Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[17]
GSMPMM1Phase1Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[18]
GSMPMM1Phase1Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[19]
GSMPMM1Phase1Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[1]
GSMPMM1Phase1Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[20]
GSMPMM1Phase1Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[21]
GSMPMM1Phase1Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[22]
GSMPMM1Phase1Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[23]
GSMPMM1Phase1Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[24]
GSMPMM1Phase1Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[25]
GSMPMM1Phase1Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[26]
GSMPMM1Phase1Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[27]
GSMPMM1Phase1Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[28]
GSMPMM1Phase1Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[29]
GSMPMM1Phase1Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[2]
GSMPMM1Phase1Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[30]
GSMPMM1Phase1Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[31]
GSMPMM1Phase1Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[32]
GSMPMM1Phase1Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[33]
GSMPMM1Phase1Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[34]
GSMPMM1Phase1Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[35]
GSMPMM1Phase1Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[36]
GSMPMM1Phase1Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[37]
GSMPMM1Phase1Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[38]
GSMPMM1Phase1Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[39]
GSMPMM1Phase1Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[3]
GSMPMM1Phase1Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[40]
GSMPMM1Phase1Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[41]
GSMPMM1Phase1Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[42]
GSMPMM1Phase1Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[4]
GSMPMM1Phase1Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[5]
GSMPMM1Phase1Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[6]
GSMPMM1Phase1Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[7]
GSMPMM1Phase1Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[8]
GSMPMM1Phase1Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[1].Current[9]
GSMPMM1Phase2Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[10]
GSMPMM1Phase2Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[11]
GSMPMM1Phase2Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[12]
GSMPMM1Phase2Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[13]
GSMPMM1Phase2Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[14]
GSMPMM1Phase2Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[15]
GSMPMM1Phase2Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[16]
GSMPMM1Phase2Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[17]
GSMPMM1Phase2Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[18]
GSMPMM1Phase2Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[19]
GSMPMM1Phase2Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[1]
GSMPMM1Phase2Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[20]
GSMPMM1Phase2Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[21]
GSMPMM1Phase2Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[22]
GSMPMM1Phase2Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[23]
GSMPMM1Phase2Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[24]
GSMPMM1Phase2Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[25]
GSMPMM1Phase2Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[26]
GSMPMM1Phase2Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[27]
GSMPMM1Phase2Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[28]
GSMPMM1Phase2Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[29]
GSMPMM1Phase2Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[2]
GSMPMM1Phase2Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[30]
GSMPMM1Phase2Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[31]
GSMPMM1Phase2Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[32]
GSMPMM1Phase2Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[33]
GSMPMM1Phase2Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[34]
GSMPMM1Phase2Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[35]
GSMPMM1Phase2Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[36]
GSMPMM1Phase2Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[37]
GSMPMM1Phase2Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[38]
GSMPMM1Phase2Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[39]
GSMPMM1Phase2Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[3]
GSMPMM1Phase2Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[40]
GSMPMM1Phase2Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[41]
GSMPMM1Phase2Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[42]
GSMPMM1Phase2Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[4]
GSMPMM1Phase2Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[5]
GSMPMM1Phase2Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[6]
GSMPMM1Phase2Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[7]
GSMPMM1Phase2Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[8]
GSMPMM1Phase2Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[2].Current[9]
GSMPMM1Phase3Current10 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[10]
GSMPMM1Phase3Current11 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[11]
GSMPMM1Phase3Current12 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[12]
GSMPMM1Phase3Current13 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[13]
GSMPMM1Phase3Current14 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[14]
GSMPMM1Phase3Current15 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[15]
GSMPMM1Phase3Current16 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[16]
GSMPMM1Phase3Current17 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[17]
GSMPMM1Phase3Current18 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[18]
GSMPMM1Phase3Current19 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[19]
GSMPMM1Phase3Current1 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[1]
GSMPMM1Phase3Current20 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[20]
GSMPMM1Phase3Current21 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[21]
GSMPMM1Phase3Current22 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[22]
GSMPMM1Phase3Current23 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[23]
GSMPMM1Phase3Current24 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[24]
GSMPMM1Phase3Current25 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[25]
GSMPMM1Phase3Current26 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[26]
GSMPMM1Phase3Current27 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[27]
GSMPMM1Phase3Current28 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[28]
GSMPMM1Phase3Current29 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[29]
GSMPMM1Phase3Current2 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[2]
GSMPMM1Phase3Current30 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[30]
GSMPMM1Phase3Current31 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[31]
GSMPMM1Phase3Current32 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[32]
GSMPMM1Phase3Current33 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[33]
GSMPMM1Phase3Current34 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[34]
GSMPMM1Phase3Current35 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[35]
GSMPMM1Phase3Current36 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[36]
GSMPMM1Phase3Current37 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[37]
GSMPMM1Phase3Current38 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[38]
GSMPMM1Phase3Current39 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[39]
GSMPMM1Phase3Current3 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[3]
GSMPMM1Phase3Current40 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[40]
GSMPMM1Phase3Current41 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[41]
GSMPMM1Phase3Current42 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[42]
GSMPMM1Phase3Current4 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[4]
GSMPMM1Phase3Current5 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[5]
GSMPMM1Phase3Current6 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[6]
GSMPMM1Phase3Current7 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[7]
GSMPMM1Phase3Current8 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[8]
GSMPMM1Phase3Current9 | REAL | IOD_GSM | GSM:.PMM[1].Phase[3].Current[9]
GSMPMM1PowerFactorSys | REAL | IOD_GSM | GSM:.PMM[1].PowerFactorSys
GSMPMM1ReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM[1].ReactiveEnergyConsumed_kVARh
GSMPMM1ReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseA
GSMPMM1ReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseB
GSMPMM1ReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].ReactivePowerPhaseC
GSMPMM1TotalActivePower_kW | REAL | IOD_GSM | GSM:.PMM[1].TotalActivePower_kW
GSMPMM1TotalAparentPower_kVA | REAL | IOD_GSM | GSM:.PMM[1].TotalAparentPower_kVA
GSMPMM1TotalPowerFactor | REAL | IOD_GSM | GSM:.PMM[1].TotalPowerFactor
GSMPMM1TotalReactivePower_kVAR | REAL | IOD_GSM | GSM:.PMM[1].TotalReactivePower_kVAR
GSMPMM1VirA_fsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_fsys
GSMPMM1VirA_Isys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Isys
GSMPMM1VirA_PFsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_PFsys
GSMPMM1VirA_Psys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Psys
GSMPMM1VirA_Qsys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Qsys
GSMPMM1VirA_Ssys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Ssys
GSMPMM1VirA_Usys | REAL | IOD_GSM | GSM:.PMM[1].VirA_Usys
GSMPMM1VirB_fsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_fsys
GSMPMM1VirB_Isys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Isys
GSMPMM1VirB_PFsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_PFsys
GSMPMM1VirB_Psys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Psys
GSMPMM1VirB_Qsys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Qsys
GSMPMM1VirB_Ssys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Ssys
GSMPMM1VirB_Usys | REAL | IOD_GSM | GSM:.PMM[1].VirB_Usys
GSMPMM1VirBActiveEnergyConsumed_kWh | REAL | IOD_GSM | GSM:.PMM[1].VirBActiveEnergyConsumed_kWh
GSMPMM1VirBActivePowerPhaseA_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseA_kW
GSMPMM1VirBActivePowerPhaseB_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseB_kW
GSMPMM1VirBActivePowerPhaseC_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBActivePowerPhaseC_kW
GSMPMM1VirBAparentPowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseA
GSMPMM1VirBAparentPowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseB
GSMPMM1VirBAparentPowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].VirBAparentPowerPhaseC
GSMPMM1VirBAverageCurrent_A | REAL | IOD_GSM | GSM:.PMM[1].VirBAverageCurrent_A
GSMPMM1VirBAveragePhaseToNeutral_V | REAL | IOD_GSM | GSM:.PMM[1].VirBAveragePhaseToNeutral_V
GSMPMM1VirBAveragePhaseToPhase_V | REAL | IOD_GSM | GSM:.PMM[1].VirBAveragePhaseToPhase_V
GSMPMM1VirBCurrentInPhaseA_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseA_A
GSMPMM1VirBCurrentInPhaseB_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseB_A
GSMPMM1VirBCurrentInPhaseC_A | REAL | IOD_GSM | GSM:.PMM[1].VirBCurrentInPhaseC_A
GSMPMM1VirBFrequency_Hz | REAL | IOD_GSM | GSM:.PMM[1].VirBFrequency_Hz
GSMPMM1VirBPowerFactorSys | REAL | IOD_GSM | GSM:.PMM[1].VirBPowerFactorSys
GSMPMM1VirBReactiveEnergyConsumed_kVARh | REAL | IOD_GSM | GSM:.PMM[1].VirBReactiveEnergyConsumed_kVARh
GSMPMM1VirBReactivePowerPhaseA | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseA
GSMPMM1VirBReactivePowerPhaseB | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseB
GSMPMM1VirBReactivePowerPhaseC | REAL | IOD_GSM | GSM:.PMM[1].VirBReactivePowerPhaseC
GSMPMM1VirBTotalActivePower_kW | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalActivePower_kW
GSMPMM1VirBTotalAparentPower_kVA | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalAparentPower_kVA
GSMPMM1VirBTotalPowerFactor | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalPowerFactor
GSMPMM1VirBTotalReactivePower_kVAR | REAL | IOD_GSM | GSM:.PMM[1].VirBTotalReactivePower_kVAR
GSMPMM1VirBVoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseAB_V
GSMPMM1VirBVoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseAN_V
GSMPMM1VirBVoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseBC_V
GSMPMM1VirBVoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseBN_V
GSMPMM1VirBVoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseCA_V
GSMPMM1VirBVoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM[1].VirBVoltageBetweenPhaseCN_V
GSMPMM1VoltageBetweenPhaseAB_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseAB_V
GSMPMM1VoltageBetweenPhaseAN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseAN_V
GSMPMM1VoltageBetweenPhaseBC_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseBC_V
GSMPMM1VoltageBetweenPhaseBN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseBN_V
GSMPMM1VoltageBetweenPhaseCA_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseCA_V
GSMPMM1VoltageBetweenPhaseCN_V | REAL | IOD_GSM | GSM:.PMM[1].VoltageBetweenPhaseCN_V
GSMPMMfaza01 | REAL | IOD_GSM | GSM:.PMMfaza01
GSMPMMfaza02 | REAL | IOD_GSM | GSM:.PMMfaza02
GSMPMMfaza03 | REAL | IOD_GSM | GSM:.PMMfaza03
GSMPMMfaza04 | REAL | IOD_GSM | GSM:.PMMfaza04
GSMPMMfaza05 | REAL | IOD_GSM | GSM:.PMMfaza05
GSMPMMfaza06 | REAL | IOD_GSM | GSM:.PMMfaza06
GSMPMMfaza07 | REAL | IOD_GSM | GSM:.PMMfaza07
GSMPMMfaza08 | REAL | IOD_GSM | GSM:.PMMfaza08
GSMPMMfaza09 | REAL | IOD_GSM | GSM:.PMMfaza09
GSMPMMfaza10 | REAL | IOD_GSM | GSM:.PMMfaza10
GSMPMMfaza11 | REAL | IOD_GSM | GSM:.PMMfaza11
GSMPMMfaza12 | REAL | IOD_GSM | GSM:.PMMfaza12
GSMPMMfaza13 | REAL | IOD_GSM | GSM:.PMMfaza13
GSMPMMfaza14 | REAL | IOD_GSM | GSM:.PMMfaza14
GSMPMMfaza15 | REAL | IOD_GSM | GSM:.PMMfaza15
GSMPMMfaza16 | REAL | IOD_GSM | GSM:.PMMfaza16
GSMPMMfaza17 | REAL | IOD_GSM | GSM:.PMMfaza17
GSMPMMfaza18 | REAL | IOD_GSM | GSM:.PMMfaza18
GSMPMMfaza19 | REAL | IOD_GSM | GSM:.PMMfaza19
GSMPMMfaza20 | REAL | IOD_GSM | GSM:.PMMfaza20
GSMPMMfaza21 | REAL | IOD_GSM | GSM:.PMMfaza21
GSMPMMfaza22 | REAL | IOD_GSM | GSM:.PMMfaza22
GSMPMMfaza23 | REAL | IOD_GSM | GSM:.PMMfaza23
GSMPMMfaza24 | REAL | IOD_GSM | GSM:.PMMfaza24
GSMPMMfaza25 | REAL | IOD_GSM | GSM:.PMMfaza25
GSMPMMfaza26 | REAL | IOD_GSM | GSM:.PMMfaza26
GSMPMMfaza27 | REAL | IOD_GSM | GSM:.PMMfaza27
GSMPMMfaza28 | REAL | IOD_GSM | GSM:.PMMfaza28
GSMPMMfaza29 | REAL | IOD_GSM | GSM:.PMMfaza29
GSMPMMfaza30 | REAL | IOD_GSM | GSM:.PMMfaza30
GSMPMMfaza31 | REAL | IOD_GSM | GSM:.PMMfaza31
GSMPMMfaza32 | REAL | IOD_GSM | GSM:.PMMfaza32
GSMPMMfaza33 | REAL | IOD_GSM | GSM:.PMMfaza33
GSMPMMfaza34 | REAL | IOD_GSM | GSM:.PMMfaza34
GSMPMMfaza35 | REAL | IOD_GSM | GSM:.PMMfaza35
GSMPMMfaza36 | REAL | IOD_GSM | GSM:.PMMfaza36
GSMPMMfaza37 | REAL | IOD_GSM | GSM:.PMMfaza37
GSMPMMfaza38 | REAL | IOD_GSM | GSM:.PMMfaza38
GSMPMMfaza39 | REAL | IOD_GSM | GSM:.PMMfaza39
GSMPMMfaza40 | REAL | IOD_GSM | GSM:.PMMfaza40
GSMPMMfaza41 | REAL | IOD_GSM | GSM:.PMMfaza41
GSMPMMfaza42 | REAL | IOD_GSM | GSM:.PMMfaza42
GSMPMMskupniTokA | REAL | IOD_GSM | GSM:.PMMskupniTokA
GSMPMMskupniTokB | REAL | IOD_GSM | GSM:.PMMskupniTokB
GSMUPS1EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[1].EstimatedChargeRemaining
GSMUPS1EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[1].EstimatedMinutesRemaining
GSMUPS1IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL1
GSMUPS1IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL2
GSMUPS1IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[1].IzhodMocL3
GSMUPS1NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[1].NapetostBaterije
GSMUPS1TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[1].TemperaturaBaterije
GSMUPS1VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL1
GSMUPS1VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL2
GSMUPS1VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[1].VhodFrekvencaL3
GSMUPS1VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL1
GSMUPS1VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL2
GSMUPS1VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[1].VhodNapetostL3
GSMUPS2EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[2].EstimatedChargeRemaining
GSMUPS2EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[2].EstimatedMinutesRemaining
GSMUPS2IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL1
GSMUPS2IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL2
GSMUPS2IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[2].IzhodMocL3
GSMUPS2NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[2].NapetostBaterije
GSMUPS2TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[2].TemperaturaBaterije
GSMUPS2VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL1
GSMUPS2VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL2
GSMUPS2VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[2].VhodFrekvencaL3
GSMUPS2VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL1
GSMUPS2VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL2
GSMUPS2VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[2].VhodNapetostL3
GSMUPS3EstimatedChargeRemaining | REAL | IOD_GSM | GSM:.UPS[3].EstimatedChargeRemaining
GSMUPS3EstimatedMinutesRemaining | REAL | IOD_GSM | GSM:.UPS[3].EstimatedMinutesRemaining
GSMUPS3IzhodMocL1 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL1
GSMUPS3IzhodMocL2 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL2
GSMUPS3IzhodMocL3 | REAL | IOD_GSM | GSM:.UPS[3].IzhodMocL3
GSMUPS3NapetostBaterije | REAL | IOD_GSM | GSM:.UPS[3].NapetostBaterije
GSMUPS3TemperaturaBaterije | REAL | IOD_GSM | GSM:.UPS[3].TemperaturaBaterije
GSMUPS3VhodFrekvencaL1 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL1
GSMUPS3VhodFrekvencaL2 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL2
GSMUPS3VhodFrekvencaL3 | REAL | IOD_GSM | GSM:.UPS[3].VhodFrekvencaL3
GSMUPS3VhodNapetostL1 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL1
GSMUPS3VhodNapetostL2 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL2
GSMUPS3VhodNapetostL3 | REAL | IOD_GSM | GSM:.UPS[3].VhodNapetostL3
GSMcas_modbus_izpad | STRING | IOD_GSM | GSM:.cas_modbus_izpad
GSMDate_Time0 | STRING | IOD_GSM | GSM:.Date_Time[0]
GSMDate_Time1 | STRING | IOD_GSM | GSM:.Date_Time[1]
GSMDate_Time2 | STRING | IOD_GSM | GSM:.Date_Time[2]
GSMDate_Time3 | STRING | IOD_GSM | GSM:.Date_Time[3]
GSMK1obrat_ure | STRING | IOD_GSM | GSM:.K1obrat_ure
GSMUserCurrentName | STRING | IOD_GSM | GSM:.UserCurrentName
GSMUserDisplay | STRING | IOD_GSM | GSM:.UserDisplay
GSMK1_obr_u_skupno | UINT | IOD_GSM | GSM:.K1_obr_u_skupno
GSMK2_obr_u_skupno | UINT | IOD_GSM | GSM:.K2_obr_u_skupno
GSMPMM2VirAAlarmPhaseC01_16_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C01_16_60to80
GSMPMM2VirAAlarmPhaseC01_16_over80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C01_16_over80
GSMPMM2VirAAlarmPhaseC17_32_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C17_32_60to80
GSMPMM2VirAAlarmPhaseC17_32_over80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C17_32_over80
GSMPMM2VirAAlarmPhaseC33_44_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C33_44_60to80
GSMPMM2VirAAlarmPhaseC33_44_over80 | UINT | IOD_GSM | GSM:.PMM2.VirAAlarmPhase.C33_44_over80
GSMPMM2VirBAlarmPhaseC01_16_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C01_16_60to80
GSMPMM2VirBAlarmPhaseC01_16_over80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C01_16_over80
GSMPMM2VirBAlarmPhaseC17_32_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C17_32_60to80
GSMPMM2VirBAlarmPhaseC17_32_over80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C17_32_over80
GSMPMM2VirBAlarmPhaseC33_44_60to80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C33_44_60to80
GSMPMM2VirBAlarmPhaseC33_44_over80 | UINT | IOD_GSM | GSM:.PMM2.VirBAlarmPhase.C33_44_over80
GSMPMM1AlarmPhase1C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C01_16_60to80
GSMPMM1AlarmPhase1C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C01_16_over80
GSMPMM1AlarmPhase1C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C17_32_60to80
GSMPMM1AlarmPhase1C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C17_32_over80
GSMPMM1AlarmPhase1C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C33_42_60to80
GSMPMM1AlarmPhase1C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[1].C33_42_over80
GSMPMM1AlarmPhase2C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C01_16_60to80
GSMPMM1AlarmPhase2C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C01_16_over80
GSMPMM1AlarmPhase2C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C17_32_60to80
GSMPMM1AlarmPhase2C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C17_32_over80
GSMPMM1AlarmPhase2C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C33_42_60to80
GSMPMM1AlarmPhase2C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[2].C33_42_over80
GSMPMM1AlarmPhase3C01_16_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C01_16_60to80
GSMPMM1AlarmPhase3C01_16_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C01_16_over80
GSMPMM1AlarmPhase3C17_32_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C17_32_60to80
GSMPMM1AlarmPhase3C17_32_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C17_32_over80
GSMPMM1AlarmPhase3C33_42_60to80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C33_42_60to80
GSMPMM1AlarmPhase3C33_42_over80 | UINT | IOD_GSM | GSM:.PMM[1].AlarmPhase[3].C33_42_over80
GSMUPS1_StatusBaterije | UINT | IOD_GSM | GSM:.UPS1_StatusBaterije
GSMUPS2_StatusBaterije | UINT | IOD_GSM | GSM:.UPS2_StatusBaterije
GSMUPS3_StatusBaterije | UINT | IOD_GSM | GSM:.UPS3_StatusBaterije
GSMUPS1StatusBaterije | UINT | IOD_GSM | GSM:.UPS[1].StatusBaterije
GSMUPS2StatusBaterije | UINT | IOD_GSM | GSM:.UPS[2].StatusBaterije
GSMUPS3StatusBaterije | UINT | IOD_GSM | GSM:.UPS[3].StatusBaterije

## variable_3
GSMAGR_Gasenje_alarm | DIGITAL | IOD_GSM_TCP | 1 | 00001 | AGR_Gasenje_alarm
GSMAGR_PozCent_napaka | DIGITAL | IOD_GSM_TCP | 2 | 00002 | AGR_PozCent_napaka
GSMAGR_PozSenzor_okvara | DIGITAL | IOD_GSM_TCP | 3 | 00003 | AGR_PozSenzor_okvara
GSMAlarmGenUPS_A_V23 | DIGITAL | IOD_GSM_TCP | 4 | 00004 | AlarmGenUPS_A_V23
GSMAlarmGenUPS_V23 | DIGITAL | IOD_GSM_TCP | 5 | 00005 | AlarmGenUPS_V23
GSMAlarmGenUPS_V25 | DIGITAL | IOD_GSM_TCP | 6 | 00006 | AlarmGenUPS_V25
GSMAlarmPMM1VirATokPrevisok | DIGITAL | IOD_GSM_TCP | 7 | 00007 | AlarmPMM1VirATokPrevisok
GSMAlarmPMM1VirATokVisok | DIGITAL | IOD_GSM_TCP | 8 | 00008 | AlarmPMM1VirATokVisok
GSMAlarmPMM1VirBTokPrevisok | DIGITAL | IOD_GSM_TCP | 9 | 00009 | AlarmPMM1VirBTokPrevisok
GSMAlarmPMM1VirBTokVisok | DIGITAL | IOD_GSM_TCP | 10 | 00010 | AlarmPMM1VirBTokVisok
GSMAlarmPMM2x17nad8010 | DIGITAL | IOD_GSM_TCP | 11 | 00011 | AlarmPMM2x17nad80[10]
GSMAlarmPMM2x17nad8011 | DIGITAL | IOD_GSM_TCP | 12 | 00012 | AlarmPMM2x17nad80[11]
GSMAlarmPMM2x17nad8012 | DIGITAL | IOD_GSM_TCP | 13 | 00013 | AlarmPMM2x17nad80[12]
GSMAlarmPMM2x17nad8013 | DIGITAL | IOD_GSM_TCP | 14 | 00014 | AlarmPMM2x17nad80[13]
GSMAlarmPMM2x17nad8014 | DIGITAL | IOD_GSM_TCP | 15 | 00015 | AlarmPMM2x17nad80[14]
GSMAlarmPMM2x17nad8015 | DIGITAL | IOD_GSM_TCP | 16 | 00016 | AlarmPMM2x17nad80[15]
GSMAlarmPMM2x17nad8016 | DIGITAL | IOD_GSM_TCP | 17 | 00017 | AlarmPMM2x17nad80[16]
GSMAlarmPMM2x17nad8017 | DIGITAL | IOD_GSM_TCP | 18 | 00018 | AlarmPMM2x17nad80[17]
GSMAlarmPMM2x17nad8018 | DIGITAL | IOD_GSM_TCP | 19 | 00019 | AlarmPMM2x17nad80[18]
GSMAlarmPMM2x17nad8019 | DIGITAL | IOD_GSM_TCP | 20 | 00020 | AlarmPMM2x17nad80[19]
GSMAlarmPMM2x17nad801 | DIGITAL | IOD_GSM_TCP | 21 | 00021 | AlarmPMM2x17nad80[1]
GSMAlarmPMM2x17nad8020 | DIGITAL | IOD_GSM_TCP | 22 | 00022 | AlarmPMM2x17nad80[20]
GSMAlarmPMM2x17nad8021 | DIGITAL | IOD_GSM_TCP | 23 | 00023 | AlarmPMM2x17nad80[21]
GSMAlarmPMM2x17nad8022 | DIGITAL | IOD_GSM_TCP | 24 | 00024 | AlarmPMM2x17nad80[22]
GSMAlarmPMM2x17nad8023 | DIGITAL | IOD_GSM_TCP | 25 | 00025 | AlarmPMM2x17nad80[23]
GSMAlarmPMM2x17nad8024 | DIGITAL | IOD_GSM_TCP | 26 | 00026 | AlarmPMM2x17nad80[24]
GSMAlarmPMM2x17nad8025 | DIGITAL | IOD_GSM_TCP | 27 | 00027 | AlarmPMM2x17nad80[25]
GSMAlarmPMM2x17nad8026 | DIGITAL | IOD_GSM_TCP | 28 | 00028 | AlarmPMM2x17nad80[26]
GSMAlarmPMM2x17nad8027 | DIGITAL | IOD_GSM_TCP | 29 | 00029 | AlarmPMM2x17nad80[27]
GSMAlarmPMM2x17nad8028 | DIGITAL | IOD_GSM_TCP | 30 | 00030 | AlarmPMM2x17nad80[28]
GSMAlarmPMM2x17nad8029 | DIGITAL | IOD_GSM_TCP | 31 | 00031 | AlarmPMM2x17nad80[29]
GSMAlarmPMM2x17nad802 | DIGITAL | IOD_GSM_TCP | 32 | 00032 | AlarmPMM2x17nad80[2]
GSMAlarmPMM2x17nad8030 | DIGITAL | IOD_GSM_TCP | 33 | 00033 | AlarmPMM2x17nad80[30]
GSMAlarmPMM2x17nad8031 | DIGITAL | IOD_GSM_TCP | 34 | 00034 | AlarmPMM2x17nad80[31]
GSMAlarmPMM2x17nad8032 | DIGITAL | IOD_GSM_TCP | 35 | 00035 | AlarmPMM2x17nad80[32]
GSMAlarmPMM2x17nad8033 | DIGITAL | IOD_GSM_TCP | 36 | 00036 | AlarmPMM2x17nad80[33]
GSMAlarmPMM2x17nad8034 | DIGITAL | IOD_GSM_TCP | 37 | 00037 | AlarmPMM2x17nad80[34]
GSMAlarmPMM2x17nad8035 | DIGITAL | IOD_GSM_TCP | 38 | 00038 | AlarmPMM2x17nad80[35]
GSMAlarmPMM2x17nad8036 | DIGITAL | IOD_GSM_TCP | 39 | 00039 | AlarmPMM2x17nad80[36]
GSMAlarmPMM2x17nad8037 | DIGITAL | IOD_GSM_TCP | 40 | 00040 | AlarmPMM2x17nad80[37]
GSMAlarmPMM2x17nad8038 | DIGITAL | IOD_GSM_TCP | 41 | 00041 | AlarmPMM2x17nad80[38]
GSMAlarmPMM2x17nad8039 | DIGITAL | IOD_GSM_TCP | 42 | 00042 | AlarmPMM2x17nad80[39]
GSMAlarmPMM2x17nad803 | DIGITAL | IOD_GSM_TCP | 43 | 00043 | AlarmPMM2x17nad80[3]
GSMAlarmPMM2x17nad8040 | DIGITAL | IOD_GSM_TCP | 44 | 00044 | AlarmPMM2x17nad80[40]
GSMAlarmPMM2x17nad8041 | DIGITAL | IOD_GSM_TCP | 45 | 00045 | AlarmPMM2x17nad80[41]
GSMAlarmPMM2x17nad8042 | DIGITAL | IOD_GSM_TCP | 46 | 00046 | AlarmPMM2x17nad80[42]
GSMAlarmPMM2x17nad804 | DIGITAL | IOD_GSM_TCP | 47 | 00047 | AlarmPMM2x17nad80[4]
GSMAlarmPMM2x17nad805 | DIGITAL | IOD_GSM_TCP | 48 | 00048 | AlarmPMM2x17nad80[5]
GSMAlarmPMM2x17nad806 | DIGITAL | IOD_GSM_TCP | 49 | 00049 | AlarmPMM2x17nad80[6]
GSMAlarmPMM2x17nad807 | DIGITAL | IOD_GSM_TCP | 50 | 00050 | AlarmPMM2x17nad80[7]
GSMAlarmPMM2x17nad808 | DIGITAL | IOD_GSM_TCP | 51 | 00051 | AlarmPMM2x17nad80[8]
GSMAlarmPMM2x17nad809 | DIGITAL | IOD_GSM_TCP | 52 | 00052 | AlarmPMM2x17nad80[9]
GSMALM_AGR_Gasenje_alarm | DIGITAL | IOD_GSM_TCP | 53 | 00053 | ALM_AGR_Gasenje_alarm
GSMALM_AGR_PozCent_napaka | DIGITAL | IOD_GSM_TCP | 54 | 00054 | ALM_AGR_PozCent_napaka
GSMALM_AGR_PozSenzor_okvara | DIGITAL | IOD_GSM_TCP | 55 | 00055 | ALM_AGR_PozSenzor_okvara
GSMALM_GSM_Gasenje_alarm | DIGITAL | IOD_GSM_TCP | 56 | 00056 | ALM_GSM_Gasenje_alarm
GSMALM_GSM_PozCent_napaka | DIGITAL | IOD_GSM_TCP | 57 | 00057 | ALM_GSM_PozCent_napaka
GSMALM_GSM_PozSenzor_okvara | DIGITAL | IOD_GSM_TCP | 58 | 00058 | ALM_GSM_PozSenzor_okvara
GSMCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_GSM_TCP | 59 | 00059 | Circ_Vpis_Dnevne_energija_scada1
GSMCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_GSM_TCP | 60 | 00060 | Circ_Vpis_Dnevne_energija_scada2
GSMCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_GSM_TCP | 61 | 00061 | Circ_Vpis_Mesecna_energija_scada1
GSMCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_GSM_TCP | 62 | 00062 | Circ_Vpis_Mesecna_energija_scada2
GSMCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_GSM_TCP | 63 | 00063 | Circ_Vpis_Tedenska_energija_scada1
GSMCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_GSM_TCP | 64 | 00064 | Circ_Vpis_Tedenska_energija_scada2
GSMComError | DIGITAL | IOD_GSM_TCP | 65 | 00065 | ComError
GSMComSCADA | DIGITAL | IOD_GSM_TCP | 66 | 00066 | ComSCADA
GSMComSCADA1 | DIGITAL | IOD_GSM_TCP | 67 | 00067 | ComSCADA1
GSMComSCADA2 | DIGITAL | IOD_GSM_TCP | 68 | 00068 | ComSCADA2
GSMComSCADA3 | DIGITAL | IOD_GSM_TCP | 69 | 00069 | ComSCADA3
GSMDI1_I11 | DIGITAL | IOD_GSM_TCP | 70 | 00070 | DI1_I11
GSMDI1_I9 | DIGITAL | IOD_GSM_TCP | 71 | 00071 | DI1_I9
GSMDI2_I14 | DIGITAL | IOD_GSM_TCP | 72 | 00072 | DI2_I14
GSMDI2_I15 | DIGITAL | IOD_GSM_TCP | 73 | 00073 | DI2_I15
GSMDI_R3KC_A_Q21_IzkljucenIzpad | DIGITAL | IOD_GSM_TCP | 74 | 00074 | DI_R3KC_A_Q21_IzkljucenIzpad
GSMDI_R3KC_A_Q22_IzkljucenIzpad | DIGITAL | IOD_GSM_TCP | 75 | 00075 | DI_R3KC_A_Q22_IzkljucenIzpad
GSMDI_SBi_RAZS_AA_Izolacija_NOT_OK | DIGITAL | IOD_GSM_TCP | 76 | 00076 | DI_SBi_RAZS_AA_Izolacija_NOT_OK
GSMDI_SBi_RAZS_AB_Izolacija_NOT_OK | DIGITAL | IOD_GSM_TCP | 77 | 00077 | DI_SBi_RAZS_AB_Izolacija_NOT_OK
GSMErrComCirc1 | DIGITAL | IOD_GSM_TCP | 78 | 00078 | ErrComCirc[1]
GSMErrComKlima1 | DIGITAL | IOD_GSM_TCP | 79 | 00079 | ErrComKlima[1]
GSMErrComKlima2 | DIGITAL | IOD_GSM_TCP | 80 | 00080 | ErrComKlima[2]
GSMErrComPMM1 | DIGITAL | IOD_GSM_TCP | 81 | 00081 | ErrComPMM[1]
GSMErrComPMM2 | DIGITAL | IOD_GSM_TCP | 82 | 00082 | ErrComPMM[2]
GSMErrComPort2 | DIGITAL | IOD_GSM_TCP | 83 | 00083 | ErrComPort2
GSMErrComPort3 | DIGITAL | IOD_GSM_TCP | 84 | 00084 | ErrComPort3
GSMErrComPort4 | DIGITAL | IOD_GSM_TCP | 85 | 00085 | ErrComPort4
GSMErrComUPS1 | DIGITAL | IOD_GSM_TCP | 86 | 00086 | ErrComUPS[1]
GSMErrComUPS2 | DIGITAL | IOD_GSM_TCP | 87 | 00087 | ErrComUPS[2]
GSMErrComUPS3 | DIGITAL | IOD_GSM_TCP | 88 | 00088 | ErrComUPS[3]
GSMErrComUPSMGE1 | DIGITAL | IOD_GSM_TCP | 89 | 00089 | ErrComUPSMGE[1]
GSMF1_1_zascita_ok | DIGITAL | IOD_GSM_TCP | 90 | 00090 | F1_1_zascita_ok
GSMGSM_Gasenje_alarm | DIGITAL | IOD_GSM_TCP | 91 | 00091 | GSM_Gasenje_alarm
GSMGSM_PozCent_napaka | DIGITAL | IOD_GSM_TCP | 92 | 00092 | GSM_PozCent_napaka
GSMGSM_PozSenzor_okvara | DIGITAL | IOD_GSM_TCP | 93 | 00093 | GSM_PozSenzor_okvara
GSMK1_SkupnaNapaka | DIGITAL | IOD_GSM_TCP | 94 | 00094 | K1_SkupnaNapaka
GSMK1_vklop_izklop_poteka | DIGITAL | IOD_GSM_TCP | 95 | 00095 | K1_vklop_izklop_poteka
GSMK1AlarmPozara | DIGITAL | IOD_GSM_TCP | 96 | 00096 | K1AlarmPozara
GSMK1KlimaZdruzenAlarm | DIGITAL | IOD_GSM_TCP | 97 | 00097 | K1KlimaZdruzenAlarm
GSMK1NiPretoka | DIGITAL | IOD_GSM_TCP | 98 | 00098 | K1NiPretoka
GSMK1OkvaraRototerma | DIGITAL | IOD_GSM_TCP | 99 | 00099 | K1OkvaraRototerma
GSMK1OkvaraVlazNap | DIGITAL | IOD_GSM_TCP | 100 | 00100 | K1OkvaraVlazNap
GSMK1PreobMotCrpGr | DIGITAL | IOD_GSM_TCP | 101 | 00101 | K1PreobMotCrpGr
GSMK1PreobMotVent | DIGITAL | IOD_GSM_TCP | 102 | 00102 | K1PreobMotVent
GSMK1ProtizamrzZascAkt | DIGITAL | IOD_GSM_TCP | 103 | 00103 | K1ProtizamrzZascAkt
GSMK1ZamasenostFiltra | DIGITAL | IOD_GSM_TCP | 104 | 00104 | K1ZamasenostFiltra
GSMK2_SkupnaNapaka | DIGITAL | IOD_GSM_TCP | 105 | 00105 | K2_SkupnaNapaka
GSMK2_vklop_izklop_poteka | DIGITAL | IOD_GSM_TCP | 106 | 00106 | K2_vklop_izklop_poteka
GSMK2AlarmPozara | DIGITAL | IOD_GSM_TCP | 107 | 00107 | K2AlarmPozara
GSMK2KlimaZdruzenAlarm | DIGITAL | IOD_GSM_TCP | 108 | 00108 | K2KlimaZdruzenAlarm
GSMK2NiPretoka | DIGITAL | IOD_GSM_TCP | 109 | 00109 | K2NiPretoka
GSMK2OkvaraRototerma | DIGITAL | IOD_GSM_TCP | 110 | 00110 | K2OkvaraRototerma
GSMK2OkvaraVlazNap | DIGITAL | IOD_GSM_TCP | 111 | 00111 | K2OkvaraVlazNap
GSMK2PreobMotCrpGr | DIGITAL | IOD_GSM_TCP | 112 | 00112 | K2PreobMotCrpGr
GSMK2PreobMotVent | DIGITAL | IOD_GSM_TCP | 113 | 00113 | K2PreobMotVent
GSMK2ProtizamrzZascAkt | DIGITAL | IOD_GSM_TCP | 114 | 00114 | K2ProtizamrzZascAkt
GSMK2ZamasenostFiltra | DIGITAL | IOD_GSM_TCP | 115 | 00115 | K2ZamasenostFiltra
GSMK3_deluje | DIGITAL | IOD_GSM_TCP | 116 | 00116 | K3_deluje
GSMK3_SkupnaNapaka | DIGITAL | IOD_GSM_TCP | 117 | 00117 | K3_SkupnaNapaka
GSMKlima1_izkljucena | DIGITAL | IOD_GSM_TCP | 118 | 00118 | Klima1_izkljucena
GSMKLIMA1_kke_pogon | DIGITAL | IOD_GSM_TCP | 119 | 00119 | KLIMA1_kke_pogon
GSMKLIMA1_krm_nap_ok | DIGITAL | IOD_GSM_TCP | 120 | 00120 | KLIMA1_krm_nap_ok
GSMKlima2_izkljucena | DIGITAL | IOD_GSM_TCP | 121 | 00121 | Klima2_izkljucena
GSMKlima3_izkljucena | DIGITAL | IOD_GSM_TCP | 122 | 00122 | Klima3_izkljucena
GSMKlima1Alarm_pozar | DIGITAL | IOD_GSM_TCP | 123 | 00123 | Klima[1].Alarm_pozar
GSMKlima1DelVentHit1 | DIGITAL | IOD_GSM_TCP | 124 | 00124 | Klima[1].DelVentHit1
GSMKlima1DelVentHit2 | DIGITAL | IOD_GSM_TCP | 125 | 00125 | Klima[1].DelVentHit2
GSMKlima1Ni_pretoka | DIGITAL | IOD_GSM_TCP | 126 | 00126 | Klima[1].Ni_pretoka
GSMKlima1OkvaraRototerm | DIGITAL | IOD_GSM_TCP | 127 | 00127 | Klima[1].OkvaraRototerm
GSMKlima1OkvaraVlazNap | DIGITAL | IOD_GSM_TCP | 128 | 00128 | Klima[1].OkvaraVlazNap
GSMKlima1PreobMotCrpGrel | DIGITAL | IOD_GSM_TCP | 129 | 00129 | Klima[1].PreobMotCrpGrel
GSMKlima1PreobMotVent | DIGITAL | IOD_GSM_TCP | 130 | 00130 | Klima[1].PreobMotVent
GSMKlima1ProtizamrzZascAktivna | DIGITAL | IOD_GSM_TCP | 131 | 00131 | Klima[1].ProtizamrzZascAktivna
GSMKlima1VklopRegKlimata | DIGITAL | IOD_GSM_TCP | 132 | 00132 | Klima[1].VklopRegKlimata
GSMKlima1ZamasenostFiltra | DIGITAL | IOD_GSM_TCP | 133 | 00133 | Klima[1].ZamasenostFiltra
GSMKlima1ZdruzAlarmA | DIGITAL | IOD_GSM_TCP | 134 | 00134 | Klima[1].ZdruzAlarmA
GSMKlima1ZdruzAlarmB | DIGITAL | IOD_GSM_TCP | 135 | 00135 | Klima[1].ZdruzAlarmB
GSMKlima2Alarm_pozar | DIGITAL | IOD_GSM_TCP | 136 | 00136 | Klima[2].Alarm_pozar
GSMKlima2DelVentHit1 | DIGITAL | IOD_GSM_TCP | 137 | 00137 | Klima[2].DelVentHit1
GSMKlima2DelVentHit2 | DIGITAL | IOD_GSM_TCP | 138 | 00138 | Klima[2].DelVentHit2
GSMKlima2Ni_pretoka | DIGITAL | IOD_GSM_TCP | 139 | 00139 | Klima[2].Ni_pretoka
GSMKlima2OkvaraRototerm | DIGITAL | IOD_GSM_TCP | 140 | 00140 | Klima[2].OkvaraRototerm
GSMKlima2OkvaraVlazNap | DIGITAL | IOD_GSM_TCP | 141 | 00141 | Klima[2].OkvaraVlazNap
GSMKlima2PreobMotCrpGrel | DIGITAL | IOD_GSM_TCP | 142 | 00142 | Klima[2].PreobMotCrpGrel
GSMKlima2PreobMotVent | DIGITAL | IOD_GSM_TCP | 143 | 00143 | Klima[2].PreobMotVent
GSMKlima2ProtizamrzZascAktivna | DIGITAL | IOD_GSM_TCP | 144 | 00144 | Klima[2].ProtizamrzZascAktivna
GSMKlima2VklopRegKlimata | DIGITAL | IOD_GSM_TCP | 145 | 00145 | Klima[2].VklopRegKlimata
GSMKlima2ZamasenostFiltra | DIGITAL | IOD_GSM_TCP | 146 | 00146 | Klima[2].ZamasenostFiltra
GSMKlima2ZdruzAlarmA | DIGITAL | IOD_GSM_TCP | 147 | 00147 | Klima[2].ZdruzAlarmA
GSMKlima2ZdruzAlarmB | DIGITAL | IOD_GSM_TCP | 148 | 00148 | Klima[2].ZdruzAlarmB
GSMKLIMA_m1_delovanje | DIGITAL | IOD_GSM_TCP | 149 | 00149 | KLIMA_m1_delovanje
GSMKLIMA_m1_napaka | DIGITAL | IOD_GSM_TCP | 150 | 00150 | KLIMA_m1_napaka
GSMKLIMA_m2_delovanje | DIGITAL | IOD_GSM_TCP | 151 | 00151 | KLIMA_m2_delovanje
GSMKLIMA_m2_napaka | DIGITAL | IOD_GSM_TCP | 152 | 00152 | KLIMA_m2_napaka
GSMKLIMAT1_delovanje | DIGITAL | IOD_GSM_TCP | 153 | 00153 | KLIMAT1_delovanje
GSMKLIMAT1_napaka | DIGITAL | IOD_GSM_TCP | 154 | 00154 | KLIMAT1_napaka
GSMKLIMAT1_R_zakleni | DIGITAL | IOD_GSM_TCP | 155 | 00155 | KLIMAT1_R_zakleni
GSMKLIMAT1_vklop_delovanja | DIGITAL | IOD_GSM_TCP | 156 | 00156 | KLIMAT1_vklop_delovanja
GSMKLIMAT1_vklop_delovanjaR | DIGITAL | IOD_GSM_TCP | 157 | 00157 | KLIMAT1_vklop_delovanjaR
GSMKLIMAT2_delovanje | DIGITAL | IOD_GSM_TCP | 158 | 00158 | KLIMAT2_delovanje
GSMKLIMAT2_napaka | DIGITAL | IOD_GSM_TCP | 159 | 00159 | KLIMAT2_napaka
GSMKLIMAT2_R_zakleni | DIGITAL | IOD_GSM_TCP | 160 | 00160 | KLIMAT2_R_zakleni
GSMKLIMAT2_vklop_delovanja | DIGITAL | IOD_GSM_TCP | 161 | 00161 | KLIMAT2_vklop_delovanja
GSMKLIMAT2_vklop_delovanjaR | DIGITAL | IOD_GSM_TCP | 162 | 00162 | KLIMAT2_vklop_delovanjaR
GSMKlimeAVTO | DIGITAL | IOD_GSM_TCP | 163 | 00163 | KlimeAVTO
GSMN_F1_1_zascita_ok | DIGITAL | IOD_GSM_TCP | 164 | 00164 | N_F1_1_zascita_ok
GSMN_KLIMA1_krm_nap_ok | DIGITAL | IOD_GSM_TCP | 165 | 00165 | N_KLIMA1_krm_nap_ok
GSMN_KLIMAT1_napaka | DIGITAL | IOD_GSM_TCP | 166 | 00166 | N_KLIMAT1_napaka
GSMN_KLIMAT2_napaka | DIGITAL | IOD_GSM_TCP | 167 | 00167 | N_KLIMAT2_napaka
GSMN_KlimeAVTO | DIGITAL | IOD_GSM_TCP | 168 | 00168 | N_KlimeAVTO
GSMN_Q12_izpad | DIGITAL | IOD_GSM_TCP | 169 | 00169 | N_Q12_izpad
GSMN_UPS_A_V23_delovanje | DIGITAL | IOD_GSM_TCP | 170 | 00170 | N_UPS_A_V23_delovanje
GSMN_UPS_A_V23_napaka | DIGITAL | IOD_GSM_TCP | 171 | 00171 | N_UPS_A_V23_napaka
GSMN_UPS_V23_delovanje | DIGITAL | IOD_GSM_TCP | 172 | 00172 | N_UPS_V23_delovanje
GSMN_UPS_V23_napaka | DIGITAL | IOD_GSM_TCP | 173 | 00173 | N_UPS_V23_napaka
GSMN_UPS_V25_delovanje | DIGITAL | IOD_GSM_TCP | 174 | 00174 | N_UPS_V25_delovanje
GSMN_UPS_V25_napaka | DIGITAL | IOD_GSM_TCP | 175 | 00175 | N_UPS_V25_napaka
GSMN_VLAZILEC1_napaka | DIGITAL | IOD_GSM_TCP | 176 | 00176 | N_VLAZILEC1_napaka
GSMN_VLAZILEC2_napaka | DIGITAL | IOD_GSM_TCP | 177 | 00177 | N_VLAZILEC2_napaka
GSMnapaka_kom_panel | DIGITAL | IOD_GSM_TCP | 178 | 00178 | napaka_kom_panel
GSMnapaka_kom_scada | DIGITAL | IOD_GSM_TCP | 179 | 00179 | napaka_kom_scada
GSMnapaka_kom_scada2 | DIGITAL | IOD_GSM_TCP | 180 | 00180 | napaka_kom_scada2
GSMNapakaSenzorSkupno | DIGITAL | IOD_GSM_TCP | 181 | 00181 | NapakaSenzorSkupno
GSMNapakaSenzorVlagaHIA1 | DIGITAL | IOD_GSM_TCP | 182 | 00182 | NapakaSenzorVlagaHIA1
GSMNapakaSenzorVlagaHIA2 | DIGITAL | IOD_GSM_TCP | 183 | 00183 | NapakaSenzorVlagaHIA2
GSMNapakaSenzorVlagaHIA3 | DIGITAL | IOD_GSM_TCP | 184 | 00184 | NapakaSenzorVlagaHIA3
GSMNapakaSenzorVlagaHIA4 | DIGITAL | IOD_GSM_TCP | 185 | 00185 | NapakaSenzorVlagaHIA4
GSMNapakaSenzorVlagaHIA5 | DIGITAL | IOD_GSM_TCP | 186 | 00186 | NapakaSenzorVlagaHIA5
GSMNapakaSenzorVlagaHIA6 | DIGITAL | IOD_GSM_TCP | 187 | 00187 | NapakaSenzorVlagaHIA6
GSMNapakaSenzorVlagaHIA7 | DIGITAL | IOD_GSM_TCP | 188 | 00188 | NapakaSenzorVlagaHIA7
GSMNapakaTSTempTIA1 | DIGITAL | IOD_GSM_TCP | 189 | 00189 | NapakaTSTempTIA1
GSMNapakaTSTempTIA2 | DIGITAL | IOD_GSM_TCP | 190 | 00190 | NapakaTSTempTIA2
GSMNapakaTSTempTIA3 | DIGITAL | IOD_GSM_TCP | 191 | 00191 | NapakaTSTempTIA3
GSMNapakaTSTempTIA4 | DIGITAL | IOD_GSM_TCP | 192 | 00192 | NapakaTSTempTIA4
GSMNapakaTSTempTIA5 | DIGITAL | IOD_GSM_TCP | 193 | 00193 | NapakaTSTempTIA5
GSMNapakaTSTempTIA6 | DIGITAL | IOD_GSM_TCP | 194 | 00194 | NapakaTSTempTIA6
GSMNapakaTSTempTIA7 | DIGITAL | IOD_GSM_TCP | 195 | 00195 | NapakaTSTempTIA7
GSMOpozoriloPMM2x17med60in8010 | DIGITAL | IOD_GSM_TCP | 196 | 00196 | OpozoriloPMM2x17med60in80[10]
GSMOpozoriloPMM2x17med60in8011 | DIGITAL | IOD_GSM_TCP | 197 | 00197 | OpozoriloPMM2x17med60in80[11]
GSMOpozoriloPMM2x17med60in8012 | DIGITAL | IOD_GSM_TCP | 198 | 00198 | OpozoriloPMM2x17med60in80[12]
GSMOpozoriloPMM2x17med60in8013 | DIGITAL | IOD_GSM_TCP | 199 | 00199 | OpozoriloPMM2x17med60in80[13]
GSMOpozoriloPMM2x17med60in8014 | DIGITAL | IOD_GSM_TCP | 200 | 00200 | OpozoriloPMM2x17med60in80[14]
GSMOpozoriloPMM2x17med60in8015 | DIGITAL | IOD_GSM_TCP | 201 | 00201 | OpozoriloPMM2x17med60in80[15]
GSMOpozoriloPMM2x17med60in8016 | DIGITAL | IOD_GSM_TCP | 202 | 00202 | OpozoriloPMM2x17med60in80[16]
GSMOpozoriloPMM2x17med60in8017 | DIGITAL | IOD_GSM_TCP | 203 | 00203 | OpozoriloPMM2x17med60in80[17]
GSMOpozoriloPMM2x17med60in8018 | DIGITAL | IOD_GSM_TCP | 204 | 00204 | OpozoriloPMM2x17med60in80[18]
GSMOpozoriloPMM2x17med60in8019 | DIGITAL | IOD_GSM_TCP | 205 | 00205 | OpozoriloPMM2x17med60in80[19]
GSMOpozoriloPMM2x17med60in801 | DIGITAL | IOD_GSM_TCP | 206 | 00206 | OpozoriloPMM2x17med60in80[1]
GSMOpozoriloPMM2x17med60in8020 | DIGITAL | IOD_GSM_TCP | 207 | 00207 | OpozoriloPMM2x17med60in80[20]
GSMOpozoriloPMM2x17med60in8021 | DIGITAL | IOD_GSM_TCP | 208 | 00208 | OpozoriloPMM2x17med60in80[21]
GSMOpozoriloPMM2x17med60in8022 | DIGITAL | IOD_GSM_TCP | 209 | 00209 | OpozoriloPMM2x17med60in80[22]
GSMOpozoriloPMM2x17med60in8023 | DIGITAL | IOD_GSM_TCP | 210 | 00210 | OpozoriloPMM2x17med60in80[23]
GSMOpozoriloPMM2x17med60in8024 | DIGITAL | IOD_GSM_TCP | 211 | 00211 | OpozoriloPMM2x17med60in80[24]
GSMOpozoriloPMM2x17med60in8025 | DIGITAL | IOD_GSM_TCP | 212 | 00212 | OpozoriloPMM2x17med60in80[25]
GSMOpozoriloPMM2x17med60in8026 | DIGITAL | IOD_GSM_TCP | 213 | 00213 | OpozoriloPMM2x17med60in80[26]
GSMOpozoriloPMM2x17med60in8027 | DIGITAL | IOD_GSM_TCP | 214 | 00214 | OpozoriloPMM2x17med60in80[27]
GSMOpozoriloPMM2x17med60in8028 | DIGITAL | IOD_GSM_TCP | 215 | 00215 | OpozoriloPMM2x17med60in80[28]
GSMOpozoriloPMM2x17med60in8029 | DIGITAL | IOD_GSM_TCP | 216 | 00216 | OpozoriloPMM2x17med60in80[29]
GSMOpozoriloPMM2x17med60in802 | DIGITAL | IOD_GSM_TCP | 217 | 00217 | OpozoriloPMM2x17med60in80[2]
GSMOpozoriloPMM2x17med60in8030 | DIGITAL | IOD_GSM_TCP | 218 | 00218 | OpozoriloPMM2x17med60in80[30]
GSMOpozoriloPMM2x17med60in8031 | DIGITAL | IOD_GSM_TCP | 219 | 00219 | OpozoriloPMM2x17med60in80[31]
GSMOpozoriloPMM2x17med60in8032 | DIGITAL | IOD_GSM_TCP | 220 | 00220 | OpozoriloPMM2x17med60in80[32]
GSMOpozoriloPMM2x17med60in8033 | DIGITAL | IOD_GSM_TCP | 221 | 00221 | OpozoriloPMM2x17med60in80[33]
GSMOpozoriloPMM2x17med60in8034 | DIGITAL | IOD_GSM_TCP | 222 | 00222 | OpozoriloPMM2x17med60in80[34]
GSMOpozoriloPMM2x17med60in8035 | DIGITAL | IOD_GSM_TCP | 223 | 00223 | OpozoriloPMM2x17med60in80[35]
GSMOpozoriloPMM2x17med60in8036 | DIGITAL | IOD_GSM_TCP | 224 | 00224 | OpozoriloPMM2x17med60in80[36]
GSMOpozoriloPMM2x17med60in8037 | DIGITAL | IOD_GSM_TCP | 225 | 00225 | OpozoriloPMM2x17med60in80[37]
GSMOpozoriloPMM2x17med60in8038 | DIGITAL | IOD_GSM_TCP | 226 | 00226 | OpozoriloPMM2x17med60in80[38]
GSMOpozoriloPMM2x17med60in8039 | DIGITAL | IOD_GSM_TCP | 227 | 00227 | OpozoriloPMM2x17med60in80[39]
GSMOpozoriloPMM2x17med60in803 | DIGITAL | IOD_GSM_TCP | 228 | 00228 | OpozoriloPMM2x17med60in80[3]
GSMOpozoriloPMM2x17med60in8040 | DIGITAL | IOD_GSM_TCP | 229 | 00229 | OpozoriloPMM2x17med60in80[40]
GSMOpozoriloPMM2x17med60in8041 | DIGITAL | IOD_GSM_TCP | 230 | 00230 | OpozoriloPMM2x17med60in80[41]
GSMOpozoriloPMM2x17med60in8042 | DIGITAL | IOD_GSM_TCP | 231 | 00231 | OpozoriloPMM2x17med60in80[42]
GSMOpozoriloPMM2x17med60in804 | DIGITAL | IOD_GSM_TCP | 232 | 00232 | OpozoriloPMM2x17med60in80[4]
GSMOpozoriloPMM2x17med60in805 | DIGITAL | IOD_GSM_TCP | 233 | 00233 | OpozoriloPMM2x17med60in80[5]
GSMOpozoriloPMM2x17med60in806 | DIGITAL | IOD_GSM_TCP | 234 | 00234 | OpozoriloPMM2x17med60in80[6]
GSMOpozoriloPMM2x17med60in807 | DIGITAL | IOD_GSM_TCP | 235 | 00235 | OpozoriloPMM2x17med60in80[7]
GSMOpozoriloPMM2x17med60in808 | DIGITAL | IOD_GSM_TCP | 236 | 00236 | OpozoriloPMM2x17med60in80[8]
GSMOpozoriloPMM2x17med60in809 | DIGITAL | IOD_GSM_TCP | 237 | 00237 | OpozoriloPMM2x17med60in80[9]
GSMPMM1OverCurrentBetw1 | DIGITAL | IOD_GSM_TCP | 238 | 00238 | PMM1OverCurrentBetw[1]
GSMPMM1OverCurrentBetw2 | DIGITAL | IOD_GSM_TCP | 239 | 00239 | PMM1OverCurrentBetw[2]
GSMPMM1OverCurrentBetw3 | DIGITAL | IOD_GSM_TCP | 240 | 00240 | PMM1OverCurrentBetw[3]
GSMPMM1OverCurrentOver1 | DIGITAL | IOD_GSM_TCP | 241 | 00241 | PMM1OverCurrentOver[1]
GSMPMM1OverCurrentOver2 | DIGITAL | IOD_GSM_TCP | 242 | 00242 | PMM1OverCurrentOver[2]
GSMPMM1OverCurrentOver3 | DIGITAL | IOD_GSM_TCP | 243 | 00243 | PMM1OverCurrentOver[3]
GSMPMM2QA1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_GSM_TCP | 244 | 00244 | PMM2.QA1_GlStik_IZKLOP_IZPAD
GSMPMM2QB1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_GSM_TCP | 245 | 00245 | PMM2.QB1_GlStik_IZKLOP_IZPAD
GSMPMM2SkNapaka_med60in80 | DIGITAL | IOD_GSM_TCP | 246 | 00246 | PMM2.SkNapaka_med60in80
GSMPMM2SkNapaka_nad80 | DIGITAL | IOD_GSM_TCP | 247 | 00247 | PMM2.SkNapaka_nad80
GSMPMM2SkNapakaVirA_med60in80 | DIGITAL | IOD_GSM_TCP | 248 | 00248 | PMM2.SkNapakaVirA_med60in80
GSMPMM2SkNapakaVirA_nad80 | DIGITAL | IOD_GSM_TCP | 249 | 00249 | PMM2.SkNapakaVirA_nad80
GSMPMM2SkNapakaVirB_med60in80 | DIGITAL | IOD_GSM_TCP | 250 | 00250 | PMM2.SkNapakaVirB_med60in80
GSMPMM2SkNapakaVirB_nad80 | DIGITAL | IOD_GSM_TCP | 251 | 00251 | PMM2.SkNapakaVirB_nad80
GSMPMM2VirA_NapakaOzemljitve | DIGITAL | IOD_GSM_TCP | 252 | 00252 | PMM2.VirA_NapakaOzemljitve
GSMPMM2VirB_NapakaOzemljitve | DIGITAL | IOD_GSM_TCP | 253 | 00253 | PMM2.VirB_NapakaOzemljitve
GSMPozarnaCentrala_skupno | DIGITAL | IOD_GSM_TCP | 254 | 00254 | PozarnaCentrala_skupno
GSMPrevisokaTemp | DIGITAL | IOD_GSM_TCP | 255 | 00255 | PrevisokaTemp
GSMQ0_izkljuceno | DIGITAL | IOD_GSM_TCP | 256 | 00256 | Q0_izkljuceno
GSMQ0_vkljuceno | DIGITAL | IOD_GSM_TCP | 257 | 00257 | Q0_vkljuceno
GSMQ12_izkljuceno | DIGITAL | IOD_GSM_TCP | 258 | 00258 | Q12_izkljuceno
GSMQ12_izpad | DIGITAL | IOD_GSM_TCP | 259 | 00259 | Q12_izpad
GSMQ12_vkljuceno | DIGITAL | IOD_GSM_TCP | 260 | 00260 | Q12_vkljuceno
GSMQ21_vkljuceno | DIGITAL | IOD_GSM_TCP | 261 | 00261 | Q21_vkljuceno
GSMQ22_vkljuceno | DIGITAL | IOD_GSM_TCP | 262 | 00262 | Q22_vkljuceno
GSMrazlitjeLAH1 | DIGITAL | IOD_GSM_TCP | 263 | 00263 | razlitjeLAH1
GSMrazlitjeLAH2 | DIGITAL | IOD_GSM_TCP | 264 | 00264 | razlitjeLAH2
GSMrazlitjeLAH3 | DIGITAL | IOD_GSM_TCP | 265 | 00265 | razlitjeLAH3
GSMrazlitjeLAH4 | DIGITAL | IOD_GSM_TCP | 266 | 00266 | razlitjeLAH4
GSMSetDateTime | DIGITAL | IOD_GSM_TCP | 267 | 00267 | SetDateTime
GSMSetDateTimeDemand | DIGITAL | IOD_GSM_TCP | 268 | 00268 | SetDateTimeDemand
GSMSetDateTimeError | DIGITAL | IOD_GSM_TCP | 269 | 00269 | SetDateTimeError
GSMSetDateTimeFinished | DIGITAL | IOD_GSM_TCP | 270 | 00270 | SetDateTimeFinished
GSMSkupneNapakeNaprav_PMM17VirBVirA | DIGITAL | IOD_GSM_TCP | 271 | 00271 | SkupneNapakeNaprav_PMM17VirBVirA
GSMSlabaBaterijaPLC | DIGITAL | IOD_GSM_TCP | 272 | 00272 | SlabaBaterijaPLC
GSMTempPovp234Previs | DIGITAL | IOD_GSM_TCP | 273 | 00273 | TempPovp234Previs
GSMTempPovp56Previs | DIGITAL | IOD_GSM_TCP | 274 | 00274 | TempPovp56Previs
GSMTIA1_previs_temp | DIGITAL | IOD_GSM_TCP | 275 | 00275 | TIA1_previs_temp
GSMTIA2_previs_temp | DIGITAL | IOD_GSM_TCP | 276 | 00276 | TIA2_previs_temp
GSMTIA3_previs_temp | DIGITAL | IOD_GSM_TCP | 277 | 00277 | TIA3_previs_temp
GSMTIA4_previs_temp | DIGITAL | IOD_GSM_TCP | 278 | 00278 | TIA4_previs_temp
GSMTIA5_previs_temp | DIGITAL | IOD_GSM_TCP | 279 | 00279 | TIA5_previs_temp
GSMTIA6_previs_temp | DIGITAL | IOD_GSM_TCP | 280 | 00280 | TIA6_previs_temp
GSMTIA7_previs_temp | DIGITAL | IOD_GSM_TCP | 281 | 00281 | TIA7_previs_temp
GSMUPS1Errors10 | DIGITAL | IOD_GSM_TCP | 282 | 00282 | UPS1Errors[10]
GSMUPS1Errors11 | DIGITAL | IOD_GSM_TCP | 283 | 00283 | UPS1Errors[11]
GSMUPS1Errors12 | DIGITAL | IOD_GSM_TCP | 284 | 00284 | UPS1Errors[12]
GSMUPS1Errors13 | DIGITAL | IOD_GSM_TCP | 285 | 00285 | UPS1Errors[13]
GSMUPS1Errors14 | DIGITAL | IOD_GSM_TCP | 286 | 00286 | UPS1Errors[14]
GSMUPS1Errors15 | DIGITAL | IOD_GSM_TCP | 287 | 00287 | UPS1Errors[15]
GSMUPS1Errors16 | DIGITAL | IOD_GSM_TCP | 288 | 00288 | UPS1Errors[16]
GSMUPS1Errors17 | DIGITAL | IOD_GSM_TCP | 289 | 00289 | UPS1Errors[17]
GSMUPS1Errors18 | DIGITAL | IOD_GSM_TCP | 290 | 00290 | UPS1Errors[18]
GSMUPS1Errors19 | DIGITAL | IOD_GSM_TCP | 291 | 00291 | UPS1Errors[19]
GSMUPS1Errors1 | DIGITAL | IOD_GSM_TCP | 292 | 00292 | UPS1Errors[1]
GSMUPS1Errors20 | DIGITAL | IOD_GSM_TCP | 293 | 00293 | UPS1Errors[20]
GSMUPS1Errors21 | DIGITAL | IOD_GSM_TCP | 294 | 00294 | UPS1Errors[21]
GSMUPS1Errors22 | DIGITAL | IOD_GSM_TCP | 295 | 00295 | UPS1Errors[22]
GSMUPS1Errors23 | DIGITAL | IOD_GSM_TCP | 296 | 00296 | UPS1Errors[23]
GSMUPS1Errors24 | DIGITAL | IOD_GSM_TCP | 297 | 00297 | UPS1Errors[24]
GSMUPS1Errors25 | DIGITAL | IOD_GSM_TCP | 298 | 00298 | UPS1Errors[25]
GSMUPS1Errors2 | DIGITAL | IOD_GSM_TCP | 299 | 00299 | UPS1Errors[2]
GSMUPS1Errors3 | DIGITAL | IOD_GSM_TCP | 300 | 00300 | UPS1Errors[3]
GSMUPS1Errors4 | DIGITAL | IOD_GSM_TCP | 301 | 00301 | UPS1Errors[4]
GSMUPS1Errors5 | DIGITAL | IOD_GSM_TCP | 302 | 00302 | UPS1Errors[5]
GSMUPS1Errors6 | DIGITAL | IOD_GSM_TCP | 303 | 00303 | UPS1Errors[6]
GSMUPS1Errors7 | DIGITAL | IOD_GSM_TCP | 304 | 00304 | UPS1Errors[7]
GSMUPS1Errors8 | DIGITAL | IOD_GSM_TCP | 305 | 00305 | UPS1Errors[8]
GSMUPS1Errors9 | DIGITAL | IOD_GSM_TCP | 306 | 00306 | UPS1Errors[9]
GSMUPS2Errors10 | DIGITAL | IOD_GSM_TCP | 307 | 00307 | UPS2Errors[10]
GSMUPS2Errors11 | DIGITAL | IOD_GSM_TCP | 308 | 00308 | UPS2Errors[11]
GSMUPS2Errors12 | DIGITAL | IOD_GSM_TCP | 309 | 00309 | UPS2Errors[12]
GSMUPS2Errors13 | DIGITAL | IOD_GSM_TCP | 310 | 00310 | UPS2Errors[13]
GSMUPS2Errors14 | DIGITAL | IOD_GSM_TCP | 311 | 00311 | UPS2Errors[14]
GSMUPS2Errors15 | DIGITAL | IOD_GSM_TCP | 312 | 00312 | UPS2Errors[15]
GSMUPS2Errors16 | DIGITAL | IOD_GSM_TCP | 313 | 00313 | UPS2Errors[16]
GSMUPS2Errors17 | DIGITAL | IOD_GSM_TCP | 314 | 00314 | UPS2Errors[17]
GSMUPS2Errors18 | DIGITAL | IOD_GSM_TCP | 315 | 00315 | UPS2Errors[18]
GSMUPS2Errors19 | DIGITAL | IOD_GSM_TCP | 316 | 00316 | UPS2Errors[19]
GSMUPS2Errors1 | DIGITAL | IOD_GSM_TCP | 317 | 00317 | UPS2Errors[1]
GSMUPS2Errors20 | DIGITAL | IOD_GSM_TCP | 318 | 00318 | UPS2Errors[20]
GSMUPS2Errors21 | DIGITAL | IOD_GSM_TCP | 319 | 00319 | UPS2Errors[21]
GSMUPS2Errors22 | DIGITAL | IOD_GSM_TCP | 320 | 00320 | UPS2Errors[22]
GSMUPS2Errors23 | DIGITAL | IOD_GSM_TCP | 321 | 00321 | UPS2Errors[23]
GSMUPS2Errors24 | DIGITAL | IOD_GSM_TCP | 322 | 00322 | UPS2Errors[24]
GSMUPS2Errors25 | DIGITAL | IOD_GSM_TCP | 323 | 00323 | UPS2Errors[25]
GSMUPS2Errors2 | DIGITAL | IOD_GSM_TCP | 324 | 00324 | UPS2Errors[2]
GSMUPS2Errors3 | DIGITAL | IOD_GSM_TCP | 325 | 00325 | UPS2Errors[3]
GSMUPS2Errors4 | DIGITAL | IOD_GSM_TCP | 326 | 00326 | UPS2Errors[4]
GSMUPS2Errors5 | DIGITAL | IOD_GSM_TCP | 327 | 00327 | UPS2Errors[5]
GSMUPS2Errors6 | DIGITAL | IOD_GSM_TCP | 328 | 00328 | UPS2Errors[6]
GSMUPS2Errors7 | DIGITAL | IOD_GSM_TCP | 329 | 00329 | UPS2Errors[7]
GSMUPS2Errors8 | DIGITAL | IOD_GSM_TCP | 330 | 00330 | UPS2Errors[8]
GSMUPS2Errors9 | DIGITAL | IOD_GSM_TCP | 331 | 00331 | UPS2Errors[9]
GSMUPS3Errors10 | DIGITAL | IOD_GSM_TCP | 332 | 00332 | UPS3Errors[10]
GSMUPS3Errors11 | DIGITAL | IOD_GSM_TCP | 333 | 00333 | UPS3Errors[11]
GSMUPS3Errors12 | DIGITAL | IOD_GSM_TCP | 334 | 00334 | UPS3Errors[12]
GSMUPS3Errors13 | DIGITAL | IOD_GSM_TCP | 335 | 00335 | UPS3Errors[13]
GSMUPS3Errors14 | DIGITAL | IOD_GSM_TCP | 336 | 00336 | UPS3Errors[14]
GSMUPS3Errors15 | DIGITAL | IOD_GSM_TCP | 337 | 00337 | UPS3Errors[15]
GSMUPS3Errors16 | DIGITAL | IOD_GSM_TCP | 338 | 00338 | UPS3Errors[16]
GSMUPS3Errors17 | DIGITAL | IOD_GSM_TCP | 339 | 00339 | UPS3Errors[17]
GSMUPS3Errors18 | DIGITAL | IOD_GSM_TCP | 340 | 00340 | UPS3Errors[18]
GSMUPS3Errors19 | DIGITAL | IOD_GSM_TCP | 341 | 00341 | UPS3Errors[19]
GSMUPS3Errors1 | DIGITAL | IOD_GSM_TCP | 342 | 00342 | UPS3Errors[1]
GSMUPS3Errors20 | DIGITAL | IOD_GSM_TCP | 343 | 00343 | UPS3Errors[20]
GSMUPS3Errors21 | DIGITAL | IOD_GSM_TCP | 344 | 00344 | UPS3Errors[21]
GSMUPS3Errors22 | DIGITAL | IOD_GSM_TCP | 345 | 00345 | UPS3Errors[22]
GSMUPS3Errors23 | DIGITAL | IOD_GSM_TCP | 346 | 00346 | UPS3Errors[23]
GSMUPS3Errors24 | DIGITAL | IOD_GSM_TCP | 347 | 00347 | UPS3Errors[24]
GSMUPS3Errors25 | DIGITAL | IOD_GSM_TCP | 348 | 00348 | UPS3Errors[25]
GSMUPS3Errors2 | DIGITAL | IOD_GSM_TCP | 349 | 00349 | UPS3Errors[2]
GSMUPS3Errors3 | DIGITAL | IOD_GSM_TCP | 350 | 00350 | UPS3Errors[3]
GSMUPS3Errors4 | DIGITAL | IOD_GSM_TCP | 351 | 00351 | UPS3Errors[4]
GSMUPS3Errors5 | DIGITAL | IOD_GSM_TCP | 352 | 00352 | UPS3Errors[5]
GSMUPS3Errors6 | DIGITAL | IOD_GSM_TCP | 353 | 00353 | UPS3Errors[6]
GSMUPS3Errors7 | DIGITAL | IOD_GSM_TCP | 354 | 00354 | UPS3Errors[7]
GSMUPS3Errors8 | DIGITAL | IOD_GSM_TCP | 355 | 00355 | UPS3Errors[8]
GSMUPS3Errors9 | DIGITAL | IOD_GSM_TCP | 356 | 00356 | UPS3Errors[9]
GSMUPS1AlarmAwaitingPower | DIGITAL | IOD_GSM_TCP | 357 | 00357 | UPS[1].AlarmAwaitingPower
GSMUPS1AlarmBypassBad | DIGITAL | IOD_GSM_TCP | 358 | 00358 | UPS[1].AlarmBypassBad
GSMUPS1AlarmChargerFailed | DIGITAL | IOD_GSM_TCP | 359 | 00359 | UPS[1].AlarmChargerFailed
GSMUPS1AlarmCommunicationsLost | DIGITAL | IOD_GSM_TCP | 360 | 00360 | UPS[1].AlarmCommunicationsLost
GSMUPS1AlarmDepletedBattery | DIGITAL | IOD_GSM_TCP | 361 | 00361 | UPS[1].AlarmDepletedBattery
GSMUPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM_TCP | 362 | 00362 | UPS[1].AlarmDiagnosticTestFailed
GSMUPS1AlarmInverterError | DIGITAL | IOD_GSM_TCP | 363 | 00363 | UPS[1].AlarmInverterError
GSMUPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 364 | 00364 | UPS[1].AlarmIzhodOffKotZahtevano
GSMUPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM_TCP | 365 | 00365 | UPS[1].AlarmIzhodPreobremenjen
GSMUPS1AlarmLowBattery | DIGITAL | IOD_GSM_TCP | 366 | 00366 | UPS[1].AlarmLowBattery
GSMUPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM_TCP | 367 | 00367 | UPS[1].AlarmNapakaNaVarovalki
GSMUPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM_TCP | 368 | 00368 | UPS[1].AlarmNapakaNaVentilatorju
GSMUPS1AlarmOnBattery | DIGITAL | IOD_GSM_TCP | 369 | 00369 | UPS[1].AlarmOnBattery
GSMUPS1AlarmOnBypass | DIGITAL | IOD_GSM_TCP | 370 | 00370 | UPS[1].AlarmOnBypass
GSMUPS1AlarmShutdownImminent | DIGITAL | IOD_GSM_TCP | 371 | 00371 | UPS[1].AlarmShutdownImminent
GSMUPS1AlarmShutdownPending | DIGITAL | IOD_GSM_TCP | 372 | 00372 | UPS[1].AlarmShutdownPending
GSMUPS1AlarmSlabaBaterija | DIGITAL | IOD_GSM_TCP | 373 | 00373 | UPS[1].AlarmSlabaBaterija
GSMUPS1AlarmSplosnaNapaka | DIGITAL | IOD_GSM_TCP | 374 | 00374 | UPS[1].AlarmSplosnaNapaka
GSMUPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 375 | 00375 | UPS[1].AlarmStanjeIzhodaIzvenToleranc
GSMUPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 376 | 00376 | UPS[1].AlarmStanjeVhodaIzvenToleranc
GSMUPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 377 | 00377 | UPS[1].AlarmTemperaturaIzvenToleranc
GSMUPS1AlarmTestInProgres | DIGITAL | IOD_GSM_TCP | 378 | 00378 | UPS[1].AlarmTestInProgres
GSMUPS1AlarmUPSIzhodOff | DIGITAL | IOD_GSM_TCP | 379 | 00379 | UPS[1].AlarmUPSIzhodOff
GSMUPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 380 | 00380 | UPS[1].AlarmUPSOffKotZahtevano
GSMUPS1AlarmUPSSystemOff | DIGITAL | IOD_GSM_TCP | 381 | 00381 | UPS[1].AlarmUPSSystemOff
GSMUPS1Napaka | DIGITAL | IOD_GSM_TCP | 382 | 00382 | UPS[1].Napaka
GSMUPS1StatusEcomodeAktiven | DIGITAL | IOD_GSM_TCP | 383 | 00383 | UPS[1].StatusEcomodeAktiven
GSMUPS1StatusInverterIsOn | DIGITAL | IOD_GSM_TCP | 384 | 00384 | UPS[1].StatusInverterIsOn
GSMUPS1StatusStopOperation | DIGITAL | IOD_GSM_TCP | 385 | 00385 | UPS[1].StatusStopOperation
GSMUPS2AlarmAwaitingPower | DIGITAL | IOD_GSM_TCP | 386 | 00386 | UPS[2].AlarmAwaitingPower
GSMUPS2AlarmBypassBad | DIGITAL | IOD_GSM_TCP | 387 | 00387 | UPS[2].AlarmBypassBad
GSMUPS2AlarmChargerFailed | DIGITAL | IOD_GSM_TCP | 388 | 00388 | UPS[2].AlarmChargerFailed
GSMUPS2AlarmCommunicationsLost | DIGITAL | IOD_GSM_TCP | 389 | 00389 | UPS[2].AlarmCommunicationsLost
GSMUPS2AlarmDepletedBattery | DIGITAL | IOD_GSM_TCP | 390 | 00390 | UPS[2].AlarmDepletedBattery
GSMUPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM_TCP | 391 | 00391 | UPS[2].AlarmDiagnosticTestFailed
GSMUPS2AlarmInverterError | DIGITAL | IOD_GSM_TCP | 392 | 00392 | UPS[2].AlarmInverterError
GSMUPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 393 | 00393 | UPS[2].AlarmIzhodOffKotZahtevano
GSMUPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM_TCP | 394 | 00394 | UPS[2].AlarmIzhodPreobremenjen
GSMUPS2AlarmLowBattery | DIGITAL | IOD_GSM_TCP | 395 | 00395 | UPS[2].AlarmLowBattery
GSMUPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM_TCP | 396 | 00396 | UPS[2].AlarmNapakaNaVarovalki
GSMUPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM_TCP | 397 | 00397 | UPS[2].AlarmNapakaNaVentilatorju
GSMUPS2AlarmOnBattery | DIGITAL | IOD_GSM_TCP | 398 | 00398 | UPS[2].AlarmOnBattery
GSMUPS2AlarmOnBypass | DIGITAL | IOD_GSM_TCP | 399 | 00399 | UPS[2].AlarmOnBypass
GSMUPS2AlarmShutdownImminent | DIGITAL | IOD_GSM_TCP | 400 | 00400 | UPS[2].AlarmShutdownImminent
GSMUPS2AlarmShutdownPending | DIGITAL | IOD_GSM_TCP | 401 | 00401 | UPS[2].AlarmShutdownPending
GSMUPS2AlarmSlabaBaterija | DIGITAL | IOD_GSM_TCP | 402 | 00402 | UPS[2].AlarmSlabaBaterija
GSMUPS2AlarmSplosnaNapaka | DIGITAL | IOD_GSM_TCP | 403 | 00403 | UPS[2].AlarmSplosnaNapaka
GSMUPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 404 | 00404 | UPS[2].AlarmStanjeIzhodaIzvenToleranc
GSMUPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 405 | 00405 | UPS[2].AlarmStanjeVhodaIzvenToleranc
GSMUPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 406 | 00406 | UPS[2].AlarmTemperaturaIzvenToleranc
GSMUPS2AlarmTestInProgres | DIGITAL | IOD_GSM_TCP | 407 | 00407 | UPS[2].AlarmTestInProgres
GSMUPS2AlarmUPSIzhodOff | DIGITAL | IOD_GSM_TCP | 408 | 00408 | UPS[2].AlarmUPSIzhodOff
GSMUPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 409 | 00409 | UPS[2].AlarmUPSOffKotZahtevano
GSMUPS2AlarmUPSSystemOff | DIGITAL | IOD_GSM_TCP | 410 | 00410 | UPS[2].AlarmUPSSystemOff
GSMUPS2Napaka | DIGITAL | IOD_GSM_TCP | 411 | 00411 | UPS[2].Napaka
GSMUPS2StatusEcomodeAktiven | DIGITAL | IOD_GSM_TCP | 412 | 00412 | UPS[2].StatusEcomodeAktiven
GSMUPS2StatusInverterIsOn | DIGITAL | IOD_GSM_TCP | 413 | 00413 | UPS[2].StatusInverterIsOn
GSMUPS2StatusStopOperation | DIGITAL | IOD_GSM_TCP | 414 | 00414 | UPS[2].StatusStopOperation
GSMUPS3AlarmAwaitingPower | DIGITAL | IOD_GSM_TCP | 415 | 00415 | UPS[3].AlarmAwaitingPower
GSMUPS3AlarmBypassBad | DIGITAL | IOD_GSM_TCP | 416 | 00416 | UPS[3].AlarmBypassBad
GSMUPS3AlarmChargerFailed | DIGITAL | IOD_GSM_TCP | 417 | 00417 | UPS[3].AlarmChargerFailed
GSMUPS3AlarmCommunicationsLost | DIGITAL | IOD_GSM_TCP | 418 | 00418 | UPS[3].AlarmCommunicationsLost
GSMUPS3AlarmDepletedBattery | DIGITAL | IOD_GSM_TCP | 419 | 00419 | UPS[3].AlarmDepletedBattery
GSMUPS3AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM_TCP | 420 | 00420 | UPS[3].AlarmDiagnosticTestFailed
GSMUPS3AlarmInverterError | DIGITAL | IOD_GSM_TCP | 421 | 00421 | UPS[3].AlarmInverterError
GSMUPS3AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 422 | 00422 | UPS[3].AlarmIzhodOffKotZahtevano
GSMUPS3AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM_TCP | 423 | 00423 | UPS[3].AlarmIzhodPreobremenjen
GSMUPS3AlarmLowBattery | DIGITAL | IOD_GSM_TCP | 424 | 00424 | UPS[3].AlarmLowBattery
GSMUPS3AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM_TCP | 425 | 00425 | UPS[3].AlarmNapakaNaVarovalki
GSMUPS3AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM_TCP | 426 | 00426 | UPS[3].AlarmNapakaNaVentilatorju
GSMUPS3AlarmOnBattery | DIGITAL | IOD_GSM_TCP | 427 | 00427 | UPS[3].AlarmOnBattery
GSMUPS3AlarmOnBypass | DIGITAL | IOD_GSM_TCP | 428 | 00428 | UPS[3].AlarmOnBypass
GSMUPS3AlarmShutdownImminent | DIGITAL | IOD_GSM_TCP | 429 | 00429 | UPS[3].AlarmShutdownImminent
GSMUPS3AlarmShutdownPending | DIGITAL | IOD_GSM_TCP | 430 | 00430 | UPS[3].AlarmShutdownPending
GSMUPS3AlarmSlabaBaterija | DIGITAL | IOD_GSM_TCP | 431 | 00431 | UPS[3].AlarmSlabaBaterija
GSMUPS3AlarmSplosnaNapaka | DIGITAL | IOD_GSM_TCP | 432 | 00432 | UPS[3].AlarmSplosnaNapaka
GSMUPS3AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 433 | 00433 | UPS[3].AlarmStanjeIzhodaIzvenToleranc
GSMUPS3AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 434 | 00434 | UPS[3].AlarmStanjeVhodaIzvenToleranc
GSMUPS3AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 435 | 00435 | UPS[3].AlarmTemperaturaIzvenToleranc
GSMUPS3AlarmTestInProgres | DIGITAL | IOD_GSM_TCP | 436 | 00436 | UPS[3].AlarmTestInProgres
GSMUPS3AlarmUPSIzhodOff | DIGITAL | IOD_GSM_TCP | 437 | 00437 | UPS[3].AlarmUPSIzhodOff
GSMUPS3AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 438 | 00438 | UPS[3].AlarmUPSOffKotZahtevano
GSMUPS3AlarmUPSSystemOff | DIGITAL | IOD_GSM_TCP | 439 | 00439 | UPS[3].AlarmUPSSystemOff
GSMUPS3Napaka | DIGITAL | IOD_GSM_TCP | 440 | 00440 | UPS[3].Napaka
GSMUPS3StatusEcomodeAktiven | DIGITAL | IOD_GSM_TCP | 441 | 00441 | UPS[3].StatusEcomodeAktiven
GSMUPS3StatusInverterIsOn | DIGITAL | IOD_GSM_TCP | 442 | 00442 | UPS[3].StatusInverterIsOn
GSMUPS3StatusStopOperation | DIGITAL | IOD_GSM_TCP | 443 | 00443 | UPS[3].StatusStopOperation
GSMUPS_A_V23_delovanje | DIGITAL | IOD_GSM_TCP | 444 | 00444 | UPS_A_V23_delovanje
GSMUPS_A_V23_napaka | DIGITAL | IOD_GSM_TCP | 445 | 00445 | UPS_A_V23_napaka
GSMups_alarm | DIGITAL | IOD_GSM_TCP | 446 | 00446 | ups_alarm
GSMups_baterijski_nac | DIGITAL | IOD_GSM_TCP | 447 | 00447 | ups_baterijski_nac
GSMUPS_MGE1BatteryChargedState | DIGITAL | IOD_GSM_TCP | 448 | 00448 | UPS_MGE[1].BatteryChargedState
GSMUPS_MGE1BatteryCircuitBreaker | DIGITAL | IOD_GSM_TCP | 449 | 00449 | UPS_MGE[1].BatteryCircuitBreaker
GSMUPS_MGE1BatteryCompInProgress | DIGITAL | IOD_GSM_TCP | 450 | 00450 | UPS_MGE[1].BatteryCompInProgress
GSMUPS_MGE1BatteryFuseFault | DIGITAL | IOD_GSM_TCP | 451 | 00451 | UPS_MGE[1].BatteryFuseFault
GSMUPS_MGE1BatteryLowWarning | DIGITAL | IOD_GSM_TCP | 452 | 00452 | UPS_MGE[1].BatteryLowWarning
GSMUPS_MGE1BatteryTempOutOfToler | DIGITAL | IOD_GSM_TCP | 453 | 00453 | UPS_MGE[1].BatteryTempOutOfToler
GSMUPS_MGE1BypassInFreeFrequency | DIGITAL | IOD_GSM_TCP | 454 | 00454 | UPS_MGE[1].BypassInFreeFrequency
GSMUPS_MGE1ChargerGeneralFault | DIGITAL | IOD_GSM_TCP | 455 | 00455 | UPS_MGE[1].ChargerGeneralFault
GSMUPS_MGE1DeviceVentilationFault | DIGITAL | IOD_GSM_TCP | 456 | 00456 | UPS_MGE[1].DeviceVentilationFault
GSMUPS_MGE1InverterFuseFault | DIGITAL | IOD_GSM_TCP | 457 | 00457 | UPS_MGE[1].InverterFuseFault
GSMUPS_MGE1InverterOverload | DIGITAL | IOD_GSM_TCP | 458 | 00458 | UPS_MGE[1].InverterOverload
GSMUPS_MGE1InverterThermalOverload | DIGITAL | IOD_GSM_TCP | 459 | 00459 | UPS_MGE[1].InverterThermalOverload
GSMUPS_MGE1Mains1VoltOutOfToler | DIGITAL | IOD_GSM_TCP | 460 | 00460 | UPS_MGE[1].Mains1VoltOutOfToler
GSMUPS_MGE1Mains2Overload | DIGITAL | IOD_GSM_TCP | 461 | 00461 | UPS_MGE[1].Mains2Overload
GSMUPS_MGE1Mains2VoltOutOfToler | DIGITAL | IOD_GSM_TCP | 462 | 00462 | UPS_MGE[1].Mains2VoltOutOfToler
GSMUPS_MGE1MaintenancePosition | DIGITAL | IOD_GSM_TCP | 463 | 00463 | UPS_MGE[1].MaintenancePosition
GSMUPS_MGE1ManualBypassSwitch | DIGITAL | IOD_GSM_TCP | 464 | 00464 | UPS_MGE[1].ManualBypassSwitch
GSMUPS_MGE1NapakaNaVarovalkah | DIGITAL | IOD_GSM_TCP | 465 | 00465 | UPS_MGE[1].NapakaNaVarovalkah
GSMUPS_MGE1OutputInShortCircuit | DIGITAL | IOD_GSM_TCP | 466 | 00466 | UPS_MGE[1].OutputInShortCircuit
GSMUPS_MGE1OutputOverload | DIGITAL | IOD_GSM_TCP | 467 | 00467 | UPS_MGE[1].OutputOverload
GSMUPS_MGE1OutputThermalOverload | DIGITAL | IOD_GSM_TCP | 468 | 00468 | UPS_MGE[1].OutputThermalOverload
GSMUPS_MGE1RectifierOn | DIGITAL | IOD_GSM_TCP | 469 | 00469 | UPS_MGE[1].RectifierOn
GSMUPS_MGE1RectifierThermOverload | DIGITAL | IOD_GSM_TCP | 470 | 00470 | UPS_MGE[1].RectifierThermOverload
GSMUPS_MGE1Skupna_napaka | DIGITAL | IOD_GSM_TCP | 471 | 00471 | UPS_MGE[1].Skupna_napaka
GSMUPS_MGE1UPS_coupled | DIGITAL | IOD_GSM_TCP | 472 | 00472 | UPS_MGE[1].UPS_coupled
GSMUPS_MGE1UPS_error | DIGITAL | IOD_GSM_TCP | 473 | 00473 | UPS_MGE[1].UPS_error
GSMUPS_MGE1UPS_in_backup | DIGITAL | IOD_GSM_TCP | 474 | 00474 | UPS_MGE[1].UPS_in_backup
GSMups_polnjenje | DIGITAL | IOD_GSM_TCP | 475 | 00475 | ups_polnjenje
GSMUPS_V23_delovanje | DIGITAL | IOD_GSM_TCP | 476 | 00476 | UPS_V23_delovanje
GSMUPS_V23_napaka | DIGITAL | IOD_GSM_TCP | 477 | 00477 | UPS_V23_napaka
GSMUPS_V25_delovanje | DIGITAL | IOD_GSM_TCP | 478 | 00478 | UPS_V25_delovanje
GSMUPS_V25_napaka | DIGITAL | IOD_GSM_TCP | 479 | 00479 | UPS_V25_napaka
GSMUPSMGEErrors10 | DIGITAL | IOD_GSM_TCP | 480 | 00480 | UPSMGEErrors[10]
GSMUPSMGEErrors11 | DIGITAL | IOD_GSM_TCP | 481 | 00481 | UPSMGEErrors[11]
GSMUPSMGEErrors12 | DIGITAL | IOD_GSM_TCP | 482 | 00482 | UPSMGEErrors[12]
GSMUPSMGEErrors13 | DIGITAL | IOD_GSM_TCP | 483 | 00483 | UPSMGEErrors[13]
GSMUPSMGEErrors14 | DIGITAL | IOD_GSM_TCP | 484 | 00484 | UPSMGEErrors[14]
GSMUPSMGEErrors15 | DIGITAL | IOD_GSM_TCP | 485 | 00485 | UPSMGEErrors[15]
GSMUPSMGEErrors16 | DIGITAL | IOD_GSM_TCP | 486 | 00486 | UPSMGEErrors[16]
GSMUPSMGEErrors17 | DIGITAL | IOD_GSM_TCP | 487 | 00487 | UPSMGEErrors[17]
GSMUPSMGEErrors1 | DIGITAL | IOD_GSM_TCP | 488 | 00488 | UPSMGEErrors[1]
GSMUPSMGEErrors2 | DIGITAL | IOD_GSM_TCP | 489 | 00489 | UPSMGEErrors[2]
GSMUPSMGEErrors3 | DIGITAL | IOD_GSM_TCP | 490 | 00490 | UPSMGEErrors[3]
GSMUPSMGEErrors4 | DIGITAL | IOD_GSM_TCP | 491 | 00491 | UPSMGEErrors[4]
GSMUPSMGEErrors5 | DIGITAL | IOD_GSM_TCP | 492 | 00492 | UPSMGEErrors[5]
GSMUPSMGEErrors6 | DIGITAL | IOD_GSM_TCP | 493 | 00493 | UPSMGEErrors[6]
GSMUPSMGEErrors7 | DIGITAL | IOD_GSM_TCP | 494 | 00494 | UPSMGEErrors[7]
GSMUPSMGEErrors8 | DIGITAL | IOD_GSM_TCP | 495 | 00495 | UPSMGEErrors[8]
GSMUPSMGEErrors9 | DIGITAL | IOD_GSM_TCP | 496 | 00496 | UPSMGEErrors[9]
GSMUserLoggedIn | DIGITAL | IOD_GSM_TCP | 497 | 00497 | UserLoggedIn
GSMVLAZILEC1_delovanje | DIGITAL | IOD_GSM_TCP | 498 | 00498 | VLAZILEC1_delovanje
GSMVLAZILEC1_napaka | DIGITAL | IOD_GSM_TCP | 499 | 00499 | VLAZILEC1_napaka
GSMVLAZILEC2_delovanje | DIGITAL | IOD_GSM_TCP | 500 | 00500 | VLAZILEC2_delovanje
GSMVLAZILEC2_napaka | DIGITAL | IOD_GSM_TCP | 501 | 00501 | VLAZILEC2_napaka
GSMXVH_AlarmOn | DIGITAL | IOD_GSM_TCP | 502 | 00502 | XVH_AlarmOn
GSMXVH_enopolna_napaka | DIGITAL | IOD_GSM_TCP | 503 | 00503 | XVH_enopolna_napaka
GSMDateTimeDan | INT | IOD_GSM_TCP | 1 | 40001 | DateTime.Dan | BYTE
GSMDateTimeLeto | INT | IOD_GSM_TCP | 2 | 40002 | DateTime.Leto | BYTE
GSMDateTimeLeto2 | INT | IOD_GSM_TCP | 3 | 40003 | DateTime.Leto2
GSMDateTimeMesec | INT | IOD_GSM_TCP | 4 | 40004 | DateTime.Mesec | BYTE
GSMDateTimeMinuta | INT | IOD_GSM_TCP | 5 | 40005 | DateTime.Minuta | BYTE
GSMDateTimePLC_Dan | INT | IOD_GSM_TCP | 6 | 40006 | DateTime.PLC_Dan | BYTE
GSMDateTimePLC_DanVTednu | INT | IOD_GSM_TCP | 7 | 40007 | DateTime.PLC_DanVTednu | BYTE
GSMDateTimePLC_Leto | INT | IOD_GSM_TCP | 8 | 40008 | DateTime.PLC_Leto | BYTE
GSMDateTimePLC_Mesec | INT | IOD_GSM_TCP | 9 | 40009 | DateTime.PLC_Mesec | BYTE
GSMDateTimePLC_Minuta | INT | IOD_GSM_TCP | 10 | 40010 | DateTime.PLC_Minuta | BYTE
GSMDateTimePLC_Sekunda | INT | IOD_GSM_TCP | 11 | 40011 | DateTime.PLC_Sekunda | BYTE
GSMDateTimePLC_Ura | INT | IOD_GSM_TCP | 12 | 40012 | DateTime.PLC_Ura | BYTE
GSMDateTimeSekunda | INT | IOD_GSM_TCP | 13 | 40013 | DateTime.Sekunda | BYTE
GSMDateTimeUra | INT | IOD_GSM_TCP | 14 | 40014 | DateTime.Ura | BYTE
GSMHIA1_vlaga_s | INT | IOD_GSM_TCP | 15 | 40015 | HIA1_vlaga_s
GSMHIA2_vlaga_s | INT | IOD_GSM_TCP | 16 | 40016 | HIA2_vlaga_s
GSMHIA3_vlaga_s | INT | IOD_GSM_TCP | 17 | 40017 | HIA3_vlaga_s
GSMHIA4_vlaga_s | INT | IOD_GSM_TCP | 18 | 40018 | HIA4_vlaga_s
GSMHIA5_vlaga_s | INT | IOD_GSM_TCP | 19 | 40019 | HIA5_vlaga_s
GSMHIA6_vlaga_s | INT | IOD_GSM_TCP | 20 | 40020 | HIA6_vlaga_s
GSMHIA7_vlaga_s | INT | IOD_GSM_TCP | 21 | 40021 | HIA7_vlaga_s
GSMKlima1Analog_izh_mesanje | INT | IOD_GSM_TCP | 22 | 40022 | Klima[1].Analog_izh_mesanje
GSMKlima1Analog_izh_rekuperator | INT | IOD_GSM_TCP | 23 | 40023 | Klima[1].Analog_izh_rekuperator
GSMKlima1Analog_izh_VentGrelnika | INT | IOD_GSM_TCP | 24 | 40024 | Klima[1].Analog_izh_VentGrelnika
GSMKlima1Analog_izh_VentHlajenja | INT | IOD_GSM_TCP | 25 | 40025 | Klima[1].Analog_izh_VentHlajenja
GSMKlima1Dejanska_zel_temp | INT | IOD_GSM_TCP | 26 | 40026 | Klima[1].Dejanska_zel_temp
GSMKlima1Hitrost_del_vent_disp | INT | IOD_GSM_TCP | 27 | 40027 | Klima[1].Hitrost_del_vent_disp
GSMKlima1Max_vpih | INT | IOD_GSM_TCP | 28 | 40028 | Klima[1].Max_vpih
GSMKlima1Min_vpih | INT | IOD_GSM_TCP | 29 | 40029 | Klima[1].Min_vpih
GSMKlima1Obrat_ure_Vent_h1 | INT | IOD_GSM_TCP | 30 | 40030 | Klima[1].Obrat_ure_Vent_h1
GSMKlima1Obrat_ure_Vent_h2 | INT | IOD_GSM_TCP | 31 | 40031 | Klima[1].Obrat_ure_Vent_h2
GSMKlima1Pol_komp_konec | INT | IOD_GSM_TCP | 32 | 40032 | Klima[1].Pol_komp_konec
GSMKlima1Pol_komp_sprem_zel_vr | INT | IOD_GSM_TCP | 33 | 40033 | Klima[1].Pol_komp_sprem_zel_vr
GSMKlima1Pol_komp_zacetek | INT | IOD_GSM_TCP | 34 | 40034 | Klima[1].Pol_komp_zacetek
GSMKlima1PreklopHitDelVent | INT | IOD_GSM_TCP | 35 | 40035 | Klima[1].PreklopHitDelVent
GSMKlima1Protizamrz_zascita | INT | IOD_GSM_TCP | 36 | 40036 | Klima[1].Protizamrz_zascita
GSMKlima1Rezim_delovanja | INT | IOD_GSM_TCP | 37 | 40037 | Klima[1].Rezim_delovanja
GSMKlima1Temperatura_dovoda | INT | IOD_GSM_TCP | 38 | 40038 | Klima[1].Temperatura_dovoda
GSMKlima1Temperatura_prostora | INT | IOD_GSM_TCP | 39 | 40039 | Klima[1].Temperatura_prostora
GSMKlima1TempPredPloscnimRekup | INT | IOD_GSM_TCP | 40 | 40040 | Klima[1].TempPredPloscnimRekup
GSMKlima1TempZaPloscnimRekup | INT | IOD_GSM_TCP | 41 | 40041 | Klima[1].TempZaPloscnimRekup
GSMKlima1Vlaga_v_prostoru | INT | IOD_GSM_TCP | 42 | 40042 | Klima[1].Vlaga_v_prostoru
GSMKlima1VlagaVstopZrakaProstor | INT | IOD_GSM_TCP | 43 | 40043 | Klima[1].VlagaVstopZrakaProstor
GSMKlima1Zel_temp_eko_gretja | INT | IOD_GSM_TCP | 44 | 40044 | Klima[1].Zel_temp_eko_gretja
GSMKlima1Zel_temp_eko_hlajenja | INT | IOD_GSM_TCP | 45 | 40045 | Klima[1].Zel_temp_eko_hlajenja
GSMKlima1Zel_temp_komf_gretja | INT | IOD_GSM_TCP | 46 | 40046 | Klima[1].Zel_temp_komf_gretja
GSMKlima1Zel_temp_komf_hlajenja | INT | IOD_GSM_TCP | 47 | 40047 | Klima[1].Zel_temp_komf_hlajenja
GSMKlima1Zim_komp_konec | INT | IOD_GSM_TCP | 48 | 40048 | Klima[1].Zim_komp_konec
GSMKlima1Zim_komp_sprem_zel_vr | INT | IOD_GSM_TCP | 49 | 40049 | Klima[1].Zim_komp_sprem_zel_vr
GSMKlima1Zim_komp_zacetek | INT | IOD_GSM_TCP | 50 | 40050 | Klima[1].Zim_komp_zacetek
GSMKlima1ZimKompMinVpihKonec | INT | IOD_GSM_TCP | 51 | 40051 | Klima[1].ZimKompMinVpihKonec
GSMKlima1ZimKompMinVpihZac | INT | IOD_GSM_TCP | 52 | 40052 | Klima[1].ZimKompMinVpihZac
GSMKlima1ZkompMinVpihSpremZelVr | INT | IOD_GSM_TCP | 53 | 40053 | Klima[1].ZkompMinVpihSpremZelVr
GSMKlima1Zunanja_temp | INT | IOD_GSM_TCP | 54 | 40054 | Klima[1].Zunanja_temp
GSMKlima2Analog_izh_mesanje | INT | IOD_GSM_TCP | 55 | 40055 | Klima[2].Analog_izh_mesanje
GSMKlima2Analog_izh_rekuperator | INT | IOD_GSM_TCP | 56 | 40056 | Klima[2].Analog_izh_rekuperator
GSMKlima2Analog_izh_VentGrelnika | INT | IOD_GSM_TCP | 57 | 40057 | Klima[2].Analog_izh_VentGrelnika
GSMKlima2Analog_izh_VentHlajenja | INT | IOD_GSM_TCP | 58 | 40058 | Klima[2].Analog_izh_VentHlajenja
GSMKlima2Dejanska_zel_temp | INT | IOD_GSM_TCP | 59 | 40059 | Klima[2].Dejanska_zel_temp
GSMKlima2Hitrost_del_vent_disp | INT | IOD_GSM_TCP | 60 | 40060 | Klima[2].Hitrost_del_vent_disp
GSMKlima2Max_vpih | INT | IOD_GSM_TCP | 61 | 40061 | Klima[2].Max_vpih
GSMKlima2Min_vpih | INT | IOD_GSM_TCP | 62 | 40062 | Klima[2].Min_vpih
GSMKlima2Obrat_ure_Vent_h1 | INT | IOD_GSM_TCP | 63 | 40063 | Klima[2].Obrat_ure_Vent_h1
GSMKlima2Obrat_ure_Vent_h2 | INT | IOD_GSM_TCP | 64 | 40064 | Klima[2].Obrat_ure_Vent_h2
GSMKlima2Pol_komp_konec | INT | IOD_GSM_TCP | 65 | 40065 | Klima[2].Pol_komp_konec
GSMKlima2Pol_komp_sprem_zel_vr | INT | IOD_GSM_TCP | 66 | 40066 | Klima[2].Pol_komp_sprem_zel_vr
GSMKlima2Pol_komp_zacetek | INT | IOD_GSM_TCP | 67 | 40067 | Klima[2].Pol_komp_zacetek
GSMKlima2PreklopHitDelVent | INT | IOD_GSM_TCP | 68 | 40068 | Klima[2].PreklopHitDelVent
GSMKlima2Protizamrz_zascita | INT | IOD_GSM_TCP | 69 | 40069 | Klima[2].Protizamrz_zascita
GSMKlima2Rezim_delovanja | INT | IOD_GSM_TCP | 70 | 40070 | Klima[2].Rezim_delovanja
GSMKlima2Temperatura_dovoda | INT | IOD_GSM_TCP | 71 | 40071 | Klima[2].Temperatura_dovoda
GSMKlima2Temperatura_prostora | INT | IOD_GSM_TCP | 72 | 40072 | Klima[2].Temperatura_prostora
GSMKlima2TempPredPloscnimRekup | INT | IOD_GSM_TCP | 73 | 40073 | Klima[2].TempPredPloscnimRekup
GSMKlima2TempZaPloscnimRekup | INT | IOD_GSM_TCP | 74 | 40074 | Klima[2].TempZaPloscnimRekup
GSMKlima2Vlaga_v_prostoru | INT | IOD_GSM_TCP | 75 | 40075 | Klima[2].Vlaga_v_prostoru
GSMKlima2VlagaVstopZrakaProstor | INT | IOD_GSM_TCP | 76 | 40076 | Klima[2].VlagaVstopZrakaProstor
GSMKlima2Zel_temp_eko_gretja | INT | IOD_GSM_TCP | 77 | 40077 | Klima[2].Zel_temp_eko_gretja
GSMKlima2Zel_temp_eko_hlajenja | INT | IOD_GSM_TCP | 78 | 40078 | Klima[2].Zel_temp_eko_hlajenja
GSMKlima2Zel_temp_komf_gretja | INT | IOD_GSM_TCP | 79 | 40079 | Klima[2].Zel_temp_komf_gretja
GSMKlima2Zel_temp_komf_hlajenja | INT | IOD_GSM_TCP | 80 | 40080 | Klima[2].Zel_temp_komf_hlajenja
GSMKlima2Zim_komp_konec | INT | IOD_GSM_TCP | 81 | 40081 | Klima[2].Zim_komp_konec
GSMKlima2Zim_komp_sprem_zel_vr | INT | IOD_GSM_TCP | 82 | 40082 | Klima[2].Zim_komp_sprem_zel_vr
GSMKlima2Zim_komp_zacetek | INT | IOD_GSM_TCP | 83 | 40083 | Klima[2].Zim_komp_zacetek
GSMKlima2ZimKompMinVpihKonec | INT | IOD_GSM_TCP | 84 | 40084 | Klima[2].ZimKompMinVpihKonec
GSMKlima2ZimKompMinVpihZac | INT | IOD_GSM_TCP | 85 | 40085 | Klima[2].ZimKompMinVpihZac
GSMKlima2ZkompMinVpihSpremZelVr | INT | IOD_GSM_TCP | 86 | 40086 | Klima[2].ZkompMinVpihSpremZelVr
GSMKlima2Zunanja_temp | INT | IOD_GSM_TCP | 87 | 40087 | Klima[2].Zunanja_temp
GSMKlimaIzklopObrUre | INT | IOD_GSM_TCP | 88 | 40088 | KlimaIzklopObrUre
GSMKlime_vklopi_n | INT | IOD_GSM_TCP | 89 | 40089 | Klime_vklopi_n
GSMkom_nast_cas_izpada | INT | IOD_GSM_TCP | 90 | 40090 | kom_nast_cas_izpada
GSMPMM1AlarmPhase1GlobalAlarmReg | INT | IOD_GSM_TCP | 91 | 40091 | PMM[1].AlarmPhase[1].GlobalAlarmReg
GSMPMM1AlarmPhase2GlobalAlarmReg | INT | IOD_GSM_TCP | 92 | 40092 | PMM[1].AlarmPhase[2].GlobalAlarmReg
GSMPMM1AlarmPhase3GlobalAlarmReg | INT | IOD_GSM_TCP | 93 | 40093 | PMM[1].AlarmPhase[3].GlobalAlarmReg
GSMQ12stanje | INT | IOD_GSM_TCP | 94 | 40094 | Q12stanje | BYTE
GSMTempHistereza | INT | IOD_GSM_TCP | 95 | 40095 | TempHistereza
GSMTempPovp234 | INT | IOD_GSM_TCP | 96 | 40096 | TempPovp234
GSMTempPovp234Alarm | INT | IOD_GSM_TCP | 97 | 40097 | TempPovp234Alarm
GSMTempPovp56 | INT | IOD_GSM_TCP | 98 | 40098 | TempPovp56
GSMTempPovp56Alarm | INT | IOD_GSM_TCP | 99 | 40099 | TempPovp56Alarm
GSMTempZaVklopKlim1 | INT | IOD_GSM_TCP | 100 | 40100 | TempZaVklopKlim1
GSMTempZaVklopKlim2 | INT | IOD_GSM_TCP | 101 | 40101 | TempZaVklopKlim2
GSMTIA1_alarm | INT | IOD_GSM_TCP | 102 | 40102 | TIA1_alarm
GSMTIA1_temp_s | INT | IOD_GSM_TCP | 103 | 40103 | TIA1_temp_s
GSMTIA2_alarm | INT | IOD_GSM_TCP | 104 | 40104 | TIA2_alarm
GSMTIA2_temp_s | INT | IOD_GSM_TCP | 105 | 40105 | TIA2_temp_s
GSMTIA3_alarm | INT | IOD_GSM_TCP | 106 | 40106 | TIA3_alarm
GSMTIA3_temp_s | INT | IOD_GSM_TCP | 107 | 40107 | TIA3_temp_s
GSMTIA4_alarm | INT | IOD_GSM_TCP | 108 | 40108 | TIA4_alarm
GSMTIA4_temp_s | INT | IOD_GSM_TCP | 109 | 40109 | TIA4_temp_s
GSMTIA5_alarm | INT | IOD_GSM_TCP | 110 | 40110 | TIA5_alarm
GSMTIA5_temp_s | INT | IOD_GSM_TCP | 111 | 40111 | TIA5_temp_s
GSMTIA6_alarm | INT | IOD_GSM_TCP | 112 | 40112 | TIA6_alarm
GSMTIA6_temp_s | INT | IOD_GSM_TCP | 113 | 40113 | TIA6_temp_s
GSMTIA7_alarm | INT | IOD_GSM_TCP | 114 | 40114 | TIA7_alarm
GSMTIA7_temp_s | INT | IOD_GSM_TCP | 115 | 40115 | TIA7_temp_s
GSMUPS1InverterStatus | INT | IOD_GSM_TCP | 116 | 40116 | UPS[1].InverterStatus
GSMUPS1OutputStatus | INT | IOD_GSM_TCP | 117 | 40117 | UPS[1].OutputStatus
GSMUPS1SteviloIzpadovVhodneLinije | INT | IOD_GSM_TCP | 118 | 40118 | UPS[1].SteviloIzpadovVhodneLinije
GSMUPS1UnitStatus | INT | IOD_GSM_TCP | 119 | 40119 | UPS[1].UnitStatus
GSMUPS2InverterStatus | INT | IOD_GSM_TCP | 120 | 40120 | UPS[2].InverterStatus
GSMUPS2OutputStatus | INT | IOD_GSM_TCP | 121 | 40121 | UPS[2].OutputStatus
GSMUPS2SteviloIzpadovVhodneLinije | INT | IOD_GSM_TCP | 122 | 40122 | UPS[2].SteviloIzpadovVhodneLinije
GSMUPS2UnitStatus | INT | IOD_GSM_TCP | 123 | 40123 | UPS[2].UnitStatus
GSMUPS3InverterStatus | INT | IOD_GSM_TCP | 124 | 40124 | UPS[3].InverterStatus
GSMUPS3OutputStatus | INT | IOD_GSM_TCP | 125 | 40125 | UPS[3].OutputStatus
GSMUPS3SteviloIzpadovVhodneLinije | INT | IOD_GSM_TCP | 126 | 40126 | UPS[3].SteviloIzpadovVhodneLinije
GSMUPS3UnitStatus | INT | IOD_GSM_TCP | 127 | 40127 | UPS[3].UnitStatus
GSMUPS_MGE1BatteryBackupTime | INT | IOD_GSM_TCP | 128 | 40128 | UPS_MGE[1].BatteryBackupTime
GSMUPS_MGE1BatteryChargingLevel | INT | IOD_GSM_TCP | 129 | 40129 | UPS_MGE[1].BatteryChargingLevel
GSMUPS_MGE1BatteryRechargeDuration | INT | IOD_GSM_TCP | 130 | 40130 | UPS_MGE[1].BatteryRechargeDuration
GSMUPS_MGE1I1output | INT | IOD_GSM_TCP | 131 | 40131 | UPS_MGE[1].I1output
GSMUPS_MGE1I2output | INT | IOD_GSM_TCP | 132 | 40132 | UPS_MGE[1].I2output
GSMUPS_MGE1I3output | INT | IOD_GSM_TCP | 133 | 40133 | UPS_MGE[1].I3output
GSMUPS_MGE1InverterFrequency | INT | IOD_GSM_TCP | 134 | 40134 | UPS_MGE[1].InverterFrequency
GSMUPS_MGE1OutputActivePower1 | INT | IOD_GSM_TCP | 135 | 40135 | UPS_MGE[1].OutputActivePower1
GSMUPS_MGE1OutputActivePower2 | INT | IOD_GSM_TCP | 136 | 40136 | UPS_MGE[1].OutputActivePower2
GSMUPS_MGE1OutputActivePower3 | INT | IOD_GSM_TCP | 137 | 40137 | UPS_MGE[1].OutputActivePower3
GSMUPS_MGE1OutputFrequency | INT | IOD_GSM_TCP | 138 | 40138 | UPS_MGE[1].OutputFrequency
GSMUPS_MGE1OutputLoadLevel | INT | IOD_GSM_TCP | 139 | 40139 | UPS_MGE[1].OutputLoadLevel
GSMUPS_MGE1StatusBaterije | INT | IOD_GSM_TCP | 140 | 40140 | UPS_MGE[1].StatusBaterije | BYTE
GSMUPS_MGE1U12mains1 | INT | IOD_GSM_TCP | 141 | 40141 | UPS_MGE[1].U12mains1
GSMUPS_MGE1U12mains2 | INT | IOD_GSM_TCP | 142 | 40142 | UPS_MGE[1].U12mains2
GSMUPS_MGE1U1N_inverter | INT | IOD_GSM_TCP | 143 | 40143 | UPS_MGE[1].U1N_inverter
GSMUPS_MGE1U1N_output | INT | IOD_GSM_TCP | 144 | 40144 | UPS_MGE[1].U1N_output
GSMUPS_MGE1U23mains1 | INT | IOD_GSM_TCP | 145 | 40145 | UPS_MGE[1].U23mains1
GSMUPS_MGE1U23mains2 | INT | IOD_GSM_TCP | 146 | 40146 | UPS_MGE[1].U23mains2
GSMUPS_MGE1U2N_inverter | INT | IOD_GSM_TCP | 147 | 40147 | UPS_MGE[1].U2N_inverter
GSMUPS_MGE1U2N_output | INT | IOD_GSM_TCP | 148 | 40148 | UPS_MGE[1].U2N_output
GSMUPS_MGE1U31mains1 | INT | IOD_GSM_TCP | 149 | 40149 | UPS_MGE[1].U31mains1
GSMUPS_MGE1U31mains2 | INT | IOD_GSM_TCP | 150 | 40150 | UPS_MGE[1].U31mains2
GSMUPS_MGE1U3N_inverter | INT | IOD_GSM_TCP | 151 | 40151 | UPS_MGE[1].U3N_inverter
GSMUPS_MGE1U3N_output | INT | IOD_GSM_TCP | 152 | 40152 | UPS_MGE[1].U3N_output
GSMUPS_MGE1U_battery | INT | IOD_GSM_TCP | 153 | 40153 | UPS_MGE[1].U_battery
GSMUserCurrentLevel | INT | IOD_GSM_TCP | 154 | 40154 | UserCurrentLevel | BYTE
GSMMAX_SOCKET_FD_SETSIZE | LONG | IOD_GSM_TCP | 3001 | 43001 | MAX_SOCKET_FD_SETSIZE
GSMCirc1CosFi_III | REAL | IOD_GSM_TCP | 4001 | 44001 | Circ[1].CosFi_III
GSMCirc1DelovnaEnergija | REAL | IOD_GSM_TCP | 4003 | 44003 | Circ[1].DelovnaEnergija
GSMCirc1DelovnaEnergija_TEMP | REAL | IOD_GSM_TCP | 4005 | 44005 | Circ[1].DelovnaEnergija_TEMP
GSMCirc1DelovnaMoc_III | REAL | IOD_GSM_TCP | 4007 | 44007 | Circ[1].DelovnaMoc_III
GSMCirc1DelovnaMoc_L1 | REAL | IOD_GSM_TCP | 4009 | 44009 | Circ[1].DelovnaMoc_L1
GSMCirc1DelovnaMoc_L2 | REAL | IOD_GSM_TCP | 4011 | 44011 | Circ[1].DelovnaMoc_L2
GSMCirc1DelovnaMoc_L3 | REAL | IOD_GSM_TCP | 4013 | 44013 | Circ[1].DelovnaMoc_L3
GSMCirc1Frekvenca_L1 | REAL | IOD_GSM_TCP | 4015 | 44015 | Circ[1].Frekvenca_L1
GSMCirc1InduktivnaEnergija | REAL | IOD_GSM_TCP | 4017 | 44017 | Circ[1].InduktivnaEnergija
GSMCirc1InduktivnaMoc_III | REAL | IOD_GSM_TCP | 4019 | 44019 | Circ[1].InduktivnaMoc_III
GSMCirc1JalovaMoc_L1 | REAL | IOD_GSM_TCP | 4021 | 44021 | Circ[1].JalovaMoc_L1
GSMCirc1JalovaMoc_L2 | REAL | IOD_GSM_TCP | 4023 | 44023 | Circ[1].JalovaMoc_L2
GSMCirc1JalovaMoc_L3 | REAL | IOD_GSM_TCP | 4025 | 44025 | Circ[1].JalovaMoc_L3
GSMCirc1KapacitivnaEnergija | REAL | IOD_GSM_TCP | 4027 | 44027 | Circ[1].KapacitivnaEnergija
GSMCirc1KapacitivnaMoc_III | REAL | IOD_GSM_TCP | 4029 | 44029 | Circ[1].KapacitivnaMoc_III
GSMCirc1MaximumDemand | REAL | IOD_GSM_TCP | 4031 | 44031 | Circ[1].MaximumDemand
GSMCirc1MaximumDemandA2 | REAL | IOD_GSM_TCP | 4033 | 44033 | Circ[1].MaximumDemandA2
GSMCirc1MaximumDemandA3 | REAL | IOD_GSM_TCP | 4035 | 44035 | Circ[1].MaximumDemandA3
GSMCirc1Napetost_L1_L2 | REAL | IOD_GSM_TCP | 4037 | 44037 | Circ[1].Napetost_L1_L2
GSMCirc1Napetost_L1_N | REAL | IOD_GSM_TCP | 4039 | 44039 | Circ[1].Napetost_L1_N
GSMCirc1Napetost_L2_L3 | REAL | IOD_GSM_TCP | 4041 | 44041 | Circ[1].Napetost_L2_L3
GSMCirc1Napetost_L2_N | REAL | IOD_GSM_TCP | 4043 | 44043 | Circ[1].Napetost_L2_N
GSMCirc1Napetost_L3_L1 | REAL | IOD_GSM_TCP | 4045 | 44045 | Circ[1].Napetost_L3_L1
GSMCirc1Napetost_L3_N | REAL | IOD_GSM_TCP | 4047 | 44047 | Circ[1].Napetost_L3_N
GSMCirc1NavideznaMoc_III | REAL | IOD_GSM_TCP | 4049 | 44049 | Circ[1].NavideznaMoc_III
GSMCirc1NicelniTok | REAL | IOD_GSM_TCP | 4051 | 44051 | Circ[1].NicelniTok
GSMCirc1PowerFactor_III | REAL | IOD_GSM_TCP | 4053 | 44053 | Circ[1].PowerFactor_III
GSMCirc1PowerFactor_L1 | REAL | IOD_GSM_TCP | 4055 | 44055 | Circ[1].PowerFactor_L1
GSMCirc1PowerFactor_L2 | REAL | IOD_GSM_TCP | 4057 | 44057 | Circ[1].PowerFactor_L2
GSMCirc1PowerFactor_L3 | REAL | IOD_GSM_TCP | 4059 | 44059 | Circ[1].PowerFactor_L3
GSMCirc1RazEner_D | REAL | IOD_GSM_TCP | 4061 | 44061 | Circ[1].RazEner_D
GSMCirc1RazEner_D_SCADA | REAL | IOD_GSM_TCP | 4063 | 44063 | Circ[1].RazEner_D_SCADA
GSMCirc1RazEner_D_TEMP | REAL | IOD_GSM_TCP | 4065 | 44065 | Circ[1].RazEner_D_TEMP
GSMCirc1RazEner_M | REAL | IOD_GSM_TCP | 4067 | 44067 | Circ[1].RazEner_M
GSMCirc1RazEner_M_SCADA | REAL | IOD_GSM_TCP | 4069 | 44069 | Circ[1].RazEner_M_SCADA
GSMCirc1RazEner_M_TEMP | REAL | IOD_GSM_TCP | 4071 | 44071 | Circ[1].RazEner_M_TEMP
GSMCirc1RazEner_T | REAL | IOD_GSM_TCP | 4073 | 44073 | Circ[1].RazEner_T
GSMCirc1RazEner_T_SCADA | REAL | IOD_GSM_TCP | 4075 | 44075 | Circ[1].RazEner_T_SCADA
GSMCirc1RazEner_T_TEMP | REAL | IOD_GSM_TCP | 4077 | 44077 | Circ[1].RazEner_T_TEMP
GSMCirc1THDI_L1 | REAL | IOD_GSM_TCP | 4079 | 44079 | Circ[1].THDI_L1
GSMCirc1THDI_L2 | REAL | IOD_GSM_TCP | 4081 | 44081 | Circ[1].THDI_L2
GSMCirc1THDI_L3 | REAL | IOD_GSM_TCP | 4083 | 44083 | Circ[1].THDI_L3
GSMCirc1THDV_L1 | REAL | IOD_GSM_TCP | 4085 | 44085 | Circ[1].THDV_L1
GSMCirc1THDV_L2 | REAL | IOD_GSM_TCP | 4087 | 44087 | Circ[1].THDV_L2
GSMCirc1THDV_L3 | REAL | IOD_GSM_TCP | 4089 | 44089 | Circ[1].THDV_L3
GSMCirc1Tok_L1 | REAL | IOD_GSM_TCP | 4091 | 44091 | Circ[1].Tok_L1
GSMCirc1Tok_L2 | REAL | IOD_GSM_TCP | 4093 | 44093 | Circ[1].Tok_L2
GSMCirc1Tok_L3 | REAL | IOD_GSM_TCP | 4095 | 44095 | Circ[1].Tok_L3
GSMCirc1TokPovprecje_III | REAL | IOD_GSM_TCP | 4097 | 44097 | Circ[1].TokPovprecje_III
GSMPMM2VirACurrent10 | REAL | IOD_GSM_TCP | 4099 | 44099 | PMM2.VirA.Current[10]
GSMPMM2VirACurrent11 | REAL | IOD_GSM_TCP | 4101 | 44101 | PMM2.VirA.Current[11]
GSMPMM2VirACurrent12 | REAL | IOD_GSM_TCP | 4103 | 44103 | PMM2.VirA.Current[12]
GSMPMM2VirACurrent13 | REAL | IOD_GSM_TCP | 4105 | 44105 | PMM2.VirA.Current[13]
GSMPMM2VirACurrent14 | REAL | IOD_GSM_TCP | 4107 | 44107 | PMM2.VirA.Current[14]
GSMPMM2VirACurrent15 | REAL | IOD_GSM_TCP | 4109 | 44109 | PMM2.VirA.Current[15]
GSMPMM2VirACurrent16 | REAL | IOD_GSM_TCP | 4111 | 44111 | PMM2.VirA.Current[16]
GSMPMM2VirACurrent17 | REAL | IOD_GSM_TCP | 4113 | 44113 | PMM2.VirA.Current[17]
GSMPMM2VirACurrent18 | REAL | IOD_GSM_TCP | 4115 | 44115 | PMM2.VirA.Current[18]
GSMPMM2VirACurrent19 | REAL | IOD_GSM_TCP | 4117 | 44117 | PMM2.VirA.Current[19]
GSMPMM2VirACurrent1 | REAL | IOD_GSM_TCP | 4119 | 44119 | PMM2.VirA.Current[1]
GSMPMM2VirACurrent20 | REAL | IOD_GSM_TCP | 4121 | 44121 | PMM2.VirA.Current[20]
GSMPMM2VirACurrent21 | REAL | IOD_GSM_TCP | 4123 | 44123 | PMM2.VirA.Current[21]
GSMPMM2VirACurrent22 | REAL | IOD_GSM_TCP | 4125 | 44125 | PMM2.VirA.Current[22]
GSMPMM2VirACurrent23 | REAL | IOD_GSM_TCP | 4127 | 44127 | PMM2.VirA.Current[23]
GSMPMM2VirACurrent24 | REAL | IOD_GSM_TCP | 4129 | 44129 | PMM2.VirA.Current[24]
GSMPMM2VirACurrent25 | REAL | IOD_GSM_TCP | 4131 | 44131 | PMM2.VirA.Current[25]
GSMPMM2VirACurrent26 | REAL | IOD_GSM_TCP | 4133 | 44133 | PMM2.VirA.Current[26]
GSMPMM2VirACurrent27 | REAL | IOD_GSM_TCP | 4135 | 44135 | PMM2.VirA.Current[27]
GSMPMM2VirACurrent28 | REAL | IOD_GSM_TCP | 4137 | 44137 | PMM2.VirA.Current[28]
GSMPMM2VirACurrent29 | REAL | IOD_GSM_TCP | 4139 | 44139 | PMM2.VirA.Current[29]
GSMPMM2VirACurrent2 | REAL | IOD_GSM_TCP | 4141 | 44141 | PMM2.VirA.Current[2]
GSMPMM2VirACurrent30 | REAL | IOD_GSM_TCP | 4143 | 44143 | PMM2.VirA.Current[30]
GSMPMM2VirACurrent31 | REAL | IOD_GSM_TCP | 4145 | 44145 | PMM2.VirA.Current[31]
GSMPMM2VirACurrent32 | REAL | IOD_GSM_TCP | 4147 | 44147 | PMM2.VirA.Current[32]
GSMPMM2VirACurrent33 | REAL | IOD_GSM_TCP | 4149 | 44149 | PMM2.VirA.Current[33]
GSMPMM2VirACurrent34 | REAL | IOD_GSM_TCP | 4151 | 44151 | PMM2.VirA.Current[34]
GSMPMM2VirACurrent35 | REAL | IOD_GSM_TCP | 4153 | 44153 | PMM2.VirA.Current[35]
GSMPMM2VirACurrent36 | REAL | IOD_GSM_TCP | 4155 | 44155 | PMM2.VirA.Current[36]
GSMPMM2VirACurrent37 | REAL | IOD_GSM_TCP | 4157 | 44157 | PMM2.VirA.Current[37]
GSMPMM2VirACurrent38 | REAL | IOD_GSM_TCP | 4159 | 44159 | PMM2.VirA.Current[38]
GSMPMM2VirACurrent39 | REAL | IOD_GSM_TCP | 4161 | 44161 | PMM2.VirA.Current[39]
GSMPMM2VirACurrent3 | REAL | IOD_GSM_TCP | 4163 | 44163 | PMM2.VirA.Current[3]
GSMPMM2VirACurrent40 | REAL | IOD_GSM_TCP | 4165 | 44165 | PMM2.VirA.Current[40]
GSMPMM2VirACurrent41 | REAL | IOD_GSM_TCP | 4167 | 44167 | PMM2.VirA.Current[41]
GSMPMM2VirACurrent42 | REAL | IOD_GSM_TCP | 4169 | 44169 | PMM2.VirA.Current[42]
GSMPMM2VirACurrent43 | REAL | IOD_GSM_TCP | 4171 | 44171 | PMM2.VirA.Current[43]
GSMPMM2VirACurrent44 | REAL | IOD_GSM_TCP | 4173 | 44173 | PMM2.VirA.Current[44]
GSMPMM2VirACurrent4 | REAL | IOD_GSM_TCP | 4175 | 44175 | PMM2.VirA.Current[4]
GSMPMM2VirACurrent5 | REAL | IOD_GSM_TCP | 4177 | 44177 | PMM2.VirA.Current[5]
GSMPMM2VirACurrent6 | REAL | IOD_GSM_TCP | 4179 | 44179 | PMM2.VirA.Current[6]
GSMPMM2VirACurrent7 | REAL | IOD_GSM_TCP | 4181 | 44181 | PMM2.VirA.Current[7]
GSMPMM2VirACurrent8 | REAL | IOD_GSM_TCP | 4183 | 44183 | PMM2.VirA.Current[8]
GSMPMM2VirACurrent9 | REAL | IOD_GSM_TCP | 4185 | 44185 | PMM2.VirA.Current[9]
GSMPMM2VirA_fsys | REAL | IOD_GSM_TCP | 4187 | 44187 | PMM2.VirA_fsys
GSMPMM2VirA_Isys | REAL | IOD_GSM_TCP | 4189 | 44189 | PMM2.VirA_Isys
GSMPMM2VirA_PFsys | REAL | IOD_GSM_TCP | 4191 | 44191 | PMM2.VirA_PFsys
GSMPMM2VirA_Psys | REAL | IOD_GSM_TCP | 4193 | 44193 | PMM2.VirA_Psys
GSMPMM2VirA_Qsys | REAL | IOD_GSM_TCP | 4195 | 44195 | PMM2.VirA_Qsys
GSMPMM2VirA_Ssys | REAL | IOD_GSM_TCP | 4197 | 44197 | PMM2.VirA_Ssys
GSMPMM2VirA_Usys | REAL | IOD_GSM_TCP | 4199 | 44199 | PMM2.VirA_Usys
GSMPMM2VirAActiveEnergyConsumed_kWh | REAL | IOD_GSM_TCP | 4201 | 44201 | PMM2.VirAActiveEnergyConsumed_kWh
GSMPMM2VirAActivePowerPhaseA_kW | REAL | IOD_GSM_TCP | 4203 | 44203 | PMM2.VirAActivePowerPhaseA_kW
GSMPMM2VirAActivePowerPhaseB_kW | REAL | IOD_GSM_TCP | 4205 | 44205 | PMM2.VirAActivePowerPhaseB_kW
GSMPMM2VirAActivePowerPhaseC_kW | REAL | IOD_GSM_TCP | 4207 | 44207 | PMM2.VirAActivePowerPhaseC_kW
GSMPMM2VirAAparentPowerPhaseA | REAL | IOD_GSM_TCP | 4209 | 44209 | PMM2.VirAAparentPowerPhaseA
GSMPMM2VirAAparentPowerPhaseB | REAL | IOD_GSM_TCP | 4211 | 44211 | PMM2.VirAAparentPowerPhaseB
GSMPMM2VirAAparentPowerPhaseC | REAL | IOD_GSM_TCP | 4213 | 44213 | PMM2.VirAAparentPowerPhaseC
GSMPMM2VirACurrentInPhaseA_A | REAL | IOD_GSM_TCP | 4215 | 44215 | PMM2.VirACurrentInPhaseA_A
GSMPMM2VirACurrentInPhaseB_A | REAL | IOD_GSM_TCP | 4217 | 44217 | PMM2.VirACurrentInPhaseB_A
GSMPMM2VirACurrentInPhaseC_A | REAL | IOD_GSM_TCP | 4219 | 44219 | PMM2.VirACurrentInPhaseC_A
GSMPMM2VirAReactiveEnergyConsumed_kVARh | REAL | IOD_GSM_TCP | 4221 | 44221 | PMM2.VirAReactiveEnergyConsumed_kVARh
GSMPMM2VirAReactivePowerPhaseA | REAL | IOD_GSM_TCP | 4223 | 44223 | PMM2.VirAReactivePowerPhaseA
GSMPMM2VirAReactivePowerPhaseB | REAL | IOD_GSM_TCP | 4225 | 44225 | PMM2.VirAReactivePowerPhaseB
GSMPMM2VirAReactivePowerPhaseC | REAL | IOD_GSM_TCP | 4227 | 44227 | PMM2.VirAReactivePowerPhaseC
GSMPMM2VirAVoltageBetweenPhaseAB_V | REAL | IOD_GSM_TCP | 4229 | 44229 | PMM2.VirAVoltageBetweenPhaseAB_V
GSMPMM2VirAVoltageBetweenPhaseAN_V | REAL | IOD_GSM_TCP | 4231 | 44231 | PMM2.VirAVoltageBetweenPhaseAN_V
GSMPMM2VirAVoltageBetweenPhaseBC_V | REAL | IOD_GSM_TCP | 4233 | 44233 | PMM2.VirAVoltageBetweenPhaseBC_V
GSMPMM2VirAVoltageBetweenPhaseBN_V | REAL | IOD_GSM_TCP | 4235 | 44235 | PMM2.VirAVoltageBetweenPhaseBN_V
GSMPMM2VirAVoltageBetweenPhaseCA_V | REAL | IOD_GSM_TCP | 4237 | 44237 | PMM2.VirAVoltageBetweenPhaseCA_V
GSMPMM2VirAVoltageBetweenPhaseCN_V | REAL | IOD_GSM_TCP | 4239 | 44239 | PMM2.VirAVoltageBetweenPhaseCN_V
GSMPMM2VirBCurrent10 | REAL | IOD_GSM_TCP | 4241 | 44241 | PMM2.VirB.Current[10]
GSMPMM2VirBCurrent11 | REAL | IOD_GSM_TCP | 4243 | 44243 | PMM2.VirB.Current[11]
GSMPMM2VirBCurrent12 | REAL | IOD_GSM_TCP | 4245 | 44245 | PMM2.VirB.Current[12]
GSMPMM2VirBCurrent13 | REAL | IOD_GSM_TCP | 4247 | 44247 | PMM2.VirB.Current[13]
GSMPMM2VirBCurrent14 | REAL | IOD_GSM_TCP | 4249 | 44249 | PMM2.VirB.Current[14]
GSMPMM2VirBCurrent15 | REAL | IOD_GSM_TCP | 4251 | 44251 | PMM2.VirB.Current[15]
GSMPMM2VirBCurrent16 | REAL | IOD_GSM_TCP | 4253 | 44253 | PMM2.VirB.Current[16]
GSMPMM2VirBCurrent17 | REAL | IOD_GSM_TCP | 4255 | 44255 | PMM2.VirB.Current[17]
GSMPMM2VirBCurrent18 | REAL | IOD_GSM_TCP | 4257 | 44257 | PMM2.VirB.Current[18]
GSMPMM2VirBCurrent19 | REAL | IOD_GSM_TCP | 4259 | 44259 | PMM2.VirB.Current[19]
GSMPMM2VirBCurrent1 | REAL | IOD_GSM_TCP | 4261 | 44261 | PMM2.VirB.Current[1]
GSMPMM2VirBCurrent20 | REAL | IOD_GSM_TCP | 4263 | 44263 | PMM2.VirB.Current[20]
GSMPMM2VirBCurrent21 | REAL | IOD_GSM_TCP | 4265 | 44265 | PMM2.VirB.Current[21]
GSMPMM2VirBCurrent22 | REAL | IOD_GSM_TCP | 4267 | 44267 | PMM2.VirB.Current[22]
GSMPMM2VirBCurrent23 | REAL | IOD_GSM_TCP | 4269 | 44269 | PMM2.VirB.Current[23]
GSMPMM2VirBCurrent24 | REAL | IOD_GSM_TCP | 4271 | 44271 | PMM2.VirB.Current[24]
GSMPMM2VirBCurrent25 | REAL | IOD_GSM_TCP | 4273 | 44273 | PMM2.VirB.Current[25]
GSMPMM2VirBCurrent26 | REAL | IOD_GSM_TCP | 4275 | 44275 | PMM2.VirB.Current[26]
GSMPMM2VirBCurrent27 | REAL | IOD_GSM_TCP | 4277 | 44277 | PMM2.VirB.Current[27]
GSMPMM2VirBCurrent28 | REAL | IOD_GSM_TCP | 4279 | 44279 | PMM2.VirB.Current[28]
GSMPMM2VirBCurrent29 | REAL | IOD_GSM_TCP | 4281 | 44281 | PMM2.VirB.Current[29]
GSMPMM2VirBCurrent2 | REAL | IOD_GSM_TCP | 4283 | 44283 | PMM2.VirB.Current[2]
GSMPMM2VirBCurrent30 | REAL | IOD_GSM_TCP | 4285 | 44285 | PMM2.VirB.Current[30]
GSMPMM2VirBCurrent31 | REAL | IOD_GSM_TCP | 4287 | 44287 | PMM2.VirB.Current[31]
GSMPMM2VirBCurrent32 | REAL | IOD_GSM_TCP | 4289 | 44289 | PMM2.VirB.Current[32]
GSMPMM2VirBCurrent33 | REAL | IOD_GSM_TCP | 4291 | 44291 | PMM2.VirB.Current[33]
GSMPMM2VirBCurrent34 | REAL | IOD_GSM_TCP | 4293 | 44293 | PMM2.VirB.Current[34]
GSMPMM2VirBCurrent35 | REAL | IOD_GSM_TCP | 4295 | 44295 | PMM2.VirB.Current[35]
GSMPMM2VirBCurrent36 | REAL | IOD_GSM_TCP | 4297 | 44297 | PMM2.VirB.Current[36]
GSMPMM2VirBCurrent37 | REAL | IOD_GSM_TCP | 4299 | 44299 | PMM2.VirB.Current[37]
GSMPMM2VirBCurrent38 | REAL | IOD_GSM_TCP | 4301 | 44301 | PMM2.VirB.Current[38]
GSMPMM2VirBCurrent39 | REAL | IOD_GSM_TCP | 4303 | 44303 | PMM2.VirB.Current[39]
GSMPMM2VirBCurrent3 | REAL | IOD_GSM_TCP | 4305 | 44305 | PMM2.VirB.Current[3]
GSMPMM2VirBCurrent40 | REAL | IOD_GSM_TCP | 4307 | 44307 | PMM2.VirB.Current[40]
GSMPMM2VirBCurrent41 | REAL | IOD_GSM_TCP | 4309 | 44309 | PMM2.VirB.Current[41]
GSMPMM2VirBCurrent42 | REAL | IOD_GSM_TCP | 4311 | 44311 | PMM2.VirB.Current[42]
GSMPMM2VirBCurrent43 | REAL | IOD_GSM_TCP | 4313 | 44313 | PMM2.VirB.Current[43]
GSMPMM2VirBCurrent44 | REAL | IOD_GSM_TCP | 4315 | 44315 | PMM2.VirB.Current[44]
GSMPMM2VirBCurrent4 | REAL | IOD_GSM_TCP | 4317 | 44317 | PMM2.VirB.Current[4]
GSMPMM2VirBCurrent5 | REAL | IOD_GSM_TCP | 4319 | 44319 | PMM2.VirB.Current[5]
GSMPMM2VirBCurrent6 | REAL | IOD_GSM_TCP | 4321 | 44321 | PMM2.VirB.Current[6]
GSMPMM2VirBCurrent7 | REAL | IOD_GSM_TCP | 4323 | 44323 | PMM2.VirB.Current[7]
GSMPMM2VirBCurrent8 | REAL | IOD_GSM_TCP | 4325 | 44325 | PMM2.VirB.Current[8]
GSMPMM2VirBCurrent9 | REAL | IOD_GSM_TCP | 4327 | 44327 | PMM2.VirB.Current[9]
GSMPMM2VirB_fsys | REAL | IOD_GSM_TCP | 4329 | 44329 | PMM2.VirB_fsys
GSMPMM2VirB_Isys | REAL | IOD_GSM_TCP | 4331 | 44331 | PMM2.VirB_Isys
GSMPMM2VirB_PFsys | REAL | IOD_GSM_TCP | 4333 | 44333 | PMM2.VirB_PFsys
GSMPMM2VirB_Psys | REAL | IOD_GSM_TCP | 4335 | 44335 | PMM2.VirB_Psys
GSMPMM2VirB_Qsys | REAL | IOD_GSM_TCP | 4337 | 44337 | PMM2.VirB_Qsys
GSMPMM2VirB_Ssys | REAL | IOD_GSM_TCP | 4339 | 44339 | PMM2.VirB_Ssys
GSMPMM2VirB_Usys | REAL | IOD_GSM_TCP | 4341 | 44341 | PMM2.VirB_Usys
GSMPMM2VirBActiveEnergyConsumed_kWh | REAL | IOD_GSM_TCP | 4343 | 44343 | PMM2.VirBActiveEnergyConsumed_kWh
GSMPMM2VirBActivePowerPhaseA_kW | REAL | IOD_GSM_TCP | 4345 | 44345 | PMM2.VirBActivePowerPhaseA_kW
GSMPMM2VirBActivePowerPhaseB_kW | REAL | IOD_GSM_TCP | 4347 | 44347 | PMM2.VirBActivePowerPhaseB_kW
GSMPMM2VirBActivePowerPhaseC_kW | REAL | IOD_GSM_TCP | 4349 | 44349 | PMM2.VirBActivePowerPhaseC_kW
GSMPMM2VirBAparentPowerPhaseA | REAL | IOD_GSM_TCP | 4351 | 44351 | PMM2.VirBAparentPowerPhaseA
GSMPMM2VirBAparentPowerPhaseB | REAL | IOD_GSM_TCP | 4353 | 44353 | PMM2.VirBAparentPowerPhaseB
GSMPMM2VirBAparentPowerPhaseC | REAL | IOD_GSM_TCP | 4355 | 44355 | PMM2.VirBAparentPowerPhaseC
GSMPMM2VirBCurrentInPhaseA_A | REAL | IOD_GSM_TCP | 4357 | 44357 | PMM2.VirBCurrentInPhaseA_A
GSMPMM2VirBCurrentInPhaseB_A | REAL | IOD_GSM_TCP | 4359 | 44359 | PMM2.VirBCurrentInPhaseB_A
GSMPMM2VirBCurrentInPhaseC_A | REAL | IOD_GSM_TCP | 4361 | 44361 | PMM2.VirBCurrentInPhaseC_A
GSMPMM2VirBReactiveEnergyConsumed_kVARh | REAL | IOD_GSM_TCP | 4363 | 44363 | PMM2.VirBReactiveEnergyConsumed_kVARh
GSMPMM2VirBReactivePowerPhaseA | REAL | IOD_GSM_TCP | 4365 | 44365 | PMM2.VirBReactivePowerPhaseA
GSMPMM2VirBReactivePowerPhaseB | REAL | IOD_GSM_TCP | 4367 | 44367 | PMM2.VirBReactivePowerPhaseB
GSMPMM2VirBReactivePowerPhaseC | REAL | IOD_GSM_TCP | 4369 | 44369 | PMM2.VirBReactivePowerPhaseC
GSMPMM2VirBVoltageBetweenPhaseAB_V | REAL | IOD_GSM_TCP | 4371 | 44371 | PMM2.VirBVoltageBetweenPhaseAB_V
GSMPMM2VirBVoltageBetweenPhaseAN_V | REAL | IOD_GSM_TCP | 4373 | 44373 | PMM2.VirBVoltageBetweenPhaseAN_V
GSMPMM2VirBVoltageBetweenPhaseBC_V | REAL | IOD_GSM_TCP | 4375 | 44375 | PMM2.VirBVoltageBetweenPhaseBC_V
GSMPMM2VirBVoltageBetweenPhaseBN_V | REAL | IOD_GSM_TCP | 4377 | 44377 | PMM2.VirBVoltageBetweenPhaseBN_V
GSMPMM2VirBVoltageBetweenPhaseCA_V | REAL | IOD_GSM_TCP | 4379 | 44379 | PMM2.VirBVoltageBetweenPhaseCA_V
GSMPMM2VirBVoltageBetweenPhaseCN_V | REAL | IOD_GSM_TCP | 4381 | 44381 | PMM2.VirBVoltageBetweenPhaseCN_V
GSMPMM1ActiveEnergyConsumed_kWh | REAL | IOD_GSM_TCP | 4383 | 44383 | PMM[1].ActiveEnergyConsumed_kWh
GSMPMM1ActivePowerPhaseA_kW | REAL | IOD_GSM_TCP | 4385 | 44385 | PMM[1].ActivePowerPhaseA_kW
GSMPMM1ActivePowerPhaseB_kW | REAL | IOD_GSM_TCP | 4387 | 44387 | PMM[1].ActivePowerPhaseB_kW
GSMPMM1ActivePowerPhaseC_kW | REAL | IOD_GSM_TCP | 4389 | 44389 | PMM[1].ActivePowerPhaseC_kW
GSMPMM1AparentPowerPhaseA | REAL | IOD_GSM_TCP | 4391 | 44391 | PMM[1].AparentPowerPhaseA
GSMPMM1AparentPowerPhaseB | REAL | IOD_GSM_TCP | 4393 | 44393 | PMM[1].AparentPowerPhaseB
GSMPMM1AparentPowerPhaseC | REAL | IOD_GSM_TCP | 4395 | 44395 | PMM[1].AparentPowerPhaseC
GSMPMM1AverageCurrent_A | REAL | IOD_GSM_TCP | 4397 | 44397 | PMM[1].AverageCurrent_A
GSMPMM1AveragePhaseToNeutral_V | REAL | IOD_GSM_TCP | 4399 | 44399 | PMM[1].AveragePhaseToNeutral_V
GSMPMM1AveragePhaseToPhase_V | REAL | IOD_GSM_TCP | 4401 | 44401 | PMM[1].AveragePhaseToPhase_V
GSMPMM1CurrentInPhaseA_A | REAL | IOD_GSM_TCP | 4403 | 44403 | PMM[1].CurrentInPhaseA_A
GSMPMM1CurrentInPhaseB_A | REAL | IOD_GSM_TCP | 4405 | 44405 | PMM[1].CurrentInPhaseB_A
GSMPMM1CurrentInPhaseC_A | REAL | IOD_GSM_TCP | 4407 | 44407 | PMM[1].CurrentInPhaseC_A
GSMPMM1Frequency_Hz | REAL | IOD_GSM_TCP | 4409 | 44409 | PMM[1].Frequency_Hz
GSMPMM1Phase1Current10 | REAL | IOD_GSM_TCP | 4411 | 44411 | PMM[1].Phase[1].Current[10]
GSMPMM1Phase1Current11 | REAL | IOD_GSM_TCP | 4413 | 44413 | PMM[1].Phase[1].Current[11]
GSMPMM1Phase1Current12 | REAL | IOD_GSM_TCP | 4415 | 44415 | PMM[1].Phase[1].Current[12]
GSMPMM1Phase1Current13 | REAL | IOD_GSM_TCP | 4417 | 44417 | PMM[1].Phase[1].Current[13]
GSMPMM1Phase1Current14 | REAL | IOD_GSM_TCP | 4419 | 44419 | PMM[1].Phase[1].Current[14]
GSMPMM1Phase1Current15 | REAL | IOD_GSM_TCP | 4421 | 44421 | PMM[1].Phase[1].Current[15]
GSMPMM1Phase1Current16 | REAL | IOD_GSM_TCP | 4423 | 44423 | PMM[1].Phase[1].Current[16]
GSMPMM1Phase1Current17 | REAL | IOD_GSM_TCP | 4425 | 44425 | PMM[1].Phase[1].Current[17]
GSMPMM1Phase1Current18 | REAL | IOD_GSM_TCP | 4427 | 44427 | PMM[1].Phase[1].Current[18]
GSMPMM1Phase1Current19 | REAL | IOD_GSM_TCP | 4429 | 44429 | PMM[1].Phase[1].Current[19]
GSMPMM1Phase1Current1 | REAL | IOD_GSM_TCP | 4431 | 44431 | PMM[1].Phase[1].Current[1]
GSMPMM1Phase1Current20 | REAL | IOD_GSM_TCP | 4433 | 44433 | PMM[1].Phase[1].Current[20]
GSMPMM1Phase1Current21 | REAL | IOD_GSM_TCP | 4435 | 44435 | PMM[1].Phase[1].Current[21]
GSMPMM1Phase1Current22 | REAL | IOD_GSM_TCP | 4437 | 44437 | PMM[1].Phase[1].Current[22]
GSMPMM1Phase1Current23 | REAL | IOD_GSM_TCP | 4439 | 44439 | PMM[1].Phase[1].Current[23]
GSMPMM1Phase1Current24 | REAL | IOD_GSM_TCP | 4441 | 44441 | PMM[1].Phase[1].Current[24]
GSMPMM1Phase1Current25 | REAL | IOD_GSM_TCP | 4443 | 44443 | PMM[1].Phase[1].Current[25]
GSMPMM1Phase1Current26 | REAL | IOD_GSM_TCP | 4445 | 44445 | PMM[1].Phase[1].Current[26]
GSMPMM1Phase1Current27 | REAL | IOD_GSM_TCP | 4447 | 44447 | PMM[1].Phase[1].Current[27]
GSMPMM1Phase1Current28 | REAL | IOD_GSM_TCP | 4449 | 44449 | PMM[1].Phase[1].Current[28]
GSMPMM1Phase1Current29 | REAL | IOD_GSM_TCP | 4451 | 44451 | PMM[1].Phase[1].Current[29]
GSMPMM1Phase1Current2 | REAL | IOD_GSM_TCP | 4453 | 44453 | PMM[1].Phase[1].Current[2]
GSMPMM1Phase1Current30 | REAL | IOD_GSM_TCP | 4455 | 44455 | PMM[1].Phase[1].Current[30]
GSMPMM1Phase1Current31 | REAL | IOD_GSM_TCP | 4457 | 44457 | PMM[1].Phase[1].Current[31]
GSMPMM1Phase1Current32 | REAL | IOD_GSM_TCP | 4459 | 44459 | PMM[1].Phase[1].Current[32]
GSMPMM1Phase1Current33 | REAL | IOD_GSM_TCP | 4461 | 44461 | PMM[1].Phase[1].Current[33]
GSMPMM1Phase1Current34 | REAL | IOD_GSM_TCP | 4463 | 44463 | PMM[1].Phase[1].Current[34]
GSMPMM1Phase1Current35 | REAL | IOD_GSM_TCP | 4465 | 44465 | PMM[1].Phase[1].Current[35]
GSMPMM1Phase1Current36 | REAL | IOD_GSM_TCP | 4467 | 44467 | PMM[1].Phase[1].Current[36]
GSMPMM1Phase1Current37 | REAL | IOD_GSM_TCP | 4469 | 44469 | PMM[1].Phase[1].Current[37]
GSMPMM1Phase1Current38 | REAL | IOD_GSM_TCP | 4471 | 44471 | PMM[1].Phase[1].Current[38]
GSMPMM1Phase1Current39 | REAL | IOD_GSM_TCP | 4473 | 44473 | PMM[1].Phase[1].Current[39]
GSMPMM1Phase1Current3 | REAL | IOD_GSM_TCP | 4475 | 44475 | PMM[1].Phase[1].Current[3]
GSMPMM1Phase1Current40 | REAL | IOD_GSM_TCP | 4477 | 44477 | PMM[1].Phase[1].Current[40]
GSMPMM1Phase1Current41 | REAL | IOD_GSM_TCP | 4479 | 44479 | PMM[1].Phase[1].Current[41]
GSMPMM1Phase1Current42 | REAL | IOD_GSM_TCP | 4481 | 44481 | PMM[1].Phase[1].Current[42]
GSMPMM1Phase1Current4 | REAL | IOD_GSM_TCP | 4483 | 44483 | PMM[1].Phase[1].Current[4]
GSMPMM1Phase1Current5 | REAL | IOD_GSM_TCP | 4485 | 44485 | PMM[1].Phase[1].Current[5]
GSMPMM1Phase1Current6 | REAL | IOD_GSM_TCP | 4487 | 44487 | PMM[1].Phase[1].Current[6]
GSMPMM1Phase1Current7 | REAL | IOD_GSM_TCP | 4489 | 44489 | PMM[1].Phase[1].Current[7]
GSMPMM1Phase1Current8 | REAL | IOD_GSM_TCP | 4491 | 44491 | PMM[1].Phase[1].Current[8]
GSMPMM1Phase1Current9 | REAL | IOD_GSM_TCP | 4493 | 44493 | PMM[1].Phase[1].Current[9]
GSMPMM1Phase2Current10 | REAL | IOD_GSM_TCP | 4495 | 44495 | PMM[1].Phase[2].Current[10]
GSMPMM1Phase2Current11 | REAL | IOD_GSM_TCP | 4497 | 44497 | PMM[1].Phase[2].Current[11]
GSMPMM1Phase2Current12 | REAL | IOD_GSM_TCP | 4499 | 44499 | PMM[1].Phase[2].Current[12]
GSMPMM1Phase2Current13 | REAL | IOD_GSM_TCP | 4501 | 44501 | PMM[1].Phase[2].Current[13]
GSMPMM1Phase2Current14 | REAL | IOD_GSM_TCP | 4503 | 44503 | PMM[1].Phase[2].Current[14]
GSMPMM1Phase2Current15 | REAL | IOD_GSM_TCP | 4505 | 44505 | PMM[1].Phase[2].Current[15]
GSMPMM1Phase2Current16 | REAL | IOD_GSM_TCP | 4507 | 44507 | PMM[1].Phase[2].Current[16]
GSMPMM1Phase2Current17 | REAL | IOD_GSM_TCP | 4509 | 44509 | PMM[1].Phase[2].Current[17]
GSMPMM1Phase2Current18 | REAL | IOD_GSM_TCP | 4511 | 44511 | PMM[1].Phase[2].Current[18]
GSMPMM1Phase2Current19 | REAL | IOD_GSM_TCP | 4513 | 44513 | PMM[1].Phase[2].Current[19]
GSMPMM1Phase2Current1 | REAL | IOD_GSM_TCP | 4515 | 44515 | PMM[1].Phase[2].Current[1]
GSMPMM1Phase2Current20 | REAL | IOD_GSM_TCP | 4517 | 44517 | PMM[1].Phase[2].Current[20]
GSMPMM1Phase2Current21 | REAL | IOD_GSM_TCP | 4519 | 44519 | PMM[1].Phase[2].Current[21]
GSMPMM1Phase2Current22 | REAL | IOD_GSM_TCP | 4521 | 44521 | PMM[1].Phase[2].Current[22]
GSMPMM1Phase2Current23 | REAL | IOD_GSM_TCP | 4523 | 44523 | PMM[1].Phase[2].Current[23]
GSMPMM1Phase2Current24 | REAL | IOD_GSM_TCP | 4525 | 44525 | PMM[1].Phase[2].Current[24]
GSMPMM1Phase2Current25 | REAL | IOD_GSM_TCP | 4527 | 44527 | PMM[1].Phase[2].Current[25]
GSMPMM1Phase2Current26 | REAL | IOD_GSM_TCP | 4529 | 44529 | PMM[1].Phase[2].Current[26]
GSMPMM1Phase2Current27 | REAL | IOD_GSM_TCP | 4531 | 44531 | PMM[1].Phase[2].Current[27]
GSMPMM1Phase2Current28 | REAL | IOD_GSM_TCP | 4533 | 44533 | PMM[1].Phase[2].Current[28]
GSMPMM1Phase2Current29 | REAL | IOD_GSM_TCP | 4535 | 44535 | PMM[1].Phase[2].Current[29]
GSMPMM1Phase2Current2 | REAL | IOD_GSM_TCP | 4537 | 44537 | PMM[1].Phase[2].Current[2]
GSMPMM1Phase2Current30 | REAL | IOD_GSM_TCP | 4539 | 44539 | PMM[1].Phase[2].Current[30]
GSMPMM1Phase2Current31 | REAL | IOD_GSM_TCP | 4541 | 44541 | PMM[1].Phase[2].Current[31]
GSMPMM1Phase2Current32 | REAL | IOD_GSM_TCP | 4543 | 44543 | PMM[1].Phase[2].Current[32]
GSMPMM1Phase2Current33 | REAL | IOD_GSM_TCP | 4545 | 44545 | PMM[1].Phase[2].Current[33]
GSMPMM1Phase2Current34 | REAL | IOD_GSM_TCP | 4547 | 44547 | PMM[1].Phase[2].Current[34]
GSMPMM1Phase2Current35 | REAL | IOD_GSM_TCP | 4549 | 44549 | PMM[1].Phase[2].Current[35]
GSMPMM1Phase2Current36 | REAL | IOD_GSM_TCP | 4551 | 44551 | PMM[1].Phase[2].Current[36]
GSMPMM1Phase2Current37 | REAL | IOD_GSM_TCP | 4553 | 44553 | PMM[1].Phase[2].Current[37]
GSMPMM1Phase2Current38 | REAL | IOD_GSM_TCP | 4555 | 44555 | PMM[1].Phase[2].Current[38]
GSMPMM1Phase2Current39 | REAL | IOD_GSM_TCP | 4557 | 44557 | PMM[1].Phase[2].Current[39]
GSMPMM1Phase2Current3 | REAL | IOD_GSM_TCP | 4559 | 44559 | PMM[1].Phase[2].Current[3]
GSMPMM1Phase2Current40 | REAL | IOD_GSM_TCP | 4561 | 44561 | PMM[1].Phase[2].Current[40]
GSMPMM1Phase2Current41 | REAL | IOD_GSM_TCP | 4563 | 44563 | PMM[1].Phase[2].Current[41]
GSMPMM1Phase2Current42 | REAL | IOD_GSM_TCP | 4565 | 44565 | PMM[1].Phase[2].Current[42]
GSMPMM1Phase2Current4 | REAL | IOD_GSM_TCP | 4567 | 44567 | PMM[1].Phase[2].Current[4]
GSMPMM1Phase2Current5 | REAL | IOD_GSM_TCP | 4569 | 44569 | PMM[1].Phase[2].Current[5]
GSMPMM1Phase2Current6 | REAL | IOD_GSM_TCP | 4571 | 44571 | PMM[1].Phase[2].Current[6]
GSMPMM1Phase2Current7 | REAL | IOD_GSM_TCP | 4573 | 44573 | PMM[1].Phase[2].Current[7]
GSMPMM1Phase2Current8 | REAL | IOD_GSM_TCP | 4575 | 44575 | PMM[1].Phase[2].Current[8]
GSMPMM1Phase2Current9 | REAL | IOD_GSM_TCP | 4577 | 44577 | PMM[1].Phase[2].Current[9]
GSMPMM1Phase3Current10 | REAL | IOD_GSM_TCP | 4579 | 44579 | PMM[1].Phase[3].Current[10]
GSMPMM1Phase3Current11 | REAL | IOD_GSM_TCP | 4581 | 44581 | PMM[1].Phase[3].Current[11]
GSMPMM1Phase3Current12 | REAL | IOD_GSM_TCP | 4583 | 44583 | PMM[1].Phase[3].Current[12]
GSMPMM1Phase3Current13 | REAL | IOD_GSM_TCP | 4585 | 44585 | PMM[1].Phase[3].Current[13]
GSMPMM1Phase3Current14 | REAL | IOD_GSM_TCP | 4587 | 44587 | PMM[1].Phase[3].Current[14]
GSMPMM1Phase3Current15 | REAL | IOD_GSM_TCP | 4589 | 44589 | PMM[1].Phase[3].Current[15]
GSMPMM1Phase3Current16 | REAL | IOD_GSM_TCP | 4591 | 44591 | PMM[1].Phase[3].Current[16]
GSMPMM1Phase3Current17 | REAL | IOD_GSM_TCP | 4593 | 44593 | PMM[1].Phase[3].Current[17]
GSMPMM1Phase3Current18 | REAL | IOD_GSM_TCP | 4595 | 44595 | PMM[1].Phase[3].Current[18]
GSMPMM1Phase3Current19 | REAL | IOD_GSM_TCP | 4597 | 44597 | PMM[1].Phase[3].Current[19]
GSMPMM1Phase3Current1 | REAL | IOD_GSM_TCP | 4599 | 44599 | PMM[1].Phase[3].Current[1]
GSMPMM1Phase3Current20 | REAL | IOD_GSM_TCP | 4601 | 44601 | PMM[1].Phase[3].Current[20]
GSMPMM1Phase3Current21 | REAL | IOD_GSM_TCP | 4603 | 44603 | PMM[1].Phase[3].Current[21]
GSMPMM1Phase3Current22 | REAL | IOD_GSM_TCP | 4605 | 44605 | PMM[1].Phase[3].Current[22]
GSMPMM1Phase3Current23 | REAL | IOD_GSM_TCP | 4607 | 44607 | PMM[1].Phase[3].Current[23]
GSMPMM1Phase3Current24 | REAL | IOD_GSM_TCP | 4609 | 44609 | PMM[1].Phase[3].Current[24]
GSMPMM1Phase3Current25 | REAL | IOD_GSM_TCP | 4611 | 44611 | PMM[1].Phase[3].Current[25]
GSMPMM1Phase3Current26 | REAL | IOD_GSM_TCP | 4613 | 44613 | PMM[1].Phase[3].Current[26]
GSMPMM1Phase3Current27 | REAL | IOD_GSM_TCP | 4615 | 44615 | PMM[1].Phase[3].Current[27]
GSMPMM1Phase3Current28 | REAL | IOD_GSM_TCP | 4617 | 44617 | PMM[1].Phase[3].Current[28]
GSMPMM1Phase3Current29 | REAL | IOD_GSM_TCP | 4619 | 44619 | PMM[1].Phase[3].Current[29]
GSMPMM1Phase3Current2 | REAL | IOD_GSM_TCP | 4621 | 44621 | PMM[1].Phase[3].Current[2]
GSMPMM1Phase3Current30 | REAL | IOD_GSM_TCP | 4623 | 44623 | PMM[1].Phase[3].Current[30]
GSMPMM1Phase3Current31 | REAL | IOD_GSM_TCP | 4625 | 44625 | PMM[1].Phase[3].Current[31]
GSMPMM1Phase3Current32 | REAL | IOD_GSM_TCP | 4627 | 44627 | PMM[1].Phase[3].Current[32]
GSMPMM1Phase3Current33 | REAL | IOD_GSM_TCP | 4629 | 44629 | PMM[1].Phase[3].Current[33]
GSMPMM1Phase3Current34 | REAL | IOD_GSM_TCP | 4631 | 44631 | PMM[1].Phase[3].Current[34]
GSMPMM1Phase3Current35 | REAL | IOD_GSM_TCP | 4633 | 44633 | PMM[1].Phase[3].Current[35]
GSMPMM1Phase3Current36 | REAL | IOD_GSM_TCP | 4635 | 44635 | PMM[1].Phase[3].Current[36]
GSMPMM1Phase3Current37 | REAL | IOD_GSM_TCP | 4637 | 44637 | PMM[1].Phase[3].Current[37]
GSMPMM1Phase3Current38 | REAL | IOD_GSM_TCP | 4639 | 44639 | PMM[1].Phase[3].Current[38]
GSMPMM1Phase3Current39 | REAL | IOD_GSM_TCP | 4641 | 44641 | PMM[1].Phase[3].Current[39]
GSMPMM1Phase3Current3 | REAL | IOD_GSM_TCP | 4643 | 44643 | PMM[1].Phase[3].Current[3]
GSMPMM1Phase3Current40 | REAL | IOD_GSM_TCP | 4645 | 44645 | PMM[1].Phase[3].Current[40]
GSMPMM1Phase3Current41 | REAL | IOD_GSM_TCP | 4647 | 44647 | PMM[1].Phase[3].Current[41]
GSMPMM1Phase3Current42 | REAL | IOD_GSM_TCP | 4649 | 44649 | PMM[1].Phase[3].Current[42]
GSMPMM1Phase3Current4 | REAL | IOD_GSM_TCP | 4651 | 44651 | PMM[1].Phase[3].Current[4]
GSMPMM1Phase3Current5 | REAL | IOD_GSM_TCP | 4653 | 44653 | PMM[1].Phase[3].Current[5]
GSMPMM1Phase3Current6 | REAL | IOD_GSM_TCP | 4655 | 44655 | PMM[1].Phase[3].Current[6]
GSMPMM1Phase3Current7 | REAL | IOD_GSM_TCP | 4657 | 44657 | PMM[1].Phase[3].Current[7]
GSMPMM1Phase3Current8 | REAL | IOD_GSM_TCP | 4659 | 44659 | PMM[1].Phase[3].Current[8]
GSMPMM1Phase3Current9 | REAL | IOD_GSM_TCP | 4661 | 44661 | PMM[1].Phase[3].Current[9]
GSMPMM1PowerFactorSys | REAL | IOD_GSM_TCP | 4663 | 44663 | PMM[1].PowerFactorSys
GSMPMM1ReactiveEnergyConsumed_kVARh | REAL | IOD_GSM_TCP | 4665 | 44665 | PMM[1].ReactiveEnergyConsumed_kVARh
GSMPMM1ReactivePowerPhaseA | REAL | IOD_GSM_TCP | 4667 | 44667 | PMM[1].ReactivePowerPhaseA
GSMPMM1ReactivePowerPhaseB | REAL | IOD_GSM_TCP | 4669 | 44669 | PMM[1].ReactivePowerPhaseB
GSMPMM1ReactivePowerPhaseC | REAL | IOD_GSM_TCP | 4671 | 44671 | PMM[1].ReactivePowerPhaseC
GSMPMM1TotalActivePower_kW | REAL | IOD_GSM_TCP | 4673 | 44673 | PMM[1].TotalActivePower_kW
GSMPMM1TotalAparentPower_kVA | REAL | IOD_GSM_TCP | 4675 | 44675 | PMM[1].TotalAparentPower_kVA
GSMPMM1TotalPowerFactor | REAL | IOD_GSM_TCP | 4677 | 44677 | PMM[1].TotalPowerFactor
GSMPMM1TotalReactivePower_kVAR | REAL | IOD_GSM_TCP | 4679 | 44679 | PMM[1].TotalReactivePower_kVAR
GSMPMM1VirA_fsys | REAL | IOD_GSM_TCP | 4681 | 44681 | PMM[1].VirA_fsys
GSMPMM1VirA_Isys | REAL | IOD_GSM_TCP | 4683 | 44683 | PMM[1].VirA_Isys
GSMPMM1VirA_PFsys | REAL | IOD_GSM_TCP | 4685 | 44685 | PMM[1].VirA_PFsys
GSMPMM1VirA_Psys | REAL | IOD_GSM_TCP | 4687 | 44687 | PMM[1].VirA_Psys
GSMPMM1VirA_Qsys | REAL | IOD_GSM_TCP | 4689 | 44689 | PMM[1].VirA_Qsys
GSMPMM1VirA_Ssys | REAL | IOD_GSM_TCP | 4691 | 44691 | PMM[1].VirA_Ssys
GSMPMM1VirA_Usys | REAL | IOD_GSM_TCP | 4693 | 44693 | PMM[1].VirA_Usys
GSMPMM1VirB_fsys | REAL | IOD_GSM_TCP | 4695 | 44695 | PMM[1].VirB_fsys
GSMPMM1VirB_Isys | REAL | IOD_GSM_TCP | 4697 | 44697 | PMM[1].VirB_Isys
GSMPMM1VirB_PFsys | REAL | IOD_GSM_TCP | 4699 | 44699 | PMM[1].VirB_PFsys
GSMPMM1VirB_Psys | REAL | IOD_GSM_TCP | 4701 | 44701 | PMM[1].VirB_Psys
GSMPMM1VirB_Qsys | REAL | IOD_GSM_TCP | 4703 | 44703 | PMM[1].VirB_Qsys
GSMPMM1VirB_Ssys | REAL | IOD_GSM_TCP | 4705 | 44705 | PMM[1].VirB_Ssys
GSMPMM1VirB_Usys | REAL | IOD_GSM_TCP | 4707 | 44707 | PMM[1].VirB_Usys
GSMPMM1VirBActiveEnergyConsumed_kWh | REAL | IOD_GSM_TCP | 4709 | 44709 | PMM[1].VirBActiveEnergyConsumed_kWh
GSMPMM1VirBActivePowerPhaseA_kW | REAL | IOD_GSM_TCP | 4711 | 44711 | PMM[1].VirBActivePowerPhaseA_kW
GSMPMM1VirBActivePowerPhaseB_kW | REAL | IOD_GSM_TCP | 4713 | 44713 | PMM[1].VirBActivePowerPhaseB_kW
GSMPMM1VirBActivePowerPhaseC_kW | REAL | IOD_GSM_TCP | 4715 | 44715 | PMM[1].VirBActivePowerPhaseC_kW
GSMPMM1VirBAparentPowerPhaseA | REAL | IOD_GSM_TCP | 4717 | 44717 | PMM[1].VirBAparentPowerPhaseA
GSMPMM1VirBAparentPowerPhaseB | REAL | IOD_GSM_TCP | 4719 | 44719 | PMM[1].VirBAparentPowerPhaseB
GSMPMM1VirBAparentPowerPhaseC | REAL | IOD_GSM_TCP | 4721 | 44721 | PMM[1].VirBAparentPowerPhaseC
GSMPMM1VirBAverageCurrent_A | REAL | IOD_GSM_TCP | 4723 | 44723 | PMM[1].VirBAverageCurrent_A
GSMPMM1VirBAveragePhaseToNeutral_V | REAL | IOD_GSM_TCP | 4725 | 44725 | PMM[1].VirBAveragePhaseToNeutral_V
GSMPMM1VirBAveragePhaseToPhase_V | REAL | IOD_GSM_TCP | 4727 | 44727 | PMM[1].VirBAveragePhaseToPhase_V
GSMPMM1VirBCurrentInPhaseA_A | REAL | IOD_GSM_TCP | 4729 | 44729 | PMM[1].VirBCurrentInPhaseA_A
GSMPMM1VirBCurrentInPhaseB_A | REAL | IOD_GSM_TCP | 4731 | 44731 | PMM[1].VirBCurrentInPhaseB_A
GSMPMM1VirBCurrentInPhaseC_A | REAL | IOD_GSM_TCP | 4733 | 44733 | PMM[1].VirBCurrentInPhaseC_A
GSMPMM1VirBFrequency_Hz | REAL | IOD_GSM_TCP | 4735 | 44735 | PMM[1].VirBFrequency_Hz
GSMPMM1VirBPowerFactorSys | REAL | IOD_GSM_TCP | 4737 | 44737 | PMM[1].VirBPowerFactorSys
GSMPMM1VirBReactiveEnergyConsumed_kVARh | REAL | IOD_GSM_TCP | 4739 | 44739 | PMM[1].VirBReactiveEnergyConsumed_kVARh
GSMPMM1VirBReactivePowerPhaseA | REAL | IOD_GSM_TCP | 4741 | 44741 | PMM[1].VirBReactivePowerPhaseA
GSMPMM1VirBReactivePowerPhaseB | REAL | IOD_GSM_TCP | 4743 | 44743 | PMM[1].VirBReactivePowerPhaseB
GSMPMM1VirBReactivePowerPhaseC | REAL | IOD_GSM_TCP | 4745 | 44745 | PMM[1].VirBReactivePowerPhaseC
GSMPMM1VirBTotalActivePower_kW | REAL | IOD_GSM_TCP | 4747 | 44747 | PMM[1].VirBTotalActivePower_kW
GSMPMM1VirBTotalAparentPower_kVA | REAL | IOD_GSM_TCP | 4749 | 44749 | PMM[1].VirBTotalAparentPower_kVA
GSMPMM1VirBTotalPowerFactor | REAL | IOD_GSM_TCP | 4751 | 44751 | PMM[1].VirBTotalPowerFactor
GSMPMM1VirBTotalReactivePower_kVAR | REAL | IOD_GSM_TCP | 4753 | 44753 | PMM[1].VirBTotalReactivePower_kVAR
GSMPMM1VirBVoltageBetweenPhaseAB_V | REAL | IOD_GSM_TCP | 4755 | 44755 | PMM[1].VirBVoltageBetweenPhaseAB_V
GSMPMM1VirBVoltageBetweenPhaseAN_V | REAL | IOD_GSM_TCP | 4757 | 44757 | PMM[1].VirBVoltageBetweenPhaseAN_V
GSMPMM1VirBVoltageBetweenPhaseBC_V | REAL | IOD_GSM_TCP | 4759 | 44759 | PMM[1].VirBVoltageBetweenPhaseBC_V
GSMPMM1VirBVoltageBetweenPhaseBN_V | REAL | IOD_GSM_TCP | 4761 | 44761 | PMM[1].VirBVoltageBetweenPhaseBN_V
GSMPMM1VirBVoltageBetweenPhaseCA_V | REAL | IOD_GSM_TCP | 4763 | 44763 | PMM[1].VirBVoltageBetweenPhaseCA_V
GSMPMM1VirBVoltageBetweenPhaseCN_V | REAL | IOD_GSM_TCP | 4765 | 44765 | PMM[1].VirBVoltageBetweenPhaseCN_V
GSMPMM1VoltageBetweenPhaseAB_V | REAL | IOD_GSM_TCP | 4767 | 44767 | PMM[1].VoltageBetweenPhaseAB_V
GSMPMM1VoltageBetweenPhaseAN_V | REAL | IOD_GSM_TCP | 4769 | 44769 | PMM[1].VoltageBetweenPhaseAN_V
GSMPMM1VoltageBetweenPhaseBC_V | REAL | IOD_GSM_TCP | 4771 | 44771 | PMM[1].VoltageBetweenPhaseBC_V
GSMPMM1VoltageBetweenPhaseBN_V | REAL | IOD_GSM_TCP | 4773 | 44773 | PMM[1].VoltageBetweenPhaseBN_V
GSMPMM1VoltageBetweenPhaseCA_V | REAL | IOD_GSM_TCP | 4775 | 44775 | PMM[1].VoltageBetweenPhaseCA_V
GSMPMM1VoltageBetweenPhaseCN_V | REAL | IOD_GSM_TCP | 4777 | 44777 | PMM[1].VoltageBetweenPhaseCN_V
GSMPMMfaza01 | REAL | IOD_GSM_TCP | 4779 | 44779 | PMMfaza01
GSMPMMfaza02 | REAL | IOD_GSM_TCP | 4781 | 44781 | PMMfaza02
GSMPMMfaza03 | REAL | IOD_GSM_TCP | 4783 | 44783 | PMMfaza03
GSMPMMfaza04 | REAL | IOD_GSM_TCP | 4785 | 44785 | PMMfaza04
GSMPMMfaza05 | REAL | IOD_GSM_TCP | 4787 | 44787 | PMMfaza05
GSMPMMfaza06 | REAL | IOD_GSM_TCP | 4789 | 44789 | PMMfaza06
GSMPMMfaza07 | REAL | IOD_GSM_TCP | 4791 | 44791 | PMMfaza07
GSMPMMfaza08 | REAL | IOD_GSM_TCP | 4793 | 44793 | PMMfaza08
GSMPMMfaza09 | REAL | IOD_GSM_TCP | 4795 | 44795 | PMMfaza09
GSMPMMfaza10 | REAL | IOD_GSM_TCP | 4797 | 44797 | PMMfaza10
GSMPMMfaza11 | REAL | IOD_GSM_TCP | 4799 | 44799 | PMMfaza11
GSMPMMfaza12 | REAL | IOD_GSM_TCP | 4801 | 44801 | PMMfaza12
GSMPMMfaza13 | REAL | IOD_GSM_TCP | 4803 | 44803 | PMMfaza13
GSMPMMfaza14 | REAL | IOD_GSM_TCP | 4805 | 44805 | PMMfaza14
GSMPMMfaza15 | REAL | IOD_GSM_TCP | 4807 | 44807 | PMMfaza15
GSMPMMfaza16 | REAL | IOD_GSM_TCP | 4809 | 44809 | PMMfaza16
GSMPMMfaza17 | REAL | IOD_GSM_TCP | 4811 | 44811 | PMMfaza17
GSMPMMfaza18 | REAL | IOD_GSM_TCP | 4813 | 44813 | PMMfaza18
GSMPMMfaza19 | REAL | IOD_GSM_TCP | 4815 | 44815 | PMMfaza19
GSMPMMfaza20 | REAL | IOD_GSM_TCP | 4817 | 44817 | PMMfaza20
GSMPMMfaza21 | REAL | IOD_GSM_TCP | 4819 | 44819 | PMMfaza21
GSMPMMfaza22 | REAL | IOD_GSM_TCP | 4821 | 44821 | PMMfaza22
GSMPMMfaza23 | REAL | IOD_GSM_TCP | 4823 | 44823 | PMMfaza23
GSMPMMfaza24 | REAL | IOD_GSM_TCP | 4825 | 44825 | PMMfaza24
GSMPMMfaza25 | REAL | IOD_GSM_TCP | 4827 | 44827 | PMMfaza25
GSMPMMfaza26 | REAL | IOD_GSM_TCP | 4829 | 44829 | PMMfaza26
GSMPMMfaza27 | REAL | IOD_GSM_TCP | 4831 | 44831 | PMMfaza27
GSMPMMfaza28 | REAL | IOD_GSM_TCP | 4833 | 44833 | PMMfaza28
GSMPMMfaza29 | REAL | IOD_GSM_TCP | 4835 | 44835 | PMMfaza29
GSMPMMfaza30 | REAL | IOD_GSM_TCP | 4837 | 44837 | PMMfaza30
GSMPMMfaza31 | REAL | IOD_GSM_TCP | 4839 | 44839 | PMMfaza31
GSMPMMfaza32 | REAL | IOD_GSM_TCP | 4841 | 44841 | PMMfaza32
GSMPMMfaza33 | REAL | IOD_GSM_TCP | 4843 | 44843 | PMMfaza33
GSMPMMfaza34 | REAL | IOD_GSM_TCP | 4845 | 44845 | PMMfaza34
GSMPMMfaza35 | REAL | IOD_GSM_TCP | 4847 | 44847 | PMMfaza35
GSMPMMfaza36 | REAL | IOD_GSM_TCP | 4849 | 44849 | PMMfaza36
GSMPMMfaza37 | REAL | IOD_GSM_TCP | 4851 | 44851 | PMMfaza37
GSMPMMfaza38 | REAL | IOD_GSM_TCP | 4853 | 44853 | PMMfaza38
GSMPMMfaza39 | REAL | IOD_GSM_TCP | 4855 | 44855 | PMMfaza39
GSMPMMfaza40 | REAL | IOD_GSM_TCP | 4857 | 44857 | PMMfaza40
GSMPMMfaza41 | REAL | IOD_GSM_TCP | 4859 | 44859 | PMMfaza41
GSMPMMfaza42 | REAL | IOD_GSM_TCP | 4861 | 44861 | PMMfaza42
GSMPMMskupniTokA | REAL | IOD_GSM_TCP | 4863 | 44863 | PMMskupniTokA
GSMPMMskupniTokB | REAL | IOD_GSM_TCP | 4865 | 44865 | PMMskupniTokB
GSMUPS1EstimatedChargeRemaining | REAL | IOD_GSM_TCP | 4867 | 44867 | UPS[1].EstimatedChargeRemaining
GSMUPS1EstimatedMinutesRemaining | REAL | IOD_GSM_TCP | 4869 | 44869 | UPS[1].EstimatedMinutesRemaining
GSMUPS1IzhodMocL1 | REAL | IOD_GSM_TCP | 4871 | 44871 | UPS[1].IzhodMocL1
GSMUPS1IzhodMocL2 | REAL | IOD_GSM_TCP | 4873 | 44873 | UPS[1].IzhodMocL2
GSMUPS1IzhodMocL3 | REAL | IOD_GSM_TCP | 4875 | 44875 | UPS[1].IzhodMocL3
GSMUPS1NapetostBaterije | REAL | IOD_GSM_TCP | 4877 | 44877 | UPS[1].NapetostBaterije
GSMUPS1TemperaturaBaterije | REAL | IOD_GSM_TCP | 4879 | 44879 | UPS[1].TemperaturaBaterije
GSMUPS1VhodFrekvencaL1 | REAL | IOD_GSM_TCP | 4881 | 44881 | UPS[1].VhodFrekvencaL1
GSMUPS1VhodFrekvencaL2 | REAL | IOD_GSM_TCP | 4883 | 44883 | UPS[1].VhodFrekvencaL2
GSMUPS1VhodFrekvencaL3 | REAL | IOD_GSM_TCP | 4885 | 44885 | UPS[1].VhodFrekvencaL3
GSMUPS1VhodNapetostL1 | REAL | IOD_GSM_TCP | 4887 | 44887 | UPS[1].VhodNapetostL1
GSMUPS1VhodNapetostL2 | REAL | IOD_GSM_TCP | 4889 | 44889 | UPS[1].VhodNapetostL2
GSMUPS1VhodNapetostL3 | REAL | IOD_GSM_TCP | 4891 | 44891 | UPS[1].VhodNapetostL3
GSMUPS2EstimatedChargeRemaining | REAL | IOD_GSM_TCP | 4893 | 44893 | UPS[2].EstimatedChargeRemaining
GSMUPS2EstimatedMinutesRemaining | REAL | IOD_GSM_TCP | 4895 | 44895 | UPS[2].EstimatedMinutesRemaining
GSMUPS2IzhodMocL1 | REAL | IOD_GSM_TCP | 4897 | 44897 | UPS[2].IzhodMocL1
GSMUPS2IzhodMocL2 | REAL | IOD_GSM_TCP | 4899 | 44899 | UPS[2].IzhodMocL2
GSMUPS2IzhodMocL3 | REAL | IOD_GSM_TCP | 4901 | 44901 | UPS[2].IzhodMocL3
GSMUPS2NapetostBaterije | REAL | IOD_GSM_TCP | 4903 | 44903 | UPS[2].NapetostBaterije
GSMUPS2TemperaturaBaterije | REAL | IOD_GSM_TCP | 4905 | 44905 | UPS[2].TemperaturaBaterije
GSMUPS2VhodFrekvencaL1 | REAL | IOD_GSM_TCP | 4907 | 44907 | UPS[2].VhodFrekvencaL1
GSMUPS2VhodFrekvencaL2 | REAL | IOD_GSM_TCP | 4909 | 44909 | UPS[2].VhodFrekvencaL2
GSMUPS2VhodFrekvencaL3 | REAL | IOD_GSM_TCP | 4911 | 44911 | UPS[2].VhodFrekvencaL3
GSMUPS2VhodNapetostL1 | REAL | IOD_GSM_TCP | 4913 | 44913 | UPS[2].VhodNapetostL1
GSMUPS2VhodNapetostL2 | REAL | IOD_GSM_TCP | 4915 | 44915 | UPS[2].VhodNapetostL2
GSMUPS2VhodNapetostL3 | REAL | IOD_GSM_TCP | 4917 | 44917 | UPS[2].VhodNapetostL3
GSMUPS3EstimatedChargeRemaining | REAL | IOD_GSM_TCP | 4919 | 44919 | UPS[3].EstimatedChargeRemaining
GSMUPS3EstimatedMinutesRemaining | REAL | IOD_GSM_TCP | 4921 | 44921 | UPS[3].EstimatedMinutesRemaining
GSMUPS3IzhodMocL1 | REAL | IOD_GSM_TCP | 4923 | 44923 | UPS[3].IzhodMocL1
GSMUPS3IzhodMocL2 | REAL | IOD_GSM_TCP | 4925 | 44925 | UPS[3].IzhodMocL2
GSMUPS3IzhodMocL3 | REAL | IOD_GSM_TCP | 4927 | 44927 | UPS[3].IzhodMocL3
GSMUPS3NapetostBaterije | REAL | IOD_GSM_TCP | 4929 | 44929 | UPS[3].NapetostBaterije
GSMUPS3TemperaturaBaterije | REAL | IOD_GSM_TCP | 4931 | 44931 | UPS[3].TemperaturaBaterije
GSMUPS3VhodFrekvencaL1 | REAL | IOD_GSM_TCP | 4933 | 44933 | UPS[3].VhodFrekvencaL1
GSMUPS3VhodFrekvencaL2 | REAL | IOD_GSM_TCP | 4935 | 44935 | UPS[3].VhodFrekvencaL2
GSMUPS3VhodFrekvencaL3 | REAL | IOD_GSM_TCP | 4937 | 44937 | UPS[3].VhodFrekvencaL3
GSMUPS3VhodNapetostL1 | REAL | IOD_GSM_TCP | 4939 | 44939 | UPS[3].VhodNapetostL1
GSMUPS3VhodNapetostL2 | REAL | IOD_GSM_TCP | 4941 | 44941 | UPS[3].VhodNapetostL2
GSMUPS3VhodNapetostL3 | REAL | IOD_GSM_TCP | 4943 | 44943 | UPS[3].VhodNapetostL3
GSMcas_modbus_izpad | STRING | IOD_GSM_TCP | 5001 | 45001[15] | cas_modbus_izpad
GSMDate_Time0 | STRING | IOD_GSM_TCP | 5016 | 45016[15] | Date_Time[0]
GSMDate_Time1 | STRING | IOD_GSM_TCP | 5031 | 45031[15] | Date_Time[1]
GSMDate_Time2 | STRING | IOD_GSM_TCP | 5046 | 45046[15] | Date_Time[2]
GSMDate_Time3 | STRING | IOD_GSM_TCP | 5061 | 45061[15] | Date_Time[3]
GSMK1obrat_ure | STRING | IOD_GSM_TCP | 5076 | 45076[15] | K1obrat_ure
GSMUserCurrentName | STRING | IOD_GSM_TCP | 5091 | 45091[15] | UserCurrentName
GSMUserDisplay | STRING | IOD_GSM_TCP | 5106 | 45106[15] | UserDisplay
GSMK1_obr_u_skupno | UINT | IOD_GSM_TCP | 6001 | 46001 | K1_obr_u_skupno
GSMK2_obr_u_skupno | UINT | IOD_GSM_TCP | 6002 | 46002 | K2_obr_u_skupno
GSMPMM2VirAAlarmPhaseC01_16_60to80 | UINT | IOD_GSM_TCP | 6003 | 46003 | PMM2.VirAAlarmPhase.C01_16_60to80
GSMPMM2VirAAlarmPhaseC01_16_over80 | UINT | IOD_GSM_TCP | 6004 | 46004 | PMM2.VirAAlarmPhase.C01_16_over80
GSMPMM2VirAAlarmPhaseC17_32_60to80 | UINT | IOD_GSM_TCP | 6005 | 46005 | PMM2.VirAAlarmPhase.C17_32_60to80
GSMPMM2VirAAlarmPhaseC17_32_over80 | UINT | IOD_GSM_TCP | 6006 | 46006 | PMM2.VirAAlarmPhase.C17_32_over80
GSMPMM2VirAAlarmPhaseC33_44_60to80 | UINT | IOD_GSM_TCP | 6007 | 46007 | PMM2.VirAAlarmPhase.C33_44_60to80
GSMPMM2VirAAlarmPhaseC33_44_over80 | UINT | IOD_GSM_TCP | 6008 | 46008 | PMM2.VirAAlarmPhase.C33_44_over80
GSMPMM2VirBAlarmPhaseC01_16_60to80 | UINT | IOD_GSM_TCP | 6009 | 46009 | PMM2.VirBAlarmPhase.C01_16_60to80
GSMPMM2VirBAlarmPhaseC01_16_over80 | UINT | IOD_GSM_TCP | 6010 | 46010 | PMM2.VirBAlarmPhase.C01_16_over80
GSMPMM2VirBAlarmPhaseC17_32_60to80 | UINT | IOD_GSM_TCP | 6011 | 46011 | PMM2.VirBAlarmPhase.C17_32_60to80
GSMPMM2VirBAlarmPhaseC17_32_over80 | UINT | IOD_GSM_TCP | 6012 | 46012 | PMM2.VirBAlarmPhase.C17_32_over80
GSMPMM2VirBAlarmPhaseC33_44_60to80 | UINT | IOD_GSM_TCP | 6013 | 46013 | PMM2.VirBAlarmPhase.C33_44_60to80
GSMPMM2VirBAlarmPhaseC33_44_over80 | UINT | IOD_GSM_TCP | 6014 | 46014 | PMM2.VirBAlarmPhase.C33_44_over80
GSMPMM1AlarmPhase1C01_16_60to80 | UINT | IOD_GSM_TCP | 6015 | 46015 | PMM[1].AlarmPhase[1].C01_16_60to80
GSMPMM1AlarmPhase1C01_16_over80 | UINT | IOD_GSM_TCP | 6016 | 46016 | PMM[1].AlarmPhase[1].C01_16_over80
GSMPMM1AlarmPhase1C17_32_60to80 | UINT | IOD_GSM_TCP | 6017 | 46017 | PMM[1].AlarmPhase[1].C17_32_60to80
GSMPMM1AlarmPhase1C17_32_over80 | UINT | IOD_GSM_TCP | 6018 | 46018 | PMM[1].AlarmPhase[1].C17_32_over80
GSMPMM1AlarmPhase1C33_42_60to80 | UINT | IOD_GSM_TCP | 6019 | 46019 | PMM[1].AlarmPhase[1].C33_42_60to80
GSMPMM1AlarmPhase1C33_42_over80 | UINT | IOD_GSM_TCP | 6020 | 46020 | PMM[1].AlarmPhase[1].C33_42_over80
GSMPMM1AlarmPhase2C01_16_60to80 | UINT | IOD_GSM_TCP | 6021 | 46021 | PMM[1].AlarmPhase[2].C01_16_60to80
GSMPMM1AlarmPhase2C01_16_over80 | UINT | IOD_GSM_TCP | 6022 | 46022 | PMM[1].AlarmPhase[2].C01_16_over80
GSMPMM1AlarmPhase2C17_32_60to80 | UINT | IOD_GSM_TCP | 6023 | 46023 | PMM[1].AlarmPhase[2].C17_32_60to80
GSMPMM1AlarmPhase2C17_32_over80 | UINT | IOD_GSM_TCP | 6024 | 46024 | PMM[1].AlarmPhase[2].C17_32_over80
GSMPMM1AlarmPhase2C33_42_60to80 | UINT | IOD_GSM_TCP | 6025 | 46025 | PMM[1].AlarmPhase[2].C33_42_60to80
GSMPMM1AlarmPhase2C33_42_over80 | UINT | IOD_GSM_TCP | 6026 | 46026 | PMM[1].AlarmPhase[2].C33_42_over80
GSMPMM1AlarmPhase3C01_16_60to80 | UINT | IOD_GSM_TCP | 6027 | 46027 | PMM[1].AlarmPhase[3].C01_16_60to80
GSMPMM1AlarmPhase3C01_16_over80 | UINT | IOD_GSM_TCP | 6028 | 46028 | PMM[1].AlarmPhase[3].C01_16_over80
GSMPMM1AlarmPhase3C17_32_60to80 | UINT | IOD_GSM_TCP | 6029 | 46029 | PMM[1].AlarmPhase[3].C17_32_60to80
GSMPMM1AlarmPhase3C17_32_over80 | UINT | IOD_GSM_TCP | 6030 | 46030 | PMM[1].AlarmPhase[3].C17_32_over80
GSMPMM1AlarmPhase3C33_42_60to80 | UINT | IOD_GSM_TCP | 6031 | 46031 | PMM[1].AlarmPhase[3].C33_42_60to80
GSMPMM1AlarmPhase3C33_42_over80 | UINT | IOD_GSM_TCP | 6032 | 46032 | PMM[1].AlarmPhase[3].C33_42_over80
GSMUPS1_StatusBaterije | UINT | IOD_GSM_TCP | 6033 | 46033 | UPS1_StatusBaterije
GSMUPS2_StatusBaterije | UINT | IOD_GSM_TCP | 6034 | 46034 | UPS2_StatusBaterije
GSMUPS3_StatusBaterije | UINT | IOD_GSM_TCP | 6035 | 46035 | UPS3_StatusBaterije
GSMUPS1StatusBaterije | UINT | IOD_GSM_TCP | 6036 | 46036 | UPS[1].StatusBaterije
GSMUPS2StatusBaterije | UINT | IOD_GSM_TCP | 6037 | 46037 | UPS[2].StatusBaterije
GSMUPS3StatusBaterije | UINT | IOD_GSM_TCP | 6038 | 46038 | UPS[3].StatusBaterije

## variable_new
GSMAGR_Gasenje_alarm | DIGITAL | IOD_GSM_TCP | 00001
GSMAGR_PozCent_napaka | DIGITAL | IOD_GSM_TCP | 00002
GSMAGR_PozSenzor_okvara | DIGITAL | IOD_GSM_TCP | 00003
GSMAlarmGenUPS_A_V23 | DIGITAL | IOD_GSM_TCP | 00004
GSMAlarmGenUPS_V23 | DIGITAL | IOD_GSM_TCP | 00005
GSMAlarmGenUPS_V25 | DIGITAL | IOD_GSM_TCP | 00006
GSMAlarmPMM1VirATokPrevisok | DIGITAL | IOD_GSM_TCP | 00007
GSMAlarmPMM1VirATokVisok | DIGITAL | IOD_GSM_TCP | 00008
GSMAlarmPMM1VirBTokPrevisok | DIGITAL | IOD_GSM_TCP | 00009
GSMAlarmPMM1VirBTokVisok | DIGITAL | IOD_GSM_TCP | 00010
GSMAlarmPMM2x17nad8010 | DIGITAL | IOD_GSM_TCP | 00011
GSMAlarmPMM2x17nad8011 | DIGITAL | IOD_GSM_TCP | 00012
GSMAlarmPMM2x17nad8012 | DIGITAL | IOD_GSM_TCP | 00013
GSMAlarmPMM2x17nad8013 | DIGITAL | IOD_GSM_TCP | 00014
GSMAlarmPMM2x17nad8014 | DIGITAL | IOD_GSM_TCP | 00015
GSMAlarmPMM2x17nad8015 | DIGITAL | IOD_GSM_TCP | 00016
GSMAlarmPMM2x17nad8016 | DIGITAL | IOD_GSM_TCP | 00017
GSMAlarmPMM2x17nad8017 | DIGITAL | IOD_GSM_TCP | 00018
GSMAlarmPMM2x17nad8018 | DIGITAL | IOD_GSM_TCP | 00019
GSMAlarmPMM2x17nad8019 | DIGITAL | IOD_GSM_TCP | 00020
GSMAlarmPMM2x17nad801 | DIGITAL | IOD_GSM_TCP | 00021
GSMAlarmPMM2x17nad8020 | DIGITAL | IOD_GSM_TCP | 00022
GSMAlarmPMM2x17nad8021 | DIGITAL | IOD_GSM_TCP | 00023
GSMAlarmPMM2x17nad8022 | DIGITAL | IOD_GSM_TCP | 00024
GSMAlarmPMM2x17nad8023 | DIGITAL | IOD_GSM_TCP | 00025
GSMAlarmPMM2x17nad8024 | DIGITAL | IOD_GSM_TCP | 00026
GSMAlarmPMM2x17nad8025 | DIGITAL | IOD_GSM_TCP | 00027
GSMAlarmPMM2x17nad8026 | DIGITAL | IOD_GSM_TCP | 00028
GSMAlarmPMM2x17nad8027 | DIGITAL | IOD_GSM_TCP | 00029
GSMAlarmPMM2x17nad8028 | DIGITAL | IOD_GSM_TCP | 00030
GSMAlarmPMM2x17nad8029 | DIGITAL | IOD_GSM_TCP | 00031
GSMAlarmPMM2x17nad802 | DIGITAL | IOD_GSM_TCP | 00032
GSMAlarmPMM2x17nad8030 | DIGITAL | IOD_GSM_TCP | 00033
GSMAlarmPMM2x17nad8031 | DIGITAL | IOD_GSM_TCP | 00034
GSMAlarmPMM2x17nad8032 | DIGITAL | IOD_GSM_TCP | 00035
GSMAlarmPMM2x17nad8033 | DIGITAL | IOD_GSM_TCP | 00036
GSMAlarmPMM2x17nad8034 | DIGITAL | IOD_GSM_TCP | 00037
GSMAlarmPMM2x17nad8035 | DIGITAL | IOD_GSM_TCP | 00038
GSMAlarmPMM2x17nad8036 | DIGITAL | IOD_GSM_TCP | 00039
GSMAlarmPMM2x17nad8037 | DIGITAL | IOD_GSM_TCP | 00040
GSMAlarmPMM2x17nad8038 | DIGITAL | IOD_GSM_TCP | 00041
GSMAlarmPMM2x17nad8039 | DIGITAL | IOD_GSM_TCP | 00042
GSMAlarmPMM2x17nad803 | DIGITAL | IOD_GSM_TCP | 00043
GSMAlarmPMM2x17nad8040 | DIGITAL | IOD_GSM_TCP | 00044
GSMAlarmPMM2x17nad8041 | DIGITAL | IOD_GSM_TCP | 00045
GSMAlarmPMM2x17nad8042 | DIGITAL | IOD_GSM_TCP | 00046
GSMAlarmPMM2x17nad804 | DIGITAL | IOD_GSM_TCP | 00047
GSMAlarmPMM2x17nad805 | DIGITAL | IOD_GSM_TCP | 00048
GSMAlarmPMM2x17nad806 | DIGITAL | IOD_GSM_TCP | 00049
GSMAlarmPMM2x17nad807 | DIGITAL | IOD_GSM_TCP | 00050
GSMAlarmPMM2x17nad808 | DIGITAL | IOD_GSM_TCP | 00051
GSMAlarmPMM2x17nad809 | DIGITAL | IOD_GSM_TCP | 00052
GSMALM_AGR_Gasenje_alarm | DIGITAL | IOD_GSM_TCP | 00053
GSMALM_AGR_PozCent_napaka | DIGITAL | IOD_GSM_TCP | 00054
GSMALM_AGR_PozSenzor_okvara | DIGITAL | IOD_GSM_TCP | 00055
GSMALM_GSM_Gasenje_alarm | DIGITAL | IOD_GSM_TCP | 00056
GSMALM_GSM_PozCent_napaka | DIGITAL | IOD_GSM_TCP | 00057
GSMALM_GSM_PozSenzor_okvara | DIGITAL | IOD_GSM_TCP | 00058
GSMcas_modbus_izpad | STRING | IOD_GSM_TCP | 45001[15]
GSMCirc1CosFi_III | REAL | IOD_GSM_TCP | 44001
GSMCirc1DelovnaEnergija | REAL | IOD_GSM_TCP | 44003
GSMCirc1DelovnaEnergija_TEMP | REAL | IOD_GSM_TCP | 44005
GSMCirc1DelovnaMoc_III | REAL | IOD_GSM_TCP | 44007
GSMCirc1DelovnaMoc_L1 | REAL | IOD_GSM_TCP | 44009
GSMCirc1DelovnaMoc_L2 | REAL | IOD_GSM_TCP | 44011
GSMCirc1DelovnaMoc_L3 | REAL | IOD_GSM_TCP | 44013
GSMCirc1Frekvenca_L1 | REAL | IOD_GSM_TCP | 44015
GSMCirc1InduktivnaEnergija | REAL | IOD_GSM_TCP | 44017
GSMCirc1InduktivnaMoc_III | REAL | IOD_GSM_TCP | 44019
GSMCirc1JalovaMoc_L1 | REAL | IOD_GSM_TCP | 44021
GSMCirc1JalovaMoc_L2 | REAL | IOD_GSM_TCP | 44023
GSMCirc1JalovaMoc_L3 | REAL | IOD_GSM_TCP | 44025
GSMCirc1KapacitivnaEnergija | REAL | IOD_GSM_TCP | 44027
GSMCirc1KapacitivnaMoc_III | REAL | IOD_GSM_TCP | 44029
GSMCirc1MaximumDemand | REAL | IOD_GSM_TCP | 44031
GSMCirc1MaximumDemandA2 | REAL | IOD_GSM_TCP | 44033
GSMCirc1MaximumDemandA3 | REAL | IOD_GSM_TCP | 44035
GSMCirc1Napetost_L1_L2 | REAL | IOD_GSM_TCP | 44037
GSMCirc1Napetost_L1_N | REAL | IOD_GSM_TCP | 44039
GSMCirc1Napetost_L2_L3 | REAL | IOD_GSM_TCP | 44041
GSMCirc1Napetost_L2_N | REAL | IOD_GSM_TCP | 44043
GSMCirc1Napetost_L3_L1 | REAL | IOD_GSM_TCP | 44045
GSMCirc1Napetost_L3_N | REAL | IOD_GSM_TCP | 44047
GSMCirc1NavideznaMoc_III | REAL | IOD_GSM_TCP | 44049
GSMCirc1NicelniTok | REAL | IOD_GSM_TCP | 44051
GSMCirc1PowerFactor_III | REAL | IOD_GSM_TCP | 44053
GSMCirc1PowerFactor_L1 | REAL | IOD_GSM_TCP | 44055
GSMCirc1PowerFactor_L2 | REAL | IOD_GSM_TCP | 44057
GSMCirc1PowerFactor_L3 | REAL | IOD_GSM_TCP | 44059
GSMCirc1RazEner_D | REAL | IOD_GSM_TCP | 44061
GSMCirc1RazEner_D_SCADA | REAL | IOD_GSM_TCP | 44063
GSMCirc1RazEner_D_TEMP | REAL | IOD_GSM_TCP | 44065
GSMCirc1RazEner_M | REAL | IOD_GSM_TCP | 44067
GSMCirc1RazEner_M_SCADA | REAL | IOD_GSM_TCP | 44069
GSMCirc1RazEner_M_TEMP | REAL | IOD_GSM_TCP | 44071
GSMCirc1RazEner_T | REAL | IOD_GSM_TCP | 44073
GSMCirc1RazEner_T_SCADA | REAL | IOD_GSM_TCP | 44075
GSMCirc1RazEner_T_TEMP | REAL | IOD_GSM_TCP | 44077
GSMCirc1THDI_L1 | REAL | IOD_GSM_TCP | 44079
GSMCirc1THDI_L2 | REAL | IOD_GSM_TCP | 44081
GSMCirc1THDI_L3 | REAL | IOD_GSM_TCP | 44083
GSMCirc1THDV_L1 | REAL | IOD_GSM_TCP | 44085
GSMCirc1THDV_L2 | REAL | IOD_GSM_TCP | 44087
GSMCirc1THDV_L3 | REAL | IOD_GSM_TCP | 44089
GSMCirc1Tok_L1 | REAL | IOD_GSM_TCP | 44091
GSMCirc1Tok_L2 | REAL | IOD_GSM_TCP | 44093
GSMCirc1Tok_L3 | REAL | IOD_GSM_TCP | 44095
GSMCirc1TokPovprecje_III | REAL | IOD_GSM_TCP | 44097
GSMCirc_Vpis_Dnevne_energija_scada1 | DIGITAL | IOD_GSM_TCP | 00059
GSMCirc_Vpis_Dnevne_energija_scada2 | DIGITAL | IOD_GSM_TCP | 00060
GSMCirc_Vpis_Mesecna_energija_scada1 | DIGITAL | IOD_GSM_TCP | 00061
GSMCirc_Vpis_Mesecna_energija_scada2 | DIGITAL | IOD_GSM_TCP | 00062
GSMCirc_Vpis_Tedenska_energija_scada1 | DIGITAL | IOD_GSM_TCP | 00063
GSMCirc_Vpis_Tedenska_energija_scada2 | DIGITAL | IOD_GSM_TCP | 00064
GSMComError | DIGITAL | IOD_GSM_TCP | 00065
GSMComSCADA | DIGITAL | IOD_GSM_TCP | 00066
GSMComSCADA1 | DIGITAL | IOD_GSM_TCP | 00067
GSMComSCADA2 | DIGITAL | IOD_GSM_TCP | 00068
GSMComSCADA3 | DIGITAL | IOD_GSM_TCP | 00069
GSMDate_Time0 | STRING | IOD_GSM_TCP | 45016[15]
GSMDate_Time1 | STRING | IOD_GSM_TCP | 45031[15]
GSMDate_Time2 | STRING | IOD_GSM_TCP | 45046[15]
GSMDate_Time3 | STRING | IOD_GSM_TCP | 45061[15]
GSMDateTimeDan | INT | IOD_GSM_TCP | 40001
GSMDateTimeLeto | INT | IOD_GSM_TCP | 40002
GSMDateTimeLeto2 | INT | IOD_GSM_TCP | 40003
GSMDateTimeMesec | INT | IOD_GSM_TCP | 40004
GSMDateTimeMinuta | INT | IOD_GSM_TCP | 40005
GSMDateTimePLC_Dan | INT | IOD_GSM_TCP | 40006
GSMDateTimePLC_DanVTednu | INT | IOD_GSM_TCP | 40007
GSMDateTimePLC_Leto | INT | IOD_GSM_TCP | 40008
GSMDateTimePLC_Mesec | INT | IOD_GSM_TCP | 40009
GSMDateTimePLC_Minuta | INT | IOD_GSM_TCP | 40010
GSMDateTimePLC_Sekunda | INT | IOD_GSM_TCP | 40011
GSMDateTimePLC_Ura | INT | IOD_GSM_TCP | 40012
GSMDateTimeSekunda | INT | IOD_GSM_TCP | 40013
GSMDateTimeUra | INT | IOD_GSM_TCP | 40014
GSMDI1_I11 | DIGITAL | IOD_GSM_TCP | 00070
GSMDI1_I9 | DIGITAL | IOD_GSM_TCP | 00071
GSMDI2_I14 | DIGITAL | IOD_GSM_TCP | 00072
GSMDI2_I15 | DIGITAL | IOD_GSM_TCP | 00073
GSMDI_R3KC_A_Q21_IzkljucenIzpad | DIGITAL | IOD_GSM_TCP | 00074
GSMDI_R3KC_A_Q22_IzkljucenIzpad | DIGITAL | IOD_GSM_TCP | 00075
GSMDI_SBi_RAZS_AA_Izolacija_NOT_OK | DIGITAL | IOD_GSM_TCP | 00076
GSMDI_SBi_RAZS_AB_Izolacija_NOT_OK | DIGITAL | IOD_GSM_TCP | 00077
GSMErrComCirc1 | DIGITAL | IOD_GSM_TCP | 00078
GSMErrComKlima1 | DIGITAL | IOD_GSM_TCP | 00079
GSMErrComKlima2 | DIGITAL | IOD_GSM_TCP | 00080
GSMErrComPMM1 | DIGITAL | IOD_GSM_TCP | 00081
GSMErrComPMM2 | DIGITAL | IOD_GSM_TCP | 00082
GSMErrComPort2 | DIGITAL | IOD_GSM_TCP | 00083
GSMErrComPort3 | DIGITAL | IOD_GSM_TCP | 00084
GSMErrComPort4 | DIGITAL | IOD_GSM_TCP | 00085
GSMErrComUPS1 | DIGITAL | IOD_GSM_TCP | 00086
GSMErrComUPS2 | DIGITAL | IOD_GSM_TCP | 00087
GSMErrComUPS3 | DIGITAL | IOD_GSM_TCP | 00088
GSMErrComUPSMGE1 | DIGITAL | IOD_GSM_TCP | 00089
GSMF1_1_zascita_ok | DIGITAL | IOD_GSM_TCP | 00090
GSMGSM_Gasenje_alarm | DIGITAL | IOD_GSM_TCP | 00091
GSMGSM_PozCent_napaka | DIGITAL | IOD_GSM_TCP | 00092
GSMGSM_PozSenzor_okvara | DIGITAL | IOD_GSM_TCP | 00093
GSMHIA1_vlaga_s | INT | IOD_GSM_TCP | 40015
GSMHIA2_vlaga_s | INT | IOD_GSM_TCP | 40016
GSMHIA3_vlaga_s | INT | IOD_GSM_TCP | 40017
GSMHIA4_vlaga_s | INT | IOD_GSM_TCP | 40018
GSMHIA5_vlaga_s | INT | IOD_GSM_TCP | 40019
GSMHIA6_vlaga_s | INT | IOD_GSM_TCP | 40020
GSMHIA7_vlaga_s | INT | IOD_GSM_TCP | 40021
GSMK1_SkupnaNapaka | DIGITAL | IOD_GSM_TCP | 00094
GSMK1_vklop_izklop_poteka | DIGITAL | IOD_GSM_TCP | 00095
GSMK1AlarmPozara | DIGITAL | IOD_GSM_TCP | 00096
GSMK1KlimaZdruzenAlarm | DIGITAL | IOD_GSM_TCP | 00097
GSMK1NiPretoka | DIGITAL | IOD_GSM_TCP | 00098
GSMK1obrat_ure | STRING | IOD_GSM_TCP | 45076[15]
GSMK1OkvaraRototerma | DIGITAL | IOD_GSM_TCP | 00099
GSMK1OkvaraVlazNap | DIGITAL | IOD_GSM_TCP | 00100
GSMK1PreobMotCrpGr | DIGITAL | IOD_GSM_TCP | 00101
GSMK1PreobMotVent | DIGITAL | IOD_GSM_TCP | 00102
GSMK1ProtizamrzZascAkt | DIGITAL | IOD_GSM_TCP | 00103
GSMK1ZamasenostFiltra | DIGITAL | IOD_GSM_TCP | 00104
GSMK2_SkupnaNapaka | DIGITAL | IOD_GSM_TCP | 00105
GSMK2_vklop_izklop_poteka | DIGITAL | IOD_GSM_TCP | 00106
GSMK2AlarmPozara | DIGITAL | IOD_GSM_TCP | 00107
GSMK2KlimaZdruzenAlarm | DIGITAL | IOD_GSM_TCP | 00108
GSMK2NiPretoka | DIGITAL | IOD_GSM_TCP | 00109
GSMK2OkvaraRototerma | DIGITAL | IOD_GSM_TCP | 00110
GSMK2OkvaraVlazNap | DIGITAL | IOD_GSM_TCP | 00111
GSMK2PreobMotCrpGr | DIGITAL | IOD_GSM_TCP | 00112
GSMK2PreobMotVent | DIGITAL | IOD_GSM_TCP | 00113
GSMK2ProtizamrzZascAkt | DIGITAL | IOD_GSM_TCP | 00114
GSMK2ZamasenostFiltra | DIGITAL | IOD_GSM_TCP | 00115
GSMK3_deluje | DIGITAL | IOD_GSM_TCP | 00116
GSMK3_SkupnaNapaka | DIGITAL | IOD_GSM_TCP | 00117
GSMKlima1_izkljucena | DIGITAL | IOD_GSM_TCP | 00118
GSMKLIMA1_kke_pogon | DIGITAL | IOD_GSM_TCP | 00119
GSMKLIMA1_krm_nap_ok | DIGITAL | IOD_GSM_TCP | 00120
GSMKlima2_izkljucena | DIGITAL | IOD_GSM_TCP | 00121
GSMKlima3_izkljucena | DIGITAL | IOD_GSM_TCP | 00122
GSMKlima1Alarm_pozar | DIGITAL | IOD_GSM_TCP | 00123
GSMKlima1Analog_izh_mesanje | INT | IOD_GSM_TCP | 40022
GSMKlima1Analog_izh_rekuperator | INT | IOD_GSM_TCP | 40023
GSMKlima1Analog_izh_VentGrelnika | INT | IOD_GSM_TCP | 40024
GSMKlima1Analog_izh_VentHlajenja | INT | IOD_GSM_TCP | 40025
GSMKlima1Dejanska_zel_temp | INT | IOD_GSM_TCP | 40026
GSMKlima1DelVentHit1 | DIGITAL | IOD_GSM_TCP | 00124
GSMKlima1DelVentHit2 | DIGITAL | IOD_GSM_TCP | 00125
GSMKlima1Hitrost_del_vent_disp | INT | IOD_GSM_TCP | 40027
GSMKlima1Max_vpih | INT | IOD_GSM_TCP | 40028
GSMKlima1Min_vpih | INT | IOD_GSM_TCP | 40029
GSMKlima1Ni_pretoka | DIGITAL | IOD_GSM_TCP | 00126
GSMKlima1Obrat_ure_Vent_h1 | INT | IOD_GSM_TCP | 40030
GSMKlima1Obrat_ure_Vent_h2 | INT | IOD_GSM_TCP | 40031
GSMKlima1OkvaraRototerm | DIGITAL | IOD_GSM_TCP | 00127
GSMKlima1OkvaraVlazNap | DIGITAL | IOD_GSM_TCP | 00128
GSMKlima1Pol_komp_konec | INT | IOD_GSM_TCP | 40032
GSMKlima1Pol_komp_sprem_zel_vr | INT | IOD_GSM_TCP | 40033
GSMKlima1Pol_komp_zacetek | INT | IOD_GSM_TCP | 40034
GSMKlima1PreklopHitDelVent | INT | IOD_GSM_TCP | 40035
GSMKlima1PreobMotCrpGrel | DIGITAL | IOD_GSM_TCP | 00129
GSMKlima1PreobMotVent | DIGITAL | IOD_GSM_TCP | 00130
GSMKlima1Protizamrz_zascita | INT | IOD_GSM_TCP | 40036
GSMKlima1ProtizamrzZascAktivna | DIGITAL | IOD_GSM_TCP | 00131
GSMKlima1Rezim_delovanja | INT | IOD_GSM_TCP | 40037
GSMKlima1Temperatura_dovoda | INT | IOD_GSM_TCP | 40038
GSMKlima1Temperatura_prostora | INT | IOD_GSM_TCP | 40039
GSMKlima1TempPredPloscnimRekup | INT | IOD_GSM_TCP | 40040
GSMKlima1TempZaPloscnimRekup | INT | IOD_GSM_TCP | 40041
GSMKlima1VklopRegKlimata | DIGITAL | IOD_GSM_TCP | 00132
GSMKlima1Vlaga_v_prostoru | INT | IOD_GSM_TCP | 40042
GSMKlima1VlagaVstopZrakaProstor | INT | IOD_GSM_TCP | 40043
GSMKlima1ZamasenostFiltra | DIGITAL | IOD_GSM_TCP | 00133
GSMKlima1ZdruzAlarmA | DIGITAL | IOD_GSM_TCP | 00134
GSMKlima1ZdruzAlarmB | DIGITAL | IOD_GSM_TCP | 00135
GSMKlima1Zel_temp_eko_gretja | INT | IOD_GSM_TCP | 40044
GSMKlima1Zel_temp_eko_hlajenja | INT | IOD_GSM_TCP | 40045
GSMKlima1Zel_temp_komf_gretja | INT | IOD_GSM_TCP | 40046
GSMKlima1Zel_temp_komf_hlajenja | INT | IOD_GSM_TCP | 40047
GSMKlima1Zim_komp_konec | INT | IOD_GSM_TCP | 40048
GSMKlima1Zim_komp_sprem_zel_vr | INT | IOD_GSM_TCP | 40049
GSMKlima1Zim_komp_zacetek | INT | IOD_GSM_TCP | 40050
GSMKlima1ZimKompMinVpihKonec | INT | IOD_GSM_TCP | 40051
GSMKlima1ZimKompMinVpihZac | INT | IOD_GSM_TCP | 40052
GSMKlima1ZkompMinVpihSpremZelVr | INT | IOD_GSM_TCP | 40053
GSMKlima1Zunanja_temp | INT | IOD_GSM_TCP | 40054
GSMKlima2Alarm_pozar | DIGITAL | IOD_GSM_TCP | 00136
GSMKlima2Analog_izh_mesanje | INT | IOD_GSM_TCP | 40055
GSMKlima2Analog_izh_rekuperator | INT | IOD_GSM_TCP | 40056
GSMKlima2Analog_izh_VentGrelnika | INT | IOD_GSM_TCP | 40057
GSMKlima2Analog_izh_VentHlajenja | INT | IOD_GSM_TCP | 40058
GSMKlima2Dejanska_zel_temp | INT | IOD_GSM_TCP | 40059
GSMKlima2DelVentHit1 | DIGITAL | IOD_GSM_TCP | 00137
GSMKlima2DelVentHit2 | DIGITAL | IOD_GSM_TCP | 00138
GSMKlima2Hitrost_del_vent_disp | INT | IOD_GSM_TCP | 40060
GSMKlima2Max_vpih | INT | IOD_GSM_TCP | 40061
GSMKlima2Min_vpih | INT | IOD_GSM_TCP | 40062
GSMKlima2Ni_pretoka | DIGITAL | IOD_GSM_TCP | 00139
GSMKlima2Obrat_ure_Vent_h1 | INT | IOD_GSM_TCP | 40063
GSMKlima2Obrat_ure_Vent_h2 | INT | IOD_GSM_TCP | 40064
GSMKlima2OkvaraRototerm | DIGITAL | IOD_GSM_TCP | 00140
GSMKlima2OkvaraVlazNap | DIGITAL | IOD_GSM_TCP | 00141
GSMKlima2Pol_komp_konec | INT | IOD_GSM_TCP | 40065
GSMKlima2Pol_komp_sprem_zel_vr | INT | IOD_GSM_TCP | 40066
GSMKlima2Pol_komp_zacetek | INT | IOD_GSM_TCP | 40067
GSMKlima2PreklopHitDelVent | INT | IOD_GSM_TCP | 40068
GSMKlima2PreobMotCrpGrel | DIGITAL | IOD_GSM_TCP | 00142
GSMKlima2PreobMotVent | DIGITAL | IOD_GSM_TCP | 00143
GSMKlima2Protizamrz_zascita | INT | IOD_GSM_TCP | 40069
GSMKlima2ProtizamrzZascAktivna | DIGITAL | IOD_GSM_TCP | 00144
GSMKlima2Rezim_delovanja | INT | IOD_GSM_TCP | 40070
GSMKlima2Temperatura_dovoda | INT | IOD_GSM_TCP | 40071
GSMKlima2Temperatura_prostora | INT | IOD_GSM_TCP | 40072
GSMKlima2TempPredPloscnimRekup | INT | IOD_GSM_TCP | 40073
GSMKlima2TempZaPloscnimRekup | INT | IOD_GSM_TCP | 40074
GSMKlima2VklopRegKlimata | DIGITAL | IOD_GSM_TCP | 00145
GSMKlima2Vlaga_v_prostoru | INT | IOD_GSM_TCP | 40075
GSMKlima2VlagaVstopZrakaProstor | INT | IOD_GSM_TCP | 40076
GSMKlima2ZamasenostFiltra | DIGITAL | IOD_GSM_TCP | 00146
GSMKlima2ZdruzAlarmA | DIGITAL | IOD_GSM_TCP | 00147
GSMKlima2ZdruzAlarmB | DIGITAL | IOD_GSM_TCP | 00148
GSMKlima2Zel_temp_eko_gretja | INT | IOD_GSM_TCP | 40077
GSMKlima2Zel_temp_eko_hlajenja | INT | IOD_GSM_TCP | 40078
GSMKlima2Zel_temp_komf_gretja | INT | IOD_GSM_TCP | 40079
GSMKlima2Zel_temp_komf_hlajenja | INT | IOD_GSM_TCP | 40080
GSMKlima2Zim_komp_konec | INT | IOD_GSM_TCP | 40081
GSMKlima2Zim_komp_sprem_zel_vr | INT | IOD_GSM_TCP | 40082
GSMKlima2Zim_komp_zacetek | INT | IOD_GSM_TCP | 40083
GSMKlima2ZimKompMinVpihKonec | INT | IOD_GSM_TCP | 40084
GSMKlima2ZimKompMinVpihZac | INT | IOD_GSM_TCP | 40085
GSMKlima2ZkompMinVpihSpremZelVr | INT | IOD_GSM_TCP | 40086
GSMKlima2Zunanja_temp | INT | IOD_GSM_TCP | 40087
GSMKLIMA_m1_delovanje | DIGITAL | IOD_GSM_TCP | 00149
GSMKLIMA_m1_napaka | DIGITAL | IOD_GSM_TCP | 00150
GSMKLIMA_m2_delovanje | DIGITAL | IOD_GSM_TCP | 00151
GSMKLIMA_m2_napaka | DIGITAL | IOD_GSM_TCP | 00152
GSMKlimaIzklopObrUre | INT | IOD_GSM_TCP | 40088
GSMKLIMAT1_delovanje | DIGITAL | IOD_GSM_TCP | 00153
GSMKLIMAT1_napaka | DIGITAL | IOD_GSM_TCP | 00154
GSMKLIMAT1_R_zakleni | DIGITAL | IOD_GSM_TCP | 00155
GSMKLIMAT1_vklop_delovanja | DIGITAL | IOD_GSM_TCP | 00156
GSMKLIMAT1_vklop_delovanjaR | DIGITAL | IOD_GSM_TCP | 00157
GSMKLIMAT2_delovanje | DIGITAL | IOD_GSM_TCP | 00158
GSMKLIMAT2_napaka | DIGITAL | IOD_GSM_TCP | 00159
GSMKLIMAT2_R_zakleni | DIGITAL | IOD_GSM_TCP | 00160
GSMKLIMAT2_vklop_delovanja | DIGITAL | IOD_GSM_TCP | 00161
GSMKLIMAT2_vklop_delovanjaR | DIGITAL | IOD_GSM_TCP | 00162
GSMKlime_vklopi_n | INT | IOD_GSM_TCP | 40089
GSMKlimeAVTO | DIGITAL | IOD_GSM_TCP | 00163
GSMkom_nast_cas_izpada | INT | IOD_GSM_TCP | 40090
GSMMAX_SOCKET_FD_SETSIZE | LONG | IOD_GSM_TCP | 43001
GSMN_F1_1_zascita_ok | DIGITAL | IOD_GSM_TCP | 00164
GSMN_KLIMA1_krm_nap_ok | DIGITAL | IOD_GSM_TCP | 00165
GSMN_KLIMAT1_napaka | DIGITAL | IOD_GSM_TCP | 00166
GSMN_KLIMAT2_napaka | DIGITAL | IOD_GSM_TCP | 00167
GSMN_KlimeAVTO | DIGITAL | IOD_GSM_TCP | 00168
GSMK1_obr_u_skupno | UINT | IOD_GSM_TCP | 46001
GSMK2_obr_u_skupno | UINT | IOD_GSM_TCP | 46002
GSMN_Q12_izpad | DIGITAL | IOD_GSM_TCP | 00169
GSMN_UPS_A_V23_delovanje | DIGITAL | IOD_GSM_TCP | 00170
GSMN_UPS_A_V23_napaka | DIGITAL | IOD_GSM_TCP | 00171
GSMN_UPS_V23_delovanje | DIGITAL | IOD_GSM_TCP | 00172
GSMN_UPS_V23_napaka | DIGITAL | IOD_GSM_TCP | 00173
GSMN_UPS_V25_delovanje | DIGITAL | IOD_GSM_TCP | 00174
GSMN_UPS_V25_napaka | DIGITAL | IOD_GSM_TCP | 00175
GSMN_VLAZILEC1_napaka | DIGITAL | IOD_GSM_TCP | 00176
GSMN_VLAZILEC2_napaka | DIGITAL | IOD_GSM_TCP | 00177
GSMnapaka_kom_panel | DIGITAL | IOD_GSM_TCP | 00178
GSMnapaka_kom_scada | DIGITAL | IOD_GSM_TCP | 00179
GSMnapaka_kom_scada2 | DIGITAL | IOD_GSM_TCP | 00180
GSMNapakaSenzorSkupno | DIGITAL | IOD_GSM_TCP | 00181
GSMNapakaSenzorVlagaHIA1 | DIGITAL | IOD_GSM_TCP | 00182
GSMNapakaSenzorVlagaHIA2 | DIGITAL | IOD_GSM_TCP | 00183
GSMNapakaSenzorVlagaHIA3 | DIGITAL | IOD_GSM_TCP | 00184
GSMNapakaSenzorVlagaHIA4 | DIGITAL | IOD_GSM_TCP | 00185
GSMNapakaSenzorVlagaHIA5 | DIGITAL | IOD_GSM_TCP | 00186
GSMNapakaSenzorVlagaHIA6 | DIGITAL | IOD_GSM_TCP | 00187
GSMNapakaSenzorVlagaHIA7 | DIGITAL | IOD_GSM_TCP | 00188
GSMNapakaTSTempTIA1 | DIGITAL | IOD_GSM_TCP | 00189
GSMNapakaTSTempTIA2 | DIGITAL | IOD_GSM_TCP | 00190
GSMNapakaTSTempTIA3 | DIGITAL | IOD_GSM_TCP | 00191
GSMNapakaTSTempTIA4 | DIGITAL | IOD_GSM_TCP | 00192
GSMNapakaTSTempTIA5 | DIGITAL | IOD_GSM_TCP | 00193
GSMNapakaTSTempTIA6 | DIGITAL | IOD_GSM_TCP | 00194
GSMNapakaTSTempTIA7 | DIGITAL | IOD_GSM_TCP | 00195
GSMOpozoriloPMM2x17med60in8010 | DIGITAL | IOD_GSM_TCP | 00196
GSMOpozoriloPMM2x17med60in8011 | DIGITAL | IOD_GSM_TCP | 00197
GSMOpozoriloPMM2x17med60in8012 | DIGITAL | IOD_GSM_TCP | 00198
GSMOpozoriloPMM2x17med60in8013 | DIGITAL | IOD_GSM_TCP | 00199
GSMOpozoriloPMM2x17med60in8014 | DIGITAL | IOD_GSM_TCP | 00200
GSMOpozoriloPMM2x17med60in8015 | DIGITAL | IOD_GSM_TCP | 00201
GSMOpozoriloPMM2x17med60in8016 | DIGITAL | IOD_GSM_TCP | 00202
GSMOpozoriloPMM2x17med60in8017 | DIGITAL | IOD_GSM_TCP | 00203
GSMOpozoriloPMM2x17med60in8018 | DIGITAL | IOD_GSM_TCP | 00204
GSMOpozoriloPMM2x17med60in8019 | DIGITAL | IOD_GSM_TCP | 00205
GSMOpozoriloPMM2x17med60in801 | DIGITAL | IOD_GSM_TCP | 00206
GSMOpozoriloPMM2x17med60in8020 | DIGITAL | IOD_GSM_TCP | 00207
GSMOpozoriloPMM2x17med60in8021 | DIGITAL | IOD_GSM_TCP | 00208
GSMOpozoriloPMM2x17med60in8022 | DIGITAL | IOD_GSM_TCP | 00209
GSMOpozoriloPMM2x17med60in8023 | DIGITAL | IOD_GSM_TCP | 00210
GSMOpozoriloPMM2x17med60in8024 | DIGITAL | IOD_GSM_TCP | 00211
GSMOpozoriloPMM2x17med60in8025 | DIGITAL | IOD_GSM_TCP | 00212
GSMOpozoriloPMM2x17med60in8026 | DIGITAL | IOD_GSM_TCP | 00213
GSMOpozoriloPMM2x17med60in8027 | DIGITAL | IOD_GSM_TCP | 00214
GSMOpozoriloPMM2x17med60in8028 | DIGITAL | IOD_GSM_TCP | 00215
GSMOpozoriloPMM2x17med60in8029 | DIGITAL | IOD_GSM_TCP | 00216
GSMOpozoriloPMM2x17med60in802 | DIGITAL | IOD_GSM_TCP | 00217
GSMOpozoriloPMM2x17med60in8030 | DIGITAL | IOD_GSM_TCP | 00218
GSMOpozoriloPMM2x17med60in8031 | DIGITAL | IOD_GSM_TCP | 00219
GSMOpozoriloPMM2x17med60in8032 | DIGITAL | IOD_GSM_TCP | 00220
GSMOpozoriloPMM2x17med60in8033 | DIGITAL | IOD_GSM_TCP | 00221
GSMOpozoriloPMM2x17med60in8034 | DIGITAL | IOD_GSM_TCP | 00222
GSMOpozoriloPMM2x17med60in8035 | DIGITAL | IOD_GSM_TCP | 00223
GSMOpozoriloPMM2x17med60in8036 | DIGITAL | IOD_GSM_TCP | 00224
GSMOpozoriloPMM2x17med60in8037 | DIGITAL | IOD_GSM_TCP | 00225
GSMOpozoriloPMM2x17med60in8038 | DIGITAL | IOD_GSM_TCP | 00226
GSMOpozoriloPMM2x17med60in8039 | DIGITAL | IOD_GSM_TCP | 00227
GSMOpozoriloPMM2x17med60in803 | DIGITAL | IOD_GSM_TCP | 00228
GSMOpozoriloPMM2x17med60in8040 | DIGITAL | IOD_GSM_TCP | 00229
GSMOpozoriloPMM2x17med60in8041 | DIGITAL | IOD_GSM_TCP | 00230
GSMOpozoriloPMM2x17med60in8042 | DIGITAL | IOD_GSM_TCP | 00231
GSMOpozoriloPMM2x17med60in804 | DIGITAL | IOD_GSM_TCP | 00232
GSMOpozoriloPMM2x17med60in805 | DIGITAL | IOD_GSM_TCP | 00233
GSMOpozoriloPMM2x17med60in806 | DIGITAL | IOD_GSM_TCP | 00234
GSMOpozoriloPMM2x17med60in807 | DIGITAL | IOD_GSM_TCP | 00235
GSMOpozoriloPMM2x17med60in808 | DIGITAL | IOD_GSM_TCP | 00236
GSMOpozoriloPMM2x17med60in809 | DIGITAL | IOD_GSM_TCP | 00237
GSMPMM1OverCurrentBetw1 | DIGITAL | IOD_GSM_TCP | 00238
GSMPMM1OverCurrentBetw2 | DIGITAL | IOD_GSM_TCP | 00239
GSMPMM1OverCurrentBetw3 | DIGITAL | IOD_GSM_TCP | 00240
GSMPMM1OverCurrentOver1 | DIGITAL | IOD_GSM_TCP | 00241
GSMPMM1OverCurrentOver2 | DIGITAL | IOD_GSM_TCP | 00242
GSMPMM1OverCurrentOver3 | DIGITAL | IOD_GSM_TCP | 00243
GSMPMM2QA1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_GSM_TCP | 00244
GSMPMM2QB1_GlStik_IZKLOP_IZPAD | DIGITAL | IOD_GSM_TCP | 00245
GSMPMM2SkNapaka_med60in80 | DIGITAL | IOD_GSM_TCP | 00246
GSMPMM2SkNapaka_nad80 | DIGITAL | IOD_GSM_TCP | 00247
GSMPMM2SkNapakaVirA_med60in80 | DIGITAL | IOD_GSM_TCP | 00248
GSMPMM2SkNapakaVirA_nad80 | DIGITAL | IOD_GSM_TCP | 00249
GSMPMM2SkNapakaVirB_med60in80 | DIGITAL | IOD_GSM_TCP | 00250
GSMPMM2SkNapakaVirB_nad80 | DIGITAL | IOD_GSM_TCP | 00251
GSMPMM2VirACurrent10 | REAL | IOD_GSM_TCP | 44099
GSMPMM2VirACurrent11 | REAL | IOD_GSM_TCP | 44101
GSMPMM2VirACurrent12 | REAL | IOD_GSM_TCP | 44103
GSMPMM2VirACurrent13 | REAL | IOD_GSM_TCP | 44105
GSMPMM2VirACurrent14 | REAL | IOD_GSM_TCP | 44107
GSMPMM2VirACurrent15 | REAL | IOD_GSM_TCP | 44109
GSMPMM2VirACurrent16 | REAL | IOD_GSM_TCP | 44111
GSMPMM2VirACurrent17 | REAL | IOD_GSM_TCP | 44113
GSMPMM2VirACurrent18 | REAL | IOD_GSM_TCP | 44115
GSMPMM2VirACurrent19 | REAL | IOD_GSM_TCP | 44117
GSMPMM2VirACurrent1 | REAL | IOD_GSM_TCP | 44119
GSMPMM2VirACurrent20 | REAL | IOD_GSM_TCP | 44121
GSMPMM2VirACurrent21 | REAL | IOD_GSM_TCP | 44123
GSMPMM2VirACurrent22 | REAL | IOD_GSM_TCP | 44125
GSMPMM2VirACurrent23 | REAL | IOD_GSM_TCP | 44127
GSMPMM2VirACurrent24 | REAL | IOD_GSM_TCP | 44129
GSMPMM2VirACurrent25 | REAL | IOD_GSM_TCP | 44131
GSMPMM2VirACurrent26 | REAL | IOD_GSM_TCP | 44133
GSMPMM2VirACurrent27 | REAL | IOD_GSM_TCP | 44135
GSMPMM2VirACurrent28 | REAL | IOD_GSM_TCP | 44137
GSMPMM2VirACurrent29 | REAL | IOD_GSM_TCP | 44139
GSMPMM2VirACurrent2 | REAL | IOD_GSM_TCP | 44141
GSMPMM2VirACurrent30 | REAL | IOD_GSM_TCP | 44143
GSMPMM2VirACurrent31 | REAL | IOD_GSM_TCP | 44145
GSMPMM2VirACurrent32 | REAL | IOD_GSM_TCP | 44147
GSMPMM2VirACurrent33 | REAL | IOD_GSM_TCP | 44149
GSMPMM2VirACurrent34 | REAL | IOD_GSM_TCP | 44151
GSMPMM2VirACurrent35 | REAL | IOD_GSM_TCP | 44153
GSMPMM2VirACurrent36 | REAL | IOD_GSM_TCP | 44155
GSMPMM2VirACurrent37 | REAL | IOD_GSM_TCP | 44157
GSMPMM2VirACurrent38 | REAL | IOD_GSM_TCP | 44159
GSMPMM2VirACurrent39 | REAL | IOD_GSM_TCP | 44161
GSMPMM2VirACurrent3 | REAL | IOD_GSM_TCP | 44163
GSMPMM2VirACurrent40 | REAL | IOD_GSM_TCP | 44165
GSMPMM2VirACurrent41 | REAL | IOD_GSM_TCP | 44167
GSMPMM2VirACurrent42 | REAL | IOD_GSM_TCP | 44169
GSMPMM2VirACurrent43 | REAL | IOD_GSM_TCP | 44171
GSMPMM2VirACurrent44 | REAL | IOD_GSM_TCP | 44173
GSMPMM2VirACurrent4 | REAL | IOD_GSM_TCP | 44175
GSMPMM2VirACurrent5 | REAL | IOD_GSM_TCP | 44177
GSMPMM2VirACurrent6 | REAL | IOD_GSM_TCP | 44179
GSMPMM2VirACurrent7 | REAL | IOD_GSM_TCP | 44181
GSMPMM2VirACurrent8 | REAL | IOD_GSM_TCP | 44183
GSMPMM2VirACurrent9 | REAL | IOD_GSM_TCP | 44185
GSMPMM2VirA_fsys | REAL | IOD_GSM_TCP | 44187
GSMPMM2VirA_Isys | REAL | IOD_GSM_TCP | 44189
GSMPMM2VirA_NapakaOzemljitve | DIGITAL | IOD_GSM_TCP | 00252
GSMPMM2VirA_PFsys | REAL | IOD_GSM_TCP | 44191
GSMPMM2VirA_Psys | REAL | IOD_GSM_TCP | 44193
GSMPMM2VirA_Qsys | REAL | IOD_GSM_TCP | 44195
GSMPMM2VirA_Ssys | REAL | IOD_GSM_TCP | 44197
GSMPMM2VirA_Usys | REAL | IOD_GSM_TCP | 44199
GSMPMM2VirAActiveEnergyConsumed_kWh | REAL | IOD_GSM_TCP | 44201
GSMPMM2VirAActivePowerPhaseA_kW | REAL | IOD_GSM_TCP | 44203
GSMPMM2VirAActivePowerPhaseB_kW | REAL | IOD_GSM_TCP | 44205
GSMPMM2VirAActivePowerPhaseC_kW | REAL | IOD_GSM_TCP | 44207
GSMPMM2VirAAlarmPhaseC01_16_60to80 | UINT | IOD_GSM_TCP | 46003
GSMPMM2VirAAlarmPhaseC01_16_over80 | UINT | IOD_GSM_TCP | 46004
GSMPMM2VirAAlarmPhaseC17_32_60to80 | UINT | IOD_GSM_TCP | 46005
GSMPMM2VirAAlarmPhaseC17_32_over80 | UINT | IOD_GSM_TCP | 46006
GSMPMM2VirAAlarmPhaseC33_44_60to80 | UINT | IOD_GSM_TCP | 46007
GSMPMM2VirAAlarmPhaseC33_44_over80 | UINT | IOD_GSM_TCP | 46008
GSMPMM2VirAAparentPowerPhaseA | REAL | IOD_GSM_TCP | 44209
GSMPMM2VirAAparentPowerPhaseB | REAL | IOD_GSM_TCP | 44211
GSMPMM2VirAAparentPowerPhaseC | REAL | IOD_GSM_TCP | 44213
GSMPMM2VirACurrentInPhaseA_A | REAL | IOD_GSM_TCP | 44215
GSMPMM2VirACurrentInPhaseB_A | REAL | IOD_GSM_TCP | 44217
GSMPMM2VirACurrentInPhaseC_A | REAL | IOD_GSM_TCP | 44219
GSMPMM2VirAReactiveEnergyConsumed_kVARh | REAL | IOD_GSM_TCP | 44221
GSMPMM2VirAReactivePowerPhaseA | REAL | IOD_GSM_TCP | 44223
GSMPMM2VirAReactivePowerPhaseB | REAL | IOD_GSM_TCP | 44225
GSMPMM2VirAReactivePowerPhaseC | REAL | IOD_GSM_TCP | 44227
GSMPMM2VirAVoltageBetweenPhaseAB_V | REAL | IOD_GSM_TCP | 44229
GSMPMM2VirAVoltageBetweenPhaseAN_V | REAL | IOD_GSM_TCP | 44231
GSMPMM2VirAVoltageBetweenPhaseBC_V | REAL | IOD_GSM_TCP | 44233
GSMPMM2VirAVoltageBetweenPhaseBN_V | REAL | IOD_GSM_TCP | 44235
GSMPMM2VirAVoltageBetweenPhaseCA_V | REAL | IOD_GSM_TCP | 44237
GSMPMM2VirAVoltageBetweenPhaseCN_V | REAL | IOD_GSM_TCP | 44239
GSMPMM2VirBCurrent10 | REAL | IOD_GSM_TCP | 44241
GSMPMM2VirBCurrent11 | REAL | IOD_GSM_TCP | 44243
GSMPMM2VirBCurrent12 | REAL | IOD_GSM_TCP | 44245
GSMPMM2VirBCurrent13 | REAL | IOD_GSM_TCP | 44247
GSMPMM2VirBCurrent14 | REAL | IOD_GSM_TCP | 44249
GSMPMM2VirBCurrent15 | REAL | IOD_GSM_TCP | 44251
GSMPMM2VirBCurrent16 | REAL | IOD_GSM_TCP | 44253
GSMPMM2VirBCurrent17 | REAL | IOD_GSM_TCP | 44255
GSMPMM2VirBCurrent18 | REAL | IOD_GSM_TCP | 44257
GSMPMM2VirBCurrent19 | REAL | IOD_GSM_TCP | 44259
GSMPMM2VirBCurrent1 | REAL | IOD_GSM_TCP | 44261
GSMPMM2VirBCurrent20 | REAL | IOD_GSM_TCP | 44263
GSMPMM2VirBCurrent21 | REAL | IOD_GSM_TCP | 44265
GSMPMM2VirBCurrent22 | REAL | IOD_GSM_TCP | 44267
GSMPMM2VirBCurrent23 | REAL | IOD_GSM_TCP | 44269
GSMPMM2VirBCurrent24 | REAL | IOD_GSM_TCP | 44271
GSMPMM2VirBCurrent25 | REAL | IOD_GSM_TCP | 44273
GSMPMM2VirBCurrent26 | REAL | IOD_GSM_TCP | 44275
GSMPMM2VirBCurrent27 | REAL | IOD_GSM_TCP | 44277
GSMPMM2VirBCurrent28 | REAL | IOD_GSM_TCP | 44279
GSMPMM2VirBCurrent29 | REAL | IOD_GSM_TCP | 44281
GSMPMM2VirBCurrent2 | REAL | IOD_GSM_TCP | 44283
GSMPMM2VirBCurrent30 | REAL | IOD_GSM_TCP | 44285
GSMPMM2VirBCurrent31 | REAL | IOD_GSM_TCP | 44287
GSMPMM2VirBCurrent32 | REAL | IOD_GSM_TCP | 44289
GSMPMM2VirBCurrent33 | REAL | IOD_GSM_TCP | 44291
GSMPMM2VirBCurrent34 | REAL | IOD_GSM_TCP | 44293
GSMPMM2VirBCurrent35 | REAL | IOD_GSM_TCP | 44295
GSMPMM2VirBCurrent36 | REAL | IOD_GSM_TCP | 44297
GSMPMM2VirBCurrent37 | REAL | IOD_GSM_TCP | 44299
GSMPMM2VirBCurrent38 | REAL | IOD_GSM_TCP | 44301
GSMPMM2VirBCurrent39 | REAL | IOD_GSM_TCP | 44303
GSMPMM2VirBCurrent3 | REAL | IOD_GSM_TCP | 44305
GSMPMM2VirBCurrent40 | REAL | IOD_GSM_TCP | 44307
GSMPMM2VirBCurrent41 | REAL | IOD_GSM_TCP | 44309
GSMPMM2VirBCurrent42 | REAL | IOD_GSM_TCP | 44311
GSMPMM2VirBCurrent43 | REAL | IOD_GSM_TCP | 44313
GSMPMM2VirBCurrent44 | REAL | IOD_GSM_TCP | 44315
GSMPMM2VirBCurrent4 | REAL | IOD_GSM_TCP | 44317
GSMPMM2VirBCurrent5 | REAL | IOD_GSM_TCP | 44319
GSMPMM2VirBCurrent6 | REAL | IOD_GSM_TCP | 44321
GSMPMM2VirBCurrent7 | REAL | IOD_GSM_TCP | 44323
GSMPMM2VirBCurrent8 | REAL | IOD_GSM_TCP | 44325
GSMPMM2VirBCurrent9 | REAL | IOD_GSM_TCP | 44327
GSMPMM2VirB_fsys | REAL | IOD_GSM_TCP | 44329
GSMPMM2VirB_Isys | REAL | IOD_GSM_TCP | 44331
GSMPMM2VirB_NapakaOzemljitve | DIGITAL | IOD_GSM_TCP | 00253
GSMPMM2VirB_PFsys | REAL | IOD_GSM_TCP | 44333
GSMPMM2VirB_Psys | REAL | IOD_GSM_TCP | 44335
GSMPMM2VirB_Qsys | REAL | IOD_GSM_TCP | 44337
GSMPMM2VirB_Ssys | REAL | IOD_GSM_TCP | 44339
GSMPMM2VirB_Usys | REAL | IOD_GSM_TCP | 44341
GSMPMM2VirBActiveEnergyConsumed_kWh | REAL | IOD_GSM_TCP | 44343
GSMPMM2VirBActivePowerPhaseA_kW | REAL | IOD_GSM_TCP | 44345
GSMPMM2VirBActivePowerPhaseB_kW | REAL | IOD_GSM_TCP | 44347
GSMPMM2VirBActivePowerPhaseC_kW | REAL | IOD_GSM_TCP | 44349
GSMPMM2VirBAlarmPhaseC01_16_60to80 | UINT | IOD_GSM_TCP | 46009
GSMPMM2VirBAlarmPhaseC01_16_over80 | UINT | IOD_GSM_TCP | 46010
GSMPMM2VirBAlarmPhaseC17_32_60to80 | UINT | IOD_GSM_TCP | 46011
GSMPMM2VirBAlarmPhaseC17_32_over80 | UINT | IOD_GSM_TCP | 46012
GSMPMM2VirBAlarmPhaseC33_44_60to80 | UINT | IOD_GSM_TCP | 46013
GSMPMM2VirBAlarmPhaseC33_44_over80 | UINT | IOD_GSM_TCP | 46014
GSMPMM2VirBAparentPowerPhaseA | REAL | IOD_GSM_TCP | 44351
GSMPMM2VirBAparentPowerPhaseB | REAL | IOD_GSM_TCP | 44353
GSMPMM2VirBAparentPowerPhaseC | REAL | IOD_GSM_TCP | 44355
GSMPMM2VirBCurrentInPhaseA_A | REAL | IOD_GSM_TCP | 44357
GSMPMM2VirBCurrentInPhaseB_A | REAL | IOD_GSM_TCP | 44359
GSMPMM2VirBCurrentInPhaseC_A | REAL | IOD_GSM_TCP | 44361
GSMPMM2VirBReactiveEnergyConsumed_kVARh | REAL | IOD_GSM_TCP | 44363
GSMPMM2VirBReactivePowerPhaseA | REAL | IOD_GSM_TCP | 44365
GSMPMM2VirBReactivePowerPhaseB | REAL | IOD_GSM_TCP | 44367
GSMPMM2VirBReactivePowerPhaseC | REAL | IOD_GSM_TCP | 44369
GSMPMM2VirBVoltageBetweenPhaseAB_V | REAL | IOD_GSM_TCP | 44371
GSMPMM2VirBVoltageBetweenPhaseAN_V | REAL | IOD_GSM_TCP | 44373
GSMPMM2VirBVoltageBetweenPhaseBC_V | REAL | IOD_GSM_TCP | 44375
GSMPMM2VirBVoltageBetweenPhaseBN_V | REAL | IOD_GSM_TCP | 44377
GSMPMM2VirBVoltageBetweenPhaseCA_V | REAL | IOD_GSM_TCP | 44379
GSMPMM2VirBVoltageBetweenPhaseCN_V | REAL | IOD_GSM_TCP | 44381
GSMPMM1ActiveEnergyConsumed_kWh | REAL | IOD_GSM_TCP | 44383
GSMPMM1ActivePowerPhaseA_kW | REAL | IOD_GSM_TCP | 44385
GSMPMM1ActivePowerPhaseB_kW | REAL | IOD_GSM_TCP | 44387
GSMPMM1ActivePowerPhaseC_kW | REAL | IOD_GSM_TCP | 44389
GSMPMM1AlarmPhase1C01_16_60to80 | UINT | IOD_GSM_TCP | 46015
GSMPMM1AlarmPhase1C01_16_over80 | UINT | IOD_GSM_TCP | 46016
GSMPMM1AlarmPhase1C17_32_60to80 | UINT | IOD_GSM_TCP | 46017
GSMPMM1AlarmPhase1C17_32_over80 | UINT | IOD_GSM_TCP | 46018
GSMPMM1AlarmPhase1C33_42_60to80 | UINT | IOD_GSM_TCP | 46019
GSMPMM1AlarmPhase1C33_42_over80 | UINT | IOD_GSM_TCP | 46020
GSMPMM1AlarmPhase1GlobalAlarmReg | INT | IOD_GSM_TCP | 40091
GSMPMM1AlarmPhase2C01_16_60to80 | UINT | IOD_GSM_TCP | 46021
GSMPMM1AlarmPhase2C01_16_over80 | UINT | IOD_GSM_TCP | 46022
GSMPMM1AlarmPhase2C17_32_60to80 | UINT | IOD_GSM_TCP | 46023
GSMPMM1AlarmPhase2C17_32_over80 | UINT | IOD_GSM_TCP | 46024
GSMPMM1AlarmPhase2C33_42_60to80 | UINT | IOD_GSM_TCP | 46025
GSMPMM1AlarmPhase2C33_42_over80 | UINT | IOD_GSM_TCP | 46026
GSMPMM1AlarmPhase2GlobalAlarmReg | INT | IOD_GSM_TCP | 40092
GSMPMM1AlarmPhase3C01_16_60to80 | UINT | IOD_GSM_TCP | 46027
GSMPMM1AlarmPhase3C01_16_over80 | UINT | IOD_GSM_TCP | 46028
GSMPMM1AlarmPhase3C17_32_60to80 | UINT | IOD_GSM_TCP | 46029
GSMPMM1AlarmPhase3C17_32_over80 | UINT | IOD_GSM_TCP | 46030
GSMPMM1AlarmPhase3C33_42_60to80 | UINT | IOD_GSM_TCP | 46031
GSMPMM1AlarmPhase3C33_42_over80 | UINT | IOD_GSM_TCP | 46032
GSMPMM1AlarmPhase3GlobalAlarmReg | INT | IOD_GSM_TCP | 40093
GSMPMM1AparentPowerPhaseA | REAL | IOD_GSM_TCP | 44391
GSMPMM1AparentPowerPhaseB | REAL | IOD_GSM_TCP | 44393
GSMPMM1AparentPowerPhaseC | REAL | IOD_GSM_TCP | 44395
GSMPMM1AverageCurrent_A | REAL | IOD_GSM_TCP | 44397
GSMPMM1AveragePhaseToNeutral_V | REAL | IOD_GSM_TCP | 44399
GSMPMM1AveragePhaseToPhase_V | REAL | IOD_GSM_TCP | 44401
GSMPMM1CurrentInPhaseA_A | REAL | IOD_GSM_TCP | 44403
GSMPMM1CurrentInPhaseB_A | REAL | IOD_GSM_TCP | 44405
GSMPMM1CurrentInPhaseC_A | REAL | IOD_GSM_TCP | 44407
GSMPMM1Frequency_Hz | REAL | IOD_GSM_TCP | 44409
GSMPMM1Phase1Current10 | REAL | IOD_GSM_TCP | 44411
GSMPMM1Phase1Current11 | REAL | IOD_GSM_TCP | 44413
GSMPMM1Phase1Current12 | REAL | IOD_GSM_TCP | 44415
GSMPMM1Phase1Current13 | REAL | IOD_GSM_TCP | 44417
GSMPMM1Phase1Current14 | REAL | IOD_GSM_TCP | 44419
GSMPMM1Phase1Current15 | REAL | IOD_GSM_TCP | 44421
GSMPMM1Phase1Current16 | REAL | IOD_GSM_TCP | 44423
GSMPMM1Phase1Current17 | REAL | IOD_GSM_TCP | 44425
GSMPMM1Phase1Current18 | REAL | IOD_GSM_TCP | 44427
GSMPMM1Phase1Current19 | REAL | IOD_GSM_TCP | 44429
GSMPMM1Phase1Current1 | REAL | IOD_GSM_TCP | 44431
GSMPMM1Phase1Current20 | REAL | IOD_GSM_TCP | 44433
GSMPMM1Phase1Current21 | REAL | IOD_GSM_TCP | 44435
GSMPMM1Phase1Current22 | REAL | IOD_GSM_TCP | 44437
GSMPMM1Phase1Current23 | REAL | IOD_GSM_TCP | 44439
GSMPMM1Phase1Current24 | REAL | IOD_GSM_TCP | 44441
GSMPMM1Phase1Current25 | REAL | IOD_GSM_TCP | 44443
GSMPMM1Phase1Current26 | REAL | IOD_GSM_TCP | 44445
GSMPMM1Phase1Current27 | REAL | IOD_GSM_TCP | 44447
GSMPMM1Phase1Current28 | REAL | IOD_GSM_TCP | 44449
GSMPMM1Phase1Current29 | REAL | IOD_GSM_TCP | 44451
GSMPMM1Phase1Current2 | REAL | IOD_GSM_TCP | 44453
GSMPMM1Phase1Current30 | REAL | IOD_GSM_TCP | 44455
GSMPMM1Phase1Current31 | REAL | IOD_GSM_TCP | 44457
GSMPMM1Phase1Current32 | REAL | IOD_GSM_TCP | 44459
GSMPMM1Phase1Current33 | REAL | IOD_GSM_TCP | 44461
GSMPMM1Phase1Current34 | REAL | IOD_GSM_TCP | 44463
GSMPMM1Phase1Current35 | REAL | IOD_GSM_TCP | 44465
GSMPMM1Phase1Current36 | REAL | IOD_GSM_TCP | 44467
GSMPMM1Phase1Current37 | REAL | IOD_GSM_TCP | 44469
GSMPMM1Phase1Current38 | REAL | IOD_GSM_TCP | 44471
GSMPMM1Phase1Current39 | REAL | IOD_GSM_TCP | 44473
GSMPMM1Phase1Current3 | REAL | IOD_GSM_TCP | 44475
GSMPMM1Phase1Current40 | REAL | IOD_GSM_TCP | 44477
GSMPMM1Phase1Current41 | REAL | IOD_GSM_TCP | 44479
GSMPMM1Phase1Current42 | REAL | IOD_GSM_TCP | 44481
GSMPMM1Phase1Current4 | REAL | IOD_GSM_TCP | 44483
GSMPMM1Phase1Current5 | REAL | IOD_GSM_TCP | 44485
GSMPMM1Phase1Current6 | REAL | IOD_GSM_TCP | 44487
GSMPMM1Phase1Current7 | REAL | IOD_GSM_TCP | 44489
GSMPMM1Phase1Current8 | REAL | IOD_GSM_TCP | 44491
GSMPMM1Phase1Current9 | REAL | IOD_GSM_TCP | 44493
GSMPMM1Phase2Current10 | REAL | IOD_GSM_TCP | 44495
GSMPMM1Phase2Current11 | REAL | IOD_GSM_TCP | 44497
GSMPMM1Phase2Current12 | REAL | IOD_GSM_TCP | 44499
GSMPMM1Phase2Current13 | REAL | IOD_GSM_TCP | 44501
GSMPMM1Phase2Current14 | REAL | IOD_GSM_TCP | 44503
GSMPMM1Phase2Current15 | REAL | IOD_GSM_TCP | 44505
GSMPMM1Phase2Current16 | REAL | IOD_GSM_TCP | 44507
GSMPMM1Phase2Current17 | REAL | IOD_GSM_TCP | 44509
GSMPMM1Phase2Current18 | REAL | IOD_GSM_TCP | 44511
GSMPMM1Phase2Current19 | REAL | IOD_GSM_TCP | 44513
GSMPMM1Phase2Current1 | REAL | IOD_GSM_TCP | 44515
GSMPMM1Phase2Current20 | REAL | IOD_GSM_TCP | 44517
GSMPMM1Phase2Current21 | REAL | IOD_GSM_TCP | 44519
GSMPMM1Phase2Current22 | REAL | IOD_GSM_TCP | 44521
GSMPMM1Phase2Current23 | REAL | IOD_GSM_TCP | 44523
GSMPMM1Phase2Current24 | REAL | IOD_GSM_TCP | 44525
GSMPMM1Phase2Current25 | REAL | IOD_GSM_TCP | 44527
GSMPMM1Phase2Current26 | REAL | IOD_GSM_TCP | 44529
GSMPMM1Phase2Current27 | REAL | IOD_GSM_TCP | 44531
GSMPMM1Phase2Current28 | REAL | IOD_GSM_TCP | 44533
GSMPMM1Phase2Current29 | REAL | IOD_GSM_TCP | 44535
GSMPMM1Phase2Current2 | REAL | IOD_GSM_TCP | 44537
GSMPMM1Phase2Current30 | REAL | IOD_GSM_TCP | 44539
GSMPMM1Phase2Current31 | REAL | IOD_GSM_TCP | 44541
GSMPMM1Phase2Current32 | REAL | IOD_GSM_TCP | 44543
GSMPMM1Phase2Current33 | REAL | IOD_GSM_TCP | 44545
GSMPMM1Phase2Current34 | REAL | IOD_GSM_TCP | 44547
GSMPMM1Phase2Current35 | REAL | IOD_GSM_TCP | 44549
GSMPMM1Phase2Current36 | REAL | IOD_GSM_TCP | 44551
GSMPMM1Phase2Current37 | REAL | IOD_GSM_TCP | 44553
GSMPMM1Phase2Current38 | REAL | IOD_GSM_TCP | 44555
GSMPMM1Phase2Current39 | REAL | IOD_GSM_TCP | 44557
GSMPMM1Phase2Current3 | REAL | IOD_GSM_TCP | 44559
GSMPMM1Phase2Current40 | REAL | IOD_GSM_TCP | 44561
GSMPMM1Phase2Current41 | REAL | IOD_GSM_TCP | 44563
GSMPMM1Phase2Current42 | REAL | IOD_GSM_TCP | 44565
GSMPMM1Phase2Current4 | REAL | IOD_GSM_TCP | 44567
GSMPMM1Phase2Current5 | REAL | IOD_GSM_TCP | 44569
GSMPMM1Phase2Current6 | REAL | IOD_GSM_TCP | 44571
GSMPMM1Phase2Current7 | REAL | IOD_GSM_TCP | 44573
GSMPMM1Phase2Current8 | REAL | IOD_GSM_TCP | 44575
GSMPMM1Phase2Current9 | REAL | IOD_GSM_TCP | 44577
GSMPMM1Phase3Current10 | REAL | IOD_GSM_TCP | 44579
GSMPMM1Phase3Current11 | REAL | IOD_GSM_TCP | 44581
GSMPMM1Phase3Current12 | REAL | IOD_GSM_TCP | 44583
GSMPMM1Phase3Current13 | REAL | IOD_GSM_TCP | 44585
GSMPMM1Phase3Current14 | REAL | IOD_GSM_TCP | 44587
GSMPMM1Phase3Current15 | REAL | IOD_GSM_TCP | 44589
GSMPMM1Phase3Current16 | REAL | IOD_GSM_TCP | 44591
GSMPMM1Phase3Current17 | REAL | IOD_GSM_TCP | 44593
GSMPMM1Phase3Current18 | REAL | IOD_GSM_TCP | 44595
GSMPMM1Phase3Current19 | REAL | IOD_GSM_TCP | 44597
GSMPMM1Phase3Current1 | REAL | IOD_GSM_TCP | 44599
GSMPMM1Phase3Current20 | REAL | IOD_GSM_TCP | 44601
GSMPMM1Phase3Current21 | REAL | IOD_GSM_TCP | 44603
GSMPMM1Phase3Current22 | REAL | IOD_GSM_TCP | 44605
GSMPMM1Phase3Current23 | REAL | IOD_GSM_TCP | 44607
GSMPMM1Phase3Current24 | REAL | IOD_GSM_TCP | 44609
GSMPMM1Phase3Current25 | REAL | IOD_GSM_TCP | 44611
GSMPMM1Phase3Current26 | REAL | IOD_GSM_TCP | 44613
GSMPMM1Phase3Current27 | REAL | IOD_GSM_TCP | 44615
GSMPMM1Phase3Current28 | REAL | IOD_GSM_TCP | 44617
GSMPMM1Phase3Current29 | REAL | IOD_GSM_TCP | 44619
GSMPMM1Phase3Current2 | REAL | IOD_GSM_TCP | 44621
GSMPMM1Phase3Current30 | REAL | IOD_GSM_TCP | 44623
GSMPMM1Phase3Current31 | REAL | IOD_GSM_TCP | 44625
GSMPMM1Phase3Current32 | REAL | IOD_GSM_TCP | 44627
GSMPMM1Phase3Current33 | REAL | IOD_GSM_TCP | 44629
GSMPMM1Phase3Current34 | REAL | IOD_GSM_TCP | 44631
GSMPMM1Phase3Current35 | REAL | IOD_GSM_TCP | 44633
GSMPMM1Phase3Current36 | REAL | IOD_GSM_TCP | 44635
GSMPMM1Phase3Current37 | REAL | IOD_GSM_TCP | 44637
GSMPMM1Phase3Current38 | REAL | IOD_GSM_TCP | 44639
GSMPMM1Phase3Current39 | REAL | IOD_GSM_TCP | 44641
GSMPMM1Phase3Current3 | REAL | IOD_GSM_TCP | 44643
GSMPMM1Phase3Current40 | REAL | IOD_GSM_TCP | 44645
GSMPMM1Phase3Current41 | REAL | IOD_GSM_TCP | 44647
GSMPMM1Phase3Current42 | REAL | IOD_GSM_TCP | 44649
GSMPMM1Phase3Current4 | REAL | IOD_GSM_TCP | 44651
GSMPMM1Phase3Current5 | REAL | IOD_GSM_TCP | 44653
GSMPMM1Phase3Current6 | REAL | IOD_GSM_TCP | 44655
GSMPMM1Phase3Current7 | REAL | IOD_GSM_TCP | 44657
GSMPMM1Phase3Current8 | REAL | IOD_GSM_TCP | 44659
GSMPMM1Phase3Current9 | REAL | IOD_GSM_TCP | 44661
GSMPMM1PowerFactorSys | REAL | IOD_GSM_TCP | 44663
GSMPMM1ReactiveEnergyConsumed_kVARh | REAL | IOD_GSM_TCP | 44665
GSMPMM1ReactivePowerPhaseA | REAL | IOD_GSM_TCP | 44667
GSMPMM1ReactivePowerPhaseB | REAL | IOD_GSM_TCP | 44669
GSMPMM1ReactivePowerPhaseC | REAL | IOD_GSM_TCP | 44671
GSMPMM1TotalActivePower_kW | REAL | IOD_GSM_TCP | 44673
GSMPMM1TotalAparentPower_kVA | REAL | IOD_GSM_TCP | 44675
GSMPMM1TotalPowerFactor | REAL | IOD_GSM_TCP | 44677
GSMPMM1TotalReactivePower_kVAR | REAL | IOD_GSM_TCP | 44679
GSMPMM1VirA_fsys | REAL | IOD_GSM_TCP | 44681
GSMPMM1VirA_Isys | REAL | IOD_GSM_TCP | 44683
GSMPMM1VirA_PFsys | REAL | IOD_GSM_TCP | 44685
GSMPMM1VirA_Psys | REAL | IOD_GSM_TCP | 44687
GSMPMM1VirA_Qsys | REAL | IOD_GSM_TCP | 44689
GSMPMM1VirA_Ssys | REAL | IOD_GSM_TCP | 44691
GSMPMM1VirA_Usys | REAL | IOD_GSM_TCP | 44693
GSMPMM1VirB_fsys | REAL | IOD_GSM_TCP | 44695
GSMPMM1VirB_Isys | REAL | IOD_GSM_TCP | 44697
GSMPMM1VirB_PFsys | REAL | IOD_GSM_TCP | 44699
GSMPMM1VirB_Psys | REAL | IOD_GSM_TCP | 44701
GSMPMM1VirB_Qsys | REAL | IOD_GSM_TCP | 44703
GSMPMM1VirB_Ssys | REAL | IOD_GSM_TCP | 44705
GSMPMM1VirB_Usys | REAL | IOD_GSM_TCP | 44707
GSMPMM1VirBActiveEnergyConsumed_kWh | REAL | IOD_GSM_TCP | 44709
GSMPMM1VirBActivePowerPhaseA_kW | REAL | IOD_GSM_TCP | 44711
GSMPMM1VirBActivePowerPhaseB_kW | REAL | IOD_GSM_TCP | 44713
GSMPMM1VirBActivePowerPhaseC_kW | REAL | IOD_GSM_TCP | 44715
GSMPMM1VirBAparentPowerPhaseA | REAL | IOD_GSM_TCP | 44717
GSMPMM1VirBAparentPowerPhaseB | REAL | IOD_GSM_TCP | 44719
GSMPMM1VirBAparentPowerPhaseC | REAL | IOD_GSM_TCP | 44721
GSMPMM1VirBAverageCurrent_A | REAL | IOD_GSM_TCP | 44723
GSMPMM1VirBAveragePhaseToNeutral_V | REAL | IOD_GSM_TCP | 44725
GSMPMM1VirBAveragePhaseToPhase_V | REAL | IOD_GSM_TCP | 44727
GSMPMM1VirBCurrentInPhaseA_A | REAL | IOD_GSM_TCP | 44729
GSMPMM1VirBCurrentInPhaseB_A | REAL | IOD_GSM_TCP | 44731
GSMPMM1VirBCurrentInPhaseC_A | REAL | IOD_GSM_TCP | 44733
GSMPMM1VirBFrequency_Hz | REAL | IOD_GSM_TCP | 44735
GSMPMM1VirBPowerFactorSys | REAL | IOD_GSM_TCP | 44737
GSMPMM1VirBReactiveEnergyConsumed_kVARh | REAL | IOD_GSM_TCP | 44739
GSMPMM1VirBReactivePowerPhaseA | REAL | IOD_GSM_TCP | 44741
GSMPMM1VirBReactivePowerPhaseB | REAL | IOD_GSM_TCP | 44743
GSMPMM1VirBReactivePowerPhaseC | REAL | IOD_GSM_TCP | 44745
GSMPMM1VirBTotalActivePower_kW | REAL | IOD_GSM_TCP | 44747
GSMPMM1VirBTotalAparentPower_kVA | REAL | IOD_GSM_TCP | 44749
GSMPMM1VirBTotalPowerFactor | REAL | IOD_GSM_TCP | 44751
GSMPMM1VirBTotalReactivePower_kVAR | REAL | IOD_GSM_TCP | 44753
GSMPMM1VirBVoltageBetweenPhaseAB_V | REAL | IOD_GSM_TCP | 44755
GSMPMM1VirBVoltageBetweenPhaseAN_V | REAL | IOD_GSM_TCP | 44757
GSMPMM1VirBVoltageBetweenPhaseBC_V | REAL | IOD_GSM_TCP | 44759
GSMPMM1VirBVoltageBetweenPhaseBN_V | REAL | IOD_GSM_TCP | 44761
GSMPMM1VirBVoltageBetweenPhaseCA_V | REAL | IOD_GSM_TCP | 44763
GSMPMM1VirBVoltageBetweenPhaseCN_V | REAL | IOD_GSM_TCP | 44765
GSMPMM1VoltageBetweenPhaseAB_V | REAL | IOD_GSM_TCP | 44767
GSMPMM1VoltageBetweenPhaseAN_V | REAL | IOD_GSM_TCP | 44769
GSMPMM1VoltageBetweenPhaseBC_V | REAL | IOD_GSM_TCP | 44771
GSMPMM1VoltageBetweenPhaseBN_V | REAL | IOD_GSM_TCP | 44773
GSMPMM1VoltageBetweenPhaseCA_V | REAL | IOD_GSM_TCP | 44775
GSMPMM1VoltageBetweenPhaseCN_V | REAL | IOD_GSM_TCP | 44777
GSMPMMfaza01 | REAL | IOD_GSM_TCP | 44779
GSMPMMfaza02 | REAL | IOD_GSM_TCP | 44781
GSMPMMfaza03 | REAL | IOD_GSM_TCP | 44783
GSMPMMfaza04 | REAL | IOD_GSM_TCP | 44785
GSMPMMfaza05 | REAL | IOD_GSM_TCP | 44787
GSMPMMfaza06 | REAL | IOD_GSM_TCP | 44789
GSMPMMfaza07 | REAL | IOD_GSM_TCP | 44791
GSMPMMfaza08 | REAL | IOD_GSM_TCP | 44793
GSMPMMfaza09 | REAL | IOD_GSM_TCP | 44795
GSMPMMfaza10 | REAL | IOD_GSM_TCP | 44797
GSMPMMfaza11 | REAL | IOD_GSM_TCP | 44799
GSMPMMfaza12 | REAL | IOD_GSM_TCP | 44801
GSMPMMfaza13 | REAL | IOD_GSM_TCP | 44803
GSMPMMfaza14 | REAL | IOD_GSM_TCP | 44805
GSMPMMfaza15 | REAL | IOD_GSM_TCP | 44807
GSMPMMfaza16 | REAL | IOD_GSM_TCP | 44809
GSMPMMfaza17 | REAL | IOD_GSM_TCP | 44811
GSMPMMfaza18 | REAL | IOD_GSM_TCP | 44813
GSMPMMfaza19 | REAL | IOD_GSM_TCP | 44815
GSMPMMfaza20 | REAL | IOD_GSM_TCP | 44817
GSMPMMfaza21 | REAL | IOD_GSM_TCP | 44819
GSMPMMfaza22 | REAL | IOD_GSM_TCP | 44821
GSMPMMfaza23 | REAL | IOD_GSM_TCP | 44823
GSMPMMfaza24 | REAL | IOD_GSM_TCP | 44825
GSMPMMfaza25 | REAL | IOD_GSM_TCP | 44827
GSMPMMfaza26 | REAL | IOD_GSM_TCP | 44829
GSMPMMfaza27 | REAL | IOD_GSM_TCP | 44831
GSMPMMfaza28 | REAL | IOD_GSM_TCP | 44833
GSMPMMfaza29 | REAL | IOD_GSM_TCP | 44835
GSMPMMfaza30 | REAL | IOD_GSM_TCP | 44837
GSMPMMfaza31 | REAL | IOD_GSM_TCP | 44839
GSMPMMfaza32 | REAL | IOD_GSM_TCP | 44841
GSMPMMfaza33 | REAL | IOD_GSM_TCP | 44843
GSMPMMfaza34 | REAL | IOD_GSM_TCP | 44845
GSMPMMfaza35 | REAL | IOD_GSM_TCP | 44847
GSMPMMfaza36 | REAL | IOD_GSM_TCP | 44849
GSMPMMfaza37 | REAL | IOD_GSM_TCP | 44851
GSMPMMfaza38 | REAL | IOD_GSM_TCP | 44853
GSMPMMfaza39 | REAL | IOD_GSM_TCP | 44855
GSMPMMfaza40 | REAL | IOD_GSM_TCP | 44857
GSMPMMfaza41 | REAL | IOD_GSM_TCP | 44859
GSMPMMfaza42 | REAL | IOD_GSM_TCP | 44861
GSMPMMskupniTokA | REAL | IOD_GSM_TCP | 44863
GSMPMMskupniTokB | REAL | IOD_GSM_TCP | 44865
GSMPozarnaCentrala_skupno | DIGITAL | IOD_GSM_TCP | 00254
GSMPrevisokaTemp | DIGITAL | IOD_GSM_TCP | 00255
GSMQ0_izkljuceno | DIGITAL | IOD_GSM_TCP | 00256
GSMQ0_vkljuceno | DIGITAL | IOD_GSM_TCP | 00257
GSMQ12_izkljuceno | DIGITAL | IOD_GSM_TCP | 00258
GSMQ12_izpad | DIGITAL | IOD_GSM_TCP | 00259
GSMQ12_vkljuceno | DIGITAL | IOD_GSM_TCP | 00260
GSMQ12stanje | INT | IOD_GSM_TCP | 40094
GSMQ21_vkljuceno | DIGITAL | IOD_GSM_TCP | 00261
GSMQ22_vkljuceno | DIGITAL | IOD_GSM_TCP | 00262
GSMrazlitjeLAH1 | DIGITAL | IOD_GSM_TCP | 00263
GSMrazlitjeLAH2 | DIGITAL | IOD_GSM_TCP | 00264
GSMrazlitjeLAH3 | DIGITAL | IOD_GSM_TCP | 00265
GSMrazlitjeLAH4 | DIGITAL | IOD_GSM_TCP | 00266
GSMSetDateTime | DIGITAL | IOD_GSM_TCP | 00267
GSMSetDateTimeDemand | DIGITAL | IOD_GSM_TCP | 00268
GSMSetDateTimeError | DIGITAL | IOD_GSM_TCP | 00269
GSMSetDateTimeFinished | DIGITAL | IOD_GSM_TCP | 00270
GSMSkupneNapakeNaprav_PMM17VirBVirA | DIGITAL | IOD_GSM_TCP | 00271
GSMSlabaBaterijaPLC | DIGITAL | IOD_GSM_TCP | 00272
GSMTempHistereza | INT | IOD_GSM_TCP | 40095
GSMTempPovp234 | INT | IOD_GSM_TCP | 40096
GSMTempPovp234Alarm | INT | IOD_GSM_TCP | 40097
GSMTempPovp234Previs | DIGITAL | IOD_GSM_TCP | 00273
GSMTempPovp56 | INT | IOD_GSM_TCP | 40098
GSMTempPovp56Alarm | INT | IOD_GSM_TCP | 40099
GSMTempPovp56Previs | DIGITAL | IOD_GSM_TCP | 00274
GSMTempZaVklopKlim1 | INT | IOD_GSM_TCP | 40100
GSMTempZaVklopKlim2 | INT | IOD_GSM_TCP | 40101
GSMTIA1_alarm | INT | IOD_GSM_TCP | 40102
GSMTIA1_previs_temp | DIGITAL | IOD_GSM_TCP | 00275
GSMTIA1_temp_s | INT | IOD_GSM_TCP | 40103
GSMTIA2_alarm | INT | IOD_GSM_TCP | 40104
GSMTIA2_previs_temp | DIGITAL | IOD_GSM_TCP | 00276
GSMTIA2_temp_s | INT | IOD_GSM_TCP | 40105
GSMTIA3_alarm | INT | IOD_GSM_TCP | 40106
GSMTIA3_previs_temp | DIGITAL | IOD_GSM_TCP | 00277
GSMTIA3_temp_s | INT | IOD_GSM_TCP | 40107
GSMTIA4_alarm | INT | IOD_GSM_TCP | 40108
GSMTIA4_previs_temp | DIGITAL | IOD_GSM_TCP | 00278
GSMTIA4_temp_s | INT | IOD_GSM_TCP | 40109
GSMTIA5_alarm | INT | IOD_GSM_TCP | 40110
GSMTIA5_previs_temp | DIGITAL | IOD_GSM_TCP | 00279
GSMTIA5_temp_s | INT | IOD_GSM_TCP | 40111
GSMTIA6_alarm | INT | IOD_GSM_TCP | 40112
GSMTIA6_previs_temp | DIGITAL | IOD_GSM_TCP | 00280
GSMTIA6_temp_s | INT | IOD_GSM_TCP | 40113
GSMTIA7_alarm | INT | IOD_GSM_TCP | 40114
GSMTIA7_previs_temp | DIGITAL | IOD_GSM_TCP | 00281
GSMTIA7_temp_s | INT | IOD_GSM_TCP | 40115
GSMUPS1_StatusBaterije | UINT | IOD_GSM_TCP | 46033
GSMUPS1Errors10 | DIGITAL | IOD_GSM_TCP | 00282
GSMUPS1Errors11 | DIGITAL | IOD_GSM_TCP | 00283
GSMUPS1Errors12 | DIGITAL | IOD_GSM_TCP | 00284
GSMUPS1Errors13 | DIGITAL | IOD_GSM_TCP | 00285
GSMUPS1Errors14 | DIGITAL | IOD_GSM_TCP | 00286
GSMUPS1Errors15 | DIGITAL | IOD_GSM_TCP | 00287
GSMUPS1Errors16 | DIGITAL | IOD_GSM_TCP | 00288
GSMUPS1Errors17 | DIGITAL | IOD_GSM_TCP | 00289
GSMUPS1Errors18 | DIGITAL | IOD_GSM_TCP | 00290
GSMUPS1Errors19 | DIGITAL | IOD_GSM_TCP | 00291
GSMUPS1Errors1 | DIGITAL | IOD_GSM_TCP | 00292
GSMUPS1Errors20 | DIGITAL | IOD_GSM_TCP | 00293
GSMUPS1Errors21 | DIGITAL | IOD_GSM_TCP | 00294
GSMUPS1Errors22 | DIGITAL | IOD_GSM_TCP | 00295
GSMUPS1Errors23 | DIGITAL | IOD_GSM_TCP | 00296
GSMUPS1Errors24 | DIGITAL | IOD_GSM_TCP | 00297
GSMUPS1Errors25 | DIGITAL | IOD_GSM_TCP | 00298
GSMUPS1Errors2 | DIGITAL | IOD_GSM_TCP | 00299
GSMUPS1Errors3 | DIGITAL | IOD_GSM_TCP | 00300
GSMUPS1Errors4 | DIGITAL | IOD_GSM_TCP | 00301
GSMUPS1Errors5 | DIGITAL | IOD_GSM_TCP | 00302
GSMUPS1Errors6 | DIGITAL | IOD_GSM_TCP | 00303
GSMUPS1Errors7 | DIGITAL | IOD_GSM_TCP | 00304
GSMUPS1Errors8 | DIGITAL | IOD_GSM_TCP | 00305
GSMUPS1Errors9 | DIGITAL | IOD_GSM_TCP | 00306
GSMUPS2_StatusBaterije | UINT | IOD_GSM_TCP | 46034
GSMUPS2Errors10 | DIGITAL | IOD_GSM_TCP | 00307
GSMUPS2Errors11 | DIGITAL | IOD_GSM_TCP | 00308
GSMUPS2Errors12 | DIGITAL | IOD_GSM_TCP | 00309
GSMUPS2Errors13 | DIGITAL | IOD_GSM_TCP | 00310
GSMUPS2Errors14 | DIGITAL | IOD_GSM_TCP | 00311
GSMUPS2Errors15 | DIGITAL | IOD_GSM_TCP | 00312
GSMUPS2Errors16 | DIGITAL | IOD_GSM_TCP | 00313
GSMUPS2Errors17 | DIGITAL | IOD_GSM_TCP | 00314
GSMUPS2Errors18 | DIGITAL | IOD_GSM_TCP | 00315
GSMUPS2Errors19 | DIGITAL | IOD_GSM_TCP | 00316
GSMUPS2Errors1 | DIGITAL | IOD_GSM_TCP | 00317
GSMUPS2Errors20 | DIGITAL | IOD_GSM_TCP | 00318
GSMUPS2Errors21 | DIGITAL | IOD_GSM_TCP | 00319
GSMUPS2Errors22 | DIGITAL | IOD_GSM_TCP | 00320
GSMUPS2Errors23 | DIGITAL | IOD_GSM_TCP | 00321
GSMUPS2Errors24 | DIGITAL | IOD_GSM_TCP | 00322
GSMUPS2Errors25 | DIGITAL | IOD_GSM_TCP | 00323
GSMUPS2Errors2 | DIGITAL | IOD_GSM_TCP | 00324
GSMUPS2Errors3 | DIGITAL | IOD_GSM_TCP | 00325
GSMUPS2Errors4 | DIGITAL | IOD_GSM_TCP | 00326
GSMUPS2Errors5 | DIGITAL | IOD_GSM_TCP | 00327
GSMUPS2Errors6 | DIGITAL | IOD_GSM_TCP | 00328
GSMUPS2Errors7 | DIGITAL | IOD_GSM_TCP | 00329
GSMUPS2Errors8 | DIGITAL | IOD_GSM_TCP | 00330
GSMUPS2Errors9 | DIGITAL | IOD_GSM_TCP | 00331
GSMUPS3_StatusBaterije | UINT | IOD_GSM_TCP | 46035
GSMUPS3Errors10 | DIGITAL | IOD_GSM_TCP | 00332
GSMUPS3Errors11 | DIGITAL | IOD_GSM_TCP | 00333
GSMUPS3Errors12 | DIGITAL | IOD_GSM_TCP | 00334
GSMUPS3Errors13 | DIGITAL | IOD_GSM_TCP | 00335
GSMUPS3Errors14 | DIGITAL | IOD_GSM_TCP | 00336
GSMUPS3Errors15 | DIGITAL | IOD_GSM_TCP | 00337
GSMUPS3Errors16 | DIGITAL | IOD_GSM_TCP | 00338
GSMUPS3Errors17 | DIGITAL | IOD_GSM_TCP | 00339
GSMUPS3Errors18 | DIGITAL | IOD_GSM_TCP | 00340
GSMUPS3Errors19 | DIGITAL | IOD_GSM_TCP | 00341
GSMUPS3Errors1 | DIGITAL | IOD_GSM_TCP | 00342
GSMUPS3Errors20 | DIGITAL | IOD_GSM_TCP | 00343
GSMUPS3Errors21 | DIGITAL | IOD_GSM_TCP | 00344
GSMUPS3Errors22 | DIGITAL | IOD_GSM_TCP | 00345
GSMUPS3Errors23 | DIGITAL | IOD_GSM_TCP | 00346
GSMUPS3Errors24 | DIGITAL | IOD_GSM_TCP | 00347
GSMUPS3Errors25 | DIGITAL | IOD_GSM_TCP | 00348
GSMUPS3Errors2 | DIGITAL | IOD_GSM_TCP | 00349
GSMUPS3Errors3 | DIGITAL | IOD_GSM_TCP | 00350
GSMUPS3Errors4 | DIGITAL | IOD_GSM_TCP | 00351
GSMUPS3Errors5 | DIGITAL | IOD_GSM_TCP | 00352
GSMUPS3Errors6 | DIGITAL | IOD_GSM_TCP | 00353
GSMUPS3Errors7 | DIGITAL | IOD_GSM_TCP | 00354
GSMUPS3Errors8 | DIGITAL | IOD_GSM_TCP | 00355
GSMUPS3Errors9 | DIGITAL | IOD_GSM_TCP | 00356
GSMUPS1AlarmAwaitingPower | DIGITAL | IOD_GSM_TCP | 00357
GSMUPS1AlarmBypassBad | DIGITAL | IOD_GSM_TCP | 00358
GSMUPS1AlarmChargerFailed | DIGITAL | IOD_GSM_TCP | 00359
GSMUPS1AlarmCommunicationsLost | DIGITAL | IOD_GSM_TCP | 00360
GSMUPS1AlarmDepletedBattery | DIGITAL | IOD_GSM_TCP | 00361
GSMUPS1AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM_TCP | 00362
GSMUPS1AlarmInverterError | DIGITAL | IOD_GSM_TCP | 00363
GSMUPS1AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 00364
GSMUPS1AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM_TCP | 00365
GSMUPS1AlarmLowBattery | DIGITAL | IOD_GSM_TCP | 00366
GSMUPS1AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM_TCP | 00367
GSMUPS1AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM_TCP | 00368
GSMUPS1AlarmOnBattery | DIGITAL | IOD_GSM_TCP | 00369
GSMUPS1AlarmOnBypass | DIGITAL | IOD_GSM_TCP | 00370
GSMUPS1AlarmShutdownImminent | DIGITAL | IOD_GSM_TCP | 00371
GSMUPS1AlarmShutdownPending | DIGITAL | IOD_GSM_TCP | 00372
GSMUPS1AlarmSlabaBaterija | DIGITAL | IOD_GSM_TCP | 00373
GSMUPS1AlarmSplosnaNapaka | DIGITAL | IOD_GSM_TCP | 00374
GSMUPS1AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00375
GSMUPS1AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00376
GSMUPS1AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00377
GSMUPS1AlarmTestInProgres | DIGITAL | IOD_GSM_TCP | 00378
GSMUPS1AlarmUPSIzhodOff | DIGITAL | IOD_GSM_TCP | 00379
GSMUPS1AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 00380
GSMUPS1AlarmUPSSystemOff | DIGITAL | IOD_GSM_TCP | 00381
GSMUPS1EstimatedChargeRemaining | REAL | IOD_GSM_TCP | 44867
GSMUPS1EstimatedMinutesRemaining | REAL | IOD_GSM_TCP | 44869
GSMUPS1InverterStatus | INT | IOD_GSM_TCP | 40116
GSMUPS1IzhodMocL1 | REAL | IOD_GSM_TCP | 44871
GSMUPS1IzhodMocL2 | REAL | IOD_GSM_TCP | 44873
GSMUPS1IzhodMocL3 | REAL | IOD_GSM_TCP | 44875
GSMUPS1Napaka | DIGITAL | IOD_GSM_TCP | 00382
GSMUPS1NapetostBaterije | REAL | IOD_GSM_TCP | 44877
GSMUPS1OutputStatus | INT | IOD_GSM_TCP | 40117
GSMUPS1StatusBaterije | UINT | IOD_GSM_TCP | 46036
GSMUPS1StatusEcomodeAktiven | DIGITAL | IOD_GSM_TCP | 00383
GSMUPS1StatusInverterIsOn | DIGITAL | IOD_GSM_TCP | 00384
GSMUPS1StatusStopOperation | DIGITAL | IOD_GSM_TCP | 00385
GSMUPS1SteviloIzpadovVhodneLinije | INT | IOD_GSM_TCP | 40118
GSMUPS1TemperaturaBaterije | REAL | IOD_GSM_TCP | 44879
GSMUPS1UnitStatus | INT | IOD_GSM_TCP | 40119
GSMUPS1VhodFrekvencaL1 | REAL | IOD_GSM_TCP | 44881
GSMUPS1VhodFrekvencaL2 | REAL | IOD_GSM_TCP | 44883
GSMUPS1VhodFrekvencaL3 | REAL | IOD_GSM_TCP | 44885
GSMUPS1VhodNapetostL1 | REAL | IOD_GSM_TCP | 44887
GSMUPS1VhodNapetostL2 | REAL | IOD_GSM_TCP | 44889
GSMUPS1VhodNapetostL3 | REAL | IOD_GSM_TCP | 44891
GSMUPS2AlarmAwaitingPower | DIGITAL | IOD_GSM_TCP | 00386
GSMUPS2AlarmBypassBad | DIGITAL | IOD_GSM_TCP | 00387
GSMUPS2AlarmChargerFailed | DIGITAL | IOD_GSM_TCP | 00388
GSMUPS2AlarmCommunicationsLost | DIGITAL | IOD_GSM_TCP | 00389
GSMUPS2AlarmDepletedBattery | DIGITAL | IOD_GSM_TCP | 00390
GSMUPS2AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM_TCP | 00391
GSMUPS2AlarmInverterError | DIGITAL | IOD_GSM_TCP | 00392
GSMUPS2AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 00393
GSMUPS2AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM_TCP | 00394
GSMUPS2AlarmLowBattery | DIGITAL | IOD_GSM_TCP | 00395
GSMUPS2AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM_TCP | 00396
GSMUPS2AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM_TCP | 00397
GSMUPS2AlarmOnBattery | DIGITAL | IOD_GSM_TCP | 00398
GSMUPS2AlarmOnBypass | DIGITAL | IOD_GSM_TCP | 00399
GSMUPS2AlarmShutdownImminent | DIGITAL | IOD_GSM_TCP | 00400
GSMUPS2AlarmShutdownPending | DIGITAL | IOD_GSM_TCP | 00401
GSMUPS2AlarmSlabaBaterija | DIGITAL | IOD_GSM_TCP | 00402
GSMUPS2AlarmSplosnaNapaka | DIGITAL | IOD_GSM_TCP | 00403
GSMUPS2AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00404
GSMUPS2AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00405
GSMUPS2AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00406
GSMUPS2AlarmTestInProgres | DIGITAL | IOD_GSM_TCP | 00407
GSMUPS2AlarmUPSIzhodOff | DIGITAL | IOD_GSM_TCP | 00408
GSMUPS2AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 00409
GSMUPS2AlarmUPSSystemOff | DIGITAL | IOD_GSM_TCP | 00410
GSMUPS2EstimatedChargeRemaining | REAL | IOD_GSM_TCP | 44893
GSMUPS2EstimatedMinutesRemaining | REAL | IOD_GSM_TCP | 44895
GSMUPS2InverterStatus | INT | IOD_GSM_TCP | 40120
GSMUPS2IzhodMocL1 | REAL | IOD_GSM_TCP | 44897
GSMUPS2IzhodMocL2 | REAL | IOD_GSM_TCP | 44899
GSMUPS2IzhodMocL3 | REAL | IOD_GSM_TCP | 44901
GSMUPS2Napaka | DIGITAL | IOD_GSM_TCP | 00411
GSMUPS2NapetostBaterije | REAL | IOD_GSM_TCP | 44903
GSMUPS2OutputStatus | INT | IOD_GSM_TCP | 40121
GSMUPS2StatusBaterije | UINT | IOD_GSM_TCP | 46037
GSMUPS2StatusEcomodeAktiven | DIGITAL | IOD_GSM_TCP | 00412
GSMUPS2StatusInverterIsOn | DIGITAL | IOD_GSM_TCP | 00413
GSMUPS2StatusStopOperation | DIGITAL | IOD_GSM_TCP | 00414
GSMUPS2SteviloIzpadovVhodneLinije | INT | IOD_GSM_TCP | 40122
GSMUPS2TemperaturaBaterije | REAL | IOD_GSM_TCP | 44905
GSMUPS2UnitStatus | INT | IOD_GSM_TCP | 40123
GSMUPS2VhodFrekvencaL1 | REAL | IOD_GSM_TCP | 44907
GSMUPS2VhodFrekvencaL2 | REAL | IOD_GSM_TCP | 44909
GSMUPS2VhodFrekvencaL3 | REAL | IOD_GSM_TCP | 44911
GSMUPS2VhodNapetostL1 | REAL | IOD_GSM_TCP | 44913
GSMUPS2VhodNapetostL2 | REAL | IOD_GSM_TCP | 44915
GSMUPS2VhodNapetostL3 | REAL | IOD_GSM_TCP | 44917
GSMUPS3AlarmAwaitingPower | DIGITAL | IOD_GSM_TCP | 00415
GSMUPS3AlarmBypassBad | DIGITAL | IOD_GSM_TCP | 00416
GSMUPS3AlarmChargerFailed | DIGITAL | IOD_GSM_TCP | 00417
GSMUPS3AlarmCommunicationsLost | DIGITAL | IOD_GSM_TCP | 00418
GSMUPS3AlarmDepletedBattery | DIGITAL | IOD_GSM_TCP | 00419
GSMUPS3AlarmDiagnosticTestFailed | DIGITAL | IOD_GSM_TCP | 00420
GSMUPS3AlarmInverterError | DIGITAL | IOD_GSM_TCP | 00421
GSMUPS3AlarmIzhodOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 00422
GSMUPS3AlarmIzhodPreobremenjen | DIGITAL | IOD_GSM_TCP | 00423
GSMUPS3AlarmLowBattery | DIGITAL | IOD_GSM_TCP | 00424
GSMUPS3AlarmNapakaNaVarovalki | DIGITAL | IOD_GSM_TCP | 00425
GSMUPS3AlarmNapakaNaVentilatorju | DIGITAL | IOD_GSM_TCP | 00426
GSMUPS3AlarmOnBattery | DIGITAL | IOD_GSM_TCP | 00427
GSMUPS3AlarmOnBypass | DIGITAL | IOD_GSM_TCP | 00428
GSMUPS3AlarmShutdownImminent | DIGITAL | IOD_GSM_TCP | 00429
GSMUPS3AlarmShutdownPending | DIGITAL | IOD_GSM_TCP | 00430
GSMUPS3AlarmSlabaBaterija | DIGITAL | IOD_GSM_TCP | 00431
GSMUPS3AlarmSplosnaNapaka | DIGITAL | IOD_GSM_TCP | 00432
GSMUPS3AlarmStanjeIzhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00433
GSMUPS3AlarmStanjeVhodaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00434
GSMUPS3AlarmTemperaturaIzvenToleranc | DIGITAL | IOD_GSM_TCP | 00435
GSMUPS3AlarmTestInProgres | DIGITAL | IOD_GSM_TCP | 00436
GSMUPS3AlarmUPSIzhodOff | DIGITAL | IOD_GSM_TCP | 00437
GSMUPS3AlarmUPSOffKotZahtevano | DIGITAL | IOD_GSM_TCP | 00438
GSMUPS3AlarmUPSSystemOff | DIGITAL | IOD_GSM_TCP | 00439
GSMUPS3EstimatedChargeRemaining | REAL | IOD_GSM_TCP | 44919
GSMUPS3EstimatedMinutesRemaining | REAL | IOD_GSM_TCP | 44921
GSMUPS3InverterStatus | INT | IOD_GSM_TCP | 40124
GSMUPS3IzhodMocL1 | REAL | IOD_GSM_TCP | 44923
GSMUPS3IzhodMocL2 | REAL | IOD_GSM_TCP | 44925
GSMUPS3IzhodMocL3 | REAL | IOD_GSM_TCP | 44927
GSMUPS3Napaka | DIGITAL | IOD_GSM_TCP | 00440
GSMUPS3NapetostBaterije | REAL | IOD_GSM_TCP | 44929
GSMUPS3OutputStatus | INT | IOD_GSM_TCP | 40125
GSMUPS3StatusBaterije | UINT | IOD_GSM_TCP | 46038
GSMUPS3StatusEcomodeAktiven | DIGITAL | IOD_GSM_TCP | 00441
GSMUPS3StatusInverterIsOn | DIGITAL | IOD_GSM_TCP | 00442
GSMUPS3StatusStopOperation | DIGITAL | IOD_GSM_TCP | 00443
GSMUPS3SteviloIzpadovVhodneLinije | INT | IOD_GSM_TCP | 40126
GSMUPS3TemperaturaBaterije | REAL | IOD_GSM_TCP | 44931
GSMUPS3UnitStatus | INT | IOD_GSM_TCP | 40127
GSMUPS3VhodFrekvencaL1 | REAL | IOD_GSM_TCP | 44933
GSMUPS3VhodFrekvencaL2 | REAL | IOD_GSM_TCP | 44935
GSMUPS3VhodFrekvencaL3 | REAL | IOD_GSM_TCP | 44937
GSMUPS3VhodNapetostL1 | REAL | IOD_GSM_TCP | 44939
GSMUPS3VhodNapetostL2 | REAL | IOD_GSM_TCP | 44941
GSMUPS3VhodNapetostL3 | REAL | IOD_GSM_TCP | 44943
GSMUPS_A_V23_delovanje | DIGITAL | IOD_GSM_TCP | 00444
GSMUPS_A_V23_napaka | DIGITAL | IOD_GSM_TCP | 00445
GSMups_alarm | DIGITAL | IOD_GSM_TCP | 00446
GSMups_baterijski_nac | DIGITAL | IOD_GSM_TCP | 00447
GSMUPS_MGE1BatteryBackupTime | INT | IOD_GSM_TCP | 40128
GSMUPS_MGE1BatteryChargedState | DIGITAL | IOD_GSM_TCP | 00448
GSMUPS_MGE1BatteryChargingLevel | INT | IOD_GSM_TCP | 40129
GSMUPS_MGE1BatteryCircuitBreaker | DIGITAL | IOD_GSM_TCP | 00449
GSMUPS_MGE1BatteryCompInProgress | DIGITAL | IOD_GSM_TCP | 00450
GSMUPS_MGE1BatteryFuseFault | DIGITAL | IOD_GSM_TCP | 00451
GSMUPS_MGE1BatteryLowWarning | DIGITAL | IOD_GSM_TCP | 00452
GSMUPS_MGE1BatteryRechargeDuration | INT | IOD_GSM_TCP | 40130
GSMUPS_MGE1BatteryTempOutOfToler | DIGITAL | IOD_GSM_TCP | 00453
GSMUPS_MGE1BypassInFreeFrequency | DIGITAL | IOD_GSM_TCP | 00454
GSMUPS_MGE1ChargerGeneralFault | DIGITAL | IOD_GSM_TCP | 00455
GSMUPS_MGE1DeviceVentilationFault | DIGITAL | IOD_GSM_TCP | 00456
GSMUPS_MGE1I1output | INT | IOD_GSM_TCP | 40131
GSMUPS_MGE1I2output | INT | IOD_GSM_TCP | 40132
GSMUPS_MGE1I3output | INT | IOD_GSM_TCP | 40133
GSMUPS_MGE1InverterFrequency | INT | IOD_GSM_TCP | 40134
GSMUPS_MGE1InverterFuseFault | DIGITAL | IOD_GSM_TCP | 00457
GSMUPS_MGE1InverterOverload | DIGITAL | IOD_GSM_TCP | 00458
GSMUPS_MGE1InverterThermalOverload | DIGITAL | IOD_GSM_TCP | 00459
GSMUPS_MGE1Mains1VoltOutOfToler | DIGITAL | IOD_GSM_TCP | 00460
GSMUPS_MGE1Mains2Overload | DIGITAL | IOD_GSM_TCP | 00461
GSMUPS_MGE1Mains2VoltOutOfToler | DIGITAL | IOD_GSM_TCP | 00462
GSMUPS_MGE1MaintenancePosition | DIGITAL | IOD_GSM_TCP | 00463
GSMUPS_MGE1ManualBypassSwitch | DIGITAL | IOD_GSM_TCP | 00464
GSMUPS_MGE1NapakaNaVarovalkah | DIGITAL | IOD_GSM_TCP | 00465
GSMUPS_MGE1OutputActivePower1 | INT | IOD_GSM_TCP | 40135
GSMUPS_MGE1OutputActivePower2 | INT | IOD_GSM_TCP | 40136
GSMUPS_MGE1OutputActivePower3 | INT | IOD_GSM_TCP | 40137
GSMUPS_MGE1OutputFrequency | INT | IOD_GSM_TCP | 40138
GSMUPS_MGE1OutputInShortCircuit | DIGITAL | IOD_GSM_TCP | 00466
GSMUPS_MGE1OutputLoadLevel | INT | IOD_GSM_TCP | 40139
GSMUPS_MGE1OutputOverload | DIGITAL | IOD_GSM_TCP | 00467
GSMUPS_MGE1OutputThermalOverload | DIGITAL | IOD_GSM_TCP | 00468
GSMUPS_MGE1RectifierOn | DIGITAL | IOD_GSM_TCP | 00469
GSMUPS_MGE1RectifierThermOverload | DIGITAL | IOD_GSM_TCP | 00470
GSMUPS_MGE1Skupna_napaka | DIGITAL | IOD_GSM_TCP | 00471
GSMUPS_MGE1StatusBaterije | INT | IOD_GSM_TCP | 40140
GSMUPS_MGE1U12mains1 | INT | IOD_GSM_TCP | 40141
GSMUPS_MGE1U12mains2 | INT | IOD_GSM_TCP | 40142
GSMUPS_MGE1U1N_inverter | INT | IOD_GSM_TCP | 40143
GSMUPS_MGE1U1N_output | INT | IOD_GSM_TCP | 40144
GSMUPS_MGE1U23mains1 | INT | IOD_GSM_TCP | 40145
GSMUPS_MGE1U23mains2 | INT | IOD_GSM_TCP | 40146
GSMUPS_MGE1U2N_inverter | INT | IOD_GSM_TCP | 40147
GSMUPS_MGE1U2N_output | INT | IOD_GSM_TCP | 40148
GSMUPS_MGE1U31mains1 | INT | IOD_GSM_TCP | 40149
GSMUPS_MGE1U31mains2 | INT | IOD_GSM_TCP | 40150
GSMUPS_MGE1U3N_inverter | INT | IOD_GSM_TCP | 40151
GSMUPS_MGE1U3N_output | INT | IOD_GSM_TCP | 40152
GSMUPS_MGE1U_battery | INT | IOD_GSM_TCP | 40153
GSMUPS_MGE1UPS_coupled | DIGITAL | IOD_GSM_TCP | 00472
GSMUPS_MGE1UPS_error | DIGITAL | IOD_GSM_TCP | 00473
GSMUPS_MGE1UPS_in_backup | DIGITAL | IOD_GSM_TCP | 00474
GSMups_polnjenje | DIGITAL | IOD_GSM_TCP | 00475
GSMUPS_V23_delovanje | DIGITAL | IOD_GSM_TCP | 00476
GSMUPS_V23_napaka | DIGITAL | IOD_GSM_TCP | 00477
GSMUPS_V25_delovanje | DIGITAL | IOD_GSM_TCP | 00478
GSMUPS_V25_napaka | DIGITAL | IOD_GSM_TCP | 00479
GSMUPSMGEErrors10 | DIGITAL | IOD_GSM_TCP | 00480
GSMUPSMGEErrors11 | DIGITAL | IOD_GSM_TCP | 00481
GSMUPSMGEErrors12 | DIGITAL | IOD_GSM_TCP | 00482
GSMUPSMGEErrors13 | DIGITAL | IOD_GSM_TCP | 00483
GSMUPSMGEErrors14 | DIGITAL | IOD_GSM_TCP | 00484
GSMUPSMGEErrors15 | DIGITAL | IOD_GSM_TCP | 00485
GSMUPSMGEErrors16 | DIGITAL | IOD_GSM_TCP | 00486
GSMUPSMGEErrors17 | DIGITAL | IOD_GSM_TCP | 00487
GSMUPSMGEErrors1 | DIGITAL | IOD_GSM_TCP | 00488
GSMUPSMGEErrors2 | DIGITAL | IOD_GSM_TCP | 00489
GSMUPSMGEErrors3 | DIGITAL | IOD_GSM_TCP | 00490
GSMUPSMGEErrors4 | DIGITAL | IOD_GSM_TCP | 00491
GSMUPSMGEErrors5 | DIGITAL | IOD_GSM_TCP | 00492
GSMUPSMGEErrors6 | DIGITAL | IOD_GSM_TCP | 00493
GSMUPSMGEErrors7 | DIGITAL | IOD_GSM_TCP | 00494
GSMUPSMGEErrors8 | DIGITAL | IOD_GSM_TCP | 00495
GSMUPSMGEErrors9 | DIGITAL | IOD_GSM_TCP | 00496
GSMUserCurrentLevel | INT | IOD_GSM_TCP | 40154
GSMUserCurrentName | STRING | IOD_GSM_TCP | 45091[15]
GSMUserDisplay | STRING | IOD_GSM_TCP | 45106[15]
GSMUserLoggedIn | DIGITAL | IOD_GSM_TCP | 00497
GSMVLAZILEC1_delovanje | DIGITAL | IOD_GSM_TCP | 00498
GSMVLAZILEC1_napaka | DIGITAL | IOD_GSM_TCP | 00499
GSMVLAZILEC2_delovanje | DIGITAL | IOD_GSM_TCP | 00500
GSMVLAZILEC2_napaka | DIGITAL | IOD_GSM_TCP | 00501
GSMXVH_AlarmOn | DIGITAL | IOD_GSM_TCP | 00502
GSMXVH_enopolna_napaka | DIGITAL | IOD_GSM_TCP | 00503
GSM_DanEnergCirc1 | LONG | IOD_GSM_disk | L0[30]
GSM_CasDDanEnergCirc1 | INT | IOD_GSM_disk | I0[30]
GSM_CasMDanEnergCirc1 | INT | IOD_GSM_disk | I30[30]
GSM_TedenEnergCirc1 | LONG | IOD_GSM_disk | L30[30]
GSM_CasDTedenEnergCirc1 | INT | IOD_GSM_disk | I60[30]
GSM_CasMTedenEnergCirc1 | INT | IOD_GSM_disk | I90[30]
GSM_MesecEnergCirc1 | LONG | IOD_GSM_disk | L90[30]
GSM_CasDMesecEnergCirc1 | INT | IOD_GSM_disk | I120[30]
GSM_CasMMesecEnergCirc1 | INT | IOD_GSM_disk | I150[30]
GSM_StSt_DanEnergCirc1 | LONG | IOD_GSM_disk | L270
GSM_StSt_TedenEnergCirc1 | LONG | IOD_GSM_disk | L272
GSM_StSt_MesecEnergCirc1 | LONG | IOD_GSM_disk | L274
GSM_StStCasDDanEnergCirc1 | INT | IOD_GSM_disk | I276
GSM_StStCasMDanEnergCirc1 | INT | IOD_GSM_disk | I277
GSM_StStCasDTedenEnergCirc1 | INT | IOD_GSM_disk | I278
GSM_StStCasMTedenEnergCirc1 | INT | IOD_GSM_disk | I279
GSM_StStCasDMesecEnergCirc1 | INT | IOD_GSM_disk | I280
GSM_StStCasMMesecEnergCirc1 | INT | IOD_GSM_disk | I281
GSM_MaxDnevnaEnergija | LONG | IOD_GSM_disk | L282 | 0 | 9999999 | 0 | 9999999 | #######
GSM_MaxMesecnaEnergija | LONG | IOD_GSM_disk | L284 | 0 | 9999999 | 0 | 9999999 | #######
GSM_MaxTedenskaEnergija | LONG | IOD_GSM_disk | L286 | 0 | 9999999 | 0 | 9999999 | #######
GSM_Prikaz_analizatorja_ce_je_1 | DIGITAL | IOD_GSM_mem | D287
GSMPMM_2x17_VirA_zavihek | DIGITAL | IOD_GSM_disk | D288
GSMPMM_2x17_VirB_zavihek | DIGITAL | IOD_GSM_disk | D289
GSMServer_B_Izpad | DIGITAL | IOD_GSM_mem | D566
GSMServer_A_Izpad | DIGITAL | IOD_GSM_mem | D567
GSM_meja_tok_opozoriloL1 | INT | IOD_GSM_disk | I300
GSM_meja_tok_opozoriloL2 | INT | IOD_GSM_disk | I302
GSM_meja_tok_opozoriloL3 | INT | IOD_GSM_disk | I304
GSM_meja_tok_alarmL1 | INT | IOD_GSM_disk | I306
GSM_meja_tok_alarmL2 | INT | IOD_GSM_disk | I308
GSM_meja_tok_alarmL3 | INT | IOD_GSM_disk | I310
GSM_omogocanje_tok_opozorilaL1 | DIGITAL | IOD_GSM_disk | D312
GSM_omogocanje_tok_opozorilaL2 | DIGITAL | IOD_GSM_disk | D313
GSM_omogocanje_tok_opozorilaL3 | DIGITAL | IOD_GSM_disk | D314
GSM_omogocanje_tok_alarmL1 | DIGITAL | IOD_GSM_disk | D315
GSM_omogocanje_tok_alarmL2 | DIGITAL | IOD_GSM_disk | D316
GSM_omogocanje_tok_alarmL3 | DIGITAL | IOD_GSM_disk | D317
GSMErrComCirc1_om | DIGITAL | IOD_GSM_disk | D318
GSMErrComKlima1_om | DIGITAL | IOD_GSM_disk | D319
GSMErrComKlima2_om | DIGITAL | IOD_GSM_disk | D320
GSMErrComPMM1_om | DIGITAL | IOD_GSM_disk | D321
GSMErrComPort2_om | DIGITAL | IOD_GSM_disk | D322
GSMErrComPort3_om | DIGITAL | IOD_GSM_disk | D323
GSMErrComPort4_om | DIGITAL | IOD_GSM_disk | D324
GSMErrComUPS1_om | DIGITAL | IOD_GSM_disk | D325
GSMErrComUPS2_om | DIGITAL | IOD_GSM_disk | D326
GSMErrComUPSMGE1_om | DIGITAL | IOD_GSM_disk | D327
GSMrazlitjeLAH1_om | DIGITAL | IOD_GSM_disk | D328
GSMrazlitjeLAH2_om | DIGITAL | IOD_GSM_disk | D329
GSMrazlitjeLAH3_om | DIGITAL | IOD_GSM_disk | D330
GSMrazlitjeLAH4_om | DIGITAL | IOD_GSM_disk | D331
GSMServer_A_Izpad_om | DIGITAL | IOD_GSM_disk | D332
GSMServer_B_Izpad_om | DIGITAL | IOD_GSM_disk | D333
GSMnapaka_kom_panel_om | DIGITAL | IOD_GSM_disk | D334
GSMSetDateTimeError_om | DIGITAL | IOD_GSM_disk | D335
GSMSlabaBaterijaPLC_om | DIGITAL | IOD_GSM_disk | D336
GSMups_baterijski_nac_om | DIGITAL | IOD_GSM_disk | D337
GSMups_alarm_om | DIGITAL | IOD_GSM_disk | D338
GSMups_polnjenje_om | DIGITAL | IOD_GSM_disk | D339
GSMQ0_izkljuceno_om | DIGITAL | IOD_GSM_disk | D340
GSMQ0_vkljuceno_om | DIGITAL | IOD_GSM_disk | D341
GSMQ12_izkljuceno_om | DIGITAL | IOD_GSM_disk | D342
GSMQ12_izpad_om | DIGITAL | IOD_GSM_disk | D343
GSMQ12_vkljuceno_om | DIGITAL | IOD_GSM_disk | D344
GSMN_F1_1_zascita_ok_om | DIGITAL | IOD_GSM_disk | D345
GSMK1_SkupnaNapaka_om | DIGITAL | IOD_GSM_disk | D346
GSMK1AlarmPozara_om | DIGITAL | IOD_GSM_disk | D347
GSMK1KlimaZdruzenAlarm_om | DIGITAL | IOD_GSM_disk | D348
GSMK1NiPretoka_om | DIGITAL | IOD_GSM_disk | D349
GSMK1OkvaraRototerma_om | DIGITAL | IOD_GSM_disk | D350
GSMK1OkvaraVlazNap_om | DIGITAL | IOD_GSM_disk | D351
GSMK1PreobMotCrpGr_om | DIGITAL | IOD_GSM_disk | D352
GSMK1PreobMotVent_om | DIGITAL | IOD_GSM_disk | D353
GSMK1ProtizamrzZascAkt_om | DIGITAL | IOD_GSM_disk | D354
GSMK1ZamasenostFiltra_om | DIGITAL | IOD_GSM_disk | D355
GSMKLIMAT1_delovanje_om | DIGITAL | IOD_GSM_disk | D356
GSMKLIMAT1_vklop_delovanja_om | DIGITAL | IOD_GSM_disk | D357
GSMN_KLIMAT1_napaka_om | DIGITAL | IOD_GSM_disk | D358
GSMKlimeAVTO_om | DIGITAL | IOD_GSM_disk | D359
GSMKlima1_izkljucena_om | DIGITAL | IOD_GSM_disk | D360
GSMN_VLAZILEC1_napaka_om | DIGITAL | IOD_GSM_disk | D361
GSMK2_SkupnaNapaka_om | DIGITAL | IOD_GSM_disk | D362
GSMK2AlarmPozara_om | DIGITAL | IOD_GSM_disk | D363
GSMK2KlimaZdruzenAlarm_om | DIGITAL | IOD_GSM_disk | D364
GSMK2NiPretoka_om | DIGITAL | IOD_GSM_disk | D365
GSMK2OkvaraRototerma_om | DIGITAL | IOD_GSM_disk | D366
GSMK2OkvaraVlazNap_om | DIGITAL | IOD_GSM_disk | D367
GSMK2PreobMotCrpGr_om | DIGITAL | IOD_GSM_disk | D368
GSMK2PreobMotVent_om | DIGITAL | IOD_GSM_disk | D369
GSMK2ProtizamrzZascAkt_om | DIGITAL | IOD_GSM_disk | D370
GSMK2ZamasenostFiltra_om | DIGITAL | IOD_GSM_disk | D371
GSMKLIMAT2_delovanje_om | DIGITAL | IOD_GSM_disk | D372
GSMKLIMAT2_vklop_delovanja_om | DIGITAL | IOD_GSM_disk | D373
GSMN_KLIMAT2_napaka_om | DIGITAL | IOD_GSM_disk | D374
GSMKlima2_izkljucena_om | DIGITAL | IOD_GSM_disk | D375
GSMN_VLAZILEC2_napaka_om | DIGITAL | IOD_GSM_disk | D376
GSMKLIMA_m1_napaka_om | DIGITAL | IOD_GSM_disk | D377
GSMKLIMA_m2_napaka_om | DIGITAL | IOD_GSM_disk | D378
GSMKlima3_izkljucena_om | DIGITAL | IOD_GSM_disk | D379
GSMN_KLIMA1_krm_nap_ok_om | DIGITAL | IOD_GSM_disk | D380
GSMKLIMA1_kke_pogon_om | DIGITAL | IOD_GSM_disk | D381
GSMKLIMA_m1_delovanje_om | DIGITAL | IOD_GSM_disk | D382
GSMKLIMA_m2_delovanje_om | DIGITAL | IOD_GSM_disk | D383
GSMK3_deluje_om | DIGITAL | IOD_GSM_disk | D384
GSMK3_SkupnaNapaka_om | DIGITAL | IOD_GSM_disk | D385
GSMN_UPS_V23_delovanje_om | DIGITAL | IOD_GSM_disk | D386
GSMN_UPS_V23_napaka_om | DIGITAL | IOD_GSM_disk | D387
GSMUPS1AlarmSlabaBaterija_om | DIGITAL | IOD_GSM_disk | D388
GSMUPS1AlarmOnBattery_om | DIGITAL | IOD_GSM_disk | D389
GSMUPS1AlarmLowBattery_om | DIGITAL | IOD_GSM_disk | D390
GSMUPS1AlarmDepletedBattery_om | DIGITAL | IOD_GSM_disk | D391
GSMUPS1AlarmTemperaturaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D392
GSMUPS1AlarmStanjeVhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D393
GSMUPS1AlarmStanjeIzhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D394
GSMUPS1AlarmIzhodPreobremenjen_om | DIGITAL | IOD_GSM_disk | D395
GSMUPS1AlarmOnBypass_om | DIGITAL | IOD_GSM_disk | D396
GSMUPS1AlarmBypassBad_om | DIGITAL | IOD_GSM_disk | D397
GSMUPS1AlarmIzhodOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D398
GSMUPS1AlarmUPSOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D399
GSMUPS1AlarmChargerFailed_om | DIGITAL | IOD_GSM_disk | D400
GSMUPS1AlarmUPSIzhodOff_om | DIGITAL | IOD_GSM_disk | D401
GSMUPS1AlarmUPSSystemOff_om | DIGITAL | IOD_GSM_disk | D402
GSMUPS1AlarmNapakaNaVentilatorju_om | DIGITAL | IOD_GSM_disk | D403
GSMUPS1AlarmNapakaNaVarovalki_om | DIGITAL | IOD_GSM_disk | D404
GSMUPS1AlarmSplosnaNapaka_om | DIGITAL | IOD_GSM_disk | D405
GSMUPS1AlarmDiagnosticTestFailed_om | DIGITAL | IOD_GSM_disk | D406
GSMUPS1AlarmCommunicationsLost_om | DIGITAL | IOD_GSM_disk | D407
GSMUPS1AlarmAwaitingPower_om | DIGITAL | IOD_GSM_disk | D408
GSMUPS1AlarmShutdownPending_om | DIGITAL | IOD_GSM_disk | D409
GSMUPS1AlarmShutdownImminent_om | DIGITAL | IOD_GSM_disk | D410
GSMUPS1AlarmTestInProgres_om | DIGITAL | IOD_GSM_disk | D411
GSMUPS1AlarmInverterError_om | DIGITAL | IOD_GSM_disk | D412
GSMN_UPS_V25_delovanje_om | DIGITAL | IOD_GSM_disk | D413
GSMN_UPS_V25_napaka_om | DIGITAL | IOD_GSM_disk | D414
GSMUPS2AlarmSlabaBaterija_om | DIGITAL | IOD_GSM_disk | D415
GSMUPS2AlarmOnBattery_om | DIGITAL | IOD_GSM_disk | D416
GSMUPS2AlarmLowBattery_om | DIGITAL | IOD_GSM_disk | D417
GSMUPS2AlarmDepletedBattery_om | DIGITAL | IOD_GSM_disk | D418
GSMUPS2AlarmTemperaturaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D419
GSMUPS2AlarmStanjeVhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D420
GSMUPS2AlarmStanjeIzhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D421
GSMUPS2AlarmIzhodPreobremenjen_om | DIGITAL | IOD_GSM_disk | D422
GSMUPS2AlarmOnBypass_om | DIGITAL | IOD_GSM_disk | D423
GSMUPS2AlarmBypassBad_om | DIGITAL | IOD_GSM_disk | D424
GSMUPS2AlarmIzhodOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D425
GSMUPS2AlarmUPSOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D426
GSMUPS2AlarmChargerFailed_om | DIGITAL | IOD_GSM_disk | D427
GSMUPS2AlarmUPSIzhodOff_om | DIGITAL | IOD_GSM_disk | D428
GSMUPS2AlarmUPSSystemOff_om | DIGITAL | IOD_GSM_disk | D429
GSMUPS2AlarmNapakaNaVentilatorju_om | DIGITAL | IOD_GSM_disk | D430
GSMUPS2AlarmNapakaNaVarovalki_om | DIGITAL | IOD_GSM_disk | D431
GSMUPS2AlarmSplosnaNapaka_om | DIGITAL | IOD_GSM_disk | D432
GSMUPS2AlarmDiagnosticTestFailed_om | DIGITAL | IOD_GSM_disk | D433
GSMUPS2AlarmCommunicationsLost_om | DIGITAL | IOD_GSM_disk | D434
GSMUPS2AlarmAwaitingPower_om | DIGITAL | IOD_GSM_disk | D435
GSMUPS2AlarmShutdownPending_om | DIGITAL | IOD_GSM_disk | D436
GSMUPS2AlarmShutdownImminent_om | DIGITAL | IOD_GSM_disk | D437
GSMUPS2AlarmTestInProgres_om | DIGITAL | IOD_GSM_disk | D438
GSMUPS2AlarmInverterError_om | DIGITAL | IOD_GSM_disk | D439
GSMUPS_MGE1UPS_error_om | DIGITAL | IOD_GSM_disk | D440
GSMUPS_MGE1BatteryLowWarning_om | DIGITAL | IOD_GSM_disk | D441
GSMUPS_MGE1DeviceVentilationFault_om | DIGITAL | IOD_GSM_disk | D442
GSMUPS_MGE1BatteryCompInProgress_om | DIGITAL | IOD_GSM_disk | D443
GSMUPS_MGE1BatteryTempOutOfToler_om | DIGITAL | IOD_GSM_disk | D444
GSMUPS_MGE1BatteryFuseFault_om | DIGITAL | IOD_GSM_disk | D445
GSMUPS_MGE1Mains1VoltOutOfToler_om | DIGITAL | IOD_GSM_disk | D446
GSMUPS_MGE1RectifierThermOverload_om | DIGITAL | IOD_GSM_disk | D447
GSMUPS_MGE1MaintenancePosition_om | DIGITAL | IOD_GSM_disk | D448
GSMUPS_MGE1ChargerGeneralFault_om | DIGITAL | IOD_GSM_disk | D449
GSMUPS_MGE1BatteryChargedState_om | DIGITAL | IOD_GSM_disk | D450
GSMUPS_MGE1InverterOverload_om | DIGITAL | IOD_GSM_disk | D451
GSMUPS_MGE1InverterThermalOverload_om | DIGITAL | IOD_GSM_disk | D452
GSMUPS_MGE1OutputThermalOverload_om | DIGITAL | IOD_GSM_disk | D453
GSMUPS_MGE1OutputOverload_om | DIGITAL | IOD_GSM_disk | D454
GSMUPS_MGE1InverterFuseFault_om | DIGITAL | IOD_GSM_disk | D455
GSMUPS_MGE1OutputInShortCircuit_om | DIGITAL | IOD_GSM_disk | D456
GSMNapakaSenzorVlagaHIA1_om | DIGITAL | IOD_GSM_disk | D457
GSMNapakaSenzorVlagaHIA2_om | DIGITAL | IOD_GSM_disk | D458
GSMNapakaSenzorVlagaHIA3_om | DIGITAL | IOD_GSM_disk | D459
GSMNapakaSenzorVlagaHIA4_om | DIGITAL | IOD_GSM_disk | D460
GSMNapakaSenzorVlagaHIA5_om | DIGITAL | IOD_GSM_disk | D461
GSMNapakaSenzorVlagaHIA6_om | DIGITAL | IOD_GSM_disk | D462
GSMNapakaSenzorVlagaHIA7_om | DIGITAL | IOD_GSM_disk | D463
GSMNapakaTSTempTIA1_om | DIGITAL | IOD_GSM_disk | D464
GSMNapakaTSTempTIA2_om | DIGITAL | IOD_GSM_disk | D465
GSMNapakaTSTempTIA3_om | DIGITAL | IOD_GSM_disk | D466
GSMNapakaTSTempTIA4_om | DIGITAL | IOD_GSM_disk | D467
GSMNapakaTSTempTIA5_om | DIGITAL | IOD_GSM_disk | D468
GSMNapakaTSTempTIA6_om | DIGITAL | IOD_GSM_disk | D469
GSMNapakaTSTempTIA7_om | DIGITAL | IOD_GSM_disk | D470
GSMTIA1_previs_temp_om | DIGITAL | IOD_GSM_disk | D471
GSMTIA2_previs_temp_om | DIGITAL | IOD_GSM_disk | D472
GSMTIA3_previs_temp_om | DIGITAL | IOD_GSM_disk | D473
GSMTIA4_previs_temp_om | DIGITAL | IOD_GSM_disk | D474
GSMTIA5_previs_temp_om | DIGITAL | IOD_GSM_disk | D475
GSMTIA6_previs_temp_om | DIGITAL | IOD_GSM_disk | D476
GSMTIA7_previs_temp_om | DIGITAL | IOD_GSM_disk | D477
GSMPMM2OverCurrentBetw_VirA_om | DIGITAL | IOD_GSM_disk | D478
GSMPMM2OverCurrentBetw_VirB_om | DIGITAL | IOD_GSM_disk | D479
GSMPMM2OverCurrentOver_VirA_om | DIGITAL | IOD_GSM_disk | D480
GSMPMM2OverCurrentOver_VirB_om | DIGITAL | IOD_GSM_disk | D481
GSMPMM2OverCurrentBetw_VirA | DIGITAL | IOD_GSM_disk | D482
GSMPMM2OverCurrentBetw_VirB | DIGITAL | IOD_GSM_disk | D483
GSMPMM2OverCurrentOver_VirA | DIGITAL | IOD_GSM_disk | D484
GSMPMM2OverCurrentOver_VirB | DIGITAL | IOD_GSM_disk | D485
GSMAlarmPMM1VirATokPrevisok_om | DIGITAL | IOD_GSM_disk | D486
GSMAlarmPMM1VirATokVisok_om | DIGITAL | IOD_GSM_disk | D487
GSMAlarmPMM1VirBTokPrevisok_om | DIGITAL | IOD_GSM_disk | D488
GSMAlarmPMM1VirBTokVisok_om | DIGITAL | IOD_GSM_disk | D489
GSMAlarmPMM2x17nad801_om | DIGITAL | IOD_GSM_disk | D490
GSMAlarmPMM2x17nad802_om | DIGITAL | IOD_GSM_disk | D491
GSMAlarmPMM2x17nad803_om | DIGITAL | IOD_GSM_disk | D492
GSMAlarmPMM2x17nad804_om | DIGITAL | IOD_GSM_disk | D493
GSMAlarmPMM2x17nad805_om | DIGITAL | IOD_GSM_disk | D494
GSMAlarmPMM2x17nad806_om | DIGITAL | IOD_GSM_disk | D495
GSMAlarmPMM2x17nad807_om | DIGITAL | IOD_GSM_disk | D496
GSMAlarmPMM2x17nad808_om | DIGITAL | IOD_GSM_disk | D497
GSMAlarmPMM2x17nad809_om | DIGITAL | IOD_GSM_disk | D498
GSMAlarmPMM2x17nad8010_om | DIGITAL | IOD_GSM_disk | D499
GSMAlarmPMM2x17nad8011_om | DIGITAL | IOD_GSM_disk | D500
GSMAlarmPMM2x17nad8012_om | DIGITAL | IOD_GSM_disk | D501
GSMAlarmPMM2x17nad8013_om | DIGITAL | IOD_GSM_disk | D502
GSMAlarmPMM2x17nad8014_om | DIGITAL | IOD_GSM_disk | D503
GSMAlarmPMM2x17nad8015_om | DIGITAL | IOD_GSM_disk | D504
GSMAlarmPMM2x17nad8016_om | DIGITAL | IOD_GSM_disk | D505
GSMAlarmPMM2x17nad8017_om | DIGITAL | IOD_GSM_disk | D506
GSMAlarmPMM2x17nad8018_om | DIGITAL | IOD_GSM_disk | D507
GSMAlarmPMM2x17nad8019_om | DIGITAL | IOD_GSM_disk | D508
GSMAlarmPMM2x17nad8020_om | DIGITAL | IOD_GSM_disk | D509
GSMAlarmPMM2x17nad8021_om | DIGITAL | IOD_GSM_disk | D510
GSMAlarmPMM2x17nad8022_om | DIGITAL | IOD_GSM_disk | D511
GSMAlarmPMM2x17nad8023_om | DIGITAL | IOD_GSM_disk | D512
GSMAlarmPMM2x17nad8024_om | DIGITAL | IOD_GSM_disk | D513
GSMAlarmPMM2x17nad8025_om | DIGITAL | IOD_GSM_disk | D514
GSMAlarmPMM2x17nad8026_om | DIGITAL | IOD_GSM_disk | D515
GSMAlarmPMM2x17nad8027_om | DIGITAL | IOD_GSM_disk | D516
GSMAlarmPMM2x17nad8028_om | DIGITAL | IOD_GSM_disk | D517
GSMOpozoriloPMM2x17med60in801_om | DIGITAL | IOD_GSM_disk | D518
GSMOpozoriloPMM2x17med60in802_om | DIGITAL | IOD_GSM_disk | D519
GSMOpozoriloPMM2x17med60in803_om | DIGITAL | IOD_GSM_disk | D520
GSMOpozoriloPMM2x17med60in804_om | DIGITAL | IOD_GSM_disk | D521
GSMOpozoriloPMM2x17med60in805_om | DIGITAL | IOD_GSM_disk | D522
GSMOpozoriloPMM2x17med60in806_om | DIGITAL | IOD_GSM_disk | D523
GSMOpozoriloPMM2x17med60in807_om | DIGITAL | IOD_GSM_disk | D524
GSMOpozoriloPMM2x17med60in808_om | DIGITAL | IOD_GSM_disk | D525
GSMOpozoriloPMM2x17med60in809_om | DIGITAL | IOD_GSM_disk | D526
GSMOpozoriloPMM2x17med60in8010_om | DIGITAL | IOD_GSM_disk | D527
GSMOpozoriloPMM2x17med60in8011_om | DIGITAL | IOD_GSM_disk | D528
GSMOpozoriloPMM2x17med60in8012_om | DIGITAL | IOD_GSM_disk | D529
GSMOpozoriloPMM2x17med60in8013_om | DIGITAL | IOD_GSM_disk | D530
GSMOpozoriloPMM2x17med60in8014_om | DIGITAL | IOD_GSM_disk | D531
GSMOpozoriloPMM2x17med60in8015_om | DIGITAL | IOD_GSM_disk | D532
GSMOpozoriloPMM2x17med60in8016_om | DIGITAL | IOD_GSM_disk | D533
GSMOpozoriloPMM2x17med60in8017_om | DIGITAL | IOD_GSM_disk | D534
GSMOpozoriloPMM2x17med60in8018_om | DIGITAL | IOD_GSM_disk | D535
GSMOpozoriloPMM2x17med60in8019_om | DIGITAL | IOD_GSM_disk | D536
GSMOpozoriloPMM2x17med60in8020_om | DIGITAL | IOD_GSM_disk | D537
GSMOpozoriloPMM2x17med60in8021_om | DIGITAL | IOD_GSM_disk | D538
GSMOpozoriloPMM2x17med60in8022_om | DIGITAL | IOD_GSM_disk | D539
GSMOpozoriloPMM2x17med60in8023_om | DIGITAL | IOD_GSM_disk | D540
GSMOpozoriloPMM2x17med60in8024_om | DIGITAL | IOD_GSM_disk | D541
GSMOpozoriloPMM2x17med60in8025_om | DIGITAL | IOD_GSM_disk | D542
GSMOpozoriloPMM2x17med60in8026_om | DIGITAL | IOD_GSM_disk | D543
GSMOpozoriloPMM2x17med60in8027_om | DIGITAL | IOD_GSM_disk | D544
GSMOpozoriloPMM2x17med60in8028_om | DIGITAL | IOD_GSM_disk | D545
GSMN_UPS_A_V23_delovanje_om | DIGITAL | IOD_GSM_disk | D546
GSMN_UPS_A_V23_napaka_om | DIGITAL | IOD_GSM_disk | D547
GSMUPS1Napaka_om | DIGITAL | IOD_GSM_disk | D548
AGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D600[300]
BGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D900[300]
CGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D1200[300]
DGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D1500[300]
EGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D1800[300]
FGSM_omogoci_sms | DIGITAL | IOD_GSM_disk | D2100[300]
GSM_Anali_razlika_dnevnaCirc1 | LONG | IOD_GSM_disk | L290
GSM_Anali_razlika_tedenCirc1 | LONG | IOD_GSM_disk | L292
GSM_Anali_razlika_mesCirc1 | LONG | IOD_GSM_disk | L294
GSMUserloggedIn_mem | DIGITAL | IOD_GSM_mem | D572
GSM_ComSCADA_stevec1 | INT | IOD_GSM_mem | I600
GSM_ComSCADA_stevec2 | INT | IOD_GSM_mem | I601
GSM_ComSCADA_stevec3 | INT | IOD_GSM_mem | I602
GSM_ComSCADA_stevec4 | INT | IOD_GSM_mem | I603
GSMUPS2Napaka_om | DIGITAL | IOD_GSM_disk | D549
GSMUPS3AlarmSlabaBaterija_om | DIGITAL | IOD_GSM_disk | D2400
GSMUPS3AlarmOnBattery_om | DIGITAL | IOD_GSM_disk | D2401
GSMUPS3AlarmLowBattery_om | DIGITAL | IOD_GSM_disk | D2402
GSMUPS3AlarmDepletedBattery_om | DIGITAL | IOD_GSM_disk | D2403
GSMUPS3AlarmTemperaturaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D2404
GSMUPS3AlarmStanjeVhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D2405
GSMUPS3AlarmStanjeIzhodaIzvenToleranc_om | DIGITAL | IOD_GSM_disk | D2406
GSMUPS3AlarmIzhodPreobremenjen_om | DIGITAL | IOD_GSM_disk | D2407
GSMUPS3AlarmOnBypass_om | DIGITAL | IOD_GSM_disk | D2408
GSMUPS3AlarmBypassBad_om | DIGITAL | IOD_GSM_disk | D2409
GSMUPS3AlarmIzhodOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D2410
GSMUPS3AlarmUPSOffKotZahtevano_om | DIGITAL | IOD_GSM_disk | D2411
GSMUPS3AlarmChargerFailed_om | DIGITAL | IOD_GSM_disk | D2412
GSMUPS3AlarmUPSIzhodOff_om | DIGITAL | IOD_GSM_disk | D2413
GSMUPS3AlarmUPSSystemOff_om | DIGITAL | IOD_GSM_disk | D2414
GSMUPS3AlarmNapakaNaVentilatorju_om | DIGITAL | IOD_GSM_disk | D2415
GSMUPS3AlarmNapakaNaVarovalki_om | DIGITAL | IOD_GSM_disk | D2416
GSMUPS3AlarmSplosnaNapaka_om | DIGITAL | IOD_GSM_disk | D2417
GSMUPS3AlarmDiagnosticTestFailed_om | DIGITAL | IOD_GSM_disk | D2418
GSMUPS3AlarmCommunicationsLost_om | DIGITAL | IOD_GSM_disk | D2419
GSMUPS3AlarmAwaitingPower_om | DIGITAL | IOD_GSM_disk | D2420
GSMUPS3AlarmShutdownPending_om | DIGITAL | IOD_GSM_disk | D2421
GSMUPS3AlarmShutdownImminent_om | DIGITAL | IOD_GSM_disk | D2422
GSMUPS3AlarmTestInProgres_om | DIGITAL | IOD_GSM_disk | D2423
GSMUPS3AlarmInverterError_om | DIGITAL | IOD_GSM_disk | D2424
GSMUPS3Napaka_om | DIGITAL | IOD_GSM_disk | D2425
GSMGSM_PozCent_napaka_om | DIGITAL | IOD_GSM_disk | D2426
GSMGSM_PozSenzor_okvara_om | DIGITAL | IOD_GSM_disk | D2427
GSMGSM_Gasenje_alarm_om | DIGITAL | IOD_GSM_disk | D2428
GSMAGR_PozCent_napaka_om | DIGITAL | IOD_GSM_disk | D2429
GSMAGR_PozSenzor_okvara_om | DIGITAL | IOD_GSM_disk | D2430
GSMAGR_Gasenje_alarm_om | DIGITAL | IOD_GSM_disk | D2431
GSMCirc_Vpis_Dnevne_energija_scada1_mem | DIGITAL | IOD_GSM_disk | D3000
GSMCirc_Vpis_Dnevne_energija_scada2_mem | DIGITAL | IOD_GSM_disk | D3001
GSMCirc_Vpis_Tedenska_energija_scada1_mem | DIGITAL | IOD_GSM_disk | D3002
GSMCirc_Vpis_Tedenska_energija_scada2_mem | DIGITAL | IOD_GSM_disk | D3003
GSMCirc_Vpis_Mesecna_energija_scada1_mem | DIGITAL | IOD_GSM_disk | D3004
GSMCirc_Vpis_Mesecna_energija_scada2_mem | DIGITAL | IOD_GSM_disk | D3005
GSMPMM2VirACurrent1_med60in80 | DIGITAL | IOD_GSM_disk | D3006
GSMPMM2VirACurrent2_med60in80 | DIGITAL | IOD_GSM_disk | D3007
GSMPMM2VirACurrent3_med60in80 | DIGITAL | IOD_GSM_disk | D3008
GSMPMM2VirACurrent4_med60in80 | DIGITAL | IOD_GSM_disk | D3009
GSMPMM2VirACurrent5_med60in80 | DIGITAL | IOD_GSM_disk | D3010
GSMPMM2VirACurrent6_med60in80 | DIGITAL | IOD_GSM_disk | D3011
GSMPMM2VirACurrent7_med60in80 | DIGITAL | IOD_GSM_disk | D3012
GSMPMM2VirACurrent8_med60in80 | DIGITAL | IOD_GSM_disk | D3013
GSMPMM2VirACurrent9_med60in80 | DIGITAL | IOD_GSM_disk | D3014
GSMPMM2VirACurrent10_med60in80 | DIGITAL | IOD_GSM_disk | D3015
GSMPMM2VirACurrent11_med60in80 | DIGITAL | IOD_GSM_disk | D3016
GSMPMM2VirACurrent12_med60in80 | DIGITAL | IOD_GSM_disk | D3017
GSMPMM2VirACurrent13_med60in80 | DIGITAL | IOD_GSM_disk | D3018
GSMPMM2VirACurrent14_med60in80 | DIGITAL | IOD_GSM_disk | D3019
GSMPMM2VirACurrent15_med60in80 | DIGITAL | IOD_GSM_disk | D3020
GSMPMM2VirACurrent16_med60in80 | DIGITAL | IOD_GSM_disk | D3021
GSMPMM2VirACurrent17_med60in80 | DIGITAL | IOD_GSM_disk | D3022
GSMPMM2VirACurrent18_med60in80 | DIGITAL | IOD_GSM_disk | D3023
GSMPMM2VirACurrent19_med60in80 | DIGITAL | IOD_GSM_disk | D3024
GSMPMM2VirACurrent20_med60in80 | DIGITAL | IOD_GSM_disk | D3025
GSMPMM2VirACurrent21_med60in80 | DIGITAL | IOD_GSM_disk | D3026
GSMPMM2VirACurrent22_med60in80 | DIGITAL | IOD_GSM_disk | D3027
GSMPMM2VirACurrent23_med60in80 | DIGITAL | IOD_GSM_disk | D3028
GSMPMM2VirACurrent24_med60in80 | DIGITAL | IOD_GSM_disk | D3029
GSMPMM2VirACurrent25_med60in80 | DIGITAL | IOD_GSM_disk | D3030
GSMPMM2VirACurrent26_med60in80 | DIGITAL | IOD_GSM_disk | D3031
GSMPMM2VirACurrent27_med60in80 | DIGITAL | IOD_GSM_disk | D3032
GSMPMM2VirACurrent28_med60in80 | DIGITAL | IOD_GSM_disk | D3033
GSMPMM2VirACurrent29_med60in80 | DIGITAL | IOD_GSM_disk | D3034
GSMPMM2VirACurrent30_med60in80 | DIGITAL | IOD_GSM_disk | D3035
GSMPMM2VirACurrent31_med60in80 | DIGITAL | IOD_GSM_disk | D3036
GSMPMM2VirACurrent32_med60in80 | DIGITAL | IOD_GSM_disk | D3037
GSMPMM2VirACurrent33_med60in80 | DIGITAL | IOD_GSM_disk | D3038
GSMPMM2VirACurrent34_med60in80 | DIGITAL | IOD_GSM_disk | D3039
GSMPMM2VirACurrent35_med60in80 | DIGITAL | IOD_GSM_disk | D3040
GSMPMM2VirACurrent36_med60in80 | DIGITAL | IOD_GSM_disk | D3041
GSMPMM2VirACurrent37_med60in80 | DIGITAL | IOD_GSM_disk | D3042
GSMPMM2VirACurrent38_med60in80 | DIGITAL | IOD_GSM_disk | D3043
GSMPMM2VirACurrent39_med60in80 | DIGITAL | IOD_GSM_disk | D3044
GSMPMM2VirACurrent40_med60in80 | DIGITAL | IOD_GSM_disk | D3045
GSMPMM2VirACurrent41_med60in80 | DIGITAL | IOD_GSM_disk | D3046
GSMPMM2VirACurrent42_med60in80 | DIGITAL | IOD_GSM_disk | D3047
GSMPMM2VirACurrent43_med60in80 | DIGITAL | IOD_GSM_disk | D3048
GSMPMM2VirACurrent44_med60in80 | DIGITAL | IOD_GSM_disk | D3049
GSMPMM2VirACurrent1_nad80 | DIGITAL | IOD_GSM_disk | D3050
GSMPMM2VirACurrent2_nad80 | DIGITAL | IOD_GSM_disk | D3051
GSMPMM2VirACurrent3_nad80 | DIGITAL | IOD_GSM_disk | D3052
GSMPMM2VirACurrent4_nad80 | DIGITAL | IOD_GSM_disk | D3053
GSMPMM2VirACurrent5_nad80 | DIGITAL | IOD_GSM_disk | D3054
GSMPMM2VirACurrent6_nad80 | DIGITAL | IOD_GSM_disk | D3055
GSMPMM2VirACurrent7_nad80 | DIGITAL | IOD_GSM_disk | D3056
GSMPMM2VirACurrent8_nad80 | DIGITAL | IOD_GSM_disk | D3057
GSMPMM2VirACurrent9_nad80 | DIGITAL | IOD_GSM_disk | D3058
GSMPMM2VirACurrent10_nad80 | DIGITAL | IOD_GSM_disk | D3059
GSMPMM2VirACurrent11_nad80 | DIGITAL | IOD_GSM_disk | D3060
GSMPMM2VirACurrent12_nad80 | DIGITAL | IOD_GSM_disk | D3061
GSMPMM2VirACurrent13_nad80 | DIGITAL | IOD_GSM_disk | D3062
GSMPMM2VirACurrent14_nad80 | DIGITAL | IOD_GSM_disk | D3063
GSMPMM2VirACurrent15_nad80 | DIGITAL | IOD_GSM_disk | D3064
GSMPMM2VirACurrent16_nad80 | DIGITAL | IOD_GSM_disk | D3065
GSMPMM2VirACurrent17_nad80 | DIGITAL | IOD_GSM_disk | D3066
GSMPMM2VirACurrent18_nad80 | DIGITAL | IOD_GSM_disk | D3067
GSMPMM2VirACurrent19_nad80 | DIGITAL | IOD_GSM_disk | D3068
GSMPMM2VirACurrent20_nad80 | DIGITAL | IOD_GSM_disk | D3069
GSMPMM2VirACurrent21_nad80 | DIGITAL | IOD_GSM_disk | D3070
GSMPMM2VirACurrent22_nad80 | DIGITAL | IOD_GSM_disk | D3071
GSMPMM2VirACurrent23_nad80 | DIGITAL | IOD_GSM_disk | D3072
GSMPMM2VirACurrent24_nad80 | DIGITAL | IOD_GSM_disk | D3073
GSMPMM2VirACurrent25_nad80 | DIGITAL | IOD_GSM_disk | D3074
GSMPMM2VirACurrent26_nad80 | DIGITAL | IOD_GSM_disk | D3075
GSMPMM2VirACurrent27_nad80 | DIGITAL | IOD_GSM_disk | D3076
GSMPMM2VirACurrent28_nad80 | DIGITAL | IOD_GSM_disk | D3077
GSMPMM2VirACurrent29_nad80 | DIGITAL | IOD_GSM_disk | D3078
GSMPMM2VirACurrent30_nad80 | DIGITAL | IOD_GSM_disk | D3079
GSMPMM2VirACurrent31_nad80 | DIGITAL | IOD_GSM_disk | D3080
GSMPMM2VirACurrent32_nad80 | DIGITAL | IOD_GSM_disk | D3081
GSMPMM2VirACurrent33_nad80 | DIGITAL | IOD_GSM_disk | D3082
GSMPMM2VirACurrent34_nad80 | DIGITAL | IOD_GSM_disk | D3083
GSMPMM2VirACurrent35_nad80 | DIGITAL | IOD_GSM_disk | D3084
GSMPMM2VirACurrent36_nad80 | DIGITAL | IOD_GSM_disk | D3085
GSMPMM2VirACurrent37_nad80 | DIGITAL | IOD_GSM_disk | D3086
GSMPMM2VirACurrent38_nad80 | DIGITAL | IOD_GSM_disk | D3087
GSMPMM2VirACurrent39_nad80 | DIGITAL | IOD_GSM_disk | D3088
GSMPMM2VirACurrent40_nad80 | DIGITAL | IOD_GSM_disk | D3089
GSMPMM2VirACurrent41_nad80 | DIGITAL | IOD_GSM_disk | D3090
GSMPMM2VirACurrent42_nad80 | DIGITAL | IOD_GSM_disk | D3091
GSMPMM2VirACurrent43_nad80 | DIGITAL | IOD_GSM_disk | D3092
GSMPMM2VirACurrent44_nad80 | DIGITAL | IOD_GSM_disk | D3093
GSMPMM2PoljeVirATok1_16_nad80 | DIGITAL | IOD_GSM_disk | D3100[16]
GSMPMM2PoljeVirATok17_32_nad80 | DIGITAL | IOD_GSM_disk | D3117[16]
GSMPMM2PoljeVirATok33_44_nad80 | DIGITAL | IOD_GSM_disk | D3134[16]
GSMPMM2PoljeVirBTok1_16_nad80 | DIGITAL | IOD_GSM_disk | D3151[16]
GSMPMM2PoljeVirBTok17_32_nad80 | DIGITAL | IOD_GSM_disk | D3168[16]
GSMPMM2PoljeVirBTok33_44_nad80 | DIGITAL | IOD_GSM_disk | D3185[16]
GSMPMM2PoljeVirATok1_16_med60_80 | DIGITAL | IOD_GSM_disk | D3202[16]
GSMPMM2PoljeVirATok17_32_med60_80 | DIGITAL | IOD_GSM_disk | D3219[16]
GSMPMM2PoljeVirATok33_44_med60_80 | DIGITAL | IOD_GSM_disk | D3236[16]
GSMPMM2PoljeVirBTok1_16_med60_80 | DIGITAL | IOD_GSM_disk | D3253[16]
GSMPMM2PoljeVirBTok17_32_med60_80 | DIGITAL | IOD_GSM_disk | D3270[16]
GSMPMM2PoljeVirBTok33_44_med60_80 | DIGITAL | IOD_GSM_disk | D3287[16]
GSMPrikaziPMM | DIGITAL | IOD_GSM_disk | D3303
GSMPMM_2x63_VirB_zavihek | DIGITAL | IOD_GSM_disk | D3304
GSMPMM_2x63_VirA_zavihek | DIGITAL | IOD_GSM_disk | D3305
GSMPMM2OverCurrentBetw1_VirA | DIGITAL | IOD_GSM_disk | D3306
GSMPMM2OverCurrentBetw1_VirB | DIGITAL | IOD_GSM_disk | D3307
GSMPMM2OverCurrentOver1_VirA | DIGITAL | IOD_GSM_disk | D3308
GSMPMM2OverCurrentOver1_VirB | DIGITAL | IOD_GSM_disk | D3309
GSMPMM2OverCurrentBetw1_VirB_Omogoci | DIGITAL | IOD_GSM_disk | D3310
GSMPMM2OverCurrentBetw1_VirA_Omogoci | DIGITAL | IOD_GSM_disk | D3311
GSMPMM2OverCurrentOver1_VirB_Omogoci | DIGITAL | IOD_GSM_disk | D3312
GSMPMM2OverCurrentOver1_VirA_Omogoci | DIGITAL | IOD_GSM_disk | D3313
GSMPMM1OverVoltage_Omogoci | DIGITAL | IOD_GSM_disk | D3314
GSMErrComPMM2_Omogoci | DIGITAL | IOD_GSM_disk | D3315
GSMPMM2VirACurrent1_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3316
GSMPMM2VirACurrent2_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3317
GSMPMM2VirACurrent3_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3318
GSMPMM2VirACurrent4_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3319
GSMPMM2VirACurrent5_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3320
GSMPMM2VirACurrent6_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3321
GSMPMM2VirACurrent7_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3322
GSMPMM2VirACurrent8_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3323
GSMPMM2VirACurrent9_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3324
GSMPMM2VirACurrent10_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3325
GSMPMM2VirACurrent11_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3326
GSMPMM2VirACurrent12_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3327
GSMPMM2VirACurrent13_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3328
GSMPMM2VirACurrent14_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3329
GSMPMM2VirACurrent15_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3330
GSMPMM2VirACurrent16_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3331
GSMPMM2VirACurrent17_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3332
GSMPMM2VirACurrent18_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3333
GSMPMM2VirACurrent19_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3334
GSMPMM2VirACurrent20_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3335
GSMPMM2VirACurrent21_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3336
GSMPMM2VirACurrent22_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3337
GSMPMM2VirACurrent23_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3338
GSMPMM2VirACurrent24_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3339
GSMPMM2VirACurrent25_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3340
GSMPMM2VirACurrent26_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3341
GSMPMM2VirACurrent27_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3342
GSMPMM2VirACurrent28_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3343
GSMPMM2VirACurrent29_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3344
GSMPMM2VirACurrent30_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3345
GSMPMM2VirACurrent31_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3346
GSMPMM2VirACurrent32_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3347
GSMPMM2VirACurrent33_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3348
GSMPMM2VirACurrent34_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3349
GSMPMM2VirACurrent35_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3350
GSMPMM2VirACurrent36_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3351
GSMPMM2VirACurrent37_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3352
GSMPMM2VirACurrent38_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3353
GSMPMM2VirACurrent39_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3354
GSMPMM2VirACurrent40_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3355
GSMPMM2VirACurrent41_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3356
GSMPMM2VirACurrent42_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3357
GSMPMM2VirACurrent43_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3358
GSMPMM2VirACurrent44_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3359
GSMPMM2VirACurrent1_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3360
GSMPMM2VirACurrent2_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3361
GSMPMM2VirACurrent3_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3362
GSMPMM2VirACurrent4_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3363
GSMPMM2VirACurrent5_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3364
GSMPMM2VirACurrent6_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3365
GSMPMM2VirACurrent7_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3366
GSMPMM2VirACurrent8_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3367
GSMPMM2VirACurrent9_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3368
GSMPMM2VirACurrent10_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3369
GSMPMM2VirACurrent11_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3370
GSMPMM2VirACurrent12_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3371
GSMPMM2VirACurrent13_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3372
GSMPMM2VirACurrent14_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3373
GSMPMM2VirACurrent15_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3374
GSMPMM2VirACurrent16_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3375
GSMPMM2VirACurrent17_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3376
GSMPMM2VirACurrent18_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3377
GSMPMM2VirACurrent19_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3378
GSMPMM2VirACurrent20_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3379
GSMPMM2VirACurrent21_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3380
GSMPMM2VirACurrent22_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3381
GSMPMM2VirACurrent23_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3382
GSMPMM2VirACurrent24_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3383
GSMPMM2VirACurrent25_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3384
GSMPMM2VirACurrent26_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3385
GSMPMM2VirACurrent27_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3386
GSMPMM2VirACurrent28_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3387
GSMPMM2VirACurrent29_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3388
GSMPMM2VirACurrent30_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3389
GSMPMM2VirACurrent31_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3390
GSMPMM2VirACurrent32_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3391
GSMPMM2VirACurrent33_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3392
GSMPMM2VirACurrent34_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3393
GSMPMM2VirACurrent35_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3394
GSMPMM2VirACurrent36_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3395
GSMPMM2VirACurrent37_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3396
GSMPMM2VirACurrent38_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3397
GSMPMM2VirACurrent39_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3398
GSMPMM2VirACurrent40_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3399
GSMPMM2VirACurrent41_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3400
GSMPMM2VirACurrent42_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3401
GSMPMM2VirACurrent43_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3402
GSMPMM2VirACurrent44_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3403
GSMPMM2OverCurrentBetw1_VirB_1 | DIGITAL | IOD_GSM_disk | D3404
GSMPMM2OverCurrentBetw1_VirA_1 | DIGITAL | IOD_GSM_disk | D3405
GSMPMM2OverCurrentOver1_VirB_1 | DIGITAL | IOD_GSM_disk | D3406
GSMPMM2OverCurrentOver1_VirA_1 | DIGITAL | IOD_GSM_disk | D3407
GSMPMM2OverCurrentBetw1_VirB_2 | DIGITAL | IOD_GSM_disk | D3408
GSMPMM2OverCurrentBetw1_VirA_2 | DIGITAL | IOD_GSM_disk | D3409
GSMPMM2OverCurrentBetw1_VirB_3 | DIGITAL | IOD_GSM_disk | D3410
GSMPMM2OverCurrentBetw1_VirA_3 | DIGITAL | IOD_GSM_disk | D3411
GSMPMM2OverCurrentOver1_VirB_2 | DIGITAL | IOD_GSM_disk | D3412
GSMPMM2OverCurrentOver1_VirA_2 | DIGITAL | IOD_GSM_disk | D3413
GSMPMM2OverCurrentOver1_VirB_3 | DIGITAL | IOD_GSM_disk | D3414
GSMPMM2OverCurrentOver1_VirA_3 | DIGITAL | IOD_GSM_disk | D3415
GSMVsotaVirB_1_16B_med | INT | IOD_GSM_disk | I604
GSMVsotaVirB_17_32B_med | INT | IOD_GSM_disk | I605
GSMVsotaVirB_33_44B_med | INT | IOD_GSM_disk | I606
GSMVsotaVirA_1_16A_med | INT | IOD_GSM_disk | I607
GSMVsotaVirA_17_32A_med | INT | IOD_GSM_disk | I608
GSMVsotaVirA_33_44A_med | INT | IOD_GSM_disk | I609
GSMVsotaVirB_1_16B_nad | INT | IOD_GSM_disk | I610
GSMVsotaVirB_17_32B_nad | INT | IOD_GSM_disk | I611
GSMVsotaVirB_33_44B_nad | INT | IOD_GSM_disk | I612
GSMVsotaVirA_1_16A_nad | INT | IOD_GSM_disk | I613
GSMVsotaVirA_17_32A_nad | INT | IOD_GSM_disk | I614
GSMVsotaVirA_33_44A_nad | INT | IOD_GSM_disk | I615
GSMPMM2VirBCurrent1_med60in80 | DIGITAL | IOD_GSM_disk | D3416
GSMPMM2VirBCurrent2_med60in80 | DIGITAL | IOD_GSM_disk | D3417
GSMPMM2VirBCurrent3_med60in80 | DIGITAL | IOD_GSM_disk | D3418
GSMPMM2VirBCurrent4_med60in80 | DIGITAL | IOD_GSM_disk | D3419
GSMPMM2VirBCurrent5_med60in80 | DIGITAL | IOD_GSM_disk | D3420
GSMPMM2VirBCurrent6_med60in80 | DIGITAL | IOD_GSM_disk | D3421
GSMPMM2VirBCurrent7_med60in80 | DIGITAL | IOD_GSM_disk | D3422
GSMPMM2VirBCurrent8_med60in80 | DIGITAL | IOD_GSM_disk | D3423
GSMPMM2VirBCurrent9_med60in80 | DIGITAL | IOD_GSM_disk | D3424
GSMPMM2VirBCurrent10_med60in80 | DIGITAL | IOD_GSM_disk | D3425
GSMPMM2VirBCurrent11_med60in80 | DIGITAL | IOD_GSM_disk | D3426
GSMPMM2VirBCurrent12_med60in80 | DIGITAL | IOD_GSM_disk | D3427
GSMPMM2VirBCurrent13_med60in80 | DIGITAL | IOD_GSM_disk | D3428
GSMPMM2VirBCurrent14_med60in80 | DIGITAL | IOD_GSM_disk | D3429
GSMPMM2VirBCurrent15_med60in80 | DIGITAL | IOD_GSM_disk | D3430
GSMPMM2VirBCurrent16_med60in80 | DIGITAL | IOD_GSM_disk | D3431
GSMPMM2VirBCurrent17_med60in80 | DIGITAL | IOD_GSM_disk | D3432
GSMPMM2VirBCurrent18_med60in80 | DIGITAL | IOD_GSM_disk | D3433
GSMPMM2VirBCurrent19_med60in80 | DIGITAL | IOD_GSM_disk | D3434
GSMPMM2VirBCurrent20_med60in80 | DIGITAL | IOD_GSM_disk | D3435
GSMPMM2VirBCurrent21_med60in80 | DIGITAL | IOD_GSM_disk | D3436
GSMPMM2VirBCurrent22_med60in80 | DIGITAL | IOD_GSM_disk | D3437
GSMPMM2VirBCurrent23_med60in80 | DIGITAL | IOD_GSM_disk | D3438
GSMPMM2VirBCurrent24_med60in80 | DIGITAL | IOD_GSM_disk | D3439
GSMPMM2VirBCurrent25_med60in80 | DIGITAL | IOD_GSM_disk | D3440
GSMPMM2VirBCurrent26_med60in80 | DIGITAL | IOD_GSM_disk | D3441
GSMPMM2VirBCurrent27_med60in80 | DIGITAL | IOD_GSM_disk | D3442
GSMPMM2VirBCurrent28_med60in80 | DIGITAL | IOD_GSM_disk | D3443
GSMPMM2VirBCurrent29_med60in80 | DIGITAL | IOD_GSM_disk | D3444
GSMPMM2VirBCurrent30_med60in80 | DIGITAL | IOD_GSM_disk | D3445
GSMPMM2VirBCurrent31_med60in80 | DIGITAL | IOD_GSM_disk | D3446
GSMPMM2VirBCurrent32_med60in80 | DIGITAL | IOD_GSM_disk | D3447
GSMPMM2VirBCurrent33_med60in80 | DIGITAL | IOD_GSM_disk | D3448
GSMPMM2VirBCurrent34_med60in80 | DIGITAL | IOD_GSM_disk | D3449
GSMPMM2VirBCurrent35_med60in80 | DIGITAL | IOD_GSM_disk | D3450
GSMPMM2VirBCurrent36_med60in80 | DIGITAL | IOD_GSM_disk | D3451
GSMPMM2VirBCurrent37_med60in80 | DIGITAL | IOD_GSM_disk | D3452
GSMPMM2VirBCurrent38_med60in80 | DIGITAL | IOD_GSM_disk | D3453
GSMPMM2VirBCurrent39_med60in80 | DIGITAL | IOD_GSM_disk | D3454
GSMPMM2VirBCurrent40_med60in80 | DIGITAL | IOD_GSM_disk | D3455
GSMPMM2VirBCurrent41_med60in80 | DIGITAL | IOD_GSM_disk | D3456
GSMPMM2VirBCurrent42_med60in80 | DIGITAL | IOD_GSM_disk | D3457
GSMPMM2VirBCurrent43_med60in80 | DIGITAL | IOD_GSM_disk | D3458
GSMPMM2VirBCurrent44_med60in80 | DIGITAL | IOD_GSM_disk | D3459
GSMPMM2VirBCurrent1_nad80 | DIGITAL | IOD_GSM_disk | D3460
GSMPMM2VirBCurrent2_nad80 | DIGITAL | IOD_GSM_disk | D3461
GSMPMM2VirBCurrent3_nad80 | DIGITAL | IOD_GSM_disk | D3462
GSMPMM2VirBCurrent4_nad80 | DIGITAL | IOD_GSM_disk | D3463
GSMPMM2VirBCurrent5_nad80 | DIGITAL | IOD_GSM_disk | D3464
GSMPMM2VirBCurrent6_nad80 | DIGITAL | IOD_GSM_disk | D3465
GSMPMM2VirBCurrent7_nad80 | DIGITAL | IOD_GSM_disk | D3466
GSMPMM2VirBCurrent8_nad80 | DIGITAL | IOD_GSM_disk | D3467
GSMPMM2VirBCurrent9_nad80 | DIGITAL | IOD_GSM_disk | D3468
GSMPMM2VirBCurrent10_nad80 | DIGITAL | IOD_GSM_disk | D3469
GSMPMM2VirBCurrent11_nad80 | DIGITAL | IOD_GSM_disk | D3470
GSMPMM2VirBCurrent12_nad80 | DIGITAL | IOD_GSM_disk | D3471
GSMPMM2VirBCurrent13_nad80 | DIGITAL | IOD_GSM_disk | D3472
GSMPMM2VirBCurrent14_nad80 | DIGITAL | IOD_GSM_disk | D3473
GSMPMM2VirBCurrent15_nad80 | DIGITAL | IOD_GSM_disk | D3474
GSMPMM2VirBCurrent16_nad80 | DIGITAL | IOD_GSM_disk | D3475
GSMPMM2VirBCurrent17_nad80 | DIGITAL | IOD_GSM_disk | D3476
GSMPMM2VirBCurrent18_nad80 | DIGITAL | IOD_GSM_disk | D3477
GSMPMM2VirBCurrent19_nad80 | DIGITAL | IOD_GSM_disk | D3478
GSMPMM2VirBCurrent20_nad80 | DIGITAL | IOD_GSM_disk | D3479
GSMPMM2VirBCurrent21_nad80 | DIGITAL | IOD_GSM_disk | D3480
GSMPMM2VirBCurrent22_nad80 | DIGITAL | IOD_GSM_disk | D3481
GSMPMM2VirBCurrent23_nad80 | DIGITAL | IOD_GSM_disk | D3482
GSMPMM2VirBCurrent24_nad80 | DIGITAL | IOD_GSM_disk | D3483
GSMPMM2VirBCurrent25_nad80 | DIGITAL | IOD_GSM_disk | D3484
GSMPMM2VirBCurrent26_nad80 | DIGITAL | IOD_GSM_disk | D3485
GSMPMM2VirBCurrent27_nad80 | DIGITAL | IOD_GSM_disk | D3486
GSMPMM2VirBCurrent28_nad80 | DIGITAL | IOD_GSM_disk | D3487
GSMPMM2VirBCurrent29_nad80 | DIGITAL | IOD_GSM_disk | D3488
GSMPMM2VirBCurrent30_nad80 | DIGITAL | IOD_GSM_disk | D3489
GSMPMM2VirBCurrent31_nad80 | DIGITAL | IOD_GSM_disk | D3490
GSMPMM2VirBCurrent32_nad80 | DIGITAL | IOD_GSM_disk | D3491
GSMPMM2VirBCurrent33_nad80 | DIGITAL | IOD_GSM_disk | D3492
GSMPMM2VirBCurrent34_nad80 | DIGITAL | IOD_GSM_disk | D3493
GSMPMM2VirBCurrent35_nad80 | DIGITAL | IOD_GSM_disk | D3494
GSMPMM2VirBCurrent36_nad80 | DIGITAL | IOD_GSM_disk | D3495
GSMPMM2VirBCurrent37_nad80 | DIGITAL | IOD_GSM_disk | D3496
GSMPMM2VirBCurrent38_nad80 | DIGITAL | IOD_GSM_disk | D3497
GSMPMM2VirBCurrent39_nad80 | DIGITAL | IOD_GSM_disk | D3498
GSMPMM2VirBCurrent40_nad80 | DIGITAL | IOD_GSM_disk | D3499
GSMPMM2VirBCurrent41_nad80 | DIGITAL | IOD_GSM_disk | D3500
GSMPMM2VirBCurrent42_nad80 | DIGITAL | IOD_GSM_disk | D3501
GSMPMM2VirBCurrent43_nad80 | DIGITAL | IOD_GSM_disk | D3502
GSMPMM2VirBCurrent44_nad80 | DIGITAL | IOD_GSM_disk | D3503
GSMPMM2VirBCurrent1_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3504
GSMPMM2VirBCurrent2_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3505
GSMPMM2VirBCurrent3_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3506
GSMPMM2VirBCurrent4_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3507
GSMPMM2VirBCurrent5_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3508
GSMPMM2VirBCurrent6_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3509
GSMPMM2VirBCurrent7_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3510
GSMPMM2VirBCurrent8_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3511
GSMPMM2VirBCurrent9_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3512
GSMPMM2VirBCurrent10_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3513
GSMPMM2VirBCurrent11_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3514
GSMPMM2VirBCurrent12_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3515
GSMPMM2VirBCurrent13_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3516
GSMPMM2VirBCurrent14_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3517
GSMPMM2VirBCurrent15_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3518
GSMPMM2VirBCurrent16_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3519
GSMPMM2VirBCurrent17_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3520
GSMPMM2VirBCurrent18_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3521
GSMPMM2VirBCurrent19_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3522
GSMPMM2VirBCurrent20_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3523
GSMPMM2VirBCurrent21_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3524
GSMPMM2VirBCurrent22_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3525
GSMPMM2VirBCurrent23_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3526
GSMPMM2VirBCurrent24_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3527
GSMPMM2VirBCurrent25_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3528
GSMPMM2VirBCurrent26_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3529
GSMPMM2VirBCurrent27_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3530
GSMPMM2VirBCurrent28_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3531
GSMPMM2VirBCurrent29_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3532
GSMPMM2VirBCurrent30_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3533
GSMPMM2VirBCurrent31_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3534
GSMPMM2VirBCurrent32_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3535
GSMPMM2VirBCurrent33_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3536
GSMPMM2VirBCurrent34_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3537
GSMPMM2VirBCurrent35_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3538
GSMPMM2VirBCurrent36_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3539
GSMPMM2VirBCurrent37_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3540
GSMPMM2VirBCurrent38_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3541
GSMPMM2VirBCurrent39_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3542
GSMPMM2VirBCurrent40_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3543
GSMPMM2VirBCurrent41_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3544
GSMPMM2VirBCurrent42_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3545
GSMPMM2VirBCurrent43_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3546
GSMPMM2VirBCurrent44_med60in80_Omogoci | DIGITAL | IOD_GSM_disk | D3547
GSMPMM2VirBCurrent1_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3548
GSMPMM2VirBCurrent2_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3549
GSMPMM2VirBCurrent3_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3550
GSMPMM2VirBCurrent4_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3551
GSMPMM2VirBCurrent5_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3552
GSMPMM2VirBCurrent6_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3553
GSMPMM2VirBCurrent7_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3554
GSMPMM2VirBCurrent8_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3555
GSMPMM2VirBCurrent9_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3556
GSMPMM2VirBCurrent10_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3557
GSMPMM2VirBCurrent11_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3558
GSMPMM2VirBCurrent12_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3559
GSMPMM2VirBCurrent13_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3560
GSMPMM2VirBCurrent14_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3561
GSMPMM2VirBCurrent15_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3562
GSMPMM2VirBCurrent16_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3563
GSMPMM2VirBCurrent17_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3564
GSMPMM2VirBCurrent18_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3565
GSMPMM2VirBCurrent19_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3566
GSMPMM2VirBCurrent20_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3567
GSMPMM2VirBCurrent21_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3568
GSMPMM2VirBCurrent22_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3569
GSMPMM2VirBCurrent23_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3570
GSMPMM2VirBCurrent24_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3571
GSMPMM2VirBCurrent25_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3572
GSMPMM2VirBCurrent26_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3573
GSMPMM2VirBCurrent27_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3574
GSMPMM2VirBCurrent28_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3575
GSMPMM2VirBCurrent29_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3576
GSMPMM2VirBCurrent30_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3577
GSMPMM2VirBCurrent31_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3578
GSMPMM2VirBCurrent32_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3579
GSMPMM2VirBCurrent33_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3580
GSMPMM2VirBCurrent34_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3581
GSMPMM2VirBCurrent35_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3582
GSMPMM2VirBCurrent36_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3583
GSMPMM2VirBCurrent37_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3584
GSMPMM2VirBCurrent38_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3585
GSMPMM2VirBCurrent39_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3586
GSMPMM2VirBCurrent40_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3587
GSMPMM2VirBCurrent41_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3588
GSMPMM2VirBCurrent42_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3589
GSMPMM2VirBCurrent43_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3590
GSMPMM2VirBCurrent44_nad80_Omogoci | DIGITAL | IOD_GSM_disk | D3591
GSMDI_R3KC_A_Q21_IzkljucenIzpad_Omogoci | DIGITAL | IOD_GSM_disk | D3592
GSMQ21_vkljuceno_Omogoci | DIGITAL | IOD_GSM_disk | D3593
GSMDI_R3KC_A_Q22_IzkljucenIzpad_Omogoci | DIGITAL | IOD_GSM_disk | D3594
GSMQ22_vkljuceno_Omogoci | DIGITAL | IOD_GSM_disk | D3595
GSMDI_SBi_RAZS_AA_Izolacija_NOT_OK_Omogoci | DIGITAL | IOD_GSM_disk | D3596
GSMDI_SBi_RAZS_AB_Izolacija_NOT_OK_Omogoci | DIGITAL | IOD_GSM_disk | D3597

## XSoft
mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Read(PRG) | mod_Write_BOOL(FC) | mod_Write_Word(FC) | mod_Write_Word(FC) | mod_Write_dWord(FC) | mod_Write_dWord(FC) | mod_Write_String(FC) | mod_Write_dWord2(FC)
(*Branje BOOL*) | (*Branje INT*) | (*Branje UINT*) | (*Branje LONG*) | (*Branje REAL*) | (*Branje STRING*) | (*Branje ULONG*) | (*Pisanje BOOL*) | (*Pisanje INT*) | (*Pisanje UINT*) | (*Pisanje LONG*) | (*Pisanje REAL*) | (*Pisanje STRING*) | (*Pisanje ULONG*)
(**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**) | (**)
mind_bool[0]:=AGR_Gasenje_alarm; | mind[0]:=DateTime.Dan; | mind[6000]:=K1_obr_u_skupno; | Read_dWord(dVar:=MAX_SOCKET_FD_SETSIZE,lo:=3000,hi:=3001); | Read_Real(rVar:=Circ[1].CosFi_III,lo:=4000,hi:=4001); | Read_String(sVar:=cas_modbus_izpad,start:=5000); |  | 0:AGR_Gasenje_alarm:=Bit_0; | 0:DateTime.Dan:=Byte_0; | 6000:K1_obr_u_skupno:=Word_01; | 3001:MAX_SOCKET_FD_SETSIZE:=Long_0; | 4001:Circ[1].CosFi_III:=Real_0; | 5000:cas_modbus_izpad:=String_0;
mind_bool[1]:=AGR_PozCent_napaka; | mind[1]:=DateTime.Leto; | mind[6001]:=K2_obr_u_skupno; |  | Read_Real(rVar:=Circ[1].DelovnaEnergija,lo:=4002,hi:=4003); | Read_String(sVar:=Date_Time[0],start:=5015); |  | 1:AGR_PozCent_napaka:=Bit_0; | 1:DateTime.Leto:=Byte_0; | 6001:K2_obr_u_skupno:=Word_01; |  | 4003:Circ[1].DelovnaEnergija:=Real_0; | 5015:Date_Time[0]:=String_0;
mind_bool[2]:=AGR_PozSenzor_okvara; | mind[2]:=DateTime.Leto2; | mind[6002]:=PMM2.VirAAlarmPhase.C01_16_60to80; |  | Read_Real(rVar:=Circ[1].DelovnaEnergija_TEMP,lo:=4004,hi:=4005); | Read_String(sVar:=Date_Time[1],start:=5030); |  | 2:AGR_PozSenzor_okvara:=Bit_0; | 2:DateTime.Leto2:=Word_01; | 6002:PMM2.VirAAlarmPhase.C01_16_60to80:=Word_01; |  | 4005:Circ[1].DelovnaEnergija_TEMP:=Real_0; | 5030:Date_Time[1]:=String_0;
mind_bool[3]:=AlarmGenUPS_A_V23; | mind[3]:=DateTime.Mesec; | mind[6003]:=PMM2.VirAAlarmPhase.C01_16_over80; |  | Read_Real(rVar:=Circ[1].DelovnaMoc_III,lo:=4006,hi:=4007); | Read_String(sVar:=Date_Time[2],start:=5045); |  | 3:AlarmGenUPS_A_V23:=Bit_0; | 3:DateTime.Mesec:=Byte_0; | 6003:PMM2.VirAAlarmPhase.C01_16_over80:=Word_01; |  | 4007:Circ[1].DelovnaMoc_III:=Real_0; | 5045:Date_Time[2]:=String_0;
mind_bool[4]:=AlarmGenUPS_V23; | mind[4]:=DateTime.Minuta; | mind[6004]:=PMM2.VirAAlarmPhase.C17_32_60to80; |  | Read_Real(rVar:=Circ[1].DelovnaMoc_L1,lo:=4008,hi:=4009); | Read_String(sVar:=Date_Time[3],start:=5060); |  | 4:AlarmGenUPS_V23:=Bit_0; | 4:DateTime.Minuta:=Byte_0; | 6004:PMM2.VirAAlarmPhase.C17_32_60to80:=Word_01; |  | 4009:Circ[1].DelovnaMoc_L1:=Real_0; | 5060:Date_Time[3]:=String_0;
mind_bool[5]:=AlarmGenUPS_V25; | mind[5]:=DateTime.PLC_Dan; | mind[6005]:=PMM2.VirAAlarmPhase.C17_32_over80; |  | Read_Real(rVar:=Circ[1].DelovnaMoc_L2,lo:=4010,hi:=4011); | Read_String(sVar:=K1obrat_ure,start:=5075); |  | 5:AlarmGenUPS_V25:=Bit_0; | 5:DateTime.PLC_Dan:=Byte_0; | 6005:PMM2.VirAAlarmPhase.C17_32_over80:=Word_01; |  | 4011:Circ[1].DelovnaMoc_L2:=Real_0; | 5075:K1obrat_ure:=String_0;
mind_bool[6]:=AlarmPMM1VirATokPrevisok; | mind[6]:=DateTime.PLC_DanVTednu; | mind[6006]:=PMM2.VirAAlarmPhase.C33_44_60to80; |  | Read_Real(rVar:=Circ[1].DelovnaMoc_L3,lo:=4012,hi:=4013); | Read_String(sVar:=UserCurrentName,start:=5090); |  | 6:AlarmPMM1VirATokPrevisok:=Bit_0; | 6:DateTime.PLC_DanVTednu:=Byte_0; | 6006:PMM2.VirAAlarmPhase.C33_44_60to80:=Word_01; |  | 4013:Circ[1].DelovnaMoc_L3:=Real_0; | 5090:UserCurrentName:=String_0;
mind_bool[7]:=AlarmPMM1VirATokVisok; | mind[7]:=DateTime.PLC_Leto; | mind[6007]:=PMM2.VirAAlarmPhase.C33_44_over80; |  | Read_Real(rVar:=Circ[1].Frekvenca_L1,lo:=4014,hi:=4015); | Read_String(sVar:=UserDisplay,start:=5105); |  | 7:AlarmPMM1VirATokVisok:=Bit_0; | 7:DateTime.PLC_Leto:=Byte_0; | 6007:PMM2.VirAAlarmPhase.C33_44_over80:=Word_01; |  | 4015:Circ[1].Frekvenca_L1:=Real_0; | 5105:UserDisplay:=String_0;
mind_bool[8]:=AlarmPMM1VirBTokPrevisok; | mind[8]:=DateTime.PLC_Mesec; | mind[6008]:=PMM2.VirBAlarmPhase.C01_16_60to80; |  | Read_Real(rVar:=Circ[1].InduktivnaEnergija,lo:=4016,hi:=4017); |  |  | 8:AlarmPMM1VirBTokPrevisok:=Bit_0; | 8:DateTime.PLC_Mesec:=Byte_0; | 6008:PMM2.VirBAlarmPhase.C01_16_60to80:=Word_01; |  | 4017:Circ[1].InduktivnaEnergija:=Real_0;
mind_bool[9]:=AlarmPMM1VirBTokVisok; | mind[9]:=DateTime.PLC_Minuta; | mind[6009]:=PMM2.VirBAlarmPhase.C01_16_over80; |  | Read_Real(rVar:=Circ[1].InduktivnaMoc_III,lo:=4018,hi:=4019); |  |  | 9:AlarmPMM1VirBTokVisok:=Bit_0; | 9:DateTime.PLC_Minuta:=Byte_0; | 6009:PMM2.VirBAlarmPhase.C01_16_over80:=Word_01; |  | 4019:Circ[1].InduktivnaMoc_III:=Real_0;
mind_bool[10]:=AlarmPMM2x17nad80[10]; | mind[10]:=DateTime.PLC_Sekunda; | mind[6010]:=PMM2.VirBAlarmPhase.C17_32_60to80; |  | Read_Real(rVar:=Circ[1].JalovaMoc_L1,lo:=4020,hi:=4021); |  |  | 10:AlarmPMM2x17nad80[10]:=Bit_0; | 10:DateTime.PLC_Sekunda:=Byte_0; | 6010:PMM2.VirBAlarmPhase.C17_32_60to80:=Word_01; |  | 4021:Circ[1].JalovaMoc_L1:=Real_0;
mind_bool[11]:=AlarmPMM2x17nad80[11]; | mind[11]:=DateTime.PLC_Ura; | mind[6011]:=PMM2.VirBAlarmPhase.C17_32_over80; |  | Read_Real(rVar:=Circ[1].JalovaMoc_L2,lo:=4022,hi:=4023); |  |  | 11:AlarmPMM2x17nad80[11]:=Bit_0; | 11:DateTime.PLC_Ura:=Byte_0; | 6011:PMM2.VirBAlarmPhase.C17_32_over80:=Word_01; |  | 4023:Circ[1].JalovaMoc_L2:=Real_0;
mind_bool[12]:=AlarmPMM2x17nad80[12]; | mind[12]:=DateTime.Sekunda; | mind[6012]:=PMM2.VirBAlarmPhase.C33_44_60to80; |  | Read_Real(rVar:=Circ[1].JalovaMoc_L3,lo:=4024,hi:=4025); |  |  | 12:AlarmPMM2x17nad80[12]:=Bit_0; | 12:DateTime.Sekunda:=Byte_0; | 6012:PMM2.VirBAlarmPhase.C33_44_60to80:=Word_01; |  | 4025:Circ[1].JalovaMoc_L3:=Real_0;
mind_bool[13]:=AlarmPMM2x17nad80[13]; | mind[13]:=DateTime.Ura; | mind[6013]:=PMM2.VirBAlarmPhase.C33_44_over80; |  | Read_Real(rVar:=Circ[1].KapacitivnaEnergija,lo:=4026,hi:=4027); |  |  | 13:AlarmPMM2x17nad80[13]:=Bit_0; | 13:DateTime.Ura:=Byte_0; | 6013:PMM2.VirBAlarmPhase.C33_44_over80:=Word_01; |  | 4027:Circ[1].KapacitivnaEnergija:=Real_0;
mind_bool[14]:=AlarmPMM2x17nad80[14]; | mind[14]:=HIA1_vlaga_s; | mind[6014]:=PMM[1].AlarmPhase[1].C01_16_60to80; |  | Read_Real(rVar:=Circ[1].KapacitivnaMoc_III,lo:=4028,hi:=4029); |  |  | 14:AlarmPMM2x17nad80[14]:=Bit_0; | 14:HIA1_vlaga_s:=Word_01; | 6014:PMM[1].AlarmPhase[1].C01_16_60to80:=Word_01; |  | 4029:Circ[1].KapacitivnaMoc_III:=Real_0;
mind_bool[15]:=AlarmPMM2x17nad80[15]; | mind[15]:=HIA2_vlaga_s; | mind[6015]:=PMM[1].AlarmPhase[1].C01_16_over80; |  | Read_Real(rVar:=Circ[1].MaximumDemand,lo:=4030,hi:=4031); |  |  | 15:AlarmPMM2x17nad80[15]:=Bit_0; | 15:HIA2_vlaga_s:=Word_01; | 6015:PMM[1].AlarmPhase[1].C01_16_over80:=Word_01; |  | 4031:Circ[1].MaximumDemand:=Real_0;
mind_bool[16]:=AlarmPMM2x17nad80[16]; | mind[16]:=HIA3_vlaga_s; | mind[6016]:=PMM[1].AlarmPhase[1].C17_32_60to80; |  | Read_Real(rVar:=Circ[1].MaximumDemandA2,lo:=4032,hi:=4033); |  |  | 16:AlarmPMM2x17nad80[16]:=Bit_0; | 16:HIA3_vlaga_s:=Word_01; | 6016:PMM[1].AlarmPhase[1].C17_32_60to80:=Word_01; |  | 4033:Circ[1].MaximumDemandA2:=Real_0;
mind_bool[17]:=AlarmPMM2x17nad80[17]; | mind[17]:=HIA4_vlaga_s; | mind[6017]:=PMM[1].AlarmPhase[1].C17_32_over80; |  | Read_Real(rVar:=Circ[1].MaximumDemandA3,lo:=4034,hi:=4035); |  |  | 17:AlarmPMM2x17nad80[17]:=Bit_0; | 17:HIA4_vlaga_s:=Word_01; | 6017:PMM[1].AlarmPhase[1].C17_32_over80:=Word_01; |  | 4035:Circ[1].MaximumDemandA3:=Real_0;
mind_bool[18]:=AlarmPMM2x17nad80[18]; | mind[18]:=HIA5_vlaga_s; | mind[6018]:=PMM[1].AlarmPhase[1].C33_42_60to80; |  | Read_Real(rVar:=Circ[1].Napetost_L1_L2,lo:=4036,hi:=4037); |  |  | 18:AlarmPMM2x17nad80[18]:=Bit_0; | 18:HIA5_vlaga_s:=Word_01; | 6018:PMM[1].AlarmPhase[1].C33_42_60to80:=Word_01; |  | 4037:Circ[1].Napetost_L1_L2:=Real_0;
mind_bool[19]:=AlarmPMM2x17nad80[19]; | mind[19]:=HIA6_vlaga_s; | mind[6019]:=PMM[1].AlarmPhase[1].C33_42_over80; |  | Read_Real(rVar:=Circ[1].Napetost_L1_N,lo:=4038,hi:=4039); |  |  | 19:AlarmPMM2x17nad80[19]:=Bit_0; | 19:HIA6_vlaga_s:=Word_01; | 6019:PMM[1].AlarmPhase[1].C33_42_over80:=Word_01; |  | 4039:Circ[1].Napetost_L1_N:=Real_0;
mind_bool[20]:=AlarmPMM2x17nad80[1]; | mind[20]:=HIA7_vlaga_s; | mind[6020]:=PMM[1].AlarmPhase[2].C01_16_60to80; |  | Read_Real(rVar:=Circ[1].Napetost_L2_L3,lo:=4040,hi:=4041); |  |  | 20:AlarmPMM2x17nad80[1]:=Bit_0; | 20:HIA7_vlaga_s:=Word_01; | 6020:PMM[1].AlarmPhase[2].C01_16_60to80:=Word_01; |  | 4041:Circ[1].Napetost_L2_L3:=Real_0;
mind_bool[21]:=AlarmPMM2x17nad80[20]; | mind[21]:=Klima[1].Analog_izh_mesanje; | mind[6021]:=PMM[1].AlarmPhase[2].C01_16_over80; |  | Read_Real(rVar:=Circ[1].Napetost_L2_N,lo:=4042,hi:=4043); |  |  | 21:AlarmPMM2x17nad80[20]:=Bit_0; | 21:Klima[1].Analog_izh_mesanje:=Word_01; | 6021:PMM[1].AlarmPhase[2].C01_16_over80:=Word_01; |  | 4043:Circ[1].Napetost_L2_N:=Real_0;
mind_bool[22]:=AlarmPMM2x17nad80[21]; | mind[22]:=Klima[1].Analog_izh_rekuperator; | mind[6022]:=PMM[1].AlarmPhase[2].C17_32_60to80; |  | Read_Real(rVar:=Circ[1].Napetost_L3_L1,lo:=4044,hi:=4045); |  |  | 22:AlarmPMM2x17nad80[21]:=Bit_0; | 22:Klima[1].Analog_izh_rekuperator:=Word_01; | 6022:PMM[1].AlarmPhase[2].C17_32_60to80:=Word_01; |  | 4045:Circ[1].Napetost_L3_L1:=Real_0;
mind_bool[23]:=AlarmPMM2x17nad80[22]; | mind[23]:=Klima[1].Analog_izh_VentGrelnika; | mind[6023]:=PMM[1].AlarmPhase[2].C17_32_over80; |  | Read_Real(rVar:=Circ[1].Napetost_L3_N,lo:=4046,hi:=4047); |  |  | 23:AlarmPMM2x17nad80[22]:=Bit_0; | 23:Klima[1].Analog_izh_VentGrelnika:=Word_01; | 6023:PMM[1].AlarmPhase[2].C17_32_over80:=Word_01; |  | 4047:Circ[1].Napetost_L3_N:=Real_0;
mind_bool[24]:=AlarmPMM2x17nad80[23]; | mind[24]:=Klima[1].Analog_izh_VentHlajenja; | mind[6024]:=PMM[1].AlarmPhase[2].C33_42_60to80; |  | Read_Real(rVar:=Circ[1].NavideznaMoc_III,lo:=4048,hi:=4049); |  |  | 24:AlarmPMM2x17nad80[23]:=Bit_0; | 24:Klima[1].Analog_izh_VentHlajenja:=Word_01; | 6024:PMM[1].AlarmPhase[2].C33_42_60to80:=Word_01; |  | 4049:Circ[1].NavideznaMoc_III:=Real_0;
mind_bool[25]:=AlarmPMM2x17nad80[24]; | mind[25]:=Klima[1].Dejanska_zel_temp; | mind[6025]:=PMM[1].AlarmPhase[2].C33_42_over80; |  | Read_Real(rVar:=Circ[1].NicelniTok,lo:=4050,hi:=4051); |  |  | 25:AlarmPMM2x17nad80[24]:=Bit_0; | 25:Klima[1].Dejanska_zel_temp:=Word_01; | 6025:PMM[1].AlarmPhase[2].C33_42_over80:=Word_01; |  | 4051:Circ[1].NicelniTok:=Real_0;
mind_bool[26]:=AlarmPMM2x17nad80[25]; | mind[26]:=Klima[1].Hitrost_del_vent_disp; | mind[6026]:=PMM[1].AlarmPhase[3].C01_16_60to80; |  | Read_Real(rVar:=Circ[1].PowerFactor_III,lo:=4052,hi:=4053); |  |  | 26:AlarmPMM2x17nad80[25]:=Bit_0; | 26:Klima[1].Hitrost_del_vent_disp:=Word_01; | 6026:PMM[1].AlarmPhase[3].C01_16_60to80:=Word_01; |  | 4053:Circ[1].PowerFactor_III:=Real_0;
mind_bool[27]:=AlarmPMM2x17nad80[26]; | mind[27]:=Klima[1].Max_vpih; | mind[6027]:=PMM[1].AlarmPhase[3].C01_16_over80; |  | Read_Real(rVar:=Circ[1].PowerFactor_L1,lo:=4054,hi:=4055); |  |  | 27:AlarmPMM2x17nad80[26]:=Bit_0; | 27:Klima[1].Max_vpih:=Word_01; | 6027:PMM[1].AlarmPhase[3].C01_16_over80:=Word_01; |  | 4055:Circ[1].PowerFactor_L1:=Real_0;
mind_bool[28]:=AlarmPMM2x17nad80[27]; | mind[28]:=Klima[1].Min_vpih; | mind[6028]:=PMM[1].AlarmPhase[3].C17_32_60to80; |  | Read_Real(rVar:=Circ[1].PowerFactor_L2,lo:=4056,hi:=4057); |  |  | 28:AlarmPMM2x17nad80[27]:=Bit_0; | 28:Klima[1].Min_vpih:=Word_01; | 6028:PMM[1].AlarmPhase[3].C17_32_60to80:=Word_01; |  | 4057:Circ[1].PowerFactor_L2:=Real_0;
mind_bool[29]:=AlarmPMM2x17nad80[28]; | mind[29]:=Klima[1].Obrat_ure_Vent_h1; | mind[6029]:=PMM[1].AlarmPhase[3].C17_32_over80; |  | Read_Real(rVar:=Circ[1].PowerFactor_L3,lo:=4058,hi:=4059); |  |  | 29:AlarmPMM2x17nad80[28]:=Bit_0; | 29:Klima[1].Obrat_ure_Vent_h1:=Word_01; | 6029:PMM[1].AlarmPhase[3].C17_32_over80:=Word_01; |  | 4059:Circ[1].PowerFactor_L3:=Real_0;
mind_bool[30]:=AlarmPMM2x17nad80[29]; | mind[30]:=Klima[1].Obrat_ure_Vent_h2; | mind[6030]:=PMM[1].AlarmPhase[3].C33_42_60to80; |  | Read_Real(rVar:=Circ[1].RazEner_D,lo:=4060,hi:=4061); |  |  | 30:AlarmPMM2x17nad80[29]:=Bit_0; | 30:Klima[1].Obrat_ure_Vent_h2:=Word_01; | 6030:PMM[1].AlarmPhase[3].C33_42_60to80:=Word_01; |  | 4061:Circ[1].RazEner_D:=Real_0;
mind_bool[31]:=AlarmPMM2x17nad80[2]; | mind[31]:=Klima[1].Pol_komp_konec; | mind[6031]:=PMM[1].AlarmPhase[3].C33_42_over80; |  | Read_Real(rVar:=Circ[1].RazEner_D_SCADA,lo:=4062,hi:=4063); |  |  | 31:AlarmPMM2x17nad80[2]:=Bit_0; | 31:Klima[1].Pol_komp_konec:=Word_01; | 6031:PMM[1].AlarmPhase[3].C33_42_over80:=Word_01; |  | 4063:Circ[1].RazEner_D_SCADA:=Real_0;
mind_bool[32]:=AlarmPMM2x17nad80[30]; | mind[32]:=Klima[1].Pol_komp_sprem_zel_vr; | mind[6032]:=UPS1_StatusBaterije; |  | Read_Real(rVar:=Circ[1].RazEner_D_TEMP,lo:=4064,hi:=4065); |  |  | 32:AlarmPMM2x17nad80[30]:=Bit_0; | 32:Klima[1].Pol_komp_sprem_zel_vr:=Word_01; | 6032:UPS1_StatusBaterije:=Word_01; |  | 4065:Circ[1].RazEner_D_TEMP:=Real_0;
mind_bool[33]:=AlarmPMM2x17nad80[31]; | mind[33]:=Klima[1].Pol_komp_zacetek; | mind[6033]:=UPS2_StatusBaterije; |  | Read_Real(rVar:=Circ[1].RazEner_M,lo:=4066,hi:=4067); |  |  | 33:AlarmPMM2x17nad80[31]:=Bit_0; | 33:Klima[1].Pol_komp_zacetek:=Word_01; | 6033:UPS2_StatusBaterije:=Word_01; |  | 4067:Circ[1].RazEner_M:=Real_0;
mind_bool[34]:=AlarmPMM2x17nad80[32]; | mind[34]:=Klima[1].PreklopHitDelVent; | mind[6034]:=UPS3_StatusBaterije; |  | Read_Real(rVar:=Circ[1].RazEner_M_SCADA,lo:=4068,hi:=4069); |  |  | 34:AlarmPMM2x17nad80[32]:=Bit_0; | 34:Klima[1].PreklopHitDelVent:=Word_01; | 6034:UPS3_StatusBaterije:=Word_01; |  | 4069:Circ[1].RazEner_M_SCADA:=Real_0;
mind_bool[35]:=AlarmPMM2x17nad80[33]; | mind[35]:=Klima[1].Protizamrz_zascita; | mind[6035]:=UPS[1].StatusBaterije; |  | Read_Real(rVar:=Circ[1].RazEner_M_TEMP,lo:=4070,hi:=4071); |  |  | 35:AlarmPMM2x17nad80[33]:=Bit_0; | 35:Klima[1].Protizamrz_zascita:=Word_01; | 6035:UPS[1].StatusBaterije:=Word_01; |  | 4071:Circ[1].RazEner_M_TEMP:=Real_0;
mind_bool[36]:=AlarmPMM2x17nad80[34]; | mind[36]:=Klima[1].Rezim_delovanja; | mind[6036]:=UPS[2].StatusBaterije; |  | Read_Real(rVar:=Circ[1].RazEner_T,lo:=4072,hi:=4073); |  |  | 36:AlarmPMM2x17nad80[34]:=Bit_0; | 36:Klima[1].Rezim_delovanja:=Word_01; | 6036:UPS[2].StatusBaterije:=Word_01; |  | 4073:Circ[1].RazEner_T:=Real_0;
mind_bool[37]:=AlarmPMM2x17nad80[35]; | mind[37]:=Klima[1].Temperatura_dovoda; | mind[6037]:=UPS[3].StatusBaterije; |  | Read_Real(rVar:=Circ[1].RazEner_T_SCADA,lo:=4074,hi:=4075); |  |  | 37:AlarmPMM2x17nad80[35]:=Bit_0; | 37:Klima[1].Temperatura_dovoda:=Word_01; | 6037:UPS[3].StatusBaterije:=Word_01; |  | 4075:Circ[1].RazEner_T_SCADA:=Real_0;
mind_bool[38]:=AlarmPMM2x17nad80[36]; | mind[38]:=Klima[1].Temperatura_prostora; |  |  | Read_Real(rVar:=Circ[1].RazEner_T_TEMP,lo:=4076,hi:=4077); |  |  | 38:AlarmPMM2x17nad80[36]:=Bit_0; | 38:Klima[1].Temperatura_prostora:=Word_01; |  |  | 4077:Circ[1].RazEner_T_TEMP:=Real_0;
mind_bool[39]:=AlarmPMM2x17nad80[37]; | mind[39]:=Klima[1].TempPredPloscnimRekup; |  |  | Read_Real(rVar:=Circ[1].THDI_L1,lo:=4078,hi:=4079); |  |  | 39:AlarmPMM2x17nad80[37]:=Bit_0; | 39:Klima[1].TempPredPloscnimRekup:=Word_01; |  |  | 4079:Circ[1].THDI_L1:=Real_0;
mind_bool[40]:=AlarmPMM2x17nad80[38]; | mind[40]:=Klima[1].TempZaPloscnimRekup; |  |  | Read_Real(rVar:=Circ[1].THDI_L2,lo:=4080,hi:=4081); |  |  | 40:AlarmPMM2x17nad80[38]:=Bit_0; | 40:Klima[1].TempZaPloscnimRekup:=Word_01; |  |  | 4081:Circ[1].THDI_L2:=Real_0;
mind_bool[41]:=AlarmPMM2x17nad80[39]; | mind[41]:=Klima[1].Vlaga_v_prostoru; |  |  | Read_Real(rVar:=Circ[1].THDI_L3,lo:=4082,hi:=4083); |  |  | 41:AlarmPMM2x17nad80[39]:=Bit_0; | 41:Klima[1].Vlaga_v_prostoru:=Word_01; |  |  | 4083:Circ[1].THDI_L3:=Real_0;
mind_bool[42]:=AlarmPMM2x17nad80[3]; | mind[42]:=Klima[1].VlagaVstopZrakaProstor; |  |  | Read_Real(rVar:=Circ[1].THDV_L1,lo:=4084,hi:=4085); |  |  | 42:AlarmPMM2x17nad80[3]:=Bit_0; | 42:Klima[1].VlagaVstopZrakaProstor:=Word_01; |  |  | 4085:Circ[1].THDV_L1:=Real_0;
mind_bool[43]:=AlarmPMM2x17nad80[40]; | mind[43]:=Klima[1].Zel_temp_eko_gretja; |  |  | Read_Real(rVar:=Circ[1].THDV_L2,lo:=4086,hi:=4087); |  |  | 43:AlarmPMM2x17nad80[40]:=Bit_0; | 43:Klima[1].Zel_temp_eko_gretja:=Word_01; |  |  | 4087:Circ[1].THDV_L2:=Real_0;
mind_bool[44]:=AlarmPMM2x17nad80[41]; | mind[44]:=Klima[1].Zel_temp_eko_hlajenja; |  |  | Read_Real(rVar:=Circ[1].THDV_L3,lo:=4088,hi:=4089); |  |  | 44:AlarmPMM2x17nad80[41]:=Bit_0; | 44:Klima[1].Zel_temp_eko_hlajenja:=Word_01; |  |  | 4089:Circ[1].THDV_L3:=Real_0;
mind_bool[45]:=AlarmPMM2x17nad80[42]; | mind[45]:=Klima[1].Zel_temp_komf_gretja; |  |  | Read_Real(rVar:=Circ[1].Tok_L1,lo:=4090,hi:=4091); |  |  | 45:AlarmPMM2x17nad80[42]:=Bit_0; | 45:Klima[1].Zel_temp_komf_gretja:=Word_01; |  |  | 4091:Circ[1].Tok_L1:=Real_0;
mind_bool[46]:=AlarmPMM2x17nad80[4]; | mind[46]:=Klima[1].Zel_temp_komf_hlajenja; |  |  | Read_Real(rVar:=Circ[1].Tok_L2,lo:=4092,hi:=4093); |  |  | 46:AlarmPMM2x17nad80[4]:=Bit_0; | 46:Klima[1].Zel_temp_komf_hlajenja:=Word_01; |  |  | 4093:Circ[1].Tok_L2:=Real_0;
mind_bool[47]:=AlarmPMM2x17nad80[5]; | mind[47]:=Klima[1].Zim_komp_konec; |  |  | Read_Real(rVar:=Circ[1].Tok_L3,lo:=4094,hi:=4095); |  |  | 47:AlarmPMM2x17nad80[5]:=Bit_0; | 47:Klima[1].Zim_komp_konec:=Word_01; |  |  | 4095:Circ[1].Tok_L3:=Real_0;
mind_bool[48]:=AlarmPMM2x17nad80[6]; | mind[48]:=Klima[1].Zim_komp_sprem_zel_vr; |  |  | Read_Real(rVar:=Circ[1].TokPovprecje_III,lo:=4096,hi:=4097); |  |  | 48:AlarmPMM2x17nad80[6]:=Bit_0; | 48:Klima[1].Zim_komp_sprem_zel_vr:=Word_01; |  |  | 4097:Circ[1].TokPovprecje_III:=Real_0;
mind_bool[49]:=AlarmPMM2x17nad80[7]; | mind[49]:=Klima[1].Zim_komp_zacetek; |  |  | Read_Real(rVar:=PMM2.VirA.Current[10],lo:=4098,hi:=4099); |  |  | 49:AlarmPMM2x17nad80[7]:=Bit_0; | 49:Klima[1].Zim_komp_zacetek:=Word_01; |  |  | 4099:PMM2.VirA.Current[10]:=Real_0;
mind_bool[50]:=AlarmPMM2x17nad80[8]; | mind[50]:=Klima[1].ZimKompMinVpihKonec; |  |  | Read_Real(rVar:=PMM2.VirA.Current[11],lo:=4100,hi:=4101); |  |  | 50:AlarmPMM2x17nad80[8]:=Bit_0; | 50:Klima[1].ZimKompMinVpihKonec:=Word_01; |  |  | 4101:PMM2.VirA.Current[11]:=Real_0;
mind_bool[51]:=AlarmPMM2x17nad80[9]; | mind[51]:=Klima[1].ZimKompMinVpihZac; |  |  | Read_Real(rVar:=PMM2.VirA.Current[12],lo:=4102,hi:=4103); |  |  | 51:AlarmPMM2x17nad80[9]:=Bit_0; | 51:Klima[1].ZimKompMinVpihZac:=Word_01; |  |  | 4103:PMM2.VirA.Current[12]:=Real_0;
mind_bool[52]:=ALM_AGR_Gasenje_alarm; | mind[52]:=Klima[1].ZkompMinVpihSpremZelVr; |  |  | Read_Real(rVar:=PMM2.VirA.Current[13],lo:=4104,hi:=4105); |  |  | 52:ALM_AGR_Gasenje_alarm:=Bit_0; | 52:Klima[1].ZkompMinVpihSpremZelVr:=Word_01; |  |  | 4105:PMM2.VirA.Current[13]:=Real_0;
mind_bool[53]:=ALM_AGR_PozCent_napaka; | mind[53]:=Klima[1].Zunanja_temp; |  |  | Read_Real(rVar:=PMM2.VirA.Current[14],lo:=4106,hi:=4107); |  |  | 53:ALM_AGR_PozCent_napaka:=Bit_0; | 53:Klima[1].Zunanja_temp:=Word_01; |  |  | 4107:PMM2.VirA.Current[14]:=Real_0;
mind_bool[54]:=ALM_AGR_PozSenzor_okvara; | mind[54]:=Klima[2].Analog_izh_mesanje; |  |  | Read_Real(rVar:=PMM2.VirA.Current[15],lo:=4108,hi:=4109); |  |  | 54:ALM_AGR_PozSenzor_okvara:=Bit_0; | 54:Klima[2].Analog_izh_mesanje:=Word_01; |  |  | 4109:PMM2.VirA.Current[15]:=Real_0;
mind_bool[55]:=ALM_GSM_Gasenje_alarm; | mind[55]:=Klima[2].Analog_izh_rekuperator; |  |  | Read_Real(rVar:=PMM2.VirA.Current[16],lo:=4110,hi:=4111); |  |  | 55:ALM_GSM_Gasenje_alarm:=Bit_0; | 55:Klima[2].Analog_izh_rekuperator:=Word_01; |  |  | 4111:PMM2.VirA.Current[16]:=Real_0;
mind_bool[56]:=ALM_GSM_PozCent_napaka; | mind[56]:=Klima[2].Analog_izh_VentGrelnika; |  |  | Read_Real(rVar:=PMM2.VirA.Current[17],lo:=4112,hi:=4113); |  |  | 56:ALM_GSM_PozCent_napaka:=Bit_0; | 56:Klima[2].Analog_izh_VentGrelnika:=Word_01; |  |  | 4113:PMM2.VirA.Current[17]:=Real_0;
mind_bool[57]:=ALM_GSM_PozSenzor_okvara; | mind[57]:=Klima[2].Analog_izh_VentHlajenja; |  |  | Read_Real(rVar:=PMM2.VirA.Current[18],lo:=4114,hi:=4115); |  |  | 57:ALM_GSM_PozSenzor_okvara:=Bit_0; | 57:Klima[2].Analog_izh_VentHlajenja:=Word_01; |  |  | 4115:PMM2.VirA.Current[18]:=Real_0;
mind_bool[58]:=Circ_Vpis_Dnevne_energija_scada1; | mind[58]:=Klima[2].Dejanska_zel_temp; |  |  | Read_Real(rVar:=PMM2.VirA.Current[19],lo:=4116,hi:=4117); |  |  | 58:Circ_Vpis_Dnevne_energija_scada1:=Bit_0; | 58:Klima[2].Dejanska_zel_temp:=Word_01; |  |  | 4117:PMM2.VirA.Current[19]:=Real_0;
mind_bool[59]:=Circ_Vpis_Dnevne_energija_scada2; | mind[59]:=Klima[2].Hitrost_del_vent_disp; |  |  | Read_Real(rVar:=PMM2.VirA.Current[1],lo:=4118,hi:=4119); |  |  | 59:Circ_Vpis_Dnevne_energija_scada2:=Bit_0; | 59:Klima[2].Hitrost_del_vent_disp:=Word_01; |  |  | 4119:PMM2.VirA.Current[1]:=Real_0;
mind_bool[60]:=Circ_Vpis_Mesecna_energija_scada1; | mind[60]:=Klima[2].Max_vpih; |  |  | Read_Real(rVar:=PMM2.VirA.Current[20],lo:=4120,hi:=4121); |  |  | 60:Circ_Vpis_Mesecna_energija_scada1:=Bit_0; | 60:Klima[2].Max_vpih:=Word_01; |  |  | 4121:PMM2.VirA.Current[20]:=Real_0;
mind_bool[61]:=Circ_Vpis_Mesecna_energija_scada2; | mind[61]:=Klima[2].Min_vpih; |  |  | Read_Real(rVar:=PMM2.VirA.Current[21],lo:=4122,hi:=4123); |  |  | 61:Circ_Vpis_Mesecna_energija_scada2:=Bit_0; | 61:Klima[2].Min_vpih:=Word_01; |  |  | 4123:PMM2.VirA.Current[21]:=Real_0;
mind_bool[62]:=Circ_Vpis_Tedenska_energija_scada1; | mind[62]:=Klima[2].Obrat_ure_Vent_h1; |  |  | Read_Real(rVar:=PMM2.VirA.Current[22],lo:=4124,hi:=4125); |  |  | 62:Circ_Vpis_Tedenska_energija_scada1:=Bit_0; | 62:Klima[2].Obrat_ure_Vent_h1:=Word_01; |  |  | 4125:PMM2.VirA.Current[22]:=Real_0;
mind_bool[63]:=Circ_Vpis_Tedenska_energija_scada2; | mind[63]:=Klima[2].Obrat_ure_Vent_h2; |  |  | Read_Real(rVar:=PMM2.VirA.Current[23],lo:=4126,hi:=4127); |  |  | 63:Circ_Vpis_Tedenska_energija_scada2:=Bit_0; | 63:Klima[2].Obrat_ure_Vent_h2:=Word_01; |  |  | 4127:PMM2.VirA.Current[23]:=Real_0;
mind_bool[64]:=ComError; | mind[64]:=Klima[2].Pol_komp_konec; |  |  | Read_Real(rVar:=PMM2.VirA.Current[24],lo:=4128,hi:=4129); |  |  | 64:ComError:=Bit_0; | 64:Klima[2].Pol_komp_konec:=Word_01; |  |  | 4129:PMM2.VirA.Current[24]:=Real_0;
mind_bool[65]:=ComSCADA; | mind[65]:=Klima[2].Pol_komp_sprem_zel_vr; |  |  | Read_Real(rVar:=PMM2.VirA.Current[25],lo:=4130,hi:=4131); |  |  | 65:ComSCADA:=Bit_0; | 65:Klima[2].Pol_komp_sprem_zel_vr:=Word_01; |  |  | 4131:PMM2.VirA.Current[25]:=Real_0;
mind_bool[66]:=ComSCADA1; | mind[66]:=Klima[2].Pol_komp_zacetek; |  |  | Read_Real(rVar:=PMM2.VirA.Current[26],lo:=4132,hi:=4133); |  |  | 66:ComSCADA1:=Bit_0; | 66:Klima[2].Pol_komp_zacetek:=Word_01; |  |  | 4133:PMM2.VirA.Current[26]:=Real_0;
mind_bool[67]:=ComSCADA2; | mind[67]:=Klima[2].PreklopHitDelVent; |  |  | Read_Real(rVar:=PMM2.VirA.Current[27],lo:=4134,hi:=4135); |  |  | 67:ComSCADA2:=Bit_0; | 67:Klima[2].PreklopHitDelVent:=Word_01; |  |  | 4135:PMM2.VirA.Current[27]:=Real_0;
mind_bool[68]:=ComSCADA3; | mind[68]:=Klima[2].Protizamrz_zascita; |  |  | Read_Real(rVar:=PMM2.VirA.Current[28],lo:=4136,hi:=4137); |  |  | 68:ComSCADA3:=Bit_0; | 68:Klima[2].Protizamrz_zascita:=Word_01; |  |  | 4137:PMM2.VirA.Current[28]:=Real_0;
mind_bool[69]:=DI1_I11; | mind[69]:=Klima[2].Rezim_delovanja; |  |  | Read_Real(rVar:=PMM2.VirA.Current[29],lo:=4138,hi:=4139); |  |  | 69:DI1_I11:=Bit_0; | 69:Klima[2].Rezim_delovanja:=Word_01; |  |  | 4139:PMM2.VirA.Current[29]:=Real_0;
mind_bool[70]:=DI1_I9; | mind[70]:=Klima[2].Temperatura_dovoda; |  |  | Read_Real(rVar:=PMM2.VirA.Current[2],lo:=4140,hi:=4141); |  |  | 70:DI1_I9:=Bit_0; | 70:Klima[2].Temperatura_dovoda:=Word_01; |  |  | 4141:PMM2.VirA.Current[2]:=Real_0;
mind_bool[71]:=DI2_I14; | mind[71]:=Klima[2].Temperatura_prostora; |  |  | Read_Real(rVar:=PMM2.VirA.Current[30],lo:=4142,hi:=4143); |  |  | 71:DI2_I14:=Bit_0; | 71:Klima[2].Temperatura_prostora:=Word_01; |  |  | 4143:PMM2.VirA.Current[30]:=Real_0;
mind_bool[72]:=DI2_I15; | mind[72]:=Klima[2].TempPredPloscnimRekup; |  |  | Read_Real(rVar:=PMM2.VirA.Current[31],lo:=4144,hi:=4145); |  |  | 72:DI2_I15:=Bit_0; | 72:Klima[2].TempPredPloscnimRekup:=Word_01; |  |  | 4145:PMM2.VirA.Current[31]:=Real_0;
mind_bool[73]:=DI_R3KC_A_Q21_IzkljucenIzpad; | mind[73]:=Klima[2].TempZaPloscnimRekup; |  |  | Read_Real(rVar:=PMM2.VirA.Current[32],lo:=4146,hi:=4147); |  |  | 73:DI_R3KC_A_Q21_IzkljucenIzpad:=Bit_0; | 73:Klima[2].TempZaPloscnimRekup:=Word_01; |  |  | 4147:PMM2.VirA.Current[32]:=Real_0;
mind_bool[74]:=DI_R3KC_A_Q22_IzkljucenIzpad; | mind[74]:=Klima[2].Vlaga_v_prostoru; |  |  | Read_Real(rVar:=PMM2.VirA.Current[33],lo:=4148,hi:=4149); |  |  | 74:DI_R3KC_A_Q22_IzkljucenIzpad:=Bit_0; | 74:Klima[2].Vlaga_v_prostoru:=Word_01; |  |  | 4149:PMM2.VirA.Current[33]:=Real_0;
mind_bool[75]:=DI_SBi_RAZS_AA_Izolacija_NOT_OK; | mind[75]:=Klima[2].VlagaVstopZrakaProstor; |  |  | Read_Real(rVar:=PMM2.VirA.Current[34],lo:=4150,hi:=4151); |  |  | 75:DI_SBi_RAZS_AA_Izolacija_NOT_OK:=Bit_0; | 75:Klima[2].VlagaVstopZrakaProstor:=Word_01; |  |  | 4151:PMM2.VirA.Current[34]:=Real_0;
mind_bool[76]:=DI_SBi_RAZS_AB_Izolacija_NOT_OK; | mind[76]:=Klima[2].Zel_temp_eko_gretja; |  |  | Read_Real(rVar:=PMM2.VirA.Current[35],lo:=4152,hi:=4153); |  |  | 76:DI_SBi_RAZS_AB_Izolacija_NOT_OK:=Bit_0; | 76:Klima[2].Zel_temp_eko_gretja:=Word_01; |  |  | 4153:PMM2.VirA.Current[35]:=Real_0;
mind_bool[77]:=ErrComCirc[1]; | mind[77]:=Klima[2].Zel_temp_eko_hlajenja; |  |  | Read_Real(rVar:=PMM2.VirA.Current[36],lo:=4154,hi:=4155); |  |  | 77:ErrComCirc[1]:=Bit_0; | 77:Klima[2].Zel_temp_eko_hlajenja:=Word_01; |  |  | 4155:PMM2.VirA.Current[36]:=Real_0;
mind_bool[78]:=ErrComKlima[1]; | mind[78]:=Klima[2].Zel_temp_komf_gretja; |  |  | Read_Real(rVar:=PMM2.VirA.Current[37],lo:=4156,hi:=4157); |  |  | 78:ErrComKlima[1]:=Bit_0; | 78:Klima[2].Zel_temp_komf_gretja:=Word_01; |  |  | 4157:PMM2.VirA.Current[37]:=Real_0;
mind_bool[79]:=ErrComKlima[2]; | mind[79]:=Klima[2].Zel_temp_komf_hlajenja; |  |  | Read_Real(rVar:=PMM2.VirA.Current[38],lo:=4158,hi:=4159); |  |  | 79:ErrComKlima[2]:=Bit_0; | 79:Klima[2].Zel_temp_komf_hlajenja:=Word_01; |  |  | 4159:PMM2.VirA.Current[38]:=Real_0;
mind_bool[80]:=ErrComPMM[1]; | mind[80]:=Klima[2].Zim_komp_konec; |  |  | Read_Real(rVar:=PMM2.VirA.Current[39],lo:=4160,hi:=4161); |  |  | 80:ErrComPMM[1]:=Bit_0; | 80:Klima[2].Zim_komp_konec:=Word_01; |  |  | 4161:PMM2.VirA.Current[39]:=Real_0;
mind_bool[81]:=ErrComPMM[2]; | mind[81]:=Klima[2].Zim_komp_sprem_zel_vr; |  |  | Read_Real(rVar:=PMM2.VirA.Current[3],lo:=4162,hi:=4163); |  |  | 81:ErrComPMM[2]:=Bit_0; | 81:Klima[2].Zim_komp_sprem_zel_vr:=Word_01; |  |  | 4163:PMM2.VirA.Current[3]:=Real_0;
mind_bool[82]:=ErrComPort2; | mind[82]:=Klima[2].Zim_komp_zacetek; |  |  | Read_Real(rVar:=PMM2.VirA.Current[40],lo:=4164,hi:=4165); |  |  | 82:ErrComPort2:=Bit_0; | 82:Klima[2].Zim_komp_zacetek:=Word_01; |  |  | 4165:PMM2.VirA.Current[40]:=Real_0;
mind_bool[83]:=ErrComPort3; | mind[83]:=Klima[2].ZimKompMinVpihKonec; |  |  | Read_Real(rVar:=PMM2.VirA.Current[41],lo:=4166,hi:=4167); |  |  | 83:ErrComPort3:=Bit_0; | 83:Klima[2].ZimKompMinVpihKonec:=Word_01; |  |  | 4167:PMM2.VirA.Current[41]:=Real_0;
mind_bool[84]:=ErrComPort4; | mind[84]:=Klima[2].ZimKompMinVpihZac; |  |  | Read_Real(rVar:=PMM2.VirA.Current[42],lo:=4168,hi:=4169); |  |  | 84:ErrComPort4:=Bit_0; | 84:Klima[2].ZimKompMinVpihZac:=Word_01; |  |  | 4169:PMM2.VirA.Current[42]:=Real_0;
mind_bool[85]:=ErrComUPS[1]; | mind[85]:=Klima[2].ZkompMinVpihSpremZelVr; |  |  | Read_Real(rVar:=PMM2.VirA.Current[43],lo:=4170,hi:=4171); |  |  | 85:ErrComUPS[1]:=Bit_0; | 85:Klima[2].ZkompMinVpihSpremZelVr:=Word_01; |  |  | 4171:PMM2.VirA.Current[43]:=Real_0;
mind_bool[86]:=ErrComUPS[2]; | mind[86]:=Klima[2].Zunanja_temp; |  |  | Read_Real(rVar:=PMM2.VirA.Current[44],lo:=4172,hi:=4173); |  |  | 86:ErrComUPS[2]:=Bit_0; | 86:Klima[2].Zunanja_temp:=Word_01; |  |  | 4173:PMM2.VirA.Current[44]:=Real_0;
mind_bool[87]:=ErrComUPS[3]; | mind[87]:=KlimaIzklopObrUre; |  |  | Read_Real(rVar:=PMM2.VirA.Current[4],lo:=4174,hi:=4175); |  |  | 87:ErrComUPS[3]:=Bit_0; | 87:KlimaIzklopObrUre:=Word_01; |  |  | 4175:PMM2.VirA.Current[4]:=Real_0;
mind_bool[88]:=ErrComUPSMGE[1]; | mind[88]:=Klime_vklopi_n; |  |  | Read_Real(rVar:=PMM2.VirA.Current[5],lo:=4176,hi:=4177); |  |  | 88:ErrComUPSMGE[1]:=Bit_0; | 88:Klime_vklopi_n:=Word_01; |  |  | 4177:PMM2.VirA.Current[5]:=Real_0;
mind_bool[89]:=F1_1_zascita_ok; | mind[89]:=kom_nast_cas_izpada; |  |  | Read_Real(rVar:=PMM2.VirA.Current[6],lo:=4178,hi:=4179); |  |  | 89:F1_1_zascita_ok:=Bit_0; | 89:kom_nast_cas_izpada:=Word_01; |  |  | 4179:PMM2.VirA.Current[6]:=Real_0;
mind_bool[90]:=GSM_Gasenje_alarm; | mind[90]:=PMM[1].AlarmPhase[1].GlobalAlarmReg; |  |  | Read_Real(rVar:=PMM2.VirA.Current[7],lo:=4180,hi:=4181); |  |  | 90:GSM_Gasenje_alarm:=Bit_0; | 90:PMM[1].AlarmPhase[1].GlobalAlarmReg:=Word_01; |  |  | 4181:PMM2.VirA.Current[7]:=Real_0;
mind_bool[91]:=GSM_PozCent_napaka; | mind[91]:=PMM[1].AlarmPhase[2].GlobalAlarmReg; |  |  | Read_Real(rVar:=PMM2.VirA.Current[8],lo:=4182,hi:=4183); |  |  | 91:GSM_PozCent_napaka:=Bit_0; | 91:PMM[1].AlarmPhase[2].GlobalAlarmReg:=Word_01; |  |  | 4183:PMM2.VirA.Current[8]:=Real_0;
mind_bool[92]:=GSM_PozSenzor_okvara; | mind[92]:=PMM[1].AlarmPhase[3].GlobalAlarmReg; |  |  | Read_Real(rVar:=PMM2.VirA.Current[9],lo:=4184,hi:=4185); |  |  | 92:GSM_PozSenzor_okvara:=Bit_0; | 92:PMM[1].AlarmPhase[3].GlobalAlarmReg:=Word_01; |  |  | 4185:PMM2.VirA.Current[9]:=Real_0;
mind_bool[93]:=K1_SkupnaNapaka; | mind[93]:=Q12stanje; |  |  | Read_Real(rVar:=PMM2.VirA_fsys,lo:=4186,hi:=4187); |  |  | 93:K1_SkupnaNapaka:=Bit_0; | 93:Q12stanje:=Byte_0; |  |  | 4187:PMM2.VirA_fsys:=Real_0;
mind_bool[94]:=K1_vklop_izklop_poteka; | mind[94]:=TempHistereza; |  |  | Read_Real(rVar:=PMM2.VirA_Isys,lo:=4188,hi:=4189); |  |  | 94:K1_vklop_izklop_poteka:=Bit_0; | 94:TempHistereza:=Word_01; |  |  | 4189:PMM2.VirA_Isys:=Real_0;
mind_bool[95]:=K1AlarmPozara; | mind[95]:=TempPovp234; |  |  | Read_Real(rVar:=PMM2.VirA_PFsys,lo:=4190,hi:=4191); |  |  | 95:K1AlarmPozara:=Bit_0; | 95:TempPovp234:=Word_01; |  |  | 4191:PMM2.VirA_PFsys:=Real_0;
mind_bool[96]:=K1KlimaZdruzenAlarm; | mind[96]:=TempPovp234Alarm; |  |  | Read_Real(rVar:=PMM2.VirA_Psys,lo:=4192,hi:=4193); |  |  | 96:K1KlimaZdruzenAlarm:=Bit_0; | 96:TempPovp234Alarm:=Word_01; |  |  | 4193:PMM2.VirA_Psys:=Real_0;
mind_bool[97]:=K1NiPretoka; | mind[97]:=TempPovp56; |  |  | Read_Real(rVar:=PMM2.VirA_Qsys,lo:=4194,hi:=4195); |  |  | 97:K1NiPretoka:=Bit_0; | 97:TempPovp56:=Word_01; |  |  | 4195:PMM2.VirA_Qsys:=Real_0;
mind_bool[98]:=K1OkvaraRototerma; | mind[98]:=TempPovp56Alarm; |  |  | Read_Real(rVar:=PMM2.VirA_Ssys,lo:=4196,hi:=4197); |  |  | 98:K1OkvaraRototerma:=Bit_0; | 98:TempPovp56Alarm:=Word_01; |  |  | 4197:PMM2.VirA_Ssys:=Real_0;
mind_bool[99]:=K1OkvaraVlazNap; | mind[99]:=TempZaVklopKlim1; |  |  | Read_Real(rVar:=PMM2.VirA_Usys,lo:=4198,hi:=4199); |  |  | 99:K1OkvaraVlazNap:=Bit_0; | 99:TempZaVklopKlim1:=Word_01; |  |  | 4199:PMM2.VirA_Usys:=Real_0;
mind_bool[100]:=K1PreobMotCrpGr; | mind[100]:=TempZaVklopKlim2; |  |  | Read_Real(rVar:=PMM2.VirAActiveEnergyConsumed_kWh,lo:=4200,hi:=4201); |  |  | 100:K1PreobMotCrpGr:=Bit_0; | 100:TempZaVklopKlim2:=Word_01; |  |  | 4201:PMM2.VirAActiveEnergyConsumed_kWh:=Real_0;
mind_bool[101]:=K1PreobMotVent; | mind[101]:=TIA1_alarm; |  |  | Read_Real(rVar:=PMM2.VirAActivePowerPhaseA_kW,lo:=4202,hi:=4203); |  |  | 101:K1PreobMotVent:=Bit_0; | 101:TIA1_alarm:=Word_01; |  |  | 4203:PMM2.VirAActivePowerPhaseA_kW:=Real_0;
mind_bool[102]:=K1ProtizamrzZascAkt; | mind[102]:=TIA1_temp_s; |  |  | Read_Real(rVar:=PMM2.VirAActivePowerPhaseB_kW,lo:=4204,hi:=4205); |  |  | 102:K1ProtizamrzZascAkt:=Bit_0; | 102:TIA1_temp_s:=Word_01; |  |  | 4205:PMM2.VirAActivePowerPhaseB_kW:=Real_0;
mind_bool[103]:=K1ZamasenostFiltra; | mind[103]:=TIA2_alarm; |  |  | Read_Real(rVar:=PMM2.VirAActivePowerPhaseC_kW,lo:=4206,hi:=4207); |  |  | 103:K1ZamasenostFiltra:=Bit_0; | 103:TIA2_alarm:=Word_01; |  |  | 4207:PMM2.VirAActivePowerPhaseC_kW:=Real_0;
mind_bool[104]:=K2_SkupnaNapaka; | mind[104]:=TIA2_temp_s; |  |  | Read_Real(rVar:=PMM2.VirAAparentPowerPhaseA,lo:=4208,hi:=4209); |  |  | 104:K2_SkupnaNapaka:=Bit_0; | 104:TIA2_temp_s:=Word_01; |  |  | 4209:PMM2.VirAAparentPowerPhaseA:=Real_0;
mind_bool[105]:=K2_vklop_izklop_poteka; | mind[105]:=TIA3_alarm; |  |  | Read_Real(rVar:=PMM2.VirAAparentPowerPhaseB,lo:=4210,hi:=4211); |  |  | 105:K2_vklop_izklop_poteka:=Bit_0; | 105:TIA3_alarm:=Word_01; |  |  | 4211:PMM2.VirAAparentPowerPhaseB:=Real_0;
mind_bool[106]:=K2AlarmPozara; | mind[106]:=TIA3_temp_s; |  |  | Read_Real(rVar:=PMM2.VirAAparentPowerPhaseC,lo:=4212,hi:=4213); |  |  | 106:K2AlarmPozara:=Bit_0; | 106:TIA3_temp_s:=Word_01; |  |  | 4213:PMM2.VirAAparentPowerPhaseC:=Real_0;
mind_bool[107]:=K2KlimaZdruzenAlarm; | mind[107]:=TIA4_alarm; |  |  | Read_Real(rVar:=PMM2.VirACurrentInPhaseA_A,lo:=4214,hi:=4215); |  |  | 107:K2KlimaZdruzenAlarm:=Bit_0; | 107:TIA4_alarm:=Word_01; |  |  | 4215:PMM2.VirACurrentInPhaseA_A:=Real_0;
mind_bool[108]:=K2NiPretoka; | mind[108]:=TIA4_temp_s; |  |  | Read_Real(rVar:=PMM2.VirACurrentInPhaseB_A,lo:=4216,hi:=4217); |  |  | 108:K2NiPretoka:=Bit_0; | 108:TIA4_temp_s:=Word_01; |  |  | 4217:PMM2.VirACurrentInPhaseB_A:=Real_0;
mind_bool[109]:=K2OkvaraRototerma; | mind[109]:=TIA5_alarm; |  |  | Read_Real(rVar:=PMM2.VirACurrentInPhaseC_A,lo:=4218,hi:=4219); |  |  | 109:K2OkvaraRototerma:=Bit_0; | 109:TIA5_alarm:=Word_01; |  |  | 4219:PMM2.VirACurrentInPhaseC_A:=Real_0;
mind_bool[110]:=K2OkvaraVlazNap; | mind[110]:=TIA5_temp_s; |  |  | Read_Real(rVar:=PMM2.VirAReactiveEnergyConsumed_kVARh,lo:=4220,hi:=4221); |  |  | 110:K2OkvaraVlazNap:=Bit_0; | 110:TIA5_temp_s:=Word_01; |  |  | 4221:PMM2.VirAReactiveEnergyConsumed_kVARh:=Real_0;
mind_bool[111]:=K2PreobMotCrpGr; | mind[111]:=TIA6_alarm; |  |  | Read_Real(rVar:=PMM2.VirAReactivePowerPhaseA,lo:=4222,hi:=4223); |  |  | 111:K2PreobMotCrpGr:=Bit_0; | 111:TIA6_alarm:=Word_01; |  |  | 4223:PMM2.VirAReactivePowerPhaseA:=Real_0;
mind_bool[112]:=K2PreobMotVent; | mind[112]:=TIA6_temp_s; |  |  | Read_Real(rVar:=PMM2.VirAReactivePowerPhaseB,lo:=4224,hi:=4225); |  |  | 112:K2PreobMotVent:=Bit_0; | 112:TIA6_temp_s:=Word_01; |  |  | 4225:PMM2.VirAReactivePowerPhaseB:=Real_0;
mind_bool[113]:=K2ProtizamrzZascAkt; | mind[113]:=TIA7_alarm; |  |  | Read_Real(rVar:=PMM2.VirAReactivePowerPhaseC,lo:=4226,hi:=4227); |  |  | 113:K2ProtizamrzZascAkt:=Bit_0; | 113:TIA7_alarm:=Word_01; |  |  | 4227:PMM2.VirAReactivePowerPhaseC:=Real_0;
mind_bool[114]:=K2ZamasenostFiltra; | mind[114]:=TIA7_temp_s; |  |  | Read_Real(rVar:=PMM2.VirAVoltageBetweenPhaseAB_V,lo:=4228,hi:=4229); |  |  | 114:K2ZamasenostFiltra:=Bit_0; | 114:TIA7_temp_s:=Word_01; |  |  | 4229:PMM2.VirAVoltageBetweenPhaseAB_V:=Real_0;
mind_bool[115]:=K3_deluje; | mind[115]:=UPS[1].InverterStatus; |  |  | Read_Real(rVar:=PMM2.VirAVoltageBetweenPhaseAN_V,lo:=4230,hi:=4231); |  |  | 115:K3_deluje:=Bit_0; | 115:UPS[1].InverterStatus:=Word_01; |  |  | 4231:PMM2.VirAVoltageBetweenPhaseAN_V:=Real_0;
mind_bool[116]:=K3_SkupnaNapaka; | mind[116]:=UPS[1].OutputStatus; |  |  | Read_Real(rVar:=PMM2.VirAVoltageBetweenPhaseBC_V,lo:=4232,hi:=4233); |  |  | 116:K3_SkupnaNapaka:=Bit_0; | 116:UPS[1].OutputStatus:=Word_01; |  |  | 4233:PMM2.VirAVoltageBetweenPhaseBC_V:=Real_0;
mind_bool[117]:=Klima1_izkljucena; | mind[117]:=UPS[1].SteviloIzpadovVhodneLinije; |  |  | Read_Real(rVar:=PMM2.VirAVoltageBetweenPhaseBN_V,lo:=4234,hi:=4235); |  |  | 117:Klima1_izkljucena:=Bit_0; | 117:UPS[1].SteviloIzpadovVhodneLinije:=Word_01; |  |  | 4235:PMM2.VirAVoltageBetweenPhaseBN_V:=Real_0;
mind_bool[118]:=KLIMA1_kke_pogon; | mind[118]:=UPS[1].UnitStatus; |  |  | Read_Real(rVar:=PMM2.VirAVoltageBetweenPhaseCA_V,lo:=4236,hi:=4237); |  |  | 118:KLIMA1_kke_pogon:=Bit_0; | 118:UPS[1].UnitStatus:=Word_01; |  |  | 4237:PMM2.VirAVoltageBetweenPhaseCA_V:=Real_0;
mind_bool[119]:=KLIMA1_krm_nap_ok; | mind[119]:=UPS[2].InverterStatus; |  |  | Read_Real(rVar:=PMM2.VirAVoltageBetweenPhaseCN_V,lo:=4238,hi:=4239); |  |  | 119:KLIMA1_krm_nap_ok:=Bit_0; | 119:UPS[2].InverterStatus:=Word_01; |  |  | 4239:PMM2.VirAVoltageBetweenPhaseCN_V:=Real_0;
mind_bool[120]:=Klima2_izkljucena; | mind[120]:=UPS[2].OutputStatus; |  |  | Read_Real(rVar:=PMM2.VirB.Current[10],lo:=4240,hi:=4241); |  |  | 120:Klima2_izkljucena:=Bit_0; | 120:UPS[2].OutputStatus:=Word_01; |  |  | 4241:PMM2.VirB.Current[10]:=Real_0;
mind_bool[121]:=Klima3_izkljucena; | mind[121]:=UPS[2].SteviloIzpadovVhodneLinije; |  |  | Read_Real(rVar:=PMM2.VirB.Current[11],lo:=4242,hi:=4243); |  |  | 121:Klima3_izkljucena:=Bit_0; | 121:UPS[2].SteviloIzpadovVhodneLinije:=Word_01; |  |  | 4243:PMM2.VirB.Current[11]:=Real_0;
mind_bool[122]:=Klima[1].Alarm_pozar; | mind[122]:=UPS[2].UnitStatus; |  |  | Read_Real(rVar:=PMM2.VirB.Current[12],lo:=4244,hi:=4245); |  |  | 122:Klima[1].Alarm_pozar:=Bit_0; | 122:UPS[2].UnitStatus:=Word_01; |  |  | 4245:PMM2.VirB.Current[12]:=Real_0;
mind_bool[123]:=Klima[1].DelVentHit1; | mind[123]:=UPS[3].InverterStatus; |  |  | Read_Real(rVar:=PMM2.VirB.Current[13],lo:=4246,hi:=4247); |  |  | 123:Klima[1].DelVentHit1:=Bit_0; | 123:UPS[3].InverterStatus:=Word_01; |  |  | 4247:PMM2.VirB.Current[13]:=Real_0;
mind_bool[124]:=Klima[1].DelVentHit2; | mind[124]:=UPS[3].OutputStatus; |  |  | Read_Real(rVar:=PMM2.VirB.Current[14],lo:=4248,hi:=4249); |  |  | 124:Klima[1].DelVentHit2:=Bit_0; | 124:UPS[3].OutputStatus:=Word_01; |  |  | 4249:PMM2.VirB.Current[14]:=Real_0;
mind_bool[125]:=Klima[1].Ni_pretoka; | mind[125]:=UPS[3].SteviloIzpadovVhodneLinije; |  |  | Read_Real(rVar:=PMM2.VirB.Current[15],lo:=4250,hi:=4251); |  |  | 125:Klima[1].Ni_pretoka:=Bit_0; | 125:UPS[3].SteviloIzpadovVhodneLinije:=Word_01; |  |  | 4251:PMM2.VirB.Current[15]:=Real_0;
mind_bool[126]:=Klima[1].OkvaraRototerm; | mind[126]:=UPS[3].UnitStatus; |  |  | Read_Real(rVar:=PMM2.VirB.Current[16],lo:=4252,hi:=4253); |  |  | 126:Klima[1].OkvaraRototerm:=Bit_0; | 126:UPS[3].UnitStatus:=Word_01; |  |  | 4253:PMM2.VirB.Current[16]:=Real_0;
mind_bool[127]:=Klima[1].OkvaraVlazNap; | mind[127]:=UPS_MGE[1].BatteryBackupTime; |  |  | Read_Real(rVar:=PMM2.VirB.Current[17],lo:=4254,hi:=4255); |  |  | 127:Klima[1].OkvaraVlazNap:=Bit_0; | 127:UPS_MGE[1].BatteryBackupTime:=Word_01; |  |  | 4255:PMM2.VirB.Current[17]:=Real_0;
mind_bool[128]:=Klima[1].PreobMotCrpGrel; | mind[128]:=UPS_MGE[1].BatteryChargingLevel; |  |  | Read_Real(rVar:=PMM2.VirB.Current[18],lo:=4256,hi:=4257); |  |  | 128:Klima[1].PreobMotCrpGrel:=Bit_0; | 128:UPS_MGE[1].BatteryChargingLevel:=Word_01; |  |  | 4257:PMM2.VirB.Current[18]:=Real_0;
mind_bool[129]:=Klima[1].PreobMotVent; | mind[129]:=UPS_MGE[1].BatteryRechargeDuration; |  |  | Read_Real(rVar:=PMM2.VirB.Current[19],lo:=4258,hi:=4259); |  |  | 129:Klima[1].PreobMotVent:=Bit_0; | 129:UPS_MGE[1].BatteryRechargeDuration:=Word_01; |  |  | 4259:PMM2.VirB.Current[19]:=Real_0;
mind_bool[130]:=Klima[1].ProtizamrzZascAktivna; | mind[130]:=UPS_MGE[1].I1output; |  |  | Read_Real(rVar:=PMM2.VirB.Current[1],lo:=4260,hi:=4261); |  |  | 130:Klima[1].ProtizamrzZascAktivna:=Bit_0; | 130:UPS_MGE[1].I1output:=Word_01; |  |  | 4261:PMM2.VirB.Current[1]:=Real_0;
mind_bool[131]:=Klima[1].VklopRegKlimata; | mind[131]:=UPS_MGE[1].I2output; |  |  | Read_Real(rVar:=PMM2.VirB.Current[20],lo:=4262,hi:=4263); |  |  | 131:Klima[1].VklopRegKlimata:=Bit_0; | 131:UPS_MGE[1].I2output:=Word_01; |  |  | 4263:PMM2.VirB.Current[20]:=Real_0;
mind_bool[132]:=Klima[1].ZamasenostFiltra; | mind[132]:=UPS_MGE[1].I3output; |  |  | Read_Real(rVar:=PMM2.VirB.Current[21],lo:=4264,hi:=4265); |  |  | 132:Klima[1].ZamasenostFiltra:=Bit_0; | 132:UPS_MGE[1].I3output:=Word_01; |  |  | 4265:PMM2.VirB.Current[21]:=Real_0;
mind_bool[133]:=Klima[1].ZdruzAlarmA; | mind[133]:=UPS_MGE[1].InverterFrequency; |  |  | Read_Real(rVar:=PMM2.VirB.Current[22],lo:=4266,hi:=4267); |  |  | 133:Klima[1].ZdruzAlarmA:=Bit_0; | 133:UPS_MGE[1].InverterFrequency:=Word_01; |  |  | 4267:PMM2.VirB.Current[22]:=Real_0;
mind_bool[134]:=Klima[1].ZdruzAlarmB; | mind[134]:=UPS_MGE[1].OutputActivePower1; |  |  | Read_Real(rVar:=PMM2.VirB.Current[23],lo:=4268,hi:=4269); |  |  | 134:Klima[1].ZdruzAlarmB:=Bit_0; | 134:UPS_MGE[1].OutputActivePower1:=Word_01; |  |  | 4269:PMM2.VirB.Current[23]:=Real_0;
mind_bool[135]:=Klima[2].Alarm_pozar; | mind[135]:=UPS_MGE[1].OutputActivePower2; |  |  | Read_Real(rVar:=PMM2.VirB.Current[24],lo:=4270,hi:=4271); |  |  | 135:Klima[2].Alarm_pozar:=Bit_0; | 135:UPS_MGE[1].OutputActivePower2:=Word_01; |  |  | 4271:PMM2.VirB.Current[24]:=Real_0;
mind_bool[136]:=Klima[2].DelVentHit1; | mind[136]:=UPS_MGE[1].OutputActivePower3; |  |  | Read_Real(rVar:=PMM2.VirB.Current[25],lo:=4272,hi:=4273); |  |  | 136:Klima[2].DelVentHit1:=Bit_0; | 136:UPS_MGE[1].OutputActivePower3:=Word_01; |  |  | 4273:PMM2.VirB.Current[25]:=Real_0;
mind_bool[137]:=Klima[2].DelVentHit2; | mind[137]:=UPS_MGE[1].OutputFrequency; |  |  | Read_Real(rVar:=PMM2.VirB.Current[26],lo:=4274,hi:=4275); |  |  | 137:Klima[2].DelVentHit2:=Bit_0; | 137:UPS_MGE[1].OutputFrequency:=Word_01; |  |  | 4275:PMM2.VirB.Current[26]:=Real_0;
mind_bool[138]:=Klima[2].Ni_pretoka; | mind[138]:=UPS_MGE[1].OutputLoadLevel; |  |  | Read_Real(rVar:=PMM2.VirB.Current[27],lo:=4276,hi:=4277); |  |  | 138:Klima[2].Ni_pretoka:=Bit_0; | 138:UPS_MGE[1].OutputLoadLevel:=Word_01; |  |  | 4277:PMM2.VirB.Current[27]:=Real_0;
mind_bool[139]:=Klima[2].OkvaraRototerm; | mind[139]:=UPS_MGE[1].StatusBaterije; |  |  | Read_Real(rVar:=PMM2.VirB.Current[28],lo:=4278,hi:=4279); |  |  | 139:Klima[2].OkvaraRototerm:=Bit_0; | 139:UPS_MGE[1].StatusBaterije:=Byte_0; |  |  | 4279:PMM2.VirB.Current[28]:=Real_0;
mind_bool[140]:=Klima[2].OkvaraVlazNap; | mind[140]:=UPS_MGE[1].U12mains1; |  |  | Read_Real(rVar:=PMM2.VirB.Current[29],lo:=4280,hi:=4281); |  |  | 140:Klima[2].OkvaraVlazNap:=Bit_0; | 140:UPS_MGE[1].U12mains1:=Word_01; |  |  | 4281:PMM2.VirB.Current[29]:=Real_0;
mind_bool[141]:=Klima[2].PreobMotCrpGrel; | mind[141]:=UPS_MGE[1].U12mains2; |  |  | Read_Real(rVar:=PMM2.VirB.Current[2],lo:=4282,hi:=4283); |  |  | 141:Klima[2].PreobMotCrpGrel:=Bit_0; | 141:UPS_MGE[1].U12mains2:=Word_01; |  |  | 4283:PMM2.VirB.Current[2]:=Real_0;
mind_bool[142]:=Klima[2].PreobMotVent; | mind[142]:=UPS_MGE[1].U1N_inverter; |  |  | Read_Real(rVar:=PMM2.VirB.Current[30],lo:=4284,hi:=4285); |  |  | 142:Klima[2].PreobMotVent:=Bit_0; | 142:UPS_MGE[1].U1N_inverter:=Word_01; |  |  | 4285:PMM2.VirB.Current[30]:=Real_0;
mind_bool[143]:=Klima[2].ProtizamrzZascAktivna; | mind[143]:=UPS_MGE[1].U1N_output; |  |  | Read_Real(rVar:=PMM2.VirB.Current[31],lo:=4286,hi:=4287); |  |  | 143:Klima[2].ProtizamrzZascAktivna:=Bit_0; | 143:UPS_MGE[1].U1N_output:=Word_01; |  |  | 4287:PMM2.VirB.Current[31]:=Real_0;
mind_bool[144]:=Klima[2].VklopRegKlimata; | mind[144]:=UPS_MGE[1].U23mains1; |  |  | Read_Real(rVar:=PMM2.VirB.Current[32],lo:=4288,hi:=4289); |  |  | 144:Klima[2].VklopRegKlimata:=Bit_0; | 144:UPS_MGE[1].U23mains1:=Word_01; |  |  | 4289:PMM2.VirB.Current[32]:=Real_0;
mind_bool[145]:=Klima[2].ZamasenostFiltra; | mind[145]:=UPS_MGE[1].U23mains2; |  |  | Read_Real(rVar:=PMM2.VirB.Current[33],lo:=4290,hi:=4291); |  |  | 145:Klima[2].ZamasenostFiltra:=Bit_0; | 145:UPS_MGE[1].U23mains2:=Word_01; |  |  | 4291:PMM2.VirB.Current[33]:=Real_0;
mind_bool[146]:=Klima[2].ZdruzAlarmA; | mind[146]:=UPS_MGE[1].U2N_inverter; |  |  | Read_Real(rVar:=PMM2.VirB.Current[34],lo:=4292,hi:=4293); |  |  | 146:Klima[2].ZdruzAlarmA:=Bit_0; | 146:UPS_MGE[1].U2N_inverter:=Word_01; |  |  | 4293:PMM2.VirB.Current[34]:=Real_0;
mind_bool[147]:=Klima[2].ZdruzAlarmB; | mind[147]:=UPS_MGE[1].U2N_output; |  |  | Read_Real(rVar:=PMM2.VirB.Current[35],lo:=4294,hi:=4295); |  |  | 147:Klima[2].ZdruzAlarmB:=Bit_0; | 147:UPS_MGE[1].U2N_output:=Word_01; |  |  | 4295:PMM2.VirB.Current[35]:=Real_0;
mind_bool[148]:=KLIMA_m1_delovanje; | mind[148]:=UPS_MGE[1].U31mains1; |  |  | Read_Real(rVar:=PMM2.VirB.Current[36],lo:=4296,hi:=4297); |  |  | 148:KLIMA_m1_delovanje:=Bit_0; | 148:UPS_MGE[1].U31mains1:=Word_01; |  |  | 4297:PMM2.VirB.Current[36]:=Real_0;
mind_bool[149]:=KLIMA_m1_napaka; | mind[149]:=UPS_MGE[1].U31mains2; |  |  | Read_Real(rVar:=PMM2.VirB.Current[37],lo:=4298,hi:=4299); |  |  | 149:KLIMA_m1_napaka:=Bit_0; | 149:UPS_MGE[1].U31mains2:=Word_01; |  |  | 4299:PMM2.VirB.Current[37]:=Real_0;
mind_bool[150]:=KLIMA_m2_delovanje; | mind[150]:=UPS_MGE[1].U3N_inverter; |  |  | Read_Real(rVar:=PMM2.VirB.Current[38],lo:=4300,hi:=4301); |  |  | 150:KLIMA_m2_delovanje:=Bit_0; | 150:UPS_MGE[1].U3N_inverter:=Word_01; |  |  | 4301:PMM2.VirB.Current[38]:=Real_0;
mind_bool[151]:=KLIMA_m2_napaka; | mind[151]:=UPS_MGE[1].U3N_output; |  |  | Read_Real(rVar:=PMM2.VirB.Current[39],lo:=4302,hi:=4303); |  |  | 151:KLIMA_m2_napaka:=Bit_0; | 151:UPS_MGE[1].U3N_output:=Word_01; |  |  | 4303:PMM2.VirB.Current[39]:=Real_0;
mind_bool[152]:=KLIMAT1_delovanje; | mind[152]:=UPS_MGE[1].U_battery; |  |  | Read_Real(rVar:=PMM2.VirB.Current[3],lo:=4304,hi:=4305); |  |  | 152:KLIMAT1_delovanje:=Bit_0; | 152:UPS_MGE[1].U_battery:=Word_01; |  |  | 4305:PMM2.VirB.Current[3]:=Real_0;
mind_bool[153]:=KLIMAT1_napaka; | mind[153]:=UserCurrentLevel; |  |  | Read_Real(rVar:=PMM2.VirB.Current[40],lo:=4306,hi:=4307); |  |  | 153:KLIMAT1_napaka:=Bit_0; | 153:UserCurrentLevel:=Byte_0; |  |  | 4307:PMM2.VirB.Current[40]:=Real_0;
mind_bool[154]:=KLIMAT1_R_zakleni; |  |  |  | Read_Real(rVar:=PMM2.VirB.Current[41],lo:=4308,hi:=4309); |  |  | 154:KLIMAT1_R_zakleni:=Bit_0; |  |  |  | 4309:PMM2.VirB.Current[41]:=Real_0;
mind_bool[155]:=KLIMAT1_vklop_delovanja; |  |  |  | Read_Real(rVar:=PMM2.VirB.Current[42],lo:=4310,hi:=4311); |  |  | 155:KLIMAT1_vklop_delovanja:=Bit_0; |  |  |  | 4311:PMM2.VirB.Current[42]:=Real_0;
mind_bool[156]:=KLIMAT1_vklop_delovanjaR; |  |  |  | Read_Real(rVar:=PMM2.VirB.Current[43],lo:=4312,hi:=4313); |  |  | 156:KLIMAT1_vklop_delovanjaR:=Bit_0; |  |  |  | 4313:PMM2.VirB.Current[43]:=Real_0;
mind_bool[157]:=KLIMAT2_delovanje; |  |  |  | Read_Real(rVar:=PMM2.VirB.Current[44],lo:=4314,hi:=4315); |  |  | 157:KLIMAT2_delovanje:=Bit_0; |  |  |  | 4315:PMM2.VirB.Current[44]:=Real_0;
mind_bool[158]:=KLIMAT2_napaka; |  |  |  | Read_Real(rVar:=PMM2.VirB.Current[4],lo:=4316,hi:=4317); |  |  | 158:KLIMAT2_napaka:=Bit_0; |  |  |  | 4317:PMM2.VirB.Current[4]:=Real_0;
mind_bool[159]:=KLIMAT2_R_zakleni; |  |  |  | Read_Real(rVar:=PMM2.VirB.Current[5],lo:=4318,hi:=4319); |  |  | 159:KLIMAT2_R_zakleni:=Bit_0; |  |  |  | 4319:PMM2.VirB.Current[5]:=Real_0;
mind_bool[160]:=KLIMAT2_vklop_delovanja; |  |  |  | Read_Real(rVar:=PMM2.VirB.Current[6],lo:=4320,hi:=4321); |  |  | 160:KLIMAT2_vklop_delovanja:=Bit_0; |  |  |  | 4321:PMM2.VirB.Current[6]:=Real_0;
mind_bool[161]:=KLIMAT2_vklop_delovanjaR; |  |  |  | Read_Real(rVar:=PMM2.VirB.Current[7],lo:=4322,hi:=4323); |  |  | 161:KLIMAT2_vklop_delovanjaR:=Bit_0; |  |  |  | 4323:PMM2.VirB.Current[7]:=Real_0;
mind_bool[162]:=KlimeAVTO; |  |  |  | Read_Real(rVar:=PMM2.VirB.Current[8],lo:=4324,hi:=4325); |  |  | 162:KlimeAVTO:=Bit_0; |  |  |  | 4325:PMM2.VirB.Current[8]:=Real_0;
mind_bool[163]:=N_F1_1_zascita_ok; |  |  |  | Read_Real(rVar:=PMM2.VirB.Current[9],lo:=4326,hi:=4327); |  |  | 163:N_F1_1_zascita_ok:=Bit_0; |  |  |  | 4327:PMM2.VirB.Current[9]:=Real_0;
mind_bool[164]:=N_KLIMA1_krm_nap_ok; |  |  |  | Read_Real(rVar:=PMM2.VirB_fsys,lo:=4328,hi:=4329); |  |  | 164:N_KLIMA1_krm_nap_ok:=Bit_0; |  |  |  | 4329:PMM2.VirB_fsys:=Real_0;
mind_bool[165]:=N_KLIMAT1_napaka; |  |  |  | Read_Real(rVar:=PMM2.VirB_Isys,lo:=4330,hi:=4331); |  |  | 165:N_KLIMAT1_napaka:=Bit_0; |  |  |  | 4331:PMM2.VirB_Isys:=Real_0;
mind_bool[166]:=N_KLIMAT2_napaka; |  |  |  | Read_Real(rVar:=PMM2.VirB_PFsys,lo:=4332,hi:=4333); |  |  | 166:N_KLIMAT2_napaka:=Bit_0; |  |  |  | 4333:PMM2.VirB_PFsys:=Real_0;
mind_bool[167]:=N_KlimeAVTO; |  |  |  | Read_Real(rVar:=PMM2.VirB_Psys,lo:=4334,hi:=4335); |  |  | 167:N_KlimeAVTO:=Bit_0; |  |  |  | 4335:PMM2.VirB_Psys:=Real_0;
mind_bool[168]:=N_Q12_izpad; |  |  |  | Read_Real(rVar:=PMM2.VirB_Qsys,lo:=4336,hi:=4337); |  |  | 168:N_Q12_izpad:=Bit_0; |  |  |  | 4337:PMM2.VirB_Qsys:=Real_0;
mind_bool[169]:=N_UPS_A_V23_delovanje; |  |  |  | Read_Real(rVar:=PMM2.VirB_Ssys,lo:=4338,hi:=4339); |  |  | 169:N_UPS_A_V23_delovanje:=Bit_0; |  |  |  | 4339:PMM2.VirB_Ssys:=Real_0;
mind_bool[170]:=N_UPS_A_V23_napaka; |  |  |  | Read_Real(rVar:=PMM2.VirB_Usys,lo:=4340,hi:=4341); |  |  | 170:N_UPS_A_V23_napaka:=Bit_0; |  |  |  | 4341:PMM2.VirB_Usys:=Real_0;
mind_bool[171]:=N_UPS_V23_delovanje; |  |  |  | Read_Real(rVar:=PMM2.VirBActiveEnergyConsumed_kWh,lo:=4342,hi:=4343); |  |  | 171:N_UPS_V23_delovanje:=Bit_0; |  |  |  | 4343:PMM2.VirBActiveEnergyConsumed_kWh:=Real_0;
mind_bool[172]:=N_UPS_V23_napaka; |  |  |  | Read_Real(rVar:=PMM2.VirBActivePowerPhaseA_kW,lo:=4344,hi:=4345); |  |  | 172:N_UPS_V23_napaka:=Bit_0; |  |  |  | 4345:PMM2.VirBActivePowerPhaseA_kW:=Real_0;
mind_bool[173]:=N_UPS_V25_delovanje; |  |  |  | Read_Real(rVar:=PMM2.VirBActivePowerPhaseB_kW,lo:=4346,hi:=4347); |  |  | 173:N_UPS_V25_delovanje:=Bit_0; |  |  |  | 4347:PMM2.VirBActivePowerPhaseB_kW:=Real_0;
mind_bool[174]:=N_UPS_V25_napaka; |  |  |  | Read_Real(rVar:=PMM2.VirBActivePowerPhaseC_kW,lo:=4348,hi:=4349); |  |  | 174:N_UPS_V25_napaka:=Bit_0; |  |  |  | 4349:PMM2.VirBActivePowerPhaseC_kW:=Real_0;
mind_bool[175]:=N_VLAZILEC1_napaka; |  |  |  | Read_Real(rVar:=PMM2.VirBAparentPowerPhaseA,lo:=4350,hi:=4351); |  |  | 175:N_VLAZILEC1_napaka:=Bit_0; |  |  |  | 4351:PMM2.VirBAparentPowerPhaseA:=Real_0;
mind_bool[176]:=N_VLAZILEC2_napaka; |  |  |  | Read_Real(rVar:=PMM2.VirBAparentPowerPhaseB,lo:=4352,hi:=4353); |  |  | 176:N_VLAZILEC2_napaka:=Bit_0; |  |  |  | 4353:PMM2.VirBAparentPowerPhaseB:=Real_0;
mind_bool[177]:=napaka_kom_panel; |  |  |  | Read_Real(rVar:=PMM2.VirBAparentPowerPhaseC,lo:=4354,hi:=4355); |  |  | 177:napaka_kom_panel:=Bit_0; |  |  |  | 4355:PMM2.VirBAparentPowerPhaseC:=Real_0;
mind_bool[178]:=napaka_kom_scada; |  |  |  | Read_Real(rVar:=PMM2.VirBCurrentInPhaseA_A,lo:=4356,hi:=4357); |  |  | 178:napaka_kom_scada:=Bit_0; |  |  |  | 4357:PMM2.VirBCurrentInPhaseA_A:=Real_0;
mind_bool[179]:=napaka_kom_scada2; |  |  |  | Read_Real(rVar:=PMM2.VirBCurrentInPhaseB_A,lo:=4358,hi:=4359); |  |  | 179:napaka_kom_scada2:=Bit_0; |  |  |  | 4359:PMM2.VirBCurrentInPhaseB_A:=Real_0;
mind_bool[180]:=NapakaSenzorSkupno; |  |  |  | Read_Real(rVar:=PMM2.VirBCurrentInPhaseC_A,lo:=4360,hi:=4361); |  |  | 180:NapakaSenzorSkupno:=Bit_0; |  |  |  | 4361:PMM2.VirBCurrentInPhaseC_A:=Real_0;
mind_bool[181]:=NapakaSenzorVlagaHIA1; |  |  |  | Read_Real(rVar:=PMM2.VirBReactiveEnergyConsumed_kVARh,lo:=4362,hi:=4363); |  |  | 181:NapakaSenzorVlagaHIA1:=Bit_0; |  |  |  | 4363:PMM2.VirBReactiveEnergyConsumed_kVARh:=Real_0;
mind_bool[182]:=NapakaSenzorVlagaHIA2; |  |  |  | Read_Real(rVar:=PMM2.VirBReactivePowerPhaseA,lo:=4364,hi:=4365); |  |  | 182:NapakaSenzorVlagaHIA2:=Bit_0; |  |  |  | 4365:PMM2.VirBReactivePowerPhaseA:=Real_0;
mind_bool[183]:=NapakaSenzorVlagaHIA3; |  |  |  | Read_Real(rVar:=PMM2.VirBReactivePowerPhaseB,lo:=4366,hi:=4367); |  |  | 183:NapakaSenzorVlagaHIA3:=Bit_0; |  |  |  | 4367:PMM2.VirBReactivePowerPhaseB:=Real_0;
mind_bool[184]:=NapakaSenzorVlagaHIA4; |  |  |  | Read_Real(rVar:=PMM2.VirBReactivePowerPhaseC,lo:=4368,hi:=4369); |  |  | 184:NapakaSenzorVlagaHIA4:=Bit_0; |  |  |  | 4369:PMM2.VirBReactivePowerPhaseC:=Real_0;
mind_bool[185]:=NapakaSenzorVlagaHIA5; |  |  |  | Read_Real(rVar:=PMM2.VirBVoltageBetweenPhaseAB_V,lo:=4370,hi:=4371); |  |  | 185:NapakaSenzorVlagaHIA5:=Bit_0; |  |  |  | 4371:PMM2.VirBVoltageBetweenPhaseAB_V:=Real_0;
mind_bool[186]:=NapakaSenzorVlagaHIA6; |  |  |  | Read_Real(rVar:=PMM2.VirBVoltageBetweenPhaseAN_V,lo:=4372,hi:=4373); |  |  | 186:NapakaSenzorVlagaHIA6:=Bit_0; |  |  |  | 4373:PMM2.VirBVoltageBetweenPhaseAN_V:=Real_0;
mind_bool[187]:=NapakaSenzorVlagaHIA7; |  |  |  | Read_Real(rVar:=PMM2.VirBVoltageBetweenPhaseBC_V,lo:=4374,hi:=4375); |  |  | 187:NapakaSenzorVlagaHIA7:=Bit_0; |  |  |  | 4375:PMM2.VirBVoltageBetweenPhaseBC_V:=Real_0;
mind_bool[188]:=NapakaTSTempTIA1; |  |  |  | Read_Real(rVar:=PMM2.VirBVoltageBetweenPhaseBN_V,lo:=4376,hi:=4377); |  |  | 188:NapakaTSTempTIA1:=Bit_0; |  |  |  | 4377:PMM2.VirBVoltageBetweenPhaseBN_V:=Real_0;
mind_bool[189]:=NapakaTSTempTIA2; |  |  |  | Read_Real(rVar:=PMM2.VirBVoltageBetweenPhaseCA_V,lo:=4378,hi:=4379); |  |  | 189:NapakaTSTempTIA2:=Bit_0; |  |  |  | 4379:PMM2.VirBVoltageBetweenPhaseCA_V:=Real_0;
mind_bool[190]:=NapakaTSTempTIA3; |  |  |  | Read_Real(rVar:=PMM2.VirBVoltageBetweenPhaseCN_V,lo:=4380,hi:=4381); |  |  | 190:NapakaTSTempTIA3:=Bit_0; |  |  |  | 4381:PMM2.VirBVoltageBetweenPhaseCN_V:=Real_0;
mind_bool[191]:=NapakaTSTempTIA4; |  |  |  | Read_Real(rVar:=PMM[1].ActiveEnergyConsumed_kWh,lo:=4382,hi:=4383); |  |  | 191:NapakaTSTempTIA4:=Bit_0; |  |  |  | 4383:PMM[1].ActiveEnergyConsumed_kWh:=Real_0;
mind_bool[192]:=NapakaTSTempTIA5; |  |  |  | Read_Real(rVar:=PMM[1].ActivePowerPhaseA_kW,lo:=4384,hi:=4385); |  |  | 192:NapakaTSTempTIA5:=Bit_0; |  |  |  | 4385:PMM[1].ActivePowerPhaseA_kW:=Real_0;
mind_bool[193]:=NapakaTSTempTIA6; |  |  |  | Read_Real(rVar:=PMM[1].ActivePowerPhaseB_kW,lo:=4386,hi:=4387); |  |  | 193:NapakaTSTempTIA6:=Bit_0; |  |  |  | 4387:PMM[1].ActivePowerPhaseB_kW:=Real_0;
mind_bool[194]:=NapakaTSTempTIA7; |  |  |  | Read_Real(rVar:=PMM[1].ActivePowerPhaseC_kW,lo:=4388,hi:=4389); |  |  | 194:NapakaTSTempTIA7:=Bit_0; |  |  |  | 4389:PMM[1].ActivePowerPhaseC_kW:=Real_0;
mind_bool[195]:=OpozoriloPMM2x17med60in80[10]; |  |  |  | Read_Real(rVar:=PMM[1].AparentPowerPhaseA,lo:=4390,hi:=4391); |  |  | 195:OpozoriloPMM2x17med60in80[10]:=Bit_0; |  |  |  | 4391:PMM[1].AparentPowerPhaseA:=Real_0;
mind_bool[196]:=OpozoriloPMM2x17med60in80[11]; |  |  |  | Read_Real(rVar:=PMM[1].AparentPowerPhaseB,lo:=4392,hi:=4393); |  |  | 196:OpozoriloPMM2x17med60in80[11]:=Bit_0; |  |  |  | 4393:PMM[1].AparentPowerPhaseB:=Real_0;
mind_bool[197]:=OpozoriloPMM2x17med60in80[12]; |  |  |  | Read_Real(rVar:=PMM[1].AparentPowerPhaseC,lo:=4394,hi:=4395); |  |  | 197:OpozoriloPMM2x17med60in80[12]:=Bit_0; |  |  |  | 4395:PMM[1].AparentPowerPhaseC:=Real_0;
mind_bool[198]:=OpozoriloPMM2x17med60in80[13]; |  |  |  | Read_Real(rVar:=PMM[1].AverageCurrent_A,lo:=4396,hi:=4397); |  |  | 198:OpozoriloPMM2x17med60in80[13]:=Bit_0; |  |  |  | 4397:PMM[1].AverageCurrent_A:=Real_0;
mind_bool[199]:=OpozoriloPMM2x17med60in80[14]; |  |  |  | Read_Real(rVar:=PMM[1].AveragePhaseToNeutral_V,lo:=4398,hi:=4399); |  |  | 199:OpozoriloPMM2x17med60in80[14]:=Bit_0; |  |  |  | 4399:PMM[1].AveragePhaseToNeutral_V:=Real_0;
mind_bool[200]:=OpozoriloPMM2x17med60in80[15]; |  |  |  | Read_Real(rVar:=PMM[1].AveragePhaseToPhase_V,lo:=4400,hi:=4401); |  |  | 200:OpozoriloPMM2x17med60in80[15]:=Bit_0; |  |  |  | 4401:PMM[1].AveragePhaseToPhase_V:=Real_0;
mind_bool[201]:=OpozoriloPMM2x17med60in80[16]; |  |  |  | Read_Real(rVar:=PMM[1].CurrentInPhaseA_A,lo:=4402,hi:=4403); |  |  | 201:OpozoriloPMM2x17med60in80[16]:=Bit_0; |  |  |  | 4403:PMM[1].CurrentInPhaseA_A:=Real_0;
mind_bool[202]:=OpozoriloPMM2x17med60in80[17]; |  |  |  | Read_Real(rVar:=PMM[1].CurrentInPhaseB_A,lo:=4404,hi:=4405); |  |  | 202:OpozoriloPMM2x17med60in80[17]:=Bit_0; |  |  |  | 4405:PMM[1].CurrentInPhaseB_A:=Real_0;
mind_bool[203]:=OpozoriloPMM2x17med60in80[18]; |  |  |  | Read_Real(rVar:=PMM[1].CurrentInPhaseC_A,lo:=4406,hi:=4407); |  |  | 203:OpozoriloPMM2x17med60in80[18]:=Bit_0; |  |  |  | 4407:PMM[1].CurrentInPhaseC_A:=Real_0;
mind_bool[204]:=OpozoriloPMM2x17med60in80[19]; |  |  |  | Read_Real(rVar:=PMM[1].Frequency_Hz,lo:=4408,hi:=4409); |  |  | 204:OpozoriloPMM2x17med60in80[19]:=Bit_0; |  |  |  | 4409:PMM[1].Frequency_Hz:=Real_0;
mind_bool[205]:=OpozoriloPMM2x17med60in80[1]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[10],lo:=4410,hi:=4411); |  |  | 205:OpozoriloPMM2x17med60in80[1]:=Bit_0; |  |  |  | 4411:PMM[1].Phase[1].Current[10]:=Real_0;
mind_bool[206]:=OpozoriloPMM2x17med60in80[20]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[11],lo:=4412,hi:=4413); |  |  | 206:OpozoriloPMM2x17med60in80[20]:=Bit_0; |  |  |  | 4413:PMM[1].Phase[1].Current[11]:=Real_0;
mind_bool[207]:=OpozoriloPMM2x17med60in80[21]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[12],lo:=4414,hi:=4415); |  |  | 207:OpozoriloPMM2x17med60in80[21]:=Bit_0; |  |  |  | 4415:PMM[1].Phase[1].Current[12]:=Real_0;
mind_bool[208]:=OpozoriloPMM2x17med60in80[22]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[13],lo:=4416,hi:=4417); |  |  | 208:OpozoriloPMM2x17med60in80[22]:=Bit_0; |  |  |  | 4417:PMM[1].Phase[1].Current[13]:=Real_0;
mind_bool[209]:=OpozoriloPMM2x17med60in80[23]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[14],lo:=4418,hi:=4419); |  |  | 209:OpozoriloPMM2x17med60in80[23]:=Bit_0; |  |  |  | 4419:PMM[1].Phase[1].Current[14]:=Real_0;
mind_bool[210]:=OpozoriloPMM2x17med60in80[24]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[15],lo:=4420,hi:=4421); |  |  | 210:OpozoriloPMM2x17med60in80[24]:=Bit_0; |  |  |  | 4421:PMM[1].Phase[1].Current[15]:=Real_0;
mind_bool[211]:=OpozoriloPMM2x17med60in80[25]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[16],lo:=4422,hi:=4423); |  |  | 211:OpozoriloPMM2x17med60in80[25]:=Bit_0; |  |  |  | 4423:PMM[1].Phase[1].Current[16]:=Real_0;
mind_bool[212]:=OpozoriloPMM2x17med60in80[26]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[17],lo:=4424,hi:=4425); |  |  | 212:OpozoriloPMM2x17med60in80[26]:=Bit_0; |  |  |  | 4425:PMM[1].Phase[1].Current[17]:=Real_0;
mind_bool[213]:=OpozoriloPMM2x17med60in80[27]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[18],lo:=4426,hi:=4427); |  |  | 213:OpozoriloPMM2x17med60in80[27]:=Bit_0; |  |  |  | 4427:PMM[1].Phase[1].Current[18]:=Real_0;
mind_bool[214]:=OpozoriloPMM2x17med60in80[28]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[19],lo:=4428,hi:=4429); |  |  | 214:OpozoriloPMM2x17med60in80[28]:=Bit_0; |  |  |  | 4429:PMM[1].Phase[1].Current[19]:=Real_0;
mind_bool[215]:=OpozoriloPMM2x17med60in80[29]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[1],lo:=4430,hi:=4431); |  |  | 215:OpozoriloPMM2x17med60in80[29]:=Bit_0; |  |  |  | 4431:PMM[1].Phase[1].Current[1]:=Real_0;
mind_bool[216]:=OpozoriloPMM2x17med60in80[2]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[20],lo:=4432,hi:=4433); |  |  | 216:OpozoriloPMM2x17med60in80[2]:=Bit_0; |  |  |  | 4433:PMM[1].Phase[1].Current[20]:=Real_0;
mind_bool[217]:=OpozoriloPMM2x17med60in80[30]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[21],lo:=4434,hi:=4435); |  |  | 217:OpozoriloPMM2x17med60in80[30]:=Bit_0; |  |  |  | 4435:PMM[1].Phase[1].Current[21]:=Real_0;
mind_bool[218]:=OpozoriloPMM2x17med60in80[31]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[22],lo:=4436,hi:=4437); |  |  | 218:OpozoriloPMM2x17med60in80[31]:=Bit_0; |  |  |  | 4437:PMM[1].Phase[1].Current[22]:=Real_0;
mind_bool[219]:=OpozoriloPMM2x17med60in80[32]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[23],lo:=4438,hi:=4439); |  |  | 219:OpozoriloPMM2x17med60in80[32]:=Bit_0; |  |  |  | 4439:PMM[1].Phase[1].Current[23]:=Real_0;
mind_bool[220]:=OpozoriloPMM2x17med60in80[33]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[24],lo:=4440,hi:=4441); |  |  | 220:OpozoriloPMM2x17med60in80[33]:=Bit_0; |  |  |  | 4441:PMM[1].Phase[1].Current[24]:=Real_0;
mind_bool[221]:=OpozoriloPMM2x17med60in80[34]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[25],lo:=4442,hi:=4443); |  |  | 221:OpozoriloPMM2x17med60in80[34]:=Bit_0; |  |  |  | 4443:PMM[1].Phase[1].Current[25]:=Real_0;
mind_bool[222]:=OpozoriloPMM2x17med60in80[35]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[26],lo:=4444,hi:=4445); |  |  | 222:OpozoriloPMM2x17med60in80[35]:=Bit_0; |  |  |  | 4445:PMM[1].Phase[1].Current[26]:=Real_0;
mind_bool[223]:=OpozoriloPMM2x17med60in80[36]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[27],lo:=4446,hi:=4447); |  |  | 223:OpozoriloPMM2x17med60in80[36]:=Bit_0; |  |  |  | 4447:PMM[1].Phase[1].Current[27]:=Real_0;
mind_bool[224]:=OpozoriloPMM2x17med60in80[37]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[28],lo:=4448,hi:=4449); |  |  | 224:OpozoriloPMM2x17med60in80[37]:=Bit_0; |  |  |  | 4449:PMM[1].Phase[1].Current[28]:=Real_0;
mind_bool[225]:=OpozoriloPMM2x17med60in80[38]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[29],lo:=4450,hi:=4451); |  |  | 225:OpozoriloPMM2x17med60in80[38]:=Bit_0; |  |  |  | 4451:PMM[1].Phase[1].Current[29]:=Real_0;
mind_bool[226]:=OpozoriloPMM2x17med60in80[39]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[2],lo:=4452,hi:=4453); |  |  | 226:OpozoriloPMM2x17med60in80[39]:=Bit_0; |  |  |  | 4453:PMM[1].Phase[1].Current[2]:=Real_0;
mind_bool[227]:=OpozoriloPMM2x17med60in80[3]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[30],lo:=4454,hi:=4455); |  |  | 227:OpozoriloPMM2x17med60in80[3]:=Bit_0; |  |  |  | 4455:PMM[1].Phase[1].Current[30]:=Real_0;
mind_bool[228]:=OpozoriloPMM2x17med60in80[40]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[31],lo:=4456,hi:=4457); |  |  | 228:OpozoriloPMM2x17med60in80[40]:=Bit_0; |  |  |  | 4457:PMM[1].Phase[1].Current[31]:=Real_0;
mind_bool[229]:=OpozoriloPMM2x17med60in80[41]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[32],lo:=4458,hi:=4459); |  |  | 229:OpozoriloPMM2x17med60in80[41]:=Bit_0; |  |  |  | 4459:PMM[1].Phase[1].Current[32]:=Real_0;
mind_bool[230]:=OpozoriloPMM2x17med60in80[42]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[33],lo:=4460,hi:=4461); |  |  | 230:OpozoriloPMM2x17med60in80[42]:=Bit_0; |  |  |  | 4461:PMM[1].Phase[1].Current[33]:=Real_0;
mind_bool[231]:=OpozoriloPMM2x17med60in80[4]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[34],lo:=4462,hi:=4463); |  |  | 231:OpozoriloPMM2x17med60in80[4]:=Bit_0; |  |  |  | 4463:PMM[1].Phase[1].Current[34]:=Real_0;
mind_bool[232]:=OpozoriloPMM2x17med60in80[5]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[35],lo:=4464,hi:=4465); |  |  | 232:OpozoriloPMM2x17med60in80[5]:=Bit_0; |  |  |  | 4465:PMM[1].Phase[1].Current[35]:=Real_0;
mind_bool[233]:=OpozoriloPMM2x17med60in80[6]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[36],lo:=4466,hi:=4467); |  |  | 233:OpozoriloPMM2x17med60in80[6]:=Bit_0; |  |  |  | 4467:PMM[1].Phase[1].Current[36]:=Real_0;
mind_bool[234]:=OpozoriloPMM2x17med60in80[7]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[37],lo:=4468,hi:=4469); |  |  | 234:OpozoriloPMM2x17med60in80[7]:=Bit_0; |  |  |  | 4469:PMM[1].Phase[1].Current[37]:=Real_0;
mind_bool[235]:=OpozoriloPMM2x17med60in80[8]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[38],lo:=4470,hi:=4471); |  |  | 235:OpozoriloPMM2x17med60in80[8]:=Bit_0; |  |  |  | 4471:PMM[1].Phase[1].Current[38]:=Real_0;
mind_bool[236]:=OpozoriloPMM2x17med60in80[9]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[39],lo:=4472,hi:=4473); |  |  | 236:OpozoriloPMM2x17med60in80[9]:=Bit_0; |  |  |  | 4473:PMM[1].Phase[1].Current[39]:=Real_0;
mind_bool[237]:=PMM1OverCurrentBetw[1]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[3],lo:=4474,hi:=4475); |  |  | 237:PMM1OverCurrentBetw[1]:=Bit_0; |  |  |  | 4475:PMM[1].Phase[1].Current[3]:=Real_0;
mind_bool[238]:=PMM1OverCurrentBetw[2]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[40],lo:=4476,hi:=4477); |  |  | 238:PMM1OverCurrentBetw[2]:=Bit_0; |  |  |  | 4477:PMM[1].Phase[1].Current[40]:=Real_0;
mind_bool[239]:=PMM1OverCurrentBetw[3]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[41],lo:=4478,hi:=4479); |  |  | 239:PMM1OverCurrentBetw[3]:=Bit_0; |  |  |  | 4479:PMM[1].Phase[1].Current[41]:=Real_0;
mind_bool[240]:=PMM1OverCurrentOver[1]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[42],lo:=4480,hi:=4481); |  |  | 240:PMM1OverCurrentOver[1]:=Bit_0; |  |  |  | 4481:PMM[1].Phase[1].Current[42]:=Real_0;
mind_bool[241]:=PMM1OverCurrentOver[2]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[4],lo:=4482,hi:=4483); |  |  | 241:PMM1OverCurrentOver[2]:=Bit_0; |  |  |  | 4483:PMM[1].Phase[1].Current[4]:=Real_0;
mind_bool[242]:=PMM1OverCurrentOver[3]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[5],lo:=4484,hi:=4485); |  |  | 242:PMM1OverCurrentOver[3]:=Bit_0; |  |  |  | 4485:PMM[1].Phase[1].Current[5]:=Real_0;
mind_bool[243]:=PMM2.QA1_GlStik_IZKLOP_IZPAD; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[6],lo:=4486,hi:=4487); |  |  | 243:PMM2.QA1_GlStik_IZKLOP_IZPAD:=Bit_0; |  |  |  | 4487:PMM[1].Phase[1].Current[6]:=Real_0;
mind_bool[244]:=PMM2.QB1_GlStik_IZKLOP_IZPAD; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[7],lo:=4488,hi:=4489); |  |  | 244:PMM2.QB1_GlStik_IZKLOP_IZPAD:=Bit_0; |  |  |  | 4489:PMM[1].Phase[1].Current[7]:=Real_0;
mind_bool[245]:=PMM2.SkNapaka_med60in80; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[8],lo:=4490,hi:=4491); |  |  | 245:PMM2.SkNapaka_med60in80:=Bit_0; |  |  |  | 4491:PMM[1].Phase[1].Current[8]:=Real_0;
mind_bool[246]:=PMM2.SkNapaka_nad80; |  |  |  | Read_Real(rVar:=PMM[1].Phase[1].Current[9],lo:=4492,hi:=4493); |  |  | 246:PMM2.SkNapaka_nad80:=Bit_0; |  |  |  | 4493:PMM[1].Phase[1].Current[9]:=Real_0;
mind_bool[247]:=PMM2.SkNapakaVirA_med60in80; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[10],lo:=4494,hi:=4495); |  |  | 247:PMM2.SkNapakaVirA_med60in80:=Bit_0; |  |  |  | 4495:PMM[1].Phase[2].Current[10]:=Real_0;
mind_bool[248]:=PMM2.SkNapakaVirA_nad80; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[11],lo:=4496,hi:=4497); |  |  | 248:PMM2.SkNapakaVirA_nad80:=Bit_0; |  |  |  | 4497:PMM[1].Phase[2].Current[11]:=Real_0;
mind_bool[249]:=PMM2.SkNapakaVirB_med60in80; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[12],lo:=4498,hi:=4499); |  |  | 249:PMM2.SkNapakaVirB_med60in80:=Bit_0; |  |  |  | 4499:PMM[1].Phase[2].Current[12]:=Real_0;
mind_bool[250]:=PMM2.SkNapakaVirB_nad80; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[13],lo:=4500,hi:=4501); |  |  | 250:PMM2.SkNapakaVirB_nad80:=Bit_0; |  |  |  | 4501:PMM[1].Phase[2].Current[13]:=Real_0;
mind_bool[251]:=PMM2.VirA_NapakaOzemljitve; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[14],lo:=4502,hi:=4503); |  |  | 251:PMM2.VirA_NapakaOzemljitve:=Bit_0; |  |  |  | 4503:PMM[1].Phase[2].Current[14]:=Real_0;
mind_bool[252]:=PMM2.VirB_NapakaOzemljitve; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[15],lo:=4504,hi:=4505); |  |  | 252:PMM2.VirB_NapakaOzemljitve:=Bit_0; |  |  |  | 4505:PMM[1].Phase[2].Current[15]:=Real_0;
mind_bool[253]:=PozarnaCentrala_skupno; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[16],lo:=4506,hi:=4507); |  |  | 253:PozarnaCentrala_skupno:=Bit_0; |  |  |  | 4507:PMM[1].Phase[2].Current[16]:=Real_0;
mind_bool[254]:=PrevisokaTemp; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[17],lo:=4508,hi:=4509); |  |  | 254:PrevisokaTemp:=Bit_0; |  |  |  | 4509:PMM[1].Phase[2].Current[17]:=Real_0;
mind_bool[255]:=Q0_izkljuceno; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[18],lo:=4510,hi:=4511); |  |  | 255:Q0_izkljuceno:=Bit_0; |  |  |  | 4511:PMM[1].Phase[2].Current[18]:=Real_0;
mind_bool[256]:=Q0_vkljuceno; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[19],lo:=4512,hi:=4513); |  |  | 256:Q0_vkljuceno:=Bit_0; |  |  |  | 4513:PMM[1].Phase[2].Current[19]:=Real_0;
mind_bool[257]:=Q12_izkljuceno; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[1],lo:=4514,hi:=4515); |  |  | 257:Q12_izkljuceno:=Bit_0; |  |  |  | 4515:PMM[1].Phase[2].Current[1]:=Real_0;
mind_bool[258]:=Q12_izpad; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[20],lo:=4516,hi:=4517); |  |  | 258:Q12_izpad:=Bit_0; |  |  |  | 4517:PMM[1].Phase[2].Current[20]:=Real_0;
mind_bool[259]:=Q12_vkljuceno; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[21],lo:=4518,hi:=4519); |  |  | 259:Q12_vkljuceno:=Bit_0; |  |  |  | 4519:PMM[1].Phase[2].Current[21]:=Real_0;
mind_bool[260]:=Q21_vkljuceno; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[22],lo:=4520,hi:=4521); |  |  | 260:Q21_vkljuceno:=Bit_0; |  |  |  | 4521:PMM[1].Phase[2].Current[22]:=Real_0;
mind_bool[261]:=Q22_vkljuceno; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[23],lo:=4522,hi:=4523); |  |  | 261:Q22_vkljuceno:=Bit_0; |  |  |  | 4523:PMM[1].Phase[2].Current[23]:=Real_0;
mind_bool[262]:=razlitjeLAH1; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[24],lo:=4524,hi:=4525); |  |  | 262:razlitjeLAH1:=Bit_0; |  |  |  | 4525:PMM[1].Phase[2].Current[24]:=Real_0;
mind_bool[263]:=razlitjeLAH2; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[25],lo:=4526,hi:=4527); |  |  | 263:razlitjeLAH2:=Bit_0; |  |  |  | 4527:PMM[1].Phase[2].Current[25]:=Real_0;
mind_bool[264]:=razlitjeLAH3; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[26],lo:=4528,hi:=4529); |  |  | 264:razlitjeLAH3:=Bit_0; |  |  |  | 4529:PMM[1].Phase[2].Current[26]:=Real_0;
mind_bool[265]:=razlitjeLAH4; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[27],lo:=4530,hi:=4531); |  |  | 265:razlitjeLAH4:=Bit_0; |  |  |  | 4531:PMM[1].Phase[2].Current[27]:=Real_0;
mind_bool[266]:=SetDateTime; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[28],lo:=4532,hi:=4533); |  |  | 266:SetDateTime:=Bit_0; |  |  |  | 4533:PMM[1].Phase[2].Current[28]:=Real_0;
mind_bool[267]:=SetDateTimeDemand; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[29],lo:=4534,hi:=4535); |  |  | 267:SetDateTimeDemand:=Bit_0; |  |  |  | 4535:PMM[1].Phase[2].Current[29]:=Real_0;
mind_bool[268]:=SetDateTimeError; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[2],lo:=4536,hi:=4537); |  |  | 268:SetDateTimeError:=Bit_0; |  |  |  | 4537:PMM[1].Phase[2].Current[2]:=Real_0;
mind_bool[269]:=SetDateTimeFinished; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[30],lo:=4538,hi:=4539); |  |  | 269:SetDateTimeFinished:=Bit_0; |  |  |  | 4539:PMM[1].Phase[2].Current[30]:=Real_0;
mind_bool[270]:=SkupneNapakeNaprav_PMM17VirBVirA; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[31],lo:=4540,hi:=4541); |  |  | 270:SkupneNapakeNaprav_PMM17VirBVirA:=Bit_0; |  |  |  | 4541:PMM[1].Phase[2].Current[31]:=Real_0;
mind_bool[271]:=SlabaBaterijaPLC; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[32],lo:=4542,hi:=4543); |  |  | 271:SlabaBaterijaPLC:=Bit_0; |  |  |  | 4543:PMM[1].Phase[2].Current[32]:=Real_0;
mind_bool[272]:=TempPovp234Previs; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[33],lo:=4544,hi:=4545); |  |  | 272:TempPovp234Previs:=Bit_0; |  |  |  | 4545:PMM[1].Phase[2].Current[33]:=Real_0;
mind_bool[273]:=TempPovp56Previs; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[34],lo:=4546,hi:=4547); |  |  | 273:TempPovp56Previs:=Bit_0; |  |  |  | 4547:PMM[1].Phase[2].Current[34]:=Real_0;
mind_bool[274]:=TIA1_previs_temp; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[35],lo:=4548,hi:=4549); |  |  | 274:TIA1_previs_temp:=Bit_0; |  |  |  | 4549:PMM[1].Phase[2].Current[35]:=Real_0;
mind_bool[275]:=TIA2_previs_temp; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[36],lo:=4550,hi:=4551); |  |  | 275:TIA2_previs_temp:=Bit_0; |  |  |  | 4551:PMM[1].Phase[2].Current[36]:=Real_0;
mind_bool[276]:=TIA3_previs_temp; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[37],lo:=4552,hi:=4553); |  |  | 276:TIA3_previs_temp:=Bit_0; |  |  |  | 4553:PMM[1].Phase[2].Current[37]:=Real_0;
mind_bool[277]:=TIA4_previs_temp; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[38],lo:=4554,hi:=4555); |  |  | 277:TIA4_previs_temp:=Bit_0; |  |  |  | 4555:PMM[1].Phase[2].Current[38]:=Real_0;
mind_bool[278]:=TIA5_previs_temp; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[39],lo:=4556,hi:=4557); |  |  | 278:TIA5_previs_temp:=Bit_0; |  |  |  | 4557:PMM[1].Phase[2].Current[39]:=Real_0;
mind_bool[279]:=TIA6_previs_temp; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[3],lo:=4558,hi:=4559); |  |  | 279:TIA6_previs_temp:=Bit_0; |  |  |  | 4559:PMM[1].Phase[2].Current[3]:=Real_0;
mind_bool[280]:=TIA7_previs_temp; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[40],lo:=4560,hi:=4561); |  |  | 280:TIA7_previs_temp:=Bit_0; |  |  |  | 4561:PMM[1].Phase[2].Current[40]:=Real_0;
mind_bool[281]:=UPS1Errors[10]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[41],lo:=4562,hi:=4563); |  |  | 281:UPS1Errors[10]:=Bit_0; |  |  |  | 4563:PMM[1].Phase[2].Current[41]:=Real_0;
mind_bool[282]:=UPS1Errors[11]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[42],lo:=4564,hi:=4565); |  |  | 282:UPS1Errors[11]:=Bit_0; |  |  |  | 4565:PMM[1].Phase[2].Current[42]:=Real_0;
mind_bool[283]:=UPS1Errors[12]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[4],lo:=4566,hi:=4567); |  |  | 283:UPS1Errors[12]:=Bit_0; |  |  |  | 4567:PMM[1].Phase[2].Current[4]:=Real_0;
mind_bool[284]:=UPS1Errors[13]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[5],lo:=4568,hi:=4569); |  |  | 284:UPS1Errors[13]:=Bit_0; |  |  |  | 4569:PMM[1].Phase[2].Current[5]:=Real_0;
mind_bool[285]:=UPS1Errors[14]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[6],lo:=4570,hi:=4571); |  |  | 285:UPS1Errors[14]:=Bit_0; |  |  |  | 4571:PMM[1].Phase[2].Current[6]:=Real_0;
mind_bool[286]:=UPS1Errors[15]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[7],lo:=4572,hi:=4573); |  |  | 286:UPS1Errors[15]:=Bit_0; |  |  |  | 4573:PMM[1].Phase[2].Current[7]:=Real_0;
mind_bool[287]:=UPS1Errors[16]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[8],lo:=4574,hi:=4575); |  |  | 287:UPS1Errors[16]:=Bit_0; |  |  |  | 4575:PMM[1].Phase[2].Current[8]:=Real_0;
mind_bool[288]:=UPS1Errors[17]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[2].Current[9],lo:=4576,hi:=4577); |  |  | 288:UPS1Errors[17]:=Bit_0; |  |  |  | 4577:PMM[1].Phase[2].Current[9]:=Real_0;
mind_bool[289]:=UPS1Errors[18]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[10],lo:=4578,hi:=4579); |  |  | 289:UPS1Errors[18]:=Bit_0; |  |  |  | 4579:PMM[1].Phase[3].Current[10]:=Real_0;
mind_bool[290]:=UPS1Errors[19]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[11],lo:=4580,hi:=4581); |  |  | 290:UPS1Errors[19]:=Bit_0; |  |  |  | 4581:PMM[1].Phase[3].Current[11]:=Real_0;
mind_bool[291]:=UPS1Errors[1]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[12],lo:=4582,hi:=4583); |  |  | 291:UPS1Errors[1]:=Bit_0; |  |  |  | 4583:PMM[1].Phase[3].Current[12]:=Real_0;
mind_bool[292]:=UPS1Errors[20]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[13],lo:=4584,hi:=4585); |  |  | 292:UPS1Errors[20]:=Bit_0; |  |  |  | 4585:PMM[1].Phase[3].Current[13]:=Real_0;
mind_bool[293]:=UPS1Errors[21]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[14],lo:=4586,hi:=4587); |  |  | 293:UPS1Errors[21]:=Bit_0; |  |  |  | 4587:PMM[1].Phase[3].Current[14]:=Real_0;
mind_bool[294]:=UPS1Errors[22]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[15],lo:=4588,hi:=4589); |  |  | 294:UPS1Errors[22]:=Bit_0; |  |  |  | 4589:PMM[1].Phase[3].Current[15]:=Real_0;
mind_bool[295]:=UPS1Errors[23]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[16],lo:=4590,hi:=4591); |  |  | 295:UPS1Errors[23]:=Bit_0; |  |  |  | 4591:PMM[1].Phase[3].Current[16]:=Real_0;
mind_bool[296]:=UPS1Errors[24]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[17],lo:=4592,hi:=4593); |  |  | 296:UPS1Errors[24]:=Bit_0; |  |  |  | 4593:PMM[1].Phase[3].Current[17]:=Real_0;
mind_bool[297]:=UPS1Errors[25]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[18],lo:=4594,hi:=4595); |  |  | 297:UPS1Errors[25]:=Bit_0; |  |  |  | 4595:PMM[1].Phase[3].Current[18]:=Real_0;
mind_bool[298]:=UPS1Errors[2]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[19],lo:=4596,hi:=4597); |  |  | 298:UPS1Errors[2]:=Bit_0; |  |  |  | 4597:PMM[1].Phase[3].Current[19]:=Real_0;
mind_bool[299]:=UPS1Errors[3]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[1],lo:=4598,hi:=4599); |  |  | 299:UPS1Errors[3]:=Bit_0; |  |  |  | 4599:PMM[1].Phase[3].Current[1]:=Real_0;
mind_bool[300]:=UPS1Errors[4]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[20],lo:=4600,hi:=4601); |  |  | 300:UPS1Errors[4]:=Bit_0; |  |  |  | 4601:PMM[1].Phase[3].Current[20]:=Real_0;
mind_bool[301]:=UPS1Errors[5]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[21],lo:=4602,hi:=4603); |  |  | 301:UPS1Errors[5]:=Bit_0; |  |  |  | 4603:PMM[1].Phase[3].Current[21]:=Real_0;
mind_bool[302]:=UPS1Errors[6]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[22],lo:=4604,hi:=4605); |  |  | 302:UPS1Errors[6]:=Bit_0; |  |  |  | 4605:PMM[1].Phase[3].Current[22]:=Real_0;
mind_bool[303]:=UPS1Errors[7]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[23],lo:=4606,hi:=4607); |  |  | 303:UPS1Errors[7]:=Bit_0; |  |  |  | 4607:PMM[1].Phase[3].Current[23]:=Real_0;
mind_bool[304]:=UPS1Errors[8]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[24],lo:=4608,hi:=4609); |  |  | 304:UPS1Errors[8]:=Bit_0; |  |  |  | 4609:PMM[1].Phase[3].Current[24]:=Real_0;
mind_bool[305]:=UPS1Errors[9]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[25],lo:=4610,hi:=4611); |  |  | 305:UPS1Errors[9]:=Bit_0; |  |  |  | 4611:PMM[1].Phase[3].Current[25]:=Real_0;
mind_bool[306]:=UPS2Errors[10]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[26],lo:=4612,hi:=4613); |  |  | 306:UPS2Errors[10]:=Bit_0; |  |  |  | 4613:PMM[1].Phase[3].Current[26]:=Real_0;
mind_bool[307]:=UPS2Errors[11]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[27],lo:=4614,hi:=4615); |  |  | 307:UPS2Errors[11]:=Bit_0; |  |  |  | 4615:PMM[1].Phase[3].Current[27]:=Real_0;
mind_bool[308]:=UPS2Errors[12]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[28],lo:=4616,hi:=4617); |  |  | 308:UPS2Errors[12]:=Bit_0; |  |  |  | 4617:PMM[1].Phase[3].Current[28]:=Real_0;
mind_bool[309]:=UPS2Errors[13]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[29],lo:=4618,hi:=4619); |  |  | 309:UPS2Errors[13]:=Bit_0; |  |  |  | 4619:PMM[1].Phase[3].Current[29]:=Real_0;
mind_bool[310]:=UPS2Errors[14]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[2],lo:=4620,hi:=4621); |  |  | 310:UPS2Errors[14]:=Bit_0; |  |  |  | 4621:PMM[1].Phase[3].Current[2]:=Real_0;
mind_bool[311]:=UPS2Errors[15]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[30],lo:=4622,hi:=4623); |  |  | 311:UPS2Errors[15]:=Bit_0; |  |  |  | 4623:PMM[1].Phase[3].Current[30]:=Real_0;
mind_bool[312]:=UPS2Errors[16]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[31],lo:=4624,hi:=4625); |  |  | 312:UPS2Errors[16]:=Bit_0; |  |  |  | 4625:PMM[1].Phase[3].Current[31]:=Real_0;
mind_bool[313]:=UPS2Errors[17]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[32],lo:=4626,hi:=4627); |  |  | 313:UPS2Errors[17]:=Bit_0; |  |  |  | 4627:PMM[1].Phase[3].Current[32]:=Real_0;
mind_bool[314]:=UPS2Errors[18]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[33],lo:=4628,hi:=4629); |  |  | 314:UPS2Errors[18]:=Bit_0; |  |  |  | 4629:PMM[1].Phase[3].Current[33]:=Real_0;
mind_bool[315]:=UPS2Errors[19]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[34],lo:=4630,hi:=4631); |  |  | 315:UPS2Errors[19]:=Bit_0; |  |  |  | 4631:PMM[1].Phase[3].Current[34]:=Real_0;
mind_bool[316]:=UPS2Errors[1]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[35],lo:=4632,hi:=4633); |  |  | 316:UPS2Errors[1]:=Bit_0; |  |  |  | 4633:PMM[1].Phase[3].Current[35]:=Real_0;
mind_bool[317]:=UPS2Errors[20]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[36],lo:=4634,hi:=4635); |  |  | 317:UPS2Errors[20]:=Bit_0; |  |  |  | 4635:PMM[1].Phase[3].Current[36]:=Real_0;
mind_bool[318]:=UPS2Errors[21]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[37],lo:=4636,hi:=4637); |  |  | 318:UPS2Errors[21]:=Bit_0; |  |  |  | 4637:PMM[1].Phase[3].Current[37]:=Real_0;
mind_bool[319]:=UPS2Errors[22]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[38],lo:=4638,hi:=4639); |  |  | 319:UPS2Errors[22]:=Bit_0; |  |  |  | 4639:PMM[1].Phase[3].Current[38]:=Real_0;
mind_bool[320]:=UPS2Errors[23]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[39],lo:=4640,hi:=4641); |  |  | 320:UPS2Errors[23]:=Bit_0; |  |  |  | 4641:PMM[1].Phase[3].Current[39]:=Real_0;
mind_bool[321]:=UPS2Errors[24]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[3],lo:=4642,hi:=4643); |  |  | 321:UPS2Errors[24]:=Bit_0; |  |  |  | 4643:PMM[1].Phase[3].Current[3]:=Real_0;
mind_bool[322]:=UPS2Errors[25]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[40],lo:=4644,hi:=4645); |  |  | 322:UPS2Errors[25]:=Bit_0; |  |  |  | 4645:PMM[1].Phase[3].Current[40]:=Real_0;
mind_bool[323]:=UPS2Errors[2]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[41],lo:=4646,hi:=4647); |  |  | 323:UPS2Errors[2]:=Bit_0; |  |  |  | 4647:PMM[1].Phase[3].Current[41]:=Real_0;
mind_bool[324]:=UPS2Errors[3]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[42],lo:=4648,hi:=4649); |  |  | 324:UPS2Errors[3]:=Bit_0; |  |  |  | 4649:PMM[1].Phase[3].Current[42]:=Real_0;
mind_bool[325]:=UPS2Errors[4]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[4],lo:=4650,hi:=4651); |  |  | 325:UPS2Errors[4]:=Bit_0; |  |  |  | 4651:PMM[1].Phase[3].Current[4]:=Real_0;
mind_bool[326]:=UPS2Errors[5]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[5],lo:=4652,hi:=4653); |  |  | 326:UPS2Errors[5]:=Bit_0; |  |  |  | 4653:PMM[1].Phase[3].Current[5]:=Real_0;
mind_bool[327]:=UPS2Errors[6]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[6],lo:=4654,hi:=4655); |  |  | 327:UPS2Errors[6]:=Bit_0; |  |  |  | 4655:PMM[1].Phase[3].Current[6]:=Real_0;
mind_bool[328]:=UPS2Errors[7]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[7],lo:=4656,hi:=4657); |  |  | 328:UPS2Errors[7]:=Bit_0; |  |  |  | 4657:PMM[1].Phase[3].Current[7]:=Real_0;
mind_bool[329]:=UPS2Errors[8]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[8],lo:=4658,hi:=4659); |  |  | 329:UPS2Errors[8]:=Bit_0; |  |  |  | 4659:PMM[1].Phase[3].Current[8]:=Real_0;
mind_bool[330]:=UPS2Errors[9]; |  |  |  | Read_Real(rVar:=PMM[1].Phase[3].Current[9],lo:=4660,hi:=4661); |  |  | 330:UPS2Errors[9]:=Bit_0; |  |  |  | 4661:PMM[1].Phase[3].Current[9]:=Real_0;
mind_bool[331]:=UPS3Errors[10]; |  |  |  | Read_Real(rVar:=PMM[1].PowerFactorSys,lo:=4662,hi:=4663); |  |  | 331:UPS3Errors[10]:=Bit_0; |  |  |  | 4663:PMM[1].PowerFactorSys:=Real_0;
mind_bool[332]:=UPS3Errors[11]; |  |  |  | Read_Real(rVar:=PMM[1].ReactiveEnergyConsumed_kVARh,lo:=4664,hi:=4665); |  |  | 332:UPS3Errors[11]:=Bit_0; |  |  |  | 4665:PMM[1].ReactiveEnergyConsumed_kVARh:=Real_0;
mind_bool[333]:=UPS3Errors[12]; |  |  |  | Read_Real(rVar:=PMM[1].ReactivePowerPhaseA,lo:=4666,hi:=4667); |  |  | 333:UPS3Errors[12]:=Bit_0; |  |  |  | 4667:PMM[1].ReactivePowerPhaseA:=Real_0;
mind_bool[334]:=UPS3Errors[13]; |  |  |  | Read_Real(rVar:=PMM[1].ReactivePowerPhaseB,lo:=4668,hi:=4669); |  |  | 334:UPS3Errors[13]:=Bit_0; |  |  |  | 4669:PMM[1].ReactivePowerPhaseB:=Real_0;
mind_bool[335]:=UPS3Errors[14]; |  |  |  | Read_Real(rVar:=PMM[1].ReactivePowerPhaseC,lo:=4670,hi:=4671); |  |  | 335:UPS3Errors[14]:=Bit_0; |  |  |  | 4671:PMM[1].ReactivePowerPhaseC:=Real_0;
mind_bool[336]:=UPS3Errors[15]; |  |  |  | Read_Real(rVar:=PMM[1].TotalActivePower_kW,lo:=4672,hi:=4673); |  |  | 336:UPS3Errors[15]:=Bit_0; |  |  |  | 4673:PMM[1].TotalActivePower_kW:=Real_0;
mind_bool[337]:=UPS3Errors[16]; |  |  |  | Read_Real(rVar:=PMM[1].TotalAparentPower_kVA,lo:=4674,hi:=4675); |  |  | 337:UPS3Errors[16]:=Bit_0; |  |  |  | 4675:PMM[1].TotalAparentPower_kVA:=Real_0;
mind_bool[338]:=UPS3Errors[17]; |  |  |  | Read_Real(rVar:=PMM[1].TotalPowerFactor,lo:=4676,hi:=4677); |  |  | 338:UPS3Errors[17]:=Bit_0; |  |  |  | 4677:PMM[1].TotalPowerFactor:=Real_0;
mind_bool[339]:=UPS3Errors[18]; |  |  |  | Read_Real(rVar:=PMM[1].TotalReactivePower_kVAR,lo:=4678,hi:=4679); |  |  | 339:UPS3Errors[18]:=Bit_0; |  |  |  | 4679:PMM[1].TotalReactivePower_kVAR:=Real_0;
mind_bool[340]:=UPS3Errors[19]; |  |  |  | Read_Real(rVar:=PMM[1].VirA_fsys,lo:=4680,hi:=4681); |  |  | 340:UPS3Errors[19]:=Bit_0; |  |  |  | 4681:PMM[1].VirA_fsys:=Real_0;
mind_bool[341]:=UPS3Errors[1]; |  |  |  | Read_Real(rVar:=PMM[1].VirA_Isys,lo:=4682,hi:=4683); |  |  | 341:UPS3Errors[1]:=Bit_0; |  |  |  | 4683:PMM[1].VirA_Isys:=Real_0;
mind_bool[342]:=UPS3Errors[20]; |  |  |  | Read_Real(rVar:=PMM[1].VirA_PFsys,lo:=4684,hi:=4685); |  |  | 342:UPS3Errors[20]:=Bit_0; |  |  |  | 4685:PMM[1].VirA_PFsys:=Real_0;
mind_bool[343]:=UPS3Errors[21]; |  |  |  | Read_Real(rVar:=PMM[1].VirA_Psys,lo:=4686,hi:=4687); |  |  | 343:UPS3Errors[21]:=Bit_0; |  |  |  | 4687:PMM[1].VirA_Psys:=Real_0;
mind_bool[344]:=UPS3Errors[22]; |  |  |  | Read_Real(rVar:=PMM[1].VirA_Qsys,lo:=4688,hi:=4689); |  |  | 344:UPS3Errors[22]:=Bit_0; |  |  |  | 4689:PMM[1].VirA_Qsys:=Real_0;
mind_bool[345]:=UPS3Errors[23]; |  |  |  | Read_Real(rVar:=PMM[1].VirA_Ssys,lo:=4690,hi:=4691); |  |  | 345:UPS3Errors[23]:=Bit_0; |  |  |  | 4691:PMM[1].VirA_Ssys:=Real_0;
mind_bool[346]:=UPS3Errors[24]; |  |  |  | Read_Real(rVar:=PMM[1].VirA_Usys,lo:=4692,hi:=4693); |  |  | 346:UPS3Errors[24]:=Bit_0; |  |  |  | 4693:PMM[1].VirA_Usys:=Real_0;
mind_bool[347]:=UPS3Errors[25]; |  |  |  | Read_Real(rVar:=PMM[1].VirB_fsys,lo:=4694,hi:=4695); |  |  | 347:UPS3Errors[25]:=Bit_0; |  |  |  | 4695:PMM[1].VirB_fsys:=Real_0;
mind_bool[348]:=UPS3Errors[2]; |  |  |  | Read_Real(rVar:=PMM[1].VirB_Isys,lo:=4696,hi:=4697); |  |  | 348:UPS3Errors[2]:=Bit_0; |  |  |  | 4697:PMM[1].VirB_Isys:=Real_0;
mind_bool[349]:=UPS3Errors[3]; |  |  |  | Read_Real(rVar:=PMM[1].VirB_PFsys,lo:=4698,hi:=4699); |  |  | 349:UPS3Errors[3]:=Bit_0; |  |  |  | 4699:PMM[1].VirB_PFsys:=Real_0;
mind_bool[350]:=UPS3Errors[4]; |  |  |  | Read_Real(rVar:=PMM[1].VirB_Psys,lo:=4700,hi:=4701); |  |  | 350:UPS3Errors[4]:=Bit_0; |  |  |  | 4701:PMM[1].VirB_Psys:=Real_0;
mind_bool[351]:=UPS3Errors[5]; |  |  |  | Read_Real(rVar:=PMM[1].VirB_Qsys,lo:=4702,hi:=4703); |  |  | 351:UPS3Errors[5]:=Bit_0; |  |  |  | 4703:PMM[1].VirB_Qsys:=Real_0;
mind_bool[352]:=UPS3Errors[6]; |  |  |  | Read_Real(rVar:=PMM[1].VirB_Ssys,lo:=4704,hi:=4705); |  |  | 352:UPS3Errors[6]:=Bit_0; |  |  |  | 4705:PMM[1].VirB_Ssys:=Real_0;
mind_bool[353]:=UPS3Errors[7]; |  |  |  | Read_Real(rVar:=PMM[1].VirB_Usys,lo:=4706,hi:=4707); |  |  | 353:UPS3Errors[7]:=Bit_0; |  |  |  | 4707:PMM[1].VirB_Usys:=Real_0;
mind_bool[354]:=UPS3Errors[8]; |  |  |  | Read_Real(rVar:=PMM[1].VirBActiveEnergyConsumed_kWh,lo:=4708,hi:=4709); |  |  | 354:UPS3Errors[8]:=Bit_0; |  |  |  | 4709:PMM[1].VirBActiveEnergyConsumed_kWh:=Real_0;
mind_bool[355]:=UPS3Errors[9]; |  |  |  | Read_Real(rVar:=PMM[1].VirBActivePowerPhaseA_kW,lo:=4710,hi:=4711); |  |  | 355:UPS3Errors[9]:=Bit_0; |  |  |  | 4711:PMM[1].VirBActivePowerPhaseA_kW:=Real_0;
mind_bool[356]:=UPS[1].AlarmAwaitingPower; |  |  |  | Read_Real(rVar:=PMM[1].VirBActivePowerPhaseB_kW,lo:=4712,hi:=4713); |  |  | 356:UPS[1].AlarmAwaitingPower:=Bit_0; |  |  |  | 4713:PMM[1].VirBActivePowerPhaseB_kW:=Real_0;
mind_bool[357]:=UPS[1].AlarmBypassBad; |  |  |  | Read_Real(rVar:=PMM[1].VirBActivePowerPhaseC_kW,lo:=4714,hi:=4715); |  |  | 357:UPS[1].AlarmBypassBad:=Bit_0; |  |  |  | 4715:PMM[1].VirBActivePowerPhaseC_kW:=Real_0;
mind_bool[358]:=UPS[1].AlarmChargerFailed; |  |  |  | Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseA,lo:=4716,hi:=4717); |  |  | 358:UPS[1].AlarmChargerFailed:=Bit_0; |  |  |  | 4717:PMM[1].VirBAparentPowerPhaseA:=Real_0;
mind_bool[359]:=UPS[1].AlarmCommunicationsLost; |  |  |  | Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseB,lo:=4718,hi:=4719); |  |  | 359:UPS[1].AlarmCommunicationsLost:=Bit_0; |  |  |  | 4719:PMM[1].VirBAparentPowerPhaseB:=Real_0;
mind_bool[360]:=UPS[1].AlarmDepletedBattery; |  |  |  | Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseC,lo:=4720,hi:=4721); |  |  | 360:UPS[1].AlarmDepletedBattery:=Bit_0; |  |  |  | 4721:PMM[1].VirBAparentPowerPhaseC:=Real_0;
mind_bool[361]:=UPS[1].AlarmDiagnosticTestFailed; |  |  |  | Read_Real(rVar:=PMM[1].VirBAverageCurrent_A,lo:=4722,hi:=4723); |  |  | 361:UPS[1].AlarmDiagnosticTestFailed:=Bit_0; |  |  |  | 4723:PMM[1].VirBAverageCurrent_A:=Real_0;
mind_bool[362]:=UPS[1].AlarmInverterError; |  |  |  | Read_Real(rVar:=PMM[1].VirBAveragePhaseToNeutral_V,lo:=4724,hi:=4725); |  |  | 362:UPS[1].AlarmInverterError:=Bit_0; |  |  |  | 4725:PMM[1].VirBAveragePhaseToNeutral_V:=Real_0;
mind_bool[363]:=UPS[1].AlarmIzhodOffKotZahtevano; |  |  |  | Read_Real(rVar:=PMM[1].VirBAveragePhaseToPhase_V,lo:=4726,hi:=4727); |  |  | 363:UPS[1].AlarmIzhodOffKotZahtevano:=Bit_0; |  |  |  | 4727:PMM[1].VirBAveragePhaseToPhase_V:=Real_0;
mind_bool[364]:=UPS[1].AlarmIzhodPreobremenjen; |  |  |  | Read_Real(rVar:=PMM[1].VirBCurrentInPhaseA_A,lo:=4728,hi:=4729); |  |  | 364:UPS[1].AlarmIzhodPreobremenjen:=Bit_0; |  |  |  | 4729:PMM[1].VirBCurrentInPhaseA_A:=Real_0;
mind_bool[365]:=UPS[1].AlarmLowBattery; |  |  |  | Read_Real(rVar:=PMM[1].VirBCurrentInPhaseB_A,lo:=4730,hi:=4731); |  |  | 365:UPS[1].AlarmLowBattery:=Bit_0; |  |  |  | 4731:PMM[1].VirBCurrentInPhaseB_A:=Real_0;
mind_bool[366]:=UPS[1].AlarmNapakaNaVarovalki; |  |  |  | Read_Real(rVar:=PMM[1].VirBCurrentInPhaseC_A,lo:=4732,hi:=4733); |  |  | 366:UPS[1].AlarmNapakaNaVarovalki:=Bit_0; |  |  |  | 4733:PMM[1].VirBCurrentInPhaseC_A:=Real_0;
mind_bool[367]:=UPS[1].AlarmNapakaNaVentilatorju; |  |  |  | Read_Real(rVar:=PMM[1].VirBFrequency_Hz,lo:=4734,hi:=4735); |  |  | 367:UPS[1].AlarmNapakaNaVentilatorju:=Bit_0; |  |  |  | 4735:PMM[1].VirBFrequency_Hz:=Real_0;
mind_bool[368]:=UPS[1].AlarmOnBattery; |  |  |  | Read_Real(rVar:=PMM[1].VirBPowerFactorSys,lo:=4736,hi:=4737); |  |  | 368:UPS[1].AlarmOnBattery:=Bit_0; |  |  |  | 4737:PMM[1].VirBPowerFactorSys:=Real_0;
mind_bool[369]:=UPS[1].AlarmOnBypass; |  |  |  | Read_Real(rVar:=PMM[1].VirBReactiveEnergyConsumed_kVARh,lo:=4738,hi:=4739); |  |  | 369:UPS[1].AlarmOnBypass:=Bit_0; |  |  |  | 4739:PMM[1].VirBReactiveEnergyConsumed_kVARh:=Real_0;
mind_bool[370]:=UPS[1].AlarmShutdownImminent; |  |  |  | Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseA,lo:=4740,hi:=4741); |  |  | 370:UPS[1].AlarmShutdownImminent:=Bit_0; |  |  |  | 4741:PMM[1].VirBReactivePowerPhaseA:=Real_0;
mind_bool[371]:=UPS[1].AlarmShutdownPending; |  |  |  | Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseB,lo:=4742,hi:=4743); |  |  | 371:UPS[1].AlarmShutdownPending:=Bit_0; |  |  |  | 4743:PMM[1].VirBReactivePowerPhaseB:=Real_0;
mind_bool[372]:=UPS[1].AlarmSlabaBaterija; |  |  |  | Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseC,lo:=4744,hi:=4745); |  |  | 372:UPS[1].AlarmSlabaBaterija:=Bit_0; |  |  |  | 4745:PMM[1].VirBReactivePowerPhaseC:=Real_0;
mind_bool[373]:=UPS[1].AlarmSplosnaNapaka; |  |  |  | Read_Real(rVar:=PMM[1].VirBTotalActivePower_kW,lo:=4746,hi:=4747); |  |  | 373:UPS[1].AlarmSplosnaNapaka:=Bit_0; |  |  |  | 4747:PMM[1].VirBTotalActivePower_kW:=Real_0;
mind_bool[374]:=UPS[1].AlarmStanjeIzhodaIzvenToleranc; |  |  |  | Read_Real(rVar:=PMM[1].VirBTotalAparentPower_kVA,lo:=4748,hi:=4749); |  |  | 374:UPS[1].AlarmStanjeIzhodaIzvenToleranc:=Bit_0; |  |  |  | 4749:PMM[1].VirBTotalAparentPower_kVA:=Real_0;
mind_bool[375]:=UPS[1].AlarmStanjeVhodaIzvenToleranc; |  |  |  | Read_Real(rVar:=PMM[1].VirBTotalPowerFactor,lo:=4750,hi:=4751); |  |  | 375:UPS[1].AlarmStanjeVhodaIzvenToleranc:=Bit_0; |  |  |  | 4751:PMM[1].VirBTotalPowerFactor:=Real_0;
mind_bool[376]:=UPS[1].AlarmTemperaturaIzvenToleranc; |  |  |  | Read_Real(rVar:=PMM[1].VirBTotalReactivePower_kVAR,lo:=4752,hi:=4753); |  |  | 376:UPS[1].AlarmTemperaturaIzvenToleranc:=Bit_0; |  |  |  | 4753:PMM[1].VirBTotalReactivePower_kVAR:=Real_0;
mind_bool[377]:=UPS[1].AlarmTestInProgres; |  |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseAB_V,lo:=4754,hi:=4755); |  |  | 377:UPS[1].AlarmTestInProgres:=Bit_0; |  |  |  | 4755:PMM[1].VirBVoltageBetweenPhaseAB_V:=Real_0;
mind_bool[378]:=UPS[1].AlarmUPSIzhodOff; |  |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseAN_V,lo:=4756,hi:=4757); |  |  | 378:UPS[1].AlarmUPSIzhodOff:=Bit_0; |  |  |  | 4757:PMM[1].VirBVoltageBetweenPhaseAN_V:=Real_0;
mind_bool[379]:=UPS[1].AlarmUPSOffKotZahtevano; |  |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseBC_V,lo:=4758,hi:=4759); |  |  | 379:UPS[1].AlarmUPSOffKotZahtevano:=Bit_0; |  |  |  | 4759:PMM[1].VirBVoltageBetweenPhaseBC_V:=Real_0;
mind_bool[380]:=UPS[1].AlarmUPSSystemOff; |  |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseBN_V,lo:=4760,hi:=4761); |  |  | 380:UPS[1].AlarmUPSSystemOff:=Bit_0; |  |  |  | 4761:PMM[1].VirBVoltageBetweenPhaseBN_V:=Real_0;
mind_bool[381]:=UPS[1].Napaka; |  |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseCA_V,lo:=4762,hi:=4763); |  |  | 381:UPS[1].Napaka:=Bit_0; |  |  |  | 4763:PMM[1].VirBVoltageBetweenPhaseCA_V:=Real_0;
mind_bool[382]:=UPS[1].StatusEcomodeAktiven; |  |  |  | Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseCN_V,lo:=4764,hi:=4765); |  |  | 382:UPS[1].StatusEcomodeAktiven:=Bit_0; |  |  |  | 4765:PMM[1].VirBVoltageBetweenPhaseCN_V:=Real_0;
mind_bool[383]:=UPS[1].StatusInverterIsOn; |  |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseAB_V,lo:=4766,hi:=4767); |  |  | 383:UPS[1].StatusInverterIsOn:=Bit_0; |  |  |  | 4767:PMM[1].VoltageBetweenPhaseAB_V:=Real_0;
mind_bool[384]:=UPS[1].StatusStopOperation; |  |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseAN_V,lo:=4768,hi:=4769); |  |  | 384:UPS[1].StatusStopOperation:=Bit_0; |  |  |  | 4769:PMM[1].VoltageBetweenPhaseAN_V:=Real_0;
mind_bool[385]:=UPS[2].AlarmAwaitingPower; |  |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseBC_V,lo:=4770,hi:=4771); |  |  | 385:UPS[2].AlarmAwaitingPower:=Bit_0; |  |  |  | 4771:PMM[1].VoltageBetweenPhaseBC_V:=Real_0;
mind_bool[386]:=UPS[2].AlarmBypassBad; |  |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseBN_V,lo:=4772,hi:=4773); |  |  | 386:UPS[2].AlarmBypassBad:=Bit_0; |  |  |  | 4773:PMM[1].VoltageBetweenPhaseBN_V:=Real_0;
mind_bool[387]:=UPS[2].AlarmChargerFailed; |  |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseCA_V,lo:=4774,hi:=4775); |  |  | 387:UPS[2].AlarmChargerFailed:=Bit_0; |  |  |  | 4775:PMM[1].VoltageBetweenPhaseCA_V:=Real_0;
mind_bool[388]:=UPS[2].AlarmCommunicationsLost; |  |  |  | Read_Real(rVar:=PMM[1].VoltageBetweenPhaseCN_V,lo:=4776,hi:=4777); |  |  | 388:UPS[2].AlarmCommunicationsLost:=Bit_0; |  |  |  | 4777:PMM[1].VoltageBetweenPhaseCN_V:=Real_0;
mind_bool[389]:=UPS[2].AlarmDepletedBattery; |  |  |  | Read_Real(rVar:=PMMfaza01,lo:=4778,hi:=4779); |  |  | 389:UPS[2].AlarmDepletedBattery:=Bit_0; |  |  |  | 4779:PMMfaza01:=Real_0;
mind_bool[390]:=UPS[2].AlarmDiagnosticTestFailed; |  |  |  | Read_Real(rVar:=PMMfaza02,lo:=4780,hi:=4781); |  |  | 390:UPS[2].AlarmDiagnosticTestFailed:=Bit_0; |  |  |  | 4781:PMMfaza02:=Real_0;
mind_bool[391]:=UPS[2].AlarmInverterError; |  |  |  | Read_Real(rVar:=PMMfaza03,lo:=4782,hi:=4783); |  |  | 391:UPS[2].AlarmInverterError:=Bit_0; |  |  |  | 4783:PMMfaza03:=Real_0;
mind_bool[392]:=UPS[2].AlarmIzhodOffKotZahtevano; |  |  |  | Read_Real(rVar:=PMMfaza04,lo:=4784,hi:=4785); |  |  | 392:UPS[2].AlarmIzhodOffKotZahtevano:=Bit_0; |  |  |  | 4785:PMMfaza04:=Real_0;
mind_bool[393]:=UPS[2].AlarmIzhodPreobremenjen; |  |  |  | Read_Real(rVar:=PMMfaza05,lo:=4786,hi:=4787); |  |  | 393:UPS[2].AlarmIzhodPreobremenjen:=Bit_0; |  |  |  | 4787:PMMfaza05:=Real_0;
mind_bool[394]:=UPS[2].AlarmLowBattery; |  |  |  | Read_Real(rVar:=PMMfaza06,lo:=4788,hi:=4789); |  |  | 394:UPS[2].AlarmLowBattery:=Bit_0; |  |  |  | 4789:PMMfaza06:=Real_0;
mind_bool[395]:=UPS[2].AlarmNapakaNaVarovalki; |  |  |  | Read_Real(rVar:=PMMfaza07,lo:=4790,hi:=4791); |  |  | 395:UPS[2].AlarmNapakaNaVarovalki:=Bit_0; |  |  |  | 4791:PMMfaza07:=Real_0;
mind_bool[396]:=UPS[2].AlarmNapakaNaVentilatorju; |  |  |  | Read_Real(rVar:=PMMfaza08,lo:=4792,hi:=4793); |  |  | 396:UPS[2].AlarmNapakaNaVentilatorju:=Bit_0; |  |  |  | 4793:PMMfaza08:=Real_0;
mind_bool[397]:=UPS[2].AlarmOnBattery; |  |  |  | Read_Real(rVar:=PMMfaza09,lo:=4794,hi:=4795); |  |  | 397:UPS[2].AlarmOnBattery:=Bit_0; |  |  |  | 4795:PMMfaza09:=Real_0;
mind_bool[398]:=UPS[2].AlarmOnBypass; |  |  |  | Read_Real(rVar:=PMMfaza10,lo:=4796,hi:=4797); |  |  | 398:UPS[2].AlarmOnBypass:=Bit_0; |  |  |  | 4797:PMMfaza10:=Real_0;
mind_bool[399]:=UPS[2].AlarmShutdownImminent; |  |  |  | Read_Real(rVar:=PMMfaza11,lo:=4798,hi:=4799); |  |  | 399:UPS[2].AlarmShutdownImminent:=Bit_0; |  |  |  | 4799:PMMfaza11:=Real_0;
mind_bool[400]:=UPS[2].AlarmShutdownPending; |  |  |  | Read_Real(rVar:=PMMfaza12,lo:=4800,hi:=4801); |  |  | 400:UPS[2].AlarmShutdownPending:=Bit_0; |  |  |  | 4801:PMMfaza12:=Real_0;
mind_bool[401]:=UPS[2].AlarmSlabaBaterija; |  |  |  | Read_Real(rVar:=PMMfaza13,lo:=4802,hi:=4803); |  |  | 401:UPS[2].AlarmSlabaBaterija:=Bit_0; |  |  |  | 4803:PMMfaza13:=Real_0;
mind_bool[402]:=UPS[2].AlarmSplosnaNapaka; |  |  |  | Read_Real(rVar:=PMMfaza14,lo:=4804,hi:=4805); |  |  | 402:UPS[2].AlarmSplosnaNapaka:=Bit_0; |  |  |  | 4805:PMMfaza14:=Real_0;
mind_bool[403]:=UPS[2].AlarmStanjeIzhodaIzvenToleranc; |  |  |  | Read_Real(rVar:=PMMfaza15,lo:=4806,hi:=4807); |  |  | 403:UPS[2].AlarmStanjeIzhodaIzvenToleranc:=Bit_0; |  |  |  | 4807:PMMfaza15:=Real_0;
mind_bool[404]:=UPS[2].AlarmStanjeVhodaIzvenToleranc; |  |  |  | Read_Real(rVar:=PMMfaza16,lo:=4808,hi:=4809); |  |  | 404:UPS[2].AlarmStanjeVhodaIzvenToleranc:=Bit_0; |  |  |  | 4809:PMMfaza16:=Real_0;
mind_bool[405]:=UPS[2].AlarmTemperaturaIzvenToleranc; |  |  |  | Read_Real(rVar:=PMMfaza17,lo:=4810,hi:=4811); |  |  | 405:UPS[2].AlarmTemperaturaIzvenToleranc:=Bit_0; |  |  |  | 4811:PMMfaza17:=Real_0;
mind_bool[406]:=UPS[2].AlarmTestInProgres; |  |  |  | Read_Real(rVar:=PMMfaza18,lo:=4812,hi:=4813); |  |  | 406:UPS[2].AlarmTestInProgres:=Bit_0; |  |  |  | 4813:PMMfaza18:=Real_0;
mind_bool[407]:=UPS[2].AlarmUPSIzhodOff; |  |  |  | Read_Real(rVar:=PMMfaza19,lo:=4814,hi:=4815); |  |  | 407:UPS[2].AlarmUPSIzhodOff:=Bit_0; |  |  |  | 4815:PMMfaza19:=Real_0;
mind_bool[408]:=UPS[2].AlarmUPSOffKotZahtevano; |  |  |  | Read_Real(rVar:=PMMfaza20,lo:=4816,hi:=4817); |  |  | 408:UPS[2].AlarmUPSOffKotZahtevano:=Bit_0; |  |  |  | 4817:PMMfaza20:=Real_0;
mind_bool[409]:=UPS[2].AlarmUPSSystemOff; |  |  |  | Read_Real(rVar:=PMMfaza21,lo:=4818,hi:=4819); |  |  | 409:UPS[2].AlarmUPSSystemOff:=Bit_0; |  |  |  | 4819:PMMfaza21:=Real_0;
mind_bool[410]:=UPS[2].Napaka; |  |  |  | Read_Real(rVar:=PMMfaza22,lo:=4820,hi:=4821); |  |  | 410:UPS[2].Napaka:=Bit_0; |  |  |  | 4821:PMMfaza22:=Real_0;
mind_bool[411]:=UPS[2].StatusEcomodeAktiven; |  |  |  | Read_Real(rVar:=PMMfaza23,lo:=4822,hi:=4823); |  |  | 411:UPS[2].StatusEcomodeAktiven:=Bit_0; |  |  |  | 4823:PMMfaza23:=Real_0;
mind_bool[412]:=UPS[2].StatusInverterIsOn; |  |  |  | Read_Real(rVar:=PMMfaza24,lo:=4824,hi:=4825); |  |  | 412:UPS[2].StatusInverterIsOn:=Bit_0; |  |  |  | 4825:PMMfaza24:=Real_0;
mind_bool[413]:=UPS[2].StatusStopOperation; |  |  |  | Read_Real(rVar:=PMMfaza25,lo:=4826,hi:=4827); |  |  | 413:UPS[2].StatusStopOperation:=Bit_0; |  |  |  | 4827:PMMfaza25:=Real_0;
mind_bool[414]:=UPS[3].AlarmAwaitingPower; |  |  |  | Read_Real(rVar:=PMMfaza26,lo:=4828,hi:=4829); |  |  | 414:UPS[3].AlarmAwaitingPower:=Bit_0; |  |  |  | 4829:PMMfaza26:=Real_0;
mind_bool[415]:=UPS[3].AlarmBypassBad; |  |  |  | Read_Real(rVar:=PMMfaza27,lo:=4830,hi:=4831); |  |  | 415:UPS[3].AlarmBypassBad:=Bit_0; |  |  |  | 4831:PMMfaza27:=Real_0;
mind_bool[416]:=UPS[3].AlarmChargerFailed; |  |  |  | Read_Real(rVar:=PMMfaza28,lo:=4832,hi:=4833); |  |  | 416:UPS[3].AlarmChargerFailed:=Bit_0; |  |  |  | 4833:PMMfaza28:=Real_0;
mind_bool[417]:=UPS[3].AlarmCommunicationsLost; |  |  |  | Read_Real(rVar:=PMMfaza29,lo:=4834,hi:=4835); |  |  | 417:UPS[3].AlarmCommunicationsLost:=Bit_0; |  |  |  | 4835:PMMfaza29:=Real_0;
mind_bool[418]:=UPS[3].AlarmDepletedBattery; |  |  |  | Read_Real(rVar:=PMMfaza30,lo:=4836,hi:=4837); |  |  | 418:UPS[3].AlarmDepletedBattery:=Bit_0; |  |  |  | 4837:PMMfaza30:=Real_0;
mind_bool[419]:=UPS[3].AlarmDiagnosticTestFailed; |  |  |  | Read_Real(rVar:=PMMfaza31,lo:=4838,hi:=4839); |  |  | 419:UPS[3].AlarmDiagnosticTestFailed:=Bit_0; |  |  |  | 4839:PMMfaza31:=Real_0;
mind_bool[420]:=UPS[3].AlarmInverterError; |  |  |  | Read_Real(rVar:=PMMfaza32,lo:=4840,hi:=4841); |  |  | 420:UPS[3].AlarmInverterError:=Bit_0; |  |  |  | 4841:PMMfaza32:=Real_0;
mind_bool[421]:=UPS[3].AlarmIzhodOffKotZahtevano; |  |  |  | Read_Real(rVar:=PMMfaza33,lo:=4842,hi:=4843); |  |  | 421:UPS[3].AlarmIzhodOffKotZahtevano:=Bit_0; |  |  |  | 4843:PMMfaza33:=Real_0;
mind_bool[422]:=UPS[3].AlarmIzhodPreobremenjen; |  |  |  | Read_Real(rVar:=PMMfaza34,lo:=4844,hi:=4845); |  |  | 422:UPS[3].AlarmIzhodPreobremenjen:=Bit_0; |  |  |  | 4845:PMMfaza34:=Real_0;
mind_bool[423]:=UPS[3].AlarmLowBattery; |  |  |  | Read_Real(rVar:=PMMfaza35,lo:=4846,hi:=4847); |  |  | 423:UPS[3].AlarmLowBattery:=Bit_0; |  |  |  | 4847:PMMfaza35:=Real_0;
mind_bool[424]:=UPS[3].AlarmNapakaNaVarovalki; |  |  |  | Read_Real(rVar:=PMMfaza36,lo:=4848,hi:=4849); |  |  | 424:UPS[3].AlarmNapakaNaVarovalki:=Bit_0; |  |  |  | 4849:PMMfaza36:=Real_0;
mind_bool[425]:=UPS[3].AlarmNapakaNaVentilatorju; |  |  |  | Read_Real(rVar:=PMMfaza37,lo:=4850,hi:=4851); |  |  | 425:UPS[3].AlarmNapakaNaVentilatorju:=Bit_0; |  |  |  | 4851:PMMfaza37:=Real_0;
mind_bool[426]:=UPS[3].AlarmOnBattery; |  |  |  | Read_Real(rVar:=PMMfaza38,lo:=4852,hi:=4853); |  |  | 426:UPS[3].AlarmOnBattery:=Bit_0; |  |  |  | 4853:PMMfaza38:=Real_0;
mind_bool[427]:=UPS[3].AlarmOnBypass; |  |  |  | Read_Real(rVar:=PMMfaza39,lo:=4854,hi:=4855); |  |  | 427:UPS[3].AlarmOnBypass:=Bit_0; |  |  |  | 4855:PMMfaza39:=Real_0;
mind_bool[428]:=UPS[3].AlarmShutdownImminent; |  |  |  | Read_Real(rVar:=PMMfaza40,lo:=4856,hi:=4857); |  |  | 428:UPS[3].AlarmShutdownImminent:=Bit_0; |  |  |  | 4857:PMMfaza40:=Real_0;
mind_bool[429]:=UPS[3].AlarmShutdownPending; |  |  |  | Read_Real(rVar:=PMMfaza41,lo:=4858,hi:=4859); |  |  | 429:UPS[3].AlarmShutdownPending:=Bit_0; |  |  |  | 4859:PMMfaza41:=Real_0;
mind_bool[430]:=UPS[3].AlarmSlabaBaterija; |  |  |  | Read_Real(rVar:=PMMfaza42,lo:=4860,hi:=4861); |  |  | 430:UPS[3].AlarmSlabaBaterija:=Bit_0; |  |  |  | 4861:PMMfaza42:=Real_0;
mind_bool[431]:=UPS[3].AlarmSplosnaNapaka; |  |  |  | Read_Real(rVar:=PMMskupniTokA,lo:=4862,hi:=4863); |  |  | 431:UPS[3].AlarmSplosnaNapaka:=Bit_0; |  |  |  | 4863:PMMskupniTokA:=Real_0;
mind_bool[432]:=UPS[3].AlarmStanjeIzhodaIzvenToleranc; |  |  |  | Read_Real(rVar:=PMMskupniTokB,lo:=4864,hi:=4865); |  |  | 432:UPS[3].AlarmStanjeIzhodaIzvenToleranc:=Bit_0; |  |  |  | 4865:PMMskupniTokB:=Real_0;
mind_bool[433]:=UPS[3].AlarmStanjeVhodaIzvenToleranc; |  |  |  | Read_Real(rVar:=UPS[1].EstimatedChargeRemaining,lo:=4866,hi:=4867); |  |  | 433:UPS[3].AlarmStanjeVhodaIzvenToleranc:=Bit_0; |  |  |  | 4867:UPS[1].EstimatedChargeRemaining:=Real_0;
mind_bool[434]:=UPS[3].AlarmTemperaturaIzvenToleranc; |  |  |  | Read_Real(rVar:=UPS[1].EstimatedMinutesRemaining,lo:=4868,hi:=4869); |  |  | 434:UPS[3].AlarmTemperaturaIzvenToleranc:=Bit_0; |  |  |  | 4869:UPS[1].EstimatedMinutesRemaining:=Real_0;
mind_bool[435]:=UPS[3].AlarmTestInProgres; |  |  |  | Read_Real(rVar:=UPS[1].IzhodMocL1,lo:=4870,hi:=4871); |  |  | 435:UPS[3].AlarmTestInProgres:=Bit_0; |  |  |  | 4871:UPS[1].IzhodMocL1:=Real_0;
mind_bool[436]:=UPS[3].AlarmUPSIzhodOff; |  |  |  | Read_Real(rVar:=UPS[1].IzhodMocL2,lo:=4872,hi:=4873); |  |  | 436:UPS[3].AlarmUPSIzhodOff:=Bit_0; |  |  |  | 4873:UPS[1].IzhodMocL2:=Real_0;
mind_bool[437]:=UPS[3].AlarmUPSOffKotZahtevano; |  |  |  | Read_Real(rVar:=UPS[1].IzhodMocL3,lo:=4874,hi:=4875); |  |  | 437:UPS[3].AlarmUPSOffKotZahtevano:=Bit_0; |  |  |  | 4875:UPS[1].IzhodMocL3:=Real_0;
mind_bool[438]:=UPS[3].AlarmUPSSystemOff; |  |  |  | Read_Real(rVar:=UPS[1].NapetostBaterije,lo:=4876,hi:=4877); |  |  | 438:UPS[3].AlarmUPSSystemOff:=Bit_0; |  |  |  | 4877:UPS[1].NapetostBaterije:=Real_0;
mind_bool[439]:=UPS[3].Napaka; |  |  |  | Read_Real(rVar:=UPS[1].TemperaturaBaterije,lo:=4878,hi:=4879); |  |  | 439:UPS[3].Napaka:=Bit_0; |  |  |  | 4879:UPS[1].TemperaturaBaterije:=Real_0;
mind_bool[440]:=UPS[3].StatusEcomodeAktiven; |  |  |  | Read_Real(rVar:=UPS[1].VhodFrekvencaL1,lo:=4880,hi:=4881); |  |  | 440:UPS[3].StatusEcomodeAktiven:=Bit_0; |  |  |  | 4881:UPS[1].VhodFrekvencaL1:=Real_0;
mind_bool[441]:=UPS[3].StatusInverterIsOn; |  |  |  | Read_Real(rVar:=UPS[1].VhodFrekvencaL2,lo:=4882,hi:=4883); |  |  | 441:UPS[3].StatusInverterIsOn:=Bit_0; |  |  |  | 4883:UPS[1].VhodFrekvencaL2:=Real_0;
mind_bool[442]:=UPS[3].StatusStopOperation; |  |  |  | Read_Real(rVar:=UPS[1].VhodFrekvencaL3,lo:=4884,hi:=4885); |  |  | 442:UPS[3].StatusStopOperation:=Bit_0; |  |  |  | 4885:UPS[1].VhodFrekvencaL3:=Real_0;
mind_bool[443]:=UPS_A_V23_delovanje; |  |  |  | Read_Real(rVar:=UPS[1].VhodNapetostL1,lo:=4886,hi:=4887); |  |  | 443:UPS_A_V23_delovanje:=Bit_0; |  |  |  | 4887:UPS[1].VhodNapetostL1:=Real_0;
mind_bool[444]:=UPS_A_V23_napaka; |  |  |  | Read_Real(rVar:=UPS[1].VhodNapetostL2,lo:=4888,hi:=4889); |  |  | 444:UPS_A_V23_napaka:=Bit_0; |  |  |  | 4889:UPS[1].VhodNapetostL2:=Real_0;
mind_bool[445]:=ups_alarm; |  |  |  | Read_Real(rVar:=UPS[1].VhodNapetostL3,lo:=4890,hi:=4891); |  |  | 445:ups_alarm:=Bit_0; |  |  |  | 4891:UPS[1].VhodNapetostL3:=Real_0;
mind_bool[446]:=ups_baterijski_nac; |  |  |  | Read_Real(rVar:=UPS[2].EstimatedChargeRemaining,lo:=4892,hi:=4893); |  |  | 446:ups_baterijski_nac:=Bit_0; |  |  |  | 4893:UPS[2].EstimatedChargeRemaining:=Real_0;
mind_bool[447]:=UPS_MGE[1].BatteryChargedState; |  |  |  | Read_Real(rVar:=UPS[2].EstimatedMinutesRemaining,lo:=4894,hi:=4895); |  |  | 447:UPS_MGE[1].BatteryChargedState:=Bit_0; |  |  |  | 4895:UPS[2].EstimatedMinutesRemaining:=Real_0;
mind_bool[448]:=UPS_MGE[1].BatteryCircuitBreaker; |  |  |  | Read_Real(rVar:=UPS[2].IzhodMocL1,lo:=4896,hi:=4897); |  |  | 448:UPS_MGE[1].BatteryCircuitBreaker:=Bit_0; |  |  |  | 4897:UPS[2].IzhodMocL1:=Real_0;
mind_bool[449]:=UPS_MGE[1].BatteryCompInProgress; |  |  |  | Read_Real(rVar:=UPS[2].IzhodMocL2,lo:=4898,hi:=4899); |  |  | 449:UPS_MGE[1].BatteryCompInProgress:=Bit_0; |  |  |  | 4899:UPS[2].IzhodMocL2:=Real_0;
mind_bool[450]:=UPS_MGE[1].BatteryFuseFault; |  |  |  | Read_Real(rVar:=UPS[2].IzhodMocL3,lo:=4900,hi:=4901); |  |  | 450:UPS_MGE[1].BatteryFuseFault:=Bit_0; |  |  |  | 4901:UPS[2].IzhodMocL3:=Real_0;
mind_bool[451]:=UPS_MGE[1].BatteryLowWarning; |  |  |  | Read_Real(rVar:=UPS[2].NapetostBaterije,lo:=4902,hi:=4903); |  |  | 451:UPS_MGE[1].BatteryLowWarning:=Bit_0; |  |  |  | 4903:UPS[2].NapetostBaterije:=Real_0;
mind_bool[452]:=UPS_MGE[1].BatteryTempOutOfToler; |  |  |  | Read_Real(rVar:=UPS[2].TemperaturaBaterije,lo:=4904,hi:=4905); |  |  | 452:UPS_MGE[1].BatteryTempOutOfToler:=Bit_0; |  |  |  | 4905:UPS[2].TemperaturaBaterije:=Real_0;
mind_bool[453]:=UPS_MGE[1].BypassInFreeFrequency; |  |  |  | Read_Real(rVar:=UPS[2].VhodFrekvencaL1,lo:=4906,hi:=4907); |  |  | 453:UPS_MGE[1].BypassInFreeFrequency:=Bit_0; |  |  |  | 4907:UPS[2].VhodFrekvencaL1:=Real_0;
mind_bool[454]:=UPS_MGE[1].ChargerGeneralFault; |  |  |  | Read_Real(rVar:=UPS[2].VhodFrekvencaL2,lo:=4908,hi:=4909); |  |  | 454:UPS_MGE[1].ChargerGeneralFault:=Bit_0; |  |  |  | 4909:UPS[2].VhodFrekvencaL2:=Real_0;
mind_bool[455]:=UPS_MGE[1].DeviceVentilationFault; |  |  |  | Read_Real(rVar:=UPS[2].VhodFrekvencaL3,lo:=4910,hi:=4911); |  |  | 455:UPS_MGE[1].DeviceVentilationFault:=Bit_0; |  |  |  | 4911:UPS[2].VhodFrekvencaL3:=Real_0;
mind_bool[456]:=UPS_MGE[1].InverterFuseFault; |  |  |  | Read_Real(rVar:=UPS[2].VhodNapetostL1,lo:=4912,hi:=4913); |  |  | 456:UPS_MGE[1].InverterFuseFault:=Bit_0; |  |  |  | 4913:UPS[2].VhodNapetostL1:=Real_0;
mind_bool[457]:=UPS_MGE[1].InverterOverload; |  |  |  | Read_Real(rVar:=UPS[2].VhodNapetostL2,lo:=4914,hi:=4915); |  |  | 457:UPS_MGE[1].InverterOverload:=Bit_0; |  |  |  | 4915:UPS[2].VhodNapetostL2:=Real_0;
mind_bool[458]:=UPS_MGE[1].InverterThermalOverload; |  |  |  | Read_Real(rVar:=UPS[2].VhodNapetostL3,lo:=4916,hi:=4917); |  |  | 458:UPS_MGE[1].InverterThermalOverload:=Bit_0; |  |  |  | 4917:UPS[2].VhodNapetostL3:=Real_0;
mind_bool[459]:=UPS_MGE[1].Mains1VoltOutOfToler; |  |  |  | Read_Real(rVar:=UPS[3].EstimatedChargeRemaining,lo:=4918,hi:=4919); |  |  | 459:UPS_MGE[1].Mains1VoltOutOfToler:=Bit_0; |  |  |  | 4919:UPS[3].EstimatedChargeRemaining:=Real_0;
mind_bool[460]:=UPS_MGE[1].Mains2Overload; |  |  |  | Read_Real(rVar:=UPS[3].EstimatedMinutesRemaining,lo:=4920,hi:=4921); |  |  | 460:UPS_MGE[1].Mains2Overload:=Bit_0; |  |  |  | 4921:UPS[3].EstimatedMinutesRemaining:=Real_0;
mind_bool[461]:=UPS_MGE[1].Mains2VoltOutOfToler; |  |  |  | Read_Real(rVar:=UPS[3].IzhodMocL1,lo:=4922,hi:=4923); |  |  | 461:UPS_MGE[1].Mains2VoltOutOfToler:=Bit_0; |  |  |  | 4923:UPS[3].IzhodMocL1:=Real_0;
mind_bool[462]:=UPS_MGE[1].MaintenancePosition; |  |  |  | Read_Real(rVar:=UPS[3].IzhodMocL2,lo:=4924,hi:=4925); |  |  | 462:UPS_MGE[1].MaintenancePosition:=Bit_0; |  |  |  | 4925:UPS[3].IzhodMocL2:=Real_0;
mind_bool[463]:=UPS_MGE[1].ManualBypassSwitch; |  |  |  | Read_Real(rVar:=UPS[3].IzhodMocL3,lo:=4926,hi:=4927); |  |  | 463:UPS_MGE[1].ManualBypassSwitch:=Bit_0; |  |  |  | 4927:UPS[3].IzhodMocL3:=Real_0;
mind_bool[464]:=UPS_MGE[1].NapakaNaVarovalkah; |  |  |  | Read_Real(rVar:=UPS[3].NapetostBaterije,lo:=4928,hi:=4929); |  |  | 464:UPS_MGE[1].NapakaNaVarovalkah:=Bit_0; |  |  |  | 4929:UPS[3].NapetostBaterije:=Real_0;
mind_bool[465]:=UPS_MGE[1].OutputInShortCircuit; |  |  |  | Read_Real(rVar:=UPS[3].TemperaturaBaterije,lo:=4930,hi:=4931); |  |  | 465:UPS_MGE[1].OutputInShortCircuit:=Bit_0; |  |  |  | 4931:UPS[3].TemperaturaBaterije:=Real_0;
mind_bool[466]:=UPS_MGE[1].OutputOverload; |  |  |  | Read_Real(rVar:=UPS[3].VhodFrekvencaL1,lo:=4932,hi:=4933); |  |  | 466:UPS_MGE[1].OutputOverload:=Bit_0; |  |  |  | 4933:UPS[3].VhodFrekvencaL1:=Real_0;
mind_bool[467]:=UPS_MGE[1].OutputThermalOverload; |  |  |  | Read_Real(rVar:=UPS[3].VhodFrekvencaL2,lo:=4934,hi:=4935); |  |  | 467:UPS_MGE[1].OutputThermalOverload:=Bit_0; |  |  |  | 4935:UPS[3].VhodFrekvencaL2:=Real_0;
mind_bool[468]:=UPS_MGE[1].RectifierOn; |  |  |  | Read_Real(rVar:=UPS[3].VhodFrekvencaL3,lo:=4936,hi:=4937); |  |  | 468:UPS_MGE[1].RectifierOn:=Bit_0; |  |  |  | 4937:UPS[3].VhodFrekvencaL3:=Real_0;
mind_bool[469]:=UPS_MGE[1].RectifierThermOverload; |  |  |  | Read_Real(rVar:=UPS[3].VhodNapetostL1,lo:=4938,hi:=4939); |  |  | 469:UPS_MGE[1].RectifierThermOverload:=Bit_0; |  |  |  | 4939:UPS[3].VhodNapetostL1:=Real_0;
mind_bool[470]:=UPS_MGE[1].Skupna_napaka; |  |  |  | Read_Real(rVar:=UPS[3].VhodNapetostL2,lo:=4940,hi:=4941); |  |  | 470:UPS_MGE[1].Skupna_napaka:=Bit_0; |  |  |  | 4941:UPS[3].VhodNapetostL2:=Real_0;
mind_bool[471]:=UPS_MGE[1].UPS_coupled; |  |  |  | Read_Real(rVar:=UPS[3].VhodNapetostL3,lo:=4942,hi:=4943); |  |  | 471:UPS_MGE[1].UPS_coupled:=Bit_0; |  |  |  | 4943:UPS[3].VhodNapetostL3:=Real_0;
mind_bool[472]:=UPS_MGE[1].UPS_error; | [6 empty] | 472:UPS_MGE[1].UPS_error:=Bit_0;
mind_bool[473]:=UPS_MGE[1].UPS_in_backup; | [6 empty] | 473:UPS_MGE[1].UPS_in_backup:=Bit_0;
mind_bool[474]:=ups_polnjenje; | [6 empty] | 474:ups_polnjenje:=Bit_0;
mind_bool[475]:=UPS_V23_delovanje; | [6 empty] | 475:UPS_V23_delovanje:=Bit_0;
mind_bool[476]:=UPS_V23_napaka; | [6 empty] | 476:UPS_V23_napaka:=Bit_0;
mind_bool[477]:=UPS_V25_delovanje; | [6 empty] | 477:UPS_V25_delovanje:=Bit_0;
mind_bool[478]:=UPS_V25_napaka; | [6 empty] | 478:UPS_V25_napaka:=Bit_0;
mind_bool[479]:=UPSMGEErrors[10]; | [6 empty] | 479:UPSMGEErrors[10]:=Bit_0;
mind_bool[480]:=UPSMGEErrors[11]; | [6 empty] | 480:UPSMGEErrors[11]:=Bit_0;
mind_bool[481]:=UPSMGEErrors[12]; | [6 empty] | 481:UPSMGEErrors[12]:=Bit_0;
mind_bool[482]:=UPSMGEErrors[13]; | [6 empty] | 482:UPSMGEErrors[13]:=Bit_0;
mind_bool[483]:=UPSMGEErrors[14]; | [6 empty] | 483:UPSMGEErrors[14]:=Bit_0;
mind_bool[484]:=UPSMGEErrors[15]; | [6 empty] | 484:UPSMGEErrors[15]:=Bit_0;
mind_bool[485]:=UPSMGEErrors[16]; | [6 empty] | 485:UPSMGEErrors[16]:=Bit_0;
mind_bool[486]:=UPSMGEErrors[17]; | [6 empty] | 486:UPSMGEErrors[17]:=Bit_0;
mind_bool[487]:=UPSMGEErrors[1]; | [6 empty] | 487:UPSMGEErrors[1]:=Bit_0;
mind_bool[488]:=UPSMGEErrors[2]; | [6 empty] | 488:UPSMGEErrors[2]:=Bit_0;
mind_bool[489]:=UPSMGEErrors[3]; | [6 empty] | 489:UPSMGEErrors[3]:=Bit_0;
mind_bool[490]:=UPSMGEErrors[4]; | [6 empty] | 490:UPSMGEErrors[4]:=Bit_0;
mind_bool[491]:=UPSMGEErrors[5]; | [6 empty] | 491:UPSMGEErrors[5]:=Bit_0;
mind_bool[492]:=UPSMGEErrors[6]; | [6 empty] | 492:UPSMGEErrors[6]:=Bit_0;
mind_bool[493]:=UPSMGEErrors[7]; | [6 empty] | 493:UPSMGEErrors[7]:=Bit_0;
mind_bool[494]:=UPSMGEErrors[8]; | [6 empty] | 494:UPSMGEErrors[8]:=Bit_0;
mind_bool[495]:=UPSMGEErrors[9]; | [6 empty] | 495:UPSMGEErrors[9]:=Bit_0;
mind_bool[496]:=UserLoggedIn; | [6 empty] | 496:UserLoggedIn:=Bit_0;
mind_bool[497]:=VLAZILEC1_delovanje; | [6 empty] | 497:VLAZILEC1_delovanje:=Bit_0;
mind_bool[498]:=VLAZILEC1_napaka; | [6 empty] | 498:VLAZILEC1_napaka:=Bit_0;
mind_bool[499]:=VLAZILEC2_delovanje; | [6 empty] | 499:VLAZILEC2_delovanje:=Bit_0;
mind_bool[500]:=VLAZILEC2_napaka; | [6 empty] | 500:VLAZILEC2_napaka:=Bit_0;
mind_bool[501]:=XVH_AlarmOn; | [6 empty] | 501:XVH_AlarmOn:=Bit_0;
mind_bool[502]:=XVH_enopolna_napaka; | [6 empty] | 502:XVH_enopolna_napaka:=Bit_0;

## XSoft_EXP
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
PROGRAM mod_Read
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*Branje BOOL*)
(**)
mind_bool[0]:=AGR_Gasenje_alarm;
mind_bool[1]:=AGR_PozCent_napaka;
mind_bool[2]:=AGR_PozSenzor_okvara;
mind_bool[3]:=AlarmGenUPS_A_V23;
mind_bool[4]:=AlarmGenUPS_V23;
mind_bool[5]:=AlarmGenUPS_V25;
mind_bool[6]:=AlarmPMM1VirATokPrevisok;
mind_bool[7]:=AlarmPMM1VirATokVisok;
mind_bool[8]:=AlarmPMM1VirBTokPrevisok;
mind_bool[9]:=AlarmPMM1VirBTokVisok;
mind_bool[10]:=AlarmPMM2x17nad80[10];
mind_bool[11]:=AlarmPMM2x17nad80[11];
mind_bool[12]:=AlarmPMM2x17nad80[12];
mind_bool[13]:=AlarmPMM2x17nad80[13];
mind_bool[14]:=AlarmPMM2x17nad80[14];
mind_bool[15]:=AlarmPMM2x17nad80[15];
mind_bool[16]:=AlarmPMM2x17nad80[16];
mind_bool[17]:=AlarmPMM2x17nad80[17];
mind_bool[18]:=AlarmPMM2x17nad80[18];
mind_bool[19]:=AlarmPMM2x17nad80[19];
mind_bool[20]:=AlarmPMM2x17nad80[1];
mind_bool[21]:=AlarmPMM2x17nad80[20];
mind_bool[22]:=AlarmPMM2x17nad80[21];
mind_bool[23]:=AlarmPMM2x17nad80[22];
mind_bool[24]:=AlarmPMM2x17nad80[23];
mind_bool[25]:=AlarmPMM2x17nad80[24];
mind_bool[26]:=AlarmPMM2x17nad80[25];
mind_bool[27]:=AlarmPMM2x17nad80[26];
mind_bool[28]:=AlarmPMM2x17nad80[27];
mind_bool[29]:=AlarmPMM2x17nad80[28];
mind_bool[30]:=AlarmPMM2x17nad80[29];
mind_bool[31]:=AlarmPMM2x17nad80[2];
mind_bool[32]:=AlarmPMM2x17nad80[30];
mind_bool[33]:=AlarmPMM2x17nad80[31];
mind_bool[34]:=AlarmPMM2x17nad80[32];
mind_bool[35]:=AlarmPMM2x17nad80[33];
mind_bool[36]:=AlarmPMM2x17nad80[34];
mind_bool[37]:=AlarmPMM2x17nad80[35];
mind_bool[38]:=AlarmPMM2x17nad80[36];
mind_bool[39]:=AlarmPMM2x17nad80[37];
mind_bool[40]:=AlarmPMM2x17nad80[38];
mind_bool[41]:=AlarmPMM2x17nad80[39];
mind_bool[42]:=AlarmPMM2x17nad80[3];
mind_bool[43]:=AlarmPMM2x17nad80[40];
mind_bool[44]:=AlarmPMM2x17nad80[41];
mind_bool[45]:=AlarmPMM2x17nad80[42];
mind_bool[46]:=AlarmPMM2x17nad80[4];
mind_bool[47]:=AlarmPMM2x17nad80[5];
mind_bool[48]:=AlarmPMM2x17nad80[6];
mind_bool[49]:=AlarmPMM2x17nad80[7];
mind_bool[50]:=AlarmPMM2x17nad80[8];
mind_bool[51]:=AlarmPMM2x17nad80[9];
mind_bool[52]:=ALM_AGR_Gasenje_alarm;
mind_bool[53]:=ALM_AGR_PozCent_napaka;
mind_bool[54]:=ALM_AGR_PozSenzor_okvara;
mind_bool[55]:=ALM_GSM_Gasenje_alarm;
mind_bool[56]:=ALM_GSM_PozCent_napaka;
mind_bool[57]:=ALM_GSM_PozSenzor_okvara;
mind_bool[58]:=Circ_Vpis_Dnevne_energija_scada1;
mind_bool[59]:=Circ_Vpis_Dnevne_energija_scada2;
mind_bool[60]:=Circ_Vpis_Mesecna_energija_scada1;
mind_bool[61]:=Circ_Vpis_Mesecna_energija_scada2;
mind_bool[62]:=Circ_Vpis_Tedenska_energija_scada1;
mind_bool[63]:=Circ_Vpis_Tedenska_energija_scada2;
mind_bool[64]:=ComError;
mind_bool[65]:=ComSCADA;
mind_bool[66]:=ComSCADA1;
mind_bool[67]:=ComSCADA2;
mind_bool[68]:=ComSCADA3;
mind_bool[69]:=DI1_I11;
mind_bool[70]:=DI1_I9;
mind_bool[71]:=DI2_I14;
mind_bool[72]:=DI2_I15;
mind_bool[73]:=DI_R3KC_A_Q21_IzkljucenIzpad;
mind_bool[74]:=DI_R3KC_A_Q22_IzkljucenIzpad;
mind_bool[75]:=DI_SBi_RAZS_AA_Izolacija_NOT_OK;
mind_bool[76]:=DI_SBi_RAZS_AB_Izolacija_NOT_OK;
mind_bool[77]:=ErrComCirc[1];
mind_bool[78]:=ErrComKlima[1];
mind_bool[79]:=ErrComKlima[2];
mind_bool[80]:=ErrComPMM[1];
mind_bool[81]:=ErrComPMM[2];
mind_bool[82]:=ErrComPort2;
mind_bool[83]:=ErrComPort3;
mind_bool[84]:=ErrComPort4;
mind_bool[85]:=ErrComUPS[1];
mind_bool[86]:=ErrComUPS[2];
mind_bool[87]:=ErrComUPS[3];
mind_bool[88]:=ErrComUPSMGE[1];
mind_bool[89]:=F1_1_zascita_ok;
mind_bool[90]:=GSM_Gasenje_alarm;
mind_bool[91]:=GSM_PozCent_napaka;
mind_bool[92]:=GSM_PozSenzor_okvara;
mind_bool[93]:=K1_SkupnaNapaka;
mind_bool[94]:=K1_vklop_izklop_poteka;
mind_bool[95]:=K1AlarmPozara;
mind_bool[96]:=K1KlimaZdruzenAlarm;
mind_bool[97]:=K1NiPretoka;
mind_bool[98]:=K1OkvaraRototerma;
mind_bool[99]:=K1OkvaraVlazNap;
mind_bool[100]:=K1PreobMotCrpGr;
mind_bool[101]:=K1PreobMotVent;
mind_bool[102]:=K1ProtizamrzZascAkt;
mind_bool[103]:=K1ZamasenostFiltra;
mind_bool[104]:=K2_SkupnaNapaka;
mind_bool[105]:=K2_vklop_izklop_poteka;
mind_bool[106]:=K2AlarmPozara;
mind_bool[107]:=K2KlimaZdruzenAlarm;
mind_bool[108]:=K2NiPretoka;
mind_bool[109]:=K2OkvaraRototerma;
mind_bool[110]:=K2OkvaraVlazNap;
mind_bool[111]:=K2PreobMotCrpGr;
mind_bool[112]:=K2PreobMotVent;
mind_bool[113]:=K2ProtizamrzZascAkt;
mind_bool[114]:=K2ZamasenostFiltra;
mind_bool[115]:=K3_deluje;
mind_bool[116]:=K3_SkupnaNapaka;
mind_bool[117]:=Klima1_izkljucena;
mind_bool[118]:=KLIMA1_kke_pogon;
mind_bool[119]:=KLIMA1_krm_nap_ok;
mind_bool[120]:=Klima2_izkljucena;
mind_bool[121]:=Klima3_izkljucena;
mind_bool[122]:=Klima[1].Alarm_pozar;
mind_bool[123]:=Klima[1].DelVentHit1;
mind_bool[124]:=Klima[1].DelVentHit2;
mind_bool[125]:=Klima[1].Ni_pretoka;
mind_bool[126]:=Klima[1].OkvaraRototerm;
mind_bool[127]:=Klima[1].OkvaraVlazNap;
mind_bool[128]:=Klima[1].PreobMotCrpGrel;
mind_bool[129]:=Klima[1].PreobMotVent;
mind_bool[130]:=Klima[1].ProtizamrzZascAktivna;
mind_bool[131]:=Klima[1].VklopRegKlimata;
mind_bool[132]:=Klima[1].ZamasenostFiltra;
mind_bool[133]:=Klima[1].ZdruzAlarmA;
mind_bool[134]:=Klima[1].ZdruzAlarmB;
mind_bool[135]:=Klima[2].Alarm_pozar;
mind_bool[136]:=Klima[2].DelVentHit1;
mind_bool[137]:=Klima[2].DelVentHit2;
mind_bool[138]:=Klima[2].Ni_pretoka;
mind_bool[139]:=Klima[2].OkvaraRototerm;
mind_bool[140]:=Klima[2].OkvaraVlazNap;
mind_bool[141]:=Klima[2].PreobMotCrpGrel;
mind_bool[142]:=Klima[2].PreobMotVent;
mind_bool[143]:=Klima[2].ProtizamrzZascAktivna;
mind_bool[144]:=Klima[2].VklopRegKlimata;
mind_bool[145]:=Klima[2].ZamasenostFiltra;
mind_bool[146]:=Klima[2].ZdruzAlarmA;
mind_bool[147]:=Klima[2].ZdruzAlarmB;
mind_bool[148]:=KLIMA_m1_delovanje;
mind_bool[149]:=KLIMA_m1_napaka;
mind_bool[150]:=KLIMA_m2_delovanje;
mind_bool[151]:=KLIMA_m2_napaka;
mind_bool[152]:=KLIMAT1_delovanje;
mind_bool[153]:=KLIMAT1_napaka;
mind_bool[154]:=KLIMAT1_R_zakleni;
mind_bool[155]:=KLIMAT1_vklop_delovanja;
mind_bool[156]:=KLIMAT1_vklop_delovanjaR;
mind_bool[157]:=KLIMAT2_delovanje;
mind_bool[158]:=KLIMAT2_napaka;
mind_bool[159]:=KLIMAT2_R_zakleni;
mind_bool[160]:=KLIMAT2_vklop_delovanja;
mind_bool[161]:=KLIMAT2_vklop_delovanjaR;
mind_bool[162]:=KlimeAVTO;
mind_bool[163]:=N_F1_1_zascita_ok;
mind_bool[164]:=N_KLIMA1_krm_nap_ok;
mind_bool[165]:=N_KLIMAT1_napaka;
mind_bool[166]:=N_KLIMAT2_napaka;
mind_bool[167]:=N_KlimeAVTO;
mind_bool[168]:=N_Q12_izpad;
mind_bool[169]:=N_UPS_A_V23_delovanje;
mind_bool[170]:=N_UPS_A_V23_napaka;
mind_bool[171]:=N_UPS_V23_delovanje;
mind_bool[172]:=N_UPS_V23_napaka;
mind_bool[173]:=N_UPS_V25_delovanje;
mind_bool[174]:=N_UPS_V25_napaka;
mind_bool[175]:=N_VLAZILEC1_napaka;
mind_bool[176]:=N_VLAZILEC2_napaka;
mind_bool[177]:=napaka_kom_panel;
mind_bool[178]:=napaka_kom_scada;
mind_bool[179]:=napaka_kom_scada2;
mind_bool[180]:=NapakaSenzorSkupno;
mind_bool[181]:=NapakaSenzorVlagaHIA1;
mind_bool[182]:=NapakaSenzorVlagaHIA2;
mind_bool[183]:=NapakaSenzorVlagaHIA3;
mind_bool[184]:=NapakaSenzorVlagaHIA4;
mind_bool[185]:=NapakaSenzorVlagaHIA5;
mind_bool[186]:=NapakaSenzorVlagaHIA6;
mind_bool[187]:=NapakaSenzorVlagaHIA7;
mind_bool[188]:=NapakaTSTempTIA1;
mind_bool[189]:=NapakaTSTempTIA2;
mind_bool[190]:=NapakaTSTempTIA3;
mind_bool[191]:=NapakaTSTempTIA4;
mind_bool[192]:=NapakaTSTempTIA5;
mind_bool[193]:=NapakaTSTempTIA6;
mind_bool[194]:=NapakaTSTempTIA7;
mind_bool[195]:=OpozoriloPMM2x17med60in80[10];
mind_bool[196]:=OpozoriloPMM2x17med60in80[11];
mind_bool[197]:=OpozoriloPMM2x17med60in80[12];
mind_bool[198]:=OpozoriloPMM2x17med60in80[13];
mind_bool[199]:=OpozoriloPMM2x17med60in80[14];
mind_bool[200]:=OpozoriloPMM2x17med60in80[15];
mind_bool[201]:=OpozoriloPMM2x17med60in80[16];
mind_bool[202]:=OpozoriloPMM2x17med60in80[17];
mind_bool[203]:=OpozoriloPMM2x17med60in80[18];
mind_bool[204]:=OpozoriloPMM2x17med60in80[19];
mind_bool[205]:=OpozoriloPMM2x17med60in80[1];
mind_bool[206]:=OpozoriloPMM2x17med60in80[20];
mind_bool[207]:=OpozoriloPMM2x17med60in80[21];
mind_bool[208]:=OpozoriloPMM2x17med60in80[22];
mind_bool[209]:=OpozoriloPMM2x17med60in80[23];
mind_bool[210]:=OpozoriloPMM2x17med60in80[24];
mind_bool[211]:=OpozoriloPMM2x17med60in80[25];
mind_bool[212]:=OpozoriloPMM2x17med60in80[26];
mind_bool[213]:=OpozoriloPMM2x17med60in80[27];
mind_bool[214]:=OpozoriloPMM2x17med60in80[28];
mind_bool[215]:=OpozoriloPMM2x17med60in80[29];
mind_bool[216]:=OpozoriloPMM2x17med60in80[2];
mind_bool[217]:=OpozoriloPMM2x17med60in80[30];
mind_bool[218]:=OpozoriloPMM2x17med60in80[31];
mind_bool[219]:=OpozoriloPMM2x17med60in80[32];
mind_bool[220]:=OpozoriloPMM2x17med60in80[33];
mind_bool[221]:=OpozoriloPMM2x17med60in80[34];
mind_bool[222]:=OpozoriloPMM2x17med60in80[35];
mind_bool[223]:=OpozoriloPMM2x17med60in80[36];
mind_bool[224]:=OpozoriloPMM2x17med60in80[37];
mind_bool[225]:=OpozoriloPMM2x17med60in80[38];
mind_bool[226]:=OpozoriloPMM2x17med60in80[39];
mind_bool[227]:=OpozoriloPMM2x17med60in80[3];
mind_bool[228]:=OpozoriloPMM2x17med60in80[40];
mind_bool[229]:=OpozoriloPMM2x17med60in80[41];
mind_bool[230]:=OpozoriloPMM2x17med60in80[42];
mind_bool[231]:=OpozoriloPMM2x17med60in80[4];
mind_bool[232]:=OpozoriloPMM2x17med60in80[5];
mind_bool[233]:=OpozoriloPMM2x17med60in80[6];
mind_bool[234]:=OpozoriloPMM2x17med60in80[7];
mind_bool[235]:=OpozoriloPMM2x17med60in80[8];
mind_bool[236]:=OpozoriloPMM2x17med60in80[9];
mind_bool[237]:=PMM1OverCurrentBetw[1];
mind_bool[238]:=PMM1OverCurrentBetw[2];
mind_bool[239]:=PMM1OverCurrentBetw[3];
mind_bool[240]:=PMM1OverCurrentOver[1];
mind_bool[241]:=PMM1OverCurrentOver[2];
mind_bool[242]:=PMM1OverCurrentOver[3];
mind_bool[243]:=PMM2.QA1_GlStik_IZKLOP_IZPAD;
mind_bool[244]:=PMM2.QB1_GlStik_IZKLOP_IZPAD;
mind_bool[245]:=PMM2.SkNapaka_med60in80;
mind_bool[246]:=PMM2.SkNapaka_nad80;
mind_bool[247]:=PMM2.SkNapakaVirA_med60in80;
mind_bool[248]:=PMM2.SkNapakaVirA_nad80;
mind_bool[249]:=PMM2.SkNapakaVirB_med60in80;
mind_bool[250]:=PMM2.SkNapakaVirB_nad80;
mind_bool[251]:=PMM2.VirA_NapakaOzemljitve;
mind_bool[252]:=PMM2.VirB_NapakaOzemljitve;
mind_bool[253]:=PozarnaCentrala_skupno;
mind_bool[254]:=PrevisokaTemp;
mind_bool[255]:=Q0_izkljuceno;
mind_bool[256]:=Q0_vkljuceno;
mind_bool[257]:=Q12_izkljuceno;
mind_bool[258]:=Q12_izpad;
mind_bool[259]:=Q12_vkljuceno;
mind_bool[260]:=Q21_vkljuceno;
mind_bool[261]:=Q22_vkljuceno;
mind_bool[262]:=razlitjeLAH1;
mind_bool[263]:=razlitjeLAH2;
mind_bool[264]:=razlitjeLAH3;
mind_bool[265]:=razlitjeLAH4;
mind_bool[266]:=SetDateTime;
mind_bool[267]:=SetDateTimeDemand;
mind_bool[268]:=SetDateTimeError;
mind_bool[269]:=SetDateTimeFinished;
mind_bool[270]:=SkupneNapakeNaprav_PMM17VirBVirA;
mind_bool[271]:=SlabaBaterijaPLC;
mind_bool[272]:=TempPovp234Previs;
mind_bool[273]:=TempPovp56Previs;
mind_bool[274]:=TIA1_previs_temp;
mind_bool[275]:=TIA2_previs_temp;
mind_bool[276]:=TIA3_previs_temp;
mind_bool[277]:=TIA4_previs_temp;
mind_bool[278]:=TIA5_previs_temp;
mind_bool[279]:=TIA6_previs_temp;
mind_bool[280]:=TIA7_previs_temp;
mind_bool[281]:=UPS1Errors[10];
mind_bool[282]:=UPS1Errors[11];
mind_bool[283]:=UPS1Errors[12];
mind_bool[284]:=UPS1Errors[13];
mind_bool[285]:=UPS1Errors[14];
mind_bool[286]:=UPS1Errors[15];
mind_bool[287]:=UPS1Errors[16];
mind_bool[288]:=UPS1Errors[17];
mind_bool[289]:=UPS1Errors[18];
mind_bool[290]:=UPS1Errors[19];
mind_bool[291]:=UPS1Errors[1];
mind_bool[292]:=UPS1Errors[20];
mind_bool[293]:=UPS1Errors[21];
mind_bool[294]:=UPS1Errors[22];
mind_bool[295]:=UPS1Errors[23];
mind_bool[296]:=UPS1Errors[24];
mind_bool[297]:=UPS1Errors[25];
mind_bool[298]:=UPS1Errors[2];
mind_bool[299]:=UPS1Errors[3];
mind_bool[300]:=UPS1Errors[4];
mind_bool[301]:=UPS1Errors[5];
mind_bool[302]:=UPS1Errors[6];
mind_bool[303]:=UPS1Errors[7];
mind_bool[304]:=UPS1Errors[8];
mind_bool[305]:=UPS1Errors[9];
mind_bool[306]:=UPS2Errors[10];
mind_bool[307]:=UPS2Errors[11];
mind_bool[308]:=UPS2Errors[12];
mind_bool[309]:=UPS2Errors[13];
mind_bool[310]:=UPS2Errors[14];
mind_bool[311]:=UPS2Errors[15];
mind_bool[312]:=UPS2Errors[16];
mind_bool[313]:=UPS2Errors[17];
mind_bool[314]:=UPS2Errors[18];
mind_bool[315]:=UPS2Errors[19];
mind_bool[316]:=UPS2Errors[1];
mind_bool[317]:=UPS2Errors[20];
mind_bool[318]:=UPS2Errors[21];
mind_bool[319]:=UPS2Errors[22];
mind_bool[320]:=UPS2Errors[23];
mind_bool[321]:=UPS2Errors[24];
mind_bool[322]:=UPS2Errors[25];
mind_bool[323]:=UPS2Errors[2];
mind_bool[324]:=UPS2Errors[3];
mind_bool[325]:=UPS2Errors[4];
mind_bool[326]:=UPS2Errors[5];
mind_bool[327]:=UPS2Errors[6];
mind_bool[328]:=UPS2Errors[7];
mind_bool[329]:=UPS2Errors[8];
mind_bool[330]:=UPS2Errors[9];
mind_bool[331]:=UPS3Errors[10];
mind_bool[332]:=UPS3Errors[11];
mind_bool[333]:=UPS3Errors[12];
mind_bool[334]:=UPS3Errors[13];
mind_bool[335]:=UPS3Errors[14];
mind_bool[336]:=UPS3Errors[15];
mind_bool[337]:=UPS3Errors[16];
mind_bool[338]:=UPS3Errors[17];
mind_bool[339]:=UPS3Errors[18];
mind_bool[340]:=UPS3Errors[19];
mind_bool[341]:=UPS3Errors[1];
mind_bool[342]:=UPS3Errors[20];
mind_bool[343]:=UPS3Errors[21];
mind_bool[344]:=UPS3Errors[22];
mind_bool[345]:=UPS3Errors[23];
mind_bool[346]:=UPS3Errors[24];
mind_bool[347]:=UPS3Errors[25];
mind_bool[348]:=UPS3Errors[2];
mind_bool[349]:=UPS3Errors[3];
mind_bool[350]:=UPS3Errors[4];
mind_bool[351]:=UPS3Errors[5];
mind_bool[352]:=UPS3Errors[6];
mind_bool[353]:=UPS3Errors[7];
mind_bool[354]:=UPS3Errors[8];
mind_bool[355]:=UPS3Errors[9];
mind_bool[356]:=UPS[1].AlarmAwaitingPower;
mind_bool[357]:=UPS[1].AlarmBypassBad;
mind_bool[358]:=UPS[1].AlarmChargerFailed;
mind_bool[359]:=UPS[1].AlarmCommunicationsLost;
mind_bool[360]:=UPS[1].AlarmDepletedBattery;
mind_bool[361]:=UPS[1].AlarmDiagnosticTestFailed;
mind_bool[362]:=UPS[1].AlarmInverterError;
mind_bool[363]:=UPS[1].AlarmIzhodOffKotZahtevano;
mind_bool[364]:=UPS[1].AlarmIzhodPreobremenjen;
mind_bool[365]:=UPS[1].AlarmLowBattery;
mind_bool[366]:=UPS[1].AlarmNapakaNaVarovalki;
mind_bool[367]:=UPS[1].AlarmNapakaNaVentilatorju;
mind_bool[368]:=UPS[1].AlarmOnBattery;
mind_bool[369]:=UPS[1].AlarmOnBypass;
mind_bool[370]:=UPS[1].AlarmShutdownImminent;
mind_bool[371]:=UPS[1].AlarmShutdownPending;
mind_bool[372]:=UPS[1].AlarmSlabaBaterija;
mind_bool[373]:=UPS[1].AlarmSplosnaNapaka;
mind_bool[374]:=UPS[1].AlarmStanjeIzhodaIzvenToleranc;
mind_bool[375]:=UPS[1].AlarmStanjeVhodaIzvenToleranc;
mind_bool[376]:=UPS[1].AlarmTemperaturaIzvenToleranc;
mind_bool[377]:=UPS[1].AlarmTestInProgres;
mind_bool[378]:=UPS[1].AlarmUPSIzhodOff;
mind_bool[379]:=UPS[1].AlarmUPSOffKotZahtevano;
mind_bool[380]:=UPS[1].AlarmUPSSystemOff;
mind_bool[381]:=UPS[1].Napaka;
mind_bool[382]:=UPS[1].StatusEcomodeAktiven;
mind_bool[383]:=UPS[1].StatusInverterIsOn;
mind_bool[384]:=UPS[1].StatusStopOperation;
mind_bool[385]:=UPS[2].AlarmAwaitingPower;
mind_bool[386]:=UPS[2].AlarmBypassBad;
mind_bool[387]:=UPS[2].AlarmChargerFailed;
mind_bool[388]:=UPS[2].AlarmCommunicationsLost;
mind_bool[389]:=UPS[2].AlarmDepletedBattery;
mind_bool[390]:=UPS[2].AlarmDiagnosticTestFailed;
mind_bool[391]:=UPS[2].AlarmInverterError;
mind_bool[392]:=UPS[2].AlarmIzhodOffKotZahtevano;
mind_bool[393]:=UPS[2].AlarmIzhodPreobremenjen;
mind_bool[394]:=UPS[2].AlarmLowBattery;
mind_bool[395]:=UPS[2].AlarmNapakaNaVarovalki;
mind_bool[396]:=UPS[2].AlarmNapakaNaVentilatorju;
mind_bool[397]:=UPS[2].AlarmOnBattery;
mind_bool[398]:=UPS[2].AlarmOnBypass;
mind_bool[399]:=UPS[2].AlarmShutdownImminent;
mind_bool[400]:=UPS[2].AlarmShutdownPending;
mind_bool[401]:=UPS[2].AlarmSlabaBaterija;
mind_bool[402]:=UPS[2].AlarmSplosnaNapaka;
mind_bool[403]:=UPS[2].AlarmStanjeIzhodaIzvenToleranc;
mind_bool[404]:=UPS[2].AlarmStanjeVhodaIzvenToleranc;
mind_bool[405]:=UPS[2].AlarmTemperaturaIzvenToleranc;
mind_bool[406]:=UPS[2].AlarmTestInProgres;
mind_bool[407]:=UPS[2].AlarmUPSIzhodOff;
mind_bool[408]:=UPS[2].AlarmUPSOffKotZahtevano;
mind_bool[409]:=UPS[2].AlarmUPSSystemOff;
mind_bool[410]:=UPS[2].Napaka;
mind_bool[411]:=UPS[2].StatusEcomodeAktiven;
mind_bool[412]:=UPS[2].StatusInverterIsOn;
mind_bool[413]:=UPS[2].StatusStopOperation;
mind_bool[414]:=UPS[3].AlarmAwaitingPower;
mind_bool[415]:=UPS[3].AlarmBypassBad;
mind_bool[416]:=UPS[3].AlarmChargerFailed;
mind_bool[417]:=UPS[3].AlarmCommunicationsLost;
mind_bool[418]:=UPS[3].AlarmDepletedBattery;
mind_bool[419]:=UPS[3].AlarmDiagnosticTestFailed;
mind_bool[420]:=UPS[3].AlarmInverterError;
mind_bool[421]:=UPS[3].AlarmIzhodOffKotZahtevano;
mind_bool[422]:=UPS[3].AlarmIzhodPreobremenjen;
mind_bool[423]:=UPS[3].AlarmLowBattery;
mind_bool[424]:=UPS[3].AlarmNapakaNaVarovalki;
mind_bool[425]:=UPS[3].AlarmNapakaNaVentilatorju;
mind_bool[426]:=UPS[3].AlarmOnBattery;
mind_bool[427]:=UPS[3].AlarmOnBypass;
mind_bool[428]:=UPS[3].AlarmShutdownImminent;
mind_bool[429]:=UPS[3].AlarmShutdownPending;
mind_bool[430]:=UPS[3].AlarmSlabaBaterija;
mind_bool[431]:=UPS[3].AlarmSplosnaNapaka;
mind_bool[432]:=UPS[3].AlarmStanjeIzhodaIzvenToleranc;
mind_bool[433]:=UPS[3].AlarmStanjeVhodaIzvenToleranc;
mind_bool[434]:=UPS[3].AlarmTemperaturaIzvenToleranc;
mind_bool[435]:=UPS[3].AlarmTestInProgres;
mind_bool[436]:=UPS[3].AlarmUPSIzhodOff;
mind_bool[437]:=UPS[3].AlarmUPSOffKotZahtevano;
mind_bool[438]:=UPS[3].AlarmUPSSystemOff;
mind_bool[439]:=UPS[3].Napaka;
mind_bool[440]:=UPS[3].StatusEcomodeAktiven;
mind_bool[441]:=UPS[3].StatusInverterIsOn;
mind_bool[442]:=UPS[3].StatusStopOperation;
mind_bool[443]:=UPS_A_V23_delovanje;
mind_bool[444]:=UPS_A_V23_napaka;
mind_bool[445]:=ups_alarm;
mind_bool[446]:=ups_baterijski_nac;
mind_bool[447]:=UPS_MGE[1].BatteryChargedState;
mind_bool[448]:=UPS_MGE[1].BatteryCircuitBreaker;
mind_bool[449]:=UPS_MGE[1].BatteryCompInProgress;
mind_bool[450]:=UPS_MGE[1].BatteryFuseFault;
mind_bool[451]:=UPS_MGE[1].BatteryLowWarning;
mind_bool[452]:=UPS_MGE[1].BatteryTempOutOfToler;
mind_bool[453]:=UPS_MGE[1].BypassInFreeFrequency;
mind_bool[454]:=UPS_MGE[1].ChargerGeneralFault;
mind_bool[455]:=UPS_MGE[1].DeviceVentilationFault;
mind_bool[456]:=UPS_MGE[1].InverterFuseFault;
mind_bool[457]:=UPS_MGE[1].InverterOverload;
mind_bool[458]:=UPS_MGE[1].InverterThermalOverload;
mind_bool[459]:=UPS_MGE[1].Mains1VoltOutOfToler;
mind_bool[460]:=UPS_MGE[1].Mains2Overload;
mind_bool[461]:=UPS_MGE[1].Mains2VoltOutOfToler;
mind_bool[462]:=UPS_MGE[1].MaintenancePosition;
mind_bool[463]:=UPS_MGE[1].ManualBypassSwitch;
mind_bool[464]:=UPS_MGE[1].NapakaNaVarovalkah;
mind_bool[465]:=UPS_MGE[1].OutputInShortCircuit;
mind_bool[466]:=UPS_MGE[1].OutputOverload;
mind_bool[467]:=UPS_MGE[1].OutputThermalOverload;
mind_bool[468]:=UPS_MGE[1].RectifierOn;
mind_bool[469]:=UPS_MGE[1].RectifierThermOverload;
mind_bool[470]:=UPS_MGE[1].Skupna_napaka;
mind_bool[471]:=UPS_MGE[1].UPS_coupled;
mind_bool[472]:=UPS_MGE[1].UPS_error;
mind_bool[473]:=UPS_MGE[1].UPS_in_backup;
mind_bool[474]:=ups_polnjenje;
mind_bool[475]:=UPS_V23_delovanje;
mind_bool[476]:=UPS_V23_napaka;
mind_bool[477]:=UPS_V25_delovanje;
mind_bool[478]:=UPS_V25_napaka;
mind_bool[479]:=UPSMGEErrors[10];
mind_bool[480]:=UPSMGEErrors[11];
mind_bool[481]:=UPSMGEErrors[12];
mind_bool[482]:=UPSMGEErrors[13];
mind_bool[483]:=UPSMGEErrors[14];
mind_bool[484]:=UPSMGEErrors[15];
mind_bool[485]:=UPSMGEErrors[16];
mind_bool[486]:=UPSMGEErrors[17];
mind_bool[487]:=UPSMGEErrors[1];
mind_bool[488]:=UPSMGEErrors[2];
mind_bool[489]:=UPSMGEErrors[3];
mind_bool[490]:=UPSMGEErrors[4];
mind_bool[491]:=UPSMGEErrors[5];
mind_bool[492]:=UPSMGEErrors[6];
mind_bool[493]:=UPSMGEErrors[7];
mind_bool[494]:=UPSMGEErrors[8];
mind_bool[495]:=UPSMGEErrors[9];
mind_bool[496]:=UserLoggedIn;
mind_bool[497]:=VLAZILEC1_delovanje;
mind_bool[498]:=VLAZILEC1_napaka;
mind_bool[499]:=VLAZILEC2_delovanje;
mind_bool[500]:=VLAZILEC2_napaka;
mind_bool[501]:=XVH_AlarmOn;
mind_bool[502]:=XVH_enopolna_napaka;
(*Branje INT*)
(**)
mind[0]:=DateTime.Dan;
mind[1]:=DateTime.Leto;
mind[2]:=DateTime.Leto2;
mind[3]:=DateTime.Mesec;
mind[4]:=DateTime.Minuta;
mind[5]:=DateTime.PLC_Dan;
mind[6]:=DateTime.PLC_DanVTednu;
mind[7]:=DateTime.PLC_Leto;
mind[8]:=DateTime.PLC_Mesec;
mind[9]:=DateTime.PLC_Minuta;
mind[10]:=DateTime.PLC_Sekunda;
mind[11]:=DateTime.PLC_Ura;
mind[12]:=DateTime.Sekunda;
mind[13]:=DateTime.Ura;
mind[14]:=HIA1_vlaga_s;
mind[15]:=HIA2_vlaga_s;
mind[16]:=HIA3_vlaga_s;
mind[17]:=HIA4_vlaga_s;
mind[18]:=HIA5_vlaga_s;
mind[19]:=HIA6_vlaga_s;
mind[20]:=HIA7_vlaga_s;
mind[21]:=Klima[1].Analog_izh_mesanje;
mind[22]:=Klima[1].Analog_izh_rekuperator;
mind[23]:=Klima[1].Analog_izh_VentGrelnika;
mind[24]:=Klima[1].Analog_izh_VentHlajenja;
mind[25]:=Klima[1].Dejanska_zel_temp;
mind[26]:=Klima[1].Hitrost_del_vent_disp;
mind[27]:=Klima[1].Max_vpih;
mind[28]:=Klima[1].Min_vpih;
mind[29]:=Klima[1].Obrat_ure_Vent_h1;
mind[30]:=Klima[1].Obrat_ure_Vent_h2;
mind[31]:=Klima[1].Pol_komp_konec;
mind[32]:=Klima[1].Pol_komp_sprem_zel_vr;
mind[33]:=Klima[1].Pol_komp_zacetek;
mind[34]:=Klima[1].PreklopHitDelVent;
mind[35]:=Klima[1].Protizamrz_zascita;
mind[36]:=Klima[1].Rezim_delovanja;
mind[37]:=Klima[1].Temperatura_dovoda;
mind[38]:=Klima[1].Temperatura_prostora;
mind[39]:=Klima[1].TempPredPloscnimRekup;
mind[40]:=Klima[1].TempZaPloscnimRekup;
mind[41]:=Klima[1].Vlaga_v_prostoru;
mind[42]:=Klima[1].VlagaVstopZrakaProstor;
mind[43]:=Klima[1].Zel_temp_eko_gretja;
mind[44]:=Klima[1].Zel_temp_eko_hlajenja;
mind[45]:=Klima[1].Zel_temp_komf_gretja;
mind[46]:=Klima[1].Zel_temp_komf_hlajenja;
mind[47]:=Klima[1].Zim_komp_konec;
mind[48]:=Klima[1].Zim_komp_sprem_zel_vr;
mind[49]:=Klima[1].Zim_komp_zacetek;
mind[50]:=Klima[1].ZimKompMinVpihKonec;
mind[51]:=Klima[1].ZimKompMinVpihZac;
mind[52]:=Klima[1].ZkompMinVpihSpremZelVr;
mind[53]:=Klima[1].Zunanja_temp;
mind[54]:=Klima[2].Analog_izh_mesanje;
mind[55]:=Klima[2].Analog_izh_rekuperator;
mind[56]:=Klima[2].Analog_izh_VentGrelnika;
mind[57]:=Klima[2].Analog_izh_VentHlajenja;
mind[58]:=Klima[2].Dejanska_zel_temp;
mind[59]:=Klima[2].Hitrost_del_vent_disp;
mind[60]:=Klima[2].Max_vpih;
mind[61]:=Klima[2].Min_vpih;
mind[62]:=Klima[2].Obrat_ure_Vent_h1;
mind[63]:=Klima[2].Obrat_ure_Vent_h2;
mind[64]:=Klima[2].Pol_komp_konec;
mind[65]:=Klima[2].Pol_komp_sprem_zel_vr;
mind[66]:=Klima[2].Pol_komp_zacetek;
mind[67]:=Klima[2].PreklopHitDelVent;
mind[68]:=Klima[2].Protizamrz_zascita;
mind[69]:=Klima[2].Rezim_delovanja;
mind[70]:=Klima[2].Temperatura_dovoda;
mind[71]:=Klima[2].Temperatura_prostora;
mind[72]:=Klima[2].TempPredPloscnimRekup;
mind[73]:=Klima[2].TempZaPloscnimRekup;
mind[74]:=Klima[2].Vlaga_v_prostoru;
mind[75]:=Klima[2].VlagaVstopZrakaProstor;
mind[76]:=Klima[2].Zel_temp_eko_gretja;
mind[77]:=Klima[2].Zel_temp_eko_hlajenja;
mind[78]:=Klima[2].Zel_temp_komf_gretja;
mind[79]:=Klima[2].Zel_temp_komf_hlajenja;
mind[80]:=Klima[2].Zim_komp_konec;
mind[81]:=Klima[2].Zim_komp_sprem_zel_vr;
mind[82]:=Klima[2].Zim_komp_zacetek;
mind[83]:=Klima[2].ZimKompMinVpihKonec;
mind[84]:=Klima[2].ZimKompMinVpihZac;
mind[85]:=Klima[2].ZkompMinVpihSpremZelVr;
mind[86]:=Klima[2].Zunanja_temp;
mind[87]:=KlimaIzklopObrUre;
mind[88]:=Klime_vklopi_n;
mind[89]:=kom_nast_cas_izpada;
mind[90]:=PMM[1].AlarmPhase[1].GlobalAlarmReg;
mind[91]:=PMM[1].AlarmPhase[2].GlobalAlarmReg;
mind[92]:=PMM[1].AlarmPhase[3].GlobalAlarmReg;
mind[93]:=Q12stanje;
mind[94]:=TempHistereza;
mind[95]:=TempPovp234;
mind[96]:=TempPovp234Alarm;
mind[97]:=TempPovp56;
mind[98]:=TempPovp56Alarm;
mind[99]:=TempZaVklopKlim1;
mind[100]:=TempZaVklopKlim2;
mind[101]:=TIA1_alarm;
mind[102]:=TIA1_temp_s;
mind[103]:=TIA2_alarm;
mind[104]:=TIA2_temp_s;
mind[105]:=TIA3_alarm;
mind[106]:=TIA3_temp_s;
mind[107]:=TIA4_alarm;
mind[108]:=TIA4_temp_s;
mind[109]:=TIA5_alarm;
mind[110]:=TIA5_temp_s;
mind[111]:=TIA6_alarm;
mind[112]:=TIA6_temp_s;
mind[113]:=TIA7_alarm;
mind[114]:=TIA7_temp_s;
mind[115]:=UPS[1].InverterStatus;
mind[116]:=UPS[1].OutputStatus;
mind[117]:=UPS[1].SteviloIzpadovVhodneLinije;
mind[118]:=UPS[1].UnitStatus;
mind[119]:=UPS[2].InverterStatus;
mind[120]:=UPS[2].OutputStatus;
mind[121]:=UPS[2].SteviloIzpadovVhodneLinije;
mind[122]:=UPS[2].UnitStatus;
mind[123]:=UPS[3].InverterStatus;
mind[124]:=UPS[3].OutputStatus;
mind[125]:=UPS[3].SteviloIzpadovVhodneLinije;
mind[126]:=UPS[3].UnitStatus;
mind[127]:=UPS_MGE[1].BatteryBackupTime;
mind[128]:=UPS_MGE[1].BatteryChargingLevel;
mind[129]:=UPS_MGE[1].BatteryRechargeDuration;
mind[130]:=UPS_MGE[1].I1output;
mind[131]:=UPS_MGE[1].I2output;
mind[132]:=UPS_MGE[1].I3output;
mind[133]:=UPS_MGE[1].InverterFrequency;
mind[134]:=UPS_MGE[1].OutputActivePower1;
mind[135]:=UPS_MGE[1].OutputActivePower2;
mind[136]:=UPS_MGE[1].OutputActivePower3;
mind[137]:=UPS_MGE[1].OutputFrequency;
mind[138]:=UPS_MGE[1].OutputLoadLevel;
mind[139]:=UPS_MGE[1].StatusBaterije;
mind[140]:=UPS_MGE[1].U12mains1;
mind[141]:=UPS_MGE[1].U12mains2;
mind[142]:=UPS_MGE[1].U1N_inverter;
mind[143]:=UPS_MGE[1].U1N_output;
mind[144]:=UPS_MGE[1].U23mains1;
mind[145]:=UPS_MGE[1].U23mains2;
mind[146]:=UPS_MGE[1].U2N_inverter;
mind[147]:=UPS_MGE[1].U2N_output;
mind[148]:=UPS_MGE[1].U31mains1;
mind[149]:=UPS_MGE[1].U31mains2;
mind[150]:=UPS_MGE[1].U3N_inverter;
mind[151]:=UPS_MGE[1].U3N_output;
mind[152]:=UPS_MGE[1].U_battery;
mind[153]:=UserCurrentLevel;
(*Branje UINT*)
(**)
mind[6000]:=K1_obr_u_skupno;
mind[6001]:=K2_obr_u_skupno;
mind[6002]:=PMM2.VirAAlarmPhase.C01_16_60to80;
mind[6003]:=PMM2.VirAAlarmPhase.C01_16_over80;
mind[6004]:=PMM2.VirAAlarmPhase.C17_32_60to80;
mind[6005]:=PMM2.VirAAlarmPhase.C17_32_over80;
mind[6006]:=PMM2.VirAAlarmPhase.C33_44_60to80;
mind[6007]:=PMM2.VirAAlarmPhase.C33_44_over80;
mind[6008]:=PMM2.VirBAlarmPhase.C01_16_60to80;
mind[6009]:=PMM2.VirBAlarmPhase.C01_16_over80;
mind[6010]:=PMM2.VirBAlarmPhase.C17_32_60to80;
mind[6011]:=PMM2.VirBAlarmPhase.C17_32_over80;
mind[6012]:=PMM2.VirBAlarmPhase.C33_44_60to80;
mind[6013]:=PMM2.VirBAlarmPhase.C33_44_over80;
mind[6014]:=PMM[1].AlarmPhase[1].C01_16_60to80;
mind[6015]:=PMM[1].AlarmPhase[1].C01_16_over80;
mind[6016]:=PMM[1].AlarmPhase[1].C17_32_60to80;
mind[6017]:=PMM[1].AlarmPhase[1].C17_32_over80;
mind[6018]:=PMM[1].AlarmPhase[1].C33_42_60to80;
mind[6019]:=PMM[1].AlarmPhase[1].C33_42_over80;
mind[6020]:=PMM[1].AlarmPhase[2].C01_16_60to80;
mind[6021]:=PMM[1].AlarmPhase[2].C01_16_over80;
mind[6022]:=PMM[1].AlarmPhase[2].C17_32_60to80;
mind[6023]:=PMM[1].AlarmPhase[2].C17_32_over80;
mind[6024]:=PMM[1].AlarmPhase[2].C33_42_60to80;
mind[6025]:=PMM[1].AlarmPhase[2].C33_42_over80;
mind[6026]:=PMM[1].AlarmPhase[3].C01_16_60to80;
mind[6027]:=PMM[1].AlarmPhase[3].C01_16_over80;
mind[6028]:=PMM[1].AlarmPhase[3].C17_32_60to80;
mind[6029]:=PMM[1].AlarmPhase[3].C17_32_over80;
mind[6030]:=PMM[1].AlarmPhase[3].C33_42_60to80;
mind[6031]:=PMM[1].AlarmPhase[3].C33_42_over80;
mind[6032]:=UPS1_StatusBaterije;
mind[6033]:=UPS2_StatusBaterije;
mind[6034]:=UPS3_StatusBaterije;
mind[6035]:=UPS[1].StatusBaterije;
mind[6036]:=UPS[2].StatusBaterije;
mind[6037]:=UPS[3].StatusBaterije;
(*Branje LONG*)
(**)
Read_dWord(dVar:=MAX_SOCKET_FD_SETSIZE,lo:=3000,hi:=3001);
(*Branje REAL*)
(**)
Read_Real(rVar:=Circ[1].CosFi_III,lo:=4000,hi:=4001);
Read_Real(rVar:=Circ[1].DelovnaEnergija,lo:=4002,hi:=4003);
Read_Real(rVar:=Circ[1].DelovnaEnergija_TEMP,lo:=4004,hi:=4005);
Read_Real(rVar:=Circ[1].DelovnaMoc_III,lo:=4006,hi:=4007);
Read_Real(rVar:=Circ[1].DelovnaMoc_L1,lo:=4008,hi:=4009);
Read_Real(rVar:=Circ[1].DelovnaMoc_L2,lo:=4010,hi:=4011);
Read_Real(rVar:=Circ[1].DelovnaMoc_L3,lo:=4012,hi:=4013);
Read_Real(rVar:=Circ[1].Frekvenca_L1,lo:=4014,hi:=4015);
Read_Real(rVar:=Circ[1].InduktivnaEnergija,lo:=4016,hi:=4017);
Read_Real(rVar:=Circ[1].InduktivnaMoc_III,lo:=4018,hi:=4019);
Read_Real(rVar:=Circ[1].JalovaMoc_L1,lo:=4020,hi:=4021);
Read_Real(rVar:=Circ[1].JalovaMoc_L2,lo:=4022,hi:=4023);
Read_Real(rVar:=Circ[1].JalovaMoc_L3,lo:=4024,hi:=4025);
Read_Real(rVar:=Circ[1].KapacitivnaEnergija,lo:=4026,hi:=4027);
Read_Real(rVar:=Circ[1].KapacitivnaMoc_III,lo:=4028,hi:=4029);
Read_Real(rVar:=Circ[1].MaximumDemand,lo:=4030,hi:=4031);
Read_Real(rVar:=Circ[1].MaximumDemandA2,lo:=4032,hi:=4033);
Read_Real(rVar:=Circ[1].MaximumDemandA3,lo:=4034,hi:=4035);
Read_Real(rVar:=Circ[1].Napetost_L1_L2,lo:=4036,hi:=4037);
Read_Real(rVar:=Circ[1].Napetost_L1_N,lo:=4038,hi:=4039);
Read_Real(rVar:=Circ[1].Napetost_L2_L3,lo:=4040,hi:=4041);
Read_Real(rVar:=Circ[1].Napetost_L2_N,lo:=4042,hi:=4043);
Read_Real(rVar:=Circ[1].Napetost_L3_L1,lo:=4044,hi:=4045);
Read_Real(rVar:=Circ[1].Napetost_L3_N,lo:=4046,hi:=4047);
Read_Real(rVar:=Circ[1].NavideznaMoc_III,lo:=4048,hi:=4049);
Read_Real(rVar:=Circ[1].NicelniTok,lo:=4050,hi:=4051);
Read_Real(rVar:=Circ[1].PowerFactor_III,lo:=4052,hi:=4053);
Read_Real(rVar:=Circ[1].PowerFactor_L1,lo:=4054,hi:=4055);
Read_Real(rVar:=Circ[1].PowerFactor_L2,lo:=4056,hi:=4057);
Read_Real(rVar:=Circ[1].PowerFactor_L3,lo:=4058,hi:=4059);
Read_Real(rVar:=Circ[1].RazEner_D,lo:=4060,hi:=4061);
Read_Real(rVar:=Circ[1].RazEner_D_SCADA,lo:=4062,hi:=4063);
Read_Real(rVar:=Circ[1].RazEner_D_TEMP,lo:=4064,hi:=4065);
Read_Real(rVar:=Circ[1].RazEner_M,lo:=4066,hi:=4067);
Read_Real(rVar:=Circ[1].RazEner_M_SCADA,lo:=4068,hi:=4069);
Read_Real(rVar:=Circ[1].RazEner_M_TEMP,lo:=4070,hi:=4071);
Read_Real(rVar:=Circ[1].RazEner_T,lo:=4072,hi:=4073);
Read_Real(rVar:=Circ[1].RazEner_T_SCADA,lo:=4074,hi:=4075);
Read_Real(rVar:=Circ[1].RazEner_T_TEMP,lo:=4076,hi:=4077);
Read_Real(rVar:=Circ[1].THDI_L1,lo:=4078,hi:=4079);
Read_Real(rVar:=Circ[1].THDI_L2,lo:=4080,hi:=4081);
Read_Real(rVar:=Circ[1].THDI_L3,lo:=4082,hi:=4083);
Read_Real(rVar:=Circ[1].THDV_L1,lo:=4084,hi:=4085);
Read_Real(rVar:=Circ[1].THDV_L2,lo:=4086,hi:=4087);
Read_Real(rVar:=Circ[1].THDV_L3,lo:=4088,hi:=4089);
Read_Real(rVar:=Circ[1].Tok_L1,lo:=4090,hi:=4091);
Read_Real(rVar:=Circ[1].Tok_L2,lo:=4092,hi:=4093);
Read_Real(rVar:=Circ[1].Tok_L3,lo:=4094,hi:=4095);
Read_Real(rVar:=Circ[1].TokPovprecje_III,lo:=4096,hi:=4097);
Read_Real(rVar:=PMM2.VirA.Current[10],lo:=4098,hi:=4099);
Read_Real(rVar:=PMM2.VirA.Current[11],lo:=4100,hi:=4101);
Read_Real(rVar:=PMM2.VirA.Current[12],lo:=4102,hi:=4103);
Read_Real(rVar:=PMM2.VirA.Current[13],lo:=4104,hi:=4105);
Read_Real(rVar:=PMM2.VirA.Current[14],lo:=4106,hi:=4107);
Read_Real(rVar:=PMM2.VirA.Current[15],lo:=4108,hi:=4109);
Read_Real(rVar:=PMM2.VirA.Current[16],lo:=4110,hi:=4111);
Read_Real(rVar:=PMM2.VirA.Current[17],lo:=4112,hi:=4113);
Read_Real(rVar:=PMM2.VirA.Current[18],lo:=4114,hi:=4115);
Read_Real(rVar:=PMM2.VirA.Current[19],lo:=4116,hi:=4117);
Read_Real(rVar:=PMM2.VirA.Current[1],lo:=4118,hi:=4119);
Read_Real(rVar:=PMM2.VirA.Current[20],lo:=4120,hi:=4121);
Read_Real(rVar:=PMM2.VirA.Current[21],lo:=4122,hi:=4123);
Read_Real(rVar:=PMM2.VirA.Current[22],lo:=4124,hi:=4125);
Read_Real(rVar:=PMM2.VirA.Current[23],lo:=4126,hi:=4127);
Read_Real(rVar:=PMM2.VirA.Current[24],lo:=4128,hi:=4129);
Read_Real(rVar:=PMM2.VirA.Current[25],lo:=4130,hi:=4131);
Read_Real(rVar:=PMM2.VirA.Current[26],lo:=4132,hi:=4133);
Read_Real(rVar:=PMM2.VirA.Current[27],lo:=4134,hi:=4135);
Read_Real(rVar:=PMM2.VirA.Current[28],lo:=4136,hi:=4137);
Read_Real(rVar:=PMM2.VirA.Current[29],lo:=4138,hi:=4139);
Read_Real(rVar:=PMM2.VirA.Current[2],lo:=4140,hi:=4141);
Read_Real(rVar:=PMM2.VirA.Current[30],lo:=4142,hi:=4143);
Read_Real(rVar:=PMM2.VirA.Current[31],lo:=4144,hi:=4145);
Read_Real(rVar:=PMM2.VirA.Current[32],lo:=4146,hi:=4147);
Read_Real(rVar:=PMM2.VirA.Current[33],lo:=4148,hi:=4149);
Read_Real(rVar:=PMM2.VirA.Current[34],lo:=4150,hi:=4151);
Read_Real(rVar:=PMM2.VirA.Current[35],lo:=4152,hi:=4153);
Read_Real(rVar:=PMM2.VirA.Current[36],lo:=4154,hi:=4155);
Read_Real(rVar:=PMM2.VirA.Current[37],lo:=4156,hi:=4157);
Read_Real(rVar:=PMM2.VirA.Current[38],lo:=4158,hi:=4159);
Read_Real(rVar:=PMM2.VirA.Current[39],lo:=4160,hi:=4161);
Read_Real(rVar:=PMM2.VirA.Current[3],lo:=4162,hi:=4163);
Read_Real(rVar:=PMM2.VirA.Current[40],lo:=4164,hi:=4165);
Read_Real(rVar:=PMM2.VirA.Current[41],lo:=4166,hi:=4167);
Read_Real(rVar:=PMM2.VirA.Current[42],lo:=4168,hi:=4169);
Read_Real(rVar:=PMM2.VirA.Current[43],lo:=4170,hi:=4171);
Read_Real(rVar:=PMM2.VirA.Current[44],lo:=4172,hi:=4173);
Read_Real(rVar:=PMM2.VirA.Current[4],lo:=4174,hi:=4175);
Read_Real(rVar:=PMM2.VirA.Current[5],lo:=4176,hi:=4177);
Read_Real(rVar:=PMM2.VirA.Current[6],lo:=4178,hi:=4179);
Read_Real(rVar:=PMM2.VirA.Current[7],lo:=4180,hi:=4181);
Read_Real(rVar:=PMM2.VirA.Current[8],lo:=4182,hi:=4183);
Read_Real(rVar:=PMM2.VirA.Current[9],lo:=4184,hi:=4185);
Read_Real(rVar:=PMM2.VirA_fsys,lo:=4186,hi:=4187);
Read_Real(rVar:=PMM2.VirA_Isys,lo:=4188,hi:=4189);
Read_Real(rVar:=PMM2.VirA_PFsys,lo:=4190,hi:=4191);
Read_Real(rVar:=PMM2.VirA_Psys,lo:=4192,hi:=4193);
Read_Real(rVar:=PMM2.VirA_Qsys,lo:=4194,hi:=4195);
Read_Real(rVar:=PMM2.VirA_Ssys,lo:=4196,hi:=4197);
Read_Real(rVar:=PMM2.VirA_Usys,lo:=4198,hi:=4199);
Read_Real(rVar:=PMM2.VirAActiveEnergyConsumed_kWh,lo:=4200,hi:=4201);
Read_Real(rVar:=PMM2.VirAActivePowerPhaseA_kW,lo:=4202,hi:=4203);
Read_Real(rVar:=PMM2.VirAActivePowerPhaseB_kW,lo:=4204,hi:=4205);
Read_Real(rVar:=PMM2.VirAActivePowerPhaseC_kW,lo:=4206,hi:=4207);
Read_Real(rVar:=PMM2.VirAAparentPowerPhaseA,lo:=4208,hi:=4209);
Read_Real(rVar:=PMM2.VirAAparentPowerPhaseB,lo:=4210,hi:=4211);
Read_Real(rVar:=PMM2.VirAAparentPowerPhaseC,lo:=4212,hi:=4213);
Read_Real(rVar:=PMM2.VirACurrentInPhaseA_A,lo:=4214,hi:=4215);
Read_Real(rVar:=PMM2.VirACurrentInPhaseB_A,lo:=4216,hi:=4217);
Read_Real(rVar:=PMM2.VirACurrentInPhaseC_A,lo:=4218,hi:=4219);
Read_Real(rVar:=PMM2.VirAReactiveEnergyConsumed_kVARh,lo:=4220,hi:=4221);
Read_Real(rVar:=PMM2.VirAReactivePowerPhaseA,lo:=4222,hi:=4223);
Read_Real(rVar:=PMM2.VirAReactivePowerPhaseB,lo:=4224,hi:=4225);
Read_Real(rVar:=PMM2.VirAReactivePowerPhaseC,lo:=4226,hi:=4227);
Read_Real(rVar:=PMM2.VirAVoltageBetweenPhaseAB_V,lo:=4228,hi:=4229);
Read_Real(rVar:=PMM2.VirAVoltageBetweenPhaseAN_V,lo:=4230,hi:=4231);
Read_Real(rVar:=PMM2.VirAVoltageBetweenPhaseBC_V,lo:=4232,hi:=4233);
Read_Real(rVar:=PMM2.VirAVoltageBetweenPhaseBN_V,lo:=4234,hi:=4235);
Read_Real(rVar:=PMM2.VirAVoltageBetweenPhaseCA_V,lo:=4236,hi:=4237);
Read_Real(rVar:=PMM2.VirAVoltageBetweenPhaseCN_V,lo:=4238,hi:=4239);
Read_Real(rVar:=PMM2.VirB.Current[10],lo:=4240,hi:=4241);
Read_Real(rVar:=PMM2.VirB.Current[11],lo:=4242,hi:=4243);
Read_Real(rVar:=PMM2.VirB.Current[12],lo:=4244,hi:=4245);
Read_Real(rVar:=PMM2.VirB.Current[13],lo:=4246,hi:=4247);
Read_Real(rVar:=PMM2.VirB.Current[14],lo:=4248,hi:=4249);
Read_Real(rVar:=PMM2.VirB.Current[15],lo:=4250,hi:=4251);
Read_Real(rVar:=PMM2.VirB.Current[16],lo:=4252,hi:=4253);
Read_Real(rVar:=PMM2.VirB.Current[17],lo:=4254,hi:=4255);
Read_Real(rVar:=PMM2.VirB.Current[18],lo:=4256,hi:=4257);
Read_Real(rVar:=PMM2.VirB.Current[19],lo:=4258,hi:=4259);
Read_Real(rVar:=PMM2.VirB.Current[1],lo:=4260,hi:=4261);
Read_Real(rVar:=PMM2.VirB.Current[20],lo:=4262,hi:=4263);
Read_Real(rVar:=PMM2.VirB.Current[21],lo:=4264,hi:=4265);
Read_Real(rVar:=PMM2.VirB.Current[22],lo:=4266,hi:=4267);
Read_Real(rVar:=PMM2.VirB.Current[23],lo:=4268,hi:=4269);
Read_Real(rVar:=PMM2.VirB.Current[24],lo:=4270,hi:=4271);
Read_Real(rVar:=PMM2.VirB.Current[25],lo:=4272,hi:=4273);
Read_Real(rVar:=PMM2.VirB.Current[26],lo:=4274,hi:=4275);
Read_Real(rVar:=PMM2.VirB.Current[27],lo:=4276,hi:=4277);
Read_Real(rVar:=PMM2.VirB.Current[28],lo:=4278,hi:=4279);
Read_Real(rVar:=PMM2.VirB.Current[29],lo:=4280,hi:=4281);
Read_Real(rVar:=PMM2.VirB.Current[2],lo:=4282,hi:=4283);
Read_Real(rVar:=PMM2.VirB.Current[30],lo:=4284,hi:=4285);
Read_Real(rVar:=PMM2.VirB.Current[31],lo:=4286,hi:=4287);
Read_Real(rVar:=PMM2.VirB.Current[32],lo:=4288,hi:=4289);
Read_Real(rVar:=PMM2.VirB.Current[33],lo:=4290,hi:=4291);
Read_Real(rVar:=PMM2.VirB.Current[34],lo:=4292,hi:=4293);
Read_Real(rVar:=PMM2.VirB.Current[35],lo:=4294,hi:=4295);
Read_Real(rVar:=PMM2.VirB.Current[36],lo:=4296,hi:=4297);
Read_Real(rVar:=PMM2.VirB.Current[37],lo:=4298,hi:=4299);
Read_Real(rVar:=PMM2.VirB.Current[38],lo:=4300,hi:=4301);
Read_Real(rVar:=PMM2.VirB.Current[39],lo:=4302,hi:=4303);
Read_Real(rVar:=PMM2.VirB.Current[3],lo:=4304,hi:=4305);
Read_Real(rVar:=PMM2.VirB.Current[40],lo:=4306,hi:=4307);
Read_Real(rVar:=PMM2.VirB.Current[41],lo:=4308,hi:=4309);
Read_Real(rVar:=PMM2.VirB.Current[42],lo:=4310,hi:=4311);
Read_Real(rVar:=PMM2.VirB.Current[43],lo:=4312,hi:=4313);
Read_Real(rVar:=PMM2.VirB.Current[44],lo:=4314,hi:=4315);
Read_Real(rVar:=PMM2.VirB.Current[4],lo:=4316,hi:=4317);
Read_Real(rVar:=PMM2.VirB.Current[5],lo:=4318,hi:=4319);
Read_Real(rVar:=PMM2.VirB.Current[6],lo:=4320,hi:=4321);
Read_Real(rVar:=PMM2.VirB.Current[7],lo:=4322,hi:=4323);
Read_Real(rVar:=PMM2.VirB.Current[8],lo:=4324,hi:=4325);
Read_Real(rVar:=PMM2.VirB.Current[9],lo:=4326,hi:=4327);
Read_Real(rVar:=PMM2.VirB_fsys,lo:=4328,hi:=4329);
Read_Real(rVar:=PMM2.VirB_Isys,lo:=4330,hi:=4331);
Read_Real(rVar:=PMM2.VirB_PFsys,lo:=4332,hi:=4333);
Read_Real(rVar:=PMM2.VirB_Psys,lo:=4334,hi:=4335);
Read_Real(rVar:=PMM2.VirB_Qsys,lo:=4336,hi:=4337);
Read_Real(rVar:=PMM2.VirB_Ssys,lo:=4338,hi:=4339);
Read_Real(rVar:=PMM2.VirB_Usys,lo:=4340,hi:=4341);
Read_Real(rVar:=PMM2.VirBActiveEnergyConsumed_kWh,lo:=4342,hi:=4343);
Read_Real(rVar:=PMM2.VirBActivePowerPhaseA_kW,lo:=4344,hi:=4345);
Read_Real(rVar:=PMM2.VirBActivePowerPhaseB_kW,lo:=4346,hi:=4347);
Read_Real(rVar:=PMM2.VirBActivePowerPhaseC_kW,lo:=4348,hi:=4349);
Read_Real(rVar:=PMM2.VirBAparentPowerPhaseA,lo:=4350,hi:=4351);
Read_Real(rVar:=PMM2.VirBAparentPowerPhaseB,lo:=4352,hi:=4353);
Read_Real(rVar:=PMM2.VirBAparentPowerPhaseC,lo:=4354,hi:=4355);
Read_Real(rVar:=PMM2.VirBCurrentInPhaseA_A,lo:=4356,hi:=4357);
Read_Real(rVar:=PMM2.VirBCurrentInPhaseB_A,lo:=4358,hi:=4359);
Read_Real(rVar:=PMM2.VirBCurrentInPhaseC_A,lo:=4360,hi:=4361);
Read_Real(rVar:=PMM2.VirBReactiveEnergyConsumed_kVARh,lo:=4362,hi:=4363);
Read_Real(rVar:=PMM2.VirBReactivePowerPhaseA,lo:=4364,hi:=4365);
Read_Real(rVar:=PMM2.VirBReactivePowerPhaseB,lo:=4366,hi:=4367);
Read_Real(rVar:=PMM2.VirBReactivePowerPhaseC,lo:=4368,hi:=4369);
Read_Real(rVar:=PMM2.VirBVoltageBetweenPhaseAB_V,lo:=4370,hi:=4371);
Read_Real(rVar:=PMM2.VirBVoltageBetweenPhaseAN_V,lo:=4372,hi:=4373);
Read_Real(rVar:=PMM2.VirBVoltageBetweenPhaseBC_V,lo:=4374,hi:=4375);
Read_Real(rVar:=PMM2.VirBVoltageBetweenPhaseBN_V,lo:=4376,hi:=4377);
Read_Real(rVar:=PMM2.VirBVoltageBetweenPhaseCA_V,lo:=4378,hi:=4379);
Read_Real(rVar:=PMM2.VirBVoltageBetweenPhaseCN_V,lo:=4380,hi:=4381);
Read_Real(rVar:=PMM[1].ActiveEnergyConsumed_kWh,lo:=4382,hi:=4383);
Read_Real(rVar:=PMM[1].ActivePowerPhaseA_kW,lo:=4384,hi:=4385);
Read_Real(rVar:=PMM[1].ActivePowerPhaseB_kW,lo:=4386,hi:=4387);
Read_Real(rVar:=PMM[1].ActivePowerPhaseC_kW,lo:=4388,hi:=4389);
Read_Real(rVar:=PMM[1].AparentPowerPhaseA,lo:=4390,hi:=4391);
Read_Real(rVar:=PMM[1].AparentPowerPhaseB,lo:=4392,hi:=4393);
Read_Real(rVar:=PMM[1].AparentPowerPhaseC,lo:=4394,hi:=4395);
Read_Real(rVar:=PMM[1].AverageCurrent_A,lo:=4396,hi:=4397);
Read_Real(rVar:=PMM[1].AveragePhaseToNeutral_V,lo:=4398,hi:=4399);
Read_Real(rVar:=PMM[1].AveragePhaseToPhase_V,lo:=4400,hi:=4401);
Read_Real(rVar:=PMM[1].CurrentInPhaseA_A,lo:=4402,hi:=4403);
Read_Real(rVar:=PMM[1].CurrentInPhaseB_A,lo:=4404,hi:=4405);
Read_Real(rVar:=PMM[1].CurrentInPhaseC_A,lo:=4406,hi:=4407);
Read_Real(rVar:=PMM[1].Frequency_Hz,lo:=4408,hi:=4409);
Read_Real(rVar:=PMM[1].Phase[1].Current[10],lo:=4410,hi:=4411);
Read_Real(rVar:=PMM[1].Phase[1].Current[11],lo:=4412,hi:=4413);
Read_Real(rVar:=PMM[1].Phase[1].Current[12],lo:=4414,hi:=4415);
Read_Real(rVar:=PMM[1].Phase[1].Current[13],lo:=4416,hi:=4417);
Read_Real(rVar:=PMM[1].Phase[1].Current[14],lo:=4418,hi:=4419);
Read_Real(rVar:=PMM[1].Phase[1].Current[15],lo:=4420,hi:=4421);
Read_Real(rVar:=PMM[1].Phase[1].Current[16],lo:=4422,hi:=4423);
Read_Real(rVar:=PMM[1].Phase[1].Current[17],lo:=4424,hi:=4425);
Read_Real(rVar:=PMM[1].Phase[1].Current[18],lo:=4426,hi:=4427);
Read_Real(rVar:=PMM[1].Phase[1].Current[19],lo:=4428,hi:=4429);
Read_Real(rVar:=PMM[1].Phase[1].Current[1],lo:=4430,hi:=4431);
Read_Real(rVar:=PMM[1].Phase[1].Current[20],lo:=4432,hi:=4433);
Read_Real(rVar:=PMM[1].Phase[1].Current[21],lo:=4434,hi:=4435);
Read_Real(rVar:=PMM[1].Phase[1].Current[22],lo:=4436,hi:=4437);
Read_Real(rVar:=PMM[1].Phase[1].Current[23],lo:=4438,hi:=4439);
Read_Real(rVar:=PMM[1].Phase[1].Current[24],lo:=4440,hi:=4441);
Read_Real(rVar:=PMM[1].Phase[1].Current[25],lo:=4442,hi:=4443);
Read_Real(rVar:=PMM[1].Phase[1].Current[26],lo:=4444,hi:=4445);
Read_Real(rVar:=PMM[1].Phase[1].Current[27],lo:=4446,hi:=4447);
Read_Real(rVar:=PMM[1].Phase[1].Current[28],lo:=4448,hi:=4449);
Read_Real(rVar:=PMM[1].Phase[1].Current[29],lo:=4450,hi:=4451);
Read_Real(rVar:=PMM[1].Phase[1].Current[2],lo:=4452,hi:=4453);
Read_Real(rVar:=PMM[1].Phase[1].Current[30],lo:=4454,hi:=4455);
Read_Real(rVar:=PMM[1].Phase[1].Current[31],lo:=4456,hi:=4457);
Read_Real(rVar:=PMM[1].Phase[1].Current[32],lo:=4458,hi:=4459);
Read_Real(rVar:=PMM[1].Phase[1].Current[33],lo:=4460,hi:=4461);
Read_Real(rVar:=PMM[1].Phase[1].Current[34],lo:=4462,hi:=4463);
Read_Real(rVar:=PMM[1].Phase[1].Current[35],lo:=4464,hi:=4465);
Read_Real(rVar:=PMM[1].Phase[1].Current[36],lo:=4466,hi:=4467);
Read_Real(rVar:=PMM[1].Phase[1].Current[37],lo:=4468,hi:=4469);
Read_Real(rVar:=PMM[1].Phase[1].Current[38],lo:=4470,hi:=4471);
Read_Real(rVar:=PMM[1].Phase[1].Current[39],lo:=4472,hi:=4473);
Read_Real(rVar:=PMM[1].Phase[1].Current[3],lo:=4474,hi:=4475);
Read_Real(rVar:=PMM[1].Phase[1].Current[40],lo:=4476,hi:=4477);
Read_Real(rVar:=PMM[1].Phase[1].Current[41],lo:=4478,hi:=4479);
Read_Real(rVar:=PMM[1].Phase[1].Current[42],lo:=4480,hi:=4481);
Read_Real(rVar:=PMM[1].Phase[1].Current[4],lo:=4482,hi:=4483);
Read_Real(rVar:=PMM[1].Phase[1].Current[5],lo:=4484,hi:=4485);
Read_Real(rVar:=PMM[1].Phase[1].Current[6],lo:=4486,hi:=4487);
Read_Real(rVar:=PMM[1].Phase[1].Current[7],lo:=4488,hi:=4489);
Read_Real(rVar:=PMM[1].Phase[1].Current[8],lo:=4490,hi:=4491);
Read_Real(rVar:=PMM[1].Phase[1].Current[9],lo:=4492,hi:=4493);
Read_Real(rVar:=PMM[1].Phase[2].Current[10],lo:=4494,hi:=4495);
Read_Real(rVar:=PMM[1].Phase[2].Current[11],lo:=4496,hi:=4497);
Read_Real(rVar:=PMM[1].Phase[2].Current[12],lo:=4498,hi:=4499);
Read_Real(rVar:=PMM[1].Phase[2].Current[13],lo:=4500,hi:=4501);
Read_Real(rVar:=PMM[1].Phase[2].Current[14],lo:=4502,hi:=4503);
Read_Real(rVar:=PMM[1].Phase[2].Current[15],lo:=4504,hi:=4505);
Read_Real(rVar:=PMM[1].Phase[2].Current[16],lo:=4506,hi:=4507);
Read_Real(rVar:=PMM[1].Phase[2].Current[17],lo:=4508,hi:=4509);
Read_Real(rVar:=PMM[1].Phase[2].Current[18],lo:=4510,hi:=4511);
Read_Real(rVar:=PMM[1].Phase[2].Current[19],lo:=4512,hi:=4513);
Read_Real(rVar:=PMM[1].Phase[2].Current[1],lo:=4514,hi:=4515);
Read_Real(rVar:=PMM[1].Phase[2].Current[20],lo:=4516,hi:=4517);
Read_Real(rVar:=PMM[1].Phase[2].Current[21],lo:=4518,hi:=4519);
Read_Real(rVar:=PMM[1].Phase[2].Current[22],lo:=4520,hi:=4521);
Read_Real(rVar:=PMM[1].Phase[2].Current[23],lo:=4522,hi:=4523);
Read_Real(rVar:=PMM[1].Phase[2].Current[24],lo:=4524,hi:=4525);
Read_Real(rVar:=PMM[1].Phase[2].Current[25],lo:=4526,hi:=4527);
Read_Real(rVar:=PMM[1].Phase[2].Current[26],lo:=4528,hi:=4529);
Read_Real(rVar:=PMM[1].Phase[2].Current[27],lo:=4530,hi:=4531);
Read_Real(rVar:=PMM[1].Phase[2].Current[28],lo:=4532,hi:=4533);
Read_Real(rVar:=PMM[1].Phase[2].Current[29],lo:=4534,hi:=4535);
Read_Real(rVar:=PMM[1].Phase[2].Current[2],lo:=4536,hi:=4537);
Read_Real(rVar:=PMM[1].Phase[2].Current[30],lo:=4538,hi:=4539);
Read_Real(rVar:=PMM[1].Phase[2].Current[31],lo:=4540,hi:=4541);
Read_Real(rVar:=PMM[1].Phase[2].Current[32],lo:=4542,hi:=4543);
Read_Real(rVar:=PMM[1].Phase[2].Current[33],lo:=4544,hi:=4545);
Read_Real(rVar:=PMM[1].Phase[2].Current[34],lo:=4546,hi:=4547);
Read_Real(rVar:=PMM[1].Phase[2].Current[35],lo:=4548,hi:=4549);
Read_Real(rVar:=PMM[1].Phase[2].Current[36],lo:=4550,hi:=4551);
Read_Real(rVar:=PMM[1].Phase[2].Current[37],lo:=4552,hi:=4553);
Read_Real(rVar:=PMM[1].Phase[2].Current[38],lo:=4554,hi:=4555);
Read_Real(rVar:=PMM[1].Phase[2].Current[39],lo:=4556,hi:=4557);
Read_Real(rVar:=PMM[1].Phase[2].Current[3],lo:=4558,hi:=4559);
Read_Real(rVar:=PMM[1].Phase[2].Current[40],lo:=4560,hi:=4561);
Read_Real(rVar:=PMM[1].Phase[2].Current[41],lo:=4562,hi:=4563);
Read_Real(rVar:=PMM[1].Phase[2].Current[42],lo:=4564,hi:=4565);
Read_Real(rVar:=PMM[1].Phase[2].Current[4],lo:=4566,hi:=4567);
Read_Real(rVar:=PMM[1].Phase[2].Current[5],lo:=4568,hi:=4569);
Read_Real(rVar:=PMM[1].Phase[2].Current[6],lo:=4570,hi:=4571);
Read_Real(rVar:=PMM[1].Phase[2].Current[7],lo:=4572,hi:=4573);
Read_Real(rVar:=PMM[1].Phase[2].Current[8],lo:=4574,hi:=4575);
Read_Real(rVar:=PMM[1].Phase[2].Current[9],lo:=4576,hi:=4577);
Read_Real(rVar:=PMM[1].Phase[3].Current[10],lo:=4578,hi:=4579);
Read_Real(rVar:=PMM[1].Phase[3].Current[11],lo:=4580,hi:=4581);
Read_Real(rVar:=PMM[1].Phase[3].Current[12],lo:=4582,hi:=4583);
Read_Real(rVar:=PMM[1].Phase[3].Current[13],lo:=4584,hi:=4585);
Read_Real(rVar:=PMM[1].Phase[3].Current[14],lo:=4586,hi:=4587);
Read_Real(rVar:=PMM[1].Phase[3].Current[15],lo:=4588,hi:=4589);
Read_Real(rVar:=PMM[1].Phase[3].Current[16],lo:=4590,hi:=4591);
Read_Real(rVar:=PMM[1].Phase[3].Current[17],lo:=4592,hi:=4593);
Read_Real(rVar:=PMM[1].Phase[3].Current[18],lo:=4594,hi:=4595);
Read_Real(rVar:=PMM[1].Phase[3].Current[19],lo:=4596,hi:=4597);
Read_Real(rVar:=PMM[1].Phase[3].Current[1],lo:=4598,hi:=4599);
Read_Real(rVar:=PMM[1].Phase[3].Current[20],lo:=4600,hi:=4601);
Read_Real(rVar:=PMM[1].Phase[3].Current[21],lo:=4602,hi:=4603);
Read_Real(rVar:=PMM[1].Phase[3].Current[22],lo:=4604,hi:=4605);
Read_Real(rVar:=PMM[1].Phase[3].Current[23],lo:=4606,hi:=4607);
Read_Real(rVar:=PMM[1].Phase[3].Current[24],lo:=4608,hi:=4609);
Read_Real(rVar:=PMM[1].Phase[3].Current[25],lo:=4610,hi:=4611);
Read_Real(rVar:=PMM[1].Phase[3].Current[26],lo:=4612,hi:=4613);
Read_Real(rVar:=PMM[1].Phase[3].Current[27],lo:=4614,hi:=4615);
Read_Real(rVar:=PMM[1].Phase[3].Current[28],lo:=4616,hi:=4617);
Read_Real(rVar:=PMM[1].Phase[3].Current[29],lo:=4618,hi:=4619);
Read_Real(rVar:=PMM[1].Phase[3].Current[2],lo:=4620,hi:=4621);
Read_Real(rVar:=PMM[1].Phase[3].Current[30],lo:=4622,hi:=4623);
Read_Real(rVar:=PMM[1].Phase[3].Current[31],lo:=4624,hi:=4625);
Read_Real(rVar:=PMM[1].Phase[3].Current[32],lo:=4626,hi:=4627);
Read_Real(rVar:=PMM[1].Phase[3].Current[33],lo:=4628,hi:=4629);
Read_Real(rVar:=PMM[1].Phase[3].Current[34],lo:=4630,hi:=4631);
Read_Real(rVar:=PMM[1].Phase[3].Current[35],lo:=4632,hi:=4633);
Read_Real(rVar:=PMM[1].Phase[3].Current[36],lo:=4634,hi:=4635);
Read_Real(rVar:=PMM[1].Phase[3].Current[37],lo:=4636,hi:=4637);
Read_Real(rVar:=PMM[1].Phase[3].Current[38],lo:=4638,hi:=4639);
Read_Real(rVar:=PMM[1].Phase[3].Current[39],lo:=4640,hi:=4641);
Read_Real(rVar:=PMM[1].Phase[3].Current[3],lo:=4642,hi:=4643);
Read_Real(rVar:=PMM[1].Phase[3].Current[40],lo:=4644,hi:=4645);
Read_Real(rVar:=PMM[1].Phase[3].Current[41],lo:=4646,hi:=4647);
Read_Real(rVar:=PMM[1].Phase[3].Current[42],lo:=4648,hi:=4649);
Read_Real(rVar:=PMM[1].Phase[3].Current[4],lo:=4650,hi:=4651);
Read_Real(rVar:=PMM[1].Phase[3].Current[5],lo:=4652,hi:=4653);
Read_Real(rVar:=PMM[1].Phase[3].Current[6],lo:=4654,hi:=4655);
Read_Real(rVar:=PMM[1].Phase[3].Current[7],lo:=4656,hi:=4657);
Read_Real(rVar:=PMM[1].Phase[3].Current[8],lo:=4658,hi:=4659);
Read_Real(rVar:=PMM[1].Phase[3].Current[9],lo:=4660,hi:=4661);
Read_Real(rVar:=PMM[1].PowerFactorSys,lo:=4662,hi:=4663);
Read_Real(rVar:=PMM[1].ReactiveEnergyConsumed_kVARh,lo:=4664,hi:=4665);
Read_Real(rVar:=PMM[1].ReactivePowerPhaseA,lo:=4666,hi:=4667);
Read_Real(rVar:=PMM[1].ReactivePowerPhaseB,lo:=4668,hi:=4669);
Read_Real(rVar:=PMM[1].ReactivePowerPhaseC,lo:=4670,hi:=4671);
Read_Real(rVar:=PMM[1].TotalActivePower_kW,lo:=4672,hi:=4673);
Read_Real(rVar:=PMM[1].TotalAparentPower_kVA,lo:=4674,hi:=4675);
Read_Real(rVar:=PMM[1].TotalPowerFactor,lo:=4676,hi:=4677);
Read_Real(rVar:=PMM[1].TotalReactivePower_kVAR,lo:=4678,hi:=4679);
Read_Real(rVar:=PMM[1].VirA_fsys,lo:=4680,hi:=4681);
Read_Real(rVar:=PMM[1].VirA_Isys,lo:=4682,hi:=4683);
Read_Real(rVar:=PMM[1].VirA_PFsys,lo:=4684,hi:=4685);
Read_Real(rVar:=PMM[1].VirA_Psys,lo:=4686,hi:=4687);
Read_Real(rVar:=PMM[1].VirA_Qsys,lo:=4688,hi:=4689);
Read_Real(rVar:=PMM[1].VirA_Ssys,lo:=4690,hi:=4691);
Read_Real(rVar:=PMM[1].VirA_Usys,lo:=4692,hi:=4693);
Read_Real(rVar:=PMM[1].VirB_fsys,lo:=4694,hi:=4695);
Read_Real(rVar:=PMM[1].VirB_Isys,lo:=4696,hi:=4697);
Read_Real(rVar:=PMM[1].VirB_PFsys,lo:=4698,hi:=4699);
Read_Real(rVar:=PMM[1].VirB_Psys,lo:=4700,hi:=4701);
Read_Real(rVar:=PMM[1].VirB_Qsys,lo:=4702,hi:=4703);
Read_Real(rVar:=PMM[1].VirB_Ssys,lo:=4704,hi:=4705);
Read_Real(rVar:=PMM[1].VirB_Usys,lo:=4706,hi:=4707);
Read_Real(rVar:=PMM[1].VirBActiveEnergyConsumed_kWh,lo:=4708,hi:=4709);
Read_Real(rVar:=PMM[1].VirBActivePowerPhaseA_kW,lo:=4710,hi:=4711);
Read_Real(rVar:=PMM[1].VirBActivePowerPhaseB_kW,lo:=4712,hi:=4713);
Read_Real(rVar:=PMM[1].VirBActivePowerPhaseC_kW,lo:=4714,hi:=4715);
Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseA,lo:=4716,hi:=4717);
Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseB,lo:=4718,hi:=4719);
Read_Real(rVar:=PMM[1].VirBAparentPowerPhaseC,lo:=4720,hi:=4721);
Read_Real(rVar:=PMM[1].VirBAverageCurrent_A,lo:=4722,hi:=4723);
Read_Real(rVar:=PMM[1].VirBAveragePhaseToNeutral_V,lo:=4724,hi:=4725);
Read_Real(rVar:=PMM[1].VirBAveragePhaseToPhase_V,lo:=4726,hi:=4727);
Read_Real(rVar:=PMM[1].VirBCurrentInPhaseA_A,lo:=4728,hi:=4729);
Read_Real(rVar:=PMM[1].VirBCurrentInPhaseB_A,lo:=4730,hi:=4731);
Read_Real(rVar:=PMM[1].VirBCurrentInPhaseC_A,lo:=4732,hi:=4733);
Read_Real(rVar:=PMM[1].VirBFrequency_Hz,lo:=4734,hi:=4735);
Read_Real(rVar:=PMM[1].VirBPowerFactorSys,lo:=4736,hi:=4737);
Read_Real(rVar:=PMM[1].VirBReactiveEnergyConsumed_kVARh,lo:=4738,hi:=4739);
Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseA,lo:=4740,hi:=4741);
Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseB,lo:=4742,hi:=4743);
Read_Real(rVar:=PMM[1].VirBReactivePowerPhaseC,lo:=4744,hi:=4745);
Read_Real(rVar:=PMM[1].VirBTotalActivePower_kW,lo:=4746,hi:=4747);
Read_Real(rVar:=PMM[1].VirBTotalAparentPower_kVA,lo:=4748,hi:=4749);
Read_Real(rVar:=PMM[1].VirBTotalPowerFactor,lo:=4750,hi:=4751);
Read_Real(rVar:=PMM[1].VirBTotalReactivePower_kVAR,lo:=4752,hi:=4753);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseAB_V,lo:=4754,hi:=4755);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseAN_V,lo:=4756,hi:=4757);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseBC_V,lo:=4758,hi:=4759);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseBN_V,lo:=4760,hi:=4761);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseCA_V,lo:=4762,hi:=4763);
Read_Real(rVar:=PMM[1].VirBVoltageBetweenPhaseCN_V,lo:=4764,hi:=4765);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseAB_V,lo:=4766,hi:=4767);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseAN_V,lo:=4768,hi:=4769);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseBC_V,lo:=4770,hi:=4771);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseBN_V,lo:=4772,hi:=4773);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseCA_V,lo:=4774,hi:=4775);
Read_Real(rVar:=PMM[1].VoltageBetweenPhaseCN_V,lo:=4776,hi:=4777);
Read_Real(rVar:=PMMfaza01,lo:=4778,hi:=4779);
Read_Real(rVar:=PMMfaza02,lo:=4780,hi:=4781);
Read_Real(rVar:=PMMfaza03,lo:=4782,hi:=4783);
Read_Real(rVar:=PMMfaza04,lo:=4784,hi:=4785);
Read_Real(rVar:=PMMfaza05,lo:=4786,hi:=4787);
Read_Real(rVar:=PMMfaza06,lo:=4788,hi:=4789);
Read_Real(rVar:=PMMfaza07,lo:=4790,hi:=4791);
Read_Real(rVar:=PMMfaza08,lo:=4792,hi:=4793);
Read_Real(rVar:=PMMfaza09,lo:=4794,hi:=4795);
Read_Real(rVar:=PMMfaza10,lo:=4796,hi:=4797);
Read_Real(rVar:=PMMfaza11,lo:=4798,hi:=4799);
Read_Real(rVar:=PMMfaza12,lo:=4800,hi:=4801);
Read_Real(rVar:=PMMfaza13,lo:=4802,hi:=4803);
Read_Real(rVar:=PMMfaza14,lo:=4804,hi:=4805);
Read_Real(rVar:=PMMfaza15,lo:=4806,hi:=4807);
Read_Real(rVar:=PMMfaza16,lo:=4808,hi:=4809);
Read_Real(rVar:=PMMfaza17,lo:=4810,hi:=4811);
Read_Real(rVar:=PMMfaza18,lo:=4812,hi:=4813);
Read_Real(rVar:=PMMfaza19,lo:=4814,hi:=4815);
Read_Real(rVar:=PMMfaza20,lo:=4816,hi:=4817);
Read_Real(rVar:=PMMfaza21,lo:=4818,hi:=4819);
Read_Real(rVar:=PMMfaza22,lo:=4820,hi:=4821);
Read_Real(rVar:=PMMfaza23,lo:=4822,hi:=4823);
Read_Real(rVar:=PMMfaza24,lo:=4824,hi:=4825);
Read_Real(rVar:=PMMfaza25,lo:=4826,hi:=4827);
Read_Real(rVar:=PMMfaza26,lo:=4828,hi:=4829);
Read_Real(rVar:=PMMfaza27,lo:=4830,hi:=4831);
Read_Real(rVar:=PMMfaza28,lo:=4832,hi:=4833);
Read_Real(rVar:=PMMfaza29,lo:=4834,hi:=4835);
Read_Real(rVar:=PMMfaza30,lo:=4836,hi:=4837);
Read_Real(rVar:=PMMfaza31,lo:=4838,hi:=4839);
Read_Real(rVar:=PMMfaza32,lo:=4840,hi:=4841);
Read_Real(rVar:=PMMfaza33,lo:=4842,hi:=4843);
Read_Real(rVar:=PMMfaza34,lo:=4844,hi:=4845);
Read_Real(rVar:=PMMfaza35,lo:=4846,hi:=4847);
Read_Real(rVar:=PMMfaza36,lo:=4848,hi:=4849);
Read_Real(rVar:=PMMfaza37,lo:=4850,hi:=4851);
Read_Real(rVar:=PMMfaza38,lo:=4852,hi:=4853);
Read_Real(rVar:=PMMfaza39,lo:=4854,hi:=4855);
Read_Real(rVar:=PMMfaza40,lo:=4856,hi:=4857);
Read_Real(rVar:=PMMfaza41,lo:=4858,hi:=4859);
Read_Real(rVar:=PMMfaza42,lo:=4860,hi:=4861);
Read_Real(rVar:=PMMskupniTokA,lo:=4862,hi:=4863);
Read_Real(rVar:=PMMskupniTokB,lo:=4864,hi:=4865);
Read_Real(rVar:=UPS[1].EstimatedChargeRemaining,lo:=4866,hi:=4867);
Read_Real(rVar:=UPS[1].EstimatedMinutesRemaining,lo:=4868,hi:=4869);
Read_Real(rVar:=UPS[1].IzhodMocL1,lo:=4870,hi:=4871);
Read_Real(rVar:=UPS[1].IzhodMocL2,lo:=4872,hi:=4873);
Read_Real(rVar:=UPS[1].IzhodMocL3,lo:=4874,hi:=4875);
Read_Real(rVar:=UPS[1].NapetostBaterije,lo:=4876,hi:=4877);
Read_Real(rVar:=UPS[1].TemperaturaBaterije,lo:=4878,hi:=4879);
Read_Real(rVar:=UPS[1].VhodFrekvencaL1,lo:=4880,hi:=4881);
Read_Real(rVar:=UPS[1].VhodFrekvencaL2,lo:=4882,hi:=4883);
Read_Real(rVar:=UPS[1].VhodFrekvencaL3,lo:=4884,hi:=4885);
Read_Real(rVar:=UPS[1].VhodNapetostL1,lo:=4886,hi:=4887);
Read_Real(rVar:=UPS[1].VhodNapetostL2,lo:=4888,hi:=4889);
Read_Real(rVar:=UPS[1].VhodNapetostL3,lo:=4890,hi:=4891);
Read_Real(rVar:=UPS[2].EstimatedChargeRemaining,lo:=4892,hi:=4893);
Read_Real(rVar:=UPS[2].EstimatedMinutesRemaining,lo:=4894,hi:=4895);
Read_Real(rVar:=UPS[2].IzhodMocL1,lo:=4896,hi:=4897);
Read_Real(rVar:=UPS[2].IzhodMocL2,lo:=4898,hi:=4899);
Read_Real(rVar:=UPS[2].IzhodMocL3,lo:=4900,hi:=4901);
Read_Real(rVar:=UPS[2].NapetostBaterije,lo:=4902,hi:=4903);
Read_Real(rVar:=UPS[2].TemperaturaBaterije,lo:=4904,hi:=4905);
Read_Real(rVar:=UPS[2].VhodFrekvencaL1,lo:=4906,hi:=4907);
Read_Real(rVar:=UPS[2].VhodFrekvencaL2,lo:=4908,hi:=4909);
Read_Real(rVar:=UPS[2].VhodFrekvencaL3,lo:=4910,hi:=4911);
Read_Real(rVar:=UPS[2].VhodNapetostL1,lo:=4912,hi:=4913);
Read_Real(rVar:=UPS[2].VhodNapetostL2,lo:=4914,hi:=4915);
Read_Real(rVar:=UPS[2].VhodNapetostL3,lo:=4916,hi:=4917);
Read_Real(rVar:=UPS[3].EstimatedChargeRemaining,lo:=4918,hi:=4919);
Read_Real(rVar:=UPS[3].EstimatedMinutesRemaining,lo:=4920,hi:=4921);
Read_Real(rVar:=UPS[3].IzhodMocL1,lo:=4922,hi:=4923);
Read_Real(rVar:=UPS[3].IzhodMocL2,lo:=4924,hi:=4925);
Read_Real(rVar:=UPS[3].IzhodMocL3,lo:=4926,hi:=4927);
Read_Real(rVar:=UPS[3].NapetostBaterije,lo:=4928,hi:=4929);
Read_Real(rVar:=UPS[3].TemperaturaBaterije,lo:=4930,hi:=4931);
Read_Real(rVar:=UPS[3].VhodFrekvencaL1,lo:=4932,hi:=4933);
Read_Real(rVar:=UPS[3].VhodFrekvencaL2,lo:=4934,hi:=4935);
Read_Real(rVar:=UPS[3].VhodFrekvencaL3,lo:=4936,hi:=4937);
Read_Real(rVar:=UPS[3].VhodNapetostL1,lo:=4938,hi:=4939);
Read_Real(rVar:=UPS[3].VhodNapetostL2,lo:=4940,hi:=4941);
Read_Real(rVar:=UPS[3].VhodNapetostL3,lo:=4942,hi:=4943);
(*Branje STRING*)
(**)
Read_String(sVar:=cas_modbus_izpad,start:=5000);
Read_String(sVar:=Date_Time[0],start:=5015);
Read_String(sVar:=Date_Time[1],start:=5030);
Read_String(sVar:=Date_Time[2],start:=5045);
Read_String(sVar:=Date_Time[3],start:=5060);
Read_String(sVar:=K1obrat_ure,start:=5075);
Read_String(sVar:=UserCurrentName,start:=5090);
Read_String(sVar:=UserDisplay,start:=5105);
(*Branje ULONG*)
(**)
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Bool : BOOL
VAR_INPUT
index: INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje BOOL*)
(**)
0:AGR_Gasenje_alarm:=Bit_0;
1:AGR_PozCent_napaka:=Bit_0;
2:AGR_PozSenzor_okvara:=Bit_0;
3:AlarmGenUPS_A_V23:=Bit_0;
4:AlarmGenUPS_V23:=Bit_0;
5:AlarmGenUPS_V25:=Bit_0;
6:AlarmPMM1VirATokPrevisok:=Bit_0;
7:AlarmPMM1VirATokVisok:=Bit_0;
8:AlarmPMM1VirBTokPrevisok:=Bit_0;
9:AlarmPMM1VirBTokVisok:=Bit_0;
10:AlarmPMM2x17nad80[10]:=Bit_0;
11:AlarmPMM2x17nad80[11]:=Bit_0;
12:AlarmPMM2x17nad80[12]:=Bit_0;
13:AlarmPMM2x17nad80[13]:=Bit_0;
14:AlarmPMM2x17nad80[14]:=Bit_0;
15:AlarmPMM2x17nad80[15]:=Bit_0;
16:AlarmPMM2x17nad80[16]:=Bit_0;
17:AlarmPMM2x17nad80[17]:=Bit_0;
18:AlarmPMM2x17nad80[18]:=Bit_0;
19:AlarmPMM2x17nad80[19]:=Bit_0;
20:AlarmPMM2x17nad80[1]:=Bit_0;
21:AlarmPMM2x17nad80[20]:=Bit_0;
22:AlarmPMM2x17nad80[21]:=Bit_0;
23:AlarmPMM2x17nad80[22]:=Bit_0;
24:AlarmPMM2x17nad80[23]:=Bit_0;
25:AlarmPMM2x17nad80[24]:=Bit_0;
26:AlarmPMM2x17nad80[25]:=Bit_0;
27:AlarmPMM2x17nad80[26]:=Bit_0;
28:AlarmPMM2x17nad80[27]:=Bit_0;
29:AlarmPMM2x17nad80[28]:=Bit_0;
30:AlarmPMM2x17nad80[29]:=Bit_0;
31:AlarmPMM2x17nad80[2]:=Bit_0;
32:AlarmPMM2x17nad80[30]:=Bit_0;
33:AlarmPMM2x17nad80[31]:=Bit_0;
34:AlarmPMM2x17nad80[32]:=Bit_0;
35:AlarmPMM2x17nad80[33]:=Bit_0;
36:AlarmPMM2x17nad80[34]:=Bit_0;
37:AlarmPMM2x17nad80[35]:=Bit_0;
38:AlarmPMM2x17nad80[36]:=Bit_0;
39:AlarmPMM2x17nad80[37]:=Bit_0;
40:AlarmPMM2x17nad80[38]:=Bit_0;
41:AlarmPMM2x17nad80[39]:=Bit_0;
42:AlarmPMM2x17nad80[3]:=Bit_0;
43:AlarmPMM2x17nad80[40]:=Bit_0;
44:AlarmPMM2x17nad80[41]:=Bit_0;
45:AlarmPMM2x17nad80[42]:=Bit_0;
46:AlarmPMM2x17nad80[4]:=Bit_0;
47:AlarmPMM2x17nad80[5]:=Bit_0;
48:AlarmPMM2x17nad80[6]:=Bit_0;
49:AlarmPMM2x17nad80[7]:=Bit_0;
50:AlarmPMM2x17nad80[8]:=Bit_0;
51:AlarmPMM2x17nad80[9]:=Bit_0;
52:ALM_AGR_Gasenje_alarm:=Bit_0;
53:ALM_AGR_PozCent_napaka:=Bit_0;
54:ALM_AGR_PozSenzor_okvara:=Bit_0;
55:ALM_GSM_Gasenje_alarm:=Bit_0;
56:ALM_GSM_PozCent_napaka:=Bit_0;
57:ALM_GSM_PozSenzor_okvara:=Bit_0;
58:Circ_Vpis_Dnevne_energija_scada1:=Bit_0;
59:Circ_Vpis_Dnevne_energija_scada2:=Bit_0;
60:Circ_Vpis_Mesecna_energija_scada1:=Bit_0;
61:Circ_Vpis_Mesecna_energija_scada2:=Bit_0;
62:Circ_Vpis_Tedenska_energija_scada1:=Bit_0;
63:Circ_Vpis_Tedenska_energija_scada2:=Bit_0;
64:ComError:=Bit_0;
65:ComSCADA:=Bit_0;
66:ComSCADA1:=Bit_0;
67:ComSCADA2:=Bit_0;
68:ComSCADA3:=Bit_0;
69:DI1_I11:=Bit_0;
70:DI1_I9:=Bit_0;
71:DI2_I14:=Bit_0;
72:DI2_I15:=Bit_0;
73:DI_R3KC_A_Q21_IzkljucenIzpad:=Bit_0;
74:DI_R3KC_A_Q22_IzkljucenIzpad:=Bit_0;
75:DI_SBi_RAZS_AA_Izolacija_NOT_OK:=Bit_0;
76:DI_SBi_RAZS_AB_Izolacija_NOT_OK:=Bit_0;
77:ErrComCirc[1]:=Bit_0;
78:ErrComKlima[1]:=Bit_0;
79:ErrComKlima[2]:=Bit_0;
80:ErrComPMM[1]:=Bit_0;
81:ErrComPMM[2]:=Bit_0;
82:ErrComPort2:=Bit_0;
83:ErrComPort3:=Bit_0;
84:ErrComPort4:=Bit_0;
85:ErrComUPS[1]:=Bit_0;
86:ErrComUPS[2]:=Bit_0;
87:ErrComUPS[3]:=Bit_0;
88:ErrComUPSMGE[1]:=Bit_0;
89:F1_1_zascita_ok:=Bit_0;
90:GSM_Gasenje_alarm:=Bit_0;
91:GSM_PozCent_napaka:=Bit_0;
92:GSM_PozSenzor_okvara:=Bit_0;
93:K1_SkupnaNapaka:=Bit_0;
94:K1_vklop_izklop_poteka:=Bit_0;
95:K1AlarmPozara:=Bit_0;
96:K1KlimaZdruzenAlarm:=Bit_0;
97:K1NiPretoka:=Bit_0;
98:K1OkvaraRototerma:=Bit_0;
99:K1OkvaraVlazNap:=Bit_0;
100:K1PreobMotCrpGr:=Bit_0;
101:K1PreobMotVent:=Bit_0;
102:K1ProtizamrzZascAkt:=Bit_0;
103:K1ZamasenostFiltra:=Bit_0;
104:K2_SkupnaNapaka:=Bit_0;
105:K2_vklop_izklop_poteka:=Bit_0;
106:K2AlarmPozara:=Bit_0;
107:K2KlimaZdruzenAlarm:=Bit_0;
108:K2NiPretoka:=Bit_0;
109:K2OkvaraRototerma:=Bit_0;
110:K2OkvaraVlazNap:=Bit_0;
111:K2PreobMotCrpGr:=Bit_0;
112:K2PreobMotVent:=Bit_0;
113:K2ProtizamrzZascAkt:=Bit_0;
114:K2ZamasenostFiltra:=Bit_0;
115:K3_deluje:=Bit_0;
116:K3_SkupnaNapaka:=Bit_0;
117:Klima1_izkljucena:=Bit_0;
118:KLIMA1_kke_pogon:=Bit_0;
119:KLIMA1_krm_nap_ok:=Bit_0;
120:Klima2_izkljucena:=Bit_0;
121:Klima3_izkljucena:=Bit_0;
122:Klima[1].Alarm_pozar:=Bit_0;
123:Klima[1].DelVentHit1:=Bit_0;
124:Klima[1].DelVentHit2:=Bit_0;
125:Klima[1].Ni_pretoka:=Bit_0;
126:Klima[1].OkvaraRototerm:=Bit_0;
127:Klima[1].OkvaraVlazNap:=Bit_0;
128:Klima[1].PreobMotCrpGrel:=Bit_0;
129:Klima[1].PreobMotVent:=Bit_0;
130:Klima[1].ProtizamrzZascAktivna:=Bit_0;
131:Klima[1].VklopRegKlimata:=Bit_0;
132:Klima[1].ZamasenostFiltra:=Bit_0;
133:Klima[1].ZdruzAlarmA:=Bit_0;
134:Klima[1].ZdruzAlarmB:=Bit_0;
135:Klima[2].Alarm_pozar:=Bit_0;
136:Klima[2].DelVentHit1:=Bit_0;
137:Klima[2].DelVentHit2:=Bit_0;
138:Klima[2].Ni_pretoka:=Bit_0;
139:Klima[2].OkvaraRototerm:=Bit_0;
140:Klima[2].OkvaraVlazNap:=Bit_0;
141:Klima[2].PreobMotCrpGrel:=Bit_0;
142:Klima[2].PreobMotVent:=Bit_0;
143:Klima[2].ProtizamrzZascAktivna:=Bit_0;
144:Klima[2].VklopRegKlimata:=Bit_0;
145:Klima[2].ZamasenostFiltra:=Bit_0;
146:Klima[2].ZdruzAlarmA:=Bit_0;
147:Klima[2].ZdruzAlarmB:=Bit_0;
148:KLIMA_m1_delovanje:=Bit_0;
149:KLIMA_m1_napaka:=Bit_0;
150:KLIMA_m2_delovanje:=Bit_0;
151:KLIMA_m2_napaka:=Bit_0;
152:KLIMAT1_delovanje:=Bit_0;
153:KLIMAT1_napaka:=Bit_0;
154:KLIMAT1_R_zakleni:=Bit_0;
155:KLIMAT1_vklop_delovanja:=Bit_0;
156:KLIMAT1_vklop_delovanjaR:=Bit_0;
157:KLIMAT2_delovanje:=Bit_0;
158:KLIMAT2_napaka:=Bit_0;
159:KLIMAT2_R_zakleni:=Bit_0;
160:KLIMAT2_vklop_delovanja:=Bit_0;
161:KLIMAT2_vklop_delovanjaR:=Bit_0;
162:KlimeAVTO:=Bit_0;
163:N_F1_1_zascita_ok:=Bit_0;
164:N_KLIMA1_krm_nap_ok:=Bit_0;
165:N_KLIMAT1_napaka:=Bit_0;
166:N_KLIMAT2_napaka:=Bit_0;
167:N_KlimeAVTO:=Bit_0;
168:N_Q12_izpad:=Bit_0;
169:N_UPS_A_V23_delovanje:=Bit_0;
170:N_UPS_A_V23_napaka:=Bit_0;
171:N_UPS_V23_delovanje:=Bit_0;
172:N_UPS_V23_napaka:=Bit_0;
173:N_UPS_V25_delovanje:=Bit_0;
174:N_UPS_V25_napaka:=Bit_0;
175:N_VLAZILEC1_napaka:=Bit_0;
176:N_VLAZILEC2_napaka:=Bit_0;
177:napaka_kom_panel:=Bit_0;
178:napaka_kom_scada:=Bit_0;
179:napaka_kom_scada2:=Bit_0;
180:NapakaSenzorSkupno:=Bit_0;
181:NapakaSenzorVlagaHIA1:=Bit_0;
182:NapakaSenzorVlagaHIA2:=Bit_0;
183:NapakaSenzorVlagaHIA3:=Bit_0;
184:NapakaSenzorVlagaHIA4:=Bit_0;
185:NapakaSenzorVlagaHIA5:=Bit_0;
186:NapakaSenzorVlagaHIA6:=Bit_0;
187:NapakaSenzorVlagaHIA7:=Bit_0;
188:NapakaTSTempTIA1:=Bit_0;
189:NapakaTSTempTIA2:=Bit_0;
190:NapakaTSTempTIA3:=Bit_0;
191:NapakaTSTempTIA4:=Bit_0;
192:NapakaTSTempTIA5:=Bit_0;
193:NapakaTSTempTIA6:=Bit_0;
194:NapakaTSTempTIA7:=Bit_0;
195:OpozoriloPMM2x17med60in80[10]:=Bit_0;
196:OpozoriloPMM2x17med60in80[11]:=Bit_0;
197:OpozoriloPMM2x17med60in80[12]:=Bit_0;
198:OpozoriloPMM2x17med60in80[13]:=Bit_0;
199:OpozoriloPMM2x17med60in80[14]:=Bit_0;
200:OpozoriloPMM2x17med60in80[15]:=Bit_0;
201:OpozoriloPMM2x17med60in80[16]:=Bit_0;
202:OpozoriloPMM2x17med60in80[17]:=Bit_0;
203:OpozoriloPMM2x17med60in80[18]:=Bit_0;
204:OpozoriloPMM2x17med60in80[19]:=Bit_0;
205:OpozoriloPMM2x17med60in80[1]:=Bit_0;
206:OpozoriloPMM2x17med60in80[20]:=Bit_0;
207:OpozoriloPMM2x17med60in80[21]:=Bit_0;
208:OpozoriloPMM2x17med60in80[22]:=Bit_0;
209:OpozoriloPMM2x17med60in80[23]:=Bit_0;
210:OpozoriloPMM2x17med60in80[24]:=Bit_0;
211:OpozoriloPMM2x17med60in80[25]:=Bit_0;
212:OpozoriloPMM2x17med60in80[26]:=Bit_0;
213:OpozoriloPMM2x17med60in80[27]:=Bit_0;
214:OpozoriloPMM2x17med60in80[28]:=Bit_0;
215:OpozoriloPMM2x17med60in80[29]:=Bit_0;
216:OpozoriloPMM2x17med60in80[2]:=Bit_0;
217:OpozoriloPMM2x17med60in80[30]:=Bit_0;
218:OpozoriloPMM2x17med60in80[31]:=Bit_0;
219:OpozoriloPMM2x17med60in80[32]:=Bit_0;
220:OpozoriloPMM2x17med60in80[33]:=Bit_0;
221:OpozoriloPMM2x17med60in80[34]:=Bit_0;
222:OpozoriloPMM2x17med60in80[35]:=Bit_0;
223:OpozoriloPMM2x17med60in80[36]:=Bit_0;
224:OpozoriloPMM2x17med60in80[37]:=Bit_0;
225:OpozoriloPMM2x17med60in80[38]:=Bit_0;
226:OpozoriloPMM2x17med60in80[39]:=Bit_0;
227:OpozoriloPMM2x17med60in80[3]:=Bit_0;
228:OpozoriloPMM2x17med60in80[40]:=Bit_0;
229:OpozoriloPMM2x17med60in80[41]:=Bit_0;
230:OpozoriloPMM2x17med60in80[42]:=Bit_0;
231:OpozoriloPMM2x17med60in80[4]:=Bit_0;
232:OpozoriloPMM2x17med60in80[5]:=Bit_0;
233:OpozoriloPMM2x17med60in80[6]:=Bit_0;
234:OpozoriloPMM2x17med60in80[7]:=Bit_0;
235:OpozoriloPMM2x17med60in80[8]:=Bit_0;
236:OpozoriloPMM2x17med60in80[9]:=Bit_0;
237:PMM1OverCurrentBetw[1]:=Bit_0;
238:PMM1OverCurrentBetw[2]:=Bit_0;
239:PMM1OverCurrentBetw[3]:=Bit_0;
240:PMM1OverCurrentOver[1]:=Bit_0;
241:PMM1OverCurrentOver[2]:=Bit_0;
242:PMM1OverCurrentOver[3]:=Bit_0;
243:PMM2.QA1_GlStik_IZKLOP_IZPAD:=Bit_0;
244:PMM2.QB1_GlStik_IZKLOP_IZPAD:=Bit_0;
245:PMM2.SkNapaka_med60in80:=Bit_0;
246:PMM2.SkNapaka_nad80:=Bit_0;
247:PMM2.SkNapakaVirA_med60in80:=Bit_0;
248:PMM2.SkNapakaVirA_nad80:=Bit_0;
249:PMM2.SkNapakaVirB_med60in80:=Bit_0;
250:PMM2.SkNapakaVirB_nad80:=Bit_0;
251:PMM2.VirA_NapakaOzemljitve:=Bit_0;
252:PMM2.VirB_NapakaOzemljitve:=Bit_0;
253:PozarnaCentrala_skupno:=Bit_0;
254:PrevisokaTemp:=Bit_0;
255:Q0_izkljuceno:=Bit_0;
256:Q0_vkljuceno:=Bit_0;
257:Q12_izkljuceno:=Bit_0;
258:Q12_izpad:=Bit_0;
259:Q12_vkljuceno:=Bit_0;
260:Q21_vkljuceno:=Bit_0;
261:Q22_vkljuceno:=Bit_0;
262:razlitjeLAH1:=Bit_0;
263:razlitjeLAH2:=Bit_0;
264:razlitjeLAH3:=Bit_0;
265:razlitjeLAH4:=Bit_0;
266:SetDateTime:=Bit_0;
267:SetDateTimeDemand:=Bit_0;
268:SetDateTimeError:=Bit_0;
269:SetDateTimeFinished:=Bit_0;
270:SkupneNapakeNaprav_PMM17VirBVirA:=Bit_0;
271:SlabaBaterijaPLC:=Bit_0;
272:TempPovp234Previs:=Bit_0;
273:TempPovp56Previs:=Bit_0;
274:TIA1_previs_temp:=Bit_0;
275:TIA2_previs_temp:=Bit_0;
276:TIA3_previs_temp:=Bit_0;
277:TIA4_previs_temp:=Bit_0;
278:TIA5_previs_temp:=Bit_0;
279:TIA6_previs_temp:=Bit_0;
280:TIA7_previs_temp:=Bit_0;
281:UPS1Errors[10]:=Bit_0;
282:UPS1Errors[11]:=Bit_0;
283:UPS1Errors[12]:=Bit_0;
284:UPS1Errors[13]:=Bit_0;
285:UPS1Errors[14]:=Bit_0;
286:UPS1Errors[15]:=Bit_0;
287:UPS1Errors[16]:=Bit_0;
288:UPS1Errors[17]:=Bit_0;
289:UPS1Errors[18]:=Bit_0;
290:UPS1Errors[19]:=Bit_0;
291:UPS1Errors[1]:=Bit_0;
292:UPS1Errors[20]:=Bit_0;
293:UPS1Errors[21]:=Bit_0;
294:UPS1Errors[22]:=Bit_0;
295:UPS1Errors[23]:=Bit_0;
296:UPS1Errors[24]:=Bit_0;
297:UPS1Errors[25]:=Bit_0;
298:UPS1Errors[2]:=Bit_0;
299:UPS1Errors[3]:=Bit_0;
300:UPS1Errors[4]:=Bit_0;
301:UPS1Errors[5]:=Bit_0;
302:UPS1Errors[6]:=Bit_0;
303:UPS1Errors[7]:=Bit_0;
304:UPS1Errors[8]:=Bit_0;
305:UPS1Errors[9]:=Bit_0;
306:UPS2Errors[10]:=Bit_0;
307:UPS2Errors[11]:=Bit_0;
308:UPS2Errors[12]:=Bit_0;
309:UPS2Errors[13]:=Bit_0;
310:UPS2Errors[14]:=Bit_0;
311:UPS2Errors[15]:=Bit_0;
312:UPS2Errors[16]:=Bit_0;
313:UPS2Errors[17]:=Bit_0;
314:UPS2Errors[18]:=Bit_0;
315:UPS2Errors[19]:=Bit_0;
316:UPS2Errors[1]:=Bit_0;
317:UPS2Errors[20]:=Bit_0;
318:UPS2Errors[21]:=Bit_0;
319:UPS2Errors[22]:=Bit_0;
320:UPS2Errors[23]:=Bit_0;
321:UPS2Errors[24]:=Bit_0;
322:UPS2Errors[25]:=Bit_0;
323:UPS2Errors[2]:=Bit_0;
324:UPS2Errors[3]:=Bit_0;
325:UPS2Errors[4]:=Bit_0;
326:UPS2Errors[5]:=Bit_0;
327:UPS2Errors[6]:=Bit_0;
328:UPS2Errors[7]:=Bit_0;
329:UPS2Errors[8]:=Bit_0;
330:UPS2Errors[9]:=Bit_0;
331:UPS3Errors[10]:=Bit_0;
332:UPS3Errors[11]:=Bit_0;
333:UPS3Errors[12]:=Bit_0;
334:UPS3Errors[13]:=Bit_0;
335:UPS3Errors[14]:=Bit_0;
336:UPS3Errors[15]:=Bit_0;
337:UPS3Errors[16]:=Bit_0;
338:UPS3Errors[17]:=Bit_0;
339:UPS3Errors[18]:=Bit_0;
340:UPS3Errors[19]:=Bit_0;
341:UPS3Errors[1]:=Bit_0;
342:UPS3Errors[20]:=Bit_0;
343:UPS3Errors[21]:=Bit_0;
344:UPS3Errors[22]:=Bit_0;
345:UPS3Errors[23]:=Bit_0;
346:UPS3Errors[24]:=Bit_0;
347:UPS3Errors[25]:=Bit_0;
348:UPS3Errors[2]:=Bit_0;
349:UPS3Errors[3]:=Bit_0;
350:UPS3Errors[4]:=Bit_0;
351:UPS3Errors[5]:=Bit_0;
352:UPS3Errors[6]:=Bit_0;
353:UPS3Errors[7]:=Bit_0;
354:UPS3Errors[8]:=Bit_0;
355:UPS3Errors[9]:=Bit_0;
356:UPS[1].AlarmAwaitingPower:=Bit_0;
357:UPS[1].AlarmBypassBad:=Bit_0;
358:UPS[1].AlarmChargerFailed:=Bit_0;
359:UPS[1].AlarmCommunicationsLost:=Bit_0;
360:UPS[1].AlarmDepletedBattery:=Bit_0;
361:UPS[1].AlarmDiagnosticTestFailed:=Bit_0;
362:UPS[1].AlarmInverterError:=Bit_0;
363:UPS[1].AlarmIzhodOffKotZahtevano:=Bit_0;
364:UPS[1].AlarmIzhodPreobremenjen:=Bit_0;
365:UPS[1].AlarmLowBattery:=Bit_0;
366:UPS[1].AlarmNapakaNaVarovalki:=Bit_0;
367:UPS[1].AlarmNapakaNaVentilatorju:=Bit_0;
368:UPS[1].AlarmOnBattery:=Bit_0;
369:UPS[1].AlarmOnBypass:=Bit_0;
370:UPS[1].AlarmShutdownImminent:=Bit_0;
371:UPS[1].AlarmShutdownPending:=Bit_0;
372:UPS[1].AlarmSlabaBaterija:=Bit_0;
373:UPS[1].AlarmSplosnaNapaka:=Bit_0;
374:UPS[1].AlarmStanjeIzhodaIzvenToleranc:=Bit_0;
375:UPS[1].AlarmStanjeVhodaIzvenToleranc:=Bit_0;
376:UPS[1].AlarmTemperaturaIzvenToleranc:=Bit_0;
377:UPS[1].AlarmTestInProgres:=Bit_0;
378:UPS[1].AlarmUPSIzhodOff:=Bit_0;
379:UPS[1].AlarmUPSOffKotZahtevano:=Bit_0;
380:UPS[1].AlarmUPSSystemOff:=Bit_0;
381:UPS[1].Napaka:=Bit_0;
382:UPS[1].StatusEcomodeAktiven:=Bit_0;
383:UPS[1].StatusInverterIsOn:=Bit_0;
384:UPS[1].StatusStopOperation:=Bit_0;
385:UPS[2].AlarmAwaitingPower:=Bit_0;
386:UPS[2].AlarmBypassBad:=Bit_0;
387:UPS[2].AlarmChargerFailed:=Bit_0;
388:UPS[2].AlarmCommunicationsLost:=Bit_0;
389:UPS[2].AlarmDepletedBattery:=Bit_0;
390:UPS[2].AlarmDiagnosticTestFailed:=Bit_0;
391:UPS[2].AlarmInverterError:=Bit_0;
392:UPS[2].AlarmIzhodOffKotZahtevano:=Bit_0;
393:UPS[2].AlarmIzhodPreobremenjen:=Bit_0;
394:UPS[2].AlarmLowBattery:=Bit_0;
395:UPS[2].AlarmNapakaNaVarovalki:=Bit_0;
396:UPS[2].AlarmNapakaNaVentilatorju:=Bit_0;
397:UPS[2].AlarmOnBattery:=Bit_0;
398:UPS[2].AlarmOnBypass:=Bit_0;
399:UPS[2].AlarmShutdownImminent:=Bit_0;
400:UPS[2].AlarmShutdownPending:=Bit_0;
401:UPS[2].AlarmSlabaBaterija:=Bit_0;
402:UPS[2].AlarmSplosnaNapaka:=Bit_0;
403:UPS[2].AlarmStanjeIzhodaIzvenToleranc:=Bit_0;
404:UPS[2].AlarmStanjeVhodaIzvenToleranc:=Bit_0;
405:UPS[2].AlarmTemperaturaIzvenToleranc:=Bit_0;
406:UPS[2].AlarmTestInProgres:=Bit_0;
407:UPS[2].AlarmUPSIzhodOff:=Bit_0;
408:UPS[2].AlarmUPSOffKotZahtevano:=Bit_0;
409:UPS[2].AlarmUPSSystemOff:=Bit_0;
410:UPS[2].Napaka:=Bit_0;
411:UPS[2].StatusEcomodeAktiven:=Bit_0;
412:UPS[2].StatusInverterIsOn:=Bit_0;
413:UPS[2].StatusStopOperation:=Bit_0;
414:UPS[3].AlarmAwaitingPower:=Bit_0;
415:UPS[3].AlarmBypassBad:=Bit_0;
416:UPS[3].AlarmChargerFailed:=Bit_0;
417:UPS[3].AlarmCommunicationsLost:=Bit_0;
418:UPS[3].AlarmDepletedBattery:=Bit_0;
419:UPS[3].AlarmDiagnosticTestFailed:=Bit_0;
420:UPS[3].AlarmInverterError:=Bit_0;
421:UPS[3].AlarmIzhodOffKotZahtevano:=Bit_0;
422:UPS[3].AlarmIzhodPreobremenjen:=Bit_0;
423:UPS[3].AlarmLowBattery:=Bit_0;
424:UPS[3].AlarmNapakaNaVarovalki:=Bit_0;
425:UPS[3].AlarmNapakaNaVentilatorju:=Bit_0;
426:UPS[3].AlarmOnBattery:=Bit_0;
427:UPS[3].AlarmOnBypass:=Bit_0;
428:UPS[3].AlarmShutdownImminent:=Bit_0;
429:UPS[3].AlarmShutdownPending:=Bit_0;
430:UPS[3].AlarmSlabaBaterija:=Bit_0;
431:UPS[3].AlarmSplosnaNapaka:=Bit_0;
432:UPS[3].AlarmStanjeIzhodaIzvenToleranc:=Bit_0;
433:UPS[3].AlarmStanjeVhodaIzvenToleranc:=Bit_0;
434:UPS[3].AlarmTemperaturaIzvenToleranc:=Bit_0;
435:UPS[3].AlarmTestInProgres:=Bit_0;
436:UPS[3].AlarmUPSIzhodOff:=Bit_0;
437:UPS[3].AlarmUPSOffKotZahtevano:=Bit_0;
438:UPS[3].AlarmUPSSystemOff:=Bit_0;
439:UPS[3].Napaka:=Bit_0;
440:UPS[3].StatusEcomodeAktiven:=Bit_0;
441:UPS[3].StatusInverterIsOn:=Bit_0;
442:UPS[3].StatusStopOperation:=Bit_0;
443:UPS_A_V23_delovanje:=Bit_0;
444:UPS_A_V23_napaka:=Bit_0;
445:ups_alarm:=Bit_0;
446:ups_baterijski_nac:=Bit_0;
447:UPS_MGE[1].BatteryChargedState:=Bit_0;
448:UPS_MGE[1].BatteryCircuitBreaker:=Bit_0;
449:UPS_MGE[1].BatteryCompInProgress:=Bit_0;
450:UPS_MGE[1].BatteryFuseFault:=Bit_0;
451:UPS_MGE[1].BatteryLowWarning:=Bit_0;
452:UPS_MGE[1].BatteryTempOutOfToler:=Bit_0;
453:UPS_MGE[1].BypassInFreeFrequency:=Bit_0;
454:UPS_MGE[1].ChargerGeneralFault:=Bit_0;
455:UPS_MGE[1].DeviceVentilationFault:=Bit_0;
456:UPS_MGE[1].InverterFuseFault:=Bit_0;
457:UPS_MGE[1].InverterOverload:=Bit_0;
458:UPS_MGE[1].InverterThermalOverload:=Bit_0;
459:UPS_MGE[1].Mains1VoltOutOfToler:=Bit_0;
460:UPS_MGE[1].Mains2Overload:=Bit_0;
461:UPS_MGE[1].Mains2VoltOutOfToler:=Bit_0;
462:UPS_MGE[1].MaintenancePosition:=Bit_0;
463:UPS_MGE[1].ManualBypassSwitch:=Bit_0;
464:UPS_MGE[1].NapakaNaVarovalkah:=Bit_0;
465:UPS_MGE[1].OutputInShortCircuit:=Bit_0;
466:UPS_MGE[1].OutputOverload:=Bit_0;
467:UPS_MGE[1].OutputThermalOverload:=Bit_0;
468:UPS_MGE[1].RectifierOn:=Bit_0;
469:UPS_MGE[1].RectifierThermOverload:=Bit_0;
470:UPS_MGE[1].Skupna_napaka:=Bit_0;
471:UPS_MGE[1].UPS_coupled:=Bit_0;
472:UPS_MGE[1].UPS_error:=Bit_0;
473:UPS_MGE[1].UPS_in_backup:=Bit_0;
474:ups_polnjenje:=Bit_0;
475:UPS_V23_delovanje:=Bit_0;
476:UPS_V23_napaka:=Bit_0;
477:UPS_V25_delovanje:=Bit_0;
478:UPS_V25_napaka:=Bit_0;
479:UPSMGEErrors[10]:=Bit_0;
480:UPSMGEErrors[11]:=Bit_0;
481:UPSMGEErrors[12]:=Bit_0;
482:UPSMGEErrors[13]:=Bit_0;
483:UPSMGEErrors[14]:=Bit_0;
484:UPSMGEErrors[15]:=Bit_0;
485:UPSMGEErrors[16]:=Bit_0;
486:UPSMGEErrors[17]:=Bit_0;
487:UPSMGEErrors[1]:=Bit_0;
488:UPSMGEErrors[2]:=Bit_0;
489:UPSMGEErrors[3]:=Bit_0;
490:UPSMGEErrors[4]:=Bit_0;
491:UPSMGEErrors[5]:=Bit_0;
492:UPSMGEErrors[6]:=Bit_0;
493:UPSMGEErrors[7]:=Bit_0;
494:UPSMGEErrors[8]:=Bit_0;
495:UPSMGEErrors[9]:=Bit_0;
496:UserLoggedIn:=Bit_0;
497:VLAZILEC1_delovanje:=Bit_0;
498:VLAZILEC1_napaka:=Bit_0;
499:VLAZILEC2_delovanje:=Bit_0;
500:VLAZILEC2_napaka:=Bit_0;
501:XVH_AlarmOn:=Bit_0;
502:XVH_enopolna_napaka:=Bit_0;
(*BOOL*)
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_dWord : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje LONG*)
(**)
3001:MAX_SOCKET_FD_SETSIZE:=Long_0;
(*Pisanje REAL*)
(**)
4001:Circ[1].CosFi_III:=Real_0;
4003:Circ[1].DelovnaEnergija:=Real_0;
4005:Circ[1].DelovnaEnergija_TEMP:=Real_0;
4007:Circ[1].DelovnaMoc_III:=Real_0;
4009:Circ[1].DelovnaMoc_L1:=Real_0;
4011:Circ[1].DelovnaMoc_L2:=Real_0;
4013:Circ[1].DelovnaMoc_L3:=Real_0;
4015:Circ[1].Frekvenca_L1:=Real_0;
4017:Circ[1].InduktivnaEnergija:=Real_0;
4019:Circ[1].InduktivnaMoc_III:=Real_0;
4021:Circ[1].JalovaMoc_L1:=Real_0;
4023:Circ[1].JalovaMoc_L2:=Real_0;
4025:Circ[1].JalovaMoc_L3:=Real_0;
4027:Circ[1].KapacitivnaEnergija:=Real_0;
4029:Circ[1].KapacitivnaMoc_III:=Real_0;
4031:Circ[1].MaximumDemand:=Real_0;
4033:Circ[1].MaximumDemandA2:=Real_0;
4035:Circ[1].MaximumDemandA3:=Real_0;
4037:Circ[1].Napetost_L1_L2:=Real_0;
4039:Circ[1].Napetost_L1_N:=Real_0;
4041:Circ[1].Napetost_L2_L3:=Real_0;
4043:Circ[1].Napetost_L2_N:=Real_0;
4045:Circ[1].Napetost_L3_L1:=Real_0;
4047:Circ[1].Napetost_L3_N:=Real_0;
4049:Circ[1].NavideznaMoc_III:=Real_0;
4051:Circ[1].NicelniTok:=Real_0;
4053:Circ[1].PowerFactor_III:=Real_0;
4055:Circ[1].PowerFactor_L1:=Real_0;
4057:Circ[1].PowerFactor_L2:=Real_0;
4059:Circ[1].PowerFactor_L3:=Real_0;
4061:Circ[1].RazEner_D:=Real_0;
4063:Circ[1].RazEner_D_SCADA:=Real_0;
4065:Circ[1].RazEner_D_TEMP:=Real_0;
4067:Circ[1].RazEner_M:=Real_0;
4069:Circ[1].RazEner_M_SCADA:=Real_0;
4071:Circ[1].RazEner_M_TEMP:=Real_0;
4073:Circ[1].RazEner_T:=Real_0;
4075:Circ[1].RazEner_T_SCADA:=Real_0;
4077:Circ[1].RazEner_T_TEMP:=Real_0;
4079:Circ[1].THDI_L1:=Real_0;
4081:Circ[1].THDI_L2:=Real_0;
4083:Circ[1].THDI_L3:=Real_0;
4085:Circ[1].THDV_L1:=Real_0;
4087:Circ[1].THDV_L2:=Real_0;
4089:Circ[1].THDV_L3:=Real_0;
4091:Circ[1].Tok_L1:=Real_0;
4093:Circ[1].Tok_L2:=Real_0;
4095:Circ[1].Tok_L3:=Real_0;
4097:Circ[1].TokPovprecje_III:=Real_0;
4099:PMM2.VirA.Current[10]:=Real_0;
4101:PMM2.VirA.Current[11]:=Real_0;
4103:PMM2.VirA.Current[12]:=Real_0;
4105:PMM2.VirA.Current[13]:=Real_0;
4107:PMM2.VirA.Current[14]:=Real_0;
4109:PMM2.VirA.Current[15]:=Real_0;
4111:PMM2.VirA.Current[16]:=Real_0;
4113:PMM2.VirA.Current[17]:=Real_0;
4115:PMM2.VirA.Current[18]:=Real_0;
4117:PMM2.VirA.Current[19]:=Real_0;
4119:PMM2.VirA.Current[1]:=Real_0;
4121:PMM2.VirA.Current[20]:=Real_0;
4123:PMM2.VirA.Current[21]:=Real_0;
4125:PMM2.VirA.Current[22]:=Real_0;
4127:PMM2.VirA.Current[23]:=Real_0;
4129:PMM2.VirA.Current[24]:=Real_0;
4131:PMM2.VirA.Current[25]:=Real_0;
4133:PMM2.VirA.Current[26]:=Real_0;
4135:PMM2.VirA.Current[27]:=Real_0;
4137:PMM2.VirA.Current[28]:=Real_0;
4139:PMM2.VirA.Current[29]:=Real_0;
4141:PMM2.VirA.Current[2]:=Real_0;
4143:PMM2.VirA.Current[30]:=Real_0;
4145:PMM2.VirA.Current[31]:=Real_0;
4147:PMM2.VirA.Current[32]:=Real_0;
4149:PMM2.VirA.Current[33]:=Real_0;
4151:PMM2.VirA.Current[34]:=Real_0;
4153:PMM2.VirA.Current[35]:=Real_0;
4155:PMM2.VirA.Current[36]:=Real_0;
4157:PMM2.VirA.Current[37]:=Real_0;
4159:PMM2.VirA.Current[38]:=Real_0;
4161:PMM2.VirA.Current[39]:=Real_0;
4163:PMM2.VirA.Current[3]:=Real_0;
4165:PMM2.VirA.Current[40]:=Real_0;
4167:PMM2.VirA.Current[41]:=Real_0;
4169:PMM2.VirA.Current[42]:=Real_0;
4171:PMM2.VirA.Current[43]:=Real_0;
4173:PMM2.VirA.Current[44]:=Real_0;
4175:PMM2.VirA.Current[4]:=Real_0;
4177:PMM2.VirA.Current[5]:=Real_0;
4179:PMM2.VirA.Current[6]:=Real_0;
4181:PMM2.VirA.Current[7]:=Real_0;
4183:PMM2.VirA.Current[8]:=Real_0;
4185:PMM2.VirA.Current[9]:=Real_0;
4187:PMM2.VirA_fsys:=Real_0;
4189:PMM2.VirA_Isys:=Real_0;
4191:PMM2.VirA_PFsys:=Real_0;
4193:PMM2.VirA_Psys:=Real_0;
4195:PMM2.VirA_Qsys:=Real_0;
4197:PMM2.VirA_Ssys:=Real_0;
4199:PMM2.VirA_Usys:=Real_0;
4201:PMM2.VirAActiveEnergyConsumed_kWh:=Real_0;
4203:PMM2.VirAActivePowerPhaseA_kW:=Real_0;
4205:PMM2.VirAActivePowerPhaseB_kW:=Real_0;
4207:PMM2.VirAActivePowerPhaseC_kW:=Real_0;
4209:PMM2.VirAAparentPowerPhaseA:=Real_0;
4211:PMM2.VirAAparentPowerPhaseB:=Real_0;
4213:PMM2.VirAAparentPowerPhaseC:=Real_0;
4215:PMM2.VirACurrentInPhaseA_A:=Real_0;
4217:PMM2.VirACurrentInPhaseB_A:=Real_0;
4219:PMM2.VirACurrentInPhaseC_A:=Real_0;
4221:PMM2.VirAReactiveEnergyConsumed_kVARh:=Real_0;
4223:PMM2.VirAReactivePowerPhaseA:=Real_0;
4225:PMM2.VirAReactivePowerPhaseB:=Real_0;
4227:PMM2.VirAReactivePowerPhaseC:=Real_0;
4229:PMM2.VirAVoltageBetweenPhaseAB_V:=Real_0;
4231:PMM2.VirAVoltageBetweenPhaseAN_V:=Real_0;
4233:PMM2.VirAVoltageBetweenPhaseBC_V:=Real_0;
4235:PMM2.VirAVoltageBetweenPhaseBN_V:=Real_0;
4237:PMM2.VirAVoltageBetweenPhaseCA_V:=Real_0;
4239:PMM2.VirAVoltageBetweenPhaseCN_V:=Real_0;
4241:PMM2.VirB.Current[10]:=Real_0;
4243:PMM2.VirB.Current[11]:=Real_0;
4245:PMM2.VirB.Current[12]:=Real_0;
4247:PMM2.VirB.Current[13]:=Real_0;
4249:PMM2.VirB.Current[14]:=Real_0;
4251:PMM2.VirB.Current[15]:=Real_0;
4253:PMM2.VirB.Current[16]:=Real_0;
4255:PMM2.VirB.Current[17]:=Real_0;
4257:PMM2.VirB.Current[18]:=Real_0;
4259:PMM2.VirB.Current[19]:=Real_0;
4261:PMM2.VirB.Current[1]:=Real_0;
4263:PMM2.VirB.Current[20]:=Real_0;
4265:PMM2.VirB.Current[21]:=Real_0;
4267:PMM2.VirB.Current[22]:=Real_0;
4269:PMM2.VirB.Current[23]:=Real_0;
4271:PMM2.VirB.Current[24]:=Real_0;
4273:PMM2.VirB.Current[25]:=Real_0;
4275:PMM2.VirB.Current[26]:=Real_0;
4277:PMM2.VirB.Current[27]:=Real_0;
4279:PMM2.VirB.Current[28]:=Real_0;
4281:PMM2.VirB.Current[29]:=Real_0;
4283:PMM2.VirB.Current[2]:=Real_0;
4285:PMM2.VirB.Current[30]:=Real_0;
4287:PMM2.VirB.Current[31]:=Real_0;
4289:PMM2.VirB.Current[32]:=Real_0;
4291:PMM2.VirB.Current[33]:=Real_0;
4293:PMM2.VirB.Current[34]:=Real_0;
4295:PMM2.VirB.Current[35]:=Real_0;
4297:PMM2.VirB.Current[36]:=Real_0;
4299:PMM2.VirB.Current[37]:=Real_0;
4301:PMM2.VirB.Current[38]:=Real_0;
4303:PMM2.VirB.Current[39]:=Real_0;
4305:PMM2.VirB.Current[3]:=Real_0;
4307:PMM2.VirB.Current[40]:=Real_0;
4309:PMM2.VirB.Current[41]:=Real_0;
4311:PMM2.VirB.Current[42]:=Real_0;
4313:PMM2.VirB.Current[43]:=Real_0;
4315:PMM2.VirB.Current[44]:=Real_0;
4317:PMM2.VirB.Current[4]:=Real_0;
4319:PMM2.VirB.Current[5]:=Real_0;
4321:PMM2.VirB.Current[6]:=Real_0;
4323:PMM2.VirB.Current[7]:=Real_0;
4325:PMM2.VirB.Current[8]:=Real_0;
4327:PMM2.VirB.Current[9]:=Real_0;
4329:PMM2.VirB_fsys:=Real_0;
4331:PMM2.VirB_Isys:=Real_0;
4333:PMM2.VirB_PFsys:=Real_0;
4335:PMM2.VirB_Psys:=Real_0;
4337:PMM2.VirB_Qsys:=Real_0;
4339:PMM2.VirB_Ssys:=Real_0;
4341:PMM2.VirB_Usys:=Real_0;
4343:PMM2.VirBActiveEnergyConsumed_kWh:=Real_0;
4345:PMM2.VirBActivePowerPhaseA_kW:=Real_0;
4347:PMM2.VirBActivePowerPhaseB_kW:=Real_0;
4349:PMM2.VirBActivePowerPhaseC_kW:=Real_0;
4351:PMM2.VirBAparentPowerPhaseA:=Real_0;
4353:PMM2.VirBAparentPowerPhaseB:=Real_0;
4355:PMM2.VirBAparentPowerPhaseC:=Real_0;
4357:PMM2.VirBCurrentInPhaseA_A:=Real_0;
4359:PMM2.VirBCurrentInPhaseB_A:=Real_0;
4361:PMM2.VirBCurrentInPhaseC_A:=Real_0;
4363:PMM2.VirBReactiveEnergyConsumed_kVARh:=Real_0;
4365:PMM2.VirBReactivePowerPhaseA:=Real_0;
4367:PMM2.VirBReactivePowerPhaseB:=Real_0;
4369:PMM2.VirBReactivePowerPhaseC:=Real_0;
4371:PMM2.VirBVoltageBetweenPhaseAB_V:=Real_0;
4373:PMM2.VirBVoltageBetweenPhaseAN_V:=Real_0;
4375:PMM2.VirBVoltageBetweenPhaseBC_V:=Real_0;
4377:PMM2.VirBVoltageBetweenPhaseBN_V:=Real_0;
4379:PMM2.VirBVoltageBetweenPhaseCA_V:=Real_0;
4381:PMM2.VirBVoltageBetweenPhaseCN_V:=Real_0;
4383:PMM[1].ActiveEnergyConsumed_kWh:=Real_0;
4385:PMM[1].ActivePowerPhaseA_kW:=Real_0;
4387:PMM[1].ActivePowerPhaseB_kW:=Real_0;
4389:PMM[1].ActivePowerPhaseC_kW:=Real_0;
4391:PMM[1].AparentPowerPhaseA:=Real_0;
4393:PMM[1].AparentPowerPhaseB:=Real_0;
4395:PMM[1].AparentPowerPhaseC:=Real_0;
4397:PMM[1].AverageCurrent_A:=Real_0;
4399:PMM[1].AveragePhaseToNeutral_V:=Real_0;
4401:PMM[1].AveragePhaseToPhase_V:=Real_0;
4403:PMM[1].CurrentInPhaseA_A:=Real_0;
4405:PMM[1].CurrentInPhaseB_A:=Real_0;
4407:PMM[1].CurrentInPhaseC_A:=Real_0;
4409:PMM[1].Frequency_Hz:=Real_0;
4411:PMM[1].Phase[1].Current[10]:=Real_0;
4413:PMM[1].Phase[1].Current[11]:=Real_0;
4415:PMM[1].Phase[1].Current[12]:=Real_0;
4417:PMM[1].Phase[1].Current[13]:=Real_0;
4419:PMM[1].Phase[1].Current[14]:=Real_0;
4421:PMM[1].Phase[1].Current[15]:=Real_0;
4423:PMM[1].Phase[1].Current[16]:=Real_0;
4425:PMM[1].Phase[1].Current[17]:=Real_0;
4427:PMM[1].Phase[1].Current[18]:=Real_0;
4429:PMM[1].Phase[1].Current[19]:=Real_0;
4431:PMM[1].Phase[1].Current[1]:=Real_0;
4433:PMM[1].Phase[1].Current[20]:=Real_0;
4435:PMM[1].Phase[1].Current[21]:=Real_0;
4437:PMM[1].Phase[1].Current[22]:=Real_0;
4439:PMM[1].Phase[1].Current[23]:=Real_0;
4441:PMM[1].Phase[1].Current[24]:=Real_0;
4443:PMM[1].Phase[1].Current[25]:=Real_0;
4445:PMM[1].Phase[1].Current[26]:=Real_0;
4447:PMM[1].Phase[1].Current[27]:=Real_0;
4449:PMM[1].Phase[1].Current[28]:=Real_0;
4451:PMM[1].Phase[1].Current[29]:=Real_0;
4453:PMM[1].Phase[1].Current[2]:=Real_0;
4455:PMM[1].Phase[1].Current[30]:=Real_0;
4457:PMM[1].Phase[1].Current[31]:=Real_0;
4459:PMM[1].Phase[1].Current[32]:=Real_0;
4461:PMM[1].Phase[1].Current[33]:=Real_0;
4463:PMM[1].Phase[1].Current[34]:=Real_0;
4465:PMM[1].Phase[1].Current[35]:=Real_0;
4467:PMM[1].Phase[1].Current[36]:=Real_0;
4469:PMM[1].Phase[1].Current[37]:=Real_0;
4471:PMM[1].Phase[1].Current[38]:=Real_0;
4473:PMM[1].Phase[1].Current[39]:=Real_0;
4475:PMM[1].Phase[1].Current[3]:=Real_0;
4477:PMM[1].Phase[1].Current[40]:=Real_0;
4479:PMM[1].Phase[1].Current[41]:=Real_0;
4481:PMM[1].Phase[1].Current[42]:=Real_0;
4483:PMM[1].Phase[1].Current[4]:=Real_0;
4485:PMM[1].Phase[1].Current[5]:=Real_0;
4487:PMM[1].Phase[1].Current[6]:=Real_0;
4489:PMM[1].Phase[1].Current[7]:=Real_0;
4491:PMM[1].Phase[1].Current[8]:=Real_0;
4493:PMM[1].Phase[1].Current[9]:=Real_0;
4495:PMM[1].Phase[2].Current[10]:=Real_0;
4497:PMM[1].Phase[2].Current[11]:=Real_0;
4499:PMM[1].Phase[2].Current[12]:=Real_0;
4501:PMM[1].Phase[2].Current[13]:=Real_0;
4503:PMM[1].Phase[2].Current[14]:=Real_0;
4505:PMM[1].Phase[2].Current[15]:=Real_0;
4507:PMM[1].Phase[2].Current[16]:=Real_0;
4509:PMM[1].Phase[2].Current[17]:=Real_0;
4511:PMM[1].Phase[2].Current[18]:=Real_0;
4513:PMM[1].Phase[2].Current[19]:=Real_0;
4515:PMM[1].Phase[2].Current[1]:=Real_0;
4517:PMM[1].Phase[2].Current[20]:=Real_0;
4519:PMM[1].Phase[2].Current[21]:=Real_0;
4521:PMM[1].Phase[2].Current[22]:=Real_0;
4523:PMM[1].Phase[2].Current[23]:=Real_0;
4525:PMM[1].Phase[2].Current[24]:=Real_0;
4527:PMM[1].Phase[2].Current[25]:=Real_0;
4529:PMM[1].Phase[2].Current[26]:=Real_0;
4531:PMM[1].Phase[2].Current[27]:=Real_0;
4533:PMM[1].Phase[2].Current[28]:=Real_0;
4535:PMM[1].Phase[2].Current[29]:=Real_0;
4537:PMM[1].Phase[2].Current[2]:=Real_0;
4539:PMM[1].Phase[2].Current[30]:=Real_0;
4541:PMM[1].Phase[2].Current[31]:=Real_0;
4543:PMM[1].Phase[2].Current[32]:=Real_0;
4545:PMM[1].Phase[2].Current[33]:=Real_0;
4547:PMM[1].Phase[2].Current[34]:=Real_0;
4549:PMM[1].Phase[2].Current[35]:=Real_0;
4551:PMM[1].Phase[2].Current[36]:=Real_0;
4553:PMM[1].Phase[2].Current[37]:=Real_0;
4555:PMM[1].Phase[2].Current[38]:=Real_0;
4557:PMM[1].Phase[2].Current[39]:=Real_0;
4559:PMM[1].Phase[2].Current[3]:=Real_0;
4561:PMM[1].Phase[2].Current[40]:=Real_0;
4563:PMM[1].Phase[2].Current[41]:=Real_0;
4565:PMM[1].Phase[2].Current[42]:=Real_0;
4567:PMM[1].Phase[2].Current[4]:=Real_0;
4569:PMM[1].Phase[2].Current[5]:=Real_0;
4571:PMM[1].Phase[2].Current[6]:=Real_0;
4573:PMM[1].Phase[2].Current[7]:=Real_0;
4575:PMM[1].Phase[2].Current[8]:=Real_0;
4577:PMM[1].Phase[2].Current[9]:=Real_0;
4579:PMM[1].Phase[3].Current[10]:=Real_0;
4581:PMM[1].Phase[3].Current[11]:=Real_0;
4583:PMM[1].Phase[3].Current[12]:=Real_0;
4585:PMM[1].Phase[3].Current[13]:=Real_0;
4587:PMM[1].Phase[3].Current[14]:=Real_0;
4589:PMM[1].Phase[3].Current[15]:=Real_0;
4591:PMM[1].Phase[3].Current[16]:=Real_0;
4593:PMM[1].Phase[3].Current[17]:=Real_0;
4595:PMM[1].Phase[3].Current[18]:=Real_0;
4597:PMM[1].Phase[3].Current[19]:=Real_0;
4599:PMM[1].Phase[3].Current[1]:=Real_0;
4601:PMM[1].Phase[3].Current[20]:=Real_0;
4603:PMM[1].Phase[3].Current[21]:=Real_0;
4605:PMM[1].Phase[3].Current[22]:=Real_0;
4607:PMM[1].Phase[3].Current[23]:=Real_0;
4609:PMM[1].Phase[3].Current[24]:=Real_0;
4611:PMM[1].Phase[3].Current[25]:=Real_0;
4613:PMM[1].Phase[3].Current[26]:=Real_0;
4615:PMM[1].Phase[3].Current[27]:=Real_0;
4617:PMM[1].Phase[3].Current[28]:=Real_0;
4619:PMM[1].Phase[3].Current[29]:=Real_0;
4621:PMM[1].Phase[3].Current[2]:=Real_0;
4623:PMM[1].Phase[3].Current[30]:=Real_0;
4625:PMM[1].Phase[3].Current[31]:=Real_0;
4627:PMM[1].Phase[3].Current[32]:=Real_0;
4629:PMM[1].Phase[3].Current[33]:=Real_0;
4631:PMM[1].Phase[3].Current[34]:=Real_0;
4633:PMM[1].Phase[3].Current[35]:=Real_0;
4635:PMM[1].Phase[3].Current[36]:=Real_0;
4637:PMM[1].Phase[3].Current[37]:=Real_0;
4639:PMM[1].Phase[3].Current[38]:=Real_0;
4641:PMM[1].Phase[3].Current[39]:=Real_0;
4643:PMM[1].Phase[3].Current[3]:=Real_0;
4645:PMM[1].Phase[3].Current[40]:=Real_0;
4647:PMM[1].Phase[3].Current[41]:=Real_0;
4649:PMM[1].Phase[3].Current[42]:=Real_0;
4651:PMM[1].Phase[3].Current[4]:=Real_0;
4653:PMM[1].Phase[3].Current[5]:=Real_0;
4655:PMM[1].Phase[3].Current[6]:=Real_0;
4657:PMM[1].Phase[3].Current[7]:=Real_0;
4659:PMM[1].Phase[3].Current[8]:=Real_0;
4661:PMM[1].Phase[3].Current[9]:=Real_0;
4663:PMM[1].PowerFactorSys:=Real_0;
4665:PMM[1].ReactiveEnergyConsumed_kVARh:=Real_0;
4667:PMM[1].ReactivePowerPhaseA:=Real_0;
4669:PMM[1].ReactivePowerPhaseB:=Real_0;
4671:PMM[1].ReactivePowerPhaseC:=Real_0;
4673:PMM[1].TotalActivePower_kW:=Real_0;
4675:PMM[1].TotalAparentPower_kVA:=Real_0;
4677:PMM[1].TotalPowerFactor:=Real_0;
4679:PMM[1].TotalReactivePower_kVAR:=Real_0;
4681:PMM[1].VirA_fsys:=Real_0;
4683:PMM[1].VirA_Isys:=Real_0;
4685:PMM[1].VirA_PFsys:=Real_0;
4687:PMM[1].VirA_Psys:=Real_0;
4689:PMM[1].VirA_Qsys:=Real_0;
4691:PMM[1].VirA_Ssys:=Real_0;
4693:PMM[1].VirA_Usys:=Real_0;
4695:PMM[1].VirB_fsys:=Real_0;
4697:PMM[1].VirB_Isys:=Real_0;
4699:PMM[1].VirB_PFsys:=Real_0;
4701:PMM[1].VirB_Psys:=Real_0;
4703:PMM[1].VirB_Qsys:=Real_0;
4705:PMM[1].VirB_Ssys:=Real_0;
4707:PMM[1].VirB_Usys:=Real_0;
4709:PMM[1].VirBActiveEnergyConsumed_kWh:=Real_0;
4711:PMM[1].VirBActivePowerPhaseA_kW:=Real_0;
4713:PMM[1].VirBActivePowerPhaseB_kW:=Real_0;
4715:PMM[1].VirBActivePowerPhaseC_kW:=Real_0;
4717:PMM[1].VirBAparentPowerPhaseA:=Real_0;
4719:PMM[1].VirBAparentPowerPhaseB:=Real_0;
4721:PMM[1].VirBAparentPowerPhaseC:=Real_0;
4723:PMM[1].VirBAverageCurrent_A:=Real_0;
4725:PMM[1].VirBAveragePhaseToNeutral_V:=Real_0;
4727:PMM[1].VirBAveragePhaseToPhase_V:=Real_0;
4729:PMM[1].VirBCurrentInPhaseA_A:=Real_0;
4731:PMM[1].VirBCurrentInPhaseB_A:=Real_0;
4733:PMM[1].VirBCurrentInPhaseC_A:=Real_0;
4735:PMM[1].VirBFrequency_Hz:=Real_0;
4737:PMM[1].VirBPowerFactorSys:=Real_0;
4739:PMM[1].VirBReactiveEnergyConsumed_kVARh:=Real_0;
4741:PMM[1].VirBReactivePowerPhaseA:=Real_0;
4743:PMM[1].VirBReactivePowerPhaseB:=Real_0;
4745:PMM[1].VirBReactivePowerPhaseC:=Real_0;
4747:PMM[1].VirBTotalActivePower_kW:=Real_0;
4749:PMM[1].VirBTotalAparentPower_kVA:=Real_0;
4751:PMM[1].VirBTotalPowerFactor:=Real_0;
4753:PMM[1].VirBTotalReactivePower_kVAR:=Real_0;
4755:PMM[1].VirBVoltageBetweenPhaseAB_V:=Real_0;
4757:PMM[1].VirBVoltageBetweenPhaseAN_V:=Real_0;
4759:PMM[1].VirBVoltageBetweenPhaseBC_V:=Real_0;
4761:PMM[1].VirBVoltageBetweenPhaseBN_V:=Real_0;
4763:PMM[1].VirBVoltageBetweenPhaseCA_V:=Real_0;
4765:PMM[1].VirBVoltageBetweenPhaseCN_V:=Real_0;
4767:PMM[1].VoltageBetweenPhaseAB_V:=Real_0;
4769:PMM[1].VoltageBetweenPhaseAN_V:=Real_0;
4771:PMM[1].VoltageBetweenPhaseBC_V:=Real_0;
4773:PMM[1].VoltageBetweenPhaseBN_V:=Real_0;
4775:PMM[1].VoltageBetweenPhaseCA_V:=Real_0;
4777:PMM[1].VoltageBetweenPhaseCN_V:=Real_0;
4779:PMMfaza01:=Real_0;
4781:PMMfaza02:=Real_0;
4783:PMMfaza03:=Real_0;
4785:PMMfaza04:=Real_0;
4787:PMMfaza05:=Real_0;
4789:PMMfaza06:=Real_0;
4791:PMMfaza07:=Real_0;
4793:PMMfaza08:=Real_0;
4795:PMMfaza09:=Real_0;
4797:PMMfaza10:=Real_0;
4799:PMMfaza11:=Real_0;
4801:PMMfaza12:=Real_0;
4803:PMMfaza13:=Real_0;
4805:PMMfaza14:=Real_0;
4807:PMMfaza15:=Real_0;
4809:PMMfaza16:=Real_0;
4811:PMMfaza17:=Real_0;
4813:PMMfaza18:=Real_0;
4815:PMMfaza19:=Real_0;
4817:PMMfaza20:=Real_0;
4819:PMMfaza21:=Real_0;
4821:PMMfaza22:=Real_0;
4823:PMMfaza23:=Real_0;
4825:PMMfaza24:=Real_0;
4827:PMMfaza25:=Real_0;
4829:PMMfaza26:=Real_0;
4831:PMMfaza27:=Real_0;
4833:PMMfaza28:=Real_0;
4835:PMMfaza29:=Real_0;
4837:PMMfaza30:=Real_0;
4839:PMMfaza31:=Real_0;
4841:PMMfaza32:=Real_0;
4843:PMMfaza33:=Real_0;
4845:PMMfaza34:=Real_0;
4847:PMMfaza35:=Real_0;
4849:PMMfaza36:=Real_0;
4851:PMMfaza37:=Real_0;
4853:PMMfaza38:=Real_0;
4855:PMMfaza39:=Real_0;
4857:PMMfaza40:=Real_0;
4859:PMMfaza41:=Real_0;
4861:PMMfaza42:=Real_0;
4863:PMMskupniTokA:=Real_0;
4865:PMMskupniTokB:=Real_0;
4867:UPS[1].EstimatedChargeRemaining:=Real_0;
4869:UPS[1].EstimatedMinutesRemaining:=Real_0;
4871:UPS[1].IzhodMocL1:=Real_0;
4873:UPS[1].IzhodMocL2:=Real_0;
4875:UPS[1].IzhodMocL3:=Real_0;
4877:UPS[1].NapetostBaterije:=Real_0;
4879:UPS[1].TemperaturaBaterije:=Real_0;
4881:UPS[1].VhodFrekvencaL1:=Real_0;
4883:UPS[1].VhodFrekvencaL2:=Real_0;
4885:UPS[1].VhodFrekvencaL3:=Real_0;
4887:UPS[1].VhodNapetostL1:=Real_0;
4889:UPS[1].VhodNapetostL2:=Real_0;
4891:UPS[1].VhodNapetostL3:=Real_0;
4893:UPS[2].EstimatedChargeRemaining:=Real_0;
4895:UPS[2].EstimatedMinutesRemaining:=Real_0;
4897:UPS[2].IzhodMocL1:=Real_0;
4899:UPS[2].IzhodMocL2:=Real_0;
4901:UPS[2].IzhodMocL3:=Real_0;
4903:UPS[2].NapetostBaterije:=Real_0;
4905:UPS[2].TemperaturaBaterije:=Real_0;
4907:UPS[2].VhodFrekvencaL1:=Real_0;
4909:UPS[2].VhodFrekvencaL2:=Real_0;
4911:UPS[2].VhodFrekvencaL3:=Real_0;
4913:UPS[2].VhodNapetostL1:=Real_0;
4915:UPS[2].VhodNapetostL2:=Real_0;
4917:UPS[2].VhodNapetostL3:=Real_0;
4919:UPS[3].EstimatedChargeRemaining:=Real_0;
4921:UPS[3].EstimatedMinutesRemaining:=Real_0;
4923:UPS[3].IzhodMocL1:=Real_0;
4925:UPS[3].IzhodMocL2:=Real_0;
4927:UPS[3].IzhodMocL3:=Real_0;
4929:UPS[3].NapetostBaterije:=Real_0;
4931:UPS[3].TemperaturaBaterije:=Real_0;
4933:UPS[3].VhodFrekvencaL1:=Real_0;
4935:UPS[3].VhodFrekvencaL2:=Real_0;
4937:UPS[3].VhodFrekvencaL3:=Real_0;
4939:UPS[3].VhodNapetostL1:=Real_0;
4941:UPS[3].VhodNapetostL2:=Real_0;
4943:UPS[3].VhodNapetostL3:=Real_0;
(*Pisanje ULONG*)
(**)
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_String : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje STRING*)
(**)
5000:cas_modbus_izpad:=String_0;
5015:Date_Time[0]:=String_0;
5030:Date_Time[1]:=String_0;
5045:Date_Time[2]:=String_0;
5060:Date_Time[3]:=String_0;
5075:K1obrat_ure:=String_0;
5090:UserCurrentName:=String_0;
5105:UserDisplay:=String_0;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION mod_Write_Word : BOOL
VAR_INPUT
Index:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
(*vpis iz scade*)
CASE index OF
(*Pisanje INT*)
(**)
0:DateTime.Dan:=Byte_0;
1:DateTime.Leto:=Byte_0;
2:DateTime.Leto2:=Word_01;
3:DateTime.Mesec:=Byte_0;
4:DateTime.Minuta:=Byte_0;
5:DateTime.PLC_Dan:=Byte_0;
6:DateTime.PLC_DanVTednu:=Byte_0;
7:DateTime.PLC_Leto:=Byte_0;
8:DateTime.PLC_Mesec:=Byte_0;
9:DateTime.PLC_Minuta:=Byte_0;
10:DateTime.PLC_Sekunda:=Byte_0;
11:DateTime.PLC_Ura:=Byte_0;
12:DateTime.Sekunda:=Byte_0;
13:DateTime.Ura:=Byte_0;
14:HIA1_vlaga_s:=Word_01;
15:HIA2_vlaga_s:=Word_01;
16:HIA3_vlaga_s:=Word_01;
17:HIA4_vlaga_s:=Word_01;
18:HIA5_vlaga_s:=Word_01;
19:HIA6_vlaga_s:=Word_01;
20:HIA7_vlaga_s:=Word_01;
21:Klima[1].Analog_izh_mesanje:=Word_01;
22:Klima[1].Analog_izh_rekuperator:=Word_01;
23:Klima[1].Analog_izh_VentGrelnika:=Word_01;
24:Klima[1].Analog_izh_VentHlajenja:=Word_01;
25:Klima[1].Dejanska_zel_temp:=Word_01;
26:Klima[1].Hitrost_del_vent_disp:=Word_01;
27:Klima[1].Max_vpih:=Word_01;
28:Klima[1].Min_vpih:=Word_01;
29:Klima[1].Obrat_ure_Vent_h1:=Word_01;
30:Klima[1].Obrat_ure_Vent_h2:=Word_01;
31:Klima[1].Pol_komp_konec:=Word_01;
32:Klima[1].Pol_komp_sprem_zel_vr:=Word_01;
33:Klima[1].Pol_komp_zacetek:=Word_01;
34:Klima[1].PreklopHitDelVent:=Word_01;
35:Klima[1].Protizamrz_zascita:=Word_01;
36:Klima[1].Rezim_delovanja:=Word_01;
37:Klima[1].Temperatura_dovoda:=Word_01;
38:Klima[1].Temperatura_prostora:=Word_01;
39:Klima[1].TempPredPloscnimRekup:=Word_01;
40:Klima[1].TempZaPloscnimRekup:=Word_01;
41:Klima[1].Vlaga_v_prostoru:=Word_01;
42:Klima[1].VlagaVstopZrakaProstor:=Word_01;
43:Klima[1].Zel_temp_eko_gretja:=Word_01;
44:Klima[1].Zel_temp_eko_hlajenja:=Word_01;
45:Klima[1].Zel_temp_komf_gretja:=Word_01;
46:Klima[1].Zel_temp_komf_hlajenja:=Word_01;
47:Klima[1].Zim_komp_konec:=Word_01;
48:Klima[1].Zim_komp_sprem_zel_vr:=Word_01;
49:Klima[1].Zim_komp_zacetek:=Word_01;
50:Klima[1].ZimKompMinVpihKonec:=Word_01;
51:Klima[1].ZimKompMinVpihZac:=Word_01;
52:Klima[1].ZkompMinVpihSpremZelVr:=Word_01;
53:Klima[1].Zunanja_temp:=Word_01;
54:Klima[2].Analog_izh_mesanje:=Word_01;
55:Klima[2].Analog_izh_rekuperator:=Word_01;
56:Klima[2].Analog_izh_VentGrelnika:=Word_01;
57:Klima[2].Analog_izh_VentHlajenja:=Word_01;
58:Klima[2].Dejanska_zel_temp:=Word_01;
59:Klima[2].Hitrost_del_vent_disp:=Word_01;
60:Klima[2].Max_vpih:=Word_01;
61:Klima[2].Min_vpih:=Word_01;
62:Klima[2].Obrat_ure_Vent_h1:=Word_01;
63:Klima[2].Obrat_ure_Vent_h2:=Word_01;
64:Klima[2].Pol_komp_konec:=Word_01;
65:Klima[2].Pol_komp_sprem_zel_vr:=Word_01;
66:Klima[2].Pol_komp_zacetek:=Word_01;
67:Klima[2].PreklopHitDelVent:=Word_01;
68:Klima[2].Protizamrz_zascita:=Word_01;
69:Klima[2].Rezim_delovanja:=Word_01;
70:Klima[2].Temperatura_dovoda:=Word_01;
71:Klima[2].Temperatura_prostora:=Word_01;
72:Klima[2].TempPredPloscnimRekup:=Word_01;
73:Klima[2].TempZaPloscnimRekup:=Word_01;
74:Klima[2].Vlaga_v_prostoru:=Word_01;
75:Klima[2].VlagaVstopZrakaProstor:=Word_01;
76:Klima[2].Zel_temp_eko_gretja:=Word_01;
77:Klima[2].Zel_temp_eko_hlajenja:=Word_01;
78:Klima[2].Zel_temp_komf_gretja:=Word_01;
79:Klima[2].Zel_temp_komf_hlajenja:=Word_01;
80:Klima[2].Zim_komp_konec:=Word_01;
81:Klima[2].Zim_komp_sprem_zel_vr:=Word_01;
82:Klima[2].Zim_komp_zacetek:=Word_01;
83:Klima[2].ZimKompMinVpihKonec:=Word_01;
84:Klima[2].ZimKompMinVpihZac:=Word_01;
85:Klima[2].ZkompMinVpihSpremZelVr:=Word_01;
86:Klima[2].Zunanja_temp:=Word_01;
87:KlimaIzklopObrUre:=Word_01;
88:Klime_vklopi_n:=Word_01;
89:kom_nast_cas_izpada:=Word_01;
90:PMM[1].AlarmPhase[1].GlobalAlarmReg:=Word_01;
91:PMM[1].AlarmPhase[2].GlobalAlarmReg:=Word_01;
92:PMM[1].AlarmPhase[3].GlobalAlarmReg:=Word_01;
93:Q12stanje:=Byte_0;
94:TempHistereza:=Word_01;
95:TempPovp234:=Word_01;
96:TempPovp234Alarm:=Word_01;
97:TempPovp56:=Word_01;
98:TempPovp56Alarm:=Word_01;
99:TempZaVklopKlim1:=Word_01;
100:TempZaVklopKlim2:=Word_01;
101:TIA1_alarm:=Word_01;
102:TIA1_temp_s:=Word_01;
103:TIA2_alarm:=Word_01;
104:TIA2_temp_s:=Word_01;
105:TIA3_alarm:=Word_01;
106:TIA3_temp_s:=Word_01;
107:TIA4_alarm:=Word_01;
108:TIA4_temp_s:=Word_01;
109:TIA5_alarm:=Word_01;
110:TIA5_temp_s:=Word_01;
111:TIA6_alarm:=Word_01;
112:TIA6_temp_s:=Word_01;
113:TIA7_alarm:=Word_01;
114:TIA7_temp_s:=Word_01;
115:UPS[1].InverterStatus:=Word_01;
116:UPS[1].OutputStatus:=Word_01;
117:UPS[1].SteviloIzpadovVhodneLinije:=Word_01;
118:UPS[1].UnitStatus:=Word_01;
119:UPS[2].InverterStatus:=Word_01;
120:UPS[2].OutputStatus:=Word_01;
121:UPS[2].SteviloIzpadovVhodneLinije:=Word_01;
122:UPS[2].UnitStatus:=Word_01;
123:UPS[3].InverterStatus:=Word_01;
124:UPS[3].OutputStatus:=Word_01;
125:UPS[3].SteviloIzpadovVhodneLinije:=Word_01;
126:UPS[3].UnitStatus:=Word_01;
127:UPS_MGE[1].BatteryBackupTime:=Word_01;
128:UPS_MGE[1].BatteryChargingLevel:=Word_01;
129:UPS_MGE[1].BatteryRechargeDuration:=Word_01;
130:UPS_MGE[1].I1output:=Word_01;
131:UPS_MGE[1].I2output:=Word_01;
132:UPS_MGE[1].I3output:=Word_01;
133:UPS_MGE[1].InverterFrequency:=Word_01;
134:UPS_MGE[1].OutputActivePower1:=Word_01;
135:UPS_MGE[1].OutputActivePower2:=Word_01;
136:UPS_MGE[1].OutputActivePower3:=Word_01;
137:UPS_MGE[1].OutputFrequency:=Word_01;
138:UPS_MGE[1].OutputLoadLevel:=Word_01;
139:UPS_MGE[1].StatusBaterije:=Byte_0;
140:UPS_MGE[1].U12mains1:=Word_01;
141:UPS_MGE[1].U12mains2:=Word_01;
142:UPS_MGE[1].U1N_inverter:=Word_01;
143:UPS_MGE[1].U1N_output:=Word_01;
144:UPS_MGE[1].U23mains1:=Word_01;
145:UPS_MGE[1].U23mains2:=Word_01;
146:UPS_MGE[1].U2N_inverter:=Word_01;
147:UPS_MGE[1].U2N_output:=Word_01;
148:UPS_MGE[1].U31mains1:=Word_01;
149:UPS_MGE[1].U31mains2:=Word_01;
150:UPS_MGE[1].U3N_inverter:=Word_01;
151:UPS_MGE[1].U3N_output:=Word_01;
152:UPS_MGE[1].U_battery:=Word_01;
153:UserCurrentLevel:=Byte_0;
(*Pisanje UINT*)
(**)
6000:K1_obr_u_skupno:=Word_01;
6001:K2_obr_u_skupno:=Word_01;
6002:PMM2.VirAAlarmPhase.C01_16_60to80:=Word_01;
6003:PMM2.VirAAlarmPhase.C01_16_over80:=Word_01;
6004:PMM2.VirAAlarmPhase.C17_32_60to80:=Word_01;
6005:PMM2.VirAAlarmPhase.C17_32_over80:=Word_01;
6006:PMM2.VirAAlarmPhase.C33_44_60to80:=Word_01;
6007:PMM2.VirAAlarmPhase.C33_44_over80:=Word_01;
6008:PMM2.VirBAlarmPhase.C01_16_60to80:=Word_01;
6009:PMM2.VirBAlarmPhase.C01_16_over80:=Word_01;
6010:PMM2.VirBAlarmPhase.C17_32_60to80:=Word_01;
6011:PMM2.VirBAlarmPhase.C17_32_over80:=Word_01;
6012:PMM2.VirBAlarmPhase.C33_44_60to80:=Word_01;
6013:PMM2.VirBAlarmPhase.C33_44_over80:=Word_01;
6014:PMM[1].AlarmPhase[1].C01_16_60to80:=Word_01;
6015:PMM[1].AlarmPhase[1].C01_16_over80:=Word_01;
6016:PMM[1].AlarmPhase[1].C17_32_60to80:=Word_01;
6017:PMM[1].AlarmPhase[1].C17_32_over80:=Word_01;
6018:PMM[1].AlarmPhase[1].C33_42_60to80:=Word_01;
6019:PMM[1].AlarmPhase[1].C33_42_over80:=Word_01;
6020:PMM[1].AlarmPhase[2].C01_16_60to80:=Word_01;
6021:PMM[1].AlarmPhase[2].C01_16_over80:=Word_01;
6022:PMM[1].AlarmPhase[2].C17_32_60to80:=Word_01;
6023:PMM[1].AlarmPhase[2].C17_32_over80:=Word_01;
6024:PMM[1].AlarmPhase[2].C33_42_60to80:=Word_01;
6025:PMM[1].AlarmPhase[2].C33_42_over80:=Word_01;
6026:PMM[1].AlarmPhase[3].C01_16_60to80:=Word_01;
6027:PMM[1].AlarmPhase[3].C01_16_over80:=Word_01;
6028:PMM[1].AlarmPhase[3].C17_32_60to80:=Word_01;
6029:PMM[1].AlarmPhase[3].C17_32_over80:=Word_01;
6030:PMM[1].AlarmPhase[3].C33_42_60to80:=Word_01;
6031:PMM[1].AlarmPhase[3].C33_42_over80:=Word_01;
6032:UPS1_StatusBaterije:=Word_01;
6033:UPS2_StatusBaterije:=Word_01;
6034:UPS3_StatusBaterije:=Word_01;
6035:UPS[1].StatusBaterije:=Word_01;
6036:UPS[2].StatusBaterije:=Word_01;
6037:UPS[3].StatusBaterije:=Word_01;
;
END_CASE
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
(*Modbus Slave Example*)
PROGRAM PLC_PRG_modnet
VAR
Slave_Adresa:BYTE:=2;
Slave_Port:INT:=502;
SlaveSetup:MBS_Setup;
SlavePoll:MBS_Poll;
SlaveAnswer:MBS_Answer;
step: USINT;
end :BOOL;
i: INT;
cycle :BOOL := FALSE; (* First cycle *)
OpenDefaultPort: BOOL;
Write_16: BOOL;
Write_15: BOOL;
Write_5: BOOL;
j: INT;
slavepollwOffset_temp: INT;
slaveanswerwCount_temp: INT;
slaveanswerwoffset_temp: INT;
END_VAR
(* @END_DECLARATION := '0' *)
(*Modbus Slave Example*)
IF Write_16=TRUE THEN (**)
FOR j := 0 TO (slaveanswerwCount_temp-1)/15 BY 1 DO (*vpiše se dword, real*)
wStr_0:=mind[slaveanswerwoffset_temp+j];
wStr_1:=mind[slaveanswerwoffset_temp+j+1];
wStr_2 :=mind[slaveanswerwoffset_temp+j+2];
wStr_3:=mind[slaveanswerwoffset_temp+j+3];
wStr_4:=mind[slaveanswerwoffset_temp+j+4];
wStr_5 :=mind[slaveanswerwoffset_temp+j+5];
wStr_6:=mind[slaveanswerwoffset_temp+j+6];
wStr_7:=mind[slaveanswerwoffset_temp+j+7];
wStr_8:=mind[slaveanswerwoffset_temp+j+8];
wStr_9:=mind[slaveanswerwoffset_temp+j+9];
wStr_10:=mind[slaveanswerwoffset_temp+j+10];
wStr_11:=mind[slaveanswerwoffset_temp+j+11];
wStr_12:=mind[slaveanswerwoffset_temp+j+12];
wStr_13:=mind[slaveanswerwoffset_temp+j+13];
wStr_14:=mind[slaveanswerwoffset_temp+j+14];
bStr_29:=0;
mod_Write_String(index:=slaveanswerwoffset_temp+j); (*vpis real in string*)
END_FOR;
FOR j := 1 TO slaveanswerwCount_temp-1 BY 2 DO (*vpiše se dword, real*)
Word_01:=mind[slaveanswerwoffset_temp+j-1];
Word_23:=mind[slaveanswerwoffset_temp+j];
mod_Write_dWord(index:=slaveanswerwoffset_temp+j); (*vpis real in dword*)
END_FOR;
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO (*vpiše se word*)
Word_01:=mind[slaveanswerwoffset_temp+j];
mod_Write_Word(index:=slaveanswerwoffset_temp+j); (*vpis word*)
END_FOR;
Write_16:=FALSE;
END_IF;
IF Write_5=TRUE OR Write_15=TRUE THEN (**)
FOR j := 0 TO slaveanswerwCount_temp-1 BY 1 DO
Bit_0:=mind_bool[slaveanswerwoffset_temp+j];
mod_Write_Bool(index:=slaveanswerwoffset_temp+j); (*vpis spremembe v spremenljivko*)
END_FOR;
Write_5:=FALSE;
Write_15:=FALSE;
END_IF;
(*iz scade ni komande za branje*)
IF Write_16=FALSE AND Write_5=FALSE AND Write_15=FALSE THEN
mod_Read();(*branje spremenljivk za scado*)
END_IF
(*Close all sockets on corresponding event*)
IF cycle = FALSE THEN
SysCallbackRegister(INDEXOF(Callback_Stop),event_stop);
SysCallbackRegister(INDEXOF(Callback_Reset),event_before_reset);
SysCallbackRegister(INDEXOF(Callback_Reset),event_shutdown);
cycle := TRUE;
END_IF
(*Close all connections via application *)
IF end = TRUE THEN
MBS_CloseAllConnections();
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=FALSE); (*Close port*)
step := 0;
END_IF
IF OpenDefaultPort=TRUE THEN
SlaveSetup (xstrobe:= TRUE,bUnitIdentifier:=Slave_Adresa,wDefaultPort:=Slave_Port,xDefaultPortActive:=TRUE); (*Close port*)
step := 0;
OpenDefaultPort:=FALSE;
END_IF
(* State machine for setup, poll and answer *)
CASE step OF
0:(**)
SlaveSetup.bUnitIdentifier:=Slave_Adresa;(*Subunitnumber*)
slavesetup.wDefaultPort:=Slave_Port;(*Standartport *)
SlaveSetup.xAdditionalPortActive:=FALSE;(*Port opened or closed*)
SlaveSetup.xSecureMode:=FALSE;(*If TRUE only preset IPs are accepted*)
SlaveSetup.tTimeout:=T#3m;(*Timeout if no communication with slave established*)
SlaveSetup(xStrobe:=TRUE);(*Strobe starts function*)
IF slavesetup.xBusy = FALSE THEN
slavesetup(xstrobe := FALSE);
step := 1 ;
END_IF;
1:(**)
SlavePoll(xStrobe:=TRUE);(*Searching for master commands*)
IF NOT SlavePoll.xBusy THEN
step:=2;
SlavePoll(xStrobe:=FALSE);
END_IF;
2:(**)
step:= 1;
CASE SlavePoll.bFunctionCode OF (*Connect accepted pollparameters with answerparameters*)
8:(**)(*Poll answers*)
;
15:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind_bool[slaveanswer.woffset+i] := slavepoll.xarData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.xarData:=slavepoll.xarData;
Write_15:=TRUE;
16:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
FOR i := 0 TO slaveanswer.wCount-1 BY 1 DO
mind[slaveanswer.woffset+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
slaveanswer.wardata := slavepoll.warData;
Write_16:=TRUE;
1,2:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slavepoll.wcount-1 BY 1 DO
slaveanswer.xarData[i]:=mind_bool[slavepoll.woffset+i]; (*Read from Data-array*)
END_FOR
3,4:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wOffset:=slavepoll.wOffset;
FOR i:= 0 TO slaveanswer.wCount-1 BY 1 DO
slaveanswer.warData[i]:=mind[slavepoll.woffset+i];(*Read from Data-array*)
END_FOR
5:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
mind_bool[slavepoll.woffset]:=slavepoll.xarData[0];(*Write to Data-array*)
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.xarData := slavepoll.xardata;
slaveanswerwoffset_temp:=slaveanswer.woffset;
slaveanswerwCount_temp:=slaveanswer.wCount;
Write_5:=TRUE;
6:
slaveanswer.bFunctionCode:= slavepoll.bFunctionCode;
mind[slavepoll.woffset]:= slavepoll.warData[0];(*Write to Data-array*)
slaveanswer.wOffset:= slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
slaveanswer.wardata := slavepoll.wardata;
23:
slaveanswer.bFunctionCode:=slavepoll.bFunctionCode;
slaveanswer.wOffset:=slavepoll.wOffset;
slaveanswer.wCount:=slavepoll.wCount;
FOR i:= 0 TO slavepoll.wCountAdd-1 BY 1 DO
mind[slavepoll.woffsetadd+i] := slavepoll.warData[i];(*Write to Data-array*)
END_FOR;
FOR i := 0 TO slavepoll.wCount BY 1 DO
slaveanswer.warData[i] := mind[1+slavepoll.woffset+i];(*Read from Data-array*)
END_FOR;
END_CASE;
IF slavepoll.xAvailable = TRUE THEN
slaveanswer();(*When Data ready, send answer*)
END_IF
END_CASE;
END_PROGRAM
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_dWord : BOOL
VAR_INPUT
dVAR: DWORD;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
DWord_0:=dVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_dWord2 : BOOL
VAR_INPUT
dVAR: DWORD;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
ULong_0:=dVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_Real : BOOL
VAR_INPUT
rVAR: REAL;
lo:INT;
hi:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
Real_0:=rVar;mind[lo]:=Word_01;mind[hi]:=Word_23;
END_FUNCTION
(* @PATH := '\/Modnet' *)
(* @SYMFILEFLAGS := '2048' *)
FUNCTION Read_String : BOOL
VAR_INPUT
sVar: STRING;
start:INT;
END_VAR
VAR
END_VAR
(* @END_DECLARATION := '0' *)
String_0:=LEFT (sVar,29);
mind[start]:=wStr_0;
mind[start+1]:=wStr_1;
mind[start+2]:=wStr_2;
mind[start+3]:=wStr_3;
mind[start+4]:=wStr_4;
mind[start+5]:=wStr_5;
mind[start+6]:=wStr_6;
mind[start+7]:=wStr_7;
mind[start+8]:=wStr_8;
mind[start+9]:=wStr_9;
mind[start+10]:=wStr_10;
mind[start+11]:=wStr_11;
mind[start+12]:=wStr_12;
mind[start+13]:=wStr_13;
bStr_29:=0;
mind[start+14]:=wStr_14;
END_FUNCTION
(* @GLOBAL_VARIABLE_LIST := 'Global_Variables_Modnet' *)
(* @PATH := '' *)
(* @SYMFILEFLAGS := '2048' *)
VAR_GLOBAL
(*delovno polje za modnet komunikacijo*)
mind :ARRAY [0..9999] OF WORD;
mind_bool :ARRAY [0..9999] OF BOOL; (*Buffer-Array*)
(*Delovni markerji //*)
Bit_0 AT %MX0.0 : BOOL;
Byte_0 AT %MB0 : BYTE;
Byte_1 AT %MB1 : BYTE;
Byte_2 AT %MB2 : BYTE;
Byte_3 AT %MB3 : BYTE;
Real_0 AT %MR0:REAL;
Long_0 AT %MD0:DINT;
ULong_0 AT %MD0:UDINT;
DWord_0 AT %MD0:DWORD;
Word_01 AT %MW0:WORD;
Word_23 AT %MW2:WORD;
String_0 AT %MW10:STRING;
wStr_0 AT %MW10:WORD;
wStr_1 AT %MW12:WORD;
wStr_2 AT %MW14:WORD;
wStr_3 AT %MW16:WORD;
wStr_4 AT %MW18:WORD;
wStr_5 AT %MW20:WORD;
wStr_6 AT %MW22:WORD;
wStr_7 AT %MW24:WORD;
wStr_8 AT %MW26:WORD;
wStr_9 AT %MW28:WORD;
wStr_10 AT %MW30:WORD;
wStr_11 AT %MW32:WORD;
wStr_12 AT %MW34:WORD;
wStr_13 AT %MW36:WORD;
wStr_14 AT %MW38:WORD;
bStr_00 AT %MB10:BYTE;
bStr_01 AT %MB11:BYTE;
bStr_02 AT %MB12:BYTE;
bStr_03 AT %MB13:BYTE;
bStr_04 AT %MB14:BYTE;
bStr_05 AT %MB15:BYTE;
bStr_06 AT %MB16:BYTE;
bStr_07 AT %MB17:BYTE;
bStr_08 AT %MB18:BYTE;
bStr_09 AT %MB19:BYTE;
bStr_10 AT %MB20:BYTE;
bStr_11 AT %MB21:BYTE;
bStr_12 AT %MB22:BYTE;
bStr_13 AT %MB23:BYTE;
bStr_14 AT %MB24:BYTE;
bStr_15 AT %MB25:BYTE;
bStr_16 AT %MB26:BYTE;
bStr_17 AT %MB27:BYTE;
bStr_18 AT %MB28:BYTE;
bStr_19 AT %MB29:BYTE;
bStr_20 AT %MB30:BYTE;
bStr_21 AT %MB31:BYTE;
bStr_22 AT %MB32:BYTE;
bStr_23 AT %MB33:BYTE;
bStr_24 AT %MB34:BYTE;
bStr_25 AT %MB35:BYTE;
bStr_26 AT %MB36:BYTE;
bStr_27 AT %MB37:BYTE;
bStr_28 AT %MB38:BYTE;
bStr_29 AT %MB39:BYTE;
(********************************************)
END_VAR
(* @OBJECT_END := 'Global_Variables_Modnet' *)
(* @CONNECTIONS := Global_Variables_Modnet
FILENAME : ''
FILETIME : 0
EXPORT : 0
NUMOFCONNECTIONS : 0
*)
(*KONEC_KODA*)